## Pre-test
DESIREE-FIRE Intermediate Scale Test 11 - Temperature Data Only
Test Date: | 2009-11-25
DCSim DAQ Start Time | 13:25
DCSim Time for Synchronization | 13:28
Heat Source Synchronization | 0:02 | hours:minutes:seconds
Heat Source DAQ Start Time | 13:26
Fire Time | 15:38
Offset | 2:13 | hours:minutes:seconds | This is the time after the DCSim DAQ was started and the heat source was initiated.
| 7980 | seconds
Heat Source Offset | 2:12 | hours:minutes:seconds | This is the time after the Heat Source DAQ was started and the heat source was initiated.
| 7945 | seconds
Heat Source Stop Time | 16:53
Test Duration | 1:15 | hours:minutes:seconds
| 4500 | seconds
CT500 turns | 2 |  | This is the number of times the lead conductor within the DCSim Panels were wrapped around the Hall Effect Device of the current transducer.
CT35 turns | 5
Pre-Test Baseline: | Gathered
Cable Information: | Record info about cable type on each circuit and which of the cable thermocouples corresponds to cable and air temperature
Unit Number | Cable Type |  | Cable TC Channel | Air TC Channel
1" Solenoid Valve | EPR/CPE, 7c, 12AWG |  | Cable thermocouples were not used for this test. | Channel 1 which is defined as "B Position - Middle" in the Temperature Data File respresents the temperature in the center of the cable tray.
Large Coil | EPR/CPE, 7c, 12AWG |  | Cable thermocouples were not used for this test. | Channel 1 which is defined as "B Position - Middle" in the Temperature Data File respresents the temperature in the center of the cable tray.
A Note on Data Conversion and Accuracy:
Two different types of voltage transducers were used for each circuit. A bidirectional transducer (Ohio Semitronics, model number VT7-005X5-11) produces a 0 - 5V output signal which is directly proportional to the DC input ranging from 0 - 150VDC. The accuracy of this device is +/-0.25% full scale at DC and the response time is 50 mircoseconds. The unidirectional DC voltage isolator (Ohio Semitronics, model number VTU-005X5) used throughout tests also produces a 0 - 5V output over a 0 - 150VDC range. The accuracy of this device is +/-0.25% Rdg., +/-1% full scale at DC and the response time is 500 microseconds. Two different current transducers were for each circuit. One current transducer (Ohio Semitronics, model number CTL-51/35) was used to detect lower (0 - 35A) amperage transient behavior through a paired and calibrated signal conditioner (CTA201RX5). The other transducer (Ohio Semitronics, model number CTL-601/500) was set to detect transient current increases from 0 - 500A. These were also paired and calibrated with a signal conditioner (CTA2-1X5).
The readings were monitored using a National Instruments SCXI-1100 modules attached to SCXI-1300 multiplexers and housed within a SCXI-1001, 12-slot chassis. The "Raw Data" worksheet has been previously converted by LabView program created for this test series. The nominal zero point readings for each current transducer was taken before each test due to an electromagnetic effect created by direct current power. Zero Point values are provided, and the full run is documented in a separate data sheet (see "Current Offsets" worksheet). The converted data are presented as nominal indications of circuit path voltage and current. The data gathering equipment (transducers and DAQ card) have not been subject to specific calibration beyond that provided by the manufacturers. The accuracy of the converted data is estimated at +/-2%.

## Raw Data
Time | A Position - Middle | B Position - Middle | C Position - 3' | C Position - Middle | C Position - 7' | D Position - 3' | D Position - Middle | D Position - 7' | E Position - 3' | E Position - Middle | E Position - 7' | Burner | spare | spare | spare | spare | spare | spare | spare | spare | spare | spare | TC 23 | TC 24 | TC 25 | TC 26
0 | 11.3844 | 11.1239 | 11.3589 | 11.7131 | 11.3676 | 11.5193 | 11.3665 | 11.2669 | NaN | NaN | NaN | 11.4081 | 1257.1114 | NaN | NaN | 1255.8395 | 249.9651 | NaN | 363.3981 | NaN | 521.0594 | 1256.5409 | NaN | 27.9944 | NaN | 3.4481
0.5042 | 11.3862 | 11.1228 | 11.3669 | 11.7137 | 11.3702 | 11.5245 | 11.3669 | 11.2721 | NaN | NaN | NaN | 11.4106 | 1257.1118 | NaN | NaN | 1255.84 | 196.7246 | NaN | 222.4233 | NaN | 545.2502 | 1256.5413 | NaN | 26.4667 | NaN | 23.8307
1.1292 | 11.3876 | 11.1171 | 11.3623 | 11.7194 | 11.3811 | 11.5307 | 11.3662 | 11.2737 | NaN | NaN | NaN | 11.4158 | 1257.1129 | NaN | NaN | 1255.841 | 120.3999 | NaN | 15.6623 | NaN | 578.4964 | 1256.5423 | NaN | 25.9744 | NaN | 28.3151
2.1292 | 11.3914 | 11.1382 | 11.3666 | 11.7246 | 11.3698 | 11.5303 | 11.373 | 11.2639 | NaN | NaN | NaN | 11.4193 | 1257.1123 | NaN | NaN | 1255.8404 | 3.0647 | NaN | NaN | NaN | 631.7744 | 1256.5417 | NaN | 26.3456 | NaN | 23.898
3.1292 | 11.3938 | 11.1455 | 11.3638 | 11.7328 | 11.3739 | 11.534 | 11.3666 | 11.2656 | NaN | NaN | NaN | 11.4211 | 1226.5439 | NaN | NaN | 1255.8399 | NaN | NaN | NaN | NaN | 687.3744 | 1256.5412 | NaN | 25.9111 | NaN | 22.857
4.1292 | 11.3967 | 11.1669 | 11.3711 | 11.7445 | 11.3823 | 11.5433 | 11.3731 | 11.2744 | NaN | NaN | NaN | 11.4308 | 1149.7606 | NaN | NaN | 1255.8407 | NaN | NaN | NaN | NaN | 749.9073 | 1256.542 | NaN | 26.1669 | NaN | 19.9118
5.1292 | 11.3925 | 11.1532 | 11.3732 | 11.7456 | 11.3779 | 11.5408 | 11.377 | 11.2688 | NaN | NaN | NaN | 11.4272 | 1078.5468 | NaN | NaN | 1255.8401 | NaN | NaN | NaN | NaN | 811.8957 | 1256.5414 | NaN | 26.5043 | NaN | 29.7605
6.1292 | 11.402 | 11.1779 | 11.3817 | 11.7548 | 11.3823 | 11.5445 | 11.3779 | 11.2673 | NaN | NaN | NaN | 11.4385 | 1010.3502 | NaN | NaN | 1213.6319 | NaN | NaN | NaN | NaN | 870.5441 | 1256.5421 | NaN | 28.8454 | NaN | 25.6116
7.1292 | 11.4014 | 11.1731 | 11.3809 | 11.7556 | 11.3787 | 11.548 | 11.383 | 11.2641 | NaN | NaN | NaN | 11.4358 | 944.9306 | NaN | NaN | 1157.1094 | NaN | NaN | NaN | NaN | 931.5698 | 1225.5984 | NaN | 29.7618 | NaN | 23.1068
8.1292 | 11.4037 | 11.1859 | 11.3774 | 11.7579 | 11.375 | 11.5491 | 11.3741 | 11.2595 | NaN | NaN | NaN | 11.4352 | 882.0671 | NaN | NaN | 1102.8964 | NaN | NaN | NaN | NaN | 988.7363 | 1191.0842 | NaN | 28.068 | NaN | 20.893
9.1292 | 11.4048 | 11.1817 | 11.374 | 11.7681 | 11.3777 | 11.5552 | 11.3809 | 11.2572 | NaN | NaN | NaN | 11.432 | 821.6989 | NaN | NaN | 1051.2661 | NaN | NaN | NaN | NaN | 1048.9848 | 1159.5975 | NaN | 25.9167 | NaN | 29.2647
10.1292 | 11.4073 | 11.1995 | 11.3779 | 11.773 | 11.3747 | 11.5572 | 11.3863 | 11.2564 | NaN | NaN | NaN | 11.4453 | 765.432 | NaN | NaN | 1003.4307 | NaN | NaN | NaN | NaN | 1054.2189 | 1128.8574 | NaN | 27.5866 | NaN | 29.0954
11.1292 | 11.4099 | 11.2071 | 11.38 | 11.7827 | 11.3752 | 11.556 | 11.3858 | 11.2618 | NaN | NaN | NaN | 11.4483 | 711.3193 | NaN | NaN | 957.2162 | NaN | NaN | NaN | NaN | 1020.9266 | 1099.2343 | NaN | 27.6012 | NaN | 20.9266
12.1292 | 11.412 | 11.2063 | 11.3876 | 11.7879 | 11.3787 | 11.5571 | 11.3905 | 11.2527 | NaN | NaN | NaN | 11.4531 | 659.1745 | NaN | NaN | 912.9741 | NaN | NaN | NaN | NaN | 989.0372 | 1070.9025 | NaN | 27.5799 | NaN | 23.5405
13.1292 | 11.4169 | 11.3809 | 11.3811 | 11.7794 | 11.3774 | 11.7999 | 11.5097 | 11.2542 | NaN | NaN | NaN | 11.4513 | 602.919 | NaN | NaN | 863.4266 | NaN | NaN | NaN | NaN | 950.08 | 1033.7097 | NaN | 27.5518 | NaN | 30.5587
14.1292 | 11.4137 | 11.4551 | 11.3851 | 11.8018 | 11.3781 | 11.8676 | 11.5228 | 11.2564 | NaN | NaN | NaN | 11.4567 | 567.3667 | NaN | NaN | 837.1347 | NaN | NaN | NaN | NaN | 933.7109 | 1021.6879 | NaN | 29.1813 | NaN | 28.9255
15.1292 | 11.4153 | 11.3426 | 11.3835 | 11.7191 | 11.3789 | 11.745 | 11.4771 | 11.261 | NaN | NaN | NaN | 11.4545 | 532.0449 | NaN | NaN | 811.3315 | NaN | NaN | NaN | NaN | 916.331 | 1010.7449 | NaN | 25.9859 | NaN | 21.6058
16.1292 | 11.4143 | 12.0921 | 11.3849 | 11.9487 | 11.3763 | 12.5716 | 11.8426 | 11.255 | NaN | NaN | NaN | 11.4611 | 491.7865 | NaN | NaN | 779.6756 | NaN | NaN | NaN | NaN | 893.9375 | 997.3457 | NaN | 29.9333 | NaN | 24.9014
17.1292 | 11.4177 | 12.0624 | 11.3907 | 11.7855 | 11.3797 | 11.9144 | 11.7338 | 11.2589 | NaN | NaN | NaN | 11.45 | 456.8156 | NaN | NaN | 753.9739 | NaN | NaN | NaN | NaN | 875.3894 | 984.7654 | NaN | 27.0837 | NaN | 22.2283
18.1292 | 11.4115 | 11.3622 | 11.3905 | 11.7845 | 11.3842 | 11.7842 | 11.4967 | 11.2543 | NaN | NaN | NaN | 11.4583 | 425.6712 | NaN | NaN | 732.7487 | NaN | NaN | NaN | NaN | 860.4773 | 974.3276 | NaN | 27.6344 | NaN | 25.6609
19.1292 | 11.4123 | 11.3907 | 11.3865 | 11.7823 | 11.38 | 11.7769 | 11.499 | 11.253 | NaN | NaN | NaN | 11.4589 | 391.4367 | NaN | NaN | 708.219 | NaN | NaN | NaN | NaN | 842.9255 | 958.3533 | NaN | 29.1477 | NaN | 26.2939
20.1292 | 11.4155 | 11.308 | 11.39 | 11.7721 | 11.3787 | 11.6966 | 11.4602 | 11.2615 | NaN | NaN | NaN | 11.4602 | 357.7666 | NaN | NaN | 684.4123 | NaN | NaN | NaN | NaN | 826.3241 | 948.5622 | NaN | 27.9117 | NaN | 22.6129
21.1292 | 11.4266 | 11.4351 | 11.3843 | 11.7596 | 11.3807 | 11.7723 | 11.4944 | 11.2609 | NaN | NaN | NaN | 11.4615 | 325.3349 | NaN | NaN | 661.5468 | NaN | NaN | NaN | NaN | 808.7095 | 935.4853 | NaN | 29.2856 | NaN | 24.1232
22.1292 | 11.4177 | 11.356 | 11.392 | 11.7326 | 11.3749 | 11.8093 | 11.4913 | 11.2642 | NaN | NaN | NaN | 11.4648 | 287.5574 | NaN | NaN | 633.3183 | NaN | NaN | NaN | NaN | 790.964 | 927.2271 | NaN | 28.8383 | NaN | 19.3684
23.1292 | 11.4189 | 11.377 | 11.3809 | 11.8187 | 11.3763 | 11.8045 | 11.501 | 11.2563 | NaN | NaN | NaN | 11.4741 | 254.3156 | NaN | NaN | 610.0988 | NaN | NaN | NaN | NaN | 774.2306 | 915.1689 | NaN | 27.9848 | NaN | 24.9293
24.1292 | 11.4183 | 11.6725 | 11.3856 | 11.8882 | 11.3726 | 11.7962 | 11.5541 | 11.2547 | NaN | NaN | NaN | 11.4701 | 223.02 | NaN | NaN | 589.2717 | NaN | NaN | NaN | NaN | 758.6293 | 903.039 | NaN | 26.9529 | NaN | 26.3132
25.1292 | 11.422 | 11.3762 | 11.3842 | 11.7311 | 11.3784 | 11.7873 | 11.4888 | 11.2608 | NaN | NaN | NaN | 11.4736 | 183.1787 | NaN | NaN | 561.0477 | NaN | NaN | NaN | NaN | 740.7473 | 893.4018 | NaN | 30.8952 | NaN | 20.1516
26.1292 | 11.4189 | 11.3674 | 11.3888 | 11.792 | 11.2323 | 11.6806 | 11.469 | 11.2603 | NaN | NaN | NaN | 11.4786 | 154.1604 | NaN | NaN | 544.6991 | NaN | NaN | NaN | NaN | 729.7849 | 883.2059 | NaN | 27.467 | NaN | 26.1876
27.1292 | 11.4173 | 11.5251 | 11.3844 | 11.7331 | 11.2484 | 11.807 | 11.5164 | 11.2585 | NaN | NaN | NaN | 11.4796 | 92.6587 | NaN | NaN | 515.9303 | NaN | NaN | NaN | NaN | 708.8777 | 875.1152 | NaN | 30.1248 | NaN | 22.1462
28.1292 | 11.4275 | 11.499 | 11.3822 | 11.7863 | 11.0929 | 11.8757 | 11.5469 | 11.2587 | NaN | NaN | NaN | 11.4753 | 93.7231 | NaN | NaN | 499.7465 | NaN | NaN | NaN | NaN | 703.6364 | 868.8168 | NaN | 27.5545 | NaN | 28.3304
29.1292 | 11.4211 | 11.3789 | 11.3836 | 11.9015 | 10.9099 | 11.7792 | 11.4972 | 11.257 | NaN | NaN | NaN | 11.4879 | 92.6338 | NaN | NaN | 479.0956 | NaN | NaN | NaN | NaN | 695.1302 | 862.9976 | NaN | 28.6177 | NaN | 28.861
30.1292 | 11.4173 | 11.3661 | 11.3817 | 11.7884 | 11.2111 | 11.7451 | 11.497 | 11.2604 | NaN | NaN | NaN | 11.4858 | 93.3514 | NaN | NaN | 464.5117 | 1198.2343 | NaN | NaN | NaN | 689.6157 | 856.1636 | NaN | 28.7458 | NaN | 22.6062
31.1292 | 11.4223 | 11.5296 | 11.3815 | 11.773 | 11.0879 | 11.9841 | 11.5603 | 11.2571 | NaN | NaN | NaN | 11.4835 | 92.7634 | NaN | NaN | 445.9307 | 839.6392 | NaN | NaN | NaN | 681.6623 | 848.9958 | NaN | 29.0761 | NaN | 27.5006
32.1292 | 11.4232 | 11.4016 | 11.3819 | 11.7469 | 11.0797 | 11.7069 | 11.496 | 11.2601 | NaN | NaN | NaN | 11.4932 | 92.5194 | NaN | NaN | 431.7979 | 616.949 | NaN | NaN | NaN | 677.209 | 843.4528 | NaN | 26.2097 | NaN | 25.2201
33.1292 | 11.4278 | 11.5291 | 11.3808 | 11.7467 | 11.3556 | 11.8679 | 11.5248 | 11.2592 | NaN | NaN | NaN | 11.4882 | 94.4613 | NaN | NaN | 414.2046 | 422.7121 | NaN | NaN | NaN | 670.048 | 836.9794 | NaN | 29.0961 | NaN | 24.1483
34.1292 | 11.4167 | 11.6901 | 11.379 | 11.8643 | 11.0288 | 11.8184 | 11.6178 | 11.2606 | NaN | NaN | NaN | 11.4884 | 90.9802 | NaN | NaN | 394.6963 | 250.1392 | NaN | NaN | NaN | 661.9111 | 831.0281 | NaN | 27.4362 | NaN | 24.0392
35.1292 | 11.4175 | 11.5149 | 11.3757 | 11.7891 | 11.1354 | 11.8432 | 11.5356 | 11.2589 | NaN | NaN | NaN | 11.4867 | 94.6381 | NaN | NaN | 379.765 | 167.145 | NaN | NaN | NaN | 656.142 | 826.2307 | NaN | 29.0892 | NaN | 27.6593
36.1292 | 11.4148 | 11.3521 | 11.389 | 11.7304 | 11.2144 | 11.7016 | 11.4886 | 11.2615 | NaN | NaN | NaN | 11.4912 | 94.2279 | NaN | NaN | 363.3436 | 91.5262 | NaN | NaN | NaN | 649.2159 | 821.2757 | NaN | 26.8792 | NaN | 28.0883
37.1292 | 11.4112 | 11.3451 | 11.3823 | 11.7945 | 11.2229 | 11.7225 | 11.4914 | 11.2569 | NaN | NaN | NaN | 11.4919 | 93.5216 | NaN | NaN | 345.4255 | 31.7654 | NaN | NaN | NaN | 642.0701 | 815.4426 | NaN | 27.585 | NaN | 25.4476
38.1292 | 11.4163 | 11.6102 | 11.3879 | 11.8619 | 11.1617 | 11.9421 | 11.6094 | 11.2584 | NaN | NaN | NaN | 11.4956 | 92.4159 | NaN | NaN | 328.157 | -5.6053 | NaN | NaN | NaN | 635.5134 | 808.4735 | NaN | 30.2193 | NaN | 22.0166
39.1292 | 11.4071 | 11.3356 | 11.3853 | 11.7675 | 11.1149 | 11.6571 | 11.4754 | 11.2549 | NaN | NaN | NaN | 11.4995 | 93.3326 | NaN | NaN | 314.4778 | NaN | NaN | NaN | NaN | 629.921 | 803.2819 | NaN | 29.2251 | NaN | 27.9209
40.1292 | 11.4135 | 11.51 | 11.391 | 11.6944 | 11.1577 | 11.717 | 11.5142 | 11.2556 | NaN | NaN | NaN | 11.4928 | 90.5652 | NaN | NaN | 296.0446 | NaN | NaN | NaN | NaN | 622.2168 | 798.1484 | NaN | 27.7459 | NaN | 26.4916
41.1292 | 11.4082 | 11.385 | 11.3925 | 11.8164 | 11.1811 | 11.7103 | 11.4737 | 11.2561 | NaN | NaN | NaN | 11.4995 | 93.4589 | NaN | NaN | 280.5757 | NaN | NaN | NaN | NaN | 616.1225 | 793.8207 | NaN | 28.0845 | NaN | 28.7813
42.1292 | 11.4083 | 11.8666 | 11.3859 | 11.7224 | 11.1174 | 12.1193 | 11.6945 | 11.2593 | NaN | NaN | NaN | 11.5043 | 92.4185 | NaN | NaN | 260.9465 | NaN | NaN | NaN | NaN | 608.2802 | 787.2042 | NaN | 26.7487 | NaN | 22.3056
43.1292 | 11.4044 | 11.4606 | 11.3941 | 11.776 | 11.2137 | 11.7776 | 11.512 | 11.2558 | NaN | NaN | NaN | 11.5066 | 88.5381 | NaN | NaN | 242.0114 | NaN | NaN | NaN | NaN | 601.123 | 780.922 | NaN | 29.9204 | NaN | 21.0644
44.1292 | 11.4049 | 11.3432 | 11.3901 | 11.8054 | 11.1307 | 11.7053 | 11.4696 | 11.2552 | NaN | NaN | NaN | 11.5097 | 92.5351 | NaN | NaN | 226.1198 | NaN | NaN | NaN | NaN | 596.1291 | 775.3194 | NaN | 28.4645 | NaN | 23.4566
45.1292 | 11.4124 | 11.3719 | 11.3966 | 11.8396 | 10.9736 | 11.808 | 11.505 | 11.2657 | NaN | NaN | NaN | 11.5055 | 92.4509 | NaN | NaN | 202.7229 | -17.486 | NaN | NaN | NaN | 587.38 | 770.3237 | NaN | 28.7056 | NaN | 18.8842
46.1292 | 11.3868 | 11.4067 | 11.393 | 11.7498 | 11.075 | 11.818 | 11.5026 | 11.2521 | NaN | NaN | NaN | 11.5064 | 90.9032 | NaN | NaN | 184.8084 | -13.7323 | NaN | NaN | NaN | 581.2453 | 764.6087 | NaN | 27.6076 | NaN | 23.6671
47.1292 | 11.3624 | 11.8088 | 11.3911 | 11.7529 | 11.0318 | 12.2088 | 11.7009 | 11.2537 | NaN | NaN | NaN | 11.5045 | 93.3834 | NaN | NaN | 172.4633 | NaN | NaN | NaN | NaN | 575.8149 | 759.9561 | NaN | 29.8499 | NaN | 28.2462
48.1292 | 11.6107 | 11.4286 | 11.3927 | 11.8421 | 11.1695 | 11.7365 | 11.4977 | 11.2577 | NaN | NaN | NaN | 11.5152 | 95.4307 | NaN | NaN | 152.8022 | -17.4093 | NaN | NaN | NaN | 570.1178 | 757.4025 | NaN | 28.0753 | NaN | 22.9543
49.1292 | 11.3923 | 11.3996 | 11.3992 | 11.7864 | 11.286 | 11.7951 | 11.5069 | 11.2555 | NaN | NaN | NaN | 11.5084 | 103.0355 | NaN | NaN | 133.9689 | -18.6313 | NaN | NaN | NaN | 565.1917 | 751.5835 | NaN | 28.6164 | NaN | 26.4883
50.1292 | 11.4447 | 11.4653 | 11.3897 | 11.7263 | 11.1229 | 11.7945 | 11.5246 | 11.2498 | NaN | NaN | NaN | 11.5024 | 95.1477 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 560.4365 | 747.0398 | NaN | 30.2089 | NaN | 25.5452
51.1448 | 11.4013 | 11.2921 | 11.3958 | 11.762 | 11.0638 | 11.6673 | 11.4605 | 11.2592 | NaN | NaN | NaN | 11.5066 | 89.0077 | NaN | NaN | NaN | -3.824 | NaN | NaN | NaN | 557.0528 | 749.1905 | NaN | 30.2384 | NaN | 24.3253
52.1292 | 11.4193 | 11.523 | 11.3904 | 11.6907 | 11.0252 | 11.8502 | 11.5422 | 11.2574 | NaN | NaN | NaN | 11.5102 | 93.1579 | NaN | NaN | NaN | -12.581 | NaN | NaN | NaN | 550.7089 | 745.0062 | NaN | 27.7085 | NaN | 22.115
53.1292 | 11.4456 | 11.4669 | 11.3919 | 11.6991 | 11.04 | 11.8921 | 11.5268 | 11.256 | NaN | NaN | NaN | 11.5096 | 91.6899 | NaN | NaN | NaN | -18.4459 | NaN | NaN | NaN | 546.2714 | 742.5097 | NaN | 28.4151 | NaN | 22.977
54.1292 | 11.4114 | 11.4392 | 11.3966 | 11.7969 | 11.0765 | 11.7796 | 11.514 | 11.255 | NaN | NaN | NaN | 11.5141 | 92.1762 | NaN | NaN | NaN | -10.8924 | NaN | NaN | NaN | 542.1707 | 735.5694 | NaN | 29.2428 | NaN | 25.8614
55.1292 | 11.3912 | 11.3634 | 11.3974 | 11.7039 | 11.0069 | 11.8518 | 11.5029 | 11.2524 | NaN | NaN | NaN | 11.529 | 92.3385 | NaN | NaN | NaN | -15.4214 | NaN | NaN | NaN | 537.8685 | 736.6609 | NaN | 29.6807 | NaN | 25.7067
56.1292 | 11.3677 | 11.3198 | 11.3999 | 11.8121 | 11.1987 | 11.6532 | 11.4546 | 11.2576 | NaN | NaN | NaN | 11.5193 | 91.3476 | NaN | NaN | NaN | -0.4113 | NaN | NaN | NaN | 535.7638 | 733.2475 | NaN | 28.4051 | NaN | 27.1641
57.1292 | 11.3413 | 11.5605 | 11.3948 | 11.7297 | 11.068 | 11.8542 | 11.5154 | 11.2587 | NaN | NaN | NaN | 11.5187 | 91.8809 | NaN | NaN | NaN | -15.7763 | NaN | NaN | NaN | 530.0748 | 731.2669 | NaN | 27.5045 | NaN | 20.6419
58.1292 | 11.3688 | 11.2322 | 11.3982 | 11.8135 | 11.1524 | 11.6095 | 11.4355 | 11.2537 | NaN | NaN | NaN | 11.5119 | 92.2716 | NaN | NaN | NaN | -7.7832 | NaN | NaN | NaN | 527.5601 | 731.5478 | NaN | 29.0669 | NaN | 25.3356
59.1292 | 11.339 | 11.6394 | 11.3951 | 11.7002 | 11.1553 | 11.9574 | 11.6136 | 11.2514 | NaN | NaN | NaN | 11.5222 | 90.3934 | NaN | NaN | NaN | -1.554 | NaN | NaN | NaN | 520.7079 | 725.1141 | NaN | 28.4864 | NaN | 24.0594
60.1292 | 11.3885 | 11.4941 | 11.3961 | 11.73 | 11.0359 | 11.8395 | 11.5391 | 11.255 | NaN | NaN | NaN | 11.5265 | 92.8835 | NaN | NaN | NaN | 4.6212 | NaN | NaN | NaN | 517.0379 | 723.5056 | NaN | 29.2058 | NaN | 24.7655
61.1292 | 11.3801 | 11.4414 | 11.3957 | 11.7379 | 11.0106 | 11.808 | 11.485 | 11.2612 | NaN | NaN | NaN | 11.5296 | 89.9479 | NaN | NaN | NaN | 7.2573 | NaN | NaN | NaN | 512.9376 | 722.4732 | NaN | 30.2465 | NaN | 21.5688
62.1292 | 11.7068 | 11.3913 | 11.3943 | 11.7144 | 11.0833 | 11.7503 | 11.4972 | 11.2627 | NaN | NaN | NaN | 11.5319 | 91.048 | NaN | NaN | NaN | -17.4292 | NaN | NaN | NaN | 508.833 | 718.784 | NaN | 27.928 | NaN | 22.3386
63.1292 | 11.5304 | 11.7052 | 11.3943 | 11.7457 | 11.0226 | 11.9127 | 11.612 | 11.2582 | NaN | NaN | NaN | 11.534 | 92.5633 | NaN | NaN | NaN | -19.6952 | NaN | NaN | NaN | 503.5422 | 715.2992 | NaN | 30.0763 | NaN | 25.8738
64.1292 | 11.4238 | 11.4461 | 11.3961 | 11.7386 | 10.9809 | 11.8251 | 11.493 | 11.2525 | NaN | NaN | NaN | 11.5293 | 92.1272 | NaN | NaN | NaN | 8.711 | NaN | NaN | NaN | 499.6577 | 713.3577 | NaN | 30.3447 | NaN | 25.5951
65.1292 | 11.3933 | 11.7824 | 11.3912 | 11.7177 | 11.0171 | 11.9174 | 11.6628 | 11.2596 | NaN | NaN | NaN | 11.5368 | 92.3861 | NaN | NaN | NaN | -16.2838 | NaN | NaN | NaN | 496.2241 | 710.7675 | NaN | 28.4208 | NaN | 27.3438
66.1292 | 11.4898 | 11.4056 | 11.3955 | 11.7757 | 11.0761 | 11.7479 | 11.4996 | 11.255 | NaN | NaN | NaN | 11.5342 | 94.0939 | NaN | NaN | NaN | 6.1281 | NaN | NaN | NaN | 494.463 | 708.3905 | NaN | 29.5104 | NaN | 25.076
67.1292 | 11.3612 | 11.5265 | 11.3961 | 11.7866 | 11.0997 | 11.8696 | 11.5403 | 11.2614 | NaN | NaN | NaN | 11.5396 | 94.2856 | NaN | NaN | NaN | -9.8083 | NaN | NaN | NaN | 489.0379 | 705.4388 | NaN | 29.1051 | NaN | 24.7308
68.1292 | 11.424 | 11.2871 | 11.3949 | 11.7591 | 11.0072 | 11.7003 | 11.4651 | 11.2576 | NaN | NaN | NaN | 11.5391 | 92.4201 | NaN | NaN | NaN | 9.5713 | NaN | NaN | NaN | 487.0607 | 707.1133 | NaN | 29.1938 | NaN | 27.4165
69.1292 | 11.4428 | 11.3336 | 11.395 | 11.74 | 11.1158 | 11.7042 | 11.4734 | 11.2606 | NaN | NaN | NaN | 11.5424 | 94.1018 | NaN | NaN | NaN | -18.7131 | NaN | NaN | NaN | 483.2363 | 705.4231 | NaN | 27.661 | NaN | 23.725
70.1292 | 11.3181 | 11.2542 | 11.3914 | 11.8492 | 11.0534 | 11.6571 | 11.4465 | 11.26 | NaN | NaN | NaN | 11.5406 | 96.019 | NaN | NaN | NaN | -11.3794 | NaN | NaN | NaN | 479.9767 | 702.5896 | NaN | 28.3595 | NaN | 22.509
71.1292 | 11.4514 | 11.5031 | 11.3996 | 11.797 | 11.239 | 11.7343 | 11.5328 | 11.2637 | NaN | NaN | NaN | 11.5469 | 90.4644 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 475.7106 | 699.2796 | NaN | 29.0499 | NaN | 21.1594
72.1292 | 11.3916 | 11.2819 | 11.3959 | 11.6781 | 11.1026 | 11.6884 | 11.4649 | 11.2679 | NaN | NaN | NaN | 11.5499 | 92.4638 | NaN | NaN | NaN | -5.7255 | NaN | NaN | NaN | 472.2567 | 700.0648 | NaN | 29.3541 | NaN | 21.5193
73.1292 | 11.4034 | 11.4247 | 11.3921 | 11.8831 | 11.1017 | 11.7727 | 11.5196 | 11.273 | NaN | NaN | NaN | 11.545 | 94.0366 | NaN | NaN | NaN | -3.2667 | NaN | NaN | NaN | 468.457 | 695.4906 | NaN | 27.4017 | NaN | 20.9828
74.1292 | 11.4662 | 11.466 | 11.3946 | 11.7512 | 11.0869 | 11.7809 | 11.4865 | 11.2637 | NaN | NaN | NaN | 11.5493 | 91.563 | NaN | NaN | NaN | -14.6551 | NaN | NaN | NaN | 466.243 | 693.2566 | NaN | 29.851 | NaN | 24.3503
75.1292 | 11.3469 | 11.4344 | 11.3937 | 11.7079 | 11.0698 | 11.7839 | 11.4878 | 11.2669 | NaN | NaN | NaN | 11.5566 | 92.2185 | NaN | NaN | NaN | -14.1747 | NaN | NaN | NaN | 462.0748 | 694.2327 | NaN | 28.3701 | NaN | 26.5265
76.1292 | 11.3793 | 11.7818 | 11.39 | 12.0476 | 11.0714 | 12.0571 | 11.5763 | 11.2675 | NaN | NaN | NaN | 11.5486 | 90.7445 | NaN | NaN | NaN | -19.878 | NaN | NaN | NaN | 458.3801 | 691.4888 | NaN | 30.0992 | NaN | 24.5436
77.1292 | 11.3789 | 11.2775 | 11.3851 | 11.746 | 11.0908 | 11.7397 | 11.446 | 11.2716 | NaN | NaN | NaN | 11.5522 | 89.454 | NaN | NaN | NaN | -9.1402 | NaN | NaN | NaN | 457.4279 | 691.0941 | NaN | 28.837 | NaN | 26.5274
78.1292 | 11.4363 | 11.599 | 11.3864 | 11.7139 | 11.0773 | 11.9232 | 11.5569 | 11.2689 | NaN | NaN | NaN | 11.5576 | 93.1812 | NaN | NaN | NaN | -14.1133 | NaN | NaN | NaN | 450.2319 | 687.7746 | NaN | 27.9106 | NaN | 21.7643
79.1292 | 11.4672 | 11.3596 | 11.3877 | 11.782 | 11.2056 | 11.7392 | 11.5052 | 11.2637 | NaN | NaN | NaN | 11.5596 | 91.9679 | NaN | NaN | NaN | -7.3976 | NaN | NaN | NaN | 448.5305 | 684.6068 | NaN | 27.4961 | NaN | 26.618
80.1292 | 11.4309 | 11.3766 | 11.3944 | 11.7152 | 11.1405 | 11.7268 | 11.4937 | 11.2607 | NaN | NaN | NaN | 11.5611 | 92.568 | NaN | NaN | NaN | -10.3322 | NaN | NaN | NaN | 445.0734 | 682.7896 | NaN | 29.9532 | NaN | 23.2551
81.1292 | 11.345 | 11.5148 | 11.3889 | 11.7448 | 11.2336 | 11.9495 | 11.5174 | 11.2633 | NaN | NaN | NaN | 11.558 | 92.9118 | NaN | NaN | NaN | -16.1688 | NaN | NaN | NaN | 440.767 | 681.5588 | NaN | 29.7251 | NaN | 19.1586
82.1292 | 11.3793 | 11.4685 | 11.3884 | 11.8083 | 11.1557 | 11.9557 | 11.5331 | 11.2669 | NaN | NaN | NaN | 11.5701 | 91.9021 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 437.6724 | 678.6352 | NaN | 30.7153 | NaN | 23.8643
83.1604 | 11.4183 | 11.7523 | 11.3887 | 11.6916 | 11.0729 | 11.9054 | 11.5806 | 11.2683 | NaN | NaN | NaN | 11.5642 | 93.2964 | NaN | NaN | NaN | -12.4907 | NaN | NaN | NaN | 432.6925 | 677.1874 | NaN | 28.2501 | NaN | 22.7378
84.1292 | 11.392 | 11.3496 | 11.3872 | 11.6882 | 11.0764 | 11.7537 | 11.5023 | 11.2649 | NaN | NaN | NaN | 11.5579 | 94.1615 | NaN | NaN | NaN | -12.2611 | NaN | NaN | NaN | 430.6081 | 673.6192 | NaN | 29.8807 | NaN | 25.5845
85.1292 | 11.5946 | 11.4887 | 11.3866 | 11.776 | 11.1413 | 11.8135 | 11.5371 | 11.2663 | NaN | NaN | NaN | 11.5605 | 91.8105 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 427.7392 | 670.0195 | NaN | 30.2413 | NaN | 21.2546
86.1292 | 11.6606 | 11.3628 | 11.3853 | 11.7145 | 11.0373 | 11.8218 | 11.5102 | 11.2592 | NaN | NaN | NaN | 11.568 | 94.0627 | NaN | NaN | NaN | -12.1294 | NaN | NaN | NaN | 422.5363 | 670.0135 | NaN | 28.3757 | NaN | 23.1214
87.1292 | 11.348 | 11.4994 | 11.3862 | 11.7411 | 11.0365 | 11.8279 | 11.5519 | 11.2668 | NaN | NaN | NaN | 11.5708 | 91.908 | NaN | NaN | NaN | 1.0227 | NaN | NaN | NaN | 421.9916 | 666.8032 | NaN | 30.9218 | NaN | 24.2411
88.1292 | 11.35 | 11.349 | 11.3813 | 11.6962 | 11.0455 | 11.6755 | 11.4881 | 11.2672 | NaN | NaN | NaN | 11.568 | 92.8644 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 418.2937 | 666.6863 | NaN | 29.415 | NaN | 21.1422
89.1292 | 11.479 | 11.3328 | 11.3854 | 11.7671 | 11.1666 | 11.7619 | 11.4771 | 11.2624 | NaN | NaN | NaN | 11.6132 | 90.5648 | NaN | NaN | NaN | -13.03 | NaN | NaN | NaN | 411.8658 | 661.7218 | NaN | 30.1569 | NaN | 23.0401
90.1292 | 11.5956 | 11.5954 | 11.3831 | 11.6963 | 11.1483 | 11.9542 | 11.5923 | 11.263 | NaN | NaN | NaN | 11.6446 | 93.2673 | NaN | NaN | NaN | -13.1614 | NaN | NaN | NaN | 409.2287 | 659.8019 | NaN | 29.9618 | NaN | 22.6211
91.1292 | 11.555 | 11.3049 | 11.3847 | 11.7268 | 11.1387 | 11.7787 | 11.5055 | 11.2648 | NaN | NaN | NaN | 11.6691 | 93.7095 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 407.3459 | 657.1687 | NaN | 28.5199 | NaN | 23.0434
92.1292 | 11.3511 | 11.3775 | 11.3872 | 11.6717 | 10.951 | 11.7444 | 11.5178 | 11.2656 | NaN | NaN | NaN | 11.6291 | 92.3597 | NaN | NaN | NaN | -9.1638 | NaN | NaN | NaN | 404.483 | 657.3462 | NaN | 29.5349 | NaN | 27.8775
93.1292 | 11.3369 | 11.7024 | 11.3792 | 11.7496 | 11.076 | 12.1649 | 11.5642 | 11.2576 | NaN | NaN | NaN | 11.6855 | 93.4044 | NaN | NaN | NaN | -12.2493 | NaN | NaN | NaN | 401.2144 | 653.7114 | NaN | 29.7291 | NaN | 26.0696
94.1292 | 11.6196 | 11.3648 | 11.3876 | 11.7406 | 11.0797 | 11.7056 | 11.4883 | 11.2684 | NaN | NaN | NaN | 11.6464 | 90.9456 | NaN | NaN | NaN | -16.0886 | NaN | NaN | NaN | 399.9348 | 651.4931 | NaN | 30.5603 | NaN | 24.9017
95.1292 | 11.4115 | 11.4128 | 11.3896 | 11.7502 | 11.1445 | 11.8107 | 11.5276 | 11.2604 | NaN | NaN | NaN | 11.6997 | 94.1725 | NaN | NaN | NaN | -10.2289 | NaN | NaN | NaN | 396.61 | 649.934 | NaN | 30.6983 | NaN | 20.5091
96.1292 | 11.3686 | 11.3205 | 11.3873 | 11.6952 | 11.1694 | 11.6692 | 11.4715 | 11.2662 | NaN | NaN | NaN | 11.6081 | 90.1683 | NaN | NaN | NaN | -14.3946 | NaN | NaN | NaN | 395.0142 | 651.2601 | NaN | 29.9186 | NaN | 22.4952
97.1292 | 11.5588 | 11.5823 | 11.3879 | 11.6951 | 11.1327 | 11.8995 | 11.5858 | 11.2623 | NaN | NaN | NaN | 11.5846 | 93.0721 | NaN | NaN | NaN | -18.435 | NaN | NaN | NaN | 390.1569 | 649.0432 | NaN | 30.4099 | NaN | 25.9071
98.1292 | 11.3734 | 11.4291 | 11.3877 | 11.6844 | 10.9549 | 11.7666 | 11.4983 | 11.2645 | NaN | NaN | NaN | 11.5556 | 91.9003 | NaN | NaN | NaN | -17.2399 | NaN | NaN | NaN | 387.4078 | 647.7736 | NaN | 30.2027 | NaN | 22.4474
99.1292 | 11.4167 | 11.3412 | 11.3929 | 11.6676 | 11.0589 | 11.773 | 11.4963 | 11.2589 | NaN | NaN | NaN | 11.6433 | 91.9087 | NaN | NaN | NaN | -7.078 | NaN | NaN | NaN | 384.9738 | 647.219 | NaN | 29.6353 | NaN | 27.443
100.1292 | 11.3202 | 11.4072 | 11.3894 | 11.7243 | 11.045 | 11.8925 | 11.5195 | 11.2629 | NaN | NaN | NaN | 11.6459 | 93.3378 | NaN | NaN | NaN | -13.2728 | NaN | NaN | NaN | 382.8059 | 644.6977 | NaN | 30.776 | NaN | 21.4581
101.1292 | 11.336 | 11.3631 | 11.3931 | 11.7354 | 11.0811 | 11.7861 | 11.5175 | 11.2627 | NaN | NaN | NaN | 11.7899 | 93.4086 | NaN | NaN | NaN | 2.5798 | NaN | NaN | NaN | 380.3573 | 642.527 | NaN | 28.8396 | NaN | 24.3509
102.1292 | 11.3488 | 11.4138 | 11.3906 | 11.7076 | 11.1223 | 11.7578 | 11.5319 | 11.2642 | NaN | NaN | NaN | 11.626 | 91.9553 | NaN | NaN | NaN | 1.0867 | NaN | NaN | NaN | 378.2824 | 641.7485 | NaN | 29.4319 | NaN | 21.0734
103.1292 | 11.4672 | 11.4439 | 11.3958 | 11.7018 | 11.0986 | 11.8272 | 11.5414 | 11.2628 | NaN | NaN | NaN | 11.7026 | 92.1239 | NaN | NaN | NaN | -2.161 | NaN | NaN | NaN | 374.7108 | 640.1163 | NaN | 30.7947 | NaN | 23.8948
104.1292 | 11.4154 | 11.283 | 11.386 | 11.8002 | 11.0449 | 11.7542 | 11.5009 | 11.2616 | NaN | NaN | NaN | 11.6451 | 93.8046 | NaN | NaN | NaN | -9.0471 | NaN | NaN | NaN | 371.4348 | 639.9331 | NaN | 29.7022 | NaN | 23.7437
105.1292 | 11.6567 | 11.2703 | 11.3948 | 11.712 | 11.0142 | 11.73 | 11.4805 | 11.2582 | NaN | NaN | NaN | 11.7044 | 92.3665 | NaN | NaN | NaN | -17.9779 | NaN | NaN | NaN | 369.6093 | 640.8593 | NaN | 28.4886 | NaN | 25.5943
106.1292 | 11.3629 | 11.2966 | 11.3853 | 11.7233 | 11.0378 | 11.7616 | 11.5119 | 11.2587 | NaN | NaN | NaN | 11.7076 | 91.6521 | NaN | NaN | NaN | 6.7483 | NaN | NaN | NaN | 366.7214 | 639.3261 | NaN | 29.27 | NaN | 25.7554
107.1292 | 11.3827 | 11.9353 | 11.3939 | 11.8408 | 11.0512 | 11.9486 | 11.6962 | 11.2597 | NaN | NaN | NaN | 11.6776 | 92.3669 | NaN | NaN | NaN | 2.1259 | NaN | NaN | NaN | 362.3049 | 636.7338 | NaN | 28.969 | NaN | 21.8229
108.1292 | 11.3121 | 11.3662 | 11.3942 | 11.7339 | 11.097 | 11.7163 | 11.4883 | 11.2686 | NaN | NaN | NaN | 11.6623 | 91.216 | NaN | NaN | NaN | -17.8651 | NaN | NaN | NaN | 361.4085 | 635.3341 | NaN | 27.5377 | NaN | 28.3675
109.1292 | 11.3531 | 11.5122 | 11.3954 | 11.7033 | 11.1073 | 11.85 | 11.536 | 11.2683 | NaN | NaN | NaN | 11.7265 | 95.1414 | NaN | NaN | NaN | -14.9247 | NaN | NaN | NaN | 359.0119 | 635.3152 | NaN | 28.3807 | NaN | 22.5726
110.1292 | 11.4592 | 11.4132 | 11.4011 | 11.6938 | 11.1061 | 11.7325 | 11.5224 | 11.2657 | NaN | NaN | NaN | 11.5807 | 90.7455 | NaN | NaN | NaN | -6.2978 | NaN | NaN | NaN | 356.2167 | 633.3003 | NaN | 29.941 | NaN | 25.6042
111.1292 | 11.3954 | 11.3151 | 11.4009 | 11.702 | 11.0911 | 11.7421 | 11.4969 | 11.2612 | NaN | NaN | NaN | 11.6473 | 91.767 | NaN | NaN | NaN | -12.0978 | NaN | NaN | NaN | 353.3574 | 634.0118 | NaN | 30.8665 | NaN | 24.2011
112.1292 | 11.3468 | 11.4783 | 11.3963 | 11.6875 | 11.1242 | 11.8471 | 11.5266 | 11.2656 | NaN | NaN | NaN | 11.7112 | 92.5884 | NaN | NaN | NaN | -8.9472 | NaN | NaN | NaN | 349.8831 | 630.9212 | NaN | 29.5206 | NaN | 21.2846
113.1292 | 11.368 | 11.4094 | 11.3974 | 11.6948 | 11.1081 | 11.7694 | 11.5373 | 11.2565 | NaN | NaN | NaN | 11.6137 | 94.4377 | NaN | NaN | NaN | -12.8333 | NaN | NaN | NaN | 346.9419 | 629.3808 | NaN | 29.3313 | NaN | 21.6586
114.1292 | 11.338 | 11.3451 | 11.4035 | 11.7069 | 11.0939 | 11.7673 | 11.5021 | 11.263 | NaN | NaN | NaN | 11.5825 | 91.4609 | NaN | NaN | NaN | -10.481 | NaN | NaN | NaN | 345.5585 | 627.4468 | NaN | 30.2471 | NaN | 21.0625
115.1292 | 11.3148 | 11.2904 | 11.396 | 11.7979 | 11.1444 | 11.7087 | 11.4934 | 11.2608 | NaN | NaN | NaN | 11.6486 | 94.2351 | NaN | NaN | NaN | -4.6879 | NaN | NaN | NaN | 344.1016 | 622.5774 | NaN | 29.4935 | NaN | 29.3518
116.1292 | 11.358 | 11.3489 | 11.4037 | 11.7474 | 11.1867 | 11.6704 | 11.4937 | 11.2575 | NaN | NaN | NaN | 11.6961 | 90.0933 | NaN | NaN | NaN | -11.5394 | NaN | NaN | NaN | 340.7536 | 623.1052 | NaN | 29.3251 | NaN | 25.3108
117.1292 | 11.3771 | 11.5063 | 11.4029 | 11.6597 | 11.0216 | 11.8021 | 11.5187 | 11.256 | NaN | NaN | NaN | 11.6223 | 94.3626 | NaN | NaN | NaN | -14.5358 | NaN | NaN | NaN | 338.2838 | 624.0787 | NaN | 30.816 | NaN | 24.7129
118.1292 | 11.3931 | 11.5868 | 11.4026 | 11.6848 | 11.0802 | 11.7402 | 11.5588 | 11.256 | NaN | NaN | NaN | 11.6225 | 93.4281 | NaN | NaN | NaN | -18.1676 | NaN | NaN | NaN | 337.2912 | 620.5854 | NaN | 27.6909 | NaN | 27.5354
119.1292 | 11.3194 | 11.4616 | 11.3989 | 11.6734 | 11.0275 | 11.7449 | 11.556 | 11.2619 | NaN | NaN | NaN | 11.6439 | 94.1412 | NaN | NaN | NaN | -2.7519 | NaN | NaN | NaN | 336.2071 | 620.0549 | NaN | 31.4447 | NaN | 26.5517
120.1292 | 11.3537 | 11.4186 | 11.4032 | 12.0118 | 11.1788 | 11.8728 | 11.5361 | 11.2592 | NaN | NaN | NaN | 11.7131 | 90.9917 | NaN | NaN | NaN | -8.5254 | NaN | NaN | NaN | 333.7539 | 620.3755 | NaN | 29.9223 | NaN | 19.7011
121.1292 | 11.5759 | 11.379 | 11.4016 | 11.7212 | 11.0662 | 11.7901 | 11.5207 | 11.2578 | NaN | NaN | NaN | 11.6831 | 92.7466 | NaN | NaN | NaN | -17.2751 | NaN | NaN | NaN | 331.8236 | 617.3978 | NaN | 29.8293 | NaN | 25.143
122.1292 | 11.4554 | 11.4581 | 11.4002 | 11.6843 | 11.1695 | 11.8025 | 11.5182 | 11.2615 | NaN | NaN | NaN | 11.6777 | 93.8264 | NaN | NaN | NaN | -6.245 | NaN | NaN | NaN | 329.7982 | 621.2007 | NaN | 32.4304 | NaN | 22.1723
123.1292 | 11.428 | 11.5971 | 11.4 | 11.8068 | 11.1124 | 11.8761 | 11.5798 | 11.2534 | NaN | NaN | NaN | 11.5784 | 92.6491 | NaN | NaN | NaN | -3.2328 | NaN | NaN | NaN | 326.896 | 621.2882 | NaN | 30.4471 | NaN | 23.3139
124.1292 | 11.349 | 11.3186 | 11.4037 | 11.66 | 11.1779 | 11.7121 | 11.5039 | 11.258 | NaN | NaN | NaN | 11.6512 | 91.6594 | NaN | NaN | NaN | 4.0151 | NaN | NaN | NaN | 326.6266 | 621.5833 | NaN | 29.7633 | NaN | 22.8353
125.1292 | 11.3654 | 11.293 | 11.3943 | 11.6994 | 11.0556 | 11.7572 | 11.497 | 11.2546 | NaN | NaN | NaN | 11.6763 | 95.755 | NaN | NaN | NaN | -15.1177 | NaN | NaN | NaN | 323.9967 | 621.2008 | NaN | 28.3155 | NaN | 25.7976
126.1292 | 11.3427 | 11.3689 | 11.3981 | 11.722 | 11.1126 | 11.8408 | 11.5287 | 11.2577 | NaN | NaN | NaN | 11.697 | 102.8113 | NaN | NaN | NaN | -17.422 | NaN | NaN | NaN | 322.0079 | 619.2191 | NaN | 29.4791 | NaN | 21.5293
127.1292 | 11.3109 | 11.6395 | 11.3993 | 11.7108 | 11.1714 | 11.9408 | 11.6604 | 11.2577 | NaN | NaN | NaN | 11.6228 | 91.0151 | NaN | NaN | NaN | -16.6984 | NaN | NaN | NaN | 320.7417 | 618.8165 | NaN | 28.8568 | NaN | 26.9869
128.1292 | 11.3685 | 11.4169 | 11.3994 | 11.7059 | 11.1046 | 11.8141 | 11.5285 | 11.2508 | NaN | NaN | NaN | 11.6097 | 93.4335 | NaN | NaN | NaN | -16.9559 | NaN | NaN | NaN | 320.2293 | 619.3938 | NaN | 28.3982 | NaN | 25.0716
129.1292 | 11.3879 | 11.2964 | 11.4047 | 11.6532 | 11.0208 | 11.6902 | 11.4746 | 11.2501 | NaN | NaN | NaN | 11.615 | 91.5637 | NaN | NaN | NaN | -18.6039 | NaN | NaN | NaN | 318.1607 | 618.6015 | NaN | 29.8694 | NaN | 25.901
130.1292 | 11.3917 | 11.5269 | 11.3979 | 12.0161 | 11.0348 | 11.8582 | 11.5688 | 11.2553 | NaN | NaN | NaN | 11.6973 | 92.6997 | NaN | NaN | NaN | -19.5749 | NaN | NaN | NaN | 315.4516 | 616.8219 | NaN | 28.23 | NaN | 23.1923
131.1292 | 11.4502 | 11.3391 | 11.4077 | 11.7639 | 11.1533 | 11.7188 | 11.4951 | 11.2554 | NaN | NaN | NaN | 11.6751 | 94.0606 | NaN | NaN | NaN | -17.5595 | NaN | NaN | NaN | 314.0865 | 615.6762 | NaN | 27.3485 | NaN | 22.4393
132.1292 | 11.612 | 11.3349 | 11.3981 | 11.6824 | 10.9917 | 11.759 | 11.5174 | 11.2528 | NaN | NaN | NaN | 11.5606 | 93.8399 | NaN | NaN | NaN | 0.1002 | NaN | NaN | NaN | 311.5381 | 617.0099 | NaN | 31.6054 | NaN | 26.5464
133.1292 | 11.3381 | 11.301 | 11.4025 | 11.6809 | 11.1118 | 11.7019 | 11.4847 | 11.2581 | NaN | NaN | NaN | 11.5983 | 93.5788 | NaN | NaN | NaN | -13.4198 | NaN | NaN | NaN | 311.407 | 616.5137 | NaN | 29.7716 | NaN | 23.1742
134.1292 | 11.3946 | 11.4482 | 11.4035 | 11.6873 | 11.1825 | 11.8364 | 11.5124 | 11.2538 | NaN | NaN | NaN | 11.636 | 92.0873 | NaN | NaN | NaN | 1.2735 | NaN | NaN | NaN | 309.1339 | 615.4093 | NaN | 30.0169 | NaN | 25.2419
135.1292 | 11.4331 | 11.4442 | 11.4004 | 11.7918 | 11.1538 | 11.8965 | 11.5515 | 11.2542 | NaN | NaN | NaN | 11.5692 | 94.3298 | NaN | NaN | NaN | -19.443 | NaN | NaN | NaN | 306.969 | 615.2201 | NaN | 29.3075 | NaN | 22.5066
136.1292 | 11.3508 | 11.5159 | 11.4 | 11.7779 | 11.0876 | 12.1067 | 11.5256 | 11.2474 | NaN | NaN | NaN | 11.55 | 91.8567 | NaN | NaN | NaN | -6.7779 | NaN | NaN | NaN | 305.5303 | 617.123 | NaN | 29.8002 | NaN | 23.7238
137.1292 | 11.3599 | 11.5102 | 11.3962 | 11.7018 | 11.0451 | 11.8394 | 11.5741 | 11.2463 | NaN | NaN | NaN | 11.7185 | 91.3238 | NaN | NaN | NaN | 6.7592 | NaN | NaN | NaN | 303.2702 | 617.1482 | NaN | 29.9378 | NaN | 25.6052
138.1292 | 11.4107 | 11.4275 | 11.3961 | 11.6444 | 11.103 | 11.7676 | 11.5186 | 11.2423 | NaN | NaN | NaN | 11.6117 | 91.0235 | NaN | NaN | NaN | -14.2067 | NaN | NaN | NaN | 301.5795 | 614.4365 | NaN | 29.3623 | NaN | 21.8128
139.1292 | 11.8824 | 11.2366 | 11.4002 | 11.7439 | 11.1056 | 11.6645 | 11.4549 | 11.2397 | NaN | NaN | NaN | 11.6528 | 94.6953 | NaN | NaN | NaN | -11.8698 | NaN | NaN | NaN | 298.8021 | 614.7933 | NaN | 29.4207 | NaN | 26.4051
140.1448 | 11.4342 | 11.4773 | 11.3903 | 11.6867 | 11.1444 | 11.7844 | 11.5247 | 11.2384 | NaN | NaN | NaN | 11.5438 | 93.1513 | NaN | NaN | NaN | -0.601 | NaN | NaN | NaN | 297.0213 | 614.4281 | NaN | 31.6952 | NaN | 20.0591
141.1292 | 11.3317 | 11.3288 | 11.3931 | 11.7218 | 11.1437 | 11.7255 | 11.4922 | 11.2377 | NaN | NaN | NaN | 11.5667 | 91.5503 | NaN | NaN | NaN | -18.6659 | NaN | NaN | NaN | 295.8464 | 615.4411 | NaN | 30.215 | NaN | 21.4779
142.1292 | 11.5111 | 11.3391 | 11.3908 | 11.7378 | 11.1629 | 11.779 | 11.5049 | 11.2367 | NaN | NaN | NaN | 11.6042 | 95.6322 | NaN | NaN | NaN | 7.5857 | NaN | NaN | NaN | 293.4448 | 613.0814 | NaN | 27.7596 | NaN | 19.0982
143.1292 | 11.3117 | 11.3176 | 11.3896 | 11.7409 | 11.1373 | 11.725 | 11.4922 | 11.2386 | NaN | NaN | NaN | 11.6171 | 93.2507 | NaN | NaN | NaN | -9.8004 | NaN | NaN | NaN | 292.4466 | 611.7324 | NaN | 28.3996 | NaN | 20.8508
144.1292 | 11.4076 | 11.3691 | 11.3862 | 11.6709 | 10.9882 | 11.8297 | 11.5175 | 11.2309 | NaN | NaN | NaN | 11.5919 | 92.211 | NaN | NaN | NaN | -18.4802 | NaN | NaN | NaN | 286.9392 | 612.8953 | NaN | 30.7704 | NaN | 24.9007
145.1292 | 11.3443 | 11.3454 | 11.3835 | 11.6771 | 11.1297 | 11.7805 | 11.4971 | 11.2368 | NaN | NaN | NaN | 11.5943 | 92.262 | NaN | NaN | NaN | -9.8834 | NaN | NaN | NaN | 285.8579 | 613.1682 | NaN | 29.2484 | NaN | 25.6967
146.1292 | 11.3373 | 11.3138 | 11.3767 | 11.6686 | 11.1211 | 11.7716 | 11.4977 | 11.2336 | NaN | NaN | NaN | 11.6715 | 95.0743 | NaN | NaN | NaN | -14.8872 | NaN | NaN | NaN | 282.1464 | 611.3124 | NaN | 30.3829 | NaN | 25.7794
147.1292 | 11.34 | 11.333 | 11.3804 | 11.7358 | 11.1331 | 11.7695 | 11.4935 | 11.2342 | NaN | NaN | NaN | 11.6074 | 95.4443 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 280.6819 | 611.5339 | NaN | 29.3842 | NaN | 25.4741
148.1292 | 11.4346 | 11.3491 | 11.375 | 11.7908 | 11.1618 | 11.8393 | 11.5029 | 11.234 | NaN | NaN | NaN | 11.5984 | 94.9305 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 276.8166 | 612.9681 | NaN | 29.3029 | NaN | 23.8533
149.1292 | 11.2886 | 11.4437 | 11.3687 | 11.7575 | 11.0619 | 11.8185 | 11.536 | 11.2266 | NaN | NaN | NaN | 11.5637 | 92.5546 | NaN | NaN | NaN | -12.0331 | NaN | NaN | NaN | 275.3496 | 613.8102 | NaN | 29.5228 | NaN | 24.0823
150.1292 | 11.4086 | 11.5429 | 11.3735 | 11.6877 | 11.1322 | 11.7794 | 11.5702 | 11.2297 | NaN | NaN | NaN | 11.6409 | 91.0176 | NaN | NaN | NaN | -12.3611 | NaN | NaN | NaN | 271.8421 | 612.6321 | NaN | 29.2904 | NaN | 27.9375
151.1292 | 11.3694 | 11.3734 | 11.3685 | 12.0836 | 11.088 | 11.7995 | 11.5173 | 11.2338 | NaN | NaN | NaN | 11.6827 | 93.2081 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 269.0748 | 613.3482 | NaN | 28.8225 | NaN | 21.3923
152.1292 | 11.3463 | 11.3085 | 11.3717 | 11.7195 | 11.0117 | 11.7045 | 11.4829 | 11.2382 | NaN | NaN | NaN | 11.6773 | 92.2368 | NaN | NaN | NaN | -6.8935 | NaN | NaN | NaN | 267.7259 | 612.0282 | NaN | 27.6224 | NaN | 22.1504
153.1292 | 11.3385 | 11.2967 | 11.3732 | 11.7038 | 11.0705 | 11.7513 | 11.4873 | 11.2272 | NaN | NaN | NaN | 11.6207 | 88.6025 | NaN | NaN | NaN | 0.3683 | NaN | NaN | NaN | 264.9618 | 613.827 | NaN | 29.9828 | NaN | 22.4086
154.1292 | 11.3253 | 11.6262 | 11.3704 | 11.6452 | 10.9691 | 11.7916 | 11.5421 | 11.2364 | NaN | NaN | NaN | 11.607 | 92.1574 | NaN | NaN | NaN | -19.4828 | NaN | NaN | NaN | 262.3241 | 612.7015 | NaN | 29.2332 | NaN | 26.2379
155.1292 | 11.356 | 11.47 | 11.3694 | 11.6714 | 11.0017 | 11.7681 | 11.5458 | 11.2306 | NaN | NaN | NaN | 11.6487 | 93.4393 | NaN | NaN | NaN | -15.9067 | NaN | NaN | NaN | 260.6523 | 612.1073 | NaN | 27.6861 | NaN | 25.4906
156.1292 | 11.3859 | 11.3089 | 11.3676 | 11.8046 | 11.2148 | 11.7648 | 11.4917 | 11.229 | NaN | NaN | NaN | 11.6796 | 96.7546 | NaN | NaN | NaN | -15.6206 | NaN | NaN | NaN | 259.3231 | 611.7586 | NaN | 29.8204 | NaN | 23.5435
157.1292 | 11.4164 | 11.3122 | 11.3703 | 11.6978 | 11.0908 | 11.769 | 11.4899 | 11.2316 | NaN | NaN | NaN | 11.657 | 93.3479 | NaN | NaN | NaN | -18.4603 | NaN | NaN | NaN | 257.5608 | 611.0446 | NaN | 30.4549 | NaN | 26.4218
158.1292 | 11.3355 | 11.2659 | 11.3718 | 11.8516 | 11.211 | 11.6881 | 11.463 | 11.2319 | NaN | NaN | NaN | 11.6392 | 94.0395 | NaN | NaN | NaN | -19.6726 | NaN | NaN | NaN | 256.6497 | 611.1565 | NaN | 30.4458 | NaN | 26.411
159.1292 | 11.2792 | 11.2872 | 11.368 | 11.7263 | 11.0835 | 11.8455 | 11.4962 | 11.2278 | NaN | NaN | NaN | 11.6925 | 92.3274 | NaN | NaN | NaN | -18.1001 | NaN | NaN | NaN | 252.7484 | 610.3687 | NaN | 29.6504 | NaN | 25.2215
160.1292 | 11.3472 | 11.3519 | 11.3685 | 11.7301 | 11.0262 | 11.7075 | 11.4829 | 11.2333 | NaN | NaN | NaN | 11.6528 | 94.8262 | NaN | NaN | NaN | -17.9893 | NaN | NaN | NaN | 252.07 | 610.0034 | NaN | 30.5025 | NaN | 27.2196
161.1292 | 11.4227 | 11.4352 | 11.3757 | 11.8046 | 11.1293 | 11.8396 | 11.5301 | 11.2345 | NaN | NaN | NaN | 11.5547 | 92.5209 | NaN | NaN | NaN | -5.1564 | NaN | NaN | NaN | 249.2456 | 610.1046 | NaN | 28.6986 | NaN | 21.5388
162.1292 | 11.4028 | 11.5774 | 11.3751 | 11.7258 | 11.0746 | 11.7941 | 11.5348 | 11.2344 | NaN | NaN | NaN | 11.6317 | 93.3293 | NaN | NaN | NaN | -14.6882 | NaN | NaN | NaN | 247.0621 | 609.8872 | NaN | 28.785 | NaN | 27.0507
163.1292 | 11.3087 | 11.3273 | 11.3752 | 11.7733 | 11.0223 | 11.8001 | 11.5153 | 11.2278 | NaN | NaN | NaN | 11.7082 | 92.3474 | NaN | NaN | NaN | -18.6427 | NaN | NaN | NaN | 245.098 | 610.8571 | NaN | 29.8634 | NaN | 25.3138
164.1292 | 11.3286 | 11.6016 | 11.3688 | 11.7025 | 10.9985 | 11.9979 | 11.6137 | 11.2276 | NaN | NaN | NaN | 11.6722 | 95.9798 | NaN | NaN | NaN | -16.2295 | NaN | NaN | NaN | 241.1661 | 609.2346 | NaN | 29.3003 | NaN | 25.9342
165.1292 | 11.3642 | 11.5835 | 11.3662 | 11.6774 | 11.0935 | 11.911 | 11.5662 | 11.2286 | NaN | NaN | NaN | 11.5865 | 94.0584 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 239.4469 | 609.4755 | NaN | 29.3495 | NaN | 22.8378
166.1292 | 11.5067 | 11.2676 | 11.3658 | 11.8053 | 11.056 | 11.7287 | 11.4826 | 11.2268 | NaN | NaN | NaN | 11.7055 | 93.9483 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 238.3008 | 611.0493 | NaN | 29.9857 | NaN | 26.3402
167.1292 | 11.3851 | 11.2428 | 11.3775 | 11.6738 | 11.0598 | 11.6638 | 11.4508 | 11.2271 | NaN | NaN | NaN | 11.6674 | 92.7328 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 237.9458 | 609.7211 | NaN | 29.5339 | NaN | 21.9192
168.1292 | 11.4538 | 11.347 | 11.3683 | 11.7102 | 11.0625 | 11.7921 | 11.5142 | 11.2289 | NaN | NaN | NaN | 11.5849 | 92.5511 | NaN | NaN | NaN | -9.3046 | NaN | NaN | NaN | 234.3542 | 609.7302 | NaN | 29.2933 | NaN | 23.6207
169.1292 | 11.403 | 11.2864 | 11.3775 | 11.7064 | 11.1271 | 11.8574 | 11.4942 | 11.2278 | NaN | NaN | NaN | 11.6454 | 92.3275 | NaN | NaN | NaN | -19.8726 | NaN | NaN | NaN | 231.8878 | 607.3134 | NaN | 30.8756 | NaN | 26.4567
170.1292 | 11.2758 | 11.4789 | 11.375 | 11.7297 | 11.1067 | 11.995 | 11.5836 | 11.2333 | NaN | NaN | NaN | 11.635 | 93.8505 | NaN | NaN | NaN | -7.8143 | NaN | NaN | NaN | 230.3663 | 607.5173 | NaN | 27.8627 | NaN | 18.409
171.1292 | 11.4067 | 11.3985 | 11.3795 | 11.7225 | 11.1231 | 11.739 | 11.5175 | 11.2286 | NaN | NaN | NaN | 11.6046 | 89.6254 | NaN | NaN | NaN | 1.5154 | NaN | NaN | NaN | 229.6868 | 604.6506 | NaN | 30.1257 | NaN | 25.9486
172.1292 | 11.5713 | 11.7406 | 11.371 | 11.661 | 10.8865 | 11.8153 | 11.6379 | 11.2353 | NaN | NaN | NaN | 11.6694 | 92.9053 | NaN | NaN | NaN | -0.9506 | NaN | NaN | NaN | 226.2284 | 603.9289 | NaN | 31.4363 | NaN | 22.11
173.1292 | 11.3095 | 11.1927 | 11.3697 | 11.6972 | 11.1126 | 11.6173 | 11.4368 | 11.2364 | NaN | NaN | NaN | 11.6772 | 91.907 | NaN | NaN | NaN | -8.3615 | NaN | NaN | NaN | 227.7744 | 604.2466 | NaN | 29.0939 | NaN | 27.8221
174.1292 | 11.3851 | 11.4027 | 11.3742 | 11.7506 | 11.0411 | 11.8652 | 11.5281 | 11.2359 | NaN | NaN | NaN | 11.5971 | 92.1575 | NaN | NaN | NaN | -13.4767 | NaN | NaN | NaN | 222.9979 | 601.8911 | NaN | 29.2065 | NaN | 25.4887
175.1292 | 11.3357 | 11.405 | 11.3696 | 11.6763 | 11.0937 | 11.7919 | 11.5381 | 11.2337 | NaN | NaN | NaN | 11.6804 | 92.7419 | NaN | NaN | NaN | 1.9738 | NaN | NaN | NaN | 220.9011 | 601.8113 | NaN | 31.2221 | NaN | 27.8223
176.1292 | 11.4109 | 11.3387 | 11.382 | 11.6723 | 11.1942 | 11.6711 | 11.4668 | 11.237 | NaN | NaN | NaN | 11.7955 | 93.5219 | NaN | NaN | NaN | -17.0487 | NaN | NaN | NaN | 220.1771 | 601.6681 | NaN | 29.2081 | NaN | 22.7558
177.1292 | 11.3406 | 11.2457 | 11.3812 | 11.7101 | 11.0952 | 11.6935 | 11.4681 | 11.2401 | NaN | NaN | NaN | 11.6386 | 91.3948 | NaN | NaN | NaN | -11.9684 | NaN | NaN | NaN | 218.4084 | 603.2023 | NaN | 29.9653 | NaN | 21.7039
178.1292 | 11.4164 | 11.244 | 11.384 | 11.7234 | 11.1443 | 11.6829 | 11.4525 | 11.2357 | NaN | NaN | NaN | 11.7383 | 91.6986 | NaN | NaN | NaN | 0.9374 | NaN | NaN | NaN | 216.5649 | 599.6747 | NaN | 29.7827 | NaN | 21.2871
179.1292 | 11.2923 | 11.2546 | 11.3767 | 11.6786 | 11.0288 | 11.6572 | 11.4621 | 11.2446 | NaN | NaN | NaN | 11.5698 | 93.6883 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 214.3724 | 601.4028 | NaN | 29.5744 | NaN | 25.6281
180.1292 | 11.4562 | 11.3468 | 11.3811 | 11.7014 | 11.0184 | 11.7845 | 11.5128 | 11.2414 | NaN | NaN | NaN | 11.573 | 91.5446 | NaN | NaN | NaN | -8.7489 | NaN | NaN | NaN | 210.6608 | 600.1713 | NaN | 30.3052 | NaN | 28.0131
181.1292 | 11.3323 | 11.3869 | 11.3791 | 11.9152 | 11.0955 | 11.9136 | 11.5223 | 11.2473 | NaN | NaN | NaN | 11.5913 | 93.8151 | NaN | NaN | NaN | -9.9203 | NaN | NaN | NaN | 208.2864 | 599.2356 | NaN | 31.2869 | NaN | 21.2824
182.1292 | 11.3145 | 11.3634 | 11.3785 | 11.9812 | 10.9366 | 11.8307 | 11.5306 | 11.2441 | NaN | NaN | NaN | 11.5841 | 92.9174 | NaN | NaN | NaN | 6.7003 | NaN | NaN | NaN | 206.4093 | 602.2201 | NaN | 29.1155 | NaN | 24.5667
183.1292 | 11.34 | 11.3027 | 11.3723 | 11.7084 | 11.0982 | 11.7127 | 11.4981 | 11.2459 | NaN | NaN | NaN | 11.6174 | 91.598 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 205.5147 | 600.7082 | NaN | 29.4193 | NaN | 24.9701
184.1292 | 11.2998 | 11.3444 | 11.3774 | 11.7854 | 11.037 | 11.768 | 11.509 | 11.2372 | NaN | NaN | NaN | 11.6947 | 92.7283 | NaN | NaN | NaN | 3.8209 | NaN | NaN | NaN | 202.3526 | 600.2664 | NaN | 29.3095 | NaN | 20.0231
185.1292 | 11.3666 | 11.5994 | 11.3769 | 11.7099 | 11.0472 | 11.9604 | 11.5373 | 11.2477 | NaN | NaN | NaN | 11.5483 | 92.1829 | NaN | NaN | NaN | -3.3793 | NaN | NaN | NaN | 197.356 | 596.9959 | NaN | 30.7725 | NaN | 24.9175
186.1292 | 11.3214 | 11.3566 | 11.379 | 11.7294 | 10.9487 | 11.7939 | 11.5169 | 11.2435 | NaN | NaN | NaN | 11.7361 | 91.6951 | NaN | NaN | NaN | -11.5533 | NaN | NaN | NaN | 195.757 | 597.7408 | NaN | 30.4571 | NaN | 26.8897
187.1292 | 11.3165 | 11.3021 | 11.3739 | 11.846 | 11.1414 | 11.6837 | 11.477 | 11.242 | NaN | NaN | NaN | 11.6229 | 93.8624 | NaN | NaN | NaN | -8.0439 | NaN | NaN | NaN | 194.6909 | 597.0027 | NaN | 29.2124 | NaN | 23.4041
188.1292 | 11.509 | 11.4063 | 11.3704 | 11.7241 | 11.0345 | 11.8266 | 11.5298 | 11.2469 | NaN | NaN | NaN | 11.6339 | 92.0305 | NaN | NaN | NaN | -16.3877 | NaN | NaN | NaN | 189.932 | 597.1169 | NaN | 29.9603 | NaN | 23.7823
189.1292 | 11.5963 | 11.6377 | 11.3669 | 11.6851 | 11.1705 | 11.752 | 11.6025 | 11.2503 | NaN | NaN | NaN | 11.5681 | 94.5673 | NaN | NaN | NaN | -12.6119 | NaN | NaN | NaN | 188.0833 | 597.5478 | NaN | 30.2437 | NaN | 18.7917
190.1292 | 11.3574 | 11.376 | 11.3644 | 11.7131 | 11.0149 | 11.7932 | 11.5222 | 11.2521 | NaN | NaN | NaN | 11.5886 | 95.014 | NaN | NaN | NaN | -17.8299 | NaN | NaN | NaN | 185.4971 | 598.4929 | NaN | 30.3595 | NaN | 26.4975
191.1292 | 11.4283 | 11.3776 | 11.3696 | 11.9567 | 11.1481 | 11.9158 | 11.5059 | 11.2521 | NaN | NaN | NaN | 11.5818 | 91.7275 | NaN | NaN | NaN | 4.5922 | NaN | NaN | NaN | 182.7552 | 599.1242 | NaN | 29.8135 | NaN | 27.9207
192.1292 | 11.2486 | 11.418 | 11.3663 | 11.7898 | 11.0338 | 11.809 | 11.5346 | 11.2534 | NaN | NaN | NaN | 11.5518 | 91.5288 | NaN | NaN | NaN | -17.8669 | NaN | NaN | NaN | 182.7353 | 599.3979 | NaN | 29.0289 | NaN | 23.0089
193.1292 | 11.3706 | 11.4357 | 11.3661 | 11.7328 | 11.1374 | 11.9248 | 11.5265 | 11.2484 | NaN | NaN | NaN | 11.6299 | 93.1945 | NaN | NaN | NaN | -2.2874 | NaN | NaN | NaN | 179.6603 | 598.0237 | NaN | 28.9355 | NaN | 22.0956
194.1292 | 11.3112 | 11.5761 | 11.3709 | 11.6717 | 11.0539 | 11.9826 | 11.6077 | 11.2467 | NaN | NaN | NaN | 11.6192 | 92.2745 | NaN | NaN | NaN | 8.5485 | NaN | NaN | NaN | 177.0949 | 600.018 | NaN | 29.2648 | NaN | 25.8207
195.1292 | 11.2852 | 11.293 | 11.3624 | 11.7023 | 11.0843 | 11.8546 | 11.4937 | 11.2446 | NaN | NaN | NaN | 11.5782 | 92.604 | NaN | NaN | NaN | -14.859 | NaN | NaN | NaN | 174.944 | 600.7581 | NaN | 31.5668 | NaN | 28.0003
196.1292 | 11.3283 | 11.4428 | 11.3597 | 11.7158 | 11.1759 | 11.8047 | 11.5275 | 11.2464 | NaN | NaN | NaN | 11.5977 | 93.0232 | NaN | NaN | NaN | -19.4824 | NaN | NaN | NaN | 171.753 | 600.9052 | NaN | 29.906 | NaN | 22.7483
197.1292 | 11.4376 | 11.3643 | 11.3622 | 11.6912 | 11.0896 | 11.7726 | 11.5074 | 11.2459 | NaN | NaN | NaN | 11.6196 | 91.1493 | NaN | NaN | NaN | -16.1642 | NaN | NaN | NaN | 167.8558 | 600.7804 | NaN | 29.3432 | NaN | 23.2457
198.1292 | 11.442 | 11.4677 | 11.3688 | 11.7199 | 11.0969 | 11.7992 | 11.5425 | 11.2465 | NaN | NaN | NaN | 11.5499 | 93.0881 | NaN | NaN | NaN | -0.0137 | NaN | NaN | NaN | 164.7904 | 597.2751 | NaN | 30.1299 | NaN | 24.7765
199.1292 | 11.3248 | 11.2816 | 11.3662 | 11.776 | 11.1127 | 11.784 | 11.4853 | 11.2508 | NaN | NaN | NaN | 11.6042 | 92.0493 | NaN | NaN | NaN | -18.1072 | NaN | NaN | NaN | 161.1095 | 598.772 | NaN | 29.1685 | NaN | 25.1975
200.1292 | 11.3412 | 11.5063 | 11.3632 | 11.6804 | 11.0743 | 11.8182 | 11.5246 | 11.2483 | NaN | NaN | NaN | 11.5933 | 92.8954 | NaN | NaN | NaN | -7.7101 | NaN | NaN | NaN | 156.1624 | 598.5418 | NaN | 29.7456 | NaN | 23.6979
201.1292 | 11.8083 | 11.3322 | 11.3705 | 11.7178 | 10.9481 | 11.7773 | 11.5006 | 11.2489 | NaN | NaN | NaN | 11.5498 | 95.214 | NaN | NaN | NaN | -13.2932 | NaN | NaN | NaN | 151.2256 | 598.0453 | NaN | 30.4913 | NaN | 26.3766
202.1292 | 11.4011 | 11.5084 | 11.3625 | 11.6678 | 10.9411 | 11.9025 | 11.543 | 11.2428 | NaN | NaN | NaN | 11.6031 | 93.1656 | NaN | NaN | NaN | -18.5489 | NaN | NaN | NaN | 145.0179 | 596.8404 | NaN | 28.073 | NaN | 24.6262
203.1292 | 11.3448 | 11.3361 | 11.3742 | 11.6709 | 11.1403 | 11.7602 | 11.5083 | 11.2493 | NaN | NaN | NaN | 11.5926 | 93.365 | NaN | NaN | NaN | -0.7091 | NaN | NaN | NaN | 139.304 | 596.5576 | NaN | 28.4819 | NaN | 16.5359
204.1292 | 11.3592 | 11.3656 | 11.3671 | 11.7104 | 11.1122 | 11.8078 | 11.517 | 11.2541 | NaN | NaN | NaN | 11.6603 | 91.9742 | NaN | NaN | NaN | -4.1307 | NaN | NaN | NaN | 131.2542 | 596.1886 | NaN | 28.9972 | NaN | 26.4578
205.1292 | 11.3226 | 11.4724 | 11.367 | 11.7115 | 11.1417 | 11.7488 | 11.5208 | 11.2522 | NaN | NaN | NaN | 11.5972 | 92.2433 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 111.8386 | 597.7146 | NaN | 30.5276 | NaN | 26.5702
206.1292 | 11.289 | 11.2773 | 11.3638 | 11.6961 | 11.169 | 11.7257 | 11.475 | 11.2458 | NaN | NaN | NaN | 11.7126 | 93.453 | NaN | NaN | NaN | -16.8619 | NaN | NaN | NaN | 25.5228 | 597.6844 | NaN | 29.3361 | NaN | 24.4488
207.1292 | 11.3302 | 11.2062 | 11.3672 | 11.8646 | 11.0752 | 11.6429 | 11.4431 | 11.2475 | NaN | NaN | NaN | 11.673 | 92.4582 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 25.2276 | 596.5208 | NaN | 28.5683 | NaN | 21.894
208.1292 | 11.3547 | 11.5811 | 11.3626 | 11.7584 | 11.0253 | 11.9349 | 11.5316 | 11.2504 | NaN | NaN | NaN | 11.668 | 98.0836 | NaN | NaN | NaN | -18.2116 | NaN | NaN | NaN | 25.6456 | 596.2644 | NaN | 29.5013 | NaN | 23.2148
209.1292 | 11.2963 | 11.2297 | 11.367 | 11.705 | 11.0772 | 11.6659 | 11.4582 | 11.25 | NaN | NaN | NaN | 11.6788 | 94.0148 | NaN | NaN | NaN | -0.5695 | NaN | NaN | NaN | 26.1776 | 597.3708 | NaN | 29.7265 | NaN | 22.6255
210.1292 | 11.5088 | 11.3728 | 11.3689 | 11.9458 | 11.0994 | 11.8304 | 11.5052 | 11.2528 | NaN | NaN | NaN | 11.705 | 99.1044 | NaN | NaN | NaN | -18.6002 | NaN | NaN | NaN | 24.5129 | 596.3629 | NaN | 29.4336 | NaN | 26.1687
211.1292 | 11.4627 | 11.5803 | 11.3708 | 11.647 | 11.0989 | 11.8113 | 11.5597 | 11.2473 | NaN | NaN | NaN | 11.6583 | 92.0006 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 27.3733 | 595.9344 | NaN | 29.2736 | NaN | 22.0612
212.1292 | 11.2977 | 11.3411 | 11.367 | 11.7861 | 11.1128 | 11.8915 | 11.5243 | 11.2466 | NaN | NaN | NaN | 11.5952 | 98.8704 | NaN | NaN | NaN | -5.2358 | NaN | NaN | NaN | 26.3176 | 595.8315 | NaN | 28.9189 | NaN | 28.295
213.1292 | 11.3124 | 11.4047 | 11.3714 | 11.6987 | 11.1036 | 11.7639 | 11.5147 | 11.2503 | NaN | NaN | NaN | 11.613 | 93.3635 | NaN | NaN | NaN | -10.6808 | NaN | NaN | NaN | 27.3233 | 592.6033 | NaN | 29.5549 | NaN | 22.6516
214.1292 | 11.3913 | 11.3182 | 11.3656 | 11.6902 | 11.1438 | 11.8137 | 11.5 | 11.2421 | NaN | NaN | NaN | 11.6067 | 95.8366 | NaN | NaN | NaN | -16.9956 | NaN | NaN | NaN | 24.6771 | 596.3858 | NaN | 28.3194 | NaN | 20.5377
215.1292 | 11.3067 | 11.4267 | 11.3619 | 11.7254 | 11.1693 | 11.8293 | 11.5297 | 11.2491 | NaN | NaN | NaN | 11.607 | 95.9012 | NaN | NaN | NaN | -18.898 | NaN | NaN | NaN | 25.8647 | 596.4575 | NaN | 28.6869 | NaN | 25.4175
216.1292 | 11.2655 | 11.4779 | 11.3666 | 11.7051 | 11.1016 | 11.9902 | 11.5346 | 11.2479 | NaN | NaN | NaN | 11.6335 | 96.4777 | NaN | NaN | NaN | -14.6549 | NaN | NaN | NaN | 25.0549 | 596.4989 | NaN | 30.2394 | NaN | 25.925
217.1292 | 11.3149 | 11.4167 | 11.3627 | 11.679 | 10.9181 | 11.8036 | 11.541 | 11.243 | NaN | NaN | NaN | 11.5668 | 91.1671 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 27.3405 | 595.8606 | NaN | 29.1637 | NaN | 24.4404
218.1292 | 11.4 | 11.399 | 11.3676 | 11.6905 | 11.1047 | 11.8682 | 11.5342 | 11.2575 | NaN | NaN | NaN | 11.6149 | 93.708 | NaN | NaN | NaN | 6.1189 | NaN | NaN | NaN | 23.233 | 595.7881 | NaN | 29.3624 | NaN | 25.655
219.1292 | 11.3012 | 11.3491 | 11.3676 | 11.6829 | 11.0938 | 11.7909 | 11.517 | 11.246 | NaN | NaN | NaN | 11.5922 | 93.9484 | NaN | NaN | NaN | -18.2487 | NaN | NaN | NaN | 26.9371 | 596.4279 | NaN | 29.8604 | NaN | 24.6752
220.1292 | 11.3993 | 11.3966 | 11.3664 | 11.6333 | 11.197 | 11.8193 | 11.5013 | 11.2487 | NaN | NaN | NaN | 11.7018 | 96.4354 | NaN | NaN | NaN | -18.9261 | NaN | NaN | NaN | 25.6151 | 595.6935 | NaN | 28.0762 | NaN | 25.9286
221.1292 | 11.3403 | 11.351 | 11.3664 | 11.6967 | 11.083 | 11.7829 | 11.4974 | 11.2496 | NaN | NaN | NaN | 11.644 | 96.259 | NaN | NaN | NaN | -9.1259 | NaN | NaN | NaN | 25.0276 | 594.2248 | NaN | 29.0567 | NaN | 24.7193
222.1292 | 11.5608 | 11.4459 | 11.3687 | 11.7663 | 11.0101 | 11.8492 | 11.4921 | 11.2552 | NaN | NaN | NaN | 11.6804 | 93.2823 | NaN | NaN | NaN | -11.2843 | NaN | NaN | NaN | 21.4071 | 595.0399 | NaN | 29.9882 | NaN | 22.7187
223.1292 | 11.3948 | 11.474 | 11.367 | 11.7083 | 10.9783 | 11.9158 | 11.5398 | 11.2475 | NaN | NaN | NaN | 11.6441 | 91.1037 | NaN | NaN | NaN | -15.2889 | NaN | NaN | NaN | 25.6298 | 596.0846 | NaN | 32.1166 | NaN | 21.6533
224.1292 | 11.241 | 11.3928 | 11.3679 | 11.6672 | 10.9995 | 11.938 | 11.5231 | 11.2463 | NaN | NaN | NaN | 11.6059 | 93.8188 | NaN | NaN | NaN | -12.2905 | NaN | NaN | NaN | 26.4395 | 597.8639 | NaN | 31.1196 | NaN | 26.5027
225.1292 | 11.3093 | 11.3348 | 11.3684 | 11.7913 | 10.9594 | 11.8143 | 11.5199 | 11.2439 | NaN | NaN | NaN | 11.5696 | 92.1806 | NaN | NaN | NaN | -11.5946 | NaN | NaN | NaN | 23.6282 | 596.5878 | NaN | 30.4473 | NaN | 22.7141
226.1292 | 11.2482 | 11.6663 | 11.3645 | 11.8414 | 11.0093 | 11.8408 | 11.5829 | 11.2417 | NaN | NaN | NaN | 11.6825 | 93.1121 | NaN | NaN | NaN | -6.8306 | NaN | NaN | NaN | 23.8071 | 594.2183 | NaN | 29.9134 | NaN | 23.9563
227.1292 | 11.3056 | 11.4068 | 11.3647 | 11.7019 | 11.0481 | 11.7819 | 11.5227 | 11.245 | NaN | NaN | NaN | 11.5754 | 91.0612 | NaN | NaN | NaN | -18.4831 | NaN | NaN | NaN | 24.0596 | 596.3964 | NaN | 30.7859 | NaN | 26.0739
228.1292 | 11.3107 | 11.6063 | 11.3604 | 11.702 | 11.0247 | 12.0016 | 11.5731 | 11.2426 | NaN | NaN | NaN | 11.6411 | 91.4584 | NaN | NaN | NaN | -15.0773 | NaN | NaN | NaN | 28.4621 | 597.5265 | NaN | 29.4042 | NaN | 23.5033
229.1292 | 11.2683 | 11.6168 | 11.3596 | 11.7312 | 10.9811 | 11.8666 | 11.6205 | 11.2468 | NaN | NaN | NaN | 11.6117 | 91.4183 | NaN | NaN | NaN | -18.4168 | NaN | NaN | NaN | 28.1341 | 597.2182 | NaN | 30.044 | NaN | 21.9684
230.1292 | 11.2993 | 11.4525 | 11.3674 | 11.7489 | 11.0869 | 11.8962 | 11.5572 | 11.2549 | NaN | NaN | NaN | 11.6785 | 94.6316 | NaN | NaN | NaN | 0.0603 | NaN | NaN | NaN | 24.7675 | 597.3151 | NaN | 30.2203 | NaN | 25.4204
231.1292 | 11.279 | 11.3398 | 11.365 | 11.7794 | 10.9051 | 11.7866 | 11.5299 | 11.2499 | NaN | NaN | NaN | 11.6445 | 92.934 | NaN | NaN | NaN | -18.6426 | NaN | NaN | NaN | 22.9807 | 598.5636 | NaN | 31.6428 | NaN | 23.2955
232.1292 | 11.4453 | 11.4659 | 11.367 | 11.8181 | 11.0339 | 11.8626 | 11.5706 | 11.2588 | NaN | NaN | NaN | 11.6489 | 92.6563 | NaN | NaN | NaN | 0.0798 | NaN | NaN | NaN | 27.19 | 598.5318 | NaN | 29.0933 | NaN | 25.4363
233.1292 | 11.3587 | 11.3536 | 11.3688 | 11.7335 | 11.0223 | 11.7849 | 11.5151 | 11.2541 | NaN | NaN | NaN | 11.5989 | 92.2307 | NaN | NaN | NaN | -19.2317 | NaN | NaN | NaN | 25.4591 | 592.3855 | NaN | 30.0088 | NaN | 23.4965
234.1292 | 11.4047 | 11.1952 | 11.3758 | 11.6897 | 11.0392 | 11.6369 | 11.4596 | 11.2521 | NaN | NaN | NaN | 11.61 | 96.4788 | NaN | NaN | NaN | -16.4976 | NaN | NaN | NaN | 24.8948 | 593.5187 | NaN | 28.9676 | NaN | 21.7282
235.1292 | 11.3393 | 11.3689 | 11.37 | 11.6798 | 11.0414 | 11.7994 | 11.5273 | 11.2555 | NaN | NaN | NaN | 11.6084 | 92.7809 | NaN | NaN | NaN | -18.8632 | NaN | NaN | NaN | 26.3232 | 592.7198 | NaN | 29.5358 | NaN | 20.9453
236.1292 | 11.3141 | 11.394 | 11.3707 | 11.7302 | 11.0842 | 11.8339 | 11.535 | 11.2575 | NaN | NaN | NaN | 11.7169 | 93.9504 | NaN | NaN | NaN | -12.9537 | NaN | NaN | NaN | 26.2145 | 589.984 | NaN | 28.6596 | NaN | 21.2872
237.1292 | 11.2727 | 11.2739 | 11.3754 | 11.7163 | 11.2255 | 11.7464 | 11.4979 | 11.2581 | NaN | NaN | NaN | 11.5764 | 97.2001 | NaN | NaN | NaN | -6.7432 | NaN | NaN | NaN | 28.1239 | 592.4862 | NaN | 30.5375 | NaN | 27.423
238.1292 | 11.3693 | 11.3454 | 11.3727 | 11.6706 | 11.1211 | 11.7924 | 11.5107 | 11.2588 | NaN | NaN | NaN | 11.7014 | 109.0145 | NaN | NaN | NaN | 0.1264 | NaN | NaN | NaN | 24.4317 | 590.8887 | NaN | 29.1528 | NaN | 23.1494
239.1292 | 11.3601 | 11.3183 | 11.3774 | 11.7134 | 10.8883 | 11.8071 | 11.5172 | 11.2574 | NaN | NaN | NaN | 11.6122 | 91.9098 | NaN | NaN | NaN | -14.4838 | NaN | NaN | NaN | 25.9036 | 591.3595 | NaN | 31.4326 | NaN | 25.7697
240.1292 | 11.2915 | 11.3273 | 11.3811 | 11.753 | 10.964 | 11.7645 | 11.5176 | 11.2583 | NaN | NaN | NaN | 11.641 | 93.1499 | NaN | NaN | NaN | -1.0595 | NaN | NaN | NaN | 24.0145 | 591.6849 | NaN | 30.0442 | NaN | 26.8319
241.1292 | 11.3205 | 11.6849 | 11.3767 | 11.8743 | 11.025 | 11.9902 | 11.6364 | 11.2649 | NaN | NaN | NaN | 11.6132 | 97.7639 | NaN | NaN | NaN | -12.245 | NaN | NaN | NaN | 28.7765 | 589.1216 | NaN | 30.9168 | NaN | 22.8151
242.1292 | 11.3714 | 11.4687 | 11.3775 | 11.6758 | 11.064 | 11.8886 | 11.5613 | 11.259 | NaN | NaN | NaN | 11.726 | 96.225 | NaN | NaN | NaN | -10.8489 | NaN | NaN | NaN | 27.1268 | 590.1947 | NaN | 30.8344 | NaN | 21.6666
243.1292 | 11.314 | 11.6302 | 11.3721 | 11.7077 | 11.018 | 11.9481 | 11.6048 | 11.2515 | NaN | NaN | NaN | 11.6905 | 95.2411 | NaN | NaN | NaN | -18.5862 | NaN | NaN | NaN | 27.02 | 588.6052 | NaN | 29.9316 | NaN | 25.8304
244.1292 | 11.2934 | 11.4622 | 11.3783 | 11.8583 | 10.9922 | 11.8536 | 11.5654 | 11.2567 | NaN | NaN | NaN | 11.5654 | 93.376 | NaN | NaN | NaN | -16.7254 | NaN | NaN | NaN | 25.3795 | 586.172 | NaN | 29.3423 | NaN | 24.8095
245.1292 | 11.6255 | 11.3666 | 11.3727 | 11.8534 | 11.1347 | 11.8518 | 11.5226 | 11.2559 | NaN | NaN | NaN | 11.6403 | 91.1176 | NaN | NaN | NaN | 7.1533 | NaN | NaN | NaN | 28.2582 | 588.0656 | NaN | 28.2023 | NaN | 23.8236
246.1292 | 11.4516 | 11.6319 | 11.3798 | 11.712 | 11.1141 | 11.793 | 11.608 | 11.2629 | NaN | NaN | NaN | 11.629 | 95.0396 | NaN | NaN | NaN | -5.0569 | NaN | NaN | NaN | 23.4444 | 588.8835 | NaN | 31.1644 | NaN | 21.2231
247.1292 | 11.2972 | 11.2876 | 11.3727 | 11.8334 | 11.0702 | 11.775 | 11.5052 | 11.2629 | NaN | NaN | NaN | 11.5847 | 96.9027 | NaN | NaN | NaN | -13.6591 | NaN | NaN | NaN | 25.5871 | 588.4168 | NaN | 31.4255 | NaN | 24.4761
248.1292 | 11.2912 | 11.336 | 11.3746 | 11.6906 | 11.0155 | 11.7525 | 11.4908 | 11.2592 | NaN | NaN | NaN | 11.6169 | 90.3346 | NaN | NaN | NaN | -18.7527 | NaN | NaN | NaN | 26.8164 | 587.9356 | NaN | 30.567 | NaN | 21.0516
249.1292 | 11.369 | 11.4355 | 11.3695 | 11.8127 | 11.1 | 11.9759 | 11.5366 | 11.2584 | NaN | NaN | NaN | 11.6371 | 99.5644 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 23.621 | 586.7862 | NaN | 28.7518 | NaN | 21.5997
250.1292 | 11.3133 | 11.3909 | 11.3626 | 11.7708 | 11.067 | 11.7727 | 11.5187 | 11.2584 | NaN | NaN | NaN | 11.6586 | 91.1054 | NaN | NaN | NaN | -14.8687 | NaN | NaN | NaN | 29.7496 | 585.7468 | NaN | 29.5958 | NaN | 22.6054
251.1292 | 11.3583 | 11.538 | 11.3706 | 11.6236 | 11.1175 | 11.9459 | 11.5446 | 11.2609 | NaN | NaN | NaN | 11.6625 | 92.5152 | NaN | NaN | NaN | -15.4362 | NaN | NaN | NaN | 26.2073 | 587.4236 | NaN | 29.9765 | NaN | 18.6771
252.1292 | 11.3772 | 11.4748 | 11.3666 | 11.6819 | 11.0827 | 12.0725 | 11.557 | 11.2607 | NaN | NaN | NaN | 11.6363 | 88.9775 | NaN | NaN | NaN | -12.0925 | NaN | NaN | NaN | 27.1378 | 586.8901 | NaN | 29.4376 | NaN | 21.243
253.1292 | 11.3563 | 11.282 | 11.368 | 11.681 | 11.0749 | 11.6991 | 11.4859 | 11.2553 | NaN | NaN | NaN | 11.729 | 95.4632 | NaN | NaN | NaN | -13.2725 | NaN | NaN | NaN | 27.0209 | 585.332 | NaN | 30.155 | NaN | 23.8905
254.1292 | 11.3559 | 11.3045 | 11.376 | 11.9732 | 11.08 | 11.7883 | 11.5083 | 11.263 | NaN | NaN | NaN | 11.6171 | 95.3963 | NaN | NaN | NaN | -3.2985 | NaN | NaN | NaN | 24.7692 | 583.8614 | NaN | 30.2264 | NaN | 25.4596
255.1292 | 11.2886 | 11.4535 | 11.3653 | 11.7338 | 11.1383 | 11.8432 | 11.556 | 11.258 | NaN | NaN | NaN | 11.6985 | 94.8398 | NaN | NaN | NaN | -14.4809 | NaN | NaN | NaN | 26.8341 | 583.6457 | NaN | 30.1239 | NaN | 25.2622
256.1292 | 11.3309 | 11.3721 | 11.3694 | 11.711 | 11.0387 | 11.7726 | 11.5214 | 11.2607 | NaN | NaN | NaN | 11.6561 | 91.2936 | NaN | NaN | NaN | -9.0547 | NaN | NaN | NaN | 26.1222 | 583.3738 | NaN | 30.1413 | NaN | 26.7838
257.1292 | 11.4153 | 11.5517 | 11.374 | 11.7056 | 11.0247 | 11.9374 | 11.5936 | 11.2567 | NaN | NaN | NaN | 11.7037 | 93.3484 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 24.6063 | 584.0157 | NaN | 28.5842 | NaN | 26.1459
258.1292 | 11.338 | 11.3222 | 11.3668 | 11.6833 | 11.0762 | 11.8034 | 11.5188 | 11.2636 | NaN | NaN | NaN | 11.737 | 98.4374 | NaN | NaN | NaN | -16.231 | NaN | NaN | NaN | 24.6832 | 582.3244 | NaN | 29.1079 | NaN | 25.7059
259.1292 | 11.2661 | 11.368 | 11.3688 | 11.7293 | 11.0272 | 11.8186 | 11.5302 | 11.2675 | NaN | NaN | NaN | 11.6393 | 93.8671 | NaN | NaN | NaN | -16.7054 | NaN | NaN | NaN | 28.7679 | 580.9774 | NaN | 29.365 | NaN | 19.7624
260.1292 | 11.3177 | 11.3167 | 11.3712 | 11.6355 | 10.9553 | 11.9062 | 11.5164 | 11.2676 | NaN | NaN | NaN | 11.6276 | 94.4609 | NaN | NaN | NaN | -14.6031 | NaN | NaN | NaN | 26.927 | 581.804 | NaN | 30.9122 | NaN | 22.4057
261.1292 | 11.3317 | 11.3338 | 11.3661 | 11.7237 | 11.0794 | 11.7445 | 11.4931 | 11.2625 | NaN | NaN | NaN | 11.6092 | 97.501 | NaN | NaN | NaN | -18.9869 | NaN | NaN | NaN | 26.5368 | 579.7114 | NaN | 30.6898 | NaN | 21.5326
262.1292 | 11.3965 | 11.3399 | 11.3693 | 11.7534 | 11.0045 | 11.767 | 11.5133 | 11.2585 | NaN | NaN | NaN | 11.5789 | 94.5268 | NaN | NaN | NaN | -18.9559 | NaN | NaN | NaN | 25.0891 | 579.7005 | NaN | 29.8045 | NaN | 26.1849
263.1292 | 11.3137 | 11.2855 | 11.3663 | 11.6893 | 11.0349 | 11.7151 | 11.5045 | 11.2643 | NaN | NaN | NaN | 11.69 | 96.2859 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 26.0826 | 582.1681 | NaN | 27.292 | NaN | 25.1008
264.1292 | 11.4816 | 11.482 | 11.3666 | 11.9403 | 11.125 | 11.9022 | 11.5936 | 11.2612 | NaN | NaN | NaN | 11.6812 | 95.7493 | NaN | NaN | NaN | -4.8271 | NaN | NaN | NaN | 24.2163 | 580.2897 | NaN | 29.5677 | NaN | 25.7279
265.1292 | 11.2555 | 11.5412 | 11.3693 | 11.7433 | 11.0484 | 11.9128 | 11.5585 | 11.2644 | NaN | NaN | NaN | 11.6712 | 93.6739 | NaN | NaN | NaN | 9.2496 | NaN | NaN | NaN | 24.7485 | 580.1934 | NaN | 30.0605 | NaN | 27.1173
266.1292 | 11.2942 | 11.2193 | 11.3745 | 11.6937 | 10.9474 | 11.671 | 11.4593 | 11.2716 | NaN | NaN | NaN | 11.7572 | 94.9203 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 24.7748 | 580.8358 | NaN | 31.5686 | NaN | 25.6798
267.1292 | 11.3278 | 11.3552 | 11.3646 | 11.7062 | 10.9952 | 11.8378 | 11.5217 | 11.2638 | NaN | NaN | NaN | 11.6289 | 96.4461 | NaN | NaN | NaN | -16.4337 | NaN | NaN | NaN | 29.006 | 577.7371 | NaN | 30.423 | NaN | 22.2514
268.1292 | 11.2292 | 11.539 | 11.3659 | 11.7788 | 11.0462 | 11.8519 | 11.5504 | 11.2651 | NaN | NaN | NaN | 11.6826 | 90.4159 | NaN | NaN | NaN | NaN | NaN | 1312.5384 | NaN | 24.9872 | 578.9017 | NaN | 28.7205 | NaN | 24.75
269.1292 | 11.3238 | 11.2266 | 11.3737 | 11.6879 | 11.1013 | 11.6673 | 11.4685 | 11.2646 | NaN | NaN | NaN | 11.6769 | 93.2128 | NaN | NaN | NaN | -17.9647 | NaN | NaN | NaN | 25.1916 | 579.3373 | NaN | 30.3438 | NaN | 24.2318
270.1292 | 11.5179 | 11.3543 | 11.3763 | 11.7382 | 11.0827 | 11.7862 | 11.5353 | 11.2643 | NaN | NaN | NaN | 11.6353 | 95.6016 | NaN | NaN | NaN | -4.293 | NaN | 1241.5402 | NaN | 24.4809 | 578.5973 | NaN | 29.7752 | NaN | 26.013
271.1292 | 11.2967 | 11.587 | 11.3747 | 11.7757 | 11.1333 | 12.3183 | 11.5513 | 11.2641 | NaN | NaN | NaN | 11.6451 | 92.1724 | NaN | NaN | NaN | -19.222 | NaN | 1237.6539 | NaN | 28.4938 | 578.1243 | NaN | 30.2591 | NaN | 22.98
272.1292 | 11.2807 | 11.2977 | 11.3737 | 11.7 | 11.1345 | 11.7912 | 11.5164 | 11.2607 | NaN | NaN | NaN | 11.7542 | 98.7415 | NaN | NaN | NaN | -18.9639 | NaN | 1174.7475 | NaN | 27.0741 | 576.8422 | NaN | 31.4898 | NaN | 28.0908
273.1292 | 11.3553 | 11.4777 | 11.379 | 11.9189 | 11.0804 | 11.9429 | 11.5721 | 11.262 | NaN | NaN | NaN | 11.6294 | 101.7891 | NaN | NaN | NaN | -15.7286 | NaN | 1129.2966 | NaN | 27.7792 | 576.2398 | NaN | 30.3438 | NaN | 26.5986
274.1292 | 11.236 | 11.3825 | 11.3738 | 11.6603 | 10.992 | 11.8582 | 11.5127 | 11.2637 | NaN | NaN | NaN | 11.6321 | 91.5511 | NaN | NaN | NaN | -15.0552 | NaN | 1074.2977 | NaN | 27.7367 | 576.8116 | NaN | 28.5199 | NaN | 24.2879
275.1292 | 11.4819 | 11.4098 | 11.3758 | 11.6603 | 10.9135 | 11.847 | 11.5584 | 11.2625 | NaN | NaN | NaN | 11.6457 | 92.8654 | NaN | NaN | NaN | 11.249 | NaN | 1041.0908 | NaN | 25.4103 | 574.7566 | NaN | 28.161 | NaN | 23.2633
276.1292 | 11.2889 | 11.3693 | 11.3787 | 11.6776 | 11.1044 | 11.79 | 11.5004 | 11.2655 | NaN | NaN | NaN | 11.6162 | 94.7426 | NaN | NaN | NaN | NaN | NaN | 1009.7303 | NaN | 22.0287 | 577.566 | NaN | 29.6538 | NaN | 21.1652
277.1292 | 11.3638 | 11.3015 | 11.3754 | 11.7107 | 11.0786 | 11.6742 | 11.4804 | 11.2638 | NaN | NaN | NaN | 11.5895 | 91.9352 | NaN | NaN | NaN | -15.0297 | NaN | 970.0074 | NaN | 25.1385 | 576.6386 | NaN | 30.8422 | NaN | 25.9386
278.1292 | 11.3032 | 11.402 | 11.3701 | 11.9339 | 10.9754 | 11.8282 | 11.521 | 11.2621 | NaN | NaN | NaN | 11.6007 | 92.9303 | NaN | NaN | NaN | NaN | NaN | 897.6613 | NaN | 23.2746 | 576.4339 | NaN | 31.1573 | NaN | 24.1145
279.1292 | 11.3017 | 11.3065 | 11.3753 | 11.7067 | 11.1868 | 11.7052 | 11.4878 | 11.2686 | NaN | NaN | NaN | 11.7403 | 93.9546 | NaN | NaN | NaN | -19.809 | NaN | 919.373 | NaN | 25.7322 | 576.8567 | NaN | 28.7972 | NaN | 20.0714
280.1292 | 11.2936 | 11.4356 | 11.3713 | 11.6582 | 11.1354 | 11.7931 | 11.5334 | 11.2619 | NaN | NaN | NaN | 11.6098 | 92.8162 | NaN | NaN | NaN | NaN | NaN | 868.7776 | NaN | 27.2515 | 576.3996 | NaN | 30.4194 | NaN | 23.407
281.1292 | 11.2273 | 11.4798 | 11.3709 | 11.7246 | 11.0889 | 11.7593 | 11.5535 | 11.2641 | NaN | NaN | NaN | 11.6401 | 92.4727 | NaN | NaN | NaN | -19.6756 | NaN | 768.0206 | NaN | 23.8931 | 574.6181 | NaN | 30.19 | NaN | 18.6004
282.1292 | 11.564 | 11.3233 | 11.3687 | 11.6712 | 11.1059 | 11.7213 | 11.4974 | 11.2672 | NaN | NaN | NaN | 11.6619 | 95.9396 | NaN | NaN | NaN | 2.766 | NaN | 816.9117 | NaN | 26.2866 | 577.4021 | NaN | 30.4768 | NaN | 23.9155
283.1292 | 11.312 | 11.3439 | 11.3686 | 11.7813 | 11.059 | 11.789 | 11.5245 | 11.2614 | NaN | NaN | NaN | 11.7856 | 92.5386 | NaN | NaN | NaN | -17.3687 | NaN | 701.7528 | NaN | 27.3071 | 577.5348 | NaN | 29.3916 | NaN | 21.4408
284.1292 | 11.2458 | 11.4276 | 11.3705 | 11.7242 | 11.057 | 11.8145 | 11.5488 | 11.2637 | NaN | NaN | NaN | 11.5984 | 96.7349 | NaN | NaN | NaN | -10.9571 | NaN | 706.439 | NaN | 24.9776 | 576.1805 | NaN | 29.0572 | NaN | 23.3766
285.1292 | 11.2842 | 11.2364 | 11.3647 | 11.9106 | 11.0904 | 11.6638 | 11.4735 | 11.2589 | NaN | NaN | NaN | 11.6626 | 94.085 | NaN | NaN | NaN | -15.8213 | NaN | 634.506 | NaN | 24.4436 | 575.3175 | NaN | 29.5972 | NaN | 27.0452
286.1292 | 11.4221 | 11.4886 | 11.3686 | 11.7219 | 10.9424 | 11.8721 | 11.5591 | 11.2597 | NaN | NaN | NaN | 11.6981 | 94.6574 | NaN | NaN | NaN | -19.396 | NaN | 582.7837 | NaN | 23.6077 | 575.0919 | NaN | 28.0299 | NaN | 20.6325
287.1292 | 11.3515 | 11.5536 | 11.3662 | 11.6956 | 11.0481 | 11.8978 | 11.5664 | 11.2613 | NaN | NaN | NaN | 11.6297 | 91.76 | NaN | NaN | NaN | -18.0495 | NaN | 570.3042 | NaN | 26.1249 | 573.0049 | NaN | 30.9969 | NaN | 26.3967
288.1292 | 11.4578 | 11.3675 | 11.3679 | 11.6915 | 10.9763 | 11.7484 | 11.5166 | 11.2601 | NaN | NaN | NaN | 11.6104 | 90.9099 | NaN | NaN | NaN | -14.9334 | NaN | 529.9992 | NaN | 24.1011 | 574.7588 | NaN | 29.7374 | NaN | 24.8893
289.1292 | 11.2751 | 11.2476 | 11.369 | 11.9767 | 11.0178 | 11.6645 | 11.4833 | 11.2675 | NaN | NaN | NaN | 11.6595 | 93.028 | NaN | NaN | NaN | -13.9714 | NaN | 525.1512 | NaN | 27.9589 | 574.3763 | NaN | 30.6531 | NaN | 17.0333
290.1292 | 11.2626 | 11.2523 | 11.3675 | 11.6523 | 11.0473 | 11.6876 | 11.4768 | 11.2643 | NaN | NaN | NaN | 11.5902 | 93.7456 | NaN | NaN | NaN | NaN | NaN | 491.7942 | NaN | 23.8798 | 573.748 | NaN | 30.3703 | NaN | 22.7653
291.1292 | 11.4132 | 11.2227 | 11.3651 | 11.8226 | 11.0781 | 11.6935 | 11.4684 | 11.264 | NaN | NaN | NaN | 11.693 | 90.9955 | NaN | NaN | NaN | -18.7152 | NaN | 448.9713 | NaN | 25.5803 | 574.9018 | NaN | 30.3634 | NaN | 21.8743
292.1292 | 11.251 | 11.4635 | 11.3578 | 11.7973 | 11.0506 | 11.8133 | 11.5483 | 11.2647 | NaN | NaN | NaN | 11.645 | 98.7323 | NaN | NaN | NaN | NaN | NaN | 439.3245 | NaN | 28.7625 | 571.9161 | NaN | 28.5242 | NaN | 23.4152
293.1292 | 11.2938 | 11.5707 | 11.3626 | 11.7095 | 11.0425 | 11.8128 | 11.5968 | 11.2659 | NaN | NaN | NaN | 11.6004 | 90.2045 | NaN | NaN | NaN | -15.2366 | NaN | 377.604 | NaN | 25.9162 | 574.7022 | NaN | 29.1241 | NaN | 26.4444
294.1292 | 11.2948 | 11.2807 | 11.3553 | 11.8423 | 11.0421 | 11.7239 | 11.5086 | 11.2703 | NaN | NaN | NaN | 11.5845 | 94.8414 | NaN | NaN | NaN | -4.5572 | NaN | 381.4712 | NaN | 23.6111 | 572.8624 | NaN | 30.1693 | NaN | 21.8903
295.1292 | 11.3724 | 11.7726 | 11.357 | 11.6828 | 11.0571 | 12.0111 | 11.6179 | 11.2643 | NaN | NaN | NaN | 11.6093 | 89.7084 | NaN | NaN | NaN | 9.326 | NaN | 330.9301 | NaN | 28.7807 | 572.4466 | NaN | 29.8431 | NaN | 24.5392
296.1292 | 11.2353 | 11.3682 | 11.3614 | 11.6899 | 11.0465 | 11.8981 | 11.518 | 11.2633 | NaN | NaN | NaN | 11.6302 | 91.0316 | NaN | NaN | NaN | 9.8609 | NaN | 317.0421 | NaN | 28.8937 | 571.1135 | NaN | 29.2568 | NaN | 22.4824
297.1292 | 11.3957 | 11.3985 | 11.3585 | 11.7022 | 11.0646 | 11.8462 | 11.5373 | 11.256 | NaN | NaN | NaN | 11.6089 | 94.3148 | NaN | NaN | NaN | -10.6627 | NaN | 265.8658 | NaN | 26.733 | 570.8092 | NaN | 29.9972 | NaN | 28.3271
298.1292 | 11.3009 | 11.2298 | 11.3674 | 11.6903 | 10.9827 | 11.6891 | 11.4769 | 11.2618 | NaN | NaN | NaN | 11.5829 | 95.0642 | NaN | NaN | NaN | -19.3949 | NaN | 291.0699 | NaN | 28.0442 | 572.6883 | NaN | 29.612 | NaN | 20.4252
299.1292 | 11.2565 | 11.3714 | 11.365 | 11.729 | 11.0157 | 11.8465 | 11.5364 | 11.2661 | NaN | NaN | NaN | 11.6049 | 96.9848 | NaN | NaN | NaN | NaN | NaN | 269.7399 | NaN | 27.1002 | 571.4619 | NaN | 28.1613 | NaN | 27.7793
300.1292 | 11.3422 | 11.6152 | 11.3616 | 11.7789 | 11.1062 | 11.9864 | 11.566 | 11.2608 | NaN | NaN | NaN | 11.6536 | 91.7213 | NaN | NaN | NaN | -15.4734 | NaN | 235.6772 | NaN | 24.6241 | 572.3061 | NaN | 29.365 | NaN | 28.5181
301.1292 | 11.2766 | 11.3188 | 11.3659 | 11.6813 | 10.9454 | 11.7352 | 11.4994 | 11.2637 | NaN | NaN | NaN | 11.5834 | 93.1728 | NaN | NaN | NaN | 8.9753 | NaN | 227.677 | NaN | 26.0407 | 572.7584 | NaN | 30.4868 | NaN | 22.1094
302.1292 | 11.3737 | 11.2789 | 11.3693 | 11.6667 | 11.0128 | 11.6762 | 11.4886 | 11.2625 | NaN | NaN | NaN | 11.6287 | 94.4092 | NaN | NaN | NaN | -7.9034 | NaN | 206.0776 | NaN | 25.6111 | 573.768 | NaN | 30.5154 | NaN | 20.2012
303.1292 | 11.4327 | 11.3357 | 11.3695 | 11.6929 | 11.0192 | 11.9262 | 11.5196 | 11.267 | NaN | NaN | NaN | 11.5752 | 94.2305 | NaN | NaN | NaN | 1.9451 | NaN | 175.7394 | NaN | 27.5023 | 571.7376 | NaN | 29.8914 | NaN | 21.4328
304.1292 | 11.2205 | 11.3143 | 11.3691 | 11.7484 | 11.0711 | 11.7765 | 11.508 | 11.2647 | NaN | NaN | NaN | 11.672 | 91.7791 | NaN | NaN | NaN | -13.2621 | NaN | 158.1279 | NaN | 29.0683 | 570.9991 | NaN | 30.1288 | NaN | 20.7915
305.1292 | 11.3319 | 11.5651 | 11.3659 | 11.8987 | 11.0696 | 11.9947 | 11.5621 | 11.2651 | NaN | NaN | NaN | 11.5953 | 96.4284 | NaN | NaN | NaN | NaN | NaN | 118.9609 | NaN | 25.5238 | 573.3817 | NaN | 28.9524 | NaN | 21.4594
306.1292 | 11.521 | 11.4801 | 11.3714 | 11.6707 | 11.0696 | 11.8872 | 11.5695 | 11.2636 | NaN | NaN | NaN | 11.5965 | 92.3344 | NaN | NaN | NaN | -9.4031 | NaN | 106.435 | NaN | 24.6954 | 570.1189 | NaN | 30.442 | NaN | 25.0951
307.1292 | 11.2953 | 11.3411 | 11.3694 | 11.7265 | 11.113 | 11.7647 | 11.5035 | 11.2628 | NaN | NaN | NaN | 11.6802 | 96.0333 | NaN | NaN | NaN | -18.11 | NaN | 119.1166 | NaN | 27.0147 | 570.5073 | NaN | 30.2114 | NaN | 19.5346
308.1292 | 11.3344 | 11.4303 | 11.3686 | 11.6715 | 11.174 | 11.8758 | 11.5371 | 11.2625 | NaN | NaN | NaN | 11.7543 | 98.8578 | NaN | NaN | NaN | 2.3223 | NaN | 79.9726 | NaN | 30.812 | 567.8884 | NaN | 30.2369 | NaN | 23.2834
309.1292 | 11.3079 | 11.3124 | 11.371 | 11.6992 | 11.0264 | 11.7056 | 11.4996 | 11.2661 | NaN | NaN | NaN | 11.6796 | 94.757 | NaN | NaN | NaN | -16.9737 | NaN | 56.9741 | NaN | 24.8027 | 569.7725 | NaN | 29.99 | NaN | 22.0687
310.1292 | 11.2539 | 11.4069 | 11.3681 | 11.7677 | 11.1012 | 11.8694 | 11.5295 | 11.2585 | NaN | NaN | NaN | 11.6083 | 92.7038 | NaN | NaN | NaN | -12.253 | NaN | 44.5633 | NaN | 25.9877 | 568.2753 | NaN | 28.2065 | NaN | 25.8644
311.1292 | 11.19 | 11.5233 | 11.3687 | 11.7353 | 11.033 | 11.955 | 11.584 | 11.2631 | NaN | NaN | NaN | 11.6239 | 89.7114 | NaN | NaN | NaN | -13.3809 | NaN | 16.9645 | NaN | 27.0586 | 568.0725 | NaN | 31.0617 | NaN | 21.8078
312.1292 | 11.2509 | 11.2894 | 11.3625 | 11.6931 | 11.0968 | 11.7337 | 11.4838 | 11.2636 | NaN | NaN | NaN | 11.7199 | 93.4208 | NaN | NaN | NaN | -6.0624 | NaN | 11.2667 | NaN | 27.1086 | 567.0061 | NaN | 28.8707 | NaN | 23.5941
313.1292 | 11.274 | 11.548 | 11.3706 | 11.6749 | 11.1005 | 11.8931 | 11.5424 | 11.2681 | NaN | NaN | NaN | 11.63 | 94.3251 | NaN | NaN | NaN | -16.4291 | NaN | NaN | NaN | 30.366 | 559.2066 | NaN | 27.9545 | NaN | 29.0108
314.1292 | 11.2636 | 11.5359 | 11.3711 | 11.8569 | 11.0068 | 11.9777 | 11.5795 | 11.262 | NaN | NaN | NaN | 11.5862 | 91.9692 | NaN | NaN | NaN | -17.1761 | NaN | NaN | NaN | 26.1308 | 560.5448 | NaN | 31.0608 | NaN | 26.1097
315.1292 | 11.2718 | 11.3389 | 11.3655 | 11.7066 | 11.0489 | 11.884 | 11.5273 | 11.2637 | NaN | NaN | NaN | 11.5884 | 91.8677 | NaN | NaN | NaN | -14.3159 | NaN | NaN | NaN | 27.0079 | 557.22 | NaN | 29.1528 | NaN | 23.1772
316.1292 | 11.3208 | 11.2454 | 11.3606 | 11.6828 | 11.0234 | 11.7348 | 11.4742 | 11.2578 | NaN | NaN | NaN | 11.6594 | 91.4613 | NaN | NaN | NaN | -15.5069 | NaN | NaN | NaN | 25.594 | 559.2453 | NaN | 30.9071 | NaN | 23.2466
317.1292 | 11.2946 | 11.2442 | 11.3637 | 11.6917 | 10.9219 | 11.7454 | 11.4823 | 11.2665 | NaN | NaN | NaN | 11.6196 | 91.4259 | NaN | NaN | NaN | -16.2772 | NaN | NaN | NaN | 26.285 | 561.7073 | NaN | 30.6895 | NaN | 22.584
318.1292 | 11.2576 | 11.5185 | 11.3704 | 11.6762 | 10.9673 | 11.8748 | 11.5721 | 11.2626 | NaN | NaN | NaN | 11.6064 | 91.8397 | NaN | NaN | NaN | -18.5027 | NaN | NaN | NaN | 25.029 | 561.5931 | NaN | 29.9544 | NaN | 25.8515
319.1292 | 11.3972 | 11.3053 | 11.367 | 11.8319 | 11.0246 | 11.8002 | 11.5068 | 11.2607 | NaN | NaN | NaN | 11.5944 | 91.8028 | NaN | NaN | NaN | -10.3008 | NaN | NaN | NaN | 26.7222 | 561.0714 | NaN | 28.7797 | NaN | 23.8915
320.1292 | 11.2469 | 11.2687 | 11.3621 | 11.7724 | 10.9567 | 11.7579 | 11.4889 | 11.2594 | NaN | NaN | NaN | 11.5891 | 91.7268 | NaN | NaN | NaN | -18.3524 | NaN | NaN | NaN | 29.4607 | 565.1514 | NaN | 28.6542 | NaN | 22.7266
321.1292 | 11.3254 | 11.5231 | 11.3675 | 11.7492 | 10.9401 | 11.9194 | 11.5859 | 11.2617 | NaN | NaN | NaN | 11.6105 | 94.1842 | NaN | NaN | NaN | -11.0994 | NaN | NaN | NaN | 23.9108 | 563.187 | NaN | 29.7115 | NaN | 22.46
322.1292 | 11.2344 | 11.4175 | 11.3701 | 11.6883 | 11.1416 | 11.9237 | 11.5436 | 11.264 | NaN | NaN | NaN | 11.6343 | 94.0025 | NaN | NaN | NaN | 9.3707 | NaN | NaN | NaN | 26.6011 | 565.4112 | NaN | 30.6211 | NaN | 21.1102
323.1292 | 11.3553 | 11.6168 | 11.368 | 11.7368 | 11.0218 | 11.998 | 11.595 | 11.2631 | NaN | NaN | NaN | 11.6403 | 93.6073 | NaN | NaN | NaN | 10.7185 | NaN | NaN | NaN | 26.002 | 564.5935 | NaN | 28.6376 | NaN | 24.6177
324.1292 | 11.2305 | 11.4098 | 11.3691 | 11.7565 | 11.0205 | 11.8107 | 11.5372 | 11.2611 | NaN | NaN | NaN | 11.7711 | 92.8776 | NaN | NaN | NaN | 11.2758 | NaN | NaN | NaN | 28.9987 | 564.7363 | NaN | 29.3928 | NaN | 24.296
325.1292 | 11.2444 | 11.4838 | 11.3696 | 11.7641 | 10.9648 | 11.894 | 11.566 | 11.2642 | NaN | NaN | NaN | 11.74 | 91.4085 | NaN | NaN | NaN | -2.361 | NaN | NaN | NaN | 25.878 | 562.8455 | NaN | 30.1358 | NaN | 20.0988
326.1292 | 11.2748 | 11.9326 | 11.3693 | 11.6977 | 11.0983 | 12.1673 | 11.6936 | 11.2637 | NaN | NaN | NaN | 11.6282 | 92.1759 | NaN | NaN | NaN | -19.4629 | NaN | NaN | NaN | 26.1893 | 562.6472 | NaN | 29.4955 | NaN | 26.3516
327.1292 | 11.3489 | 11.4243 | 11.3705 | 11.6882 | 11.0537 | 11.9804 | 11.572 | 11.2616 | NaN | NaN | NaN | 11.6479 | 94.1535 | NaN | NaN | NaN | -10.9114 | NaN | NaN | NaN | 27.4915 | 564.6248 | NaN | 29.9465 | NaN | 26.3479
328.1292 | 11.2872 | 11.3889 | 11.374 | 11.7148 | 11.0256 | 11.8793 | 11.5422 | 11.2674 | NaN | NaN | NaN | 11.7105 | 93.0645 | NaN | NaN | NaN | -17.5539 | NaN | NaN | NaN | 26.6952 | 566.5656 | NaN | 29.9231 | NaN | 23.0775
329.1292 | 11.426 | 11.381 | 11.368 | 11.7256 | 11.017 | 11.8213 | 11.5234 | 11.2651 | NaN | NaN | NaN | 11.6578 | 90.0457 | NaN | NaN | NaN | -8.3431 | NaN | NaN | NaN | 28.3986 | 566.0722 | NaN | 30.2895 | NaN | 22.7218
330.1292 | 11.4696 | 11.514 | 11.3652 | 11.7017 | 11.1216 | 11.9801 | 11.6017 | 11.2588 | NaN | NaN | NaN | 11.5933 | 92.8781 | NaN | NaN | NaN | -10.0218 | NaN | NaN | NaN | 25.8154 | 565.3116 | NaN | 29.8493 | NaN | 26.7094
331.1292 | 11.4308 | 11.6166 | 11.3695 | 11.6819 | 11.1243 | 12.0369 | 11.6359 | 11.2548 | NaN | NaN | NaN | 11.6308 | 92.72 | NaN | NaN | NaN | -18.9606 | NaN | NaN | NaN | 27.9003 | 562.5502 | NaN | 31.8508 | NaN | 20.0091
332.1292 | 11.3039 | 11.3249 | 11.3687 | 11.6795 | 11.0944 | 11.7446 | 11.4921 | 11.2581 | NaN | NaN | NaN | 11.8292 | 91.3999 | NaN | NaN | NaN | -7.5287 | NaN | NaN | NaN | 30.263 | 563.2411 | NaN | 31.5178 | NaN | 27.5401
333.1292 | 11.2636 | 11.5481 | 11.3638 | 11.701 | 11.1204 | 12.0011 | 11.5786 | 11.2551 | NaN | NaN | NaN | 11.6745 | 95.9428 | NaN | NaN | NaN | 9.8144 | NaN | NaN | NaN | 27.385 | 565.2642 | NaN | 32.1376 | NaN | 26.1928
334.1292 | 11.3034 | 11.3659 | 11.3675 | 11.7544 | 10.9732 | 11.8774 | 11.5339 | 11.2569 | NaN | NaN | NaN | 11.5971 | 91.772 | NaN | NaN | NaN | -7.7242 | NaN | NaN | NaN | 28.915 | 564.9704 | NaN | 30.5863 | NaN | 26.9769
335.1292 | 11.3973 | 11.4448 | 11.3728 | 11.821 | 11.0461 | 11.9397 | 11.5549 | 11.261 | NaN | NaN | NaN | 11.5351 | 97.0234 | NaN | NaN | NaN | -12.041 | NaN | NaN | NaN | 28.3496 | 564.8753 | NaN | 30.7739 | NaN | 24.7302
336.1292 | 11.3063 | 11.3977 | 11.3714 | 11.7592 | 10.9446 | 11.8511 | 11.5511 | 11.2617 | NaN | NaN | NaN | 11.7237 | 93.7622 | NaN | NaN | NaN | -15.6522 | NaN | NaN | NaN | 26.293 | 565.3564 | NaN | 30.4119 | NaN | 25.832
337.1292 | 11.2457 | 11.3231 | 11.3757 | 11.6917 | 11.0866 | 11.791 | 11.5201 | 11.2632 | NaN | NaN | NaN | 11.6722 | 93.7233 | NaN | NaN | NaN | -0.2979 | NaN | NaN | NaN | 25.5606 | 565.7828 | NaN | 29.3814 | NaN | 20.6388
338.1292 | 11.2915 | 11.3593 | 11.3735 | 11.76 | 11.0646 | 11.8676 | 11.5346 | 11.2601 | NaN | NaN | NaN | 11.685 | 92.7255 | NaN | NaN | NaN | -11.1667 | NaN | NaN | NaN | 28.848 | 564.1387 | NaN | 30.0158 | NaN | 23.4225
339.1292 | 11.2719 | 11.7955 | 11.3804 | 11.7391 | 11.1194 | 12.0456 | 11.6589 | 11.255 | NaN | NaN | NaN | 11.5711 | 91.9158 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 26.8545 | 564.4504 | NaN | 29.0085 | NaN | 20.4174
340.1292 | 11.5035 | 11.5686 | 11.3808 | 11.6558 | 10.9902 | 11.8119 | 11.598 | 11.26 | NaN | NaN | NaN | 11.6393 | 94.6509 | NaN | NaN | NaN | -13.2429 | NaN | NaN | NaN | 25.913 | 566.1671 | NaN | 29.4357 | NaN | 24.6857
341.1292 | 11.2713 | 11.29 | 11.3801 | 11.7703 | 11.0023 | 11.7865 | 11.5161 | 11.2618 | NaN | NaN | NaN | 11.629 | 92.7571 | NaN | NaN | NaN | -18.6888 | NaN | NaN | NaN | 27.7016 | 566.2317 | NaN | 29.8604 | NaN | 23.1933
342.1292 | 11.3756 | 11.3446 | 11.3929 | 11.6674 | 10.8912 | 11.8677 | 11.5216 | 11.2568 | NaN | NaN | NaN | 11.5929 | 95.8767 | NaN | NaN | NaN | -8.5955 | NaN | NaN | NaN | 28.5481 | 566.3557 | NaN | 29.2106 | NaN | 24.2319
343.1292 | 11.3113 | 11.4512 | 11.3876 | 11.7303 | 10.9389 | 11.8883 | 11.5692 | 11.2545 | NaN | NaN | NaN | 11.6095 | 93.3319 | NaN | NaN | NaN | -16.5087 | NaN | NaN | NaN | 27.5529 | 567.7466 | NaN | 30.1025 | NaN | 26.4324
344.1292 | 11.2523 | 11.3934 | 11.3931 | 11.6645 | 11.0098 | 11.9695 | 11.5654 | 11.2636 | NaN | NaN | NaN | 11.6499 | 91.5314 | NaN | NaN | NaN | -16.0489 | NaN | NaN | NaN | 26.6488 | 567.0728 | NaN | 30.2149 | NaN | 25.2071
345.1292 | 11.2883 | 11.4368 | 11.388 | 11.6949 | 11.0749 | 11.9427 | 11.5498 | 11.2647 | NaN | NaN | NaN | 11.5779 | 93.5993 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 26.0981 | 565.1186 | NaN | 30.5757 | NaN | 20.004
346.1292 | 11.2906 | 11.504 | 11.3824 | 11.6793 | 11.0997 | 11.9751 | 11.5981 | 11.2574 | NaN | NaN | NaN | 11.6657 | 93.7804 | NaN | NaN | NaN | -19.5741 | NaN | NaN | NaN | 28.4681 | 564.0456 | NaN | 29.9909 | NaN | 21.439
347.1292 | 11.442 | 11.5439 | 11.3858 | 11.7818 | 11.1205 | 11.9697 | 11.6149 | 11.2668 | NaN | NaN | NaN | 11.5805 | 90.8519 | NaN | NaN | NaN | 11.1159 | NaN | NaN | NaN | 27.4148 | 564.7223 | NaN | 30.9279 | NaN | 25.4454
348.1292 | 11.336 | 11.6277 | 11.3825 | 11.7954 | 11.11 | 11.9635 | 11.6288 | 11.2616 | NaN | NaN | NaN | 11.5815 | 93.9616 | NaN | NaN | NaN | -9.8983 | NaN | NaN | NaN | 23.6301 | 565.0216 | NaN | 29.8644 | NaN | 22.9184
349.1292 | 11.4673 | 11.4543 | 11.3857 | 11.8378 | 11.0464 | 11.9302 | 11.5435 | 11.261 | NaN | NaN | NaN | 11.5974 | 96.946 | NaN | NaN | NaN | -12.1391 | NaN | NaN | NaN | 26.5283 | 565.2657 | NaN | 31.1815 | NaN | 23.3664
350.1292 | 11.3774 | 11.3915 | 11.3844 | 11.6931 | 11.0463 | 11.8265 | 11.5262 | 11.2652 | NaN | NaN | NaN | 11.5744 | 93.9362 | NaN | NaN | NaN | -19.4897 | NaN | NaN | NaN | 26.0206 | 566.4458 | NaN | 32.3208 | NaN | 22.4538
351.1292 | 11.3126 | 11.3026 | 11.382 | 11.6894 | 11.1157 | 11.8083 | 11.5185 | 11.2597 | NaN | NaN | NaN | 11.6939 | 95.4063 | NaN | NaN | NaN | -15.2684 | NaN | NaN | NaN | 25.8462 | 567.2462 | NaN | 28.084 | NaN | 21.2414
352.1292 | 11.2902 | 11.404 | 11.3913 | 11.8863 | 10.954 | 11.892 | 11.5552 | 11.2663 | NaN | NaN | NaN | 11.5867 | 97.972 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 27.1417 | 566.0347 | NaN | 30.0189 | NaN | 24.2118
353.1292 | 11.3909 | 11.634 | 11.3869 | 11.6869 | 10.9647 | 12.0708 | 11.5912 | 11.2667 | NaN | NaN | NaN | 11.6542 | 92.6066 | NaN | NaN | NaN | -6.7886 | NaN | NaN | NaN | 27.6172 | 568.7634 | NaN | 31.2473 | NaN | 26.1836
354.1292 | 11.343 | 11.4285 | 11.3928 | 11.6955 | 11.0363 | 11.8267 | 11.5549 | 11.2662 | NaN | NaN | NaN | 11.5646 | 94.203 | NaN | NaN | NaN | -12.3435 | NaN | NaN | NaN | 26.7284 | 568.1972 | NaN | 31.1932 | NaN | 21.1218
355.1292 | 11.2973 | 11.6778 | 11.3874 | 11.687 | 11.0154 | 12.0838 | 11.5765 | 11.2723 | NaN | NaN | NaN | 11.6693 | 95.9866 | NaN | NaN | NaN | -17.5568 | NaN | NaN | NaN | 27.4911 | 568.9687 | NaN | 31.5263 | NaN | 27.3792
356.1292 | 11.3494 | 11.3626 | 11.3906 | 11.9548 | 11.0219 | 11.846 | 11.5352 | 11.2602 | NaN | NaN | NaN | 11.5378 | 93.7708 | NaN | NaN | NaN | -17.9877 | NaN | NaN | NaN | 27.7222 | 568.3191 | NaN | 29.6702 | NaN | 22.5035
357.1292 | 11.2924 | 11.4187 | 11.3909 | 11.7597 | 11.0274 | 11.974 | 11.5682 | 11.2614 | NaN | NaN | NaN | 11.6451 | 93.9433 | NaN | NaN | NaN | -8.6967 | NaN | NaN | NaN | 25.2129 | 569.6906 | NaN | 30.607 | NaN | 24.715
358.1292 | 11.3712 | 11.3389 | 11.3937 | 11.6582 | 11.1573 | 11.8059 | 11.5078 | 11.2633 | NaN | NaN | NaN | 11.6579 | 100.6149 | NaN | NaN | NaN | -16.5905 | NaN | NaN | NaN | 28.6792 | 569.8034 | NaN | 32.2046 | NaN | 21.8367
359.1292 | 11.3533 | 11.3218 | 11.3833 | 11.7151 | 11.0621 | 11.8199 | 11.5253 | 11.2631 | NaN | NaN | NaN | 11.6239 | 95.0528 | NaN | NaN | NaN | -17.0569 | NaN | NaN | NaN | 28.4273 | 569.4361 | NaN | 28.9043 | NaN | 25.4366
360.1292 | 11.3707 | 11.4473 | 11.3935 | 11.7038 | 11.0367 | 11.8952 | 11.5575 | 11.2695 | NaN | NaN | NaN | 11.6584 | 94.6013 | NaN | NaN | NaN | -7.1419 | NaN | NaN | NaN | 26.33 | 568.7078 | NaN | 30.8751 | NaN | 20.5716
361.1292 | 11.2856 | 11.2191 | 11.3889 | 11.7484 | 11.1425 | 11.7139 | 11.4729 | 11.2706 | NaN | NaN | NaN | 11.6338 | 91.6861 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 25.9068 | 569.4626 | NaN | 30.1492 | NaN | 22.0943
362.1292 | 11.2738 | 11.766 | 11.3945 | 11.7564 | 10.9523 | 11.9588 | 11.6289 | 11.266 | NaN | NaN | NaN | 11.675 | 93.2348 | NaN | NaN | NaN | -16.922 | NaN | NaN | NaN | 25.3392 | 569.5216 | NaN | 31.5906 | NaN | 22.9961
363.1292 | 11.2929 | 11.3485 | 11.3894 | 11.6859 | 11.0024 | 11.8375 | 11.5133 | 11.2717 | NaN | NaN | NaN | 11.6372 | 90.4762 | NaN | NaN | NaN | 3.3058 | NaN | NaN | NaN | 25.4059 | 570.0949 | NaN | 30.0533 | NaN | 21.4811
364.1292 | 11.3439 | 11.6396 | 11.3901 | 11.6808 | 11.0809 | 11.9222 | 11.5903 | 11.263 | NaN | NaN | NaN | 11.6534 | 92.1398 | NaN | NaN | NaN | -15.0757 | NaN | NaN | NaN | 27.2765 | 571.8443 | NaN | 30.5141 | NaN | 28.2144
365.1292 | 11.4713 | 11.4797 | 11.3934 | 11.6543 | 11.0118 | 11.9727 | 11.5779 | 11.261 | NaN | NaN | NaN | 11.601 | 91.7022 | NaN | NaN | NaN | -13.7576 | NaN | NaN | NaN | 27.9404 | 572.4292 | NaN | 29.9067 | NaN | 21.5208
366.1292 | 11.3131 | 11.5253 | 11.3968 | 11.7983 | 10.9603 | 11.9642 | 11.577 | 11.2654 | NaN | NaN | NaN | 11.5865 | 95.9373 | NaN | NaN | NaN | -19.3232 | NaN | NaN | NaN | 28.4001 | 571.7157 | NaN | 30.0895 | NaN | 21.6848
367.1292 | 11.2584 | 11.4272 | 11.3936 | 11.6591 | 11.0804 | 11.8796 | 11.5445 | 11.2663 | NaN | NaN | NaN | 11.6758 | 92.7141 | NaN | NaN | NaN | -18.3124 | NaN | NaN | NaN | 26.7196 | 573.5096 | NaN | 30.5276 | NaN | 25.3798
368.1292 | 11.3543 | 11.3543 | 11.3914 | 11.6683 | 10.9847 | 11.8793 | 11.5336 | 11.2645 | NaN | NaN | NaN | 11.6565 | 91.7596 | NaN | NaN | NaN | -10.6685 | NaN | NaN | NaN | 29.1335 | 574.4987 | NaN | 30.4744 | NaN | 25.6091
369.1292 | 11.3011 | 11.2612 | 11.4027 | 11.7624 | 11.1405 | 11.7738 | 11.5005 | 11.2682 | NaN | NaN | NaN | 11.6062 | 91.3642 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 25.706 | 574.488 | NaN | 31.1752 | NaN | 23.2479
370.1292 | 11.4102 | 11.4007 | 11.397 | 11.6688 | 11.0944 | 11.8228 | 11.5297 | 11.2658 | NaN | NaN | NaN | 11.7061 | 92.1386 | NaN | NaN | NaN | -11.2752 | NaN | NaN | NaN | 26.2155 | 573.122 | NaN | 29.2984 | NaN | 22.9517
371.1292 | 11.4447 | 11.5335 | 11.4038 | 11.7644 | 11.106 | 11.9757 | 11.5978 | 11.2693 | NaN | NaN | NaN | 11.6458 | 91.6988 | NaN | NaN | NaN | -13.649 | NaN | NaN | NaN | 27.4622 | 575.4242 | NaN | 31.0938 | NaN | 18.8162
372.1292 | 11.3888 | 11.4053 | 11.4008 | 11.7517 | 10.9942 | 12.063 | 11.5641 | 11.2704 | NaN | NaN | NaN | 11.6801 | 94.365 | NaN | NaN | NaN | -19.9662 | NaN | NaN | NaN | 28.2942 | 575.4886 | NaN | 29.3617 | NaN | 22.8907
373.1292 | 11.2406 | 11.3665 | 11.406 | 11.859 | 11.1032 | 11.8743 | 11.5191 | 11.2712 | NaN | NaN | NaN | 11.6014 | 92.4935 | NaN | NaN | NaN | -18.7919 | NaN | NaN | NaN | 25.0597 | 578.38 | NaN | 30.8216 | NaN | 24.9617
374.1292 | 11.345 | 11.3154 | 11.3981 | 11.8626 | 11.0573 | 11.9041 | 11.5293 | 11.2736 | NaN | NaN | NaN | 11.6454 | 91.9262 | NaN | NaN | NaN | -17.1656 | NaN | NaN | NaN | 25.7814 | 576.4044 | NaN | 30.8293 | NaN | 23.6192
375.1292 | 11.3459 | 11.4024 | 11.4028 | 11.689 | 10.9844 | 11.8293 | 11.5481 | 11.2729 | NaN | NaN | NaN | 11.5772 | 94.378 | NaN | NaN | NaN | -17.0687 | NaN | NaN | NaN | 29.4733 | 578.4709 | NaN | 30.3007 | NaN | 27.6418
376.1292 | 11.3394 | 11.343 | 11.405 | 11.6912 | 11.0745 | 11.8554 | 11.536 | 11.2741 | NaN | NaN | NaN | 11.5947 | 95.0912 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 24.0649 | 577.7457 | NaN | 29.2055 | NaN | 24.7835
377.1292 | 11.7347 | 11.3314 | 11.4019 | 11.723 | 11.0617 | 11.816 | 11.5337 | 11.2801 | NaN | NaN | NaN | 11.7273 | 91.6278 | NaN | NaN | NaN | 5.4763 | NaN | NaN | NaN | 26.4753 | 578.0076 | NaN | 28.6623 | NaN | 21.9801
378.1292 | 11.2854 | 11.9088 | 11.4003 | 11.7471 | 11.1095 | 12.0197 | 11.6722 | 11.2699 | NaN | NaN | NaN | 11.5807 | 93.4765 | NaN | NaN | NaN | -16.357 | NaN | NaN | NaN | 29.4871 | 578.7127 | NaN | 27.4736 | NaN | 19.8805
379.1292 | 11.2873 | 11.4138 | 11.4029 | 11.8156 | 10.9901 | 11.9796 | 11.5688 | 11.278 | NaN | NaN | NaN | 11.6127 | 94.8559 | NaN | NaN | NaN | -8.5919 | NaN | NaN | NaN | 26.9824 | 578.7588 | NaN | 28.522 | NaN | 21.2272
380.1292 | 11.3162 | 11.299 | 11.4065 | 11.8292 | 10.9607 | 11.7153 | 11.476 | 11.2773 | NaN | NaN | NaN | 11.6502 | 92.3979 | NaN | NaN | NaN | -14.0392 | NaN | NaN | NaN | 26.4252 | 576.5549 | NaN | 32.1688 | NaN | 25.176
381.1292 | 11.3814 | 11.415 | 11.4125 | 11.7572 | 11.067 | 11.8894 | 11.5483 | 11.2749 | NaN | NaN | NaN | 11.6756 | 94.5713 | NaN | NaN | NaN | -10.6373 | NaN | NaN | NaN | 25.8099 | 578.2991 | NaN | 30.7796 | NaN | 22.752
382.1292 | 11.3289 | 11.4786 | 11.4138 | 11.7444 | 11.144 | 11.9052 | 11.5723 | 11.2724 | NaN | NaN | NaN | 11.5963 | 92.505 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 25.8663 | 580.5595 | NaN | 30.9446 | NaN | 23.2158
383.1292 | 11.3093 | 11.3344 | 11.413 | 11.7112 | 11.0331 | 11.7706 | 11.5216 | 11.2759 | NaN | NaN | NaN | 11.6359 | 94.2978 | NaN | NaN | NaN | -6.5667 | NaN | NaN | NaN | 27.105 | 581.3363 | NaN | 29.9969 | NaN | 23.5314
384.1292 | 11.3738 | 11.4612 | 11.4159 | 11.7043 | 11.0031 | 11.8818 | 11.5909 | 11.2769 | NaN | NaN | NaN | 11.614 | 93.5286 | NaN | NaN | NaN | -19.0393 | NaN | NaN | NaN | 26.3059 | 578.6976 | NaN | 30.2882 | NaN | 25.5725
385.1292 | 11.2673 | 11.5537 | 11.4109 | 11.7632 | 11.0295 | 11.8639 | 11.5591 | 11.2774 | NaN | NaN | NaN | 11.7142 | 92.2336 | NaN | NaN | NaN | -5.1827 | NaN | NaN | NaN | 23.7058 | 581.2921 | NaN | 30.5409 | NaN | 23.2456
386.1292 | 11.3492 | 11.3363 | 11.4121 | 11.7777 | 11.1198 | 11.787 | 11.5216 | 11.2752 | NaN | NaN | NaN | 11.6765 | 92.7932 | NaN | NaN | NaN | -0.0592 | NaN | NaN | NaN | 25.4101 | 581.0471 | NaN | 29.843 | NaN | 23.9104
387.1292 | 11.2735 | 11.3323 | 11.4059 | 11.7644 | 11.1994 | 11.835 | 11.5231 | 11.279 | NaN | NaN | NaN | 11.6505 | 94.7107 | NaN | NaN | NaN | -0.5853 | NaN | NaN | NaN | 27.6756 | 583.6203 | NaN | 30.3477 | NaN | 25.8213
388.1292 | 11.3737 | 11.4126 | 11.4111 | 11.6469 | 11.0598 | 11.8949 | 11.5597 | 11.2811 | NaN | NaN | NaN | 11.5838 | 93.9245 | NaN | NaN | NaN | -12.9581 | NaN | NaN | NaN | 23.4961 | 582.4074 | NaN | 32.1618 | NaN | 28.2388
389.1292 | 11.3429 | 11.4437 | 11.4118 | 11.7068 | 10.9621 | 11.8252 | 11.5741 | 11.2821 | NaN | NaN | NaN | 11.5908 | 92.9582 | NaN | NaN | NaN | -19.3843 | NaN | NaN | NaN | 23.7949 | 581.0802 | NaN | 32.1346 | NaN | 27.011
390.1292 | 11.2738 | 11.3875 | 11.4098 | 11.6552 | 11.0623 | 11.8411 | 11.5336 | 11.2779 | NaN | NaN | NaN | 11.6107 | 95.7323 | NaN | NaN | NaN | -18.5465 | NaN | NaN | NaN | 26.6523 | 582.936 | NaN | 30.2962 | NaN | 23.0668
391.1292 | 11.258 | 11.4912 | 11.4097 | 11.7486 | 10.9722 | 11.8758 | 11.5787 | 11.2743 | NaN | NaN | NaN | 11.6247 | 90.3433 | NaN | NaN | NaN | 2.4344 | NaN | NaN | NaN | 27.5908 | 584.0964 | NaN | 30.8983 | NaN | 22.9335
392.1292 | 11.3009 | 11.3171 | 11.4146 | 11.7378 | 11.034 | 11.9419 | 11.5149 | 11.2771 | NaN | NaN | NaN | 11.6268 | 90.434 | NaN | NaN | NaN | -13.9507 | NaN | NaN | NaN | 27.5789 | 582.5671 | NaN | 30.2984 | NaN | 24.614
393.1292 | 11.2877 | 11.4326 | 11.4141 | 11.7376 | 11.0708 | 11.7891 | 11.5437 | 11.2785 | NaN | NaN | NaN | 11.7445 | 93.9728 | NaN | NaN | NaN | -17.8327 | NaN | NaN | NaN | 28.1913 | 581.0154 | NaN | 31.6374 | NaN | 25.0385
394.1292 | 11.3226 | 11.3525 | 11.4123 | 11.7205 | 11.0477 | 11.792 | 11.5364 | 11.2766 | NaN | NaN | NaN | 11.6624 | 94.5366 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 26.1132 | 581.4883 | NaN | 30.9986 | NaN | 29.6656
395.1292 | 11.3477 | 11.3231 | 11.4044 | 11.6419 | 11.0785 | 11.8293 | 11.5225 | 11.2757 | NaN | NaN | NaN | 11.6519 | 94.5566 | NaN | NaN | NaN | -17.7699 | NaN | NaN | NaN | 26.7819 | 583.1196 | NaN | 30.4825 | NaN | 23.687
396.1292 | 11.3208 | 11.3163 | 11.4088 | 11.6449 | 11.0408 | 11.8381 | 11.535 | 11.2793 | NaN | NaN | NaN | 11.5455 | 91.2394 | NaN | NaN | NaN | -9.3329 | NaN | NaN | NaN | 25.7757 | 582.7581 | NaN | 30.3775 | NaN | 24.8062
397.1292 | 11.343 | 11.3929 | 11.4119 | 11.7759 | 10.9556 | 11.8893 | 11.552 | 11.2808 | NaN | NaN | NaN | 11.7014 | 100.5207 | NaN | NaN | NaN | -18.4397 | NaN | NaN | NaN | 25.9812 | 583.4539 | NaN | 32.0331 | NaN | 27.038
398.1292 | 11.3124 | 11.328 | 11.4121 | 11.7255 | 11.0645 | 11.8472 | 11.5558 | 11.2793 | NaN | NaN | NaN | 11.6919 | 92.5703 | NaN | NaN | NaN | -19.8204 | NaN | NaN | NaN | 26.4458 | 582.9868 | NaN | 30.3357 | NaN | 22.4645
399.1292 | 11.3509 | 11.7321 | 11.41 | 11.7065 | 11.0124 | 12.0034 | 11.62 | 11.2765 | NaN | NaN | NaN | 11.6202 | 95.1269 | NaN | NaN | NaN | -14.9421 | NaN | NaN | NaN | 28.432 | 582.8302 | NaN | 28.3368 | NaN | 23.5844
400.1292 | 11.38 | 11.4451 | 11.4207 | 11.6777 | 11.0417 | 11.8247 | 11.5536 | 11.2867 | NaN | NaN | NaN | 11.6233 | 95.7762 | NaN | NaN | NaN | -15.0557 | NaN | NaN | NaN | 26.0179 | 582.1097 | NaN | 29.4104 | NaN | 23.7728
401.1292 | 11.3272 | 11.3795 | 11.4192 | 11.7479 | 11.029 | 11.7896 | 11.5328 | 11.2778 | NaN | NaN | NaN | 11.6452 | 92.9336 | NaN | NaN | NaN | -15.1972 | NaN | NaN | NaN | 28.9119 | 581.1756 | NaN | 29.4951 | NaN | 20.9772
402.1292 | 11.3802 | 11.5103 | 11.4192 | 12.0219 | 11.0324 | 11.8906 | 11.5861 | 11.2852 | NaN | NaN | NaN | 11.6901 | 94.4624 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 27.6379 | 583.412 | NaN | 31.7539 | NaN | 21.3851
403.1292 | 11.3508 | 11.4721 | 11.4204 | 11.7374 | 10.9897 | 12.0076 | 11.5763 | 11.2821 | NaN | NaN | NaN | 11.6123 | 93.0593 | NaN | NaN | NaN | -16.8412 | NaN | NaN | NaN | 29.4183 | 584.8133 | NaN | 30.066 | NaN | 19.989
404.1292 | 11.3113 | 11.6305 | 11.421 | 11.7096 | 11.091 | 11.8507 | 11.627 | 11.2803 | NaN | NaN | NaN | 11.6294 | 92.5524 | NaN | NaN | NaN | -16.2158 | NaN | NaN | NaN | 26.4532 | 583.8519 | NaN | 30.9177 | NaN | 25.6552
405.1292 | 11.4337 | 11.4547 | 11.4197 | 11.7656 | 11.0689 | 11.8787 | 11.5588 | 11.285 | NaN | NaN | NaN | 11.5951 | 93.8833 | NaN | NaN | NaN | -15.193 | NaN | NaN | NaN | 25.9767 | 584.2082 | NaN | 28.7062 | NaN | 21.5805
406.1292 | 11.2739 | 11.5339 | 11.4163 | 11.6928 | 10.981 | 11.9209 | 11.5741 | 11.2833 | NaN | NaN | NaN | 11.6118 | 92.1471 | NaN | NaN | NaN | 1.4713 | NaN | NaN | NaN | 28.8329 | 584.1645 | NaN | 30.0083 | NaN | 21.468
407.1292 | 11.3023 | 11.3522 | 11.4127 | 11.7326 | 11.0846 | 11.897 | 11.5404 | 11.2813 | NaN | NaN | NaN | 11.6848 | 91.1853 | NaN | NaN | NaN | -11.1061 | NaN | NaN | NaN | 26.2528 | 581.0203 | NaN | 29.1164 | NaN | 27.7969
408.1292 | 11.3062 | 11.4239 | 11.4174 | 11.6494 | 11.1509 | 11.9699 | 11.5622 | 11.2738 | NaN | NaN | NaN | 11.6751 | 93.8894 | NaN | NaN | NaN | -19.4165 | NaN | NaN | NaN | 30.9945 | 581.9001 | NaN | 29.578 | NaN | 24.8645
409.1292 | 11.2826 | 11.3273 | 11.4145 | 11.7265 | 11.0712 | 11.8243 | 11.5372 | 11.2853 | NaN | NaN | NaN | 11.6305 | 91.1058 | NaN | NaN | NaN | -3.9711 | NaN | NaN | NaN | 28.2289 | 584.0194 | NaN | 31.6042 | NaN | 22.7424
410.1292 | 11.3242 | 11.3588 | 11.4095 | 11.7244 | 11.1065 | 11.8793 | 11.5506 | 11.2851 | NaN | NaN | NaN | 11.784 | 96.4347 | NaN | NaN | NaN | -16.147 | NaN | NaN | NaN | 29.7515 | 583.0319 | NaN | 30.3487 | NaN | 27.0137
411.1292 | 11.3177 | 11.3783 | 11.4092 | 11.7329 | 11.0243 | 11.8952 | 11.5405 | 11.2824 | NaN | NaN | NaN | 11.6054 | 91.2739 | NaN | NaN | NaN | -19.4464 | NaN | NaN | NaN | 26.1942 | 582.4344 | NaN | 31.0804 | NaN | 23.1364
412.1292 | 11.3458 | 11.4165 | 11.4104 | 11.6983 | 11.1038 | 11.9689 | 11.5701 | 11.2912 | NaN | NaN | NaN | 11.6266 | 92.1252 | NaN | NaN | NaN | -19.1595 | NaN | NaN | NaN | 30.0444 | 582.9088 | NaN | 31.1074 | NaN | 23.7865
413.1292 | 11.3149 | 11.4226 | 11.4108 | 11.7154 | 11.0196 | 11.8741 | 11.5724 | 11.2854 | NaN | NaN | NaN | 11.649 | 96.9812 | NaN | NaN | NaN | -13.3035 | NaN | NaN | NaN | 28.9928 | 581.7895 | NaN | 31.457 | NaN | 27.8511
414.1292 | 11.4437 | 11.4119 | 11.401 | 11.7464 | 11.0249 | 11.8607 | 11.5631 | 11.284 | NaN | NaN | NaN | 11.703 | 91.539 | NaN | NaN | NaN | -7.2564 | NaN | NaN | NaN | 27.9131 | 582.0539 | NaN | 30.7967 | NaN | 23.2806
415.1292 | 11.2847 | 11.3038 | 11.409 | 11.7102 | 11.1406 | 11.7646 | 11.5185 | 11.2848 | NaN | NaN | NaN | 11.6806 | 88.6574 | NaN | NaN | NaN | -9.3306 | NaN | NaN | NaN | 27.7241 | 582.3261 | NaN | 29.653 | NaN | 24.3303
416.1292 | 11.2996 | 11.7856 | 11.406 | 11.7564 | 11.0695 | 11.9289 | 11.6504 | 11.2873 | NaN | NaN | NaN | 11.717 | 92.4305 | NaN | NaN | NaN | 0.0326 | NaN | NaN | NaN | 27.483 | 580.3564 | NaN | 32.7442 | NaN | 21.8342
417.1292 | 11.3086 | 11.406 | 11.409 | 11.7816 | 10.9995 | 11.9186 | 11.5479 | 11.2826 | NaN | NaN | NaN | 11.6348 | 100.0739 | NaN | NaN | NaN | -14.2399 | NaN | NaN | NaN | 29.1519 | 581.8595 | NaN | 30.6617 | NaN | 24.7202
418.1292 | 11.3436 | 11.3935 | 11.4084 | 11.793 | 11.0865 | 11.9259 | 11.5485 | 11.2802 | NaN | NaN | NaN | 11.6275 | 94.1321 | NaN | NaN | NaN | -13.4378 | NaN | NaN | NaN | 26.5607 | 581.5595 | NaN | 30.9652 | NaN | 24.1231
419.1292 | 11.3509 | 11.354 | 11.4107 | 11.6735 | 11.1375 | 11.8007 | 11.5424 | 11.2796 | NaN | NaN | NaN | 11.599 | 99.0618 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 27.4036 | 580.4246 | NaN | 29.6246 | NaN | 23.9795
420.1292 | 11.4766 | 11.3379 | 11.4132 | 11.7426 | 11.0538 | 11.8113 | 11.5349 | 11.2869 | NaN | NaN | NaN | 11.612 | 94.2717 | NaN | NaN | NaN | -17.1148 | NaN | NaN | NaN | 27.1959 | 581.2439 | NaN | 32.0463 | NaN | 22.2771
421.1292 | 11.4097 | 11.355 | 11.4017 | 11.7094 | 11.1911 | 11.8038 | 11.5293 | 11.2901 | NaN | NaN | NaN | 11.6453 | 94.3886 | NaN | NaN | NaN | -19.3134 | NaN | NaN | NaN | 22.9618 | 578.8275 | NaN | 28.7791 | NaN | 23.504
422.1292 | 11.3292 | 11.4123 | 11.4031 | 11.7621 | 11.0735 | 11.8153 | 11.5582 | 11.2894 | NaN | NaN | NaN | 11.614 | 93.3489 | NaN | NaN | NaN | -14.7732 | NaN | NaN | NaN | 26.1709 | 581.4073 | NaN | 29.2201 | NaN | 26.8011
423.1292 | 11.3207 | 11.4377 | 11.4115 | 11.7226 | 11.1054 | 11.8504 | 11.5595 | 11.2897 | NaN | NaN | NaN | 11.6266 | 92.7398 | NaN | NaN | NaN | -12.9626 | NaN | NaN | NaN | 27.0347 | 582.3016 | NaN | 31.0744 | NaN | 24.9726
424.1292 | 11.3797 | 11.5845 | 11.4104 | 11.6892 | 10.9922 | 11.993 | 11.5834 | 11.2804 | NaN | NaN | NaN | 11.645 | 93.5681 | NaN | NaN | NaN | -19.8923 | NaN | NaN | NaN | 29.2381 | 580.236 | NaN | 30.0683 | NaN | 22.4963
425.1292 | 11.2734 | 11.2944 | 11.4072 | 11.723 | 11.1056 | 11.7518 | 11.5084 | 11.2856 | NaN | NaN | NaN | 11.6619 | 93.4247 | NaN | NaN | NaN | 4.0774 | NaN | NaN | NaN | 27.2067 | 580.399 | NaN | 30.7281 | NaN | 19.9958
426.1292 | 11.3472 | 11.6639 | 11.4072 | 11.6956 | 11.1195 | 11.9173 | 11.6679 | 11.2868 | NaN | NaN | NaN | 11.7127 | 93.584 | NaN | NaN | NaN | -19.3031 | NaN | NaN | NaN | 26.4197 | 580.0175 | NaN | 30.9071 | NaN | 24.8755
427.1292 | 11.4258 | 11.7141 | 11.4137 | 11.7221 | 11.0851 | 11.9563 | 11.6524 | 11.2878 | NaN | NaN | NaN | 11.5991 | 92.0118 | NaN | NaN | NaN | -14.8467 | NaN | NaN | NaN | 25.8122 | 580.7787 | NaN | 29.7209 | NaN | 21.4078
428.1292 | 11.3373 | 11.4524 | 11.4157 | 11.6649 | 11.0537 | 11.8909 | 11.5792 | 11.287 | NaN | NaN | NaN | 11.6594 | 90.6983 | NaN | NaN | NaN | 1.7149 | NaN | NaN | NaN | 28.4294 | 581.4474 | NaN | 28.6952 | NaN | 21.628
429.1292 | 11.3522 | 11.4057 | 11.4168 | 11.7288 | 11.0687 | 11.8309 | 11.5493 | 11.2873 | NaN | NaN | NaN | 11.6431 | 93.4952 | NaN | NaN | NaN | -19.4165 | NaN | NaN | NaN | 27.8138 | 583.4267 | NaN | 30.3664 | NaN | 23.5829
430.1292 | 11.3121 | 11.425 | 11.4137 | 11.6712 | 11.0581 | 11.8547 | 11.5753 | 11.2942 | NaN | NaN | NaN | 11.6951 | 95.2668 | NaN | NaN | NaN | -13.5711 | NaN | NaN | NaN | 27.4991 | 582.6731 | NaN | 30.5791 | NaN | 24.3895
431.1292 | 11.3093 | 11.3418 | 11.4116 | 11.6892 | 11.0482 | 11.8207 | 11.5569 | 11.2852 | NaN | NaN | NaN | 11.6407 | 91.4763 | NaN | NaN | NaN | -12.6476 | NaN | NaN | NaN | 28.6962 | 584.0415 | NaN | 30.1069 | NaN | 25.6825
432.1292 | 11.3802 | 11.347 | 11.4154 | 11.6995 | 11.1501 | 11.7932 | 11.5323 | 11.2857 | NaN | NaN | NaN | 11.6932 | 91.6318 | NaN | NaN | NaN | -18.5885 | NaN | NaN | NaN | 26.6412 | 581.6463 | NaN | 29.5939 | NaN | 24.6942
433.1292 | 11.3702 | 11.6024 | 11.414 | 11.7123 | 11.1086 | 12.0508 | 11.5977 | 11.2902 | NaN | NaN | NaN | 11.6612 | 91.1798 | NaN | NaN | NaN | -15.7157 | NaN | NaN | NaN | 27.4402 | 582.2007 | NaN | 30.7284 | NaN | 21.736
434.1292 | 11.3065 | 11.6948 | 11.4124 | 11.7728 | 11.0143 | 11.8355 | 11.6284 | 11.2877 | NaN | NaN | NaN | 11.732 | 91.0426 | NaN | NaN | NaN | -3.3657 | NaN | NaN | NaN | 29.329 | 582.5108 | NaN | 30.1074 | NaN | 22.6536
435.1292 | 11.3288 | 11.9754 | 11.4116 | 11.7245 | 11.0407 | 11.9135 | 11.7367 | 11.2909 | NaN | NaN | NaN | 11.6839 | 94.7627 | NaN | NaN | NaN | -12.6177 | NaN | NaN | NaN | 29.9951 | 583.4137 | NaN | 31.6865 | NaN | 21.8532
436.1292 | 11.3558 | 11.6377 | 11.4111 | 11.7074 | 11.1924 | 11.9026 | 11.656 | 11.2912 | NaN | NaN | NaN | 11.7128 | 92.622 | NaN | NaN | NaN | -19.5944 | NaN | NaN | NaN | 28.6167 | 582.9549 | NaN | 30.7697 | NaN | 24.2969
437.1292 | 11.3082 | 11.3856 | 11.4148 | 11.686 | 11.0705 | 11.8864 | 11.5606 | 11.2885 | NaN | NaN | NaN | 11.6943 | 93.6557 | NaN | NaN | NaN | -6.8508 | NaN | NaN | NaN | 27.6613 | 582.7131 | NaN | 29.0328 | NaN | 24.737
438.1292 | 11.3749 | 11.3883 | 11.4154 | 11.7259 | 11.1154 | 11.9206 | 11.5693 | 11.2974 | NaN | NaN | NaN | 11.6223 | 93.86 | NaN | NaN | NaN | -7.3705 | NaN | NaN | NaN | 26.9822 | 584.1398 | NaN | 30.8724 | NaN | 20.8965
439.1292 | 11.3483 | 11.4539 | 11.4184 | 11.7595 | 10.9819 | 11.881 | 11.5731 | 11.2901 | NaN | NaN | NaN | 11.6494 | 93.1123 | NaN | NaN | NaN | -19.3094 | NaN | NaN | NaN | 27.0161 | 583.6908 | NaN | 32.1687 | NaN | 26.9704
440.1292 | 11.3608 | 11.5267 | 11.411 | 11.6817 | 10.9931 | 11.9447 | 11.6012 | 11.2878 | NaN | NaN | NaN | 11.6423 | 94.8994 | NaN | NaN | NaN | -12.4376 | NaN | NaN | NaN | 27.6715 | 583.1659 | NaN | 29.4687 | NaN | 25.1955
441.1292 | 11.2728 | 11.6321 | 11.4172 | 11.711 | 11.0313 | 11.9774 | 11.6174 | 11.2858 | NaN | NaN | NaN | 11.6487 | 95.9897 | NaN | NaN | NaN | 9.0134 | NaN | NaN | NaN | 25.09 | 583.443 | NaN | 30.5071 | NaN | 27.7083
442.1292 | 11.3479 | 11.4124 | 11.424 | 11.7462 | 11.0663 | 11.924 | 11.5567 | 11.2833 | NaN | NaN | NaN | 11.6159 | 93.5532 | NaN | NaN | NaN | -13.0773 | NaN | NaN | NaN | 27.6021 | 582.7257 | NaN | 29.3212 | NaN | 24.1825
443.1292 | 11.3568 | 11.4403 | 11.4151 | 11.7572 | 11.0223 | 11.8101 | 11.544 | 11.2921 | NaN | NaN | NaN | 11.7178 | 90.7989 | NaN | NaN | NaN | -12.7972 | NaN | NaN | NaN | 30.0007 | 583.6528 | NaN | 28.7935 | NaN | 23.7716
444.1292 | 11.3225 | 11.3669 | 11.416 | 11.8922 | 11.0248 | 11.8107 | 11.542 | 11.288 | NaN | NaN | NaN | 11.6432 | 95.9666 | NaN | NaN | NaN | -17.0892 | NaN | NaN | NaN | 26.1452 | 584.465 | NaN | 30.4048 | NaN | 26.2961
445.1292 | 11.465 | 11.3283 | 11.4186 | 11.7132 | 11.0327 | 11.7799 | 11.531 | 11.2858 | NaN | NaN | NaN | 11.6596 | 92.6964 | NaN | NaN | NaN | -15.5849 | NaN | NaN | NaN | 26.7954 | 583.1519 | NaN | 29.0118 | NaN | 23.6324
446.1292 | 11.3159 | 11.4886 | 11.4254 | 11.7166 | 11.0046 | 11.8789 | 11.5913 | 11.2893 | NaN | NaN | NaN | 11.5965 | 90.9033 | NaN | NaN | NaN | 0.3589 | NaN | NaN | NaN | 25.3814 | 585.9555 | NaN | 29.8747 | NaN | 22.8796
447.1292 | 11.3442 | 11.3949 | 11.4193 | 11.7101 | 11.0676 | 11.9131 | 11.5749 | 11.2801 | NaN | NaN | NaN | 11.7504 | 92.7383 | NaN | NaN | NaN | -6.909 | NaN | NaN | NaN | 26.1761 | 585.6856 | NaN | 30.9244 | NaN | 22.1233
448.1292 | 11.4461 | 11.4196 | 11.4209 | 11.8944 | 10.9741 | 11.8911 | 11.5631 | 11.2888 | NaN | NaN | NaN | 11.607 | 94.7654 | NaN | NaN | NaN | -10.5887 | NaN | NaN | NaN | 27.75 | 585.4978 | NaN | 29.4617 | NaN | 23.1597
449.1292 | 11.3754 | 11.4702 | 11.4211 | 11.7018 | 11.0302 | 11.8894 | 11.5839 | 11.2878 | NaN | NaN | NaN | 11.7204 | 92.9593 | NaN | NaN | NaN | -18.569 | NaN | NaN | NaN | 27.317 | 587.7479 | NaN | 30.3306 | NaN | 23.4327
450.1292 | 11.3955 | 11.3702 | 11.4221 | 11.9045 | 10.9734 | 11.8396 | 11.5446 | 11.2877 | NaN | NaN | NaN | 11.6708 | 92.3991 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 28.2633 | 586.5182 | NaN | 30.794 | NaN | 28.3494
451.1292 | 11.3537 | 11.4933 | 11.4247 | 11.6818 | 11.0784 | 11.8075 | 11.5939 | 11.2852 | NaN | NaN | NaN | 11.7376 | 90.5018 | NaN | NaN | NaN | -18.6688 | NaN | NaN | NaN | 26.8891 | 588.4958 | NaN | 31.6503 | NaN | 23.0672
452.1292 | 11.3339 | 11.5091 | 11.4279 | 12.0491 | 11.1413 | 11.9515 | 11.6004 | 11.2857 | NaN | NaN | NaN | 11.7059 | 91.8358 | NaN | NaN | NaN | -13.5937 | NaN | NaN | NaN | 27.4052 | 589.1505 | NaN | 29.7017 | NaN | 21.5891
453.1292 | 11.4345 | 11.5099 | 11.4282 | 11.7583 | 11.0729 | 11.9953 | 11.6062 | 11.2815 | NaN | NaN | NaN | 11.6475 | 92.9008 | NaN | NaN | NaN | -18.5856 | NaN | NaN | NaN | 27.4444 | 589.1512 | NaN | 28.3279 | NaN | 21.5603
454.1292 | 11.3306 | 11.5472 | 11.4229 | 11.7308 | 10.9754 | 12.002 | 11.6191 | 11.2908 | NaN | NaN | NaN | 11.6842 | 93.4331 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 26.9802 | 589.5894 | NaN | 30.6632 | NaN | 23.9365
455.1292 | 11.4889 | 11.5259 | 11.4224 | 11.7943 | 11.0726 | 11.9656 | 11.6114 | 11.291 | NaN | NaN | NaN | 11.6241 | 94.3975 | NaN | NaN | NaN | -16.8624 | NaN | NaN | NaN | 27.5567 | 588.2948 | NaN | 31.8469 | NaN | 25.979
456.1292 | 11.3059 | 11.3785 | 11.4137 | 11.7092 | 11.0977 | 11.8108 | 11.5504 | 11.2949 | NaN | NaN | NaN | 11.6843 | 92.0103 | NaN | NaN | NaN | -2.8342 | NaN | NaN | NaN | 26.0469 | 587.8969 | NaN | 31.2313 | NaN | 20.3061
457.1292 | 11.3426 | 11.3744 | 11.4182 | 11.7464 | 11.1154 | 11.7702 | 11.5308 | 11.2942 | NaN | NaN | NaN | 11.6249 | 92.9084 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 26.7613 | 586.6001 | NaN | 29.7651 | NaN | 25.1195
458.1292 | 11.3151 | 11.5908 | 11.4093 | 11.9709 | 11.0919 | 11.9463 | 11.6107 | 11.2975 | NaN | NaN | NaN | 11.7193 | 92.3431 | NaN | NaN | NaN | -15.345 | NaN | NaN | NaN | 26.9467 | 588.1503 | NaN | 30.1932 | NaN | 23.5832
459.1292 | 11.3506 | 11.5621 | 11.4121 | 11.7093 | 11.1206 | 11.9726 | 11.5935 | 11.2958 | NaN | NaN | NaN | 11.6176 | 91.4917 | NaN | NaN | NaN | -16.2253 | NaN | NaN | NaN | 25.3395 | 589.0481 | NaN | 29.8438 | NaN | 21.5299
460.1292 | 11.4012 | 11.3964 | 11.4156 | 11.7014 | 11.0579 | 11.7984 | 11.5617 | 11.2971 | NaN | NaN | NaN | 11.633 | 93.3006 | NaN | NaN | NaN | -17.6477 | NaN | NaN | NaN | 26.2488 | 588.2927 | NaN | 30.3401 | NaN | 23.8742
461.1292 | 11.3956 | 11.3221 | 11.4158 | 11.7504 | 11.1142 | 11.7281 | 11.5227 | 11.2935 | NaN | NaN | NaN | 11.6487 | 92.2689 | NaN | NaN | NaN | -15.4407 | NaN | NaN | NaN | 28.801 | 588.7469 | NaN | 30.8507 | NaN | 25.0319
462.1292 | 11.3202 | 11.4546 | 11.4182 | 11.8282 | 11.0535 | 11.8724 | 11.5833 | 11.2992 | NaN | NaN | NaN | 11.6683 | 93.2637 | NaN | NaN | NaN | 6.9088 | NaN | NaN | NaN | 25.7072 | 587.686 | NaN | 30.3656 | NaN | 25.4949
463.1292 | 11.4819 | 11.495 | 11.4197 | 11.7331 | 11.0689 | 11.8727 | 11.5705 | 11.2998 | NaN | NaN | NaN | 11.6158 | 90.2632 | NaN | NaN | NaN | -18.5671 | NaN | NaN | NaN | 27.3222 | 588.1419 | NaN | 29.7962 | NaN | 25.9362
464.1292 | 11.3476 | 11.3904 | 11.4158 | 11.8077 | 11.0277 | 11.8007 | 11.5497 | 11.2949 | NaN | NaN | NaN | 11.7029 | 92.4014 | NaN | NaN | NaN | -15.144 | NaN | NaN | NaN | 26.61 | 587.0539 | NaN | 30.296 | NaN | 22.2342
465.1292 | 11.3647 | 11.5082 | 11.4197 | 11.747 | 11.0658 | 11.9123 | 11.6097 | 11.2972 | NaN | NaN | NaN | 11.7348 | 95.432 | NaN | NaN | NaN | -18.7114 | NaN | NaN | NaN | 28.0794 | 588.472 | NaN | 29.6299 | NaN | 24.2475
466.1292 | 11.3861 | 11.6525 | 11.4273 | 11.7218 | 10.9487 | 11.8514 | 11.6032 | 11.3026 | NaN | NaN | NaN | 11.744 | 90.6423 | NaN | NaN | NaN | -8.4868 | NaN | NaN | NaN | 28.6049 | 589.1259 | NaN | 30.3788 | NaN | 27.3686
467.1292 | 11.3038 | 11.7228 | 11.4212 | 11.7026 | 11.0637 | 11.8434 | 11.6699 | 11.3022 | NaN | NaN | NaN | 11.7002 | 92.4909 | NaN | NaN | NaN | -18.5843 | NaN | NaN | NaN | 28.1616 | 586.2729 | NaN | 28.9104 | NaN | 22.2938
468.1292 | 11.4187 | 11.6605 | 11.42 | 12.0718 | 10.9431 | 12.0599 | 11.6343 | 11.3041 | NaN | NaN | NaN | 11.6085 | 91.678 | NaN | NaN | NaN | -13.035 | NaN | NaN | NaN | 24.9034 | 587.372 | NaN | 29.8976 | NaN | 18.9528
469.1292 | 11.4287 | 11.433 | 11.4269 | 11.7124 | 11.0102 | 11.9902 | 11.5677 | 11.3048 | NaN | NaN | NaN | 11.614 | 94.6341 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 27.4966 | 589.2901 | NaN | 30.4999 | NaN | 21.436
470.1292 | 11.3599 | 11.5394 | 11.4202 | 11.8317 | 11.0627 | 12.0157 | 11.6102 | 11.3034 | NaN | NaN | NaN | 11.6889 | 94.4644 | NaN | NaN | NaN | -8.3897 | NaN | NaN | NaN | 25.0998 | 587.2635 | NaN | 31.0646 | NaN | 25.7807
471.1292 | 11.4279 | 11.6074 | 11.4256 | 11.7185 | 11.0808 | 12.0636 | 11.6333 | 11.301 | NaN | NaN | NaN | 11.6473 | 94.9066 | NaN | NaN | NaN | -10.6461 | NaN | NaN | NaN | 26.1559 | 588.0095 | NaN | 30.7493 | NaN | 24.9651
472.1292 | 11.3736 | 11.6464 | 11.4274 | 11.722 | 11.116 | 12.0692 | 11.6596 | 11.2996 | NaN | NaN | NaN | 11.5899 | 94.4963 | NaN | NaN | NaN | -17.003 | NaN | NaN | NaN | 27.6766 | 586.4436 | NaN | 29.1366 | NaN | 26.9116
473.1292 | 11.3186 | 11.4395 | 11.4284 | 11.7203 | 11.1805 | 11.9023 | 11.5956 | 11.306 | NaN | NaN | NaN | 11.6737 | 92.9881 | NaN | NaN | NaN | -15.9611 | NaN | NaN | NaN | 26.6761 | 588.0954 | NaN | 31.447 | NaN | 23.5891
474.1292 | 11.415 | 11.4955 | 11.4318 | 11.704 | 11.0383 | 11.8082 | 11.582 | 11.3038 | NaN | NaN | NaN | 11.5927 | 95.1813 | NaN | NaN | NaN | -10.2941 | NaN | NaN | NaN | 26.8832 | 588.5547 | NaN | 29.7934 | NaN | 26.7873
475.1292 | 11.2936 | 11.6154 | 11.432 | 11.7428 | 11.0038 | 12.0022 | 11.6239 | 11.304 | NaN | NaN | NaN | 11.6556 | 92.9622 | NaN | NaN | NaN | -6.032 | NaN | NaN | NaN | 26.8099 | 587.989 | NaN | 31.3527 | NaN | 22.5846
476.1292 | 11.3635 | 11.5635 | 11.4324 | 11.7601 | 11.0706 | 11.9675 | 11.6312 | 11.3074 | NaN | NaN | NaN | 11.6073 | 91.2373 | NaN | NaN | NaN | -15.5132 | NaN | NaN | NaN | 28.2089 | 587.8905 | NaN | 29.7492 | NaN | 25.3201
477.1292 | 11.5182 | 11.5465 | 11.4357 | 11.7106 | 11.0636 | 12.0126 | 11.6333 | 11.3043 | NaN | NaN | NaN | 11.6593 | 93.6185 | NaN | NaN | NaN | -17.9589 | NaN | NaN | NaN | 27.8004 | 586.5294 | NaN | 31.4023 | NaN | 26.279
478.1292 | 11.4565 | 11.5885 | 11.4349 | 11.701 | 11.1595 | 11.9752 | 11.6442 | 11.2985 | NaN | NaN | NaN | 11.6494 | 92.3271 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 27.5059 | 585.6166 | NaN | 30.2438 | NaN | 23.9025
479.1292 | 11.5023 | 11.4753 | 11.43 | 11.768 | 11.0205 | 11.9587 | 11.6167 | 11.3049 | NaN | NaN | NaN | 11.6104 | 92.7905 | NaN | NaN | NaN | -16.8992 | NaN | NaN | NaN | 25.9445 | 587.0265 | NaN | 31.7528 | NaN | 26.2298
480.1292 | 11.3114 | 11.4415 | 11.4338 | 11.7252 | 11.1842 | 11.9061 | 11.5662 | 11.3026 | NaN | NaN | NaN | 11.6392 | 93.5441 | NaN | NaN | NaN | -17.9736 | NaN | NaN | NaN | 28.467 | 587.9449 | NaN | 27.7658 | NaN | 21.9655
481.1292 | 11.3013 | 11.2534 | 11.433 | 11.7433 | 11.1176 | 11.72 | 11.5156 | 11.3074 | NaN | NaN | NaN | 11.6943 | 94.5585 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 27.1497 | 586.4876 | NaN | 29.7366 | NaN | 28.9074
482.1292 | 11.3369 | 11.2952 | 11.432 | 11.7466 | 11.0199 | 11.7998 | 11.5545 | 11.309 | NaN | NaN | NaN | 11.7234 | 92.4765 | NaN | NaN | NaN | -4.1469 | NaN | NaN | NaN | 27.2543 | 587.7669 | NaN | 30.6923 | NaN | 24.6898
483.1292 | 11.3179 | 11.8722 | 11.4343 | 11.726 | 11.0666 | 12.1394 | 11.7344 | 11.3113 | NaN | NaN | NaN | 11.7222 | 94.6218 | NaN | NaN | NaN | -19.2733 | NaN | NaN | NaN | 27.5473 | 588.2182 | NaN | 30.4147 | NaN | 24.5648
484.1292 | 11.4978 | 11.416 | 11.4335 | 11.7185 | 11.1188 | 11.9347 | 11.5884 | 11.3131 | NaN | NaN | NaN | 11.6514 | 95.6379 | NaN | NaN | NaN | -11.2599 | NaN | NaN | NaN | 26.5271 | 586.5361 | NaN | 30.6844 | NaN | 25.9241
485.1292 | 11.316 | 11.4309 | 11.4327 | 11.7778 | 11.069 | 11.8699 | 11.5694 | 11.3137 | NaN | NaN | NaN | 11.7002 | 94.8649 | NaN | NaN | NaN | -16.4451 | NaN | NaN | NaN | 24.0706 | 586.278 | NaN | 31.3221 | NaN | 23.0775
486.1292 | 11.3913 | 11.3589 | 11.4273 | 11.7855 | 11.1366 | 11.8494 | 11.5857 | 11.3147 | NaN | NaN | NaN | 11.6621 | 93.7183 | NaN | NaN | NaN | -15.9727 | NaN | NaN | NaN | 28.278 | 589.5246 | NaN | 31.2799 | NaN | 25.0446
487.1292 | 11.4389 | 11.4325 | 11.4299 | 11.9171 | 11.1813 | 11.9082 | 11.5901 | 11.3129 | NaN | NaN | NaN | 11.7474 | 93.8369 | NaN | NaN | NaN | -12.6472 | NaN | NaN | NaN | 25.6933 | 586.3111 | NaN | 28.8846 | NaN | 25.0258
488.1292 | 11.5957 | 11.5427 | 11.4323 | 11.728 | 11.1672 | 11.9421 | 11.6199 | 11.32 | NaN | NaN | NaN | 11.6599 | 91.9169 | NaN | NaN | NaN | -6.6856 | NaN | NaN | NaN | 28.482 | 587.976 | NaN | 28.9662 | NaN | 21.3656
489.1292 | 11.4099 | 11.5295 | 11.431 | 11.7535 | 11.1034 | 11.926 | 11.6437 | 11.3171 | NaN | NaN | NaN | 11.6935 | 94.0215 | NaN | NaN | NaN | -11.7313 | NaN | NaN | NaN | 28.4921 | 588.0273 | NaN | 32.1175 | NaN | 29.2099
490.1292 | 11.3022 | 11.6756 | 11.4284 | 11.7444 | 11.1942 | 12.1192 | 11.6616 | 11.3168 | NaN | NaN | NaN | 11.7313 | 91.3556 | NaN | NaN | NaN | -11.6366 | NaN | NaN | NaN | 26.5218 | 588.4907 | NaN | 30.6613 | NaN | 26.4653
491.1292 | 11.4233 | 11.4202 | 11.4344 | 11.7044 | 11.1166 | 11.865 | 11.5974 | 11.3224 | NaN | NaN | NaN | 11.6461 | 95.6699 | NaN | NaN | NaN | -15.8153 | NaN | NaN | NaN | 24.798 | 587.7707 | NaN | 30.8305 | NaN | 20.0859
492.1292 | 11.3607 | 11.8047 | 11.4277 | 11.891 | 11.0814 | 12.0502 | 11.679 | 11.3236 | NaN | NaN | NaN | 11.7473 | 93.1095 | NaN | NaN | NaN | -4.7863 | NaN | NaN | NaN | 27.6736 | 588.8336 | NaN | 30.8453 | NaN | 21.0356
493.1448 | 11.4303 | 11.648 | 11.4283 | 11.6842 | 11.0495 | 12.0288 | 11.6522 | 11.3291 | NaN | NaN | NaN | 11.8183 | 94.6769 | NaN | NaN | NaN | -12.7739 | NaN | NaN | NaN | 26.2585 | 589.4321 | NaN | 31.0127 | NaN | 23.6924
494.1292 | 11.3807 | 11.397 | 11.4324 | 11.7329 | 11.1368 | 11.8605 | 11.5751 | 11.3206 | NaN | NaN | NaN | 11.7952 | 95.1986 | NaN | NaN | NaN | -13.3521 | NaN | NaN | NaN | 29.5166 | 589.4387 | NaN | 31.2471 | NaN | 24.9101
495.1292 | 11.3915 | 11.3837 | 11.426 | 11.7325 | 11.1468 | 11.8119 | 11.5658 | 11.3285 | NaN | NaN | NaN | 11.7169 | 91.7084 | NaN | NaN | NaN | -17.859 | NaN | NaN | NaN | 25.9204 | 588.9421 | NaN | 31.5527 | NaN | 25.853
496.1292 | 11.3486 | 11.4205 | 11.4316 | 11.7672 | 11.214 | 11.8879 | 11.5905 | 11.3281 | NaN | NaN | NaN | 11.779 | 92.0844 | NaN | NaN | NaN | -18.5949 | NaN | NaN | NaN | 26.9433 | 591.0745 | NaN | 30.4521 | NaN | 24.7605
497.1292 | 11.4555 | 11.4558 | 11.4353 | 11.7495 | 11.0029 | 11.9325 | 11.6129 | 11.3274 | NaN | NaN | NaN | 11.7535 | 92.8036 | NaN | NaN | NaN | -16.0246 | NaN | NaN | NaN | 26.3879 | 590.9878 | NaN | 29.892 | NaN | 22.8788
498.1292 | 11.3928 | 11.4857 | 11.4294 | 11.7054 | 11.1345 | 11.9223 | 11.6194 | 11.332 | NaN | NaN | NaN | 11.734 | 95.4186 | NaN | NaN | NaN | -19.859 | NaN | NaN | NaN | 25.8557 | 589.7037 | NaN | 31.0955 | NaN | 22.1966
499.1292 | 11.4518 | 11.6387 | 11.4355 | 11.7666 | 11.1413 | 11.9675 | 11.6438 | 11.3306 | NaN | NaN | NaN | 11.6873 | 94.7942 | NaN | NaN | NaN | -18.335 | NaN | NaN | NaN | 28.2826 | 589.2719 | NaN | 30.629 | NaN | 23.622
500.1292 | 11.3932 | 11.3574 | 11.4315 | 11.9239 | 11.1182 | 11.8606 | 11.5835 | 11.3314 | NaN | NaN | NaN | 11.8284 | 92.3724 | NaN | NaN | NaN | -15.3153 | NaN | NaN | NaN | 26.7047 | 589.4905 | NaN | 30.9341 | NaN | 25.225
501.1292 | 11.5004 | 11.8054 | 11.4425 | 11.7798 | 10.9675 | 12.055 | 11.7087 | 11.3326 | NaN | NaN | NaN | 11.6353 | 91.0658 | NaN | NaN | NaN | -8.9901 | NaN | NaN | NaN | 27.801 | 589.1732 | NaN | 30.6818 | NaN | 20.0644
502.1292 | 11.3761 | 11.5843 | 11.4417 | 11.8849 | 11.1816 | 11.9648 | 11.6598 | 11.3335 | NaN | NaN | NaN | 11.6973 | 94.9731 | NaN | NaN | NaN | 5.8692 | NaN | NaN | NaN | 27.9031 | 588.2289 | NaN | 29.2549 | NaN | 25.301
503.1292 | 11.3486 | 11.5597 | 11.4388 | 11.7443 | 11.1169 | 12.098 | 11.6488 | 11.3344 | NaN | NaN | NaN | 11.6781 | 98.4969 | NaN | NaN | NaN | -14.7437 | NaN | NaN | NaN | 30.1091 | 590.1428 | NaN | 31.554 | NaN | 25.1892
504.1292 | 11.454 | 11.4249 | 11.4408 | 11.863 | 11.0035 | 11.9074 | 11.5988 | 11.3342 | NaN | NaN | NaN | 11.6732 | 99.9619 | NaN | NaN | NaN | -18.3552 | NaN | NaN | NaN | 30.6844 | 589.4167 | NaN | 30.1565 | NaN | 19.5994
505.1292 | 11.3803 | 11.4172 | 11.4409 | 11.7901 | 11.2255 | 11.8965 | 11.5888 | 11.3341 | NaN | NaN | NaN | 11.6958 | 90.5723 | NaN | NaN | NaN | 0.8034 | NaN | NaN | NaN | 26.7258 | 590.8916 | NaN | 29.7211 | NaN | 25.4884
506.1292 | 11.4371 | 11.3977 | 11.4468 | 11.8573 | 11.1165 | 11.9472 | 11.6031 | 11.3373 | NaN | NaN | NaN | 11.7016 | 95.9444 | NaN | NaN | NaN | 8.8036 | NaN | NaN | NaN | 26.3923 | 587.696 | NaN | 30.9815 | NaN | 18.5408
507.1292 | 11.4326 | 11.8135 | 11.4463 | 11.7936 | 10.9732 | 12.1471 | 11.7256 | 11.3381 | NaN | NaN | NaN | 11.7021 | 95.2798 | NaN | NaN | NaN | 6.8391 | NaN | NaN | NaN | 30.0281 | 589.023 | NaN | 31.0833 | NaN | 23.4262
508.1292 | 11.4102 | 11.4971 | 11.4464 | 11.8376 | 11.1455 | 11.9037 | 11.6337 | 11.3394 | NaN | NaN | NaN | 11.6648 | 91.9057 | NaN | NaN | NaN | -13.794 | NaN | NaN | NaN | 29.6038 | 588.6255 | NaN | 30.2086 | NaN | 25.847
509.1292 | 11.5078 | 11.6691 | 11.4525 | 11.7647 | 11.026 | 12.0874 | 11.6644 | 11.3407 | NaN | NaN | NaN | 11.6615 | 96.4009 | NaN | NaN | NaN | -15.2329 | NaN | NaN | NaN | 27.4972 | 589.2561 | NaN | 30.9113 | NaN | 27.1118
510.1292 | 11.4321 | 11.6226 | 11.453 | 11.7697 | 11.0888 | 12.0733 | 11.6549 | 11.3362 | NaN | NaN | NaN | 11.759 | 96.3357 | NaN | NaN | NaN | -15.352 | NaN | NaN | NaN | 29.7087 | 589.6868 | NaN | 29.6488 | NaN | 25.5799
511.1292 | 11.4646 | 11.5057 | 11.4545 | 11.7387 | 11.2016 | 11.9432 | 11.6229 | 11.3455 | NaN | NaN | NaN | 11.7277 | 94.8756 | NaN | NaN | NaN | -14.0712 | NaN | NaN | NaN | 24.4312 | 589.1012 | NaN | 30.877 | NaN | 17.8991
512.1292 | 11.575 | 11.4528 | 11.4598 | 11.8117 | 11.2583 | 11.9271 | 11.6223 | 11.3399 | NaN | NaN | NaN | 11.7061 | 92.8601 | NaN | NaN | NaN | -18.8451 | NaN | NaN | NaN | 28.5087 | 588.0444 | NaN | 30.6541 | NaN | 24.0816
513.1292 | 11.3655 | 11.4092 | 11.4566 | 11.7657 | 11.105 | 11.9267 | 11.616 | 11.3464 | NaN | NaN | NaN | 11.6728 | 95.7391 | NaN | NaN | NaN | -7.4056 | NaN | NaN | NaN | 29.2152 | 589.1384 | NaN | 30.3277 | NaN | 22.5336
514.1292 | 11.3654 | 11.4402 | 11.4589 | 11.8052 | 11.0981 | 11.978 | 11.6176 | 11.3435 | NaN | NaN | NaN | 11.6632 | 95.8755 | NaN | NaN | NaN | -17.288 | NaN | NaN | NaN | 28.0524 | 590.1541 | NaN | 30.8536 | NaN | 23.1136
515.1292 | 11.4021 | 11.4556 | 11.4612 | 11.8438 | 11.109 | 11.913 | 11.6156 | 11.3516 | NaN | NaN | NaN | 11.7311 | 95.4674 | NaN | NaN | NaN | -1.4385 | NaN | NaN | NaN | 27.3034 | 587.5666 | NaN | 30.0944 | NaN | 24.3194
516.1292 | 11.517 | 11.581 | 11.4579 | 11.7646 | 11.0763 | 11.9837 | 11.6617 | 11.3471 | NaN | NaN | NaN | 11.7219 | 94.4681 | NaN | NaN | NaN | -1.465 | NaN | NaN | NaN | 25.8475 | 587.0703 | NaN | 29.8809 | NaN | 22.6675
517.1292 | 11.3911 | 11.5633 | 11.4619 | 11.7505 | 11.0784 | 11.9791 | 11.6388 | 11.3504 | NaN | NaN | NaN | 11.7824 | 95.3114 | NaN | NaN | NaN | 2.86 | NaN | NaN | NaN | 29.9458 | 586.8574 | NaN | 29.7595 | NaN | 27.9138
518.1292 | 11.5578 | 11.4867 | 11.4591 | 11.7847 | 11.1943 | 11.844 | 11.6181 | 11.3514 | NaN | NaN | NaN | 11.6701 | 95.578 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 24.4476 | 586.7539 | NaN | 28.9715 | NaN | 25.4264
519.1292 | 11.3908 | 11.4354 | 11.463 | 11.7578 | 11.1127 | 11.9155 | 11.6176 | 11.3474 | NaN | NaN | NaN | 11.7126 | 91.5552 | NaN | NaN | NaN | -15.6279 | NaN | NaN | NaN | 28.2513 | 588.9237 | NaN | 32.6377 | NaN | 19.7419
520.1292 | 11.3617 | 11.5048 | 11.4586 | 11.7997 | 11.1157 | 11.9767 | 11.6569 | 11.3513 | NaN | NaN | NaN | 11.7502 | 92.7397 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 28.3936 | 587.9783 | NaN | 31.4058 | NaN | 20.3505
521.1292 | 11.4014 | 11.3878 | 11.4617 | 11.8061 | 11.1491 | 11.8335 | 11.5972 | 11.3539 | NaN | NaN | NaN | 11.7963 | 91.8794 | NaN | NaN | NaN | -13.1112 | NaN | NaN | NaN | 26.7216 | 590.2591 | NaN | 30.8952 | NaN | 24.1645
522.1292 | 11.4998 | 11.4278 | 11.4629 | 11.7229 | 11.1573 | 11.8097 | 11.5944 | 11.3545 | NaN | NaN | NaN | 11.7734 | 94.2113 | NaN | NaN | NaN | -15.7183 | NaN | NaN | NaN | 26.9309 | 589.0402 | NaN | 28.536 | NaN | 21.6303
523.1292 | 11.4067 | 11.5146 | 11.4649 | 11.7833 | 11.0775 | 11.9355 | 11.6326 | 11.3624 | NaN | NaN | NaN | 11.6612 | 93.3702 | NaN | NaN | NaN | -18.5036 | NaN | NaN | NaN | 28.2037 | 590.1559 | NaN | 30.8579 | NaN | 27.8362
524.1292 | 11.4783 | 11.5852 | 11.4572 | 11.7823 | 10.9934 | 11.9593 | 11.6786 | 11.3561 | NaN | NaN | NaN | 11.7414 | 92.4252 | NaN | NaN | NaN | -9.6645 | NaN | NaN | NaN | 27.4655 | 589.9317 | NaN | 29.4699 | NaN | 20.0082
525.1292 | 11.4309 | 11.8164 | 11.4662 | 11.8039 | 11.1579 | 12.1459 | 11.7106 | 11.3596 | NaN | NaN | NaN | 11.6943 | 92.9095 | NaN | NaN | NaN | -10.8722 | NaN | NaN | NaN | 26.6084 | 590.3151 | NaN | 30.8145 | NaN | 24.1357
526.1292 | 11.4537 | 11.6484 | 11.4715 | 11.7744 | 11.1001 | 11.9755 | 11.6736 | 11.3647 | NaN | NaN | NaN | 11.6843 | 95.7026 | NaN | NaN | NaN | -12.614 | NaN | NaN | NaN | 27.3665 | 591.062 | NaN | 30.6893 | NaN | 25.4511
527.1292 | 11.4817 | 11.4674 | 11.466 | 11.8241 | 11.1434 | 11.9997 | 11.6462 | 11.3595 | NaN | NaN | NaN | 11.7068 | 94.2767 | NaN | NaN | NaN | -18.7272 | NaN | NaN | NaN | 27.1187 | 591.5666 | NaN | 29.3363 | NaN | 26.8024
528.1292 | 11.4012 | 11.328 | 11.4682 | 11.7943 | 11.1138 | 11.7951 | 11.5873 | 11.3607 | NaN | NaN | NaN | 11.7971 | 92.7087 | NaN | NaN | NaN | -19.6024 | NaN | NaN | NaN | 27.2114 | 590.1373 | NaN | 30.5681 | NaN | 20.5505
529.1292 | 11.4126 | 11.416 | 11.4734 | 11.8242 | 11.1433 | 11.8657 | 11.6201 | 11.3644 | NaN | NaN | NaN | 11.717 | 90.5063 | NaN | NaN | NaN | -6.602 | NaN | NaN | NaN | 28.3738 | 590.9179 | NaN | 29.3122 | NaN | 19.8763
530.1292 | 11.4542 | 11.453 | 11.4715 | 11.7964 | 11.1133 | 11.9378 | 11.6383 | 11.3652 | NaN | NaN | NaN | 11.7302 | 93.973 | NaN | NaN | NaN | -17.4541 | NaN | NaN | NaN | 25.722 | 592.954 | NaN | 32.0977 | NaN | 22.0247
531.1292 | 11.417 | 11.6758 | 11.4788 | 11.8363 | 11.1179 | 12.0929 | 11.6981 | 11.3586 | NaN | NaN | NaN | 11.7422 | 92.0199 | NaN | NaN | NaN | -17.6266 | NaN | NaN | NaN | 28.5653 | 589.5048 | NaN | 30.3496 | NaN | 26.9671
532.1292 | 11.4151 | 11.4299 | 11.483 | 11.8353 | 11.1969 | 11.8727 | 11.6121 | 11.3657 | NaN | NaN | NaN | 11.6956 | 98.4355 | NaN | NaN | NaN | -14.5802 | NaN | NaN | NaN | 27.34 | 588.4891 | NaN | 31.6102 | NaN | 24.292
533.1292 | 11.4368 | 11.7117 | 11.4868 | 12.0267 | 11.1441 | 11.9756 | 11.6775 | 11.3607 | NaN | NaN | NaN | 11.8453 | 90.0902 | NaN | NaN | NaN | 0.4659 | NaN | NaN | NaN | 28.7135 | 588.7197 | NaN | 30.6017 | NaN | 28.6003
534.1292 | 11.3919 | 11.7184 | 11.4889 | 11.8427 | 11.1443 | 11.9865 | 11.7016 | 11.3669 | NaN | NaN | NaN | 11.7345 | 104.5322 | NaN | NaN | NaN | -16.1813 | NaN | NaN | NaN | 26.6681 | 589.8761 | NaN | 31.3995 | NaN | 26.1891
535.1292 | 11.5275 | 11.4687 | 11.4908 | 11.8264 | 11.103 | 11.9273 | 11.6335 | 11.3697 | NaN | NaN | NaN | 11.6948 | 93.383 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 27.8388 | 589.1163 | NaN | 29.7277 | NaN | 27.1473
536.1292 | 11.4972 | 11.5245 | 11.4938 | 11.8046 | 11.165 | 11.9546 | 11.6608 | 11.3677 | NaN | NaN | NaN | 11.7962 | 93.4448 | NaN | NaN | NaN | -2.0308 | NaN | NaN | NaN | 25.2593 | 588.2843 | NaN | 30.0361 | NaN | 24.9898
537.1292 | 11.4213 | 11.6431 | 11.4938 | 11.7532 | 11.0828 | 11.9663 | 11.672 | 11.3676 | NaN | NaN | NaN | 11.7661 | 92.7241 | NaN | NaN | NaN | -15.0536 | NaN | NaN | NaN | 26.3086 | 589.8367 | NaN | 31.3777 | NaN | 28.2794
538.1292 | 11.5673 | 11.7749 | 11.4996 | 11.8011 | 11.1582 | 11.9638 | 11.7053 | 11.374 | NaN | NaN | NaN | 11.6951 | 90.7791 | NaN | NaN | NaN | -19.653 | NaN | NaN | NaN | 26.6867 | 588.4101 | NaN | 28.3204 | NaN | 21.8944
539.1292 | 11.5062 | 12.03 | 11.4927 | 11.903 | 11.2638 | 12.2116 | 11.7713 | 11.3676 | NaN | NaN | NaN | 11.745 | 94.2548 | NaN | NaN | NaN | -16.7807 | NaN | NaN | NaN | 27.2898 | 587.3896 | NaN | 30.1423 | NaN | 24.1953
540.1292 | 11.4076 | 11.5215 | 11.4973 | 11.8195 | 11.2145 | 11.9777 | 11.6371 | 11.379 | NaN | NaN | NaN | 11.7612 | 98.3515 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 27.8767 | 586.8202 | NaN | 30.9062 | NaN | 25.5833
541.1292 | 11.4041 | 11.5519 | 11.5054 | 11.872 | 11.0825 | 11.9233 | 11.6438 | 11.3678 | NaN | NaN | NaN | 11.8973 | 91.6221 | NaN | NaN | NaN | -11.3935 | NaN | NaN | NaN | 29.3398 | 587.0177 | NaN | 32.1503 | NaN | 23.9036
542.1292 | 11.4541 | 11.7129 | 11.5006 | 11.9106 | 11.049 | 12.0949 | 11.7321 | 11.3747 | NaN | NaN | NaN | 11.802 | 95.8728 | NaN | NaN | NaN | 8.5712 | NaN | NaN | NaN | 28.555 | 587.1397 | NaN | 30.4611 | NaN | 22.7266
543.1292 | 11.4961 | 11.5393 | 11.5106 | 11.8612 | 11.1287 | 12.0065 | 11.6413 | 11.3699 | NaN | NaN | NaN | 11.8504 | 92.9155 | NaN | NaN | NaN | -17.9805 | NaN | NaN | NaN | 29.6369 | 587.2985 | NaN | 30.8164 | NaN | 26.127
544.1292 | 11.4513 | 11.5506 | 11.5063 | 11.8092 | 11.1008 | 12.0166 | 11.6543 | 11.3773 | NaN | NaN | NaN | 11.7884 | 89.7823 | NaN | NaN | NaN | -14.7824 | NaN | NaN | NaN | 29.6821 | 589.3716 | NaN | 29.0425 | NaN | 23.1323
545.1292 | 11.7324 | 11.4781 | 11.5164 | 12.0126 | 11.1559 | 11.8269 | 11.6021 | 11.3748 | NaN | NaN | NaN | 11.8307 | 94.1902 | NaN | NaN | NaN | -19.4604 | NaN | NaN | NaN | 27.8937 | 585.4321 | NaN | 28.4521 | NaN | 22.5857
546.1292 | 11.4457 | 11.6159 | 11.5146 | 11.8299 | 11.032 | 12.0332 | 11.6986 | 11.3751 | NaN | NaN | NaN | 11.8239 | 95.2328 | NaN | NaN | NaN | -1.2436 | NaN | NaN | NaN | 26.0469 | 588.1187 | NaN | 30.5078 | NaN | 24.0985
547.1292 | 11.5192 | 11.5534 | 11.5143 | 11.9015 | 11.0119 | 12.0394 | 11.6582 | 11.382 | NaN | NaN | NaN | 11.7647 | 92.8956 | NaN | NaN | NaN | -12.5282 | NaN | NaN | NaN | 27.0222 | 587.1045 | NaN | 30.5917 | NaN | 22.7741
548.1292 | 11.6668 | 11.5748 | 11.5129 | 11.8086 | 11.1492 | 11.9695 | 11.6544 | 11.3794 | NaN | NaN | NaN | 11.8186 | 92.6179 | NaN | NaN | NaN | -13.9518 | NaN | NaN | NaN | 27.9152 | 587.8249 | NaN | 29.698 | NaN | 24.8185
549.1292 | 11.5861 | 11.4235 | 11.5212 | 11.8389 | 11.1693 | 11.8233 | 11.595 | 11.3794 | NaN | NaN | NaN | 11.8816 | 97.0947 | NaN | NaN | NaN | -2.973 | NaN | NaN | NaN | 27.411 | 585.9083 | NaN | 28.338 | NaN | 28.6437
550.1292 | 11.6069 | 11.7138 | 11.5237 | 11.8115 | 11.1753 | 12.1149 | 11.7058 | 11.3806 | NaN | NaN | NaN | 11.8232 | 92.4874 | NaN | NaN | NaN | -12.6766 | NaN | NaN | NaN | 26.9895 | 584.0716 | NaN | 30.3038 | NaN | 21.9758
551.1292 | 11.5311 | 11.7783 | 11.5266 | 11.8634 | 11.2724 | 12.1701 | 11.7274 | 11.3872 | NaN | NaN | NaN | 11.8188 | 90.3227 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 27.2674 | 581.1223 | NaN | 29.9432 | NaN | 24.4106
552.1292 | 11.5062 | 11.5895 | 11.5369 | 11.929 | 11.2728 | 11.9481 | 11.6545 | 11.3914 | NaN | NaN | NaN | 11.7664 | 92.9753 | NaN | NaN | NaN | -10.376 | NaN | NaN | NaN | 25.8727 | 581.9022 | NaN | 31.1031 | NaN | 26.7297
553.1292 | 11.4571 | 11.6581 | 11.5337 | 11.8855 | 11.1953 | 12.0549 | 11.684 | 11.3853 | NaN | NaN | NaN | 11.8632 | 93.9657 | NaN | NaN | NaN | -17.3821 | NaN | NaN | NaN | 23.7901 | 582.7316 | NaN | 30.7707 | NaN | 25.2982
554.1292 | 11.6376 | 11.4665 | 11.5327 | 12.0007 | 11.18 | 11.9484 | 11.6344 | 11.3939 | NaN | NaN | NaN | 11.7883 | 93.8534 | NaN | NaN | NaN | -14.2889 | NaN | NaN | NaN | 27.8038 | 583.9044 | NaN | 29.0198 | NaN | 21.697
555.1292 | 11.5521 | 11.4754 | 11.5352 | 11.8565 | 11.2984 | 11.9462 | 11.6345 | 11.3883 | NaN | NaN | NaN | 11.9169 | 94.7543 | NaN | NaN | NaN | -8.7632 | NaN | NaN | NaN | 27.9633 | 583.4905 | NaN | 29.9427 | NaN | 20.8293
556.1292 | 11.6414 | 11.7664 | 11.5343 | 11.8105 | 11.2038 | 12.0107 | 11.6548 | 11.4001 | NaN | NaN | NaN | 11.746 | 93.0346 | NaN | NaN | NaN | -10.5534 | NaN | NaN | NaN | 24.0255 | 582.7522 | NaN | 31.4202 | NaN | 20.134
557.1292 | 11.4948 | 11.5185 | 11.5327 | 11.8785 | 11.1814 | 11.9835 | 11.6477 | 11.3996 | NaN | NaN | NaN | 11.8553 | 94.6339 | NaN | NaN | NaN | -16.3999 | NaN | NaN | NaN | 24.3001 | 583.7274 | NaN | 29.3472 | NaN | 26.1043
558.1292 | 11.514 | 11.4639 | 11.5366 | 11.8342 | 11.1841 | 11.8518 | 11.5967 | 11.4119 | NaN | NaN | NaN | 11.7964 | 94.546 | NaN | NaN | NaN | -10.7188 | NaN | NaN | NaN | 26.5174 | 582.0406 | NaN | 30.7127 | NaN | 23.2148
559.1292 | 11.5062 | 11.6836 | 11.5357 | 12.1681 | 11.1563 | 11.9462 | 11.655 | 11.4039 | NaN | NaN | NaN | 11.8431 | 90.2118 | NaN | NaN | NaN | -6.4903 | NaN | NaN | NaN | 28.5666 | 582.9085 | NaN | 28.1381 | NaN | 17.9049
560.1292 | 11.5872 | 11.5707 | 11.5405 | 11.8217 | 11.19 | 12.0319 | 11.6686 | 11.4041 | NaN | NaN | NaN | 11.8402 | 94.3635 | NaN | NaN | NaN | -14.815 | NaN | NaN | NaN | 26.1393 | 582.7434 | NaN | 29.736 | NaN | 21.7398
561.1292 | 11.4968 | 11.4124 | 11.5383 | 11.8581 | 11.1863 | 11.837 | 11.6012 | 11.409 | NaN | NaN | NaN | 11.9619 | 91.1297 | NaN | NaN | NaN | -17.8774 | NaN | NaN | NaN | 29.2167 | 582.4313 | NaN | 30.048 | NaN | 25.1356
562.1292 | 11.5803 | 11.8327 | 11.5479 | 11.8613 | 11.0842 | 12.0976 | 11.7417 | 11.4113 | NaN | NaN | NaN | 11.7947 | 90.5126 | NaN | NaN | NaN | -7.6161 | NaN | NaN | NaN | 26.5437 | 581.7784 | NaN | 31.1644 | NaN | 24.0317
563.1292 | 11.4987 | 11.5312 | 11.5461 | 11.8888 | 11.1088 | 11.9468 | 11.6472 | 11.4128 | NaN | NaN | NaN | 11.7627 | 91.6203 | NaN | NaN | NaN | -19.8694 | NaN | NaN | NaN | 28.8575 | 584.0059 | NaN | 30.0093 | NaN | 26.9338
564.1292 | 11.6214 | 11.634 | 11.5451 | 12.0134 | 11.171 | 12.0669 | 11.6687 | 11.409 | NaN | NaN | NaN | 11.7792 | 95.1915 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 27.618 | 582.1907 | NaN | 29.3437 | NaN | 25.4319
565.1292 | 11.558 | 11.6783 | 11.549 | 11.8328 | 11.2331 | 12.0674 | 11.7108 | 11.4103 | NaN | NaN | NaN | 11.7719 | 91.368 | NaN | NaN | NaN | -15.3411 | NaN | NaN | NaN | 25.0642 | 583.4475 | NaN | 29.0461 | NaN | 24.9353
566.1292 | 11.5691 | 11.4934 | 11.5548 | 11.8179 | 11.3218 | 11.9577 | 11.6486 | 11.417 | NaN | NaN | NaN | 11.8813 | 93.5524 | NaN | NaN | NaN | 2.7829 | NaN | NaN | NaN | 26.8317 | 582.4829 | NaN | 29.9637 | NaN | 19.8175
567.1292 | 11.5469 | 11.7066 | 11.5556 | 11.9439 | 11.243 | 12.116 | 11.7055 | 11.423 | NaN | NaN | NaN | 11.852 | 94.1057 | NaN | NaN | NaN | -16.8744 | NaN | NaN | NaN | 28.1631 | 583.4731 | NaN | 29.9863 | NaN | 20.1774
568.1292 | 11.5952 | 11.7111 | 11.5614 | 11.9098 | 11.1156 | 12.1294 | 11.7258 | 11.4147 | NaN | NaN | NaN | 11.8439 | 94.4177 | NaN | NaN | NaN | -15.5988 | NaN | NaN | NaN | 25.7775 | 581.7229 | NaN | 29.2507 | NaN | 28.6814
569.1292 | 11.4945 | 11.683 | 11.5593 | 11.9588 | 11.2154 | 12.1385 | 11.7251 | 11.4174 | NaN | NaN | NaN | 11.9051 | 93.6769 | NaN | NaN | NaN | -15.0888 | NaN | NaN | NaN | 27.5988 | 582.3171 | NaN | 29.7815 | NaN | 24.4602
570.1292 | 11.6887 | 11.6254 | 11.5625 | 11.8341 | 11.18 | 12.1026 | 11.709 | 11.4242 | NaN | NaN | NaN | 11.8363 | 94.3788 | NaN | NaN | NaN | -3.725 | NaN | NaN | NaN | 27.1909 | 581.9659 | NaN | 30.6095 | NaN | 22.0546
571.1292 | 11.4962 | 11.5184 | 11.566 | 11.9023 | 11.264 | 11.9715 | 11.6703 | 11.4304 | NaN | NaN | NaN | 11.8782 | 98.8336 | NaN | NaN | NaN | -11.0421 | NaN | NaN | NaN | 28.2819 | 578.5028 | NaN | 29.7769 | NaN | 25.027
572.1292 | 11.567 | 11.6128 | 11.5666 | 11.8807 | 11.2744 | 12.054 | 11.6912 | 11.425 | NaN | NaN | NaN | 11.8287 | 92.6163 | NaN | NaN | NaN | 1.179 | NaN | NaN | NaN | 25.8278 | 581.0577 | NaN | 31.8181 | NaN | 26.4278
573.1292 | 11.6449 | 11.5848 | 11.5684 | 11.957 | 11.258 | 12.0515 | 11.6944 | 11.4275 | NaN | NaN | NaN | 11.8693 | 91.9397 | NaN | NaN | NaN | -16.2289 | NaN | NaN | NaN | 25.5372 | 579.6092 | NaN | 30.5509 | NaN | 29.0065
574.1292 | 11.6546 | 11.7016 | 11.5707 | 11.9084 | 11.053 | 12.1239 | 11.7222 | 11.4265 | NaN | NaN | NaN | 11.8425 | 93.2103 | NaN | NaN | NaN | -19.8257 | NaN | NaN | NaN | 27.4815 | 580.829 | NaN | 30.8528 | NaN | 19.8378
575.1292 | 11.5575 | 11.5301 | 11.5679 | 11.9791 | 11.2138 | 11.9361 | 11.6633 | 11.4279 | NaN | NaN | NaN | 11.7989 | 93.1058 | NaN | NaN | NaN | -14.2547 | NaN | NaN | NaN | 26.8458 | 579.964 | NaN | 30.663 | NaN | 24.1851
576.1292 | 11.5934 | 11.8218 | 11.5665 | 11.909 | 11.1482 | 12.2661 | 11.7481 | 11.4316 | NaN | NaN | NaN | 11.8159 | 93.099 | NaN | NaN | NaN | -0.573 | NaN | NaN | NaN | 28.4532 | 580.2075 | NaN | 29.3622 | NaN | 22.9927
577.1292 | 11.539 | 11.5073 | 11.5792 | 12.0277 | 11.1888 | 11.9735 | 11.6711 | 11.4342 | NaN | NaN | NaN | 11.8243 | 97.8407 | NaN | NaN | NaN | -18.0656 | NaN | NaN | NaN | 28.537 | 581.6938 | NaN | 29.17 | NaN | 26.8532
578.1292 | 11.5689 | 11.6691 | 11.5793 | 11.8652 | 11.325 | 12.0781 | 11.7444 | 11.4395 | NaN | NaN | NaN | 11.8967 | 97.1583 | NaN | NaN | NaN | -10.0075 | NaN | NaN | NaN | 26.7012 | 580.4249 | NaN | 29.8843 | NaN | 24.9638
579.1292 | 11.5788 | 11.7029 | 11.5763 | 11.8947 | 11.1326 | 12.2276 | 11.7316 | 11.4359 | NaN | NaN | NaN | 11.8632 | 93.1323 | NaN | NaN | NaN | -16.5098 | NaN | NaN | NaN | 28.5829 | 580.7753 | NaN | 30.4802 | NaN | 24.8775
580.1292 | 11.5282 | 11.6185 | 11.5835 | 11.8639 | 11.0792 | 12.0279 | 11.6959 | 11.4407 | NaN | NaN | NaN | 11.8842 | 92.873 | NaN | NaN | NaN | -17.4259 | NaN | NaN | NaN | 27.222 | 581.9946 | NaN | 29.4869 | NaN | 23.9218
581.1292 | 11.6347 | 11.6936 | 11.592 | 11.9498 | 11.2752 | 12.119 | 11.7202 | 11.4378 | NaN | NaN | NaN | 11.8223 | 94.6435 | NaN | NaN | NaN | -6.4169 | NaN | NaN | NaN | 27.5423 | 582.4199 | NaN | 30.6736 | NaN | 18.5236
582.1292 | 11.7587 | 11.5521 | 11.5873 | 11.9449 | 11.1884 | 11.9969 | 11.7 | 11.4464 | NaN | NaN | NaN | 11.8892 | 92.4738 | NaN | NaN | NaN | -15.8239 | NaN | NaN | NaN | 23.8086 | 582.7484 | NaN | 30.1363 | NaN | 23.8105
583.1292 | 11.8149 | 11.7349 | 11.593 | 11.9899 | 11.2473 | 12.1673 | 11.7369 | 11.4414 | NaN | NaN | NaN | 11.8357 | 92.904 | NaN | NaN | NaN | 1.5478 | NaN | NaN | NaN | 27.0104 | 583.0615 | NaN | 27.562 | NaN | 24.7979
584.1292 | 11.6831 | 11.67 | 11.5925 | 12.1101 | 11.1503 | 12.1095 | 11.7345 | 11.4459 | NaN | NaN | NaN | 11.7624 | 93.1254 | NaN | NaN | NaN | -7.0717 | NaN | NaN | NaN | 25.7385 | 579.8209 | NaN | 30.3422 | NaN | 21.4327
585.1292 | 11.5857 | 11.6482 | 11.592 | 11.8794 | 11.2128 | 12.0803 | 11.717 | 11.4511 | NaN | NaN | NaN | 11.8239 | 94.2216 | NaN | NaN | NaN | -18.6992 | NaN | NaN | NaN | 28.1133 | 581.0669 | NaN | 29.2437 | NaN | 27.9687
586.1292 | 11.6131 | 11.658 | 11.5937 | 11.8858 | 11.2897 | 12.0526 | 11.7103 | 11.4535 | NaN | NaN | NaN | 11.7986 | 93.9895 | NaN | NaN | NaN | -5.1984 | NaN | NaN | NaN | 26.8734 | 580.8198 | NaN | 30.1113 | NaN | 27.8594
587.1292 | 11.5913 | 12.0602 | 11.5971 | 11.9546 | 11.2344 | 12.3458 | 11.8279 | 11.4541 | NaN | NaN | NaN | 11.7625 | 93.0086 | NaN | NaN | NaN | -15.3164 | NaN | NaN | NaN | 28.3344 | 583.4556 | NaN | 30.3726 | NaN | 20.9602
588.1292 | 11.6099 | 11.4824 | 11.6026 | 11.9629 | 11.3232 | 11.9701 | 11.6799 | 11.4523 | NaN | NaN | NaN | 11.8839 | 92.4995 | NaN | NaN | NaN | -12.2345 | NaN | NaN | NaN | 30.4533 | 581.9836 | NaN | 31.3108 | NaN | 29.3594
589.1292 | 11.6458 | 11.6243 | 11.6053 | 11.9452 | 11.1813 | 12.1533 | 11.7363 | 11.4637 | NaN | NaN | NaN | 11.7795 | 92.148 | NaN | NaN | NaN | 10.3712 | NaN | NaN | NaN | 24.9763 | 582.2346 | NaN | 29.9875 | NaN | 24.7633
590.1292 | 11.6197 | 11.5149 | 11.6041 | 11.9769 | 11.3133 | 12.0265 | 11.6902 | 11.4613 | NaN | NaN | NaN | 11.8396 | 93.0682 | NaN | NaN | NaN | -16.7104 | NaN | NaN | NaN | 27.124 | 584.1327 | NaN | 29.9691 | NaN | 24.7961
591.1292 | 11.5438 | 12.0638 | 11.6136 | 11.9014 | 11.3414 | 12.4163 | 11.8363 | 11.4691 | NaN | NaN | NaN | 11.7787 | 92.7278 | NaN | NaN | NaN | -18.0178 | NaN | NaN | NaN | 27.6057 | 582.5708 | NaN | 27.1686 | NaN | 27.4696
592.1292 | 11.5861 | 11.626 | 11.6135 | 11.9132 | 11.2818 | 12.0977 | 11.7251 | 11.4709 | NaN | NaN | NaN | 11.8652 | 91.5833 | NaN | NaN | NaN | -16.758 | NaN | NaN | NaN | 26.8448 | 580.6164 | NaN | 30.4206 | NaN | 24.3493
593.1292 | 11.6062 | 11.8434 | 11.6132 | 11.9332 | 11.2295 | 12.1953 | 11.7423 | 11.4625 | NaN | NaN | NaN | 11.8031 | 93.2162 | NaN | NaN | NaN | 6.9159 | NaN | NaN | NaN | 29.9951 | 580.3174 | NaN | 30.3369 | NaN | 29.2624
594.1292 | 11.6401 | 11.5478 | 11.6214 | 11.8536 | 11.1804 | 11.9445 | 11.6815 | 11.4635 | NaN | NaN | NaN | 11.8431 | 93.3806 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 26.4088 | 577.3423 | NaN | 30.4327 | NaN | 29.466
595.1292 | 11.763 | 11.8336 | 11.6227 | 12.2403 | 11.2314 | 12.3698 | 11.7846 | 11.4697 | NaN | NaN | NaN | 11.8058 | 96.465 | NaN | NaN | NaN | -11.9966 | NaN | NaN | NaN | 26.2349 | 578.8781 | NaN | 30.34 | NaN | 24.8108
596.1292 | 11.583 | 11.4734 | 11.6287 | 11.9055 | 11.219 | 11.9293 | 11.664 | 11.4672 | NaN | NaN | NaN | 11.8024 | 92.3192 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 27.2817 | 578.7522 | NaN | 30.6013 | NaN | 27.4578
597.1292 | 11.6429 | 11.6104 | 11.6263 | 11.9874 | 11.3042 | 12.049 | 11.7289 | 11.4663 | NaN | NaN | NaN | 11.8915 | 92.3222 | NaN | NaN | NaN | -16.9087 | NaN | NaN | NaN | 28.7206 | 577.0345 | NaN | 30.0357 | NaN | 22.764
598.1292 | 11.655 | 11.7249 | 11.6238 | 11.9169 | 11.3574 | 12.1656 | 11.7625 | 11.4681 | NaN | NaN | NaN | 11.9384 | 92.5358 | NaN | NaN | NaN | -3.3797 | NaN | NaN | NaN | 26.0532 | 576.3565 | NaN | 30.247 | NaN | 26.2774
599.1292 | 11.6544 | 11.8011 | 11.6237 | 11.9666 | 11.2804 | 12.1263 | 11.7635 | 11.4658 | NaN | NaN | NaN | 11.801 | 93.628 | NaN | NaN | NaN | -6.0404 | NaN | NaN | NaN | 27.1335 | 576.9854 | NaN | 29.5503 | NaN | 22.4913
600.1292 | 11.673 | 11.5921 | 11.6289 | 11.9053 | 11.2493 | 12.0733 | 11.7113 | 11.4615 | NaN | NaN | NaN | 11.8253 | 94.8067 | NaN | NaN | NaN | -16.0593 | NaN | NaN | NaN | 23.6387 | 576.2809 | NaN | 28.9996 | NaN | 23.3378
601.1292 | 11.6384 | 11.446 | 11.6232 | 11.9306 | 11.5235 | 11.8585 | 11.6327 | 11.4742 | NaN | NaN | NaN | 11.7602 | 165.8792 | NaN | NaN | 68.2687 | 17.9802 | NaN | 217.5942 | NaN | 41.0195 | 483.3334 | NaN | -5.3848 | NaN | -1.2776
602.1292 | 11.6144 | 11.4118 | 11.6274 | 11.9661 | 11.5071 | 11.8311 | 11.6219 | 11.4824 | NaN | NaN | NaN | 11.741 | 170.4758 | NaN | NaN | -17.1901 | NaN | NaN | 222.3474 | NaN | 31.4321 | 464.0928 | NaN | -16.9481 | NaN | -11.1359
603.1292 | 11.661 | 11.4442 | 11.6307 | 11.9472 | 11.5568 | 11.8462 | 11.6295 | 11.476 | NaN | NaN | NaN | 11.7706 | 173.1823 | NaN | NaN | -0.489 | NaN | NaN | 221.0108 | NaN | 42.3214 | 456.8332 | NaN | -12.6142 | NaN | -7.0326
604.1292 | 11.6517 | 11.3942 | 11.6334 | 11.9869 | 11.5382 | 11.8064 | 11.6155 | 11.4782 | NaN | NaN | NaN | 11.7577 | 181.8259 | NaN | NaN | -12.755 | NaN | NaN | 235.5387 | NaN | 49.2202 | 452.8461 | NaN | -12.4667 | NaN | 7.4942
605.1292 | 11.6368 | 11.4131 | 11.6376 | 11.9705 | 11.5653 | 11.8351 | 11.6201 | 11.4812 | NaN | NaN | NaN | 11.7638 | 175.7974 | NaN | NaN | 5.5251 | NaN | NaN | 228.6947 | NaN | 45.8394 | 449.4886 | NaN | -12.7671 | NaN | -8.5729
606.1292 | 11.7133 | 11.4312 | 11.6284 | 11.9721 | 11.5215 | 11.8453 | 11.6255 | 11.4844 | NaN | NaN | NaN | 11.7535 | 179.8169 | NaN | NaN | 19.8399 | NaN | NaN | 223.6948 | NaN | 33.3948 | 446.8493 | NaN | NaN | NaN | -16.2423
607.1292 | 11.6347 | 11.4306 | 11.6364 | 11.9939 | 11.5672 | 11.8464 | 11.6237 | 11.4867 | NaN | NaN | NaN | 11.76 | 176.0359 | NaN | NaN | -13.1476 | NaN | NaN | 229.1613 | NaN | 45.5544 | 449.2499 | NaN | -1.5486 | NaN | 8.6364
608.1292 | 11.7033 | 11.4083 | 11.6356 | 12.0313 | 11.4824 | 11.8381 | 11.6253 | 11.4825 | NaN | NaN | NaN | 11.78 | 181.359 | NaN | NaN | -11.2 | NaN | NaN | 239.1421 | NaN | 46.3143 | 447.2315 | NaN | 12.8513 | NaN | 17.166
609.1292 | 11.6615 | 11.4042 | 11.6373 | 12.0015 | 11.5199 | 11.8343 | 11.6153 | 11.4854 | NaN | NaN | NaN | 11.8012 | 171.4952 | NaN | NaN | -2.9537 | NaN | NaN | 228.7377 | NaN | 42.4247 | 445.5789 | NaN | NaN | NaN | -0.5068
610.1292 | 11.8105 | 11.5563 | 11.6428 | 11.9442 | 11.543 | 11.9406 | 11.6599 | 11.4911 | NaN | NaN | NaN | 11.8148 | 181.2991 | NaN | NaN | 0.4905 | NaN | NaN | 222.5011 | NaN | 43.0809 | 444.6785 | NaN | -11.8289 | NaN | 12.1414
611.1292 | 11.6395 | 11.4328 | 11.646 | 11.983 | 11.5128 | 11.8607 | 11.6333 | 11.4924 | NaN | NaN | NaN | 11.8508 | 166.3104 | NaN | NaN | NaN | NaN | NaN | 227.1156 | NaN | 51.9812 | 443.5529 | NaN | -5.8978 | NaN | -5.7268
612.1292 | 11.6945 | 11.4253 | 11.6459 | 11.9724 | 11.5863 | 11.8396 | 11.6239 | 11.4902 | NaN | NaN | NaN | 11.9213 | 183.8519 | NaN | NaN | 1.3038 | NaN | NaN | 224.4085 | NaN | 31.1246 | 444.2269 | NaN | -14.4848 | NaN | 4.1788
613.1448 | 11.6823 | 11.4608 | 11.6557 | 11.9697 | 11.5843 | 11.8592 | 11.6337 | 11.4949 | NaN | NaN | NaN | 11.9602 | 183.4408 | NaN | NaN | 32.6237 | NaN | NaN | 221.9976 | NaN | 41.4796 | 447.7181 | NaN | -1.1746 | NaN | 7.2513
614.1292 | 11.678 | 11.4355 | 11.6585 | 11.9721 | 11.5575 | 11.8515 | 11.6363 | 11.5009 | NaN | NaN | NaN | 12.0461 | 185.1034 | NaN | NaN | NaN | NaN | NaN | 227.6907 | NaN | 36.0073 | 456.0167 | NaN | -19.4453 | NaN | -13.1302
615.1292 | 11.666 | 11.4214 | 11.6518 | 12.0088 | 11.6096 | 11.8355 | 11.6329 | 11.5054 | NaN | NaN | NaN | 12.1279 | 182.3549 | NaN | NaN | -2.4001 | NaN | NaN | 245.1895 | NaN | 37.3901 | 448.6246 | NaN | -2.801 | NaN | 1.0042
616.1292 | 11.6869 | 11.4818 | 11.6619 | 11.9917 | 11.5923 | 11.8886 | 11.6452 | 11.5005 | NaN | NaN | NaN | 12.2727 | 179.3602 | NaN | NaN | -10.4773 | NaN | NaN | 226.3202 | NaN | 38.3119 | 439.6769 | NaN | NaN | NaN | -11.8189
617.1292 | 11.6713 | 11.4383 | 11.6611 | 12.0017 | 11.6072 | 11.856 | 11.6432 | 11.5023 | NaN | NaN | NaN | 12.505 | 188.4322 | NaN | NaN | 3.6483 | NaN | NaN | 231.3414 | NaN | 43.1347 | 439.4617 | NaN | NaN | NaN | 7.9593
618.1292 | 11.6883 | 11.4312 | 11.6676 | 12.016 | 11.6316 | 11.826 | 11.6294 | 11.5047 | NaN | NaN | NaN | 12.8076 | 191.6178 | NaN | NaN | NaN | NaN | NaN | 210.4578 | NaN | 49.0614 | 444.6645 | NaN | 24.6711 | NaN | 25.5414
619.1292 | 11.6508 | 11.4391 | 11.6628 | 12.027 | 11.6526 | 11.8224 | 11.6318 | 11.5055 | NaN | NaN | NaN | 13.0986 | 95.5046 | NaN | NaN | NaN | NaN | NaN | 74.2558 | NaN | 87.6826 | 498.043 | NaN | 29.7178 | NaN | 27.6718
620.1292 | 11.702 | 11.438 | 11.6749 | 12.0145 | 11.4352 | 11.855 | 11.6503 | 11.5082 | NaN | NaN | NaN | 13.4646 | 90.4601 | NaN | NaN | NaN | 0.6833 | NaN | 64.7516 | NaN | 27.0021 | 537.6466 | NaN | 30.372 | NaN | 25.6478
621.1292 | 11.6683 | 11.8224 | 11.6732 | 11.9276 | 11.3456 | 12.2486 | 11.7832 | 11.5075 | NaN | NaN | NaN | 13.699 | 95.2515 | NaN | NaN | NaN | -11.8742 | NaN | 66.1613 | NaN | 27.8852 | 543.4138 | NaN | 29.6358 | NaN | 26.5411
622.1292 | 11.6824 | 11.6355 | 11.6757 | 11.9803 | 11.274 | 12.0791 | 11.7399 | 11.5091 | NaN | NaN | NaN | 14.0746 | 91.3241 | NaN | NaN | NaN | -1.4168 | NaN | 65.1814 | NaN | 25.3458 | 546.1465 | NaN | 29.483 | NaN | 22.9008
623.1292 | 11.8617 | 11.6581 | 11.6821 | 12.0057 | 11.3089 | 12.1023 | 11.7553 | 11.5144 | NaN | NaN | NaN | 14.3748 | 91.0723 | NaN | NaN | NaN | -11.1201 | NaN | 65.6127 | NaN | 26.418 | 547.3608 | NaN | 31.1161 | NaN | 23.2977
624.1292 | 11.8247 | 12.0671 | 11.6797 | 11.9969 | 11.3094 | 12.2706 | 11.8878 | 11.514 | NaN | NaN | NaN | 14.6356 | 92.659 | NaN | NaN | NaN | -18.3155 | NaN | 66.9152 | NaN | 27.2295 | 547.2343 | NaN | 29.1127 | NaN | 24.0046
625.1292 | 11.6852 | 11.7097 | 11.6824 | 11.9964 | 11.3775 | 12.0919 | 11.7714 | 11.5088 | NaN | NaN | NaN | 14.7946 | 93.9779 | NaN | NaN | NaN | -18.0141 | NaN | 64.5079 | NaN | 24.8849 | 548.0423 | NaN | 28.6008 | NaN | 28.2567
626.1292 | 11.7119 | 11.6503 | 11.6869 | 11.9526 | 11.277 | 12.0771 | 11.7676 | 11.521 | NaN | NaN | NaN | 15.0011 | 92.1604 | NaN | NaN | NaN | -13.4193 | NaN | 67.8965 | NaN | 26.9407 | 549.4462 | NaN | 28.9784 | NaN | 28.4349
627.1292 | 11.74 | 11.9306 | 11.68 | 12.0055 | 11.4157 | 12.2521 | 11.815 | 11.52 | NaN | NaN | NaN | 15.2029 | 97.9558 | NaN | NaN | NaN | NaN | NaN | 64.6328 | NaN | 29.9294 | 549.9618 | NaN | 27.9585 | NaN | 23.0825
628.1292 | 11.7825 | 11.686 | 11.6925 | 11.9818 | 11.381 | 12.1057 | 11.7823 | 11.524 | NaN | NaN | NaN | 15.3564 | 91.7386 | NaN | NaN | NaN | -17.1584 | NaN | 66.7493 | NaN | 26.1237 | 550.9731 | NaN | 28.6949 | NaN | 21.5533
629.1292 | 11.7267 | 11.7321 | 11.6926 | 12.0062 | 11.3586 | 12.0804 | 11.7656 | 11.5197 | NaN | NaN | NaN | 15.5353 | 93.1177 | NaN | NaN | NaN | -19.1904 | NaN | 65.0496 | NaN | 27.1035 | 548.3941 | NaN | 29.4399 | NaN | 27.6435
630.1292 | 11.7101 | 11.5649 | 11.6968 | 12.0275 | 11.3057 | 11.9808 | 11.7385 | 11.5229 | NaN | NaN | NaN | 15.6931 | 93.0658 | NaN | NaN | NaN | -11.5539 | NaN | 65.2801 | NaN | 25.7882 | 552.2849 | NaN | 28.8248 | NaN | 29.1738
631.1292 | 11.7458 | 11.8023 | 11.691 | 12.0618 | 11.331 | 12.1657 | 11.7983 | 11.5252 | NaN | NaN | NaN | 15.758 | 91.9789 | NaN | NaN | NaN | -12.079 | NaN | 65.5487 | NaN | 24.486 | 550.9282 | NaN | 29.31 | NaN | 27.5111
632.1292 | 11.797 | 11.7444 | 11.6947 | 12.1023 | 11.3411 | 12.067 | 11.7911 | 11.522 | NaN | NaN | NaN | 15.9226 | 95.0797 | NaN | NaN | NaN | -11.4205 | NaN | 65.0786 | NaN | 24.1322 | 551.0534 | NaN | 29.7543 | NaN | 23.0365
633.1292 | 11.7405 | 11.7524 | 11.6964 | 12.0611 | 11.3753 | 12.2103 | 11.8145 | 11.5278 | NaN | NaN | NaN | 16.017 | 90.6848 | NaN | NaN | NaN | -9.7561 | NaN | 63.9462 | NaN | 25.4186 | 551.4753 | NaN | 29.2483 | NaN | 27.737
634.1292 | 11.7534 | 11.7638 | 11.695 | 11.9823 | 11.506 | 12.1623 | 11.7866 | 11.5259 | NaN | NaN | NaN | 16.1865 | 103.8081 | NaN | NaN | NaN | -7.7651 | NaN | 64.5834 | NaN | 15.3712 | 556.2635 | NaN | 28.6516 | NaN | 28.2644
635.1292 | 11.71 | 11.6985 | 11.6986 | 11.9339 | 11.3796 | 12.1086 | 11.7616 | 11.5352 | NaN | NaN | NaN | 16.2574 | 97.1228 | NaN | NaN | NaN | NaN | NaN | 65.5671 | NaN | 30.622 | 568.3711 | NaN | 31.0543 | NaN | 29.6671
636.1292 | 11.7198 | 11.782 | 11.7013 | 12.0766 | 11.4501 | 12.1063 | 11.7843 | 11.5348 | NaN | NaN | NaN | 16.2998 | 92.6777 | NaN | NaN | NaN | -12.3396 | NaN | 64.8651 | NaN | 23.5808 | 579.9913 | NaN | 29.57 | NaN | 26.9959
637.1292 | 11.7191 | 11.6059 | 11.7055 | 12.0032 | 11.3544 | 12.0535 | 11.7442 | 11.5451 | NaN | NaN | NaN | 16.3796 | 91.7664 | NaN | NaN | NaN | -18.5345 | NaN | 65.9671 | NaN | 25.9375 | 590.9483 | NaN | 30.5094 | NaN | 25.0248
638.1292 | 11.7237 | 11.7075 | 11.7076 | 12.0004 | 11.3559 | 12.1357 | 11.8016 | 11.5428 | NaN | NaN | NaN | 16.4282 | 93.3701 | NaN | NaN | NaN | NaN | NaN | 64.5641 | NaN | 27.1991 | 603.2137 | NaN | 30.5448 | NaN | 22.253
639.1292 | 11.7189 | 11.8609 | 11.7004 | 12.0333 | 11.4046 | 12.3023 | 11.8536 | 11.5445 | NaN | NaN | NaN | 16.4899 | 94.8045 | NaN | NaN | NaN | -18.6507 | NaN | 65.2388 | NaN | 26.3939 | 611.7902 | NaN | 30.0939 | NaN | 21.9376
640.1292 | 11.7245 | 11.8024 | 11.7107 | 12.0152 | 11.2265 | 12.158 | 11.8185 | 11.5536 | NaN | NaN | NaN | 16.5834 | 92.5998 | NaN | NaN | NaN | -10.0636 | NaN | 66.2363 | NaN | 27.8671 | 622.8505 | NaN | 30.1927 | NaN | 28.3352
641.1292 | 11.724 | 11.8024 | 11.7104 | 11.9918 | 11.4142 | 12.2308 | 11.819 | 11.5536 | NaN | NaN | NaN | 16.6629 | 91.5947 | NaN | NaN | NaN | 1.7289 | NaN | 66.2473 | NaN | 29.708 | 636.9048 | NaN | 30.0476 | NaN | 30.0184
642.1292 | 11.7194 | 11.7874 | 11.7133 | 12.2743 | 11.2976 | 12.21 | 11.8347 | 11.5609 | NaN | NaN | NaN | 16.7238 | 91.6887 | NaN | NaN | NaN | -5.4192 | NaN | 65.0213 | NaN | 25.7392 | 645.8222 | NaN | 28.9008 | NaN | 27.7454
643.1292 | 11.7273 | 11.706 | 11.7209 | 12.0271 | 11.396 | 12.0579 | 11.7906 | 11.5581 | NaN | NaN | NaN | 16.7611 | 92.3175 | NaN | NaN | NaN | 0.462 | NaN | 66.3528 | NaN | 25.4775 | 660.1219 | NaN | 29.5426 | NaN | 29.0762
644.1292 | 11.7268 | 11.8232 | 11.7209 | 12.0436 | 11.3671 | 12.1297 | 11.8183 | 11.5621 | NaN | NaN | NaN | 16.7844 | 95.1274 | NaN | NaN | NaN | -12.2421 | NaN | 65.9288 | NaN | 27.7168 | 663.4466 | NaN | 30.0012 | NaN | 24.0296
645.1292 | 11.7355 | 11.7319 | 11.7322 | 12.1973 | 11.3073 | 12.1272 | 11.8191 | 11.5646 | NaN | NaN | NaN | 16.7893 | 91.8643 | NaN | NaN | NaN | -9.7369 | NaN | 65.8704 | NaN | 26.0131 | 660.9004 | NaN | 29.2942 | NaN | 29.1047
646.1292 | 11.738 | 11.7644 | 11.7292 | 11.9827 | 11.3513 | 12.0982 | 11.7929 | 11.5647 | NaN | NaN | NaN | 16.798 | 90.7802 | NaN | NaN | NaN | NaN | NaN | 65.3384 | NaN | 26.6516 | 667.5832 | NaN | 30.3182 | NaN | 28.7742
647.1292 | 11.7377 | 11.7708 | 11.7323 | 12.0177 | 11.3346 | 12.2803 | 11.8392 | 11.5575 | NaN | NaN | NaN | 16.7777 | 93.2862 | NaN | NaN | NaN | -10.6199 | NaN | 64.2959 | NaN | 26.2318 | 679.4033 | NaN | 29.7848 | NaN | 28.651
648.1292 | 11.7454 | 11.6339 | 11.736 | 12.0436 | 11.3519 | 12.0515 | 11.7634 | 11.5602 | NaN | NaN | NaN | 16.7852 | 90.4367 | NaN | NaN | NaN | -19.3922 | NaN | 66.1484 | NaN | 24.0347 | 696.0775 | NaN | 29.8225 | NaN | 28.4407
649.1292 | 11.7497 | 11.7886 | 11.7412 | 12.0154 | 11.3963 | 12.2033 | 11.8157 | 11.5614 | NaN | NaN | NaN | 16.7699 | 91.8854 | NaN | NaN | NaN | -15.9202 | NaN | 66.426 | NaN | 24.0004 | 667.6018 | NaN | 30.1851 | NaN | 28.2104
650.1292 | 11.7525 | 11.7267 | 11.7378 | 12.0735 | 11.4563 | 12.0399 | 11.7931 | 11.5537 | NaN | NaN | NaN | 16.7589 | 92.1908 | NaN | NaN | NaN | -19.1597 | NaN | 65.328 | NaN | 25.6615 | 656.9389 | NaN | 29.1733 | NaN | 29.6728
651.1292 | 11.7543 | 11.691 | 11.7379 | 12.0329 | 11.3996 | 12.1477 | 11.8157 | 11.5612 | NaN | NaN | NaN | 16.7369 | 93.7925 | NaN | NaN | NaN | -9.314 | NaN | 64.7229 | NaN | 24.6217 | 657.9276 | NaN | 28.6002 | NaN | 20.8146
652.1292 | 11.7606 | 11.7219 | 11.742 | 12.0451 | 11.3763 | 12.1263 | 11.8134 | 11.5606 | NaN | NaN | NaN | 16.7225 | 93.0887 | NaN | NaN | NaN | 11.2929 | NaN | 64.117 | NaN | 28.1478 | 658.8927 | NaN | 28.5473 | NaN | 29.4548
653.1292 | 11.7628 | 11.8164 | 11.7449 | 12.0022 | 11.358 | 12.0853 | 11.843 | 11.5646 | NaN | NaN | NaN | 16.6958 | 91.7574 | NaN | NaN | NaN | 2.0862 | NaN | 65.0462 | NaN | 28.4675 | 659.9531 | NaN | 31.1648 | NaN | 28.5449
654.1292 | 11.7609 | 11.8706 | 11.7437 | 12.0783 | 11.3761 | 12.2521 | 11.8468 | 11.5616 | NaN | NaN | NaN | 16.6778 | 94.4797 | NaN | NaN | NaN | -14.144 | NaN | 65.8606 | NaN | 27.035 | 660.3878 | NaN | 29.6766 | NaN | 21.0667
655.1292 | 11.7674 | 11.862 | 11.7521 | 12.0125 | 11.3762 | 12.1963 | 11.8488 | 11.5616 | NaN | NaN | NaN | 16.6371 | 93.0718 | NaN | NaN | NaN | -12.5421 | NaN | 65.1385 | NaN | 23.0601 | 658.7221 | NaN | 29.4294 | NaN | 28.7874
656.1292 | 11.7743 | 11.8096 | 11.7493 | 12.3253 | 11.4338 | 12.1706 | 11.8543 | 11.5652 | NaN | NaN | NaN | 16.5941 | 92.5754 | NaN | NaN | NaN | -12.5806 | NaN | 66.047 | NaN | 25.5424 | 656.2305 | NaN | 30.4985 | NaN | 26.6809
657.1292 | 11.7777 | 11.7416 | 11.7563 | 12.031 | 11.3581 | 12.1513 | 11.8064 | 11.5679 | NaN | NaN | NaN | 16.5632 | 93.0642 | NaN | NaN | NaN | -5.5036 | NaN | 64.3474 | NaN | 25.6 | 654.057 | NaN | 30.3591 | NaN | 28.6279
658.1292 | 11.7772 | 11.6609 | 11.7639 | 12.3604 | 11.3941 | 12.039 | 11.7985 | 11.5705 | NaN | NaN | NaN | 16.5263 | 95.9332 | NaN | NaN | NaN | 3.9883 | NaN | 64.6898 | NaN | 27.2017 | 654.3793 | NaN | 29.9928 | NaN | 28.2222
659.1292 | 11.7857 | 11.6293 | 11.7669 | 12.1466 | 11.4903 | 12.0158 | 11.7647 | 11.5775 | NaN | NaN | NaN | 16.4798 | 93.6039 | NaN | NaN | NaN | -10.3177 | NaN | 65.4678 | NaN | 26.9336 | 648.646 | NaN | 28.7788 | NaN | 28.1688
660.1292 | 11.7903 | 11.7188 | 11.7707 | 12.0748 | 11.3293 | 12.0686 | 11.8006 | 11.58 | NaN | NaN | NaN | 16.4362 | 91.2769 | NaN | NaN | NaN | -17.7344 | NaN | 66.5102 | NaN | 26.8868 | 648.2021 | NaN | 29.424 | NaN | 27.714
661.1292 | 11.7907 | 11.6451 | 11.7659 | 12.2217 | 11.38 | 12.0041 | 11.7888 | 11.5792 | NaN | NaN | NaN | 16.3917 | 93.0777 | NaN | NaN | NaN | -3.8122 | NaN | 66.693 | NaN | 25.3922 | 647.0367 | NaN | 29.3691 | NaN | 27.5439
662.1292 | 11.7977 | 11.7864 | 11.7696 | 12.0497 | 11.4395 | 12.1321 | 11.8495 | 11.5776 | NaN | NaN | NaN | 16.3482 | 94.0947 | NaN | NaN | NaN | -15.3017 | NaN | 65.0841 | NaN | 26.7711 | 646.3204 | NaN | 29.412 | NaN | 25.9765
663.1292 | 11.8009 | 11.9363 | 11.7665 | 12.047 | 11.4097 | 12.1859 | 11.8957 | 11.5836 | NaN | NaN | NaN | 16.3028 | 91.3032 | NaN | NaN | NaN | -4.5766 | NaN | 64.1406 | NaN | 25.8673 | 645.7233 | NaN | 28.5951 | NaN | 29.35
664.1292 | 11.8068 | 12.2018 | 11.7713 | 12.1421 | 11.317 | 12.4985 | 11.9813 | 11.5877 | NaN | NaN | NaN | 16.25 | 91.6862 | NaN | NaN | NaN | -18.3779 | NaN | 64.5473 | NaN | 26.1558 | 642.4298 | NaN | 30.8691 | NaN | 30.1782
665.1292 | 11.8101 | 12.1083 | 11.7772 | 12.0846 | 11.3564 | 12.4174 | 11.9586 | 11.5886 | NaN | NaN | NaN | 16.2097 | 91.7039 | NaN | NaN | NaN | -0.4404 | NaN | 64.783 | NaN | 25.8661 | 641.7808 | NaN | 27.8532 | NaN | 26.2384
666.1292 | 11.8072 | 11.7226 | 11.7786 | 12.075 | 11.4991 | 12.0992 | 11.8185 | 11.5976 | NaN | NaN | NaN | 16.164 | 98.9951 | NaN | NaN | NaN | -11.1976 | NaN | 65.105 | NaN | 28.1768 | 640.6838 | NaN | 30.0593 | NaN | 28.1303
667.1292 | 11.8092 | 11.8182 | 11.7832 | 12.1441 | 11.356 | 12.2403 | 11.8632 | 11.592 | NaN | NaN | NaN | 16.1284 | 93.1579 | NaN | NaN | NaN | -16.1328 | NaN | 65.9761 | NaN | 25.4617 | 639.1112 | NaN | 29.9246 | NaN | 28.5062
668.1292 | 11.8108 | 11.925 | 11.7829 | 12.0994 | 11.4507 | 12.2004 | 11.8939 | 11.5922 | NaN | NaN | NaN | 16.0833 | 94.863 | NaN | NaN | NaN | 8.9163 | NaN | 64.9104 | NaN | 26.3239 | 635.8745 | NaN | 27.968 | NaN | 25.9649
669.1292 | 11.8177 | 11.6697 | 11.781 | 12.0903 | 11.4767 | 12.043 | 11.8032 | 11.5945 | NaN | NaN | NaN | 16.0526 | 93.3574 | NaN | NaN | NaN | -15.825 | NaN | 65.2174 | NaN | 24.6745 | 634.4108 | NaN | 29.363 | NaN | 29.1283
670.1292 | 11.8184 | 11.8507 | 11.7747 | 12.0695 | 11.395 | 12.0941 | 11.8556 | 11.5959 | NaN | NaN | NaN | 16.0166 | 92.8811 | NaN | NaN | NaN | -16.125 | NaN | 65.6178 | NaN | 24.9378 | 631.7895 | NaN | 29.6107 | NaN | 28.4182
671.1292 | 11.814 | 11.7934 | 11.7811 | 12.1099 | 11.4297 | 12.1835 | 11.856 | 11.5951 | NaN | NaN | NaN | 15.9798 | 90.4977 | NaN | NaN | NaN | -13.4182 | NaN | 64.2058 | NaN | 26.2355 | 629.1062 | NaN | 30.0794 | NaN | 27.5388
672.1292 | 11.8147 | 11.832 | 11.7847 | 12.0844 | 11.4448 | 12.2267 | 11.8575 | 11.6034 | NaN | NaN | NaN | 15.9443 | 92.2791 | NaN | NaN | NaN | -9.3965 | NaN | 64.3697 | NaN | 28.9666 | 626.9042 | NaN | 28.4533 | NaN | 25.628
673.1292 | 11.8895 | 11.729 | 11.7838 | 12.2216 | 11.4341 | 12.1234 | 11.8296 | 11.6016 | NaN | NaN | NaN | 15.9189 | 92.3175 | NaN | NaN | NaN | -13.7748 | NaN | 65.4796 | NaN | 26.4501 | 622.6405 | NaN | 29.6245 | NaN | 28.3894
674.1448 | 11.932 | 11.7985 | 11.7786 | 12.0814 | 11.3816 | 12.1925 | 11.864 | 11.6083 | NaN | NaN | NaN | 15.8878 | 92.923 | NaN | NaN | NaN | -6.7992 | NaN | 66.3491 | NaN | 25.3762 | 624.3019 | NaN | 30.7567 | NaN | 28.1323
675.1292 | 11.8858 | 11.974 | 11.7844 | 12.1968 | 11.4875 | 12.3374 | 11.9312 | 11.6139 | NaN | NaN | NaN | 15.8739 | 92.283 | NaN | NaN | NaN | -0.7706 | NaN | 65.0468 | NaN | 24.1334 | 622.0115 | NaN | 29.3676 | NaN | 26.3064
676.1292 | 11.8 | 11.83 | 11.7769 | 12.0792 | 11.4644 | 12.264 | 11.8678 | 11.609 | NaN | NaN | NaN | 15.8535 | 95.3348 | NaN | NaN | NaN | 5.2509 | NaN | 66.2373 | NaN | 27.1789 | 621.0699 | NaN | 27.63 | NaN | 28.9082
677.1292 | 11.7761 | 11.8496 | 11.7836 | 12.0936 | 11.443 | 12.15 | 11.8693 | 11.6114 | NaN | NaN | NaN | 15.843 | 92.6034 | NaN | NaN | NaN | -13.2749 | NaN | 65.828 | NaN | 26.977 | 618.4673 | NaN | 28.8589 | NaN | 24.298
678.1292 | 11.8122 | 12.2025 | 11.7905 | 12.1349 | 11.4506 | 12.4013 | 12.0079 | 11.6153 | NaN | NaN | NaN | 15.8061 | 93.1587 | NaN | NaN | NaN | -17.9924 | NaN | 64.9138 | NaN | 28.3103 | 615.9916 | NaN | 30.2427 | NaN | 26.2528
679.1292 | 11.9747 | 12.0232 | 11.7888 | 12.1193 | 11.3364 | 12.2253 | 11.9043 | 11.6114 | NaN | NaN | NaN | 15.7704 | 94.2763 | NaN | NaN | NaN | -14.7199 | NaN | 64.8683 | NaN | 27.2767 | 615.2018 | NaN | 28.7425 | NaN | 27.7926
680.1292 | 11.9775 | 11.8194 | 11.8006 | 12.2006 | 11.4608 | 12.2847 | 11.8763 | 11.6111 | NaN | NaN | NaN | 15.7277 | 97.7916 | NaN | NaN | NaN | -13.8067 | NaN | 64.9141 | NaN | 25.8024 | 613.8888 | NaN | 28.0368 | NaN | 24.959
681.1292 | 12.0008 | 12.0958 | 11.8003 | 12.2577 | 11.4893 | 12.2335 | 11.9249 | 11.6148 | NaN | NaN | NaN | 15.6897 | 94.9794 | NaN | NaN | NaN | NaN | NaN | 64.3718 | NaN | 27.2659 | 612.496 | NaN | 31.8941 | NaN | 27.3624
682.1292 | 11.8121 | 12.0804 | 11.804 | 12.1104 | 11.4259 | 12.3456 | 11.9147 | 11.6209 | NaN | NaN | NaN | 15.6601 | 91.2779 | NaN | NaN | NaN | -5.8487 | NaN | 65.0208 | NaN | 24.9242 | 609.6418 | NaN | 30.3102 | NaN | 28.8541
683.1292 | 11.965 | 11.7973 | 11.8044 | 12.0981 | 11.5096 | 12.1681 | 11.8404 | 11.626 | NaN | NaN | NaN | 15.5968 | 95.5482 | NaN | NaN | NaN | -14.6702 | NaN | 65.4776 | NaN | 30.5309 | 609.8339 | NaN | 30.5609 | NaN | 24.2647
684.1292 | 11.8109 | 11.9234 | 11.8133 | 12.1705 | 11.4569 | 12.2207 | 11.8927 | 11.6232 | NaN | NaN | NaN | 15.5538 | 91.9257 | NaN | NaN | NaN | 13.0332 | NaN | 65.1608 | NaN | 29.3645 | 608.4143 | NaN | 30.6461 | NaN | 24.2118
685.1292 | 11.8406 | 11.9467 | 11.8051 | 12.147 | 11.47 | 12.2581 | 11.9187 | 11.6208 | NaN | NaN | NaN | 15.5106 | 93.5061 | NaN | NaN | NaN | -17.8058 | NaN | 63.6262 | NaN | 25.0167 | 607.3407 | NaN | 29.2901 | NaN | 27.3785
686.1292 | 11.8762 | 11.7947 | 11.8139 | 12.1745 | 11.3485 | 12.2304 | 11.8731 | 11.6291 | NaN | NaN | NaN | 15.4649 | 89.5908 | NaN | NaN | NaN | -16.7475 | NaN | 65.8482 | NaN | 25.1149 | 608.3258 | NaN | 29.3367 | NaN | 29.4048
687.1292 | 11.959 | 11.8489 | 11.8127 | 12.2289 | 11.5118 | 12.2533 | 11.8989 | 11.631 | NaN | NaN | NaN | 15.4206 | 91.2208 | NaN | NaN | NaN | -14.712 | NaN | 64.6684 | NaN | 24.9194 | 606.8083 | NaN | 29.2305 | NaN | 28.4526
688.1292 | 11.836 | 12.2155 | 11.8179 | 12.1208 | 11.496 | 12.4144 | 11.949 | 11.6303 | NaN | NaN | NaN | 15.3787 | 91.6019 | NaN | NaN | NaN | -16.4825 | NaN | 64.9197 | NaN | 27.1624 | 605.2321 | NaN | 30.5607 | NaN | 28.7442
689.1292 | 11.8346 | 12.0144 | 11.8191 | 12.2028 | 11.5122 | 12.3917 | 11.9093 | 11.6314 | NaN | NaN | NaN | 15.3258 | 93.1198 | NaN | NaN | NaN | 3.8653 | NaN | 66.74 | NaN | 26.3575 | 605.3905 | NaN | 28.8826 | NaN | 28.7611
690.1292 | 11.828 | 11.9305 | 11.8218 | 12.2914 | 11.5085 | 12.2827 | 11.914 | 11.6292 | NaN | NaN | NaN | 15.2735 | 95.8569 | NaN | NaN | NaN | 2.7992 | NaN | 64.9519 | NaN | 26.4479 | 602.5479 | NaN | 30.2526 | NaN | 28.4686
691.1292 | 11.9938 | 11.8826 | 11.8293 | 12.2028 | 11.5465 | 12.2702 | 11.8859 | 11.6345 | NaN | NaN | NaN | 15.2335 | 92.1756 | NaN | NaN | NaN | -16.5154 | NaN | 65.2118 | NaN | 27.8946 | 601.5605 | NaN | 29.5295 | NaN | 29.601
692.1292 | 12.0488 | 11.7892 | 11.824 | 12.1724 | 11.5252 | 12.1629 | 11.86 | 11.6396 | NaN | NaN | NaN | 15.1875 | 93.1334 | NaN | NaN | NaN | -5.6536 | NaN | 64.3195 | NaN | 28.5877 | 601.378 | NaN | 29.8766 | NaN | 26.7425
693.1292 | 12.2321 | 11.9668 | 11.8302 | 12.1297 | 11.5367 | 12.1992 | 11.9152 | 11.6392 | NaN | NaN | NaN | 15.137 | 93.9642 | NaN | NaN | NaN | -15.6647 | NaN | 63.2717 | NaN | 27.6466 | 598.3845 | NaN | 28.8552 | NaN | 27.4591
694.1292 | 12.0776 | 11.9196 | 11.8367 | 12.1496 | 11.5033 | 12.2122 | 11.8811 | 11.6431 | NaN | NaN | NaN | 15.0871 | 90.7529 | NaN | NaN | NaN | NaN | NaN | 65.5049 | NaN | 28.0496 | 598.9743 | NaN | 27.8317 | NaN | 29.2346
695.1292 | 11.8894 | 12.2028 | 11.8403 | 12.1901 | 11.456 | 12.2258 | 12.0057 | 11.644 | NaN | NaN | NaN | 15.0446 | 90.0026 | NaN | NaN | NaN | -2.2736 | NaN | 66.8759 | NaN | 23.7716 | 584.1866 | NaN | 31.0181 | NaN | 24.7996
696.1292 | 11.8736 | 11.8443 | 11.8518 | 12.1637 | 11.5953 | 12.2624 | 11.8922 | 11.6446 | NaN | NaN | NaN | 15 | 89.989 | NaN | NaN | NaN | -15.175 | NaN | 62.3585 | NaN | 26.5082 | 520.2219 | NaN | 28.0292 | NaN | 29.349
697.1292 | 11.8422 | 11.9266 | 11.8516 | 12.1763 | 11.5385 | 12.2762 | 11.9189 | 11.6515 | NaN | NaN | NaN | 14.9585 | 90.999 | NaN | NaN | NaN | 4.5468 | NaN | 64.726 | NaN | 26.0247 | 533.6338 | NaN | 29.8675 | NaN | 24.0008
698.1292 | 11.9991 | 11.8527 | 11.8533 | 12.2182 | 11.3346 | 12.2176 | 11.8917 | 11.6511 | NaN | NaN | NaN | 14.9126 | 91.4704 | NaN | NaN | NaN | -2.7675 | NaN | 65.1367 | NaN | 26.0307 | 551.8467 | NaN | 29.6258 | NaN | 29.018
699.1292 | 11.9578 | 11.8422 | 11.8523 | 12.1881 | 11.5672 | 12.1758 | 11.8858 | 11.659 | NaN | NaN | NaN | 14.872 | 91.6643 | NaN | NaN | NaN | -13.5594 | NaN | 64.3941 | NaN | 25.2497 | 570.6891 | NaN | 30.6338 | NaN | 29.4113
700.1292 | 11.9494 | 12.117 | 11.8585 | 12.1983 | 11.4912 | 12.2707 | 11.921 | 11.6639 | NaN | NaN | NaN | 14.8217 | 93.0482 | NaN | NaN | NaN | -10.0481 | NaN | 65.7144 | NaN | 27.9981 | 587.6129 | NaN | 30.4601 | NaN | 25.7678
701.1292 | 11.8822 | 11.8456 | 11.861 | 12.1705 | 11.4085 | 12.1904 | 11.8954 | 11.6648 | NaN | NaN | NaN | 14.7783 | 93.4638 | NaN | NaN | NaN | -11.6807 | NaN | 66.6293 | NaN | 26.4189 | 594.3203 | NaN | 30.0255 | NaN | 25.8992
702.1292 | 11.8663 | 11.9383 | 11.8635 | 12.5051 | 11.4592 | 12.3793 | 11.9232 | 11.6644 | NaN | NaN | NaN | 14.7374 | 92.5016 | NaN | NaN | NaN | -11.8388 | NaN | 65.1806 | NaN | 27.7496 | 593.0411 | NaN | 29.6507 | NaN | 28.5314
703.1292 | 11.9232 | 11.9474 | 11.8659 | 12.2057 | 11.4573 | 12.2359 | 11.9184 | 11.6654 | NaN | NaN | NaN | 14.6969 | 91.6652 | NaN | NaN | NaN | 4.906 | NaN | 63.276 | NaN | 24.9801 | 588.9827 | NaN | 29.594 | NaN | 28.7377
704.1292 | 11.9205 | 11.9344 | 11.8716 | 12.1844 | 11.5289 | 12.2482 | 11.9234 | 11.6655 | NaN | NaN | NaN | 14.6568 | 92.4591 | NaN | NaN | NaN | -16.7853 | NaN | 65.6586 | NaN | 25.6883 | 590.0604 | NaN | 30.5423 | NaN | 28.731
705.1292 | 12.0504 | 12.0564 | 11.8745 | 12.1599 | 11.554 | 12.4133 | 11.9175 | 11.6704 | NaN | NaN | NaN | 14.6221 | 91.4605 | NaN | NaN | NaN | -2.1269 | NaN | 65.0148 | NaN | 28.1518 | 589.9554 | NaN | 27.8211 | NaN | 28.7833
706.1292 | 11.9717 | 12.1519 | 11.8774 | 12.2552 | 11.4406 | 12.297 | 11.939 | 11.6747 | NaN | NaN | NaN | 14.5892 | 93.8491 | NaN | NaN | NaN | -4.9298 | NaN | 64.3329 | NaN | 23.1805 | 589.8189 | NaN | 28.4982 | NaN | 27.9096
707.1292 | 11.9106 | 11.9283 | 11.8812 | 12.1576 | 11.5545 | 12.244 | 11.9177 | 11.6776 | NaN | NaN | NaN | 14.5513 | 93.699 | NaN | NaN | NaN | -10.7446 | NaN | 64.4788 | NaN | 26.2229 | 587.6284 | NaN | 30.5882 | NaN | 28.3323
708.1292 | 11.8903 | 12.1944 | 11.8808 | 12.4725 | 11.4337 | 12.3567 | 12.0032 | 11.6819 | NaN | NaN | NaN | 14.5268 | 94.7865 | NaN | NaN | NaN | -14.6683 | NaN | 65.8772 | NaN | 23.404 | 588.6313 | NaN | 28.627 | NaN | 25.9734
709.1292 | 11.9626 | 12.1029 | 11.8909 | 12.2634 | 11.4668 | 12.3495 | 11.9783 | 11.6868 | NaN | NaN | NaN | 14.4896 | 90.1779 | NaN | NaN | NaN | -7.0089 | NaN | 63.4893 | NaN | 25.1509 | 587.415 | NaN | 26.4016 | NaN | 29.0024
710.1292 | 11.9193 | 11.9368 | 11.8869 | 12.2279 | 11.5981 | 12.1311 | 11.884 | 11.6861 | NaN | NaN | NaN | 14.4471 | 96.3829 | NaN | NaN | NaN | 5.4628 | NaN | 63.8238 | NaN | 28.7149 | 586.0114 | NaN | 29.9221 | NaN | 27.8419
711.1292 | 11.9924 | 12.1351 | 11.8907 | 12.2345 | 11.4585 | 12.1891 | 12.0036 | 11.689 | NaN | NaN | NaN | 14.4159 | 92.0774 | NaN | NaN | NaN | -6.8297 | NaN | 64.4386 | NaN | 26.4864 | 588.086 | NaN | 29.1403 | NaN | 29.3078
712.1292 | 11.9202 | 11.9234 | 11.8921 | 12.1997 | 11.5024 | 12.1728 | 11.9112 | 11.687 | NaN | NaN | NaN | 14.3763 | 93.5978 | NaN | NaN | NaN | -9.1379 | NaN | 65.4434 | NaN | 27.6229 | 586.8178 | NaN | 29.4057 | NaN | 27.2624
713.1292 | 12.1756 | 11.9315 | 11.8959 | 12.2135 | 11.5238 | 12.3034 | 11.916 | 11.6906 | NaN | NaN | NaN | 14.3381 | 88.7683 | NaN | NaN | NaN | -0.0269 | NaN | 64.0935 | NaN | 24.6652 | 585.4608 | NaN | 27.1872 | NaN | 27.5643
714.1292 | 11.9127 | 12.0064 | 11.9013 | 12.2411 | 11.4906 | 12.2443 | 11.9142 | 11.6917 | NaN | NaN | NaN | 14.2987 | 91.6572 | NaN | NaN | NaN | -19.4085 | NaN | 65.1004 | NaN | 28.8548 | 583.6117 | NaN | 28.9641 | NaN | 29.1375
715.1292 | 11.8784 | 11.9659 | 11.9047 | 12.1822 | 11.5811 | 12.2038 | 11.9164 | 11.7013 | NaN | NaN | NaN | 14.2575 | 94.6573 | NaN | NaN | NaN | -0.2573 | NaN | 64.1355 | NaN | 27.458 | 584.6871 | NaN | 29.1781 | NaN | 27.2638
716.1448 | 11.9187 | 11.946 | 11.909 | 12.2175 | 11.5906 | 12.2293 | 11.9183 | 11.6939 | NaN | NaN | NaN | 14.2349 | 90.685 | NaN | NaN | NaN | 1.7676 | NaN | 63.8148 | NaN | 26.0104 | 583.7919 | NaN | 29.0892 | NaN | 28.5289
717.1292 | 11.9428 | 12.0178 | 11.913 | 12.5572 | 11.5803 | 12.1765 | 11.9252 | 11.6936 | NaN | NaN | NaN | 14.2039 | 92.3996 | NaN | NaN | NaN | -18.5509 | NaN | 64.9703 | NaN | 26.656 | 583.1477 | NaN | 29.2494 | NaN | 28.4698
718.1292 | 12.1703 | 11.9859 | 11.9159 | 12.1836 | 11.6353 | 12.1741 | 11.9259 | 11.7003 | NaN | NaN | NaN | 14.1765 | 92.4401 | NaN | NaN | NaN | -18.2633 | NaN | 65.1392 | NaN | 23.4773 | 581.1321 | NaN | 26.7383 | NaN | 23.1789
719.1292 | 11.9531 | 11.9957 | 11.9171 | 12.2163 | 11.6436 | 12.2766 | 11.9276 | 11.7003 | NaN | NaN | NaN | 14.146 | 90.7011 | NaN | NaN | NaN | -10.7875 | NaN | 64.4052 | NaN | 26.5108 | 580.6564 | NaN | 30.171 | NaN | 29.5245
720.1292 | 11.968 | 11.9385 | 11.92 | 12.2044 | 11.5757 | 12.2088 | 11.9014 | 11.7001 | NaN | NaN | NaN | 14.115 | 92.8445 | NaN | NaN | NaN | -1.8117 | NaN | 64.7142 | NaN | 26.6194 | 579.2171 | NaN | 30.0486 | NaN | 26.9418
721.1292 | 11.9382 | 12.3047 | 11.9286 | 12.4044 | 11.5119 | 12.3098 | 11.9692 | 11.7061 | NaN | NaN | NaN | 14.0922 | 98.7532 | NaN | NaN | NaN | -18.7569 | NaN | 65.9296 | NaN | 23.5015 | 577.3963 | NaN | 27.7548 | NaN | 27.7766
722.1292 | 11.9776 | 11.8152 | 11.926 | 12.2873 | 11.6961 | 12.1111 | 11.8714 | 11.705 | NaN | NaN | NaN | 14.0646 | 95.2727 | NaN | NaN | NaN | NaN | NaN | 63.8996 | NaN | 24.2569 | 574.5616 | NaN | 27.651 | NaN | 23.3837
723.1292 | 12.0172 | 11.9941 | 11.9331 | 12.2462 | 11.6179 | 12.3807 | 11.9496 | 11.7052 | NaN | NaN | NaN | 14.0457 | 91.7907 | NaN | NaN | NaN | -5.5217 | NaN | 65.3165 | NaN | 25.7871 | 576.398 | NaN | 28.1653 | NaN | 25.8697
724.1292 | 11.9736 | 12.4973 | 11.9282 | 12.2494 | 11.4913 | 12.2629 | 12.0591 | 11.7029 | NaN | NaN | NaN | 14.0105 | 93.4007 | NaN | NaN | NaN | -16.1521 | NaN | 64.7566 | NaN | 24.8228 | 577.198 | NaN | 29.2482 | NaN | 28.9443
725.1292 | 12.0797 | 12.0621 | 11.9363 | 12.2231 | 11.4279 | 12.3712 | 11.9673 | 11.7095 | NaN | NaN | NaN | 13.9909 | 93.1347 | NaN | NaN | NaN | -0.5461 | NaN | 65.8652 | NaN | 25.1155 | 575.2195 | NaN | 27.912 | NaN | 28.3772
726.1292 | 12.0011 | 11.9361 | 11.941 | 12.2517 | 11.4949 | 12.1873 | 11.9267 | 11.7063 | NaN | NaN | NaN | 13.9608 | 89.6785 | NaN | NaN | NaN | -9.8939 | NaN | 64.9804 | NaN | 29.1338 | 575.4008 | NaN | 31.0009 | NaN | 21.8068
727.1292 | 12.095 | 11.965 | 11.9377 | 12.2456 | 11.4943 | 12.2421 | 11.9435 | 11.7086 | NaN | NaN | NaN | 13.9366 | 92.8512 | NaN | NaN | NaN | -14.1051 | NaN | 66.4204 | NaN | 30.2154 | 573.8444 | NaN | 28.4732 | NaN | 27.2959
728.1292 | 11.9568 | 11.9686 | 11.9434 | 12.2644 | 11.527 | 12.1741 | 11.9132 | 11.7117 | NaN | NaN | NaN | 13.9227 | 89.58 | NaN | NaN | NaN | -10.5132 | NaN | 64.3128 | NaN | 24.3596 | 572.6114 | NaN | 28.8544 | NaN | 21.2537
729.1292 | 11.9805 | 12.2284 | 11.9444 | 12.2343 | 11.5089 | 12.3177 | 12.0093 | 11.7133 | NaN | NaN | NaN | 13.9044 | 93.4027 | NaN | NaN | NaN | 6.1096 | NaN | 65.6141 | NaN | -9.4197 | 573.6046 | NaN | 28.7936 | NaN | 24.0926
730.1292 | 12.0112 | 12.1289 | 11.9417 | 12.2965 | 11.5277 | 12.3346 | 11.968 | 11.7168 | NaN | NaN | NaN | 13.891 | 92.0819 | NaN | NaN | NaN | 4.2027 | NaN | 64.675 | NaN | NaN | 573.1379 | NaN | 27.9782 | NaN | 29.0569
731.1292 | 11.9677 | 11.9718 | 11.9424 | 12.2996 | 11.4624 | 12.2121 | 11.9056 | 11.7172 | NaN | NaN | NaN | 13.8859 | 92.0978 | NaN | NaN | NaN | -18.5122 | NaN | 63.9061 | NaN | NaN | 573.4538 | NaN | 27.8749 | NaN | 28.1261
732.1292 | 12.0537 | 11.9855 | 11.9398 | 12.2634 | 11.649 | 12.2012 | 11.9258 | 11.7114 | NaN | NaN | NaN | 13.8788 | 92.8365 | NaN | NaN | NaN | -13.8549 | NaN | 65.4865 | NaN | NaN | 573.2163 | NaN | 29.8863 | NaN | 28.5062
733.1292 | 12.0346 | 12.0631 | 11.9501 | 12.2806 | 11.4556 | 12.3089 | 11.9742 | 11.714 | NaN | NaN | NaN | 13.8798 | 91.8614 | NaN | NaN | NaN | -17.6004 | NaN | 63.8291 | NaN | NaN | 570.5863 | NaN | 28.1439 | NaN | 29.3212
734.1292 | 12.0167 | 12.3033 | 11.9484 | 12.3629 | 11.6313 | 12.3041 | 12.0293 | 11.7207 | NaN | NaN | NaN | 13.8829 | 93.1826 | NaN | NaN | NaN | -6.2134 | NaN | 64.8549 | NaN | NaN | 554.7448 | NaN | 28.007 | NaN | 29.0955
735.1292 | 11.9978 | 12.057 | 11.9488 | 12.4241 | 11.4963 | 12.3138 | 11.9243 | 11.7218 | NaN | NaN | NaN | 13.9028 | 92.2188 | NaN | NaN | NaN | -10.8148 | NaN | 65.016 | NaN | NaN | 515.4146 | NaN | 29.6017 | NaN | 27.4836
736.1292 | 11.9466 | 11.9006 | 11.9449 | 12.2723 | 11.6211 | 12.1726 | 11.8816 | 11.7205 | NaN | NaN | NaN | 13.9366 | 91.8704 | NaN | NaN | NaN | -3.6863 | NaN | 64.1733 | NaN | NaN | 543.8175 | NaN | 29.2503 | NaN | 29.125
737.1292 | 12.0796 | 12.0145 | 11.9507 | 12.3126 | 11.5292 | 12.2927 | 11.927 | 11.7167 | NaN | NaN | NaN | 13.9814 | 91.1847 | NaN | NaN | NaN | -8.2018 | NaN | 65.4414 | NaN | NaN | 571.1937 | NaN | 29.9424 | NaN | 28.3711
738.1292 | 12.2722 | 12.2734 | 11.9495 | 12.2616 | 11.5689 | 12.4262 | 11.9803 | 11.7151 | NaN | NaN | NaN | 14.0137 | 91.6485 | NaN | NaN | NaN | -18.4713 | NaN | 63.7996 | NaN | NaN | 574.3053 | NaN | 30.6616 | NaN | 28.042
739.1292 | 12.1454 | 12.169 | 11.9544 | 12.3414 | 11.5814 | 12.4153 | 11.9446 | 11.7121 | NaN | NaN | NaN | 14.0619 | 92.2854 | NaN | NaN | NaN | -17.6471 | NaN | 66.2733 | NaN | NaN | 573.0161 | NaN | 29.0721 | NaN | 24.0313
740.1292 | 12.0312 | 12.108 | 11.9574 | 12.2903 | 11.6264 | 12.3742 | 11.9276 | 11.7125 | NaN | NaN | NaN | 14.0985 | 91.6448 | NaN | NaN | NaN | -14.5649 | NaN | 64.0863 | NaN | NaN | 572.3752 | NaN | 30.9311 | NaN | 25.7658
741.1292 | 12.0404 | 12.5183 | 11.9645 | 12.294 | 11.6274 | 12.3911 | 12.0151 | 11.7136 | NaN | NaN | NaN | 14.1376 | 92.0328 | NaN | NaN | NaN | -14.0942 | NaN | 66.4205 | NaN | NaN | 573.9098 | NaN | 29.5226 | NaN | 28.877
742.1292 | 12.0374 | 12.0286 | 11.9664 | 12.258 | 11.7322 | 12.2563 | 11.939 | 11.7091 | NaN | NaN | NaN | 14.1655 | 94.1966 | NaN | NaN | NaN | -16.0541 | NaN | 64.5592 | NaN | NaN | 572.2508 | NaN | 26.8155 | NaN | 29.3455
743.1292 | 11.9539 | 12.1415 | 11.9758 | 12.2553 | 11.4465 | 12.2626 | 11.9339 | 11.7159 | NaN | NaN | NaN | 14.1956 | 91.2451 | NaN | NaN | NaN | 11.0081 | NaN | 65.319 | NaN | NaN | 571.3889 | NaN | 29.2422 | NaN | 27.009
744.1292 | 12.0056 | 11.9482 | 11.9717 | 12.27 | 11.5765 | 12.2563 | 11.9133 | 11.7194 | NaN | NaN | NaN | 14.211 | 92.2991 | NaN | NaN | NaN | -10.953 | NaN | 64.6678 | NaN | NaN | 572.4702 | NaN | 28.0173 | NaN | 29.2152
745.1292 | 12.0198 | 12.1165 | 11.9742 | 12.2658 | 11.664 | 12.3485 | 11.9245 | 11.7211 | NaN | NaN | NaN | 14.2273 | 92.4462 | NaN | NaN | NaN | -17.5774 | NaN | 64.4195 | NaN | NaN | 571.047 | NaN | 28.2421 | NaN | 28.8828
746.1292 | 12.0915 | 11.9474 | 11.9745 | 12.4125 | 11.559 | 12.2235 | 11.9079 | 11.714 | NaN | NaN | NaN | 14.2379 | 91.8101 | NaN | NaN | NaN | -7.0211 | NaN | 64.5706 | NaN | NaN | 571.4516 | NaN | 28.7397 | NaN | 29.0421
747.1292 | 12.0584 | 11.9589 | 11.9777 | 12.2466 | 11.6203 | 12.2167 | 11.9085 | 11.7194 | NaN | NaN | NaN | 14.2626 | 92.2363 | NaN | NaN | NaN | -14.9072 | NaN | 65.455 | NaN | NaN | 571.2661 | NaN | 27.3534 | NaN | 27.2852
748.1292 | 12.0109 | 12.1362 | 11.9774 | 12.2566 | 11.5142 | 12.4575 | 11.9694 | 11.7158 | NaN | NaN | NaN | 14.2649 | 93.1986 | NaN | NaN | NaN | -15.3187 | NaN | 64.8211 | NaN | NaN | 570.6162 | NaN | 29.164 | NaN | 28.0973
749.1292 | 12.1026 | 12.2639 | 11.9791 | 12.2473 | 11.6602 | 12.3995 | 11.9589 | 11.7156 | NaN | NaN | NaN | 14.2573 | 95.9868 | NaN | NaN | NaN | 7.4015 | NaN | 64.8551 | NaN | NaN | 569.8461 | NaN | 27.7454 | NaN | 28.9773
750.1292 | 12.08 | 12.1057 | 11.9837 | 12.3502 | 11.7447 | 12.2821 | 11.9642 | 11.7161 | NaN | NaN | NaN | 14.2567 | 91.8535 | NaN | NaN | NaN | -13.2503 | NaN | 64.6833 | NaN | NaN | 567.5099 | NaN | 27.435 | NaN | 29.0722
751.1292 | 12.084 | 12.2336 | 11.9847 | 12.3805 | 11.6234 | 12.3659 | 12.0062 | 11.7161 | NaN | NaN | NaN | 14.2512 | 93.9397 | NaN | NaN | NaN | -6.7074 | NaN | 64.0915 | NaN | NaN | 569.6435 | NaN | 30.4163 | NaN | 28.5756
752.1292 | 12.2495 | 12.3155 | 11.9886 | 12.5192 | 11.6063 | 12.4913 | 11.9848 | 11.7193 | NaN | NaN | NaN | 14.2403 | 92.7648 | NaN | NaN | NaN | -12.5265 | NaN | 65.7232 | NaN | NaN | 568.2326 | NaN | 28.3036 | NaN | 29.2848
753.1292 | 12.1923 | 11.9824 | 11.9904 | 12.2512 | 11.6874 | 12.2568 | 11.9346 | 11.7116 | NaN | NaN | NaN | 14.2292 | 92.0371 | NaN | NaN | NaN | 6.1112 | NaN | 64.7532 | NaN | NaN | 569.1971 | NaN | 28.5993 | NaN | 28.5834
754.1292 | 12.1516 | 12.2196 | 11.9985 | 12.3598 | 11.6082 | 12.4254 | 11.9811 | 11.714 | NaN | NaN | NaN | 14.2028 | 91.4538 | NaN | NaN | NaN | -18.0796 | NaN | 65.1122 | NaN | NaN | 567.5898 | NaN | 30.2722 | NaN | 28.6627
755.1292 | 12.0508 | 11.9609 | 11.999 | 12.2772 | 11.6504 | 12.2432 | 11.925 | 11.7121 | NaN | NaN | NaN | 14.1875 | 90.5913 | NaN | NaN | NaN | 0.8471 | NaN | 64.0502 | NaN | NaN | 565.9946 | NaN | 29.7193 | NaN | 28.1403
756.1292 | 12.3465 | 12.1455 | 12.0047 | 12.308 | 11.6029 | 12.3509 | 12.0124 | 11.7225 | NaN | NaN | NaN | 14.146 | 92.8588 | NaN | NaN | NaN | -7.0783 | NaN | 65.3242 | NaN | NaN | 563.079 | NaN | 30.3218 | NaN | 27.978
757.1292 | 12.0622 | 12.0944 | 11.9984 | 12.2688 | 11.6078 | 12.3219 | 11.9464 | 11.7203 | NaN | NaN | NaN | 14.1171 | 91.2913 | NaN | NaN | NaN | -14.0294 | NaN | 66.0637 | NaN | NaN | 562.7018 | NaN | 29.3706 | NaN | 28.9385
758.1292 | 12.2321 | 12.2328 | 12.0077 | 12.4028 | 11.5586 | 12.3128 | 12.0311 | 11.7291 | NaN | NaN | NaN | 14.0947 | 91.4601 | NaN | NaN | NaN | -12.7007 | NaN | 66.2932 | NaN | NaN | 562.3647 | NaN | 28.0709 | NaN | 27.2797
759.1292 | 12.0644 | 12.5153 | 12.013 | 12.292 | 11.5492 | 12.4392 | 12.0801 | 11.7268 | NaN | NaN | NaN | 14.0581 | 91.767 | NaN | NaN | NaN | -16.0186 | NaN | 66.0737 | NaN | NaN | 563.6871 | NaN | 27.2785 | NaN | 29.1447
760.1292 | 12.1194 | 12.1469 | 12.0158 | 12.3107 | 11.6405 | 12.3314 | 11.9924 | 11.7296 | NaN | NaN | NaN | 14.0293 | 91.495 | NaN | NaN | NaN | -12.4974 | NaN | 63.6239 | NaN | NaN | 560.1786 | NaN | 27.6989 | NaN | 28.6054
761.1292 | 12.2271 | 12.244 | 12.0211 | 12.3335 | 11.5276 | 12.3775 | 12.0228 | 11.729 | NaN | NaN | NaN | 13.9963 | 92.3297 | NaN | NaN | NaN | 6.7676 | NaN | 64.985 | NaN | NaN | 556.9151 | NaN | 27.9263 | NaN | 29.9184
762.1292 | 12.0919 | 12.09 | 12.0097 | 12.3357 | 11.6433 | 12.3662 | 11.9778 | 11.7297 | NaN | NaN | NaN | 13.9723 | 91.4296 | NaN | NaN | NaN | -6.7236 | NaN | 65.4817 | NaN | NaN | 560.4578 | NaN | 28.0039 | NaN | 29.2214
763.1292 | 12.1109 | 12.0234 | 12.0183 | 12.4943 | 11.7074 | 12.3387 | 11.9725 | 11.7352 | NaN | NaN | NaN | 13.9408 | 91.1931 | NaN | NaN | NaN | -16.0571 | NaN | 63.5163 | NaN | NaN | 557.8739 | NaN | 26.3623 | NaN | 29.1082
764.1292 | 12.2124 | 12.0031 | 12.0209 | 12.3323 | 11.669 | 12.3652 | 11.972 | 11.7367 | NaN | NaN | NaN | 13.9227 | 92.9907 | NaN | NaN | NaN | -14.1372 | NaN | 65.6758 | NaN | NaN | 556.3682 | NaN | 26.8639 | NaN | 28.1673
765.1292 | 12.0494 | 12.2174 | 12.02 | 12.3472 | 11.5755 | 12.3614 | 11.9914 | 11.7377 | NaN | NaN | NaN | 13.8698 | 91.5081 | NaN | NaN | NaN | -5.562 | NaN | 65.8232 | NaN | NaN | 555.3451 | NaN | 30.4589 | NaN | 28.1558
766.1292 | 12.4396 | 11.981 | 12.0193 | 12.3567 | 11.5831 | 12.2621 | 11.9535 | 11.7398 | NaN | NaN | NaN | 13.8309 | 91.9893 | NaN | NaN | NaN | -18.3135 | NaN | 66.1015 | NaN | NaN | 557.6415 | NaN | 29.106 | NaN | 28.8155
767.1292 | 12.113 | 12.4076 | 12.0196 | 12.3625 | 11.699 | 12.535 | 12.0538 | 11.737 | NaN | NaN | NaN | 13.7986 | 92.7273 | NaN | NaN | NaN | -18.0746 | NaN | 63.7472 | NaN | NaN | 556.1387 | NaN | 28.9728 | NaN | 29.0817
768.1292 | 12.2078 | 12.1226 | 12.0261 | 12.3609 | 11.5544 | 12.3239 | 11.9734 | 11.7445 | NaN | NaN | NaN | 13.7805 | 93.5191 | NaN | NaN | NaN | -1.7753 | NaN | 64.2012 | NaN | NaN | 557.4523 | NaN | 27.323 | NaN | 28.7239
769.1292 | 12.1908 | 12.6323 | 12.0249 | 12.3217 | 11.599 | 12.4166 | 12.201 | 11.7408 | NaN | NaN | NaN | 13.7507 | 92.404 | NaN | NaN | NaN | -17.3519 | NaN | 65.6629 | NaN | NaN | 555.6356 | NaN | 26.6378 | NaN | 20.576
770.1292 | 12.1003 | 12.1666 | 12.0258 | 12.3761 | 11.614 | 12.4765 | 11.9958 | 11.7484 | NaN | NaN | NaN | 13.7192 | 91.7223 | NaN | NaN | NaN | -6.9872 | NaN | 64.2936 | NaN | NaN | 560.2822 | NaN | 27.147 | NaN | 29.0584
771.1292 | 12.1319 | 12.1147 | 12.0337 | 12.4251 | 11.5699 | 12.373 | 11.9748 | 11.7433 | NaN | NaN | NaN | 13.682 | 92.4079 | NaN | NaN | NaN | -14.102 | NaN | 64.7846 | NaN | NaN | 556.3693 | NaN | 27.7529 | NaN | 27.7348
772.1292 | 12.2302 | 12.0405 | 12.0289 | 12.3682 | 11.7308 | 12.4491 | 11.9736 | 11.7525 | NaN | NaN | NaN | 13.6508 | 91.5355 | NaN | NaN | NaN | -11.3575 | NaN | 65.0423 | NaN | NaN | 556.7378 | NaN | 30.7997 | NaN | 28.5277
773.1292 | 12.1349 | 12.4154 | 12.0319 | 12.3751 | 11.6812 | 12.4538 | 12.0861 | 11.7465 | NaN | NaN | NaN | 13.612 | 92.4119 | NaN | NaN | NaN | -5.4439 | NaN | 64.8724 | NaN | NaN | 557.376 | NaN | 27.3801 | NaN | 29.0426
774.1292 | 12.2814 | 12.3431 | 12.0305 | 12.4905 | 11.5348 | 12.496 | 12.0186 | 11.7521 | NaN | NaN | NaN | 13.5769 | 92.2338 | NaN | NaN | NaN | -2.4008 | NaN | 66.3653 | NaN | NaN | 557.8209 | NaN | 27.518 | NaN | 20.5972
775.1292 | 12.1634 | 12.0353 | 12.0385 | 12.3759 | 11.5706 | 12.2998 | 11.9703 | 11.7504 | NaN | NaN | NaN | 13.5392 | 91.7516 | NaN | NaN | NaN | NaN | NaN | 65.5911 | NaN | NaN | 558.749 | NaN | 28.0519 | NaN | 28.5782
776.1292 | 12.1896 | 12.3499 | 12.041 | 12.4295 | 11.6643 | 12.4347 | 12.0766 | 11.7556 | NaN | NaN | NaN | 13.5219 | 92.3549 | NaN | NaN | NaN | -15.4684 | NaN | 65.6192 | NaN | NaN | 556.1418 | NaN | 28.359 | NaN | 28.6512
777.1292 | 12.1042 | 12.1844 | 12.0447 | 12.3902 | 11.6007 | 12.3546 | 12.0059 | 11.7585 | NaN | NaN | NaN | 13.4822 | 92.0598 | NaN | NaN | NaN | -11.4252 | NaN | 64.7725 | NaN | NaN | 557.0199 | NaN | 26.5048 | NaN | 28.5428
778.1292 | 12.1608 | 11.9578 | 12.0505 | 12.3029 | 11.6702 | 12.253 | 11.9591 | 11.7559 | NaN | NaN | NaN | 13.4551 | 91.5885 | NaN | NaN | NaN | -17.1095 | NaN | 65.3167 | NaN | NaN | 556.8451 | NaN | 29.7141 | NaN | 29.0376
779.1292 | 12.2402 | 12.2454 | 12.0547 | 12.4569 | 11.6104 | 12.3555 | 12.0187 | 11.7537 | NaN | NaN | NaN | 13.4063 | 92.0379 | NaN | NaN | NaN | 5.0712 | NaN | 64.6278 | NaN | NaN | 555.1059 | NaN | 28.02 | NaN | 29.1436
780.1292 | 12.27 | 12.1003 | 12.0603 | 12.3352 | 11.6046 | 12.3843 | 11.9912 | 11.7632 | NaN | NaN | NaN | 13.3915 | 91.4899 | NaN | NaN | NaN | -18.9173 | NaN | 65.2086 | NaN | NaN | 556.9352 | NaN | 28.1477 | NaN | 26.4216
781.1292 | 12.3478 | 11.9915 | 12.0646 | 12.3875 | 11.7178 | 12.3648 | 11.9843 | 11.7598 | NaN | NaN | NaN | 13.3559 | 91.6712 | NaN | NaN | NaN | -14.9583 | NaN | 65.4168 | NaN | NaN | 554.3751 | NaN | 28.3493 | NaN | 29.2903
782.1292 | 12.3867 | 12.1166 | 12.064 | 12.3274 | 11.6484 | 12.3362 | 12.0018 | 11.7637 | NaN | NaN | NaN | 13.3312 | 91.0003 | NaN | NaN | NaN | -1.2531 | NaN | 64.3535 | NaN | NaN | 554.7281 | NaN | 27.812 | NaN | 29.2744
783.1292 | 12.17 | 12.1103 | 12.0668 | 12.5724 | 11.671 | 12.3658 | 12.0017 | 11.7678 | NaN | NaN | NaN | 13.3097 | 92.3103 | NaN | NaN | NaN | -7.1697 | NaN | 64.1331 | NaN | NaN | 552.9057 | NaN | 28.2695 | NaN | 29.2151
784.1292 | 12.146 | 12.1804 | 12.071 | 12.5157 | 11.7096 | 12.4007 | 12.0262 | 11.7655 | NaN | NaN | NaN | 13.2926 | 92.0182 | NaN | NaN | NaN | -1.9538 | NaN | 64.147 | NaN | NaN | 555.4329 | NaN | 29.3066 | NaN | 28.1812
785.1292 | 12.3936 | 12.3627 | 12.0716 | 12.2839 | 11.5755 | 12.7502 | 12.0857 | 11.7732 | NaN | NaN | NaN | 13.2775 | 91.0998 | NaN | NaN | NaN | -14.2413 | NaN | 66.8324 | NaN | NaN | 554.6882 | NaN | 28.1554 | NaN | 28.4029
786.1292 | 12.2467 | 12.0734 | 12.0726 | 12.4262 | 11.5839 | 12.4174 | 11.9982 | 11.7673 | NaN | NaN | NaN | 13.2265 | 95.1249 | NaN | NaN | NaN | -3.8138 | NaN | 63.9536 | NaN | NaN | 555.4112 | NaN | 26.9249 | NaN | 28.6454
787.1292 | 12.1623 | 12.4628 | 12.0746 | 12.3325 | 11.7058 | 12.6819 | 12.1083 | 11.7743 | NaN | NaN | NaN | 13.2039 | 91.2773 | NaN | NaN | NaN | -13.4828 | NaN | 65.0002 | NaN | NaN | 552.8561 | NaN | 26.8023 | NaN | 28.7797
788.1292 | 12.1744 | 12.0875 | 12.0753 | 12.363 | 11.7468 | 12.3456 | 11.9782 | 11.7779 | NaN | NaN | NaN | 13.1753 | 93.1899 | NaN | NaN | NaN | -6.3501 | NaN | 63.6754 | NaN | NaN | 548.8575 | NaN | 28.4983 | NaN | 29.0133
789.1292 | 12.1886 | 12.1204 | 12.0792 | 12.4784 | 11.7326 | 12.3815 | 12.0132 | 11.7745 | NaN | NaN | NaN | 13.1609 | 92.9178 | NaN | NaN | NaN | -15.606 | NaN | 63.9919 | NaN | NaN | 547.2698 | NaN | 27.4794 | NaN | 27.2922
790.1292 | 12.2575 | 12.1086 | 12.0796 | 12.3314 | 11.7488 | 12.4017 | 12.0081 | 11.7796 | NaN | NaN | NaN | 13.1334 | 91.8522 | NaN | NaN | NaN | -9.2303 | NaN | 63.2916 | NaN | NaN | 551.8543 | NaN | 29.5455 | NaN | 29.1209
791.1292 | 12.3402 | 12.2115 | 12.0845 | 12.2957 | 11.7083 | 12.3355 | 12.0454 | 11.7807 | NaN | NaN | NaN | 13.1158 | 91.2018 | NaN | NaN | NaN | -1.7321 | NaN | 63.7996 | NaN | NaN | 551.4052 | NaN | 27.775 | NaN | 27.1546
792.1292 | 12.2321 | 12.7609 | 12.0795 | 12.2816 | 11.7446 | 12.6252 | 12.2237 | 11.7804 | NaN | NaN | NaN | 13.0958 | 92.9042 | NaN | NaN | NaN | -12.4026 | NaN | 64.137 | NaN | NaN | 551.9629 | NaN | 29.3913 | NaN | 28.4603
793.1292 | 12.291 | 12.3196 | 12.0814 | 12.3811 | 11.73 | 12.4291 | 12.0791 | 11.7876 | NaN | NaN | NaN | 13.0793 | 90.9479 | NaN | NaN | NaN | -1.2976 | NaN | 63.8779 | NaN | NaN | 552.3628 | NaN | 27.4618 | NaN | 28.3841
794.1292 | 12.1492 | 12.1763 | 12.0799 | 12.4657 | 11.7099 | 12.3671 | 12.0384 | 11.7844 | NaN | NaN | NaN | 13.0589 | 92.2147 | NaN | NaN | NaN | -11.8979 | NaN | 64.7907 | NaN | NaN | 551.9258 | NaN | 26.5044 | NaN | 26.6673
795.1292 | 12.2098 | 12.2169 | 12.0883 | 12.3875 | 11.7188 | 12.6254 | 12.0437 | 11.7859 | NaN | NaN | NaN | 13.0411 | 92.3503 | NaN | NaN | NaN | 29.2168 | NaN | 64.6209 | NaN | NaN | 552.8061 | NaN | 28.9015 | NaN | 27.7111
796.1292 | 12.3418 | 12.075 | 12.0849 | 12.3701 | 11.5901 | 12.3662 | 12.0127 | 11.7871 | NaN | NaN | NaN | 13.0273 | 91.8228 | NaN | NaN | NaN | -12.5436 | NaN | 65.1394 | NaN | NaN | 554.8894 | NaN | 29.2265 | NaN | 28.1735
797.1292 | 12.2618 | 12.2758 | 12.0848 | 12.4008 | 11.7351 | 12.4363 | 12.0333 | 11.7886 | NaN | NaN | NaN | 13.0081 | 91.5432 | NaN | NaN | NaN | -17.5832 | NaN | 65.2235 | NaN | NaN | 553.8227 | NaN | 28.4988 | NaN | 28.1977
798.1292 | 12.2068 | 12.244 | 12.0871 | 12.3162 | 11.6945 | 12.4577 | 12.0691 | 11.7971 | NaN | NaN | NaN | 12.9906 | 92.52 | NaN | NaN | NaN | -18.6044 | NaN | 64.1915 | NaN | NaN | 554.8555 | NaN | 28.3571 | NaN | 26.4162
799.1292 | 12.4294 | 12.2721 | 12.0895 | 12.3109 | 11.7152 | 12.4658 | 12.0459 | 11.7976 | NaN | NaN | NaN | 12.9741 | 92.2038 | NaN | NaN | NaN | -7.175 | NaN | 65.4797 | NaN | NaN | 552.9026 | NaN | 27.7773 | NaN | 28.34
800.1292 | 12.4122 | 12.4125 | 12.0937 | 12.3474 | 11.7395 | 12.623 | 12.1277 | 11.7961 | NaN | NaN | NaN | 12.9511 | 92.7707 | NaN | NaN | NaN | -13.7085 | NaN | 64.2125 | NaN | NaN | 556.0146 | NaN | 27.5187 | NaN | 28.7686
801.1292 | 12.407 | 12.1401 | 12.0983 | 12.3536 | 11.6233 | 12.3946 | 12.0258 | 11.7966 | NaN | NaN | NaN | 12.945 | 92.2507 | NaN | NaN | NaN | -13.0203 | NaN | 64.5858 | NaN | NaN | 555.4778 | NaN | 29.0448 | NaN | 28.8831
802.1292 | 12.2845 | 12.1138 | 12.099 | 12.3946 | 11.6569 | 12.4397 | 12.0343 | 11.7932 | NaN | NaN | NaN | 12.9263 | 90.977 | NaN | NaN | NaN | -12.0397 | NaN | 63.7866 | NaN | NaN | 553.5663 | NaN | 27.2469 | NaN | 28.7303
803.1292 | 12.4642 | 12.2441 | 12.099 | 12.2968 | 11.6502 | 12.4478 | 12.037 | 11.8019 | NaN | NaN | NaN | 12.929 | 91.7296 | NaN | NaN | NaN | -12.3194 | NaN | 63.7878 | NaN | NaN | 554.0625 | NaN | 27.9809 | NaN | 28.8073
804.1292 | 12.2343 | 12.2839 | 12.0922 | 12.3855 | 11.6712 | 12.5029 | 12.0348 | 11.7991 | NaN | NaN | NaN | 12.8919 | 91.7337 | NaN | NaN | NaN | -11.9439 | NaN | 64.9022 | NaN | NaN | 555.9737 | NaN | 28.621 | NaN | 29.4227
805.1292 | 12.5845 | 12.1611 | 12.0961 | 12.4748 | 11.6989 | 12.3941 | 12.0444 | 11.7973 | NaN | NaN | NaN | 12.882 | 91.2107 | NaN | NaN | NaN | -9.4494 | NaN | 63.9342 | NaN | NaN | 556.2819 | NaN | 28.8324 | NaN | 28.9065
806.1292 | 12.469 | 12.0718 | 12.1042 | 12.46 | 11.6776 | 12.3387 | 12.0196 | 11.8044 | NaN | NaN | NaN | 12.8672 | 91.7397 | NaN | NaN | NaN | -5.8245 | NaN | 64.2724 | NaN | NaN | 557.1988 | NaN | 28.2178 | NaN | 27.9935
807.1292 | 12.2308 | 12.1998 | 12.1009 | 12.3476 | 11.6925 | 12.4894 | 12.0554 | 11.7999 | NaN | NaN | NaN | 12.8646 | 92.9562 | NaN | NaN | NaN | -14.5695 | NaN | 65.308 | NaN | NaN | 557.3834 | NaN | 29.7166 | NaN | 28.8936
808.1292 | 12.3789 | 12.1908 | 12.1067 | 12.363 | 11.7602 | 12.4988 | 12.0266 | 11.8079 | NaN | NaN | NaN | 12.8518 | 92.3707 | NaN | NaN | NaN | -18.8491 | NaN | 63.7532 | NaN | NaN | 557.5228 | NaN | 29.2751 | NaN | 28.2478
809.1292 | 12.3137 | 12.4109 | 12.1081 | 12.3611 | 11.6391 | 12.6281 | 12.0994 | 11.8021 | NaN | NaN | NaN | 12.8467 | 92.1783 | NaN | NaN | NaN | -17.6239 | NaN | 64.7527 | NaN | NaN | 555.1943 | NaN | 28.1505 | NaN | 26.2716
810.1292 | 12.3768 | 12.1483 | 12.1079 | 12.3556 | 11.7941 | 12.4184 | 12.0457 | 11.8101 | NaN | NaN | NaN | 12.8248 | 92.6424 | NaN | NaN | NaN | -17.9503 | NaN | 63.2401 | NaN | NaN | 554.6563 | NaN | 29.2341 | NaN | 28.2028
811.1292 | 12.5212 | 12.5069 | 12.1118 | 12.3296 | 11.7277 | 12.746 | 12.1682 | 11.8063 | NaN | NaN | NaN | 12.823 | 95.773 | NaN | NaN | NaN | -15.3424 | NaN | 64.1996 | NaN | NaN | 557.6098 | NaN | 28.2203 | NaN | 27.9164
812.1292 | 12.1848 | 12.0934 | 12.1143 | 12.7131 | 11.6283 | 12.4221 | 12.022 | 11.8085 | NaN | NaN | NaN | 12.8109 | 91.6399 | NaN | NaN | NaN | -15.9615 | NaN | 65.4824 | NaN | NaN | 556.3725 | NaN | 30.2283 | NaN | 28.9657
813.1292 | 12.2152 | 12.2695 | 12.1131 | 12.4212 | 11.6484 | 12.5202 | 12.0762 | 11.8119 | NaN | NaN | NaN | 12.8062 | 92.3851 | NaN | NaN | NaN | -5.5376 | NaN | 64.76 | NaN | NaN | 557.8728 | NaN | 28.2019 | NaN | 29.1017
814.1292 | 12.4864 | 12.136 | 12.114 | 12.3948 | 11.6752 | 12.3843 | 12.0133 | 11.8063 | NaN | NaN | NaN | 12.8034 | 96.2548 | NaN | NaN | NaN | -15.3097 | NaN | 65.4592 | NaN | NaN | 555.6832 | NaN | 28.5996 | NaN | 28.8573
815.1292 | 12.2815 | 12.1852 | 12.115 | 12.4152 | 11.7312 | 12.4006 | 12.0108 | 11.8112 | NaN | NaN | NaN | 12.789 | 92.3865 | NaN | NaN | NaN | -14.3359 | NaN | 64.4763 | NaN | NaN | 555.626 | NaN | 29.7982 | NaN | 28.138
816.1292 | 12.2471 | 12.184 | 12.1174 | 12.3694 | 11.683 | 12.3958 | 12.0287 | 11.814 | NaN | NaN | NaN | 12.7833 | 90.7137 | NaN | NaN | NaN | -2.7082 | NaN | 62.4387 | NaN | NaN | 552.8507 | NaN | 28.3832 | NaN | 28.6985
817.1292 | 12.3184 | 12.2947 | 12.1142 | 12.3571 | 11.7492 | 12.4671 | 12.0529 | 11.8094 | NaN | NaN | NaN | 12.7674 | 91.6792 | NaN | NaN | NaN | -17.402 | NaN | 63.1942 | NaN | NaN | 551.5579 | NaN | 29.0426 | NaN | 27.0651
818.1292 | 12.3889 | 12.5152 | 12.1141 | 12.6929 | 11.689 | 12.7603 | 12.1051 | 11.8093 | NaN | NaN | NaN | 12.7633 | 91.7617 | NaN | NaN | NaN | -1.9483 | NaN | 64.6754 | NaN | NaN | 553.3751 | NaN | 28.6882 | NaN | 28.7751
819.1292 | 12.2203 | 12.1019 | 12.1154 | 12.3869 | 11.69 | 12.3874 | 11.9797 | 11.8073 | NaN | NaN | NaN | 12.744 | 91.9028 | NaN | NaN | NaN | 15.517 | NaN | 64.8494 | NaN | NaN | 552.016 | NaN | 28.483 | NaN | 24.292
820.1292 | 12.3471 | 12.1776 | 12.1282 | 12.4515 | 11.7038 | 12.4916 | 12.0237 | 11.8098 | NaN | NaN | NaN | 12.7509 | 91.0339 | NaN | NaN | NaN | 17.929 | NaN | 64.9577 | NaN | NaN | 553.8101 | NaN | 29.0164 | NaN | 28.8961
821.1292 | 12.2336 | 12.3788 | 12.1239 | 12.4036 | 11.7633 | 12.6107 | 12.0834 | 11.8096 | NaN | NaN | NaN | 12.7371 | 93.132 | NaN | NaN | NaN | 9.7719 | NaN | 62.8791 | NaN | NaN | 552.7355 | NaN | 29.7068 | NaN | 29.0168
822.1292 | 12.4207 | 12.2331 | 12.1306 | 12.4294 | 11.5969 | 12.389 | 12.0596 | 11.8161 | NaN | NaN | NaN | 12.7271 | 93.146 | NaN | NaN | NaN | -14.6689 | NaN | 63.4137 | NaN | NaN | 553.7739 | NaN | 29.8851 | NaN | 28.6987
823.1292 | 12.2581 | 12.1832 | 12.132 | 12.3678 | 11.7009 | 12.4169 | 12.0295 | 11.8074 | NaN | NaN | NaN | 12.7277 | 91.6906 | NaN | NaN | NaN | -18.2393 | NaN | 63.4334 | NaN | NaN | 553.5552 | NaN | 28.729 | NaN | 28.849
824.1292 | 12.3226 | 12.1978 | 12.1349 | 12.3917 | 11.7402 | 12.4003 | 12.0443 | 11.8104 | NaN | NaN | NaN | 12.7164 | 93.2758 | NaN | NaN | NaN | -18.2094 | NaN | 64.9947 | NaN | NaN | 555.9622 | NaN | 28.8242 | NaN | 29.3227
825.1292 | 12.3116 | 12.146 | 12.1316 | 12.3814 | 11.8411 | 12.3776 | 12.0288 | 11.8137 | NaN | NaN | NaN | 12.7089 | 93.7636 | NaN | NaN | NaN | -10.3676 | NaN | 63.6366 | NaN | NaN | 555.0856 | NaN | 29.6612 | NaN | 28.5414
826.1292 | 12.2562 | 12.0734 | 12.1356 | 12.5068 | 11.7735 | 12.3847 | 12.0218 | 11.8155 | NaN | NaN | NaN | 12.7074 | 92.916 | NaN | NaN | NaN | -12.1041 | NaN | 63.9226 | NaN | NaN | 553.86 | NaN | 29.4969 | NaN | 29.4624
827.1292 | 12.2358 | 12.839 | 12.14 | 12.3898 | 11.7777 | 12.8358 | 12.2754 | 11.8099 | NaN | NaN | NaN | 12.7219 | 94.6402 | NaN | NaN | NaN | -9.2609 | NaN | 65.171 | NaN | NaN | 553.8125 | NaN | 29.2074 | NaN | 28.5502
828.1292 | 12.2895 | 12.3519 | 12.1397 | 12.3709 | 11.7848 | 12.6561 | 12.1278 | 11.8182 | NaN | NaN | NaN | 12.707 | 91.433 | NaN | NaN | NaN | -8.8566 | NaN | 63.6897 | NaN | NaN | 552.4368 | NaN | 28.3421 | NaN | 28.444
829.1292 | 12.237 | 12.1684 | 12.1378 | 12.4282 | 11.7008 | 12.3697 | 12.0443 | 11.8175 | NaN | NaN | NaN | 12.7118 | 91.8193 | NaN | NaN | NaN | -17.0047 | NaN | 64.271 | NaN | NaN | 550.4443 | NaN | 30.3488 | NaN | 28.5243
830.1292 | 12.2318 | 12.2269 | 12.1443 | 12.4003 | 11.7273 | 12.5199 | 12.0663 | 11.8259 | NaN | NaN | NaN | 12.7047 | 91.7699 | NaN | NaN | NaN | -16.2536 | NaN | 64.3493 | NaN | NaN | 551.8294 | NaN | 30.8906 | NaN | 28.9247
831.1292 | 12.587 | 12.1125 | 12.1446 | 12.7124 | 11.748 | 12.405 | 12.038 | 11.8275 | NaN | NaN | NaN | 12.7024 | 89.7937 | NaN | NaN | NaN | -12.7217 | NaN | 63.9428 | NaN | NaN | 549.0551 | NaN | 30.1023 | NaN | 28.6061
832.1292 | 12.3924 | 12.4404 | 12.1386 | 12.4201 | 11.7409 | 12.4273 | 12.0976 | 11.8228 | NaN | NaN | NaN | 12.6911 | 93.7984 | NaN | NaN | NaN | -17.5388 | NaN | 64.6711 | NaN | NaN | 549.2365 | NaN | 28.9577 | NaN | 28.7376
833.1292 | 12.2469 | 12.2845 | 12.1405 | 12.4149 | 11.8396 | 12.4288 | 12.0731 | 11.8274 | NaN | NaN | NaN | 12.6907 | 92.4024 | NaN | NaN | NaN | -6.3456 | NaN | 63.941 | NaN | NaN | 551.8156 | NaN | 29.3296 | NaN | 28.1344
834.1292 | 12.3163 | 12.0874 | 12.1468 | 12.4088 | 11.6675 | 12.3498 | 12.033 | 11.8301 | NaN | NaN | NaN | 12.6805 | 91.4939 | NaN | NaN | NaN | 5.8346 | NaN | 63.7798 | NaN | NaN | 549.4505 | NaN | 30.3809 | NaN | 28.8101
835.1292 | 12.2107 | 12.1654 | 12.1448 | 12.418 | 11.7104 | 12.4048 | 12.0563 | 11.8273 | NaN | NaN | NaN | 12.6703 | 92.7196 | NaN | NaN | NaN | NaN | NaN | 62.6212 | NaN | NaN | 551.103 | NaN | 30.5143 | NaN | 28.7943
836.1292 | 12.2836 | 12.1972 | 12.1432 | 12.6337 | 11.6362 | 12.4464 | 12.0903 | 11.8348 | NaN | NaN | NaN | 12.6764 | 91.8525 | NaN | NaN | NaN | -7.1201 | NaN | 65.2904 | NaN | NaN | 552.0598 | NaN | 28.7732 | NaN | 28.5524
837.1292 | 12.2431 | 12.2225 | 12.1487 | 12.4079 | 11.6766 | 12.3818 | 12.0419 | 11.8349 | NaN | NaN | NaN | 12.6676 | 91.4422 | NaN | NaN | NaN | -15.3756 | NaN | 63.9929 | NaN | NaN | 551.9799 | NaN | 32.2118 | NaN | 29.5765
838.1292 | 12.2824 | 12.314 | 12.1477 | 12.3708 | 11.7799 | 12.5352 | 12.1268 | 11.8369 | NaN | NaN | NaN | 12.663 | 92.1385 | NaN | NaN | NaN | -11.8595 | NaN | 64.0881 | NaN | NaN | 551.5273 | NaN | 29.1903 | NaN | 28.6136
839.1292 | 12.3988 | 12.1541 | 12.1569 | 12.4912 | 11.6869 | 12.4044 | 12.0789 | 11.8385 | NaN | NaN | NaN | 12.6615 | 91.0862 | NaN | NaN | NaN | -11.7289 | NaN | 66.0441 | NaN | NaN | 551.6953 | NaN | 29.4377 | NaN | 28.2573
840.1292 | 12.3385 | 12.0635 | 12.1532 | 12.3753 | 11.7531 | 12.3197 | 12.021 | 11.8405 | NaN | NaN | NaN | 12.6585 | 91.6011 | NaN | NaN | NaN | -4.9561 | NaN | 62.8291 | NaN | NaN | 550.3229 | NaN | 30.607 | NaN | 29.5162
841.1292 | 12.2629 | 12.4217 | 12.1621 | 12.3961 | 11.711 | 12.589 | 12.1996 | 11.8432 | NaN | NaN | NaN | 12.6549 | 92.2352 | NaN | NaN | NaN | -7.5015 | NaN | 64.8014 | NaN | NaN | 552.2713 | NaN | 28.9903 | NaN | 28.9805
842.1292 | 12.3688 | 12.3148 | 12.1594 | 12.3465 | 11.7338 | 12.5612 | 12.1112 | 11.8427 | NaN | NaN | NaN | 12.6513 | 91.8783 | NaN | NaN | NaN | -10.1304 | NaN | 65.8558 | NaN | NaN | 551.6003 | NaN | 30.4446 | NaN | 26.8159
843.1292 | 12.2719 | 12.1499 | 12.1579 | 12.4423 | 11.6715 | 12.3658 | 12.0547 | 11.8434 | NaN | NaN | NaN | 12.6463 | 92.0816 | NaN | NaN | NaN | -18.7461 | NaN | 63.5692 | NaN | NaN | 548.9051 | NaN | 31.208 | NaN | 29.3402
844.1292 | 12.4273 | 12.2014 | 12.1544 | 12.4354 | 11.7436 | 12.4505 | 12.0845 | 11.8453 | NaN | NaN | NaN | 12.6468 | 92.6716 | NaN | NaN | NaN | -13.7034 | NaN | 63.434 | NaN | NaN | 550.5247 | NaN | 30.2485 | NaN | 28.2124
845.1292 | 12.3577 | 12.1166 | 12.1649 | 12.4191 | 11.7728 | 12.3262 | 12.0395 | 11.8428 | NaN | NaN | NaN | 12.6557 | 91.5894 | NaN | NaN | NaN | -13.8698 | NaN | 63.9139 | NaN | NaN | 550.2202 | NaN | 30.3873 | NaN | 27.616
846.1292 | 12.2849 | 12.2206 | 12.1645 | 12.4038 | 11.6649 | 12.4652 | 12.0686 | 11.8559 | NaN | NaN | NaN | 12.6593 | 92.3735 | NaN | NaN | NaN | -11.4642 | NaN | 65.4543 | NaN | NaN | 548.9797 | NaN | 31.89 | NaN | 28.4877
847.1292 | 12.3151 | 12.1303 | 12.1653 | 12.4418 | 11.7581 | 12.3734 | 12.0675 | 11.8412 | NaN | NaN | NaN | 12.6716 | 93.153 | NaN | NaN | NaN | -15.8015 | NaN | 64.078 | NaN | NaN | 550.6176 | NaN | 28.8155 | NaN | 29.039
848.1292 | 12.2515 | 12.2447 | 12.17 | 12.4251 | 11.7146 | 12.5256 | 12.0939 | 11.8449 | NaN | NaN | NaN | 12.6808 | 92.9437 | NaN | NaN | NaN | 3.1177 | NaN | 65.288 | NaN | NaN | 548.0615 | NaN | 29.4638 | NaN | 27.6474
849.1292 | 12.4368 | 12.1833 | 12.1713 | 12.5008 | 11.7243 | 12.4078 | 12.0852 | 11.8489 | NaN | NaN | NaN | 12.679 | 90.9688 | NaN | NaN | NaN | 27.7464 | NaN | 63.2361 | NaN | NaN | 546.4932 | NaN | 30.2857 | NaN | 28.5587
850.1292 | 12.3527 | 12.1346 | 12.1739 | 12.365 | 11.8152 | 12.3581 | 12.0549 | 11.8498 | NaN | NaN | NaN | 12.6835 | 92.6214 | NaN | NaN | NaN | -2.5378 | NaN | 64.5111 | NaN | NaN | 549.0176 | NaN | 29.6664 | NaN | 27.5624
851.1292 | 12.2529 | 12.3819 | 12.169 | 12.4944 | 11.7809 | 12.5668 | 12.1483 | 11.8609 | NaN | NaN | NaN | 12.6855 | 91.6699 | NaN | NaN | NaN | 10.6203 | NaN | 65.2051 | NaN | NaN | 549.4168 | NaN | 30.5864 | NaN | 28.5929
852.1292 | 12.324 | 12.0946 | 12.1744 | 12.4982 | 11.6677 | 12.2825 | 12.0461 | 11.8592 | NaN | NaN | NaN | 12.6661 | 91.66 | NaN | NaN | NaN | 18.9691 | NaN | 63.8204 | NaN | NaN | 545.7891 | NaN | 30.6571 | NaN | 28.3153
853.1292 | 12.3959 | 12.4929 | 12.1729 | 12.428 | 11.7175 | 12.432 | 12.13 | 11.8598 | NaN | NaN | NaN | 12.6751 | 92.0949 | NaN | NaN | NaN | -8.8889 | NaN | 64.2834 | NaN | NaN | 546.1165 | NaN | 31.1471 | NaN | 27.5956
854.1292 | 12.4427 | 12.3559 | 12.1745 | 12.4253 | 11.7289 | 12.5535 | 12.1245 | 11.8629 | NaN | NaN | NaN | 12.6627 | 92.0701 | NaN | NaN | NaN | -14.8563 | NaN | 63.4236 | NaN | NaN | 546.9132 | NaN | 28.3923 | NaN | 28.7964
855.1292 | 12.3094 | 12.2814 | 12.1818 | 12.4116 | 11.8004 | 12.5424 | 12.064 | 11.8615 | NaN | NaN | NaN | 12.6635 | 91.9579 | NaN | NaN | NaN | -7.814 | NaN | 64.8353 | NaN | NaN | 547.8204 | NaN | 29.8852 | NaN | 28.8741
856.1292 | 12.4169 | 12.2245 | 12.1798 | 12.4384 | 11.7819 | 12.3888 | 12.0632 | 11.8664 | NaN | NaN | NaN | 12.6593 | 91.469 | NaN | NaN | NaN | -6.7794 | NaN | 62.3389 | NaN | NaN | 547.2547 | NaN | 28.8225 | NaN | 28.7952
857.1292 | 12.5906 | 12.1751 | 12.1877 | 12.5265 | 11.6877 | 12.416 | 12.0489 | 11.8672 | NaN | NaN | NaN | 12.6422 | 92.2341 | NaN | NaN | NaN | -18.0306 | NaN | 64.4574 | NaN | NaN | 547.756 | NaN | 28.373 | NaN | 28.286
858.1292 | 12.5487 | 12.3989 | 12.1868 | 12.3915 | 11.8157 | 12.5223 | 12.1394 | 11.8651 | NaN | NaN | NaN | 12.6468 | 92.0455 | NaN | NaN | NaN | 19.8756 | NaN | 63.6266 | NaN | NaN | 544.7786 | NaN | 30.6269 | NaN | 28.4761
859.1292 | 12.3303 | 12.3893 | 12.1876 | 12.4315 | 11.6499 | 12.5602 | 12.0873 | 11.8745 | NaN | NaN | NaN | 12.6469 | 92.2035 | NaN | NaN | NaN | 33.8151 | NaN | 65.1443 | NaN | NaN | 545.8425 | NaN | 30.9112 | NaN | 28.6358
860.1292 | 12.2831 | 12.5693 | 12.1918 | 12.4433 | 11.6629 | 12.6989 | 12.1473 | 11.8746 | NaN | NaN | NaN | 12.6551 | 91.8148 | NaN | NaN | NaN | -5.6218 | NaN | 64.1726 | NaN | NaN | 545.2173 | NaN | 30.2457 | NaN | 28.9454
861.1292 | 12.3204 | 12.2075 | 12.1936 | 12.4761 | 11.7996 | 12.4231 | 12.0798 | 11.8719 | NaN | NaN | NaN | 12.6433 | 91.9872 | NaN | NaN | NaN | -6.4125 | NaN | 64.8367 | NaN | NaN | 544.159 | NaN | 31.2602 | NaN | 27.7981
862.1292 | 12.3227 | 12.2227 | 12.1885 | 12.4581 | 11.8393 | 12.6133 | 12.0797 | 11.8816 | NaN | NaN | NaN | 12.6372 | 91.5484 | NaN | NaN | NaN | -15.4761 | NaN | 64.5828 | NaN | NaN | 545.3135 | NaN | 29.6479 | NaN | 28.5585
863.1292 | 12.303 | 12.1951 | 12.1924 | 12.6121 | 11.7936 | 12.4215 | 12.0736 | 11.8769 | NaN | NaN | NaN | 12.6259 | 91.8671 | NaN | NaN | NaN | -10.7289 | NaN | 64.4943 | NaN | NaN | 545.2483 | NaN | 30.8014 | NaN | 27.5128
864.1292 | 12.3696 | 12.3449 | 12.1852 | 12.4457 | 11.8444 | 12.4267 | 12.1476 | 11.8854 | NaN | NaN | NaN | 12.6332 | 92.5955 | NaN | NaN | NaN | -12.5494 | NaN | 62.9316 | NaN | NaN | 545.2325 | NaN | 30.4641 | NaN | 28.8904
865.1292 | 12.3424 | 12.2085 | 12.1922 | 12.6708 | 11.7574 | 12.5867 | 12.087 | 11.8784 | NaN | NaN | NaN | 12.6307 | 91.4338 | NaN | NaN | NaN | 3.2521 | NaN | 63.5322 | NaN | NaN | 546.0746 | NaN | 30.2494 | NaN | 28.6991
866.1292 | 12.3209 | 12.1552 | 12.1909 | 12.5366 | 11.8138 | 12.5353 | 12.0994 | 11.8835 | NaN | NaN | NaN | 12.6249 | 92.9909 | NaN | NaN | NaN | 41.3598 | NaN | 63.7477 | NaN | NaN | 548.0981 | NaN | 28.1572 | NaN | 28.9457
867.1292 | 12.3405 | 12.2764 | 12.1933 | 12.4942 | 11.7764 | 12.5282 | 12.1261 | 11.8862 | NaN | NaN | NaN | 12.6199 | 93.1538 | NaN | NaN | NaN | -8.1279 | NaN | 64.0186 | NaN | NaN | 549.0108 | NaN | 31.132 | NaN | 28.7061
868.1292 | 12.3743 | 12.1743 | 12.1923 | 12.4462 | 11.8525 | 12.3937 | 12.07 | 11.8854 | NaN | NaN | NaN | 12.627 | 91.2032 | NaN | NaN | NaN | 19.998 | NaN | 62.9305 | NaN | NaN | 548.3479 | NaN | 30.0391 | NaN | 28.7094
869.1292 | 12.3318 | 12.1697 | 12.1935 | 12.7532 | 11.7214 | 12.3615 | 12.0597 | 11.8847 | NaN | NaN | NaN | 12.6194 | 91.7458 | NaN | NaN | NaN | 26.3475 | NaN | 62.7322 | NaN | NaN | 546.7667 | NaN | 27.9684 | NaN | 28.2771
870.1292 | 12.3111 | 12.2263 | 12.1971 | 12.4636 | 11.7725 | 12.399 | 12.0836 | 11.888 | NaN | NaN | NaN | 12.6174 | 92.4252 | NaN | NaN | NaN | -3.3551 | NaN | 64.3668 | NaN | NaN | 548.5316 | NaN | 27.2423 | NaN | 28.2192
871.1292 | 12.4783 | 12.3639 | 12.1996 | 12.4962 | 11.829 | 12.591 | 12.1382 | 11.8908 | NaN | NaN | NaN | 12.6188 | 92.7744 | NaN | NaN | NaN | -12.5138 | NaN | 63.2817 | NaN | NaN | 550.9531 | NaN | 28.7901 | NaN | 28.8213
872.1292 | 12.2886 | 12.3113 | 12.1999 | 12.4392 | 11.8278 | 12.4566 | 12.1007 | 11.8922 | NaN | NaN | NaN | 12.6147 | 92.0473 | NaN | NaN | NaN | -5.1822 | NaN | 63.4835 | NaN | NaN | 553.0693 | NaN | 28.5817 | NaN | 28.9016
873.1448 | 12.5098 | 12.2362 | 12.208 | 12.4795 | 11.7693 | 12.4855 | 12.0981 | 11.8903 | NaN | NaN | NaN | 12.6155 | 91.6266 | NaN | NaN | NaN | -9.3312 | NaN | 63.5922 | NaN | NaN | 552.4993 | NaN | 29.5474 | NaN | 28.9369
874.1292 | 12.3769 | 12.6208 | 12.2076 | 12.595 | 11.634 | 12.9264 | 12.2179 | 11.8959 | NaN | NaN | NaN | 12.6198 | 89.6665 | NaN | NaN | NaN | -8.8334 | NaN | 64.808 | NaN | NaN | 555.1368 | NaN | 30.8775 | NaN | 28.328
875.1292 | 12.3935 | 12.3745 | 12.2076 | 12.5574 | 11.9447 | 12.5126 | 12.1144 | 11.8933 | NaN | NaN | NaN | 12.6123 | 91.9352 | NaN | NaN | NaN | 9.6564 | NaN | 62.2727 | NaN | NaN | 555.3483 | NaN | 31.124 | NaN | 28.9012
876.1292 | 12.5949 | 12.1812 | 12.2148 | 12.6168 | 11.8385 | 12.448 | 12.0999 | 11.8995 | NaN | NaN | NaN | 12.6139 | 94.0187 | NaN | NaN | NaN | -6.6925 | NaN | 64.2789 | NaN | NaN | 558.2542 | NaN | 31.2111 | NaN | 28.345
877.1292 | 12.3816 | 12.4521 | 12.2194 | 12.5133 | 11.8042 | 12.5955 | 12.1601 | 11.9001 | NaN | NaN | NaN | 12.6102 | 90.7448 | NaN | NaN | NaN | -6.6313 | NaN | 64.834 | NaN | NaN | 556.7621 | NaN | 28.7123 | NaN | 28.7081
878.1292 | 12.3213 | 12.6318 | 12.2145 | 12.4221 | 11.8257 | 12.5149 | 12.1778 | 11.9004 | NaN | NaN | NaN | 12.6091 | 91.4169 | NaN | NaN | NaN | -17.5366 | NaN | 66.8315 | NaN | NaN | 560.4206 | NaN | 28.3182 | NaN | 29.408
879.1292 | 12.4279 | 12.3898 | 12.2151 | 12.5071 | 11.8388 | 12.4991 | 12.1302 | 11.8994 | NaN | NaN | NaN | 12.6102 | 91.293 | NaN | NaN | NaN | -9.6278 | NaN | 63.4447 | NaN | NaN | 560.3844 | NaN | 30.0366 | NaN | 28.9289
880.1292 | 12.5432 | 12.25 | 12.2123 | 12.4945 | 11.8054 | 12.4433 | 12.135 | 11.903 | NaN | NaN | NaN | 12.6145 | 90.7616 | NaN | NaN | NaN | 11.9685 | NaN | 64.6699 | NaN | NaN | 562.0729 | NaN | 28.4067 | NaN | 28.8929
881.1292 | 12.3227 | 12.3116 | 12.2051 | 12.5876 | 11.7407 | 12.5994 | 12.1515 | 11.9054 | NaN | NaN | NaN | 12.6069 | 92.3658 | NaN | NaN | NaN | -10.395 | NaN | 62.9056 | NaN | NaN | 563.665 | NaN | 28.2322 | NaN | 28.2491
882.1448 | 12.4947 | 12.3512 | 12.212 | 12.5212 | 11.7946 | 12.4979 | 12.1574 | 11.9056 | NaN | NaN | NaN | 12.6257 | 93.3974 | NaN | NaN | NaN | -17.8401 | NaN | 63.7301 | NaN | NaN | 564.7018 | NaN | 29.8287 | NaN | 29.6205
883.1292 | 12.3451 | 12.3943 | 12.2093 | 12.4883 | 11.8789 | 12.6265 | 12.193 | 11.9065 | NaN | NaN | NaN | 12.6144 | 91.218 | NaN | NaN | NaN | -10.089 | NaN | 64.0281 | NaN | NaN | 565.2833 | NaN | 29.8623 | NaN | 28.1607
884.1292 | 12.3369 | 12.1683 | 12.209 | 12.5154 | 11.9026 | 12.4279 | 12.085 | 11.9074 | NaN | NaN | NaN | 12.6342 | 91.5648 | NaN | NaN | NaN | 29.5984 | NaN | 63.5399 | NaN | NaN | 567.3735 | NaN | 29.7912 | NaN | 28.183
885.1292 | 12.3494 | 12.3333 | 12.2173 | 12.4816 | 11.7736 | 12.4889 | 12.109 | 11.9106 | NaN | NaN | NaN | 12.6264 | 92.8672 | NaN | NaN | NaN | 23.3504 | NaN | 64.0368 | NaN | NaN | 568.3594 | NaN | 31.4867 | NaN | 28.9315
886.1292 | 12.4111 | 12.2633 | 12.2205 | 12.4627 | 11.9072 | 12.442 | 12.1113 | 11.9069 | NaN | NaN | NaN | 12.6437 | 92.0281 | NaN | NaN | NaN | -5.5719 | NaN | 63.0099 | NaN | NaN | 569.9737 | NaN | 27.5445 | NaN | 28.4615
887.1292 | 12.4465 | 12.3547 | 12.2141 | 12.4954 | 11.8509 | 12.5974 | 12.1548 | 11.9098 | NaN | NaN | NaN | 12.6638 | 91.7719 | NaN | NaN | NaN | 3.0596 | NaN | 63.7833 | NaN | NaN | 569.0205 | NaN | 28.931 | NaN | 27.8038
888.1292 | 12.3313 | 12.152 | 12.2326 | 12.4812 | 11.792 | 12.3712 | 12.079 | 11.9094 | NaN | NaN | NaN | 12.7097 | 91.7989 | NaN | NaN | NaN | 17.7184 | NaN | 64.2394 | NaN | NaN | 568.0411 | NaN | 28.8555 | NaN | 28.4299
889.1292 | 12.3494 | 12.2746 | 12.2237 | 12.4688 | 11.8646 | 12.5001 | 12.1296 | 11.9157 | NaN | NaN | NaN | 12.7267 | 92.8265 | NaN | NaN | NaN | -6.9002 | NaN | 61.9595 | NaN | NaN | 569.6111 | NaN | 30.4862 | NaN | 27.9923
890.1292 | 12.3898 | 12.1956 | 12.2264 | 12.4788 | 11.8562 | 12.4008 | 12.0985 | 11.9185 | NaN | NaN | NaN | 12.7546 | 91.3533 | NaN | NaN | NaN | -2.2373 | NaN | 62.728 | NaN | NaN | 567.4833 | NaN | 29.7419 | NaN | 27.8724
891.1292 | 12.3443 | 12.4279 | 12.2348 | 12.8138 | 11.8151 | 12.6086 | 12.1326 | 11.9122 | NaN | NaN | NaN | 12.764 | 91.0869 | NaN | NaN | NaN | 2.3184 | NaN | 63.1369 | NaN | NaN | 568.4131 | NaN | 30.5297 | NaN | 28.4684
892.1292 | 12.3641 | 12.217 | 12.2361 | 12.5202 | 11.8999 | 12.4478 | 12.1152 | 11.9153 | NaN | NaN | NaN | 12.7674 | 92.1379 | NaN | NaN | NaN | 8.2346 | NaN | 62.36 | NaN | NaN | 570.4056 | NaN | 30.6193 | NaN | 27.9527
893.1292 | 12.3265 | 12.1706 | 12.2311 | 12.4743 | 11.7839 | 12.428 | 12.095 | 11.9197 | NaN | NaN | NaN | 12.7789 | 91.7941 | NaN | NaN | NaN | -19.0862 | NaN | 63.9092 | NaN | NaN | 573.1637 | NaN | 29.6714 | NaN | 28.1563
894.1292 | 12.3378 | 12.1955 | 12.2377 | 12.5359 | 11.8497 | 12.4463 | 12.1192 | 11.9184 | NaN | NaN | NaN | 12.7895 | 92.2538 | NaN | NaN | NaN | 3.2578 | NaN | 64.606 | NaN | NaN | 570.9168 | NaN | 26.6857 | NaN | 28.4544
895.1292 | 12.407 | 12.4014 | 12.2434 | 12.4994 | 11.6957 | 12.5114 | 12.1726 | 11.9203 | NaN | NaN | NaN | 12.7917 | 91.8689 | NaN | NaN | NaN | -19.703 | NaN | 65.2241 | NaN | NaN | 571.2681 | NaN | 27.5115 | NaN | 28.2826
896.1292 | 12.3442 | 12.3629 | 12.2488 | 12.517 | 11.8293 | 12.5209 | 12.1358 | 11.9238 | NaN | NaN | NaN | 12.8031 | 93.378 | NaN | NaN | NaN | -1.0763 | NaN | 61.486 | NaN | NaN | 570.2626 | NaN | 29.0481 | NaN | 28.5064
897.1292 | 12.3372 | 12.3313 | 12.2446 | 12.5359 | 11.8473 | 12.5716 | 12.166 | 11.9213 | NaN | NaN | NaN | 12.8098 | 92.6271 | NaN | NaN | NaN | 4.9016 | NaN | 64.4679 | NaN | NaN | 571.3049 | NaN | 27.2643 | NaN | 28.434
898.1292 | 12.6564 | 12.389 | 12.2503 | 12.4937 | 11.8172 | 12.5823 | 12.1872 | 11.925 | NaN | NaN | NaN | 12.806 | 96.6862 | NaN | NaN | NaN | -11.9056 | NaN | 64.2745 | NaN | NaN | 571.46 | NaN | 27.573 | NaN | 28.0431
899.1292 | 12.5818 | 12.4916 | 12.2492 | 12.541 | 11.8192 | 12.7129 | 12.2123 | 11.9196 | NaN | NaN | NaN | 12.8091 | 92.126 | NaN | NaN | NaN | -10.542 | NaN | 62.9689 | NaN | NaN | 570.7476 | NaN | 27.1511 | NaN | 28.5091
900.1292 | 12.3581 | 12.5712 | 12.2627 | 12.5478 | 11.8866 | 12.7589 | 12.1962 | 11.926 | NaN | NaN | NaN | 12.8012 | 92.7881 | NaN | NaN | NaN | -18.6149 | NaN | 63.0655 | NaN | NaN | 571.4118 | NaN | 27.4627 | NaN | 28.5352
901.1292 | 12.6412 | 12.3054 | 12.2531 | 12.5811 | 11.8297 | 12.5419 | 12.1563 | 11.9233 | NaN | NaN | NaN | 12.8006 | 92.0687 | NaN | NaN | NaN | -9.0201 | NaN | 63.135 | NaN | NaN | 569.2345 | NaN | 28.9492 | NaN | 27.5407
902.1292 | 12.4039 | 12.2773 | 12.2541 | 12.5526 | 11.8021 | 12.5298 | 12.159 | 11.9233 | NaN | NaN | NaN | 12.8059 | 92.26 | NaN | NaN | NaN | -16.947 | NaN | 65.1986 | NaN | NaN | 572.3824 | NaN | 27.8864 | NaN | 28.1521
903.1292 | 12.4228 | 12.2581 | 12.2611 | 12.5073 | 11.7337 | 12.4881 | 12.1481 | 11.9256 | NaN | NaN | NaN | 12.8051 | 92.0625 | NaN | NaN | NaN | 15.9365 | NaN | 62.8963 | NaN | NaN | 572.0265 | NaN | 30.3133 | NaN | 28.195
904.1292 | 12.5052 | 12.3585 | 12.2594 | 12.5367 | 11.903 | 12.5559 | 12.1629 | 11.9237 | NaN | NaN | NaN | 12.8025 | 93.3007 | NaN | NaN | NaN | 4.1364 | NaN | 62.3906 | NaN | NaN | 572.0397 | NaN | 29.2725 | NaN | 28.6664
905.1292 | 12.3991 | 12.7548 | 12.2653 | 12.5282 | 11.8527 | 12.8242 | 12.3549 | 11.9202 | NaN | NaN | NaN | 12.805 | 93.4839 | NaN | NaN | NaN | -16.9954 | NaN | 62.5912 | NaN | NaN | 570.9141 | NaN | 29.2835 | NaN | 28.4845
906.1292 | 12.5092 | 12.4165 | 12.2632 | 12.4818 | 11.9335 | 12.4707 | 12.181 | 11.9239 | NaN | NaN | NaN | 12.8039 | 90.7459 | NaN | NaN | NaN | -16.4306 | NaN | 62.8974 | NaN | NaN | 570.3205 | NaN | 30.4193 | NaN | 27.3193
907.1292 | 12.3687 | 12.3106 | 12.2757 | 12.5155 | 11.8706 | 12.5302 | 12.1558 | 11.9235 | NaN | NaN | NaN | 12.8075 | 96.6236 | NaN | NaN | NaN | 10.2445 | NaN | 64.4232 | NaN | NaN | 569.5327 | NaN | 29.5994 | NaN | 29.1945
908.1292 | 12.4168 | 12.2917 | 12.2685 | 12.5049 | 11.8003 | 12.4986 | 12.1552 | 11.9279 | NaN | NaN | NaN | 12.8122 | 92.3694 | NaN | NaN | NaN | -17.6161 | NaN | 64.0037 | NaN | NaN | 570.0113 | NaN | 31.2428 | NaN | 27.939
909.1292 | 12.4976 | 12.4516 | 12.2671 | 12.5353 | 11.8779 | 12.6349 | 12.204 | 11.9268 | NaN | NaN | NaN | 12.8011 | 92.0722 | NaN | NaN | NaN | -17.7367 | NaN | 63.3772 | NaN | NaN | 571.2326 | NaN | 28.4773 | NaN | 28.3719
910.1292 | 12.3645 | 12.2236 | 12.2729 | 12.5969 | 11.8661 | 12.4501 | 12.1363 | 11.9257 | NaN | NaN | NaN | 12.8599 | 91.7337 | NaN | NaN | NaN | 24.3639 | NaN | 63.7695 | NaN | NaN | 569.435 | NaN | 29.0792 | NaN | 27.0937
911.1292 | 12.7017 | 12.2634 | 12.2729 | 12.5396 | 11.8594 | 12.4899 | 12.1563 | 11.9211 | NaN | NaN | NaN | 12.8193 | 92.7706 | NaN | NaN | NaN | -14.3121 | NaN | 63.7003 | NaN | NaN | 570.1762 | NaN | 27.3995 | NaN | 29.0651
912.1292 | 12.4553 | 12.2335 | 12.2742 | 12.503 | 11.8939 | 12.438 | 12.14 | 11.9308 | NaN | NaN | NaN | 12.7791 | 91.9937 | NaN | NaN | NaN | 7.7588 | NaN | 63.0754 | NaN | NaN | 571.7668 | NaN | 27.1567 | NaN | 28.4811
913.1292 | 12.4012 | 12.308 | 12.2758 | 12.5723 | 11.8677 | 12.4889 | 12.1802 | 11.9262 | NaN | NaN | NaN | 12.8426 | 93.9035 | NaN | NaN | NaN | -3.3121 | NaN | 63.0363 | NaN | NaN | 569.1871 | NaN | 27.6837 | NaN | 27.9134
914.1292 | 12.3962 | 12.4624 | 12.2822 | 12.5458 | 11.9537 | 12.6023 | 12.2076 | 11.9302 | NaN | NaN | NaN | 12.8794 | 92.5775 | NaN | NaN | NaN | -11.9206 | NaN | 62.8558 | NaN | NaN | 571.7713 | NaN | 29.6766 | NaN | 23.3997
915.1292 | 12.6457 | 12.4413 | 12.2709 | 12.7051 | 11.8612 | 12.6272 | 12.1946 | 11.9308 | NaN | NaN | NaN | 12.8535 | 92.1932 | NaN | NaN | NaN | 2.9047 | NaN | 63.1035 | NaN | NaN | 570.8204 | NaN | 27.9221 | NaN | 29.0472
916.1292 | 12.4467 | 12.4336 | 12.2816 | 12.882 | 11.8545 | 12.6227 | 12.2228 | 11.9353 | NaN | NaN | NaN | 12.8146 | 91.9513 | NaN | NaN | NaN | 1.5774 | NaN | 63.8382 | NaN | NaN | 571.91 | NaN | 27.8716 | NaN | 27.8629
917.1292 | 12.7484 | 12.2675 | 12.2807 | 12.5613 | 11.8911 | 12.4619 | 12.1539 | 11.9338 | NaN | NaN | NaN | 12.8424 | 93.7354 | NaN | NaN | NaN | -8.8634 | NaN | 63.785 | NaN | NaN | 569.9845 | NaN | 29.2582 | NaN | 27.1302
918.1292 | 12.7257 | 12.4098 | 12.2874 | 12.521 | 11.9044 | 12.5134 | 12.2152 | 11.9363 | NaN | NaN | NaN | 12.8929 | 93.5231 | NaN | NaN | NaN | -17.673 | NaN | 63.9005 | NaN | NaN | 573.1216 | NaN | 29.2243 | NaN | 27.0969
919.1292 | 12.4202 | 12.2154 | 12.2821 | 12.6271 | 11.9359 | 12.4148 | 12.1347 | 11.9387 | NaN | NaN | NaN | 12.8161 | 92.2178 | NaN | NaN | NaN | 9.716 | NaN | 61.8367 | NaN | NaN | 572.4093 | NaN | 29.8846 | NaN | 29.2076
920.1292 | 12.4564 | 12.5394 | 12.2908 | 12.5754 | 11.8744 | 12.6777 | 12.2286 | 11.9369 | NaN | NaN | NaN | 12.8004 | 93.9917 | NaN | NaN | NaN | 5.0305 | NaN | 63.839 | NaN | NaN | 572.9759 | NaN | 28.2749 | NaN | 27.0123
921.1292 | 12.4514 | 12.608 | 12.2952 | 12.5152 | 11.8502 | 12.5401 | 12.2638 | 11.9384 | NaN | NaN | NaN | 12.8022 | 90.9586 | NaN | NaN | NaN | -1.2592 | NaN | 62.7247 | NaN | NaN | 572.0229 | NaN | 30.0852 | NaN | 29.329
922.1292 | 12.4342 | 12.3388 | 12.2874 | 12.6138 | 11.879 | 12.6008 | 12.183 | 11.9345 | NaN | NaN | NaN | 12.7987 | 92.4827 | NaN | NaN | NaN | -0.6156 | NaN | 63.1417 | NaN | NaN | 571.1859 | NaN | 28.154 | NaN | 28.9442
923.1292 | 12.4138 | 12.3695 | 12.2914 | 12.7046 | 11.9495 | 12.5373 | 12.197 | 11.939 | NaN | NaN | NaN | 12.7867 | 91.0039 | NaN | NaN | NaN | -2.721 | NaN | 63.2332 | NaN | NaN | 570.3003 | NaN | 28.1202 | NaN | 27.3434
924.1292 | 12.4743 | 12.3457 | 12.2917 | 12.5542 | 11.8985 | 12.5276 | 12.1866 | 11.9441 | NaN | NaN | NaN | 12.8362 | 92.6068 | NaN | NaN | NaN | -15.4618 | NaN | 62.2549 | NaN | NaN | 568.7298 | NaN | 30.3639 | NaN | 27.942
925.1292 | 12.4961 | 12.5412 | 12.2969 | 12.7106 | 11.844 | 12.6518 | 12.2648 | 11.9425 | NaN | NaN | NaN | 12.7657 | 92.3398 | NaN | NaN | NaN | -10.3521 | NaN | 62.8621 | NaN | NaN | 568.6173 | NaN | 27.1931 | NaN | 28.4124
926.1292 | 12.4511 | 12.2856 | 12.2972 | 12.5837 | 11.8052 | 12.4822 | 12.179 | 11.9436 | NaN | NaN | NaN | 12.8483 | 91.3283 | NaN | NaN | NaN | 44.0997 | NaN | 65.0888 | NaN | NaN | 571.0135 | NaN | 29.8798 | NaN | 29.5838
927.1292 | 12.412 | 12.4533 | 12.303 | 12.6003 | 11.9179 | 12.6632 | 12.2425 | 11.9498 | NaN | NaN | NaN | 12.9672 | 91.8915 | NaN | NaN | NaN | -11.2987 | NaN | 62.8319 | NaN | NaN | 570.028 | NaN | 29.131 | NaN | 29.6326
928.1292 | 12.3953 | 12.5268 | 12.3087 | 12.5735 | 11.8332 | 12.6312 | 12.2129 | 11.9496 | NaN | NaN | NaN | 12.9302 | 92.116 | NaN | NaN | NaN | -10.5458 | NaN | 62.9766 | NaN | NaN | 565.5307 | NaN | 26.7668 | NaN | 26.9828
929.1292 | 12.4259 | 12.2348 | 12.3013 | 12.6738 | 11.8521 | 12.4339 | 12.1602 | 11.9541 | NaN | NaN | NaN | 12.9496 | 93.5373 | NaN | NaN | NaN | -14.6745 | NaN | 62.7366 | NaN | NaN | 568.4032 | NaN | 27.3988 | NaN | 27.1255
930.1292 | 12.4628 | 12.3984 | 12.3105 | 12.5584 | 11.7939 | 12.5459 | 12.2155 | 11.9571 | NaN | NaN | NaN | 12.9631 | 92.0672 | NaN | NaN | NaN | -2.3519 | NaN | 62.8151 | NaN | NaN | 568.4065 | NaN | 28.8854 | NaN | 28.1941
931.1292 | 12.51 | 12.2781 | 12.3093 | 12.6987 | 11.9059 | 12.4972 | 12.1806 | 11.9519 | NaN | NaN | NaN | 12.9051 | 91.7306 | NaN | NaN | NaN | -14.7662 | NaN | 62.8789 | NaN | NaN | 567.0322 | NaN | 30.7108 | NaN | 28.4141
932.1292 | 12.4239 | 12.2782 | 12.3098 | 12.7523 | 11.9625 | 12.4273 | 12.1663 | 11.9652 | NaN | NaN | NaN | 12.8965 | 92.3495 | NaN | NaN | NaN | -9.8885 | NaN | 63.1106 | NaN | NaN | 567.7324 | NaN | 28.1332 | NaN | 28.681
933.1292 | 12.4379 | 12.5431 | 12.316 | 12.5529 | 11.9758 | 12.6492 | 12.2562 | 11.9609 | NaN | NaN | NaN | 12.8673 | 91.6965 | NaN | NaN | NaN | -17.4277 | NaN | 62.4285 | NaN | NaN | 570.0747 | NaN | 30.2505 | NaN | 27.9524
934.1292 | 12.5331 | 12.5226 | 12.3227 | 12.5863 | 11.8653 | 12.6249 | 12.2264 | 11.9642 | NaN | NaN | NaN | 12.922 | 93.4002 | NaN | NaN | NaN | -19.4636 | NaN | 62.4854 | NaN | NaN | 570.9362 | NaN | 26.9497 | NaN | 28.0653
935.1292 | 12.6561 | 12.3136 | 12.3209 | 12.5857 | 11.8625 | 12.5758 | 12.2067 | 11.9656 | NaN | NaN | NaN | 12.8727 | 92.7679 | NaN | NaN | NaN | -13.4607 | NaN | 63.8563 | NaN | NaN | 572.4554 | NaN | 27.3227 | NaN | 27.7078
936.1292 | 12.4685 | 12.6717 | 12.3265 | 12.5613 | 11.9496 | 12.8564 | 12.3106 | 11.9712 | NaN | NaN | NaN | 12.8786 | 92.9337 | NaN | NaN | NaN | -0.3495 | NaN | 65.484 | NaN | NaN | 573.5576 | NaN | 29.0459 | NaN | 26.9644
937.1292 | 12.6888 | 12.436 | 12.3264 | 12.5399 | 12.0385 | 12.61 | 12.2256 | 11.9785 | NaN | NaN | NaN | 12.9517 | 91.6175 | NaN | NaN | NaN | -7.9075 | NaN | 63.7523 | NaN | NaN | 571.683 | NaN | 28.6143 | NaN | 27.4175
938.1292 | 12.5192 | 12.8808 | 12.3309 | 12.7861 | 11.918 | 12.7868 | 12.2931 | 11.9766 | NaN | NaN | NaN | 12.8854 | 92.3991 | NaN | NaN | NaN | -17.3889 | NaN | 63.9649 | NaN | NaN | 574.8194 | NaN | 29.0722 | NaN | 26.9612
939.1292 | 12.4602 | 12.3355 | 12.3292 | 12.5382 | 11.9129 | 12.5443 | 12.1976 | 11.9808 | NaN | NaN | NaN | 12.908 | 93.3778 | NaN | NaN | NaN | 2.4505 | NaN | 63.5525 | NaN | NaN | 576.1768 | NaN | 28.7487 | NaN | 29.3329
940.1292 | 12.4172 | 12.3287 | 12.3346 | 12.7926 | 11.9028 | 12.5576 | 12.204 | 11.9824 | NaN | NaN | NaN | 12.8805 | 91.5187 | NaN | NaN | NaN | 7.9199 | NaN | 63.5412 | NaN | NaN | 576.1683 | NaN | 28.6481 | NaN | 20.0424
941.1292 | 12.4614 | 12.4614 | 12.3342 | 12.6584 | 11.8016 | 12.6314 | 12.2334 | 11.9865 | NaN | NaN | NaN | 12.8577 | 91.3946 | NaN | NaN | NaN | -11.4018 | NaN | 65.7672 | NaN | NaN | 577.1967 | NaN | 27.9064 | NaN | 27.7745
942.1292 | 12.5633 | 12.5967 | 12.3402 | 12.7949 | 11.8847 | 12.7219 | 12.2551 | 11.9935 | NaN | NaN | NaN | 12.8579 | 91.4827 | NaN | NaN | NaN | -15.3007 | NaN | 65.6713 | NaN | NaN | 578.1491 | NaN | 28.97 | NaN | 27.6557
943.1292 | 12.64 | 12.4141 | 12.3422 | 12.6493 | 11.8941 | 12.6211 | 12.23 | 11.9917 | NaN | NaN | NaN | 12.8645 | 93.0036 | NaN | NaN | NaN | 20.7976 | NaN | 63.6217 | NaN | NaN | 576.5883 | NaN | 27.1785 | NaN | 28.1498
944.1292 | 12.4745 | 12.3412 | 12.3466 | 12.5763 | 11.8694 | 12.5157 | 12.1885 | 11.9989 | NaN | NaN | NaN | 12.9485 | 93.2829 | NaN | NaN | NaN | -17.3825 | NaN | 62.3943 | NaN | NaN | 576.5472 | NaN | 28.1886 | NaN | 28.0517
945.1292 | 12.451 | 12.3611 | 12.341 | 12.5629 | 11.9283 | 12.5845 | 12.223 | 11.9957 | NaN | NaN | NaN | 12.9656 | 92.0604 | NaN | NaN | NaN | -8.8929 | NaN | 63.3273 | NaN | NaN | 579.2968 | NaN | 28.762 | NaN | 27.5361
946.1292 | 12.5797 | 12.3507 | 12.3509 | 12.6281 | 11.9174 | 12.5851 | 12.2198 | 12.004 | NaN | NaN | NaN | 12.9483 | 92.3889 | NaN | NaN | NaN | 4.4018 | NaN | 61.5947 | NaN | NaN | 575.1687 | NaN | 27.4077 | NaN | 29.4893
947.1292 | 12.4822 | 12.47 | 12.3488 | 12.6401 | 11.8463 | 12.641 | 12.2339 | 12.0078 | NaN | NaN | NaN | 12.8875 | 91.3581 | NaN | NaN | NaN | 2.6994 | NaN | 61.9834 | NaN | NaN | 576.1869 | NaN | 28.1477 | NaN | 28.4297
948.1292 | 12.488 | 12.5451 | 12.3454 | 12.5878 | 11.8846 | 12.6323 | 12.2555 | 11.9965 | NaN | NaN | NaN | 12.958 | 93.2433 | NaN | NaN | NaN | -16.052 | NaN | 64.3052 | NaN | NaN | 578.4328 | NaN | 28.7651 | NaN | 28.359
949.1292 | 12.5736 | 12.3849 | 12.3378 | 12.6088 | 11.8296 | 12.5658 | 12.2169 | 12.0078 | NaN | NaN | NaN | 12.955 | 90.1484 | NaN | NaN | NaN | -19.7459 | NaN | 62.6681 | NaN | NaN | 579.7507 | NaN | 29.4733 | NaN | 28.0753
950.1292 | 12.4745 | 12.5398 | 12.3492 | 12.593 | 11.8732 | 12.6555 | 12.2594 | 12.017 | NaN | NaN | NaN | 12.9638 | 91.8808 | NaN | NaN | NaN | 4.5928 | NaN | 63.3752 | NaN | NaN | 580.4542 | NaN | 28.3608 | NaN | 29.58
951.1292 | 12.5367 | 12.4563 | 12.3558 | 12.5698 | 12.0133 | 12.6423 | 12.2607 | 12.0132 | NaN | NaN | NaN | 12.8774 | 95.7959 | NaN | NaN | NaN | 1.0071 | NaN | 64.1539 | NaN | NaN | 577.6617 | NaN | 26.657 | NaN | 27.6752
952.1292 | 12.6613 | 12.6503 | 12.353 | 12.5899 | 11.9384 | 12.8063 | 12.2868 | 12.0232 | NaN | NaN | NaN | 12.9149 | 92.3927 | NaN | NaN | NaN | -18.0343 | NaN | 63.6215 | NaN | NaN | 576.9854 | NaN | 26.579 | NaN | 28.6643
953.1292 | 12.5576 | 12.5457 | 12.3571 | 12.6611 | 11.9325 | 12.7119 | 12.2979 | 12.0188 | NaN | NaN | NaN | 12.9245 | 94.3215 | NaN | NaN | NaN | -18.3413 | NaN | 63.1583 | NaN | NaN | 578.3205 | NaN | 28.1129 | NaN | 27.5851
954.1292 | 12.5195 | 12.5273 | 12.3641 | 12.6342 | 12.0197 | 12.7296 | 12.2729 | 12.02 | NaN | NaN | NaN | 12.8931 | 93.0644 | NaN | NaN | NaN | 2.7116 | NaN | 62.6939 | NaN | NaN | 578.5302 | NaN | 30.956 | NaN | 29.7126
955.1292 | 12.5191 | 12.3399 | 12.3568 | 12.5809 | 11.9338 | 12.508 | 12.2231 | 12.0244 | NaN | NaN | NaN | 12.8946 | 93.3434 | NaN | NaN | NaN | -12.953 | NaN | 62.381 | NaN | NaN | 578.8479 | NaN | 27.4793 | NaN | 27.5503
956.1292 | 12.51 | 12.3366 | 12.3568 | 12.5975 | 11.8775 | 12.5461 | 12.2316 | 12.028 | NaN | NaN | NaN | 12.8569 | 91.0343 | NaN | NaN | NaN | -0.916 | NaN | 64.4142 | NaN | NaN | 579.2606 | NaN | 27.761 | NaN | 23.0892
957.1292 | 12.7273 | 12.4021 | 12.3575 | 12.6275 | 12.0166 | 12.5807 | 12.2505 | 12.0265 | NaN | NaN | NaN | 12.8843 | 92.7714 | NaN | NaN | NaN | -19.5703 | NaN | 62.4615 | NaN | NaN | 577.0414 | NaN | 29.132 | NaN | 27.8349
958.1292 | 12.5851 | 12.4484 | 12.3586 | 12.6297 | 12.0268 | 12.6105 | 12.2576 | 12.0296 | NaN | NaN | NaN | 12.9618 | 94.3485 | NaN | NaN | NaN | 5.2344 | NaN | 62.122 | NaN | NaN | 578.5967 | NaN | 27.0103 | NaN | 27.9227
959.1292 | 12.5318 | 12.6206 | 12.3543 | 12.7732 | 11.9292 | 12.6408 | 12.2967 | 12.0348 | NaN | NaN | NaN | 12.8835 | 92.672 | NaN | NaN | NaN | 5.1007 | NaN | 61.9802 | NaN | NaN | 580.0265 | NaN | 28.2462 | NaN | 29.4228
960.1292 | 12.5722 | 12.3874 | 12.3527 | 12.572 | 11.9032 | 12.5595 | 12.25 | 12.0387 | NaN | NaN | NaN | 12.916 | 91.6694 | NaN | NaN | NaN | -17.5565 | NaN | 63.497 | NaN | NaN | 578.5829 | NaN | 27.9848 | NaN | 28.4446
961.1292 | 12.5318 | 12.3998 | 12.3466 | 12.994 | 12.0387 | 12.5257 | 12.2472 | 12.0369 | NaN | NaN | NaN | 12.8939 | 91.7014 | NaN | NaN | NaN | -14.7442 | NaN | 61.2114 | NaN | NaN | 576.422 | NaN | 27.4195 | NaN | 29.1061
962.1292 | 12.5404 | 12.4166 | 12.351 | 12.5881 | 11.9891 | 12.5933 | 12.2719 | 12.047 | NaN | NaN | NaN | 12.9365 | 92.9974 | NaN | NaN | NaN | -16.7977 | NaN | 62.176 | NaN | NaN | 575.1016 | NaN | 28.098 | NaN | 27.3025
963.1292 | 12.5393 | 12.5677 | 12.3434 | 12.6531 | 11.8526 | 12.7256 | 12.3051 | 12.0444 | NaN | NaN | NaN | 12.86 | 93.0764 | NaN | NaN | NaN | -8.1385 | NaN | 61.2823 | NaN | NaN | 574.7882 | NaN | 28.0998 | NaN | 28.4807
964.1292 | 12.5863 | 12.4665 | 12.3386 | 12.6578 | 11.9533 | 12.6382 | 12.2669 | 12.043 | NaN | NaN | NaN | 12.8743 | 91.7313 | NaN | NaN | NaN | 0.7562 | NaN | 61.6858 | NaN | NaN | 574.7808 | NaN | 27.4609 | NaN | 28.1745
965.1292 | 12.6218 | 12.5122 | 12.3292 | 12.5919 | 11.9571 | 12.7083 | 12.304 | 12.0484 | NaN | NaN | NaN | 12.8589 | 92.7522 | NaN | NaN | NaN | -11.6071 | NaN | 62.6884 | NaN | NaN | 574.997 | NaN | 27.9262 | NaN | 27.1302
966.1292 | 12.5731 | 12.4275 | 12.3395 | 12.6322 | 11.8587 | 12.6047 | 12.2668 | 12.0419 | NaN | NaN | NaN | 12.9619 | 91.5844 | NaN | NaN | NaN | 41.4755 | NaN | 61.063 | NaN | NaN | 572.1515 | NaN | 28.403 | NaN | 28.5153
967.1292 | 12.5565 | 12.4766 | 12.3439 | 12.6204 | 11.9625 | 12.5934 | 12.2674 | 12.0549 | NaN | NaN | NaN | 12.9027 | 91.6577 | NaN | NaN | NaN | -15.7661 | NaN | 63.3368 | NaN | NaN | 574.9626 | NaN | 28.8244 | NaN | 28.7212
968.1292 | 12.5655 | 12.4362 | 12.3462 | 12.5922 | 11.8958 | 12.5582 | 12.2652 | 12.0506 | NaN | NaN | NaN | 12.8315 | 93.9112 | NaN | NaN | NaN | -19.7435 | NaN | 63.5969 | NaN | NaN | 571.0416 | NaN | 27.5294 | NaN | 27.1451
969.1292 | 12.5078 | 12.3809 | 12.3417 | 12.6612 | 12.0164 | 12.5488 | 12.2534 | 12.0619 | NaN | NaN | NaN | 12.87 | 92.2038 | NaN | NaN | NaN | -19.1334 | NaN | 62.6694 | NaN | NaN | 570.8684 | NaN | 29.4264 | NaN | 25.3042
970.1292 | 12.5402 | 12.8021 | 12.334 | 12.6194 | 11.9232 | 12.9167 | 12.3654 | 12.0575 | NaN | NaN | NaN | 12.8776 | 91.783 | NaN | NaN | NaN | -18.4742 | NaN | 63.1411 | NaN | NaN | 571.8637 | NaN | 29.3612 | NaN | 28.6244
971.1292 | 12.5165 | 12.3443 | 12.3397 | 12.6675 | 11.9205 | 12.5056 | 12.2455 | 12.0548 | NaN | NaN | NaN | 12.8562 | 93.2569 | NaN | NaN | NaN | -18.1489 | NaN | 61.5459 | NaN | NaN | 572.218 | NaN | 28.121 | NaN | 26.797
972.1292 | 12.7737 | 12.4664 | 12.3442 | 12.6398 | 11.8909 | 12.6536 | 12.2961 | 12.0659 | NaN | NaN | NaN | 12.9008 | 91.856 | NaN | NaN | NaN | -5.7815 | NaN | 63.1804 | NaN | NaN | 571.5846 | NaN | 28.1417 | NaN | 27.0681
973.1292 | 12.5873 | 12.363 | 12.3403 | 12.6323 | 11.8935 | 12.5385 | 12.2567 | 12.0597 | NaN | NaN | NaN | 12.8912 | 91.5291 | NaN | NaN | NaN | 0.8326 | NaN | 61.7506 | NaN | NaN | 570.7251 | NaN | 29.1123 | NaN | 28.1432
974.1292 | 12.637 | 12.7307 | 12.3497 | 12.6444 | 11.8647 | 12.8395 | 12.4014 | 12.0627 | NaN | NaN | NaN | 12.8916 | 91.8151 | NaN | NaN | NaN | -7.3414 | NaN | 63.1592 | NaN | NaN | 570.6159 | NaN | 28.5632 | NaN | 27.6602
975.1292 | 12.5666 | 12.4003 | 12.3556 | 12.5765 | 11.8273 | 12.6061 | 12.2722 | 12.0662 | NaN | NaN | NaN | 12.8547 | 91.8654 | NaN | NaN | NaN | -5.3264 | NaN | 62.6481 | NaN | NaN | 572.4497 | NaN | 27.9582 | NaN | 27.5833
976.1292 | 12.6818 | 12.3821 | 12.3568 | 12.6424 | 11.9701 | 12.5364 | 12.2503 | 12.0647 | NaN | NaN | NaN | 12.8011 | 89.2965 | NaN | NaN | NaN | NaN | NaN | 62.3387 | NaN | NaN | 569.1031 | NaN | 29.6276 | NaN | 27.8835
977.1292 | 12.6239 | 12.4056 | 12.3545 | 12.6813 | 12.0487 | 12.5956 | 12.2721 | 12.0705 | NaN | NaN | NaN | 12.8689 | 91.9097 | NaN | NaN | NaN | -15.7812 | NaN | 62.7846 | NaN | NaN | 569.996 | NaN | 28.4857 | NaN | 28.1445
978.1292 | 12.528 | 12.3856 | 12.3593 | 12.7243 | 11.8766 | 12.5589 | 12.2604 | 12.0713 | NaN | NaN | NaN | 12.8203 | 91.5012 | NaN | NaN | NaN | 0.0094 | NaN | 61.4635 | NaN | NaN | 570.5452 | NaN | 28.2794 | NaN | 28.6886
979.1292 | 12.7682 | 12.4332 | 12.3709 | 12.5968 | 11.9949 | 12.6457 | 12.2911 | 12.0722 | NaN | NaN | NaN | 12.8805 | 92.0479 | NaN | NaN | NaN | -16.9695 | NaN | 62.7992 | NaN | NaN | 569.5954 | NaN | 27.0736 | NaN | 27.0059
980.1292 | 12.6014 | 12.454 | 12.369 | 12.661 | 11.8916 | 12.6756 | 12.2897 | 12.0758 | NaN | NaN | NaN | 12.766 | 92.3822 | NaN | NaN | NaN | -14.1399 | NaN | 62.2262 | NaN | NaN | 567.1419 | NaN | 28.1912 | NaN | 27.4801
981.1292 | 12.6664 | 12.8175 | 12.3717 | 12.757 | 11.9621 | 12.8582 | 12.4449 | 12.0804 | NaN | NaN | NaN | 12.8303 | 92.2523 | NaN | NaN | NaN | -7.2139 | NaN | 63.9858 | NaN | NaN | 567.2819 | NaN | 28.6414 | NaN | 28.0009
982.1292 | 12.5618 | 12.3805 | 12.3719 | 12.7512 | 11.9408 | 12.5341 | 12.2558 | 12.0741 | NaN | NaN | NaN | 12.872 | 91.911 | NaN | NaN | NaN | 15.455 | NaN | 61.5901 | NaN | NaN | 564.4449 | NaN | 27.4605 | NaN | 26.1538
983.1292 | 12.5906 | 12.4148 | 12.3709 | 12.6204 | 11.9558 | 12.591 | 12.2765 | 12.0836 | NaN | NaN | NaN | 12.8879 | 91.772 | NaN | NaN | NaN | 29.3169 | NaN | 62.9464 | NaN | NaN | 566.4974 | NaN | 27.8243 | NaN | 27.5658
984.1292 | 12.5464 | 12.4282 | 12.3683 | 12.6005 | 11.9972 | 12.6322 | 12.2959 | 12.0827 | NaN | NaN | NaN | 12.8761 | 92.746 | NaN | NaN | NaN | 18.1523 | NaN | 61.6512 | NaN | NaN | 566.1476 | NaN | 27.6838 | NaN | 20.6245
985.1292 | 12.5425 | 12.6644 | 12.3714 | 12.6231 | 11.9291 | 12.7579 | 12.32 | 12.0841 | NaN | NaN | NaN | 12.8658 | 92.1965 | NaN | NaN | NaN | -17.3979 | NaN | 61.5802 | NaN | NaN | 566.6759 | NaN | 26.7184 | NaN | 26.221
986.1292 | 12.532 | 12.4848 | 12.3807 | 12.6293 | 12.0181 | 12.6204 | 12.2935 | 12.0875 | NaN | NaN | NaN | 12.7708 | 93.5419 | NaN | NaN | NaN | 12.8104 | NaN | 63.4565 | NaN | NaN | 567.0947 | NaN | 28.8984 | NaN | 25.1052
987.1292 | 12.5867 | 12.5946 | 12.3755 | 12.8872 | 11.9707 | 12.753 | 12.3019 | 12.0897 | NaN | NaN | NaN | 12.8022 | 92.9201 | NaN | NaN | NaN | -17.9082 | NaN | 64.0569 | NaN | NaN | 567.5443 | NaN | 27.5113 | NaN | 28.3979
988.1292 | 12.51 | 12.6956 | 12.3826 | 12.656 | 11.9804 | 12.7755 | 12.3498 | 12.0989 | NaN | NaN | NaN | 12.8662 | 92.8532 | NaN | NaN | NaN | 7.5737 | NaN | 62.8376 | NaN | NaN | 566.3712 | NaN | 28.5438 | NaN | 26.7953
989.1292 | 12.5347 | 12.3935 | 12.3851 | 12.6079 | 11.9967 | 12.6239 | 12.2807 | 12.0873 | NaN | NaN | NaN | 12.7883 | 92.4859 | NaN | NaN | NaN | -13.7036 | NaN | 62.6521 | NaN | NaN | 569.238 | NaN | 26.498 | NaN | 26.6091
990.1292 | 12.6594 | 12.6345 | 12.3869 | 12.6822 | 11.9854 | 12.7407 | 12.3491 | 12.0991 | NaN | NaN | NaN | 12.7818 | 89.6271 | NaN | NaN | NaN | NaN | NaN | 62.3126 | NaN | NaN | 568.8777 | NaN | 27.9401 | NaN | 27.2685
991.1292 | 12.5368 | 12.439 | 12.3846 | 12.652 | 12.0144 | 12.6269 | 12.2986 | 12.0983 | NaN | NaN | NaN | 12.7714 | 92.5783 | NaN | NaN | NaN | -16.3441 | NaN | 62.3161 | NaN | NaN | 569.5772 | NaN | 28.1263 | NaN | 27.5443
992.1292 | 12.604 | 12.4231 | 12.388 | 12.6602 | 11.8875 | 12.6306 | 12.291 | 12.1014 | NaN | NaN | NaN | 12.7719 | 91.4541 | NaN | NaN | NaN | -7.9057 | NaN | 63.1131 | NaN | NaN | 568.2128 | NaN | 27.3843 | NaN | 28.1394
993.1292 | 12.5903 | 12.5165 | 12.3913 | 12.6503 | 11.9535 | 12.7427 | 12.3358 | 12.1042 | NaN | NaN | NaN | 12.7697 | 92.6016 | NaN | NaN | NaN | -14.0279 | NaN | 62.3666 | NaN | NaN | 568.8393 | NaN | 28.7304 | NaN | 27.8572
994.1292 | 12.581 | 12.5091 | 12.3857 | 12.6548 | 11.9084 | 12.6763 | 12.3258 | 12.1066 | NaN | NaN | NaN | 12.841 | 93.4819 | NaN | NaN | NaN | 1.7622 | NaN | 61.9639 | NaN | NaN | 568.9033 | NaN | 28.4351 | NaN | 26.8508
995.1292 | 12.5287 | 12.4994 | 12.3879 | 12.6713 | 11.9721 | 12.6661 | 12.2902 | 12.1114 | NaN | NaN | NaN | 12.8021 | 91.5502 | NaN | NaN | NaN | -13.7689 | NaN | 60.6144 | NaN | NaN | 568.6114 | NaN | 28.6805 | NaN | 26.9001
996.1292 | 12.6245 | 12.6395 | 12.3851 | 12.8035 | 12.0121 | 12.7685 | 12.324 | 12.1072 | NaN | NaN | NaN | 12.7853 | 92.0971 | NaN | NaN | NaN | -9.8106 | NaN | 61.2163 | NaN | NaN | 568.6336 | NaN | 26.4164 | NaN | 27.6059
997.1292 | 12.6183 | 13.0161 | 12.3842 | 12.717 | 12.0656 | 13.0229 | 12.4662 | 12.1132 | NaN | NaN | NaN | 12.8046 | 90.9801 | NaN | NaN | NaN | -10.7586 | NaN | 62.5376 | NaN | NaN | 568.7371 | NaN | 27.0257 | NaN | 29.3065
998.1292 | 12.5549 | 12.5338 | 12.3861 | 12.9584 | 12.0386 | 12.7042 | 12.2978 | 12.106 | NaN | NaN | NaN | 12.7608 | 92.949 | NaN | NaN | NaN | -2.0519 | NaN | 62.2539 | NaN | NaN | 568.8708 | NaN | 28.6601 | NaN | 26.0912
999.1292 | 12.579 | 12.4375 | 12.3805 | 12.6069 | 11.9933 | 12.598 | 12.2799 | 12.107 | NaN | NaN | NaN | 12.7816 | 90.3566 | NaN | NaN | NaN | 1.464 | NaN | 62.6587 | NaN | NaN | 569.3962 | NaN | 27.8555 | NaN | 28.8314
1000.1292 | 12.5953 | 12.5909 | 12.3779 | 12.6553 | 12.0566 | 12.7536 | 12.3315 | 12.1092 | NaN | NaN | NaN | 12.7606 | 92.8621 | NaN | NaN | NaN | NaN | NaN | 62.9316 | NaN | NaN | 565.8493 | NaN | 28.5441 | NaN | 24.375
1001.1292 | 12.6187 | 12.5778 | 12.3798 | 12.7627 | 12.0578 | 12.7241 | 12.3126 | 12.108 | NaN | NaN | NaN | 12.7718 | 91.7832 | NaN | NaN | NaN | 3.0239 | NaN | 62.3211 | NaN | NaN | 563.7155 | NaN | 27.0404 | NaN | 28.3126
1002.1292 | 12.7982 | 12.5021 | 12.3804 | 12.7204 | 11.9859 | 12.6211 | 12.293 | 12.112 | NaN | NaN | NaN | 12.7779 | 91.3159 | NaN | NaN | NaN | -11.0255 | NaN | 62.6396 | NaN | NaN | 566.099 | NaN | 27.7278 | NaN | 27.5744
1003.1292 | 12.6096 | 12.4576 | 12.3831 | 12.7125 | 12.1091 | 12.5877 | 12.2732 | 12.1106 | NaN | NaN | NaN | 12.81 | 92.8268 | NaN | NaN | NaN | 42.5474 | NaN | 61.4579 | NaN | NaN | 567.9082 | NaN | 29.5336 | NaN | 25.3541
1004.1292 | 12.6536 | 12.4615 | 12.383 | 12.695 | 12.0889 | 12.597 | 12.2719 | 12.1074 | NaN | NaN | NaN | 12.7717 | 91.9537 | NaN | NaN | NaN | 10.7411 | NaN | 62.083 | NaN | NaN | 567.4662 | NaN | 28.3485 | NaN | 25.5056
1005.1292 | 12.5835 | 12.5112 | 12.3931 | 12.6865 | 11.9014 | 12.6751 | 12.2987 | 12.1022 | NaN | NaN | NaN | 12.8739 | 91.2555 | NaN | NaN | NaN | -14.5965 | NaN | 63.5882 | NaN | NaN | 568.9294 | NaN | 27.3268 | NaN | 28.038
1006.1292 | 12.7577 | 12.7626 | 12.3876 | 12.7135 | 12.078 | 12.8261 | 12.3584 | 12.1103 | NaN | NaN | NaN | 12.7866 | 92.9789 | NaN | NaN | NaN | -17.6612 | NaN | 62.3229 | NaN | NaN | 566.9767 | NaN | 27.3311 | NaN | 26.2408
1007.1292 | 12.725 | 12.6643 | 12.3873 | 12.7158 | 12.0558 | 12.7588 | 12.3259 | 12.1096 | NaN | NaN | NaN | 12.7808 | 90.1763 | NaN | NaN | NaN | -8.9984 | NaN | 62.982 | NaN | NaN | 567.6713 | NaN | 29.1893 | NaN | 27.4735
1008.1292 | 12.6089 | 12.4564 | 12.3857 | 12.6961 | 11.8494 | 12.5711 | 12.2487 | 12.1104 | NaN | NaN | NaN | 12.7914 | 91.846 | NaN | NaN | NaN | NaN | NaN | 63.3513 | NaN | NaN | 568.4186 | NaN | 27.7604 | NaN | 28.4007
1009.1292 | 12.5957 | 12.5634 | 12.3906 | 12.6643 | 11.9885 | 12.6779 | 12.3116 | 12.1015 | NaN | NaN | NaN | 12.7553 | 89.9332 | NaN | NaN | NaN | 1.0507 | NaN | 62.5619 | NaN | NaN | 569.0595 | NaN | 25.9368 | NaN | 24.8611
1010.1292 | 12.6126 | 12.6858 | 12.3838 | 12.7259 | 11.9023 | 12.7044 | 12.3314 | 12.1027 | NaN | NaN | NaN | 12.7341 | 91.8561 | NaN | NaN | NaN | -10.9798 | NaN | 62.9435 | NaN | NaN | 569.2323 | NaN | 26.979 | NaN | 28.9745
1011.1292 | 12.6417 | 12.5917 | 12.3834 | 12.8112 | 12.034 | 12.6315 | 12.2967 | 12.1043 | NaN | NaN | NaN | 12.7569 | 91.7529 | NaN | NaN | NaN | -8.5338 | NaN | 62.4932 | NaN | NaN | 569.0276 | NaN | 27.94 | NaN | 28.6263
1012.1292 | 12.5778 | 12.6064 | 12.385 | 12.8451 | 11.9229 | 12.6789 | 12.3062 | 12.107 | NaN | NaN | NaN | 12.7556 | 92.6717 | NaN | NaN | NaN | -14.0223 | NaN | 62.0344 | NaN | NaN | 569.3582 | NaN | 27.9158 | NaN | 28.1857
1013.1292 | 12.6266 | 12.4717 | 12.3796 | 12.6993 | 12.0023 | 12.5819 | 12.2762 | 12.1069 | NaN | NaN | NaN | 12.7659 | 91.3941 | NaN | NaN | NaN | -8.3261 | NaN | 62.4273 | NaN | NaN | 570.6536 | NaN | 28.2648 | NaN | 26.87
1014.1292 | 12.7306 | 12.7143 | 12.381 | 12.6398 | 12.0846 | 12.7479 | 12.3134 | 12.1085 | NaN | NaN | NaN | 12.717 | 90.8462 | NaN | NaN | NaN | 8.3829 | NaN | 63.3661 | NaN | NaN | 569.1606 | NaN | 27.8433 | NaN | 24.6645
1015.1292 | 12.6291 | 12.3845 | 12.379 | 12.691 | 11.9926 | 12.5328 | 12.2302 | 12.1082 | NaN | NaN | NaN | 12.7047 | 92.2805 | NaN | NaN | NaN | 4.2232 | NaN | 62.6901 | NaN | NaN | 572.6548 | NaN | 25.403 | NaN | 28.4964
1016.1292 | 12.6195 | 12.3866 | 12.3811 | 12.7217 | 12.035 | 12.5122 | 12.233 | 12.1071 | NaN | NaN | NaN | 12.713 | 91.9498 | NaN | NaN | NaN | -16.037 | NaN | 61.9433 | NaN | NaN | 570.9301 | NaN | 27.2662 | NaN | 28.5486
1017.1292 | 12.6657 | 12.5115 | 12.3815 | 12.7386 | 12.0996 | 12.6935 | 12.2766 | 12.1054 | NaN | NaN | NaN | 12.7528 | 91.6443 | NaN | NaN | NaN | -9.8615 | NaN | 62.0643 | NaN | NaN | 571.2807 | NaN | 27.7533 | NaN | 26.5294
1018.1292 | 12.7849 | 12.7559 | 12.3855 | 12.7187 | 12.0773 | 12.8932 | 12.3627 | 12.1058 | NaN | NaN | NaN | 12.7735 | 93.4153 | NaN | NaN | NaN | 1.222 | NaN | 63.0436 | NaN | NaN | 571.8943 | NaN | 27.6927 | NaN | 26.6531
1019.1292 | 12.7417 | 12.3671 | 12.3871 | 12.7211 | 11.988 | 12.529 | 12.2367 | 12.1063 | NaN | NaN | NaN | 12.751 | 91.7905 | NaN | NaN | NaN | -8.1094 | NaN | 62.7703 | NaN | NaN | 574.5677 | NaN | 28.7166 | NaN | 29.15
1020.1292 | 12.6319 | 12.606 | 12.3915 | 12.7801 | 12.0541 | 12.6614 | 12.2907 | 12.1083 | NaN | NaN | NaN | 12.7547 | 90.8575 | NaN | NaN | NaN | -14.8412 | NaN | 61.3914 | NaN | NaN | 572.8605 | NaN | 29.2221 | NaN | 29.0826
1021.1292 | 12.5686 | 12.4019 | 12.3896 | 12.6628 | 12.1684 | 12.6249 | 12.2578 | 12.1093 | NaN | NaN | NaN | 12.7216 | 93.2168 | NaN | NaN | NaN | 26.9478 | NaN | 62.2373 | NaN | NaN | 576.1743 | NaN | 27.792 | NaN | 28.5333
1022.1292 | 12.5647 | 12.9778 | 12.3929 | 12.7462 | 12.0676 | 12.9925 | 12.4193 | 12.1027 | NaN | NaN | NaN | 12.7387 | 91.7899 | NaN | NaN | NaN | -13.7729 | NaN | 61.4929 | NaN | NaN | 576.3829 | NaN | 26.4793 | NaN | 29.3138
1023.1292 | 12.8903 | 12.4839 | 12.3901 | 12.741 | 12.0765 | 12.6583 | 12.2817 | 12.1076 | NaN | NaN | NaN | 12.8132 | 89.0588 | NaN | NaN | NaN | -15.7048 | NaN | 60.3478 | NaN | NaN | 577.2711 | NaN | 27.6247 | NaN | 27.3181
1024.1292 | 12.5792 | 12.6085 | 12.3954 | 12.7225 | 12.0463 | 12.7636 | 12.292 | 12.101 | NaN | NaN | NaN | 12.812 | 92.064 | NaN | NaN | NaN | -5.503 | NaN | 63.2904 | NaN | NaN | 578.1816 | NaN | 27.4579 | NaN | 25.6945
1025.1292 | 12.6355 | 12.8345 | 12.3935 | 12.7659 | 12.052 | 12.9313 | 12.3213 | 12.1019 | NaN | NaN | NaN | 12.7693 | 91.1896 | NaN | NaN | NaN | 15.0115 | NaN | 61.3055 | NaN | NaN | 577.9072 | NaN | 27.912 | NaN | 28.4072
1026.1292 | 12.6865 | 12.82 | 12.3951 | 12.7832 | 11.9228 | 12.7642 | 12.3315 | 12.1045 | NaN | NaN | NaN | 12.7297 | 92.0527 | NaN | NaN | NaN | -13.8174 | NaN | 62.6057 | NaN | NaN | 577.895 | NaN | 28.5891 | NaN | 26.6591
1027.1292 | 12.7007 | 12.4785 | 12.3909 | 12.7578 | 12.0518 | 12.7054 | 12.2696 | 12.1065 | NaN | NaN | NaN | 12.7348 | 92.125 | NaN | NaN | NaN | -19.265 | NaN | 61.3948 | NaN | NaN | 577.9633 | NaN | 27.1017 | NaN | 28.2189
1028.1292 | 12.6105 | 12.3187 | 12.3912 | 12.7364 | 12.0645 | 12.4892 | 12.2067 | 12.1051 | NaN | NaN | NaN | 12.7549 | 92.3027 | NaN | NaN | NaN | -15.1714 | NaN | 62.7152 | NaN | NaN | 578.8078 | NaN | 27.2906 | NaN | 25.0811
1029.1292 | 12.6873 | 12.5119 | 12.3823 | 12.695 | 12.1288 | 12.6753 | 12.2615 | 12.1055 | NaN | NaN | NaN | 12.7436 | 91.6784 | NaN | NaN | NaN | -18.7801 | NaN | 61.5011 | NaN | NaN | 578.0243 | NaN | 28.8086 | NaN | 27.7911
1030.1292 | 12.6679 | 12.5066 | 12.3786 | 12.7176 | 12.0142 | 12.7115 | 12.2793 | 12.1071 | NaN | NaN | NaN | 12.8439 | 91.1376 | NaN | NaN | NaN | -12.808 | NaN | 62.4197 | NaN | NaN | 579.7067 | NaN | 27.8634 | NaN | 27.5653
1031.1292 | 12.6317 | 12.6693 | 12.379 | 12.8232 | 12.1146 | 12.7345 | 12.278 | 12.1084 | NaN | NaN | NaN | 12.766 | 92.437 | NaN | NaN | NaN | -15.7843 | NaN | 62.1044 | NaN | NaN | 579.0857 | NaN | 28.5304 | NaN | 27.6736
1032.1292 | 12.6848 | 12.4984 | 12.3753 | 12.7202 | 11.9831 | 12.7391 | 12.2828 | 12.1142 | NaN | NaN | NaN | 12.7723 | 91.8967 | NaN | NaN | NaN | -3.4126 | NaN | 62.4119 | NaN | NaN | 580.3867 | NaN | 27.219 | NaN | 28.9388
1033.1292 | 12.6462 | 12.6893 | 12.3787 | 12.6965 | 12.1486 | 12.7886 | 12.3101 | 12.1134 | NaN | NaN | NaN | 12.7197 | 92.7796 | NaN | NaN | NaN | -2.0804 | NaN | 62.623 | NaN | NaN | 579.7231 | NaN | 27.4032 | NaN | 28.1705
1034.1292 | 12.6515 | 12.5998 | 12.3763 | 12.6764 | 12.0486 | 12.7841 | 12.2896 | 12.1093 | NaN | NaN | NaN | 12.7342 | 92.9457 | NaN | NaN | NaN | -10.3466 | NaN | 62.6258 | NaN | NaN | 581.1978 | NaN | 27.681 | NaN | 27.0699
1035.1292 | 12.8554 | 12.4285 | 12.3801 | 12.7033 | 12.1772 | 12.5998 | 12.2344 | 12.1104 | NaN | NaN | NaN | 12.784 | 91.8497 | NaN | NaN | NaN | 6.0708 | NaN | 62.6372 | NaN | NaN | 579.7643 | NaN | 29.4511 | NaN | 28.5234
1036.1292 | 12.6248 | 12.3683 | 12.3825 | 12.903 | 11.994 | 12.5569 | 12.2247 | 12.1062 | NaN | NaN | NaN | 12.7992 | 89.3284 | NaN | NaN | NaN | 2.9474 | NaN | 62.6161 | NaN | NaN | 581.287 | NaN | 27.9947 | NaN | 28.3558
1037.1292 | 12.6856 | 12.5887 | 12.3795 | 12.6894 | 12.0487 | 12.7479 | 12.3135 | 12.1108 | NaN | NaN | NaN | 12.7493 | 89.0614 | NaN | NaN | NaN | -1.0028 | NaN | 61.553 | NaN | NaN | 580.519 | NaN | 26.3513 | NaN | 26.035
1038.1292 | 12.6529 | 12.4704 | 12.3863 | 12.7413 | 12.01 | 12.619 | 12.2395 | 12.1022 | NaN | NaN | NaN | 12.6992 | 92.1959 | NaN | NaN | NaN | -16.389 | NaN | 62.0323 | NaN | NaN | 581.3356 | NaN | 27.1342 | NaN | 28.1406
1039.1292 | 12.5975 | 12.6163 | 12.3884 | 12.7232 | 12.0431 | 12.7831 | 12.2948 | 12.1083 | NaN | NaN | NaN | 12.717 | 92.1765 | NaN | NaN | NaN | -17.0245 | NaN | 62.7959 | NaN | NaN | 582.5378 | NaN | 26.7075 | NaN | 26.6396
1040.1292 | 12.7496 | 12.5787 | 12.3907 | 12.8067 | 11.9566 | 12.7257 | 12.2909 | 12.1111 | NaN | NaN | NaN | 12.787 | 93.4593 | NaN | NaN | NaN | -6.831 | NaN | 62.5971 | NaN | NaN | 582.3139 | NaN | 26.1703 | NaN | 27.0412
1041.1292 | 12.6905 | 12.508 | 12.386 | 12.7117 | 12.0865 | 12.7031 | 12.2824 | 12.1197 | NaN | NaN | NaN | 12.733 | 92.9381 | NaN | NaN | NaN | -15.5394 | NaN | 61.8647 | NaN | NaN | 583.4144 | NaN | 27.0608 | NaN | 28.611
1042.1292 | 12.6393 | 12.4603 | 12.3918 | 12.7633 | 12.0952 | 12.5982 | 12.2567 | 12.1012 | NaN | NaN | NaN | 12.6999 | 92.2633 | NaN | NaN | NaN | -13.6471 | NaN | 61.533 | NaN | NaN | 584.361 | NaN | 27.9339 | NaN | 27.78
1043.1292 | 12.692 | 12.5999 | 12.3878 | 12.8961 | 12.0656 | 12.7626 | 12.3144 | 12.1091 | NaN | NaN | NaN | 12.7223 | 92.6627 | NaN | NaN | NaN | -18.4015 | NaN | 63.5294 | NaN | NaN | 584.402 | NaN | 27.3395 | NaN | 26.5988
1044.1292 | 12.6631 | 12.3591 | 12.3944 | 12.7892 | 12.1034 | 12.4888 | 12.2282 | 12.1049 | NaN | NaN | NaN | 12.7187 | 90.8248 | NaN | NaN | NaN | -16.872 | NaN | 60.7521 | NaN | NaN | 582.9029 | NaN | 27.3121 | NaN | 27.9318
1045.1292 | 12.6958 | 12.5156 | 12.391 | 12.7813 | 12.0751 | 12.68 | 12.2974 | 12.1128 | NaN | NaN | NaN | 12.7342 | 91.7285 | NaN | NaN | NaN | -14.7591 | NaN | 62.4227 | NaN | NaN | 581.3414 | NaN | 28.546 | NaN | 27.125
1046.1292 | 12.6085 | 12.5912 | 12.3963 | 12.7071 | 12.0123 | 12.7038 | 12.3082 | 12.1028 | NaN | NaN | NaN | 12.7764 | 92.1123 | NaN | NaN | NaN | -7.1285 | NaN | 63.0203 | NaN | NaN | 580.249 | NaN | 27.2784 | NaN | 27.954
1047.1292 | 12.7385 | 12.5159 | 12.3942 | 12.7599 | 12.1777 | 12.6805 | 12.2865 | 12.1136 | NaN | NaN | NaN | 12.7359 | 92.4487 | NaN | NaN | NaN | -16.191 | NaN | 60.8801 | NaN | NaN | 582.5947 | NaN | 26.2783 | NaN | 26.7504
1048.1292 | 12.6486 | 12.5142 | 12.3913 | 12.7599 | 12.1852 | 12.6633 | 12.2829 | 12.1148 | NaN | NaN | NaN | 12.7858 | 91.5144 | NaN | NaN | NaN | -17.5721 | NaN | 60.408 | NaN | NaN | 582.7496 | NaN | 26.6471 | NaN | 26.6936
1049.1292 | 12.8142 | 12.6063 | 12.393 | 12.8362 | 12.1033 | 12.754 | 12.2865 | 12.1083 | NaN | NaN | NaN | 12.761 | 90.1634 | NaN | NaN | NaN | 13.6217 | NaN | 61.783 | NaN | NaN | 581.5325 | NaN | 26.8195 | NaN | 28.4523
1050.1292 | 12.6032 | 12.5716 | 12.3922 | 12.8004 | 12.1443 | 12.7124 | 12.2867 | 12.113 | NaN | NaN | NaN | 12.7656 | 92.1951 | NaN | NaN | NaN | NaN | NaN | 60.864 | NaN | NaN | 581.6977 | NaN | 26.216 | NaN | 26.9355
1051.1292 | 12.7579 | 12.6724 | 12.3918 | 13.0037 | 11.9541 | 12.8163 | 12.3116 | 12.1174 | NaN | NaN | NaN | 12.7624 | 91.3576 | NaN | NaN | NaN | -13.7237 | NaN | 64.9807 | NaN | NaN | 581.5484 | NaN | 25.5461 | NaN | 26.1853
1052.1292 | 12.6479 | 12.6516 | 12.3949 | 12.9056 | 12.0438 | 12.8003 | 12.3139 | 12.115 | NaN | NaN | NaN | 12.7056 | 90.7446 | NaN | NaN | NaN | -13.9861 | NaN | 63.1505 | NaN | NaN | 583.1938 | NaN | 27.0011 | NaN | 28.2166
1053.1292 | 12.6324 | 12.5156 | 12.3982 | 12.725 | 12.0799 | 12.6013 | 12.2772 | 12.1207 | NaN | NaN | NaN | 12.802 | 91.631 | NaN | NaN | NaN | -11.3478 | NaN | 61.6561 | NaN | NaN | 583.1819 | NaN | 27.4965 | NaN | 28.9327
1054.1292 | 12.663 | 12.411 | 12.4031 | 12.7227 | 12.136 | 12.5572 | 12.2453 | 12.1215 | NaN | NaN | NaN | 12.7183 | 92.0199 | NaN | NaN | NaN | -3.2322 | NaN | 61.9526 | NaN | NaN | 584.1265 | NaN | 26.2583 | NaN | 26.6413
1055.1292 | 12.8054 | 12.5541 | 12.4054 | 12.9574 | 11.9765 | 12.7512 | 12.3154 | 12.1277 | NaN | NaN | NaN | 12.7066 | 91.5087 | NaN | NaN | NaN | -13.3024 | NaN | 64.0809 | NaN | NaN | 583.6605 | NaN | 26.4862 | NaN | 28.9834
1056.1292 | 12.6519 | 12.5909 | 12.4032 | 12.771 | 12.0039 | 12.7119 | 12.3141 | 12.1314 | NaN | NaN | NaN | 12.7914 | 91.7745 | NaN | NaN | NaN | 2.597 | NaN | 62.656 | NaN | NaN | 584.0708 | NaN | 26.1482 | NaN | 27.0722
1057.1292 | 12.8452 | 12.5473 | 12.4035 | 12.7558 | 12.1123 | 12.723 | 12.3058 | 12.1274 | NaN | NaN | NaN | 12.7416 | 91.9726 | NaN | NaN | NaN | -4.5344 | NaN | 62.8612 | NaN | NaN | 584.4286 | NaN | 27.5481 | NaN | 26.6613
1058.1292 | 12.6771 | 12.5739 | 12.4002 | 12.7235 | 11.953 | 12.7589 | 12.3102 | 12.1213 | NaN | NaN | NaN | 12.7071 | 91.4517 | NaN | NaN | NaN | NaN | NaN | 61.9845 | NaN | NaN | 584.9743 | NaN | 25.4127 | NaN | 28.5287
1059.1292 | 12.8796 | 12.5185 | 12.4099 | 12.7585 | 12.0071 | 12.6879 | 12.2989 | 12.137 | NaN | NaN | NaN | 12.6748 | 91.5167 | NaN | NaN | NaN | 17.2793 | NaN | 61.8312 | NaN | NaN | 583.2458 | NaN | 25.8877 | NaN | 27.816
1060.1292 | 12.6334 | 12.6176 | 12.4074 | 12.7747 | 12.0745 | 12.7815 | 12.3317 | 12.1251 | NaN | NaN | NaN | 12.8168 | 94.9497 | NaN | NaN | NaN | -19.3572 | NaN | 61.9762 | NaN | NaN | 584.6257 | NaN | 25.1019 | NaN | 27.9079
1061.1292 | 12.6284 | 12.4587 | 12.4076 | 12.8203 | 12.1129 | 12.6519 | 12.2966 | 12.1368 | NaN | NaN | NaN | 12.7598 | 92.655 | NaN | NaN | NaN | -3.9182 | NaN | 61.6502 | NaN | NaN | 582.8883 | NaN | 24.4572 | NaN | 26.9542
1062.1292 | 12.8168 | 12.4889 | 12.4108 | 12.7284 | 12.0608 | 12.6843 | 12.2986 | 12.1303 | NaN | NaN | NaN | 12.7142 | 92.4178 | NaN | NaN | NaN | -14.8612 | NaN | 61.5484 | NaN | NaN | 582.1794 | NaN | 26.3456 | NaN | 28.3847
1063.1292 | 12.6602 | 12.627 | 12.4156 | 12.8123 | 12.0758 | 12.7645 | 12.3299 | 12.1278 | NaN | NaN | NaN | 12.7118 | 94.2659 | NaN | NaN | NaN | -9.959 | NaN | 61.6742 | NaN | NaN | 577.2187 | NaN | 25.7833 | NaN | 28.3251
1064.1292 | 13.0281 | 12.6264 | 12.4134 | 12.7586 | 12.0165 | 12.7518 | 12.3296 | 12.135 | NaN | NaN | NaN | 12.715 | 91.1726 | NaN | NaN | NaN | NaN | NaN | 62.8682 | NaN | NaN | 579.2253 | NaN | 29.2536 | NaN | 27.8654
1065.1292 | 12.7572 | 12.5181 | 12.414 | 12.7816 | 12.0637 | 12.7104 | 12.292 | 12.1291 | NaN | NaN | NaN | 12.7493 | 92.6358 | NaN | NaN | NaN | -6.2314 | NaN | 61.5542 | NaN | NaN | 578.9388 | NaN | 27.5969 | NaN | 28.4043
1066.1292 | 12.633 | 12.5442 | 12.4091 | 12.8113 | 12.0788 | 12.6773 | 12.3208 | 12.1295 | NaN | NaN | NaN | 12.7384 | 92.0694 | NaN | NaN | NaN | 5.4841 | NaN | 62.4945 | NaN | NaN | 580.0131 | NaN | 26.2896 | NaN | 28.6874
1067.1292 | 12.6824 | 12.6489 | 12.4167 | 12.8142 | 12.0492 | 12.8346 | 12.3477 | 12.1359 | NaN | NaN | NaN | 12.7835 | 93.1254 | NaN | NaN | NaN | -18.352 | NaN | 61.301 | NaN | NaN | 580.6358 | NaN | 27.8504 | NaN | 28.2537
1068.1292 | 12.6138 | 12.5844 | 12.4188 | 12.8577 | 12.2055 | 12.7393 | 12.3185 | 12.1337 | NaN | NaN | NaN | 12.6997 | 91.7754 | NaN | NaN | NaN | 17.234 | NaN | 63.4548 | NaN | NaN | 581.0209 | NaN | 28.2515 | NaN | 27.5449
1069.1292 | 12.7113 | 12.597 | 12.4228 | 12.7711 | 12.1398 | 12.6297 | 12.3323 | 12.1284 | NaN | NaN | NaN | 12.7149 | 89.7286 | NaN | NaN | NaN | -2.4162 | NaN | 62.6549 | NaN | NaN | 580.5191 | NaN | 26.2882 | NaN | 27.767
1070.1292 | 12.6115 | 12.4509 | 12.4267 | 12.8025 | 12.0857 | 12.6129 | 12.283 | 12.1259 | NaN | NaN | NaN | 12.7492 | 91.9965 | NaN | NaN | NaN | -13.2426 | NaN | 61.0889 | NaN | NaN | 583.5844 | NaN | 28.3423 | NaN | 28.022
1071.1292 | 13.0402 | 12.4785 | 12.4274 | 12.7933 | 12.1909 | 12.6259 | 12.2997 | 12.1225 | NaN | NaN | NaN | 12.8326 | 91.506 | NaN | NaN | NaN | NaN | NaN | 61.6208 | NaN | NaN | 580.9394 | NaN | 26.028 | NaN | 27.911
1072.1292 | 12.6361 | 12.6823 | 12.4251 | 12.7684 | 12.1652 | 12.8062 | 12.3291 | 12.1271 | NaN | NaN | NaN | 12.7606 | 92.8637 | NaN | NaN | NaN | -12.7506 | NaN | 61.2399 | NaN | NaN | 579.2955 | NaN | 25.2231 | NaN | 27.0453
1073.1292 | 12.6237 | 12.8323 | 12.4246 | 12.8084 | 12.1758 | 12.8064 | 12.3871 | 12.1223 | NaN | NaN | NaN | 12.7494 | 92.2669 | NaN | NaN | NaN | 20.888 | NaN | 62.1433 | NaN | NaN | 580.1598 | NaN | 26.6978 | NaN | 28.0493
1074.1292 | 12.6055 | 12.5518 | 12.4274 | 12.8523 | 12.2456 | 12.7035 | 12.3145 | 12.1273 | NaN | NaN | NaN | 12.7816 | 92.1847 | NaN | NaN | NaN | -10.8512 | NaN | 60.4677 | NaN | NaN | 580.6075 | NaN | 27.6425 | NaN | 28.9251
1075.1292 | 12.6564 | 12.8711 | 12.4272 | 12.7192 | 11.9865 | 12.9102 | 12.4054 | 12.1326 | NaN | NaN | NaN | 12.7914 | 91.3766 | NaN | NaN | NaN | -17.4613 | NaN | 61.3231 | NaN | NaN | 580.5341 | NaN | 28.1911 | NaN | 26.9067
1076.1292 | 12.606 | 12.4821 | 12.432 | 12.7943 | 12.0098 | 12.6174 | 12.2976 | 12.1323 | NaN | NaN | NaN | 12.8436 | 91.9475 | NaN | NaN | NaN | NaN | NaN | 61.6797 | NaN | NaN | 584.2029 | NaN | 26.4113 | NaN | 27.4983
1077.1292 | 12.6608 | 12.7792 | 12.4286 | 12.7752 | 12.0279 | 12.8786 | 12.36 | 12.1277 | NaN | NaN | NaN | 12.7546 | 92.7419 | NaN | NaN | NaN | -19.34 | NaN | 62.8263 | NaN | NaN | 582.9539 | NaN | 25.9111 | NaN | 28.3022
1078.1292 | 12.6437 | 12.6896 | 12.4346 | 12.7726 | 12.1428 | 12.846 | 12.3562 | 12.1313 | NaN | NaN | NaN | 12.7255 | 92.62 | NaN | NaN | NaN | 36.6828 | NaN | 61.3231 | NaN | NaN | 582.9463 | NaN | 26.2624 | NaN | 28.9244
1079.1292 | 12.9565 | 12.7726 | 12.4374 | 12.7552 | 12.0537 | 12.8188 | 12.3753 | 12.1413 | NaN | NaN | NaN | 12.7653 | 91.2399 | NaN | NaN | NaN | -13.3965 | NaN | 62.1122 | NaN | NaN | 580.9733 | NaN | 25.9995 | NaN | 26.9625
1080.1292 | 12.6446 | 12.6688 | 12.4436 | 12.7735 | 12.0095 | 12.8202 | 12.3643 | 12.1415 | NaN | NaN | NaN | 12.7321 | 91.3498 | NaN | NaN | NaN | -15.2842 | NaN | 63.5086 | NaN | NaN | 582.8695 | NaN | 26.6823 | NaN | 28.2619
1081.1292 | 12.713 | 12.808 | 12.4538 | 12.8397 | 12.0488 | 12.8835 | 12.395 | 12.1441 | NaN | NaN | NaN | 12.7428 | 92.474 | NaN | NaN | NaN | 0.6592 | NaN | 61.4548 | NaN | NaN | 581.2381 | NaN | 26.6475 | NaN | 28.3605
1082.1292 | 12.6325 | 12.6195 | 12.4568 | 12.7664 | 12.1399 | 12.6997 | 12.3346 | 12.1462 | NaN | NaN | NaN | 12.7873 | 91.1877 | NaN | NaN | NaN | -10.7692 | NaN | 61.8743 | NaN | NaN | 579.6572 | NaN | 26.1333 | NaN | 27.8229
1083.1292 | 12.7308 | 12.5623 | 12.4563 | 12.9699 | 12.1368 | 12.705 | 12.3372 | 12.1509 | NaN | NaN | NaN | 12.799 | 91.6305 | NaN | NaN | NaN | 11.3779 | NaN | 62.7008 | NaN | NaN | 579.9412 | NaN | 26.9928 | NaN | 27.5449
1084.1292 | 12.6119 | 12.5714 | 12.4569 | 12.768 | 12.1904 | 12.7337 | 12.3321 | 12.1518 | NaN | NaN | NaN | 12.7915 | 92.452 | NaN | NaN | NaN | -0.2848 | NaN | 60.591 | NaN | NaN | 580.2681 | NaN | 27.4074 | NaN | 27.5052
1085.1292 | 12.7372 | 12.5422 | 12.4591 | 12.7759 | 12.2103 | 12.6982 | 12.3185 | 12.1494 | NaN | NaN | NaN | 12.7613 | 90.8912 | NaN | NaN | NaN | 0.0183 | NaN | 61.1638 | NaN | NaN | 582.466 | NaN | 27.3243 | NaN | 27.9609
1086.1292 | 12.6299 | 12.6541 | 12.454 | 12.7815 | 12.0753 | 12.78 | 12.3425 | 12.1548 | NaN | NaN | NaN | 12.8205 | 92.0375 | NaN | NaN | NaN | -19.5016 | NaN | 62.5455 | NaN | NaN | 580.9451 | NaN | 28.7005 | NaN | 27.5688
1087.1292 | 12.6237 | 12.5201 | 12.4459 | 12.7567 | 11.9984 | 12.6898 | 12.3222 | 12.1565 | NaN | NaN | NaN | 12.8229 | 91.4983 | NaN | NaN | NaN | -1.8824 | NaN | 62.5208 | NaN | NaN | 579.6859 | NaN | 25.9705 | NaN | 27.9801
1088.1292 | 12.6418 | 12.7738 | 12.4449 | 12.811 | 12.1972 | 12.878 | 12.3782 | 12.154 | NaN | NaN | NaN | 12.8043 | 88.712 | NaN | NaN | NaN | 0.5163 | NaN | 60.7231 | NaN | NaN | 579.5579 | NaN | 26.1916 | NaN | 27.2678
1089.1292 | 12.6387 | 12.4659 | 12.4401 | 12.8287 | 12.0996 | 12.6418 | 12.299 | 12.159 | NaN | NaN | NaN | 12.7876 | 91.6696 | NaN | NaN | NaN | -8.0105 | NaN | 60.5277 | NaN | NaN | 579.0283 | NaN | 25.9221 | NaN | 27.2892
1090.1292 | 12.6428 | 12.5218 | 12.4466 | 12.8187 | 12.1775 | 12.6931 | 12.3163 | 12.1603 | NaN | NaN | NaN | 12.8036 | 91.5627 | NaN | NaN | NaN | -15.5915 | NaN | 61.2924 | NaN | NaN | 579.3298 | NaN | 27.3258 | NaN | 26.1772
1091.1292 | 12.6377 | 12.4687 | 12.4451 | 12.7712 | 12.1389 | 12.6128 | 12.2918 | 12.1511 | NaN | NaN | NaN | 12.8164 | 92.3287 | NaN | NaN | NaN | -14.8439 | NaN | 61.5108 | NaN | NaN | 579.2215 | NaN | 25.5055 | NaN | 27.4348
1092.1292 | 12.6551 | 12.6178 | 12.4484 | 12.7246 | 12.1807 | 12.7923 | 12.3512 | 12.1621 | NaN | NaN | NaN | 12.8097 | 92.4859 | NaN | NaN | NaN | 8.4116 | NaN | 62.7322 | NaN | NaN | 580.586 | NaN | 26.3332 | NaN | 27.7084
1093.1292 | 12.6663 | 12.5369 | 12.4545 | 12.7649 | 12.1365 | 12.7018 | 12.3264 | 12.1544 | NaN | NaN | NaN | 12.8221 | 93.0586 | NaN | NaN | NaN | -17.8346 | NaN | 61.777 | NaN | NaN | 579.9951 | NaN | 26.6387 | NaN | 27.5887
1094.1292 | 12.7252 | 12.7892 | 12.4619 | 12.7794 | 12.12 | 12.8912 | 12.4032 | 12.1613 | NaN | NaN | NaN | 12.8688 | 91.0273 | NaN | NaN | NaN | -13.3831 | NaN | 62.8603 | NaN | NaN | 580.6679 | NaN | 26.8273 | NaN | 25.8504
1095.1292 | 13.1552 | 12.5155 | 12.462 | 12.8103 | 12.1989 | 12.7348 | 12.3389 | 12.1574 | NaN | NaN | NaN | 12.805 | 92.6037 | NaN | NaN | NaN | -1.5839 | NaN | 61.4713 | NaN | NaN | 580.8277 | NaN | 25.7426 | NaN | 24.821
1096.1292 | 12.6847 | 12.4592 | 12.4653 | 12.8055 | 12.1547 | 12.631 | 12.294 | 12.1525 | NaN | NaN | NaN | 12.7725 | 91.2712 | NaN | NaN | NaN | 4.9612 | NaN | 60.5361 | NaN | NaN | 582.395 | NaN | 25.0619 | NaN | 26.5748
1097.1292 | 12.67 | 12.6066 | 12.4704 | 13.1358 | 12.2206 | 12.7644 | 12.3441 | 12.1547 | NaN | NaN | NaN | 12.8668 | 92.3943 | NaN | NaN | NaN | -15.9524 | NaN | 61.9738 | NaN | NaN | 579.7356 | NaN | 26.902 | NaN | 26.0766
1098.1292 | 12.6328 | 12.631 | 12.4738 | 12.8035 | 12.1794 | 12.7452 | 12.3409 | 12.1629 | NaN | NaN | NaN | 12.8215 | 91.8091 | NaN | NaN | NaN | 28.4981 | NaN | 59.825 | NaN | NaN | 578.6834 | NaN | 26.5138 | NaN | 25.0857
1099.1292 | 12.6389 | 12.5777 | 12.4713 | 12.8105 | 12.1862 | 12.7284 | 12.3362 | 12.1683 | NaN | NaN | NaN | 12.7926 | 93.1033 | NaN | NaN | NaN | -16.7836 | NaN | 62.2593 | NaN | NaN | 582.6153 | NaN | 27.2932 | NaN | 28.6488
1100.1292 | 12.6271 | 12.7017 | 12.4846 | 12.8064 | 12.1513 | 12.8111 | 12.3798 | 12.1623 | NaN | NaN | NaN | 12.7624 | 91.8214 | NaN | NaN | NaN | -16.5536 | NaN | 61.6247 | NaN | NaN | 582.3817 | NaN | 26.8957 | NaN | 26.8325
1101.1292 | 12.6549 | 12.6961 | 12.4752 | 12.8158 | 12.0791 | 12.8112 | 12.3887 | 12.1691 | NaN | NaN | NaN | 12.8016 | 92.1426 | NaN | NaN | NaN | -11.1894 | NaN | 61.611 | NaN | NaN | 583.299 | NaN | 28.4546 | NaN | 29.3173
1102.1292 | 12.6119 | 12.8739 | 12.4727 | 12.8431 | 12.0744 | 12.9039 | 12.3796 | 12.1759 | NaN | NaN | NaN | 12.8578 | 91.1608 | NaN | NaN | NaN | -10.3451 | NaN | 61.3228 | NaN | NaN | 582.2016 | NaN | 24.5598 | NaN | 26.5924
1103.1292 | 12.62 | 12.7754 | 12.4789 | 12.8093 | 12.2207 | 12.8347 | 12.3798 | 12.1756 | NaN | NaN | NaN | 12.8082 | 93.7309 | NaN | NaN | NaN | 9.0415 | NaN | 61.0392 | NaN | NaN | 583.6999 | NaN | 25.2398 | NaN | 27.9698
1104.1292 | 12.7013 | 12.5232 | 12.4779 | 12.9759 | 12.108 | 12.7129 | 12.3497 | 12.1689 | NaN | NaN | NaN | 12.8093 | 90.9735 | NaN | NaN | NaN | 4.2626 | NaN | 60.3434 | NaN | NaN | 584.7699 | NaN | 26.339 | NaN | 26.8143
1105.1292 | 12.683 | 12.6406 | 12.4824 | 12.944 | 12.1012 | 12.7268 | 12.3569 | 12.1649 | NaN | NaN | NaN | 12.7595 | 91.1465 | NaN | NaN | NaN | -12.2766 | NaN | 60.9613 | NaN | NaN | 581.2552 | NaN | 27.0948 | NaN | 28.7826
1106.1292 | 12.6315 | 12.8 | 12.4844 | 12.7788 | 12.1729 | 12.8195 | 12.4209 | 12.1719 | NaN | NaN | NaN | 12.7902 | 91.2917 | NaN | NaN | NaN | -16.4224 | NaN | 61.7578 | NaN | NaN | 582.6206 | NaN | 26.8749 | NaN | 28.6328
1107.1292 | 12.6416 | 12.6086 | 12.4876 | 12.823 | 12.1751 | 12.7831 | 12.3816 | 12.1693 | NaN | NaN | NaN | 12.7952 | 90.7715 | NaN | NaN | NaN | -15.8536 | NaN | 62.2972 | NaN | NaN | 585.3916 | NaN | 27.2383 | NaN | 27.0455
1108.1292 | 12.8235 | 12.6091 | 12.4838 | 12.8256 | 12.0665 | 12.6862 | 12.3556 | 12.1746 | NaN | NaN | NaN | 12.779 | 90.6375 | NaN | NaN | NaN | -18.7213 | NaN | 61.3455 | NaN | NaN | 582.5018 | NaN | 24.6563 | NaN | 28.291
1109.1292 | 12.6674 | 12.5904 | 12.4845 | 12.8576 | 12.1765 | 12.7 | 12.3375 | 12.1777 | NaN | NaN | NaN | 12.8938 | 92.3921 | NaN | NaN | NaN | -15.8123 | NaN | 61.7206 | NaN | NaN | 586.5796 | NaN | 27.4759 | NaN | 28.046
1110.1292 | 12.6975 | 12.5757 | 12.4808 | 12.8057 | 12.2031 | 12.7402 | 12.3655 | 12.1782 | NaN | NaN | NaN | 12.8781 | 93.2004 | NaN | NaN | NaN | -4.2725 | NaN | 60.8739 | NaN | NaN | 587.2302 | NaN | 26.8004 | NaN | 28.4201
1111.1292 | 12.7597 | 12.6156 | 12.4823 | 12.8382 | 12.1313 | 12.7572 | 12.3627 | 12.181 | NaN | NaN | NaN | 12.867 | 91.4953 | NaN | NaN | NaN | 3.7511 | NaN | 61.8545 | NaN | NaN | 590.1054 | NaN | 25.9086 | NaN | 28.2652
1112.1292 | 12.6509 | 12.4425 | 12.4857 | 12.8144 | 12.1832 | 12.5587 | 12.3012 | 12.177 | NaN | NaN | NaN | 12.837 | 90.0716 | NaN | NaN | NaN | 4.7807 | NaN | 61.1871 | NaN | NaN | 590.191 | NaN | 27.9105 | NaN | 27.5004
1113.1292 | 12.6819 | 12.646 | 12.4766 | 12.7972 | 12.1399 | 12.7284 | 12.3639 | 12.1791 | NaN | NaN | NaN | 12.8921 | 91.6119 | NaN | NaN | NaN | -14.738 | NaN | 61.8051 | NaN | NaN | 588.8781 | NaN | 28.1154 | NaN | 27.8837
1114.1292 | 12.7765 | 12.5581 | 12.4786 | 12.8212 | 12.0162 | 12.6915 | 12.3428 | 12.174 | NaN | NaN | NaN | 12.8011 | 91.7758 | NaN | NaN | NaN | -17.4927 | NaN | 61.5746 | NaN | NaN | 591.4457 | NaN | 26.2937 | NaN | 28.8236
1115.1292 | 12.703 | 12.7159 | 12.4836 | 12.7913 | 12.1682 | 12.7862 | 12.3728 | 12.1741 | NaN | NaN | NaN | 12.7919 | 91.2881 | NaN | NaN | NaN | -2.1034 | NaN | 61.7703 | NaN | NaN | 588.622 | NaN | 25.2059 | NaN | 27.7123
1116.1292 | 12.7738 | 12.7278 | 12.4809 | 12.8223 | 12.0598 | 12.8353 | 12.3802 | 12.1698 | NaN | NaN | NaN | 12.8389 | 91.4937 | NaN | NaN | NaN | -12.2111 | NaN | 60.872 | NaN | NaN | 590.9444 | NaN | 25.9367 | NaN | 27.2268
1117.1292 | 13.302 | 12.5605 | 12.4822 | 12.8481 | 12.1723 | 12.6975 | 12.3187 | 12.1673 | NaN | NaN | NaN | 12.7896 | 90.077 | NaN | NaN | NaN | -1.0506 | NaN | 61.1626 | NaN | NaN | 590.905 | NaN | 27.6125 | NaN | 27.0881
1118.1292 | 12.7572 | 12.5748 | 12.4829 | 12.8612 | 12.0689 | 12.6999 | 12.3252 | 12.1711 | NaN | NaN | NaN | 12.8295 | 91.0242 | NaN | NaN | NaN | 33.1171 | NaN | 61.039 | NaN | NaN | 590.4245 | NaN | 25.4642 | NaN | 26.1997
1119.1292 | 12.6144 | 12.7731 | 12.4816 | 12.8561 | 12.1925 | 12.8541 | 12.3394 | 12.1717 | NaN | NaN | NaN | 12.873 | 90.7731 | NaN | NaN | NaN | -13.3872 | NaN | 61.9418 | NaN | NaN | 588.9061 | NaN | 26.1617 | NaN | 26.1554
1120.1292 | 12.6534 | 12.6069 | 12.4831 | 12.86 | 12.2221 | 12.7063 | 12.3339 | 12.1711 | NaN | NaN | NaN | 12.8535 | 92.2449 | NaN | NaN | NaN | -6.9917 | NaN | 61.4822 | NaN | NaN | 590.9182 | NaN | 25.2926 | NaN | 26.5403
1121.1292 | 12.7071 | 12.6397 | 12.4885 | 12.8797 | 12.1396 | 12.7815 | 12.346 | 12.1669 | NaN | NaN | NaN | 12.877 | 91.5097 | NaN | NaN | NaN | 0.7051 | NaN | 62.1639 | NaN | NaN | 590.4429 | NaN | 26.0476 | NaN | 28.4011
1122.1292 | 12.778 | 12.6051 | 12.4875 | 12.8054 | 12.2095 | 12.7376 | 12.3235 | 12.158 | NaN | NaN | NaN | 12.8774 | 93.4214 | NaN | NaN | NaN | -15.1883 | NaN | 61.3637 | NaN | NaN | 588.1194 | NaN | 27.3916 | NaN | 27.951
1123.1292 | 13.2587 | 12.5615 | 12.4921 | 12.8547 | 12.2514 | 12.6811 | 12.3157 | 12.1643 | NaN | NaN | NaN | 12.8746 | 91.4056 | NaN | NaN | NaN | -13.8 | NaN | 60.8625 | NaN | NaN | 588.9895 | NaN | 27.0187 | NaN | 28.6859
1124.1292 | 12.7334 | 12.4959 | 12.4966 | 12.8396 | 12.1287 | 12.6243 | 12.3056 | 12.1638 | NaN | NaN | NaN | 12.9113 | 92.2137 | NaN | NaN | NaN | 0.3348 | NaN | 61.9815 | NaN | NaN | 589.052 | NaN | 29.1011 | NaN | 26.9313
1125.1292 | 12.675 | 12.6855 | 12.4995 | 12.8458 | 12.0938 | 12.762 | 12.3512 | 12.1592 | NaN | NaN | NaN | 12.9142 | 91.9705 | NaN | NaN | NaN | -18.9594 | NaN | 61.4961 | NaN | NaN | 590.3781 | NaN | 26.2074 | NaN | 27.6408
1126.1292 | 12.7692 | 12.7294 | 12.5028 | 12.8737 | 12.1834 | 12.819 | 12.3591 | 12.1564 | NaN | NaN | NaN | 12.9567 | 91.8585 | NaN | NaN | NaN | 5.4312 | NaN | 63.13 | NaN | NaN | 589.0394 | NaN | 27.659 | NaN | 25.8295
1127.1292 | 12.7211 | 12.7156 | 12.5038 | 12.7669 | 12.2989 | 12.7885 | 12.3389 | 12.1643 | NaN | NaN | NaN | 12.9207 | 92.5656 | NaN | NaN | NaN | -11.3623 | NaN | 61.1609 | NaN | NaN | 589.8535 | NaN | 26.0113 | NaN | 26.8112
1128.1292 | 12.9274 | 12.651 | 12.5076 | 13.0228 | 12.2485 | 12.7639 | 12.3319 | 12.1631 | NaN | NaN | NaN | 12.8761 | 91.2025 | NaN | NaN | NaN | -14.7415 | NaN | 61.1068 | NaN | NaN | 586.4511 | NaN | 25.0764 | NaN | 26.8349
1129.1292 | 12.6446 | 12.6924 | 12.5075 | 12.8308 | 12.2991 | 12.7393 | 12.314 | 12.1626 | NaN | NaN | NaN | 12.8903 | 91.3425 | NaN | NaN | NaN | -3.5639 | NaN | 62.8523 | NaN | NaN | 590.1228 | NaN | 26.2876 | NaN | 28.6301
1130.1292 | 12.7508 | 12.6692 | 12.5061 | 12.8162 | 12.195 | 12.7328 | 12.3213 | 12.1573 | NaN | NaN | NaN | 12.8765 | 91.2654 | NaN | NaN | NaN | -10.6625 | NaN | 61.1559 | NaN | NaN | 589.6243 | NaN | 25.0952 | NaN | 26.0574
1131.1292 | 12.7296 | 12.5829 | 12.5106 | 12.8455 | 12.1704 | 12.7305 | 12.3195 | 12.1568 | NaN | NaN | NaN | 12.8345 | 91.728 | NaN | NaN | NaN | 5.5697 | NaN | 61.3076 | NaN | NaN | 585.9687 | NaN | 25.6486 | NaN | 27.5135
1132.1292 | 12.7422 | 12.9431 | 12.5197 | 12.8079 | 12.1022 | 12.9567 | 12.3789 | 12.1625 | NaN | NaN | NaN | 12.8431 | 90.5813 | NaN | NaN | NaN | 18.4235 | NaN | 63.0241 | NaN | NaN | 590.7374 | NaN | 26.4087 | NaN | 25.7737
1133.1292 | 12.7075 | 12.6337 | 12.517 | 12.8526 | 12.0188 | 12.7459 | 12.313 | 12.1599 | NaN | NaN | NaN | 12.879 | 91.8193 | NaN | NaN | NaN | 11.448 | NaN | 61.689 | NaN | NaN | 588.9636 | NaN | 26.7568 | NaN | 28.4603
1134.1292 | 12.8214 | 12.8593 | 12.5178 | 12.8639 | 12.1472 | 12.9235 | 12.3571 | 12.1682 | NaN | NaN | NaN | 12.8199 | 90.5884 | NaN | NaN | NaN | -8.8172 | NaN | 59.025 | NaN | NaN | 587.688 | NaN | 26.4181 | NaN | 27.5321
1135.1292 | 12.7267 | 12.705 | 12.5161 | 12.9283 | 12.2375 | 12.8419 | 12.3586 | 12.1625 | NaN | NaN | NaN | 12.8636 | 91.2611 | NaN | NaN | NaN | -2.2848 | NaN | 62.3102 | NaN | NaN | 588.2223 | NaN | 25.2585 | NaN | 26.8592
1136.1292 | 12.72 | 12.5502 | 12.5163 | 12.7859 | 12.0737 | 12.6868 | 12.2937 | 12.1597 | NaN | NaN | NaN | 12.8097 | 91.2468 | NaN | NaN | NaN | -15.9895 | NaN | 61.6215 | NaN | NaN | 589.4778 | NaN | 26.762 | NaN | 27.6454
1137.1292 | 12.7305 | 12.5877 | 12.5276 | 12.8312 | 12.2265 | 12.7038 | 12.3068 | 12.1592 | NaN | NaN | NaN | 12.8107 | 94.0621 | NaN | NaN | NaN | -16.2773 | NaN | 61.2187 | NaN | NaN | 590.6973 | NaN | 24.2747 | NaN | 29.4575
1138.1292 | 12.7159 | 12.8607 | 12.5277 | 12.8579 | 12.2078 | 12.9397 | 12.3917 | 12.1544 | NaN | NaN | NaN | 12.8182 | 93.2844 | NaN | NaN | NaN | 6.3785 | NaN | 61.209 | NaN | NaN | 591.315 | NaN | 28.6094 | NaN | 28.4831
1139.1292 | 12.7152 | 12.663 | 12.5254 | 12.7902 | 12.1141 | 12.8364 | 12.3535 | 12.1472 | NaN | NaN | NaN | 12.8545 | 91.8127 | NaN | NaN | NaN | -5.104 | NaN | 62.4354 | NaN | NaN | 588.7776 | NaN | 26.4327 | NaN | 25.2881
1140.1292 | 12.8097 | 12.5517 | 12.528 | 12.8634 | 12.2141 | 12.7018 | 12.2982 | 12.1537 | NaN | NaN | NaN | 12.8431 | 91.6298 | NaN | NaN | NaN | -13.7446 | NaN | 60.1842 | NaN | NaN | 587.208 | NaN | 26.3468 | NaN | 26.9457
1141.1292 | 12.9699 | 12.6336 | 12.5382 | 12.8032 | 12.2562 | 12.7559 | 12.3451 | 12.1469 | NaN | NaN | NaN | 12.8105 | 91.1925 | NaN | NaN | NaN | NaN | NaN | 62.1261 | NaN | NaN | 588.7157 | NaN | 27.8528 | NaN | 27.8696
1142.1292 | 12.7391 | 12.6333 | 12.5321 | 12.9278 | 12.1683 | 12.7844 | 12.3391 | 12.1511 | NaN | NaN | NaN | 12.824 | 93.4389 | NaN | NaN | NaN | -12.4793 | NaN | 60.6258 | NaN | NaN | 587.122 | NaN | 25.859 | NaN | 26.9815
1143.1448 | 12.7133 | 12.571 | 12.5332 | 13.094 | 12.2191 | 12.7426 | 12.3111 | 12.1494 | NaN | NaN | NaN | 12.8815 | 92.0841 | NaN | NaN | NaN | -1.5483 | NaN | 60.4483 | NaN | NaN | 586.3588 | NaN | 25.9137 | NaN | 27.2703
1144.1292 | 12.8088 | 12.5491 | 12.5379 | 12.8797 | 12.2197 | 12.721 | 12.3071 | 12.1528 | NaN | NaN | NaN | 12.8331 | 92.0845 | NaN | NaN | NaN | -16.2691 | NaN | 59.337 | NaN | NaN | 585.3777 | NaN | 26.6406 | NaN | 26.0402
1145.1292 | 12.6707 | 12.5527 | 12.5431 | 12.8763 | 12.2719 | 12.6685 | 12.3166 | 12.1552 | NaN | NaN | NaN | 12.8794 | 92.7547 | NaN | NaN | NaN | -7.1002 | NaN | 59.8573 | NaN | NaN | 588.8657 | NaN | 24.5875 | NaN | 28.8286
1146.1292 | 12.9306 | 12.8094 | 12.5501 | 12.9888 | 12.1942 | 12.9416 | 12.3881 | 12.1527 | NaN | NaN | NaN | 12.8726 | 91.4331 | NaN | NaN | NaN | -8.2584 | NaN | 62.8164 | NaN | NaN | 590.2297 | NaN | 26.6393 | NaN | 27.1979
1147.1292 | 12.676 | 12.7822 | 12.5432 | 12.8931 | 12.1648 | 12.9196 | 12.3788 | 12.161 | NaN | NaN | NaN | 12.8201 | 92.1232 | NaN | NaN | NaN | 0.7397 | NaN | 60.9488 | NaN | NaN | 588.6809 | NaN | 27.1572 | NaN | 27.9467
1148.1292 | 12.7003 | 12.6467 | 12.5467 | 12.9014 | 12.1295 | 12.7628 | 12.3293 | 12.1586 | NaN | NaN | NaN | 12.8179 | 92.5371 | NaN | NaN | NaN | -17.8753 | NaN | 60.4185 | NaN | NaN | 589.9954 | NaN | 26.2483 | NaN | 26.9139
1149.1292 | 12.6833 | 12.6251 | 12.5438 | 12.8944 | 12.1296 | 12.8025 | 12.3579 | 12.1525 | NaN | NaN | NaN | 12.8271 | 92.7238 | NaN | NaN | NaN | NaN | NaN | 58.795 | NaN | NaN | 590.0475 | NaN | 25.6215 | NaN | 28.0462
1150.1292 | 12.7356 | 12.6676 | 12.5486 | 13.0366 | 12.1927 | 12.8214 | 12.3572 | 12.1552 | NaN | NaN | NaN | 12.8708 | 95.5868 | NaN | NaN | NaN | -0.9505 | NaN | 61.3396 | NaN | NaN | 588.6757 | NaN | 28.0183 | NaN | 28.3898
1151.1292 | 12.7387 | 12.7635 | 12.5495 | 12.8923 | 12.2034 | 12.8983 | 12.3696 | 12.1569 | NaN | NaN | NaN | 12.955 | 92.2508 | NaN | NaN | NaN | -5.6319 | NaN | 61.2826 | NaN | NaN | 589.2788 | NaN | 27.088 | NaN | 28.7267
1152.1292 | 12.7297 | 12.6632 | 12.5539 | 13.216 | 12.2226 | 12.7187 | 12.3418 | 12.1522 | NaN | NaN | NaN | 12.8714 | 91.7498 | NaN | NaN | NaN | NaN | NaN | 60.6009 | NaN | NaN | 590.0223 | NaN | 25.4651 | NaN | 27.3419
1153.1448 | 12.6845 | 12.7261 | 12.5529 | 12.8859 | 12.208 | 12.8269 | 12.3403 | 12.1511 | NaN | NaN | NaN | 12.8548 | 91.3265 | NaN | NaN | NaN | -3.448 | NaN | 59.5708 | NaN | NaN | 590.2661 | NaN | 27.1303 | NaN | 26.0662
1154.1292 | 12.7234 | 12.5882 | 12.5527 | 12.9219 | 12.2311 | 12.7723 | 12.352 | 12.154 | NaN | NaN | NaN | 12.8804 | 91.6987 | NaN | NaN | NaN | -18.5782 | NaN | 59.4683 | NaN | NaN | 590.1531 | NaN | 25.915 | NaN | 26.0421
1155.1292 | 12.7264 | 12.5912 | 12.5547 | 12.9547 | 12.1771 | 12.7696 | 12.334 | 12.151 | NaN | NaN | NaN | 12.8461 | 92.7611 | NaN | NaN | NaN | -1.7481 | NaN | 60.1517 | NaN | NaN | 592.4764 | NaN | 26.0459 | NaN | 27.7587
1156.1292 | 12.7507 | 12.5583 | 12.5592 | 12.8676 | 12.241 | 12.7333 | 12.327 | 12.1498 | NaN | NaN | NaN | 12.8788 | 92.2344 | NaN | NaN | NaN | -17.7364 | NaN | 59.9165 | NaN | NaN | 592.2585 | NaN | 25.9581 | NaN | 26.91
1157.1292 | 12.7312 | 12.7086 | 12.5583 | 12.855 | 12.0732 | 12.824 | 12.3607 | 12.1429 | NaN | NaN | NaN | 12.9714 | 92.858 | NaN | NaN | NaN | 10.3622 | NaN | 61.4788 | NaN | NaN | 591.9348 | NaN | 26.9191 | NaN | 28.4057
1158.1292 | 12.8951 | 12.6048 | 12.5595 | 12.877 | 12.1881 | 12.7775 | 12.338 | 12.1465 | NaN | NaN | NaN | 12.8123 | 91.3685 | NaN | NaN | NaN | -18.7614 | NaN | 59.336 | NaN | NaN | 589.2218 | NaN | 26.5323 | NaN | 29.2342
1159.1292 | 12.7172 | 12.7785 | 12.5652 | 12.8782 | 12.0566 | 12.8605 | 12.3662 | 12.1425 | NaN | NaN | NaN | 12.8273 | 91.4424 | NaN | NaN | NaN | NaN | NaN | 62.7861 | NaN | NaN | 589.6676 | NaN | 26.8354 | NaN | 27.923
1160.1292 | 12.6931 | 12.6328 | 12.5629 | 12.8716 | 12.2552 | 12.7513 | 12.3388 | 12.1471 | NaN | NaN | NaN | 12.9445 | 94.8925 | NaN | NaN | NaN | -16.6853 | NaN | 60.5734 | NaN | NaN | 586.8117 | NaN | 25.5493 | NaN | 26.567
1161.1292 | 12.751 | 12.6626 | 12.57 | 12.8596 | 12.1597 | 12.8285 | 12.3478 | 12.1401 | NaN | NaN | NaN | 12.8729 | 93.953 | NaN | NaN | NaN | -8.9607 | NaN | 60.3244 | NaN | NaN | 589.5941 | NaN | 24.456 | NaN | 26.8153
1162.1292 | 12.7673 | 12.6051 | 12.5674 | 12.8315 | 12.1368 | 12.7701 | 12.3448 | 12.1468 | NaN | NaN | NaN | 12.8968 | 91.9917 | NaN | NaN | NaN | 5.9209 | NaN | 59.485 | NaN | NaN | 590.8237 | NaN | 26.8357 | NaN | 28.9452
1163.1292 | 12.7702 | 12.7905 | 12.5701 | 12.8699 | 12.2528 | 12.9193 | 12.414 | 12.1478 | NaN | NaN | NaN | 12.8315 | 89.445 | NaN | NaN | NaN | -0.9959 | NaN | 60.992 | NaN | NaN | 591.4956 | NaN | 26.0564 | NaN | 28.3008
1164.1292 | 12.7738 | 12.7905 | 12.5689 | 12.8378 | 12.2727 | 12.9334 | 12.4281 | 12.1514 | NaN | NaN | NaN | 12.8907 | 92.0795 | NaN | NaN | NaN | -15.4144 | NaN | 59.919 | NaN | NaN | 591.1219 | NaN | 26.0286 | NaN | 25.3966
1165.1292 | 12.8569 | 12.6184 | 12.5685 | 12.8247 | 12.2513 | 12.761 | 12.3488 | 12.1496 | NaN | NaN | NaN | 12.8337 | 91.2866 | NaN | NaN | NaN | 4.9863 | NaN | 60.4262 | NaN | NaN | 590.7407 | NaN | 26.9795 | NaN | 27.3744
1166.1292 | 12.7382 | 12.6111 | 12.5744 | 12.8372 | 12.2419 | 12.7885 | 12.3517 | 12.1471 | NaN | NaN | NaN | 12.8463 | 91.5206 | NaN | NaN | NaN | -16.1981 | NaN | 59.4257 | NaN | NaN | 590.9412 | NaN | 25.8227 | NaN | 28.3484
1167.1292 | 12.811 | 12.6097 | 12.5768 | 12.8578 | 12.1515 | 12.7786 | 12.3558 | 12.1476 | NaN | NaN | NaN | 12.8585 | 93.5693 | NaN | NaN | NaN | -14.8873 | NaN | 60.5234 | NaN | NaN | 589.3273 | NaN | 25.9271 | NaN | 28.0027
1168.1292 | 12.9079 | 12.895 | 12.5679 | 12.8699 | 12.256 | 12.9141 | 12.3782 | 12.1519 | NaN | NaN | NaN | 12.8203 | 91.6677 | NaN | NaN | NaN | -11.7509 | NaN | 60.7417 | NaN | NaN | 590.4188 | NaN | 26.9735 | NaN | 27.1858
1169.1292 | 12.7673 | 12.6743 | 12.5727 | 12.812 | 12.1796 | 12.8539 | 12.3787 | 12.1528 | NaN | NaN | NaN | 12.8269 | 90.9146 | NaN | NaN | NaN | 1.7295 | NaN | 61.2149 | NaN | NaN | 590.4183 | NaN | 25.1478 | NaN | 26.959
1170.1292 | 12.7373 | 12.7535 | 12.5808 | 12.9012 | 12.1521 | 12.9086 | 12.3897 | 12.1469 | NaN | NaN | NaN | 12.9319 | 92.4112 | NaN | NaN | NaN | -5.4056 | NaN | 61.2866 | NaN | NaN | 591.368 | NaN | 26.8959 | NaN | 27.0455
1171.1292 | 12.763 | 12.6068 | 12.5758 | 13.1556 | 12.081 | 12.7954 | 12.3603 | 12.1468 | NaN | NaN | NaN | 12.8918 | 91.4013 | NaN | NaN | NaN | -18.878 | NaN | 60.8784 | NaN | NaN | 591.8064 | NaN | 25.5249 | NaN | 28.2172
1172.1292 | 12.7476 | 12.594 | 12.5771 | 12.8536 | 12.2448 | 12.776 | 12.3633 | 12.1503 | NaN | NaN | NaN | 12.9881 | 91.8157 | NaN | NaN | NaN | -18.3574 | NaN | 60.6179 | NaN | NaN | 591.6449 | NaN | 27.1936 | NaN | 28.2915
1173.1292 | 12.7474 | 13.1175 | 12.5768 | 12.8385 | 12.1391 | 13.1103 | 12.4401 | 12.1493 | NaN | NaN | NaN | 12.9544 | 91.446 | NaN | NaN | NaN | 19.221 | NaN | 61.8096 | NaN | NaN | 591.4835 | NaN | 25.1731 | NaN | 26.1468
1174.1292 | 12.9019 | 12.7978 | 12.5751 | 12.8456 | 12.2628 | 12.8267 | 12.3768 | 12.1518 | NaN | NaN | NaN | 12.951 | 91.0422 | NaN | NaN | NaN | -0.16 | NaN | 61.7548 | NaN | NaN | 591.9981 | NaN | 24.958 | NaN | 27.6368
1175.1292 | 12.7522 | 13.2017 | 12.5771 | 12.9189 | 12.1095 | 13.1384 | 12.4871 | 12.1527 | NaN | NaN | NaN | 12.9866 | 92.2606 | NaN | NaN | NaN | NaN | NaN | 60.4586 | NaN | NaN | 592.0193 | NaN | 27.1254 | NaN | 28.0743
1176.1292 | 12.7596 | 12.595 | 12.5735 | 12.886 | 12.2136 | 12.8073 | 12.3643 | 12.1546 | NaN | NaN | NaN | 12.9046 | 92.0609 | NaN | NaN | NaN | -4.5646 | NaN | 61.0031 | NaN | NaN | 591.6541 | NaN | 26.2382 | NaN | 26.7395
1177.1292 | 12.7688 | 12.5775 | 12.5698 | 13.2145 | 12.2056 | 12.758 | 12.3665 | 12.1478 | NaN | NaN | NaN | 12.9667 | 92.1965 | NaN | NaN | NaN | NaN | NaN | 62.9123 | NaN | NaN | 591.9493 | NaN | 24.2391 | NaN | 28.0969
1178.1292 | 12.7474 | 12.5447 | 12.5693 | 12.9748 | 12.1783 | 12.7419 | 12.3457 | 12.1515 | NaN | NaN | NaN | 12.9442 | 90.8642 | NaN | NaN | NaN | NaN | NaN | 59.8193 | NaN | NaN | 592.6396 | NaN | 25.3943 | NaN | 28.3791
1179.1292 | 12.761 | 12.8757 | 12.568 | 12.8572 | 12.2556 | 12.9624 | 12.416 | 12.1529 | NaN | NaN | NaN | 12.9115 | 89.5164 | NaN | NaN | NaN | 9.7865 | NaN | 63.2732 | NaN | NaN | 591.4062 | NaN | 27.8891 | NaN | 27.7342
1180.1292 | 12.7536 | 12.6547 | 12.5688 | 12.8407 | 12.1866 | 12.7796 | 12.3648 | 12.1506 | NaN | NaN | NaN | 12.9397 | 90.6471 | NaN | NaN | NaN | -2.8819 | NaN | 60.5618 | NaN | NaN | 590.8902 | NaN | 26.3079 | NaN | 25.8655
1181.1292 | 12.7375 | 12.7812 | 12.572 | 12.883 | 12.281 | 12.8456 | 12.3947 | 12.1516 | NaN | NaN | NaN | 12.903 | 91.8816 | NaN | NaN | NaN | 22.5423 | NaN | 59.17 | NaN | NaN | 594.1467 | NaN | 24.2781 | NaN | 27.5239
1182.1292 | 12.7393 | 12.6441 | 12.5721 | 12.9595 | 12.2747 | 12.8197 | 12.374 | 12.1467 | NaN | NaN | NaN | 12.9983 | 91.1647 | NaN | NaN | NaN | -17.9561 | NaN | 60.5393 | NaN | NaN | 592.2105 | NaN | 26.3789 | NaN | 24.836
1183.1292 | 12.7713 | 12.5466 | 12.5809 | 12.8739 | 12.1897 | 12.7016 | 12.3404 | 12.1527 | NaN | NaN | NaN | 12.9566 | 91.7025 | NaN | NaN | NaN | -18.4256 | NaN | 60.549 | NaN | NaN | 590.6197 | NaN | 26.2005 | NaN | 27.8902
1184.1292 | 12.7625 | 12.5915 | 12.5774 | 12.8265 | 12.223 | 12.7828 | 12.3725 | 12.1487 | NaN | NaN | NaN | 12.9207 | 92.4595 | NaN | NaN | NaN | 2.0575 | NaN | 62.048 | NaN | NaN | 592.0055 | NaN | 27.0623 | NaN | 27.9242
1185.1292 | 12.7527 | 12.7155 | 12.5821 | 12.8626 | 12.2606 | 12.8066 | 12.4005 | 12.1501 | NaN | NaN | NaN | 12.9521 | 91.4049 | NaN | NaN | NaN | -17.5489 | NaN | 61.0932 | NaN | NaN | 590.5937 | NaN | 25.6306 | NaN | 24.9014
1186.1292 | 12.7937 | 12.9763 | 12.5864 | 12.8655 | 12.2133 | 13.0084 | 12.4394 | 12.1493 | NaN | NaN | NaN | 12.9167 | 92.8087 | NaN | NaN | NaN | -14.4962 | NaN | 61.1143 | NaN | NaN | 591.7781 | NaN | 26.338 | NaN | 28.2467
1187.1292 | 12.816 | 12.8601 | 12.587 | 13.085 | 12.1757 | 12.9896 | 12.4636 | 12.1506 | NaN | NaN | NaN | 12.9443 | 91.5604 | NaN | NaN | NaN | -11.5762 | NaN | 61.2893 | NaN | NaN | 591.9864 | NaN | 24.2471 | NaN | 27.0787
1188.1292 | 12.7727 | 12.6639 | 12.5912 | 13.0081 | 12.2859 | 12.8051 | 12.3915 | 12.1515 | NaN | NaN | NaN | 13.0012 | 92.412 | NaN | NaN | NaN | 33.0474 | NaN | 60.8608 | NaN | NaN | 592.5975 | NaN | 24.5545 | NaN | 27.9959
1189.1292 | 12.7269 | 12.5669 | 12.5884 | 12.8016 | 12.3062 | 12.7598 | 12.3658 | 12.1499 | NaN | NaN | NaN | 12.9285 | 91.7194 | NaN | NaN | NaN | -11.3834 | NaN | 60.6182 | NaN | NaN | 592.5894 | NaN | 27.2818 | NaN | 27.7826
1190.1292 | 12.806 | 12.7891 | 12.5875 | 12.884 | 12.1185 | 12.8797 | 12.3952 | 12.1447 | NaN | NaN | NaN | 12.9181 | 91.7374 | NaN | NaN | NaN | -19.3549 | NaN | 60.3011 | NaN | NaN | 594.1873 | NaN | 27.4267 | NaN | 26.5423
1191.1292 | 12.7511 | 12.9309 | 12.5819 | 12.8613 | 12.2788 | 13.0092 | 12.4929 | 12.1392 | NaN | NaN | NaN | 12.9462 | 94.1163 | NaN | NaN | NaN | -5.151 | NaN | 61.2125 | NaN | NaN | 592.4859 | NaN | 26.0502 | NaN | 26.6623
1192.1292 | 12.7604 | 12.5863 | 12.5844 | 12.889 | 12.2648 | 12.8112 | 12.3699 | 12.1335 | NaN | NaN | NaN | 12.9197 | 92.2274 | NaN | NaN | NaN | -12.1768 | NaN | 60.5226 | NaN | NaN | 594.7086 | NaN | 25.1499 | NaN | 25.7719
1193.1292 | 12.6894 | 13.1551 | 12.5863 | 13.08 | 12.167 | 13.145 | 12.5336 | 12.1361 | NaN | NaN | NaN | 12.8912 | 91.6141 | NaN | NaN | NaN | -18.0126 | NaN | 61.7268 | NaN | NaN | 593.2114 | NaN | 25.486 | NaN | 27.7412
1194.1292 | 12.9363 | 12.6589 | 12.5899 | 12.8306 | 12.1775 | 12.7941 | 12.368 | 12.1343 | NaN | NaN | NaN | 12.869 | 94.5903 | NaN | NaN | NaN | -15.4543 | NaN | 60.1046 | NaN | NaN | 591.6924 | NaN | 26.4161 | NaN | 27.7174
1195.1292 | 12.7578 | 12.519 | 12.5858 | 12.8723 | 12.2982 | 12.6812 | 12.3279 | 12.1382 | NaN | NaN | NaN | 12.8563 | 90.8587 | NaN | NaN | NaN | 26.7131 | NaN | 59.7688 | NaN | NaN | 590.8253 | NaN | 26.0712 | NaN | 28.0464
1196.1292 | 13.1095 | 12.6739 | 12.5906 | 12.942 | 12.1777 | 12.8265 | 12.374 | 12.1412 | NaN | NaN | NaN | 12.9179 | 92.788 | NaN | NaN | NaN | 9.7419 | NaN | 61.114 | NaN | NaN | 592.5797 | NaN | 27.426 | NaN | 26.8151
1197.1292 | 12.733 | 12.8933 | 12.5918 | 12.8681 | 12.1283 | 13.0236 | 12.4422 | 12.1455 | NaN | NaN | NaN | 12.9112 | 91.6696 | NaN | NaN | NaN | 4.6183 | NaN | 60.6664 | NaN | NaN | 591.575 | NaN | 26.0725 | NaN | 27.6592
1198.1292 | 12.7205 | 12.519 | 12.5939 | 12.9109 | 12.3215 | 12.6933 | 12.3374 | 12.1468 | NaN | NaN | NaN | 12.8632 | 92.1781 | NaN | NaN | NaN | -6.7982 | NaN | 60.7933 | NaN | NaN | 590.4712 | NaN | 24.6364 | NaN | 26.5104
1199.1292 | 12.7253 | 12.6576 | 12.5937 | 12.9002 | 12.3085 | 12.8472 | 12.4021 | 12.1483 | NaN | NaN | NaN | 12.8665 | 91.4747 | NaN | NaN | NaN | 9.7261 | NaN | 60.6663 | NaN | NaN | 589.6081 | NaN | 25.2394 | NaN | 28.2473
1200.1292 | 12.7225 | 12.5622 | 12.5922 | 12.8816 | 12.2877 | 12.7368 | 12.351 | 12.1454 | NaN | NaN | NaN | 12.8682 | 89.8666 | NaN | NaN | NaN | -14.5518 | NaN | 60.0247 | NaN | NaN | 592.4651 | NaN | 26.7152 | NaN | 27.3707
1201.1292 | 12.7669 | 12.5851 | 12.5975 | 12.869 | 12.16 | 12.7826 | 12.3775 | 12.1543 | NaN | NaN | NaN | 12.8549 | 92.2546 | NaN | NaN | NaN | 1.5875 | NaN | 59.4108 | NaN | NaN | 589.1659 | NaN | 27.7453 | NaN | 27.6587
1202.1292 | 12.7505 | 12.6064 | 12.5985 | 12.9447 | 12.3119 | 12.8402 | 12.3988 | 12.1531 | NaN | NaN | NaN | 12.9187 | 93.7999 | NaN | NaN | NaN | -12.0944 | NaN | 60.143 | NaN | NaN | 591.6692 | NaN | 26.7606 | NaN | 28.8602
1203.1292 | 12.7725 | 12.6451 | 12.5936 | 12.8846 | 12.1594 | 12.8259 | 12.3931 | 12.1548 | NaN | NaN | NaN | 12.8817 | 92.2335 | NaN | NaN | NaN | -13.3915 | NaN | 60.6597 | NaN | NaN | 592.4145 | NaN | 24.8282 | NaN | 28.3553
1204.1292 | 12.7297 | 12.5635 | 12.5971 | 13.0965 | 12.2154 | 12.7626 | 12.3694 | 12.155 | NaN | NaN | NaN | 12.8659 | 92.1044 | NaN | NaN | NaN | -16.156 | NaN | 60.0914 | NaN | NaN | 593.8502 | NaN | 24.3909 | NaN | 28.7241
1205.1292 | 12.7702 | 12.6355 | 12.6083 | 12.9381 | 12.1779 | 12.8501 | 12.4031 | 12.1588 | NaN | NaN | NaN | 12.8191 | 90.4826 | NaN | NaN | NaN | 9.3377 | NaN | 60.756 | NaN | NaN | 590.4224 | NaN | 25.4036 | NaN | 27.5174
1206.1292 | 12.8792 | 12.545 | 12.6012 | 12.898 | 12.2929 | 12.7427 | 12.3545 | 12.157 | NaN | NaN | NaN | 12.8646 | 92.7365 | NaN | NaN | NaN | -1.7942 | NaN | 59.0101 | NaN | NaN | 593.8321 | NaN | 25.7331 | NaN | 27.0301
1207.1292 | 12.7415 | 12.5851 | 12.6056 | 12.8467 | 12.1896 | 12.7919 | 12.3837 | 12.1556 | NaN | NaN | NaN | 12.9376 | 93.112 | NaN | NaN | NaN | 0.237 | NaN | 61.4272 | NaN | NaN | 589.9077 | NaN | 25.7493 | NaN | 25.8856
1208.1292 | 12.8747 | 12.6197 | 12.6092 | 12.9708 | 12.1722 | 12.7972 | 12.3868 | 12.1504 | NaN | NaN | NaN | 12.8628 | 90.4722 | NaN | NaN | NaN | -3.0547 | NaN | 60.3408 | NaN | NaN | 592.065 | NaN | 26.1329 | NaN | 28.1501
1209.1292 | 12.7516 | 12.5787 | 12.6037 | 12.9152 | 12.3037 | 12.7222 | 12.3625 | 12.1476 | NaN | NaN | NaN | 12.8747 | 91.9456 | NaN | NaN | NaN | -15.5262 | NaN | 60.0829 | NaN | NaN | 590.5653 | NaN | 25.9023 | NaN | 25.2733
1210.1292 | 12.7189 | 12.6032 | 12.598 | 12.8957 | 12.3304 | 12.7721 | 12.3911 | 12.1519 | NaN | NaN | NaN | 12.8565 | 93.675 | NaN | NaN | NaN | 10.8432 | NaN | 59.3289 | NaN | NaN | 592.8269 | NaN | 24.7501 | NaN | 26.2592
1211.1292 | 12.8175 | 12.677 | 12.6035 | 12.8489 | 12.2016 | 12.8258 | 12.4 | 12.149 | NaN | NaN | NaN | 12.8537 | 92.0597 | NaN | NaN | NaN | -3.8183 | NaN | 60.6466 | NaN | NaN | 592.6693 | NaN | 24.0369 | NaN | 28.0688
1212.1292 | 12.7214 | 12.9127 | 12.5967 | 12.8648 | 12.222 | 13.0507 | 12.454 | 12.1422 | NaN | NaN | NaN | 12.8571 | 92.1284 | NaN | NaN | NaN | -8.1843 | NaN | 62.026 | NaN | NaN | 594.8744 | NaN | 26.8373 | NaN | 28.1377
1213.1292 | 12.8298 | 12.6702 | 12.5963 | 12.9099 | 12.1132 | 12.868 | 12.3813 | 12.1396 | NaN | NaN | NaN | 12.888 | 92.7115 | NaN | NaN | NaN | -15.7246 | NaN | 60.6628 | NaN | NaN | 592.238 | NaN | 24.9313 | NaN | 28.1213
1214.1292 | 12.7228 | 12.6806 | 12.5959 | 12.8301 | 12.1856 | 12.8621 | 12.4071 | 12.1395 | NaN | NaN | NaN | 12.8339 | 92.0892 | NaN | NaN | NaN | -0.6685 | NaN | 60.8279 | NaN | NaN | 594.0448 | NaN | 26.8624 | NaN | 26.2031
1215.1292 | 12.8376 | 12.6599 | 12.5912 | 12.9144 | 12.2303 | 12.8209 | 12.3941 | 12.1408 | NaN | NaN | NaN | 12.9206 | 91.1675 | NaN | NaN | NaN | -16.9596 | NaN | 59.9317 | NaN | NaN | 591.4132 | NaN | 23.9396 | NaN | 26.2652
1216.1292 | 12.773 | 12.8066 | 12.5963 | 12.83 | 12.1982 | 12.9105 | 12.3954 | 12.1475 | NaN | NaN | NaN | 12.846 | 92.0314 | NaN | NaN | NaN | -17.2809 | NaN | 61.1687 | NaN | NaN | 590.9793 | NaN | 25.7263 | NaN | 28.3048
1217.1292 | 12.6995 | 13.1257 | 12.5912 | 12.8395 | 12.2039 | 12.9829 | 12.4829 | 12.1394 | NaN | NaN | NaN | 12.8951 | 91.007 | NaN | NaN | NaN | 3.0663 | NaN | 61.7515 | NaN | NaN | 591.4417 | NaN | 27.2823 | NaN | 28.0122
1218.1292 | 13.1893 | 12.7678 | 12.5917 | 12.9047 | 12.2755 | 12.83 | 12.4013 | 12.1454 | NaN | NaN | NaN | 12.9209 | 90.48 | NaN | NaN | NaN | -1.3955 | NaN | 61.614 | NaN | NaN | 590.1767 | NaN | 24.7794 | NaN | 27.3097
1219.1292 | 12.8319 | 12.584 | 12.5933 | 12.9037 | 12.2198 | 12.7405 | 12.3755 | 12.142 | NaN | NaN | NaN | 12.8865 | 93.3075 | NaN | NaN | NaN | 0.9654 | NaN | 60.8163 | NaN | NaN | 589.634 | NaN | 26.7896 | NaN | 28.3675
1220.1292 | 12.8488 | 12.7464 | 12.5892 | 12.8588 | 12.188 | 12.869 | 12.4079 | 12.1457 | NaN | NaN | NaN | 12.8332 | 91.1542 | NaN | NaN | NaN | -7.6684 | NaN | 59.5026 | NaN | NaN | 588.5279 | NaN | 27.4434 | NaN | 28.8446
1221.1292 | 12.7679 | 12.626 | 12.5952 | 12.968 | 12.1375 | 12.8066 | 12.386 | 12.1458 | NaN | NaN | NaN | 12.8459 | 91.9873 | NaN | NaN | NaN | -3.3484 | NaN | 60.2446 | NaN | NaN | 586.7309 | NaN | 24.7351 | NaN | 27.2926
1222.1292 | 12.7828 | 12.5701 | 12.5999 | 12.898 | 12.1805 | 12.7079 | 12.3443 | 12.1387 | NaN | NaN | NaN | 12.8186 | 92.4053 | NaN | NaN | NaN | -1.7534 | NaN | 61.0489 | NaN | NaN | 580.901 | NaN | 24.5019 | NaN | 25.2575
1223.1292 | 12.8814 | 12.51 | 12.5901 | 12.8663 | 12.2231 | 12.665 | 12.3348 | 12.145 | NaN | NaN | NaN | 12.8363 | 92.8057 | NaN | NaN | NaN | NaN | NaN | 60.2668 | NaN | NaN | 583.9216 | NaN | 26.2516 | NaN | 26.2174
1224.1292 | 12.8457 | 12.5651 | 12.5916 | 12.9053 | 12.1396 | 12.724 | 12.3585 | 12.1397 | NaN | NaN | NaN | 12.7984 | 92.3356 | NaN | NaN | NaN | -12.2888 | NaN | 60.8767 | NaN | NaN | 586.8662 | NaN | 26.577 | NaN | 28.4814
1225.1292 | 12.9753 | 12.7499 | 12.586 | 12.8446 | 12.3099 | 12.8639 | 12.382 | 12.1432 | NaN | NaN | NaN | 12.8658 | 91.2647 | NaN | NaN | NaN | -7.8057 | NaN | 59.532 | NaN | NaN | 586.945 | NaN | 24.405 | NaN | 26.0121
1226.1292 | 12.7003 | 12.6243 | 12.5901 | 12.8432 | 12.256 | 12.7335 | 12.3604 | 12.1412 | NaN | NaN | NaN | 12.9916 | 92.3547 | NaN | NaN | NaN | -11.3959 | NaN | 60.7521 | NaN | NaN | 588.0812 | NaN | 25.8301 | NaN | 27.5143
1227.1292 | 12.7693 | 12.6001 | 12.5939 | 12.9074 | 12.2164 | 12.7087 | 12.347 | 12.144 | NaN | NaN | NaN | 12.9062 | 92.1069 | NaN | NaN | NaN | -12.7534 | NaN | 60.1158 | NaN | NaN | 584.6135 | NaN | 26.2971 | NaN | 26.9524
1228.1292 | 12.7532 | 12.7119 | 12.59 | 12.9525 | 12.1759 | 12.8336 | 12.3748 | 12.1396 | NaN | NaN | NaN | 12.9857 | 92.1673 | NaN | NaN | NaN | NaN | NaN | 60.8462 | NaN | NaN | 586.5999 | NaN | 25.6018 | NaN | 28.2211
1229.1292 | 12.7626 | 12.7361 | 12.5913 | 12.9146 | 12.204 | 12.8645 | 12.3914 | 12.1397 | NaN | NaN | NaN | 12.9055 | 92.228 | NaN | NaN | NaN | 8.5405 | NaN | 60.656 | NaN | NaN | 584.7645 | NaN | 25.8254 | NaN | 27.8241
1230.1292 | 12.7483 | 12.6321 | 12.5935 | 12.9079 | 12.2842 | 12.7881 | 12.3733 | 12.1416 | NaN | NaN | NaN | 12.9088 | 91.6882 | NaN | NaN | NaN | NaN | NaN | 60.3096 | NaN | NaN | 584.1488 | NaN | 25.2203 | NaN | 28.0439
1231.1292 | 12.7032 | 12.7125 | 12.5923 | 12.8902 | 12.1333 | 12.8053 | 12.3911 | 12.1375 | NaN | NaN | NaN | 13.0214 | 92.8402 | NaN | NaN | NaN | -18.8821 | NaN | 61.8824 | NaN | NaN | 581.3786 | NaN | 26.4031 | NaN | 24.9018
1232.1292 | 12.7279 | 12.7856 | 12.6036 | 12.8582 | 12.2352 | 12.8926 | 12.3975 | 12.1425 | NaN | NaN | NaN | 12.898 | 91.4025 | NaN | NaN | NaN | 0.3648 | NaN | 61.1151 | NaN | NaN | 583.2806 | NaN | 26.8215 | NaN | 28.2758
1233.1292 | 12.7604 | 12.5364 | 12.5998 | 12.8832 | 12.1927 | 12.6654 | 12.3412 | 12.1377 | NaN | NaN | NaN | 12.8942 | 92.1448 | NaN | NaN | NaN | -17.5738 | NaN | 61.8812 | NaN | NaN | 582.3362 | NaN | 26.78 | NaN | 27.7896
1234.1292 | 12.7355 | 12.615 | 12.6007 | 12.8934 | 12.2697 | 12.7829 | 12.3974 | 12.1364 | NaN | NaN | NaN | 12.9036 | 91.0035 | NaN | NaN | NaN | 8.0604 | NaN | 63.1889 | NaN | NaN | 581.5686 | NaN | 25.9106 | NaN | 26.9142
1235.1292 | 12.8252 | 12.9451 | 12.5964 | 12.856 | 12.2301 | 12.8419 | 12.4108 | 12.1434 | NaN | NaN | NaN | 12.9218 | 92.2945 | NaN | NaN | NaN | -0.4932 | NaN | 61.6316 | NaN | NaN | 580.5685 | NaN | 25.1666 | NaN | 26.574
1236.1292 | 12.7537 | 12.6569 | 12.6008 | 12.8844 | 12.2932 | 12.7146 | 12.3675 | 12.1421 | NaN | NaN | NaN | 13.0216 | 91.8823 | NaN | NaN | NaN | -18.6842 | NaN | 60.6017 | NaN | NaN | 580.7514 | NaN | 26.8386 | NaN | 25.6201
1237.1292 | 12.8319 | 12.6608 | 12.6053 | 12.8622 | 12.1394 | 12.7744 | 12.3848 | 12.1484 | NaN | NaN | NaN | 12.9261 | 91.81 | NaN | NaN | NaN | -7.8931 | NaN | 60.7152 | NaN | NaN | 581.6462 | NaN | 24.3279 | NaN | 27.1599
1238.1292 | 12.7575 | 12.5684 | 12.5977 | 12.8706 | 12.2306 | 12.7172 | 12.3627 | 12.1423 | NaN | NaN | NaN | 12.8827 | 91.8503 | NaN | NaN | NaN | 1.0567 | NaN | 60.912 | NaN | NaN | 579.7945 | NaN | 27.7026 | NaN | 26.8158
1239.1292 | 13.018 | 12.7841 | 12.5917 | 12.9006 | 12.1826 | 12.7816 | 12.3941 | 12.1389 | NaN | NaN | NaN | 12.9211 | 92.3334 | NaN | NaN | NaN | -10.5559 | NaN | 60.3982 | NaN | NaN | 578.974 | NaN | 25.5298 | NaN | 26.9282
1240.1292 | 12.7976 | 12.571 | 12.6027 | 12.8551 | 12.2643 | 12.6767 | 12.3427 | 12.1418 | NaN | NaN | NaN | 12.9102 | 91.76 | NaN | NaN | NaN | -14.4607 | NaN | 59.3266 | NaN | NaN | 582.3828 | NaN | 26.2551 | NaN | 26.701
1241.1292 | 12.8 | 12.6602 | 12.5986 | 12.8668 | 12.3178 | 12.7294 | 12.3717 | 12.1418 | NaN | NaN | NaN | 12.9794 | 94.5389 | NaN | NaN | NaN | -8.7257 | NaN | 59.319 | NaN | NaN | 581.1028 | NaN | 26.0432 | NaN | 28.1521
1242.1292 | 12.759 | 12.6232 | 12.597 | 12.8994 | 12.3209 | 12.7609 | 12.3715 | 12.1428 | NaN | NaN | NaN | 12.9441 | 91.8791 | NaN | NaN | NaN | -0.7915 | NaN | 60.0305 | NaN | NaN | 578.4619 | NaN | 26.6347 | NaN | 28.7768
1243.1292 | 12.8057 | 12.6492 | 12.5948 | 12.9369 | 12.2471 | 12.7334 | 12.3732 | 12.1468 | NaN | NaN | NaN | 12.8975 | 90.8662 | NaN | NaN | NaN | NaN | NaN | 59.6904 | NaN | NaN | 579.1586 | NaN | 24.7057 | NaN | 26.609
1244.1292 | 13.0087 | 12.7894 | 12.5981 | 12.8657 | 12.2334 | 12.8352 | 12.4485 | 12.1474 | NaN | NaN | NaN | 12.9139 | 90.5453 | NaN | NaN | NaN | -8.7738 | NaN | 62.7863 | NaN | NaN | 580.9531 | NaN | 24.3463 | NaN | 28.1832
1245.1292 | 12.811 | 12.5414 | 12.597 | 12.8494 | 12.333 | 12.6466 | 12.3295 | 12.1473 | NaN | NaN | NaN | 12.9391 | 91.9336 | NaN | NaN | NaN | -1.8986 | NaN | 60.7945 | NaN | NaN | 581.2574 | NaN | 24.6007 | NaN | 27.3226
1246.1292 | 12.7781 | 12.5792 | 12.603 | 12.9112 | 12.2517 | 12.7419 | 12.3716 | 12.1524 | NaN | NaN | NaN | 12.906 | 88.3213 | NaN | NaN | NaN | -1.187 | NaN | 60.9263 | NaN | NaN | 582.479 | NaN | 25.2721 | NaN | 27.6929
1247.1292 | 12.8159 | 12.7043 | 12.6079 | 12.9158 | 12.1776 | 12.8345 | 12.3865 | 12.1494 | NaN | NaN | NaN | 12.9387 | 90.0919 | NaN | NaN | NaN | -1.9336 | NaN | 61.4545 | NaN | NaN | 583.516 | NaN | 24.9258 | NaN | 26.8426
1248.1292 | 12.8045 | 12.6473 | 12.605 | 12.8674 | 12.3132 | 12.7938 | 12.3686 | 12.1441 | NaN | NaN | NaN | 12.94 | 95.124 | NaN | NaN | NaN | -0.5135 | NaN | 60.3619 | NaN | NaN | 585.0821 | NaN | 26.1727 | NaN | 28.0223
1249.1292 | 12.8071 | 12.7956 | 12.6117 | 12.8534 | 12.1817 | 12.8398 | 12.3944 | 12.1549 | NaN | NaN | NaN | 12.9094 | 89.9724 | NaN | NaN | NaN | 9.7847 | NaN | 63.0135 | NaN | NaN | 585.293 | NaN | 27.321 | NaN | 25.9774
1250.1292 | 12.7679 | 12.807 | 12.6049 | 13.1084 | 12.2231 | 12.8846 | 12.4065 | 12.1467 | NaN | NaN | NaN | 12.9134 | 90.6841 | NaN | NaN | NaN | 0.2175 | NaN | 61.1265 | NaN | NaN | 583.6439 | NaN | 25.4743 | NaN | 25.4927
1251.1292 | 12.7651 | 12.5798 | 12.6098 | 12.8748 | 12.344 | 12.6788 | 12.3479 | 12.158 | NaN | NaN | NaN | 12.9075 | 91.0246 | NaN | NaN | NaN | NaN | NaN | 59.5667 | NaN | NaN | 585.2847 | NaN | 25.4874 | NaN | 25.9354
1252.1292 | 12.8229 | 12.5452 | 12.6086 | 12.8465 | 12.3134 | 12.6499 | 12.3307 | 12.1463 | NaN | NaN | NaN | 12.9226 | 91.9716 | NaN | NaN | NaN | -15.3308 | NaN | 58.8618 | NaN | NaN | 583.1968 | NaN | 26.2629 | NaN | 27.5401
1253.1292 | 13.0355 | 12.6371 | 12.5997 | 12.8847 | 12.2954 | 12.7602 | 12.3723 | 12.1486 | NaN | NaN | NaN | 12.9229 | 91.0944 | NaN | NaN | NaN | -16.8307 | NaN | 59.2388 | NaN | NaN | 584.6879 | NaN | 24.7906 | NaN | 28.618
1254.1292 | 12.7487 | 12.6531 | 12.6063 | 12.9045 | 12.3173 | 12.6619 | 12.3506 | 12.1557 | NaN | NaN | NaN | 12.8997 | 91.7485 | NaN | NaN | NaN | -2.2225 | NaN | 61.089 | NaN | NaN | 586.5247 | NaN | 25.6551 | NaN | 26.4736
1255.1292 | 12.7903 | 12.6233 | 12.6123 | 13.0535 | 12.2753 | 12.6795 | 12.341 | 12.1585 | NaN | NaN | NaN | 12.8565 | 90.6487 | NaN | NaN | NaN | -5.1709 | NaN | 59.7399 | NaN | NaN | 585.2422 | NaN | 23.9929 | NaN | 28.8429
1256.1292 | 12.8078 | 12.9375 | 12.6124 | 12.8555 | 12.2755 | 12.9515 | 12.4361 | 12.1515 | NaN | NaN | NaN | 12.8486 | 92.2182 | NaN | NaN | NaN | 3.3127 | NaN | 61.9147 | NaN | NaN | 584.6443 | NaN | 26.7415 | NaN | 24.4677
1257.1292 | 12.7518 | 13.0472 | 12.6141 | 12.8367 | 12.2846 | 12.7453 | 12.4939 | 12.1582 | NaN | NaN | NaN | 12.8846 | 94.3988 | NaN | NaN | NaN | 3.7454 | NaN | 60.7322 | NaN | NaN | 585.2831 | NaN | 26.32 | NaN | 26.0857
1258.1292 | 12.972 | 12.6139 | 12.6155 | 13.002 | 12.2984 | 12.7702 | 12.3851 | 12.1601 | NaN | NaN | NaN | 12.8884 | 91.759 | NaN | NaN | NaN | -16.7365 | NaN | 60.9597 | NaN | NaN | 586.5775 | NaN | 24.4324 | NaN | 27.3542
1259.1292 | 12.7942 | 12.8192 | 12.6176 | 12.8698 | 12.2523 | 12.909 | 12.4051 | 12.1598 | NaN | NaN | NaN | 12.8724 | 90.8074 | NaN | NaN | NaN | 0.1103 | NaN | 58.4893 | NaN | NaN | 586.9393 | NaN | 25.185 | NaN | 28.1956
1260.1292 | 12.7786 | 12.7449 | 12.6211 | 12.8317 | 12.3018 | 12.7352 | 12.4011 | 12.1645 | NaN | NaN | NaN | 12.8546 | 92.1842 | NaN | NaN | NaN | -6.6861 | NaN | 58.7866 | NaN | NaN | 586.5308 | NaN | 26.2797 | NaN | 25.8625
1261.1292 | 12.7729 | 12.6405 | 12.6183 | 12.9878 | 12.2484 | 12.7526 | 12.3816 | 12.1588 | NaN | NaN | NaN | 12.9019 | 91.398 | NaN | NaN | NaN | -14.6402 | NaN | 60.5654 | NaN | NaN | 586.7573 | NaN | 26.2339 | NaN | 26.6659
1262.1292 | 12.7909 | 12.7114 | 12.6219 | 12.8533 | 12.3287 | 12.7935 | 12.3855 | 12.1656 | NaN | NaN | NaN | 12.8696 | 92.5127 | NaN | NaN | NaN | -19.2881 | NaN | 59.6358 | NaN | NaN | 586.0693 | NaN | 23.912 | NaN | 27.2884
1263.1292 | 12.7511 | 12.9905 | 12.6242 | 12.8949 | 12.1633 | 12.9553 | 12.4094 | 12.1683 | NaN | NaN | NaN | 12.8441 | 91.4621 | NaN | NaN | NaN | 36.5008 | NaN | 59.095 | NaN | NaN | 588.0803 | NaN | 24.3547 | NaN | 28.0591
1264.1292 | 12.8532 | 12.5868 | 12.6283 | 12.9715 | 12.3326 | 12.7091 | 12.3606 | 12.1674 | NaN | NaN | NaN | 12.888 | 90.9111 | NaN | NaN | NaN | -6.2831 | NaN | 59.1749 | NaN | NaN | 585.105 | NaN | 26.1164 | NaN | 25.5951
1265.1292 | 12.8165 | 12.6114 | 12.6242 | 12.926 | 12.225 | 12.7221 | 12.3652 | 12.1657 | NaN | NaN | NaN | 12.8313 | 92.2772 | NaN | NaN | NaN | -7.2687 | NaN | 61.3052 | NaN | NaN | 587.0417 | NaN | 24.8064 | NaN | 27.6057
1266.1292 | 12.9108 | 12.6128 | 12.6264 | 12.9045 | 12.2126 | 12.692 | 12.3616 | 12.1657 | NaN | NaN | NaN | 12.9172 | 91.305 | NaN | NaN | NaN | -16.1691 | NaN | 59.9592 | NaN | NaN | 585.1496 | NaN | 24.3008 | NaN | 26.3394
1267.1292 | 13.2566 | 12.5889 | 12.623 | 12.882 | 12.345 | 12.6964 | 12.3488 | 12.1695 | NaN | NaN | NaN | 12.981 | 92.1605 | NaN | NaN | NaN | -0.5878 | NaN | 59.8886 | NaN | NaN | 585.9329 | NaN | 25.0613 | NaN | 27.4438
1268.1292 | 12.8201 | 12.6232 | 12.6261 | 12.9116 | 12.3247 | 12.7297 | 12.3582 | 12.1705 | NaN | NaN | NaN | 12.8413 | 92.8884 | NaN | NaN | NaN | -16.4934 | NaN | 59.2491 | NaN | NaN | 585.4978 | NaN | 25.1157 | NaN | 26.9278
1269.1292 | 12.7628 | 12.7232 | 12.6316 | 12.8844 | 12.2736 | 12.7774 | 12.3892 | 12.1728 | NaN | NaN | NaN | 12.931 | 92.083 | NaN | NaN | NaN | -7.5275 | NaN | 59.1636 | NaN | NaN | 585.4758 | NaN | 23.7746 | NaN | 28.5656
1270.1292 | 12.7732 | 12.6255 | 12.6248 | 12.8958 | 12.237 | 12.7608 | 12.37 | 12.1708 | NaN | NaN | NaN | 12.9335 | 91.9524 | NaN | NaN | NaN | -14.6723 | NaN | 60.6958 | NaN | NaN | 586.9629 | NaN | 25.3643 | NaN | 26.1821
1271.1292 | 12.7882 | 12.8822 | 12.6315 | 12.8137 | 12.1697 | 12.9476 | 12.4134 | 12.1701 | NaN | NaN | NaN | 12.8688 | 93.2572 | NaN | NaN | NaN | 6.0799 | NaN | 60.1175 | NaN | NaN | 584.539 | NaN | 24.8545 | NaN | 27.7589
1272.1292 | 12.8774 | 12.5618 | 12.63 | 12.9138 | 12.2417 | 12.6953 | 12.3437 | 12.1676 | NaN | NaN | NaN | 12.879 | 95.4089 | NaN | NaN | NaN | 4.2702 | NaN | 59.7477 | NaN | NaN | 584.1661 | NaN | 25.8386 | NaN | 28.6561
1273.1292 | 12.8197 | 12.9844 | 12.6302 | 12.8606 | 12.1563 | 13.0027 | 12.4217 | 12.1798 | NaN | NaN | NaN | 12.9158 | 90.8929 | NaN | NaN | NaN | -8.4473 | NaN | 60.0188 | NaN | NaN | 584.6395 | NaN | 25.7633 | NaN | 25.9801
1274.1292 | 12.8511 | 12.6671 | 12.6289 | 12.8825 | 12.2118 | 12.7795 | 12.3667 | 12.1778 | NaN | NaN | NaN | 12.8608 | 88.9606 | NaN | NaN | NaN | 4.2004 | NaN | 59.2986 | NaN | NaN | 583.6328 | NaN | 22.4346 | NaN | 26.3809
1275.1292 | 12.8352 | 12.7612 | 12.6283 | 12.9837 | 12.283 | 12.8643 | 12.3974 | 12.1777 | NaN | NaN | NaN | 12.8883 | 91.3509 | NaN | NaN | NaN | -13.4882 | NaN | 60.1752 | NaN | NaN | 585.6877 | NaN | 26.4652 | NaN | 25.8225
1276.1292 | 12.8829 | 12.7996 | 12.6278 | 12.884 | 12.2895 | 12.8633 | 12.4036 | 12.1791 | NaN | NaN | NaN | 12.8459 | 91.4652 | NaN | NaN | NaN | -12.3027 | NaN | 60.0777 | NaN | NaN | 586.5557 | NaN | 25.9606 | NaN | 26.2493
1277.1292 | 12.7628 | 12.624 | 12.6182 | 12.9128 | 12.1643 | 12.7676 | 12.3508 | 12.1726 | NaN | NaN | NaN | 12.8627 | 93.2709 | NaN | NaN | NaN | 1.3802 | NaN | 59.7424 | NaN | NaN | 588.84 | NaN | 24.0402 | NaN | 25.9392
1278.1292 | 12.8337 | 12.6641 | 12.6213 | 12.8737 | 12.1792 | 12.7955 | 12.3794 | 12.1769 | NaN | NaN | NaN | 12.8093 | 91.7683 | NaN | NaN | NaN | -17.0735 | NaN | 60.8022 | NaN | NaN | 588.6615 | NaN | 25.6348 | NaN | 27.6667
1279.1292 | 12.8309 | 12.6853 | 12.6216 | 12.9706 | 12.2828 | 12.8087 | 12.3764 | 12.1695 | NaN | NaN | NaN | 12.8835 | 93.8441 | NaN | NaN | NaN | -3.4509 | NaN | 60.1427 | NaN | NaN | 584.7103 | NaN | 25.8929 | NaN | 27.6575
1280.1292 | 12.8641 | 12.621 | 12.6193 | 12.9187 | 12.1843 | 12.7923 | 12.371 | 12.1668 | NaN | NaN | NaN | 12.798 | 93.3928 | NaN | NaN | NaN | -15.537 | NaN | 59.5057 | NaN | NaN | 586.0366 | NaN | 23.898 | NaN | 25.2163
1281.1292 | 12.8149 | 12.8933 | 12.6185 | 12.9279 | 12.3668 | 12.987 | 12.4031 | 12.1715 | NaN | NaN | NaN | 12.829 | 91.9347 | NaN | NaN | NaN | -10.4606 | NaN | 61.2887 | NaN | NaN | 587.762 | NaN | 24.1271 | NaN | 26.9988
1282.1292 | 12.8638 | 12.5673 | 12.6245 | 12.8547 | 12.1532 | 12.698 | 12.344 | 12.1736 | NaN | NaN | NaN | 12.9067 | 90.6237 | NaN | NaN | NaN | 15.7698 | NaN | 60.4271 | NaN | NaN | 586.7809 | NaN | 23.0259 | NaN | 27.3692
1283.1292 | 12.9273 | 12.5645 | 12.6265 | 12.8707 | 12.2802 | 12.7215 | 12.365 | 12.1754 | NaN | NaN | NaN | 12.8729 | 90.6401 | NaN | NaN | NaN | -13.3671 | NaN | 62.7521 | NaN | NaN | 587.4566 | NaN | 25.4777 | NaN | 28.6599
1284.1292 | 12.9357 | 12.5958 | 12.6203 | 12.8841 | 12.2244 | 12.7594 | 12.3736 | 12.1766 | NaN | NaN | NaN | 12.8913 | 92.1235 | NaN | NaN | NaN | 2.4026 | NaN | 59.7033 | NaN | NaN | 587.7739 | NaN | 26.1838 | NaN | 27.3867
1285.1292 | 12.7894 | 12.6396 | 12.6279 | 12.8738 | 12.2268 | 12.8162 | 12.3905 | 12.1761 | NaN | NaN | NaN | 12.8579 | 91.4054 | NaN | NaN | NaN | -6.0087 | NaN | 60.4145 | NaN | NaN | 589.8223 | NaN | 25.3593 | NaN | 27.005
1286.1292 | 12.838 | 12.8212 | 12.6204 | 12.9281 | 12.2453 | 12.9082 | 12.4207 | 12.1712 | NaN | NaN | NaN | 12.8258 | 90.0454 | NaN | NaN | NaN | -15.945 | NaN | 59.6801 | NaN | NaN | 586.4656 | NaN | 26.3035 | NaN | 26.484
1287.1292 | 12.8794 | 12.5094 | 12.6263 | 12.8629 | 12.3395 | 12.6382 | 12.3335 | 12.1735 | NaN | NaN | NaN | 12.8748 | 94.3685 | NaN | NaN | NaN | 73.688 | NaN | NaN | NaN | NaN | 593.6752 | NaN | 25.6609 | NaN | 26.2733
1288.1292 | 12.7997 | 12.5578 | 12.6284 | 12.8538 | 12.2777 | 12.6783 | 12.3531 | 12.1785 | NaN | NaN | NaN | 12.8515 | 91.5299 | NaN | NaN | NaN | -18.5009 | NaN | NaN | NaN | NaN | 601.296 | NaN | 23.9934 | NaN | 27.3422
1289.1292 | 12.7909 | 12.7019 | 12.6296 | 12.9065 | 12.2423 | 12.7627 | 12.3798 | 12.1763 | NaN | NaN | NaN | 12.8333 | 91.5023 | NaN | NaN | NaN | -19.4668 | NaN | NaN | NaN | NaN | 601.1963 | NaN | 25.1829 | NaN | 27.2893
1290.1292 | 12.8885 | 12.7646 | 12.628 | 12.9311 | 12.17 | 12.8831 | 12.419 | 12.174 | NaN | NaN | NaN | 12.8377 | 92.0496 | NaN | NaN | NaN | -9.2813 | NaN | NaN | NaN | NaN | 602.2473 | NaN | 25.5474 | NaN | 26.9334
1291.1292 | 12.8238 | 12.6606 | 12.6315 | 12.8807 | 12.1685 | 12.8197 | 12.3755 | 12.1753 | NaN | NaN | NaN | 12.7837 | 91.8517 | NaN | NaN | NaN | -14.9802 | NaN | NaN | NaN | NaN | 605.5044 | NaN | 24.9844 | NaN | 26.8984
1292.1292 | 12.8256 | 12.681 | 12.6273 | 12.9715 | 12.2486 | 12.8125 | 12.3842 | 12.1795 | NaN | NaN | NaN | 12.8236 | 91.9027 | NaN | NaN | NaN | -12.2347 | NaN | NaN | NaN | NaN | 602.3065 | NaN | 25.801 | NaN | 27.9774
1293.1292 | 13.1234 | 12.6577 | 12.6219 | 12.9287 | 12.2821 | 12.7532 | 12.3643 | 12.1861 | NaN | NaN | NaN | 12.8273 | 93.3907 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 602.1334 | NaN | 22.1674 | NaN | 24.4152
1294.1292 | 12.8363 | 12.6294 | 12.6261 | 12.976 | 12.1106 | 12.776 | 12.3739 | 12.1869 | NaN | NaN | NaN | 12.7826 | 91.9326 | NaN | NaN | NaN | -15.5397 | NaN | NaN | NaN | NaN | 605.7965 | NaN | 26.7975 | NaN | 27.2717
1295.1292 | 12.8599 | 12.5657 | 12.6239 | 12.9194 | 12.3197 | 12.711 | 12.3629 | 12.1845 | NaN | NaN | NaN | 12.7938 | 93.5197 | NaN | NaN | NaN | -15.5811 | NaN | NaN | NaN | NaN | 604.3139 | NaN | 22.981 | NaN | 28.2769
1296.1292 | 12.7834 | 12.6572 | 12.6257 | 12.9868 | 12.2873 | 12.7574 | 12.3697 | 12.1834 | NaN | NaN | NaN | 12.8373 | 93.5396 | NaN | NaN | NaN | -7.6834 | NaN | NaN | NaN | NaN | 604.0463 | NaN | 22.2661 | NaN | 26.9416
1297.1292 | 12.8014 | 12.7052 | 12.6289 | 12.9914 | 12.2414 | 12.8112 | 12.3743 | 12.1864 | NaN | NaN | NaN | 12.8252 | 91.9445 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 603.6445 | NaN | 26.6599 | NaN | 26.5363
1298.1292 | 12.8911 | 12.7663 | 12.6325 | 12.8729 | 12.3273 | 12.8439 | 12.4032 | 12.1892 | NaN | NaN | NaN | 12.8384 | 93.7558 | NaN | NaN | NaN | -10.4899 | NaN | NaN | NaN | NaN | 604.3561 | NaN | 23.5104 | NaN | 24.6026
1299.1292 | 12.853 | 12.7847 | 12.6351 | 12.9126 | 12.3025 | 12.8306 | 12.4355 | 12.1898 | NaN | NaN | NaN | 12.8432 | 93.1169 | NaN | NaN | NaN | -5.6974 | NaN | NaN | NaN | NaN | 602.7809 | NaN | 23.882 | NaN | 24.4205
1300.1292 | 12.7855 | 12.6466 | 12.6325 | 12.8412 | 12.2326 | 12.786 | 12.3732 | 12.1888 | NaN | NaN | NaN | 12.9319 | 98.9942 | NaN | NaN | NaN | 4.0264 | NaN | NaN | NaN | NaN | 605.2774 | NaN | 21.9495 | NaN | 28.1163
1301.1292 | 12.9024 | 12.6983 | 12.6328 | 12.8501 | 12.34 | 12.7962 | 12.3856 | 12.1931 | NaN | NaN | NaN | 12.7704 | 94.8927 | NaN | NaN | NaN | -13.0533 | NaN | NaN | NaN | NaN | 603.8925 | NaN | 25.4494 | NaN | 27.3106
1302.1292 | 12.8176 | 12.6894 | 12.6362 | 12.9046 | 12.2869 | 12.7842 | 12.3674 | 12.1923 | NaN | NaN | NaN | 12.7694 | 91.6047 | NaN | NaN | NaN | -6.4055 | NaN | NaN | NaN | NaN | 604.8442 | NaN | 24.3756 | NaN | 26.8654
1303.1292 | 12.8558 | 12.5803 | 12.6354 | 12.9326 | 12.208 | 12.7327 | 12.3653 | 12.1926 | NaN | NaN | NaN | 12.8145 | 91.5859 | NaN | NaN | NaN | -13.071 | NaN | NaN | NaN | NaN | 604.4901 | NaN | 25.2996 | NaN | 27.9465
1304.1292 | 12.814 | 12.9935 | 12.6369 | 12.8397 | 12.3153 | 13.1146 | 12.4792 | 12.1973 | NaN | NaN | NaN | 12.8457 | 91.2134 | NaN | NaN | NaN | -16.8049 | NaN | NaN | NaN | NaN | 605.4292 | NaN | 25.4044 | NaN | 27.643
1305.1292 | 12.7916 | 12.5907 | 12.6358 | 12.8609 | 12.1805 | 12.7312 | 12.3631 | 12.1983 | NaN | NaN | NaN | 12.7705 | 93.1905 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 606.6552 | NaN | 25.3329 | NaN | 24.6928
1306.1292 | 12.9513 | 12.7665 | 12.632 | 12.9116 | 12.2049 | 12.863 | 12.4104 | 12.1974 | NaN | NaN | NaN | 12.7871 | 91.726 | NaN | NaN | NaN | -12.0045 | NaN | NaN | NaN | NaN | 605.329 | NaN | 23.2728 | NaN | 25.8986
1307.1292 | 12.8075 | 12.7225 | 12.6467 | 12.8533 | 12.2384 | 12.8195 | 12.4012 | 12.1966 | NaN | NaN | NaN | 12.8562 | 91.7489 | NaN | NaN | NaN | 35.3072 | NaN | NaN | NaN | NaN | 604.1518 | NaN | 23.9025 | NaN | 26.2519
1308.1292 | 13.1891 | 12.5445 | 12.6399 | 12.8813 | 12.2517 | 12.6688 | 12.3512 | 12.1986 | NaN | NaN | NaN | 12.8129 | 91.7053 | NaN | NaN | NaN | -14.7616 | NaN | NaN | NaN | NaN | 606.2739 | NaN | 23.6232 | NaN | 26.5193
1309.1292 | 12.8122 | 12.6254 | 12.6404 | 12.8815 | 12.4066 | 12.7516 | 12.3799 | 12.1993 | NaN | NaN | NaN | 12.8191 | 92.7135 | NaN | NaN | NaN | 9.3171 | NaN | NaN | NaN | NaN | 606.561 | NaN | 25.1464 | NaN | 27.5965
1310.1292 | 12.8348 | 12.6973 | 12.6431 | 12.8769 | 12.3451 | 12.7735 | 12.3755 | 12.199 | NaN | NaN | NaN | 12.7887 | 88.6369 | NaN | NaN | NaN | -2.4309 | NaN | NaN | NaN | NaN | 607.013 | NaN | 23.8505 | NaN | 27.105
1311.1292 | 12.784 | 12.7529 | 12.6449 | 12.909 | 12.3521 | 12.8248 | 12.3815 | 12.1928 | NaN | NaN | NaN | 12.841 | 92.0124 | NaN | NaN | NaN | -1.8105 | NaN | NaN | NaN | NaN | 607.5873 | NaN | 25.3596 | NaN | 27.015
1312.1292 | 12.8427 | 12.6534 | 12.6484 | 12.8791 | 12.3476 | 12.7673 | 12.3867 | 12.2009 | NaN | NaN | NaN | 12.8589 | 91.6374 | NaN | NaN | NaN | -14.9475 | NaN | NaN | NaN | NaN | 608.4408 | NaN | 23.9316 | NaN | 25.4059
1313.1292 | 12.8258 | 12.6118 | 12.6442 | 12.9877 | 12.2414 | 12.7454 | 12.3858 | 12.1926 | NaN | NaN | NaN | 12.8212 | 93.2147 | NaN | NaN | NaN | 4.3671 | NaN | NaN | NaN | NaN | 607.4863 | NaN | 21.6308 | NaN | 26.8386
1314.1292 | 12.8349 | 12.6991 | 12.6478 | 12.8899 | 12.2789 | 12.7602 | 12.3904 | 12.1917 | NaN | NaN | NaN | 12.822 | 95.7563 | NaN | NaN | NaN | 8.6971 | NaN | NaN | NaN | NaN | 605.2471 | NaN | 24.7544 | NaN | 25.9182
1315.1292 | 12.8437 | 12.6263 | 12.6473 | 12.935 | 12.1335 | 12.7325 | 12.3668 | 12.1931 | NaN | NaN | NaN | 12.8742 | 94.4957 | NaN | NaN | NaN | -4.6561 | NaN | NaN | NaN | NaN | 606.5626 | NaN | 23.1427 | NaN | 27.428
1316.1292 | 12.7901 | 12.7655 | 12.6527 | 12.9174 | 12.2062 | 12.8038 | 12.4201 | 12.1927 | NaN | NaN | NaN | 12.7944 | 92.7267 | NaN | NaN | NaN | -12.2871 | NaN | NaN | NaN | NaN | 606.1641 | NaN | 24.6673 | NaN | 24.1953
1317.1292 | 12.7893 | 12.5831 | 12.6463 | 12.8696 | 12.1958 | 12.6976 | 12.3584 | 12.1928 | NaN | NaN | NaN | 12.8601 | 91.7267 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 607.4459 | NaN | 22.5814 | NaN | 26.6309
1318.1292 | 12.9657 | 12.7311 | 12.6538 | 12.8788 | 12.2692 | 12.84 | 12.4086 | 12.1901 | NaN | NaN | NaN | 12.7751 | 88.6257 | NaN | NaN | NaN | 3.3022 | NaN | NaN | NaN | NaN | 604.6644 | NaN | 21.525 | NaN | 28.4878
1319.1292 | 12.8016 | 12.6372 | 12.6548 | 12.8841 | 12.2468 | 12.7441 | 12.3726 | 12.198 | NaN | NaN | NaN | 12.9041 | 92.6478 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 605.9605 | NaN | 23.5143 | NaN | 26.6419
1320.1292 | 12.8491 | 12.5931 | 12.6556 | 12.9387 | 12.1359 | 12.6874 | 12.365 | 12.194 | NaN | NaN | NaN | 12.8062 | 92.0296 | NaN | NaN | NaN | -1.8448 | NaN | NaN | NaN | NaN | 603.9571 | NaN | 23.2278 | NaN | 27.4011
1321.1292 | 12.8348 | 12.6897 | 12.6556 | 12.9671 | 12.4151 | 12.7466 | 12.3696 | 12.1931 | NaN | NaN | NaN | 12.7773 | 92.5287 | NaN | NaN | NaN | 5.7279 | NaN | NaN | NaN | NaN | 604.3186 | NaN | 24.4024 | NaN | 27.7347
1322.1292 | 12.825 | 12.6036 | 12.6587 | 12.88 | 12.3187 | 12.7441 | 12.3788 | 12.2004 | NaN | NaN | NaN | 12.7675 | 90.9421 | NaN | NaN | NaN | -15.1988 | NaN | NaN | NaN | NaN | 605.4196 | NaN | 24.7118 | NaN | 26.6817
1323.1292 | 12.8278 | 12.6164 | 12.6605 | 13.0109 | 12.2463 | 12.7116 | 12.363 | 12.2013 | NaN | NaN | NaN | 12.823 | 94.2123 | NaN | NaN | NaN | -13.0754 | NaN | NaN | NaN | NaN | 603.3722 | NaN | 23.7307 | NaN | 25.6303
1324.1292 | 12.8141 | 12.9957 | 12.6628 | 12.9817 | 12.286 | 12.9883 | 12.4622 | 12.2012 | NaN | NaN | NaN | 12.8594 | 87.6382 | NaN | NaN | NaN | 8.0226 | NaN | NaN | NaN | NaN | 601.9473 | NaN | 23.1247 | NaN | 25.1306
1325.1292 | 12.8655 | 12.5897 | 12.6674 | 12.8933 | 12.2251 | 12.7054 | 12.3831 | 12.2058 | NaN | NaN | NaN | 12.7595 | 91.1221 | NaN | NaN | NaN | -12.6899 | NaN | NaN | NaN | NaN | 605.2265 | NaN | 24.9367 | NaN | 27.1884
1326.1292 | 12.7717 | 12.619 | 12.6586 | 12.8985 | 12.2257 | 12.6894 | 12.3661 | 12.2053 | NaN | NaN | NaN | 12.8303 | 93.8172 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 604.071 | NaN | 20.3068 | NaN | 25.8057
1327.1292 | 12.8037 | 12.5529 | 12.6586 | 12.9336 | 12.2477 | 12.6815 | 12.3807 | 12.2056 | NaN | NaN | NaN | 12.8841 | 91.8347 | NaN | NaN | NaN | 19.3564 | NaN | NaN | NaN | NaN | 606.0662 | NaN | 24.4723 | NaN | 25.4476
1328.1292 | 12.8272 | 12.5612 | 12.6566 | 12.9266 | 12.2626 | 12.6633 | 12.3732 | 12.205 | NaN | NaN | NaN | 12.7699 | 91.3416 | NaN | NaN | NaN | 3.6988 | NaN | NaN | NaN | NaN | 604.3119 | NaN | 24.5296 | NaN | 26.127
1329.1292 | 12.8453 | 12.5971 | 12.6527 | 13.0059 | 12.4041 | 12.6916 | 12.3743 | 12.2078 | NaN | NaN | NaN | 12.8066 | 89.2101 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 603.0312 | NaN | 21.7303 | NaN | 26.822
1330.1292 | 13.0916 | 12.794 | 12.6535 | 12.9746 | 12.2348 | 12.8851 | 12.4291 | 12.2067 | NaN | NaN | NaN | 12.8733 | 91.3396 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 606.7366 | NaN | 21.4851 | NaN | 26.2132
1331.1292 | 12.8551 | 12.6193 | 12.6506 | 12.8483 | 12.255 | 12.7029 | 12.4065 | 12.2052 | NaN | NaN | NaN | 12.7942 | 92.3809 | NaN | NaN | NaN | 7.9324 | NaN | NaN | NaN | NaN | 605.0828 | NaN | 24.3045 | NaN | 25.088
1332.1292 | 12.8372 | 12.6134 | 12.6494 | 13.1116 | 12.2953 | 12.7711 | 12.3989 | 12.194 | NaN | NaN | NaN | 12.7942 | 94.3773 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 603.3247 | NaN | 22.243 | NaN | 29.0073
1333.1292 | 12.8318 | 12.5896 | 12.6399 | 12.9154 | 12.3861 | 12.7254 | 12.3916 | 12.194 | NaN | NaN | NaN | 12.8716 | 95.4817 | NaN | NaN | NaN | -18.102 | NaN | NaN | NaN | NaN | 599.0555 | NaN | 22.013 | NaN | 28.0527
1334.1292 | 12.8694 | 12.7147 | 12.641 | 12.8653 | 12.2877 | 12.8057 | 12.4189 | 12.1999 | NaN | NaN | NaN | 12.8255 | 94.0982 | NaN | NaN | NaN | 0.6028 | NaN | NaN | NaN | NaN | 598.935 | NaN | 25.3482 | NaN | 25.1289
1335.1292 | 12.8547 | 12.5376 | 12.6323 | 12.9271 | 12.2981 | 12.6677 | 12.3795 | 12.1986 | NaN | NaN | NaN | 12.9487 | 92.0988 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 601.7037 | NaN | 23.779 | NaN | 25.3642
1336.1292 | 12.8452 | 12.8038 | 12.6254 | 12.914 | 12.2506 | 12.86 | 12.4391 | 12.2034 | NaN | NaN | NaN | 12.8139 | 91.58 | NaN | NaN | NaN | -4.1659 | NaN | NaN | NaN | NaN | 602.211 | NaN | 24.3723 | NaN | 26.4378
1337.1292 | 12.9106 | 12.6443 | 12.6279 | 12.9394 | 12.206 | 12.7604 | 12.4165 | 12.2004 | NaN | NaN | NaN | 12.8273 | 95.2609 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 601.6951 | NaN | 26.4639 | NaN | 27.729
1338.1292 | 12.9581 | 12.6186 | 12.6231 | 12.912 | 12.1769 | 12.7689 | 12.4048 | 12.2087 | NaN | NaN | NaN | 12.9027 | 95.3487 | NaN | NaN | NaN | -16.3775 | NaN | NaN | NaN | NaN | 602.9347 | NaN | 22.8268 | NaN | 27.0719
1339.1292 | 12.881 | 12.6083 | 12.6121 | 12.9312 | 12.2864 | 12.7508 | 12.4127 | 12.2015 | NaN | NaN | NaN | 12.8378 | 91.1262 | NaN | NaN | NaN | -9.4824 | NaN | NaN | NaN | NaN | 602.2914 | NaN | 23.5727 | NaN | 27.0731
1340.1292 | 12.8666 | 12.5958 | 12.6053 | 13 | 12.1875 | 12.7535 | 12.4114 | 12.2017 | NaN | NaN | NaN | 12.8501 | 92.681 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 601.1937 | NaN | 23.9265 | NaN | 25.7839
1341.1292 | 12.8484 | 12.611 | 12.6058 | 12.9144 | 12.282 | 12.7965 | 12.4121 | 12.1983 | NaN | NaN | NaN | 12.867 | 90.7096 | NaN | NaN | NaN | -5.0036 | NaN | NaN | NaN | NaN | 602.8935 | NaN | 24.2135 | NaN | 26.9263
1342.1292 | 12.8483 | 12.5393 | 12.6018 | 13.0345 | 12.3766 | 12.683 | 12.3907 | 12.2061 | NaN | NaN | NaN | 12.8316 | 92.3084 | NaN | NaN | NaN | 2.3092 | NaN | NaN | NaN | NaN | 601.5097 | NaN | 23.2829 | NaN | 26.3376
1343.1292 | 12.8005 | 12.8112 | 12.6034 | 12.9181 | 12.1606 | 12.897 | 12.4345 | 12.207 | NaN | NaN | NaN | 12.8303 | 91.6301 | NaN | NaN | NaN | -13.7102 | NaN | NaN | NaN | NaN | 597.9132 | NaN | 26.0748 | NaN | 25.617
1344.1292 | 12.8315 | 12.6332 | 12.5979 | 12.9703 | 12.3324 | 12.7502 | 12.4092 | 12.2141 | NaN | NaN | NaN | 12.8041 | 89.741 | NaN | NaN | NaN | -6.0159 | NaN | NaN | NaN | NaN | 596.9643 | NaN | 22.5975 | NaN | 25.4026
1345.1292 | 12.7966 | 12.759 | 12.6052 | 12.9947 | 12.2514 | 12.9403 | 12.4459 | 12.2123 | NaN | NaN | NaN | 12.8369 | 91.2174 | NaN | NaN | NaN | -11.0616 | NaN | NaN | NaN | NaN | 600.8504 | NaN | 25.8963 | NaN | 25.9211
1346.1292 | 12.7803 | 12.5694 | 12.6047 | 13.0762 | 12.2859 | 12.7386 | 12.4019 | 12.2079 | NaN | NaN | NaN | 12.8774 | 92.2244 | NaN | NaN | NaN | -4.7924 | NaN | NaN | NaN | NaN | 600.3388 | NaN | 22.0981 | NaN | 26.7052
1347.1292 | 12.8479 | 12.5799 | 12.599 | 12.9947 | 12.2585 | 12.7773 | 12.395 | 12.2092 | NaN | NaN | NaN | 12.8368 | 93.8136 | NaN | NaN | NaN | -12.4658 | NaN | NaN | NaN | NaN | 598.8788 | NaN | 23.1568 | NaN | 23.8828
1348.1292 | 12.8552 | 12.5868 | 12.6032 | 12.9486 | 12.1267 | 12.7636 | 12.4098 | 12.2123 | NaN | NaN | NaN | 12.8187 | 91.9633 | NaN | NaN | NaN | 14.8646 | NaN | NaN | NaN | NaN | 597.4456 | NaN | 24.6973 | NaN | 26.3295
1349.1292 | 12.7951 | 12.5243 | 12.6038 | 12.905 | 12.2494 | 12.6802 | 12.3759 | 12.2116 | NaN | NaN | NaN | 12.9194 | 93.0151 | NaN | NaN | NaN | -18.5391 | NaN | NaN | NaN | NaN | 599.4988 | NaN | 22.5264 | NaN | 27.2975
1350.1292 | 12.8726 | 12.6268 | 12.607 | 12.9085 | 12.2849 | 12.8006 | 12.4024 | 12.2153 | NaN | NaN | NaN | 12.8406 | 92.8436 | NaN | NaN | NaN | 2.8833 | NaN | NaN | NaN | NaN | 600.0093 | NaN | 21.1741 | NaN | 26.0622
1351.1292 | 12.8921 | 12.5984 | 12.6094 | 12.9292 | 12.3107 | 12.7693 | 12.415 | 12.2193 | NaN | NaN | NaN | 12.8236 | 92.8387 | NaN | NaN | NaN | -5.1871 | NaN | NaN | NaN | NaN | 595.8679 | NaN | 24.7849 | NaN | 27.0544
1352.1292 | 12.8488 | 12.6238 | 12.6162 | 12.8976 | 12.347 | 12.7847 | 12.4124 | 12.2197 | NaN | NaN | NaN | 12.8404 | 91.9001 | NaN | NaN | NaN | 3.3194 | NaN | NaN | NaN | NaN | 597.5396 | NaN | 20.7815 | NaN | 27.7316
1353.1292 | 12.7809 | 12.5191 | 12.6148 | 12.9537 | 12.3356 | 12.6372 | 12.3588 | 12.2181 | NaN | NaN | NaN | 12.8557 | 92.7857 | NaN | NaN | NaN | -5.2717 | NaN | NaN | NaN | NaN | 596.3509 | NaN | 24.9622 | NaN | 27.7436
1354.1292 | 12.9894 | 12.7085 | 12.6198 | 12.942 | 12.2884 | 12.7129 | 12.4115 | 12.215 | NaN | NaN | NaN | 12.7975 | 90.9973 | NaN | NaN | NaN | 18.5727 | NaN | NaN | NaN | NaN | 595.6696 | NaN | 20.9929 | NaN | 27.265
1355.1292 | 12.8349 | 12.6573 | 12.6175 | 12.9035 | 12.2357 | 12.7733 | 12.4066 | 12.2153 | NaN | NaN | NaN | 12.8484 | 91.8477 | NaN | NaN | NaN | -5.5814 | NaN | NaN | NaN | NaN | 594.7737 | NaN | 25.316 | NaN | 26.5743
1356.1292 | 12.8313 | 12.6521 | 12.6144 | 12.9414 | 12.3131 | 12.7378 | 12.4171 | 12.216 | NaN | NaN | NaN | 12.816 | 91.4353 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 592.7936 | NaN | 22.1931 | NaN | 25.1325
1357.1292 | 12.8308 | 12.9957 | 12.6193 | 13.0573 | 12.2335 | 13.036 | 12.4579 | 12.2138 | NaN | NaN | NaN | 12.7644 | 92.5757 | NaN | NaN | NaN | -1.5373 | NaN | NaN | NaN | NaN | 595.9179 | NaN | 22.4308 | NaN | 26.2166
1358.1292 | 12.774 | 12.6682 | 12.6229 | 12.9306 | 12.2035 | 12.7549 | 12.4195 | 12.2198 | NaN | NaN | NaN | 12.7981 | 92.8392 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 595.6194 | NaN | 26.9543 | NaN | 28.3365
1359.1292 | 12.8882 | 12.879 | 12.6217 | 12.9508 | 12.3001 | 12.8353 | 12.4452 | 12.2157 | NaN | NaN | NaN | 12.7784 | 92.4608 | NaN | NaN | NaN | -14.2959 | NaN | NaN | NaN | NaN | 591.8674 | NaN | 24.0297 | NaN | 26.7895
1360.1292 | 12.8112 | 12.6566 | 12.6201 | 12.9774 | 12.3204 | 12.7239 | 12.4123 | 12.2157 | NaN | NaN | NaN | 12.8305 | 93.2903 | NaN | NaN | NaN | -10.8048 | NaN | NaN | NaN | NaN | 593.4363 | NaN | 25.0637 | NaN | 26.7169
1361.1292 | 12.8128 | 12.6152 | 12.6185 | 12.9801 | 12.3136 | 12.7245 | 12.4005 | 12.2144 | NaN | NaN | NaN | 12.7803 | 89.4333 | NaN | NaN | NaN | 15.7653 | NaN | NaN | NaN | NaN | 592.7943 | NaN | 23.993 | NaN | 27.6366
1362.1292 | 12.8205 | 12.6648 | 12.6183 | 12.8879 | 12.1726 | 12.701 | 12.3951 | 12.2049 | NaN | NaN | NaN | 12.8636 | 97.9181 | NaN | NaN | NaN | -19.9188 | NaN | NaN | NaN | NaN | 594.548 | NaN | 24.9162 | NaN | 27.2843
1363.1292 | 12.7906 | 12.6872 | 12.6197 | 12.9085 | 12.3186 | 12.8123 | 12.4291 | 12.2089 | NaN | NaN | NaN | 12.8389 | 90.4839 | NaN | NaN | NaN | -12.7743 | NaN | NaN | NaN | NaN | 591.7963 | NaN | 23.3418 | NaN | 27.6582
1364.1292 | 12.8549 | 12.6122 | 12.6201 | 12.9404 | 12.309 | 12.7132 | 12.403 | 12.2017 | NaN | NaN | NaN | 12.7652 | 91.1225 | NaN | NaN | NaN | -9.3183 | NaN | NaN | NaN | NaN | 587.8264 | NaN | 21.0491 | NaN | 25.9748
1365.1292 | 12.8278 | 12.5906 | 12.6211 | 12.9455 | 12.2983 | 12.6896 | 12.3973 | 12.2008 | NaN | NaN | NaN | 12.8897 | 92.6436 | NaN | NaN | NaN | -0.4477 | NaN | NaN | NaN | NaN | 590.6356 | NaN | 23.1338 | NaN | 24.7924
1366.1292 | 12.7938 | 12.5881 | 12.6227 | 12.9216 | 12.2997 | 12.713 | 12.3978 | 12.2043 | NaN | NaN | NaN | 12.8012 | 93.1632 | NaN | NaN | NaN | -11.9976 | NaN | NaN | NaN | NaN | 593.3912 | NaN | 23.4117 | NaN | 27.7712
1367.1292 | 12.8263 | 12.6545 | 12.6223 | 12.8947 | 12.2649 | 12.7743 | 12.4233 | 12.1957 | NaN | NaN | NaN | 12.7728 | 91.7148 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 592.74 | NaN | 23.7839 | NaN | 26.1643
1368.1292 | 12.8521 | 12.6037 | 12.6211 | 12.9371 | 12.2553 | 12.7686 | 12.4071 | 12.1981 | NaN | NaN | NaN | 12.8277 | 91.9686 | NaN | NaN | NaN | -13.5203 | NaN | NaN | NaN | NaN | 588.1039 | NaN | 25.0949 | NaN | 28.2122
1369.1292 | 12.858 | 12.5736 | 12.6211 | 12.8849 | 12.3338 | 12.6517 | 12.3708 | 12.1955 | NaN | NaN | NaN | 12.7339 | 91.551 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 588.7141 | NaN | 21.4439 | NaN | 27.612
1370.1292 | 12.8436 | 12.6252 | 12.6238 | 12.9253 | 12.2356 | 12.7541 | 12.3798 | 12.197 | NaN | NaN | NaN | 12.7572 | 91.4207 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 591.5977 | NaN | 25.4351 | NaN | 27.5006
1371.1292 | 12.8197 | 12.5541 | 12.6192 | 13.0085 | 12.3616 | 12.6866 | 12.3885 | 12.1963 | NaN | NaN | NaN | 12.7621 | 91.8253 | NaN | NaN | NaN | -15.955 | NaN | NaN | NaN | NaN | 594.4742 | NaN | 25.346 | NaN | 26.3573
1372.1292 | 13.006 | 12.8909 | 12.6199 | 12.926 | 12.1847 | 12.7949 | 12.4472 | 12.1958 | NaN | NaN | NaN | 12.7691 | 92.2769 | NaN | NaN | NaN | 1.1012 | NaN | NaN | NaN | NaN | 591.3493 | NaN | 24.4756 | NaN | 27.1975
1373.1292 | 12.8734 | 13.0364 | 12.6216 | 12.9055 | 12.2451 | 13.0832 | 12.5026 | 12.1884 | NaN | NaN | NaN | 12.7538 | 91.9507 | NaN | NaN | NaN | -16.475 | NaN | NaN | NaN | NaN | 589.6497 | NaN | 26.0367 | NaN | 27.5035
1374.1292 | 12.8121 | 12.8931 | 12.6181 | 12.9544 | 12.2786 | 12.9632 | 12.4129 | 12.1999 | NaN | NaN | NaN | 12.7546 | 91.138 | NaN | NaN | NaN | -16.5099 | NaN | NaN | NaN | NaN | 590.6218 | NaN | 23.2063 | NaN | 26.9967
1375.1292 | 12.9061 | 12.6125 | 12.6147 | 12.9121 | 12.3267 | 12.7319 | 12.406 | 12.1951 | NaN | NaN | NaN | 12.7419 | 93.0181 | NaN | NaN | NaN | 14.3398 | NaN | NaN | NaN | NaN | 591.0947 | NaN | 24.312 | NaN | 27.6846
1376.1292 | 12.8287 | 12.647 | 12.611 | 12.913 | 12.335 | 12.6815 | 12.3815 | 12.1864 | NaN | NaN | NaN | 12.7461 | 91.3313 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 591.8395 | NaN | 21.7957 | NaN | 27.4989
1377.1292 | 12.8872 | 12.5808 | 12.6147 | 12.9398 | 12.3267 | 12.7171 | 12.3847 | 12.1922 | NaN | NaN | NaN | 12.8137 | 91.4961 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 593.1541 | NaN | 22.9113 | NaN | 26.5744
1378.1292 | 12.8642 | 12.6156 | 12.6201 | 12.9383 | 12.2713 | 12.7605 | 12.4002 | 12.194 | NaN | NaN | NaN | 12.7432 | 91.0708 | NaN | NaN | NaN | 11.5563 | NaN | NaN | NaN | NaN | 593.0866 | NaN | 25.9514 | NaN | 26.7905
1379.1292 | 12.7687 | 12.6426 | 12.6276 | 12.9346 | 12.3263 | 12.7508 | 12.4151 | 12.1891 | NaN | NaN | NaN | 12.8271 | 93.795 | NaN | NaN | NaN | -14.6878 | NaN | NaN | NaN | NaN | 592.3195 | NaN | 22.3812 | NaN | 24.6169
1380.1292 | 12.8028 | 12.5463 | 12.6331 | 12.9086 | 12.2595 | 12.7191 | 12.3917 | 12.2009 | NaN | NaN | NaN | 12.7465 | 91.9825 | NaN | NaN | NaN | -17.4093 | NaN | NaN | NaN | NaN | 592.9841 | NaN | 21.3108 | NaN | 26.5924
1381.1292 | 12.8136 | 12.6351 | 12.6305 | 12.8772 | 12.2619 | 12.653 | 12.3901 | 12.1964 | NaN | NaN | NaN | 12.7532 | 92.0522 | NaN | NaN | NaN | -5.8501 | NaN | NaN | NaN | NaN | 590.0294 | NaN | 26.4594 | NaN | 26.4464
1382.1292 | 12.7955 | 13.1197 | 12.6316 | 12.8801 | 12.2195 | 12.9638 | 12.4839 | 12.1986 | NaN | NaN | NaN | 12.723 | 91.8965 | NaN | NaN | NaN | -10.1336 | NaN | NaN | NaN | NaN | 592.4744 | NaN | 23.1056 | NaN | 27.0711
1383.1292 | 12.7799 | 12.6109 | 12.6315 | 12.9268 | 12.3056 | 12.7098 | 12.3896 | 12.1983 | NaN | NaN | NaN | 12.7243 | 91.3989 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 592.0239 | NaN | 24.5295 | NaN | 27.1099
1384.1292 | 12.8162 | 12.6043 | 12.6279 | 12.959 | 12.2082 | 12.6717 | 12.3825 | 12.1904 | NaN | NaN | NaN | 12.7198 | 91.7638 | NaN | NaN | NaN | 0.7439 | NaN | NaN | NaN | NaN | 589.6059 | NaN | 20.2194 | NaN | 28.3612
1385.1292 | 12.776 | 12.5404 | 12.6284 | 12.878 | 12.325 | 12.6691 | 12.3801 | 12.196 | NaN | NaN | NaN | 12.7237 | 92.8452 | NaN | NaN | NaN | -4.0682 | NaN | NaN | NaN | NaN | 592.4268 | NaN | 21.1912 | NaN | 26.8292
1386.1292 | 12.7962 | 12.8781 | 12.6286 | 12.9351 | 12.3006 | 12.9124 | 12.4509 | 12.1985 | NaN | NaN | NaN | 12.7365 | 91.2692 | NaN | NaN | NaN | 6.0848 | NaN | NaN | NaN | NaN | 594.0922 | NaN | 25.0494 | NaN | 27.1865
1387.1292 | 12.8128 | 12.8661 | 12.6247 | 12.8804 | 12.2673 | 12.9546 | 12.478 | 12.1953 | NaN | NaN | NaN | 12.718 | 91.7154 | NaN | NaN | NaN | -12.1144 | NaN | NaN | NaN | NaN | 594.8227 | NaN | 23.8497 | NaN | 28.3988
1388.1292 | 12.8007 | 12.5701 | 12.6276 | 12.8943 | 12.3039 | 12.7272 | 12.3829 | 12.1911 | NaN | NaN | NaN | 12.7384 | 93.3305 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 594.5799 | NaN | 24.8758 | NaN | 26.5779
1389.1292 | 12.825 | 12.7624 | 12.6303 | 13.0062 | 12.202 | 12.7716 | 12.4402 | 12.1937 | NaN | NaN | NaN | 12.7639 | 91.6568 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 594.4922 | NaN | 22.5532 | NaN | 25.0989
1390.1292 | 12.8084 | 12.5373 | 12.6292 | 12.8942 | 12.2899 | 12.6691 | 12.3825 | 12.1948 | NaN | NaN | NaN | 12.7461 | 91.9166 | NaN | NaN | NaN | 24.1293 | NaN | NaN | NaN | NaN | 592.095 | NaN | 26.543 | NaN | 25.0524
1391.1292 | 12.8435 | 12.7356 | 12.6288 | 12.9603 | 12.2062 | 12.8371 | 12.4172 | 12.1922 | NaN | NaN | NaN | 12.6953 | 92.7293 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 594.6845 | NaN | 25.6264 | NaN | 26.2198
1392.1292 | 12.8152 | 12.578 | 12.6288 | 12.8959 | 12.2363 | 12.7384 | 12.4022 | 12.1903 | NaN | NaN | NaN | 12.8197 | 91.2024 | NaN | NaN | NaN | 2.7337 | NaN | NaN | NaN | NaN | 590.5036 | NaN | 26.1261 | NaN | 26.2245
1393.1292 | 12.783 | 12.5932 | 12.6216 | 12.8814 | 12.2733 | 12.7331 | 12.3981 | 12.1896 | NaN | NaN | NaN | 12.7994 | 93.2662 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 594.1978 | NaN | 23.977 | NaN | 26.1599
1394.1292 | 12.839 | 12.5521 | 12.6335 | 12.913 | 12.2579 | 12.6734 | 12.3725 | 12.1883 | NaN | NaN | NaN | 12.7344 | 96.1527 | NaN | NaN | NaN | 1.7723 | NaN | NaN | NaN | NaN | 593.8009 | NaN | 24.3441 | NaN | 26.0831
1395.1292 | 12.8484 | 12.542 | 12.6317 | 12.8874 | 12.2862 | 12.6996 | 12.3812 | 12.1899 | NaN | NaN | NaN | 12.7281 | 92.1295 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 593.9609 | NaN | 21.822 | NaN | 28.1671
1396.1292 | 12.9451 | 12.6034 | 12.6359 | 12.9259 | 12.3415 | 12.708 | 12.3763 | 12.1903 | NaN | NaN | NaN | 12.6958 | 91.1223 | NaN | NaN | NaN | -5.1515 | NaN | NaN | NaN | NaN | 593.9702 | NaN | 20.9264 | NaN | 24.5384
1397.1292 | 12.779 | 12.5895 | 12.6274 | 12.8352 | 12.276 | 12.7218 | 12.3856 | 12.1833 | NaN | NaN | NaN | 12.6855 | 91.4162 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 595.9814 | NaN | 21.8969 | NaN | 26.2461
1398.1292 | 12.7643 | 12.576 | 12.6277 | 12.8722 | 12.2699 | 12.708 | 12.3894 | 12.1881 | NaN | NaN | NaN | 12.6736 | 93.3851 | NaN | NaN | NaN | -3.5596 | NaN | NaN | NaN | NaN | 591.7664 | NaN | 25.0448 | NaN | 26.5549
1399.1292 | 12.798 | 13.039 | 12.6338 | 12.9591 | 12.2158 | 12.9426 | 12.5386 | 12.1856 | NaN | NaN | NaN | 12.6973 | 91.645 | NaN | NaN | NaN | -10.8286 | NaN | NaN | NaN | NaN | 592.6986 | NaN | 22.5124 | NaN | 27.372
1400.1292 | 13.1282 | 12.5453 | 12.6271 | 12.9114 | 12.1494 | 12.7043 | 12.3764 | 12.1825 | NaN | NaN | NaN | 12.724 | 93.6992 | NaN | NaN | NaN | 12.5215 | NaN | NaN | NaN | NaN | 594.2009 | NaN | 22.2247 | NaN | 26.5642
1401.1292 | 12.8243 | 12.6422 | 12.6369 | 13.0615 | 12.2523 | 12.7871 | 12.4168 | 12.1839 | NaN | NaN | NaN | 12.6759 | 91.4822 | NaN | NaN | NaN | -6.5755 | NaN | NaN | NaN | NaN | 594.2463 | NaN | 23.1171 | NaN | 26.6188
1402.1292 | 12.8351 | 12.6162 | 12.6265 | 12.8805 | 12.3438 | 12.7542 | 12.4004 | 12.1821 | NaN | NaN | NaN | 12.7191 | 92.6765 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 593.5701 | NaN | 20.9097 | NaN | 28.6477
1403.1292 | 12.8184 | 12.7601 | 12.6401 | 12.878 | 12.1185 | 12.8268 | 12.4185 | 12.1843 | NaN | NaN | NaN | 12.7122 | 91.8365 | NaN | NaN | NaN | 3.3349 | NaN | NaN | NaN | NaN | 594.1089 | NaN | 21.8192 | NaN | 26.4729
1404.1292 | 12.7827 | 12.5975 | 12.6323 | 12.8878 | 12.2971 | 12.7278 | 12.3828 | 12.1826 | NaN | NaN | NaN | 12.7182 | 91.8929 | NaN | NaN | NaN | -17.0453 | NaN | NaN | NaN | NaN | 593.8662 | NaN | 21.6115 | NaN | 24.5205
1405.1292 | 12.84 | 12.5567 | 12.6405 | 12.8752 | 12.1528 | 12.662 | 12.3599 | 12.1817 | NaN | NaN | NaN | 12.6854 | 91.7432 | NaN | NaN | NaN | -3.6688 | NaN | NaN | NaN | NaN | 590.782 | NaN | 24.2489 | NaN | 27.1997
1406.1292 | 12.7545 | 12.5068 | 12.6397 | 12.9338 | 12.2133 | 12.6452 | 12.3536 | 12.184 | NaN | NaN | NaN | 12.6795 | 91.8565 | NaN | NaN | NaN | 14.5998 | NaN | NaN | NaN | NaN | 591.4058 | NaN | 20.5357 | NaN | 25.7992
1407.1292 | 12.811 | 12.491 | 12.6305 | 12.9118 | 12.4493 | 12.5915 | 12.3357 | 12.1849 | NaN | NaN | NaN | 12.6668 | 112.2768 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 571.2021 | NaN | 17.4262 | NaN | 18.4698
1408.1292 | 12.8092 | 12.4518 | 12.6307 | 12.9081 | 12.359 | 12.5544 | 12.3174 | 12.1865 | NaN | NaN | NaN | 12.6591 | 131.2265 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 556.2141 | NaN | 20.2877 | NaN | 19.4653
1409.1292 | 12.8002 | 12.4406 | 12.6355 | 12.8967 | 12.3717 | 12.5566 | 12.3161 | 12.1818 | NaN | NaN | NaN | 12.6926 | 128.3211 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 557.7166 | NaN | 16.714 | NaN | 16.0155
1410.1292 | 12.8087 | 12.4877 | 12.6439 | 12.8713 | 12.4806 | 12.5751 | 12.3291 | 12.1828 | NaN | NaN | NaN | 12.7024 | 117.9612 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 553.5097 | NaN | 19.4557 | NaN | 19.4911
1411.1292 | 12.8023 | 12.4711 | 12.6441 | 12.9205 | 12.3569 | 12.5738 | 12.3225 | 12.1791 | NaN | NaN | NaN | 12.6694 | 117.7164 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 553.8578 | NaN | 13.8226 | NaN | 9.6245
1412.1292 | 12.7765 | 12.4735 | 12.6421 | 12.9086 | 12.4769 | 12.5649 | 12.3163 | 12.1786 | NaN | NaN | NaN | 12.6519 | 124.8649 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 548.2257 | NaN | 23.6591 | NaN | 18.848
1413.1292 | 12.8859 | 12.4848 | 12.6401 | 12.9135 | 12.4426 | 12.5741 | 12.3202 | 12.1821 | NaN | NaN | NaN | 12.67 | 121.1113 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 548.4373 | NaN | 22.4798 | NaN | 17.1446
1414.1292 | 12.8164 | 12.4666 | 12.644 | 12.9205 | 12.4659 | 12.5649 | 12.3222 | 12.1841 | NaN | NaN | NaN | 12.6627 | 119.0941 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 545.414 | NaN | 24.3394 | NaN | 19.7783
1415.1292 | 12.8631 | 12.5028 | 12.6435 | 12.9075 | 12.4269 | 12.5739 | 12.3253 | 12.1757 | NaN | NaN | NaN | 12.6588 | 125.4772 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 547.9018 | NaN | 21.2993 | NaN | 18.8199
1416.1292 | 12.9386 | 12.4368 | 12.6365 | 12.9127 | 12.4202 | 12.56 | 12.3152 | 12.1723 | NaN | NaN | NaN | 12.6621 | 125.1419 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 546.9886 | NaN | 13.0997 | NaN | 18.2331
1417.1292 | 12.8257 | 12.5639 | 12.641 | 12.8793 | 12.4308 | 12.6339 | 12.348 | 12.1751 | NaN | NaN | NaN | 12.6415 | 119.2919 | NaN | NaN | NaN | -8.7718 | NaN | NaN | NaN | NaN | 548.0776 | NaN | 16.2989 | NaN | 17.5914
1418.1292 | 12.8257 | 12.4494 | 12.6414 | 12.8509 | 12.4452 | 12.5912 | 12.3161 | 12.1693 | NaN | NaN | NaN | 12.6706 | 131.8155 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 549.9687 | NaN | 10.4974 | NaN | 15.0341
1419.1292 | 12.8169 | 12.4454 | 12.641 | 12.8833 | 12.4049 | 12.5838 | 12.3054 | 12.1706 | NaN | NaN | NaN | 12.6589 | 132.1971 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 548.8343 | NaN | 18.6707 | NaN | 8.9995
1420.1292 | 12.8219 | 12.4234 | 12.6414 | 12.884 | 12.4068 | 12.5785 | 12.312 | 12.1708 | NaN | NaN | NaN | 12.6704 | 124.0592 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 546.5562 | NaN | 30.2339 | NaN | 12.7167
1421.1292 | 12.9183 | 12.4244 | 12.631 | 12.9189 | 12.37 | 12.5824 | 12.3101 | 12.1634 | NaN | NaN | NaN | 12.646 | 128.0416 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -11.6307 | 546.7464 | NaN | 15.2568 | NaN | 18.3032
1422.1292 | 12.8098 | 12.4945 | 12.6272 | 12.9167 | 12.3715 | 12.6172 | 12.3168 | 12.1582 | NaN | NaN | NaN | 12.6432 | 125.038 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 545.6401 | NaN | 17.7048 | NaN | 16.243
1423.1292 | 12.8619 | 12.4317 | 12.6311 | 12.9252 | 12.4053 | 12.5809 | 12.3141 | 12.1612 | NaN | NaN | NaN | 12.6302 | 119.9622 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 545.8068 | NaN | 21.2742 | NaN | 18.1104
1424.1292 | 12.9124 | 12.4919 | 12.6298 | 12.8707 | 12.3951 | 12.6084 | 12.3254 | 12.1611 | NaN | NaN | NaN | 12.6544 | 116.7821 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 547.9494 | NaN | 12.8723 | NaN | 19.6583
1425.1292 | 12.8069 | 12.4394 | 12.6295 | 12.8938 | 12.3535 | 12.5941 | 12.3156 | 12.1605 | NaN | NaN | NaN | 12.6358 | 125.074 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 549.2008 | NaN | 22.3886 | NaN | 19.0038
1426.1292 | 12.805 | 12.4652 | 12.6372 | 12.8733 | 12.4285 | 12.5955 | 12.3111 | 12.1608 | NaN | NaN | NaN | 12.6441 | 116.8904 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 548.6353 | NaN | 21.3032 | NaN | 18.8208
1427.1292 | 12.8105 | 12.4425 | 12.6334 | 12.9494 | 12.4824 | 12.5779 | 12.313 | 12.1551 | NaN | NaN | NaN | 12.6417 | 126.6551 | NaN | NaN | NaN | -3.7079 | NaN | NaN | NaN | NaN | 548.3842 | NaN | 14.7134 | NaN | 21.2501
1428.1292 | 12.8178 | 12.4716 | 12.635 | 12.9203 | 12.4024 | 12.5847 | 12.3077 | 12.1548 | NaN | NaN | NaN | 12.6532 | 129.8422 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 548.3049 | NaN | 24.5988 | NaN | 16.5075
1429.1292 | 12.8193 | 12.4824 | 12.625 | 12.8891 | 12.3868 | 12.6125 | 12.3156 | 12.1539 | NaN | NaN | NaN | 12.6353 | 133.6863 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 546.5598 | NaN | 21.7595 | NaN | 18.6648
1430.1292 | 12.8074 | 12.4352 | 12.6317 | 12.9168 | 12.3381 | 12.5865 | 12.3111 | 12.1506 | NaN | NaN | NaN | 12.6692 | 115.1366 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 543.6702 | NaN | 12.6994 | NaN | 17.6013
1431.1292 | 12.8159 | 12.4405 | 12.6304 | 12.9085 | 12.4002 | 12.5704 | 12.306 | 12.1473 | NaN | NaN | NaN | 12.6238 | 117.1888 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 545.5973 | NaN | 15.5473 | NaN | 14.4416
1432.1292 | 12.8302 | 12.535 | 12.6276 | 12.8699 | 12.4545 | 12.611 | 12.3227 | 12.1507 | NaN | NaN | NaN | 12.6625 | 133.3473 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 549.2932 | NaN | 9.8318 | NaN | 14.3254
1433.1292 | 12.8335 | 12.4687 | 12.6292 | 12.9167 | 12.4189 | 12.5857 | 12.3148 | 12.1619 | NaN | NaN | NaN | 12.6352 | 137.2602 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 546.425 | NaN | 12.1915 | NaN | 19.33
1434.1292 | 12.8289 | 12.4571 | 12.6358 | 12.9042 | 12.3675 | 12.5825 | 12.3202 | 12.1527 | NaN | NaN | NaN | 12.6442 | 126.33 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 547.9326 | NaN | 16.3357 | NaN | 12.6264
1435.1292 | 12.8301 | 12.4457 | 12.6327 | 12.9197 | 12.3761 | 12.5667 | 12.3107 | 12.1515 | NaN | NaN | NaN | 12.707 | 124.4712 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 549.0111 | NaN | 26.2466 | NaN | 18.0193
1436.1292 | 12.8281 | 12.438 | 12.6319 | 12.8762 | 12.4101 | 12.5707 | 12.308 | 12.1575 | NaN | NaN | NaN | 12.7322 | 122.3314 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 547.6799 | NaN | 30.3393 | NaN | 18.6947
1437.1292 | 12.8312 | 12.4634 | 12.6335 | 12.9357 | 12.4501 | 12.5764 | 12.3017 | 12.1528 | NaN | NaN | NaN | 12.7056 | 120.5133 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 550.0908 | NaN | 36.0943 | NaN | 19.0434
1438.1292 | 12.8265 | 12.4347 | 12.6291 | 12.9263 | 12.4269 | 12.5612 | 12.3016 | 12.1541 | NaN | NaN | NaN | 12.6783 | 123.3029 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 547.4445 | NaN | 26.0139 | NaN | 17.6003
1439.1292 | 12.8214 | 12.4307 | 12.6275 | 12.9135 | 12.3597 | 12.5675 | 12.3084 | 12.1593 | NaN | NaN | NaN | 12.6984 | 121.7049 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 548.5016 | NaN | 13.314 | NaN | 18.1354
1440.1292 | 12.8219 | 12.4344 | 12.6202 | 12.968 | 12.4542 | 12.5504 | 12.3036 | 12.1548 | NaN | NaN | NaN | 12.6732 | 123.5797 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 550.4395 | NaN | 18.6923 | NaN | 16.0799
1441.1292 | 12.8154 | 12.4374 | 12.6239 | 12.924 | 12.4809 | 12.552 | 12.3105 | 12.1557 | NaN | NaN | NaN | 12.6956 | 122.3951 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 546.6216 | NaN | 13.4108 | NaN | 17.1995
1442.1292 | 12.7821 | 12.4671 | 12.6224 | 12.8898 | 12.439 | 12.5657 | 12.314 | 12.1534 | NaN | NaN | NaN | 12.6864 | 119.7581 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 548.7284 | NaN | 22.9133 | NaN | 18.5902
1443.1292 | 12.7891 | 12.444 | 12.6201 | 12.9564 | 12.3343 | 12.5846 | 12.3166 | 12.1508 | NaN | NaN | NaN | 12.6931 | 131.256 | NaN | NaN | NaN | -16.5486 | NaN | NaN | NaN | NaN | 549.2161 | NaN | 11.8665 | NaN | 19.2121
1444.1292 | 12.8051 | 12.4682 | 12.6199 | 12.944 | 12.4448 | 12.5792 | 12.3076 | 12.1492 | NaN | NaN | NaN | 12.6507 | 122.1749 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 547.5227 | NaN | 24.6864 | NaN | 6.2421
1445.1292 | 12.8087 | 12.4197 | 12.6153 | 12.882 | 12.3759 | 12.562 | 12.3055 | 12.1564 | NaN | NaN | NaN | 12.6715 | 125.507 | NaN | NaN | NaN | -0.9234 | NaN | NaN | NaN | NaN | 548.7603 | NaN | 16.5766 | NaN | 25.6314
1446.1292 | 12.8013 | 12.4121 | 12.6137 | 12.9116 | 12.4188 | 12.5446 | 12.3091 | 12.1502 | NaN | NaN | NaN | 12.6636 | 117.3297 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 545.0702 | NaN | 16.0356 | NaN | 16.5188
1447.1292 | 12.8141 | 12.4511 | 12.6088 | 12.8879 | 12.44 | 12.5607 | 12.3078 | 12.1544 | NaN | NaN | NaN | 12.6602 | 126.6315 | NaN | NaN | NaN | -17.7088 | NaN | NaN | NaN | NaN | 546.8548 | NaN | 15.561 | NaN | 18.2564
1448.1292 | 12.8148 | 12.4151 | 12.6107 | 12.906 | 12.3703 | 12.5588 | 12.309 | 12.1527 | NaN | NaN | NaN | 12.69 | 114.0174 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 547.4499 | NaN | 11.6951 | NaN | 14.9465
1449.1292 | 12.8172 | 12.4144 | 12.6067 | 12.9034 | 12.3956 | 12.5555 | 12.3081 | 12.1508 | NaN | NaN | NaN | 12.6767 | 136.9863 | NaN | NaN | NaN | -10.0916 | NaN | NaN | NaN | NaN | 541.7465 | NaN | 12.2806 | NaN | 20.0394
1450.1292 | 12.8167 | 12.457 | 12.6023 | 12.884 | 12.3628 | 12.5817 | 12.3127 | 12.1596 | NaN | NaN | NaN | 12.6696 | 118.8788 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 540.625 | NaN | 21.1858 | NaN | 17.1447
1451.1292 | 12.8157 | 12.4007 | 12.6004 | 12.88 | 12.4091 | 12.5561 | 12.3044 | 12.1545 | NaN | NaN | NaN | 12.6594 | 128.9236 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 541.4285 | NaN | 30.6095 | NaN | 19.6044
1452.1292 | 12.8106 | 12.3971 | 12.6041 | 12.8784 | 12.4305 | 12.557 | 12.3093 | 12.1471 | NaN | NaN | NaN | 12.6853 | 121.0766 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 543.2152 | NaN | 26.9591 | NaN | 19.1561
1453.1292 | 12.8205 | 12.4683 | 12.6057 | 12.8805 | 12.422 | 12.5841 | 12.3189 | 12.1434 | NaN | NaN | NaN | 12.6611 | 121.3109 | NaN | NaN | NaN | -4.7748 | NaN | NaN | NaN | NaN | 541.9062 | NaN | 19.0527 | NaN | 19.0746
1454.1292 | 12.8132 | 12.4202 | 12.6036 | 12.9214 | 12.4243 | 12.5708 | 12.3117 | 12.1516 | NaN | NaN | NaN | 12.6438 | 117.491 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 543.6823 | NaN | 18.5658 | NaN | 18.7066
1455.1292 | 12.8207 | 12.3952 | 12.6051 | 12.9307 | 12.4053 | 12.5635 | 12.3143 | 12.1519 | NaN | NaN | NaN | 12.6536 | 118.4486 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 539.4348 | NaN | 27.2891 | NaN | 18.5613
1456.1292 | 12.7906 | 12.4169 | 12.602 | 12.9314 | 12.3277 | 12.5687 | 12.3062 | 12.1431 | NaN | NaN | NaN | 12.6601 | 114.9529 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 535.5375 | NaN | 24.8738 | NaN | 16.4094
1457.1292 | 12.791 | 12.5203 | 12.5986 | 12.9712 | 12.3918 | 12.5927 | 12.324 | 12.1408 | NaN | NaN | NaN | 12.6554 | 135.5588 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 537.1517 | NaN | 31.2961 | NaN | 19.3747
1458.1292 | 12.8634 | 12.3864 | 12.6006 | 12.8921 | 12.4575 | 12.5547 | 12.306 | 12.1392 | NaN | NaN | NaN | 12.6422 | 127.6266 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 536.7939 | NaN | 24.4309 | NaN | 17.9643
1459.1292 | 12.9594 | 12.3846 | 12.5948 | 12.8744 | 12.4243 | 12.5481 | 12.3119 | 12.1337 | NaN | NaN | NaN | 12.6504 | 128.4554 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 539.0242 | NaN | 20.5127 | NaN | 18.7099
1460.1292 | 12.9004 | 12.4153 | 12.5975 | 12.9031 | 12.3433 | 12.5738 | 12.3139 | 12.1331 | NaN | NaN | NaN | 12.6477 | 127.0178 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 540.0256 | NaN | 28.3761 | NaN | 17.1578
1461.1292 | 12.9051 | 12.4338 | 12.5898 | 12.9023 | 12.3654 | 12.5515 | 12.315 | 12.1371 | NaN | NaN | NaN | 12.6028 | 128.8924 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 537.0768 | NaN | 32.9634 | NaN | 16.728
1462.1292 | 12.8311 | 12.4419 | 12.5867 | 12.8768 | 12.3353 | 12.5596 | 12.3172 | 12.1261 | NaN | NaN | NaN | 12.6075 | 122.8792 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 539.3041 | NaN | 25.921 | NaN | 19.5578
1463.1292 | 12.7926 | 12.4737 | 12.5882 | 12.9088 | 12.3531 | 12.5898 | 12.3103 | 12.1405 | NaN | NaN | NaN | 12.6253 | 120.0159 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 539.0485 | NaN | 21.1308 | NaN | 18.7367
1464.1292 | 12.7721 | 12.4728 | 12.5926 | 12.9003 | 12.4018 | 12.5717 | 12.3219 | 12.1339 | NaN | NaN | NaN | 12.6227 | 125.7743 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 536.9272 | NaN | 11.7195 | NaN | 17.0989
1465.1292 | 12.7912 | 12.4049 | 12.5861 | 12.8612 | 12.3584 | 12.5478 | 12.3125 | 12.1422 | NaN | NaN | NaN | 12.6508 | 118.687 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 538.1485 | NaN | 32.2804 | NaN | 18.4697
1466.1292 | 12.7901 | 12.413 | 12.5917 | 12.9159 | 12.3787 | 12.536 | 12.2973 | 12.1365 | NaN | NaN | NaN | 12.6204 | 124.4341 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 536.1829 | NaN | 15.3972 | NaN | 17.7273
1467.1292 | 12.79 | 12.4402 | 12.5878 | 12.9055 | 12.3808 | 12.5526 | 12.3144 | 12.1362 | NaN | NaN | NaN | 12.6139 | 129.1871 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 536.7783 | NaN | 35.0956 | NaN | 18.3137
1468.1292 | 12.8014 | 12.4651 | 12.5899 | 12.9269 | 12.4423 | 12.5616 | 12.3186 | 12.1287 | NaN | NaN | NaN | 12.5773 | 116.8871 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 534.6778 | NaN | 28.0546 | NaN | 19.0235
1469.1292 | 12.8097 | 12.4052 | 12.5932 | 12.9111 | 12.3551 | 12.5532 | 12.3112 | 12.1344 | NaN | NaN | NaN | 12.5939 | 126.8865 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 535.0315 | NaN | 37.2496 | NaN | 18.8755
1470.1292 | 12.8127 | 12.4545 | 12.5888 | 12.8824 | 12.3357 | 12.5741 | 12.3042 | 12.1253 | NaN | NaN | NaN | 12.6031 | 120.8265 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 535.9948 | NaN | 36.5631 | NaN | 18.6493
1471.1292 | 12.8084 | 12.4127 | 12.5854 | 12.8998 | 12.4326 | 12.5492 | 12.3008 | 12.1305 | NaN | NaN | NaN | 12.6067 | 121.2332 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 535.2931 | NaN | 21.5474 | NaN | 15.8741
1472.1292 | 12.8237 | 12.5139 | 12.595 | 12.9142 | 12.4093 | 12.5985 | 12.3169 | 12.1222 | NaN | NaN | NaN | 12.5788 | 124.5127 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 535.537 | NaN | 31.3016 | NaN | 18.6536
1473.1292 | 12.8124 | 12.4533 | 12.5866 | 12.9055 | 12.4464 | 12.5636 | 12.3018 | 12.1307 | NaN | NaN | NaN | 12.6205 | 142.0663 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 529.5368 | NaN | 19.6392 | NaN | 16.4133
1474.1292 | 12.8211 | 12.4744 | 12.5934 | 12.8901 | 12.3554 | 12.5828 | 12.3074 | 12.1273 | NaN | NaN | NaN | 12.5951 | 123.7665 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 532.3373 | NaN | 15.7387 | NaN | 17.3874
1475.1292 | 12.8091 | 12.4211 | 12.5938 | 12.893 | 12.4233 | 12.5484 | 12.2976 | 12.1289 | NaN | NaN | NaN | 12.6366 | 129.4171 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 532.839 | NaN | 19.7083 | NaN | 18.2629
1476.1292 | 12.8137 | 12.4355 | 12.5979 | 12.9039 | 12.4162 | 12.5524 | 12.2993 | 12.1246 | NaN | NaN | NaN | 12.6056 | 117.4677 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 534.9254 | NaN | 22.4406 | NaN | 13.4396
1477.1292 | 12.8342 | 12.4092 | 12.6001 | 12.9319 | 12.3398 | 12.5649 | 12.2995 | 12.1335 | NaN | NaN | NaN | 12.5837 | 115.3897 | NaN | NaN | NaN | -7.9869 | NaN | NaN | NaN | NaN | 535.632 | NaN | 18.5825 | NaN | 20.3753
1478.1292 | 12.8271 | 12.4234 | 12.5982 | 12.8885 | 12.3652 | 12.5509 | 12.2977 | 12.1347 | NaN | NaN | NaN | 12.5864 | 117.2828 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 532.8601 | NaN | 34.0812 | NaN | 15.4186
1479.1292 | 12.8027 | 12.4409 | 12.5988 | 12.8953 | 12.3531 | 12.5705 | 12.3147 | 12.1394 | NaN | NaN | NaN | 12.5791 | 127.4702 | NaN | NaN | NaN | -0.092 | NaN | NaN | NaN | NaN | 533.8787 | NaN | 24.6627 | NaN | 17.9974
1480.1292 | 12.7993 | 12.4516 | 12.5959 | 12.943 | 12.3178 | 12.5734 | 12.3049 | 12.1365 | NaN | NaN | NaN | 12.5903 | 120.6308 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 535.8226 | NaN | 29.6086 | NaN | 14.3643
1481.1292 | 12.8065 | 12.472 | 12.5991 | 12.899 | 12.4217 | 12.5737 | 12.3105 | 12.1409 | NaN | NaN | NaN | 12.5906 | 122.2397 | NaN | NaN | NaN | -10.4354 | NaN | NaN | NaN | NaN | 534.8979 | NaN | 18.203 | NaN | 18.5278
1482.1292 | 12.8106 | 12.5085 | 12.6004 | 12.9112 | 12.3917 | 12.6031 | 12.3222 | 12.1433 | NaN | NaN | NaN | 12.5777 | 119.4377 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 534.5511 | NaN | 24.7866 | NaN | 27.8691
1483.1292 | 12.8008 | 12.4622 | 12.596 | 12.9244 | 12.335 | 12.5763 | 12.3128 | 12.1391 | NaN | NaN | NaN | 12.5841 | 128.7591 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 537.8244 | NaN | 19.0658 | NaN | 18.6475
1484.1292 | 12.7868 | 12.4517 | 12.5932 | 12.9324 | 12.3862 | 12.5725 | 12.3124 | 12.1368 | NaN | NaN | NaN | 12.5689 | 121.2006 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 537.2395 | NaN | 19.2138 | NaN | 15.3879
1485.1292 | 12.7927 | 12.4295 | 12.5814 | 12.9294 | 12.4389 | 12.5515 | 12.3023 | 12.1363 | NaN | NaN | NaN | 12.5679 | 119.1117 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 537.6874 | NaN | 22.9221 | NaN | 15.878
1486.1292 | 12.7834 | 12.5685 | 12.5826 | 12.9371 | 12.4052 | 12.608 | 12.3302 | 12.1372 | NaN | NaN | NaN | 12.5958 | 127.7149 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 537.3069 | NaN | 10.1511 | NaN | 15.7363
1487.1292 | 12.7908 | 12.4324 | 12.5798 | 12.9057 | 12.4349 | 12.5453 | 12.305 | 12.1452 | NaN | NaN | NaN | 12.5698 | 121.5718 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 537.2447 | NaN | 17.1459 | NaN | 8.092
1488.1292 | 12.7876 | 12.4382 | 12.5823 | 12.9015 | 12.355 | 12.5636 | 12.3075 | 12.1431 | NaN | NaN | NaN | 12.5938 | 120.0174 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 538.0957 | NaN | 23.0586 | NaN | 17.8242
1489.1292 | 12.7996 | 12.4512 | 12.5791 | 12.8792 | 12.3625 | 12.5718 | 12.3052 | 12.1464 | NaN | NaN | NaN | 12.6424 | 137.7685 | NaN | NaN | NaN | 1.3411 | NaN | NaN | NaN | NaN | 536.0952 | NaN | 20.0613 | NaN | 19.431
1490.1292 | 12.8061 | 12.4209 | 12.581 | 12.8749 | 12.3847 | 12.5443 | 12.2971 | 12.137 | NaN | NaN | NaN | 12.5672 | 133.5194 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 534.6926 | NaN | 27.4328 | NaN | 17.5295
1491.1292 | 12.8026 | 12.4495 | 12.5873 | 12.8595 | 12.4099 | 12.56 | 12.3018 | 12.137 | NaN | NaN | NaN | 12.6406 | 124.6437 | NaN | NaN | NaN | -17.1922 | NaN | NaN | NaN | NaN | 535.8795 | NaN | 13.2788 | NaN | 18.6826
1492.1292 | 12.8085 | 12.4451 | 12.5906 | 12.941 | 12.4096 | 12.5494 | 12.2905 | 12.1421 | NaN | NaN | NaN | 12.5789 | 114.9895 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 533.9657 | NaN | 32.2965 | NaN | 19.4363
1493.1292 | 12.8202 | 12.4231 | 12.5939 | 12.8864 | 12.4053 | 12.5406 | 12.2943 | 12.1385 | NaN | NaN | NaN | 12.5777 | 114.3148 | NaN | NaN | NaN | -14.5882 | NaN | NaN | NaN | NaN | 535.3287 | NaN | 16.4607 | NaN | 20.4994
1494.1292 | 12.8269 | 12.4723 | 12.5913 | 12.9014 | 12.4366 | 12.559 | 12.2977 | 12.1386 | NaN | NaN | NaN | 12.5773 | 124.3582 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 531.6381 | NaN | 37.3404 | NaN | 16.8096
1495.1292 | 12.8563 | 12.4349 | 12.5854 | 12.8883 | 12.355 | 12.5571 | 12.3051 | 12.1338 | NaN | NaN | NaN | 12.5718 | 120.3696 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 531.0756 | NaN | 14.1157 | NaN | 14.4026
1496.1292 | 12.8112 | 12.4799 | 12.5894 | 12.895 | 12.4263 | 12.5702 | 12.3092 | 12.1357 | NaN | NaN | NaN | 12.5661 | 124.1703 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 531.3365 | NaN | 22.49 | NaN | 19.0665
1497.1292 | 12.8246 | 12.475 | 12.5907 | 12.866 | 12.4188 | 12.5536 | 12.2989 | 12.1288 | NaN | NaN | NaN | 12.5948 | 129.7318 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 530.9207 | NaN | 19.7462 | NaN | 16.41
1498.1292 | 12.8236 | 12.4568 | 12.5919 | 12.9067 | 12.4068 | 12.5552 | 12.298 | 12.1281 | NaN | NaN | NaN | 12.5444 | 119.6487 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 529.589 | NaN | 11.5815 | NaN | 20.1964
1499.1292 | 12.7723 | 12.4437 | 12.5864 | 12.9062 | 12.4462 | 12.5416 | 12.2991 | 12.1302 | NaN | NaN | NaN | 12.5733 | 126.4898 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 530.6287 | NaN | 18.8821 | NaN | 17.9632
1500.1292 | 12.771 | 12.4777 | 12.582 | 12.8479 | 12.3494 | 12.5752 | 12.2948 | 12.1263 | NaN | NaN | NaN | 12.5753 | 132.2239 | NaN | NaN | NaN | -6.5531 | NaN | NaN | NaN | NaN | 531.0144 | NaN | 20.2177 | NaN | 17.2666
1501.1292 | 12.8037 | 12.4665 | 12.5911 | 12.9133 | 12.4141 | 12.5578 | 12.3034 | 12.1268 | NaN | NaN | NaN | 12.5696 | 116.2143 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -10.0177 | 530.0999 | NaN | 13.1857 | NaN | 20.8157
1502.1292 | 12.7726 | 12.4105 | 12.5949 | 12.937 | 12.4249 | 12.5414 | 12.2972 | 12.1226 | NaN | NaN | NaN | 12.6036 | 125.2948 | NaN | NaN | NaN | -12.5044 | NaN | NaN | NaN | NaN | 529.4418 | NaN | 18.8475 | NaN | 18.2842
1503.1292 | 12.785 | 12.4244 | 12.5943 | 12.896 | 12.3352 | 12.54 | 12.3049 | 12.125 | NaN | NaN | NaN | 12.6509 | 119.8695 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 526.8162 | NaN | 22.2127 | NaN | 20.1139
1504.1448 | 12.7782 | 12.4245 | 12.5908 | 12.8768 | 12.4337 | 12.5444 | 12.3041 | 12.1256 | NaN | NaN | NaN | 12.5677 | 122.5875 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 528.0098 | NaN | 11.6809 | NaN | 14.4742
1505.1292 | 12.7832 | 12.4966 | 12.5846 | 12.9181 | 12.2817 | 12.5886 | 12.3096 | 12.1299 | NaN | NaN | NaN | 12.5582 | 121.5538 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 530.0758 | NaN | 29.9842 | NaN | 16.6312
1506.1292 | 12.7818 | 12.4186 | 12.5923 | 12.9107 | 12.3616 | 12.5473 | 12.3015 | 12.1311 | NaN | NaN | NaN | 12.5422 | 131.357 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 530.1929 | NaN | 22.8477 | NaN | 8.1298
1507.1292 | 12.8047 | 12.451 | 12.5961 | 12.8935 | 12.4292 | 12.5661 | 12.3136 | 12.1316 | NaN | NaN | NaN | 12.5594 | 128.5392 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 529.2532 | NaN | 13.1127 | NaN | 9.3134
1508.1292 | 12.8106 | 12.4064 | 12.5986 | 12.8932 | 12.3348 | 12.5544 | 12.3098 | 12.1327 | NaN | NaN | NaN | 12.5581 | 120.4208 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 534.6688 | NaN | 12.0289 | NaN | 9.3021
1509.1292 | 12.8061 | 12.4205 | 12.5975 | 12.8673 | 12.3702 | 12.5613 | 12.3015 | 12.1294 | NaN | NaN | NaN | 12.6422 | 114.8901 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -17.0517 | 533.9169 | NaN | 25.9836 | NaN | 19.1695
1510.1292 | 12.8105 | 12.465 | 12.6012 | 12.866 | 12.3885 | 12.5815 | 12.3044 | 12.1219 | NaN | NaN | NaN | 12.6251 | 125.3028 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 531.4727 | NaN | 12.2193 | NaN | 15.4747
1511.1292 | 12.8119 | 12.4081 | 12.6018 | 12.9116 | 12.4003 | 12.5609 | 12.3122 | 12.1132 | NaN | NaN | NaN | 12.5637 | 127.8824 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 532.4206 | NaN | 27.0868 | NaN | 18.6411
1512.1292 | 12.8255 | 12.4518 | 12.6052 | 12.8903 | 12.3445 | 12.5696 | 12.2982 | 12.1219 | NaN | NaN | NaN | 12.5447 | 116.1259 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 533.1757 | NaN | 22.3941 | NaN | 18.5688
1513.1292 | 12.8107 | 12.4334 | 12.5987 | 12.9703 | 12.4108 | 12.5716 | 12.3093 | 12.1147 | NaN | NaN | NaN | 12.6038 | 122.0087 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 530.7159 | NaN | 20.2535 | NaN | 17.0108
1514.1292 | 12.8166 | 12.3928 | 12.5958 | 12.9207 | 12.3251 | 12.5599 | 12.3086 | 12.1175 | NaN | NaN | NaN | 12.5627 | 121.0991 | NaN | NaN | NaN | 1.5957 | NaN | NaN | NaN | NaN | 531.0889 | NaN | 19.5132 | NaN | 15.023
1515.1292 | 12.8117 | 12.4158 | 12.6024 | 12.8967 | 12.3233 | 12.5481 | 12.3025 | 12.1219 | NaN | NaN | NaN | 12.565 | 125.3147 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 527.4668 | NaN | 28.164 | NaN | 17.1904
1516.1292 | 12.8263 | 12.424 | 12.5974 | 12.8958 | 12.3675 | 12.5445 | 12.2978 | 12.116 | NaN | NaN | NaN | 12.5834 | 128.4406 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 525.6829 | NaN | 24.0097 | NaN | 8.6888
1517.1292 | 12.8187 | 12.4987 | 12.5963 | 12.8839 | 12.3513 | 12.5974 | 12.3072 | 12.1182 | NaN | NaN | NaN | 12.5608 | 124.8987 | NaN | NaN | NaN | -9.0785 | NaN | NaN | NaN | NaN | 532.1286 | NaN | 25.004 | NaN | 19.7944
1518.1292 | 12.8156 | 12.4437 | 12.5967 | 12.9192 | 12.4386 | 12.5727 | 12.3006 | 12.1131 | NaN | NaN | NaN | 12.5736 | 131.915 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 529.3492 | NaN | 14.4504 | NaN | 13.7585
1519.1292 | 12.8257 | 12.4527 | 12.5944 | 12.8897 | 12.4359 | 12.57 | 12.2953 | 12.1157 | NaN | NaN | NaN | 12.5656 | 133.9959 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 528.484 | NaN | 19.1066 | NaN | 19.4831
1520.1292 | 12.8075 | 12.438 | 12.59 | 12.9068 | 12.3448 | 12.5804 | 12.3038 | 12.1205 | NaN | NaN | NaN | 12.5762 | 130.9655 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 529.5445 | NaN | 10.013 | NaN | 18.0338
1521.1292 | 12.8027 | 12.4481 | 12.5867 | 12.8985 | 12.3752 | 12.5737 | 12.3 | 12.116 | NaN | NaN | NaN | 12.5751 | 117.135 | NaN | NaN | NaN | 4.1755 | NaN | NaN | NaN | NaN | 531.4293 | NaN | 10.4589 | NaN | 23.0844
1522.1292 | 12.8531 | 12.3994 | 12.581 | 12.8915 | 12.3861 | 12.556 | 12.294 | 12.1158 | NaN | NaN | NaN | 12.5927 | 130.8334 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 528.2042 | NaN | 28.0887 | NaN | 18.9662
1523.1292 | 12.8192 | 12.388 | 12.5755 | 12.8844 | 12.4103 | 12.5482 | 12.2883 | 12.1166 | NaN | NaN | NaN | 12.5832 | 126.5862 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 530.082 | NaN | 25.5291 | NaN | 18.7019
1524.1292 | 12.8161 | 12.3902 | 12.5839 | 12.9176 | 12.3146 | 12.5506 | 12.2862 | 12.1187 | NaN | NaN | NaN | 12.6021 | 119.4508 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 532.1799 | NaN | 18.0942 | NaN | 16.8502
1525.1292 | 12.824 | 12.435 | 12.581 | 12.893 | 12.4289 | 12.5649 | 12.2893 | 12.1199 | NaN | NaN | NaN | 12.5904 | 121.5604 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 531.3071 | NaN | 25.8424 | NaN | 19.2421
1526.1292 | 12.8317 | 12.4055 | 12.579 | 12.8826 | 12.4118 | 12.5497 | 12.2867 | 12.114 | NaN | NaN | NaN | 12.6002 | 116.5649 | NaN | NaN | NaN | -1.1542 | NaN | NaN | NaN | NaN | 530.5841 | NaN | 13.4388 | NaN | 19.3241
1527.1292 | 12.8008 | 12.396 | 12.5793 | 12.8805 | 12.4131 | 12.5605 | 12.2878 | 12.1131 | NaN | NaN | NaN | 12.6046 | 120.8454 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 530.8374 | NaN | 34.0628 | NaN | 21.2892
1528.1292 | 12.8031 | 12.5613 | 12.5771 | 12.8786 | 12.4221 | 12.6295 | 12.3266 | 12.1169 | NaN | NaN | NaN | 12.5981 | 118.3503 | NaN | NaN | NaN | -2.8513 | NaN | NaN | NaN | NaN | 529.4694 | NaN | 16.8251 | NaN | 19.7093
1529.1292 | 12.8083 | 12.4017 | 12.5804 | 12.8855 | 12.4096 | 12.5667 | 12.3032 | 12.1147 | NaN | NaN | NaN | 12.6165 | 125.653 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 530.2303 | NaN | 21.9897 | NaN | 19.9086
1530.1292 | 12.7937 | 12.4119 | 12.5822 | 12.8825 | 12.3888 | 12.563 | 12.2924 | 12.113 | NaN | NaN | NaN | 12.6104 | 124.7637 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 528.2707 | NaN | 23.2663 | NaN | 19.3803
1531.1292 | 12.7965 | 12.4042 | 12.5804 | 12.8798 | 12.3627 | 12.5601 | 12.2897 | 12.1048 | NaN | NaN | NaN | 12.606 | 129.4345 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 529.8401 | NaN | 16.3495 | NaN | 20.136
1532.1292 | 12.8367 | 12.4935 | 12.5768 | 12.9067 | 12.3421 | 12.5989 | 12.3013 | 12.1044 | NaN | NaN | NaN | 12.6353 | 122.5689 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 532.8686 | NaN | 10.1482 | NaN | 20.0421
1533.1292 | 12.7802 | 12.3991 | 12.5821 | 12.8311 | 12.3529 | 12.5476 | 12.2877 | 12.1088 | NaN | NaN | NaN | 12.6277 | 116.6127 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 531.1128 | NaN | 25.3124 | NaN | 16.2825
1534.1292 | 12.7782 | 12.4293 | 12.5784 | 12.8515 | 12.3814 | 12.5759 | 12.3048 | 12.1068 | NaN | NaN | NaN | 12.6808 | 127.9204 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 530.3097 | NaN | 13.9225 | NaN | 19.1282
1535.1292 | 12.8049 | 12.3887 | 12.576 | 12.8615 | 12.3375 | 12.5439 | 12.2933 | 12.1091 | NaN | NaN | NaN | 12.6125 | 116.1328 | NaN | NaN | NaN | 3.9665 | NaN | NaN | NaN | NaN | 526.6627 | NaN | 16.5909 | NaN | 19.3185
1536.1292 | 12.7952 | 12.4928 | 12.5775 | 12.8539 | 12.3557 | 12.5714 | 12.3082 | 12.1125 | NaN | NaN | NaN | 12.6491 | 130.7684 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 523.8287 | NaN | 22.2289 | NaN | 16.816
1537.1292 | 12.7964 | 12.3924 | 12.5756 | 12.8611 | 12.4168 | 12.5509 | 12.3013 | 12.1109 | NaN | NaN | NaN | 12.6355 | 115.1575 | NaN | NaN | NaN | -7.6491 | NaN | NaN | NaN | NaN | 530.7755 | NaN | 26.4174 | NaN | 6.3416
1538.1292 | 12.7875 | 12.4385 | 12.5748 | 12.8352 | 12.3539 | 12.5694 | 12.3062 | 12.1127 | NaN | NaN | NaN | 12.6118 | 124.0465 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 528.9473 | NaN | 15.9349 | NaN | 10.6221
1539.1292 | 12.8583 | 12.3973 | 12.5795 | 12.8255 | 12.326 | 12.552 | 12.3131 | 12.1117 | NaN | NaN | NaN | 12.6524 | 116.9496 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 529.055 | NaN | 14.5036 | NaN | 17.9122
1540.1292 | 12.8863 | 12.4866 | 12.5794 | 12.9167 | 12.391 | 12.5774 | 12.3184 | 12.1061 | NaN | NaN | NaN | 12.6432 | 131.1212 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 526.6092 | NaN | 29.5359 | NaN | 21.0448
1541.1292 | 12.8093 | 12.4525 | 12.5892 | 12.8242 | 12.393 | 12.5681 | 12.3147 | 12.109 | NaN | NaN | NaN | 12.663 | 114.1437 | NaN | NaN | NaN | -14.9819 | NaN | NaN | NaN | NaN | 526.1732 | NaN | 12.8757 | NaN | 17.1402
1542.1292 | 12.7673 | 12.4398 | 12.587 | 12.8874 | 12.3371 | 12.5643 | 12.317 | 12.1102 | NaN | NaN | NaN | 12.6463 | 124.1802 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 520.9426 | NaN | 22.2825 | NaN | 2.1443
1543.1292 | 12.769 | 12.4547 | 12.5897 | 12.8164 | 12.414 | 12.5579 | 12.3123 | 12.1174 | NaN | NaN | NaN | 12.6638 | 119.4792 | NaN | NaN | NaN | -8.2866 | NaN | NaN | NaN | NaN | 519.5935 | NaN | 20.3018 | NaN | 18.6087
1544.1292 | 12.7691 | 12.4805 | 12.5891 | 12.871 | 12.4284 | 12.5863 | 12.3188 | 12.1131 | NaN | NaN | NaN | 12.6688 | 117.6628 | NaN | NaN | NaN | -9.4486 | NaN | NaN | NaN | NaN | 520.1022 | NaN | 19.5004 | NaN | 19.7668
1545.1292 | 12.7839 | 12.4304 | 12.5919 | 12.856 | 12.3961 | 12.5572 | 12.3147 | 12.1172 | NaN | NaN | NaN | 12.6511 | 126.7787 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 524.2343 | NaN | 18.6974 | NaN | 16.0334
1546.1292 | 12.7752 | 12.4844 | 12.5916 | 12.817 | 12.354 | 12.5781 | 12.3232 | 12.118 | NaN | NaN | NaN | 12.6615 | 120.2214 | NaN | NaN | NaN | -14.7882 | NaN | NaN | NaN | NaN | 525.7162 | NaN | 24.4269 | NaN | 20.3904
1547.1292 | 12.7885 | 12.4055 | 12.5822 | 12.8373 | 12.3967 | 12.5423 | 12.3067 | 12.123 | NaN | NaN | NaN | 12.6952 | 120.3241 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 523.3621 | NaN | 23.3454 | NaN | 20.4978
1548.1292 | 12.7962 | 12.4483 | 12.5864 | 12.8094 | 12.3605 | 12.5729 | 12.3197 | 12.1162 | NaN | NaN | NaN | 12.6771 | 120.5452 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 522.2633 | NaN | 9.7487 | NaN | 17.1809
1549.1292 | 12.8102 | 12.4584 | 12.5801 | 12.8894 | 12.3883 | 12.5635 | 12.3151 | 12.1139 | NaN | NaN | NaN | 12.6412 | 132.714 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 523.7503 | NaN | 23.131 | NaN | 17.4254
1550.1448 | 12.8119 | 12.4 | 12.5808 | 12.8573 | 12.3918 | 12.5359 | 12.2982 | 12.1195 | NaN | NaN | NaN | 12.6358 | 129.0288 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 520.4884 | NaN | 14.5976 | NaN | 18.3604
1551.1292 | 12.7963 | 12.4235 | 12.5838 | 12.8796 | 12.309 | 12.5479 | 12.3064 | 12.1115 | NaN | NaN | NaN | 12.671 | 134.6275 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 522.4181 | NaN | 40.2178 | NaN | 17.1405
1552.1292 | 12.8387 | 12.4597 | 12.5826 | 12.8426 | 12.3438 | 12.5574 | 12.3068 | 12.1181 | NaN | NaN | NaN | 12.6475 | 121.7128 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 521.037 | NaN | 27.9411 | NaN | 18.5754
1553.1292 | 12.8013 | 12.4247 | 12.5803 | 12.8412 | 12.4224 | 12.5513 | 12.2978 | 12.1103 | NaN | NaN | NaN | 12.6254 | 121.8374 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 522.806 | NaN | 14.8775 | NaN | 14.7689
1554.1292 | 12.8206 | 12.4254 | 12.5843 | 12.8467 | 12.3678 | 12.5544 | 12.3038 | 12.1055 | NaN | NaN | NaN | 12.6462 | 121.818 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 519.8573 | NaN | 22.5071 | NaN | 18.927
1555.1292 | 12.7769 | 12.4228 | 12.5802 | 12.846 | 12.4162 | 12.5379 | 12.299 | 12.1077 | NaN | NaN | NaN | 12.6273 | 137.4673 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 520.9208 | NaN | 11.1773 | NaN | 17.4824
1556.1292 | 12.8328 | 12.4063 | 12.5864 | 12.8619 | 12.4074 | 12.5443 | 12.298 | 12.1091 | NaN | NaN | NaN | 12.6314 | 118.9758 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 521.3693 | NaN | 15.9515 | NaN | 19.8361
1557.1292 | 12.8569 | 12.4462 | 12.5795 | 12.825 | 12.3298 | 12.5575 | 12.3054 | 12.1096 | NaN | NaN | NaN | 12.6435 | 126.7837 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 521.8737 | NaN | 20.5049 | NaN | 19.2542
1558.1292 | 12.8521 | 12.4364 | 12.5766 | 12.7847 | 12.2902 | 12.5541 | 12.2999 | 12.1143 | NaN | NaN | NaN | 12.6187 | 127.8209 | NaN | NaN | NaN | -7.6905 | NaN | NaN | NaN | NaN | 520.4693 | NaN | 21.0748 | NaN | 21.3596
1559.1292 | 12.7778 | 12.459 | 12.573 | 12.8239 | 12.3505 | 12.565 | 12.3075 | 12.1085 | NaN | NaN | NaN | 12.6291 | 130.3405 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 520.2438 | NaN | 16.0429 | NaN | 11.3607
1560.1292 | 12.8198 | 12.4475 | 12.5721 | 12.8617 | 12.366 | 12.5729 | 12.3135 | 12.1086 | NaN | NaN | NaN | 12.6387 | 120.866 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 525.4441 | NaN | 7.8133 | NaN | 14.674
1561.1292 | 12.7792 | 12.426 | 12.5777 | 12.8663 | 12.4079 | 12.5416 | 12.3022 | 12.1082 | NaN | NaN | NaN | 12.6365 | 112.7469 | NaN | NaN | NaN | -7.3173 | NaN | NaN | NaN | NaN | 521.5621 | NaN | 11.339 | NaN | 19.5339
1562.1292 | 12.789 | 12.4708 | 12.5746 | 12.8539 | 12.4263 | 12.5645 | 12.3129 | 12.1061 | NaN | NaN | NaN | 12.6508 | 126.4907 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 524.3303 | NaN | 18.9018 | NaN | 18.4288
1563.1292 | 12.7834 | 12.4158 | 12.5711 | 12.8159 | 12.3689 | 12.5395 | 12.299 | 12.1019 | NaN | NaN | NaN | 12.659 | 125.1446 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 522.5503 | NaN | 30.4369 | NaN | 18.889
1564.1292 | 12.7837 | 12.4303 | 12.5787 | 12.8582 | 12.3165 | 12.5564 | 12.3082 | 12.1125 | NaN | NaN | NaN | 12.6587 | 119.7917 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 522.0828 | NaN | 27.7026 | NaN | 19.7534
1565.1292 | 12.7908 | 12.4297 | 12.5812 | 12.8796 | 12.3792 | 12.5348 | 12.2904 | 12.1069 | NaN | NaN | NaN | 12.6421 | 129.9793 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 521.6216 | NaN | 10.5659 | NaN | 17.7546
1566.1292 | 12.7861 | 12.4517 | 12.5757 | 12.8489 | 12.3497 | 12.553 | 12.2959 | 12.1065 | NaN | NaN | NaN | 12.6338 | 131.4972 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 517.4858 | NaN | 15.1805 | NaN | 12.8268
1567.1292 | 12.776 | 12.492 | 12.5721 | 12.8049 | 12.3835 | 12.5613 | 12.2983 | 12.1036 | NaN | NaN | NaN | 12.6252 | 114.6453 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 520.6987 | NaN | 22.3781 | NaN | 19.8814
1568.1292 | 12.7622 | 12.4204 | 12.565 | 12.9221 | 12.3484 | 12.5346 | 12.2864 | 12.1039 | NaN | NaN | NaN | 12.6338 | 117.9721 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 514.7187 | NaN | 29.6998 | NaN | 16.6713
1569.1292 | 12.7837 | 12.4279 | 12.5681 | 12.8403 | 12.3487 | 12.538 | 12.2874 | 12.1032 | NaN | NaN | NaN | 12.6448 | 126.6111 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 513.8576 | NaN | 23.4055 | NaN | 18.6501
1570.1292 | 12.7942 | 12.5087 | 12.5595 | 12.841 | 12.3941 | 12.5585 | 12.3072 | 12.1013 | NaN | NaN | NaN | 12.64 | 133.7331 | NaN | NaN | NaN | -3.8336 | NaN | NaN | NaN | NaN | 520.6732 | NaN | 25.3172 | NaN | 14.6615
1571.1292 | 12.7918 | 12.426 | 12.5634 | 12.8442 | 12.3158 | 12.5394 | 12.2872 | 12.1004 | NaN | NaN | NaN | 12.6453 | 118.6056 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 522.086 | NaN | 14.8282 | NaN | 18.8373
1572.1292 | 12.7975 | 12.4526 | 12.57 | 12.851 | 12.2795 | 12.5642 | 12.2942 | 12.1022 | NaN | NaN | NaN | 12.6514 | 128.6163 | NaN | NaN | NaN | -12.712 | NaN | NaN | NaN | NaN | 521.3573 | NaN | 17.1942 | NaN | 15.9591
1573.1292 | 12.7925 | 12.4178 | 12.5726 | 12.8333 | 12.3658 | 12.519 | 12.2787 | 12.0905 | NaN | NaN | NaN | 12.6433 | 129.1415 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 517.2347 | NaN | 18.9882 | NaN | 19.3422
1574.1292 | 12.7981 | 12.4599 | 12.5682 | 12.8533 | 12.3984 | 12.5454 | 12.2932 | 12.0944 | NaN | NaN | NaN | 12.6279 | 116.0782 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 520.5924 | NaN | 23.4292 | NaN | 19.2994
1575.1292 | 12.8561 | 12.4943 | 12.5711 | 12.8295 | 12.3718 | 12.5918 | 12.2999 | 12.0988 | NaN | NaN | NaN | 12.6557 | 125.5934 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 521.8513 | NaN | 25.3365 | NaN | 14.4441
1576.1292 | 12.7488 | 12.516 | 12.559 | 12.8195 | 12.3262 | 12.5982 | 12.2956 | 12.0942 | NaN | NaN | NaN | 12.6623 | 127.4531 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 520.7186 | NaN | 15.9558 | NaN | 18.9139
1577.1292 | 12.8041 | 12.4621 | 12.5649 | 12.8051 | 12.366 | 12.5655 | 12.2918 | 12.0952 | NaN | NaN | NaN | 12.6699 | 126.6295 | NaN | NaN | NaN | -1.1814 | NaN | NaN | NaN | NaN | 522.1835 | NaN | 15.0915 | NaN | 24.2866
1578.1292 | 12.7603 | 12.4448 | 12.5619 | 12.8804 | 12.3089 | 12.5427 | 12.2812 | 12.0908 | NaN | NaN | NaN | 12.6474 | 122.1386 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 520.7617 | NaN | 17.6922 | NaN | 24.8432
1579.1292 | 12.7655 | 12.46 | 12.5535 | 12.8972 | 12.3276 | 12.5686 | 12.292 | 12.0866 | NaN | NaN | NaN | 12.6638 | 117.748 | NaN | NaN | NaN | -16.3809 | NaN | NaN | NaN | NaN | 517.6966 | NaN | 20.4183 | NaN | 18.6327
1580.1292 | 12.7733 | 12.4296 | 12.5517 | 12.8506 | 12.3393 | 12.533 | 12.2834 | 12.0966 | NaN | NaN | NaN | 12.6265 | 113.5247 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 520.7972 | NaN | 21.0391 | NaN | 15.9816
1581.1292 | 12.766 | 12.4724 | 12.5514 | 12.8389 | 12.3716 | 12.5697 | 12.2947 | 12.0924 | NaN | NaN | NaN | 12.6483 | 123.8145 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 519.3652 | NaN | 23.6278 | NaN | 18.8427
1582.1292 | 12.7688 | 12.4428 | 12.5456 | 12.849 | 12.2916 | 12.561 | 12.2851 | 12.0949 | NaN | NaN | NaN | 12.6315 | 120.0165 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 523.7672 | NaN | 25.5847 | NaN | 19.5479
1583.1292 | 12.7772 | 12.4366 | 12.5423 | 12.8462 | 12.3914 | 12.5486 | 12.2782 | 12.0876 | NaN | NaN | NaN | 12.6385 | 123.4029 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.865 | NaN | 13.172 | NaN | 17.6807
1584.1292 | 12.7756 | 12.4052 | 12.5454 | 12.8467 | 12.3227 | 12.5301 | 12.274 | 12.0793 | NaN | NaN | NaN | 12.6369 | 125.9775 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 513.3468 | NaN | 25.1564 | NaN | 16.1855
1585.1292 | 12.7867 | 12.4316 | 12.5459 | 12.8572 | 12.3367 | 12.5529 | 12.2823 | 12.085 | NaN | NaN | NaN | 12.6304 | 115.8501 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 517.0962 | NaN | 11.2327 | NaN | 16.4912
1586.1292 | 12.7804 | 12.4233 | 12.5478 | 12.7995 | 12.327 | 12.5487 | 12.2771 | 12.0796 | NaN | NaN | NaN | 12.6224 | 126.7648 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 509.1213 | NaN | 11.583 | NaN | 21.6881
1587.1292 | 12.7852 | 12.441 | 12.552 | 12.838 | 12.3569 | 12.5552 | 12.2879 | 12.078 | NaN | NaN | NaN | 12.6229 | 122.9153 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 508.7956 | NaN | 23.5383 | NaN | 15.1862
1588.1292 | 12.7667 | 12.3858 | 12.5528 | 12.9356 | 12.3701 | 12.5228 | 12.2713 | 12.0814 | NaN | NaN | NaN | 12.606 | 127.7755 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 511.7943 | NaN | 18.2799 | NaN | 23.6237
1589.1292 | 12.7762 | 12.4011 | 12.5483 | 12.8305 | 12.3403 | 12.5281 | 12.272 | 12.0809 | NaN | NaN | NaN | 12.586 | 122.4073 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 515.3581 | NaN | 14.4607 | NaN | 19.4576
1590.1292 | 12.7862 | 12.4279 | 12.5565 | 12.8342 | 12.3123 | 12.5557 | 12.287 | 12.0818 | NaN | NaN | NaN | 12.5673 | 127.2112 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 523.2116 | NaN | 12.5879 | NaN | 16.9492
1591.1292 | 12.8567 | 12.3938 | 12.5472 | 12.8408 | 12.3693 | 12.5287 | 12.274 | 12.0841 | NaN | NaN | NaN | 12.6007 | 124.2887 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 520.933 | NaN | 26.7462 | NaN | 16.2188
1592.1292 | 12.7952 | 12.5996 | 12.5515 | 12.8897 | 12.2896 | 12.5743 | 12.3053 | 12.0827 | NaN | NaN | NaN | 12.6026 | 122.0679 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 522.34 | NaN | 32.1821 | NaN | 19.5771
1593.1292 | 12.8041 | 12.3986 | 12.5506 | 12.8516 | 12.3689 | 12.5195 | 12.2684 | 12.0718 | NaN | NaN | NaN | 12.6027 | 126.2467 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 521.1753 | NaN | 18.1834 | NaN | 13.9508
1594.1292 | 12.7734 | 12.4309 | 12.5571 | 12.8338 | 12.3751 | 12.5541 | 12.2859 | 12.0776 | NaN | NaN | NaN | 12.5867 | 126.6241 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 523.6861 | NaN | 34.8695 | NaN | 19.866
1595.1292 | 12.788 | 12.4452 | 12.5505 | 12.8014 | 12.3633 | 12.5484 | 12.2802 | 12.0726 | NaN | NaN | NaN | 12.5753 | 120.8808 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 522.7977 | NaN | 15.7123 | NaN | 18.299
1596.1292 | 12.7907 | 12.3876 | 12.5603 | 12.8781 | 12.3841 | 12.5216 | 12.266 | 12.0655 | NaN | NaN | NaN | 12.6045 | 131.0829 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 522.876 | NaN | 33.0976 | NaN | 18.3497
1597.1292 | 12.7887 | 12.4369 | 12.5576 | 12.8453 | 12.3547 | 12.5406 | 12.2761 | 12.0712 | NaN | NaN | NaN | 12.5808 | 123.9544 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 520.8522 | NaN | 21.4683 | NaN | 18.5152
1598.1292 | 12.7877 | 12.3889 | 12.5573 | 12.8407 | 12.4117 | 12.5195 | 12.2649 | 12.0619 | NaN | NaN | NaN | 12.5808 | 116.4602 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 523.3266 | NaN | 14.1625 | NaN | 18.0759
1599.1292 | 12.7466 | 12.3865 | 12.5544 | 12.8161 | 12.2918 | 12.5283 | 12.261 | 12.0666 | NaN | NaN | NaN | 12.5812 | 129.3123 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 524.5078 | NaN | 18.2533 | NaN | 18.3781
1600.1292 | 12.75 | 12.3749 | 12.5569 | 12.8617 | 12.3329 | 12.5174 | 12.2644 | 12.0635 | NaN | NaN | NaN | 12.6037 | 122.5471 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 524.8652 | NaN | 18.6583 | NaN | 18.623
1601.1292 | 12.7491 | 12.3632 | 12.5516 | 12.8386 | 12.4005 | 12.5124 | 12.2663 | 12.0657 | NaN | NaN | NaN | 12.6006 | 129.2887 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 528.26 | NaN | 7.0377 | NaN | 19.4763
1602.1292 | 12.7278 | 12.451 | 12.544 | 12.8272 | 12.3871 | 12.5458 | 12.2668 | 12.0616 | NaN | NaN | NaN | 12.5648 | 122.0428 | NaN | NaN | NaN | -18.7747 | NaN | NaN | NaN | NaN | 526.0369 | NaN | 18.1695 | NaN | 17.2231
1603.1292 | 12.7904 | 12.3897 | 12.5579 | 12.8243 | 12.348 | 12.5246 | 12.2676 | 12.0605 | NaN | NaN | NaN | 12.5627 | 124.0686 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 525.8239 | NaN | 14.231 | NaN | 20.8747
1604.1292 | 12.7607 | 12.3665 | 12.5511 | 12.9084 | 12.3549 | 12.5241 | 12.2661 | 12.0647 | NaN | NaN | NaN | 12.55 | 120.2311 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 527.0716 | NaN | 17.5478 | NaN | 16.672
1605.1292 | 12.7766 | 12.3809 | 12.5487 | 12.8437 | 12.3586 | 12.5221 | 12.2681 | 12.0687 | NaN | NaN | NaN | 12.553 | 122.7396 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 524.9479 | NaN | 17.4359 | NaN | 14.3924
1606.1292 | 12.7415 | 12.4067 | 12.5472 | 12.8349 | 12.3433 | 12.5268 | 12.2593 | 12.0613 | NaN | NaN | NaN | 12.6203 | 121.4379 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 524.6379 | NaN | 13.7061 | NaN | 18.1409
1607.1292 | 12.7414 | 12.3789 | 12.5387 | 12.8474 | 12.3349 | 12.5107 | 12.2594 | 12.0566 | NaN | NaN | NaN | 12.5419 | 131.8916 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 524.7812 | NaN | 22.8353 | NaN | 17.4812
1608.1292 | 12.7511 | 12.349 | 12.5441 | 12.8421 | 12.378 | 12.5044 | 12.2686 | 12.061 | NaN | NaN | NaN | 12.5373 | 127.9822 | NaN | NaN | NaN | -13.8799 | NaN | NaN | NaN | NaN | 527.597 | NaN | 9.2057 | NaN | 18.0834
1609.1292 | 12.7514 | 12.3674 | 12.5444 | 12.8762 | 12.3992 | 12.4983 | 12.2598 | 12.0582 | NaN | NaN | NaN | 12.5576 | 125.8901 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 525.982 | NaN | 15.048 | NaN | 15.9572
1610.1292 | 12.7458 | 12.3506 | 12.5495 | 12.8279 | 12.3258 | 12.507 | 12.2647 | 12.0559 | NaN | NaN | NaN | 12.5747 | 123.5503 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 526.3583 | NaN | 12.1693 | NaN | 14.3908
1611.1292 | 12.7435 | 12.3466 | 12.5491 | 12.8452 | 12.3491 | 12.4849 | 12.2533 | 12.0567 | NaN | NaN | NaN | 12.5406 | 121.8997 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 521.8972 | NaN | 14.3298 | NaN | 18.5825
1612.1292 | 12.7466 | 12.349 | 12.5401 | 12.8919 | 12.3639 | 12.4992 | 12.2638 | 12.0541 | NaN | NaN | NaN | 12.5404 | 110.5439 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 524.3451 | NaN | 23.8285 | NaN | 19.2849
1613.1292 | 12.7499 | 12.3485 | 12.5379 | 12.821 | 12.2781 | 12.4932 | 12.2552 | 12.0555 | NaN | NaN | NaN | 12.5623 | 123.8775 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 522.2652 | NaN | 12.9133 | NaN | 23.0549
1614.1292 | 12.7574 | 12.3312 | 12.5397 | 12.8245 | 12.3394 | 12.4813 | 12.2486 | 12.0547 | NaN | NaN | NaN | 12.5338 | 115.2613 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 525.7215 | NaN | 14.505 | NaN | 6.8328
1615.1292 | 12.7499 | 12.3476 | 12.5365 | 12.8275 | 12.3154 | 12.4932 | 12.2545 | 12.046 | NaN | NaN | NaN | 12.5516 | 129.0612 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 524.536 | NaN | 26.0776 | NaN | 19.1024
1616.1292 | 12.7512 | 12.3455 | 12.5347 | 12.8281 | 12.3601 | 12.494 | 12.2589 | 12.0602 | NaN | NaN | NaN | 12.5455 | 125.6115 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 527.1037 | NaN | 26.9672 | NaN | 13.353
1617.1292 | 12.822 | 12.3039 | 12.5358 | 12.7968 | 12.2842 | 12.4839 | 12.2615 | 12.0623 | NaN | NaN | NaN | 12.5519 | 118.4868 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 526.9368 | NaN | 12.1637 | NaN | 19.6809
1618.1292 | 12.7321 | 12.3195 | 12.5423 | 12.8558 | 12.3969 | 12.4733 | 12.2563 | 12.054 | NaN | NaN | NaN | 12.5388 | 123.9963 | NaN | NaN | NaN | -18.4208 | NaN | NaN | NaN | NaN | 525.8391 | NaN | 32.8921 | NaN | 19.1006
1619.1292 | 12.7341 | 12.3227 | 12.5431 | 12.8405 | 12.3874 | 12.4805 | 12.2573 | 12.0693 | NaN | NaN | NaN | 12.5517 | 128.1462 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 523.9615 | NaN | 23.4029 | NaN | 18.0417
1620.1292 | 12.8157 | 12.3391 | 12.5443 | 12.805 | 12.337 | 12.5038 | 12.2621 | 12.0578 | NaN | NaN | NaN | 12.5338 | 123.9289 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 525.1701 | NaN | 9.9486 | NaN | 19.9038
1621.1292 | 12.7684 | 12.314 | 12.5382 | 12.8672 | 12.3823 | 12.4797 | 12.2544 | 12.0597 | NaN | NaN | NaN | 12.5689 | 117.313 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 528.3778 | NaN | 13.2111 | NaN | 17.6552
1622.1292 | 12.7277 | 12.416 | 12.5398 | 12.8342 | 12.3529 | 12.5053 | 12.2731 | 12.0615 | NaN | NaN | NaN | 12.548 | 123.8137 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 525.9158 | NaN | 18.4842 | NaN | 16.8041
1623.1292 | 12.8889 | 12.4252 | 12.5414 | 12.8002 | 12.337 | 12.5537 | 12.2759 | 12.0619 | NaN | NaN | NaN | 12.5329 | 119.9418 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 525.6355 | NaN | 19.7029 | NaN | 10.5696
1624.1292 | 12.7826 | 12.3141 | 12.5389 | 12.8554 | 12.3744 | 12.4934 | 12.2617 | 12.0591 | NaN | NaN | NaN | 12.5332 | 121.8892 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 526.5499 | NaN | 15.47 | NaN | 19.7166
1625.1292 | 12.766 | 12.3445 | 12.5351 | 12.8111 | 12.284 | 12.5005 | 12.2572 | 12.0602 | NaN | NaN | NaN | 12.5534 | 126.1124 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 524.7393 | NaN | 17.6985 | NaN | 18.2251
1626.1292 | 12.8134 | 12.3564 | 12.5367 | 12.8383 | 12.3481 | 12.5085 | 12.2658 | 12.0567 | NaN | NaN | NaN | 12.5382 | 119.9503 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 521.264 | NaN | 21.8287 | NaN | 18.4574
1627.1292 | 12.8718 | 12.3418 | 12.5355 | 12.8427 | 12.3655 | 12.5039 | 12.2726 | 12.061 | NaN | NaN | NaN | 12.5468 | 112.4549 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 519.9872 | NaN | 24.6234 | NaN | 18.296
1628.1292 | 12.7772 | 12.3842 | 12.5404 | 12.8462 | 12.3576 | 12.5258 | 12.2716 | 12.0638 | NaN | NaN | NaN | 12.5243 | 133.823 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 521.0705 | NaN | 8.612 | NaN | 11.731
1629.1292 | 12.7592 | 12.3227 | 12.5386 | 12.8201 | 12.302 | 12.4898 | 12.2557 | 12.0522 | NaN | NaN | NaN | 12.5213 | 121.4395 | NaN | NaN | NaN | -5.1825 | NaN | NaN | NaN | NaN | 524.9 | NaN | 18.2775 | NaN | 16.8902
1630.1292 | 12.7603 | 12.4656 | 12.5379 | 12.9083 | 12.3605 | 12.5604 | 12.286 | 12.0555 | NaN | NaN | NaN | 12.5432 | 128.396 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 524.0265 | NaN | 16.8172 | NaN | 19.9686
1631.1292 | 12.7627 | 12.3272 | 12.5318 | 12.8434 | 12.3251 | 12.5038 | 12.2644 | 12.0554 | NaN | NaN | NaN | 12.5594 | 125.1401 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 515.8822 | NaN | 16.2341 | NaN | 19.5779
1632.1292 | 12.7684 | 12.3483 | 12.5401 | 12.896 | 12.3121 | 12.5007 | 12.2615 | 12.0633 | NaN | NaN | NaN | 12.5223 | 132.8745 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.0091 | NaN | 29.802 | NaN | 17.3034
1633.1292 | 12.7711 | 12.3823 | 12.5395 | 12.8284 | 12.3099 | 12.5249 | 12.2681 | 12.0598 | NaN | NaN | NaN | 12.557 | 129.1306 | NaN | NaN | NaN | -8.3761 | NaN | NaN | NaN | NaN | 519.5038 | NaN | 20.6777 | NaN | 16.0458
1634.1292 | 12.7851 | 12.3317 | 12.5395 | 12.8403 | 12.3115 | 12.491 | 12.258 | 12.0605 | NaN | NaN | NaN | 12.5262 | 117.205 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 520.5975 | NaN | 12.7308 | NaN | 14.3498
1635.1292 | 12.795 | 12.3521 | 12.5394 | 12.8197 | 12.33 | 12.5119 | 12.2555 | 12.0585 | NaN | NaN | NaN | 12.5297 | 126.139 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.837 | NaN | 22.2989 | NaN | 18.9777
1636.1292 | 12.8135 | 12.341 | 12.5333 | 12.8904 | 12.2671 | 12.515 | 12.2642 | 12.0604 | NaN | NaN | NaN | 12.5493 | 112.9456 | NaN | NaN | NaN | 5.7379 | NaN | NaN | NaN | NaN | 520.4404 | NaN | 20.0366 | NaN | 24.0903
1637.1292 | 12.7849 | 12.3627 | 12.5354 | 12.7907 | 12.3724 | 12.5022 | 12.2628 | 12.0612 | NaN | NaN | NaN | 12.5357 | 124.8501 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 515.1483 | NaN | 11.5522 | NaN | 7.1193
1638.1292 | 12.7635 | 12.4422 | 12.5274 | 12.8451 | 12.3607 | 12.5409 | 12.2793 | 12.0615 | NaN | NaN | NaN | 12.5616 | 114.0753 | NaN | NaN | NaN | 0.9924 | NaN | NaN | NaN | NaN | 518.1226 | NaN | 13.5027 | NaN | 6.8391
1639.1292 | 12.7636 | 12.357 | 12.5211 | 12.8353 | 12.3404 | 12.5103 | 12.2733 | 12.0612 | NaN | NaN | NaN | 12.5608 | 130.4787 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.2324 | NaN | 28.677 | NaN | 19.8724
1640.1292 | 12.7672 | 12.392 | 12.5211 | 12.8219 | 12.3473 | 12.5172 | 12.2697 | 12.0642 | NaN | NaN | NaN | 12.5517 | 124.854 | NaN | NaN | NaN | 0.7728 | NaN | NaN | NaN | NaN | 516.2113 | NaN | 32.851 | NaN | 11.6698
1641.1292 | 12.7702 | 12.4005 | 12.5112 | 12.827 | 12.3014 | 12.5345 | 12.2784 | 12.0689 | NaN | NaN | NaN | 12.5566 | 127.4349 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 513.6353 | NaN | 16.6029 | NaN | 20.3496
1642.1292 | 12.7917 | 12.4025 | 12.5058 | 12.8152 | 12.2959 | 12.5303 | 12.2735 | 12.0738 | NaN | NaN | NaN | 12.5457 | 113.4744 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 512.1754 | NaN | 11.9355 | NaN | 21.2994
1643.1292 | 12.7318 | 12.3731 | 12.5036 | 12.8397 | 12.2464 | 12.5168 | 12.27 | 12.0751 | NaN | NaN | NaN | 12.5487 | 116.8538 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 519.2233 | NaN | 23.239 | NaN | 20.7463
1644.1292 | 12.7503 | 12.4109 | 12.5016 | 12.7781 | 12.3476 | 12.5425 | 12.2776 | 12.0762 | NaN | NaN | NaN | 12.5596 | 128.8109 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 519.6528 | NaN | 9.6335 | NaN | 24.0163
1645.1292 | 12.9262 | 12.373 | 12.4928 | 12.8787 | 12.3399 | 12.5168 | 12.2688 | 12.0741 | NaN | NaN | NaN | 12.5262 | 121.2954 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.078 | NaN | 15.0167 | NaN | 8.6947
1646.1292 | 12.7796 | 12.4077 | 12.5003 | 12.8462 | 12.363 | 12.5365 | 12.2732 | 12.0704 | NaN | NaN | NaN | 12.55 | 121.8014 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 521.2132 | NaN | 12.6365 | NaN | 20.8358
1647.1292 | 12.8222 | 12.375 | 12.4966 | 12.8263 | 12.3758 | 12.5254 | 12.2767 | 12.0739 | NaN | NaN | NaN | 12.5339 | 121.9623 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 519.985 | NaN | 17.9835 | NaN | 25.7363
1648.1292 | 12.7531 | 12.3651 | 12.4882 | 12.8369 | 12.3805 | 12.522 | 12.268 | 12.075 | NaN | NaN | NaN | 12.583 | 121.4408 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 520.1103 | NaN | 11.0673 | NaN | 20.9055
1649.1292 | 12.749 | 12.3696 | 12.4912 | 12.8021 | 12.3117 | 12.526 | 12.2694 | 12.0793 | NaN | NaN | NaN | 12.534 | 113.8113 | NaN | NaN | NaN | 8.2139 | NaN | NaN | NaN | NaN | 520.8231 | NaN | 17.1178 | NaN | 18.1828
1650.1292 | 12.7556 | 12.3856 | 12.4877 | 12.8432 | 12.3731 | 12.5375 | 12.2809 | 12.0793 | NaN | NaN | NaN | 12.5673 | 124.7841 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 521.2767 | NaN | 17.7754 | NaN | 19.3043
1651.1292 | 12.7292 | 12.4607 | 12.4879 | 12.7913 | 12.3744 | 12.5594 | 12.2741 | 12.0795 | NaN | NaN | NaN | 12.5688 | 120.6039 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 520.6599 | NaN | 18.5061 | NaN | 21.0126
1652.1292 | 12.8816 | 12.4094 | 12.4909 | 12.8314 | 12.3663 | 12.5317 | 12.2841 | 12.0823 | NaN | NaN | NaN | 12.5397 | 128.3511 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 516.506 | NaN | 10.7978 | NaN | 18.541
1653.1292 | 12.776 | 12.4085 | 12.4913 | 12.8274 | 12.2965 | 12.5384 | 12.2821 | 12.0803 | NaN | NaN | NaN | 12.5305 | 115.1231 | NaN | NaN | NaN | 8.7366 | NaN | NaN | NaN | NaN | 519.7516 | NaN | 10.3132 | NaN | 22.1295
1654.1292 | 12.7524 | 12.3665 | 12.4934 | 12.8329 | 12.3638 | 12.5105 | 12.2776 | 12.0846 | NaN | NaN | NaN | 12.5565 | 133.8681 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 520.6531 | NaN | 10.451 | NaN | 19.7937
1655.1292 | 12.7423 | 12.3729 | 12.4986 | 12.8228 | 12.2692 | 12.5162 | 12.2751 | 12.0852 | NaN | NaN | NaN | 12.5679 | 116.596 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 520.8773 | NaN | 22.0978 | NaN | 20.7191
1656.1292 | 12.7545 | 12.3887 | 12.4982 | 12.8319 | 12.3284 | 12.5117 | 12.2768 | 12.0902 | NaN | NaN | NaN | 12.5414 | 124.2994 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 516.5235 | NaN | 2.6361 | NaN | 12.7184
1657.1292 | 12.7928 | 12.3885 | 12.4992 | 12.8024 | 12.2927 | 12.5297 | 12.2846 | 12.0906 | NaN | NaN | NaN | 12.5699 | 125.6275 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.8107 | NaN | 23.2162 | NaN | 8.181
1658.1292 | 12.7336 | 12.3627 | 12.5006 | 12.8281 | 12.3573 | 12.5048 | 12.2788 | 12.0951 | NaN | NaN | NaN | 12.5451 | 127.2215 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.7882 | NaN | 22.8446 | NaN | 19.4809
1659.1292 | 12.7436 | 12.4104 | 12.4982 | 12.8479 | 12.2981 | 12.5222 | 12.2801 | 12.0886 | NaN | NaN | NaN | 12.5646 | 117.1637 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.6712 | NaN | 13.5374 | NaN | 18.8211
1660.1292 | 12.7449 | 12.3996 | 12.4979 | 12.8233 | 12.3274 | 12.5233 | 12.2849 | 12.0899 | NaN | NaN | NaN | 12.5416 | 122.2061 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 519.0104 | NaN | 15.1916 | NaN | 16.2649
1661.1292 | 12.759 | 12.3822 | 12.4981 | 12.7977 | 12.347 | 12.5068 | 12.282 | 12.0909 | NaN | NaN | NaN | 12.5686 | 128.7587 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 519.0613 | NaN | 22.6255 | NaN | 19.879
1662.1292 | 12.7565 | 12.3928 | 12.4961 | 12.9197 | 12.2779 | 12.5175 | 12.2859 | 12.0946 | NaN | NaN | NaN | 12.5541 | 131.6781 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 519.4226 | NaN | 14.0167 | NaN | 22.4083
1663.1292 | 12.7592 | 12.494 | 12.5028 | 12.8382 | 12.3488 | 12.5624 | 12.3005 | 12.0934 | NaN | NaN | NaN | 12.5687 | 129.378 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 516.9753 | NaN | 31.9162 | NaN | 17.1794
1664.1292 | 12.7594 | 12.415 | 12.5088 | 12.8485 | 12.3748 | 12.5199 | 12.282 | 12.0956 | NaN | NaN | NaN | 12.5468 | 134.5787 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 515.4681 | NaN | 21.4364 | NaN | 16.1337
1665.1292 | 12.7534 | 12.3775 | 12.5037 | 12.8295 | 12.3509 | 12.5122 | 12.2783 | 12.096 | NaN | NaN | NaN | 12.5749 | 122.3143 | NaN | NaN | NaN | 0.244 | NaN | NaN | NaN | NaN | 514.9485 | NaN | 6.9267 | NaN | 20.1396
1666.1292 | 12.7588 | 12.4659 | 12.5055 | 12.835 | 12.2463 | 12.5477 | 12.2782 | 12.095 | NaN | NaN | NaN | 12.5512 | 121.7099 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 512.6599 | NaN | 27.4533 | NaN | 19.7196
1667.1292 | 12.7649 | 12.419 | 12.4982 | 12.8434 | 12.3934 | 12.5125 | 12.2702 | 12.0905 | NaN | NaN | NaN | 12.5546 | 120.9173 | NaN | NaN | NaN | -8.0737 | NaN | NaN | NaN | NaN | 514.5556 | NaN | 23.1255 | NaN | 20.354
1668.1292 | 12.7683 | 12.4045 | 12.5038 | 12.818 | 12.3307 | 12.5171 | 12.2657 | 12.0906 | NaN | NaN | NaN | 12.5547 | 121.8696 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 516.1392 | NaN | 13.0317 | NaN | 15.5084
1669.1292 | 12.7627 | 12.4035 | 12.4927 | 12.841 | 12.2711 | 12.5305 | 12.2675 | 12.0869 | NaN | NaN | NaN | 12.5784 | 117.5104 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 515.5291 | NaN | 16.137 | NaN | 18.3584
1670.1292 | 12.7695 | 12.3953 | 12.501 | 12.8354 | 12.3295 | 12.514 | 12.2526 | 12.0909 | NaN | NaN | NaN | 12.5597 | 113.088 | NaN | NaN | NaN | -11.8861 | NaN | NaN | NaN | NaN | 518.1411 | NaN | 18.0051 | NaN | 16.2211
1671.1292 | 12.7615 | 12.4856 | 12.4932 | 12.8694 | 12.3184 | 12.5566 | 12.2718 | 12.0848 | NaN | NaN | NaN | 12.5858 | 116.9594 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 520.3533 | NaN | 14.1132 | NaN | 18.7717
1672.1292 | 12.7632 | 12.4086 | 12.4906 | 12.8299 | 12.3068 | 12.5187 | 12.2628 | 12.0899 | NaN | NaN | NaN | 12.5897 | 121.8927 | NaN | NaN | NaN | 8.9464 | NaN | NaN | NaN | NaN | 520.0737 | NaN | 35.3674 | NaN | 18.3825
1673.1292 | 12.7679 | 12.3963 | 12.4896 | 12.8252 | 12.3783 | 12.5222 | 12.257 | 12.0929 | NaN | NaN | NaN | 12.5718 | 124.3348 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 521.6011 | NaN | 21.1829 | NaN | 17.8026
1674.1292 | 12.766 | 12.5008 | 12.4922 | 12.8228 | 12.3728 | 12.5594 | 12.273 | 12.0819 | NaN | NaN | NaN | 12.5658 | 117.9745 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 521.1177 | NaN | 28.8684 | NaN | 20.6838
1675.1292 | 12.7676 | 12.4478 | 12.4939 | 12.8104 | 12.3386 | 12.5415 | 12.2596 | 12.0771 | NaN | NaN | NaN | 12.5357 | 123.6555 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 525.1503 | NaN | 32.3788 | NaN | 16.2782
1676.1292 | 12.7636 | 12.4027 | 12.4853 | 12.8622 | 12.3489 | 12.5239 | 12.2558 | 12.0855 | NaN | NaN | NaN | 12.5603 | 111.4896 | NaN | NaN | NaN | -18.199 | NaN | NaN | NaN | NaN | 520.1428 | NaN | 15.9994 | NaN | 17.6524
1677.1292 | 12.7715 | 12.4244 | 12.4886 | 12.814 | 12.3649 | 12.5257 | 12.2555 | 12.0802 | NaN | NaN | NaN | 12.5292 | 136.5369 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 521.2327 | NaN | 14.7771 | NaN | 17.6495
1678.1292 | 12.73 | 12.4033 | 12.4949 | 12.7978 | 12.327 | 12.5158 | 12.2516 | 12.0772 | NaN | NaN | NaN | 12.5761 | 132.0278 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 521.6224 | NaN | 33.0195 | NaN | 19.145
1679.1292 | 12.8067 | 12.4599 | 12.4907 | 12.8242 | 12.3107 | 12.5543 | 12.2717 | 12.0844 | NaN | NaN | NaN | 12.5246 | 130.8935 | NaN | NaN | NaN | -13.7707 | NaN | NaN | NaN | NaN | 516.816 | NaN | 26.9746 | NaN | 13.0592
1680.1292 | 12.7352 | 12.4271 | 12.4941 | 12.7963 | 12.3341 | 12.5405 | 12.2551 | 12.0723 | NaN | NaN | NaN | 12.5352 | 119.1697 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 520.0263 | NaN | 23.3933 | NaN | 17.5953
1681.1292 | 12.7356 | 12.4086 | 12.4942 | 12.797 | 12.3173 | 12.518 | 12.26 | 12.0679 | NaN | NaN | NaN | 12.5618 | 118.7493 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 519.5141 | NaN | 27.978 | NaN | 18.12
1682.1292 | 12.7468 | 12.4484 | 12.5024 | 12.7729 | 12.3381 | 12.5579 | 12.2688 | 12.0792 | NaN | NaN | NaN | 12.5547 | 123.4903 | NaN | NaN | NaN | -8.0807 | NaN | NaN | NaN | -12.0682 | 518.3407 | NaN | 17.9852 | NaN | 18.3474
1683.1292 | 12.7421 | 12.4158 | 12.5036 | 12.783 | 12.3635 | 12.5217 | 12.256 | 12.068 | NaN | NaN | NaN | 12.56 | 130.4279 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 519.2495 | NaN | 13.1 | NaN | 16.5632
1684.1292 | 12.7361 | 12.3855 | 12.5017 | 12.8805 | 12.3999 | 12.5195 | 12.2589 | 12.073 | NaN | NaN | NaN | 12.5521 | 118.845 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.8641 | NaN | 13.8464 | NaN | 19.4141
1685.1292 | 12.7427 | 12.3878 | 12.4994 | 12.827 | 12.3345 | 12.5268 | 12.2666 | 12.065 | NaN | NaN | NaN | 12.5501 | 128.9561 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.727 | NaN | 12.3953 | NaN | 21.0485
1686.1292 | 12.7638 | 12.3848 | 12.5084 | 12.8068 | 12.3706 | 12.5133 | 12.2653 | 12.0725 | NaN | NaN | NaN | 12.5485 | 112.4452 | NaN | NaN | NaN | -3.833 | NaN | NaN | NaN | NaN | 518.1893 | NaN | 19.1641 | NaN | 19.0229
1687.1292 | 12.7449 | 12.4045 | 12.5007 | 12.807 | 12.387 | 12.518 | 12.2638 | 12.0782 | NaN | NaN | NaN | 12.5842 | 122.2712 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 521.5209 | NaN | 19.0078 | NaN | 18.7552
1688.1292 | 12.7338 | 12.4139 | 12.4965 | 12.8018 | 12.3776 | 12.5343 | 12.268 | 12.0807 | NaN | NaN | NaN | 12.5927 | 133.0913 | NaN | NaN | NaN | -7.7333 | NaN | NaN | NaN | NaN | 521.7989 | NaN | 10.8652 | NaN | 20.26
1689.1292 | 12.7576 | 12.5017 | 12.5019 | 12.7815 | 12.3095 | 12.5901 | 12.2994 | 12.0689 | NaN | NaN | NaN | 12.5695 | 122.6342 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 522.2671 | NaN | 18.651 | NaN | 20.1603
1690.1292 | 12.7572 | 12.3837 | 12.5037 | 12.8384 | 12.233 | 12.5241 | 12.2597 | 12.0736 | NaN | NaN | NaN | 12.5928 | 121.7964 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 522.6234 | NaN | 24.6106 | NaN | 24.3838
1691.1292 | 12.7798 | 12.4129 | 12.5041 | 12.7982 | 12.3706 | 12.5567 | 12.2736 | 12.0751 | NaN | NaN | NaN | 12.5585 | 114.9208 | NaN | NaN | NaN | 1.2997 | NaN | NaN | NaN | NaN | 520.6263 | NaN | 27.3323 | NaN | 17.3166
1692.1292 | 12.7468 | 12.368 | 12.5035 | 12.8058 | 12.3204 | 12.528 | 12.2664 | 12.0808 | NaN | NaN | NaN | 12.5465 | 123.9035 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 524.4726 | NaN | 26.0962 | NaN | 19.3146
1693.1292 | 12.7483 | 12.4097 | 12.507 | 12.7601 | 12.3559 | 12.5618 | 12.2682 | 12.0831 | NaN | NaN | NaN | 12.5388 | 131.6339 | NaN | NaN | NaN | -3.6039 | NaN | NaN | NaN | NaN | 524.3338 | NaN | 16.3153 | NaN | 15.6783
1694.1292 | 12.7663 | 12.3837 | 12.512 | 12.8167 | 12.286 | 12.5473 | 12.2582 | 12.08 | NaN | NaN | NaN | 12.5563 | 124.4036 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 524.2642 | NaN | 28.3172 | NaN | 15.8306
1695.1292 | 12.7641 | 12.371 | 12.5116 | 12.8093 | 12.3907 | 12.5303 | 12.2606 | 12.0786 | NaN | NaN | NaN | 12.5465 | 111.1209 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 525.6539 | NaN | 23.0079 | NaN | 19.5136
1696.1292 | 12.7718 | 12.3749 | 12.5166 | 12.801 | 12.3466 | 12.5275 | 12.2566 | 12.0825 | NaN | NaN | NaN | 12.5303 | 121.0707 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 526.7125 | NaN | 20.4469 | NaN | 20.1607
1697.1292 | 12.725 | 12.382 | 12.518 | 12.789 | 12.333 | 12.5311 | 12.2592 | 12.0745 | NaN | NaN | NaN | 12.525 | 114.6354 | NaN | NaN | NaN | 1.6329 | NaN | NaN | NaN | NaN | 526.5633 | NaN | 24.686 | NaN | 19.4052
1698.1292 | 12.7419 | 12.4209 | 12.5111 | 12.788 | 12.2692 | 12.5334 | 12.2687 | 12.0843 | NaN | NaN | NaN | 12.534 | 127.1432 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 530.3308 | NaN | 9.8516 | NaN | 15.0868
1699.1292 | 12.7461 | 12.3695 | 12.509 | 12.7953 | 12.3908 | 12.5094 | 12.2571 | 12.0787 | NaN | NaN | NaN | 12.5342 | 118.6523 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 527.6118 | NaN | 13.2187 | NaN | 18.5597
1700.1292 | 12.752 | 12.4073 | 12.5047 | 12.7831 | 12.3523 | 12.5342 | 12.2659 | 12.0886 | NaN | NaN | NaN | 12.5489 | 117.7783 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 529.0591 | NaN | 31.9187 | NaN | 15.8966
1701.1292 | 12.7504 | 12.4215 | 12.5055 | 12.7851 | 12.2906 | 12.5486 | 12.2641 | 12.084 | NaN | NaN | NaN | 12.5392 | 116.2772 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -12.2943 | 527.1305 | NaN | 32.7989 | NaN | 17.4386
1702.1292 | 12.7378 | 12.3793 | 12.5119 | 12.7677 | 12.3112 | 12.5398 | 12.2627 | 12.0802 | NaN | NaN | NaN | 12.5442 | 129.2154 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 527.7634 | NaN | 14.2128 | NaN | 20.3105
1703.1292 | 12.7465 | 12.398 | 12.5168 | 12.8066 | 12.3578 | 12.5396 | 12.2709 | 12.0841 | NaN | NaN | NaN | 12.5751 | 118.7637 | NaN | NaN | NaN | 10.1036 | NaN | NaN | NaN | NaN | 529.5743 | NaN | 13.7713 | NaN | 20.3722
1704.1292 | 12.7268 | 12.3612 | 12.5117 | 12.7722 | 12.2895 | 12.5248 | 12.2656 | 12.0833 | NaN | NaN | NaN | 12.5514 | 115.9342 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 529.39 | NaN | 24.7776 | NaN | 21.0688
1705.1292 | 12.7397 | 12.3506 | 12.5119 | 12.7874 | 12.3028 | 12.5211 | 12.265 | 12.0866 | NaN | NaN | NaN | 12.5451 | 117.7723 | NaN | NaN | NaN | 2.7962 | NaN | NaN | NaN | NaN | 531.9861 | NaN | 25.8935 | NaN | 18.4462
1706.1292 | 12.7155 | 12.4408 | 12.5107 | 12.8234 | 12.2992 | 12.5536 | 12.2781 | 12.0853 | NaN | NaN | NaN | 12.5277 | 119.1372 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 531.1067 | NaN | 15.1532 | NaN | 18.4015
1707.1292 | 12.7374 | 12.383 | 12.5121 | 12.846 | 12.3702 | 12.5189 | 12.2669 | 12.0922 | NaN | NaN | NaN | 12.5606 | 121.9153 | NaN | NaN | NaN | -5.269 | NaN | NaN | NaN | NaN | 531.8985 | NaN | 22.0579 | NaN | 19.376
1708.1292 | 12.7269 | 12.3851 | 12.5158 | 12.7713 | 12.3115 | 12.5227 | 12.2709 | 12.0857 | NaN | NaN | NaN | 12.5737 | 118.3568 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 531.3875 | NaN | 21.0182 | NaN | 18.3453
1709.1292 | 12.735 | 12.3438 | 12.5139 | 12.752 | 12.2983 | 12.5131 | 12.2699 | 12.0835 | NaN | NaN | NaN | 12.5405 | 127.8426 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 532.0238 | NaN | 29.7917 | NaN | 16.5797
1710.1292 | 12.7371 | 12.3612 | 12.5174 | 12.7531 | 12.3011 | 12.5238 | 12.2655 | 12.0864 | NaN | NaN | NaN | 12.5717 | 122.2596 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 531.511 | NaN | 19.3762 | NaN | 12.6371
1711.1292 | 12.7411 | 12.3454 | 12.5169 | 12.8177 | 12.3772 | 12.524 | 12.2702 | 12.0825 | NaN | NaN | NaN | 12.5711 | 126.9772 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 530.899 | NaN | 26.8668 | NaN | 19.7012
1712.1292 | 12.7471 | 12.3886 | 12.5218 | 12.8128 | 12.3114 | 12.5334 | 12.2651 | 12.0799 | NaN | NaN | NaN | 12.5858 | 125.3652 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 527.9608 | NaN | 24.0921 | NaN | 8.9761
1713.1292 | 12.7464 | 12.3562 | 12.5141 | 12.8107 | 12.326 | 12.5179 | 12.2651 | 12.0769 | NaN | NaN | NaN | 12.5333 | 133.5943 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 531.3615 | NaN | 9.0602 | NaN | 10.0923
1714.1292 | 12.7366 | 12.4115 | 12.5258 | 12.7665 | 12.3117 | 12.5444 | 12.2677 | 12.0785 | NaN | NaN | NaN | 12.57 | 125.456 | NaN | NaN | NaN | 5.0837 | NaN | NaN | NaN | NaN | 532.0533 | NaN | 13.5679 | NaN | 20.1886
1715.1292 | 12.7427 | 12.3699 | 12.5214 | 12.7738 | 12.3889 | 12.5242 | 12.2683 | 12.0824 | NaN | NaN | NaN | 12.5742 | 124.3431 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -8.9671 | 529.1962 | NaN | 18.2724 | NaN | 18.5319
1716.1292 | 12.7421 | 12.3585 | 12.5174 | 12.7982 | 12.3804 | 12.519 | 12.2674 | 12.0747 | NaN | NaN | NaN | 12.5645 | 128.0606 | NaN | NaN | NaN | -15.5865 | NaN | NaN | NaN | NaN | 527.6423 | NaN | 12.1711 | NaN | 26.1356
1717.1292 | 12.7526 | 12.3488 | 12.5154 | 12.8116 | 12.338 | 12.5045 | 12.2594 | 12.0743 | NaN | NaN | NaN | 12.5417 | 129.7801 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 523.5029 | NaN | 13.8917 | NaN | 17.0095
1718.1292 | 12.7435 | 12.3769 | 12.5191 | 12.7865 | 12.2966 | 12.5312 | 12.2765 | 12.0708 | NaN | NaN | NaN | 12.5771 | 126.0856 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 527.747 | NaN | 9.9485 | NaN | 18.1972
1719.1292 | 12.7308 | 12.3845 | 12.5205 | 12.8018 | 12.3832 | 12.5188 | 12.2662 | 12.073 | NaN | NaN | NaN | 12.5616 | 136.7162 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 526.1945 | NaN | 20.8433 | NaN | 16.3852
1720.1292 | 12.7318 | 12.3662 | 12.5179 | 12.8392 | 12.303 | 12.503 | 12.2593 | 12.0682 | NaN | NaN | NaN | 12.5664 | 121.8192 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 521.4457 | NaN | 22.2004 | NaN | 11.2112
1721.1292 | 12.729 | 12.3827 | 12.5204 | 12.7978 | 12.3864 | 12.5203 | 12.2747 | 12.0712 | NaN | NaN | NaN | 12.5341 | 122.7799 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 519.7843 | NaN | 24.5607 | NaN | 18.3225
1722.1292 | 12.7411 | 12.3998 | 12.521 | 12.801 | 12.3376 | 12.523 | 12.2738 | 12.0727 | NaN | NaN | NaN | 12.5668 | 119.3929 | NaN | NaN | NaN | 7.6739 | NaN | NaN | NaN | NaN | 525.3498 | NaN | 20.798 | NaN | 16.8555
1723.1292 | 12.7435 | 12.3478 | 12.5131 | 12.7736 | 12.3121 | 12.5125 | 12.2793 | 12.071 | NaN | NaN | NaN | 12.5573 | 128.6782 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 526.7116 | NaN | 23.5922 | NaN | 16.3374
1724.1292 | 12.7368 | 12.3864 | 12.5157 | 12.7874 | 12.3703 | 12.5273 | 12.2815 | 12.077 | NaN | NaN | NaN | 12.5678 | 132.3829 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 524.6549 | NaN | 27.4966 | NaN | 16.6809
1725.1292 | 12.7897 | 12.3428 | 12.5162 | 12.7609 | 12.3693 | 12.4975 | 12.2638 | 12.0646 | NaN | NaN | NaN | 12.5836 | 122.5278 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 527.5049 | NaN | 26.7463 | NaN | 18.9357
1726.1292 | 12.7198 | 12.3646 | 12.5142 | 12.8203 | 12.3423 | 12.5149 | 12.2671 | 12.0765 | NaN | NaN | NaN | 12.5572 | 120.4775 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 526.0071 | NaN | 10.6505 | NaN | 18.9722
1727.1292 | 12.7271 | 12.3583 | 12.5186 | 12.8044 | 12.3391 | 12.5019 | 12.2667 | 12.0718 | NaN | NaN | NaN | 12.5516 | 117.465 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 524.1859 | NaN | 30.2547 | NaN | 20.2823
1728.1292 | 12.7269 | 12.3336 | 12.524 | 12.8248 | 12.4027 | 12.5096 | 12.2661 | 12.0793 | NaN | NaN | NaN | 12.5491 | 126.3626 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 525.4131 | NaN | 23.4088 | NaN | 18.0058
1729.1292 | 12.7218 | 12.3473 | 12.5182 | 12.7798 | 12.3608 | 12.5028 | 12.2698 | 12.0685 | NaN | NaN | NaN | 12.566 | 125.3734 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 528.3903 | NaN | 17.4973 | NaN | 16.9623
1730.1292 | 12.7194 | 12.3925 | 12.5222 | 12.7873 | 12.2914 | 12.5179 | 12.267 | 12.0683 | NaN | NaN | NaN | 12.5882 | 120.744 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 527.3173 | NaN | 17.0229 | NaN | 19.8024
1731.1292 | 12.7144 | 12.3521 | 12.5153 | 12.7972 | 12.2766 | 12.498 | 12.267 | 12.0735 | NaN | NaN | NaN | 12.5533 | 116.0585 | NaN | NaN | NaN | 5.567 | NaN | NaN | NaN | NaN | 528.625 | NaN | 21.6014 | NaN | 18.2219
1732.1292 | 12.7276 | 12.3717 | 12.5249 | 12.799 | 12.285 | 12.5153 | 12.2761 | 12.0635 | NaN | NaN | NaN | 12.5472 | 130.2495 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 526.8486 | NaN | 15.7887 | NaN | 18.6722
1733.1292 | 12.7183 | 12.3498 | 12.5252 | 12.7802 | 12.3762 | 12.5024 | 12.2707 | 12.0643 | NaN | NaN | NaN | 12.535 | 135.77 | NaN | NaN | NaN | -10.2881 | NaN | NaN | NaN | NaN | 524.7228 | NaN | 29.8866 | NaN | 18.5176
1734.1292 | 12.7265 | 12.3606 | 12.5226 | 12.8172 | 12.2965 | 12.5151 | 12.2721 | 12.0695 | NaN | NaN | NaN | 12.5413 | 118.3736 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 525.845 | NaN | 21.4478 | NaN | 19.4842
1735.1292 | 12.6929 | 12.3612 | 12.5189 | 12.8183 | 12.4004 | 12.5126 | 12.2665 | 12.0656 | NaN | NaN | NaN | 12.5435 | 122.9147 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 528.2313 | NaN | 23.4047 | NaN | 17.1538
1736.1292 | 12.6989 | 12.3914 | 12.5198 | 12.7951 | 12.308 | 12.5183 | 12.2734 | 12.0596 | NaN | NaN | NaN | 12.5504 | 123.3814 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 527.3502 | NaN | 18.0512 | NaN | 15.8231
1737.1292 | 12.6938 | 12.3427 | 12.5231 | 12.7857 | 12.3392 | 12.501 | 12.2659 | 12.0655 | NaN | NaN | NaN | 12.5604 | 123.9562 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 526.321 | NaN | 23.1521 | NaN | 19.7515
1738.1292 | 12.6852 | 12.3704 | 12.5212 | 12.8 | 12.3361 | 12.4987 | 12.2619 | 12.0627 | NaN | NaN | NaN | 12.5914 | 126.9561 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 523.0487 | NaN | 14.4689 | NaN | 13.0534
1739.1292 | 12.7007 | 12.3351 | 12.5142 | 12.7769 | 12.3106 | 12.4982 | 12.2585 | 12.06 | NaN | NaN | NaN | 12.547 | 122.1457 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 524.0931 | NaN | 25.2988 | NaN | 20.2466
1740.1292 | 12.7125 | 12.3392 | 12.5124 | 12.7934 | 12.3462 | 12.5061 | 12.2605 | 12.0646 | NaN | NaN | NaN | 12.5712 | 119.9384 | NaN | NaN | NaN | 5.5449 | NaN | NaN | NaN | NaN | 523.788 | NaN | 27.3227 | NaN | 29.1308
1741.1292 | 12.7089 | 12.3621 | 12.5122 | 12.7853 | 12.3604 | 12.5159 | 12.2677 | 12.0566 | NaN | NaN | NaN | 12.549 | 121.6447 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 526.3025 | NaN | 25.2343 | NaN | 7.6441
1742.1292 | 12.7255 | 12.3499 | 12.5092 | 12.7945 | 12.3256 | 12.5034 | 12.2562 | 12.0538 | NaN | NaN | NaN | 12.5637 | 127.8406 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 525.7592 | NaN | 22.5719 | NaN | 16.5013
1743.1292 | 12.8155 | 12.3386 | 12.509 | 12.8155 | 12.339 | 12.4984 | 12.2588 | 12.0579 | NaN | NaN | NaN | 12.537 | 126.89 | NaN | NaN | NaN | 0.154 | NaN | NaN | NaN | NaN | 523.7317 | NaN | 20.6025 | NaN | 19.7944
1744.1292 | 12.7233 | 12.3863 | 12.5113 | 12.8014 | 12.3136 | 12.5289 | 12.2644 | 12.059 | NaN | NaN | NaN | 12.5703 | 122.3735 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 525.7997 | NaN | 19.8731 | NaN | 18.7353
1745.1292 | 12.6797 | 12.3336 | 12.5118 | 12.8229 | 12.3721 | 12.5127 | 12.2525 | 12.0519 | NaN | NaN | NaN | 12.551 | 119.2143 | NaN | NaN | NaN | -4.3816 | NaN | NaN | NaN | NaN | 528.8857 | NaN | 34.5505 | NaN | 19.1787
1746.1292 | 12.7432 | 12.3606 | 12.509 | 12.8222 | 12.3008 | 12.5156 | 12.2531 | 12.055 | NaN | NaN | NaN | 12.548 | 117.6881 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 525.9926 | NaN | 31.2911 | NaN | 14.8592
1747.1292 | 12.7034 | 12.3407 | 12.5062 | 12.8931 | 12.3673 | 12.5014 | 12.2393 | 12.053 | NaN | NaN | NaN | 12.5662 | 138.9072 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 526.7715 | NaN | 11.5564 | NaN | 19.799
1748.1292 | 12.6921 | 12.3892 | 12.498 | 12.8096 | 12.3373 | 12.5402 | 12.2614 | 12.0529 | NaN | NaN | NaN | 12.5375 | 125.0648 | NaN | NaN | NaN | -0.9914 | NaN | NaN | NaN | NaN | 527.812 | NaN | 15.6093 | NaN | 6.2491
1749.1292 | 12.6831 | 12.3862 | 12.5002 | 12.792 | 12.3631 | 12.5331 | 12.2586 | 12.0534 | NaN | NaN | NaN | 12.5564 | 128.0619 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 528.3161 | NaN | 16.0819 | NaN | 8.8417
1750.1292 | 12.695 | 12.3489 | 12.5026 | 12.7922 | 12.3247 | 12.5077 | 12.2471 | 12.0529 | NaN | NaN | NaN | 12.5637 | 124.5532 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 525.6065 | NaN | 21.2854 | NaN | 21.9082
1751.1292 | 12.6995 | 12.3532 | 12.5049 | 12.8002 | 12.2879 | 12.522 | 12.2502 | 12.043 | NaN | NaN | NaN | 12.5415 | 128.8674 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 530.5955 | NaN | 14.4093 | NaN | 12.0279
1752.1292 | 12.7001 | 12.3805 | 12.5055 | 12.8022 | 12.3439 | 12.5276 | 12.2588 | 12.0491 | NaN | NaN | NaN | 12.5609 | 119.1522 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 528.6599 | NaN | 30.6714 | NaN | 11.1931
1753.1292 | 12.704 | 12.3564 | 12.5051 | 12.7963 | 12.2702 | 12.5243 | 12.2551 | 12.0487 | NaN | NaN | NaN | 12.5717 | 129.7296 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 529.0763 | NaN | 21.5008 | NaN | 19.1853
1754.1292 | 12.6991 | 12.4236 | 12.5017 | 12.8056 | 12.3734 | 12.5307 | 12.26 | 12.0548 | NaN | NaN | NaN | 12.5375 | 134.584 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 525.8366 | NaN | 7.3115 | NaN | 19.2365
1755.1292 | 12.7044 | 12.3514 | 12.5136 | 12.7841 | 12.3622 | 12.5026 | 12.2496 | 12.0546 | NaN | NaN | NaN | 12.5765 | 126.0173 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 528.8973 | NaN | 10.5551 | NaN | 19.1382
1756.1292 | 12.713 | 12.3421 | 12.5053 | 12.8858 | 12.3444 | 12.5086 | 12.2587 | 12.0518 | NaN | NaN | NaN | 12.6156 | 129.6512 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 530.0219 | NaN | 20.0064 | NaN | 18.4099
1757.1292 | 12.7125 | 12.4284 | 12.5043 | 12.8256 | 12.3102 | 12.5279 | 12.2639 | 12.0534 | NaN | NaN | NaN | 12.5714 | 119.6138 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 530.5819 | NaN | 21.4957 | NaN | 20.5877
1758.1292 | 12.7199 | 12.3855 | 12.5033 | 12.8177 | 12.3474 | 12.5176 | 12.2567 | 12.0548 | NaN | NaN | NaN | 12.5389 | 134.3505 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 529.5827 | NaN | 14.4272 | NaN | 15.0462
1759.1292 | 12.6861 | 12.4039 | 12.4989 | 12.8464 | 12.3528 | 12.5138 | 12.2508 | 12.0525 | NaN | NaN | NaN | 12.5593 | 119.7483 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 530.1321 | NaN | 18.1122 | NaN | 17.1852
1760.1292 | 12.71 | 12.4794 | 12.513 | 12.8184 | 12.3337 | 12.5645 | 12.2762 | 12.0538 | NaN | NaN | NaN | 12.5551 | 117.8172 | NaN | NaN | NaN | -9.4922 | NaN | NaN | NaN | NaN | 531.0599 | NaN | 12.5399 | NaN | 19.7018
1761.1292 | 12.7033 | 12.4143 | 12.5085 | 12.7998 | 12.3082 | 12.5163 | 12.249 | 12.0512 | NaN | NaN | NaN | 12.5761 | 117.8044 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 527.179 | NaN | 19.2866 | NaN | 7.864
1762.1292 | 12.6975 | 12.3789 | 12.5125 | 12.7883 | 12.3824 | 12.4993 | 12.2482 | 12.053 | NaN | NaN | NaN | 12.5729 | 128.1444 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 527.2179 | NaN | 26.5308 | NaN | 19.3263
1763.1292 | 12.7274 | 12.3897 | 12.5123 | 12.7831 | 12.2791 | 12.5091 | 12.244 | 12.0574 | NaN | NaN | NaN | 12.546 | 117.4506 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 526.4789 | NaN | 18.1845 | NaN | 20.9975
1764.1292 | 12.6825 | 12.4099 | 12.5168 | 12.7632 | 12.301 | 12.5248 | 12.2453 | 12.0588 | NaN | NaN | NaN | 12.5925 | 131.5353 | NaN | NaN | NaN | 0.8913 | NaN | NaN | NaN | NaN | 527.5391 | NaN | 32.1261 | NaN | 17.7553
1765.1292 | 12.7804 | 12.3668 | 12.5123 | 12.7926 | 12.3185 | 12.4987 | 12.2387 | 12.0531 | NaN | NaN | NaN | 12.5384 | 129.3013 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 526.7761 | NaN | 22.4502 | NaN | 16.9192
1766.1292 | 12.7176 | 12.3625 | 12.5149 | 12.7919 | 12.3471 | 12.5082 | 12.2425 | 12.0588 | NaN | NaN | NaN | 12.5453 | 121.9917 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 526.1377 | NaN | 28.4583 | NaN | 10.6603
1767.1292 | 12.7564 | 12.3478 | 12.5165 | 12.7961 | 12.2477 | 12.5023 | 12.2469 | 12.057 | NaN | NaN | NaN | 12.5695 | 122.8984 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 526.3204 | NaN | 18.6256 | NaN | 18.8298
1768.1292 | 12.6756 | 12.4075 | 12.5115 | 12.7451 | 12.2998 | 12.5353 | 12.2491 | 12.053 | NaN | NaN | NaN | 12.5507 | 121.7412 | NaN | NaN | NaN | 2.354 | NaN | NaN | NaN | NaN | 526.0541 | NaN | 12.7546 | NaN | 24.5641
1769.1292 | 12.6702 | 12.3618 | 12.5159 | 12.7597 | 12.351 | 12.4887 | 12.2357 | 12.0519 | NaN | NaN | NaN | 12.5592 | 118.2163 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 527.7737 | NaN | 12.9088 | NaN | 21.4258
1770.1292 | 12.8949 | 12.3651 | 12.5161 | 12.8122 | 12.3271 | 12.4984 | 12.2397 | 12.0526 | NaN | NaN | NaN | 12.5527 | 129.6272 | NaN | NaN | NaN | 1.4033 | NaN | NaN | NaN | NaN | 527.0072 | NaN | 18.5512 | NaN | 18.8561
1771.1292 | 12.6868 | 12.3784 | 12.5125 | 12.768 | 12.3408 | 12.5191 | 12.2546 | 12.0542 | NaN | NaN | NaN | 12.5787 | 123.0125 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 526.781 | NaN | 16.8978 | NaN | 6.641
1772.1292 | 12.6611 | 12.3472 | 12.5176 | 12.7692 | 12.3774 | 12.4994 | 12.2335 | 12.0471 | NaN | NaN | NaN | 12.5823 | 120.2361 | NaN | NaN | NaN | -1.1331 | NaN | NaN | NaN | NaN | 521.9197 | NaN | 12.8887 | NaN | 15.3488
1773.1292 | 12.637 | 12.3513 | 12.5214 | 12.7778 | 12.3621 | 12.4934 | 12.2308 | 12.0586 | NaN | NaN | NaN | 12.5883 | 115.3168 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 526.2177 | NaN | 18.6224 | NaN | 20.4147
1774.1292 | 12.7794 | 12.4188 | 12.518 | 12.7702 | 12.3475 | 12.5342 | 12.2437 | 12.0576 | NaN | NaN | NaN | 12.5692 | 124.0483 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 528.1953 | NaN | 29.9992 | NaN | 10.8289
1775.1292 | 12.6764 | 12.3561 | 12.5183 | 12.7778 | 12.3309 | 12.5032 | 12.2313 | 12.0576 | NaN | NaN | NaN | 12.5809 | 124.7336 | NaN | NaN | NaN | 0.8387 | NaN | NaN | NaN | NaN | 523.0303 | NaN | 21.6577 | NaN | 16.8688
1776.1292 | 12.6601 | 12.361 | 12.513 | 12.7396 | 12.3497 | 12.5137 | 12.2392 | 12.0555 | NaN | NaN | NaN | 12.5787 | 128.2563 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 526.3393 | NaN | 18.1472 | NaN | 23.3
1777.1292 | 12.6416 | 12.3802 | 12.5147 | 12.8294 | 12.2665 | 12.5283 | 12.2397 | 12.0615 | NaN | NaN | NaN | 12.5769 | 134.8531 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 528.521 | NaN | 7.4671 | NaN | 16.4939
1778.1292 | 12.662 | 12.3749 | 12.5187 | 12.7644 | 12.3721 | 12.5091 | 12.2315 | 12.0583 | NaN | NaN | NaN | 12.6109 | 125.4926 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 526.6929 | NaN | 15.9718 | NaN | 19.3297
1779.1292 | 12.6621 | 12.3389 | 12.5107 | 12.7516 | 12.2763 | 12.5099 | 12.2333 | 12.0593 | NaN | NaN | NaN | 12.6186 | 130.5239 | NaN | NaN | NaN | 4.1587 | NaN | NaN | NaN | NaN | 530.8365 | NaN | 22.5632 | NaN | 18.1656
1780.1292 | 12.6533 | 12.4094 | 12.5115 | 12.7524 | 12.2692 | 12.535 | 12.2362 | 12.0582 | NaN | NaN | NaN | 12.5831 | 120.5009 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 531.556 | NaN | 12.8416 | NaN | 26.6247
1781.1292 | 12.6583 | 12.3501 | 12.5186 | 12.734 | 12.2894 | 12.4973 | 12.2247 | 12.0632 | NaN | NaN | NaN | 12.5759 | 118.7249 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 529.1971 | NaN | 27.4825 | NaN | 17.3287
1782.1448 | 12.673 | 12.3348 | 12.5119 | 12.7998 | 12.3464 | 12.4932 | 12.2275 | 12.0643 | NaN | NaN | NaN | 12.5694 | 117.8068 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 527.2191 | NaN | 17.764 | NaN | 15.5624
1783.1292 | 12.628 | 12.3614 | 12.5165 | 12.7875 | 12.3176 | 12.5116 | 12.235 | 12.0627 | NaN | NaN | NaN | 12.5833 | 121.1318 | NaN | NaN | NaN | 3.1082 | NaN | NaN | NaN | NaN | 529.2963 | NaN | 12.6946 | NaN | 18.2825
1784.1292 | 12.789 | 12.367 | 12.5171 | 12.7742 | 12.3101 | 12.4965 | 12.2292 | 12.0671 | NaN | NaN | NaN | 12.5685 | 121.767 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 528.6289 | NaN | 22.119 | NaN | 18.113
1785.1292 | 12.6869 | 12.3504 | 12.5131 | 12.7373 | 12.3271 | 12.5023 | 12.2423 | 12.0627 | NaN | NaN | NaN | 12.5609 | 126.8387 | NaN | NaN | NaN | -3.3906 | NaN | NaN | NaN | NaN | 531.5116 | NaN | 14.9326 | NaN | 18.1261
1786.1292 | 12.6678 | 12.3671 | 12.514 | 12.7774 | 12.2543 | 12.5061 | 12.234 | 12.0634 | NaN | NaN | NaN | 12.5716 | 111.363 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 533.0841 | NaN | 22.749 | NaN | 19.8134
1787.1292 | 12.6255 | 12.3222 | 12.5087 | 12.7778 | 12.3342 | 12.481 | 12.223 | 12.0609 | NaN | NaN | NaN | 12.6031 | 117.3201 | NaN | NaN | NaN | -18.7093 | NaN | NaN | NaN | NaN | 534.6819 | NaN | 14.9678 | NaN | 16.2233
1788.1292 | 12.6371 | 12.3822 | 12.5091 | 12.7805 | 12.3801 | 12.5145 | 12.2464 | 12.0558 | NaN | NaN | NaN | 12.5671 | 121.704 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 533.3206 | NaN | 24.289 | NaN | 13.7032
1789.1292 | 12.6435 | 12.3339 | 12.5086 | 12.7712 | 12.3615 | 12.4798 | 12.2257 | 12.0589 | NaN | NaN | NaN | 12.6103 | 110.2248 | NaN | NaN | NaN | -15.4513 | NaN | NaN | NaN | NaN | 534.2163 | NaN | 16.3761 | NaN | 20.0675
1790.1292 | 12.635 | 12.33 | 12.5142 | 12.7675 | 12.3442 | 12.4845 | 12.2241 | 12.0566 | NaN | NaN | NaN | 12.5885 | 119.2771 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 533.8755 | NaN | 28.4886 | NaN | 17.0642
1791.1292 | 12.6461 | 12.3814 | 12.5112 | 12.754 | 12.3142 | 12.4994 | 12.2376 | 12.0548 | NaN | NaN | NaN | 12.5523 | 128.9869 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 537.0344 | NaN | 18.022 | NaN | 7.8712
1792.1292 | 12.6344 | 12.3315 | 12.5185 | 12.7439 | 12.292 | 12.4838 | 12.227 | 12.0545 | NaN | NaN | NaN | 12.6453 | 125.9507 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 537.2163 | NaN | 22.958 | NaN | 18.5447
1793.1292 | 12.6121 | 12.3023 | 12.5146 | 12.7968 | 12.2797 | 12.473 | 12.2265 | 12.0537 | NaN | NaN | NaN | 12.5858 | 120.6618 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 537.7522 | NaN | 8.2837 | NaN | 14.8553
1794.1292 | 12.6143 | 12.2998 | 12.5128 | 12.7857 | 12.3087 | 12.4719 | 12.2247 | 12.0457 | NaN | NaN | NaN | 12.5609 | 122.2834 | NaN | NaN | NaN | -12.6819 | NaN | NaN | NaN | NaN | 535.898 | NaN | 11.2763 | NaN | 20.6118
1795.1292 | 12.6099 | 12.3046 | 12.514 | 12.7791 | 12.3787 | 12.4803 | 12.2252 | 12.0512 | NaN | NaN | NaN | 12.5547 | 121.6451 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 535.1756 | NaN | 18.0619 | NaN | 22.5326
1796.1292 | 12.6264 | 12.3211 | 12.512 | 12.7627 | 12.225 | 12.4785 | 12.2286 | 12.0458 | NaN | NaN | NaN | 12.6094 | 119.9298 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 538.6021 | NaN | 27.6216 | NaN | 20.0695
1797.1292 | 12.6183 | 12.3574 | 12.5122 | 12.8085 | 12.3406 | 12.4818 | 12.2293 | 12.0449 | NaN | NaN | NaN | 12.5707 | 123.2905 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 534.9507 | NaN | 32.2411 | NaN | 20.3667
1798.1292 | 12.6069 | 12.2971 | 12.512 | 12.7809 | 12.3074 | 12.4582 | 12.2162 | 12.0447 | NaN | NaN | NaN | 12.5481 | 127.082 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 536.2662 | NaN | 12.8035 | NaN | 16.8449
1799.1292 | 12.6045 | 12.3131 | 12.5066 | 12.769 | 12.3323 | 12.4829 | 12.2296 | 12.0481 | NaN | NaN | NaN | 12.5589 | 116.8575 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 535.8765 | NaN | 14.2267 | NaN | 16.9917
1800.1292 | 12.6107 | 12.3427 | 12.509 | 12.7313 | 12.2884 | 12.496 | 12.2373 | 12.0426 | NaN | NaN | NaN | 12.5899 | 123.2548 | NaN | NaN | NaN | -17.9696 | NaN | NaN | NaN | NaN | 538.0101 | NaN | 13.7974 | NaN | 20.5786
1801.1292 | 12.6084 | 12.3535 | 12.5007 | 12.8311 | 12.239 | 12.4961 | 12.2366 | 12.0426 | NaN | NaN | NaN | 12.5447 | 127.3456 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 536.9525 | NaN | 6.7577 | NaN | 19.1287
1802.1292 | 12.6144 | 12.3501 | 12.4971 | 12.7497 | 12.2768 | 12.488 | 12.228 | 12.0415 | NaN | NaN | NaN | 12.5444 | 133.0177 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 536.4168 | NaN | 30.5518 | NaN | 15.4867
1803.1292 | 12.6111 | 12.3485 | 12.5002 | 12.7088 | 12.31 | 12.4868 | 12.2173 | 12.0372 | NaN | NaN | NaN | 12.5657 | 124.0753 | NaN | NaN | NaN | -15.1572 | NaN | NaN | NaN | NaN | 538.1772 | NaN | 26.6451 | NaN | 18.7191
1804.1292 | 12.6113 | 12.2932 | 12.5029 | 12.7708 | 12.2629 | 12.4572 | 12.2128 | 12.0431 | NaN | NaN | NaN | 12.5499 | 125.5272 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 536.8847 | NaN | 12.2976 | NaN | 15.8507
1805.1292 | 12.6677 | 12.2806 | 12.5043 | 12.7775 | 12.3453 | 12.4706 | 12.2248 | 12.0453 | NaN | NaN | NaN | 12.5626 | 121.5571 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 536.8536 | NaN | 16.1289 | NaN | 14.3266
1806.1292 | 12.598 | 12.3569 | 12.4972 | 12.7525 | 12.296 | 12.5067 | 12.2358 | 12.0397 | NaN | NaN | NaN | 12.5548 | 133.077 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 539.87 | NaN | 16.5454 | NaN | 32.5726
1807.1292 | 12.5995 | 12.3037 | 12.4984 | 12.7374 | 12.2828 | 12.4654 | 12.2238 | 12.0399 | NaN | NaN | NaN | 12.5429 | 117.4172 | NaN | NaN | NaN | 3.865 | NaN | NaN | NaN | NaN | 541.4413 | NaN | 15.2617 | NaN | 18.8833
1808.1292 | 12.5944 | 12.3392 | 12.4964 | 12.7681 | 12.3443 | 12.4791 | 12.2235 | 12.0353 | NaN | NaN | NaN | 12.5118 | 127.1773 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 545.4339 | NaN | 24.8175 | NaN | 21.0967
1809.1292 | 12.6035 | 12.2823 | 12.503 | 12.7463 | 12.2781 | 12.4561 | 12.2169 | 12.0397 | NaN | NaN | NaN | 12.5195 | 124.1823 | NaN | NaN | NaN | 4.9839 | NaN | NaN | NaN | NaN | 542.7706 | NaN | 25.1623 | NaN | 17.9697
1810.1292 | 12.6009 | 12.3097 | 12.5001 | 12.7337 | 12.2857 | 12.47 | 12.2167 | 12.0392 | NaN | NaN | NaN | 12.5315 | 136.1786 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 542.6614 | NaN | 28.0708 | NaN | 9.7575
1811.1292 | 12.6015 | 12.3151 | 12.4931 | 12.744 | 12.2608 | 12.4758 | 12.2271 | 12.0415 | NaN | NaN | NaN | 12.5349 | 120.4138 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 543.3611 | NaN | 27.914 | NaN | 19.6246
1812.1292 | 12.6075 | 12.3041 | 12.4971 | 12.7459 | 12.3481 | 12.4569 | 12.2183 | 12.0374 | NaN | NaN | NaN | 12.5576 | 137.6877 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 543.3045 | NaN | 14.9319 | NaN | 11.3494
1813.1292 | 12.6396 | 12.2823 | 12.5015 | 12.747 | 12.3165 | 12.4568 | 12.22 | 12.0394 | NaN | NaN | NaN | 12.5484 | 125.3643 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 541.7598 | NaN | 20.0933 | NaN | 17.7258
1814.1292 | 12.614 | 12.3233 | 12.4938 | 12.7493 | 12.3322 | 12.4849 | 12.231 | 12.0365 | NaN | NaN | NaN | 12.5299 | 119.0295 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 544.126 | NaN | 18.714 | NaN | 17.9321
1815.1292 | 12.632 | 12.305 | 12.4951 | 12.7404 | 12.2922 | 12.4628 | 12.2148 | 12.0402 | NaN | NaN | NaN | 12.5403 | 117.2563 | NaN | NaN | NaN | 4.8788 | NaN | NaN | NaN | NaN | 543.5332 | NaN | 31.7354 | NaN | 15.4824
1816.1292 | 12.6426 | 12.3168 | 12.4976 | 12.7462 | 12.3532 | 12.4658 | 12.2262 | 12.0374 | NaN | NaN | NaN | 12.5213 | 136.2206 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 539.1769 | NaN | 18.2264 | NaN | 20.3814
1817.1292 | 12.606 | 12.3007 | 12.4949 | 12.7247 | 12.2987 | 12.4567 | 12.2099 | 12.0331 | NaN | NaN | NaN | 12.5532 | 129.3374 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 538.3025 | NaN | 12.1985 | NaN | 16.777
1818.1292 | 12.6095 | 12.3033 | 12.4973 | 12.7308 | 12.2834 | 12.4655 | 12.2237 | 12.0333 | NaN | NaN | NaN | 12.5317 | 121.9373 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 542.8827 | NaN | 22.3147 | NaN | 19.8157
1819.1292 | 12.6471 | 12.2817 | 12.4973 | 12.7402 | 12.2655 | 12.4455 | 12.2113 | 12.036 | NaN | NaN | NaN | 12.5313 | 120.7126 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 545.5352 | NaN | 27.01 | NaN | 20.0312
1820.1292 | 12.5816 | 12.2928 | 12.4958 | 12.7181 | 12.2955 | 12.4435 | 12.217 | 12.0359 | NaN | NaN | NaN | 12.5317 | 128.2368 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 545.8279 | NaN | 27.9242 | NaN | 19.7747
1821.1292 | 12.598 | 12.3061 | 12.4986 | 12.7109 | 12.2976 | 12.4622 | 12.2166 | 12.0353 | NaN | NaN | NaN | 12.533 | 131.7286 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 544.07 | NaN | 31.0636 | NaN | 17.5275
1822.1292 | 12.6149 | 12.2693 | 12.4998 | 12.7316 | 12.3159 | 12.4498 | 12.2142 | 12.04 | NaN | NaN | NaN | 12.5418 | 137.2237 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 543.4511 | NaN | 17.9065 | NaN | 19.9629
1823.1292 | 12.6149 | 12.2857 | 12.5038 | 12.8062 | 12.3226 | 12.4498 | 12.2185 | 12.0331 | NaN | NaN | NaN | 12.5334 | 123.8736 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 543.2919 | NaN | 10.7726 | NaN | 14.4814
1824.1292 | 12.7016 | 12.2682 | 12.5003 | 12.7374 | 12.2983 | 12.441 | 12.2031 | 12.0306 | NaN | NaN | NaN | 12.5087 | 121.9059 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 543.0826 | NaN | 15.0652 | NaN | 16.6755
1825.1292 | 12.6177 | 12.27 | 12.4969 | 12.7245 | 12.2481 | 12.4601 | 12.2211 | 12.0336 | NaN | NaN | NaN | 12.5277 | 127.5875 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 541.945 | NaN | 15.5086 | NaN | 18.5994
1826.1292 | 12.6443 | 12.2989 | 12.4972 | 12.7054 | 12.2687 | 12.4768 | 12.231 | 12.0293 | NaN | NaN | NaN | 12.5345 | 114.0794 | NaN | NaN | NaN | 1.9067 | NaN | NaN | NaN | NaN | 544.3551 | NaN | 22.2482 | NaN | 20.0723
1827.1292 | 12.7239 | 12.2845 | 12.5035 | 12.7247 | 12.2503 | 12.4607 | 12.2159 | 12.0326 | NaN | NaN | NaN | 12.5654 | 129.1525 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 545.3817 | NaN | 16.3525 | NaN | 19.3815
1828.1292 | 12.66 | 12.2911 | 12.5036 | 12.7236 | 12.2551 | 12.4687 | 12.2198 | 12.0329 | NaN | NaN | NaN | 12.5462 | 127.4324 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 546.7571 | NaN | 17.335 | NaN | 19.4466
1829.1292 | 12.6142 | 12.3058 | 12.4985 | 12.7321 | 12.3123 | 12.4574 | 12.2171 | 12.0228 | NaN | NaN | NaN | 12.5091 | 114.4473 | NaN | NaN | NaN | -16.3054 | NaN | NaN | NaN | NaN | 546.0464 | NaN | 11.4489 | NaN | 20.0744
1830.1292 | 12.6347 | 12.2858 | 12.5088 | 12.7362 | 12.3007 | 12.4575 | 12.2159 | 12.0312 | NaN | NaN | NaN | 12.4822 | 122.5875 | NaN | NaN | NaN | 9.1832 | NaN | NaN | NaN | NaN | 546.6333 | NaN | 22.1772 | NaN | 19.6412
1831.1292 | 12.632 | 12.3098 | 12.5035 | 12.7535 | 12.2887 | 12.4674 | 12.213 | 12.0316 | NaN | NaN | NaN | 12.5103 | 117.8301 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 546.9391 | NaN | 20.399 | NaN | 18.8159
1832.1292 | 12.6568 | 12.3186 | 12.4999 | 12.7487 | 12.2743 | 12.4649 | 12.2122 | 12.0287 | NaN | NaN | NaN | 12.4811 | 117.0165 | NaN | NaN | NaN | -10.4623 | NaN | NaN | NaN | NaN | 544.742 | NaN | 29.2956 | NaN | 18.2893
1833.1292 | 12.6215 | 12.3656 | 12.5071 | 12.7649 | 12.27 | 12.4941 | 12.2179 | 12.0254 | NaN | NaN | NaN | 12.4931 | 131.0557 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 544.7265 | NaN | 19.0037 | NaN | 12.4451
1834.1292 | 12.6057 | 12.3405 | 12.5044 | 12.732 | 12.2592 | 12.4905 | 12.2167 | 12.0306 | NaN | NaN | NaN | 12.5033 | 117.6512 | NaN | NaN | NaN | -18.4424 | NaN | NaN | NaN | NaN | 542.7395 | NaN | 18.415 | NaN | 5.7251
1835.1292 | 12.6613 | 12.2732 | 12.5011 | 12.752 | 12.3036 | 12.4411 | 12.1943 | 12.0347 | NaN | NaN | NaN | 12.5019 | 120.4263 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 545.6685 | NaN | 26.5308 | NaN | 16.9548
1836.1292 | 12.6337 | 12.3167 | 12.5026 | 12.7502 | 12.3006 | 12.4762 | 12.208 | 12.0273 | NaN | NaN | NaN | 12.4697 | 120.07 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 545.65 | NaN | 19.6339 | NaN | 19.3677
1837.1292 | 12.6398 | 12.3317 | 12.4994 | 12.7217 | 12.2361 | 12.491 | 12.211 | 12.032 | NaN | NaN | NaN | 12.499 | 127.1892 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 548.2825 | NaN | 9.4035 | NaN | 9.2196
1838.1292 | 12.6276 | 12.3039 | 12.5029 | 12.7333 | 12.3038 | 12.4699 | 12.2019 | 12.0282 | NaN | NaN | NaN | 12.5505 | 124.6666 | NaN | NaN | NaN | -11.6623 | NaN | NaN | NaN | NaN | 545.6821 | NaN | 19.3301 | NaN | 17.8819
1839.1292 | 12.7043 | 12.3096 | 12.5059 | 12.7371 | 12.2278 | 12.4829 | 12.2146 | 12.0345 | NaN | NaN | NaN | 12.4833 | 123.6488 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 546.5963 | NaN | 12.4908 | NaN | 17.221
1840.1292 | 12.6436 | 12.4133 | 12.5154 | 12.7396 | 12.3196 | 12.5294 | 12.2365 | 12.0306 | NaN | NaN | NaN | 12.5436 | 121.6646 | NaN | NaN | NaN | -4.0357 | NaN | NaN | NaN | NaN | 548.2098 | NaN | 11.2941 | NaN | 20.7851
1841.1292 | 12.6007 | 12.273 | 12.5097 | 12.7346 | 12.3511 | 12.4533 | 12.2062 | 12.0354 | NaN | NaN | NaN | 12.4909 | 124.7858 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 547.8291 | NaN | 16.4622 | NaN | 9.3781
1842.1292 | 12.6032 | 12.3228 | 12.5081 | 12.7407 | 12.3405 | 12.4725 | 12.2007 | 12.0334 | NaN | NaN | NaN | 12.4836 | 122.4316 | NaN | NaN | NaN | 1.8009 | NaN | NaN | NaN | NaN | 545.9417 | NaN | 22.3589 | NaN | 18.5075
1843.1292 | 12.6022 | 12.3347 | 12.5029 | 12.7309 | 12.3002 | 12.4698 | 12.2114 | 12.0341 | NaN | NaN | NaN | 12.4416 | 120.2269 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 546.9083 | NaN | 11.7044 | NaN | 20.3384
1844.1292 | 12.622 | 12.383 | 12.5016 | 12.8017 | 12.2918 | 12.4963 | 12.2118 | 12.0331 | NaN | NaN | NaN | 12.4909 | 116.8824 | NaN | NaN | NaN | 4.4376 | NaN | NaN | NaN | NaN | 543.4168 | NaN | 25.9605 | NaN | 21.8802
1845.1292 | 12.6371 | 12.276 | 12.5038 | 12.729 | 12.2412 | 12.4503 | 12.1975 | 12.0367 | NaN | NaN | NaN | 12.4497 | 125.1231 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 540.3294 | NaN | 9.6111 | NaN | 15.9819
1846.1292 | 12.6327 | 12.3138 | 12.5087 | 12.7107 | 12.3213 | 12.4652 | 12.2022 | 12.027 | NaN | NaN | NaN | 12.4627 | 124.8564 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 540.858 | NaN | 13.271 | NaN | 15.0444
1847.1292 | 12.6392 | 12.2862 | 12.5066 | 12.7265 | 12.2979 | 12.4636 | 12.2027 | 12.029 | NaN | NaN | NaN | 12.4561 | 126.1127 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 542.964 | NaN | 26.3464 | NaN | 14.702
1848.1292 | 12.6096 | 12.3654 | 12.51 | 12.7102 | 12.2732 | 12.5042 | 12.2016 | 12.0288 | NaN | NaN | NaN | 12.4927 | 121.9187 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 545.9032 | NaN | 4.6357 | NaN | 6.1298
1849.1292 | 12.6194 | 12.3289 | 12.5035 | 12.7123 | 12.2997 | 12.4686 | 12.1963 | 12.0295 | NaN | NaN | NaN | 12.5848 | 127.2954 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 546.8535 | NaN | 11.028 | NaN | 19.0826
1850.1292 | 12.6394 | 12.2845 | 12.5011 | 12.7404 | 12.3507 | 12.4497 | 12.1975 | 12.0333 | NaN | NaN | NaN | 12.4678 | 121.7261 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 544.3712 | NaN | 13.6331 | NaN | 21.9612
1851.1292 | 12.6352 | 12.3085 | 12.502 | 12.7133 | 12.252 | 12.4584 | 12.1906 | 12.0296 | NaN | NaN | NaN | 12.4727 | 127.3886 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 549.1276 | NaN | 16.6684 | NaN | 16.7519
1852.1292 | 12.6436 | 12.335 | 12.5096 | 12.7124 | 12.3064 | 12.4711 | 12.1983 | 12.0239 | NaN | NaN | NaN | 12.4591 | 125.7368 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 546.7515 | NaN | 8.4748 | NaN | 16.411
1853.1292 | 12.6394 | 12.2971 | 12.5063 | 12.7275 | 12.2962 | 12.4461 | 12.1905 | 12.0218 | NaN | NaN | NaN | 12.4527 | 127.6455 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 547.0671 | NaN | 24.5945 | NaN | 17.6938
1854.1292 | 12.6384 | 12.3162 | 12.5052 | 12.7244 | 12.3242 | 12.4557 | 12.195 | 12.0233 | NaN | NaN | NaN | 12.4702 | 120.4422 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 547.7179 | NaN | 21.4357 | NaN | 19.1723
1855.1292 | 12.6877 | 12.3123 | 12.5126 | 12.725 | 12.2727 | 12.4582 | 12.1923 | 12.0284 | NaN | NaN | NaN | 12.5006 | 119.8801 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 547.7281 | NaN | 18.9413 | NaN | 19.4582
1856.1292 | 12.683 | 12.3085 | 12.5094 | 12.7277 | 12.222 | 12.4664 | 12.196 | 12.0266 | NaN | NaN | NaN | 12.452 | 124.7053 | NaN | NaN | NaN | 5.4797 | NaN | NaN | NaN | NaN | 547.1618 | NaN | 21.5852 | NaN | 18.6805
1857.1292 | 12.5989 | 12.3535 | 12.5119 | 12.7216 | 12.326 | 12.467 | 12.1909 | 12.0315 | NaN | NaN | NaN | 12.4734 | 119.6407 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 546.2835 | NaN | 20.46 | NaN | 19.5638
1858.1292 | 12.6719 | 12.3621 | 12.509 | 12.7128 | 12.2092 | 12.4827 | 12.1922 | 12.0319 | NaN | NaN | NaN | 12.481 | 129.1389 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 545.9896 | NaN | 22.1025 | NaN | 17.8712
1859.1292 | 12.6318 | 12.3079 | 12.5076 | 12.7235 | 12.2238 | 12.4402 | 12.1825 | 12.0228 | NaN | NaN | NaN | 12.4657 | 123.8977 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 541.6469 | NaN | 21.5967 | NaN | 19.3521
1860.1292 | 12.6244 | 12.37 | 12.5067 | 12.7283 | 12.2536 | 12.4775 | 12.1944 | 12.025 | NaN | NaN | NaN | 12.4614 | 119.6731 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 543.7947 | NaN | 23.1183 | NaN | 21.3901
1861.1292 | 12.621 | 12.3286 | 12.5123 | 12.7132 | 12.307 | 12.4512 | 12.1896 | 12.0257 | NaN | NaN | NaN | 12.4568 | 116.5554 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -15.0309 | 543.958 | NaN | 14.0985 | NaN | 16.8968
1862.1292 | 12.626 | 12.3341 | 12.513 | 12.6803 | 12.2147 | 12.4464 | 12.1753 | 12.0257 | NaN | NaN | NaN | 12.4761 | 124.6484 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -19.5365 | 542.1762 | NaN | 24.8691 | NaN | 21.1409
1863.1292 | 12.6228 | 12.324 | 12.5136 | 12.7772 | 12.2749 | 12.4513 | 12.1849 | 12.0231 | NaN | NaN | NaN | 12.4323 | 130.8783 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 534.5674 | NaN | 17.5466 | NaN | 17.6766
1864.1292 | 12.6358 | 12.3071 | 12.5102 | 12.7897 | 12.2282 | 12.4282 | 12.1774 | 12.0273 | NaN | NaN | NaN | 12.4515 | 125.5264 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 536.7212 | NaN | 29.5399 | NaN | 20.9442
1865.1292 | 12.7263 | 12.3063 | 12.5078 | 12.7361 | 12.2725 | 12.4316 | 12.1844 | 12.029 | NaN | NaN | NaN | 12.4547 | 123.821 | NaN | NaN | NaN | -4.7914 | NaN | NaN | NaN | NaN | 535.6433 | NaN | 15.3519 | NaN | 18.573
1866.1292 | 12.6361 | 12.3139 | 12.5092 | 12.6865 | 12.2564 | 12.4299 | 12.1734 | 12.0202 | NaN | NaN | NaN | 12.4614 | 120.5167 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 539.3042 | NaN | 31.5077 | NaN | 20.0632
1867.1292 | 12.6259 | 12.407 | 12.5065 | 12.7594 | 12.2986 | 12.468 | 12.1961 | 12.0205 | NaN | NaN | NaN | 12.5056 | 114.3034 | NaN | NaN | NaN | 7.7852 | NaN | NaN | NaN | NaN | 540.4177 | NaN | 14.4836 | NaN | 11.6806
1868.1292 | 12.6264 | 12.3593 | 12.5062 | 12.7376 | 12.3277 | 12.4396 | 12.1823 | 12.0198 | NaN | NaN | NaN | 12.4672 | 130.5674 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 533.1786 | NaN | 33.0771 | NaN | 20.5453
1869.1292 | 12.6308 | 12.3756 | 12.5056 | 12.7421 | 12.2858 | 12.4535 | 12.1927 | 12.0175 | NaN | NaN | NaN | 12.4721 | 126.6545 | NaN | NaN | NaN | 1.0291 | NaN | NaN | NaN | NaN | 536.3175 | NaN | 31.5562 | NaN | 19.0603
1870.1292 | 12.6245 | 12.345 | 12.5032 | 12.7213 | 12.2881 | 12.4399 | 12.1943 | 12.0206 | NaN | NaN | NaN | 12.4491 | 119.7507 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 539.5533 | NaN | 19.0429 | NaN | 19.1048
1871.1292 | 12.6218 | 12.4284 | 12.505 | 12.8244 | 12.226 | 12.4682 | 12.2047 | 12.0143 | NaN | NaN | NaN | 12.4705 | 112.9616 | NaN | NaN | NaN | -11.2317 | NaN | NaN | NaN | NaN | 542.5568 | NaN | 19.1634 | NaN | 17.7507
1872.1292 | 12.6236 | 12.3222 | 12.5004 | 12.7103 | 12.2041 | 12.4213 | 12.1805 | 12.0125 | NaN | NaN | NaN | 12.4802 | 124.2198 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 543.5629 | NaN | 26.1441 | NaN | 21.3303
1873.1292 | 12.6319 | 12.3803 | 12.4981 | 12.6859 | 12.3009 | 12.452 | 12.2088 | 12.0107 | NaN | NaN | NaN | 12.4762 | 120.7465 | NaN | NaN | NaN | -16.4321 | NaN | NaN | NaN | NaN | 541.283 | NaN | 31.9871 | NaN | 19.9231
1874.1292 | 12.5947 | 12.3269 | 12.4979 | 12.794 | 12.3132 | 12.4332 | 12.1881 | 12.0189 | NaN | NaN | NaN | 12.482 | 119.467 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 542.4058 | NaN | 32.0851 | NaN | 20.0594
1875.1292 | 12.6061 | 12.3163 | 12.4976 | 12.7362 | 12.3071 | 12.4222 | 12.1773 | 12.0205 | NaN | NaN | NaN | 12.5006 | 121.8211 | NaN | NaN | NaN | -16.2039 | NaN | NaN | NaN | NaN | 542.4133 | NaN | 8.4016 | NaN | 19.9808
1876.1292 | 12.5999 | 12.2815 | 12.4995 | 12.7488 | 12.2233 | 12.4224 | 12.1849 | 12.0174 | NaN | NaN | NaN | 12.5199 | 119.1543 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 541.6747 | NaN | 16.6879 | NaN | 19.7119
1877.1292 | 12.6059 | 12.2911 | 12.4992 | 12.7236 | 12.3003 | 12.4377 | 12.1905 | 12.0156 | NaN | NaN | NaN | 12.5231 | 123.0168 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 544.2995 | NaN | 16.4836 | NaN | 18.7572
1878.1292 | 12.6209 | 12.3116 | 12.5003 | 12.7152 | 12.2425 | 12.4262 | 12.173 | 12.0217 | NaN | NaN | NaN | 12.5471 | 119.0349 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 542.3759 | NaN | 9.5428 | NaN | 9.9413
1879.1292 | 12.6154 | 12.3669 | 12.5038 | 12.734 | 12.2983 | 12.4589 | 12.1985 | 12.0169 | NaN | NaN | NaN | 12.5287 | 125.1276 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 542.7275 | NaN | 28.8031 | NaN | 26.1939
1880.1292 | 12.6234 | 12.3002 | 12.5045 | 12.7225 | 12.2314 | 12.4218 | 12.1834 | 12.0171 | NaN | NaN | NaN | 12.5472 | 130.5527 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 540.2233 | NaN | 21.6717 | NaN | 23.708
1881.1292 | 12.6103 | 12.2947 | 12.5011 | 12.7444 | 12.2073 | 12.4266 | 12.181 | 12.0161 | NaN | NaN | NaN | 12.5126 | 118.9212 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 544.0336 | NaN | 11.8316 | NaN | 15.7988
1882.1292 | 12.6252 | 12.3433 | 12.5027 | 12.6983 | 12.2611 | 12.4434 | 12.1847 | 12.0203 | NaN | NaN | NaN | 12.5424 | 122.7858 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 544.2549 | NaN | 26.9636 | NaN | 19.5907
1883.1292 | 12.6237 | 12.3416 | 12.5071 | 12.6985 | 12.2963 | 12.4345 | 12.1868 | 12.0198 | NaN | NaN | NaN | 12.5206 | 127.7413 | NaN | NaN | NaN | -5.0337 | NaN | NaN | NaN | NaN | 542.0171 | NaN | 11.0206 | NaN | 16.2858
1884.1292 | 12.6246 | 12.2876 | 12.5014 | 12.7187 | 12.325 | 12.4156 | 12.1717 | 12.0211 | NaN | NaN | NaN | 12.6029 | 125.1329 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 545.9739 | NaN | 29.2343 | NaN | 20.6991
1885.1292 | 12.6362 | 12.2909 | 12.5063 | 12.6821 | 12.3086 | 12.4148 | 12.1716 | 12.018 | NaN | NaN | NaN | 12.5379 | 121.8548 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 545.5284 | NaN | 26.7276 | NaN | 19.9161
1886.1292 | 12.6294 | 12.2788 | 12.5061 | 12.7332 | 12.2958 | 12.4132 | 12.1817 | 12.0223 | NaN | NaN | NaN | 12.5432 | 121.2879 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 545.6923 | NaN | 14.2665 | NaN | 18.6285
1887.1292 | 12.6583 | 12.2735 | 12.5057 | 12.7364 | 12.3123 | 12.4049 | 12.1707 | 12.0176 | NaN | NaN | NaN | 12.5377 | 120.7469 | NaN | NaN | NaN | -5.6319 | NaN | NaN | NaN | NaN | 545.112 | NaN | 14.2294 | NaN | 19.5272
1888.1292 | 12.639 | 12.3381 | 12.5051 | 12.7059 | 12.2124 | 12.4508 | 12.1897 | 12.0148 | NaN | NaN | NaN | 12.5125 | 118.7028 | NaN | NaN | NaN | 2.3543 | NaN | NaN | NaN | NaN | 544.1495 | NaN | 27.9723 | NaN | 19.838
1889.1292 | 12.6917 | 12.2734 | 12.5084 | 12.7352 | 12.3276 | 12.4033 | 12.1679 | 12.0229 | NaN | NaN | NaN | 12.5199 | 122.8007 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 538.2661 | NaN | 17.1896 | NaN | 20.028
1890.1292 | 12.6319 | 12.2923 | 12.5096 | 12.771 | 12.3274 | 12.4207 | 12.1739 | 12.0174 | NaN | NaN | NaN | 12.5192 | 131.594 | NaN | NaN | NaN | 6.0855 | NaN | NaN | NaN | NaN | 540.9795 | NaN | 23.2899 | NaN | 20.823
1891.1292 | 12.6803 | 12.3296 | 12.5031 | 12.7369 | 12.3345 | 12.4288 | 12.1801 | 12.0152 | NaN | NaN | NaN | 12.5091 | 130.1455 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 542.2275 | NaN | 18.6282 | NaN | 16.91
1892.1292 | 12.6908 | 12.2748 | 12.496 | 12.7169 | 12.3174 | 12.4107 | 12.1727 | 12.0172 | NaN | NaN | NaN | 12.4996 | 121.8741 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 542.9274 | NaN | 22.1327 | NaN | 20.5825
1893.1292 | 12.6358 | 12.2713 | 12.497 | 12.7301 | 12.3375 | 12.4118 | 12.1652 | 12.0185 | NaN | NaN | NaN | 12.5074 | 130.3919 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 543.2353 | NaN | 24.9053 | NaN | 20.7853
1894.1292 | 12.6259 | 12.2874 | 12.4957 | 12.7331 | 12.2729 | 12.409 | 12.1701 | 12.025 | NaN | NaN | NaN | 12.5191 | 125.7765 | NaN | NaN | NaN | 0.0696 | NaN | NaN | NaN | NaN | 543.0885 | NaN | 20.2054 | NaN | 19.8424
1895.1292 | 12.6409 | 12.2915 | 12.4988 | 12.7261 | 12.2608 | 12.4059 | 12.1705 | 12.0197 | NaN | NaN | NaN | 12.5375 | 129.5545 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 542.8434 | NaN | 25.2465 | NaN | 19.2555
1896.1292 | 12.6436 | 12.3574 | 12.4958 | 12.7189 | 12.2344 | 12.4578 | 12.1847 | 12.0206 | NaN | NaN | NaN | 12.5202 | 133.2299 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 541.5707 | NaN | 13.4819 | NaN | 21.558
1897.1292 | 12.7218 | 12.3609 | 12.501 | 12.7066 | 12.1978 | 12.4532 | 12.1846 | 12.0253 | NaN | NaN | NaN | 12.4984 | 129.226 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 539.3591 | NaN | 19.7002 | NaN | 16.3543
1898.1292 | 12.6497 | 12.2956 | 12.4988 | 12.7212 | 12.2952 | 12.399 | 12.1701 | 12.0224 | NaN | NaN | NaN | 12.4934 | 126.4677 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 538.8243 | NaN | 16.7526 | NaN | 17.3934
1899.1292 | 12.6241 | 12.371 | 12.5053 | 12.7313 | 12.322 | 12.4287 | 12.1902 | 12.0232 | NaN | NaN | NaN | 12.5271 | 126.5226 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 539.7704 | NaN | 21.5883 | NaN | 20.7545
1900.1292 | 12.6288 | 12.3018 | 12.5077 | 12.7465 | 12.2776 | 12.4031 | 12.1642 | 12.0187 | NaN | NaN | NaN | 12.4906 | 131.2518 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 541.8052 | NaN | 16.4057 | NaN | 26.3016
1901.1292 | 12.6355 | 12.3137 | 12.5041 | 12.7303 | 12.2757 | 12.4215 | 12.1733 | 12.027 | NaN | NaN | NaN | 12.509 | 128.9612 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 541.1125 | NaN | 14.6182 | NaN | 22.3163
1902.1448 | 12.6355 | 12.292 | 12.5012 | 12.7708 | 12.2236 | 12.4071 | 12.1766 | 12.0174 | NaN | NaN | NaN | 12.4868 | 129.3014 | NaN | NaN | NaN | -2.6534 | NaN | NaN | NaN | NaN | 538.1172 | NaN | 16.0996 | NaN | 17.1975
1903.1292 | 12.6275 | 12.2926 | 12.508 | 12.7411 | 12.2517 | 12.4092 | 12.1722 | 12.0192 | NaN | NaN | NaN | 12.4964 | 120.8905 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 539.2518 | NaN | 35.0286 | NaN | 18.9544
1904.1448 | 12.6355 | 12.288 | 12.5046 | 12.72 | 12.3045 | 12.4021 | 12.1642 | 12.0198 | NaN | NaN | NaN | 12.5137 | 122.6539 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 541.5787 | NaN | 22.2372 | NaN | 18.8702
1905.1292 | 12.6328 | 12.3753 | 12.5048 | 12.7381 | 12.3145 | 12.4408 | 12.1778 | 12.0196 | NaN | NaN | NaN | 12.5123 | 128.9584 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 541.1888 | NaN | 20.5685 | NaN | 6.2783
1906.1292 | 12.639 | 12.3509 | 12.5007 | 12.7025 | 12.2231 | 12.4398 | 12.1746 | 12.0193 | NaN | NaN | NaN | 12.4783 | 126.0058 | NaN | NaN | NaN | -19.484 | NaN | NaN | NaN | NaN | 542.1785 | NaN | 6.4431 | NaN | 21.9245
1907.1292 | 12.6377 | 12.3265 | 12.5056 | 12.7573 | 12.3364 | 12.4213 | 12.1762 | 12.0199 | NaN | NaN | NaN | 12.4979 | 129.3437 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 541.1219 | NaN | 24.3213 | NaN | 24.5625
1908.1292 | 12.6136 | 12.2702 | 12.5104 | 12.8091 | 12.2331 | 12.4099 | 12.1791 | 12.0226 | NaN | NaN | NaN | 12.5098 | 122.5024 | NaN | NaN | NaN | -19.8262 | NaN | NaN | NaN | NaN | 540.6087 | NaN | 13.64 | NaN | 18.7865
1909.1292 | 12.6557 | 12.3161 | 12.5124 | 12.7619 | 12.3138 | 12.4221 | 12.1789 | 12.0164 | NaN | NaN | NaN | 12.5034 | 115.5911 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 539.5637 | NaN | 30.5979 | NaN | 18.7241
1910.1292 | 12.6011 | 12.3147 | 12.5103 | 12.7629 | 12.3048 | 12.4327 | 12.1813 | 12.0279 | NaN | NaN | NaN | 12.5132 | 119.6286 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 538.7557 | NaN | 13.9289 | NaN | 19.6386
1911.1292 | 12.7387 | 12.3681 | 12.5096 | 12.7128 | 12.2312 | 12.4594 | 12.1844 | 12.0281 | NaN | NaN | NaN | 12.4722 | 119.7767 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 538.2719 | NaN | 12.8218 | NaN | 5.6535
1912.1292 | 12.615 | 12.3035 | 12.5073 | 12.7783 | 12.3385 | 12.4215 | 12.1745 | 12.0246 | NaN | NaN | NaN | 12.5054 | 120.2627 | NaN | NaN | NaN | 7.6025 | NaN | NaN | NaN | NaN | 539.2023 | NaN | 18.936 | NaN | 9.3907
1913.1292 | 12.6113 | 12.3034 | 12.5122 | 12.7641 | 12.3229 | 12.4035 | 12.1734 | 12.0238 | NaN | NaN | NaN | 12.5197 | 126.5637 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 538.3102 | NaN | 13.4622 | NaN | 20.425
1914.1292 | 12.6553 | 12.278 | 12.5113 | 12.7696 | 12.3365 | 12.3926 | 12.1644 | 12.0248 | NaN | NaN | NaN | 12.4882 | 118.7469 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 538.0237 | NaN | 16.5906 | NaN | 20.6041
1915.1292 | 12.6288 | 12.2853 | 12.5101 | 12.7503 | 12.2985 | 12.399 | 12.1789 | 12.0227 | NaN | NaN | NaN | 12.54 | 121.9209 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 537.9926 | NaN | 23.138 | NaN | 19.3324
1916.1292 | 12.6266 | 12.2906 | 12.512 | 12.7272 | 12.2947 | 12.4014 | 12.1763 | 12.0365 | NaN | NaN | NaN | 12.4829 | 133.4318 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 537.4323 | NaN | 17.5666 | NaN | 13.8193
1917.1292 | 12.6317 | 12.3417 | 12.5128 | 12.7461 | 12.2402 | 12.4215 | 12.1781 | 12.0314 | NaN | NaN | NaN | 12.5088 | 119.9943 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 536.1447 | NaN | 25.1021 | NaN | 17.5374
1918.1292 | 12.6356 | 12.3625 | 12.5152 | 12.7585 | 12.3008 | 12.4359 | 12.1927 | 12.0314 | NaN | NaN | NaN | 12.5344 | 109.6007 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 523.0194 | NaN | 13.4862 | NaN | 20.7064
1919.1292 | 12.6398 | 12.381 | 12.5139 | 12.7291 | 12.2912 | 12.4582 | 12.1935 | 12.0284 | NaN | NaN | NaN | 12.4748 | 131.3304 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 538.3337 | NaN | 32.1106 | NaN | 17.9214
1920.1292 | 12.6548 | 12.2803 | 12.5124 | 12.7431 | 12.2544 | 12.3923 | 12.1637 | 12.0353 | NaN | NaN | NaN | 12.4798 | 130.0969 | NaN | NaN | NaN | 1.6895 | NaN | NaN | NaN | NaN | 535.6503 | NaN | 26.6912 | NaN | 17.0777
1921.1292 | 12.6453 | 12.2732 | 12.5084 | 12.751 | 12.317 | 12.3912 | 12.1675 | 12.0351 | NaN | NaN | NaN | 12.4951 | 138.6591 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 534.1112 | NaN | 32.8299 | NaN | 19.2746
1922.1292 | 12.6496 | 12.3231 | 12.5171 | 12.7399 | 12.2817 | 12.4177 | 12.1833 | 12.0376 | NaN | NaN | NaN | 12.485 | 120.6295 | NaN | NaN | NaN | 3.5301 | NaN | NaN | NaN | NaN | 538.5677 | NaN | 4.4661 | NaN | 10.4418
1923.1292 | 12.6825 | 12.2975 | 12.5101 | 12.8035 | 12.3387 | 12.3983 | 12.1821 | 12.0368 | NaN | NaN | NaN | 12.5068 | 118.0847 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 534.8216 | NaN | 17.016 | NaN | 20.9842
1924.1292 | 12.6497 | 12.2991 | 12.5114 | 12.7478 | 12.2894 | 12.4135 | 12.1822 | 12.036 | NaN | NaN | NaN | 12.4836 | 118.6279 | NaN | NaN | NaN | 1.6021 | NaN | NaN | NaN | NaN | 535.2453 | NaN | 17.1822 | NaN | 22.0759
1925.1292 | 12.7463 | 12.2542 | 12.5092 | 12.7499 | 12.2975 | 12.3927 | 12.175 | 12.0407 | NaN | NaN | NaN | 12.5057 | 128.5722 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 534.0421 | NaN | 6.9823 | NaN | 12.0117
1926.1292 | 12.7216 | 12.2736 | 12.5091 | 12.7429 | 12.2274 | 12.4009 | 12.178 | 12.0441 | NaN | NaN | NaN | 12.4777 | 117.561 | NaN | NaN | NaN | -18.5519 | NaN | NaN | NaN | NaN | 534.7225 | NaN | 11.8524 | NaN | 17.4781
1927.1292 | 12.6304 | 12.2789 | 12.5112 | 12.7753 | 12.2537 | 12.4124 | 12.1873 | 12.0405 | NaN | NaN | NaN | 12.5151 | 119.6358 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 538.1324 | NaN | 25.5923 | NaN | 8.9086
1928.1292 | 12.638 | 12.2998 | 12.5093 | 12.7517 | 12.3138 | 12.4064 | 12.1868 | 12.0436 | NaN | NaN | NaN | 12.5216 | 128.3692 | NaN | NaN | NaN | 10.6455 | NaN | NaN | NaN | NaN | 538.7039 | NaN | 17.094 | NaN | 18.3642
1929.1292 | 12.6414 | 12.2984 | 12.5045 | 12.7553 | 12.2978 | 12.399 | 12.182 | 12.0384 | NaN | NaN | NaN | 12.4913 | 136.641 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 533.2442 | NaN | 20.5464 | NaN | 17.856
1930.1292 | 12.6495 | 12.3406 | 12.5122 | 12.7538 | 12.2718 | 12.4092 | 12.1908 | 12.0453 | NaN | NaN | NaN | 12.5354 | 122.6363 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 534.0413 | NaN | 14.1956 | NaN | 19.2766
1931.1292 | 12.6446 | 12.3612 | 12.5089 | 12.7589 | 12.296 | 12.432 | 12.1909 | 12.0444 | NaN | NaN | NaN | 12.4873 | 133.5525 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 529.0745 | NaN | 27.9751 | NaN | 19.7151
1932.1292 | 12.6482 | 12.2661 | 12.5068 | 12.7346 | 12.2944 | 12.3881 | 12.1688 | 12.0466 | NaN | NaN | NaN | 12.5207 | 126.3099 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 525.2557 | NaN | 11.1759 | NaN | 13.5784
1933.1292 | 12.6513 | 12.2623 | 12.5027 | 12.7275 | 12.2306 | 12.3864 | 12.1807 | 12.0454 | NaN | NaN | NaN | 12.5357 | 128.3348 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 525.8109 | NaN | 24.5463 | NaN | 22.3268
1934.1292 | 12.6702 | 12.2676 | 12.5047 | 12.7621 | 12.3071 | 12.397 | 12.1789 | 12.0412 | NaN | NaN | NaN | 12.5301 | 124.0968 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 525.7438 | NaN | 24.6341 | NaN | 11.6048
1935.1292 | 12.8142 | 12.293 | 12.5034 | 12.7942 | 12.309 | 12.4148 | 12.1883 | 12.0513 | NaN | NaN | NaN | 12.5397 | 115.7724 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 527.1847 | NaN | 15.9091 | NaN | 22.8364
1936.1292 | 12.6554 | 12.2747 | 12.5066 | 12.8108 | 12.3252 | 12.3844 | 12.1779 | 12.046 | NaN | NaN | NaN | 12.5473 | 127.0163 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 525.1963 | NaN | 21.2266 | NaN | 7.9756
1937.1292 | 12.6305 | 12.2625 | 12.5097 | 12.7272 | 12.2958 | 12.3931 | 12.1731 | 12.0512 | NaN | NaN | NaN | 12.532 | 121.7072 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 526.3776 | NaN | 11.1724 | NaN | 20.5565
1938.1292 | 12.6347 | 12.2719 | 12.5057 | 12.7755 | 12.305 | 12.3885 | 12.1885 | 12.0496 | NaN | NaN | NaN | 12.5664 | 127.1403 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 523.3936 | NaN | 15.3231 | NaN | 11.1816
1939.1292 | 12.6458 | 12.3138 | 12.5099 | 12.7635 | 12.284 | 12.4105 | 12.189 | 12.049 | NaN | NaN | NaN | 12.5481 | 117.0957 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 523.5012 | NaN | 26.2859 | NaN | 19.9877
1940.1292 | 12.6565 | 12.3737 | 12.5042 | 12.7322 | 12.2743 | 12.4394 | 12.1955 | 12.0495 | NaN | NaN | NaN | 12.5393 | 125.5531 | NaN | NaN | NaN | -14.2859 | NaN | NaN | NaN | NaN | 523.1414 | NaN | 14.1182 | NaN | 20.0973
1941.1292 | 12.6541 | 12.3197 | 12.5115 | 12.7825 | 12.2823 | 12.4133 | 12.1878 | 12.0456 | NaN | NaN | NaN | 12.5774 | 121.0998 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 521.953 | NaN | 20.9271 | NaN | 11.3299
1942.1292 | 12.6656 | 12.2935 | 12.5075 | 12.7723 | 12.3063 | 12.3814 | 12.1728 | 12.0509 | NaN | NaN | NaN | 12.5603 | 126.9117 | NaN | NaN | NaN | -12.5373 | NaN | NaN | NaN | NaN | 524.8831 | NaN | 15.9028 | NaN | 17.7637
1943.1292 | 12.663 | 12.2737 | 12.5009 | 12.7115 | 12.2507 | 12.3948 | 12.1743 | 12.0538 | NaN | NaN | NaN | 12.5725 | 118.6164 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 525.4456 | NaN | 20.3691 | NaN | 16.8669
1944.1292 | 12.6613 | 12.2649 | 12.5082 | 12.793 | 12.2785 | 12.3883 | 12.1764 | 12.0485 | NaN | NaN | NaN | 12.5665 | 123.5068 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 523.1268 | NaN | 13.5179 | NaN | 8.8413
1945.1292 | 12.6675 | 12.3283 | 12.5006 | 12.8193 | 12.2972 | 12.405 | 12.19 | 12.0528 | NaN | NaN | NaN | 12.5646 | 130.2047 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 523.8292 | NaN | 31.2018 | NaN | 21.3395
1946.1292 | 12.6679 | 12.2758 | 12.5046 | 12.7744 | 12.2112 | 12.3842 | 12.1828 | 12.0504 | NaN | NaN | NaN | 12.5694 | 125.6026 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 526.5588 | NaN | 15.9297 | NaN | 19.9106
1947.1292 | 12.7035 | 12.273 | 12.5128 | 12.7783 | 12.2774 | 12.3864 | 12.1795 | 12.0547 | NaN | NaN | NaN | 12.5694 | 115.2318 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 530.4806 | NaN | 24.3123 | NaN | 17.8145
1948.1292 | 12.6399 | 12.2738 | 12.5026 | 12.7886 | 12.2493 | 12.3915 | 12.1803 | 12.0512 | NaN | NaN | NaN | 12.5642 | 115.1307 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 529.4464 | NaN | 18.6843 | NaN | 5.6692
1949.1292 | 12.7339 | 12.2953 | 12.5076 | 12.7612 | 12.244 | 12.3961 | 12.1786 | 12.0541 | NaN | NaN | NaN | 12.5423 | 122.6601 | NaN | NaN | NaN | -7.3011 | NaN | NaN | NaN | NaN | 528.4897 | NaN | 16.3918 | NaN | 10.9973
1950.1292 | 12.6369 | 12.2765 | 12.5072 | 12.8061 | 12.1895 | 12.3849 | 12.1837 | 12.0511 | NaN | NaN | NaN | 12.5424 | 123.525 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 528.3229 | NaN | 7.3458 | NaN | 20.0005
1951.1292 | 12.6652 | 12.3193 | 12.504 | 12.7798 | 12.2741 | 12.4149 | 12.1879 | 12.0519 | NaN | NaN | NaN | 12.5685 | 133.6836 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 526.6209 | NaN | 29.2954 | NaN | 17.9332
1952.1292 | 12.6158 | 12.2902 | 12.5081 | 12.7664 | 12.2803 | 12.4001 | 12.1779 | 12.0498 | NaN | NaN | NaN | 12.5807 | 124.1742 | NaN | NaN | NaN | -10.3106 | NaN | NaN | NaN | NaN | 526.5022 | NaN | 3.5221 | NaN | 20.3531
1953.1292 | 12.6687 | 12.2855 | 12.5073 | 12.7535 | 12.2383 | 12.4039 | 12.1826 | 12.05 | NaN | NaN | NaN | 12.6009 | 122.0598 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 523.8106 | NaN | 15.0491 | NaN | 19.3022
1954.1292 | 12.7453 | 12.2675 | 12.5116 | 12.7892 | 12.3036 | 12.3969 | 12.1812 | 12.0495 | NaN | NaN | NaN | 12.5384 | 121.0177 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 528.5073 | NaN | 11.902 | NaN | 16.9032
1955.1292 | 12.6532 | 12.2598 | 12.5127 | 12.7727 | 12.3024 | 12.3864 | 12.1811 | 12.0406 | NaN | NaN | NaN | 12.5517 | 119.911 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 522.8107 | NaN | 36.7219 | NaN | 15.3385
1956.1292 | 12.6742 | 12.2663 | 12.5006 | 12.7685 | 12.3108 | 12.3853 | 12.1798 | 12.0457 | NaN | NaN | NaN | 12.5699 | 114.9182 | NaN | NaN | NaN | 4.9739 | NaN | NaN | NaN | NaN | 524.7915 | NaN | 18.8605 | NaN | 22.5351
1957.1292 | 12.6912 | 12.2595 | 12.5066 | 12.8055 | 12.2493 | 12.3851 | 12.1815 | 12.05 | NaN | NaN | NaN | 12.5575 | 120.0807 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 523.3126 | NaN | 19.2282 | NaN | 14.607
1958.1292 | 12.6583 | 12.2846 | 12.5079 | 12.7562 | 12.2749 | 12.4009 | 12.1796 | 12.051 | NaN | NaN | NaN | 12.5626 | 121.6968 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 526.3831 | NaN | 29.9135 | NaN | 10.1735
1959.1292 | 12.6375 | 12.2595 | 12.5073 | 12.769 | 12.2605 | 12.3915 | 12.1805 | 12.0505 | NaN | NaN | NaN | 12.5664 | 116.1954 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 526.8541 | NaN | 22.0888 | NaN | 25.5649
1960.1292 | 12.6147 | 12.2891 | 12.5 | 12.7462 | 12.314 | 12.4002 | 12.1787 | 12.0494 | NaN | NaN | NaN | 12.555 | 118.4806 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 527.2087 | NaN | 13.6797 | NaN | 15.8001
1961.1292 | 12.6297 | 12.3208 | 12.5074 | 12.775 | 12.3181 | 12.4254 | 12.1932 | 12.0465 | NaN | NaN | NaN | 12.585 | 122.6146 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 528.3139 | NaN | 21.3748 | NaN | 15.9752
1962.1448 | 12.6264 | 12.2966 | 12.5049 | 12.7809 | 12.2659 | 12.4084 | 12.1769 | 12.0523 | NaN | NaN | NaN | 12.5648 | 111.2986 | NaN | NaN | NaN | -0.1562 | NaN | NaN | NaN | NaN | 526.9798 | NaN | 16.962 | NaN | 20.4346
1963.1292 | 12.6269 | 12.276 | 12.501 | 12.7877 | 12.283 | 12.4026 | 12.183 | 12.0463 | NaN | NaN | NaN | 12.5459 | 123.0197 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 526.0572 | NaN | 20.2961 | NaN | 16.6753
1964.1448 | 12.643 | 12.27 | 12.5054 | 12.7729 | 12.3011 | 12.392 | 12.177 | 12.0531 | NaN | NaN | NaN | 12.5516 | 121.5608 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 528.4019 | NaN | 25.8021 | NaN | 19.2417
1965.1292 | 12.6258 | 12.2628 | 12.5035 | 12.7511 | 12.2791 | 12.3943 | 12.1762 | 12.0483 | NaN | NaN | NaN | 12.5654 | 129.8147 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 526.8547 | NaN | 11.6196 | NaN | 17.0407
1966.1292 | 12.6375 | 12.2421 | 12.5009 | 12.7748 | 12.2457 | 12.3911 | 12.1753 | 12.0503 | NaN | NaN | NaN | 12.5287 | 125.7081 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 529.1028 | NaN | 15.1668 | NaN | 15.4348
1967.1292 | 12.6185 | 12.2889 | 12.5029 | 12.778 | 12.3239 | 12.4107 | 12.1832 | 12.0477 | NaN | NaN | NaN | 12.5691 | 121.5924 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 529.9277 | NaN | 18.6915 | NaN | 18.1341
1968.1292 | 12.6194 | 12.25 | 12.5012 | 12.7968 | 12.2448 | 12.3911 | 12.1725 | 12.0491 | NaN | NaN | NaN | 12.5488 | 121.6351 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 527.7356 | NaN | 25.3601 | NaN | 17.5648
1969.1292 | 12.6311 | 12.3251 | 12.5035 | 12.8081 | 12.3357 | 12.4278 | 12.2034 | 12.0502 | NaN | NaN | NaN | 12.5485 | 127.1764 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 526.0728 | NaN | 31.0468 | NaN | 16.4692
1970.1292 | 12.6181 | 12.2267 | 12.5013 | 12.8126 | 12.2757 | 12.3921 | 12.1783 | 12.0466 | NaN | NaN | NaN | 12.5739 | 118.2897 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 528.7742 | NaN | 9.185 | NaN | 26.5967
1971.1292 | 12.6328 | 12.2331 | 12.5031 | 12.8051 | 12.3231 | 12.3952 | 12.1854 | 12.0477 | NaN | NaN | NaN | 12.5304 | 123.5098 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 528.4044 | NaN | 15.7622 | NaN | 20.0484
1972.1292 | 12.6244 | 12.3003 | 12.499 | 12.7519 | 12.266 | 12.4187 | 12.1956 | 12.0534 | NaN | NaN | NaN | 12.5308 | 128.3161 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 525.3843 | NaN | 16.1614 | NaN | 18.4257
1973.1292 | 12.6289 | 12.2261 | 12.4976 | 12.8277 | 12.282 | 12.3963 | 12.1891 | 12.0512 | NaN | NaN | NaN | 12.5533 | 133.4708 | NaN | NaN | NaN | -9.9064 | NaN | NaN | NaN | NaN | 529.5516 | NaN | 19.3327 | NaN | 16.3633
1974.1292 | 12.6311 | 12.238 | 12.5031 | 12.8232 | 12.303 | 12.3865 | 12.182 | 12.0469 | NaN | NaN | NaN | 12.5215 | 113.7666 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 530.5667 | NaN | 20.5741 | NaN | 19.649
1975.1292 | 12.6411 | 12.2753 | 12.4988 | 12.7705 | 12.3224 | 12.4088 | 12.188 | 12.052 | NaN | NaN | NaN | 12.5244 | 126.548 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 527.4855 | NaN | 22.4183 | NaN | 8.6754
1976.1292 | 12.6288 | 12.2885 | 12.5027 | 12.7754 | 12.3014 | 12.4179 | 12.2033 | 12.0423 | NaN | NaN | NaN | 12.5254 | 122.9997 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 526.2884 | NaN | 26.5235 | NaN | 25.3681
1977.1292 | 12.6425 | 12.3122 | 12.5054 | 12.7781 | 12.3161 | 12.4242 | 12.2003 | 12.0536 | NaN | NaN | NaN | 12.5554 | 138.9743 | NaN | NaN | NaN | -1.749 | NaN | NaN | NaN | NaN | 528.5002 | NaN | 10.1783 | NaN | 9.062
1978.1292 | 12.6406 | 12.2396 | 12.5035 | 12.7621 | 12.2421 | 12.3862 | 12.1802 | 12.0495 | NaN | NaN | NaN | 12.5033 | 125.0591 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 528.2697 | NaN | 21.0142 | NaN | 20.9112
1979.1292 | 12.6606 | 12.3472 | 12.5023 | 12.7647 | 12.2937 | 12.4273 | 12.2029 | 12.0524 | NaN | NaN | NaN | 12.522 | 114.4517 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 526.865 | NaN | 8.7388 | NaN | 5.8965
1980.1292 | 12.6293 | 12.2379 | 12.4994 | 12.7849 | 12.2957 | 12.3843 | 12.1812 | 12.0528 | NaN | NaN | NaN | 12.5209 | 131.5806 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 523.6089 | NaN | 29.9192 | NaN | 18.7848
1981.1292 | 12.6346 | 12.3489 | 12.502 | 12.8017 | 12.2433 | 12.4473 | 12.2063 | 12.055 | NaN | NaN | NaN | 12.5305 | 124.8176 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 527.1801 | NaN | 13.4294 | NaN | 20.1616
1982.1292 | 12.6376 | 12.267 | 12.5024 | 12.818 | 12.283 | 12.4038 | 12.1899 | 12.0544 | NaN | NaN | NaN | 12.4973 | 120.0451 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 529.4337 | NaN | 14.4166 | NaN | 7.3598
1983.1292 | 12.6443 | 12.246 | 12.498 | 12.8105 | 12.312 | 12.3876 | 12.1828 | 12.0495 | NaN | NaN | NaN | 12.5314 | 121.4135 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 527.854 | NaN | 17.5276 | NaN | 19.0635
1984.1292 | 12.6435 | 12.2504 | 12.499 | 12.7848 | 12.2429 | 12.3899 | 12.1818 | 12.0477 | NaN | NaN | NaN | 12.5044 | 136.0746 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 528.1325 | NaN | 18.1389 | NaN | 6.086
1985.1292 | 12.6708 | 12.3333 | 12.4979 | 12.7842 | 12.299 | 12.4348 | 12.2116 | 12.0515 | NaN | NaN | NaN | 12.4767 | 137.5207 | NaN | NaN | -18.7858 | NaN | NaN | NaN | NaN | NaN | 523.3799 | NaN | 6.3589 | NaN | 8.8257
1986.1292 | 12.6324 | 12.2565 | 12.502 | 12.7869 | 12.2538 | 12.3946 | 12.1855 | 12.0511 | NaN | NaN | NaN | 12.561 | 135.3888 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -18.8421 | 524.4539 | NaN | 28.4656 | NaN | 13.2584
1987.1292 | 12.6436 | 12.2573 | 12.503 | 12.7902 | 12.2788 | 12.3969 | 12.1881 | 12.0466 | NaN | NaN | NaN | 12.4775 | 123.1959 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 520.7792 | NaN | 18.3969 | NaN | 19.0061
1988.1292 | 12.6463 | 12.2711 | 12.4985 | 12.7981 | 12.3092 | 12.3965 | 12.1922 | 12.055 | NaN | NaN | NaN | 12.5143 | 124.1931 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -6.3518 | 524.4699 | NaN | 8.7876 | NaN | 15.755
1989.1292 | 12.6219 | 12.3078 | 12.4977 | 12.7754 | 12.2981 | 12.4163 | 12.1972 | 12.0509 | NaN | NaN | NaN | 12.4883 | 141.9903 | NaN | NaN | NaN | -1.5775 | NaN | NaN | NaN | NaN | 526.927 | NaN | 14.9826 | NaN | 18.9757
1990.1292 | 12.6152 | 12.3386 | 12.4984 | 12.8114 | 12.311 | 12.4193 | 12.195 | 12.0478 | NaN | NaN | NaN | 12.4854 | 120.3761 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 524.3181 | NaN | 21.9342 | NaN | 21.0835
1991.1292 | 12.6151 | 12.2888 | 12.5021 | 12.8327 | 12.3152 | 12.398 | 12.1855 | 12.0438 | NaN | NaN | NaN | 12.4931 | 129.412 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 522.699 | NaN | 11.9493 | NaN | 16.5013
1992.1292 | 12.6216 | 12.2731 | 12.4985 | 12.7905 | 12.2885 | 12.4023 | 12.1913 | 12.045 | NaN | NaN | NaN | 12.5418 | 126.4693 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 523.3131 | NaN | 17.6393 | NaN | 19.5906
1993.1292 | 12.6212 | 12.2797 | 12.4982 | 12.7773 | 12.3084 | 12.3996 | 12.1905 | 12.0428 | NaN | NaN | NaN | 12.4773 | 126.1054 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 524.5075 | NaN | 16.9806 | NaN | 18.9173
1994.1292 | 12.6345 | 12.3445 | 12.4969 | 12.7739 | 12.215 | 12.4417 | 12.194 | 12.0458 | NaN | NaN | NaN | 12.4836 | 131.3924 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 523.3613 | NaN | 22.3233 | NaN | 15.0756
1995.1292 | 12.6361 | 12.3113 | 12.4966 | 12.7662 | 12.2705 | 12.4285 | 12.2008 | 12.0465 | NaN | NaN | NaN | 12.4793 | 135.536 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 523.6323 | NaN | 14.3581 | NaN | 21.017
1996.1292 | 12.6343 | 12.3035 | 12.4962 | 12.7417 | 12.278 | 12.4121 | 12.1947 | 12.043 | NaN | NaN | NaN | 12.4954 | 117.7854 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 524.1288 | NaN | 20.8448 | NaN | 19.6446
1997.1292 | 12.6351 | 12.296 | 12.4997 | 12.7559 | 12.2454 | 12.4049 | 12.1846 | 12.0467 | NaN | NaN | NaN | 12.4883 | 124.4933 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 524.1276 | NaN | 21.6784 | NaN | 22.0593
1998.1292 | 12.5933 | 12.3452 | 12.4905 | 12.7472 | 12.3408 | 12.4048 | 12.1912 | 12.0423 | NaN | NaN | NaN | 12.5128 | 133.2117 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 523.483 | NaN | 15.9532 | NaN | 16.8116
1999.1292 | 12.604 | 12.3044 | 12.5027 | 12.8082 | 12.2754 | 12.4007 | 12.1918 | 12.0453 | NaN | NaN | NaN | 12.4612 | 123.8629 | NaN | NaN | NaN | -7.4115 | NaN | NaN | NaN | NaN | 526.0904 | NaN | 16.5487 | NaN | 19.28
2000.1448 | 12.6218 | 12.2779 | 12.4942 | 12.7814 | 12.3142 | 12.3987 | 12.1855 | 12.0479 | NaN | NaN | NaN | 12.4564 | 126.377 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 525.7702 | NaN | 18.0458 | NaN | 13.9872
2001.1292 | 12.6335 | 12.2972 | 12.4938 | 12.775 | 12.2553 | 12.4097 | 12.187 | 12.0422 | NaN | NaN | NaN | 12.4571 | 129.348 | NaN | NaN | NaN | -7.7788 | NaN | NaN | NaN | NaN | 527.2214 | NaN | 5.1219 | NaN | 18.8832
2002.1292 | 12.6268 | 12.3595 | 12.489 | 12.7791 | 12.2214 | 12.4541 | 12.209 | 12.0419 | NaN | NaN | NaN | 12.4552 | 118.2784 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 525.1363 | NaN | 22.0303 | NaN | 19.0921
2003.1448 | 12.6322 | 12.337 | 12.493 | 12.7654 | 12.2163 | 12.4382 | 12.1888 | 12.0464 | NaN | NaN | NaN | 12.4761 | 117.7035 | NaN | NaN | NaN | -3.1633 | NaN | NaN | NaN | NaN | 527.8766 | NaN | 33.8282 | NaN | 22.0244
2004.1292 | 12.6568 | 12.3627 | 12.4918 | 12.8093 | 12.3285 | 12.4285 | 12.1965 | 12.0424 | NaN | NaN | NaN | 12.4752 | 114.921 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 523.9717 | NaN | 13.2041 | NaN | 20.695
2005.1292 | 12.6144 | 12.2931 | 12.4913 | 12.7731 | 12.3352 | 12.4101 | 12.1829 | 12.0369 | NaN | NaN | NaN | 12.4991 | 127.2902 | NaN | NaN | NaN | -13.5854 | NaN | NaN | NaN | NaN | 523.5443 | NaN | 20.9777 | NaN | 16.9817
2006.1292 | 12.6185 | 12.2849 | 12.4934 | 12.7729 | 12.2828 | 12.4055 | 12.1744 | 12.0346 | NaN | NaN | NaN | 12.4999 | 126.3482 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 523.7209 | NaN | 23.0604 | NaN | 27.7882
2007.1292 | 12.6172 | 12.2835 | 12.493 | 12.7628 | 12.3184 | 12.4134 | 12.1833 | 12.0349 | NaN | NaN | NaN | 12.4589 | 123.7316 | NaN | NaN | NaN | -2.6637 | NaN | NaN | NaN | NaN | 524.031 | NaN | 17.5885 | NaN | 15.0035
2008.1292 | 12.6415 | 12.3302 | 12.4927 | 12.7749 | 12.3206 | 12.4224 | 12.1862 | 12.0292 | NaN | NaN | NaN | 12.4691 | 136.0212 | NaN | NaN | NaN | 10.3218 | NaN | NaN | NaN | NaN | 525.1438 | NaN | 23.2819 | NaN | 19.4298
2009.1292 | 12.6627 | 12.3379 | 12.4929 | 12.7811 | 12.3399 | 12.4272 | 12.1869 | 12.0332 | NaN | NaN | NaN | 12.4586 | 115.9571 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 525.775 | NaN | 16.4298 | NaN | 16.726
2010.1292 | 12.6758 | 12.288 | 12.492 | 12.7832 | 12.3167 | 12.4205 | 12.1842 | 12.0373 | NaN | NaN | NaN | 12.4551 | 123.675 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 528.3928 | NaN | 22.3544 | NaN | 21.4011
2011.1292 | 12.6295 | 12.3171 | 12.4894 | 12.7756 | 12.3155 | 12.4265 | 12.1845 | 12.0323 | NaN | NaN | NaN | 12.4329 | 126.888 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 526.4578 | NaN | 19.9766 | NaN | 19.4068
2012.1292 | 12.6193 | 12.3095 | 12.4894 | 12.759 | 12.2251 | 12.4218 | 12.1819 | 12.0349 | NaN | NaN | NaN | 12.4449 | 120.2555 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 524.6287 | NaN | 24.7687 | NaN | 19.1417
2013.1292 | 12.6319 | 12.3061 | 12.4862 | 12.7701 | 12.3272 | 12.4212 | 12.188 | 12.0341 | NaN | NaN | NaN | 12.4774 | 117.9786 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 525.9472 | NaN | 25.7852 | NaN | 19.0468
2014.1292 | 12.6387 | 12.2728 | 12.4832 | 12.7802 | 12.2473 | 12.4208 | 12.1834 | 12.0276 | NaN | NaN | NaN | 12.4473 | 131.1125 | NaN | NaN | NaN | -18.249 | NaN | NaN | NaN | NaN | 525.7805 | NaN | 30.9362 | NaN | 14.4947
2015.1292 | 12.6243 | 12.3385 | 12.4793 | 12.7746 | 12.3167 | 12.4334 | 12.1923 | 12.0291 | NaN | NaN | NaN | 12.4567 | 120.5257 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 523.2446 | NaN | 24.0762 | NaN | 17.9152
2016.1292 | 12.6787 | 12.3042 | 12.4769 | 12.7801 | 12.3193 | 12.4267 | 12.1895 | 12.0341 | NaN | NaN | NaN | 12.5145 | 124.6972 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 524.4167 | NaN | 22.6651 | NaN | 15.5573
2017.1292 | 12.6172 | 12.3079 | 12.4711 | 12.759 | 12.3166 | 12.4461 | 12.2001 | 12.0381 | NaN | NaN | NaN | 12.4518 | 122.4995 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 522.7469 | NaN | 16.2961 | NaN | 19.6413
2018.1292 | 12.6312 | 12.3295 | 12.4607 | 12.757 | 12.3253 | 12.4422 | 12.1976 | 12.0318 | NaN | NaN | NaN | 12.4493 | 133.6395 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 519.1972 | NaN | 17.9208 | NaN | 19.3289
2019.1292 | 12.626 | 12.2742 | 12.4641 | 12.7425 | 12.2767 | 12.4387 | 12.1996 | 12.0361 | NaN | NaN | NaN | 12.4797 | 131.2001 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 519.4477 | NaN | 19.5551 | NaN | 16.1679
2020.1292 | 12.634 | 12.3619 | 12.4594 | 12.8316 | 12.3035 | 12.4558 | 12.2147 | 12.0334 | NaN | NaN | NaN | 12.4459 | 131.3938 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.9974 | NaN | 4.2496 | NaN | 19.7947
2021.1292 | 12.6311 | 12.2716 | 12.468 | 12.7678 | 12.2194 | 12.4354 | 12.2003 | 12.0369 | NaN | NaN | NaN | 12.4929 | 126.0851 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.0807 | NaN | 20.9924 | NaN | 21.4742
2022.1292 | 12.6319 | 12.3221 | 12.4635 | 12.8047 | 12.2577 | 12.4665 | 12.2171 | 12.0272 | NaN | NaN | NaN | 12.4939 | 121.041 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 519.4329 | NaN | 9.8627 | NaN | 13.5814
2023.1292 | 12.6438 | 12.2713 | 12.4643 | 12.8054 | 12.2957 | 12.4303 | 12.1945 | 12.0318 | NaN | NaN | NaN | 12.4436 | 123.0092 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 516.4422 | NaN | 22.9032 | NaN | 19.3109
2024.1448 | 12.5895 | 12.2971 | 12.4624 | 12.7747 | 12.3115 | 12.437 | 12.2058 | 12.0392 | NaN | NaN | NaN | 12.4582 | 118.0846 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 516.9132 | NaN | 15.6649 | NaN | 19.2205
2025.1292 | 12.5918 | 12.2691 | 12.4657 | 12.7792 | 12.3126 | 12.4267 | 12.1926 | 12.0346 | NaN | NaN | NaN | 12.4708 | 122.0671 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 517.3815 | NaN | 15.1883 | NaN | 19.9559
2026.1292 | 12.598 | 12.2455 | 12.4619 | 12.7811 | 12.2258 | 12.4396 | 12.2011 | 12.032 | NaN | NaN | NaN | 12.4562 | 119.6018 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.9204 | NaN | 17.2422 | NaN | 17.1414
2027.1292 | 12.584 | 12.3301 | 12.4608 | 12.8212 | 12.317 | 12.47 | 12.2208 | 12.0304 | NaN | NaN | NaN | 12.4652 | 119.4253 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 521.3244 | NaN | 12.0025 | NaN | 19.6589
2028.1292 | 12.6326 | 12.257 | 12.4572 | 12.7711 | 12.3132 | 12.4435 | 12.2014 | 12.0356 | NaN | NaN | NaN | 12.4367 | 132.1514 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 520.6396 | NaN | 21.4534 | NaN | 19.0139
2029.1292 | 12.7447 | 12.2872 | 12.4627 | 12.7772 | 12.3037 | 12.4574 | 12.2049 | 12.0388 | NaN | NaN | NaN | 12.4254 | 126.0221 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 517.6168 | NaN | 20.3044 | NaN | 19.401
2030.1292 | 12.5942 | 12.2761 | 12.4591 | 12.7739 | 12.3105 | 12.4358 | 12.1959 | 12.0284 | NaN | NaN | NaN | 12.4379 | 138.5608 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 516.3384 | NaN | 28.9402 | NaN | 19.1081
2031.1292 | 12.6079 | 12.2996 | 12.4594 | 12.7507 | 12.3071 | 12.4615 | 12.203 | 12.0252 | NaN | NaN | NaN | 12.417 | 127.8282 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 515.2405 | NaN | 29.9817 | NaN | 19.5476
2032.1292 | 12.6109 | 12.2946 | 12.4609 | 12.7488 | 12.2596 | 12.4692 | 12.2037 | 12.0215 | NaN | NaN | NaN | 12.4459 | 124.2788 | NaN | NaN | NaN | -9.8424 | NaN | NaN | NaN | NaN | 518.7798 | NaN | 27.8459 | NaN | 19.8436
2033.1292 | 12.6113 | 12.233 | 12.4606 | 12.7719 | 12.3063 | 12.4295 | 12.1853 | 12.0276 | NaN | NaN | NaN | 12.4337 | 133.5959 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 519.1135 | NaN | 10.9317 | NaN | 23.9416
2034.1292 | 12.6108 | 12.2525 | 12.4565 | 12.7759 | 12.2526 | 12.4364 | 12.1922 | 12.0228 | NaN | NaN | NaN | 12.4275 | 124.5113 | NaN | NaN | NaN | -13.9829 | NaN | NaN | NaN | NaN | 518.9301 | NaN | 18.1168 | NaN | 18.7708
2035.1292 | 12.617 | 12.2266 | 12.4596 | 12.7628 | 12.2901 | 12.4407 | 12.1872 | 12.0295 | NaN | NaN | NaN | 12.4253 | 130.0602 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.6081 | NaN | 19.5884 | NaN | 18.1316
2036.1292 | 12.624 | 12.2349 | 12.458 | 12.7626 | 12.2503 | 12.4348 | 12.1958 | 12.0262 | NaN | NaN | NaN | 12.4693 | 126.7863 | NaN | NaN | NaN | -6.9853 | NaN | NaN | NaN | NaN | 521.9991 | NaN | 15.5608 | NaN | 21.5889
2037.1292 | 12.6173 | 12.2806 | 12.4609 | 12.7381 | 12.3076 | 12.4525 | 12.1954 | 12.0189 | NaN | NaN | NaN | 12.4176 | 126.011 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 523.3893 | NaN | 33.2342 | NaN | 15.0437
2038.1292 | 12.739 | 12.3006 | 12.4571 | 12.7722 | 12.2723 | 12.4732 | 12.2073 | 12.0253 | NaN | NaN | NaN | 12.408 | 124.8151 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 523.8575 | NaN | 20.2418 | NaN | 16.5111
2039.1292 | 12.5884 | 12.2526 | 12.4637 | 12.7719 | 12.287 | 12.44 | 12.1908 | 12.0226 | NaN | NaN | NaN | 12.4249 | 123.9265 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 523.3382 | NaN | 5.8858 | NaN | 19.161
2040.1292 | 12.6693 | 12.292 | 12.4578 | 12.7355 | 12.2847 | 12.4574 | 12.2044 | 12.0191 | NaN | NaN | NaN | 12.4127 | 131.0539 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 522.7017 | NaN | 28.741 | NaN | 19.3034
2041.1292 | 12.5933 | 12.3047 | 12.4622 | 12.7902 | 12.207 | 12.4695 | 12.2165 | 12.0175 | NaN | NaN | NaN | 12.4463 | 111.5717 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 525.3826 | NaN | 8.5391 | NaN | 15.594
2042.1292 | 12.5876 | 12.2526 | 12.4646 | 12.8175 | 12.2183 | 12.4486 | 12.2056 | 12.0271 | NaN | NaN | NaN | 12.4225 | 123.437 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 528.4758 | NaN | 24.8963 | NaN | 24.3031
2043.1292 | 12.6031 | 12.2659 | 12.4615 | 12.795 | 12.2189 | 12.4359 | 12.2003 | 12.0235 | NaN | NaN | NaN | 12.4251 | 129.343 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -4.6245 | 523.3218 | NaN | 13.4569 | NaN | 17.1083
2044.1292 | 12.6051 | 12.2554 | 12.4604 | 12.7836 | 12.324 | 12.4238 | 12.1887 | 12.0185 | NaN | NaN | NaN | 12.4115 | 123.3021 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 21.4691 | 526.0287 | NaN | 15.5002 | NaN | 17.8013
2045.1292 | 12.6043 | 12.2439 | 12.4617 | 12.7893 | 12.3082 | 12.4425 | 12.1907 | 12.0237 | NaN | NaN | NaN | 12.4439 | 130.2184 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 22.6853 | 526.3718 | NaN | 20.0476 | NaN | 9.5845
2046.1292 | 12.6053 | 12.2402 | 12.4554 | 12.7803 | 12.2808 | 12.4214 | 12.1846 | 12.0121 | NaN | NaN | NaN | 12.427 | 136.522 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 34.522 | 526.149 | NaN | 33.6405 | NaN | 15.2989
2047.1292 | 12.5897 | 12.2289 | 12.4581 | 12.7911 | 12.296 | 12.4072 | 12.1723 | 12.0246 | NaN | NaN | NaN | 12.4167 | 112.8162 | NaN | NaN | NaN | 3.4577 | NaN | NaN | NaN | 28.5471 | 528.3857 | NaN | 17.8072 | NaN | 20.0634
2048.1292 | 12.6334 | 12.304 | 12.4617 | 12.7733 | 12.196 | 12.4664 | 12.1964 | 12.0158 | NaN | NaN | NaN | 12.4284 | 118.2237 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 24.1039 | 528.3039 | NaN | 30.2661 | NaN | 19.0058
2049.1292 | 12.5967 | 12.228 | 12.4599 | 12.7838 | 12.2822 | 12.4168 | 12.1877 | 12.0181 | NaN | NaN | NaN | 12.4161 | 137.5475 | NaN | NaN | NaN | -3.4769 | NaN | NaN | NaN | 20.5162 | 527.8601 | NaN | 20.3416 | NaN | 13.4223
2050.1292 | 12.5976 | 12.2458 | 12.462 | 12.805 | 12.2471 | 12.4304 | 12.1943 | 12.0221 | NaN | NaN | NaN | 12.4377 | 116.1027 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 33.12 | 529.6461 | NaN | 13.1514 | NaN | 17.7927
2051.1292 | 12.5915 | 12.212 | 12.4618 | 12.7886 | 12.2421 | 12.4204 | 12.1941 | 12.0221 | NaN | NaN | NaN | 12.4747 | 135.7213 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 33.0767 | 531.343 | NaN | 10.1599 | NaN | 14.0458
2052.1292 | 12.6006 | 12.2106 | 12.4573 | 12.7738 | 12.2405 | 12.4066 | 12.1822 | 12.0243 | NaN | NaN | NaN | 12.438 | 116.705 | NaN | NaN | NaN | -13.0109 | NaN | NaN | NaN | 33.5974 | 531.706 | NaN | 10.8386 | NaN | 18.6374
2053.1292 | 12.5939 | 12.2294 | 12.4589 | 12.7793 | 12.2156 | 12.4175 | 12.1968 | 12.0221 | NaN | NaN | NaN | 12.4411 | 119.6873 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 24.768 | 533.8796 | NaN | 20.3442 | NaN | 18.2903
2054.1292 | 12.6221 | 12.25 | 12.4607 | 12.7658 | 12.2379 | 12.437 | 12.193 | 12.0205 | NaN | NaN | NaN | 12.4283 | 125.0488 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 29.9618 | 532.6691 | NaN | 22.0159 | NaN | 17.973
2055.1292 | 12.6219 | 12.2519 | 12.4609 | 12.7679 | 12.3033 | 12.431 | 12.1971 | 12.0294 | NaN | NaN | NaN | 12.4462 | 130.6886 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 21.6253 | 531.8366 | NaN | 11.8257 | NaN | 16.8758
2056.1292 | 12.6296 | 12.2394 | 12.4641 | 12.7387 | 12.206 | 12.432 | 12.1819 | 12.0273 | NaN | NaN | NaN | 12.4391 | 122.6769 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 18.8246 | 532.7386 | NaN | 15.9461 | NaN | 16.9246
2057.1292 | 12.5799 | 12.2147 | 12.4633 | 12.747 | 12.2537 | 12.4122 | 12.179 | 12.0246 | NaN | NaN | NaN | 12.4383 | 138.1085 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 29.1848 | 533.0275 | NaN | 22.0285 | NaN | 16.0643
2058.1292 | 12.5677 | 12.2615 | 12.4607 | 12.7579 | 12.2718 | 12.4286 | 12.1911 | 12.025 | NaN | NaN | NaN | 12.4206 | 125.092 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 32.8478 | 532.8681 | NaN | 16.7757 | NaN | 14.8038
2059.1292 | 12.5884 | 12.2691 | 12.4678 | 12.7589 | 12.3014 | 12.4324 | 12.189 | 12.0227 | NaN | NaN | NaN | 12.444 | 124.3416 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 19.0673 | 529.057 | NaN | 12.1033 | NaN | 18.8797
2060.1292 | 12.5763 | 12.1959 | 12.4593 | 12.7567 | 12.2713 | 12.4105 | 12.1875 | 12.0239 | NaN | NaN | NaN | 12.4371 | 130.1894 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 535.1878 | NaN | 11.5321 | NaN | 17.9209
2061.1292 | 12.5886 | 12.2072 | 12.4586 | 12.7688 | 12.2819 | 12.4192 | 12.1843 | 12.0266 | NaN | NaN | NaN | 12.453 | 124.0359 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 534.0542 | NaN | 25.0003 | NaN | 17.921
2062.1292 | 12.5939 | 12.2472 | 12.4542 | 12.7679 | 12.2625 | 12.4327 | 12.1883 | 12.021 | NaN | NaN | NaN | 12.4369 | 115.9061 | NaN | NaN | NaN | -2.3591 | NaN | NaN | NaN | NaN | 535.3626 | NaN | 20.7343 | NaN | 17.2275
2063.1292 | 12.5858 | 12.2333 | 12.4571 | 12.7746 | 12.3079 | 12.4167 | 12.1859 | 12.0289 | NaN | NaN | NaN | 12.4295 | 121.4023 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 534.8021 | NaN | 19.0041 | NaN | 18.4669
2064.1292 | 12.599 | 12.2751 | 12.456 | 12.7506 | 12.2958 | 12.4222 | 12.1898 | 12.034 | NaN | NaN | NaN | 12.4484 | 121.0924 | NaN | NaN | NaN | -7.5772 | NaN | NaN | NaN | NaN | 534.4224 | NaN | 29.9587 | NaN | 19.1438
2065.1292 | 12.6015 | 12.2073 | 12.4559 | 12.7455 | 12.2689 | 12.4207 | 12.1865 | 12.0303 | NaN | NaN | NaN | 12.4576 | 120.9765 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 535.8412 | NaN | 22.0594 | NaN | 18.2687
2066.1292 | 12.6 | 12.2694 | 12.4588 | 12.7589 | 12.2652 | 12.4265 | 12.1888 | 12.0304 | NaN | NaN | NaN | 12.4224 | 132.1497 | NaN | NaN | NaN | -0.8666 | NaN | NaN | NaN | NaN | 535.1623 | NaN | 23.1624 | NaN | 15.1885
2067.1292 | 12.5833 | 12.2308 | 12.4579 | 12.7573 | 12.2676 | 12.4142 | 12.1767 | 12.0354 | NaN | NaN | NaN | 12.4296 | 113.3276 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 535.2193 | NaN | 13.4884 | NaN | 16.0925
2068.1292 | 12.6292 | 12.2833 | 12.4618 | 12.7705 | 12.2827 | 12.4498 | 12.1989 | 12.0367 | NaN | NaN | NaN | 12.4175 | 138.4307 | NaN | NaN | NaN | -18.6324 | NaN | NaN | NaN | NaN | 532.8781 | NaN | 32.1746 | NaN | 18.3704
2069.1292 | 12.5762 | 12.2433 | 12.4602 | 12.7803 | 12.2854 | 12.4154 | 12.1842 | 12.0358 | NaN | NaN | NaN | 12.433 | 115.4705 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 535.7233 | NaN | 9.3766 | NaN | 14.9457
2070.1292 | 12.5832 | 12.2414 | 12.4614 | 12.7274 | 12.262 | 12.4114 | 12.1775 | 12.0351 | NaN | NaN | NaN | 12.4364 | 116.8515 | NaN | NaN | NaN | -10.6773 | NaN | NaN | NaN | NaN | 538.9097 | NaN | 11.002 | NaN | 20.547
2071.1292 | 12.5847 | 12.2425 | 12.4625 | 12.7747 | 12.3158 | 12.4122 | 12.1779 | 12.0302 | NaN | NaN | NaN | 12.4444 | 115.3661 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 534.3703 | NaN | 18.9054 | NaN | 20.1529
2072.1292 | 12.5788 | 12.2267 | 12.4651 | 12.7788 | 12.2127 | 12.4086 | 12.1767 | 12.0326 | NaN | NaN | NaN | 12.4344 | 117.9081 | NaN | NaN | NaN | 7.8652 | NaN | NaN | NaN | NaN | 537.2078 | NaN | 11.1251 | NaN | 18.6235
2073.1292 | 12.5805 | 12.2998 | 12.463 | 12.7238 | 12.2689 | 12.4405 | 12.1894 | 12.0343 | NaN | NaN | NaN | 12.4478 | 124.915 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 537.6847 | NaN | 14.1474 | NaN | 9.9945
2074.1292 | 12.6659 | 12.2786 | 12.4623 | 12.7598 | 12.2861 | 12.4371 | 12.1903 | 12.0355 | NaN | NaN | NaN | 12.4373 | 123.0105 | NaN | NaN | NaN | -18.7843 | NaN | NaN | NaN | NaN | 538.4977 | NaN | 29.8055 | NaN | 16.3027
2075.1292 | 12.5955 | 12.2649 | 12.4627 | 12.7266 | 12.297 | 12.4271 | 12.1769 | 12.0309 | NaN | NaN | NaN | 12.4635 | 124.1885 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 535.7265 | NaN | 8.1167 | NaN | 19.0949
2076.1292 | 12.6185 | 12.2493 | 12.4607 | 12.7813 | 12.2764 | 12.4265 | 12.1837 | 12.0353 | NaN | NaN | NaN | 12.4231 | 112.9635 | NaN | NaN | NaN | 2.3231 | NaN | NaN | NaN | NaN | 535.7721 | NaN | 16.9491 | NaN | 15.9243
2077.1292 | 12.5997 | 12.2994 | 12.4679 | 12.7813 | 12.2527 | 12.4372 | 12.1806 | 12.032 | NaN | NaN | NaN | 12.4371 | 118.9775 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 537.3765 | NaN | 16.3065 | NaN | 23.7911
2078.1292 | 12.6984 | 12.2411 | 12.4661 | 12.7986 | 12.302 | 12.4116 | 12.1736 | 12.0403 | NaN | NaN | NaN | 12.4194 | 110.7709 | NaN | NaN | NaN | 0.9408 | NaN | NaN | NaN | NaN | 536.7105 | NaN | 17.6392 | NaN | 17.0029
2079.1292 | 12.5925 | 12.2489 | 12.4636 | 12.7572 | 12.2599 | 12.4153 | 12.1771 | 12.037 | NaN | NaN | NaN | 12.4352 | 124.7328 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 537.2801 | NaN | 17.3918 | NaN | 18.4826
2080.1292 | 12.6548 | 12.2309 | 12.4621 | 12.788 | 12.1954 | 12.426 | 12.1854 | 12.0394 | NaN | NaN | NaN | 12.4307 | 123.771 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 537.7889 | NaN | 19.6333 | NaN | 18.6724
2081.1292 | 12.586 | 12.2819 | 12.4651 | 12.7487 | 12.2452 | 12.4278 | 12.1738 | 12.0417 | NaN | NaN | NaN | 12.4616 | 114.6632 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -12.6609 | 535.6957 | NaN | 9.3436 | NaN | 15.3705
2082.1292 | 12.5858 | 12.2867 | 12.4542 | 12.7602 | 12.2768 | 12.4314 | 12.1901 | 12.04 | NaN | NaN | NaN | 12.4433 | 115.0176 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -15.0872 | 538.1431 | NaN | 6.773 | NaN | 17.7754
2083.1292 | 12.5937 | 12.2498 | 12.4545 | 12.7596 | 12.2883 | 12.4152 | 12.1806 | 12.0398 | NaN | NaN | NaN | 12.4882 | 130.7608 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.623 | 535.8039 | NaN | 17.137 | NaN | 11.6493
2084.1292 | 12.593 | 12.2594 | 12.4462 | 12.7363 | 12.2005 | 12.4225 | 12.1707 | 12.0447 | NaN | NaN | NaN | 12.4193 | 129.5978 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.7186 | 534.1589 | NaN | 13.6125 | NaN | 17.2128
2085.1292 | 12.5915 | 12.2729 | 12.4423 | 12.7343 | 12.2689 | 12.4235 | 12.1725 | 12.0515 | NaN | NaN | NaN | 12.4225 | 117.3713 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 535.6854 | NaN | 22.0452 | NaN | 14.6663
2086.1292 | 12.5948 | 12.2633 | 12.4475 | 12.734 | 12.2763 | 12.424 | 12.1612 | 12.0462 | NaN | NaN | NaN | 12.4407 | 129.8744 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 534.5578 | NaN | 25.716 | NaN | 15.7498
2087.1292 | 12.5907 | 12.2967 | 12.4444 | 12.7192 | 12.3042 | 12.4259 | 12.1633 | 12.05 | NaN | NaN | NaN | 12.4597 | 117.7588 | NaN | NaN | NaN | -1.7415 | NaN | NaN | NaN | NaN | 536.4826 | NaN | 19.1557 | NaN | 16.0835
2088.1292 | 12.5929 | 12.2695 | 12.4415 | 12.774 | 12.1946 | 12.413 | 12.1569 | 12.0462 | NaN | NaN | NaN | 12.4399 | 117.3961 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 536.7901 | NaN | 9.3316 | NaN | 18.6456
2089.1292 | 12.6403 | 12.2921 | 12.4372 | 12.7683 | 12.296 | 12.4287 | 12.1678 | 12.0483 | NaN | NaN | NaN | 12.4234 | 118.3433 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 536.3489 | NaN | 20.0578 | NaN | 18.1617
2090.1292 | 12.5746 | 12.2581 | 12.4452 | 12.7724 | 12.31 | 12.4014 | 12.1446 | 12.0494 | NaN | NaN | NaN | 12.4502 | 119.5051 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 535.8625 | NaN | 21.3509 | NaN | 24.8546
2091.1292 | 12.6979 | 12.2986 | 12.4396 | 12.7655 | 12.266 | 12.4292 | 12.1596 | 12.0388 | NaN | NaN | NaN | 12.4471 | 135.9829 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 533.9349 | NaN | 23.3104 | NaN | 22.3382
2092.1292 | 12.6233 | 12.2868 | 12.4417 | 12.7711 | 12.2542 | 12.421 | 12.1613 | 12.0425 | NaN | NaN | NaN | 12.4336 | 120.9932 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 535.0618 | NaN | 26.9601 | NaN | 18.8353
2093.1292 | 12.6555 | 12.2595 | 12.4502 | 12.7581 | 12.2241 | 12.3997 | 12.1508 | 12.0422 | NaN | NaN | NaN | 12.4805 | 119.9377 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 537.9348 | NaN | 14.4552 | NaN | 13.1598
2094.1292 | 12.5766 | 12.3243 | 12.446 | 12.7437 | 12.3036 | 12.4287 | 12.169 | 12.0392 | NaN | NaN | NaN | 12.4262 | 125.4032 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 537.1274 | NaN | 20.3693 | NaN | 18.2192
2095.1292 | 12.599 | 12.3283 | 12.4473 | 12.8018 | 12.2038 | 12.4406 | 12.1754 | 12.0318 | NaN | NaN | NaN | 12.4066 | 130.8828 | NaN | NaN | NaN | -4.7794 | NaN | NaN | NaN | NaN | 536.6698 | NaN | 2.8271 | NaN | 18.3698
2096.1292 | 12.6033 | 12.3021 | 12.4508 | 12.7373 | 12.291 | 12.4175 | 12.1695 | 12.0304 | NaN | NaN | NaN | 12.4532 | 122.0417 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 536.3005 | NaN | 16.9538 | NaN | 15.9963
2097.1292 | 12.6057 | 12.3293 | 12.4508 | 12.754 | 12.2934 | 12.4461 | 12.1814 | 12.0287 | NaN | NaN | NaN | 12.4239 | 126.7869 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 535.416 | NaN | 19.9273 | NaN | 18.2228
2098.1292 | 12.5707 | 12.3246 | 12.4485 | 12.76 | 12.2472 | 12.4288 | 12.1739 | 12.0326 | NaN | NaN | NaN | 12.4306 | 127.8936 | NaN | NaN | NaN | 10.3786 | NaN | NaN | NaN | NaN | 535.0906 | NaN | 25.4343 | NaN | 18.0311
2099.1292 | 12.5791 | 12.2987 | 12.4549 | 12.7393 | 12.2431 | 12.4353 | 12.1758 | 12.0322 | NaN | NaN | NaN | 12.4206 | 117.5109 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 538.5663 | NaN | 14.1012 | NaN | 24.8227
2100.1292 | 12.5816 | 12.2816 | 12.4553 | 12.7954 | 12.2996 | 12.4101 | 12.169 | 12.0278 | NaN | NaN | NaN | 12.4074 | 125.6518 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 535.746 | NaN | 13.7067 | NaN | 15.9416
2101.1292 | 12.5857 | 12.2804 | 12.4529 | 12.7499 | 12.2643 | 12.428 | 12.1755 | 12.0328 | NaN | NaN | NaN | 12.4088 | 125.4229 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 535.6898 | NaN | 18.2227 | NaN | 17.1372
2102.1292 | 12.5948 | 12.3346 | 12.4534 | 12.7283 | 12.3047 | 12.439 | 12.1774 | 12.0276 | NaN | NaN | NaN | 12.4215 | 122.9745 | NaN | NaN | NaN | -19.309 | NaN | NaN | NaN | NaN | 533.6861 | NaN | 31.5802 | NaN | 16.4382
2103.1292 | 12.5624 | 12.3096 | 12.4513 | 12.7691 | 12.2916 | 12.4192 | 12.1748 | 12.0319 | NaN | NaN | NaN | 12.4542 | 128.1403 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 533.8572 | NaN | 28.362 | NaN | 17.6361
2104.1292 | 12.5659 | 12.3728 | 12.453 | 12.764 | 12.2975 | 12.4509 | 12.1839 | 12.0278 | NaN | NaN | NaN | 12.4439 | 119.4071 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 534.5201 | NaN | 29.4969 | NaN | 18.7867
2105.1292 | 12.5712 | 12.2925 | 12.4537 | 12.7672 | 12.2288 | 12.4353 | 12.1816 | 12.0339 | NaN | NaN | NaN | 12.4431 | 130.4744 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 533.669 | NaN | 20.0783 | NaN | 16.675
2106.1292 | 12.579 | 12.2792 | 12.4543 | 12.7678 | 12.2753 | 12.4189 | 12.1736 | 12.0275 | NaN | NaN | NaN | 12.4064 | 125.2162 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 538.2449 | NaN | 12.6404 | NaN | 18.0759
2107.1292 | 12.6373 | 12.2802 | 12.4544 | 12.7698 | 12.2763 | 12.4247 | 12.1803 | 12.0343 | NaN | NaN | NaN | 12.3929 | 121.5453 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 539.4206 | NaN | 8.8292 | NaN | 13.5329
2108.1292 | 12.5733 | 12.2922 | 12.4511 | 12.7583 | 12.2939 | 12.4058 | 12.17 | 12.0383 | NaN | NaN | NaN | 12.4392 | 125.5154 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 538.953 | NaN | 19.0482 | NaN | 17.3561
2109.1292 | 12.5707 | 12.284 | 12.4489 | 12.7459 | 12.2786 | 12.4168 | 12.1729 | 12.034 | NaN | NaN | NaN | 12.4193 | 124.732 | NaN | NaN | NaN | -6.5024 | NaN | NaN | NaN | NaN | 537.6598 | NaN | 19.8143 | NaN | 14.7208
2110.1292 | 12.5731 | 12.2948 | 12.4499 | 12.7956 | 12.2966 | 12.4099 | 12.1746 | 12.0322 | NaN | NaN | NaN | 12.402 | 128.2073 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 538.7487 | NaN | 29.826 | NaN | 16.8111
2111.1292 | 12.5775 | 12.3004 | 12.45 | 12.7618 | 12.2824 | 12.4155 | 12.18 | 12.0294 | NaN | NaN | NaN | 12.4071 | 120.195 | NaN | NaN | NaN | 3.832 | NaN | NaN | NaN | NaN | 541.7213 | NaN | 15.7952 | NaN | 17.7401
2112.1292 | 12.5753 | 12.2934 | 12.4535 | 12.7894 | 12.3033 | 12.4052 | 12.1737 | 12.0305 | NaN | NaN | NaN | 12.44 | 119.9268 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 540.5916 | NaN | 14.4128 | NaN | 18.4985
2113.1292 | 12.594 | 12.3007 | 12.4574 | 12.7685 | 12.2934 | 12.4127 | 12.18 | 12.0275 | NaN | NaN | NaN | 12.4873 | 114.5196 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 539.9519 | NaN | 20.7322 | NaN | 17.9459
2114.1292 | 12.5998 | 12.337 | 12.4513 | 12.7655 | 12.2641 | 12.4273 | 12.181 | 12.0326 | NaN | NaN | NaN | 12.412 | 121.5171 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 541.8846 | NaN | 29.9193 | NaN | 14.7609
2115.1292 | 12.7207 | 12.3104 | 12.4531 | 12.7477 | 12.2511 | 12.4275 | 12.1869 | 12.0263 | NaN | NaN | NaN | 12.4606 | 117.0934 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 543.0362 | NaN | 32.1811 | NaN | 14.0879
2116.1292 | 12.6455 | 12.2889 | 12.4533 | 12.752 | 12.2105 | 12.4078 | 12.1696 | 12.022 | NaN | NaN | NaN | 12.4426 | 114.8603 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 544.1421 | NaN | 13.5092 | NaN | 21.8692
2117.1292 | 12.6094 | 12.2924 | 12.4496 | 12.7485 | 12.2648 | 12.4042 | 12.1734 | 12.0195 | NaN | NaN | NaN | 12.4232 | 126.8809 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 541.9432 | NaN | 24.4546 | NaN | 18.2913
2118.1292 | 12.6378 | 12.2965 | 12.4566 | 12.7827 | 12.2958 | 12.4047 | 12.1712 | 12.0219 | NaN | NaN | NaN | 12.3982 | 118.536 | NaN | NaN | NaN | -8.046 | NaN | NaN | NaN | NaN | 539.6171 | NaN | 15.1615 | NaN | 17.426
2119.1292 | 12.6101 | 12.3204 | 12.4513 | 12.7734 | 12.298 | 12.4056 | 12.166 | 12.0155 | NaN | NaN | NaN | 12.4194 | 126.1025 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 543.1378 | NaN | 20.5466 | NaN | 16.8686
2120.1292 | 12.5572 | 12.3605 | 12.4521 | 12.7713 | 12.3007 | 12.4269 | 12.1787 | 12.0148 | NaN | NaN | NaN | 12.4288 | 111.7671 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 542.4531 | NaN | 21.2661 | NaN | 19.2615
2121.1292 | 12.662 | 12.3126 | 12.454 | 12.8183 | 12.2033 | 12.4191 | 12.1728 | 12.0136 | NaN | NaN | NaN | 12.4359 | 118.6359 | NaN | NaN | NaN | 0.5662 | NaN | NaN | NaN | NaN | 542.2793 | NaN | 23.8431 | NaN | 18.9156
2122.1292 | 12.6759 | 12.3317 | 12.452 | 12.7342 | 12.2745 | 12.4163 | 12.1786 | 12.0173 | NaN | NaN | NaN | 12.4277 | 124.7544 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 540.6575 | NaN | 27.2896 | NaN | 16.5391
2123.1292 | 12.5752 | 12.3272 | 12.4515 | 12.7442 | 12.2884 | 12.4194 | 12.1741 | 12.0209 | NaN | NaN | NaN | 12.4697 | 105.2895 | NaN | NaN | NaN | 1.4598 | NaN | NaN | NaN | NaN | 544.2902 | NaN | 16.6783 | NaN | 19.4304
2124.1292 | 12.5871 | 12.325 | 12.4491 | 12.7637 | 12.2769 | 12.4141 | 12.1733 | 12.0137 | NaN | NaN | NaN | 12.4176 | 116.9753 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 545.5345 | NaN | 10.5702 | NaN | 18.1843
2125.1292 | 12.5966 | 12.3143 | 12.4486 | 12.7513 | 12.212 | 12.4165 | 12.1774 | 12.0106 | NaN | NaN | NaN | 12.4479 | 122.0557 | NaN | NaN | NaN | -3.8501 | NaN | NaN | NaN | NaN | 547.0939 | NaN | 15.4839 | NaN | 16.4715
2126.1292 | 12.5971 | 12.2935 | 12.4488 | 12.7511 | 12.275 | 12.4015 | 12.1688 | 12.0125 | NaN | NaN | NaN | 12.4556 | 126.6067 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 544.398 | NaN | 18.9552 | NaN | 14.8916
2127.1292 | 12.5989 | 12.3039 | 12.4503 | 12.7464 | 12.2627 | 12.4156 | 12.1769 | 12.0111 | NaN | NaN | NaN | 12.4738 | 114.0428 | NaN | NaN | NaN | -19.4979 | NaN | NaN | NaN | NaN | 544.9802 | NaN | 11.9185 | NaN | 17.6116
2128.1292 | 12.6325 | 12.3213 | 12.4478 | 12.7553 | 12.2971 | 12.4073 | 12.1694 | 12.019 | NaN | NaN | NaN | 12.455 | 121.7668 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 543.3502 | NaN | 16.8299 | NaN | 19.6459
2129.1292 | 12.5787 | 12.3107 | 12.455 | 12.7436 | 12.2821 | 12.4057 | 12.168 | 12.0127 | NaN | NaN | NaN | 12.471 | 129.8693 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 542.7645 | NaN | 24.1219 | NaN | 18.7028
2130.1292 | 12.5886 | 12.3421 | 12.4532 | 12.7293 | 12.289 | 12.4283 | 12.1758 | 12.0128 | NaN | NaN | NaN | 12.4285 | 122.5293 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 545.8262 | NaN | 21.1556 | NaN | 15.0965
2131.1292 | 12.5964 | 12.3212 | 12.4565 | 12.8093 | 12.2239 | 12.4139 | 12.1743 | 12.0147 | NaN | NaN | NaN | 12.4372 | 125.6064 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 545.7447 | NaN | 36.3242 | NaN | 14.3866
2132.1292 | 12.6023 | 12.3695 | 12.4514 | 12.7684 | 12.2615 | 12.4267 | 12.1852 | 12.0126 | NaN | NaN | NaN | 12.4677 | 130.5918 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 546.4739 | NaN | 26.6464 | NaN | 19.608
2133.1292 | 12.6026 | 12.3405 | 12.4552 | 12.7728 | 12.2876 | 12.4208 | 12.178 | 12.012 | NaN | NaN | NaN | 12.4792 | 127.7327 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 544.8525 | NaN | 14.2729 | NaN | 16.1807
2134.1292 | 12.6096 | 12.3215 | 12.4513 | 12.7624 | 12.2264 | 12.4237 | 12.1784 | 12.0107 | NaN | NaN | NaN | 12.4394 | 123.8572 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 543.7541 | NaN | 21.5701 | NaN | 17.9914
2135.1292 | 12.6479 | 12.3126 | 12.455 | 12.7847 | 12.2284 | 12.4215 | 12.1747 | 12.0063 | NaN | NaN | NaN | 12.4761 | 115.1196 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 547.4437 | NaN | 24.7817 | NaN | 19.8945
2136.1292 | 12.6201 | 12.2774 | 12.4501 | 12.7631 | 12.3183 | 12.3997 | 12.1746 | 12.0119 | NaN | NaN | NaN | 12.4638 | 122.2142 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 548.7645 | NaN | 16.4473 | NaN | 16.498
2137.1292 | 12.5684 | 12.2998 | 12.4532 | 12.7648 | 12.2878 | 12.4235 | 12.1849 | 12.0109 | NaN | NaN | NaN | 12.4586 | 124.9548 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 548.2269 | NaN | 23.1687 | NaN | 17.0936
2138.1292 | 12.5771 | 12.3229 | 12.4519 | 12.7585 | 12.2988 | 12.4413 | 12.1933 | 12.0091 | NaN | NaN | NaN | 12.478 | 128.6422 | NaN | NaN | NaN | -8.5429 | NaN | NaN | NaN | NaN | 547.5829 | NaN | 33.237 | NaN | 19.833
2139.1292 | 12.5918 | 12.3063 | 12.4495 | 12.7772 | 12.2766 | 12.421 | 12.1868 | 12.005 | NaN | NaN | NaN | 12.4624 | 135.1126 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 545.2904 | NaN | 19.8863 | NaN | 16.8385
2140.1292 | 12.5908 | 12.2658 | 12.4531 | 12.7696 | 12.2945 | 12.3907 | 12.1847 | 12.0031 | NaN | NaN | NaN | 12.4934 | 130.3596 | NaN | NaN | NaN | -4.457 | NaN | NaN | NaN | NaN | 545.3319 | NaN | 13.8438 | NaN | 17.6742
2141.1292 | 12.5823 | 12.3515 | 12.451 | 12.7616 | 12.2583 | 12.4258 | 12.1931 | 12.0139 | NaN | NaN | NaN | 12.4389 | 126.1527 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 546.9933 | NaN | 32.4559 | NaN | 18.3684
2142.1448 | 12.5854 | 12.2999 | 12.4491 | 12.7303 | 12.2416 | 12.4177 | 12.1852 | 12.0079 | NaN | NaN | NaN | 12.4589 | 123.7292 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 550.5809 | NaN | 18.7329 | NaN | 17.8124
2143.1292 | 12.5885 | 12.314 | 12.4521 | 12.7703 | 12.2334 | 12.4246 | 12.1916 | 12.006 | NaN | NaN | NaN | 12.4641 | 117.6102 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 548.3105 | NaN | 9.3865 | NaN | 19.5584
2144.1292 | 12.5517 | 12.3257 | 12.4559 | 12.7892 | 12.2821 | 12.4327 | 12.1954 | 11.9981 | NaN | NaN | NaN | 12.4362 | 110.3586 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 548.8839 | NaN | 23.4762 | NaN | 18.0685
2145.1292 | 12.5674 | 12.3046 | 12.4532 | 12.7106 | 12.287 | 12.4187 | 12.1863 | 12.0042 | NaN | NaN | NaN | 12.4903 | 133.2229 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 548.7045 | NaN | 13.2924 | NaN | 19.6955
2146.1292 | 12.5776 | 12.2805 | 12.4551 | 12.7528 | 12.1934 | 12.4123 | 12.1858 | 12.004 | NaN | NaN | NaN | 12.4726 | 112.4939 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 549.8438 | NaN | 32.9351 | NaN | 18.315
2147.1292 | 12.5834 | 12.2648 | 12.4592 | 12.7591 | 12.2792 | 12.4009 | 12.1818 | 12.0066 | NaN | NaN | NaN | 12.4414 | 133.8454 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 549.7492 | NaN | 24.1232 | NaN | 18.0036
2148.1292 | 12.5878 | 12.3429 | 12.4557 | 12.7742 | 12.2955 | 12.426 | 12.1945 | 12.012 | NaN | NaN | NaN | 12.5706 | 128.9209 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 549.0233 | NaN | 22.711 | NaN | 17.3736
2149.1292 | 12.5881 | 12.284 | 12.4541 | 12.7602 | 12.2566 | 12.407 | 12.1886 | 12.0063 | NaN | NaN | NaN | 12.4601 | 128.7975 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 547.4409 | NaN | 27.5748 | NaN | 14.307
2150.1292 | 12.6128 | 12.2844 | 12.4559 | 12.7496 | 12.2374 | 12.4059 | 12.1906 | 12.006 | NaN | NaN | NaN | 12.439 | 117.2776 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 546.4882 | NaN | 18.9482 | NaN | 11.9617
2151.1292 | 12.5935 | 12.2599 | 12.4524 | 12.7198 | 12.1976 | 12.4105 | 12.1869 | 12.0137 | NaN | NaN | NaN | 12.4522 | 128.6832 | NaN | NaN | NaN | -5.3927 | NaN | NaN | NaN | NaN | 549.331 | NaN | 22.5358 | NaN | 11.509
2152.1292 | 12.5886 | 12.2625 | 12.4462 | 12.7704 | 12.3092 | 12.3929 | 12.1853 | 12.0097 | NaN | NaN | NaN | 12.4263 | 129.4528 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 544.8769 | NaN | 16.9621 | NaN | 8.5641
2153.1292 | 12.582 | 12.2794 | 12.453 | 12.7691 | 12.3047 | 12.4071 | 12.1904 | 12.0172 | NaN | NaN | NaN | 12.444 | 114.1806 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 544.2262 | NaN | 13.4684 | NaN | 1.1453
2154.1292 | 12.5922 | 12.327 | 12.4532 | 12.7615 | 12.2679 | 12.4238 | 12.2044 | 12.0157 | NaN | NaN | NaN | 12.4438 | 120.7701 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 545.3925 | NaN | 28.2457 | NaN | 19.4152
2155.1292 | 12.599 | 12.34 | 12.455 | 12.752 | 12.2692 | 12.4255 | 12.2014 | 12.0141 | NaN | NaN | NaN | 12.4341 | 142.4334 | NaN | NaN | NaN | 2.6424 | NaN | NaN | NaN | NaN | 544.5598 | NaN | 9.1748 | NaN | 21.5653
2156.1292 | 12.5968 | 12.3102 | 12.4533 | 12.7639 | 12.28 | 12.4317 | 12.1974 | 12.0151 | NaN | NaN | NaN | 12.4185 | 125.0401 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 545.0476 | NaN | 18.934 | NaN | 17.997
2157.1292 | 12.6061 | 12.3084 | 12.4525 | 12.7467 | 12.2718 | 12.4333 | 12.1987 | 12.0169 | NaN | NaN | NaN | 12.4779 | 129.0641 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 546.4446 | NaN | 15.6189 | NaN | 14.839
2158.1292 | 12.5661 | 12.2917 | 12.4534 | 12.7485 | 12.291 | 12.4177 | 12.1982 | 12.0199 | NaN | NaN | NaN | 12.4532 | 128.6249 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 546.0327 | NaN | 27.5449 | NaN | 16.8355
2159.1292 | 12.5812 | 12.2986 | 12.4505 | 12.7244 | 12.2908 | 12.4218 | 12.2034 | 12.0166 | NaN | NaN | NaN | 12.4289 | 119.0772 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 542.765 | NaN | 24.7196 | NaN | 17.1344
2160.1292 | 12.5888 | 12.3096 | 12.4596 | 12.8003 | 12.2223 | 12.4447 | 12.2092 | 12.0171 | NaN | NaN | NaN | 12.4275 | 128.9137 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 544.7353 | NaN | 14.0399 | NaN | 13.1681
2161.1292 | 12.6047 | 12.2799 | 12.45 | 12.751 | 12.2695 | 12.405 | 12.1938 | 12.017 | NaN | NaN | NaN | 12.4527 | 115.1342 | NaN | NaN | NaN | 7.5127 | NaN | NaN | NaN | NaN | 545.9395 | NaN | 22.0112 | NaN | 18.5966
2162.1292 | 12.6717 | 12.2896 | 12.4552 | 12.7379 | 12.2288 | 12.4219 | 12.2019 | 12.0136 | NaN | NaN | NaN | 12.4314 | 126.2351 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 546.1872 | NaN | 10.3528 | NaN | 18.2659
2163.1292 | 12.5999 | 12.3872 | 12.4612 | 12.7784 | 12.2935 | 12.4789 | 12.2367 | 12.0131 | NaN | NaN | NaN | 12.4424 | 119.1072 | NaN | NaN | 1.3178 | NaN | NaN | NaN | NaN | NaN | 543.442 | NaN | 19.4552 | NaN | 15.4882
2164.1292 | 12.5945 | 12.3548 | 12.4565 | 12.7444 | 12.2382 | 12.4437 | 12.2148 | 12.0084 | NaN | NaN | NaN | 12.4341 | 134.8349 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 544.3301 | NaN | 17.1255 | NaN | 17.0074
2165.1292 | 12.5914 | 12.3124 | 12.4541 | 12.7342 | 12.1838 | 12.4289 | 12.1995 | 12.0068 | NaN | NaN | NaN | 12.4458 | 124.0836 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 544.0262 | NaN | 20.0627 | NaN | 17.7463
2166.1292 | 12.6041 | 12.4053 | 12.4546 | 12.7223 | 12.2772 | 12.4653 | 12.2182 | 12.0128 | NaN | NaN | NaN | 12.4719 | 122.0387 | NaN | NaN | NaN | -0.0331 | NaN | NaN | NaN | NaN | 543.9421 | NaN | 18.31 | NaN | 17.0867
2167.1292 | 12.7039 | 12.2968 | 12.459 | 12.7675 | 12.2573 | 12.4272 | 12.2085 | 12.0184 | NaN | NaN | NaN | 12.4522 | 126.5719 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 545.2951 | NaN | 11.7231 | NaN | 18.5916
2168.1292 | 12.6128 | 12.3434 | 12.4583 | 12.7811 | 12.1706 | 12.4394 | 12.2033 | 12.007 | NaN | NaN | NaN | 12.4355 | 114.4035 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 544.634 | NaN | 16.5913 | NaN | 13.9974
2169.1292 | 12.735 | 12.319 | 12.4626 | 12.7387 | 12.2139 | 12.4212 | 12.2079 | 12.0122 | NaN | NaN | NaN | 12.4319 | 123.1897 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 543.203 | NaN | 17.0962 | NaN | 17.8832
2170.1292 | 12.7038 | 12.3129 | 12.4637 | 12.7189 | 12.2187 | 12.4218 | 12.2025 | 12.013 | NaN | NaN | NaN | 12.4392 | 119.2594 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 543.5486 | NaN | 26.4068 | NaN | 12.9406
2171.1292 | 12.6178 | 12.3445 | 12.4612 | 12.7875 | 12.1532 | 12.4584 | 12.209 | 12.0081 | NaN | NaN | NaN | 12.4436 | 128.0613 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 539.9452 | NaN | 24.1869 | NaN | 17.7049
2172.1292 | 12.6232 | 12.3041 | 12.4606 | 12.7557 | 12.2703 | 12.4268 | 12.206 | 12.0137 | NaN | NaN | NaN | 12.436 | 119.3469 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 539.1088 | NaN | 21.6556 | NaN | 17.4704
2173.1292 | 12.5829 | 12.3151 | 12.4558 | 12.7812 | 12.2784 | 12.4304 | 12.2151 | 12.0102 | NaN | NaN | NaN | 12.4502 | 117.0338 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 539.6585 | NaN | 30.1126 | NaN | 16.9737
2174.1292 | 12.6406 | 12.2876 | 12.4551 | 12.7461 | 12.2872 | 12.4201 | 12.1951 | 12.0114 | NaN | NaN | NaN | 12.4449 | 140.4196 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 538.8364 | NaN | 7.4645 | NaN | 9.5437
2175.1292 | 12.5831 | 12.3501 | 12.4591 | 12.7399 | 12.2025 | 12.4566 | 12.2089 | 12.0135 | NaN | NaN | NaN | 12.468 | 128.908 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 541.5895 | NaN | 9.0522 | NaN | 15.25
2176.1292 | 12.5952 | 12.2945 | 12.4665 | 12.7559 | 12.2399 | 12.4261 | 12.1979 | 12.0118 | NaN | NaN | NaN | 12.4556 | 117.0974 | NaN | NaN | NaN | -16.6898 | NaN | NaN | NaN | NaN | 545.4089 | NaN | 17.4157 | NaN | 14.7141
2177.1292 | 12.5961 | 12.2858 | 12.4533 | 12.756 | 12.3017 | 12.4255 | 12.1993 | 12.0124 | NaN | NaN | NaN | 12.4596 | 125.7246 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 548.1605 | NaN | 16.2838 | NaN | 17.1369
2178.1292 | 12.6097 | 12.2779 | 12.4693 | 12.7613 | 12.2401 | 12.4252 | 12.1916 | 12.011 | NaN | NaN | NaN | 12.4817 | 127.015 | NaN | NaN | NaN | -2.1323 | NaN | NaN | NaN | NaN | 545.4384 | NaN | 26.043 | NaN | 14.7359
2179.1292 | 12.6654 | 12.2773 | 12.4622 | 12.7442 | 12.2452 | 12.4285 | 12.1927 | 12.0199 | NaN | NaN | NaN | 12.462 | 119.4161 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 547.2728 | NaN | 17.794 | NaN | 15.1586
2180.1292 | 12.6129 | 12.3387 | 12.4587 | 12.7357 | 12.2634 | 12.445 | 12.2061 | 12.0118 | NaN | NaN | NaN | 12.4144 | 122.0263 | NaN | NaN | NaN | -10.7191 | NaN | NaN | NaN | NaN | 547.3563 | NaN | 38.2973 | NaN | 16.5336
2181.1292 | 12.6191 | 12.2756 | 12.4586 | 12.7578 | 12.2337 | 12.4368 | 12.2065 | 12.0218 | NaN | NaN | NaN | 12.4689 | 123.9559 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 543.9271 | NaN | 27.3855 | NaN | 18.2563
2182.1292 | 12.6136 | 12.285 | 12.4582 | 12.7533 | 12.2175 | 12.4247 | 12.1941 | 12.0173 | NaN | NaN | NaN | 12.4361 | 117.8067 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 542.9853 | NaN | 23.0804 | NaN | 17.744
2183.1292 | 12.5927 | 12.2743 | 12.457 | 12.6956 | 12.2204 | 12.4311 | 12.1973 | 12.0166 | NaN | NaN | NaN | 12.4826 | 128.765 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 544.1487 | NaN | 17.3437 | NaN | 16.6985
2184.1292 | 12.5937 | 12.3061 | 12.4626 | 12.7365 | 12.256 | 12.4412 | 12.205 | 12.0203 | NaN | NaN | NaN | 12.46 | 124.4485 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 545.3909 | NaN | 15.6701 | NaN | 14.5108
2185.1292 | 12.601 | 12.2957 | 12.4594 | 12.8053 | 12.2698 | 12.4366 | 12.2079 | 12.0175 | NaN | NaN | NaN | 12.4506 | 125.8588 | NaN | NaN | NaN | -17.1137 | NaN | NaN | NaN | NaN | 543.6395 | NaN | 32.1074 | NaN | 18.0553
2186.1292 | 12.6032 | 12.3337 | 12.4545 | 12.7052 | 12.1825 | 12.4586 | 12.2035 | 12.0231 | NaN | NaN | NaN | 12.4648 | 124.4508 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 545.324 | NaN | 25.941 | NaN | 18.565
2187.1292 | 12.6089 | 12.2963 | 12.4635 | 12.7503 | 12.2835 | 12.4386 | 12.2011 | 12.0167 | NaN | NaN | NaN | 12.4867 | 131.0473 | NaN | NaN | NaN | -6.5443 | NaN | NaN | NaN | NaN | 542.1487 | NaN | 24.1526 | NaN | 18.4906
2188.1292 | 12.5704 | 12.2952 | 12.4596 | 12.7547 | 12.26 | 12.4304 | 12.1926 | 12.0144 | NaN | NaN | NaN | 12.4489 | 120.16 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 544.6495 | NaN | 13.6467 | NaN | 15.4369
2189.1292 | 12.5934 | 12.3504 | 12.4568 | 12.765 | 12.2371 | 12.4529 | 12.2049 | 12.0224 | NaN | NaN | NaN | 12.4504 | 108.0443 | NaN | NaN | NaN | 9.7461 | NaN | NaN | NaN | NaN | 547.0229 | NaN | 12.6905 | NaN | 18.63
2190.1292 | 12.5982 | 12.2688 | 12.4539 | 12.7738 | 12.2464 | 12.4082 | 12.1784 | 12.0195 | NaN | NaN | NaN | 12.5113 | 110.4843 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 547.7912 | NaN | 21.1655 | NaN | 19.0957
2191.1292 | 12.6387 | 12.263 | 12.4598 | 12.7273 | 12.1903 | 12.4254 | 12.1834 | 12.0183 | NaN | NaN | NaN | 12.4804 | 135.7872 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 547.7922 | NaN | 27.8939 | NaN | 18.1216
2192.1292 | 12.5699 | 12.3138 | 12.4595 | 12.7453 | 12.1888 | 12.4363 | 12.1933 | 12.0198 | NaN | NaN | NaN | 12.4858 | 131.4908 | NaN | NaN | NaN | 2.388 | NaN | NaN | NaN | NaN | 544.1137 | NaN | 20.989 | NaN | 18.0246
2193.1292 | 12.5898 | 12.3015 | 12.4623 | 12.7626 | 12.3151 | 12.4318 | 12.1927 | 12.0233 | NaN | NaN | NaN | 12.5024 | 115.1732 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 548.0436 | NaN | 24.3376 | NaN | 18.1349
2194.1292 | 12.596 | 12.2824 | 12.4597 | 12.7753 | 12.2002 | 12.4321 | 12.1949 | 12.0222 | NaN | NaN | NaN | 12.4908 | 129.0254 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 544.9659 | NaN | 12.4288 | NaN | 16.955
2195.1292 | 12.6462 | 12.2682 | 12.4612 | 12.7758 | 12.2589 | 12.4143 | 12.1907 | 12.0275 | NaN | NaN | NaN | 12.4717 | 121.6554 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 546.8526 | NaN | 12.0198 | NaN | 17.4498
2196.1292 | 12.625 | 12.2746 | 12.4562 | 12.8708 | 12.2647 | 12.4138 | 12.1878 | 12.0222 | NaN | NaN | NaN | 12.492 | 123.41 | NaN | NaN | NaN | -2.9255 | NaN | NaN | NaN | NaN | 546.9719 | NaN | 23.4104 | NaN | 11.6419
2197.1292 | 12.6109 | 12.3111 | 12.454 | 12.7472 | 12.2608 | 12.4374 | 12.2066 | 12.0234 | NaN | NaN | NaN | 12.4927 | 123.1277 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 547.1946 | NaN | 20.4449 | NaN | 17.394
2198.1292 | 12.5857 | 12.2718 | 12.4558 | 12.7626 | 12.1905 | 12.4179 | 12.1874 | 12.0201 | NaN | NaN | NaN | 12.4866 | 127.8511 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 549.7178 | NaN | 27.2841 | NaN | 12.4785
2199.1292 | 12.5951 | 12.3352 | 12.4526 | 12.7918 | 12.3057 | 12.4482 | 12.2033 | 12.0215 | NaN | NaN | NaN | 12.4789 | 131.8096 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.3107 | 548.7807 | NaN | 28.3418 | NaN | 15.8815
2200.1292 | 12.5902 | 12.2637 | 12.4505 | 12.7466 | 12.2471 | 12.4079 | 12.1871 | 12.0213 | NaN | NaN | NaN | 12.5009 | 136.5217 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 29.35 | 547.8732 | NaN | 28.5437 | NaN | 17.2264
2201.1292 | 12.6329 | 12.3505 | 12.4574 | 12.7313 | 12.2418 | 12.4458 | 12.199 | 12.0203 | NaN | NaN | NaN | 12.5011 | 126.8165 | NaN | NaN | NaN | -14.2247 | NaN | NaN | NaN | 23.3494 | 545.3214 | NaN | 24.4966 | NaN | 19.3427
2202.1292 | 12.5938 | 12.2602 | 12.457 | 12.7499 | 12.1659 | 12.4144 | 12.1936 | 12.0156 | NaN | NaN | NaN | 12.489 | 117.5075 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 17.7044 | 546.367 | NaN | 19.269 | NaN | 18.4627
2203.1292 | 12.6135 | 12.3462 | 12.4597 | 12.7508 | 12.273 | 12.4501 | 12.2021 | 12.0172 | NaN | NaN | NaN | 12.5042 | 119.1151 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 28.2263 | 546.0943 | NaN | 13.4515 | NaN | 16.7045
2204.1292 | 12.5743 | 12.2729 | 12.4561 | 12.755 | 12.244 | 12.3987 | 12.1868 | 12.0188 | NaN | NaN | NaN | 12.4676 | 119.2239 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.4818 | 545.9508 | NaN | 18.3935 | NaN | 14.0671
2205.1292 | 12.5822 | 12.2856 | 12.4607 | 12.6923 | 12.2629 | 12.4061 | 12.1901 | 12.0124 | NaN | NaN | NaN | 12.5149 | 133.5867 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -18.9349 | 547.0274 | NaN | 29.5649 | NaN | 17.7631
2206.1292 | 12.5942 | 12.2835 | 12.4581 | 12.7568 | 12.174 | 12.4219 | 12.194 | 12.0108 | NaN | NaN | NaN | 12.5025 | 118.971 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 550.2488 | NaN | 14.2681 | NaN | 12.7812
2207.1292 | 12.5952 | 12.262 | 12.4574 | 12.7608 | 12.2802 | 12.4021 | 12.1842 | 12.0134 | NaN | NaN | NaN | 12.4866 | 124.1953 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 547.3202 | NaN | 12.443 | NaN | 15.8028
2208.1292 | 12.5895 | 12.2515 | 12.4567 | 12.7198 | 12.2351 | 12.4088 | 12.1809 | 12.0156 | NaN | NaN | NaN | 12.5085 | 135.4332 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 545.0729 | NaN | 22.1552 | NaN | 15.9065
2209.1292 | 12.5685 | 12.2938 | 12.467 | 12.7086 | 12.1745 | 12.4375 | 12.1886 | 12.0156 | NaN | NaN | NaN | 12.4656 | 120.4095 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 544.857 | NaN | 10.242 | NaN | 14.7882
2210.1292 | 12.5691 | 12.2765 | 12.4635 | 12.7174 | 12.2665 | 12.4221 | 12.1899 | 12.0064 | NaN | NaN | NaN | 12.4758 | 137.3021 | NaN | NaN | NaN | -4.9294 | NaN | NaN | NaN | NaN | 539.0589 | NaN | 23.5438 | NaN | 14.7176
2211.1292 | 12.5559 | 12.238 | 12.4598 | 12.7316 | 12.2504 | 12.4089 | 12.1845 | 12.0123 | NaN | NaN | NaN | 12.4818 | 127.8844 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 543.5161 | NaN | 9.5013 | NaN | 16.1808
2212.1292 | 12.5747 | 12.278 | 12.4615 | 12.7065 | 12.2506 | 12.4251 | 12.189 | 12.0077 | NaN | NaN | NaN | 12.4775 | 125.0256 | NaN | NaN | NaN | -4.7973 | NaN | NaN | NaN | NaN | 543.0194 | NaN | 13.7484 | NaN | 16.4767
2213.1292 | 12.5721 | 12.3659 | 12.4625 | 12.6758 | 12.1791 | 12.5036 | 12.2134 | 12.0135 | NaN | NaN | NaN | 12.48 | 126.001 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 540.234 | NaN | 28.7357 | NaN | 6.0113
2214.1292 | 12.5774 | 12.254 | 12.4573 | 12.6975 | 12.2252 | 12.4034 | 12.1813 | 12.0097 | NaN | NaN | NaN | 12.5303 | 122.0574 | NaN | NaN | NaN | 4.2204 | NaN | NaN | NaN | NaN | 541.7355 | NaN | 27.2413 | NaN | 17.2909
2215.1292 | 12.5695 | 12.2428 | 12.4596 | 12.7693 | 12.2449 | 12.4079 | 12.1841 | 12.013 | NaN | NaN | NaN | 12.5 | 120.5134 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 541.2941 | NaN | 20.5145 | NaN | 14.7315
2216.1292 | 12.5829 | 12.2717 | 12.4547 | 12.7291 | 12.1871 | 12.4099 | 12.1894 | 12.01 | NaN | NaN | NaN | 12.497 | 115.1779 | NaN | NaN | NaN | 23.2011 | NaN | NaN | NaN | NaN | 539.3121 | NaN | 15.8248 | NaN | 17.9401
2217.1292 | 12.5831 | 12.2452 | 12.4552 | 12.7061 | 12.2539 | 12.4106 | 12.1923 | 12.0128 | NaN | NaN | NaN | 12.4743 | 118.2068 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 544.1913 | NaN | 19.7844 | NaN | 18.6274
2218.1292 | 12.5789 | 12.2508 | 12.4562 | 12.7045 | 12.2575 | 12.4152 | 12.1899 | 12.0053 | NaN | NaN | NaN | 12.4925 | 129.5864 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 542.4511 | NaN | 31.0707 | NaN | 13.2626
2219.1292 | 12.5842 | 12.2315 | 12.4541 | 12.6996 | 12.2518 | 12.4022 | 12.1776 | 12.0058 | NaN | NaN | NaN | 12.4849 | 123.0997 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 540.3602 | NaN | 37.3116 | NaN | 11.1854
2220.1292 | 12.5992 | 12.2324 | 12.4576 | 12.7074 | 12.2401 | 12.4026 | 12.1842 | 12.0072 | NaN | NaN | NaN | 12.4935 | 116.9696 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 542.1503 | NaN | 22.155 | NaN | 21.0563
2221.1292 | 12.5511 | 12.3103 | 12.4582 | 12.7297 | 12.2569 | 12.4216 | 12.192 | 12.0111 | NaN | NaN | NaN | 12.49 | 133.6337 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 540.3829 | NaN | 26.1963 | NaN | 18.5984
2222.1292 | 12.6552 | 12.2228 | 12.46 | 12.714 | 12.2639 | 12.398 | 12.1794 | 12.0131 | NaN | NaN | NaN | 12.4922 | 126.1194 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 540.2229 | NaN | 15.1137 | NaN | 17.5107
2223.1292 | 12.5939 | 12.2364 | 12.4607 | 12.7148 | 12.2525 | 12.4038 | 12.184 | 12.0105 | NaN | NaN | NaN | 12.4934 | 123.3045 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 542.4435 | NaN | 14.1341 | NaN | 17.5005
2224.1292 | 12.5824 | 12.2476 | 12.4578 | 12.7109 | 12.2417 | 12.4109 | 12.1937 | 12.0067 | NaN | NaN | NaN | 12.4939 | 126.12 | NaN | NaN | NaN | -7.3735 | NaN | NaN | NaN | NaN | 543.335 | NaN | 8.2825 | NaN | 12.8145
2225.1292 | 12.5841 | 12.3798 | 12.4585 | 12.7054 | 12.2307 | 12.4932 | 12.2333 | 12.005 | NaN | NaN | NaN | 12.4669 | 123.4866 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 542.3542 | NaN | 12.8495 | NaN | 16.5392
2226.1292 | 12.6205 | 12.2413 | 12.4569 | 12.7039 | 12.2208 | 12.4258 | 12.1871 | 12.0051 | NaN | NaN | NaN | 12.4718 | 116.4889 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 544.2375 | NaN | 20.271 | NaN | 17.1593
2227.1292 | 12.5715 | 12.2651 | 12.4607 | 12.6673 | 12.2348 | 12.4286 | 12.178 | 12.0096 | NaN | NaN | NaN | 12.4715 | 131.9696 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 542.5013 | NaN | 13.8621 | NaN | 17.5197
2228.1292 | 12.5779 | 12.2776 | 12.4585 | 12.6846 | 12.193 | 12.4357 | 12.1841 | 12.0107 | NaN | NaN | NaN | 12.4891 | 126.5863 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 543.4526 | NaN | 19.1239 | NaN | 16.616
2229.1292 | 12.59 | 12.2363 | 12.4601 | 12.7766 | 12.1652 | 12.4218 | 12.1783 | 12.0073 | NaN | NaN | NaN | 12.4716 | 130.162 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 538.2024 | NaN | 22.4433 | NaN | 16.8571
2230.1292 | 12.5524 | 12.3168 | 12.4609 | 12.7357 | 12.1496 | 12.4567 | 12.1904 | 12.0117 | NaN | NaN | NaN | 12.4989 | 121.6108 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 541.2174 | NaN | 17 | NaN | 17.178
2231.1292 | 12.5712 | 12.2693 | 12.4611 | 12.7292 | 12.2848 | 12.4263 | 12.176 | 12.0052 | NaN | NaN | NaN | 12.4938 | 119.3583 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 543.4535 | NaN | 18.8144 | NaN | 15.9935
2232.1292 | 12.5789 | 12.3058 | 12.4573 | 12.7677 | 12.2849 | 12.4393 | 12.1804 | 12.0134 | NaN | NaN | NaN | 12.4834 | 130.4809 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 553.4358 | NaN | 17.533 | NaN | 14.0228
2233.1292 | 12.5849 | 12.2978 | 12.4612 | 12.706 | 12.2413 | 12.4597 | 12.18 | 12.0099 | NaN | NaN | NaN | 12.4758 | 118.1612 | NaN | NaN | NaN | 0.9543 | NaN | NaN | NaN | NaN | 539.7762 | NaN | 24.9626 | NaN | 17.6736
2234.1292 | 12.5772 | 12.2887 | 12.4659 | 12.6671 | 12.242 | 12.4503 | 12.1775 | 12.0112 | NaN | NaN | NaN | 12.5011 | 129.5139 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 537.5478 | NaN | 22.5857 | NaN | 17.3212
2235.1292 | 12.5899 | 12.2706 | 12.4674 | 12.7348 | 12.2661 | 12.4492 | 12.1866 | 12.0115 | NaN | NaN | NaN | 12.4725 | 129.3884 | NaN | NaN | NaN | -5.8332 | NaN | NaN | NaN | NaN | 537.4549 | NaN | 19.0497 | NaN | 16.8357
2236.1292 | 12.6145 | 12.289 | 12.4648 | 12.7024 | 12.2451 | 12.459 | 12.189 | 12.0142 | NaN | NaN | NaN | 12.4851 | 117.5158 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 537.0441 | NaN | 22.258 | NaN | 18.3515
2237.1292 | 12.6428 | 12.2646 | 12.4607 | 12.6747 | 12.1661 | 12.4269 | 12.1675 | 12.0189 | NaN | NaN | NaN | 12.4624 | 124.433 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 536.6803 | NaN | 25.0942 | NaN | 16.5549
2238.1292 | 12.5791 | 12.2863 | 12.4717 | 12.7195 | 12.1861 | 12.4338 | 12.1744 | 12.0208 | NaN | NaN | NaN | 12.4712 | 114.7623 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 535.6984 | NaN | 24.1762 | NaN | 14.9696
2239.1292 | 12.5892 | 12.2766 | 12.4662 | 12.7451 | 12.1922 | 12.4356 | 12.1774 | 12.0173 | NaN | NaN | NaN | 12.4902 | 123.0335 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 536.1247 | NaN | 24.6562 | NaN | 16.426
2240.1292 | 12.572 | 12.2658 | 12.4633 | 12.7217 | 12.2288 | 12.4288 | 12.1642 | 12.0246 | NaN | NaN | NaN | 12.4918 | 123.5093 | NaN | NaN | NaN | 5.0992 | NaN | NaN | NaN | NaN | 536.6449 | NaN | 9.8429 | NaN | 15.3275
2241.1292 | 12.5894 | 12.2904 | 12.4717 | 12.7222 | 12.246 | 12.4432 | 12.1771 | 12.0208 | NaN | NaN | NaN | 12.4884 | 116.6621 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 538.2892 | NaN | 22.2424 | NaN | 17.2787
2242.1292 | 12.5867 | 12.2721 | 12.4644 | 12.7264 | 12.2684 | 12.4297 | 12.1686 | 12.0216 | NaN | NaN | NaN | 12.5108 | 121.9345 | NaN | NaN | NaN | -14.9807 | NaN | NaN | NaN | NaN | 535.7425 | NaN | 20.2949 | NaN | 15.9133
2243.1292 | 12.6919 | 12.2703 | 12.4652 | 12.723 | 12.2906 | 12.4254 | 12.1658 | 12.0245 | NaN | NaN | NaN | 12.49 | 126.7096 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 532.785 | NaN | 21.4734 | NaN | 15.656
2244.1292 | 12.6098 | 12.2711 | 12.4575 | 12.6994 | 12.2344 | 12.4234 | 12.1645 | 12.0209 | NaN | NaN | NaN | 12.4895 | 126.219 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 535.3088 | NaN | 24.3101 | NaN | 15.9125
2245.1292 | 12.6093 | 12.2628 | 12.4611 | 12.7225 | 12.2423 | 12.4297 | 12.1616 | 12.0226 | NaN | NaN | NaN | 12.4955 | 125.4388 | NaN | NaN | NaN | 1.5088 | NaN | NaN | NaN | NaN | 533.1774 | NaN | 22.9627 | NaN | 15.0286
2246.1292 | 12.5844 | 12.272 | 12.4641 | 12.7332 | 12.2842 | 12.4339 | 12.1661 | 12.0239 | NaN | NaN | NaN | 12.4913 | 132.278 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 528.225 | NaN | 10.2606 | NaN | 17.0202
2247.1292 | 12.5672 | 12.3512 | 12.4614 | 12.8681 | 12.2482 | 12.483 | 12.1935 | 12.0182 | NaN | NaN | NaN | 12.4915 | 124.8121 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 533.1907 | NaN | 7.952 | NaN | 17.1412
2248.1292 | 12.5817 | 12.3098 | 12.462 | 12.7175 | 12.2266 | 12.4452 | 12.172 | 12.0138 | NaN | NaN | NaN | 12.4993 | 132.0302 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 534.5691 | NaN | 27.4386 | NaN | 16.5993
2249.1292 | 12.5882 | 12.2856 | 12.46 | 12.7136 | 12.1904 | 12.4355 | 12.1723 | 12.0184 | NaN | NaN | NaN | 12.4913 | 120.8906 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 537.3335 | NaN | 21.5598 | NaN | 15.0951
2250.1292 | 12.6901 | 12.3414 | 12.4643 | 12.7155 | 12.2472 | 12.4741 | 12.1968 | 12.0167 | NaN | NaN | NaN | 12.4812 | 125.9676 | NaN | NaN | NaN | -13.873 | NaN | NaN | NaN | NaN | 534.9847 | NaN | 17.7767 | NaN | 16.6796
2251.1292 | 12.5799 | 12.2818 | 12.4684 | 12.7194 | 12.175 | 12.437 | 12.1816 | 12.017 | NaN | NaN | NaN | 12.478 | 127.1193 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 535.7014 | NaN | 26.8153 | NaN | 15.7214
2252.1292 | 12.5884 | 12.2734 | 12.4685 | 12.7369 | 12.1968 | 12.424 | 12.1646 | 12.0124 | NaN | NaN | NaN | 12.4946 | 124.0429 | NaN | NaN | NaN | -5.9746 | NaN | NaN | NaN | NaN | 534.433 | NaN | 18.5427 | NaN | 16.0009
2253.1292 | 12.5982 | 12.2862 | 12.4614 | 12.7378 | 12.2347 | 12.4357 | 12.1751 | 12.0212 | NaN | NaN | NaN | 12.5117 | 126.9062 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 533.7795 | NaN | 19.6349 | NaN | 13.0036
2254.1292 | 12.5983 | 12.2654 | 12.4603 | 12.7483 | 12.2547 | 12.4182 | 12.1626 | 12.0185 | NaN | NaN | NaN | 12.4978 | 128.6638 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 536.0411 | NaN | 18.7061 | NaN | 16.8048
2255.1292 | 12.5985 | 12.2611 | 12.4579 | 12.7372 | 12.2659 | 12.4217 | 12.1664 | 12.0125 | NaN | NaN | NaN | 12.5161 | 119.9158 | NaN | NaN | NaN | -6.2211 | NaN | NaN | NaN | NaN | 537.8883 | NaN | 14.9797 | NaN | 16.6496
2256.1292 | 12.5947 | 12.2952 | 12.4584 | 12.7267 | 12.2819 | 12.4391 | 12.1847 | 12.0173 | NaN | NaN | NaN | 12.4672 | 124.9439 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 537.315 | NaN | 25.2575 | NaN | 16.593
2257.1292 | 12.5912 | 12.2559 | 12.4496 | 12.692 | 12.1898 | 12.4277 | 12.18 | 12.014 | NaN | NaN | NaN | 12.511 | 118.4293 | NaN | NaN | NaN | -17.0809 | NaN | NaN | NaN | NaN | 536.6627 | NaN | 21.3236 | NaN | 17.231
2258.1292 | 12.5952 | 12.2783 | 12.4481 | 12.702 | 12.238 | 12.4272 | 12.1783 | 12.018 | NaN | NaN | NaN | 12.4835 | 125.3065 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 536.1541 | NaN | 20.6663 | NaN | 15.6436
2259.1292 | 12.5911 | 12.2573 | 12.4446 | 12.7225 | 12.2607 | 12.4222 | 12.1724 | 12.018 | NaN | NaN | NaN | 12.4866 | 114.3141 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 536.8935 | NaN | 12.0779 | NaN | 17.0433
2260.1292 | 12.5835 | 12.2584 | 12.4531 | 12.7062 | 12.1974 | 12.4336 | 12.1749 | 12.0172 | NaN | NaN | NaN | 12.4849 | 125.5733 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 534.3458 | NaN | 18.7687 | NaN | 14.5914
2261.1292 | 12.6443 | 12.2449 | 12.4481 | 12.752 | 12.2196 | 12.4379 | 12.1797 | 12.0158 | NaN | NaN | NaN | 12.4696 | 125.2475 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 531.8637 | NaN | 11.6434 | NaN | 15.3347
2262.1292 | 12.5567 | 12.2541 | 12.4495 | 12.7742 | 12.1694 | 12.43 | 12.1742 | 12.0148 | NaN | NaN | NaN | 12.4846 | 118.3516 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 531.6637 | NaN | 20.827 | NaN | 15.423
2263.1292 | 12.6236 | 12.2315 | 12.4496 | 12.7234 | 12.1934 | 12.4241 | 12.1747 | 12.0163 | NaN | NaN | NaN | 12.5286 | 116.9627 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 531.726 | NaN | 22.9705 | NaN | 15.6062
2264.1292 | 12.6867 | 12.3128 | 12.4478 | 12.7229 | 12.199 | 12.462 | 12.1813 | 12.0174 | NaN | NaN | NaN | 12.4619 | 132.0704 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 530.631 | NaN | 9.7617 | NaN | 15.8529
2265.1292 | 12.5886 | 12.2926 | 12.453 | 12.7836 | 12.2442 | 12.4533 | 12.1834 | 12.0252 | NaN | NaN | NaN | 12.4702 | 123.1182 | NaN | NaN | NaN | 2.9975 | NaN | NaN | NaN | NaN | 532.6076 | NaN | 33.4497 | NaN | 17.719
2266.1292 | 12.5903 | 12.298 | 12.4499 | 12.7741 | 12.2751 | 12.4648 | 12.2042 | 12.0246 | NaN | NaN | NaN | 12.5273 | 112.78 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 534.6554 | NaN | 12.9003 | NaN | 16.4612
2267.1292 | 12.5852 | 12.2339 | 12.4422 | 12.6829 | 12.2468 | 12.4158 | 12.1676 | 12.0163 | NaN | NaN | NaN | 12.4689 | 124.0356 | NaN | NaN | NaN | -19.7376 | NaN | NaN | NaN | NaN | 533.3648 | NaN | 20.3444 | NaN | 17.2507
2268.1292 | 12.5993 | 12.2481 | 12.4453 | 12.7428 | 12.2729 | 12.4256 | 12.1698 | 12.014 | NaN | NaN | NaN | 12.479 | 129.0793 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 531.9646 | NaN | 27.0925 | NaN | 13.2332
2269.1292 | 12.6087 | 12.2328 | 12.4478 | 12.7734 | 12.2775 | 12.4123 | 12.1713 | 12.0207 | NaN | NaN | NaN | 12.4772 | 127.8629 | NaN | NaN | NaN | -4.9848 | NaN | NaN | NaN | NaN | 528.8861 | NaN | 16.842 | NaN | 14.7802
2270.1292 | 12.5811 | 12.2511 | 12.4448 | 12.7294 | 12.2332 | 12.4215 | 12.1757 | 12.0115 | NaN | NaN | NaN | 12.4761 | 126.5413 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 529.9586 | NaN | 28.4882 | NaN | 16.9924
2271.1292 | 12.5775 | 12.2243 | 12.4486 | 12.7473 | 12.2258 | 12.4009 | 12.1738 | 12.0075 | NaN | NaN | NaN | 12.4746 | 113.3051 | NaN | NaN | NaN | -8.4017 | NaN | NaN | NaN | NaN | 531.3415 | NaN | 17.8797 | NaN | 16.5766
2272.1292 | 12.6492 | 12.2244 | 12.4487 | 12.7471 | 12.1793 | 12.4084 | 12.1762 | 12.0078 | NaN | NaN | NaN | 12.4399 | 125.432 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 531.935 | NaN | 21.0367 | NaN | 16.3764
2273.1292 | 12.5864 | 12.2249 | 12.4503 | 12.749 | 12.2285 | 12.4065 | 12.1705 | 12.0016 | NaN | NaN | NaN | 12.4838 | 116.4631 | NaN | NaN | NaN | -2.2399 | NaN | NaN | NaN | NaN | 530.3991 | NaN | 10.6236 | NaN | 15.5339
2274.1292 | 12.5841 | 12.2426 | 12.4465 | 12.735 | 12.1727 | 12.4187 | 12.181 | 12.0054 | NaN | NaN | NaN | 12.4719 | 123.3198 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 532.8772 | NaN | 15.911 | NaN | 13.3653
2275.1292 | 12.5862 | 12.2335 | 12.4473 | 12.7297 | 12.182 | 12.4123 | 12.1806 | 12.0069 | NaN | NaN | NaN | 12.4967 | 125.0585 | NaN | NaN | NaN | -7.1891 | NaN | NaN | NaN | NaN | 531.7445 | NaN | 12.8275 | NaN | 16.2537
2276.1292 | 12.5819 | 12.3674 | 12.4411 | 12.7207 | 12.2302 | 12.4669 | 12.214 | 12.0107 | NaN | NaN | NaN | 12.4557 | 111.9282 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 530.6536 | NaN | 29.9205 | NaN | 16.9897
2277.1292 | 12.5598 | 12.2358 | 12.4526 | 12.7365 | 12.2804 | 12.416 | 12.1823 | 12.0051 | NaN | NaN | NaN | 12.462 | 120.1391 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 535.585 | NaN | 19.9877 | NaN | 15.6825
2278.1292 | 12.5689 | 12.257 | 12.4517 | 12.7365 | 12.2196 | 12.4236 | 12.1797 | 12.0046 | NaN | NaN | NaN | 12.4427 | 127.0422 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 534.1007 | NaN | 17.9608 | NaN | 17.5697
2279.1292 | 12.5644 | 12.2625 | 12.4476 | 12.7623 | 12.2728 | 12.43 | 12.19 | 12.0063 | NaN | NaN | NaN | 12.4302 | 122.4487 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 533.9421 | NaN | 28.3831 | NaN | 15.0359
2280.1292 | 12.5643 | 12.2951 | 12.4476 | 12.7448 | 12.2028 | 12.451 | 12.188 | 12.0093 | NaN | NaN | NaN | 12.4679 | 121.5127 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 532.873 | NaN | 32.3905 | NaN | 15.6592
2281.1292 | 12.5709 | 12.2621 | 12.4403 | 12.7383 | 12.2247 | 12.4254 | 12.187 | 12.0073 | NaN | NaN | NaN | 12.469 | 123.4727 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 532.3698 | NaN | 10.3479 | NaN | 14.7801
2282.1292 | 12.5698 | 12.2927 | 12.4506 | 12.7433 | 12.2758 | 12.4352 | 12.1906 | 12.0062 | NaN | NaN | NaN | 12.46 | 123.1253 | NaN | NaN | NaN | 4.237 | NaN | NaN | NaN | NaN | 530.5488 | NaN | 11.4659 | NaN | 16.661
2283.1292 | 12.5641 | 12.2245 | 12.4511 | 12.7801 | 12.146 | 12.4152 | 12.1792 | 12.0017 | NaN | NaN | NaN | 12.4967 | 121.8287 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 530.74 | NaN | 30.765 | NaN | 16.8758
2284.1292 | 12.5626 | 12.2273 | 12.4463 | 12.7388 | 12.2562 | 12.408 | 12.1746 | 12.0076 | NaN | NaN | NaN | 12.4764 | 126.8703 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 533.1374 | NaN | 23.1247 | NaN | 15.9424
2285.1292 | 12.6574 | 12.2157 | 12.4502 | 12.7586 | 12.2653 | 12.4097 | 12.1758 | 12.0033 | NaN | NaN | NaN | 12.461 | 124.276 | NaN | NaN | -19.9429 | NaN | NaN | NaN | NaN | NaN | 532.154 | NaN | 7.6696 | NaN | 16.9312
2286.1292 | 12.6013 | 12.2672 | 12.4462 | 12.7212 | 12.2353 | 12.452 | 12.194 | 12.0057 | NaN | NaN | NaN | 12.4667 | 123.2303 | NaN | NaN | NaN | -1.6963 | NaN | NaN | NaN | NaN | 532.8654 | NaN | 17.7908 | NaN | 16.7276
2287.1292 | 12.5461 | 12.2172 | 12.4446 | 12.8043 | 12.255 | 12.4093 | 12.1695 | 12.0097 | NaN | NaN | NaN | 12.4289 | 128.1802 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 531.7603 | NaN | 19.9237 | NaN | 16.3504
2288.1292 | 12.5527 | 12.1978 | 12.4459 | 12.7153 | 12.199 | 12.4018 | 12.1761 | 12.0079 | NaN | NaN | NaN | 12.4669 | 127.613 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 533.1735 | NaN | 17.4125 | NaN | 14.395
2289.1292 | 12.5526 | 12.2054 | 12.4425 | 12.7074 | 12.2119 | 12.4073 | 12.1816 | 12.0038 | NaN | NaN | NaN | 12.4216 | 129.8811 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 531.9454 | NaN | 21.5806 | NaN | 15.8329
2290.1292 | 12.5602 | 12.2736 | 12.447 | 12.7781 | 12.1774 | 12.4629 | 12.197 | 12.0033 | NaN | NaN | NaN | 12.4108 | 115.9271 | NaN | NaN | NaN | -8.8723 | NaN | NaN | NaN | NaN | 534.482 | NaN | 9.3161 | NaN | 16.7092
2291.1292 | 12.5297 | 12.2281 | 12.4392 | 12.7517 | 12.2169 | 12.4176 | 12.1768 | 12.0084 | NaN | NaN | NaN | 12.4323 | 129.4142 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 531.0585 | NaN | 29.1477 | NaN | 16.6779
2292.1292 | 12.6071 | 12.2821 | 12.4369 | 12.7573 | 12.1912 | 12.4527 | 12.1869 | 12.0041 | NaN | NaN | NaN | 12.4746 | 132.5207 | NaN | NaN | NaN | -6.9505 | NaN | NaN | NaN | NaN | 530.3832 | NaN | 11.4911 | NaN | 16.5012
2293.1292 | 12.5302 | 12.2364 | 12.433 | 12.7512 | 12.1932 | 12.4199 | 12.1827 | 12.0052 | NaN | NaN | NaN | 12.4487 | 115.1765 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 533.6275 | NaN | 29.0389 | NaN | 15.6877
2294.1292 | 12.5465 | 12.2138 | 12.4226 | 12.7222 | 12.2305 | 12.4176 | 12.1795 | 12.0048 | NaN | NaN | NaN | 12.4314 | 129.6261 | NaN | NaN | NaN | -14.0509 | NaN | NaN | NaN | NaN | 534.1656 | NaN | 22.3198 | NaN | 16.4722
2295.1292 | 12.5561 | 12.2038 | 12.4228 | 12.6981 | 12.2766 | 12.3962 | 12.1709 | 12.0132 | NaN | NaN | NaN | 12.4646 | 129.1892 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 532.1367 | NaN | 27.5048 | NaN | 15.6688
2296.1292 | 12.5607 | 12.2018 | 12.4263 | 12.77 | 12.214 | 12.3982 | 12.1755 | 12.0085 | NaN | NaN | NaN | 12.4437 | 121.4178 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 532.3531 | NaN | 19.0601 | NaN | 16.6529
2297.1292 | 12.5703 | 12.3173 | 12.422 | 12.7479 | 12.24 | 12.4751 | 12.219 | 12.0117 | NaN | NaN | NaN | 12.4452 | 120.8036 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 529.66 | NaN | 22.0109 | NaN | 16.1644
2298.1292 | 12.5702 | 12.2194 | 12.4226 | 12.7459 | 12.2626 | 12.4012 | 12.18 | 12.0082 | NaN | NaN | NaN | 12.4396 | 126.1951 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 531.701 | NaN | 24.8788 | NaN | 16.2588
2299.1292 | 12.5967 | 12.1975 | 12.4205 | 12.7371 | 12.2187 | 12.4073 | 12.1808 | 12.0049 | NaN | NaN | NaN | 12.4416 | 124.5141 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 534.5543 | NaN | 12.7817 | NaN | 16.8253
2300.1292 | 12.5563 | 12.2373 | 12.4224 | 12.7199 | 12.1807 | 12.428 | 12.1798 | 12.0068 | NaN | NaN | NaN | 12.4892 | 126.7678 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 531.8429 | NaN | 28.3855 | NaN | 15.9637
2301.1292 | 12.5756 | 12.2377 | 12.4223 | 12.7114 | 12.262 | 12.41 | 12.173 | 12.0077 | NaN | NaN | NaN | 12.444 | 122.3942 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 531.9926 | NaN | 26.5114 | NaN | 14.1067
2302.1292 | 12.5764 | 12.2388 | 12.422 | 12.7335 | 12.2837 | 12.408 | 12.1789 | 12.0128 | NaN | NaN | NaN | 12.4857 | 121.071 | NaN | NaN | NaN | -15.6979 | NaN | NaN | NaN | NaN | 533.2451 | NaN | 23.7051 | NaN | 17.0615
2303.1292 | 12.5881 | 12.2285 | 12.4215 | 12.749 | 12.2056 | 12.3893 | 12.1707 | 12.0118 | NaN | NaN | NaN | 12.4735 | 119.5122 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 529.4557 | NaN | 13.7891 | NaN | 16.4187
2304.1292 | 12.5935 | 12.3097 | 12.4139 | 12.7272 | 12.2214 | 12.435 | 12.1952 | 12.0148 | NaN | NaN | NaN | 12.4395 | 123.748 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 527.7775 | NaN | 17.0833 | NaN | 16.3508
2305.1292 | 12.5888 | 12.3083 | 12.4271 | 12.7637 | 12.2444 | 12.4339 | 12.1788 | 12.0173 | NaN | NaN | NaN | 12.456 | 119.8748 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 529.0801 | NaN | 14.8808 | NaN | 16.8421
2306.1292 | 12.5854 | 12.2659 | 12.4269 | 12.7459 | 12.2657 | 12.4072 | 12.1709 | 12.0154 | NaN | NaN | NaN | 12.4558 | 138.5818 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 525.1091 | NaN | 16.188 | NaN | 16.0396
2307.1292 | 12.5962 | 12.2616 | 12.4212 | 12.7137 | 12.275 | 12.4106 | 12.1748 | 12.0152 | NaN | NaN | NaN | 12.4704 | 136.2774 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 528.6836 | NaN | 24.3958 | NaN | 15.1234
2308.1292 | 12.6047 | 12.3197 | 12.4261 | 12.7508 | 12.1322 | 12.4474 | 12.1847 | 12.0122 | NaN | NaN | NaN | 12.44 | 133.1303 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 525.8856 | NaN | 12.6441 | NaN | 13.5704
2309.1292 | 12.6229 | 12.3649 | 12.4243 | 12.7788 | 12.1278 | 12.4543 | 12.196 | 12.0207 | NaN | NaN | NaN | 12.4485 | 128.4476 | NaN | NaN | NaN | -13.7088 | NaN | NaN | NaN | NaN | 527.0847 | NaN | 22.2446 | NaN | 17.4148
2310.1292 | 12.6165 | 12.3778 | 12.4262 | 12.7163 | 12.2123 | 12.4626 | 12.2029 | 12.0178 | NaN | NaN | NaN | 12.4807 | 122.1349 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 531.1862 | NaN | 14.9731 | NaN | 16.5239
2311.1292 | 12.6106 | 12.2817 | 12.4222 | 12.7755 | 12.2283 | 12.412 | 12.1791 | 12.019 | NaN | NaN | NaN | 12.4559 | 122.3224 | NaN | NaN | NaN | 6.357 | NaN | NaN | NaN | NaN | 533.0991 | NaN | 14.7513 | NaN | 17.2239
2312.1292 | 12.6865 | 12.2818 | 12.4242 | 12.7496 | 12.183 | 12.4124 | 12.1854 | 12.0172 | NaN | NaN | NaN | 12.4536 | 113.5895 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 529.9077 | NaN | 16.2234 | NaN | 17.7342
2313.1292 | 12.6139 | 12.2701 | 12.4239 | 12.7403 | 12.194 | 12.4111 | 12.193 | 12.02 | NaN | NaN | NaN | 12.4228 | 128.2727 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 530.5788 | NaN | 12.8392 | NaN | 14.3886
2314.1292 | 12.6871 | 12.2774 | 12.4181 | 12.7218 | 12.2509 | 12.4082 | 12.1846 | 12.0259 | NaN | NaN | NaN | 12.4506 | 122.1006 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 530.5485 | NaN | 9.7078 | NaN | 19.3801
2315.1292 | 12.6608 | 12.3732 | 12.409 | 12.7404 | 12.2526 | 12.4513 | 12.2108 | 12.0276 | NaN | NaN | NaN | 12.4632 | 128.9933 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 528.5012 | NaN | 22.6826 | NaN | 15.4886
2316.1292 | 12.613 | 12.3004 | 12.4175 | 12.7212 | 12.2876 | 12.4138 | 12.183 | 12.0306 | NaN | NaN | NaN | 12.4576 | 130.0344 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 530.1796 | NaN | 18.2921 | NaN | 17.1203
2317.1292 | 12.6101 | 12.2953 | 12.4091 | 12.7531 | 12.266 | 12.4171 | 12.1894 | 12.0269 | NaN | NaN | NaN | 12.4488 | 114.9296 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 529.3579 | NaN | 21.1878 | NaN | 17.4564
2318.1292 | 12.6201 | 12.36 | 12.4048 | 12.7488 | 12.1402 | 12.4643 | 12.202 | 12.0326 | NaN | NaN | NaN | 12.4795 | 123.8928 | NaN | NaN | NaN | -3.7955 | NaN | NaN | NaN | NaN | 531.2044 | NaN | 10.8326 | NaN | 15.1584
2319.1292 | 12.6429 | 12.2919 | 12.4109 | 12.7322 | 12.2547 | 12.4102 | 12.1876 | 12.0356 | NaN | NaN | NaN | 12.4353 | 126.4342 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 530.4965 | NaN | 26.4942 | NaN | 15.7702
2320.1292 | 12.631 | 12.3871 | 12.4133 | 12.7726 | 12.2599 | 12.4647 | 12.2043 | 12.0383 | NaN | NaN | NaN | 12.4692 | 114.0071 | NaN | NaN | NaN | 6.9406 | NaN | NaN | NaN | NaN | 530.3039 | NaN | 21.0492 | NaN | 18.2
2321.1292 | 12.5923 | 12.2733 | 12.4124 | 12.7585 | 12.2513 | 12.4069 | 12.1833 | 12.0354 | NaN | NaN | NaN | 12.5059 | 131.7784 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 528.4022 | NaN | 13.733 | NaN | 16.8704
2322.1292 | 12.5917 | 12.2989 | 12.413 | 12.7548 | 12.2639 | 12.4161 | 12.1784 | 12.0355 | NaN | NaN | NaN | 12.4683 | 117.3316 | NaN | NaN | NaN | 4.0358 | NaN | NaN | NaN | NaN | 530.8455 | NaN | 17.4167 | NaN | 16.9236
2323.1292 | 12.607 | 12.2765 | 12.4101 | 12.7469 | 12.2734 | 12.3932 | 12.1693 | 12.0408 | NaN | NaN | NaN | 12.454 | 126.7531 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 530.686 | NaN | 20.0488 | NaN | 13.1259
2324.1292 | 12.6089 | 12.3242 | 12.4101 | 12.7481 | 12.2734 | 12.4422 | 12.1928 | 12.0282 | NaN | NaN | NaN | 12.4567 | 116.5107 | NaN | NaN | NaN | -9.9109 | NaN | NaN | NaN | NaN | 530.3679 | NaN | 22.5085 | NaN | 17.1628
2325.1292 | 12.6044 | 12.3672 | 12.4132 | 12.7393 | 12.2097 | 12.4455 | 12.1959 | 12.0306 | NaN | NaN | NaN | 12.4519 | 135.2764 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 532.5609 | NaN | 30.8454 | NaN | 16.6717
2326.1292 | 12.6111 | 12.2708 | 12.4127 | 12.7355 | 12.1976 | 12.4257 | 12.1849 | 12.0244 | NaN | NaN | NaN | 12.4447 | 126.376 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 534.0509 | NaN | 20.8101 | NaN | 15.896
2327.1292 | 12.614 | 12.3169 | 12.4142 | 12.7432 | 12.2811 | 12.4243 | 12.1809 | 12.0248 | NaN | NaN | NaN | 12.4369 | 127.9731 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 534.2596 | NaN | 17.5542 | NaN | 16.2095
2328.1292 | 12.6185 | 12.2608 | 12.4139 | 12.7281 | 12.2761 | 12.4085 | 12.1732 | 12.021 | NaN | NaN | NaN | 12.4653 | 130.9517 | NaN | NaN | NaN | -9.6634 | NaN | NaN | NaN | NaN | 533.7578 | NaN | 19.9971 | NaN | 16.8026
2329.1292 | 12.6205 | 12.2475 | 12.4078 | 12.7556 | 12.2575 | 12.3978 | 12.1637 | 12.0256 | NaN | NaN | NaN | 12.4424 | 132.7734 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 533.277 | NaN | 17.9976 | NaN | 14.8827
2330.1292 | 12.6232 | 12.2917 | 12.4089 | 12.7357 | 12.2586 | 12.4182 | 12.177 | 12.0197 | NaN | NaN | NaN | 12.4191 | 119.4861 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 536.6999 | NaN | 15.2113 | NaN | 17.5089
2331.1292 | 12.6489 | 12.2628 | 12.405 | 12.7225 | 12.2313 | 12.4046 | 12.1733 | 12.0226 | NaN | NaN | NaN | 12.4639 | 134.8257 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 530.7202 | NaN | 24.2397 | NaN | 16.8873
2332.1292 | 12.6583 | 12.3097 | 12.4068 | 12.8187 | 12.1756 | 12.4319 | 12.1906 | 12.0172 | NaN | NaN | NaN | 12.4633 | 136.4023 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 531.7185 | NaN | 10.7302 | NaN | 16.2829
2333.1292 | 12.623 | 12.2794 | 12.4094 | 12.7477 | 12.2691 | 12.4343 | 12.1785 | 12.0215 | NaN | NaN | NaN | 12.4631 | 127.1756 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 532.6157 | NaN | 14.753 | NaN | 17.4184
2334.1292 | 12.6334 | 12.2518 | 12.4136 | 12.7585 | 12.2812 | 12.4217 | 12.1707 | 12.0199 | NaN | NaN | NaN | 12.4305 | 120.5122 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 533.9668 | NaN | 15.4551 | NaN | 16.4848
2335.1292 | 12.635 | 12.289 | 12.4083 | 12.7389 | 12.1599 | 12.453 | 12.185 | 12.0139 | NaN | NaN | NaN | 12.4615 | 124.7829 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 535.167 | NaN | 22.151 | NaN | 16.8145
2336.1292 | 12.639 | 12.3834 | 12.4115 | 12.8116 | 12.2818 | 12.4942 | 12.2269 | 12.0179 | NaN | NaN | NaN | 12.47 | 129.2109 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 533.0978 | NaN | 28.7012 | NaN | 15.3835
2337.1292 | 12.6266 | 12.2348 | 12.413 | 12.7668 | 12.2393 | 12.4197 | 12.1723 | 12.0169 | NaN | NaN | NaN | 12.4333 | 117.9105 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 533.6414 | NaN | 25.2184 | NaN | 18.7811
2338.1292 | 12.6278 | 12.2365 | 12.418 | 12.7809 | 12.2845 | 12.4028 | 12.1694 | 12.012 | NaN | NaN | NaN | 12.4524 | 122.4942 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 533.0759 | NaN | 13.6778 | NaN | 16.1326
2339.1292 | 12.628 | 12.3657 | 12.4058 | 12.7229 | 12.2489 | 12.456 | 12.1992 | 12.0014 | NaN | NaN | NaN | 12.4397 | 111.1041 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 531.4033 | NaN | 33.9211 | NaN | 16.6548
2340.1292 | 12.6204 | 12.2541 | 12.4118 | 12.7527 | 12.263 | 12.4202 | 12.1747 | 12.0201 | NaN | NaN | NaN | 12.4371 | 131.4785 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 533.9824 | NaN | 19.067 | NaN | 15.9241
2341.1292 | 12.6733 | 12.2419 | 12.4036 | 12.7383 | 12.1574 | 12.4185 | 12.1777 | 12.0131 | NaN | NaN | NaN | 12.4383 | 129.7966 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 530.875 | NaN | 9.9017 | NaN | 16.7055
2342.1292 | 12.6139 | 12.2664 | 12.4057 | 12.7233 | 12.2006 | 12.4249 | 12.1779 | 12.0154 | NaN | NaN | NaN | 12.4418 | 118.596 | NaN | NaN | NaN | -1.0745 | NaN | NaN | NaN | NaN | 532.4103 | NaN | 14.8699 | NaN | 17.1216
2343.1292 | 12.6152 | 12.2548 | 12.4066 | 12.8071 | 12.2584 | 12.4322 | 12.1864 | 12.0079 | NaN | NaN | NaN | 12.4343 | 117.6026 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 532.8285 | NaN | 20.183 | NaN | 15.1278
2344.1292 | 12.6127 | 12.2636 | 12.4117 | 12.7285 | 12.2378 | 12.4485 | 12.2003 | 12.0107 | NaN | NaN | NaN | 12.4413 | 119.041 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 537.2202 | NaN | 14.2275 | NaN | 14.5827
2345.1292 | 12.6189 | 12.3769 | 12.4053 | 12.7689 | 12.266 | 12.4891 | 12.2228 | 12.0066 | NaN | NaN | NaN | 12.4263 | 123.5665 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 537.2144 | NaN | 21.5772 | NaN | 14.6151
2346.1292 | 12.6252 | 12.283 | 12.4039 | 12.7832 | 12.2985 | 12.4398 | 12.1854 | 12.0065 | NaN | NaN | NaN | 12.4333 | 123.5595 | NaN | NaN | NaN | 2.7457 | NaN | NaN | NaN | NaN | 536.668 | NaN | 23.4638 | NaN | 16.2927
2347.1292 | 12.6326 | 12.2933 | 12.3927 | 12.7413 | 12.162 | 12.4747 | 12.1864 | 12.0053 | NaN | NaN | NaN | 12.4507 | 122.1712 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 537.3911 | NaN | 25.2721 | NaN | 23.282
2348.1292 | 12.6084 | 12.27 | 12.3931 | 12.7478 | 12.2614 | 12.4504 | 12.1927 | 12.0135 | NaN | NaN | NaN | 12.4403 | 114.4718 | NaN | NaN | NaN | -11.3859 | NaN | NaN | NaN | NaN | 534.9651 | NaN | 10.2432 | NaN | 14.3551
2349.1292 | 12.6184 | 12.2592 | 12.3864 | 12.7516 | 12.2593 | 12.4406 | 12.1924 | 12.0104 | NaN | NaN | NaN | 12.4375 | 128.7839 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 533.5609 | NaN | 12.7313 | NaN | 15.0552
2350.1292 | 12.6251 | 12.265 | 12.3833 | 12.7498 | 12.2815 | 12.4512 | 12.1884 | 12.0062 | NaN | NaN | NaN | 12.4879 | 130.0543 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 534.135 | NaN | 17.5244 | NaN | 15.3896
2351.1292 | 12.6254 | 12.2779 | 12.3841 | 12.762 | 12.2636 | 12.4681 | 12.199 | 12.0036 | NaN | NaN | NaN | 12.4514 | 122.6084 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 533.1188 | NaN | 28.6225 | NaN | 12.7029
2352.1292 | 12.6221 | 12.2546 | 12.3922 | 12.7529 | 12.2692 | 12.4555 | 12.1954 | 12.0022 | NaN | NaN | NaN | 12.4843 | 127.3137 | NaN | NaN | NaN | 7.7919 | NaN | NaN | NaN | NaN | 529.2829 | NaN | 24.5656 | NaN | 15.3142
2353.1292 | 12.6341 | 12.2468 | 12.3943 | 12.7671 | 12.2757 | 12.4697 | 12.1943 | 12.004 | NaN | NaN | NaN | 12.4554 | 121.1704 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 534.0288 | NaN | 17.7288 | NaN | 16.4071
2354.1292 | 12.6369 | 12.2797 | 12.389 | 12.7363 | 12.2671 | 12.4814 | 12.201 | 12.0013 | NaN | NaN | NaN | 12.4458 | 124.9563 | NaN | NaN | NaN | 1.2325 | NaN | NaN | NaN | NaN | 534.8155 | NaN | 25.4304 | NaN | 16.3016
2355.1292 | 12.6733 | 12.3483 | 12.3915 | 12.776 | 12.2109 | 12.5077 | 12.2102 | 12.005 | NaN | NaN | NaN | 12.4449 | 122.3417 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 532.9753 | NaN | 25.3303 | NaN | 15.9805
2356.1292 | 12.678 | 12.2731 | 12.4028 | 12.7261 | 12.2466 | 12.4776 | 12.1922 | 12.0051 | NaN | NaN | NaN | 12.4575 | 121.2796 | NaN | NaN | NaN | -7.2116 | NaN | NaN | NaN | NaN | 530.0377 | NaN | 10.3221 | NaN | 15.969
2357.1292 | 12.6139 | 12.2551 | 12.4015 | 12.8221 | 12.261 | 12.4734 | 12.1997 | 12.0031 | NaN | NaN | NaN | 12.5514 | 128.2155 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 531.3748 | NaN | 18.1692 | NaN | 16.6563
2358.1292 | 12.6292 | 12.2567 | 12.403 | 12.7441 | 12.2572 | 12.4866 | 12.2083 | 12.0086 | NaN | NaN | NaN | 12.4672 | 126.0013 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 528.5426 | NaN | 20.2503 | NaN | 14.9661
2359.1292 | 12.637 | 12.2423 | 12.3986 | 12.7438 | 12.2884 | 12.4747 | 12.1998 | 12.0118 | NaN | NaN | NaN | 12.4804 | 127.5976 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 529.6274 | NaN | 14.3476 | NaN | 15.1953
2360.1292 | 12.6866 | 12.2406 | 12.3985 | 12.7323 | 12.2375 | 12.4764 | 12.2117 | 12.0051 | NaN | NaN | NaN | 12.4911 | 130.019 | NaN | NaN | NaN | -16.112 | NaN | NaN | NaN | NaN | 531.2419 | NaN | 16.311 | NaN | 16.8428
2361.1292 | 12.642 | 12.2359 | 12.4089 | 12.7321 | 12.265 | 12.4786 | 12.202 | 12.0057 | NaN | NaN | NaN | 12.4819 | 121.0882 | NaN | NaN | NaN | 2.6769 | NaN | NaN | NaN | NaN | 530.4887 | NaN | 12.718 | NaN | 15.6672
2362.1292 | 12.6276 | 12.262 | 12.4018 | 12.7141 | 12.1985 | 12.4947 | 12.209 | 12.0053 | NaN | NaN | NaN | 12.4839 | 121.8371 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 532.9905 | NaN | 10.3277 | NaN | 15.458
2363.1292 | 12.6357 | 12.247 | 12.4078 | 12.7287 | 12.3024 | 12.4775 | 12.2 | 12.0065 | NaN | NaN | NaN | 12.509 | 136.4632 | NaN | NaN | NaN | -17.7735 | NaN | NaN | NaN | NaN | 528.7509 | NaN | 24.9409 | NaN | 15.8566
2364.1292 | 12.6306 | 12.2604 | 12.4145 | 12.7247 | 12.2674 | 12.4948 | 12.1975 | 12.0066 | NaN | NaN | NaN | 12.4601 | 113.6221 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 533.873 | NaN | 15.8816 | NaN | 15.9226
2365.1292 | 12.6349 | 12.3168 | 12.4103 | 12.724 | 12.2651 | 12.5137 | 12.2075 | 12.0028 | NaN | NaN | NaN | 12.4941 | 131.2692 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 529.3086 | NaN | 22.8638 | NaN | 16.8696
2366.1292 | 12.641 | 12.2626 | 12.4126 | 12.7113 | 12.2108 | 12.4996 | 12.2065 | 12.0042 | NaN | NaN | NaN | 12.49 | 130.3451 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 525.976 | NaN | 28.0824 | NaN | 14.1576
2367.1292 | 12.6206 | 12.2775 | 12.412 | 12.7124 | 12.2553 | 12.4973 | 12.1973 | 12.0015 | NaN | NaN | NaN | 12.4667 | 119.5928 | NaN | NaN | NaN | 3.6319 | NaN | NaN | NaN | NaN | 527.0998 | NaN | 25.9318 | NaN | 16.9222
2368.1292 | 12.6193 | 12.2873 | 12.4188 | 12.7084 | 12.2671 | 12.509 | 12.2012 | 12.0058 | NaN | NaN | NaN | 12.4858 | 120.7542 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 528.9502 | NaN | 9.0755 | NaN | 17.0618
2369.1292 | 12.6175 | 12.345 | 12.4163 | 12.721 | 12.3011 | 12.5197 | 12.2049 | 12.0041 | NaN | NaN | NaN | 12.4822 | 119.9232 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 529.4126 | NaN | 23.4236 | NaN | 16.8534
2370.1292 | 12.6191 | 12.3241 | 12.4162 | 12.7008 | 12.1802 | 12.5148 | 12.2027 | 12.0023 | NaN | NaN | NaN | 12.4909 | 122.0239 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 528.66 | NaN | 21.3335 | NaN | 16.1927
2371.1292 | 12.6238 | 12.2696 | 12.4173 | 12.7126 | 12.2978 | 12.4899 | 12.193 | 12.0115 | NaN | NaN | NaN | 12.4667 | 126.2887 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 528.4082 | NaN | 17.5537 | NaN | 12.8794
2372.1292 | 12.6202 | 12.2532 | 12.4147 | 12.6824 | 12.1971 | 12.4835 | 12.1938 | 12.011 | NaN | NaN | NaN | 12.4613 | 119.587 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 528.1166 | NaN | 13.1878 | NaN | 14.2128
2373.1292 | 12.6283 | 12.2759 | 12.4174 | 12.6981 | 12.2862 | 12.4892 | 12.195 | 12.0118 | NaN | NaN | NaN | 12.4816 | 123.6779 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 526.5131 | NaN | 14.857 | NaN | 15.5624
2374.1292 | 12.6414 | 12.3211 | 12.4192 | 12.7574 | 12.1297 | 12.5316 | 12.2023 | 12.0052 | NaN | NaN | NaN | 12.4705 | 125.3887 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 525.7284 | NaN | 9.1859 | NaN | 15.3575
2375.1292 | 12.6031 | 12.2719 | 12.4214 | 12.6905 | 12.286 | 12.4852 | 12.1988 | 12.0099 | NaN | NaN | NaN | 12.4787 | 118.7986 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 527.0484 | NaN | 30.0987 | NaN | 14.6331
2376.1292 | 12.5924 | 12.3933 | 12.4293 | 12.7542 | 12.2297 | 12.5566 | 12.2428 | 12.0111 | NaN | NaN | NaN | 12.4735 | 119.0988 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 529.2694 | NaN | 8.3079 | NaN | 14.8609
2377.1292 | 12.6139 | 12.3428 | 12.4277 | 12.7359 | 12.2915 | 12.508 | 12.1975 | 12.0121 | NaN | NaN | NaN | 12.4919 | 121.2199 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 525.6275 | NaN | 14.8297 | NaN | 14.7447
2378.1292 | 12.6181 | 12.2809 | 12.4279 | 12.7394 | 12.2747 | 12.4902 | 12.1979 | 12.0166 | NaN | NaN | NaN | 12.4844 | 114.4802 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 526.7144 | NaN | 30.6666 | NaN | 16.3223
2379.1292 | 12.615 | 12.3196 | 12.4288 | 12.7153 | 12.2552 | 12.5033 | 12.2041 | 12.0123 | NaN | NaN | NaN | 12.482 | 113.9285 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 527.2224 | NaN | 22.1477 | NaN | 16.3012
2380.1292 | 12.6214 | 12.2819 | 12.4288 | 12.7208 | 12.2251 | 12.4761 | 12.1831 | 12.0139 | NaN | NaN | NaN | 12.5345 | 131.8982 | NaN | NaN | NaN | -19.418 | NaN | NaN | NaN | NaN | 525.8557 | NaN | 19.7084 | NaN | 15.8675
2381.1292 | 12.6221 | 12.2718 | 12.4311 | 12.6893 | 12.284 | 12.4799 | 12.1904 | 12.0127 | NaN | NaN | NaN | 12.4774 | 135.2316 | NaN | NaN | NaN | -6.6986 | NaN | NaN | NaN | NaN | 522.6316 | NaN | 25.1648 | NaN | 15.6754
2382.1292 | 12.628 | 12.2502 | 12.4306 | 12.7739 | 12.288 | 12.4612 | 12.1841 | 12.019 | NaN | NaN | NaN | 12.5003 | 124.3468 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 529.0965 | NaN | 13.6703 | NaN | 15.4751
2383.1292 | 12.607 | 12.3063 | 12.4306 | 12.729 | 12.3011 | 12.4831 | 12.1942 | 12.02 | NaN | NaN | NaN | 12.512 | 120.5388 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 528.3857 | NaN | 16.8591 | NaN | 13.881
2384.1292 | 12.6171 | 12.2439 | 12.4407 | 12.7362 | 12.2112 | 12.471 | 12.1863 | 12.0189 | NaN | NaN | NaN | 12.5068 | 120.717 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 530.7602 | NaN | 12.8044 | NaN | 16.2449
2385.1292 | 12.6163 | 12.2581 | 12.4444 | 12.7805 | 12.213 | 12.465 | 12.1939 | 12.0245 | NaN | NaN | NaN | 12.4704 | 128.1882 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 531.4048 | NaN | 24.3586 | NaN | 13.6221
2386.1292 | 12.6179 | 12.2628 | 12.4355 | 12.7733 | 12.2136 | 12.4628 | 12.1948 | 12.0271 | NaN | NaN | NaN | 12.4906 | 129.341 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 531.6779 | NaN | 22.9243 | NaN | 16.3285
2387.1292 | 12.6197 | 12.3248 | 12.4343 | 12.7065 | 12.2788 | 12.4742 | 12.2038 | 12.0185 | NaN | NaN | NaN | 12.4727 | 124.0912 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 531.9976 | NaN | 10.5394 | NaN | 16.4084
2388.1292 | 12.6139 | 12.2653 | 12.4421 | 12.6997 | 12.1844 | 12.4679 | 12.1994 | 12.0162 | NaN | NaN | NaN | 12.4657 | 117.8701 | NaN | NaN | NaN | -9.2424 | NaN | NaN | NaN | NaN | 531.8945 | NaN | 22.6183 | NaN | 15.6425
2389.1292 | 12.615 | 12.2673 | 12.4377 | 12.7187 | 12.2674 | 12.4568 | 12.1915 | 12.0195 | NaN | NaN | NaN | 12.5126 | 123.9899 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 530.8546 | NaN | 38.2669 | NaN | 15.3612
2390.1292 | 12.5858 | 12.3002 | 12.4374 | 12.731 | 12.2659 | 12.4759 | 12.2031 | 12.0254 | NaN | NaN | NaN | 12.4968 | 129.814 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 530.5153 | NaN | 22.1737 | NaN | 15.6181
2391.1292 | 12.5909 | 12.2978 | 12.4424 | 12.6846 | 12.2921 | 12.4649 | 12.1988 | 12.0228 | NaN | NaN | NaN | 12.4742 | 125.8405 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 531.2139 | NaN | 27.2886 | NaN | 14.6436
2392.1292 | 12.6538 | 12.252 | 12.4378 | 12.7742 | 12.2549 | 12.452 | 12.1957 | 12.0268 | NaN | NaN | NaN | 12.4896 | 130.5997 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 532.8394 | NaN | 26.553 | NaN | 16.9044
2393.1292 | 12.6007 | 12.2774 | 12.4439 | 12.6992 | 12.2674 | 12.4545 | 12.2015 | 12.0238 | NaN | NaN | NaN | 12.5131 | 116.0947 | NaN | NaN | NaN | -7.4376 | NaN | NaN | NaN | NaN | 533.1629 | NaN | 15.7995 | NaN | 16.8762
2394.1292 | 12.6085 | 12.2683 | 12.446 | 12.7115 | 12.2523 | 12.4518 | 12.1914 | 12.0237 | NaN | NaN | NaN | 12.4978 | 131.0762 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 533.8938 | NaN | 19.7872 | NaN | 15.9768
2395.1292 | 12.6053 | 12.319 | 12.4409 | 12.7479 | 12.2242 | 12.4913 | 12.2059 | 12.03 | NaN | NaN | NaN | 12.502 | 133.1227 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 534.1646 | NaN | 16.3278 | NaN | 17.9454
2396.1292 | 12.6122 | 12.2624 | 12.4459 | 12.7429 | 12.2104 | 12.4516 | 12.1973 | 12.0272 | NaN | NaN | NaN | 12.4891 | 135.108 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 533.16 | NaN | 13.4421 | NaN | 15.3277
2397.1292 | 12.6044 | 12.2484 | 12.4492 | 12.7548 | 12.2899 | 12.4343 | 12.1866 | 12.0301 | NaN | NaN | NaN | 12.524 | 117.7096 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 534.4978 | NaN | 27.3168 | NaN | 15.8856
2398.1292 | 12.5916 | 12.2516 | 12.4467 | 12.7235 | 12.222 | 12.4418 | 12.1936 | 12.0242 | NaN | NaN | NaN | 12.5035 | 119.9363 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 531.8133 | NaN | 15.2922 | NaN | 12.3593
2399.1292 | 12.6123 | 12.2661 | 12.45 | 12.732 | 12.288 | 12.4448 | 12.1997 | 12.027 | NaN | NaN | NaN | 12.5006 | 125.9556 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 534.2748 | NaN | 13.9992 | NaN | 16.6444
2400.1292 | 12.6105 | 12.275 | 12.4496 | 12.729 | 12.2896 | 12.4463 | 12.1948 | 12.0292 | NaN | NaN | NaN | 12.4926 | 117.794 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 532.8402 | NaN | 22.4274 | NaN | 16.738
2401.1292 | 12.6011 | 12.2993 | 12.4431 | 12.707 | 12.2045 | 12.4747 | 12.2098 | 12.0263 | NaN | NaN | NaN | 12.5083 | 122.0009 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 532.7168 | NaN | 29.1342 | NaN | 15.9544
2402.1292 | 12.6113 | 12.2908 | 12.4509 | 12.7219 | 12.1911 | 12.4786 | 12.1956 | 12.0238 | NaN | NaN | NaN | 12.4922 | 125.3044 | NaN | NaN | NaN | -5.4021 | NaN | NaN | NaN | NaN | 533.6129 | NaN | 11.5504 | NaN | 16.6679
2403.1292 | 12.6188 | 12.2289 | 12.4489 | 12.7731 | 12.2805 | 12.4411 | 12.1943 | 12.028 | NaN | NaN | NaN | 12.4837 | 117.9427 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 532.0487 | NaN | 23.696 | NaN | 16.1774
2404.1292 | 12.6516 | 12.2963 | 12.4516 | 12.7433 | 12.2653 | 12.461 | 12.2066 | 12.0248 | NaN | NaN | NaN | 12.4819 | 142.3614 | NaN | NaN | NaN | 2.9769 | NaN | NaN | NaN | NaN | 528.3685 | NaN | 21.0349 | NaN | 19.1981
2405.1292 | 12.6172 | 12.2576 | 12.4525 | 12.7192 | 12.2127 | 12.4547 | 12.2013 | 12.0288 | NaN | NaN | NaN | 12.5038 | 124.1125 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 532.372 | NaN | 32.7446 | NaN | 15.5481
2406.1292 | 12.6895 | 12.2869 | 12.4522 | 12.7163 | 12.2688 | 12.4654 | 12.2022 | 12.0242 | NaN | NaN | NaN | 12.4723 | 130.6759 | NaN | NaN | NaN | -4.2656 | NaN | NaN | NaN | NaN | 531.2182 | NaN | 22.4037 | NaN | 15.7491
2407.1292 | 12.6399 | 12.2152 | 12.4526 | 12.782 | 12.181 | 12.4421 | 12.1913 | 12.0329 | NaN | NaN | NaN | 12.5039 | 111.6302 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 531.1473 | NaN | 19.492 | NaN | 15.9315
2408.1292 | 12.6338 | 12.2151 | 12.4546 | 12.7726 | 12.2757 | 12.4377 | 12.195 | 12.0328 | NaN | NaN | NaN | 12.5123 | 137.5579 | NaN | NaN | NaN | -6.7335 | NaN | NaN | NaN | -2.5489 | 528.3153 | NaN | 13.3762 | NaN | 16.2348
2409.1292 | 12.6066 | 12.2664 | 12.4472 | 12.7266 | 12.2389 | 12.4597 | 12.1955 | 12.0268 | NaN | NaN | NaN | 12.5121 | 126.6633 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 528.5823 | NaN | 11.8864 | NaN | 13.3812
2410.1292 | 12.6039 | 12.2486 | 12.4533 | 12.7011 | 12.1772 | 12.4447 | 12.1994 | 12.0229 | NaN | NaN | NaN | 12.5284 | 125.923 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 530.2243 | NaN | 12.9568 | NaN | 13.8724
2411.1292 | 12.6094 | 12.224 | 12.4461 | 12.7152 | 12.2171 | 12.439 | 12.1999 | 12.0245 | NaN | NaN | NaN | 12.5387 | 124.7331 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 530.723 | NaN | 21.7507 | NaN | 16.7352
2412.1292 | 12.5774 | 12.2736 | 12.4471 | 12.7724 | 12.2789 | 12.4578 | 12.2154 | 12.0269 | NaN | NaN | NaN | 12.5103 | 119.1579 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 526.9562 | NaN | 23.4685 | NaN | 17.1069
2413.1292 | 12.5899 | 12.2921 | 12.4524 | 12.7492 | 12.2511 | 12.468 | 12.2201 | 12.0332 | NaN | NaN | NaN | 12.4985 | 113.9745 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 526.6761 | NaN | 14.6978 | NaN | 16.1788
2414.1292 | 12.7032 | 12.2825 | 12.4431 | 12.7451 | 12.2876 | 12.4613 | 12.2183 | 12.0349 | NaN | NaN | NaN | 12.5197 | 120.9458 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 528.6239 | NaN | 27.6042 | NaN | 15.9334
2415.1292 | 12.6117 | 12.248 | 12.451 | 12.7867 | 12.2552 | 12.4298 | 12.2051 | 12.0359 | NaN | NaN | NaN | 12.5417 | 113.7278 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 526.85 | NaN | 16.9602 | NaN | 16.4508
2416.1292 | 12.5955 | 12.3031 | 12.4525 | 12.7304 | 12.2867 | 12.4497 | 12.212 | 12.0357 | NaN | NaN | NaN | 12.5255 | 129.4053 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 527.1024 | NaN | 10.3462 | NaN | 15.3862
2417.1292 | 12.5974 | 12.2271 | 12.4563 | 12.7159 | 12.2715 | 12.4246 | 12.208 | 12.0398 | NaN | NaN | NaN | 12.532 | 124.7607 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 525.651 | NaN | 23.9841 | NaN | 16.5841
2418.1292 | 12.5886 | 12.2225 | 12.453 | 12.7233 | 12.2774 | 12.4213 | 12.2037 | 12.0429 | NaN | NaN | NaN | 12.542 | 114.835 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 526.1075 | NaN | 26.9661 | NaN | 15.7688
2419.1292 | 12.6072 | 12.224 | 12.4528 | 12.7491 | 12.2734 | 12.4144 | 12.2076 | 12.0432 | NaN | NaN | NaN | 12.5368 | 131.9279 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 523.3911 | NaN | 29.3722 | NaN | 15.7103
2420.1292 | 12.6175 | 12.2436 | 12.4423 | 12.7463 | 12.2849 | 12.4135 | 12.2107 | 12.0504 | NaN | NaN | NaN | 12.5297 | 113.3434 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 527.1213 | NaN | 23.6956 | NaN | 16.8606
2421.1292 | 12.6219 | 12.2411 | 12.4486 | 12.7885 | 12.2501 | 12.4043 | 12.211 | 12.0423 | NaN | NaN | NaN | 12.5407 | 121.2777 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 523.9711 | NaN | 15.1707 | NaN | 16.28
2422.1292 | 12.6259 | 12.3078 | 12.4452 | 12.767 | 12.3166 | 12.4445 | 12.2214 | 12.0487 | NaN | NaN | NaN | 12.564 | 125.1139 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 524.5398 | NaN | 35.1199 | NaN | 17.0404
2423.1292 | 12.6227 | 12.2521 | 12.4444 | 12.7882 | 12.303 | 12.4161 | 12.2218 | 12.0429 | NaN | NaN | NaN | 12.5494 | 126.4328 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 525.0626 | NaN | 15.6991 | NaN | 16.5639
2424.1292 | 12.6263 | 12.2381 | 12.4399 | 12.7398 | 12.2693 | 12.4151 | 12.214 | 12.0491 | NaN | NaN | NaN | 12.5344 | 129.4354 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 526.5667 | NaN | 24.6414 | NaN | 16.4376
2425.1292 | 12.6145 | 12.2542 | 12.4341 | 12.7272 | 12.2905 | 12.4195 | 12.2143 | 12.0449 | NaN | NaN | NaN | 12.5338 | 123.8262 | NaN | NaN | NaN | -19.8111 | NaN | NaN | NaN | NaN | 525.3824 | NaN | 30.1939 | NaN | 17.3836
2426.1292 | 12.6266 | 12.2708 | 12.4361 | 12.7274 | 12.2753 | 12.433 | 12.2154 | 12.0515 | NaN | NaN | NaN | 12.5526 | 126.0136 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 528.1663 | NaN | 19.7446 | NaN | 17.2482
2427.1292 | 12.6291 | 12.2533 | 12.4453 | 12.7583 | 12.2629 | 12.4258 | 12.2137 | 12.0484 | NaN | NaN | NaN | 12.536 | 136.2197 | NaN | NaN | NaN | -6.1853 | NaN | NaN | NaN | NaN | 526.7158 | NaN | 16.0585 | NaN | 14.7185
2428.1292 | 12.6244 | 12.2651 | 12.4433 | 12.7226 | 12.3047 | 12.429 | 12.2238 | 12.053 | NaN | NaN | NaN | 12.5588 | 125.2834 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 524.7524 | NaN | 16.7764 | NaN | 16.9112
2429.1292 | 12.63 | 12.2673 | 12.4379 | 12.7055 | 12.2974 | 12.4424 | 12.2239 | 12.0581 | NaN | NaN | NaN | 12.5598 | 121.5148 | NaN | NaN | NaN | -0.3706 | NaN | NaN | NaN | NaN | 523.9299 | NaN | 25.4358 | NaN | 15.7902
2430.1292 | 12.6059 | 12.3041 | 12.4384 | 12.7676 | 12.2418 | 12.4501 | 12.2165 | 12.0571 | NaN | NaN | NaN | 12.5512 | 133.9746 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 524.0578 | NaN | 14.0369 | NaN | 17.6967
2431.1292 | 12.6019 | 12.2991 | 12.4458 | 12.8134 | 12.2809 | 12.4496 | 12.2165 | 12.0583 | NaN | NaN | NaN | 12.5567 | 109.4539 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 525.0227 | NaN | 32.2175 | NaN | 19.1486
2432.1292 | 12.6256 | 12.2532 | 12.4418 | 12.7379 | 12.2792 | 12.4199 | 12.2219 | 12.0632 | NaN | NaN | NaN | 12.5519 | 125.7591 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 523.6644 | NaN | 22.5845 | NaN | 17.0428
2433.1292 | 12.625 | 12.2611 | 12.4426 | 12.7337 | 12.3012 | 12.4293 | 12.2222 | 12.065 | NaN | NaN | NaN | 12.5942 | 120.3935 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 527.2934 | NaN | 28.4283 | NaN | 18.5964
2434.1292 | 12.6248 | 12.2566 | 12.4448 | 12.7256 | 12.2857 | 12.4239 | 12.2268 | 12.0636 | NaN | NaN | NaN | 12.5396 | 118.9674 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 524.7382 | NaN | 16.4567 | NaN | 15.4291
2435.1292 | 12.6241 | 12.2494 | 12.4396 | 12.7435 | 12.2349 | 12.4227 | 12.2277 | 12.0686 | NaN | NaN | NaN | 12.5527 | 114.0499 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 524.8871 | NaN | 12.328 | NaN | 14.9502
2436.1292 | 12.6447 | 12.2457 | 12.4494 | 12.7467 | 12.282 | 12.4228 | 12.2304 | 12.0754 | NaN | NaN | NaN | 12.5649 | 128.0954 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 525.5458 | NaN | 11.2913 | NaN | 16.9531
2437.1292 | 12.6474 | 12.2657 | 12.452 | 12.7266 | 12.3062 | 12.427 | 12.2318 | 12.0722 | NaN | NaN | NaN | 12.5751 | 131.3264 | NaN | NaN | NaN | 4.2663 | NaN | NaN | NaN | NaN | 524.5912 | NaN | 19.5078 | NaN | 18.132
2438.1292 | 12.6173 | 12.2758 | 12.4449 | 12.73 | 12.2452 | 12.4218 | 12.2293 | 12.0752 | NaN | NaN | NaN | 12.5685 | 129.613 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 521.6229 | NaN | 13.4455 | NaN | 16.5385
2439.1292 | 12.6969 | 12.2646 | 12.4454 | 12.7154 | 12.2648 | 12.4318 | 12.23 | 12.0715 | NaN | NaN | NaN | 12.5237 | 117.8039 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 524.3164 | NaN | 29.9367 | NaN | 15.0455
2440.1292 | 12.6365 | 12.3024 | 12.4467 | 12.7609 | 12.2843 | 12.4313 | 12.2227 | 12.0753 | NaN | NaN | NaN | 12.5613 | 133.132 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 519.2124 | NaN | 13.0688 | NaN | 17.1589
2441.1292 | 12.6357 | 12.2616 | 12.4538 | 12.7413 | 12.3091 | 12.414 | 12.2095 | 12.0769 | NaN | NaN | NaN | 12.5491 | 120.1454 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 524.1152 | NaN | 28.4328 | NaN | 18.1539
2442.1292 | 12.6429 | 12.2581 | 12.4561 | 12.7345 | 12.2666 | 12.4148 | 12.2077 | 12.0834 | NaN | NaN | NaN | 12.563 | 120.9244 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 525.7012 | NaN | 26.5658 | NaN | 19.2189
2443.1292 | 12.6413 | 12.25 | 12.454 | 12.7524 | 12.2894 | 12.4132 | 12.208 | 12.0778 | NaN | NaN | NaN | 12.5549 | 131.6375 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 523.7652 | NaN | 22.5234 | NaN | 18.9725
2444.1292 | 12.6722 | 12.2981 | 12.4545 | 12.7275 | 12.2866 | 12.4412 | 12.22 | 12.0786 | NaN | NaN | NaN | 12.5529 | 121.266 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 523.1534 | NaN | 23.5836 | NaN | 15.1811
2445.1292 | 12.6442 | 12.2939 | 12.4549 | 12.7397 | 12.2781 | 12.4394 | 12.2206 | 12.0825 | NaN | NaN | NaN | 12.5468 | 123.0555 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 525.1535 | NaN | 24.8717 | NaN | 16.8762
2446.1292 | 12.6485 | 12.354 | 12.4611 | 12.7343 | 12.2373 | 12.4779 | 12.2404 | 12.0859 | NaN | NaN | NaN | 12.6005 | 126.9175 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 524.5384 | NaN | 22.4582 | NaN | 16.6919
2447.1292 | 12.6614 | 12.2546 | 12.4633 | 12.7345 | 12.2168 | 12.4228 | 12.2164 | 12.0864 | NaN | NaN | NaN | 12.5521 | 130.9645 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 526.1635 | NaN | 16.1669 | NaN | 18.1395
2448.1292 | 12.6107 | 12.3327 | 12.463 | 12.7554 | 12.2917 | 12.4637 | 12.223 | 12.0884 | NaN | NaN | NaN | 12.556 | 128.1504 | NaN | NaN | NaN | -16.4363 | NaN | NaN | NaN | NaN | 524.3038 | NaN | 32.8816 | NaN | 16.0542
2449.1292 | 12.7193 | 12.2953 | 12.4578 | 12.7605 | 12.2636 | 12.4473 | 12.2232 | 12.0825 | NaN | NaN | NaN | 12.5542 | 121.5123 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 526.0139 | NaN | 14.3399 | NaN | 18.5509
2450.1292 | 12.8167 | 12.2612 | 12.4645 | 12.7207 | 12.2096 | 12.4242 | 12.2061 | 12.0773 | NaN | NaN | NaN | 12.5492 | 125.3151 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 526.1946 | NaN | 25.1557 | NaN | 16.5622
2451.1292 | 12.7168 | 12.3422 | 12.4672 | 12.7294 | 12.2756 | 12.4589 | 12.2246 | 12.0776 | NaN | NaN | NaN | 12.5581 | 120.7901 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 524.8145 | NaN | 21.1222 | NaN | 18.214
2452.1292 | 12.6786 | 12.2705 | 12.4716 | 12.7126 | 12.256 | 12.4244 | 12.2028 | 12.0751 | NaN | NaN | NaN | 12.5416 | 127.8567 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 529.2007 | NaN | 23.9494 | NaN | 12.3346
2453.1292 | 12.6595 | 12.2885 | 12.4643 | 12.7484 | 12.3217 | 12.429 | 12.2093 | 12.0728 | NaN | NaN | NaN | 12.5588 | 118.767 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 527.2967 | NaN | 22.5914 | NaN | 15.3307
2454.1292 | 12.6625 | 12.2817 | 12.474 | 12.7266 | 12.2199 | 12.4402 | 12.2185 | 12.082 | NaN | NaN | NaN | 12.6095 | 123.0529 | NaN | NaN | NaN | -1.583 | NaN | NaN | NaN | NaN | 523.2716 | NaN | 21.5497 | NaN | 19.3013
2455.1292 | 12.6588 | 12.3295 | 12.4735 | 12.7407 | 12.2636 | 12.46 | 12.2216 | 12.0747 | NaN | NaN | NaN | 12.5697 | 128.8038 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 524.9954 | NaN | 26.5802 | NaN | 18.602
2456.1292 | 12.6483 | 12.333 | 12.4709 | 12.7248 | 12.2082 | 12.4476 | 12.2207 | 12.0699 | NaN | NaN | NaN | 12.5647 | 135.728 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 527.0182 | NaN | 20.5404 | NaN | 17.2729
2457.1292 | 12.6531 | 12.2732 | 12.4762 | 12.7217 | 12.2902 | 12.4274 | 12.2071 | 12.0733 | NaN | NaN | NaN | 12.5657 | 124.9468 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 527.8823 | NaN | 24.0211 | NaN | 15.8968
2458.1292 | 12.6621 | 12.2927 | 12.4809 | 12.7977 | 12.2808 | 12.439 | 12.2188 | 12.0787 | NaN | NaN | NaN | 12.5366 | 119.6041 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 529.6452 | NaN | 18.6812 | NaN | 17.0594
2459.1292 | 12.688 | 12.3368 | 12.4811 | 12.7588 | 12.2931 | 12.4551 | 12.2273 | 12.0667 | NaN | NaN | NaN | 12.5393 | 123.9773 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 527.4276 | NaN | 20.8036 | NaN | 9.4945
2460.1292 | 12.6633 | 12.2758 | 12.4857 | 12.7937 | 12.1863 | 12.4469 | 12.2247 | 12.073 | NaN | NaN | NaN | 12.5168 | 125.9972 | NaN | NaN | NaN | -18.0829 | NaN | NaN | NaN | NaN | 528.257 | NaN | 19.167 | NaN | 18.0219
2461.1292 | 12.6231 | 12.3277 | 12.4854 | 12.7664 | 12.2091 | 12.4604 | 12.227 | 12.0741 | NaN | NaN | NaN | 12.5398 | 121.1329 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 529.6521 | NaN | 12.0867 | NaN | 18.1896
2462.1292 | 12.638 | 12.3233 | 12.4879 | 12.788 | 12.2366 | 12.4545 | 12.2362 | 12.0677 | NaN | NaN | NaN | 12.563 | 124.5838 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 530.8414 | NaN | 18.4053 | NaN | 14.5513
2463.1292 | 12.6444 | 12.3301 | 12.4873 | 12.7621 | 12.2922 | 12.4504 | 12.2311 | 12.0715 | NaN | NaN | NaN | 12.5656 | 123.9219 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 529.4902 | NaN | 29.7967 | NaN | 17.0272
2464.1292 | 12.6429 | 12.3148 | 12.4906 | 12.7549 | 12.3184 | 12.4486 | 12.2396 | 12.0736 | NaN | NaN | NaN | 12.5591 | 116.5661 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 530.4217 | NaN | 12.4768 | NaN | 15.8152
2465.1292 | 12.7592 | 12.3173 | 12.4951 | 12.7498 | 12.3042 | 12.4526 | 12.2388 | 12.0699 | NaN | NaN | NaN | 12.5469 | 116.1567 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 529.7538 | NaN | 24.2781 | NaN | 16.9783
2466.1292 | 12.6627 | 12.3263 | 12.4923 | 12.7528 | 12.2041 | 12.4525 | 12.2337 | 12.0731 | NaN | NaN | NaN | 12.5455 | 122.1294 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 530.443 | NaN | 25.6861 | NaN | 18.8527
2467.1292 | 12.6435 | 12.287 | 12.4984 | 12.7498 | 12.3238 | 12.4326 | 12.2231 | 12.0654 | NaN | NaN | NaN | 12.5626 | 115.9171 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 530.4055 | NaN | 19.7318 | NaN | 17.8216
2468.1292 | 12.6462 | 12.3212 | 12.5002 | 12.7187 | 12.237 | 12.4642 | 12.2387 | 12.0641 | NaN | NaN | NaN | 12.5503 | 119.126 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 534.0543 | NaN | 10.1249 | NaN | 19.1374
2469.1292 | 12.647 | 12.2786 | 12.5014 | 12.802 | 12.2137 | 12.4526 | 12.2345 | 12.0651 | NaN | NaN | NaN | 12.5375 | 124.5526 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 531.6175 | NaN | 20.4203 | NaN | 17.3696
2470.1292 | 12.6927 | 12.2732 | 12.507 | 12.7072 | 12.2625 | 12.4381 | 12.2346 | 12.0668 | NaN | NaN | NaN | 12.564 | 130.8544 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 531.7998 | NaN | 14.83 | NaN | 18.0234
2471.1292 | 12.6775 | 12.2898 | 12.5018 | 12.7612 | 12.2767 | 12.4556 | 12.2361 | 12.0681 | NaN | NaN | NaN | 12.5591 | 132.7875 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 530.6877 | NaN | 12.549 | NaN | 25.0029
2472.1292 | 12.6274 | 12.3702 | 12.5016 | 12.7755 | 12.2743 | 12.475 | 12.243 | 12.0772 | NaN | NaN | NaN | 12.5866 | 118.7781 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 533.2318 | NaN | 13.7192 | NaN | 18.6642
2473.1292 | 12.6349 | 12.3089 | 12.5033 | 12.7397 | 12.2359 | 12.4504 | 12.2321 | 12.0696 | NaN | NaN | NaN | 12.6269 | 118.77 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 532.0469 | NaN | 11.612 | NaN | 19.006
2474.1292 | 12.6438 | 12.3002 | 12.5018 | 12.742 | 12.3024 | 12.4644 | 12.2401 | 12.0721 | NaN | NaN | NaN | 12.581 | 130.275 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 531.3782 | NaN | 12.3332 | NaN | 14.1918
2475.1292 | 12.8323 | 12.3448 | 12.5077 | 12.7654 | 12.2582 | 12.482 | 12.2568 | 12.0733 | NaN | NaN | NaN | 12.5519 | 120.9591 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 535.7878 | NaN | 27.447 | NaN | 10.4449
2476.1292 | 12.7258 | 12.3209 | 12.5113 | 12.7169 | 12.3025 | 12.4703 | 12.239 | 12.0718 | NaN | NaN | NaN | 12.5418 | 120.3301 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 534.1272 | NaN | 28.4779 | NaN | 17.0099
2477.1292 | 12.6318 | 12.2927 | 12.5055 | 12.7662 | 12.2968 | 12.4416 | 12.2316 | 12.0668 | NaN | NaN | NaN | 12.5423 | 127.4872 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 533.0771 | NaN | 16.2352 | NaN | 14.5358
2478.1292 | 12.6553 | 12.2979 | 12.5083 | 12.7604 | 12.295 | 12.4513 | 12.232 | 12.0693 | NaN | NaN | NaN | 12.5701 | 128.2137 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 533.965 | NaN | 16.565 | NaN | 19.747
2479.1292 | 12.6428 | 12.376 | 12.5039 | 12.7608 | 12.3066 | 12.4729 | 12.2365 | 12.0702 | NaN | NaN | NaN | 12.5347 | 123.8048 | NaN | NaN | NaN | 4.2719 | NaN | NaN | NaN | NaN | 534.0988 | NaN | 16.5408 | NaN | 19.4407
2480.1292 | 12.6502 | 12.3054 | 12.5117 | 12.7705 | 12.3144 | 12.4633 | 12.2283 | 12.0713 | NaN | NaN | NaN | 12.5389 | 124.6065 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 535.9721 | NaN | 21.1352 | NaN | 18.3647
2481.1292 | 12.6749 | 12.4076 | 12.513 | 12.7428 | 12.2038 | 12.5296 | 12.254 | 12.0712 | NaN | NaN | NaN | 12.5508 | 107.4615 | NaN | NaN | NaN | 3.9023 | NaN | NaN | NaN | NaN | 535.2951 | NaN | 26.0556 | NaN | 17.8428
2482.1292 | 12.716 | 12.3414 | 12.5124 | 12.7579 | 12.3275 | 12.4697 | 12.2419 | 12.0653 | NaN | NaN | NaN | 12.5267 | 121.6805 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 535.5302 | NaN | 11.5953 | NaN | 7.3175
2483.1292 | 12.6433 | 12.4106 | 12.5042 | 12.7546 | 12.3398 | 12.5025 | 12.2551 | 12.0704 | NaN | NaN | NaN | 12.5545 | 138.5991 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 533.8362 | NaN | 22.1665 | NaN | 19.3168
2484.1292 | 12.664 | 12.324 | 12.5053 | 12.7572 | 12.3025 | 12.4528 | 12.24 | 12.0682 | NaN | NaN | NaN | 12.5272 | 132.4376 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 531.6724 | NaN | 23.7129 | NaN | 16.9797
2485.1292 | 12.6379 | 12.3165 | 12.5076 | 12.7564 | 12.3007 | 12.4632 | 12.2487 | 12.0655 | NaN | NaN | NaN | 12.5443 | 120.2649 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 533.7917 | NaN | 24.1782 | NaN | 17.2952
2486.1292 | 12.6406 | 12.3206 | 12.5041 | 12.744 | 12.2862 | 12.4602 | 12.2383 | 12.0696 | NaN | NaN | NaN | 12.5418 | 116.9287 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 534.7957 | NaN | 12.4879 | NaN | 16.1951
2487.1292 | 12.6371 | 12.3135 | 12.5051 | 12.7598 | 12.2519 | 12.4593 | 12.2338 | 12.0647 | NaN | NaN | NaN | 12.5549 | 137.0449 | NaN | NaN | -12.4076 | -0.3781 | NaN | NaN | NaN | NaN | 528.8688 | NaN | 22.0928 | NaN | 15.6625
2488.1292 | 12.6473 | 12.3351 | 12.5033 | 12.74 | 12.3227 | 12.4621 | 12.2449 | 12.0655 | NaN | NaN | NaN | 12.5403 | 124.8285 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 535.7052 | NaN | 23.7119 | NaN | 17.4424
2489.1292 | 12.6645 | 12.323 | 12.4967 | 12.7305 | 12.2887 | 12.4614 | 12.2429 | 12.062 | NaN | NaN | NaN | 12.539 | 133.4467 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 535.8998 | NaN | 17.6552 | NaN | 18.3543
2490.1292 | 12.6204 | 12.3543 | 12.498 | 12.721 | 12.3026 | 12.4765 | 12.2489 | 12.0618 | NaN | NaN | NaN | 12.5526 | 126.6065 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 536.9028 | NaN | 16.9325 | NaN | 16.6301
2491.1292 | 12.628 | 12.3474 | 12.4974 | 12.8106 | 12.2925 | 12.4631 | 12.2452 | 12.0713 | NaN | NaN | NaN | 12.5547 | 114.6647 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 536.3726 | NaN | 14.5738 | NaN | 18.5902
2492.1292 | 12.6367 | 12.3379 | 12.497 | 12.8586 | 12.2899 | 12.4656 | 12.237 | 12.0685 | NaN | NaN | NaN | 12.5631 | 115.6673 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 536.3465 | NaN | 32.574 | NaN | 20.1355
2493.1292 | 12.6428 | 12.4375 | 12.5005 | 12.8874 | 12.3218 | 12.5199 | 12.2698 | 12.0732 | NaN | NaN | NaN | 12.5738 | 130.4808 | NaN | NaN | NaN | -9.8755 | NaN | NaN | NaN | NaN | 537.3106 | NaN | 22.3901 | NaN | 9.9504
2494.1292 | 12.6382 | 12.328 | 12.4943 | 12.7674 | 12.3292 | 12.4619 | 12.2405 | 12.0749 | NaN | NaN | NaN | 12.5225 | 127.9394 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 535.6417 | NaN | 17.9759 | NaN | 6.2917
2495.1292 | 12.6433 | 12.3522 | 12.4989 | 12.7499 | 12.3374 | 12.4658 | 12.247 | 12.0747 | NaN | NaN | NaN | 12.5335 | 127.9721 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 533.8872 | NaN | 38.2605 | NaN | 19.0243
2496.1292 | 12.7201 | 12.4137 | 12.492 | 12.7334 | 12.3231 | 12.4942 | 12.2608 | 12.0774 | NaN | NaN | NaN | 12.5185 | 128.1236 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 532.8629 | NaN | 22.2506 | NaN | 18.7111
2497.1292 | 12.6378 | 12.341 | 12.4998 | 12.7382 | 12.3102 | 12.4748 | 12.2553 | 12.0843 | NaN | NaN | NaN | 12.5636 | 119.2216 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -16.4643 | 534.5602 | NaN | 30.147 | NaN | 18.7902
2498.1292 | 12.6494 | 12.4034 | 12.4933 | 12.7505 | 12.2426 | 12.5048 | 12.2605 | 12.0861 | NaN | NaN | NaN | 12.5749 | 124.6823 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 532.9631 | NaN | 25.5048 | NaN | 20.2002
2499.1292 | 12.6603 | 12.3771 | 12.4978 | 12.7435 | 12.2869 | 12.4833 | 12.2461 | 12.0875 | NaN | NaN | NaN | 12.531 | 115.8764 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 537.3737 | NaN | 18.054 | NaN | 10.1044
2500.1292 | 12.6679 | 12.3796 | 12.4996 | 12.7236 | 12.3217 | 12.4734 | 12.2568 | 12.09 | NaN | NaN | NaN | 12.5259 | 124.6381 | NaN | NaN | NaN | -16.8659 | NaN | NaN | NaN | NaN | 537.0429 | NaN | 12.5362 | NaN | 18.9614
2501.1292 | 12.6797 | 12.3698 | 12.4957 | 12.735 | 12.3254 | 12.4936 | 12.2579 | 12.0847 | NaN | NaN | NaN | 12.5451 | 117.2704 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 536.8226 | NaN | 13.2394 | NaN | 19.1218
2502.1292 | 12.6284 | 12.3871 | 12.5047 | 12.7509 | 12.2814 | 12.4938 | 12.2492 | 12.0851 | NaN | NaN | NaN | 12.561 | 114.5348 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 534.9223 | NaN | 23.6586 | NaN | 17.9588
2503.1292 | 12.6384 | 12.415 | 12.4992 | 12.7831 | 12.3435 | 12.5108 | 12.2588 | 12.0841 | NaN | NaN | NaN | 12.5253 | 122.5555 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 538.9433 | NaN | 23.6884 | NaN | 18.7162
2504.1292 | 12.6502 | 12.3612 | 12.5046 | 12.704 | 12.2465 | 12.4982 | 12.2493 | 12.0843 | NaN | NaN | NaN | 12.548 | 125.9256 | NaN | NaN | NaN | 3.6055 | NaN | NaN | NaN | NaN | 538.8731 | NaN | 17.4678 | NaN | 18.4337
2505.1292 | 12.6572 | 12.3487 | 12.4966 | 12.7294 | 12.3074 | 12.4866 | 12.2552 | 12.0815 | NaN | NaN | NaN | 12.531 | 115.5463 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 538.6518 | NaN | 22.3658 | NaN | 27.1751
2506.1292 | 12.6542 | 12.3488 | 12.497 | 12.7477 | 12.2133 | 12.4813 | 12.2481 | 12.0888 | NaN | NaN | NaN | 12.5688 | 130.9326 | NaN | NaN | NaN | 4.5223 | NaN | NaN | NaN | NaN | 538.3444 | NaN | 18.2671 | NaN | 18.5776
2507.1292 | 12.6542 | 12.3318 | 12.4938 | 12.7038 | 12.3023 | 12.476 | 12.256 | 12.0885 | NaN | NaN | NaN | 12.5175 | 122.9349 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 539.8797 | NaN | 25.6494 | NaN | 13.651
2508.1292 | 12.6633 | 12.3409 | 12.4941 | 12.7109 | 12.3159 | 12.4834 | 12.2527 | 12.0895 | NaN | NaN | NaN | 12.5888 | 117.1202 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 539.7761 | NaN | 31.1479 | NaN | 16.0467
2509.1292 | 12.6688 | 12.3638 | 12.4933 | 12.6942 | 12.3225 | 12.4953 | 12.2543 | 12.0904 | NaN | NaN | NaN | 12.5127 | 120.0752 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 539.3944 | NaN | 13.1872 | NaN | 18.3298
2510.1292 | 12.6307 | 12.3785 | 12.4911 | 12.7807 | 12.3484 | 12.5102 | 12.267 | 12.09 | NaN | NaN | NaN | 12.5152 | 122.5809 | NaN | NaN | NaN | 11.6082 | NaN | NaN | NaN | NaN | 539.5315 | NaN | 33.2199 | NaN | 18.214
2511.1292 | 12.6392 | 12.3438 | 12.4981 | 12.7219 | 12.3219 | 12.4882 | 12.2467 | 12.0883 | NaN | NaN | NaN | 12.5058 | 119.5127 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 541.6898 | NaN | 14.8373 | NaN | 20.4277
2512.1292 | 12.6385 | 12.357 | 12.4934 | 12.7604 | 12.2985 | 12.4982 | 12.2582 | 12.0816 | NaN | NaN | NaN | 12.5018 | 123.9122 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 540.6479 | NaN | 16.9779 | NaN | 19.059
2513.1292 | 12.646 | 12.3573 | 12.5028 | 12.7364 | 12.3337 | 12.5038 | 12.2576 | 12.0734 | NaN | NaN | NaN | 12.5186 | 133.5225 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 540.9088 | NaN | 20.7457 | NaN | 17.0481
2514.1292 | 12.6425 | 12.3104 | 12.5041 | 12.746 | 12.2992 | 12.4879 | 12.2538 | 12.078 | NaN | NaN | NaN | 12.5654 | 127.1526 | NaN | NaN | NaN | -15.3361 | NaN | NaN | NaN | NaN | 539.6509 | NaN | 16.0679 | NaN | 17.716
2515.1292 | 12.6499 | 12.3096 | 12.505 | 12.8506 | 12.3089 | 12.5067 | 12.2564 | 12.0808 | NaN | NaN | NaN | 12.5155 | 116.9622 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 542.7588 | NaN | 17.5764 | NaN | 19.8818
2516.1292 | 12.6259 | 12.3179 | 12.5085 | 12.7843 | 12.2819 | 12.499 | 12.2527 | 12.0898 | NaN | NaN | NaN | 12.5295 | 124.5623 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 542.1519 | NaN | 18.0501 | NaN | 18.4435
2517.1292 | 12.6288 | 12.3096 | 12.5028 | 12.7249 | 12.3043 | 12.495 | 12.2466 | 12.0882 | NaN | NaN | NaN | 12.5193 | 121.3188 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 540.5618 | NaN | 15.9859 | NaN | 17.191
2518.1292 | 12.6381 | 12.3591 | 12.4996 | 12.7048 | 12.2911 | 12.5269 | 12.2572 | 12.0905 | NaN | NaN | NaN | 12.5292 | 127.3739 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 539.55 | NaN | 20.215 | NaN | 18.5817
2519.1292 | 12.6456 | 12.4108 | 12.4979 | 12.7882 | 12.3397 | 12.5483 | 12.2712 | 12.082 | NaN | NaN | NaN | 12.5275 | 118.7543 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 538.9326 | NaN | 20.0562 | NaN | 19.2227
2520.1292 | 12.6513 | 12.3139 | 12.4869 | 12.765 | 12.3576 | 12.4869 | 12.2531 | 12.087 | NaN | NaN | NaN | 12.5176 | 114.9062 | NaN | NaN | NaN | -16.0691 | NaN | NaN | NaN | NaN | 534.5453 | NaN | 18.1225 | NaN | 20.319
2521.1292 | 12.6367 | 12.3067 | 12.4872 | 12.7532 | 12.2916 | 12.5052 | 12.2539 | 12.0853 | NaN | NaN | NaN | 12.6528 | 123.7321 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 535.5339 | NaN | 28.4325 | NaN | 15.8892
2522.1292 | 12.6458 | 12.333 | 12.4811 | 12.7287 | 12.3175 | 12.5119 | 12.2516 | 12.086 | NaN | NaN | NaN | 12.5167 | 118.671 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 530.2432 | NaN | 23.0997 | NaN | 27.091
2523.1292 | 12.6613 | 12.3256 | 12.4795 | 12.7273 | 12.3719 | 12.4974 | 12.2559 | 12.0901 | NaN | NaN | NaN | 12.515 | 120.8416 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 525.7601 | NaN | 20.9191 | NaN | 18.1756
2524.1292 | 12.6272 | 12.2987 | 12.4802 | 12.7631 | 12.2808 | 12.5015 | 12.2579 | 12.0909 | NaN | NaN | NaN | 12.515 | 124.6619 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 529.7909 | NaN | 19.6522 | NaN | 22.0986
2525.1292 | 12.6995 | 12.4337 | 12.4804 | 12.735 | 12.2583 | 12.5745 | 12.2755 | 12.0854 | NaN | NaN | NaN | 12.5086 | 127.2093 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 534.8749 | NaN | 19.4732 | NaN | 16.5225
2526.1292 | 12.6402 | 12.3116 | 12.4762 | 12.7556 | 12.3393 | 12.4865 | 12.2544 | 12.0898 | NaN | NaN | NaN | 12.5197 | 121.1249 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 531.4048 | NaN | 20.7904 | NaN | 16.8582
2527.1292 | 12.7051 | 12.33 | 12.4803 | 12.7599 | 12.3138 | 12.4925 | 12.2475 | 12.0896 | NaN | NaN | NaN | 12.4937 | 125.5803 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 528.2044 | NaN | 15.3007 | NaN | 11.683
2528.1292 | 12.6531 | 12.3185 | 12.4846 | 12.7453 | 12.3064 | 12.4832 | 12.2455 | 12.0862 | NaN | NaN | NaN | 12.4975 | 134.1721 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 529.3718 | NaN | 15.4534 | NaN | 15.0323
2529.1292 | 12.6496 | 12.3193 | 12.482 | 12.7509 | 12.2969 | 12.4842 | 12.2444 | 12.0915 | NaN | NaN | NaN | 12.4968 | 115.7896 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 528.5612 | NaN | 21.4975 | NaN | 16.6174
2530.1292 | 12.6498 | 12.3251 | 12.4816 | 12.7666 | 12.2972 | 12.4864 | 12.2463 | 12.0855 | NaN | NaN | NaN | 12.4749 | 121.9007 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 528.7202 | NaN | 16.3486 | NaN | 15.8414
2531.1292 | 12.6671 | 12.3362 | 12.4781 | 12.7808 | 12.2576 | 12.5061 | 12.2581 | 12.0945 | NaN | NaN | NaN | 12.4855 | 133.6315 | NaN | NaN | NaN | 3.1206 | NaN | NaN | NaN | NaN | 523.016 | NaN | 20.483 | NaN | 15.9753
2532.1292 | 12.6515 | 12.3053 | 12.4804 | 12.7602 | 12.2819 | 12.4928 | 12.2554 | 12.0963 | NaN | NaN | NaN | 12.5171 | 123.1041 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 527.4224 | NaN | 23.6551 | NaN | -0.5531
2533.1292 | 12.6346 | 12.3316 | 12.4843 | 12.7653 | 12.2373 | 12.4905 | 12.2459 | 12.0925 | NaN | NaN | NaN | 12.5186 | 118.8059 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 527.9277 | NaN | 18.8387 | NaN | 19.6172
2534.1292 | 12.63 | 12.4124 | 12.4847 | 12.7409 | 12.2685 | 12.5551 | 12.2673 | 12.0991 | NaN | NaN | NaN | 12.4932 | 134.9522 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 523.6902 | NaN | 15.1074 | NaN | 16.992
2535.1292 | 12.6306 | 12.339 | 12.4805 | 12.781 | 12.2805 | 12.5063 | 12.2526 | 12.1009 | NaN | NaN | NaN | 12.4979 | 127.15 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 520.9171 | NaN | 11.4735 | NaN | 15.6227
2536.1292 | 12.6289 | 12.3772 | 12.4769 | 12.8104 | 12.2536 | 12.523 | 12.2579 | 12.0997 | NaN | NaN | NaN | 12.5012 | 131.12 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 521.0869 | NaN | 36.8395 | NaN | 17.1436
2537.1292 | 12.6368 | 12.3361 | 12.4714 | 12.7939 | 12.2712 | 12.5005 | 12.2447 | 12.1007 | NaN | NaN | NaN | 12.5263 | 134.3045 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 519.7781 | NaN | 20.4322 | NaN | 14.9472
2538.1292 | 12.6529 | 12.3233 | 12.4781 | 12.7971 | 12.3606 | 12.493 | 12.2424 | 12.1017 | NaN | NaN | NaN | 12.5032 | 123.3708 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 519.626 | NaN | 21.4548 | NaN | 18.7636
2539.1292 | 12.6498 | 12.316 | 12.473 | 12.7893 | 12.3129 | 12.5055 | 12.2471 | 12.1085 | NaN | NaN | NaN | 12.5014 | 125.3338 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 523.6611 | NaN | 22.4866 | NaN | 17.24
2540.1292 | 12.6731 | 12.3016 | 12.4808 | 12.8174 | 12.3532 | 12.4837 | 12.2389 | 12.0993 | NaN | NaN | NaN | 12.5137 | 108.4761 | NaN | NaN | NaN | -13.968 | NaN | NaN | NaN | NaN | 524.1353 | NaN | 14.8507 | NaN | 17.7265
2541.1292 | 12.6276 | 12.3928 | 12.4818 | 12.7907 | 12.3265 | 12.5183 | 12.2659 | 12.1051 | NaN | NaN | NaN | 12.5298 | 124.3108 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 525.7903 | NaN | 27.1896 | NaN | 14.0356
2542.1292 | 12.6408 | 12.3055 | 12.4771 | 12.7783 | 12.2516 | 12.4895 | 12.2547 | 12.1106 | NaN | NaN | NaN | 12.514 | 128.4862 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 524.5184 | NaN | 17.9492 | NaN | 18.5476
2543.1292 | 12.6521 | 12.3269 | 12.4831 | 12.7794 | 12.341 | 12.4884 | 12.2512 | 12.1048 | NaN | NaN | NaN | 12.5177 | 121.9681 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 527.644 | NaN | 12.1388 | NaN | 17.4144
2544.1292 | 12.666 | 12.3176 | 12.4827 | 12.8042 | 12.3157 | 12.4844 | 12.2448 | 12.1034 | NaN | NaN | NaN | 12.5278 | 130.877 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 526.0496 | NaN | 28.3746 | NaN | 25.2354
2545.1292 | 12.6768 | 12.3677 | 12.4787 | 12.7728 | 12.2885 | 12.5207 | 12.2632 | 12.1046 | NaN | NaN | NaN | 12.5221 | 125.9242 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 528.5511 | NaN | 16.4928 | NaN | 18.9429
2546.1292 | 12.6395 | 12.3494 | 12.483 | 12.7967 | 12.3196 | 12.5076 | 12.2585 | 12.1053 | NaN | NaN | NaN | 12.5118 | 129.0955 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 529.2377 | NaN | 20.043 | NaN | 18.7941
2547.1292 | 12.6768 | 12.3425 | 12.4789 | 12.7879 | 12.2881 | 12.5134 | 12.2621 | 12.102 | NaN | NaN | NaN | 12.5021 | 117.5838 | NaN | NaN | NaN | -6.2409 | NaN | NaN | NaN | NaN | 531.2025 | NaN | 25.7595 | NaN | 17.8728
2548.1292 | 12.6548 | 12.3315 | 12.4798 | 12.7962 | 12.3064 | 12.4899 | 12.2616 | 12.1079 | NaN | NaN | NaN | 12.5066 | 134.8411 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 529.0225 | NaN | 13.8359 | NaN | 14.8215
2549.1292 | 12.6623 | 12.338 | 12.483 | 12.7917 | 12.3444 | 12.5007 | 12.255 | 12.1104 | NaN | NaN | NaN | 12.4904 | 127.0646 | NaN | NaN | NaN | -1.8209 | NaN | NaN | NaN | NaN | 528.8555 | NaN | 16.7177 | NaN | 18.4421
2550.1292 | 12.6645 | 12.3405 | 12.4851 | 12.7923 | 12.3372 | 12.4884 | 12.2515 | 12.105 | NaN | NaN | NaN | 12.5056 | 125.7205 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 528.4498 | NaN | 28.938 | NaN | 18.7012
2551.1292 | 12.6669 | 12.3348 | 12.4729 | 12.8118 | 12.3388 | 12.4901 | 12.2415 | 12.1083 | NaN | NaN | NaN | 12.4874 | 130.3707 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 525.4385 | NaN | 24.6811 | NaN | 15.0201
2552.1292 | 12.6979 | 12.334 | 12.4752 | 12.7787 | 12.3147 | 12.4972 | 12.2541 | 12.1124 | NaN | NaN | NaN | 12.5218 | 112.7569 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 529.6228 | NaN | 13.2919 | NaN | 14.9979
2553.1292 | 12.651 | 12.3525 | 12.4813 | 12.8146 | 12.3303 | 12.5072 | 12.2681 | 12.1142 | NaN | NaN | NaN | 12.5064 | 124.9808 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 527.0688 | NaN | 14.5101 | NaN | 15.6803
2554.1292 | 12.6723 | 12.3991 | 12.4714 | 12.8168 | 12.3221 | 12.5187 | 12.2703 | 12.104 | NaN | NaN | NaN | 12.4945 | 126.5975 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 525.2619 | NaN | 14.385 | NaN | 17.99
2555.1292 | 12.6516 | 12.3818 | 12.47 | 12.777 | 12.3026 | 12.5223 | 12.267 | 12.111 | NaN | NaN | NaN | 12.5103 | 121.3563 | NaN | NaN | NaN | -0.1373 | NaN | NaN | NaN | NaN | 523.827 | NaN | 18.7425 | NaN | 15.0299
2556.1292 | 12.6475 | 12.3535 | 12.479 | 12.802 | 12.3129 | 12.5031 | 12.2662 | 12.1135 | NaN | NaN | NaN | 12.5047 | 119.8899 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 524.19 | NaN | 17.6434 | NaN | 16.2034
2557.1292 | 12.6692 | 12.3597 | 12.4742 | 12.8041 | 12.2972 | 12.4986 | 12.2595 | 12.1094 | NaN | NaN | NaN | 12.4928 | 125.3111 | NaN | NaN | NaN | -9.4726 | NaN | NaN | NaN | NaN | 521.9511 | NaN | 24.5574 | NaN | 18.0368
2558.1292 | 12.6508 | 12.3874 | 12.4809 | 12.8607 | 12.3368 | 12.5218 | 12.2769 | 12.1076 | NaN | NaN | NaN | 12.5198 | 120.6735 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 524.4161 | NaN | 9.0536 | NaN | 17.871
2559.1292 | 12.655 | 12.3911 | 12.4791 | 12.8026 | 12.3157 | 12.5073 | 12.2611 | 12.1148 | NaN | NaN | NaN | 12.5156 | 120.5414 | NaN | NaN | NaN | 2.63 | NaN | NaN | NaN | NaN | 520.5389 | NaN | 24.241 | NaN | 18.9569
2560.1292 | 12.6842 | 12.3732 | 12.4715 | 12.8119 | 12.2857 | 12.5073 | 12.2523 | 12.1144 | NaN | NaN | NaN | 12.4951 | 122.4689 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 521.0866 | NaN | 25.7401 | NaN | 16.2321
2561.1292 | 12.6853 | 12.3653 | 12.4781 | 12.809 | 12.3083 | 12.5046 | 12.2555 | 12.1167 | NaN | NaN | NaN | 12.4951 | 126.178 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 519.2849 | NaN | 27.4561 | NaN | 17.1624
2562.1292 | 12.6939 | 12.3771 | 12.493 | 12.8441 | 12.2678 | 12.5143 | 12.258 | 12.1189 | NaN | NaN | NaN | 12.5262 | 122.3591 | NaN | NaN | NaN | 5.211 | NaN | NaN | NaN | NaN | 519.4766 | NaN | 28.0689 | NaN | 16.4917
2563.1292 | 12.7008 | 12.4679 | 12.4884 | 12.8061 | 12.2663 | 12.5607 | 12.287 | 12.1157 | NaN | NaN | NaN | 12.5068 | 126.8588 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 516.5021 | NaN | 14.3593 | NaN | 14.7717
2564.1292 | 12.6636 | 12.3801 | 12.4845 | 12.7963 | 12.2994 | 12.5211 | 12.2601 | 12.1131 | NaN | NaN | NaN | 12.5091 | 126.2478 | NaN | NaN | NaN | -6.2849 | NaN | NaN | NaN | NaN | 522.3997 | NaN | 23.9766 | NaN | 18.6617
2565.1292 | 12.6782 | 12.3892 | 12.4865 | 12.7656 | 12.3026 | 12.5176 | 12.2623 | 12.1222 | NaN | NaN | NaN | 12.4977 | 128.8438 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 522.5568 | NaN | 27.5174 | NaN | 19.5357
2566.1292 | 12.7884 | 12.3913 | 12.4822 | 12.7711 | 12.2715 | 12.5295 | 12.2673 | 12.1191 | NaN | NaN | NaN | 12.5015 | 131.4486 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 523.9061 | NaN | 23.4785 | NaN | 18.69
2567.1292 | 12.6816 | 12.3934 | 12.4883 | 12.8084 | 12.3328 | 12.5191 | 12.2538 | 12.1185 | NaN | NaN | NaN | 12.5191 | 126.5576 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 520.7463 | NaN | 24.5425 | NaN | 18.0886
2568.1292 | 12.6879 | 12.3786 | 12.49 | 12.8822 | 12.3137 | 12.513 | 12.2577 | 12.1145 | NaN | NaN | NaN | 12.5253 | 123.5309 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 517.2916 | NaN | 21.5718 | NaN | 26.1342
2569.1292 | 12.6884 | 12.3777 | 12.4796 | 12.8126 | 12.3278 | 12.5192 | 12.2641 | 12.1208 | NaN | NaN | NaN | 12.5156 | 120.9224 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 515.1098 | NaN | 13.8065 | NaN | 18.9666
2570.1292 | 12.7018 | 12.3722 | 12.4843 | 12.8124 | 12.3441 | 12.508 | 12.2529 | 12.1282 | NaN | NaN | NaN | 12.4951 | 124.6381 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.2054 | NaN | 20.7245 | NaN | 16.3037
2571.1292 | 12.6949 | 12.4031 | 12.4787 | 12.7912 | 12.3079 | 12.5324 | 12.2601 | 12.1268 | NaN | NaN | NaN | 12.5171 | 109.3787 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 517.4322 | NaN | 24.1822 | NaN | 29.37
2572.1292 | 12.7083 | 12.3948 | 12.4876 | 12.7555 | 12.3213 | 12.5292 | 12.2602 | 12.1298 | NaN | NaN | NaN | 12.5532 | 119.0785 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 520.2771 | NaN | 15.2106 | NaN | 16.914
2573.1292 | 12.7744 | 12.3685 | 12.4852 | 12.8511 | 12.318 | 12.5232 | 12.2616 | 12.13 | NaN | NaN | NaN | 12.5265 | 125.4579 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.0679 | NaN | 34.1573 | NaN | 14.2282
2574.1292 | 12.7377 | 12.3581 | 12.4864 | 12.8213 | 12.3104 | 12.4982 | 12.2507 | 12.1324 | NaN | NaN | NaN | 12.5287 | 121.0482 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 521.4763 | NaN | 20.3739 | NaN | 16.5394
2575.1292 | 12.759 | 12.3618 | 12.4836 | 12.815 | 12.2964 | 12.5145 | 12.2589 | 12.1354 | NaN | NaN | NaN | 12.5173 | 128.3142 | NaN | NaN | NaN | -6.6392 | NaN | NaN | NaN | NaN | 521.2235 | NaN | 19.8325 | NaN | 18.4159
2576.1448 | 12.7248 | 12.3528 | 12.4802 | 12.8206 | 12.3375 | 12.4902 | 12.2481 | 12.1309 | NaN | NaN | NaN | 12.5105 | 128.3647 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 516.7303 | NaN | 17.0078 | NaN | 13.8357
2577.1292 | 12.6673 | 12.3638 | 12.4883 | 12.8116 | 12.3123 | 12.506 | 12.2507 | 12.1288 | NaN | NaN | NaN | 12.5129 | 121.908 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 516.4281 | NaN | 12.7237 | NaN | 16.9426
2578.1292 | 12.6404 | 12.3581 | 12.4857 | 12.7632 | 12.2806 | 12.5063 | 12.2515 | 12.1253 | NaN | NaN | NaN | 12.5347 | 112.865 | NaN | NaN | NaN | -8.6737 | NaN | NaN | NaN | NaN | 517.1156 | NaN | 11.4817 | NaN | 18.2194
2579.1292 | 12.798 | 12.3425 | 12.4851 | 12.8351 | 12.3611 | 12.4895 | 12.2509 | 12.1185 | NaN | NaN | NaN | 12.5126 | 117.6711 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 514.614 | NaN | 19.5754 | NaN | 17.5514
2580.1292 | 12.6715 | 12.3436 | 12.4896 | 12.8183 | 12.2787 | 12.4973 | 12.2544 | 12.1172 | NaN | NaN | NaN | 12.5261 | 125.7268 | NaN | NaN | NaN | -10.7124 | NaN | NaN | NaN | NaN | 514.4783 | NaN | 27.6089 | NaN | 16.8067
2581.1292 | 12.6572 | 12.359 | 12.4901 | 12.8036 | 12.347 | 12.5005 | 12.2647 | 12.1237 | NaN | NaN | NaN | 12.541 | 126.2259 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 513.8652 | NaN | 34.8637 | NaN | 18.9033
2582.1292 | 12.6615 | 12.4243 | 12.4818 | 12.805 | 12.3482 | 12.5255 | 12.2728 | 12.1213 | NaN | NaN | NaN | 12.5033 | 123.3264 | NaN | NaN | NaN | -15.988 | NaN | NaN | NaN | NaN | 514.1093 | NaN | 11.3108 | NaN | 16.423
2583.1292 | 12.6476 | 12.3436 | 12.485 | 12.8054 | 12.3357 | 12.4975 | 12.2589 | 12.1224 | NaN | NaN | NaN | 12.5227 | 130.6116 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 512.3374 | NaN | 18.4885 | NaN | 15.0734
2584.1292 | 12.6647 | 12.3619 | 12.4878 | 12.7946 | 12.3251 | 12.5081 | 12.2621 | 12.1197 | NaN | NaN | NaN | 12.5079 | 127.9087 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 512.2425 | NaN | 15.6721 | NaN | 17.2714
2585.1292 | 12.6471 | 12.3426 | 12.4914 | 12.8504 | 12.298 | 12.4772 | 12.2517 | 12.114 | NaN | NaN | NaN | 12.5814 | 133.3497 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 513.1413 | NaN | 20.6749 | NaN | 15.7863
2586.1292 | 12.6539 | 12.3461 | 12.4902 | 12.8167 | 12.3108 | 12.4897 | 12.2528 | 12.1183 | NaN | NaN | NaN | 12.5245 | 121.2695 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 511.6354 | NaN | 16.8479 | NaN | 16.9373
2587.1292 | 12.6577 | 12.3759 | 12.4854 | 12.7826 | 12.3193 | 12.516 | 12.2597 | 12.1166 | NaN | NaN | NaN | 12.5324 | 123.0725 | NaN | NaN | NaN | -2.7668 | NaN | NaN | NaN | NaN | 510.9193 | NaN | 21.4653 | NaN | 15.7183
2588.1292 | 12.6568 | 12.3858 | 12.4922 | 12.8025 | 12.2901 | 12.5029 | 12.2574 | 12.1145 | NaN | NaN | NaN | 12.5277 | 136.6689 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 513.4561 | NaN | 16.6481 | NaN | 18.9288
2589.1292 | 12.6555 | 12.3386 | 12.4972 | 12.7973 | 12.2751 | 12.5056 | 12.2656 | 12.1169 | NaN | NaN | NaN | 12.5454 | 126.101 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 515.2195 | NaN | 17.5784 | NaN | 16.7343
2590.1292 | 12.656 | 12.3995 | 12.4933 | 12.8024 | 12.3382 | 12.5191 | 12.2597 | 12.1142 | NaN | NaN | NaN | 12.54 | 131.5826 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 515.1841 | NaN | 19.1022 | NaN | 14.3832
2591.1292 | 12.6562 | 12.351 | 12.5028 | 12.8114 | 12.2945 | 12.5002 | 12.2599 | 12.1208 | NaN | NaN | NaN | 12.5173 | 119.6236 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 514.599 | NaN | 29.8155 | NaN | 15.1636
2592.1292 | 12.662 | 12.3452 | 12.5012 | 12.8001 | 12.3445 | 12.4964 | 12.2605 | 12.1221 | NaN | NaN | NaN | 12.5334 | 124.6066 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.3879 | NaN | 27.712 | NaN | 17.279
2593.1292 | 12.6571 | 12.3481 | 12.5029 | 12.8438 | 12.3068 | 12.5008 | 12.2567 | 12.1233 | NaN | NaN | NaN | 12.5435 | 129.0377 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 513.85 | NaN | 17.401 | NaN | 15.9941
2594.1292 | 12.6482 | 12.3857 | 12.5005 | 12.8239 | 12.2924 | 12.5153 | 12.2672 | 12.124 | NaN | NaN | NaN | 12.5329 | 125.5714 | NaN | NaN | NaN | -1.4809 | NaN | NaN | NaN | NaN | 511.7884 | NaN | 25.3626 | NaN | 16.861
2595.1292 | 12.6544 | 12.3203 | 12.4956 | 12.8251 | 12.3563 | 12.4861 | 12.2575 | 12.1201 | NaN | NaN | NaN | 12.5562 | 128.37 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 511.2196 | NaN | 20.8005 | NaN | 15.6533
2596.1292 | 12.679 | 12.3273 | 12.4984 | 12.86 | 12.3796 | 12.4898 | 12.2471 | 12.1171 | NaN | NaN | NaN | 12.5664 | 126.0634 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 511.9324 | NaN | 15.6874 | NaN | 17.4051
2597.1292 | 12.6132 | 12.3777 | 12.5027 | 12.7797 | 12.3248 | 12.5183 | 12.2632 | 12.1148 | NaN | NaN | NaN | 12.5177 | 139.1358 | NaN | NaN | NaN | -0.1248 | NaN | NaN | NaN | NaN | 515.4712 | NaN | 27.8714 | NaN | 16.264
2598.1292 | 12.6108 | 12.3238 | 12.5034 | 12.7923 | 12.3498 | 12.4954 | 12.2608 | 12.1167 | NaN | NaN | NaN | 12.5502 | 122.2555 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 517.3734 | NaN | 23.7427 | NaN | 17.028
2599.1292 | 12.6231 | 12.3833 | 12.505 | 12.8065 | 12.3499 | 12.5105 | 12.2616 | 12.1194 | NaN | NaN | NaN | 12.5183 | 126.3756 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 517.7362 | NaN | 13.6729 | NaN | 19.3673
2600.1292 | 12.6367 | 12.3544 | 12.5006 | 12.8305 | 12.3296 | 12.4938 | 12.2466 | 12.1218 | NaN | NaN | NaN | 12.5209 | 118.7635 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 513.4959 | NaN | 21.1689 | NaN | 20.3569
2601.1292 | 12.642 | 12.405 | 12.5021 | 12.8201 | 12.2564 | 12.5317 | 12.2666 | 12.124 | NaN | NaN | NaN | 12.5513 | 120.8354 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 516.7027 | NaN | 12.4957 | NaN | 15.3172
2602.1292 | 12.6603 | 12.3522 | 12.5011 | 12.8229 | 12.3673 | 12.4947 | 12.2618 | 12.1215 | NaN | NaN | NaN | 12.5168 | 129.3986 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 516.1057 | NaN | 31.6137 | NaN | 15.9735
2603.1292 | 12.7241 | 12.3153 | 12.4983 | 12.8053 | 12.3382 | 12.478 | 12.2552 | 12.1209 | NaN | NaN | NaN | 12.5358 | 114.8498 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 517.2576 | NaN | 21.7544 | NaN | 13.7291
2604.1292 | 12.6589 | 12.3037 | 12.5026 | 12.8306 | 12.3003 | 12.4921 | 12.2602 | 12.1183 | NaN | NaN | NaN | 12.5341 | 116.6305 | NaN | NaN | NaN | 2.6567 | NaN | NaN | NaN | NaN | 517.6804 | NaN | 25.004 | NaN | 17.2679
2605.1292 | 12.6523 | 12.287 | 12.5058 | 12.8278 | 12.307 | 12.481 | 12.2536 | 12.1198 | NaN | NaN | NaN | 12.5401 | 130.4949 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 516.6756 | NaN | 11.5227 | NaN | 16.7221
2606.1292 | 12.6489 | 12.3616 | 12.5026 | 12.7943 | 12.3597 | 12.5081 | 12.2714 | 12.1192 | NaN | NaN | NaN | 12.5675 | 122.5106 | NaN | NaN | NaN | -5.8764 | NaN | NaN | NaN | NaN | 515.4213 | NaN | 14.1495 | NaN | 17.4811
2607.1292 | 12.6557 | 12.3283 | 12.5067 | 12.8018 | 12.3775 | 12.4908 | 12.2622 | 12.1124 | NaN | NaN | NaN | 12.5366 | 118.9132 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -10.7115 | 514.7652 | NaN | 10.932 | NaN | 16.5142
2608.1292 | 12.6663 | 12.3015 | 12.506 | 12.7987 | 12.3242 | 12.4781 | 12.2567 | 12.1135 | NaN | NaN | NaN | 12.5554 | 125.1135 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 516.3023 | NaN | 35.4442 | NaN | 17.0762
2609.1292 | 12.6614 | 12.2954 | 12.5056 | 12.8471 | 12.346 | 12.4865 | 12.2594 | 12.1093 | NaN | NaN | NaN | 12.5139 | 124.5658 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 516.1903 | NaN | 12.3269 | NaN | 15.5521
2610.1292 | 12.6934 | 12.2873 | 12.518 | 12.8372 | 12.3713 | 12.4598 | 12.253 | 12.1101 | NaN | NaN | NaN | 12.5295 | 123.3252 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 513.192 | NaN | 21.7993 | NaN | 17.3436
2611.1292 | 12.6567 | 12.2995 | 12.5123 | 12.8221 | 12.3914 | 12.4784 | 12.257 | 12.1151 | NaN | NaN | NaN | 12.5703 | 119.7677 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 512.5895 | NaN | 22.6946 | NaN | 14.9609
2612.1292 | 12.6792 | 12.2964 | 12.5087 | 12.8322 | 12.3561 | 12.473 | 12.2539 | 12.1137 | NaN | NaN | NaN | 12.5648 | 138.0587 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 510.7064 | NaN | 8.1345 | NaN | 17.3765
2613.1292 | 12.6534 | 12.294 | 12.5166 | 12.8224 | 12.3849 | 12.4737 | 12.2575 | 12.1191 | NaN | NaN | NaN | 12.5388 | 110.2248 | NaN | NaN | NaN | 0.3272 | NaN | NaN | NaN | NaN | 506.2159 | NaN | 22.3331 | NaN | 16.5062
2614.1292 | 12.6706 | 12.3337 | 12.5141 | 12.8251 | 12.2731 | 12.5015 | 12.2674 | 12.1185 | NaN | NaN | NaN | 12.537 | 117.8353 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 511.0689 | NaN | 17.8306 | NaN | 13.6953
2615.1292 | 12.6163 | 12.3016 | 12.5151 | 12.8131 | 12.3563 | 12.4873 | 12.263 | 12.1208 | NaN | NaN | NaN | 12.55 | 126.4565 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 509.5472 | NaN | 27.869 | NaN | 17.0816
2616.1292 | 12.617 | 12.3264 | 12.5139 | 12.8088 | 12.3584 | 12.4887 | 12.2658 | 12.1215 | NaN | NaN | NaN | 12.5473 | 135.6056 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 505.4645 | NaN | 28.8001 | NaN | 14.7927
2617.1292 | 12.629 | 12.2847 | 12.5165 | 12.8262 | 12.3775 | 12.4801 | 12.2589 | 12.1234 | NaN | NaN | NaN | 12.5488 | 122.969 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 510.6931 | NaN | 24.0712 | NaN | 17.0104
2618.1448 | 12.65 | 12.2725 | 12.5127 | 12.8331 | 12.3286 | 12.4839 | 12.2606 | 12.121 | NaN | NaN | NaN | 12.5378 | 130.0496 | NaN | NaN | NaN | -11.5059 | NaN | NaN | NaN | NaN | 509.5014 | NaN | 23.1593 | NaN | 16.1819
2619.1292 | 12.6527 | 12.3633 | 12.5174 | 12.8275 | 12.389 | 12.5122 | 12.2755 | 12.1199 | NaN | NaN | NaN | 12.5539 | 134.9541 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 510.9805 | NaN | 8.8442 | NaN | 13.6652
2620.1292 | 12.6473 | 12.2777 | 12.5184 | 12.8145 | 12.3386 | 12.4822 | 12.256 | 12.1265 | NaN | NaN | NaN | 12.5349 | 129.0902 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 510.9061 | NaN | 20.8326 | NaN | 16.0372
2621.1292 | 12.6554 | 12.3023 | 12.5172 | 12.8473 | 12.3696 | 12.4884 | 12.2693 | 12.1238 | NaN | NaN | NaN | 12.5559 | 120.2351 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 504.6473 | NaN | 19.6128 | NaN | 17.4797
2622.1292 | 12.6691 | 12.2907 | 12.5233 | 12.8007 | 12.3499 | 12.4932 | 12.2656 | 12.116 | NaN | NaN | NaN | 12.5235 | 120.953 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 510.8629 | NaN | 24.6951 | NaN | 16.7826
2623.1292 | 12.6687 | 12.3454 | 12.5205 | 12.8313 | 12.2695 | 12.5074 | 12.2624 | 12.1238 | NaN | NaN | NaN | 12.5637 | 121.65 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 512.2451 | NaN | 17.2677 | NaN | 17.5239
2624.1292 | 12.6814 | 12.3425 | 12.5224 | 12.8268 | 12.3705 | 12.5088 | 12.2726 | 12.1271 | NaN | NaN | NaN | 12.5506 | 122.9474 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 513.4419 | NaN | 32.4205 | NaN | 17.2993
2625.1292 | 12.6603 | 12.2909 | 12.5202 | 12.836 | 12.3 | 12.4858 | 12.2694 | 12.1253 | NaN | NaN | NaN | 12.5419 | 121.7303 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 511.4534 | NaN | 16.4114 | NaN | 16.2814
2626.1292 | 12.6601 | 12.4187 | 12.5145 | 12.8261 | 12.2313 | 12.5788 | 12.3189 | 12.1245 | NaN | NaN | NaN | 12.5554 | 126.8582 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 514.0861 | NaN | 13.836 | NaN | 13.3627
2627.1292 | 12.6601 | 12.2976 | 12.5173 | 12.8201 | 12.3212 | 12.499 | 12.2714 | 12.1197 | NaN | NaN | NaN | 12.5601 | 116.541 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 511.3301 | NaN | 15.1769 | NaN | 16.4689
2628.1292 | 12.7644 | 12.3576 | 12.5174 | 12.7839 | 12.34 | 12.5077 | 12.2875 | 12.1205 | NaN | NaN | NaN | 12.594 | 125.358 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -19.7047 | 510.9954 | NaN | 26.4354 | NaN | 17.4177
2629.1292 | 12.6752 | 12.317 | 12.5076 | 12.8488 | 12.2822 | 12.4922 | 12.2696 | 12.1269 | NaN | NaN | NaN | 12.5833 | 121.1068 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 511.3818 | NaN | 18.8439 | NaN | 15.5982
2630.1292 | 12.6722 | 12.4187 | 12.5146 | 12.8791 | 12.3601 | 12.5512 | 12.3037 | 12.1339 | NaN | NaN | NaN | 12.5776 | 123.0908 | NaN | NaN | NaN | 2.3536 | NaN | NaN | NaN | NaN | 512.0118 | NaN | 22.1172 | NaN | 17.2946
2631.1292 | 12.6956 | 12.3441 | 12.5182 | 12.882 | 12.3775 | 12.5049 | 12.2847 | 12.1303 | NaN | NaN | NaN | 12.5583 | 111.9526 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 511.8753 | NaN | 7.1986 | NaN | 17.4739
2632.1292 | 12.693 | 12.3255 | 12.5154 | 12.8353 | 12.326 | 12.5023 | 12.2816 | 12.132 | NaN | NaN | NaN | 12.5703 | 123.1451 | NaN | NaN | NaN | -7.247 | NaN | NaN | NaN | NaN | 514.3245 | NaN | 35.0128 | NaN | 16.3996
2633.1448 | 12.7139 | 12.282 | 12.5203 | 12.8533 | 12.3937 | 12.4693 | 12.2734 | 12.1312 | NaN | NaN | NaN | 12.5838 | 119.4718 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -16.6231 | 513.3942 | NaN | 30.8413 | NaN | 17.4579
2634.1292 | 12.725 | 12.276 | 12.5172 | 12.8547 | 12.318 | 12.4745 | 12.2688 | 12.1338 | NaN | NaN | NaN | 12.5475 | 123.3589 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 510.7939 | NaN | 28.5664 | NaN | 16.2979
2635.1292 | 12.7064 | 12.3146 | 12.5174 | 12.8535 | 12.3888 | 12.484 | 12.2796 | 12.1254 | NaN | NaN | NaN | 12.5401 | 117.5626 | NaN | NaN | NaN | 4.1566 | NaN | NaN | NaN | NaN | 512.4409 | NaN | 21.9689 | NaN | 16.118
2636.1292 | 12.6812 | 12.3899 | 12.5173 | 12.86 | 12.2691 | 12.5407 | 12.2978 | 12.1248 | NaN | NaN | NaN | 12.5469 | 117.9221 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 512.7969 | NaN | 23.2693 | NaN | 13.8033
2637.1292 | 12.6868 | 12.315 | 12.5197 | 12.8348 | 12.2587 | 12.4877 | 12.2876 | 12.1292 | NaN | NaN | NaN | 12.5164 | 116.5234 | NaN | NaN | NaN | -17.2812 | NaN | NaN | NaN | NaN | 515.5625 | NaN | 20.8317 | NaN | 15.2345
2638.1292 | 12.694 | 12.3852 | 12.5179 | 12.8361 | 12.3306 | 12.5098 | 12.2972 | 12.1278 | NaN | NaN | NaN | 12.5639 | 111.9545 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 514.2015 | NaN | 10.4226 | NaN | 16.9338
2639.1292 | 12.7168 | 12.3329 | 12.5209 | 12.811 | 12.3229 | 12.4909 | 12.2871 | 12.127 | NaN | NaN | NaN | 12.5374 | 124.1131 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 513.4353 | NaN | 20.354 | NaN | 14.7417
2640.1292 | 12.7748 | 12.3105 | 12.5226 | 12.8356 | 12.2883 | 12.4911 | 12.295 | 12.1299 | NaN | NaN | NaN | 12.536 | 129.4772 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 513.1486 | NaN | 22.3343 | NaN | 15.8173
2641.1292 | 12.7521 | 12.3384 | 12.5266 | 12.9488 | 12.2374 | 12.4921 | 12.2759 | 12.1297 | NaN | NaN | NaN | 12.5235 | 121.2351 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 516.4464 | NaN | 18.3356 | NaN | 16.1281
2642.1292 | 12.6918 | 12.3867 | 12.5245 | 12.8695 | 12.3724 | 12.5069 | 12.29 | 12.1323 | NaN | NaN | NaN | 12.5463 | 126.6651 | NaN | NaN | NaN | -18.4394 | NaN | NaN | NaN | NaN | 516.8217 | NaN | 35.0695 | NaN | 16.9211
2643.1292 | 12.6919 | 12.4118 | 12.5213 | 12.8168 | 12.3335 | 12.5371 | 12.3068 | 12.1322 | NaN | NaN | NaN | 12.5165 | 127.5903 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 519.5639 | NaN | 17.4726 | NaN | 15.1434
2644.1292 | 12.697 | 12.3231 | 12.5223 | 12.8159 | 12.3679 | 12.4839 | 12.2775 | 12.1275 | NaN | NaN | NaN | 12.5366 | 132.5471 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 520.7296 | NaN | 28.5601 | NaN | 13.6455
2645.1292 | 12.6932 | 12.4126 | 12.5204 | 12.7561 | 12.3847 | 12.5181 | 12.2845 | 12.1304 | NaN | NaN | NaN | 12.549 | 136.3323 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 520.8473 | NaN | 26.3217 | NaN | 16.4701
2646.1292 | 12.6956 | 12.3536 | 12.5068 | 12.8152 | 12.2448 | 12.5135 | 12.2875 | 12.1272 | NaN | NaN | NaN | 12.5077 | 124.7504 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 521.6377 | NaN | 26.6598 | NaN | 17.4936
2647.1292 | 12.7065 | 12.3529 | 12.5056 | 12.7637 | 12.3307 | 12.4961 | 12.2828 | 12.121 | NaN | NaN | NaN | 12.5493 | 122.3015 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 519.3302 | NaN | 18.5147 | NaN | 16.955
2648.1292 | 12.7056 | 12.3403 | 12.5029 | 12.8231 | 12.3348 | 12.4891 | 12.2787 | 12.1239 | NaN | NaN | NaN | 12.5228 | 135.8545 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 520.6066 | NaN | 24.0121 | NaN | 13.4775
2649.1292 | 12.7304 | 12.4571 | 12.4977 | 12.9077 | 12.3369 | 12.534 | 12.3009 | 12.1191 | NaN | NaN | NaN | 12.6053 | 124.023 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 524.1149 | NaN | 23.4898 | NaN | 17.1025
2650.1292 | 12.7109 | 12.354 | 12.4878 | 12.8568 | 12.3769 | 12.5029 | 12.2931 | 12.1221 | NaN | NaN | NaN | 12.5143 | 118.5483 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 524.2597 | NaN | 24.124 | NaN | 16.2053
2651.1292 | 12.7272 | 12.4022 | 12.4836 | 12.7879 | 12.3237 | 12.5435 | 12.3111 | 12.1276 | NaN | NaN | NaN | 12.5551 | 121.2374 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 521.9475 | NaN | 17.8957 | NaN | 17.8515
2652.1292 | 12.759 | 12.3588 | 12.4834 | 12.7959 | 12.3672 | 12.5061 | 12.2935 | 12.1215 | NaN | NaN | NaN | 12.5289 | 117.96 | NaN | NaN | NaN | 1.2579 | NaN | NaN | NaN | NaN | 524.0342 | NaN | 24.8541 | NaN | 18.1108
2653.1292 | 12.6881 | 12.344 | 12.4783 | 12.7712 | 12.3003 | 12.4943 | 12.286 | 12.1202 | NaN | NaN | NaN | 12.5446 | 125.7477 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 521.5451 | NaN | 21.2833 | NaN | 14.3183
2654.1292 | 12.7 | 12.3562 | 12.4711 | 12.7407 | 12.2609 | 12.5134 | 12.2937 | 12.1233 | NaN | NaN | NaN | 12.538 | 122.6658 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 523.2003 | NaN | 32.709 | NaN | 16.4809
2655.1292 | 12.7071 | 12.3881 | 12.4687 | 12.8237 | 12.2769 | 12.5105 | 12.2917 | 12.1252 | NaN | NaN | NaN | 12.5047 | 119.8637 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 517.3352 | NaN | 20.6466 | NaN | 16.0697
2656.1292 | 12.7148 | 12.44 | 12.4705 | 12.8326 | 12.351 | 12.5314 | 12.3066 | 12.1248 | NaN | NaN | NaN | 12.5003 | 118.3852 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 517.9983 | NaN | 31.484 | NaN | 16.3084
2657.1292 | 12.6932 | 12.3506 | 12.4772 | 12.8005 | 12.3527 | 12.4975 | 12.2816 | 12.1208 | NaN | NaN | NaN | 12.5316 | 125.3562 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 517.2881 | NaN | 11.6706 | NaN | 15.922
2658.1292 | 12.7619 | 12.3376 | 12.4774 | 12.794 | 12.2624 | 12.497 | 12.283 | 12.1246 | NaN | NaN | NaN | 12.5192 | 119.9238 | NaN | NaN | NaN | -1.994 | NaN | NaN | NaN | NaN | 517.6809 | NaN | 28.073 | NaN | 16.0436
2659.1292 | 12.708 | 12.3346 | 12.4842 | 12.7733 | 12.3549 | 12.494 | 12.2783 | 12.1244 | NaN | NaN | NaN | 12.5064 | 126.3458 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 520.0496 | NaN | 23.2543 | NaN | 14.0697
2660.1292 | 12.7144 | 12.5333 | 12.4896 | 12.8539 | 12.3257 | 12.566 | 12.3145 | 12.1282 | NaN | NaN | NaN | 12.5125 | 127.2801 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 522.5557 | NaN | 13.3244 | NaN | 14.4382
2661.1292 | 12.8024 | 12.3412 | 12.4817 | 12.7634 | 12.3338 | 12.4912 | 12.2703 | 12.1257 | NaN | NaN | NaN | 12.5031 | 130.4498 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 520.8517 | NaN | 16.5689 | NaN | 14.6885
2662.1292 | 12.6773 | 12.37 | 12.4895 | 12.7603 | 12.3056 | 12.522 | 12.2798 | 12.1317 | NaN | NaN | NaN | 12.5139 | 131.8122 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 521.6896 | NaN | 16.2754 | NaN | 15.4427
2663.1292 | 12.7575 | 12.3597 | 12.4921 | 12.7588 | 12.232 | 12.5093 | 12.2841 | 12.1352 | NaN | NaN | NaN | 12.4895 | 119.231 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 520.6338 | NaN | 11.7714 | NaN | 16.8891
2664.1292 | 12.7023 | 12.3227 | 12.4916 | 12.7752 | 12.3084 | 12.493 | 12.2654 | 12.1295 | NaN | NaN | NaN | 12.519 | 120.9988 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 523.2968 | NaN | 24.3231 | NaN | 16.0373
2665.1292 | 12.7229 | 12.3221 | 12.4933 | 12.7674 | 12.2727 | 12.496 | 12.2693 | 12.1317 | NaN | NaN | NaN | 12.5268 | 125.1938 | NaN | NaN | NaN | -12.412 | NaN | NaN | NaN | NaN | 520.4333 | NaN | 28.2327 | NaN | 15.2658
2666.1292 | 12.7101 | 12.3596 | 12.4989 | 12.779 | 12.3111 | 12.5204 | 12.282 | 12.1263 | NaN | NaN | NaN | 12.5077 | 128.6959 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 522.1351 | NaN | 12.9673 | NaN | 15.7744
2667.1448 | 12.7122 | 12.3603 | 12.501 | 12.7849 | 12.3577 | 12.5078 | 12.2832 | 12.1253 | NaN | NaN | NaN | 12.5082 | 123.4025 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 522.2794 | NaN | 29.3061 | NaN | 15.996
2668.1292 | 12.7199 | 12.3231 | 12.4962 | 12.8126 | 12.3646 | 12.4963 | 12.2634 | 12.1258 | NaN | NaN | NaN | 12.5096 | 132.7211 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 519.0386 | NaN | 14.0699 | NaN | 16.2116
2669.1292 | 12.7164 | 12.3575 | 12.4992 | 12.7628 | 12.364 | 12.5212 | 12.2783 | 12.1251 | NaN | NaN | NaN | 12.5088 | 127.4313 | NaN | NaN | NaN | 11.0173 | NaN | NaN | NaN | NaN | 523.1682 | NaN | 14.9852 | NaN | 16.1815
2670.1292 | 12.7168 | 12.3512 | 12.5001 | 12.7401 | 12.2469 | 12.513 | 12.2656 | 12.122 | NaN | NaN | NaN | 12.5142 | 127.7903 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 522.535 | NaN | 20.7698 | NaN | 15.0468
2671.1292 | 12.7157 | 12.3147 | 12.5019 | 12.7915 | 12.3547 | 12.4969 | 12.2636 | 12.1238 | NaN | NaN | NaN | 12.5441 | 131.8618 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 523.0065 | NaN | 31.584 | NaN | 15.8336
2672.1448 | 12.7184 | 12.315 | 12.4946 | 12.7639 | 12.3336 | 12.4908 | 12.2629 | 12.1286 | NaN | NaN | NaN | 12.5383 | 130.1892 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 520.8454 | NaN | 16.3504 | NaN | 16.5283
2673.1292 | 12.795 | 12.3159 | 12.491 | 12.7613 | 12.2777 | 12.4975 | 12.2639 | 12.1244 | NaN | NaN | NaN | 12.5282 | 122.2092 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 519.3725 | NaN | 27.6018 | NaN | 16.5162
2674.1292 | 12.7229 | 12.3509 | 12.4995 | 12.7645 | 12.3654 | 12.4978 | 12.2757 | 12.1254 | NaN | NaN | NaN | 12.5298 | 120.0056 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 522.4901 | NaN | 15.3637 | NaN | 12.3214
2675.1448 | 12.6918 | 12.3818 | 12.498 | 12.7582 | 12.2978 | 12.525 | 12.2768 | 12.1172 | NaN | NaN | NaN | 12.5087 | 126.4753 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 522.3921 | NaN | 21.4192 | NaN | 16.3616
2676.1292 | 12.746 | 12.4365 | 12.5004 | 12.7409 | 12.344 | 12.5513 | 12.2943 | 12.1218 | NaN | NaN | NaN | 12.5594 | 131.5716 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 523.0545 | NaN | 18.4651 | NaN | 14.0327
2677.1292 | 12.6906 | 12.3746 | 12.4956 | 12.8138 | 12.3661 | 12.5259 | 12.2806 | 12.1179 | NaN | NaN | NaN | 12.5051 | 124.4291 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 523.5604 | NaN | 19.1891 | NaN | 15.5178
2678.1292 | 12.6728 | 12.3571 | 12.4993 | 12.7631 | 12.369 | 12.5103 | 12.2684 | 12.1283 | NaN | NaN | NaN | 12.6016 | 117.0085 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 522.7308 | NaN | 27.674 | NaN | 15.4415
2679.1292 | 12.6949 | 12.3239 | 12.493 | 12.769 | 12.3692 | 12.4909 | 12.26 | 12.1257 | NaN | NaN | NaN | 12.5441 | 132.2224 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 519.8213 | NaN | 13.9318 | NaN | 14.4178
2680.1292 | 12.7086 | 12.4027 | 12.4909 | 12.7471 | 12.2733 | 12.5384 | 12.2874 | 12.1207 | NaN | NaN | NaN | 12.5284 | 132.6488 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 519.7673 | NaN | 31.6692 | NaN | 20.352
2681.1292 | 12.711 | 12.3009 | 12.4893 | 12.7816 | 12.3624 | 12.4856 | 12.257 | 12.1279 | NaN | NaN | NaN | 12.5235 | 120.2403 | NaN | NaN | NaN | -18.8632 | NaN | NaN | NaN | NaN | 521.5299 | NaN | 22.1341 | NaN | 16.0983
2682.1292 | 12.705 | 12.3457 | 12.4964 | 12.848 | 12.3237 | 12.5117 | 12.2712 | 12.1274 | NaN | NaN | NaN | 12.5313 | 120.2698 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 524.6011 | NaN | 18.9555 | NaN | 16.6786
2683.1292 | 12.7052 | 12.3846 | 12.4962 | 12.7703 | 12.349 | 12.537 | 12.2796 | 12.1183 | NaN | NaN | NaN | 12.5048 | 122.5202 | NaN | NaN | NaN | 6.0072 | NaN | NaN | NaN | NaN | 523.5514 | NaN | 17.1082 | NaN | 15.5475
2684.1292 | 12.7158 | 12.3591 | 12.496 | 12.7734 | 12.2691 | 12.5323 | 12.2765 | 12.1198 | NaN | NaN | NaN | 12.5122 | 118.468 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 526.2175 | NaN | 21.79 | NaN | 16.1204
2685.1292 | 12.7226 | 12.3659 | 12.4992 | 12.7769 | 12.2905 | 12.5372 | 12.2826 | 12.1202 | NaN | NaN | NaN | 12.531 | 127.2582 | NaN | NaN | NaN | -16.2908 | NaN | NaN | NaN | NaN | 522.4339 | NaN | 21.2311 | NaN | 15.8319
2686.1292 | 12.7439 | 12.4079 | 12.504 | 12.7807 | 12.3459 | 12.5313 | 12.2836 | 12.1147 | NaN | NaN | NaN | 12.5961 | 118.6171 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 524.3251 | NaN | 12.4495 | NaN | 15.5982
2687.1292 | 12.7434 | 12.328 | 12.5045 | 12.7805 | 12.3232 | 12.5088 | 12.2702 | 12.1223 | NaN | NaN | NaN | 12.5265 | 127.7326 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 525.3716 | NaN | 19.3122 | NaN | 12.5387
2688.1292 | 12.7235 | 12.3289 | 12.5075 | 12.7902 | 12.3444 | 12.5183 | 12.2776 | 12.1244 | NaN | NaN | NaN | 12.5207 | 125.2588 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 524.9469 | NaN | 17.9056 | NaN | 16.1734
2689.1292 | 12.7256 | 12.3471 | 12.4991 | 12.7947 | 12.2698 | 12.5259 | 12.2815 | 12.1238 | NaN | NaN | NaN | 12.5423 | 131.2442 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 526.3071 | NaN | 28.7616 | NaN | 16.1352
2690.1292 | 12.7209 | 12.3277 | 12.4994 | 12.7761 | 12.3675 | 12.5076 | 12.2678 | 12.1277 | NaN | NaN | NaN | 12.5421 | 124.424 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 524.8456 | NaN | 27.4939 | NaN | 16.7829
2691.1292 | 12.7215 | 12.3533 | 12.5053 | 12.783 | 12.3593 | 12.5108 | 12.2794 | 12.1281 | NaN | NaN | NaN | 12.5411 | 123.1719 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 524.3599 | NaN | 30.5064 | NaN | 16.8192
2692.1292 | 12.726 | 12.3628 | 12.5033 | 12.7822 | 12.3142 | 12.5277 | 12.28 | 12.1212 | NaN | NaN | NaN | 12.5461 | 121.0613 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 522.7122 | NaN | 21.3207 | NaN | 14.8452
2693.1292 | 12.7246 | 12.335 | 12.5046 | 12.7673 | 12.2887 | 12.5082 | 12.2718 | 12.1141 | NaN | NaN | NaN | 12.5712 | 127.0811 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 524.8892 | NaN | 12.6421 | NaN | 14.004
2694.1292 | 12.7286 | 12.3189 | 12.509 | 12.813 | 12.3537 | 12.51 | 12.2736 | 12.1211 | NaN | NaN | NaN | 12.5561 | 122.5751 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 527.1937 | NaN | 28.3026 | NaN | 16.5175
2695.1292 | 12.7304 | 12.3274 | 12.5073 | 12.7914 | 12.3486 | 12.5097 | 12.2799 | 12.1191 | NaN | NaN | NaN | 12.5905 | 124.9046 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 523.2475 | NaN | 9.6431 | NaN | 14.1001
2696.1292 | 12.7441 | 12.3284 | 12.5083 | 12.8272 | 12.2914 | 12.5231 | 12.2743 | 12.119 | NaN | NaN | NaN | 12.5183 | 125.7664 | NaN | NaN | NaN | -3.6747 | NaN | NaN | NaN | NaN | 526.4436 | NaN | 30.5143 | NaN | 16.2591
2697.1292 | 12.7881 | 12.3655 | 12.5122 | 12.8345 | 12.3564 | 12.5332 | 12.2822 | 12.1183 | NaN | NaN | NaN | 12.5404 | 129.4865 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 517.9043 | NaN | 16.7656 | NaN | 14.6995
2698.1292 | 12.8033 | 12.3712 | 12.5117 | 12.7979 | 12.3542 | 12.5232 | 12.2731 | 12.1181 | NaN | NaN | NaN | 12.5181 | 129.1157 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 524.8298 | NaN | 6.9327 | NaN | 15.9835
2699.1292 | 12.71 | 12.384 | 12.5054 | 12.7819 | 12.3618 | 12.5274 | 12.2657 | 12.1082 | NaN | NaN | NaN | 12.5462 | 127.4681 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 522.7849 | NaN | 29.9239 | NaN | 16.1265
2700.1292 | 12.7848 | 12.3811 | 12.5054 | 12.7943 | 12.3775 | 12.5149 | 12.2642 | 12.1089 | NaN | NaN | NaN | 12.5466 | 134.2344 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 521.6978 | NaN | 20.1953 | NaN | 15.0411
2701.1292 | 12.7661 | 12.3734 | 12.5041 | 12.7758 | 12.3316 | 12.5323 | 12.2701 | 12.1119 | NaN | NaN | NaN | 12.5578 | 138.9852 | NaN | NaN | NaN | 3.9883 | NaN | NaN | NaN | NaN | 518.2876 | NaN | 36.2999 | NaN | 14.1138
2702.1292 | 12.7186 | 12.4001 | 12.512 | 12.7593 | 12.2793 | 12.5454 | 12.2751 | 12.1109 | NaN | NaN | NaN | 12.5303 | 125.0157 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 522.2758 | NaN | 22.7765 | NaN | 15.8313
2703.1292 | 12.8993 | 12.3555 | 12.5092 | 12.8512 | 12.3135 | 12.5247 | 12.2675 | 12.1122 | NaN | NaN | NaN | 12.5488 | 132.7312 | NaN | NaN | NaN | -14.8566 | NaN | NaN | NaN | NaN | 516.1188 | NaN | 13.6642 | NaN | 15.4516
2704.1292 | 12.7821 | 12.4376 | 12.512 | 12.8438 | 12.3689 | 12.5586 | 12.2811 | 12.1167 | NaN | NaN | NaN | 12.5511 | 125.6045 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 520.788 | NaN | 9.3219 | NaN | 15.5785
2705.1292 | 12.8162 | 12.3672 | 12.5129 | 12.8064 | 12.3772 | 12.5163 | 12.2598 | 12.1126 | NaN | NaN | NaN | 12.5726 | 117.1139 | NaN | NaN | NaN | 5.9788 | NaN | NaN | NaN | NaN | 519.4843 | NaN | 19.8936 | NaN | 16.7997
2706.1292 | 12.7718 | 12.3984 | 12.5215 | 12.756 | 12.3681 | 12.5427 | 12.2734 | 12.1118 | NaN | NaN | NaN | 12.5981 | 123.1186 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 522.155 | NaN | 23.1618 | NaN | 15.4325
2707.1292 | 12.7284 | 12.3691 | 12.5203 | 12.8266 | 12.3383 | 12.5528 | 12.2851 | 12.1136 | NaN | NaN | NaN | 12.5561 | 119.6584 | NaN | NaN | NaN | -2.111 | NaN | NaN | NaN | NaN | 523.2821 | NaN | 17.1462 | NaN | 14.7826
2708.1292 | 12.7472 | 12.3831 | 12.5246 | 12.8161 | 12.3187 | 12.5523 | 12.2772 | 12.1104 | NaN | NaN | NaN | 12.604 | 117.9723 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 522.5807 | NaN | 17.5686 | NaN | 15.832
2709.1292 | 12.7433 | 12.3761 | 12.5275 | 12.7763 | 12.3209 | 12.5471 | 12.2754 | 12.1141 | NaN | NaN | NaN | 12.5662 | 128.5334 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 521.6061 | NaN | 27.9355 | NaN | 15.6378
2710.1292 | 12.7519 | 12.4774 | 12.5282 | 12.8219 | 12.371 | 12.572 | 12.2866 | 12.1124 | NaN | NaN | NaN | 12.5998 | 126.9082 | NaN | NaN | NaN | -4.1809 | NaN | NaN | NaN | NaN | 520.1824 | NaN | 12.0902 | NaN | 16.1145
2711.1292 | 12.7492 | 12.4029 | 12.5327 | 12.772 | 12.3013 | 12.5559 | 12.2667 | 12.1124 | NaN | NaN | NaN | 12.5563 | 116.8145 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 525.0032 | NaN | 26.9659 | NaN | 16.3358
2712.1292 | 12.7571 | 12.398 | 12.5352 | 12.7628 | 12.3572 | 12.5629 | 12.279 | 12.1063 | NaN | NaN | NaN | 12.5331 | 129.7463 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 523.9673 | NaN | 15.561 | NaN | 14.8466
2713.1292 | 12.7807 | 12.3746 | 12.5349 | 12.8605 | 12.3108 | 12.565 | 12.2775 | 12.1126 | NaN | NaN | NaN | 12.5859 | 132.5851 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 519.6988 | NaN | 27.9116 | NaN | 14.6345
2714.1292 | 12.7779 | 12.4839 | 12.5369 | 12.8131 | 12.3026 | 12.5932 | 12.2823 | 12.1029 | NaN | NaN | NaN | 12.5476 | 114.2732 | NaN | NaN | NaN | -11.8953 | NaN | NaN | NaN | NaN | 523.8006 | NaN | 19.0076 | NaN | 16.7822
2715.1292 | 12.7596 | 12.3819 | 12.539 | 12.7881 | 12.3768 | 12.5525 | 12.268 | 12.1039 | NaN | NaN | NaN | 12.5739 | 128.2436 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 519.3939 | NaN | 9.7744 | NaN | 16.2771
2716.1292 | 12.759 | 12.4062 | 12.5326 | 12.7614 | 12.2902 | 12.5541 | 12.2616 | 12.1084 | NaN | NaN | NaN | 12.5495 | 114.0418 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 526.2203 | NaN | 27.7944 | NaN | 16.7536
2717.1292 | 12.7588 | 12.3949 | 12.5361 | 12.7554 | 12.3792 | 12.5612 | 12.2658 | 12.1072 | NaN | NaN | NaN | 12.5922 | 125.6844 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 521.5087 | NaN | 23.6249 | NaN | 14.8094
2718.1292 | 12.7494 | 12.4366 | 12.5399 | 12.7658 | 12.3405 | 12.5874 | 12.2815 | 12.1033 | NaN | NaN | NaN | 12.5363 | 132.7241 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 523.5705 | NaN | 29.8587 | NaN | 15.5116
2719.1292 | 12.7519 | 12.4617 | 12.5402 | 12.8136 | 12.3548 | 12.5992 | 12.2854 | 12.1105 | NaN | NaN | NaN | 12.5151 | 124.7553 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 522.9186 | NaN | 26.0361 | NaN | 14.5123
2720.1292 | 12.7421 | 12.364 | 12.5429 | 12.7504 | 12.3028 | 12.5658 | 12.2616 | 12.1101 | NaN | NaN | NaN | 12.5381 | 123.3885 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 526.3323 | NaN | 12.4597 | NaN | 15.296
2721.1292 | 12.7477 | 12.3858 | 12.5408 | 12.8383 | 12.2953 | 12.5781 | 12.2715 | 12.105 | NaN | NaN | NaN | 12.516 | 115.4118 | NaN | NaN | NaN | 7.8441 | NaN | NaN | NaN | NaN | 526.4327 | NaN | 11.0074 | NaN | 15.841
2722.1292 | 12.7552 | 12.4242 | 12.5392 | 12.7811 | 12.2813 | 12.5956 | 12.2694 | 12.1131 | NaN | NaN | NaN | 12.5351 | 134.3141 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 527.3898 | NaN | 13.1987 | NaN | 14.377
2723.1292 | 12.7353 | 12.4356 | 12.5379 | 12.7676 | 12.3793 | 12.5912 | 12.276 | 12.1173 | NaN | NaN | NaN | 12.5236 | 131.0423 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 526.6652 | NaN | 19.0918 | NaN | 13.7839
2724.1292 | 12.7338 | 12.3404 | 12.5314 | 12.7664 | 12.3671 | 12.567 | 12.269 | 12.109 | NaN | NaN | NaN | 12.5529 | 117.9634 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 527.1883 | NaN | 28.0067 | NaN | 16.1777
2725.1292 | 12.7305 | 12.3814 | 12.535 | 12.7714 | 12.3709 | 12.5721 | 12.27 | 12.1116 | NaN | NaN | NaN | 12.5615 | 117.0217 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 523.7478 | NaN | 17.2377 | NaN | 15.5339
2726.1292 | 12.7294 | 12.3836 | 12.5256 | 12.8066 | 12.3297 | 12.5743 | 12.2755 | 12.1121 | NaN | NaN | NaN | 12.5313 | 123.2364 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 524.5987 | NaN | 12.1617 | NaN | 16.2049
2727.1292 | 12.7359 | 12.4069 | 12.5278 | 12.7793 | 12.348 | 12.589 | 12.2821 | 12.1073 | NaN | NaN | NaN | 12.6061 | 128.9589 | NaN | NaN | NaN | 3.0034 | NaN | NaN | NaN | NaN | 524.0957 | NaN | 20.7708 | NaN | 14.9943
2728.1292 | 12.7395 | 12.3603 | 12.5266 | 12.779 | 12.3787 | 12.5648 | 12.283 | 12.1093 | NaN | NaN | NaN | 12.5347 | 122.0807 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 527.3426 | NaN | 25.1376 | NaN | 16.3694
2729.1292 | 12.7882 | 12.3709 | 12.5269 | 12.7693 | 12.3432 | 12.5611 | 12.2779 | 12.1021 | NaN | NaN | NaN | 12.5262 | 118.3742 | NaN | NaN | NaN | -19.1921 | NaN | NaN | NaN | NaN | 527.1709 | NaN | 21.5435 | NaN | 15.8236
2730.1292 | 12.7201 | 12.3991 | 12.5189 | 12.7698 | 12.2426 | 12.579 | 12.2796 | 12.1062 | NaN | NaN | NaN | 12.5191 | 120.7007 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 526.7344 | NaN | 14.9264 | NaN | 11.6693
2731.1292 | 12.7617 | 12.3861 | 12.5214 | 12.7552 | 12.3133 | 12.5629 | 12.2823 | 12.1096 | NaN | NaN | NaN | 12.5302 | 128.0115 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 527.5608 | NaN | 29.2214 | NaN | 13.7388
2732.1292 | 12.7821 | 12.3547 | 12.5234 | 12.7514 | 12.3717 | 12.5475 | 12.2746 | 12.1016 | NaN | NaN | NaN | 12.5432 | 119.8453 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 525.8978 | NaN | 11.064 | NaN | 13.3851
2733.1292 | 12.7213 | 12.3298 | 12.5244 | 12.7902 | 12.2968 | 12.54 | 12.2811 | 12.1091 | NaN | NaN | NaN | 12.5626 | 129.9575 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 526.7374 | NaN | 14.4764 | NaN | 16.7162
2734.1292 | 12.7224 | 12.4311 | 12.5267 | 12.7824 | 12.3669 | 12.5604 | 12.2886 | 12.0999 | NaN | NaN | NaN | 12.5322 | 128.6079 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 525.4422 | NaN | 15.6014 | NaN | 16.2634
2735.1292 | 12.7403 | 12.3602 | 12.5276 | 12.8487 | 12.4034 | 12.5346 | 12.2814 | 12.1001 | NaN | NaN | NaN | 12.5367 | 121.1623 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 527.4063 | NaN | 17.6679 | NaN | 16.2372
2736.1292 | 12.7446 | 12.3178 | 12.5296 | 12.7906 | 12.3779 | 12.5148 | 12.2748 | 12.1071 | NaN | NaN | NaN | 12.5606 | 122.1418 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 527.1873 | NaN | 13.3546 | NaN | 14.3983
2737.1292 | 12.7425 | 12.3521 | 12.5282 | 12.7698 | 12.36 | 12.5442 | 12.2934 | 12.1045 | NaN | NaN | NaN | 12.5379 | 121.2413 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 527.8395 | NaN | 33.9214 | NaN | 14.8305
2738.1292 | 12.736 | 12.3647 | 12.5317 | 12.8167 | 12.3652 | 12.5377 | 12.2905 | 12.1051 | NaN | NaN | NaN | 12.5467 | 132.3507 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 525.5477 | NaN | 12.7035 | NaN | 14.9631
2739.1292 | 12.7349 | 12.388 | 12.5304 | 12.7527 | 12.3343 | 12.5359 | 12.2854 | 12.1091 | NaN | NaN | NaN | 12.5282 | 128.8329 | NaN | NaN | NaN | -11.7339 | NaN | NaN | NaN | NaN | 521.8042 | NaN | 31.0201 | NaN | 11.6269
2740.1292 | 12.7405 | 12.4535 | 12.5286 | 12.8001 | 12.3736 | 12.5699 | 12.3149 | 12.1028 | NaN | NaN | NaN | 12.5515 | 119.7895 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -19.6011 | 521.5424 | NaN | 10.1169 | NaN | 15.3008
2741.1292 | 12.7437 | 12.3297 | 12.5284 | 12.7768 | 12.3631 | 12.5191 | 12.277 | 12.0995 | NaN | NaN | NaN | 12.5349 | 119.3376 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 522.3049 | NaN | 22.7521 | NaN | 15.6423
2742.1292 | 12.7392 | 12.3679 | 12.5296 | 12.7653 | 12.3774 | 12.5261 | 12.2849 | 12.1033 | NaN | NaN | NaN | 12.5458 | 125.3834 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 521.2554 | NaN | 36.06 | NaN | 16.4688
2743.1292 | 12.7417 | 12.3299 | 12.5312 | 12.7729 | 12.3642 | 12.5124 | 12.2805 | 12.108 | NaN | NaN | NaN | 12.5494 | 115.8769 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 521.1985 | NaN | 14.7777 | NaN | 14.946
2744.1292 | 12.7286 | 12.4292 | 12.5351 | 12.8089 | 12.3483 | 12.5668 | 12.302 | 12.1049 | NaN | NaN | NaN | 12.5262 | 125.3577 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 519.6082 | NaN | 10.8796 | NaN | 16.0673
2745.1292 | 12.7319 | 12.3299 | 12.5284 | 12.7631 | 12.3528 | 12.5028 | 12.2779 | 12.1082 | NaN | NaN | NaN | 12.5477 | 111.9529 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 519.8036 | NaN | 29.0433 | NaN | 15.7331
2746.1292 | 12.7365 | 12.3421 | 12.5331 | 12.7598 | 12.3179 | 12.5157 | 12.2845 | 12.1118 | NaN | NaN | NaN | 12.5525 | 127.718 | NaN | NaN | NaN | -3.4756 | NaN | NaN | NaN | NaN | 517.1198 | NaN | 14.7834 | NaN | 15.3896
2747.1292 | 12.7449 | 12.3333 | 12.5387 | 12.7892 | 12.385 | 12.5027 | 12.2667 | 12.11 | NaN | NaN | NaN | 12.5551 | 124.9757 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 520.0134 | NaN | 12.3063 | NaN | 15.682
2748.1292 | 12.7488 | 12.3753 | 12.5352 | 12.7825 | 12.3739 | 12.5214 | 12.2727 | 12.1115 | NaN | NaN | NaN | 12.5483 | 127.8705 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 517.6545 | NaN | 19.4184 | NaN | 15.3333
2749.1292 | 12.7604 | 12.3715 | 12.5404 | 12.8026 | 12.2987 | 12.5302 | 12.2835 | 12.115 | NaN | NaN | NaN | 12.5397 | 116.0004 | NaN | NaN | NaN | -19.1691 | NaN | NaN | NaN | NaN | 517.3575 | NaN | 27.7415 | NaN | 14.4835
2750.1292 | 12.7289 | 12.3338 | 12.5363 | 12.8304 | 12.396 | 12.5179 | 12.2774 | 12.1121 | NaN | NaN | NaN | 12.5492 | 118.1842 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 520.5348 | NaN | 27.0944 | NaN | 16.4859
2751.1292 | 12.7404 | 12.3224 | 12.5409 | 12.8014 | 12.3892 | 12.5108 | 12.2677 | 12.1129 | NaN | NaN | NaN | 12.5802 | 127.2805 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 513.8633 | NaN | 18.2445 | NaN | 14.6293
2752.1292 | 12.7458 | 12.338 | 12.5389 | 12.7853 | 12.327 | 12.5205 | 12.2748 | 12.1154 | NaN | NaN | NaN | 12.5479 | 119.7643 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 516.2299 | NaN | 21.8632 | NaN | 15.1446
2753.1292 | 12.7517 | 12.3604 | 12.5424 | 12.8411 | 12.39 | 12.5165 | 12.2736 | 12.1092 | NaN | NaN | NaN | 12.5424 | 118.0788 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 510.0345 | NaN | 28.2383 | NaN | 15.7346
2754.1292 | 12.7726 | 12.4386 | 12.5387 | 12.794 | 12.378 | 12.5607 | 12.2959 | 12.1112 | NaN | NaN | NaN | 12.5306 | 124.9884 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 510.4845 | NaN | 18.2103 | NaN | 15.2216
2755.1292 | 12.8114 | 12.3297 | 12.5449 | 12.788 | 12.3631 | 12.5101 | 12.2736 | 12.1217 | NaN | NaN | NaN | 12.5454 | 132.3816 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 508.313 | NaN | 26.985 | NaN | 12.6745
2756.1292 | 12.7539 | 12.3781 | 12.5446 | 12.7832 | 12.3722 | 12.5244 | 12.2767 | 12.1157 | NaN | NaN | NaN | 12.5587 | 140.4454 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 512.4279 | NaN | 31.2085 | NaN | 15.022
2757.1292 | 12.8158 | 12.3689 | 12.5485 | 12.8004 | 12.3961 | 12.5192 | 12.277 | 12.116 | NaN | NaN | NaN | 12.5363 | 140.6107 | NaN | NaN | NaN | 8.4187 | NaN | NaN | NaN | NaN | 512.2755 | NaN | 14.6226 | NaN | 15.772
2758.1292 | 12.737 | 12.381 | 12.5422 | 12.7691 | 12.3564 | 12.5401 | 12.2874 | 12.1171 | NaN | NaN | NaN | 12.5222 | 132.2988 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 510.5059 | NaN | 24.9547 | NaN | 13.1281
2759.1292 | 12.7612 | 12.346 | 12.5478 | 12.8024 | 12.2827 | 12.5173 | 12.2761 | 12.117 | NaN | NaN | NaN | 12.5774 | 130.1516 | NaN | NaN | NaN | -0.155 | NaN | NaN | NaN | NaN | 508.6072 | NaN | 14.391 | NaN | 15.148
2760.1292 | 12.7295 | 12.3134 | 12.5477 | 12.8246 | 12.2948 | 12.5069 | 12.2702 | 12.1238 | NaN | NaN | NaN | 12.521 | 126.3896 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 513.3982 | NaN | 16.321 | NaN | 13.6392
2761.1292 | 12.7358 | 12.3925 | 12.5413 | 12.8083 | 12.2681 | 12.5301 | 12.2803 | 12.1162 | NaN | NaN | NaN | 12.5113 | 131.5693 | NaN | NaN | NaN | -14.7336 | NaN | NaN | NaN | NaN | 514.1536 | NaN | 20.4151 | NaN | 14.6552
2762.1292 | 12.7333 | 12.3809 | 12.5505 | 12.7714 | 12.3446 | 12.5336 | 12.2749 | 12.1218 | NaN | NaN | NaN | 12.5373 | 114.2423 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 516.2121 | NaN | 34.0755 | NaN | 16.1472
2763.1292 | 12.7389 | 12.3102 | 12.5485 | 12.7818 | 12.3359 | 12.4967 | 12.2646 | 12.1174 | NaN | NaN | NaN | 12.5141 | 127.5486 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 513.0388 | NaN | 17.6818 | NaN | 15.1963
2764.1292 | 12.7898 | 12.3823 | 12.5467 | 12.7561 | 12.3966 | 12.5169 | 12.2737 | 12.1256 | NaN | NaN | NaN | 12.5173 | 132.0336 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 514.9128 | NaN | 19.0936 | NaN | 14.6746
2765.1292 | 12.7164 | 12.3669 | 12.5506 | 12.8313 | 12.3306 | 12.5415 | 12.2857 | 12.1245 | NaN | NaN | NaN | 12.5546 | 129.8513 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 516.9645 | NaN | 14.1063 | NaN | 14.7757
2766.1292 | 12.7154 | 12.4474 | 12.5478 | 12.794 | 12.3417 | 12.577 | 12.3055 | 12.1249 | NaN | NaN | NaN | 12.5173 | 125.8124 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 517.0486 | NaN | 19.2715 | NaN | 15.6809
2767.1292 | 12.7296 | 12.3157 | 12.5471 | 12.7873 | 12.3844 | 12.5144 | 12.267 | 12.1315 | NaN | NaN | NaN | 12.5335 | 131.8446 | NaN | NaN | NaN | 5.1718 | NaN | NaN | NaN | NaN | 518.5074 | NaN | 7.7769 | NaN | 14.5745
2768.1292 | 12.739 | 12.3084 | 12.5512 | 12.7559 | 12.3162 | 12.5131 | 12.2673 | 12.1359 | NaN | NaN | NaN | 12.5219 | 129.3326 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 520.1078 | NaN | 13.2338 | NaN | 13.8559
2769.1292 | 12.7056 | 12.3346 | 12.5574 | 12.7645 | 12.3809 | 12.5279 | 12.2709 | 12.1395 | NaN | NaN | NaN | 12.5417 | 131.6058 | NaN | NaN | NaN | -9.8569 | NaN | NaN | NaN | NaN | 522.1146 | NaN | 9.1991 | NaN | 15.2322
2770.1292 | 12.841 | 12.3037 | 12.5565 | 12.8118 | 12.3268 | 12.5048 | 12.2614 | 12.1362 | NaN | NaN | NaN | 12.5312 | 129.264 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 520.0084 | NaN | 12.5587 | NaN | 13.48
2771.1292 | 12.7457 | 12.3024 | 12.5586 | 12.8017 | 12.3739 | 12.5152 | 12.2618 | 12.1435 | NaN | NaN | NaN | 12.566 | 121.7095 | NaN | NaN | NaN | -18.0768 | NaN | NaN | NaN | NaN | 521.027 | NaN | 24.1606 | NaN | 13.6909
2772.1292 | 12.719 | 12.3359 | 12.5558 | 12.8015 | 12.2773 | 12.5205 | 12.2685 | 12.1374 | NaN | NaN | NaN | 12.5625 | 129.7405 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 520.0884 | NaN | 22.5339 | NaN | 15.8717
2773.1292 | 12.7247 | 12.3243 | 12.561 | 12.7957 | 12.3517 | 12.5161 | 12.2685 | 12.1404 | NaN | NaN | NaN | 12.5314 | 118.5727 | NaN | NaN | NaN | 0.6321 | NaN | NaN | NaN | NaN | 520.8311 | NaN | 21.6787 | NaN | 14.3854
2774.1292 | 12.739 | 12.3179 | 12.5631 | 12.7888 | 12.3699 | 12.5085 | 12.2628 | 12.1406 | NaN | NaN | NaN | 12.5858 | 118.6714 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 522.7215 | NaN | 16.459 | NaN | 14.8902
2775.1292 | 12.7411 | 12.3247 | 12.5633 | 12.8343 | 12.3412 | 12.5168 | 12.2677 | 12.1484 | NaN | NaN | NaN | 12.5301 | 123.8098 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 522.6898 | NaN | 30.1931 | NaN | 15.7575
2776.1292 | 12.7477 | 12.3254 | 12.5647 | 12.8335 | 12.3442 | 12.5246 | 12.2679 | 12.1364 | NaN | NaN | NaN | 12.5425 | 130.5506 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 520.3714 | NaN | 14.1555 | NaN | 15.0617
2777.1292 | 12.7414 | 12.3126 | 12.5619 | 12.8069 | 12.335 | 12.5221 | 12.2618 | 12.142 | NaN | NaN | NaN | 12.533 | 123.9315 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 522.1999 | NaN | 15.381 | NaN | 14.6791
2778.1292 | 12.7392 | 12.3107 | 12.565 | 12.8004 | 12.3877 | 12.5101 | 12.2653 | 12.1523 | NaN | NaN | NaN | 12.5643 | 123.4427 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 523.212 | NaN | 10.8816 | NaN | 14.7129
2779.1292 | 12.7501 | 12.3168 | 12.5613 | 12.817 | 12.3967 | 12.5079 | 12.2555 | 12.1467 | NaN | NaN | NaN | 12.5417 | 123.6563 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 521.5074 | NaN | 23.9879 | NaN | 15.1325
2780.1292 | 12.7893 | 12.3121 | 12.5666 | 12.8114 | 12.3789 | 12.5177 | 12.2598 | 12.1556 | NaN | NaN | NaN | 12.5332 | 122.8112 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 520.8429 | NaN | 24.5816 | NaN | 15.2909
2781.1292 | 12.7468 | 12.3099 | 12.5661 | 12.8443 | 12.3643 | 12.5265 | 12.266 | 12.1518 | NaN | NaN | NaN | 12.5549 | 129.5923 | NaN | NaN | NaN | -6.378 | NaN | NaN | NaN | NaN | 518.6181 | NaN | 18.6379 | NaN | 15.107
2782.1292 | 12.8352 | 12.3106 | 12.5642 | 12.8514 | 12.3871 | 12.5177 | 12.2566 | 12.151 | NaN | NaN | NaN | 12.5183 | 117.8016 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 520.4763 | NaN | 15.4723 | NaN | 15.7858
2783.1292 | 12.8045 | 12.3228 | 12.568 | 12.8211 | 12.3769 | 12.5296 | 12.2674 | 12.1491 | NaN | NaN | NaN | 12.5408 | 124.0086 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.9888 | NaN | 33.3663 | NaN | 14.5253
2784.1292 | 12.7474 | 12.3809 | 12.5653 | 12.8129 | 12.2866 | 12.5589 | 12.2712 | 12.1478 | NaN | NaN | NaN | 12.5582 | 123.6303 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.2395 | NaN | 28.1499 | NaN | 16.1116
2785.1292 | 12.741 | 12.4695 | 12.5663 | 12.8085 | 12.3614 | 12.6043 | 12.2982 | 12.1524 | NaN | NaN | NaN | 12.5389 | 126.5421 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 521.7994 | NaN | 9.7071 | NaN | 15.7118
2786.1292 | 12.7314 | 12.3292 | 12.5679 | 12.7836 | 12.369 | 12.5362 | 12.2697 | 12.1395 | NaN | NaN | NaN | 12.5574 | 122.8683 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 524.1445 | NaN | 12.8643 | NaN | 14.2048
2787.1292 | 12.726 | 12.3829 | 12.5632 | 12.8006 | 12.4072 | 12.5396 | 12.2762 | 12.1462 | NaN | NaN | NaN | 12.5281 | 133.5738 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -19.2808 | 520.8536 | NaN | 16.5462 | NaN | 13.9577
2788.1292 | 12.7228 | 12.3227 | 12.5679 | 12.7995 | 12.2973 | 12.5445 | 12.2671 | 12.1409 | NaN | NaN | NaN | 12.5614 | 128.158 | NaN | NaN | NaN | 8.6221 | NaN | NaN | NaN | NaN | 518.1825 | NaN | 10.7942 | NaN | 16.0501
2789.1292 | 12.731 | 12.3103 | 12.5725 | 12.8511 | 12.3723 | 12.521 | 12.2619 | 12.139 | NaN | NaN | NaN | 12.5322 | 135.1581 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 522.5416 | NaN | 17.3238 | NaN | 11.2568
2790.1292 | 12.7572 | 12.3788 | 12.5643 | 12.8291 | 12.3654 | 12.5536 | 12.2709 | 12.1356 | NaN | NaN | NaN | 12.5309 | 129.8942 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 523.1409 | NaN | 20.8858 | NaN | 18.7777
2791.1292 | 12.7208 | 12.3078 | 12.5733 | 12.8276 | 12.3371 | 12.5347 | 12.2591 | 12.1327 | NaN | NaN | NaN | 12.5459 | 134.8904 | NaN | NaN | NaN | -8.0139 | NaN | NaN | NaN | NaN | 520.9312 | NaN | 23.381 | NaN | 13.5156
2792.1292 | 12.7377 | 12.3476 | 12.5761 | 12.8325 | 12.3776 | 12.5525 | 12.2664 | 12.1307 | NaN | NaN | NaN | 12.541 | 122.0088 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 522.916 | NaN | 17.2451 | NaN | 16.0478
2793.1292 | 12.6924 | 12.3319 | 12.5767 | 12.8143 | 12.3393 | 12.5447 | 12.2653 | 12.1315 | NaN | NaN | NaN | 12.5142 | 128.4555 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 522.6986 | NaN | 16.2174 | NaN | 13.8913
2794.1292 | 12.6937 | 12.3134 | 12.5791 | 12.8186 | 12.3253 | 12.5316 | 12.2656 | 12.1354 | NaN | NaN | NaN | 12.5295 | 120.068 | NaN | NaN | NaN | 4.241 | NaN | NaN | NaN | NaN | 517.9925 | NaN | 29.1045 | NaN | 15.9528
2795.1292 | 12.7097 | 12.3487 | 12.5739 | 12.8258 | 12.338 | 12.5565 | 12.2671 | 12.1268 | NaN | NaN | NaN | 12.5209 | 125.3906 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 521.5885 | NaN | 18.9155 | NaN | 14.2482
2796.1292 | 12.7139 | 12.3417 | 12.5807 | 12.8214 | 12.3784 | 12.5509 | 12.2744 | 12.1286 | NaN | NaN | NaN | 12.5227 | 124.769 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 523.7053 | NaN | 20.5848 | NaN | 13.3637
2797.1292 | 12.7119 | 12.4065 | 12.5785 | 12.7996 | 12.3036 | 12.6062 | 12.2889 | 12.1245 | NaN | NaN | NaN | 12.5821 | 129.1877 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 522.7345 | NaN | 10.9431 | NaN | 11.7299
2798.1292 | 12.7198 | 12.3566 | 12.587 | 12.8719 | 12.2757 | 12.5594 | 12.2717 | 12.124 | NaN | NaN | NaN | 12.5439 | 128.0462 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.9594 | NaN | 34.9955 | NaN | 14.2337
2799.1448 | 12.7128 | 12.303 | 12.5809 | 12.8239 | 12.3571 | 12.5394 | 12.2669 | 12.1212 | NaN | NaN | NaN | 12.5262 | 117.997 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 517.7705 | NaN | 19.4295 | NaN | 15.1113
2800.1292 | 12.8402 | 12.2957 | 12.5786 | 12.8203 | 12.3603 | 12.5371 | 12.2687 | 12.1218 | NaN | NaN | NaN | 12.5268 | 120.2979 | NaN | NaN | NaN | 4.5226 | NaN | NaN | NaN | NaN | 521.5723 | NaN | 13.6447 | NaN | 15.5614
2801.1292 | 12.7251 | 12.3507 | 12.5768 | 12.8364 | 12.3402 | 12.5568 | 12.2782 | 12.1219 | NaN | NaN | NaN | 12.5594 | 131.7323 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 521.8344 | NaN | 23.7646 | NaN | 13.9935
2802.1292 | 12.7582 | 12.3497 | 12.5825 | 12.8196 | 12.3127 | 12.557 | 12.275 | 12.1209 | NaN | NaN | NaN | 12.6393 | 125.3873 | NaN | NaN | NaN | -14.6768 | NaN | NaN | NaN | NaN | 517.0828 | NaN | 12.2779 | NaN | 16.0354
2803.1292 | 12.7598 | 12.3488 | 12.5885 | 12.8077 | 12.3127 | 12.5496 | 12.2736 | 12.1204 | NaN | NaN | NaN | 12.4971 | 116.3234 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.2967 | NaN | 29.3036 | NaN | 15.8364
2804.1292 | 12.6874 | 12.351 | 12.5835 | 12.8381 | 12.3925 | 12.5549 | 12.2815 | 12.1246 | NaN | NaN | NaN | 12.5616 | 127.9408 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 519.3147 | NaN | 28.9751 | NaN | 14.1985
2805.1448 | 12.699 | 12.2967 | 12.5789 | 12.837 | 12.3408 | 12.5193 | 12.2607 | 12.1228 | NaN | NaN | NaN | 12.5233 | 127.459 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.5477 | NaN | 10.8667 | NaN | 15.5553
2806.1292 | 12.7027 | 12.3358 | 12.5774 | 12.8124 | 12.3209 | 12.5388 | 12.2759 | 12.1208 | NaN | NaN | NaN | 12.5178 | 107.9283 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.1632 | NaN | 11.4507 | NaN | 16.1293
2807.1292 | 12.8118 | 12.3308 | 12.5808 | 12.8205 | 12.2973 | 12.5472 | 12.2761 | 12.1225 | NaN | NaN | NaN | 12.5383 | 119.0384 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.7442 | NaN | 20.0556 | NaN | 16.2959
2808.1292 | 12.6807 | 12.3152 | 12.5743 | 12.8076 | 12.3913 | 12.5354 | 12.2742 | 12.1303 | NaN | NaN | NaN | 12.5287 | 114.2634 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 517.9084 | NaN | 31.4856 | NaN | 14.967
2809.1292 | 12.6767 | 12.3069 | 12.5855 | 12.82 | 12.3536 | 12.5197 | 12.2598 | 12.1387 | NaN | NaN | NaN | 12.586 | 119.3496 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 517.0977 | NaN | 15.8527 | NaN | 14.8315
2810.1292 | 12.697 | 12.3627 | 12.5872 | 12.8064 | 12.3417 | 12.5512 | 12.2756 | 12.1351 | NaN | NaN | NaN | 12.5502 | 123.5505 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 514.1342 | NaN | 36.6048 | NaN | 14.1118
2811.1448 | 12.7082 | 12.3537 | 12.5872 | 12.8897 | 12.371 | 12.5407 | 12.2844 | 12.1451 | NaN | NaN | NaN | 12.5266 | 122.4382 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 515.2778 | NaN | 26.0706 | NaN | 14.9035
2812.1292 | 12.7192 | 12.3864 | 12.5858 | 12.8291 | 12.3907 | 12.5486 | 12.2876 | 12.1464 | NaN | NaN | NaN | 12.546 | 124.1353 | NaN | NaN | NaN | 3.4042 | NaN | NaN | NaN | NaN | 518.3623 | NaN | 28.4467 | NaN | 14.5738
2813.1448 | 12.7192 | 12.3959 | 12.5889 | 12.8785 | 12.3518 | 12.5481 | 12.2869 | 12.1426 | NaN | NaN | NaN | 12.535 | 131.0176 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 519.189 | NaN | 35.6148 | NaN | 13.7315
2814.1292 | 12.7206 | 12.3233 | 12.5857 | 12.8512 | 12.2956 | 12.5165 | 12.2729 | 12.1489 | NaN | NaN | NaN | 12.5475 | 127.8025 | NaN | NaN | NaN | -19.9204 | NaN | NaN | NaN | NaN | 520.8102 | NaN | 22.4225 | NaN | 16.0212
2815.1292 | 12.8758 | 12.3301 | 12.5913 | 12.8554 | 12.4098 | 12.5112 | 12.2752 | 12.1502 | NaN | NaN | NaN | 12.5312 | 123.2494 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 515.7186 | NaN | 24.378 | NaN | 14.5277
2816.1292 | 12.7236 | 12.3448 | 12.5917 | 12.8385 | 12.354 | 12.5277 | 12.2822 | 12.1518 | NaN | NaN | NaN | 12.5487 | 122.497 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 515.7906 | NaN | 22.2067 | NaN | 14.9979
2817.1292 | 12.7331 | 12.3807 | 12.5859 | 12.8244 | 12.3475 | 12.5484 | 12.2834 | 12.1517 | NaN | NaN | NaN | 12.535 | 127.4229 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.0802 | NaN | 28.0041 | NaN | 12.9075
2818.1292 | 12.7378 | 12.342 | 12.5894 | 12.8382 | 12.3778 | 12.5159 | 12.2781 | 12.1485 | NaN | NaN | NaN | 12.5317 | 135.5901 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 517.5295 | NaN | 16.5459 | NaN | 15.049
2819.1292 | 12.7654 | 12.335 | 12.591 | 12.8474 | 12.3846 | 12.5182 | 12.2823 | 12.146 | NaN | NaN | NaN | 12.5289 | 125.2563 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 513.4018 | NaN | 17.9702 | NaN | 15.5333
2820.1292 | 12.7236 | 12.3418 | 12.5849 | 12.8549 | 12.363 | 12.5176 | 12.2803 | 12.1479 | NaN | NaN | NaN | 12.5446 | 125.5109 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 515.9463 | NaN | 25.5801 | NaN | 15.1277
2821.1292 | 12.7249 | 12.3997 | 12.5853 | 12.8911 | 12.3691 | 12.5452 | 12.298 | 12.1506 | NaN | NaN | NaN | 12.523 | 122.8579 | NaN | NaN | NaN | 4.0669 | NaN | NaN | NaN | NaN | 512.6608 | NaN | 28.424 | NaN | 14.4992
2822.1292 | 12.7317 | 12.4426 | 12.5807 | 12.8726 | 12.3877 | 12.5638 | 12.3066 | 12.1541 | NaN | NaN | NaN | 12.5351 | 120.2381 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 512.3326 | NaN | 23.0563 | NaN | 15.5811
2823.1292 | 12.7263 | 12.4171 | 12.5841 | 12.8956 | 12.3794 | 12.5357 | 12.2902 | 12.1606 | NaN | NaN | NaN | 12.602 | 115.2192 | NaN | NaN | NaN | 5.8708 | NaN | NaN | NaN | NaN | 514.702 | NaN | 12.8165 | NaN | 16.2381
2824.1292 | 12.6916 | 12.395 | 12.5813 | 12.8816 | 12.3081 | 12.5415 | 12.3007 | 12.1552 | NaN | NaN | NaN | 12.5386 | 129.4976 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 517.2177 | NaN | 13.7515 | NaN | 14.6989
2825.1292 | 12.7045 | 12.3626 | 12.58 | 12.8278 | 12.3459 | 12.527 | 12.2927 | 12.1603 | NaN | NaN | NaN | 12.5704 | 121.1773 | NaN | NaN | NaN | -17.4208 | NaN | NaN | NaN | NaN | 515.2577 | NaN | 38.0256 | NaN | 15.5813
2826.1292 | 12.7349 | 12.3806 | 12.584 | 12.8639 | 12.3732 | 12.5201 | 12.2987 | 12.1668 | NaN | NaN | NaN | 12.549 | 117.7744 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 513.9689 | NaN | 22.0604 | NaN | 15.0247
2827.1292 | 12.7213 | 12.367 | 12.5774 | 12.9212 | 12.3491 | 12.5178 | 12.295 | 12.16 | NaN | NaN | NaN | 12.5316 | 123.0095 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 513.4239 | NaN | 13.6545 | NaN | 16.991
2828.1292 | 12.7256 | 12.3739 | 12.5805 | 12.8725 | 12.3529 | 12.5297 | 12.3114 | 12.163 | NaN | NaN | NaN | 12.539 | 135.0119 | NaN | NaN | NaN | 9.5811 | NaN | NaN | NaN | NaN | 513.9503 | NaN | 30.948 | NaN | 14.6619
2829.1292 | 12.7347 | 12.3699 | 12.5772 | 12.8574 | 12.3011 | 12.5149 | 12.3045 | 12.1709 | NaN | NaN | NaN | 12.5294 | 117.9539 | NaN | NaN | NaN | 7.4192 | NaN | NaN | NaN | NaN | 514.4751 | NaN | 20.7034 | NaN | 14.3679
2830.1292 | 12.7173 | 12.4062 | 12.5741 | 12.841 | 12.304 | 12.5362 | 12.3126 | 12.1654 | NaN | NaN | NaN | 12.5245 | 129.2134 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 511.6461 | NaN | 18.7102 | NaN | 14.3651
2831.1292 | 12.7238 | 12.3958 | 12.5821 | 12.8783 | 12.3234 | 12.5291 | 12.3065 | 12.1641 | NaN | NaN | NaN | 12.541 | 121.2793 | NaN | NaN | NaN | -19.9848 | NaN | NaN | NaN | NaN | 510.4317 | NaN | 22.2091 | NaN | 14.992
2832.1292 | 12.8157 | 12.392 | 12.5806 | 12.8469 | 12.3075 | 12.5222 | 12.3089 | 12.1634 | NaN | NaN | NaN | 12.5267 | 127.8945 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 509.29 | NaN | 26.0174 | NaN | 14.1884
2833.1292 | 12.7499 | 12.4547 | 12.5792 | 12.8238 | 12.3788 | 12.5349 | 12.3168 | 12.1675 | NaN | NaN | NaN | 12.5284 | 118.5446 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 509.7947 | NaN | 20.125 | NaN | 14.9224
2834.1292 | 12.7174 | 12.4358 | 12.583 | 12.89 | 12.3857 | 12.5358 | 12.3192 | 12.1572 | NaN | NaN | NaN | 12.5408 | 118.1242 | NaN | NaN | NaN | -3.0748 | NaN | NaN | NaN | NaN | 510.0405 | NaN | 14.6972 | NaN | 14.3159
2835.1448 | 12.7248 | 12.4206 | 12.5819 | 12.8657 | 12.4003 | 12.5206 | 12.3197 | 12.1613 | NaN | NaN | NaN | 12.542 | 125.8435 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 507.6864 | NaN | 11.1163 | NaN | 13.2383
2836.1292 | 12.726 | 12.428 | 12.5857 | 12.8538 | 12.3652 | 12.5323 | 12.314 | 12.1572 | NaN | NaN | NaN | 12.5473 | 125.0178 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 507.6198 | NaN | 24.7553 | NaN | 21.4236
2837.1292 | 12.7301 | 12.4004 | 12.5793 | 12.8949 | 12.3455 | 12.5318 | 12.3078 | 12.1661 | NaN | NaN | NaN | 12.5545 | 122.1306 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 507.1636 | NaN | 12.3796 | NaN | 14.1318
2838.1292 | 12.6997 | 12.3912 | 12.5842 | 12.9295 | 12.3902 | 12.5083 | 12.2902 | 12.155 | NaN | NaN | NaN | 12.5519 | 123.6467 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 509.7042 | NaN | 14.0839 | NaN | 15.3974
2839.1292 | 12.7957 | 12.3754 | 12.5836 | 12.8629 | 12.3114 | 12.5058 | 12.2947 | 12.1547 | NaN | NaN | NaN | 12.5533 | 123.3952 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 509.2975 | NaN | 19.9978 | NaN | 13.3771
2840.1292 | 12.7178 | 12.3771 | 12.5848 | 12.8095 | 12.3279 | 12.5099 | 12.2993 | 12.1533 | NaN | NaN | NaN | 12.5691 | 120.2321 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 510.9035 | NaN | 24.8407 | NaN | 14.4366
2841.1292 | 12.7303 | 12.3925 | 12.5876 | 12.8693 | 12.3113 | 12.5182 | 12.3109 | 12.1537 | NaN | NaN | NaN | 12.5215 | 124.1946 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 511.4766 | NaN | 22.4679 | NaN | 14.4636
2842.1292 | 12.7349 | 12.4431 | 12.5869 | 12.9111 | 12.4011 | 12.5316 | 12.3116 | 12.158 | NaN | NaN | NaN | 12.5595 | 133.6503 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 509.7024 | NaN | 16.5349 | NaN | 15.3726
2843.1292 | 12.7433 | 12.3747 | 12.5877 | 12.8561 | 12.3596 | 12.5095 | 12.3 | 12.1521 | NaN | NaN | NaN | 12.5271 | 118.1563 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 512.2556 | NaN | 23.9081 | NaN | 14.067
2844.1292 | 12.7421 | 12.3811 | 12.5922 | 12.866 | 12.3913 | 12.508 | 12.3016 | 12.1504 | NaN | NaN | NaN | 12.5302 | 126.9335 | NaN | NaN | NaN | -19.2921 | NaN | NaN | NaN | NaN | 511.2594 | NaN | 12.5176 | NaN | 13.4399
2845.1292 | 12.7689 | 12.3883 | 12.5951 | 12.8797 | 12.268 | 12.5069 | 12.296 | 12.151 | NaN | NaN | NaN | 12.5417 | 121.3021 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 511.7466 | NaN | 25.0328 | NaN | 14.2308
2846.1292 | 12.7658 | 12.3752 | 12.588 | 12.8818 | 12.4091 | 12.499 | 12.2933 | 12.1524 | NaN | NaN | NaN | 12.5569 | 123.9526 | NaN | NaN | NaN | -17.4625 | NaN | NaN | NaN | NaN | 511.5456 | NaN | 18.1809 | NaN | 14.3556
2847.1292 | 12.7448 | 12.4057 | 12.5865 | 12.8547 | 12.3943 | 12.5212 | 12.3105 | 12.1485 | NaN | NaN | NaN | 12.5756 | 129.2092 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 508.9931 | NaN | 22.448 | NaN | 14.47
2848.1292 | 12.7069 | 12.3677 | 12.5879 | 12.8872 | 12.3366 | 12.5115 | 12.3037 | 12.1391 | NaN | NaN | NaN | 12.5633 | 117.6257 | NaN | NaN | NaN | -18.7293 | NaN | NaN | NaN | NaN | 509.3176 | NaN | 13.0844 | NaN | 15.5721
2849.1292 | 12.7089 | 12.3918 | 12.5883 | 12.8579 | 12.3557 | 12.5094 | 12.298 | 12.1339 | NaN | NaN | NaN | 12.5361 | 126.1404 | NaN | NaN | NaN | -17.0296 | NaN | NaN | NaN | NaN | 509.694 | NaN | 23.1938 | NaN | 13.5213
2850.1292 | 12.707 | 12.3772 | 12.6024 | 12.8403 | 12.3221 | 12.5058 | 12.292 | 12.1377 | NaN | NaN | NaN | 12.5518 | 121.3408 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 511.4774 | NaN | 18.9009 | NaN | 15.0451
2851.1292 | 12.7115 | 12.3827 | 12.5926 | 12.8767 | 12.3488 | 12.5032 | 12.2913 | 12.1303 | NaN | NaN | NaN | 12.5829 | 119.287 | NaN | NaN | NaN | 6.0453 | NaN | NaN | NaN | NaN | 510.2568 | NaN | 12.2047 | NaN | 14.9835
2852.1292 | 12.7528 | 12.3795 | 12.5925 | 12.858 | 12.3687 | 12.5061 | 12.2945 | 12.1299 | NaN | NaN | NaN | 12.5619 | 120.3887 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 511.1699 | NaN | 34.8897 | NaN | 14.515
2853.1292 | 12.8104 | 12.3464 | 12.5875 | 12.8547 | 12.3647 | 12.5031 | 12.2941 | 12.13 | NaN | NaN | NaN | 12.5443 | 119.0609 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 512.4295 | NaN | 21.0711 | NaN | 15.3522
2854.1292 | 12.7557 | 12.3577 | 12.5946 | 12.8555 | 12.3706 | 12.4977 | 12.3021 | 12.1349 | NaN | NaN | NaN | 12.5311 | 121.9881 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 509.8419 | NaN | 31.3462 | NaN | 19.4059
2855.1292 | 12.749 | 12.3873 | 12.5958 | 12.8784 | 12.387 | 12.5163 | 12.3026 | 12.1365 | NaN | NaN | NaN | 12.5674 | 131.1117 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 510.7998 | NaN | 12.4589 | NaN | 13.6184
2856.1292 | 12.7493 | 12.3494 | 12.5906 | 12.8437 | 12.3167 | 12.4994 | 12.2926 | 12.1342 | NaN | NaN | NaN | 12.5615 | 119.0986 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 513.0225 | NaN | 22.3525 | NaN | 13.5941
2857.1292 | 12.7062 | 12.3781 | 12.5926 | 12.8368 | 12.2767 | 12.5315 | 12.296 | 12.1295 | NaN | NaN | NaN | 12.5272 | 124.1524 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 511.5302 | NaN | 28.8896 | NaN | 13.2483
2858.1292 | 12.7116 | 12.3814 | 12.593 | 12.9093 | 12.3668 | 12.5023 | 12.2931 | 12.1407 | NaN | NaN | NaN | 12.5295 | 127.3239 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 512.0143 | NaN | 32.8635 | NaN | 14.6522
2859.1292 | 12.7224 | 12.3913 | 12.5976 | 12.8905 | 12.3839 | 12.5153 | 12.2939 | 12.1329 | NaN | NaN | NaN | 12.5671 | 116.5843 | NaN | NaN | NaN | -1.9756 | NaN | NaN | NaN | NaN | 510.7123 | NaN | 17.5463 | NaN | 13.7969
2860.1292 | 12.7299 | 12.3846 | 12.5933 | 12.8941 | 12.3791 | 12.5184 | 12.2908 | 12.1389 | NaN | NaN | NaN | 12.5325 | 127.9304 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 511.3798 | NaN | 14.2363 | NaN | 14.2561
2861.1292 | 12.7321 | 12.358 | 12.5901 | 12.8823 | 12.3983 | 12.5107 | 12.2895 | 12.1366 | NaN | NaN | NaN | 12.5543 | 119.3055 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 511.8497 | NaN | 27.8236 | NaN | 15.3417
2862.1292 | 12.7386 | 12.3672 | 12.5914 | 12.8814 | 12.3922 | 12.5193 | 12.2882 | 12.1369 | NaN | NaN | NaN | 12.5403 | 121.6864 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 514.4197 | NaN | 19.8724 | NaN | 15.1041
2863.1292 | 12.7727 | 12.3461 | 12.5942 | 12.8935 | 12.3788 | 12.5114 | 12.2912 | 12.1376 | NaN | NaN | NaN | 12.5288 | 123.2368 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 515.4222 | NaN | 17.9128 | NaN | 14.869
2864.1292 | 12.7372 | 12.3574 | 12.5875 | 12.8557 | 12.2907 | 12.5138 | 12.285 | 12.14 | NaN | NaN | NaN | 12.5491 | 133.7087 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 515.6341 | NaN | 15.6714 | NaN | 15.7817
2865.1292 | 12.7398 | 12.3709 | 12.5918 | 12.8537 | 12.3587 | 12.5126 | 12.2907 | 12.1414 | NaN | NaN | NaN | 12.5694 | 124.5283 | NaN | NaN | NaN | 5.1427 | NaN | NaN | NaN | NaN | 516.2126 | NaN | 11.4338 | NaN | 14.6358
2866.1292 | 12.743 | 12.3424 | 12.5881 | 12.8522 | 12.3691 | 12.5065 | 12.2837 | 12.1456 | NaN | NaN | NaN | 12.5366 | 127.1553 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 517.7551 | NaN | 19.2548 | NaN | 13.9471
2867.1292 | 12.7427 | 12.3352 | 12.594 | 12.8691 | 12.3652 | 12.512 | 12.2877 | 12.1549 | NaN | NaN | NaN | 12.5215 | 132.3425 | NaN | NaN | NaN | -6.089 | NaN | NaN | NaN | NaN | 517.9989 | NaN | 28.8904 | NaN | 14.6419
2868.1292 | 12.7381 | 12.3471 | 12.5952 | 12.864 | 12.3879 | 12.5136 | 12.2869 | 12.1536 | NaN | NaN | NaN | 12.5787 | 132.1199 | NaN | NaN | NaN | -17.9392 | NaN | NaN | NaN | NaN | 517.6048 | NaN | 14.5656 | NaN | 15.2591
2869.1292 | 12.7451 | 12.4371 | 12.5967 | 12.8157 | 12.3777 | 12.5473 | 12.299 | 12.1453 | NaN | NaN | NaN | 12.5685 | 128.8685 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 515.5521 | NaN | 33.8296 | NaN | 14.8832
2870.1292 | 12.7473 | 12.3794 | 12.5972 | 12.8684 | 12.3696 | 12.5261 | 12.2925 | 12.1516 | NaN | NaN | NaN | 12.544 | 121.4536 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.0754 | NaN | 14.0783 | NaN | 15.0197
2871.1292 | 12.7524 | 12.3528 | 12.5904 | 12.8433 | 12.3182 | 12.5105 | 12.2819 | 12.1586 | NaN | NaN | NaN | 12.5503 | 129.7719 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 516.7564 | NaN | 29.8019 | NaN | 12.9044
2872.1292 | 12.7373 | 12.4009 | 12.5951 | 12.883 | 12.3725 | 12.5145 | 12.2974 | 12.1547 | NaN | NaN | NaN | 12.5626 | 117.2138 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 516.4668 | NaN | 13.6173 | NaN | 22.369
2873.1292 | 12.7265 | 12.3519 | 12.5976 | 12.8516 | 12.3468 | 12.5153 | 12.2884 | 12.1541 | NaN | NaN | NaN | 12.5121 | 120.5372 | NaN | NaN | NaN | -19.9605 | NaN | NaN | NaN | NaN | 521.01 | NaN | 38.984 | NaN | 14.649
2874.1292 | 12.7257 | 12.3345 | 12.594 | 12.8526 | 12.3249 | 12.5181 | 12.2882 | 12.1536 | NaN | NaN | NaN | 12.5372 | 115.9723 | NaN | NaN | NaN | 8.4397 | NaN | NaN | NaN | NaN | 522.09 | NaN | 17.9794 | NaN | 22.3418
2875.1292 | 12.73 | 12.3437 | 12.6011 | 12.8542 | 12.369 | 12.5133 | 12.2919 | 12.1529 | NaN | NaN | NaN | 12.5157 | 128.2565 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 523.252 | NaN | 35.3222 | NaN | 15.0648
2876.1292 | 12.8012 | 12.3579 | 12.5909 | 12.8669 | 12.3502 | 12.5093 | 12.2906 | 12.1515 | NaN | NaN | NaN | 12.5041 | 117.0362 | NaN | NaN | NaN | -10.7721 | NaN | NaN | NaN | NaN | 522.5583 | NaN | 22.3938 | NaN | 14.564
2877.1292 | 12.701 | 12.3231 | 12.5922 | 12.8727 | 12.3481 | 12.5068 | 12.2947 | 12.1478 | NaN | NaN | NaN | 12.5452 | 125.5916 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 522.2617 | NaN | 13.1989 | NaN | 14.5409
2878.1292 | 12.7675 | 12.3484 | 12.5943 | 12.8729 | 12.292 | 12.5086 | 12.2946 | 12.1441 | NaN | NaN | NaN | 12.5346 | 117.8947 | NaN | NaN | NaN | -16.7355 | NaN | NaN | NaN | NaN | 521.1604 | NaN | 26.8468 | NaN | 23.2897
2879.1292 | 12.7399 | 12.3737 | 12.5977 | 12.8618 | 12.2682 | 12.5297 | 12.2923 | 12.1435 | NaN | NaN | NaN | 12.5481 | 124.7932 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.9586 | NaN | 27.338 | NaN | 14.9528
2880.1292 | 12.7122 | 12.3777 | 12.5986 | 12.8477 | 12.3013 | 12.5094 | 12.2844 | 12.1411 | NaN | NaN | NaN | 12.5051 | 122.5679 | NaN | NaN | NaN | -1.8435 | NaN | NaN | NaN | NaN | 518.782 | NaN | 18.1718 | NaN | 15.5947
2881.1292 | 12.7543 | 12.3385 | 12.5961 | 12.8735 | 12.3639 | 12.4992 | 12.2914 | 12.1414 | NaN | NaN | NaN | 12.5741 | 128.0276 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 521.357 | NaN | 17.1221 | NaN | 15.1179
2882.1292 | 12.757 | 12.3453 | 12.6 | 12.8665 | 12.3237 | 12.5103 | 12.2946 | 12.1317 | NaN | NaN | NaN | 12.5621 | 117.0336 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 519.9047 | NaN | 13.3646 | NaN | 15.9096
2883.1292 | 12.7375 | 12.3863 | 12.6058 | 12.8517 | 12.2629 | 12.5239 | 12.3016 | 12.1346 | NaN | NaN | NaN | 12.5218 | 132.2617 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 520.0069 | NaN | 28.6762 | NaN | 14.7741
2884.1292 | 12.8262 | 12.3725 | 12.6026 | 12.8557 | 12.3564 | 12.5094 | 12.3001 | 12.1389 | NaN | NaN | NaN | 12.5277 | 130.183 | NaN | NaN | NaN | 3.6028 | NaN | NaN | NaN | NaN | 519.7541 | NaN | 16.7323 | NaN | 14.3905
2885.1292 | 12.7461 | 12.3444 | 12.6008 | 12.8429 | 12.3453 | 12.4896 | 12.2868 | 12.1282 | NaN | NaN | NaN | 12.5421 | 127.6745 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 524.6706 | NaN | 26.9412 | NaN | 15.2752
2886.1292 | 12.731 | 12.3541 | 12.5985 | 12.8569 | 12.2936 | 12.5224 | 12.2958 | 12.1319 | NaN | NaN | NaN | 12.5532 | 125.9579 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 523.656 | NaN | 28.2079 | NaN | 14.6051
2887.1292 | 12.7488 | 12.3842 | 12.6015 | 12.8527 | 12.3761 | 12.5168 | 12.3021 | 12.1282 | NaN | NaN | NaN | 12.5655 | 129.3863 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 522.2371 | NaN | 21.5609 | NaN | 15.6983
2888.1292 | 12.7522 | 12.3994 | 12.6045 | 12.8412 | 12.2695 | 12.5411 | 12.3073 | 12.1286 | NaN | NaN | NaN | 12.5687 | 114.5003 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 524.2051 | NaN | 16.1092 | NaN | 15.468
2889.1292 | 12.7508 | 12.3669 | 12.6004 | 12.896 | 12.274 | 12.52 | 12.3043 | 12.1223 | NaN | NaN | NaN | 12.5482 | 124.8312 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 524.186 | NaN | 27.4744 | NaN | 14.4405
2890.1292 | 12.7269 | 12.3506 | 12.5992 | 12.8468 | 12.321 | 12.5114 | 12.2936 | 12.124 | NaN | NaN | NaN | 12.5293 | 126.6495 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 525.8375 | NaN | 27.9344 | NaN | 14.8276
2891.1292 | 12.7339 | 12.4333 | 12.6027 | 12.9218 | 12.3467 | 12.5478 | 12.304 | 12.1244 | NaN | NaN | NaN | 12.5569 | 125.4602 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 526.4162 | NaN | 30.7339 | NaN | 15.6535
2892.1292 | 12.7449 | 12.3696 | 12.5924 | 12.8152 | 12.3357 | 12.5125 | 12.3004 | 12.126 | NaN | NaN | NaN | 12.5645 | 131.6252 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 526.5602 | NaN | 19.2123 | NaN | 13.421
2893.1292 | 12.7451 | 12.4409 | 12.6 | 12.8236 | 12.3261 | 12.5664 | 12.3204 | 12.1377 | NaN | NaN | NaN | 12.5571 | 125.7878 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 528.0395 | NaN | 33.4917 | NaN | 14.2562
2894.1292 | 12.7428 | 12.427 | 12.5977 | 12.8797 | 12.389 | 12.5417 | 12.3098 | 12.1404 | NaN | NaN | NaN | 12.5698 | 116.8225 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 525.6612 | NaN | 18.6335 | NaN | 14.7342
2895.1448 | 12.7273 | 12.3847 | 12.5961 | 12.8396 | 12.3339 | 12.5417 | 12.316 | 12.1397 | NaN | NaN | NaN | 12.5615 | 132.8026 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 528.6051 | NaN | 23.2788 | NaN | 14.5829
2896.1292 | 12.7281 | 12.3633 | 12.5923 | 12.8037 | 12.3723 | 12.5257 | 12.3103 | 12.1386 | NaN | NaN | NaN | 12.5536 | 118.6457 | NaN | NaN | NaN | -1.2032 | NaN | NaN | NaN | NaN | 531.5916 | NaN | 11.1702 | NaN | 14.6046
2897.1292 | 12.7396 | 12.3543 | 12.5957 | 12.8469 | 12.3573 | 12.532 | 12.3054 | 12.1491 | NaN | NaN | NaN | 12.5833 | 126.5779 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 527.5575 | NaN | 17.122 | NaN | 12.9486
2898.1292 | 12.7258 | 12.3617 | 12.5988 | 12.8445 | 12.3946 | 12.5332 | 12.3068 | 12.1441 | NaN | NaN | NaN | 12.5768 | 123.3846 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 526.3339 | NaN | 23.1857 | NaN | 13.7223
2899.1292 | 12.7351 | 12.3946 | 12.5938 | 12.8579 | 12.2822 | 12.5489 | 12.3044 | 12.1443 | NaN | NaN | NaN | 12.5725 | 127.4906 | NaN | NaN | NaN | 3.1598 | NaN | NaN | NaN | NaN | 524.249 | NaN | 24.1915 | NaN | 14.3419
2900.1292 | 12.7463 | 12.4395 | 12.5948 | 12.8159 | 12.323 | 12.5602 | 12.3063 | 12.1394 | NaN | NaN | NaN | 12.5542 | 131.2192 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 520.645 | NaN | 11.8032 | NaN | 14.2025
2901.1292 | 12.7468 | 12.386 | 12.5885 | 12.8082 | 12.2877 | 12.5361 | 12.3118 | 12.1389 | NaN | NaN | NaN | 12.5931 | 124.0076 | NaN | NaN | NaN | -2.5765 | NaN | NaN | NaN | NaN | 524.1211 | NaN | 24.2083 | NaN | 14.8393
2902.1292 | 12.7443 | 12.3666 | 12.5932 | 12.8614 | 12.3191 | 12.54 | 12.307 | 12.1383 | NaN | NaN | NaN | 12.5835 | 126.9279 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 525.9831 | NaN | 21.9224 | NaN | 17.6016
2903.1292 | 12.7418 | 12.5022 | 12.5962 | 12.844 | 12.3652 | 12.5781 | 12.3354 | 12.1374 | NaN | NaN | NaN | 12.7136 | 128.0701 | NaN | NaN | NaN | -6.6766 | NaN | NaN | NaN | NaN | 525.8651 | NaN | 24.1813 | NaN | 13.6577
2904.1292 | 12.7476 | 12.395 | 12.5899 | 12.8551 | 12.2673 | 12.5476 | 12.3024 | 12.1387 | NaN | NaN | NaN | 12.5762 | 126.578 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 523.3577 | NaN | 14.7428 | NaN | 14.0206
2905.1292 | 12.7405 | 12.3641 | 12.5883 | 12.7879 | 12.3394 | 12.5441 | 12.306 | 12.1374 | NaN | NaN | NaN | 12.6002 | 124.2366 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 522.9066 | NaN | 11.9948 | NaN | 14.3573
2906.1292 | 12.7351 | 12.3761 | 12.5891 | 12.8343 | 12.3596 | 12.5543 | 12.3073 | 12.1368 | NaN | NaN | NaN | 12.5752 | 110.6867 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 520.3076 | NaN | 23.9461 | NaN | 14.8568
2907.1292 | 12.7346 | 12.3848 | 12.5938 | 12.8075 | 12.3528 | 12.5616 | 12.2977 | 12.1357 | NaN | NaN | NaN | 12.5713 | 120.1885 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 524.9033 | NaN | 15.4063 | NaN | 14.8615
2908.1292 | 12.7419 | 12.3897 | 12.5851 | 12.8332 | 12.389 | 12.5512 | 12.3024 | 12.1366 | NaN | NaN | NaN | 12.5858 | 118.9271 | NaN | NaN | NaN | -19.6898 | NaN | NaN | NaN | NaN | 522.7181 | NaN | 31.7876 | NaN | 15.5822
2909.1292 | 12.7411 | 12.3928 | 12.5946 | 12.8155 | 12.3536 | 12.554 | 12.3083 | 12.139 | NaN | NaN | NaN | 12.6103 | 125.5558 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 521.4388 | NaN | 18.4501 | NaN | 13.8182
2910.1292 | 12.7387 | 12.3825 | 12.5926 | 12.8521 | 12.3287 | 12.5501 | 12.3046 | 12.1353 | NaN | NaN | NaN | 12.5998 | 120.3027 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 520.1352 | NaN | 21.4146 | NaN | 13.589
2911.1292 | 12.7254 | 12.3714 | 12.5911 | 12.8265 | 12.2899 | 12.5522 | 12.3057 | 12.1402 | NaN | NaN | NaN | 12.5849 | 136.5513 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 521.6823 | NaN | 20.5256 | NaN | 14.7468
2912.1292 | 12.7327 | 12.3785 | 12.5929 | 12.8105 | 12.3338 | 12.5464 | 12.3054 | 12.1361 | NaN | NaN | NaN | 12.5748 | 126.8275 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 522.589 | NaN | 21.9741 | NaN | 13.8994
2913.1292 | 12.7229 | 12.4345 | 12.5904 | 12.7939 | 12.3719 | 12.5602 | 12.3058 | 12.1334 | NaN | NaN | NaN | 12.589 | 130.6513 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 520.1883 | NaN | 26.6609 | NaN | 14.1239
2914.1292 | 12.7508 | 12.3741 | 12.5945 | 12.7913 | 12.3296 | 12.5627 | 12.3156 | 12.1355 | NaN | NaN | NaN | 12.6109 | 120.6255 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.8045 | NaN | 18.5578 | NaN | 13.2762
2915.1292 | 12.7268 | 12.4212 | 12.5918 | 12.8062 | 12.2627 | 12.5868 | 12.3138 | 12.1368 | NaN | NaN | NaN | 12.6041 | 128.2944 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 519.7652 | NaN | 23.9525 | NaN | 13.4616
2916.1292 | 12.724 | 12.411 | 12.5942 | 12.8442 | 12.3131 | 12.5782 | 12.3065 | 12.1398 | NaN | NaN | NaN | 12.62 | 132.5709 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.398 | NaN | 34.3749 | NaN | 14.3921
2917.1292 | 12.7362 | 12.3774 | 12.5911 | 12.8659 | 12.3725 | 12.5484 | 12.3038 | 12.1364 | NaN | NaN | NaN | 12.6073 | 117.9878 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.6796 | NaN | 24.8537 | NaN | 15.869
2918.1292 | 12.7403 | 12.3524 | 12.5866 | 12.8681 | 12.2846 | 12.5468 | 12.3099 | 12.1398 | NaN | NaN | NaN | 12.5893 | 124.4872 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 517.2411 | NaN | 16.4608 | NaN | 12.5987
2919.1292 | 12.7586 | 12.4707 | 12.5871 | 12.7617 | 12.2738 | 12.615 | 12.3068 | 12.1398 | NaN | NaN | NaN | 12.625 | 130.1062 | NaN | NaN | NaN | -8.2942 | NaN | NaN | NaN | NaN | 514.4858 | NaN | 25.7801 | NaN | 13.0105
2920.1292 | 12.7445 | 12.3621 | 12.5847 | 12.8196 | 12.3795 | 12.5517 | 12.3124 | 12.1433 | NaN | NaN | NaN | 12.5982 | 123.5992 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 515.6118 | NaN | 14.0417 | NaN | 14.7807
2921.1292 | 12.7359 | 12.347 | 12.5813 | 12.8081 | 12.3816 | 12.5514 | 12.3098 | 12.1449 | NaN | NaN | NaN | 12.6182 | 119.3904 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 515.7124 | NaN | 20.7063 | NaN | 14.8587
2922.1292 | 12.7295 | 12.3595 | 12.5863 | 12.8101 | 12.2995 | 12.5584 | 12.3112 | 12.1505 | NaN | NaN | NaN | 12.6359 | 125.4378 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 514.0642 | NaN | 17.4872 | NaN | 14.6513
2923.1292 | 12.738 | 12.3425 | 12.5827 | 12.8157 | 12.3679 | 12.5471 | 12.3107 | 12.1511 | NaN | NaN | NaN | 12.6091 | 125.763 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 515.1943 | NaN | 14.4373 | NaN | 12.8552
2924.1292 | 12.7438 | 12.3365 | 12.5886 | 12.7919 | 12.3195 | 12.5519 | 12.3057 | 12.1492 | NaN | NaN | NaN | 12.6435 | 128.0299 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 514.9581 | NaN | 12.6379 | NaN | 11.9921
2925.1292 | 12.7651 | 12.3593 | 12.5938 | 12.8242 | 12.2654 | 12.5537 | 12.3046 | 12.1517 | NaN | NaN | NaN | 12.6078 | 114.9004 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 515.5626 | NaN | 28.3191 | NaN | 15.5046
2926.1292 | 12.7076 | 12.3746 | 12.5926 | 12.8421 | 12.37 | 12.5571 | 12.3147 | 12.1561 | NaN | NaN | NaN | 12.6179 | 121.2788 | NaN | NaN | NaN | -11.285 | NaN | NaN | NaN | NaN | 515.1958 | NaN | 30.3766 | NaN | 14.6559
2927.1292 | 12.7412 | 12.3599 | 12.597 | 12.812 | 12.3279 | 12.5462 | 12.3067 | 12.1566 | NaN | NaN | NaN | 12.6271 | 118.9969 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.3551 | NaN | 32.5539 | NaN | 14.3639
2928.1292 | 12.7327 | 12.3679 | 12.5917 | 12.7921 | 12.3481 | 12.5502 | 12.3125 | 12.1575 | NaN | NaN | NaN | 12.6609 | 130.3607 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 516.4091 | NaN | 17.7312 | NaN | 14.8884
2929.1292 | 12.7383 | 12.4226 | 12.5941 | 12.9135 | 12.3598 | 12.5734 | 12.33 | 12.1633 | NaN | NaN | NaN | 12.6223 | 121.1309 | NaN | NaN | NaN | 7.2427 | NaN | NaN | NaN | NaN | 514.2319 | NaN | 20.5104 | NaN | 16.9893
2930.1292 | 12.7423 | 12.3761 | 12.5958 | 12.8096 | 12.3389 | 12.5567 | 12.3174 | 12.1662 | NaN | NaN | NaN | 12.6273 | 123.1839 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 516.7682 | NaN | 26.2186 | NaN | 13.8668
2931.1292 | 12.738 | 12.3644 | 12.5898 | 12.8679 | 12.3701 | 12.538 | 12.3116 | 12.1621 | NaN | NaN | NaN | 12.6544 | 115.2247 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 517.0233 | NaN | 16.2012 | NaN | 14.9404
2932.1292 | 12.7491 | 12.3257 | 12.5926 | 12.8185 | 12.3583 | 12.5141 | 12.3027 | 12.1639 | NaN | NaN | NaN | 12.6491 | 119.7904 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.9623 | NaN | 16.9828 | NaN | 15.472
2933.1292 | 12.7452 | 12.3427 | 12.5887 | 12.8086 | 12.3479 | 12.5312 | 12.3081 | 12.164 | NaN | NaN | NaN | 12.6113 | 126.2698 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 519.5444 | NaN | 23.1896 | NaN | 14.863
2934.1292 | 12.7494 | 12.4546 | 12.5927 | 12.8861 | 12.3803 | 12.5552 | 12.3076 | 12.1659 | NaN | NaN | NaN | 12.6392 | 120.7502 | NaN | NaN | NaN | 6.4579 | NaN | NaN | NaN | NaN | 520.322 | NaN | 22.3605 | NaN | 15.1116
2935.1292 | 12.7411 | 12.3367 | 12.5881 | 12.8438 | 12.3493 | 12.5149 | 12.298 | 12.162 | NaN | NaN | NaN | 12.6041 | 125.592 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 520.7035 | NaN | 18.657 | NaN | 14.3834
2936.1292 | 12.7469 | 12.3287 | 12.5878 | 12.8213 | 12.3702 | 12.5128 | 12.2931 | 12.1658 | NaN | NaN | NaN | 12.6254 | 124.7041 | NaN | NaN | NaN | -13.4544 | NaN | NaN | NaN | NaN | 518.0627 | NaN | 13.1439 | NaN | 12.9113
2937.1292 | 12.7461 | 12.4283 | 12.5838 | 12.8593 | 12.3953 | 12.5676 | 12.3285 | 12.1654 | NaN | NaN | NaN | 12.6563 | 126.1153 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 515.2257 | NaN | 22.5466 | NaN | 15.1437
2938.1292 | 12.7515 | 12.3378 | 12.5809 | 12.8965 | 12.3516 | 12.5253 | 12.3037 | 12.1644 | NaN | NaN | NaN | 12.6513 | 120.1481 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 517.8238 | NaN | 33.2204 | NaN | 14.3374
2939.1292 | 12.7618 | 12.3741 | 12.5864 | 12.8288 | 12.402 | 12.5298 | 12.3011 | 12.163 | NaN | NaN | NaN | 12.6372 | 121.5927 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 516.9887 | NaN | 31.7727 | NaN | 16.1676
2940.1292 | 12.7597 | 12.3499 | 12.5796 | 12.8327 | 12.3632 | 12.513 | 12.2969 | 12.1661 | NaN | NaN | NaN | 12.6225 | 126.0133 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 516.6485 | NaN | 25.5254 | NaN | 14.9106
2941.1292 | 12.7885 | 12.4302 | 12.5819 | 12.8836 | 12.3941 | 12.548 | 12.3116 | 12.1694 | NaN | NaN | NaN | 12.6389 | 120.8137 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 516.8565 | NaN | 14.5812 | NaN | 15.1435
2942.1292 | 12.7751 | 12.4411 | 12.5847 | 12.8414 | 12.395 | 12.5537 | 12.317 | 12.1696 | NaN | NaN | NaN | 12.6319 | 118.5378 | NaN | NaN | NaN | -7.0789 | NaN | NaN | NaN | NaN | 512.2364 | NaN | 28.2503 | NaN | 14.4841
2943.1292 | 12.7372 | 12.3669 | 12.5742 | 12.7987 | 12.3198 | 12.5112 | 12.297 | 12.1696 | NaN | NaN | NaN | 12.6267 | 123.5616 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 514.5134 | NaN | 14.0355 | NaN | 13.907
2944.1292 | 12.7447 | 12.419 | 12.5831 | 12.8086 | 12.3644 | 12.538 | 12.3124 | 12.1685 | NaN | NaN | NaN | 12.5905 | 125.7175 | NaN | NaN | NaN | -2.3384 | NaN | NaN | NaN | NaN | 519.1166 | NaN | 34.3015 | NaN | 13.3848
2945.1292 | 12.7402 | 12.4208 | 12.5834 | 12.7853 | 12.3947 | 12.5393 | 12.3165 | 12.1662 | NaN | NaN | NaN | 12.6094 | 130.6839 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 516.7163 | NaN | 13.7453 | NaN | 14.1354
2946.1292 | 12.7577 | 12.4268 | 12.5811 | 12.8295 | 12.3518 | 12.5365 | 12.3106 | 12.1706 | NaN | NaN | NaN | 12.6183 | 124.83 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 519.9663 | NaN | 38.3386 | NaN | 15.3597
2947.1292 | 12.7618 | 12.3694 | 12.5783 | 12.8121 | 12.3867 | 12.5091 | 12.3013 | 12.1794 | NaN | NaN | NaN | 12.627 | 139.6853 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 519.9607 | NaN | 17.8313 | NaN | 13.1468
2948.1292 | 12.7643 | 12.3743 | 12.5801 | 12.8525 | 12.2806 | 12.5097 | 12.3019 | 12.1753 | NaN | NaN | NaN | 12.614 | 121.4679 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 520.3059 | NaN | 22.2097 | NaN | 14.2639
2949.1292 | 12.7639 | 12.3867 | 12.5787 | 12.8177 | 12.3503 | 12.5259 | 12.3186 | 12.1708 | NaN | NaN | NaN | 12.6178 | 132.4233 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.9293 | NaN | 25.5926 | NaN | 13.5577
2950.1292 | 12.7591 | 12.3851 | 12.5778 | 12.808 | 12.3843 | 12.5348 | 12.3118 | 12.1751 | NaN | NaN | NaN | 12.6269 | 133.6172 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 521.0662 | NaN | 27.937 | NaN | 12.7143
2951.1292 | 12.7714 | 12.3833 | 12.5839 | 12.8527 | 12.3562 | 12.5206 | 12.3047 | 12.1712 | NaN | NaN | NaN | 12.6053 | 122.7216 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 519.5278 | NaN | 18.5893 | NaN | 13.7686
2952.1292 | 12.7634 | 12.3977 | 12.5794 | 12.8483 | 12.3392 | 12.5365 | 12.3163 | 12.1784 | NaN | NaN | NaN | 12.6216 | 118.5618 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 520.8395 | NaN | 22.2284 | NaN | 15.6798
2953.1292 | 12.766 | 12.3776 | 12.5804 | 12.8511 | 12.3862 | 12.5243 | 12.3082 | 12.1822 | NaN | NaN | NaN | 12.6099 | 136.2982 | NaN | NaN | NaN | -8.9288 | NaN | NaN | NaN | NaN | 518.586 | NaN | 33.3467 | NaN | 14.4891
2954.1292 | 12.7602 | 12.4123 | 12.5833 | 12.8555 | 12.3748 | 12.5518 | 12.3238 | 12.1773 | NaN | NaN | NaN | 12.6272 | 120.6783 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 519.5045 | NaN | 21.5907 | NaN | 15.0733
2955.1448 | 12.7637 | 12.4547 | 12.5823 | 12.8078 | 12.4139 | 12.5694 | 12.3259 | 12.1813 | NaN | NaN | NaN | 12.6305 | 123.498 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.4404 | NaN | 21.5089 | NaN | 14.426
2956.1292 | 12.7682 | 12.4065 | 12.5788 | 12.8264 | 12.4086 | 12.5341 | 12.3177 | 12.1789 | NaN | NaN | NaN | 12.6224 | 116.6564 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 520.7369 | NaN | 24.304 | NaN | 12.8236
2957.1292 | 12.776 | 12.395 | 12.5823 | 12.8619 | 12.332 | 12.5467 | 12.3246 | 12.181 | NaN | NaN | NaN | 12.6651 | 121.0959 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 521.3694 | NaN | 29.4683 | NaN | 14.6725
2958.1292 | 12.7991 | 12.3709 | 12.5822 | 12.8015 | 12.3744 | 12.5233 | 12.3157 | 12.1822 | NaN | NaN | NaN | 12.5994 | 132.1395 | NaN | NaN | NaN | -13.9818 | NaN | NaN | NaN | NaN | 519.345 | NaN | 28.0813 | NaN | 14.0787
2959.1292 | 12.7826 | 12.388 | 12.5845 | 12.8402 | 12.4103 | 12.5225 | 12.3183 | 12.1847 | NaN | NaN | NaN | 12.6592 | 124.4566 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 513.474 | NaN | 22.7109 | NaN | 17.0028
2960.1292 | 12.8574 | 12.3848 | 12.589 | 12.8254 | 12.4112 | 12.5424 | 12.3246 | 12.1834 | NaN | NaN | NaN | 12.6023 | 119.8521 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 506.9566 | NaN | 24.7847 | NaN | 19.7392
2961.1292 | 12.8314 | 12.4272 | 12.5816 | 12.7991 | 12.3427 | 12.5584 | 12.3318 | 12.1827 | NaN | NaN | NaN | 12.6011 | 122.5072 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 504.9486 | NaN | 11.5773 | NaN | 19.6784
2962.1292 | 12.8168 | 12.4019 | 12.5885 | 12.8117 | 12.3515 | 12.5238 | 12.3263 | 12.1817 | NaN | NaN | NaN | 12.597 | 125.2327 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 508.1155 | NaN | 16.5433 | NaN | 15.5384
2963.1292 | 12.8428 | 12.3911 | 12.5896 | 12.8157 | 12.4099 | 12.5223 | 12.3245 | 12.1824 | NaN | NaN | NaN | 12.6063 | 115.1689 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 510.8084 | NaN | 29.4421 | NaN | 15.6405
2964.1292 | 12.7871 | 12.3815 | 12.5874 | 12.8505 | 12.3996 | 12.5231 | 12.3264 | 12.1775 | NaN | NaN | NaN | 12.6021 | 127.2661 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 516.359 | NaN | 16.7461 | NaN | 13.8784
2965.1292 | 12.7778 | 12.4965 | 12.5883 | 12.7911 | 12.4087 | 12.5721 | 12.3447 | 12.1787 | NaN | NaN | NaN | 12.625 | 127.248 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 514.0197 | NaN | 33.005 | NaN | 15.8648
2966.1292 | 12.7817 | 12.3852 | 12.5904 | 12.884 | 12.3923 | 12.5441 | 12.328 | 12.1803 | NaN | NaN | NaN | 12.6426 | 121.5494 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 516.0438 | NaN | 25.7668 | NaN | 14.6889
2967.1292 | 12.8524 | 12.3894 | 12.5897 | 12.7877 | 12.3499 | 12.5432 | 12.3275 | 12.1844 | NaN | NaN | NaN | 12.5756 | 120.9804 | NaN | NaN | NaN | -3.7503 | NaN | NaN | NaN | NaN | 516.27 | NaN | 10.5763 | NaN | 14.7698
2968.1292 | 12.7676 | 12.3913 | 12.5912 | 12.8341 | 12.344 | 12.5356 | 12.319 | 12.1819 | NaN | NaN | NaN | 12.5902 | 122.6489 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 517.1483 | NaN | 25.2798 | NaN | 16.5217
2969.1292 | 12.7625 | 12.4226 | 12.5995 | 12.8026 | 12.349 | 12.5707 | 12.3471 | 12.1861 | NaN | NaN | NaN | 12.6098 | 123.2646 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 519.3792 | NaN | 14.5685 | NaN | 13.5433
2970.1292 | 12.7551 | 12.4056 | 12.5995 | 12.7965 | 12.4055 | 12.5429 | 12.3194 | 12.1837 | NaN | NaN | NaN | 12.6009 | 125.1647 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 514.8055 | NaN | 11.4488 | NaN | 14.2137
2971.1292 | 12.7641 | 12.4316 | 12.5926 | 12.8111 | 12.3895 | 12.5604 | 12.3347 | 12.1844 | NaN | NaN | NaN | 12.5625 | 120.7856 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 516.7103 | NaN | 25.0128 | NaN | 15.1368
2972.1292 | 12.7067 | 12.409 | 12.5907 | 12.8004 | 12.2667 | 12.5461 | 12.3307 | 12.1914 | NaN | NaN | NaN | 12.6007 | 117.3176 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 516.4301 | NaN | 36.6682 | NaN | 14.2995
2973.1292 | 12.8238 | 12.4032 | 12.5873 | 12.8686 | 12.3385 | 12.5444 | 12.3388 | 12.1921 | NaN | NaN | NaN | 12.5873 | 122.4294 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 516.8051 | NaN | 25.5778 | NaN | 15.4766
2974.1292 | 12.7381 | 12.4155 | 12.5794 | 12.8108 | 12.4038 | 12.5281 | 12.3246 | 12.1953 | NaN | NaN | NaN | 12.5868 | 127.8829 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 516.3616 | NaN | 28.3635 | NaN | 13.6037
2975.1292 | 12.735 | 12.4309 | 12.574 | 12.7946 | 12.3738 | 12.5482 | 12.3383 | 12.1909 | NaN | NaN | NaN | 12.6317 | 131.0935 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 515.4729 | NaN | 36.1004 | NaN | 14.8367
2976.1292 | 12.7405 | 12.4671 | 12.567 | 12.7922 | 12.3494 | 12.5508 | 12.3385 | 12.1899 | NaN | NaN | NaN | 12.5956 | 128.1753 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 515.7114 | NaN | 35.4808 | NaN | 13.1228
2977.1292 | 12.7373 | 12.5498 | 12.5646 | 12.7697 | 12.3935 | 12.5681 | 12.3511 | 12.1939 | NaN | NaN | NaN | 12.6027 | 123.7752 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 517.3721 | NaN | 31.8304 | NaN | 16.349
2978.1292 | 12.7314 | 12.4358 | 12.5606 | 12.8416 | 12.3262 | 12.5458 | 12.3385 | 12.1949 | NaN | NaN | NaN | 12.5823 | 129.2631 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 514.8783 | NaN | 24.5302 | NaN | 13.9231
2979.1292 | 12.7363 | 12.4314 | 12.5535 | 12.7913 | 12.4032 | 12.5413 | 12.3359 | 12.199 | NaN | NaN | NaN | 12.5838 | 129.6523 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 514.9891 | NaN | 21.6367 | NaN | 14.765
2980.1292 | 12.7334 | 12.475 | 12.5501 | 12.7825 | 12.3836 | 12.5525 | 12.3359 | 12.2023 | NaN | NaN | NaN | 12.5945 | 121.856 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 515.8329 | NaN | 25.906 | NaN | 13.8388
2981.1292 | 12.7252 | 12.4241 | 12.5493 | 12.8322 | 12.4014 | 12.5343 | 12.3313 | 12.2027 | NaN | NaN | NaN | 12.6385 | 135.5069 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.1137 | NaN | 19.1371 | NaN | 13.6352
2982.1292 | 12.7274 | 12.4142 | 12.5473 | 12.7927 | 12.3416 | 12.5284 | 12.3256 | 12.2066 | NaN | NaN | NaN | 12.5904 | 119.9556 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 517.6604 | NaN | 29.8551 | NaN | 13.7995
2983.1292 | 12.7112 | 12.5299 | 12.548 | 12.7784 | 12.3702 | 12.5955 | 12.3476 | 12.2143 | NaN | NaN | NaN | 12.6009 | 124.6121 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 516.8643 | NaN | 23.4576 | NaN | 14.2785
2984.1292 | 12.7291 | 12.4295 | 12.5528 | 12.799 | 12.3841 | 12.5385 | 12.3185 | 12.2126 | NaN | NaN | NaN | 12.5802 | 117.9541 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 517.1833 | NaN | 23.2884 | NaN | 15.0285
2985.1448 | 12.7427 | 12.4753 | 12.5573 | 12.7868 | 12.3101 | 12.5735 | 12.3454 | 12.209 | NaN | NaN | NaN | 12.5931 | 124.6404 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 517.01 | NaN | 27.8597 | NaN | 14.5809
2986.1292 | 12.7464 | 12.451 | 12.5526 | 12.7583 | 12.4266 | 12.5538 | 12.3403 | 12.2108 | NaN | NaN | NaN | 12.6053 | 114.1685 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.5783 | NaN | 25.8411 | NaN | 15.1095
2987.1292 | 12.7453 | 12.4039 | 12.5594 | 12.835 | 12.3308 | 12.5379 | 12.334 | 12.2142 | NaN | NaN | NaN | 12.6257 | 131.0477 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.7844 | NaN | 25.2948 | NaN | 15.9277
2988.1292 | 12.7584 | 12.4068 | 12.558 | 12.7903 | 12.3597 | 12.5439 | 12.3363 | 12.2109 | NaN | NaN | NaN | 12.6004 | 118.5462 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 521.774 | NaN | 10.096 | NaN | 19.3391
2989.1448 | 12.7649 | 12.4168 | 12.5561 | 12.7873 | 12.3858 | 12.5473 | 12.3407 | 12.2086 | NaN | NaN | NaN | 12.6308 | 119.5219 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.8019 | NaN | 15.0729 | NaN | 16.8751
2990.1292 | 12.7671 | 12.3765 | 12.5592 | 12.7978 | 12.3898 | 12.5287 | 12.3362 | 12.2133 | NaN | NaN | NaN | 12.6501 | 112.3819 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 520.1135 | NaN | 33.7708 | NaN | 15.2466
2991.1448 | 12.7126 | 12.3877 | 12.5587 | 12.7603 | 12.3714 | 12.5224 | 12.3325 | 12.2142 | NaN | NaN | NaN | 12.6143 | 132.2656 | NaN | NaN | NaN | -19.67 | NaN | NaN | NaN | NaN | 519.5822 | NaN | 18.0138 | NaN | 24.7174
2992.1292 | 12.7053 | 12.3947 | 12.5621 | 12.8343 | 12.3397 | 12.548 | 12.3508 | 12.2248 | NaN | NaN | NaN | 12.6082 | 127.9761 | NaN | NaN | NaN | -15.6651 | NaN | NaN | NaN | NaN | 519.2846 | NaN | 27.1081 | NaN | 14.0241
2993.1292 | 12.6957 | 12.4197 | 12.5683 | 12.8131 | 12.3994 | 12.5566 | 12.3531 | 12.2212 | NaN | NaN | NaN | 12.61 | 125.4693 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.0585 | NaN | 9.9363 | NaN | 14.554
2994.1292 | 12.7276 | 12.3788 | 12.5634 | 12.8003 | 12.3995 | 12.5517 | 12.333 | 12.2194 | NaN | NaN | NaN | 12.6254 | 127.569 | NaN | NaN | NaN | -18.2639 | NaN | NaN | NaN | NaN | 518.9324 | NaN | 10.0661 | NaN | 14.1755
2995.1292 | 12.6773 | 12.4397 | 12.5675 | 12.8087 | 12.3955 | 12.5677 | 12.3337 | 12.2242 | NaN | NaN | NaN | 12.6357 | 133.4114 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.2651 | NaN | 27.5842 | NaN | 14.6578
2996.1292 | 12.6917 | 12.3902 | 12.5638 | 12.8131 | 12.4204 | 12.5542 | 12.3312 | 12.2243 | NaN | NaN | NaN | 12.6024 | 112.9174 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 517.3823 | NaN | 18.4762 | NaN | 18.5145
2997.1292 | 12.6974 | 12.3639 | 12.5678 | 12.8045 | 12.4022 | 12.5392 | 12.3216 | 12.2279 | NaN | NaN | NaN | 12.6124 | 113.4996 | NaN | NaN | NaN | 2.7328 | NaN | NaN | NaN | NaN | 517.5414 | NaN | 24.7936 | NaN | 14.6833
2998.1292 | 12.6863 | 12.4 | 12.5713 | 12.7924 | 12.3484 | 12.5538 | 12.3263 | 12.2225 | NaN | NaN | NaN | 12.6233 | 122.685 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 517.0117 | NaN | 13.7394 | NaN | 15.3489
2999.1292 | 12.6865 | 12.3962 | 12.572 | 12.8041 | 12.3672 | 12.5478 | 12.3272 | 12.223 | NaN | NaN | NaN | 12.596 | 116.9123 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 513.6344 | NaN | 24.9581 | NaN | 14.2898
3000.1292 | 12.6817 | 12.3613 | 12.5738 | 12.763 | 12.3932 | 12.5411 | 12.3262 | 12.2251 | NaN | NaN | NaN | 12.6067 | 120.1748 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 514.0225 | NaN | 11.1135 | NaN | 13.488
3001.1292 | 12.6949 | 12.4158 | 12.5672 | 12.7919 | 12.3964 | 12.5655 | 12.3341 | 12.2285 | NaN | NaN | NaN | 12.6385 | 126.702 | NaN | NaN | NaN | -1.0137 | NaN | NaN | NaN | NaN | 511.1464 | NaN | 36.4856 | NaN | 19.5885
3002.1292 | 12.6947 | 12.4254 | 12.5692 | 12.8095 | 12.4139 | 12.5599 | 12.3364 | 12.2257 | NaN | NaN | NaN | 12.6036 | 129.9475 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 508.2058 | NaN | 30.5017 | NaN | 14.589
3003.1292 | 12.7136 | 12.4574 | 12.5717 | 12.8019 | 12.3617 | 12.5693 | 12.3364 | 12.2203 | NaN | NaN | NaN | 12.5716 | 120.4374 | NaN | NaN | NaN | -18.8417 | NaN | NaN | NaN | NaN | 513.6287 | NaN | 18.8252 | NaN | 14.2438
3004.1292 | 12.6938 | 12.3896 | 12.5659 | 12.788 | 12.4046 | 12.5437 | 12.3225 | 12.2317 | NaN | NaN | NaN | 12.579 | 130.7351 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 513.1073 | NaN | 25.3952 | NaN | 11.2707
3005.1292 | 12.7019 | 12.3663 | 12.5671 | 12.7894 | 12.3862 | 12.5394 | 12.3292 | 12.2338 | NaN | NaN | NaN | 12.5916 | 120.1932 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 515.3021 | NaN | 30.4112 | NaN | 14.3717
3006.1292 | 12.6951 | 12.4 | 12.5663 | 12.9248 | 12.3983 | 12.5612 | 12.3356 | 12.2297 | NaN | NaN | NaN | 12.6058 | 124.3135 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 515.4322 | NaN | 34.3226 | NaN | 13.6738
3007.1292 | 12.696 | 12.3727 | 12.5631 | 12.8746 | 12.3825 | 12.5394 | 12.324 | 12.2232 | NaN | NaN | NaN | 12.5778 | 127.3088 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 516.0253 | NaN | 12.1076 | NaN | 13.9271
3008.1292 | 12.7078 | 12.3839 | 12.5647 | 12.7901 | 12.3656 | 12.5541 | 12.3277 | 12.2302 | NaN | NaN | NaN | 12.6367 | 131.5623 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 512.1711 | NaN | 14.1583 | NaN | 20.4151
3009.1292 | 12.6834 | 12.4215 | 12.5656 | 12.7972 | 12.4069 | 12.5648 | 12.3384 | 12.2311 | NaN | NaN | NaN | 12.5751 | 115.0034 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 513.7174 | NaN | 11.2595 | NaN | 13.6149
3010.1292 | 12.7008 | 12.3959 | 12.5641 | 12.7761 | 12.3493 | 12.5612 | 12.3255 | 12.2227 | NaN | NaN | NaN | 12.6077 | 113.8305 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 513.396 | NaN | 27.5544 | NaN | 14.7694
3011.1292 | 12.7012 | 12.4254 | 12.5678 | 12.8397 | 12.2881 | 12.5931 | 12.3424 | 12.2269 | NaN | NaN | NaN | 12.579 | 120.185 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 511.8742 | NaN | 22.0397 | NaN | 13.7576
3012.1292 | 12.7421 | 12.3649 | 12.5584 | 12.7843 | 12.3704 | 12.5455 | 12.3205 | 12.2289 | NaN | NaN | NaN | 12.6032 | 115.8427 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 513.8102 | NaN | 22.822 | NaN | 13.6969
3013.1448 | 12.6917 | 12.3988 | 12.56 | 12.8108 | 12.289 | 12.576 | 12.3355 | 12.2335 | NaN | NaN | NaN | 12.5936 | 124.0407 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 513.9581 | NaN | 27.8316 | NaN | 13.817
3014.1292 | 12.7299 | 12.3671 | 12.5598 | 12.8401 | 12.3498 | 12.55 | 12.3329 | 12.2342 | NaN | NaN | NaN | 12.5633 | 118.2056 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 511.5749 | NaN | 33.7364 | NaN | 14.4247
3015.1292 | 12.7692 | 12.4257 | 12.5629 | 12.8315 | 12.2882 | 12.5705 | 12.3357 | 12.2272 | NaN | NaN | NaN | 12.57 | 129.7671 | NaN | NaN | NaN | -18.751 | NaN | NaN | NaN | NaN | 510.2274 | NaN | 12.4705 | NaN | 13.9211
3016.1292 | 12.6974 | 12.4353 | 12.5574 | 12.8324 | 12.3751 | 12.5762 | 12.3391 | 12.2225 | NaN | NaN | NaN | 12.5919 | 123.0098 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 509.4031 | NaN | 34.6267 | NaN | 15.6045
3017.1292 | 12.7169 | 12.3636 | 12.5659 | 12.8328 | 12.3793 | 12.5315 | 12.3249 | 12.2171 | NaN | NaN | NaN | 12.6198 | 131.1745 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 513.449 | NaN | 27.2693 | NaN | 15.0841
3018.1292 | 12.7301 | 12.4515 | 12.5583 | 12.861 | 12.3514 | 12.5812 | 12.3448 | 12.221 | NaN | NaN | NaN | 12.5895 | 125.9357 | NaN | NaN | NaN | -6.1307 | NaN | NaN | NaN | NaN | 511.6496 | NaN | 35.9483 | NaN | 25.74
3019.1292 | 12.733 | 12.3952 | 12.559 | 12.8188 | 12.3712 | 12.5547 | 12.3319 | 12.2172 | NaN | NaN | NaN | 12.5779 | 122.4248 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 509.9654 | NaN | 27.2265 | NaN | 21.4386
3020.1292 | 12.7291 | 12.3613 | 12.5642 | 12.877 | 12.3643 | 12.5425 | 12.3245 | 12.2136 | NaN | NaN | NaN | 12.5862 | 129.9564 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 509.5457 | NaN | 30.5743 | NaN | 13.3971
3021.1292 | 12.741 | 12.3507 | 12.5551 | 12.807 | 12.2898 | 12.5513 | 12.3249 | 12.21 | NaN | NaN | NaN | 12.5842 | 116.2007 | NaN | NaN | NaN | -0.6217 | NaN | NaN | NaN | NaN | 512.8454 | NaN | 27.76 | NaN | 16.7359
3022.1292 | 12.7527 | 12.37 | 12.5647 | 12.813 | 12.3537 | 12.5553 | 12.3254 | 12.2028 | NaN | NaN | NaN | 12.567 | 125.053 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 510.8663 | NaN | 23.775 | NaN | 18.526
3023.1292 | 12.7455 | 12.3876 | 12.5668 | 12.8118 | 12.3539 | 12.5667 | 12.3284 | 12.2027 | NaN | NaN | NaN | 12.6023 | 115.5478 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 512.668 | NaN | 32.6932 | NaN | 14.0161
3024.1292 | 12.7497 | 12.3805 | 12.5639 | 12.8077 | 12.3594 | 12.5598 | 12.3365 | 12.2022 | NaN | NaN | NaN | 12.6113 | 127.9356 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 510.4565 | NaN | 13.8745 | NaN | 23.111
3025.1292 | 12.8158 | 12.368 | 12.5614 | 12.8138 | 12.3753 | 12.5636 | 12.3298 | 12.2098 | NaN | NaN | NaN | 12.5645 | 127.6758 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 515.2405 | NaN | 17.8499 | NaN | 16.0077
3026.1292 | 12.7266 | 12.3511 | 12.5625 | 12.8082 | 12.3381 | 12.5627 | 12.3313 | 12.2015 | NaN | NaN | NaN | 12.572 | 125.3303 | NaN | NaN | NaN | -6.8872 | NaN | NaN | NaN | NaN | 511.265 | NaN | 21.932 | NaN | 12.5826
3027.1292 | 12.7319 | 12.385 | 12.5618 | 12.7708 | 12.3547 | 12.5718 | 12.3332 | 12.1963 | NaN | NaN | NaN | 12.5994 | 119.6862 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 512.1976 | NaN | 43.2349 | NaN | 15.313
3028.1292 | 12.7477 | 12.3414 | 12.5664 | 12.9184 | 12.384 | 12.5544 | 12.3318 | 12.1966 | NaN | NaN | NaN | 12.5911 | 115.3763 | NaN | NaN | NaN | 5.6864 | NaN | NaN | NaN | NaN | 512.431 | NaN | 10.5853 | NaN | 19.9108
3029.1292 | 12.7458 | 12.3515 | 12.564 | 12.8901 | 12.3528 | 12.5501 | 12.3278 | 12.2 | NaN | NaN | NaN | 12.5914 | 124.9374 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 515.4315 | NaN | 18.3685 | NaN | 14.0169
3030.1292 | 12.756 | 12.3478 | 12.5606 | 12.8278 | 12.3866 | 12.5575 | 12.3297 | 12.198 | NaN | NaN | NaN | 12.5897 | 124.0822 | NaN | NaN | NaN | -10.6766 | NaN | NaN | NaN | NaN | 515.758 | NaN | 10.715 | NaN | 19.8332
3031.1292 | 12.7616 | 12.3902 | 12.5588 | 12.8248 | 12.4116 | 12.5729 | 12.3389 | 12.1988 | NaN | NaN | NaN | 12.607 | 139.0432 | NaN | NaN | NaN | 0.3898 | NaN | NaN | NaN | NaN | 510.4703 | NaN | 29.1924 | NaN | 12.7996
3032.1292 | 12.7578 | 12.3699 | 12.5586 | 12.8084 | 12.3584 | 12.5571 | 12.3365 | 12.1984 | NaN | NaN | NaN | 12.6025 | 123.2768 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 512.3423 | NaN | 14.4335 | NaN | 14.4921
3033.1292 | 12.7628 | 12.3403 | 12.5645 | 12.7857 | 12.3498 | 12.534 | 12.3231 | 12.2003 | NaN | NaN | NaN | 12.5881 | 122.2046 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 514.3619 | NaN | 29.1654 | NaN | 14.1773
3034.1292 | 12.7541 | 12.3693 | 12.5568 | 12.8299 | 12.369 | 12.5541 | 12.3261 | 12.1946 | NaN | NaN | NaN | 12.5656 | 129.131 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 514.3068 | NaN | 37.0981 | NaN | 22.2407
3035.1292 | 12.7314 | 12.3828 | 12.5591 | 12.8165 | 12.377 | 12.5562 | 12.3367 | 12.1908 | NaN | NaN | NaN | 12.5982 | 126.9388 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 513.483 | NaN | 32.1592 | NaN | 20.4622
3036.1292 | 12.7312 | 12.3824 | 12.5663 | 12.8075 | 12.3387 | 12.5548 | 12.3256 | 12.1882 | NaN | NaN | NaN | 12.5837 | 127.9875 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 512.4397 | NaN | 20.0668 | NaN | 14.6823
3037.1292 | 12.7146 | 12.3933 | 12.5715 | 12.8074 | 12.3756 | 12.5614 | 12.3367 | 12.195 | NaN | NaN | NaN | 12.6282 | 121.7558 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 512.5471 | NaN | 19.5426 | NaN | 15.1216
3038.1292 | 12.7135 | 12.3645 | 12.566 | 12.848 | 12.2866 | 12.5493 | 12.322 | 12.1891 | NaN | NaN | NaN | 12.623 | 139.3029 | NaN | NaN | NaN | 9.5125 | NaN | NaN | NaN | NaN | 511.0968 | NaN | 23.4305 | NaN | 13.6814
3039.1292 | 12.753 | 12.3728 | 12.5624 | 12.83 | 12.3973 | 12.5478 | 12.3326 | 12.1833 | NaN | NaN | NaN | 12.6022 | 117.0975 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 510.6807 | NaN | 14.4721 | NaN | 13.6148
3040.1292 | 12.7276 | 12.3431 | 12.5692 | 12.8297 | 12.4019 | 12.5277 | 12.324 | 12.1816 | NaN | NaN | NaN | 12.6329 | 123.6974 | NaN | NaN | NaN | 3.2505 | NaN | NaN | NaN | NaN | 511.913 | NaN | 29.5578 | NaN | 13.8176
3041.1292 | 12.7841 | 12.3724 | 12.5673 | 12.8304 | 12.3439 | 12.5641 | 12.3351 | 12.1863 | NaN | NaN | NaN | 12.6044 | 126.3396 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 514.1037 | NaN | 19.575 | NaN | 17.5349
3042.1292 | 12.7297 | 12.4256 | 12.5608 | 12.8168 | 12.2962 | 12.5925 | 12.3497 | 12.187 | NaN | NaN | NaN | 12.5896 | 116.1852 | NaN | NaN | NaN | -9.9064 | NaN | NaN | NaN | NaN | 513.4961 | NaN | 16.924 | NaN | 17.4914
3043.1292 | 12.7421 | 12.3768 | 12.5672 | 12.8267 | 12.4054 | 12.5394 | 12.3224 | 12.1891 | NaN | NaN | NaN | 12.5958 | 123.0587 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 513.7776 | NaN | 18.466 | NaN | 14.4723
3044.1292 | 12.7472 | 12.403 | 12.5642 | 12.8462 | 12.2566 | 12.558 | 12.3312 | 12.1845 | NaN | NaN | NaN | 12.6575 | 122.4294 | NaN | NaN | NaN | -14.8252 | NaN | NaN | NaN | NaN | 514.3161 | NaN | 22.74 | NaN | 13.7528
3045.1292 | 12.7372 | 12.415 | 12.5578 | 12.7926 | 12.3423 | 12.5661 | 12.3343 | 12.1873 | NaN | NaN | NaN | 12.6074 | 122.0186 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 512.989 | NaN | 27.1951 | NaN | 15.3281
3046.1292 | 12.7247 | 12.4029 | 12.5642 | 12.8504 | 12.3293 | 12.5508 | 12.3397 | 12.1877 | NaN | NaN | NaN | 12.5956 | 119.5542 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 515.4435 | NaN | 22.047 | NaN | 14.0085
3047.1292 | 12.7149 | 12.4467 | 12.5696 | 12.8014 | 12.3672 | 12.5638 | 12.3372 | 12.1926 | NaN | NaN | NaN | 12.6024 | 136.9343 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 516.8626 | NaN | 18.9107 | NaN | 13.1046
3048.1292 | 12.7715 | 12.371 | 12.5677 | 12.8383 | 12.3162 | 12.5422 | 12.3308 | 12.1892 | NaN | NaN | NaN | 12.6013 | 120.6609 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 510.5592 | NaN | 13.5889 | NaN | 15.3551
3049.1292 | 12.8523 | 12.5183 | 12.5646 | 12.7833 | 12.2715 | 12.6316 | 12.3639 | 12.1927 | NaN | NaN | NaN | 12.622 | 119.2506 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 513.5528 | NaN | 13.7136 | NaN | 19.0921
3050.1292 | 12.7921 | 12.3892 | 12.5762 | 12.8562 | 12.3688 | 12.5332 | 12.3204 | 12.1988 | NaN | NaN | NaN | 12.5971 | 125.5453 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 513.0127 | NaN | 29.1921 | NaN | 17.2078
3051.1292 | 12.7677 | 12.4233 | 12.5685 | 12.8452 | 12.3946 | 12.5551 | 12.3392 | 12.1985 | NaN | NaN | NaN | 12.6162 | 122.6825 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 513.1286 | NaN | 20.3764 | NaN | 18.7097
3052.1292 | 12.7338 | 12.4239 | 12.562 | 12.7903 | 12.3639 | 12.5713 | 12.3437 | 12.1942 | NaN | NaN | NaN | 12.5703 | 136.4969 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 514.9917 | NaN | 13.4644 | NaN | 13.311
3053.1292 | 12.7406 | 12.451 | 12.5657 | 12.8176 | 12.3385 | 12.5747 | 12.3402 | 12.1971 | NaN | NaN | NaN | 12.6258 | 129.7992 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 515.1221 | NaN | 31.4081 | NaN | 14.8791
3054.1292 | 12.7396 | 12.3885 | 12.5657 | 12.8293 | 12.3743 | 12.5539 | 12.3292 | 12.2047 | NaN | NaN | NaN | 12.6093 | 131.9801 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 515.3723 | NaN | 23.4391 | NaN | 23.8604
3055.1292 | 12.7437 | 12.425 | 12.572 | 12.8418 | 12.33 | 12.5755 | 12.3417 | 12.1979 | NaN | NaN | NaN | 12.5836 | 135.6898 | NaN | NaN | NaN | 0.6706 | NaN | NaN | NaN | NaN | 512.1309 | NaN | 12.8972 | NaN | 13.9603
3056.1292 | 12.7387 | 12.4164 | 12.5648 | 12.8503 | 12.3784 | 12.5655 | 12.3248 | 12.1974 | NaN | NaN | NaN | 12.6363 | 121.1618 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 513.842 | NaN | 15.8881 | NaN | 15.6436
3057.1292 | 12.7492 | 12.4384 | 12.5648 | 12.8308 | 12.3751 | 12.5798 | 12.3374 | 12.1965 | NaN | NaN | NaN | 12.5829 | 129.6354 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 512.2591 | NaN | 19.8742 | NaN | 18.9897
3058.1292 | 12.8019 | 12.3799 | 12.5736 | 12.8484 | 12.3283 | 12.5504 | 12.3178 | 12.2026 | NaN | NaN | NaN | 12.6113 | 124.5813 | NaN | NaN | NaN | -14.5972 | NaN | NaN | NaN | NaN | 511.3641 | NaN | 28.4367 | NaN | 17.5939
3059.1292 | 12.7503 | 12.5048 | 12.5659 | 12.8111 | 12.3406 | 12.61 | 12.3488 | 12.209 | NaN | NaN | NaN | 12.6114 | 127.7219 | NaN | NaN | NaN | -2.9149 | NaN | NaN | NaN | NaN | 515.3787 | NaN | 13.8014 | NaN | 14.8479
3060.1292 | 12.7445 | 12.4146 | 12.5756 | 12.8437 | 12.2871 | 12.5787 | 12.3141 | 12.2049 | NaN | NaN | NaN | 12.6276 | 123.6997 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 514.414 | NaN | 29.1266 | NaN | 15.1051
3061.1292 | 12.7264 | 12.403 | 12.5723 | 12.8354 | 12.2847 | 12.5677 | 12.318 | 12.2025 | NaN | NaN | NaN | 12.6214 | 120.0206 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 513.099 | NaN | 22.6912 | NaN | 17.7305
3062.1292 | 12.7323 | 12.3719 | 12.5751 | 12.8329 | 12.3892 | 12.5583 | 12.3212 | 12.2032 | NaN | NaN | NaN | 12.6177 | 126.5159 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 513.7052 | NaN | 22.4946 | NaN | 14.8156
3063.1292 | 12.7363 | 12.4035 | 12.5731 | 12.7947 | 12.3137 | 12.5609 | 12.3295 | 12.2036 | NaN | NaN | NaN | 12.6332 | 135.7012 | NaN | NaN | NaN | 8.0051 | NaN | NaN | NaN | NaN | 511.4758 | NaN | 12.3689 | NaN | 20.214
3064.1292 | 12.7328 | 12.4151 | 12.5789 | 12.8504 | 12.3766 | 12.5767 | 12.3248 | 12.2027 | NaN | NaN | NaN | 12.6311 | 127.5432 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 511.8779 | NaN | 12.8335 | NaN | 15.1472
3065.1292 | 12.7301 | 12.394 | 12.576 | 12.841 | 12.3934 | 12.5602 | 12.3284 | 12.2167 | NaN | NaN | NaN | 12.5958 | 123.2118 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 514.4588 | NaN | 21.445 | NaN | 15.8152
3066.1292 | 12.7371 | 12.3778 | 12.5739 | 12.811 | 12.3324 | 12.5597 | 12.3303 | 12.2103 | NaN | NaN | NaN | 12.6263 | 124.3791 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 516.6983 | NaN | 22.1241 | NaN | 14.7865
3067.1292 | 12.7306 | 12.3697 | 12.5789 | 12.8434 | 12.3388 | 12.5452 | 12.3222 | 12.2177 | NaN | NaN | NaN | 12.6814 | 120.2838 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 516.2795 | NaN | 22.7981 | NaN | 23.4152
3068.1292 | 12.7367 | 12.3791 | 12.5689 | 12.8461 | 12.3642 | 12.5601 | 12.3184 | 12.2161 | NaN | NaN | NaN | 12.6441 | 120.1854 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 512.7635 | NaN | 26.4518 | NaN | 20.4151
3069.1292 | 12.7336 | 12.3567 | 12.5647 | 12.8481 | 12.3519 | 12.5501 | 12.3218 | 12.2133 | NaN | NaN | NaN | 12.658 | 123.1047 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 515.5108 | NaN | 29.7695 | NaN | 22.9124
3070.1292 | 12.7426 | 12.3769 | 12.568 | 12.8187 | 12.3819 | 12.556 | 12.3161 | 12.2149 | NaN | NaN | NaN | 12.6555 | 116.845 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 516.6177 | NaN | 34.199 | NaN | 14.1124
3071.1292 | 12.7408 | 12.4044 | 12.5671 | 12.8412 | 12.3919 | 12.5709 | 12.3256 | 12.2124 | NaN | NaN | NaN | 12.6763 | 132.6329 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 515.997 | NaN | 12.1457 | NaN | 15.5378
3072.1292 | 12.7541 | 12.4816 | 12.5758 | 12.8828 | 12.3615 | 12.6133 | 12.3418 | 12.2104 | NaN | NaN | NaN | 12.703 | 126.6968 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 513.1158 | NaN | 24.8679 | NaN | 13.5727
3073.1292 | 12.7368 | 12.4014 | 12.5707 | 12.8436 | 12.2855 | 12.5874 | 12.3188 | 12.2127 | NaN | NaN | NaN | 12.654 | 126.1263 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 514.3809 | NaN | 23.5579 | NaN | 17.2637
3074.1292 | 12.743 | 12.4594 | 12.5712 | 12.8332 | 12.3632 | 12.6173 | 12.3303 | 12.2034 | NaN | NaN | NaN | 12.6549 | 113.1914 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 515.393 | NaN | 13.4942 | NaN | 12.8721
3075.1292 | 12.7544 | 12.4224 | 12.571 | 12.8448 | 12.3564 | 12.6055 | 12.3391 | 12.2026 | NaN | NaN | NaN | 12.6308 | 130.9794 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 511.6137 | NaN | 25.3752 | NaN | 8.1403
3076.1292 | 12.745 | 12.3595 | 12.5716 | 12.8693 | 12.399 | 12.577 | 12.3251 | 12.2061 | NaN | NaN | NaN | 12.6207 | 115.5283 | NaN | NaN | NaN | -5.8839 | NaN | NaN | NaN | NaN | 512.0108 | NaN | 17.6394 | NaN | 23.915
3077.1292 | 12.7406 | 12.4784 | 12.5719 | 12.8565 | 12.2877 | 12.6363 | 12.3381 | 12.1988 | NaN | NaN | NaN | 12.6174 | 121.1751 | NaN | NaN | NaN | 3.7318 | NaN | NaN | NaN | NaN | 511.0418 | NaN | 33.2432 | NaN | 16.0312
3078.1292 | 12.7548 | 12.4454 | 12.5683 | 12.8417 | 12.3065 | 12.6215 | 12.3421 | 12.2052 | NaN | NaN | NaN | 12.6735 | 121.6735 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 513.2939 | NaN | 26.3615 | NaN | 20.6243
3079.1292 | 12.7954 | 12.3648 | 12.5775 | 12.8442 | 12.3546 | 12.5763 | 12.3132 | 12.2035 | NaN | NaN | NaN | 12.615 | 121.1482 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 515.0722 | NaN | 15.7294 | NaN | 17.725
3080.1292 | 12.7444 | 12.3458 | 12.5786 | 12.8381 | 12.3643 | 12.5695 | 12.3162 | 12.2119 | NaN | NaN | NaN | 12.6802 | 134.2309 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 513.8114 | NaN | 30.481 | NaN | 12.4074
3081.1292 | 12.741 | 12.3734 | 12.5776 | 12.8882 | 12.3893 | 12.5652 | 12.3116 | 12.2083 | NaN | NaN | NaN | 12.6508 | 116.0682 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 517.1705 | NaN | 15.7743 | NaN | 15.5707
3082.1292 | 12.7349 | 12.3904 | 12.5645 | 12.8267 | 12.2882 | 12.596 | 12.3217 | 12.2074 | NaN | NaN | NaN | 12.611 | 119.7155 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 513.8863 | NaN | 15.2892 | NaN | 15.5897
3083.1292 | 12.7453 | 12.3662 | 12.568 | 12.9427 | 12.3921 | 12.5622 | 12.3142 | 12.213 | NaN | NaN | NaN | 12.6469 | 119.9149 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 512.3631 | NaN | 20.7417 | NaN | 23.565
3084.1292 | 12.7499 | 12.425 | 12.5693 | 12.8475 | 12.4089 | 12.5912 | 12.3291 | 12.2131 | NaN | NaN | NaN | 12.6122 | 133.2901 | NaN | NaN | NaN | -10.0805 | NaN | NaN | NaN | NaN | 511.4159 | NaN | 19.0157 | NaN | 15.4664
3085.1292 | 12.7693 | 12.3488 | 12.5649 | 12.8416 | 12.3305 | 12.5445 | 12.3155 | 12.2135 | NaN | NaN | NaN | 12.6376 | 123.4775 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 514.8276 | NaN | 15.7625 | NaN | 21.9764
3086.1292 | 12.817 | 12.3465 | 12.5622 | 12.8537 | 12.3872 | 12.5445 | 12.3138 | 12.2222 | NaN | NaN | NaN | 12.6108 | 118.3998 | NaN | NaN | NaN | -3.3649 | NaN | NaN | NaN | NaN | 512.6603 | NaN | 16.0236 | NaN | 13.8301
3087.1292 | 12.7675 | 12.3846 | 12.5649 | 12.8307 | 12.3695 | 12.5747 | 12.3237 | 12.2157 | NaN | NaN | NaN | 12.6329 | 111.4845 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 516.081 | NaN | 31.3904 | NaN | 17.2967
3088.1292 | 12.7225 | 12.3661 | 12.5665 | 12.8465 | 12.3593 | 12.5557 | 12.32 | 12.2067 | NaN | NaN | NaN | 12.6137 | 123.792 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 513.1711 | NaN | 32.1286 | NaN | 16.7455
3089.1292 | 12.7204 | 12.3924 | 12.5677 | 12.8435 | 12.4059 | 12.5836 | 12.3336 | 12.217 | NaN | NaN | NaN | 12.6154 | 118.8695 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.4239 | NaN | 21.3085 | NaN | 14.5395
3090.1292 | 12.7207 | 12.3889 | 12.5625 | 12.8519 | 12.3358 | 12.5892 | 12.3328 | 12.2178 | NaN | NaN | NaN | 12.6333 | 121.4803 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 516.7306 | NaN | 23.4653 | NaN | 13.5954
3091.1292 | 12.7247 | 12.391 | 12.562 | 12.8719 | 12.3136 | 12.572 | 12.3296 | 12.2116 | NaN | NaN | NaN | 12.6166 | 127.8475 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.0216 | NaN | 40.1044 | NaN | 18.7801
3092.1292 | 12.7317 | 12.3675 | 12.5657 | 12.8977 | 12.4227 | 12.5613 | 12.3242 | 12.2131 | NaN | NaN | NaN | 12.6095 | 122.4569 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 519.3162 | NaN | 33.3424 | NaN | 15.9039
3093.1292 | 12.7353 | 12.367 | 12.5712 | 12.877 | 12.4239 | 12.5642 | 12.3223 | 12.2124 | NaN | NaN | NaN | 12.6226 | 122.9884 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 519.3693 | NaN | 15.8243 | NaN | 13.9113
3094.1292 | 12.731 | 12.341 | 12.5652 | 12.9092 | 12.4037 | 12.5446 | 12.3223 | 12.2219 | NaN | NaN | NaN | 12.6294 | 137.3605 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 522.2896 | NaN | 19.0793 | NaN | 13.2975
3095.1448 | 12.7101 | 12.4351 | 12.5648 | 12.8456 | 12.2505 | 12.6077 | 12.3353 | 12.2122 | NaN | NaN | NaN | 12.6077 | 118.7046 | NaN | NaN | NaN | -5.1552 | NaN | NaN | NaN | NaN | 518.165 | NaN | 19.7525 | NaN | 25.6147
3096.1292 | 12.7098 | 12.3753 | 12.5614 | 12.8481 | 12.3222 | 12.5623 | 12.3309 | 12.2159 | NaN | NaN | NaN | 12.6463 | 121.8966 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.3754 | NaN | 21.5476 | NaN | 13.77
3097.1292 | 12.7244 | 12.3327 | 12.5636 | 12.8277 | 12.3331 | 12.5454 | 12.3207 | 12.2182 | NaN | NaN | NaN | 12.6058 | 121.0432 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 522.6114 | NaN | 16.8216 | NaN | 21.7006
3098.1292 | 12.7302 | 12.3888 | 12.562 | 12.8292 | 12.4088 | 12.5569 | 12.3298 | 12.212 | NaN | NaN | NaN | 12.6199 | 131.6 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 520.3915 | NaN | 27.2442 | NaN | 19.0033
3099.1292 | 12.7671 | 12.406 | 12.5693 | 12.8728 | 12.3145 | 12.5853 | 12.3401 | 12.2125 | NaN | NaN | NaN | 12.6251 | 127.8769 | NaN | NaN | NaN | 1.934 | NaN | NaN | NaN | NaN | 520.3486 | NaN | 33.7828 | NaN | 15.2805
3100.1292 | 12.7311 | 12.4315 | 12.5625 | 12.8656 | 12.3777 | 12.5708 | 12.3337 | 12.2146 | NaN | NaN | NaN | 12.5937 | 125.1767 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 516.9433 | NaN | 12.3224 | NaN | 16.098
3101.1292 | 12.7718 | 12.3796 | 12.5718 | 12.844 | 12.342 | 12.5572 | 12.3292 | 12.2193 | NaN | NaN | NaN | 12.5844 | 113.6151 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 519.464 | NaN | 25.6975 | NaN | 21.5437
3102.1292 | 12.7406 | 12.4133 | 12.5738 | 12.8512 | 12.2831 | 12.5721 | 12.334 | 12.221 | NaN | NaN | NaN | 12.6324 | 131.8482 | NaN | NaN | NaN | -18.6131 | NaN | NaN | NaN | NaN | 519.5506 | NaN | 30.1495 | NaN | 14.7126
3103.1292 | 12.7373 | 12.412 | 12.5732 | 12.8354 | 12.3859 | 12.5736 | 12.3391 | 12.2211 | NaN | NaN | NaN | 12.6252 | 117.286 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 514.5536 | NaN | 18.2961 | NaN | 18.3055
3104.1292 | 12.7413 | 12.3698 | 12.5743 | 12.8498 | 12.4108 | 12.5489 | 12.3331 | 12.2224 | NaN | NaN | NaN | 12.6124 | 123.1222 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 513.0544 | NaN | 28.864 | NaN | 23.8954
3105.1292 | 12.7444 | 12.3959 | 12.5746 | 12.8317 | 12.2884 | 12.5564 | 12.3296 | 12.221 | NaN | NaN | NaN | 12.622 | 127.0121 | NaN | NaN | NaN | -3.0073 | NaN | NaN | NaN | NaN | 518.8732 | NaN | 14.1226 | NaN | 21.4907
3106.1292 | 12.7499 | 12.4076 | 12.5803 | 12.8267 | 12.3397 | 12.5783 | 12.3288 | 12.2272 | NaN | NaN | NaN | 12.643 | 119.981 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 514.9522 | NaN | 26.2853 | NaN | 15.5845
3107.1292 | 12.745 | 12.4309 | 12.5742 | 12.8128 | 12.3979 | 12.5489 | 12.3232 | 12.2305 | NaN | NaN | NaN | 12.5976 | 114.2925 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 517.2374 | NaN | 12.9774 | NaN | 19.9504
3108.1292 | 12.7469 | 12.4664 | 12.5782 | 12.7698 | 12.3604 | 12.5815 | 12.3492 | 12.2295 | NaN | NaN | NaN | 12.6433 | 124.3968 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 517.165 | NaN | 39.8351 | NaN | 21.5484
3109.1292 | 12.755 | 12.4096 | 12.5696 | 12.8285 | 12.3119 | 12.5567 | 12.3351 | 12.2233 | NaN | NaN | NaN | 12.6032 | 126.3222 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.3284 | NaN | 18.5551 | NaN | 15.6134
3110.1292 | 12.755 | 12.3893 | 12.5765 | 12.8363 | 12.3856 | 12.5433 | 12.3427 | 12.223 | NaN | NaN | NaN | 12.6056 | 127.1848 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 520.8219 | NaN | 25.1273 | NaN | 13.2437
3111.1292 | 12.7489 | 12.4285 | 12.5785 | 12.8056 | 12.3716 | 12.5587 | 12.3371 | 12.2176 | NaN | NaN | NaN | 12.6367 | 128.2846 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 522.5082 | NaN | 17.7179 | NaN | 13.5864
3112.1292 | 12.7457 | 12.3952 | 12.578 | 12.8098 | 12.4068 | 12.5421 | 12.3391 | 12.2187 | NaN | NaN | NaN | 12.6251 | 113.6917 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 520.0936 | NaN | 10.0766 | NaN | 15.2319
3113.1292 | 12.7392 | 12.4336 | 12.5772 | 12.8031 | 12.3796 | 12.5454 | 12.3467 | 12.222 | NaN | NaN | NaN | 12.5948 | 135.6746 | NaN | NaN | NaN | -17.5446 | NaN | NaN | NaN | NaN | 521.898 | NaN | 20.8848 | NaN | 12.9055
3114.1292 | 12.736 | 12.3575 | 12.5745 | 12.7537 | 12.3621 | 12.5253 | 12.335 | 12.2212 | NaN | NaN | NaN | 12.6143 | 129.6257 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 525.7545 | NaN | 10.594 | NaN | 12.2187
3115.1292 | 12.7403 | 12.4106 | 12.5828 | 12.7606 | 12.3437 | 12.5572 | 12.3483 | 12.2231 | NaN | NaN | NaN | 12.6341 | 127.48 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 521.52 | NaN | 21.6044 | NaN | 16.7022
3116.1292 | 12.7534 | 12.4445 | 12.5845 | 12.7663 | 12.3292 | 12.5828 | 12.3667 | 12.2186 | NaN | NaN | NaN | 12.6243 | 124.1867 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 521.269 | NaN | 19.8119 | NaN | 13.5175
3117.1292 | 12.8151 | 12.4069 | 12.587 | 12.743 | 12.3417 | 12.5578 | 12.3556 | 12.211 | NaN | NaN | NaN | 12.6142 | 128.7443 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 524.6195 | NaN | 24.2088 | NaN | 13.1307
3118.1292 | 12.7565 | 12.3758 | 12.5876 | 12.7928 | 12.374 | 12.542 | 12.3405 | 12.2167 | NaN | NaN | NaN | 12.6005 | 117.8265 | NaN | NaN | NaN | -6.7555 | NaN | NaN | NaN | NaN | 523.3565 | NaN | 14.4992 | NaN | 14.5314
3119.1292 | 12.7472 | 12.3982 | 12.5914 | 12.7835 | 12.3468 | 12.5384 | 12.3457 | 12.2176 | NaN | NaN | NaN | 12.6236 | 127.0368 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 521.5305 | NaN | 30.3247 | NaN | 16.0446
3120.1292 | 12.7463 | 12.384 | 12.5872 | 12.8656 | 12.3147 | 12.5418 | 12.3479 | 12.2163 | NaN | NaN | NaN | 12.5896 | 125.9818 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 523.0021 | NaN | 36.3411 | NaN | 13.961
3121.1292 | 12.7961 | 12.3715 | 12.585 | 12.7835 | 12.3688 | 12.5313 | 12.3312 | 12.22 | NaN | NaN | NaN | 12.6088 | 126.9433 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 520.0859 | NaN | 20.5755 | NaN | 21.467
3122.1292 | 12.8274 | 12.3675 | 12.5941 | 12.7661 | 12.3635 | 12.5344 | 12.334 | 12.2193 | NaN | NaN | NaN | 12.6024 | 121.6742 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 521.719 | NaN | 34.3576 | NaN | 23.9382
3123.1292 | 12.7441 | 12.3948 | 12.594 | 12.7729 | 12.3568 | 12.5412 | 12.3351 | 12.2195 | NaN | NaN | NaN | 12.6202 | 123.7846 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 519.8862 | NaN | 14.6981 | NaN | 16.5784
3124.1292 | 12.7547 | 12.3776 | 12.5879 | 12.7836 | 12.3586 | 12.5356 | 12.3329 | 12.2292 | NaN | NaN | NaN | 12.6227 | 122.4233 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 524.534 | NaN | 27.6444 | NaN | 16.9106
3125.1292 | 12.7383 | 12.4332 | 12.5882 | 12.7695 | 12.2744 | 12.5722 | 12.3518 | 12.2187 | NaN | NaN | NaN | 12.5991 | 124.0107 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 522.0591 | NaN | 34.1172 | NaN | 18.6794
3126.1292 | 12.7464 | 12.4201 | 12.5866 | 12.7834 | 12.3663 | 12.5481 | 12.3399 | 12.2166 | NaN | NaN | NaN | 12.5935 | 120.2239 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 521.4948 | NaN | 18.0554 | NaN | 19.9324
3127.1292 | 12.7502 | 12.39 | 12.5858 | 12.7504 | 12.3612 | 12.5495 | 12.3479 | 12.2196 | NaN | NaN | NaN | 12.5795 | 118.8473 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 519.8574 | NaN | 39.283 | NaN | 19.9427
3128.1292 | 12.7598 | 12.4712 | 12.5873 | 12.7669 | 12.4052 | 12.5655 | 12.3692 | 12.2125 | NaN | NaN | NaN | 12.5756 | 127.3001 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 514.9583 | NaN | 9.0978 | NaN | 12.5032
3129.1292 | 12.7612 | 12.4089 | 12.5885 | 12.8101 | 12.4269 | 12.5419 | 12.3463 | 12.2175 | NaN | NaN | NaN | 12.6111 | 118.4308 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 517.0807 | NaN | 29.8465 | NaN | 22.133
3130.1292 | 12.8491 | 12.3848 | 12.5909 | 12.8197 | 12.3122 | 12.5324 | 12.3356 | 12.2092 | NaN | NaN | NaN | 12.5844 | 119.8948 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 522.0276 | NaN | 10.3467 | NaN | 21.8976
3131.1292 | 12.8317 | 12.3968 | 12.5907 | 12.7937 | 12.3864 | 12.5317 | 12.3409 | 12.2097 | NaN | NaN | NaN | 12.5802 | 124.8517 | NaN | NaN | NaN | -13.8808 | NaN | NaN | NaN | NaN | 520.064 | NaN | 28.594 | NaN | 23.5951
3132.1292 | 12.7824 | 12.448 | 12.5906 | 12.78 | 12.2973 | 12.5762 | 12.3498 | 12.2106 | NaN | NaN | NaN | 12.5948 | 125.1071 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 521.4649 | NaN | 9.6231 | NaN | 28.6052
3133.1292 | 12.751 | 12.4223 | 12.5881 | 12.8476 | 12.3669 | 12.5362 | 12.3407 | 12.2105 | NaN | NaN | NaN | 12.5935 | 124.391 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 520.7736 | NaN | 27.3719 | NaN | 26.6478
3134.1292 | 12.8621 | 12.4208 | 12.589 | 12.7667 | 12.3746 | 12.5469 | 12.3389 | 12.2085 | NaN | NaN | NaN | 12.5965 | 127.8315 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 522.4667 | NaN | 12.9471 | NaN | 21.8634
3135.1292 | 12.7916 | 12.428 | 12.5948 | 12.7947 | 12.3509 | 12.5587 | 12.339 | 12.205 | NaN | NaN | NaN | 12.5885 | 113.975 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 523.4281 | NaN | 30.3291 | NaN | 20.1767
3136.1292 | 12.7483 | 12.4715 | 12.5877 | 12.7778 | 12.3875 | 12.5929 | 12.3677 | 12.2024 | NaN | NaN | NaN | 12.585 | 123.7258 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 522.2193 | NaN | 36.3696 | NaN | 11.5792
3137.1292 | 12.7615 | 12.3839 | 12.5957 | 12.7515 | 12.3496 | 12.5457 | 12.3437 | 12.2032 | NaN | NaN | NaN | 12.5918 | 120.2059 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 525.1601 | NaN | 10.677 | NaN | 21.1669
3138.1292 | 12.7374 | 12.3679 | 12.5972 | 12.8111 | 12.3779 | 12.5544 | 12.344 | 12.1995 | NaN | NaN | NaN | 12.5945 | 128.5786 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 527.2013 | NaN | 23.3691 | NaN | 19.455
3139.1292 | 12.738 | 12.3646 | 12.601 | 12.8193 | 12.3368 | 12.5511 | 12.341 | 12.1919 | NaN | NaN | NaN | 12.5795 | 130.8072 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 523.5709 | NaN | 8.763 | NaN | 6.5083
3140.1292 | 12.7404 | 12.3945 | 12.5992 | 12.78 | 12.3328 | 12.5571 | 12.3401 | 12.1903 | NaN | NaN | NaN | 12.5702 | 128.6836 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 524.853 | NaN | 22.4038 | NaN | 14.6248
3141.1292 | 12.7576 | 12.4008 | 12.5956 | 12.7562 | 12.3909 | 12.5696 | 12.3415 | 12.1958 | NaN | NaN | NaN | 12.5638 | 115.8944 | NaN | NaN | NaN | 3.5035 | NaN | NaN | NaN | NaN | 525.8941 | NaN | 25.7987 | NaN | 17.1756
3142.1292 | 12.7615 | 12.4051 | 12.5973 | 12.7591 | 12.3811 | 12.5717 | 12.3327 | 12.1951 | NaN | NaN | NaN | 12.5861 | 130.1206 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 526.2391 | NaN | 9.9161 | NaN | 17.8748
3143.1292 | 12.8311 | 12.3898 | 12.6028 | 12.7407 | 12.3933 | 12.5772 | 12.3423 | 12.1937 | NaN | NaN | NaN | 12.5467 | 118.5227 | NaN | NaN | NaN | 2.3608 | NaN | NaN | NaN | NaN | 526.6163 | NaN | 16.0035 | NaN | 21.9066
3144.1292 | 12.7511 | 12.3952 | 12.5967 | 12.8102 | 12.4225 | 12.5702 | 12.3445 | 12.2021 | NaN | NaN | NaN | 12.5795 | 139.7239 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 524.6338 | NaN | 24.4327 | NaN | 15.8701
3145.1292 | 12.7487 | 12.3983 | 12.5979 | 12.7967 | 12.3741 | 12.5814 | 12.3469 | 12.1972 | NaN | NaN | NaN | 12.5556 | 128.1484 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 524.0131 | NaN | 27.4978 | NaN | 16.4189
3146.1292 | 12.8405 | 12.4016 | 12.5914 | 12.7754 | 12.3442 | 12.583 | 12.3421 | 12.1928 | NaN | NaN | NaN | 12.553 | 127.7788 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 524.8571 | NaN | 21.7684 | NaN | 23.8659
3147.1292 | 12.7198 | 12.3856 | 12.6041 | 12.7785 | 12.3982 | 12.5661 | 12.341 | 12.1964 | NaN | NaN | NaN | 12.6119 | 123.3443 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 526.271 | NaN | 8.7212 | NaN | 10.4965
3148.1292 | 12.8436 | 12.3487 | 12.5998 | 12.7957 | 12.343 | 12.569 | 12.3429 | 12.1914 | NaN | NaN | NaN | 12.594 | 128.2375 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 523.3619 | NaN | 22.8577 | NaN | 22.0542
3149.1292 | 12.7436 | 12.3946 | 12.6014 | 12.7999 | 12.3828 | 12.5782 | 12.3411 | 12.194 | NaN | NaN | NaN | 12.5844 | 125.5192 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 523.6808 | NaN | 14.9742 | NaN | 13.0792
3150.1292 | 12.75 | 12.4101 | 12.6016 | 12.7672 | 12.3134 | 12.5997 | 12.3581 | 12.1973 | NaN | NaN | NaN | 12.5789 | 127.5657 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 522.465 | NaN | 26.4306 | NaN | 20.2927
3151.1292 | 12.7654 | 12.3907 | 12.5956 | 12.8076 | 12.3285 | 12.5859 | 12.3438 | 12.1941 | NaN | NaN | NaN | 12.5824 | 132.5721 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 524.0996 | NaN | 10.5142 | NaN | 22.7105
3152.1292 | 12.7554 | 12.3964 | 12.6035 | 12.8201 | 12.2932 | 12.5927 | 12.3417 | 12.1972 | NaN | NaN | NaN | 12.5953 | 121.1625 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 521.5115 | NaN | 28.355 | NaN | 13.5968
3153.1292 | 12.7509 | 12.406 | 12.6023 | 12.8029 | 12.4221 | 12.5879 | 12.3413 | 12.1912 | NaN | NaN | NaN | 12.5889 | 123.7403 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 521.9068 | NaN | 33.4439 | NaN | 15.0705
3154.1292 | 12.7431 | 12.3602 | 12.5923 | 12.7939 | 12.3551 | 12.5799 | 12.3413 | 12.1901 | NaN | NaN | NaN | 12.5729 | 129.0735 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 525.2157 | NaN | 10.9555 | NaN | 22.5743
3155.1292 | 12.7792 | 12.4063 | 12.6036 | 12.8464 | 12.3602 | 12.598 | 12.3481 | 12.1947 | NaN | NaN | NaN | 12.5799 | 112.2336 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 524.3385 | NaN | 32.2438 | NaN | 22.7637
3156.1292 | 12.7459 | 12.3756 | 12.5963 | 12.8193 | 12.4061 | 12.5735 | 12.3379 | 12.1976 | NaN | NaN | NaN | 12.5809 | 130.0839 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 524.2557 | NaN | 18.2157 | NaN | 18.4993
3157.1292 | 12.7539 | 12.3763 | 12.5993 | 12.809 | 12.305 | 12.5842 | 12.3464 | 12.1959 | NaN | NaN | NaN | 12.5949 | 129.067 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 525.4527 | NaN | 23.9741 | NaN | 29.6749
3158.1292 | 12.7564 | 12.3974 | 12.598 | 12.8201 | 12.3853 | 12.5855 | 12.3451 | 12.2044 | NaN | NaN | NaN | 12.5812 | 124.8576 | NaN | NaN | NaN | -15.5001 | NaN | NaN | NaN | NaN | 525.0324 | NaN | 26.1697 | NaN | 18.9223
3159.1292 | 12.7539 | 12.439 | 12.5957 | 12.8202 | 12.3573 | 12.5985 | 12.3609 | 12.2045 | NaN | NaN | NaN | 12.6009 | 122.5903 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 524.6288 | NaN | 23.5259 | NaN | 16.9027
3160.1292 | 12.7469 | 12.38 | 12.588 | 12.8728 | 12.3849 | 12.5696 | 12.3392 | 12.1997 | NaN | NaN | NaN | 12.6092 | 129.9028 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 524.7041 | NaN | 9.3543 | NaN | 16.8808
3161.1292 | 12.7516 | 12.42 | 12.5841 | 12.8286 | 12.3584 | 12.5872 | 12.351 | 12.1972 | NaN | NaN | NaN | 12.5807 | 132.1239 | NaN | NaN | NaN | -3.227 | NaN | NaN | NaN | NaN | 524.9611 | NaN | 9.424 | NaN | 15.1986
3162.1292 | 12.7503 | 12.3761 | 12.5922 | 12.7954 | 12.3898 | 12.5702 | 12.3522 | 12.1945 | NaN | NaN | NaN | 12.5866 | 120.2305 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -15.1298 | 521.3313 | NaN | 12.4958 | NaN | 14.6147
3163.1292 | 12.7438 | 12.4435 | 12.5971 | 12.8223 | 12.389 | 12.5949 | 12.3585 | 12.1873 | NaN | NaN | NaN | 12.5696 | 125.431 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -14.8528 | 520.9642 | NaN | 22.6135 | NaN | 21.065
3164.1292 | 12.7633 | 12.4138 | 12.5991 | 12.7988 | 12.3373 | 12.5816 | 12.3496 | 12.189 | NaN | NaN | NaN | 12.5936 | 122.0728 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 513.6946 | NaN | 43.8506 | NaN | 17.4663
3165.1292 | 12.7595 | 12.5143 | 12.5906 | 12.7862 | 12.4025 | 12.6027 | 12.3845 | 12.1881 | NaN | NaN | NaN | 12.7284 | 117.9806 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 517.5531 | NaN | 15.013 | NaN | 18.3276
3166.1292 | 12.7739 | 12.419 | 12.5902 | 12.7825 | 12.3432 | 12.5875 | 12.3533 | 12.1823 | NaN | NaN | NaN | 12.5675 | 122.1082 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 519.4923 | NaN | 46.4545 | NaN | 20.8154
3167.1292 | 12.779 | 12.382 | 12.5946 | 12.7718 | 12.4036 | 12.5826 | 12.3526 | 12.1876 | NaN | NaN | NaN | 12.5785 | 117.9449 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 521.8323 | NaN | 21.8388 | NaN | 22.3774
3168.1292 | 12.7777 | 12.4042 | 12.5933 | 12.8192 | 12.3043 | 12.5966 | 12.3621 | 12.1894 | NaN | NaN | NaN | 12.5691 | 129.058 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 521.547 | NaN | 13.9161 | NaN | 26.7162
3169.1292 | 12.8546 | 12.4154 | 12.5924 | 12.8488 | 12.2707 | 12.6104 | 12.3633 | 12.1899 | NaN | NaN | NaN | 12.5964 | 121.7269 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 520.3877 | NaN | 30.4715 | NaN | 18.4512
3170.1292 | 12.8045 | 12.4078 | 12.5938 | 12.8007 | 12.3141 | 12.5988 | 12.3653 | 12.1916 | NaN | NaN | NaN | 12.562 | 130.8018 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 521.9231 | NaN | 13.0166 | NaN | 23.869
3171.1292 | 12.774 | 12.4112 | 12.5963 | 12.805 | 12.3044 | 12.585 | 12.3551 | 12.2027 | NaN | NaN | NaN | 12.5924 | 121.8873 | NaN | NaN | NaN | -7.0424 | NaN | NaN | NaN | NaN | 522.1716 | NaN | 19.4806 | NaN | 18.9418
3172.1292 | 12.8211 | 12.4277 | 12.5978 | 12.7929 | 12.299 | 12.6152 | 12.3719 | 12.1906 | NaN | NaN | NaN | 12.5715 | 127.0002 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 524.6277 | NaN | 26.9148 | NaN | 14.5763
3173.1292 | 12.7601 | 12.42 | 12.5963 | 12.7542 | 12.3268 | 12.6069 | 12.3579 | 12.2022 | NaN | NaN | NaN | 12.6833 | 124.095 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 524.3576 | NaN | 27.3207 | NaN | 22.9936
3174.1292 | 12.7636 | 12.4308 | 12.6011 | 12.7758 | 12.3166 | 12.6023 | 12.3592 | 12.2034 | NaN | NaN | NaN | 12.5641 | 131.1849 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 525.2414 | NaN | 17.4855 | NaN | 18.8283
3175.1292 | 12.7724 | 12.3898 | 12.6037 | 12.7826 | 12.3238 | 12.5838 | 12.3611 | 12.2037 | NaN | NaN | NaN | 12.6127 | 117.635 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 524.1534 | NaN | 33.9225 | NaN | 16.2584
3176.1292 | 12.7722 | 12.4182 | 12.6014 | 12.7885 | 12.3711 | 12.5973 | 12.3688 | 12.2064 | NaN | NaN | NaN | 12.5859 | 128.33 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 526.9142 | NaN | 14.8036 | NaN | 15.5356
3177.1292 | 12.7802 | 12.4954 | 12.5934 | 12.7676 | 12.2846 | 12.648 | 12.3785 | 12.1979 | NaN | NaN | NaN | 12.601 | 118.4522 | NaN | NaN | NaN | 7.6225 | NaN | NaN | NaN | NaN | 524.7734 | NaN | 28.7777 | NaN | 19.8506
3178.1292 | 12.7868 | 12.4476 | 12.5902 | 12.7754 | 12.4012 | 12.5966 | 12.3705 | 12.1914 | NaN | NaN | NaN | 12.588 | 112.0245 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 523.8522 | NaN | 17.1146 | NaN | 16.0317
3179.1292 | 12.7451 | 12.4257 | 12.5888 | 12.7503 | 12.317 | 12.5912 | 12.372 | 12.1986 | NaN | NaN | NaN | 12.616 | 134.6833 | NaN | NaN | NaN | -15.2207 | NaN | NaN | NaN | NaN | 522.2746 | NaN | 31.0936 | NaN | 24.3124
3180.1292 | 12.7524 | 12.4249 | 12.5952 | 12.839 | 12.3597 | 12.6018 | 12.365 | 12.1985 | NaN | NaN | NaN | 12.5613 | 127.377 | NaN | NaN | NaN | -2.4606 | NaN | NaN | NaN | NaN | 523.7955 | NaN | 25.3378 | NaN | 28.8666
3181.1292 | 12.8299 | 12.5494 | 12.5911 | 12.7934 | 12.2794 | 12.6536 | 12.3838 | 12.1982 | NaN | NaN | NaN | 12.6195 | 122.3222 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 519.1335 | NaN | 26.8101 | NaN | 21.6164
3182.1292 | 12.7431 | 12.4495 | 12.5964 | 12.792 | 12.3802 | 12.5961 | 12.3688 | 12.1959 | NaN | NaN | NaN | 12.582 | 118.2691 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 521.6653 | NaN | 11.1783 | NaN | 22.5608
3183.1292 | 12.7488 | 12.4449 | 12.6004 | 12.8128 | 12.3658 | 12.6078 | 12.3666 | 12.1963 | NaN | NaN | NaN | 12.5951 | 114.3976 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 521.5206 | NaN | 25.8554 | NaN | 20.7335
3184.1292 | 12.7626 | 12.432 | 12.6059 | 12.8137 | 12.3126 | 12.6144 | 12.3799 | 12.2065 | NaN | NaN | NaN | 12.5927 | 126.5137 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 521.1208 | NaN | 22.6222 | NaN | 19.5393
3185.1292 | 12.7584 | 12.4772 | 12.6019 | 12.8011 | 12.3878 | 12.592 | 12.3759 | 12.2016 | NaN | NaN | NaN | 12.5892 | 130.9867 | NaN | NaN | NaN | -18.4349 | NaN | NaN | NaN | NaN | 516.5686 | NaN | 22.4799 | NaN | 17.6982
3186.1292 | 12.7708 | 12.4381 | 12.6046 | 12.8436 | 12.4048 | 12.5959 | 12.3784 | 12.1995 | NaN | NaN | NaN | 12.5988 | 134.7986 | NaN | NaN | NaN | -3.3653 | NaN | NaN | NaN | NaN | 521.2385 | NaN | 24.486 | NaN | 15.543
3187.1292 | 12.7924 | 12.4807 | 12.6095 | 12.7982 | 12.3744 | 12.6058 | 12.3771 | 12.2068 | NaN | NaN | NaN | 12.5891 | 125.2658 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 522.2303 | NaN | 14.2686 | NaN | 14.5779
3188.1292 | 12.7636 | 12.4972 | 12.61 | 12.8018 | 12.3262 | 12.6178 | 12.3817 | 12.2047 | NaN | NaN | NaN | 12.5815 | 121.6057 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 520.3299 | NaN | 14.4381 | NaN | 21.542
3189.1292 | 12.7635 | 12.4689 | 12.6065 | 12.7671 | 12.2688 | 12.6077 | 12.3792 | 12.2046 | NaN | NaN | NaN | 12.5778 | 121.763 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 522.3645 | NaN | 23.1469 | NaN | 24.1695
3190.1292 | 12.7683 | 12.4861 | 12.601 | 12.7659 | 12.3748 | 12.6098 | 12.3753 | 12.1979 | NaN | NaN | NaN | 12.6079 | 124.9437 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 523.2716 | NaN | 27.3403 | NaN | 16.565
3191.1292 | 12.747 | 12.4918 | 12.6072 | 12.8117 | 12.4003 | 12.5914 | 12.3686 | 12.2026 | NaN | NaN | NaN | 12.594 | 125.3603 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 522.9344 | NaN | 30.7912 | NaN | 14.1749
3192.1292 | 12.7456 | 12.5018 | 12.6015 | 12.7809 | 12.3888 | 12.5957 | 12.3755 | 12.1976 | NaN | NaN | NaN | 12.5897 | 127.0666 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 521.0631 | NaN | 28.1486 | NaN | 15.3535
3193.1292 | 12.753 | 12.504 | 12.6163 | 12.7268 | 12.3841 | 12.6005 | 12.3775 | 12.1976 | NaN | NaN | NaN | 12.6103 | 122.5558 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 523.6076 | NaN | 29.4131 | NaN | 13.6282
3194.1292 | 12.7486 | 12.4774 | 12.6116 | 12.8087 | 12.3625 | 12.5803 | 12.3683 | 12.2071 | NaN | NaN | NaN | 12.6073 | 126.9563 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 522.4242 | NaN | 35.08 | NaN | 26.0339
3195.1292 | 12.7532 | 12.4996 | 12.6148 | 12.7508 | 12.3845 | 12.6069 | 12.3772 | 12.2 | NaN | NaN | NaN | 12.6725 | 127.5081 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 524.7657 | NaN | 29.554 | NaN | 18.6123
3196.1292 | 12.7555 | 12.4347 | 12.6036 | 12.7507 | 12.3632 | 12.5713 | 12.3631 | 12.2116 | NaN | NaN | NaN | 12.6028 | 121.2686 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 522.8944 | NaN | 43.4317 | NaN | 19.4032
3197.1292 | 12.7616 | 12.4794 | 12.6146 | 12.785 | 12.4118 | 12.5812 | 12.373 | 12.2024 | NaN | NaN | NaN | 12.6141 | 125.9855 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 522.3779 | NaN | 5.9657 | NaN | 14.2324
3198.1292 | 12.7546 | 12.4443 | 12.6149 | 12.7485 | 12.3542 | 12.568 | 12.3643 | 12.2093 | NaN | NaN | NaN | 12.6446 | 126.9417 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 522.7238 | NaN | 37.3378 | NaN | 17.0973
3199.1292 | 12.7555 | 12.419 | 12.6112 | 12.7613 | 12.3508 | 12.5625 | 12.3643 | 12.2095 | NaN | NaN | NaN | 12.6188 | 122.9505 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 524.8309 | NaN | 27.8941 | NaN | 22.666
3200.1292 | 12.8199 | 12.4237 | 12.6114 | 12.8123 | 12.3992 | 12.5569 | 12.3533 | 12.2137 | NaN | NaN | NaN | 12.6199 | 121.5746 | NaN | NaN | NaN | -5.8745 | NaN | NaN | NaN | NaN | 524.4276 | NaN | 28.3094 | NaN | 21.1434
3201.1292 | 12.7605 | 12.4757 | 12.6052 | 12.7717 | 12.3914 | 12.5798 | 12.3747 | 12.2199 | NaN | NaN | NaN | 12.6259 | 125.6627 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 525.6594 | NaN | 26.644 | NaN | 15.7241
3202.1292 | 12.7439 | 12.4483 | 12.6107 | 12.778 | 12.3919 | 12.5801 | 12.3726 | 12.21 | NaN | NaN | NaN | 12.614 | 121.5085 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 525.9741 | NaN | 39.9484 | NaN | 23.4993
3203.1292 | 12.7974 | 12.4289 | 12.6116 | 12.7819 | 12.3491 | 12.5669 | 12.3627 | 12.2096 | NaN | NaN | NaN | 12.6192 | 129.6443 | NaN | NaN | NaN | -14.6426 | NaN | NaN | NaN | NaN | 523.2687 | NaN | 15.1432 | NaN | 12.4896
3204.1292 | 12.8389 | 12.4205 | 12.6073 | 12.7943 | 12.3354 | 12.5659 | 12.3691 | 12.2153 | NaN | NaN | NaN | 12.6074 | 124.961 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 521.9049 | NaN | 18.7213 | NaN | 23.2588
3205.1292 | 12.7415 | 12.424 | 12.6096 | 12.7918 | 12.3778 | 12.5663 | 12.3657 | 12.2145 | NaN | NaN | NaN | 12.6095 | 127.3613 | NaN | NaN | NaN | -3.8189 | NaN | NaN | NaN | NaN | 523.8535 | NaN | 13.3474 | NaN | 28.1396
3206.1292 | 12.8471 | 12.4039 | 12.6043 | 12.7951 | 12.3616 | 12.5617 | 12.3678 | 12.2159 | NaN | NaN | NaN | 12.5963 | 127.1251 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 522.8024 | NaN | 22.3963 | NaN | 21.0564
3207.1292 | 12.7784 | 12.4029 | 12.6107 | 12.7715 | 12.336 | 12.5574 | 12.3575 | 12.2104 | NaN | NaN | NaN | 12.6275 | 116.4492 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 523.9993 | NaN | 28.1122 | NaN | 23.1167
3208.1292 | 12.7676 | 12.3991 | 12.6166 | 12.8072 | 12.3603 | 12.5664 | 12.3642 | 12.218 | NaN | NaN | NaN | 12.6242 | 126.4943 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 522.5961 | NaN | 22.5918 | NaN | 21.8108
3209.1292 | 12.7241 | 12.419 | 12.6075 | 12.747 | 12.4072 | 12.5647 | 12.3605 | 12.2162 | NaN | NaN | NaN | 12.6491 | 120.5077 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 521.3779 | NaN | 26.5061 | NaN | 23.5372
3210.1292 | 12.7792 | 12.4381 | 12.6106 | 12.7661 | 12.3366 | 12.5854 | 12.3631 | 12.2241 | NaN | NaN | NaN | 12.637 | 123.9956 | NaN | NaN | NaN | 1.8765 | NaN | NaN | NaN | NaN | 521.099 | NaN | 17.209 | NaN | 15.5324
3211.1292 | 12.7848 | 12.4053 | 12.614 | 12.7944 | 12.3983 | 12.5727 | 12.3606 | 12.2249 | NaN | NaN | NaN | 12.6531 | 119.8135 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 520.0592 | NaN | 24.7206 | NaN | 16.05
3212.1292 | 12.7646 | 12.4011 | 12.6155 | 12.7565 | 12.3439 | 12.5732 | 12.3579 | 12.2274 | NaN | NaN | NaN | 12.6222 | 125.0241 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 520.9083 | NaN | 18.4105 | NaN | 20.344
3213.1292 | 12.7651 | 12.4252 | 12.6183 | 12.8252 | 12.3377 | 12.5803 | 12.3569 | 12.2254 | NaN | NaN | NaN | 12.6452 | 126.4653 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 516.9514 | NaN | 11.7014 | NaN | 13.5914
3214.1292 | 12.7578 | 12.4112 | 12.6137 | 12.799 | 12.3815 | 12.5666 | 12.3536 | 12.2227 | NaN | NaN | NaN | 12.6435 | 118.7089 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 520.1541 | NaN | 19.7749 | NaN | 19.7524
3215.1292 | 12.7566 | 12.3953 | 12.6138 | 12.8275 | 12.3894 | 12.5576 | 12.3506 | 12.2349 | NaN | NaN | NaN | 12.6502 | 121.596 | NaN | NaN | NaN | -11.7631 | NaN | NaN | NaN | NaN | 518.6336 | NaN | 43.8005 | NaN | 14.6973
3216.1292 | 12.7609 | 12.3916 | 12.6142 | 12.785 | 12.3607 | 12.5523 | 12.3472 | 12.2368 | NaN | NaN | NaN | 12.6162 | 117.4536 | NaN | NaN | NaN | -9.4403 | NaN | NaN | NaN | NaN | 514.119 | NaN | 30.6867 | NaN | 16.9672
3217.1292 | 12.7607 | 12.41 | 12.6135 | 12.8563 | 12.365 | 12.575 | 12.3527 | 12.2385 | NaN | NaN | NaN | 12.6151 | 120.742 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.3629 | NaN | 20.6652 | NaN | 19.5517
3218.1292 | 12.7557 | 12.3901 | 12.6104 | 12.796 | 12.3914 | 12.5459 | 12.3349 | 12.2342 | NaN | NaN | NaN | 12.6185 | 116.0063 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 519.7822 | NaN | 27.4863 | NaN | 24.9444
3219.1292 | 12.7702 | 12.3869 | 12.6144 | 12.8084 | 12.3285 | 12.558 | 12.3537 | 12.2416 | NaN | NaN | NaN | 12.6244 | 118.4485 | NaN | NaN | NaN | -1.5991 | NaN | NaN | NaN | NaN | 518.2544 | NaN | 31.5683 | NaN | 9.452
3220.1292 | 12.8311 | 12.4208 | 12.6133 | 12.792 | 12.3756 | 12.5676 | 12.354 | 12.2335 | NaN | NaN | NaN | 12.6302 | 113.8021 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 519.5467 | NaN | 24.6871 | NaN | 16.9966
3221.1292 | 12.7896 | 12.4258 | 12.6197 | 12.792 | 12.3708 | 12.57 | 12.3532 | 12.2411 | NaN | NaN | NaN | 12.6158 | 132.2156 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 515.1417 | NaN | 21.9451 | NaN | 15.456
3222.1292 | 12.8823 | 12.3993 | 12.6199 | 12.7864 | 12.2944 | 12.5525 | 12.3398 | 12.2344 | NaN | NaN | NaN | 12.6268 | 124.3166 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.6616 | NaN | 30.5847 | NaN | 19.2117
3223.1292 | 12.7536 | 12.4087 | 12.6233 | 12.8342 | 12.314 | 12.5803 | 12.3559 | 12.2304 | NaN | NaN | NaN | 12.6266 | 121.4115 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.2881 | NaN | 25.6721 | NaN | 19.775
3224.1292 | 12.7284 | 12.3804 | 12.6149 | 12.8248 | 12.3848 | 12.5394 | 12.3446 | 12.2275 | NaN | NaN | NaN | 12.6353 | 131.3976 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 515.4572 | NaN | 24.9521 | NaN | 14.556
3225.1292 | 12.7898 | 12.4437 | 12.6197 | 12.7617 | 12.4007 | 12.5681 | 12.3561 | 12.2266 | NaN | NaN | NaN | 12.6237 | 122.1841 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 520.112 | NaN | 10.6256 | NaN | 17.6499
3226.1292 | 12.7162 | 12.4603 | 12.6196 | 12.8131 | 12.3499 | 12.572 | 12.3562 | 12.2303 | NaN | NaN | NaN | 12.6448 | 114.2683 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 520.0229 | NaN | 8.1894 | NaN | 16.5216
3227.1292 | 12.7453 | 12.4287 | 12.6196 | 12.8061 | 12.2873 | 12.5772 | 12.3569 | 12.2252 | NaN | NaN | NaN | 12.6033 | 119.2672 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.5344 | NaN | 44.2409 | NaN | 23.7661
3228.1292 | 12.7373 | 12.4695 | 12.6104 | 12.8192 | 12.3923 | 12.5781 | 12.357 | 12.2268 | NaN | NaN | NaN | 12.6063 | 133.6346 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 517.8548 | NaN | 17.2108 | NaN | 18.8148
3229.1292 | 12.729 | 12.3962 | 12.6245 | 12.7989 | 12.3226 | 12.5497 | 12.3423 | 12.2206 | NaN | NaN | NaN | 12.6273 | 112.5911 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 520.2516 | NaN | 47.3891 | NaN | 27.1231
3230.1292 | 12.7228 | 12.3929 | 12.6212 | 12.8271 | 12.4262 | 12.5662 | 12.3485 | 12.2266 | NaN | NaN | NaN | 12.6152 | 124.2809 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 519.3627 | NaN | 18.8934 | NaN | 25.399
3231.1292 | 12.7177 | 12.405 | 12.6177 | 12.815 | 12.3151 | 12.5601 | 12.3484 | 12.2308 | NaN | NaN | NaN | 12.5924 | 121.7048 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 520.0445 | NaN | 9.6316 | NaN | 20.9857
3232.1292 | 12.732 | 12.3663 | 12.6137 | 12.8202 | 12.3416 | 12.5558 | 12.3419 | 12.2265 | NaN | NaN | NaN | 12.6169 | 124.0973 | NaN | NaN | NaN | -1.1187 | NaN | NaN | NaN | NaN | 519.7079 | NaN | 26.2586 | NaN | 15.754
3233.1292 | 12.7342 | 12.3798 | 12.6173 | 12.7819 | 12.3534 | 12.56 | 12.3406 | 12.228 | NaN | NaN | NaN | 12.6321 | 113.3985 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 517.1506 | NaN | 41.7959 | NaN | 15.3758
3234.1292 | 12.732 | 12.4603 | 12.6117 | 12.8751 | 12.4203 | 12.584 | 12.3562 | 12.2267 | NaN | NaN | NaN | 12.5988 | 130.1539 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 520.6775 | NaN | 13.3963 | NaN | 14.6007
3235.1292 | 12.7362 | 12.4281 | 12.6167 | 12.8283 | 12.3781 | 12.5875 | 12.3457 | 12.2219 | NaN | NaN | NaN | 12.5887 | 120.5943 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.8991 | NaN | 14.4789 | NaN | 13.938
3236.1292 | 12.7313 | 12.3752 | 12.6149 | 12.8043 | 12.4197 | 12.5676 | 12.3317 | 12.2237 | NaN | NaN | NaN | 12.6277 | 124.2361 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 519.0273 | NaN | 16.3342 | NaN | 22.0462
3237.1292 | 12.7413 | 12.3979 | 12.6199 | 12.8284 | 12.381 | 12.5623 | 12.3398 | 12.2194 | NaN | NaN | NaN | 12.6055 | 123.5697 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 520.2538 | NaN | 27.9307 | NaN | 21.0205
3238.1292 | 12.7439 | 12.3515 | 12.6191 | 12.835 | 12.3946 | 12.5611 | 12.3462 | 12.2193 | NaN | NaN | NaN | 12.5816 | 128.763 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 516.6941 | NaN | 30.0891 | NaN | 19.5421
3239.1292 | 12.7466 | 12.3908 | 12.6138 | 12.8413 | 12.3278 | 12.5664 | 12.3379 | 12.223 | NaN | NaN | NaN | 12.5958 | 132.1813 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 517.2658 | NaN | 22.1005 | NaN | 17.8046
3240.1292 | 12.7783 | 12.3499 | 12.6085 | 12.8086 | 12.362 | 12.5581 | 12.3353 | 12.2206 | NaN | NaN | NaN | 12.5679 | 124.4841 | NaN | NaN | NaN | -13.3899 | NaN | NaN | NaN | NaN | 521.5073 | NaN | 31.8829 | NaN | 21.9951
3241.1292 | 12.7431 | 12.3481 | 12.614 | 12.792 | 12.3599 | 12.56 | 12.3423 | 12.2276 | NaN | NaN | NaN | 12.6338 | 123.9644 | NaN | NaN | NaN | -9.092 | NaN | NaN | NaN | NaN | 521.694 | NaN | 10.07 | NaN | 22.2964
3242.1292 | 12.7465 | 12.4136 | 12.6165 | 12.8131 | 12.3483 | 12.6 | 12.3464 | 12.2313 | NaN | NaN | NaN | 12.6174 | 134.7229 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 517.281 | NaN | 22.184 | NaN | 18.6064
3243.1292 | 12.751 | 12.4345 | 12.6156 | 12.8014 | 12.3244 | 12.6138 | 12.366 | 12.2203 | NaN | NaN | NaN | 12.5721 | 127.9975 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 520.8762 | NaN | 14.9905 | NaN | 14.5936
3244.1292 | 12.7415 | 12.3854 | 12.6147 | 12.8324 | 12.3528 | 12.5812 | 12.3527 | 12.2265 | NaN | NaN | NaN | 12.5943 | 116.8176 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 520.7136 | NaN | 28.4862 | NaN | 16.4901
3245.1292 | 12.7472 | 12.4559 | 12.6148 | 12.8218 | 12.4071 | 12.6242 | 12.3645 | 12.2269 | NaN | NaN | NaN | 12.5691 | 137.596 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.3706 | NaN | 28.1285 | NaN | 15.6965
3246.1292 | 12.743 | 12.3542 | 12.6135 | 12.816 | 12.3786 | 12.5501 | 12.3388 | 12.2248 | NaN | NaN | NaN | 12.5957 | 123.4769 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.3736 | NaN | 27.5508 | NaN | 25.1068
3247.1292 | 12.7467 | 12.436 | 12.6117 | 12.7966 | 12.3845 | 12.5918 | 12.3521 | 12.2296 | NaN | NaN | NaN | 12.6195 | 119.2077 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 519.0302 | NaN | 24.7711 | NaN | 16.2966
3248.1292 | 12.7352 | 12.401 | 12.6083 | 12.781 | 12.3546 | 12.5858 | 12.3527 | 12.2237 | NaN | NaN | NaN | 12.566 | 134.0693 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.708 | NaN | 25.0767 | NaN | 13.628
3249.1292 | 12.7348 | 12.3716 | 12.6005 | 12.7973 | 12.3974 | 12.5728 | 12.3407 | 12.2255 | NaN | NaN | NaN | 12.5861 | 113.9345 | NaN | NaN | NaN | 5.1891 | NaN | NaN | NaN | NaN | 517.1157 | NaN | 20.7823 | NaN | 17.3215
3250.1292 | 12.7359 | 12.4425 | 12.6023 | 12.842 | 12.2548 | 12.6141 | 12.3673 | 12.2285 | NaN | NaN | NaN | 12.5886 | 131.3361 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 517.7385 | NaN | 27.4988 | NaN | 14.6096
3251.1292 | 12.7316 | 12.3633 | 12.6004 | 12.8072 | 12.4097 | 12.5812 | 12.3511 | 12.2187 | NaN | NaN | NaN | 12.5645 | 113.1274 | NaN | NaN | NaN | -1.7551 | NaN | NaN | NaN | NaN | 521.1284 | NaN | 11.6135 | NaN | 18.9236
3252.1292 | 12.7308 | 12.394 | 12.5989 | 12.7993 | 12.4096 | 12.5761 | 12.3469 | 12.2332 | NaN | NaN | NaN | 12.5926 | 123.5496 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 523.2438 | NaN | 10.4817 | NaN | 10.5416
3253.1292 | 12.7267 | 12.4822 | 12.6105 | 12.7713 | 12.4041 | 12.6255 | 12.3731 | 12.2315 | NaN | NaN | NaN | 12.5723 | 126.3049 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 519.0557 | NaN | 16.367 | NaN | 15.8675
3254.1292 | 12.7228 | 12.3526 | 12.6076 | 12.828 | 12.3956 | 12.5757 | 12.3496 | 12.2333 | NaN | NaN | NaN | 12.6154 | 137.4352 | NaN | NaN | NaN | -12.3442 | NaN | NaN | NaN | NaN | 519.2237 | NaN | 26.3127 | NaN | 12.0234
3255.1292 | 12.7262 | 12.3518 | 12.607 | 12.8203 | 12.3347 | 12.5704 | 12.3433 | 12.2401 | NaN | NaN | NaN | 12.6725 | 114.5563 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.6956 | NaN | 11.6452 | NaN | 28.1679
3256.1292 | 12.7216 | 12.3383 | 12.6076 | 12.7892 | 12.3389 | 12.5639 | 12.3428 | 12.2348 | NaN | NaN | NaN | 12.6016 | 124.9188 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 517.5613 | NaN | 15.0066 | NaN | 21.8945
3257.1292 | 12.7268 | 12.3616 | 12.6111 | 12.8632 | 12.376 | 12.5869 | 12.3567 | 12.2399 | NaN | NaN | NaN | 12.5831 | 119.2388 | NaN | NaN | NaN | -0.4048 | NaN | NaN | NaN | NaN | 517.3007 | NaN | 7.6243 | NaN | 22.413
3258.1292 | 12.7273 | 12.3872 | 12.6152 | 12.7967 | 12.3694 | 12.5853 | 12.3511 | 12.2409 | NaN | NaN | NaN | 12.5851 | 123.2838 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 519.2165 | NaN | 16.5104 | NaN | 18.73
3259.1292 | 12.7316 | 12.3206 | 12.6118 | 12.8289 | 12.4123 | 12.5635 | 12.3489 | 12.2423 | NaN | NaN | NaN | 12.5688 | 129.3103 | NaN | NaN | NaN | -17.2133 | NaN | NaN | NaN | NaN | 517.4895 | NaN | 15.922 | NaN | 18.0807
3260.1292 | 12.8075 | 12.3624 | 12.619 | 12.8499 | 12.3851 | 12.581 | 12.3625 | 12.2435 | NaN | NaN | NaN | 12.566 | 127.5023 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 516.3898 | NaN | 20.2546 | NaN | 18.8858
3261.1292 | 12.7853 | 12.3505 | 12.6145 | 12.8495 | 12.3766 | 12.5681 | 12.3459 | 12.2495 | NaN | NaN | NaN | 12.5813 | 119.6973 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.8993 | NaN | 26.7235 | NaN | 22.6501
3262.1292 | 12.7443 | 12.3543 | 12.6107 | 12.8356 | 12.3386 | 12.5774 | 12.3501 | 12.2545 | NaN | NaN | NaN | 12.5908 | 120.2298 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 515.2408 | NaN | 25.068 | NaN | 18.8946
3263.1292 | 12.7468 | 12.3835 | 12.6113 | 12.8277 | 12.2922 | 12.596 | 12.3541 | 12.2502 | NaN | NaN | NaN | 12.6139 | 114.3151 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 517.7497 | NaN | 25.848 | NaN | 15.541
3264.1292 | 12.7566 | 12.3316 | 12.6157 | 12.8382 | 12.4149 | 12.5576 | 12.3437 | 12.2538 | NaN | NaN | NaN | 12.5991 | 118.9906 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.5431 | NaN | 10.9671 | NaN | 19.3846
3265.1292 | 12.8039 | 12.3667 | 12.6138 | 12.833 | 12.357 | 12.5705 | 12.3454 | 12.2517 | NaN | NaN | NaN | 12.5867 | 121.0028 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 520.8813 | NaN | 19.6537 | NaN | 14.07
3266.1292 | 12.7465 | 12.3832 | 12.6089 | 12.8391 | 12.3542 | 12.5761 | 12.3493 | 12.2556 | NaN | NaN | NaN | 12.5923 | 135.1182 | NaN | NaN | NaN | -15.5833 | NaN | NaN | NaN | NaN | 519.5259 | NaN | 17.8356 | NaN | 24.7493
3267.1292 | 12.7548 | 12.3572 | 12.6131 | 12.9296 | 12.3503 | 12.5607 | 12.3418 | 12.26 | NaN | NaN | NaN | 12.6142 | 133.6213 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 519.9807 | NaN | 19.3107 | NaN | 12.316
3268.1292 | 12.7574 | 12.3703 | 12.6131 | 12.8614 | 12.3892 | 12.5727 | 12.3516 | 12.2579 | NaN | NaN | NaN | 12.6066 | 117.683 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 519.0315 | NaN | 15.1205 | NaN | 21.2764
3269.1292 | 12.7631 | 12.3794 | 12.6105 | 12.8502 | 12.3675 | 12.5746 | 12.3504 | 12.2629 | NaN | NaN | NaN | 12.6166 | 120.4553 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 516.5192 | NaN | 9.7025 | NaN | 15.0775
3270.1292 | 12.7467 | 12.3639 | 12.6098 | 12.8977 | 12.416 | 12.5627 | 12.3485 | 12.2629 | NaN | NaN | NaN | 12.6183 | 119.3299 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 517.6855 | NaN | 18.3207 | NaN | 19.8335
3271.1292 | 12.7377 | 12.3702 | 12.6159 | 12.8129 | 12.4087 | 12.58 | 12.3517 | 12.2638 | NaN | NaN | NaN | 12.6771 | 117.7356 | NaN | NaN | NaN | -7.139 | NaN | NaN | NaN | NaN | 519.9488 | NaN | 9.7741 | NaN | 24.2976
3272.1292 | 12.7925 | 12.4157 | 12.6184 | 12.8512 | 12.3661 | 12.6109 | 12.36 | 12.2672 | NaN | NaN | NaN | 12.6288 | 121.803 | NaN | NaN | NaN | 4.1145 | NaN | NaN | NaN | NaN | 517.3085 | NaN | 25.5529 | NaN | 10.59
3273.1292 | 12.8446 | 12.3602 | 12.6158 | 12.8546 | 12.306 | 12.5747 | 12.3527 | 12.2695 | NaN | NaN | NaN | 12.6334 | 130.7297 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.812 | NaN | 17.278 | NaN | 27.7753
3274.1292 | 12.7903 | 12.3991 | 12.6178 | 12.7843 | 12.3145 | 12.592 | 12.3523 | 12.2624 | NaN | NaN | NaN | 12.624 | 120.129 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 521.2801 | NaN | 21.5716 | NaN | 25.7821
3275.1292 | 12.8215 | 12.4131 | 12.6187 | 12.8907 | 12.4266 | 12.5793 | 12.3534 | 12.2669 | NaN | NaN | NaN | 12.6277 | 113.8209 | NaN | NaN | NaN | 2.7378 | NaN | NaN | NaN | NaN | 518.9798 | NaN | 26.1034 | NaN | 13.1576
3276.1292 | 12.7486 | 12.4395 | 12.6186 | 12.834 | 12.4007 | 12.6008 | 12.37 | 12.2696 | NaN | NaN | NaN | 12.6133 | 135.5885 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 519.8687 | NaN | 23.0427 | NaN | 17.1329
3277.1292 | 12.7544 | 12.3788 | 12.6202 | 12.9348 | 12.4142 | 12.5683 | 12.3396 | 12.2731 | NaN | NaN | NaN | 12.6482 | 138.1901 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 521.7938 | NaN | 21.3616 | NaN | 20.926
3278.1292 | 12.7459 | 12.3996 | 12.6212 | 12.8297 | 12.314 | 12.6001 | 12.3466 | 12.2727 | NaN | NaN | NaN | 12.6464 | 116.4566 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 521.4706 | NaN | 13.0943 | NaN | 15.4637
3279.1292 | 12.7493 | 12.3948 | 12.6267 | 12.8636 | 12.4283 | 12.5812 | 12.3511 | 12.27 | NaN | NaN | NaN | 12.6161 | 125.079 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.955 | NaN | 17.4715 | NaN | 18.1091
3280.1292 | 12.7459 | 12.3791 | 12.6197 | 12.8363 | 12.351 | 12.5784 | 12.3566 | 12.2717 | NaN | NaN | NaN | 12.6371 | 116.2461 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 520.408 | NaN | 27.475 | NaN | 21.5953
3281.1292 | 12.7436 | 12.3818 | 12.6222 | 12.8295 | 12.426 | 12.5665 | 12.3455 | 12.2701 | NaN | NaN | NaN | 12.5916 | 122.5003 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 515.8959 | NaN | 41.6548 | NaN | 16.9489
3282.1292 | 12.7562 | 12.3865 | 12.621 | 12.8223 | 12.42 | 12.5655 | 12.3406 | 12.2815 | NaN | NaN | NaN | 12.6014 | 116.428 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 514.8967 | NaN | 20.2072 | NaN | 17.7465
3283.1292 | 12.7495 | 12.3957 | 12.6235 | 12.8144 | 12.3746 | 12.558 | 12.3453 | 12.275 | NaN | NaN | NaN | 12.6332 | 122.7968 | NaN | NaN | NaN | -12.5339 | NaN | NaN | NaN | NaN | 518.2221 | NaN | 25.1615 | NaN | 24.7872
3284.1292 | 12.747 | 12.4153 | 12.6235 | 12.8334 | 12.4507 | 12.5752 | 12.3443 | 12.2819 | NaN | NaN | NaN | 12.6363 | 125.8698 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 516.3566 | NaN | 22.6565 | NaN | 23.63
3285.1292 | 12.797 | 12.3823 | 12.6227 | 12.8095 | 12.3663 | 12.5758 | 12.3364 | 12.2773 | NaN | NaN | NaN | 12.6298 | 127.396 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 512.6326 | NaN | 15.2503 | NaN | 15.5409
3286.1448 | 12.8559 | 12.4058 | 12.6236 | 12.7799 | 12.3849 | 12.5846 | 12.3523 | 12.2827 | NaN | NaN | NaN | 12.6395 | 117.0772 | NaN | NaN | NaN | -19.843 | NaN | NaN | NaN | NaN | 512.4132 | NaN | 21.5494 | NaN | 24.1689
3287.1292 | 12.737 | 12.4573 | 12.6242 | 12.7755 | 12.4237 | 12.5857 | 12.342 | 12.2833 | NaN | NaN | NaN | 12.6762 | 125.4605 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 515.3656 | NaN | 29.7912 | NaN | 22.9546
3288.1292 | 12.7399 | 12.4627 | 12.6316 | 12.8138 | 12.4065 | 12.6026 | 12.3383 | 12.2847 | NaN | NaN | NaN | 12.6169 | 114.7926 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 521.9305 | NaN | 11.2338 | NaN | 14.943
3289.1292 | 12.724 | 12.4684 | 12.6225 | 12.7739 | 12.3554 | 12.6114 | 12.3414 | 12.2904 | NaN | NaN | NaN | 12.6233 | 119.1657 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 520.4384 | NaN | 9.0319 | NaN | 25.7855
3290.1292 | 12.8083 | 12.5627 | 12.6247 | 12.8107 | 12.3433 | 12.6871 | 12.3775 | 12.2864 | NaN | NaN | NaN | 12.7642 | 132.3567 | NaN | NaN | NaN | 0.3344 | NaN | NaN | NaN | NaN | 518.0605 | NaN | 14.5547 | NaN | 22.7193
3291.1292 | 12.7197 | 12.4552 | 12.6324 | 12.7956 | 12.3608 | 12.5829 | 12.3351 | 12.2872 | NaN | NaN | NaN | 12.6605 | 127.5131 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.8649 | NaN | 16.4297 | NaN | 14.0845
3292.1292 | 12.7284 | 12.5681 | 12.6285 | 12.863 | 12.4067 | 12.6382 | 12.3741 | 12.2893 | NaN | NaN | NaN | 12.6637 | 125.0258 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 519.0343 | NaN | 18.0538 | NaN | 14.8294
3293.1292 | 12.7367 | 12.4407 | 12.6272 | 12.8362 | 12.453 | 12.5804 | 12.334 | 12.2892 | NaN | NaN | NaN | 12.667 | 122.9575 | NaN | NaN | NaN | -3.2188 | NaN | NaN | NaN | NaN | 516.2931 | NaN | 30.6932 | NaN | 21.0598
3294.1292 | 12.7435 | 12.4759 | 12.6213 | 12.8234 | 12.4574 | 12.5926 | 12.3427 | 12.2869 | NaN | NaN | NaN | 12.6559 | 116.9757 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 519.4867 | NaN | 20.8727 | NaN | 16.2398
3295.1292 | 12.7562 | 12.4953 | 12.6231 | 12.8228 | 12.3539 | 12.602 | 12.3432 | 12.2944 | NaN | NaN | NaN | 12.6524 | 124.06 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.8546 | NaN | 25.1776 | NaN | 23.2078
3296.1292 | 12.7646 | 12.4655 | 12.6267 | 12.8116 | 12.4353 | 12.6023 | 12.3485 | 12.2901 | NaN | NaN | NaN | 12.6457 | 129.8675 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 510.2006 | NaN | 23.3761 | NaN | 12.9674
3297.1292 | 12.7528 | 12.5035 | 12.6209 | 12.8275 | 12.3963 | 12.6057 | 12.3451 | 12.29 | NaN | NaN | NaN | 12.6313 | 126.6411 | NaN | NaN | NaN | -19.2495 | NaN | NaN | NaN | NaN | 515.1205 | NaN | 25.4869 | NaN | 22.7023
3298.1292 | 12.7429 | 12.4653 | 12.6218 | 12.8243 | 12.4265 | 12.5823 | 12.3345 | 12.2964 | NaN | NaN | NaN | 12.6668 | 124.2999 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 516.7795 | NaN | 10.3529 | NaN | 20.8026
3299.1292 | 12.7311 | 12.4974 | 12.6216 | 12.7991 | 12.4235 | 12.6062 | 12.3549 | 12.295 | NaN | NaN | NaN | 12.6831 | 117.8936 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 519.3355 | NaN | 27.9918 | NaN | 16.3897
3300.1292 | 12.7474 | 12.4579 | 12.6301 | 12.8684 | 12.4439 | 12.5927 | 12.3435 | 12.2954 | NaN | NaN | NaN | 12.6589 | 122.6274 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 515.7515 | NaN | 13.7444 | NaN | 17.0233
3301.1292 | 12.7569 | 12.4535 | 12.6254 | 12.8067 | 12.4266 | 12.5755 | 12.3434 | 12.3034 | NaN | NaN | NaN | 12.6781 | 125.4868 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 519.9155 | NaN | 10.1774 | NaN | 21.6059
3302.1292 | 12.7649 | 12.4321 | 12.6215 | 12.7959 | 12.4413 | 12.572 | 12.3486 | 12.2959 | NaN | NaN | NaN | 12.7112 | 134.0254 | NaN | NaN | NaN | -11.3619 | NaN | NaN | NaN | NaN | 520.8937 | NaN | 24.9788 | NaN | 17.175
3303.1292 | 12.7653 | 12.4388 | 12.6253 | 12.8552 | 12.3649 | 12.5891 | 12.3554 | 12.2942 | NaN | NaN | NaN | 12.6662 | 122.0252 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 520.3966 | NaN | 8.8064 | NaN | 19.0965
3304.1292 | 12.764 | 12.484 | 12.6259 | 12.8246 | 12.45 | 12.6117 | 12.3656 | 12.2933 | NaN | NaN | NaN | 12.6702 | 123.4448 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 519.8233 | NaN | 27.5798 | NaN | 17.7765
3305.1292 | 12.7675 | 12.4477 | 12.6282 | 12.8179 | 12.4029 | 12.6062 | 12.356 | 12.301 | NaN | NaN | NaN | 12.6938 | 131.096 | NaN | NaN | NaN | -4.5562 | NaN | NaN | NaN | NaN | 521.4454 | NaN | 20.0891 | NaN | 10.4741
3306.1292 | 12.7717 | 12.5003 | 12.6312 | 12.8187 | 12.4503 | 12.608 | 12.3676 | 12.2987 | NaN | NaN | NaN | 12.6579 | 133.1899 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 519.1724 | NaN | 27.8189 | NaN | 16.7426
3307.1292 | 12.7789 | 12.4543 | 12.6341 | 12.8061 | 12.4076 | 12.6049 | 12.3509 | 12.2927 | NaN | NaN | NaN | 12.6891 | 132.5324 | NaN | NaN | NaN | -8.6576 | NaN | NaN | NaN | NaN | 523.6577 | NaN | 11.6226 | NaN | 21.9021
3308.1292 | 12.7826 | 12.478 | 12.6302 | 12.8124 | 12.4445 | 12.5981 | 12.3465 | 12.2991 | NaN | NaN | NaN | 12.6928 | 134.4678 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 519.2519 | NaN | 9.3398 | NaN | 21.0871
3309.1292 | 12.791 | 12.4196 | 12.634 | 12.8046 | 12.4343 | 12.5867 | 12.353 | 12.3082 | NaN | NaN | NaN | 12.6996 | 127.739 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 519.5879 | NaN | 27.6419 | NaN | 16.954
3310.1292 | 12.7666 | 12.4645 | 12.635 | 12.7731 | 12.3803 | 12.6079 | 12.3618 | 12.302 | NaN | NaN | NaN | 12.6986 | 125.7132 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 520.5158 | NaN | 20.8841 | NaN | 14.7366
3311.1292 | 12.7673 | 12.4785 | 12.6363 | 12.83 | 12.4282 | 12.6057 | 12.3648 | 12.3048 | NaN | NaN | NaN | 12.6425 | 127.6112 | NaN | NaN | NaN | -15.2726 | NaN | NaN | NaN | NaN | 518.2422 | NaN | 14.0859 | NaN | 24.4155
3312.1292 | 12.7698 | 12.4788 | 12.6317 | 12.7715 | 12.4056 | 12.6087 | 12.3656 | 12.3068 | NaN | NaN | NaN | 12.6752 | 123.5232 | NaN | NaN | NaN | -2.5439 | NaN | NaN | NaN | NaN | 518.6381 | NaN | 29.7646 | NaN | 19.3614
3313.1292 | 12.7653 | 12.5432 | 12.6317 | 12.834 | 12.4479 | 12.6266 | 12.3776 | 12.3044 | NaN | NaN | NaN | 12.7204 | 114.7329 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 515.1083 | NaN | 26.0097 | NaN | 25.4134
3314.1292 | 12.856 | 12.4159 | 12.6303 | 12.836 | 12.4454 | 12.5863 | 12.3588 | 12.3019 | NaN | NaN | NaN | 12.7212 | 124.9787 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 516.0828 | NaN | 30.4756 | NaN | 20.2802
3315.1292 | 12.7754 | 12.4291 | 12.6319 | 12.8578 | 12.44 | 12.5991 | 12.3572 | 12.3024 | NaN | NaN | NaN | 12.7189 | 122.4737 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 519.5672 | NaN | 19.7448 | NaN | 20.9234
3316.1292 | 12.7836 | 12.437 | 12.6343 | 12.8253 | 12.4333 | 12.5888 | 12.3627 | 12.3051 | NaN | NaN | NaN | 12.6833 | 129.9636 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 516.3835 | NaN | 44.0594 | NaN | 27.6408
3317.1292 | 12.7931 | 12.4138 | 12.6307 | 12.8077 | 12.3853 | 12.5914 | 12.368 | 12.2955 | NaN | NaN | NaN | 12.6771 | 130.6808 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 520.8099 | NaN | 33.5006 | NaN | 13.2203
3318.1292 | 12.8039 | 12.5041 | 12.6254 | 12.8423 | 12.4467 | 12.6318 | 12.383 | 12.3051 | NaN | NaN | NaN | 12.6855 | 119.861 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 521.5463 | NaN | 29.228 | NaN | 23.8171
3319.1292 | 12.817 | 12.5334 | 12.6286 | 12.8316 | 12.3312 | 12.6927 | 12.4072 | 12.2925 | NaN | NaN | NaN | 12.6593 | 119.1418 | NaN | NaN | NaN | -14.5042 | NaN | NaN | NaN | NaN | 520.7199 | NaN | 13.4389 | NaN | 26.3591
3320.1292 | 12.8176 | 12.592 | 12.6292 | 12.8334 | 12.3905 | 12.6517 | 12.3915 | 12.2952 | NaN | NaN | NaN | 12.699 | 129.4954 | NaN | NaN | NaN | -4.8466 | NaN | NaN | NaN | NaN | 518.5925 | NaN | 31.4529 | NaN | 17.2112
3321.1292 | 12.8158 | 12.4289 | 12.6293 | 12.8008 | 12.4266 | 12.6141 | 12.3773 | 12.3015 | NaN | NaN | NaN | 12.6838 | 128.1995 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 521.0565 | NaN | 11.2394 | NaN | 28.1605
3322.1292 | 12.8405 | 12.4801 | 12.6373 | 12.83 | 12.3783 | 12.6453 | 12.3822 | 12.293 | NaN | NaN | NaN | 12.6761 | 124.7788 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 519.0396 | NaN | 29.9997 | NaN | 26.3323
3323.1292 | 12.836 | 12.4486 | 12.6342 | 12.8369 | 12.4005 | 12.6207 | 12.3801 | 12.2916 | NaN | NaN | NaN | 12.6525 | 119.1654 | NaN | NaN | NaN | 4.6155 | NaN | NaN | NaN | NaN | 517.1133 | NaN | 9.2726 | NaN | 19.2668
3324.1292 | 12.8857 | 12.4395 | 12.6322 | 12.8469 | 12.4407 | 12.6065 | 12.3778 | 12.2865 | NaN | NaN | NaN | 12.6707 | 117.796 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 516.1007 | NaN | 41.6103 | NaN | 23.7748
3325.1292 | 12.8149 | 12.4378 | 12.6393 | 12.8197 | 12.4441 | 12.6039 | 12.3793 | 12.2889 | NaN | NaN | NaN | 12.6612 | 120.098 | NaN | NaN | NaN | -6.8084 | NaN | NaN | NaN | NaN | 519.1803 | NaN | 10.9653 | NaN | 13.3415
3326.1292 | 12.8011 | 12.4524 | 12.6358 | 12.8133 | 12.3924 | 12.6274 | 12.3798 | 12.2909 | NaN | NaN | NaN | 12.6935 | 126.9224 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.7254 | NaN | 38.1796 | NaN | 13.1561
3327.1292 | 12.8053 | 12.4468 | 12.64 | 12.8652 | 12.3732 | 12.6146 | 12.3756 | 12.2915 | NaN | NaN | NaN | 12.6819 | 125.6762 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 517.8801 | NaN | 31.4143 | NaN | 22.5696
3328.1292 | 12.8079 | 12.449 | 12.6414 | 12.8549 | 12.3686 | 12.632 | 12.385 | 12.2862 | NaN | NaN | NaN | 12.6669 | 130.1097 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 520.1555 | NaN | 44.3824 | NaN | 25.1957
3329.1292 | 12.8112 | 12.5963 | 12.6356 | 12.8405 | 12.4151 | 12.641 | 12.4099 | 12.2861 | NaN | NaN | NaN | 12.6649 | 123.1321 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 522.5703 | NaN | 19.463 | NaN | 17.9293
3330.1292 | 12.8139 | 12.4568 | 12.6367 | 12.8201 | 12.3997 | 12.6246 | 12.3759 | 12.2901 | NaN | NaN | NaN | 12.6803 | 125.1515 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 521.1692 | NaN | 21.2787 | NaN | 19.4411
3331.1292 | 12.8126 | 12.4384 | 12.6375 | 12.8837 | 12.3588 | 12.6257 | 12.3899 | 12.2892 | NaN | NaN | NaN | 12.694 | 118.1266 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 519.0073 | NaN | 36.3162 | NaN | 13.2179
3332.1292 | 12.7994 | 12.4472 | 12.6401 | 12.8269 | 12.3986 | 12.614 | 12.381 | 12.2882 | NaN | NaN | NaN | 12.6799 | 123.4225 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 521.9877 | NaN | 31.2321 | NaN | 20.39
3333.1292 | 12.8096 | 12.4478 | 12.6365 | 12.855 | 12.3899 | 12.618 | 12.3876 | 12.2906 | NaN | NaN | NaN | 12.685 | 132.3159 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 520.8996 | NaN | 19.4759 | NaN | 26.2213
3334.1292 | 12.8075 | 12.4674 | 12.6346 | 12.8512 | 12.4279 | 12.6233 | 12.3817 | 12.2932 | NaN | NaN | NaN | 12.7003 | 127.6411 | NaN | NaN | NaN | -2.6379 | NaN | NaN | NaN | NaN | 522.2619 | NaN | 9.7854 | NaN | 17.3376
3335.1292 | 12.8019 | 12.4766 | 12.6359 | 12.8518 | 12.4108 | 12.626 | 12.3858 | 12.2964 | NaN | NaN | NaN | 12.6735 | 129.4632 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 521.5083 | NaN | 36.6061 | NaN | 21.5253
3336.1292 | 12.8465 | 12.4847 | 12.6345 | 12.8348 | 12.4478 | 12.6145 | 12.3901 | 12.2962 | NaN | NaN | NaN | 12.6795 | 137.8431 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 519.2947 | NaN | 13.2332 | NaN | 24.0556
3337.1292 | 12.7694 | 12.4457 | 12.6349 | 12.8734 | 12.4358 | 12.6047 | 12.3781 | 12.3026 | NaN | NaN | NaN | 12.7049 | 126.9676 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 517.8818 | NaN | 15.6823 | NaN | 19.0422
3338.1292 | 12.7745 | 12.4829 | 12.6362 | 12.874 | 12.4512 | 12.6228 | 12.3902 | 12.3001 | NaN | NaN | NaN | 12.6705 | 124.5017 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 519.3649 | NaN | 21.2099 | NaN | 22.2424
3339.1292 | 12.7843 | 12.4496 | 12.6385 | 12.8639 | 12.4313 | 12.6129 | 12.3806 | 12.2998 | NaN | NaN | NaN | 12.6979 | 123.239 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 519.0683 | NaN | 17.2928 | NaN | 23.1654
3340.1292 | 12.7828 | 12.5367 | 12.6354 | 12.8368 | 12.359 | 12.6613 | 12.3961 | 12.3003 | NaN | NaN | NaN | 12.6707 | 117.7223 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 521.0898 | NaN | 9.2839 | NaN | 19.2417
3341.1292 | 12.7859 | 12.4517 | 12.637 | 12.904 | 12.4563 | 12.6021 | 12.3779 | 12.295 | NaN | NaN | NaN | 12.683 | 125.2631 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.482 | NaN | 10.8275 | NaN | 17.7701
3342.1292 | 12.7887 | 12.4841 | 12.6306 | 12.8772 | 12.4169 | 12.613 | 12.3898 | 12.3023 | NaN | NaN | NaN | 12.7414 | 123.6872 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 520.5006 | NaN | 14.3237 | NaN | 22.9543
3343.1292 | 12.7911 | 12.4514 | 12.6315 | 12.8414 | 12.3642 | 12.6097 | 12.3869 | 12.3104 | NaN | NaN | NaN | 12.6801 | 115.9995 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 522.0213 | NaN | 14.8494 | NaN | 20.1011
3344.1292 | 12.7969 | 12.5171 | 12.6256 | 12.8391 | 12.4347 | 12.6248 | 12.3997 | 12.3057 | NaN | NaN | NaN | 12.7031 | 129.0125 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.3321 | NaN | 10.4707 | NaN | 26.1513
3345.1292 | 12.8034 | 12.4617 | 12.6319 | 12.9745 | 12.4322 | 12.5991 | 12.3888 | 12.3144 | NaN | NaN | NaN | 12.703 | 124.4186 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.1601 | NaN | 9.3619 | NaN | 19.0257
3346.1292 | 12.8445 | 12.4497 | 12.6343 | 12.8729 | 12.3358 | 12.5925 | 12.3895 | 12.3111 | NaN | NaN | NaN | 12.6703 | 130.5022 | NaN | NaN | NaN | 3.4519 | NaN | NaN | NaN | NaN | 516.8321 | NaN | 20.0895 | NaN | 22.6828
3347.1292 | 12.785 | 12.4886 | 12.6326 | 12.8733 | 12.3269 | 12.6299 | 12.3907 | 12.3158 | NaN | NaN | NaN | 12.6693 | 126.3197 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 517.4133 | NaN | 31.0305 | NaN | 21.441
3348.1292 | 12.7951 | 12.5192 | 12.6284 | 12.9132 | 12.4523 | 12.6171 | 12.392 | 12.3116 | NaN | NaN | NaN | 12.6613 | 130.0135 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 520.2389 | NaN | 8.8129 | NaN | 25.3672
3349.1292 | 12.8022 | 12.4849 | 12.6304 | 12.8527 | 12.3984 | 12.6093 | 12.3875 | 12.3072 | NaN | NaN | NaN | 12.6578 | 118.9442 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 521.7143 | NaN | 35.8442 | NaN | 19.2834
3350.1292 | 12.8068 | 12.5063 | 12.6327 | 12.8901 | 12.3401 | 12.6202 | 12.3941 | 12.3054 | NaN | NaN | NaN | 12.692 | 130.5407 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 516.9316 | NaN | 40.0613 | NaN | 28.2437
3351.1292 | 12.7744 | 12.4474 | 12.6286 | 12.9204 | 12.4613 | 12.5925 | 12.3869 | 12.3121 | NaN | NaN | NaN | 12.6903 | 123.3074 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 517.375 | NaN | 17.9981 | NaN | 18.7389
3352.1292 | 12.8182 | 12.4473 | 12.6295 | 12.8633 | 12.425 | 12.5996 | 12.3838 | 12.3046 | NaN | NaN | NaN | 12.6788 | 126.2883 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 517.931 | NaN | 11.1718 | NaN | 26.2885
3353.1292 | 12.8144 | 12.4819 | 12.6219 | 12.9217 | 12.3114 | 12.633 | 12.3962 | 12.3082 | NaN | NaN | NaN | 12.6536 | 126.9356 | NaN | NaN | NaN | 4.9261 | NaN | NaN | NaN | NaN | 518.5404 | NaN | 25.2069 | NaN | 14.3018
3354.1292 | 12.8857 | 12.4623 | 12.6214 | 12.9246 | 12.4144 | 12.6153 | 12.389 | 12.3127 | NaN | NaN | NaN | 12.6435 | 119.1987 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.128 | NaN | 17.2055 | NaN | 20.705
3355.1292 | 12.8859 | 12.4411 | 12.6183 | 12.8831 | 12.4266 | 12.6139 | 12.3919 | 12.3041 | NaN | NaN | NaN | 12.6511 | 115.1976 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 522.5045 | NaN | 26.3623 | NaN | 17.8883
3356.1292 | 12.8846 | 12.4374 | 12.6169 | 12.8424 | 12.4124 | 12.5992 | 12.3798 | 12.3059 | NaN | NaN | NaN | 12.6596 | 130.8723 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 519.1753 | NaN | 21.4747 | NaN | 20.344
3357.1292 | 12.905 | 12.4566 | 12.6204 | 12.8594 | 12.3844 | 12.627 | 12.3899 | 12.3003 | NaN | NaN | NaN | 12.6578 | 124.6018 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 520.9193 | NaN | 25.3138 | NaN | 24.7554
3358.1292 | 12.7942 | 12.4377 | 12.617 | 12.9071 | 12.3172 | 12.6131 | 12.3868 | 12.301 | NaN | NaN | NaN | 12.6814 | 120.58 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 520.5634 | NaN | 41.1492 | NaN | 26.9238
3359.1292 | 12.8866 | 12.4608 | 12.6213 | 12.8472 | 12.4301 | 12.6119 | 12.3944 | 12.2926 | NaN | NaN | NaN | 12.6807 | 121.5256 | NaN | NaN | NaN | -11.8423 | NaN | NaN | NaN | NaN | 518.3873 | NaN | 11.8455 | NaN | 20.4408
3360.1292 | 12.9044 | 12.4804 | 12.6189 | 12.83 | 12.353 | 12.6293 | 12.3973 | 12.2854 | NaN | NaN | NaN | 12.7207 | 118.89 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.4934 | NaN | 27.2278 | NaN | 24.1425
3361.1292 | 12.7958 | 12.4455 | 12.6229 | 12.8765 | 12.3978 | 12.6149 | 12.3917 | 12.2925 | NaN | NaN | NaN | 12.6352 | 124.7399 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.5674 | NaN | 8.5664 | NaN | 19.5872
3362.1292 | 12.81 | 12.5164 | 12.6263 | 12.8916 | 12.3246 | 12.6469 | 12.4111 | 12.2892 | NaN | NaN | NaN | 12.6568 | 127.9323 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.3025 | NaN | 46.0123 | NaN | 18.4204
3363.1292 | 12.7808 | 12.4867 | 12.6267 | 12.8078 | 12.4336 | 12.6266 | 12.3995 | 12.2894 | NaN | NaN | NaN | 12.6786 | 109.0066 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 521.6648 | NaN | 14.1461 | NaN | 19.3241
3364.1292 | 12.889 | 12.5115 | 12.6271 | 12.8866 | 12.445 | 12.6459 | 12.425 | 12.2826 | NaN | NaN | NaN | 12.637 | 131.8169 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 520.3157 | NaN | 6.9565 | NaN | 16.5101
3365.1292 | 12.7723 | 12.5269 | 12.6275 | 12.8539 | 12.4566 | 12.6584 | 12.4312 | 12.2876 | NaN | NaN | NaN | 12.6585 | 127.9731 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 521.6313 | NaN | 13.7497 | NaN | 17.0762
3366.1292 | 12.76 | 12.4877 | 12.6222 | 12.8311 | 12.4438 | 12.6182 | 12.4007 | 12.281 | NaN | NaN | NaN | 12.6397 | 129.7494 | NaN | NaN | NaN | -2.3787 | NaN | NaN | NaN | NaN | 519.148 | NaN | 43.3013 | NaN | 20.2272
3367.1292 | 12.7645 | 12.505 | 12.6207 | 12.8604 | 12.4312 | 12.633 | 12.4071 | 12.2831 | NaN | NaN | NaN | 12.6671 | 128.3357 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 515.8525 | NaN | 11.5643 | NaN | 12.1289
3368.1292 | 12.7559 | 12.4378 | 12.6278 | 12.9179 | 12.4035 | 12.5898 | 12.3881 | 12.2829 | NaN | NaN | NaN | 12.7043 | 133.9161 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 516.4185 | NaN | 29.1263 | NaN | 15.2094
3369.1292 | 12.7276 | 12.4259 | 12.6248 | 12.8674 | 12.3649 | 12.6118 | 12.3927 | 12.2756 | NaN | NaN | NaN | 12.6574 | 119.7272 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 517.7847 | NaN | 8.6835 | NaN | 26.0517
3370.1292 | 12.7847 | 12.4226 | 12.6306 | 12.8591 | 12.4306 | 12.6018 | 12.3836 | 12.2818 | NaN | NaN | NaN | 12.6548 | 123.3456 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.6844 | NaN | 34.1864 | NaN | 21.4919
3371.1292 | 12.7494 | 12.4572 | 12.6351 | 12.856 | 12.4193 | 12.615 | 12.3956 | 12.2797 | NaN | NaN | NaN | 12.6565 | 114.7914 | NaN | NaN | NaN | 1.8484 | NaN | NaN | NaN | NaN | 519.0622 | NaN | 31.6612 | NaN | 25.1242
3372.1292 | 12.7662 | 12.4824 | 12.6317 | 12.8831 | 12.4288 | 12.6146 | 12.3995 | 12.2755 | NaN | NaN | NaN | 12.6135 | 131.9587 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 516.3569 | NaN | 35.5262 | NaN | 20.2602
3373.1292 | 12.7655 | 12.4357 | 12.6322 | 12.8786 | 12.4095 | 12.5975 | 12.3852 | 12.271 | NaN | NaN | NaN | 12.6385 | 111.4837 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.4093 | NaN | 16.9558 | NaN | 25.1138
3374.1292 | 12.7737 | 12.4186 | 12.6335 | 12.8935 | 12.4168 | 12.5811 | 12.3808 | 12.2742 | NaN | NaN | NaN | 12.6406 | 126.9922 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 517.943 | NaN | 35.5691 | NaN | 20.2845
3375.1292 | 12.7687 | 12.4277 | 12.6287 | 12.8651 | 12.4168 | 12.5919 | 12.3782 | 12.2836 | NaN | NaN | NaN | 12.6487 | 117.5766 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 516.5242 | NaN | 17.1565 | NaN | 18.0403
3376.1292 | 12.7913 | 12.4267 | 12.6299 | 12.8582 | 12.405 | 12.6052 | 12.3884 | 12.2763 | NaN | NaN | NaN | 12.6298 | 123.4632 | NaN | NaN | NaN | -1.8679 | NaN | NaN | NaN | NaN | 513.5629 | NaN | 18.6291 | NaN | 18.9933
3377.1292 | 12.7915 | 12.4622 | 12.6229 | 12.9323 | 12.4202 | 12.6216 | 12.4019 | 12.2756 | NaN | NaN | NaN | 12.6808 | 126.9085 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 511.7207 | NaN | 19.1613 | NaN | 25.1818
3378.1292 | 12.7745 | 12.4196 | 12.6256 | 12.842 | 12.4571 | 12.5945 | 12.3978 | 12.27 | NaN | NaN | NaN | 12.6406 | 131.3466 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 509.478 | NaN | 32.1938 | NaN | 17.845
3379.1292 | 12.778 | 12.4257 | 12.6287 | 12.9075 | 12.3957 | 12.5823 | 12.3918 | 12.2701 | NaN | NaN | NaN | 12.6498 | 124.9796 | NaN | NaN | NaN | 0.6642 | NaN | NaN | NaN | NaN | 507.1173 | NaN | 27.5842 | NaN | 26.1589
3380.1292 | 12.782 | 12.6258 | 12.6177 | 12.846 | 12.4647 | 12.6651 | 12.4497 | 12.2639 | NaN | NaN | NaN | 12.6811 | 110.3492 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 507.0394 | NaN | 7.8378 | NaN | 15.5607
3381.1292 | 12.7976 | 12.4217 | 12.6123 | 12.872 | 12.4256 | 12.5911 | 12.3894 | 12.2635 | NaN | NaN | NaN | 12.6286 | 130.0077 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 505.5497 | NaN | 9.7981 | NaN | 21.4393
3382.1292 | 12.801 | 12.4513 | 12.6082 | 12.848 | 12.4631 | 12.5969 | 12.4021 | 12.2638 | NaN | NaN | NaN | 12.6754 | 112.2656 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 510.9617 | NaN | 35.8075 | NaN | 16.5869
3383.1292 | 12.8257 | 12.4362 | 12.6115 | 12.9049 | 12.3642 | 12.6085 | 12.4037 | 12.2634 | NaN | NaN | NaN | 12.6288 | 127.4972 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 513.8743 | NaN | 16.4655 | NaN | 19.5421
3384.1292 | 12.8151 | 12.4294 | 12.609 | 12.8946 | 12.4538 | 12.5848 | 12.3928 | 12.2572 | NaN | NaN | NaN | 12.6569 | 115.4133 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 511.4801 | NaN | 12.5119 | NaN | 18.1293
3385.1292 | 12.8084 | 12.4242 | 12.6114 | 12.8907 | 12.4082 | 12.5836 | 12.3857 | 12.2516 | NaN | NaN | NaN | 12.7089 | 124.4005 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 513.3132 | NaN | 8.0862 | NaN | 14.0845
3386.1292 | 12.8144 | 12.433 | 12.604 | 12.8886 | 12.3629 | 12.5994 | 12.4015 | 12.2536 | NaN | NaN | NaN | 12.6533 | 125.7085 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 516.2141 | NaN | 11.2081 | NaN | 30.9149
3387.1292 | 12.8148 | 12.4635 | 12.6097 | 12.884 | 12.4185 | 12.6084 | 12.4126 | 12.2526 | NaN | NaN | NaN | 12.6597 | 120.4088 | NaN | NaN | NaN | 2.467 | NaN | NaN | NaN | NaN | 516.7466 | NaN | 31.1291 | NaN | 21.839
3388.1292 | 12.813 | 12.4386 | 12.6215 | 12.8488 | 12.3959 | 12.5975 | 12.3974 | 12.2587 | NaN | NaN | NaN | 12.6849 | 119.5494 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 512.5796 | NaN | 33.2117 | NaN | 12.3955
3389.1292 | 12.8132 | 12.4605 | 12.6126 | 12.9034 | 12.3405 | 12.6092 | 12.4019 | 12.2519 | NaN | NaN | NaN | 12.6488 | 116.3658 | NaN | NaN | NaN | -18.6354 | NaN | NaN | NaN | NaN | 507.0439 | NaN | 8.8193 | NaN | 20.9804
3390.1292 | 12.8097 | 12.4288 | 12.6139 | 12.8608 | 12.3933 | 12.5873 | 12.403 | 12.2511 | NaN | NaN | NaN | 12.699 | 123.6545 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 511.6042 | NaN | 42.3942 | NaN | 10.2225
3391.1292 | 12.8076 | 12.4194 | 12.6111 | 12.9007 | 12.3886 | 12.5878 | 12.4081 | 12.2542 | NaN | NaN | NaN | 12.6478 | 121.7073 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 509.0082 | NaN | 34.7332 | NaN | 20.0502
3392.1292 | 12.8175 | 12.486 | 12.615 | 12.8972 | 12.4581 | 12.6091 | 12.4162 | 12.2512 | NaN | NaN | NaN | 12.6521 | 129.3232 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 510.9949 | NaN | 12.4809 | NaN | 17.0891
3393.1292 | 12.796 | 12.4278 | 12.6121 | 12.9222 | 12.4204 | 12.5953 | 12.4114 | 12.2505 | NaN | NaN | NaN | 12.6745 | 119.9588 | NaN | NaN | NaN | 2.2934 | NaN | NaN | NaN | NaN | 512.2419 | NaN | 9.8823 | NaN | 26.0271
3394.1292 | 12.8402 | 12.4245 | 12.6146 | 12.9454 | 12.4582 | 12.602 | 12.4182 | 12.2484 | NaN | NaN | NaN | 12.697 | 122.65 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 516.6463 | NaN | 18.3575 | NaN | 26.7115
3395.1292 | 12.8798 | 12.4954 | 12.6108 | 12.8352 | 12.4632 | 12.6154 | 12.4216 | 12.2568 | NaN | NaN | NaN | 12.6708 | 124.9449 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 515.5461 | NaN | 39.9591 | NaN | 13.2684
3396.1292 | 12.8031 | 12.5519 | 12.6139 | 12.8749 | 12.4292 | 12.6434 | 12.4345 | 12.258 | NaN | NaN | NaN | 12.6604 | 114.575 | NaN | NaN | NaN | -4.9851 | NaN | NaN | NaN | NaN | 517.3489 | NaN | 8.7228 | NaN | 21.3699
3397.1292 | 12.7884 | 12.4419 | 12.6138 | 12.9029 | 12.461 | 12.5905 | 12.4115 | 12.2555 | NaN | NaN | NaN | 12.6507 | 114.3588 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 519.0516 | NaN | 9.9978 | NaN | 21.3854
3398.1292 | 12.8706 | 12.4461 | 12.6204 | 12.8735 | 12.3798 | 12.5907 | 12.4105 | 12.2593 | NaN | NaN | NaN | 12.7007 | 127.7455 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 517.1889 | NaN | 15.5265 | NaN | 24.1582
3399.1292 | 12.813 | 12.4443 | 12.6182 | 12.8694 | 12.4 | 12.5951 | 12.4137 | 12.2615 | NaN | NaN | NaN | 12.6594 | 121.81 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.8885 | NaN | 29.0222 | NaN | 18.2185
3400.1292 | 12.8164 | 12.4882 | 12.6168 | 12.8899 | 12.4346 | 12.6181 | 12.4233 | 12.2522 | NaN | NaN | NaN | 12.6369 | 126.0676 | NaN | NaN | NaN | -3.8744 | NaN | NaN | NaN | NaN | 520.7727 | NaN | 26.4603 | NaN | 21.7679
3401.1292 | 12.8253 | 12.5274 | 12.6206 | 12.867 | 12.4504 | 12.6315 | 12.4235 | 12.2602 | NaN | NaN | NaN | 12.657 | 125.5002 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 521.0743 | NaN | 40.6819 | NaN | 18.4901
3402.1292 | 12.8224 | 12.4856 | 12.6192 | 12.8947 | 12.4621 | 12.6212 | 12.4199 | 12.258 | NaN | NaN | NaN | 12.6694 | 113.7478 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 519.6969 | NaN | 8.5392 | NaN | 21.2016
3403.1292 | 12.8253 | 12.4809 | 12.6175 | 12.837 | 12.3726 | 12.6267 | 12.4178 | 12.2592 | NaN | NaN | NaN | 12.6701 | 129.6699 | NaN | NaN | NaN | -1.079 | NaN | NaN | NaN | NaN | 520.0709 | NaN | 10.7435 | NaN | 27.5029
3404.1292 | 12.8228 | 12.4865 | 12.6172 | 12.8722 | 12.3778 | 12.6469 | 12.4278 | 12.2563 | NaN | NaN | NaN | 12.6627 | 123.8663 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 517.1361 | NaN | 14.1659 | NaN | 17.529
3405.1292 | 12.8274 | 12.4759 | 12.6168 | 12.8897 | 12.4258 | 12.6267 | 12.4169 | 12.2666 | NaN | NaN | NaN | 12.6699 | 117.9649 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 517.2157 | NaN | 22.4696 | NaN | 23.0942
3406.1292 | 12.8246 | 12.4542 | 12.625 | 12.8666 | 12.4734 | 12.6036 | 12.4272 | 12.2593 | NaN | NaN | NaN | 12.6895 | 126.4284 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 517.836 | NaN | 47.2286 | NaN | 26.2696
3407.1292 | 12.8712 | 12.4486 | 12.6246 | 12.8815 | 12.4193 | 12.6185 | 12.4206 | 12.2563 | NaN | NaN | NaN | 12.6658 | 124.9386 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 519.7683 | NaN | 26.2201 | NaN | 20.2712
3408.1292 | 12.8297 | 12.4796 | 12.6222 | 12.8655 | 12.4388 | 12.6216 | 12.4196 | 12.2641 | NaN | NaN | NaN | 12.6789 | 117.9524 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.6292 | NaN | 27.8592 | NaN | 23.3824
3409.1292 | 12.8524 | 12.4553 | 12.6227 | 12.9187 | 12.4186 | 12.6077 | 12.4144 | 12.2553 | NaN | NaN | NaN | 12.6498 | 120.3243 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 517.3026 | NaN | 9.0105 | NaN | 16.1021
3410.1292 | 12.9053 | 12.441 | 12.6287 | 12.8615 | 12.4267 | 12.6035 | 12.4149 | 12.2641 | NaN | NaN | NaN | 12.6519 | 128.9162 | NaN | NaN | NaN | 0.333 | NaN | NaN | NaN | NaN | 517.1527 | NaN | 12.3182 | NaN | 17.6072
3411.1292 | 12.8471 | 12.4736 | 12.627 | 12.902 | 12.458 | 12.6187 | 12.4184 | 12.2541 | NaN | NaN | NaN | 12.7521 | 114.5394 | NaN | NaN | NaN | 13.273 | NaN | NaN | NaN | NaN | 514.3873 | NaN | 34.0727 | NaN | 20.5956
3412.1292 | 12.8377 | 12.4771 | 12.6292 | 12.8623 | 12.434 | 12.6191 | 12.4071 | 12.2494 | NaN | NaN | NaN | 12.7043 | 124.0231 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 513.7849 | NaN | 19.3794 | NaN | 32.1644
3413.1292 | 12.8282 | 12.4888 | 12.6214 | 12.8356 | 12.4739 | 12.6155 | 12.4152 | 12.249 | NaN | NaN | NaN | 12.6504 | 124.4883 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 517.7277 | NaN | 12.6646 | NaN | 22.6346
3414.1292 | 12.8307 | 12.5109 | 12.6189 | 12.8816 | 12.358 | 12.6336 | 12.4233 | 12.2492 | NaN | NaN | NaN | 12.7157 | 124.3649 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 513.0589 | NaN | 15.6038 | NaN | 22.7525
3415.1292 | 12.825 | 12.4747 | 12.6156 | 12.8344 | 12.4072 | 12.6157 | 12.4085 | 12.2495 | NaN | NaN | NaN | 12.6408 | 125.449 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.0161 | NaN | 31.2991 | NaN | 23.6702
3416.1292 | 12.8277 | 12.4856 | 12.6256 | 12.8642 | 12.4072 | 12.6341 | 12.4104 | 12.2392 | NaN | NaN | NaN | 12.6532 | 118.0996 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 514.8167 | NaN | 12.4791 | NaN | 23.4214
3417.1292 | 12.8945 | 12.499 | 12.6183 | 12.8613 | 12.4206 | 12.6348 | 12.4224 | 12.2485 | NaN | NaN | NaN | 12.6382 | 130.6235 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 517.2841 | NaN | 8.7133 | NaN | 25.2051
3418.1292 | 12.8511 | 12.501 | 12.619 | 12.8273 | 12.3961 | 12.6389 | 12.4219 | 12.2466 | NaN | NaN | NaN | 12.6223 | 110.1927 | NaN | NaN | NaN | -8.681 | NaN | NaN | NaN | NaN | 517.2261 | NaN | 7.2505 | NaN | 20.2818
3419.1292 | 12.8483 | 12.4922 | 12.6124 | 12.8509 | 12.4128 | 12.6311 | 12.4172 | 12.2441 | NaN | NaN | NaN | 12.6598 | 123.0672 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 514.637 | NaN | 13.4346 | NaN | 27.6188
3420.1292 | 12.8423 | 12.5022 | 12.6196 | 12.8395 | 12.4362 | 12.638 | 12.4208 | 12.2431 | NaN | NaN | NaN | 12.6335 | 119.7766 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 517.9423 | NaN | 14.6461 | NaN | 19.1274
3421.1292 | 12.853 | 12.4543 | 12.6205 | 12.8705 | 12.4627 | 12.6261 | 12.4172 | 12.2371 | NaN | NaN | NaN | 12.6495 | 132.258 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.2213 | NaN | 12.6252 | NaN | 13.9747
3422.1292 | 12.8398 | 12.5868 | 12.6202 | 12.8143 | 12.4113 | 12.6837 | 12.4493 | 12.2385 | NaN | NaN | NaN | 12.6742 | 124.601 | NaN | NaN | NaN | -5.4962 | NaN | NaN | NaN | NaN | 518.2669 | NaN | 42.8204 | NaN | 19.4114
3423.1292 | 12.9833 | 12.4846 | 12.6134 | 12.8348 | 12.4467 | 12.6419 | 12.4299 | 12.2508 | NaN | NaN | NaN | 12.6324 | 127.0059 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.5501 | NaN | 18.2993 | NaN | 13.4474
3424.1292 | 12.8734 | 12.4352 | 12.61 | 12.8708 | 12.3747 | 12.6225 | 12.4141 | 12.2517 | NaN | NaN | NaN | 12.6359 | 124.9154 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.0566 | NaN | 19.4453 | NaN | 17.7054
3425.1292 | 12.8588 | 12.4643 | 12.6131 | 12.8574 | 12.4537 | 12.6261 | 12.4149 | 12.2408 | NaN | NaN | NaN | 12.6381 | 130.2367 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 515.1316 | NaN | 41.3206 | NaN | 18.7707
3426.1292 | 12.8653 | 12.4827 | 12.613 | 12.8992 | 12.4795 | 12.6269 | 12.4209 | 12.247 | NaN | NaN | NaN | 12.6281 | 120.0721 | NaN | NaN | NaN | 7.7994 | NaN | NaN | NaN | NaN | 513.2107 | NaN | 16.5093 | NaN | 18.1824
3427.1292 | 12.853 | 12.4635 | 12.6154 | 12.8642 | 12.4514 | 12.6234 | 12.4133 | 12.2514 | NaN | NaN | NaN | 12.6485 | 125.9124 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 510.5744 | NaN | 18.0125 | NaN | 17.668
3428.1292 | 12.8495 | 12.4462 | 12.6151 | 12.8606 | 12.464 | 12.6073 | 12.408 | 12.2487 | NaN | NaN | NaN | 12.6823 | 131.6608 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 509.6049 | NaN | 35.8715 | NaN | 18.5857
3429.1292 | 12.8533 | 12.5156 | 12.6105 | 12.8428 | 12.3928 | 12.6487 | 12.4255 | 12.2543 | NaN | NaN | NaN | 12.6507 | 127.4797 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 512.3105 | NaN | 27.6072 | NaN | 19.421
3430.1292 | 12.8463 | 12.4876 | 12.625 | 12.8705 | 12.4197 | 12.628 | 12.4131 | 12.2509 | NaN | NaN | NaN | 12.6686 | 135.6493 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 513.7875 | NaN | 10.7125 | NaN | 21.2173
3431.1292 | 12.8446 | 12.4513 | 12.6218 | 12.8523 | 12.4351 | 12.609 | 12.4142 | 12.2533 | NaN | NaN | NaN | 12.6616 | 127.8702 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 513.9565 | NaN | 31.6098 | NaN | 23.8024
3432.1292 | 12.8466 | 12.4855 | 12.6231 | 12.8695 | 12.4324 | 12.6301 | 12.4167 | 12.2572 | NaN | NaN | NaN | 12.6586 | 115.5969 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 512.7265 | NaN | 11.3027 | NaN | 22.8856
3433.1292 | 12.9253 | 12.5274 | 12.6238 | 12.8561 | 12.4913 | 12.6303 | 12.4305 | 12.2602 | NaN | NaN | NaN | 12.6373 | 116.4556 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 512.1382 | NaN | 10.9043 | NaN | 19.84
3434.1292 | 12.8232 | 12.5478 | 12.6294 | 12.8786 | 12.4811 | 12.6275 | 12.4296 | 12.2632 | NaN | NaN | NaN | 12.6856 | 138.2008 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 511.7947 | NaN | 16.2782 | NaN | 16.4593
3435.1292 | 12.9157 | 12.4976 | 12.6228 | 12.8382 | 12.4574 | 12.6253 | 12.4188 | 12.2666 | NaN | NaN | NaN | 12.7174 | 118.6902 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 513.8013 | NaN | 27.9456 | NaN | 13.2914
3436.1292 | 12.8509 | 12.4908 | 12.6241 | 12.9123 | 12.4539 | 12.6349 | 12.4263 | 12.2658 | NaN | NaN | NaN | 12.6946 | 127.3558 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 513.7994 | NaN | 11.1439 | NaN | 15.9553
3437.1292 | 12.8423 | 12.4779 | 12.615 | 12.8352 | 12.4355 | 12.6122 | 12.4165 | 12.2698 | NaN | NaN | NaN | 12.6776 | 129.139 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 512.972 | NaN | 26.5291 | NaN | 23.433
3438.1292 | 12.8326 | 12.5204 | 12.6082 | 12.8766 | 12.4666 | 12.6367 | 12.4264 | 12.2759 | NaN | NaN | NaN | 12.7019 | 122.5122 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 512.5081 | NaN | 14.3318 | NaN | 16.623
3439.1292 | 12.8471 | 12.5073 | 12.6029 | 12.8231 | 12.4432 | 12.6283 | 12.4206 | 12.2735 | NaN | NaN | NaN | 12.6897 | 125.9811 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 515.5952 | NaN | 8.7691 | NaN | 17.877
3440.1292 | 12.8444 | 12.5269 | 12.5932 | 12.8709 | 12.4254 | 12.6479 | 12.4288 | 12.274 | NaN | NaN | NaN | 12.6893 | 124.0645 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 514.2661 | NaN | 46.3665 | NaN | 21.921
3441.1292 | 12.8438 | 12.5194 | 12.5933 | 12.8414 | 12.4816 | 12.6321 | 12.4225 | 12.2822 | NaN | NaN | NaN | 12.6877 | 126.6659 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 516.2078 | NaN | 14.6537 | NaN | 13.6968
3442.1292 | 12.8409 | 12.4812 | 12.5904 | 12.8855 | 12.4329 | 12.6184 | 12.4196 | 12.2787 | NaN | NaN | NaN | 12.7228 | 134.1725 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 516.3699 | NaN | 9.5132 | NaN | 19.6593
3443.1292 | 12.8403 | 12.4893 | 12.5846 | 12.868 | 12.5029 | 12.6174 | 12.4162 | 12.2838 | NaN | NaN | NaN | 12.6812 | 117.8924 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 516.2779 | NaN | 14.4723 | NaN | 11.5544
3444.1292 | 12.8151 | 12.4902 | 12.5804 | 12.8211 | 12.4244 | 12.6289 | 12.4124 | 12.2743 | NaN | NaN | NaN | 12.6905 | 129.6749 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 515.4043 | NaN | 33.4313 | NaN | 23.0741
3445.1292 | 12.8769 | 12.5206 | 12.5809 | 12.8173 | 12.4004 | 12.6321 | 12.4134 | 12.2811 | NaN | NaN | NaN | 12.6708 | 119.6389 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.6086 | NaN | 22.0735 | NaN | 25.6639
3446.1292 | 12.8395 | 12.4949 | 12.5759 | 12.841 | 12.4551 | 12.6051 | 12.3958 | 12.2823 | NaN | NaN | NaN | 12.7297 | 147.3642 | NaN | NaN | NaN | -1.8601 | NaN | NaN | NaN | NaN | 517.7182 | NaN | 23.3361 | NaN | 19.3531
3447.1292 | 12.8404 | 12.5166 | 12.569 | 12.8488 | 12.4059 | 12.6256 | 12.4079 | 12.2796 | NaN | NaN | NaN | 12.6772 | 131.3631 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 514.5568 | NaN | 13.6903 | NaN | 15.8808
3448.1292 | 12.8415 | 12.5119 | 12.5672 | 12.8437 | 12.4533 | 12.621 | 12.4068 | 12.273 | NaN | NaN | NaN | 12.683 | 125.6915 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 517.1518 | NaN | 24.8543 | NaN | 21.2741
3449.1292 | 12.8338 | 12.571 | 12.5657 | 12.8219 | 12.469 | 12.6333 | 12.4209 | 12.283 | NaN | NaN | NaN | 12.694 | 126.6761 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 517.9858 | NaN | 29.1963 | NaN | 18.9522
3450.1292 | 12.8972 | 12.5209 | 12.5714 | 12.8717 | 12.4859 | 12.624 | 12.4063 | 12.2801 | NaN | NaN | NaN | 12.6705 | 125.1157 | NaN | NaN | NaN | -3.8805 | NaN | NaN | NaN | NaN | 513.9781 | NaN | 25.4877 | NaN | 20.5923
3451.1292 | 12.8315 | 12.5129 | 12.5658 | 12.8413 | 12.4363 | 12.616 | 12.3985 | 12.2795 | NaN | NaN | NaN | 12.6778 | 125.7262 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 513.4643 | NaN | 27.49 | NaN | 26.1469
3452.1292 | 12.8365 | 12.5178 | 12.5684 | 12.8074 | 12.4339 | 12.6198 | 12.397 | 12.2792 | NaN | NaN | NaN | 12.7183 | 126.8263 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 514.5322 | NaN | 8.422 | NaN | 27.0417
3453.1292 | 12.8299 | 12.4915 | 12.5685 | 12.8429 | 12.4448 | 12.6039 | 12.4012 | 12.2813 | NaN | NaN | NaN | 12.7287 | 122.0632 | NaN | NaN | NaN | 2.5188 | NaN | NaN | NaN | NaN | 511.5994 | NaN | 17.6358 | NaN | 12.5166
3454.1292 | 12.8747 | 12.5494 | 12.5673 | 12.8698 | 12.3472 | 12.6337 | 12.4117 | 12.2851 | NaN | NaN | NaN | 12.6948 | 122.8762 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 515.408 | NaN | 30.2766 | NaN | 13.5315
3455.1292 | 12.834 | 12.5166 | 12.5745 | 12.872 | 12.4102 | 12.6063 | 12.4001 | 12.2904 | NaN | NaN | NaN | 12.7104 | 134.0218 | NaN | NaN | NaN | -15.2654 | NaN | NaN | NaN | NaN | 515.9826 | NaN | 36.4375 | NaN | 24.7491
3456.1292 | 12.8704 | 12.5172 | 12.5749 | 12.8736 | 12.4796 | 12.6132 | 12.4093 | 12.2865 | NaN | NaN | NaN | 12.7203 | 126.3628 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 512.2331 | NaN | 13.4811 | NaN | 10.3239
3457.1292 | 12.9238 | 12.5155 | 12.5729 | 12.8601 | 12.4053 | 12.6047 | 12.4066 | 12.2893 | NaN | NaN | NaN | 12.6971 | 124.5207 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 512.1101 | NaN | 14.0487 | NaN | 22.6495
3458.1292 | 12.9002 | 12.5209 | 12.5798 | 12.903 | 12.3967 | 12.61 | 12.4013 | 12.2847 | NaN | NaN | NaN | 12.7093 | 126.4582 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -10.7763 | 513.3165 | NaN | 27.638 | NaN | 12.8693
3459.1292 | 12.8667 | 12.6065 | 12.5755 | 12.892 | 12.4473 | 12.6145 | 12.4204 | 12.2818 | NaN | NaN | NaN | 12.7018 | 124.7877 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 515.5168 | NaN | 26.2777 | NaN | 25.4095
3460.1292 | 12.8706 | 12.5651 | 12.5798 | 12.8694 | 12.4172 | 12.6255 | 12.4075 | 12.284 | NaN | NaN | NaN | 12.6871 | 120.6206 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 513.0331 | NaN | 29.8332 | NaN | 18.7466
3461.1292 | 12.8758 | 12.5404 | 12.5821 | 12.8555 | 12.5021 | 12.6089 | 12.4058 | 12.2866 | NaN | NaN | NaN | 12.6927 | 141.1916 | NaN | NaN | NaN | -15.3434 | NaN | NaN | NaN | NaN | 511.7086 | NaN | 8.7811 | NaN | 21.4475
3462.1292 | 12.8515 | 12.5171 | 12.58 | 12.8312 | 12.4819 | 12.6164 | 12.4023 | 12.2885 | NaN | NaN | NaN | 12.7021 | 120.013 | NaN | NaN | NaN | -0.1237 | NaN | NaN | NaN | NaN | 517.3795 | NaN | 18.9581 | NaN | 24.2638
3463.1292 | 12.863 | 12.5875 | 12.5777 | 12.8676 | 12.3848 | 12.6663 | 12.4107 | 12.2853 | NaN | NaN | NaN | 12.6902 | 128.1368 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 513.9325 | NaN | 14.1748 | NaN | 21.4462
3464.1292 | 12.866 | 12.6116 | 12.5862 | 12.8458 | 12.4079 | 12.6484 | 12.4108 | 12.2873 | NaN | NaN | NaN | 12.7107 | 130.1376 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 517.2531 | NaN | 11.7733 | NaN | 12.5126
3465.1292 | 12.8661 | 12.5577 | 12.5801 | 12.8628 | 12.4216 | 12.6515 | 12.4081 | 12.2915 | NaN | NaN | NaN | 12.7127 | 122.0832 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.1981 | NaN | 9.9843 | NaN | 16.875
3466.1292 | 12.8468 | 12.5075 | 12.5842 | 12.8688 | 12.4791 | 12.6084 | 12.3924 | 12.2894 | NaN | NaN | NaN | 12.6755 | 117.4662 | NaN | NaN | NaN | 4.7417 | NaN | NaN | NaN | NaN | 516.2764 | NaN | 11.609 | NaN | 28.6962
3467.1292 | 12.9132 | 12.6041 | 12.5879 | 12.8629 | 12.4809 | 12.6612 | 12.4278 | 12.2952 | NaN | NaN | NaN | 12.698 | 121.4355 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 513.3985 | NaN | 12.9099 | NaN | 24.1775
3468.1292 | 12.8525 | 12.5293 | 12.5903 | 12.8334 | 12.4638 | 12.6465 | 12.3947 | 12.2912 | NaN | NaN | NaN | 12.6659 | 126.7715 | NaN | NaN | NaN | -3.6442 | NaN | NaN | NaN | NaN | 513.3502 | NaN | 13.0121 | NaN | 27.2871
3469.1292 | 12.8762 | 12.5559 | 12.5955 | 12.8865 | 12.3871 | 12.6605 | 12.4077 | 12.2973 | NaN | NaN | NaN | 12.6722 | 122.1391 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 513.7445 | NaN | 11.4438 | NaN | 17.1189
3470.1292 | 12.8817 | 12.5161 | 12.5934 | 12.8834 | 12.4293 | 12.6407 | 12.4017 | 12.2978 | NaN | NaN | NaN | 12.714 | 115.9918 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 511.793 | NaN | 25.1599 | NaN | 25.9838
3471.1292 | 12.8642 | 12.6086 | 12.5988 | 12.9275 | 12.4357 | 12.6831 | 12.4165 | 12.2996 | NaN | NaN | NaN | 12.7311 | 123.0644 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 515.2613 | NaN | 21.1705 | NaN | 19.4995
3472.1292 | 12.8466 | 12.502 | 12.5955 | 12.9478 | 12.4777 | 12.6347 | 12.3926 | 12.3027 | NaN | NaN | NaN | 12.7008 | 125.0906 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 512.0017 | NaN | 33.3922 | NaN | 14.7788
3473.1292 | 12.8243 | 12.527 | 12.6011 | 12.8738 | 12.3896 | 12.6627 | 12.4066 | 12.3017 | NaN | NaN | NaN | 12.7146 | 116.6004 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 513.1163 | NaN | 30.407 | NaN | 26.1833
3474.1292 | 12.8932 | 12.5178 | 12.6038 | 12.8803 | 12.373 | 12.661 | 12.401 | 12.294 | NaN | NaN | NaN | 12.7485 | 123.027 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 512.019 | NaN | 18.4242 | NaN | 21.7766
3475.1292 | 12.8586 | 12.512 | 12.6015 | 12.9092 | 12.4016 | 12.6612 | 12.407 | 12.2994 | NaN | NaN | NaN | 12.7046 | 121.7352 | NaN | NaN | NaN | 0.3462 | NaN | NaN | NaN | NaN | 512.5514 | NaN | 28.9647 | NaN | 25.3464
3476.1292 | 12.9417 | 12.532 | 12.608 | 12.9014 | 12.4466 | 12.6625 | 12.4126 | 12.2967 | NaN | NaN | NaN | 12.7425 | 128.2188 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 512.399 | NaN | 8.6444 | NaN | 23.1174
3477.1292 | 12.8901 | 12.5209 | 12.6027 | 12.8556 | 12.3761 | 12.6796 | 12.4082 | 12.3007 | NaN | NaN | NaN | 12.7195 | 124.7638 | NaN | NaN | NaN | -3.0218 | NaN | NaN | NaN | NaN | 512.9163 | NaN | 38.6481 | NaN | 7.2143
3478.1292 | 12.884 | 12.526 | 12.6047 | 12.8612 | 12.444 | 12.6673 | 12.41 | 12.2941 | NaN | NaN | NaN | 12.69 | 126.2859 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 512.9179 | NaN | 10.5869 | NaN | 22.9019
3479.1292 | 12.8303 | 12.5222 | 12.614 | 12.8816 | 12.4674 | 12.6518 | 12.4052 | 12.2931 | NaN | NaN | NaN | 12.7064 | 124.2016 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 512.0985 | NaN | 21.5974 | NaN | 16.6214
3480.1292 | 12.8331 | 12.5166 | 12.6099 | 12.8639 | 12.5134 | 12.6465 | 12.408 | 12.2895 | NaN | NaN | NaN | 12.7231 | 117.1156 | NaN | NaN | NaN | -16.662 | NaN | NaN | NaN | NaN | 512.218 | NaN | 43.7382 | NaN | 25.8524
3481.1292 | 12.8387 | 12.534 | 12.6126 | 12.9206 | 12.5102 | 12.6631 | 12.416 | 12.288 | NaN | NaN | NaN | 12.6987 | 118.5011 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 511.5433 | NaN | 11.7031 | NaN | 19.1717
3482.1292 | 12.892 | 12.5121 | 12.6185 | 12.8763 | 12.4697 | 12.636 | 12.4071 | 12.2859 | NaN | NaN | NaN | 12.7045 | 122.5764 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 515.5984 | NaN | 26.9687 | NaN | 17.4818
3483.1292 | 12.8597 | 12.4955 | 12.619 | 12.9194 | 12.4032 | 12.6377 | 12.4105 | 12.2927 | NaN | NaN | NaN | 12.7332 | 119.2756 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 516.8764 | NaN | 14.6684 | NaN | 21.1858
3484.1292 | 12.8376 | 12.5013 | 12.615 | 12.9013 | 12.5102 | 12.6314 | 12.4015 | 12.2866 | NaN | NaN | NaN | 12.7273 | 122.0398 | NaN | NaN | NaN | -7.5368 | NaN | NaN | NaN | NaN | 513.7792 | NaN | 31.5207 | NaN | 27.8539
3485.1292 | 12.8514 | 12.5288 | 12.6232 | 12.9273 | 12.4234 | 12.6517 | 12.4079 | 12.2844 | NaN | NaN | NaN | 12.7116 | 126.8093 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 515.2148 | NaN | 8.2656 | NaN | 22.3687
3486.1292 | 12.8007 | 12.5477 | 12.6193 | 12.9272 | 12.3865 | 12.6589 | 12.4052 | 12.2841 | NaN | NaN | NaN | 12.6874 | 126.1554 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 516.6083 | NaN | 29.3103 | NaN | 18.258
3487.1292 | 12.8565 | 12.5799 | 12.6192 | 12.8539 | 12.469 | 12.6474 | 12.4068 | 12.2831 | NaN | NaN | NaN | 12.7181 | 116.54 | NaN | NaN | NaN | -9.2108 | NaN | NaN | NaN | NaN | 518.9336 | NaN | 23.4798 | NaN | 23.7598
3488.1292 | 12.9448 | 12.5594 | 12.6214 | 12.9102 | 12.4862 | 12.653 | 12.4066 | 12.2805 | NaN | NaN | NaN | 12.7081 | 119.5564 | NaN | NaN | NaN | 20.9031 | NaN | NaN | NaN | NaN | 518.0813 | NaN | 9.9848 | NaN | 16.6243
3489.1292 | 12.8513 | 12.5599 | 12.6236 | 12.8957 | 12.4961 | 12.6296 | 12.4119 | 12.2767 | NaN | NaN | NaN | 12.6912 | 123.0854 | NaN | NaN | NaN | 7.5155 | NaN | NaN | NaN | NaN | 516.2161 | NaN | 10.916 | NaN | 18.9711
3490.1292 | 12.8955 | 12.6417 | 12.6286 | 12.8688 | 12.497 | 12.6797 | 12.4231 | 12.2734 | NaN | NaN | NaN | 12.7122 | 130.6491 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 517.0147 | NaN | 8.305 | NaN | 26.918
3491.1292 | 12.9422 | 12.5057 | 12.6257 | 12.8842 | 12.4182 | 12.6348 | 12.4042 | 12.2812 | NaN | NaN | NaN | 12.7296 | 125.2148 | NaN | NaN | NaN | -2.9922 | NaN | NaN | NaN | NaN | 518.391 | NaN | 30.7123 | NaN | 17.309
3492.1292 | 12.849 | 12.5559 | 12.6339 | 12.9199 | 12.447 | 12.6454 | 12.4086 | 12.272 | NaN | NaN | NaN | 12.7316 | 128.1413 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 520.7536 | NaN | 28.2557 | NaN | 11.883
3493.1292 | 12.8769 | 12.516 | 12.6355 | 12.9332 | 12.4858 | 12.6263 | 12.4041 | 12.2808 | NaN | NaN | NaN | 12.695 | 119.4732 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 517.9344 | NaN | 8.5921 | NaN | 15.0667
3494.1292 | 12.8519 | 12.4901 | 12.6298 | 12.8774 | 12.4963 | 12.6077 | 12.401 | 12.278 | NaN | NaN | NaN | 12.7013 | 126.4406 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.8761 | NaN | 37.4984 | NaN | 23.7651
3495.1292 | 12.8154 | 12.5202 | 12.6287 | 12.8491 | 12.4812 | 12.6319 | 12.4128 | 12.2757 | NaN | NaN | NaN | 12.7231 | 118.3464 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.5479 | NaN | 17.532 | NaN | 22.274
3496.1292 | 12.7926 | 12.5169 | 12.6256 | 12.9064 | 12.4952 | 12.6343 | 12.4118 | 12.2812 | NaN | NaN | NaN | 12.8059 | 116.639 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 513.1593 | NaN | 28.76 | NaN | 22.9281
3497.1292 | 12.8185 | 12.5455 | 12.622 | 12.8928 | 12.4539 | 12.651 | 12.4085 | 12.2835 | NaN | NaN | NaN | 12.725 | 124.8452 | NaN | NaN | NaN | 0.3192 | NaN | NaN | NaN | NaN | 515.2545 | NaN | 15.8919 | NaN | 19.2981
3498.1292 | 12.8173 | 12.523 | 12.6236 | 12.8646 | 12.3768 | 12.6569 | 12.4084 | 12.2768 | NaN | NaN | NaN | 12.7495 | 129.3957 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 517.5955 | NaN | 10.0616 | NaN | 20.4813
3499.1292 | 12.8217 | 12.4774 | 12.629 | 12.9034 | 12.4695 | 12.6217 | 12.3966 | 12.2755 | NaN | NaN | NaN | 12.7196 | 128.4367 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.7725 | NaN | 22.3356 | NaN | 22.7764
3500.1292 | 12.824 | 12.5347 | 12.6258 | 12.9538 | 12.4842 | 12.6641 | 12.4201 | 12.2802 | NaN | NaN | NaN | 12.7023 | 127.1653 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 517.2067 | NaN | 17.8351 | NaN | 24.7957
3501.1292 | 12.8178 | 12.4918 | 12.6263 | 12.8992 | 12.478 | 12.6517 | 12.4142 | 12.2764 | NaN | NaN | NaN | 12.7345 | 125.7392 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 517.7063 | NaN | 8.9542 | NaN | 29.5289
3502.1292 | 12.8166 | 12.5049 | 12.6325 | 12.9516 | 12.5069 | 12.639 | 12.3963 | 12.2792 | NaN | NaN | NaN | 12.7039 | 130.2514 | NaN | NaN | NaN | 2.5082 | NaN | NaN | NaN | NaN | 513.3254 | NaN | 28.7686 | NaN | 20.395
3503.1292 | 12.8186 | 12.5103 | 12.6247 | 12.9208 | 12.4729 | 12.6456 | 12.3995 | 12.2769 | NaN | NaN | NaN | 12.6941 | 130.6958 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 515.1593 | NaN | 20.9379 | NaN | 27.6958
3504.1292 | 12.8165 | 12.513 | 12.6246 | 12.9137 | 12.4598 | 12.6547 | 12.4019 | 12.2818 | NaN | NaN | NaN | 12.7101 | 127.4493 | NaN | NaN | NaN | -6.1956 | NaN | NaN | NaN | NaN | 513.9308 | NaN | 13.6499 | NaN | 27.9177
3505.1292 | 12.8233 | 12.5097 | 12.6218 | 12.8823 | 12.3873 | 12.6724 | 12.4027 | 12.2735 | NaN | NaN | NaN | 12.7054 | 112.6533 | NaN | NaN | NaN | -2.6606 | NaN | NaN | NaN | NaN | 512.2518 | NaN | 8.4679 | NaN | 20.2392
3506.1292 | 12.8144 | 12.5263 | 12.6257 | 12.9063 | 12.3994 | 12.6692 | 12.406 | 12.2741 | NaN | NaN | NaN | 12.711 | 123.1202 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 517.9682 | NaN | 13.9325 | NaN | 14.3257
3507.1292 | 12.8309 | 12.5013 | 12.621 | 12.9111 | 12.4723 | 12.6419 | 12.3953 | 12.2742 | NaN | NaN | NaN | 12.7109 | 129.1219 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 519.5767 | NaN | 8.1998 | NaN | 23.6488
3508.1292 | 12.8308 | 12.53 | 12.6209 | 12.8902 | 12.4108 | 12.6716 | 12.4038 | 12.2709 | NaN | NaN | NaN | 12.7107 | 119.5816 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.8792 | NaN | 30.6777 | NaN | 30.5758
3509.1292 | 12.8388 | 12.5538 | 12.6198 | 12.9564 | 12.4997 | 12.6746 | 12.4187 | 12.2711 | NaN | NaN | NaN | 12.8309 | 124.3437 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.3739 | NaN | 25.1285 | NaN | 18.9598
3510.1292 | 12.8282 | 12.6496 | 12.6238 | 12.936 | 12.3917 | 12.7434 | 12.4257 | 12.27 | NaN | NaN | NaN | 12.6943 | 124.3041 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 519.9181 | NaN | 32.5224 | NaN | 18.7718
3511.1292 | 12.8274 | 12.5098 | 12.6214 | 12.8857 | 12.4654 | 12.6823 | 12.4133 | 12.2738 | NaN | NaN | NaN | 12.7014 | 117.8105 | NaN | NaN | NaN | 10.1763 | NaN | NaN | NaN | NaN | 518.0849 | NaN | 9.5099 | NaN | 26.0358
3512.1292 | 12.8245 | 12.5224 | 12.6171 | 12.9312 | 12.3829 | 12.6856 | 12.4126 | 12.2728 | NaN | NaN | NaN | 12.7133 | 123.5452 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.3041 | NaN | 14.9476 | NaN | 17.9736
3513.1292 | 12.8241 | 12.4947 | 12.6214 | 12.9672 | 12.517 | 12.6591 | 12.408 | 12.2776 | NaN | NaN | NaN | 12.7043 | 133.4872 | NaN | NaN | NaN | -16.3655 | NaN | NaN | NaN | NaN | 517.1243 | NaN | 19.1168 | NaN | 19.1056
3514.1292 | 12.8089 | 12.4903 | 12.6198 | 12.9266 | 12.4689 | 12.6638 | 12.4156 | 12.2785 | NaN | NaN | NaN | 12.7001 | 122.1552 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 516.2908 | NaN | 40.5873 | NaN | 18.8132
3515.1292 | 12.808 | 12.4871 | 12.6185 | 12.909 | 12.4833 | 12.6591 | 12.4142 | 12.2757 | NaN | NaN | NaN | 12.7026 | 132.1718 | NaN | NaN | NaN | -19.4507 | NaN | NaN | NaN | NaN | 516.7943 | NaN | 17.2447 | NaN | 20.2603
3516.1292 | 12.823 | 12.5509 | 12.6245 | 12.9361 | 12.3942 | 12.6921 | 12.4248 | 12.2765 | NaN | NaN | NaN | 12.6736 | 127.9239 | NaN | NaN | NaN | -7.0887 | NaN | NaN | NaN | NaN | 518.6168 | NaN | 7.2601 | NaN | 12.0867
3517.1292 | 12.8293 | 12.5438 | 12.6302 | 12.9209 | 12.5014 | 12.6756 | 12.428 | 12.2778 | NaN | NaN | NaN | 12.6961 | 129.1731 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 517.5277 | NaN | 38.9863 | NaN | 31.534
3518.1292 | 12.8283 | 12.536 | 12.6261 | 12.9192 | 12.4306 | 12.6753 | 12.4228 | 12.2666 | NaN | NaN | NaN | 12.6921 | 126.7705 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 517.0953 | NaN | 15.0333 | NaN | 13.3581
3519.1292 | 12.8336 | 12.4874 | 12.6326 | 12.9012 | 12.4776 | 12.6558 | 12.4062 | 12.2693 | NaN | NaN | NaN | 12.7243 | 117.4761 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 515.3879 | NaN | 10.5541 | NaN | 16.3062
3520.1292 | 12.8317 | 12.5923 | 12.6242 | 12.9408 | 12.4903 | 12.6978 | 12.4322 | 12.2664 | NaN | NaN | NaN | 12.7093 | 129.8208 | NaN | NaN | NaN | 5.8216 | NaN | NaN | NaN | NaN | 510.6165 | NaN | 11.8491 | NaN | 23.2206
3521.1292 | 12.8264 | 12.4973 | 12.6237 | 12.9748 | 12.394 | 12.6631 | 12.4103 | 12.2639 | NaN | NaN | NaN | 12.6839 | 121.1414 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 516.0413 | NaN | 41.6299 | NaN | 25.2081
3522.1292 | 12.8286 | 12.5116 | 12.6194 | 12.9085 | 12.4303 | 12.683 | 12.4109 | 12.2649 | NaN | NaN | NaN | 12.6966 | 123.7187 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 515.0953 | NaN | 7.4016 | NaN | 22.3185
3523.1292 | 12.8263 | 12.5161 | 12.6186 | 12.9041 | 12.4696 | 12.6903 | 12.4182 | 12.2572 | NaN | NaN | NaN | 12.7285 | 125.649 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 516.4387 | NaN | 19.7594 | NaN | 18.6351
3524.1292 | 12.8207 | 12.4785 | 12.628 | 12.8778 | 12.4602 | 12.6818 | 12.4157 | 12.2633 | NaN | NaN | NaN | 12.6878 | 124.9239 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.7927 | NaN | 30.7658 | NaN | 26.5857
3525.1292 | 12.8223 | 12.496 | 12.6227 | 12.9411 | 12.3811 | 12.686 | 12.4236 | 12.2632 | NaN | NaN | NaN | 12.6777 | 123.4345 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 517.6107 | NaN | 11.551 | NaN | 20.6681
3526.1292 | 12.8368 | 12.6391 | 12.6241 | 12.8788 | 12.3782 | 12.7549 | 12.4432 | 12.2636 | NaN | NaN | NaN | 12.7012 | 126.155 | NaN | NaN | NaN | -15.5112 | NaN | NaN | NaN | NaN | 520.004 | NaN | 21.9422 | NaN | 16.9478
3527.1292 | 12.8385 | 12.5648 | 12.6358 | 12.9471 | 12.4493 | 12.7156 | 12.4416 | 12.2639 | NaN | NaN | NaN | 12.6884 | 125.0771 | NaN | NaN | NaN | 0.2873 | NaN | NaN | NaN | NaN | 521.2929 | NaN | 10.7565 | NaN | 15.5328
3528.1292 | 12.8163 | 12.5414 | 12.633 | 12.9237 | 12.4286 | 12.7108 | 12.4313 | 12.268 | NaN | NaN | NaN | 12.6923 | 130.7123 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 519.4348 | NaN | 9.3944 | NaN | 18.9051
3529.1292 | 12.8174 | 12.4886 | 12.6302 | 12.9174 | 12.4263 | 12.7076 | 12.4267 | 12.2709 | NaN | NaN | NaN | 12.6802 | 123.6645 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 520.8456 | NaN | 17.5984 | NaN | 16.5082
3530.1292 | 12.8105 | 12.4878 | 12.6309 | 12.935 | 12.4931 | 12.6973 | 12.4271 | 12.275 | NaN | NaN | NaN | 12.6792 | 115.3226 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.5526 | NaN | 7.0129 | NaN | 27.3847
3531.1292 | 12.8033 | 12.5076 | 12.6321 | 12.8914 | 12.3816 | 12.7128 | 12.4364 | 12.2738 | NaN | NaN | NaN | 12.6844 | 127.6821 | NaN | NaN | NaN | -11.6459 | NaN | NaN | NaN | NaN | 520.4825 | NaN | 11.2381 | NaN | 24.8734
3532.1292 | 12.8534 | 12.5162 | 12.6392 | 12.9231 | 12.4446 | 12.7085 | 12.4287 | 12.2756 | NaN | NaN | NaN | 12.6596 | 118.4126 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 516.8949 | NaN | 12.3889 | NaN | 19.031
3533.1292 | 12.7839 | 12.5027 | 12.6389 | 12.9247 | 12.4761 | 12.7125 | 12.4389 | 12.2734 | NaN | NaN | NaN | 12.6765 | 126.9775 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 520.2234 | NaN | 16.2106 | NaN | 22.0258
3534.1292 | 12.839 | 12.4858 | 12.6387 | 12.8985 | 12.4658 | 12.6961 | 12.4271 | 12.2728 | NaN | NaN | NaN | 12.6574 | 126.0501 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 519.1751 | NaN | 8.3063 | NaN | 14.4363
3535.1292 | 12.7956 | 12.4937 | 12.638 | 12.981 | 12.4792 | 12.6936 | 12.433 | 12.278 | NaN | NaN | NaN | 12.6696 | 121.1764 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 519.217 | NaN | 22.5855 | NaN | 21.8346
3536.1292 | 12.7922 | 12.4963 | 12.6406 | 12.9001 | 12.4742 | 12.7077 | 12.4366 | 12.2751 | NaN | NaN | NaN | 12.6739 | 123.9738 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 522.6453 | NaN | 12.9729 | NaN | 18.647
3537.1292 | 12.8077 | 12.518 | 12.6453 | 12.9254 | 12.498 | 12.7125 | 12.4423 | 12.2784 | NaN | NaN | NaN | 12.6712 | 124.3044 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 524.0259 | NaN | 15.0971 | NaN | 23.4082
3538.1292 | 12.8395 | 12.4789 | 12.6456 | 12.922 | 12.4677 | 12.6967 | 12.4263 | 12.2756 | NaN | NaN | NaN | 12.7543 | 124.3196 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 521.7836 | NaN | 11.1186 | NaN | 21.8145
3539.1292 | 12.9027 | 12.5161 | 12.6485 | 12.9497 | 12.3568 | 12.7299 | 12.4349 | 12.2825 | NaN | NaN | NaN | 12.7641 | 126.4254 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 525.0866 | NaN | 38.9651 | NaN | 27.2057
3540.1292 | 12.8087 | 12.514 | 12.6518 | 12.912 | 12.4658 | 12.7072 | 12.4399 | 12.2756 | NaN | NaN | NaN | 12.7058 | 126.725 | NaN | NaN | NaN | -0.6984 | NaN | NaN | NaN | NaN | 523.1178 | NaN | 20.0487 | NaN | 22.1617
3541.1292 | 12.7984 | 12.4791 | 12.6446 | 12.8955 | 12.4705 | 12.6862 | 12.4239 | 12.2853 | NaN | NaN | NaN | 12.701 | 121.4772 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 522.1044 | NaN | 7.6445 | NaN | 22.1917
3542.1292 | 12.8155 | 12.4848 | 12.6517 | 12.9511 | 12.4865 | 12.6826 | 12.4279 | 12.2832 | NaN | NaN | NaN | 12.6695 | 128.3197 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 521.6175 | NaN | 29.7827 | NaN | 22.5677
3543.1292 | 12.8276 | 12.4947 | 12.6521 | 12.9388 | 12.4019 | 12.6934 | 12.4356 | 12.2866 | NaN | NaN | NaN | 12.6861 | 117.4347 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 523.3317 | NaN | 23.6137 | NaN | 23.9661
3544.1292 | 12.8328 | 12.4787 | 12.6566 | 12.9392 | 12.489 | 12.6901 | 12.4285 | 12.2897 | NaN | NaN | NaN | 12.6985 | 124.2164 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 523.1646 | NaN | 13.7685 | NaN | 26.7205
3545.1292 | 12.8375 | 12.5446 | 12.657 | 12.9687 | 12.3836 | 12.7303 | 12.4293 | 12.2865 | NaN | NaN | NaN | 12.7244 | 122.8801 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 525.1141 | NaN | 33.2208 | NaN | 24.6822
3546.1292 | 12.8091 | 12.4989 | 12.6613 | 12.9466 | 12.4839 | 12.6876 | 12.4327 | 12.2856 | NaN | NaN | NaN | 12.7915 | 114.9094 | NaN | NaN | NaN | 1.141 | NaN | NaN | NaN | NaN | 520.9064 | NaN | 11.8002 | NaN | 13.522
3547.1292 | 12.8097 | 12.4787 | 12.6586 | 12.9715 | 12.4585 | 12.6839 | 12.4312 | 12.2847 | NaN | NaN | NaN | 12.725 | 112.262 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 519.0914 | NaN | 10.4384 | NaN | 26.7055
3548.1292 | 12.8498 | 12.5028 | 12.6578 | 12.9455 | 12.5083 | 12.6915 | 12.4361 | 12.2756 | NaN | NaN | NaN | 12.7307 | 115.4343 | NaN | NaN | NaN | 2.706 | NaN | NaN | NaN | NaN | 519.0434 | NaN | 42.7313 | NaN | 21.0596
3549.1292 | 12.8923 | 12.4766 | 12.6591 | 12.9343 | 12.5179 | 12.6737 | 12.4259 | 12.2876 | NaN | NaN | NaN | 12.7196 | 116.9318 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 521.8137 | NaN | 38.2217 | NaN | 23.181
3550.1292 | 12.8585 | 12.5017 | 12.661 | 12.8814 | 12.4758 | 12.6974 | 12.4353 | 12.2784 | NaN | NaN | NaN | 12.747 | 122.1491 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 524.5165 | NaN | 21.3291 | NaN | 21.2503
3551.1292 | 12.8135 | 12.4978 | 12.6547 | 12.9242 | 12.4756 | 12.7068 | 12.4263 | 12.2825 | NaN | NaN | NaN | 12.713 | 121.8459 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 522.8539 | NaN | 12.0301 | NaN | 19.5293
3552.1292 | 12.824 | 12.4828 | 12.6554 | 12.8949 | 12.4659 | 12.6992 | 12.4245 | 12.2812 | NaN | NaN | NaN | 12.7422 | 124.4427 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 524.5108 | NaN | 9.9226 | NaN | 21.0051
3553.1292 | 12.818 | 12.5111 | 12.6578 | 12.9297 | 12.4534 | 12.7113 | 12.4278 | 12.2814 | NaN | NaN | NaN | 12.7083 | 127.9322 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 522.0009 | NaN | 20.6876 | NaN | 22.9701
3554.1292 | 12.8184 | 12.5301 | 12.6576 | 12.9169 | 12.4127 | 12.7293 | 12.4326 | 12.2805 | NaN | NaN | NaN | 12.7522 | 129.4561 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 521.4756 | NaN | 40.8978 | NaN | 21.0623
3555.1292 | 12.8162 | 12.4671 | 12.6562 | 12.9735 | 12.4189 | 12.6907 | 12.4195 | 12.28 | NaN | NaN | NaN | 12.7389 | 130.175 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 523.1143 | NaN | 13.3866 | NaN | 24.0126
3556.1292 | 12.864 | 12.4922 | 12.6534 | 12.9513 | 12.4698 | 12.6941 | 12.4351 | 12.2715 | NaN | NaN | NaN | 12.7327 | 126.5623 | NaN | NaN | NaN | 3.3601 | NaN | NaN | NaN | NaN | 521.4468 | NaN | 8.1424 | NaN | 27.6508
3557.1292 | 12.846 | 12.4947 | 12.66 | 12.9159 | 12.442 | 12.7035 | 12.425 | 12.2783 | NaN | NaN | NaN | 12.7505 | 118.1149 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 523.485 | NaN | 16.7451 | NaN | 22.6187
3558.1292 | 12.8488 | 12.494 | 12.6583 | 12.9209 | 12.4196 | 12.6901 | 12.4276 | 12.268 | NaN | NaN | NaN | 12.7286 | 116.7792 | NaN | NaN | NaN | -17.0466 | NaN | NaN | NaN | NaN | 526.9057 | NaN | 25.909 | NaN | 27.9522
3559.1292 | 12.8311 | 12.4946 | 12.6615 | 12.9182 | 12.4839 | 12.69 | 12.4329 | 12.276 | NaN | NaN | NaN | 12.7163 | 125.9405 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 524.4112 | NaN | 43.9805 | NaN | 22.5467
3560.1292 | 12.8164 | 12.5224 | 12.659 | 12.8978 | 12.505 | 12.693 | 12.4342 | 12.2745 | NaN | NaN | NaN | 12.7228 | 123.5412 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 521.7877 | NaN | 7.276 | NaN | 22.3031
3561.1292 | 12.8359 | 12.4942 | 12.6535 | 12.9142 | 12.4811 | 12.6708 | 12.4149 | 12.2749 | NaN | NaN | NaN | 12.7491 | 122.9228 | NaN | NaN | NaN | -7.3157 | NaN | NaN | NaN | NaN | 526.3432 | NaN | 27.0545 | NaN | 19.0714
3562.1292 | 12.8279 | 12.5399 | 12.6601 | 12.8697 | 12.4979 | 12.6971 | 12.4365 | 12.2681 | NaN | NaN | NaN | 12.7103 | 114.6372 | NaN | NaN | NaN | -11.1209 | NaN | NaN | NaN | NaN | 528.0668 | NaN | 11.3637 | NaN | 29.1454
3563.1292 | 12.8376 | 12.5245 | 12.6585 | 12.8992 | 12.4942 | 12.6875 | 12.4299 | 12.267 | NaN | NaN | NaN | 12.7111 | 126.9005 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 528.2662 | NaN | 43.6865 | NaN | 13.112
3564.1292 | 12.8199 | 12.5266 | 12.6518 | 12.8631 | 12.4942 | 12.6864 | 12.4282 | 12.2677 | NaN | NaN | NaN | 12.7228 | 137.1761 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 525.9783 | NaN | 13.3316 | NaN | 18.8415
3565.1292 | 12.8263 | 12.4813 | 12.6528 | 12.9705 | 12.4844 | 12.675 | 12.4189 | 12.2694 | NaN | NaN | NaN | 12.7576 | 119.5901 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 523.6059 | NaN | 20.6835 | NaN | 10.1948
3566.1292 | 12.8374 | 12.4918 | 12.6545 | 12.884 | 12.5021 | 12.6696 | 12.4154 | 12.2697 | NaN | NaN | NaN | 12.7169 | 119.6583 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 522.5266 | NaN | 7.2231 | NaN | 22.698
3567.1292 | 12.8279 | 12.5986 | 12.6522 | 12.9203 | 12.4457 | 12.7234 | 12.4427 | 12.2676 | NaN | NaN | NaN | 12.7237 | 125.6606 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 523.3979 | NaN | 10.2218 | NaN | 18.4607
3568.1292 | 12.8181 | 12.5765 | 12.6495 | 12.8871 | 12.4683 | 12.7013 | 12.4345 | 12.2678 | NaN | NaN | NaN | 12.7252 | 129.6327 | NaN | NaN | NaN | -16.0878 | NaN | NaN | NaN | NaN | 521.7908 | NaN | 25.0508 | NaN | 24.7213
3569.1292 | 12.8006 | 12.5204 | 12.6392 | 12.9085 | 12.4859 | 12.6917 | 12.4275 | 12.2708 | NaN | NaN | NaN | 12.7149 | 116.5732 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 520.6483 | NaN | 29.2514 | NaN | 18.6715
3570.1292 | 12.8379 | 12.5181 | 12.6442 | 12.8947 | 12.4432 | 12.6868 | 12.4254 | 12.2671 | NaN | NaN | NaN | 12.6945 | 126.9003 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 524.5428 | NaN | 11.6108 | NaN | 23.8208
3571.1292 | 12.8354 | 12.5266 | 12.6446 | 12.8944 | 12.3856 | 12.6836 | 12.4156 | 12.2665 | NaN | NaN | NaN | 12.7053 | 132.8141 | NaN | NaN | NaN | -13.3003 | NaN | NaN | NaN | NaN | 522.3632 | NaN | 9.7975 | NaN | 23.8964
3572.1292 | 12.8345 | 12.4613 | 12.6385 | 12.8661 | 12.4248 | 12.6617 | 12.4175 | 12.2702 | NaN | NaN | NaN | 12.6873 | 123.5826 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 522.7329 | NaN | 18.0148 | NaN | 23.6659
3573.1292 | 12.8209 | 12.457 | 12.6378 | 12.9431 | 12.4955 | 12.6422 | 12.4059 | 12.2676 | NaN | NaN | NaN | 12.7031 | 119.6737 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 522.0559 | NaN | 8.9301 | NaN | 24.1636
3574.1292 | 12.8268 | 12.4521 | 12.6301 | 12.8979 | 12.4691 | 12.6611 | 12.4117 | 12.2703 | NaN | NaN | NaN | 12.7354 | 130.0436 | NaN | NaN | NaN | -11.9081 | NaN | NaN | NaN | NaN | 522.6091 | NaN | 29.3657 | NaN | 22.8527
3575.1292 | 12.8249 | 12.4674 | 12.6305 | 12.8753 | 12.435 | 12.6411 | 12.411 | 12.2703 | NaN | NaN | NaN | 12.7044 | 117.873 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 523.5467 | NaN | 14.4376 | NaN | 28.9666
3576.1292 | 12.8059 | 12.4661 | 12.624 | 12.885 | 12.4444 | 12.6577 | 12.4195 | 12.2724 | NaN | NaN | NaN | 12.6928 | 120.7357 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 524.337 | NaN | 17.2638 | NaN | 22.2149
3577.1292 | 12.8222 | 12.4979 | 12.6255 | 12.8776 | 12.4054 | 12.674 | 12.425 | 12.2724 | NaN | NaN | NaN | 12.6996 | 118.0478 | NaN | NaN | NaN | 5.835 | NaN | NaN | NaN | NaN | 519.1983 | NaN | 13.3439 | NaN | 23.3422
3578.1292 | 12.8202 | 12.6447 | 12.6304 | 12.9207 | 12.4647 | 12.7142 | 12.4746 | 12.2761 | NaN | NaN | NaN | 12.7603 | 122.7694 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 523.6481 | NaN | 27.1252 | NaN | 21.5047
3579.1292 | 12.8278 | 12.5102 | 12.6237 | 12.8906 | 12.4336 | 12.6605 | 12.4316 | 12.2764 | NaN | NaN | NaN | 12.7111 | 128.7454 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 523.0452 | NaN | 15.4444 | NaN | 14.4745
3580.1292 | 12.8259 | 12.5669 | 12.6289 | 12.8727 | 12.4883 | 12.6667 | 12.4459 | 12.2828 | NaN | NaN | NaN | 12.6818 | 114.9083 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 523.1892 | NaN | 10.4952 | NaN | 19.1806
3581.1292 | 12.8217 | 12.4759 | 12.6257 | 12.9425 | 12.376 | 12.6603 | 12.4319 | 12.276 | NaN | NaN | NaN | 12.7076 | 121.4061 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 522.9769 | NaN | 14.9595 | NaN | 17.0277
3582.1292 | 12.8234 | 12.4747 | 12.6321 | 12.8525 | 12.4189 | 12.6541 | 12.4162 | 12.2738 | NaN | NaN | NaN | 12.7324 | 121.1513 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 524.6327 | NaN | 10.4048 | NaN | 19.6319
3583.1292 | 12.8367 | 12.5029 | 12.6316 | 12.9002 | 12.4296 | 12.6804 | 12.4288 | 12.2759 | NaN | NaN | NaN | 12.6909 | 125.4845 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 523.9902 | NaN | 37.1496 | NaN | 22.9603
3584.1292 | 12.819 | 12.4994 | 12.6385 | 12.8749 | 12.4751 | 12.6717 | 12.4356 | 12.2785 | NaN | NaN | NaN | 12.7068 | 124.464 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 523.3046 | NaN | 8.7072 | NaN | 20.7989
3585.1292 | 12.8399 | 12.4648 | 12.6336 | 12.9075 | 12.445 | 12.6516 | 12.4213 | 12.2763 | NaN | NaN | NaN | 12.6881 | 121.0531 | NaN | NaN | NaN | -15.436 | NaN | NaN | NaN | NaN | 518.6666 | NaN | 46.5678 | NaN | 24.063
3586.1292 | 12.8451 | 12.4822 | 12.6374 | 12.9008 | 12.4199 | 12.663 | 12.4319 | 12.2789 | NaN | NaN | NaN | 12.7069 | 127.3704 | NaN | NaN | NaN | 1.0403 | NaN | NaN | NaN | NaN | 518.2429 | NaN | 23.2208 | NaN | 24.9973
3587.1292 | 12.8504 | 12.5061 | 12.6332 | 12.9898 | 12.3632 | 12.6888 | 12.4356 | 12.2763 | NaN | NaN | NaN | 12.7099 | 123.351 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 523.2073 | NaN | 20.3443 | NaN | 17.6067
3588.1292 | 12.8608 | 12.4912 | 12.6307 | 12.9298 | 12.4736 | 12.6541 | 12.4262 | 12.2755 | NaN | NaN | NaN | 12.7284 | 117.2901 | NaN | NaN | NaN | -17.5059 | NaN | NaN | NaN | NaN | 517.5163 | NaN | 9.7595 | NaN | 29.2115
3589.1292 | 12.8594 | 12.4403 | 12.6259 | 12.9128 | 12.4652 | 12.6517 | 12.4202 | 12.2743 | NaN | NaN | NaN | 12.7835 | 117.7545 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 519.5109 | NaN | 22.7805 | NaN | 19.4593
3590.1292 | 12.8795 | 12.4398 | 12.636 | 12.9139 | 12.4164 | 12.6616 | 12.4294 | 12.2701 | NaN | NaN | NaN | 12.7347 | 117.0281 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 519.5466 | NaN | 19.2513 | NaN | 21.6638
3591.1292 | 12.8577 | 12.4719 | 12.6205 | 12.9158 | 12.4585 | 12.6718 | 12.4298 | 12.2745 | NaN | NaN | NaN | 12.7227 | 131.4503 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.7003 | NaN | 22.3887 | NaN | 22.3612
3592.1292 | 12.8643 | 12.5161 | 12.616 | 12.9013 | 12.4472 | 12.681 | 12.4401 | 12.2727 | NaN | NaN | NaN | 12.7175 | 127.5113 | NaN | NaN | NaN | -4.8749 | NaN | NaN | NaN | NaN | 521.1353 | NaN | 26.111 | NaN | 26.42
3593.1292 | 12.9995 | 12.4285 | 12.6231 | 12.922 | 12.4125 | 12.6497 | 12.4255 | 12.2746 | NaN | NaN | NaN | 12.7237 | 125.7761 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 521.9162 | NaN | 17.7546 | NaN | 22.1787
3594.1292 | 12.8648 | 12.5176 | 12.6149 | 12.9195 | 12.4878 | 12.687 | 12.4672 | 12.2754 | NaN | NaN | NaN | 12.7128 | 129.1062 | NaN | NaN | NaN | -18.6584 | NaN | NaN | NaN | NaN | 521.7399 | NaN | 6.4949 | NaN | 24.5753
3595.1292 | 12.8415 | 12.4769 | 12.6197 | 12.9286 | 12.4919 | 12.6684 | 12.4395 | 12.275 | NaN | NaN | NaN | 12.7009 | 124.8157 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 523.1609 | NaN | 25.3499 | NaN | 19.6402
3596.1292 | 12.8417 | 12.4788 | 12.6235 | 12.9234 | 12.4459 | 12.6766 | 12.4379 | 12.2764 | NaN | NaN | NaN | 12.6967 | 122.5304 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 521.1064 | NaN | 20.4436 | NaN | 26.2118
3597.1292 | 12.8773 | 12.4938 | 12.6255 | 12.895 | 12.4013 | 12.6959 | 12.4429 | 12.2829 | NaN | NaN | NaN | 12.726 | 117.3318 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 517.9065 | NaN | 27.6279 | NaN | 19.5123
3598.1292 | 12.8695 | 12.477 | 12.6294 | 12.8686 | 12.4746 | 12.68 | 12.4363 | 12.2804 | NaN | NaN | NaN | 12.7104 | 121.6143 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 519.8841 | NaN | 6.1431 | NaN | 17.6845
3599.1292 | 12.8767 | 12.4329 | 12.6271 | 12.9417 | 12.4301 | 12.6486 | 12.4211 | 12.2823 | NaN | NaN | NaN | 12.7197 | 116.7971 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.1927 | NaN | 24.23 | NaN | 20.784
3600.1292 | 12.8741 | 12.4189 | 12.6299 | 12.9474 | 12.4599 | 12.6426 | 12.4171 | 12.2876 | NaN | NaN | NaN | 12.7061 | 117.6664 | NaN | NaN | NaN | -13.0993 | NaN | NaN | NaN | NaN | 522.9193 | NaN | 9.2597 | NaN | 23.6983
3601.1292 | 12.8642 | 12.5 | 12.6297 | 12.9176 | 12.495 | 12.6956 | 12.4453 | 12.2726 | NaN | NaN | NaN | 12.7205 | 132.0433 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 519.064 | NaN | 9.9678 | NaN | 26.4746
3602.1292 | 12.8761 | 12.4368 | 12.6254 | 12.9055 | 12.449 | 12.6598 | 12.4126 | 12.28 | NaN | NaN | NaN | 12.7169 | 128.647 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 520.671 | NaN | 30.0197 | NaN | 19.9
3603.1292 | 12.8832 | 12.4821 | 12.6235 | 12.9353 | 12.4855 | 12.6739 | 12.434 | 12.2774 | NaN | NaN | NaN | 12.7183 | 119.2374 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 519.9066 | NaN | 34.4407 | NaN | 20.7524
3604.1292 | 12.8726 | 12.4396 | 12.6289 | 12.9125 | 12.4405 | 12.6636 | 12.4201 | 12.2747 | NaN | NaN | NaN | 12.707 | 127.5695 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 522.2485 | NaN | 7.8937 | NaN | 20.6153
3605.1292 | 12.8825 | 12.5217 | 12.6276 | 12.9262 | 12.4344 | 12.7085 | 12.4422 | 12.2831 | NaN | NaN | NaN | 12.7012 | 128.7011 | NaN | NaN | NaN | -10.0052 | NaN | NaN | NaN | NaN | 521.129 | NaN | 20.1719 | NaN | 20.4432
3606.1292 | 12.8656 | 12.511 | 12.635 | 12.9551 | 12.365 | 12.7167 | 12.4367 | 12.2829 | NaN | NaN | NaN | 12.7439 | 125.3061 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 520.0492 | NaN | 7.2354 | NaN | 20.5038
3607.1292 | 12.8567 | 12.4217 | 12.6399 | 12.9629 | 12.4071 | 12.6767 | 12.4192 | 12.2773 | NaN | NaN | NaN | 12.755 | 121.2883 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 522.2118 | NaN | 29.9545 | NaN | 19.2962
3608.1292 | 12.8751 | 12.5131 | 12.6297 | 12.9405 | 12.484 | 12.7178 | 12.4459 | 12.2802 | NaN | NaN | NaN | 12.7372 | 127.0924 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.4011 | NaN | 8.8021 | NaN | 24.3458
3609.1292 | 12.8814 | 12.5027 | 12.6286 | 12.9585 | 12.4252 | 12.7212 | 12.4269 | 12.2922 | NaN | NaN | NaN | 12.7289 | 118.3665 | NaN | NaN | NaN | 2.1212 | NaN | NaN | NaN | NaN | 516.3046 | NaN | 14.8945 | NaN | 21.5181
3610.1292 | 12.859 | 12.4386 | 12.627 | 12.9361 | 12.4598 | 12.6797 | 12.4232 | 12.2748 | NaN | NaN | NaN | 12.7325 | 114.3443 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 521.3179 | NaN | 11.401 | NaN | 25.3372
3611.1292 | 12.868 | 12.4688 | 12.6295 | 12.9308 | 12.4955 | 12.6816 | 12.4269 | 12.2781 | NaN | NaN | NaN | 12.7136 | 117.6956 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 520.6067 | NaN | 14.8797 | NaN | 25.8234
3612.1292 | 12.8543 | 12.5171 | 12.6232 | 12.9445 | 12.4613 | 12.7013 | 12.4335 | 12.278 | NaN | NaN | NaN | 12.7378 | 120.3952 | NaN | NaN | NaN | -16.0668 | NaN | NaN | NaN | NaN | 521.1024 | NaN | 8.5702 | NaN | 16.5807
3613.1292 | 12.8695 | 12.4763 | 12.6263 | 12.9511 | 12.4543 | 12.7012 | 12.4308 | 12.2746 | NaN | NaN | NaN | 12.7314 | 122.4683 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 519.6004 | NaN | 46.5442 | NaN | 25.7692
3614.1292 | 12.8567 | 12.5123 | 12.622 | 12.9529 | 12.4 | 12.717 | 12.4466 | 12.2823 | NaN | NaN | NaN | 12.7228 | 119.683 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 519.9579 | NaN | 24.5349 | NaN | 18.2403
3615.1292 | 12.8496 | 12.4881 | 12.6316 | 12.9257 | 12.3704 | 12.7183 | 12.4393 | 12.285 | NaN | NaN | NaN | 12.7632 | 133.93 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 520.4818 | NaN | 8.5707 | NaN | 25.0752
3616.1292 | 12.8635 | 12.4672 | 12.6324 | 12.9466 | 12.4581 | 12.6921 | 12.4339 | 12.2848 | NaN | NaN | NaN | 12.7532 | 127.4569 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 521.1485 | NaN | 47.6658 | NaN | 18.9134
3617.1292 | 12.8699 | 12.4344 | 12.6343 | 12.9243 | 12.4528 | 12.7059 | 12.4386 | 12.2826 | NaN | NaN | NaN | 12.7539 | 114.3345 | NaN | NaN | NaN | -19.1909 | NaN | NaN | NaN | NaN | 521.8278 | NaN | 8.1736 | NaN | 27.5216
3618.1292 | 12.8578 | 12.4359 | 12.6403 | 12.9578 | 12.4923 | 12.6867 | 12.4267 | 12.2782 | NaN | NaN | NaN | 12.7163 | 128.4801 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.7746 | NaN | 7.9893 | NaN | 21.4904
3619.1292 | 12.8679 | 12.4582 | 12.6416 | 12.9362 | 12.4976 | 12.708 | 12.4373 | 12.2866 | NaN | NaN | NaN | 12.7409 | 123.0798 | NaN | NaN | NaN | 0.5111 | NaN | NaN | NaN | NaN | 519.1355 | NaN | 10.3629 | NaN | 24.3838
3620.1292 | 12.8719 | 12.4448 | 12.6384 | 12.9344 | 12.4448 | 12.7077 | 12.4382 | 12.2865 | NaN | NaN | NaN | 12.7072 | 128.9501 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 517.075 | NaN | 7.0278 | NaN | 30.1578
3621.1292 | 12.8694 | 12.4909 | 12.6392 | 12.9107 | 12.4036 | 12.7347 | 12.4328 | 12.2943 | NaN | NaN | NaN | 12.7656 | 116.8663 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.3061 | NaN | 26.9354 | NaN | 20.5084
3622.1292 | 12.8693 | 12.4272 | 12.6449 | 12.961 | 12.4809 | 12.6951 | 12.4235 | 12.2852 | NaN | NaN | NaN | 12.7438 | 115.8535 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 516.0805 | NaN | 22.6052 | NaN | 25.2983
3623.1292 | 12.8689 | 12.4649 | 12.6418 | 12.93 | 12.447 | 12.7221 | 12.4211 | 12.2895 | NaN | NaN | NaN | 12.7107 | 119.0813 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 515.2635 | NaN | 12.7673 | NaN | 17.1113
3624.1292 | 12.8686 | 12.5784 | 12.6454 | 12.9691 | 12.399 | 12.7481 | 12.4371 | 12.284 | NaN | NaN | NaN | 12.7498 | 123.3363 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.6093 | NaN | 6.9887 | NaN | 20.8698
3625.1292 | 12.8772 | 12.4578 | 12.6512 | 12.9353 | 12.4769 | 12.7259 | 12.4285 | 12.2898 | NaN | NaN | NaN | 12.735 | 127.0158 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 516.0449 | NaN | 26.9944 | NaN | 27.6017
3626.1292 | 12.8879 | 12.4782 | 12.6475 | 12.9139 | 12.444 | 12.7442 | 12.4332 | 12.283 | NaN | NaN | NaN | 12.7156 | 124.6176 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 520.7439 | NaN | 10.7828 | NaN | 23.4016
3627.1292 | 12.8785 | 12.4535 | 12.6505 | 12.9396 | 12.4599 | 12.7393 | 12.4288 | 12.2821 | NaN | NaN | NaN | 12.8238 | 132.2456 | NaN | NaN | NaN | -15.0445 | NaN | NaN | NaN | NaN | 517.1839 | NaN | 39.5434 | NaN | 23.1212
3628.1292 | 12.8777 | 12.4491 | 12.6554 | 12.9824 | 12.472 | 12.7318 | 12.4201 | 12.2911 | NaN | NaN | NaN | 12.7242 | 119.7782 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 517.7385 | NaN | 43.2135 | NaN | 16.8947
3629.1292 | 12.8267 | 12.4392 | 12.6498 | 12.9344 | 12.4605 | 12.715 | 12.4227 | 12.2858 | NaN | NaN | NaN | 12.7196 | 112.3694 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.1425 | NaN | 38.4518 | NaN | 25.0259
3630.1292 | 12.8655 | 12.4338 | 12.6537 | 12.9764 | 12.4956 | 12.7196 | 12.4325 | 12.2854 | NaN | NaN | NaN | 12.7342 | 120.0458 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 514.6263 | NaN | 29.6807 | NaN | 23.4998
3631.1292 | 12.8978 | 12.5141 | 12.6574 | 12.9594 | 12.4688 | 12.7605 | 12.4546 | 12.2843 | NaN | NaN | NaN | 12.7102 | 134.1519 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 514.8723 | NaN | 23.649 | NaN | 20.9914
3632.1292 | 12.943 | 12.5058 | 12.6601 | 12.9731 | 12.5044 | 12.7353 | 12.4516 | 12.2842 | NaN | NaN | NaN | 12.7113 | 112.4491 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 513.9489 | NaN | 7.759 | NaN | 24.5104
3633.1292 | 12.8798 | 12.4837 | 12.658 | 12.959 | 12.3978 | 12.7583 | 12.4425 | 12.2914 | NaN | NaN | NaN | 12.771 | 132.0051 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 513.7279 | NaN | 44.5788 | NaN | 19.0498
3634.1292 | 12.8441 | 12.4454 | 12.6631 | 12.9448 | 12.4623 | 12.7116 | 12.4326 | 12.2926 | NaN | NaN | NaN | 12.8028 | 122.3331 | NaN | NaN | NaN | -15.3371 | NaN | NaN | NaN | NaN | 514.7203 | NaN | 6.4457 | NaN | 21.6675
3635.1292 | 12.8457 | 12.4484 | 12.6609 | 12.9335 | 12.4722 | 12.706 | 12.433 | 12.2945 | NaN | NaN | NaN | 12.7698 | 123.804 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.204 | NaN | 37.1763 | NaN | 21.511
3636.1292 | 12.8618 | 12.4909 | 12.6638 | 12.9057 | 12.4012 | 12.7317 | 12.4393 | 12.2955 | NaN | NaN | NaN | 12.7429 | 122.3109 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.6169 | NaN | 18.8441 | NaN | 26.4005
3637.1292 | 12.8684 | 12.4844 | 12.6643 | 12.9271 | 12.4647 | 12.7197 | 12.4464 | 12.3071 | NaN | NaN | NaN | 12.7278 | 125.4898 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.2695 | NaN | 10.8445 | NaN | 25.3715
3638.1292 | 12.8491 | 12.4669 | 12.6674 | 12.9382 | 12.485 | 12.6935 | 12.44 | 12.3058 | NaN | NaN | NaN | 12.7544 | 128.5112 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 516.6287 | NaN | 8.4954 | NaN | 26.7194
3639.1292 | 12.8711 | 12.4698 | 12.6579 | 12.9909 | 12.4958 | 12.7043 | 12.4568 | 12.3101 | NaN | NaN | NaN | 12.6962 | 122.6473 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 516.0405 | NaN | 10.6788 | NaN | 21.2688
3640.1292 | 12.8521 | 12.4798 | 12.662 | 12.969 | 12.4577 | 12.7132 | 12.4504 | 12.3071 | NaN | NaN | NaN | 12.749 | 135.2526 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 515.5082 | NaN | 7.5297 | NaN | 20.2906
3641.1292 | 12.8505 | 12.4928 | 12.6628 | 12.96 | 12.4234 | 12.7173 | 12.4509 | 12.3131 | NaN | NaN | NaN | 12.7317 | 124.2363 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.9277 | NaN | 19.8905 | NaN | 25.2072
3642.1292 | 12.8626 | 12.4794 | 12.6652 | 12.9545 | 12.4802 | 12.6956 | 12.455 | 12.3236 | NaN | NaN | NaN | 12.7116 | 121.481 | NaN | NaN | NaN | -10.0262 | NaN | NaN | NaN | NaN | 516.8938 | NaN | 9.6509 | NaN | 24.0092
3643.1292 | 12.8672 | 12.4804 | 12.6678 | 12.9369 | 12.4594 | 12.6934 | 12.4552 | 12.3179 | NaN | NaN | NaN | 12.7801 | 117.8477 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 520.305 | NaN | 8.8633 | NaN | 20.2769
3644.1292 | 12.8675 | 12.5139 | 12.6686 | 12.9763 | 12.3965 | 12.7052 | 12.4565 | 12.3184 | NaN | NaN | NaN | 12.7308 | 119.4206 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 517.8973 | NaN | 6.7151 | NaN | 20.3449
3645.1292 | 12.8759 | 12.5058 | 12.6764 | 12.9647 | 12.4956 | 12.7022 | 12.4547 | 12.3212 | NaN | NaN | NaN | 12.7698 | 111.8565 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 516.3811 | NaN | 25.0807 | NaN | 26.8794
3646.1292 | 12.8647 | 12.5213 | 12.6811 | 13.0074 | 12.4392 | 12.7098 | 12.4594 | 12.3254 | NaN | NaN | NaN | 12.7862 | 110.3077 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.2716 | NaN | 45.3507 | NaN | 18.3417
3647.1292 | 12.857 | 12.5397 | 12.682 | 12.9315 | 12.4521 | 12.7155 | 12.4773 | 12.3221 | NaN | NaN | NaN | 12.7351 | 126.7372 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 519.3516 | NaN | 7.5634 | NaN | 29.9293
3648.1292 | 12.864 | 12.503 | 12.678 | 12.9831 | 12.5202 | 12.6995 | 12.4625 | 12.3233 | NaN | NaN | NaN | 12.7375 | 130.8808 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.7793 | NaN | 16.0129 | NaN | 19.2242
3649.1292 | 12.8804 | 12.5017 | 12.6844 | 12.9828 | 12.4786 | 12.6962 | 12.4613 | 12.3235 | NaN | NaN | NaN | 12.7136 | 115.8049 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.1067 | NaN | 9.4044 | NaN | 23.8363
3650.1292 | 12.9308 | 12.6212 | 12.6837 | 13.026 | 12.4652 | 12.7052 | 12.4957 | 12.3178 | NaN | NaN | NaN | 12.7196 | 133.6549 | NaN | NaN | NaN | -2.8255 | NaN | NaN | NaN | NaN | 519.1107 | NaN | 7.2821 | NaN | 21.8741
3651.1292 | 12.8492 | 12.4992 | 12.6819 | 12.9805 | 12.5233 | 12.6769 | 12.4697 | 12.3298 | NaN | NaN | NaN | 12.7452 | 126.0341 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 519.0158 | NaN | 12.5983 | NaN | 26.2747
3652.1292 | 12.8405 | 12.5086 | 12.6786 | 12.9398 | 12.4819 | 12.6934 | 12.4662 | 12.3275 | NaN | NaN | NaN | 12.7758 | 124.2733 | NaN | NaN | NaN | -12.2392 | NaN | NaN | NaN | NaN | 519.267 | NaN | 27.5376 | NaN | 21.4071
3653.1292 | 12.8467 | 12.5412 | 12.6841 | 12.9119 | 12.4093 | 12.7025 | 12.4633 | 12.327 | NaN | NaN | NaN | 12.7524 | 127.787 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.5851 | NaN | 15.0028 | NaN | 26.2646
3654.1292 | 12.8548 | 12.5107 | 12.6843 | 12.9596 | 12.5064 | 12.6789 | 12.4562 | 12.3322 | NaN | NaN | NaN | 12.7381 | 129.7289 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 519.7163 | NaN | 8.2324 | NaN | 19.5329
3655.1292 | 12.8431 | 12.5395 | 12.6812 | 12.9252 | 12.4329 | 12.7201 | 12.4607 | 12.3298 | NaN | NaN | NaN | 12.7553 | 114.8976 | NaN | NaN | NaN | 2.1474 | NaN | NaN | NaN | NaN | 516.8956 | NaN | 19.2879 | NaN | 28.4107
3656.1292 | 12.8468 | 12.5447 | 12.6842 | 12.9248 | 12.4141 | 12.6952 | 12.4699 | 12.3285 | NaN | NaN | NaN | 12.737 | 119.2533 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 515.3752 | NaN | 32.0432 | NaN | 14.8733
3657.1292 | 12.8514 | 12.5037 | 12.6756 | 12.9745 | 12.5336 | 12.6824 | 12.4609 | 12.3283 | NaN | NaN | NaN | 12.7571 | 124.1523 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 516.6191 | NaN | 6.8207 | NaN | 18.5358
3658.1292 | 12.8482 | 12.5165 | 12.6736 | 12.9544 | 12.5139 | 12.6987 | 12.4687 | 12.327 | NaN | NaN | NaN | 12.7436 | 125.4119 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 515.0449 | NaN | 31.1995 | NaN | 12.5282
3659.1292 | 12.852 | 12.5967 | 12.6775 | 12.9189 | 12.5287 | 12.7257 | 12.4739 | 12.3218 | NaN | NaN | NaN | 12.7406 | 143.0467 | NaN | NaN | NaN | 2.1166 | NaN | NaN | NaN | NaN | 517.9643 | NaN | 15.1277 | NaN | 23.425
3660.1292 | 12.8253 | 12.5347 | 12.6725 | 12.9077 | 12.476 | 12.7038 | 12.4663 | 12.3137 | NaN | NaN | NaN | 12.7122 | 120.1363 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.2571 | NaN | 8.0582 | NaN | 23.2462
3661.1292 | 12.8385 | 12.5555 | 12.6793 | 12.9226 | 12.4112 | 12.7273 | 12.4721 | 12.326 | NaN | NaN | NaN | 12.7178 | 121.2184 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 517.2271 | NaN | 42.937 | NaN | 21.0188
3662.1292 | 12.9449 | 12.535 | 12.6788 | 12.9419 | 12.5071 | 12.7115 | 12.4709 | 12.3243 | NaN | NaN | NaN | 12.7111 | 129.9819 | NaN | NaN | NaN | 0.818 | NaN | NaN | NaN | NaN | 515.7449 | NaN | 7.2154 | NaN | 25.9493
3663.1292 | 12.872 | 12.5193 | 12.6715 | 12.988 | 12.416 | 12.7262 | 12.4715 | 12.326 | NaN | NaN | NaN | 12.7396 | 128.5257 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 513.0838 | NaN | 44.6509 | NaN | 25.2079
3664.1292 | 12.8351 | 12.5266 | 12.6773 | 12.9447 | 12.4206 | 12.7148 | 12.4585 | 12.3175 | NaN | NaN | NaN | 12.7246 | 129.2679 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.6197 | NaN | 10.9645 | NaN | 27.5474
3665.1292 | 12.8385 | 12.5121 | 12.6724 | 12.9505 | 12.4694 | 12.7072 | 12.4588 | 12.3231 | NaN | NaN | NaN | 12.7455 | 115.7345 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.139 | NaN | 23.5207 | NaN | 23.2165
3666.1292 | 12.8708 | 12.5942 | 12.6728 | 12.9326 | 12.4933 | 12.7492 | 12.4676 | 12.3255 | NaN | NaN | NaN | 12.7071 | 125.1744 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 517.1652 | NaN | 6.4473 | NaN | 26.6054
3667.1292 | 12.8423 | 12.5543 | 12.6711 | 12.9647 | 12.5116 | 12.7317 | 12.473 | 12.3307 | NaN | NaN | NaN | 12.7249 | 118.2956 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 516.3221 | NaN | 21.4216 | NaN | 22.0888
3668.1292 | 12.8575 | 12.5193 | 12.6634 | 12.9365 | 12.5325 | 12.7171 | 12.4736 | 12.326 | NaN | NaN | NaN | 12.7236 | 127.5998 | NaN | NaN | NaN | 1.6527 | NaN | NaN | NaN | NaN | 515.9255 | NaN | 7.7039 | NaN | 22.2563
3669.1292 | 12.8463 | 12.5229 | 12.6603 | 12.9441 | 12.5325 | 12.7195 | 12.4711 | 12.3254 | NaN | NaN | NaN | 12.7367 | 113.6156 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 516.3523 | NaN | 7.1672 | NaN | 22.4983
3670.1292 | 12.9408 | 12.5497 | 12.6539 | 12.8975 | 12.509 | 12.7287 | 12.4723 | 12.33 | NaN | NaN | NaN | 12.7177 | 124.8287 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 517.5762 | NaN | 9.3129 | NaN | 30.2136
3671.1292 | 12.8854 | 12.5747 | 12.6546 | 12.9685 | 12.5239 | 12.7444 | 12.4861 | 12.3271 | NaN | NaN | NaN | 12.7275 | 119.9638 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 519.6003 | NaN | 12.8328 | NaN | 27.7855
3672.1292 | 12.8786 | 12.5329 | 12.6585 | 12.93 | 12.4494 | 12.7459 | 12.4722 | 12.3334 | NaN | NaN | NaN | 12.7071 | 130.0662 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 517.7087 | NaN | 10.853 | NaN | 23.8014
3673.1292 | 12.8792 | 12.5088 | 12.6538 | 12.9145 | 12.5351 | 12.7071 | 12.467 | 12.3303 | NaN | NaN | NaN | 12.7257 | 132.7364 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 517.4959 | NaN | 25.0669 | NaN | 10.7779
3674.1292 | 12.88 | 12.5488 | 12.6561 | 12.9185 | 12.4627 | 12.7423 | 12.4815 | 12.3343 | NaN | NaN | NaN | 12.7314 | 128.7238 | NaN | NaN | NaN | 6.5919 | NaN | NaN | NaN | NaN | 514.9899 | NaN | 15.7033 | NaN | 22.059
3675.1292 | 12.8774 | 12.5056 | 12.6602 | 12.9085 | 12.4928 | 12.7187 | 12.4764 | 12.3293 | NaN | NaN | NaN | 12.7366 | 126.1547 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 516.7323 | NaN | 33.9181 | NaN | 26.0414
3676.1292 | 12.881 | 12.4854 | 12.6619 | 12.9817 | 12.4298 | 12.7259 | 12.4731 | 12.331 | NaN | NaN | NaN | 12.7082 | 131.0511 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 515.3508 | NaN | 29.82 | NaN | 24.7383
3677.1292 | 12.8889 | 12.515 | 12.6571 | 12.9307 | 12.4861 | 12.7225 | 12.4729 | 12.3322 | NaN | NaN | NaN | 12.7364 | 130.5672 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 516.7378 | NaN | 7.3831 | NaN | 23.9331
3678.1292 | 12.8783 | 12.5919 | 12.668 | 12.932 | 12.414 | 12.7735 | 12.5122 | 12.3328 | NaN | NaN | NaN | 12.8079 | 122.1796 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.9828 | NaN | 7.9695 | NaN | 21.6994
3679.1292 | 12.8865 | 12.5221 | 12.6645 | 12.9519 | 12.415 | 12.7339 | 12.4829 | 12.3288 | NaN | NaN | NaN | 12.7006 | 127.0939 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 517.4202 | NaN | 7.6653 | NaN | 28.1844
3680.1292 | 12.8597 | 12.518 | 12.6704 | 12.9252 | 12.53 | 12.7086 | 12.4652 | 12.326 | NaN | NaN | NaN | 12.7187 | 112.5498 | NaN | NaN | NaN | -5.0304 | NaN | NaN | NaN | NaN | 516.4582 | NaN | 9.2319 | NaN | 21.3672
3681.1292 | 12.9675 | 12.4829 | 12.6682 | 12.9349 | 12.5142 | 12.7034 | 12.4649 | 12.32 | NaN | NaN | NaN | 12.7041 | 126.9585 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.518 | NaN | 33.9761 | NaN | 21.8335
3682.1292 | 12.8554 | 12.5235 | 12.6695 | 12.9347 | 12.4286 | 12.7268 | 12.4626 | 12.3157 | NaN | NaN | NaN | 12.7509 | 118.585 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.1428 | NaN | 8.6352 | NaN | 21.5902
3683.1292 | 12.8797 | 12.5495 | 12.6646 | 12.9292 | 12.4471 | 12.732 | 12.4685 | 12.3149 | NaN | NaN | NaN | 12.7232 | 125.1285 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 516.4324 | NaN | 6.7324 | NaN | 25.9129
3684.1292 | 12.8697 | 12.508 | 12.6649 | 12.9383 | 12.5094 | 12.7165 | 12.4702 | 12.3207 | NaN | NaN | NaN | 12.7363 | 113.9587 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 516.7805 | NaN | 22.5355 | NaN | 21.2466
3685.1292 | 12.851 | 12.5401 | 12.6648 | 12.9231 | 12.4895 | 12.7235 | 12.4608 | 12.3279 | NaN | NaN | NaN | 12.7419 | 132.6983 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 516.9469 | NaN | 18.9479 | NaN | 16.8498
3686.1292 | 12.8384 | 12.5432 | 12.6653 | 13.0307 | 12.5165 | 12.7388 | 12.4672 | 12.3272 | NaN | NaN | NaN | 12.7162 | 129.297 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 515.1911 | NaN | 8.1915 | NaN | 15.9012
3687.1292 | 12.8657 | 12.5116 | 12.66 | 12.9302 | 12.5291 | 12.7208 | 12.4738 | 12.3243 | NaN | NaN | NaN | 12.7362 | 120.2465 | NaN | NaN | NaN | -11.8351 | NaN | NaN | NaN | NaN | 517.3232 | NaN | 15.719 | NaN | 27.7218
3688.1292 | 12.8582 | 12.5291 | 12.6662 | 13.0347 | 12.4564 | 12.7283 | 12.4717 | 12.3218 | NaN | NaN | NaN | 12.7303 | 126.1984 | NaN | NaN | NaN | 3.1665 | NaN | NaN | NaN | NaN | 517.3845 | NaN | 30.8175 | NaN | 22.4535
3689.1292 | 12.8543 | 12.4759 | 12.6693 | 12.992 | 12.4095 | 12.723 | 12.4628 | 12.3246 | NaN | NaN | NaN | 12.724 | 126.6256 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 519.7127 | NaN | 9.7567 | NaN | 20.6196
3690.1292 | 12.8633 | 12.5073 | 12.6642 | 12.9631 | 12.4813 | 12.7198 | 12.4568 | 12.3224 | NaN | NaN | NaN | 12.744 | 128.3558 | NaN | NaN | NaN | -3.7305 | NaN | NaN | NaN | NaN | 517.6596 | NaN | 6.9621 | NaN | 25.0791
3691.1292 | 12.8534 | 12.458 | 12.6682 | 12.9599 | 12.4855 | 12.6875 | 12.4553 | 12.3258 | NaN | NaN | NaN | 12.7186 | 119.1576 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 516.6923 | NaN | 14.3262 | NaN | 21.8279
3692.1292 | 12.8563 | 12.4851 | 12.6746 | 12.9466 | 12.5084 | 12.7059 | 12.4611 | 12.3244 | NaN | NaN | NaN | 12.7151 | 125.9034 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 519.3216 | NaN | 9.69 | NaN | 21.3394
3693.1292 | 12.8486 | 12.4692 | 12.671 | 12.9384 | 12.5019 | 12.6939 | 12.4589 | 12.3215 | NaN | NaN | NaN | 12.736 | 120.5876 | NaN | NaN | NaN | -17.9846 | NaN | NaN | NaN | NaN | 517.0052 | NaN | 15.6857 | NaN | 23.2059
3694.1292 | 12.8496 | 12.4829 | 12.6746 | 12.9432 | 12.5168 | 12.6842 | 12.4623 | 12.3237 | NaN | NaN | NaN | 12.7482 | 111.8439 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 519.3146 | NaN | 7.2275 | NaN | 16.4012
3695.1292 | 12.8398 | 12.465 | 12.678 | 12.9458 | 12.4802 | 12.6856 | 12.4582 | 12.3237 | NaN | NaN | NaN | 12.7334 | 126.7531 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 517.8682 | NaN | 45.7575 | NaN | 22.114
3696.1292 | 13.0021 | 12.4672 | 12.6713 | 12.9282 | 12.5008 | 12.6947 | 12.4678 | 12.3225 | NaN | NaN | NaN | 12.7151 | 127.0479 | NaN | NaN | NaN | 0.9024 | NaN | NaN | NaN | NaN | 519.6113 | NaN | 7.1175 | NaN | 26.3426
3697.1292 | 12.8488 | 12.4721 | 12.6845 | 12.9782 | 12.5274 | 12.6977 | 12.4655 | 12.3222 | NaN | NaN | NaN | 12.7214 | 126.0627 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 517.9934 | NaN | 30.326 | NaN | 25.6938
3698.1292 | 12.8536 | 12.4719 | 12.677 | 12.9303 | 12.5253 | 12.7001 | 12.4691 | 12.3282 | NaN | NaN | NaN | 12.7365 | 138.0169 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 517.0292 | NaN | 31.0269 | NaN | 21.3886
3699.1292 | 12.836 | 12.4502 | 12.6767 | 12.9222 | 12.4647 | 12.6842 | 12.4663 | 12.3258 | NaN | NaN | NaN | 12.7446 | 136.6889 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 520.949 | NaN | 40.5741 | NaN | 23.9506
3700.1292 | 12.8449 | 12.435 | 12.679 | 12.959 | 12.4472 | 12.6797 | 12.4607 | 12.3305 | NaN | NaN | NaN | 12.7251 | 116.7138 | NaN | NaN | NaN | -15.6828 | NaN | NaN | NaN | NaN | 518.0482 | NaN | 8.8164 | NaN | 23.3392
3701.1292 | 12.8455 | 12.5355 | 12.6753 | 12.9346 | 12.5391 | 12.698 | 12.476 | 12.328 | NaN | NaN | NaN | 12.7379 | 135.8387 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 520.5764 | NaN | 13.786 | NaN | 27.5746
3702.1292 | 12.8449 | 12.497 | 12.6732 | 12.943 | 12.4214 | 12.7146 | 12.4623 | 12.3343 | NaN | NaN | NaN | 12.7342 | 115.4181 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 523.7483 | NaN | 6.0187 | NaN | 14.0803
3703.1292 | 12.9512 | 12.5162 | 12.6767 | 12.9367 | 12.5441 | 12.7051 | 12.471 | 12.3289 | NaN | NaN | NaN | 12.726 | 128.904 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 520.3478 | NaN | 12.0151 | NaN | 20.0523
3704.1292 | 12.8571 | 12.4753 | 12.6752 | 12.9523 | 12.5481 | 12.6656 | 12.4582 | 12.3362 | NaN | NaN | NaN | 12.7201 | 126.6126 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 521.4073 | NaN | 15.4777 | NaN | 19.0248
3705.1292 | 12.8896 | 12.5501 | 12.6748 | 12.9276 | 12.4518 | 12.7381 | 12.4648 | 12.3315 | NaN | NaN | NaN | 12.7128 | 128.2055 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 523.0277 | NaN | 41.8025 | NaN | 27.9094
3706.1292 | 12.8461 | 12.5502 | 12.6838 | 12.9421 | 12.5261 | 12.7031 | 12.4683 | 12.3328 | NaN | NaN | NaN | 12.7001 | 121.6285 | NaN | NaN | NaN | 2.115 | NaN | NaN | NaN | NaN | 518.3156 | NaN | 6.006 | NaN | 17.7653
3707.1292 | 12.8306 | 12.5441 | 12.6836 | 12.9514 | 12.4696 | 12.7158 | 12.4748 | 12.3357 | NaN | NaN | NaN | 12.6973 | 124.5509 | NaN | NaN | NaN | -11.6133 | NaN | NaN | NaN | NaN | 521.5418 | NaN | 35.9458 | NaN | 33.1452
3708.1292 | 12.8427 | 12.5926 | 12.6815 | 12.9472 | 12.5351 | 12.719 | 12.4923 | 12.3385 | NaN | NaN | NaN | 12.7365 | 136.1039 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.8112 | NaN | 16.7164 | NaN | 17.2286
3709.1292 | 12.8431 | 12.53 | 12.6848 | 12.9446 | 12.5301 | 12.6884 | 12.4681 | 12.3375 | NaN | NaN | NaN | 12.7317 | 122.8311 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 521.7749 | NaN | 28.7037 | NaN | 12.3805
3710.1292 | 12.8432 | 12.5535 | 12.6947 | 12.9396 | 12.5464 | 12.6914 | 12.4666 | 12.3359 | NaN | NaN | NaN | 12.7127 | 133.2847 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 521.5597 | NaN | 7.8188 | NaN | 14.5928
3711.1292 | 12.8457 | 12.5277 | 12.6903 | 12.9367 | 12.5577 | 12.6805 | 12.4672 | 12.3346 | NaN | NaN | NaN | 12.7278 | 133.2072 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 522.0816 | NaN | 31.6772 | NaN | 22.6493
3712.1292 | 12.8309 | 12.5298 | 12.6913 | 12.9653 | 12.464 | 12.6913 | 12.4622 | 12.3394 | NaN | NaN | NaN | 12.7171 | 128.8437 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 520.642 | NaN | 10.7399 | NaN | 13.093
3713.1292 | 12.9198 | 12.544 | 12.6859 | 13.0003 | 12.5008 | 12.6964 | 12.4761 | 12.3378 | NaN | NaN | NaN | 12.7349 | 130.0259 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 519.6965 | NaN | 8.3741 | NaN | 21.8874
3714.1292 | 12.8394 | 12.5216 | 12.6883 | 12.9149 | 12.4839 | 12.6909 | 12.4618 | 12.3364 | NaN | NaN | NaN | 12.7149 | 127.7572 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 520.1841 | NaN | 11.0166 | NaN | 26.5106
3715.1292 | 12.8499 | 12.5071 | 12.6847 | 12.95 | 12.5271 | 12.6716 | 12.4633 | 12.3431 | NaN | NaN | NaN | 12.7199 | 129.0442 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 522.6813 | NaN | 8.6261 | NaN | 23.9087
3716.1292 | 12.8574 | 12.55 | 12.6919 | 12.9056 | 12.5047 | 12.6986 | 12.4728 | 12.3346 | NaN | NaN | NaN | 12.7101 | 135.0321 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 521.7186 | NaN | 23.7499 | NaN | 19.2801
3717.1292 | 12.8684 | 12.516 | 12.6841 | 12.951 | 12.5358 | 12.6782 | 12.4605 | 12.3375 | NaN | NaN | NaN | 12.7174 | 118.5597 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 522.0837 | NaN | 28.2348 | NaN | 26.3984
3718.1292 | 12.8609 | 12.5474 | 12.701 | 12.9054 | 12.515 | 12.6919 | 12.4662 | 12.3348 | NaN | NaN | NaN | 12.7218 | 133.1813 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 523.1666 | NaN | 38.3975 | NaN | 23.855
3719.1292 | 12.8606 | 12.5272 | 12.6932 | 12.9594 | 12.5103 | 12.6741 | 12.4548 | 12.3351 | NaN | NaN | NaN | 12.6957 | 133.0784 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 526.5339 | NaN | 6.4698 | NaN | 12.7152
3720.1292 | 12.8307 | 12.5601 | 12.6914 | 12.9319 | 12.5145 | 12.6884 | 12.4738 | 12.342 | NaN | NaN | NaN | 12.6973 | 131.0321 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 527.6404 | NaN | 15.8475 | NaN | 29.8772
3721.1292 | 12.9058 | 12.5095 | 12.6957 | 12.9596 | 12.505 | 12.6621 | 12.4566 | 12.3425 | NaN | NaN | NaN | 12.6989 | 116.4244 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 526.4294 | NaN | 12.7095 | NaN | 21.6025
3722.1292 | 12.8747 | 12.5226 | 12.6931 | 12.9564 | 12.4977 | 12.6742 | 12.4511 | 12.3422 | NaN | NaN | NaN | 12.728 | 125.5707 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 524.8496 | NaN | 6.3764 | NaN | 27.3179
3723.1292 | 12.8722 | 12.5866 | 12.6982 | 12.9327 | 12.5139 | 12.6908 | 12.4706 | 12.3406 | NaN | NaN | NaN | 12.7043 | 135.3742 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 527.669 | NaN | 12.0011 | NaN | 20.7428
3724.1292 | 12.8717 | 12.515 | 12.6919 | 12.9112 | 12.5556 | 12.6705 | 12.4567 | 12.3394 | NaN | NaN | NaN | 12.708 | 117.4659 | NaN | NaN | NaN | -14.525 | NaN | NaN | NaN | NaN | 527.8241 | NaN | 18.1766 | NaN | 22.2106
3725.1292 | 12.8563 | 12.6534 | 12.6913 | 12.9117 | 12.4812 | 12.7457 | 12.503 | 12.3347 | NaN | NaN | NaN | 12.7286 | 121.2019 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 527.0947 | NaN | 9.7131 | NaN | 24.4121
3726.1292 | 12.8472 | 12.5732 | 12.6901 | 12.8864 | 12.5425 | 12.6851 | 12.4715 | 12.3351 | NaN | NaN | NaN | 12.7319 | 137.0496 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 525.8344 | NaN | 5.5053 | NaN | 27.2272
3727.1292 | 12.8304 | 12.5214 | 12.6952 | 12.8961 | 12.4927 | 12.6774 | 12.4633 | 12.3376 | NaN | NaN | NaN | 12.697 | 125.7585 | NaN | NaN | NaN | -7.5338 | NaN | NaN | NaN | NaN | 521.4224 | NaN | 20.6176 | NaN | 20.7604
3728.1292 | 12.879 | 12.4881 | 12.6942 | 12.9268 | 12.5609 | 12.658 | 12.447 | 12.3318 | NaN | NaN | NaN | 12.7026 | 127.7273 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 524.1762 | NaN | 6.279 | NaN | 23.6518
3729.1292 | 12.8549 | 12.5011 | 12.6911 | 12.9027 | 12.5376 | 12.668 | 12.4513 | 12.3319 | NaN | NaN | NaN | 12.7239 | 129.4334 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 522.5551 | NaN | 18.0827 | NaN | 28.1406
3730.1292 | 12.8715 | 12.588 | 12.6898 | 13.1014 | 12.4257 | 12.7275 | 12.4748 | 12.3331 | NaN | NaN | NaN | 12.7311 | 125.327 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 525.9035 | NaN | 20.8062 | NaN | 25.9574
3731.1292 | 12.9715 | 12.4905 | 12.6901 | 12.9062 | 12.5225 | 12.6648 | 12.4546 | 12.3356 | NaN | NaN | NaN | 12.6868 | 127.2836 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 527.3023 | NaN | 16.8862 | NaN | 27.4714
3732.1292 | 12.8446 | 12.5191 | 12.6834 | 12.9503 | 12.5313 | 12.6863 | 12.467 | 12.3275 | NaN | NaN | NaN | 12.7074 | 120.205 | NaN | NaN | NaN | -1.6414 | NaN | NaN | NaN | NaN | 526.6969 | NaN | 6.6067 | NaN | 19.7185
3733.1292 | 12.8499 | 12.4713 | 12.6893 | 12.923 | 12.4994 | 12.6511 | 12.4506 | 12.3221 | NaN | NaN | NaN | 12.729 | 121.7376 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 527.3058 | NaN | 11.2604 | NaN | 29.2723
3734.1292 | 12.8524 | 12.4911 | 12.6893 | 12.9066 | 12.5334 | 12.6672 | 12.4593 | 12.3215 | NaN | NaN | NaN | 12.7314 | 126.2194 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 525.4087 | NaN | 24.173 | NaN | 18.4761
3735.1292 | 12.8643 | 12.4973 | 12.6905 | 12.8973 | 12.5066 | 12.6647 | 12.4619 | 12.32 | NaN | NaN | NaN | 12.7063 | 132.9062 | NaN | NaN | NaN | -2.7475 | NaN | NaN | NaN | NaN | 528.5018 | NaN | 24.6888 | NaN | 21.29
3736.1292 | 12.861 | 12.4805 | 12.6863 | 12.9134 | 12.5387 | 12.6593 | 12.4534 | 12.3134 | NaN | NaN | NaN | 12.7367 | 121.6655 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 529.1927 | NaN | 8.4613 | NaN | 17.7752
3737.1292 | 12.855 | 12.504 | 12.6867 | 12.9479 | 12.4503 | 12.6741 | 12.4595 | 12.306 | NaN | NaN | NaN | 12.7188 | 129.0219 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 530.221 | NaN | 25.4939 | NaN | 29.9579
3738.1292 | 12.8516 | 12.5144 | 12.6847 | 12.9356 | 12.4538 | 12.6764 | 12.4587 | 12.314 | NaN | NaN | NaN | 12.7153 | 124.4301 | NaN | NaN | NaN | 0.5163 | NaN | NaN | NaN | NaN | 528.1409 | NaN | 14.4356 | NaN | 28.1318
3739.1292 | 12.8636 | 12.5494 | 12.6829 | 12.8668 | 12.5191 | 12.6779 | 12.4677 | 12.3084 | NaN | NaN | NaN | 12.7291 | 122.5226 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 528.6602 | NaN | 9.2958 | NaN | 17.6209
3740.1292 | 12.8643 | 12.5345 | 12.6776 | 12.9174 | 12.43 | 12.687 | 12.4636 | 12.3091 | NaN | NaN | NaN | 12.6832 | 134.2536 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 529.7628 | NaN | 39.8432 | NaN | 19.6855
3741.1292 | 12.859 | 12.4887 | 12.6797 | 12.9133 | 12.4973 | 12.6657 | 12.4564 | 12.3071 | NaN | NaN | NaN | 12.7039 | 119.4678 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 530.379 | NaN | 10.858 | NaN | 27.284
3742.1292 | 12.8548 | 12.5248 | 12.6831 | 12.8928 | 12.5088 | 12.6653 | 12.4524 | 12.3158 | NaN | NaN | NaN | 12.7069 | 125.1066 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 530.0421 | NaN | 5.3253 | NaN | 22.0266
3743.1292 | 12.9145 | 12.5192 | 12.6911 | 12.923 | 12.47 | 12.6651 | 12.452 | 12.3063 | NaN | NaN | NaN | 12.7048 | 132.1881 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 529.9694 | NaN | 19.8405 | NaN | 20.5892
3744.1292 | 12.8758 | 12.5238 | 12.6886 | 12.8885 | 12.4439 | 12.6671 | 12.4452 | 12.3052 | NaN | NaN | NaN | 12.7056 | 125.4064 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 531.4635 | NaN | 12.9655 | NaN | 16.5593
3745.1292 | 12.878 | 12.4998 | 12.6927 | 12.9494 | 12.4632 | 12.6555 | 12.4455 | 12.311 | NaN | NaN | NaN | 12.6985 | 127.2238 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 530.3713 | NaN | 16.1233 | NaN | 22.2556
3746.1292 | 12.9227 | 12.513 | 12.6945 | 12.9146 | 12.4431 | 12.6663 | 12.4549 | 12.3133 | NaN | NaN | NaN | 12.7134 | 123.1321 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 530.4578 | NaN | 30.7274 | NaN | 21.33
3747.1292 | 12.8956 | 12.5262 | 12.691 | 12.9166 | 12.5181 | 12.6645 | 12.4538 | 12.3119 | NaN | NaN | NaN | 12.6951 | 122.4339 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 532.8329 | NaN | 32.2501 | NaN | 23.0783
3748.1292 | 12.8748 | 12.5393 | 12.6921 | 12.914 | 12.3866 | 12.685 | 12.4571 | 12.3221 | NaN | NaN | NaN | 12.7242 | 135.831 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 533.6519 | NaN | 13.9532 | NaN | 24.2969
3749.1292 | 12.873 | 12.4993 | 12.6915 | 12.9532 | 12.5155 | 12.6548 | 12.4498 | 12.316 | NaN | NaN | NaN | 12.6995 | 121.567 | NaN | NaN | NaN | 1.425 | NaN | NaN | NaN | NaN | 530.1462 | NaN | 23.9548 | NaN | 20.2713
3750.1292 | 12.8839 | 12.5735 | 12.6977 | 12.9884 | 12.4895 | 12.6879 | 12.4646 | 12.3162 | NaN | NaN | NaN | 12.6997 | 139.6283 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 533.1323 | NaN | 8.5898 | NaN | 25.0497
3751.1292 | 12.877 | 12.5253 | 12.6973 | 12.916 | 12.5039 | 12.6818 | 12.4629 | 12.3177 | NaN | NaN | NaN | 12.6916 | 124.2476 | NaN | NaN | NaN | -14.8719 | NaN | NaN | NaN | NaN | 532.7199 | NaN | 6.4373 | NaN | 26.3737
3752.1292 | 12.8731 | 12.5135 | 12.6986 | 12.9369 | 12.4791 | 12.6802 | 12.4669 | 12.3209 | NaN | NaN | NaN | 12.7187 | 117.1636 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 528.7633 | NaN | 33.6978 | NaN | 24.2968
3753.1292 | 12.8743 | 12.5434 | 12.6995 | 12.9178 | 12.5009 | 12.6848 | 12.4609 | 12.3226 | NaN | NaN | NaN | 12.6973 | 124.6199 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 534.4297 | NaN | 6.2102 | NaN | 22.0791
3754.1292 | 12.8679 | 12.4957 | 12.6941 | 12.905 | 12.5007 | 12.6593 | 12.4464 | 12.3251 | NaN | NaN | NaN | 12.713 | 124.8233 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 534.5078 | NaN | 30.3023 | NaN | 22.1606
3755.1292 | 12.8671 | 12.4901 | 12.7014 | 12.9404 | 12.4571 | 12.6663 | 12.4523 | 12.3199 | NaN | NaN | NaN | 12.7342 | 126.711 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 532.1071 | NaN | 6.6151 | NaN | 24.8166
3756.1292 | 12.8565 | 12.575 | 12.6975 | 12.9234 | 12.4982 | 12.7069 | 12.4759 | 12.324 | NaN | NaN | NaN | 12.7236 | 121.9461 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 530.7623 | NaN | 36.5965 | NaN | 25.5454
3757.1292 | 12.8734 | 12.4981 | 12.708 | 12.9091 | 12.4635 | 12.6758 | 12.4634 | 12.3189 | NaN | NaN | NaN | 12.7842 | 126.3698 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 531.5175 | NaN | 23.1426 | NaN | 27.8964
3758.1292 | 12.831 | 12.5199 | 12.709 | 12.9384 | 12.5316 | 12.678 | 12.4594 | 12.3216 | NaN | NaN | NaN | 12.767 | 122.8861 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 535.1829 | NaN | 5.8614 | NaN | 26.9373
3759.1292 | 12.9343 | 12.4898 | 12.7092 | 12.8822 | 12.5015 | 12.6868 | 12.4618 | 12.3175 | NaN | NaN | NaN | 12.6979 | 127.0425 | NaN | NaN | NaN | -18.8632 | NaN | NaN | NaN | NaN | 532.1062 | NaN | 36.4727 | NaN | 27.7514
3760.1292 | 12.87 | 12.4954 | 12.7112 | 12.9505 | 12.441 | 12.6812 | 12.4533 | 12.3197 | NaN | NaN | NaN | 12.7251 | 117.563 | NaN | NaN | NaN | -12.7747 | NaN | NaN | NaN | NaN | 535.588 | NaN | 9.4482 | NaN | 14.5971
3761.1292 | 12.8666 | 12.5692 | 12.7102 | 12.8822 | 12.4416 | 12.7286 | 12.4761 | 12.317 | NaN | NaN | NaN | 12.7072 | 131.7261 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 535.5698 | NaN | 20.2071 | NaN | 24.0587
3762.1292 | 12.8603 | 12.6267 | 12.7125 | 12.8833 | 12.3986 | 12.8166 | 12.5214 | 12.3177 | NaN | NaN | NaN | 12.7124 | 115.9131 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 538.8099 | NaN | 10.6019 | NaN | 22.5591
3763.1292 | 12.8356 | 12.5585 | 12.7104 | 13.0017 | 12.4901 | 12.7346 | 12.4973 | 12.3183 | NaN | NaN | NaN | 12.7012 | 124.1339 | NaN | NaN | NaN | -1.7014 | NaN | NaN | NaN | NaN | 532.6911 | NaN | 25.5465 | NaN | 20.3677
3764.1292 | 12.8804 | 12.5217 | 12.7087 | 12.9379 | 12.5105 | 12.708 | 12.478 | 12.3172 | NaN | NaN | NaN | 12.709 | 124.3063 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 533.9753 | NaN | 12.6058 | NaN | 16.8101
3765.1292 | 12.8937 | 12.4587 | 12.7034 | 12.94 | 12.4649 | 12.6879 | 12.4681 | 12.3072 | NaN | NaN | NaN | 12.6956 | 123.9991 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 536.8014 | NaN | 29.0102 | NaN | 23.8
3766.1292 | 12.8967 | 12.4796 | 12.7129 | 12.9175 | 12.5195 | 12.6938 | 12.4671 | 12.314 | NaN | NaN | NaN | 12.7082 | 118.5933 | NaN | NaN | NaN | -18.5985 | NaN | NaN | NaN | NaN | 533.7925 | NaN | 21.9683 | NaN | 15.0473
3767.1292 | 12.8841 | 12.447 | 12.7095 | 12.9419 | 12.4916 | 12.6967 | 12.4726 | 12.3164 | NaN | NaN | NaN | 12.7187 | 117.3044 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 535.8893 | NaN | 8.2911 | NaN | 23.5914
3768.1292 | 12.8791 | 12.5433 | 12.7074 | 12.9166 | 12.4937 | 12.7182 | 12.4831 | 12.3176 | NaN | NaN | NaN | 12.7089 | 129.4313 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 534.1807 | NaN | 6.3071 | NaN | 24.9858
3769.1292 | 12.8896 | 12.4506 | 12.6995 | 12.9199 | 12.5085 | 12.6872 | 12.4728 | 12.3219 | NaN | NaN | NaN | 12.7051 | 127.126 | NaN | NaN | NaN | 1.9536 | NaN | NaN | NaN | NaN | 534.2987 | NaN | 16.6427 | NaN | 25.7889
3770.1292 | 12.8872 | 12.5092 | 12.6976 | 12.9767 | 12.4054 | 12.7201 | 12.4795 | 12.3198 | NaN | NaN | NaN | 12.7304 | 128.56 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 533.9308 | NaN | 23.8277 | NaN | 18.0783
3771.1292 | 12.9296 | 12.5512 | 12.6992 | 12.9089 | 12.5311 | 12.732 | 12.4864 | 12.3214 | NaN | NaN | NaN | 12.7272 | 126.2636 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 531.7903 | NaN | 4.0718 | NaN | 16.2497
3772.1292 | 12.9019 | 12.4839 | 12.6897 | 12.9497 | 12.461 | 12.6974 | 12.4742 | 12.3195 | NaN | NaN | NaN | 12.7411 | 130.7579 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 531.4489 | NaN | 27.4545 | NaN | 28.9417
3773.1292 | 12.8728 | 12.4767 | 12.6932 | 12.9561 | 12.4631 | 12.6801 | 12.4675 | 12.3185 | NaN | NaN | NaN | 12.7578 | 113.5763 | NaN | NaN | NaN | -5.2714 | NaN | NaN | NaN | NaN | 531.7491 | NaN | 13.9534 | NaN | 24.0138
3774.1292 | 12.8636 | 12.4492 | 12.6877 | 12.9348 | 12.4718 | 12.6753 | 12.4624 | 12.3177 | NaN | NaN | NaN | 12.7484 | 132.5558 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 532.9624 | NaN | 6.0753 | NaN | 22.8207
3775.1292 | 12.86 | 12.4849 | 12.6845 | 12.9373 | 12.5221 | 12.7022 | 12.479 | 12.3183 | NaN | NaN | NaN | 12.7693 | 131.063 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 533.796 | NaN | 14.04 | NaN | 24.068
3776.1292 | 12.8715 | 12.4806 | 12.6862 | 12.9407 | 12.4646 | 12.6979 | 12.476 | 12.32 | NaN | NaN | NaN | 12.7879 | 130.1809 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 530.0275 | NaN | 10.0659 | NaN | 21.9877
3777.1292 | 12.8735 | 12.4464 | 12.6806 | 12.9988 | 12.4184 | 12.6751 | 12.4601 | 12.3156 | NaN | NaN | NaN | 12.7468 | 125.4327 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 528.9702 | NaN | 7.7987 | NaN | 26.1515
3778.1292 | 12.8806 | 12.5628 | 12.6868 | 12.9355 | 12.4077 | 12.7388 | 12.4935 | 12.323 | NaN | NaN | NaN | 12.7544 | 121.8019 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 532.1986 | NaN | 16.9911 | NaN | 23.8121
3779.1292 | 12.8742 | 12.4714 | 12.6839 | 12.906 | 12.4177 | 12.6832 | 12.4701 | 12.323 | NaN | NaN | NaN | 12.7706 | 121.5581 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 532.5582 | NaN | 5.6135 | NaN | 23.2218
3780.1292 | 12.8787 | 12.4574 | 12.6846 | 12.9363 | 12.4743 | 12.6749 | 12.4682 | 12.3232 | NaN | NaN | NaN | 12.7732 | 123.269 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 533.4241 | NaN | 27.0423 | NaN | 27.0111
3781.1292 | 12.8557 | 12.5608 | 12.6896 | 12.9799 | 12.5245 | 12.7065 | 12.4917 | 12.3255 | NaN | NaN | NaN | 12.7772 | 127.5174 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 530.4933 | NaN | 5.8264 | NaN | 12.2059
3782.1292 | 12.9661 | 12.4944 | 12.6897 | 12.9447 | 12.5369 | 12.6723 | 12.4707 | 12.3192 | NaN | NaN | NaN | 12.7475 | 130.1475 | NaN | NaN | NaN | -12.9063 | NaN | NaN | NaN | NaN | 525.9521 | NaN | 19.9592 | NaN | 26.3464
3783.1292 | 12.9006 | 12.5019 | 12.6891 | 12.9527 | 12.4902 | 12.692 | 12.4746 | 12.3263 | NaN | NaN | NaN | 12.7436 | 126.9177 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 526.6873 | NaN | 4.9043 | NaN | 18.6378
3784.1292 | 12.9867 | 12.5644 | 12.6917 | 12.9117 | 12.4611 | 12.713 | 12.4915 | 12.3234 | NaN | NaN | NaN | 12.7646 | 118.0404 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 528.2069 | NaN | 7.8548 | NaN | 19.5697
3785.1292 | 12.9414 | 12.5188 | 12.6884 | 12.9631 | 12.4408 | 12.6951 | 12.4776 | 12.3167 | NaN | NaN | NaN | 12.7414 | 125.9889 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 528.1441 | NaN | 10.0485 | NaN | 26.7382
3786.1292 | 12.9999 | 12.4662 | 12.693 | 12.9707 | 12.5466 | 12.6685 | 12.4697 | 12.3278 | NaN | NaN | NaN | 12.7895 | 126.1188 | NaN | NaN | NaN | -0.4999 | NaN | NaN | NaN | NaN | 528.2995 | NaN | 9.3939 | NaN | 12.2494
3787.1292 | 12.8964 | 12.4803 | 12.6919 | 12.9557 | 12.4498 | 12.6757 | 12.4661 | 12.3247 | NaN | NaN | NaN | 12.802 | 113.2572 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 527.9582 | NaN | 8.4917 | NaN | 26.7448
3788.1292 | 12.8993 | 12.4984 | 12.6911 | 12.9473 | 12.5142 | 12.6895 | 12.488 | 12.3238 | NaN | NaN | NaN | 12.8296 | 134.9858 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 528.6141 | NaN | 5.6734 | NaN | 20.9865
3789.1292 | 12.9135 | 12.5145 | 12.6913 | 12.9827 | 12.5047 | 12.6891 | 12.4879 | 12.3344 | NaN | NaN | NaN | 12.7703 | 114.7249 | NaN | NaN | NaN | 4.8883 | NaN | NaN | NaN | NaN | 529.5812 | NaN | 11.0745 | NaN | 30.0602
3790.1292 | 12.9239 | 12.5118 | 12.7 | 12.9788 | 12.4178 | 12.6814 | 12.4771 | 12.3331 | NaN | NaN | NaN | 12.7747 | 122.815 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 528.5377 | NaN | 22.4474 | NaN | 23.0557
3791.1292 | 12.9748 | 12.5422 | 12.6962 | 12.9684 | 12.4799 | 12.7084 | 12.4817 | 12.3401 | NaN | NaN | NaN | 12.8509 | 118.9996 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 530.1981 | NaN | 10.0614 | NaN | 19.165
3792.4885 | 12.9016 | 12.4643 | 12.6977 | 12.9899 | 12.4518 | 12.6603 | 12.4782 | 12.3337 | NaN | NaN | NaN | 12.7694 | 121.6083 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 529.7111 | NaN | 6.6292 | NaN | 18.9977
3793.176 | 12.866 | 12.5599 | 12.6956 | 12.9882 | 12.4883 | 12.691 | 12.4925 | 12.3413 | NaN | NaN | NaN | 12.7928 | 129.6636 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 531.3646 | NaN | 16.1019 | NaN | 26.418
3794.2854 | 12.9187 | 12.5393 | 12.702 | 12.967 | 12.5343 | 12.6829 | 12.4922 | 12.3484 | NaN | NaN | NaN | 12.761 | 114.1636 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 531.3656 | NaN | 14.0341 | NaN | 24.8047
3795.1917 | 12.8829 | 12.4632 | 12.7029 | 12.9798 | 12.4739 | 12.6659 | 12.4724 | 12.3448 | NaN | NaN | NaN | 12.7824 | 124.3843 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 532.4572 | NaN | 8.0274 | NaN | 26.0952
3796.2229 | 12.9191 | 12.4603 | 12.6998 | 12.9846 | 12.4586 | 12.6485 | 12.4685 | 12.3536 | NaN | NaN | NaN | 12.7609 | 124.8635 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 532.4435 | NaN | 22.1298 | NaN | 17.3498
3797.5979 | 12.8677 | 12.4809 | 12.7049 | 13.0462 | 12.5093 | 12.6755 | 12.4655 | 12.3568 | NaN | NaN | NaN | 12.773 | 123.1261 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 532.5426 | NaN | 23.4942 | NaN | 24.1348
3798.1292 | 12.8384 | 12.5187 | 12.708 | 12.9675 | 12.496 | 12.6823 | 12.4677 | 12.3581 | NaN | NaN | NaN | 12.8031 | 126.178 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 529.7835 | NaN | 37.9239 | NaN | 30.4744
3799.1292 | 12.8829 | 12.4575 | 12.7075 | 13.0316 | 12.4324 | 12.6708 | 12.4722 | 12.3561 | NaN | NaN | NaN | 12.7622 | 121.274 | NaN | NaN | NaN | -16.1495 | NaN | NaN | NaN | NaN | 531.1861 | NaN | 25.2537 | NaN | 27.867
3800.1292 | 12.8634 | 12.4628 | 12.7099 | 12.999 | 12.5478 | 12.672 | 12.4684 | 12.3597 | NaN | NaN | NaN | 12.7651 | 119.1807 | NaN | NaN | NaN | -5.9833 | NaN | NaN | NaN | NaN | 527.3769 | NaN | 43.0675 | NaN | 22.8536
3801.1292 | 12.8609 | 12.5593 | 12.709 | 12.9771 | 12.4836 | 12.7021 | 12.4866 | 12.3629 | NaN | NaN | NaN | 12.7995 | 129.6914 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 529.5101 | NaN | 9.0174 | NaN | 19.3144
3802.1292 | 12.8715 | 12.5887 | 12.7074 | 12.956 | 12.5124 | 12.7201 | 12.48 | 12.3677 | NaN | NaN | NaN | 12.7483 | 112.8172 | NaN | NaN | NaN | -18.0059 | NaN | NaN | NaN | NaN | 529.864 | NaN | 9.3887 | NaN | 27.621
3803.1292 | 12.8686 | 12.5529 | 12.7167 | 13.0003 | 12.4985 | 12.7251 | 12.5077 | 12.3725 | NaN | NaN | NaN | 12.7435 | 114.1317 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 528.8684 | NaN | 21.5103 | NaN | 21.0321
3804.1292 | 12.8688 | 12.4871 | 12.721 | 12.9841 | 12.4675 | 12.6802 | 12.4736 | 12.3704 | NaN | NaN | NaN | 12.7455 | 124.8195 | NaN | NaN | NaN | -3.3949 | NaN | NaN | NaN | NaN | 528.9485 | NaN | 9.5498 | NaN | 26.0735
3805.1292 | 12.8636 | 12.5129 | 12.7196 | 12.9491 | 12.4828 | 12.6975 | 12.4817 | 12.3723 | NaN | NaN | NaN | 12.7608 | 131.3254 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 527.6508 | NaN | 5.4878 | NaN | 25.4471
3806.1292 | 12.863 | 12.4469 | 12.7257 | 13.0095 | 12.4826 | 12.6632 | 12.4751 | 12.3769 | NaN | NaN | NaN | 12.7649 | 124.5887 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 530.0242 | NaN | 24.9845 | NaN | 22.3892
3807.1292 | 12.8503 | 12.4516 | 12.7282 | 12.9925 | 12.5186 | 12.6571 | 12.4822 | 12.3716 | NaN | NaN | NaN | 12.7472 | 126.8031 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 527.8145 | NaN | 5.9099 | NaN | 16.5746
3808.1292 | 12.8584 | 12.5077 | 12.7307 | 13.029 | 12.4296 | 12.6997 | 12.4937 | 12.3805 | NaN | NaN | NaN | 12.7627 | 120.2584 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 527.8277 | NaN | 6.5955 | NaN | 27.2954
3809.1292 | 12.8604 | 12.4863 | 12.7322 | 13.0022 | 12.5361 | 12.6747 | 12.4919 | 12.3703 | NaN | NaN | NaN | 12.7528 | 126.1959 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 526.7792 | NaN | 7.0431 | NaN | 18.313
3810.1292 | 12.8497 | 12.4647 | 12.7301 | 13.0194 | 12.4746 | 12.6662 | 12.4805 | 12.3677 | NaN | NaN | NaN | 12.7875 | 129.3201 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 527.4306 | NaN | 8.5241 | NaN | 23.8754
3811.1292 | 12.8645 | 12.4749 | 12.7332 | 12.945 | 12.4505 | 12.6726 | 12.4819 | 12.373 | NaN | NaN | NaN | 12.8018 | 121.3863 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 528.9288 | NaN | 7.5891 | NaN | 12.4542
3812.1292 | 12.8631 | 12.4585 | 12.7356 | 12.9942 | 12.5179 | 12.6784 | 12.4781 | 12.3735 | NaN | NaN | NaN | 12.782 | 129.1019 | NaN | NaN | NaN | -7.6254 | NaN | NaN | NaN | NaN | 525.6365 | NaN | 15.5025 | NaN | 24.0144
3813.1292 | 12.8583 | 12.4472 | 12.7329 | 12.9989 | 12.4815 | 12.6633 | 12.4721 | 12.3753 | NaN | NaN | NaN | 12.7702 | 128.7563 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 523.1968 | NaN | 28.5588 | NaN | 21.6099
3814.1292 | 12.8674 | 12.4293 | 12.7356 | 12.982 | 12.5247 | 12.6619 | 12.474 | 12.3761 | NaN | NaN | NaN | 12.759 | 128.8401 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 524.4101 | NaN | 26.8198 | NaN | 19.4695
3815.1292 | 12.8642 | 12.4792 | 12.7341 | 12.996 | 12.4891 | 12.6771 | 12.4776 | 12.3794 | NaN | NaN | NaN | 12.7559 | 114.927 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 525.6474 | NaN | 15.6294 | NaN | 24.9105
3816.1292 | 12.8723 | 12.4929 | 12.7414 | 12.9687 | 12.5136 | 12.6811 | 12.4818 | 12.3757 | NaN | NaN | NaN | 12.7553 | 117.7069 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 526.3574 | NaN | 10.5247 | NaN | 18.6267
3817.1292 | 12.8735 | 12.498 | 12.7457 | 12.9816 | 12.5146 | 12.6885 | 12.484 | 12.3748 | NaN | NaN | NaN | 12.7749 | 124.2431 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 525.8674 | NaN | 20.317 | NaN | 23.5104
3818.1292 | 12.8698 | 12.4573 | 12.7454 | 13.0273 | 12.4391 | 12.66 | 12.471 | 12.3704 | NaN | NaN | NaN | 12.783 | 126.3897 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 525.377 | NaN | 21.3707 | NaN | 22.9901
3819.1292 | 12.8869 | 12.4577 | 12.7434 | 13.0108 | 12.4856 | 12.6609 | 12.4793 | 12.3777 | NaN | NaN | NaN | 12.7657 | 120.7509 | NaN | NaN | NaN | 18.9683 | NaN | NaN | NaN | NaN | 523.7672 | NaN | 10.2336 | NaN | 20.0936
3820.1292 | 12.8777 | 12.4841 | 12.7445 | 13.0767 | 12.4511 | 12.6737 | 12.4849 | 12.3733 | NaN | NaN | NaN | 12.7312 | 128.1115 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 522.5111 | NaN | 5.8693 | NaN | 23.7043
3821.1292 | 12.8889 | 12.4902 | 12.7504 | 12.9794 | 12.5357 | 12.6678 | 12.4893 | 12.3701 | NaN | NaN | NaN | 12.7679 | 126.8319 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 523.7977 | NaN | 7.7163 | NaN | 18.5699
3822.1292 | 12.9116 | 12.4991 | 12.7449 | 12.9842 | 12.5227 | 12.666 | 12.487 | 12.3759 | NaN | NaN | NaN | 12.741 | 116.9084 | NaN | NaN | NaN | 2.9529 | NaN | NaN | NaN | NaN | 524.7775 | NaN | 12.4609 | NaN | 27.5496
3823.1292 | 12.8803 | 12.5721 | 12.7497 | 12.968 | 12.4883 | 12.7092 | 12.5109 | 12.3707 | NaN | NaN | NaN | 12.7348 | 115.4305 | NaN | NaN | NaN | -6.6186 | NaN | NaN | NaN | NaN | 523.2412 | NaN | 15.6636 | NaN | 25.9664
3824.1292 | 12.8822 | 12.5227 | 12.7526 | 12.9665 | 12.5227 | 12.6953 | 12.4944 | 12.3769 | NaN | NaN | NaN | 12.7505 | 125.9365 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 523.3783 | NaN | 8.9052 | NaN | 22.6645
3825.1292 | 12.8873 | 12.5647 | 12.75 | 12.9625 | 12.5537 | 12.6875 | 12.5052 | 12.379 | NaN | NaN | NaN | 12.7682 | 131.7098 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.8968 | NaN | 20.003 | NaN | 28.4598
3826.1448 | 12.8971 | 12.4767 | 12.7524 | 12.9962 | 12.5352 | 12.6625 | 12.4885 | 12.3815 | NaN | NaN | NaN | 12.7871 | 132.5389 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 520.8917 | NaN | 14.7411 | NaN | 25.8275
3827.1292 | 12.883 | 12.4908 | 12.7486 | 13.0038 | 12.5299 | 12.6606 | 12.488 | 12.3815 | NaN | NaN | NaN | 12.7952 | 123.0619 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 522.2517 | NaN | 7.2703 | NaN | 21.1875
3828.1448 | 12.8874 | 12.5064 | 12.7575 | 12.9595 | 12.4818 | 12.6802 | 12.4991 | 12.3763 | NaN | NaN | NaN | 12.7504 | 126.2252 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 525.451 | NaN | 12.8843 | NaN | 23.295
3829.1448 | 12.8774 | 12.5092 | 12.7599 | 13.0115 | 12.545 | 12.6731 | 12.4967 | 12.3811 | NaN | NaN | NaN | 12.754 | 120.923 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 524.0239 | NaN | 9.9376 | NaN | 28.6242
3830.1292 | 12.8909 | 12.564 | 12.7601 | 12.9736 | 12.4593 | 12.6973 | 12.4978 | 12.3825 | NaN | NaN | NaN | 12.7463 | 124.5248 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 526.3841 | NaN | 10.686 | NaN | 23.1073
3831.1448 | 12.8924 | 12.6177 | 12.7558 | 12.9895 | 12.4724 | 12.7269 | 12.5117 | 12.3808 | NaN | NaN | NaN | 12.7688 | 123.7576 | NaN | NaN | NaN | -3.9136 | NaN | NaN | NaN | NaN | 526.1411 | NaN | 5.7277 | NaN | 16.8135
3832.1448 | 12.8985 | 12.543 | 12.7559 | 12.9787 | 12.5539 | 12.6736 | 12.4992 | 12.3826 | NaN | NaN | NaN | 12.7579 | 127.5226 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 525.3393 | NaN | 32.9907 | NaN | 23.9946
3833.1292 | 12.8932 | 12.5315 | 12.7595 | 13.0037 | 12.5329 | 12.6803 | 12.4922 | 12.3792 | NaN | NaN | NaN | 12.7434 | 119.3871 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 526.9486 | NaN | 12.5781 | NaN | 21.1941
3834.1292 | 12.895 | 12.5476 | 12.7544 | 12.9591 | 12.483 | 12.6969 | 12.4903 | 12.3839 | NaN | NaN | NaN | 12.8115 | 128.2575 | NaN | NaN | NaN | -19.1411 | NaN | NaN | NaN | NaN | 526.6762 | NaN | 6.2537 | NaN | 21.9863
3835.1292 | 12.9197 | 12.5444 | 12.7559 | 13.0247 | 12.499 | 12.6791 | 12.4944 | 12.3833 | NaN | NaN | NaN | 12.7546 | 128.4482 | NaN | NaN | NaN | -3.8986 | NaN | NaN | NaN | NaN | 525.4186 | NaN | 6.1042 | NaN | 26.6079
3836.1292 | 12.8687 | 12.6091 | 12.7552 | 13.0073 | 12.4893 | 12.703 | 12.5002 | 12.3786 | NaN | NaN | NaN | 12.7665 | 121.9902 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 525.0428 | NaN | 6.2734 | NaN | 26.8755
3837.1292 | 12.919 | 12.5427 | 12.7528 | 12.9987 | 12.5293 | 12.6827 | 12.4839 | 12.3874 | NaN | NaN | NaN | 12.7496 | 113.2154 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 524.9095 | NaN | 6.7787 | NaN | 24.5692
3838.1292 | 12.9757 | 12.5475 | 12.7547 | 12.9813 | 12.5632 | 12.6863 | 12.4825 | 12.3807 | NaN | NaN | NaN | 12.7901 | 120.7741 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 524.399 | NaN | 6.1279 | NaN | 20.3712
3839.1292 | 12.9929 | 12.5279 | 12.7527 | 13.039 | 12.5455 | 12.6697 | 12.4831 | 12.3804 | NaN | NaN | NaN | 12.7812 | 118.3942 | NaN | NaN | NaN | -5.6644 | NaN | NaN | NaN | NaN | 526.5745 | NaN | 6.5523 | NaN | 19.0947
3840.1292 | 12.9128 | 12.5582 | 12.7497 | 13.0052 | 12.5382 | 12.697 | 12.5013 | 12.3752 | NaN | NaN | NaN | 12.7515 | 112.7792 | NaN | NaN | NaN | -0.4744 | NaN | NaN | NaN | NaN | 526.778 | NaN | 5.7408 | NaN | 25.9093
3841.1292 | 12.9745 | 12.5303 | 12.7532 | 12.9946 | 12.5331 | 12.6757 | 12.485 | 12.3728 | NaN | NaN | NaN | 12.7326 | 121.2702 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 527.2008 | NaN | 34.5741 | NaN | 13.7047
3842.1292 | 12.9263 | 12.5513 | 12.7545 | 13.0459 | 12.462 | 12.6991 | 12.503 | 12.3744 | NaN | NaN | NaN | 12.7304 | 121.8986 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 526.2111 | NaN | 6.9786 | NaN | 21.1343
3843.1292 | 12.9154 | 12.5294 | 12.7533 | 12.9811 | 12.525 | 12.6875 | 12.492 | 12.3733 | NaN | NaN | NaN | 12.7379 | 120.9767 | NaN | NaN | NaN | -19.1355 | NaN | NaN | NaN | NaN | 526.6861 | NaN | 4.8921 | NaN | 26.1026
3844.1292 | 12.9152 | 12.5678 | 12.756 | 13.0376 | 12.5148 | 12.7052 | 12.4875 | 12.3717 | NaN | NaN | NaN | 12.7277 | 140.1828 | NaN | NaN | NaN | -12.8863 | NaN | NaN | NaN | NaN | 521.0066 | NaN | 5.3141 | NaN | 20.1736
3845.1292 | 12.9175 | 12.5568 | 12.7597 | 13.0235 | 12.4472 | 12.6951 | 12.4896 | 12.3745 | NaN | NaN | NaN | 12.7319 | 116.7243 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 523.5902 | NaN | 33.4745 | NaN | 27.1247
3846.1292 | 12.9132 | 12.5543 | 12.7556 | 12.9836 | 12.4911 | 12.6984 | 12.4869 | 12.373 | NaN | NaN | NaN | 12.7373 | 125.6767 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 526.2419 | NaN | 5.6318 | NaN | 26.0761
3847.1292 | 12.9133 | 12.5621 | 12.7605 | 13.0224 | 12.4531 | 12.6892 | 12.4919 | 12.3698 | NaN | NaN | NaN | 12.7711 | 132.8309 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 523.2005 | NaN | 39.7404 | NaN | 22.0198
3848.1292 | 12.9149 | 12.5732 | 12.7607 | 12.9942 | 12.4971 | 12.7039 | 12.5049 | 12.3738 | NaN | NaN | NaN | 12.7844 | 133.0443 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 526.6649 | NaN | 12.3173 | NaN | 21.0173
3849.1292 | 12.9267 | 12.6241 | 12.7624 | 13.0684 | 12.5576 | 12.724 | 12.5035 | 12.3822 | NaN | NaN | NaN | 12.7403 | 123.071 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 525.1037 | NaN | 6.6639 | NaN | 28.1636
3850.1292 | 12.9095 | 12.6506 | 12.7524 | 13.0281 | 12.5731 | 12.7496 | 12.5093 | 12.3791 | NaN | NaN | NaN | 12.7389 | 123.8176 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 524.5068 | NaN | 7.8355 | NaN | 8.7311
3851.1292 | 12.9125 | 12.5747 | 12.7581 | 13.0238 | 12.473 | 12.7061 | 12.4941 | 12.38 | NaN | NaN | NaN | 12.7231 | 124.9417 | NaN | NaN | NaN | 2.5843 | NaN | NaN | NaN | NaN | 524.2601 | NaN | 9.3589 | NaN | 20.3353
3852.1292 | 12.9133 | 12.5556 | 12.7612 | 13.0269 | 12.5153 | 12.7023 | 12.4975 | 12.3771 | NaN | NaN | NaN | 12.7343 | 123.1023 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 528.6051 | NaN | 5.3821 | NaN | 25.4793
3853.1292 | 12.9146 | 12.5939 | 12.7608 | 13.0036 | 12.471 | 12.7239 | 12.5005 | 12.3796 | NaN | NaN | NaN | 12.7414 | 121.8446 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 526.1812 | NaN | 24.5346 | NaN | 25.5285
3854.1292 | 12.9198 | 12.5533 | 12.7636 | 12.9943 | 12.5387 | 12.7095 | 12.4961 | 12.3793 | NaN | NaN | NaN | 12.7165 | 118.9003 | NaN | NaN | NaN | -5.7933 | NaN | NaN | NaN | NaN | 526.1451 | NaN | 6.9015 | NaN | 22.945
3855.1292 | 12.9186 | 12.5638 | 12.7603 | 13.0243 | 12.5693 | 12.7126 | 12.4973 | 12.371 | NaN | NaN | NaN | 12.712 | 118.8857 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 524.3007 | NaN | 4.4801 | NaN | 23.2668
3856.1448 | 12.9265 | 12.5633 | 12.7603 | 13.0055 | 12.4614 | 12.7236 | 12.5026 | 12.3734 | NaN | NaN | NaN | 12.7213 | 122.1293 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 526.9591 | NaN | 12.3343 | NaN | 25.5155
3857.1292 | 12.9154 | 12.5546 | 12.7631 | 13.0271 | 12.4747 | 12.7201 | 12.4975 | 12.3781 | NaN | NaN | NaN | 12.7035 | 114.3448 | NaN | NaN | NaN | 4.8145 | NaN | NaN | NaN | NaN | 522.7643 | NaN | 6.7959 | NaN | 19.704
3858.1292 | 12.9191 | 12.5593 | 12.7613 | 13.0781 | 12.4758 | 12.7327 | 12.5084 | 12.3723 | NaN | NaN | NaN | 12.7142 | 121.5647 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 526.1337 | NaN | 5.0421 | NaN | 24.8852
3859.1292 | 12.9202 | 12.5597 | 12.7702 | 12.989 | 12.5711 | 12.7197 | 12.5101 | 12.3821 | NaN | NaN | NaN | 12.705 | 122.9283 | NaN | NaN | NaN | 1.9486 | NaN | NaN | NaN | NaN | 528.9468 | NaN | 36.2024 | NaN | 24.0289
3860.1292 | 12.9181 | 12.5943 | 12.7641 | 13.0341 | 12.4812 | 12.7357 | 12.5073 | 12.3814 | NaN | NaN | NaN | 12.7227 | 131.5148 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 526.5357 | NaN | 13.8663 | NaN | 26.7607
3861.1292 | 12.9255 | 12.5967 | 12.771 | 12.98 | 12.5208 | 12.7281 | 12.5078 | 12.3838 | NaN | NaN | NaN | 12.7429 | 140.5314 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 527.1814 | NaN | 44.1446 | NaN | 25.5723
3862.1292 | 12.9169 | 12.6179 | 12.7634 | 12.9764 | 12.5328 | 12.7357 | 12.5102 | 12.3839 | NaN | NaN | NaN | 12.7012 | 123.9203 | NaN | NaN | NaN | -1.2459 | NaN | NaN | NaN | NaN | 526.2642 | NaN | 34.5401 | NaN | 26.043
3863.1292 | 12.9219 | 12.5781 | 12.7672 | 13.0212 | 12.5115 | 12.7286 | 12.5055 | 12.3793 | NaN | NaN | NaN | 12.7301 | 135.4027 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 527.764 | NaN | 8.3446 | NaN | 26.24
3864.1292 | 12.9255 | 12.6024 | 12.7608 | 13.0105 | 12.5528 | 12.7207 | 12.5086 | 12.3822 | NaN | NaN | NaN | 12.6976 | 124.5374 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 530.9692 | NaN | 6.5426 | NaN | 18.4394
3865.1292 | 12.9317 | 12.6303 | 12.7605 | 12.9762 | 12.491 | 12.7553 | 12.5241 | 12.3803 | NaN | NaN | NaN | 12.6967 | 126.9002 | NaN | NaN | NaN | -4.0223 | NaN | NaN | NaN | NaN | 528.503 | NaN | 12.8475 | NaN | 19.7874
3866.1292 | 13.0049 | 12.5976 | 12.7686 | 13.0357 | 12.4325 | 12.7438 | 12.5133 | 12.386 | NaN | NaN | NaN | 12.7455 | 125.0897 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 529.4733 | NaN | 7.8551 | NaN | 26.6074
3867.1292 | 12.9106 | 12.5995 | 12.7736 | 13.014 | 12.5699 | 12.7154 | 12.5128 | 12.3845 | NaN | NaN | NaN | 12.6947 | 124.1141 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 530.798 | NaN | 8.3728 | NaN | 20.8916
3868.1292 | 12.9539 | 12.5912 | 12.7708 | 12.9952 | 12.5411 | 12.7212 | 12.5128 | 12.3817 | NaN | NaN | NaN | 12.7076 | 127.9631 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 530.4201 | NaN | 9.8613 | NaN | 27.9203
3869.1292 | 12.8898 | 12.6208 | 12.7737 | 12.9774 | 12.5514 | 12.7437 | 12.516 | 12.3911 | NaN | NaN | NaN | 12.7184 | 122.2777 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 530.4844 | NaN | 8.3373 | NaN | 19.9578
3870.1292 | 12.9057 | 12.5979 | 12.7693 | 13.052 | 12.4452 | 12.7264 | 12.5229 | 12.3879 | NaN | NaN | NaN | 12.6874 | 128.4813 | NaN | NaN | NaN | -16.662 | NaN | NaN | NaN | NaN | 529.7633 | NaN | 5.2895 | NaN | 24.7344
3871.1292 | 12.9175 | 12.7373 | 12.7713 | 12.97 | 12.5717 | 12.7967 | 12.5506 | 12.3868 | NaN | NaN | NaN | 12.7113 | 125.385 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 529.1021 | NaN | 6.9106 | NaN | 23.9283
3872.1292 | 12.9039 | 12.6176 | 12.7719 | 13.0089 | 12.5627 | 12.7242 | 12.5249 | 12.3873 | NaN | NaN | NaN | 12.7137 | 131.0912 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 527.5979 | NaN | 5.8443 | NaN | 17.9365
3873.1292 | 12.9074 | 12.6551 | 12.7684 | 12.9857 | 12.559 | 12.7374 | 12.5288 | 12.3898 | NaN | NaN | NaN | 12.7022 | 132.529 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 529.2362 | NaN | 24.1381 | NaN | 21.1446
3874.1292 | 12.917 | 12.5916 | 12.768 | 13.022 | 12.5088 | 12.711 | 12.5194 | 12.389 | NaN | NaN | NaN | 12.7705 | 121.1597 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 528.0386 | NaN | 5.8565 | NaN | 23.5486
3875.1292 | 12.9227 | 12.6208 | 12.7701 | 13.0396 | 12.4617 | 12.7308 | 12.525 | 12.3889 | NaN | NaN | NaN | 12.7017 | 124.3363 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 529.7878 | NaN | 42.0311 | NaN | 22.3883
3876.1292 | 12.9727 | 12.5919 | 12.7662 | 13.0143 | 12.5322 | 12.7099 | 12.5214 | 12.3895 | NaN | NaN | NaN | 12.7291 | 124.4262 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 528.3357 | NaN | 26.7534 | NaN | 26.4867
3877.1292 | 12.99 | 12.624 | 12.773 | 13.0049 | 12.5398 | 12.7165 | 12.5218 | 12.3873 | NaN | NaN | NaN | 12.755 | 134.9597 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 526.9298 | NaN | 4.8873 | NaN | 24.4474
3878.1292 | 12.938 | 12.6524 | 12.7671 | 13.0426 | 12.4598 | 12.7303 | 12.5249 | 12.3825 | NaN | NaN | NaN | 12.7178 | 123.3406 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 527.1878 | NaN | 33.5488 | NaN | 26.0593
3879.1292 | 13.0052 | 12.6812 | 12.7792 | 13.0096 | 12.5614 | 12.7408 | 12.5382 | 12.3906 | NaN | NaN | NaN | 12.7087 | 126.4207 | NaN | NaN | NaN | 2.3857 | NaN | NaN | NaN | NaN | 525.4109 | NaN | 5.3085 | NaN | 21.851
3880.1292 | 12.9273 | 12.6534 | 12.7802 | 12.9959 | 12.4928 | 12.7378 | 12.5364 | 12.3897 | NaN | NaN | NaN | 12.7383 | 133.8504 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 527.1211 | NaN | 40.5706 | NaN | 16.5337
3881.1292 | 12.9264 | 12.6012 | 12.7738 | 12.9988 | 12.5742 | 12.7137 | 12.5304 | 12.3903 | NaN | NaN | NaN | 12.7415 | 125.0003 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 529.6739 | NaN | 5.1932 | NaN | 24.7072
3882.1292 | 12.9405 | 12.6418 | 12.7705 | 13.0114 | 12.5666 | 12.7185 | 12.5429 | 12.3953 | NaN | NaN | NaN | 12.7556 | 128.2076 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 528.0201 | NaN | 43.1128 | NaN | 18.2904
3883.1292 | 12.9312 | 12.6416 | 12.7622 | 13.0096 | 12.5578 | 12.7238 | 12.537 | 12.3896 | NaN | NaN | NaN | 12.7497 | 128.4903 | NaN | NaN | NaN | 2.9453 | NaN | NaN | NaN | NaN | 528.1008 | NaN | 14.4025 | NaN | 17.4232
3884.1292 | 12.9381 | 12.591 | 12.7653 | 13.0107 | 12.5669 | 12.7154 | 12.5295 | 12.396 | NaN | NaN | NaN | 12.7597 | 125.2868 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 528.1263 | NaN | 6.8338 | NaN | 26.1383
3885.1292 | 12.9351 | 12.614 | 12.7661 | 13.0213 | 12.5667 | 12.7191 | 12.5251 | 12.3978 | NaN | NaN | NaN | 12.7717 | 115.7092 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 529.0957 | NaN | 8.0408 | NaN | 22.5733
3886.1604 | 12.9276 | 12.5936 | 12.7607 | 12.9806 | 12.5315 | 12.7137 | 12.5219 | 12.3986 | NaN | NaN | NaN | 12.7808 | 130.1776 | NaN | NaN | NaN | -0.915 | NaN | NaN | NaN | NaN | 532.6086 | NaN | 7.614 | NaN | 24.6635
3887.1292 | 12.9285 | 12.5627 | 12.7559 | 13.0149 | 12.5231 | 12.7089 | 12.5218 | 12.393 | NaN | NaN | NaN | 12.7617 | 125.2134 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 532.1905 | NaN | 7.4101 | NaN | 23.4306
3888.1292 | 12.9186 | 12.5767 | 12.7594 | 12.9886 | 12.5624 | 12.7195 | 12.5289 | 12.3999 | NaN | NaN | NaN | 12.7635 | 128.6343 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 533.4075 | NaN | 24.9536 | NaN | 17.1607
3889.1292 | 12.9176 | 12.5814 | 12.7474 | 12.9909 | 12.5659 | 12.7192 | 12.5288 | 12.4017 | NaN | NaN | NaN | 12.7854 | 118.8103 | NaN | NaN | NaN | -19.1029 | NaN | NaN | NaN | NaN | 532.5144 | NaN | 43.9214 | NaN | 21.6112
3890.1292 | 12.9214 | 12.5571 | 12.7474 | 13.0236 | 12.5573 | 12.7183 | 12.5331 | 12.4034 | NaN | NaN | NaN | 12.774 | 130.069 | NaN | NaN | NaN | -3.9638 | NaN | NaN | NaN | NaN | 532.6053 | NaN | 27.8388 | NaN | 20.4386
3891.1292 | 12.919 | 12.6573 | 12.7452 | 13.0102 | 12.5213 | 12.7517 | 12.5469 | 12.4046 | NaN | NaN | NaN | 12.7498 | 129.655 | NaN | NaN | NaN | 18.6072 | NaN | NaN | NaN | NaN | 531.5117 | NaN | 6.0868 | NaN | 26.1868
3892.1292 | 12.9151 | 12.6157 | 12.7456 | 13.075 | 12.5882 | 12.7308 | 12.5344 | 12.4174 | NaN | NaN | NaN | 12.7462 | 126.6979 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 534.795 | NaN | 35.029 | NaN | 20.7479
3893.1292 | 12.9123 | 12.5657 | 12.7471 | 12.9737 | 12.5799 | 12.7106 | 12.5276 | 12.4089 | NaN | NaN | NaN | 12.7534 | 121.9687 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 533.6285 | NaN | 5.9447 | NaN | 17.9964
3894.1292 | 12.9059 | 12.5781 | 12.7469 | 12.9969 | 12.5699 | 12.7271 | 12.5338 | 12.4091 | NaN | NaN | NaN | 12.7436 | 124.5842 | NaN | NaN | NaN | -2.4822 | NaN | NaN | NaN | NaN | 532.0966 | NaN | 38.6855 | NaN | 18.1835
3895.1292 | 12.8945 | 12.5526 | 12.746 | 12.9903 | 12.5395 | 12.7248 | 12.5291 | 12.4173 | NaN | NaN | NaN | 12.7366 | 129.7792 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 533.697 | NaN | 28.6906 | NaN | 25.6883
3896.1292 | 12.902 | 12.5375 | 12.7459 | 12.9763 | 12.5434 | 12.7216 | 12.528 | 12.4131 | NaN | NaN | NaN | 12.7269 | 126.5471 | NaN | NaN | NaN | -11.6571 | NaN | NaN | NaN | NaN | 533.2599 | NaN | 18.2099 | NaN | 27.1306
3897.1292 | 12.8992 | 12.5368 | 12.7462 | 12.9867 | 12.5354 | 12.7064 | 12.5284 | 12.4189 | NaN | NaN | NaN | 12.7518 | 132.6468 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 536.2423 | NaN | 10.749 | NaN | 20.422
3898.1292 | 12.904 | 12.5454 | 12.7426 | 13.0758 | 12.4845 | 12.7097 | 12.5211 | 12.4167 | NaN | NaN | NaN | 12.746 | 115.1602 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 536.3922 | NaN | 8.8839 | NaN | 17.6549
3899.1292 | 12.9141 | 12.5302 | 12.7415 | 13.0003 | 12.5648 | 12.7002 | 12.5198 | 12.4183 | NaN | NaN | NaN | 12.7432 | 121.4437 | NaN | NaN | NaN | -5.6914 | NaN | NaN | NaN | NaN | 534.5254 | NaN | 5.6528 | NaN | 24.9868
3900.1292 | 12.8947 | 12.5251 | 12.7514 | 13.0682 | 12.5654 | 12.708 | 12.5238 | 12.4165 | NaN | NaN | NaN | 12.7482 | 133.6754 | NaN | NaN | NaN | -2.7158 | NaN | NaN | NaN | NaN | 536.5832 | NaN | 23.8198 | NaN | 20.6375
3901.1292 | 12.9514 | 12.527 | 12.7459 | 12.9952 | 12.5811 | 12.7044 | 12.513 | 12.4196 | NaN | NaN | NaN | 12.7415 | 122.9533 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 536.771 | NaN | 6.9732 | NaN | 23.7766
3902.1292 | 12.9351 | 12.5231 | 12.7491 | 12.9745 | 12.5149 | 12.72 | 12.5241 | 12.4223 | NaN | NaN | NaN | 12.739 | 121.2643 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 540.8095 | NaN | 9.0545 | NaN | 27.2597
3903.1292 | 12.9604 | 12.55 | 12.7515 | 13.0249 | 12.4827 | 12.7305 | 12.5282 | 12.4149 | NaN | NaN | NaN | 12.7413 | 128.2494 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 537.6833 | NaN | 11.5627 | NaN | 22.7692
3904.1292 | 13.0745 | 12.5203 | 12.7442 | 12.9787 | 12.5319 | 12.722 | 12.519 | 12.4212 | NaN | NaN | NaN | 12.7297 | 124.6274 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 538.9779 | NaN | 8.6826 | NaN | 21.0836
3905.1292 | 12.9323 | 12.5071 | 12.7535 | 13.0223 | 12.5865 | 12.7132 | 12.5141 | 12.4214 | NaN | NaN | NaN | 12.749 | 121.5318 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 540.0494 | NaN | 7.0922 | NaN | 24.761
3906.1292 | 12.9285 | 12.5036 | 12.7499 | 13.0056 | 12.5331 | 12.7194 | 12.5254 | 12.4279 | NaN | NaN | NaN | 12.7631 | 123.969 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 541.0072 | NaN | 6.5148 | NaN | 22.5856
3907.1292 | 12.9398 | 12.5104 | 12.752 | 12.9828 | 12.5366 | 12.7133 | 12.5155 | 12.4209 | NaN | NaN | NaN | 12.7401 | 126.6666 | NaN | NaN | NaN | -14.8253 | NaN | NaN | NaN | NaN | 542.126 | NaN | 19.9036 | NaN | 21.4672
3908.1292 | 13.005 | 12.5043 | 12.7521 | 13.0242 | 12.5388 | 12.7139 | 12.5184 | 12.4245 | NaN | NaN | NaN | 12.7311 | 130.6603 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 538.756 | NaN | 32.5551 | NaN | 21.5087
3909.1292 | 12.9284 | 12.4983 | 12.747 | 13.0199 | 12.5732 | 12.7129 | 12.5189 | 12.4281 | NaN | NaN | NaN | 12.7683 | 131.1607 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 540.8446 | NaN | 4.0819 | NaN | 29.5788
3910.1292 | 12.9213 | 12.4811 | 12.7499 | 13.0034 | 12.4958 | 12.7038 | 12.5113 | 12.4274 | NaN | NaN | NaN | 12.7166 | 129.2362 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 543.4 | NaN | 4.7202 | NaN | 26.7981
3911.1292 | 12.9299 | 12.5272 | 12.7571 | 13.0028 | 12.5042 | 12.7418 | 12.5254 | 12.4255 | NaN | NaN | NaN | 12.7035 | 122.2299 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 541.4394 | NaN | 5.1683 | NaN | 22.7979
3912.1292 | 12.9236 | 12.5693 | 12.7512 | 13.0191 | 12.5136 | 12.7414 | 12.531 | 12.4235 | NaN | NaN | NaN | 12.7814 | 119.4482 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 541.1678 | NaN | 33.2315 | NaN | 23.1596
3913.1292 | 12.9278 | 12.5557 | 12.7529 | 12.989 | 12.4649 | 12.7371 | 12.5314 | 12.4199 | NaN | NaN | NaN | 12.7019 | 123.8241 | NaN | NaN | NaN | -2.6855 | NaN | NaN | NaN | NaN | 541.0164 | NaN | 8.9667 | NaN | 26.7874
3914.1292 | 12.9032 | 12.527 | 12.7466 | 13.0002 | 12.5976 | 12.7216 | 12.5254 | 12.4325 | NaN | NaN | NaN | 12.7312 | 119.6533 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 541.7501 | NaN | 4.4951 | NaN | 27.6218
3915.1292 | 13.0792 | 12.4937 | 12.7589 | 13.0251 | 12.5343 | 12.701 | 12.521 | 12.4281 | NaN | NaN | NaN | 12.7125 | 127.7667 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 540.7598 | NaN | 32.1754 | NaN | 23.2195
3916.1448 | 12.9263 | 12.4892 | 12.7506 | 13.0253 | 12.5404 | 12.6998 | 12.5227 | 12.4254 | NaN | NaN | NaN | 12.7497 | 128.6906 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 540.4061 | NaN | 7.5825 | NaN | 23.5065
3917.1292 | 12.9342 | 12.5248 | 12.758 | 12.9991 | 12.5431 | 12.7122 | 12.5265 | 12.43 | NaN | NaN | NaN | 12.723 | 122.4925 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 538.499 | NaN | 10.7498 | NaN | 24.2248
3918.1292 | 12.8953 | 12.5501 | 12.7538 | 13.0395 | 12.4618 | 12.7416 | 12.5216 | 12.4248 | NaN | NaN | NaN | 12.7329 | 119.2781 | NaN | NaN | NaN | -5.6982 | NaN | NaN | NaN | NaN | 537.7967 | NaN | 6.7665 | NaN | 18.7082
3919.1292 | 12.9966 | 12.4925 | 12.7558 | 13.0339 | 12.4753 | 12.7057 | 12.5167 | 12.429 | NaN | NaN | NaN | 12.7196 | 124.1695 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 539.9267 | NaN | 5.23 | NaN | 20.2321
3920.1292 | 12.9543 | 12.5222 | 12.7548 | 13.0488 | 12.5983 | 12.7027 | 12.52 | 12.4275 | NaN | NaN | NaN | 12.7167 | 114.4853 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 539.919 | NaN | 3.9972 | NaN | 20.6226
3921.1292 | 12.9547 | 12.5007 | 12.7494 | 12.9834 | 12.5083 | 12.6981 | 12.5151 | 12.4229 | NaN | NaN | NaN | 12.7333 | 117.0015 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 540.977 | NaN | 10.1226 | NaN | 10.9459
3922.1292 | 12.9166 | 12.5084 | 12.7514 | 13.0293 | 12.5394 | 12.6996 | 12.5188 | 12.421 | NaN | NaN | NaN | 12.7417 | 121.6047 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 537.3716 | NaN | 18.1988 | NaN | 14.044
3923.1292 | 12.9057 | 12.5394 | 12.7507 | 13.0038 | 12.5687 | 12.7207 | 12.5243 | 12.4251 | NaN | NaN | NaN | 12.7205 | 119.1832 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 536.6168 | NaN | 9.8469 | NaN | 26.4213
3924.1292 | 12.8914 | 12.5502 | 12.7519 | 12.9967 | 12.5332 | 12.7161 | 12.519 | 12.4218 | NaN | NaN | NaN | 12.7274 | 129.6904 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 538.8524 | NaN | 8.9942 | NaN | 24.5936
3925.1292 | 13.0088 | 12.5285 | 12.7482 | 13.0323 | 12.508 | 12.715 | 12.516 | 12.4178 | NaN | NaN | NaN | 12.8272 | 121.8209 | NaN | NaN | NaN | -17.8772 | NaN | NaN | NaN | NaN | 536.121 | NaN | 23.4451 | NaN | 27.2359
3926.1292 | 12.917 | 12.5274 | 12.7465 | 13.0199 | 12.5758 | 12.7064 | 12.5182 | 12.4147 | NaN | NaN | NaN | 12.7535 | 129.561 | NaN | NaN | NaN | 4.3669 | NaN | NaN | NaN | NaN | 538.067 | NaN | 5.8084 | NaN | 25.1356
3927.1292 | 13.0369 | 12.5569 | 12.7457 | 13.0028 | 12.4797 | 12.7085 | 12.5188 | 12.4187 | NaN | NaN | NaN | 12.6904 | 121.8657 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 536.8677 | NaN | 16.7152 | NaN | 25.954
3928.1292 | 12.9475 | 12.5159 | 12.747 | 13.0117 | 12.571 | 12.698 | 12.511 | 12.424 | NaN | NaN | NaN | 12.7387 | 124.7534 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 539.787 | NaN | 5.749 | NaN | 15.718
3929.1292 | 12.9221 | 12.5364 | 12.7429 | 13.0696 | 12.5416 | 12.7166 | 12.5198 | 12.4194 | NaN | NaN | NaN | 12.7294 | 123.5166 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 537.9711 | NaN | 32.6319 | NaN | 26.993
3930.1292 | 12.9177 | 12.537 | 12.7435 | 13.0025 | 12.5911 | 12.7168 | 12.5146 | 12.4193 | NaN | NaN | NaN | 12.7175 | 127.0805 | NaN | NaN | NaN | 4.5607 | NaN | NaN | NaN | NaN | 535.4221 | NaN | 4.8368 | NaN | 22.5899
3931.1292 | 12.9059 | 12.5485 | 12.7438 | 13.0286 | 12.511 | 12.728 | 12.5154 | 12.4177 | NaN | NaN | NaN | 12.6973 | 132.551 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 535.9344 | NaN | 5.0049 | NaN | 20.9066
3932.1292 | 12.9022 | 12.5861 | 12.7434 | 13.0051 | 12.5825 | 12.7287 | 12.5232 | 12.4195 | NaN | NaN | NaN | 12.7039 | 120.0375 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 534.9316 | NaN | 6.3762 | NaN | 25.9583
3933.1292 | 12.8755 | 12.571 | 12.7399 | 13.0709 | 12.4698 | 12.7496 | 12.5222 | 12.4195 | NaN | NaN | NaN | 12.7022 | 126.5369 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 534.3938 | NaN | 32.3812 | NaN | 24.4198
3934.1292 | 12.8896 | 12.5563 | 12.7382 | 13.049 | 12.594 | 12.7232 | 12.508 | 12.4157 | NaN | NaN | NaN | 12.7125 | 129.5657 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 531.2225 | NaN | 8.0556 | NaN | 15.1612
3935.1292 | 12.897 | 12.5663 | 12.7428 | 13.0352 | 12.5161 | 12.7408 | 12.5139 | 12.4183 | NaN | NaN | NaN | 12.7693 | 126.6088 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 533.9452 | NaN | 27.2009 | NaN | 24.9986
3936.1292 | 12.8912 | 12.578 | 12.7423 | 13.0037 | 12.5892 | 12.7413 | 12.5118 | 12.4207 | NaN | NaN | NaN | 12.6949 | 131.098 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 533.1862 | NaN | 5.1757 | NaN | 24.5337
3937.1292 | 13.0188 | 12.5352 | 12.7401 | 13.0504 | 12.6039 | 12.7179 | 12.4971 | 12.4149 | NaN | NaN | NaN | 12.7079 | 122.8162 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 532.3393 | NaN | 6.2831 | NaN | 25.7239
3938.1292 | 12.929 | 12.5327 | 12.7421 | 13.0672 | 12.5403 | 12.7196 | 12.4942 | 12.4251 | NaN | NaN | NaN | 12.7042 | 118.1676 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 530.85 | NaN | 5.8254 | NaN | 21.9198
3939.1292 | 12.9352 | 12.5501 | 12.7457 | 13.0212 | 12.5014 | 12.728 | 12.4901 | 12.4251 | NaN | NaN | NaN | 12.7295 | 127.73 | NaN | NaN | NaN | -12.9327 | NaN | NaN | NaN | NaN | 531.7427 | NaN | 4.7682 | NaN | 26.8201
3940.1292 | 12.9084 | 12.5727 | 12.7489 | 13.0127 | 12.4729 | 12.7494 | 12.4996 | 12.4154 | NaN | NaN | NaN | 12.7323 | 121.6798 | NaN | NaN | NaN | 0.376 | NaN | NaN | NaN | NaN | 532.5198 | NaN | 5.538 | NaN | 25.2447
3941.1292 | 12.9056 | 12.5389 | 12.7483 | 13.0674 | 12.5871 | 12.7177 | 12.4934 | 12.4251 | NaN | NaN | NaN | 12.6909 | 126.3435 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 529.0433 | NaN | 10.5335 | NaN | 26.7786
3942.1292 | 12.9028 | 12.5665 | 12.7498 | 13.1023 | 12.6022 | 12.7315 | 12.4924 | 12.4197 | NaN | NaN | NaN | 12.7139 | 130.3841 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 527.9317 | NaN | 13.513 | NaN | 22.063
3943.1292 | 12.8949 | 12.5612 | 12.751 | 13.0071 | 12.5909 | 12.7405 | 12.4971 | 12.4108 | NaN | NaN | NaN | 12.7231 | 136.7532 | NaN | NaN | NaN | 2.4462 | NaN | NaN | NaN | NaN | 527.2195 | NaN | 5.8602 | NaN | 21.611
3944.1292 | 12.8844 | 12.6124 | 12.7505 | 13.0398 | 12.5849 | 12.7719 | 12.5161 | 12.4191 | NaN | NaN | NaN | 12.745 | 128.7261 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 528.1027 | NaN | 6.6517 | NaN | 18.4362
3945.1292 | 12.8912 | 12.5448 | 12.7508 | 13.0101 | 12.5168 | 12.731 | 12.4984 | 12.4157 | NaN | NaN | NaN | 12.7192 | 120.1399 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 526.9974 | NaN | 12.8464 | NaN | 27.6401
3946.1292 | 12.8876 | 12.5581 | 12.7558 | 13.0728 | 12.5216 | 12.7367 | 12.4979 | 12.4116 | NaN | NaN | NaN | 12.7325 | 127.9978 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 525.8172 | NaN | 10.8945 | NaN | 25.0102
3947.1292 | 12.9571 | 12.6044 | 12.7561 | 13.0383 | 12.5992 | 12.7571 | 12.5082 | 12.4178 | NaN | NaN | NaN | 12.734 | 121.9826 | NaN | NaN | NaN | -10.4715 | NaN | NaN | NaN | NaN | 520.8916 | NaN | 5.3025 | NaN | 21.5869
3948.1292 | 12.9075 | 12.5733 | 12.7543 | 13.0753 | 12.5062 | 12.733 | 12.5059 | 12.4134 | NaN | NaN | NaN | 12.7214 | 120.2885 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 523.3134 | NaN | 6.1736 | NaN | 24.4322
3949.1292 | 12.8942 | 12.6444 | 12.7658 | 13.0369 | 12.5714 | 12.761 | 12.5226 | 12.4122 | NaN | NaN | NaN | 12.7074 | 120.9363 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 519.6897 | NaN | 4.2206 | NaN | 25.3652
3950.1292 | 12.8908 | 12.5723 | 12.7617 | 13.0877 | 12.4738 | 12.745 | 12.514 | 12.4074 | NaN | NaN | NaN | 12.7231 | 132.0418 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 522.0498 | NaN | 4.7076 | NaN | 25.8631
3951.1292 | 12.9345 | 12.5946 | 12.7641 | 13.0782 | 12.4654 | 12.755 | 12.5109 | 12.4099 | NaN | NaN | NaN | 12.7064 | 125.6227 | NaN | NaN | NaN | -10.058 | NaN | NaN | NaN | NaN | 523.3873 | NaN | 8.6755 | NaN | 25.7036
3952.1292 | 12.9205 | 12.6411 | 12.7608 | 13.0463 | 12.5736 | 12.7484 | 12.5162 | 12.4157 | NaN | NaN | NaN | 12.7299 | 131.1127 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 520.9776 | NaN | 10.9535 | NaN | 20.0266
3953.1292 | 12.9087 | 12.6186 | 12.7648 | 13.0217 | 12.4885 | 12.7521 | 12.5066 | 12.4139 | NaN | NaN | NaN | 12.7365 | 119.9524 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 525.069 | NaN | 4.8479 | NaN | 18.3894
3954.1292 | 12.9183 | 12.6155 | 12.7648 | 13.0255 | 12.5904 | 12.7461 | 12.5171 | 12.4088 | NaN | NaN | NaN | 12.735 | 130.1292 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 524.8096 | NaN | 14.0241 | NaN | 24.8704
3955.1292 | 12.9022 | 12.587 | 12.7656 | 13.049 | 12.5312 | 12.7337 | 12.5194 | 12.4109 | NaN | NaN | NaN | 12.7595 | 122.4712 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 525.481 | NaN | 21.0013 | NaN | 27.2647
3956.1292 | 12.9113 | 12.6872 | 12.7721 | 13.0357 | 12.5689 | 12.7898 | 12.5402 | 12.4097 | NaN | NaN | NaN | 12.7698 | 120.4478 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 524.0618 | NaN | 7.9016 | NaN | 21.3298
3957.1292 | 12.9172 | 12.6705 | 12.7671 | 13.028 | 12.4641 | 12.7718 | 12.5373 | 12.4112 | NaN | NaN | NaN | 12.7213 | 123.9882 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 522.5836 | NaN | 5.0558 | NaN | 26.3391
3958.1292 | 12.9176 | 12.5864 | 12.7629 | 13.0513 | 12.5143 | 12.7216 | 12.5147 | 12.4075 | NaN | NaN | NaN | 12.7329 | 114.5476 | NaN | NaN | NaN | 0.209 | NaN | NaN | NaN | NaN | 520.5791 | NaN | 29.3411 | NaN | 27.7245
3959.1292 | 12.8761 | 12.6087 | 12.7613 | 13.0358 | 12.5991 | 12.7272 | 12.5155 | 12.397 | NaN | NaN | NaN | 12.7604 | 123.5996 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 521.1718 | NaN | 15.4948 | NaN | 26.6613
3960.1292 | 12.9484 | 12.6583 | 12.7663 | 13.0594 | 12.6158 | 12.7594 | 12.5272 | 12.4061 | NaN | NaN | NaN | 12.7506 | 112.0852 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 521.5171 | NaN | 3.8224 | NaN | 25.4213
3961.1292 | 12.9535 | 12.5856 | 12.7697 | 13.0135 | 12.5128 | 12.7382 | 12.5127 | 12.3993 | NaN | NaN | NaN | 12.7708 | 125.8814 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 521.1685 | NaN | 11.8709 | NaN | 20.784
3962.1292 | 12.8972 | 12.6135 | 12.7723 | 13.04 | 12.5858 | 12.7497 | 12.5151 | 12.3943 | NaN | NaN | NaN | 12.7538 | 122.9658 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 521.439 | NaN | 30.8445 | NaN | 19.1648
3963.1292 | 12.9051 | 12.6681 | 12.7699 | 13.0185 | 12.5834 | 12.7632 | 12.5187 | 12.3954 | NaN | NaN | NaN | 12.7791 | 128.5426 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 523.5187 | NaN | 5.3925 | NaN | 19.7951
3964.1292 | 12.9657 | 12.6084 | 12.7722 | 13.0527 | 12.5021 | 12.7485 | 12.5176 | 12.3953 | NaN | NaN | NaN | 12.7522 | 121.0942 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 521.6333 | NaN | 5.209 | NaN | 25.9936
3965.1292 | 12.8884 | 12.6345 | 12.7671 | 13.064 | 12.6097 | 12.769 | 12.5249 | 12.3985 | NaN | NaN | NaN | 12.75 | 120.2307 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 522.0215 | NaN | 22.6866 | NaN | 24.7076
3966.1292 | 12.9345 | 12.6718 | 12.7679 | 13.0548 | 12.4869 | 12.7848 | 12.5374 | 12.3943 | NaN | NaN | NaN | 12.747 | 126.7652 | NaN | NaN | NaN | -10.8252 | NaN | NaN | NaN | NaN | 522.3545 | NaN | 3.9171 | NaN | 26.6216
3967.1292 | 12.8988 | 12.5855 | 12.7715 | 13.0418 | 12.5607 | 12.7424 | 12.5293 | 12.398 | NaN | NaN | NaN | 12.8067 | 130.0641 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 520.3485 | NaN | 26.1355 | NaN | 25.7534
3968.1292 | 12.9061 | 12.612 | 12.7696 | 13.0617 | 12.5864 | 12.7366 | 12.5255 | 12.3989 | NaN | NaN | NaN | 12.7467 | 123.8344 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 519.8362 | NaN | 9.8146 | NaN | 18.0799
3969.1292 | 12.8919 | 12.6152 | 12.7664 | 13.054 | 12.5345 | 12.7501 | 12.5304 | 12.3988 | NaN | NaN | NaN | 12.7734 | 127.0915 | NaN | NaN | NaN | -0.1892 | NaN | NaN | NaN | NaN | 518.1247 | NaN | 3.7923 | NaN | 25.9109
3970.1292 | 12.9853 | 12.7414 | 12.7702 | 13.1024 | 12.5818 | 12.796 | 12.5557 | 12.3957 | NaN | NaN | NaN | 12.7319 | 119.7699 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 519.0554 | NaN | 20.0929 | NaN | 22.0981
3971.1292 | 12.8893 | 12.6419 | 12.7716 | 13.0399 | 12.5915 | 12.7351 | 12.5254 | 12.3952 | NaN | NaN | NaN | 12.8001 | 125.2756 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.2685 | NaN | 33.7365 | NaN | 19.6231
3972.1292 | 12.9485 | 12.6159 | 12.7638 | 13.0438 | 12.5606 | 12.7304 | 12.5211 | 12.3993 | NaN | NaN | NaN | 12.7989 | 116.7231 | NaN | NaN | NaN | -19.1818 | NaN | NaN | NaN | NaN | 518.9976 | NaN | 8.256 | NaN | 25.7127
3973.1292 | 12.9092 | 12.6887 | 12.7688 | 13.0381 | 12.5379 | 12.7674 | 12.5361 | 12.4048 | NaN | NaN | NaN | 12.7562 | 121.7058 | NaN | NaN | NaN | 1.1553 | NaN | NaN | NaN | NaN | 517.4909 | NaN | 7.9359 | NaN | 27.2397
3974.1292 | 12.9259 | 12.6303 | 12.7622 | 12.9988 | 12.5453 | 12.7378 | 12.5185 | 12.4082 | NaN | NaN | NaN | 12.7768 | 130.2004 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 517.1814 | NaN | 10.1394 | NaN | 26.6806
3975.1292 | 12.9083 | 12.5843 | 12.7608 | 13.0487 | 12.5614 | 12.7202 | 12.5143 | 12.4046 | NaN | NaN | NaN | 12.7596 | 119.3246 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.1062 | NaN | 8.297 | NaN | 24.1422
3976.1292 | 12.8882 | 12.6381 | 12.7571 | 13.0347 | 12.5262 | 12.7437 | 12.5292 | 12.405 | NaN | NaN | NaN | 12.73 | 123.5831 | NaN | NaN | NaN | -1.0239 | NaN | NaN | NaN | NaN | 517.5955 | NaN | 21.2669 | NaN | 21.5325
3977.1292 | 12.8862 | 12.6534 | 12.7621 | 13.1382 | 12.5512 | 12.7244 | 12.5239 | 12.4007 | NaN | NaN | NaN | 12.7593 | 122.3233 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 513.8832 | NaN | 35.145 | NaN | 25.0678
3978.1292 | 12.8955 | 12.6075 | 12.7582 | 13.0349 | 12.528 | 12.7193 | 12.5262 | 12.4106 | NaN | NaN | NaN | 12.7897 | 131.0169 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.8214 | NaN | 5.2701 | NaN | 12.6526
3979.1292 | 12.9323 | 12.6143 | 12.7509 | 13.0188 | 12.5697 | 12.7218 | 12.5214 | 12.4096 | NaN | NaN | NaN | 12.7333 | 121.3078 | NaN | NaN | NaN | -5.8328 | NaN | NaN | NaN | NaN | 518.3504 | NaN | 7.7986 | NaN | 26.4829
3980.1292 | 12.8936 | 12.604 | 12.7528 | 13.0569 | 12.4928 | 12.7113 | 12.5211 | 12.4083 | NaN | NaN | NaN | 12.782 | 114.4966 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.866 | NaN | 5.8996 | NaN | 14.4104
3981.1292 | 12.9306 | 12.6603 | 12.7454 | 13.0295 | 12.5212 | 12.7354 | 12.5266 | 12.41 | NaN | NaN | NaN | 12.7209 | 121.8913 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.5306 | NaN | 27.9146 | NaN | 23.4159
3982.1292 | 12.9534 | 12.6714 | 12.7455 | 13.0499 | 12.5793 | 12.7288 | 12.5255 | 12.4101 | NaN | NaN | NaN | 12.7353 | 134.0104 | NaN | NaN | NaN | -18.048 | NaN | NaN | NaN | NaN | 518.5961 | NaN | 7.4084 | NaN | 13.1966
3983.1292 | 12.9152 | 12.6127 | 12.7541 | 13.0961 | 12.6108 | 12.7321 | 12.5252 | 12.4101 | NaN | NaN | NaN | 12.7744 | 117.1467 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 519.3867 | NaN | 6.4507 | NaN | 26.8188
3984.1292 | 12.9011 | 12.6341 | 12.7454 | 13.0545 | 12.4942 | 12.7285 | 12.5304 | 12.4131 | NaN | NaN | NaN | 12.7596 | 120.4789 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 519.6343 | NaN | 9.5283 | NaN | 25.2197
3985.1292 | 12.8999 | 12.6188 | 12.7452 | 13.0946 | 12.5687 | 12.734 | 12.5235 | 12.4124 | NaN | NaN | NaN | 12.7961 | 126.7131 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.6214 | NaN | 5.1848 | NaN | 23.7596
3986.1292 | 12.902 | 12.62 | 12.7351 | 13.0607 | 12.5648 | 12.7363 | 12.5232 | 12.4033 | NaN | NaN | NaN | 12.7543 | 126.6294 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 516.9013 | NaN | 24.7597 | NaN | 26.9087
3987.1292 | 12.8929 | 12.6419 | 12.7426 | 13.055 | 12.5052 | 12.7523 | 12.5323 | 12.4136 | NaN | NaN | NaN | 12.7481 | 120.6255 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 517.2985 | NaN | 6.5136 | NaN | 16.192
3988.1292 | 12.8902 | 12.6177 | 12.7381 | 13.0484 | 12.5876 | 12.7247 | 12.5193 | 12.4158 | NaN | NaN | NaN | 12.7802 | 120.3779 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 516.8161 | NaN | 26.3084 | NaN | 24.4927
3989.1292 | 12.8845 | 12.6791 | 12.7425 | 13.0442 | 12.535 | 12.7909 | 12.5356 | 12.4157 | NaN | NaN | NaN | 12.7626 | 129.7919 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 517.6584 | NaN | 4.9301 | NaN | 26.9533
3990.1292 | 12.8875 | 12.6199 | 12.7429 | 13.0599 | 12.5647 | 12.7374 | 12.5248 | 12.4103 | NaN | NaN | NaN | 12.7573 | 125.2135 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 517.2242 | NaN | 25.4659 | NaN | 20.472
3991.1292 | 12.8867 | 12.6609 | 12.7425 | 13.0785 | 12.5643 | 12.7379 | 12.5256 | 12.4085 | NaN | NaN | NaN | 12.76 | 124.7221 | NaN | NaN | NaN | -1.3753 | NaN | NaN | NaN | NaN | 516.2423 | NaN | 10.193 | NaN | 22.4994
3992.1292 | 12.8919 | 12.6087 | 12.7446 | 13.058 | 12.5433 | 12.7267 | 12.5165 | 12.4142 | NaN | NaN | NaN | 12.7497 | 125.7164 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 516.9096 | NaN | 6.0835 | NaN | 26.4101
3993.1292 | 12.8875 | 12.6563 | 12.74 | 13.041 | 12.5453 | 12.7571 | 12.5331 | 12.4108 | NaN | NaN | NaN | 12.7594 | 129.6659 | NaN | NaN | NaN | -15.2389 | NaN | NaN | NaN | NaN | 518.3365 | NaN | 4.0434 | NaN | 29.0908
3994.1292 | 12.8739 | 12.617 | 12.7393 | 13.0267 | 12.5623 | 12.7359 | 12.5295 | 12.4139 | NaN | NaN | NaN | 12.7422 | 124.5432 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.7908 | NaN | 8.5409 | NaN | 23.9195
3995.1292 | 12.8683 | 12.6445 | 12.7459 | 13.0285 | 12.5524 | 12.7554 | 12.5478 | 12.4133 | NaN | NaN | NaN | 12.787 | 128.8855 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 519.3687 | NaN | 12.5022 | NaN | 16.7551
3996.1292 | 12.9034 | 12.6124 | 12.7435 | 13.0524 | 12.5424 | 12.7361 | 12.5295 | 12.4067 | NaN | NaN | NaN | 12.7531 | 126.3596 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.4412 | NaN | 16.5428 | NaN | 28.7293
3997.1292 | 12.8865 | 12.6372 | 12.7488 | 13.0529 | 12.5417 | 12.7571 | 12.5447 | 12.4112 | NaN | NaN | NaN | 12.793 | 129.4871 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 519.3461 | NaN | 14.8303 | NaN | 23.2078
3998.1292 | 12.8819 | 12.6445 | 12.7456 | 13.0402 | 12.5393 | 12.7435 | 12.5456 | 12.4028 | NaN | NaN | NaN | 12.7633 | 118.0037 | NaN | NaN | NaN | -4.2461 | NaN | NaN | NaN | NaN | 520.6072 | NaN | 17.8562 | NaN | 20.9362
3999.1292 | 12.881 | 12.6892 | 12.7504 | 13.0443 | 12.5882 | 12.7626 | 12.5383 | 12.4062 | NaN | NaN | NaN | 12.7801 | 129.6842 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 517.9362 | NaN | 29.7607 | NaN | 27.9709
4000.1292 | 12.8856 | 12.6704 | 12.7481 | 12.9912 | 12.4669 | 12.7868 | 12.5522 | 12.4061 | NaN | NaN | NaN | 12.7711 | 126.3974 | NaN | NaN | NaN | -4.1237 | NaN | NaN | NaN | NaN | 518.1185 | NaN | 3.2059 | NaN | 23.7046
4001.1292 | 12.8905 | 12.6853 | 12.7482 | 13.0402 | 12.5839 | 12.7733 | 12.5537 | 12.4093 | NaN | NaN | NaN | 12.7769 | 132.0055 | NaN | NaN | NaN | 3.7329 | NaN | NaN | NaN | NaN | 515.1298 | NaN | 4.9675 | NaN | 21.8778
4002.1292 | 12.8958 | 12.626 | 12.7526 | 13.0223 | 12.4957 | 12.7621 | 12.5414 | 12.4045 | NaN | NaN | NaN | 12.7696 | 128.3721 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 515.0915 | NaN | 7.037 | NaN | 17.9425
4003.1292 | 12.8529 | 12.6282 | 12.7493 | 13.0527 | 12.521 | 12.76 | 12.5316 | 12.396 | NaN | NaN | NaN | 12.7455 | 114.5392 | NaN | NaN | NaN | 10.4551 | NaN | NaN | NaN | NaN | 514.9086 | NaN | 8.4194 | NaN | 25.945
4004.1292 | 12.978 | 12.5925 | 12.7498 | 13.0205 | 12.5762 | 12.7448 | 12.5315 | 12.3984 | NaN | NaN | NaN | 12.7463 | 131.0107 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 517.1539 | NaN | 5.2115 | NaN | 28.1973
4005.1292 | 12.8897 | 12.6089 | 12.7562 | 13.0107 | 12.5327 | 12.7648 | 12.5369 | 12.4005 | NaN | NaN | NaN | 12.7453 | 113.1066 | NaN | NaN | NaN | 15.9497 | NaN | NaN | NaN | NaN | 512.4835 | NaN | 7.077 | NaN | 25.7425
4006.1292 | 12.8875 | 12.6537 | 12.7527 | 13.0339 | 12.5356 | 12.7751 | 12.541 | 12.4044 | NaN | NaN | NaN | 12.7592 | 123.8145 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 501.8992 | NaN | 19.3322 | NaN | 25.4165
4007.1292 | 12.8809 | 12.614 | 12.7565 | 13.0518 | 12.5738 | 12.7455 | 12.5279 | 12.4033 | NaN | NaN | NaN | 12.7516 | 124.8306 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 499.613 | NaN | 11.9 | NaN | 25.7808
4008.1292 | 12.8692 | 12.6001 | 12.7494 | 13.0144 | 12.565 | 12.7439 | 12.5294 | 12.4064 | NaN | NaN | NaN | 12.7879 | 126.259 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 501.3528 | NaN | 10.3029 | NaN | 25.1098
4009.1292 | 12.8421 | 12.6073 | 12.7549 | 13.0106 | 12.5154 | 12.7356 | 12.5227 | 12.4038 | NaN | NaN | NaN | 12.802 | 127.984 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 506.6633 | NaN | 4.601 | NaN | 25.3836
4010.1292 | 12.8726 | 12.604 | 12.7476 | 12.9687 | 12.5016 | 12.7482 | 12.5342 | 12.4069 | NaN | NaN | NaN | 12.7646 | 117.7384 | NaN | NaN | NaN | 2.4147 | NaN | NaN | NaN | NaN | 510.7438 | NaN | 4.5661 | NaN | 20.1197
4011.1292 | 12.8866 | 12.6051 | 12.7527 | 13.0224 | 12.564 | 12.7405 | 12.5243 | 12.4027 | NaN | NaN | NaN | 12.7463 | 127.4 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 512.5214 | NaN | 20.5755 | NaN | 23.439
4012.1292 | 12.8814 | 12.6237 | 12.7553 | 13.0153 | 12.5948 | 12.7462 | 12.5315 | 12.402 | NaN | NaN | NaN | 12.7611 | 125.442 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 511.9498 | NaN | 13.7228 | NaN | 24.6463
4013.1292 | 12.8716 | 12.6281 | 12.7535 | 13.0356 | 12.5402 | 12.7525 | 12.5327 | 12.3961 | NaN | NaN | NaN | 12.7819 | 122.1781 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 508.5643 | NaN | 6.2439 | NaN | 23.5621
4014.1292 | 12.8775 | 12.6549 | 12.7543 | 13.0317 | 12.5828 | 12.7531 | 12.5309 | 12.3967 | NaN | NaN | NaN | 12.7376 | 131.1224 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 509.9245 | NaN | 17.5966 | NaN | 25.5241
4015.1292 | 12.8738 | 12.6202 | 12.754 | 13.0185 | 12.572 | 12.7671 | 12.5337 | 12.393 | NaN | NaN | NaN | 12.7636 | 113.0386 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 510.506 | NaN | 6.5334 | NaN | 24.0712
4016.1292 | 12.8754 | 12.6888 | 12.7551 | 13.0187 | 12.5757 | 12.7985 | 12.5544 | 12.3918 | NaN | NaN | NaN | 12.738 | 121.1517 | NaN | NaN | NaN | 3.5921 | NaN | NaN | NaN | NaN | 510.4759 | NaN | 6.3044 | NaN | 25.4525
4017.1292 | 12.8704 | 12.5929 | 12.7534 | 12.9988 | 12.5034 | 12.7472 | 12.5207 | 12.3853 | NaN | NaN | NaN | 12.748 | 126.8678 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 509.8644 | NaN | 8.4304 | NaN | 25.6635
4018.1292 | 12.8749 | 12.5805 | 12.7534 | 13.0494 | 12.5418 | 12.7366 | 12.5174 | 12.3867 | NaN | NaN | NaN | 12.7759 | 127.7996 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 511.4979 | NaN | 5.5228 | NaN | 28.0967
4019.1292 | 12.8724 | 12.6327 | 12.7485 | 13.004 | 12.568 | 12.7645 | 12.5273 | 12.3819 | NaN | NaN | NaN | 12.7493 | 126.1423 | NaN | NaN | NaN | 8.2634 | NaN | NaN | NaN | NaN | 509.2349 | NaN | 7.7914 | NaN | 26.5442
4020.1292 | 12.8527 | 12.6091 | 12.7574 | 13.0787 | 12.5592 | 12.7555 | 12.5292 | 12.3762 | NaN | NaN | NaN | 12.7792 | 121.0689 | NaN | NaN | NaN | -10.5108 | NaN | NaN | NaN | NaN | 509.804 | NaN | 4.8742 | NaN | 26.2439
4021.1292 | 12.8515 | 12.6029 | 12.7567 | 13.0265 | 12.5396 | 12.7655 | 12.5283 | 12.3705 | NaN | NaN | NaN | 12.8436 | 127.455 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 506.6187 | NaN | 11.0712 | NaN | 20.9318
4022.1292 | 12.9245 | 12.6201 | 12.7532 | 13.0167 | 12.6146 | 12.7567 | 12.5226 | 12.3798 | NaN | NaN | NaN | 12.762 | 129.7279 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 509.2756 | NaN | 6.5398 | NaN | 25.3955
4023.1292 | 12.8695 | 12.6028 | 12.7535 | 12.966 | 12.5603 | 12.763 | 12.5168 | 12.3759 | NaN | NaN | NaN | 12.7633 | 125.9146 | NaN | NaN | NaN | 1.2903 | NaN | NaN | NaN | NaN | 511.0528 | NaN | 5.588 | NaN | 26.8307
4024.1292 | 12.8618 | 12.5966 | 12.7566 | 13.0084 | 12.5798 | 12.7479 | 12.5208 | 12.3758 | NaN | NaN | NaN | 12.7604 | 124.9425 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 509.362 | NaN | 5.2424 | NaN | 20.7581
4025.1292 | 12.8636 | 12.588 | 12.7542 | 12.9913 | 12.5932 | 12.7389 | 12.5129 | 12.3744 | NaN | NaN | NaN | 12.7695 | 123.7943 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 511.2957 | NaN | 5.2934 | NaN | 26.8601
4026.1292 | 12.8707 | 12.6323 | 12.7506 | 13.0194 | 12.4715 | 12.7852 | 12.5363 | 12.373 | NaN | NaN | NaN | 12.7542 | 130.5663 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 512.0348 | NaN | 4.0347 | NaN | 34.1419
4027.1292 | 12.8658 | 12.5712 | 12.7427 | 12.9938 | 12.6015 | 12.7281 | 12.5131 | 12.3774 | NaN | NaN | NaN | 12.7394 | 130.6411 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 510.3218 | NaN | 6.0117 | NaN | 25.1214
4028.1292 | 12.8712 | 12.5987 | 12.759 | 13.0068 | 12.592 | 12.7444 | 12.5294 | 12.3832 | NaN | NaN | NaN | 12.8001 | 127.8251 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 511.7236 | NaN | 15.5537 | NaN | 24.2163
4029.1292 | 12.8598 | 12.5569 | 12.7536 | 12.9511 | 12.5818 | 12.7395 | 12.5188 | 12.3855 | NaN | NaN | NaN | 12.7849 | 117.1867 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 512.407 | NaN | 16.9398 | NaN | 21.4001
4030.1292 | 12.8835 | 12.5514 | 12.7594 | 12.9991 | 12.5356 | 12.7333 | 12.5124 | 12.371 | NaN | NaN | NaN | 12.7496 | 124.2604 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 513.6269 | NaN | 33.1162 | NaN | 26.7799
4031.1292 | 12.9492 | 12.5499 | 12.7573 | 12.992 | 12.5584 | 12.7246 | 12.5134 | 12.3759 | NaN | NaN | NaN | 12.7529 | 124.3456 | NaN | NaN | NaN | -2.4096 | NaN | NaN | NaN | NaN | 511.0522 | NaN | 31.3275 | NaN | 25.4554
4032.1292 | 12.9375 | 12.5954 | 12.7561 | 12.9684 | 12.5161 | 12.7437 | 12.5206 | 12.3713 | NaN | NaN | NaN | 12.7476 | 123.0401 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 512.5971 | NaN | 5.7969 | NaN | 22.6194
4033.1292 | 12.8582 | 12.5757 | 12.7586 | 12.9857 | 12.5501 | 12.7386 | 12.5171 | 12.376 | NaN | NaN | NaN | 12.7358 | 123.0283 | NaN | NaN | NaN | -1.4137 | NaN | NaN | NaN | NaN | 512.2088 | NaN | 6.121 | NaN | 23.1293
4034.1292 | 12.857 | 12.5829 | 12.7641 | 12.9614 | 12.4898 | 12.7467 | 12.5169 | 12.3779 | NaN | NaN | NaN | 12.8055 | 126.3719 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 514.6439 | NaN | 5.1105 | NaN | 20.4659
4035.1292 | 12.8522 | 12.5767 | 12.7717 | 13.0117 | 12.4926 | 12.7676 | 12.5255 | 12.3838 | NaN | NaN | NaN | 12.746 | 116.6786 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 515.4847 | NaN | 6.1459 | NaN | 24.7136
4036.1292 | 12.8398 | 12.5958 | 12.7591 | 12.9902 | 12.4793 | 12.7553 | 12.5286 | 12.3824 | NaN | NaN | NaN | 12.7551 | 119.4046 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 514.9351 | NaN | 5.4986 | NaN | 22.0378
4037.1292 | 12.8551 | 12.5956 | 12.7675 | 13.0225 | 12.5848 | 12.7658 | 12.5437 | 12.3868 | NaN | NaN | NaN | 12.7607 | 123.4385 | NaN | NaN | NaN | -7.9435 | NaN | NaN | NaN | NaN | 514.0341 | NaN | 22.3802 | NaN | 26.7736
4038.1292 | 12.8626 | 12.5878 | 12.7745 | 13.0066 | 12.4909 | 12.7614 | 12.5313 | 12.3862 | NaN | NaN | NaN | 12.8452 | 125.3562 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 515.5394 | NaN | 5.4892 | NaN | 24.2674
4039.1292 | 12.8654 | 12.6216 | 12.7742 | 13.0093 | 12.559 | 12.7758 | 12.5422 | 12.3837 | NaN | NaN | NaN | 12.7563 | 119.8915 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 517.6837 | NaN | 28.2462 | NaN | 25.1927
4040.1292 | 12.8673 | 12.5529 | 12.7735 | 12.9941 | 12.5459 | 12.7444 | 12.527 | 12.387 | NaN | NaN | NaN | 12.7492 | 134.8436 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.3579 | NaN | 19.6053 | NaN | 26.3804
4041.1292 | 12.86 | 12.5912 | 12.7741 | 12.963 | 12.5427 | 12.7812 | 12.5445 | 12.3919 | NaN | NaN | NaN | 12.7391 | 112.2516 | NaN | NaN | NaN | -5.8853 | NaN | NaN | NaN | NaN | 518.7733 | NaN | 6.4303 | NaN | 25.6865
4042.1292 | 12.8546 | 12.5752 | 12.7743 | 12.9988 | 12.4697 | 12.7609 | 12.5378 | 12.3957 | NaN | NaN | NaN | 12.7543 | 118.7549 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 518.0366 | NaN | 4.2452 | NaN | 27.2242
4043.1292 | 12.853 | 12.645 | 12.7666 | 12.9734 | 12.5268 | 12.8007 | 12.5568 | 12.389 | NaN | NaN | NaN | 12.7311 | 131.1576 | NaN | NaN | NaN | 0.2124 | NaN | NaN | NaN | NaN | 518.8747 | NaN | 4.7956 | NaN | 19.854
4044.1292 | 12.897 | 12.5227 | 12.7815 | 12.957 | 12.5654 | 12.7318 | 12.5281 | 12.3955 | NaN | NaN | NaN | 12.7474 | 122.2222 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 522.026 | NaN | 14.7291 | NaN | 29.1621
4045.1292 | 12.8802 | 12.5357 | 12.7804 | 13.0442 | 12.59 | 12.7302 | 12.5277 | 12.4006 | NaN | NaN | NaN | 12.7186 | 123.928 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 522.3667 | NaN | 6.1163 | NaN | 14.766
4046.1292 | 12.9028 | 12.5251 | 12.7751 | 12.9826 | 12.5513 | 12.729 | 12.5228 | 12.3991 | NaN | NaN | NaN | 12.7207 | 119.9515 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 521.7339 | NaN | 22.9275 | NaN | 23.9531
4047.1292 | 12.8784 | 12.5382 | 12.7736 | 12.9735 | 12.5221 | 12.7497 | 12.5294 | 12.3967 | NaN | NaN | NaN | 12.7493 | 118.2548 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 525.835 | NaN | 11.8955 | NaN | 23.4531
4048.1292 | 12.8977 | 12.5187 | 12.776 | 13.0112 | 12.5785 | 12.734 | 12.5152 | 12.3972 | NaN | NaN | NaN | 12.7317 | 123.8633 | NaN | NaN | NaN | 6.8941 | NaN | NaN | NaN | NaN | 524.5766 | NaN | 28.1314 | NaN | 23.6844
4049.1292 | 12.8785 | 12.5205 | 12.7763 | 13.0602 | 12.5359 | 12.7293 | 12.5227 | 12.4018 | NaN | NaN | NaN | 12.7306 | 118.8136 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 524.9736 | NaN | 20.2406 | NaN | 26.0749
4050.1292 | 12.8745 | 12.5591 | 12.7814 | 12.9932 | 12.577 | 12.752 | 12.5301 | 12.3954 | NaN | NaN | NaN | 12.7313 | 130.5735 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 524.4159 | NaN | 7.019 | NaN | 18.4288
4051.1292 | 12.8741 | 12.5788 | 12.7779 | 12.9897 | 12.5534 | 12.7633 | 12.5357 | 12.4036 | NaN | NaN | NaN | 12.7159 | 123.9213 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 527.8523 | NaN | 6.41 | NaN | 23.2379
4052.1292 | 12.8785 | 12.5934 | 12.782 | 12.9898 | 12.5606 | 12.7607 | 12.525 | 12.4058 | NaN | NaN | NaN | 12.7334 | 119.2093 | NaN | NaN | NaN | -3.43 | NaN | NaN | NaN | NaN | 526.2481 | NaN | 5.8064 | NaN | 24.8329
4053.1292 | 12.887 | 12.5184 | 12.7755 | 12.9804 | 12.5759 | 12.7466 | 12.5271 | 12.407 | NaN | NaN | NaN | 12.7524 | 119.562 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 527.4006 | NaN | 25.8705 | NaN | 18.5253
4054.1292 | 12.8843 | 12.5744 | 12.785 | 13.019 | 12.5529 | 12.7656 | 12.5368 | 12.4088 | NaN | NaN | NaN | 12.7335 | 117.5676 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 528.4397 | NaN | 13.671 | NaN | 24.9871
4055.1292 | 12.8818 | 12.5827 | 12.7811 | 12.9915 | 12.5862 | 12.7589 | 12.5355 | 12.4149 | NaN | NaN | NaN | 12.8088 | 122.6452 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 529.0662 | NaN | 7.57 | NaN | 30.7369
4056.1292 | 12.8748 | 12.5337 | 12.7845 | 13.0254 | 12.5584 | 12.7287 | 12.5211 | 12.4141 | NaN | NaN | NaN | 12.7264 | 126.7114 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 530.2102 | NaN | 4.1257 | NaN | 26.4064
4057.1292 | 13.0563 | 12.645 | 12.7821 | 12.9999 | 12.5209 | 12.7985 | 12.5559 | 12.415 | NaN | NaN | NaN | 12.7428 | 118.371 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 531.4901 | NaN | 6.9023 | NaN | 16.633
4058.1292 | 12.9227 | 12.5737 | 12.7866 | 13.007 | 12.523 | 12.7589 | 12.5329 | 12.4166 | NaN | NaN | NaN | 12.748 | 121.9155 | NaN | NaN | NaN | 5.331 | NaN | NaN | NaN | NaN | 531.1526 | NaN | 4.4413 | NaN | 22.5171
4059.1292 | 12.8916 | 12.6261 | 12.7844 | 12.9879 | 12.4772 | 12.8006 | 12.5315 | 12.4171 | NaN | NaN | NaN | 12.7251 | 128.2421 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 531.7782 | NaN | 27.4762 | NaN | 22.1243
4060.1292 | 12.8889 | 12.584 | 12.7855 | 12.9871 | 12.5353 | 12.7583 | 12.525 | 12.4232 | NaN | NaN | NaN | 12.7221 | 119.137 | NaN | NaN | NaN | -2.3517 | NaN | NaN | NaN | NaN | 531.1344 | NaN | 33.1694 | NaN | 22.0177
4061.1292 | 12.8885 | 12.6535 | 12.7823 | 13.0458 | 12.5874 | 12.7641 | 12.5372 | 12.419 | NaN | NaN | NaN | 12.6993 | 130.8177 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 529.9273 | NaN | 2.9077 | NaN | 19.0172
4062.1292 | 12.8809 | 12.5521 | 12.7925 | 13.0158 | 12.5249 | 12.7395 | 12.5236 | 12.4192 | NaN | NaN | NaN | 12.7105 | 128.1825 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 533.2989 | NaN | 29.9104 | NaN | 14.1248
4063.1292 | 12.8735 | 12.5848 | 12.788 | 12.9993 | 12.5227 | 12.7546 | 12.5267 | 12.4204 | NaN | NaN | NaN | 12.7172 | 125.5895 | NaN | NaN | NaN | -15.4942 | NaN | NaN | NaN | NaN | 531.5494 | NaN | 31.8712 | NaN | 25.0205
4064.1292 | 12.8692 | 12.5838 | 12.7901 | 12.9795 | 12.4669 | 12.7383 | 12.5274 | 12.4266 | NaN | NaN | NaN | 12.7499 | 121.6122 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 528.5256 | NaN | 6.6247 | NaN | 26.8777
4065.1292 | 12.8698 | 12.5663 | 12.7888 | 13.0042 | 12.5257 | 12.7396 | 12.5304 | 12.4183 | NaN | NaN | NaN | 12.7256 | 129.0621 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 530.1824 | NaN | 10.2136 | NaN | 24.175
4066.1292 | 12.8748 | 12.6446 | 12.7951 | 13.009 | 12.5541 | 12.7659 | 12.5457 | 12.4236 | NaN | NaN | NaN | 12.7097 | 126.1814 | NaN | NaN | NaN | -3.3287 | NaN | NaN | NaN | NaN | 530.7362 | NaN | 35.5206 | NaN | 24.6864
4067.1292 | 12.8723 | 12.6178 | 12.7878 | 12.9695 | 12.5044 | 12.7629 | 12.542 | 12.4219 | NaN | NaN | NaN | 12.7201 | 119.2847 | NaN | NaN | NaN | 3.0451 | NaN | NaN | NaN | NaN | 532.4432 | NaN | 8.1866 | NaN | 15.3657
4068.1292 | 12.9006 | 12.5695 | 12.7843 | 12.9871 | 12.5155 | 12.7268 | 12.5257 | 12.427 | NaN | NaN | NaN | 12.7236 | 117.282 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 532.6599 | NaN | 6.7782 | NaN | 22.4524
4069.1292 | 12.8998 | 12.5961 | 12.79 | 12.9782 | 12.4434 | 12.7349 | 12.5211 | 12.4231 | NaN | NaN | NaN | 12.7309 | 115.3668 | NaN | NaN | NaN | -10.472 | NaN | NaN | NaN | NaN | 530.4798 | NaN | 6.0432 | NaN | 24.8652
4070.1292 | 12.9017 | 12.6009 | 12.7797 | 12.9972 | 12.4913 | 12.7289 | 12.5411 | 12.4217 | NaN | NaN | NaN | 12.7471 | 121.4114 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 532.3163 | NaN | 5.8349 | NaN | 19.8153
4071.1292 | 12.9016 | 12.5748 | 12.7892 | 13.0282 | 12.5482 | 12.7211 | 12.5264 | 12.4206 | NaN | NaN | NaN | 12.7265 | 122.3977 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 536.4437 | NaN | 8.3774 | NaN | 25.9191
4072.1292 | 12.8997 | 12.5884 | 12.7856 | 13.0031 | 12.4683 | 12.7259 | 12.5236 | 12.4256 | NaN | NaN | NaN | 12.7239 | 123.2021 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 532.9069 | NaN | 11.9646 | NaN | 18.6591
4073.1292 | 12.8854 | 12.5865 | 12.7851 | 13.0079 | 12.5406 | 12.7295 | 12.5288 | 12.4218 | NaN | NaN | NaN | 12.7709 | 119.3584 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 535.0163 | NaN | 13.1099 | NaN | 24.4152
4074.1292 | 12.9445 | 12.6365 | 12.7867 | 13.0107 | 12.435 | 12.7626 | 12.5307 | 12.4229 | NaN | NaN | NaN | 12.7484 | 123.9138 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 534.4057 | NaN | 5.3435 | NaN | 28.1833
4075.1292 | 12.9651 | 12.6695 | 12.7871 | 13.0306 | 12.5669 | 12.777 | 12.5525 | 12.4214 | NaN | NaN | NaN | 12.7156 | 124.1343 | NaN | NaN | NaN | -9.6381 | NaN | NaN | NaN | NaN | 531.8727 | NaN | 6.2144 | NaN | 26.5575
4076.1292 | 13.0309 | 12.5962 | 12.7841 | 13.02 | 12.4714 | 12.7466 | 12.5271 | 12.4179 | NaN | NaN | NaN | 12.7498 | 120.5954 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 534.5233 | NaN | 5.8934 | NaN | 26.5789
4077.1292 | 12.9201 | 12.5895 | 12.7934 | 12.9894 | 12.5088 | 12.7385 | 12.5352 | 12.4188 | NaN | NaN | NaN | 12.7209 | 118.8006 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 533.8594 | NaN | 4.8428 | NaN | 26.1564
4078.1292 | 12.9149 | 12.5704 | 12.7951 | 13.0197 | 12.5536 | 12.7218 | 12.528 | 12.4162 | NaN | NaN | NaN | 12.7367 | 127.47 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 534.926 | NaN | 5.6613 | NaN | 26.5791
4079.1292 | 12.9313 | 12.573 | 12.7931 | 13.0018 | 12.5018 | 12.736 | 12.5409 | 12.4205 | NaN | NaN | NaN | 12.76 | 118.1545 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 536.0147 | NaN | 9.9978 | NaN | 26.7399
4080.1292 | 12.9256 | 12.5711 | 12.7959 | 13.0118 | 12.5087 | 12.7463 | 12.537 | 12.4193 | NaN | NaN | NaN | 12.7347 | 124.9963 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 532.3358 | NaN | 6.3176 | NaN | 28.066
4081.1292 | 12.9332 | 12.5761 | 12.7902 | 13.0061 | 12.5082 | 12.7339 | 12.5366 | 12.419 | NaN | NaN | NaN | 12.7588 | 119.0417 | NaN | NaN | NaN | -4.7752 | NaN | NaN | NaN | NaN | 534.4594 | NaN | 10.901 | NaN | 26.6055
4082.1292 | 12.94 | 12.5816 | 12.7915 | 12.9785 | 12.5804 | 12.7447 | 12.5354 | 12.4141 | NaN | NaN | NaN | 12.7486 | 121.3849 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 536.1692 | NaN | 16.5678 | NaN | 32.955
4083.1292 | 12.9355 | 12.57 | 12.7975 | 13.0224 | 12.5284 | 12.7402 | 12.5279 | 12.4151 | NaN | NaN | NaN | 12.7167 | 126.0161 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 536.8046 | NaN | 6.3797 | NaN | 20.7082
4084.1292 | 12.9321 | 12.5509 | 12.7936 | 12.9897 | 12.4911 | 12.7421 | 12.5254 | 12.4172 | NaN | NaN | NaN | 12.7653 | 124.0331 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 537.1835 | NaN | 26.9106 | NaN | 26.1498
4085.1292 | 13.0328 | 12.5466 | 12.7949 | 12.974 | 12.5084 | 12.728 | 12.5209 | 12.4182 | NaN | NaN | NaN | 12.7305 | 114.018 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 536.7696 | NaN | 14.228 | NaN | 20.3226
4086.1292 | 12.9535 | 12.5473 | 12.7939 | 12.9806 | 12.4916 | 12.754 | 12.5309 | 12.4182 | NaN | NaN | NaN | 12.7391 | 120.3173 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 537.1667 | NaN | 5.8487 | NaN | 20.045
4087.1292 | 12.9486 | 12.6284 | 12.7877 | 13.0079 | 12.5294 | 12.8087 | 12.5431 | 12.4206 | NaN | NaN | NaN | 12.7405 | 130.5035 | NaN | NaN | NaN | -9.3607 | NaN | NaN | NaN | NaN | 538.0929 | NaN | 5.5802 | NaN | 25.4996
4088.1292 | 12.9471 | 12.5714 | 12.7834 | 13.0004 | 12.4489 | 12.77 | 12.5362 | 12.416 | NaN | NaN | NaN | 12.7243 | 123.2557 | NaN | NaN | NaN | -5.1106 | NaN | NaN | NaN | NaN | 538.4386 | NaN | 31.6666 | NaN | 27.4686
4089.1292 | 12.9476 | 12.5378 | 12.7729 | 12.9888 | 12.5436 | 12.7457 | 12.5199 | 12.4141 | NaN | NaN | NaN | 12.7305 | 116.9078 | NaN | NaN | NaN | 4.0507 | NaN | NaN | NaN | NaN | 539.0117 | NaN | 4.8232 | NaN | 27.0785
4090.1292 | 12.9468 | 12.5517 | 12.7728 | 12.9886 | 12.6227 | 12.7472 | 12.5329 | 12.4238 | NaN | NaN | NaN | 12.8554 | 127.6775 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 537.756 | NaN | 3.3037 | NaN | 26.7184
4091.1292 | 12.9535 | 12.5637 | 12.7797 | 13.0192 | 12.5829 | 12.7351 | 12.5394 | 12.4212 | NaN | NaN | NaN | 12.7204 | 126.4298 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 537.3381 | NaN | 5.101 | NaN | 26.4014
4092.1292 | 12.9486 | 12.5685 | 12.775 | 12.9773 | 12.4854 | 12.7552 | 12.551 | 12.4206 | NaN | NaN | NaN | 12.7431 | 132.2064 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 539.5113 | NaN | 5.8298 | NaN | 26.5914
4093.1292 | 12.952 | 12.613 | 12.7788 | 13.0306 | 12.5622 | 12.7833 | 12.5571 | 12.4207 | NaN | NaN | NaN | 12.7251 | 127.3349 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 539.1383 | NaN | 10.8876 | NaN | 29.0079
4094.1292 | 12.9492 | 12.5162 | 12.7845 | 12.9987 | 12.5552 | 12.7372 | 12.5322 | 12.4161 | NaN | NaN | NaN | 12.769 | 133.8657 | NaN | NaN | NaN | -11.3864 | NaN | NaN | NaN | NaN | 541.7144 | NaN | 3.3951 | NaN | 24.8441
4095.1292 | 12.9538 | 12.5785 | 12.79 | 13.0052 | 12.5618 | 12.7578 | 12.5412 | 12.4162 | NaN | NaN | NaN | 12.7555 | 131.1431 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 540.2744 | NaN | 5.4926 | NaN | 21.7225
4096.1292 | 12.9544 | 12.5553 | 12.7892 | 12.9805 | 12.4762 | 12.7654 | 12.5332 | 12.4152 | NaN | NaN | NaN | 12.7313 | 126.9916 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 539.7639 | NaN | 4.4086 | NaN | 26.8099
4097.1292 | 12.9599 | 12.5914 | 12.791 | 12.9646 | 12.5529 | 12.7554 | 12.543 | 12.4222 | NaN | NaN | NaN | 12.7607 | 126.9166 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 540.574 | NaN | 6.297 | NaN | 22.8088
4098.1292 | 13.1109 | 12.7091 | 12.7864 | 13.0192 | 12.566 | 12.8095 | 12.5797 | 12.4233 | NaN | NaN | NaN | 12.7184 | 124.8809 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 539.3203 | NaN | 4.1161 | NaN | 25.2622
4099.1292 | 12.9345 | 12.5564 | 12.7863 | 13.0153 | 12.4807 | 12.75 | 12.5343 | 12.4206 | NaN | NaN | NaN | 12.7243 | 113.9768 | NaN | NaN | NaN | -4.6041 | NaN | NaN | NaN | NaN | 538.8766 | NaN | 5.0404 | NaN | 19.4948
4100.1292 | 12.988 | 12.6163 | 12.7866 | 12.9926 | 12.4879 | 12.797 | 12.5556 | 12.4221 | NaN | NaN | NaN | 12.7294 | 130.8693 | NaN | NaN | NaN | 6.2143 | NaN | NaN | NaN | NaN | 541.2947 | NaN | 5.7506 | NaN | 13.6191
4101.1292 | 12.9678 | 12.6145 | 12.7841 | 13.0226 | 12.5386 | 12.7659 | 12.5516 | 12.4274 | NaN | NaN | NaN | 12.7211 | 127.6247 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 541.4116 | NaN | 20.5439 | NaN | 18.9452
4102.1292 | 12.9774 | 12.6002 | 12.784 | 13.0087 | 12.5746 | 12.7606 | 12.5485 | 12.4291 | NaN | NaN | NaN | 12.7545 | 118.4051 | NaN | NaN | NaN | -10.6235 | NaN | NaN | NaN | NaN | 541.9568 | NaN | 11.3865 | NaN | 29.5636
4103.1292 | 12.9689 | 12.5585 | 12.7856 | 13.0341 | 12.5654 | 12.7588 | 12.5527 | 12.4275 | NaN | NaN | NaN | 12.7513 | 119.314 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 542.0357 | NaN | 9.4313 | NaN | 24.8126
4104.1292 | 12.9647 | 12.5492 | 12.7795 | 13.0283 | 12.5054 | 12.7559 | 12.5617 | 12.4298 | NaN | NaN | NaN | 12.7378 | 126.1614 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 544.1951 | NaN | 7.7168 | NaN | 17.483
4105.1292 | 12.9651 | 12.5624 | 12.7801 | 13.0172 | 12.4726 | 12.772 | 12.5477 | 12.4302 | NaN | NaN | NaN | 12.7072 | 129.5226 | NaN | NaN | NaN | -4.0604 | NaN | NaN | NaN | NaN | 544.6688 | NaN | 31.6683 | NaN | 27.1604
4106.1292 | 12.9647 | 12.5968 | 12.7828 | 13.0056 | 12.4937 | 12.7885 | 12.5561 | 12.424 | NaN | NaN | NaN | 12.7547 | 126.802 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 542.6274 | NaN | 5.9452 | NaN | 21.6305
4107.1292 | 12.9587 | 12.567 | 12.779 | 13.0335 | 12.5395 | 12.7711 | 12.5549 | 12.4259 | NaN | NaN | NaN | 12.7017 | 125.7044 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 542.6871 | NaN | 5.0804 | NaN | 18.9351
4108.1292 | 12.936 | 12.5627 | 12.7833 | 13.0428 | 12.4705 | 12.7627 | 12.5408 | 12.4185 | NaN | NaN | NaN | 12.7242 | 126.8606 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 543.293 | NaN | 4.9447 | NaN | 25.4275
4109.1292 | 12.9892 | 12.5392 | 12.7849 | 12.9807 | 12.5077 | 12.7574 | 12.5424 | 12.4197 | NaN | NaN | NaN | 12.7026 | 120.3499 | NaN | NaN | NaN | -8.3048 | NaN | NaN | NaN | NaN | 545.1452 | NaN | 5.4347 | NaN | 26.5096
4110.1292 | 12.9731 | 12.589 | 12.779 | 13.0483 | 12.545 | 12.7924 | 12.5559 | 12.421 | NaN | NaN | NaN | 12.7319 | 119.6627 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 545.9439 | NaN | 26.4794 | NaN | 21.694
4111.1292 | 13.0801 | 12.513 | 12.7782 | 13.0351 | 12.5241 | 12.7452 | 12.5286 | 12.4271 | NaN | NaN | NaN | 12.7243 | 131.2366 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 545.263 | NaN | 6.2704 | NaN | 24.2458
4112.1292 | 12.9621 | 12.5455 | 12.7759 | 13.0397 | 12.5478 | 12.772 | 12.5418 | 12.4219 | NaN | NaN | NaN | 12.7197 | 112.8975 | NaN | NaN | NaN | -16.8786 | NaN | NaN | NaN | NaN | 545.4239 | NaN | 5.3523 | NaN | 16.9182
4113.1292 | 12.9539 | 12.5293 | 12.7723 | 13.0246 | 12.5156 | 12.7634 | 12.537 | 12.4285 | NaN | NaN | NaN | 12.7294 | 121.5781 | NaN | NaN | NaN | -2.3275 | NaN | NaN | NaN | NaN | 545.096 | NaN | 29.8653 | NaN | 22.3038
4114.1292 | 12.9621 | 12.5184 | 12.7704 | 13.0323 | 12.5605 | 12.7463 | 12.5256 | 12.4255 | NaN | NaN | NaN | 12.7433 | 134.3765 | NaN | NaN | NaN | -17.7464 | NaN | NaN | NaN | NaN | 544.0574 | NaN | 16.747 | NaN | 27.6375
4115.1292 | 12.9874 | 12.5752 | 12.7717 | 12.9954 | 12.5694 | 12.7614 | 12.5293 | 12.4268 | NaN | NaN | NaN | 12.74 | 118.8627 | NaN | NaN | NaN | -16.6717 | NaN | NaN | NaN | NaN | 544.3041 | NaN | 33.3238 | NaN | 15.5382
4116.1292 | 13.2317 | 12.5827 | 12.7686 | 13.0635 | 12.585 | 12.7643 | 12.5322 | 12.423 | NaN | NaN | NaN | 12.7897 | 124.2484 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 543.8133 | NaN | 7.1184 | NaN | 22.5843
4117.1292 | 12.9698 | 12.5364 | 12.7608 | 13.0308 | 12.5571 | 12.7467 | 12.5221 | 12.4263 | NaN | NaN | NaN | 12.8398 | 125.6421 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 547.2371 | NaN | 4.171 | NaN | 27.3018
4118.1292 | 12.9527 | 12.618 | 12.7649 | 13.0361 | 12.5316 | 12.7599 | 12.5461 | 12.4243 | NaN | NaN | NaN | 12.7585 | 128.4353 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 546.6784 | NaN | 6.2259 | NaN | 21.4905
4119.1292 | 12.9739 | 12.6526 | 12.7553 | 13.0437 | 12.4774 | 12.8046 | 12.5465 | 12.4283 | NaN | NaN | NaN | 12.8009 | 132.6408 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 545.4375 | NaN | 5.7449 | NaN | 22.3549
4120.1292 | 12.9696 | 12.6129 | 12.7522 | 13.0641 | 12.5771 | 12.7495 | 12.5412 | 12.4249 | NaN | NaN | NaN | 12.7632 | 129.6943 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 545.8341 | NaN | 10.8288 | NaN | 25.8098
4121.1292 | 12.961 | 12.622 | 12.7617 | 13.0596 | 12.5005 | 12.76 | 12.5524 | 12.4254 | NaN | NaN | NaN | 12.768 | 129.1945 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 544.2372 | NaN | 9.7052 | NaN | 18.4356
4122.1292 | 12.967 | 12.619 | 12.7523 | 13.0473 | 12.518 | 12.7711 | 12.5473 | 12.4319 | NaN | NaN | NaN | 12.7602 | 126.5185 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 545.7422 | NaN | 13.0852 | NaN | 21.3345
4123.1292 | 12.9458 | 12.6013 | 12.7563 | 13.0537 | 12.5588 | 12.7632 | 12.5504 | 12.4319 | NaN | NaN | NaN | 12.78 | 126.7772 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 544.7831 | NaN | 9.2839 | NaN | 20.8662
4124.1292 | 13.0151 | 12.5626 | 12.7546 | 13.0377 | 12.5866 | 12.7476 | 12.5424 | 12.4347 | NaN | NaN | NaN | 12.7878 | 120.3634 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 546.1734 | NaN | 5.5948 | NaN | 24.534
4125.1292 | 13.0079 | 12.5746 | 12.759 | 13.0872 | 12.4996 | 12.7456 | 12.5473 | 12.4362 | NaN | NaN | NaN | 12.7771 | 122.0482 | NaN | NaN | NaN | -16.8637 | NaN | NaN | NaN | NaN | 541.2956 | NaN | 4.5642 | NaN | 28.5042
4126.1292 | 12.9778 | 12.5918 | 12.7568 | 13.0468 | 12.4982 | 12.7641 | 12.5446 | 12.4304 | NaN | NaN | NaN | 12.847 | 130.7972 | NaN | NaN | NaN | -12.0095 | NaN | NaN | NaN | NaN | 544.2831 | NaN | 4.7652 | NaN | 25.0593
4127.1292 | 12.9854 | 12.5586 | 12.758 | 13.0706 | 12.5342 | 12.751 | 12.531 | 12.4254 | NaN | NaN | NaN | 12.79 | 119.4043 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 544.7017 | NaN | 6.1519 | NaN | 16.1146
4128.1292 | 12.9921 | 12.541 | 12.756 | 13.0635 | 12.6008 | 12.7331 | 12.5236 | 12.4247 | NaN | NaN | NaN | 12.7685 | 125.6922 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 542.4536 | NaN | 6.3704 | NaN | 24.9976
4129.1292 | 12.9893 | 12.6303 | 12.7674 | 13.0381 | 12.5837 | 12.774 | 12.5497 | 12.4253 | NaN | NaN | NaN | 12.7805 | 134.1262 | NaN | NaN | NaN | -7.2844 | NaN | NaN | NaN | NaN | 541.8268 | NaN | 18.8652 | NaN | 22.8372
4130.1292 | 12.9869 | 12.6336 | 12.7587 | 13.0683 | 12.5617 | 12.7733 | 12.5492 | 12.4236 | NaN | NaN | NaN | 12.7843 | 122.1314 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 544.6493 | NaN | 5.4813 | NaN | 14.0852
4131.1292 | 12.9731 | 12.6227 | 12.7576 | 13.066 | 12.5045 | 12.8019 | 12.55 | 12.4263 | NaN | NaN | NaN | 12.8056 | 133.4225 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 546.3076 | NaN | 30.4219 | NaN | 24.2388
4132.1292 | 12.9878 | 12.5808 | 12.757 | 13.0456 | 12.6072 | 12.7562 | 12.5394 | 12.4228 | NaN | NaN | NaN | 12.8103 | 118.4271 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 544.3283 | NaN | 12.4913 | NaN | 22.404
4133.1292 | 12.9957 | 12.6469 | 12.7561 | 13.0884 | 12.472 | 12.8155 | 12.5635 | 12.4276 | NaN | NaN | NaN | 12.7869 | 128.2421 | NaN | NaN | NaN | -7.7875 | NaN | NaN | NaN | NaN | 543.6485 | NaN | 4.8227 | NaN | 19.9809
4134.1292 | 12.9894 | 12.5865 | 12.7551 | 13.0289 | 12.5089 | 12.75 | 12.5446 | 12.4199 | NaN | NaN | NaN | 12.8188 | 129.6092 | NaN | NaN | NaN | -0.6539 | NaN | NaN | NaN | NaN | 545.517 | NaN | 12.9411 | NaN | 28.3511
4135.1292 | 12.9796 | 12.5669 | 12.7524 | 13.0546 | 12.5415 | 12.7524 | 12.5357 | 12.4177 | NaN | NaN | NaN | 12.7839 | 123.5373 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 544.0604 | NaN | 7.0163 | NaN | 28.5163
4136.1292 | 12.9722 | 12.5714 | 12.7517 | 13.0405 | 12.5346 | 12.7557 | 12.5343 | 12.4158 | NaN | NaN | NaN | 12.8357 | 132.9565 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 542.9379 | NaN | 18.8638 | NaN | 22.0866
4137.1292 | 13.0517 | 12.5927 | 12.7475 | 13.0184 | 12.5748 | 12.7641 | 12.5513 | 12.4204 | NaN | NaN | NaN | 12.7926 | 125.6642 | NaN | NaN | NaN | -0.516 | NaN | NaN | NaN | NaN | 544.135 | NaN | 8.1397 | NaN | 27.9501
4138.1292 | 13.0003 | 12.6069 | 12.7553 | 13.0577 | 12.505 | 12.7817 | 12.5381 | 12.4148 | NaN | NaN | NaN | 12.793 | 115.736 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 543.0127 | NaN | 10.829 | NaN | 26.5869
4139.1292 | 12.9868 | 12.5739 | 12.7637 | 13.0449 | 12.5886 | 12.7451 | 12.5363 | 12.4121 | NaN | NaN | NaN | 12.8158 | 117.8215 | NaN | NaN | NaN | 4.5704 | NaN | NaN | NaN | NaN | 546.0031 | NaN | 5.7428 | NaN | 17.9488
4140.1292 | 12.972 | 12.6047 | 12.7618 | 13.0828 | 12.5833 | 12.7505 | 12.5387 | 12.4071 | NaN | NaN | NaN | 12.8804 | 115.724 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 542.478 | NaN | 21.0029 | NaN | 22.5455
4141.1292 | 12.9781 | 12.5871 | 12.7655 | 12.9992 | 12.5837 | 12.7435 | 12.5354 | 12.4091 | NaN | NaN | NaN | 12.7839 | 128.453 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 542.4193 | NaN | 7.6276 | NaN | 25.8633
4142.1292 | 12.9869 | 12.59 | 12.7626 | 13.05 | 12.5217 | 12.7552 | 12.5361 | 12.4098 | NaN | NaN | NaN | 12.7808 | 127.1531 | NaN | NaN | NaN | -11.0937 | NaN | NaN | NaN | NaN | 544.4234 | NaN | 33.463 | NaN | 23.3138
4143.1292 | 12.9906 | 12.5977 | 12.7651 | 13.0249 | 12.5535 | 12.7698 | 12.5518 | 12.4116 | NaN | NaN | NaN | 12.8169 | 126.6951 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 541.4677 | NaN | 13.9877 | NaN | 25.4711
4144.1292 | 12.9963 | 12.5939 | 12.7632 | 13.0415 | 12.4957 | 12.7665 | 12.5388 | 12.413 | NaN | NaN | NaN | 12.8252 | 127.6395 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 541.3544 | NaN | 5.0928 | NaN | 24.1519
4145.1292 | 12.9902 | 12.6386 | 12.7697 | 13.0493 | 12.5457 | 12.7833 | 12.553 | 12.4109 | NaN | NaN | NaN | 12.7867 | 125.6539 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 540.8863 | NaN | 21.8908 | NaN | 26.4576
4146.1292 | 13.0016 | 12.5958 | 12.7634 | 13.0086 | 12.5912 | 12.7608 | 12.551 | 12.4082 | NaN | NaN | NaN | 12.8007 | 129.2586 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 538.6301 | NaN | 9.7012 | NaN | 29.3692
4147.1292 | 12.9974 | 12.5814 | 12.7705 | 13.046 | 12.5711 | 12.7769 | 12.5424 | 12.4127 | NaN | NaN | NaN | 12.8047 | 123.8747 | NaN | NaN | NaN | -14.0597 | NaN | NaN | NaN | NaN | 542.928 | NaN | 33.7572 | NaN | 15.2227
4148.1292 | 13.0007 | 12.6369 | 12.7754 | 13.0435 | 12.5803 | 12.8018 | 12.5592 | 12.4145 | NaN | NaN | NaN | 12.7924 | 131.9652 | NaN | NaN | NaN | -6.1185 | NaN | NaN | NaN | NaN | 540.2581 | NaN | 7.9494 | NaN | 27.7491
4149.1292 | 12.9994 | 12.5745 | 12.7781 | 13.0901 | 12.4828 | 12.753 | 12.5443 | 12.4051 | NaN | NaN | NaN | 12.7825 | 116.2536 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 540.3388 | NaN | 5.2279 | NaN | 25.4328
4150.1292 | 12.9938 | 12.6653 | 12.7759 | 13.0368 | 12.5934 | 12.8052 | 12.5709 | 12.4131 | NaN | NaN | NaN | 12.8194 | 128.2932 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 540.5523 | NaN | 5.1501 | NaN | 27.4136
4151.1292 | 12.9924 | 12.6281 | 12.7736 | 13.0727 | 12.5918 | 12.7785 | 12.5507 | 12.4107 | NaN | NaN | NaN | 12.807 | 119.5411 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 540.3853 | NaN | 9.104 | NaN | 24.3371
4152.1292 | 12.9826 | 12.663 | 12.7726 | 13.0503 | 12.5102 | 12.8139 | 12.5674 | 12.4129 | NaN | NaN | NaN | 12.8001 | 114.9579 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 543.0545 | NaN | 7.4991 | NaN | 26.3876
4153.1292 | 12.9889 | 12.6103 | 12.7703 | 13.0251 | 12.5659 | 12.7834 | 12.5515 | 12.4082 | NaN | NaN | NaN | 12.805 | 121.4902 | NaN | NaN | NaN | -18.131 | NaN | NaN | NaN | NaN | 542.6094 | NaN | 8.8139 | NaN | 18.4194
4154.1292 | 13.0355 | 12.646 | 12.7685 | 13.0502 | 12.5665 | 12.8059 | 12.5556 | 12.41 | NaN | NaN | NaN | 12.8263 | 115.3758 | NaN | NaN | NaN | -2.8126 | NaN | NaN | NaN | NaN | 537.823 | NaN | 7.0891 | NaN | 20.5435
4155.1292 | 12.982 | 12.5946 | 12.7689 | 13.1204 | 12.468 | 12.8027 | 12.5682 | 12.4139 | NaN | NaN | NaN | 12.8391 | 121.2473 | NaN | NaN | NaN | 7.3564 | NaN | NaN | NaN | NaN | 539.5039 | NaN | 5.5534 | NaN | 27.3136
4156.1292 | 12.9663 | 12.6068 | 12.7656 | 13.0504 | 12.5017 | 12.8092 | 12.5742 | 12.4135 | NaN | NaN | NaN | 12.8236 | 119.5305 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 539.7778 | NaN | 8.2523 | NaN | 22.9197
4157.1292 | 13.0536 | 12.7003 | 12.7663 | 13.0015 | 12.6025 | 12.8345 | 12.5857 | 12.4247 | NaN | NaN | NaN | 12.7805 | 118.2078 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 536.082 | NaN | 11.4208 | NaN | 24.4581
4158.1292 | 13.0096 | 12.7085 | 12.7626 | 13.0378 | 12.5367 | 12.8055 | 12.6113 | 12.4179 | NaN | NaN | NaN | 12.8266 | 118.7266 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 538.4344 | NaN | 6.275 | NaN | 26.5817
4159.1292 | 13.0072 | 12.6159 | 12.7638 | 13.0526 | 12.6168 | 12.7988 | 12.5659 | 12.4203 | NaN | NaN | NaN | 12.8175 | 116.0821 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 538.358 | NaN | 6.7875 | NaN | 21.6381
4160.1292 | 13.0848 | 12.5975 | 12.7634 | 13.1682 | 12.5165 | 12.8011 | 12.568 | 12.4125 | NaN | NaN | NaN | 12.7885 | 121.6035 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 540.3834 | NaN | 14.0092 | NaN | 29.4155
4161.1292 | 13.0148 | 12.6084 | 12.7643 | 13.0395 | 12.5754 | 12.7805 | 12.5633 | 12.4232 | NaN | NaN | NaN | 12.8152 | 118.9711 | NaN | NaN | NaN | -14.2458 | NaN | NaN | NaN | NaN | 538.7545 | NaN | 6.4208 | NaN | 27.15
4162.1292 | 13.004 | 12.6884 | 12.7644 | 13.0358 | 12.5958 | 12.8166 | 12.5663 | 12.4183 | NaN | NaN | NaN | 12.8177 | 127.0888 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 540.725 | NaN | 5.9878 | NaN | 21.6798
4163.1292 | 13.0169 | 12.6256 | 12.7637 | 13.0671 | 12.501 | 12.8025 | 12.5608 | 12.4231 | NaN | NaN | NaN | 12.7938 | 121.4676 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 540.0862 | NaN | 5.0545 | NaN | 25.1894
4164.1292 | 13.0097 | 12.6783 | 12.7658 | 13.0868 | 12.5224 | 12.8142 | 12.5622 | 12.4196 | NaN | NaN | NaN | 12.8014 | 127.2445 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 537.4334 | NaN | 25.306 | NaN | 23.6322
4165.1292 | 13.009 | 12.6128 | 12.768 | 13.0452 | 12.5807 | 12.7794 | 12.559 | 12.4214 | NaN | NaN | NaN | 12.9148 | 121.6503 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 539.0978 | NaN | 4.5603 | NaN | 26.8542
4166.1292 | 12.9954 | 12.6188 | 12.7694 | 13.0192 | 12.5669 | 12.7997 | 12.5539 | 12.4247 | NaN | NaN | NaN | 12.8201 | 118.1609 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 535.5705 | NaN | 28.3602 | NaN | 19.9256
4167.1292 | 12.9951 | 12.6139 | 12.7717 | 13.0656 | 12.5274 | 12.8068 | 12.5625 | 12.4208 | NaN | NaN | NaN | 12.8064 | 117.2347 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 539.6492 | NaN | 6.6517 | NaN | 25.1674
4168.1292 | 12.9905 | 12.6009 | 12.7783 | 13.107 | 12.5557 | 12.8045 | 12.5652 | 12.425 | NaN | NaN | NaN | 12.8194 | 118.1547 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 538.2353 | NaN | 31.0716 | NaN | 21.1744
4169.1292 | 12.9955 | 12.6837 | 12.7748 | 13.0307 | 12.5591 | 12.8131 | 12.5869 | 12.4291 | NaN | NaN | NaN | 12.8297 | 132.3617 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 537.0463 | NaN | 4.1152 | NaN | 25.7134
4170.1292 | 12.9837 | 12.5875 | 12.7771 | 13.0688 | 12.5407 | 12.7894 | 12.553 | 12.4209 | NaN | NaN | NaN | 12.874 | 114.7889 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 537.1809 | NaN | 19.9639 | NaN | 31.5154
4171.1292 | 12.9968 | 12.6024 | 12.776 | 13.0443 | 12.5826 | 12.7865 | 12.5629 | 12.4232 | NaN | NaN | NaN | 12.8173 | 121.9076 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 539.5724 | NaN | 5.5321 | NaN | 26.1291
4172.1292 | 13.0068 | 12.6111 | 12.7763 | 13.0714 | 12.4993 | 12.8068 | 12.5639 | 12.4175 | NaN | NaN | NaN | 12.8157 | 116.5189 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 538.8414 | NaN | 4.1431 | NaN | 25.7678
4173.1292 | 12.9943 | 12.5909 | 12.7788 | 13.0247 | 12.5238 | 12.7929 | 12.5621 | 12.4148 | NaN | NaN | NaN | 12.8244 | 122.7673 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 540.1219 | NaN | 8.5236 | NaN | 18.6077
4174.1292 | 12.9967 | 12.6138 | 12.7828 | 13.0724 | 12.5641 | 12.7861 | 12.5623 | 12.4231 | NaN | NaN | NaN | 12.8304 | 122.2078 | NaN | NaN | NaN | -1.5444 | NaN | NaN | NaN | NaN | 533.8719 | NaN | 38.3378 | NaN | 22.8557
4175.1292 | 12.9988 | 12.5792 | 12.7838 | 13.0502 | 12.576 | 12.7845 | 12.5611 | 12.4148 | NaN | NaN | NaN | 12.8382 | 122.7091 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 534.7939 | NaN | 30.405 | NaN | 12.9356
4176.1292 | 12.9906 | 12.5738 | 12.7813 | 13.0193 | 12.5857 | 12.7838 | 12.5651 | 12.4177 | NaN | NaN | NaN | 12.8438 | 124.4947 | NaN | NaN | NaN | -12.7307 | NaN | NaN | NaN | NaN | 537.4186 | NaN | 4.9443 | NaN | 25.166
4177.1292 | 13.0816 | 12.604 | 12.7876 | 13.0936 | 12.5054 | 12.7842 | 12.5616 | 12.4169 | NaN | NaN | NaN | 12.8585 | 117.1218 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 534.3235 | NaN | 5.1187 | NaN | 15.8821
4178.1292 | 13.0011 | 12.6652 | 12.7884 | 13.1378 | 12.5978 | 12.8151 | 12.583 | 12.4258 | NaN | NaN | NaN | 12.8429 | 121.8733 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 534.5611 | NaN | 31.0097 | NaN | 26.8645
4179.1292 | 12.9785 | 12.6328 | 12.7783 | 13.0478 | 12.5738 | 12.8064 | 12.5749 | 12.4259 | NaN | NaN | NaN | 12.8742 | 121.1909 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 535.2306 | NaN | 7.8224 | NaN | 14.221
4180.1292 | 12.9907 | 12.7351 | 12.7795 | 13.0297 | 12.5364 | 12.7978 | 12.595 | 12.4207 | NaN | NaN | NaN | 12.8007 | 124.3801 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 538.5151 | NaN | 8.6693 | NaN | 25.0392
4181.1292 | 12.9816 | 12.6032 | 12.7785 | 12.9993 | 12.5602 | 12.7839 | 12.5537 | 12.4166 | NaN | NaN | NaN | 12.8186 | 119.8495 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 535.9335 | NaN | 30.9532 | NaN | 27.391
4182.1292 | 12.9873 | 12.6445 | 12.779 | 13.0528 | 12.5113 | 12.7982 | 12.5625 | 12.4147 | NaN | NaN | NaN | 12.811 | 116.7129 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 535.9262 | NaN | 4.1993 | NaN | 26.0331
4183.1292 | 12.9848 | 12.7038 | 12.7853 | 13.0622 | 12.5992 | 12.8022 | 12.56 | 12.4191 | NaN | NaN | NaN | 12.8509 | 126.3432 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 536.1676 | NaN | 15.4223 | NaN | 23.5884
4184.1292 | 12.9523 | 12.641 | 12.7905 | 13.0753 | 12.4985 | 12.799 | 12.5459 | 12.4117 | NaN | NaN | NaN | 12.9148 | 135.5093 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 535.2414 | NaN | 4.5575 | NaN | 16.6823
4185.1292 | 13.0185 | 12.6525 | 12.7882 | 13.0248 | 12.5756 | 12.7891 | 12.5498 | 12.4101 | NaN | NaN | NaN | 12.8286 | 118.4327 | NaN | NaN | NaN | -6.6068 | NaN | NaN | NaN | NaN | 538.008 | NaN | 5.4615 | NaN | 24.5726
4186.1292 | 13.0002 | 12.6515 | 12.7914 | 13.0502 | 12.6096 | 12.7916 | 12.5518 | 12.4102 | NaN | NaN | NaN | 12.8163 | 116.64 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 537.0411 | NaN | 5.7261 | NaN | 18.667
4187.1292 | 12.9486 | 12.6018 | 12.7866 | 13.0608 | 12.5566 | 12.7688 | 12.54 | 12.4061 | NaN | NaN | NaN | 12.8315 | 123.7501 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 536.6593 | NaN | 4.8039 | NaN | 14.167
4188.1292 | 12.96 | 12.6196 | 12.7915 | 13.0832 | 12.605 | 12.7781 | 12.5386 | 12.4122 | NaN | NaN | NaN | 12.8369 | 123.1611 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 536.3219 | NaN | 5.1786 | NaN | 29.6178
4189.1292 | 12.9918 | 12.6657 | 12.7983 | 13.0509 | 12.5793 | 12.808 | 12.5546 | 12.4116 | NaN | NaN | NaN | 12.8484 | 124.3092 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 538.4546 | NaN | 18.5047 | NaN | 21.801
4190.1292 | 12.9656 | 12.6226 | 12.7912 | 13.0772 | 12.6032 | 12.7716 | 12.5432 | 12.4038 | NaN | NaN | NaN | 12.8976 | 123.8234 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 536.6999 | NaN | 3.8272 | NaN | 27.3649
4191.1292 | 13.0509 | 12.6074 | 12.7956 | 13.0312 | 12.5899 | 12.7781 | 12.5431 | 12.4115 | NaN | NaN | NaN | 12.8097 | 137.3122 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 539.2546 | NaN | 8.7885 | NaN | 24.685
4192.1292 | 12.9801 | 12.6247 | 12.7959 | 13.069 | 12.6349 | 12.7963 | 12.5455 | 12.4118 | NaN | NaN | NaN | 12.8253 | 118.6202 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 538.5155 | NaN | 4.9336 | NaN | 16.6779
4193.1292 | 12.9761 | 12.6061 | 12.7945 | 13.0533 | 12.5786 | 12.7964 | 12.5516 | 12.4088 | NaN | NaN | NaN | 12.8265 | 119.8204 | NaN | NaN | NaN | -16.8162 | NaN | NaN | NaN | NaN | 541.149 | NaN | 7.1704 | NaN | 21.4154
4194.1292 | 12.9487 | 12.5908 | 12.7931 | 13.095 | 12.6172 | 12.7799 | 12.5442 | 12.4128 | NaN | NaN | NaN | 12.8272 | 116.9864 | NaN | NaN | NaN | -7.1046 | NaN | NaN | NaN | NaN | 539.3245 | NaN | 6.7298 | NaN | 29.1563
4195.1292 | 12.9605 | 12.5924 | 12.7949 | 13.0153 | 12.5499 | 12.7898 | 12.5515 | 12.4111 | NaN | NaN | NaN | 12.8276 | 123.4938 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 542.348 | NaN | 13.5983 | NaN | 29.4456
4196.1292 | 12.9616 | 12.6043 | 12.7884 | 13.076 | 12.6278 | 12.7862 | 12.5486 | 12.4105 | NaN | NaN | NaN | 12.834 | 111.0963 | NaN | NaN | NaN | -18.5931 | NaN | NaN | NaN | NaN | 539.5133 | NaN | 7.4121 | NaN | 27.9476
4197.1292 | 13.0269 | 12.6039 | 12.7923 | 13.0644 | 12.59 | 12.7929 | 12.5412 | 12.4118 | NaN | NaN | NaN | 12.8186 | 123.9445 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 537.6646 | NaN | 37.0828 | NaN | 23.2453
4198.1292 | 12.9785 | 12.7599 | 12.7945 | 13.0785 | 12.5695 | 12.8992 | 12.5961 | 12.4187 | NaN | NaN | NaN | 12.8248 | 121.6939 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 539.8933 | NaN | 12.2188 | NaN | 25.0779
4199.1292 | 12.9739 | 12.6296 | 12.8006 | 13.0627 | 12.5783 | 12.8013 | 12.5541 | 12.4172 | NaN | NaN | NaN | 12.8498 | 133.5909 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 537.7852 | NaN | 6.7536 | NaN | 35.6605
4200.1292 | 12.9906 | 12.6187 | 12.7937 | 13.0875 | 12.5916 | 12.8046 | 12.5667 | 12.4223 | NaN | NaN | NaN | 12.8193 | 129.955 | NaN | NaN | NaN | -17.2187 | NaN | NaN | NaN | NaN | 540.0832 | NaN | 29.865 | NaN | 19.7976
4201.1292 | 12.9744 | 12.6602 | 12.8023 | 13.0838 | 12.5659 | 12.8051 | 12.5697 | 12.4245 | NaN | NaN | NaN | 12.8484 | 131.6045 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 540.8146 | NaN | 4.2072 | NaN | 23.5048
4202.1292 | 12.9325 | 12.6449 | 12.7975 | 13.0565 | 12.6197 | 12.8027 | 12.56 | 12.4196 | NaN | NaN | NaN | 12.8321 | 124.7593 | NaN | NaN | NaN | -3.2764 | NaN | NaN | NaN | NaN | 536.4427 | NaN | 6.6665 | NaN | 26.7737
4203.1292 | 13.0262 | 12.66 | 12.7962 | 13.0251 | 12.6211 | 12.8183 | 12.568 | 12.4207 | NaN | NaN | NaN | 12.8361 | 127.2343 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 538.302 | NaN | 4.1907 | NaN | 24.8153
4204.1292 | 12.9579 | 12.6618 | 12.798 | 12.9998 | 12.5682 | 12.823 | 12.555 | 12.4289 | NaN | NaN | NaN | 12.8374 | 129.0837 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 537.9095 | NaN | 11.1913 | NaN | 21.3575
4205.1292 | 12.9607 | 12.6274 | 12.7934 | 13.0777 | 12.5923 | 12.7909 | 12.5471 | 12.4272 | NaN | NaN | NaN | 12.8125 | 129.1358 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 540.7063 | NaN | 5.3535 | NaN | 26.635
4206.1292 | 12.9822 | 12.6857 | 12.7897 | 13.0165 | 12.6289 | 12.8023 | 12.5553 | 12.4221 | NaN | NaN | NaN | 12.835 | 117.1496 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 537.0864 | NaN | 8.3049 | NaN | 18.8448
4207.1292 | 12.9501 | 12.6882 | 12.7857 | 13.0877 | 12.607 | 12.795 | 12.5568 | 12.4305 | NaN | NaN | NaN | 12.8232 | 119.2469 | NaN | NaN | NaN | 1.0403 | NaN | NaN | NaN | NaN | 532.7854 | NaN | 19.2376 | NaN | 23.9088
4208.1292 | 12.9428 | 12.6754 | 12.7838 | 13.0677 | 12.5837 | 12.7981 | 12.5536 | 12.4298 | NaN | NaN | NaN | 12.8597 | 124.731 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 534.069 | NaN | 28.0918 | NaN | 22.4865
4209.1292 | 12.9281 | 12.6524 | 12.7752 | 13.074 | 12.6263 | 12.7858 | 12.5511 | 12.4295 | NaN | NaN | NaN | 12.8425 | 119.5424 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 535.2091 | NaN | 34.408 | NaN | 25.5375
4210.1292 | 12.9657 | 12.6313 | 12.7746 | 13.0415 | 12.6033 | 12.7784 | 12.5486 | 12.428 | NaN | NaN | NaN | 12.8159 | 121.2295 | NaN | NaN | NaN | -19.9974 | NaN | NaN | NaN | NaN | 535.1613 | NaN | 4.5195 | NaN | 21.8635
4211.1292 | 12.9794 | 12.6132 | 12.7847 | 13.0785 | 12.601 | 12.7679 | 12.5513 | 12.4245 | NaN | NaN | NaN | 12.8565 | 124.9991 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 532.82 | NaN | 5.3084 | NaN | 23.4672
4212.1292 | 12.9809 | 12.6286 | 12.7766 | 13.1 | 12.623 | 12.7821 | 12.5456 | 12.4264 | NaN | NaN | NaN | 12.8094 | 123.481 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 534.8062 | NaN | 5.4142 | NaN | 23.9175
4213.1292 | 12.9657 | 12.6369 | 12.7719 | 13.0588 | 12.6073 | 12.79 | 12.555 | 12.4157 | NaN | NaN | NaN | 12.8402 | 119.0669 | NaN | NaN | NaN | 1.2232 | NaN | NaN | NaN | NaN | 537.5609 | NaN | 28.3692 | NaN | 24.1312
4214.1292 | 12.982 | 12.6318 | 12.7775 | 13.052 | 12.5184 | 12.7894 | 12.5517 | 12.4204 | NaN | NaN | NaN | 12.8458 | 126.476 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 534.4396 | NaN | 28.4673 | NaN | 14.9511
4215.1292 | 12.9508 | 12.681 | 12.779 | 13.141 | 12.6161 | 12.8052 | 12.5652 | 12.4214 | NaN | NaN | NaN | 12.8327 | 116.975 | NaN | NaN | NaN | -13.2164 | NaN | NaN | NaN | NaN | 534.1457 | NaN | 24.0031 | NaN | 24.1265
4216.1292 | 12.9484 | 12.6879 | 12.7828 | 13.0824 | 12.5853 | 12.8028 | 12.5625 | 12.4267 | NaN | NaN | NaN | 12.8807 | 124.0449 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 536.013 | NaN | 30.9177 | NaN | 26.0676
4217.1292 | 12.9469 | 12.6418 | 12.7853 | 13.1926 | 12.5937 | 12.8022 | 12.5574 | 12.4179 | NaN | NaN | NaN | 12.8225 | 125.2929 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 537.0566 | NaN | 25.1477 | NaN | 21.7884
4218.1292 | 12.9449 | 12.6159 | 12.7833 | 13.0612 | 12.638 | 12.7825 | 12.5556 | 12.4221 | NaN | NaN | NaN | 12.838 | 130.6763 | NaN | NaN | NaN | -3.0886 | NaN | NaN | NaN | NaN | 539.7733 | NaN | 4.7133 | NaN | 27.1801
4219.1292 | 12.935 | 12.6068 | 12.7849 | 13.0783 | 12.5549 | 12.776 | 12.5568 | 12.4221 | NaN | NaN | NaN | 12.857 | 130.6622 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 534.4867 | NaN | 15.6424 | NaN | 24.7052
4220.1292 | 12.9074 | 12.6367 | 12.785 | 13.0645 | 12.6178 | 12.7981 | 12.5669 | 12.43 | NaN | NaN | NaN | 12.8745 | 120.2465 | NaN | NaN | NaN | 3.7101 | NaN | NaN | NaN | NaN | 537.0845 | NaN | 4.0429 | NaN | 28.5925
4221.1292 | 12.9831 | 12.6928 | 12.7872 | 13.0858 | 12.5517 | 12.8105 | 12.5705 | 12.4189 | NaN | NaN | NaN | 12.828 | 124.205 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 539.4152 | NaN | 6.5834 | NaN | 22.0555
4222.1292 | 13.0097 | 12.7251 | 12.7873 | 13.1019 | 12.6418 | 12.8299 | 12.5935 | 12.4273 | NaN | NaN | NaN | 12.8491 | 129.6931 | NaN | NaN | NaN | 3.3472 | NaN | NaN | NaN | NaN | 538.0199 | NaN | 3.9298 | NaN | 22.884
4223.1292 | 12.9961 | 12.6814 | 12.7911 | 13.0582 | 12.6101 | 12.7925 | 12.5744 | 12.4156 | NaN | NaN | NaN | 12.826 | 126.5365 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 539.9132 | NaN | 3.8999 | NaN | 30.4841
4224.1292 | 12.9504 | 12.6314 | 12.789 | 13.0457 | 12.5946 | 12.7809 | 12.5578 | 12.4174 | NaN | NaN | NaN | 12.8611 | 133.3387 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 539.6498 | NaN | 9.6981 | NaN | 20.4022
4225.1292 | 12.9106 | 12.6579 | 12.7848 | 13.096 | 12.6178 | 12.7947 | 12.5733 | 12.4165 | NaN | NaN | NaN | 12.834 | 125.9899 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 539.3787 | NaN | 16.8992 | NaN | 28.5525
4226.1292 | 12.9615 | 12.6731 | 12.7849 | 13.0802 | 12.5547 | 12.7925 | 12.5754 | 12.4152 | NaN | NaN | NaN | 12.8296 | 118.0061 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 540.6019 | NaN | 4.8508 | NaN | 25.2423
4227.1292 | 12.9103 | 12.6701 | 12.7885 | 13.0614 | 12.5748 | 12.7727 | 12.5685 | 12.4162 | NaN | NaN | NaN | 12.8501 | 123.6026 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 540.6154 | NaN | 14.7102 | NaN | 21.4519
4228.1292 | 12.9263 | 12.6348 | 12.7895 | 13.0755 | 12.6189 | 12.7594 | 12.5542 | 12.4135 | NaN | NaN | NaN | 12.8511 | 132.3108 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 541.9613 | NaN | 12.2012 | NaN | 25.7554
4229.1292 | 12.9248 | 12.6756 | 12.7905 | 13.0521 | 12.6397 | 12.7909 | 12.5721 | 12.4133 | NaN | NaN | NaN | 12.8585 | 131.4643 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 542.7684 | NaN | 26.5412 | NaN | 19.0957
4230.1292 | 12.9182 | 12.7252 | 12.7884 | 13.0858 | 12.6042 | 12.7919 | 12.5638 | 12.4182 | NaN | NaN | NaN | 12.8643 | 114.8783 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 543.2982 | NaN | 4.2426 | NaN | 17.2346
4231.1292 | 12.9499 | 12.6706 | 12.7915 | 13.1022 | 12.5672 | 12.7764 | 12.5566 | 12.4079 | NaN | NaN | NaN | 12.8282 | 124.591 | NaN | NaN | NaN | -12.6417 | NaN | NaN | NaN | NaN | 543.4864 | NaN | 4.9301 | NaN | 24.7807
4232.1292 | 12.9579 | 12.6993 | 12.7935 | 13.0787 | 12.6077 | 12.7851 | 12.5532 | 12.4085 | NaN | NaN | NaN | 12.8348 | 127.8643 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 542.2616 | NaN | 32.714 | NaN | 29.1048
4233.1292 | 12.9485 | 12.7082 | 12.796 | 13.0691 | 12.6104 | 12.8019 | 12.5502 | 12.41 | NaN | NaN | NaN | 12.8385 | 118.7021 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 546.043 | NaN | 6.4518 | NaN | 24.4928
4234.1292 | 12.9523 | 12.7433 | 12.7898 | 13.0486 | 12.6106 | 12.7967 | 12.5636 | 12.4033 | NaN | NaN | NaN | 12.8299 | 127.7784 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 546.7816 | NaN | 6.9191 | NaN | 27.2016
4235.1292 | 12.9495 | 12.7305 | 12.7906 | 13.1383 | 12.5835 | 12.8239 | 12.5641 | 12.4046 | NaN | NaN | NaN | 12.8553 | 131.5943 | NaN | NaN | NaN | -17.4094 | NaN | NaN | NaN | NaN | 546.4511 | NaN | 6.4572 | NaN | 19.7132
4236.1292 | 12.9493 | 12.6705 | 12.7794 | 13.1124 | 12.6079 | 12.7858 | 12.5479 | 12.4004 | NaN | NaN | NaN | 12.8513 | 124.0542 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 545.4116 | NaN | 12.4763 | NaN | 14.3319
4237.1292 | 12.9545 | 12.7114 | 12.7838 | 13.0803 | 12.6555 | 12.8029 | 12.5583 | 12.4158 | NaN | NaN | NaN | 12.8908 | 130.0984 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 549.1017 | NaN | 5.4492 | NaN | 22.3802
4238.1292 | 12.938 | 12.6658 | 12.7898 | 13.1089 | 12.649 | 12.7749 | 12.5394 | 12.4074 | NaN | NaN | NaN | 12.8619 | 125.0581 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 548.1908 | NaN | 8.9175 | NaN | 27.6375
4239.1292 | 12.9841 | 12.7098 | 12.7899 | 13.0563 | 12.6152 | 12.7905 | 12.5555 | 12.4089 | NaN | NaN | NaN | 12.8336 | 123.8464 | NaN | NaN | NaN | 2.0906 | NaN | NaN | NaN | NaN | 548.62 | NaN | 31.5476 | NaN | 25.5565
4240.1292 | 12.9188 | 12.7146 | 12.7939 | 13.1009 | 12.6351 | 12.807 | 12.5539 | 12.4075 | NaN | NaN | NaN | 12.8632 | 123.759 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 550.5865 | NaN | 8.2164 | NaN | 26.2735
4241.1292 | 13.08 | 12.6649 | 12.7922 | 13.0694 | 12.5789 | 12.786 | 12.5595 | 12.4089 | NaN | NaN | NaN | 12.845 | 125.0015 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 552.2486 | NaN | 30.2294 | NaN | 27.075
4242.1292 | 12.9439 | 12.6877 | 12.7955 | 13.1036 | 12.6414 | 12.7904 | 12.5571 | 12.4059 | NaN | NaN | NaN | 12.8984 | 128.2709 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 550.906 | NaN | 5.0763 | NaN | 24.5198
4243.1292 | 12.9371 | 12.6931 | 12.7944 | 13.0759 | 12.5704 | 12.8154 | 12.5543 | 12.4137 | NaN | NaN | NaN | 12.8696 | 122.1574 | NaN | NaN | NaN | 1.1 | NaN | NaN | NaN | NaN | 550.2186 | NaN | 17.2152 | NaN | 26.7537
4244.1292 | 12.9479 | 12.6619 | 12.7942 | 13.121 | 12.6571 | 12.7872 | 12.5472 | 12.4109 | NaN | NaN | NaN | 12.8613 | 130.7342 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 550.0991 | NaN | 7.6057 | NaN | 24.5615
4245.1292 | 12.9353 | 12.7798 | 12.8 | 13.0891 | 12.5812 | 12.8589 | 12.5769 | 12.4107 | NaN | NaN | NaN | 12.8766 | 121.9596 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 550.7278 | NaN | 36.9247 | NaN | 24.161
4246.1292 | 13.0097 | 12.6962 | 12.809 | 13.0947 | 12.6504 | 12.8113 | 12.5682 | 12.4108 | NaN | NaN | NaN | 12.8565 | 123.7637 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 550.0284 | NaN | 22.839 | NaN | 25.3752
4247.1292 | 12.9183 | 12.7027 | 12.8037 | 13.1007 | 12.6081 | 12.8182 | 12.5639 | 12.4125 | NaN | NaN | NaN | 12.8288 | 127.9883 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 552.9682 | NaN | 13.8661 | NaN | 30.3189
4248.1292 | 12.9736 | 12.6525 | 12.7965 | 13.1938 | 12.6515 | 12.7943 | 12.5583 | 12.4074 | NaN | NaN | NaN | 12.8478 | 118.9612 | NaN | NaN | NaN | -19.4464 | NaN | NaN | NaN | NaN | 552.4316 | NaN | 10.9842 | NaN | 24.0795
4249.1292 | 12.9642 | 12.7264 | 12.7891 | 13.1063 | 12.6264 | 12.8155 | 12.575 | 12.4112 | NaN | NaN | NaN | 12.8313 | 116.8567 | NaN | NaN | NaN | 3.6062 | NaN | NaN | NaN | NaN | 552.8582 | NaN | 11.1938 | NaN | 19.5825
4250.1292 | 12.953 | 12.6973 | 12.7831 | 13.1082 | 12.6638 | 12.8055 | 12.5645 | 12.4162 | NaN | NaN | NaN | 12.8342 | 131.0476 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 551.8204 | NaN | 4.3529 | NaN | 24.1793
4251.1292 | 12.9455 | 12.6664 | 12.7847 | 13.1119 | 12.5442 | 12.8015 | 12.5544 | 12.4133 | NaN | NaN | NaN | 12.8401 | 120.7334 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 553.3598 | NaN | 10.9425 | NaN | 26.0491
4252.1292 | 12.9555 | 12.6564 | 12.7856 | 13.074 | 12.6043 | 12.7963 | 12.5558 | 12.4147 | NaN | NaN | NaN | 12.8348 | 132.9586 | NaN | NaN | NaN | -12.3719 | NaN | NaN | NaN | NaN | 552.7618 | NaN | 11.9254 | NaN | 20.0947
4253.1292 | 12.9576 | 12.6699 | 12.7855 | 13.1509 | 12.5935 | 12.8029 | 12.5619 | 12.4079 | NaN | NaN | NaN | 12.8528 | 122.4296 | NaN | NaN | NaN | -5.1613 | NaN | NaN | NaN | NaN | 553.0343 | NaN | 8.8363 | NaN | 12.5946
4254.1292 | 12.9544 | 12.654 | 12.7878 | 13.0676 | 12.6645 | 12.7985 | 12.5556 | 12.4104 | NaN | NaN | NaN | 12.8711 | 139.8085 | NaN | NaN | NaN | -10.2457 | NaN | NaN | NaN | NaN | 551.2989 | NaN | 5.054 | NaN | 29.3798
4255.1292 | 12.9486 | 12.6517 | 12.783 | 13.0726 | 12.6015 | 12.7961 | 12.5518 | 12.408 | NaN | NaN | NaN | 12.8546 | 127.2158 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 552.0202 | NaN | 19.5253 | NaN | 26.3252
4256.1292 | 12.9558 | 12.7139 | 12.788 | 13.1024 | 12.5852 | 12.8371 | 12.5649 | 12.4075 | NaN | NaN | NaN | 12.8677 | 121.0867 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 552.8422 | NaN | 13.8821 | NaN | 19.3876
4257.1292 | 12.9387 | 12.6737 | 12.7829 | 13.1263 | 12.5722 | 12.8141 | 12.565 | 12.4162 | NaN | NaN | NaN | 12.8342 | 124.6755 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 551.4104 | NaN | 28.1332 | NaN | 12.9814
4258.1292 | 12.9424 | 12.6867 | 12.794 | 13.0676 | 12.5695 | 12.8366 | 12.5706 | 12.4147 | NaN | NaN | NaN | 12.8558 | 135.8859 | NaN | NaN | NaN | 2.4972 | NaN | NaN | NaN | NaN | 549.9635 | NaN | 5.8028 | NaN | 26.3059
4259.1292 | 12.9563 | 12.6517 | 12.7873 | 13.1277 | 12.5736 | 12.8118 | 12.5725 | 12.4104 | NaN | NaN | NaN | 12.863 | 123.7604 | NaN | NaN | NaN | -19.2616 | NaN | NaN | NaN | NaN | 548.8416 | NaN | 5.6138 | NaN | 25.8951
4260.1292 | 12.9863 | 12.7031 | 12.7863 | 13.1266 | 12.5627 | 12.8418 | 12.5884 | 12.4151 | NaN | NaN | NaN | 12.8698 | 124.5031 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 548.81 | NaN | 11.2061 | NaN | 24.142
4261.1292 | 12.9685 | 12.6975 | 12.7874 | 13.1087 | 12.6066 | 12.8582 | 12.5829 | 12.4184 | NaN | NaN | NaN | 12.8511 | 119.8447 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 548.1895 | NaN | 12.7484 | NaN | 27.7921
4262.1292 | 13.0045 | 12.6932 | 12.7905 | 13.0955 | 12.628 | 12.8353 | 12.5883 | 12.4224 | NaN | NaN | NaN | 12.8695 | 136.3466 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 549.0354 | NaN | 5.9089 | NaN | 32.0431
4263.1292 | 13.0325 | 12.6771 | 12.7868 | 13.1018 | 12.5711 | 12.8332 | 12.5832 | 12.4213 | NaN | NaN | NaN | 12.8278 | 124.6718 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 549.0302 | NaN | 13.2356 | NaN | 24.9418
4264.1292 | 12.9533 | 12.8118 | 12.7896 | 13.0634 | 12.6469 | 12.8501 | 12.6111 | 12.4251 | NaN | NaN | NaN | 12.9017 | 124.1173 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 549.2676 | NaN | 4.5003 | NaN | 28.0899
4265.1292 | 12.9713 | 12.6431 | 12.7842 | 13.1165 | 12.6189 | 12.8004 | 12.5768 | 12.4267 | NaN | NaN | NaN | 12.8594 | 132.9422 | NaN | NaN | NaN | -19.1396 | NaN | NaN | NaN | NaN | 547.811 | NaN | 23.3581 | NaN | 24.9788
4266.1292 | 12.9632 | 12.6504 | 12.7911 | 13.1741 | 12.521 | 12.8123 | 12.5825 | 12.4233 | NaN | NaN | NaN | 12.9362 | 118.7549 | NaN | NaN | NaN | -10.5827 | NaN | NaN | NaN | NaN | 548.3056 | NaN | 19.2106 | NaN | 16.7041
4267.1292 | 12.9771 | 12.6632 | 12.7848 | 13.0863 | 12.5558 | 12.8093 | 12.5839 | 12.4267 | NaN | NaN | NaN | 12.8884 | 131.2057 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 547.1773 | NaN | 5.4643 | NaN | 24.1407
4268.1292 | 13.0158 | 12.7555 | 12.795 | 13.0927 | 12.5357 | 12.872 | 12.5962 | 12.4336 | NaN | NaN | NaN | 12.838 | 122.7684 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 549.652 | NaN | 5.0754 | NaN | 25.6787
4269.1292 | 12.948 | 12.7528 | 12.7917 | 13.1351 | 12.666 | 12.8496 | 12.6105 | 12.4403 | NaN | NaN | NaN | 12.8635 | 121.7629 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 548.817 | NaN | 20.0795 | NaN | 14.9707
4270.1292 | 12.9942 | 12.6808 | 12.7924 | 13.0812 | 12.618 | 12.824 | 12.5828 | 12.431 | NaN | NaN | NaN | 12.8566 | 117.8446 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 551.5171 | NaN | 4.7027 | NaN | 17.1465
4271.1292 | 12.993 | 12.6435 | 12.7956 | 13.0728 | 12.5384 | 12.8099 | 12.5851 | 12.4368 | NaN | NaN | NaN | 12.8858 | 119.6994 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 552.0819 | NaN | 9.6459 | NaN | 28.1436
4272.1292 | 12.9923 | 12.6588 | 12.8038 | 13.1093 | 12.6471 | 12.8212 | 12.5878 | 12.4314 | NaN | NaN | NaN | 12.8604 | 123.6608 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 549.0627 | NaN | 18.7304 | NaN | 26.5043
4273.1292 | 12.9923 | 12.6572 | 12.8012 | 13.0972 | 12.6029 | 12.8135 | 12.5866 | 12.4314 | NaN | NaN | NaN | 12.8501 | 127.9112 | NaN | NaN | NaN | -17.9526 | NaN | NaN | NaN | NaN | 549.4685 | NaN | 3.3034 | NaN | 28.5289
4274.1292 | 12.9845 | 12.6946 | 12.8005 | 13.1432 | 12.5986 | 12.8357 | 12.6 | 12.4331 | NaN | NaN | NaN | 12.8957 | 110.9274 | NaN | NaN | NaN | -2.1428 | NaN | NaN | NaN | NaN | 547.4234 | NaN | 30.9349 | NaN | 19.2438
4275.1292 | 12.9816 | 12.7182 | 12.8005 | 13.1112 | 12.617 | 12.8314 | 12.5948 | 12.4374 | NaN | NaN | NaN | 12.8878 | 118.8485 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 545.0401 | NaN | 25.5859 | NaN | 23.155
4276.1292 | 12.9446 | 12.6519 | 12.7952 | 13.1377 | 12.5135 | 12.8097 | 12.584 | 12.4276 | NaN | NaN | NaN | 12.8528 | 117.0656 | NaN | NaN | NaN | -0.1441 | NaN | NaN | NaN | NaN | 543.1027 | NaN | 22.0325 | NaN | 28.8415
4277.1292 | 13.045 | 12.7065 | 12.7971 | 13.0855 | 12.6222 | 12.8319 | 12.6009 | 12.4243 | NaN | NaN | NaN | 12.8351 | 133.5578 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 541.9183 | NaN | 24.4039 | NaN | 26.5361
4278.1292 | 13.0029 | 12.6537 | 12.7965 | 13.0784 | 12.6672 | 12.8069 | 12.5994 | 12.4258 | NaN | NaN | NaN | 12.8476 | 116.012 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 546.2527 | NaN | 9.9496 | NaN | 22.3338
4279.1292 | 12.9855 | 12.6484 | 12.796 | 13.1106 | 12.672 | 12.8124 | 12.5982 | 12.427 | NaN | NaN | NaN | 12.8488 | 130.3082 | NaN | NaN | NaN | -6.3889 | NaN | NaN | NaN | NaN | 542.9623 | NaN | 12.4237 | NaN | 24.1405
4280.1292 | 12.985 | 12.6439 | 12.7938 | 13.0674 | 12.5553 | 12.8019 | 12.6 | 12.4305 | NaN | NaN | NaN | 12.8626 | 130.6456 | NaN | NaN | NaN | -17.7651 | NaN | NaN | NaN | NaN | 543.4161 | NaN | 12.3628 | NaN | 25.9699
4281.1292 | 12.9678 | 12.6477 | 12.7993 | 13.0543 | 12.5863 | 12.8231 | 12.5991 | 12.4274 | NaN | NaN | NaN | 12.847 | 121.2504 | NaN | NaN | NaN | 1.2481 | NaN | NaN | NaN | NaN | 545.6641 | NaN | 4.2645 | NaN | 22.8107
4282.1292 | 13.0878 | 12.6424 | 12.7979 | 13.1096 | 12.6233 | 12.8176 | 12.5922 | 12.427 | NaN | NaN | NaN | 12.8449 | 120.268 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 541.75 | NaN | 5.5296 | NaN | 24.3983
4283.1292 | 12.9605 | 12.6475 | 12.7963 | 13.0787 | 12.6666 | 12.8144 | 12.6059 | 12.4259 | NaN | NaN | NaN | 12.8686 | 128.4232 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 542.0588 | NaN | 3.8424 | NaN | 10.617
4284.1292 | 12.9668 | 12.7137 | 12.7985 | 13.0442 | 12.5879 | 12.8703 | 12.6238 | 12.4252 | NaN | NaN | NaN | 12.8799 | 123.5843 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 542.8068 | NaN | 4.1175 | NaN | 27.4388
4285.1292 | 12.9562 | 12.629 | 12.8016 | 13.0678 | 12.5981 | 12.7989 | 12.6083 | 12.4237 | NaN | NaN | NaN | 12.8415 | 121.3982 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 544.9964 | NaN | 8.642 | NaN | 27.4235
4286.1292 | 12.9563 | 12.624 | 12.7945 | 13.0657 | 12.6204 | 12.7937 | 12.6017 | 12.4224 | NaN | NaN | NaN | 12.8542 | 132.4533 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 543.9119 | NaN | 19.1428 | NaN | 27.5122
4287.1292 | 12.9672 | 12.6208 | 12.8013 | 13.0918 | 12.6556 | 12.79 | 12.597 | 12.4277 | NaN | NaN | NaN | 12.8784 | 124.2862 | NaN | NaN | NaN | -17.4034 | NaN | NaN | NaN | NaN | 541.2977 | NaN | 14.5563 | NaN | 15.2809
4288.1292 | 12.9599 | 12.6405 | 12.8036 | 13.0433 | 12.5762 | 12.8157 | 12.6117 | 12.4162 | NaN | NaN | NaN | 12.8814 | 122.8715 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 541.0729 | NaN | 9.1039 | NaN | 15.8976
4289.1292 | 12.9717 | 12.6113 | 12.803 | 13.1262 | 12.6561 | 12.7839 | 12.5928 | 12.4268 | NaN | NaN | NaN | 12.8479 | 117.3833 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 544.1546 | NaN | 7.7685 | NaN | 22.229
4290.1292 | 12.9735 | 12.6329 | 12.8043 | 13.0688 | 12.5302 | 12.8047 | 12.6048 | 12.4279 | NaN | NaN | NaN | 12.8523 | 133.6267 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 539.8148 | NaN | 10.9863 | NaN | 24.2208
4291.1292 | 12.9613 | 12.6457 | 12.811 | 13.0838 | 12.6165 | 12.8145 | 12.606 | 12.4267 | NaN | NaN | NaN | 12.8881 | 115.7319 | NaN | NaN | NaN | 1.5433 | NaN | NaN | NaN | NaN | 541.7603 | NaN | 37.5882 | NaN | 15.4184
4292.1292 | 12.9673 | 12.7235 | 12.8057 | 13.1032 | 12.5108 | 12.8694 | 12.6232 | 12.435 | NaN | NaN | NaN | 12.8599 | 133.2608 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 539.0859 | NaN | 32.6374 | NaN | 22.7025
4293.1292 | 12.9599 | 12.6095 | 12.8088 | 13.0793 | 12.5726 | 12.7959 | 12.6019 | 12.4291 | NaN | NaN | NaN | 12.8561 | 120.4295 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 531.7379 | NaN | 33.108 | NaN | 24.0823
4294.1292 | 12.9922 | 12.6437 | 12.8056 | 13.0441 | 12.5604 | 12.8079 | 12.6087 | 12.4337 | NaN | NaN | NaN | 12.8298 | 127.0765 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 536.3758 | NaN | 14.9712 | NaN | 26.6686
4295.1292 | 13.0373 | 12.6216 | 12.8071 | 13.0675 | 12.5859 | 12.7975 | 12.6054 | 12.4378 | NaN | NaN | NaN | 12.8427 | 116.17 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 538.2448 | NaN | 36.1823 | NaN | 22.2929
4296.1292 | 12.9595 | 12.6427 | 12.8025 | 13.0496 | 12.578 | 12.8077 | 12.5987 | 12.4385 | NaN | NaN | NaN | 12.8417 | 125.8729 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 539.9603 | NaN | 6.3054 | NaN | 16.1583
4297.1292 | 12.9613 | 12.6009 | 12.8012 | 13.0848 | 12.6469 | 12.7825 | 12.5905 | 12.4386 | NaN | NaN | NaN | 12.8344 | 120.9648 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 538.3036 | NaN | 7.6455 | NaN | 25.1987
4298.1292 | 12.9542 | 12.6262 | 12.8063 | 13.0889 | 12.6185 | 12.8208 | 12.5986 | 12.4415 | NaN | NaN | NaN | 12.9504 | 126.8229 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 537.8125 | NaN | 6.2944 | NaN | 16.0611
4299.1292 | 12.9509 | 12.6238 | 12.8007 | 13.1068 | 12.5388 | 12.8002 | 12.5934 | 12.4453 | NaN | NaN | NaN | 12.8444 | 127.1788 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 536.044 | NaN | 11.901 | NaN | 21.3548
4300.1292 | 12.9217 | 12.6328 | 12.803 | 13.094 | 12.5081 | 12.7894 | 12.5906 | 12.449 | NaN | NaN | NaN | 12.8308 | 132.9412 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 538.5782 | NaN | 30.0877 | NaN | 26.5358
4301.1292 | 12.9696 | 12.6039 | 12.7958 | 13.0792 | 12.6085 | 12.7793 | 12.5915 | 12.4461 | NaN | NaN | NaN | 12.8488 | 120.2228 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 539.5362 | NaN | 4.9237 | NaN | 10.2105
4302.1292 | 12.9764 | 12.6162 | 12.8012 | 13.0777 | 12.5288 | 12.7959 | 12.5943 | 12.4479 | NaN | NaN | NaN | 12.8401 | 130.9628 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 536.7635 | NaN | 9.739 | NaN | 20.2371
4303.1292 | 12.9611 | 12.6658 | 12.805 | 13.0652 | 12.5855 | 12.8138 | 12.601 | 12.4455 | NaN | NaN | NaN | 12.8754 | 118.7543 | NaN | NaN | NaN | -17.3979 | NaN | NaN | NaN | NaN | 537.9794 | NaN | 8.4186 | NaN | 13.2585
4304.1292 | 12.9559 | 12.6484 | 12.7996 | 13.0407 | 12.5345 | 12.8339 | 12.5987 | 12.4413 | NaN | NaN | NaN | 12.8793 | 121.5109 | NaN | NaN | NaN | -12.6351 | NaN | NaN | NaN | NaN | 539.3096 | NaN | 6.1363 | NaN | 22.736
4305.1292 | 12.9806 | 12.6581 | 12.8045 | 13.0432 | 12.6146 | 12.8263 | 12.6121 | 12.4419 | NaN | NaN | NaN | 12.8689 | 126.6944 | NaN | NaN | NaN | -18.9322 | NaN | NaN | NaN | NaN | 539.1199 | NaN | 5.4254 | NaN | 20.8133
4306.1292 | 12.9339 | 12.6369 | 12.8078 | 13.034 | 12.602 | 12.8271 | 12.5904 | 12.4405 | NaN | NaN | NaN | 12.846 | 130.9172 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 539.0089 | NaN | 14.2287 | NaN | 27.2074
4307.1292 | 13.0838 | 12.6303 | 12.8015 | 13.0634 | 12.6431 | 12.8057 | 12.5891 | 12.4399 | NaN | NaN | NaN | 12.8266 | 126.4096 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 537.9808 | NaN | 5.2133 | NaN | 21.3562
4308.1292 | 12.9811 | 12.6293 | 12.8088 | 13.0366 | 12.6499 | 12.8281 | 12.5893 | 12.4338 | NaN | NaN | NaN | 12.931 | 120.584 | NaN | NaN | NaN | 4.9922 | NaN | NaN | NaN | NaN | 536.3392 | NaN | 6.6965 | NaN | 21.3587
4309.1292 | 12.9948 | 12.641 | 12.806 | 13.0732 | 12.541 | 12.8196 | 12.5917 | 12.4353 | NaN | NaN | NaN | 12.8712 | 135.2308 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 536.4452 | NaN | 5.2583 | NaN | 18.3372
4310.1292 | 12.9964 | 12.6388 | 12.8047 | 12.9832 | 12.5516 | 12.8185 | 12.595 | 12.4364 | NaN | NaN | NaN | 12.8744 | 124.6506 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 538.3418 | NaN | 8.5099 | NaN | 16.4579
4311.1292 | 12.9906 | 12.6416 | 12.8161 | 13.0153 | 12.6009 | 12.8089 | 12.5942 | 12.4373 | NaN | NaN | NaN | 12.8512 | 128.3491 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 537.9079 | NaN | 11.4549 | NaN | 28.0176
4312.1292 | 12.9814 | 12.6697 | 12.812 | 13.0601 | 12.6257 | 12.8189 | 12.6013 | 12.4404 | NaN | NaN | NaN | 12.8466 | 122.7383 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 537.9587 | NaN | 5.3507 | NaN | 16.9787
4313.1292 | 12.9649 | 12.6354 | 12.8138 | 13.0358 | 12.6554 | 12.8061 | 12.5845 | 12.4355 | NaN | NaN | NaN | 12.8482 | 125.2087 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 536.0137 | NaN | 32.9424 | NaN | 16.4517
4314.1292 | 12.967 | 12.6765 | 12.8183 | 13.058 | 12.6141 | 12.8314 | 12.5897 | 12.4376 | NaN | NaN | NaN | 12.8379 | 125.5784 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 537.2192 | NaN | 18.6095 | NaN | 25.069
4315.1292 | 13.0104 | 12.6209 | 12.8145 | 13.038 | 12.5499 | 12.7987 | 12.5778 | 12.4333 | NaN | NaN | NaN | 12.857 | 133.2137 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 535.7245 | NaN | 11.5772 | NaN | 22.4734
4316.1292 | 13.0138 | 12.6441 | 12.8186 | 13.024 | 12.5629 | 12.8279 | 12.5781 | 12.4429 | NaN | NaN | NaN | 12.8506 | 120.4227 | NaN | NaN | NaN | -5.9816 | NaN | NaN | NaN | NaN | 539.4232 | NaN | 9.9787 | NaN | 24.0792
4317.1292 | 12.9865 | 12.6611 | 12.8225 | 13.067 | 12.4959 | 12.8313 | 12.5875 | 12.4344 | NaN | NaN | NaN | 12.85 | 114.3416 | NaN | NaN | NaN | -1.7389 | NaN | NaN | NaN | NaN | 536.9149 | NaN | 30.9643 | NaN | 25.8964
4318.1292 | 13.0603 | 12.6379 | 12.8231 | 13.0411 | 12.6077 | 12.8147 | 12.5812 | 12.4417 | NaN | NaN | NaN | 12.833 | 126.8036 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 536.9372 | NaN | 18.3401 | NaN | 23.6404
4319.1292 | 12.9848 | 12.5962 | 12.8208 | 13.0078 | 12.608 | 12.7897 | 12.5724 | 12.438 | NaN | NaN | NaN | 12.8333 | 126.5378 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 540.4375 | NaN | 25.8809 | NaN | 18.2105
4320.1292 | 12.9941 | 12.5993 | 12.8237 | 13.0248 | 12.6181 | 12.8005 | 12.5782 | 12.4301 | NaN | NaN | NaN | 12.8221 | 118.1272 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 538.8666 | NaN | 6.3899 | NaN | 29.331
4321.1292 | 12.9893 | 12.6224 | 12.8239 | 13.0548 | 12.623 | 12.8079 | 12.5838 | 12.4339 | NaN | NaN | NaN | 12.8755 | 127.9108 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 539.7922 | NaN | 35.278 | NaN | 19.0888
4322.1292 | 12.981 | 12.5901 | 12.8247 | 13.1128 | 12.6277 | 12.7991 | 12.5782 | 12.4256 | NaN | NaN | NaN | 12.8205 | 124.794 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 540.8228 | NaN | 6.0918 | NaN | 22.671
4323.1292 | 12.9755 | 12.633 | 12.8257 | 13.0406 | 12.5604 | 12.8003 | 12.5741 | 12.4335 | NaN | NaN | NaN | 12.8381 | 128.5398 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 537.4054 | NaN | 21.808 | NaN | 20.3032
4324.1292 | 12.9842 | 12.6211 | 12.8209 | 13.0239 | 12.5835 | 12.8125 | 12.5823 | 12.435 | NaN | NaN | NaN | 12.9111 | 119.7832 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 539.1951 | NaN | 9.5143 | NaN | 24.1817
4325.1292 | 12.9766 | 12.6078 | 12.8248 | 13.061 | 12.58 | 12.7973 | 12.5733 | 12.4322 | NaN | NaN | NaN | 12.8265 | 122.4127 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 536.6222 | NaN | 5.7641 | NaN | 20.0061
4326.1292 | 12.9861 | 12.6037 | 12.829 | 13.0661 | 12.5916 | 12.8008 | 12.5823 | 12.428 | NaN | NaN | NaN | 12.8591 | 127.1391 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 539.747 | NaN | 18.4799 | NaN | 25.5955
4327.1292 | 12.9852 | 12.6543 | 12.8346 | 13.0061 | 12.6395 | 12.8123 | 12.5933 | 12.4281 | NaN | NaN | NaN | 12.8339 | 127.5371 | NaN | NaN | NaN | 0.5037 | NaN | NaN | NaN | NaN | 536.2685 | NaN | 32.1698 | NaN | 21.3306
4328.1292 | 12.978 | 12.6224 | 12.8293 | 13.0392 | 12.5509 | 12.8023 | 12.5828 | 12.4257 | NaN | NaN | NaN | 12.8299 | 133.4945 | NaN | NaN | NaN | -18.4031 | NaN | NaN | NaN | NaN | 536.675 | NaN | 3.8052 | NaN | 28.1769
4329.1292 | 12.9886 | 12.638 | 12.8342 | 13.0794 | 12.487 | 12.8119 | 12.5863 | 12.428 | NaN | NaN | NaN | 12.9416 | 124.4261 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 536.535 | NaN | 4.1209 | NaN | 21.3885
4330.1292 | 12.9936 | 12.6549 | 12.8287 | 13.0799 | 12.6312 | 12.8258 | 12.5856 | 12.4356 | NaN | NaN | NaN | 12.8925 | 119.4324 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 534.4695 | NaN | 12.0524 | NaN | 13.9499
4331.1292 | 12.9768 | 12.6159 | 12.8291 | 13.0533 | 12.6234 | 12.8054 | 12.583 | 12.4293 | NaN | NaN | NaN | 12.8992 | 124.4917 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 536.075 | NaN | 8.1885 | NaN | 25.4732
4332.1292 | 13.0607 | 12.6685 | 12.8364 | 13.0048 | 12.5577 | 12.8163 | 12.5825 | 12.4318 | NaN | NaN | NaN | 12.8522 | 114.2407 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 534.0666 | NaN | 29.1769 | NaN | 23.29
4333.1292 | 12.9938 | 12.6069 | 12.8272 | 13.0545 | 12.5903 | 12.7916 | 12.5802 | 12.4229 | NaN | NaN | NaN | 12.8504 | 126.6989 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 535.3146 | NaN | 5.3556 | NaN | 19.5989
4334.1292 | 12.9861 | 12.6061 | 12.8329 | 13.1007 | 12.5459 | 12.778 | 12.5826 | 12.4255 | NaN | NaN | NaN | 12.8458 | 123.5259 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 536.3902 | NaN | 5.5475 | NaN | 25.0258
4335.1292 | 13.0112 | 12.6238 | 12.8284 | 13.0684 | 12.5665 | 12.7966 | 12.5981 | 12.4317 | NaN | NaN | NaN | 12.8628 | 127.1094 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 535.6665 | NaN | 5.0383 | NaN | 22.8907
4336.1292 | 13.0017 | 12.6524 | 12.8263 | 13.0567 | 12.6187 | 12.799 | 12.5934 | 12.4274 | NaN | NaN | NaN | 12.9003 | 117.1672 | NaN | NaN | NaN | -1.7158 | NaN | NaN | NaN | NaN | 532.8711 | NaN | 4.7494 | NaN | 23.9412
4337.1292 | 13.0104 | 12.6187 | 12.8364 | 13.0785 | 12.5742 | 12.7989 | 12.5966 | 12.4283 | NaN | NaN | NaN | 12.8374 | 127.3073 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 528.6064 | NaN | 16.1697 | NaN | 16.6956
4338.1292 | 13.0077 | 12.658 | 12.8327 | 13.0343 | 12.5925 | 12.8293 | 12.6046 | 12.4239 | NaN | NaN | NaN | 12.8368 | 131.9908 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 528.4625 | NaN | 10.9605 | NaN | 28.9465
4339.1292 | 13.0027 | 12.6265 | 12.8321 | 13.0997 | 12.557 | 12.8077 | 12.592 | 12.4268 | NaN | NaN | NaN | 12.8488 | 124.2941 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 532.3043 | NaN | 15.8509 | NaN | 31.297
4340.1292 | 13.0047 | 12.6359 | 12.8355 | 13.1742 | 12.5705 | 12.8042 | 12.6021 | 12.4252 | NaN | NaN | NaN | 12.8158 | 134.9325 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 532.2003 | NaN | 29.6 | NaN | 23.742
4341.1292 | 12.9776 | 12.6284 | 12.827 | 13.0486 | 12.5197 | 12.8279 | 12.5901 | 12.4322 | NaN | NaN | NaN | 12.8356 | 119.8022 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 534.5161 | NaN | 36.5915 | NaN | 17.3074
4342.1292 | 13.048 | 12.6725 | 12.8246 | 13.0765 | 12.5388 | 12.8513 | 12.5879 | 12.4313 | NaN | NaN | NaN | 12.8397 | 115.5161 | NaN | NaN | NaN | -3.4325 | NaN | NaN | NaN | NaN | 535.7657 | NaN | 4.5529 | NaN | 22.3106
4343.1292 | 13.102 | 12.7165 | 12.8171 | 13.0818 | 12.599 | 12.849 | 12.6073 | 12.4335 | NaN | NaN | NaN | 12.8343 | 125.801 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 534.1416 | NaN | 3.266 | NaN | 25.9849
4344.1292 | 13.1057 | 12.612 | 12.8168 | 13.0997 | 12.5904 | 12.8029 | 12.5953 | 12.4356 | NaN | NaN | NaN | 12.8261 | 128.6138 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 536.8965 | NaN | 35.8348 | NaN | 24.4518
4345.1448 | 13.0277 | 12.6146 | 12.8228 | 13.0901 | 12.5257 | 12.8065 | 12.5991 | 12.4358 | NaN | NaN | NaN | 12.8204 | 122.1164 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 536.6845 | NaN | 4.5262 | NaN | 19.7743
4346.1292 | 13.0181 | 12.618 | 12.8179 | 13.0635 | 12.5466 | 12.8054 | 12.6002 | 12.4374 | NaN | NaN | NaN | 12.8355 | 126.9406 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 537.7546 | NaN | 3.6723 | NaN | 24.8092
4347.1292 | 13.0256 | 12.5826 | 12.812 | 13.0825 | 12.6441 | 12.7883 | 12.5932 | 12.4427 | NaN | NaN | NaN | 12.8283 | 121.3549 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 540.0124 | NaN | 10.2234 | NaN | 25.5966
4348.1292 | 13.0279 | 12.6083 | 12.807 | 13.1258 | 12.5806 | 12.7981 | 12.6067 | 12.4458 | NaN | NaN | NaN | 12.8349 | 127.7739 | NaN | NaN | NaN | -16.1984 | NaN | NaN | NaN | NaN | 539.0835 | NaN | 9.1604 | NaN | 16.01
4349.1292 | 13.0356 | 12.7012 | 12.8175 | 13.0663 | 12.6071 | 12.8205 | 12.6273 | 12.4473 | NaN | NaN | NaN | 12.8202 | 118.836 | NaN | NaN | NaN | -3.3708 | NaN | NaN | NaN | NaN | 539.5086 | NaN | 7.365 | NaN | 22.4387
4350.1292 | 13.0244 | 12.6356 | 12.8151 | 13.0775 | 12.5885 | 12.8082 | 12.6025 | 12.4454 | NaN | NaN | NaN | 12.8235 | 113.8788 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 537.6086 | NaN | 7.1906 | NaN | 24.9154
4351.1292 | 13.0261 | 12.6158 | 12.8149 | 13.0692 | 12.5727 | 12.8048 | 12.6085 | 12.4435 | NaN | NaN | NaN | 12.8145 | 130.4977 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 539.221 | NaN | 11.7475 | NaN | 17.6267
4352.1292 | 13.0255 | 12.6224 | 12.8191 | 13.0974 | 12.5633 | 12.8264 | 12.6117 | 12.4427 | NaN | NaN | NaN | 12.8489 | 118.0571 | NaN | NaN | NaN | 2.9869 | NaN | NaN | NaN | NaN | 536.4926 | NaN | 9.2839 | NaN | 25.9426
4353.1292 | 13.0247 | 12.597 | 12.8159 | 13.074 | 12.6475 | 12.7918 | 12.6052 | 12.4469 | NaN | NaN | NaN | 12.8589 | 118.9056 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 539.1503 | NaN | 6.5924 | NaN | 19.2893
4354.1292 | 13.0222 | 12.6504 | 12.8199 | 13.0618 | 12.6591 | 12.8024 | 12.6247 | 12.4463 | NaN | NaN | NaN | 12.8297 | 114.7568 | NaN | NaN | NaN | -16.9406 | NaN | NaN | NaN | NaN | 540.1264 | NaN | 10.3022 | NaN | 8.6701
4355.1292 | 12.9973 | 12.6049 | 12.8172 | 13.1058 | 12.5165 | 12.799 | 12.6041 | 12.4505 | NaN | NaN | NaN | 12.8198 | 114.8282 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 539.7845 | NaN | 11.7567 | NaN | 25.8208
4356.1292 | 12.9976 | 12.6119 | 12.8115 | 13.1025 | 12.603 | 12.7904 | 12.6151 | 12.4441 | NaN | NaN | NaN | 12.8213 | 124.6268 | NaN | NaN | NaN | -18.7977 | NaN | NaN | NaN | NaN | 540.183 | NaN | 34.1898 | NaN | 14.6172
4357.1292 | 13.0061 | 12.5882 | 12.8145 | 13.0637 | 12.6344 | 12.7808 | 12.6133 | 12.4486 | NaN | NaN | NaN | 12.8348 | 117.1007 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 536.8769 | NaN | 11.9085 | NaN | 21.1039
4358.1292 | 13.0375 | 12.5876 | 12.8256 | 13.1006 | 12.6417 | 12.7759 | 12.6085 | 12.4506 | NaN | NaN | NaN | 12.8371 | 126.3253 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 536.0702 | NaN | 11.5904 | NaN | 25.7484
4359.1292 | 12.9836 | 12.632 | 12.8247 | 13.1073 | 12.6281 | 12.8034 | 12.6135 | 12.4492 | NaN | NaN | NaN | 12.829 | 119.9877 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 540.816 | NaN | 12.3669 | NaN | 17.0649
4360.1292 | 13.085 | 12.6955 | 12.8223 | 13.1107 | 12.515 | 12.853 | 12.6071 | 12.4497 | NaN | NaN | NaN | 12.8178 | 135.2746 | NaN | NaN | NaN | -19.5283 | NaN | NaN | NaN | NaN | 535.6272 | NaN | 18.4462 | NaN | 27.1425
4361.1292 | 13.041 | 12.6503 | 12.8325 | 13.0779 | 12.5989 | 12.8176 | 12.6263 | 12.4546 | NaN | NaN | NaN | 12.8597 | 126.4421 | NaN | NaN | NaN | -7.6011 | NaN | NaN | NaN | NaN | 535.4408 | NaN | 7.9044 | NaN | 21.3815
4362.1292 | 13.066 | 12.5902 | 12.8277 | 13.0528 | 12.623 | 12.7868 | 12.6024 | 12.446 | NaN | NaN | NaN | 12.8456 | 128.7136 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 540.7848 | NaN | 17.3316 | NaN | 18.3772
4363.1292 | 13.0448 | 12.6851 | 12.8332 | 13.0774 | 12.5748 | 12.8653 | 12.6394 | 12.4527 | NaN | NaN | NaN | 12.8244 | 122.3531 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 536.41 | NaN | 3.8176 | NaN | 24.8435
4364.1292 | 13.091 | 12.6292 | 12.8286 | 13.0935 | 12.5895 | 12.7987 | 12.5983 | 12.4502 | NaN | NaN | NaN | 12.9173 | 121.2127 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 531.3142 | NaN | 35.1487 | NaN | 23.1817
4365.1292 | 13.002 | 12.6678 | 12.8335 | 13.0537 | 12.5413 | 12.822 | 12.6047 | 12.4562 | NaN | NaN | NaN | 12.8333 | 138.3248 | NaN | NaN | NaN | -16.3343 | NaN | NaN | NaN | NaN | 533.3201 | NaN | 3.9154 | NaN | 19.7606
4366.1292 | 13.0338 | 12.6438 | 12.8372 | 13.0724 | 12.5874 | 12.7982 | 12.6103 | 12.4536 | NaN | NaN | NaN | 12.8396 | 117.7511 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 536.5252 | NaN | 8.5895 | NaN | 17.6208
4367.1292 | 13.0258 | 12.6334 | 12.8351 | 13.1063 | 12.6583 | 12.7768 | 12.6039 | 12.4534 | NaN | NaN | NaN | 12.8693 | 129.1753 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 537.1613 | NaN | 12.3738 | NaN | 20.7878
4368.1292 | 13.0147 | 12.6488 | 12.8386 | 13.1074 | 12.6141 | 12.8009 | 12.6293 | 12.4519 | NaN | NaN | NaN | 12.8372 | 123.9075 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 538.4951 | NaN | 32.5733 | NaN | 25.7726
4369.1292 | 13.0245 | 12.6531 | 12.8376 | 13.0847 | 12.5291 | 12.8123 | 12.6207 | 12.4479 | NaN | NaN | NaN | 12.8651 | 123.2936 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 539.5937 | NaN | 5.9464 | NaN | 26.5722
4370.1292 | 13.0144 | 12.6897 | 12.8423 | 13.1268 | 12.5333 | 12.8172 | 12.6197 | 12.454 | NaN | NaN | NaN | 12.871 | 118.3852 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 539.2704 | NaN | 11.9924 | NaN | 10.5984
4371.1292 | 13.0204 | 12.592 | 12.8428 | 13.0892 | 12.642 | 12.7733 | 12.603 | 12.4547 | NaN | NaN | NaN | 12.8558 | 131.9194 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 542.8916 | NaN | 5.6221 | NaN | 17.32
4372.1292 | 12.9865 | 12.6419 | 12.8414 | 13.0959 | 12.5341 | 12.7891 | 12.6107 | 12.455 | NaN | NaN | NaN | 12.8377 | 123.5765 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 539.7368 | NaN | 5.82 | NaN | 23.6623
4373.1292 | 13.0866 | 12.6329 | 12.8409 | 13.0646 | 12.5989 | 12.7933 | 12.6015 | 12.4539 | NaN | NaN | NaN | 12.8342 | 127.5219 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 537.4234 | NaN | 22.1837 | NaN | 27.4731
4374.1292 | 13.0967 | 12.6621 | 12.8507 | 13.0992 | 12.5608 | 12.7946 | 12.6071 | 12.4533 | NaN | NaN | NaN | 12.8185 | 116.7305 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 539.7533 | NaN | 5.6051 | NaN | 20.5052
4375.1292 | 13.0592 | 12.6286 | 12.8501 | 13.087 | 12.6089 | 12.7868 | 12.6029 | 12.453 | NaN | NaN | NaN | 12.8356 | 125.0955 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 538.514 | NaN | 4.1336 | NaN | 22.6867
4376.1292 | 13.0289 | 12.7119 | 12.853 | 13.0505 | 12.5915 | 12.7969 | 12.6168 | 12.4573 | NaN | NaN | NaN | 12.8896 | 124.6886 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 542.0132 | NaN | 5.4318 | NaN | 24.6966
4377.1292 | 13.0182 | 12.637 | 12.8526 | 13.0949 | 12.6422 | 12.7705 | 12.6099 | 12.4592 | NaN | NaN | NaN | 12.8386 | 120.7734 | NaN | NaN | NaN | -11.1093 | NaN | NaN | NaN | NaN | 538.4492 | NaN | 5.6644 | NaN | 18.9414
4378.1292 | 13.0035 | 12.6746 | 12.8539 | 13.1079 | 12.6633 | 12.7944 | 12.6222 | 12.4531 | NaN | NaN | NaN | 12.8947 | 132.1446 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 539.7386 | NaN | 7.9819 | NaN | 24.2697
4379.1292 | 13.0086 | 12.6396 | 12.847 | 13.1139 | 12.6588 | 12.7802 | 12.6113 | 12.4487 | NaN | NaN | NaN | 12.8371 | 121.2614 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 537.7453 | NaN | 4.7851 | NaN | 25.045
4380.1292 | 13.0652 | 12.7231 | 12.8581 | 13.0644 | 12.5971 | 12.8017 | 12.6328 | 12.4554 | NaN | NaN | NaN | 12.8414 | 123.3632 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 539.8721 | NaN | 4.2346 | NaN | 22.9388
4381.1292 | 13.0287 | 12.6914 | 12.8585 | 13.072 | 12.5675 | 12.7952 | 12.6178 | 12.4545 | NaN | NaN | NaN | 12.8705 | 130.6989 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 539.0797 | NaN | 3.7576 | NaN | 23.6625
4382.1292 | 13.0086 | 12.6687 | 12.8587 | 13.1137 | 12.6509 | 12.7694 | 12.6146 | 12.4594 | NaN | NaN | NaN | 12.8609 | 124.4438 | NaN | NaN | NaN | -17.5482 | NaN | NaN | NaN | NaN | 537.9468 | NaN | 18.5361 | NaN | 23.1744
4383.1292 | 13.0069 | 12.6827 | 12.8606 | 13.0905 | 12.6211 | 12.7873 | 12.6191 | 12.4599 | NaN | NaN | NaN | 12.8838 | 121.537 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 539.562 | NaN | 22.9588 | NaN | 24.7695
4384.1292 | 13.0108 | 12.6535 | 12.8588 | 13.0937 | 12.6577 | 12.7759 | 12.6144 | 12.4544 | NaN | NaN | NaN | 12.8643 | 113.2857 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 539.3781 | NaN | 7.4678 | NaN | 21.4555
4385.1292 | 13.0172 | 12.6549 | 12.8631 | 13.0653 | 12.5801 | 12.7831 | 12.6137 | 12.4588 | NaN | NaN | NaN | 12.9027 | 122.3604 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 538.7796 | NaN | 32.5863 | NaN | 19.8
4386.1292 | 13.0549 | 12.6733 | 12.8569 | 13.0901 | 12.6021 | 12.7845 | 12.6113 | 12.4626 | NaN | NaN | NaN | 12.8753 | 123.8352 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 538.4604 | NaN | 22.8711 | NaN | 22.2602
4387.1292 | 13.0483 | 12.6714 | 12.8621 | 13.1068 | 12.5961 | 12.7836 | 12.6144 | 12.4609 | NaN | NaN | NaN | 12.8743 | 124.8981 | NaN | NaN | NaN | -2.1281 | NaN | NaN | NaN | NaN | 540.4033 | NaN | 21.3999 | NaN | 20.269
4388.1292 | 13.0384 | 12.6594 | 12.8558 | 13.06 | 12.5793 | 12.7768 | 12.6067 | 12.4627 | NaN | NaN | NaN | 12.8854 | 125.8215 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 538.477 | NaN | 28.934 | NaN | 30.6693
4389.1292 | 13.0279 | 12.8139 | 12.862 | 13.0953 | 12.5468 | 12.8887 | 12.6532 | 12.4646 | NaN | NaN | NaN | 12.8423 | 118.7216 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 541.7607 | NaN | 7.9128 | NaN | 21.3284
4390.1292 | 13.0216 | 12.6602 | 12.8609 | 13.1355 | 12.5451 | 12.7884 | 12.6073 | 12.4607 | NaN | NaN | NaN | 12.8734 | 124.1404 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 540.7932 | NaN | 27.9318 | NaN | 17.3519
4391.1292 | 13.0232 | 12.6773 | 12.8628 | 13.1199 | 12.5958 | 12.7811 | 12.6077 | 12.4637 | NaN | NaN | NaN | 12.8562 | 113.7292 | NaN | NaN | NaN | 3.7125 | NaN | NaN | NaN | NaN | 540.1774 | NaN | 27.3933 | NaN | 21.5493
4392.1292 | 13.0198 | 12.7195 | 12.8626 | 13.0839 | 12.5336 | 12.816 | 12.6091 | 12.469 | NaN | NaN | NaN | 12.9153 | 128.1267 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 540.4574 | NaN | 11.5124 | NaN | 23.6454
4393.1292 | 13.0533 | 12.7108 | 12.8622 | 13.0928 | 12.6217 | 12.7898 | 12.6018 | 12.4672 | NaN | NaN | NaN | 12.9111 | 129.0997 | NaN | NaN | NaN | -16.0253 | NaN | NaN | NaN | NaN | 540.2359 | NaN | 5.8049 | NaN | 25.7414
4394.1292 | 13.0217 | 12.7001 | 12.8649 | 13.1041 | 12.6428 | 12.8037 | 12.6057 | 12.468 | NaN | NaN | NaN | 12.8864 | 122.4589 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 540.4697 | NaN | 13.9816 | NaN | 26.7963
4395.1292 | 13.0224 | 12.7187 | 12.8622 | 13.1186 | 12.6296 | 12.8023 | 12.6146 | 12.4682 | NaN | NaN | NaN | 12.8912 | 117.4395 | NaN | NaN | NaN | -13.8484 | NaN | NaN | NaN | NaN | 541.0209 | NaN | 5.7066 | NaN | 22.1871
4396.1292 | 12.9947 | 12.7018 | 12.8673 | 13.0898 | 12.6013 | 12.7983 | 12.6022 | 12.4673 | NaN | NaN | NaN | 12.89 | 134.3752 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 541.9846 | NaN | 4.2746 | NaN | 23.0488
4397.1292 | 13.0386 | 12.7287 | 12.8639 | 13.0957 | 12.6148 | 12.8266 | 12.6193 | 12.4693 | NaN | NaN | NaN | 12.8539 | 120.5022 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 540.5491 | NaN | 38.5838 | NaN | 24.1387
4398.1292 | 13.0549 | 12.7274 | 12.8636 | 13.1064 | 12.6734 | 12.8134 | 12.6206 | 12.4721 | NaN | NaN | NaN | 12.8653 | 123.637 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 538.8424 | NaN | 10.1572 | NaN | 25.2444
4399.1292 | 13.0418 | 12.7693 | 12.8623 | 13.0581 | 12.6027 | 12.8288 | 12.6256 | 12.4732 | NaN | NaN | NaN | 12.916 | 124.7931 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 539.0165 | NaN | 13.3094 | NaN | 13.1107
4400.1292 | 13.0213 | 12.6859 | 12.8621 | 13.0832 | 12.5684 | 12.7902 | 12.6056 | 12.4776 | NaN | NaN | NaN | 12.9571 | 125.1192 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 540.5172 | NaN | 7.678 | NaN | 26.3204
4401.1292 | 13.0191 | 12.6988 | 12.8612 | 13.0396 | 12.6202 | 12.7847 | 12.6013 | 12.4645 | NaN | NaN | NaN | 12.8579 | 126.6284 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 544.8065 | NaN | 12.7871 | NaN | 25.1532
4402.1292 | 12.9981 | 12.751 | 12.8645 | 13.0586 | 12.5417 | 12.8231 | 12.612 | 12.4623 | NaN | NaN | NaN | 12.8483 | 120.846 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 540.9422 | NaN | 5.1829 | NaN | 20.8777
4403.1292 | 13.0223 | 12.7088 | 12.8638 | 13.0744 | 12.6357 | 12.8 | 12.598 | 12.4662 | NaN | NaN | NaN | 12.8712 | 124.6701 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 539.1249 | NaN | 5.7628 | NaN | 20.9827
4404.1292 | 13.0168 | 12.6962 | 12.8645 | 13.0722 | 12.6486 | 12.7893 | 12.6042 | 12.4652 | NaN | NaN | NaN | 12.8428 | 126.768 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 538.1884 | NaN | 9.3684 | NaN | 22.1894
4405.1292 | 13.0088 | 12.7039 | 12.8613 | 13.0387 | 12.5538 | 12.7949 | 12.6064 | 12.4675 | NaN | NaN | NaN | 12.8635 | 117.436 | NaN | NaN | NaN | 0.2552 | NaN | NaN | NaN | NaN | 541.0791 | NaN | 8.2619 | NaN | 23.9567
4406.1292 | 13.1514 | 12.7407 | 12.8654 | 13.0714 | 12.639 | 12.8128 | 12.6084 | 12.4713 | NaN | NaN | NaN | 12.8325 | 122.8598 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 538.9585 | NaN | 7.3084 | NaN | 21.1668
4407.1292 | 13.0946 | 12.754 | 12.8634 | 13.1079 | 12.5828 | 12.8316 | 12.6097 | 12.4617 | NaN | NaN | NaN | 12.8983 | 126.2502 | NaN | NaN | NaN | -7.2546 | NaN | NaN | NaN | NaN | 536.3452 | NaN | 38.5085 | NaN | 28.7535
4408.1292 | 13.0347 | 12.7597 | 12.8591 | 13.0773 | 12.6358 | 12.8237 | 12.6147 | 12.4614 | NaN | NaN | NaN | 12.8775 | 120.6327 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 534.0583 | NaN | 17.0076 | NaN | 23.4501
4409.1292 | 13.0399 | 12.7377 | 12.8622 | 13.0382 | 12.5842 | 12.8139 | 12.6066 | 12.4614 | NaN | NaN | NaN | 12.8493 | 121.0634 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 536.0803 | NaN | 23.1866 | NaN | 21.7373
4410.1292 | 13.0338 | 12.7886 | 12.8606 | 13.1473 | 12.5674 | 12.8238 | 12.6253 | 12.4651 | NaN | NaN | NaN | 12.8721 | 134.9706 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 538.52 | NaN | 3.7771 | NaN | 17.1435
4411.1292 | 13.0479 | 12.7526 | 12.8599 | 13.0528 | 12.5872 | 12.8135 | 12.6136 | 12.462 | NaN | NaN | NaN | 12.8365 | 129.8539 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 537.341 | NaN | 30.147 | NaN | 20.7209
4412.1292 | 13.0778 | 12.8335 | 12.8585 | 13.0758 | 12.5407 | 12.8663 | 12.6289 | 12.4675 | NaN | NaN | NaN | 12.8676 | 136.7988 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 534.6915 | NaN | 8.1646 | NaN | 30.8216
4413.1292 | 13.0512 | 12.7435 | 12.8589 | 13.0929 | 12.653 | 12.8001 | 12.6191 | 12.4679 | NaN | NaN | NaN | 12.8551 | 117.4889 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 538.0942 | NaN | 13.1243 | NaN | 21.1208
4414.1292 | 13.0375 | 12.7145 | 12.8523 | 13.0493 | 12.5758 | 12.7924 | 12.6194 | 12.4719 | NaN | NaN | NaN | 12.8361 | 119.131 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 534.9204 | NaN | 30.3042 | NaN | 24.0857
4415.1292 | 13.0372 | 12.7552 | 12.8522 | 13.0645 | 12.611 | 12.8247 | 12.6384 | 12.4703 | NaN | NaN | NaN | 12.8671 | 122.5856 | NaN | NaN | NaN | -19.4415 | NaN | NaN | NaN | NaN | 533.4026 | NaN | 9.1663 | NaN | 27.0523
4416.1292 | 13.1009 | 12.7035 | 12.8584 | 13.0523 | 12.6614 | 12.7978 | 12.6239 | 12.471 | NaN | NaN | NaN | 12.8461 | 116.0466 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 536.1753 | NaN | 8.7518 | NaN | 16.7682
4417.1292 | 13.021 | 12.7054 | 12.8573 | 13.0727 | 12.6452 | 12.7828 | 12.6108 | 12.4635 | NaN | NaN | NaN | 12.8626 | 117.399 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 538.0766 | NaN | 8.524 | NaN | 24.758
4418.1292 | 13.1109 | 12.7015 | 12.856 | 13.0788 | 12.6587 | 12.7853 | 12.621 | 12.4698 | NaN | NaN | NaN | 12.8298 | 117.1748 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 534.0286 | NaN | 9.0972 | NaN | 20.5701
4419.1292 | 13.06 | 12.7819 | 12.857 | 13.0774 | 12.6523 | 12.8209 | 12.636 | 12.4715 | NaN | NaN | NaN | 12.8711 | 132.1909 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 535.7316 | NaN | 19.2477 | NaN | 22.3138
4420.1292 | 13.0574 | 12.7337 | 12.8596 | 13.0792 | 12.6711 | 12.8056 | 12.624 | 12.4719 | NaN | NaN | NaN | 12.8353 | 123.7952 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 537.6861 | NaN | 8.9942 | NaN | 25.2496
4421.1292 | 13.0618 | 12.7582 | 12.8592 | 13.0873 | 12.5527 | 12.8079 | 12.6235 | 12.4726 | NaN | NaN | NaN | 12.8225 | 131.4345 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 535.8837 | NaN | 14.6831 | NaN | 17.9133
4422.1292 | 13.0609 | 12.7381 | 12.863 | 13.0858 | 12.5467 | 12.7881 | 12.6192 | 12.4687 | NaN | NaN | NaN | 12.8588 | 126.7127 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 537.9965 | NaN | 9.9281 | NaN | 23.3923
4423.1292 | 13.0485 | 12.731 | 12.8619 | 13.0496 | 12.5976 | 12.7934 | 12.619 | 12.481 | NaN | NaN | NaN | 12.8996 | 133.0429 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 536.9538 | NaN | 11.4668 | NaN | 20.57
4424.1292 | 13.0883 | 12.7446 | 12.8602 | 13.078 | 12.5816 | 12.8008 | 12.6261 | 12.4795 | NaN | NaN | NaN | 12.861 | 108.3087 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 537.4264 | NaN | 7.6783 | NaN | 16.9279
4425.1292 | 13.1107 | 12.7428 | 12.8666 | 13.0595 | 12.6302 | 12.8085 | 12.621 | 12.4742 | NaN | NaN | NaN | 12.8604 | 109.5388 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 536.4033 | NaN | 22.4603 | NaN | 24.6564
4426.1292 | 13.0995 | 12.8049 | 12.8588 | 13.0906 | 12.6558 | 12.8358 | 12.6569 | 12.4793 | NaN | NaN | NaN | 12.876 | 120.7206 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 536.1325 | NaN | 4.2416 | NaN | 23.8857
4427.1292 | 13.075 | 12.7704 | 12.8612 | 13.0616 | 12.5735 | 12.8237 | 12.6314 | 12.4784 | NaN | NaN | NaN | 12.8436 | 119.929 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 535.4636 | NaN | 28.4108 | NaN | 25.4485
4428.1292 | 13.0747 | 12.7333 | 12.8582 | 13.0355 | 12.6278 | 12.8002 | 12.627 | 12.4811 | NaN | NaN | NaN | 12.8511 | 121.7082 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 538.1066 | NaN | 17.7038 | NaN | 24.4002
4429.1292 | 13.0589 | 12.7385 | 12.8653 | 13.0702 | 12.6182 | 12.8078 | 12.6174 | 12.4796 | NaN | NaN | NaN | 12.8418 | 124.7112 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 536.2409 | NaN | 30.4592 | NaN | 25.9241
4430.1292 | 13.0669 | 12.7146 | 12.8646 | 13.0365 | 12.6265 | 12.8087 | 12.6243 | 12.4796 | NaN | NaN | NaN | 12.8672 | 130.9566 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 536.7965 | NaN | 7.2445 | NaN | 22.6535
4431.1292 | 13.0706 | 12.7333 | 12.8651 | 13.0722 | 12.5917 | 12.8025 | 12.6201 | 12.4806 | NaN | NaN | NaN | 12.8654 | 117.1543 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 535.5349 | NaN | 9.7273 | NaN | 17.7815
4432.1292 | 13.0659 | 12.7742 | 12.8612 | 13.0642 | 12.5642 | 12.832 | 12.6254 | 12.4786 | NaN | NaN | NaN | 12.8326 | 128.8325 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 536.4634 | NaN | 8.9 | NaN | 28.6388
4433.1292 | 13.0503 | 12.745 | 12.8618 | 13.0407 | 12.5853 | 12.798 | 12.6215 | 12.4847 | NaN | NaN | NaN | 12.8361 | 119.2265 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 535.1892 | NaN | 21.9273 | NaN | 24.58
4434.1292 | 13.0342 | 12.7749 | 12.867 | 13.0563 | 12.5933 | 12.8115 | 12.6302 | 12.4855 | NaN | NaN | NaN | 12.8598 | 112.8534 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 535.0615 | NaN | 24.5984 | NaN | 25.9196
4435.1292 | 13.0731 | 12.7988 | 12.8627 | 13.0785 | 12.5721 | 12.8526 | 12.6488 | 12.4889 | NaN | NaN | NaN | 12.8775 | 122.1877 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 532.4819 | NaN | 7.4124 | NaN | 24.4663
4436.1292 | 13.0622 | 12.7998 | 12.8686 | 13.074 | 12.517 | 12.8645 | 12.6455 | 12.487 | NaN | NaN | NaN | 12.8653 | 132.0849 | NaN | NaN | NaN | -9.0893 | NaN | NaN | NaN | NaN | 532.0614 | NaN | 31.4455 | NaN | 21.9382
4437.1292 | 13.0559 | 12.7854 | 12.8667 | 13.0599 | 12.6293 | 12.8366 | 12.6529 | 12.4886 | NaN | NaN | NaN | 12.851 | 114.6015 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 535.4806 | NaN | 10.4311 | NaN | 21.6544
4438.1292 | 13.0962 | 12.8595 | 12.8642 | 13.0915 | 12.5765 | 12.8744 | 12.6762 | 12.4926 | NaN | NaN | NaN | 12.9556 | 131.4915 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 534.8801 | NaN | 6.0637 | NaN | 16.508
4439.1292 | 13.0963 | 12.7507 | 12.8666 | 13.0743 | 12.6516 | 12.8204 | 12.642 | 12.4858 | NaN | NaN | NaN | 12.8518 | 127.9717 | NaN | NaN | NaN | -18.6668 | NaN | NaN | NaN | NaN | 533.8334 | NaN | 21.0103 | NaN | 27.3764
4440.1292 | 13.0531 | 12.7802 | 12.8661 | 13.0411 | 12.6225 | 12.8214 | 12.6413 | 12.4961 | NaN | NaN | NaN | 12.8518 | 130.3611 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 534.6328 | NaN | 5.552 | NaN | 15.5114
4441.1292 | 13.1781 | 12.7633 | 12.8596 | 13.0781 | 12.5874 | 12.8335 | 12.6467 | 12.4947 | NaN | NaN | NaN | 12.8589 | 125.4112 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 534.8415 | NaN | 20.5127 | NaN | 24.658
4442.1292 | 13.0812 | 12.8061 | 12.8654 | 13.0493 | 12.6596 | 12.8439 | 12.6645 | 12.4943 | NaN | NaN | NaN | 12.8579 | 124.0856 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 535.9708 | NaN | 34.032 | NaN | 29.2066
4443.1292 | 13.0773 | 12.7374 | 12.8616 | 13.0932 | 12.6882 | 12.8014 | 12.6481 | 12.4991 | NaN | NaN | NaN | 12.8426 | 122.083 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 537.1029 | NaN | 7.5082 | NaN | 20.4433
4444.1292 | 13.0547 | 12.7672 | 12.8633 | 13.1252 | 12.6746 | 12.826 | 12.6535 | 12.4997 | NaN | NaN | NaN | 12.8607 | 124.6684 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 534.7914 | NaN | 18.9236 | NaN | 25.4365
4445.1292 | 13.0402 | 12.7418 | 12.8648 | 13.064 | 12.6239 | 12.8204 | 12.6481 | 12.4934 | NaN | NaN | NaN | 12.8384 | 131.7491 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 537.3691 | NaN | 16.7678 | NaN | 21.3367
4446.1292 | 13.0435 | 12.7962 | 12.8648 | 13.0108 | 12.5768 | 12.8399 | 12.6412 | 12.497 | NaN | NaN | NaN | 12.8565 | 119.7556 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 537.9874 | NaN | 16.1435 | NaN | 24.8507
4447.1292 | 13.0433 | 12.7961 | 12.8636 | 13.0666 | 12.5594 | 12.869 | 12.6405 | 12.4972 | NaN | NaN | NaN | 12.8655 | 125.8614 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 536.4141 | NaN | 38.1477 | NaN | 28.1818
4448.1292 | 13.0221 | 12.7578 | 12.8665 | 13.1172 | 12.5922 | 12.8242 | 12.6477 | 12.5028 | NaN | NaN | NaN | 12.8463 | 130.7676 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 537.1907 | NaN | 25.209 | NaN | 30.6709
4449.1292 | 13.1036 | 12.7625 | 12.8671 | 13.0832 | 12.6355 | 12.8377 | 12.6571 | 12.5007 | NaN | NaN | NaN | 12.8297 | 127.2488 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 535.2464 | NaN | 30.1713 | NaN | 24.367
4450.1292 | 13.0617 | 12.7283 | 12.8699 | 13.0349 | 12.6468 | 12.8242 | 12.648 | 12.4992 | NaN | NaN | NaN | 12.8439 | 115.4539 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 537.2691 | NaN | 18.8775 | NaN | 12.6386
4451.1292 | 13.0454 | 12.767 | 12.8729 | 13.1195 | 12.5188 | 12.8747 | 12.6583 | 12.4931 | NaN | NaN | NaN | 12.8753 | 137.2874 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 537.6035 | NaN | 3.8802 | NaN | 23.4645
4452.1292 | 13.0592 | 12.7467 | 12.8764 | 13.0846 | 12.6505 | 12.8257 | 12.6408 | 12.4947 | NaN | NaN | NaN | 12.844 | 116.9819 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 536.648 | NaN | 21.0234 | NaN | 23.3157
4453.1292 | 13.0515 | 12.709 | 12.8744 | 13.0862 | 12.6676 | 12.8238 | 12.6377 | 12.4959 | NaN | NaN | NaN | 12.8475 | 118.7757 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 536.7475 | NaN | 4.2367 | NaN | 23.4533
4454.1292 | 13.0445 | 12.7037 | 12.8694 | 13.0702 | 12.6339 | 12.8311 | 12.6391 | 12.4963 | NaN | NaN | NaN | 12.8307 | 113.0781 | NaN | NaN | NaN | -7.9931 | NaN | NaN | NaN | NaN | 534.1022 | NaN | 9.5279 | NaN | 14.4039
4455.1292 | 13.0339 | 12.71 | 12.8759 | 13.029 | 12.5197 | 12.8267 | 12.6335 | 12.4921 | NaN | NaN | NaN | 12.8821 | 125.1493 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 536.4429 | NaN | 12.2996 | NaN | 25.8317
4456.1292 | 13.0465 | 12.7063 | 12.8756 | 13.1046 | 12.6249 | 12.8154 | 12.6374 | 12.4927 | NaN | NaN | NaN | 12.8592 | 109.3149 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 534.8567 | NaN | 29.8891 | NaN | 18.3459
4457.1292 | 13.037 | 12.7074 | 12.8757 | 13.0601 | 12.6462 | 12.8203 | 12.6497 | 12.4898 | NaN | NaN | NaN | 12.9077 | 137.7359 | NaN | NaN | NaN | -6.4872 | NaN | NaN | NaN | NaN | 535.3059 | NaN | 10.3457 | NaN | 18.6973
4458.1292 | 13.0348 | 12.7252 | 12.8785 | 13.0855 | 12.6497 | 12.8395 | 12.6513 | 12.4904 | NaN | NaN | NaN | 12.8611 | 129.2497 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 533.8647 | NaN | 29.9709 | NaN | 24.5978
4459.1292 | 13.0506 | 12.704 | 12.8812 | 13.0916 | 12.6474 | 12.8355 | 12.6397 | 12.485 | NaN | NaN | NaN | 12.85 | 117.1343 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 535.5354 | NaN | 5.0283 | NaN | 19.0055
4460.1292 | 13.0485 | 12.6662 | 12.8784 | 13.1081 | 12.5616 | 12.822 | 12.6374 | 12.4862 | NaN | NaN | NaN | 12.8331 | 118.9111 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 535.0872 | NaN | 20.3191 | NaN | 24.6546
4461.1292 | 13.0468 | 12.6864 | 12.8802 | 13.1047 | 12.6541 | 12.8348 | 12.6297 | 12.4836 | NaN | NaN | NaN | 12.8125 | 129.3525 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 534.0412 | NaN | 11.3378 | NaN | 26.3414
4462.1292 | 13.033 | 12.6814 | 12.8767 | 13.1045 | 12.6238 | 12.8277 | 12.6433 | 12.485 | NaN | NaN | NaN | 12.845 | 120.8339 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 534.3352 | NaN | 12.4822 | NaN | 17.0656
4463.1292 | 13.0369 | 12.712 | 12.8779 | 13.1262 | 12.5967 | 12.8492 | 12.6419 | 12.4834 | NaN | NaN | NaN | 12.8264 | 124.6266 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 535.1757 | NaN | 24.7922 | NaN | 20.4292
4464.1292 | 13.1137 | 12.6438 | 12.8766 | 13.1659 | 12.6337 | 12.8316 | 12.6375 | 12.488 | NaN | NaN | NaN | 12.8282 | 137.2453 | NaN | NaN | NaN | 0.1865 | NaN | NaN | NaN | NaN | 537.4643 | NaN | 7.3022 | NaN | 19.9133
4465.1292 | 13.0399 | 12.6535 | 12.8736 | 13.1071 | 12.666 | 12.8256 | 12.6295 | 12.4903 | NaN | NaN | NaN | 12.8362 | 119.6748 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 534.62 | NaN | 19.0683 | NaN | 22.6165
4466.1292 | 13.137 | 12.6318 | 12.8745 | 13.1116 | 12.6407 | 12.8286 | 12.6349 | 12.4885 | NaN | NaN | NaN | 12.8244 | 118.0721 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 534.9049 | NaN | 12.6704 | NaN | 19.1442
4467.1292 | 13.0632 | 12.6706 | 12.874 | 13.0316 | 12.6466 | 12.8321 | 12.6356 | 12.4906 | NaN | NaN | NaN | 12.8115 | 123.2777 | NaN | NaN | NaN | -3.9775 | NaN | NaN | NaN | NaN | 534.3812 | NaN | 12.918 | NaN | 26.5005
4468.1292 | 13.0654 | 12.6756 | 12.8754 | 13.0817 | 12.6447 | 12.8305 | 12.6378 | 12.4869 | NaN | NaN | NaN | 12.843 | 130.2941 | NaN | NaN | NaN | 1.1279 | NaN | NaN | NaN | NaN | 534.1122 | NaN | 4.9806 | NaN | 23.0767
4469.1292 | 13.0584 | 12.6704 | 12.8799 | 13.0762 | 12.6049 | 12.8369 | 12.6397 | 12.4866 | NaN | NaN | NaN | 12.8313 | 118.2271 | NaN | NaN | NaN | -4.3781 | NaN | NaN | NaN | NaN | 533.8733 | NaN | 23.9431 | NaN | 19.5671
4470.1292 | 13.0638 | 12.6922 | 12.8729 | 13.1098 | 12.5943 | 12.8528 | 12.6362 | 12.4832 | NaN | NaN | NaN | 12.8334 | 127.793 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 533.0405 | NaN | 3.5253 | NaN | 25.444
4471.1292 | 13.0442 | 12.6671 | 12.8721 | 13.0846 | 12.6154 | 12.8348 | 12.6418 | 12.4866 | NaN | NaN | NaN | 12.8545 | 129.7746 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 531.4014 | NaN | 6.2073 | NaN | 22.8917
4472.1292 | 13.0573 | 12.6609 | 12.8771 | 13.1073 | 12.6424 | 12.8284 | 12.6311 | 12.4912 | NaN | NaN | NaN | 12.8466 | 121.7475 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 533.4936 | NaN | 8.1506 | NaN | 27.7587
4473.1292 | 13.0584 | 12.6596 | 12.8651 | 13.085 | 12.6552 | 12.8235 | 12.6327 | 12.487 | NaN | NaN | NaN | 12.8391 | 120.2424 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 531.3378 | NaN | 6.0651 | NaN | 20.6431
4474.1292 | 13.0596 | 12.6699 | 12.8709 | 13.0691 | 12.6008 | 12.8248 | 12.627 | 12.4878 | NaN | NaN | NaN | 12.859 | 116.4625 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 531.5637 | NaN | 19.1587 | NaN | 25.5699
4475.1292 | 13.1344 | 12.7406 | 12.8719 | 13.1054 | 12.6622 | 12.8298 | 12.6342 | 12.4919 | NaN | NaN | NaN | 12.8736 | 127.8841 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 532.6618 | NaN | 20.0905 | NaN | 15.1585
4476.1292 | 13.1179 | 12.7146 | 12.871 | 13.0966 | 12.6121 | 12.8497 | 12.639 | 12.4915 | NaN | NaN | NaN | 12.8553 | 118.1265 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 530.6762 | NaN | 5.1418 | NaN | 18.116
4477.1292 | 13.187 | 12.6994 | 12.8694 | 13.045 | 12.6731 | 12.8269 | 12.6286 | 12.4949 | NaN | NaN | NaN | 12.8444 | 120.0919 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 533.3842 | NaN | 5.3326 | NaN | 22.9281
4478.1292 | 13.0676 | 12.737 | 12.8734 | 13.0771 | 12.5916 | 12.8466 | 12.6333 | 12.4886 | NaN | NaN | NaN | 12.9194 | 124.4008 | NaN | NaN | NaN | -7.1953 | NaN | NaN | NaN | NaN | 529.7619 | NaN | 8.5155 | NaN | 22.1946
4479.1292 | 13.0534 | 12.6739 | 12.8678 | 13.0779 | 12.6373 | 12.8131 | 12.6191 | 12.4871 | NaN | NaN | NaN | 12.8297 | 129.7779 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 531.3913 | NaN | 31.817 | NaN | 27.5435
4480.1292 | 13.0518 | 12.6878 | 12.8686 | 13.1161 | 12.6066 | 12.8217 | 12.6335 | 12.4874 | NaN | NaN | NaN | 12.8369 | 116.3923 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 532.9175 | NaN | 31.4426 | NaN | 11.2232
4481.1292 | 13.0802 | 12.7108 | 12.8695 | 13.0809 | 12.6553 | 12.816 | 12.6493 | 12.4898 | NaN | NaN | NaN | 12.829 | 110.681 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 532.9711 | NaN | 5.2009 | NaN | 21.1838
4482.1292 | 13.0787 | 12.6753 | 12.8732 | 13.1141 | 12.6659 | 12.8211 | 12.6367 | 12.4863 | NaN | NaN | NaN | 12.8394 | 120.4593 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 529.756 | NaN | 3.3506 | NaN | 23.1928
4483.1292 | 13.0827 | 12.6753 | 12.879 | 13.1304 | 12.6225 | 12.8381 | 12.6394 | 12.4964 | NaN | NaN | NaN | 12.8611 | 126.0064 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 532.9774 | NaN | 11.1837 | NaN | 23.9154
4484.1292 | 13.0874 | 12.7441 | 12.8702 | 13.1412 | 12.5947 | 12.8642 | 12.6555 | 12.4888 | NaN | NaN | NaN | 12.8629 | 126.2145 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 534.8622 | NaN | 10.3221 | NaN | 22.6813
4485.1292 | 13.1003 | 12.6598 | 12.872 | 13.0824 | 12.6286 | 12.8094 | 12.6338 | 12.4944 | NaN | NaN | NaN | 12.852 | 122.1452 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 534.9747 | NaN | 10.1076 | NaN | 23.7732
4486.1292 | 13.0835 | 12.7787 | 12.8788 | 13.1431 | 12.5598 | 12.8849 | 12.6447 | 12.4895 | NaN | NaN | NaN | 12.8407 | 123.088 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 535.9251 | NaN | 17.0724 | NaN | 20.8251
4487.1292 | 13.0785 | 12.6761 | 12.8712 | 13.0997 | 12.6147 | 12.8372 | 12.629 | 12.4931 | NaN | NaN | NaN | 12.8295 | 120.4407 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 537.1499 | NaN | 5.8554 | NaN | 22.7026
4488.1292 | 13.0729 | 12.6977 | 12.8811 | 13.1181 | 12.6313 | 12.8519 | 12.6389 | 12.4954 | NaN | NaN | NaN | 12.8708 | 131.4033 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 537.4146 | NaN | 13.602 | NaN | 18.9073
4489.1292 | 13.0804 | 12.6942 | 12.8754 | 13.087 | 12.6705 | 12.8448 | 12.6327 | 12.4962 | NaN | NaN | NaN | 12.8643 | 121.086 | NaN | NaN | NaN | 6.1875 | NaN | NaN | NaN | NaN | 536.3238 | NaN | 6.5238 | NaN | 18.2141
4490.1292 | 13.0763 | 12.7428 | 12.8801 | 13.1053 | 12.6518 | 12.8576 | 12.6398 | 12.4956 | NaN | NaN | NaN | 12.8384 | 123.0956 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 536.3105 | NaN | 4.4681 | NaN | 26.9106
4491.1292 | 13.063 | 12.7088 | 12.8807 | 13.086 | 12.6975 | 12.836 | 12.6339 | 12.4957 | NaN | NaN | NaN | 12.8425 | 118.3574 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 537.3113 | NaN | 14.1613 | NaN | 26.2744
4492.1292 | 13.0569 | 12.7151 | 12.882 | 13.0829 | 12.6709 | 12.8569 | 12.6317 | 12.4997 | NaN | NaN | NaN | 12.8887 | 135.0689 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 537.5458 | NaN | 13.9803 | NaN | 18.3568
4493.1292 | 13.1161 | 12.7108 | 12.8832 | 13.089 | 12.6081 | 12.8409 | 12.6241 | 12.5037 | NaN | NaN | NaN | 12.842 | 129.0861 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 536.7291 | NaN | 28.48 | NaN | 25.2825
4494.1292 | 13.0953 | 12.7707 | 12.8854 | 13.1036 | 12.5793 | 12.8762 | 12.6379 | 12.4992 | NaN | NaN | NaN | 12.8632 | 130.4081 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 535.8639 | NaN | 17.6217 | NaN | 17.0433
4495.1292 | 13.0997 | 12.7009 | 12.884 | 13.1361 | 12.6054 | 12.836 | 12.6216 | 12.5005 | NaN | NaN | NaN | 12.8459 | 141.9361 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 534.7887 | NaN | 5.1994 | NaN | 21.1498
4496.1292 | 13.0922 | 12.7845 | 12.8794 | 13.0666 | 12.6812 | 12.8796 | 12.6441 | 12.4997 | NaN | NaN | NaN | 12.8811 | 127.3561 | NaN | NaN | NaN | -15.3043 | NaN | NaN | NaN | NaN | 538.3304 | NaN | 15.8482 | NaN | 14.458
4497.1292 | 13.0861 | 12.7858 | 12.8838 | 13.0925 | 12.6411 | 12.8756 | 12.6382 | 12.4995 | NaN | NaN | NaN | 12.8251 | 117.9898 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 537.324 | NaN | 20.6793 | NaN | 26.053
4498.1292 | 13.0864 | 12.797 | 12.8807 | 13.0765 | 12.639 | 12.8754 | 12.6397 | 12.4943 | NaN | NaN | NaN | 12.8729 | 120.1191 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 538.2967 | NaN | 5.0582 | NaN | 27.2089
4499.1292 | 13.0639 | 12.7411 | 12.8751 | 13.0936 | 12.6595 | 12.8388 | 12.6196 | 12.497 | NaN | NaN | NaN | 12.8298 | 131.7722 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 536.6877 | NaN | 29.1416 | NaN | 18.1171
4500.1292 | 13.057 | 12.7014 | 12.8766 | 13.1149 | 12.6464 | 12.8327 | 12.6239 | 12.4952 | NaN | NaN | NaN | 12.8769 | 122.3171 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 539.8295 | NaN | 4.9718 | NaN | 20.6579
4501.1292 | 13.1177 | 12.7926 | 12.8837 | 13.0251 | 12.5952 | 12.9012 | 12.6367 | 12.4915 | NaN | NaN | NaN | 12.8761 | 127.3424 | NaN | NaN | NaN | -5.9407 | NaN | NaN | NaN | NaN | 539.3269 | NaN | 25.8262 | NaN | 24.2959
4502.1292 | 13.1648 | 12.7827 | 12.8837 | 13.0843 | 12.591 | 12.9073 | 12.6465 | 12.4887 | NaN | NaN | NaN | 12.842 | 126.2284 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 538.4616 | NaN | 29.8935 | NaN | 25.0001
4503.1292 | 13.0737 | 12.7047 | 12.8749 | 13.0679 | 12.6122 | 12.85 | 12.6279 | 12.4837 | NaN | NaN | NaN | 12.8229 | 117.3712 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 540.1874 | NaN | 5.329 | NaN | 18.3426
4504.1292 | 13.0726 | 12.7005 | 12.8743 | 13.0513 | 12.7118 | 12.8496 | 12.6297 | 12.4914 | NaN | NaN | NaN | 12.84 | 118.2164 | NaN | NaN | NaN | -11.8776 | NaN | NaN | NaN | NaN | 540.2676 | NaN | 27.7169 | NaN | 20.6501
4505.1292 | 13.032 | 12.6964 | 12.8738 | 13.0952 | 12.6608 | 12.8468 | 12.6407 | 12.4888 | NaN | NaN | NaN | 12.8338 | 124.0447 | NaN | NaN | NaN | -13.1994 | NaN | NaN | NaN | NaN | 539.5449 | NaN | 8.9571 | NaN | 24.3363
4506.1292 | 13.0801 | 12.6701 | 12.8675 | 13.075 | 12.6695 | 12.8314 | 12.6339 | 12.4899 | NaN | NaN | NaN | 12.8428 | 116.7848 | NaN | NaN | NaN | -1.994 | NaN | NaN | NaN | NaN | 535.369 | NaN | 11.4369 | NaN | 25.061
4507.1292 | 13.0973 | 12.6697 | 12.8738 | 13.0355 | 12.6302 | 12.8436 | 12.6289 | 12.4871 | NaN | NaN | NaN | 12.8452 | 121.3415 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 539.0013 | NaN | 15.4227 | NaN | 16.9031
4508.1292 | 13.0617 | 12.6843 | 12.8753 | 13.0625 | 12.6317 | 12.8416 | 12.6321 | 12.4929 | NaN | NaN | NaN | 12.8667 | 123.5791 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 535.0295 | NaN | 24.1319 | NaN | 18.1835
4509.1292 | 13.058 | 12.6678 | 12.8716 | 13.0412 | 12.6471 | 12.8405 | 12.6268 | 12.485 | NaN | NaN | NaN | 12.8504 | 130.4603 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 538.7596 | NaN | 23.5862 | NaN | 25.6643
4510.1292 | 13.0502 | 12.7204 | 12.8806 | 13.1243 | 12.6697 | 12.8702 | 12.6326 | 12.492 | NaN | NaN | NaN | 12.8441 | 112.8908 | NaN | NaN | NaN | -9.7361 | NaN | NaN | NaN | NaN | 535.1184 | NaN | 11.1278 | NaN | 17.3251
4511.1292 | 13.1482 | 12.6489 | 12.8748 | 13.0305 | 12.645 | 12.8513 | 12.6325 | 12.4843 | NaN | NaN | NaN | 12.8409 | 119.1603 | NaN | NaN | NaN | 5.7251 | NaN | NaN | NaN | NaN | 534.6992 | NaN | 13.469 | NaN | 24.2476
4512.1292 | 13.1129 | 12.7269 | 12.8779 | 13.0203 | 12.6109 | 12.8797 | 12.6335 | 12.4869 | NaN | NaN | NaN | 12.8187 | 126.3761 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 535.5385 | NaN | 25.9234 | NaN | 24.6434
4513.1292 | 13.1113 | 12.7344 | 12.8729 | 13.0769 | 12.637 | 12.8654 | 12.6529 | 12.4858 | NaN | NaN | NaN | 12.8696 | 131.0784 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 535.9541 | NaN | 16.9598 | NaN | 25.5346
4514.1292 | 13.0696 | 12.6751 | 12.8766 | 13.0715 | 12.6359 | 12.857 | 12.6234 | 12.4871 | NaN | NaN | NaN | 12.9198 | 127.793 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 536.0366 | NaN | 24.6632 | NaN | 22.9082
4515.1292 | 13.072 | 12.7252 | 12.885 | 13.0832 | 12.6571 | 12.8553 | 12.6385 | 12.4969 | NaN | NaN | NaN | 12.8626 | 124.195 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 535.7516 | NaN | 15.5446 | NaN | 19.6141
4516.1292 | 13.0696 | 12.7216 | 12.8875 | 13.0809 | 12.68 | 12.8567 | 12.6389 | 12.5016 | NaN | NaN | NaN | 12.8592 | 125.7394 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 536.4603 | NaN | 9.4225 | NaN | 15.3526
4517.1292 | 13.0601 | 12.7094 | 12.8883 | 13.0703 | 12.6523 | 12.8665 | 12.6387 | 12.5047 | NaN | NaN | NaN | 12.8301 | 125.5725 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 536.684 | NaN | 23.2054 | NaN | 19.0456
4518.1292 | 13.0843 | 12.7804 | 12.8908 | 13.058 | 12.5902 | 12.8955 | 12.6644 | 12.4977 | NaN | NaN | NaN | 12.8534 | 126.5345 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 537.0528 | NaN | 31.8089 | NaN | 24.6104
4519.1292 | 13.0858 | 12.7045 | 12.8873 | 13.081 | 12.6437 | 12.8703 | 12.6535 | 12.5042 | NaN | NaN | NaN | 12.8387 | 120.9706 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 537.7043 | NaN | 8.732 | NaN | 20.3147
4520.1292 | 13.0841 | 12.6622 | 12.8911 | 13.0638 | 12.6521 | 12.8352 | 12.6382 | 12.5152 | NaN | NaN | NaN | 12.8861 | 125.047 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 536.2568 | NaN | 23.017 | NaN | 22.8684
4521.1292 | 13.0844 | 12.708 | 12.8918 | 13.0664 | 12.5776 | 12.8905 | 12.6489 | 12.5044 | NaN | NaN | NaN | 12.8744 | 120.6089 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 533.6818 | NaN | 28.9688 | NaN | 25.8738
4522.1292 | 13.0982 | 12.6677 | 12.8961 | 13.0972 | 12.6384 | 12.8435 | 12.6355 | 12.5035 | NaN | NaN | NaN | 12.8811 | 119.1493 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 533.6321 | NaN | 16.2688 | NaN | 28.516
4523.1292 | 13.2067 | 12.6979 | 12.896 | 13.1274 | 12.6556 | 12.8614 | 12.6433 | 12.4939 | NaN | NaN | NaN | 12.8615 | 131.7321 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 532.9117 | NaN | 9.9551 | NaN | 20.6025
4524.1292 | 13.0802 | 12.6573 | 12.8928 | 13.0977 | 12.6106 | 12.8575 | 12.6461 | 12.4911 | NaN | NaN | NaN | 12.8611 | 125.0974 | NaN | NaN | NaN | -14.8954 | NaN | NaN | NaN | NaN | 533.4694 | NaN | 23.5656 | NaN | 23.4832
4525.1292 | 13.0694 | 12.6656 | 12.8914 | 13.1266 | 12.6734 | 12.8525 | 12.6339 | 12.4997 | NaN | NaN | NaN | 12.8805 | 126.2458 | NaN | NaN | NaN | 2.809 | NaN | NaN | NaN | NaN | 534.0217 | NaN | 25.3151 | NaN | 23.3711
4526.1292 | 13.0513 | 12.7799 | 12.8929 | 13.0708 | 12.6326 | 12.916 | 12.6631 | 12.4931 | NaN | NaN | NaN | 12.8641 | 126.2573 | NaN | NaN | NaN | -10.9138 | NaN | NaN | NaN | NaN | 535.8611 | NaN | 26.3888 | NaN | 24.7973
4527.1292 | 13.0681 | 12.7316 | 12.8985 | 13.0735 | 12.6862 | 12.8624 | 12.6479 | 12.4942 | NaN | NaN | NaN | 12.8773 | 126.112 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 535.5888 | NaN | 5.7535 | NaN | 25.6657
4528.1292 | 13.0639 | 12.7398 | 12.9021 | 13.0781 | 12.6251 | 12.8949 | 12.6494 | 12.499 | NaN | NaN | NaN | 12.8618 | 121.7747 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 537.4872 | NaN | 5.8546 | NaN | 25.0287
4529.1292 | 13.1231 | 12.6813 | 12.8938 | 13.1163 | 12.6094 | 12.8381 | 12.6442 | 12.4894 | NaN | NaN | NaN | 12.8573 | 129.5347 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 537.1409 | NaN | 9.8004 | NaN | 28.9289
4530.1292 | 13.0858 | 12.6841 | 12.8935 | 13.0662 | 12.6718 | 12.8447 | 12.6439 | 12.4975 | NaN | NaN | NaN | 12.8592 | 118.5308 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 539.1642 | NaN | 5.5657 | NaN | 28.0031
4531.1292 | 13.0845 | 12.7431 | 12.8962 | 13.0777 | 12.6218 | 12.8632 | 12.6487 | 12.4964 | NaN | NaN | NaN | 12.8767 | 132.2687 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 538.3195 | NaN | 26.7912 | NaN | 17.129
4532.1292 | 13.0596 | 12.7326 | 12.9009 | 13.1337 | 12.5941 | 12.8725 | 12.6573 | 12.4947 | NaN | NaN | NaN | 12.8695 | 120.1001 | NaN | NaN | NaN | -19.0351 | NaN | NaN | NaN | NaN | 534.8424 | NaN | 6.7518 | NaN | 21.1273
4533.1292 | 13.0467 | 12.7228 | 12.9043 | 13.1194 | 12.6652 | 12.8415 | 12.6423 | 12.5012 | NaN | NaN | NaN | 12.8568 | 120.6991 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 533.7181 | NaN | 4.2829 | NaN | 21.6315
4534.1292 | 13.1071 | 12.7188 | 12.9053 | 13.0577 | 12.5887 | 12.8522 | 12.6444 | 12.5026 | NaN | NaN | NaN | 12.8783 | 132.2182 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 537.0543 | NaN | 19.1732 | NaN | 11.8514
4535.1292 | 13.0679 | 12.7049 | 12.9021 | 13.0953 | 12.6218 | 12.8366 | 12.6344 | 12.5056 | NaN | NaN | NaN | 12.9534 | 124.2048 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 537.9192 | NaN | 13.5424 | NaN | 23.6945
4536.1292 | 13.0691 | 12.7249 | 12.9035 | 13.1064 | 12.6532 | 12.8433 | 12.6319 | 12.5099 | NaN | NaN | NaN | 12.8567 | 120.6759 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 537.5791 | NaN | 9.189 | NaN | 20.8894
4537.1292 | 13.1208 | 12.7837 | 12.9044 | 13.0937 | 12.6431 | 12.8759 | 12.6388 | 12.5046 | NaN | NaN | NaN | 12.8951 | 123.8943 | NaN | NaN | NaN | -19.9141 | NaN | NaN | NaN | NaN | 539.3365 | NaN | 11.7974 | NaN | 28.8212
4538.1292 | 13.1046 | 12.7162 | 12.9013 | 13.1462 | 12.5873 | 12.8637 | 12.6366 | 12.5108 | NaN | NaN | NaN | 12.8598 | 119.5514 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 535.9561 | NaN | 31.9854 | NaN | 16.6955
4539.1292 | 13.1193 | 12.7288 | 12.9052 | 13.0927 | 12.5526 | 12.8627 | 12.6311 | 12.5169 | NaN | NaN | NaN | 12.901 | 119.2175 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 534.2487 | NaN | 29.7823 | NaN | 20.2452
4540.1292 | 13.0844 | 12.7545 | 12.9116 | 13.0934 | 12.6041 | 12.8657 | 12.6375 | 12.5161 | NaN | NaN | NaN | 12.9012 | 123.397 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 533.1494 | NaN | 11.018 | NaN | 21.6571
4541.1292 | 13.0821 | 12.7873 | 12.9091 | 13.1162 | 12.657 | 12.8699 | 12.6478 | 12.5151 | NaN | NaN | NaN | 12.9182 | 124.4206 | NaN | NaN | NaN | -0.0073 | NaN | NaN | NaN | NaN | 533.8474 | NaN | 11.5551 | NaN | 28.3037
4542.1292 | 13.1087 | 12.7327 | 12.9123 | 13.1358 | 12.578 | 12.8776 | 12.6333 | 12.524 | NaN | NaN | NaN | 12.8555 | 125.6647 | NaN | NaN | NaN | -13.6226 | NaN | NaN | NaN | NaN | 534.5253 | NaN | 29.7763 | NaN | 23.3182
4543.1292 | 13.0812 | 12.7683 | 12.9144 | 13.1117 | 12.6821 | 12.8638 | 12.635 | 12.5173 | NaN | NaN | NaN | 12.9002 | 130.6282 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 536.8851 | NaN | 8.3632 | NaN | 14.4594
4544.1292 | 13.1098 | 12.7418 | 12.9084 | 13.1479 | 12.6563 | 12.8504 | 12.624 | 12.5156 | NaN | NaN | NaN | 12.8867 | 124.0491 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 533.7462 | NaN | 30.6749 | NaN | 20.4277
4545.1292 | 13.0966 | 12.7696 | 12.914 | 13.142 | 12.5674 | 12.8865 | 12.6325 | 12.5226 | NaN | NaN | NaN | 12.925 | 121.8824 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 534.1967 | NaN | 14.8307 | NaN | 14.7783
4546.1292 | 13.0833 | 12.8372 | 12.9151 | 13.1295 | 12.661 | 12.8952 | 12.6331 | 12.5182 | NaN | NaN | NaN | 12.9053 | 120.3354 | NaN | NaN | NaN | -0.0609 | NaN | NaN | NaN | NaN | 534.8817 | NaN | 28.431 | NaN | 24.734
4547.1292 | 13.0887 | 12.8196 | 12.9152 | 13.1184 | 12.584 | 12.9068 | 12.6412 | 12.5168 | NaN | NaN | NaN | 12.9021 | 119.6987 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 535.3042 | NaN | 13.2006 | NaN | 19.0009
4548.1292 | 13.137 | 12.7783 | 12.9154 | 13.1136 | 12.6224 | 12.8654 | 12.6269 | 12.5144 | NaN | NaN | NaN | 12.914 | 126.0815 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 533.4115 | NaN | 20.5499 | NaN | 16.9315
4549.1292 | 13.108 | 12.7693 | 12.9159 | 13.1022 | 12.6742 | 12.8698 | 12.621 | 12.5164 | NaN | NaN | NaN | 12.8775 | 130.5022 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 537.0802 | NaN | 14.2404 | NaN | 15.7659
4550.1292 | 13.1021 | 12.7581 | 12.9117 | 13.1356 | 12.7077 | 12.8574 | 12.6091 | 12.5164 | NaN | NaN | NaN | 12.8948 | 116.9567 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 535.2445 | NaN | 18.9583 | NaN | 14.3375
4551.1292 | 13.1014 | 12.7522 | 12.9191 | 13.051 | 12.634 | 12.8561 | 12.6108 | 12.5167 | NaN | NaN | NaN | 12.8805 | 130.9752 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 537.3724 | NaN | 17.5854 | NaN | 23.377
4552.1292 | 13.0622 | 12.8723 | 12.9216 | 13.1181 | 12.5814 | 12.9585 | 12.6477 | 12.5099 | NaN | NaN | NaN | 12.8959 | 126.6945 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 534.2842 | NaN | 6.59 | NaN | 31.5969
4553.1292 | 13.1076 | 12.7724 | 12.9186 | 13.1423 | 12.5812 | 12.8761 | 12.6261 | 12.5066 | NaN | NaN | NaN | 12.8869 | 123.2235 | NaN | NaN | NaN | 7.3874 | NaN | NaN | NaN | NaN | 538.8256 | NaN | 7.617 | NaN | 22.0245
4554.1292 | 13.1138 | 12.772 | 12.9096 | 13.088 | 12.7097 | 12.8689 | 12.6249 | 12.5112 | NaN | NaN | NaN | 12.8712 | 120.1954 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 537.9338 | NaN | 20.9836 | NaN | 23.7462
4555.1292 | 13.1125 | 12.7707 | 12.9185 | 13.0996 | 12.6606 | 12.8536 | 12.6174 | 12.5025 | NaN | NaN | NaN | 12.8935 | 130.4423 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 538.4546 | NaN | 5.3441 | NaN | 20.7773
4556.1292 | 13.1099 | 12.7564 | 12.9133 | 13.0757 | 12.6163 | 12.8483 | 12.6286 | 12.5061 | NaN | NaN | NaN | 12.8976 | 130.1834 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 539.7791 | NaN | 9.8171 | NaN | 14.6868
4557.1292 | 13.119 | 12.7948 | 12.9167 | 13.118 | 12.701 | 12.8596 | 12.6313 | 12.5033 | NaN | NaN | NaN | 12.8897 | 111.2977 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 538.1522 | NaN | 19.8232 | NaN | 19.4736
4558.1292 | 13.1101 | 12.8403 | 12.9185 | 13.0919 | 12.6048 | 12.9017 | 12.6427 | 12.5027 | NaN | NaN | NaN | 12.887 | 117.0769 | NaN | NaN | NaN | -15.9871 | NaN | NaN | NaN | NaN | 537.3497 | NaN | 26.865 | NaN | 21.1634
4559.1292 | 13.0975 | 12.7755 | 12.9117 | 13.1337 | 12.6562 | 12.8667 | 12.6322 | 12.5004 | NaN | NaN | NaN | 12.9697 | 119.1925 | NaN | NaN | NaN | -0.3928 | NaN | NaN | NaN | NaN | 532.902 | NaN | 20.4876 | NaN | 24.4109
4560.1292 | 13.1244 | 12.8267 | 12.9156 | 13.1649 | 12.6888 | 12.8557 | 12.6446 | 12.5008 | NaN | NaN | NaN | 12.9023 | 139.7768 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 532.511 | NaN | 29.44 | NaN | 22.5579
4561.1292 | 13.0654 | 12.7861 | 12.9174 | 13.1561 | 12.6132 | 12.873 | 12.6549 | 12.5031 | NaN | NaN | NaN | 12.8798 | 115.9658 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 535.6679 | NaN | 23.6274 | NaN | 25.8319
4562.1292 | 13.1413 | 12.7625 | 12.9129 | 13.1426 | 12.7078 | 12.8573 | 12.6514 | 12.5022 | NaN | NaN | NaN | 12.8936 | 116.5732 | NaN | NaN | NaN | -4.3181 | NaN | NaN | NaN | NaN | 536.9263 | NaN | 5.4672 | NaN | 21.76
4563.1292 | 13.1055 | 12.8179 | 12.9151 | 13.1062 | 12.5465 | 12.8919 | 12.6507 | 12.506 | NaN | NaN | NaN | 12.9075 | 123.7463 | NaN | NaN | NaN | -0.9462 | NaN | NaN | NaN | NaN | 536.3346 | NaN | 19.2324 | NaN | 23.1665
4564.1292 | 13.1126 | 12.7725 | 12.9155 | 13.0951 | 12.6958 | 12.8532 | 12.6521 | 12.5076 | NaN | NaN | NaN | 12.89 | 116.8002 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 537.8713 | NaN | 12.2268 | NaN | 23.8048
4565.1292 | 13.0964 | 12.855 | 12.9134 | 13.1245 | 12.6486 | 12.9174 | 12.6681 | 12.5117 | NaN | NaN | NaN | 12.8939 | 136.8538 | NaN | NaN | NaN | -4.1315 | NaN | NaN | NaN | NaN | 534.8452 | NaN | 10.6049 | NaN | 25.0051
4566.1292 | 13.0684 | 12.7769 | 12.9073 | 13.2455 | 12.6723 | 12.8605 | 12.6608 | 12.5123 | NaN | NaN | NaN | 12.8716 | 107.8442 | NaN | NaN | NaN | -3.8557 | NaN | NaN | NaN | NaN | 536.1489 | NaN | 16.5044 | NaN | 18.7029
4567.1292 | 13.1042 | 12.7538 | 12.9166 | 13.0705 | 12.6322 | 12.8464 | 12.6634 | 12.5152 | NaN | NaN | NaN | 12.863 | 121.7625 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 535.5753 | NaN | 22.477 | NaN | 17.2136
4568.1292 | 13.0865 | 12.7897 | 12.9123 | 13.1055 | 12.6458 | 12.8616 | 12.6548 | 12.5144 | NaN | NaN | NaN | 12.8701 | 119.2416 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 533.3754 | NaN | 14.3693 | NaN | 20.0017
4569.1292 | 13.193 | 12.8455 | 12.9186 | 13.165 | 12.6898 | 12.8553 | 12.6624 | 12.5205 | NaN | NaN | NaN | 12.8676 | 122.3358 | NaN | NaN | NaN | -7.6565 | NaN | NaN | NaN | NaN | 531.9444 | NaN | 18.9735 | NaN | 17.2712
4570.1292 | 13.1052 | 12.7558 | 12.9119 | 13.087 | 12.6264 | 12.8434 | 12.6607 | 12.5131 | NaN | NaN | NaN | 12.8934 | 129.1363 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 533.4752 | NaN | 28.0927 | NaN | 18.6545
4571.1292 | 13.0903 | 12.7967 | 12.9116 | 13.1274 | 12.6551 | 12.8631 | 12.6634 | 12.5156 | NaN | NaN | NaN | 12.882 | 127.4169 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 535.319 | NaN | 26.3962 | NaN | 23.0182
4572.1292 | 13.0847 | 12.8424 | 12.9127 | 13.0975 | 12.6944 | 12.8792 | 12.676 | 12.5091 | NaN | NaN | NaN | 12.8891 | 113.522 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 536.2851 | NaN | 11.206 | NaN | 15.7492
4573.1292 | 13.1127 | 12.769 | 12.9092 | 13.1207 | 12.6592 | 12.8468 | 12.6646 | 12.5127 | NaN | NaN | NaN | 12.8701 | 129.0363 | NaN | NaN | NaN | 1.6466 | NaN | NaN | NaN | NaN | 533.4619 | NaN | 27.03 | NaN | 22.7683
4574.1292 | 13.0782 | 12.8218 | 12.9119 | 13.0984 | 12.6734 | 12.8536 | 12.6671 | 12.509 | NaN | NaN | NaN | 12.8478 | 119.7904 | NaN | NaN | NaN | -12.1607 | NaN | NaN | NaN | NaN | 535.4456 | NaN | 14.239 | NaN | 7.9802
4575.1292 | 13.1488 | 12.7683 | 12.9049 | 13.1051 | 12.6206 | 12.85 | 12.658 | 12.5116 | NaN | NaN | NaN | 12.8892 | 113.0949 | NaN | NaN | NaN | -7.6038 | NaN | NaN | NaN | NaN | 535.5236 | NaN | 23.5343 | NaN | 21.8461
4576.1292 | 13.0974 | 12.8062 | 12.9118 | 13.12 | 12.7138 | 12.8614 | 12.6636 | 12.5151 | NaN | NaN | NaN | 12.9015 | 122.3286 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 535.1647 | NaN | 5.7855 | NaN | 17.0342
4577.1292 | 13.0865 | 12.7745 | 12.9087 | 13.1203 | 12.6057 | 12.8549 | 12.6627 | 12.5168 | NaN | NaN | NaN | 12.8527 | 127.9031 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 535.8097 | NaN | 23.8865 | NaN | 23.7063
4578.1292 | 13.071 | 12.7619 | 12.9083 | 13.1411 | 12.7041 | 12.8476 | 12.6566 | 12.5204 | NaN | NaN | NaN | 12.899 | 118.9021 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 533.9807 | NaN | 13.0105 | NaN | 26.1924
4579.1292 | 13.065 | 12.8139 | 12.9137 | 13.1286 | 12.5883 | 12.891 | 12.6634 | 12.513 | NaN | NaN | NaN | 12.8474 | 120.5505 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 535.4403 | NaN | 6.1256 | NaN | 15.3669
4580.1292 | 13.0592 | 12.8521 | 12.9057 | 13.1283 | 12.6543 | 12.8606 | 12.6976 | 12.5172 | NaN | NaN | NaN | 12.9585 | 130.1626 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 534.6566 | NaN | 23.8045 | NaN | 13.3081
4581.1292 | 13.0617 | 12.8091 | 12.9049 | 13.0683 | 12.611 | 12.8919 | 12.6725 | 12.5125 | NaN | NaN | NaN | 12.8718 | 131.7554 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 536.5467 | NaN | 30.6951 | NaN | 23.9045
4582.1292 | 13.1063 | 12.8084 | 12.8964 | 13.0631 | 12.6363 | 12.8906 | 12.6747 | 12.5118 | NaN | NaN | NaN | 12.8933 | 128.5327 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 536.1469 | NaN | 23.8747 | NaN | 24.5462
4583.1292 | 13.0839 | 12.8108 | 12.8966 | 13.1272 | 12.6618 | 12.882 | 12.6835 | 12.5152 | NaN | NaN | NaN | 12.9126 | 126.7611 | NaN | NaN | NaN | -19.7305 | NaN | NaN | NaN | NaN | 537.0734 | NaN | 27.1687 | NaN | 25.8602
4584.1292 | 13.0936 | 12.7743 | 12.8951 | 13.0878 | 12.7002 | 12.8647 | 12.6694 | 12.5108 | NaN | NaN | NaN | 12.9068 | 127.151 | NaN | NaN | NaN | -4.1866 | NaN | NaN | NaN | NaN | 537.524 | NaN | 16.0005 | NaN | 15.1131
4585.1292 | 13.1065 | 12.7449 | 12.896 | 13.1031 | 12.6782 | 12.8404 | 12.6548 | 12.5151 | NaN | NaN | NaN | 12.9035 | 126.0751 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 534.7039 | NaN | 23.0887 | NaN | 26.4443
4586.1292 | 13.0893 | 12.8216 | 12.8993 | 13.1405 | 12.704 | 12.8826 | 12.6736 | 12.5155 | NaN | NaN | NaN | 12.8748 | 125.0173 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 536.365 | NaN | 5.7802 | NaN | 16.8318
4587.1292 | 13.0562 | 12.7289 | 12.8975 | 13.0931 | 12.72 | 12.8411 | 12.6496 | 12.5094 | NaN | NaN | NaN | 12.9018 | 115.465 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 535.1907 | NaN | 25.8803 | NaN | 24.1246
4588.1292 | 13.1316 | 12.7288 | 12.8921 | 13.0934 | 12.6638 | 12.85 | 12.6477 | 12.5161 | NaN | NaN | NaN | 12.8857 | 123.6006 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 536.5499 | NaN | 11.449 | NaN | 16.8058
4589.1292 | 13.0786 | 12.7235 | 12.8932 | 13.0924 | 12.6523 | 12.8593 | 12.6649 | 12.5192 | NaN | NaN | NaN | 12.9124 | 133.3768 | NaN | NaN | NaN | -0.6652 | NaN | NaN | NaN | NaN | 537.0076 | NaN | 15.591 | NaN | 24.7175
4590.1292 | 13.0771 | 12.7449 | 12.8917 | 13.0973 | 12.645 | 12.8666 | 12.6698 | 12.5172 | NaN | NaN | NaN | 12.8934 | 126.9824 | NaN | NaN | NaN | 3.957 | NaN | NaN | NaN | NaN | 534.2528 | NaN | 9.0596 | NaN | 24.4483
4591.1292 | 13.0818 | 12.7701 | 12.8959 | 13.0682 | 12.6905 | 12.867 | 12.6697 | 12.5088 | NaN | NaN | NaN | 12.8922 | 124.298 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 537.9324 | NaN | 13.3113 | NaN | 18.1036
4592.1292 | 13.0851 | 12.7142 | 12.8925 | 13.1136 | 12.7 | 12.8354 | 12.6527 | 12.5168 | NaN | NaN | NaN | 12.889 | 130.466 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 540.6455 | NaN | 7.9209 | NaN | 25.8753
4593.1292 | 13.0863 | 12.7485 | 12.892 | 13.0888 | 12.7162 | 12.88 | 12.6589 | 12.5123 | NaN | NaN | NaN | 12.9293 | 127.7418 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 539.656 | NaN | 4.1464 | NaN | 24.8097
4594.1292 | 13.0853 | 12.7087 | 12.8915 | 13.1284 | 12.5895 | 12.8444 | 12.651 | 12.5084 | NaN | NaN | NaN | 12.9114 | 123.728 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 542.5993 | NaN | 13.18 | NaN | 23.7354
4595.1292 | 13.0866 | 12.7918 | 12.8936 | 13.1158 | 12.6674 | 12.8665 | 12.6805 | 12.5117 | NaN | NaN | NaN | 12.9158 | 130.1501 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 539.6115 | NaN | 7.1422 | NaN | 15.1339
4596.1292 | 13.1084 | 12.7344 | 12.8913 | 13.152 | 12.74 | 12.8595 | 12.6629 | 12.5153 | NaN | NaN | NaN | 12.9311 | 121.5499 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 539.4699 | NaN | 15.0405 | NaN | 16.7964
4597.1292 | 13.1073 | 12.7832 | 12.8931 | 13.066 | 12.6855 | 12.878 | 12.6778 | 12.5231 | NaN | NaN | NaN | 12.8883 | 125.7732 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 541.5519 | NaN | 39.3696 | NaN | 21.0517
4598.1292 | 13.1242 | 12.7633 | 12.8932 | 13.1117 | 12.7036 | 12.8602 | 12.6713 | 12.5125 | NaN | NaN | NaN | 12.919 | 121.7567 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 539.2824 | NaN | 15.7434 | NaN | 17.5681
4599.1292 | 13.1827 | 12.8419 | 12.895 | 13.0448 | 12.6569 | 12.8782 | 12.6864 | 12.5191 | NaN | NaN | NaN | 12.8826 | 131.4541 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 542.1871 | NaN | 10.1846 | NaN | 23.8169
4600.1292 | 13.1254 | 12.7703 | 12.8856 | 13.1117 | 12.6392 | 12.8834 | 12.6816 | 12.515 | NaN | NaN | NaN | 12.8847 | 122.3324 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 539.921 | NaN | 13.6187 | NaN | 21.0436
4601.1292 | 13.0874 | 12.7651 | 12.8939 | 13.0976 | 12.704 | 12.8726 | 12.671 | 12.5148 | NaN | NaN | NaN | 12.9361 | 124.3523 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 539.8256 | NaN | 30.1241 | NaN | 18.709
4602.1292 | 13.082 | 12.743 | 12.8947 | 13.1217 | 12.6721 | 12.8609 | 12.6663 | 12.5173 | NaN | NaN | NaN | 12.9388 | 121.4044 | NaN | NaN | NaN | 0.3478 | NaN | NaN | NaN | NaN | 538.3353 | NaN | 11.4148 | NaN | 21.0336
4603.1292 | 13.0743 | 12.7363 | 12.8961 | 13.2316 | 12.7465 | 12.8616 | 12.6732 | 12.5139 | NaN | NaN | NaN | 13.0034 | 133.5475 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 534.3641 | NaN | 11.2078 | NaN | 22.569
4604.1292 | 13.0994 | 12.7602 | 12.8978 | 13.1334 | 12.5833 | 12.8853 | 12.683 | 12.5154 | NaN | NaN | NaN | 12.8987 | 122.1835 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 540.0259 | NaN | 4.7883 | NaN | 23.0305
4605.1292 | 13.0956 | 12.6956 | 12.8892 | 13.116 | 12.7191 | 12.8373 | 12.6625 | 12.5156 | NaN | NaN | NaN | 12.9565 | 119.0074 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 539.228 | NaN | 12.3484 | NaN | 16.8165
4606.1292 | 13.0788 | 12.7012 | 12.8936 | 13.1092 | 12.63 | 12.8427 | 12.6653 | 12.5134 | NaN | NaN | NaN | 12.9378 | 128.4046 | NaN | NaN | NaN | -11.0411 | NaN | NaN | NaN | NaN | 543.6617 | NaN | 20.6272 | NaN | 26.3827
4607.1292 | 13.0909 | 12.8367 | 12.8984 | 13.0882 | 12.7137 | 12.8744 | 12.6979 | 12.5062 | NaN | NaN | NaN | 12.9041 | 116.4299 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 542.1449 | NaN | 8.175 | NaN | 21.5103
4608.1292 | 13.0704 | 12.7934 | 12.9019 | 13.1275 | 12.638 | 12.8799 | 12.6828 | 12.5126 | NaN | NaN | NaN | 12.905 | 116.2012 | NaN | NaN | NaN | -11.4648 | NaN | NaN | NaN | NaN | 541.726 | NaN | 23.814 | NaN | 26.4947
4609.1292 | 13.1333 | 12.7705 | 12.9009 | 13.0681 | 12.6595 | 12.8822 | 12.6771 | 12.5121 | NaN | NaN | NaN | 12.9114 | 110.4281 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 543.1703 | NaN | 11.0137 | NaN | 22.704
4610.1292 | 13.1567 | 12.7248 | 12.8969 | 13.0889 | 12.6039 | 12.8415 | 12.6755 | 12.5084 | NaN | NaN | NaN | 12.9084 | 119.0866 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 545.3268 | NaN | 17.3609 | NaN | 27.3708
4611.1292 | 13.0945 | 12.7188 | 12.8967 | 13.0977 | 12.6209 | 12.842 | 12.6705 | 12.5169 | NaN | NaN | NaN | 12.8984 | 130.4361 | NaN | NaN | NaN | -16.8567 | NaN | NaN | NaN | NaN | 544.7427 | NaN | 14.4002 | NaN | 25.3308
4612.1292 | 13.0821 | 12.7203 | 12.8984 | 13.1474 | 12.6049 | 12.8491 | 12.6772 | 12.5091 | NaN | NaN | NaN | 12.9223 | 116.9281 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 545.464 | NaN | 14.4295 | NaN | 21.7645
4613.1292 | 13.0837 | 12.8562 | 12.9119 | 13.1194 | 12.7359 | 12.8835 | 12.7086 | 12.5155 | NaN | NaN | NaN | 12.9224 | 132.0788 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 545.5573 | NaN | 8.1926 | NaN | 23.1163
4614.1292 | 13.0828 | 12.7747 | 12.9051 | 13.1391 | 12.7033 | 12.8587 | 12.6858 | 12.5108 | NaN | NaN | NaN | 12.9027 | 130.1314 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 545.8396 | NaN | 11.6454 | NaN | 28.6305
4615.1292 | 13.1184 | 12.789 | 12.9029 | 13.1381 | 12.6932 | 12.8621 | 12.6946 | 12.511 | NaN | NaN | NaN | 12.8822 | 118.1089 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 547.7435 | NaN | 22.1859 | NaN | 18.5631
4616.1292 | 13.1285 | 12.7457 | 12.9063 | 13.1041 | 12.7098 | 12.849 | 12.6765 | 12.5173 | NaN | NaN | NaN | 12.9224 | 125.042 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 546.2009 | NaN | 11.3219 | NaN | 14.2817
4617.1292 | 13.1423 | 12.7435 | 12.9002 | 13.1847 | 12.6294 | 12.8478 | 12.6859 | 12.518 | NaN | NaN | NaN | 12.904 | 120.5015 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 546.9164 | NaN | 17.7168 | NaN | 14.9738
4618.1292 | 13.1072 | 12.7406 | 12.9048 | 13.1586 | 12.6958 | 12.8341 | 12.6817 | 12.5208 | NaN | NaN | NaN | 12.8917 | 128.4306 | NaN | NaN | NaN | -4.8321 | NaN | NaN | NaN | NaN | 545.8953 | NaN | 11.2189 | NaN | 14.3977
4619.1292 | 13.1106 | 12.7428 | 12.9116 | 13.1294 | 12.7122 | 12.8454 | 12.6851 | 12.5178 | NaN | NaN | NaN | 12.8787 | 133.4558 | NaN | NaN | NaN | -14.2583 | NaN | NaN | NaN | NaN | 546.2121 | NaN | 22.0999 | NaN | 24.2227
4620.1292 | 13.0779 | 12.822 | 12.9097 | 13.158 | 12.7141 | 12.8528 | 12.6995 | 12.5242 | NaN | NaN | NaN | 12.8918 | 120.5731 | NaN | NaN | NaN | 4.8279 | NaN | NaN | NaN | NaN | 543.5333 | NaN | 17.1775 | NaN | 21.6888
4621.1292 | 13.109 | 12.7607 | 12.9004 | 13.1177 | 12.6277 | 12.8615 | 12.6993 | 12.5204 | NaN | NaN | NaN | 12.8823 | 123.1643 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 547.7738 | NaN | 7.8611 | NaN | 19.4043
4622.1292 | 13.0565 | 12.7855 | 12.91 | 13.1501 | 12.6015 | 12.8865 | 12.7054 | 12.5285 | NaN | NaN | NaN | 12.9055 | 128.8519 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 546.6555 | NaN | 22.7867 | NaN | 20.0941
4623.1292 | 13.1017 | 12.7895 | 12.9046 | 13.1727 | 12.6188 | 12.8592 | 12.7061 | 12.5215 | NaN | NaN | NaN | 12.8636 | 115.5699 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 548.7759 | NaN | 25.4271 | NaN | 18.0101
4624.1292 | 13.0864 | 12.7754 | 12.916 | 13.1176 | 12.6834 | 12.8553 | 12.7029 | 12.5251 | NaN | NaN | NaN | 12.8872 | 132.0786 | NaN | NaN | NaN | -8.4904 | NaN | NaN | NaN | NaN | 547.0222 | NaN | 21.2946 | NaN | 19.1596
4625.1292 | 13.074 | 12.804 | 12.9079 | 13.0947 | 12.7025 | 12.8656 | 12.7113 | 12.5179 | NaN | NaN | NaN | 12.9433 | 122.1332 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 548.4451 | NaN | 5.2808 | NaN | 21.8263
4626.1292 | 13.0909 | 12.7708 | 12.9096 | 13.1533 | 12.7108 | 12.8417 | 12.7043 | 12.526 | NaN | NaN | NaN | 12.8655 | 121.9292 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 548.3318 | NaN | 9.1351 | NaN | 23.8531
4627.1292 | 13.0591 | 12.7939 | 12.9167 | 13.1688 | 12.6251 | 12.8722 | 12.7055 | 12.5279 | NaN | NaN | NaN | 12.8556 | 129.4188 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 549.1918 | NaN | 21.4197 | NaN | 29.3686
4628.1292 | 13.0985 | 12.7893 | 12.9169 | 13.1337 | 12.7384 | 12.8536 | 12.7038 | 12.534 | NaN | NaN | NaN | 12.8637 | 124.3512 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 551.9779 | NaN | 21.9261 | NaN | 24.9495
4629.1292 | 13.1394 | 12.7545 | 12.9173 | 13.1594 | 12.7367 | 12.8337 | 12.6999 | 12.5287 | NaN | NaN | NaN | 12.841 | 122.488 | NaN | NaN | NaN | -5.971 | NaN | NaN | NaN | NaN | 551.4257 | NaN | 28.3795 | NaN | 23.3444
4630.1292 | 13.054 | 12.8715 | 12.9282 | 13.1548 | 12.7109 | 12.8797 | 12.7218 | 12.528 | NaN | NaN | NaN | 12.8765 | 140.7422 | NaN | NaN | NaN | 2.8975 | NaN | NaN | NaN | NaN | 550.3213 | NaN | 26.767 | NaN | 25.2983
4631.1292 | 13.1159 | 12.781 | 12.9238 | 13.1597 | 12.7246 | 12.8416 | 12.6968 | 12.5397 | NaN | NaN | NaN | 12.874 | 115.0456 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 551.9812 | NaN | 14.2967 | NaN | 24.8801
4632.1292 | 13.0966 | 12.7953 | 12.9184 | 13.1037 | 12.6435 | 12.8639 | 12.7057 | 12.5348 | NaN | NaN | NaN | 12.8716 | 116.4541 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 553.2363 | NaN | 7.6256 | NaN | 25.6971
4633.1292 | 13.0936 | 12.7935 | 12.9165 | 13.1631 | 12.6858 | 12.8623 | 12.7137 | 12.5413 | NaN | NaN | NaN | 12.8941 | 120.0836 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 553.4756 | NaN | 18.9065 | NaN | 20.1542
4634.1292 | 13.0814 | 12.8162 | 12.9246 | 13.1619 | 12.6877 | 12.8737 | 12.7098 | 12.5463 | NaN | NaN | NaN | 12.8877 | 117.6041 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 555.3343 | NaN | 10.3622 | NaN | 21.6759
4635.1292 | 13.0613 | 12.7713 | 12.9169 | 13.1235 | 12.6094 | 12.8672 | 12.7029 | 12.5362 | NaN | NaN | NaN | 12.8652 | 123.7459 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 556.5528 | NaN | 16.325 | NaN | 14.9165
4636.1292 | 13.065 | 12.8408 | 12.9199 | 13.1131 | 12.6575 | 12.8931 | 12.718 | 12.5371 | NaN | NaN | NaN | 12.8703 | 123.0822 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 553.3369 | NaN | 14.9631 | NaN | 24.1004
4637.1292 | 13.144 | 12.8294 | 12.9283 | 13.1528 | 12.679 | 12.8877 | 12.7074 | 12.54 | NaN | NaN | NaN | 12.8532 | 124.1185 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 555.3389 | NaN | 35.6585 | NaN | 22.1038
4638.1292 | 13.0988 | 12.831 | 12.9268 | 13.1634 | 12.7023 | 12.8549 | 12.7111 | 12.5456 | NaN | NaN | NaN | 12.8605 | 129.3893 | NaN | NaN | NaN | -17.7251 | NaN | NaN | NaN | NaN | 554.3646 | NaN | 13.7478 | NaN | 23.9997
4639.1292 | 13.0863 | 12.7744 | 12.9267 | 13.1833 | 12.7373 | 12.8465 | 12.6881 | 12.5415 | NaN | NaN | NaN | 12.8595 | 125.0496 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 556.8457 | NaN | 20.6017 | NaN | 19.5819
4640.1292 | 13.0785 | 12.8223 | 12.9255 | 13.1383 | 12.6418 | 12.8806 | 12.701 | 12.5463 | NaN | NaN | NaN | 12.8296 | 122.0693 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 558.9274 | NaN | 7.8141 | NaN | 18.0891
4641.1292 | 13.0786 | 12.8021 | 12.9249 | 13.1698 | 12.6651 | 12.8788 | 12.6934 | 12.5401 | NaN | NaN | NaN | 12.8627 | 116.9673 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 558.9988 | NaN | 36.0015 | NaN | 29.3901
4642.1292 | 13.0805 | 12.7724 | 12.9254 | 13.1561 | 12.6673 | 12.8664 | 12.6866 | 12.5371 | NaN | NaN | NaN | 12.8501 | 130.4174 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 560.0036 | NaN | 28.3889 | NaN | 22.4078
4643.1292 | 13.0646 | 12.7663 | 12.9253 | 13.1771 | 12.6399 | 12.8708 | 12.6874 | 12.5405 | NaN | NaN | NaN | 12.8526 | 120.8756 | NaN | NaN | NaN | -6.5769 | NaN | NaN | NaN | NaN | 558.4833 | NaN | 32.0017 | NaN | 26.6157
4644.1292 | 13.1265 | 12.8393 | 12.9251 | 13.1701 | 12.7011 | 12.9064 | 12.7156 | 12.5456 | NaN | NaN | NaN | 12.825 | 115.1703 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 559.8325 | NaN | 18.1035 | NaN | 18.2985
4645.1292 | 13.1547 | 12.8193 | 12.934 | 13.1672 | 12.7264 | 12.8871 | 12.6942 | 12.5399 | NaN | NaN | NaN | 12.8896 | 130.6296 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 557.6399 | NaN | 7.0648 | NaN | 18.8268
4646.1292 | 13.1905 | 12.7867 | 12.9271 | 13.1689 | 12.6737 | 12.8657 | 12.6806 | 12.5383 | NaN | NaN | NaN | 12.845 | 129.1629 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 559.8243 | NaN | 32.645 | NaN | 22.4106
4647.1292 | 13.136 | 12.8071 | 12.9246 | 13.1495 | 12.6944 | 12.8787 | 12.6903 | 12.5346 | NaN | NaN | NaN | 12.845 | 115.5382 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 559.7087 | NaN | 20.9914 | NaN | 20.1101
4648.1292 | 13.1135 | 12.7992 | 12.9258 | 13.1151 | 12.6707 | 12.8698 | 12.6945 | 12.5317 | NaN | NaN | NaN | 12.8549 | 119.3308 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 559.5511 | NaN | 11.8074 | NaN | 21.5372
4649.1292 | 13.1134 | 12.8041 | 12.9302 | 13.1582 | 12.5997 | 12.8733 | 12.6896 | 12.5268 | NaN | NaN | NaN | 12.835 | 120.4975 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 557.7885 | NaN | 8.1258 | NaN | 24.7458
4650.1292 | 13.117 | 12.8319 | 12.9287 | 13.1543 | 12.6307 | 12.9022 | 12.702 | 12.5256 | NaN | NaN | NaN | 12.8491 | 125.059 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 557.0976 | NaN | 23.1521 | NaN | 23.0979
4651.1292 | 13.1059 | 12.8628 | 12.932 | 13.1776 | 12.6392 | 12.9047 | 12.7017 | 12.5291 | NaN | NaN | NaN | 12.8812 | 120.4614 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 558.2624 | NaN | 31.6362 | NaN | 24.4867
4652.1292 | 13.1081 | 12.8179 | 12.9299 | 13.171 | 12.7071 | 12.884 | 12.7092 | 12.5304 | NaN | NaN | NaN | 12.9106 | 122.3573 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 557.6157 | NaN | 26.579 | NaN | 21.7359
4653.1292 | 13.093 | 12.8078 | 12.9286 | 13.1271 | 12.7113 | 12.877 | 12.7043 | 12.5267 | NaN | NaN | NaN | 12.8359 | 132.2673 | NaN | NaN | NaN | -14.9841 | NaN | NaN | NaN | NaN | 560.3949 | NaN | 15.617 | NaN | 21.9094
4654.1292 | 13.1395 | 12.7826 | 12.9319 | 13.148 | 12.669 | 12.8819 | 12.7009 | 12.534 | NaN | NaN | NaN | 12.889 | 126.1188 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 557.8781 | NaN | 7.644 | NaN | 27.4301
4655.1292 | 13.1248 | 12.8116 | 12.9339 | 13.1667 | 12.6503 | 12.9035 | 12.7144 | 12.5318 | NaN | NaN | NaN | 12.9018 | 128.1492 | NaN | NaN | NaN | -18.2593 | NaN | NaN | NaN | NaN | 559.7613 | NaN | 15.076 | NaN | 37.9267
4656.1292 | 13.1526 | 12.8249 | 12.9312 | 13.159 | 12.5929 | 12.9121 | 12.7009 | 12.5295 | NaN | NaN | NaN | 12.8251 | 127.7684 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 558.6623 | NaN | 25.9684 | NaN | 22.6827
4657.1292 | 13.1188 | 12.7675 | 12.9286 | 13.1886 | 12.6466 | 12.8861 | 12.6962 | 12.535 | NaN | NaN | NaN | 12.8323 | 114.5343 | NaN | NaN | NaN | -6.2521 | NaN | NaN | NaN | NaN | 557.0232 | NaN | 27.8952 | NaN | 18.1072
4658.1292 | 13.1146 | 12.8169 | 12.9285 | 13.1577 | 12.6949 | 12.9096 | 12.708 | 12.538 | NaN | NaN | NaN | 12.8123 | 124.5014 | NaN | NaN | NaN | -3.1277 | NaN | NaN | NaN | NaN | 559.2815 | NaN | 17.6839 | NaN | 25.3181
4659.1292 | 13.1043 | 12.8243 | 12.9404 | 13.1734 | 12.7297 | 12.8983 | 12.6975 | 12.5382 | NaN | NaN | NaN | 12.8452 | 124.1237 | NaN | NaN | NaN | -19.3406 | NaN | NaN | NaN | NaN | 559.371 | NaN | 17.5175 | NaN | 19.0433
4660.1292 | 13.1003 | 12.7921 | 12.9318 | 13.1446 | 12.635 | 12.8995 | 12.6949 | 12.542 | NaN | NaN | NaN | 12.8512 | 127.0389 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 561.1367 | NaN | 18.7861 | NaN | 18.098
4661.1292 | 13.1218 | 12.78 | 12.9362 | 13.1646 | 12.6742 | 12.8926 | 12.6949 | 12.5407 | NaN | NaN | NaN | 12.8715 | 122.0171 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 561.4823 | NaN | 12.1288 | NaN | 22.9723
4662.1292 | 13.0955 | 12.7688 | 12.9397 | 13.1668 | 12.6949 | 12.9072 | 12.6951 | 12.5421 | NaN | NaN | NaN | 12.8608 | 132.4493 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 561.9337 | NaN | 22.5828 | NaN | 24.8224
4663.1292 | 13.1956 | 12.7777 | 12.9281 | 13.1742 | 12.7229 | 12.898 | 12.6947 | 12.5434 | NaN | NaN | NaN | 12.9623 | 125.4287 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 562.1525 | NaN | 12.8607 | NaN | 31.5179
4664.1292 | 13.1508 | 12.7931 | 12.9278 | 13.1541 | 12.6539 | 12.9365 | 12.6972 | 12.5421 | NaN | NaN | NaN | 12.8059 | 126.2974 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 562.9725 | NaN | 33.5833 | NaN | 25.3469
4665.1292 | 13.0898 | 12.9038 | 12.9314 | 13.1444 | 12.6033 | 13.0186 | 12.7214 | 12.539 | NaN | NaN | NaN | 12.8866 | 128.2679 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 562.7738 | NaN | 14.2749 | NaN | 20.8752
4666.1292 | 13.0994 | 12.8084 | 12.9348 | 13.178 | 12.6773 | 12.9194 | 12.6985 | 12.5381 | NaN | NaN | NaN | 12.8248 | 124.8218 | NaN | NaN | NaN | -7.1102 | NaN | NaN | NaN | NaN | 563.668 | NaN | 22.0945 | NaN | 17.5809
4667.1292 | 13.1775 | 12.8056 | 12.9384 | 13.2241 | 12.7266 | 12.9202 | 12.7053 | 12.5317 | NaN | NaN | NaN | 12.8781 | 119.1423 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 561.6771 | NaN | 22.0259 | NaN | 21.441
4668.1292 | 13.1455 | 12.7844 | 12.9363 | 13.1364 | 12.6965 | 12.9002 | 12.6915 | 12.5351 | NaN | NaN | NaN | 12.8333 | 122.4409 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 565.2486 | NaN | 30.6464 | NaN | 26.8579
4669.1292 | 13.1238 | 12.845 | 12.9422 | 13.1681 | 12.6488 | 12.9216 | 12.6981 | 12.5343 | NaN | NaN | NaN | 12.8847 | 130.668 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 562.7237 | NaN | 16.8771 | NaN | 27.7554
4670.1292 | 13.1306 | 12.8055 | 12.9402 | 13.1816 | 12.6151 | 12.9275 | 12.6976 | 12.5302 | NaN | NaN | NaN | 12.8396 | 120.2463 | NaN | NaN | NaN | 5.441 | NaN | NaN | NaN | NaN | 565.2464 | NaN | 12.9492 | NaN | 14.7854
4671.1292 | 13.1158 | 12.8191 | 12.9416 | 13.2083 | 12.7105 | 12.9189 | 12.7094 | 12.5261 | NaN | NaN | NaN | 12.8443 | 118.5505 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 564.1872 | NaN | 10.6783 | NaN | 23.3546
4672.1292 | 13.1838 | 12.8375 | 12.9447 | 13.1663 | 12.709 | 12.917 | 12.6963 | 12.5323 | NaN | NaN | NaN | 12.8558 | 115.5813 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 563.7203 | NaN | 30.1373 | NaN | 28.5871
4673.1292 | 13.1333 | 12.7944 | 12.9436 | 13.2088 | 12.5984 | 12.9092 | 12.6897 | 12.5329 | NaN | NaN | NaN | 12.8289 | 115.4497 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 564.842 | NaN | 25.5021 | NaN | 24.434
4674.1292 | 13.1487 | 12.8584 | 12.9466 | 13.2013 | 12.7073 | 12.9153 | 12.7035 | 12.5261 | NaN | NaN | NaN | 12.8651 | 124.8039 | NaN | NaN | NaN | -1.2119 | NaN | NaN | NaN | NaN | 563.727 | NaN | 25.1725 | NaN | 26.5507
4675.1292 | 13.1411 | 12.8429 | 12.9459 | 13.2142 | 12.7252 | 12.9248 | 12.6994 | 12.528 | NaN | NaN | NaN | 12.8429 | 121.6741 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 564.0811 | NaN | 9.4865 | NaN | 16.6979
4676.1292 | 13.1068 | 12.8685 | 12.9427 | 13.1897 | 12.6423 | 12.9476 | 12.7067 | 12.5271 | NaN | NaN | NaN | 12.817 | 130.2759 | NaN | NaN | NaN | -16.489 | NaN | NaN | NaN | NaN | 566.9262 | NaN | 8.7547 | NaN | 26.896
4677.1292 | 13.1867 | 12.7953 | 12.949 | 13.1761 | 12.6768 | 12.8977 | 12.6816 | 12.5287 | NaN | NaN | NaN | 12.8276 | 123.2701 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 566.9353 | NaN | 22.1139 | NaN | 23.4521
4678.1292 | 13.1745 | 12.8906 | 12.9442 | 13.2018 | 12.6987 | 12.9174 | 12.7089 | 12.5294 | NaN | NaN | NaN | 12.8684 | 130.5 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 567.0315 | NaN | 12.5869 | NaN | 25.0732
4679.1292 | 13.1405 | 12.8441 | 12.9489 | 13.1309 | 12.6784 | 12.9083 | 12.6962 | 12.5251 | NaN | NaN | NaN | 12.8884 | 120.5725 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 568.0677 | NaN | 13.4089 | NaN | 25.4526
4680.1292 | 13.1895 | 12.8196 | 12.9469 | 13.1689 | 12.6486 | 12.9029 | 12.6944 | 12.5292 | NaN | NaN | NaN | 12.8999 | 132.0822 | NaN | NaN | NaN | 7.5966 | NaN | NaN | NaN | NaN | 567.0076 | NaN | 16.807 | NaN | 20.0677
4681.1292 | 13.1411 | 12.7864 | 12.9488 | 13.168 | 12.7067 | 12.8924 | 12.6868 | 12.528 | NaN | NaN | NaN | 12.8651 | 121.8625 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 569.1573 | NaN | 13.4326 | NaN | 17.8079
4682.1292 | 13.1396 | 12.824 | 12.9458 | 13.181 | 12.6781 | 12.9178 | 12.6881 | 12.5274 | NaN | NaN | NaN | 12.8666 | 125.4452 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 567.5013 | NaN | 24.8471 | NaN | 25.1008
4683.1292 | 13.1091 | 12.8057 | 12.9435 | 13.1882 | 12.6109 | 12.9074 | 12.6906 | 12.5244 | NaN | NaN | NaN | 12.8729 | 128.3429 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 568.6404 | NaN | 29.8241 | NaN | 17.0975
4684.1292 | 13.1619 | 12.8196 | 12.9414 | 13.2047 | 12.7069 | 12.9072 | 12.689 | 12.5326 | NaN | NaN | NaN | 12.8859 | 121.0662 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 565.5844 | NaN | 8.9043 | NaN | 16.5077
4685.1292 | 13.1508 | 12.8176 | 12.9456 | 13.1782 | 12.7092 | 12.909 | 12.68 | 12.5349 | NaN | NaN | NaN | 12.901 | 137.8614 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 565.9483 | NaN | 27.0826 | NaN | 24.0968
4686.1292 | 13.1441 | 12.8221 | 12.9451 | 13.2182 | 12.6994 | 12.9045 | 12.6839 | 12.5363 | NaN | NaN | NaN | 12.9578 | 117.2123 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 567.1696 | NaN | 29.8896 | NaN | 20.7623
4687.1292 | 13.1763 | 12.8108 | 12.9472 | 13.1693 | 12.6559 | 12.9185 | 12.6952 | 12.5357 | NaN | NaN | NaN | 12.8657 | 122.7984 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 566.3771 | NaN | 19.1917 | NaN | 27.2902
4688.1292 | 13.1362 | 12.8128 | 12.9454 | 13.2058 | 12.6803 | 12.904 | 12.6812 | 12.537 | NaN | NaN | NaN | 12.8877 | 122.0437 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 566.4958 | NaN | 9.8865 | NaN | 14.7898
4689.1292 | 13.1301 | 12.7935 | 12.9471 | 13.1889 | 12.6799 | 12.8842 | 12.676 | 12.5404 | NaN | NaN | NaN | 12.9182 | 118.5144 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 565.5656 | NaN | 21.4601 | NaN | 18.2109
4690.1292 | 13.1503 | 12.8911 | 12.9463 | 13.1996 | 12.6939 | 12.9608 | 12.7151 | 12.5435 | NaN | NaN | NaN | 12.9387 | 128.5584 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 564.002 | NaN | 28.7757 | NaN | 24.7033
4691.1292 | 13.1338 | 12.8159 | 12.9448 | 13.1666 | 12.7151 | 12.899 | 12.6905 | 12.5489 | NaN | NaN | NaN | 12.911 | 117.531 | NaN | NaN | NaN | -3.2294 | NaN | NaN | NaN | NaN | 564.7811 | NaN | 32.7594 | NaN | 23.02
4692.1292 | 13.1298 | 12.8415 | 12.9459 | 13.2483 | 12.7223 | 12.9074 | 12.6858 | 12.5473 | NaN | NaN | NaN | 12.9278 | 118.1033 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 564.3228 | NaN | 21.7684 | NaN | 18.7263
4693.1292 | 13.1064 | 12.8331 | 12.9503 | 13.17 | 12.6423 | 12.9154 | 12.6976 | 12.551 | NaN | NaN | NaN | 12.9301 | 113.1068 | NaN | NaN | NaN | 16.6871 | NaN | NaN | NaN | NaN | 563.6906 | NaN | 26.7743 | NaN | 24.8407
4694.1292 | 13.1003 | 12.8065 | 12.9395 | 13.1797 | 12.6821 | 12.9046 | 12.6885 | 12.5486 | NaN | NaN | NaN | 12.9174 | 129.4992 | NaN | NaN | NaN | -13.3905 | NaN | NaN | NaN | NaN | 563.8094 | NaN | 11.492 | NaN | 13.3734
4695.1292 | 13.1462 | 12.8154 | 12.9403 | 13.1921 | 12.6903 | 12.8989 | 12.6926 | 12.5565 | NaN | NaN | NaN | 12.9406 | 120.4326 | NaN | NaN | NaN | 0.3351 | NaN | NaN | NaN | NaN | 561.1567 | NaN | 16.1803 | NaN | 21.4031
4696.1292 | 13.1222 | 12.8436 | 12.9442 | 13.1793 | 12.6643 | 12.9221 | 12.6946 | 12.5537 | NaN | NaN | NaN | 12.9342 | 121.4965 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 559.4066 | NaN | 12.8954 | NaN | 17.1055
4697.1292 | 13.1059 | 12.8624 | 12.9432 | 13.1736 | 12.7048 | 12.9166 | 12.6919 | 12.5467 | NaN | NaN | NaN | 12.9053 | 124.0635 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 559.8488 | NaN | 24.1987 | NaN | 21.3183
4698.1292 | 13.1121 | 12.9096 | 12.9377 | 13.1614 | 12.7106 | 12.9178 | 12.7048 | 12.5485 | NaN | NaN | NaN | 12.9435 | 111.3268 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 561.9263 | NaN | 28.4863 | NaN | 21.3442
4699.1292 | 13.1141 | 12.8157 | 12.9423 | 13.1806 | 12.6534 | 12.8964 | 12.6832 | 12.5502 | NaN | NaN | NaN | 12.9309 | 116.8019 | NaN | NaN | NaN | -7.9339 | NaN | NaN | NaN | NaN | 562.632 | NaN | 11.4088 | NaN | 26.4505
4700.1292 | 13.1115 | 12.8581 | 12.948 | 13.1731 | 12.7521 | 12.9035 | 12.6915 | 12.5506 | NaN | NaN | NaN | 12.8944 | 119.6257 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 561.8988 | NaN | 25.3676 | NaN | 21.3257
4701.1292 | 13.1122 | 12.8406 | 12.9436 | 13.1961 | 12.7391 | 12.89 | 12.6889 | 12.5598 | NaN | NaN | NaN | 12.9068 | 121.6499 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 560.7222 | NaN | 16.4749 | NaN | 20.332
4702.1292 | 13.1102 | 12.8645 | 12.9434 | 13.1907 | 12.7294 | 12.8942 | 12.691 | 12.5541 | NaN | NaN | NaN | 12.9062 | 123.1522 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 559.9345 | NaN | 12.4408 | NaN | 19.6941
4703.1292 | 13.172 | 12.8288 | 12.9422 | 13.1793 | 12.6578 | 12.9013 | 12.684 | 12.5568 | NaN | NaN | NaN | 12.9268 | 128.9071 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 559.6668 | NaN | 13.8429 | NaN | 24.0557
4704.1292 | 13.138 | 12.8535 | 12.9572 | 13.1842 | 12.711 | 12.8896 | 12.6818 | 12.5552 | NaN | NaN | NaN | 12.9152 | 133.5849 | NaN | NaN | NaN | -10.8274 | NaN | NaN | NaN | NaN | 559.6898 | NaN | 14.8378 | NaN | 24.9422
4705.1292 | 13.1241 | 12.8465 | 12.9585 | 13.13 | 12.673 | 12.906 | 12.6815 | 12.5542 | NaN | NaN | NaN | 12.892 | 125.5246 | NaN | NaN | NaN | -0.7917 | NaN | NaN | NaN | NaN | 561.4447 | NaN | 27.8331 | NaN | 21.207
4706.1292 | 13.205 | 12.8627 | 12.9519 | 13.1593 | 12.6706 | 12.92 | 12.6958 | 12.5557 | NaN | NaN | NaN | 12.8958 | 127.9016 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 561.7875 | NaN | 10.8419 | NaN | 23.0981
4707.1292 | 13.2035 | 12.8355 | 12.9497 | 13.1562 | 12.7192 | 12.8981 | 12.6884 | 12.5602 | NaN | NaN | NaN | 12.9068 | 125.8643 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 561.1792 | NaN | 30.4756 | NaN | 19.7806
4708.1292 | 13.1922 | 12.916 | 12.9593 | 13.1861 | 12.716 | 12.9079 | 12.7183 | 12.5581 | NaN | NaN | NaN | 12.908 | 117.6876 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 558.6271 | NaN | 25.2522 | NaN | 27.4261
4709.1292 | 13.1405 | 12.8927 | 12.9554 | 13.1741 | 12.6972 | 12.9183 | 12.716 | 12.5644 | NaN | NaN | NaN | 12.9461 | 124.3068 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 559.3766 | NaN | 18.8664 | NaN | 18.4567
4710.1292 | 13.1131 | 12.8822 | 12.9522 | 13.1638 | 12.7354 | 12.9104 | 12.7091 | 12.5608 | NaN | NaN | NaN | 12.9286 | 124.819 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 559.9437 | NaN | 27.8528 | NaN | 29.6911
4711.1292 | 13.2529 | 12.8374 | 12.9588 | 13.1343 | 12.6598 | 12.8876 | 12.6946 | 12.5626 | NaN | NaN | NaN | 12.9092 | 119.8437 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 562.5846 | NaN | 24.5468 | NaN | 25.3717
4712.1292 | 13.1292 | 12.8265 | 12.9593 | 13.1818 | 12.7179 | 12.876 | 12.7042 | 12.5629 | NaN | NaN | NaN | 12.9083 | 119.7987 | NaN | NaN | NaN | -1.8111 | NaN | NaN | NaN | NaN | 560.2766 | NaN | 18.0196 | NaN | 21.3872
4713.1292 | 13.1294 | 12.8449 | 12.9622 | 13.1615 | 12.6444 | 12.8905 | 12.698 | 12.5593 | NaN | NaN | NaN | 12.9111 | 123.4079 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 560.3091 | NaN | 31.5039 | NaN | 24.7643
4714.1292 | 13.1011 | 12.8168 | 12.9582 | 13.1761 | 12.7098 | 12.8946 | 12.7031 | 12.556 | NaN | NaN | NaN | 12.9048 | 126.3099 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 561.4396 | NaN | 14.3923 | NaN | 21.799
4715.1292 | 13.1384 | 12.8455 | 12.958 | 13.1436 | 12.745 | 12.8847 | 12.7099 | 12.5578 | NaN | NaN | NaN | 12.9034 | 131.8263 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 563.5468 | NaN | 9.2083 | NaN | 19.8159
4716.1292 | 13.1714 | 12.832 | 12.9502 | 13.1644 | 12.731 | 12.8876 | 12.7168 | 12.5545 | NaN | NaN | NaN | 12.95 | 117.2478 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 561.3513 | NaN | 17.5546 | NaN | 25.0919
4717.1292 | 13.1303 | 12.8691 | 12.9518 | 13.1516 | 12.6967 | 12.9157 | 12.717 | 12.5525 | NaN | NaN | NaN | 12.9043 | 123.2485 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 563.0219 | NaN | 8.7861 | NaN | 27.1165
4718.1292 | 13.118 | 12.8569 | 12.9512 | 13.1952 | 12.7132 | 12.9037 | 12.7138 | 12.5541 | NaN | NaN | NaN | 12.8943 | 126.2115 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 562.8841 | NaN | 31.9296 | NaN | 28.4765
4719.1292 | 13.1162 | 12.8271 | 12.9458 | 13.1366 | 12.7077 | 12.8851 | 12.6981 | 12.5575 | NaN | NaN | NaN | 12.9327 | 131.1459 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 562.659 | NaN | 22.7903 | NaN | 18.1996
4720.1292 | 13.1482 | 12.8491 | 12.9518 | 13.1465 | 12.6997 | 12.91 | 12.7075 | 12.5564 | NaN | NaN | NaN | 12.9187 | 124.9761 | NaN | NaN | NaN | 1.4856 | NaN | NaN | NaN | NaN | 561.2519 | NaN | 7.5011 | NaN | 28.2294
4721.1292 | 13.1336 | 12.9104 | 12.9494 | 13.1541 | 12.7147 | 12.9105 | 12.7196 | 12.5492 | NaN | NaN | NaN | 12.9122 | 121.85 | NaN | NaN | NaN | 6.024 | NaN | NaN | NaN | NaN | 562.5219 | NaN | 15.9937 | NaN | 24.7387
4722.1292 | 13.1361 | 12.94 | 12.955 | 13.1701 | 12.7045 | 12.8993 | 12.7252 | 12.5609 | NaN | NaN | NaN | 12.8961 | 133.2857 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 559.3305 | NaN | 11.2741 | NaN | 24.705
4723.1292 | 13.1117 | 12.9101 | 12.9513 | 13.1729 | 12.7273 | 12.925 | 12.7299 | 12.5539 | NaN | NaN | NaN | 12.9118 | 121.9292 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 556.6204 | NaN | 22.8285 | NaN | 13.0635
4724.1292 | 13.1993 | 12.8167 | 12.9495 | 13.1307 | 12.7324 | 12.8854 | 12.7058 | 12.5494 | NaN | NaN | NaN | 12.9316 | 120.4636 | NaN | NaN | NaN | 1.8472 | NaN | NaN | NaN | NaN | 560.2504 | NaN | 22.7996 | NaN | 18.5427
4725.1292 | 13.1713 | 12.9469 | 12.9513 | 13.1457 | 12.6944 | 12.9085 | 12.7356 | 12.5499 | NaN | NaN | NaN | 12.9177 | 117.7676 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 559.775 | NaN | 22.6505 | NaN | 21.6432
4726.1292 | 13.1564 | 12.8387 | 12.951 | 13.1659 | 12.6879 | 12.8884 | 12.6988 | 12.5522 | NaN | NaN | NaN | 12.9057 | 128.9244 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 557.533 | NaN | 15.9598 | NaN | 22.842
4727.1292 | 13.1855 | 12.8774 | 12.951 | 13.1623 | 12.5996 | 12.9111 | 12.7138 | 12.5515 | NaN | NaN | NaN | 12.9401 | 126.8963 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 559.2651 | NaN | 19.5165 | NaN | 18.6725
4728.1292 | 13.1998 | 12.8263 | 12.9472 | 13.1344 | 12.7289 | 12.8829 | 12.7062 | 12.5474 | NaN | NaN | NaN | 12.874 | 126.282 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 562.2158 | NaN | 25.3096 | NaN | 24.0946
4729.1448 | 13.1648 | 12.8619 | 12.947 | 13.1867 | 12.7065 | 12.9138 | 12.7139 | 12.5484 | NaN | NaN | NaN | 12.9098 | 121.5902 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 560.7308 | NaN | 36.6233 | NaN | 14.3714
4730.1448 | 13.1597 | 12.8014 | 12.9459 | 13.1791 | 12.724 | 12.8835 | 12.6987 | 12.544 | NaN | NaN | NaN | 12.9328 | 126.7603 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 560.5507 | NaN | 22.6493 | NaN | 24.0557
4731.176 | 13.1541 | 12.8113 | 12.9417 | 13.119 | 12.7196 | 12.8839 | 12.6983 | 12.5451 | NaN | NaN | NaN | 12.9014 | 125.8975 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 559.9725 | NaN | 23.4175 | NaN | 15.9022
4732.1448 | 13.1548 | 12.8285 | 12.9431 | 13.1142 | 12.6724 | 12.9027 | 12.7005 | 12.5508 | NaN | NaN | NaN | 12.9558 | 126.1312 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 559.7098 | NaN | 11.1594 | NaN | 26.8097
4733.2698 | 13.1342 | 12.8072 | 12.9409 | 13.1561 | 12.6785 | 12.8905 | 12.7061 | 12.545 | NaN | NaN | NaN | 12.9266 | 124.1574 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 560.4122 | NaN | 8.8548 | NaN | 21.7253
4734.1448 | 13.1659 | 12.8563 | 12.9466 | 13.1861 | 12.6596 | 12.9322 | 12.7047 | 12.5423 | NaN | NaN | NaN | 12.9104 | 122.3285 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 560.8332 | NaN | 12.6351 | NaN | 26.3851
4735.2385 | 13.1471 | 12.7962 | 12.9495 | 13.168 | 12.6806 | 12.8955 | 12.7052 | 12.5471 | NaN | NaN | NaN | 12.9288 | 120.2605 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 560.8473 | NaN | 26.6114 | NaN | 15.0557
4736.1292 | 13.2383 | 12.8543 | 12.9496 | 13.1452 | 12.722 | 12.9207 | 12.7182 | 12.5434 | NaN | NaN | NaN | 12.9113 | 119.6056 | NaN | NaN | NaN | -13.8432 | NaN | NaN | NaN | NaN | 560.7949 | NaN | 25.7097 | NaN | 17.4179
4737.1292 | 13.1876 | 12.7998 | 12.9448 | 13.1644 | 12.7086 | 12.8824 | 12.7035 | 12.5467 | NaN | NaN | NaN | 12.9221 | 118.4883 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 560.545 | NaN | 17.1427 | NaN | 22.5674
4738.1292 | 13.1608 | 12.8164 | 12.9418 | 13.1648 | 12.6574 | 12.8833 | 12.7018 | 12.548 | NaN | NaN | NaN | 12.9225 | 123.3615 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 559.6875 | NaN | 30.4868 | NaN | 17.4209
4739.1292 | 13.1732 | 12.8951 | 12.9372 | 13.1717 | 12.7079 | 12.9405 | 12.7272 | 12.5429 | NaN | NaN | NaN | 12.9184 | 120.0058 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 559.9831 | NaN | 26.9792 | NaN | 20.5372
4740.1292 | 13.1365 | 12.8618 | 12.9373 | 13.1715 | 12.7228 | 12.9162 | 12.7144 | 12.548 | NaN | NaN | NaN | 12.917 | 130.0081 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 560.0492 | NaN | 7.9663 | NaN | 19.1993
4741.1292 | 13.2145 | 12.8557 | 12.936 | 13.1719 | 12.7115 | 12.9135 | 12.7105 | 12.5511 | NaN | NaN | NaN | 12.9301 | 123.451 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 561.3112 | NaN | 18.7561 | NaN | 27.3082
4742.1292 | 13.2239 | 12.823 | 12.9348 | 13.1678 | 12.7387 | 12.8943 | 12.7016 | 12.555 | NaN | NaN | NaN | 12.914 | 128.2468 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 561.9593 | NaN | 15.5396 | NaN | 13.0923
4743.1292 | 13.174 | 12.8086 | 12.9357 | 13.1584 | 12.6582 | 12.8898 | 12.7016 | 12.5552 | NaN | NaN | NaN | 12.9188 | 118.964 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 561.307 | NaN | 16.8292 | NaN | 25.18
4744.1292 | 13.253 | 12.8275 | 12.9336 | 13.1845 | 12.6936 | 12.9056 | 12.7057 | 12.5522 | NaN | NaN | NaN | 13.057 | 131.3861 | NaN | NaN | NaN | -15.7412 | NaN | NaN | NaN | NaN | 559.3837 | NaN | 12.2525 | NaN | 26.7159
4745.1292 | 13.3467 | 12.8665 | 12.9418 | 13.1663 | 12.6281 | 12.8993 | 12.7034 | 12.5571 | NaN | NaN | NaN | 12.912 | 125.6442 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 560.2401 | NaN | 14.7877 | NaN | 20.4643
4746.1292 | 13.1805 | 12.8209 | 12.9374 | 13.1924 | 12.6282 | 12.8822 | 12.6924 | 12.5582 | NaN | NaN | NaN | 12.9358 | 126.223 | NaN | NaN | NaN | -11.1576 | NaN | NaN | NaN | NaN | 559.1937 | NaN | 18.9174 | NaN | 24.9564
4747.1292 | 13.1721 | 12.8229 | 12.9366 | 13.1456 | 12.6783 | 12.8795 | 12.6923 | 12.5607 | NaN | NaN | NaN | 12.9274 | 135.7249 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 561.0047 | NaN | 18.5971 | NaN | 22.3626
4748.1292 | 13.1654 | 12.8163 | 12.9371 | 13.1728 | 12.684 | 12.8896 | 12.7016 | 12.5555 | NaN | NaN | NaN | 12.9436 | 123.4224 | NaN | NaN | NaN | -0.6097 | NaN | NaN | NaN | NaN | 561.0537 | NaN | 17.1872 | NaN | 21.2106
4749.1292 | 13.2666 | 12.9515 | 12.9398 | 13.1547 | 12.6339 | 12.9755 | 12.7355 | 12.5512 | NaN | NaN | NaN | 12.9007 | 131.7336 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 558.0225 | NaN | 26.9112 | NaN | 23.6052
4750.1292 | 13.1547 | 12.9126 | 12.9445 | 13.1532 | 12.6988 | 12.9373 | 12.7333 | 12.5555 | NaN | NaN | NaN | 12.9427 | 125.759 | NaN | NaN | NaN | 3.6008 | NaN | NaN | NaN | NaN | 559.9078 | NaN | 13.8428 | NaN | 23.4602
4751.1292 | 13.1611 | 12.8746 | 12.9383 | 13.1288 | 12.629 | 12.9071 | 12.7168 | 12.5525 | NaN | NaN | NaN | 12.9173 | 123.0056 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 561.8592 | NaN | 14.1512 | NaN | 26.6627
4752.1292 | 13.1693 | 12.8302 | 12.9415 | 13.1774 | 12.7471 | 12.8904 | 12.7053 | 12.5498 | NaN | NaN | NaN | 12.9697 | 127.271 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 561.6565 | NaN | 15.7185 | NaN | 23.1856
4753.1292 | 13.128 | 12.9574 | 12.9536 | 13.2171 | 12.7374 | 12.9227 | 12.7643 | 12.5526 | NaN | NaN | NaN | 12.935 | 125.9356 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 560.1159 | NaN | 31.2764 | NaN | 32.844
4754.1292 | 13.1868 | 12.8758 | 12.9473 | 13.165 | 12.7316 | 12.8947 | 12.7127 | 12.5601 | NaN | NaN | NaN | 12.9058 | 119.7048 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 560.5464 | NaN | 20.4376 | NaN | 23.109
4755.1292 | 13.1781 | 12.8401 | 12.9471 | 13.2407 | 12.7243 | 12.9055 | 12.7162 | 12.5614 | NaN | NaN | NaN | 12.9791 | 123.6052 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 558.7603 | NaN | 20.0291 | NaN | 27.0353
4756.1292 | 13.1773 | 12.8172 | 12.9461 | 13.2101 | 12.6985 | 12.9 | 12.7163 | 12.5681 | NaN | NaN | NaN | 12.9478 | 114.1006 | NaN | NaN | NaN | -9.2116 | NaN | NaN | NaN | NaN | 561.2253 | NaN | 16.4367 | NaN | 16.9724
4757.1292 | 13.1494 | 12.8272 | 12.949 | 13.1937 | 12.7319 | 12.895 | 12.7023 | 12.5623 | NaN | NaN | NaN | 12.9223 | 127.1846 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 558.9881 | NaN | 35.2846 | NaN | 22.483
4758.1292 | 13.1772 | 12.8288 | 12.9472 | 13.2088 | 12.6657 | 12.8911 | 12.7017 | 12.5548 | NaN | NaN | NaN | 12.9532 | 134.9032 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 563.1837 | NaN | 6.2128 | NaN | 24.8331
4759.1292 | 13.1558 | 12.8188 | 12.9604 | 13.1514 | 12.6486 | 12.8947 | 12.7137 | 12.5513 | NaN | NaN | NaN | 12.9454 | 121.7715 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 563.3576 | NaN | 20.5256 | NaN | 19.9791
4760.1292 | 13.1859 | 12.8324 | 12.9628 | 13.1899 | 12.7228 | 12.8885 | 12.7092 | 12.5528 | NaN | NaN | NaN | 12.9302 | 120.4316 | NaN | NaN | NaN | -5.3513 | NaN | NaN | NaN | NaN | 562.1456 | NaN | 16.949 | NaN | 20.3931
4761.1292 | 13.185 | 12.8582 | 12.9631 | 13.2028 | 12.7324 | 12.923 | 12.7226 | 12.5493 | NaN | NaN | NaN | 12.971 | 132.0592 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 563.5883 | NaN | 12.0708 | NaN | 23.6075
4762.1292 | 13.1912 | 12.8161 | 12.967 | 13.195 | 12.6905 | 12.9077 | 12.7167 | 12.5507 | NaN | NaN | NaN | 12.9379 | 128.2173 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 564.7117 | NaN | 26.3453 | NaN | 16.0827
4763.1292 | 13.1926 | 12.8274 | 12.9645 | 13.1768 | 12.7216 | 12.8993 | 12.7108 | 12.5468 | NaN | NaN | NaN | 12.9221 | 124.1979 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 562.8021 | NaN | 7.5379 | NaN | 23.1625
4764.1292 | 13.1751 | 12.8243 | 12.9663 | 13.2118 | 12.7053 | 12.8995 | 12.6967 | 12.547 | NaN | NaN | NaN | 12.9418 | 126.9366 | NaN | NaN | NaN | -14.7169 | NaN | NaN | NaN | NaN | 562.4034 | NaN | 13.7635 | NaN | 24.7762
4765.1292 | 13.1648 | 12.8159 | 12.967 | 13.1616 | 12.732 | 12.8963 | 12.6995 | 12.5515 | NaN | NaN | NaN | 12.942 | 119.2659 | NaN | NaN | NaN | 14.7308 | NaN | NaN | NaN | NaN | 562.2785 | NaN | 15.0104 | NaN | 27.2388
4766.1292 | 13.2673 | 12.8299 | 12.9619 | 13.1969 | 12.6706 | 12.9063 | 12.7038 | 12.5479 | NaN | NaN | NaN | 12.9417 | 122.8122 | NaN | NaN | NaN | -4.9356 | NaN | NaN | NaN | NaN | 560.4481 | NaN | 27.2378 | NaN | 29.6106
4767.1292 | 13.1941 | 12.8545 | 12.9663 | 13.2103 | 12.7048 | 12.918 | 12.7052 | 12.5467 | NaN | NaN | NaN | 12.9453 | 122.4312 | NaN | NaN | NaN | 1.5892 | NaN | NaN | NaN | NaN | 562.501 | NaN | 10.2118 | NaN | 20.5931
4768.1292 | 13.1772 | 12.8237 | 12.9675 | 13.2088 | 12.7203 | 12.9022 | 12.6888 | 12.5438 | NaN | NaN | NaN | 12.9408 | 124.2801 | NaN | NaN | NaN | -3.6922 | NaN | NaN | NaN | NaN | 561.5041 | NaN | 23.3202 | NaN | 29.1818
4769.1292 | 13.1753 | 12.8426 | 12.9668 | 13.2138 | 12.7213 | 12.9116 | 12.6852 | 12.5467 | NaN | NaN | NaN | 12.984 | 129.3547 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 559.5638 | NaN | 11.8415 | NaN | 22.028
4770.1292 | 13.2755 | 12.854 | 12.9699 | 13.2026 | 12.7559 | 12.9101 | 12.6852 | 12.5448 | NaN | NaN | NaN | 12.9637 | 118.3568 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 561.4734 | NaN | 24.2398 | NaN | 22.9151
4771.1292 | 13.1721 | 12.8487 | 12.9758 | 13.21 | 12.7267 | 12.9198 | 12.698 | 12.5431 | NaN | NaN | NaN | 12.929 | 122.8645 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 560.0452 | NaN | 16.6438 | NaN | 17.0548
4772.1292 | 13.1779 | 12.8822 | 12.9725 | 13.2194 | 12.732 | 12.9304 | 12.6986 | 12.5427 | NaN | NaN | NaN | 12.9411 | 129.2465 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 559.095 | NaN | 18.2491 | NaN | 29.2005
4773.1292 | 13.1809 | 12.8868 | 12.9714 | 13.1477 | 12.7388 | 12.9224 | 12.6889 | 12.5457 | NaN | NaN | NaN | 12.9495 | 119.9284 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 562.5956 | NaN | 22.0748 | NaN | 20.5717
4774.1292 | 13.1703 | 12.8695 | 12.9749 | 13.2298 | 12.7492 | 12.9235 | 12.6876 | 12.5494 | NaN | NaN | NaN | 12.9463 | 119.6658 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 561.4875 | NaN | 16.2753 | NaN | 22.1938
4775.1292 | 13.2042 | 12.901 | 12.9687 | 13.1903 | 12.7139 | 12.9545 | 12.7053 | 12.5468 | NaN | NaN | NaN | 12.9611 | 132.0727 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 561.1133 | NaN | 22.6902 | NaN | 27.823
4776.1292 | 13.2295 | 12.8414 | 12.9711 | 13.2079 | 12.7223 | 12.9176 | 12.6836 | 12.553 | NaN | NaN | NaN | 12.948 | 126.6522 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 563.1181 | NaN | 11.3937 | NaN | 20.1317
4777.1292 | 13.1702 | 12.8509 | 12.9653 | 13.1973 | 12.6957 | 12.9263 | 12.6818 | 12.5524 | NaN | NaN | NaN | 12.9529 | 129.6585 | NaN | NaN | NaN | -5.552 | NaN | NaN | NaN | NaN | 561.7491 | NaN | 9.2378 | NaN | 22.9051
4778.1292 | 13.1369 | 12.8645 | 12.9734 | 13.1871 | 12.6451 | 12.9301 | 12.6837 | 12.5512 | NaN | NaN | NaN | 12.9446 | 129.3138 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 561.5616 | NaN | 15.8034 | NaN | 23.173
4779.1292 | 13.1317 | 12.8252 | 12.963 | 13.197 | 12.6693 | 12.9245 | 12.6812 | 12.5613 | NaN | NaN | NaN | 13.0019 | 127.9301 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 559.4941 | NaN | 29.2627 | NaN | 28.4149
4780.1292 | 13.1651 | 12.8534 | 12.9637 | 13.1548 | 12.6674 | 12.9369 | 12.6853 | 12.5578 | NaN | NaN | NaN | 12.9669 | 127.178 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 561.5536 | NaN | 18.0716 | NaN | 25.8945
4781.1292 | 13.1867 | 12.8258 | 12.9643 | 13.1961 | 12.6577 | 12.9399 | 12.687 | 12.5614 | NaN | NaN | NaN | 12.9631 | 127.8416 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 560.1578 | NaN | 21.8059 | NaN | 18.5478
4782.1292 | 13.176 | 12.9637 | 12.9737 | 13.1912 | 12.6726 | 12.9869 | 12.7203 | 12.5682 | NaN | NaN | NaN | 12.9339 | 121.9959 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 558.0247 | NaN | 18.8235 | NaN | 28.1598
4783.1292 | 13.1708 | 12.7977 | 12.973 | 13.1886 | 12.7029 | 12.9116 | 12.6707 | 12.5703 | NaN | NaN | NaN | 12.9921 | 129.6313 | NaN | NaN | NaN | -19.4649 | NaN | NaN | NaN | NaN | 560.1513 | NaN | 29.3588 | NaN | 19.9098
4784.1292 | 13.1592 | 12.8393 | 12.9693 | 13.1646 | 12.7646 | 12.9324 | 12.6839 | 12.5673 | NaN | NaN | NaN | 12.9974 | 121.043 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 557.3579 | NaN | 8.5633 | NaN | 21.52
4785.1292 | 13.1605 | 12.8478 | 12.9644 | 13.1886 | 12.7251 | 12.9409 | 12.68 | 12.5663 | NaN | NaN | NaN | 12.9437 | 132.9499 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 558.4829 | NaN | 20.6534 | NaN | 21.4107
4786.1292 | 13.1537 | 12.7985 | 12.9554 | 13.2308 | 12.7299 | 12.9212 | 12.6831 | 12.564 | NaN | NaN | NaN | 13.0346 | 120.3092 | NaN | NaN | NaN | -9.2344 | NaN | NaN | NaN | NaN | 560.6861 | NaN | 10.5667 | NaN | 22.3857
4787.1448 | 13.1253 | 12.8315 | 12.9521 | 13.2056 | 12.6414 | 12.9465 | 12.6772 | 12.5587 | NaN | NaN | NaN | 12.974 | 115.987 | NaN | NaN | NaN | -13.3064 | NaN | NaN | NaN | NaN | 558.4935 | NaN | 28.8652 | NaN | 25.676
4788.1292 | 13.188 | 12.8467 | 12.9538 | 13.1691 | 12.6643 | 12.9572 | 12.6793 | 12.5587 | NaN | NaN | NaN | 12.9533 | 123.0755 | NaN | NaN | NaN | -1.2614 | NaN | NaN | NaN | NaN | 562.6763 | NaN | 29.9602 | NaN | 21.9254
4789.1292 | 13.1578 | 12.7774 | 12.9464 | 13.2366 | 12.6863 | 12.906 | 12.6753 | 12.5621 | NaN | NaN | NaN | 12.96 | 122.9323 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 564.0656 | NaN | 16.2447 | NaN | 26.6856
4790.1292 | 13.151 | 12.8206 | 12.9498 | 13.1583 | 12.7559 | 12.9139 | 12.689 | 12.5544 | NaN | NaN | NaN | 12.9465 | 130.4054 | NaN | NaN | NaN | 2.9428 | NaN | NaN | NaN | NaN | 557.6754 | NaN | 14.1854 | NaN | 20.8198
4791.1292 | 13.1575 | 12.7837 | 12.9537 | 13.2044 | 12.7037 | 12.9133 | 12.6793 | 12.5587 | NaN | NaN | NaN | 12.9507 | 128.7117 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 559.9569 | NaN | 12.8694 | NaN | 25.5393
4792.1292 | 13.1568 | 12.8506 | 12.9443 | 13.2261 | 12.7014 | 12.9239 | 12.6973 | 12.5533 | NaN | NaN | NaN | 12.9979 | 116.4747 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 562.0065 | NaN | 16.3973 | NaN | 19.342
4793.1292 | 13.155 | 12.8723 | 12.9503 | 13.2393 | 12.7005 | 12.9299 | 12.6909 | 12.545 | NaN | NaN | NaN | 12.9529 | 126.2314 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 561.9268 | NaN | 26.4656 | NaN | 24.4782
4794.1292 | 13.1446 | 12.8078 | 12.9435 | 13.1674 | 12.6961 | 12.9152 | 12.6894 | 12.5482 | NaN | NaN | NaN | 12.9631 | 122.3264 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 562.7884 | NaN | 27.3261 | NaN | 18.8671
4795.1292 | 13.1395 | 12.8094 | 12.9379 | 13.2467 | 12.7355 | 12.9117 | 12.6918 | 12.5495 | NaN | NaN | NaN | 12.9667 | 121.7281 | NaN | NaN | NaN | -19.4132 | NaN | NaN | NaN | NaN | 561.4328 | NaN | 16.274 | NaN | 27.3241
4796.1292 | 13.2103 | 12.8041 | 12.9455 | 13.1673 | 12.7117 | 12.902 | 12.6842 | 12.545 | NaN | NaN | NaN | 13.0052 | 123.4918 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 562.1224 | NaN | 12.1498 | NaN | 24.1655
4797.1292 | 13.1466 | 12.8792 | 12.9433 | 13.2104 | 12.6632 | 12.9399 | 12.7054 | 12.5421 | NaN | NaN | NaN | 12.9529 | 128.5308 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 561.1316 | NaN | 29.0578 | NaN | 22.4348
4798.1292 | 13.248 | 12.8468 | 12.9476 | 13.2591 | 12.6451 | 12.9234 | 12.6923 | 12.5445 | NaN | NaN | NaN | 12.9398 | 122.9535 | NaN | NaN | NaN | -0.8938 | NaN | NaN | NaN | NaN | 560.0964 | NaN | 13.3031 | NaN | 24.3002
4799.1292 | 13.1732 | 12.8887 | 12.9473 | 13.1829 | 12.7159 | 12.9248 | 12.702 | 12.547 | NaN | NaN | NaN | 12.9316 | 124.6398 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 561.2159 | NaN | 25.3217 | NaN | 22.6198
4800.1292 | 13.1773 | 12.7984 | 12.9414 | 13.1904 | 12.6799 | 12.895 | 12.6842 | 12.5445 | NaN | NaN | NaN | 12.9333 | 116.1056 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 561.5347 | NaN | 15.2871 | NaN | 29.5454
4801.1292 | 13.1645 | 12.8652 | 12.9469 | 13.2057 | 12.7107 | 12.9332 | 12.7059 | 12.5498 | NaN | NaN | NaN | 12.9563 | 127.28 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 562.233 | NaN | 30.6634 | NaN | 18.782
4802.1292 | 13.1583 | 12.842 | 12.9478 | 13.2383 | 12.7267 | 12.9225 | 12.7033 | 12.5485 | NaN | NaN | NaN | 12.976 | 127.3191 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 560.2121 | NaN | 3.3223 | NaN | 21.5635
4803.1292 | 13.1471 | 12.8263 | 12.955 | 13.2114 | 12.657 | 12.9141 | 12.7023 | 12.5509 | NaN | NaN | NaN | 12.9741 | 124.8002 | NaN | NaN | NaN | -19.4485 | NaN | NaN | NaN | NaN | 561.0783 | NaN | 33.529 | NaN | 29.7463
4804.1292 | 13.1579 | 12.8531 | 12.9554 | 13.1905 | 12.6567 | 12.9214 | 12.6948 | 12.5558 | NaN | NaN | NaN | 12.9652 | 121.1854 | NaN | NaN | NaN | -16.6826 | NaN | NaN | NaN | NaN | 562.875 | NaN | 27.4031 | NaN | 27.8485
4805.1292 | 13.141 | 12.8219 | 12.954 | 13.2862 | 12.7051 | 12.9061 | 12.6943 | 12.5513 | NaN | NaN | NaN | 12.9576 | 131.2267 | NaN | NaN | NaN | -1.7086 | NaN | NaN | NaN | NaN | 559.5055 | NaN | 26.6483 | NaN | 20.4426
4806.1292 | 13.1367 | 12.8428 | 12.9563 | 13.2036 | 12.7401 | 12.9144 | 12.7012 | 12.5513 | NaN | NaN | NaN | 12.984 | 122.9744 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 559.3698 | NaN | 11.4447 | NaN | 30.9231
4807.1292 | 13.2043 | 12.8351 | 12.9531 | 13.2212 | 12.6 | 12.9213 | 12.7004 | 12.5455 | NaN | NaN | NaN | 12.9596 | 118.2187 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 560.3088 | NaN | 30.5616 | NaN | 24.7893
4808.1292 | 13.1524 | 12.8743 | 12.9534 | 13.2029 | 12.7378 | 12.9321 | 12.7129 | 12.5551 | NaN | NaN | NaN | 12.9515 | 126.3108 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 557.721 | NaN | 9.071 | NaN | 23.4915
4809.1292 | 13.1843 | 12.837 | 12.9469 | 13.1923 | 12.6308 | 12.9117 | 12.708 | 12.5552 | NaN | NaN | NaN | 12.9376 | 127.4565 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 559.8639 | NaN | 17.7458 | NaN | 21.417
4810.1292 | 13.1762 | 12.842 | 12.9526 | 13.2455 | 12.7055 | 12.9034 | 12.7033 | 12.5517 | NaN | NaN | NaN | 12.9627 | 125.1246 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 560.7632 | NaN | 24.5523 | NaN | 17.7079
4811.1292 | 13.3318 | 12.8702 | 12.9487 | 13.1922 | 12.6685 | 12.934 | 12.726 | 12.5532 | NaN | NaN | NaN | 12.9375 | 130.7414 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 558.7208 | NaN | 12.3365 | NaN | 30.1853
4812.1292 | 13.1868 | 12.8386 | 12.9542 | 13.1536 | 12.7049 | 12.9112 | 12.7068 | 12.5475 | NaN | NaN | NaN | 12.9471 | 123.1585 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 560.0697 | NaN | 32.6567 | NaN | 23.9931
4813.1292 | 13.1849 | 12.8588 | 12.9508 | 13.1598 | 12.6686 | 12.9307 | 12.7191 | 12.5522 | NaN | NaN | NaN | 12.974 | 121.5838 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 562.4365 | NaN | 2.7093 | NaN | 23.8793
4814.1292 | 13.1865 | 12.8476 | 12.9512 | 13.1933 | 12.6688 | 12.9142 | 12.7105 | 12.5598 | NaN | NaN | NaN | 12.947 | 132.9917 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 560.9725 | NaN | 28.1819 | NaN | 23.3353
4815.1292 | 13.1914 | 12.92 | 12.9557 | 13.1508 | 12.6283 | 12.9685 | 12.718 | 12.5593 | NaN | NaN | NaN | 12.9612 | 129.0543 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 561.8135 | NaN | 20.7586 | NaN | 26.031
4816.1448 | 13.1942 | 12.8481 | 12.9542 | 13.1676 | 12.6955 | 12.9173 | 12.7163 | 12.5611 | NaN | NaN | NaN | 12.9444 | 137.4161 | NaN | NaN | NaN | -2.2165 | NaN | NaN | NaN | NaN | 559.6863 | NaN | 22.8114 | NaN | 24.5589
4817.1448 | 13.1905 | 12.8895 | 12.9559 | 13.2061 | 12.7078 | 12.9356 | 12.7233 | 12.5636 | NaN | NaN | NaN | 12.9696 | 128.903 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 560.6356 | NaN | 23.0106 | NaN | 19.5879
4818.1292 | 13.1915 | 12.8809 | 12.9557 | 13.1668 | 12.7305 | 12.9249 | 12.7243 | 12.5572 | NaN | NaN | NaN | 12.9336 | 127.5163 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 559.6743 | NaN | 12.5612 | NaN | 16.923
4819.1448 | 13.2138 | 12.9104 | 12.9578 | 13.1567 | 12.7178 | 12.9155 | 12.7256 | 12.5624 | NaN | NaN | NaN | 12.9762 | 137.67 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 557.3559 | NaN | 8.3221 | NaN | 16.6454
4820.1292 | 13.1713 | 12.8855 | 12.9592 | 13.1619 | 12.671 | 12.9223 | 12.7162 | 12.5587 | NaN | NaN | NaN | 13.0188 | 128.5222 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 558.9041 | NaN | 25.9868 | NaN | 17.3452
4821.1448 | 13.1749 | 12.8381 | 12.9466 | 13.1696 | 12.7235 | 12.9105 | 12.7065 | 12.5647 | NaN | NaN | NaN | 12.9497 | 118.0536 | NaN | NaN | NaN | -15.6017 | NaN | NaN | NaN | NaN | 557.0604 | NaN | 25.4642 | NaN | 26.3731
4822.1292 | 13.1725 | 12.9376 | 12.9557 | 13.1629 | 12.7144 | 12.94 | 12.7311 | 12.569 | NaN | NaN | NaN | 13.0384 | 128.5888 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 557.043 | NaN | 29.1229 | NaN | 23.1771
4823.1448 | 13.1919 | 12.8715 | 12.9495 | 13.1496 | 12.6901 | 12.9319 | 12.7211 | 12.5731 | NaN | NaN | NaN | 12.9705 | 123.8888 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 559.2797 | NaN | 14.8139 | NaN | 32.2987
4824.1292 | 13.1574 | 12.8855 | 12.9615 | 13.1368 | 12.7597 | 12.9254 | 12.7203 | 12.5744 | NaN | NaN | NaN | 12.9634 | 124.6404 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 559.0938 | NaN | 26.1773 | NaN | 25.0625
4825.1292 | 13.1932 | 12.8374 | 12.9544 | 13.1777 | 12.7154 | 12.9114 | 12.7012 | 12.5706 | NaN | NaN | NaN | 12.9597 | 121.852 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 559.6785 | NaN | 31.3845 | NaN | 29.7255
4826.1292 | 13.1892 | 12.8722 | 12.9561 | 13.1748 | 12.6421 | 12.931 | 12.722 | 12.5699 | NaN | NaN | NaN | 12.9332 | 119.6733 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 561.1087 | NaN | 29.4446 | NaN | 30.2509
4827.1292 | 13.176 | 12.8574 | 12.9589 | 13.1698 | 12.7268 | 12.9137 | 12.7122 | 12.5692 | NaN | NaN | NaN | 12.9597 | 122.952 | NaN | NaN | NaN | -3.1642 | NaN | NaN | NaN | NaN | 559.0529 | NaN | 20.0159 | NaN | 23.0585
4828.1292 | 13.1993 | 12.8564 | 12.9567 | 13.1573 | 12.7537 | 12.9196 | 12.7217 | 12.5751 | NaN | NaN | NaN | 12.9491 | 120.37 | NaN | NaN | NaN | -2.7898 | NaN | NaN | NaN | NaN | 559.2937 | NaN | 11.3838 | NaN | 16.1018
4829.1292 | 13.1911 | 12.898 | 12.9621 | 13.1753 | 12.6848 | 12.9498 | 12.7258 | 12.5745 | NaN | NaN | NaN | 12.9699 | 132.2276 | NaN | NaN | NaN | 3.258 | NaN | NaN | NaN | NaN | 557.6613 | NaN | 12.2177 | NaN | 23.4002
4830.1292 | 13.1871 | 12.8582 | 12.9583 | 13.1265 | 12.7143 | 12.9174 | 12.7223 | 12.5679 | NaN | NaN | NaN | 12.9338 | 115.1039 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 561.0879 | NaN | 14.8759 | NaN | 21.9948
4831.1292 | 13.2 | 12.8649 | 12.9657 | 13.1775 | 12.7214 | 12.927 | 12.7278 | 12.565 | NaN | NaN | NaN | 12.9474 | 121.1245 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 562.9337 | NaN | 7.8917 | NaN | 22.947
4832.1292 | 13.17 | 12.8884 | 12.9606 | 13.1774 | 12.6671 | 12.9659 | 12.7372 | 12.5677 | NaN | NaN | NaN | 12.9224 | 129.7397 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 560.2679 | NaN | 29.6828 | NaN | 22.8443
4833.1292 | 13.2288 | 12.9328 | 12.9559 | 13.1527 | 12.6574 | 12.9775 | 12.7531 | 12.5652 | NaN | NaN | NaN | 12.9285 | 118.3087 | NaN | NaN | NaN | -16.6243 | NaN | NaN | NaN | NaN | 560.4196 | NaN | 24.5718 | NaN | 23.0835
4834.1292 | 13.2175 | 12.9003 | 12.9565 | 13.1366 | 12.7287 | 12.9261 | 12.7203 | 12.5677 | NaN | NaN | NaN | 12.9203 | 130.4076 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 559.2029 | NaN | 31.0817 | NaN | 26.4407
4835.1292 | 13.2239 | 12.8726 | 12.9584 | 13.1697 | 12.6317 | 12.9452 | 12.7267 | 12.5648 | NaN | NaN | NaN | 12.9331 | 114.6812 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 557.1881 | NaN | 24.8302 | NaN | 19.1474
4836.1292 | 13.2513 | 12.8904 | 12.9617 | 13.101 | 12.6446 | 12.9408 | 12.7335 | 12.5602 | NaN | NaN | NaN | 12.9328 | 123.2979 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 559.5355 | NaN | 20.7769 | NaN | 18.098
4837.1292 | 13.2019 | 12.8585 | 12.9538 | 13.1532 | 12.6854 | 12.9096 | 12.7083 | 12.5576 | NaN | NaN | NaN | 12.9393 | 119.7081 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 559.0873 | NaN | 28.066 | NaN | 14.3265
4838.1292 | 13.2337 | 12.9203 | 12.966 | 13.19 | 12.679 | 12.958 | 12.7348 | 12.5541 | NaN | NaN | NaN | 12.9448 | 124.0286 | NaN | NaN | NaN | 12.3426 | NaN | NaN | NaN | NaN | 559.3369 | NaN | 20.9704 | NaN | 26.5562
4839.1292 | 13.2172 | 12.9083 | 12.9664 | 13.1301 | 12.6608 | 12.9659 | 12.7393 | 12.5557 | NaN | NaN | NaN | 12.9333 | 122.8998 | NaN | NaN | NaN | 5.8124 | NaN | NaN | NaN | NaN | 559.1725 | NaN | 21.5732 | NaN | 18.9949
4840.1292 | 13.1971 | 13.0039 | 12.9645 | 13.2204 | 12.6321 | 13.0028 | 12.7731 | 12.5594 | NaN | NaN | NaN | 12.9592 | 122.8263 | NaN | NaN | NaN | -19.2752 | NaN | NaN | NaN | NaN | 560.7906 | NaN | 10.807 | NaN | 23.5937
4841.1292 | 13.2074 | 12.8954 | 12.9721 | 13.1718 | 12.6068 | 12.9451 | 12.7111 | 12.558 | NaN | NaN | NaN | 12.9352 | 124.3756 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 559.5042 | NaN | 27.0672 | NaN | 22.5817
4842.1292 | 13.2164 | 12.8623 | 12.9588 | 13.1634 | 12.7195 | 12.932 | 12.7156 | 12.5597 | NaN | NaN | NaN | 12.9247 | 126.7621 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 560.5606 | NaN | 5.7451 | NaN | 24.8184
4843.1448 | 13.1853 | 12.9592 | 12.9573 | 13.1521 | 12.7098 | 12.9648 | 12.7222 | 12.5661 | NaN | NaN | NaN | 12.9628 | 120.1651 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 560.659 | NaN | 37.7484 | NaN | 25.7604
4844.1292 | 13.2376 | 12.8998 | 12.9589 | 13.1371 | 12.6662 | 12.9462 | 12.72 | 12.5694 | NaN | NaN | NaN | 12.9713 | 124.0515 | NaN | NaN | NaN | 0.8726 | NaN | NaN | NaN | NaN | 560.2968 | NaN | 23.8099 | NaN | 24.5314
4845.1292 | 13.2164 | 12.8763 | 12.954 | 13.1638 | 12.6314 | 12.9331 | 12.7187 | 12.5599 | NaN | NaN | NaN | 12.9242 | 125.4384 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 559.0384 | NaN | 22.0809 | NaN | 26.092
4846.1292 | 13.2193 | 12.9343 | 12.9555 | 13.1155 | 12.6105 | 12.9532 | 12.7154 | 12.5586 | NaN | NaN | NaN | 12.9288 | 121.6547 | NaN | NaN | NaN | -19.543 | NaN | NaN | NaN | NaN | 558.4293 | NaN | 20.5691 | NaN | 24.8071
4847.1448 | 13.2095 | 12.879 | 12.9569 | 13.1658 | 12.6823 | 12.9165 | 12.7176 | 12.5612 | NaN | NaN | NaN | 12.8973 | 127.4717 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 557.6238 | NaN | 13.7469 | NaN | 24.9013
4848.1292 | 13.1706 | 12.8851 | 12.9604 | 13.1171 | 12.7154 | 12.9198 | 12.7144 | 12.5638 | NaN | NaN | NaN | 12.9251 | 127.8071 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 558.5651 | NaN | 35.6385 | NaN | 29.0412
4849.1292 | 13.2156 | 12.8998 | 12.9639 | 13.1478 | 12.7575 | 12.9199 | 12.7226 | 12.5646 | NaN | NaN | NaN | 12.9229 | 132.8127 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 559.955 | NaN | 14.2495 | NaN | 27.1299
4850.1292 | 13.2179 | 12.8797 | 12.9622 | 13.174 | 12.6198 | 12.9287 | 12.7162 | 12.5658 | NaN | NaN | NaN | 12.9298 | 122.8481 | NaN | NaN | NaN | -3.3175 | NaN | NaN | NaN | NaN | 558.7986 | NaN | 27.2585 | NaN | 24.0892
4851.1292 | 13.2223 | 12.8679 | 12.9587 | 13.1607 | 12.6423 | 12.9135 | 12.7017 | 12.5606 | NaN | NaN | NaN | 12.9069 | 132.9327 | NaN | NaN | NaN | -11.5688 | NaN | NaN | NaN | NaN | 558.603 | NaN | 27.0619 | NaN | 23.7059
4852.1292 | 13.2235 | 12.9357 | 12.9626 | 13.1605 | 12.7445 | 12.9386 | 12.7218 | 12.5583 | NaN | NaN | NaN | 12.9368 | 124.2514 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 558.6134 | NaN | 25.2842 | NaN | 18.0464
4853.1292 | 13.2184 | 12.9833 | 12.9539 | 13.1206 | 12.7191 | 12.9399 | 12.7491 | 12.5586 | NaN | NaN | NaN | 12.9262 | 121.0345 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 560.2724 | NaN | 22.3799 | NaN | 22.0027
4854.1292 | 13.2067 | 12.8633 | 12.9565 | 13.1392 | 12.6294 | 12.9077 | 12.714 | 12.5517 | NaN | NaN | NaN | 12.9236 | 124.6231 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 558.7818 | NaN | 24.4689 | NaN | 15.3958
4855.1292 | 13.218 | 12.8941 | 12.9587 | 13.1299 | 12.6204 | 12.9412 | 12.7289 | 12.5537 | NaN | NaN | NaN | 12.9253 | 121.2498 | NaN | NaN | NaN | -2.2402 | NaN | NaN | NaN | NaN | 560.4676 | NaN | 21.8686 | NaN | 24.7041
4856.1292 | 13.2417 | 12.9708 | 12.9564 | 13.1882 | 12.6462 | 12.9668 | 12.739 | 12.5507 | NaN | NaN | NaN | 12.9101 | 128.9529 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 553.4369 | NaN | 11.3329 | NaN | 28.4625
4857.1292 | 13.2422 | 12.8969 | 12.961 | 13.1436 | 12.746 | 12.9406 | 12.7207 | 12.5447 | NaN | NaN | NaN | 12.9006 | 115.8664 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 557.381 | NaN | 26.6821 | NaN | 23.7659
4858.1292 | 13.1988 | 12.8959 | 12.9538 | 13.0836 | 12.6773 | 12.9516 | 12.7195 | 12.5483 | NaN | NaN | NaN | 12.9286 | 122.7502 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 558.0871 | NaN | 16.3318 | NaN | 26.1233
4859.1292 | 13.2872 | 12.9561 | 12.9647 | 13.1202 | 12.6259 | 12.9789 | 12.7244 | 12.5384 | NaN | NaN | NaN | 12.874 | 125.946 | NaN | NaN | NaN | -19.4589 | NaN | NaN | NaN | NaN | 558.2571 | NaN | 14.0917 | NaN | 25.6153
4860.1292 | 13.2547 | 12.8714 | 12.9603 | 13.1304 | 12.6656 | 12.9495 | 12.7303 | 12.5326 | NaN | NaN | NaN | 12.8899 | 119.4937 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 557.8239 | NaN | 23.8984 | NaN | 16.181
4861.1292 | 13.2733 | 12.9064 | 12.9641 | 13.1289 | 12.662 | 12.9769 | 12.7333 | 12.5448 | NaN | NaN | NaN | 12.9259 | 120.4421 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 559.2337 | NaN | 29.0084 | NaN | 24.4711
4862.1292 | 13.2276 | 12.8972 | 12.9594 | 13.124 | 12.737 | 12.945 | 12.7253 | 12.5391 | NaN | NaN | NaN | 12.9279 | 128.5208 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 561.7599 | NaN | 27.9605 | NaN | 26.9133
4863.1292 | 13.2248 | 12.8646 | 12.9643 | 13.1255 | 12.7402 | 12.9334 | 12.7223 | 12.5454 | NaN | NaN | NaN | 12.933 | 125.4974 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 560.9977 | NaN | 33.2305 | NaN | 27.8236
4864.1292 | 13.2162 | 12.8518 | 12.9498 | 13.1468 | 12.6606 | 12.9246 | 12.7188 | 12.5445 | NaN | NaN | NaN | 12.9285 | 123.311 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 557.6869 | NaN | 13.3949 | NaN | 23.1136
4865.1292 | 13.208 | 12.8798 | 12.9432 | 13.0822 | 12.6867 | 12.954 | 12.7386 | 12.5505 | NaN | NaN | NaN | 12.9372 | 121.5027 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 560.5681 | NaN | 15.7946 | NaN | 25.4292
4866.1292 | 13.275 | 12.8712 | 12.9436 | 13.1118 | 12.7349 | 12.9457 | 12.727 | 12.5537 | NaN | NaN | NaN | 12.9219 | 120.8075 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 559.746 | NaN | 21.1552 | NaN | 24.9274
4867.1292 | 13.23 | 12.8985 | 12.9409 | 13.2247 | 12.7533 | 12.94 | 12.7323 | 12.5542 | NaN | NaN | NaN | 12.9225 | 135.4701 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 558.3518 | NaN | 10.1902 | NaN | 13.0285
4868.1292 | 13.2219 | 12.9032 | 12.937 | 13.0961 | 12.6505 | 12.9701 | 12.7404 | 12.5544 | NaN | NaN | NaN | 12.9642 | 132.542 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 557.4838 | NaN | 24.3666 | NaN | 26.8277
4869.1292 | 13.1843 | 12.8595 | 12.942 | 13.133 | 12.6757 | 12.9428 | 12.7229 | 12.5651 | NaN | NaN | NaN | 12.9105 | 125.2686 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 555.936 | NaN | 24.7757 | NaN | 17.1568
4870.1292 | 13.2332 | 12.9276 | 12.939 | 13.1329 | 12.6684 | 12.9616 | 12.7374 | 12.5633 | NaN | NaN | NaN | 12.914 | 118.4637 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 556.1299 | NaN | 23.3935 | NaN | 27.3109
4871.1292 | 13.2142 | 12.8577 | 12.9409 | 13.1996 | 12.6125 | 12.9484 | 12.7268 | 12.5604 | NaN | NaN | NaN | 12.9595 | 127.0924 | NaN | NaN | NaN | -13.2656 | NaN | NaN | NaN | NaN | 557.9178 | NaN | 19.6904 | NaN | 25.0307
4872.1292 | 13.3932 | 12.846 | 12.9452 | 13.1858 | 12.7154 | 12.9343 | 12.7178 | 12.5666 | NaN | NaN | NaN | 12.8903 | 122.9965 | NaN | NaN | NaN | -18.8761 | NaN | NaN | NaN | NaN | 556.7404 | NaN | 12.8186 | NaN | 21.3364
4873.1292 | 13.2145 | 12.9181 | 12.944 | 13.1908 | 12.7491 | 12.9501 | 12.7264 | 12.5561 | NaN | NaN | NaN | 12.9118 | 141.181 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 555.9699 | NaN | 35.0529 | NaN | 19.8136
4874.1292 | 13.1972 | 12.8673 | 12.944 | 13.2088 | 12.7221 | 12.9473 | 12.7231 | 12.5607 | NaN | NaN | NaN | 12.9118 | 126.0967 | NaN | NaN | NaN | 21.1412 | NaN | NaN | NaN | NaN | 556.375 | NaN | 18.2542 | NaN | 19.7111
4875.1292 | 13.2183 | 12.8565 | 12.942 | 13.1724 | 12.6505 | 12.9479 | 12.728 | 12.5511 | NaN | NaN | NaN | 12.9215 | 122.6412 | NaN | NaN | NaN | 1.8189 | NaN | NaN | NaN | NaN | 557.8386 | NaN | 14.0186 | NaN | 23.43
4876.1292 | 13.2263 | 12.9201 | 12.9439 | 13.1666 | 12.6537 | 12.9767 | 12.7418 | 12.5494 | NaN | NaN | NaN | 12.9041 | 126.3546 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 554.9347 | NaN | 14.4523 | NaN | 24.6179
4877.1448 | 13.2119 | 12.9113 | 12.9485 | 13.1419 | 12.7469 | 12.973 | 12.7449 | 12.5387 | NaN | NaN | NaN | 12.9139 | 123.7955 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 556.1043 | NaN | 20.9627 | NaN | 23.6074
4878.1292 | 13.2002 | 12.9111 | 12.9447 | 13.1217 | 12.6941 | 12.9524 | 12.7456 | 12.5478 | NaN | NaN | NaN | 12.9082 | 128.9756 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 554.7935 | NaN | 30.5585 | NaN | 27.8158
4879.1292 | 13.2048 | 12.8464 | 12.9439 | 13.1671 | 12.7103 | 12.9292 | 12.7229 | 12.5484 | NaN | NaN | NaN | 12.8964 | 121.7475 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 556.5715 | NaN | 14.2583 | NaN | 20.8793
4880.1292 | 13.2072 | 12.9062 | 12.9531 | 13.1806 | 12.6961 | 12.9601 | 12.7376 | 12.555 | NaN | NaN | NaN | 12.9161 | 120.6853 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 555.3339 | NaN | 31.7023 | NaN | 24.8415
4881.1292 | 13.1901 | 12.8551 | 12.9525 | 13.1667 | 12.6922 | 12.9326 | 12.7213 | 12.5537 | NaN | NaN | NaN | 12.9251 | 131.47 | NaN | NaN | NaN | 26.3456 | NaN | NaN | NaN | NaN | 551.2504 | NaN | 14.0195 | NaN | 20.7613
4882.1292 | 13.2044 | 12.9402 | 12.9435 | 13.171 | 12.6987 | 12.9729 | 12.7339 | 12.5575 | NaN | NaN | NaN | 12.922 | 126.0485 | NaN | NaN | NaN | -18.1138 | NaN | NaN | NaN | NaN | 551.0566 | NaN | 36.4403 | NaN | 22.5038
4883.1292 | 13.1621 | 12.873 | 12.9405 | 13.1401 | 12.6921 | 12.9394 | 12.7309 | 12.554 | NaN | NaN | NaN | 12.9202 | 122.3533 | NaN | NaN | NaN | -8.9574 | NaN | NaN | NaN | NaN | 554.368 | NaN | 10.8364 | NaN | 22.3067
4884.1292 | 13.2027 | 12.9053 | 12.9382 | 13.1485 | 12.7237 | 12.9621 | 12.7317 | 12.5625 | NaN | NaN | NaN | 12.9007 | 140.59 | NaN | NaN | NaN | -16.4942 | NaN | NaN | NaN | NaN | 552.8655 | NaN | 12.3458 | NaN | 26.9161
4885.1292 | 13.1647 | 12.8904 | 12.9371 | 13.1294 | 12.7489 | 12.9434 | 12.7326 | 12.5588 | NaN | NaN | NaN | 12.9023 | 129.9612 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 550.2423 | NaN | 26.3028 | NaN | 26.5774
4886.1292 | 13.1713 | 12.8949 | 12.9387 | 13.1558 | 12.7116 | 12.9775 | 12.7335 | 12.5583 | NaN | NaN | NaN | 12.9068 | 132.4017 | NaN | NaN | NaN | -17.8066 | NaN | NaN | NaN | NaN | 552.8593 | NaN | 15.4156 | NaN | 16.3863
4887.1292 | 13.203 | 12.855 | 12.9373 | 13.1805 | 12.7173 | 12.9314 | 12.7218 | 12.5675 | NaN | NaN | NaN | 12.905 | 124.0794 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 552.3951 | NaN | 14.0803 | NaN | 24.353
4888.1292 | 13.1865 | 12.866 | 12.9368 | 13.207 | 12.6827 | 12.9233 | 12.7189 | 12.5706 | NaN | NaN | NaN | 12.9334 | 126.7142 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 549.9029 | NaN | 22.8597 | NaN | 23.5927
4889.1292 | 13.1987 | 12.8686 | 12.9353 | 13.1869 | 12.7284 | 12.9338 | 12.7162 | 12.5716 | NaN | NaN | NaN | 12.931 | 126.8784 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 550.0736 | NaN | 18.0195 | NaN | 28.2486
4890.1292 | 13.1974 | 12.8819 | 12.9355 | 13.174 | 12.6916 | 12.9559 | 12.7217 | 12.571 | NaN | NaN | NaN | 12.8952 | 116.4931 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 549.3845 | NaN | 25.6055 | NaN | 23.5498
4891.1292 | 13.1884 | 12.8874 | 12.9398 | 13.2057 | 12.7744 | 12.9342 | 12.7217 | 12.5715 | NaN | NaN | NaN | 12.9057 | 122.7537 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 550.5699 | NaN | 27.1362 | NaN | 24.7894
4892.1292 | 13.1851 | 12.8627 | 12.9385 | 13.1965 | 12.7397 | 12.9302 | 12.7189 | 12.5807 | NaN | NaN | NaN | 12.8941 | 118.9044 | NaN | NaN | NaN | -2.8806 | NaN | NaN | NaN | NaN | 548.1499 | NaN | 22.9106 | NaN | 25.5667
4893.1292 | 13.1654 | 12.9849 | 12.9448 | 13.1685 | 12.6918 | 12.9652 | 12.7493 | 12.5736 | NaN | NaN | NaN | 12.9211 | 124.6143 | NaN | NaN | NaN | 6.234 | NaN | NaN | NaN | NaN | 547.3353 | NaN | 10.012 | NaN | 22.0154
4894.1292 | 13.1868 | 12.8696 | 12.9437 | 13.2017 | 12.6848 | 12.9393 | 12.7196 | 12.5697 | NaN | NaN | NaN | 12.9577 | 119.0298 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 549.2033 | NaN | 17.2967 | NaN | 22.0565
4895.1292 | 13.1751 | 12.8941 | 12.9501 | 13.1874 | 12.6714 | 12.9431 | 12.7162 | 12.5708 | NaN | NaN | NaN | 12.9365 | 123.4175 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 548.7966 | NaN | 13.1866 | NaN | 14.9851
4896.1292 | 13.1856 | 12.9469 | 12.9507 | 13.2013 | 12.7743 | 12.9498 | 12.729 | 12.5709 | NaN | NaN | NaN | 12.9371 | 127.3488 | NaN | NaN | NaN | -7.1342 | NaN | NaN | NaN | NaN | 547.4763 | NaN | 23.4959 | NaN | 23.6793
4897.1292 | 13.1666 | 12.9068 | 12.9514 | 13.187 | 12.7414 | 12.9477 | 12.7237 | 12.5752 | NaN | NaN | NaN | 13.0039 | 125.5962 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 545.3589 | NaN | 18.1767 | NaN | 24.0709
4898.1292 | 13.1813 | 12.9256 | 12.9475 | 13.1397 | 12.7256 | 12.9695 | 12.741 | 12.5782 | NaN | NaN | NaN | 12.905 | 130.5388 | NaN | NaN | NaN | -13.519 | NaN | NaN | NaN | NaN | 546.4279 | NaN | 25.6828 | NaN | 26.9854
4899.1292 | 13.1697 | 12.8794 | 12.9464 | 13.1605 | 12.7708 | 12.936 | 12.7201 | 12.5848 | NaN | NaN | NaN | 12.965 | 122.339 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 545.7232 | NaN | 25.8774 | NaN | 21.4971
4900.1292 | 13.2149 | 12.9799 | 12.9489 | 13.1783 | 12.6664 | 12.991 | 12.7446 | 12.5806 | NaN | NaN | NaN | 12.9489 | 125.7211 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 545.4519 | NaN | 27.2444 | NaN | 21.9963
4901.1292 | 13.2108 | 12.8872 | 12.9453 | 13.2279 | 12.7389 | 12.9445 | 12.7348 | 12.5885 | NaN | NaN | NaN | 12.9737 | 128.4271 | NaN | NaN | NaN | -9.2795 | NaN | NaN | NaN | NaN | 541.6969 | NaN | 35.1169 | NaN | 26.8604
4902.1292 | 13.1939 | 12.9094 | 12.9479 | 13.2093 | 12.7664 | 12.9617 | 12.7458 | 12.5875 | NaN | NaN | NaN | 12.9136 | 117.6044 | NaN | NaN | NaN | -4.485 | NaN | NaN | NaN | NaN | 543.4554 | NaN | 23.2043 | NaN | 26.9135
4903.1448 | 13.1983 | 12.935 | 12.9492 | 13.2037 | 12.6884 | 12.9773 | 12.7395 | 12.5936 | NaN | NaN | NaN | 12.9273 | 120.77 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 542.9739 | NaN | 22.1522 | NaN | 27.5665
4904.1292 | 13.1795 | 12.909 | 12.9483 | 13.2045 | 12.6875 | 12.9659 | 12.7452 | 12.5953 | NaN | NaN | NaN | 12.9312 | 128.2817 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 543.1937 | NaN | 17.4638 | NaN | 15.4667
4905.1292 | 13.2117 | 12.9281 | 12.9478 | 13.2095 | 12.7849 | 12.9577 | 12.7378 | 12.5939 | NaN | NaN | NaN | 12.9221 | 128.0071 | NaN | NaN | NaN | -11.6274 | NaN | NaN | NaN | NaN | 546.6033 | NaN | 31.1756 | NaN | 24.9252
4906.1292 | 13.2047 | 12.8832 | 12.9487 | 13.2318 | 12.7769 | 12.9316 | 12.7191 | 12.5995 | NaN | NaN | NaN | 12.937 | 125.0823 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 545.7216 | NaN | 11.8609 | NaN | 24.3355
4907.1448 | 13.1845 | 12.8986 | 12.9479 | 13.2143 | 12.7098 | 12.964 | 12.745 | 12.598 | NaN | NaN | NaN | 12.9527 | 128.5512 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 544.8417 | NaN | 25.2527 | NaN | 24.8392
4908.1292 | 13.1829 | 12.9281 | 12.951 | 13.1757 | 12.7677 | 12.9721 | 12.7491 | 12.6015 | NaN | NaN | NaN | 12.9422 | 124.5381 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 547.7554 | NaN | 30.8364 | NaN | 23.4237
4909.1292 | 13.1931 | 12.9622 | 12.9514 | 13.2054 | 12.7725 | 12.9792 | 12.7519 | 12.6015 | NaN | NaN | NaN | 12.9367 | 127.0785 | NaN | NaN | NaN | -18.0892 | NaN | NaN | NaN | NaN | 544.8813 | NaN | 32.9272 | NaN | 20.2791
4910.1292 | 13.2025 | 12.8955 | 12.9474 | 13.2112 | 12.7802 | 12.9542 | 12.7429 | 12.6033 | NaN | NaN | NaN | 12.9389 | 125.781 | NaN | NaN | NaN | 1.1285 | NaN | NaN | NaN | NaN | 543.9747 | NaN | 27.2345 | NaN | 30.5728
4911.1292 | 13.1884 | 12.8991 | 12.9536 | 13.2241 | 12.7988 | 12.9437 | 12.7305 | 12.602 | NaN | NaN | NaN | 12.952 | 115.0044 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 541.7674 | NaN | 36.5335 | NaN | 25.1189
4912.1292 | 13.1609 | 12.9234 | 12.9438 | 13.2372 | 12.7071 | 12.9621 | 12.7577 | 12.592 | NaN | NaN | NaN | 12.9417 | 119.0831 | NaN | NaN | NaN | -9.4744 | NaN | NaN | NaN | NaN | 541.7329 | NaN | 24.2792 | NaN | 25.517
4913.1292 | 13.2704 | 12.9267 | 12.95 | 13.1861 | 12.7114 | 12.9654 | 12.7479 | 12.5927 | NaN | NaN | NaN | 12.923 | 120.1881 | NaN | NaN | NaN | -4.2235 | NaN | NaN | NaN | NaN | 540.53 | NaN | 22.1875 | NaN | 22.4398
4914.1292 | 13.2073 | 12.9347 | 12.948 | 13.2155 | 12.7938 | 12.9605 | 12.7525 | 12.5937 | NaN | NaN | NaN | 12.9568 | 120.8432 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 542.2553 | NaN | 17.3347 | NaN | 25.9544
4915.1292 | 13.1978 | 12.918 | 12.9507 | 13.2228 | 12.7588 | 12.9508 | 12.7528 | 12.5917 | NaN | NaN | NaN | 12.9337 | 119.8508 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 542.5967 | NaN | 19.6728 | NaN | 21.7491
4916.1292 | 13.2044 | 12.9058 | 12.9539 | 13.2072 | 12.7537 | 12.9528 | 12.7525 | 12.594 | NaN | NaN | NaN | 12.9479 | 124.1434 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 542.6857 | NaN | 9.777 | NaN | 31.8188
4917.1292 | 13.1968 | 12.9237 | 12.959 | 13.2156 | 12.6937 | 12.9565 | 12.753 | 12.5916 | NaN | NaN | NaN | 12.9294 | 127.0259 | NaN | NaN | NaN | -15.9399 | NaN | NaN | NaN | NaN | 540.6911 | NaN | 13.8789 | NaN | 28.6917
4918.1292 | 13.195 | 12.9648 | 12.9576 | 13.209 | 12.8059 | 12.9723 | 12.7779 | 12.5974 | NaN | NaN | NaN | 12.949 | 133.4028 | NaN | NaN | NaN | -12.667 | NaN | NaN | NaN | NaN | 542.0804 | NaN | 16.4534 | NaN | 23.2051
4919.1292 | 13.1833 | 12.9251 | 12.9593 | 13.2656 | 12.7339 | 12.9621 | 12.7641 | 12.5939 | NaN | NaN | NaN | 12.9446 | 117.5449 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 543.7193 | NaN | 16.3069 | NaN | 27.2562
4920.1292 | 13.1732 | 12.9096 | 12.962 | 13.1848 | 12.7008 | 12.9536 | 12.7618 | 12.5978 | NaN | NaN | NaN | 12.938 | 127.8112 | NaN | NaN | NaN | -17.4334 | NaN | NaN | NaN | NaN | 541.1705 | NaN | 15.7335 | NaN | 22.6622
4921.1292 | 13.2336 | 12.9755 | 12.9647 | 13.2116 | 12.7402 | 13.0042 | 12.7724 | 12.5972 | NaN | NaN | NaN | 12.9397 | 131.0719 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 539.4497 | NaN | 9.2439 | NaN | 25.6559
4922.1292 | 13.2252 | 12.9349 | 12.9639 | 13.2206 | 12.7249 | 12.9471 | 12.7621 | 12.6019 | NaN | NaN | NaN | 12.9706 | 120.5204 | NaN | NaN | NaN | 6.8695 | NaN | NaN | NaN | NaN | 540.6212 | NaN | 14.9787 | NaN | 20.6885
4923.1292 | 13.1499 | 12.936 | 12.9639 | 13.2484 | 12.7794 | 12.9523 | 12.7691 | 12.6044 | NaN | NaN | NaN | 12.9615 | 123.6566 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 541.1675 | NaN | 29.7213 | NaN | 25.2787
4924.1292 | 13.1852 | 12.8757 | 12.9612 | 13.1959 | 12.6945 | 12.933 | 12.7613 | 12.6094 | NaN | NaN | NaN | 12.9627 | 130.3704 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 541.7951 | NaN | 22.3491 | NaN | 23.9603
4925.1292 | 13.1698 | 12.8882 | 12.967 | 13.2473 | 12.7671 | 12.9309 | 12.7568 | 12.6014 | NaN | NaN | NaN | 12.941 | 127.3473 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 541.2551 | NaN | 12.0959 | NaN | 24.2526
4926.1292 | 13.1469 | 12.9544 | 12.9677 | 13.2419 | 12.6661 | 12.9669 | 12.7694 | 12.6013 | NaN | NaN | NaN | 12.956 | 130.8806 | NaN | NaN | NaN | 3.856 | NaN | NaN | NaN | NaN | 539.05 | NaN | 19.0902 | NaN | 24.4397
4927.1292 | 13.2164 | 12.9676 | 12.9635 | 13.2523 | 12.6894 | 12.9684 | 12.7712 | 12.6019 | NaN | NaN | NaN | 12.9316 | 116.5291 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 541.3505 | NaN | 13.0905 | NaN | 25.7902
4928.1292 | 13.2048 | 12.9062 | 12.9703 | 13.275 | 12.7861 | 12.9377 | 12.7524 | 12.5967 | NaN | NaN | NaN | 12.94 | 123.3383 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 540.0028 | NaN | 22.3848 | NaN | 21.3156
4929.1292 | 13.1575 | 12.9779 | 12.97 | 13.26 | 12.7875 | 12.9949 | 12.781 | 12.591 | NaN | NaN | NaN | 12.9719 | 124.8923 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 542.1614 | NaN | 14.9886 | NaN | 28.0754
4930.1292 | 13.1449 | 12.9167 | 12.9698 | 13.2341 | 12.7456 | 12.9599 | 12.7665 | 12.5832 | NaN | NaN | NaN | 12.9615 | 125.7585 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 543.6423 | NaN | 26.5064 | NaN | 24.2416
4931.1292 | 13.2211 | 12.9016 | 12.9761 | 13.2154 | 12.7834 | 12.9562 | 12.7633 | 12.5845 | NaN | NaN | NaN | 12.9361 | 131.6685 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 544.8333 | NaN | 10.9827 | NaN | 28.1351
4932.1292 | 13.2557 | 12.9245 | 12.9757 | 13.1975 | 12.7335 | 12.9701 | 12.7662 | 12.5771 | NaN | NaN | NaN | 12.9974 | 115.388 | NaN | NaN | NaN | -11.4935 | NaN | NaN | NaN | NaN | 544.8644 | NaN | 27.2827 | NaN | 21.5987
4933.1292 | 13.1836 | 12.9079 | 12.9696 | 13.2279 | 12.8014 | 12.9389 | 12.7555 | 12.5777 | NaN | NaN | NaN | 12.962 | 116.3685 | NaN | NaN | NaN | -11.5765 | NaN | NaN | NaN | NaN | 543.2602 | NaN | 26.3972 | NaN | 18.0988
4934.1292 | 13.2052 | 12.8997 | 12.9764 | 13.2676 | 12.7321 | 12.9639 | 12.7616 | 12.5771 | NaN | NaN | NaN | 12.9356 | 133.2845 | NaN | NaN | NaN | 2.6641 | NaN | NaN | NaN | NaN | 543.622 | NaN | 28.0809 | NaN | 20.4014
4935.1292 | 13.1828 | 12.8828 | 12.9753 | 13.2307 | 12.7827 | 12.9444 | 12.7467 | 12.5786 | NaN | NaN | NaN | 13.0163 | 129.7403 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 542.8672 | NaN | 18.6992 | NaN | 24.3222
4936.1292 | 13.2082 | 12.8817 | 12.9723 | 13.2167 | 12.7649 | 12.9447 | 12.7484 | 12.5744 | NaN | NaN | NaN | 12.9632 | 129.087 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 543.1273 | NaN | 17.7901 | NaN | 19.9053
4937.1292 | 13.1552 | 12.9059 | 12.9834 | 13.2343 | 12.6921 | 12.9532 | 12.7507 | 12.5824 | NaN | NaN | NaN | 12.991 | 131.0931 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 542.9498 | NaN | 19.3308 | NaN | 18.5637
4938.1292 | 13.1254 | 12.8986 | 12.9837 | 13.2804 | 12.7014 | 12.9523 | 12.7563 | 12.5742 | NaN | NaN | NaN | 12.9653 | 121.4821 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 542.0803 | NaN | 23.0161 | NaN | 28.1334
4939.1292 | 13.1741 | 12.8741 | 12.9718 | 13.2089 | 12.7423 | 12.944 | 12.7408 | 12.5687 | NaN | NaN | NaN | 12.9623 | 121.7497 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 543.6144 | NaN | 15.1374 | NaN | 20.5702
4940.1292 | 13.1707 | 12.9105 | 12.9775 | 13.2537 | 12.7527 | 12.9581 | 12.7522 | 12.5746 | NaN | NaN | NaN | 12.9925 | 120.2601 | NaN | NaN | NaN | 4.2746 | NaN | NaN | NaN | NaN | 541.886 | NaN | 20.3004 | NaN | 24.573
4941.1292 | 13.1585 | 12.9942 | 12.9808 | 13.2517 | 12.8145 | 12.9804 | 12.7724 | 12.577 | NaN | NaN | NaN | 12.956 | 123.4756 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 542.7788 | NaN | 9.1419 | NaN | 24.2437
4942.1292 | 13.1382 | 12.9365 | 12.9853 | 13.2372 | 12.7718 | 12.9587 | 12.7629 | 12.5772 | NaN | NaN | NaN | 12.951 | 119.1825 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 540.9564 | NaN | 25.8947 | NaN | 22.9536
4943.1292 | 13.1685 | 12.9228 | 12.9824 | 13.2466 | 12.8178 | 12.9765 | 12.7621 | 12.5724 | NaN | NaN | NaN | 12.9807 | 120.9554 | NaN | NaN | NaN | -19.9132 | NaN | NaN | NaN | NaN | 541.9257 | NaN | 27.7824 | NaN | 24.5618
4944.1292 | 13.1509 | 13.0155 | 12.9815 | 13.2784 | 12.7732 | 13.0048 | 12.7897 | 12.577 | NaN | NaN | NaN | 12.9515 | 114.6433 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 543.527 | NaN | 21.2793 | NaN | 15.1601
4945.1292 | 13.1328 | 12.9945 | 12.9837 | 13.2835 | 12.7487 | 13.0182 | 12.7904 | 12.5756 | NaN | NaN | NaN | 12.9995 | 125.5301 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 544.814 | NaN | 23.1108 | NaN | 24.3622
4946.1292 | 13.1756 | 12.9893 | 12.975 | 13.2578 | 12.6698 | 13.0118 | 12.7914 | 12.5795 | NaN | NaN | NaN | 12.9464 | 126.4886 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 543.507 | NaN | 23.2211 | NaN | 25.4123
4947.1292 | 13.1747 | 12.9319 | 12.9719 | 13.1995 | 12.7844 | 12.9809 | 12.7691 | 12.5838 | NaN | NaN | NaN | 12.9705 | 128.1815 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 544.7114 | NaN | 11.7068 | NaN | 25.9279
4948.1292 | 13.1777 | 12.8906 | 12.9685 | 13.2521 | 12.8063 | 12.9655 | 12.7637 | 12.5849 | NaN | NaN | NaN | 12.9959 | 132.9583 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 541.1732 | NaN | 27.7713 | NaN | 18.3099
4949.1292 | 13.1829 | 12.8989 | 12.972 | 13.2806 | 12.749 | 12.9605 | 12.7525 | 12.5866 | NaN | NaN | NaN | 12.9842 | 116.2912 | NaN | NaN | NaN | 6.825 | NaN | NaN | NaN | NaN | 540.7116 | NaN | 28.6478 | NaN | 29.1327
4950.1292 | 13.158 | 12.8828 | 12.9745 | 13.2474 | 12.7579 | 12.9525 | 12.7509 | 12.5917 | NaN | NaN | NaN | 12.9917 | 123.8287 | NaN | NaN | NaN | -7.5094 | NaN | NaN | NaN | NaN | 537.3097 | NaN | 22.8474 | NaN | 20.6208
4951.1292 | 13.1858 | 12.8929 | 12.9711 | 13.2446 | 12.7733 | 12.9533 | 12.7542 | 12.5861 | NaN | NaN | NaN | 12.9885 | 134.9424 | NaN | NaN | NaN | 2.7613 | NaN | NaN | NaN | NaN | 537.9176 | NaN | 12.5899 | NaN | 28.0105
4952.1292 | 13.189 | 12.8697 | 12.9753 | 13.2493 | 12.6916 | 12.9308 | 12.7383 | 12.5946 | NaN | NaN | NaN | 12.9789 | 130.5161 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 543.7087 | NaN | 32.3375 | NaN | 27.3366
4953.1292 | 13.1937 | 12.8951 | 12.9838 | 13.2177 | 12.7807 | 12.9574 | 12.744 | 12.5986 | NaN | NaN | NaN | 12.9847 | 126.2357 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 541.226 | NaN | 16.277 | NaN | 22.7462
4954.1292 | 13.1948 | 12.8931 | 12.9827 | 13.2286 | 12.7439 | 12.9533 | 12.7539 | 12.602 | NaN | NaN | NaN | 12.9656 | 117.6542 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 541.2055 | NaN | 9.0595 | NaN | 17.1064
4955.1292 | 13.1964 | 12.898 | 12.9774 | 13.2221 | 12.73 | 12.9663 | 12.7555 | 12.6029 | NaN | NaN | NaN | 12.9528 | 119.943 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 541.9705 | NaN | 25.4221 | NaN | 27.1758
4956.1292 | 13.1787 | 12.9171 | 12.986 | 13.2576 | 12.7202 | 12.9785 | 12.7578 | 12.5996 | NaN | NaN | NaN | 12.9741 | 118.4917 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 542.5959 | NaN | 24.3593 | NaN | 31.0134
4957.1292 | 13.1649 | 12.9187 | 12.9824 | 13.3193 | 12.6987 | 12.957 | 12.7542 | 12.5991 | NaN | NaN | NaN | 12.9406 | 132.4005 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 541.9293 | NaN | 14.9178 | NaN | 27.628
4958.1292 | 13.1704 | 12.8983 | 12.9803 | 13.2395 | 12.7613 | 12.9477 | 12.7503 | 12.602 | NaN | NaN | NaN | 12.9801 | 127.2882 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 539.9836 | NaN | 31.026 | NaN | 27.5675
4959.1292 | 13.1525 | 12.9281 | 12.9883 | 13.2278 | 12.808 | 12.9608 | 12.7619 | 12.6048 | NaN | NaN | NaN | 12.9781 | 133.1777 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 541.342 | NaN | 20.6917 | NaN | 15.6011
4960.1292 | 13.1931 | 12.9222 | 12.9908 | 13.2327 | 12.8054 | 12.9537 | 12.7534 | 12.6037 | NaN | NaN | NaN | 13.002 | 125.5166 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 538.5911 | NaN | 31.3943 | NaN | 16.747
4961.1292 | 13.1677 | 12.9035 | 12.9914 | 13.244 | 12.8273 | 12.9498 | 12.7511 | 12.5957 | NaN | NaN | NaN | 12.9695 | 121.6291 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 539.2175 | NaN | 14.6821 | NaN | 28.8056
4962.1292 | 13.1618 | 12.9114 | 12.9871 | 13.2745 | 12.8173 | 12.9505 | 12.7378 | 12.6055 | NaN | NaN | NaN | 12.9676 | 117.8007 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 541.0617 | NaN | 10.8512 | NaN | 35.0547
4963.1292 | 13.1573 | 12.8964 | 12.9846 | 13.2491 | 12.7687 | 12.9542 | 12.7512 | 12.6049 | NaN | NaN | NaN | 12.9522 | 133.6216 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 538.438 | NaN | 31.5087 | NaN | 25.5564
4964.1292 | 13.1644 | 12.8923 | 12.9814 | 13.2331 | 12.8068 | 12.9563 | 12.7569 | 12.6051 | NaN | NaN | NaN | 12.9547 | 127.8556 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 540.3075 | NaN | 23.3163 | NaN | 22.1243
4965.1292 | 13.18 | 12.8759 | 12.981 | 13.1842 | 12.7391 | 12.9392 | 12.7517 | 12.6106 | NaN | NaN | NaN | 12.9918 | 126.273 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 537.8166 | NaN | 31.5664 | NaN | 28.2043
4966.1292 | 13.1608 | 12.8693 | 12.9859 | 13.2077 | 12.6948 | 12.9335 | 12.7501 | 12.6095 | NaN | NaN | NaN | 12.9783 | 118.5461 | NaN | NaN | NaN | -19.625 | NaN | NaN | NaN | NaN | 539.1924 | NaN | 28.9035 | NaN | 31.3806
4967.1292 | 13.2718 | 12.9207 | 12.9867 | 13.1715 | 12.7092 | 12.968 | 12.7679 | 12.605 | NaN | NaN | NaN | 12.9819 | 131.5617 | NaN | NaN | NaN | -4.1375 | NaN | NaN | NaN | NaN | 537.5719 | NaN | 30.2572 | NaN | 23.0196
4968.1292 | 13.1364 | 12.8867 | 12.983 | 13.2029 | 12.7807 | 12.9419 | 12.7587 | 12.6121 | NaN | NaN | NaN | 13.0322 | 114.7408 | NaN | NaN | NaN | 8.443 | NaN | NaN | NaN | NaN | 538.2968 | NaN | 20.4885 | NaN | 30.7293
4969.1292 | 13.2359 | 12.9595 | 12.9914 | 13.2306 | 12.7504 | 12.9586 | 12.7652 | 12.6112 | NaN | NaN | NaN | 12.9547 | 125.9916 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 538.4106 | NaN | 20.643 | NaN | 19.9564
4970.1292 | 13.1748 | 12.8805 | 12.9895 | 13.201 | 12.7039 | 12.9607 | 12.7518 | 12.6073 | NaN | NaN | NaN | 13.0035 | 113.829 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 539.1602 | NaN | 26.4664 | NaN | 32.1358
4971.1292 | 13.1749 | 12.8875 | 12.9902 | 13.207 | 12.7688 | 12.9541 | 12.7645 | 12.6119 | NaN | NaN | NaN | 12.9819 | 128.6545 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 536.4702 | NaN | 13.7602 | NaN | 26.5455
4972.1292 | 13.1665 | 12.8932 | 12.9887 | 13.211 | 12.7864 | 12.9693 | 12.7582 | 12.6095 | NaN | NaN | NaN | 12.9592 | 133.3488 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 535.4448 | NaN | 26.4822 | NaN | 24.2916
4973.1292 | 13.1961 | 12.9407 | 12.9984 | 13.2082 | 12.7717 | 12.9842 | 12.77 | 12.6038 | NaN | NaN | NaN | 12.9757 | 127.1259 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 534.992 | NaN | 25.7109 | NaN | 23.9761
4974.1292 | 13.1786 | 12.9239 | 12.9934 | 13.24 | 12.6725 | 13.001 | 12.7653 | 12.6128 | NaN | NaN | NaN | 13.0027 | 126.5644 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 538.9958 | NaN | 15.1651 | NaN | 32.8968
4975.1292 | 13.1633 | 12.8867 | 12.9911 | 13.1847 | 12.8043 | 12.9592 | 12.7587 | 12.6216 | NaN | NaN | NaN | 13.0207 | 125.0223 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 535.5957 | NaN | 21.71 | NaN | 24.4132
4976.1292 | 13.166 | 12.8813 | 12.9976 | 13.2273 | 12.7247 | 12.9686 | 12.7597 | 12.616 | NaN | NaN | NaN | 12.9991 | 130.9253 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 535.8205 | NaN | 25.0572 | NaN | 21.9275
4977.1292 | 13.1545 | 12.9415 | 12.9932 | 13.2184 | 12.7527 | 12.9969 | 12.7706 | 12.6206 | NaN | NaN | NaN | 12.9756 | 126.8193 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 534.1738 | NaN | 20.7326 | NaN | 22.4746
4978.1292 | 13.245 | 12.9812 | 13.0062 | 13.2318 | 12.7686 | 13.0094 | 12.7826 | 12.6165 | NaN | NaN | NaN | 12.9652 | 123.4645 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 538.1823 | NaN | 21.4508 | NaN | 22.2415
4979.1292 | 13.2682 | 12.9448 | 12.9965 | 13.2672 | 12.8066 | 12.9918 | 12.7727 | 12.6182 | NaN | NaN | NaN | 12.9772 | 124.2615 | NaN | NaN | NaN | -13.801 | NaN | NaN | NaN | NaN | 539.736 | NaN | 11.0525 | NaN | 26.371
4980.1292 | 13.1557 | 12.9113 | 12.9954 | 13.1824 | 12.7196 | 12.9836 | 12.7508 | 12.6143 | NaN | NaN | NaN | 12.968 | 124.8779 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 540.8237 | NaN | 19.8937 | NaN | 26.7949
4981.1292 | 13.1535 | 12.9634 | 13.0037 | 13.2341 | 12.8233 | 12.9635 | 12.7536 | 12.6132 | NaN | NaN | NaN | 12.971 | 133.3562 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 538.8783 | NaN | 14.0868 | NaN | 25.1498
4982.1292 | 13.1426 | 12.8975 | 13.0012 | 13.2184 | 12.7802 | 12.95 | 12.7473 | 12.614 | NaN | NaN | NaN | 12.9799 | 121.4345 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 541.688 | NaN | 12.0559 | NaN | 20.899
4983.1292 | 13.1382 | 12.9481 | 12.996 | 13.1615 | 12.8016 | 12.958 | 12.7703 | 12.6122 | NaN | NaN | NaN | 12.9712 | 121.4706 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 541.5829 | NaN | 11.5377 | NaN | 30.7952
4984.1292 | 13.1252 | 12.8867 | 12.9904 | 13.2389 | 12.7804 | 12.954 | 12.746 | 12.6109 | NaN | NaN | NaN | 13.0133 | 121.2095 | NaN | NaN | NaN | -7.9146 | NaN | NaN | NaN | NaN | 539.02 | NaN | 24.1426 | NaN | 18.5455
4985.1292 | 13.169 | 12.977 | 12.9955 | 13.2075 | 12.719 | 13.0112 | 12.7621 | 12.6117 | NaN | NaN | NaN | 13.0082 | 128.3843 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 539.9527 | NaN | 21.7819 | NaN | 27.0777
4986.1292 | 13.1343 | 12.917 | 12.9885 | 13.2215 | 12.8031 | 12.9776 | 12.7616 | 12.6135 | NaN | NaN | NaN | 12.9875 | 126.9628 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 540.1842 | NaN | 14.8641 | NaN | 24.4343
4987.1292 | 13.1859 | 12.8761 | 12.9853 | 13.2617 | 12.7546 | 12.9606 | 12.75 | 12.6142 | NaN | NaN | NaN | 12.9562 | 131.6108 | NaN | NaN | NaN | -17.4235 | NaN | NaN | NaN | NaN | 540.9747 | NaN | 27.6147 | NaN | 26.4798
4988.1292 | 13.13 | 12.8851 | 12.9888 | 13.2211 | 12.7771 | 12.9624 | 12.7559 | 12.6181 | NaN | NaN | NaN | 12.9895 | 125.7633 | NaN | NaN | NaN | 5.7951 | NaN | NaN | NaN | NaN | 540.9968 | NaN | 21.6195 | NaN | 24.3781
4989.1292 | 13.1521 | 12.8795 | 12.982 | 13.2522 | 12.7835 | 12.975 | 12.7527 | 12.6168 | NaN | NaN | NaN | 12.9756 | 124.5135 | NaN | NaN | NaN | -19.7224 | NaN | NaN | NaN | NaN | 540.1014 | NaN | 30.882 | NaN | 30.3425
4990.1292 | 13.1842 | 12.9362 | 12.9936 | 13.228 | 12.7144 | 13.0233 | 12.7636 | 12.6256 | NaN | NaN | NaN | 12.9721 | 127.635 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 541.6224 | NaN | 21.8312 | NaN | 22.2093
4991.1292 | 13.1503 | 12.8897 | 12.9941 | 13.1734 | 12.7438 | 12.9746 | 12.7571 | 12.6258 | NaN | NaN | NaN | 12.9864 | 130.3327 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 542.492 | NaN | 16.2118 | NaN | 29.5854
4992.1292 | 13.1188 | 12.8806 | 12.9926 | 13.2135 | 12.698 | 12.9818 | 12.7478 | 12.626 | NaN | NaN | NaN | 12.986 | 128.3529 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 542.0499 | NaN | 20.9151 | NaN | 29.9491
4993.1292 | 13.2148 | 12.8654 | 12.9922 | 13.2417 | 12.6842 | 12.959 | 12.7434 | 12.6211 | NaN | NaN | NaN | 13.059 | 113.861 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 541.3418 | NaN | 21.3369 | NaN | 26.2116
4994.1292 | 13.2167 | 12.903 | 12.9958 | 13.2195 | 12.7872 | 12.9785 | 12.7652 | 12.6158 | NaN | NaN | NaN | 12.9783 | 127.1386 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 542.0146 | NaN | 26.4634 | NaN | 22.924
4995.1292 | 13.1469 | 12.891 | 13.0004 | 13.2196 | 12.8318 | 12.9614 | 12.7556 | 12.6121 | NaN | NaN | NaN | 12.9907 | 122.6098 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 541.0915 | NaN | 18.2457 | NaN | 29.0402
4996.1292 | 13.1379 | 12.8799 | 12.9943 | 13.2395 | 12.7366 | 12.9603 | 12.7504 | 12.6139 | NaN | NaN | NaN | 13.0256 | 123.4624 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 539.4184 | NaN | 25.6795 | NaN | 21.6686
4997.1448 | 13.1406 | 13.0056 | 13.0034 | 13.3086 | 12.8032 | 12.967 | 12.7655 | 12.6139 | NaN | NaN | NaN | 13.106 | 128.193 | NaN | NaN | NaN | -15.6914 | NaN | NaN | NaN | NaN | 541.6222 | NaN | 17.2466 | NaN | 29.2384
4998.1292 | 13.1471 | 12.9149 | 12.9985 | 13.226 | 12.7041 | 12.9635 | 12.7658 | 12.6073 | NaN | NaN | NaN | 13.0228 | 120.4568 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 542.9581 | NaN | 29.8296 | NaN | 25.3891
4999.1292 | 13.1409 | 12.8498 | 13.0061 | 13.2444 | 12.7222 | 12.9523 | 12.7546 | 12.608 | NaN | NaN | NaN | 13.0045 | 123.3174 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 543.4026 | NaN | 21.1838 | NaN | 26.0483
5000.1292 | 13.2117 | 12.8768 | 13.0039 | 13.2576 | 12.7684 | 12.9606 | 12.766 | 12.6077 | NaN | NaN | NaN | 12.9891 | 124.6384 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 544.1745 | NaN | 25.1189 | NaN | 19.8672
5001.1292 | 13.1499 | 12.8603 | 13.0034 | 13.2409 | 12.7591 | 12.9577 | 12.7504 | 12.6007 | NaN | NaN | NaN | 13.0031 | 124.5045 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 544.7579 | NaN | 28.7112 | NaN | 16.9415
5002.1292 | 13.1455 | 12.9404 | 13.0045 | 13.2821 | 12.7676 | 12.965 | 12.7723 | 12.6016 | NaN | NaN | NaN | 12.9756 | 119.0515 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 545.0186 | NaN | 17.6536 | NaN | 28.7618
5003.1292 | 13.1359 | 12.8557 | 13.0018 | 13.1821 | 12.7508 | 12.9659 | 12.7613 | 12.6061 | NaN | NaN | NaN | 12.9959 | 129.0569 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 546.1062 | NaN | 15.9456 | NaN | 28.0642
5004.1292 | 13.1254 | 12.9222 | 13.0028 | 13.2379 | 12.7959 | 12.9836 | 12.7649 | 12.6073 | NaN | NaN | NaN | 12.9804 | 116.3831 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 546.3592 | NaN | 17.8402 | NaN | 19.9803
5005.1292 | 13.1759 | 12.8825 | 13.0129 | 13.2366 | 12.6896 | 12.9994 | 12.7559 | 12.611 | NaN | NaN | NaN | 12.9965 | 119.6317 | NaN | NaN | NaN | -0.4179 | NaN | NaN | NaN | NaN | 544.477 | NaN | 23.1587 | NaN | 29.9515
5006.1292 | 13.205 | 12.8172 | 13.0058 | 13.2503 | 12.6899 | 12.9527 | 12.7519 | 12.6144 | NaN | NaN | NaN | 13.0256 | 119.1213 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 544.1378 | NaN | 18.3096 | NaN | 25.8444
5007.1292 | 13.1201 | 12.8037 | 13.0066 | 13.2374 | 12.6778 | 12.953 | 12.7634 | 12.6152 | NaN | NaN | NaN | 13.1192 | 92.5101 | NaN | NaN | NaN | -1.1101 | NaN | NaN | NaN | NaN | 562.8993 | NaN | 28.8777 | NaN | 28.6945
5008.1292 | 13.119 | 12.918 | 13 | 13.2902 | 12.6402 | 13.0049 | 12.7904 | 12.6097 | NaN | NaN | NaN | 13.0575 | 94.584 | NaN | NaN | NaN | -7.6202 | NaN | NaN | NaN | NaN | 576.5643 | NaN | 28.5371 | NaN | 28.1775
5009.1292 | 13.1191 | 12.9951 | 13.0084 | 13.2464 | 12.6152 | 13.1164 | 12.8251 | 12.6105 | NaN | NaN | NaN | 13.0783 | 92.2875 | NaN | NaN | NaN | -18.5299 | NaN | NaN | NaN | NaN | 578.919 | NaN | 29.0888 | NaN | 26.6557
5010.1292 | 13.1089 | 12.8363 | 13.0042 | 13.1749 | 12.4904 | 12.9907 | 12.7631 | 12.6135 | NaN | NaN | NaN | 13.0275 | 91.1436 | NaN | NaN | NaN | -5.3974 | NaN | NaN | NaN | NaN | 582.4359 | NaN | 28.1465 | NaN | 28.9032
5011.1292 | 13.0971 | 12.8513 | 12.991 | 13.1947 | 12.5906 | 13.062 | 12.7817 | 12.6172 | NaN | NaN | NaN | 13.0239 | 93.8969 | NaN | NaN | NaN | -14.1237 | NaN | NaN | NaN | NaN | 581.9128 | NaN | 29.0109 | NaN | 28.3584
5012.1292 | 13.3347 | 12.8808 | 12.9914 | 13.1994 | 12.603 | 13.0194 | 12.7883 | 12.6145 | NaN | NaN | NaN | 13.0448 | 92.0367 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 581.6666 | NaN | 28.5875 | NaN | 29.5736
5013.1292 | 13.1822 | 13.0215 | 12.9902 | 13.1519 | 12.5313 | 13.0662 | 12.8296 | 12.6229 | NaN | NaN | NaN | 13.0482 | 90.2717 | NaN | NaN | NaN | 0.5661 | NaN | NaN | NaN | NaN | 581.1675 | NaN | 28.0423 | NaN | 27.1625
5014.1292 | 13.2667 | 12.9331 | 12.9838 | 13.1768 | 12.5288 | 13.0393 | 12.7957 | 12.6246 | NaN | NaN | NaN | 13.1443 | 95.5535 | NaN | NaN | NaN | -15.2441 | NaN | NaN | NaN | NaN | 583.5762 | NaN | 28.2887 | NaN | 28.8052
5015.1292 | 13.1386 | 12.9271 | 12.9831 | 13.1483 | 12.7196 | 13.0507 | 12.7969 | 12.6176 | NaN | NaN | NaN | 13.0933 | 92.5612 | NaN | NaN | NaN | -11.394 | NaN | NaN | NaN | NaN | 582.2132 | NaN | 28.5823 | NaN | 27.0607
5016.1292 | 13.2466 | 13.0725 | 12.9945 | 13.2435 | 12.6767 | 13.0444 | 12.815 | 12.6207 | NaN | NaN | NaN | 12.9978 | 92.8074 | NaN | NaN | NaN | -11.8676 | NaN | NaN | NaN | NaN | 583.0003 | NaN | 27.3628 | NaN | 28.2373
5017.1292 | 13.1621 | 12.9911 | 12.9923 | 13.5695 | 12.6279 | 13.0482 | 12.8049 | 12.619 | NaN | NaN | NaN | 12.9937 | 88.3774 | NaN | NaN | NaN | 11.6537 | NaN | NaN | NaN | NaN | 583.9497 | NaN | 29.051 | NaN | 29.7023
5018.1292 | 13.0679 | 12.9412 | 12.9944 | 13.2767 | 12.6995 | 13.1047 | 12.8089 | 12.6218 | NaN | NaN | NaN | 13.0946 | 92.7158 | NaN | NaN | NaN | 5.2712 | NaN | NaN | NaN | NaN | 584.7923 | NaN | 28.8817 | NaN | 29.857
5019.1292 | 13.1728 | 12.8677 | 12.9867 | 13.2578 | 12.6574 | 13.0526 | 12.7688 | 12.626 | NaN | NaN | NaN | 12.9812 | 94.6066 | NaN | NaN | NaN | 4.5531 | NaN | NaN | NaN | NaN | 584.7391 | NaN | 27.6999 | NaN | 29.0191
5020.1292 | 13.1449 | 13.2267 | 12.9941 | 13.3502 | 12.5587 | 13.0317 | 12.8373 | 12.624 | NaN | NaN | NaN | 13.127 | 93.1938 | NaN | NaN | NaN | -10.5899 | NaN | NaN | NaN | NaN | 586.4143 | NaN | 29.6538 | NaN | 29.01
5021.1292 | 13.1264 | 12.9011 | 12.9912 | 13.244 | 12.6163 | 13.0435 | 12.795 | 12.6269 | NaN | NaN | NaN | 13.0112 | 94.1759 | NaN | NaN | NaN | 9.2157 | NaN | NaN | NaN | NaN | 587.9431 | NaN | 27.563 | NaN | 29.2633
5022.1292 | 13.3142 | 12.8904 | 12.996 | 13.2008 | 12.504 | 13.0701 | 12.7912 | 12.6205 | NaN | NaN | NaN | 13.0757 | 92.6451 | NaN | NaN | NaN | 7.0088 | NaN | NaN | NaN | NaN | 589.1973 | NaN | 28.362 | NaN | 27.9769
5023.1448 | 13.0708 | 12.9876 | 12.9987 | 13.155 | 12.6456 | 13.1415 | 12.8198 | 12.6269 | NaN | NaN | NaN | 13.0546 | 93.2511 | NaN | NaN | NaN | -13.3907 | NaN | NaN | NaN | NaN | 590.9573 | NaN | 29.5021 | NaN | 28.6199
5024.1292 | 13.2775 | 13.0178 | 13.0003 | 13.2443 | 12.4615 | 13.0085 | 12.7984 | 12.6261 | NaN | NaN | NaN | 13.0456 | 93.6707 | NaN | NaN | NaN | 1.0628 | NaN | NaN | NaN | NaN | 586.6637 | NaN | 29.5357 | NaN | 29.0695
5025.1292 | 13.2138 | 12.9536 | 13.0029 | 13.2106 | 12.5842 | 13.1249 | 12.7889 | 12.6303 | NaN | NaN | NaN | 12.9898 | 92.4557 | NaN | NaN | NaN | -2.6147 | NaN | NaN | NaN | NaN | 588.815 | NaN | 29.5401 | NaN | 28.4383
5026.1292 | 13.148 | 12.9074 | 13.0008 | 13.1592 | 12.5708 | 13.0307 | 12.7703 | 12.6282 | NaN | NaN | NaN | 13.0046 | 92.3947 | NaN | NaN | NaN | -9.5804 | NaN | NaN | NaN | NaN | 589.5373 | NaN | 27.3874 | NaN | 29.3311
5027.1448 | 13.1634 | 13.0427 | 13.0141 | 13.2225 | 12.6139 | 13.0822 | 12.805 | 12.6286 | NaN | NaN | NaN | 12.9731 | 92.8482 | NaN | NaN | NaN | -10.4292 | NaN | NaN | NaN | NaN | 589.7139 | NaN | 26.8163 | NaN | 29.1337
5028.1292 | 13.1422 | 12.9331 | 13.01 | 13.239 | 12.6166 | 13.0309 | 12.7798 | 12.627 | NaN | NaN | NaN | 13.0339 | 92.7293 | NaN | NaN | NaN | -3.5069 | NaN | NaN | NaN | NaN | 588.842 | NaN | 29.0695 | NaN | 28.7906
5029.1292 | 13.2821 | 13.0007 | 13.0135 | 13.1788 | 12.5317 | 13.0585 | 12.782 | 12.6271 | NaN | NaN | NaN | 12.9963 | 94.4957 | NaN | NaN | NaN | -15.562 | NaN | NaN | NaN | NaN | 587.4552 | NaN | 27.84 | NaN | 28.1244
5030.1292 | 13.1847 | 12.9336 | 13.012 | 13.2364 | 12.6383 | 13.0569 | 12.7676 | 12.6384 | NaN | NaN | NaN | 13.0146 | 93.7547 | NaN | NaN | NaN | -14.784 | NaN | NaN | NaN | NaN | 588.8918 | NaN | 28.7032 | NaN | 27.3655
5031.1292 | 13.1505 | 12.9976 | 13.0095 | 13.2039 | 12.7411 | 13.1835 | 12.8119 | 12.6329 | NaN | NaN | NaN | 13.1085 | 95.1222 | NaN | NaN | NaN | 42.7859 | NaN | NaN | NaN | NaN | 590.6912 | NaN | 29.9018 | NaN | 28.6098
5032.1292 | 13.1045 | 13.0204 | 13.0103 | 13.2335 | 12.4928 | 13.0589 | 12.7874 | 12.6256 | NaN | NaN | NaN | 13.0363 | 92.8032 | NaN | NaN | NaN | 6.6188 | NaN | NaN | NaN | NaN | 589.7132 | NaN | 29.1312 | NaN | 29.98
5033.1292 | 13.0846 | 12.9601 | 13.0078 | 13.1595 | 12.59 | 13.037 | 12.7758 | 12.6359 | NaN | NaN | NaN | 13.0087 | 92.5902 | NaN | NaN | NaN | -9.3244 | NaN | NaN | NaN | NaN | 587.6302 | NaN | 28.2511 | NaN | 29.8954
5034.1292 | 13.1355 | 12.9245 | 13.0129 | 13.522 | 12.676 | 13.0548 | 12.7738 | 12.6294 | NaN | NaN | NaN | 13.0454 | 92.8809 | NaN | NaN | NaN | -0.1364 | NaN | NaN | NaN | NaN | 589.2116 | NaN | 27.6021 | NaN | 28.5442
5035.1292 | 13.1895 | 12.9911 | 13.0137 | 13.1942 | 12.5097 | 13.0391 | 12.7879 | 12.6299 | NaN | NaN | NaN | 13.0864 | 92.4872 | NaN | NaN | NaN | -8.7432 | NaN | NaN | NaN | NaN | 590.8158 | NaN | 29.7234 | NaN | 28.8747
5036.1292 | 13.187 | 12.9225 | 13.0109 | 13.1926 | 12.6203 | 13.0342 | 12.7687 | 12.6254 | NaN | NaN | NaN | 13.1113 | 91.0231 | NaN | NaN | NaN | -1.1044 | NaN | NaN | NaN | NaN | 590.916 | NaN | 29.3452 | NaN | 29.1266
5037.1292 | 13.1639 | 12.9578 | 13.0167 | 13.1641 | 12.639 | 13.0569 | 12.7883 | 12.6305 | NaN | NaN | NaN | 13.0859 | 92.5679 | NaN | NaN | NaN | 33.8279 | NaN | NaN | NaN | NaN | 589.8055 | NaN | 26.566 | NaN | 28.5397
5038.1292 | 13.1476 | 13.035 | 13.0149 | 13.1662 | 12.6644 | 13.0279 | 12.8052 | 12.6233 | NaN | NaN | NaN | 13.0951 | 94.1678 | NaN | NaN | NaN | -4.0304 | NaN | NaN | NaN | NaN | 589.5416 | NaN | 28.5849 | NaN | 28.512
5039.1292 | 13.19 | 12.9065 | 13.0154 | 13.1676 | 12.5995 | 13.0117 | 12.7479 | 12.6312 | NaN | NaN | NaN | 13.0574 | 92.3329 | NaN | NaN | NaN | -3.1148 | NaN | NaN | NaN | NaN | 590.0475 | NaN | 29.1882 | NaN | 27.6408
5040.1292 | 13.1518 | 13.0922 | 13.0103 | 13.1449 | 12.5637 | 13.0842 | 12.8025 | 12.6304 | NaN | NaN | NaN | 13.0976 | 94.0738 | NaN | NaN | NaN | -17.0726 | NaN | NaN | NaN | NaN | 588.5862 | NaN | 29.1481 | NaN | 29.5229
5041.1292 | 13.2331 | 13.3471 | 13.0158 | 13.2383 | 12.5708 | 13.3099 | 12.9187 | 12.6285 | NaN | NaN | NaN | 13.1206 | 92.739 | NaN | NaN | NaN | -1.5493 | NaN | NaN | NaN | NaN | 587.1952 | NaN | 28.02 | NaN | 28.9326
5042.1292 | 13.1643 | 12.8891 | 13.0119 | 13.2153 | 12.6451 | 13.0048 | 12.7508 | 12.6238 | NaN | NaN | NaN | 13.0176 | 93.0636 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 589.0304 | NaN | 27.0037 | NaN | 29.4757
5043.1292 | 13.1117 | 13.318 | 13.0151 | 13.3039 | 12.6114 | 13.0801 | 12.9044 | 12.6197 | NaN | NaN | NaN | 13.1172 | 93.4727 | NaN | NaN | NaN | -12.9529 | NaN | NaN | NaN | NaN | 587.3243 | NaN | 28.0671 | NaN | 28.4206
5044.1292 | 13.1671 | 12.9878 | 13.0128 | 13.1215 | 12.6904 | 13.0873 | 12.8021 | 12.6223 | NaN | NaN | NaN | 13.0109 | 94.2274 | NaN | NaN | NaN | -17.011 | NaN | NaN | NaN | NaN | 588.8518 | NaN | 29.1682 | NaN | 27.8727
5045.1292 | 13.2359 | 12.9438 | 13.0112 | 13.1753 | 12.5937 | 13.0698 | 12.7914 | 12.6124 | NaN | NaN | NaN | 13.0663 | 92.6678 | NaN | NaN | NaN | 5.3736 | NaN | NaN | NaN | NaN | 588.9913 | NaN | 28.2176 | NaN | 28.1293
5046.1292 | 13.2268 | 12.9237 | 13.0207 | 13.1237 | 12.7143 | 13.022 | 12.7768 | 12.614 | NaN | NaN | NaN | 13.009 | 92.5888 | NaN | NaN | NaN | -6.1182 | NaN | NaN | NaN | NaN | 590.3824 | NaN | 26.7542 | NaN | 29.0847
5047.1292 | 13.2916 | 12.9258 | 13.0147 | 13.1327 | 12.5315 | 13.0794 | 12.7863 | 12.6108 | NaN | NaN | NaN | 13.0497 | 94.2161 | NaN | NaN | NaN | 1.4389 | NaN | NaN | NaN | NaN | 591.5651 | NaN | 29.034 | NaN | 29.2535
5048.1292 | 13.1541 | 12.9586 | 13.0112 | 13.1493 | 12.6591 | 13.0791 | 12.7946 | 12.6179 | NaN | NaN | NaN | 13.0578 | 91.799 | NaN | NaN | NaN | -17.2077 | NaN | NaN | NaN | NaN | 593.1811 | NaN | 29.1855 | NaN | 29.3179
5049.1292 | 13.3845 | 12.9791 | 13.0158 | 13.1076 | 12.6722 | 13.013 | 12.7829 | 12.6089 | NaN | NaN | NaN | 13.0432 | 92.0678 | NaN | NaN | NaN | -0.7515 | NaN | NaN | NaN | NaN | 592.863 | NaN | 28.1281 | NaN | 28.9584
5050.1292 | 13.4097 | 12.9802 | 13.0209 | 13.1306 | 12.6799 | 13.0585 | 12.7947 | 12.6109 | NaN | NaN | NaN | 13.0106 | 94.7909 | NaN | NaN | NaN | -14.0453 | NaN | NaN | NaN | NaN | 591.3034 | NaN | 27.7616 | NaN | 24.749
5051.1292 | 13.1579 | 12.9497 | 13.0143 | 13.1276 | 12.6051 | 13.0521 | 12.7864 | 12.6107 | NaN | NaN | NaN | 13.0518 | 92.0316 | NaN | NaN | NaN | 35.5249 | NaN | NaN | NaN | NaN | 592.622 | NaN | 28.0088 | NaN | 30.0255
5052.1292 | 13.1933 | 12.9238 | 13.0099 | 13.1422 | 12.5508 | 13.0095 | 12.7653 | 12.6127 | NaN | NaN | NaN | 13.1253 | 92.8524 | NaN | NaN | NaN | -0.2972 | NaN | NaN | NaN | NaN | 592.7595 | NaN | 27.7895 | NaN | 27.6813
5053.1292 | 13.1248 | 12.9438 | 13.0186 | 13.162 | 12.6228 | 12.9937 | 12.7843 | 12.6153 | NaN | NaN | NaN | 13.171 | 92.5788 | NaN | NaN | NaN | 15.4225 | NaN | NaN | NaN | NaN | 591.1383 | NaN | 30.8405 | NaN | 27.6989
5054.1292 | 13.1499 | 12.9629 | 13.0222 | 13.1782 | 12.5317 | 13.0302 | 12.8053 | 12.616 | NaN | NaN | NaN | 13.016 | 94.1065 | NaN | NaN | NaN | -2.2928 | NaN | NaN | NaN | NaN | 592.3042 | NaN | 28.8214 | NaN | 28.4305
5055.1292 | 13.1747 | 12.9906 | 13.0154 | 13.1342 | 12.5308 | 13.0289 | 12.8099 | 12.617 | NaN | NaN | NaN | 13.049 | 92.5901 | NaN | NaN | NaN | 14.4284 | NaN | NaN | NaN | NaN | 593.0292 | NaN | 28.9596 | NaN | 28.9604
5056.1292 | 13.1755 | 13.1077 | 13.0142 | 13.3838 | 12.5997 | 13.0928 | 12.839 | 12.6175 | NaN | NaN | NaN | 13.0187 | 92.9431 | NaN | NaN | NaN | -18.5434 | NaN | NaN | NaN | NaN | 589.9491 | NaN | 27.6482 | NaN | 23.7362
5057.1448 | 13.1594 | 13.0175 | 13.013 | 13.1756 | 12.6002 | 13.0291 | 12.8161 | 12.6175 | NaN | NaN | NaN | 13.0044 | 92.343 | NaN | NaN | NaN | -17.2039 | NaN | NaN | NaN | NaN | 593.7219 | NaN | 27.9696 | NaN | 28.6268
5058.1292 | 13.223 | 12.9916 | 13.0135 | 13.211 | 12.6506 | 13.0019 | 12.8157 | 12.6261 | NaN | NaN | NaN | 13.0851 | 94.4317 | NaN | NaN | NaN | -1.1781 | NaN | NaN | NaN | NaN | 593.0032 | NaN | 27.8287 | NaN | 28.0722
5059.1292 | 13.1691 | 12.9173 | 13.0146 | 13.1822 | 12.6672 | 12.9677 | 12.7807 | 12.6222 | NaN | NaN | NaN | 13.0525 | 93.4393 | NaN | NaN | NaN | -11.9125 | NaN | NaN | NaN | NaN | 593.782 | NaN | 28.5372 | NaN | 27.5538
5060.1292 | 13.192 | 12.9766 | 13.0207 | 13.1685 | 12.5311 | 13.0819 | 12.8276 | 12.6285 | NaN | NaN | NaN | 13.0576 | 95.6264 | NaN | NaN | NaN | -3.5443 | NaN | NaN | NaN | NaN | 594.2803 | NaN | 28.8495 | NaN | 27.7867
5061.1292 | 13.1187 | 12.9184 | 13.0161 | 13.2939 | 12.5899 | 13.0203 | 12.7946 | 12.6304 | NaN | NaN | NaN | 13.0845 | 94.3922 | NaN | NaN | NaN | -17.0975 | NaN | NaN | NaN | NaN | 594.5878 | NaN | 28.5434 | NaN | 29.1625
5062.1292 | 13.1487 | 12.925 | 13.0154 | 13.1155 | 12.6777 | 12.9959 | 12.7832 | 12.6254 | NaN | NaN | NaN | 13.0593 | 91.5251 | NaN | NaN | NaN | -3.6536 | NaN | NaN | NaN | NaN | 593.517 | NaN | 28.5683 | NaN | 29.0507
5063.1292 | 13.1496 | 12.9905 | 13.0236 | 13.155 | 12.5994 | 12.986 | 12.8088 | 12.6327 | NaN | NaN | NaN | 13.0227 | 92.3125 | NaN | NaN | NaN | -6.9479 | NaN | NaN | NaN | NaN | 581.8671 | NaN | 27.7949 | NaN | 28.4914
5064.1292 | 13.1469 | 12.9499 | 13.0233 | 13.1225 | 12.6659 | 13.0291 | 12.8028 | 12.6314 | NaN | NaN | NaN | 13.1185 | 92.606 | NaN | NaN | NaN | 4.8554 | NaN | NaN | NaN | NaN | 580.271 | NaN | 28.8512 | NaN | 29.7471
5065.1292 | 13.1805 | 12.9559 | 13.0176 | 13.1492 | 12.5299 | 13.0692 | 12.8185 | 12.6328 | NaN | NaN | NaN | 13.04 | 92.1436 | NaN | NaN | NaN | 2.1283 | NaN | NaN | NaN | NaN | 578.2799 | NaN | 28.9291 | NaN | 29.8552
5066.1292 | 13.176 | 12.9504 | 13.0231 | 13.1628 | 12.6088 | 13.042 | 12.8073 | 12.6369 | NaN | NaN | NaN | 13.0603 | 89.3162 | NaN | NaN | NaN | 17.7129 | NaN | NaN | NaN | NaN | 579.3117 | NaN | 27.7759 | NaN | 28.2304
5067.1292 | 13.1588 | 12.9403 | 13.0254 | 13.1902 | 12.5732 | 13.0668 | 12.8185 | 12.6364 | NaN | NaN | NaN | 13.0423 | 93.3342 | NaN | NaN | NaN | 17.14 | NaN | NaN | NaN | NaN | 575.1745 | NaN | 27.6201 | NaN | 27.2315
5068.1292 | 13.1605 | 12.9902 | 13.0205 | 13.2287 | 12.4767 | 13.3756 | 12.8183 | 12.6424 | NaN | NaN | NaN | 13.0963 | 94.3946 | NaN | NaN | NaN | -1.1974 | NaN | NaN | NaN | NaN | 577.718 | NaN | 26.1029 | NaN | 28.2625
5069.1292 | 13.197 | 13.2447 | 13.0212 | 13.2795 | 12.5898 | 13.018 | 12.9066 | 12.6338 | NaN | NaN | NaN | 13.1383 | 95.1682 | NaN | NaN | NaN | -6.1539 | NaN | NaN | NaN | NaN | 574.8694 | NaN | 28.4523 | NaN | 26.9117
5070.1292 | 13.0776 | 12.9541 | 13.0174 | 13.1624 | 12.6626 | 13.2408 | 12.8215 | 12.6346 | NaN | NaN | NaN | 13.0005 | 93.861 | NaN | NaN | NaN | -3.6716 | NaN | NaN | NaN | NaN | 576.2902 | NaN | 27.8922 | NaN | 29.3233
5071.1292 | 13.1903 | 13.084 | 13.0193 | 13.1247 | 12.7103 | 13.0363 | 12.841 | 12.6381 | NaN | NaN | NaN | 13.1145 | 89.8679 | NaN | NaN | NaN | 25.5477 | NaN | NaN | NaN | NaN | 576.4583 | NaN | 29.7487 | NaN | 27.2898
5072.1292 | 13.168 | 13.1422 | 13.0187 | 13.1799 | 12.6052 | 13.0861 | 12.8514 | 12.6408 | NaN | NaN | NaN | 13.0251 | 91.4434 | NaN | NaN | NaN | -13.0916 | NaN | NaN | NaN | NaN | 577.242 | NaN | 27.9278 | NaN | 29.1154
5073.1292 | 13.1838 | 13.0672 | 13.0197 | 13.1533 | 12.553 | 13.0866 | 12.8383 | 12.6409 | NaN | NaN | NaN | 13.1325 | 93.7561 | NaN | NaN | NaN | -2.2865 | NaN | NaN | NaN | NaN | 576.3338 | NaN | 29.3642 | NaN | 28.7036
5074.1292 | 13.1565 | 12.9407 | 13.0191 | 13.1968 | 12.6758 | 13.0614 | 12.8241 | 12.6437 | NaN | NaN | NaN | 13.0799 | 93.933 | NaN | NaN | NaN | -15.9256 | NaN | NaN | NaN | NaN | 576.891 | NaN | 27.719 | NaN | 28.7635
5075.1292 | 13.1707 | 12.9541 | 13.0206 | 13.2138 | 12.6591 | 13.0489 | 12.8166 | 12.6409 | NaN | NaN | NaN | 13.0271 | 93.3512 | NaN | NaN | NaN | 40.538 | NaN | NaN | NaN | NaN | 577.1704 | NaN | 28.9613 | NaN | 26.0268
5076.1292 | 13.1547 | 13.0982 | 13.029 | 13.1721 | 12.6652 | 13.2522 | 12.8448 | 12.6395 | NaN | NaN | NaN | 13.0302 | 93.6123 | NaN | NaN | NaN | -10.4957 | NaN | NaN | NaN | NaN | 575.4851 | NaN | 28.6287 | NaN | 27.671
5077.1292 | 13.1635 | 12.9405 | 13.0261 | 13.3039 | 12.6904 | 13.0746 | 12.8027 | 12.6368 | NaN | NaN | NaN | 13.0559 | 92.1085 | NaN | NaN | NaN | 4.0671 | NaN | NaN | NaN | NaN | 576.7498 | NaN | 29.7236 | NaN | 27.9581
5078.1292 | 13.1178 | 13.0036 | 13.0272 | 13.1283 | 12.5576 | 13.1332 | 12.8305 | 12.636 | NaN | NaN | NaN | 13.061 | 93.2454 | NaN | NaN | NaN | 7.4995 | NaN | NaN | NaN | NaN | 577.9996 | NaN | 29.0807 | NaN | 21.134
5079.1292 | 13.1896 | 13.0289 | 13.0303 | 13.1629 | 12.6824 | 13.0834 | 12.8551 | 12.6424 | NaN | NaN | NaN | 13.0176 | 91.7187 | NaN | NaN | NaN | -8.6132 | NaN | NaN | NaN | NaN | 578.8594 | NaN | 27.8905 | NaN | 28.6548
5080.1292 | 13.1946 | 12.9604 | 13.0317 | 13.1586 | 12.6237 | 13.1756 | 12.8291 | 12.6419 | NaN | NaN | NaN | 13.1235 | 93.5999 | NaN | NaN | NaN | -18.1453 | NaN | NaN | NaN | NaN | 578.8508 | NaN | 28.4558 | NaN | 25.9811
5081.1292 | 13.1703 | 13.1643 | 13.0295 | 13.2301 | 12.586 | 13.0864 | 12.8756 | 12.6467 | NaN | NaN | NaN | 13.0896 | 94.4008 | NaN | NaN | NaN | 4.394 | NaN | NaN | NaN | NaN | 578.4571 | NaN | 26.6381 | NaN | 29.2626
5082.1292 | 13.1817 | 13.1881 | 13.0304 | 13.2188 | 12.6823 | 13.2238 | 12.8588 | 12.6431 | NaN | NaN | NaN | 13.0927 | 92.0936 | NaN | NaN | NaN | -9.6986 | NaN | NaN | NaN | NaN | 578.0208 | NaN | 27.3764 | NaN | 29.1578
5083.1292 | 13.1445 | 12.9368 | 13.0264 | 13.1383 | 12.5738 | 13.1058 | 12.8257 | 12.647 | NaN | NaN | NaN | 13.134 | 93.9238 | NaN | NaN | NaN | -12.1856 | NaN | NaN | NaN | NaN | 581.6928 | NaN | 28.3237 | NaN | 28.0117
5084.1292 | 13.4748 | 13.0608 | 13.0322 | 13.1025 | 12.6306 | 13.1134 | 12.8341 | 12.6515 | NaN | NaN | NaN | 13.2297 | 95.071 | NaN | NaN | NaN | 4.0627 | NaN | NaN | NaN | NaN | 580.4189 | NaN | 26.5107 | NaN | 29.0781
5085.1292 | 13.2535 | 13.3181 | 13.0362 | 13.1095 | 12.5917 | 13.1229 | 12.9169 | 12.6491 | NaN | NaN | NaN | 13.0429 | 92.8901 | NaN | NaN | NaN | 11.9767 | NaN | NaN | NaN | NaN | 581.1706 | NaN | 29.612 | NaN | 28.4787
5086.1292 | 13.1929 | 12.9785 | 13.034 | 13.1974 | 12.5343 | 13.1796 | 12.8245 | 12.6488 | NaN | NaN | NaN | 13.1769 | 93.2248 | NaN | NaN | NaN | 2.4465 | NaN | NaN | NaN | NaN | 580.2419 | NaN | 30.0501 | NaN | 27.1318
5087.1292 | 13.229 | 13.0647 | 13.0362 | 13.1388 | 12.6438 | 13.1447 | 12.842 | 12.6503 | NaN | NaN | NaN | 13.1057 | 91.9126 | NaN | NaN | NaN | 11.5581 | NaN | NaN | NaN | NaN | 581.0779 | NaN | 27.8689 | NaN | 27.5356
5088.1292 | 13.1533 | 13.159 | 13.0321 | 13.2324 | 12.7057 | 13.0811 | 12.8367 | 12.6498 | NaN | NaN | NaN | 13.133 | 92.0444 | NaN | NaN | NaN | 4.848 | NaN | NaN | NaN | NaN | 580.4202 | NaN | 28.3812 | NaN | 28.295
5089.1292 | 13.2918 | 12.987 | 13.0275 | 13.1327 | 12.6999 | 13.1323 | 12.8192 | 12.6454 | NaN | NaN | NaN | 13.0168 | 92.7967 | NaN | NaN | NaN | -5.3466 | NaN | NaN | NaN | NaN | 583.8318 | NaN | 29.3832 | NaN | 29.6722
5090.1292 | 13.3355 | 12.9403 | 13.0295 | 13.1826 | 12.6704 | 13.0468 | 12.7992 | 12.6512 | NaN | NaN | NaN | 13.0982 | 92.8881 | NaN | NaN | NaN | -16.9154 | NaN | NaN | NaN | NaN | 580.2267 | NaN | 28.6317 | NaN | 28.7328
5091.1292 | 13.1512 | 13.1092 | 13.0312 | 13.14 | 12.5896 | 13.1521 | 12.8229 | 12.6462 | NaN | NaN | NaN | 13.0715 | 94.0882 | NaN | NaN | NaN | -11.6141 | NaN | NaN | NaN | NaN | 580.9417 | NaN | 29.0195 | NaN | 29.1292
5092.1292 | 13.1975 | 13.1965 | 13.0369 | 13.1841 | 12.6745 | 13.1007 | 12.8243 | 12.6386 | NaN | NaN | NaN | 13.0362 | 90.8196 | NaN | NaN | NaN | 6.5799 | NaN | NaN | NaN | NaN | 583.7907 | NaN | 27.743 | NaN | 28.116
5093.1292 | 13.184 | 13.0612 | 13.0445 | 13.185 | 12.6448 | 13.1818 | 12.8254 | 12.65 | NaN | NaN | NaN | 13.0538 | 92.8711 | NaN | NaN | NaN | 16.8185 | NaN | NaN | NaN | NaN | 584.879 | NaN | 29.0166 | NaN | 29.8792
5094.1292 | 13.2908 | 12.967 | 13.037 | 13.3091 | 12.6787 | 13.3184 | 12.8139 | 12.6421 | NaN | NaN | NaN | 13.0647 | 92.2093 | NaN | NaN | NaN | -10.0606 | NaN | NaN | NaN | NaN | 584.1672 | NaN | 28.3253 | NaN | 28.0351
5095.1292 | 13.1375 | 12.9703 | 13.0411 | 13.4205 | 12.5393 | 13.1388 | 12.8079 | 12.647 | NaN | NaN | NaN | 13.0571 | 92.0949 | NaN | NaN | NaN | 8.8743 | NaN | NaN | NaN | NaN | 583.8999 | NaN | 27.4456 | NaN | 28.276
5096.1292 | 13.1694 | 12.9419 | 13.0377 | 13.1708 | 12.5968 | 13.0762 | 12.8058 | 12.6503 | NaN | NaN | NaN | 13.0802 | 92.9267 | NaN | NaN | NaN | -6.7102 | NaN | NaN | NaN | NaN | 584.0437 | NaN | 28.3867 | NaN | 29.7027
5097.1292 | 13.2489 | 12.9856 | 13.0462 | 13.3164 | 12.5589 | 13.1699 | 12.8221 | 12.6466 | NaN | NaN | NaN | 13.0517 | 94.2173 | NaN | NaN | NaN | -8.6002 | NaN | NaN | NaN | NaN | 584.6622 | NaN | 29.2658 | NaN | 27.5763
5098.1292 | 13.2068 | 13.0895 | 13.046 | 13.2418 | 12.7815 | 13.2156 | 12.8287 | 12.6546 | NaN | NaN | NaN | 13.1054 | 93.5481 | NaN | NaN | NaN | 13.3152 | NaN | NaN | NaN | NaN | 583.4982 | NaN | 27.596 | NaN | 28.8454
5099.1292 | 13.2094 | 13.0286 | 13.0493 | 13.2306 | 12.607 | 13.1024 | 12.8317 | 12.6596 | NaN | NaN | NaN | 13.0539 | 93.788 | NaN | NaN | NaN | 11.0717 | NaN | NaN | NaN | NaN | 585.9593 | NaN | 27.4618 | NaN | 29.8038
5100.1292 | 13.2004 | 12.9862 | 13.0573 | 13.2056 | 12.6631 | 13.1266 | 12.827 | 12.6539 | NaN | NaN | NaN | 13.1312 | 91.3268 | NaN | NaN | NaN | 9.9523 | NaN | NaN | NaN | NaN | 586.712 | NaN | 28.6349 | NaN | 27.7307
5101.1292 | 13.2129 | 12.9737 | 13.0488 | 13.2274 | 12.6339 | 13.2364 | 12.8173 | 12.6591 | NaN | NaN | NaN | 13.0903 | 94.6225 | NaN | NaN | NaN | -18.2013 | NaN | NaN | NaN | NaN | 588.2866 | NaN | 28.476 | NaN | 28.5735
5102.1292 | 13.2688 | 13.0212 | 13.0438 | 13.1571 | 12.5363 | 13.1034 | 12.8274 | 12.6624 | NaN | NaN | NaN | 13.1147 | 93.433 | NaN | NaN | NaN | -5.3618 | NaN | NaN | NaN | NaN | 587.7813 | NaN | 28.5679 | NaN | 29.1755
5103.1292 | 13.2185 | 13.0146 | 13.0518 | 13.1746 | 12.6862 | 13.1464 | 12.8317 | 12.6623 | NaN | NaN | NaN | 13.0859 | 92.3571 | NaN | NaN | NaN | 19.6296 | NaN | NaN | NaN | NaN | 587.0459 | NaN | 29.8736 | NaN | 28.0982
5104.1292 | 13.2564 | 12.995 | 13.0529 | 13.2346 | 12.7163 | 13.1139 | 12.815 | 12.6691 | NaN | NaN | NaN | 13.1066 | 92.9414 | NaN | NaN | NaN | 11.9007 | NaN | NaN | NaN | NaN | 587.6231 | NaN | 27.0513 | NaN | 22.447
5105.1292 | 13.191 | 13.0229 | 13.05 | 13.2546 | 12.6862 | 13.1305 | 12.8262 | 12.6724 | NaN | NaN | NaN | 13.2819 | 94.0734 | NaN | NaN | NaN | -0.862 | NaN | NaN | NaN | NaN | 586.6682 | NaN | 27.4684 | NaN | 25.8232
5106.1292 | 13.2203 | 13.0047 | 13.0525 | 13.2548 | 12.5856 | 13.1636 | 12.8242 | 12.6716 | NaN | NaN | NaN | 13.0492 | 93.577 | NaN | NaN | NaN | -4.2424 | NaN | NaN | NaN | NaN | 587.2718 | NaN | 27.5074 | NaN | 29.1006
5107.1292 | 13.2174 | 12.9944 | 13.0625 | 13.1694 | 12.646 | 13.3096 | 12.8287 | 12.6747 | NaN | NaN | NaN | 13.0518 | 92.7359 | NaN | NaN | NaN | -7.7525 | NaN | NaN | NaN | NaN | 589.3643 | NaN | 26.8543 | NaN | 29.238
5108.1292 | 13.2774 | 13.0439 | 13.0562 | 13.2063 | 12.6292 | 13.4853 | 12.8362 | 12.677 | NaN | NaN | NaN | 13.0629 | 93.3059 | NaN | NaN | NaN | 33.6708 | NaN | NaN | NaN | NaN | 584.785 | NaN | 26.9547 | NaN | 27.4067
5109.1292 | 13.3026 | 12.9403 | 13.0535 | 13.3125 | 12.668 | 13.0773 | 12.8028 | 12.6807 | NaN | NaN | NaN | 13.0485 | 91.6958 | NaN | NaN | NaN | 10.157 | NaN | NaN | NaN | NaN | 587.7819 | NaN | 26.7907 | NaN | 28.8255
5110.1292 | 13.237 | 12.9938 | 13.0598 | 13.2451 | 12.5406 | 13.0981 | 12.8297 | 12.6781 | NaN | NaN | NaN | 13.0619 | 94.6716 | NaN | NaN | NaN | 12.0411 | NaN | NaN | NaN | NaN | 588.9611 | NaN | 27.8754 | NaN | 18.8977
5111.1292 | 13.3256 | 12.9631 | 13.0599 | 13.1887 | 12.6691 | 13.0507 | 12.8127 | 12.6837 | NaN | NaN | NaN | 13.1064 | 93.6669 | NaN | NaN | NaN | 18.164 | NaN | NaN | NaN | NaN | 588.5724 | NaN | 28.1575 | NaN | 28.7751
5112.1292 | 13.3507 | 12.9847 | 13.0573 | 13.2481 | 12.6212 | 13.1157 | 12.8092 | 12.685 | NaN | NaN | NaN | 13.0717 | 92.9861 | NaN | NaN | NaN | 4.8117 | NaN | NaN | NaN | NaN | 588.6866 | NaN | 26.7397 | NaN | 28.9505
5113.1292 | 13.2531 | 13.0661 | 13.0575 | 13.2495 | 12.6275 | 13.0941 | 12.8484 | 12.6804 | NaN | NaN | NaN | 13.1369 | 92.2925 | NaN | NaN | NaN | 10.6302 | NaN | NaN | NaN | NaN | 591.3032 | NaN | 27.4767 | NaN | 29.5421
5114.1292 | 13.2552 | 13.0367 | 13.0569 | 13.2456 | 12.7005 | 13.3574 | 12.836 | 12.6863 | NaN | NaN | NaN | 13.1173 | 92.451 | NaN | NaN | NaN | -17.702 | NaN | NaN | NaN | NaN | 591.6981 | NaN | 27.3406 | NaN | 27.9563
5115.1292 | 13.2149 | 12.9755 | 13.0629 | 13.3088 | 12.7084 | 13.0981 | 12.8207 | 12.6882 | NaN | NaN | NaN | 13.1908 | 93.6837 | NaN | NaN | NaN | -5.208 | NaN | NaN | NaN | NaN | 591.1667 | NaN | 29.0776 | NaN | 29.9636
5116.1292 | 13.6235 | 12.9808 | 13.0637 | 13.2367 | 12.6083 | 13.1276 | 12.8223 | 12.6907 | NaN | NaN | NaN | 13.1651 | 94.2156 | NaN | NaN | NaN | 9.4362 | NaN | NaN | NaN | NaN | 593.3937 | NaN | 27.9062 | NaN | 27.7371
5117.1292 | 13.1892 | 13.0419 | 13.0671 | 13.2109 | 12.7379 | 13.1405 | 12.8528 | 12.6886 | NaN | NaN | NaN | 13.1007 | 94.8012 | NaN | NaN | NaN | 10.9987 | NaN | NaN | NaN | NaN | 597.4956 | NaN | 28.5537 | NaN | 25.8821
5118.1292 | 13.2402 | 12.9869 | 13.068 | 13.4237 | 12.7724 | 13.1065 | 12.8322 | 12.6868 | NaN | NaN | NaN | 13.2046 | 93.9729 | NaN | NaN | NaN | -15.0617 | NaN | NaN | NaN | NaN | 601.7328 | NaN | 27.5839 | NaN | 29.1949
5119.1292 | 13.2627 | 12.9567 | 13.0692 | 13.2309 | 12.5865 | 13.075 | 12.8296 | 12.6914 | NaN | NaN | NaN | 13.131 | 92.3767 | NaN | NaN | NaN | 2.5669 | NaN | NaN | NaN | NaN | 601.6011 | NaN | 27.3148 | NaN | 28.2586
5120.1292 | 13.4791 | 13.0505 | 13.076 | 13.4074 | 12.8002 | 13.3097 | 12.8531 | 12.6913 | NaN | NaN | NaN | 13.0932 | 93.927 | NaN | NaN | NaN | 26.0957 | NaN | NaN | NaN | NaN | 597.6988 | NaN | 27.2187 | NaN | 21.2138
5121.1292 | 13.5253 | 13.0743 | 13.0759 | 13.2674 | 12.6126 | 13.1484 | 12.8636 | 12.6979 | NaN | NaN | NaN | 13.1487 | 94.6812 | NaN | NaN | NaN | -3.2714 | NaN | NaN | NaN | NaN | 595.5096 | NaN | 27.9868 | NaN | 29.2536
5122.1292 | 13.2201 | 13.0248 | 13.0772 | 13.2112 | 12.7403 | 13.1136 | 12.8495 | 12.6972 | NaN | NaN | NaN | 13.0393 | 97.0263 | NaN | NaN | NaN | 11.3108 | NaN | NaN | NaN | NaN | 598.8718 | NaN | 26.7497 | NaN | 28.412
5123.1292 | 13.3097 | 13.0047 | 13.0724 | 13.2477 | 12.7465 | 13.1892 | 12.8438 | 12.6951 | NaN | NaN | NaN | 13.154 | 92.3326 | NaN | NaN | NaN | -2.5144 | NaN | NaN | NaN | NaN | 596.4335 | NaN | 28.164 | NaN | 26.0483
5124.1292 | 13.2595 | 12.963 | 13.0825 | 13.2163 | 12.784 | 13.0409 | 12.8074 | 12.6963 | NaN | NaN | NaN | 13.1433 | 97.0787 | NaN | NaN | NaN | -12.8529 | NaN | NaN | NaN | NaN | 598.182 | NaN | 29.0797 | NaN | 27.9877
5125.1292 | 13.2298 | 13.318 | 13.0807 | 13.2267 | 12.714 | 13.1503 | 12.8922 | 12.7001 | NaN | NaN | NaN | 13.1575 | 93.089 | NaN | NaN | NaN | -8.5313 | NaN | NaN | NaN | NaN | 596.849 | NaN | 27.5108 | NaN | 30.2266
5126.1292 | 13.2719 | 13.0379 | 13.087 | 13.2163 | 12.6153 | 13.1365 | 12.8324 | 12.7071 | NaN | NaN | NaN | 13.1252 | 91.8468 | NaN | NaN | NaN | 13.9465 | NaN | NaN | NaN | NaN | 598.5031 | NaN | 29.3433 | NaN | 28.092
5127.1292 | 13.3267 | 13.0071 | 13.082 | 13.2282 | 12.5833 | 13.0912 | 12.8269 | 12.703 | NaN | NaN | NaN | 13.1459 | 93.1291 | NaN | NaN | NaN | 1.1165 | NaN | NaN | NaN | NaN | 597.4039 | NaN | 27.3642 | NaN | 28.746
5128.1292 | 13.2627 | 13.1255 | 13.0907 | 13.2297 | 12.7082 | 13.1624 | 12.8554 | 12.7014 | NaN | NaN | NaN | 13.0893 | 93.7052 | NaN | NaN | NaN | -2.3074 | NaN | NaN | NaN | NaN | 596.7647 | NaN | 27.9528 | NaN | 28.0629
5129.1292 | 13.3094 | 13.0099 | 13.0897 | 13.5263 | 12.7841 | 13.2356 | 12.8354 | 12.6972 | NaN | NaN | NaN | 13.1477 | 92.553 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 598.6358 | NaN | 27.5411 | NaN | 28.7532
5130.1292 | 13.3918 | 12.9842 | 13.0865 | 13.2026 | 12.6845 | 13.1966 | 12.8321 | 12.706 | NaN | NaN | NaN | 13.158 | 94.0886 | NaN | NaN | NaN | -5.3327 | NaN | NaN | NaN | NaN | 597.7966 | NaN | 27.0501 | NaN | 30.0731
5131.1292 | 13.2849 | 13.066 | 13.0953 | 13.209 | 12.6343 | 13.1288 | 12.8459 | 12.7039 | NaN | NaN | NaN | 13.179 | 93.6083 | NaN | NaN | NaN | -0.3372 | NaN | NaN | NaN | NaN | 595.263 | NaN | 26.9317 | NaN | 23.1503
5132.1292 | 13.2132 | 13.0145 | 13.0963 | 13.1883 | 12.6592 | 13.1274 | 12.8338 | 12.7034 | NaN | NaN | NaN | 13.1089 | 92.6838 | NaN | NaN | NaN | 11.3058 | NaN | NaN | NaN | NaN | 595.7079 | NaN | 26.1633 | NaN | 28.0865
5133.1292 | 13.2774 | 12.9988 | 13.0973 | 13.2878 | 12.6786 | 13.0953 | 12.8224 | 12.7068 | NaN | NaN | NaN | 13.1331 | 93.5594 | NaN | NaN | NaN | 48.8734 | NaN | NaN | NaN | NaN | 595.8727 | NaN | 28.6339 | NaN | 29.4722
5134.1292 | 13.2931 | 13.0224 | 13.0963 | 13.2744 | 12.5895 | 13.2324 | 12.8424 | 12.6954 | NaN | NaN | NaN | 13.2194 | 91.8047 | NaN | NaN | NaN | -6.4597 | NaN | NaN | NaN | NaN | 597.7805 | NaN | 27.6143 | NaN | 25.4878
5135.1292 | 13.4299 | 13.0078 | 13.1002 | 13.2548 | 12.6386 | 13.1772 | 12.8285 | 12.7072 | NaN | NaN | NaN | 13.1062 | 92.8819 | NaN | NaN | NaN | -10.3798 | NaN | NaN | NaN | NaN | 598.0219 | NaN | 27.1687 | NaN | 26.6705
5136.1292 | 13.4761 | 13.0697 | 13.1016 | 13.2869 | 12.6478 | 13.5288 | 12.8482 | 12.7033 | NaN | NaN | NaN | 13.2056 | 95.0287 | NaN | NaN | NaN | -15.0163 | NaN | NaN | NaN | NaN | 596.7133 | NaN | 26.8462 | NaN | 28.6918
5137.1292 | 13.7396 | 13.0206 | 13.1028 | 13.2621 | 12.6598 | 13.279 | 12.8329 | 12.6983 | NaN | NaN | NaN | 13.1045 | 94.2165 | NaN | NaN | NaN | -15.2723 | NaN | NaN | NaN | NaN | 599.6684 | NaN | 25.6217 | NaN | 29.1114
5138.1292 | 13.2205 | 13.0691 | 13.1007 | 13.2164 | 12.6639 | 13.1429 | 12.8428 | 12.7096 | NaN | NaN | NaN | 13.1246 | 93.7344 | NaN | NaN | NaN | -16.4648 | NaN | NaN | NaN | NaN | 599.7131 | NaN | 27.3257 | NaN | 30.0627
5139.1292 | 13.2633 | 13.0933 | 13.1013 | 13.2919 | 12.7649 | 13.1103 | 12.8477 | 12.7045 | NaN | NaN | NaN | 13.092 | 94.1374 | NaN | NaN | NaN | -19.0816 | NaN | NaN | NaN | NaN | 599.8669 | NaN | 27.7769 | NaN | 28.0407
5140.1292 | 13.2503 | 13.07 | 13.1019 | 13.4357 | 12.7207 | 13.1157 | 12.8533 | 12.7053 | NaN | NaN | NaN | 13.0788 | 94.552 | NaN | NaN | NaN | -10.7114 | NaN | NaN | NaN | NaN | 601.7405 | NaN | 28.2673 | NaN | 29.1728
5141.1292 | 13.5073 | 13.1137 | 13.107 | 13.2432 | 12.6039 | 13.1942 | 12.8472 | 12.6944 | NaN | NaN | NaN | 13.2072 | 92.9598 | NaN | NaN | NaN | -11.9495 | NaN | NaN | NaN | NaN | 600.731 | NaN | 28.5312 | NaN | 28.6331
5142.1292 | 13.2462 | 13.0557 | 13.1047 | 13.2669 | 12.6586 | 13.201 | 12.8315 | 12.6993 | NaN | NaN | NaN | 13.1057 | 93.8737 | NaN | NaN | NaN | -13.0496 | NaN | NaN | NaN | NaN | 601.2783 | NaN | 26.6524 | NaN | 28.9363
5143.1292 | 13.2878 | 12.984 | 13.106 | 13.2544 | 12.7193 | 13.1508 | 12.8133 | 12.6998 | NaN | NaN | NaN | 13.1449 | 93.4334 | NaN | NaN | NaN | -10.5994 | NaN | NaN | NaN | NaN | 601.7908 | NaN | 27.9741 | NaN | 28.8484
5144.1292 | 13.3363 | 13.1498 | 13.1097 | 13.2301 | 12.6125 | 13.1633 | 12.8489 | 12.6933 | NaN | NaN | NaN | 13.1598 | 93.0093 | NaN | NaN | NaN | -3.3277 | NaN | NaN | NaN | NaN | 594.1292 | NaN | 27.1872 | NaN | 29.268
5145.1292 | 13.2643 | 13.0714 | 13.1155 | 13.3201 | 12.7684 | 13.3186 | 12.8475 | 12.694 | NaN | NaN | NaN | 13.1226 | 92.5201 | NaN | NaN | NaN | -12.6459 | NaN | NaN | NaN | NaN | 599.5606 | NaN | 27.7973 | NaN | 27.67
5146.1292 | 13.2949 | 13.0101 | 13.1162 | 13.2988 | 12.6128 | 13.1209 | 12.8218 | 12.6957 | NaN | NaN | NaN | 13.0525 | 92.3809 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 602.8107 | NaN | 26.8686 | NaN | 29.4304
5147.1292 | 13.2279 | 13.0044 | 13.1138 | 13.4102 | 12.7312 | 13.099 | 12.8158 | 12.6867 | NaN | NaN | NaN | 13.1418 | 92.5724 | NaN | NaN | NaN | 4.5517 | NaN | NaN | NaN | NaN | 602.5076 | NaN | 28.8713 | NaN | 28.4889
5148.1292 | 13.2086 | 13.0247 | 13.1167 | 13.2811 | 12.7429 | 13.0499 | 12.8059 | 12.6867 | NaN | NaN | NaN | 13.1599 | 92.0934 | NaN | NaN | NaN | -13.0894 | NaN | NaN | NaN | NaN | 601.8098 | NaN | 27.7585 | NaN | 26.2996
5149.1292 | 13.4417 | 13.0136 | 13.1194 | 13.205 | 12.6115 | 13.2233 | 12.8164 | 12.6927 | NaN | NaN | NaN | 13.1123 | 92.8168 | NaN | NaN | NaN | 41.3163 | NaN | NaN | NaN | NaN | 601.037 | NaN | 27.5422 | NaN | 26.8091
5150.1292 | 13.2644 | 13.0548 | 13.1215 | 13.241 | 12.7128 | 13.1307 | 12.8383 | 12.6827 | NaN | NaN | NaN | 13.1466 | 93.6217 | NaN | NaN | NaN | 31.4312 | NaN | NaN | NaN | NaN | 602.0367 | NaN | 26.8058 | NaN | 28.9679
5151.1292 | 13.3306 | 13.1123 | 13.1225 | 13.2969 | 12.7031 | 13.2157 | 12.8692 | 12.6827 | NaN | NaN | NaN | 13.0589 | 94.3725 | NaN | NaN | NaN | 3.5349 | NaN | NaN | NaN | NaN | 602.5786 | NaN | 26.6261 | NaN | 29.0678
5152.1292 | 13.3399 | 13.3723 | 13.1245 | 13.322 | 12.708 | 13.1994 | 12.925 | 12.6776 | NaN | NaN | NaN | 13.2221 | 92.0118 | NaN | NaN | NaN | -12.0585 | NaN | NaN | NaN | NaN | 535.8074 | NaN | 30.1189 | NaN | 28.6033
5153.1292 | 13.2909 | 12.969 | 13.1172 | 13.3218 | 12.9402 | 12.9998 | 12.7768 | 12.682 | NaN | NaN | NaN | 13.0834 | 93.0329 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 484 | NaN | 26.5135 | NaN | 28.6989
5154.1292 | 13.2702 | 12.9809 | 13.1237 | 13.3238 | 12.9475 | 12.9996 | 12.7835 | 12.6827 | NaN | NaN | NaN | 13.1283 | 93.3867 | NaN | NaN | NaN | -19.2823 | NaN | NaN | NaN | NaN | 512.8714 | NaN | 27.244 | NaN | 29.4625
5155.1292 | 13.5634 | 13.1131 | 13.1224 | 13.3854 | 12.8955 | 13.1297 | 12.8487 | 12.6859 | NaN | NaN | NaN | 13.0735 | 94.1863 | NaN | NaN | NaN | 8.7499 | NaN | NaN | NaN | NaN | 544.4701 | NaN | 27.4704 | NaN | 28.4255
5156.1292 | 13.2383 | 13.0993 | 13.1231 | 13.3444 | 12.6822 | 13.1137 | 12.8516 | 12.6854 | NaN | NaN | NaN | 13.079 | 91.4243 | NaN | NaN | NaN | -12.7617 | NaN | NaN | NaN | NaN | 565.4368 | NaN | 28.7686 | NaN | 29.2457
5157.1292 | 13.2652 | 13.1316 | 13.1313 | 13.3183 | 12.7332 | 13.1522 | 12.8393 | 12.6898 | NaN | NaN | NaN | 13.2172 | 92.5897 | NaN | NaN | NaN | 7.6736 | NaN | NaN | NaN | NaN | 579.3617 | NaN | 25.9398 | NaN | 29.3253
5158.1292 | 13.3046 | 13.1994 | 13.1347 | 13.2907 | 12.7237 | 13.2062 | 12.8546 | 12.6916 | NaN | NaN | NaN | 13.1782 | 92.7175 | NaN | NaN | NaN | -10.3417 | NaN | NaN | NaN | NaN | 600.203 | NaN | 27.9742 | NaN | 29.1953
5159.1292 | 13.2735 | 13.1285 | 13.1356 | 13.3033 | 12.6668 | 13.3083 | 12.8751 | 12.6915 | NaN | NaN | NaN | 13.1419 | 93.0619 | NaN | NaN | NaN | -9.9717 | NaN | NaN | NaN | NaN | 601.5364 | NaN | 27.474 | NaN | 29.5914
5160.1292 | 13.2779 | 13.0783 | 13.1333 | 13.2736 | 12.7194 | 13.1356 | 12.8372 | 12.6949 | NaN | NaN | NaN | 13.0682 | 91.7088 | NaN | NaN | NaN | -11.9149 | NaN | NaN | NaN | NaN | 604.2098 | NaN | 27.1825 | NaN | 28.1366
5161.1292 | 13.3192 | 13.0177 | 13.1376 | 13.3052 | 12.7731 | 13.123 | 12.8332 | 12.7007 | NaN | NaN | NaN | 13.1376 | 93.3099 | NaN | NaN | NaN | 15.6469 | NaN | NaN | NaN | NaN | 604.0529 | NaN | 27.1115 | NaN | 26.0045
5162.1292 | 13.2204 | 13.064 | 13.1385 | 13.3467 | 12.7106 | 13.1616 | 12.852 | 12.6978 | NaN | NaN | NaN | 13.1312 | 94.093 | NaN | NaN | NaN | 15.3224 | NaN | NaN | NaN | NaN | 603.9898 | NaN | 27.7873 | NaN | 28.2522
5163.1292 | 13.2729 | 13.0776 | 13.1472 | 13.3151 | 12.7254 | 13.3227 | 12.8533 | 12.7057 | NaN | NaN | NaN | 13.0802 | 92.0316 | NaN | NaN | NaN | -19.3495 | NaN | NaN | NaN | NaN | 604.4809 | NaN | 26.6557 | NaN | 26.9085
5164.1292 | 13.2855 | 13.4881 | 13.1452 | 13.2628 | 12.7476 | 13.1726 | 12.9417 | 12.7028 | NaN | NaN | NaN | 13.1789 | 92.8342 | NaN | NaN | NaN | -17.4393 | NaN | NaN | NaN | NaN | 603.4042 | NaN | 27.649 | NaN | 29.2525
5165.1292 | 13.2314 | 13.0819 | 13.1462 | 13.2991 | 12.6655 | 13.2027 | 12.8647 | 12.7105 | NaN | NaN | NaN | 13.1756 | 93.4453 | NaN | NaN | NaN | 6.4029 | NaN | NaN | NaN | NaN | 603.5005 | NaN | 27.6542 | NaN | 29.322
5166.1292 | 13.286 | 13.1239 | 13.1455 | 13.2705 | 12.8256 | 13.2962 | 12.8902 | 12.7131 | NaN | NaN | NaN | 13.1579 | 91.7974 | NaN | NaN | NaN | 12.0973 | NaN | NaN | NaN | NaN | 604.201 | NaN | 27.2111 | NaN | 28.752
5167.1292 | 13.283 | 13.0872 | 13.1575 | 13.2789 | 12.8636 | 13.405 | 12.8872 | 12.7119 | NaN | NaN | NaN | 13.1289 | 92.204 | NaN | NaN | NaN | -15.0382 | NaN | NaN | NaN | NaN | 604.2136 | NaN | 28.1312 | NaN | 28.7773
5168.1292 | 13.2395 | 13.1978 | 13.1486 | 13.3031 | 12.7488 | 13.1979 | 12.8945 | 12.71 | NaN | NaN | NaN | 13.0842 | 93.8557 | NaN | NaN | NaN | -16.2575 | NaN | NaN | NaN | NaN | 605.5346 | NaN | 27.2082 | NaN | 28.9165
5169.1292 | 13.2991 | 13.0911 | 13.1526 | 13.438 | 12.7036 | 13.1824 | 12.8632 | 12.7078 | NaN | NaN | NaN | 13.1417 | 94.2722 | NaN | NaN | NaN | 19.7654 | NaN | NaN | NaN | NaN | 607.0241 | NaN | 28.3384 | NaN | 26.9628
5170.1292 | 13.2739 | 13.0667 | 13.1522 | 13.3418 | 12.6412 | 13.2695 | 12.8607 | 12.7155 | NaN | NaN | NaN | 13.0804 | 92.4764 | NaN | NaN | NaN | -17.9739 | NaN | NaN | NaN | NaN | 607.9411 | NaN | 28.4282 | NaN | 29.2975
5171.1292 | 13.4974 | 13.1282 | 13.1565 | 13.2924 | 12.817 | 13.1383 | 12.8805 | 12.7141 | NaN | NaN | NaN | 13.0618 | 94.8194 | NaN | NaN | NaN | -15.4364 | NaN | NaN | NaN | NaN | 606.3794 | NaN | 27.8319 | NaN | 28.2939
5172.1292 | 13.3254 | 13.0905 | 13.1562 | 13.3532 | 12.608 | 13.2201 | 12.8707 | 12.7176 | NaN | NaN | NaN | 13.1033 | 92.6096 | NaN | NaN | NaN | -9.2212 | NaN | NaN | NaN | NaN | 596.8956 | NaN | 26.9295 | NaN | 27.1666
5173.1292 | 13.3765 | 13.1032 | 13.1651 | 13.3864 | 12.6613 | 13.2493 | 12.8774 | 12.7191 | NaN | NaN | NaN | 13.2091 | 92.4385 | NaN | NaN | NaN | -8.4851 | NaN | NaN | NaN | NaN | 594.9825 | NaN | 27.7464 | NaN | 29.5949
5174.1292 | 13.3166 | 13.0466 | 13.1653 | 13.3244 | 12.7853 | 13.1417 | 12.8562 | 12.7174 | NaN | NaN | NaN | 13.2133 | 93.4531 | NaN | NaN | NaN | -16.1284 | NaN | NaN | NaN | NaN | 609.802 | NaN | 28.1201 | NaN | 27.702
5175.1292 | 13.2962 | 13.2231 | 13.1683 | 13.3485 | 12.7262 | 13.2095 | 12.8677 | 12.7254 | NaN | NaN | NaN | 13.1378 | 93.2829 | NaN | NaN | NaN | 12.4646 | NaN | NaN | NaN | NaN | 609.5238 | NaN | 26.957 | NaN | 28.73
5176.1292 | 13.3719 | 13.1971 | 13.1655 | 13.3236 | 12.7767 | 13.1922 | 12.8926 | 12.726 | NaN | NaN | NaN | 13.0876 | 91.5085 | NaN | NaN | NaN | 0.3177 | NaN | NaN | NaN | NaN | 612.0571 | NaN | 27.1028 | NaN | 29.174
5177.1292 | 13.3213 | 13.0701 | 13.1688 | 13.3393 | 12.6604 | 13.1969 | 12.8687 | 12.7295 | NaN | NaN | NaN | 13.1218 | 94.1043 | NaN | NaN | NaN | -11.1861 | NaN | NaN | NaN | NaN | 611.3498 | NaN | 28.5413 | NaN | 29.16
5178.1292 | 13.2704 | 13.0236 | 13.1718 | 13.3309 | 12.7947 | 13.1188 | 12.8364 | 12.727 | NaN | NaN | NaN | 13.1869 | 93.536 | NaN | NaN | NaN | -18.9179 | NaN | NaN | NaN | NaN | 611.4247 | NaN | 27.939 | NaN | 27.704
5179.1292 | 13.2923 | 13.0982 | 13.1658 | 13.3306 | 12.8281 | 13.2469 | 12.8807 | 12.7213 | NaN | NaN | NaN | 13.1547 | 92.6193 | NaN | NaN | NaN | -17.1663 | NaN | NaN | NaN | NaN | 611.287 | NaN | 26.8616 | NaN | 27.5343
5180.1292 | 13.3255 | 13.0848 | 13.1751 | 13.3683 | 12.6875 | 13.2299 | 12.8566 | 12.7182 | NaN | NaN | NaN | 13.069 | 94.7713 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 619.4816 | NaN | 29.5945 | NaN | 26.4104
5181.1292 | 13.4272 | 13.0775 | 13.1662 | 13.3572 | 12.7444 | 13.1151 | 12.8527 | 12.724 | NaN | NaN | NaN | 13.1071 | 93.3458 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 330.3997 | NaN | 27.8337 | NaN | 28.0037
5182.1292 | 13.29 | 13.1813 | 13.1636 | 13.3536 | 12.6741 | 13.3143 | 12.9033 | 12.7193 | NaN | NaN | NaN | 13.1133 | 92.6427 | NaN | NaN | NaN | -1.7288 | NaN | NaN | NaN | NaN | 369.8885 | NaN | 28.3186 | NaN | 28.5601
5183.1292 | 13.3626 | 13.0702 | 13.1767 | 13.346 | 12.7607 | 13.221 | 12.8568 | 12.7238 | NaN | NaN | NaN | 13.2328 | 93.9763 | NaN | NaN | NaN | -19.8943 | NaN | NaN | NaN | NaN | 400.5961 | NaN | 27.9968 | NaN | 28.8577
5184.1292 | 13.425 | 13.1089 | 13.1785 | 13.3602 | 12.7348 | 13.2686 | 12.8841 | 12.7263 | NaN | NaN | NaN | 13.0741 | 92.459 | NaN | NaN | NaN | 8.2891 | NaN | NaN | NaN | NaN | 440.1889 | NaN | 28.1868 | NaN | 28.87
5185.1292 | 13.3675 | 13.1405 | 13.1709 | 13.3541 | 12.8289 | 13.1723 | 12.8913 | 12.718 | NaN | NaN | NaN | 13.1075 | 93.4042 | NaN | NaN | NaN | 28.3381 | NaN | NaN | NaN | NaN | 467.7217 | NaN | 26.92 | NaN | 28.9551
5186.1292 | 13.3407 | 13.2451 | 13.1766 | 13.3385 | 12.8157 | 13.25 | 12.9001 | 12.7263 | NaN | NaN | NaN | 13.1998 | 92.647 | NaN | NaN | NaN | 6.8588 | NaN | NaN | NaN | NaN | 496.5279 | NaN | 27.5027 | NaN | 29.3811
5187.1292 | 13.4163 | 13.0729 | 13.1742 | 13.3964 | 12.9485 | 13.1443 | 12.8488 | 12.7189 | NaN | NaN | NaN | 13.0888 | 68.377 | NaN | NaN | NaN | -19.0938 | NaN | NaN | NaN | NaN | 46.6245 | NaN | 27.3674 | NaN | 27.5871
5188.1292 | 13.4144 | 13.1084 | 13.1729 | 13.615 | 12.7603 | 13.0942 | 12.8716 | 12.7296 | NaN | NaN | NaN | 13.111 | 92.4877 | NaN | NaN | NaN | 91.9308 | NaN | NaN | NaN | 27.999 | NaN | NaN | 28.4209 | NaN | 28.6386
5189.1292 | 13.3755 | 13.1115 | 13.1835 | 13.3335 | 12.7522 | 13.1281 | 12.8888 | 12.7286 | NaN | NaN | NaN | 13.1289 | 98.3485 | NaN | NaN | NaN | 67.3081 | NaN | NaN | NaN | 31.6858 | 59.2467 | NaN | 27.4219 | NaN | 29.5861
5190.1292 | 13.3956 | 13.0817 | 13.1789 | 13.3602 | 12.8381 | 13.1338 | 12.8583 | 12.7356 | NaN | NaN | NaN | 13.1885 | 96.0986 | NaN | NaN | NaN | 0.8027 | NaN | NaN | NaN | 19.9836 | 119.7835 | NaN | 27.6771 | NaN | 29.4227
5191.1292 | 13.4628 | 13.0438 | 13.1839 | 13.3773 | 12.7252 | 13.1906 | 12.8535 | 12.7282 | NaN | NaN | NaN | 13.2179 | 92.8301 | NaN | NaN | NaN | -17.0305 | NaN | NaN | NaN | 22.8964 | 168.2031 | NaN | 26.7494 | NaN | 27.2157
5192.1292 | 13.3702 | 13.0907 | 13.1817 | 13.3856 | 12.7679 | 13.201 | 12.8711 | 12.7267 | NaN | NaN | NaN | 13.1186 | 93.8083 | NaN | NaN | NaN | 1.0428 | NaN | NaN | NaN | 34.5533 | 202.2466 | NaN | 27.4456 | NaN | 28.8238
5193.1292 | 13.3681 | 13.1217 | 13.1872 | 13.3687 | 12.8268 | 13.1607 | 12.8795 | 12.7193 | NaN | NaN | NaN | 13.0976 | 95.6152 | NaN | NaN | NaN | 3.3466 | NaN | NaN | NaN | 24.5162 | 225.4988 | NaN | 27.8065 | NaN | 29.4342
5194.1292 | 13.3598 | 13.1024 | 13.1916 | 13.4009 | 12.7221 | 13.1321 | 12.9027 | 12.7348 | NaN | NaN | NaN | 13.1618 | 96.1267 | NaN | NaN | NaN | -10.9506 | NaN | NaN | NaN | 25.6409 | 256.5966 | NaN | 27.9549 | NaN | 29.5668
5195.1292 | 13.4133 | 13.0395 | 13.1895 | 13.3633 | 12.7952 | 13.1703 | 12.8715 | 12.7347 | NaN | NaN | NaN | 13.0994 | 94.2675 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 23.2516 | 285.3829 | NaN | 27.2024 | NaN | 28.6337
5196.1292 | 13.5611 | 13.3259 | 13.184 | 13.4022 | 12.8298 | 12.9976 | 12.9731 | 12.4326 | NaN | NaN | NaN | 13.1688 | 94.9482 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 257.7862 | NaN | 28.0572 | NaN | 27.0969
5197.1292 | 13.4817 | 13.2558 | 13.1895 | 13.3421 | 12.747 | 13.1639 | 12.9101 | 12.7087 | NaN | NaN | NaN | 13.1523 | 93.5559 | NaN | NaN | NaN | -10.1568 | NaN | NaN | NaN | NaN | 276.529 | NaN | 28.5015 | NaN | 27.45
5198.1292 | 13.3881 | 13.126 | 13.1877 | 13.3821 | 12.9342 | 13.092 | 12.9062 | 12.7494 | NaN | NaN | NaN | 13.0654 | 96.2419 | NaN | NaN | NaN | -6.7414 | NaN | NaN | NaN | NaN | 298.4471 | NaN | 28.5932 | NaN | 30.2047
5199.1292 | 13.4435 | 13.1106 | 13.2147 | 13.3986 | 12.8324 | 13.1434 | 12.9218 | 12.7888 | NaN | NaN | NaN | 13.0323 | 64.9867 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 63.8884 | NaN | 25.8652 | NaN | 28.5826
5200.1292 | 13.4141 | 13.131 | 13.1956 | 13.3727 | 12.7796 | 13.2222 | 12.8966 | 12.7541 | NaN | NaN | NaN | 13.1033 | 92.0765 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -17.3399 | 263.2502 | NaN | 27.7454 | NaN | 29.1547
5201.1292 | 13.6058 | 13.2771 | 13.1967 | 13.3673 | 12.7621 | 13.1492 | 12.9176 | 12.7551 | NaN | NaN | NaN | 13.2068 | 93.6913 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 296.2104 | NaN | 26.8946 | NaN | 28.0287
5202.1292 | 13.4163 | 13.0884 | 13.204 | 13.3814 | 12.8309 | 13.2066 | 12.8771 | 12.7566 | NaN | NaN | NaN | 13.1647 | 94.9237 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 309.4953 | NaN | 27.7184 | NaN | 28.725
5203.1292 | 13.4266 | 13.304 | 13.2057 | 13.3965 | 12.7537 | 13.1687 | 12.9521 | 12.7595 | NaN | NaN | NaN | 13.1471 | 93.8609 | NaN | NaN | NaN | -3.5587 | NaN | NaN | NaN | NaN | 348.4414 | NaN | 26.5512 | NaN | 26.9024
5204.1292 | 13.4375 | 13.1084 | 13.2109 | 13.3819 | 12.7758 | 13.2073 | 12.8891 | 12.7528 | NaN | NaN | NaN | 13.1921 | 92.8837 | NaN | NaN | NaN | -3.4383 | NaN | NaN | NaN | NaN | 385.9834 | NaN | 28.7416 | NaN | 28.5471
5205.1292 | 13.4315 | 13.2993 | 13.2132 | 13.404 | 12.8991 | 13.1545 | 12.9326 | 12.756 | NaN | NaN | NaN | 13.3626 | 94.0067 | NaN | NaN | NaN | 22.7863 | NaN | NaN | NaN | NaN | 282.2399 | NaN | 28.4488 | NaN | 28.7908
5206.1292 | 13.5508 | 13.099 | 13.2175 | 13.326 | 12.7008 | 13.1156 | 12.8873 | 12.7565 | NaN | NaN | NaN | 13.1393 | 92.5912 | NaN | NaN | NaN | 40.7263 | NaN | NaN | NaN | NaN | 413.3794 | NaN | 27.1554 | NaN | 29.0391
5207.1292 | 13.4234 | 13.0723 | 13.2049 | 13.439 | 13.0134 | 13.1078 | 12.8609 | 12.7653 | NaN | NaN | NaN | 13.1348 | 93.5242 | NaN | NaN | NaN | 32.1279 | NaN | NaN | NaN | NaN | 467.9145 | NaN | 27.5569 | NaN | 28.6704
5208.1292 | 13.5987 | 13.2077 | 13.2106 | 13.4869 | 12.8771 | 13.1192 | 12.9303 | 12.7536 | NaN | NaN | NaN | 13.2247 | 94.5469 | NaN | NaN | NaN | -13.0366 | NaN | NaN | NaN | NaN | 547.6494 | NaN | 25.9916 | NaN | 29.7391
5209.1292 | 13.4252 | 13.06 | 13.2226 | 13.4351 | 13.0173 | 13.1167 | 12.8784 | 12.77 | NaN | NaN | NaN | 13.3336 | 93.746 | NaN | NaN | NaN | -17.0667 | NaN | NaN | NaN | NaN | 531.7575 | NaN | 28.549 | NaN | 24.9741
5210.1292 | 13.4181 | 13.197 | 13.2286 | 13.5593 | 12.8081 | 13.5282 | 12.9354 | 12.7643 | NaN | NaN | NaN | 13.2132 | 91.5579 | NaN | NaN | NaN | 5.5243 | NaN | NaN | NaN | NaN | 543.8118 | NaN | 28.9176 | NaN | 28.5248
5211.1292 | 13.4311 | 13.0778 | 13.2251 | 13.4362 | 13.0103 | 13.118 | 12.8821 | 12.7742 | NaN | NaN | NaN | 13.2276 | 94.4382 | NaN | NaN | NaN | 1.3864 | NaN | NaN | NaN | NaN | 543.0388 | NaN | 26.525 | NaN | 28.1686
5212.1292 | 13.4205 | 13.1438 | 13.2229 | 13.4885 | 13.0216 | 13.1754 | 12.9307 | 12.7719 | NaN | NaN | NaN | 13.3112 | 94.6277 | NaN | NaN | NaN | -4.2043 | NaN | NaN | NaN | NaN | 569.5993 | NaN | 27.837 | NaN | 29.3759
5213.1292 | 13.4366 | 13.3392 | 13.2185 | 13.4116 | 13.0113 | 13.4083 | 12.9556 | 12.7789 | NaN | NaN | NaN | 13.2868 | 95.4908 | NaN | NaN | NaN | -9.9084 | NaN | NaN | NaN | NaN | 570.0984 | NaN | 28.2501 | NaN | 29.4008
5214.1292 | 13.4383 | 13.215 | 13.1999 | 13.4401 | 13.0087 | 13.1209 | 12.9716 | 12.7919 | NaN | NaN | NaN | 13.178 | 94.6621 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 458.2943 | NaN | 26.5156 | NaN | 28.2045
5215.1292 | 13.458 | 13.2321 | 13.2097 | 13.4541 | 13.0194 | 13.1593 | 12.9604 | 12.7845 | NaN | NaN | NaN | 13.3743 | 93.3213 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 24.1867 | 564.811 | NaN | 28.1717 | NaN | 29.0373
5216.1292 | 13.4641 | 13.1905 | 13.2071 | 13.4168 | 13.0121 | 13.1899 | 12.9335 | 12.7896 | NaN | NaN | NaN | 13.2096 | 92.1502 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 24.6837 | 576.319 | NaN | 26.3123 | NaN | 27.2567
5217.1292 | 13.4785 | 13.2106 | 13.2018 | 13.4264 | 13.0193 | 13.1252 | 12.9513 | 12.7975 | NaN | NaN | NaN | 13.2338 | 98.3461 | NaN | NaN | NaN | -8.9575 | NaN | NaN | NaN | 23.0141 | 600.5667 | NaN | 26.8543 | NaN | 28.0921
5218.1292 | 13.4695 | 13.1241 | 13.1978 | 13.4357 | 13.0137 | 13.1266 | 12.9031 | 12.8023 | NaN | NaN | NaN | 13.1983 | 86.4132 | NaN | NaN | NaN | 8.1573 | NaN | NaN | NaN | 33.5327 | 573.0965 | NaN | 26.1913 | NaN | 29.0585
5219.1292 | 13.4782 | 13.1753 | 13.1984 | 13.4469 | 13.0162 | 13.1356 | 12.9565 | 12.8094 | NaN | NaN | NaN | 13.3921 | 94.1776 | NaN | NaN | NaN | -17.8725 | NaN | NaN | NaN | 32.9542 | 602.1624 | NaN | 27.1382 | NaN | 26.0279
5220.1292 | 13.4837 | 13.2623 | 13.1948 | 13.6528 | 13.0233 | 13.1905 | 12.9677 | 12.812 | NaN | NaN | NaN | 13.212 | 99.2133 | NaN | NaN | NaN | -17.0799 | NaN | NaN | NaN | 27.6709 | 622.3346 | NaN | 26.0447 | NaN | 28.8527
5221.1292 | 13.4881 | 13.1704 | 13.1847 | 13.4131 | 13.0251 | 13.1431 | 12.9413 | 12.8229 | NaN | NaN | NaN | 13.485 | 92.9358 | NaN | NaN | NaN | 78.1067 | NaN | NaN | NaN | NaN | 518.8345 | NaN | 27.4488 | NaN | 28.8768
5222.1448 | 13.4995 | 13.2419 | 13.1779 | 13.3894 | 13.0296 | 13.1369 | 12.9508 | 12.845 | NaN | NaN | NaN | 13.1646 | 92.559 | NaN | NaN | NaN | 55.2274 | NaN | NaN | NaN | NaN | 617.2735 | NaN | 26.7333 | NaN | 26.8992
5223.1292 | 13.5036 | 13.2155 | 13.1787 | 13.566 | 13.0254 | 13.1412 | 12.9638 | 12.8515 | NaN | NaN | NaN | 13.2363 | 92.6909 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 637.7465 | NaN | 25.8753 | NaN | 29.6856
5224.1292 | 13.504 | 13.2066 | 13.1724 | 13.5475 | 13.031 | 13.1385 | 12.9494 | 12.8612 | NaN | NaN | NaN | 13.2653 | 93.6324 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 648.0025 | NaN | 25.4594 | NaN | 27.3419
5225.1292 | 13.4972 | 13.1902 | 13.1646 | 13.468 | 13.0383 | 13.1441 | 12.963 | 12.868 | NaN | NaN | NaN | 13.2622 | 94.1998 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 649.1633 | NaN | 26.4177 | NaN | 28.5887
5226.1292 | 13.4948 | 13.2429 | 13.1699 | 13.5378 | 13.0373 | 13.1486 | 12.9721 | 12.8732 | NaN | NaN | NaN | 13.2387 | 93.4244 | NaN | NaN | NaN | 15.7859 | NaN | NaN | NaN | NaN | 643.8491 | NaN | 27.1053 | NaN | 29.2729
5227.1292 | 13.4987 | 13.2716 | 13.1683 | 13.455 | 13.0434 | 13.1504 | 12.9753 | 12.8767 | NaN | NaN | NaN | 13.2695 | 95.3742 | NaN | NaN | NaN | 6.712 | NaN | NaN | NaN | NaN | 642.5294 | NaN | 27.1641 | NaN | 27.8805
5228.1292 | 13.4947 | 13.1574 | 13.1674 | 13.439 | 13.0417 | 13.1583 | 12.9388 | 12.8786 | NaN | NaN | NaN | 13.2765 | 92.0374 | NaN | NaN | NaN | 3.5204 | NaN | NaN | NaN | NaN | 644.3479 | NaN | 26.7118 | NaN | 27.6511
5229.1292 | 13.4967 | 13.5488 | 13.1654 | 13.4668 | 13.0433 | 13.1579 | 13.0606 | 12.8823 | NaN | NaN | NaN | 13.2134 | 93.2642 | NaN | NaN | NaN | -14.5289 | NaN | NaN | NaN | NaN | 630.8214 | NaN | 26.6159 | NaN | 28.9373
5230.1292 | 13.4895 | 13.1661 | 13.1703 | 13.4252 | 13.0518 | 13.1552 | 12.9601 | 12.8815 | NaN | NaN | NaN | 13.2088 | 93.1677 | NaN | NaN | NaN | -9.9376 | NaN | NaN | NaN | NaN | 643.4764 | NaN | 27.5402 | NaN | 28.3871
5231.1292 | 13.4914 | 13.1721 | 13.168 | 13.4443 | 13.0537 | 13.1596 | 12.952 | 12.8899 | NaN | NaN | NaN | 13.2195 | 93.1406 | NaN | NaN | NaN | -1.9866 | NaN | NaN | NaN | NaN | 642.5956 | NaN | 26.7019 | NaN | 28.1065
5232.1292 | 13.4795 | 13.319 | 13.1756 | 13.4403 | 13.0557 | 13.1615 | 13.0208 | 12.8949 | NaN | NaN | NaN | 13.2596 | 94.612 | NaN | NaN | NaN | -12.6368 | NaN | NaN | NaN | NaN | 640.9375 | NaN | 27.2779 | NaN | 18.7858
5233.1292 | 13.4545 | 13.2355 | 13.1739 | 13.3997 | 13.0657 | 13.1803 | 12.9916 | 12.8901 | NaN | NaN | NaN | 13.2722 | 92.3034 | NaN | NaN | NaN | 10.7133 | NaN | NaN | NaN | NaN | 632.9381 | NaN | 26.2419 | NaN | 28.1687
5234.1292 | 13.4448 | 13.2254 | 13.1748 | 13.4595 | 13.0715 | 13.2601 | 12.9949 | 12.8769 | NaN | NaN | NaN | 13.2185 | 92.2904 | NaN | NaN | NaN | -14.9668 | NaN | NaN | NaN | NaN | 635.4648 | NaN | 27.0537 | NaN | 28.4794
5235.1292 | 13.5007 | 13.2433 | 13.1744 | 13.5933 | 13.0743 | 13.2159 | 13.0028 | 12.8715 | NaN | NaN | NaN | 13.3068 | 93.8991 | NaN | NaN | NaN | -15.3298 | NaN | NaN | NaN | NaN | 633.7222 | NaN | 27.5715 | NaN | 29.2403
5236.1292 | 13.4558 | 13.1675 | 13.1755 | 13.4653 | 13.0785 | 13.2657 | 12.9871 | 12.8812 | NaN | NaN | NaN | 13.2729 | 93.6299 | NaN | NaN | NaN | -16.9531 | NaN | NaN | NaN | NaN | 640.9659 | NaN | 27.2952 | NaN | 29.2316
5237.1292 | 13.4297 | 13.1967 | 13.179 | 13.4327 | 13.0846 | 13.2343 | 13.0065 | 12.8706 | NaN | NaN | NaN | 13.3286 | 92.8997 | NaN | NaN | NaN | 10.6617 | NaN | NaN | NaN | NaN | 635.8175 | NaN | 27.9814 | NaN | 27.3692
5238.1292 | 13.4494 | 13.1705 | 13.1817 | 13.4456 | 13.0897 | 13.2461 | 13.0001 | 12.8702 | NaN | NaN | NaN | 13.2142 | 91.6481 | NaN | NaN | NaN | 23.1658 | NaN | NaN | NaN | NaN | 643.4957 | NaN | 27.4413 | NaN | 27.9024
5239.1292 | 13.4975 | 13.1915 | 13.1912 | 13.4194 | 13.0899 | 13.2337 | 13.0249 | 12.8721 | NaN | NaN | NaN | 13.1927 | 93.6499 | NaN | NaN | NaN | -0.9974 | NaN | NaN | NaN | NaN | 591.0275 | NaN | 27.6867 | NaN | 29.2845
5240.1292 | 13.729 | 13.3538 | 13.1887 | 13.4021 | 13.0941 | 13.3101 | 13.0281 | 12.8618 | NaN | NaN | NaN | 13.2277 | 94.8641 | NaN | NaN | NaN | 29.3292 | NaN | NaN | NaN | 24.1609 | 550.264 | NaN | 28.2007 | NaN | 29.3709
5241.1292 | 13.4606 | 13.1258 | 13.2003 | 13.4352 | 13.0883 | 13.3341 | 13.0107 | 12.8727 | NaN | NaN | NaN | 13.2185 | 93.2248 | NaN | NaN | NaN | -7.0608 | NaN | NaN | NaN | 24.0862 | 628.1567 | NaN | 28.1071 | NaN | 28.2673
5242.1292 | 13.4728 | 13.1904 | 13.1917 | 13.4292 | 13.0945 | 13.2549 | 13.0076 | 12.8755 | NaN | NaN | NaN | 13.2455 | 94.2179 | NaN | NaN | NaN | 13.0702 | NaN | NaN | NaN | 38.9076 | 578.3913 | NaN | 26.9557 | NaN | 28.3151
5243.1292 | 13.499 | 13.1692 | 13.1985 | 13.4946 | 13.0931 | 13.2688 | 13.0167 | 12.8689 | NaN | NaN | NaN | 13.2059 | 93.5588 | NaN | NaN | NaN | -3.9784 | NaN | NaN | NaN | 25.1889 | 554.0714 | NaN | 27.777 | NaN | 27.8778
5244.1292 | 13.7441 | 13.3522 | 13.1908 | 13.4619 | 12.9578 | 13.363 | 13.0569 | 12.8743 | NaN | NaN | NaN | 13.3246 | 92.2874 | NaN | NaN | NaN | 25.6646 | NaN | NaN | NaN | 32.1039 | 566.5969 | NaN | 26.6842 | NaN | 28.0996
5245.1292 | 13.4435 | 13.255 | 13.1927 | 13.4751 | 12.9111 | 13.2464 | 13.0484 | 12.8717 | NaN | NaN | NaN | 13.2353 | 93.7998 | NaN | NaN | NaN | 7.4592 | NaN | NaN | NaN | 23.5842 | 551.3008 | NaN | 29.097 | NaN | 28.8944
5246.1292 | 13.4818 | 13.182 | 13.1927 | 13.4722 | 12.8065 | 13.2483 | 13.0262 | 12.876 | NaN | NaN | NaN | 13.27 | 92.8508 | NaN | NaN | NaN | 1.9951 | NaN | NaN | NaN | 24.7849 | 562.1801 | NaN | 27.542 | NaN | 27.0315
5247.1292 | 13.4448 | 13.2348 | 13.1909 | 13.5588 | 12.9155 | 13.2596 | 13.0337 | 12.8771 | NaN | NaN | NaN | 13.2661 | 92.1827 | NaN | NaN | NaN | -6.2544 | NaN | NaN | NaN | 21.3938 | 563.3459 | NaN | 28.5587 | NaN | 29.9138
5248.1292 | 13.4514 | 13.1957 | 13.1997 | 13.4542 | 12.9033 | 13.2708 | 13.0289 | 12.8761 | NaN | NaN | NaN | 13.21 | 89.2089 | NaN | NaN | NaN | -11.6702 | NaN | NaN | NaN | 27.2442 | 575.6324 | NaN | 26.0078 | NaN | 27.9028
5249.1292 | 13.4449 | 13.1883 | 13.2011 | 13.502 | 12.965 | 13.259 | 13.0243 | 12.8799 | NaN | NaN | NaN | 13.1973 | 92.91 | NaN | NaN | NaN | -1.3777 | NaN | NaN | NaN | 22.2572 | 597.5772 | NaN | 27.4893 | NaN | 28.1157
5250.1292 | 13.4102 | 13.2222 | 13.2 | 13.4885 | 12.783 | 13.3321 | 13.0487 | 12.8778 | NaN | NaN | NaN | 13.2716 | 92.9234 | NaN | NaN | NaN | -14.9953 | NaN | NaN | NaN | 23.7654 | 613.767 | NaN | 27.2477 | NaN | 26.7666
5251.1292 | 13.5556 | 13.1678 | 13.2028 | 13.637 | 12.8989 | 13.3256 | 13.0181 | 12.8699 | NaN | NaN | NaN | 13.2288 | 93.6868 | NaN | NaN | NaN | 0.3424 | NaN | NaN | NaN | 23.692 | 611.1925 | NaN | 26.5809 | NaN | 28.9954
5252.1292 | 13.4454 | 13.2257 | 13.208 | 13.5166 | 12.7777 | 13.2629 | 13.0437 | 12.8739 | NaN | NaN | NaN | 13.2885 | 94.2461 | NaN | NaN | NaN | -9.691 | NaN | NaN | NaN | 26.5089 | 609.3078 | NaN | 27.2856 | NaN | 29.3401
5253.1292 | 13.4353 | 13.5055 | 13.2105 | 13.562 | 12.9847 | 13.3937 | 13.1148 | 12.8785 | NaN | NaN | NaN | 13.2225 | 93.0871 | NaN | NaN | NaN | 7.5866 | NaN | NaN | NaN | 26.1842 | 628.2718 | NaN | 26.6409 | NaN | 28.6552
5254.1292 | 13.4582 | 13.1927 | 13.2072 | 13.5191 | 12.854 | 13.2494 | 13.0276 | 12.8793 | NaN | NaN | NaN | 13.3313 | 92.4635 | NaN | NaN | NaN | 9.3276 | NaN | NaN | NaN | 24.8326 | 587.5985 | NaN | 26.8915 | NaN | 28.6581
5255.1292 | 13.5025 | 13.2146 | 13.2122 | 13.4344 | 12.9563 | 13.263 | 13.0337 | 12.8762 | NaN | NaN | NaN | 13.2423 | 93.6254 | NaN | NaN | NaN | 5.6004 | NaN | NaN | NaN | 25.9673 | 606.9845 | NaN | 27.248 | NaN | 27.9879
5256.1292 | 13.4891 | 13.1537 | 13.2167 | 13.4789 | 12.7343 | 13.2419 | 13.0201 | 12.8792 | NaN | NaN | NaN | 13.2919 | 96.6234 | NaN | NaN | NaN | 38.9294 | NaN | NaN | NaN | 22.0471 | 626.0005 | NaN | 27.7971 | NaN | 29.7315
5257.1292 | 13.457 | 13.1705 | 13.2182 | 13.5193 | 12.7969 | 13.274 | 13.029 | 12.8767 | NaN | NaN | NaN | 13.2359 | 93.7102 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 25.2556 | 634.0448 | NaN | 27.6063 | NaN | 29.4625
5258.1292 | 13.4647 | 13.1772 | 13.2275 | 13.5525 | 12.8633 | 13.2659 | 13.0381 | 12.8889 | NaN | NaN | NaN | 13.3084 | 93.5327 | NaN | NaN | NaN | -18.0387 | NaN | NaN | NaN | 26.4602 | 634.5663 | NaN | 26.3308 | NaN | 26.6787
5259.1292 | 13.5324 | 13.2092 | 13.2225 | 13.498 | 12.8078 | 13.4253 | 13.0446 | 12.8801 | NaN | NaN | NaN | 13.2799 | 92.0535 | NaN | NaN | NaN | -17.281 | NaN | NaN | NaN | 31.5959 | 633.1087 | NaN | 28.6969 | NaN | 26.9785
5260.1292 | 13.5945 | 13.1599 | 13.2207 | 13.5154 | 12.8538 | 13.2882 | 13.0355 | 12.878 | NaN | NaN | NaN | 13.3436 | 95.598 | NaN | NaN | NaN | -1.1961 | NaN | NaN | NaN | 32.1366 | 633.043 | NaN | 28.1182 | NaN | 26.5364
5261.1292 | 13.4296 | 13.2108 | 13.2225 | 13.5336 | 12.9191 | 13.3541 | 13.0464 | 12.8845 | NaN | NaN | NaN | 13.2693 | 92.1179 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 24.4686 | 634.4232 | NaN | 26.8743 | NaN | 27.4753
5262.1292 | 13.6177 | 13.2265 | 13.231 | 13.5467 | 12.9422 | 13.3164 | 13.0537 | 12.8823 | NaN | NaN | NaN | 13.264 | 95.4836 | NaN | NaN | NaN | -15.5185 | NaN | NaN | NaN | 18.8441 | 629.1871 | NaN | 26.3278 | NaN | 29.5857
5263.1292 | 13.46 | 13.1902 | 13.2336 | 13.5295 | 13.0717 | 13.3402 | 13.0403 | 12.8806 | NaN | NaN | NaN | 13.2327 | 92.6516 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 34.3671 | 635.9262 | NaN | 27.3495 | NaN | 27.8192
5264.1292 | 13.4763 | 13.1736 | 13.2303 | 13.5184 | 12.8769 | 13.2654 | 13.0383 | 12.8678 | NaN | NaN | NaN | 13.2554 | 93.2164 | NaN | NaN | NaN | 3.6887 | NaN | NaN | NaN | 24.7478 | 634.6081 | NaN | 27.7253 | NaN | 25.7569
5265.1292 | 13.4261 | 13.2183 | 13.233 | 13.4939 | 12.9127 | 13.2822 | 13.0462 | 12.8698 | NaN | NaN | NaN | 13.2782 | 93.1988 | NaN | NaN | NaN | 13.8615 | NaN | NaN | NaN | 24.9601 | 634.9654 | NaN | 28.4915 | NaN | 29.0194
5266.1292 | 13.4382 | 13.1663 | 13.2335 | 13.4946 | 12.7882 | 13.2657 | 13.0362 | 12.87 | NaN | NaN | NaN | 13.2436 | 93.8442 | NaN | NaN | NaN | -8.2294 | NaN | NaN | NaN | 32.4402 | 634.1273 | NaN | 27.8343 | NaN | 30.408
5267.1292 | 13.4529 | 13.2133 | 13.2312 | 13.5493 | 12.815 | 13.3202 | 13.0477 | 12.8768 | NaN | NaN | NaN | 13.2573 | 92.1196 | NaN | NaN | NaN | -6.0054 | NaN | NaN | NaN | 25.463 | 633.811 | NaN | 27.5476 | NaN | 27.2897
5268.1292 | 13.4785 | 13.188 | 13.2263 | 13.5365 | 12.8122 | 13.2251 | 13.0252 | 12.8903 | NaN | NaN | NaN | 13.1877 | 92.1729 | NaN | NaN | NaN | 6.0694 | NaN | NaN | NaN | 23.7711 | 635.3341 | NaN | 27.9935 | NaN | 28.6913
5269.1292 | 13.4442 | 13.205 | 13.2264 | 13.4646 | 12.8724 | 13.2249 | 13.0517 | 12.897 | NaN | NaN | NaN | 13.2071 | 90.6537 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 28.3438 | 634.6163 | NaN | 27.2545 | NaN | 29.7213
5270.1292 | 13.461 | 13.1728 | 13.225 | 13.5018 | 12.8618 | 13.2489 | 13.0337 | 12.8973 | NaN | NaN | NaN | 13.2408 | 88.2565 | NaN | NaN | NaN | 4.6116 | NaN | NaN | NaN | 18.3299 | 631.6362 | NaN | 26.8916 | NaN | 28.1951
5271.1292 | 13.4336 | 13.1615 | 13.2184 | 13.5303 | 12.7781 | 13.3415 | 13.023 | 12.8917 | NaN | NaN | NaN | 13.2352 | 91.8158 | NaN | NaN | NaN | -8.3781 | NaN | NaN | NaN | 31.7176 | 636.1638 | NaN | 28.6257 | NaN | 28.028
5272.1292 | 13.4678 | 13.2469 | 13.2173 | 13.6142 | 12.9342 | 13.3697 | 13.0588 | 12.8958 | NaN | NaN | NaN | 13.2987 | 93.646 | NaN | NaN | NaN | -5.3495 | NaN | NaN | NaN | 41.0262 | 641.8019 | NaN | 26.8271 | NaN | 26.9443
5273.1292 | 13.4778 | 13.2197 | 13.2158 | 13.5596 | 13.1167 | 13.2158 | 13.0354 | 12.8951 | NaN | NaN | NaN | 13.1937 | 95.1625 | NaN | NaN | NaN | -18.6475 | NaN | NaN | NaN | 23.9023 | 629.0794 | NaN | 27.0594 | NaN | 28.8619
5274.1292 | 13.4056 | 13.2028 | 13.2116 | 13.5094 | 13.1055 | 13.2669 | 13.0575 | 12.897 | NaN | NaN | NaN | 13.1981 | 88.9981 | NaN | NaN | NaN | 11.0695 | NaN | NaN | NaN | 32.0311 | 636.8042 | NaN | 27.8812 | NaN | 27.9228
5275.1292 | 13.4765 | 13.1397 | 13.1955 | 13.5415 | 13.128 | 13.2122 | 13.0094 | 12.9055 | NaN | NaN | NaN | 13.3484 | 94.0283 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 23.0587 | 618.7184 | NaN | 27.3465 | NaN | 28.5665
5276.1292 | 13.4739 | 13.1507 | 13.185 | 13.5434 | 13.1269 | 13.2208 | 13.0065 | 12.8967 | NaN | NaN | NaN | 13.1917 | 92.6959 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 23.5406 | 657.9513 | NaN | 26.9117 | NaN | 28.2427
5277.1292 | 13.4697 | 13.1472 | 13.1955 | 13.5572 | 13.1286 | 13.2244 | 13.0109 | 12.906 | NaN | NaN | NaN | 13.3301 | 95.5297 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 22.5265 | 687.1855 | NaN | 26.7502 | NaN | 27.4237
5278.1292 | 13.5055 | 13.1744 | 13.1944 | 13.5485 | 13.1286 | 13.2304 | 13.051 | 12.876 | NaN | NaN | NaN | 13.255 | 93.2975 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 34.7811 | 297.4564 | NaN | 27.2912 | NaN | 27.9682
5279.1292 | 13.4751 | 13.2425 | 13.1881 | 13.52 | 12.8551 | 13.2894 | 13.0528 | 12.9007 | NaN | NaN | NaN | 13.2072 | 92.5002 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 158.9697 | NaN | 27.6572 | NaN | 28.242
5280.1292 | 13.357 | 13.1838 | 13.1892 | 13.5233 | 13.085 | 13.287 | 13.0389 | 12.9059 | NaN | NaN | NaN | 13.3801 | 93.9005 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 254.7927 | NaN | 27.6703 | NaN | 29.6722
5281.1292 | 13.5093 | 13.1964 | 13.2028 | 14.014 | 13.1365 | 13.4503 | 13.0501 | 12.8856 | NaN | NaN | NaN | 13.2684 | 91.8458 | NaN | NaN | NaN | -16.8618 | NaN | NaN | NaN | NaN | 328.919 | NaN | 28.085 | NaN | 27.4346
5282.1292 | 13.6003 | 13.2034 | 13.2007 | 13.5403 | 12.8539 | 13.3062 | 13.0526 | 12.8793 | NaN | NaN | NaN | 13.2075 | 93.3096 | NaN | NaN | NaN | -13.3551 | NaN | NaN | NaN | NaN | 372.8802 | NaN | 29.2466 | NaN | 29.6003
5283.1292 | 13.4337 | 13.158 | 13.2066 | 13.5687 | 13.1386 | 13.2094 | 13.0085 | 12.8901 | NaN | NaN | NaN | 13.1926 | 92.3455 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 400.7812 | NaN | 27.7865 | NaN | 29.2149
5284.1292 | 13.4381 | 13.129 | 13.195 | 13.5383 | 13.0977 | 13.2019 | 13.0079 | 12.8885 | NaN | NaN | NaN | 13.1788 | 92.7876 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -14.279 | 388.992 | NaN | 27.1664 | NaN | 28.1306
5285.1292 | 13.431 | 13.1254 | 13.1991 | 13.5431 | 13.1204 | 13.2024 | 13.0044 | 12.8757 | NaN | NaN | NaN | 13.1724 | 93.0694 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 31.9983 | 434.8378 | NaN | 28.7175 | NaN | 29.0489
5286.1292 | 13.4378 | 13.1413 | 13.2011 | 13.5423 | 13.116 | 13.2049 | 13.0057 | 12.8846 | NaN | NaN | NaN | 13.1795 | 92.7206 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 86.6313 | 470.7699 | NaN | 27.6422 | NaN | 27.759
5287.1292 | 13.4261 | 13.1461 | 13.209 | 13.5573 | 13.1146 | 13.2082 | 13.0384 | 12.877 | NaN | NaN | NaN | 13.1861 | 93.3438 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 130.583 | 505.0967 | NaN | 27.2757 | NaN | 27.8208
5288.1292 | 13.4399 | 13.2576 | 13.2118 | 13.563 | 13.1317 | 13.2111 | 13.0512 | 12.8743 | NaN | NaN | NaN | 13.1918 | 93.7727 | NaN | NaN | NaN | -5.9761 | NaN | NaN | NaN | 105.3218 | 538.4755 | NaN | 28.479 | NaN | 28.414
5289.1292 | 13.4242 | 13.291 | 13.2173 | 13.565 | 13.1251 | 13.2109 | 13.0694 | 12.8711 | NaN | NaN | NaN | 13.1864 | 94.5825 | NaN | NaN | NaN | -15.9276 | NaN | NaN | NaN | 33.9336 | 569.9764 | NaN | 26.5444 | NaN | 28.62
5290.1292 | 13.4353 | 13.2063 | 13.2187 | 13.5815 | 13.1403 | 13.3773 | 13.0481 | 12.87 | NaN | NaN | NaN | 13.2674 | 94.9018 | NaN | NaN | NaN | 5.1547 | NaN | NaN | NaN | 22.309 | 601.9614 | NaN | 27.8436 | NaN | 29.2494
5291.1292 | 13.4243 | 13.212 | 13.2182 | 13.5768 | 13.1317 | 13.2373 | 13.0381 | 12.876 | NaN | NaN | NaN | 13.1701 | 91.9315 | NaN | NaN | NaN | -9.7009 | NaN | NaN | NaN | 28.0017 | 618.4406 | NaN | 26.8266 | NaN | 27.0388
5292.1292 | 13.4383 | 13.2451 | 13.2236 | 13.5214 | 13.1442 | 13.3395 | 13.0547 | 12.8728 | NaN | NaN | NaN | 13.3715 | 93.6804 | NaN | NaN | NaN | -19.0354 | NaN | NaN | NaN | 25.7593 | 645.2593 | NaN | 26.4208 | NaN | 28.8729
5293.1292 | 13.4319 | 13.2701 | 13.2296 | 13.618 | 13.1392 | 13.2811 | 13.0652 | 12.8714 | NaN | NaN | NaN | 13.2025 | 94.3394 | NaN | NaN | NaN | -17.2244 | NaN | NaN | NaN | 26.001 | 647.0413 | NaN | 26.786 | NaN | 27.6939
5294.1292 | 13.4364 | 13.2665 | 13.236 | 13.7328 | 13.1342 | 13.2727 | 13.0785 | 12.8711 | NaN | NaN | NaN | 13.2773 | 92.0108 | NaN | NaN | NaN | 11.7579 | NaN | NaN | NaN | 38.3349 | 647.171 | NaN | 27.1595 | NaN | 27.421
5295.1292 | 13.4243 | 13.1876 | 13.2353 | 13.6895 | 13.1426 | 13.4218 | 13.0714 | 12.8663 | NaN | NaN | NaN | 13.2809 | 94.776 | NaN | NaN | NaN | -11.7254 | NaN | NaN | NaN | 26.2007 | 644.0246 | NaN | 26.7508 | NaN | 27.9794
5296.1292 | 13.427 | 13.1444 | 13.233 | 13.6088 | 13.1408 | 13.6011 | 13.0446 | 12.8717 | NaN | NaN | NaN | 13.3094 | 96.3867 | NaN | NaN | NaN | 4.3647 | NaN | NaN | NaN | 24.416 | 645.3044 | NaN | 27.3174 | NaN | 26.3762
5297.1292 | 13.415 | 13.1739 | 13.231 | 13.5622 | 13.1374 | 13.2468 | 13.0469 | 12.859 | NaN | NaN | NaN | 13.2643 | 94.4921 | NaN | NaN | NaN | -13.6181 | NaN | NaN | NaN | 19.3938 | 641.8749 | NaN | 27.6841 | NaN | 28.5039
5298.1292 | 13.3688 | 13.2428 | 13.2258 | 13.5408 | 13.1376 | 13.2396 | 13.0757 | 12.8614 | NaN | NaN | NaN | 13.347 | 94.2966 | NaN | NaN | NaN | 31.9948 | NaN | NaN | NaN | 24.3389 | 640.361 | NaN | 27.8917 | NaN | 26.3018
5299.1292 | 13.6339 | 13.2692 | 13.225 | 13.5577 | 13.1361 | 13.4288 | 13.1034 | 12.8647 | NaN | NaN | NaN | 13.2211 | 94.402 | NaN | NaN | NaN | -6.7217 | NaN | NaN | NaN | 24.7265 | 639.0374 | NaN | 27.2718 | NaN | 27.4368
5300.1292 | 13.3848 | 13.1687 | 13.2292 | 13.5473 | 13.1356 | 13.4491 | 13.0396 | 12.861 | NaN | NaN | NaN | 13.3018 | 95.3778 | NaN | NaN | NaN | -3.6304 | NaN | NaN | NaN | 22.3152 | 639.569 | NaN | 26.2916 | NaN | 27.0369
5301.1292 | 13.437 | 13.3358 | 13.2235 | 13.5935 | 13.1368 | 13.2144 | 13.1264 | 12.8562 | NaN | NaN | NaN | 13.24 | 95.8722 | NaN | NaN | NaN | -18.0892 | NaN | NaN | NaN | 32.1804 | 638.3121 | NaN | 26.2109 | NaN | 29.2373
5302.1292 | 13.475 | 13.1947 | 13.2207 | 13.5228 | 13.1372 | 13.3776 | 13.0587 | 12.8534 | NaN | NaN | NaN | 13.1594 | 93.7108 | NaN | NaN | NaN | 5.1048 | NaN | NaN | NaN | 21.5714 | 636.1256 | NaN | 27.4094 | NaN | 27.4197
5303.1292 | 13.3707 | 13.1463 | 13.2213 | 13.5301 | 13.142 | 13.2442 | 13.0379 | 12.8617 | NaN | NaN | NaN | 13.1856 | 96.7757 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 34.5268 | 635.3808 | NaN | 26.9507 | NaN | 27.4661
5304.1292 | 13.4028 | 13.2248 | 13.2217 | 13.5533 | 13.1397 | 13.3316 | 13.0718 | 12.8585 | NaN | NaN | NaN | 13.259 | 90.5552 | NaN | NaN | NaN | 4.95 | NaN | NaN | NaN | 22.5806 | 636.385 | NaN | 28.5027 | NaN | 27.8081
5305.1292 | 13.5304 | 13.2835 | 13.2282 | 13.6745 | 13.14 | 13.2105 | 13.0621 | 12.8552 | NaN | NaN | NaN | 13.1662 | 94.0702 | NaN | NaN | NaN | 21.8504 | NaN | NaN | NaN | 23.28 | 637.6627 | NaN | 26.2191 | NaN | 29.1306
5306.1292 | 13.3796 | 13.2543 | 13.2199 | 13.9141 | 13.1377 | 13.3332 | 13.0913 | 12.8524 | NaN | NaN | NaN | 13.2092 | 93.2957 | NaN | NaN | NaN | -7.6042 | NaN | NaN | NaN | 22.7411 | 636.9873 | NaN | 27.4612 | NaN | 28.4601
5307.1292 | 13.3965 | 13.1694 | 13.2261 | 13.5106 | 13.1298 | 13.2636 | 13.0625 | 12.8581 | NaN | NaN | NaN | 13.1856 | 94.0319 | NaN | NaN | NaN | 14.4093 | NaN | NaN | NaN | 34.4798 | 635.5795 | NaN | 27.9052 | NaN | 28.9792
5308.1292 | 13.4243 | 13.2134 | 13.2231 | 13.5202 | 13.1381 | 13.3038 | 13.0638 | 12.8542 | NaN | NaN | NaN | 13.1884 | 97.233 | NaN | NaN | NaN | -4.7415 | NaN | NaN | NaN | 24.8342 | 634.2917 | NaN | 27.5309 | NaN | 28.6825
5309.1292 | 13.4814 | 13.1649 | 13.2287 | 13.5225 | 13.1329 | 13.2736 | 13.05 | 12.8557 | NaN | NaN | NaN | 13.2496 | 96.7877 | NaN | NaN | NaN | -13.2205 | NaN | NaN | NaN | 30.4223 | 634.7445 | NaN | 26.5118 | NaN | 28.9408
5310.1292 | 13.389 | 13.1733 | 13.2296 | 13.5221 | 13.1369 | 13.3038 | 13.0576 | 12.8511 | NaN | NaN | NaN | 13.2022 | 93.2537 | NaN | NaN | NaN | 16.762 | NaN | NaN | NaN | 25.0469 | 628.2914 | NaN | 26.7134 | NaN | 28.8157
5311.1292 | 13.4793 | 13.3113 | 13.2262 | 13.6592 | 13.1361 | 13.3753 | 13.1019 | 12.8606 | NaN | NaN | NaN | 13.2671 | 92.8051 | NaN | NaN | NaN | -12.4221 | NaN | NaN | NaN | 22.7918 | 623.4869 | NaN | 26.6857 | NaN | 27.6166
5312.1292 | 13.3866 | 13.1655 | 13.227 | 13.5148 | 13.135 | 13.2947 | 13.0549 | 12.8578 | NaN | NaN | NaN | 13.2082 | 91.436 | NaN | NaN | NaN | 4.4994 | NaN | NaN | NaN | 23.9223 | 616.795 | NaN | 26.7648 | NaN | 27.9756
5313.1448 | 13.3929 | 13.193 | 13.2296 | 13.5046 | 13.1284 | 13.1824 | 13.0758 | 12.8586 | NaN | NaN | NaN | 13.2474 | 89.8018 | NaN | NaN | NaN | 12.5647 | NaN | NaN | NaN | 25.7229 | 591.6511 | NaN | 29.0189 | NaN | 28.856
5314.1292 | 13.443 | 13.2481 | 13.2342 | 13.5127 | 13.132 | 13.3637 | 13.0877 | 12.856 | NaN | NaN | NaN | 13.1987 | 92.2721 | NaN | NaN | NaN | -19.2745 | NaN | NaN | NaN | 25.2037 | 606.3577 | NaN | 26.7621 | NaN | 28.2503
5315.1292 | 13.4751 | 13.2003 | 13.2262 | 13.5252 | 13.1352 | 13.2167 | 13.0795 | 12.8623 | NaN | NaN | NaN | 13.2292 | 91.8742 | NaN | NaN | NaN | -18.839 | NaN | NaN | NaN | 25.7145 | 613.0383 | NaN | 27.9185 | NaN | 28.2881
5316.1292 | 13.5364 | 13.1913 | 13.2287 | 13.5017 | 13.1348 | 13.2499 | 13.0753 | 12.8602 | NaN | NaN | NaN | 13.1939 | 90.6764 | NaN | NaN | NaN | 32.1368 | NaN | NaN | NaN | 27.8293 | 622.2856 | NaN | 28.1174 | NaN | 29.1859
5317.1448 | 13.4924 | 13.1842 | 13.2283 | 13.5533 | 13.1325 | 13.3843 | 13.068 | 12.8582 | NaN | NaN | NaN | 13.1447 | 94.0317 | NaN | NaN | NaN | -14.2724 | NaN | NaN | NaN | 22.6378 | 625.4669 | NaN | 25.5651 | NaN | 27.3825
5318.1292 | 13.7192 | 13.2343 | 13.2343 | 13.5449 | 13.1382 | 13.2281 | 13.0995 | 12.8572 | NaN | NaN | NaN | 13.2091 | 97.7727 | NaN | NaN | NaN | 15.9941 | NaN | NaN | NaN | 35.1924 | 623.8505 | NaN | 26.8928 | NaN | 27.3745
5319.1448 | 13.4632 | 13.2034 | 13.2327 | 13.4712 | 13.136 | 13.2249 | 13.0819 | 12.8545 | NaN | NaN | NaN | 13.2629 | 93.6741 | NaN | NaN | NaN | -19.1329 | NaN | NaN | NaN | 25.279 | 626.4243 | NaN | 29.3622 | NaN | 29.2186
5320.1292 | 13.3963 | 13.1816 | 13.2317 | 13.487 | 13.1359 | 13.3032 | 13.0811 | 12.858 | NaN | NaN | NaN | 13.19 | 94.5986 | NaN | NaN | NaN | -14.9753 | NaN | NaN | NaN | 21.7611 | 625.3425 | NaN | 26.8369 | NaN | 28.0079
5321.1448 | 13.4549 | 13.1767 | 13.2296 | 13.6524 | 13.1322 | 13.2967 | 13.0798 | 12.8562 | NaN | NaN | NaN | 13.2142 | 93.6874 | NaN | NaN | NaN | -13.6699 | NaN | NaN | NaN | 19.6972 | 623.6152 | NaN | 28.8343 | NaN | 27.9189
5322.1292 | 13.5793 | 13.1912 | 13.2305 | 13.5514 | 13.1218 | 13.3498 | 13.0933 | 12.8635 | NaN | NaN | NaN | 13.1337 | 90.9583 | NaN | NaN | NaN | 5.9327 | NaN | NaN | NaN | 19.9858 | 620.9373 | NaN | 25.2158 | NaN | 27.5998
5323.1448 | 13.4179 | 13.4711 | 13.2303 | 13.5286 | 13.1305 | 13.5819 | 13.127 | 12.8516 | NaN | NaN | NaN | 13.2194 | 93.9959 | NaN | NaN | NaN | -3.6991 | NaN | NaN | NaN | 34.1439 | 623.4053 | NaN | 28.1763 | NaN | 28.1839
5324.1292 | 13.4169 | 13.1753 | 13.2156 | 13.4976 | 13.1305 | 13.2323 | 13.076 | 12.8535 | NaN | NaN | NaN | 13.1443 | 97.0479 | NaN | NaN | NaN | -16.9351 | NaN | NaN | NaN | 24.4802 | 625.575 | NaN | 27.94 | NaN | 27.6105
5325.1292 | 13.4476 | 13.1678 | 13.2238 | 13.5712 | 13.1314 | 13.4034 | 13.0761 | 12.857 | NaN | NaN | NaN | 13.1578 | 91.9221 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 26.821 | 622.863 | NaN | 28.1586 | NaN | 28.8823
5326.1292 | 13.524 | 13.2384 | 13.2179 | 13.4823 | 13.1262 | 13.2332 | 13.0898 | 12.8609 | NaN | NaN | NaN | 13.2154 | 93.6126 | NaN | NaN | NaN | 5.4097 | NaN | NaN | NaN | 25.4996 | 621.0215 | NaN | 25.8499 | NaN | 28.4492
5327.1292 | 13.446 | 13.2241 | 13.2181 | 13.4961 | 13.1245 | 13.2849 | 13.0921 | 12.8599 | NaN | NaN | NaN | 13.3229 | 92.8802 | NaN | NaN | NaN | -4.9125 | NaN | NaN | NaN | 27.8554 | 622.3227 | NaN | 26.7369 | NaN | 28.7602
5328.1292 | 13.4478 | 13.2042 | 13.2178 | 13.477 | 13.126 | 13.3864 | 13.0706 | 12.861 | NaN | NaN | NaN | 13.1601 | 93.0117 | NaN | NaN | NaN | -4.1036 | NaN | NaN | NaN | 25.7177 | 625.2594 | NaN | 27.489 | NaN | 29.3909
5329.1292 | 13.3975 | 13.1518 | 13.2161 | 13.5444 | 13.1201 | 13.2233 | 13.062 | 12.8632 | NaN | NaN | NaN | 13.2982 | 94.9353 | NaN | NaN | NaN | -16.3774 | NaN | NaN | NaN | 22.1261 | 625.902 | NaN | 28.1719 | NaN | 27.4006
5330.1292 | 13.4245 | 13.1827 | 13.2179 | 13.5172 | 13.1149 | 13.2391 | 13.08 | 12.8566 | NaN | NaN | NaN | 13.2564 | 98.5869 | NaN | NaN | NaN | 51.6121 | NaN | NaN | NaN | 27.5399 | 621.7563 | NaN | 28.2128 | NaN | 29.2588
5331.1292 | 13.5067 | 13.1601 | 13.2235 | 13.4901 | 13.1246 | 13.2479 | 13.0773 | 12.8629 | NaN | NaN | NaN | 13.152 | 94.6371 | NaN | NaN | NaN | -11.6267 | NaN | NaN | NaN | 21.1718 | 623.8069 | NaN | 27.5459 | NaN | 28.2826
5332.1292 | 13.375 | 13.1522 | 13.2216 | 13.5346 | 13.1241 | 13.2895 | 13.0596 | 12.8617 | NaN | NaN | NaN | 13.2665 | 105.5418 | NaN | NaN | NaN | -1.2402 | NaN | NaN | NaN | 32.6327 | 623.0545 | NaN | 27.7612 | NaN | 29.0638
5333.1292 | 13.637 | 13.2687 | 13.2281 | 13.4506 | 13.1142 | 13.2501 | 13.1005 | 12.87 | NaN | NaN | NaN | 13.2628 | 93.7643 | NaN | NaN | NaN | -19.7446 | NaN | NaN | NaN | 28.3361 | 624.2361 | NaN | 27.3418 | NaN | 26.5761
5334.1292 | 13.4324 | 13.1898 | 13.2291 | 13.6035 | 13.1169 | 13.2976 | 13.0724 | 12.8643 | NaN | NaN | NaN | 13.1863 | 92.2698 | NaN | NaN | NaN | -2.1979 | NaN | NaN | NaN | 28.8588 | 623.7921 | NaN | 27.8743 | NaN | 28.8398
5335.1292 | 13.4486 | 13.1666 | 13.2245 | 13.5979 | 13.1099 | 13.252 | 13.0511 | 12.8668 | NaN | NaN | NaN | 13.2294 | 94.1077 | NaN | NaN | NaN | -15.0235 | NaN | NaN | NaN | 27.5153 | 625.2503 | NaN | 26.2502 | NaN | 27.4118
5336.1292 | 13.4282 | 13.2995 | 13.2234 | 13.5022 | 13.1005 | 13.2647 | 13.0987 | 12.8622 | NaN | NaN | NaN | 13.2042 | 97.0761 | NaN | NaN | NaN | -13.76 | NaN | NaN | NaN | 21.3641 | 615.8906 | NaN | 25.9199 | NaN | 24.7037
5337.1292 | 13.4266 | 13.3022 | 13.2249 | 13.5354 | 13.1017 | 13.2237 | 13.0887 | 12.8689 | NaN | NaN | NaN | 13.1697 | 94.9675 | NaN | NaN | NaN | 7.8745 | NaN | NaN | NaN | 21.0073 | 601.2969 | NaN | 26.2135 | NaN | 28.3189
5338.1292 | 13.3987 | 13.183 | 13.2262 | 13.5044 | 13.1046 | 13.255 | 13.0694 | 12.868 | NaN | NaN | NaN | 13.2763 | 93.7856 | NaN | NaN | NaN | -18.9234 | NaN | NaN | NaN | 28.2304 | 620.6264 | NaN | 26.0913 | NaN | 28.0514
5339.1292 | 13.3822 | 13.1959 | 13.2297 | 13.5056 | 13.1079 | 13.2831 | 13.0756 | 12.8696 | NaN | NaN | NaN | 13.2992 | 91.7101 | NaN | NaN | NaN | 1.8141 | NaN | NaN | NaN | 33.8858 | 624.9819 | NaN | 25.9142 | NaN | 26.9721
5340.1292 | 13.4001 | 13.4548 | 13.2152 | 13.4291 | 13.1008 | 13.2531 | 13.1517 | 12.861 | NaN | NaN | NaN | 13.2214 | 95.3425 | NaN | NaN | NaN | 0.9086 | NaN | NaN | NaN | 35.8665 | 624.0966 | NaN | 28.8605 | NaN | 29.8361
5341.1292 | 13.3989 | 13.2078 | 13.2116 | 13.5137 | 13.1077 | 13.2681 | 13.0603 | 12.8682 | NaN | NaN | NaN | 13.18 | 93.9039 | NaN | NaN | NaN | 4.2594 | NaN | NaN | NaN | 25.0267 | 623.0616 | NaN | 27.9232 | NaN | 28.4195
5342.1292 | 13.4089 | 13.3037 | 13.2049 | 13.5027 | 13.095 | 13.2603 | 13.0799 | 12.8627 | NaN | NaN | NaN | 13.1237 | 91.7883 | NaN | NaN | NaN | -17.23 | NaN | NaN | NaN | 22.6699 | 621.818 | NaN | 28.358 | NaN | 29.8707
5343.1292 | 13.4443 | 13.1521 | 13.2023 | 13.5178 | 13.0901 | 13.3894 | 13.0642 | 12.8606 | NaN | NaN | NaN | 13.1261 | 92.0598 | NaN | NaN | NaN | 9.0241 | NaN | NaN | NaN | 24.666 | 619.316 | NaN | 27.7387 | NaN | 28.2241
5344.1292 | 13.4306 | 13.2037 | 13.2006 | 13.7158 | 12.8953 | 13.2438 | 13.0698 | 12.8631 | NaN | NaN | NaN | 13.2395 | 96.5066 | NaN | NaN | NaN | 17.1381 | NaN | NaN | NaN | 23.2364 | 618.5384 | NaN | 27.544 | NaN | 29.5939
5345.1292 | 13.3933 | 13.1738 | 13.1981 | 13.4969 | 12.8465 | 13.3736 | 13.064 | 12.8652 | NaN | NaN | NaN | 13.2032 | 94.536 | NaN | NaN | NaN | -10.868 | NaN | NaN | NaN | 24.0163 | 614.4845 | NaN | 27.2079 | NaN | 29.2555
5346.1292 | 13.3982 | 13.1923 | 13.1978 | 13.5864 | 12.9168 | 13.2371 | 13.0687 | 12.8672 | NaN | NaN | NaN | 13.2348 | 94.8243 | NaN | NaN | NaN | -8.7648 | NaN | NaN | NaN | 44.2973 | 616.95 | NaN | 28.4843 | NaN | 29.0055
5347.1292 | 13.3974 | 13.2471 | 13.1972 | 13.5639 | 12.9308 | 13.4379 | 13.0655 | 12.8729 | NaN | NaN | NaN | 13.1803 | 93.5263 | NaN | NaN | NaN | 11.7807 | NaN | NaN | NaN | 17.1306 | 615.3076 | NaN | 27.9304 | NaN | 29.1478
5348.1292 | 13.4424 | 13.2269 | 13.1973 | 13.4296 | 12.9131 | 13.2407 | 13.0625 | 12.867 | NaN | NaN | NaN | 13.122 | 93.7675 | NaN | NaN | NaN | 17.8634 | NaN | NaN | NaN | 21.34 | 614.4771 | NaN | 26.1827 | NaN | 28.0347
5349.1292 | 13.4004 | 13.1556 | 13.1981 | 13.5328 | 12.7279 | 13.3247 | 13.0432 | 12.8642 | NaN | NaN | NaN | 13.1957 | 95.0625 | NaN | NaN | NaN | -14.7999 | NaN | NaN | NaN | 29.1814 | 612.5333 | NaN | 26.8185 | NaN | 28.6584
5350.1292 | 13.4321 | 13.2402 | 13.2101 | 13.5297 | 12.8975 | 13.2409 | 13.0801 | 12.8629 | NaN | NaN | NaN | 13.216 | 98.6069 | NaN | NaN | NaN | -9.1372 | NaN | NaN | NaN | 26.1428 | 611.7526 | NaN | 27.6851 | NaN | 28.0481
5351.1292 | 13.4278 | 13.209 | 13.2016 | 13.5206 | 12.846 | 13.2874 | 13.0572 | 12.8656 | NaN | NaN | NaN | 13.1778 | 97.2405 | NaN | NaN | NaN | -8.4594 | NaN | NaN | NaN | 24.5592 | 611.3569 | NaN | 27.238 | NaN | 27.2849
5352.1292 | 13.4211 | 13.259 | 13.208 | 13.4784 | 12.819 | 13.2383 | 13.0772 | 12.8576 | NaN | NaN | NaN | 13.1367 | 97.2416 | NaN | NaN | NaN | 12.876 | NaN | NaN | NaN | 22.3493 | 608.9238 | NaN | 27.2512 | NaN | 27.4164
5353.1292 | 13.541 | 13.1786 | 13.2079 | 13.4698 | 12.86 | 13.2261 | 13.0445 | 12.8545 | NaN | NaN | NaN | 13.198 | 96.1041 | NaN | NaN | NaN | -2.4174 | NaN | NaN | NaN | 22.8617 | 610.0305 | NaN | 28.4246 | NaN | 29.8555
5354.1292 | 13.4591 | 13.2021 | 13.2157 | 13.5009 | 12.7522 | 13.2372 | 13.0427 | 12.8601 | NaN | NaN | NaN | 13.1557 | 92.2614 | NaN | NaN | NaN | 1.3478 | NaN | NaN | NaN | 22.0173 | 610.0778 | NaN | 27.3543 | NaN | 29.6447
5355.1292 | 13.4225 | 13.1732 | 13.2161 | 13.5234 | 12.9633 | 13.4329 | 13.0503 | 12.8588 | NaN | NaN | NaN | 13.1155 | 94.133 | NaN | NaN | NaN | 7.2235 | NaN | NaN | NaN | 17.6074 | 611.4981 | NaN | 28.2072 | NaN | 28.9591
5356.1292 | 13.4657 | 13.3953 | 13.2193 | 13.4396 | 12.7783 | 13.6539 | 13.0935 | 12.857 | NaN | NaN | NaN | 13.1936 | 95.9374 | NaN | NaN | NaN | 17.6503 | NaN | NaN | NaN | 27.5542 | 610.3279 | NaN | 27.4229 | NaN | 29.5104
5357.1292 | 13.4253 | 13.1918 | 13.218 | 13.4576 | 12.9079 | 13.2588 | 13.0407 | 12.8576 | NaN | NaN | NaN | 13.1231 | 94.4192 | NaN | NaN | NaN | 3.7156 | NaN | NaN | NaN | 22.5023 | 611.7496 | NaN | 27.0516 | NaN | 28.2376
5358.1292 | 13.6125 | 13.207 | 13.2279 | 13.5074 | 12.8855 | 13.2547 | 13.0528 | 12.8645 | NaN | NaN | NaN | 13.113 | 92.0912 | NaN | NaN | NaN | -8.0987 | NaN | NaN | NaN | 23.6548 | 607.7785 | NaN | 28.0613 | NaN | 26.2716
5359.1292 | 13.3767 | 13.2092 | 13.2294 | 13.474 | 12.8297 | 13.7632 | 13.061 | 12.864 | NaN | NaN | NaN | 13.1589 | 92.9092 | NaN | NaN | NaN | -2.072 | NaN | NaN | NaN | 43.5639 | 608.7332 | NaN | 27.7343 | NaN | 28.8979
5360.1292 | 13.4381 | 13.1962 | 13.2293 | 13.6201 | 12.7582 | 13.4505 | 13.0475 | 12.8628 | NaN | NaN | NaN | 13.1092 | 92.4683 | NaN | NaN | NaN | -10.5471 | NaN | NaN | NaN | 27.1577 | 604.3881 | NaN | 26.7938 | NaN | 28.3093
5361.1292 | 13.393 | 13.2849 | 13.2202 | 13.4837 | 12.8489 | 13.3192 | 13.0694 | 12.8606 | NaN | NaN | NaN | 13.1335 | 95.8213 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 22.497 | 605.0887 | NaN | 26.1565 | NaN | 27.8048
5362.1292 | 13.4591 | 13.3402 | 13.2265 | 13.539 | 12.9248 | 13.2341 | 13.0881 | 12.858 | NaN | NaN | NaN | 13.1106 | 89.6574 | NaN | NaN | NaN | 3.6513 | NaN | NaN | NaN | 28.9686 | 606.268 | NaN | 27.5089 | NaN | 27.7938
5363.1292 | 13.525 | 13.2829 | 13.2177 | 13.5051 | 12.8574 | 13.2383 | 13.0689 | 12.8512 | NaN | NaN | NaN | 13.125 | 89.5074 | NaN | NaN | NaN | 6.6717 | NaN | NaN | NaN | 37.8054 | 606.0412 | NaN | 26.7654 | NaN | 26.4854
5364.1292 | 13.3982 | 13.2908 | 13.2142 | 13.5366 | 12.8971 | 13.2739 | 13.0728 | 12.8537 | NaN | NaN | NaN | 13.1168 | 93.7967 | NaN | NaN | NaN | 3.7798 | NaN | NaN | NaN | 23.737 | 602.24 | NaN | 27.2543 | NaN | 28.0283
5365.1292 | 13.43 | 13.1867 | 13.2174 | 13.6725 | 12.7766 | 13.2417 | 13.0497 | 12.8539 | NaN | NaN | NaN | 13.1893 | 93.8692 | NaN | NaN | NaN | -2.8718 | NaN | NaN | NaN | 22.8883 | 606.6199 | NaN | 25.7314 | NaN | 28.5885
5366.1292 | 13.4112 | 13.1831 | 13.2162 | 13.546 | 12.8902 | 13.3844 | 13.0535 | 12.8494 | NaN | NaN | NaN | 13.2368 | 92.9354 | NaN | NaN | NaN | 17.9177 | NaN | NaN | NaN | 47.2815 | 606.4857 | NaN | 27.0568 | NaN | 27.6522
5367.1292 | 13.768 | 13.2486 | 13.2178 | 13.4469 | 12.8836 | 13.3516 | 13.0629 | 12.8465 | NaN | NaN | NaN | 13.1706 | 92.3596 | NaN | NaN | NaN | 13.5696 | NaN | NaN | NaN | 19.126 | 604.8218 | NaN | 28.7185 | NaN | 29.2749
5368.1292 | 13.4616 | 13.2672 | 13.2187 | 13.5058 | 12.9791 | 13.2867 | 13.0574 | 12.8462 | NaN | NaN | NaN | 13.2441 | 93.8523 | NaN | NaN | NaN | -13.4269 | NaN | NaN | NaN | 35.6262 | 604.4441 | NaN | 27.2927 | NaN | 27.8014
5369.1292 | 13.4434 | 13.2113 | 13.2146 | 13.5043 | 12.848 | 13.2566 | 13.0545 | 12.8414 | NaN | NaN | NaN | 13.207 | 94.2402 | NaN | NaN | NaN | -19.4134 | NaN | NaN | NaN | 22.5349 | 606.3713 | NaN | 28.2837 | NaN | 28.1151
5370.1292 | 13.4056 | 13.2052 | 13.2142 | 13.455 | 12.872 | 13.3199 | 13.0567 | 12.8393 | NaN | NaN | NaN | 13.2262 | 94.2942 | NaN | NaN | NaN | -12.8787 | NaN | NaN | NaN | 36.6505 | 606.3626 | NaN | 27.0218 | NaN | 29.2152
5371.1292 | 13.3969 | 13.2411 | 13.2077 | 13.5179 | 12.9101 | 13.2475 | 13.0691 | 12.8457 | NaN | NaN | NaN | 13.109 | 92.3176 | NaN | NaN | NaN | 13.934 | NaN | NaN | NaN | 36.8786 | 606.6322 | NaN | 26.65 | NaN | 28.647
5372.1292 | 13.4489 | 13.1774 | 13.2134 | 13.4928 | 12.8337 | 13.2329 | 13.0523 | 12.8394 | NaN | NaN | NaN | 13.1352 | 92.7415 | NaN | NaN | NaN | 1.0735 | NaN | NaN | NaN | 25.3684 | 606.9441 | NaN | 26.0449 | NaN | 28.3739
5373.1292 | 13.4305 | 13.2115 | 13.2088 | 13.562 | 12.9393 | 13.2814 | 13.049 | 12.8363 | NaN | NaN | NaN | 13.2003 | 93.7406 | NaN | NaN | NaN | -10.628 | NaN | NaN | NaN | 22.6629 | 605.8238 | NaN | 27.9485 | NaN | 25.3685
5374.1292 | 13.5553 | 13.1846 | 13.2072 | 13.5162 | 12.7373 | 13.2778 | 13.0393 | 12.8366 | NaN | NaN | NaN | 13.2218 | 93.1781 | NaN | NaN | NaN | -18.2687 | NaN | NaN | NaN | 26.4189 | 606.3527 | NaN | 27.895 | NaN | 28.6774
5375.1292 | 13.4812 | 13.2023 | 13.2099 | 13.6618 | 12.9028 | 13.2741 | 13.047 | 12.8377 | NaN | NaN | NaN | 13.1335 | 93.2877 | NaN | NaN | NaN | 9.2096 | NaN | NaN | NaN | 25.0879 | 603.0179 | NaN | 27.7384 | NaN | 27.801
5376.1292 | 13.4007 | 13.3324 | 13.2129 | 13.4938 | 12.7447 | 13.2764 | 13.0736 | 12.8394 | NaN | NaN | NaN | 13.1562 | 95.1446 | NaN | NaN | NaN | -6.4386 | NaN | NaN | NaN | 40.9661 | 605.8717 | NaN | 28.3487 | NaN | 28.6201
5377.1292 | 13.4433 | 13.1966 | 13.2159 | 13.5161 | 12.847 | 13.2701 | 13.0434 | 12.8382 | NaN | NaN | NaN | 13.2339 | 93.6395 | NaN | NaN | NaN | -4.2906 | NaN | NaN | NaN | 21.9143 | 603.8022 | NaN | 26.7444 | NaN | 28.1572
5378.1292 | 13.5941 | 13.1977 | 13.2165 | 13.4993 | 12.8256 | 13.2504 | 13.0405 | 12.8397 | NaN | NaN | NaN | 13.1536 | 92.6847 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 23.6498 | 606.3624 | NaN | 26.5131 | NaN | 28.13
5379.1292 | 13.4366 | 13.2319 | 13.209 | 13.4522 | 12.8364 | 13.3655 | 13.052 | 12.8379 | NaN | NaN | NaN | 13.2317 | 88.1892 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 26.8124 | 603.9879 | NaN | 27.5508 | NaN | 27.498
5380.1292 | 13.4301 | 13.1908 | 13.2075 | 13.4636 | 12.8571 | 13.2521 | 13.0276 | 12.8431 | NaN | NaN | NaN | 13.1653 | 94.8443 | NaN | NaN | NaN | -15.4564 | NaN | NaN | NaN | 25.5438 | 607.7041 | NaN | 26.5346 | NaN | 27.3523
5381.1292 | 13.4277 | 13.4311 | 13.2074 | 13.5136 | 12.8731 | 13.2633 | 13.1187 | 12.8378 | NaN | NaN | NaN | 13.2182 | 94.6427 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 23.5588 | 604.4344 | NaN | 26.5152 | NaN | 26.1529
5382.1292 | 13.4047 | 13.2961 | 13.1998 | 13.5021 | 12.7933 | 13.3484 | 13.0387 | 12.8358 | NaN | NaN | NaN | 13.1779 | 93.9121 | NaN | NaN | NaN | -8.4134 | NaN | NaN | NaN | 20.9186 | 604.5113 | NaN | 26.3566 | NaN | 27.5888
5383.1448 | 13.4604 | 13.4521 | 13.1972 | 13.4516 | 12.8681 | 13.2726 | 13.0755 | 12.8347 | NaN | NaN | NaN | 13.1758 | 93.7535 | NaN | NaN | NaN | 1.9781 | NaN | NaN | NaN | 21.9468 | 602.4683 | NaN | 26.4369 | NaN | 28.8129
5384.1292 | 13.5255 | 13.2134 | 13.1974 | 13.4802 | 12.7731 | 13.3346 | 13.0593 | 12.8378 | NaN | NaN | NaN | 13.1729 | 98.5881 | NaN | NaN | NaN | 7.0524 | NaN | NaN | NaN | 23.4598 | 604.971 | NaN | 26.1606 | NaN | 28.0906
5385.1292 | 13.448 | 13.251 | 13.1982 | 13.4741 | 12.8436 | 13.2553 | 13.0634 | 12.8408 | NaN | NaN | NaN | 13.1644 | 96.6746 | NaN | NaN | NaN | 1.8314 | NaN | NaN | NaN | 22.9486 | 604.8001 | NaN | 26.9395 | NaN | 27.1645
5386.1292 | 13.4826 | 13.2297 | 13.2044 | 13.5065 | 12.8958 | 13.2757 | 13.0505 | 12.835 | NaN | NaN | NaN | 13.2603 | 92.7668 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 23.6801 | 603.7843 | NaN | 25.645 | NaN | 28.6602
5387.1292 | 13.5224 | 13.2259 | 13.2044 | 13.5051 | 12.8822 | 13.4515 | 13.0581 | 12.8359 | NaN | NaN | NaN | 13.2037 | 94.4199 | NaN | NaN | NaN | -9.1077 | NaN | NaN | NaN | 24.05 | 602.6043 | NaN | 28.0329 | NaN | 28.9054
5388.1292 | 13.4685 | 13.2018 | 13.2022 | 13.547 | 12.8531 | 13.2411 | 13.04 | 12.8338 | NaN | NaN | NaN | 13.2548 | 94.0206 | NaN | NaN | NaN | 11.4516 | NaN | NaN | NaN | 22.7709 | 602.3117 | NaN | 28.0956 | NaN | 27.101
5389.1292 | 13.4992 | 13.1919 | 13.2081 | 13.504 | 12.9448 | 13.5526 | 13.0432 | 12.8354 | NaN | NaN | NaN | 13.1963 | 90.6265 | NaN | NaN | NaN | -9.7323 | NaN | NaN | NaN | 25.248 | 601.6188 | NaN | 25.9363 | NaN | 28.4935
5390.1292 | 13.4627 | 13.3116 | 13.2115 | 13.4757 | 12.9296 | 13.2599 | 13.064 | 12.8373 | NaN | NaN | NaN | 13.1789 | 98.6368 | NaN | NaN | NaN | 23.3017 | NaN | NaN | NaN | 23.6586 | 603.1259 | NaN | 26.9356 | NaN | 26.9503
5391.1292 | 13.4966 | 13.2178 | 13.2139 | 13.4767 | 12.8943 | 13.3022 | 13.0638 | 12.8352 | NaN | NaN | NaN | 13.1827 | 94.7208 | NaN | NaN | NaN | 8.1742 | NaN | NaN | NaN | 20.562 | 600.0373 | NaN | 28.9892 | NaN | 27.2208
5392.1292 | 13.4222 | 13.2075 | 13.217 | 13.5251 | 12.923 | 13.2542 | 13.0474 | 12.8345 | NaN | NaN | NaN | 13.1718 | 90.8708 | NaN | NaN | NaN | 10.7976 | NaN | NaN | NaN | 23.5312 | 601.2543 | NaN | 26.4631 | NaN | 29.1485
5393.1292 | 13.4904 | 13.2916 | 13.2141 | 13.454 | 12.9649 | 13.3753 | 13.0759 | 12.8368 | NaN | NaN | NaN | 13.166 | 94.7756 | NaN | NaN | NaN | 10.5865 | NaN | NaN | NaN | 31.2116 | 601.002 | NaN | 25.9207 | NaN | 29.6676
5394.1292 | 13.4954 | 13.1762 | 13.2196 | 13.4337 | 13.0043 | 13.3704 | 13.0476 | 12.8323 | NaN | NaN | NaN | 13.239 | 92.1283 | NaN | NaN | NaN | 17.1849 | NaN | NaN | NaN | 26.4156 | 598.5748 | NaN | 27.0351 | NaN | 28.6953
5395.1292 | 13.475 | 13.2488 | 13.2256 | 13.5377 | 12.8209 | 13.5431 | 13.066 | 12.8281 | NaN | NaN | NaN | 13.1763 | 92.5853 | NaN | NaN | NaN | -2.4042 | NaN | NaN | NaN | 24.2778 | 603.0048 | NaN | 26.8932 | NaN | 28.7374
5396.1292 | 13.4445 | 13.1847 | 13.2202 | 13.5144 | 12.9278 | 13.3283 | 13.0189 | 12.8322 | NaN | NaN | NaN | 13.169 | 95.79 | NaN | NaN | NaN | -2.4991 | NaN | NaN | NaN | 28.0755 | 599.8314 | NaN | 28.0683 | NaN | 27.404
5397.1292 | 13.5374 | 13.2102 | 13.2259 | 13.5768 | 12.8376 | 13.2853 | 13.0372 | 12.8364 | NaN | NaN | NaN | 13.1685 | 94.4973 | NaN | NaN | NaN | -16.3264 | NaN | NaN | NaN | 23.1356 | 598.3548 | NaN | 26.0098 | NaN | 25.6076
5398.1292 | 13.4938 | 13.1916 | 13.2211 | 13.5053 | 12.8906 | 13.3041 | 13.0367 | 12.8381 | NaN | NaN | NaN | 13.2834 | 93.4863 | NaN | NaN | NaN | -16.2868 | NaN | NaN | NaN | 18.5601 | 600.562 | NaN | 26.9718 | NaN | 28.4681
5399.1292 | 13.4271 | 13.2314 | 13.2142 | 13.5025 | 12.8901 | 13.2498 | 13.0417 | 12.836 | NaN | NaN | NaN | 13.2381 | 94.4929 | NaN | NaN | NaN | -15.9037 | NaN | NaN | NaN | 27.3753 | 603.5761 | NaN | 27.1361 | NaN | 28.017
5400.1292 | 13.4659 | 13.2323 | 13.2156 | 13.4183 | 12.8951 | 13.4754 | 13.0622 | 12.8395 | NaN | NaN | NaN | 13.2295 | 97.6292 | NaN | NaN | NaN | -11.7458 | NaN | NaN | NaN | 29.7733 | 602.4894 | NaN | 27.2655 | NaN | 28.3963
5401.1292 | 13.5102 | 13.2311 | 13.2199 | 13.507 | 12.8686 | 13.321 | 13.0305 | 12.8405 | NaN | NaN | NaN | 13.2202 | 92.8398 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 41.6045 | 601.7548 | NaN | 26.3874 | NaN | 27.0001
5402.1292 | 13.5073 | 13.402 | 13.2157 | 13.4499 | 12.8792 | 13.2525 | 13.1148 | 12.8396 | NaN | NaN | NaN | 13.2401 | 93.9696 | NaN | NaN | NaN | -12.8184 | NaN | NaN | NaN | 21.6851 | 602.404 | NaN | 26.8598 | NaN | 29.3115
5403.1292 | 13.4789 | 13.2057 | 13.2209 | 13.4684 | 12.9684 | 13.272 | 13.043 | 12.842 | NaN | NaN | NaN | 13.2315 | 93.0104 | NaN | NaN | NaN | -1.3001 | NaN | NaN | NaN | 37.6093 | 601.4826 | NaN | 25.5247 | NaN | 28.4049
5404.1292 | 13.4938 | 13.3086 | 13.2228 | 13.5254 | 12.9765 | 13.3223 | 13.056 | 12.836 | NaN | NaN | NaN | 13.1926 | 97.635 | NaN | NaN | NaN | -2.5675 | NaN | NaN | NaN | 24.12 | 601.4394 | NaN | 27.6649 | NaN | 28.143
5405.1292 | 13.543 | 13.2188 | 13.224 | 13.4627 | 12.8517 | 13.2386 | 13.0396 | 12.8389 | NaN | NaN | NaN | 13.1974 | 94.8805 | NaN | NaN | NaN | -19.1147 | NaN | NaN | NaN | 34.9809 | 602.1881 | NaN | 28.7381 | NaN | 27.9087
5406.1292 | 13.4772 | 13.1907 | 13.2279 | 13.4647 | 12.8456 | 13.2692 | 13.037 | 12.8492 | NaN | NaN | NaN | 13.2041 | 93.2137 | NaN | NaN | NaN | -13.2597 | NaN | NaN | NaN | 22.4106 | 599.8501 | NaN | 28.2629 | NaN | 28.7867
5407.1292 | 13.5965 | 13.1953 | 13.2327 | 13.4671 | 12.8788 | 13.3904 | 13.0502 | 12.8533 | NaN | NaN | NaN | 13.2249 | 95.6164 | NaN | NaN | NaN | -10.9269 | NaN | NaN | NaN | 22.8004 | 598.8683 | NaN | 26.0796 | NaN | 27.9337
5408.1292 | 13.4349 | 13.3279 | 13.2304 | 13.4801 | 12.8703 | 13.3394 | 13.0715 | 12.8534 | NaN | NaN | NaN | 13.1995 | 98.4682 | NaN | NaN | NaN | 6.5434 | NaN | NaN | NaN | 23.5627 | 598.1002 | NaN | 27.9062 | NaN | 28.3297
5409.1292 | 13.4241 | 13.221 | 13.2422 | 13.7625 | 12.769 | 13.3026 | 13.0631 | 12.8552 | NaN | NaN | NaN | 13.1798 | 93.3914 | NaN | NaN | NaN | -15.9394 | NaN | NaN | NaN | 36.9353 | 598.8748 | NaN | 27.915 | NaN | 27.1566
5410.1292 | 13.4644 | 13.46 | 13.2406 | 13.4824 | 12.9096 | 13.274 | 13.1182 | 12.8462 | NaN | NaN | NaN | 13.2793 | 92.2813 | NaN | NaN | NaN | 12.7514 | NaN | NaN | NaN | 22.6244 | 598.1607 | NaN | 27.6804 | NaN | 27.3714
5411.1292 | 13.6344 | 13.2342 | 13.2427 | 13.439 | 12.9482 | 13.2647 | 13.0552 | 12.8547 | NaN | NaN | NaN | 13.2981 | 90.372 | NaN | NaN | NaN | 38.3606 | NaN | NaN | NaN | 28.3642 | 596.8496 | NaN | 25.9963 | NaN | 27.3117
5412.1292 | 13.4283 | 13.3309 | 13.2441 | 13.586 | 12.8343 | 13.2961 | 13.068 | 12.858 | NaN | NaN | NaN | 13.2802 | 92.2009 | NaN | NaN | NaN | -13.8202 | NaN | NaN | NaN | 26.108 | 598.9309 | NaN | 25.5748 | NaN | 29.2272
5413.1292 | 13.464 | 13.1787 | 13.2421 | 13.5366 | 12.8052 | 13.2555 | 13.041 | 12.856 | NaN | NaN | NaN | 13.2513 | 93.3616 | NaN | NaN | NaN | 1.6298 | NaN | NaN | NaN | 41.1213 | 600.6452 | NaN | 27.2943 | NaN | 28.7448
5414.1292 | 13.4209 | 13.1909 | 13.2448 | 13.4398 | 12.8801 | 13.449 | 13.0367 | 12.8541 | NaN | NaN | NaN | 13.2413 | 100.5838 | NaN | NaN | NaN | 7.1463 | NaN | NaN | NaN | 18.6356 | 596.0613 | NaN | 28.0502 | NaN | 28.3114
5415.1292 | 13.486 | 13.2391 | 13.2474 | 13.5466 | 12.9696 | 13.365 | 13.0611 | 12.8484 | NaN | NaN | NaN | 13.18 | 90.356 | NaN | NaN | NaN | 11.4833 | NaN | NaN | NaN | 22.7729 | 597.8919 | NaN | 26.6508 | NaN | 28.6073
5416.1292 | 13.6744 | 13.1676 | 13.2448 | 13.4561 | 12.899 | 13.325 | 13.0234 | 12.8508 | NaN | NaN | NaN | 13.1833 | 90.1519 | NaN | NaN | NaN | 2.1152 | NaN | NaN | NaN | 26.0889 | 596.3927 | NaN | 26.956 | NaN | 28.2573
5417.1292 | 13.5342 | 13.2853 | 13.2515 | 13.7347 | 12.993 | 13.2663 | 13.0861 | 12.8484 | NaN | NaN | NaN | 13.3171 | 91.9858 | NaN | NaN | NaN | 21.1721 | NaN | NaN | NaN | 25.428 | 597.7412 | NaN | 27.6576 | NaN | 29.6816
5418.1292 | 13.4654 | 13.2338 | 13.2497 | 13.4605 | 12.8858 | 13.3294 | 13.0591 | 12.8546 | NaN | NaN | NaN | 13.2231 | 91.2554 | NaN | NaN | NaN | 23.3314 | NaN | NaN | NaN | 30.3875 | 599.1308 | NaN | 27.3349 | NaN | 28.4387
5419.1292 | 13.4707 | 13.348 | 13.245 | 13.4961 | 12.8625 | 13.2861 | 13.0976 | 12.8558 | NaN | NaN | NaN | 13.3865 | 91.5752 | NaN | NaN | NaN | -1.9061 | NaN | NaN | NaN | 29.164 | 600.7283 | NaN | 25.4572 | NaN | 28.0069
5420.1292 | 13.4933 | 13.2173 | 13.2523 | 13.5406 | 12.9222 | 13.3129 | 13.061 | 12.8531 | NaN | NaN | NaN | 13.2049 | 93.255 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 31.4029 | 601.3317 | NaN | 26.5167 | NaN | 29.2426
5421.1292 | 13.4433 | 13.2092 | 13.2519 | 13.5125 | 12.834 | 13.5823 | 13.0684 | 12.8486 | NaN | NaN | NaN | 13.2651 | 95.2039 | NaN | NaN | NaN | -14.7884 | NaN | NaN | NaN | 23.4159 | 600.0243 | NaN | 26.9345 | NaN | 28.9319
5422.1292 | 13.4655 | 13.1525 | 13.2488 | 13.5271 | 12.8718 | 13.2646 | 13.0415 | 12.8496 | NaN | NaN | NaN | 13.1976 | 94.615 | NaN | NaN | NaN | 40.3575 | NaN | NaN | NaN | 25.9433 | 600.2374 | NaN | 26.559 | NaN | 29.2724
5423.1292 | 13.492 | 13.1981 | 13.2637 | 13.6938 | 12.8716 | 13.2396 | 13.0531 | 12.8437 | NaN | NaN | NaN | 13.2285 | 96.9974 | NaN | NaN | NaN | 4.6036 | NaN | NaN | NaN | 23.9511 | 599.033 | NaN | 26.3751 | NaN | 28.6142
5424.1292 | 13.5576 | 13.1955 | 13.2648 | 13.4823 | 12.8766 | 13.2696 | 13.0599 | 12.8487 | NaN | NaN | NaN | 13.3236 | 97.2694 | NaN | NaN | NaN | 19.565 | NaN | NaN | NaN | 21.2675 | 598.2939 | NaN | 27.8488 | NaN | 28.4687
5425.1292 | 13.5095 | 13.1894 | 13.2604 | 13.5291 | 12.9986 | 13.2328 | 13.0462 | 12.8541 | NaN | NaN | NaN | 13.2794 | 96.8209 | NaN | NaN | NaN | -11.5668 | NaN | NaN | NaN | 23.686 | 600.5479 | NaN | 25.3948 | NaN | 28.2235
5426.1292 | 13.6069 | 13.2536 | 13.266 | 13.4835 | 12.7701 | 13.3097 | 13.0713 | 12.8558 | NaN | NaN | NaN | 13.2597 | 93.5527 | NaN | NaN | NaN | 36.385 | NaN | NaN | NaN | 23.7889 | 598.3723 | NaN | 27.0244 | NaN | 28.0811
5427.1292 | 13.4967 | 13.2223 | 13.2719 | 13.6264 | 12.9378 | 13.3189 | 13.0548 | 12.8555 | NaN | NaN | NaN | 13.303 | 91.7713 | NaN | NaN | NaN | 0.6606 | NaN | NaN | NaN | 33.0022 | 602.1493 | NaN | 27.2674 | NaN | 27.6289
5428.1292 | 13.5325 | 13.1458 | 13.281 | 13.6258 | 12.914 | 13.2966 | 13.0301 | 12.8544 | NaN | NaN | NaN | 13.2535 | 93.3872 | NaN | NaN | NaN | -16.6352 | NaN | NaN | NaN | 27.2891 | 599.2969 | NaN | 26.7478 | NaN | 29.0531
5429.1292 | 13.4771 | 13.5728 | 13.2731 | 13.4863 | 12.8443 | 13.2676 | 13.1714 | 12.8488 | NaN | NaN | NaN | 13.2462 | 92.0212 | NaN | NaN | NaN | 15.8869 | NaN | NaN | NaN | 47.5792 | 601.4515 | NaN | 26.0481 | NaN | 29.4372
5430.1292 | 13.5075 | 13.1874 | 13.2751 | 13.5495 | 12.9443 | 13.3438 | 13.0604 | 12.8504 | NaN | NaN | NaN | 13.2065 | 93.3529 | NaN | NaN | NaN | 30.3078 | NaN | NaN | NaN | 26.3226 | 602.5844 | NaN | 26.7756 | NaN | 28.3877
5431.1292 | 13.5042 | 13.1724 | 13.2775 | 13.5174 | 12.9945 | 13.2699 | 13.0523 | 12.8575 | NaN | NaN | NaN | 13.2611 | 93.028 | NaN | NaN | NaN | -11.1927 | NaN | NaN | NaN | 24.0619 | 602.5678 | NaN | 28.0924 | NaN | 28.4638
5432.1292 | 13.465 | 13.1447 | 13.2817 | 13.5123 | 12.9138 | 13.3553 | 13.0396 | 12.8575 | NaN | NaN | NaN | 13.248 | 93.4038 | NaN | NaN | NaN | -4.5081 | NaN | NaN | NaN | 22.422 | 599.5852 | NaN | 27.8638 | NaN | 28.914
5433.1292 | 13.5192 | 13.1807 | 13.2825 | 13.4866 | 12.9661 | 13.3615 | 13.0652 | 12.8528 | NaN | NaN | NaN | 13.2025 | 96.4627 | NaN | NaN | NaN | -12.8337 | NaN | NaN | NaN | 26.5636 | 599.9831 | NaN | 26.8396 | NaN | 27.6833
5434.1292 | 13.5321 | 13.1371 | 13.2878 | 13.4685 | 12.8084 | 13.2802 | 13.0471 | 12.8509 | NaN | NaN | NaN | 13.2369 | 96.2145 | NaN | NaN | NaN | 1.5629 | NaN | NaN | NaN | 26.6685 | 601.0986 | NaN | 26.8738 | NaN | 28.9631
5435.1292 | 13.504 | 13.1998 | 13.2782 | 13.4609 | 12.9656 | 13.4143 | 13.0781 | 12.8442 | NaN | NaN | NaN | 13.3184 | 92.1957 | NaN | NaN | NaN | 1.8663 | NaN | NaN | NaN | 25.4118 | 601.1932 | NaN | 26.7037 | NaN | 28.7383
5436.1292 | 13.5522 | 13.121 | 13.2793 | 13.4851 | 12.8292 | 13.4193 | 13.0558 | 12.8476 | NaN | NaN | NaN | 13.2689 | 92.2857 | NaN | NaN | NaN | -13.2608 | NaN | NaN | NaN | 22.273 | 603.6468 | NaN | 26.9142 | NaN | 28.4432
5437.1292 | 13.5251 | 13.1067 | 13.2765 | 13.6062 | 13.0147 | 13.3385 | 13.0546 | 12.8467 | NaN | NaN | NaN | 13.2401 | 93.3738 | NaN | NaN | NaN | -12.8163 | NaN | NaN | NaN | 28.4537 | 606.7988 | NaN | 29.3722 | NaN | 29.5504
5438.1292 | 13.554 | 13.563 | 13.2829 | 13.5266 | 12.8732 | 13.2686 | 13.1429 | 12.8477 | NaN | NaN | NaN | 13.2389 | 89.3296 | NaN | NaN | NaN | 18.1894 | NaN | NaN | NaN | 22.6174 | 611.698 | NaN | 27.9227 | NaN | 29.3486
5439.1292 | 13.5578 | 13.1401 | 13.2829 | 13.4934 | 12.9457 | 13.2777 | 13.0532 | 12.8439 | NaN | NaN | NaN | 13.2382 | 96.0858 | NaN | NaN | NaN | -0.799 | NaN | NaN | NaN | 21.1772 | 601.5635 | NaN | 28.4501 | NaN | 29.313
5440.1292 | 13.5379 | 13.1341 | 13.289 | 13.5272 | 12.8552 | 13.3459 | 13.0481 | 12.8462 | NaN | NaN | NaN | 13.2593 | 93.1494 | NaN | NaN | NaN | -5.5435 | NaN | NaN | NaN | 36.1852 | 597.418 | NaN | 27.4478 | NaN | 27.6332
5441.1292 | 13.4965 | 13.1849 | 13.2898 | 13.5054 | 12.9634 | 13.262 | 13.0694 | 12.8472 | NaN | NaN | NaN | 13.4416 | 94.9377 | NaN | NaN | NaN | -18.575 | NaN | NaN | NaN | 20.7282 | 599.5098 | NaN | 27.0725 | NaN | 27.2866
5442.1292 | 13.5265 | 13.2088 | 13.2946 | 13.5967 | 12.9397 | 13.2364 | 13.0751 | 12.8465 | NaN | NaN | NaN | 13.2656 | 90.9217 | NaN | NaN | NaN | 1.4289 | NaN | NaN | NaN | 40.2816 | 599.1399 | NaN | 26.8161 | NaN | 28.1635
5443.1292 | 13.5823 | 13.4736 | 13.2902 | 13.4624 | 12.8008 | 13.3091 | 13.1149 | 12.8505 | NaN | NaN | NaN | 13.2383 | 92.0115 | NaN | NaN | NaN | 9.8008 | NaN | NaN | NaN | 24.7294 | 598.2879 | NaN | 27.9601 | NaN | 28.3935
5444.1292 | 13.6235 | 13.1963 | 13.2974 | 13.5072 | 12.9922 | 13.3416 | 13.0844 | 12.85 | NaN | NaN | NaN | 13.2565 | 92.9526 | NaN | NaN | NaN | -15.944 | NaN | NaN | NaN | 29.3953 | 597.488 | NaN | 26.6092 | NaN | 28.2998
5445.1292 | 13.5079 | 13.1587 | 13.2958 | 13.4801 | 12.9052 | 13.3467 | 13.0794 | 12.8575 | NaN | NaN | NaN | 13.2293 | 92.1974 | NaN | NaN | NaN | 1.1933 | NaN | NaN | NaN | 27.2707 | 598.9732 | NaN | 26.4602 | NaN | 28.265
5446.1292 | 13.6103 | 13.1667 | 13.3028 | 13.6344 | 12.8492 | 13.2895 | 13.0693 | 12.8566 | NaN | NaN | NaN | 13.388 | 92.7376 | NaN | NaN | NaN | -15.7492 | NaN | NaN | NaN | 34.6425 | 597.4195 | NaN | 28.165 | NaN | 28.7162
5447.1292 | 13.5825 | 13.2748 | 13.3 | 13.6011 | 12.9495 | 13.3578 | 13.0772 | 12.8603 | NaN | NaN | NaN | 13.2572 | 98.0272 | NaN | NaN | NaN | -15.2696 | NaN | NaN | NaN | 13.7465 | 595.3506 | NaN | 22.7509 | NaN | 27.6801
5448.1292 | 13.5585 | 13.1429 | 13.2931 | 13.456 | 12.8066 | 13.4196 | 13.0775 | 12.8603 | NaN | NaN | NaN | 13.2801 | 93.2907 | NaN | NaN | NaN | -17.9402 | NaN | NaN | NaN | 25.6366 | 597.0738 | NaN | 28.5695 | NaN | 28.0872
5449.1292 | 13.6083 | 13.142 | 13.2976 | 13.4844 | 12.9185 | 13.3321 | 13.0591 | 12.8586 | NaN | NaN | NaN | 13.268 | 91.2947 | NaN | NaN | NaN | 1.2374 | NaN | NaN | NaN | 28.7709 | 595.8872 | NaN | 26.0788 | NaN | 26.9723
5450.1292 | 13.8357 | 13.1223 | 13.2923 | 13.4266 | 12.9117 | 13.3193 | 13.0576 | 12.8585 | NaN | NaN | NaN | 13.2993 | 93.9062 | NaN | NaN | NaN | 21.7272 | NaN | NaN | NaN | 24.8424 | 597.7886 | NaN | 27.3395 | NaN | 29.1216
5451.1292 | 13.5022 | 13.1871 | 13.2851 | 13.668 | 12.8391 | 13.407 | 13.0885 | 12.8551 | NaN | NaN | NaN | 13.3036 | 92.6034 | NaN | NaN | NaN | -5.5577 | NaN | NaN | NaN | 24.8799 | 595.4279 | NaN | 26.9442 | NaN | 29.4839
5452.1292 | 13.6939 | 13.1716 | 13.2867 | 13.6513 | 12.8982 | 13.255 | 13.0902 | 12.8575 | NaN | NaN | NaN | 13.2126 | 92.4864 | NaN | NaN | NaN | -12.42 | NaN | NaN | NaN | 28.9191 | 597.7123 | NaN | 25.6938 | NaN | 28.496
5453.1292 | 13.5279 | 13.1264 | 13.2821 | 13.4597 | 12.9132 | 13.3549 | 13.0603 | 12.8583 | NaN | NaN | NaN | 13.2204 | 104.7518 | NaN | NaN | NaN | -7.3533 | NaN | NaN | NaN | 23.3319 | 597.0436 | NaN | 26.1892 | NaN | 28.0346
5454.1292 | 13.5448 | 13.1641 | 13.2752 | 13.438 | 12.9067 | 13.3198 | 13.0817 | 12.8545 | NaN | NaN | NaN | 13.2326 | 92.6534 | NaN | NaN | NaN | -5.2631 | NaN | NaN | NaN | 25.2485 | 598.3556 | NaN | 26.6094 | NaN | 28.154
5455.1292 | 13.547 | 13.2216 | 13.2767 | 13.5337 | 12.9612 | 13.3101 | 13.078 | 12.8543 | NaN | NaN | NaN | 13.2088 | 93.9703 | NaN | NaN | NaN | 33.3216 | NaN | NaN | NaN | 25.7977 | 597.1105 | NaN | 26.1935 | NaN | 27.6968
5456.1292 | 13.525 | 13.1777 | 13.2744 | 13.4674 | 12.9428 | 13.2833 | 13.0746 | 12.8569 | NaN | NaN | NaN | 13.4081 | 95.1488 | NaN | NaN | NaN | -11.1983 | NaN | NaN | NaN | 22.7197 | 597.1035 | NaN | 27.7079 | NaN | 28.6472
5457.1292 | 13.5423 | 13.1563 | 13.2832 | 13.5276 | 12.8835 | 13.2899 | 13.0566 | 12.863 | NaN | NaN | NaN | 13.3415 | 90.008 | NaN | NaN | NaN | 8.193 | NaN | NaN | NaN | 27.9003 | 597.3127 | NaN | 26.4151 | NaN | 28.2831
5458.1292 | 13.6391 | 13.1535 | 13.2861 | 13.4928 | 12.9319 | 13.33 | 13.0521 | 12.8716 | NaN | NaN | NaN | 13.2511 | 96.5484 | NaN | NaN | NaN | 38.1444 | NaN | NaN | NaN | 25.3464 | 597.3522 | NaN | 27.7995 | NaN | 29.1637
5459.1292 | 13.5258 | 13.1811 | 13.2926 | 13.4769 | 12.9271 | 13.2987 | 13.0615 | 12.8724 | NaN | NaN | NaN | 13.2324 | 93.5416 | NaN | NaN | NaN | -4.459 | NaN | NaN | NaN | 18.3699 | 598.506 | NaN | 26.8444 | NaN | 28.9704
5460.1292 | 13.5685 | 13.2865 | 13.2922 | 13.483 | 13.023 | 13.2844 | 13.1109 | 12.8758 | NaN | NaN | NaN | 13.2115 | 97.0483 | NaN | NaN | NaN | -11.553 | NaN | NaN | NaN | 25.4992 | 597.8699 | NaN | 26.9463 | NaN | 27.2918
5461.1292 | 13.5631 | 13.2255 | 13.297 | 13.5014 | 12.9265 | 13.2966 | 13.0859 | 12.8723 | NaN | NaN | NaN | 13.2299 | 90.9705 | NaN | NaN | NaN | -13.0803 | NaN | NaN | NaN | 21.794 | 596.2035 | NaN | 27.2091 | NaN | 27.952
5462.1292 | 13.5375 | 13.2045 | 13.2891 | 13.4534 | 12.9816 | 13.2701 | 13.0661 | 12.8763 | NaN | NaN | NaN | 13.2306 | 95.5555 | NaN | NaN | NaN | -6.4351 | NaN | NaN | NaN | 26.874 | 597.0252 | NaN | 27.0032 | NaN | 27.9
5463.1292 | 13.5253 | 13.1985 | 13.2884 | 13.5096 | 12.9083 | 13.3755 | 13.0589 | 12.8763 | NaN | NaN | NaN | 13.2272 | 92.6954 | NaN | NaN | NaN | -1.9435 | NaN | NaN | NaN | 19.7362 | 596.4867 | NaN | 26.4415 | NaN | 27.2691
5464.1292 | 13.6022 | 13.1938 | 13.2925 | 13.4842 | 12.8401 | 13.2797 | 13.0649 | 12.883 | NaN | NaN | NaN | 13.1979 | 94.8873 | NaN | NaN | NaN | -6.5276 | NaN | NaN | NaN | 22.806 | 596.5347 | NaN | 26.5753 | NaN | 26.6711
5465.1292 | 13.5865 | 13.1526 | 13.2949 | 13.5031 | 12.9473 | 13.2964 | 13.05 | 12.8795 | NaN | NaN | NaN | 13.2118 | 91.8948 | NaN | NaN | NaN | -17.132 | NaN | NaN | NaN | 24.4686 | 596.3415 | NaN | 28.0027 | NaN | 28.8576
5466.1292 | 13.819 | 13.278 | 13.2983 | 13.5434 | 12.7986 | 13.2948 | 13.1046 | 12.8755 | NaN | NaN | NaN | 13.3287 | 94.3082 | NaN | NaN | NaN | -17.1455 | NaN | NaN | NaN | 27.5837 | 595.4064 | NaN | 26.1018 | NaN | 26.2756
5467.1292 | 13.5552 | 13.2095 | 13.2937 | 13.5116 | 12.9613 | 13.3572 | 13.0888 | 12.878 | NaN | NaN | NaN | 13.2959 | 97.5639 | NaN | NaN | NaN | -14.8699 | NaN | NaN | NaN | 27.0208 | 595.7653 | NaN | 27.8412 | NaN | 27.3314
5468.1292 | 13.5689 | 13.1794 | 13.3031 | 13.5129 | 13.0065 | 13.2896 | 13.0791 | 12.8798 | NaN | NaN | NaN | 13.2495 | 93.3416 | NaN | NaN | NaN | -17.4777 | NaN | NaN | NaN | 27.0317 | 598.6748 | NaN | 26.9743 | NaN | 25.878
5469.1292 | 13.5803 | 13.2174 | 13.2987 | 13.5038 | 12.9296 | 13.393 | 13.1045 | 12.874 | NaN | NaN | NaN | 13.243 | 104.8012 | NaN | NaN | NaN | -4.6005 | NaN | NaN | NaN | 27.3363 | 597.1073 | NaN | 27.1108 | NaN | 28.8277
5470.1292 | 13.6555 | 13.2158 | 13.3055 | 13.4636 | 12.9547 | 13.3442 | 13.1049 | 12.8843 | NaN | NaN | NaN | 13.3137 | 95.1573 | NaN | NaN | NaN | -11.0587 | NaN | NaN | NaN | 26.9721 | 597.9257 | NaN | 26.5533 | NaN | 28.1985
5471.1292 | 13.588 | 13.1443 | 13.3117 | 13.476 | 12.9719 | 13.3967 | 13.0772 | 12.8834 | NaN | NaN | NaN | 13.3559 | 92.2142 | NaN | NaN | NaN | -2.8963 | NaN | NaN | NaN | 22.6952 | 597.542 | NaN | 27.2365 | NaN | 28.5931
5472.1292 | 13.6002 | 13.1918 | 13.3146 | 13.4772 | 12.9321 | 13.3032 | 13.0994 | 12.8825 | NaN | NaN | NaN | 13.2653 | 93.2995 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 25.8552 | 599.0804 | NaN | 27.7822 | NaN | 27.2199
5473.1292 | 13.5871 | 13.2031 | 13.3165 | 13.4892 | 12.8964 | 13.351 | 13.0954 | 12.8813 | NaN | NaN | NaN | 13.2938 | 92.5638 | NaN | NaN | NaN | -12.8779 | NaN | NaN | NaN | 23.0219 | 596.8199 | NaN | 26.3736 | NaN | 28.2452
5474.1292 | 13.5177 | 13.3857 | 13.3077 | 13.5302 | 12.8901 | 13.4137 | 13.1271 | 12.8861 | NaN | NaN | NaN | 13.4056 | 99.9093 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 39.7358 | 596.2692 | NaN | 26.5385 | NaN | 27.099
5475.1292 | 13.6413 | 13.1361 | 13.3092 | 13.7452 | 13.0574 | 13.2766 | 13.063 | 12.8852 | NaN | NaN | NaN | 13.2902 | 95.1404 | NaN | NaN | NaN | 31.5251 | NaN | NaN | NaN | 34.5608 | 597.6451 | NaN | 24.844 | NaN | 28.0865
5476.1292 | 13.5322 | 13.3556 | 13.3058 | 13.8605 | 12.9951 | 13.3805 | 13.1211 | 12.8796 | NaN | NaN | NaN | 13.3619 | 94.6231 | NaN | NaN | NaN | -15.5314 | NaN | NaN | NaN | 44.9995 | 596.4956 | NaN | 24.3317 | NaN | 26.5319
5477.1292 | 13.5748 | 13.1585 | 13.3047 | 13.5953 | 12.9112 | 13.2907 | 13.0659 | 12.8888 | NaN | NaN | NaN | 13.2812 | 93.7102 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 30.0023 | 597.5632 | NaN | 26.8249 | NaN | 27.8614
5478.1292 | 13.5699 | 13.6271 | 13.2883 | 13.5885 | 13.0885 | 13.3661 | 13.1767 | 12.8841 | NaN | NaN | NaN | 13.3478 | 90.3406 | NaN | NaN | NaN | 0.2555 | NaN | NaN | NaN | 31.8276 | 596.1628 | NaN | 27.1153 | NaN | 28.3803
5479.1292 | 13.5981 | 13.2283 | 13.2912 | 13.6002 | 12.8789 | 13.3405 | 13.1033 | 12.8835 | NaN | NaN | NaN | 13.377 | 98.3668 | NaN | NaN | NaN | -3.0344 | NaN | NaN | NaN | 34.2037 | 597.671 | NaN | 25.9997 | NaN | 27.9339
5480.1292 | 13.5727 | 13.1531 | 13.2997 | 13.5511 | 12.8948 | 13.3542 | 13.0786 | 12.887 | NaN | NaN | NaN | 13.2815 | 93.0099 | NaN | NaN | NaN | -19.391 | NaN | NaN | NaN | 24.5532 | 598.4828 | NaN | 25.9607 | NaN | 28.6915
5481.1292 | 13.5299 | 13.1582 | 13.2972 | 13.555 | 12.9579 | 13.2944 | 13.0861 | 12.8832 | NaN | NaN | NaN | 13.5902 | 92.9899 | NaN | NaN | NaN | 11.2912 | NaN | NaN | NaN | 22.1088 | 599.3086 | NaN | 28.0883 | NaN | 26.8135
5482.1292 | 13.5356 | 13.3344 | 13.3041 | 13.8651 | 12.9288 | 13.3125 | 13.1157 | 12.8863 | NaN | NaN | NaN | 13.3126 | 91.554 | NaN | NaN | NaN | 5.1575 | NaN | NaN | NaN | 33.6268 | 597.7284 | NaN | 25.9631 | NaN | 28.0914
5483.1292 | 13.5504 | 13.1893 | 13.3087 | 13.5815 | 12.9541 | 13.4667 | 13.1052 | 12.8835 | NaN | NaN | NaN | 13.3143 | 92.1607 | NaN | NaN | NaN | 6.1838 | NaN | NaN | NaN | 32.2933 | 598.679 | NaN | 25.857 | NaN | 27.0726
5484.1292 | 13.5642 | 13.1694 | 13.3124 | 13.5675 | 13.0053 | 13.3554 | 13.0956 | 12.8915 | NaN | NaN | NaN | 13.3116 | 95.898 | NaN | NaN | NaN | -9.184 | NaN | NaN | NaN | 30.3043 | 599.7636 | NaN | 26.8203 | NaN | 27.7788
5485.1292 | 13.5704 | 13.1823 | 13.3119 | 13.5282 | 13.0249 | 13.297 | 13.0999 | 12.8929 | NaN | NaN | NaN | 13.3695 | 91.4944 | NaN | NaN | NaN | -16.7932 | NaN | NaN | NaN | 25.2448 | 601.6189 | NaN | 27.1411 | NaN | 28.6541
5486.1292 | 13.5512 | 13.3288 | 13.3126 | 13.5298 | 12.8547 | 13.2995 | 13.1318 | 12.8998 | NaN | NaN | NaN | 13.3167 | 93.5006 | NaN | NaN | NaN | -8.7972 | NaN | NaN | NaN | 27.2133 | 597.9463 | NaN | 25.0054 | NaN | 28.3254
5487.1292 | 13.6689 | 13.2391 | 13.3154 | 13.494 | 13.0035 | 13.3999 | 13.1272 | 12.8837 | NaN | NaN | NaN | 13.4078 | 94.4668 | NaN | NaN | NaN | 13.1312 | NaN | NaN | NaN | 18.822 | 598.5906 | NaN | 26.208 | NaN | 28.7627
5488.1292 | 13.5345 | 13.192 | 13.3083 | 13.5198 | 12.9669 | 13.3685 | 13.1115 | 12.8946 | NaN | NaN | NaN | 13.2729 | 91.7237 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 24.3027 | 598.4333 | NaN | 25.7704 | NaN | 27.1163
5489.1292 | 13.587 | 13.2492 | 13.3178 | 13.5615 | 13.0639 | 13.3907 | 13.1311 | 12.8941 | NaN | NaN | NaN | 13.3337 | 95.5378 | NaN | NaN | NaN | -9.578 | NaN | NaN | NaN | 23.6739 | 598.3626 | NaN | 26.5013 | NaN | 29.8724
5490.1292 | 13.6204 | 13.1621 | 13.3231 | 13.5801 | 13.0274 | 13.352 | 13.1091 | 12.8902 | NaN | NaN | NaN | 13.3036 | 90.8172 | NaN | NaN | NaN | -17.1827 | NaN | NaN | NaN | 25.7782 | 597.4403 | NaN | 25.9397 | NaN | 29.0944
5491.1292 | 13.5406 | 13.2417 | 13.3163 | 13.5466 | 13.0739 | 13.3448 | 13.1305 | 12.8949 | NaN | NaN | NaN | 13.3403 | 91.9263 | NaN | NaN | NaN | -11.3824 | NaN | NaN | NaN | 35.7044 | 597.3214 | NaN | 27.3901 | NaN | 25.9202
5492.1292 | 13.6948 | 13.1927 | 13.3255 | 13.4948 | 12.9335 | 13.3399 | 13.097 | 12.8939 | NaN | NaN | NaN | 13.2574 | 93.2859 | NaN | NaN | NaN | -17.5024 | NaN | NaN | NaN | 22.433 | 599.4516 | NaN | 27.4112 | NaN | 27.9964
5493.1292 | 13.6615 | 13.1849 | 13.3208 | 13.5128 | 12.9596 | 13.319 | 13.1052 | 12.894 | NaN | NaN | NaN | 13.2985 | 96.5357 | NaN | NaN | NaN | -15.4837 | NaN | NaN | NaN | 21.9218 | 596.4075 | NaN | 25.1709 | NaN | 30.0966
5494.1292 | 13.628 | 13.1722 | 13.3212 | 13.5796 | 13.0575 | 13.4212 | 13.0908 | 12.8969 | NaN | NaN | NaN | 13.3437 | 94.0464 | NaN | NaN | NaN | -11.3122 | NaN | NaN | NaN | 12.6456 | 593.4708 | NaN | 25.5848 | NaN | 25.7397
5495.1292 | 13.6888 | 13.1526 | 13.3335 | 13.647 | 12.9298 | 13.3913 | 13.0876 | 12.8907 | NaN | NaN | NaN | 13.2518 | 94.4069 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 25.9863 | 596.5688 | NaN | 27.66 | NaN | 27.4752
5496.1292 | 13.6064 | 13.2193 | 13.332 | 13.5285 | 13.0085 | 13.2918 | 13.0926 | 12.9035 | NaN | NaN | NaN | 13.3839 | 92.902 | NaN | NaN | NaN | -17.796 | NaN | NaN | NaN | 21.2876 | 596.4335 | NaN | 25.3485 | NaN | 27.8938
5497.1292 | 13.6099 | 13.1979 | 13.335 | 13.5339 | 13.0752 | 13.3081 | 13.092 | 12.9019 | NaN | NaN | NaN | 13.483 | 94.7784 | NaN | NaN | NaN | 0.8243 | NaN | NaN | NaN | 34.9092 | 595.432 | NaN | 24.7148 | NaN | 27.9201
5498.1292 | 13.5679 | 13.2196 | 13.3369 | 13.506 | 12.8292 | 13.3625 | 13.1029 | 12.9003 | NaN | NaN | NaN | 13.2865 | 92.7956 | NaN | NaN | NaN | -15.3732 | NaN | NaN | NaN | 37.4002 | 594.1658 | NaN | 24.7264 | NaN | 28.1391
5499.1292 | 13.6825 | 13.1701 | 13.3363 | 13.5211 | 12.9378 | 13.3676 | 13.0751 | 12.9011 | NaN | NaN | NaN | 13.2444 | 92.9823 | NaN | NaN | NaN | -0.586 | NaN | NaN | NaN | 22.2027 | 593.4299 | NaN | 26.9411 | NaN | 27.8799
5500.1292 | 13.5342 | 13.1744 | 13.3446 | 13.5468 | 12.951 | 13.4991 | 13.0916 | 12.9028 | NaN | NaN | NaN | 13.4003 | 93.3211 | NaN | NaN | NaN | 17.9581 | NaN | NaN | NaN | 24.4866 | 592.1758 | NaN | 26.4996 | NaN | 27.2425
5501.1292 | 13.5298 | 13.2359 | 13.342 | 13.5389 | 12.9409 | 13.3588 | 13.1058 | 12.9051 | NaN | NaN | NaN | 13.3166 | 93.5557 | NaN | NaN | NaN | -3.8574 | NaN | NaN | NaN | 22.6433 | 591.4279 | NaN | 26.2461 | NaN | 29.2262
5502.1292 | 13.5922 | 13.2055 | 13.3409 | 13.6313 | 13.0544 | 13.3038 | 13.101 | 12.9043 | NaN | NaN | NaN | 13.2953 | 95.9903 | NaN | NaN | NaN | -2.8385 | NaN | NaN | NaN | 25.7929 | 593.3667 | NaN | 26.5955 | NaN | 28.0757
5503.1292 | 13.6758 | 13.2329 | 13.3478 | 13.507 | 12.9579 | 13.3677 | 13.1207 | 12.9014 | NaN | NaN | NaN | 13.2742 | 93.6319 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 49.1413 | 595.1612 | NaN | 27.6612 | NaN | 27.9157
5504.1292 | 13.6728 | 13.2081 | 13.3516 | 13.5352 | 12.9567 | 13.4209 | 13.0888 | 12.9059 | NaN | NaN | NaN | 13.4381 | 93.3838 | NaN | NaN | NaN | -2.0383 | NaN | NaN | NaN | 19.3078 | 594.4572 | NaN | 24.8002 | NaN | 26.1981
5505.1292 | 13.5957 | 13.6196 | 13.3482 | 13.4875 | 12.8327 | 13.4135 | 13.1727 | 12.905 | NaN | NaN | NaN | 13.2912 | 94.2844 | NaN | NaN | NaN | -5.2042 | NaN | NaN | NaN | 30.0206 | 595.5606 | NaN | 22.6844 | NaN | 28.8606
5506.1292 | 13.5748 | 13.2096 | 13.3483 | 13.5636 | 12.9558 | 13.3334 | 13.1034 | 12.8971 | NaN | NaN | NaN | 13.3792 | 93.7312 | NaN | NaN | NaN | -11.4613 | NaN | NaN | NaN | 20.5342 | 594.8427 | NaN | 26.0168 | NaN | 27.892
5507.1292 | 13.5838 | 13.2183 | 13.3499 | 13.5347 | 13.0602 | 13.3607 | 13.0952 | 12.8997 | NaN | NaN | NaN | 13.3333 | 93.9563 | NaN | NaN | NaN | 52.0086 | NaN | NaN | NaN | 18.975 | 593.8471 | NaN | 27.6736 | NaN | 27.1595
5508.1292 | 13.5867 | 13.174 | 13.3554 | 13.4978 | 13.0157 | 13.3427 | 13.0881 | 12.8909 | NaN | NaN | NaN | 13.2941 | 89.6154 | NaN | NaN | NaN | 9.7589 | NaN | NaN | NaN | 23.3114 | 595.1936 | NaN | 27.6235 | NaN | 27.9834
5509.1292 | 13.5868 | 13.2461 | 13.3484 | 13.5241 | 13.0003 | 13.3218 | 13.1127 | 12.8848 | NaN | NaN | NaN | 13.3442 | 93.8809 | NaN | NaN | NaN | -0.6435 | NaN | NaN | NaN | 22.8295 | 595.4849 | NaN | 27.4588 | NaN | 28.1935
5510.1292 | 13.6249 | 13.2303 | 13.3483 | 13.5026 | 13.0232 | 13.3609 | 13.1022 | 12.8891 | NaN | NaN | NaN | 13.3752 | 92.7804 | NaN | NaN | NaN | -13.7822 | NaN | NaN | NaN | 21.49 | 594.5458 | NaN | 25.4209 | NaN | 26.7039
5511.1292 | 13.5906 | 13.1756 | 13.3527 | 13.7034 | 13.0444 | 13.5133 | 13.0861 | 12.8884 | NaN | NaN | NaN | 13.3762 | 95.2756 | NaN | NaN | NaN | -5.4279 | NaN | NaN | NaN | 17.8844 | 593.0754 | NaN | 27.2995 | NaN | 28.5185
5512.1292 | 13.5643 | 13.1605 | 13.344 | 13.5136 | 12.8979 | 13.3752 | 13.0948 | 12.8905 | NaN | NaN | NaN | 13.287 | 94.6495 | NaN | NaN | NaN | 16.8125 | NaN | NaN | NaN | 23.781 | 594.7571 | NaN | 27.4086 | NaN | 26.076
5513.1292 | 13.5611 | 13.1666 | 13.3444 | 13.5497 | 12.987 | 13.3245 | 13.0935 | 12.8942 | NaN | NaN | NaN | 13.3884 | 95.5917 | NaN | NaN | NaN | 48.3007 | NaN | NaN | NaN | 28.0017 | 596.8659 | NaN | 26.425 | NaN | 27.474
5514.1292 | 13.5491 | 13.1903 | 13.3503 | 13.5835 | 13.0511 | 13.3191 | 13.1063 | 12.8967 | NaN | NaN | NaN | 13.3387 | 92.6594 | NaN | NaN | NaN | -6.4932 | NaN | NaN | NaN | 23.5819 | 595.7026 | NaN | 25.9671 | NaN | 28.1255
5515.1292 | 13.5328 | 13.2033 | 13.348 | 13.5528 | 12.9424 | 13.3436 | 13.1028 | 12.8933 | NaN | NaN | NaN | 13.3086 | 96.5632 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 22.6089 | 593.9664 | NaN | 26.2528 | NaN | 27.7287
5516.1292 | 13.5602 | 13.2913 | 13.3432 | 13.6579 | 13.0796 | 13.2868 | 13.1197 | 12.898 | NaN | NaN | NaN | 13.3228 | 90.2303 | NaN | NaN | NaN | 7.6605 | NaN | NaN | NaN | 24.8583 | 594.396 | NaN | 24.1608 | NaN | 28.1774
5517.1292 | 13.5839 | 13.1665 | 13.3493 | 13.5565 | 13.0258 | 13.327 | 13.0994 | 12.8974 | NaN | NaN | NaN | 13.421 | 93.0928 | NaN | NaN | NaN | 1.1973 | NaN | NaN | NaN | 24.9605 | 591.371 | NaN | 25.4876 | NaN | 27.6621
5518.1292 | 13.6321 | 13.2302 | 13.3522 | 13.5246 | 13.0185 | 13.3218 | 13.1195 | 12.9025 | NaN | NaN | NaN | 13.3044 | 93.2537 | NaN | NaN | NaN | -18.7039 | NaN | NaN | NaN | 27.814 | 596.3904 | NaN | 26.188 | NaN | 27.93
5519.1292 | 13.563 | 13.1663 | 13.3527 | 13.5685 | 12.9671 | 13.5133 | 13.1087 | 12.9058 | NaN | NaN | NaN | 13.3125 | 92.1233 | NaN | NaN | NaN | 3.0576 | NaN | NaN | NaN | 23.347 | 598.0969 | NaN | 26.2161 | NaN | 27.0282
5520.1292 | 13.5622 | 13.2034 | 13.3567 | 13.7984 | 12.9174 | 13.4107 | 13.1132 | 12.9033 | NaN | NaN | NaN | 13.3547 | 91.9431 | NaN | NaN | NaN | -10.6621 | NaN | NaN | NaN | 24.4225 | 598.8482 | NaN | 27.1879 | NaN | 29.0475
5521.1292 | 13.549 | 13.1752 | 13.3645 | 13.5173 | 12.9281 | 13.3803 | 13.1057 | 12.9102 | NaN | NaN | NaN | 13.3849 | 92.5811 | NaN | NaN | NaN | -18.1362 | NaN | NaN | NaN | 24.953 | 598.6505 | NaN | 25.1646 | NaN | 28.4837
5522.1292 | 13.5386 | 13.3083 | 13.3562 | 13.5563 | 12.9378 | 13.3335 | 13.1366 | 12.9075 | NaN | NaN | NaN | 13.3466 | 90.783 | NaN | NaN | NaN | 2.6898 | NaN | NaN | NaN | 35.2778 | 596.7053 | NaN | 25.7785 | NaN | 28.5293
5523.1292 | 13.62 | 13.1861 | 13.3553 | 13.605 | 12.9925 | 13.3244 | 13.1075 | 12.9106 | NaN | NaN | NaN | 13.2901 | 92.5679 | NaN | NaN | NaN | -18.6518 | NaN | NaN | NaN | 33.6295 | 597.1904 | NaN | 26.4632 | NaN | 26.5436
5524.1292 | 13.6281 | 13.1706 | 13.3591 | 13.6092 | 13.0807 | 13.3037 | 13.0956 | 12.913 | NaN | NaN | NaN | 13.3159 | 95.7794 | NaN | NaN | NaN | 6.1402 | NaN | NaN | NaN | 25.2202 | 593.8325 | NaN | 24.8734 | NaN | 28.8904
5525.1292 | 13.5547 | 13.1852 | 13.3583 | 13.5373 | 12.9372 | 13.3157 | 13.1105 | 12.919 | NaN | NaN | NaN | 13.3467 | 94.9603 | NaN | NaN | NaN | -1.6797 | NaN | NaN | NaN | 31.4943 | 595.2682 | NaN | 27.4538 | NaN | 29.378
5526.1292 | 13.7061 | 13.2312 | 13.3547 | 13.5366 | 13.0028 | 13.3212 | 13.1138 | 12.9212 | NaN | NaN | NaN | 13.4009 | 94.2985 | NaN | NaN | NaN | 46.2195 | NaN | NaN | NaN | 24.189 | 596.3625 | NaN | 25.8428 | NaN | 26.0535
5527.1292 | 13.5803 | 13.1874 | 13.3607 | 13.55 | 13.0496 | 13.3785 | 13.1141 | 12.9272 | NaN | NaN | NaN | 13.3086 | 95.2752 | NaN | NaN | NaN | -16.9704 | NaN | NaN | NaN | 31.1688 | 594.8167 | NaN | 24.9397 | NaN | 27.4427
5528.1292 | 13.5466 | 13.1547 | 13.3614 | 13.5686 | 13.0171 | 13.4683 | 13.0852 | 12.9267 | NaN | NaN | NaN | 13.3024 | 90.1954 | NaN | NaN | NaN | -19.5914 | NaN | NaN | NaN | 21.1966 | 594.6686 | NaN | 26.296 | NaN | 28.2273
5529.1292 | 13.5188 | 13.1834 | 13.3557 | 13.5729 | 12.9785 | 13.3513 | 13.122 | 12.9241 | NaN | NaN | NaN | 13.3611 | 94.0743 | NaN | NaN | NaN | -0.4126 | NaN | NaN | NaN | 20.0275 | 595.906 | NaN | 24.776 | NaN | 28.6797
5530.1292 | 13.7308 | 13.1924 | 13.3576 | 13.5958 | 12.9409 | 13.4501 | 13.1113 | 12.9241 | NaN | NaN | NaN | 13.3542 | 92.1387 | NaN | NaN | NaN | 18.0686 | NaN | NaN | NaN | 59.7333 | 593.773 | NaN | 26.5412 | NaN | 27.0114
5531.1292 | 13.6435 | 13.2139 | 13.3545 | 13.6151 | 12.9823 | 13.4372 | 13.116 | 12.9234 | NaN | NaN | NaN | 13.3179 | 91.1647 | NaN | NaN | NaN | -9.5172 | NaN | NaN | NaN | 22.3084 | 595.7261 | NaN | 24.1226 | NaN | 26.6753
5532.1292 | 13.5566 | 13.1661 | 13.3547 | 13.5936 | 12.9851 | 13.3388 | 13.1081 | 12.9307 | NaN | NaN | NaN | 13.3074 | 93.0887 | NaN | NaN | NaN | 16.8777 | NaN | NaN | NaN | 34.5772 | 597.7336 | NaN | 27.1008 | NaN | 26.5807
5533.1292 | 13.6415 | 13.2241 | 13.3562 | 13.5741 | 12.9439 | 13.3429 | 13.1198 | 12.9327 | NaN | NaN | NaN | 13.4276 | 92.0091 | NaN | NaN | NaN | 1.4326 | NaN | NaN | NaN | 24.7155 | 595.7129 | NaN | 24.8924 | NaN | 29.3907
5534.1292 | 13.509 | 13.2518 | 13.36 | 13.6034 | 12.8881 | 13.4963 | 13.1384 | 12.937 | NaN | NaN | NaN | 13.3496 | 97.0696 | NaN | NaN | NaN | 8.1037 | NaN | NaN | NaN | 26.3619 | 596.2437 | NaN | 26.6032 | NaN | 27.4993
5535.1292 | 13.5191 | 13.1815 | 13.3648 | 13.5978 | 13.007 | 13.3642 | 13.1192 | 12.9313 | NaN | NaN | NaN | 13.348 | 91.8617 | NaN | NaN | NaN | -18.0428 | NaN | NaN | NaN | 18.836 | 597.5402 | NaN | 24.9171 | NaN | 26.9053
5536.1292 | 13.5152 | 13.1712 | 13.3638 | 13.5932 | 13.0906 | 13.3799 | 13.1248 | 12.9401 | NaN | NaN | NaN | 13.4167 | 92.2797 | NaN | NaN | NaN | -2.7811 | NaN | NaN | NaN | 19.0375 | 595.5183 | NaN | 27.7454 | NaN | 28.7861
5537.1292 | 13.5619 | 13.1914 | 13.3526 | 13.6571 | 13.0766 | 13.3258 | 13.1363 | 12.9365 | NaN | NaN | NaN | 13.3454 | 91.3795 | NaN | NaN | NaN | 14.6927 | NaN | NaN | NaN | 23.3211 | 597.7373 | NaN | 25.5458 | NaN | 27.9231
5538.1292 | 13.6532 | 13.1499 | 13.3537 | 13.6005 | 12.9822 | 13.3202 | 13.1154 | 12.9459 | NaN | NaN | NaN | 13.3491 | 91.7261 | NaN | NaN | NaN | 12.0005 | NaN | NaN | NaN | 27.3708 | 598.7068 | NaN | 25.3327 | NaN | 26.7401
5539.1292 | 13.6096 | 13.1495 | 13.3538 | 13.7047 | 13.0377 | 13.3826 | 13.1225 | 12.936 | NaN | NaN | NaN | 13.3582 | 92.5616 | NaN | NaN | NaN | 1.9051 | NaN | NaN | NaN | 31.1101 | 596.132 | NaN | 26.8747 | NaN | 28.1998
5540.1292 | 13.5527 | 13.1967 | 13.3517 | 13.6392 | 13.1069 | 13.4069 | 13.1437 | 12.9418 | NaN | NaN | NaN | 13.3311 | 82.4147 | NaN | NaN | NaN | 22.3406 | NaN | NaN | NaN | 26.183 | 595.1053 | NaN | 24.9688 | NaN | 28.7821
5541.1292 | 13.5728 | 13.2303 | 13.3554 | 13.6282 | 13.0913 | 13.3369 | 13.1513 | 12.9429 | NaN | NaN | NaN | 13.3629 | 94.4164 | NaN | NaN | NaN | -11.6503 | NaN | NaN | NaN | 31.6407 | 596.5834 | NaN | 28.2389 | NaN | 28.346
5542.1292 | 13.5465 | 13.1908 | 13.3596 | 13.5792 | 12.9729 | 13.3624 | 13.1493 | 12.9473 | NaN | NaN | NaN | 13.3958 | 97.3517 | NaN | NaN | NaN | -1.1147 | NaN | NaN | NaN | 24.2031 | 594.8338 | NaN | 26.4478 | NaN | 27.6763
5543.1292 | 13.5671 | 13.2186 | 13.3533 | 13.5888 | 13.0388 | 13.3412 | 13.1417 | 12.9474 | NaN | NaN | NaN | 13.3737 | 95.7058 | NaN | NaN | NaN | 28.5108 | NaN | NaN | NaN | 28.2252 | 594.0823 | NaN | 25.9462 | NaN | 28.4779
5544.1292 | 13.5778 | 13.2963 | 13.3523 | 13.7256 | 13.0887 | 13.4235 | 13.1663 | 12.946 | NaN | NaN | NaN | 13.5139 | 92.8574 | NaN | NaN | NaN | 3.5472 | NaN | NaN | NaN | 24.6482 | 593.2064 | NaN | 28.4888 | NaN | 28.3736
5545.1292 | 13.5451 | 13.2428 | 13.3541 | 13.5718 | 13.0187 | 13.625 | 13.1684 | 12.9504 | NaN | NaN | NaN | 13.3085 | 91.4972 | NaN | NaN | NaN | -19.8916 | NaN | NaN | NaN | 28.6165 | 590.9696 | NaN | 26.6684 | NaN | 27.9084
5546.1292 | 13.6222 | 13.2641 | 13.3558 | 13.5919 | 12.998 | 13.3505 | 13.1674 | 12.9502 | NaN | NaN | NaN | 13.3419 | 92.1998 | NaN | NaN | NaN | -19.6554 | NaN | NaN | NaN | 22.7761 | 590.5899 | NaN | 22.4836 | NaN | 26.6958
5547.1292 | 13.571 | 13.3829 | 13.3548 | 13.6578 | 12.9475 | 13.4393 | 13.1735 | 12.958 | NaN | NaN | NaN | 13.3854 | 89.8272 | NaN | NaN | NaN | -6.0825 | NaN | NaN | NaN | 22.5062 | 588.5204 | NaN | 25.5158 | NaN | 29.3748
5548.1292 | 13.6202 | 13.295 | 13.356 | 13.5942 | 13.0275 | 13.3435 | 13.1576 | 12.9626 | NaN | NaN | NaN | 13.3891 | 93.0323 | NaN | NaN | NaN | 2.0488 | NaN | NaN | NaN | 27.3493 | 587.2871 | NaN | 25.8604 | NaN | 28.4931
5549.1292 | 13.5966 | 13.248 | 13.3658 | 13.6438 | 13.0404 | 13.3855 | 13.1409 | 12.9611 | NaN | NaN | NaN | 13.3812 | 95.2157 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 22.9123 | 588.6722 | NaN | 21.5447 | NaN | 27.5007
5550.1292 | 13.888 | 13.2276 | 13.3568 | 13.6205 | 12.8863 | 13.5182 | 13.1569 | 12.9703 | NaN | NaN | NaN | 13.3209 | 93.2305 | NaN | NaN | NaN | -11.3526 | NaN | NaN | NaN | 24.7235 | 586.4242 | NaN | 27.0362 | NaN | 29.0213
5551.1292 | 13.8173 | 13.251 | 13.3535 | 13.6913 | 13.0946 | 13.3901 | 13.1389 | 12.961 | NaN | NaN | NaN | 13.4789 | 103.4416 | NaN | NaN | NaN | -16.8654 | NaN | NaN | NaN | 28.7695 | 587.5693 | NaN | 26.493 | NaN | 29.3787
5552.1292 | 13.6003 | 13.2808 | 13.3504 | 13.7764 | 12.9365 | 13.5132 | 13.151 | 12.9701 | NaN | NaN | NaN | 13.3613 | 95.1734 | NaN | NaN | NaN | -5.0318 | NaN | NaN | NaN | 22.0508 | 587.6338 | NaN | 25.2971 | NaN | 28.5445
5553.1292 | 13.5975 | 13.2904 | 13.3457 | 13.7279 | 12.9676 | 13.5343 | 13.1597 | 12.968 | NaN | NaN | NaN | 13.4022 | 93.6014 | NaN | NaN | NaN | 3.621 | NaN | NaN | NaN | 21.5705 | 586.6605 | NaN | 24.4562 | NaN | 26.6711
5554.1292 | 13.6284 | 13.1869 | 13.334 | 13.6475 | 13.0005 | 13.4166 | 13.1327 | 12.9711 | NaN | NaN | NaN | 13.3599 | 98.411 | NaN | NaN | NaN | -15.9767 | NaN | NaN | NaN | 22.266 | 587.9236 | NaN | 27.0457 | NaN | 28.2493
5555.1292 | 13.5756 | 13.2487 | 13.3407 | 13.6495 | 13.0914 | 13.4625 | 13.1313 | 12.9714 | NaN | NaN | NaN | 13.3232 | 92.8005 | NaN | NaN | NaN | 48.0832 | NaN | NaN | NaN | 21.1084 | 587.8116 | NaN | 26.8929 | NaN | 28.8814
5556.1292 | 13.6109 | 13.2089 | 13.3365 | 13.6714 | 12.9416 | 13.3891 | 13.1232 | 12.975 | NaN | NaN | NaN | 13.3891 | 99.108 | NaN | NaN | NaN | 7.5789 | NaN | NaN | NaN | 22.0777 | 587.4885 | NaN | 27.9368 | NaN | 28.5842
5557.1292 | 13.6136 | 13.1993 | 13.3328 | 13.6139 | 13.0217 | 13.4116 | 13.1229 | 12.9729 | NaN | NaN | NaN | 13.4414 | 93.2004 | NaN | NaN | NaN | -14.2208 | NaN | NaN | NaN | 28.9967 | 583.1957 | NaN | 27.2284 | NaN | 27.8835
5558.1292 | 13.6252 | 13.2047 | 13.336 | 13.6281 | 13.0237 | 13.3562 | 13.1104 | 12.9741 | NaN | NaN | NaN | 13.3774 | 92.8648 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 46.224 | 535.2883 | NaN | 25.16 | NaN | 26.6054
5559.1292 | 13.6353 | 13.1956 | 13.3308 | 13.6784 | 13.2661 | 13.3474 | 13.0935 | 12.9755 | NaN | NaN | NaN | 13.3736 | 94.2107 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 20.0855 | 528.258 | NaN | 25.0178 | NaN | 29.6118
5560.1292 | 13.5897 | 13.2833 | 13.3388 | 13.6433 | 13.2057 | 13.3523 | 13.153 | 12.9735 | NaN | NaN | NaN | 13.3316 | 89.9507 | NaN | NaN | NaN | 12.9538 | NaN | NaN | NaN | 25.4809 | 546.9783 | NaN | 25.918 | NaN | 27.6548
5561.1292 | 13.6077 | 13.232 | 13.3417 | 13.7038 | 13.0155 | 13.4491 | 13.1385 | 12.9733 | NaN | NaN | NaN | 13.3497 | 94.9623 | NaN | NaN | NaN | -18.2479 | NaN | NaN | NaN | 27.0281 | 561.8056 | NaN | 26.4339 | NaN | 27.5681
5562.1292 | 13.6599 | 13.2415 | 13.3444 | 13.6277 | 13.0061 | 13.4188 | 13.1331 | 12.9815 | NaN | NaN | NaN | 13.3608 | 91.0989 | NaN | NaN | NaN | -19.4178 | NaN | NaN | NaN | 25.7076 | 579.4907 | NaN | 24.8267 | NaN | 28.4965
5563.1292 | 13.6285 | 13.2492 | 13.3434 | 13.7634 | 13.1375 | 13.4096 | 13.1354 | 12.975 | NaN | NaN | NaN | 13.3101 | 96.9339 | NaN | NaN | NaN | 4.7713 | NaN | NaN | NaN | 25.6678 | 588.0378 | NaN | 26.7104 | NaN | 26.3379
5564.1292 | 13.6419 | 13.2494 | 13.3586 | 13.6602 | 13.0222 | 13.4093 | 13.1604 | 12.9826 | NaN | NaN | NaN | 13.3378 | 91.484 | NaN | NaN | NaN | -5.4783 | NaN | NaN | NaN | 24.9482 | 586.0571 | NaN | 25.8559 | NaN | 29.0901
5565.1292 | 13.6386 | 13.2948 | 13.3635 | 13.7676 | 13.0364 | 13.3939 | 13.1712 | 12.9764 | NaN | NaN | NaN | 13.3495 | 92.6008 | NaN | NaN | NaN | 48.592 | NaN | NaN | NaN | 25.4709 | 586.0361 | NaN | 24.3171 | NaN | 28.1832
5566.1292 | 13.6485 | 13.3679 | 13.3615 | 13.6378 | 13.0127 | 13.4074 | 13.1742 | 12.984 | NaN | NaN | NaN | 13.36 | 97.4928 | NaN | NaN | NaN | 13.0414 | NaN | NaN | NaN | 22.0724 | 584.9271 | NaN | 24.6957 | NaN | 27.3046
5567.1292 | 13.6158 | 13.2935 | 13.3676 | 13.7359 | 12.9914 | 13.6444 | 13.1656 | 12.9789 | NaN | NaN | NaN | 13.3391 | 96.4176 | NaN | NaN | NaN | 21.7284 | NaN | NaN | NaN | 25.0331 | 583.5038 | NaN | 26.4374 | NaN | 27.5801
5568.1292 | 13.7023 | 13.2438 | 13.3749 | 13.6727 | 13.1175 | 13.3996 | 13.1653 | 12.9803 | NaN | NaN | NaN | 13.3572 | 92.6135 | NaN | NaN | NaN | -12.9327 | NaN | NaN | NaN | 36.9199 | 582.5218 | NaN | 26.4901 | NaN | 28.1901
5569.1292 | 13.6587 | 13.3328 | 13.369 | 13.6437 | 13.0658 | 13.4104 | 13.1985 | 12.9694 | NaN | NaN | NaN | 13.3618 | 95.8973 | NaN | NaN | NaN | -9.7272 | NaN | NaN | NaN | 23.4613 | 584.0847 | NaN | 25.9488 | NaN | 26.8536
5570.1292 | 13.6906 | 13.261 | 13.3751 | 13.7902 | 13.0004 | 13.3891 | 13.1567 | 12.9643 | NaN | NaN | NaN | 13.3653 | 91.9424 | NaN | NaN | NaN | -19.1908 | NaN | NaN | NaN | 39.1522 | 584.7307 | NaN | 25.9388 | NaN | 26.9559
5571.1292 | 13.6823 | 13.3247 | 13.3797 | 13.6513 | 12.9375 | 13.4743 | 13.1866 | 12.9734 | NaN | NaN | NaN | 13.3985 | 93.0078 | NaN | NaN | NaN | -18.8543 | NaN | NaN | NaN | 33.1904 | 585.7384 | NaN | 26.342 | NaN | 28.6982
5572.1292 | 13.6986 | 13.3016 | 13.3767 | 13.7446 | 13.1102 | 13.4462 | 13.1745 | 12.9637 | NaN | NaN | NaN | 13.3165 | 90.2024 | NaN | NaN | NaN | 20.8058 | NaN | NaN | NaN | 24.6145 | 582.9381 | NaN | 27.3784 | NaN | 27.7238
5573.1292 | 13.7218 | 13.2986 | 13.3725 | 13.62 | 13.0443 | 13.4633 | 13.1622 | 12.9667 | NaN | NaN | NaN | 13.3589 | 92.0781 | NaN | NaN | NaN | -10.6071 | NaN | NaN | NaN | 24.9218 | 583.4483 | NaN | 26.2572 | NaN | 28.1531
5574.1292 | 13.6481 | 13.2357 | 13.3825 | 13.6593 | 12.9989 | 13.397 | 13.1388 | 12.9671 | NaN | NaN | NaN | 13.4041 | 94.4087 | NaN | NaN | NaN | 10.1458 | NaN | NaN | NaN | 23.6193 | 585.1212 | NaN | 24.3379 | NaN | 28.0264
5575.1292 | 13.6572 | 13.2468 | 13.377 | 13.6507 | 13.1189 | 13.4485 | 13.1466 | 12.9673 | NaN | NaN | NaN | 13.4313 | 93.1193 | NaN | NaN | NaN | 16.2508 | NaN | NaN | NaN | 21.5423 | 585.5229 | NaN | 26.1446 | NaN | 28.5288
5576.1292 | 13.6482 | 13.2708 | 13.3754 | 13.7483 | 13.0016 | 13.4357 | 13.1448 | 12.9732 | NaN | NaN | NaN | 13.3742 | 94.851 | NaN | NaN | NaN | 5.8191 | NaN | NaN | NaN | 20.1714 | 584.0145 | NaN | 25.9254 | NaN | 27.498
5577.1292 | 13.6411 | 13.4254 | 13.3853 | 13.9767 | 13.052 | 13.415 | 13.1969 | 12.9682 | NaN | NaN | NaN | 13.3504 | 92.54 | NaN | NaN | NaN | -6.3625 | NaN | NaN | NaN | 25.3268 | 586.44 | NaN | 25.713 | NaN | 28.2253
5578.1292 | 13.6277 | 13.2323 | 13.3837 | 13.6946 | 13.0736 | 13.5263 | 13.1386 | 12.9653 | NaN | NaN | NaN | 13.4562 | 92.3135 | NaN | NaN | NaN | 6.6373 | NaN | NaN | NaN | 30.8497 | 588.1777 | NaN | 26.719 | NaN | 29.6414
5579.1292 | 13.6472 | 13.312 | 13.3935 | 13.7047 | 13.0834 | 13.3913 | 13.1651 | 12.9555 | NaN | NaN | NaN | 13.3968 | 94.622 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 24.7908 | 585.5414 | NaN | 23.5636 | NaN | 28.0608
5580.1292 | 13.6219 | 13.2476 | 13.3999 | 13.6908 | 13.1435 | 13.443 | 13.149 | 12.9616 | NaN | NaN | NaN | 13.4103 | 92.2785 | NaN | NaN | NaN | -9.8522 | NaN | NaN | NaN | 20.934 | 587.4982 | NaN | 26.5396 | NaN | 27.9442
5581.1292 | 13.684 | 13.2369 | 13.3959 | 13.7085 | 13.088 | 13.5127 | 13.1353 | 12.951 | NaN | NaN | NaN | 13.3744 | 93.9218 | NaN | NaN | NaN | -2.5803 | NaN | NaN | NaN | 32.9198 | 589.6 | NaN | 25.7335 | NaN | 27.8625
5582.1292 | 13.6977 | 13.3525 | 13.4016 | 13.6438 | 12.9934 | 13.5051 | 13.1686 | 12.9562 | NaN | NaN | NaN | 13.3388 | 91.6005 | NaN | NaN | NaN | -18.3862 | NaN | NaN | NaN | 24.0786 | 589.1714 | NaN | 25.8531 | NaN | 26.7889
5583.1292 | 13.6894 | 13.2221 | 13.3987 | 13.6872 | 13.1256 | 13.4471 | 13.145 | 12.9526 | NaN | NaN | NaN | 13.4161 | 92.7705 | NaN | NaN | NaN | -14.2717 | NaN | NaN | NaN | 21.4315 | 588.7406 | NaN | 26.2483 | NaN | 27.4655
5584.1292 | 13.6635 | 13.3226 | 13.3903 | 13.7179 | 13.1245 | 13.3862 | 13.169 | 12.9527 | NaN | NaN | NaN | 13.3459 | 88.6504 | NaN | NaN | NaN | 9.1307 | NaN | NaN | NaN | 23.679 | 590.1769 | NaN | 26.7205 | NaN | 27.8308
5585.1292 | 13.6645 | 13.2954 | 13.3832 | 13.6938 | 13.0745 | 13.5801 | 13.1688 | 12.957 | NaN | NaN | NaN | 13.3583 | 93.9878 | NaN | NaN | NaN | 53.336 | NaN | NaN | NaN | 29.8665 | 590.4013 | NaN | 26.6205 | NaN | 27.3579
5586.1292 | 13.6546 | 13.2293 | 13.3828 | 13.7304 | 13.1154 | 13.3935 | 13.1474 | 12.9577 | NaN | NaN | NaN | 13.3515 | 95.6998 | NaN | NaN | NaN | 5.7554 | NaN | NaN | NaN | 28.2546 | 594.5879 | NaN | 26.1629 | NaN | 27.2918
5587.1292 | 13.668 | 13.3013 | 13.3845 | 13.668 | 13.0737 | 13.4405 | 13.1701 | 12.9567 | NaN | NaN | NaN | 13.5836 | 91.6981 | NaN | NaN | NaN | -19.2732 | NaN | NaN | NaN | 22.5402 | 591.7719 | NaN | 23.2469 | NaN | 28.1871
5588.1292 | 13.6615 | 13.2967 | 13.3801 | 13.7 | 12.9886 | 13.4697 | 13.1762 | 12.9559 | NaN | NaN | NaN | 13.3891 | 93.4367 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 22.5498 | 591.5761 | NaN | 26.8491 | NaN | 28.3158
5589.1292 | 13.6432 | 13.3025 | 13.3861 | 13.7164 | 13.0562 | 13.3951 | 13.1823 | 12.9562 | NaN | NaN | NaN | 13.4037 | 93.1155 | NaN | NaN | NaN | -12.5097 | NaN | NaN | NaN | 26.2914 | 594.2068 | NaN | 27.0235 | NaN | 27.0408
5590.1292 | 13.8371 | 13.2699 | 13.3945 | 13.7414 | 13.0663 | 13.4045 | 13.1556 | 12.9577 | NaN | NaN | NaN | 13.3926 | 93.8471 | NaN | NaN | NaN | -10.3734 | NaN | NaN | NaN | 39.9484 | 592.9737 | NaN | 27.4616 | NaN | 27.7389
5591.1292 | 13.658 | 13.2827 | 13.3902 | 13.7209 | 13.0901 | 13.41 | 13.1606 | 12.9594 | NaN | NaN | NaN | 13.4455 | 92.5749 | NaN | NaN | NaN | -13.586 | NaN | NaN | NaN | 26.2089 | 595.4532 | NaN | 26.7006 | NaN | 27.2843
5592.1292 | 13.7983 | 13.3247 | 13.3922 | 13.7391 | 13.0379 | 13.4479 | 13.1845 | 12.9615 | NaN | NaN | NaN | 13.4718 | 93.7359 | NaN | NaN | NaN | -3.9378 | NaN | NaN | NaN | 22.5124 | 594.0961 | NaN | 23.779 | NaN | 28.6018
5593.1292 | 13.6775 | 13.2826 | 13.403 | 13.7442 | 13.0328 | 13.5995 | 13.1743 | 12.96 | NaN | NaN | NaN | 13.4523 | 94.1741 | NaN | NaN | NaN | -15.1365 | NaN | NaN | NaN | 36.219 | 595.5478 | NaN | 23.3937 | NaN | 27.9828
5594.1292 | 13.6671 | 13.3683 | 13.4079 | 13.6918 | 12.9294 | 13.4171 | 13.1987 | 12.966 | NaN | NaN | NaN | 13.4116 | 91.6418 | NaN | NaN | NaN | 10.907 | NaN | NaN | NaN | 31.3232 | 596.4394 | NaN | 26.5308 | NaN | 26.6322
5595.1292 | 13.6244 | 13.5517 | 13.4146 | 13.8168 | 13.1157 | 13.4491 | 13.2136 | 12.968 | NaN | NaN | NaN | 13.3888 | 92.7952 | NaN | NaN | NaN | 10.907 | NaN | NaN | NaN | 27.8168 | 597.2953 | NaN | 24.1548 | NaN | 26.1062
5596.1292 | 13.8251 | 13.2896 | 13.4171 | 13.676 | 13.2363 | 13.5008 | 13.1812 | 12.9679 | NaN | NaN | NaN | 13.4666 | 96.7526 | NaN | NaN | NaN | -15.0766 | NaN | NaN | NaN | 20.7918 | 595.6429 | NaN | 27.9835 | NaN | 27.4204
5597.1292 | 13.6772 | 13.3152 | 13.4163 | 13.7215 | 13.1477 | 13.4148 | 13.1867 | 12.9645 | NaN | NaN | NaN | 13.4792 | 102.0427 | NaN | NaN | NaN | -16.8131 | NaN | NaN | NaN | 17.4438 | 596.4164 | NaN | 26.8729 | NaN | 29.4527
5598.1292 | 13.768 | 13.3736 | 13.4227 | 13.6871 | 13.1236 | 13.4365 | 13.2041 | 12.9616 | NaN | NaN | NaN | 13.5042 | 94.2157 | NaN | NaN | NaN | 2.1621 | NaN | NaN | NaN | 46.5603 | 595.367 | NaN | 28.0006 | NaN | 27.4755
5599.1292 | 13.6779 | 13.3026 | 13.4194 | 13.7467 | 13.048 | 13.7463 | 13.1931 | 12.9613 | NaN | NaN | NaN | 13.3912 | 93.0718 | NaN | NaN | NaN | -14.374 | NaN | NaN | NaN | 27.7871 | 596.3059 | NaN | 24.3993 | NaN | 27.6213
5600.1292 | 13.6871 | 13.3754 | 13.4169 | 13.7133 | 13.1781 | 13.4025 | 13.2044 | 12.9725 | NaN | NaN | NaN | 13.5366 | 93.516 | NaN | NaN | NaN | -15.5957 | NaN | NaN | NaN | 20.6473 | 597.8227 | NaN | 24.0864 | NaN | 27.5991
5601.1292 | 13.6463 | 13.3206 | 13.415 | 13.807 | 13.1384 | 13.4088 | 13.1988 | 12.9754 | NaN | NaN | NaN | 13.4687 | 94.6108 | NaN | NaN | NaN | -12.3085 | NaN | NaN | NaN | 19.9046 | 599.6283 | NaN | 25.7104 | NaN | 25.9225
5602.1292 | 13.7067 | 13.3228 | 13.4165 | 13.7209 | 12.9962 | 13.4844 | 13.1697 | 12.9839 | NaN | NaN | NaN | 13.4911 | 93.9847 | NaN | NaN | NaN | -16.8394 | NaN | NaN | NaN | 23.0988 | 599.5296 | NaN | 25.3411 | NaN | 24.9687
5603.1292 | 13.7058 | 13.3515 | 13.4163 | 13.6788 | 13.2319 | 13.437 | 13.1934 | 12.9816 | NaN | NaN | NaN | 13.4189 | 97.3651 | NaN | NaN | NaN | -19.5747 | NaN | NaN | NaN | -6.5161 | 600.0869 | NaN | 25.4479 | NaN | 27.0383
5604.1292 | 13.6584 | 13.4337 | 13.4168 | 13.7 | 13.0103 | 13.4759 | 13.2172 | 12.9843 | NaN | NaN | NaN | 13.3729 | 90.7145 | NaN | NaN | NaN | 28.142 | NaN | NaN | NaN | NaN | 601.5541 | NaN | 25.014 | NaN | 25.4113
5605.1292 | 13.6796 | 13.3181 | 13.4285 | 13.7706 | 13.0034 | 13.4458 | 13.1843 | 12.9866 | NaN | NaN | NaN | 13.4396 | 93.4956 | NaN | NaN | NaN | 1.9408 | NaN | NaN | NaN | NaN | 602.5843 | NaN | 27.1288 | NaN | 28.2484
5606.1292 | 13.6689 | 13.3353 | 13.4321 | 13.7694 | 13.0621 | 13.5313 | 13.186 | 12.9831 | NaN | NaN | NaN | 13.4077 | 93.2779 | NaN | NaN | NaN | -7.5688 | NaN | NaN | NaN | NaN | 600.9039 | NaN | 25.9608 | NaN | 27.6011
5607.1292 | 13.7244 | 13.3267 | 13.4358 | 13.7551 | 13.1308 | 13.3924 | 13.1995 | 12.9768 | NaN | NaN | NaN | 13.391 | 94.5174 | NaN | NaN | NaN | 37.3192 | NaN | NaN | NaN | NaN | 608.2431 | NaN | 26.7693 | NaN | 28.1497
5608.1292 | 13.671 | 13.3763 | 13.4375 | 13.7739 | 13.0976 | 13.4103 | 13.2186 | 12.9787 | NaN | NaN | NaN | 13.4358 | 94.6641 | NaN | NaN | NaN | 1.8896 | NaN | NaN | NaN | NaN | 612.918 | NaN | 27.1691 | NaN | 27.3275
5609.1292 | 13.81 | 13.5016 | 13.4363 | 13.7396 | 13.199 | 13.4215 | 13.2134 | 12.9778 | NaN | NaN | NaN | 13.472 | 94.4639 | NaN | NaN | NaN | 18.9549 | NaN | NaN | NaN | NaN | 616.7151 | NaN | 25.4195 | NaN | 27.5391
5610.1292 | 13.7127 | 13.6008 | 13.4344 | 13.6955 | 13.1806 | 13.4692 | 13.2606 | 12.9749 | NaN | NaN | NaN | 13.546 | 93.947 | NaN | NaN | NaN | -18.4533 | NaN | NaN | NaN | NaN | 618.7888 | NaN | 25.0265 | NaN | 29.2708
5611.1292 | 13.7321 | 13.498 | 13.4348 | 13.709 | 13.1798 | 13.4085 | 13.2435 | 12.9755 | NaN | NaN | NaN | 13.4524 | 94.0268 | NaN | NaN | NaN | -18.8061 | NaN | NaN | NaN | NaN | 619.346 | NaN | 25.3816 | NaN | 27.6354
5612.1292 | 13.7386 | 13.3521 | 13.4317 | 13.7671 | 12.9544 | 13.4243 | 13.1913 | 12.9767 | NaN | NaN | NaN | 13.4359 | 93.6454 | NaN | NaN | NaN | -14.0867 | NaN | NaN | NaN | NaN | 620.9019 | NaN | 26.6641 | NaN | 28.6248
5613.1292 | 13.7451 | 13.3538 | 13.4394 | 13.7607 | 13.0947 | 13.5037 | 13.183 | 12.9692 | NaN | NaN | NaN | 13.5187 | 93.047 | NaN | NaN | NaN | -11.6729 | NaN | NaN | NaN | NaN | 621.2713 | NaN | 25.4821 | NaN | 29.2454
5614.1292 | 13.7562 | 13.3413 | 13.4314 | 13.784 | 13.1676 | 13.465 | 13.177 | 12.9681 | NaN | NaN | NaN | 13.4166 | 93.7452 | NaN | NaN | NaN | -4.5509 | NaN | NaN | NaN | NaN | 621.7942 | NaN | 25.242 | NaN | 27.4094
5615.1292 | 13.8188 | 13.3622 | 13.4333 | 13.7632 | 13.1611 | 13.4287 | 13.1822 | 12.9731 | NaN | NaN | NaN | 13.4211 | 93.239 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 621.9936 | NaN | 24.2858 | NaN | 27.3987
5616.1292 | 13.7397 | 13.3551 | 13.4438 | 13.7273 | 13.0464 | 13.4512 | 13.1887 | 12.9657 | NaN | NaN | NaN | 13.4321 | 92.6547 | NaN | NaN | NaN | 49.6472 | NaN | NaN | NaN | NaN | 624.7001 | NaN | 24.9304 | NaN | 27.6061
5617.1292 | 13.7828 | 13.4912 | 13.4447 | 13.7317 | 13.0435 | 13.5214 | 13.227 | 12.9695 | NaN | NaN | NaN | 13.4713 | 92.6496 | NaN | NaN | NaN | -0.2088 | NaN | NaN | NaN | NaN | 624.6321 | NaN | 26.6047 | NaN | 27.93
5618.1292 | 13.7117 | 13.3486 | 13.4423 | 13.7508 | 13.0809 | 13.5865 | 13.2048 | 12.9837 | NaN | NaN | NaN | 13.5252 | 94.0495 | NaN | NaN | NaN | 31.3448 | NaN | NaN | NaN | NaN | 625.697 | NaN | 27.7904 | NaN | 27.3369
5619.1292 | 13.7526 | 13.3336 | 13.4416 | 13.7382 | 13.0858 | 13.4516 | 13.1872 | 12.9836 | NaN | NaN | NaN | 13.4263 | 94.5934 | NaN | NaN | NaN | -15.479 | NaN | NaN | NaN | NaN | 622.6716 | NaN | 27.4773 | NaN | 28.3831
5620.1292 | 13.6946 | 13.5267 | 13.4471 | 13.8511 | 13.0657 | 13.5024 | 13.2365 | 12.9795 | NaN | NaN | NaN | 13.4234 | 93.4413 | NaN | NaN | NaN | 14.1843 | NaN | NaN | NaN | NaN | 625.8599 | NaN | 24.3726 | NaN | 27.8021
5621.1292 | 13.7375 | 13.3414 | 13.4453 | 13.7872 | 13.0408 | 13.5073 | 13.1756 | 12.9914 | NaN | NaN | NaN | 13.5116 | 93.7516 | NaN | NaN | NaN | -3.3271 | NaN | NaN | NaN | NaN | 624.825 | NaN | 26.2415 | NaN | 28.5678
5622.1292 | 13.7597 | 13.3401 | 13.4486 | 13.8009 | 13.096 | 13.5733 | 13.2065 | 12.9908 | NaN | NaN | NaN | 13.3946 | 93.1253 | NaN | NaN | NaN | 6.0675 | NaN | NaN | NaN | NaN | 621.0747 | NaN | 24.9505 | NaN | 27.3962
5623.1292 | 13.6813 | 13.404 | 13.4467 | 13.7642 | 13.0574 | 13.4362 | 13.2116 | 12.9836 | NaN | NaN | NaN | 13.4633 | 94.488 | NaN | NaN | NaN | 2.3401 | NaN | NaN | NaN | NaN | 623.6943 | NaN | 25.9249 | NaN | 28.2683
5624.1292 | 13.7195 | 13.3979 | 13.4474 | 13.8098 | 13.1636 | 13.4405 | 13.2083 | 12.9875 | NaN | NaN | NaN | 13.4374 | 94.13 | NaN | NaN | NaN | 28.8479 | NaN | NaN | NaN | NaN | 622.517 | NaN | 27.4531 | NaN | 27.6026
5625.1292 | 13.7623 | 13.4416 | 13.4464 | 13.7911 | 13.2334 | 13.4454 | 13.2056 | 12.9876 | NaN | NaN | NaN | 13.4084 | 92.5661 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 625.1425 | NaN | 27.1154 | NaN | 27.8921
5626.1292 | 13.7743 | 13.3404 | 13.4531 | 13.7845 | 13.1035 | 13.4705 | 13.2056 | 12.9872 | NaN | NaN | NaN | 13.3906 | 93.2103 | NaN | NaN | NaN | 28.4691 | NaN | NaN | NaN | NaN | 623.641 | NaN | 25.8966 | NaN | 27.4311
5627.1292 | 13.7088 | 13.4217 | 13.4579 | 13.7321 | 13.0104 | 13.4801 | 13.2335 | 12.9846 | NaN | NaN | NaN | 13.61 | 93.8431 | NaN | NaN | NaN | 0.3127 | NaN | NaN | NaN | NaN | 623.2063 | NaN | 27.0749 | NaN | 27.5072
5628.1292 | 13.7492 | 13.3784 | 13.4454 | 13.7558 | 13.1711 | 13.4666 | 13.2117 | 12.9831 | NaN | NaN | NaN | 13.3979 | 92.8303 | NaN | NaN | NaN | -10.6857 | NaN | NaN | NaN | NaN | 624.6359 | NaN | 23.5759 | NaN | 28.5189
5629.1292 | 13.7979 | 13.3734 | 13.4366 | 13.7346 | 13.1948 | 13.615 | 13.207 | 12.9924 | NaN | NaN | NaN | 13.5222 | 92.9608 | NaN | NaN | NaN | -8.92 | NaN | NaN | NaN | NaN | 623.5381 | NaN | 26.8145 | NaN | 28.4319
5630.1292 | 13.7547 | 13.3472 | 13.4337 | 13.746 | 13.1053 | 13.5809 | 13.1893 | 12.9931 | NaN | NaN | NaN | 13.5255 | 93.1702 | NaN | NaN | NaN | -11.3763 | NaN | NaN | NaN | NaN | 624.5457 | NaN | 26.1814 | NaN | 29.2605
5631.1292 | 13.8711 | 13.3739 | 13.4352 | 13.7849 | 13.1776 | 13.4898 | 13.2206 | 12.996 | NaN | NaN | NaN | 13.397 | 92.6239 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 623.261 | NaN | 25.9577 | NaN | 27.039
5632.1292 | 13.7656 | 13.3422 | 13.4316 | 13.8125 | 13.096 | 13.4654 | 13.1895 | 13.0052 | NaN | NaN | NaN | 13.4027 | 92.8369 | NaN | NaN | NaN | -12.5148 | NaN | NaN | NaN | NaN | 620.7889 | NaN | 26.5733 | NaN | 28.4893
5633.1292 | 13.8452 | 13.3681 | 13.4315 | 13.9836 | 13.2119 | 13.5348 | 13.2224 | 12.9945 | NaN | NaN | NaN | 13.4627 | 89.9677 | NaN | NaN | NaN | 20.0118 | NaN | NaN | NaN | NaN | 619.2384 | NaN | 27.3848 | NaN | 27.0425
5634.1292 | 13.7547 | 13.3455 | 13.4335 | 13.7603 | 13.1387 | 13.4656 | 13.2126 | 12.9985 | NaN | NaN | NaN | 13.4794 | 91.3265 | NaN | NaN | NaN | -12.9113 | NaN | NaN | NaN | NaN | 622.6513 | NaN | 25.2124 | NaN | 28.0136
5635.1292 | 13.7107 | 13.4581 | 13.4307 | 13.8205 | 13.0868 | 13.4729 | 13.2261 | 12.9994 | NaN | NaN | NaN | 13.4631 | 93.6117 | NaN | NaN | NaN | 6.4371 | NaN | NaN | NaN | NaN | 619.6015 | NaN | 25.6709 | NaN | 28.692
5636.1292 | 13.7669 | 13.3932 | 13.4373 | 13.804 | 13.154 | 13.5124 | 13.2153 | 12.9943 | NaN | NaN | NaN | 13.4244 | 95.11 | NaN | NaN | NaN | -18.8076 | NaN | NaN | NaN | NaN | 618.6988 | NaN | 26.5597 | NaN | 26.5309
5637.1292 | 13.8875 | 13.3674 | 13.4339 | 13.7546 | 13.1344 | 13.4885 | 13.2217 | 12.9878 | NaN | NaN | NaN | 13.468 | 92.7462 | NaN | NaN | NaN | 15.2464 | NaN | NaN | NaN | NaN | 618.108 | NaN | 26.4438 | NaN | 27.4559
5638.1292 | 13.7317 | 13.3521 | 13.4374 | 13.7821 | 13.1183 | 13.4674 | 13.1901 | 12.987 | NaN | NaN | NaN | 13.4836 | 92.3308 | NaN | NaN | NaN | 36.1606 | NaN | NaN | NaN | NaN | 607.9916 | NaN | 24.6225 | NaN | 29.4704
5639.1292 | 13.7447 | 13.3593 | 13.4356 | 13.7696 | 13.1642 | 13.5331 | 13.2043 | 12.9921 | NaN | NaN | NaN | 13.4654 | 93.7666 | NaN | NaN | NaN | 38.4548 | NaN | NaN | NaN | NaN | 608.1942 | NaN | 27.3499 | NaN | 27.5231
5640.1292 | 13.8858 | 13.3359 | 13.4365 | 13.7512 | 13.2779 | 13.4673 | 13.2093 | 12.9847 | NaN | NaN | NaN | 13.5471 | 93.0033 | NaN | NaN | NaN | -13.6977 | NaN | NaN | NaN | NaN | 605.5546 | NaN | 25.1514 | NaN | 26.3782
5641.1292 | 13.7268 | 13.4249 | 13.4397 | 13.813 | 13.1423 | 13.5487 | 13.2182 | 12.989 | NaN | NaN | NaN | 13.4191 | 92.3983 | NaN | NaN | NaN | 12.8439 | NaN | NaN | NaN | NaN | 605.1439 | NaN | 25.9692 | NaN | 28.4165
5642.1292 | 13.7607 | 13.3372 | 13.4373 | 13.8328 | 13.0827 | 13.6691 | 13.2015 | 12.9867 | NaN | NaN | NaN | 13.4497 | 93.6699 | NaN | NaN | NaN | -5.1075 | NaN | NaN | NaN | NaN | 603.9579 | NaN | 26.9699 | NaN | 28.9732
5643.1292 | 13.9994 | 13.3415 | 13.4431 | 13.7673 | 13.0648 | 13.5366 | 13.1994 | 12.9874 | NaN | NaN | NaN | 13.4311 | 91.6935 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 604.2844 | NaN | 25.3707 | NaN | 26.4967
5644.1292 | 13.7922 | 13.3799 | 13.4507 | 13.7847 | 13.17 | 13.5361 | 13.2263 | 12.9934 | NaN | NaN | NaN | 13.4466 | 92.742 | NaN | NaN | NaN | 7.0705 | NaN | NaN | NaN | NaN | 602.645 | NaN | 25.5847 | NaN | 27.8177
5645.1292 | 13.7982 | 13.4315 | 13.4469 | 13.7059 | 13.0978 | 13.5008 | 13.2319 | 12.9906 | NaN | NaN | NaN | 13.4247 | 93.7342 | NaN | NaN | NaN | -12.0658 | NaN | NaN | NaN | NaN | 601.827 | NaN | 25.7104 | NaN | 27.0165
5646.1292 | 13.7333 | 13.3439 | 13.4388 | 13.7697 | 13.1996 | 13.4691 | 13.1973 | 12.9889 | NaN | NaN | NaN | 13.4524 | 92.6044 | NaN | NaN | NaN | -3.7748 | NaN | NaN | NaN | NaN | 601.3215 | NaN | 23.4629 | NaN | 28.8596
5647.1292 | 13.7926 | 13.4406 | 13.4397 | 13.8156 | 13.1227 | 13.5408 | 13.2165 | 12.9921 | NaN | NaN | NaN | 13.39 | 93.2079 | NaN | NaN | NaN | -6.2704 | NaN | NaN | NaN | NaN | 599.9023 | NaN | 24.4676 | NaN | 28.5761
5648.1292 | 13.7309 | 13.4109 | 13.4471 | 13.789 | 13.2425 | 13.4972 | 13.2222 | 12.996 | NaN | NaN | NaN | 13.3886 | 94.0551 | NaN | NaN | NaN | 28.3027 | NaN | NaN | NaN | NaN | 598.6112 | NaN | 24.6863 | NaN | 28.7132
5649.1292 | 13.8114 | 13.4863 | 13.4367 | 13.8139 | 13.1081 | 13.5758 | 13.2355 | 12.9904 | NaN | NaN | NaN | 13.4529 | 92.5336 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 599.2986 | NaN | 25.8745 | NaN | 27.9867
5650.1292 | 13.718 | 13.5051 | 13.4457 | 13.7585 | 13.1736 | 13.5707 | 13.2612 | 12.9951 | NaN | NaN | NaN | 13.4032 | 92.1265 | NaN | NaN | NaN | 14.1178 | NaN | NaN | NaN | NaN | 598.3643 | NaN | 24.5251 | NaN | 27.3344
5651.1292 | 13.7367 | 13.3815 | 13.453 | 13.8163 | 13.1446 | 13.514 | 13.2224 | 12.9985 | NaN | NaN | NaN | 13.4501 | 93.2231 | NaN | NaN | NaN | 3.9146 | NaN | NaN | NaN | NaN | 599.5828 | NaN | 24.6455 | NaN | 27.7905
5652.1292 | 13.7766 | 13.3588 | 13.4609 | 13.8182 | 13.1756 | 13.6104 | 13.2048 | 12.9978 | NaN | NaN | NaN | 13.4795 | 91.5089 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 600.7942 | NaN | 24.5633 | NaN | 29.0087
5653.1292 | 13.7531 | 13.3517 | 13.4545 | 13.7496 | 13.1769 | 13.5299 | 13.2075 | 12.9957 | NaN | NaN | NaN | 13.4101 | 94.6043 | NaN | NaN | NaN | 10.6348 | NaN | NaN | NaN | NaN | 601.0222 | NaN | 27.1057 | NaN | 27.7251
5654.1292 | 13.7701 | 13.4136 | 13.4568 | 13.7867 | 13.1212 | 13.4892 | 13.2341 | 12.9935 | NaN | NaN | NaN | 13.4303 | 92.4112 | NaN | NaN | NaN | 2.8625 | NaN | NaN | NaN | NaN | 596.548 | NaN | 23.1338 | NaN | 27.9302
5655.1292 | 13.7547 | 13.3546 | 13.4664 | 13.7878 | 13.108 | 13.4788 | 13.2025 | 12.9948 | NaN | NaN | NaN | 13.4094 | 93.9874 | NaN | NaN | NaN | 17.118 | NaN | NaN | NaN | NaN | 600.1823 | NaN | 26.7402 | NaN | 28.7697
5656.1292 | 13.7561 | 13.4433 | 13.4595 | 13.7835 | 13.19 | 13.5957 | 13.2439 | 12.9929 | NaN | NaN | NaN | 13.4487 | 93.2911 | NaN | NaN | NaN | 8.5683 | NaN | NaN | NaN | NaN | 598.504 | NaN | 23.3606 | NaN | 26.3773
5657.1292 | 13.8392 | 13.3655 | 13.4689 | 13.8077 | 13.276 | 13.5751 | 13.2236 | 12.9918 | NaN | NaN | NaN | 13.3969 | 93.6199 | NaN | NaN | NaN | 11.4591 | NaN | NaN | NaN | NaN | 597.5621 | NaN | 26.9764 | NaN | 28.8121
5658.1292 | 13.7605 | 13.3833 | 13.4698 | 13.7609 | 13.1018 | 13.5521 | 13.2445 | 12.9954 | NaN | NaN | NaN | 13.4197 | 92.4367 | NaN | NaN | NaN | -15.0784 | NaN | NaN | NaN | NaN | 599.8813 | NaN | 25.7052 | NaN | 26.5055
5659.1292 | 13.7664 | 13.414 | 13.474 | 14.008 | 13.2499 | 13.4948 | 13.2277 | 13.0024 | NaN | NaN | NaN | 13.4185 | 92.3678 | NaN | NaN | NaN | -7.6076 | NaN | NaN | NaN | NaN | 599.7933 | NaN | 24.7265 | NaN | 27.7644
5660.1292 | 13.7713 | 13.4594 | 13.4742 | 13.8167 | 13.1033 | 13.5519 | 13.2367 | 13.0044 | NaN | NaN | NaN | 13.4007 | 93.7516 | NaN | NaN | NaN | 7.6284 | NaN | NaN | NaN | NaN | 598.6306 | NaN | 21.4349 | NaN | 27.6955
5661.1292 | 13.9023 | 13.4145 | 13.4698 | 13.7799 | 13.0631 | 13.6095 | 13.2421 | 12.9998 | NaN | NaN | NaN | 13.4431 | 92.8149 | NaN | NaN | NaN | 2.8291 | NaN | NaN | NaN | NaN | 598.4773 | NaN | 25.1551 | NaN | 28.3238
5662.1292 | 13.7432 | 13.3652 | 13.4799 | 13.8966 | 13.2204 | 13.5183 | 13.2174 | 13.0035 | NaN | NaN | NaN | 13.4381 | 92.5391 | NaN | NaN | NaN | 9.2333 | NaN | NaN | NaN | NaN | 599.2692 | NaN | 25.2934 | NaN | 28.2716
5663.1292 | 13.7787 | 13.3765 | 13.4818 | 13.7779 | 13.1632 | 13.5076 | 13.2277 | 12.9997 | NaN | NaN | NaN | 13.4761 | 93.1573 | NaN | NaN | NaN | -16.9818 | NaN | NaN | NaN | NaN | 596.9493 | NaN | 24.4711 | NaN | 29.1384
5664.1292 | 13.7809 | 13.3505 | 13.4792 | 13.8044 | 13.2424 | 13.5634 | 13.2162 | 13.0067 | NaN | NaN | NaN | 13.4043 | 92.3931 | NaN | NaN | NaN | 5.8034 | NaN | NaN | NaN | NaN | 597.0175 | NaN | 24.3551 | NaN | 27.2264
5665.1292 | 13.7186 | 13.4015 | 13.4763 | 13.7536 | 13.1455 | 13.6748 | 13.2286 | 13.0102 | NaN | NaN | NaN | 13.5648 | 92.6049 | NaN | NaN | NaN | 0.6113 | NaN | NaN | NaN | NaN | 598.1908 | NaN | 25.2853 | NaN | 26.9592
5666.1292 | 13.8016 | 13.4956 | 13.4696 | 13.8139 | 13.1663 | 13.8376 | 13.2338 | 12.998 | NaN | NaN | NaN | 13.5433 | 92.0787 | NaN | NaN | NaN | -10.2305 | NaN | NaN | NaN | NaN | 597.9241 | NaN | 24.5264 | NaN | 28.573
5667.1292 | 13.8037 | 13.4162 | 13.471 | 13.7733 | 13.0121 | 13.564 | 13.2364 | 12.9963 | NaN | NaN | NaN | 13.4412 | 92.3881 | NaN | NaN | NaN | 0.5556 | NaN | NaN | NaN | NaN | 598.0768 | NaN | 25.4598 | NaN | 28.7363
5668.1292 | 13.8187 | 13.5203 | 13.4684 | 13.8269 | 13.2175 | 13.5311 | 13.2716 | 12.9974 | NaN | NaN | NaN | 13.4175 | 95.6779 | NaN | NaN | NaN | 0.4196 | NaN | NaN | NaN | NaN | 599.2525 | NaN | 25.3497 | NaN | 26.5382
5669.1292 | 13.7268 | 13.3753 | 13.4652 | 13.7515 | 13.2226 | 13.7001 | 13.2189 | 13 | NaN | NaN | NaN | 13.4182 | 93.986 | NaN | NaN | NaN | -6.4607 | NaN | NaN | NaN | NaN | 600.8554 | NaN | 26.4068 | NaN | 28.6983
5670.1292 | 13.7506 | 13.387 | 13.4573 | 13.793 | 13.1623 | 13.5537 | 13.2327 | 12.9974 | NaN | NaN | NaN | 13.5174 | 94.4048 | NaN | NaN | NaN | -14.8673 | NaN | NaN | NaN | NaN | 600.6753 | NaN | 23.6073 | NaN | 27.3383
5671.1292 | 13.8838 | 13.4226 | 13.4608 | 13.8267 | 13.2056 | 13.5545 | 13.2152 | 12.9982 | NaN | NaN | NaN | 13.4245 | 93.1473 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 598.0719 | NaN | 21.1751 | NaN | 27.94
5672.1292 | 13.7849 | 13.4418 | 13.4525 | 13.7593 | 13.1353 | 13.691 | 13.2496 | 12.9949 | NaN | NaN | NaN | 13.4792 | 91.6768 | NaN | NaN | NaN | -11.8476 | NaN | NaN | NaN | NaN | 599.7638 | NaN | 26.0341 | NaN | 29.3423
5673.1448 | 13.7922 | 13.362 | 13.4576 | 13.8085 | 13.2358 | 13.7114 | 13.2144 | 13.0022 | NaN | NaN | NaN | 13.496 | 92.7093 | NaN | NaN | NaN | -15.7091 | NaN | NaN | NaN | NaN | 599.4432 | NaN | 25.686 | NaN | 28.4443
5674.1292 | 13.7582 | 13.4289 | 13.4544 | 13.9533 | 13.2314 | 13.5164 | 13.2329 | 13.0033 | NaN | NaN | NaN | 13.4043 | 92.9421 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 598.3666 | NaN | 22.8524 | NaN | 27.2266
5675.1292 | 13.7434 | 13.4987 | 13.4517 | 13.8565 | 13.2309 | 13.5498 | 13.2426 | 13.0032 | NaN | NaN | NaN | 13.4968 | 94.446 | NaN | NaN | NaN | 6.95 | NaN | NaN | NaN | NaN | 597.9912 | NaN | 25.3207 | NaN | 26.9559
5676.1292 | 13.732 | 13.3793 | 13.4575 | 13.7415 | 13.178 | 13.6157 | 13.2394 | 13.0107 | NaN | NaN | NaN | 13.4062 | 92.4775 | NaN | NaN | NaN | 18.0596 | NaN | NaN | NaN | NaN | 598.7294 | NaN | 24.5352 | NaN | 27.9036
5677.1292 | 13.7284 | 13.5371 | 13.4582 | 13.8499 | 13.2789 | 13.6373 | 13.2577 | 13.0157 | NaN | NaN | NaN | 13.4377 | 94.7221 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 599.282 | NaN | 24.5328 | NaN | 28.1951
5678.1292 | 13.7174 | 13.5168 | 13.4615 | 13.816 | 13.2402 | 13.5233 | 13.2672 | 13.018 | NaN | NaN | NaN | 13.4555 | 93.4155 | NaN | NaN | NaN | 35.4681 | NaN | NaN | NaN | NaN | 599.1635 | NaN | 24.4564 | NaN | 27.8206
5679.1292 | 13.7562 | 13.4285 | 13.4652 | 13.8207 | 13.2167 | 13.5373 | 13.2573 | 13.0163 | NaN | NaN | NaN | 13.5737 | 93.5547 | NaN | NaN | NaN | -10.4529 | NaN | NaN | NaN | NaN | 595.1949 | NaN | 21.7289 | NaN | 29.7062
5680.1292 | 13.7489 | 13.4845 | 13.4587 | 13.7949 | 13.1096 | 13.5513 | 13.2684 | 13.0176 | NaN | NaN | NaN | 13.525 | 95.0328 | NaN | NaN | NaN | 31.6051 | NaN | NaN | NaN | NaN | 595.1607 | NaN | 25.5896 | NaN | 28.1539
5681.1292 | 13.7557 | 13.3839 | 13.4623 | 13.7658 | 13.1783 | 13.522 | 13.2382 | 13.0231 | NaN | NaN | NaN | 13.4122 | 94.9608 | NaN | NaN | NaN | 9.6929 | NaN | NaN | NaN | NaN | 594.9002 | NaN | 24.5289 | NaN | 28.1931
5682.1292 | 13.7602 | 13.3577 | 13.4657 | 13.7511 | 13.1681 | 13.6274 | 13.2473 | 13.0296 | NaN | NaN | NaN | 13.5892 | 93.4442 | NaN | NaN | NaN | 22.9089 | NaN | NaN | NaN | NaN | 597.8417 | NaN | 24.6057 | NaN | 27.3169
5683.1292 | 13.785 | 13.3377 | 13.4642 | 13.8664 | 13.2069 | 13.5814 | 13.2342 | 13.031 | NaN | NaN | NaN | 13.4471 | 92.4647 | NaN | NaN | NaN | 2.8865 | NaN | NaN | NaN | NaN | 597.1606 | NaN | 24.7075 | NaN | 27.3266
5684.1292 | 13.7235 | 13.5145 | 13.4721 | 13.8662 | 13.0802 | 13.5616 | 13.2728 | 13.0358 | NaN | NaN | NaN | 13.4943 | 98.3983 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 598.1267 | NaN | 27.7101 | NaN | 28.2018
5685.1292 | 14.0012 | 13.4028 | 13.4752 | 13.7811 | 13.1802 | 13.5289 | 13.2592 | 13.0308 | NaN | NaN | NaN | 13.4313 | 94.4558 | NaN | NaN | NaN | 8.4076 | NaN | NaN | NaN | NaN | 598.3676 | NaN | 24.8392 | NaN | 25.6448
5686.1292 | 13.7753 | 13.4586 | 13.4807 | 13.8529 | 13.0791 | 13.5547 | 13.2566 | 13.0444 | NaN | NaN | NaN | 13.4981 | 92.2597 | NaN | NaN | NaN | -14.7769 | NaN | NaN | NaN | NaN | 597.9945 | NaN | 24.097 | NaN | 26.8212
5687.1292 | 13.7619 | 13.3713 | 13.4874 | 13.7851 | 13.2222 | 13.5441 | 13.2356 | 13.0396 | NaN | NaN | NaN | 13.3986 | 94.4313 | NaN | NaN | NaN | 10.3377 | NaN | NaN | NaN | NaN | 596.7544 | NaN | 25.2694 | NaN | 29.1266
5688.1292 | 13.7719 | 13.4603 | 13.4851 | 13.7652 | 13.2688 | 13.5354 | 13.2545 | 13.043 | NaN | NaN | NaN | 13.5187 | 96.3367 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 595.729 | NaN | 24.6237 | NaN | 28.4531
5689.1292 | 13.7578 | 13.3918 | 13.4838 | 13.8316 | 13.196 | 13.5218 | 13.2287 | 13.0439 | NaN | NaN | NaN | 13.4409 | 92.1856 | NaN | NaN | NaN | -18.3153 | NaN | NaN | NaN | NaN | 594.317 | NaN | 25.5502 | NaN | 29.1297
5690.1292 | 14.1082 | 13.4451 | 13.4759 | 13.808 | 13.2078 | 13.5253 | 13.257 | 13.04 | NaN | NaN | NaN | 13.4315 | 92.9879 | NaN | NaN | NaN | 36.1203 | NaN | NaN | NaN | NaN | 593.9782 | NaN | 25.1262 | NaN | 29.451
5691.1292 | 13.7544 | 13.5178 | 13.4734 | 13.8024 | 13.0806 | 13.6044 | 13.3013 | 13.0438 | NaN | NaN | NaN | 13.3947 | 98.2332 | NaN | NaN | NaN | 43.3231 | NaN | NaN | NaN | NaN | 594.242 | NaN | 24.8553 | NaN | 27.3448
5692.1292 | 13.8888 | 13.3933 | 13.4705 | 13.7978 | 13.2187 | 13.5361 | 13.2373 | 13.0461 | NaN | NaN | NaN | 13.3811 | 92.5607 | NaN | NaN | NaN | -14.403 | NaN | NaN | NaN | NaN | 596.1912 | NaN | 25.4763 | NaN | 27.3634
5693.1292 | 13.7352 | 13.3877 | 13.4714 | 13.8469 | 13.1196 | 13.5752 | 13.2368 | 13.0487 | NaN | NaN | NaN | 13.5222 | 93.7066 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 594.3735 | NaN | 25.46 | NaN | 27.3233
5694.1292 | 13.7446 | 13.4203 | 13.4773 | 13.7924 | 13.2254 | 13.5448 | 13.2472 | 13.0524 | NaN | NaN | NaN | 13.3943 | 99.2326 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 594.8568 | NaN | 24.1616 | NaN | 27.5595
5695.1292 | 13.7692 | 13.3736 | 13.4754 | 13.7789 | 13.1113 | 13.6267 | 13.2415 | 13.0474 | NaN | NaN | NaN | 13.4597 | 92.5261 | NaN | NaN | NaN | 47.2612 | NaN | NaN | NaN | NaN | 598.8063 | NaN | 24.0014 | NaN | 28.3628
5696.1292 | 13.7644 | 13.4012 | 13.4763 | 13.8509 | 13.1189 | 13.6035 | 13.251 | 13.0584 | NaN | NaN | NaN | 13.4341 | 91.9345 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 596.1774 | NaN | 26.6585 | NaN | 27.7207
5697.1292 | 13.9136 | 13.4302 | 13.4798 | 13.8424 | 13.2108 | 13.5037 | 13.2633 | 13.0552 | NaN | NaN | NaN | 13.5337 | 93.27 | NaN | NaN | NaN | -19.9264 | NaN | NaN | NaN | NaN | 595.0308 | NaN | 26.9761 | NaN | 27.186
5698.1292 | 13.8365 | 13.3689 | 13.4823 | 14.0537 | 13.1969 | 13.5546 | 13.2551 | 13.0615 | NaN | NaN | NaN | 13.463 | 93.4637 | NaN | NaN | NaN | -19.0914 | NaN | NaN | NaN | NaN | 596.6048 | NaN | 21.618 | NaN | 28.4429
5699.1292 | 13.7119 | 13.3971 | 13.4796 | 13.8351 | 13.2822 | 13.5922 | 13.2522 | 13.0633 | NaN | NaN | NaN | 13.4064 | 93.2182 | NaN | NaN | NaN | 7.308 | NaN | NaN | NaN | NaN | 595.7141 | NaN | 24.8178 | NaN | 28.4793
5700.1292 | 13.833 | 13.3954 | 13.4855 | 13.8088 | 13.1531 | 13.5604 | 13.2528 | 13.059 | NaN | NaN | NaN | 13.4297 | 92.5089 | NaN | NaN | NaN | 33.6327 | NaN | NaN | NaN | NaN | 592.8719 | NaN | 25.4709 | NaN | 27.1885
5701.1292 | 13.7737 | 13.4196 | 13.4887 | 13.8034 | 13.265 | 13.5045 | 13.2627 | 13.0598 | NaN | NaN | NaN | 13.4324 | 96.1283 | NaN | NaN | NaN | -12.7684 | NaN | NaN | NaN | NaN | 597.7748 | NaN | 22.9655 | NaN | 27.5819
5702.1292 | 13.769 | 13.381 | 13.4911 | 13.8273 | 13.2448 | 13.5239 | 13.248 | 13.0572 | NaN | NaN | NaN | 13.4031 | 93.2524 | NaN | NaN | NaN | -1.0362 | NaN | NaN | NaN | NaN | 593.7318 | NaN | 24.9776 | NaN | 27.4086
5703.1292 | 13.7711 | 13.4754 | 13.494 | 13.8308 | 13.1296 | 13.5007 | 13.2675 | 13.0596 | NaN | NaN | NaN | 13.4203 | 94.1688 | NaN | NaN | NaN | 1.2503 | NaN | NaN | NaN | NaN | 593.1863 | NaN | 21.7002 | NaN | 26.2333
5704.1292 | 13.7357 | 13.4638 | 13.4979 | 13.8078 | 13.2447 | 13.5108 | 13.2709 | 13.0578 | NaN | NaN | NaN | 13.4788 | 93.6426 | NaN | NaN | NaN | 19.6422 | NaN | NaN | NaN | NaN | 593.045 | NaN | 24.005 | NaN | 26.5542
5705.1292 | 14.0305 | 13.4858 | 13.4994 | 13.8415 | 13.1806 | 13.541 | 13.266 | 13.0698 | NaN | NaN | NaN | 13.4298 | 91.6476 | NaN | NaN | NaN | 19.6179 | NaN | NaN | NaN | NaN | 590.7324 | NaN | 24.4489 | NaN | 29.243
5706.1292 | 13.7297 | 13.5198 | 13.4967 | 13.7964 | 13.1132 | 13.5051 | 13.2838 | 13.0692 | NaN | NaN | NaN | 13.4462 | 94.5178 | NaN | NaN | NaN | -18.0525 | NaN | NaN | NaN | NaN | 594.2718 | NaN | 26.3306 | NaN | 27.4369
5707.1292 | 13.867 | 13.3989 | 13.494 | 13.8049 | 13.0807 | 13.6157 | 13.2458 | 13.0713 | NaN | NaN | NaN | 13.4468 | 93.7807 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 593.632 | NaN | 24.3009 | NaN | 26.2871
5708.1292 | 13.7811 | 13.4095 | 13.4997 | 13.7683 | 13.1517 | 13.5109 | 13.2496 | 13.0722 | NaN | NaN | NaN | 13.4975 | 93.4035 | NaN | NaN | NaN | 43.301 | NaN | NaN | NaN | NaN | 591.4118 | NaN | 21.7053 | NaN | 26.4977
5709.1292 | 13.7474 | 13.39 | 13.4932 | 13.8405 | 13.0956 | 13.794 | 13.256 | 13.0788 | NaN | NaN | NaN | 13.4679 | 91.9634 | NaN | NaN | NaN | -0.0729 | NaN | NaN | NaN | NaN | 591.5967 | NaN | 27.5801 | NaN | 26.0284
5710.1292 | 13.7684 | 13.4153 | 13.4908 | 13.8315 | 13.126 | 13.5023 | 13.2715 | 13.0827 | NaN | NaN | NaN | 13.4269 | 92.688 | NaN | NaN | NaN | -17.5741 | NaN | NaN | NaN | NaN | 592.5442 | NaN | 24.0034 | NaN | 28.2573
5711.1292 | 13.7626 | 13.388 | 13.4805 | 13.896 | 13.1151 | 13.5463 | 13.2492 | 13.0852 | NaN | NaN | NaN | 13.4953 | 92.3623 | NaN | NaN | NaN | 18.9769 | NaN | NaN | NaN | NaN | 593.1584 | NaN | 24.7612 | NaN | 27.4562
5712.1292 | 13.732 | 13.4568 | 13.4799 | 13.7893 | 13.2605 | 13.5243 | 13.2655 | 13.0817 | NaN | NaN | NaN | 13.4207 | 94.3256 | NaN | NaN | NaN | -9.0385 | NaN | NaN | NaN | NaN | 588.3329 | NaN | 23.5039 | NaN | 27.261
5713.1292 | 13.8509 | 13.4238 | 13.4791 | 13.8117 | 13.0994 | 13.5199 | 13.2588 | 13.0929 | NaN | NaN | NaN | 13.4517 | 93.7674 | NaN | NaN | NaN | 21.6305 | NaN | NaN | NaN | NaN | 591.884 | NaN | 26.0248 | NaN | 27.0593
5714.1292 | 13.8216 | 13.4658 | 13.4732 | 13.78 | 13.167 | 13.541 | 13.2767 | 13.0941 | NaN | NaN | NaN | 13.43 | 92.8873 | NaN | NaN | NaN | 10.8777 | NaN | NaN | NaN | NaN | 592.6949 | NaN | 25.3401 | NaN | 26.209
5715.1292 | 13.7718 | 13.5617 | 13.4725 | 13.895 | 13.199 | 13.5291 | 13.2885 | 13.0906 | NaN | NaN | NaN | 13.4275 | 92.2313 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 591.0097 | NaN | 24.6541 | NaN | 25.3131
5716.1292 | 13.807 | 13.4152 | 13.4776 | 13.9108 | 13.2802 | 13.4984 | 13.2623 | 13.0962 | NaN | NaN | NaN | 13.4714 | 91.7858 | NaN | NaN | NaN | -8.1549 | NaN | NaN | NaN | NaN | 590.8464 | NaN | 26.3943 | NaN | 26.3948
5717.1292 | 13.7951 | 13.4574 | 13.4663 | 13.806 | 13.1839 | 13.5522 | 13.2805 | 13.086 | NaN | NaN | NaN | 13.456 | 94.2093 | NaN | NaN | NaN | 10.9443 | NaN | NaN | NaN | NaN | 592.4144 | NaN | 22.3324 | NaN | 26.8668
5718.1292 | 13.7691 | 13.4579 | 13.4694 | 13.8484 | 13.1436 | 13.5376 | 13.2746 | 13.0881 | NaN | NaN | NaN | 13.4539 | 92.5667 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 592.724 | NaN | 25.861 | NaN | 27.0002
5719.1292 | 13.8679 | 13.4165 | 13.4625 | 13.8547 | 13.2035 | 13.4907 | 13.2548 | 13.0913 | NaN | NaN | NaN | 13.4511 | 93.9653 | NaN | NaN | NaN | -16.3804 | NaN | NaN | NaN | NaN | 591.5375 | NaN | 22.9279 | NaN | 26.3727
5720.1292 | 13.8223 | 13.3895 | 13.4615 | 13.7934 | 13.1579 | 13.4844 | 13.2445 | 13.0881 | NaN | NaN | NaN | 13.4329 | 93.5428 | NaN | NaN | NaN | 18.6845 | NaN | NaN | NaN | NaN | 592.82 | NaN | 21.0729 | NaN | 27.062
5721.1292 | 13.8619 | 13.3795 | 13.4668 | 13.806 | 13.2457 | 13.4766 | 13.256 | 13.092 | NaN | NaN | NaN | 13.4517 | 92.5681 | NaN | NaN | NaN | 47.2991 | NaN | NaN | NaN | NaN | 595.5116 | NaN | 23.6645 | NaN | 27.6974
5722.1292 | 13.7499 | 13.3771 | 13.4701 | 13.8866 | 13.1577 | 13.4857 | 13.2584 | 13.0975 | NaN | NaN | NaN | 13.5736 | 92.7808 | NaN | NaN | NaN | 30.7935 | NaN | NaN | NaN | NaN | 594.9762 | NaN | 25.5451 | NaN | 28.9482
5723.1292 | 13.8683 | 13.5096 | 13.4712 | 13.7654 | 13.166 | 13.5075 | 13.2755 | 13.0952 | NaN | NaN | NaN | 13.4171 | 93.0493 | NaN | NaN | NaN | -4.7987 | NaN | NaN | NaN | NaN | 597.5506 | NaN | 23.1543 | NaN | 25.9626
5724.1292 | 13.8252 | 13.4527 | 13.4763 | 13.9081 | 13.2687 | 13.4718 | 13.2696 | 13.1049 | NaN | NaN | NaN | 13.5131 | 92.7046 | NaN | NaN | NaN | -18.4814 | NaN | NaN | NaN | NaN | 595.5069 | NaN | 23.4545 | NaN | 29.6556
5725.1292 | 13.8139 | 13.4069 | 13.4751 | 13.9208 | 13.1982 | 13.5128 | 13.249 | 13.1026 | NaN | NaN | NaN | 13.4457 | 91.9303 | NaN | NaN | NaN | 18.4927 | NaN | NaN | NaN | NaN | 595.3138 | NaN | 27.2833 | NaN | 27.9517
5726.1292 | 13.8123 | 13.3864 | 13.4787 | 13.8334 | 13.3094 | 13.5152 | 13.2434 | 13.1044 | NaN | NaN | NaN | 13.4508 | 93.7947 | NaN | NaN | NaN | 11.8852 | NaN | NaN | NaN | NaN | 595.4681 | NaN | 22.1069 | NaN | 28.9969
5727.1292 | 13.7612 | 13.3913 | 13.4798 | 13.8133 | 13.2194 | 13.4901 | 13.2492 | 13.1059 | NaN | NaN | NaN | 13.4872 | 107.4624 | NaN | NaN | NaN | 4.9271 | NaN | NaN | NaN | NaN | 595.1211 | NaN | 25.2288 | NaN | 26.8115
5728.1292 | 14.0162 | 13.4423 | 13.4859 | 13.8211 | 13.2098 | 13.5866 | 13.2577 | 13.1051 | NaN | NaN | NaN | 13.4368 | 92.0473 | NaN | NaN | NaN | 39.0841 | NaN | NaN | NaN | NaN | 598.5273 | NaN | 22.1039 | NaN | 28.3004
5729.1292 | 13.759 | 13.5439 | 13.4926 | 13.809 | 13.1757 | 13.6353 | 13.2738 | 13.0959 | NaN | NaN | NaN | 13.5024 | 92.1424 | NaN | NaN | NaN | -9.8137 | NaN | NaN | NaN | NaN | 597.6589 | NaN | 22.67 | NaN | 28.5675
5730.1292 | 13.7917 | 13.3767 | 13.4886 | 13.8063 | 13.1418 | 13.4989 | 13.2556 | 13.1083 | NaN | NaN | NaN | 13.5687 | 93.9516 | NaN | NaN | NaN | 20.5672 | NaN | NaN | NaN | NaN | 597.2523 | NaN | 23.9792 | NaN | 28.8833
5731.1292 | 13.8959 | 13.3956 | 13.4967 | 13.8035 | 13.1462 | 13.6415 | 13.2554 | 13.1036 | NaN | NaN | NaN | 13.5208 | 91.8921 | NaN | NaN | NaN | 3.6203 | NaN | NaN | NaN | NaN | 598.0353 | NaN | 25.2326 | NaN | 26.4542
5732.1292 | 13.8195 | 13.3922 | 13.5033 | 13.8156 | 13.1935 | 13.6292 | 13.2524 | 13.1096 | NaN | NaN | NaN | 13.4892 | 93.0616 | NaN | NaN | NaN | -5.51 | NaN | NaN | NaN | NaN | 598.4645 | NaN | 23.2046 | NaN | 25.8706
5733.1292 | 13.8449 | 13.417 | 13.5002 | 13.8197 | 13.2351 | 13.4858 | 13.2573 | 13.1061 | NaN | NaN | NaN | 13.4953 | 93.3843 | NaN | NaN | NaN | 3.1559 | NaN | NaN | NaN | NaN | 600.2743 | NaN | 24.0189 | NaN | 28.9711
5734.1292 | 13.8134 | 13.414 | 13.5017 | 13.7732 | 13.1447 | 13.4769 | 13.2449 | 13.1083 | NaN | NaN | NaN | 13.5029 | 92.2008 | NaN | NaN | NaN | 56.0673 | NaN | NaN | NaN | NaN | 600.9493 | NaN | 24.3731 | NaN | 26.8021
5735.1292 | 13.8964 | 13.4912 | 13.5077 | 13.8033 | 13.2506 | 13.5652 | 13.2709 | 13.1167 | NaN | NaN | NaN | 13.5609 | 92.7524 | NaN | NaN | NaN | 5.899 | NaN | NaN | NaN | NaN | 599.6648 | NaN | 25.5564 | NaN | 25.9729
5736.1292 | 13.8214 | 13.4441 | 13.5169 | 13.8373 | 13.1668 | 13.5024 | 13.2551 | 13.112 | NaN | NaN | NaN | 13.5481 | 94.517 | NaN | NaN | NaN | 20.7 | NaN | NaN | NaN | NaN | 600.6793 | NaN | 21.9695 | NaN | 29.1873
5737.1292 | 13.8302 | 13.3919 | 13.5183 | 13.7886 | 13.2333 | 13.598 | 13.2333 | 13.1079 | NaN | NaN | NaN | 13.4498 | 92.4285 | NaN | NaN | NaN | 20.1803 | NaN | NaN | NaN | NaN | 601.5908 | NaN | 25.4679 | NaN | 27.5586
5738.1292 | 13.7917 | 13.4633 | 13.5196 | 13.7864 | 13.1314 | 13.6318 | 13.2638 | 13.1069 | NaN | NaN | NaN | 13.4373 | 96.3358 | NaN | NaN | NaN | -10.1365 | NaN | NaN | NaN | NaN | 600.3122 | NaN | 21.0835 | NaN | 28.9909
5739.1292 | 13.874 | 13.4831 | 13.5212 | 13.7661 | 13.1483 | 13.5039 | 13.2847 | 13.1085 | NaN | NaN | NaN | 13.4759 | 102.2945 | NaN | NaN | NaN | 7.7766 | NaN | NaN | NaN | NaN | 595.5119 | NaN | 24.1374 | NaN | 26.8065
5740.1292 | 13.8109 | 13.4562 | 13.5199 | 13.7457 | 13.2273 | 13.5052 | 13.2641 | 13.106 | NaN | NaN | NaN | 13.539 | 92.6915 | NaN | NaN | NaN | 12.8109 | NaN | NaN | NaN | NaN | 600.0424 | NaN | 22.0154 | NaN | 28.5252
5741.1292 | 13.7761 | 13.4074 | 13.5182 | 13.8031 | 13.2543 | 13.5307 | 13.2507 | 13.1141 | NaN | NaN | NaN | 13.5025 | 92.5049 | NaN | NaN | NaN | -14.5571 | NaN | NaN | NaN | NaN | 598.994 | NaN | 21.739 | NaN | 27.9704
5742.1292 | 13.792 | 13.4298 | 13.523 | 13.9361 | 13.1274 | 13.5025 | 13.2738 | 13.1077 | NaN | NaN | NaN | 13.5213 | 93.0779 | NaN | NaN | NaN | -12.2727 | NaN | NaN | NaN | NaN | 599.5384 | NaN | 23.0308 | NaN | 26.7347
5743.1292 | 13.8064 | 13.4878 | 13.5271 | 13.8361 | 13.1854 | 13.5122 | 13.2725 | 13.1099 | NaN | NaN | NaN | 13.4535 | 93.1695 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 598.9851 | NaN | 24.2241 | NaN | 28.3451
5744.1292 | 13.8173 | 13.42 | 13.5226 | 13.8232 | 13.2033 | 13.5615 | 13.2596 | 13.1115 | NaN | NaN | NaN | 13.4513 | 93.7876 | NaN | NaN | NaN | 7.8971 | NaN | NaN | NaN | NaN | 597.2879 | NaN | 22.2043 | NaN | 27.1756
5745.1292 | 13.8199 | 13.4922 | 13.527 | 13.7864 | 13.2294 | 13.5817 | 13.27 | 13.1076 | NaN | NaN | NaN | 13.4746 | 93.5317 | NaN | NaN | NaN | 25.3755 | NaN | NaN | NaN | NaN | 598.8197 | NaN | 27.7441 | NaN | 26.7957
5746.1292 | 13.8088 | 13.5252 | 13.5348 | 13.7987 | 13.1652 | 13.6166 | 13.2642 | 13.1047 | NaN | NaN | NaN | 13.4156 | 91.2328 | NaN | NaN | NaN | 7.8823 | NaN | NaN | NaN | NaN | 596.2478 | NaN | 23.9446 | NaN | 27.3324
5747.1292 | 13.8189 | 13.5372 | 13.5379 | 13.7625 | 13.0767 | 13.6084 | 13.2631 | 13.11 | NaN | NaN | NaN | 13.4245 | 93.636 | NaN | NaN | NaN | 43.5747 | NaN | NaN | NaN | NaN | 597.6623 | NaN | 22.9036 | NaN | 27.9755
5748.1292 | 13.8169 | 13.462 | 13.5392 | 13.8191 | 13.2755 | 13.5894 | 13.2369 | 13.1134 | NaN | NaN | NaN | 13.4656 | 94.0611 | NaN | NaN | NaN | -17.7575 | NaN | NaN | NaN | NaN | 598.2462 | NaN | 21.6387 | NaN | 26.5628
5749.1292 | 14.1023 | 13.4782 | 13.5412 | 13.7581 | 13.247 | 13.5398 | 13.2379 | 13.1118 | NaN | NaN | NaN | 13.5202 | 93.0825 | NaN | NaN | NaN | -14.324 | NaN | NaN | NaN | NaN | 599.948 | NaN | 24.6472 | NaN | 28.7571
5750.1292 | 13.8362 | 13.4451 | 13.5417 | 13.7331 | 13.304 | 13.6577 | 13.2403 | 13.1078 | NaN | NaN | NaN | 13.4234 | 93.7137 | NaN | NaN | NaN | -3.004 | NaN | NaN | NaN | NaN | 600.6237 | NaN | 21.2245 | NaN | 26.8206
5751.1292 | 13.8276 | 13.5824 | 13.5393 | 13.7801 | 13.1709 | 13.5134 | 13.2615 | 13.1066 | NaN | NaN | NaN | 13.4575 | 94.0321 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 598.6581 | NaN | 21.8521 | NaN | 29.2407
5752.1292 | 13.9015 | 13.435 | 13.5332 | 13.7321 | 13.1813 | 13.6321 | 13.229 | 13.1024 | NaN | NaN | NaN | 13.4963 | 91.6493 | NaN | NaN | NaN | -16.3146 | NaN | NaN | NaN | NaN | 601.5206 | NaN | 26.081 | NaN | 28.4216
5753.1292 | 13.8202 | 13.4632 | 13.5297 | 13.7562 | 13.1699 | 13.5241 | 13.2503 | 13.1039 | NaN | NaN | NaN | 13.4134 | 91.7657 | NaN | NaN | NaN | 8.5886 | NaN | NaN | NaN | NaN | 599.9411 | NaN | 23.0307 | NaN | 26.1864
5754.1292 | 13.8056 | 13.5087 | 13.5242 | 13.7116 | 13.2192 | 13.6421 | 13.2607 | 13.0996 | NaN | NaN | NaN | 13.4376 | 92.8084 | NaN | NaN | NaN | -18.026 | NaN | NaN | NaN | NaN | 599.7147 | NaN | 27.4373 | NaN | 27.44
5755.1292 | 13.7865 | 13.4998 | 13.5201 | 13.7814 | 13.2757 | 13.5545 | 13.2569 | 13.095 | NaN | NaN | NaN | 13.4033 | 92.6353 | NaN | NaN | NaN | 29.9097 | NaN | NaN | NaN | NaN | 598.7362 | NaN | 20.4878 | NaN | 28.3768
5756.1292 | 13.8285 | 13.5156 | 13.518 | 13.8138 | 13.332 | 13.6099 | 13.266 | 13.0988 | NaN | NaN | NaN | 13.4505 | 91.7928 | NaN | NaN | NaN | 23.2436 | NaN | NaN | NaN | NaN | 602.1355 | NaN | 22.0206 | NaN | 29.2947
5757.1292 | 13.8161 | 13.4555 | 13.5146 | 13.8377 | 13.2075 | 13.5338 | 13.2614 | 13.0988 | NaN | NaN | NaN | 13.4596 | 92.1634 | NaN | NaN | NaN | -18.2048 | NaN | NaN | NaN | NaN | 602.3837 | NaN | 22.8419 | NaN | 26.991
5758.1292 | 13.8671 | 13.619 | 13.5115 | 13.784 | 13.1958 | 13.7205 | 13.3179 | 13.1007 | NaN | NaN | NaN | 13.5032 | 94.4128 | NaN | NaN | NaN | -2.1433 | NaN | NaN | NaN | NaN | 602.7615 | NaN | 21.1734 | NaN | 26.8129
5759.1292 | 13.8775 | 13.5431 | 13.5116 | 13.7388 | 13.1623 | 13.5248 | 13.2839 | 13.1001 | NaN | NaN | NaN | 13.4506 | 94.0959 | NaN | NaN | NaN | 13.0572 | NaN | NaN | NaN | NaN | 603.4871 | NaN | 22.5965 | NaN | 25.8152
5760.1292 | 13.8814 | 13.461 | 13.511 | 13.7928 | 13.2237 | 13.5514 | 13.264 | 13.1007 | NaN | NaN | NaN | 13.43 | 93.1545 | NaN | NaN | NaN | -10.0836 | NaN | NaN | NaN | NaN | 603.1715 | NaN | 24.3214 | NaN | 24.7541
5761.1292 | 13.8645 | 13.4767 | 13.5117 | 13.8731 | 13.3048 | 13.5753 | 13.2624 | 13.1093 | NaN | NaN | NaN | 13.5249 | 93.4484 | NaN | NaN | NaN | 56.816 | NaN | NaN | NaN | NaN | 598.6171 | NaN | 21.8991 | NaN | 26.4311
5762.1292 | 13.8477 | 13.5126 | 13.5078 | 13.7954 | 13.305 | 13.5172 | 13.2935 | 13.1061 | NaN | NaN | NaN | 13.4227 | 92.9381 | NaN | NaN | NaN | -8.5316 | NaN | NaN | NaN | NaN | 605.9263 | NaN | 21.1783 | NaN | 29.2701
5763.1292 | 13.8364 | 13.4696 | 13.5046 | 13.8282 | 13.2317 | 13.5302 | 13.2548 | 13.1096 | NaN | NaN | NaN | 13.5576 | 92.825 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 604.12 | NaN | 21.7939 | NaN | 25.7915
5764.1292 | 13.8103 | 13.4478 | 13.505 | 13.8142 | 13.1683 | 13.5599 | 13.2616 | 13.1126 | NaN | NaN | NaN | 13.4869 | 93.7363 | NaN | NaN | NaN | -6.1419 | NaN | NaN | NaN | NaN | 604.3037 | NaN | 22.3891 | NaN | 25.1249
5765.1292 | 13.894 | 13.5313 | 13.5008 | 13.8183 | 13.1462 | 13.5509 | 13.2786 | 13.1121 | NaN | NaN | NaN | 13.4226 | 92.5398 | NaN | NaN | NaN | -15.877 | NaN | NaN | NaN | NaN | 600.655 | NaN | 23.7631 | NaN | 27.233
5766.1292 | 13.8037 | 13.5235 | 13.4925 | 13.7712 | 13.266 | 13.5744 | 13.2932 | 13.1144 | NaN | NaN | NaN | 13.4486 | 92.5166 | NaN | NaN | NaN | -2.9909 | NaN | NaN | NaN | NaN | 603.235 | NaN | 21.1727 | NaN | 27.2902
5767.1292 | 13.8327 | 13.4961 | 13.4814 | 13.8123 | 13.2446 | 13.5806 | 13.2892 | 13.1116 | NaN | NaN | NaN | 13.4721 | 95.387 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 604.8439 | NaN | 22.0115 | NaN | 28.3084
5768.1292 | 13.9338 | 13.4724 | 13.4884 | 13.8588 | 13.2013 | 13.5206 | 13.2743 | 13.115 | NaN | NaN | NaN | 13.3968 | 95.068 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 603.2278 | NaN | 22.626 | NaN | 27.8572
5769.1292 | 13.8015 | 13.4693 | 13.4809 | 13.7918 | 13.2237 | 13.5423 | 13.2835 | 13.1119 | NaN | NaN | NaN | 13.4633 | 93.2518 | NaN | NaN | NaN | -4.9826 | NaN | NaN | NaN | NaN | 608.4774 | NaN | 22.7625 | NaN | 27.2281
5770.1292 | 13.8055 | 13.4503 | 13.4852 | 13.8141 | 13.1384 | 13.5313 | 13.2639 | 13.1104 | NaN | NaN | NaN | 13.5758 | 91.668 | NaN | NaN | NaN | 5.7304 | NaN | NaN | NaN | NaN | 605.9396 | NaN | 22.3306 | NaN | 25.8501
5771.1292 | 13.7863 | 13.5218 | 13.4884 | 13.7898 | 13.3058 | 13.5484 | 13.2951 | 13.1124 | NaN | NaN | NaN | 13.4772 | 95.339 | NaN | NaN | NaN | -16.5512 | NaN | NaN | NaN | NaN | 603.8945 | NaN | 22.0974 | NaN | 26.4357
5772.1292 | 13.8196 | 13.4407 | 13.5017 | 13.8131 | 13.2447 | 13.5309 | 13.2898 | 13.1093 | NaN | NaN | NaN | 13.4297 | 91.6805 | NaN | NaN | NaN | 0.5765 | NaN | NaN | NaN | NaN | 605.3595 | NaN | 22.7074 | NaN | 27.4777
5773.1292 | 13.8184 | 13.4716 | 13.5012 | 13.8697 | 13.2239 | 13.5334 | 13.3059 | 13.113 | NaN | NaN | NaN | 13.5169 | 92.4318 | NaN | NaN | NaN | 7.7326 | NaN | NaN | NaN | NaN | 605.6536 | NaN | 21.4544 | NaN | 28.537
5774.1292 | 13.986 | 13.4244 | 13.511 | 13.8387 | 13.2124 | 13.668 | 13.2742 | 13.1135 | NaN | NaN | NaN | 13.6185 | 93.4493 | NaN | NaN | NaN | 25.2434 | NaN | NaN | NaN | NaN | 606.3843 | NaN | 21.354 | NaN | 26.2147
5775.1292 | 13.803 | 13.4577 | 13.5104 | 13.8549 | 13.1735 | 13.541 | 13.2925 | 13.112 | NaN | NaN | NaN | 13.5111 | 92.837 | NaN | NaN | NaN | -15.5713 | NaN | NaN | NaN | NaN | 606.076 | NaN | 23.1915 | NaN | 27.8272
5776.1292 | 14.175 | 13.4821 | 13.5191 | 13.7777 | 13.1917 | 13.6284 | 13.2954 | 13.1099 | NaN | NaN | NaN | 13.4182 | 91.2533 | NaN | NaN | NaN | 13.4371 | NaN | NaN | NaN | NaN | 606.978 | NaN | 23.4955 | NaN | 27.4043
5777.1292 | 13.8603 | 13.4509 | 13.5241 | 13.8466 | 13.165 | 13.5621 | 13.2857 | 13.1123 | NaN | NaN | NaN | 13.4568 | 92.4726 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 607.0664 | NaN | 20.3679 | NaN | 26.0635
5778.1292 | 13.8279 | 13.4258 | 13.5242 | 13.7757 | 13.3879 | 13.558 | 13.2732 | 13.1111 | NaN | NaN | NaN | 13.5615 | 93.1203 | NaN | NaN | NaN | -13.0504 | NaN | NaN | NaN | NaN | 607.267 | NaN | 23.4504 | NaN | 25.1846
5779.1292 | 13.7866 | 13.4896 | 13.5256 | 13.8022 | 13.1692 | 13.536 | 13.2913 | 13.1077 | NaN | NaN | NaN | 13.4713 | 93.5638 | NaN | NaN | NaN | -15.4307 | NaN | NaN | NaN | NaN | 609.8056 | NaN | 22.9838 | NaN | 27.5164
5780.1292 | 14.0157 | 13.468 | 13.5295 | 13.8416 | 13.3536 | 13.5601 | 13.2928 | 13.113 | NaN | NaN | NaN | 13.4458 | 91.6257 | NaN | NaN | NaN | 7.5486 | NaN | NaN | NaN | NaN | 608.5175 | NaN | 23.2399 | NaN | 27.0649
5781.1292 | 13.8122 | 13.4087 | 13.5329 | 13.8459 | 13.2234 | 13.5774 | 13.2597 | 13.1138 | NaN | NaN | NaN | 13.4896 | 91.6078 | NaN | NaN | NaN | -17.8705 | NaN | NaN | NaN | NaN | 608.9832 | NaN | 22.2406 | NaN | 27.3624
5782.1292 | 13.7887 | 13.482 | 13.5328 | 13.8746 | 13.1761 | 13.5643 | 13.3032 | 13.1077 | NaN | NaN | NaN | 13.4598 | 95.5205 | NaN | NaN | NaN | -6.9406 | NaN | NaN | NaN | NaN | 608.7866 | NaN | 24.8596 | NaN | 26.108
5783.1292 | 13.8212 | 13.4714 | 13.5338 | 13.875 | 13.1669 | 13.6663 | 13.305 | 13.0992 | NaN | NaN | NaN | 13.4418 | 93.9412 | NaN | NaN | NaN | -16.8504 | NaN | NaN | NaN | NaN | 611.738 | NaN | 22.5063 | NaN | 26.9027
5784.1292 | 13.814 | 13.4258 | 13.5311 | 13.8837 | 13.1487 | 13.5451 | 13.2682 | 13.1022 | NaN | NaN | NaN | 13.5705 | 94.5976 | NaN | NaN | NaN | -13.4382 | NaN | NaN | NaN | NaN | 607.5649 | NaN | 22.8526 | NaN | 26.4725
5785.1292 | 13.8235 | 13.4581 | 13.5258 | 13.8362 | 13.2681 | 13.5991 | 13.2865 | 13.0967 | NaN | NaN | NaN | 13.4371 | 92.6264 | NaN | NaN | NaN | 2.4578 | NaN | NaN | NaN | NaN | 609.3109 | NaN | 23.6344 | NaN | 29.2702
5786.1292 | 14.0662 | 13.5329 | 13.5291 | 13.8517 | 13.2979 | 13.658 | 13.2991 | 13.1009 | NaN | NaN | NaN | 13.4431 | 92.1459 | NaN | NaN | NaN | 8.9996 | NaN | NaN | NaN | NaN | 608.2206 | NaN | 22.2613 | NaN | 29.599
5787.1292 | 13.8045 | 13.4999 | 13.5169 | 13.8799 | 13.2076 | 13.6331 | 13.2961 | 13.0958 | NaN | NaN | NaN | 13.5438 | 92.4398 | NaN | NaN | NaN | -0.5288 | NaN | NaN | NaN | NaN | 610.7361 | NaN | 22.4843 | NaN | 27.6665
5788.1292 | 13.8416 | 13.6259 | 13.5199 | 13.8612 | 13.2462 | 13.5529 | 13.3148 | 13.0945 | NaN | NaN | NaN | 13.4107 | 91.2555 | NaN | NaN | NaN | -16.0456 | NaN | NaN | NaN | NaN | 612.8818 | NaN | 22.5649 | NaN | 28.0464
5789.1292 | 13.7676 | 13.6206 | 13.5248 | 13.8781 | 13.1814 | 13.5516 | 13.3314 | 13.1056 | NaN | NaN | NaN | 13.4504 | 93.3317 | NaN | NaN | NaN | -12.6442 | NaN | NaN | NaN | NaN | 611.1723 | NaN | 22.0009 | NaN | 25.9292
5790.1292 | 13.7865 | 13.568 | 13.522 | 13.8195 | 13.3384 | 13.7107 | 13.2993 | 13.1107 | NaN | NaN | NaN | 13.6744 | 94.0242 | NaN | NaN | NaN | 2.1232 | NaN | NaN | NaN | NaN | 613.2895 | NaN | 22.2317 | NaN | 25.711
5791.1292 | 13.8168 | 13.4371 | 13.5301 | 13.85 | 13.166 | 13.5483 | 13.2953 | 13.1086 | NaN | NaN | NaN | 13.4534 | 92.8197 | NaN | NaN | NaN | 13.8682 | NaN | NaN | NaN | NaN | 615.1633 | NaN | 24.4301 | NaN | 28.1003
5792.1292 | 13.8326 | 13.4963 | 13.5311 | 13.8163 | 13.2124 | 13.5551 | 13.3113 | 13.1106 | NaN | NaN | NaN | 13.5557 | 92.7553 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 612.8387 | NaN | 22.0281 | NaN | 26.0332
5793.1292 | 13.7788 | 13.5632 | 13.5389 | 13.8273 | 13.2854 | 13.5547 | 13.321 | 13.1176 | NaN | NaN | NaN | 13.5093 | 89.821 | NaN | NaN | NaN | -15.8362 | NaN | NaN | NaN | NaN | 616.4321 | NaN | 21.9362 | NaN | 25.0826
5794.1292 | 13.8441 | 13.5516 | 13.5369 | 13.8306 | 13.2792 | 13.7163 | 13.3209 | 13.1151 | NaN | NaN | NaN | 13.4329 | 92.4555 | NaN | NaN | NaN | 22.0213 | NaN | NaN | NaN | NaN | 613.7031 | NaN | 23.149 | NaN | 28.4678
5795.1292 | 13.8383 | 13.4786 | 13.5265 | 13.8743 | 13.3599 | 13.6094 | 13.2922 | 13.1153 | NaN | NaN | NaN | 13.4479 | 92.0686 | NaN | NaN | NaN | -14.182 | NaN | NaN | NaN | NaN | 612.3953 | NaN | 23.0017 | NaN | 26.433
5796.1292 | 13.8165 | 13.4551 | 13.5278 | 13.8492 | 13.4302 | 13.5749 | 13.3054 | 13.1159 | NaN | NaN | NaN | 13.4897 | 93.3167 | NaN | NaN | NaN | -4.4551 | NaN | NaN | NaN | NaN | 615.4874 | NaN | 23.6416 | NaN | 28.6091
5797.1292 | 13.8169 | 13.5062 | 13.5233 | 13.849 | 13.2883 | 13.585 | 13.3066 | 13.1192 | NaN | NaN | NaN | 13.4938 | 95.323 | NaN | NaN | NaN | -13.0373 | NaN | NaN | NaN | NaN | 614.3068 | NaN | 22.0466 | NaN | 28.1584
5798.1292 | 13.7725 | 13.629 | 13.5263 | 13.8875 | 13.3304 | 13.7635 | 13.3163 | 13.1076 | NaN | NaN | NaN | 13.5375 | 90.9887 | NaN | NaN | NaN | 50.7193 | NaN | NaN | NaN | NaN | 615.5399 | NaN | 23.6657 | NaN | 26.8151
5799.1292 | 13.8755 | 13.4612 | 13.5297 | 13.8849 | 13.3407 | 13.6321 | 13.2894 | 13.1084 | NaN | NaN | NaN | 13.5548 | 92.6768 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 611.214 | NaN | 21.7591 | NaN | 27.1893
5800.1292 | 13.8164 | 13.4505 | 13.5404 | 13.9027 | 13.2867 | 13.6135 | 13.2972 | 13.1024 | NaN | NaN | NaN | 13.4813 | 91.9095 | NaN | NaN | NaN | 4.0813 | NaN | NaN | NaN | NaN | 617.7019 | NaN | 24.3299 | NaN | 27.6535
5801.1292 | 13.8372 | 13.4525 | 13.5407 | 13.8117 | 13.2475 | 13.7802 | 13.2887 | 13.107 | NaN | NaN | NaN | 13.5007 | 92.2176 | NaN | NaN | NaN | 27.7112 | NaN | NaN | NaN | NaN | 618.7053 | NaN | 22.9286 | NaN | 26.8336
5802.1292 | 13.8253 | 13.5028 | 13.5364 | 13.8211 | 13.1287 | 13.605 | 13.3014 | 13.1078 | NaN | NaN | NaN | 13.4487 | 92.759 | NaN | NaN | NaN | -2.2715 | NaN | NaN | NaN | NaN | 618.6567 | NaN | 22.7814 | NaN | 27.6114
5803.1292 | 13.7726 | 13.4761 | 13.5421 | 13.8806 | 13.1697 | 13.682 | 13.2928 | 13.113 | NaN | NaN | NaN | 13.4997 | 91.9972 | NaN | NaN | NaN | 0.1477 | NaN | NaN | NaN | NaN | 619.0642 | NaN | 22.7168 | NaN | 28.3684
5804.1292 | 13.8426 | 13.5283 | 13.5419 | 13.8947 | 13.0776 | 13.6381 | 13.2992 | 13.1161 | NaN | NaN | NaN | 13.4642 | 92.1136 | NaN | NaN | NaN | 6.2549 | NaN | NaN | NaN | NaN | 622.2221 | NaN | 23.7315 | NaN | 26.3312
5805.1292 | 13.8583 | 13.4822 | 13.5384 | 13.8512 | 13.2473 | 13.6013 | 13.3015 | 13.1145 | NaN | NaN | NaN | 13.4111 | 94.8704 | NaN | NaN | NaN | 9.9923 | NaN | NaN | NaN | NaN | 621.6079 | NaN | 24.2694 | NaN | 26.5474
5806.1292 | 13.8893 | 13.4443 | 13.542 | 13.8589 | 13.234 | 13.5958 | 13.2762 | 13.116 | NaN | NaN | NaN | 13.5192 | 92.6469 | NaN | NaN | NaN | -8.1733 | NaN | NaN | NaN | NaN | 621.0436 | NaN | 22.3556 | NaN | 24.4909
5807.1292 | 13.852 | 13.5071 | 13.5419 | 13.8576 | 13.3579 | 13.5702 | 13.3143 | 13.1121 | NaN | NaN | NaN | 13.51 | 92.9731 | NaN | NaN | NaN | -6.8699 | NaN | NaN | NaN | NaN | 622.1969 | NaN | 22.7069 | NaN | 27.9064
5808.1292 | 13.8438 | 13.5129 | 13.5442 | 13.8119 | 13.3094 | 13.7048 | 13.3089 | 13.1124 | NaN | NaN | NaN | 13.4696 | 93.6566 | NaN | NaN | NaN | 4.3241 | NaN | NaN | NaN | NaN | 621.7069 | NaN | 20.1711 | NaN | 27.2017
5809.1292 | 13.9275 | 13.5928 | 13.5404 | 13.8174 | 13.2214 | 13.5791 | 13.3459 | 13.1181 | NaN | NaN | NaN | 13.4582 | 93.2648 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 622.1123 | NaN | 22.7579 | NaN | 28.4743
5810.1292 | 13.8272 | 13.4854 | 13.5386 | 13.8802 | 13.2408 | 13.5683 | 13.2924 | 13.1176 | NaN | NaN | NaN | 13.449 | 93.3642 | NaN | NaN | NaN | -18.8468 | NaN | NaN | NaN | NaN | 623.1491 | NaN | 22.8501 | NaN | 25.251
5811.1292 | 13.8207 | 13.5314 | 13.5431 | 13.909 | 13.3021 | 13.5797 | 13.3166 | 13.1094 | NaN | NaN | NaN | 13.5167 | 93.0099 | NaN | NaN | NaN | 53.9215 | NaN | NaN | NaN | NaN | 621.313 | NaN | 21.6684 | NaN | 25.7824
5812.1448 | 13.8384 | 13.5943 | 13.5412 | 13.9271 | 13.3369 | 13.6374 | 13.3407 | 13.1187 | NaN | NaN | NaN | 13.4253 | 90.6432 | NaN | NaN | NaN | -19.9883 | NaN | NaN | NaN | NaN | 620.5481 | NaN | 21.4148 | NaN | 25.1503
5813.1292 | 13.845 | 13.4939 | 13.5442 | 13.8539 | 13.1465 | 13.6131 | 13.3221 | 13.1218 | NaN | NaN | NaN | 13.4437 | 93.1944 | NaN | NaN | NaN | -18.9371 | NaN | NaN | NaN | NaN | 622.2281 | NaN | 22.6502 | NaN | 28.5313
5814.1292 | 13.8222 | 13.4975 | 13.5359 | 13.8873 | 13.3746 | 13.5873 | 13.3161 | 13.1199 | NaN | NaN | NaN | 13.5147 | 95.9848 | NaN | NaN | NaN | -13.3888 | NaN | NaN | NaN | NaN | 618.5495 | NaN | 24.1905 | NaN | 26.922
5815.1292 | 13.8792 | 13.5095 | 13.542 | 13.8853 | 13.3108 | 13.5798 | 13.3165 | 13.1214 | NaN | NaN | NaN | 13.4381 | 93.2728 | NaN | NaN | NaN | 39.4348 | NaN | NaN | NaN | NaN | 614.6317 | NaN | 23.075 | NaN | 27.7368
5816.1292 | 14.5169 | 13.4919 | 13.5473 | 13.9389 | 13.183 | 13.587 | 13.2986 | 13.1141 | NaN | NaN | NaN | 13.5492 | 93.4883 | NaN | NaN | NaN | 18.9478 | NaN | NaN | NaN | NaN | 615.2793 | NaN | 22.4105 | NaN | 25.4995
5817.1292 | 13.8775 | 13.5403 | 13.5472 | 13.9291 | 13.3453 | 13.5876 | 13.3221 | 13.1199 | NaN | NaN | NaN | 13.599 | 94.1146 | NaN | NaN | NaN | -17.7091 | NaN | NaN | NaN | NaN | 616.5083 | NaN | 24.318 | NaN | 25.1126
5818.1292 | 13.8834 | 13.5097 | 13.5433 | 13.884 | 13.2601 | 13.6839 | 13.32 | 13.1242 | NaN | NaN | NaN | 13.4361 | 93.087 | NaN | NaN | NaN | 45.3246 | NaN | NaN | NaN | NaN | 615.1612 | NaN | 23.8261 | NaN | 26.9187
5819.1292 | 13.8726 | 13.5348 | 13.5494 | 14.1677 | 13.3199 | 13.6263 | 13.3113 | 13.1253 | NaN | NaN | NaN | 13.5778 | 94.1953 | NaN | NaN | NaN | 23.4573 | NaN | NaN | NaN | NaN | 614.3134 | NaN | 21.9624 | NaN | 27.9805
5820.1292 | 13.8498 | 13.4887 | 13.5487 | 13.8849 | 13.2128 | 13.6111 | 13.3001 | 13.1258 | NaN | NaN | NaN | 13.4761 | 93.1442 | NaN | NaN | NaN | -1.3815 | NaN | NaN | NaN | NaN | 614.6547 | NaN | 23.7733 | NaN | 25.7431
5821.1292 | 13.8557 | 13.4848 | 13.5516 | 13.9008 | 13.2956 | 13.6194 | 13.3029 | 13.1167 | NaN | NaN | NaN | 13.4691 | 92.7896 | NaN | NaN | NaN | 3.3958 | NaN | NaN | NaN | NaN | 616.2884 | NaN | 24.155 | NaN | 27.1081
5822.1292 | 13.8483 | 13.5194 | 13.5571 | 13.9063 | 13.2603 | 13.5975 | 13.3182 | 13.1151 | NaN | NaN | NaN | 13.4522 | 93.4566 | NaN | NaN | NaN | -7.8646 | NaN | NaN | NaN | NaN | 617.3217 | NaN | 22.1242 | NaN | 27.2902
5823.1292 | 13.8536 | 13.5726 | 13.5602 | 13.909 | 13.3629 | 13.5782 | 13.3321 | 13.1206 | NaN | NaN | NaN | 13.5033 | 92.5947 | NaN | NaN | NaN | 1.4812 | NaN | NaN | NaN | NaN | 615.2299 | NaN | 23.7267 | NaN | 26.2156
5824.1292 | 13.8951 | 13.5328 | 13.5621 | 13.9567 | 13.3739 | 13.677 | 13.3109 | 13.1206 | NaN | NaN | NaN | 13.4718 | 94.7405 | NaN | NaN | NaN | -15.8524 | NaN | NaN | NaN | NaN | 616.0979 | NaN | 21.8596 | NaN | 27.6246
5825.1292 | 13.845 | 13.6267 | 13.5526 | 13.9023 | 13.3967 | 13.6474 | 13.3516 | 13.1203 | NaN | NaN | NaN | 13.4954 | 97.1872 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 614.4732 | NaN | 22.8124 | NaN | 26.6734
5826.1292 | 13.8607 | 13.5266 | 13.5607 | 13.8227 | 13.3717 | 13.578 | 13.3139 | 13.1148 | NaN | NaN | NaN | 13.4634 | 93.2849 | NaN | NaN | NaN | -3.7888 | NaN | NaN | NaN | NaN | 613.1561 | NaN | 23.7835 | NaN | 27.2194
5827.1292 | 13.8648 | 13.5359 | 13.5545 | 13.8827 | 13.3371 | 13.5656 | 13.3187 | 13.116 | NaN | NaN | NaN | 13.4942 | 92.8964 | NaN | NaN | NaN | -17.5776 | NaN | NaN | NaN | NaN | 617.3205 | NaN | 24.2054 | NaN | 26.4654
5828.1292 | 13.9106 | 13.53 | 13.5526 | 13.9214 | 13.2494 | 13.5845 | 13.3264 | 13.1216 | NaN | NaN | NaN | 13.4843 | 92.8447 | NaN | NaN | NaN | -8.4407 | NaN | NaN | NaN | NaN | 613.4884 | NaN | 23.815 | NaN | 26.5216
5829.1292 | 13.9086 | 13.5158 | 13.5487 | 13.9298 | 13.1536 | 13.5789 | 13.3151 | 13.116 | NaN | NaN | NaN | 13.5082 | 93.4459 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 612.073 | NaN | 25.9471 | NaN | 27.4814
5830.1292 | 13.8816 | 13.5331 | 13.542 | 13.8867 | 13.2239 | 13.6594 | 13.3393 | 13.1214 | NaN | NaN | NaN | 13.5318 | 94.429 | NaN | NaN | NaN | 0.0829 | NaN | NaN | NaN | NaN | 614.9811 | NaN | 23.9433 | NaN | 27.4114
5831.1292 | 13.8843 | 13.6099 | 13.5475 | 13.9065 | 13.3451 | 13.6008 | 13.3508 | 13.1193 | NaN | NaN | NaN | 13.5919 | 94.3261 | NaN | NaN | NaN | -8.8616 | NaN | NaN | NaN | NaN | 612.1783 | NaN | 22.9726 | NaN | 24.9339
5832.1292 | 13.9353 | 13.4957 | 13.5387 | 13.8965 | 13.3726 | 13.606 | 13.3098 | 13.116 | NaN | NaN | NaN | 13.4677 | 92.9023 | NaN | NaN | NaN | 31.5099 | NaN | NaN | NaN | NaN | 610.2813 | NaN | 25.6901 | NaN | 26.0881
5833.1292 | 13.8937 | 13.5159 | 13.5471 | 13.8782 | 13.2265 | 13.5914 | 13.3359 | 13.1187 | NaN | NaN | NaN | 13.5009 | 95.6197 | NaN | NaN | NaN | -1.4441 | NaN | NaN | NaN | NaN | 614.6896 | NaN | 24.6413 | NaN | 26.9609
5834.1292 | 13.8559 | 13.5311 | 13.5449 | 13.927 | 13.297 | 13.6161 | 13.3223 | 13.1163 | NaN | NaN | NaN | 13.4873 | 93.5065 | NaN | NaN | NaN | 43.3399 | NaN | NaN | NaN | NaN | 615.1611 | NaN | 24.4063 | NaN | 26.263
5835.1292 | 13.9278 | 13.7376 | 13.5577 | 13.9155 | 13.3818 | 13.6472 | 13.3732 | 13.1121 | NaN | NaN | NaN | 13.5112 | 95.5428 | NaN | NaN | NaN | 18.0077 | NaN | NaN | NaN | NaN | 610.9873 | NaN | 25.6288 | NaN | 29.4926
5836.1292 | 13.9947 | 13.6434 | 13.5595 | 13.8951 | 13.2238 | 13.8153 | 13.3387 | 13.1234 | NaN | NaN | NaN | 13.4711 | 93.9506 | NaN | NaN | NaN | -8.2066 | NaN | NaN | NaN | NaN | 611.1642 | NaN | 22.1586 | NaN | 26.5404
5837.1292 | 13.8837 | 13.5438 | 13.5569 | 13.9095 | 13.2337 | 13.6045 | 13.3324 | 13.1235 | NaN | NaN | NaN | 13.4931 | 92.9524 | NaN | NaN | NaN | -0.5627 | NaN | NaN | NaN | NaN | 610.6879 | NaN | 25.3551 | NaN | 27.0741
5838.1292 | 13.8507 | 13.7113 | 13.5583 | 13.9354 | 13.1222 | 13.6011 | 13.3914 | 13.1225 | NaN | NaN | NaN | 13.4911 | 94.042 | NaN | NaN | NaN | 4.4661 | NaN | NaN | NaN | NaN | 610.1929 | NaN | 24.2077 | NaN | 26.7613
5839.1292 | 13.9198 | 13.5277 | 13.5566 | 13.8884 | 13.291 | 13.6128 | 13.3266 | 13.1244 | NaN | NaN | NaN | 13.4467 | 93.8465 | NaN | NaN | NaN | -1.9748 | NaN | NaN | NaN | NaN | 608.9323 | NaN | 25.5236 | NaN | 27.4862
5840.1292 | 13.8734 | 13.4987 | 13.5552 | 13.8794 | 13.3306 | 13.6047 | 13.3103 | 13.1275 | NaN | NaN | NaN | 13.5197 | 94.9396 | NaN | NaN | NaN | 13.9286 | NaN | NaN | NaN | NaN | 609.7351 | NaN | 27.78 | NaN | 26.3385
5841.1292 | 13.8748 | 13.4931 | 13.5573 | 13.8536 | 13.2669 | 13.6278 | 13.3103 | 13.1243 | NaN | NaN | NaN | 13.5004 | 93.0706 | NaN | NaN | NaN | 52.4665 | NaN | NaN | NaN | NaN | 610.3793 | NaN | 23.8783 | NaN | 27.4094
5842.1292 | 13.8726 | 13.4827 | 13.559 | 13.98 | 13.2011 | 13.6114 | 13.3103 | 13.1267 | NaN | NaN | NaN | 13.555 | 92.9555 | NaN | NaN | NaN | -19.7833 | NaN | NaN | NaN | NaN | 610.4289 | NaN | 25.4774 | NaN | 26.3986
5843.1292 | 13.9771 | 13.5797 | 13.5635 | 13.9008 | 13.3013 | 13.7521 | 13.3363 | 13.1344 | NaN | NaN | NaN | 13.4534 | 96.2966 | NaN | NaN | NaN | -0.0211 | NaN | NaN | NaN | NaN | 607.0854 | NaN | 25.8901 | NaN | 27.5046
5844.1292 | 13.9073 | 13.5073 | 13.5658 | 13.9179 | 13.2394 | 13.6306 | 13.3295 | 13.1362 | NaN | NaN | NaN | 13.4266 | 95.3375 | NaN | NaN | NaN | 6.7982 | NaN | NaN | NaN | NaN | 607.576 | NaN | 24.6768 | NaN | 28.6074
5845.1292 | 13.9343 | 13.4707 | 13.5603 | 13.9348 | 13.223 | 13.6659 | 13.3181 | 13.1322 | NaN | NaN | NaN | 13.4617 | 92.8634 | NaN | NaN | NaN | 56.6528 | NaN | NaN | NaN | NaN | 610.4574 | NaN | 24.9964 | NaN | 26.2985
5846.1292 | 14.037 | 13.5121 | 13.5636 | 13.9017 | 13.3258 | 13.684 | 13.3265 | 13.1378 | NaN | NaN | NaN | 13.4435 | 91.7081 | NaN | NaN | NaN | -15.4265 | NaN | NaN | NaN | NaN | 604.549 | NaN | 25.2047 | NaN | 28.3188
5847.1292 | 13.8846 | 13.5382 | 13.5621 | 13.9066 | 13.4306 | 13.6791 | 13.3137 | 13.1368 | NaN | NaN | NaN | 13.4265 | 92.629 | NaN | NaN | NaN | 0.8505 | NaN | NaN | NaN | NaN | 605.6085 | NaN | 25.6557 | NaN | 26.7675
5848.1292 | 14.0689 | 13.527 | 13.5733 | 13.8679 | 13.3485 | 13.6455 | 13.3232 | 13.1408 | NaN | NaN | NaN | 13.4174 | 92.7086 | NaN | NaN | NaN | 53.0982 | NaN | NaN | NaN | NaN | 606.2313 | NaN | 24.8492 | NaN | 27.2781
5849.1292 | 14.0259 | 13.5911 | 13.5702 | 13.8643 | 13.2073 | 13.64 | 13.3218 | 13.1465 | NaN | NaN | NaN | 13.4636 | 93.2973 | NaN | NaN | NaN | 7.1932 | NaN | NaN | NaN | NaN | 604.5915 | NaN | 24.8216 | NaN | 26.1464
5850.1292 | 13.9762 | 13.5385 | 13.5667 | 13.8933 | 13.2267 | 13.6417 | 13.3307 | 13.139 | NaN | NaN | NaN | 13.4473 | 92.8182 | NaN | NaN | NaN | -18.2142 | NaN | NaN | NaN | NaN | 606.6165 | NaN | 25.7704 | NaN | 26.7954
5851.1292 | 13.8746 | 13.5151 | 13.5604 | 13.8725 | 13.2508 | 13.6777 | 13.3099 | 13.1451 | NaN | NaN | NaN | 13.4332 | 93.4889 | NaN | NaN | NaN | -12.9807 | NaN | NaN | NaN | NaN | 610.0319 | NaN | 25.9229 | NaN | 27.4818
5852.1292 | 13.8828 | 13.5171 | 13.5646 | 13.8278 | 13.3043 | 13.7166 | 13.3057 | 13.1488 | NaN | NaN | NaN | 13.4836 | 92.7372 | NaN | NaN | NaN | -5.858 | NaN | NaN | NaN | NaN | 608.6235 | NaN | 25.7849 | NaN | 27.9785
5853.1292 | 13.8982 | 13.5313 | 13.5661 | 13.8753 | 13.2341 | 13.8115 | 13.3263 | 13.1539 | NaN | NaN | NaN | 13.4839 | 92.0986 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 608.8727 | NaN | 26.558 | NaN | 27.8338
5854.1292 | 13.8689 | 13.5068 | 13.5719 | 13.9178 | 13.2804 | 13.6066 | 13.2959 | 13.1504 | NaN | NaN | NaN | 13.4971 | 93.0062 | NaN | NaN | NaN | -18.3479 | NaN | NaN | NaN | NaN | 607.2264 | NaN | 26.8828 | NaN | 28.0415
5855.1292 | 13.9218 | 13.5221 | 13.5731 | 13.8475 | 13.3851 | 13.6887 | 13.2994 | 13.1464 | NaN | NaN | NaN | 13.4654 | 92.6058 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 607.5737 | NaN | 24.0884 | NaN | 28.4506
5856.1292 | 13.9079 | 13.4905 | 13.578 | 13.8846 | 13.1453 | 13.7227 | 13.3222 | 13.1451 | NaN | NaN | NaN | 13.4705 | 93.5367 | NaN | NaN | NaN | -19.0628 | NaN | NaN | NaN | NaN | 607.6652 | NaN | 25.1878 | NaN | 25.4992
5857.1292 | 13.9395 | 13.4935 | 13.5786 | 13.8854 | 13.3562 | 13.6763 | 13.2918 | 13.1463 | NaN | NaN | NaN | 13.4618 | 93.8429 | NaN | NaN | NaN | 48.679 | NaN | NaN | NaN | NaN | 610.8323 | NaN | 25.5735 | NaN | 26.6376
5858.1292 | 13.8899 | 13.5231 | 13.5712 | 13.9731 | 13.2823 | 13.6322 | 13.3202 | 13.1459 | NaN | NaN | NaN | 13.5241 | 94.11 | NaN | NaN | NaN | -18.6437 | NaN | NaN | NaN | NaN | 608.1821 | NaN | 25.0442 | NaN | 26.93
5859.1292 | 13.8884 | 13.589 | 13.5671 | 13.9438 | 13.2703 | 13.6393 | 13.3481 | 13.1418 | NaN | NaN | NaN | 13.509 | 94.3135 | NaN | NaN | NaN | 0.9262 | NaN | NaN | NaN | NaN | 608.5058 | NaN | 24.0697 | NaN | 27.9412
5860.1292 | 13.9777 | 13.5522 | 13.5632 | 13.8838 | 13.2769 | 13.6351 | 13.3179 | 13.1362 | NaN | NaN | NaN | 13.4407 | 94.4824 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 607.4681 | NaN | 26.6777 | NaN | 28.7788
5861.1292 | 13.9113 | 13.5807 | 13.5681 | 13.908 | 13.2229 | 13.6157 | 13.3352 | 13.1342 | NaN | NaN | NaN | 13.5057 | 92.3768 | NaN | NaN | NaN | 59.9047 | NaN | NaN | NaN | NaN | 606.1633 | NaN | 25.2136 | NaN | 27.4756
5862.1292 | 13.9101 | 13.5895 | 13.5718 | 13.8744 | 13.3812 | 13.6412 | 13.3394 | 13.1289 | NaN | NaN | NaN | 13.6177 | 94.11 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 606.4064 | NaN | 26.4176 | NaN | 25.35
5863.1292 | 13.904 | 13.4868 | 13.5689 | 13.8797 | 13.3401 | 13.6322 | 13.3138 | 13.1323 | NaN | NaN | NaN | 13.5034 | 94.2358 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 608.128 | NaN | 27.6826 | NaN | 27.6359
5864.1292 | 13.8911 | 13.4768 | 13.5736 | 13.8759 | 13.2301 | 13.6692 | 13.3112 | 13.1285 | NaN | NaN | NaN | 13.5022 | 94.8009 | NaN | NaN | NaN | 24.4067 | NaN | NaN | NaN | NaN | 607.5976 | NaN | 23.9487 | NaN | 27.5155
5865.1292 | 13.895 | 13.4902 | 13.571 | 13.9122 | 13.3089 | 13.5912 | 13.31 | 13.1178 | NaN | NaN | NaN | 13.4731 | 93.9215 | NaN | NaN | NaN | 1.0994 | NaN | NaN | NaN | NaN | 607.4364 | NaN | 25.089 | NaN | 28.2861
5866.1292 | 13.9747 | 13.5576 | 13.5724 | 13.9137 | 13.2649 | 13.6243 | 13.3357 | 13.1285 | NaN | NaN | NaN | 13.4525 | 92.1399 | NaN | NaN | NaN | 10.7755 | NaN | NaN | NaN | NaN | 608.9618 | NaN | 25.4909 | NaN | 26.9128
5867.1292 | 13.9057 | 13.6576 | 13.5784 | 13.8614 | 13.2695 | 13.6325 | 13.3441 | 13.1212 | NaN | NaN | NaN | 13.4581 | 92.3498 | NaN | NaN | NaN | -16.9483 | NaN | NaN | NaN | NaN | 606.879 | NaN | 24.3464 | NaN | 28.7734
5868.1292 | 14.6192 | 13.4595 | 13.5687 | 13.9749 | 13.3359 | 13.6237 | 13.3146 | 13.116 | NaN | NaN | NaN | 13.5554 | 92.8186 | NaN | NaN | NaN | 53.6783 | NaN | NaN | NaN | NaN | 606.6333 | NaN | 27.2143 | NaN | 26.5113
5869.1292 | 13.9098 | 13.5237 | 13.5799 | 13.9075 | 13.3891 | 13.6083 | 13.3308 | 13.1215 | NaN | NaN | NaN | 13.4832 | 92.2707 | NaN | NaN | NaN | 58.695 | NaN | NaN | NaN | NaN | 606.887 | NaN | 24.7422 | NaN | 28.2563
5870.1292 | 13.9033 | 13.5787 | 13.5799 | 13.8907 | 13.3144 | 13.654 | 13.3339 | 13.119 | NaN | NaN | NaN | 13.481 | 91.8375 | NaN | NaN | NaN | -15.0353 | NaN | NaN | NaN | NaN | 608.6647 | NaN | 25.5411 | NaN | 27.2644
5871.1292 | 13.9218 | 13.4767 | 13.5831 | 13.9352 | 13.3118 | 13.677 | 13.3137 | 13.1237 | NaN | NaN | NaN | 13.4541 | 92.7699 | NaN | NaN | NaN | 21.3412 | NaN | NaN | NaN | NaN | 608.0974 | NaN | 26.8139 | NaN | 27.9284
5872.1292 | 13.928 | 13.5201 | 13.5859 | 13.8586 | 13.3486 | 13.6622 | 13.3294 | 13.1232 | NaN | NaN | NaN | 13.53 | 93.3848 | NaN | NaN | NaN | 4.3957 | NaN | NaN | NaN | NaN | 608.7723 | NaN | 23.7081 | NaN | 26.3203
5873.1292 | 13.8621 | 13.5491 | 13.5906 | 13.9386 | 13.2504 | 13.6752 | 13.3381 | 13.1278 | NaN | NaN | NaN | 13.4576 | 90.3763 | NaN | NaN | NaN | -14.5418 | NaN | NaN | NaN | NaN | 607.5345 | NaN | 25.9754 | NaN | 29.0657
5874.1292 | 13.9245 | 13.4656 | 13.5888 | 13.9087 | 13.1895 | 13.6494 | 13.3269 | 13.122 | NaN | NaN | NaN | 13.4892 | 92.1337 | NaN | NaN | NaN | 7.3675 | NaN | NaN | NaN | NaN | 611.5321 | NaN | 27.7082 | NaN | 29.0392
5875.1292 | 13.9138 | 13.659 | 13.5892 | 14.0797 | 13.3533 | 13.6149 | 13.373 | 13.1243 | NaN | NaN | NaN | 13.5061 | 93.7218 | NaN | NaN | NaN | -18.3825 | NaN | NaN | NaN | NaN | 610.452 | NaN | 24.2772 | NaN | 25.8448
5876.1292 | 13.9215 | 13.4927 | 13.5962 | 13.9106 | 13.3788 | 13.5999 | 13.3292 | 13.1227 | NaN | NaN | NaN | 13.4911 | 93.4815 | NaN | NaN | NaN | 3.3091 | NaN | NaN | NaN | NaN | 607.7802 | NaN | 24.1999 | NaN | 28.0151
5877.1292 | 14.1047 | 13.5102 | 13.5989 | 13.8869 | 13.3792 | 13.6177 | 13.3267 | 13.1256 | NaN | NaN | NaN | 13.4757 | 92.0859 | NaN | NaN | NaN | -15.2877 | NaN | NaN | NaN | NaN | 608.5757 | NaN | 26.7942 | NaN | 27.7893
5878.1292 | 13.8869 | 13.5198 | 13.5942 | 13.8691 | 13.2968 | 13.6204 | 13.3382 | 13.1277 | NaN | NaN | NaN | 13.4977 | 94.6243 | NaN | NaN | NaN | -14.7507 | NaN | NaN | NaN | NaN | 612.2808 | NaN | 25.7914 | NaN | 25.7711
5879.1292 | 13.926 | 13.7839 | 13.5914 | 13.911 | 13.3495 | 13.6216 | 13.4198 | 13.1281 | NaN | NaN | NaN | 13.4806 | 93.3091 | NaN | NaN | NaN | -3.5025 | NaN | NaN | NaN | NaN | 612.8497 | NaN | 25.6018 | NaN | 28.6318
5880.1292 | 13.8675 | 13.6122 | 13.5941 | 13.9467 | 13.3246 | 13.6423 | 13.3622 | 13.1259 | NaN | NaN | NaN | 13.4552 | 92.1908 | NaN | NaN | NaN | -18.6018 | NaN | NaN | NaN | NaN | 611.0118 | NaN | 23.3497 | NaN | 27.9773
5881.1292 | 13.9362 | 13.5489 | 13.6023 | 13.8984 | 13.2858 | 13.6042 | 13.342 | 13.1262 | NaN | NaN | NaN | 13.5893 | 92.6975 | NaN | NaN | NaN | 0.9766 | NaN | NaN | NaN | NaN | 610.9083 | NaN | 25.0413 | NaN | 27.1493
5882.1292 | 13.9346 | 13.6672 | 13.6124 | 13.901 | 13.3566 | 13.6207 | 13.3568 | 13.1293 | NaN | NaN | NaN | 13.4668 | 92.5144 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 611.5803 | NaN | 27.1759 | NaN | 26.5344
5883.1292 | 13.9762 | 13.4916 | 13.6053 | 13.8894 | 13.4476 | 13.5936 | 13.3295 | 13.1249 | NaN | NaN | NaN | 13.4623 | 90.0797 | NaN | NaN | NaN | 4.8684 | NaN | NaN | NaN | NaN | 612.5389 | NaN | 26.7453 | NaN | 27.2178
5884.1292 | 13.9244 | 13.5153 | 13.604 | 13.8889 | 13.3142 | 13.5866 | 13.3249 | 13.1334 | NaN | NaN | NaN | 13.5071 | 93.5524 | NaN | NaN | NaN | -2.0573 | NaN | NaN | NaN | NaN | 613.9974 | NaN | 25.1006 | NaN | 26.688
5885.1292 | 13.8967 | 13.5082 | 13.6148 | 13.9206 | 13.3402 | 13.5913 | 13.3306 | 13.1248 | NaN | NaN | NaN | 13.5309 | 93.2322 | NaN | NaN | NaN | 0.2776 | NaN | NaN | NaN | NaN | 610.2655 | NaN | 28.0117 | NaN | 26.8083
5886.1292 | 13.919 | 13.565 | 13.6194 | 13.9057 | 13.347 | 13.6773 | 13.3538 | 13.1242 | NaN | NaN | NaN | 13.4449 | 95.4647 | NaN | NaN | NaN | 9.0156 | NaN | NaN | NaN | NaN | 610.6994 | NaN | 26.5453 | NaN | 27.7085
5887.1292 | 13.985 | 13.5311 | 13.6086 | 13.9156 | 13.2067 | 13.6558 | 13.3354 | 13.1249 | NaN | NaN | NaN | 13.4609 | 92.9685 | NaN | NaN | NaN | 41.3639 | NaN | NaN | NaN | NaN | 610.3939 | NaN | 26.041 | NaN | 27.0844
5888.1292 | 13.9671 | 13.5514 | 13.6103 | 13.8591 | 13.3207 | 13.6696 | 13.3349 | 13.1232 | NaN | NaN | NaN | 13.5214 | 92.5906 | NaN | NaN | NaN | 27.2701 | NaN | NaN | NaN | NaN | 611.8471 | NaN | 25.6566 | NaN | 27.614
5889.1292 | 13.9002 | 13.5228 | 13.6158 | 13.8835 | 13.3369 | 13.6742 | 13.3297 | 13.1209 | NaN | NaN | NaN | 13.4342 | 92.1839 | NaN | NaN | NaN | 35.7037 | NaN | NaN | NaN | NaN | 612.5511 | NaN | 25.7004 | NaN | 27.1445
5890.1292 | 13.908 | 13.569 | 13.6158 | 13.9125 | 13.2761 | 13.5761 | 13.323 | 13.1308 | NaN | NaN | NaN | 13.5023 | 95.083 | NaN | NaN | NaN | -8.2011 | NaN | NaN | NaN | NaN | 613.2382 | NaN | 26.18 | NaN | 29.3023
5891.1292 | 13.8955 | 13.5558 | 13.614 | 13.8937 | 13.2312 | 13.5885 | 13.3361 | 13.1232 | NaN | NaN | NaN | 13.5006 | 93.1259 | NaN | NaN | NaN | 10.6988 | NaN | NaN | NaN | NaN | 614.5646 | NaN | 26.0891 | NaN | 27.4018
5892.1292 | 14.0305 | 13.5254 | 13.617 | 13.9464 | 13.3086 | 13.6365 | 13.3231 | 13.1187 | NaN | NaN | NaN | 13.5133 | 92.3106 | NaN | NaN | NaN | 29.8332 | NaN | NaN | NaN | NaN | 613.3226 | NaN | 22.8629 | NaN | 26.9123
5893.1292 | 13.8779 | 13.5113 | 13.6098 | 13.8999 | 13.2885 | 13.5821 | 13.3354 | 13.1234 | NaN | NaN | NaN | 13.4832 | 94.0985 | NaN | NaN | NaN | -8.9816 | NaN | NaN | NaN | NaN | 617.0082 | NaN | 20.5899 | NaN | 24.8576
5894.1292 | 14.0172 | 13.5934 | 13.6122 | 13.8795 | 13.3458 | 13.5719 | 13.3498 | 13.1226 | NaN | NaN | NaN | 13.4674 | 93.0372 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 616.7761 | NaN | 28.2462 | NaN | 28.7508
5895.1292 | 13.9106 | 13.5218 | 13.6165 | 13.908 | 13.3107 | 13.6112 | 13.324 | 13.1244 | NaN | NaN | NaN | 13.5856 | 91.4282 | NaN | NaN | NaN | -5.4411 | NaN | NaN | NaN | NaN | 617.8726 | NaN | 26.2293 | NaN | 26.2175
5896.1292 | 13.8813 | 13.7757 | 13.6196 | 13.9152 | 13.2485 | 13.6069 | 13.3867 | 13.1268 | NaN | NaN | NaN | 13.5009 | 92.6001 | NaN | NaN | NaN | -19.6061 | NaN | NaN | NaN | NaN | 619.8481 | NaN | 22.9914 | NaN | 27.3149
5897.1292 | 13.9274 | 13.5179 | 13.6235 | 13.8519 | 13.2989 | 13.5698 | 13.3355 | 13.1288 | NaN | NaN | NaN | 13.5845 | 90.971 | NaN | NaN | NaN | 56.6823 | NaN | NaN | NaN | NaN | 619.9024 | NaN | 27.1164 | NaN | 27.6803
5898.1292 | 13.9131 | 13.5278 | 13.6172 | 13.8852 | 13.2766 | 13.6282 | 13.3419 | 13.1295 | NaN | NaN | NaN | 13.5778 | 90.9485 | NaN | NaN | NaN | 3.5358 | NaN | NaN | NaN | NaN | 620.6058 | NaN | 23.8929 | NaN | 25.6712
5899.1292 | 13.9601 | 13.5573 | 13.6216 | 13.8631 | 13.3509 | 13.6204 | 13.3499 | 13.1274 | NaN | NaN | NaN | 13.5292 | 91.6397 | NaN | NaN | NaN | 11.5208 | NaN | NaN | NaN | NaN | 622.3172 | NaN | 26.473 | NaN | 25.2145
5900.1292 | 13.9313 | 13.5794 | 13.6216 | 13.8955 | 13.3853 | 13.64 | 13.3442 | 13.1327 | NaN | NaN | NaN | 13.5817 | 92.4233 | NaN | NaN | NaN | -19.8408 | NaN | NaN | NaN | NaN | 621.0162 | NaN | 25.6913 | NaN | 25.9271
5901.1292 | 13.9168 | 13.572 | 13.6262 | 13.8865 | 13.2343 | 13.6383 | 13.3401 | 13.132 | NaN | NaN | NaN | 13.4634 | 96.6615 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 622.8452 | NaN | 27.0087 | NaN | 26.9014
5902.1292 | 13.8792 | 13.6201 | 13.6165 | 13.9014 | 13.2776 | 13.6265 | 13.3493 | 13.1302 | NaN | NaN | NaN | 13.5649 | 94.6425 | NaN | NaN | NaN | -4.2218 | NaN | NaN | NaN | NaN | 624.0325 | NaN | 23.2712 | NaN | 24.6633
5903.1292 | 13.9021 | 13.6747 | 13.617 | 13.914 | 13.3689 | 13.6019 | 13.382 | 13.1323 | NaN | NaN | NaN | 13.4886 | 90.8194 | NaN | NaN | NaN | 36.173 | NaN | NaN | NaN | NaN | 622.8534 | NaN | 25.6052 | NaN | 27.1669
5904.1292 | 13.8595 | 13.5808 | 13.6252 | 13.9129 | 13.2075 | 13.6085 | 13.3439 | 13.145 | NaN | NaN | NaN | 13.5571 | 92.7806 | NaN | NaN | NaN | -10.2442 | NaN | NaN | NaN | NaN | 624.9415 | NaN | 22.9707 | NaN | 28.5053
5905.1292 | 13.892 | 13.5618 | 13.6274 | 13.8803 | 13.3564 | 13.5775 | 13.3302 | 13.1396 | NaN | NaN | NaN | 13.4921 | 93.2491 | NaN | NaN | NaN | -11.4504 | NaN | NaN | NaN | NaN | 626.9428 | NaN | 25.1765 | NaN | 27.0686
5906.1292 | 13.9602 | 13.5757 | 13.6303 | 13.899 | 13.2778 | 13.7133 | 13.3271 | 13.1428 | NaN | NaN | NaN | 13.5579 | 92.8507 | NaN | NaN | NaN | 1.4561 | NaN | NaN | NaN | NaN | 622.9284 | NaN | 25.6259 | NaN | 26.7923
5907.1292 | 13.8877 | 13.549 | 13.6265 | 13.9047 | 13.3135 | 13.5869 | 13.3171 | 13.1401 | NaN | NaN | NaN | 13.5417 | 93.8566 | NaN | NaN | NaN | 8.0235 | NaN | NaN | NaN | NaN | 626.5385 | NaN | 26.4518 | NaN | 27.2053
5908.1292 | 13.8722 | 13.5685 | 13.6245 | 13.9325 | 13.3758 | 13.6727 | 13.3228 | 13.1373 | NaN | NaN | NaN | 13.4926 | 92.3378 | NaN | NaN | NaN | -16.4148 | NaN | NaN | NaN | NaN | 626.5486 | NaN | 26.8868 | NaN | 27.1343
5909.1292 | 13.9592 | 13.5467 | 13.6273 | 13.9124 | 13.2674 | 13.6247 | 13.3201 | 13.1403 | NaN | NaN | NaN | 13.471 | 92.1746 | NaN | NaN | NaN | -11.0579 | NaN | NaN | NaN | NaN | 626.6097 | NaN | 24.6164 | NaN | 26.887
5910.1292 | 13.8683 | 13.5658 | 13.6226 | 13.8986 | 13.3495 | 13.5884 | 13.316 | 13.1369 | NaN | NaN | NaN | 13.6677 | 93.6336 | NaN | NaN | NaN | -10.9441 | NaN | NaN | NaN | NaN | 624.9191 | NaN | 26.1867 | NaN | 27.1967
5911.1292 | 13.8932 | 13.5557 | 13.6301 | 13.8849 | 13.3277 | 13.6988 | 13.3183 | 13.1368 | NaN | NaN | NaN | 13.5434 | 92.524 | NaN | NaN | NaN | 10.1015 | NaN | NaN | NaN | NaN | 624.5193 | NaN | 26.96 | NaN | 27.81
5912.1292 | 13.9025 | 13.5738 | 13.6236 | 13.8656 | 13.3326 | 13.6174 | 13.3254 | 13.1311 | NaN | NaN | NaN | 13.4654 | 93.2392 | NaN | NaN | NaN | 46.4679 | NaN | NaN | NaN | NaN | 623.1965 | NaN | 25.5645 | NaN | 26.363
5913.1292 | 13.9568 | 13.5773 | 13.623 | 13.8898 | 13.2958 | 13.6102 | 13.333 | 13.135 | NaN | NaN | NaN | 13.4765 | 91.5539 | NaN | NaN | NaN | -16.1292 | NaN | NaN | NaN | NaN | 626.2608 | NaN | 24.9825 | NaN | 28.1495
5914.1292 | 14.0244 | 13.57 | 13.6225 | 13.9021 | 13.3306 | 13.6335 | 13.3131 | 13.1402 | NaN | NaN | NaN | 13.4698 | 92.2113 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 623.7885 | NaN | 27.1282 | NaN | 27.3562
5915.1292 | 13.9348 | 13.5488 | 13.6206 | 13.8823 | 13.3747 | 13.6885 | 13.3331 | 13.1359 | NaN | NaN | NaN | 13.4993 | 93.0351 | NaN | NaN | NaN | 20.7816 | NaN | NaN | NaN | NaN | 626.6668 | NaN | 26.5316 | NaN | 28.6265
5916.1292 | 13.9247 | 13.5509 | 13.6257 | 13.9094 | 13.4373 | 13.619 | 13.3159 | 13.1427 | NaN | NaN | NaN | 13.5994 | 95.4377 | NaN | NaN | NaN | 30.6956 | NaN | NaN | NaN | NaN | 623.7851 | NaN | 28.9129 | NaN | 24.3
5917.1292 | 14.0332 | 13.5645 | 13.6235 | 13.9083 | 13.3241 | 13.6242 | 13.3188 | 13.1347 | NaN | NaN | NaN | 13.5489 | 92.478 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 627.6483 | NaN | 26.6359 | NaN | 27.8515
5918.1292 | 13.9995 | 13.7223 | 13.6291 | 13.9075 | 13.2367 | 13.6594 | 13.3581 | 13.1351 | NaN | NaN | NaN | 13.5655 | 90.2294 | NaN | NaN | NaN | 16.8427 | NaN | NaN | NaN | NaN | 628.8202 | NaN | 23.6861 | NaN | 28.1543
5919.1292 | 13.9255 | 13.5803 | 13.6189 | 13.9114 | 13.3554 | 13.5908 | 13.3234 | 13.135 | NaN | NaN | NaN | 13.6312 | 93.8848 | NaN | NaN | NaN | 6.1665 | NaN | NaN | NaN | NaN | 631.0868 | NaN | 24.7981 | NaN | 25.7904
5920.1292 | 13.9263 | 13.6288 | 13.624 | 13.8693 | 13.3745 | 13.6052 | 13.333 | 13.1212 | NaN | NaN | NaN | 13.4651 | 92.8592 | NaN | NaN | NaN | 30.7769 | NaN | NaN | NaN | NaN | 632.249 | NaN | 24.5422 | NaN | 29.109
5921.1292 | 13.9707 | 13.5459 | 13.6177 | 13.9299 | 13.295 | 13.5764 | 13.3114 | 13.1275 | NaN | NaN | NaN | 13.499 | 92.0516 | NaN | NaN | NaN | -1.3888 | NaN | NaN | NaN | NaN | 629.9951 | NaN | 25.888 | NaN | 27.7794
5922.1292 | 13.9429 | 13.5801 | 13.6166 | 13.9417 | 13.4191 | 13.6008 | 13.3208 | 13.1198 | NaN | NaN | NaN | 13.5616 | 90.2003 | NaN | NaN | NaN | 15.6826 | NaN | NaN | NaN | NaN | 628.9572 | NaN | 23.9029 | NaN | 28.7299
5923.1292 | 13.9533 | 13.5976 | 13.6221 | 13.8903 | 13.434 | 13.6756 | 13.3411 | 13.1234 | NaN | NaN | NaN | 13.5328 | 91.9039 | NaN | NaN | NaN | 43.4868 | NaN | NaN | NaN | NaN | 630.412 | NaN | 26.6719 | NaN | 28.5671
5924.1292 | 13.9556 | 13.6087 | 13.6199 | 13.9031 | 13.2784 | 13.6051 | 13.3201 | 13.1248 | NaN | NaN | NaN | 13.5194 | 93.4355 | NaN | NaN | NaN | -2.1044 | NaN | NaN | NaN | NaN | 628.607 | NaN | 21.7366 | NaN | 27.8603
5925.1292 | 13.8686 | 13.5737 | 13.6253 | 13.9116 | 13.371 | 13.5733 | 13.3132 | 13.1334 | NaN | NaN | NaN | 13.5341 | 92.5817 | NaN | NaN | NaN | 24.4265 | NaN | NaN | NaN | NaN | 630.5383 | NaN | 26.4995 | NaN | 26.3194
5926.1292 | 13.8907 | 13.6364 | 13.6218 | 13.8628 | 13.3371 | 13.5865 | 13.3375 | 13.1255 | NaN | NaN | NaN | 13.5569 | 95.665 | NaN | NaN | NaN | 6.7462 | NaN | NaN | NaN | NaN | 629.1712 | NaN | 21.3398 | NaN | 27.1397
5927.1292 | 13.8947 | 13.6043 | 13.6167 | 13.9417 | 13.4104 | 13.591 | 13.3214 | 13.1297 | NaN | NaN | NaN | 13.6426 | 93.7051 | NaN | NaN | NaN | -1.3758 | NaN | NaN | NaN | NaN | 628.3326 | NaN | 26.3639 | NaN | 30.0017
5928.1292 | 13.8866 | 13.6056 | 13.6266 | 13.8676 | 13.2545 | 13.5877 | 13.3386 | 13.129 | NaN | NaN | NaN | 13.5099 | 94.0641 | NaN | NaN | NaN | -18.1784 | NaN | NaN | NaN | NaN | 631.3896 | NaN | 27.4681 | NaN | 28.6564
5929.1292 | 13.9234 | 13.7241 | 13.6292 | 13.9034 | 13.3437 | 13.5825 | 13.3396 | 13.1307 | NaN | NaN | NaN | 13.4977 | 92.5683 | NaN | NaN | NaN | 23.5566 | NaN | NaN | NaN | NaN | 631.4425 | NaN | 22.1729 | NaN | 27.2825
5930.1292 | 13.9189 | 13.5609 | 13.6346 | 13.9187 | 13.3214 | 13.6892 | 13.318 | 13.1327 | NaN | NaN | NaN | 13.4616 | 95.4877 | NaN | NaN | NaN | 5.1504 | NaN | NaN | NaN | NaN | 634.265 | NaN | 25.5397 | NaN | 28.4564
5931.1292 | 13.9093 | 13.5565 | 13.6361 | 13.9205 | 13.3823 | 13.5817 | 13.2921 | 13.1352 | NaN | NaN | NaN | 13.5017 | 94.1083 | NaN | NaN | NaN | 1.6035 | NaN | NaN | NaN | NaN | 634.7658 | NaN | 22.9235 | NaN | 26.5957
5932.1292 | 13.8854 | 13.5848 | 13.6292 | 13.9109 | 13.337 | 13.6199 | 13.3219 | 13.1335 | NaN | NaN | NaN | 13.5224 | 93.1608 | NaN | NaN | NaN | 18.4955 | NaN | NaN | NaN | NaN | 633.1071 | NaN | 27.275 | NaN | 28.007
5933.1292 | 13.9015 | 13.5506 | 13.6276 | 13.9409 | 13.3724 | 13.5897 | 13.302 | 13.1389 | NaN | NaN | NaN | 13.565 | 92.2906 | NaN | NaN | NaN | 14.0294 | NaN | NaN | NaN | NaN | 632.9732 | NaN | 23.7987 | NaN | 25.5403
5934.1292 | 13.8852 | 13.636 | 13.6294 | 13.8761 | 13.3403 | 13.6487 | 13.3338 | 13.1404 | NaN | NaN | NaN | 13.4988 | 91.9951 | NaN | NaN | NaN | -4.267 | NaN | NaN | NaN | NaN | 630.8211 | NaN | 24.9323 | NaN | 24.3443
5935.1292 | 13.8523 | 13.7212 | 13.6192 | 13.8611 | 13.2442 | 13.6092 | 13.3329 | 13.1443 | NaN | NaN | NaN | 13.538 | 102.001 | NaN | NaN | NaN | 11.8298 | NaN | NaN | NaN | NaN | 630.6322 | NaN | 26.5954 | NaN | 27.042
5936.1292 | 13.8849 | 13.5364 | 13.6172 | 13.9087 | 13.1965 | 13.6823 | 13.299 | 13.143 | NaN | NaN | NaN | 13.5219 | 91.9055 | NaN | NaN | NaN | 2.3924 | NaN | NaN | NaN | NaN | 634.8878 | NaN | 23.9782 | NaN | 26.7027
5937.1292 | 13.8477 | 13.5824 | 13.618 | 13.8916 | 13.3332 | 13.6585 | 13.3281 | 13.14 | NaN | NaN | NaN | 13.5122 | 92.9995 | NaN | NaN | NaN | 60.7568 | NaN | NaN | NaN | NaN | 632.1413 | NaN | 26.589 | NaN | 26.7926
5938.1292 | 13.8394 | 13.5996 | 13.612 | 13.9212 | 13.2633 | 13.6759 | 13.3274 | 13.1433 | NaN | NaN | NaN | 13.4664 | 93.2082 | NaN | NaN | NaN | -16.2736 | NaN | NaN | NaN | NaN | 632.6777 | NaN | 26.0609 | NaN | 27.7003
5939.1292 | 13.8686 | 13.5713 | 13.6164 | 13.8857 | 13.3373 | 13.6631 | 13.322 | 13.1438 | NaN | NaN | NaN | 13.5628 | 93.7499 | NaN | NaN | NaN | -17.6408 | NaN | NaN | NaN | NaN | 633.14 | NaN | 25.3217 | NaN | 27.9286
5940.1292 | 13.8763 | 13.5686 | 13.6155 | 13.9135 | 13.378 | 13.6733 | 13.315 | 13.1395 | NaN | NaN | NaN | 13.541 | 92.4442 | NaN | NaN | NaN | 8.8487 | NaN | NaN | NaN | NaN | 630.5052 | NaN | 24.6428 | NaN | 26.9151
5941.1292 | 13.9014 | 13.5788 | 13.6162 | 14.0041 | 13.2337 | 13.6251 | 13.3276 | 13.1399 | NaN | NaN | NaN | 13.5272 | 93.5456 | NaN | NaN | NaN | -0.5689 | NaN | NaN | NaN | NaN | 630.3339 | NaN | 26.2862 | NaN | 27.1825
5942.1292 | 13.9781 | 13.5506 | 13.6198 | 13.9115 | 13.2725 | 13.6927 | 13.3254 | 13.1425 | NaN | NaN | NaN | 13.5245 | 93.0479 | NaN | NaN | NaN | 40.0777 | NaN | NaN | NaN | NaN | 633.6175 | NaN | 22.1662 | NaN | 26.5545
5943.1292 | 13.8966 | 13.5667 | 13.6225 | 13.9064 | 13.2724 | 13.6709 | 13.3214 | 13.155 | NaN | NaN | NaN | 13.4865 | 91.7667 | NaN | NaN | NaN | -13.3535 | NaN | NaN | NaN | NaN | 633.5663 | NaN | 25.2964 | NaN | 26.1241
5944.1292 | 13.9296 | 13.6108 | 13.6254 | 13.9934 | 13.3163 | 13.7272 | 13.3312 | 13.1545 | NaN | NaN | NaN | 13.5523 | 93.2276 | NaN | NaN | NaN | -1.7411 | NaN | NaN | NaN | NaN | 630.6345 | NaN | 24.3958 | NaN | 29.5456
5945.1292 | 13.935 | 13.7177 | 13.6246 | 13.9018 | 13.2246 | 13.6389 | 13.3529 | 13.1566 | NaN | NaN | NaN | 13.479 | 92.7573 | NaN | NaN | NaN | 21.9119 | NaN | NaN | NaN | NaN | 633.2935 | NaN | 24.4525 | NaN | 27.8416
5946.1292 | 13.8951 | 13.8957 | 13.6181 | 13.8984 | 13.2291 | 13.5973 | 13.4014 | 13.1601 | NaN | NaN | NaN | 13.5002 | 92.107 | NaN | NaN | NaN | -14.4195 | NaN | NaN | NaN | NaN | 632.0322 | NaN | 25.492 | NaN | 27.0855
5947.1292 | 13.8899 | 13.5418 | 13.6257 | 13.9096 | 13.32 | 13.7343 | 13.3166 | 13.1604 | NaN | NaN | NaN | 13.484 | 93.4353 | NaN | NaN | NaN | 43.0659 | NaN | NaN | NaN | NaN | 633.6774 | NaN | 23.233 | NaN | 27.3486
5948.1292 | 13.8842 | 13.5831 | 13.6265 | 13.9314 | 13.2719 | 13.7024 | 13.3317 | 13.1636 | NaN | NaN | NaN | 13.4919 | 92.417 | NaN | NaN | NaN | -5.9014 | NaN | NaN | NaN | NaN | 632.1553 | NaN | 21.33 | NaN | 26.2199
5949.1292 | 13.9596 | 13.6944 | 13.6294 | 14.0108 | 13.327 | 13.675 | 13.357 | 13.1726 | NaN | NaN | NaN | 13.5218 | 91.5484 | NaN | NaN | NaN | -1.5014 | NaN | NaN | NaN | NaN | 631.9547 | NaN | 21.8498 | NaN | 27.7417
5950.1292 | 13.8899 | 13.6973 | 13.6296 | 14.0158 | 13.2573 | 13.5912 | 13.3741 | 13.17 | NaN | NaN | NaN | 13.594 | 93.9536 | NaN | NaN | NaN | 27.8931 | NaN | NaN | NaN | NaN | 631.5561 | NaN | 20.6106 | NaN | 25.8824
5951.1292 | 13.9761 | 13.5751 | 13.6249 | 13.9481 | 13.3385 | 13.7031 | 13.3291 | 13.1722 | NaN | NaN | NaN | 13.5306 | 93.4877 | NaN | NaN | NaN | 6.7687 | NaN | NaN | NaN | NaN | 634.7784 | NaN | 24.6282 | NaN | 27.545
5952.1292 | 13.9358 | 13.5997 | 13.6252 | 13.9413 | 13.3815 | 13.6042 | 13.3511 | 13.1699 | NaN | NaN | NaN | 13.6549 | 92.1466 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 632.1362 | NaN | 26.0128 | NaN | 25.5646
5953.1292 | 13.9235 | 13.5755 | 13.6294 | 13.9585 | 13.3052 | 13.5988 | 13.3228 | 13.1771 | NaN | NaN | NaN | 13.6536 | 93.8253 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 628.2873 | NaN | 24.5461 | NaN | 28.1916
5954.1292 | 13.9487 | 13.5811 | 13.62 | 13.9232 | 13.4235 | 13.621 | 13.3344 | 13.1704 | NaN | NaN | NaN | 13.5061 | 95.5916 | NaN | NaN | NaN | -6.2602 | NaN | NaN | NaN | NaN | 627.6873 | NaN | 26.0537 | NaN | 27.1741
5955.1292 | 14.1198 | 13.6161 | 13.622 | 13.9222 | 13.3847 | 13.5915 | 13.3489 | 13.1793 | NaN | NaN | NaN | 13.5468 | 92.8232 | NaN | NaN | NaN | 21.5192 | NaN | NaN | NaN | NaN | 622.5112 | NaN | 25.6138 | NaN | 27.1689
5956.1292 | 13.8753 | 13.5661 | 13.6238 | 13.9137 | 13.2861 | 13.5983 | 13.3313 | 13.1754 | NaN | NaN | NaN | 13.4947 | 93.2558 | NaN | NaN | NaN | 52.6622 | NaN | NaN | NaN | NaN | 622.2891 | NaN | 22.1408 | NaN | 26.1948
5957.1292 | 13.877 | 13.5814 | 13.6286 | 13.9602 | 13.2045 | 13.6172 | 13.333 | 13.174 | NaN | NaN | NaN | 13.4923 | 92.6896 | NaN | NaN | NaN | -11.2881 | NaN | NaN | NaN | NaN | 626.75 | NaN | 25.9444 | NaN | 28.4206
5958.1292 | 13.8854 | 13.6165 | 13.6377 | 13.8608 | 13.2819 | 13.5936 | 13.3386 | 13.1678 | NaN | NaN | NaN | 13.516 | 93.9239 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 625.323 | NaN | 22.3555 | NaN | 27.659
5959.1292 | 13.9779 | 13.5879 | 13.6325 | 13.9521 | 13.3592 | 13.5896 | 13.3181 | 13.1743 | NaN | NaN | NaN | 13.5732 | 93.3353 | NaN | NaN | NaN | -3.6514 | NaN | NaN | NaN | NaN | 621.928 | NaN | 25.9346 | NaN | 27.5341
5960.1292 | 13.9193 | 13.6776 | 13.643 | 13.8859 | 13.3127 | 13.6125 | 13.3365 | 13.1681 | NaN | NaN | NaN | 13.5208 | 93.6726 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 627.7701 | NaN | 25.3174 | NaN | 27.857
5961.1292 | 13.9376 | 13.5893 | 13.6379 | 13.9366 | 13.3021 | 13.5905 | 13.3243 | 13.1678 | NaN | NaN | NaN | 13.5007 | 91.6946 | NaN | NaN | NaN | -5.5724 | NaN | NaN | NaN | NaN | 623.0913 | NaN | 26.3728 | NaN | 27.507
5962.1292 | 13.9426 | 13.6008 | 13.6437 | 13.9124 | 13.5099 | 13.6187 | 13.3186 | 13.1624 | NaN | NaN | NaN | 13.4984 | 92.2551 | NaN | NaN | NaN | 43.6424 | NaN | NaN | NaN | NaN | 622.4614 | NaN | 21.2656 | NaN | 28.4956
5963.1292 | 13.9537 | 13.6183 | 13.6574 | 13.9167 | 13.4442 | 13.6868 | 13.3373 | 13.1618 | NaN | NaN | NaN | 13.5116 | 92.529 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 622.6246 | NaN | 24.0188 | NaN | 27.4119
5964.1292 | 13.9275 | 13.6218 | 13.6476 | 13.9203 | 13.4981 | 13.6262 | 13.3368 | 13.1649 | NaN | NaN | NaN | 13.5417 | 95.0505 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 623.2394 | NaN | 24.5127 | NaN | 25.1932
5965.1292 | 13.9434 | 13.6733 | 13.6507 | 13.9281 | 13.296 | 13.6478 | 13.3661 | 13.161 | NaN | NaN | NaN | 13.5345 | 94.518 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 625.1964 | NaN | 23.129 | NaN | 26.1119
5966.1292 | 13.9403 | 13.709 | 13.6533 | 13.9861 | 13.2798 | 13.6662 | 13.3477 | 13.1586 | NaN | NaN | NaN | 13.5247 | 90.8743 | NaN | NaN | NaN | 41.6902 | NaN | NaN | NaN | NaN | 622.5679 | NaN | 25.9965 | NaN | 26.7686
5967.1292 | 13.9847 | 13.6333 | 13.6493 | 13.9163 | 13.3877 | 13.6259 | 13.3399 | 13.1637 | NaN | NaN | NaN | 13.5056 | 92.9068 | NaN | NaN | NaN | 2.2802 | NaN | NaN | NaN | NaN | 622.8418 | NaN | 27.0924 | NaN | 27.3829
5968.1292 | 13.9222 | 13.643 | 13.6533 | 13.9139 | 13.2605 | 13.6002 | 13.3427 | 13.1644 | NaN | NaN | NaN | 13.5061 | 93.776 | NaN | NaN | NaN | 12.9912 | NaN | NaN | NaN | NaN | 623.4256 | NaN | 23.0559 | NaN | 25.6748
5969.1292 | 13.9392 | 13.6074 | 13.6489 | 13.919 | 13.3458 | 13.8359 | 13.3359 | 13.1659 | NaN | NaN | NaN | 13.51 | 93.4305 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 623.2804 | NaN | 22.7765 | NaN | 26.2385
5970.1292 | 13.8834 | 13.6624 | 13.6455 | 13.916 | 13.4177 | 13.6503 | 13.358 | 13.1689 | NaN | NaN | NaN | 13.5383 | 93.5849 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 621.5965 | NaN | 24.504 | NaN | 26.7151
5971.1292 | 13.8884 | 13.6247 | 13.6553 | 13.872 | 13.361 | 13.6133 | 13.3411 | 13.1699 | NaN | NaN | NaN | 13.6292 | 92.708 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 625.0156 | NaN | 22.5659 | NaN | 28.4015
5972.1292 | 13.9034 | 13.6462 | 13.66 | 13.8877 | 13.3586 | 13.589 | 13.3287 | 13.1768 | NaN | NaN | NaN | 13.5517 | 96.7579 | NaN | NaN | NaN | -16.3761 | NaN | NaN | NaN | NaN | 621.8414 | NaN | 24.2648 | NaN | 29.0484
5973.1292 | 13.8904 | 13.6755 | 13.657 | 13.878 | 13.2108 | 13.7071 | 13.3552 | 13.1752 | NaN | NaN | NaN | 13.5055 | 93.7519 | NaN | NaN | NaN | -19.187 | NaN | NaN | NaN | NaN | 620.6453 | NaN | 24.8344 | NaN | 27.5739
5974.1292 | 13.8939 | 13.7454 | 13.6613 | 13.9154 | 13.2611 | 13.595 | 13.3686 | 13.1737 | NaN | NaN | NaN | 13.521 | 92.0275 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 622.6602 | NaN | 24.7129 | NaN | 26.6052
5975.1292 | 13.8739 | 13.6386 | 13.6641 | 13.9128 | 13.2988 | 13.725 | 13.3624 | 13.1792 | NaN | NaN | NaN | 13.5305 | 92.938 | NaN | NaN | NaN | -13.5381 | NaN | NaN | NaN | NaN | 623.1288 | NaN | 25.3043 | NaN | 26.5802
5976.1292 | 13.8789 | 13.8257 | 13.6634 | 13.8994 | 13.2761 | 13.6296 | 13.3791 | 13.1819 | NaN | NaN | NaN | 13.5181 | 93.2533 | NaN | NaN | NaN | 1.148 | NaN | NaN | NaN | NaN | 623.6799 | NaN | 26.8376 | NaN | 27.6639
5977.1292 | 13.8599 | 13.6512 | 13.6575 | 13.8999 | 13.4152 | 13.6029 | 13.3572 | 13.1785 | NaN | NaN | NaN | 13.5522 | 95.5143 | NaN | NaN | NaN | -10.9344 | NaN | NaN | NaN | NaN | 622.4272 | NaN | 24.079 | NaN | 26.9505
5978.1292 | 14.2204 | 13.6246 | 13.6623 | 13.9412 | 13.3175 | 13.6669 | 13.3475 | 13.1748 | NaN | NaN | NaN | 13.4984 | 93.385 | NaN | NaN | NaN | 42.5466 | NaN | NaN | NaN | NaN | 623.6028 | NaN | 23.4655 | NaN | 27.014
5979.1292 | 13.9185 | 13.6601 | 13.6737 | 13.9116 | 13.3723 | 13.726 | 13.3617 | 13.1738 | NaN | NaN | NaN | 13.6092 | 92.4612 | NaN | NaN | NaN | 4.9023 | NaN | NaN | NaN | NaN | 621.6704 | NaN | 26.6581 | NaN | 28.5716
5980.1292 | 13.9245 | 13.6856 | 13.663 | 13.9943 | 13.3928 | 13.6716 | 13.3529 | 13.1786 | NaN | NaN | NaN | 13.5148 | 92.1955 | NaN | NaN | NaN | 2.8076 | NaN | NaN | NaN | NaN | 620.5271 | NaN | 23.6499 | NaN | 26.9922
5981.1292 | 13.9551 | 13.9338 | 13.6664 | 14.0442 | 13.308 | 13.6416 | 13.4545 | 13.1679 | NaN | NaN | NaN | 13.4977 | 92.5612 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 620.9049 | NaN | 24.2247 | NaN | 26.9454
5982.1292 | 13.8731 | 13.6194 | 13.6717 | 13.9086 | 13.3362 | 13.6333 | 13.3659 | 13.1796 | NaN | NaN | NaN | 13.5266 | 92.4968 | NaN | NaN | NaN | 24.5698 | NaN | NaN | NaN | NaN | 621.2633 | NaN | 23.955 | NaN | 28.134
5983.1292 | 13.8887 | 13.6636 | 13.6684 | 13.9359 | 13.2766 | 13.6525 | 13.3722 | 13.1807 | NaN | NaN | NaN | 13.5339 | 91.4483 | NaN | NaN | NaN | 1.0642 | NaN | NaN | NaN | NaN | 620.78 | NaN | 24.674 | NaN | 27.2204
5984.1292 | 13.9012 | 13.6215 | 13.669 | 13.9398 | 13.3662 | 13.6073 | 13.3522 | 13.1829 | NaN | NaN | NaN | 13.5142 | 93.1448 | NaN | NaN | NaN | -13.5969 | NaN | NaN | NaN | NaN | 620.8228 | NaN | 27.9807 | NaN | 28.5371
5985.1292 | 13.9235 | 13.5883 | 13.6706 | 13.9664 | 13.3255 | 13.6604 | 13.35 | 13.1859 | NaN | NaN | NaN | 13.5155 | 94.4277 | NaN | NaN | NaN | 25.0497 | NaN | NaN | NaN | NaN | 622.163 | NaN | 22.9514 | NaN | 27.0695
5986.1292 | 13.9098 | 13.7491 | 13.6704 | 13.8981 | 13.4031 | 13.6402 | 13.3854 | 13.186 | NaN | NaN | NaN | 13.5478 | 92.583 | NaN | NaN | NaN | -3.5039 | NaN | NaN | NaN | NaN | 622.8811 | NaN | 23.8487 | NaN | 25.8539
5987.1292 | 13.9232 | 13.5949 | 13.6726 | 13.9263 | 13.344 | 13.6109 | 13.3492 | 13.1856 | NaN | NaN | NaN | 13.5125 | 92.6134 | NaN | NaN | NaN | 17.6671 | NaN | NaN | NaN | NaN | 623.395 | NaN | 24.3846 | NaN | 27.2184
5988.1448 | 13.8973 | 13.6229 | 13.6792 | 13.8921 | 13.3599 | 13.7045 | 13.3734 | 13.1967 | NaN | NaN | NaN | 13.5332 | 92.1727 | NaN | NaN | NaN | 56.2609 | NaN | NaN | NaN | NaN | 621.9838 | NaN | 22.9242 | NaN | 27.8852
5989.1292 | 13.8892 | 13.6103 | 13.674 | 13.9112 | 13.3136 | 13.6404 | 13.3613 | 13.1948 | NaN | NaN | NaN | 13.5733 | 92.282 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 621.9874 | NaN | 24.3883 | NaN | 28.4586
5990.1292 | 14.0381 | 13.7122 | 13.6734 | 13.9289 | 13.3228 | 13.6708 | 13.3909 | 13.1933 | NaN | NaN | NaN | 13.5553 | 94.829 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 621.9952 | NaN | 25.3312 | NaN | 26.9377
5991.1292 | 13.925 | 13.5946 | 13.6723 | 13.8688 | 13.3917 | 13.6607 | 13.3541 | 13.1936 | NaN | NaN | NaN | 13.5196 | 95.1311 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 622.8031 | NaN | 25.0509 | NaN | 27.3119
5992.1292 | 13.9208 | 13.7064 | 13.665 | 13.9584 | 13.3796 | 13.6491 | 13.373 | 13.1949 | NaN | NaN | NaN | 13.5409 | 94.3175 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 623.7272 | NaN | 26.3989 | NaN | 27.3803
5993.1292 | 13.9052 | 13.6322 | 13.6753 | 13.8649 | 13.4154 | 13.6055 | 13.3614 | 13.1959 | NaN | NaN | NaN | 13.5572 | 91.5658 | NaN | NaN | NaN | 43.5025 | NaN | NaN | NaN | NaN | 622.0938 | NaN | 23.0728 | NaN | 25.0313
5994.1292 | 13.888 | 13.62 | 13.6758 | 13.9095 | 13.4078 | 13.6382 | 13.3643 | 13.1934 | NaN | NaN | NaN | 13.5408 | 94.0388 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 620.3144 | NaN | 24.7451 | NaN | 26.7989
5995.1292 | 13.9097 | 13.673 | 13.6763 | 13.9381 | 13.3222 | 13.6072 | 13.3765 | 13.2022 | NaN | NaN | NaN | 13.5904 | 92.3085 | NaN | NaN | NaN | 24.2223 | NaN | NaN | NaN | NaN | 618.5067 | NaN | 25.3067 | NaN | 28.3461
5996.1292 | 13.9118 | 13.6721 | 13.6783 | 13.9082 | 13.4299 | 13.6255 | 13.3792 | 13.2078 | NaN | NaN | NaN | 13.5672 | 93.9026 | NaN | NaN | NaN | -9.4388 | NaN | NaN | NaN | NaN | 621.4436 | NaN | 25.9387 | NaN | 27.0996
5997.1292 | 13.9158 | 13.7219 | 13.6714 | 13.8905 | 13.2226 | 13.6364 | 13.394 | 13.2123 | NaN | NaN | NaN | 13.5161 | 93.2903 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 621.0879 | NaN | 21.701 | NaN | 27.4939
5998.1292 | 13.9074 | 13.6312 | 13.6711 | 13.9138 | 13.3418 | 13.6313 | 13.3682 | 13.2077 | NaN | NaN | NaN | 13.5787 | 95.225 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 617.9632 | NaN | 23.0187 | NaN | 25.8463
5999.1292 | 13.8863 | 13.6538 | 13.6751 | 13.8756 | 13.2513 | 13.6463 | 13.3769 | 13.2059 | NaN | NaN | NaN | 13.5398 | 91.7439 | NaN | NaN | NaN | -6.6019 | NaN | NaN | NaN | NaN | 618.6224 | NaN | 25.6274 | NaN | 27.412
6000.1292 | 13.9448 | 13.6832 | 13.6758 | 13.8883 | 13.3635 | 13.6034 | 13.3975 | 13.21 | NaN | NaN | NaN | 13.5415 | 93.7856 | NaN | NaN | NaN | 24.1461 | NaN | NaN | NaN | NaN | 619.9563 | NaN | 20.8532 | NaN | 25.3914
6001.1292 | 13.9465 | 13.6928 | 13.684 | 13.8628 | 13.3636 | 13.614 | 13.3754 | 13.2125 | NaN | NaN | NaN | 13.575 | 85.531 | NaN | NaN | NaN | 12.0662 | NaN | NaN | NaN | NaN | 617.4621 | NaN | 23.9448 | NaN | 28.9883
6002.1292 | 13.9276 | 13.6534 | 13.6875 | 13.9533 | 13.2888 | 13.7484 | 13.3703 | 13.2174 | NaN | NaN | NaN | 13.5327 | 92.0038 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 614.0287 | NaN | 25.3768 | NaN | 27.5706
6003.1292 | 13.9396 | 13.7259 | 13.6802 | 13.9055 | 13.364 | 13.7075 | 13.3964 | 13.208 | NaN | NaN | NaN | 13.527 | 93.5135 | NaN | NaN | NaN | 39.156 | NaN | NaN | NaN | NaN | 613.0476 | NaN | 21.9711 | NaN | 26.0852
6004.1292 | 13.8877 | 13.6185 | 13.6844 | 13.9101 | 13.4152 | 13.6019 | 13.3667 | 13.2109 | NaN | NaN | NaN | 13.5622 | 93.9625 | NaN | NaN | NaN | 22.1368 | NaN | NaN | NaN | NaN | 611.7389 | NaN | 25.3385 | NaN | 28.2118
6005.1292 | 13.9042 | 13.6338 | 13.6789 | 13.8608 | 13.3505 | 13.7197 | 13.3633 | 13.2128 | NaN | NaN | NaN | 13.5605 | 93.0383 | NaN | NaN | NaN | 40.9644 | NaN | NaN | NaN | NaN | 612.8934 | NaN | 24.5411 | NaN | 26.9375
6006.1292 | 13.9458 | 13.6478 | 13.6864 | 13.885 | 13.3717 | 13.6426 | 13.3871 | 13.2116 | NaN | NaN | NaN | 13.5862 | 92.312 | NaN | NaN | NaN | 47.7496 | NaN | NaN | NaN | NaN | 613.2651 | NaN | 29.0202 | NaN | 25.63
6007.1292 | 13.9453 | 13.6452 | 13.684 | 13.9189 | 13.3273 | 13.6698 | 13.3897 | 13.2178 | NaN | NaN | NaN | 13.5617 | 93.942 | NaN | NaN | NaN | 4.6036 | NaN | NaN | NaN | NaN | 614.2241 | NaN | 23.0999 | NaN | 27.8657
6008.1292 | 14.0138 | 13.6361 | 13.6881 | 13.8907 | 13.2677 | 13.6626 | 13.3706 | 13.2173 | NaN | NaN | NaN | 13.5337 | 91.208 | NaN | NaN | NaN | 26.1487 | NaN | NaN | NaN | NaN | 614.9598 | NaN | 24.6431 | NaN | 26.4832
6009.1292 | 14.0202 | 13.6597 | 13.6862 | 13.9551 | 13.4914 | 13.6751 | 13.3609 | 13.2192 | NaN | NaN | NaN | 13.5173 | 91.1195 | NaN | NaN | NaN | 10.5509 | NaN | NaN | NaN | NaN | 612.5587 | NaN | 24.2796 | NaN | 27.1731
6010.1292 | 13.9246 | 13.7421 | 13.6902 | 13.8783 | 13.3981 | 13.6531 | 13.3749 | 13.2175 | NaN | NaN | NaN | 13.5535 | 95.8828 | NaN | NaN | NaN | -17.7066 | NaN | NaN | NaN | NaN | 612.5022 | NaN | 22.5019 | NaN | 25.945
6011.1292 | 13.9138 | 13.6701 | 13.6899 | 13.8789 | 13.3413 | 13.6387 | 13.3731 | 13.2188 | NaN | NaN | NaN | 13.5391 | 92.369 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 613.6086 | NaN | 23.6842 | NaN | 26.7409
6012.1292 | 13.9151 | 13.6743 | 13.6989 | 13.9354 | 13.2542 | 13.7023 | 13.3845 | 13.2152 | NaN | NaN | NaN | 13.6397 | 95.4415 | NaN | NaN | NaN | -10.6523 | NaN | NaN | NaN | NaN | 610.6933 | NaN | 23.4105 | NaN | 26.0784
6013.1292 | 13.9094 | 13.6335 | 13.6898 | 13.8708 | 13.3951 | 13.7178 | 13.3662 | 13.2219 | NaN | NaN | NaN | 13.556 | 93.4225 | NaN | NaN | NaN | 27.3939 | NaN | NaN | NaN | NaN | 610.0726 | NaN | 25.7374 | NaN | 25.3812
6014.1292 | 13.9382 | 13.6583 | 13.6919 | 13.8934 | 13.3974 | 13.6143 | 13.3721 | 13.2156 | NaN | NaN | NaN | 13.5335 | 93.3297 | NaN | NaN | NaN | 28.5973 | NaN | NaN | NaN | NaN | 612.637 | NaN | 23.2826 | NaN | 26.799
6015.1292 | 13.9407 | 13.6619 | 13.6863 | 13.9127 | 13.2883 | 13.8459 | 13.3803 | 13.2195 | NaN | NaN | NaN | 13.5312 | 93.2282 | NaN | NaN | NaN | 11.1261 | NaN | NaN | NaN | NaN | 613.3824 | NaN | 24.6976 | NaN | 27.5315
6016.1292 | 13.9248 | 13.6174 | 13.6816 | 13.8818 | 13.3053 | 13.6681 | 13.3505 | 13.2217 | NaN | NaN | NaN | 13.6255 | 92.491 | NaN | NaN | NaN | -13.4146 | NaN | NaN | NaN | NaN | 613.872 | NaN | 22.1978 | NaN | 27.0184
6017.1292 | 13.9359 | 13.7499 | 13.6796 | 13.9383 | 13.3198 | 13.6346 | 13.3803 | 13.2174 | NaN | NaN | NaN | 13.5486 | 89.7646 | NaN | NaN | NaN | -12.8724 | NaN | NaN | NaN | NaN | 609.3719 | NaN | 24.1754 | NaN | 26.8712
6018.1292 | 13.9167 | 13.6344 | 13.6843 | 13.9024 | 13.3743 | 13.6436 | 13.3609 | 13.223 | NaN | NaN | NaN | 13.5137 | 89.8995 | NaN | NaN | NaN | 2.5602 | NaN | NaN | NaN | NaN | 610.7694 | NaN | 24.3101 | NaN | 28.4535
6019.1292 | 13.9334 | 13.6144 | 13.6735 | 13.9053 | 13.3524 | 13.7399 | 13.3496 | 13.2247 | NaN | NaN | NaN | 13.5638 | 94.0334 | NaN | NaN | NaN | -18.111 | NaN | NaN | NaN | NaN | 611.1684 | NaN | 20.9408 | NaN | 26.7454
6020.1292 | 13.937 | 13.622 | 13.6721 | 13.9319 | 13.3514 | 13.6438 | 13.3518 | 13.2244 | NaN | NaN | NaN | 13.5352 | 90.8628 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 607.0205 | NaN | 23.4877 | NaN | 27.9092
6021.1292 | 13.9354 | 13.6326 | 13.6834 | 13.8908 | 13.4297 | 13.6844 | 13.358 | 13.2228 | NaN | NaN | NaN | 13.5245 | 93.1813 | NaN | NaN | NaN | 15.7613 | NaN | NaN | NaN | NaN | 611.223 | NaN | 23.1513 | NaN | 27.0228
6022.1292 | 13.9402 | 13.624 | 13.6841 | 13.851 | 13.3734 | 13.6396 | 13.3552 | 13.2238 | NaN | NaN | NaN | 13.6554 | 94.1661 | NaN | NaN | NaN | 15.9721 | NaN | NaN | NaN | NaN | 611.8672 | NaN | 26.8437 | NaN | 27.1525
6023.1292 | 13.9429 | 13.6417 | 13.6792 | 13.909 | 13.3344 | 13.6497 | 13.365 | 13.2227 | NaN | NaN | NaN | 13.609 | 93.4318 | NaN | NaN | NaN | -7.043 | NaN | NaN | NaN | NaN | 607.5954 | NaN | 23.4328 | NaN | 25.3975
6024.1292 | 13.9337 | 13.6535 | 13.6769 | 13.9026 | 13.4208 | 13.6522 | 13.3747 | 13.2199 | NaN | NaN | NaN | 13.555 | 97.0442 | NaN | NaN | NaN | -11.0208 | NaN | NaN | NaN | NaN | 605.9674 | NaN | 25.0545 | NaN | 26.8377
6025.1292 | 13.9398 | 13.6508 | 13.6735 | 13.8754 | 13.3363 | 13.717 | 13.3732 | 13.2225 | NaN | NaN | NaN | 13.6138 | 94.2295 | NaN | NaN | NaN | -13.0879 | NaN | NaN | NaN | NaN | 606.4777 | NaN | 25.242 | NaN | 27.0453
6026.1292 | 13.9684 | 13.6317 | 13.6684 | 13.9233 | 13.3468 | 13.6418 | 13.3567 | 13.2193 | NaN | NaN | NaN | 13.6486 | 91.8923 | NaN | NaN | NaN | -13.3667 | NaN | NaN | NaN | NaN | 607.0555 | NaN | 23.2231 | NaN | 26.6293
6027.1292 | 13.9225 | 13.752 | 13.6674 | 13.8548 | 13.3109 | 13.6437 | 13.38 | 13.2181 | NaN | NaN | NaN | 13.6645 | 93.2089 | NaN | NaN | NaN | 24.7739 | NaN | NaN | NaN | NaN | 608.168 | NaN | 25.1382 | NaN | 24.2319
6028.1292 | 13.9369 | 13.6408 | 13.6642 | 13.9895 | 13.3217 | 13.6883 | 13.3589 | 13.2151 | NaN | NaN | NaN | 13.5556 | 91.8592 | NaN | NaN | NaN | 1.0059 | NaN | NaN | NaN | NaN | 605.2996 | NaN | 22.4644 | NaN | 25.1874
6029.1292 | 13.9603 | 13.7635 | 13.6611 | 13.9207 | 13.4052 | 13.6786 | 13.3853 | 13.2125 | NaN | NaN | NaN | 13.5876 | 92.7503 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 609.5242 | NaN | 24.8262 | NaN | 26.1094
6030.1292 | 13.9251 | 13.7116 | 13.6676 | 13.9005 | 13.3664 | 13.76 | 13.3933 | 13.2147 | NaN | NaN | NaN | 13.5371 | 92.3079 | NaN | NaN | NaN | -3.1391 | NaN | NaN | NaN | NaN | 604.7067 | NaN | 23.8487 | NaN | 26.3976
6031.1292 | 13.941 | 13.6599 | 13.663 | 13.8473 | 13.406 | 13.6395 | 13.3689 | 13.2056 | NaN | NaN | NaN | 13.5771 | 92.1659 | NaN | NaN | NaN | 12.6208 | NaN | NaN | NaN | NaN | 602.99 | NaN | 23.0299 | NaN | 26.1418
6032.1292 | 13.9182 | 13.6235 | 13.6597 | 13.8774 | 13.3738 | 13.6362 | 13.3718 | 13.203 | NaN | NaN | NaN | 13.5254 | 95.6089 | NaN | NaN | NaN | -18.1447 | NaN | NaN | NaN | NaN | 599.7266 | NaN | 22.5318 | NaN | 27.8523
6033.1292 | 13.9136 | 13.6413 | 13.6728 | 13.8788 | 13.3974 | 13.6376 | 13.3527 | 13.2094 | NaN | NaN | NaN | 13.534 | 92.5281 | NaN | NaN | NaN | 18.2601 | NaN | NaN | NaN | NaN | 602.0546 | NaN | 23.8755 | NaN | 27.4086
6034.1292 | 13.9429 | 13.6541 | 13.6713 | 13.8573 | 13.509 | 13.6366 | 13.3534 | 13.2067 | NaN | NaN | NaN | 13.5964 | 93.5161 | NaN | NaN | NaN | -12.6587 | NaN | NaN | NaN | NaN | 604.4468 | NaN | 24.9836 | NaN | 27.0354
6035.1292 | 13.9429 | 13.6356 | 13.6799 | 13.8876 | 13.3437 | 13.7122 | 13.3575 | 13.2144 | NaN | NaN | NaN | 13.6122 | 95.6257 | NaN | NaN | NaN | -6.1837 | NaN | NaN | NaN | NaN | 603.9333 | NaN | 23.6926 | NaN | 26.6655
6036.1292 | 13.9708 | 13.6506 | 13.6804 | 13.919 | 13.4646 | 13.7418 | 13.3586 | 13.2108 | NaN | NaN | NaN | 13.5559 | 96.1773 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 604.2237 | NaN | 23.7439 | NaN | 26.2944
6037.1292 | 13.9623 | 13.6385 | 13.6776 | 13.9091 | 13.3185 | 13.7283 | 13.3552 | 13.209 | NaN | NaN | NaN | 13.5507 | 102.7266 | NaN | NaN | NaN | -17.6008 | NaN | NaN | NaN | NaN | 603.0251 | NaN | 24.0725 | NaN | 26.9539
6038.1292 | 13.9191 | 13.6637 | 13.6823 | 13.8718 | 13.4201 | 13.6731 | 13.3746 | 13.2163 | NaN | NaN | NaN | 13.6257 | 92.439 | NaN | NaN | NaN | -13.4006 | NaN | NaN | NaN | NaN | 606.4934 | NaN | 24.1043 | NaN | 25.9414
6039.1292 | 13.93 | 13.743 | 13.6823 | 13.8644 | 13.3852 | 13.7318 | 13.3768 | 13.2186 | NaN | NaN | NaN | 13.543 | 90.3337 | NaN | NaN | NaN | 11.1933 | NaN | NaN | NaN | NaN | 605.2989 | NaN | 23.265 | NaN | 27.7436
6040.1292 | 13.9435 | 13.6586 | 13.6824 | 13.953 | 13.3601 | 13.6689 | 13.3719 | 13.2112 | NaN | NaN | NaN | 13.5663 | 92.1879 | NaN | NaN | NaN | 56.1625 | NaN | NaN | NaN | NaN | 603.2681 | NaN | 22.7016 | NaN | 25.5292
6041.1292 | 13.9211 | 13.7389 | 13.6822 | 13.9175 | 13.3866 | 13.6773 | 13.401 | 13.2138 | NaN | NaN | NaN | 13.5355 | 92.239 | NaN | NaN | NaN | 24.0512 | NaN | NaN | NaN | NaN | 599.3797 | NaN | 24.334 | NaN | 24.5143
6042.1292 | 13.9478 | 13.6566 | 13.6777 | 13.9065 | 13.3574 | 13.7281 | 13.3836 | 13.2133 | NaN | NaN | NaN | 13.5431 | 93.1831 | NaN | NaN | NaN | 19.0095 | NaN | NaN | NaN | NaN | 601.1198 | NaN | 26.6104 | NaN | 25.8358
6043.1292 | 14.1462 | 13.6458 | 13.6723 | 13.884 | 13.3935 | 13.6798 | 13.3617 | 13.2115 | NaN | NaN | NaN | 13.5341 | 91.5374 | NaN | NaN | NaN | 60.4292 | NaN | NaN | NaN | NaN | 600.3365 | NaN | 23.3805 | NaN | 28.1073
6044.1292 | 13.9605 | 13.6925 | 13.6708 | 13.893 | 13.3852 | 13.7315 | 13.3924 | 13.2105 | NaN | NaN | NaN | 13.5618 | 91.7718 | NaN | NaN | NaN | 12.2275 | NaN | NaN | NaN | NaN | 602.9854 | NaN | 23.1228 | NaN | 26.9521
6045.1292 | 14.3129 | 13.647 | 13.6656 | 13.8821 | 13.4246 | 13.6917 | 13.3686 | 13.2151 | NaN | NaN | NaN | 13.6174 | 94.513 | NaN | NaN | NaN | 40.0834 | NaN | NaN | NaN | NaN | 600.6889 | NaN | 22.9036 | NaN | 25.0561
6046.1292 | 14.1133 | 13.6669 | 13.6731 | 13.902 | 13.2515 | 13.6787 | 13.3757 | 13.219 | NaN | NaN | NaN | 13.5264 | 92.6108 | NaN | NaN | NaN | -12.7254 | NaN | NaN | NaN | NaN | 598.6922 | NaN | 25.3877 | NaN | 27.7334
6047.1292 | 13.9221 | 13.6832 | 13.6737 | 14.0627 | 13.3716 | 13.6647 | 13.3782 | 13.2191 | NaN | NaN | NaN | 13.6193 | 92.5126 | NaN | NaN | NaN | 10.0877 | NaN | NaN | NaN | NaN | 601.4232 | NaN | 23.2035 | NaN | 27.3724
6048.1292 | 13.9645 | 13.6951 | 13.6739 | 13.9225 | 13.3656 | 13.6609 | 13.3767 | 13.2131 | NaN | NaN | NaN | 13.5298 | 93.7865 | NaN | NaN | NaN | -4.2215 | NaN | NaN | NaN | NaN | 602.674 | NaN | 22.3166 | NaN | 26.6029
6049.1292 | 13.9146 | 13.6604 | 13.6745 | 13.8848 | 13.4289 | 13.6693 | 13.3783 | 13.2159 | NaN | NaN | NaN | 13.5369 | 91.5333 | NaN | NaN | NaN | 8.7179 | NaN | NaN | NaN | NaN | 603.3091 | NaN | 22.9345 | NaN | 25.4715
6050.1292 | 13.935 | 13.6644 | 13.6801 | 13.8871 | 13.3013 | 13.7084 | 13.3691 | 13.2172 | NaN | NaN | NaN | 13.5504 | 92.1645 | NaN | NaN | NaN | 10.2837 | NaN | NaN | NaN | NaN | 598.2394 | NaN | 23.6453 | NaN | 28.3197
6051.1292 | 13.9243 | 13.7206 | 13.6813 | 13.9083 | 13.4491 | 13.7158 | 13.3839 | 13.2172 | NaN | NaN | NaN | 13.5928 | 93.485 | NaN | NaN | NaN | 38.3132 | NaN | NaN | NaN | NaN | 600.7964 | NaN | 24.8733 | NaN | 25.9544
6052.1292 | 13.9636 | 13.6386 | 13.6796 | 13.8801 | 13.4381 | 13.6552 | 13.3832 | 13.2217 | NaN | NaN | NaN | 13.5785 | 97.9661 | NaN | NaN | NaN | -16.9233 | NaN | NaN | NaN | NaN | 597.9322 | NaN | 22.4836 | NaN | 26.4567
6053.1292 | 13.9358 | 13.6599 | 13.6747 | 13.9279 | 13.4418 | 13.665 | 13.3737 | 13.2239 | NaN | NaN | NaN | 13.56 | 93.1745 | NaN | NaN | NaN | 41.1462 | NaN | NaN | NaN | NaN | 598.1464 | NaN | 23.7908 | NaN | 27.1969
6054.1292 | 13.9238 | 13.7161 | 13.677 | 13.9559 | 13.4145 | 13.7184 | 13.392 | 13.2212 | NaN | NaN | NaN | 13.5783 | 94.5307 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 596.3542 | NaN | 22.4692 | NaN | 25.1432
6055.1292 | 13.986 | 13.6595 | 13.6746 | 13.9251 | 13.4374 | 13.7424 | 13.3783 | 13.2226 | NaN | NaN | NaN | 13.6562 | 92.9226 | NaN | NaN | NaN | -9.5077 | NaN | NaN | NaN | NaN | 597.0686 | NaN | 23.8524 | NaN | 24.8951
6056.1292 | 13.9369 | 13.6813 | 13.6715 | 13.897 | 13.3282 | 13.6449 | 13.3867 | 13.2239 | NaN | NaN | NaN | 13.5625 | 96.2434 | NaN | NaN | NaN | 22.6344 | NaN | NaN | NaN | NaN | 594.4678 | NaN | 21.8317 | NaN | 26.2276
6057.1292 | 13.9969 | 13.6371 | 13.6684 | 13.9456 | 13.3052 | 13.6678 | 13.3693 | 13.2248 | NaN | NaN | NaN | 13.5176 | 93.0508 | NaN | NaN | NaN | 10.0124 | NaN | NaN | NaN | NaN | 588.7673 | NaN | 24.2655 | NaN | 25.4874
6058.1448 | 13.9338 | 13.6369 | 13.6584 | 14.1532 | 13.2993 | 13.6816 | 13.3893 | 13.2259 | NaN | NaN | NaN | 13.6094 | 93.3035 | NaN | NaN | NaN | 9.3449 | NaN | NaN | NaN | NaN | 584.7848 | NaN | 23.1303 | NaN | 26.417
6059.1292 | 13.9417 | 13.6219 | 13.6637 | 13.9333 | 13.4281 | 13.6499 | 13.371 | 13.2291 | NaN | NaN | NaN | 13.6216 | 95.4453 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 571.5148 | NaN | 22.8383 | NaN | 27.6882
6060.1448 | 13.9493 | 13.6546 | 13.6661 | 13.9156 | 13.3788 | 13.6459 | 13.4013 | 13.2293 | NaN | NaN | NaN | 13.5396 | 93.0083 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 560.0968 | NaN | 23.1143 | NaN | 26.1597
6061.1292 | 13.9805 | 13.6333 | 13.67 | 13.8729 | 13.4338 | 13.6544 | 13.385 | 13.2331 | NaN | NaN | NaN | 13.5744 | 100.8315 | NaN | NaN | NaN | -18.4717 | NaN | NaN | NaN | NaN | 559.7538 | NaN | 23.2087 | NaN | 27.8554
6062.1292 | 13.9594 | 13.7032 | 13.6694 | 13.9393 | 13.38 | 13.6764 | 13.4109 | 13.2332 | NaN | NaN | NaN | 13.595 | 91.5912 | NaN | NaN | NaN | 41.8655 | NaN | NaN | NaN | NaN | 559.5579 | NaN | 22.3913 | NaN | 27.2871
6063.1292 | 13.9754 | 13.6189 | 13.6723 | 13.9357 | 13.4117 | 13.6443 | 13.3963 | 13.2375 | NaN | NaN | NaN | 13.5585 | 92.3507 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 566.1173 | NaN | 23.266 | NaN | 27.2358
6064.1448 | 13.9298 | 13.6313 | 13.674 | 13.9336 | 13.3497 | 13.6517 | 13.3861 | 13.2361 | NaN | NaN | NaN | 13.5724 | 92.987 | NaN | NaN | NaN | 48.4672 | NaN | NaN | NaN | NaN | 583.9068 | NaN | 25.2978 | NaN | 27.8977
6065.1292 | 13.9403 | 13.6267 | 13.6837 | 13.9521 | 13.2819 | 13.717 | 13.3911 | 13.2332 | NaN | NaN | NaN | 13.5811 | 92.7025 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 591.9659 | NaN | 22.8651 | NaN | 25.0648
6066.1292 | 13.9585 | 13.6287 | 13.6745 | 13.8883 | 13.3526 | 13.677 | 13.3923 | 13.2364 | NaN | NaN | NaN | 13.5562 | 90.0933 | NaN | NaN | NaN | 18.9843 | NaN | NaN | NaN | NaN | 593.2534 | NaN | 23.8625 | NaN | 26.8869
6067.1292 | 13.9171 | 13.7482 | 13.686 | 13.871 | 13.3319 | 13.7155 | 13.4179 | 13.2391 | NaN | NaN | NaN | 13.6087 | 91.0789 | NaN | NaN | NaN | 5.4745 | NaN | NaN | NaN | NaN | 592.0259 | NaN | 23.4484 | NaN | 26.5821
6068.1292 | 14.0113 | 13.6651 | 13.6773 | 13.8956 | 13.3716 | 13.6891 | 13.4113 | 13.2363 | NaN | NaN | NaN | 13.5957 | 92.3504 | NaN | NaN | NaN | 29.8604 | NaN | NaN | NaN | NaN | 593.8795 | NaN | 24.2133 | NaN | 27.4413
6069.1292 | 13.926 | 13.7426 | 13.6682 | 13.9254 | 13.3299 | 13.7325 | 13.4242 | 13.2396 | NaN | NaN | NaN | 13.5528 | 91.6676 | NaN | NaN | NaN | 16.5454 | NaN | NaN | NaN | NaN | 595.3672 | NaN | 22.5964 | NaN | 27.0531
6070.1292 | 13.9692 | 13.7195 | 13.6704 | 14.0094 | 13.491 | 13.6827 | 13.4236 | 13.2349 | NaN | NaN | NaN | 13.5528 | 94.3627 | NaN | NaN | NaN | 18.4128 | NaN | NaN | NaN | NaN | 594.1939 | NaN | 25.0614 | NaN | 26.7608
6071.1292 | 14.0031 | 13.6981 | 13.6681 | 13.9101 | 13.3541 | 13.6713 | 13.3957 | 13.2429 | NaN | NaN | NaN | 13.5436 | 93.2278 | NaN | NaN | NaN | 20.1257 | NaN | NaN | NaN | NaN | 591.9539 | NaN | 22.7142 | NaN | 26.9655
6072.1292 | 14.007 | 13.6402 | 13.6636 | 13.9309 | 13.3384 | 13.6633 | 13.3858 | 13.2382 | NaN | NaN | NaN | 13.5308 | 91.7782 | NaN | NaN | NaN | -3.8803 | NaN | NaN | NaN | NaN | 591.9273 | NaN | 23.1552 | NaN | 25.94
6073.1292 | 14.025 | 13.6704 | 13.67 | 13.8702 | 13.3801 | 13.6773 | 13.3876 | 13.229 | NaN | NaN | NaN | 13.6506 | 94.7277 | NaN | NaN | NaN | -12.1306 | NaN | NaN | NaN | NaN | 594.3859 | NaN | 22.5429 | NaN | 24.0865
6074.1292 | 13.9692 | 13.714 | 13.665 | 13.8717 | 13.3801 | 13.755 | 13.3864 | 13.2342 | NaN | NaN | NaN | 13.5629 | 94.0703 | NaN | NaN | NaN | 28.9028 | NaN | NaN | NaN | NaN | 592.0971 | NaN | 20.7884 | NaN | 27.1034
6075.1292 | 13.9633 | 13.6394 | 13.6688 | 13.8602 | 13.3755 | 13.7626 | 13.3986 | 13.228 | NaN | NaN | NaN | 13.5803 | 92.5063 | NaN | NaN | NaN | 23.1775 | NaN | NaN | NaN | NaN | 591.3459 | NaN | 24.1125 | NaN | 26.4172
6076.1292 | 13.9572 | 13.6896 | 13.6751 | 13.9147 | 13.1924 | 13.6857 | 13.3994 | 13.2358 | NaN | NaN | NaN | 13.6603 | 92.3856 | NaN | NaN | NaN | 29.2662 | NaN | NaN | NaN | NaN | 589.266 | NaN | 23.2177 | NaN | 27.2824
6077.1292 | 14.0184 | 13.65 | 13.6734 | 13.9334 | 13.3248 | 13.7305 | 13.3955 | 13.2259 | NaN | NaN | NaN | 13.5233 | 93.7101 | NaN | NaN | NaN | 21.7643 | NaN | NaN | NaN | NaN | 591.3868 | NaN | 23.5541 | NaN | 28.0137
6078.1448 | 14.0758 | 13.6893 | 13.6712 | 13.9318 | 13.4054 | 13.6771 | 13.3964 | 13.2276 | NaN | NaN | NaN | 13.535 | 91.7303 | NaN | NaN | NaN | -7.3145 | NaN | NaN | NaN | NaN | 586.9454 | NaN | 23.7235 | NaN | 27.4921
6079.1292 | 13.9969 | 13.7197 | 13.6771 | 13.9138 | 13.2982 | 13.7435 | 13.4271 | 13.2275 | NaN | NaN | NaN | 13.5245 | 92.7647 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 590.038 | NaN | 24.848 | NaN | 27.1038
6080.1292 | 13.9355 | 13.6958 | 13.6713 | 13.8551 | 13.3074 | 13.721 | 13.4053 | 13.225 | NaN | NaN | NaN | 13.5618 | 94.192 | NaN | NaN | NaN | 23.8422 | NaN | NaN | NaN | NaN | 588.2147 | NaN | 22.2916 | NaN | 25.1441
6081.1292 | 13.9296 | 13.7285 | 13.679 | 13.9407 | 13.2519 | 13.7003 | 13.4128 | 13.2253 | NaN | NaN | NaN | 13.5332 | 94.2349 | NaN | NaN | NaN | 49.2911 | NaN | NaN | NaN | NaN | 590.2749 | NaN | 23.0329 | NaN | 27.018
6082.1292 | 13.9511 | 13.8973 | 13.6843 | 13.8733 | 13.3743 | 13.7066 | 13.4434 | 13.2199 | NaN | NaN | NaN | 13.6568 | 88.7652 | NaN | NaN | NaN | 9.6459 | NaN | NaN | NaN | NaN | 585.0202 | NaN | 20.3792 | NaN | 26.3261
6083.1292 | 13.954 | 13.7055 | 13.6788 | 13.876 | 13.3407 | 13.6387 | 13.4003 | 13.2252 | NaN | NaN | NaN | 13.5772 | 93.4085 | NaN | NaN | NaN | -17.9938 | NaN | NaN | NaN | NaN | 583.0046 | NaN | 26.8644 | NaN | 28.0318
6084.1292 | 14.0104 | 13.6868 | 13.6806 | 13.9281 | 13.2817 | 13.7048 | 13.4094 | 13.2172 | NaN | NaN | NaN | 13.5826 | 93.3455 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 584.0677 | NaN | 24.9855 | NaN | 26.8814
6085.1292 | 13.9849 | 13.6808 | 13.6844 | 13.9028 | 13.3256 | 13.7001 | 13.3987 | 13.2232 | NaN | NaN | NaN | 13.5387 | 92.4193 | NaN | NaN | NaN | -13.7374 | NaN | NaN | NaN | NaN | 586.6112 | NaN | 24.1992 | NaN | 27.8918
6086.1292 | 13.9612 | 13.6567 | 13.6851 | 13.9721 | 13.2933 | 13.6735 | 13.3884 | 13.2238 | NaN | NaN | NaN | 13.5508 | 93.0113 | NaN | NaN | NaN | -13.6755 | NaN | NaN | NaN | NaN | 592.559 | NaN | 24.3863 | NaN | 24.1565
6087.1292 | 14.0977 | 13.7541 | 13.6888 | 13.8841 | 13.403 | 13.7593 | 13.4107 | 13.2202 | NaN | NaN | NaN | 13.6261 | 93.2333 | NaN | NaN | NaN | 5.1926 | NaN | NaN | NaN | NaN | 588.6416 | NaN | 23.2933 | NaN | 28.7157
6088.1292 | 13.9999 | 13.6522 | 13.6883 | 13.9831 | 13.3967 | 13.6748 | 13.3956 | 13.2194 | NaN | NaN | NaN | 13.5943 | 91.3689 | NaN | NaN | NaN | 49.8815 | NaN | NaN | NaN | NaN | 585.2446 | NaN | 22.4612 | NaN | 25.1487
6089.1292 | 13.9396 | 13.6699 | 13.6828 | 13.9067 | 13.3104 | 13.662 | 13.3861 | 13.2163 | NaN | NaN | NaN | 13.5767 | 92.5249 | NaN | NaN | NaN | 20.8005 | NaN | NaN | NaN | NaN | 579.5034 | NaN | 24.0358 | NaN | 28.1632
6090.1292 | 13.9663 | 13.6904 | 13.6969 | 13.9095 | 13.2496 | 13.6913 | 13.4111 | 13.2123 | NaN | NaN | NaN | 13.6086 | 93.7922 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 590.2007 | NaN | 23.2502 | NaN | 27.3419
6091.1292 | 14.0023 | 13.6713 | 13.6971 | 13.9216 | 13.3562 | 13.6605 | 13.4001 | 13.2158 | NaN | NaN | NaN | 13.6148 | 91.9791 | NaN | NaN | NaN | 33.2894 | NaN | NaN | NaN | NaN | 588.4158 | NaN | 22.9536 | NaN | 26.0568
6092.1292 | 14.0106 | 13.692 | 13.6935 | 13.9376 | 13.4372 | 13.6934 | 13.4051 | 13.2153 | NaN | NaN | NaN | 13.621 | 91.1361 | NaN | NaN | NaN | -19.7896 | NaN | NaN | NaN | NaN | 583.5253 | NaN | 23.4428 | NaN | 27.5049
6093.1292 | 13.9154 | 13.7088 | 13.6848 | 13.8981 | 13.4125 | 13.6783 | 13.4041 | 13.2185 | NaN | NaN | NaN | 13.5314 | 91.8994 | NaN | NaN | NaN | 21.6735 | NaN | NaN | NaN | NaN | 584.6644 | NaN | 22.6121 | NaN | 26.5783
6094.1292 | 13.93 | 13.7046 | 13.6856 | 13.8694 | 13.3947 | 13.6869 | 13.4153 | 13.2176 | NaN | NaN | NaN | 13.5167 | 95.0199 | NaN | NaN | NaN | -11.0436 | NaN | NaN | NaN | NaN | 584.2816 | NaN | 23.7309 | NaN | 25.9938
6095.1292 | 14.0821 | 13.6844 | 13.6889 | 13.8632 | 13.3578 | 13.6392 | 13.3856 | 13.2084 | NaN | NaN | NaN | 13.5497 | 93.3156 | NaN | NaN | NaN | -10.2258 | NaN | NaN | NaN | NaN | 580.468 | NaN | 21.9469 | NaN | 26.9967
6096.1292 | 13.8991 | 13.6966 | 13.6883 | 14.1254 | 13.4072 | 13.6488 | 13.4011 | 13.2137 | NaN | NaN | NaN | 13.5388 | 93.1884 | NaN | NaN | NaN | 24.0819 | NaN | NaN | NaN | NaN | 575.6122 | NaN | 23.8026 | NaN | 27.8322
6097.1292 | 13.9358 | 13.693 | 13.6945 | 13.9005 | 13.3512 | 13.6572 | 13.388 | 13.2097 | NaN | NaN | NaN | 13.5393 | 91.6571 | NaN | NaN | NaN | -11.108 | NaN | NaN | NaN | NaN | 579.2185 | NaN | 23.0344 | NaN | 27.1948
6098.1292 | 13.9639 | 13.6436 | 13.6939 | 13.9197 | 13.3826 | 13.6283 | 13.3953 | 13.2148 | NaN | NaN | NaN | 13.5456 | 92.9046 | NaN | NaN | NaN | -11.7997 | NaN | NaN | NaN | NaN | 581.9789 | NaN | 26.2443 | NaN | 26.8838
6099.1292 | 13.942 | 13.6987 | 13.6909 | 13.8754 | 13.3977 | 13.6519 | 13.4028 | 13.212 | NaN | NaN | NaN | 13.5333 | 93.1447 | NaN | NaN | NaN | 12.343 | NaN | NaN | NaN | NaN | 585.3708 | NaN | 21.9673 | NaN | 27.6072
6100.1292 | 13.9546 | 13.7494 | 13.6908 | 13.9047 | 13.3816 | 13.6624 | 13.4123 | 13.2031 | NaN | NaN | NaN | 13.5308 | 93.8619 | NaN | NaN | NaN | 24.8225 | NaN | NaN | NaN | NaN | 581.9598 | NaN | 23.1188 | NaN | 25.7073
6101.1292 | 13.9324 | 13.6875 | 13.6975 | 13.955 | 13.3998 | 13.6338 | 13.3827 | 13.2122 | NaN | NaN | NaN | 13.5563 | 92.8848 | NaN | NaN | NaN | -6.0549 | NaN | NaN | NaN | NaN | 580.8484 | NaN | 24.1599 | NaN | 26.8107
6102.1292 | 13.955 | 13.6654 | 13.6936 | 13.9658 | 13.3682 | 13.6451 | 13.3969 | 13.2099 | NaN | NaN | NaN | 13.5307 | 92.0697 | NaN | NaN | NaN | -16.4901 | NaN | NaN | NaN | NaN | 582.1396 | NaN | 23.7074 | NaN | 26.915
6103.1292 | 13.9206 | 13.6837 | 13.6983 | 13.941 | 13.3822 | 13.7018 | 13.3835 | 13.2108 | NaN | NaN | NaN | 13.6182 | 91.9152 | NaN | NaN | NaN | -12.2508 | NaN | NaN | NaN | NaN | 582.7393 | NaN | 25.4263 | NaN | 26.669
6104.1292 | 13.9345 | 13.695 | 13.6967 | 13.953 | 13.3725 | 13.6335 | 13.3869 | 13.2093 | NaN | NaN | NaN | 13.5324 | 92.4486 | NaN | NaN | NaN | 5.7404 | NaN | NaN | NaN | NaN | 581.0221 | NaN | 23.2361 | NaN | 26.6738
6105.1292 | 13.9251 | 13.662 | 13.6976 | 13.9305 | 13.2918 | 13.7115 | 13.3923 | 13.2148 | NaN | NaN | NaN | 13.5256 | 92.8144 | NaN | NaN | NaN | 19.6496 | NaN | NaN | NaN | NaN | 582.1091 | NaN | 24.0746 | NaN | 25.9572
6106.1292 | 13.9436 | 13.7015 | 13.6994 | 13.917 | 13.4493 | 13.6532 | 13.3838 | 13.2186 | NaN | NaN | NaN | 13.5572 | 97.2421 | NaN | NaN | NaN | 30.3518 | NaN | NaN | NaN | NaN | 579.082 | NaN | 23.0172 | NaN | 26.0931
6107.1292 | 13.9437 | 13.7109 | 13.7076 | 13.9314 | 13.4342 | 13.6524 | 13.387 | 13.2172 | NaN | NaN | NaN | 13.5678 | 91.9546 | NaN | NaN | NaN | 3.5084 | NaN | NaN | NaN | NaN | 579.6073 | NaN | 23.5682 | NaN | 26.9428
6108.1448 | 13.9516 | 13.7646 | 13.7069 | 13.896 | 13.4438 | 13.6415 | 13.4043 | 13.2025 | NaN | NaN | NaN | 13.55 | 92.1877 | NaN | NaN | NaN | -11.5064 | NaN | NaN | NaN | NaN | 581.9989 | NaN | 23.1043 | NaN | 26.1518
6109.1292 | 13.9615 | 13.6724 | 13.7056 | 13.9588 | 13.2977 | 13.6364 | 13.3765 | 13.2048 | NaN | NaN | NaN | 13.5108 | 92.5035 | NaN | NaN | NaN | -2.6745 | NaN | NaN | NaN | NaN | 581.3797 | NaN | 24.5476 | NaN | 25.6789
6110.1292 | 13.9473 | 13.7016 | 13.7038 | 13.8886 | 13.3843 | 13.7059 | 13.3928 | 13.2011 | NaN | NaN | NaN | 13.5807 | 93.0593 | NaN | NaN | NaN | 6.1956 | NaN | NaN | NaN | NaN | 583.2897 | NaN | 21.8463 | NaN | 26.7619
6111.1292 | 13.9715 | 13.6667 | 13.6975 | 13.9235 | 13.2767 | 13.7243 | 13.3927 | 13.2074 | NaN | NaN | NaN | 13.5181 | 92.688 | NaN | NaN | NaN | -15.1224 | NaN | NaN | NaN | NaN | 580.7043 | NaN | 22.5679 | NaN | 27.9423
6112.1292 | 13.8947 | 13.6488 | 13.6932 | 13.9638 | 13.2829 | 13.6707 | 13.3829 | 13.1898 | NaN | NaN | NaN | 13.5415 | 94.3445 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 582.8203 | NaN | 23.5383 | NaN | 26.1559
6113.1292 | 13.9288 | 13.6903 | 13.6937 | 13.924 | 13.2769 | 13.7542 | 13.3691 | 13.1998 | NaN | NaN | NaN | 13.5644 | 93.8556 | NaN | NaN | NaN | 16.8357 | NaN | NaN | NaN | NaN | 582.0824 | NaN | 22.1608 | NaN | 25.5623
6114.1292 | 13.9505 | 13.7015 | 13.6963 | 13.9502 | 13.3282 | 13.6879 | 13.3932 | 13.195 | NaN | NaN | NaN | 13.5351 | 96.0653 | NaN | NaN | NaN | 49.9779 | NaN | NaN | NaN | NaN | 582.1912 | NaN | 24.4927 | NaN | 26.4401
6115.1292 | 13.9176 | 13.6507 | 13.6923 | 13.9347 | 13.323 | 13.7356 | 13.3846 | 13.194 | NaN | NaN | NaN | 13.5723 | 97.927 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 580.8698 | NaN | 23.3306 | NaN | 26.4512
6116.1292 | 13.9144 | 13.7047 | 13.6967 | 13.9599 | 13.3651 | 13.6379 | 13.3907 | 13.1978 | NaN | NaN | NaN | 13.5109 | 95.2278 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 580.0038 | NaN | 22.4814 | NaN | 26.461
6117.1292 | 13.9317 | 13.6491 | 13.6909 | 13.9743 | 13.3981 | 13.6579 | 13.3751 | 13.1967 | NaN | NaN | NaN | 13.5149 | 92.5093 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 580.0322 | NaN | 24.1011 | NaN | 27.9467
6118.1292 | 13.9261 | 13.6825 | 13.6969 | 13.9415 | 13.4561 | 13.6508 | 13.3828 | 13.1949 | NaN | NaN | NaN | 13.5831 | 94.1014 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 572.55 | NaN | 22.1332 | NaN | 26.7683
6119.1292 | 14.0227 | 13.6523 | 13.6988 | 13.9327 | 13.4576 | 13.6773 | 13.384 | 13.2009 | NaN | NaN | NaN | 13.5691 | 93.6042 | NaN | NaN | NaN | -13.4517 | NaN | NaN | NaN | NaN | 574.0744 | NaN | 23.3686 | NaN | 25.0867
6120.1292 | 13.9334 | 13.7931 | 13.6916 | 13.91 | 13.3228 | 13.6295 | 13.4161 | 13.1963 | NaN | NaN | NaN | 13.5285 | 93.0358 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 578.6398 | NaN | 24.2893 | NaN | 26.6952
6121.1292 | 13.935 | 13.624 | 13.6986 | 13.9358 | 13.384 | 13.6804 | 13.3843 | 13.1921 | NaN | NaN | NaN | 13.5126 | 92.3157 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 581.0008 | NaN | 21.7154 | NaN | 27.6841
6122.1292 | 13.9229 | 13.7082 | 13.6942 | 14.1085 | 13.3743 | 13.6312 | 13.3925 | 13.1998 | NaN | NaN | NaN | 13.5621 | 95.1446 | NaN | NaN | NaN | -13.474 | NaN | NaN | NaN | NaN | 583.3116 | NaN | 22.7001 | NaN | 25.9558
6123.1292 | 13.9226 | 13.708 | 13.6989 | 13.9097 | 13.4215 | 13.6581 | 13.4013 | 13.1962 | NaN | NaN | NaN | 13.594 | 92.2674 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 581.9829 | NaN | 21.4242 | NaN | 27.3196
6124.1292 | 13.9287 | 13.6804 | 13.6985 | 13.9648 | 13.3984 | 13.6555 | 13.3952 | 13.1948 | NaN | NaN | NaN | 13.5595 | 90.2248 | NaN | NaN | NaN | 34.4135 | NaN | NaN | NaN | NaN | 580.2976 | NaN | 22.0117 | NaN | 26.5225
6125.1292 | 13.9775 | 13.7926 | 13.6963 | 13.9209 | 13.2686 | 13.6579 | 13.3999 | 13.1976 | NaN | NaN | NaN | 13.5265 | 91.6575 | NaN | NaN | NaN | 1.9725 | NaN | NaN | NaN | NaN | 580.5045 | NaN | 24.145 | NaN | 26.9078
6126.1292 | 13.8715 | 13.6616 | 13.7041 | 13.9622 | 13.4178 | 13.6694 | 13.4019 | 13.2044 | NaN | NaN | NaN | 13.5221 | 93.107 | NaN | NaN | NaN | -16.2469 | NaN | NaN | NaN | NaN | 583.6612 | NaN | 23.7585 | NaN | 26.7283
6127.1292 | 13.9493 | 13.6376 | 13.6882 | 14.0088 | 13.2664 | 13.6388 | 13.377 | 13.2029 | NaN | NaN | NaN | 13.5108 | 93.8407 | NaN | NaN | NaN | 14.6161 | NaN | NaN | NaN | NaN | 583.0002 | NaN | 22.2388 | NaN | 28.5563
6128.1292 | 13.9224 | 13.6295 | 13.6899 | 14.0357 | 13.2268 | 13.634 | 13.3688 | 13.2038 | NaN | NaN | NaN | 13.5213 | 93.579 | NaN | NaN | NaN | 17.6699 | NaN | NaN | NaN | NaN | 587.3038 | NaN | 22.2717 | NaN | 27.7737
6129.1292 | 13.9355 | 13.6738 | 13.6834 | 13.9533 | 13.4336 | 13.907 | 13.3805 | 13.2071 | NaN | NaN | NaN | 13.5449 | 86.2415 | NaN | NaN | NaN | 9.07 | NaN | NaN | NaN | NaN | 586.2712 | NaN | 20.8087 | NaN | 26.8771
6130.1292 | 13.9305 | 13.6176 | 13.683 | 13.9364 | 13.3599 | 13.6316 | 13.3722 | 13.2098 | NaN | NaN | NaN | 13.5578 | 91.8885 | NaN | NaN | NaN | -18.9147 | NaN | NaN | NaN | NaN | 584.9708 | NaN | 24.9805 | NaN | 27.4561
6131.1292 | 13.9637 | 13.6067 | 13.6837 | 13.9674 | 13.401 | 13.6841 | 13.3779 | 13.2065 | NaN | NaN | NaN | 13.5873 | 93.195 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 586.9693 | NaN | 22.2535 | NaN | 25.6416
6132.1292 | 13.9184 | 13.6486 | 13.6854 | 13.939 | 13.4072 | 13.6517 | 13.393 | 13.2129 | NaN | NaN | NaN | 13.5399 | 93.1044 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 587.3648 | NaN | 21.945 | NaN | 27.8034
6133.1292 | 13.916 | 13.6174 | 13.6794 | 14.1573 | 13.4086 | 13.6576 | 13.3794 | 13.2129 | NaN | NaN | NaN | 13.5318 | 93.1465 | NaN | NaN | NaN | 2.2621 | NaN | NaN | NaN | NaN | 586.639 | NaN | 24.3758 | NaN | 25.1829
6134.1292 | 13.9362 | 13.6012 | 13.6804 | 13.9259 | 13.3802 | 13.6595 | 13.3863 | 13.2151 | NaN | NaN | NaN | 13.507 | 90.6447 | NaN | NaN | NaN | 60.4787 | NaN | NaN | NaN | NaN | 584.415 | NaN | 23.4565 | NaN | 27.7615
6135.1292 | 13.9286 | 13.666 | 13.6832 | 13.8978 | 13.3368 | 13.6908 | 13.3918 | 13.2167 | NaN | NaN | NaN | 13.5783 | 93.3585 | NaN | NaN | NaN | 12.0173 | NaN | NaN | NaN | NaN | 583.6353 | NaN | 22.3776 | NaN | 27.1412
6136.1292 | 13.8814 | 13.6155 | 13.6837 | 14.1597 | 13.4082 | 13.6515 | 13.3797 | 13.2106 | NaN | NaN | NaN | 13.6365 | 93.6076 | NaN | NaN | NaN | 27.1137 | NaN | NaN | NaN | NaN | 584.9632 | NaN | 24.5162 | NaN | 25.9596
6137.1292 | 13.9298 | 13.6572 | 13.6834 | 14.009 | 13.2089 | 14.0563 | 13.3853 | 13.2126 | NaN | NaN | NaN | 13.5074 | 92.2357 | NaN | NaN | NaN | -13.5353 | NaN | NaN | NaN | NaN | 586.3642 | NaN | 21.0195 | NaN | 26.2939
6138.1292 | 14.0761 | 13.725 | 13.6812 | 13.9477 | 13.3653 | 13.6854 | 13.395 | 13.2195 | NaN | NaN | NaN | 13.4969 | 90.9208 | NaN | NaN | NaN | 1.0374 | NaN | NaN | NaN | NaN | 584.8609 | NaN | 21.0374 | NaN | 27.9792
6139.1292 | 13.9462 | 13.6812 | 13.6825 | 14 | 13.4503 | 13.639 | 13.3958 | 13.2157 | NaN | NaN | NaN | 13.4998 | 93.4425 | NaN | NaN | NaN | 8.4952 | NaN | NaN | NaN | NaN | 582.6182 | NaN | 24.0866 | NaN | 25.69
6140.1292 | 13.9421 | 13.6161 | 13.6817 | 13.9432 | 13.4274 | 13.6101 | 13.3917 | 13.2181 | NaN | NaN | NaN | 13.5472 | 91.6347 | NaN | NaN | NaN | 42.2451 | NaN | NaN | NaN | NaN | 580.9146 | NaN | 25.357 | NaN | 26.6203
6141.1292 | 13.9268 | 13.6806 | 13.679 | 13.9806 | 13.4161 | 13.632 | 13.3973 | 13.2142 | NaN | NaN | NaN | 13.5359 | 91.3825 | NaN | NaN | NaN | -3.4361 | NaN | NaN | NaN | NaN | 580.5223 | NaN | 21.6584 | NaN | 26.8801
6142.1292 | 13.9524 | 13.733 | 13.6687 | 13.9714 | 13.2557 | 13.6118 | 13.4049 | 13.2065 | NaN | NaN | NaN | 13.6124 | 93.5852 | NaN | NaN | NaN | 0.9456 | NaN | NaN | NaN | NaN | 582.3893 | NaN | 24.044 | NaN | 26.0084
6143.1292 | 14.0003 | 13.6447 | 13.67 | 13.9677 | 13.3074 | 13.6811 | 13.395 | 13.2068 | NaN | NaN | NaN | 13.5381 | 94.9565 | NaN | NaN | NaN | 16.3101 | NaN | NaN | NaN | NaN | 583.898 | NaN | 24.2539 | NaN | 26.6104
6144.1292 | 13.9274 | 13.6443 | 13.663 | 13.9867 | 13.3029 | 13.7206 | 13.4015 | 13.2143 | NaN | NaN | NaN | 13.6932 | 92.46 | NaN | NaN | NaN | -5.0463 | NaN | NaN | NaN | NaN | 582.4686 | NaN | 20.9304 | NaN | 27.8498
6145.1292 | 13.9405 | 13.6307 | 13.6529 | 14.0021 | 13.3413 | 13.609 | 13.3882 | 13.2112 | NaN | NaN | NaN | 13.5101 | 91.9955 | NaN | NaN | NaN | 4.7207 | NaN | NaN | NaN | NaN | 577.1173 | NaN | 21.5268 | NaN | 26.0889
6146.1292 | 13.9367 | 13.6233 | 13.6667 | 13.9988 | 13.3966 | 13.6225 | 13.3903 | 13.2088 | NaN | NaN | NaN | 13.5391 | 93.1193 | NaN | NaN | NaN | 9.203 | NaN | NaN | NaN | NaN | 581.6254 | NaN | 22.0859 | NaN | 24.7416
6147.1292 | 13.9466 | 13.6196 | 13.665 | 13.9331 | 13.3748 | 13.5988 | 13.3854 | 13.2111 | NaN | NaN | NaN | 13.4947 | 91.0958 | NaN | NaN | NaN | 21.4417 | NaN | NaN | NaN | NaN | 583.962 | NaN | 22.1211 | NaN | 25.692
6148.1292 | 13.9253 | 13.6515 | 13.6646 | 13.9514 | 13.2877 | 13.6145 | 13.3875 | 13.2082 | NaN | NaN | NaN | 13.4796 | 93.2869 | NaN | NaN | NaN | 3.5654 | NaN | NaN | NaN | NaN | 585.5633 | NaN | 23.0568 | NaN | 26.602
6149.1292 | 14.0407 | 13.7058 | 13.6603 | 14.0079 | 13.3652 | 13.614 | 13.4039 | 13.2062 | NaN | NaN | NaN | 13.5213 | 94.286 | NaN | NaN | NaN | 47.5574 | NaN | NaN | NaN | NaN | 582.8291 | NaN | 19.2836 | NaN | 26.137
6150.1292 | 13.9306 | 13.6823 | 13.648 | 14.032 | 13.3245 | 13.63 | 13.3978 | 13.2144 | NaN | NaN | NaN | 13.5996 | 90.9299 | NaN | NaN | NaN | 27.3583 | NaN | NaN | NaN | NaN | 586.337 | NaN | 21.2761 | NaN | 28.2792
6151.1292 | 13.9815 | 13.6014 | 13.6527 | 13.954 | 13.3449 | 13.6569 | 13.3779 | 13.2033 | NaN | NaN | NaN | 13.5487 | 93.4954 | NaN | NaN | NaN | 12.5446 | NaN | NaN | NaN | NaN | 581.9081 | NaN | 21.8841 | NaN | 26.6298
6152.1292 | 13.8966 | 13.6039 | 13.6548 | 13.9453 | 13.3157 | 13.5924 | 13.3755 | 13.2007 | NaN | NaN | NaN | 13.5281 | 102.149 | NaN | NaN | NaN | 39.3134 | NaN | NaN | NaN | NaN | 579.8527 | NaN | 20.4358 | NaN | 25.2392
6153.1292 | 13.9045 | 13.638 | 13.6555 | 13.9799 | 13.4214 | 13.6297 | 13.3908 | 13.2023 | NaN | NaN | NaN | 13.5959 | 93.297 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 579.5745 | NaN | 21.6348 | NaN | 25.6775
6154.1292 | 13.9062 | 13.5873 | 13.6548 | 13.9769 | 13.4763 | 13.603 | 13.3832 | 13.205 | NaN | NaN | NaN | 13.5344 | 94.172 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 578.8554 | NaN | 22.9392 | NaN | 25.6737
6155.1292 | 13.9525 | 13.6027 | 13.6611 | 13.95 | 13.3541 | 13.6229 | 13.3856 | 13.2046 | NaN | NaN | NaN | 13.4729 | 91.3117 | NaN | NaN | NaN | 9.4348 | NaN | NaN | NaN | NaN | 579.974 | NaN | 21.2017 | NaN | 25.5966
6156.1292 | 13.9592 | 13.7874 | 13.6644 | 13.9765 | 13.3269 | 13.6412 | 13.4064 | 13.2065 | NaN | NaN | NaN | 13.5089 | 97.4758 | NaN | NaN | NaN | -12.6692 | NaN | NaN | NaN | NaN | 584.9939 | NaN | 21.7316 | NaN | 25.0972
6157.1292 | 13.9662 | 13.6101 | 13.6638 | 13.971 | 13.4612 | 13.601 | 13.373 | 13.2011 | NaN | NaN | NaN | 13.5517 | 94.6366 | NaN | NaN | NaN | -12.5779 | NaN | NaN | NaN | NaN | 582.3126 | NaN | 20.8121 | NaN | 27.2825
6158.1292 | 14.0264 | 13.7142 | 13.6654 | 13.945 | 13.3023 | 13.6174 | 13.4037 | 13.1977 | NaN | NaN | NaN | 13.4672 | 93.2955 | NaN | NaN | NaN | -10.7865 | NaN | NaN | NaN | NaN | 582.9848 | NaN | 23.1328 | NaN | 26.1151
6159.1292 | 14.0658 | 13.6244 | 13.6599 | 13.9491 | 13.4137 | 13.6372 | 13.3869 | 13.2032 | NaN | NaN | NaN | 13.5166 | 91.8932 | NaN | NaN | NaN | -16.6718 | NaN | NaN | NaN | NaN | 583.111 | NaN | 23.1383 | NaN | 27.701
6160.1292 | 13.9195 | 13.6759 | 13.6672 | 13.9613 | 13.336 | 13.7355 | 13.3931 | 13.2092 | NaN | NaN | NaN | 13.4525 | 92.1862 | NaN | NaN | NaN | -10.2133 | NaN | NaN | NaN | NaN | 583.4594 | NaN | 23.2063 | NaN | 25.9342
6161.1292 | 14.0011 | 13.6501 | 13.6623 | 13.9495 | 13.2994 | 13.6224 | 13.3906 | 13.2079 | NaN | NaN | NaN | 13.529 | 92.9553 | NaN | NaN | NaN | -18.7798 | NaN | NaN | NaN | NaN | 583.8786 | NaN | 22.5505 | NaN | 27.1205
6162.1292 | 14.2536 | 13.5707 | 13.6639 | 14 | 13.3381 | 13.6355 | 13.3706 | 13.2044 | NaN | NaN | NaN | 13.4405 | 96.1562 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 583.1967 | NaN | 21.4221 | NaN | 27.9365
6163.1292 | 13.9472 | 13.5788 | 13.6642 | 13.9721 | 13.3335 | 13.6519 | 13.3594 | 13.2034 | NaN | NaN | NaN | 13.4734 | 91.967 | NaN | NaN | NaN | -6.7013 | NaN | NaN | NaN | NaN | 580.9028 | NaN | 23.6997 | NaN | 27.4514
6164.1292 | 13.9638 | 13.5863 | 13.6588 | 13.9656 | 13.373 | 13.6573 | 13.3707 | 13.2054 | NaN | NaN | NaN | 13.47 | 93.3285 | NaN | NaN | NaN | 3.7548 | NaN | NaN | NaN | NaN | 580.9278 | NaN | 23.2066 | NaN | 27.1369
6165.1292 | 13.9789 | 13.5844 | 13.6572 | 13.9573 | 13.3964 | 13.6061 | 13.3602 | 13.2021 | NaN | NaN | NaN | 13.5303 | 92.301 | NaN | NaN | NaN | 49.7008 | NaN | NaN | NaN | NaN | 584.2711 | NaN | 22.8889 | NaN | 27.5527
6166.1292 | 13.9693 | 13.6331 | 13.6674 | 13.9738 | 13.4742 | 13.6857 | 13.3717 | 13.2028 | NaN | NaN | NaN | 13.5248 | 93.6791 | NaN | NaN | NaN | -12.2378 | NaN | NaN | NaN | NaN | 584.0303 | NaN | 22.4024 | NaN | 25.9227
6167.1292 | 14.0337 | 13.6271 | 13.6638 | 13.9315 | 13.3797 | 13.7041 | 13.3848 | 13.1999 | NaN | NaN | NaN | 13.505 | 97.1905 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 583.7322 | NaN | 22.2943 | NaN | 27.0666
6168.1292 | 14.0166 | 13.5785 | 13.6627 | 13.9221 | 13.266 | 13.6777 | 13.3698 | 13.2086 | NaN | NaN | NaN | 13.5742 | 91.8499 | NaN | NaN | NaN | -18.6128 | NaN | NaN | NaN | NaN | 586.2464 | NaN | 22.9363 | NaN | 24.9765
6169.1292 | 13.9911 | 13.5685 | 13.6661 | 13.955 | 13.3099 | 13.6403 | 13.378 | 13.2094 | NaN | NaN | NaN | 13.5821 | 95.3985 | NaN | NaN | NaN | -10.3302 | NaN | NaN | NaN | NaN | 586.5297 | NaN | 20.7582 | NaN | 23.4351
6170.1292 | 13.9745 | 13.5569 | 13.6769 | 13.961 | 13.4693 | 13.5976 | 13.3735 | 13.2025 | NaN | NaN | NaN | 13.4582 | 93.1733 | NaN | NaN | NaN | -16.4336 | NaN | NaN | NaN | NaN | 588.0367 | NaN | 21.585 | NaN | 26.2041
6171.1292 | 13.9914 | 13.6175 | 13.6721 | 13.9544 | 13.4502 | 13.6187 | 13.3804 | 13.2066 | NaN | NaN | NaN | 13.4718 | 92.1498 | NaN | NaN | NaN | -16.8554 | NaN | NaN | NaN | NaN | 585.2046 | NaN | 21.8215 | NaN | 27.7248
6172.1292 | 13.9303 | 13.63 | 13.6758 | 13.9047 | 13.2984 | 13.6309 | 13.3868 | 13.1979 | NaN | NaN | NaN | 13.4467 | 91.333 | NaN | NaN | NaN | -17.5677 | NaN | NaN | NaN | NaN | 588.7085 | NaN | 22.5803 | NaN | 25.4778
6173.1292 | 13.9572 | 13.6007 | 13.6746 | 13.9619 | 13.3001 | 13.6281 | 13.3861 | 13.2053 | NaN | NaN | NaN | 13.5089 | 92.0715 | NaN | NaN | NaN | -16.6711 | NaN | NaN | NaN | NaN | 587.3523 | NaN | 22.7697 | NaN | 24.5987
6174.1292 | 13.9636 | 13.7863 | 13.6736 | 14.023 | 13.3265 | 13.6685 | 13.4029 | 13.2069 | NaN | NaN | NaN | 13.4688 | 86.3701 | NaN | NaN | NaN | 19.9072 | NaN | NaN | NaN | NaN | 586.3378 | NaN | 23.2198 | NaN | 27.0105
6175.1292 | 14.0052 | 13.6601 | 13.6794 | 13.9748 | 13.3944 | 13.6124 | 13.4061 | 13.2086 | NaN | NaN | NaN | 13.4992 | 93.9582 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 584.3319 | NaN | 23.5398 | NaN | 26.3527
6176.1292 | 14.0046 | 13.5806 | 13.6839 | 13.988 | 13.43 | 13.7413 | 13.3719 | 13.2064 | NaN | NaN | NaN | 13.4919 | 91.8344 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 584.835 | NaN | 22.0523 | NaN | 25.9361
6177.1292 | 14.0535 | 13.5865 | 13.685 | 14.0812 | 13.3699 | 13.7251 | 13.3822 | 13.2085 | NaN | NaN | NaN | 13.5167 | 93.1568 | NaN | NaN | NaN | 19.9478 | NaN | NaN | NaN | NaN | 586.3288 | NaN | 23.3674 | NaN | 25.2043
6178.1292 | 13.9712 | 13.5949 | 13.6829 | 13.9651 | 13.4817 | 13.6948 | 13.3712 | 13.209 | NaN | NaN | NaN | 13.4792 | 93.1218 | NaN | NaN | NaN | -8.6256 | NaN | NaN | NaN | NaN | 585.4522 | NaN | 22.6548 | NaN | 26.319
6179.1292 | 13.9995 | 13.5891 | 13.6795 | 13.9279 | 13.341 | 13.6275 | 13.3647 | 13.2149 | NaN | NaN | NaN | 13.4811 | 92.4054 | NaN | NaN | NaN | -11.0544 | NaN | NaN | NaN | NaN | 583.024 | NaN | 23.3238 | NaN | 26.7721
6180.1292 | 14.0285 | 13.6543 | 13.6755 | 13.9907 | 13.4093 | 13.6528 | 13.3712 | 13.2112 | NaN | NaN | NaN | 13.4752 | 93.7919 | NaN | NaN | NaN | -6.0282 | NaN | NaN | NaN | NaN | 580.0595 | NaN | 20.2992 | NaN | 25.7643
6181.1292 | 13.997 | 13.6133 | 13.6779 | 13.9108 | 13.3742 | 13.6836 | 13.3839 | 13.2109 | NaN | NaN | NaN | 13.5527 | 94.2363 | NaN | NaN | NaN | -10.4956 | NaN | NaN | NaN | NaN | 584.6883 | NaN | 23.513 | NaN | 25.7372
6182.1292 | 14.015 | 13.6745 | 13.6788 | 13.9344 | 13.3601 | 13.6346 | 13.3909 | 13.2052 | NaN | NaN | NaN | 13.6275 | 95.1397 | NaN | NaN | NaN | 20.4927 | NaN | NaN | NaN | NaN | 584.2179 | NaN | 22.637 | NaN | 26.5353
6183.1292 | 13.9771 | 13.5809 | 13.6852 | 13.8999 | 13.2801 | 13.6625 | 13.3804 | 13.2103 | NaN | NaN | NaN | 13.5464 | 90.5316 | NaN | NaN | NaN | 28.3891 | NaN | NaN | NaN | NaN | 583.5655 | NaN | 21.388 | NaN | 25.789
6184.1292 | 14.0062 | 13.6251 | 13.6826 | 14.0683 | 13.2444 | 13.6267 | 13.3683 | 13.2106 | NaN | NaN | NaN | 13.5195 | 92.0458 | NaN | NaN | NaN | -1.9731 | NaN | NaN | NaN | NaN | 583.5729 | NaN | 22.7925 | NaN | 24.203
6185.1292 | 13.9596 | 13.5923 | 13.6858 | 13.9482 | 13.3323 | 13.6268 | 13.3686 | 13.1983 | NaN | NaN | NaN | 13.4686 | 92.2902 | NaN | NaN | NaN | 15.3144 | NaN | NaN | NaN | NaN | 584.1622 | NaN | 21.5294 | NaN | 27.8874
6186.1292 | 13.9775 | 13.6093 | 13.6806 | 13.938 | 13.375 | 13.6925 | 13.3791 | 13.2048 | NaN | NaN | NaN | 13.6114 | 93.4096 | NaN | NaN | NaN | 24.4795 | NaN | NaN | NaN | NaN | 584.771 | NaN | 20.9847 | NaN | 25.9626
6187.1292 | 13.9579 | 13.5856 | 13.6929 | 13.9706 | 13.311 | 13.7914 | 13.3722 | 13.2026 | NaN | NaN | NaN | 13.4984 | 92.6241 | NaN | NaN | NaN | -10.475 | NaN | NaN | NaN | NaN | 584.7311 | NaN | 22.495 | NaN | 26.1414
6188.1292 | 14.0075 | 13.6131 | 13.6911 | 13.9654 | 13.4179 | 13.6543 | 13.3627 | 13.1993 | NaN | NaN | NaN | 13.4803 | 94.6603 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 580.7021 | NaN | 21.244 | NaN | 25.7056
6189.1292 | 13.941 | 13.6538 | 13.6882 | 13.9189 | 13.404 | 13.6476 | 13.3726 | 13.2009 | NaN | NaN | NaN | 13.485 | 93.7097 | NaN | NaN | NaN | -10.3291 | NaN | NaN | NaN | NaN | 583.7509 | NaN | 22.7848 | NaN | 26.1773
6190.1292 | 13.9826 | 13.6032 | 13.6829 | 13.9708 | 13.3587 | 13.6473 | 13.3659 | 13.1994 | NaN | NaN | NaN | 13.5286 | 93.3554 | NaN | NaN | NaN | 45.3821 | NaN | NaN | NaN | NaN | 581.7445 | NaN | 22.6443 | NaN | 27.5842
6191.1292 | 13.9982 | 13.587 | 13.6855 | 13.9949 | 13.4048 | 13.6523 | 13.3641 | 13.1945 | NaN | NaN | NaN | 13.7382 | 92.6443 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 581.7934 | NaN | 21.2143 | NaN | 24.5341
6192.1292 | 13.9796 | 13.6309 | 13.6927 | 13.958 | 13.3902 | 13.6493 | 13.3777 | 13.195 | NaN | NaN | NaN | 13.4535 | 91.5966 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 582.9056 | NaN | 24.1788 | NaN | 27.0777
6193.1292 | 13.9661 | 13.7049 | 13.6914 | 13.9231 | 13.3751 | 13.8118 | 13.3797 | 13.2034 | NaN | NaN | NaN | 13.4675 | 94.3409 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 582.7491 | NaN | 22.6111 | NaN | 27.3362
6194.1292 | 13.9843 | 13.5941 | 13.6871 | 13.9691 | 13.4052 | 13.6695 | 13.3602 | 13.2009 | NaN | NaN | NaN | 13.5155 | 91.7076 | NaN | NaN | NaN | -10.5367 | NaN | NaN | NaN | NaN | 583.702 | NaN | 23.1561 | NaN | 27.7715
6195.1292 | 14.1304 | 13.5872 | 13.6893 | 13.963 | 13.3093 | 13.6685 | 13.37 | 13.2102 | NaN | NaN | NaN | 13.5737 | 91.3702 | NaN | NaN | NaN | 60.1379 | NaN | NaN | NaN | NaN | 587.7459 | NaN | 21.572 | NaN | 27.3825
6196.1292 | 13.9636 | 13.552 | 13.6903 | 13.9811 | 13.369 | 13.6712 | 13.3497 | 13.209 | NaN | NaN | NaN | 13.475 | 91.3355 | NaN | NaN | NaN | 10.0603 | NaN | NaN | NaN | NaN | 584.5623 | NaN | 20.7451 | NaN | 26.1818
6197.1292 | 13.9688 | 13.5688 | 13.6907 | 13.9681 | 13.2959 | 13.7295 | 13.3468 | 13.2099 | NaN | NaN | NaN | 13.5331 | 92.3384 | NaN | NaN | NaN | 19.0414 | NaN | NaN | NaN | NaN | 587.6282 | NaN | 23.0881 | NaN | 26.6339
6198.1292 | 13.9859 | 13.5784 | 13.6907 | 13.9138 | 13.4102 | 13.6444 | 13.3513 | 13.2054 | NaN | NaN | NaN | 13.5591 | 93.236 | NaN | NaN | NaN | 21.7394 | NaN | NaN | NaN | NaN | 583.3807 | NaN | 21.5402 | NaN | 26.0859
6199.1292 | 13.9782 | 13.5644 | 13.6894 | 13.9525 | 13.3068 | 13.6381 | 13.3615 | 13.2102 | NaN | NaN | NaN | 13.4493 | 93.0752 | NaN | NaN | NaN | 24.1264 | NaN | NaN | NaN | NaN | 584.3981 | NaN | 21.1798 | NaN | 28.4406
6200.1292 | 13.9871 | 13.5812 | 13.6924 | 13.935 | 13.3777 | 13.6413 | 13.3611 | 13.2049 | NaN | NaN | NaN | 13.5424 | 92.1963 | NaN | NaN | NaN | 3.941 | NaN | NaN | NaN | NaN | 587.7212 | NaN | 22.4909 | NaN | 27.8492
6201.1292 | 14.0285 | 13.6879 | 13.6958 | 13.9701 | 13.3983 | 13.6686 | 13.3879 | 13.2064 | NaN | NaN | NaN | 13.4657 | 91.8671 | NaN | NaN | NaN | 0.5465 | NaN | NaN | NaN | NaN | 586.3947 | NaN | 20.8231 | NaN | 26.7807
6202.1292 | 13.9949 | 13.5618 | 13.6906 | 13.9306 | 13.3151 | 13.6309 | 13.3715 | 13.1993 | NaN | NaN | NaN | 13.4552 | 92.3071 | NaN | NaN | NaN | -3.3188 | NaN | NaN | NaN | NaN | 588.1684 | NaN | 23.1515 | NaN | 26.3564
6203.1292 | 13.9727 | 13.6255 | 13.6901 | 13.9893 | 13.3938 | 13.6577 | 13.3741 | 13.1981 | NaN | NaN | NaN | 13.4975 | 91.9054 | NaN | NaN | NaN | 23.7389 | NaN | NaN | NaN | NaN | 584.4233 | NaN | 19.723 | NaN | 27.8496
6204.1292 | 13.9681 | 13.6175 | 13.6886 | 13.9344 | 13.3236 | 13.6218 | 13.3612 | 13.1963 | NaN | NaN | NaN | 13.5892 | 96.2949 | NaN | NaN | NaN | -6.1589 | NaN | NaN | NaN | NaN | 579.6883 | NaN | 20.7228 | NaN | 25.7789
6205.1292 | 13.9733 | 13.6639 | 13.6909 | 13.9717 | 13.3233 | 13.6485 | 13.3861 | 13.2023 | NaN | NaN | NaN | 13.4773 | 94.9632 | NaN | NaN | NaN | 19.587 | NaN | NaN | NaN | NaN | 572.3806 | NaN | 21.2162 | NaN | 27.7029
6206.1292 | 13.9986 | 13.5725 | 13.6917 | 13.9387 | 13.3871 | 13.679 | 13.3621 | 13.1985 | NaN | NaN | NaN | 13.4714 | 91.938 | NaN | NaN | NaN | -17.7643 | NaN | NaN | NaN | NaN | 574.8154 | NaN | 20.99 | NaN | 27.1036
6207.1292 | 14.0802 | 13.6095 | 13.6875 | 13.9916 | 13.3652 | 13.7056 | 13.367 | 13.2019 | NaN | NaN | NaN | 13.4655 | 93.7183 | NaN | NaN | NaN | -19.5549 | NaN | NaN | NaN | NaN | 576.131 | NaN | 19.0582 | NaN | 28.1223
6208.1292 | 13.9833 | 13.6461 | 13.6843 | 13.9796 | 13.3839 | 13.6642 | 13.3859 | 13.1958 | NaN | NaN | NaN | 13.4942 | 95.8149 | NaN | NaN | NaN | -17.5811 | NaN | NaN | NaN | NaN | 572.5731 | NaN | 21.7783 | NaN | 26.1567
6209.1292 | 13.9935 | 13.5953 | 13.6809 | 13.9479 | 13.2467 | 13.7002 | 13.3608 | 13.2001 | NaN | NaN | NaN | 13.4734 | 93.1386 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 571.0462 | NaN | 19.1015 | NaN | 26.3765
6210.1292 | 14.0366 | 13.6175 | 13.6757 | 13.9294 | 13.4319 | 13.6738 | 13.3776 | 13.2019 | NaN | NaN | NaN | 13.4521 | 93.5686 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 575.3737 | NaN | 23.0151 | NaN | 26.3898
6211.1292 | 13.9261 | 13.628 | 13.6738 | 13.9577 | 13.3122 | 13.6497 | 13.3743 | 13.1959 | NaN | NaN | NaN | 13.5191 | 92.0523 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 573.1515 | NaN | 23.7817 | NaN | 26.6625
6212.1292 | 13.9481 | 13.5851 | 13.6745 | 13.9603 | 13.4412 | 13.8326 | 13.3647 | 13.2004 | NaN | NaN | NaN | 13.5954 | 91.8505 | NaN | NaN | NaN | -10.9666 | NaN | NaN | NaN | NaN | 571.964 | NaN | 21.7684 | NaN | 25.2465
6213.1292 | 13.9792 | 13.579 | 13.678 | 13.94 | 13.3164 | 13.6408 | 13.3746 | 13.1989 | NaN | NaN | NaN | 13.4582 | 92.7296 | NaN | NaN | NaN | 28.4746 | NaN | NaN | NaN | NaN | 573.7642 | NaN | 22.2308 | NaN | 25.3156
6214.1292 | 14.2149 | 13.6033 | 13.6792 | 13.9824 | 13.4263 | 13.6653 | 13.3746 | 13.2019 | NaN | NaN | NaN | 13.4705 | 91.7625 | NaN | NaN | NaN | -18.2859 | NaN | NaN | NaN | NaN | 577.1746 | NaN | 19.9181 | NaN | 27.4026
6215.1292 | 14.0294 | 13.6266 | 13.6741 | 13.9745 | 13.2724 | 13.701 | 13.3672 | 13.1952 | NaN | NaN | NaN | 13.4826 | 94.1313 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 581.5542 | NaN | 22.8054 | NaN | 24.9563
6216.1292 | 14.0399 | 13.6287 | 13.6805 | 13.9697 | 13.4286 | 13.7136 | 13.3703 | 13.1933 | NaN | NaN | NaN | 13.4683 | 93.507 | NaN | NaN | NaN | -13.2189 | NaN | NaN | NaN | NaN | 581.4531 | NaN | 19.3946 | NaN | 25.6947
6217.1292 | 14.0824 | 13.615 | 13.6853 | 13.9609 | 13.3733 | 13.6586 | 13.362 | 13.1986 | NaN | NaN | NaN | 13.4522 | 92.6939 | NaN | NaN | NaN | -9.8037 | NaN | NaN | NaN | NaN | 580.6331 | NaN | 22.1843 | NaN | 26.1212
6218.1292 | 13.9352 | 13.5698 | 13.6754 | 13.9353 | 13.3968 | 13.6299 | 13.3566 | 13.1934 | NaN | NaN | NaN | 13.5224 | 95.3173 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 579.4423 | NaN | 23.0202 | NaN | 26.6874
6219.1292 | 13.9195 | 13.5847 | 13.6877 | 13.9425 | 13.4289 | 13.6388 | 13.3579 | 13.194 | NaN | NaN | NaN | 13.5275 | 92.3662 | NaN | NaN | NaN | -9.5928 | NaN | NaN | NaN | NaN | 578.0767 | NaN | 23.4434 | NaN | 26.9999
6220.1292 | 13.9371 | 13.6444 | 13.6807 | 13.937 | 13.4407 | 13.6292 | 13.3766 | 13.203 | NaN | NaN | NaN | 13.4647 | 99.6425 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 568.9801 | NaN | 24.9507 | NaN | 27.2898
6221.1292 | 13.9782 | 13.5692 | 13.6808 | 13.9118 | 13.3387 | 13.646 | 13.3679 | 13.2045 | NaN | NaN | NaN | 13.6131 | 92.0163 | NaN | NaN | NaN | -2.982 | NaN | NaN | NaN | NaN | 565.326 | NaN | 23.1448 | NaN | 25.5269
6222.1292 | 14.0478 | 13.5635 | 13.686 | 13.892 | 13.4089 | 13.6467 | 13.381 | 13.2009 | NaN | NaN | NaN | 13.4812 | 95.8648 | NaN | NaN | NaN | 29.1137 | NaN | NaN | NaN | NaN | 559.9328 | NaN | 22.0751 | NaN | 26.8255
6223.1292 | 13.9692 | 13.5659 | 13.682 | 13.9914 | 13.3652 | 13.6496 | 13.3632 | 13.1996 | NaN | NaN | NaN | 13.5008 | 93.0368 | NaN | NaN | NaN | 6.8497 | NaN | NaN | NaN | NaN | 556.6274 | NaN | 21.5539 | NaN | 25.0655
6224.1292 | 14.3221 | 13.6559 | 13.6839 | 13.9513 | 13.37 | 13.7456 | 13.3786 | 13.2052 | NaN | NaN | NaN | 13.496 | 93.0496 | NaN | NaN | NaN | 32.5999 | NaN | NaN | NaN | NaN | 561.9571 | NaN | 23.2388 | NaN | 27.5918
6225.1292 | 13.9379 | 13.5945 | 13.6794 | 13.9962 | 13.3146 | 13.624 | 13.3622 | 13.2019 | NaN | NaN | NaN | 13.4524 | 90.6261 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 550.6045 | NaN | 22.5829 | NaN | 26.1672
6226.1292 | 13.9692 | 13.6162 | 13.6799 | 13.9662 | 13.4566 | 13.6472 | 13.3784 | 13.1967 | NaN | NaN | NaN | 13.522 | 93.5825 | NaN | NaN | NaN | -19.4774 | NaN | NaN | NaN | NaN | 545.7282 | NaN | 22.3558 | NaN | 27.7655
6227.1292 | 13.9757 | 13.61 | 13.6806 | 14.0067 | 13.3171 | 13.7832 | 13.379 | 13.197 | NaN | NaN | NaN | 13.4734 | 91.7785 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 550.2342 | NaN | 21.7712 | NaN | 26.4754
6228.1292 | 14.0437 | 13.6373 | 13.6836 | 14.0526 | 13.3139 | 13.6517 | 13.3786 | 13.1969 | NaN | NaN | NaN | 13.5649 | 94.9657 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 560.3719 | NaN | 22.1246 | NaN | 28.1703
6229.1292 | 13.9931 | 13.6859 | 13.6881 | 13.916 | 13.3174 | 13.6502 | 13.3962 | 13.197 | NaN | NaN | NaN | 13.5312 | 90.9376 | NaN | NaN | NaN | 13.8249 | NaN | NaN | NaN | NaN | 571.4812 | NaN | 22.0511 | NaN | 26.2357
6230.1292 | 13.9819 | 13.6053 | 13.6905 | 14.0035 | 13.3825 | 13.686 | 13.3745 | 13.1911 | NaN | NaN | NaN | 13.4821 | 93.2646 | NaN | NaN | NaN | -9.6406 | NaN | NaN | NaN | NaN | 581.142 | NaN | 22.1847 | NaN | 25.7964
6231.1292 | 14.0858 | 13.5888 | 13.6857 | 13.9884 | 13.3801 | 13.7026 | 13.3735 | 13.1989 | NaN | NaN | NaN | 13.5026 | 93.0065 | NaN | NaN | NaN | -3.2517 | NaN | NaN | NaN | NaN | 582.3314 | NaN | 23.8497 | NaN | 27.2636
6232.1292 | 13.9567 | 13.6177 | 13.69 | 13.9899 | 13.362 | 13.7193 | 13.3793 | 13.1958 | NaN | NaN | NaN | 13.5577 | 93.7498 | NaN | NaN | NaN | 30.4071 | NaN | NaN | NaN | NaN | 581.5873 | NaN | 22.6394 | NaN | 26.5096
6233.1292 | 13.9665 | 13.6555 | 13.6798 | 13.9473 | 13.3061 | 13.66 | 13.3853 | 13.2017 | NaN | NaN | NaN | 13.4962 | 94.2794 | NaN | NaN | NaN | -5.5473 | NaN | NaN | NaN | NaN | 580.4716 | NaN | 23.5293 | NaN | 28.0782
6234.1292 | 13.9785 | 13.6179 | 13.6904 | 13.955 | 13.428 | 13.6842 | 13.378 | 13.1894 | NaN | NaN | NaN | 13.4921 | 91.2881 | NaN | NaN | NaN | 3.8237 | NaN | NaN | NaN | NaN | 581.464 | NaN | 21.9198 | NaN | 27.0684
6235.1292 | 13.9424 | 13.7396 | 13.682 | 13.964 | 13.4203 | 13.7931 | 13.4027 | 13.1976 | NaN | NaN | NaN | 13.465 | 92.2206 | NaN | NaN | NaN | 41.1616 | NaN | NaN | NaN | NaN | 580.2832 | NaN | 21.9031 | NaN | 26.509
6236.1292 | 13.952 | 13.7172 | 13.6791 | 13.9926 | 13.4136 | 13.7418 | 13.4015 | 13.1976 | NaN | NaN | NaN | 13.5106 | 91.6597 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 581.2348 | NaN | 22.7249 | NaN | 27.2644
6237.1292 | 13.9596 | 13.7487 | 13.6794 | 14.0522 | 13.401 | 13.755 | 13.3806 | 13.1974 | NaN | NaN | NaN | 13.5509 | 92.8042 | NaN | NaN | NaN | -10.9202 | NaN | NaN | NaN | NaN | 578.879 | NaN | 23.6867 | NaN | 28.12
6238.1292 | 13.9796 | 13.6056 | 13.6705 | 13.9718 | 13.3764 | 13.6455 | 13.3686 | 13.1959 | NaN | NaN | NaN | 13.5484 | 92.461 | NaN | NaN | NaN | 18.2925 | NaN | NaN | NaN | NaN | 579.3958 | NaN | 24.2627 | NaN | 27.2531
6239.1292 | 14.0054 | 13.6219 | 13.6665 | 13.9935 | 13.4117 | 13.6555 | 13.367 | 13.1998 | NaN | NaN | NaN | 13.6164 | 94.3969 | NaN | NaN | NaN | 24.7568 | NaN | NaN | NaN | NaN | 583.194 | NaN | 20.5445 | NaN | 23.7399
6240.1292 | 13.9491 | 13.6538 | 13.6627 | 13.9564 | 13.3917 | 13.6889 | 13.3772 | 13.205 | NaN | NaN | NaN | 13.4903 | 94.4853 | NaN | NaN | NaN | 4.7191 | NaN | NaN | NaN | NaN | 581.7236 | NaN | 22.6568 | NaN | 27.1881
6241.1292 | 13.9767 | 13.7078 | 13.6564 | 14.008 | 13.3622 | 13.6678 | 13.3876 | 13.2018 | NaN | NaN | NaN | 13.4783 | 91.9803 | NaN | NaN | NaN | 57.2475 | NaN | NaN | NaN | NaN | 582.8466 | NaN | 20.5214 | NaN | 26.6952
6242.1292 | 14.0184 | 13.7028 | 13.659 | 14.0914 | 13.3653 | 13.6707 | 13.4117 | 13.1999 | NaN | NaN | NaN | 13.4654 | 91.4356 | NaN | NaN | NaN | 4.1503 | NaN | NaN | NaN | NaN | 585.2244 | NaN | 22.0949 | NaN | 26.0496
6243.1292 | 14.0688 | 13.6297 | 13.6522 | 14.0374 | 13.4563 | 13.6529 | 13.3658 | 13.1993 | NaN | NaN | NaN | 13.4881 | 93.7945 | NaN | NaN | NaN | -1.7244 | NaN | NaN | NaN | NaN | 580.826 | NaN | 20.6002 | NaN | 25.4745
6244.1292 | 13.9736 | 13.7112 | 13.6559 | 13.9847 | 13.405 | 13.721 | 13.3931 | 13.2004 | NaN | NaN | NaN | 13.5126 | 93.2303 | NaN | NaN | NaN | -13.7266 | NaN | NaN | NaN | NaN | 581.5727 | NaN | 22.4308 | NaN | 26.8653
6245.1292 | 14.0475 | 13.7141 | 13.6531 | 13.9499 | 13.3757 | 13.7497 | 13.3922 | 13.2038 | NaN | NaN | NaN | 13.4841 | 92.6506 | NaN | NaN | NaN | 11.1449 | NaN | NaN | NaN | NaN | 582.7869 | NaN | 22.2323 | NaN | 27.1727
6246.1292 | 13.9327 | 13.6348 | 13.6515 | 13.9857 | 13.4547 | 13.6558 | 13.3679 | 13.2024 | NaN | NaN | NaN | 13.481 | 92.7625 | NaN | NaN | NaN | 9.6583 | NaN | NaN | NaN | NaN | 581.3703 | NaN | 22.8055 | NaN | 25.3751
6247.1292 | 13.9718 | 13.6252 | 13.6539 | 14.0086 | 13.2672 | 13.7466 | 13.3751 | 13.2031 | NaN | NaN | NaN | 13.6183 | 92.1288 | NaN | NaN | NaN | 44.5703 | NaN | NaN | NaN | NaN | 581.9901 | NaN | 21.536 | NaN | 23.8194
6248.1292 | 14.1007 | 13.6376 | 13.6512 | 13.9852 | 13.2846 | 13.6388 | 13.3653 | 13.1995 | NaN | NaN | NaN | 13.4888 | 91.8419 | NaN | NaN | NaN | -17.2818 | NaN | NaN | NaN | NaN | 580.3253 | NaN | 21.0667 | NaN | 25.9871
6249.1292 | 14.1024 | 13.6478 | 13.6502 | 14.0161 | 13.3337 | 13.6664 | 13.3674 | 13.1954 | NaN | NaN | NaN | 13.5148 | 95.3611 | NaN | NaN | NaN | 13.6761 | NaN | NaN | NaN | NaN | 578.4603 | NaN | 21.832 | NaN | 24.6265
6250.1292 | 13.9393 | 13.6931 | 13.6471 | 13.9327 | 13.2352 | 13.7041 | 13.3874 | 13.203 | NaN | NaN | NaN | 13.6171 | 93.9172 | NaN | NaN | NaN | 15.7239 | NaN | NaN | NaN | NaN | 579.7833 | NaN | 22.5319 | NaN | 23.6727
6251.1292 | 13.9741 | 13.6902 | 13.6436 | 13.9454 | 13.3373 | 13.671 | 13.3831 | 13.1997 | NaN | NaN | NaN | 13.5551 | 93.1949 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 574.961 | NaN | 20.2726 | NaN | 27.3693
6252.1292 | 13.9695 | 13.7645 | 13.6477 | 13.9329 | 13.3305 | 13.6632 | 13.4112 | 13.2051 | NaN | NaN | NaN | 13.5061 | 96.8514 | NaN | NaN | NaN | -14.9327 | NaN | NaN | NaN | NaN | 575.286 | NaN | 18.8666 | NaN | 25.8114
6253.1292 | 13.9484 | 13.6866 | 13.6452 | 14.0264 | 13.4658 | 13.7249 | 13.3881 | 13.2085 | NaN | NaN | NaN | 13.4676 | 88.7804 | NaN | NaN | NaN | -12.0129 | NaN | NaN | NaN | NaN | 584.9426 | NaN | 23.6843 | NaN | 26.1459
6254.1292 | 13.9707 | 13.6718 | 13.6437 | 13.9803 | 13.3019 | 13.6819 | 13.3647 | 13.2058 | NaN | NaN | NaN | 13.53 | 92.0153 | NaN | NaN | NaN | -18.7104 | NaN | NaN | NaN | NaN | 581.9974 | NaN | 22.2043 | NaN | 26.0748
6255.1292 | 13.9457 | 13.658 | 13.6421 | 13.9479 | 13.336 | 13.7596 | 13.379 | 13.2037 | NaN | NaN | NaN | 13.4785 | 95.894 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 584.3938 | NaN | 22.4333 | NaN | 26.0576
6256.1292 | 13.924 | 13.7255 | 13.6505 | 14.0192 | 13.3967 | 13.6717 | 13.3979 | 13.2112 | NaN | NaN | NaN | 13.4831 | 92.4934 | NaN | NaN | NaN | -11.2258 | NaN | NaN | NaN | NaN | 584.4001 | NaN | 20.506 | NaN | 27.8643
6257.1292 | 13.959 | 13.8608 | 13.6456 | 14.0187 | 13.4889 | 13.788 | 13.4264 | 13.2084 | NaN | NaN | NaN | 13.5371 | 92.0456 | NaN | NaN | NaN | 41.5284 | NaN | NaN | NaN | NaN | 582.919 | NaN | 19.425 | NaN | 27.1212
6258.1292 | 13.9438 | 13.7076 | 13.6466 | 14.0063 | 13.3365 | 13.6855 | 13.3869 | 13.2123 | NaN | NaN | NaN | 13.5245 | 94.8751 | NaN | NaN | NaN | -15.2211 | NaN | NaN | NaN | NaN | 581.7898 | NaN | 22.2595 | NaN | 27.3577
6259.1292 | 13.9513 | 13.6476 | 13.642 | 13.9595 | 13.3466 | 13.6899 | 13.3822 | 13.2117 | NaN | NaN | NaN | 13.6067 | 94.4162 | NaN | NaN | NaN | -13.1756 | NaN | NaN | NaN | NaN | 577.9296 | NaN | 19.7698 | NaN | 26.6468
6260.1292 | 13.9929 | 13.6334 | 13.6585 | 13.9889 | 13.4109 | 13.6034 | 13.3473 | 13.2061 | NaN | NaN | NaN | 13.5233 | 93.0173 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 579.2891 | NaN | 22.4267 | NaN | 25.522
6261.1292 | 13.9519 | 13.6709 | 13.6542 | 14.0104 | 13.3721 | 13.6552 | 13.3676 | 13.2013 | NaN | NaN | NaN | 13.4821 | 96.2334 | NaN | NaN | NaN | -10.8495 | NaN | NaN | NaN | NaN | 576.7349 | NaN | 21.7066 | NaN | 27.4216
6262.1292 | 13.9515 | 13.72 | 13.6595 | 13.972 | 13.4181 | 13.6867 | 13.4032 | 13.1916 | NaN | NaN | NaN | 13.4838 | 93.7989 | NaN | NaN | NaN | -16.7173 | NaN | NaN | NaN | NaN | 579.5699 | NaN | 21.216 | NaN | 25.9472
6263.1292 | 13.9579 | 13.6762 | 13.6607 | 13.9635 | 13.4353 | 13.6643 | 13.3762 | 13.1966 | NaN | NaN | NaN | 13.5103 | 94.5573 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 577.5508 | NaN | 22.2563 | NaN | 27.9896
6264.1292 | 13.9326 | 13.6781 | 13.6607 | 14.1713 | 13.4499 | 13.6631 | 13.3872 | 13.194 | NaN | NaN | NaN | 13.4953 | 98.6417 | NaN | NaN | NaN | -18.7949 | NaN | NaN | NaN | NaN | 579.0957 | NaN | 22.3467 | NaN | 27.2156
6265.1292 | 13.9599 | 13.6519 | 13.6539 | 13.9788 | 13.3137 | 13.6188 | 13.3641 | 13.1988 | NaN | NaN | NaN | 13.4846 | 91.7729 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 580.9275 | NaN | 21.3711 | NaN | 27.098
6266.1292 | 13.9549 | 13.7571 | 13.6651 | 13.9879 | 13.3259 | 13.6887 | 13.3935 | 13.1931 | NaN | NaN | NaN | 13.4636 | 91.6802 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 579.8551 | NaN | 19.3252 | NaN | 25.1264
6267.1292 | 13.9983 | 13.6468 | 13.6621 | 14.0199 | 13.3956 | 13.6795 | 13.3766 | 13.1903 | NaN | NaN | NaN | 13.5076 | 94.794 | NaN | NaN | NaN | 7.6536 | NaN | NaN | NaN | NaN | 579.2692 | NaN | 21.6118 | NaN | 26.9076
6268.1292 | 13.9553 | 13.6388 | 13.6637 | 13.9905 | 13.4118 | 13.8067 | 13.3868 | 13.1936 | NaN | NaN | NaN | 13.4729 | 93.5448 | NaN | NaN | NaN | -10.3415 | NaN | NaN | NaN | NaN | 577.5742 | NaN | 22.2092 | NaN | 24.083
6269.1292 | 14.059 | 13.629 | 13.6632 | 13.9511 | 13.3433 | 13.6612 | 13.3753 | 13.1914 | NaN | NaN | NaN | 13.491 | 95.1315 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 580.2965 | NaN | 22.3579 | NaN | 28.8726
6270.1292 | 13.9639 | 13.6757 | 13.6574 | 13.9704 | 13.359 | 13.6664 | 13.381 | 13.1916 | NaN | NaN | NaN | 13.4988 | 90.1147 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -10.7107 | 581.045 | NaN | 19.2968 | NaN | 25.7669
6271.1292 | 13.9279 | 13.7515 | 13.6662 | 13.9892 | 13.3628 | 13.7301 | 13.376 | 13.183 | NaN | NaN | NaN | 13.4991 | 88.3624 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 578.3356 | NaN | 22.6219 | NaN | 25.5408
6272.1292 | 13.9553 | 13.7081 | 13.6634 | 13.9844 | 13.3172 | 13.666 | 13.3901 | 13.184 | NaN | NaN | NaN | 13.486 | 95.9779 | NaN | NaN | NaN | 6.2808 | NaN | NaN | NaN | NaN | 578.3707 | NaN | 19.0921 | NaN | 25.9241
6273.1292 | 13.9401 | 13.7075 | 13.6656 | 13.9523 | 13.2885 | 13.6703 | 13.3942 | 13.1831 | NaN | NaN | NaN | 13.5333 | 94.9572 | NaN | NaN | NaN | 56.5242 | NaN | NaN | NaN | NaN | 581.6694 | NaN | 20.5137 | NaN | 26.9444
6274.1292 | 13.9564 | 13.6932 | 13.6673 | 14.1066 | 13.4113 | 13.6797 | 13.3832 | 13.1843 | NaN | NaN | NaN | 13.4847 | 97.33 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 580.2466 | NaN | 21.5717 | NaN | 24.5099
6275.1292 | 13.956 | 13.7639 | 13.6645 | 13.9644 | 13.2211 | 13.7263 | 13.4106 | 13.1849 | NaN | NaN | NaN | 13.4805 | 92.9705 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 576.5305 | NaN | 21.6107 | NaN | 25.8063
6276.1292 | 13.9691 | 13.6533 | 13.6662 | 13.8968 | 13.2891 | 13.7938 | 13.3889 | 13.1764 | NaN | NaN | NaN | 13.4793 | 93.601 | NaN | NaN | NaN | 31.4242 | NaN | NaN | NaN | NaN | 577.4763 | NaN | 22.8149 | NaN | 26.846
6277.1292 | 13.9568 | 13.672 | 13.6747 | 13.9595 | 13.2768 | 13.6515 | 13.3751 | 13.1788 | NaN | NaN | NaN | 13.5202 | 91.7514 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 580.2052 | NaN | 22.2161 | NaN | 27.5822
6278.1292 | 13.9503 | 13.629 | 13.671 | 13.975 | 13.3268 | 13.6546 | 13.3915 | 13.1807 | NaN | NaN | NaN | 13.5459 | 91.1866 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 578.9974 | NaN | 22.4408 | NaN | 28.2219
6279.1292 | 14.0386 | 13.6303 | 13.6714 | 13.9951 | 13.3811 | 13.7029 | 13.3823 | 13.1767 | NaN | NaN | NaN | 13.4866 | 91.4634 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 579.1763 | NaN | 23.278 | NaN | 25.1027
6280.1292 | 13.9528 | 13.6255 | 13.6742 | 13.9386 | 13.3823 | 13.6952 | 13.3759 | 13.1755 | NaN | NaN | NaN | 13.5293 | 92.2594 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 574.0679 | NaN | 22.9035 | NaN | 26.935
6281.1292 | 13.9703 | 13.6869 | 13.6762 | 13.9499 | 13.2777 | 13.672 | 13.3862 | 13.1766 | NaN | NaN | NaN | 13.4626 | 93.156 | NaN | NaN | NaN | 35.9868 | NaN | NaN | NaN | NaN | 577.3112 | NaN | 22.053 | NaN | 25.7221
6282.1292 | 13.9315 | 13.6908 | 13.6782 | 13.9707 | 13.4368 | 13.704 | 13.3935 | 13.1752 | NaN | NaN | NaN | 13.4753 | 93.0106 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 580.0192 | NaN | 22.1313 | NaN | 24.1551
6283.1292 | 13.9549 | 13.5871 | 13.6811 | 14.0375 | 13.2518 | 13.7069 | 13.3592 | 13.1779 | NaN | NaN | NaN | 13.4584 | 98.0804 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 582.0854 | NaN | 21.9539 | NaN | 25.0606
6284.1292 | 14.0318 | 13.7112 | 13.6867 | 13.9043 | 13.3957 | 13.7082 | 13.3922 | 13.1782 | NaN | NaN | NaN | 13.5732 | 91.7252 | NaN | NaN | NaN | -9.1824 | NaN | NaN | NaN | NaN | 579.8541 | NaN | 21.0221 | NaN | 26.3242
6285.1292 | 13.9385 | 13.6479 | 13.6861 | 14.0477 | 13.4032 | 13.6964 | 13.3756 | 13.1751 | NaN | NaN | NaN | 13.504 | 90.1361 | NaN | NaN | NaN | 36.3523 | NaN | NaN | NaN | NaN | 581.8847 | NaN | 22.0027 | NaN | 26.6945
6286.1292 | 13.9714 | 13.6269 | 13.6849 | 13.9712 | 13.2379 | 13.6888 | 13.3811 | 13.1774 | NaN | NaN | NaN | 13.4577 | 92.8052 | NaN | NaN | NaN | -2.467 | NaN | NaN | NaN | NaN | 581.7203 | NaN | 21.4771 | NaN | 26.1441
6287.1292 | 13.9337 | 13.6085 | 13.6861 | 14.0155 | 13.4704 | 13.7045 | 13.3772 | 13.1783 | NaN | NaN | NaN | 13.5514 | 90.6892 | NaN | NaN | NaN | 1.9643 | NaN | NaN | NaN | NaN | 577.0501 | NaN | 21.86 | NaN | 26.3184
6288.1292 | 13.958 | 13.7182 | 13.6878 | 13.955 | 13.3686 | 13.6687 | 13.3878 | 13.1748 | NaN | NaN | NaN | 13.5002 | 93.0275 | NaN | NaN | NaN | -13.036 | NaN | NaN | NaN | NaN | 577.3348 | NaN | 22.5806 | NaN | 26.5595
6289.1292 | 13.9903 | 13.7546 | 13.6853 | 13.9706 | 13.4227 | 13.6727 | 13.4113 | 13.1778 | NaN | NaN | NaN | 13.444 | 94.5666 | NaN | NaN | NaN | -19.4382 | NaN | NaN | NaN | NaN | 579.2426 | NaN | 23.0054 | NaN | 24.0352
6290.1292 | 13.9198 | 13.5835 | 13.6894 | 13.9823 | 13.3776 | 13.6178 | 13.3574 | 13.1823 | NaN | NaN | NaN | 13.6246 | 92.268 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 581.7823 | NaN | 24.4928 | NaN | 27.9303
6291.1292 | 13.9121 | 13.8146 | 13.6862 | 13.9832 | 13.3151 | 13.6719 | 13.3922 | 13.1746 | NaN | NaN | NaN | 13.4924 | 91.5428 | NaN | NaN | NaN | -15.1661 | NaN | NaN | NaN | NaN | 581.836 | NaN | 20.8022 | NaN | 26.1905
6292.1292 | 13.9636 | 13.6342 | 13.676 | 13.9713 | 13.4401 | 13.6846 | 13.3757 | 13.1763 | NaN | NaN | NaN | 13.4585 | 91.6033 | NaN | NaN | NaN | 5.8267 | NaN | NaN | NaN | NaN | 581.3889 | NaN | 23.2042 | NaN | 25.511
6293.1292 | 13.9541 | 13.6402 | 13.6746 | 13.9375 | 13.3437 | 13.676 | 13.3696 | 13.1742 | NaN | NaN | NaN | 13.4683 | 95.0228 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 581.7267 | NaN | 19.6152 | NaN | 26.5462
6294.1292 | 14.0989 | 13.6048 | 13.6747 | 14.0296 | 13.3042 | 13.7064 | 13.3737 | 13.1683 | NaN | NaN | NaN | 13.4939 | 93.1225 | NaN | NaN | NaN | 2.4518 | NaN | NaN | NaN | NaN | 581.7467 | NaN | 22.3764 | NaN | 24.0225
6295.1292 | 13.9269 | 13.8718 | 13.6671 | 13.9558 | 13.2838 | 13.7485 | 13.3848 | 13.1649 | NaN | NaN | NaN | 13.5548 | 94.6271 | NaN | NaN | NaN | -7.8069 | NaN | NaN | NaN | NaN | 579.1801 | NaN | 22.369 | NaN | 26.5603
6296.1292 | 14.0557 | 13.6454 | 13.6684 | 13.9661 | 13.4256 | 13.6476 | 13.3498 | 13.1671 | NaN | NaN | NaN | 13.4874 | 92.1286 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 579.0762 | NaN | 20.5222 | NaN | 26.3394
6297.1292 | 13.9668 | 13.5858 | 13.6629 | 13.9349 | 13.2078 | 13.6233 | 13.3533 | 13.1756 | NaN | NaN | NaN | 13.496 | 94.8319 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 581.1667 | NaN | 21.7503 | NaN | 26.808
6298.1292 | 13.9765 | 13.5994 | 13.6612 | 13.9365 | 13.2782 | 13.65 | 13.3524 | 13.1716 | NaN | NaN | NaN | 13.5413 | 99.2822 | NaN | NaN | NaN | -17.4469 | NaN | NaN | NaN | NaN | 583.1279 | NaN | 20.8495 | NaN | 26.1579
6299.1292 | 13.9844 | 13.6554 | 13.6588 | 13.9544 | 13.4293 | 13.717 | 13.3598 | 13.1709 | NaN | NaN | NaN | 13.4817 | 93.8065 | NaN | NaN | NaN | -9.6652 | NaN | NaN | NaN | NaN | 582.0721 | NaN | 21.6879 | NaN | 25.9441
6300.1292 | 13.9249 | 13.6517 | 13.6518 | 13.9705 | 13.4309 | 13.6878 | 13.3594 | 13.1686 | NaN | NaN | NaN | 13.446 | 97.1982 | NaN | NaN | NaN | 49.5462 | NaN | NaN | NaN | NaN | 579.9852 | NaN | 23.2968 | NaN | 26.3876
6301.1292 | 13.9591 | 13.6859 | 13.6574 | 13.9899 | 13.3652 | 13.769 | 13.3724 | 13.172 | NaN | NaN | NaN | 13.5272 | 92.635 | NaN | NaN | NaN | 19.869 | NaN | NaN | NaN | NaN | 581.4704 | NaN | 22.1961 | NaN | 27.3002
6302.1292 | 14.0354 | 13.6078 | 13.6477 | 13.9685 | 13.4072 | 13.6479 | 13.3522 | 13.1626 | NaN | NaN | NaN | 13.477 | 89.5265 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 583.2948 | NaN | 21.7588 | NaN | 23.1469
6303.1292 | 13.9441 | 13.6385 | 13.6614 | 13.9568 | 13.4169 | 13.7385 | 13.3693 | 13.1646 | NaN | NaN | NaN | 13.5177 | 90.8207 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 582.7076 | NaN | 22.5198 | NaN | 24.9589
6304.1448 | 13.9668 | 13.5988 | 13.6577 | 13.9957 | 13.4373 | 13.647 | 13.3424 | 13.1695 | NaN | NaN | NaN | 13.5199 | 94.4543 | NaN | NaN | NaN | -5.7916 | NaN | NaN | NaN | NaN | 585.0341 | NaN | 20.3185 | NaN | 24.9647
6305.1292 | 13.961 | 13.6044 | 13.6593 | 13.927 | 13.2817 | 13.6772 | 13.3555 | 13.1735 | NaN | NaN | NaN | 13.6215 | 90.9058 | NaN | NaN | NaN | 6.597 | NaN | NaN | NaN | NaN | 585.0013 | NaN | 22.0557 | NaN | 28.252
6306.1292 | 13.9746 | 13.6647 | 13.6588 | 13.9916 | 13.4191 | 13.7023 | 13.3569 | 13.1738 | NaN | NaN | NaN | 13.4679 | 95.3532 | NaN | NaN | NaN | -12.1145 | NaN | NaN | NaN | NaN | 581.2305 | NaN | 20.3127 | NaN | 25.813
6307.1292 | 13.9684 | 13.6221 | 13.6562 | 14.0376 | 13.323 | 13.6767 | 13.3357 | 13.1756 | NaN | NaN | NaN | 13.4691 | 98.2023 | NaN | NaN | NaN | -18.7477 | NaN | NaN | NaN | NaN | 583.9176 | NaN | 21.6969 | NaN | 26.9987
6308.1292 | 14.1049 | 13.6107 | 13.6587 | 13.9729 | 13.3501 | 13.6664 | 13.3473 | 13.1762 | NaN | NaN | NaN | 13.5884 | 92.3047 | NaN | NaN | NaN | -12.3987 | NaN | NaN | NaN | NaN | 578.7003 | NaN | 21.5219 | NaN | 27.0562
6309.1292 | 13.9595 | 13.5896 | 13.6559 | 13.9774 | 13.3947 | 13.6158 | 13.3282 | 13.1717 | NaN | NaN | NaN | 13.4828 | 94.6225 | NaN | NaN | NaN | -7.3768 | NaN | NaN | NaN | NaN | 578.0146 | NaN | 19.4181 | NaN | 25.763
6310.1292 | 13.9607 | 13.6815 | 13.6511 | 13.9198 | 13.3801 | 13.7177 | 13.3492 | 13.1796 | NaN | NaN | NaN | 13.5643 | 94.5564 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 583.6171 | NaN | 22.7868 | NaN | 25.8909
6311.1292 | 13.9815 | 13.6244 | 13.6569 | 14.0387 | 13.3854 | 13.6705 | 13.3323 | 13.1775 | NaN | NaN | NaN | 13.496 | 92.8621 | NaN | NaN | NaN | -2.9944 | NaN | NaN | NaN | NaN | 585.1384 | NaN | 20.6376 | NaN | 27.7373
6312.1292 | 13.9892 | 13.6426 | 13.6553 | 13.9675 | 13.3674 | 13.7106 | 13.3541 | 13.1826 | NaN | NaN | NaN | 13.4483 | 91.2326 | NaN | NaN | NaN | 16.5779 | NaN | NaN | NaN | NaN | 586.9651 | NaN | 25.0446 | NaN | 26.8733
6313.1292 | 13.9399 | 13.6507 | 13.6615 | 13.9621 | 13.4287 | 13.7209 | 13.363 | 13.1831 | NaN | NaN | NaN | 13.5132 | 93.1681 | NaN | NaN | NaN | 51.0769 | NaN | NaN | NaN | NaN | 585.3932 | NaN | 22.289 | NaN | 25.321
6314.1292 | 13.9535 | 13.6046 | 13.6625 | 13.9395 | 13.3868 | 13.6795 | 13.3523 | 13.1748 | NaN | NaN | NaN | 13.6199 | 93.5898 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 584.9768 | NaN | 21.4639 | NaN | 27.4644
6315.1292 | 13.9706 | 13.6001 | 13.6665 | 13.9601 | 13.2951 | 13.6569 | 13.3397 | 13.1764 | NaN | NaN | NaN | 13.4996 | 91.3129 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 584.5644 | NaN | 22.651 | NaN | 26.1636
6316.1292 | 14.0148 | 13.6272 | 13.6689 | 13.9514 | 13.3505 | 13.684 | 13.3344 | 13.1879 | NaN | NaN | NaN | 13.446 | 92.94 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 584.0642 | NaN | 21.8767 | NaN | 26.8041
6317.1292 | 13.9646 | 13.6098 | 13.664 | 13.9958 | 13.4613 | 13.6507 | 13.3263 | 13.1794 | NaN | NaN | NaN | 13.4921 | 92.6246 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 577.0012 | NaN | 20.5266 | NaN | 27.9799
6318.1292 | 13.9795 | 13.5633 | 13.6587 | 13.91 | 13.2995 | 13.6099 | 13.3218 | 13.1739 | NaN | NaN | NaN | 13.514 | 92.1244 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 575.4048 | NaN | 21.188 | NaN | 27.4687
6319.1292 | 13.9692 | 13.7185 | 13.6646 | 13.9595 | 13.3696 | 13.6907 | 13.3642 | 13.1757 | NaN | NaN | NaN | 13.4854 | 91.8535 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 580.5248 | NaN | 20.9307 | NaN | 25.3473
6320.1292 | 13.9926 | 13.6264 | 13.6668 | 13.9283 | 13.2529 | 13.6768 | 13.3422 | 13.1712 | NaN | NaN | NaN | 13.4589 | 92.003 | NaN | NaN | NaN | -18.5429 | NaN | NaN | NaN | NaN | 582.0395 | NaN | 21.1248 | NaN | 26.0193
6321.1292 | 13.9648 | 13.611 | 13.6652 | 13.9584 | 13.4379 | 13.6755 | 13.339 | 13.1715 | NaN | NaN | NaN | 13.5274 | 90.5254 | NaN | NaN | NaN | 42.3431 | NaN | NaN | NaN | NaN | 583.0055 | NaN | 20.3783 | NaN | 26.4115
6322.1292 | 13.9161 | 13.6568 | 13.6659 | 13.9465 | 13.3637 | 13.6857 | 13.3473 | 13.167 | NaN | NaN | NaN | 13.4919 | 94.1756 | NaN | NaN | NaN | -7.944 | NaN | NaN | NaN | NaN | 580.5735 | NaN | 22.0658 | NaN | 27.1429
6323.1292 | 13.9402 | 13.6877 | 13.6637 | 13.9197 | 13.3794 | 13.7009 | 13.3594 | 13.1657 | NaN | NaN | NaN | 13.6394 | 94.2126 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 578.419 | NaN | 22.7288 | NaN | 26.8263
6324.1292 | 14.0461 | 13.6184 | 13.6588 | 13.9136 | 13.2819 | 13.6424 | 13.3345 | 13.1713 | NaN | NaN | NaN | 13.5513 | 91.7214 | NaN | NaN | NaN | 3.7074 | NaN | NaN | NaN | NaN | 583.7294 | NaN | 21.3533 | NaN | 24.6945
6325.1292 | 13.9585 | 13.629 | 13.6551 | 13.9587 | 13.2856 | 13.6491 | 13.3307 | 13.1657 | NaN | NaN | NaN | 13.5034 | 94.2583 | NaN | NaN | NaN | 7.0948 | NaN | NaN | NaN | NaN | 577.6107 | NaN | 20.583 | NaN | 25.0577
6326.1292 | 14.2528 | 13.5983 | 13.6548 | 13.9075 | 13.2687 | 13.6901 | 13.3403 | 13.158 | NaN | NaN | NaN | 13.4636 | 92.7929 | NaN | NaN | NaN | 56.3805 | NaN | NaN | NaN | NaN | 579.4772 | NaN | 20.1146 | NaN | 24.6417
6327.1292 | 13.9614 | 13.6313 | 13.6542 | 13.9565 | 13.3437 | 13.6559 | 13.3306 | 13.1632 | NaN | NaN | NaN | 13.5153 | 92.5984 | NaN | NaN | NaN | -10.0338 | NaN | NaN | NaN | NaN | 576.3032 | NaN | 20.5465 | NaN | 24.8055
6328.1448 | 13.9246 | 13.6917 | 13.6548 | 13.9632 | 13.1875 | 13.6987 | 13.3572 | 13.1625 | NaN | NaN | NaN | 13.4741 | 91.3978 | NaN | NaN | NaN | -16.2844 | NaN | NaN | NaN | NaN | 576.3917 | NaN | 22.7451 | NaN | 24.6854
6329.1292 | 13.9665 | 13.6344 | 13.6545 | 13.9296 | 13.2931 | 13.6209 | 13.3142 | 13.1617 | NaN | NaN | NaN | 13.7544 | 92.4753 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 579.5595 | NaN | 18.7586 | NaN | 28.3746
6330.1292 | 13.9454 | 13.6915 | 13.6522 | 13.9392 | 13.3634 | 13.6484 | 13.3425 | 13.155 | NaN | NaN | NaN | 13.4677 | 91.2375 | NaN | NaN | NaN | 7.6753 | NaN | NaN | NaN | NaN | 579.5623 | NaN | 21.62 | NaN | 27.8524
6331.1292 | 13.986 | 13.7455 | 13.6511 | 13.915 | 13.3315 | 13.68 | 13.3502 | 13.1625 | NaN | NaN | NaN | 13.4482 | 94.4657 | NaN | NaN | NaN | 53.6705 | NaN | NaN | NaN | NaN | 580.251 | NaN | 19.0035 | NaN | 27.7875
6332.1292 | 13.9529 | 13.7083 | 13.6536 | 13.8996 | 13.3504 | 13.7788 | 13.3519 | 13.1589 | NaN | NaN | NaN | 13.4752 | 92.0223 | NaN | NaN | NaN | 20.7835 | NaN | NaN | NaN | NaN | 584.7831 | NaN | 21.5744 | NaN | 26.8969
6333.1292 | 14.0364 | 13.6342 | 13.655 | 13.9201 | 13.3333 | 13.6644 | 13.346 | 13.164 | NaN | NaN | NaN | 13.4555 | 92.5854 | NaN | NaN | NaN | 33.9569 | NaN | NaN | NaN | NaN | 582.918 | NaN | 22.3475 | NaN | 22.2861
6334.1292 | 13.933 | 13.6638 | 13.6601 | 13.9335 | 13.4151 | 13.7016 | 13.3465 | 13.1664 | NaN | NaN | NaN | 13.4844 | 95.6589 | NaN | NaN | NaN | -4.6434 | NaN | NaN | NaN | NaN | 586.3337 | NaN | 20.6928 | NaN | 25.113
6335.1292 | 13.9823 | 13.7003 | 13.6591 | 13.9156 | 13.3767 | 13.6627 | 13.3503 | 13.1633 | NaN | NaN | NaN | 13.4589 | 92.7023 | NaN | NaN | NaN | 31.0013 | NaN | NaN | NaN | NaN | 585.4537 | NaN | 21.8901 | NaN | 27.1572
6336.1292 | 13.9318 | 13.6169 | 13.667 | 13.8916 | 13.414 | 13.6282 | 13.3155 | 13.1698 | NaN | NaN | NaN | 13.4522 | 98.4958 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 585.2848 | NaN | 22.3601 | NaN | 27.0521
6337.1292 | 13.9551 | 13.6462 | 13.6701 | 13.964 | 13.3076 | 13.7171 | 13.3551 | 13.1707 | NaN | NaN | NaN | 13.461 | 92.7136 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 585.0961 | NaN | 22.8789 | NaN | 25.5356
6338.1292 | 13.9414 | 13.6498 | 13.6656 | 13.9057 | 13.3462 | 13.7928 | 13.3525 | 13.1686 | NaN | NaN | NaN | 13.4716 | 91.7671 | NaN | NaN | NaN | -14.3484 | NaN | NaN | NaN | NaN | 582.3818 | NaN | 20.388 | NaN | 25.1444
6339.1292 | 14.0115 | 13.6594 | 13.663 | 13.9226 | 13.321 | 13.6934 | 13.3645 | 13.1672 | NaN | NaN | NaN | 13.4692 | 90.5134 | NaN | NaN | NaN | 28.7153 | NaN | NaN | NaN | NaN | 583.0891 | NaN | 22.3699 | NaN | 24.3476
6340.1292 | 13.9508 | 13.7067 | 13.6717 | 13.922 | 13.3662 | 13.6718 | 13.3646 | 13.1721 | NaN | NaN | NaN | 13.461 | 97.1855 | NaN | NaN | NaN | -19.5216 | NaN | NaN | NaN | NaN | 583.7113 | NaN | 19.8533 | NaN | 25.6602
6341.1292 | 13.9816 | 13.6956 | 13.6689 | 13.9295 | 13.3467 | 13.6659 | 13.3675 | 13.1657 | NaN | NaN | NaN | 13.4677 | 99.5948 | NaN | NaN | NaN | -16.2801 | NaN | NaN | NaN | NaN | 582.4651 | NaN | 21.6686 | NaN | 27.0031
6342.1292 | 14.0233 | 13.685 | 13.6751 | 13.8772 | 13.3323 | 13.6715 | 13.3512 | 13.1735 | NaN | NaN | NaN | 13.5053 | 101.8756 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 583.6631 | NaN | 18.9193 | NaN | 27.2626
6343.1292 | 13.9255 | 13.6323 | 13.681 | 13.9513 | 13.3275 | 13.6484 | 13.3512 | 13.1718 | NaN | NaN | NaN | 13.4922 | 90.6409 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 575.0734 | NaN | 22.2025 | NaN | 27.0089
6344.1292 | 13.9432 | 13.6548 | 13.676 | 13.9723 | 13.3166 | 13.6584 | 13.3725 | 13.1721 | NaN | NaN | NaN | 13.5013 | 93.0935 | NaN | NaN | NaN | -1.0293 | NaN | NaN | NaN | NaN | 582.0764 | NaN | 21.6956 | NaN | 27.2211
6345.1292 | 13.9779 | 13.6249 | 13.6778 | 13.9467 | 13.4055 | 13.6431 | 13.3449 | 13.1827 | NaN | NaN | NaN | 13.4948 | 91.5491 | NaN | NaN | NaN | 10.9751 | NaN | NaN | NaN | NaN | 582.4659 | NaN | 19.6527 | NaN | 25.6186
6346.1292 | 13.9675 | 13.6731 | 13.6827 | 13.9294 | 13.4344 | 13.6582 | 13.357 | 13.1721 | NaN | NaN | NaN | 13.4815 | 91.1361 | NaN | NaN | NaN | 13.5816 | NaN | NaN | NaN | NaN | 583.6204 | NaN | 20.3438 | NaN | 27.3616
6347.1292 | 14.0499 | 13.6468 | 13.685 | 13.988 | 13.4577 | 13.655 | 13.3526 | 13.1821 | NaN | NaN | NaN | 13.4693 | 91.338 | NaN | NaN | NaN | -7.6018 | NaN | NaN | NaN | NaN | 582.7307 | NaN | 21.4348 | NaN | 25.7815
6348.1292 | 13.9689 | 13.6599 | 13.6874 | 13.8931 | 13.3452 | 13.6515 | 13.3509 | 13.1816 | NaN | NaN | NaN | 13.4733 | 91.767 | NaN | NaN | NaN | 12.6786 | NaN | NaN | NaN | NaN | 580.279 | NaN | 20.734 | NaN | 26.7273
6349.1292 | 13.9415 | 13.6387 | 13.6831 | 13.9282 | 13.3821 | 13.6841 | 13.35 | 13.1875 | NaN | NaN | NaN | 13.4972 | 91.9821 | NaN | NaN | NaN | 0.7101 | NaN | NaN | NaN | NaN | 584.7266 | NaN | 20.0121 | NaN | 27.1015
6350.1292 | 13.9522 | 13.7102 | 13.686 | 14.0042 | 13.3733 | 13.7898 | 13.3724 | 13.1844 | NaN | NaN | NaN | 13.4848 | 93.0488 | NaN | NaN | NaN | 23.2585 | NaN | NaN | NaN | NaN | 581.8387 | NaN | 22.4569 | NaN | 24.5322
6351.1292 | 13.9715 | 13.6199 | 13.6888 | 13.9558 | 13.2893 | 13.614 | 13.3252 | 13.1847 | NaN | NaN | NaN | 13.4721 | 92.7816 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 577.8189 | NaN | 20.0436 | NaN | 23.3077
6352.1292 | 13.9438 | 13.6244 | 13.6895 | 13.9601 | 13.2917 | 13.6564 | 13.3445 | 13.1806 | NaN | NaN | NaN | 13.5167 | 92.3662 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 578.6538 | NaN | 21.8955 | NaN | 25.4028
6353.1292 | 13.9609 | 13.6496 | 13.689 | 13.9772 | 13.2721 | 13.727 | 13.3561 | 13.187 | NaN | NaN | NaN | 13.4699 | 97.5798 | NaN | NaN | NaN | 9.0048 | NaN | NaN | NaN | NaN | 579.8957 | NaN | 22.6069 | NaN | 25.4649
6354.1292 | 14.0433 | 13.905 | 13.6869 | 13.9606 | 13.2564 | 13.7418 | 13.3927 | 13.1828 | NaN | NaN | NaN | 13.5818 | 93.589 | NaN | NaN | NaN | -11.1591 | NaN | NaN | NaN | NaN | 576.4967 | NaN | 22.1594 | NaN | 25.3764
6355.1292 | 13.9802 | 13.7565 | 13.6906 | 13.9633 | 13.351 | 13.7128 | 13.3815 | 13.1836 | NaN | NaN | NaN | 13.5156 | 93.6331 | NaN | NaN | NaN | -4.549 | NaN | NaN | NaN | NaN | 563.6048 | NaN | 19.898 | NaN | 27.3771
6356.1292 | 13.9799 | 13.6311 | 13.6903 | 13.9182 | 13.2811 | 13.6537 | 13.3381 | 13.1814 | NaN | NaN | NaN | 13.4505 | 91.9883 | NaN | NaN | NaN | -15.8882 | NaN | NaN | NaN | NaN | 547.2572 | NaN | 20.7385 | NaN | 26.4427
6357.1292 | 13.9713 | 13.6611 | 13.6981 | 13.9186 | 13.3177 | 13.6946 | 13.3531 | 13.189 | NaN | NaN | NaN | 13.5081 | 93.6454 | NaN | NaN | NaN | -14.6971 | NaN | NaN | NaN | NaN | 542.4385 | NaN | 17.6041 | NaN | 24.2304
6358.1292 | 13.9636 | 13.6525 | 13.6943 | 13.9634 | 13.2975 | 13.7313 | 13.3607 | 13.1801 | NaN | NaN | NaN | 13.4693 | 95.9496 | NaN | NaN | NaN | -1.6493 | NaN | NaN | NaN | NaN | 539.7886 | NaN | 21.9978 | NaN | 26.7103
6359.1292 | 13.9463 | 13.672 | 13.6925 | 13.9235 | 13.2367 | 13.7047 | 13.373 | 13.1791 | NaN | NaN | NaN | 13.4739 | 91.9385 | NaN | NaN | NaN | -19.702 | NaN | NaN | NaN | NaN | 539.2951 | NaN | 19.8646 | NaN | 24.261
6360.1292 | 13.9805 | 13.7047 | 13.701 | 13.9477 | 13.4 | 13.6858 | 13.3643 | 13.1844 | NaN | NaN | NaN | 13.4473 | 94.4782 | NaN | NaN | NaN | -10.4232 | NaN | NaN | NaN | NaN | 532.9058 | NaN | 20.9293 | NaN | 26.2235
6361.1292 | 13.9593 | 13.6534 | 13.6997 | 13.8737 | 13.3398 | 13.7334 | 13.3601 | 13.1727 | NaN | NaN | NaN | 13.4749 | 95.421 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 529.0183 | NaN | 21.3693 | NaN | 24.521
6362.1292 | 13.9513 | 13.6023 | 13.7003 | 13.9294 | 13.3783 | 13.6808 | 13.3576 | 13.1785 | NaN | NaN | NaN | 13.5051 | 91.9913 | NaN | NaN | NaN | -19.7102 | NaN | NaN | NaN | NaN | 530.7241 | NaN | 21.4718 | NaN | 26.4068
6363.1292 | 13.983 | 13.665 | 13.702 | 14.1949 | 13.469 | 13.6832 | 13.3748 | 13.1752 | NaN | NaN | NaN | 13.5022 | 91.7274 | NaN | NaN | NaN | 16.9461 | NaN | NaN | NaN | NaN | 532.9422 | NaN | 22.7675 | NaN | 23.9371
6364.1292 | 13.9487 | 13.6276 | 13.6968 | 13.953 | 13.2782 | 13.6554 | 13.3675 | 13.1793 | NaN | NaN | NaN | 13.5824 | 92.8498 | NaN | NaN | NaN | -4.1228 | NaN | NaN | NaN | NaN | 543.0964 | NaN | 21.8477 | NaN | 26.7206
6365.1292 | 13.9536 | 13.7412 | 13.6964 | 14.027 | 13.3411 | 13.6745 | 13.3838 | 13.1842 | NaN | NaN | NaN | 13.5145 | 99.8524 | NaN | NaN | NaN | -17.0518 | NaN | NaN | NaN | NaN | 548.3316 | NaN | 20.0127 | NaN | 27.6657
6366.1292 | 13.9555 | 13.7347 | 13.6981 | 13.9126 | 13.3835 | 13.6571 | 13.3793 | 13.1798 | NaN | NaN | NaN | 13.5362 | 91.5606 | NaN | NaN | NaN | -2.3633 | NaN | NaN | NaN | NaN | 556.5528 | NaN | 21.535 | NaN | 26.9018
6367.1292 | 13.9327 | 13.6499 | 13.6972 | 13.9458 | 13.365 | 13.7178 | 13.3884 | 13.1816 | NaN | NaN | NaN | 13.4927 | 91.7353 | NaN | NaN | NaN | -19.2726 | NaN | NaN | NaN | NaN | 559.2226 | NaN | 21.9022 | NaN | 26.8099
6368.1292 | 13.9598 | 13.7109 | 13.6972 | 13.931 | 13.3697 | 13.6908 | 13.3886 | 13.1842 | NaN | NaN | NaN | 13.512 | 96.3359 | NaN | NaN | NaN | -17.8444 | NaN | NaN | NaN | NaN | 567.734 | NaN | 22.0287 | NaN | 27.6511
6369.1448 | 13.9276 | 13.6358 | 13.7011 | 13.9207 | 13.3167 | 13.6826 | 13.3857 | 13.1872 | NaN | NaN | NaN | 13.4706 | 92.8847 | NaN | NaN | NaN | -16.1064 | NaN | NaN | NaN | NaN | 575.7857 | NaN | 21.4459 | NaN | 26.4511
6370.1292 | 13.9397 | 13.6448 | 13.7026 | 13.9007 | 13.2468 | 13.7026 | 13.384 | 13.1812 | NaN | NaN | NaN | 13.5088 | 91.4766 | NaN | NaN | NaN | -1.5812 | NaN | NaN | NaN | NaN | 581.3339 | NaN | 20.5985 | NaN | 26.8317
6371.1292 | 13.8903 | 13.7883 | 13.7047 | 13.9047 | 13.357 | 13.7858 | 13.4216 | 13.1872 | NaN | NaN | NaN | 13.5321 | 92.9173 | NaN | NaN | NaN | -18.9375 | NaN | NaN | NaN | NaN | 580.92 | NaN | 21.6933 | NaN | 24.2473
6372.1292 | 13.9524 | 13.5972 | 13.7021 | 13.9426 | 13.4842 | 13.655 | 13.3735 | 13.1837 | NaN | NaN | NaN | 13.4747 | 92.0687 | NaN | NaN | NaN | -10.5169 | NaN | NaN | NaN | NaN | 580.9883 | NaN | 21.3762 | NaN | 26.6023
6373.1292 | 13.9736 | 13.7028 | 13.704 | 13.9607 | 13.3625 | 13.6638 | 13.41 | 13.192 | NaN | NaN | NaN | 13.4747 | 90.0081 | NaN | NaN | NaN | -19.2695 | NaN | NaN | NaN | NaN | 578.1783 | NaN | 21.777 | NaN | 26.3725
6374.1292 | 13.9597 | 13.6536 | 13.7023 | 13.8863 | 13.3534 | 13.6551 | 13.3916 | 13.191 | NaN | NaN | NaN | 13.4675 | 93.1122 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 581.26 | NaN | 22.8831 | NaN | 26.4496
6375.1292 | 13.9215 | 13.6189 | 13.7029 | 13.8626 | 13.2276 | 13.6992 | 13.3953 | 13.1918 | NaN | NaN | NaN | 13.5044 | 93.0164 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 581.214 | NaN | 19.8566 | NaN | 26.5936
6376.1292 | 13.9203 | 13.6821 | 13.7005 | 13.8727 | 13.3743 | 13.7817 | 13.4184 | 13.1921 | NaN | NaN | NaN | 13.5046 | 92.7932 | NaN | NaN | NaN | 39.4677 | NaN | NaN | NaN | NaN | 582.4767 | NaN | 21.0461 | NaN | 24.1397
6377.1292 | 13.9642 | 13.612 | 13.6896 | 13.9427 | 13.2904 | 13.6372 | 13.3784 | 13.1966 | NaN | NaN | NaN | 13.4803 | 93.2836 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 578.0241 | NaN | 21.0404 | NaN | 24.255
6378.1292 | 13.9643 | 13.6008 | 13.685 | 13.9112 | 13.3537 | 13.6228 | 13.375 | 13.2014 | NaN | NaN | NaN | 13.4895 | 92.4569 | NaN | NaN | NaN | 13.9161 | NaN | NaN | NaN | NaN | 577.2449 | NaN | 20.7081 | NaN | 26.9673
6379.1292 | 13.8983 | 13.6211 | 13.6769 | 13.8917 | 13.3421 | 13.6541 | 13.3865 | 13.2009 | NaN | NaN | NaN | 13.4848 | 93.4305 | NaN | NaN | NaN | -4.8414 | NaN | NaN | NaN | NaN | 579.3842 | NaN | 21.7664 | NaN | 27.1081
6380.1292 | 13.9502 | 13.6431 | 13.6796 | 13.9068 | 13.4261 | 13.6776 | 13.4016 | 13.206 | NaN | NaN | NaN | 13.4999 | 91.6183 | NaN | NaN | NaN | 2.3068 | NaN | NaN | NaN | NaN | 580.4263 | NaN | 23.024 | NaN | 25.1392
6381.1292 | 13.9171 | 13.5924 | 13.6749 | 13.9174 | 13.3136 | 13.6228 | 13.3776 | 13.207 | NaN | NaN | NaN | 13.526 | 93.0902 | NaN | NaN | NaN | 25.0435 | NaN | NaN | NaN | NaN | 579.3508 | NaN | 20.4758 | NaN | 24.5012
6382.1292 | 13.9872 | 13.5934 | 13.6752 | 13.9057 | 13.3196 | 13.6364 | 13.3876 | 13.209 | NaN | NaN | NaN | 13.4874 | 91.3074 | NaN | NaN | NaN | 27.2147 | NaN | NaN | NaN | NaN | 579.496 | NaN | 23.1372 | NaN | 26.9548
6383.1292 | 13.9239 | 13.5916 | 13.671 | 13.902 | 13.2356 | 13.6272 | 13.382 | 13.2053 | NaN | NaN | NaN | 13.5486 | 91.7365 | NaN | NaN | NaN | -1.7982 | NaN | NaN | NaN | NaN | 578.2394 | NaN | 20.6928 | NaN | 27.7761
6384.1292 | 13.9976 | 13.6698 | 13.6668 | 14.0281 | 13.398 | 13.6819 | 13.4193 | 13.2094 | NaN | NaN | NaN | 13.5083 | 94.2907 | NaN | NaN | NaN | -3.1231 | NaN | NaN | NaN | NaN | 576.614 | NaN | 20.4203 | NaN | 23.248
6385.1292 | 13.9561 | 13.6526 | 13.6696 | 13.9208 | 13.3753 | 13.6735 | 13.4049 | 13.211 | NaN | NaN | NaN | 13.5218 | 95.2378 | NaN | NaN | NaN | -10.4971 | NaN | NaN | NaN | NaN | 577.9289 | NaN | 24.7332 | NaN | 25.8137
6386.1292 | 13.9404 | 13.6195 | 13.6687 | 13.8654 | 13.3269 | 13.6287 | 13.3832 | 13.2043 | NaN | NaN | NaN | 13.5555 | 93.1868 | NaN | NaN | NaN | -17.5976 | NaN | NaN | NaN | NaN | 576.1482 | NaN | 21.8698 | NaN | 26.4253
6387.1292 | 13.9518 | 13.6073 | 13.6631 | 13.8965 | 13.3495 | 13.6417 | 13.3891 | 13.2164 | NaN | NaN | NaN | 13.6322 | 92.8091 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 572.6078 | NaN | 20.1941 | NaN | 25.4256
6388.1292 | 13.9528 | 13.6283 | 13.6651 | 13.8906 | 13.3272 | 13.6633 | 13.3987 | 13.2117 | NaN | NaN | NaN | 13.5147 | 93.0879 | NaN | NaN | NaN | 14.2542 | NaN | NaN | NaN | NaN | 572.2621 | NaN | 21.4786 | NaN | 26.0615
6389.1292 | 14.051 | 13.6245 | 13.6679 | 13.9006 | 13.2663 | 13.6542 | 13.388 | 13.2186 | NaN | NaN | NaN | 13.4889 | 91.9631 | NaN | NaN | NaN | -19.9328 | NaN | NaN | NaN | NaN | 577.0957 | NaN | 19.0129 | NaN | 26.8097
6390.1292 | 13.9322 | 13.6368 | 13.6686 | 13.9403 | 13.3607 | 13.6746 | 13.3867 | 13.2162 | NaN | NaN | NaN | 13.6107 | 96.485 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 581.2346 | NaN | 20.8071 | NaN | 24.4502
6391.1292 | 13.9759 | 13.6094 | 13.6689 | 13.8825 | 13.3624 | 13.6515 | 13.392 | 13.2143 | NaN | NaN | NaN | 13.5614 | 92.4775 | NaN | NaN | NaN | 43.9412 | NaN | NaN | NaN | NaN | 583.2214 | NaN | 20.9036 | NaN | 24.7184
6392.1292 | 13.9448 | 13.6642 | 13.6712 | 13.8912 | 13.3466 | 13.7323 | 13.3943 | 13.2073 | NaN | NaN | NaN | 13.4874 | 94.093 | NaN | NaN | NaN | -14.4905 | NaN | NaN | NaN | NaN | 582.7762 | NaN | 19.8348 | NaN | 25.9101
6393.1292 | 13.9955 | 13.6322 | 13.6695 | 13.9253 | 13.4198 | 13.635 | 13.3735 | 13.2106 | NaN | NaN | NaN | 13.4745 | 93.1197 | NaN | NaN | NaN | 6.1319 | NaN | NaN | NaN | NaN | 584.6672 | NaN | 22.7469 | NaN | 25.5881
6394.1292 | 13.9948 | 13.6195 | 13.6651 | 13.857 | 13.3549 | 13.6619 | 13.3809 | 13.2134 | NaN | NaN | NaN | 13.4611 | 93.0642 | NaN | NaN | NaN | 12.9788 | NaN | NaN | NaN | NaN | 585.9237 | NaN | 21.0407 | NaN | 24.96
6395.1292 | 14.1616 | 13.6274 | 13.6613 | 13.9333 | 13.3737 | 13.669 | 13.3775 | 13.2103 | NaN | NaN | NaN | 13.4639 | 92.5192 | NaN | NaN | NaN | -19.204 | NaN | NaN | NaN | NaN | 585.2714 | NaN | 21.6682 | NaN | 25.7014
6396.1292 | 13.9352 | 13.8248 | 13.6611 | 13.9007 | 13.3358 | 13.7938 | 13.4232 | 13.2199 | NaN | NaN | NaN | 13.4929 | 93.659 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 587.4493 | NaN | 19.6745 | NaN | 25.65
6397.1292 | 13.9441 | 13.6382 | 13.6588 | 13.9179 | 13.2791 | 13.6574 | 13.3848 | 13.2166 | NaN | NaN | NaN | 13.5673 | 101.799 | NaN | NaN | NaN | 15.3655 | NaN | NaN | NaN | NaN | 586.7257 | NaN | 18.0746 | NaN | 26.5464
6398.1292 | 14.0152 | 13.6156 | 13.6634 | 13.8875 | 13.407 | 13.6153 | 13.3648 | 13.2186 | NaN | NaN | NaN | 13.4541 | 91.6348 | NaN | NaN | NaN | 27.0655 | NaN | NaN | NaN | NaN | 588.6321 | NaN | 20.5969 | NaN | 26.0983
6399.1292 | 14.0528 | 13.6676 | 13.6528 | 13.8862 | 13.3125 | 13.6827 | 13.386 | 13.2197 | NaN | NaN | NaN | 13.4767 | 95.0307 | NaN | NaN | NaN | -7.611 | NaN | NaN | NaN | NaN | 591.0435 | NaN | 22.6776 | NaN | 24.8441
6400.1292 | 13.9421 | 13.8152 | 13.6568 | 13.8689 | 13.393 | 13.8002 | 13.4212 | 13.2213 | NaN | NaN | NaN | 13.4591 | 92.3485 | NaN | NaN | NaN | 13.5122 | NaN | NaN | NaN | NaN | 589.411 | NaN | 21.0047 | NaN | 27.6199
6401.1292 | 13.9669 | 13.6322 | 13.6497 | 13.9076 | 13.3325 | 13.6369 | 13.3792 | 13.2187 | NaN | NaN | NaN | 13.5472 | 93.4122 | NaN | NaN | NaN | -10.627 | NaN | NaN | NaN | NaN | 589.5092 | NaN | 24.4109 | NaN | 24.8164
6402.1292 | 13.9597 | 13.6646 | 13.6551 | 13.9106 | 13.2351 | 13.6406 | 13.3873 | 13.2227 | NaN | NaN | NaN | 13.4651 | 93.5441 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 590.2952 | NaN | 22.2102 | NaN | 26.8526
6403.1292 | 14.157 | 13.6828 | 13.6588 | 13.8628 | 13.3382 | 13.7361 | 13.4057 | 13.2226 | NaN | NaN | NaN | 13.5289 | 94.0776 | NaN | NaN | NaN | -17.2144 | NaN | NaN | NaN | NaN | 590.0696 | NaN | 21.5097 | NaN | 25.6316
6404.1292 | 13.9352 | 13.6524 | 13.6628 | 13.8749 | 13.4116 | 13.6466 | 13.3783 | 13.2239 | NaN | NaN | NaN | 13.5262 | 94.7755 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 589.5083 | NaN | 21.4132 | NaN | 26.0252
6405.1292 | 14.1732 | 13.7076 | 13.6631 | 13.9088 | 13.3282 | 13.6724 | 13.3941 | 13.2159 | NaN | NaN | NaN | 13.4852 | 91.928 | NaN | NaN | NaN | -9.9936 | NaN | NaN | NaN | NaN | 587.7854 | NaN | 20.5293 | NaN | 26.2213
6406.1292 | 13.9498 | 13.6556 | 13.6655 | 13.9632 | 13.3795 | 13.6779 | 13.3953 | 13.2216 | NaN | NaN | NaN | 13.5377 | 94.4409 | NaN | NaN | NaN | 1.1847 | NaN | NaN | NaN | NaN | 588.9768 | NaN | 20.3039 | NaN | 25.7093
6407.1292 | 13.9157 | 13.6108 | 13.659 | 13.9241 | 13.2879 | 13.6085 | 13.3631 | 13.2168 | NaN | NaN | NaN | 13.4549 | 92.2816 | NaN | NaN | NaN | -8.306 | NaN | NaN | NaN | NaN | 587.8582 | NaN | 21.8696 | NaN | 26.6818
6408.1292 | 13.967 | 13.6523 | 13.6691 | 13.8939 | 13.3968 | 13.6537 | 13.3849 | 13.2181 | NaN | NaN | NaN | 13.4775 | 92.804 | NaN | NaN | NaN | -9.5575 | NaN | NaN | NaN | NaN | 587.5439 | NaN | 19.6547 | NaN | 25.2213
6409.1292 | 13.9662 | 13.631 | 13.6594 | 13.8716 | 13.3904 | 13.6612 | 13.3849 | 13.2153 | NaN | NaN | NaN | 13.4444 | 94.6974 | NaN | NaN | NaN | 17.4404 | NaN | NaN | NaN | NaN | 590.5837 | NaN | 22.152 | NaN | 24.5647
6410.1292 | 13.9285 | 13.6817 | 13.6637 | 13.9264 | 13.4131 | 13.6762 | 13.3864 | 13.2137 | NaN | NaN | NaN | 13.5121 | 94.3043 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 588.6291 | NaN | 20.1982 | NaN | 26.2925
6411.1292 | 13.9812 | 13.6725 | 13.6597 | 13.8366 | 13.2283 | 13.7642 | 13.39 | 13.2199 | NaN | NaN | NaN | 13.4494 | 92.9117 | NaN | NaN | NaN | -18.6812 | NaN | NaN | NaN | NaN | 590.6743 | NaN | 20.1712 | NaN | 25.3532
6412.1292 | 13.9506 | 13.6197 | 13.6632 | 13.8928 | 13.3889 | 13.6409 | 13.3692 | 13.2158 | NaN | NaN | NaN | 13.4983 | 94.7545 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 593.153 | NaN | 19.4387 | NaN | 25.4407
6413.1292 | 13.9714 | 13.6195 | 13.6661 | 13.8966 | 13.3458 | 13.6316 | 13.3635 | 13.2127 | NaN | NaN | NaN | 13.4978 | 90.6247 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 584.4902 | NaN | 21.4959 | NaN | 26.3623
6414.1292 | 13.9786 | 13.6048 | 13.6659 | 13.9186 | 13.3318 | 13.62 | 13.3602 | 13.2113 | NaN | NaN | NaN | 13.4762 | 92.4089 | NaN | NaN | NaN | 53.2111 | NaN | NaN | NaN | NaN | 591.3718 | NaN | 22.8986 | NaN | 26.9357
6415.1292 | 13.9633 | 13.6405 | 13.6713 | 13.862 | 13.2919 | 13.6375 | 13.3711 | 13.2089 | NaN | NaN | NaN | 13.4622 | 93.0414 | NaN | NaN | NaN | 27.1408 | NaN | NaN | NaN | NaN | 590.2647 | NaN | 18.5737 | NaN | 24.8789
6416.1292 | 13.954 | 13.7111 | 13.6725 | 13.9498 | 13.3026 | 13.654 | 13.3587 | 13.2118 | NaN | NaN | NaN | 13.4473 | 89.9918 | NaN | NaN | NaN | -18.3207 | NaN | NaN | NaN | NaN | 586.811 | NaN | 19.5021 | NaN | 25.792
6417.1292 | 13.9601 | 13.6101 | 13.6719 | 13.9138 | 13.3177 | 13.5949 | 13.3438 | 13.2097 | NaN | NaN | NaN | 13.517 | 93.6386 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 588.1379 | NaN | 19.8236 | NaN | 24.424
6418.1292 | 13.9605 | 13.6322 | 13.6709 | 13.8964 | 13.3403 | 13.6366 | 13.3559 | 13.2166 | NaN | NaN | NaN | 13.4459 | 92.3614 | NaN | NaN | NaN | 12.9993 | NaN | NaN | NaN | NaN | 587.8163 | NaN | 20.733 | NaN | 23.9412
6419.1292 | 14.0894 | 13.6698 | 13.6739 | 14.0043 | 13.5559 | 13.6585 | 13.3649 | 13.2038 | NaN | NaN | NaN | 13.5176 | 91.6735 | NaN | NaN | NaN | -19.377 | NaN | NaN | NaN | NaN | 589.2541 | NaN | 21.7674 | NaN | 24.6656
6420.1292 | 13.9462 | 13.6141 | 13.6756 | 13.9369 | 13.3728 | 13.6178 | 13.3542 | 13.2041 | NaN | NaN | NaN | 13.5586 | 93.0746 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 587.5115 | NaN | 19.0688 | NaN | 27.4469
6421.1292 | 13.9963 | 13.6351 | 13.6709 | 13.9365 | 13.4021 | 13.5994 | 13.3421 | 13.2016 | NaN | NaN | NaN | 13.4948 | 91.9041 | NaN | NaN | NaN | 43.4648 | NaN | NaN | NaN | NaN | 589.9337 | NaN | 17.9117 | NaN | 23.7549
6422.1292 | 13.9677 | 13.6561 | 13.6712 | 13.9062 | 13.4043 | 13.6398 | 13.3567 | 13.1978 | NaN | NaN | NaN | 13.4609 | 92.3012 | NaN | NaN | NaN | 40.0452 | NaN | NaN | NaN | NaN | 590.2222 | NaN | 18.5736 | NaN | 26.7476
6423.1292 | 13.9336 | 13.6293 | 13.6695 | 13.9143 | 13.4203 | 13.6552 | 13.3428 | 13.1922 | NaN | NaN | NaN | 13.4382 | 94.1775 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 593.4011 | NaN | 17.8301 | NaN | 26.6327
6424.1292 | 13.9605 | 13.6217 | 13.6711 | 13.8919 | 13.3511 | 13.691 | 13.3513 | 13.1937 | NaN | NaN | NaN | 13.4442 | 90.496 | NaN | NaN | NaN | 28.5297 | NaN | NaN | NaN | NaN | 590.2509 | NaN | 19.4561 | NaN | 24.2613
6425.1292 | 13.9471 | 13.7227 | 13.6744 | 13.9064 | 13.4421 | 13.6585 | 13.3682 | 13.1896 | NaN | NaN | NaN | 13.4341 | 93.8339 | NaN | NaN | NaN | -12.4892 | NaN | NaN | NaN | NaN | 592.83 | NaN | 21.9387 | NaN | 26.7979
6426.1292 | 13.9726 | 13.6645 | 13.6734 | 14.0012 | 13.3844 | 13.6511 | 13.3606 | 13.1857 | NaN | NaN | NaN | 13.462 | 94.5184 | NaN | NaN | NaN | -13.7919 | NaN | NaN | NaN | NaN | 589.3615 | NaN | 20.7457 | NaN | 25.7844
6427.1292 | 13.9533 | 13.6214 | 13.6708 | 13.8844 | 13.3498 | 13.6113 | 13.3289 | 13.1903 | NaN | NaN | NaN | 13.4909 | 94.3607 | NaN | NaN | NaN | -13.4065 | NaN | NaN | NaN | NaN | 589.117 | NaN | 20.2777 | NaN | 24.5413
6428.1292 | 13.9956 | 13.7017 | 13.6807 | 13.8996 | 13.4292 | 13.6737 | 13.3536 | 13.1847 | NaN | NaN | NaN | 13.4505 | 93.5841 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 588.9844 | NaN | 20.3346 | NaN | 24.4531
6429.1292 | 13.9619 | 13.7297 | 13.6747 | 13.8468 | 13.4048 | 13.7442 | 13.3688 | 13.1868 | NaN | NaN | NaN | 13.5079 | 92.3645 | NaN | NaN | NaN | -16.9533 | NaN | NaN | NaN | NaN | 592.3223 | NaN | 18.8909 | NaN | 24.9439
6430.1292 | 14.1318 | 13.6045 | 13.6811 | 13.94 | 13.3398 | 13.6113 | 13.3296 | 13.1853 | NaN | NaN | NaN | 13.5352 | 92.3375 | NaN | NaN | NaN | -16.893 | NaN | NaN | NaN | NaN | 592.7764 | NaN | 20.3762 | NaN | 25.9987
6431.1292 | 13.9618 | 13.6552 | 13.6798 | 13.918 | 13.4915 | 13.6881 | 13.3539 | 13.1905 | NaN | NaN | NaN | 13.4389 | 90.8027 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 591.6172 | NaN | 20.8491 | NaN | 27.1721
6432.1292 | 13.9209 | 13.6374 | 13.6754 | 13.8947 | 13.3091 | 13.6509 | 13.3513 | 13.187 | NaN | NaN | NaN | 13.4525 | 95.0509 | NaN | NaN | NaN | -16.4304 | NaN | NaN | NaN | NaN | 591.5899 | NaN | 21.5784 | NaN | 25.1978
6433.1292 | 13.9614 | 13.6376 | 13.6761 | 13.8844 | 13.3265 | 13.6967 | 13.3532 | 13.1924 | NaN | NaN | NaN | 13.6008 | 92.6705 | NaN | NaN | NaN | -5.2208 | NaN | NaN | NaN | NaN | 590.913 | NaN | 22.1051 | NaN | 24.045
6434.1292 | 13.9199 | 13.634 | 13.6789 | 13.858 | 13.3995 | 13.6566 | 13.3501 | 13.1974 | NaN | NaN | NaN | 13.4747 | 93.1859 | NaN | NaN | NaN | 4.4463 | NaN | NaN | NaN | NaN | 590.0968 | NaN | 19.8774 | NaN | 27.5765
6435.1292 | 13.9642 | 13.6085 | 13.6813 | 13.8753 | 13.2444 | 13.7007 | 13.3613 | 13.1936 | NaN | NaN | NaN | 13.5376 | 97.5233 | NaN | NaN | NaN | -9.5905 | NaN | NaN | NaN | NaN | 590.6766 | NaN | 23.8223 | NaN | 26.2453
6436.1292 | 13.9695 | 13.6689 | 13.673 | 13.8585 | 13.2254 | 13.6552 | 13.3697 | 13.1953 | NaN | NaN | NaN | 13.4945 | 94.1019 | NaN | NaN | NaN | 28.1888 | NaN | NaN | NaN | NaN | 591.3761 | NaN | 21.5331 | NaN | 25.6245
6437.1292 | 13.995 | 13.6124 | 13.6718 | 13.8882 | 13.3937 | 13.7303 | 13.353 | 13.1967 | NaN | NaN | NaN | 13.4599 | 93.5128 | NaN | NaN | NaN | 2.5475 | NaN | NaN | NaN | NaN | 592.4621 | NaN | 20.2704 | NaN | 26.447
6438.1292 | 13.9672 | 13.5986 | 13.6802 | 13.9131 | 13.327 | 13.64 | 13.3366 | 13.1989 | NaN | NaN | NaN | 13.5291 | 93.875 | NaN | NaN | NaN | -6.0219 | NaN | NaN | NaN | NaN | 590.1496 | NaN | 21.1316 | NaN | 26.724
6439.1292 | 13.9451 | 13.6902 | 13.6703 | 13.9034 | 13.4289 | 13.6942 | 13.3703 | 13.1914 | NaN | NaN | NaN | 13.4219 | 93.5465 | NaN | NaN | NaN | 13.5105 | NaN | NaN | NaN | NaN | 590.6793 | NaN | 21.1703 | NaN | 26.8959
6440.1292 | 13.9899 | 13.6301 | 13.6707 | 13.8967 | 13.3101 | 13.6458 | 13.3493 | 13.1945 | NaN | NaN | NaN | 13.439 | 92.6333 | NaN | NaN | NaN | -15.1065 | NaN | NaN | NaN | NaN | 591.668 | NaN | 21.7417 | NaN | 26.3247
6441.1292 | 13.9527 | 13.6125 | 13.6722 | 13.9201 | 13.3474 | 13.6415 | 13.351 | 13.1969 | NaN | NaN | NaN | 13.4855 | 92.3719 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 592.3762 | NaN | 21.7358 | NaN | 27.7145
6442.1292 | 14.0416 | 13.7095 | 13.6752 | 13.9789 | 13.2741 | 13.6849 | 13.38 | 13.1935 | NaN | NaN | NaN | 13.4459 | 93.5948 | NaN | NaN | NaN | -14.6599 | NaN | NaN | NaN | NaN | 591.4658 | NaN | 19.3716 | NaN | 24.4689
6443.1292 | 13.9992 | 13.6161 | 13.6774 | 13.8889 | 13.4502 | 13.6589 | 13.3491 | 13.1998 | NaN | NaN | NaN | 13.4768 | 93.4975 | NaN | NaN | NaN | -18.8613 | NaN | NaN | NaN | NaN | 590.1412 | NaN | 20.3643 | NaN | 25.0983
6444.1292 | 14.2137 | 13.739 | 13.6785 | 13.9021 | 13.4207 | 13.7111 | 13.3659 | 13.188 | NaN | NaN | NaN | 13.4552 | 93.0843 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 592.6505 | NaN | 21.2933 | NaN | 26.1177
6445.1292 | 13.9565 | 13.6146 | 13.6807 | 14.0611 | 13.3667 | 13.6441 | 13.355 | 13.1937 | NaN | NaN | NaN | 13.4512 | 96.0223 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 593.5161 | NaN | 18.8226 | NaN | 25.349
6446.1292 | 13.9759 | 13.716 | 13.6834 | 13.9616 | 13.3035 | 13.7694 | 13.351 | 13.1974 | NaN | NaN | NaN | 13.437 | 93.5501 | NaN | NaN | NaN | -12.9379 | NaN | NaN | NaN | NaN | 592.1227 | NaN | 21.2747 | NaN | 24.6233
6447.1292 | 13.9667 | 13.7778 | 13.689 | 13.9128 | 13.3129 | 13.691 | 13.3764 | 13.202 | NaN | NaN | NaN | 13.4268 | 99.6542 | NaN | NaN | NaN | 47.1211 | NaN | NaN | NaN | NaN | 592.3508 | NaN | 23.4406 | NaN | 26.4308
6448.1292 | 13.9934 | 13.5988 | 13.6818 | 13.985 | 13.3823 | 13.6812 | 13.3547 | 13.1975 | NaN | NaN | NaN | 13.4263 | 91.5797 | NaN | NaN | NaN | -5.375 | NaN | NaN | NaN | -18.984 | 594.3638 | NaN | 20.352 | NaN | 25.9808
6449.1292 | 13.9567 | 13.5978 | 13.6868 | 13.9326 | 13.2907 | 13.6531 | 13.3425 | 13.2046 | NaN | NaN | NaN | 13.4325 | 94.3601 | NaN | NaN | NaN | -19.4751 | NaN | NaN | NaN | NaN | 596.0851 | NaN | 20.0053 | NaN | 25.5827
6450.1292 | 13.9376 | 13.6873 | 13.6855 | 13.9093 | 13.421 | 13.6472 | 13.3438 | 13.2009 | NaN | NaN | NaN | 13.4471 | 91.9863 | NaN | NaN | NaN | -7.8841 | NaN | NaN | NaN | NaN | 593.5928 | NaN | 20.6559 | NaN | 25.0059
6451.1292 | 13.9831 | 13.6564 | 13.6829 | 13.9363 | 13.4145 | 13.6461 | 13.3429 | 13.2014 | NaN | NaN | NaN | 13.4203 | 94.9608 | NaN | NaN | NaN | -16.9136 | NaN | NaN | NaN | NaN | 595.9203 | NaN | 20.2587 | NaN | 26.3503
6452.1292 | 13.9435 | 13.6171 | 13.6801 | 13.915 | 13.2888 | 13.6314 | 13.3342 | 13.1989 | NaN | NaN | NaN | 13.5102 | 93.3614 | NaN | NaN | NaN | -8.4833 | NaN | NaN | NaN | NaN | 596.0457 | NaN | 20.2723 | NaN | 25.9018
6453.1292 | 13.9464 | 13.6448 | 13.6828 | 13.9426 | 13.3478 | 13.723 | 13.3425 | 13.2018 | NaN | NaN | NaN | 13.4716 | 92.9929 | NaN | NaN | NaN | 2.8387 | NaN | NaN | NaN | NaN | 593.8371 | NaN | 22.9495 | NaN | 26.541
6454.1292 | 13.9624 | 13.6067 | 13.6878 | 13.9443 | 13.3003 | 13.6093 | 13.3156 | 13.2071 | NaN | NaN | NaN | 13.4302 | 91.5561 | NaN | NaN | NaN | 14.6405 | NaN | NaN | NaN | NaN | 593.1693 | NaN | 20.4994 | NaN | 25.2852
6455.1292 | 13.9911 | 13.6287 | 13.6883 | 13.9634 | 13.2965 | 13.6854 | 13.3524 | 13.2076 | NaN | NaN | NaN | 13.4149 | 94.3125 | NaN | NaN | NaN | -19.0464 | NaN | NaN | NaN | NaN | 593.6233 | NaN | 22.154 | NaN | 27.3367
6456.1292 | 13.9763 | 13.6304 | 13.6874 | 13.9325 | 13.289 | 13.6141 | 13.3262 | 13.1962 | NaN | NaN | NaN | 13.4586 | 93.4996 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 595.1282 | NaN | 21.6437 | NaN | 26.908
6457.1292 | 13.9628 | 13.6176 | 13.6882 | 13.8694 | 13.3639 | 13.6607 | 13.3351 | 13.1969 | NaN | NaN | NaN | 13.473 | 90.7352 | NaN | NaN | NaN | 23.838 | NaN | NaN | NaN | NaN | 594.5057 | NaN | 20.0008 | NaN | 27.552
6458.1292 | 14.0255 | 13.6252 | 13.6903 | 13.8839 | 13.3977 | 13.6038 | 13.3228 | 13.2055 | NaN | NaN | NaN | 13.4119 | 94.08 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 590.4509 | NaN | 21.6321 | NaN | 25.6546
6459.1292 | 13.9658 | 13.6685 | 13.6919 | 13.9098 | 13.2982 | 13.7371 | 13.3617 | 13.1973 | NaN | NaN | NaN | 13.4445 | 92.0233 | NaN | NaN | NaN | 41.0986 | NaN | NaN | NaN | NaN | 594.5058 | NaN | 21.7735 | NaN | 26.64
6460.1292 | 13.9343 | 13.6415 | 13.6978 | 13.9715 | 13.3447 | 13.6345 | 13.343 | 13.2049 | NaN | NaN | NaN | 13.4196 | 92.7384 | NaN | NaN | NaN | -16.2423 | NaN | NaN | NaN | NaN | 596.7144 | NaN | 22.6706 | NaN | 26.8711
6461.1292 | 13.9697 | 13.7384 | 13.6982 | 14.0162 | 13.2096 | 13.6812 | 13.3816 | 13.2001 | NaN | NaN | NaN | 13.4563 | 98.4574 | NaN | NaN | NaN | 12.7392 | NaN | NaN | NaN | NaN | 592.6388 | NaN | 22.4589 | NaN | 26.7456
6462.1292 | 13.963 | 13.6909 | 13.6958 | 13.9368 | 13.314 | 13.6792 | 13.3462 | 13.2014 | NaN | NaN | NaN | 13.7002 | 94.9332 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 593.5045 | NaN | 18.3249 | NaN | 24.1914
6463.1292 | 13.9181 | 13.6284 | 13.6978 | 13.9496 | 13.3549 | 13.6157 | 13.3218 | 13.202 | NaN | NaN | NaN | 13.5241 | 92.9817 | NaN | NaN | NaN | 25.3418 | NaN | NaN | NaN | NaN | 595.4064 | NaN | 20.283 | NaN | 26.1071
6464.1292 | 13.9696 | 13.632 | 13.6972 | 13.8996 | 13.3202 | 13.6124 | 13.3321 | 13.2014 | NaN | NaN | NaN | 13.5754 | 93.259 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 596.8237 | NaN | 21.4434 | NaN | 24.4507
6465.1292 | 13.9377 | 13.6397 | 13.6915 | 13.9275 | 13.3817 | 13.6396 | 13.3486 | 13.1964 | NaN | NaN | NaN | 13.4555 | 93.3334 | NaN | NaN | NaN | -12.2826 | NaN | NaN | NaN | NaN | 598.4618 | NaN | 21.4095 | NaN | 27.0761
6466.1292 | 14.0031 | 13.6281 | 13.699 | 13.9285 | 13.3403 | 13.6309 | 13.342 | 13.1965 | NaN | NaN | NaN | 13.5584 | 95.2401 | NaN | NaN | NaN | 2.7611 | NaN | NaN | NaN | NaN | 599.5827 | NaN | 19.894 | NaN | 27.9643
6467.1292 | 13.9535 | 13.6598 | 13.6956 | 13.9159 | 13.2096 | 13.6461 | 13.3351 | 13.197 | NaN | NaN | NaN | 13.4131 | 92.3129 | NaN | NaN | NaN | 25.984 | NaN | NaN | NaN | NaN | 599.5343 | NaN | 18.8636 | NaN | 24.928
6468.1292 | 13.955 | 13.8758 | 13.6985 | 13.936 | 13.4012 | 13.667 | 13.3929 | 13.203 | NaN | NaN | NaN | 13.4375 | 95.4451 | NaN | NaN | NaN | -13.236 | NaN | NaN | NaN | NaN | 598.6692 | NaN | 20.2182 | NaN | 25.6212
6469.1292 | 13.9422 | 13.7472 | 13.6962 | 13.9568 | 13.418 | 13.704 | 13.3495 | 13.1976 | NaN | NaN | NaN | 13.45 | 91.7942 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 603.9334 | NaN | 21.4318 | NaN | 25.0246
6470.1292 | 13.9661 | 13.7174 | 13.701 | 13.9435 | 13.3703 | 13.7017 | 13.3539 | 13.199 | NaN | NaN | NaN | 13.4436 | 94.5944 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 601.6062 | NaN | 20.767 | NaN | 24.8555
6471.1292 | 13.9456 | 13.8683 | 13.6986 | 13.9668 | 13.3996 | 13.6966 | 13.4003 | 13.194 | NaN | NaN | NaN | 13.4415 | 95.9712 | NaN | NaN | NaN | 11.243 | NaN | NaN | NaN | NaN | 601.3722 | NaN | 18.5782 | NaN | 26.3023
6472.1292 | 14.0372 | 13.6886 | 13.6951 | 13.9473 | 13.2933 | 13.7038 | 13.3663 | 13.1897 | NaN | NaN | NaN | 13.4031 | 95.9556 | NaN | NaN | NaN | -16.3037 | NaN | NaN | NaN | NaN | 599.798 | NaN | 19.4242 | NaN | 28.0017
6473.1292 | 13.975 | 13.6887 | 13.6983 | 13.8783 | 13.2848 | 13.7659 | 13.3585 | 13.1987 | NaN | NaN | NaN | 13.4249 | 93.2435 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 601.1075 | NaN | 19.6821 | NaN | 26.5069
6474.1292 | 13.9231 | 13.6728 | 13.7003 | 13.9575 | 13.3645 | 13.7619 | 13.355 | 13.1937 | NaN | NaN | NaN | 13.4519 | 91.4004 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 601.004 | NaN | 20.5433 | NaN | 26.3346
6475.1292 | 13.9572 | 13.663 | 13.7041 | 14.0495 | 13.2236 | 13.7004 | 13.3572 | 13.2009 | NaN | NaN | NaN | 13.4216 | 91.6574 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 603.2766 | NaN | 19.8989 | NaN | 25.5643
6476.1292 | 13.9166 | 13.6982 | 13.7035 | 13.9686 | 13.4041 | 13.646 | 13.3683 | 13.202 | NaN | NaN | NaN | 13.4182 | 93.6646 | NaN | NaN | NaN | -13.5538 | NaN | NaN | NaN | NaN | 600.077 | NaN | 20.9462 | NaN | 25.1154
6477.1292 | 13.9597 | 13.6688 | 13.7004 | 13.9631 | 13.2378 | 13.7313 | 13.3558 | 13.2084 | NaN | NaN | NaN | 13.4744 | 93.6457 | NaN | NaN | NaN | 12.2074 | NaN | NaN | NaN | NaN | 604.8695 | NaN | 20.888 | NaN | 27.7049
6478.1292 | 13.9433 | 13.7263 | 13.7039 | 13.9607 | 13.3732 | 13.6246 | 13.3684 | 13.201 | NaN | NaN | NaN | 13.4415 | 94.9487 | NaN | NaN | NaN | -1.0512 | NaN | NaN | NaN | NaN | 605.5771 | NaN | 19.7421 | NaN | 25.7972
6479.1292 | 13.9637 | 13.7858 | 13.6993 | 13.9754 | 13.4349 | 13.7166 | 13.3774 | 13.2042 | NaN | NaN | NaN | 13.4476 | 93.1771 | NaN | NaN | NaN | 26.5613 | NaN | NaN | NaN | NaN | 605.2157 | NaN | 19.5365 | NaN | 27.8419
6480.1292 | 14.0514 | 13.6764 | 13.6984 | 13.9346 | 13.3724 | 13.6265 | 13.3422 | 13.1976 | NaN | NaN | NaN | 13.4 | 93.7736 | NaN | NaN | NaN | -0.3543 | NaN | NaN | NaN | NaN | 603.2688 | NaN | 18.7226 | NaN | 23.9314
6481.1292 | 13.9452 | 13.6984 | 13.704 | 13.9669 | 13.4286 | 13.6509 | 13.3454 | 13.2077 | NaN | NaN | NaN | 13.4864 | 91.7099 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 603.4015 | NaN | 22.7987 | NaN | 25.8291
6482.1292 | 13.9653 | 13.6744 | 13.7012 | 13.9832 | 13.4301 | 13.6842 | 13.3428 | 13.1992 | NaN | NaN | NaN | 13.4018 | 95.2268 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 606.2194 | NaN | 18.6021 | NaN | 26.4783
6483.1292 | 14.0553 | 13.7522 | 13.7067 | 14.0126 | 13.3546 | 13.6716 | 13.3617 | 13.2014 | NaN | NaN | NaN | 13.4164 | 93.4099 | NaN | NaN | NaN | 12.41 | NaN | NaN | NaN | NaN | 602.8252 | NaN | 18.8492 | NaN | 24.3382
6484.1292 | 13.937 | 13.7734 | 13.7037 | 13.9351 | 13.418 | 13.6838 | 13.3598 | 13.2021 | NaN | NaN | NaN | 13.4973 | 91.5856 | NaN | NaN | NaN | -2.3414 | NaN | NaN | NaN | NaN | 599.0349 | NaN | 20.9321 | NaN | 28.0052
6485.1292 | 13.9407 | 13.7318 | 13.7019 | 13.9183 | 13.3578 | 13.6677 | 13.3425 | 13.1923 | NaN | NaN | NaN | 13.4521 | 94.0806 | NaN | NaN | NaN | -13.0242 | NaN | NaN | NaN | NaN | 599.4217 | NaN | 25.5063 | NaN | 25.9936
6486.1292 | 13.9135 | 13.686 | 13.7052 | 13.9211 | 13.3217 | 13.675 | 13.3465 | 13.1943 | NaN | NaN | NaN | 13.4597 | 95.1988 | NaN | NaN | NaN | -17.94 | NaN | NaN | NaN | NaN | 597.8821 | NaN | 18.8056 | NaN | 24.8931
6487.1292 | 13.9654 | 13.7252 | 13.7029 | 13.9747 | 13.4554 | 13.6885 | 13.3579 | 13.1921 | NaN | NaN | NaN | 13.405 | 92.7137 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 596.1086 | NaN | 20.54 | NaN | 26.3365
6488.1292 | 13.9247 | 13.6903 | 13.6937 | 13.9381 | 13.3072 | 13.7246 | 13.3573 | 13.1974 | NaN | NaN | NaN | 13.443 | 95.6872 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 582.4509 | NaN | 21.4611 | NaN | 26.7253
6489.1292 | 13.9458 | 13.6838 | 13.6927 | 13.9287 | 13.4247 | 13.6487 | 13.3474 | 13.1952 | NaN | NaN | NaN | 13.4558 | 94.8761 | NaN | NaN | NaN | -4.054 | NaN | NaN | NaN | NaN | 579.2492 | NaN | 18.8162 | NaN | 26.6137
6490.1292 | 13.901 | 13.6438 | 13.6939 | 14.1105 | 13.3605 | 13.6265 | 13.3412 | 13.1988 | NaN | NaN | NaN | 13.5421 | 92.2687 | NaN | NaN | NaN | -13.8254 | NaN | NaN | NaN | NaN | 573.0294 | NaN | 19.8183 | NaN | 22.9349
6491.1292 | 13.9976 | 13.6692 | 13.6915 | 13.973 | 13.3598 | 13.6375 | 13.3376 | 13.1952 | NaN | NaN | NaN | 13.4643 | 97.4 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 576.0026 | NaN | 20.2145 | NaN | 25.752
6492.1292 | 13.9046 | 13.8562 | 13.6903 | 13.9046 | 13.3749 | 13.736 | 13.3618 | 13.1995 | NaN | NaN | NaN | 13.4529 | 98.0579 | NaN | NaN | NaN | 21.9453 | NaN | NaN | NaN | NaN | 583.9531 | NaN | 21.9034 | NaN | 26.9575
6493.1292 | 13.9483 | 13.726 | 13.6896 | 13.9359 | 13.351 | 13.6442 | 13.3663 | 13.2017 | NaN | NaN | NaN | 13.426 | 92.7977 | NaN | NaN | NaN | 23.9073 | NaN | NaN | NaN | NaN | 583.083 | NaN | 20.9767 | NaN | 25.4527
6494.1292 | 13.9393 | 13.6999 | 13.6898 | 13.9751 | 13.433 | 13.6952 | 13.3583 | 13.2004 | NaN | NaN | NaN | 13.4273 | 94.7319 | NaN | NaN | NaN | -3.7976 | NaN | NaN | NaN | NaN | 578.6102 | NaN | 19.2779 | NaN | 27.1991
6495.1292 | 13.9075 | 13.6326 | 13.6877 | 13.9354 | 13.3002 | 13.6507 | 13.3463 | 13.1972 | NaN | NaN | NaN | 13.4232 | 93.9822 | NaN | NaN | NaN | -15.6743 | NaN | NaN | NaN | NaN | 582.9715 | NaN | 23.0276 | NaN | 26.3734
6496.1292 | 13.9509 | 13.7095 | 13.6851 | 13.9199 | 13.2625 | 13.7227 | 13.366 | 13.2017 | NaN | NaN | NaN | 13.4315 | 95.4688 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 584.9779 | NaN | 20.3247 | NaN | 24.799
6497.1292 | 13.8997 | 13.6248 | 13.688 | 13.9567 | 13.3752 | 13.6333 | 13.3323 | 13.2022 | NaN | NaN | NaN | 13.4196 | 94.7647 | NaN | NaN | NaN | -15.0927 | NaN | NaN | NaN | NaN | 585.837 | NaN | 20.3416 | NaN | 25.5433
6498.1292 | 13.9319 | 13.7247 | 13.6874 | 13.9357 | 13.2495 | 13.7979 | 13.3724 | 13.2032 | NaN | NaN | NaN | 13.4478 | 95.4947 | NaN | NaN | NaN | 7.0922 | NaN | NaN | NaN | NaN | 585.8671 | NaN | 20.8921 | NaN | 27.1778
6499.1292 | 13.8872 | 13.6914 | 13.6895 | 13.9229 | 13.267 | 13.6711 | 13.3421 | 13.1961 | NaN | NaN | NaN | 13.5003 | 91.7614 | NaN | NaN | NaN | 0.0655 | NaN | NaN | NaN | NaN | 585.7537 | NaN | 19.5355 | NaN | 25.4626
6500.1292 | 13.9036 | 13.6225 | 13.6857 | 13.962 | 13.3135 | 13.6441 | 13.3447 | 13.1916 | NaN | NaN | NaN | 13.4254 | 98.0687 | NaN | NaN | NaN | 6.1514 | NaN | NaN | NaN | NaN | 588.6881 | NaN | 19.7233 | NaN | 25.6295
6501.1292 | 13.9515 | 13.6739 | 13.683 | 13.9986 | 13.3755 | 13.6825 | 13.3595 | 13.198 | NaN | NaN | NaN | 13.4476 | 99.3439 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 589.6135 | NaN | 20.5909 | NaN | 26.3388
6502.1292 | 13.9438 | 13.6782 | 13.6814 | 13.9426 | 13.4217 | 13.6636 | 13.3585 | 13.1915 | NaN | NaN | NaN | 13.4101 | 94.5946 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 584.3298 | NaN | 18.8715 | NaN | 24.9964
6503.1292 | 14.0227 | 13.6426 | 13.6923 | 13.9621 | 13.3516 | 13.6998 | 13.3675 | 13.196 | NaN | NaN | NaN | 13.4187 | 92.7481 | NaN | NaN | NaN | -2.6838 | NaN | NaN | NaN | NaN | 586.9363 | NaN | 18.9109 | NaN | 25.9275
6504.1292 | 13.9422 | 13.6449 | 13.6891 | 14.0347 | 13.3665 | 13.6585 | 13.3607 | 13.1911 | NaN | NaN | NaN | 13.4307 | 94.5461 | NaN | NaN | NaN | 16.6915 | NaN | NaN | NaN | NaN | 591.8326 | NaN | 18.5287 | NaN | 25.0406
6505.1292 | 13.9339 | 13.6136 | 13.6862 | 13.9517 | 13.2741 | 13.6541 | 13.3509 | 13.1899 | NaN | NaN | NaN | 13.4607 | 92.2102 | NaN | NaN | NaN | -9.4316 | NaN | NaN | NaN | NaN | 603.3896 | NaN | 21.3976 | NaN | 26.586
6506.1292 | 13.9551 | 13.6156 | 13.6886 | 13.9522 | 13.2345 | 13.7052 | 13.3505 | 13.199 | NaN | NaN | NaN | 13.4867 | 94.5285 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 606.0289 | NaN | 20.4451 | NaN | 25.6458
6507.1292 | 13.9329 | 13.6975 | 13.684 | 13.972 | 13.3528 | 13.6942 | 13.3549 | 13.1875 | NaN | NaN | NaN | 13.4218 | 92.18 | NaN | NaN | NaN | -10.8505 | NaN | NaN | NaN | NaN | 608.3529 | NaN | 17.8865 | NaN | 26.3388
6508.1292 | 13.9134 | 13.6187 | 13.6915 | 13.9518 | 13.3116 | 13.6587 | 13.3455 | 13.1811 | NaN | NaN | NaN | 13.4078 | 91.7064 | NaN | NaN | NaN | -11.4305 | NaN | NaN | NaN | NaN | 608.485 | NaN | 21.8207 | NaN | 26.4295
6509.1292 | 13.9683 | 13.6259 | 13.6882 | 13.9583 | 13.4424 | 13.7001 | 13.3439 | 13.1752 | NaN | NaN | NaN | 13.4189 | 90.1082 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 609.8866 | NaN | 19.1593 | NaN | 26.7899
6510.1292 | 13.93 | 13.6231 | 13.6863 | 13.9254 | 13.3587 | 13.6316 | 13.3225 | 13.175 | NaN | NaN | NaN | 13.395 | 92.2179 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 607.2907 | NaN | 22.7397 | NaN | 24.8085
6511.1292 | 14.0058 | 13.6522 | 13.6902 | 13.9843 | 13.3049 | 13.6562 | 13.3445 | 13.1801 | NaN | NaN | NaN | 13.5842 | 93.5983 | NaN | NaN | NaN | 10.8712 | NaN | NaN | NaN | NaN | 607.0441 | NaN | 20.3354 | NaN | 25.7895
6512.1292 | 13.912 | 13.6473 | 13.6901 | 13.923 | 13.3751 | 13.6521 | 13.3367 | 13.1792 | NaN | NaN | NaN | 13.4172 | 92.6125 | NaN | NaN | NaN | -10.8376 | NaN | NaN | NaN | NaN | 607.0687 | NaN | 21.4479 | NaN | 27.4643
6513.1292 | 13.9389 | 13.612 | 13.6909 | 13.956 | 13.2591 | 13.647 | 13.3423 | 13.1749 | NaN | NaN | NaN | 13.5153 | 93.2278 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 608.2779 | NaN | 22.1405 | NaN | 23.9798
6514.1292 | 14.2486 | 13.6094 | 13.692 | 14.0026 | 13.2911 | 13.67 | 13.3322 | 13.1745 | NaN | NaN | NaN | 13.3907 | 92.211 | NaN | NaN | NaN | -7.2717 | NaN | NaN | NaN | NaN | 608.2167 | NaN | 23.3385 | NaN | 26.4186
6515.1292 | 13.9142 | 13.6765 | 13.6925 | 13.985 | 13.3141 | 13.6476 | 13.3499 | 13.1772 | NaN | NaN | NaN | 13.4261 | 94.1156 | NaN | NaN | NaN | -13.1758 | NaN | NaN | NaN | NaN | 606.9729 | NaN | 21.4485 | NaN | 26.1731
6516.1292 | 13.9009 | 13.6155 | 13.6828 | 13.9429 | 13.4286 | 13.6858 | 13.3471 | 13.1782 | NaN | NaN | NaN | 13.4428 | 94.5508 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 609.8415 | NaN | 19.3839 | NaN | 25.4701
6517.1292 | 14.0034 | 13.6207 | 13.684 | 13.9629 | 13.3203 | 13.619 | 13.3275 | 13.175 | NaN | NaN | NaN | 13.432 | 94.9352 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 607.5083 | NaN | 18.6724 | NaN | 25.0133
6518.1292 | 13.9382 | 13.603 | 13.6877 | 13.9787 | 13.4385 | 13.6812 | 13.325 | 13.175 | NaN | NaN | NaN | 13.4279 | 91.0024 | NaN | NaN | NaN | 15.464 | NaN | NaN | NaN | NaN | 608.9931 | NaN | 20.3325 | NaN | 24.9249
6519.1292 | 13.9287 | 13.6673 | 13.6929 | 13.9766 | 13.2565 | 13.6394 | 13.3445 | 13.1745 | NaN | NaN | NaN | 13.4446 | 92.467 | NaN | NaN | NaN | -11.0353 | NaN | NaN | NaN | NaN | 605.7832 | NaN | 19.6227 | NaN | 25.6748
6520.1292 | 13.9568 | 13.6213 | 13.6921 | 13.9327 | 13.3559 | 13.6398 | 13.3288 | 13.1758 | NaN | NaN | NaN | 13.4393 | 92.9175 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 608.9919 | NaN | 19.9801 | NaN | 27.1387
6521.1292 | 13.9077 | 13.6302 | 13.692 | 13.9976 | 13.4362 | 13.6509 | 13.3463 | 13.1776 | NaN | NaN | NaN | 13.4134 | 92.0375 | NaN | NaN | NaN | -13.5733 | NaN | NaN | NaN | NaN | 610.1302 | NaN | 20.1842 | NaN | 25.1597
6522.1292 | 14.0279 | 13.6247 | 13.6879 | 13.9992 | 13.3801 | 13.6218 | 13.3326 | 13.1776 | NaN | NaN | NaN | 13.5741 | 91.8597 | NaN | NaN | NaN | -4.047 | NaN | NaN | NaN | NaN | 606.2855 | NaN | 21.1455 | NaN | 27.5628
6523.1292 | 13.9276 | 13.6154 | 13.6947 | 13.9898 | 13.4312 | 13.6161 | 13.3267 | 13.1757 | NaN | NaN | NaN | 13.4406 | 94.6848 | NaN | NaN | NaN | 25.3063 | NaN | NaN | NaN | NaN | 609.5215 | NaN | 17.8085 | NaN | 22.4026
6524.1292 | 14.0175 | 13.6484 | 13.6844 | 13.9976 | 13.4007 | 13.6378 | 13.3406 | 13.1774 | NaN | NaN | NaN | 13.4244 | 92.6356 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 608.589 | NaN | 18.1612 | NaN | 25.9136
6525.1292 | 13.8946 | 13.629 | 13.6851 | 13.9499 | 13.3513 | 13.6538 | 13.3389 | 13.1704 | NaN | NaN | NaN | 13.4429 | 91.5091 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -9.4098 | 608.6983 | NaN | 21.159 | NaN | 26.9165
6526.1292 | 13.9218 | 13.6233 | 13.6825 | 13.9726 | 13.4281 | 13.6204 | 13.3346 | 13.1752 | NaN | NaN | NaN | 13.6483 | 92.1309 | NaN | NaN | NaN | -15.3397 | NaN | NaN | NaN | NaN | 605.3586 | NaN | 20.3003 | NaN | 23.6494
6527.1292 | 13.9838 | 13.6578 | 13.6777 | 13.9906 | 13.4225 | 13.6649 | 13.3598 | 13.1697 | NaN | NaN | NaN | 13.415 | 99.1984 | NaN | NaN | NaN | 10.6181 | NaN | NaN | NaN | NaN | 606.5427 | NaN | 18.3634 | NaN | 24.7638
6528.1292 | 13.9654 | 13.6078 | 13.6853 | 13.9811 | 13.3429 | 13.6394 | 13.3422 | 13.1726 | NaN | NaN | NaN | 13.4327 | 94.4763 | NaN | NaN | NaN | -17.2991 | NaN | NaN | NaN | NaN | 609.2134 | NaN | 20.7877 | NaN | 26.1573
6529.1292 | 13.9019 | 13.6532 | 13.6836 | 13.966 | 13.3829 | 13.6363 | 13.3431 | 13.1735 | NaN | NaN | NaN | 13.4614 | 91.9907 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 610.1757 | NaN | 21.3239 | NaN | 25.8056
6530.1292 | 13.9999 | 13.7699 | 13.6895 | 13.9862 | 13.4236 | 13.7154 | 13.3721 | 13.1703 | NaN | NaN | NaN | 13.6462 | 93.7482 | NaN | NaN | NaN | 27.9209 | NaN | NaN | NaN | NaN | 600.2241 | NaN | 21.499 | NaN | 27.381
6531.1292 | 14.0014 | 13.7288 | 13.6888 | 13.9937 | 13.4628 | 13.6642 | 13.3689 | 13.1723 | NaN | NaN | NaN | 13.5385 | 94.4418 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 595.7182 | NaN | 20.4373 | NaN | 24.6955
6532.1292 | 13.9103 | 13.6425 | 13.6867 | 13.9291 | 13.2906 | 13.6694 | 13.3552 | 13.1744 | NaN | NaN | NaN | 13.4431 | 91.2068 | NaN | NaN | NaN | 5.43 | NaN | NaN | NaN | NaN | 597.0262 | NaN | 18.3845 | NaN | 23.9834
6533.1292 | 13.9466 | 13.6309 | 13.6856 | 13.9452 | 13.2759 | 13.7411 | 13.357 | 13.1755 | NaN | NaN | NaN | 13.4184 | 99.2605 | NaN | NaN | NaN | 26.7454 | NaN | NaN | NaN | NaN | 596.0685 | NaN | 20.3773 | NaN | 25.5252
6534.1292 | 13.9291 | 13.6384 | 13.688 | 14.0127 | 13.3568 | 13.6701 | 13.3421 | 13.1755 | NaN | NaN | NaN | 13.4292 | 93.524 | NaN | NaN | NaN | -10.5054 | NaN | NaN | NaN | NaN | 596.9918 | NaN | 22.1309 | NaN | 22.4867
6535.1292 | 13.9419 | 13.7151 | 13.6928 | 13.9865 | 13.3559 | 13.6515 | 13.3747 | 13.1767 | NaN | NaN | NaN | 13.4189 | 91.586 | NaN | NaN | NaN | 17.6979 | NaN | NaN | NaN | NaN | 595.5291 | NaN | 17.8872 | NaN | 23.0034
6536.1292 | 13.9482 | 13.6354 | 13.6903 | 13.968 | 13.3872 | 13.6547 | 13.3488 | 13.1828 | NaN | NaN | NaN | 13.4357 | 93.3153 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 597.0085 | NaN | 19.4928 | NaN | 23.0146
6537.1292 | 14.0036 | 13.7172 | 13.6896 | 13.9313 | 13.4302 | 13.6452 | 13.3644 | 13.1771 | NaN | NaN | NaN | 13.3988 | 92.0766 | NaN | NaN | NaN | 11.298 | NaN | NaN | NaN | NaN | 603.6263 | NaN | 23.881 | NaN | 27.0101
6538.1292 | 14.2168 | 13.7349 | 13.6924 | 13.9946 | 13.3399 | 13.6558 | 13.3733 | 13.1787 | NaN | NaN | NaN | 13.5933 | 95.5947 | NaN | NaN | NaN | 21.6169 | NaN | NaN | NaN | NaN | 605.0826 | NaN | 18.1908 | NaN | 25.9714
6539.1292 | 13.9529 | 13.6496 | 13.6893 | 14.0168 | 13.36 | 13.6589 | 13.3717 | 13.1808 | NaN | NaN | NaN | 13.4171 | 97.6781 | NaN | NaN | NaN | -13.2708 | NaN | NaN | NaN | NaN | 606.5229 | NaN | 19.8175 | NaN | 25.3207
6540.1292 | 13.9601 | 13.6413 | 13.6845 | 13.9872 | 13.3917 | 13.6792 | 13.3698 | 13.1763 | NaN | NaN | NaN | 13.3784 | 93.8118 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 607.7685 | NaN | 18.3426 | NaN | 24.5376
6541.1292 | 13.9547 | 13.6483 | 13.6765 | 13.944 | 13.4004 | 13.6254 | 13.3591 | 13.1771 | NaN | NaN | NaN | 13.4105 | 92.5041 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 605.7024 | NaN | 20.085 | NaN | 26.7529
6542.1292 | 13.9049 | 13.6795 | 13.6767 | 13.9635 | 13.356 | 13.7399 | 13.3789 | 13.1785 | NaN | NaN | NaN | 13.4837 | 92.5382 | NaN | NaN | NaN | 14.1202 | NaN | NaN | NaN | NaN | 609.4325 | NaN | 17.9924 | NaN | 24.6825
6543.1292 | 13.9671 | 13.6409 | 13.6746 | 13.9528 | 13.3205 | 13.6517 | 13.3668 | 13.1738 | NaN | NaN | NaN | 13.4468 | 97.194 | NaN | NaN | NaN | -13.8856 | NaN | NaN | NaN | NaN | 609.6679 | NaN | 20.6917 | NaN | 23.3024
6544.1292 | 13.9832 | 13.617 | 13.6685 | 14.0123 | 13.4134 | 13.6212 | 13.3459 | 13.1777 | NaN | NaN | NaN | 13.5509 | 95.3003 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 606.8466 | NaN | 18.1801 | NaN | 26.0005
6545.1292 | 14.0266 | 13.6508 | 13.6732 | 13.9319 | 13.2278 | 13.6412 | 13.3618 | 13.1786 | NaN | NaN | NaN | 13.3929 | 93.8483 | NaN | NaN | NaN | 1.0149 | NaN | NaN | NaN | NaN | 608.7166 | NaN | 20.3392 | NaN | 25.9849
6546.1292 | 13.956 | 13.6275 | 13.6709 | 13.9729 | 13.361 | 13.8225 | 13.3614 | 13.1794 | NaN | NaN | NaN | 13.4929 | 93.928 | NaN | NaN | NaN | 29.4604 | NaN | NaN | NaN | NaN | 604.1793 | NaN | 20.4342 | NaN | 24.9546
6547.1292 | 13.9715 | 13.6591 | 13.6714 | 13.9274 | 13.308 | 13.6835 | 13.3786 | 13.1727 | NaN | NaN | NaN | 13.5127 | 92.1469 | NaN | NaN | NaN | -19.1362 | NaN | NaN | NaN | NaN | 609.2229 | NaN | 20.3829 | NaN | 26.7857
6548.1292 | 13.9417 | 13.6284 | 13.6676 | 13.9379 | 13.2968 | 13.6272 | 13.3667 | 13.1815 | NaN | NaN | NaN | 13.4455 | 93.5473 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 607.7528 | NaN | 18.1887 | NaN | 24.4433
6549.1292 | 13.9305 | 13.7773 | 13.6759 | 13.991 | 13.3156 | 13.6581 | 13.4038 | 13.1736 | NaN | NaN | NaN | 13.4845 | 94.1306 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 611.5473 | NaN | 22.382 | NaN | 26.126
6550.1292 | 13.9742 | 13.6247 | 13.6679 | 13.9744 | 13.4638 | 13.6347 | 13.361 | 13.1816 | NaN | NaN | NaN | 13.4066 | 94.1993 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 609.8331 | NaN | 19.5586 | NaN | 27.7381
6551.1292 | 13.9352 | 13.6705 | 13.6696 | 13.9537 | 13.2974 | 13.6657 | 13.3749 | 13.1769 | NaN | NaN | NaN | 13.4389 | 93.581 | NaN | NaN | NaN | 1.3022 | NaN | NaN | NaN | NaN | 608.0978 | NaN | 21.9018 | NaN | 25.5316
6552.1292 | 13.9622 | 13.63 | 13.6666 | 13.9345 | 13.3177 | 13.625 | 13.3726 | 13.1779 | NaN | NaN | NaN | 13.4352 | 92.0917 | NaN | NaN | NaN | 22.5306 | NaN | NaN | NaN | NaN | 606.071 | NaN | 20.9004 | NaN | 23.8928
6553.1292 | 13.9309 | 13.6688 | 13.6715 | 13.963 | 13.3937 | 13.6197 | 13.3794 | 13.179 | NaN | NaN | NaN | 13.4611 | 91.9315 | NaN | NaN | NaN | 25.5303 | NaN | NaN | NaN | NaN | 604.534 | NaN | 20.0222 | NaN | 26.6949
6554.1292 | 13.951 | 13.6417 | 13.6661 | 13.9383 | 13.3526 | 13.6949 | 13.386 | 13.177 | NaN | NaN | NaN | 13.4228 | 91.1306 | NaN | NaN | NaN | 29.3455 | NaN | NaN | NaN | NaN | 610.8679 | NaN | 19.6145 | NaN | 26.0552
6555.1292 | 13.9315 | 13.6024 | 13.6633 | 13.9532 | 13.3798 | 13.6425 | 13.3712 | 13.1785 | NaN | NaN | NaN | 13.4605 | 92.2691 | NaN | NaN | NaN | -8.8477 | NaN | NaN | NaN | NaN | 609.9727 | NaN | 20.6024 | NaN | 23.8354
6556.1292 | 14.0944 | 13.5973 | 13.6646 | 13.9483 | 13.3606 | 13.6393 | 13.3644 | 13.1786 | NaN | NaN | NaN | 13.4446 | 94.0891 | NaN | NaN | NaN | -18.6158 | NaN | NaN | NaN | NaN | 611.4828 | NaN | 19.5534 | NaN | 27.3342
6557.1292 | 13.9343 | 13.6737 | 13.6621 | 13.9693 | 13.3681 | 13.8277 | 13.3728 | 13.1751 | NaN | NaN | NaN | 13.4593 | 92.2003 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 612.2631 | NaN | 18.3769 | NaN | 27.611
6558.1292 | 13.9311 | 13.6164 | 13.6663 | 13.9423 | 13.4314 | 13.628 | 13.3732 | 13.1802 | NaN | NaN | NaN | 13.4158 | 91.5692 | NaN | NaN | NaN | 21.3543 | NaN | NaN | NaN | NaN | 612.8108 | NaN | 21.1007 | NaN | 25.8337
6559.1292 | 14.0768 | 13.6021 | 13.6641 | 13.9116 | 13.5371 | 13.6302 | 13.3592 | 13.1803 | NaN | NaN | NaN | 13.4275 | 92.2467 | NaN | NaN | NaN | -9.6735 | NaN | NaN | NaN | NaN | 613.0739 | NaN | 21.4243 | NaN | 23.8792
6560.1292 | 13.9745 | 13.6326 | 13.668 | 13.9647 | 13.3974 | 13.6285 | 13.3797 | 13.1788 | NaN | NaN | NaN | 13.4282 | 92.9005 | NaN | NaN | NaN | -16.0322 | NaN | NaN | NaN | NaN | 614.6082 | NaN | 20.347 | NaN | 24.9203
6561.1292 | 13.9916 | 13.5819 | 13.6697 | 13.9574 | 13.3159 | 13.6405 | 13.3545 | 13.1794 | NaN | NaN | NaN | 13.4502 | 91.328 | NaN | NaN | NaN | -18.6529 | NaN | NaN | NaN | NaN | 610.7981 | NaN | 21.6334 | NaN | 26.7909
6562.1292 | 13.9382 | 13.5791 | 13.6762 | 13.9692 | 13.3613 | 13.6435 | 13.3617 | 13.1745 | NaN | NaN | NaN | 13.4312 | 93.7318 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 615.0222 | NaN | 20.4461 | NaN | 26.1141
6563.1292 | 13.9097 | 13.5704 | 13.6689 | 14.0422 | 13.3351 | 13.6268 | 13.3539 | 13.1717 | NaN | NaN | NaN | 13.4492 | 90.7274 | NaN | NaN | NaN | 31.1796 | NaN | NaN | NaN | NaN | 613.7154 | NaN | 20.6827 | NaN | 24.3889
6564.1292 | 13.9174 | 13.6036 | 13.67 | 13.9477 | 13.3252 | 13.6573 | 13.3674 | 13.1782 | NaN | NaN | NaN | 13.4626 | 93.8493 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 614.0543 | NaN | 22.2063 | NaN | 24.4013
6565.1292 | 13.9458 | 13.6642 | 13.6731 | 13.9579 | 13.3836 | 13.6594 | 13.381 | 13.1818 | NaN | NaN | NaN | 13.4607 | 94.0616 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 609.3 | NaN | 19.7776 | NaN | 25.8511
6566.1292 | 13.9373 | 13.6188 | 13.6648 | 13.9971 | 13.4305 | 13.6376 | 13.3625 | 13.1836 | NaN | NaN | NaN | 13.4358 | 91.9465 | NaN | NaN | NaN | 9.6411 | NaN | NaN | NaN | NaN | 605.6077 | NaN | 19.9363 | NaN | 26.4345
6567.1292 | 13.8877 | 13.6275 | 13.676 | 13.9732 | 13.3672 | 13.6897 | 13.3717 | 13.1785 | NaN | NaN | NaN | 13.4448 | 97.4909 | NaN | NaN | NaN | -11.4229 | NaN | NaN | NaN | NaN | 610.3192 | NaN | 17.5031 | NaN | 26.0944
6568.1292 | 13.9349 | 13.6414 | 13.6801 | 13.9568 | 13.4286 | 13.7039 | 13.3725 | 13.1805 | NaN | NaN | NaN | 13.5328 | 92.5069 | NaN | NaN | NaN | -17.5415 | NaN | NaN | NaN | NaN | 614.8472 | NaN | 20.4388 | NaN | 23.1938
6569.1292 | 13.92 | 13.6119 | 13.6701 | 13.9397 | 13.3289 | 13.7216 | 13.3792 | 13.1843 | NaN | NaN | NaN | 13.4602 | 98.6898 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 613.1891 | NaN | 18.34 | NaN | 22.8214
6570.1292 | 13.9816 | 13.6358 | 13.6793 | 13.9825 | 13.3161 | 13.6494 | 13.37 | 13.1866 | NaN | NaN | NaN | 13.4521 | 92.5365 | NaN | NaN | NaN | -4.5284 | NaN | NaN | NaN | NaN | 611.7432 | NaN | 19.7287 | NaN | 22.5367
6571.1292 | 13.9256 | 13.6303 | 13.679 | 13.9844 | 13.4282 | 13.6964 | 13.3781 | 13.182 | NaN | NaN | NaN | 13.4083 | 91.9296 | NaN | NaN | NaN | 23.4369 | NaN | NaN | NaN | NaN | 612.0926 | NaN | 19.8244 | NaN | 24.5934
6572.1292 | 13.9575 | 13.6892 | 13.6748 | 13.9618 | 13.4547 | 13.7923 | 13.403 | 13.1842 | NaN | NaN | NaN | 13.5597 | 94.6403 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 613.034 | NaN | 18.1019 | NaN | 23.7294
6573.1292 | 13.9341 | 13.646 | 13.674 | 13.9939 | 13.4871 | 13.6694 | 13.3779 | 13.1856 | NaN | NaN | NaN | 13.4519 | 103.5649 | NaN | NaN | NaN | -4.2788 | NaN | NaN | NaN | NaN | 610.2657 | NaN | 17.4284 | NaN | 25.2512
6574.1292 | 14.105 | 13.5869 | 13.6797 | 13.951 | 13.4013 | 13.6549 | 13.3764 | 13.1823 | NaN | NaN | NaN | 13.4805 | 91.9394 | NaN | NaN | NaN | 29.4131 | NaN | NaN | NaN | NaN | 615.4047 | NaN | 21.4083 | NaN | 26.4988
6575.1292 | 13.9398 | 13.6448 | 13.6783 | 13.9729 | 13.3502 | 13.6474 | 13.3874 | 13.1896 | NaN | NaN | NaN | 13.4225 | 91.9479 | NaN | NaN | NaN | -12.5212 | NaN | NaN | NaN | NaN | 615.6774 | NaN | 19.3274 | NaN | 27.544
6576.1292 | 13.9314 | 13.6693 | 13.6847 | 14.0029 | 13.4635 | 13.6672 | 13.399 | 13.1898 | NaN | NaN | NaN | 13.4456 | 93.5908 | NaN | NaN | NaN | -12.9838 | NaN | NaN | NaN | NaN | 615.4006 | NaN | 19.7049 | NaN | 25.0674
6577.1292 | 13.9753 | 13.6734 | 13.6704 | 13.9805 | 13.261 | 13.6515 | 13.3843 | 13.186 | NaN | NaN | NaN | 13.4404 | 94.202 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 615.0984 | NaN | 18.0703 | NaN | 25.8813
6578.1292 | 13.9177 | 13.8082 | 13.6769 | 13.9696 | 13.3014 | 13.6361 | 13.412 | 13.193 | NaN | NaN | NaN | 13.5726 | 92.7717 | NaN | NaN | NaN | -11.1512 | NaN | NaN | NaN | NaN | 612.9401 | NaN | 20.5291 | NaN | 23.1473
6579.1292 | 13.8762 | 13.6424 | 13.6742 | 14.0463 | 13.3175 | 13.668 | 13.3888 | 13.1875 | NaN | NaN | NaN | 13.486 | 90.8804 | NaN | NaN | NaN | 22.1597 | NaN | NaN | NaN | NaN | 612.5607 | NaN | 21.0043 | NaN | 23.9961
6580.1292 | 13.9447 | 13.6349 | 13.6805 | 13.9709 | 13.4326 | 13.6483 | 13.3703 | 13.1912 | NaN | NaN | NaN | 13.4408 | 91.2458 | NaN | NaN | NaN | -6.3964 | NaN | NaN | NaN | NaN | 615.0619 | NaN | 17.9385 | NaN | 27.6382
6581.1292 | 13.9338 | 13.6615 | 13.6818 | 14.0034 | 13.4079 | 13.6422 | 13.3752 | 13.1965 | NaN | NaN | NaN | 13.4919 | 93.1454 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 611.174 | NaN | 18.4044 | NaN | 27.0493
6582.1292 | 13.9367 | 13.6384 | 13.6792 | 13.9452 | 13.3106 | 13.6543 | 13.3633 | 13.1994 | NaN | NaN | NaN | 13.4654 | 94.0735 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 612.4037 | NaN | 21.064 | NaN | 26.5654
6583.1292 | 14.0099 | 13.6934 | 13.6828 | 13.9681 | 13.386 | 13.6796 | 13.3819 | 13.197 | NaN | NaN | NaN | 13.413 | 89.4156 | NaN | NaN | NaN | 31.8696 | NaN | NaN | NaN | NaN | 610.3955 | NaN | 20.2529 | NaN | 26.9194
6584.1292 | 13.9315 | 13.6791 | 13.6833 | 13.9333 | 13.3762 | 13.6639 | 13.386 | 13.1951 | NaN | NaN | NaN | 13.4476 | 94.6594 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 607.069 | NaN | 19.496 | NaN | 27.3456
6585.1292 | 13.9731 | 13.6395 | 13.6827 | 14.0197 | 13.2664 | 13.6728 | 13.373 | 13.1962 | NaN | NaN | NaN | 13.452 | 93.047 | NaN | NaN | NaN | -12.5444 | NaN | NaN | NaN | NaN | 602.4204 | NaN | 19.0559 | NaN | 26.9971
6586.1292 | 13.9644 | 13.5982 | 13.6845 | 14.0123 | 13.3343 | 13.6859 | 13.366 | 13.1985 | NaN | NaN | NaN | 13.4601 | 93.1427 | NaN | NaN | NaN | 24.6939 | NaN | NaN | NaN | NaN | 608.1031 | NaN | 21.2424 | NaN | 26.2372
6587.1292 | 13.9566 | 13.602 | 13.6841 | 13.9692 | 13.4398 | 13.6364 | 13.372 | 13.2043 | NaN | NaN | NaN | 13.4377 | 97.3298 | NaN | NaN | NaN | -14.1095 | NaN | NaN | NaN | NaN | 611.0037 | NaN | 17.3177 | NaN | 23.8671
6588.1292 | 13.9419 | 13.6948 | 13.6861 | 13.9328 | 13.3728 | 13.7034 | 13.3766 | 13.2039 | NaN | NaN | NaN | 13.4449 | 92.4853 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 611.2852 | NaN | 18.6557 | NaN | 26.0103
6589.1292 | 13.9416 | 13.7031 | 13.6929 | 14.0157 | 13.263 | 13.6502 | 13.3875 | 13.205 | NaN | NaN | NaN | 13.608 | 91.9258 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 607.9929 | NaN | 17.8729 | NaN | 26.8689
6590.1292 | 13.9597 | 13.6721 | 13.6901 | 13.9826 | 13.4083 | 13.6769 | 13.3904 | 13.1976 | NaN | NaN | NaN | 13.4568 | 94.3104 | NaN | NaN | NaN | 5.3959 | NaN | NaN | NaN | NaN | 610.0305 | NaN | 20.5458 | NaN | 26.6073
6591.1292 | 13.9534 | 13.6617 | 13.6916 | 13.9703 | 13.3344 | 13.6684 | 13.3759 | 13.2061 | NaN | NaN | NaN | 13.5346 | 93.6925 | NaN | NaN | NaN | -10.074 | NaN | NaN | NaN | NaN | 605.7561 | NaN | 17.5793 | NaN | 25.5642
6592.1292 | 13.9928 | 13.5939 | 13.6924 | 13.983 | 13.3531 | 13.6406 | 13.3724 | 13.2042 | NaN | NaN | NaN | 13.4357 | 91.8714 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 606.573 | NaN | 19.6388 | NaN | 26.4499
6593.1292 | 13.9556 | 13.6079 | 13.6914 | 14.003 | 13.2906 | 13.6544 | 13.3765 | 13.1983 | NaN | NaN | NaN | 13.4615 | 93.6088 | NaN | NaN | NaN | -7.2798 | NaN | NaN | NaN | NaN | 609.9357 | NaN | 20.0983 | NaN | 25.4789
6594.1292 | 13.9437 | 13.6085 | 13.6986 | 14.0321 | 13.4486 | 13.6476 | 13.3608 | 13.2009 | NaN | NaN | NaN | 13.4763 | 94.8801 | NaN | NaN | NaN | -4.8283 | NaN | NaN | NaN | NaN | 602.7877 | NaN | 18.698 | NaN | 27.5109
6595.1292 | 13.9516 | 13.6471 | 13.6977 | 14.0342 | 13.3229 | 13.6662 | 13.3908 | 13.2024 | NaN | NaN | NaN | 13.4482 | 91.6285 | NaN | NaN | NaN | -11.2391 | NaN | NaN | NaN | NaN | 605.2122 | NaN | 19.6163 | NaN | 25.4772
6596.1292 | 13.9686 | 13.5969 | 13.699 | 13.9953 | 13.421 | 13.7133 | 13.3793 | 13.2003 | NaN | NaN | NaN | 13.4726 | 93.8196 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 598.7711 | NaN | 18.5705 | NaN | 24.3464
6597.1292 | 13.9501 | 13.5998 | 13.7019 | 13.9427 | 13.49 | 13.7639 | 13.3801 | 13.2014 | NaN | NaN | NaN | 13.452 | 93.7074 | NaN | NaN | NaN | -16.0459 | NaN | NaN | NaN | NaN | 594.1742 | NaN | 20.2174 | NaN | 25.5249
6598.1292 | 13.9303 | 13.6012 | 13.7021 | 14.0103 | 13.4105 | 13.6553 | 13.3826 | 13.2087 | NaN | NaN | NaN | 13.4278 | 93.74 | NaN | NaN | NaN | 6.4315 | NaN | NaN | NaN | NaN | 590.6963 | NaN | 22.4886 | NaN | 25.3865
6599.1292 | 13.9546 | 13.599 | 13.7009 | 13.9772 | 13.4026 | 13.6982 | 13.3804 | 13.2082 | NaN | NaN | NaN | 13.454 | 91.0495 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 590.1821 | NaN | 20.7721 | NaN | 26.9722
6600.1448 | 13.9382 | 13.5958 | 13.705 | 14.0225 | 13.3925 | 13.6892 | 13.3774 | 13.2004 | NaN | NaN | NaN | 13.441 | 91.3612 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 595.0173 | NaN | 17.7546 | NaN | 25.3507
6601.1292 | 13.9621 | 13.6173 | 13.7008 | 14.0009 | 13.3251 | 13.6526 | 13.3697 | 13.1998 | NaN | NaN | NaN | 13.5245 | 93.4528 | NaN | NaN | NaN | -3.3438 | NaN | NaN | NaN | NaN | 589.8447 | NaN | 19.811 | NaN | 26.7449
6602.1292 | 14.0328 | 13.5835 | 13.6978 | 13.9924 | 13.3752 | 13.7975 | 13.3828 | 13.1992 | NaN | NaN | NaN | 13.46 | 91.4727 | NaN | NaN | NaN | -16.5764 | NaN | NaN | NaN | NaN | 591.3233 | NaN | 21.4308 | NaN | 25.2032
6603.1292 | 13.9716 | 13.5919 | 13.6981 | 13.9984 | 13.35 | 13.7222 | 13.3796 | 13.1947 | NaN | NaN | NaN | 13.4402 | 91.9379 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 585.4329 | NaN | 20.4897 | NaN | 26.8676
6604.1292 | 13.9171 | 13.6106 | 13.6958 | 14.0083 | 13.4875 | 13.7545 | 13.379 | 13.195 | NaN | NaN | NaN | 13.4682 | 94.5821 | NaN | NaN | NaN | 6.8182 | NaN | NaN | NaN | NaN | 591.5175 | NaN | 18.5638 | NaN | 24.6904
6605.1292 | 13.9376 | 13.5892 | 13.6956 | 13.9924 | 13.3776 | 13.6553 | 13.3826 | 13.196 | NaN | NaN | NaN | 13.4621 | 94.4355 | NaN | NaN | NaN | 29.7251 | NaN | NaN | NaN | NaN | 601.6687 | NaN | 20.4337 | NaN | 24.8598
6606.1292 | 13.8837 | 13.6242 | 13.6922 | 14.0138 | 13.3878 | 13.6702 | 13.3935 | 13.1957 | NaN | NaN | NaN | 13.5984 | 91.4583 | NaN | NaN | NaN | 5.5639 | NaN | NaN | NaN | NaN | 603.7997 | NaN | 19.3119 | NaN | 25.162
6607.1292 | 13.9228 | 13.6814 | 13.6941 | 14.0383 | 13.3551 | 13.6901 | 13.3859 | 13.2024 | NaN | NaN | NaN | 13.4759 | 91.0995 | NaN | NaN | NaN | -3.5327 | NaN | NaN | NaN | NaN | 604.5224 | NaN | 20.3729 | NaN | 27.6208
6608.1292 | 13.9434 | 13.5962 | 13.7028 | 14.1302 | 13.3125 | 13.6465 | 13.3812 | 13.2013 | NaN | NaN | NaN | 13.6453 | 92.6898 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 601.5718 | NaN | 17.8832 | NaN | 22.7412
6609.1292 | 13.9106 | 13.6037 | 13.7011 | 14 | 13.28 | 13.6626 | 13.3682 | 13.206 | NaN | NaN | NaN | 13.4573 | 99.8563 | NaN | NaN | NaN | 2.4238 | NaN | NaN | NaN | NaN | 602.0583 | NaN | 17.8689 | NaN | 26.6934
6610.1292 | 13.9535 | 13.6165 | 13.6969 | 13.9501 | 13.4462 | 13.7186 | 13.3818 | 13.1997 | NaN | NaN | NaN | 13.4532 | 91.8873 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 598.6142 | NaN | 19.1229 | NaN | 26.3582
6611.1292 | 13.9356 | 13.6077 | 13.6914 | 13.9634 | 13.3534 | 13.6439 | 13.3736 | 13.2021 | NaN | NaN | NaN | 13.4588 | 94.8893 | NaN | NaN | NaN | 2.0065 | NaN | NaN | NaN | NaN | 598.9077 | NaN | 18.8827 | NaN | 27.0621
6612.1292 | 13.9575 | 13.6058 | 13.6886 | 14.0006 | 13.4164 | 13.6595 | 13.387 | 13.2054 | NaN | NaN | NaN | 13.4562 | 91.0482 | NaN | NaN | NaN | 21.1743 | NaN | NaN | NaN | NaN | 605.7738 | NaN | 18.4869 | NaN | 25.5093
6613.1292 | 13.9339 | 13.5971 | 13.6911 | 13.9936 | 13.3457 | 13.7965 | 13.3883 | 13.2037 | NaN | NaN | NaN | 13.4602 | 91.096 | NaN | NaN | NaN | -14.4819 | NaN | NaN | NaN | NaN | 604.3218 | NaN | 20.1103 | NaN | 26.0186
6614.1292 | 14.0016 | 13.5757 | 13.6878 | 14.0025 | 13.3357 | 13.6577 | 13.3845 | 13.2056 | NaN | NaN | NaN | 13.4979 | 93.2504 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 604.5429 | NaN | 20.5798 | NaN | 27.4722
6615.1292 | 13.9486 | 13.5802 | 13.6823 | 13.991 | 13.2965 | 13.6615 | 13.3745 | 13.2082 | NaN | NaN | NaN | 13.484 | 93.6564 | NaN | NaN | NaN | 20.8208 | NaN | NaN | NaN | NaN | 601.9592 | NaN | 19.6788 | NaN | 26.4196
6616.1292 | 13.9183 | 13.5976 | 13.6706 | 14.011 | 13.3688 | 13.7135 | 13.3969 | 13.2122 | NaN | NaN | NaN | 13.4602 | 92.6775 | NaN | NaN | NaN | -8.0753 | NaN | NaN | NaN | NaN | 599.9556 | NaN | 20.7306 | NaN | 25.9709
6617.1292 | 13.916 | 13.6615 | 13.6718 | 13.9626 | 13.3616 | 13.6544 | 13.4055 | 13.2068 | NaN | NaN | NaN | 13.4581 | 96.6112 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 602.9539 | NaN | 22.3039 | NaN | 26.1781
6618.1292 | 13.9617 | 13.6345 | 13.6742 | 13.9967 | 13.3654 | 13.7328 | 13.4097 | 13.2027 | NaN | NaN | NaN | 13.4752 | 93.6773 | NaN | NaN | NaN | -1.937 | NaN | NaN | NaN | NaN | 601.0914 | NaN | 20.072 | NaN | 25.2823
6619.1292 | 14.0753 | 13.5848 | 13.6716 | 13.9903 | 13.4099 | 13.6635 | 13.3855 | 13.199 | NaN | NaN | NaN | 13.5468 | 93.1247 | NaN | NaN | NaN | -10.4304 | NaN | NaN | NaN | NaN | 604.968 | NaN | 18.9437 | NaN | 26.2157
6620.1292 | 13.9441 | 13.6255 | 13.6778 | 13.96 | 13.3829 | 13.663 | 13.3848 | 13.2051 | NaN | NaN | NaN | 13.4679 | 92.9376 | NaN | NaN | NaN | -15.0479 | NaN | NaN | NaN | NaN | 605.7396 | NaN | 19.6758 | NaN | 24.4043
6621.1292 | 13.9432 | 13.656 | 13.6628 | 13.9932 | 13.4526 | 13.7214 | 13.4072 | 13.2023 | NaN | NaN | NaN | 13.4605 | 92.8023 | NaN | NaN | NaN | -17.8109 | NaN | NaN | NaN | NaN | 606.1378 | NaN | 19.6376 | NaN | 24.9817
6622.1292 | 13.8875 | 13.5885 | 13.6653 | 13.9916 | 13.3559 | 13.671 | 13.3897 | 13.201 | NaN | NaN | NaN | 13.4621 | 94.564 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 608.4063 | NaN | 21.1166 | NaN | 23.2858
6623.1292 | 13.9382 | 13.5948 | 13.6695 | 13.9632 | 13.3486 | 13.6492 | 13.3829 | 13.1985 | NaN | NaN | NaN | 13.465 | 93.081 | NaN | NaN | NaN | 18.7507 | NaN | NaN | NaN | NaN | 606.2329 | NaN | 19.0421 | NaN | 25.6394
6624.1292 | 13.9197 | 13.6019 | 13.6668 | 13.9733 | 13.3347 | 13.6448 | 13.3871 | 13.1958 | NaN | NaN | NaN | 13.4974 | 93.7752 | NaN | NaN | NaN | 8.7357 | NaN | NaN | NaN | NaN | 603.2931 | NaN | 21.4613 | NaN | 25.6032
6625.1292 | 13.9394 | 13.607 | 13.6633 | 13.9815 | 13.3963 | 13.7124 | 13.3839 | 13.1926 | NaN | NaN | NaN | 13.4689 | 91.6255 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 600.9735 | NaN | 16.6182 | NaN | 26.1888
6626.1292 | 13.885 | 13.6246 | 13.6619 | 13.9911 | 13.4101 | 13.6692 | 13.3884 | 13.1882 | NaN | NaN | NaN | 13.498 | 94.2769 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 604.5185 | NaN | 18.8269 | NaN | 26.0038
6627.1292 | 13.9379 | 13.6565 | 13.6563 | 13.9533 | 13.3674 | 13.6949 | 13.4198 | 13.1927 | NaN | NaN | NaN | 13.5386 | 92.7625 | NaN | NaN | NaN | -7.9148 | NaN | NaN | NaN | NaN | 604.8595 | NaN | 22.0611 | NaN | 24.8692
6628.1292 | 13.8828 | 13.6922 | 13.6515 | 14.0672 | 13.458 | 13.657 | 13.4086 | 13.191 | NaN | NaN | NaN | 13.5036 | 92.9606 | NaN | NaN | NaN | 4.6511 | NaN | NaN | NaN | NaN | 605.8107 | NaN | 18.8401 | NaN | 25.3182
6629.1292 | 13.9397 | 13.592 | 13.6546 | 13.9785 | 13.4885 | 13.6355 | 13.3873 | 13.1864 | NaN | NaN | NaN | 13.4527 | 91.2028 | NaN | NaN | NaN | -10.1419 | NaN | NaN | NaN | NaN | 605.1728 | NaN | 21.5604 | NaN | 26.3691
6630.1292 | 13.9068 | 13.6166 | 13.6505 | 13.9437 | 13.2347 | 13.76 | 13.3828 | 13.1929 | NaN | NaN | NaN | 13.4728 | 92.926 | NaN | NaN | NaN | -0.4946 | NaN | NaN | NaN | NaN | 603.18 | NaN | 19.7899 | NaN | 25.1508
6631.1292 | 13.9986 | 13.6194 | 13.6477 | 13.9459 | 13.3885 | 13.6355 | 13.3866 | 13.1943 | NaN | NaN | NaN | 13.4651 | 94.5276 | NaN | NaN | NaN | -7.5548 | NaN | NaN | NaN | NaN | 598.898 | NaN | 19.8549 | NaN | 25.1647
6632.1292 | 13.9293 | 13.6195 | 13.6487 | 13.9457 | 13.4389 | 13.6534 | 13.4021 | 13.1986 | NaN | NaN | NaN | 13.4509 | 96.6167 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 603.5411 | NaN | 17.6454 | NaN | 26.3534
6633.1292 | 13.9368 | 13.6184 | 13.6469 | 13.9878 | 13.4369 | 13.6356 | 13.3851 | 13.1942 | NaN | NaN | NaN | 13.4613 | 95.7467 | NaN | NaN | NaN | -16.2976 | NaN | NaN | NaN | NaN | 600.0553 | NaN | 18.3572 | NaN | 24.4079
6634.1292 | 13.9324 | 13.6405 | 13.6491 | 13.9342 | 13.4196 | 13.6631 | 13.4028 | 13.2022 | NaN | NaN | NaN | 13.444 | 93.3776 | NaN | NaN | NaN | 21.4365 | NaN | NaN | NaN | NaN | 604.0666 | NaN | 17.3056 | NaN | 25.9655
6635.1292 | 13.883 | 13.6366 | 13.6567 | 14.0216 | 13.368 | 13.6464 | 13.3923 | 13.1993 | NaN | NaN | NaN | 13.4797 | 106.7052 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 603.0395 | NaN | 21.6971 | NaN | 25.7174
6636.1292 | 13.9274 | 13.6429 | 13.6556 | 13.9443 | 13.3657 | 13.6351 | 13.4184 | 13.2049 | NaN | NaN | NaN | 13.5139 | 93.8146 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 604.0779 | NaN | 20.1084 | NaN | 25.2207
6637.1292 | 13.8653 | 13.6535 | 13.6536 | 13.967 | 13.3486 | 13.7232 | 13.4125 | 13.2033 | NaN | NaN | NaN | 13.5092 | 92.0916 | NaN | NaN | NaN | -11.9338 | NaN | NaN | NaN | NaN | 603.0314 | NaN | 20.2077 | NaN | 26.7783
6638.1292 | 13.9028 | 13.6388 | 13.6477 | 13.9395 | 13.3222 | 13.7027 | 13.4143 | 13.1965 | NaN | NaN | NaN | 13.4807 | 94.5037 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 600.7468 | NaN | 20.4381 | NaN | 24.6623
6639.1448 | 13.9266 | 13.6173 | 13.6503 | 13.9806 | 13.4069 | 13.7308 | 13.3978 | 13.2026 | NaN | NaN | NaN | 13.4854 | 94.9794 | NaN | NaN | NaN | 4.7876 | NaN | NaN | NaN | NaN | 600.3827 | NaN | 20.0324 | NaN | 24.704
6640.1292 | 13.9222 | 13.6126 | 13.6608 | 13.9324 | 13.2961 | 13.6749 | 13.4022 | 13.2022 | NaN | NaN | NaN | 13.5422 | 92.5008 | NaN | NaN | NaN | -12.8312 | NaN | NaN | NaN | NaN | 604.0074 | NaN | 19.8068 | NaN | 25.2422
6641.1448 | 13.9144 | 13.6039 | 13.6581 | 13.9949 | 13.3122 | 13.7177 | 13.4025 | 13.2057 | NaN | NaN | NaN | 13.4923 | 90.5821 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 602.7855 | NaN | 23.6137 | NaN | 27.1204
6642.1292 | 13.892 | 13.6192 | 13.6586 | 13.9802 | 13.3789 | 13.6268 | 13.3925 | 13.2076 | NaN | NaN | NaN | 13.4906 | 89.1772 | NaN | NaN | NaN | 16.6945 | NaN | NaN | NaN | NaN | 598.4543 | NaN | 18.4575 | NaN | 25.604
6643.1292 | 14.0345 | 13.6667 | 13.6628 | 13.9197 | 13.3812 | 13.6479 | 13.4179 | 13.2077 | NaN | NaN | NaN | 13.4645 | 93.4679 | NaN | NaN | NaN | -15.6204 | NaN | NaN | NaN | NaN | 604.6764 | NaN | 20.9799 | NaN | 24.861
6644.1292 | 13.9177 | 13.6244 | 13.6549 | 13.9918 | 13.4035 | 13.6375 | 13.4013 | 13.2085 | NaN | NaN | NaN | 13.4569 | 91.5742 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 604.3829 | NaN | 17.0583 | NaN | 24.5598
6645.1292 | 13.9479 | 13.6319 | 13.6604 | 13.971 | 13.323 | 13.7271 | 13.3972 | 13.2111 | NaN | NaN | NaN | 13.4779 | 92.2784 | NaN | NaN | NaN | 24.0766 | NaN | NaN | NaN | NaN | 603.084 | NaN | 19.0328 | NaN | 26.826
6646.1292 | 13.9162 | 13.655 | 13.6647 | 13.9917 | 13.2794 | 13.6477 | 13.4048 | 13.2096 | NaN | NaN | NaN | 13.4831 | 94.0025 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 605.5741 | NaN | 19.6928 | NaN | 25.695
6647.1448 | 13.9555 | 13.6457 | 13.6616 | 13.9588 | 13.5043 | 13.6639 | 13.4 | 13.2085 | NaN | NaN | NaN | 13.4555 | 93.1533 | NaN | NaN | NaN | 1.1589 | NaN | NaN | NaN | NaN | 606.1862 | NaN | 18.0582 | NaN | 27.3704
6648.1292 | 13.906 | 13.6673 | 13.6716 | 13.9973 | 13.4306 | 13.6416 | 13.396 | 13.209 | NaN | NaN | NaN | 13.4572 | 93.7988 | NaN | NaN | NaN | -7.4477 | NaN | NaN | NaN | NaN | 603.5479 | NaN | 17.5095 | NaN | 25.9788
6649.1292 | 13.9229 | 13.6367 | 13.6659 | 13.9701 | 13.2997 | 13.6396 | 13.4144 | 13.2016 | NaN | NaN | NaN | 13.6258 | 90.5121 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 606.2193 | NaN | 20.088 | NaN | 24.6678
6650.1292 | 13.8836 | 13.6372 | 13.6702 | 13.9779 | 13.3603 | 13.7069 | 13.4041 | 13.2075 | NaN | NaN | NaN | 13.4552 | 93.1837 | NaN | NaN | NaN | -2.5535 | NaN | NaN | NaN | NaN | 605.1825 | NaN | 19.4519 | NaN | 27.9785
6651.1292 | 13.9446 | 13.651 | 13.67 | 13.9849 | 13.4965 | 13.6456 | 13.3905 | 13.2042 | NaN | NaN | NaN | 13.465 | 94.5376 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 605.1143 | NaN | 15.9544 | NaN | 25.8063
6652.1292 | 13.9285 | 13.6301 | 13.6683 | 13.9413 | 13.3627 | 13.6347 | 13.3958 | 13.2028 | NaN | NaN | NaN | 13.6447 | 93.9561 | NaN | NaN | NaN | 22.6083 | NaN | NaN | NaN | NaN | 605.0946 | NaN | 21.3093 | NaN | 25.2496
6653.1292 | 13.9114 | 13.6638 | 13.6736 | 13.9297 | 13.373 | 13.6343 | 13.404 | 13.2105 | NaN | NaN | NaN | 13.4589 | 96.5261 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 607.5146 | NaN | 17.2482 | NaN | 24.5895
6654.1292 | 13.9172 | 13.7271 | 13.6723 | 13.971 | 13.4538 | 13.6275 | 13.4091 | 13.2044 | NaN | NaN | NaN | 13.4567 | 99.0141 | NaN | NaN | NaN | -5.4832 | NaN | NaN | NaN | NaN | 611.0917 | NaN | 15.7515 | NaN | 26.6263
6655.1292 | 13.9574 | 13.6727 | 13.6782 | 13.9741 | 13.3869 | 13.6272 | 13.4048 | 13.2001 | NaN | NaN | NaN | 13.4597 | 92.9885 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 608.9337 | NaN | 20.6737 | NaN | 26.6284
6656.1292 | 13.9294 | 13.673 | 13.6798 | 13.9301 | 13.4422 | 13.6381 | 13.4042 | 13.2083 | NaN | NaN | NaN | 13.4973 | 92.4915 | NaN | NaN | NaN | -17.2471 | NaN | NaN | NaN | NaN | 606.9055 | NaN | 21.1519 | NaN | 25.2003
6657.1292 | 13.9186 | 13.6407 | 13.6799 | 13.9807 | 13.2913 | 13.6341 | 13.395 | 13.2034 | NaN | NaN | NaN | 13.4618 | 93.9373 | NaN | NaN | NaN | 27.4895 | NaN | NaN | NaN | NaN | 603.8555 | NaN | 18.8095 | NaN | 24.1934
6658.1448 | 14.0775 | 13.699 | 13.6793 | 13.9699 | 13.3873 | 13.6493 | 13.4195 | 13.1957 | NaN | NaN | NaN | 13.4504 | 91.3293 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 600.8006 | NaN | 19.5574 | NaN | 25.2416
6659.1292 | 13.9543 | 13.6774 | 13.6787 | 13.9533 | 13.3531 | 13.6434 | 13.4122 | 13.2044 | NaN | NaN | NaN | 13.4724 | 93.857 | NaN | NaN | NaN | -1.9783 | NaN | NaN | NaN | NaN | 597.078 | NaN | 20.2849 | NaN | 26.3982
6660.1292 | 13.9317 | 13.6994 | 13.6842 | 13.9839 | 13.3366 | 13.6344 | 13.4184 | 13.198 | NaN | NaN | NaN | 13.662 | 92.4963 | NaN | NaN | NaN | -17.0219 | NaN | NaN | NaN | NaN | 599.5589 | NaN | 20.1789 | NaN | 26.5435
6661.1292 | 13.8971 | 13.6476 | 13.683 | 13.9192 | 13.4418 | 13.6374 | 13.4062 | 13.1982 | NaN | NaN | NaN | 13.485 | 93.0923 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 607.7355 | NaN | 19.066 | NaN | 25.4497
6662.1292 | 13.9082 | 13.6768 | 13.6814 | 13.8886 | 13.4719 | 13.6616 | 13.4137 | 13.1999 | NaN | NaN | NaN | 13.5445 | 94.9195 | NaN | NaN | NaN | -6.0594 | NaN | NaN | NaN | NaN | 604.5457 | NaN | 18.7345 | NaN | 29.3986
6663.1292 | 13.9428 | 13.6485 | 13.6865 | 13.9396 | 13.4391 | 13.7287 | 13.3932 | 13.2024 | NaN | NaN | NaN | 13.4716 | 90.9708 | NaN | NaN | NaN | -19.4363 | NaN | NaN | NaN | NaN | 606.9197 | NaN | 18.9236 | NaN | 23.7891
6664.1292 | 13.9359 | 13.6476 | 13.6908 | 13.9571 | 13.4009 | 13.6884 | 13.3913 | 13.2021 | NaN | NaN | NaN | 13.4422 | 93.5424 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 600.4145 | NaN | 20.7379 | NaN | 25.5136
6665.1292 | 13.9584 | 13.8428 | 13.687 | 13.9078 | 13.4392 | 13.6608 | 13.4467 | 13.2044 | NaN | NaN | NaN | 13.4581 | 92.9825 | NaN | NaN | NaN | 23.6179 | NaN | NaN | NaN | NaN | 603.8046 | NaN | 17.7772 | NaN | 24.1745
6666.1292 | 13.9336 | 13.6595 | 13.6856 | 13.8937 | 13.3838 | 13.7142 | 13.3883 | 13.2065 | NaN | NaN | NaN | 13.4921 | 91.5546 | NaN | NaN | NaN | -15.359 | NaN | NaN | NaN | NaN | 596.283 | NaN | 18.2086 | NaN | 24.4974
6667.1292 | 13.9324 | 13.6745 | 13.6853 | 13.9542 | 13.3451 | 13.657 | 13.3887 | 13.2084 | NaN | NaN | NaN | 13.4761 | 92.8365 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 580.7874 | NaN | 18.9783 | NaN | 26.3904
6668.1292 | 13.8905 | 13.6946 | 13.6807 | 13.9195 | 13.4523 | 13.6494 | 13.4039 | 13.209 | NaN | NaN | NaN | 13.4791 | 90.6917 | NaN | NaN | NaN | -14.0264 | NaN | NaN | NaN | NaN | 582.8847 | NaN | 20.1303 | NaN | 24.8464
6669.1292 | 13.9319 | 13.6557 | 13.6887 | 13.9189 | 13.2979 | 13.6431 | 13.393 | 13.2093 | NaN | NaN | NaN | 13.6054 | 93.8191 | NaN | NaN | NaN | -7.1691 | NaN | NaN | NaN | NaN | 582.7396 | NaN | 18.9757 | NaN | 23.4112
6670.1292 | 13.8982 | 13.7367 | 13.691 | 13.9361 | 13.2843 | 13.6445 | 13.4073 | 13.2122 | NaN | NaN | NaN | 13.5107 | 93.2298 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 590.0173 | NaN | 22.8411 | NaN | 25.5727
6671.1292 | 13.9235 | 13.6997 | 13.6891 | 13.9075 | 13.462 | 13.6743 | 13.388 | 13.2107 | NaN | NaN | NaN | 13.4437 | 92.1354 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 592.4395 | NaN | 18.155 | NaN | 24.6036
6672.1292 | 13.9103 | 13.687 | 13.6843 | 13.9233 | 13.4557 | 13.673 | 13.3982 | 13.2099 | NaN | NaN | NaN | 13.5254 | 101.9974 | NaN | NaN | NaN | -12.5695 | NaN | NaN | NaN | NaN | 590.8851 | NaN | 16.1646 | NaN | 23.2284
6673.1292 | 14.0625 | 13.6795 | 13.687 | 13.9092 | 13.4477 | 13.7502 | 13.3809 | 13.2062 | NaN | NaN | NaN | 13.4707 | 92.8299 | NaN | NaN | NaN | -19.8147 | NaN | NaN | NaN | NaN | 580.7019 | NaN | 20.0787 | NaN | 24.0196
6674.1292 | 13.9379 | 13.747 | 13.6873 | 13.9545 | 13.3709 | 13.6467 | 13.3912 | 13.2036 | NaN | NaN | NaN | 13.4774 | 94.287 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 569.0151 | NaN | 18.4322 | NaN | 26.175
6675.1292 | 13.9356 | 13.6915 | 13.6926 | 13.9565 | 13.4547 | 13.6652 | 13.3958 | 13.208 | NaN | NaN | NaN | 13.4553 | 91.2435 | NaN | NaN | NaN | 1.9381 | NaN | NaN | NaN | NaN | 566.6817 | NaN | 21.9879 | NaN | 25.0935
6676.1292 | 13.9038 | 13.655 | 13.6873 | 13.9898 | 13.2398 | 13.6506 | 13.3871 | 13.196 | NaN | NaN | NaN | 13.4996 | 94.0448 | NaN | NaN | NaN | -14.912 | NaN | NaN | NaN | NaN | 567.4192 | NaN | 19.9966 | NaN | 26.8248
6677.1292 | 13.9578 | 13.6666 | 13.6931 | 13.9585 | 13.4414 | 13.6464 | 13.3749 | 13.1978 | NaN | NaN | NaN | 13.4467 | 95.9147 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 566.7928 | NaN | 21.6373 | NaN | 25.8977
6678.1292 | 13.9408 | 13.7256 | 13.6892 | 13.8883 | 13.3452 | 13.6721 | 13.3993 | 13.1942 | NaN | NaN | NaN | 13.4564 | 91.594 | NaN | NaN | NaN | -3.5179 | NaN | NaN | NaN | NaN | 577.6987 | NaN | 21.5567 | NaN | 24.1424
6679.1292 | 13.9186 | 13.6577 | 13.6966 | 13.9424 | 13.3867 | 13.6451 | 13.3822 | 13.1977 | NaN | NaN | NaN | 13.6846 | 91.5825 | NaN | NaN | NaN | 3.3595 | NaN | NaN | NaN | NaN | 583.436 | NaN | 16.6924 | NaN | 24.7115
6680.1292 | 13.9052 | 13.7022 | 13.6947 | 13.9519 | 13.4115 | 13.658 | 13.3917 | 13.1991 | NaN | NaN | NaN | 13.4812 | 92.5745 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 600.0182 | NaN | 21.8379 | NaN | 24.6167
6681.1292 | 13.9382 | 13.6625 | 13.69 | 13.9279 | 13.329 | 13.6685 | 13.3957 | 13.1918 | NaN | NaN | NaN | 13.4371 | 92.5713 | NaN | NaN | NaN | -9.5234 | NaN | NaN | NaN | NaN | 605.9629 | NaN | 17.4477 | NaN | 26.3591
6682.1292 | 14.008 | 13.6674 | 13.688 | 13.9283 | 13.2565 | 13.6799 | 13.3843 | 13.1989 | NaN | NaN | NaN | 13.4781 | 103.1772 | NaN | NaN | NaN | 19.417 | NaN | NaN | NaN | NaN | 600.6695 | NaN | 18.823 | NaN | 25.0483
6683.1292 | 13.9204 | 13.6604 | 13.6944 | 13.9246 | 13.4992 | 13.6858 | 13.3699 | 13.1897 | NaN | NaN | NaN | 13.5112 | 93.4858 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 600.0938 | NaN | 20.9291 | NaN | 26.2386
6684.1292 | 13.9507 | 13.6643 | 13.6853 | 13.9406 | 13.4281 | 13.6457 | 13.3847 | 13.1869 | NaN | NaN | NaN | 13.4494 | 94.0413 | NaN | NaN | NaN | -17.8378 | NaN | NaN | NaN | NaN | 602.0142 | NaN | 18.4621 | NaN | 24.3761
6685.1292 | 13.9047 | 13.6762 | 13.6875 | 13.9587 | 13.3862 | 13.7104 | 13.3766 | 13.1852 | NaN | NaN | NaN | 13.4468 | 92.3538 | NaN | NaN | NaN | -3.0837 | NaN | NaN | NaN | NaN | 602.7427 | NaN | 20.4293 | NaN | 25.1736
6686.1292 | 13.9266 | 13.659 | 13.6765 | 13.9583 | 13.4007 | 13.6567 | 13.3709 | 13.1843 | NaN | NaN | NaN | 13.5014 | 93.3468 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 602.3837 | NaN | 16.9129 | NaN | 23.507
6687.1292 | 13.8895 | 13.682 | 13.6756 | 13.9726 | 13.3879 | 13.6482 | 13.374 | 13.1789 | NaN | NaN | NaN | 13.5716 | 92.5973 | NaN | NaN | NaN | 2.9684 | NaN | NaN | NaN | NaN | 603.2005 | NaN | 18.8708 | NaN | 25.4084
6688.1292 | 14.1327 | 13.6515 | 13.6771 | 14.022 | 13.4685 | 13.6463 | 13.3724 | 13.1818 | NaN | NaN | NaN | 13.4233 | 91.091 | NaN | NaN | NaN | 12.9313 | NaN | NaN | NaN | NaN | 603.3722 | NaN | 18.3766 | NaN | 24.7115
6689.1292 | 13.9129 | 13.6672 | 13.6725 | 13.9822 | 13.3944 | 13.7426 | 13.3724 | 13.181 | NaN | NaN | NaN | 13.424 | 94.4888 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 605.1201 | NaN | 19.1399 | NaN | 25.279
6690.1292 | 13.8776 | 13.6891 | 13.6723 | 13.9233 | 13.3688 | 13.6496 | 13.3857 | 13.1812 | NaN | NaN | NaN | 13.4673 | 93.9313 | NaN | NaN | NaN | -2.2699 | NaN | NaN | NaN | NaN | 606.9303 | NaN | 19.1486 | NaN | 24.0833
6691.1292 | 13.9145 | 13.6924 | 13.6715 | 14.0007 | 13.4474 | 13.6433 | 13.3749 | 13.1781 | NaN | NaN | NaN | 13.4401 | 93.8831 | NaN | NaN | NaN | -11.9815 | NaN | NaN | NaN | NaN | 607.4407 | NaN | 19.5551 | NaN | 25.439
6692.1292 | 13.9485 | 13.6587 | 13.6762 | 13.9932 | 13.3863 | 13.6986 | 13.3787 | 13.1773 | NaN | NaN | NaN | 13.5142 | 92.5233 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 606.4155 | NaN | 17.5635 | NaN | 24.1278
6693.1292 | 13.9266 | 13.6581 | 13.6727 | 13.9218 | 13.389 | 13.728 | 13.3666 | 13.1769 | NaN | NaN | NaN | 13.4683 | 91.0658 | NaN | NaN | NaN | 16.6853 | NaN | NaN | NaN | NaN | 605.1618 | NaN | 16.6079 | NaN | 26.4493
6694.1292 | 13.9079 | 13.6467 | 13.6716 | 13.971 | 13.4482 | 13.7052 | 13.3659 | 13.1727 | NaN | NaN | NaN | 13.4478 | 92.2195 | NaN | NaN | NaN | -19.5185 | NaN | NaN | NaN | NaN | 602.7437 | NaN | 17.2169 | NaN | 23.1908
6695.1292 | 14.0554 | 13.6507 | 13.6685 | 13.9297 | 13.3989 | 13.641 | 13.3661 | 13.1731 | NaN | NaN | NaN | 13.6643 | 92.3244 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 602.914 | NaN | 16.2402 | NaN | 26.4862
6696.1292 | 13.9331 | 13.7637 | 13.6735 | 13.9202 | 13.4602 | 13.6289 | 13.3819 | 13.1789 | NaN | NaN | NaN | 13.4786 | 95.5444 | NaN | NaN | NaN | -7.3372 | NaN | NaN | NaN | NaN | 595.2789 | NaN | 15.3743 | NaN | 24.8825
6697.1292 | 13.9171 | 13.6618 | 13.6641 | 13.9632 | 13.4412 | 13.6378 | 13.3517 | 13.1797 | NaN | NaN | NaN | 13.4322 | 94.3648 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 592.5476 | NaN | 16.2299 | NaN | 25.2407
6698.1292 | 13.9307 | 13.6957 | 13.6655 | 13.9444 | 13.2597 | 13.7156 | 13.3682 | 13.1802 | NaN | NaN | NaN | 13.4411 | 93.2998 | NaN | NaN | NaN | 5.8637 | NaN | NaN | NaN | NaN | 602.3045 | NaN | 18.2779 | NaN | 25.605
6699.1292 | 13.9504 | 13.67 | 13.6684 | 14.0397 | 13.3661 | 13.6333 | 13.3594 | 13.1828 | NaN | NaN | NaN | 13.5512 | 93.4041 | NaN | NaN | NaN | -3.8072 | NaN | NaN | NaN | NaN | 606.6122 | NaN | 19.4793 | NaN | 27.2079
6700.1292 | 13.9188 | 13.6704 | 13.6755 | 13.9516 | 13.436 | 13.6321 | 13.3451 | 13.1824 | NaN | NaN | NaN | 13.4482 | 102.2392 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 608.6295 | NaN | 17.4656 | NaN | 25.4664
6701.1292 | 13.9268 | 13.6575 | 13.6733 | 13.9036 | 13.4214 | 13.617 | 13.3431 | 13.1797 | NaN | NaN | NaN | 13.4546 | 100.3308 | NaN | NaN | NaN | 19.1919 | NaN | NaN | NaN | NaN | 609.7039 | NaN | 16.409 | NaN | 25.7709
6702.1292 | 13.909 | 13.6664 | 13.6742 | 13.9788 | 13.4225 | 13.652 | 13.3673 | 13.1812 | NaN | NaN | NaN | 13.5794 | 95.2384 | NaN | NaN | NaN | -15.5603 | NaN | NaN | NaN | NaN | 609.0848 | NaN | 17.9609 | NaN | 25.0218
6703.1292 | 13.985 | 13.7748 | 13.6721 | 13.927 | 13.3539 | 13.6614 | 13.3658 | 13.1694 | NaN | NaN | NaN | 13.4164 | 90.3634 | NaN | NaN | NaN | -19.5581 | NaN | NaN | NaN | NaN | 612.3297 | NaN | 20.1308 | NaN | 24.3498
6704.1292 | 13.9099 | 13.7372 | 13.6712 | 13.9888 | 13.4503 | 13.6507 | 13.3639 | 13.1807 | NaN | NaN | NaN | 13.4353 | 103.0602 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 608.9534 | NaN | 13.6026 | NaN | 22.8443
6705.1292 | 14.1279 | 13.6672 | 13.6716 | 14.0751 | 13.3767 | 13.633 | 13.3464 | 13.1853 | NaN | NaN | NaN | 13.4603 | 93.7624 | NaN | NaN | NaN | 29.7379 | NaN | NaN | NaN | NaN | 608.2854 | NaN | 16.3662 | NaN | 24.5137
6706.1292 | 13.8948 | 13.6806 | 13.6761 | 13.9066 | 13.3781 | 13.6322 | 13.3509 | 13.1791 | NaN | NaN | NaN | 13.4087 | 92.7754 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 611.5808 | NaN | 17.1275 | NaN | 26.1151
6707.1292 | 13.9268 | 13.6656 | 13.6722 | 13.9415 | 13.3148 | 13.6254 | 13.3431 | 13.1835 | NaN | NaN | NaN | 13.4031 | 91.5738 | NaN | NaN | NaN | 24.0006 | NaN | NaN | NaN | NaN | 608.3782 | NaN | 20.6516 | NaN | 25.816
6708.1292 | 13.9135 | 13.6676 | 13.6753 | 13.9633 | 13.4561 | 13.6243 | 13.3492 | 13.18 | NaN | NaN | NaN | 13.4215 | 93.4971 | NaN | NaN | NaN | -11.3903 | NaN | NaN | NaN | NaN | 612.3203 | NaN | 18.0332 | NaN | 21.1889
6709.1292 | 13.8974 | 13.6562 | 13.6761 | 13.8978 | 13.3483 | 13.61 | 13.3444 | 13.182 | NaN | NaN | NaN | 13.4266 | 93.4585 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 611.8298 | NaN | 17.3977 | NaN | 23.7407
6710.1292 | 13.9177 | 13.692 | 13.6728 | 13.9595 | 13.3917 | 13.6198 | 13.3464 | 13.1846 | NaN | NaN | NaN | 13.4092 | 93.4675 | NaN | NaN | NaN | 1.4134 | NaN | NaN | NaN | NaN | 606.4154 | NaN | 21.9739 | NaN | 24.6651
6711.1292 | 13.8988 | 13.737 | 13.6783 | 13.9112 | 13.4569 | 13.6346 | 13.3707 | 13.1868 | NaN | NaN | NaN | 13.4149 | 90.6074 | NaN | NaN | NaN | 8.5375 | NaN | NaN | NaN | NaN | 612.6104 | NaN | 17.5237 | NaN | 24.0351
6712.1292 | 13.9386 | 13.7601 | 13.6761 | 13.9726 | 13.4403 | 13.6343 | 13.374 | 13.1812 | NaN | NaN | NaN | 13.3977 | 92.0092 | NaN | NaN | NaN | -9.9265 | NaN | NaN | NaN | NaN | 609.6188 | NaN | 19.2432 | NaN | 24.9271
6713.1292 | 13.9144 | 13.7102 | 13.6784 | 13.994 | 13.343 | 13.6278 | 13.3546 | 13.1876 | NaN | NaN | NaN | 13.3826 | 91.6719 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 609.9039 | NaN | 17.8208 | NaN | 22.8097
6714.1292 | 13.9024 | 13.7225 | 13.6847 | 13.9319 | 13.2689 | 13.6413 | 13.3614 | 13.1796 | NaN | NaN | NaN | 13.5561 | 96.264 | NaN | NaN | NaN | 22.9699 | NaN | NaN | NaN | NaN | 607.4911 | NaN | 21.0563 | NaN | 24.9971
6715.1292 | 13.8893 | 13.6713 | 13.6752 | 13.9377 | 13.3066 | 13.6261 | 13.3481 | 13.1801 | NaN | NaN | NaN | 13.4574 | 97.3637 | NaN | NaN | NaN | -6.4922 | NaN | NaN | NaN | NaN | 610.1075 | NaN | 16.6794 | NaN | 22.5419
6716.1292 | 13.9206 | 13.6795 | 13.6738 | 13.9465 | 13.4415 | 13.608 | 13.3486 | 13.1847 | NaN | NaN | NaN | 13.4124 | 93.7218 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 612.13 | NaN | 17.3683 | NaN | 25.9552
6717.1292 | 13.8971 | 13.7863 | 13.6813 | 13.9574 | 13.4644 | 13.7204 | 13.3702 | 13.1791 | NaN | NaN | NaN | 13.5654 | 93.6443 | NaN | NaN | NaN | 8.4224 | NaN | NaN | NaN | NaN | 610.7754 | NaN | 17.7092 | NaN | 25.2115
6718.1292 | 13.8759 | 13.7699 | 13.6825 | 13.8885 | 13.3118 | 13.6088 | 13.3592 | 13.1795 | NaN | NaN | NaN | 13.4127 | 93.0734 | NaN | NaN | NaN | -11.8842 | NaN | NaN | NaN | NaN | 613.0434 | NaN | 21.4026 | NaN | 25.3966
6719.1292 | 14.0066 | 13.6696 | 13.6813 | 13.9478 | 13.459 | 13.621 | 13.3516 | 13.1755 | NaN | NaN | NaN | 13.3856 | 93.1738 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 616.5464 | NaN | 18.0349 | NaN | 25.9438
6720.1292 | 13.901 | 13.6793 | 13.6742 | 13.9543 | 13.3755 | 13.6213 | 13.3418 | 13.1743 | NaN | NaN | NaN | 13.4295 | 105.3371 | NaN | NaN | NaN | 9.2695 | NaN | NaN | NaN | NaN | 615.0533 | NaN | 16.8649 | NaN | 24.0478
6721.1292 | 13.8874 | 13.6701 | 13.6768 | 13.9677 | 13.37 | 13.5996 | 13.3369 | 13.1703 | NaN | NaN | NaN | 13.4305 | 92.2023 | NaN | NaN | NaN | -15.3063 | NaN | NaN | NaN | NaN | 613.6537 | NaN | 21.1999 | NaN | 25.3839
6722.1292 | 13.8931 | 13.6715 | 13.6792 | 13.9517 | 13.3703 | 13.6258 | 13.3557 | 13.1706 | NaN | NaN | NaN | 13.4274 | 96.9448 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -13.965 | 615.4245 | NaN | 17.3219 | NaN | 26.8539
6723.1292 | 13.8779 | 13.6758 | 13.6838 | 13.9429 | 13.3546 | 13.7572 | 13.3578 | 13.1746 | NaN | NaN | NaN | 13.4255 | 92.4558 | NaN | NaN | NaN | 6.9863 | NaN | NaN | NaN | NaN | 614.0698 | NaN | 16.4697 | NaN | 24.583
6724.1292 | 13.8957 | 13.7284 | 13.6825 | 13.9121 | 13.3628 | 13.6105 | 13.3626 | 13.1695 | NaN | NaN | NaN | 13.4235 | 95.4748 | NaN | NaN | NaN | -15.3376 | NaN | NaN | NaN | NaN | 615.7442 | NaN | 18.5016 | NaN | 26.5352
6725.1292 | 13.8453 | 13.8018 | 13.6808 | 13.9556 | 13.3313 | 13.7972 | 13.362 | 13.174 | NaN | NaN | NaN | 13.463 | 90.8704 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 616.5306 | NaN | 19.2244 | NaN | 23.8759
6726.1292 | 13.8874 | 13.6577 | 13.6747 | 13.9086 | 13.2279 | 13.7069 | 13.3579 | 13.1694 | NaN | NaN | NaN | 13.4476 | 91.2214 | NaN | NaN | NaN | 0.0096 | NaN | NaN | NaN | NaN | 615.7427 | NaN | 17.5996 | NaN | 25.3502
6727.1292 | 13.8638 | 13.6503 | 13.6781 | 13.9296 | 13.2842 | 13.809 | 13.3493 | 13.1699 | NaN | NaN | NaN | 13.4512 | 92.1828 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 616.7617 | NaN | 16.9242 | NaN | 26.084
6728.1292 | 13.9187 | 13.7264 | 13.6684 | 13.9134 | 13.312 | 13.6588 | 13.3584 | 13.1685 | NaN | NaN | NaN | 13.4148 | 92.0236 | NaN | NaN | NaN | 26.4595 | NaN | NaN | NaN | NaN | 614.0344 | NaN | 14.9309 | NaN | 25.9102
6729.1292 | 13.8486 | 13.6472 | 13.6633 | 13.962 | 13.3553 | 13.6306 | 13.3285 | 13.1656 | NaN | NaN | NaN | 13.4109 | 93.5467 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 612.0235 | NaN | 17.7565 | NaN | 26.8053
6730.1292 | 13.892 | 13.6611 | 13.6609 | 13.9596 | 13.3021 | 13.6218 | 13.3266 | 13.1634 | NaN | NaN | NaN | 13.4684 | 96.2207 | NaN | NaN | NaN | -18.5041 | NaN | NaN | NaN | NaN | 611.8432 | NaN | 16.7213 | NaN | 26.7393
6731.1292 | 13.882 | 13.6708 | 13.6549 | 13.9508 | 13.315 | 13.6006 | 13.3252 | 13.1634 | NaN | NaN | NaN | 13.426 | 93.4457 | NaN | NaN | NaN | -19.4635 | NaN | NaN | NaN | NaN | 615.061 | NaN | 16.4828 | NaN | 22.9646
6732.1292 | 13.9055 | 13.7103 | 13.6542 | 13.9569 | 13.4464 | 13.6229 | 13.3492 | 13.1703 | NaN | NaN | NaN | 13.4433 | 93.2187 | NaN | NaN | NaN | -19.7661 | NaN | NaN | NaN | NaN | 619.5525 | NaN | 21.1601 | NaN | 24.4329
6733.1292 | 13.8794 | 13.6847 | 13.65 | 13.936 | 13.4123 | 13.789 | 13.3546 | 13.1692 | NaN | NaN | NaN | 13.4174 | 94.5043 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 617.2703 | NaN | 16.7705 | NaN | 23.9881
6734.1292 | 13.905 | 13.6371 | 13.6565 | 13.9514 | 13.3979 | 13.5966 | 13.3299 | 13.1748 | NaN | NaN | NaN | 13.4592 | 101.0036 | NaN | NaN | NaN | -7.7943 | NaN | NaN | NaN | NaN | 621.5616 | NaN | 16.6747 | NaN | 23.8028
6735.1292 | 13.8589 | 13.6419 | 13.6532 | 13.9135 | 13.292 | 13.614 | 13.332 | 13.1669 | NaN | NaN | NaN | 13.5155 | 92.9142 | NaN | NaN | NaN | -12.5812 | NaN | NaN | NaN | NaN | 618.9268 | NaN | 18.2889 | NaN | 25.6312
6736.1292 | 13.9071 | 13.6462 | 13.6451 | 13.9569 | 13.39 | 13.6215 | 13.3358 | 13.171 | NaN | NaN | NaN | 13.4862 | 91.8302 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 615.4523 | NaN | 18.9323 | NaN | 26.0849
6737.1292 | 14.0687 | 13.6339 | 13.6486 | 13.9553 | 13.3429 | 13.6934 | 13.3233 | 13.1702 | NaN | NaN | NaN | 13.4081 | 93.2285 | NaN | NaN | NaN | -4.357 | NaN | NaN | NaN | NaN | 616.5411 | NaN | 15.638 | NaN | 24.0153
6738.1292 | 13.9076 | 13.6884 | 13.6535 | 13.93 | 13.3078 | 13.6361 | 13.3554 | 13.1672 | NaN | NaN | NaN | 13.4035 | 92.8726 | NaN | NaN | NaN | -19.6957 | NaN | NaN | NaN | NaN | 615.2115 | NaN | 17.3661 | NaN | 26.6914
6739.1292 | 13.9149 | 13.6211 | 13.6495 | 13.9473 | 13.3828 | 13.6781 | 13.3381 | 13.1656 | NaN | NaN | NaN | 13.4348 | 93.3521 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 607.4052 | NaN | 16.6523 | NaN | 25.9123
6740.1292 | 13.8912 | 13.6181 | 13.6487 | 13.9054 | 13.4485 | 13.6086 | 13.332 | 13.1665 | NaN | NaN | NaN | 13.4414 | 95.4119 | NaN | NaN | NaN | -15.8273 | NaN | NaN | NaN | NaN | 609.8635 | NaN | 16.5863 | NaN | 23.5846
6741.1292 | 13.916 | 13.6052 | 13.6451 | 13.9119 | 13.4487 | 13.5924 | 13.3254 | 13.1619 | NaN | NaN | NaN | 13.4013 | 94.2295 | NaN | NaN | NaN | -8.2837 | NaN | NaN | NaN | NaN | 604.5831 | NaN | 16.9936 | NaN | 24.1124
6742.1292 | 13.9085 | 13.6306 | 13.649 | 13.938 | 13.3003 | 13.6064 | 13.3267 | 13.154 | NaN | NaN | NaN | 13.4139 | 96.707 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 606.2106 | NaN | 15.6328 | NaN | 26.2146
6743.1292 | 13.8993 | 13.6393 | 13.6556 | 13.9145 | 13.3238 | 13.6132 | 13.3299 | 13.166 | NaN | NaN | NaN | 13.4183 | 102.6736 | NaN | NaN | NaN | -8.1554 | NaN | NaN | NaN | NaN | 605.5185 | NaN | 16.1117 | NaN | 26.2447
6744.1292 | 13.9841 | 13.623 | 13.6579 | 13.8925 | 13.333 | 13.6097 | 13.3308 | 13.1604 | NaN | NaN | NaN | 13.4735 | 90.3357 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 605.5541 | NaN | 18.1817 | NaN | 26.826
6745.1292 | 13.8988 | 13.6266 | 13.6522 | 13.8968 | 13.3616 | 13.6148 | 13.3406 | 13.1621 | NaN | NaN | NaN | 13.4139 | 93.787 | NaN | NaN | NaN | -1.0785 | NaN | NaN | NaN | NaN | 609.1104 | NaN | 15.8226 | NaN | 26.3609
6746.1292 | 13.8706 | 13.6564 | 13.657 | 13.9139 | 13.415 | 13.7321 | 13.3451 | 13.1614 | NaN | NaN | NaN | 13.4275 | 97.9929 | NaN | NaN | NaN | -11.3595 | NaN | NaN | NaN | NaN | 606.5819 | NaN | 17.8468 | NaN | 25.6782
6747.1292 | 13.9163 | 13.6286 | 13.6492 | 13.9298 | 13.376 | 13.6113 | 13.3188 | 13.1634 | NaN | NaN | NaN | 13.4713 | 94.9522 | NaN | NaN | NaN | -18.82 | NaN | NaN | NaN | NaN | 605.5664 | NaN | 16.3031 | NaN | 27.4001
6748.1292 | 13.8986 | 13.5961 | 13.6498 | 13.9247 | 13.417 | 13.8073 | 13.3327 | 13.1548 | NaN | NaN | NaN | 13.4252 | 91.7983 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 602.5913 | NaN | 16.1483 | NaN | 23.2714
6749.1292 | 13.8869 | 13.6134 | 13.6528 | 13.8804 | 13.3903 | 13.5989 | 13.3276 | 13.1608 | NaN | NaN | NaN | 13.4419 | 95.0469 | NaN | NaN | NaN | -13.2802 | NaN | NaN | NaN | NaN | 599.0627 | NaN | 16.5904 | NaN | 24.1663
6750.1292 | 13.9229 | 13.5983 | 13.6594 | 13.933 | 13.2908 | 13.5948 | 13.3189 | 13.1636 | NaN | NaN | NaN | 13.4211 | 92.6426 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 594.9226 | NaN | 17.0257 | NaN | 25.1819
6751.1292 | 13.9045 | 13.6206 | 13.6524 | 13.9216 | 13.4191 | 13.6353 | 13.326 | 13.1605 | NaN | NaN | NaN | 13.397 | 91.2671 | NaN | NaN | NaN | 6.4437 | NaN | NaN | NaN | NaN | 601.8136 | NaN | 17.9771 | NaN | 25.2941
6752.1292 | 13.8477 | 13.6151 | 13.6531 | 13.9633 | 13.4131 | 13.6117 | 13.3182 | 13.1535 | NaN | NaN | NaN | 13.4008 | 92.9915 | NaN | NaN | NaN | -15.4565 | NaN | NaN | NaN | NaN | 600.944 | NaN | 16.8629 | NaN | 23.961
6753.1292 | 13.9023 | 13.6101 | 13.6539 | 13.9061 | 13.2831 | 13.6813 | 13.3198 | 13.1571 | NaN | NaN | NaN | 13.4068 | 91.3952 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 598.3702 | NaN | 17.4868 | NaN | 24.2978
6754.1292 | 13.905 | 13.6194 | 13.6548 | 13.9444 | 13.3676 | 13.6028 | 13.3337 | 13.1619 | NaN | NaN | NaN | 13.4249 | 91.9526 | NaN | NaN | NaN | 14.2468 | NaN | NaN | NaN | NaN | 597.2309 | NaN | 17.8727 | NaN | 23.603
6755.1292 | 13.8939 | 13.6394 | 13.6521 | 13.879 | 13.3307 | 13.6717 | 13.3338 | 13.1627 | NaN | NaN | NaN | 13.4231 | 92.619 | NaN | NaN | NaN | -5.4807 | NaN | NaN | NaN | NaN | 594.8696 | NaN | 15.6728 | NaN | 26.2886
6756.1292 | 13.9265 | 13.6124 | 13.6544 | 13.9126 | 13.3135 | 13.7045 | 13.3189 | 13.167 | NaN | NaN | NaN | 13.4168 | 92.9789 | NaN | NaN | NaN | -17.44 | NaN | NaN | NaN | NaN | 600.4409 | NaN | 16.062 | NaN | 23.0313
6757.1292 | 13.9007 | 13.631 | 13.6575 | 13.9119 | 13.3576 | 13.6279 | 13.3311 | 13.1641 | NaN | NaN | NaN | 13.414 | 93.3391 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 599.1289 | NaN | 18.2759 | NaN | 24.2176
6758.1292 | 13.8599 | 13.6402 | 13.6536 | 13.9251 | 13.3518 | 13.6085 | 13.326 | 13.1707 | NaN | NaN | NaN | 13.4337 | 96.1153 | NaN | NaN | NaN | 28.0065 | NaN | NaN | NaN | NaN | 597.2002 | NaN | 17.3791 | NaN | 23.9253
6759.1292 | 14.0198 | 13.6155 | 13.6564 | 13.9577 | 13.351 | 13.6421 | 13.3226 | 13.1685 | NaN | NaN | NaN | 13.3928 | 94.5608 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 594.6016 | NaN | 17.7922 | NaN | 22.7412
6760.1292 | 13.8684 | 13.5906 | 13.66 | 13.8672 | 13.2745 | 13.6183 | 13.3203 | 13.1728 | NaN | NaN | NaN | 13.6573 | 93.4656 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 596.9938 | NaN | 18.2225 | NaN | 25.6047
6761.1292 | 13.8691 | 13.605 | 13.6581 | 13.9069 | 13.3687 | 13.6099 | 13.3238 | 13.1706 | NaN | NaN | NaN | 13.4005 | 91.1587 | NaN | NaN | NaN | 27.2793 | NaN | NaN | NaN | NaN | 591.2954 | NaN | 16.2503 | NaN | 24.7437
6762.1292 | 13.8908 | 13.6632 | 13.6652 | 13.9491 | 13.3019 | 13.6165 | 13.3395 | 13.1689 | NaN | NaN | NaN | 13.4903 | 93.3111 | NaN | NaN | NaN | -19.2309 | NaN | NaN | NaN | NaN | 591.6277 | NaN | 16.4621 | NaN | 21.9938
6763.1292 | 13.8604 | 13.5837 | 13.6577 | 14.199 | 13.448 | 13.6384 | 13.3242 | 13.1641 | NaN | NaN | NaN | 13.3996 | 92.6224 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 593.7648 | NaN | 18.35 | NaN | 25.2882
6764.1292 | 13.8987 | 13.678 | 13.6566 | 13.9119 | 13.2914 | 13.6178 | 13.3476 | 13.1697 | NaN | NaN | NaN | 13.4336 | 91.4658 | NaN | NaN | NaN | -7.9753 | NaN | NaN | NaN | NaN | 598.0382 | NaN | 16.3122 | NaN | 25.0503
6765.1292 | 13.8628 | 13.6121 | 13.6639 | 13.9345 | 13.3324 | 13.6406 | 13.3383 | 13.1651 | NaN | NaN | NaN | 13.4075 | 92.3436 | NaN | NaN | NaN | -17.2858 | NaN | NaN | NaN | NaN | 595.7462 | NaN | 18.3199 | NaN | 25.6681
6766.1292 | 13.9041 | 13.6023 | 13.6553 | 13.9829 | 13.3035 | 13.6084 | 13.3263 | 13.1617 | NaN | NaN | NaN | 13.4302 | 92.9131 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 595.0401 | NaN | 18.4493 | NaN | 25.228
6767.1292 | 13.8769 | 13.5701 | 13.6584 | 13.9033 | 13.2927 | 13.6165 | 13.3342 | 13.1619 | NaN | NaN | NaN | 13.4793 | 90.8684 | NaN | NaN | NaN | 30.1324 | NaN | NaN | NaN | NaN | 599.5831 | NaN | 18.1342 | NaN | 20.7612
6768.1292 | 13.9074 | 13.5967 | 13.6537 | 13.9462 | 13.2604 | 13.6204 | 13.3278 | 13.1582 | NaN | NaN | NaN | 13.4104 | 90.8279 | NaN | NaN | NaN | -14.9813 | NaN | NaN | NaN | NaN | 600.8889 | NaN | 15.8244 | NaN | 25.9254
6769.1292 | 13.8866 | 13.5655 | 13.6543 | 13.8798 | 13.271 | 13.6703 | 13.327 | 13.1466 | NaN | NaN | NaN | 13.458 | 90.5052 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 598.2543 | NaN | 16.1123 | NaN | 24.8099
6770.1292 | 13.8711 | 13.5766 | 13.6529 | 13.9349 | 13.3743 | 13.5995 | 13.332 | 13.1512 | NaN | NaN | NaN | 13.4972 | 91.1726 | NaN | NaN | NaN | 27.2347 | NaN | NaN | NaN | NaN | 597.1327 | NaN | 16.1538 | NaN | 24.6332
6771.1292 | 13.9901 | 13.5713 | 13.6522 | 13.9614 | 13.4025 | 13.5907 | 13.318 | 13.1526 | NaN | NaN | NaN | 13.4435 | 92.9361 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 600.9849 | NaN | 19.1995 | NaN | 27.4733
6772.1292 | 13.876 | 13.6527 | 13.6543 | 13.9301 | 13.2981 | 13.7265 | 13.3531 | 13.1542 | NaN | NaN | NaN | 13.4265 | 95.9661 | NaN | NaN | NaN | 6.0056 | NaN | NaN | NaN | NaN | 605.2906 | NaN | 18.0098 | NaN | 27.3711
6773.1292 | 13.8832 | 13.5624 | 13.6524 | 13.9313 | 13.3761 | 13.6061 | 13.3279 | 13.1556 | NaN | NaN | NaN | 13.4663 | 96.6271 | NaN | NaN | NaN | -15.7891 | NaN | NaN | NaN | NaN | 600.4493 | NaN | 16.2485 | NaN | 26.534
6774.1292 | 13.8547 | 13.5789 | 13.6539 | 13.9316 | 13.464 | 13.6174 | 13.332 | 13.1533 | NaN | NaN | NaN | 13.4545 | 93.0949 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 599.6779 | NaN | 16.491 | NaN | 25.6971
6775.1292 | 13.9032 | 13.5838 | 13.6542 | 13.9543 | 13.4154 | 13.5987 | 13.3319 | 13.1505 | NaN | NaN | NaN | 13.4083 | 91.2228 | NaN | NaN | NaN | 21.2936 | NaN | NaN | NaN | NaN | 601.5476 | NaN | 15.9418 | NaN | 24.0795
6776.1292 | 13.8861 | 13.6459 | 13.6586 | 13.9625 | 13.3258 | 13.6462 | 13.3468 | 13.155 | NaN | NaN | NaN | 13.4377 | 90.0608 | NaN | NaN | NaN | -1.6226 | NaN | NaN | NaN | NaN | 603.7114 | NaN | 16.0414 | NaN | 24.9866
6777.1292 | 13.8829 | 13.5645 | 13.6535 | 13.9221 | 13.3045 | 13.6242 | 13.3328 | 13.1538 | NaN | NaN | NaN | 13.4197 | 92.6429 | NaN | NaN | NaN | -17.826 | NaN | NaN | NaN | NaN | 605.0672 | NaN | 16.9182 | NaN | 24.8435
6778.1292 | 14.0048 | 13.5758 | 13.655 | 14.0471 | 13.2919 | 13.5999 | 13.3238 | 13.1518 | NaN | NaN | NaN | 13.432 | 91.786 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 605.4738 | NaN | 16.0354 | NaN | 25.918
6779.1292 | 13.8999 | 13.5812 | 13.6585 | 13.884 | 13.4939 | 13.6719 | 13.3324 | 13.1541 | NaN | NaN | NaN | 13.4391 | 94.3445 | NaN | NaN | NaN | 7.5714 | NaN | NaN | NaN | NaN | 604.5304 | NaN | 16.6789 | NaN | 26.1791
6780.1292 | 13.8999 | 13.6151 | 13.6552 | 13.9405 | 13.3403 | 13.6724 | 13.3488 | 13.1487 | NaN | NaN | NaN | 13.4312 | 96.9438 | NaN | NaN | NaN | 30.907 | NaN | NaN | NaN | NaN | 602.0334 | NaN | 15.8352 | NaN | 25.294
6781.1292 | 13.88 | 13.5826 | 13.6582 | 13.9088 | 13.3817 | 13.6594 | 13.3483 | 13.1553 | NaN | NaN | NaN | 13.4331 | 94.8186 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 604.5066 | NaN | 18.8083 | NaN | 26.3173
6782.1292 | 13.8539 | 13.613 | 13.6574 | 13.9008 | 13.3881 | 13.6088 | 13.353 | 13.153 | NaN | NaN | NaN | 13.5892 | 93.3722 | NaN | NaN | NaN | 5.2248 | NaN | NaN | NaN | NaN | 604.6775 | NaN | 17.454 | NaN | 26.3918
6783.1292 | 13.8794 | 13.5782 | 13.6598 | 13.9561 | 13.2154 | 13.6527 | 13.3544 | 13.1628 | NaN | NaN | NaN | 13.4926 | 94.5125 | NaN | NaN | NaN | -19.0493 | NaN | NaN | NaN | NaN | 604.4695 | NaN | 17.2266 | NaN | 24.6974
6784.1292 | 13.8536 | 13.5791 | 13.6593 | 13.8941 | 13.2378 | 13.6009 | 13.3326 | 13.1616 | NaN | NaN | NaN | 13.436 | 102.8813 | NaN | NaN | NaN | -11.599 | NaN | NaN | NaN | NaN | 606.6393 | NaN | 16.8279 | NaN | 26.0565
6785.1292 | 13.8889 | 13.6034 | 13.6573 | 13.916 | 13.4607 | 13.5865 | 13.3352 | 13.158 | NaN | NaN | NaN | 13.4128 | 93.3284 | NaN | NaN | NaN | -15.3906 | NaN | NaN | NaN | NaN | 600.7225 | NaN | 16.1358 | NaN | 24.6307
6786.1292 | 13.9141 | 13.5807 | 13.6582 | 13.9367 | 13.4139 | 13.6559 | 13.3354 | 13.1632 | NaN | NaN | NaN | 13.4123 | 94.9967 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 599.2191 | NaN | 17.772 | NaN | 25.8895
6787.1292 | 13.9045 | 13.5782 | 13.6603 | 13.9464 | 13.4973 | 13.6017 | 13.338 | 13.1628 | NaN | NaN | NaN | 13.4313 | 93.9797 | NaN | NaN | NaN | 11.7732 | NaN | NaN | NaN | NaN | 601.8235 | NaN | 16.6107 | NaN | 26.5607
6788.1292 | 13.8872 | 13.6341 | 13.6578 | 13.9586 | 13.4075 | 13.5903 | 13.339 | 13.1639 | NaN | NaN | NaN | 13.5085 | 94.0346 | NaN | NaN | NaN | -16.7898 | NaN | NaN | NaN | NaN | 601.2116 | NaN | 17.6325 | NaN | 24.7793
6789.1292 | 13.865 | 13.6839 | 13.6616 | 13.935 | 13.3584 | 13.6514 | 13.3562 | 13.1637 | NaN | NaN | NaN | 13.714 | 95.8223 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 603.1604 | NaN | 14.931 | NaN | 25.2047
6790.1292 | 13.8532 | 13.592 | 13.6609 | 13.958 | 13.3785 | 13.5827 | 13.326 | 13.1685 | NaN | NaN | NaN | 13.4334 | 92.7187 | NaN | NaN | NaN | 15.8481 | NaN | NaN | NaN | NaN | 601.5932 | NaN | 17.3733 | NaN | 26.47
6791.1292 | 13.8978 | 13.6206 | 13.6577 | 13.9676 | 13.3867 | 13.6129 | 13.3444 | 13.1635 | NaN | NaN | NaN | 13.4797 | 92.3888 | NaN | NaN | NaN | -18.1392 | NaN | NaN | NaN | NaN | 603.3378 | NaN | 15.6924 | NaN | 25.1269
6792.1292 | 13.9859 | 13.7435 | 13.6632 | 13.9176 | 13.4104 | 13.6707 | 13.3643 | 13.1639 | NaN | NaN | NaN | 13.4488 | 95.1662 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 604.8683 | NaN | 16.8913 | NaN | 22.8235
6793.1292 | 13.9084 | 13.5935 | 13.6589 | 13.9247 | 13.2978 | 13.6638 | 13.3342 | 13.1667 | NaN | NaN | NaN | 13.3859 | 96.3474 | NaN | NaN | NaN | -5.1676 | NaN | NaN | NaN | NaN | 604.6242 | NaN | 17.5723 | NaN | 26.4754
6794.1292 | 13.9429 | 13.6021 | 13.6567 | 13.9263 | 13.4256 | 13.58 | 13.3203 | 13.1664 | NaN | NaN | NaN | 13.4559 | 95.3668 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 601.9346 | NaN | 16.5132 | NaN | 25.4282
6795.1292 | 13.8654 | 13.6325 | 13.6657 | 13.9101 | 13.3139 | 13.5926 | 13.3227 | 13.1645 | NaN | NaN | NaN | 13.4365 | 99.9609 | NaN | NaN | NaN | 8.3927 | NaN | NaN | NaN | NaN | 603.2202 | NaN | 16.4094 | NaN | 26.5104
6796.1292 | 13.9606 | 13.621 | 13.6547 | 13.9283 | 13.3171 | 13.6175 | 13.3378 | 13.1663 | NaN | NaN | NaN | 13.4324 | 91.2748 | NaN | NaN | NaN | 5.4799 | NaN | NaN | NaN | NaN | 601.3892 | NaN | 16.815 | NaN | 23.8918
6797.1292 | 13.8607 | 13.608 | 13.6572 | 13.9159 | 13.2613 | 13.5989 | 13.3247 | 13.1677 | NaN | NaN | NaN | 13.3861 | 95.9997 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 598.0787 | NaN | 17.25 | NaN | 26.5767
6798.1292 | 13.9098 | 13.6235 | 13.6551 | 13.9128 | 13.3571 | 13.6105 | 13.3263 | 13.1705 | NaN | NaN | NaN | 13.4068 | 91.8931 | NaN | NaN | NaN | 9.4012 | NaN | NaN | NaN | NaN | 595.8502 | NaN | 16.3792 | NaN | 25.5788
6799.1292 | 13.9079 | 13.6379 | 13.6592 | 13.9536 | 13.3224 | 13.6347 | 13.3225 | 13.161 | NaN | NaN | NaN | 13.4018 | 101.5708 | NaN | NaN | NaN | -19.9255 | NaN | NaN | NaN | NaN | 586.72 | NaN | 16.102 | NaN | 25.1159
6800.1292 | 13.9309 | 13.5915 | 13.664 | 13.9112 | 13.2664 | 13.6106 | 13.3178 | 13.1635 | NaN | NaN | NaN | 13.4429 | 92.1297 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 581.6274 | NaN | 18.6573 | NaN | 26.8181
6801.1292 | 13.9249 | 13.6238 | 13.6613 | 13.8752 | 13.3508 | 13.6809 | 13.3307 | 13.1694 | NaN | NaN | NaN | 13.4126 | 94.2137 | NaN | NaN | NaN | -14.4604 | NaN | NaN | NaN | NaN | 583.0949 | NaN | 16.6553 | NaN | 24.2481
6802.1292 | 14.0161 | 13.5954 | 13.661 | 13.9428 | 13.2679 | 13.6055 | 13.3439 | 13.1709 | NaN | NaN | NaN | 13.437 | 93.3828 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 591.1847 | NaN | 16.8622 | NaN | 24.1329
6803.1292 | 13.9653 | 13.7033 | 13.6644 | 13.9142 | 13.3612 | 13.6191 | 13.3527 | 13.1769 | NaN | NaN | NaN | 13.428 | 92.6848 | NaN | NaN | NaN | 31.1139 | NaN | NaN | NaN | NaN | 600.1856 | NaN | 14.5864 | NaN | 26.2582
6804.1292 | 13.9293 | 13.6202 | 13.6648 | 13.9099 | 13.3948 | 13.6136 | 13.3406 | 13.1776 | NaN | NaN | NaN | 13.4149 | 99.0845 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 602.5065 | NaN | 16.453 | NaN | 24.2114
6805.1292 | 13.9309 | 13.6117 | 13.6542 | 13.9615 | 13.404 | 13.6223 | 13.3307 | 13.1716 | NaN | NaN | NaN | 13.4873 | 94.7238 | NaN | NaN | NaN | 13.9281 | NaN | NaN | NaN | NaN | 602.0909 | NaN | 16.0899 | NaN | 26.8252
6806.1292 | 13.9309 | 13.5815 | 13.6602 | 13.9449 | 13.3196 | 13.6188 | 13.3231 | 13.1642 | NaN | NaN | NaN | 13.4143 | 92.5229 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 601.3233 | NaN | 16.2913 | NaN | 24.5632
6807.1292 | 13.9172 | 13.5775 | 13.6618 | 13.8971 | 13.2761 | 13.6134 | 13.3313 | 13.1724 | NaN | NaN | NaN | 13.5122 | 95.8195 | NaN | NaN | NaN | -5.5292 | NaN | NaN | NaN | NaN | 603.1862 | NaN | 17.9044 | NaN | 23.9388
6808.1292 | 13.9105 | 13.6137 | 13.6534 | 13.9347 | 13.4265 | 13.6005 | 13.3263 | 13.1719 | NaN | NaN | NaN | 13.3829 | 92.1542 | NaN | NaN | NaN | -14.9844 | NaN | NaN | NaN | NaN | 602.5834 | NaN | 17.0245 | NaN | 25.3689
6809.1292 | 13.9107 | 13.6436 | 13.658 | 13.9767 | 13.376 | 13.6432 | 13.3476 | 13.1729 | NaN | NaN | NaN | 13.408 | 92.9927 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 603.7142 | NaN | 18.1979 | NaN | 26.9533
6810.1292 | 13.9458 | 13.5928 | 13.6484 | 13.939 | 13.2813 | 13.6184 | 13.3234 | 13.1731 | NaN | NaN | NaN | 13.3863 | 93.0965 | NaN | NaN | NaN | -0.9176 | NaN | NaN | NaN | NaN | 601.2673 | NaN | 15.8384 | NaN | 22.5714
6811.1292 | 13.9498 | 13.6552 | 13.6543 | 13.9461 | 13.4315 | 13.6296 | 13.3501 | 13.1752 | NaN | NaN | NaN | 13.3965 | 92.6901 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 604.4931 | NaN | 17.4787 | NaN | 21.7935
6812.1292 | 14.0091 | 13.6613 | 13.6562 | 13.9396 | 13.3911 | 13.6133 | 13.3315 | 13.1759 | NaN | NaN | NaN | 13.3921 | 93.1912 | NaN | NaN | NaN | -2.0973 | NaN | NaN | NaN | NaN | 603.5348 | NaN | 15.8107 | NaN | 26.7856
6813.1292 | 13.9176 | 13.6219 | 13.6453 | 13.9261 | 13.3133 | 13.605 | 13.3394 | 13.1743 | NaN | NaN | NaN | 13.3667 | 94.5114 | NaN | NaN | NaN | -12.1179 | NaN | NaN | NaN | NaN | 607.8507 | NaN | 15.7322 | NaN | 22.9163
6814.1292 | 13.9143 | 13.6705 | 13.6522 | 13.8825 | 13.3636 | 13.6342 | 13.3437 | 13.1724 | NaN | NaN | NaN | 13.4567 | 93.0563 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 607.0727 | NaN | 17.0455 | NaN | 24.6835
6815.1292 | 13.9121 | 13.5975 | 13.6479 | 13.9187 | 13.3762 | 13.6913 | 13.3353 | 13.1793 | NaN | NaN | NaN | 13.4707 | 92.0985 | NaN | NaN | NaN | -5.0535 | NaN | NaN | NaN | NaN | 606.164 | NaN | 17.5508 | NaN | 25.8092
6816.1292 | 13.9559 | 13.6179 | 13.6566 | 13.9558 | 13.3427 | 13.722 | 13.3238 | 13.1746 | NaN | NaN | NaN | 13.4682 | 93.8309 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 608.3429 | NaN | 17.3811 | NaN | 25.4928
6817.1292 | 13.9281 | 13.6292 | 13.6529 | 13.8973 | 13.277 | 13.6243 | 13.3308 | 13.1683 | NaN | NaN | NaN | 13.4173 | 93.7845 | NaN | NaN | NaN | 30.1392 | NaN | NaN | NaN | NaN | 599.4135 | NaN | 17.5427 | NaN | 25.6674
6818.1292 | 13.9049 | 13.6606 | 13.6595 | 13.9441 | 13.2967 | 13.6438 | 13.3536 | 13.1632 | NaN | NaN | NaN | 13.3797 | 92.8881 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 600.0253 | NaN | 18.429 | NaN | 26.2702
6819.1292 | 13.9771 | 13.6701 | 13.6585 | 13.9024 | 13.2597 | 13.6431 | 13.3472 | 13.1678 | NaN | NaN | NaN | 13.3886 | 96.7308 | NaN | NaN | NaN | -19.6842 | NaN | NaN | NaN | NaN | 603.7915 | NaN | 17.7029 | NaN | 26.5924
6820.1292 | 13.9884 | 13.6867 | 13.6529 | 13.9488 | 13.386 | 13.6845 | 13.343 | 13.1638 | NaN | NaN | NaN | 13.3796 | 96.1269 | NaN | NaN | NaN | -1.2452 | NaN | NaN | NaN | NaN | 606.6057 | NaN | 17.4367 | NaN | 26.5682
6821.1292 | 13.9361 | 13.5914 | 13.652 | 13.9493 | 13.3104 | 13.6402 | 13.3206 | 13.1627 | NaN | NaN | NaN | 13.7269 | 92.1616 | NaN | NaN | NaN | -17.1901 | NaN | NaN | NaN | NaN | 605.3787 | NaN | 17.5884 | NaN | 23.3727
6822.1292 | 13.9226 | 13.5808 | 13.6529 | 13.9066 | 13.3981 | 13.6463 | 13.3251 | 13.1633 | NaN | NaN | NaN | 13.3956 | 92.3456 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 605.597 | NaN | 18.5013 | NaN | 23.8357
6823.1292 | 13.9608 | 13.5963 | 13.6536 | 13.8813 | 13.2669 | 13.6866 | 13.3191 | 13.1566 | NaN | NaN | NaN | 13.3564 | 91.937 | NaN | NaN | NaN | 1.9572 | NaN | NaN | NaN | NaN | 606.1229 | NaN | 17.3582 | NaN | 25.7355
6824.1292 | 13.9012 | 13.5801 | 13.6539 | 13.9521 | 13.4341 | 13.6794 | 13.3213 | 13.159 | NaN | NaN | NaN | 13.3743 | 93.2081 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 602.6938 | NaN | 17.9723 | NaN | 25.669
6825.1292 | 13.9264 | 13.6463 | 13.6562 | 13.9582 | 13.2822 | 13.651 | 13.3455 | 13.1575 | NaN | NaN | NaN | 13.3738 | 90.5535 | NaN | NaN | NaN | 7.2451 | NaN | NaN | NaN | NaN | 608.1809 | NaN | 17.637 | NaN | 22.1108
6826.1292 | 13.9782 | 13.7491 | 13.6593 | 13.9735 | 13.1954 | 13.6293 | 13.3506 | 13.1526 | NaN | NaN | NaN | 13.4113 | 93.2896 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 606.755 | NaN | 15.1503 | NaN | 22.4625
6827.1292 | 13.9578 | 13.6308 | 13.6626 | 13.8688 | 13.3811 | 13.6233 | 13.3448 | 13.1508 | NaN | NaN | NaN | 13.4041 | 90.0975 | NaN | NaN | NaN | 20.031 | NaN | NaN | NaN | NaN | 602.0332 | NaN | 15.7592 | NaN | 25.0659
6828.1292 | 13.949 | 13.5812 | 13.6528 | 13.9427 | 13.3413 | 13.6106 | 13.3305 | 13.1515 | NaN | NaN | NaN | 13.3621 | 92.3931 | NaN | NaN | NaN | -19.7057 | NaN | NaN | NaN | NaN | 598.2535 | NaN | 17.7499 | NaN | 25.7831
6829.1292 | 13.9049 | 13.6504 | 13.6557 | 13.9492 | 13.3134 | 13.6441 | 13.3422 | 13.1466 | NaN | NaN | NaN | 13.3679 | 93.3556 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 601.5154 | NaN | 17.9416 | NaN | 24.8777
6830.1292 | 13.9515 | 13.6049 | 13.663 | 14.0298 | 13.3364 | 13.6048 | 13.3287 | 13.1574 | NaN | NaN | NaN | 13.4044 | 103.7281 | NaN | NaN | NaN | -17.64 | NaN | NaN | NaN | NaN | 601.9893 | NaN | 16.7393 | NaN | 22.8817
6831.1292 | 13.8761 | 13.6111 | 13.6622 | 13.9337 | 13.3688 | 13.6568 | 13.3184 | 13.1468 | NaN | NaN | NaN | 13.4022 | 94.6781 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 598.5719 | NaN | 17.2316 | NaN | 25.6213
6832.1292 | 13.9424 | 13.5892 | 13.6684 | 13.9585 | 13.3736 | 13.6258 | 13.3244 | 13.143 | NaN | NaN | NaN | 13.3886 | 93.2111 | NaN | NaN | NaN | -8.2834 | NaN | NaN | NaN | NaN | 604.3234 | NaN | 17.1817 | NaN | 26.0733
6833.1292 | 13.9583 | 13.7137 | 13.6721 | 14.0166 | 13.2757 | 13.6307 | 13.3648 | 13.1487 | NaN | NaN | NaN | 13.3859 | 92.9788 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 604.1029 | NaN | 16.9307 | NaN | 26.3124
6834.1292 | 13.9605 | 13.5817 | 13.6655 | 13.9528 | 13.3172 | 13.6274 | 13.3212 | 13.1466 | NaN | NaN | NaN | 13.421 | 93.2967 | NaN | NaN | NaN | 0.6772 | NaN | NaN | NaN | NaN | 601.911 | NaN | 17.9506 | NaN | 24.5304
6835.1292 | 13.9465 | 13.6736 | 13.6699 | 13.956 | 13.3419 | 13.6268 | 13.3512 | 13.1517 | NaN | NaN | NaN | 13.3601 | 99.4272 | NaN | NaN | NaN | -17.3661 | NaN | NaN | NaN | NaN | 605.7131 | NaN | 15.3998 | NaN | 23.121
6836.1292 | 13.9497 | 13.6963 | 13.6704 | 13.9622 | 13.2809 | 13.6657 | 13.3493 | 13.1455 | NaN | NaN | NaN | 13.4882 | 92.3871 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 603.8906 | NaN | 15.9723 | NaN | 20.0239
6837.1292 | 13.945 | 13.5825 | 13.6638 | 13.9508 | 13.3502 | 13.6279 | 13.3198 | 13.1461 | NaN | NaN | NaN | 13.4194 | 91.8047 | NaN | NaN | NaN | 18.5322 | NaN | NaN | NaN | NaN | 601.8744 | NaN | 17.9033 | NaN | 23.8723
6838.1292 | 13.9715 | 13.5718 | 13.6594 | 13.99 | 13.35 | 13.6241 | 13.3315 | 13.1464 | NaN | NaN | NaN | 13.5117 | 91.4549 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 607.3557 | NaN | 17.4136 | NaN | 22.4218
6839.1292 | 13.9616 | 13.563 | 13.6587 | 13.9569 | 13.4068 | 13.6173 | 13.3214 | 13.1427 | NaN | NaN | NaN | 13.3484 | 92.0225 | NaN | NaN | NaN | -16.3109 | NaN | NaN | NaN | NaN | 605.9188 | NaN | 15.6485 | NaN | 26.7041
6840.1292 | 14.0176 | 13.5714 | 13.6587 | 14.0046 | 13.2737 | 13.6302 | 13.3171 | 13.1474 | NaN | NaN | NaN | 13.4228 | 93.8058 | NaN | NaN | NaN | -11.5514 | NaN | NaN | NaN | NaN | 606.9012 | NaN | 16.8052 | NaN | 26.1949
6841.1292 | 13.9662 | 13.6401 | 13.6579 | 13.9227 | 13.2755 | 13.631 | 13.3584 | 13.1473 | NaN | NaN | NaN | 13.4811 | 96.7965 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 606.9666 | NaN | 17.5769 | NaN | 25.0517
6842.1292 | 13.9446 | 13.666 | 13.6594 | 13.9033 | 13.3238 | 13.6752 | 13.349 | 13.1496 | NaN | NaN | NaN | 13.3496 | 88.0027 | NaN | NaN | NaN | 24.9065 | NaN | NaN | NaN | NaN | 606.1616 | NaN | 17.1 | NaN | 25.1036
6843.1292 | 14.0273 | 13.5754 | 13.6584 | 13.9368 | 13.3249 | 13.622 | 13.3201 | 13.1464 | NaN | NaN | NaN | 13.4156 | 91.4947 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 606.4136 | NaN | 17.5382 | NaN | 22.0567
6844.1292 | 13.9588 | 13.6096 | 13.6619 | 13.9103 | 13.4226 | 13.6162 | 13.3405 | 13.1501 | NaN | NaN | NaN | 13.3869 | 92.9961 | NaN | NaN | NaN | -0.9112 | NaN | NaN | NaN | NaN | 605.6776 | NaN | 17.2397 | NaN | 24.931
6845.1292 | 13.9546 | 13.6002 | 13.6575 | 13.9562 | 13.3226 | 13.6201 | 13.3216 | 13.1534 | NaN | NaN | NaN | 13.368 | 91.848 | NaN | NaN | NaN | -11.1966 | NaN | NaN | NaN | NaN | 604.4761 | NaN | 17.6167 | NaN | 26.5827
6846.1292 | 13.9365 | 13.5723 | 13.6679 | 13.9273 | 13.2608 | 13.6327 | 13.3277 | 13.1533 | NaN | NaN | NaN | 13.4624 | 91.3514 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 607.7495 | NaN | 15.8796 | NaN | 27.5668
6847.1292 | 13.9466 | 13.5888 | 13.6657 | 13.9241 | 13.3911 | 13.6278 | 13.3221 | 13.1513 | NaN | NaN | NaN | 13.3862 | 107.2198 | NaN | NaN | NaN | 12.5252 | NaN | NaN | NaN | NaN | 607.7245 | NaN | 17.2546 | NaN | 25.0791
6848.1292 | 13.9344 | 13.594 | 13.6649 | 13.9581 | 13.3656 | 13.9571 | 13.3226 | 13.1486 | NaN | NaN | NaN | 13.4803 | 93.1357 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 608.1379 | NaN | 17.413 | NaN | 26.1317
6849.1292 | 14.0001 | 13.5789 | 13.667 | 13.9218 | 13.3197 | 13.6735 | 13.3263 | 13.1521 | NaN | NaN | NaN | 13.3772 | 94.0452 | NaN | NaN | NaN | -8.3241 | NaN | NaN | NaN | NaN | 609.3913 | NaN | 16.0769 | NaN | 23.1512
6850.1292 | 13.9384 | 13.5723 | 13.6696 | 13.9748 | 13.2813 | 13.6461 | 13.3123 | 13.1483 | NaN | NaN | NaN | 13.5344 | 92.1361 | NaN | NaN | NaN | -10.3895 | NaN | NaN | NaN | NaN | 608.1222 | NaN | 17.8369 | NaN | 23.7073
6851.1292 | 13.9237 | 13.5717 | 13.6614 | 13.9663 | 13.3513 | 13.6448 | 13.3162 | 13.152 | NaN | NaN | NaN | 13.3845 | 92.355 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 609.9501 | NaN | 19.1303 | NaN | 25.5775
6852.1292 | 13.986 | 13.6802 | 13.667 | 13.9218 | 13.344 | 13.6696 | 13.3353 | 13.1471 | NaN | NaN | NaN | 13.5053 | 95.1673 | NaN | NaN | NaN | -17.1369 | NaN | NaN | NaN | NaN | 606.5081 | NaN | 14.8757 | NaN | 25.6732
6853.1292 | 13.9278 | 13.6328 | 13.6691 | 13.9928 | 13.2736 | 13.7791 | 13.3432 | 13.1516 | NaN | NaN | NaN | 13.4172 | 95.6709 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 606.0497 | NaN | 17.9547 | NaN | 25.469
6854.1292 | 13.9729 | 13.6516 | 13.6595 | 13.9735 | 13.317 | 13.615 | 13.3389 | 13.1549 | NaN | NaN | NaN | 13.4373 | 92.3829 | NaN | NaN | NaN | -1.9269 | NaN | NaN | NaN | NaN | 606.1453 | NaN | 17.4262 | NaN | 25.7485
6855.1292 | 13.9185 | 13.6513 | 13.6581 | 13.9475 | 13.328 | 13.6279 | 13.3439 | 13.1554 | NaN | NaN | NaN | 13.4055 | 93.102 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 604.8608 | NaN | 18.8928 | NaN | 26.023
6856.1292 | 13.9953 | 13.5767 | 13.6586 | 13.9592 | 13.281 | 13.6841 | 13.3417 | 13.1573 | NaN | NaN | NaN | 13.3707 | 93.3439 | NaN | NaN | NaN | -9.0021 | NaN | NaN | NaN | NaN | 605.8569 | NaN | 17.0984 | NaN | 24.6468
6857.1292 | 13.9789 | 13.6323 | 13.6551 | 13.8854 | 13.3958 | 13.6895 | 13.3442 | 13.1593 | NaN | NaN | NaN | 13.4359 | 92.2674 | NaN | NaN | NaN | 26.9856 | NaN | NaN | NaN | NaN | 605.4716 | NaN | 16.7773 | NaN | 26.4659
6858.1292 | 13.9405 | 13.5811 | 13.657 | 14.0026 | 13.4055 | 13.7279 | 13.3263 | 13.1564 | NaN | NaN | NaN | 13.5387 | 94.8348 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 604.2615 | NaN | 14.951 | NaN | 25.1848
6859.1292 | 13.9421 | 13.5796 | 13.6543 | 13.9303 | 13.3752 | 13.6105 | 13.3315 | 13.1525 | NaN | NaN | NaN | 13.5493 | 92.0225 | NaN | NaN | NaN | -5.7045 | NaN | NaN | NaN | NaN | 605.7115 | NaN | 15.3223 | NaN | 25.4591
6860.1292 | 13.9216 | 13.5786 | 13.6574 | 13.9661 | 13.4274 | 13.616 | 13.3217 | 13.1509 | NaN | NaN | NaN | 13.3693 | 90.4836 | NaN | NaN | NaN | -8.7735 | NaN | NaN | NaN | NaN | 603.0241 | NaN | 18.4141 | NaN | 25.0293
6861.1292 | 13.9617 | 13.6609 | 13.6558 | 13.994 | 13.3008 | 13.6444 | 13.3542 | 13.1514 | NaN | NaN | NaN | 13.3782 | 95.6136 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 609.0981 | NaN | 17.6295 | NaN | 23.4166
6862.1292 | 13.9466 | 13.5712 | 13.6549 | 13.945 | 13.3818 | 13.6061 | 13.3295 | 13.1546 | NaN | NaN | NaN | 13.4045 | 91.6979 | NaN | NaN | NaN | -7.1889 | NaN | NaN | NaN | NaN | 610.008 | NaN | 15.7582 | NaN | 25.2904
6863.1292 | 14.1285 | 13.6744 | 13.6561 | 13.9593 | 13.3429 | 13.6321 | 13.3381 | 13.1496 | NaN | NaN | NaN | 13.4527 | 92.3902 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 609.4056 | NaN | 15.9392 | NaN | 25.3173
6864.1292 | 13.9644 | 13.5616 | 13.6537 | 13.9614 | 13.3584 | 13.669 | 13.3271 | 13.162 | NaN | NaN | NaN | 13.4173 | 93.2485 | NaN | NaN | NaN | 3.2877 | NaN | NaN | NaN | NaN | 611.5206 | NaN | 17.2729 | NaN | 23.3046
6865.1292 | 13.9505 | 13.5732 | 13.6538 | 13.9516 | 13.4017 | 13.6117 | 13.3284 | 13.1559 | NaN | NaN | NaN | 13.5412 | 92.5028 | NaN | NaN | NaN | -17.4832 | NaN | NaN | NaN | NaN | 612.4735 | NaN | 18.4331 | NaN | 24.5708
6866.1292 | 13.9475 | 13.5897 | 13.6551 | 13.9665 | 13.4097 | 13.6139 | 13.3335 | 13.1589 | NaN | NaN | NaN | 13.4414 | 92.7887 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 610.2988 | NaN | 16.3329 | NaN | 24.8516
6867.1292 | 13.974 | 13.6365 | 13.6504 | 13.9789 | 13.3866 | 13.6223 | 13.3412 | 13.1574 | NaN | NaN | NaN | 13.3656 | 93.7922 | NaN | NaN | NaN | 30.3811 | NaN | NaN | NaN | NaN | 609.8677 | NaN | 16.5242 | NaN | 23.7528
6868.1292 | 13.9662 | 13.6318 | 13.6545 | 13.9584 | 13.3971 | 13.6894 | 13.3377 | 13.1587 | NaN | NaN | NaN | 13.598 | 92.4378 | NaN | NaN | NaN | -14.2783 | NaN | NaN | NaN | NaN | 610.1318 | NaN | 18.7564 | NaN | 27.3674
6869.1448 | 13.9553 | 13.5818 | 13.6542 | 13.9545 | 13.308 | 13.6163 | 13.3347 | 13.1615 | NaN | NaN | NaN | 13.3637 | 92.8977 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 608.1123 | NaN | 17.9305 | NaN | 27.2944
6870.1292 | 13.9401 | 13.5473 | 13.6623 | 13.954 | 13.4099 | 13.6113 | 13.3144 | 13.1589 | NaN | NaN | NaN | 13.3968 | 94.1131 | NaN | NaN | NaN | 12.4626 | NaN | NaN | NaN | NaN | 610.3581 | NaN | 18.7744 | NaN | 23.3462
6871.1292 | 13.9781 | 13.5591 | 13.6524 | 13.9396 | 13.3456 | 13.6222 | 13.3188 | 13.1628 | NaN | NaN | NaN | 13.3834 | 93.2063 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 611.8844 | NaN | 17.8941 | NaN | 23.3075
6872.1292 | 13.98 | 13.5843 | 13.6645 | 13.8982 | 13.2953 | 13.5985 | 13.3243 | 13.1616 | NaN | NaN | NaN | 13.4525 | 92.5929 | NaN | NaN | NaN | 24.4 | NaN | NaN | NaN | NaN | 607.4024 | NaN | 18.0635 | NaN | 25.9677
6873.1292 | 13.9669 | 13.5631 | 13.654 | 13.9496 | 13.3928 | 13.5937 | 13.3121 | 13.1589 | NaN | NaN | NaN | 13.3886 | 92.0941 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 609.7182 | NaN | 18.1769 | NaN | 24.8368
6874.1292 | 13.9599 | 13.696 | 13.6584 | 13.9478 | 13.3546 | 13.6206 | 13.3409 | 13.1593 | NaN | NaN | NaN | 13.4223 | 97.8858 | NaN | NaN | NaN | -8.4725 | NaN | NaN | NaN | NaN | 608.934 | NaN | 15.8132 | NaN | 22.6259
6875.1292 | 14.0113 | 13.6375 | 13.6505 | 13.9044 | 13.4072 | 13.6086 | 13.3348 | 13.1611 | NaN | NaN | NaN | 13.4142 | 106.6457 | NaN | NaN | NaN | -5.5405 | NaN | NaN | NaN | NaN | 609.5853 | NaN | 15.9064 | NaN | 22.3469
6876.1292 | 13.9893 | 13.617 | 13.6438 | 13.9191 | 13.3697 | 13.6265 | 13.3427 | 13.1552 | NaN | NaN | NaN | 13.4237 | 92.9161 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 0.7079 | 609.8294 | NaN | 16.7009 | NaN | 22.6279
6877.1292 | 13.9782 | 13.5873 | 13.6389 | 13.9888 | 13.3822 | 13.6273 | 13.3449 | 13.1576 | NaN | NaN | NaN | 13.4314 | 92.8077 | NaN | NaN | NaN | 1.4336 | NaN | NaN | NaN | 18.9651 | 609.2306 | NaN | 17.864 | NaN | 24.1965
6878.1292 | 13.9733 | 13.6155 | 13.6521 | 13.9846 | 13.2807 | 13.6147 | 13.3434 | 13.1527 | NaN | NaN | NaN | 13.3881 | 91.7278 | NaN | NaN | NaN | -18.4572 | NaN | NaN | NaN | 15.7737 | 604.6606 | NaN | 19.111 | NaN | 25.9811
6879.1292 | 13.9455 | 13.6623 | 13.6498 | 13.9725 | 13.3049 | 13.6546 | 13.336 | 13.1597 | NaN | NaN | NaN | 13.4523 | 99.2294 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.8437 | 606.0051 | NaN | 16.9019 | NaN | 23.6507
6880.1292 | 14.0069 | 13.6551 | 13.6478 | 13.9389 | 13.3709 | 13.6376 | 13.3579 | 13.1503 | NaN | NaN | NaN | 13.3895 | 97.3858 | NaN | NaN | NaN | 18.9191 | NaN | NaN | NaN | 19.8163 | 607.8012 | NaN | 15.6888 | NaN | 24.7377
6881.1292 | 13.9716 | 13.6415 | 13.6509 | 13.9663 | 13.2454 | 13.6727 | 13.3393 | 13.1577 | NaN | NaN | NaN | 13.4675 | 94.4913 | NaN | NaN | NaN | -18.6508 | NaN | NaN | NaN | NaN | 610.4033 | NaN | 16.1742 | NaN | 22.8818
6882.1292 | 13.9787 | 13.6154 | 13.6529 | 13.918 | 13.3583 | 13.6733 | 13.3385 | 13.165 | NaN | NaN | NaN | 13.4459 | 91.632 | NaN | NaN | NaN | -11.529 | NaN | NaN | NaN | NaN | 612.3986 | NaN | 17.1385 | NaN | 25.8338
6883.1292 | 13.9683 | 13.6248 | 13.6504 | 13.9343 | 13.465 | 13.6056 | 13.3469 | 13.1622 | NaN | NaN | NaN | 13.549 | 96.9438 | NaN | NaN | NaN | -1.8237 | NaN | NaN | NaN | NaN | 609.0376 | NaN | 17.8543 | NaN | 26.4501
6884.1292 | 13.9642 | 13.6087 | 13.6436 | 13.9466 | 13.4354 | 13.632 | 13.3301 | 13.1655 | NaN | NaN | NaN | 13.393 | 103.5787 | NaN | NaN | NaN | -7.173 | NaN | NaN | NaN | -18.6386 | 610.5624 | NaN | 15.7532 | NaN | 24.921
6885.1292 | 14.0118 | 13.7055 | 13.647 | 13.99 | 13.3848 | 13.6084 | 13.3521 | 13.1564 | NaN | NaN | NaN | 13.512 | 89.9873 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 613.0437 | NaN | 17.709 | NaN | 24.1088
6886.1292 | 13.9545 | 13.5685 | 13.644 | 13.9758 | 13.3966 | 13.5985 | 13.3207 | 13.168 | NaN | NaN | NaN | 13.4556 | 94.708 | NaN | NaN | NaN | 3.0928 | NaN | NaN | NaN | NaN | 612.4889 | NaN | 17.4748 | NaN | 24.1717
6887.1448 | 13.9357 | 13.6256 | 13.6438 | 13.967 | 13.2829 | 13.6138 | 13.3315 | 13.1616 | NaN | NaN | NaN | 13.4055 | 93.1901 | NaN | NaN | NaN | -13.849 | NaN | NaN | NaN | NaN | 614.5226 | NaN | 16.1725 | NaN | 24.8715
6888.1448 | 13.9432 | 13.5825 | 13.6406 | 13.9776 | 13.324 | 13.6041 | 13.3275 | 13.1598 | NaN | NaN | NaN | 13.4347 | 94.926 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 611.3708 | NaN | 18.7487 | NaN | 27.0189
6889.1448 | 13.9696 | 13.5918 | 13.6381 | 13.9649 | 13.4504 | 13.6027 | 13.3206 | 13.16 | NaN | NaN | NaN | 13.3922 | 104.8299 | NaN | NaN | NaN | -12.4331 | NaN | NaN | NaN | NaN | 613.1876 | NaN | 18.3015 | NaN | 25.9314
6890.1292 | 13.9638 | 13.5693 | 13.6414 | 13.9715 | 13.4315 | 13.6128 | 13.3274 | 13.1604 | NaN | NaN | NaN | 13.4749 | 98.3094 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 613.2513 | NaN | 19.2046 | NaN | 26.1822
6891.1448 | 13.9361 | 13.6136 | 13.6373 | 13.9827 | 13.4507 | 13.6609 | 13.3309 | 13.1617 | NaN | NaN | NaN | 13.4062 | 94.3324 | NaN | NaN | NaN | 17.5699 | NaN | NaN | NaN | NaN | 613.2852 | NaN | 16.9618 | NaN | 23.1146
6892.1292 | 13.993 | 13.645 | 13.6327 | 13.9678 | 13.4879 | 13.6199 | 13.3392 | 13.1579 | NaN | NaN | NaN | 13.4044 | 93.1896 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 610.4984 | NaN | 16.6912 | NaN | 25.3562
6893.1292 | 13.9514 | 13.5888 | 13.6366 | 13.9229 | 13.4799 | 13.6192 | 13.3486 | 13.1558 | NaN | NaN | NaN | 13.4153 | 93.7027 | NaN | NaN | NaN | -1.442 | NaN | NaN | NaN | NaN | 614.0411 | NaN | 16.4443 | NaN | 23.1298
6894.1292 | 13.9603 | 13.5545 | 13.6462 | 13.9885 | 13.395 | 13.6734 | 13.3475 | 13.1554 | NaN | NaN | NaN | 13.4158 | 92.4919 | NaN | NaN | NaN | -10.7745 | NaN | NaN | NaN | NaN | 612.8371 | NaN | 16.3035 | NaN | 25.1086
6895.1292 | 13.953 | 13.5649 | 13.6401 | 13.9793 | 13.3758 | 13.5982 | 13.3254 | 13.156 | NaN | NaN | NaN | 13.4119 | 96.5734 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 611.0248 | NaN | 17.656 | NaN | 24.8272
6896.1292 | 13.9414 | 13.5702 | 13.6411 | 13.9722 | 13.2602 | 13.5999 | 13.3186 | 13.1573 | NaN | NaN | NaN | 13.3983 | 92.5172 | NaN | NaN | NaN | 1.8803 | NaN | NaN | NaN | NaN | 609.4959 | NaN | 19.1716 | NaN | 26.2379
6897.1292 | 13.9796 | 13.6714 | 13.646 | 13.9461 | 13.323 | 13.6301 | 13.347 | 13.1561 | NaN | NaN | NaN | 13.3841 | 98.4501 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 609.864 | NaN | 18.5251 | NaN | 25.3831
6898.1292 | 13.9662 | 13.5674 | 13.6438 | 13.9739 | 13.3885 | 13.6233 | 13.3336 | 13.163 | NaN | NaN | NaN | 13.4532 | 100.1976 | NaN | NaN | NaN | -10.8201 | NaN | NaN | NaN | NaN | 611.5764 | NaN | 17.9589 | NaN | 25.8554
6899.1292 | 13.9512 | 13.5629 | 13.6493 | 13.944 | 13.4289 | 13.6067 | 13.3315 | 13.1535 | NaN | NaN | NaN | 13.3858 | 93.4372 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 609.1134 | NaN | 19.1814 | NaN | 24.796
6900.1292 | 13.9705 | 13.5831 | 13.65 | 13.9306 | 13.3478 | 13.6045 | 13.3286 | 13.1549 | NaN | NaN | NaN | 13.3939 | 91.0459 | NaN | NaN | NaN | -11.2633 | NaN | NaN | NaN | NaN | 614.4042 | NaN | 17.166 | NaN | 24.8372
6901.1292 | 13.9387 | 13.552 | 13.6489 | 13.9722 | 13.3942 | 13.6037 | 13.3295 | 13.1562 | NaN | NaN | NaN | 13.3813 | 94.5765 | NaN | NaN | NaN | -16.2711 | NaN | NaN | NaN | NaN | 615.2012 | NaN | 17.2041 | NaN | 27.3286
6902.1292 | 13.9042 | 13.6261 | 13.651 | 13.9513 | 13.3289 | 13.6165 | 13.3537 | 13.1444 | NaN | NaN | NaN | 13.4022 | 94.8062 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 613.6602 | NaN | 17.0528 | NaN | 24.8703
6903.1292 | 13.9454 | 13.5845 | 13.655 | 13.9575 | 13.2895 | 13.6865 | 13.3415 | 13.1482 | NaN | NaN | NaN | 13.4978 | 91.6678 | NaN | NaN | NaN | 14.8165 | NaN | NaN | NaN | NaN | 614.1629 | NaN | 17.9107 | NaN | 21.6484
6904.1292 | 13.9366 | 13.579 | 13.6516 | 13.9643 | 13.4095 | 13.6113 | 13.3538 | 13.1524 | NaN | NaN | NaN | 13.4088 | 90.3622 | NaN | NaN | NaN | -18.5887 | NaN | NaN | NaN | NaN | 612.1906 | NaN | 17.5086 | NaN | 26.8499
6905.1292 | 13.9314 | 13.5753 | 13.655 | 13.9327 | 13.3142 | 13.6205 | 13.3308 | 13.1542 | NaN | NaN | NaN | 13.4153 | 92.6077 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 609.7171 | NaN | 21.1614 | NaN | 23.0009
6906.1292 | 13.9169 | 13.561 | 13.6502 | 13.9661 | 13.3039 | 13.5966 | 13.3422 | 13.1475 | NaN | NaN | NaN | 13.5408 | 101.6929 | NaN | NaN | NaN | -7.3782 | NaN | NaN | NaN | NaN | 608.7685 | NaN | 18.8462 | NaN | 24.4386
6907.1292 | 14.013 | 13.5611 | 13.6644 | 13.9011 | 13.3217 | 13.6225 | 13.3383 | 13.1443 | NaN | NaN | NaN | 13.5084 | 94.3938 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 607.1645 | NaN | 17.554 | NaN | 23.8024
6908.1292 | 13.9285 | 13.5631 | 13.6604 | 13.9777 | 13.3997 | 13.6705 | 13.3398 | 13.1498 | NaN | NaN | NaN | 13.3719 | 97.5815 | NaN | NaN | NaN | 24.3588 | NaN | NaN | NaN | NaN | 602.8095 | NaN | 19.3269 | NaN | 25.0597
6909.1292 | 13.9261 | 13.5623 | 13.6606 | 13.9526 | 13.3598 | 13.6051 | 13.3304 | 13.1455 | NaN | NaN | NaN | 13.3988 | 100.3122 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 598.989 | NaN | 15.4132 | NaN | 28.8569
6910.1292 | 13.8872 | 13.5888 | 13.6568 | 13.9171 | 13.3513 | 13.654 | 13.3455 | 13.1472 | NaN | NaN | NaN | 13.3749 | 93.5218 | NaN | NaN | NaN | -11.0482 | NaN | NaN | NaN | NaN | 594.9465 | NaN | 19.0466 | NaN | 27.6404
6911.1292 | 13.9266 | 13.5741 | 13.655 | 13.9799 | 13.4431 | 13.6262 | 13.3372 | 13.1463 | NaN | NaN | NaN | 13.56 | 100.6076 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 584.5951 | NaN | 17.3931 | NaN | 23.6062
6912.1292 | 13.9126 | 13.6104 | 13.6627 | 13.9106 | 13.3402 | 13.617 | 13.3344 | 13.1461 | NaN | NaN | NaN | 13.366 | 93.9112 | NaN | NaN | NaN | 0.8568 | NaN | NaN | NaN | NaN | 590.4291 | NaN | 16.3283 | NaN | 24.0953
6913.1292 | 13.9582 | 13.5668 | 13.657 | 13.9457 | 13.3951 | 13.5987 | 13.3254 | 13.1448 | NaN | NaN | NaN | 13.3668 | 93.7333 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 602.9143 | NaN | 20.1082 | NaN | 26.1377
6914.1292 | 13.9047 | 13.5808 | 13.6598 | 13.9709 | 13.2958 | 13.6792 | 13.3318 | 13.1511 | NaN | NaN | NaN | 13.4344 | 90.8302 | NaN | NaN | NaN | -5.5872 | NaN | NaN | NaN | NaN | 610.8179 | NaN | 17.1151 | NaN | 23.5848
6915.1292 | 13.9354 | 13.5884 | 13.6528 | 13.9568 | 13.3995 | 13.5997 | 13.331 | 13.1461 | NaN | NaN | NaN | 13.3981 | 87.6677 | NaN | NaN | NaN | 15.0317 | NaN | NaN | NaN | NaN | 611.4547 | NaN | 16.8646 | NaN | 24.0186
6916.1292 | 13.9308 | 13.7365 | 13.646 | 14.0379 | 13.3908 | 13.6263 | 13.3647 | 13.1473 | NaN | NaN | NaN | 13.4211 | 93.0185 | NaN | NaN | NaN | -15.225 | NaN | NaN | NaN | NaN | 608.1174 | NaN | 17.5411 | NaN | 23.2409
6917.1292 | 13.9223 | 13.5669 | 13.6475 | 13.926 | 13.2878 | 13.6421 | 13.335 | 13.1436 | NaN | NaN | NaN | 13.3747 | 93.4125 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 611.8758 | NaN | 18.4102 | NaN | 25.5135
6918.1292 | 13.9653 | 13.6768 | 13.6488 | 13.9012 | 13.3898 | 13.6381 | 13.3434 | 13.1501 | NaN | NaN | NaN | 13.4315 | 93.1287 | NaN | NaN | NaN | 27.0526 | NaN | NaN | NaN | -19.9471 | 609.42 | NaN | 17.4775 | NaN | 25.8601
6919.1292 | 13.9232 | 13.6084 | 13.6554 | 13.9331 | 13.367 | 13.6099 | 13.3319 | 13.1487 | NaN | NaN | NaN | 13.3788 | 94.4282 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -18.0544 | 606.5531 | NaN | 15.748 | NaN | 23.7162
6920.1292 | 13.9788 | 13.6122 | 13.6569 | 13.9212 | 13.4255 | 13.6188 | 13.3493 | 13.1496 | NaN | NaN | NaN | 13.4346 | 98.1825 | NaN | NaN | NaN | 2.4775 | NaN | NaN | NaN | NaN | 611.6916 | NaN | 16.7028 | NaN | 22.9471
6921.1292 | 13.8818 | 13.6403 | 13.6488 | 13.9882 | 13.4076 | 13.7364 | 13.33 | 13.1501 | NaN | NaN | NaN | 13.4885 | 96.8127 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 604.9376 | NaN | 16.0078 | NaN | 23.4636
6922.1292 | 13.9374 | 13.6471 | 13.6519 | 13.9349 | 13.2853 | 13.7701 | 13.3399 | 13.1445 | NaN | NaN | NaN | 13.3703 | 92.2536 | NaN | NaN | NaN | 26.3839 | NaN | NaN | NaN | NaN | 609.2921 | NaN | 18.7781 | NaN | 26.1242
6923.1292 | 13.9325 | 13.5587 | 13.6365 | 13.9846 | 13.3312 | 13.6099 | 13.3207 | 13.1453 | NaN | NaN | NaN | 13.42 | 94.3506 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 610.8824 | NaN | 16.9877 | NaN | 26.6796
6924.1292 | 13.9258 | 13.5745 | 13.6387 | 13.9615 | 13.4622 | 13.6001 | 13.3037 | 13.1408 | NaN | NaN | NaN | 13.3833 | 98.1036 | NaN | NaN | NaN | 4.9188 | NaN | NaN | NaN | NaN | 604.3756 | NaN | 17.9251 | NaN | 23.9665
6925.1292 | 13.9154 | 13.5626 | 13.6309 | 14.0059 | 13.3883 | 13.6882 | 13.3072 | 13.1468 | NaN | NaN | NaN | 13.397 | 93.39 | NaN | NaN | NaN | -14.5518 | NaN | NaN | NaN | NaN | 607.5618 | NaN | 18.8479 | NaN | 25.086
6926.1292 | 13.904 | 13.5633 | 13.6345 | 13.9651 | 13.2325 | 13.6152 | 13.3043 | 13.1468 | NaN | NaN | NaN | 13.4026 | 95.9909 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 612.9014 | NaN | 18.2791 | NaN | 24.2819
6927.1292 | 13.9272 | 13.5906 | 13.6346 | 13.9838 | 13.2964 | 13.632 | 13.3127 | 13.1457 | NaN | NaN | NaN | 13.3823 | 107.0527 | NaN | NaN | NaN | -1.9493 | NaN | NaN | NaN | NaN | 611.1063 | NaN | 18.9946 | NaN | 23.7043
6928.1292 | 13.8596 | 13.6086 | 13.6333 | 13.9348 | 13.38 | 13.5952 | 13.3212 | 13.1468 | NaN | NaN | NaN | 13.4077 | 93.5317 | NaN | NaN | NaN | -13.2758 | NaN | NaN | NaN | NaN | 609.638 | NaN | 16.2294 | NaN | 23.6079
6929.1292 | 13.9192 | 13.642 | 13.6306 | 13.952 | 13.42 | 13.6059 | 13.3286 | 13.1444 | NaN | NaN | NaN | 13.4773 | 96.9948 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 611.2867 | NaN | 16.638 | NaN | 23.3304
6930.1292 | 13.9168 | 13.6059 | 13.6325 | 13.9455 | 13.3152 | 13.6485 | 13.3225 | 13.1474 | NaN | NaN | NaN | 13.4443 | 92.1732 | NaN | NaN | NaN | 19.7993 | NaN | NaN | NaN | NaN | 610.7225 | NaN | 17.6091 | NaN | 21.3882
6931.1292 | 13.899 | 13.5693 | 13.6345 | 13.9518 | 13.3428 | 13.6403 | 13.3098 | 13.1468 | NaN | NaN | NaN | 13.412 | 94.2551 | NaN | NaN | NaN | -14.8029 | NaN | NaN | NaN | NaN | 610.5308 | NaN | 18.899 | NaN | 24.7637
6932.1292 | 14.0215 | 13.5681 | 13.6363 | 13.9937 | 13.3534 | 13.5923 | 13.2971 | 13.1522 | NaN | NaN | NaN | 13.3928 | 93.3796 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 609.3558 | NaN | 16.7984 | NaN | 25.7123
6933.1292 | 13.9289 | 13.5976 | 13.6318 | 13.9676 | 13.4343 | 13.6085 | 13.3056 | 13.1455 | NaN | NaN | NaN | 13.4069 | 93.0674 | NaN | NaN | NaN | 24.7978 | NaN | NaN | NaN | NaN | 610.1823 | NaN | 18.1466 | NaN | 26.305
6934.1292 | 13.917 | 13.6252 | 13.6377 | 13.9116 | 13.3005 | 13.6404 | 13.313 | 13.1472 | NaN | NaN | NaN | 13.4231 | 97.7839 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 610.699 | NaN | 17.778 | NaN | 24.5399
6935.1292 | 13.9108 | 13.6664 | 13.6375 | 13.959 | 13.3827 | 13.6134 | 13.3225 | 13.1514 | NaN | NaN | NaN | 13.4705 | 104.1047 | NaN | NaN | NaN | 6.6329 | NaN | NaN | NaN | NaN | 613.275 | NaN | 16.1622 | NaN | 23.6094
6936.1292 | 13.9597 | 13.6868 | 13.6397 | 14.0575 | 13.3014 | 13.6242 | 13.3333 | 13.1465 | NaN | NaN | NaN | 13.4131 | 95.9003 | NaN | NaN | NaN | -10.6207 | NaN | NaN | NaN | NaN | 612.5543 | NaN | 18.3734 | NaN | 25.2833
6937.1292 | 13.9234 | 13.6083 | 13.646 | 13.9528 | 13.3834 | 13.6275 | 13.313 | 13.1519 | NaN | NaN | NaN | 13.4159 | 94.736 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 612.3467 | NaN | 18.5772 | NaN | 25.8947
6938.1292 | 13.9227 | 13.589 | 13.6444 | 13.9655 | 13.3107 | 13.6669 | 13.3089 | 13.1495 | NaN | NaN | NaN | 13.4047 | 92.2454 | NaN | NaN | NaN | -16.8892 | NaN | NaN | NaN | -16.5067 | 613.0935 | NaN | 18.7171 | NaN | 26.1583
6939.1292 | 13.918 | 13.579 | 13.6411 | 13.9526 | 13.3276 | 13.665 | 13.3087 | 13.1531 | NaN | NaN | NaN | 13.611 | 93.136 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 609.9103 | NaN | 19.8859 | NaN | 25.3135
6940.1292 | 13.8869 | 13.5932 | 13.646 | 14.0653 | 13.3107 | 13.6752 | 13.2932 | 13.1478 | NaN | NaN | NaN | 13.4836 | 91.7492 | NaN | NaN | NaN | -10.7363 | NaN | NaN | NaN | NaN | 611.0299 | NaN | 16.191 | NaN | 25.8264
6941.1292 | 14.0285 | 13.6304 | 13.6464 | 13.9175 | 13.298 | 13.6043 | 13.305 | 13.1552 | NaN | NaN | NaN | 13.4776 | 92.9815 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 609.4145 | NaN | 16.7566 | NaN | 21.6919
6942.1292 | 13.9541 | 13.5811 | 13.6427 | 13.9542 | 13.2582 | 13.591 | 13.2929 | 13.1545 | NaN | NaN | NaN | 13.3887 | 92.1835 | NaN | NaN | NaN | 16.1836 | NaN | NaN | NaN | NaN | 607.8312 | NaN | 17.7933 | NaN | 25.0274
6943.1292 | 13.9111 | 13.5728 | 13.644 | 13.936 | 13.3289 | 13.5987 | 13.2964 | 13.1491 | NaN | NaN | NaN | 13.4334 | 92.2572 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 605.0783 | NaN | 16.0506 | NaN | 25.654
6944.1292 | 13.9092 | 13.676 | 13.6485 | 13.9467 | 13.3928 | 13.5911 | 13.3099 | 13.1536 | NaN | NaN | NaN | 13.3823 | 93.8549 | NaN | NaN | NaN | 6.4429 | NaN | NaN | NaN | -17.6126 | 602.4243 | NaN | 18.6079 | NaN | 25.7026
6945.1292 | 13.9132 | 13.6662 | 13.6442 | 13.9326 | 13.3766 | 13.6011 | 13.3269 | 13.1539 | NaN | NaN | NaN | 13.385 | 97.5066 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 595.5196 | NaN | 16.316 | NaN | 26.206
6946.1292 | 13.9141 | 13.5872 | 13.6381 | 13.9328 | 13.4129 | 13.6003 | 13.3086 | 13.1538 | NaN | NaN | NaN | 13.4027 | 92.3314 | NaN | NaN | NaN | -3.2253 | NaN | NaN | NaN | NaN | 598.2931 | NaN | 18.9197 | NaN | 24.5287
6947.1292 | 13.9458 | 13.6321 | 13.6458 | 13.9123 | 13.3329 | 13.6426 | 13.3168 | 13.1531 | NaN | NaN | NaN | 13.409 | 90.6843 | NaN | NaN | NaN | 0.0477 | NaN | NaN | NaN | NaN | 605.8918 | NaN | 16.6256 | NaN | 25.9976
6948.1292 | 13.9144 | 13.5769 | 13.6468 | 13.9489 | 13.4291 | 13.5854 | 13.3047 | 13.1565 | NaN | NaN | NaN | 13.4258 | 91.9818 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 600.9673 | NaN | 19.4914 | NaN | 24.4958
6949.1292 | 13.932 | 13.588 | 13.6508 | 13.9622 | 13.4109 | 13.6524 | 13.3102 | 13.1491 | NaN | NaN | NaN | 13.3988 | 92.71 | NaN | NaN | NaN | -19.4815 | NaN | NaN | NaN | NaN | 607.1931 | NaN | 16.2344 | NaN | 22.57
6950.1292 | 13.915 | 13.5665 | 13.6486 | 13.9645 | 13.3512 | 13.5915 | 13.3103 | 13.1564 | NaN | NaN | NaN | 13.4211 | 93.3597 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 609.6215 | NaN | 16.1569 | NaN | 25.9404
6951.1292 | 13.9524 | 13.5858 | 13.6514 | 13.942 | 13.343 | 13.6034 | 13.3022 | 13.1595 | NaN | NaN | NaN | 13.4144 | 94.2264 | NaN | NaN | NaN | -19.2316 | NaN | NaN | NaN | NaN | 608.709 | NaN | 19.6964 | NaN | 23.8179
6952.1292 | 13.9062 | 13.5921 | 13.6506 | 14.0038 | 13.4638 | 13.597 | 13.3075 | 13.1557 | NaN | NaN | NaN | 13.4321 | 102.4773 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 608.327 | NaN | 16.8292 | NaN | 25.0091
6953.1292 | 13.942 | 13.5845 | 13.6542 | 13.9545 | 13.3358 | 13.753 | 13.3075 | 13.156 | NaN | NaN | NaN | 13.3957 | 92.5547 | NaN | NaN | NaN | -8.4958 | NaN | NaN | NaN | NaN | 610.0163 | NaN | 18.2132 | NaN | 24.9829
6954.1292 | 13.9279 | 13.6375 | 13.6524 | 13.9559 | 13.318 | 13.5836 | 13.3115 | 13.1492 | NaN | NaN | NaN | 13.4011 | 96.9267 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 608.6295 | NaN | 19.7417 | NaN | 24.8184
6955.1292 | 13.9108 | 13.712 | 13.6468 | 13.9033 | 13.2707 | 13.5975 | 13.3543 | 13.1475 | NaN | NaN | NaN | 13.3781 | 90.0817 | NaN | NaN | NaN | -0.1312 | NaN | NaN | NaN | NaN | 610.165 | NaN | 17.0632 | NaN | 24.4632
6956.1292 | 14.0347 | 13.5747 | 13.6458 | 13.9883 | 13.2885 | 13.5996 | 13.3161 | 13.15 | NaN | NaN | NaN | 13.4987 | 92.3052 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 615.6591 | NaN | 19.9606 | NaN | 26.23
6957.1292 | 13.9345 | 13.57 | 13.6421 | 13.966 | 13.453 | 13.5799 | 13.2966 | 13.142 | NaN | NaN | NaN | 13.4005 | 98.1793 | NaN | NaN | NaN | 21.4795 | NaN | NaN | NaN | NaN | 617.0432 | NaN | 20.2749 | NaN | 24.6752
6958.1292 | 13.9218 | 13.5585 | 13.6423 | 13.9889 | 13.399 | 13.6879 | 13.3059 | 13.1469 | NaN | NaN | NaN | 13.409 | 95.5209 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 618.3044 | NaN | 18.6492 | NaN | 25.5848
6959.1292 | 13.9184 | 13.5709 | 13.6353 | 13.9655 | 13.3799 | 13.6096 | 13.3149 | 13.1419 | NaN | NaN | NaN | 13.3985 | 93.255 | NaN | NaN | NaN | -15.4833 | NaN | NaN | NaN | NaN | 618.091 | NaN | 17.2417 | NaN | 22.5511
6960.1292 | 13.8924 | 13.5825 | 13.6408 | 13.9555 | 13.2375 | 13.6082 | 13.3135 | 13.1443 | NaN | NaN | NaN | 13.4581 | 91.9362 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 619.7643 | NaN | 17.2056 | NaN | 25.2963
6961.1292 | 13.9454 | 13.5761 | 13.6408 | 14.1252 | 13.346 | 13.6657 | 13.3133 | 13.1446 | NaN | NaN | NaN | 13.3852 | 92.6944 | NaN | NaN | NaN | -9.5715 | NaN | NaN | NaN | NaN | 621.1168 | NaN | 15.9806 | NaN | 25.5395
6962.1292 | 13.9337 | 13.5587 | 13.6456 | 13.9517 | 13.2368 | 13.6447 | 13.3197 | 13.1431 | NaN | NaN | NaN | 13.4565 | 97.7074 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 622.8707 | NaN | 18.2811 | NaN | 25.7857
6963.1292 | 13.8934 | 13.6035 | 13.6412 | 13.9492 | 13.3037 | 13.592 | 13.3194 | 13.1404 | NaN | NaN | NaN | 13.3806 | 92.6308 | NaN | NaN | NaN | 3.8078 | NaN | NaN | NaN | NaN | 621.0079 | NaN | 19.2669 | NaN | 24.9054
6964.1292 | 13.9053 | 13.5616 | 13.6408 | 13.9485 | 13.4109 | 13.5803 | 13.3015 | 13.1429 | NaN | NaN | NaN | 13.4503 | 102.6434 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 622.5451 | NaN | 17.7518 | NaN | 25.1742
6965.1292 | 13.8984 | 13.5998 | 13.6413 | 13.915 | 13.3721 | 13.5973 | 13.3245 | 13.1455 | NaN | NaN | NaN | 13.374 | 90.5119 | NaN | NaN | NaN | 7.7971 | NaN | NaN | NaN | NaN | 622.3654 | NaN | 17.1752 | NaN | 22.9078
6966.1292 | 14.0213 | 13.5586 | 13.6483 | 13.9499 | 13.3233 | 13.6036 | 13.312 | 13.144 | NaN | NaN | NaN | 13.3853 | 93.1428 | NaN | NaN | NaN | -12.1278 | NaN | NaN | NaN | NaN | 623.8309 | NaN | 17.9978 | NaN | 22.9207
6967.1292 | 13.905 | 13.6135 | 13.6477 | 13.9606 | 13.4681 | 13.6263 | 13.3103 | 13.1492 | NaN | NaN | NaN | 13.4061 | 93.8532 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 626.7054 | NaN | 17.2495 | NaN | 26.5517
6968.1292 | 13.9663 | 13.5858 | 13.6455 | 13.9561 | 13.4382 | 13.591 | 13.3103 | 13.1483 | NaN | NaN | NaN | 13.3829 | 94.4175 | NaN | NaN | NaN | -16.22 | NaN | NaN | NaN | NaN | 621.0162 | NaN | 14.696 | NaN | 25.973
6969.1292 | 13.9031 | 13.6718 | 13.641 | 13.9242 | 13.2944 | 13.6663 | 13.3382 | 13.1492 | NaN | NaN | NaN | 13.3796 | 91.2677 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 626.5828 | NaN | 16.4615 | NaN | 24.3285
6970.1292 | 13.9113 | 13.5697 | 13.6435 | 13.925 | 13.4281 | 13.6602 | 13.3147 | 13.1436 | NaN | NaN | NaN | 13.3878 | 92.8702 | NaN | NaN | NaN | -16.5498 | NaN | NaN | NaN | NaN | 624.4041 | NaN | 17.9665 | NaN | 26.1828
6971.1292 | 13.8965 | 13.5601 | 13.6451 | 13.9409 | 13.304 | 13.5891 | 13.317 | 13.1498 | NaN | NaN | NaN | 13.3794 | 92.2767 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 625.5293 | NaN | 18.5907 | NaN | 24.8319
6972.1292 | 13.8726 | 13.5467 | 13.636 | 13.9261 | 13.3278 | 13.6702 | 13.3203 | 13.1564 | NaN | NaN | NaN | 13.4433 | 93.9531 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 626.9929 | NaN | 17.4864 | NaN | 24.4455
6973.1292 | 14.0243 | 13.5588 | 13.6323 | 13.9519 | 13.2831 | 13.6329 | 13.3123 | 13.1479 | NaN | NaN | NaN | 13.4184 | 91.2858 | NaN | NaN | NaN | -7.379 | NaN | NaN | NaN | NaN | 623.0432 | NaN | 16.555 | NaN | 22.9679
6974.1292 | 13.8713 | 13.5619 | 13.6312 | 13.9105 | 13.3259 | 13.5788 | 13.31 | 13.148 | NaN | NaN | NaN | 13.4013 | 90.8664 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 626.6482 | NaN | 17.8446 | NaN | 25.8202
6975.1292 | 13.9066 | 13.5531 | 13.6297 | 13.9477 | 13.3483 | 13.5759 | 13.3114 | 13.1477 | NaN | NaN | NaN | 13.3941 | 94.6659 | NaN | NaN | NaN | -10.5649 | NaN | NaN | NaN | NaN | 622.2324 | NaN | 19.4475 | NaN | 26.2105
6976.1292 | 13.9239 | 13.5513 | 13.6356 | 13.8721 | 13.3379 | 13.5866 | 13.3288 | 13.1496 | NaN | NaN | NaN | 13.4262 | 98.9684 | NaN | NaN | NaN | -18.1472 | NaN | NaN | NaN | NaN | 623.1827 | NaN | 19.3271 | NaN | 24.5588
6977.1292 | 13.9099 | 13.5421 | 13.6411 | 13.9438 | 13.4059 | 13.579 | 13.3166 | 13.1539 | NaN | NaN | NaN | 13.4224 | 93.1674 | NaN | NaN | NaN | -16.5312 | NaN | NaN | NaN | NaN | 618.3676 | NaN | 17.3812 | NaN | 23.4461
6978.1292 | 13.8722 | 13.5789 | 13.6258 | 13.9473 | 13.4089 | 13.5906 | 13.3199 | 13.1459 | NaN | NaN | NaN | 13.4064 | 93.6514 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 619.9664 | NaN | 18.7692 | NaN | 25.3973
6979.1292 | 13.9 | 13.5665 | 13.6317 | 13.8934 | 13.324 | 13.6024 | 13.3234 | 13.1509 | NaN | NaN | NaN | 13.3901 | 93.2487 | NaN | NaN | NaN | 12.8037 | NaN | NaN | NaN | NaN | 622.8981 | NaN | 18.8539 | NaN | 25.2017
6980.1292 | 13.8941 | 13.5351 | 13.6299 | 13.9212 | 13.2866 | 13.5944 | 13.3211 | 13.1458 | NaN | NaN | NaN | 13.4083 | 94.1798 | NaN | NaN | NaN | -17.0084 | NaN | NaN | NaN | NaN | 625.8411 | NaN | 19.5147 | NaN | 22.9928
6981.1292 | 13.8813 | 13.5273 | 13.6296 | 13.9405 | 13.2828 | 13.604 | 13.3064 | 13.1474 | NaN | NaN | NaN | 13.4446 | 96.0441 | NaN | NaN | NaN | -14.9134 | NaN | NaN | NaN | NaN | 621.2816 | NaN | 17.9294 | NaN | 23.8987
6982.1292 | 13.8664 | 13.5732 | 13.6265 | 13.8778 | 13.377 | 13.5956 | 13.3151 | 13.1472 | NaN | NaN | NaN | 13.3673 | 92.6997 | NaN | NaN | NaN | -12.8891 | NaN | NaN | NaN | NaN | 623.0771 | NaN | 17.7323 | NaN | 22.7911
6983.1292 | 13.8543 | 13.6245 | 13.627 | 13.929 | 13.4212 | 13.5799 | 13.3331 | 13.1489 | NaN | NaN | NaN | 13.4038 | 93.6783 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 622.6324 | NaN | 18.4333 | NaN | 23.1745
6984.1292 | 13.8978 | 13.5469 | 13.6294 | 13.9346 | 13.2764 | 13.6572 | 13.3124 | 13.153 | NaN | NaN | NaN | 13.3752 | 96.4695 | NaN | NaN | NaN | 8.3232 | NaN | NaN | NaN | NaN | 621.3597 | NaN | 20.1261 | NaN | 25.196
6985.1292 | 13.9024 | 13.5696 | 13.626 | 13.9404 | 13.2792 | 13.5989 | 13.3211 | 13.1509 | NaN | NaN | NaN | 13.3975 | 94.4959 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 625.0249 | NaN | 17.4298 | NaN | 22.1467
6986.1292 | 13.8608 | 13.5163 | 13.622 | 13.8783 | 13.2361 | 13.6476 | 13.3135 | 13.1444 | NaN | NaN | NaN | 13.3709 | 94.5664 | NaN | NaN | NaN | 1.7685 | NaN | NaN | NaN | NaN | 624.3315 | NaN | 16.8976 | NaN | 23.6518
6987.1292 | 13.8955 | 13.531 | 13.625 | 13.9375 | 13.3631 | 13.6246 | 13.3079 | 13.154 | NaN | NaN | NaN | 13.403 | 92.8614 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 622.4917 | NaN | 16.9541 | NaN | 24.0976
6988.1292 | 13.8955 | 13.603 | 13.6189 | 13.9891 | 13.4152 | 13.6707 | 13.3264 | 13.1522 | NaN | NaN | NaN | 13.3511 | 98.8016 | NaN | NaN | NaN | -15.8982 | NaN | NaN | NaN | NaN | 621.4835 | NaN | 17.4268 | NaN | 24.7814
6989.1292 | 13.8789 | 13.554 | 13.6256 | 13.9281 | 13.3389 | 13.6071 | 13.3145 | 13.1496 | NaN | NaN | NaN | 13.3692 | 92.3769 | NaN | NaN | NaN | -11.675 | NaN | NaN | NaN | NaN | 619.3575 | NaN | 19.4836 | NaN | 24.7105
6990.1292 | 13.8409 | 13.6228 | 13.616 | 13.9023 | 13.3321 | 13.623 | 13.313 | 13.1512 | NaN | NaN | NaN | 13.3689 | 94.168 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 617.4213 | NaN | 19.4728 | NaN | 25.8982
6991.1292 | 13.8955 | 13.6781 | 13.6255 | 13.9488 | 13.2914 | 13.607 | 13.3325 | 13.1521 | NaN | NaN | NaN | 13.4056 | 97.0916 | NaN | NaN | NaN | -3.7996 | NaN | NaN | NaN | NaN | 618.9227 | NaN | 18.0064 | NaN | 23.4945
6992.1292 | 13.891 | 13.5475 | 13.6243 | 13.9221 | 13.2933 | 13.588 | 13.2963 | 13.1543 | NaN | NaN | NaN | 13.405 | 94.3812 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 622.2446 | NaN | 21.0466 | NaN | 26.5942
6993.1292 | 13.8961 | 13.6244 | 13.6238 | 13.9813 | 13.3891 | 13.6029 | 13.3122 | 13.1489 | NaN | NaN | NaN | 13.4597 | 95.8225 | NaN | NaN | NaN | 10.6986 | NaN | NaN | NaN | NaN | 619.6403 | NaN | 16.1488 | NaN | 24.807
6994.1292 | 13.8946 | 13.5597 | 13.623 | 13.8847 | 13.4295 | 13.5766 | 13.2852 | 13.1546 | NaN | NaN | NaN | 13.4281 | 96.8676 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 618.2981 | NaN | 18.9412 | NaN | 24.6534
6995.1292 | 13.8904 | 13.5869 | 13.634 | 13.9008 | 13.2872 | 13.6138 | 13.3029 | 13.1485 | NaN | NaN | NaN | 13.4189 | 93.5272 | NaN | NaN | NaN | 29.0954 | NaN | NaN | NaN | NaN | 617.4765 | NaN | 19.2987 | NaN | 22.9607
6996.1292 | 13.8745 | 13.5727 | 13.6235 | 13.9832 | 13.3046 | 13.5872 | 13.2941 | 13.1471 | NaN | NaN | NaN | 13.4003 | 93.2489 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 616.732 | NaN | 17.3703 | NaN | 26.3184
6997.1292 | 13.8747 | 13.6134 | 13.6233 | 13.9458 | 13.2956 | 13.6065 | 13.2936 | 13.1473 | NaN | NaN | NaN | 13.3591 | 93.6414 | NaN | NaN | NaN | -3.6948 | NaN | NaN | NaN | NaN | 618.7963 | NaN | 19.7992 | NaN | 23.8586
6998.1292 | 13.9102 | 13.5793 | 13.6209 | 13.9098 | 13.3201 | 13.5849 | 13.2926 | 13.1489 | NaN | NaN | NaN | 13.4058 | 92.4986 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 619.0734 | NaN | 14.8809 | NaN | 22.3341
6999.1292 | 13.8256 | 13.5762 | 13.6269 | 13.9389 | 13.4196 | 13.5786 | 13.2952 | 13.1389 | NaN | NaN | NaN | 13.3633 | 92.2651 | NaN | NaN | NaN | 24.2534 | NaN | NaN | NaN | NaN | 618.333 | NaN | 16.905 | NaN | 23.8082
7000.1292 | 13.9155 | 13.6357 | 13.6248 | 13.9645 | 13.3648 | 13.7382 | 13.293 | 13.1405 | NaN | NaN | NaN | 13.3401 | 94.2684 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 616.8031 | NaN | 18.6729 | NaN | 25.117
7001.1292 | 13.8673 | 13.5416 | 13.6252 | 13.8988 | 13.3041 | 13.5725 | 13.2783 | 13.1365 | NaN | NaN | NaN | 13.3557 | 93.1253 | NaN | NaN | NaN | 23.7171 | NaN | NaN | NaN | NaN | 619.6603 | NaN | 18.3932 | NaN | 22.7221
7002.1292 | 13.9938 | 13.6297 | 13.6253 | 13.8954 | 13.3264 | 13.6101 | 13.313 | 13.1371 | NaN | NaN | NaN | 13.3401 | 93.7458 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 613.5624 | NaN | 19.1855 | NaN | 24.0887
7003.1292 | 13.8849 | 13.6 | 13.6268 | 13.8781 | 13.3058 | 13.8155 | 13.2995 | 13.1384 | NaN | NaN | NaN | 13.4112 | 91.2508 | NaN | NaN | NaN | -3.436 | NaN | NaN | NaN | NaN | 614.3426 | NaN | 20.1197 | NaN | 25.5168
7004.1292 | 13.8513 | 13.5662 | 13.6238 | 13.9251 | 13.2958 | 13.6003 | 13.2879 | 13.1359 | NaN | NaN | NaN | 13.3503 | 91.6429 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 612.6881 | NaN | 18.6662 | NaN | 24.3831
7005.1292 | 13.8813 | 13.5502 | 13.6183 | 13.9186 | 13.3418 | 13.5716 | 13.2869 | 13.138 | NaN | NaN | NaN | 13.3686 | 94.7988 | NaN | NaN | NaN | 0.586 | NaN | NaN | NaN | NaN | 614.5628 | NaN | 17.327 | NaN | 24.6801
7006.1292 | 13.8821 | 13.5479 | 13.6316 | 13.9339 | 13.3597 | 13.5697 | 13.28 | 13.1315 | NaN | NaN | NaN | 13.3474 | 92.5061 | NaN | NaN | NaN | -19.942 | NaN | NaN | NaN | NaN | 615.7204 | NaN | 18.1836 | NaN | 26.182
7007.1448 | 13.8668 | 13.5505 | 13.6252 | 13.9234 | 13.3216 | 13.5857 | 13.3007 | 13.1339 | NaN | NaN | NaN | 13.38 | 91.8623 | NaN | NaN | NaN | -9.9476 | NaN | NaN | NaN | NaN | 621.0913 | NaN | 17.5001 | NaN | 25.0633
7008.1292 | 13.955 | 13.5388 | 13.6274 | 13.9883 | 13.3683 | 13.6101 | 13.2895 | 13.1311 | NaN | NaN | NaN | 13.377 | 101.3673 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 620.625 | NaN | 16.5834 | NaN | 24.9617
7009.1292 | 13.8874 | 13.5372 | 13.6291 | 13.9328 | 13.3901 | 13.5712 | 13.2879 | 13.13 | NaN | NaN | NaN | 13.4304 | 91.0387 | NaN | NaN | NaN | 11.7925 | NaN | NaN | NaN | NaN | 616.2907 | NaN | 17.6538 | NaN | 22.231
7010.1292 | 13.8527 | 13.58 | 13.6297 | 13.9274 | 13.3954 | 13.5825 | 13.2933 | 13.1298 | NaN | NaN | NaN | 13.3757 | 99.3411 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -17.7972 | 615.7931 | NaN | 18.926 | NaN | 23.072
7011.1292 | 13.8547 | 13.5586 | 13.6278 | 13.9187 | 13.2958 | 13.6127 | 13.2907 | 13.1263 | NaN | NaN | NaN | 13.3426 | 92.8453 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 618.8325 | NaN | 17.7676 | NaN | 24.2453
7012.1292 | 13.8542 | 13.5369 | 13.6355 | 13.9721 | 13.3078 | 13.5648 | 13.2803 | 13.1292 | NaN | NaN | NaN | 13.3789 | 94.424 | NaN | NaN | NaN | -10.7237 | NaN | NaN | NaN | NaN | 618.5605 | NaN | 19.3059 | NaN | 26.3132
7013.1292 | 13.898 | 13.5566 | 13.633 | 13.8931 | 13.2559 | 13.6253 | 13.2964 | 13.127 | NaN | NaN | NaN | 13.385 | 90.9002 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 620.7958 | NaN | 18.4191 | NaN | 24.969
7014.1292 | 13.8852 | 13.5463 | 13.6322 | 13.9087 | 13.4158 | 13.6106 | 13.2948 | 13.1276 | NaN | NaN | NaN | 13.3327 | 95.8643 | NaN | NaN | NaN | -5.1764 | NaN | NaN | NaN | NaN | 618.3488 | NaN | 20.4465 | NaN | 24.882
7015.1292 | 13.8769 | 13.546 | 13.6274 | 13.9218 | 13.2777 | 13.5789 | 13.2884 | 13.1311 | NaN | NaN | NaN | 13.3527 | 96.1346 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 620.6412 | NaN | 19.2909 | NaN | 25.0553
7016.1448 | 13.9007 | 13.5944 | 13.6312 | 13.8982 | 13.278 | 13.6278 | 13.2889 | 13.1264 | NaN | NaN | NaN | 13.3827 | 92.5899 | NaN | NaN | NaN | 3.3998 | NaN | NaN | NaN | NaN | 620.8737 | NaN | 19.9589 | NaN | 24.4316
7017.1292 | 13.8762 | 13.5284 | 13.6322 | 13.8778 | 13.3923 | 13.5741 | 13.2851 | 13.1247 | NaN | NaN | NaN | 13.3391 | 97.9092 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 622.5604 | NaN | 18.6169 | NaN | 24.6155
7018.1292 | 13.921 | 13.5837 | 13.6307 | 13.8834 | 13.3123 | 13.5975 | 13.2922 | 13.1171 | NaN | NaN | NaN | 13.3916 | 95.4158 | NaN | NaN | NaN | -17.5134 | NaN | NaN | NaN | NaN | 621.034 | NaN | 16.8592 | NaN | 22.1405
7019.1292 | 13.8414 | 13.5627 | 13.6341 | 13.9032 | 13.3653 | 13.6435 | 13.3027 | 13.1178 | NaN | NaN | NaN | 13.3551 | 92.618 | NaN | NaN | NaN | -16.5959 | NaN | NaN | NaN | NaN | 621.7499 | NaN | 19.2641 | NaN | 23.3599
7020.1292 | 13.8784 | 13.5616 | 13.632 | 13.8353 | 13.2773 | 13.5946 | 13.2961 | 13.1221 | NaN | NaN | NaN | 13.4615 | 91.0834 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 622.2228 | NaN | 18.5442 | NaN | 26.651
7021.1292 | 13.8353 | 13.5928 | 13.6332 | 13.9019 | 13.4028 | 13.7037 | 13.3057 | 13.1219 | NaN | NaN | NaN | 13.3933 | 101.4282 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 621.6111 | NaN | 18.5492 | NaN | 23.6
7022.1292 | 13.8954 | 13.5607 | 13.6359 | 13.8553 | 13.2894 | 13.6039 | 13.2974 | 13.1165 | NaN | NaN | NaN | 13.3755 | 92.4902 | NaN | NaN | NaN | 8.1615 | NaN | NaN | NaN | NaN | 626.0536 | NaN | 18.2048 | NaN | 24.4006
7023.1292 | 13.8885 | 13.5302 | 13.6309 | 13.9015 | 13.3666 | 13.6403 | 13.2916 | 13.1203 | NaN | NaN | NaN | 13.3662 | 94.4857 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 624.8093 | NaN | 18.6714 | NaN | 23.2649
7024.1292 | 13.8662 | 13.5225 | 13.6394 | 13.9121 | 13.3878 | 13.5529 | 13.2822 | 13.1145 | NaN | NaN | NaN | 13.3692 | 96.4241 | NaN | NaN | NaN | -19.1593 | NaN | NaN | NaN | NaN | 624.4255 | NaN | 17.9047 | NaN | 24.6306
7025.1292 | 13.8475 | 13.6602 | 13.635 | 13.922 | 13.412 | 13.617 | 13.3103 | 13.1154 | NaN | NaN | NaN | 13.3755 | 95.8788 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 625.4311 | NaN | 17.5344 | NaN | 26.4007
7026.1292 | 13.8917 | 13.5699 | 13.6344 | 13.8606 | 13.3277 | 13.5863 | 13.2956 | 13.1107 | NaN | NaN | NaN | 13.5879 | 94.8692 | NaN | NaN | NaN | -15.0559 | NaN | NaN | NaN | NaN | 625.3905 | NaN | 19.6063 | NaN | 26.4708
7027.1292 | 13.8817 | 13.5785 | 13.6361 | 13.9152 | 13.2239 | 13.6002 | 13.2875 | 13.1095 | NaN | NaN | NaN | 13.3511 | 94.9747 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 622.6191 | NaN | 17.8759 | NaN | 24.2017
7028.1292 | 13.9179 | 13.5369 | 13.6314 | 13.8617 | 13.2935 | 13.5736 | 13.285 | 13.1092 | NaN | NaN | NaN | 13.3605 | 93.6771 | NaN | NaN | NaN | 11.9624 | NaN | NaN | NaN | NaN | 622.4904 | NaN | 19.0966 | NaN | 22.2674
7029.1292 | 13.9039 | 13.5554 | 13.6263 | 13.8823 | 13.358 | 13.6271 | 13.3054 | 13.1112 | NaN | NaN | NaN | 13.3888 | 92.4124 | NaN | NaN | NaN | -19.4698 | NaN | NaN | NaN | NaN | 624.4674 | NaN | 18.3784 | NaN | 24.405
7030.1292 | 13.9008 | 13.527 | 13.6155 | 13.8958 | 13.2537 | 13.5729 | 13.282 | 13.1149 | NaN | NaN | NaN | 13.4195 | 92.2307 | NaN | NaN | NaN | 2.1379 | NaN | NaN | NaN | NaN | 621.5678 | NaN | 19.2677 | NaN | 24.2345
7031.1292 | 13.8955 | 13.5468 | 13.6229 | 13.9943 | 13.3388 | 13.6314 | 13.2951 | 13.1102 | NaN | NaN | NaN | 13.3508 | 94.0137 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 618.8777 | NaN | 19.846 | NaN | 24.3886
7032.1292 | 13.8911 | 13.6196 | 13.6199 | 13.972 | 13.3504 | 13.594 | 13.3215 | 13.1136 | NaN | NaN | NaN | 13.3827 | 91.6958 | NaN | NaN | NaN | -1.1375 | NaN | NaN | NaN | NaN | 617.2403 | NaN | 19.6023 | NaN | 24.229
7033.1292 | 13.8665 | 13.5511 | 13.6227 | 13.9023 | 13.2017 | 13.6552 | 13.2975 | 13.1138 | NaN | NaN | NaN | 13.3279 | 93.8245 | NaN | NaN | NaN | 1.3516 | NaN | NaN | NaN | NaN | 620.4621 | NaN | 19.7496 | NaN | 24.6783
7034.1448 | 13.903 | 13.5442 | 13.6237 | 13.88 | 13.2514 | 13.5794 | 13.2918 | 13.1129 | NaN | NaN | NaN | 13.3661 | 95.5112 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 616.5218 | NaN | 17.2406 | NaN | 24.5629
7035.1292 | 13.8965 | 13.5656 | 13.6251 | 13.8804 | 13.3529 | 13.6476 | 13.297 | 13.1176 | NaN | NaN | NaN | 13.3299 | 91.3555 | NaN | NaN | NaN | 30.5514 | NaN | NaN | NaN | NaN | 615.7441 | NaN | 19.2729 | NaN | 24.7431
7036.1292 | 13.8709 | 13.5688 | 13.6238 | 13.9117 | 13.2915 | 13.5957 | 13.306 | 13.1192 | NaN | NaN | NaN | 13.4182 | 95.8187 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 611.4442 | NaN | 17.5772 | NaN | 23.6779
7037.1292 | 13.8804 | 13.5469 | 13.6245 | 13.9127 | 13.2665 | 13.6418 | 13.3079 | 13.1137 | NaN | NaN | NaN | 13.3634 | 92.5307 | NaN | NaN | NaN | -5.4812 | NaN | NaN | NaN | NaN | 619.6885 | NaN | 18.9734 | NaN | 24.2089
7038.1292 | 13.9484 | 13.5393 | 13.626 | 13.9166 | 13.2933 | 13.5975 | 13.2901 | 13.1187 | NaN | NaN | NaN | 13.3963 | 91.2008 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 619.927 | NaN | 20.4539 | NaN | 22.9127
7039.1292 | 13.8702 | 13.5548 | 13.6279 | 13.8815 | 13.3061 | 13.6557 | 13.3025 | 13.1149 | NaN | NaN | NaN | 13.3677 | 91.0274 | NaN | NaN | NaN | 29.9784 | NaN | NaN | NaN | NaN | 621.2633 | NaN | 20.3322 | NaN | 24.873
7040.1292 | 13.8551 | 13.568 | 13.6191 | 13.8914 | 13.2984 | 13.5942 | 13.3042 | 13.1129 | NaN | NaN | NaN | 13.4994 | 95.6283 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 620.602 | NaN | 18.2695 | NaN | 27.2256
7041.1292 | 13.9197 | 13.549 | 13.6168 | 13.8752 | 13.2459 | 13.626 | 13.2964 | 13.1153 | NaN | NaN | NaN | 13.3635 | 93.3587 | NaN | NaN | NaN | 5.8145 | NaN | NaN | NaN | NaN | 620.7511 | NaN | 20.1204 | NaN | 26.0724
7042.1292 | 13.8817 | 13.5605 | 13.6143 | 13.8627 | 13.3266 | 13.6719 | 13.3132 | 13.1173 | NaN | NaN | NaN | 13.3555 | 94.8372 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 616.9557 | NaN | 21.4377 | NaN | 24.7308
7043.1292 | 13.878 | 13.5831 | 13.6108 | 13.8569 | 13.2202 | 13.5926 | 13.3009 | 13.1146 | NaN | NaN | NaN | 13.4685 | 92.7302 | NaN | NaN | NaN | 20.1747 | NaN | NaN | NaN | NaN | 618.5007 | NaN | 18.4031 | NaN | 25.2465
7044.1292 | 13.8731 | 13.551 | 13.6105 | 13.8799 | 13.2725 | 13.5772 | 13.3044 | 13.1152 | NaN | NaN | NaN | 13.3861 | 92.4716 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 623.177 | NaN | 19.8517 | NaN | 26.3899
7045.1292 | 13.9183 | 13.57 | 13.617 | 13.8776 | 13.3053 | 13.6408 | 13.3045 | 13.1167 | NaN | NaN | NaN | 13.3366 | 94.7793 | NaN | NaN | NaN | 14.5961 | NaN | NaN | NaN | NaN | 624.1075 | NaN | 18.0982 | NaN | 24.8585
7046.1292 | 13.8427 | 13.5412 | 13.6142 | 13.8343 | 13.3092 | 13.5571 | 13.2831 | 13.1163 | NaN | NaN | NaN | 13.3576 | 93.3132 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 621.925 | NaN | 19.3096 | NaN | 26.4047
7047.1292 | 13.8955 | 13.5525 | 13.6103 | 13.8685 | 13.2561 | 13.5937 | 13.2875 | 13.1142 | NaN | NaN | NaN | 13.3694 | 91.3101 | NaN | NaN | NaN | 30.3583 | NaN | NaN | NaN | NaN | 620.7247 | NaN | 19.4702 | NaN | 25.1822
7048.1292 | 13.8957 | 13.5903 | 13.6135 | 13.8464 | 13.2846 | 13.648 | 13.2953 | 13.1134 | NaN | NaN | NaN | 13.3555 | 92.2859 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 617.5042 | NaN | 20.2923 | NaN | 26.2346
7049.1292 | 13.8828 | 13.5689 | 13.6078 | 13.9141 | 13.3784 | 13.7458 | 13.2824 | 13.117 | NaN | NaN | NaN | 13.3956 | 90.5029 | NaN | NaN | NaN | 15.6904 | NaN | NaN | NaN | NaN | 618.8824 | NaN | 17.053 | NaN | 24.7539
7050.1292 | 13.875 | 13.6339 | 13.6033 | 13.8755 | 13.3478 | 13.5898 | 13.2845 | 13.1235 | NaN | NaN | NaN | 13.376 | 91.6063 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 616.0505 | NaN | 18.2956 | NaN | 24.4916
7051.1292 | 13.9716 | 13.5704 | 13.607 | 13.8484 | 13.2654 | 13.6455 | 13.2775 | 13.125 | NaN | NaN | NaN | 13.3504 | 94.8847 | NaN | NaN | NaN | -9.3971 | NaN | NaN | NaN | NaN | 616.9265 | NaN | 19.451 | NaN | 23.7369
7052.1292 | 13.8741 | 13.5709 | 13.6037 | 14.0006 | 13.3883 | 13.5639 | 13.2723 | 13.1186 | NaN | NaN | NaN | 13.3399 | 91.7422 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 617.1994 | NaN | 17.2718 | NaN | 22.6158
7053.1292 | 13.9965 | 13.7331 | 13.6073 | 13.8607 | 13.3683 | 13.5745 | 13.3391 | 13.1249 | NaN | NaN | NaN | 13.3483 | 93.8327 | NaN | NaN | NaN | -2.3294 | NaN | NaN | NaN | NaN | 619.467 | NaN | 18.971 | NaN | 23.9257
7054.1292 | 13.8736 | 13.5513 | 13.6088 | 13.8582 | 13.3749 | 13.5629 | 13.2717 | 13.1226 | NaN | NaN | NaN | 13.4278 | 97.8257 | NaN | NaN | NaN | -7.4917 | NaN | NaN | NaN | NaN | 614.4048 | NaN | 19.771 | NaN | 26.814
7055.1292 | 13.8478 | 13.6401 | 13.6107 | 13.8703 | 13.3881 | 13.5991 | 13.2953 | 13.1266 | NaN | NaN | NaN | 13.3727 | 93.2632 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 613.5666 | NaN | 17.283 | NaN | 26.8103
7056.1292 | 13.8744 | 13.5583 | 13.6123 | 13.8783 | 13.422 | 13.6043 | 13.2842 | 13.1229 | NaN | NaN | NaN | 13.3693 | 90.8696 | NaN | NaN | NaN | 29.8367 | NaN | NaN | NaN | NaN | 607.9138 | NaN | 16.6726 | NaN | 26.2284
7057.1292 | 13.8639 | 13.56 | 13.6132 | 13.8774 | 13.3017 | 13.5623 | 13.2809 | 13.1253 | NaN | NaN | NaN | 13.5105 | 95.926 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 604.1497 | NaN | 17.6511 | NaN | 24.8781
7058.1292 | 13.8464 | 13.6657 | 13.6112 | 13.8872 | 13.377 | 13.6192 | 13.3036 | 13.1261 | NaN | NaN | NaN | 13.3715 | 91.8615 | NaN | NaN | NaN | 24.6443 | NaN | NaN | NaN | -3.5146 | 608.5126 | NaN | 18.8789 | NaN | 23.2662
7059.1292 | 13.9368 | 13.5765 | 13.615 | 13.8756 | 13.2871 | 13.5686 | 13.2796 | 13.1228 | NaN | NaN | NaN | 13.4476 | 105.7872 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 608.2136 | NaN | 20.5265 | NaN | 25.2721
7060.1292 | 13.8724 | 13.5977 | 13.6136 | 13.8884 | 13.3996 | 13.6161 | 13.2939 | 13.1218 | NaN | NaN | NaN | 13.3532 | 94.063 | NaN | NaN | NaN | 23.5752 | NaN | NaN | NaN | NaN | 608.7811 | NaN | 21.7278 | NaN | 24.6592
7061.1292 | 13.8654 | 13.5767 | 13.6159 | 13.8436 | 13.318 | 13.6511 | 13.284 | 13.1251 | NaN | NaN | NaN | 13.3607 | 92.5289 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 597.5191 | NaN | 16.935 | NaN | 25.0503
7062.1292 | 13.8748 | 13.6 | 13.6163 | 13.8471 | 13.269 | 13.5823 | 13.2928 | 13.1195 | NaN | NaN | NaN | 13.3375 | 94.9107 | NaN | NaN | NaN | 5.9006 | NaN | NaN | NaN | NaN | 596.2455 | NaN | 21.0876 | NaN | 26.3357
7063.1292 | 13.8473 | 13.5901 | 13.6147 | 13.8875 | 13.4325 | 13.6692 | 13.2979 | 13.1201 | NaN | NaN | NaN | 13.351 | 92.9986 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 593.468 | NaN | 15.5729 | NaN | 26.4328
7064.1292 | 13.8994 | 13.5806 | 13.611 | 13.8921 | 13.2607 | 13.6593 | 13.2913 | 13.12 | NaN | NaN | NaN | 13.3833 | 94.0576 | NaN | NaN | NaN | 1.4622 | NaN | NaN | NaN | NaN | 593.4694 | NaN | 19.4005 | NaN | 25.7045
7065.1292 | 13.8749 | 13.5699 | 13.612 | 13.8985 | 13.2833 | 13.568 | 13.2811 | 13.121 | NaN | NaN | NaN | 13.3752 | 93.2068 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 601.8046 | NaN | 19.9253 | NaN | 26.9017
7066.1292 | 13.8566 | 13.5519 | 13.6154 | 13.8519 | 13.3593 | 13.5678 | 13.2919 | 13.1225 | NaN | NaN | NaN | 13.365 | 98.9259 | NaN | NaN | NaN | 33 | NaN | NaN | NaN | NaN | 607.6936 | NaN | 18.2635 | NaN | 24.5469
7067.1292 | 13.8506 | 13.6311 | 13.6202 | 13.8455 | 13.411 | 13.5979 | 13.301 | 13.1189 | NaN | NaN | NaN | 13.335 | 92.8593 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -18.2659 | 608.6012 | NaN | 18.5949 | NaN | 23.2394
7068.1292 | 13.8234 | 13.6493 | 13.6127 | 13.8366 | 13.2853 | 13.6169 | 13.3085 | 13.1212 | NaN | NaN | NaN | 13.3583 | 93.3543 | NaN | NaN | NaN | 6.5074 | NaN | NaN | NaN | NaN | 607.9321 | NaN | 18.1579 | NaN | 22.3875
7069.1448 | 13.9015 | 13.5496 | 13.6188 | 13.872 | 13.4297 | 13.5414 | 13.28 | 13.1235 | NaN | NaN | NaN | 13.3656 | 100.207 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 602.7018 | NaN | 18.4764 | NaN | 25.7766
7070.1292 | 13.8653 | 13.5778 | 13.6117 | 13.867 | 13.2876 | 13.6259 | 13.302 | 13.1155 | NaN | NaN | NaN | 13.6461 | 92.1112 | NaN | NaN | NaN | -19.0614 | NaN | NaN | NaN | NaN | 606.4196 | NaN | 18.5307 | NaN | 24.0384
7071.1292 | 13.8663 | 13.7332 | 13.6177 | 13.8449 | 13.3871 | 13.5983 | 13.3124 | 13.1193 | NaN | NaN | NaN | 13.3435 | 96.2159 | NaN | NaN | NaN | -11.6765 | NaN | NaN | NaN | NaN | 606.7105 | NaN | 20.077 | NaN | 24.8639
7072.1292 | 13.8633 | 13.5982 | 13.6148 | 13.8558 | 13.3651 | 13.5932 | 13.2944 | 13.1185 | NaN | NaN | NaN | 13.3775 | 92.1258 | NaN | NaN | NaN | -1.2305 | NaN | NaN | NaN | NaN | 607.6191 | NaN | 18.3443 | NaN | 23.8669
7073.1292 | 13.8493 | 13.5535 | 13.6153 | 13.8819 | 13.3186 | 13.5721 | 13.2868 | 13.1217 | NaN | NaN | NaN | 13.3576 | 93.7406 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 607.4378 | NaN | 18.2608 | NaN | 25.3492
7074.1292 | 13.8548 | 13.5573 | 13.6184 | 13.8656 | 13.2614 | 13.5654 | 13.2785 | 13.1257 | NaN | NaN | NaN | 13.4529 | 94.949 | NaN | NaN | NaN | -12.2433 | NaN | NaN | NaN | NaN | 607.0847 | NaN | 17.5203 | NaN | 26.5836
7075.1292 | 14.012 | 13.5597 | 13.619 | 13.8745 | 13.3433 | 13.6014 | 13.3086 | 13.1232 | NaN | NaN | NaN | 13.381 | 91.3316 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 609.9803 | NaN | 17.9036 | NaN | 23.8259
7076.1292 | 13.8646 | 13.5558 | 13.6227 | 13.867 | 13.2733 | 13.5634 | 13.2982 | 13.1276 | NaN | NaN | NaN | 13.3652 | 93.1342 | NaN | NaN | NaN | -19.9235 | NaN | NaN | NaN | NaN | 610.8396 | NaN | 19.5139 | NaN | 23.9407
7077.1292 | 13.8411 | 13.6134 | 13.6202 | 13.9237 | 13.3848 | 13.5757 | 13.3205 | 13.123 | NaN | NaN | NaN | 13.367 | 108.2932 | NaN | NaN | NaN | -10.5053 | NaN | NaN | NaN | -8.4957 | 605.1302 | NaN | 17.5085 | NaN | 24.7515
7078.1292 | 13.8593 | 13.527 | 13.621 | 13.8415 | 13.3021 | 13.5636 | 13.2886 | 13.1264 | NaN | NaN | NaN | 13.3553 | 93.9514 | NaN | NaN | NaN | -17.0433 | NaN | NaN | NaN | NaN | 605.4214 | NaN | 21.8091 | NaN | 25.8099
7079.1292 | 13.8587 | 13.5254 | 13.6194 | 13.8597 | 13.3275 | 13.5497 | 13.2902 | 13.131 | NaN | NaN | NaN | 13.3564 | 96.7065 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 608.4609 | NaN | 22.07 | NaN | 24.3831
7080.1292 | 13.8491 | 13.6472 | 13.6191 | 13.8744 | 13.295 | 13.5606 | 13.3033 | 13.1322 | NaN | NaN | NaN | 13.3685 | 93.3161 | NaN | NaN | NaN | -1.7083 | NaN | NaN | NaN | NaN | 607.6755 | NaN | 18.0331 | NaN | 25.8005
7081.1292 | 13.8993 | 13.5456 | 13.6253 | 13.8234 | 13.2733 | 13.6872 | 13.2856 | 13.1259 | NaN | NaN | NaN | 13.3971 | 92.2743 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 607.2393 | NaN | 16.0767 | NaN | 24.5954
7082.1292 | 13.8759 | 13.5914 | 13.6213 | 13.8902 | 13.3285 | 13.5678 | 13.2943 | 13.1318 | NaN | NaN | NaN | 13.3638 | 91.1391 | NaN | NaN | NaN | 13.0017 | NaN | NaN | NaN | NaN | 601.2272 | NaN | 16.8919 | NaN | 25.0016
7083.1292 | 13.8733 | 13.5393 | 13.6229 | 13.8706 | 13.4433 | 13.5949 | 13.2975 | 13.1266 | NaN | NaN | NaN | 13.3794 | 95.7784 | NaN | NaN | NaN | -15.9933 | NaN | NaN | NaN | NaN | 603.6839 | NaN | 17.6236 | NaN | 25.4745
7084.1292 | 13.8851 | 13.5325 | 13.6251 | 13.8826 | 13.343 | 13.552 | 13.2759 | 13.1222 | NaN | NaN | NaN | 13.3614 | 92.7902 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 604.7892 | NaN | 18.5179 | NaN | 24.647
7085.1292 | 13.8714 | 13.5257 | 13.625 | 13.871 | 13.382 | 13.5455 | 13.2803 | 13.1261 | NaN | NaN | NaN | 13.4512 | 96.5195 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 601.7235 | NaN | 16.1729 | NaN | 25.7306
7086.1292 | 13.8781 | 13.5443 | 13.6276 | 13.8312 | 13.3135 | 13.6008 | 13.2896 | 13.1204 | NaN | NaN | NaN | 13.352 | 93.5902 | NaN | NaN | NaN | -14.2409 | NaN | NaN | NaN | NaN | 602.196 | NaN | 20.2064 | NaN | 24.4042
7087.1292 | 13.8523 | 13.5479 | 13.63 | 13.8682 | 13.4249 | 13.6581 | 13.2941 | 13.1216 | NaN | NaN | NaN | 13.4602 | 93.1823 | NaN | NaN | NaN | -12.5517 | NaN | NaN | NaN | NaN | 605.3195 | NaN | 20.0489 | NaN | 26.1702
7088.1292 | 13.8291 | 13.6017 | 13.6306 | 13.843 | 13.384 | 13.5702 | 13.2919 | 13.1189 | NaN | NaN | NaN | 13.3676 | 90.9413 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 608.5738 | NaN | 17.4219 | NaN | 23.1419
7089.1292 | 13.8957 | 13.5593 | 13.6276 | 13.8581 | 13.2961 | 13.6046 | 13.3086 | 13.1254 | NaN | NaN | NaN | 13.356 | 89.954 | NaN | NaN | NaN | 4.8007 | NaN | NaN | NaN | NaN | 609.516 | NaN | 19.8148 | NaN | 23.5263
7090.1292 | 13.8742 | 13.529 | 13.6306 | 13.8812 | 13.2857 | 13.5716 | 13.2895 | 13.1196 | NaN | NaN | NaN | 13.37 | 94.1987 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 611.3314 | NaN | 16.3289 | NaN | 26.1111
7091.1292 | 13.8589 | 13.583 | 13.6284 | 13.8132 | 13.3818 | 13.7349 | 13.3102 | 13.1219 | NaN | NaN | NaN | 13.4222 | 95.8418 | NaN | NaN | NaN | -9.008 | NaN | NaN | NaN | -19.6929 | 611.854 | NaN | 19.045 | NaN | 25.4507
7092.1292 | 13.9535 | 13.5461 | 13.6248 | 13.8875 | 13.285 | 13.588 | 13.3061 | 13.1171 | NaN | NaN | NaN | 13.4055 | 90.0634 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 613.8299 | NaN | 18.691 | NaN | 22.177
7093.1292 | 13.8758 | 13.5702 | 13.6335 | 13.8676 | 13.2927 | 13.5854 | 13.3019 | 13.1191 | NaN | NaN | NaN | 13.3874 | 94.8756 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 612.5602 | NaN | 16.7544 | NaN | 22.4437
7094.1292 | 13.8584 | 13.6748 | 13.6332 | 13.8283 | 13.3199 | 13.6296 | 13.3102 | 13.1181 | NaN | NaN | NaN | 13.3686 | 92.3765 | NaN | NaN | NaN | 16.5973 | NaN | NaN | NaN | NaN | 617.087 | NaN | 17.365 | NaN | 23.3477
7095.1448 | 13.9417 | 13.5552 | 13.6347 | 13.8233 | 13.3268 | 13.6043 | 13.2935 | 13.1186 | NaN | NaN | NaN | 13.3943 | 103.0354 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 614.2613 | NaN | 17.8634 | NaN | 22.9277
7096.1292 | 13.85 | 13.5586 | 13.6331 | 13.8441 | 13.2511 | 13.6318 | 13.3134 | 13.1211 | NaN | NaN | NaN | 13.3789 | 91.8086 | NaN | NaN | NaN | 5.6664 | NaN | NaN | NaN | NaN | 611.6143 | NaN | 19.1442 | NaN | 22.7177
7097.1292 | 14.1282 | 13.6357 | 13.6296 | 13.8103 | 13.3117 | 13.6171 | 13.3137 | 13.115 | NaN | NaN | NaN | 13.493 | 88.621 | NaN | NaN | NaN | -15.6671 | NaN | NaN | NaN | NaN | 613.2915 | NaN | 21.4726 | NaN | 23.9379
7098.1448 | 13.8835 | 13.5881 | 13.6338 | 13.891 | 13.2207 | 13.5979 | 13.3117 | 13.1239 | NaN | NaN | NaN | 13.3774 | 91.5907 | NaN | NaN | NaN | -18.0303 | NaN | NaN | NaN | NaN | 614.9412 | NaN | 16.4499 | NaN | 25.5254
7099.1292 | 13.8815 | 13.5391 | 13.636 | 13.8673 | 13.3899 | 13.5792 | 13.3025 | 13.1209 | NaN | NaN | NaN | 13.4646 | 95.4543 | NaN | NaN | NaN | -16.2991 | NaN | NaN | NaN | NaN | 610.9682 | NaN | 21.255 | NaN | 23.4228
7100.1292 | 13.8697 | 13.5564 | 13.6354 | 13.9081 | 13.3807 | 13.6752 | 13.3041 | 13.1215 | NaN | NaN | NaN | 13.6197 | 94.953 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 613.339 | NaN | 19.1002 | NaN | 26.5405
7101.1292 | 13.8776 | 13.5727 | 13.6369 | 13.8896 | 13.2418 | 13.6044 | 13.3099 | 13.1183 | NaN | NaN | NaN | 13.4116 | 92.6449 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 607.7332 | NaN | 15.9891 | NaN | 25.8007
7102.1292 | 13.8716 | 13.5984 | 13.6312 | 13.86 | 13.4001 | 13.6487 | 13.317 | 13.1268 | NaN | NaN | NaN | 13.4183 | 92.4394 | NaN | NaN | NaN | 15.1872 | NaN | NaN | NaN | NaN | 608.3613 | NaN | 20.1362 | NaN | 24.213
7103.1292 | 13.8618 | 13.5898 | 13.6242 | 13.8814 | 13.3946 | 13.6058 | 13.315 | 13.1244 | NaN | NaN | NaN | 13.3884 | 91.9525 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 605.751 | NaN | 16.8501 | NaN | 24.3777
7104.1292 | 13.8939 | 13.5871 | 13.6251 | 13.9016 | 13.2327 | 13.6224 | 13.3075 | 13.1193 | NaN | NaN | NaN | 13.3644 | 91.6969 | NaN | NaN | NaN | 5.1547 | NaN | NaN | NaN | NaN | 611.5349 | NaN | 17.6517 | NaN | 22.7189
7105.1292 | 13.8855 | 13.5949 | 13.6203 | 13.8496 | 13.3897 | 13.5873 | 13.3006 | 13.1233 | NaN | NaN | NaN | 13.3909 | 103.9651 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 615.3655 | NaN | 17.8393 | NaN | 25.3456
7106.1292 | 13.8858 | 13.6224 | 13.617 | 13.9255 | 13.3563 | 13.6341 | 13.3214 | 13.1293 | NaN | NaN | NaN | 13.3821 | 92.1202 | NaN | NaN | NaN | -11.7154 | NaN | NaN | NaN | NaN | 618.0147 | NaN | 17.1302 | NaN | 23.5887
7107.1292 | 13.8817 | 13.6838 | 13.6169 | 13.8703 | 13.3985 | 13.6311 | 13.3211 | 13.1268 | NaN | NaN | NaN | 13.5389 | 91.4921 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 611.3329 | NaN | 17.0723 | NaN | 25.7065
7108.1448 | 13.862 | 13.5422 | 13.6117 | 13.8823 | 13.3191 | 13.5837 | 13.2956 | 13.1188 | NaN | NaN | NaN | 13.4062 | 95.2033 | NaN | NaN | NaN | -6.1842 | NaN | NaN | NaN | -12.1745 | 611.1365 | NaN | 22.1206 | NaN | 24.4038
7109.1292 | 13.9045 | 13.5469 | 13.6173 | 13.8957 | 13.2922 | 13.5788 | 13.2845 | 13.1275 | NaN | NaN | NaN | 13.3762 | 92.0972 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 609.469 | NaN | 18.3965 | NaN | 25.6479
7110.1292 | 13.8756 | 13.6095 | 13.6199 | 13.8905 | 13.3067 | 13.6224 | 13.3078 | 13.121 | NaN | NaN | NaN | 13.3736 | 92.538 | NaN | NaN | NaN | -8.3893 | NaN | NaN | NaN | -14.0807 | 611.3874 | NaN | 18.387 | NaN | 25.0207
7111.1292 | 13.8775 | 13.5678 | 13.6235 | 13.8797 | 13.2862 | 13.6064 | 13.2906 | 13.1255 | NaN | NaN | NaN | 13.4968 | 91.1124 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 613.4796 | NaN | 15.367 | NaN | 24.552
7112.1292 | 13.8514 | 13.5956 | 13.6195 | 13.8965 | 13.2391 | 13.6473 | 13.3025 | 13.1259 | NaN | NaN | NaN | 13.4414 | 91.4104 | NaN | NaN | NaN | 12.54 | NaN | NaN | NaN | NaN | 611.7791 | NaN | 20.3538 | NaN | 25.081
7113.1292 | 13.886 | 13.5749 | 13.6286 | 13.8725 | 13.3513 | 13.5935 | 13.2906 | 13.1281 | NaN | NaN | NaN | 13.3873 | 94.7044 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 608.3373 | NaN | 19.8474 | NaN | 25.4998
7114.1292 | 13.8794 | 13.6317 | 13.6272 | 13.8923 | 13.321 | 13.6379 | 13.3149 | 13.13 | NaN | NaN | NaN | 13.478 | 93.448 | NaN | NaN | NaN | 1.7089 | NaN | NaN | NaN | -11.5643 | 606.2441 | NaN | 16.7822 | NaN | 24.262
7115.1292 | 13.8827 | 13.5718 | 13.6289 | 13.9135 | 13.4233 | 13.6152 | 13.2923 | 13.1314 | NaN | NaN | NaN | 13.3862 | 92.9124 | NaN | NaN | NaN | -19.364 | NaN | NaN | NaN | -14.2142 | 609.8994 | NaN | 17.3036 | NaN | 25.8683
7116.1292 | 13.8638 | 13.5605 | 13.6279 | 13.9082 | 13.4416 | 13.6595 | 13.2943 | 13.129 | NaN | NaN | NaN | 13.5537 | 92.5766 | NaN | NaN | NaN | -17.6885 | NaN | NaN | NaN | NaN | 611.1337 | NaN | 18.9511 | NaN | 24.1109
7117.1292 | 13.8459 | 13.595 | 13.6269 | 13.9182 | 13.3209 | 13.6058 | 13.3062 | 13.1215 | NaN | NaN | NaN | 13.4132 | 97.9066 | NaN | NaN | NaN | -12.3858 | NaN | NaN | NaN | NaN | 607.6482 | NaN | 21.6621 | NaN | 24.2808
7118.1292 | 13.9774 | 13.6815 | 13.6285 | 13.9129 | 13.3633 | 13.6332 | 13.3112 | 13.1286 | NaN | NaN | NaN | 13.4611 | 90.7022 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 609.9791 | NaN | 17.4842 | NaN | 22.6638
7119.1292 | 13.8656 | 13.585 | 13.6289 | 13.8814 | 13.3139 | 13.6527 | 13.2935 | 13.1343 | NaN | NaN | NaN | 13.3764 | 92.1211 | NaN | NaN | NaN | 3.7974 | NaN | NaN | NaN | NaN | 613.9189 | NaN | 18.0271 | NaN | 23.354
7120.1292 | 13.9114 | 13.6244 | 13.6237 | 13.9198 | 13.2949 | 13.5988 | 13.3174 | 13.1334 | NaN | NaN | NaN | 13.3955 | 92.505 | NaN | NaN | NaN | -17.6307 | NaN | NaN | NaN | NaN | 611.4725 | NaN | 17.8166 | NaN | 22.9751
7121.1292 | 13.8767 | 13.6397 | 13.6317 | 13.9242 | 13.3028 | 13.5985 | 13.3106 | 13.1352 | NaN | NaN | NaN | 13.4107 | 92.3578 | NaN | NaN | NaN | -17.9794 | NaN | NaN | NaN | NaN | 609.2762 | NaN | 17.4607 | NaN | 22.9411
7122.1448 | 13.8522 | 13.5914 | 13.6308 | 13.9226 | 13.3327 | 13.6114 | 13.3138 | 13.1358 | NaN | NaN | NaN | 13.4065 | 91.7086 | NaN | NaN | NaN | 28.1082 | NaN | NaN | NaN | NaN | 605.8006 | NaN | 19.458 | NaN | 24.6564
7123.1292 | 13.9037 | 13.6125 | 13.6322 | 13.9202 | 13.3992 | 13.6097 | 13.3211 | 13.1359 | NaN | NaN | NaN | 13.4336 | 95.8925 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 603.7003 | NaN | 17.2358 | NaN | 21.7019
7124.1292 | 13.8832 | 13.5594 | 13.6258 | 13.91 | 13.2929 | 13.6178 | 13.3052 | 13.1376 | NaN | NaN | NaN | 13.4193 | 99.3972 | NaN | NaN | NaN | -9.841 | NaN | NaN | NaN | 13.5279 | 605.3442 | NaN | 17.3138 | NaN | 24.4638
7125.1292 | 13.8886 | 13.5539 | 13.6248 | 13.9106 | 13.31 | 13.7659 | 13.3192 | 13.1412 | NaN | NaN | NaN | 13.4343 | 96.0543 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -1.241 | 612.9824 | NaN | 18.3251 | NaN | 25.1673
7126.1292 | 13.8955 | 13.5603 | 13.6234 | 13.9261 | 13.425 | 13.5858 | 13.3039 | 13.139 | NaN | NaN | NaN | 13.4193 | 94.4989 | NaN | NaN | NaN | 16.9252 | NaN | NaN | NaN | 24.4955 | 611.9595 | NaN | 20.2432 | NaN | 24.5907
7127.1292 | 13.8793 | 13.5541 | 13.6223 | 13.9141 | 13.391 | 13.6363 | 13.305 | 13.1385 | NaN | NaN | NaN | 13.4373 | 96.2157 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.1301 | 611.7872 | NaN | 19.4642 | NaN | 24.1777
7128.1292 | 13.9099 | 13.5561 | 13.622 | 13.9121 | 13.3742 | 13.6379 | 13.3119 | 13.1386 | NaN | NaN | NaN | 13.4592 | 93.5737 | NaN | NaN | NaN | -12.4904 | NaN | NaN | NaN | 11.9358 | 608.7774 | NaN | 19.1077 | NaN | 24.2871
7129.1448 | 14.0005 | 13.5716 | 13.6194 | 13.9467 | 13.2192 | 13.6448 | 13.3116 | 13.1479 | NaN | NaN | NaN | 13.4353 | 94.0677 | NaN | NaN | NaN | -11.354 | NaN | NaN | NaN | 14.6246 | 611.525 | NaN | 18.4052 | NaN | 27.0663
7130.1292 | 13.9059 | 13.5655 | 13.619 | 13.9277 | 13.3104 | 13.6125 | 13.3217 | 13.1408 | NaN | NaN | NaN | 13.5019 | 90.8313 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 609.8597 | NaN | 20.6471 | NaN | 27.1244
7131.1292 | 13.9016 | 13.5945 | 13.6154 | 13.8595 | 13.3597 | 13.694 | 13.3241 | 13.147 | NaN | NaN | NaN | 13.4509 | 91.9873 | NaN | NaN | NaN | -6.4522 | NaN | NaN | NaN | NaN | 609.229 | NaN | 18.3808 | NaN | 25.5657
7132.1292 | 13.9012 | 13.577 | 13.6126 | 13.8822 | 13.3606 | 13.6538 | 13.3211 | 13.1443 | NaN | NaN | NaN | 13.4855 | 93.5066 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 610.4012 | NaN | 16.0706 | NaN | 25.5068
7133.1292 | 13.8789 | 13.7373 | 13.6067 | 13.9026 | 13.3029 | 13.7245 | 13.3426 | 13.1436 | NaN | NaN | NaN | 13.4639 | 95.7668 | NaN | NaN | NaN | -7.2982 | NaN | NaN | NaN | 17.8208 | 609.416 | NaN | 19.5686 | NaN | 23.2781
7134.1292 | 13.8853 | 13.5915 | 13.5959 | 13.8996 | 13.3467 | 13.6068 | 13.322 | 13.1447 | NaN | NaN | NaN | 13.4839 | 105.1461 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.5271 | 610.9246 | NaN | 20.6726 | NaN | 27.355
7135.1292 | 13.936 | 13.8994 | 13.5966 | 13.9718 | 13.3621 | 13.757 | 13.3694 | 13.1456 | NaN | NaN | NaN | 13.6524 | 98.4493 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 23.7535 | 610.6438 | NaN | 15.8512 | NaN | 22.9647
7136.1292 | 13.9076 | 13.6075 | 13.5937 | 13.8648 | 13.3104 | 13.6211 | 13.3263 | 13.1504 | NaN | NaN | NaN | 13.5022 | 89.5157 | NaN | NaN | NaN | 23.2334 | NaN | NaN | NaN | 21.9008 | 609.1882 | NaN | 15.6176 | NaN | 25.5171
7137.1292 | 13.9029 | 13.6413 | 13.5997 | 13.8946 | 13.4144 | 13.695 | 13.3275 | 13.1487 | NaN | NaN | NaN | 13.4666 | 93.8915 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 28.2606 | 607.9318 | NaN | 18.7503 | NaN | 23.8661
7138.1292 | 13.8771 | 13.5893 | 13.6011 | 13.978 | 13.3362 | 13.6063 | 13.3196 | 13.1518 | NaN | NaN | NaN | 13.4552 | 102.3495 | NaN | NaN | NaN | 15.6568 | NaN | NaN | NaN | -1.5831 | 606.7827 | NaN | 19.7104 | NaN | 24.0749
7139.1292 | 13.9109 | 13.5757 | 13.6028 | 13.9162 | 13.4051 | 13.6454 | 13.3344 | 13.1513 | NaN | NaN | NaN | 13.4485 | 98.4045 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.116 | 601.3461 | NaN | 18.3569 | NaN | 22.7304
7140.1292 | 13.8989 | 13.5966 | 13.5953 | 13.8768 | 13.353 | 13.6916 | 13.3481 | 13.1534 | NaN | NaN | NaN | 13.4661 | 94.1951 | NaN | NaN | NaN | 13.5783 | NaN | NaN | NaN | 16.8493 | 606.1294 | NaN | 20.8055 | NaN | 23.845
7141.1292 | 13.8753 | 13.5795 | 13.5991 | 13.868 | 13.285 | 13.7085 | 13.3443 | 13.1567 | NaN | NaN | NaN | 13.4456 | 93.905 | NaN | NaN | NaN | -14.164 | NaN | NaN | NaN | 26.7843 | 600.3787 | NaN | 18.5583 | NaN | 25.4528
7142.1292 | 13.8369 | 13.6338 | 13.6008 | 13.9133 | 13.3706 | 13.6417 | 13.3459 | 13.1562 | NaN | NaN | NaN | 13.4617 | 93.3925 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.7706 | 599.4367 | NaN | 16.1563 | NaN | 23.2187
7143.1292 | 13.9195 | 13.5857 | 13.6066 | 13.9577 | 13.2515 | 13.6382 | 13.3289 | 13.1671 | NaN | NaN | NaN | 13.4599 | 104.0728 | NaN | NaN | NaN | 16.8601 | NaN | NaN | NaN | -9.4308 | 601.9025 | NaN | 15.7372 | NaN | 25.6139
7144.1292 | 13.9116 | 13.5766 | 13.5996 | 13.8974 | 13.3003 | 13.615 | 13.3391 | 13.1596 | NaN | NaN | NaN | 13.6054 | 96.2288 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.244 | 602.5186 | NaN | 16.1552 | NaN | 26.2388
7145.1292 | 13.9037 | 13.6734 | 13.6027 | 13.9059 | 13.2469 | 13.7402 | 13.3445 | 13.1553 | NaN | NaN | NaN | 13.4527 | 92.2751 | NaN | NaN | NaN | 5.9071 | NaN | NaN | NaN | 18.6142 | 603.0977 | NaN | 16.2487 | NaN | 22.1574
7146.1292 | 13.8933 | 13.5786 | 13.6066 | 13.9081 | 13.313 | 13.6155 | 13.335 | 13.1632 | NaN | NaN | NaN | 13.474 | 97.6917 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 17.3325 | 598.8637 | NaN | 17.6632 | NaN | 23.9077
7147.1292 | 13.8871 | 13.5867 | 13.6109 | 13.9 | 13.2894 | 13.6699 | 13.3422 | 13.1661 | NaN | NaN | NaN | 13.4588 | 93.5254 | NaN | NaN | NaN | 8.9365 | NaN | NaN | NaN | 11.4802 | 598.9718 | NaN | 15.8955 | NaN | 23.5235
7148.1292 | 13.9283 | 13.5864 | 13.6123 | 13.9112 | 13.3988 | 13.6227 | 13.3357 | 13.1675 | NaN | NaN | NaN | 13.489 | 91.1578 | NaN | NaN | NaN | 11.3281 | NaN | NaN | NaN | 13.669 | 595.3466 | NaN | 18.5842 | NaN | 24.4005
7149.1292 | 13.9061 | 13.6631 | 13.6122 | 13.874 | 13.2807 | 13.6655 | 13.376 | 13.1698 | NaN | NaN | NaN | 13.519 | 92.1188 | NaN | NaN | NaN | -17.1624 | NaN | NaN | NaN | 13.3374 | 598.0502 | NaN | 18.4494 | NaN | 22.3522
7150.1292 | 13.913 | 13.5816 | 13.6065 | 13.9093 | 13.395 | 13.6386 | 13.3429 | 13.1699 | NaN | NaN | NaN | 13.4837 | 93.2227 | NaN | NaN | NaN | -6.7173 | NaN | NaN | NaN | 24.5431 | 593.3684 | NaN | 15.5192 | NaN | 26.4872
7151.1292 | 13.9055 | 13.582 | 13.6135 | 13.9108 | 13.4125 | 13.6542 | 13.3549 | 13.1664 | NaN | NaN | NaN | 13.517 | 101.2091 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.4151 | 593.4902 | NaN | 17.528 | NaN | 26.0039
7152.1292 | 13.8878 | 13.6198 | 13.618 | 13.8831 | 13.3139 | 13.6673 | 13.361 | 13.1713 | NaN | NaN | NaN | 13.4859 | 92.6048 | NaN | NaN | NaN | 23.7742 | NaN | NaN | NaN | 21.4253 | 593.3617 | NaN | 20.4047 | NaN | 24.2231
7153.1292 | 13.9346 | 13.6628 | 13.619 | 13.876 | 13.2825 | 13.6821 | 13.3661 | 13.1762 | NaN | NaN | NaN | 13.4984 | 92.7885 | NaN | NaN | NaN | -15.7624 | NaN | NaN | NaN | -6.1512 | 593.0432 | NaN | 17.5841 | NaN | 24.4429
7154.1292 | 13.9289 | 13.6228 | 13.6234 | 13.9674 | 13.3995 | 13.6402 | 13.3559 | 13.1698 | NaN | NaN | NaN | 13.4963 | 92.3201 | NaN | NaN | NaN | -18.709 | NaN | NaN | NaN | NaN | 596.1674 | NaN | 19.092 | NaN | 23.9539
7155.1292 | 13.9105 | 13.6143 | 13.6247 | 13.8371 | 13.3745 | 13.7334 | 13.3646 | 13.1707 | NaN | NaN | NaN | 13.4983 | 94.3566 | NaN | NaN | NaN | -19.7816 | NaN | NaN | NaN | -12.3268 | 594.4524 | NaN | 16.739 | NaN | 24.3864
7156.1292 | 13.8915 | 13.6716 | 13.6224 | 13.994 | 13.2492 | 13.7039 | 13.3771 | 13.1705 | NaN | NaN | NaN | 13.5235 | 92.0207 | NaN | NaN | NaN | -2.5239 | NaN | NaN | NaN | NaN | 587.929 | NaN | 18.4092 | NaN | 26.8165
7157.1292 | 13.9319 | 13.5977 | 13.6278 | 13.9112 | 13.3602 | 13.6738 | 13.3556 | 13.173 | NaN | NaN | NaN | 13.4767 | 92.461 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 587.2855 | NaN | 17.5028 | NaN | 25.6597
7158.1292 | 13.9868 | 13.6174 | 13.6283 | 13.9089 | 13.4239 | 13.6494 | 13.3527 | 13.1706 | NaN | NaN | NaN | 13.4728 | 96.0593 | NaN | NaN | NaN | 1.5416 | NaN | NaN | NaN | NaN | 585.2438 | NaN | 18.7878 | NaN | 24.0527
7159.1448 | 13.9212 | 13.6654 | 13.6357 | 13.9198 | 13.3877 | 13.6523 | 13.3627 | 13.1766 | NaN | NaN | NaN | 13.4862 | 94.4127 | NaN | NaN | NaN | -19.3585 | NaN | NaN | NaN | NaN | 590.2678 | NaN | 22.1783 | NaN | 26.253
7160.1292 | 13.9169 | 13.6212 | 13.6313 | 13.9226 | 13.3783 | 13.6494 | 13.3706 | 13.1785 | NaN | NaN | NaN | 13.4725 | 100.5793 | NaN | NaN | NaN | -3.195 | NaN | NaN | NaN | NaN | 596.5987 | NaN | 20.2137 | NaN | 24.6269
7161.1292 | 13.9129 | 13.6159 | 13.6338 | 13.8756 | 13.4605 | 13.6638 | 13.3635 | 13.1781 | NaN | NaN | NaN | 13.507 | 97.4974 | NaN | NaN | NaN | -17.309 | NaN | NaN | NaN | NaN | 603.2098 | NaN | 21.8496 | NaN | 25.7891
7162.1292 | 13.877 | 13.6273 | 13.6363 | 13.8685 | 13.4329 | 13.6653 | 13.3619 | 13.1791 | NaN | NaN | NaN | 13.5228 | 89.2133 | NaN | NaN | NaN | -9.6546 | NaN | NaN | NaN | NaN | 597.6135 | NaN | 18.9388 | NaN | 25.649
7163.1292 | 13.9517 | 13.6746 | 13.6407 | 13.8695 | 13.3025 | 13.6821 | 13.3713 | 13.1761 | NaN | NaN | NaN | 13.5138 | 92.8393 | NaN | NaN | NaN | -6.944 | NaN | NaN | NaN | NaN | 594.3302 | NaN | 18.1701 | NaN | 26.882
7164.1292 | 13.9248 | 13.6306 | 13.6403 | 13.8898 | 13.2747 | 13.7477 | 13.3656 | 13.1776 | NaN | NaN | NaN | 13.5604 | 95.0212 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 588.7904 | NaN | 19.4481 | NaN | 23.9643
7165.1292 | 13.9222 | 13.5875 | 13.6369 | 13.9123 | 13.3245 | 13.6187 | 13.348 | 13.1714 | NaN | NaN | NaN | 13.486 | 93.8294 | NaN | NaN | NaN | 22.0307 | NaN | NaN | NaN | NaN | 590.5783 | NaN | 18.0154 | NaN | 23.9445
7166.1292 | 13.925 | 13.5929 | 13.6397 | 13.8867 | 13.3373 | 13.6375 | 13.3467 | 13.1742 | NaN | NaN | NaN | 13.6519 | 95.2962 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 592.7963 | NaN | 18.941 | NaN | 24.402
7167.1292 | 13.9205 | 13.6089 | 13.6393 | 13.9375 | 13.2658 | 13.7079 | 13.3688 | 13.1783 | NaN | NaN | NaN | 13.6415 | 93.5485 | NaN | NaN | NaN | 5.0574 | NaN | NaN | NaN | NaN | 596.1335 | NaN | 18.6841 | NaN | 24.2815
7168.1292 | 13.9057 | 13.6203 | 13.6447 | 13.9024 | 13.3595 | 13.6609 | 13.3575 | 13.1709 | NaN | NaN | NaN | 13.512 | 94.8996 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 599.2067 | NaN | 20.5373 | NaN | 24.9185
7169.1292 | 13.9305 | 13.7214 | 13.6359 | 13.9213 | 13.3342 | 13.7071 | 13.3816 | 13.1752 | NaN | NaN | NaN | 13.5 | 98.6405 | NaN | NaN | NaN | -10.2241 | NaN | NaN | NaN | NaN | 604.9422 | NaN | 18.5693 | NaN | 26.0251
7170.1292 | 13.8987 | 13.666 | 13.6391 | 14.0477 | 13.4245 | 13.6772 | 13.3753 | 13.1746 | NaN | NaN | NaN | 13.5247 | 94.4048 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 609.1294 | NaN | 18.0262 | NaN | 24.6772
7171.1292 | 14.1541 | 13.6491 | 13.6414 | 13.9386 | 13.405 | 13.7116 | 13.346 | 13.1782 | NaN | NaN | NaN | 13.5145 | 94.5951 | NaN | NaN | NaN | -10.8655 | NaN | NaN | NaN | NaN | 604.8476 | NaN | 17.2007 | NaN | 23.7821
7172.1292 | 13.9277 | 13.6241 | 13.6419 | 13.9384 | 13.4356 | 13.6709 | 13.3582 | 13.173 | NaN | NaN | NaN | 13.5153 | 94.1595 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 604.1533 | NaN | 15.646 | NaN | 22.8395
7173.1292 | 13.9203 | 13.6027 | 13.6408 | 13.9576 | 13.3474 | 13.6698 | 13.3626 | 13.1786 | NaN | NaN | NaN | 13.5743 | 94.2466 | NaN | NaN | NaN | -17.8655 | NaN | NaN | NaN | NaN | 607.4086 | NaN | 18.5777 | NaN | 21.8871
7174.1292 | 13.9171 | 13.6324 | 13.6428 | 13.9346 | 13.4454 | 13.6804 | 13.3634 | 13.1794 | NaN | NaN | NaN | 13.5422 | 91.6164 | NaN | NaN | NaN | -12.9874 | NaN | NaN | NaN | NaN | 609.0651 | NaN | 18.2696 | NaN | 23.7422
7175.1292 | 14.0076 | 13.6218 | 13.6367 | 13.9061 | 13.3598 | 13.6285 | 13.3595 | 13.1817 | NaN | NaN | NaN | 13.4944 | 92.3776 | NaN | NaN | NaN | -12.8522 | NaN | NaN | NaN | NaN | 609.6139 | NaN | 19.8737 | NaN | 23.5216
7176.1292 | 13.9237 | 13.6314 | 13.646 | 13.9192 | 13.3489 | 13.6696 | 13.3691 | 13.1779 | NaN | NaN | NaN | 13.4725 | 93.6078 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 611.5708 | NaN | 19.7506 | NaN | 22.464
7177.1292 | 13.9317 | 13.6513 | 13.64 | 13.9377 | 13.4022 | 13.6516 | 13.3623 | 13.1826 | NaN | NaN | NaN | 13.4686 | 95.0572 | NaN | NaN | NaN | -9.7124 | NaN | NaN | NaN | NaN | 607.3798 | NaN | 17.8238 | NaN | 25.9576
7178.1292 | 13.9231 | 13.626 | 13.6373 | 13.9653 | 13.3008 | 13.6709 | 13.3692 | 13.1797 | NaN | NaN | NaN | 13.5561 | 96.7075 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 610.1559 | NaN | 20.5912 | NaN | 25.7714
7179.1292 | 13.8797 | 13.6603 | 13.643 | 13.9625 | 13.2593 | 13.6492 | 13.3642 | 13.179 | NaN | NaN | NaN | 13.7213 | 93.8051 | NaN | NaN | NaN | -11.2127 | NaN | NaN | NaN | NaN | 610.129 | NaN | 20.6974 | NaN | 22.6875
7180.1292 | 13.9025 | 13.6576 | 13.6437 | 13.9245 | 13.3673 | 13.6594 | 13.37 | 13.1822 | NaN | NaN | NaN | 13.5095 | 89.1667 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 611.0768 | NaN | 13.9869 | NaN | 24.5749
7181.1292 | 13.938 | 13.6065 | 13.645 | 13.9025 | 13.3515 | 13.6111 | 13.3495 | 13.1819 | NaN | NaN | NaN | 13.4832 | 91.6478 | NaN | NaN | NaN | -6.5548 | NaN | NaN | NaN | NaN | 606.9161 | NaN | 16.1612 | NaN | 22.7456
7182.1292 | 13.888 | 13.645 | 13.6427 | 13.9228 | 13.3551 | 13.651 | 13.3631 | 13.1789 | NaN | NaN | NaN | 13.4909 | 105.7357 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -19.6193 | 608.7426 | NaN | 15.6332 | NaN | 24.0372
7183.1292 | 13.9135 | 13.6625 | 13.6454 | 13.8821 | 13.3836 | 13.6649 | 13.3668 | 13.1854 | NaN | NaN | NaN | 13.5052 | 93.3638 | NaN | NaN | NaN | 5.5136 | NaN | NaN | NaN | NaN | 608.7386 | NaN | 16.0916 | NaN | 24.8802
7184.1292 | 14.0167 | 13.6088 | 13.6544 | 13.9383 | 13.3475 | 13.6176 | 13.3548 | 13.1837 | NaN | NaN | NaN | 13.4837 | 94.9251 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 611.333 | NaN | 15.0078 | NaN | 23.6418
7185.1292 | 14.0288 | 13.6258 | 13.6405 | 13.9223 | 13.4342 | 13.6445 | 13.3723 | 13.1862 | NaN | NaN | NaN | 13.6217 | 92.6203 | NaN | NaN | NaN | -2.9914 | NaN | NaN | NaN | NaN | 607.5423 | NaN | 20.1122 | NaN | 23.1389
7186.1292 | 13.9285 | 13.7246 | 13.6491 | 13.9369 | 13.3229 | 13.6417 | 13.3681 | 13.1813 | NaN | NaN | NaN | 13.5538 | 102.5079 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 597.6047 | NaN | 15.992 | NaN | 20.5025
7187.1292 | 13.8816 | 13.6253 | 13.6474 | 13.9368 | 13.3827 | 13.6227 | 13.3649 | 13.1807 | NaN | NaN | NaN | 13.4936 | 94.3253 | NaN | NaN | NaN | -11.8258 | NaN | NaN | NaN | NaN | 599.2843 | NaN | 20.4695 | NaN | 21.6257
7188.1292 | 13.8939 | 13.633 | 13.6453 | 13.9516 | 13.403 | 13.6385 | 13.3676 | 13.1822 | NaN | NaN | NaN | 13.5182 | 94.2273 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 605.2089 | NaN | 19.5253 | NaN | 24.2778
7189.1448 | 13.9737 | 13.6599 | 13.6438 | 13.9313 | 13.3779 | 13.7468 | 13.3726 | 13.1857 | NaN | NaN | NaN | 13.4831 | 92.5 | NaN | NaN | NaN | -5.4427 | NaN | NaN | NaN | -6.3218 | 611.0562 | NaN | 19.3021 | NaN | 25.2305
7190.1292 | 13.9106 | 13.63 | 13.6432 | 14.0105 | 13.3535 | 13.6555 | 13.3667 | 13.1844 | NaN | NaN | NaN | 13.5116 | 94.3935 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 611.2687 | NaN | 16.1563 | NaN | 23.8003
7191.1292 | 13.8951 | 13.6491 | 13.6449 | 13.95 | 13.3179 | 13.6362 | 13.366 | 13.1815 | NaN | NaN | NaN | 13.4856 | 93.1682 | NaN | NaN | NaN | 20.4289 | NaN | NaN | NaN | 7.0117 | 607.8221 | NaN | 17.6494 | NaN | 24.565
7192.1292 | 13.9249 | 13.6287 | 13.64 | 13.9733 | 13.4455 | 13.6252 | 13.3592 | 13.1779 | NaN | NaN | NaN | 13.5056 | 94.5483 | NaN | NaN | NaN | -16.3511 | NaN | NaN | NaN | -13.4345 | 607.1273 | NaN | 19.1737 | NaN | 25.7731
7193.1292 | 13.9924 | 13.6806 | 13.6556 | 14.0122 | 13.4453 | 13.7586 | 13.4016 | 13.1866 | NaN | NaN | NaN | 13.5095 | 102.032 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 612.1532 | NaN | 16.2004 | NaN | 21.1942
7194.1292 | 13.9281 | 13.7442 | 13.6492 | 13.9329 | 13.4024 | 13.6494 | 13.3925 | 13.1871 | NaN | NaN | NaN | 13.4935 | 93.69 | NaN | NaN | NaN | -13.0609 | NaN | NaN | NaN | NaN | 610.9802 | NaN | 18.0343 | NaN | 25.0871
7195.1292 | 13.9095 | 13.6899 | 13.6569 | 13.937 | 13.3548 | 13.6575 | 13.3813 | 13.1869 | NaN | NaN | NaN | 13.4776 | 100.9581 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 614.9329 | NaN | 18.3816 | NaN | 22.5152
7196.1292 | 13.894 | 13.6634 | 13.6478 | 13.9543 | 13.399 | 13.641 | 13.3891 | 13.1885 | NaN | NaN | NaN | 13.4809 | 93.5827 | NaN | NaN | NaN | -10.9997 | NaN | NaN | NaN | NaN | 612.7725 | NaN | 17.745 | NaN | 26.9531
7197.1292 | 13.882 | 13.8239 | 13.6505 | 13.9047 | 13.4025 | 13.6872 | 13.4294 | 13.1936 | NaN | NaN | NaN | 13.4817 | 90.7168 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 616.0164 | NaN | 16.291 | NaN | 21.6758
7198.1292 | 13.9376 | 13.7683 | 13.6535 | 13.9536 | 13.3745 | 13.6346 | 13.3946 | 13.1873 | NaN | NaN | NaN | 13.5276 | 91.3567 | NaN | NaN | NaN | -4.5991 | NaN | NaN | NaN | NaN | 614.5469 | NaN | 17.2823 | NaN | 23.0569
7199.1292 | 13.9187 | 13.6388 | 13.657 | 13.9395 | 13.3208 | 13.6114 | 13.3624 | 13.1894 | NaN | NaN | NaN | 13.5162 | 93.9142 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 616.7169 | NaN | 15.9707 | NaN | 26.802
7200.1292 | 13.9024 | 13.6604 | 13.6567 | 13.9237 | 13.34 | 13.6957 | 13.3964 | 13.1847 | NaN | NaN | NaN | 13.521 | 93.2322 | NaN | NaN | NaN | 0.7403 | NaN | NaN | NaN | NaN | 616.886 | NaN | 19.2655 | NaN | 23.9676
7201.1292 | 13.9007 | 13.775 | 13.6622 | 13.953 | 13.3486 | 13.6483 | 13.3995 | 13.1907 | NaN | NaN | NaN | 13.4953 | 97.1776 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 617.2916 | NaN | 18.8169 | NaN | 21.7845
7202.1292 | 13.931 | 13.6417 | 13.6592 | 13.9353 | 13.4177 | 13.5996 | 13.3668 | 13.1916 | NaN | NaN | NaN | 13.526 | 104.4586 | NaN | NaN | NaN | -2.3683 | NaN | NaN | NaN | NaN | 616.3109 | NaN | 17.3432 | NaN | 20.6954
7203.1292 | 13.8732 | 13.6362 | 13.6656 | 13.9543 | 13.4482 | 13.7025 | 13.3934 | 13.1932 | NaN | NaN | NaN | 13.582 | 91.7484 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 620.8439 | NaN | 18.8652 | NaN | 22.8313
7204.1292 | 13.9477 | 13.6726 | 13.6627 | 13.9506 | 13.4817 | 13.6798 | 13.3897 | 13.1943 | NaN | NaN | NaN | 13.4755 | 87.9356 | NaN | NaN | NaN | 11.0934 | NaN | NaN | NaN | NaN | 618.6318 | NaN | 17.1042 | NaN | 26.8762
7205.1292 | 13.9225 | 13.6721 | 13.6679 | 13.9411 | 13.31 | 13.6321 | 13.3905 | 13.1943 | NaN | NaN | NaN | 13.512 | 94.7076 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 618.4428 | NaN | 16.4697 | NaN | 24.6544
7206.1292 | 13.8703 | 13.6755 | 13.6758 | 13.9488 | 13.4023 | 13.6359 | 13.3979 | 13.1946 | NaN | NaN | NaN | 13.487 | 91.3291 | NaN | NaN | NaN | 24.8546 | NaN | NaN | NaN | NaN | 620.345 | NaN | 16.5835 | NaN | 24.6306
7207.1292 | 14.0354 | 13.6334 | 13.6755 | 13.9449 | 13.3684 | 13.6087 | 13.3766 | 13.1919 | NaN | NaN | NaN | 13.4607 | 96.0934 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 622.6255 | NaN | 17.1882 | NaN | 22.8875
7208.1292 | 13.9458 | 13.7295 | 13.6743 | 13.9611 | 13.419 | 13.6633 | 13.3993 | 13.1938 | NaN | NaN | NaN | 13.4455 | 92.5584 | NaN | NaN | NaN | 4.1462 | NaN | NaN | NaN | NaN | 623.1055 | NaN | 18.0059 | NaN | 24.4729
7209.1292 | 13.9442 | 13.7682 | 13.6804 | 13.9116 | 13.4104 | 13.7151 | 13.4129 | 13.1984 | NaN | NaN | NaN | 13.5423 | 89.6802 | NaN | NaN | NaN | -13.4631 | NaN | NaN | NaN | NaN | 622.2501 | NaN | 19.3017 | NaN | 24.239
7210.1292 | 14.1414 | 13.6576 | 13.672 | 13.99 | 13.3196 | 13.6322 | 13.3946 | 13.1958 | NaN | NaN | NaN | 13.5622 | 93.0363 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 623.5578 | NaN | 15.9114 | NaN | 23.652
7211.1292 | 13.9173 | 13.6748 | 13.6825 | 13.9085 | 13.4088 | 13.6636 | 13.3829 | 13.1908 | NaN | NaN | NaN | 13.492 | 94.0514 | NaN | NaN | NaN | -19.0551 | NaN | NaN | NaN | NaN | 619.8023 | NaN | 19.8316 | NaN | 23.1203
7212.1292 | 13.9233 | 13.7117 | 13.6816 | 13.9383 | 13.4417 | 13.6245 | 13.391 | 13.1985 | NaN | NaN | NaN | 13.468 | 92.1791 | NaN | NaN | NaN | -11.4485 | NaN | NaN | NaN | NaN | 618.1577 | NaN | 17.7949 | NaN | 26.05
7213.1292 | 13.9015 | 13.6886 | 13.6842 | 13.9562 | 13.4601 | 13.6534 | 13.4003 | 13.1946 | NaN | NaN | NaN | 13.4503 | 92.7115 | NaN | NaN | NaN | -12.2144 | NaN | NaN | NaN | NaN | 620.28 | NaN | 17.4815 | NaN | 25.6022
7214.1292 | 13.9055 | 13.6725 | 13.6772 | 13.9687 | 13.4309 | 13.6096 | 13.3728 | 13.1974 | NaN | NaN | NaN | 13.4755 | 93.5531 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 615.6393 | NaN | 18.2811 | NaN | 25.0815
7215.1292 | 13.9051 | 13.6909 | 13.687 | 13.9197 | 13.4088 | 13.6512 | 13.3717 | 13.202 | NaN | NaN | NaN | 13.4715 | 94.4893 | NaN | NaN | NaN | -12.1669 | NaN | NaN | NaN | NaN | 616.5721 | NaN | 18.6521 | NaN | 24.3877
7216.1292 | 13.9012 | 13.7145 | 13.6827 | 13.9444 | 13.3477 | 13.6705 | 13.389 | 13.2015 | NaN | NaN | NaN | 13.4786 | 90.6941 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 620.6709 | NaN | 16.1969 | NaN | 26.383
7217.1292 | 13.8669 | 13.8091 | 13.6812 | 14.0697 | 13.298 | 13.6473 | 13.4016 | 13.1978 | NaN | NaN | NaN | 13.4469 | 95.4075 | NaN | NaN | NaN | -0.6519 | NaN | NaN | NaN | NaN | 618.467 | NaN | 14.3293 | NaN | 25.0871
7218.1292 | 13.9164 | 13.6496 | 13.6786 | 13.9644 | 13.3822 | 13.6091 | 13.3675 | 13.2011 | NaN | NaN | NaN | 13.4678 | 98.6984 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 618.9478 | NaN | 16.5077 | NaN | 22.1359
7219.1448 | 13.9158 | 13.7026 | 13.677 | 13.9738 | 13.3842 | 13.6052 | 13.3719 | 13.201 | NaN | NaN | NaN | 13.4748 | 90.9397 | NaN | NaN | NaN | -15.8851 | NaN | NaN | NaN | NaN | 613.486 | NaN | 15.6208 | NaN | 25.9475
7220.1292 | 13.9078 | 13.9191 | 13.6738 | 14.012 | 13.3285 | 13.8128 | 13.4113 | 13.1959 | NaN | NaN | NaN | 13.4718 | 91.259 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -3.6354 | 617.7534 | NaN | 15.9495 | NaN | 24.1805
7221.1292 | 13.9055 | 13.6866 | 13.6727 | 13.9644 | 13.3345 | 13.6535 | 13.3919 | 13.2 | NaN | NaN | NaN | 13.4762 | 96.1239 | NaN | NaN | NaN | -14.3822 | NaN | NaN | NaN | NaN | 615.8279 | NaN | 16.6574 | NaN | 24.0797
7222.1292 | 13.8763 | 13.8049 | 13.6794 | 13.9819 | 13.3668 | 13.6891 | 13.4082 | 13.1956 | NaN | NaN | NaN | 13.4687 | 98.497 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 617.1892 | NaN | 14.4452 | NaN | 25.2348
7223.1292 | 13.9782 | 13.7993 | 13.6724 | 13.9453 | 13.3419 | 13.7425 | 13.4026 | 13.194 | NaN | NaN | NaN | 13.4404 | 97.6071 | NaN | NaN | NaN | -6.7418 | NaN | NaN | NaN | NaN | 620.9023 | NaN | 16.779 | NaN | 24.7522
7224.1292 | 13.9022 | 13.6743 | 13.6725 | 13.9597 | 13.43 | 13.63 | 13.3764 | 13.1967 | NaN | NaN | NaN | 13.4648 | 95.8557 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 621.028 | NaN | 17.4087 | NaN | 24.3744
7225.1292 | 13.8461 | 13.6801 | 13.6719 | 13.9694 | 13.3417 | 13.6647 | 13.393 | 13.1955 | NaN | NaN | NaN | 13.4733 | 90.9861 | NaN | NaN | NaN | 31.8451 | NaN | NaN | NaN | NaN | 620.2982 | NaN | 17.1622 | NaN | 24.3668
7226.1292 | 13.9123 | 13.6834 | 13.6656 | 13.9548 | 13.4131 | 13.6486 | 13.3803 | 13.1942 | NaN | NaN | NaN | 13.4937 | 92.3604 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 620.7232 | NaN | 17.6422 | NaN | 25.9044
7227.1292 | 13.9099 | 13.6846 | 13.6716 | 13.9631 | 13.3787 | 13.6639 | 13.391 | 13.1932 | NaN | NaN | NaN | 13.4904 | 89.0453 | NaN | NaN | NaN | -14.315 | NaN | NaN | NaN | -11.3225 | 620.16 | NaN | 17.948 | NaN | 26.8347
7228.1292 | 13.8825 | 13.6846 | 13.663 | 13.9384 | 13.4084 | 13.6711 | 13.3837 | 13.1983 | NaN | NaN | NaN | 13.5269 | 95.9482 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 623.5469 | NaN | 15.4628 | NaN | 23.907
7229.1292 | 13.9227 | 13.6609 | 13.6648 | 14.0608 | 13.45 | 13.6448 | 13.3826 | 13.2027 | NaN | NaN | NaN | 13.4531 | 92.6701 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 619.5413 | NaN | 17.0707 | NaN | 22.0581
7230.1292 | 13.9266 | 13.7017 | 13.6682 | 13.9664 | 13.4506 | 13.6792 | 13.3846 | 13.1973 | NaN | NaN | NaN | 13.4575 | 92.7449 | NaN | NaN | NaN | 9.1205 | NaN | NaN | NaN | -15.4333 | 621.6981 | NaN | 17.1517 | NaN | 20.198
7231.1292 | 13.9135 | 13.677 | 13.659 | 13.9348 | 13.4523 | 13.6337 | 13.3689 | 13.1959 | NaN | NaN | NaN | 13.418 | 92.9742 | NaN | NaN | NaN | -18.1058 | NaN | NaN | NaN | NaN | 619.8339 | NaN | 16.8275 | NaN | 23.1852
7232.1292 | 13.9035 | 13.711 | 13.6623 | 13.9622 | 13.4305 | 13.6842 | 13.3832 | 13.203 | NaN | NaN | NaN | 13.4761 | 92.0533 | NaN | NaN | NaN | -7.6495 | NaN | NaN | NaN | NaN | 620.1164 | NaN | 17.886 | NaN | 25.3317
7233.1292 | 13.9372 | 13.6796 | 13.6628 | 13.9496 | 13.4561 | 13.6568 | 13.3785 | 13.1969 | NaN | NaN | NaN | 13.4537 | 104.234 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 619.305 | NaN | 20.6497 | NaN | 23.6485
7234.1292 | 13.8852 | 13.6768 | 13.6657 | 13.9668 | 13.3622 | 13.6621 | 13.378 | 13.2091 | NaN | NaN | NaN | 13.4652 | 93.3052 | NaN | NaN | NaN | 3.64 | NaN | NaN | NaN | NaN | 617.9013 | NaN | 15.3516 | NaN | 23.8706
7235.1292 | 13.9253 | 13.7066 | 13.6567 | 13.9744 | 13.3662 | 13.6767 | 13.3859 | 13.2036 | NaN | NaN | NaN | 13.4464 | 101.0817 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 615.727 | NaN | 19.5193 | NaN | 24.337
7236.1292 | 13.9927 | 13.6953 | 13.6661 | 13.9827 | 13.4308 | 13.688 | 13.3868 | 13.2111 | NaN | NaN | NaN | 13.4611 | 95.3568 | NaN | NaN | NaN | 17.1868 | NaN | NaN | NaN | NaN | 613.0872 | NaN | 17.1595 | NaN | 22.0345
7237.1292 | 13.9215 | 13.6952 | 13.6641 | 13.9528 | 13.4395 | 13.6884 | 13.3795 | 13.2106 | NaN | NaN | NaN | 13.4414 | 91.7026 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 611.6112 | NaN | 16.5916 | NaN | 21.7973
7238.1292 | 13.923 | 13.7925 | 13.6697 | 13.97 | 13.3377 | 13.7548 | 13.392 | 13.2089 | NaN | NaN | NaN | 13.4978 | 93.8758 | NaN | NaN | NaN | 30.5284 | NaN | NaN | NaN | NaN | 614.6172 | NaN | 14.3513 | NaN | 21.0171
7239.1292 | 14.0169 | 13.9093 | 13.6656 | 13.9314 | 13.3745 | 13.8447 | 13.4051 | 13.2049 | NaN | NaN | NaN | 13.4227 | 90.7309 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 613.777 | NaN | 17.5702 | NaN | 24.0462
7240.1292 | 13.9119 | 13.7962 | 13.6719 | 13.9136 | 13.3106 | 13.755 | 13.3887 | 13.2119 | NaN | NaN | NaN | 13.4311 | 93.0442 | NaN | NaN | NaN | 23.6277 | NaN | NaN | NaN | NaN | 604.9453 | NaN | 16.8303 | NaN | 24.9834
7241.1292 | 13.9136 | 13.7185 | 13.6664 | 13.9088 | 13.3273 | 13.7026 | 13.3751 | 13.2102 | NaN | NaN | NaN | 13.4261 | 93.6394 | NaN | NaN | NaN | -19.9558 | NaN | NaN | NaN | NaN | 602.7688 | NaN | 16.7863 | NaN | 24.2701
7242.1292 | 13.9183 | 13.7194 | 13.6671 | 13.9637 | 13.3254 | 13.6656 | 13.3765 | 13.2102 | NaN | NaN | NaN | 13.4359 | 93.0269 | NaN | NaN | NaN | 0.3414 | NaN | NaN | NaN | NaN | 602.7022 | NaN | 18.4909 | NaN | 24.4069
7243.1292 | 13.9116 | 13.7644 | 13.6654 | 13.9615 | 13.3735 | 13.74 | 13.377 | 13.2144 | NaN | NaN | NaN | 13.4208 | 94.2322 | NaN | NaN | NaN | -18.0874 | NaN | NaN | NaN | NaN | 606.4322 | NaN | 16.525 | NaN | 23.8488
7244.1292 | 13.9124 | 13.9657 | 13.6669 | 13.9461 | 13.2792 | 13.8114 | 13.3988 | 13.2091 | NaN | NaN | NaN | 13.3961 | 96.3089 | NaN | NaN | NaN | -14.0571 | NaN | NaN | NaN | NaN | 613.3384 | NaN | 16.9938 | NaN | 25.392
7245.1292 | 13.8942 | 13.7527 | 13.672 | 13.9509 | 13.2511 | 13.6973 | 13.3822 | 13.2092 | NaN | NaN | NaN | 13.4522 | 96.0011 | NaN | NaN | NaN | -8.0019 | NaN | NaN | NaN | 14.9443 | 611.6523 | NaN | 15.8621 | NaN | 24.6552
7246.1292 | 14.0118 | 13.6699 | 13.6698 | 13.9765 | 13.4533 | 13.6628 | 13.3797 | 13.211 | NaN | NaN | NaN | 13.4006 | 93.7156 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.9006 | 613.7016 | NaN | 17.249 | NaN | 24.0595
7247.1292 | 13.9169 | 13.7066 | 13.671 | 13.9754 | 13.3932 | 13.6824 | 13.3807 | 13.2146 | NaN | NaN | NaN | 13.3973 | 92.2253 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.5361 | 618.7883 | NaN | 17.1603 | NaN | 24.3614
7248.1292 | 13.9524 | 13.7364 | 13.6681 | 13.9746 | 13.3485 | 13.7141 | 13.4002 | 13.2147 | NaN | NaN | NaN | 13.4096 | 91.1815 | NaN | NaN | NaN | 18.1549 | NaN | NaN | NaN | 21.8773 | 617.6215 | NaN | 19.9672 | NaN | 24.7356
7249.1292 | 14.0721 | 13.7685 | 13.6757 | 13.9463 | 13.449 | 13.756 | 13.4133 | 13.2133 | NaN | NaN | NaN | 13.5091 | 91.4162 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -4.815 | 618.8509 | NaN | 20.7513 | NaN | 21.7986
7250.1292 | 13.9577 | 13.6718 | 13.6733 | 13.9925 | 13.3311 | 13.6823 | 13.3854 | 13.2181 | NaN | NaN | NaN | 13.4099 | 90.9132 | NaN | NaN | NaN | 24.2613 | NaN | NaN | NaN | NaN | 616.9776 | NaN | 15.6914 | NaN | 24.5454
7251.1292 | 13.9174 | 13.7419 | 13.6779 | 14.0071 | 13.315 | 13.7027 | 13.4119 | 13.2143 | NaN | NaN | NaN | 13.4252 | 93.1752 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -4.6987 | 615.4888 | NaN | 16.3497 | NaN | 22.7707
7252.1292 | 13.9176 | 13.7242 | 13.6736 | 13.958 | 13.4263 | 13.7177 | 13.3973 | 13.2207 | NaN | NaN | NaN | 13.4175 | 94.4038 | NaN | NaN | NaN | -0.0473 | NaN | NaN | NaN | 16.4111 | 617.201 | NaN | 15.3916 | NaN | 24.6109
7253.1292 | 13.9004 | 13.712 | 13.6804 | 13.9762 | 13.2998 | 13.6901 | 13.3839 | 13.2158 | NaN | NaN | NaN | 13.4775 | 95.6975 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.4851 | 616.4196 | NaN | 17.8018 | NaN | 25.0575
7254.1292 | 13.891 | 13.6726 | 13.683 | 13.9309 | 13.3756 | 13.6672 | 13.3764 | 13.2199 | NaN | NaN | NaN | 13.4164 | 102.0125 | NaN | NaN | NaN | -11.7142 | NaN | NaN | NaN | 20.5039 | 619.0437 | NaN | 17.4748 | NaN | 24.5429
7255.1292 | 13.8828 | 13.7209 | 13.6738 | 13.9274 | 13.3884 | 13.725 | 13.3952 | 13.2193 | NaN | NaN | NaN | 13.4032 | 93.2472 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.8319 | 616.0759 | NaN | 17.6236 | NaN | 23.5925
7256.1292 | 13.9544 | 13.7706 | 13.676 | 13.9604 | 13.3515 | 13.7311 | 13.3879 | 13.2201 | NaN | NaN | NaN | 13.4286 | 95.2378 | NaN | NaN | NaN | -6.602 | NaN | NaN | NaN | 15.0611 | 614.3004 | NaN | 15.3944 | NaN | 22.0756
7257.1292 | 14.0136 | 13.6927 | 13.6809 | 13.9529 | 13.3559 | 13.7092 | 13.401 | 13.2218 | NaN | NaN | NaN | 13.411 | 92.3209 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.4674 | 619.3299 | NaN | 18.5609 | NaN | 23.0029
7258.1292 | 13.9246 | 13.658 | 13.6783 | 13.9699 | 13.3605 | 13.674 | 13.3909 | 13.2279 | NaN | NaN | NaN | 13.3796 | 94.6327 | NaN | NaN | NaN | 10.7484 | NaN | NaN | NaN | 12.4745 | 614.3785 | NaN | 16.4342 | NaN | 23.8496
7259.1292 | 13.9228 | 13.7382 | 13.674 | 13.9789 | 13.4076 | 13.7049 | 13.3989 | 13.2226 | NaN | NaN | NaN | 13.4003 | 101.8818 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 22.1149 | 616.805 | NaN | 17.3084 | NaN | 24.6836
7260.1292 | 13.9193 | 13.6865 | 13.6731 | 13.9327 | 13.3175 | 13.7257 | 13.392 | 13.2298 | NaN | NaN | NaN | 13.381 | 90.9313 | NaN | NaN | NaN | 6.3517 | NaN | NaN | NaN | 9.8736 | 618.5738 | NaN | 17.0618 | NaN | 23.7791
7261.1292 | 14.0446 | 13.6998 | 13.6749 | 13.9495 | 13.3468 | 13.7089 | 13.3893 | 13.2247 | NaN | NaN | NaN | 13.4222 | 92.1777 | NaN | NaN | NaN | -10.2019 | NaN | NaN | NaN | 19.0775 | 616.1677 | NaN | 15.8913 | NaN | 23.7277
7262.1292 | 13.932 | 13.7837 | 13.6767 | 13.9845 | 13.3804 | 13.7678 | 13.3955 | 13.2234 | NaN | NaN | NaN | 13.4798 | 89.9429 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 19.0523 | 618.3296 | NaN | 16.9021 | NaN | 25.1111
7263.1292 | 13.9318 | 13.6771 | 13.6765 | 13.9371 | 13.3768 | 13.7049 | 13.3704 | 13.2287 | NaN | NaN | NaN | 13.409 | 92.7088 | NaN | NaN | NaN | -4.7599 | NaN | NaN | NaN | 19.4685 | 618.1578 | NaN | 15.5368 | NaN | 25.664
7264.1292 | 13.923 | 13.6812 | 13.673 | 13.9757 | 13.4081 | 13.6939 | 13.3822 | 13.2282 | NaN | NaN | NaN | 13.4067 | 93.2188 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 21.1783 | 616.0645 | NaN | 17.0206 | NaN | 24.4047
7265.1292 | 13.9284 | 13.7023 | 13.6781 | 13.9971 | 13.4335 | 13.7146 | 13.3654 | 13.226 | NaN | NaN | NaN | 13.3801 | 95.8001 | NaN | NaN | NaN | 2.2358 | NaN | NaN | NaN | NaN | 615.0668 | NaN | 15.9484 | NaN | 24.423
7266.1292 | 13.9239 | 13.8105 | 13.6834 | 13.937 | 13.4147 | 13.6888 | 13.378 | 13.23 | NaN | NaN | NaN | 13.3741 | 93.1045 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -11.5566 | 613.9896 | NaN | 17.5618 | NaN | 26.2653
7267.1292 | 13.9153 | 13.7276 | 13.6789 | 13.9435 | 13.3522 | 13.7132 | 13.3759 | 13.2284 | NaN | NaN | NaN | 13.3708 | 96.7176 | NaN | NaN | NaN | 26.4437 | NaN | NaN | NaN | -11.519 | 617.616 | NaN | 16.9763 | NaN | 24.0693
7268.1292 | 13.9187 | 13.7372 | 13.6822 | 13.9571 | 13.3148 | 13.7096 | 13.3826 | 13.227 | NaN | NaN | NaN | 13.7016 | 93.2841 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 617.215 | NaN | 16.4614 | NaN | 25.1132
7269.1292 | 13.9123 | 13.7644 | 13.6776 | 13.9703 | 13.4513 | 13.7486 | 13.387 | 13.2245 | NaN | NaN | NaN | 13.3834 | 89.141 | NaN | NaN | NaN | 27.3137 | NaN | NaN | NaN | NaN | 615.0302 | NaN | 17.8558 | NaN | 24.0448
7270.1292 | 14.0055 | 13.7273 | 13.6773 | 13.9643 | 13.2896 | 13.7388 | 13.3851 | 13.2266 | NaN | NaN | NaN | 13.3903 | 101.5895 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 618.9648 | NaN | 15.4652 | NaN | 25.3284
7271.1292 | 13.9187 | 13.7041 | 13.6813 | 13.9962 | 13.4042 | 13.688 | 13.3733 | 13.2246 | NaN | NaN | NaN | 13.4095 | 97.3686 | NaN | NaN | NaN | -7.7833 | NaN | NaN | NaN | NaN | 612.763 | NaN | 16.4552 | NaN | 24.3222
7272.1292 | 13.9215 | 13.7295 | 13.6879 | 13.9341 | 13.4364 | 13.7468 | 13.3785 | 13.2265 | NaN | NaN | NaN | 13.4891 | 91.8208 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 612.7346 | NaN | 16.6493 | NaN | 22.8935
7273.1292 | 13.9106 | 13.6936 | 13.6802 | 13.9071 | 13.4117 | 13.718 | 13.3872 | 13.2199 | NaN | NaN | NaN | 13.3774 | 92.4267 | NaN | NaN | NaN | -11.8358 | NaN | NaN | NaN | NaN | 615.6936 | NaN | 17.0106 | NaN | 23.753
7274.1292 | 13.902 | 13.7252 | 13.6877 | 13.9621 | 13.429 | 13.7351 | 13.3983 | 13.2327 | NaN | NaN | NaN | 13.3994 | 95.485 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -9.2309 | 617.8486 | NaN | 15.0501 | NaN | 19.7538
7275.1292 | 13.8896 | 13.695 | 13.6887 | 13.9626 | 13.3461 | 13.7099 | 13.385 | 13.2249 | NaN | NaN | NaN | 13.3783 | 90.7725 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.7077 | 615.4383 | NaN | 18.5718 | NaN | 23.7104
7276.1292 | 13.9224 | 13.6765 | 13.6943 | 14.0511 | 13.4597 | 13.7188 | 13.3889 | 13.2235 | NaN | NaN | NaN | 13.3855 | 94.7515 | NaN | NaN | NaN | 18.3301 | NaN | NaN | NaN | 15.8228 | 617.2579 | NaN | 18.2454 | NaN | 24.5603
7277.1292 | 13.8921 | 13.7199 | 13.6816 | 13.9658 | 13.3514 | 13.7512 | 13.3913 | 13.2228 | NaN | NaN | NaN | 13.3779 | 98.9132 | NaN | NaN | NaN | -15.2833 | NaN | NaN | NaN | 13.106 | 615.2157 | NaN | 19.2431 | NaN | 23.7847
7278.1292 | 13.9434 | 13.7242 | 13.6947 | 14.0077 | 13.4437 | 13.7315 | 13.3942 | 13.2235 | NaN | NaN | NaN | 13.3285 | 93.2412 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 23.8024 | 615.4445 | NaN | 17.497 | NaN | 23.5156
7279.1292 | 14.1109 | 13.6925 | 13.689 | 13.9829 | 13.3612 | 13.7129 | 13.3842 | 13.2226 | NaN | NaN | NaN | 13.3512 | 90.9658 | NaN | NaN | NaN | -14.9789 | NaN | NaN | NaN | 20.2949 | 615.0998 | NaN | 20.3753 | NaN | 22.9795
7280.1292 | 13.9035 | 13.7528 | 13.6873 | 13.9841 | 13.3135 | 13.7639 | 13.3977 | 13.2307 | NaN | NaN | NaN | 13.4466 | 92.7404 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 20.8061 | 615.6853 | NaN | 19.82 | NaN | 24.2157
7281.1292 | 13.8976 | 13.702 | 13.69 | 13.9543 | 13.3411 | 13.7188 | 13.3877 | 13.2283 | NaN | NaN | NaN | 13.3836 | 92.9107 | NaN | NaN | NaN | -19.9248 | NaN | NaN | NaN | 11.6299 | 614.5936 | NaN | 16.6826 | NaN | 25.1114
7282.1292 | 13.906 | 13.755 | 13.6891 | 13.9346 | 13.3975 | 13.7447 | 13.4055 | 13.2308 | NaN | NaN | NaN | 13.3937 | 103.2536 | NaN | NaN | NaN | 11.8128 | NaN | NaN | NaN | 26.2146 | 615.186 | NaN | 19.0183 | NaN | 24.8153
7283.1292 | 13.8888 | 13.7259 | 13.6903 | 13.9611 | 13.314 | 13.7678 | 13.4012 | 13.2236 | NaN | NaN | NaN | 13.4071 | 91.3716 | NaN | NaN | NaN | -15.7002 | NaN | NaN | NaN | 19.5728 | 618.232 | NaN | 17.7672 | NaN | 24.9599
7284.1292 | 13.8766 | 13.6963 | 13.6864 | 13.9751 | 13.4031 | 13.7777 | 13.402 | 13.2266 | NaN | NaN | NaN | 13.5296 | 101.734 | NaN | NaN | NaN | 0.193 | NaN | NaN | NaN | 21.1338 | 618.6488 | NaN | 17.8387 | NaN | 24.2694
7285.1292 | 13.9232 | 13.6992 | 13.6891 | 13.9768 | 13.4824 | 13.7432 | 13.389 | 13.2289 | NaN | NaN | NaN | 13.3935 | 92.2511 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.9961 | 615.9602 | NaN | 18.3441 | NaN | 24.333
7286.1292 | 13.914 | 13.6564 | 13.6952 | 13.965 | 13.4374 | 13.7254 | 13.3917 | 13.2357 | NaN | NaN | NaN | 13.3678 | 94.6297 | NaN | NaN | NaN | 12.702 | NaN | NaN | NaN | 24.3486 | 619.3355 | NaN | 15.9723 | NaN | 24.6923
7287.1292 | 13.9117 | 13.6818 | 13.69 | 13.9666 | 13.3529 | 13.7322 | 13.3912 | 13.2289 | NaN | NaN | NaN | 13.3882 | 92.7458 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -4.9032 | 616.8552 | NaN | 17.3135 | NaN | 23.9889
7288.1292 | 13.9075 | 13.7689 | 13.6911 | 14.0117 | 13.2883 | 13.826 | 13.4048 | 13.2289 | NaN | NaN | NaN | 13.4782 | 93.8092 | NaN | NaN | NaN | 18.0321 | NaN | NaN | NaN | 15.6975 | 618.7636 | NaN | 17.4327 | NaN | 23.6016
7289.1292 | 13.9107 | 13.6923 | 13.6864 | 13.9772 | 13.4003 | 13.7117 | 13.3806 | 13.2291 | NaN | NaN | NaN | 13.3827 | 93.5603 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.2119 | 615.1021 | NaN | 14.3226 | NaN | 24.0174
7290.1292 | 13.8994 | 13.7682 | 13.691 | 13.989 | 13.3627 | 13.7571 | 13.4088 | 13.2301 | NaN | NaN | NaN | 13.3597 | 91.8432 | NaN | NaN | NaN | 19.4883 | NaN | NaN | NaN | 16.7811 | 616.5865 | NaN | 16.1118 | NaN | 25.972
7291.1292 | 13.8997 | 13.7365 | 13.689 | 13.8935 | 13.3006 | 13.7383 | 13.418 | 13.2354 | NaN | NaN | NaN | 13.3814 | 97.9601 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 17.1903 | 617.839 | NaN | 16.0888 | NaN | 22.3956
7292.1292 | 13.9157 | 13.6878 | 13.6862 | 13.9777 | 13.3541 | 13.7284 | 13.3897 | 13.2288 | NaN | NaN | NaN | 13.3806 | 96.2112 | NaN | NaN | NaN | 19.0172 | NaN | NaN | NaN | -18.3635 | 616.0404 | NaN | 14.9129 | NaN | 22.0859
7293.1292 | 13.9026 | 13.7736 | 13.6936 | 13.9763 | 13.2949 | 13.7668 | 13.4081 | 13.2253 | NaN | NaN | NaN | 13.3396 | 92.801 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 618.3432 | NaN | 15.9401 | NaN | 23.4092
7294.1292 | 13.903 | 13.6679 | 13.693 | 13.9743 | 13.4307 | 13.7316 | 13.4029 | 13.2313 | NaN | NaN | NaN | 13.3628 | 93.6594 | NaN | NaN | NaN | 17.7272 | NaN | NaN | NaN | NaN | 619.8963 | NaN | 17.7333 | NaN | 22.0081
7295.1292 | 13.905 | 13.6756 | 13.6857 | 13.9825 | 13.3934 | 13.7332 | 13.4028 | 13.2338 | NaN | NaN | NaN | 13.3918 | 94.5042 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 619.2872 | NaN | 14.8893 | NaN | 22.8568
7296.1292 | 13.8788 | 13.6541 | 13.6905 | 13.9806 | 13.4564 | 13.7379 | 13.3866 | 13.2233 | NaN | NaN | NaN | 13.4132 | 91.4431 | NaN | NaN | NaN | 22.0001 | NaN | NaN | NaN | NaN | 617.8901 | NaN | 17.2452 | NaN | 24.384
7297.1292 | 13.884 | 13.6944 | 13.6969 | 13.9346 | 13.3877 | 13.7766 | 13.3959 | 13.2274 | NaN | NaN | NaN | 13.5174 | 92.9954 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 620.0904 | NaN | 17.3075 | NaN | 23.0427
7298.1292 | 13.9152 | 13.7082 | 13.694 | 13.9748 | 13.2929 | 13.7324 | 13.407 | 13.23 | NaN | NaN | NaN | 13.375 | 93.8705 | NaN | NaN | NaN | 21.6253 | NaN | NaN | NaN | NaN | 621.6242 | NaN | 17.0454 | NaN | 21.9272
7299.1292 | 13.8943 | 13.7414 | 13.6836 | 13.9809 | 13.4435 | 13.7673 | 13.4212 | 13.2313 | NaN | NaN | NaN | 13.383 | 94.8016 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 618.8258 | NaN | 16.3343 | NaN | 24.2572
7300.1292 | 13.8855 | 13.7624 | 13.6874 | 13.957 | 13.3689 | 13.8188 | 13.41 | 13.227 | NaN | NaN | NaN | 13.4264 | 91.4811 | NaN | NaN | NaN | -17.4522 | NaN | NaN | NaN | NaN | 621.2607 | NaN | 18.4085 | NaN | 23.6836
7301.1292 | 13.8697 | 13.6682 | 13.6826 | 13.947 | 13.4244 | 13.7625 | 13.4133 | 13.2317 | NaN | NaN | NaN | 13.3584 | 93.8994 | NaN | NaN | NaN | -5.5191 | NaN | NaN | NaN | NaN | 622.0274 | NaN | 16.0584 | NaN | 24.6317
7302.1292 | 13.9211 | 13.6533 | 13.6796 | 13.9685 | 13.3804 | 13.759 | 13.4053 | 13.2301 | NaN | NaN | NaN | 13.3515 | 97.2139 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 620.4716 | NaN | 15.498 | NaN | 24.1541
7303.1292 | 14.0101 | 13.9236 | 13.6892 | 13.8952 | 13.3814 | 13.7379 | 13.4311 | 13.2257 | NaN | NaN | NaN | 13.375 | 90.4707 | NaN | NaN | NaN | 1.8419 | NaN | NaN | NaN | NaN | 619.0752 | NaN | 16.6347 | NaN | 25.3291
7304.1292 | 13.9086 | 13.6527 | 13.685 | 13.9396 | 13.3116 | 13.7439 | 13.3942 | 13.2312 | NaN | NaN | NaN | 13.3868 | 92.9243 | NaN | NaN | NaN | -19.852 | NaN | NaN | NaN | NaN | 619.2385 | NaN | 14.8874 | NaN | 25.7905
7305.1292 | 13.9 | 13.6799 | 13.6736 | 14.053 | 13.4101 | 13.7289 | 13.4014 | 13.2288 | NaN | NaN | NaN | 13.3729 | 93.1796 | NaN | NaN | NaN | 6.1904 | NaN | NaN | NaN | NaN | 618.4895 | NaN | 15.0517 | NaN | 24.181
7306.1292 | 13.9044 | 13.6328 | 13.6854 | 13.9774 | 13.3516 | 13.7214 | 13.3886 | 13.2261 | NaN | NaN | NaN | 13.3468 | 90.8749 | NaN | NaN | NaN | -14.5059 | NaN | NaN | NaN | NaN | 619.1875 | NaN | 19.0979 | NaN | 24.1934
7307.1292 | 13.9094 | 13.6257 | 13.6794 | 14.0291 | 13.3263 | 13.7347 | 13.3874 | 13.2311 | NaN | NaN | NaN | 13.4022 | 94.6075 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 617.3111 | NaN | 19.0148 | NaN | 22.7206
7308.1292 | 13.8945 | 13.6437 | 13.6781 | 13.9456 | 13.3138 | 13.7451 | 13.4012 | 13.2291 | NaN | NaN | NaN | 13.4006 | 94.5181 | NaN | NaN | NaN | -7.6498 | NaN | NaN | NaN | NaN | 619.3749 | NaN | 16.295 | NaN | 22.394
7309.1292 | 13.8808 | 13.6392 | 13.6756 | 13.9659 | 13.3835 | 13.7397 | 13.3988 | 13.2215 | NaN | NaN | NaN | 13.4016 | 93.678 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 618.4988 | NaN | 20.8927 | NaN | 21.5213
7310.1292 | 13.8473 | 13.7368 | 13.6754 | 13.9498 | 13.355 | 13.7565 | 13.412 | 13.2269 | NaN | NaN | NaN | 13.3755 | 98.1403 | NaN | NaN | NaN | -5.8184 | NaN | NaN | NaN | NaN | 617.5161 | NaN | 15.9569 | NaN | 19.6101
7311.1292 | 13.9085 | 13.6192 | 13.6701 | 13.9431 | 13.3604 | 13.7226 | 13.3932 | 13.2256 | NaN | NaN | NaN | 13.3852 | 96.787 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 617.2769 | NaN | 17.6132 | NaN | 24.0757
7312.1292 | 13.9023 | 13.8109 | 13.6706 | 13.944 | 13.2881 | 13.7502 | 13.4137 | 13.2235 | NaN | NaN | NaN | 13.3513 | 94.3132 | NaN | NaN | NaN | -2.4982 | NaN | NaN | NaN | -19.6981 | 617.2863 | NaN | 14.0293 | NaN | 24.6018
7313.1292 | 13.9099 | 13.7716 | 13.6718 | 13.9834 | 13.2695 | 13.7965 | 13.4206 | 13.2266 | NaN | NaN | NaN | 13.4012 | 94.6513 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 616.9531 | NaN | 16.4253 | NaN | 23.2376
7314.1292 | 13.9591 | 13.6522 | 13.6737 | 14.0182 | 13.308 | 13.7593 | 13.4037 | 13.2238 | NaN | NaN | NaN | 13.3299 | 93.822 | NaN | NaN | NaN | 24.0488 | NaN | NaN | NaN | NaN | 617.4574 | NaN | 15.9997 | NaN | 22.1524
7315.1292 | 13.9057 | 13.769 | 13.6724 | 14.0058 | 13.4433 | 13.8209 | 13.4254 | 13.2241 | NaN | NaN | NaN | 13.3224 | 97.407 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 613.9056 | NaN | 18.9263 | NaN | 24.8238
7316.1292 | 13.8962 | 13.6658 | 13.6714 | 13.9665 | 13.3259 | 13.7496 | 13.4128 | 13.226 | NaN | NaN | NaN | 13.3283 | 93.2433 | NaN | NaN | NaN | 16.7566 | NaN | NaN | NaN | NaN | 617.2289 | NaN | 18.6574 | NaN | 23.9134
7317.1292 | 13.8946 | 13.6077 | 13.6715 | 13.9268 | 13.3245 | 13.6853 | 13.3862 | 13.2272 | NaN | NaN | NaN | 13.356 | 93.2448 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 620.4913 | NaN | 18.2262 | NaN | 24.3068
7318.1292 | 13.896 | 13.6187 | 13.6696 | 13.9818 | 13.4197 | 13.7084 | 13.4019 | 13.216 | NaN | NaN | NaN | 13.3737 | 96.1748 | NaN | NaN | NaN | -10.7938 | NaN | NaN | NaN | NaN | 618.4093 | NaN | 16.15 | NaN | 22.8847
7319.1292 | 13.8992 | 13.6783 | 13.6732 | 13.964 | 13.4112 | 13.7238 | 13.4101 | 13.2142 | NaN | NaN | NaN | 13.3454 | 102.7809 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 616.3317 | NaN | 16.3089 | NaN | 23.7783
7320.1292 | 13.8895 | 13.6684 | 13.6728 | 13.9589 | 13.3333 | 13.7532 | 13.4135 | 13.2245 | NaN | NaN | NaN | 13.3267 | 95.5628 | NaN | NaN | NaN | -4.6537 | NaN | NaN | NaN | NaN | 619.5745 | NaN | 17.4058 | NaN | 23.6642
7321.1292 | 13.8753 | 13.6867 | 13.6644 | 13.9624 | 13.4641 | 13.7617 | 13.4056 | 13.2235 | NaN | NaN | NaN | 13.4138 | 96.8751 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 619.9109 | NaN | 18.4433 | NaN | 20.8912
7322.1292 | 13.8688 | 13.6725 | 13.6705 | 13.9844 | 13.3705 | 13.7224 | 13.4116 | 13.2234 | NaN | NaN | NaN | 13.3403 | 91.4454 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 618.5671 | NaN | 15.0761 | NaN | 25.0564
7323.1292 | 13.9066 | 13.6352 | 13.6702 | 13.9491 | 13.3502 | 13.7183 | 13.4077 | 13.2214 | NaN | NaN | NaN | 13.3569 | 98.2247 | NaN | NaN | NaN | 8.4268 | NaN | NaN | NaN | NaN | 615.8518 | NaN | 18.6334 | NaN | 25.2564
7324.1292 | 13.8943 | 13.6368 | 13.6717 | 13.9969 | 13.3048 | 13.692 | 13.4031 | 13.2194 | NaN | NaN | NaN | 13.3501 | 92.7297 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 615.8398 | NaN | 17.1028 | NaN | 25.8377
7325.1292 | 13.8906 | 13.6218 | 13.6739 | 13.9549 | 13.3651 | 13.7027 | 13.4024 | 13.2215 | NaN | NaN | NaN | 13.4205 | 95.4109 | NaN | NaN | NaN | 23.1815 | NaN | NaN | NaN | NaN | 615.8805 | NaN | 19.3693 | NaN | 25.9683
7326.1292 | 13.8925 | 13.7024 | 13.6694 | 13.9557 | 13.4246 | 13.7479 | 13.4156 | 13.2204 | NaN | NaN | NaN | 13.3275 | 91.1185 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 619.8811 | NaN | 16.4793 | NaN | 25.3692
7327.1292 | 13.8477 | 13.6369 | 13.6718 | 13.9515 | 13.3168 | 13.715 | 13.4075 | 13.2235 | NaN | NaN | NaN | 13.392 | 90.4192 | NaN | NaN | NaN | 17.8148 | NaN | NaN | NaN | -15.374 | 619.655 | NaN | 16.5291 | NaN | 24.419
7328.1292 | 13.8674 | 13.6285 | 13.6758 | 13.9962 | 13.2464 | 13.6906 | 13.3941 | 13.2211 | NaN | NaN | NaN | 13.4124 | 93.7063 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 619.7882 | NaN | 19.2055 | NaN | 25.4251
7329.1292 | 13.9009 | 13.6272 | 13.6755 | 14.0225 | 13.3564 | 13.7019 | 13.4006 | 13.2233 | NaN | NaN | NaN | 13.3701 | 100.2948 | NaN | NaN | NaN | 13.1464 | NaN | NaN | NaN | NaN | 618.1886 | NaN | 18.5348 | NaN | 25.5735
7330.1292 | 13.8606 | 13.6495 | 13.6725 | 13.9848 | 13.4105 | 13.7243 | 13.4063 | 13.2337 | NaN | NaN | NaN | 13.3227 | 98.459 | NaN | NaN | NaN | -19.9938 | NaN | NaN | NaN | NaN | 618.8652 | NaN | 17.1069 | NaN | 23.813
7331.1292 | 13.9451 | 13.622 | 13.6784 | 14.1944 | 13.3608 | 13.6815 | 13.3892 | 13.2343 | NaN | NaN | NaN | 13.3257 | 92.1169 | NaN | NaN | NaN | 4.066 | NaN | NaN | NaN | NaN | 621.6789 | NaN | 19.1242 | NaN | 26.4962
7332.1292 | 13.8302 | 13.7145 | 13.6763 | 13.9776 | 13.436 | 13.7459 | 13.4 | 13.2327 | NaN | NaN | NaN | 13.3549 | 87.6781 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 618.9744 | NaN | 15.3601 | NaN | 25.4594
7333.1292 | 13.8866 | 13.6484 | 13.6754 | 14.002 | 13.4027 | 13.7284 | 13.4087 | 13.2245 | NaN | NaN | NaN | 13.3619 | 98.4733 | NaN | NaN | NaN | 3.9759 | NaN | NaN | NaN | NaN | 619.6669 | NaN | 17.0218 | NaN | 24.249
7334.1292 | 13.875 | 13.6587 | 13.6748 | 13.9354 | 13.2776 | 13.7347 | 13.4155 | 13.232 | NaN | NaN | NaN | 13.3499 | 96.7923 | NaN | NaN | NaN | -17.1489 | NaN | NaN | NaN | 3.5157 | 620.0671 | NaN | 16.3824 | NaN | 21.3099
7335.1292 | 13.8684 | 13.7007 | 13.6774 | 13.9685 | 13.4488 | 13.7294 | 13.4117 | 13.2294 | NaN | NaN | NaN | 13.3682 | 98.1574 | NaN | NaN | NaN | -14.2425 | NaN | NaN | NaN | 20.2644 | 620.1033 | NaN | 16.7693 | NaN | 24.1943
7336.1292 | 13.95 | 13.6675 | 13.6743 | 13.9358 | 13.3481 | 13.7219 | 13.4059 | 13.2333 | NaN | NaN | NaN | 13.4361 | 90.1997 | NaN | NaN | NaN | -9.1966 | NaN | NaN | NaN | 16.4274 | 619.5558 | NaN | 18.5315 | NaN | 22.7947
7337.1292 | 13.8907 | 13.7065 | 13.6757 | 13.9863 | 13.4451 | 13.742 | 13.4194 | 13.2352 | NaN | NaN | NaN | 13.3965 | 93.2283 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 621.6647 | NaN | 20.1553 | NaN | 24.6597
7338.1292 | 13.8627 | 13.7 | 13.6792 | 14.0391 | 13.4014 | 13.7374 | 13.4139 | 13.2309 | NaN | NaN | NaN | 13.4651 | 91.3338 | NaN | NaN | NaN | -17.5667 | NaN | NaN | NaN | NaN | 618.6459 | NaN | 18.7243 | NaN | 22.783
7339.1292 | 13.8628 | 13.6699 | 13.6738 | 13.9739 | 13.4206 | 13.7422 | 13.4061 | 13.2291 | NaN | NaN | NaN | 13.4025 | 93.2608 | NaN | NaN | NaN | 0.9024 | NaN | NaN | NaN | NaN | 619.8602 | NaN | 19.0045 | NaN | 24.5053
7340.1292 | 13.8555 | 13.6869 | 13.6813 | 14.0496 | 13.3625 | 13.7166 | 13.4225 | 13.2275 | NaN | NaN | NaN | 13.3387 | 100.2224 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 618.7614 | NaN | 17.0042 | NaN | 25.8375
7341.1292 | 14.1591 | 13.7146 | 13.678 | 13.9748 | 13.4361 | 13.7446 | 13.4135 | 13.2321 | NaN | NaN | NaN | 13.3424 | 94.8017 | NaN | NaN | NaN | -6.5945 | NaN | NaN | NaN | NaN | 618.3418 | NaN | 15.1401 | NaN | 22.6236
7342.1292 | 13.8781 | 13.6535 | 13.6782 | 13.9625 | 13.4018 | 13.6989 | 13.4031 | 13.2272 | NaN | NaN | NaN | 13.3282 | 94.5018 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 618.9908 | NaN | 17.8569 | NaN | 25.1996
7343.1292 | 13.856 | 13.6602 | 13.6811 | 13.9561 | 13.3802 | 13.7211 | 13.4065 | 13.2282 | NaN | NaN | NaN | 13.3447 | 95.0101 | NaN | NaN | NaN | -5.5942 | NaN | NaN | NaN | NaN | 613.2904 | NaN | 16.1687 | NaN | 24.8888
7344.1292 | 13.8922 | 13.636 | 13.6781 | 13.9746 | 13.2999 | 13.6848 | 13.3981 | 13.2293 | NaN | NaN | NaN | 13.3627 | 94.064 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 611.0573 | NaN | 17.49 | NaN | 24.4401
7345.1292 | 13.8695 | 13.7088 | 13.6753 | 14.0166 | 13.4066 | 13.7041 | 13.4222 | 13.2327 | NaN | NaN | NaN | 13.341 | 104.9456 | NaN | NaN | NaN | -9.4456 | NaN | NaN | NaN | NaN | 615.8002 | NaN | 17.1173 | NaN | 24.3578
7346.1292 | 13.8661 | 13.685 | 13.6797 | 13.9619 | 13.3664 | 13.7312 | 13.4127 | 13.2309 | NaN | NaN | NaN | 13.3495 | 91.254 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 621.3379 | NaN | 14.6747 | NaN | 23.0429
7347.1292 | 13.8579 | 13.6893 | 13.6787 | 13.9642 | 13.3167 | 13.749 | 13.4162 | 13.2282 | NaN | NaN | NaN | 13.3544 | 91.8209 | NaN | NaN | NaN | -12.2591 | NaN | NaN | NaN | NaN | 622.3771 | NaN | 16.7186 | NaN | 24.1593
7348.1292 | 13.8516 | 13.6913 | 13.68 | 13.9327 | 13.4332 | 13.7668 | 13.4154 | 13.2307 | NaN | NaN | NaN | 13.3543 | 92.9276 | NaN | NaN | NaN | -19.6976 | NaN | NaN | NaN | -13.721 | 621.4603 | NaN | 17.0999 | NaN | 26.0288
7349.1292 | 13.8479 | 13.6478 | 13.6813 | 13.9702 | 13.4527 | 13.6736 | 13.3886 | 13.2342 | NaN | NaN | NaN | 13.3504 | 96.5789 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 609.6766 | NaN | 14.106 | NaN | 26.2004
7350.1292 | 13.8752 | 13.6477 | 13.6809 | 13.9565 | 13.3123 | 13.7201 | 13.4011 | 13.231 | NaN | NaN | NaN | 13.3524 | 92.2945 | NaN | NaN | NaN | 5.9183 | NaN | NaN | NaN | NaN | 607.1551 | NaN | 14.4902 | NaN | 24.7895
7351.1292 | 13.8683 | 13.6706 | 13.6743 | 13.9639 | 13.3908 | 13.7045 | 13.3954 | 13.2343 | NaN | NaN | NaN | 13.3889 | 92.9828 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 609.1361 | NaN | 17.2564 | NaN | 25.8133
7352.1292 | 13.8547 | 13.6725 | 13.6821 | 13.9675 | 13.4461 | 13.7067 | 13.3804 | 13.2338 | NaN | NaN | NaN | 13.4404 | 91.9842 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 613.6834 | NaN | 15.1251 | NaN | 24.0399
7353.1292 | 13.9867 | 13.6728 | 13.6782 | 13.9864 | 13.281 | 13.7016 | 13.3855 | 13.2325 | NaN | NaN | NaN | 13.4076 | 100.574 | NaN | NaN | NaN | 6.286 | NaN | NaN | NaN | NaN | 609.7831 | NaN | 17.4679 | NaN | 24.2792
7354.1292 | 13.9037 | 13.6401 | 13.6751 | 13.9754 | 13.3344 | 13.6829 | 13.386 | 13.2337 | NaN | NaN | NaN | 13.4467 | 100.7661 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 618.1554 | NaN | 19.5343 | NaN | 25.8106
7355.1292 | 13.8739 | 13.7234 | 13.6861 | 13.9664 | 13.3998 | 13.7233 | 13.4049 | 13.233 | NaN | NaN | NaN | 13.5133 | 94.2864 | NaN | NaN | NaN | 18.919 | NaN | NaN | NaN | NaN | 616.8637 | NaN | 15.5369 | NaN | 22.8136
7356.1292 | 13.8984 | 13.7257 | 13.6789 | 13.9897 | 13.3425 | 13.7569 | 13.405 | 13.2332 | NaN | NaN | NaN | 13.4398 | 92.9424 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 616.6596 | NaN | 17.1742 | NaN | 24.7133
7357.1292 | 13.8884 | 13.7579 | 13.6827 | 13.9776 | 13.4448 | 13.8024 | 13.4112 | 13.2272 | NaN | NaN | NaN | 13.3752 | 99.3172 | NaN | NaN | NaN | 0.2927 | NaN | NaN | NaN | 7.7349 | 617.7506 | NaN | 17.0821 | NaN | 25.5547
7358.1292 | 13.8745 | 13.7004 | 13.679 | 14.0087 | 13.3705 | 13.6883 | 13.3899 | 13.2403 | NaN | NaN | NaN | 13.4833 | 93.9325 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.9482 | 620.291 | NaN | 15.8439 | NaN | 22.4728
7359.1292 | 13.8574 | 13.7011 | 13.6836 | 13.9553 | 13.3493 | 13.7427 | 13.4019 | 13.2377 | NaN | NaN | NaN | 13.3584 | 96.0792 | NaN | NaN | NaN | 26.6238 | NaN | NaN | NaN | 17.1167 | 619.4876 | NaN | 17.6093 | NaN | 24.4958
7360.1292 | 13.8292 | 13.6625 | 13.6812 | 14.0026 | 13.4393 | 13.6843 | 13.3933 | 13.242 | NaN | NaN | NaN | 13.3625 | 95.2286 | NaN | NaN | NaN | -17.1531 | NaN | NaN | NaN | 11.6791 | 619.8012 | NaN | 14.6346 | NaN | 25.0109
7361.1292 | 14.0225 | 13.7439 | 13.6787 | 14.0189 | 13.3845 | 13.7715 | 13.4027 | 13.2397 | NaN | NaN | NaN | 13.37 | 92.789 | NaN | NaN | NaN | -6.6744 | NaN | NaN | NaN | 6.35 | 620.1711 | NaN | 15.704 | NaN | 24.9321
7362.1292 | 13.8674 | 13.8355 | 13.6815 | 13.977 | 13.3252 | 13.784 | 13.4529 | 13.2401 | NaN | NaN | NaN | 13.3849 | 95.3371 | NaN | NaN | NaN | -7.8993 | NaN | NaN | NaN | 12.0815 | 618.9791 | NaN | 17.0255 | NaN | 25.0938
7363.1292 | 13.8509 | 13.7166 | 13.6831 | 13.9422 | 13.4058 | 13.7313 | 13.3921 | 13.2355 | NaN | NaN | NaN | 13.4249 | 106.0102 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -12.8066 | 620.0439 | NaN | 13.5404 | NaN | 24.1753
7364.1292 | 13.8121 | 13.6673 | 13.6796 | 13.9618 | 13.4314 | 13.6903 | 13.3852 | 13.2391 | NaN | NaN | NaN | 13.3758 | 102.9704 | NaN | NaN | NaN | -15.1473 | NaN | NaN | NaN | NaN | 620.9095 | NaN | 16.8361 | NaN | 23.1989
7365.1292 | 13.9134 | 13.7086 | 13.6851 | 13.9928 | 13.4157 | 13.7273 | 13.4112 | 13.2451 | NaN | NaN | NaN | 13.3809 | 92.2622 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 620.318 | NaN | 14.6041 | NaN | 24.2988
7366.1292 | 13.8729 | 13.6689 | 13.6767 | 13.9639 | 13.3617 | 13.7034 | 13.3914 | 13.2391 | NaN | NaN | NaN | 13.3708 | 97.3863 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 619.555 | NaN | 19.0257 | NaN | 24.5105
7367.1292 | 13.8638 | 13.6615 | 13.6803 | 13.9537 | 13.3601 | 13.6865 | 13.3849 | 13.2403 | NaN | NaN | NaN | 13.4319 | 99.7824 | NaN | NaN | NaN | 5.6263 | NaN | NaN | NaN | NaN | 613.0504 | NaN | 20.692 | NaN | 24.0669
7368.1292 | 13.8527 | 13.6752 | 13.682 | 13.9926 | 13.462 | 13.7168 | 13.3877 | 13.2373 | NaN | NaN | NaN | 13.3781 | 91.7839 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 615.5839 | NaN | 17.855 | NaN | 24.9377
7369.1292 | 13.8873 | 13.6789 | 13.6816 | 13.9572 | 13.3443 | 13.6902 | 13.3832 | 13.2412 | NaN | NaN | NaN | 13.4037 | 92.0173 | NaN | NaN | NaN | 18.9478 | NaN | NaN | NaN | NaN | 616.448 | NaN | 14.2895 | NaN | 24.9421
7370.1292 | 13.8632 | 13.6905 | 13.6827 | 13.9998 | 13.3399 | 13.7445 | 13.4053 | 13.2394 | NaN | NaN | NaN | 13.3854 | 94.7354 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 621.6324 | NaN | 14.674 | NaN | 23.5136
7371.1292 | 13.866 | 13.7043 | 13.6829 | 13.9642 | 13.4209 | 13.7493 | 13.3991 | 13.2356 | NaN | NaN | NaN | 13.3697 | 96.2021 | NaN | NaN | NaN | 1.871 | NaN | NaN | NaN | NaN | 620.4066 | NaN | 17.9584 | NaN | 23.9073
7372.1292 | 13.869 | 13.6501 | 13.6807 | 13.9754 | 13.4857 | 13.6705 | 13.3811 | 13.2417 | NaN | NaN | NaN | 13.3648 | 93.0836 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 613.8782 | NaN | 15.7305 | NaN | 27.9826
7373.1292 | 13.86 | 13.7128 | 13.6805 | 13.9894 | 13.3438 | 13.7096 | 13.4023 | 13.236 | NaN | NaN | NaN | 13.378 | 91.5561 | NaN | NaN | NaN | -9.4273 | NaN | NaN | NaN | NaN | 614.088 | NaN | 18.422 | NaN | 25.341
7374.1292 | 13.8406 | 13.8369 | 13.6795 | 13.9228 | 13.3621 | 13.7248 | 13.4452 | 13.2419 | NaN | NaN | NaN | 13.3877 | 95.3142 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 618.5212 | NaN | 16.3603 | NaN | 25.9964
7375.1292 | 13.9351 | 13.6754 | 13.6783 | 13.9518 | 13.3698 | 13.7194 | 13.3983 | 13.2432 | NaN | NaN | NaN | 13.3636 | 91.9276 | NaN | NaN | NaN | -6.9706 | NaN | NaN | NaN | NaN | 619.6096 | NaN | 16.4885 | NaN | 25.6779
7376.1292 | 13.8863 | 13.838 | 13.6851 | 13.9568 | 13.3048 | 13.7402 | 13.4138 | 13.2434 | NaN | NaN | NaN | 13.5461 | 96.8958 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 618.7368 | NaN | 17.685 | NaN | 22.9264
7377.1292 | 13.8682 | 13.6591 | 13.6773 | 13.9812 | 13.474 | 13.6983 | 13.3889 | 13.2452 | NaN | NaN | NaN | 13.3996 | 95.5411 | NaN | NaN | NaN | -10.0643 | NaN | NaN | NaN | NaN | 615.5182 | NaN | 16.5191 | NaN | 27.6536
7378.1292 | 13.9201 | 13.6513 | 13.681 | 13.9339 | 13.4059 | 13.6979 | 13.3862 | 13.2408 | NaN | NaN | NaN | 13.5533 | 92.6216 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 615.2502 | NaN | 18.4206 | NaN | 25.639
7379.1292 | 13.8623 | 13.7783 | 13.683 | 14.0303 | 13.3767 | 13.7584 | 13.398 | 13.2474 | NaN | NaN | NaN | 13.3896 | 92.613 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 616.1781 | NaN | 16.2692 | NaN | 23.2656
7380.1292 | 13.8131 | 13.7179 | 13.6851 | 13.979 | 13.2289 | 13.7271 | 13.4096 | 13.2461 | NaN | NaN | NaN | 13.3976 | 95.0983 | NaN | NaN | NaN | 26.9705 | NaN | NaN | NaN | NaN | 616.145 | NaN | 16.9221 | NaN | 24.1059
7381.1292 | 13.8774 | 13.7293 | 13.687 | 13.9907 | 13.4295 | 13.7092 | 13.3967 | 13.2468 | NaN | NaN | NaN | 13.374 | 104.3482 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 613.1149 | NaN | 17.9306 | NaN | 25.8991
7382.1292 | 13.8549 | 13.7642 | 13.6862 | 13.9882 | 13.4163 | 13.7625 | 13.3997 | 13.2427 | NaN | NaN | NaN | 13.3689 | 92.8717 | NaN | NaN | NaN | 19.3329 | NaN | NaN | NaN | -9.4492 | 613.0529 | NaN | 15.1449 | NaN | 24.3788
7383.1292 | 13.8032 | 13.7135 | 13.6931 | 13.9232 | 13.3973 | 13.7139 | 13.4066 | 13.2427 | NaN | NaN | NaN | 13.3827 | 90.5377 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 609.7909 | NaN | 15.7789 | NaN | 26.4276
7384.1292 | 13.8676 | 13.6782 | 13.6872 | 13.988 | 13.3961 | 13.7258 | 13.3974 | 13.2396 | NaN | NaN | NaN | 13.368 | 91.7733 | NaN | NaN | NaN | 26.9237 | NaN | NaN | NaN | NaN | 605.4405 | NaN | 15.3624 | NaN | 24.8632
7385.1292 | 13.8608 | 13.7036 | 13.6904 | 13.9641 | 13.4434 | 13.7672 | 13.4011 | 13.2454 | NaN | NaN | NaN | 13.4089 | 92.5409 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 604.3573 | NaN | 16.0271 | NaN | 24.788
7386.1292 | 13.8602 | 13.6322 | 13.6869 | 13.9746 | 13.4173 | 13.6827 | 13.3771 | 13.2398 | NaN | NaN | NaN | 13.4321 | 92.3144 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 609.3631 | NaN | 15.2373 | NaN | 26.6363
7387.1292 | 13.8352 | 13.867 | 13.686 | 13.9127 | 13.3698 | 13.8873 | 13.42 | 13.2372 | NaN | NaN | NaN | 13.4204 | 93.201 | NaN | NaN | NaN | 9.0824 | NaN | NaN | NaN | NaN | 610.3922 | NaN | 17.513 | NaN | 26.8183
7388.1292 | 13.832 | 13.7425 | 13.6854 | 13.9688 | 13.3426 | 13.7174 | 13.419 | 13.2416 | NaN | NaN | NaN | 13.3683 | 93.8736 | NaN | NaN | NaN | -12.9876 | NaN | NaN | NaN | NaN | 608.6971 | NaN | 18.3747 | NaN | 26.4499
7389.1292 | 13.9328 | 13.6869 | 13.6854 | 13.9416 | 13.5345 | 13.7121 | 13.3987 | 13.2325 | NaN | NaN | NaN | 13.3774 | 92.2208 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 613.6267 | NaN | 16.0768 | NaN | 25.1697
7390.1292 | 13.8561 | 13.6519 | 13.6807 | 13.9817 | 13.4716 | 13.6943 | 13.3875 | 13.2395 | NaN | NaN | NaN | 13.3831 | 94.105 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 610.4714 | NaN | 15.7312 | NaN | 25.3381
7391.1292 | 13.8532 | 13.6988 | 13.6865 | 13.9752 | 13.3883 | 13.7541 | 13.3993 | 13.2421 | NaN | NaN | NaN | 13.3547 | 103.9389 | NaN | NaN | NaN | 4.4238 | NaN | NaN | NaN | NaN | 613.4072 | NaN | 16.6185 | NaN | 25.1578
7392.1292 | 13.8184 | 13.6824 | 13.6857 | 13.9698 | 13.3943 | 13.7331 | 13.3965 | 13.2316 | NaN | NaN | NaN | 13.3991 | 91.3495 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -19.404 | 613.3338 | NaN | 16.1842 | NaN | 25.501
7393.1292 | 13.9758 | 13.6512 | 13.6881 | 13.9484 | 13.3872 | 13.7222 | 13.3916 | 13.2345 | NaN | NaN | NaN | 13.3615 | 90.5313 | NaN | NaN | NaN | 19.9218 | NaN | NaN | NaN | NaN | 612.5728 | NaN | 17.0316 | NaN | 24.3592
7394.1292 | 13.8524 | 13.7204 | 13.6829 | 13.9973 | 13.4624 | 13.7602 | 13.4047 | 13.2362 | NaN | NaN | NaN | 13.3639 | 94.5271 | NaN | NaN | NaN | -19.9448 | NaN | NaN | NaN | NaN | 613.7079 | NaN | 18.6078 | NaN | 25.4064
7395.1292 | 13.8523 | 13.7156 | 13.6871 | 13.9534 | 13.366 | 13.7449 | 13.4049 | 13.2395 | NaN | NaN | NaN | 13.3708 | 97.3939 | NaN | NaN | NaN | 13.2428 | NaN | NaN | NaN | NaN | 614.4441 | NaN | 16.9441 | NaN | 25.6439
7396.1292 | 14.1939 | 13.6431 | 13.6831 | 13.9882 | 13.4344 | 13.7255 | 13.3968 | 13.2343 | NaN | NaN | NaN | 13.3987 | 91.0944 | NaN | NaN | NaN | -13.4477 | NaN | NaN | NaN | NaN | 611.994 | NaN | 18.2126 | NaN | 23.841
7397.1292 | 13.8614 | 13.6644 | 13.6855 | 13.9611 | 13.398 | 13.7475 | 13.4035 | 13.2362 | NaN | NaN | NaN | 13.3882 | 95.8845 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 604.1123 | NaN | 17.9804 | NaN | 25.2364
7398.1292 | 13.8371 | 13.6432 | 13.6826 | 13.9921 | 13.3283 | 13.6963 | 13.39 | 13.236 | NaN | NaN | NaN | 13.3911 | 93.4588 | NaN | NaN | NaN | -10.3825 | NaN | NaN | NaN | NaN | 593.2521 | NaN | 18.4672 | NaN | 25.7322
7399.1292 | 13.9552 | 13.6494 | 13.6829 | 13.9749 | 13.425 | 13.7216 | 13.3995 | 13.2296 | NaN | NaN | NaN | 13.3933 | 91.0978 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 587.6108 | NaN | 16.0651 | NaN | 25.6482
7400.1292 | 13.9094 | 13.7069 | 13.6808 | 13.9792 | 13.4329 | 13.7881 | 13.406 | 13.2346 | NaN | NaN | NaN | 13.348 | 93.3396 | NaN | NaN | NaN | 18.479 | NaN | NaN | NaN | NaN | 582.8122 | NaN | 15.1948 | NaN | 25.4301
7401.1292 | 13.9159 | 13.6827 | 13.6816 | 13.9693 | 13.3979 | 13.719 | 13.3984 | 13.2419 | NaN | NaN | NaN | 13.3702 | 93.1789 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 576.3378 | NaN | 14.5773 | NaN | 24.8983
7402.1292 | 13.804 | 13.6616 | 13.6784 | 14.0738 | 13.2692 | 13.7526 | 13.4102 | 13.2403 | NaN | NaN | NaN | 13.4076 | 92.9097 | NaN | NaN | NaN | -6.261 | NaN | NaN | NaN | -17.6352 | 579.3689 | NaN | 15.1176 | NaN | 20.5112
7403.1292 | 13.8808 | 13.6921 | 13.6827 | 13.9673 | 13.3212 | 13.7516 | 13.3964 | 13.2358 | NaN | NaN | NaN | 13.3771 | 93.2462 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 578.8885 | NaN | 14.8174 | NaN | 25.0555
7404.1292 | 13.8572 | 13.6807 | 13.6744 | 13.9926 | 13.317 | 13.7431 | 13.3987 | 13.2342 | NaN | NaN | NaN | 13.3736 | 95.5126 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 581.485 | NaN | 18.2651 | NaN | 24.521
7405.1292 | 13.864 | 13.6345 | 13.6847 | 13.9693 | 13.3936 | 13.6783 | 13.3827 | 13.2355 | NaN | NaN | NaN | 13.4096 | 93.3055 | NaN | NaN | NaN | 26.5806 | NaN | NaN | NaN | NaN | 582.5675 | NaN | 15.9388 | NaN | 21.0273
7406.1292 | 13.8534 | 13.7403 | 13.6765 | 13.9821 | 13.4353 | 13.7378 | 13.3998 | 13.228 | NaN | NaN | NaN | 13.3656 | 99.1211 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 583.9595 | NaN | 15.0683 | NaN | 27.6856
7407.1292 | 13.8505 | 13.6642 | 13.676 | 13.9506 | 13.362 | 13.7242 | 13.4062 | 13.2372 | NaN | NaN | NaN | 13.3854 | 91.7491 | NaN | NaN | NaN | -7.2853 | NaN | NaN | NaN | NaN | 588.0262 | NaN | 17.2324 | NaN | 23.37
7408.1292 | 13.8585 | 13.7268 | 13.6749 | 13.976 | 13.3693 | 13.7415 | 13.404 | 13.2286 | NaN | NaN | NaN | 13.3648 | 93.2753 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 596.1436 | NaN | 15.1813 | NaN | 25.3617
7409.1292 | 13.8488 | 13.6945 | 13.6677 | 13.9592 | 13.3978 | 13.7614 | 13.4027 | 13.2365 | NaN | NaN | NaN | 13.3873 | 90.981 | NaN | NaN | NaN | -8.5544 | NaN | NaN | NaN | NaN | 603.4307 | NaN | 16.5009 | NaN | 24.0071
7410.1292 | 13.8546 | 13.7208 | 13.668 | 13.9824 | 13.4582 | 13.7574 | 13.4096 | 13.2466 | NaN | NaN | NaN | 13.4871 | 93.0555 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 608.7707 | NaN | 15.6783 | NaN | 25.2778
7411.1292 | 13.851 | 13.7026 | 13.6698 | 13.9733 | 13.3816 | 13.7314 | 13.4065 | 13.2401 | NaN | NaN | NaN | 13.6349 | 90.7717 | NaN | NaN | NaN | -18.7543 | NaN | NaN | NaN | NaN | 602.0958 | NaN | 14.0357 | NaN | 24.2227
7412.1292 | 13.8439 | 13.644 | 13.6718 | 13.9516 | 13.4327 | 13.7026 | 13.3894 | 13.2438 | NaN | NaN | NaN | 13.6194 | 97.1006 | NaN | NaN | NaN | -4.4509 | NaN | NaN | NaN | NaN | 601.9718 | NaN | 17.0068 | NaN | 24.1053
7413.1292 | 13.9236 | 13.6837 | 13.6681 | 13.978 | 13.3672 | 13.7578 | 13.4117 | 13.2339 | NaN | NaN | NaN | 13.362 | 95.1411 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 607.5509 | NaN | 16.7574 | NaN | 25.1339
7414.1292 | 13.8469 | 13.7545 | 13.6669 | 13.9837 | 13.4259 | 13.7666 | 13.4202 | 13.2432 | NaN | NaN | NaN | 13.3749 | 96.4968 | NaN | NaN | NaN | -7.1502 | NaN | NaN | NaN | NaN | 607.57 | NaN | 16.9206 | NaN | 26.0753
7415.1292 | 13.8726 | 13.6975 | 13.664 | 13.9744 | 13.401 | 13.7305 | 13.4157 | 13.2414 | NaN | NaN | NaN | 13.3627 | 94.2505 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 611.2682 | NaN | 17.532 | NaN | 24.6165
7416.1292 | 13.8758 | 13.6383 | 13.6661 | 13.9631 | 13.4403 | 13.7119 | 13.4041 | 13.2416 | NaN | NaN | NaN | 13.4201 | 91.9255 | NaN | NaN | NaN | -12.3082 | NaN | NaN | NaN | NaN | 607.727 | NaN | 16.9823 | NaN | 25.2391
7417.1292 | 14.2093 | 13.6674 | 13.6727 | 13.9738 | 13.3473 | 13.7331 | 13.4027 | 13.2356 | NaN | NaN | NaN | 13.3507 | 92.6019 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 608.8953 | NaN | 18.5645 | NaN | 24.1799
7418.1292 | 13.8641 | 13.6881 | 13.6711 | 13.9564 | 13.3893 | 13.7512 | 13.4132 | 13.2394 | NaN | NaN | NaN | 13.3712 | 93.5022 | NaN | NaN | NaN | -14.8308 | NaN | NaN | NaN | NaN | 609.1515 | NaN | 16.6485 | NaN | 23.9641
7419.1292 | 13.852 | 13.6912 | 13.6739 | 13.9757 | 13.44 | 13.756 | 13.4186 | 13.2344 | NaN | NaN | NaN | 13.4136 | 98.0766 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 599.8524 | NaN | 17.2784 | NaN | 21.331
7420.1292 | 13.8563 | 13.6588 | 13.673 | 13.9376 | 13.4 | 13.7254 | 13.4079 | 13.2421 | NaN | NaN | NaN | 13.3759 | 106.1528 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 597.1203 | NaN | 17.6515 | NaN | 26.6673
7421.1292 | 14.1732 | 13.651 | 13.6771 | 13.9827 | 13.4321 | 13.7146 | 13.4045 | 13.2305 | NaN | NaN | NaN | 13.3772 | 93.7123 | NaN | NaN | NaN | 8.2691 | NaN | NaN | NaN | NaN | 597.597 | NaN | 17.156 | NaN | 25.4274
7422.1292 | 13.87 | 13.6911 | 13.6688 | 13.932 | 13.4507 | 13.7526 | 13.4153 | 13.237 | NaN | NaN | NaN | 13.3618 | 92.5521 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 599.4674 | NaN | 16.3945 | NaN | 25.5937
7423.1292 | 13.8741 | 13.6974 | 13.6739 | 13.964 | 13.331 | 13.7936 | 13.4181 | 13.2377 | NaN | NaN | NaN | 13.3725 | 97.703 | NaN | NaN | NaN | -2.4956 | NaN | NaN | NaN | NaN | 598.4527 | NaN | 17.9475 | NaN | 24.9157
7424.1292 | 13.8598 | 13.664 | 13.6665 | 13.9745 | 13.3382 | 13.7447 | 13.4057 | 13.2387 | NaN | NaN | NaN | 13.378 | 92.0416 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -18.8509 | 607.3774 | NaN | 18.759 | NaN | 21.824
7425.1292 | 13.8463 | 13.6748 | 13.6711 | 14.0008 | 13.4981 | 13.7319 | 13.4163 | 13.2338 | NaN | NaN | NaN | 13.3474 | 92.9591 | NaN | NaN | NaN | -12.9768 | NaN | NaN | NaN | NaN | 606.6859 | NaN | 19.2688 | NaN | 26.0691
7426.1292 | 13.9235 | 13.6552 | 13.6729 | 13.9213 | 13.3513 | 13.7442 | 13.4172 | 13.2275 | NaN | NaN | NaN | 13.3971 | 95.4388 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 607.7433 | NaN | 16.9982 | NaN | 22.5046
7427.1292 | 13.8692 | 13.7151 | 13.6702 | 13.9362 | 13.4425 | 13.7763 | 13.4263 | 13.2309 | NaN | NaN | NaN | 13.3731 | 95.7388 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 607.0352 | NaN | 17.2302 | NaN | 26.4041
7428.1292 | 13.8564 | 13.6947 | 13.6784 | 13.9909 | 13.3124 | 13.7624 | 13.4184 | 13.2391 | NaN | NaN | NaN | 13.3437 | 93.9343 | NaN | NaN | NaN | -8.6534 | NaN | NaN | NaN | NaN | 598.258 | NaN | 18.168 | NaN | 27.7115
7429.1292 | 14.0263 | 13.7703 | 13.6761 | 13.9929 | 13.4878 | 13.7867 | 13.4275 | 13.2311 | NaN | NaN | NaN | 13.3549 | 91.3991 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 587.3982 | NaN | 15.604 | NaN | 23.7262
7430.1292 | 13.8525 | 13.6474 | 13.6792 | 13.9564 | 13.3895 | 13.7143 | 13.4118 | 13.2318 | NaN | NaN | NaN | 13.3366 | 92.9579 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 590.3242 | NaN | 18.1001 | NaN | 25.2242
7431.1292 | 13.8748 | 13.6981 | 13.6758 | 13.9752 | 13.4086 | 13.7729 | 13.4275 | 13.2292 | NaN | NaN | NaN | 13.3578 | 91.7204 | NaN | NaN | NaN | 22.6196 | NaN | NaN | NaN | NaN | 591.7596 | NaN | 17.5612 | NaN | 25.1635
7432.1292 | 13.8784 | 13.7097 | 13.6772 | 13.9463 | 13.4278 | 13.7392 | 13.4265 | 13.2344 | NaN | NaN | NaN | 13.3587 | 96.3459 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 593.2412 | NaN | 13.4492 | NaN | 21.1229
7433.1292 | 13.8683 | 13.7092 | 13.6819 | 13.9534 | 13.4018 | 13.7416 | 13.4193 | 13.2389 | NaN | NaN | NaN | 13.377 | 89.8597 | NaN | NaN | NaN | -7.65 | NaN | NaN | NaN | NaN | 597.8206 | NaN | 14.0888 | NaN | 23.8363
7434.1292 | 13.8572 | 13.6745 | 13.6842 | 13.9702 | 13.3817 | 13.7333 | 13.4287 | 13.2316 | NaN | NaN | NaN | 13.484 | 95.9105 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 605.2523 | NaN | 17.009 | NaN | 22.388
7435.1292 | 13.846 | 13.6962 | 13.682 | 13.9845 | 13.3556 | 13.7605 | 13.4324 | 13.2361 | NaN | NaN | NaN | 13.3341 | 96.9334 | NaN | NaN | NaN | -16.8626 | NaN | NaN | NaN | NaN | 602.9859 | NaN | 15.6032 | NaN | 25.989
7436.1292 | 13.8687 | 13.6633 | 13.683 | 13.9509 | 13.3597 | 13.7341 | 13.4251 | 13.2361 | NaN | NaN | NaN | 13.3533 | 97.0545 | NaN | NaN | NaN | -6.0763 | NaN | NaN | NaN | NaN | 602.9855 | NaN | 15.6254 | NaN | 25.6667
7437.1292 | 13.8606 | 13.6879 | 13.6794 | 13.9378 | 13.3707 | 13.7581 | 13.4289 | 13.2404 | NaN | NaN | NaN | 13.3244 | 99.7082 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 601.6211 | NaN | 16.3886 | NaN | 26.6654
7438.1292 | 13.9525 | 13.6863 | 13.6788 | 13.9549 | 13.3014 | 13.7628 | 13.4434 | 13.2384 | NaN | NaN | NaN | 13.3565 | 91.9675 | NaN | NaN | NaN | -10.3431 | NaN | NaN | NaN | NaN | 603.4618 | NaN | 16.2141 | NaN | 23.286
7439.1292 | 13.9122 | 13.6961 | 13.6778 | 13.982 | 13.4228 | 13.7635 | 13.4436 | 13.2388 | NaN | NaN | NaN | 13.3205 | 96.2048 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 608.2331 | NaN | 15.5596 | NaN | 25.3372
7440.1292 | 13.8519 | 13.8163 | 13.6813 | 13.9756 | 13.4474 | 13.8203 | 13.4379 | 13.2408 | NaN | NaN | NaN | 13.3475 | 108.7347 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 605.2329 | NaN | 14.2166 | NaN | 26.2651
7441.1292 | 13.9259 | 13.7246 | 13.6806 | 13.9664 | 13.4496 | 13.7658 | 13.4464 | 13.2368 | NaN | NaN | NaN | 13.3397 | 94.2095 | NaN | NaN | NaN | 7.0177 | NaN | NaN | NaN | NaN | 606.7411 | NaN | 13.7325 | NaN | 23.7286
7442.1292 | 13.8548 | 13.8211 | 13.6784 | 13.9619 | 13.3404 | 13.8702 | 13.463 | 13.2363 | NaN | NaN | NaN | 13.5364 | 94.1546 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 609.9984 | NaN | 14.9513 | NaN | 25.8588
7443.1292 | 13.8384 | 13.6545 | 13.6772 | 13.9981 | 13.3935 | 13.7097 | 13.4282 | 13.2301 | NaN | NaN | NaN | 13.3239 | 90.8423 | NaN | NaN | NaN | 31.0865 | NaN | NaN | NaN | NaN | 612.0685 | NaN | 18.5119 | NaN | 25.7275
7444.1292 | 13.9607 | 13.6881 | 13.6703 | 13.9798 | 13.4386 | 13.7393 | 13.4401 | 13.2397 | NaN | NaN | NaN | 13.3192 | 91.4283 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 607.4172 | NaN | 16.1578 | NaN | 25.138
7445.1292 | 13.8533 | 13.6753 | 13.6814 | 14.034 | 13.4276 | 13.743 | 13.4412 | 13.2338 | NaN | NaN | NaN | 13.3656 | 97.3928 | NaN | NaN | NaN | -15.7821 | NaN | NaN | NaN | NaN | 603.0594 | NaN | 15.8263 | NaN | 23.8122
7446.1292 | 13.9344 | 13.6697 | 13.6755 | 13.9547 | 13.4195 | 13.7378 | 13.426 | 13.241 | NaN | NaN | NaN | 13.3253 | 97.9702 | NaN | NaN | NaN | -4.2676 | NaN | NaN | NaN | NaN | 607.7729 | NaN | 14.9975 | NaN | 24.8599
7447.1292 | 13.8735 | 13.6622 | 13.674 | 13.9848 | 13.4239 | 13.7322 | 13.4309 | 13.2381 | NaN | NaN | NaN | 13.3457 | 94.8873 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 605.0364 | NaN | 16.1407 | NaN | 25.3617
7448.1292 | 13.8621 | 13.738 | 13.6697 | 13.9364 | 13.3385 | 13.8183 | 13.4481 | 13.2395 | NaN | NaN | NaN | 13.3545 | 92.3599 | NaN | NaN | NaN | 12.2891 | NaN | NaN | NaN | NaN | 607.4381 | NaN | 18.0857 | NaN | 24.5095
7449.1292 | 13.8464 | 13.6977 | 13.665 | 14.0318 | 13.4318 | 13.7222 | 13.444 | 13.2317 | NaN | NaN | NaN | 13.3846 | 90.2101 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 600.132 | NaN | 15.1232 | NaN | 26.4509
7450.1292 | 13.8491 | 13.6704 | 13.6648 | 13.9316 | 13.45 | 13.7354 | 13.4398 | 13.2327 | NaN | NaN | NaN | 13.4128 | 100.2942 | NaN | NaN | NaN | -7.8964 | NaN | NaN | NaN | NaN | 599.507 | NaN | 15.7687 | NaN | 24.3702
7451.1292 | 13.8318 | 13.7482 | 13.6687 | 13.9774 | 13.4158 | 13.7739 | 13.433 | 13.2373 | NaN | NaN | NaN | 13.3392 | 90.394 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 600.9627 | NaN | 18.2204 | NaN | 24.9288
7452.1292 | 13.8412 | 13.724 | 13.6643 | 13.9532 | 13.4533 | 13.7592 | 13.4431 | 13.2296 | NaN | NaN | NaN | 13.341 | 94.4758 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 608.2937 | NaN | 17.1618 | NaN | 27.0379
7453.1292 | 13.8857 | 13.7059 | 13.669 | 13.9592 | 13.4643 | 13.7731 | 13.4429 | 13.2381 | NaN | NaN | NaN | 13.3503 | 88.562 | NaN | NaN | NaN | 29.3952 | NaN | NaN | NaN | NaN | 607.7597 | NaN | 15.7379 | NaN | 24.5625
7454.1292 | 13.8503 | 13.6996 | 13.6706 | 13.9707 | 13.4434 | 13.7675 | 13.4411 | 13.2452 | NaN | NaN | NaN | 13.3509 | 93.3743 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 607.6958 | NaN | 15.2518 | NaN | 25.6499
7455.1292 | 13.8864 | 13.6834 | 13.6755 | 13.9789 | 13.4268 | 13.7664 | 13.4436 | 13.241 | NaN | NaN | NaN | 13.3427 | 90.2867 | NaN | NaN | NaN | 14.0722 | NaN | NaN | NaN | NaN | 608.1186 | NaN | 15.183 | NaN | 24.9334
7456.1292 | 13.8745 | 13.6979 | 13.6807 | 13.9741 | 13.2994 | 13.7978 | 13.4493 | 13.235 | NaN | NaN | NaN | 13.3564 | 100.4518 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 609.6725 | NaN | 18.2204 | NaN | 25.0871
7457.1292 | 13.873 | 13.7053 | 13.683 | 14.0056 | 13.444 | 13.7377 | 13.4404 | 13.2326 | NaN | NaN | NaN | 13.4776 | 93.6413 | NaN | NaN | NaN | -17.1887 | NaN | NaN | NaN | NaN | 607.0684 | NaN | 16.0621 | NaN | 27.2973
7458.1292 | 13.8688 | 13.6582 | 13.6793 | 13.9708 | 13.4693 | 13.7248 | 13.4355 | 13.246 | NaN | NaN | NaN | 13.3305 | 94.8025 | NaN | NaN | NaN | -11.3666 | NaN | NaN | NaN | -17.2179 | 607.8395 | NaN | 16.1719 | NaN | 24.6676
7459.1292 | 13.875 | 13.6782 | 13.6778 | 14.0478 | 13.4662 | 13.7446 | 13.4417 | 13.2391 | NaN | NaN | NaN | 13.4068 | 101.7787 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 604.5412 | NaN | 16.0988 | NaN | 25.0335
7460.1292 | 13.8775 | 13.6778 | 13.6686 | 13.9185 | 13.3878 | 13.7524 | 13.4317 | 13.2394 | NaN | NaN | NaN | 13.3408 | 91.1295 | NaN | NaN | NaN | 16.8953 | NaN | NaN | NaN | NaN | 599.8894 | NaN | 16.2501 | NaN | 25.884
7461.1292 | 13.8949 | 13.6361 | 13.6744 | 13.933 | 13.4716 | 13.7021 | 13.423 | 13.2349 | NaN | NaN | NaN | 13.5379 | 93.3588 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 597.8501 | NaN | 16.9307 | NaN | 23.4857
7462.1292 | 13.8702 | 13.7046 | 13.6716 | 13.9491 | 13.3731 | 13.8044 | 13.4502 | 13.2316 | NaN | NaN | NaN | 13.3629 | 93.5083 | NaN | NaN | NaN | -2.8059 | NaN | NaN | NaN | NaN | 599.8316 | NaN | 15.8352 | NaN | 24.8145
7463.1292 | 13.8629 | 13.7002 | 13.6741 | 13.9809 | 13.4314 | 13.7481 | 13.4358 | 13.2377 | NaN | NaN | NaN | 13.3566 | 92.6083 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 600.7268 | NaN | 14.8632 | NaN | 26.8585
7464.1292 | 13.8665 | 13.6735 | 13.6737 | 13.9726 | 13.327 | 13.7312 | 13.4303 | 13.2418 | NaN | NaN | NaN | 13.3339 | 92.87 | NaN | NaN | NaN | -9.1779 | NaN | NaN | NaN | NaN | 606.1341 | NaN | 14.3535 | NaN | 24.7475
7465.1292 | 13.8595 | 13.7037 | 13.6712 | 13.9827 | 13.4118 | 13.7461 | 13.4398 | 13.2396 | NaN | NaN | NaN | 13.3343 | 90.4212 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 604.365 | NaN | 14.5154 | NaN | 25.2003
7466.1292 | 13.8444 | 13.6488 | 13.6802 | 14.1128 | 13.4475 | 13.7288 | 13.4333 | 13.2443 | NaN | NaN | NaN | 13.3769 | 93.6726 | NaN | NaN | NaN | -19.6619 | NaN | NaN | NaN | NaN | 607.8651 | NaN | 15.4857 | NaN | 25.6374
7467.1292 | 13.8506 | 13.6779 | 13.6792 | 13.9748 | 13.3404 | 13.7484 | 13.442 | 13.2349 | NaN | NaN | NaN | 13.3664 | 94.1692 | NaN | NaN | NaN | 7.4393 | NaN | NaN | NaN | -15.5085 | 607.4096 | NaN | 15.5383 | NaN | 25.9688
7468.1292 | 13.8435 | 13.7383 | 13.6729 | 13.9601 | 13.408 | 13.7733 | 13.4291 | 13.237 | NaN | NaN | NaN | 13.3417 | 94.0558 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 607.6043 | NaN | 14.5379 | NaN | 24.2529
7469.1292 | 13.8608 | 13.6838 | 13.6748 | 13.9769 | 13.3578 | 13.7853 | 13.4465 | 13.2365 | NaN | NaN | NaN | 13.3365 | 93.9152 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 608.1719 | NaN | 16.1468 | NaN | 25.7599
7470.1292 | 13.8591 | 13.6714 | 13.6791 | 13.9852 | 13.4145 | 13.7304 | 13.4248 | 13.2392 | NaN | NaN | NaN | 13.4183 | 93.9007 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 605.4246 | NaN | 15.3174 | NaN | 25.099
7471.1292 | 13.8578 | 13.7223 | 13.6788 | 14.0545 | 13.4693 | 13.7706 | 13.4565 | 13.2386 | NaN | NaN | NaN | 13.3522 | 93.1546 | NaN | NaN | NaN | 20.1965 | NaN | NaN | NaN | NaN | 604.1493 | NaN | 18.4108 | NaN | 22.8222
7472.1292 | 13.8584 | 13.7162 | 13.6746 | 13.9681 | 13.3249 | 13.7715 | 13.4392 | 13.2366 | NaN | NaN | NaN | 13.5176 | 101.679 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -15.5498 | 606.6829 | NaN | 12.7525 | NaN | 24.9628
7473.1292 | 13.8394 | 13.6805 | 13.679 | 13.9591 | 13.3492 | 13.7465 | 13.4302 | 13.2404 | NaN | NaN | NaN | 13.3662 | 91.537 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.5589 | 607.4222 | NaN | 16.7984 | NaN | 22.0065
7474.1292 | 13.8318 | 13.676 | 13.6823 | 14.0048 | 13.3314 | 13.7544 | 13.4335 | 13.2393 | NaN | NaN | NaN | 13.3457 | 94.035 | NaN | NaN | NaN | 21.6166 | NaN | NaN | NaN | 17.8273 | 605.6702 | NaN | 16.2426 | NaN | 24.0942
7475.1292 | 13.8569 | 13.6808 | 13.6864 | 14.0011 | 13.2768 | 13.7625 | 13.4331 | 13.2424 | NaN | NaN | NaN | 13.3477 | 104.8803 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.4289 | 606.5156 | NaN | 16.3395 | NaN | 25.8089
7476.1292 | 13.8512 | 13.7955 | 13.6841 | 13.9956 | 13.3465 | 13.8549 | 13.4539 | 13.2403 | NaN | NaN | NaN | 13.3563 | 92.7217 | NaN | NaN | NaN | -2.487 | NaN | NaN | NaN | 45.4427 | 608.7827 | NaN | 17.4843 | NaN | 26.0678
7477.1292 | 13.8684 | 13.6647 | 13.6849 | 13.9549 | 13.4186 | 13.7557 | 13.4301 | 13.238 | NaN | NaN | NaN | 13.3203 | 90.1978 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 57.9077 | 606.3734 | NaN | 17.1645 | NaN | 26.4956
7478.1292 | 13.8912 | 13.6715 | 13.6838 | 13.9643 | 13.3841 | 13.7849 | 13.4476 | 13.2429 | NaN | NaN | NaN | 13.3491 | 97.3351 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.4288 | 607.0372 | NaN | 16.1733 | NaN | 25.4873
7479.1292 | 13.9199 | 13.6564 | 13.6913 | 13.9929 | 13.2958 | 13.7829 | 13.4521 | 13.2418 | NaN | NaN | NaN | 13.3394 | 90.4717 | NaN | NaN | NaN | 22.5164 | NaN | NaN | NaN | 15.8842 | 606.8086 | NaN | 15.3844 | NaN | 24.1873
7480.1292 | 13.9122 | 13.6799 | 13.6878 | 13.9925 | 13.2875 | 13.7547 | 13.4333 | 13.2479 | NaN | NaN | NaN | 13.407 | 92.1246 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -11.9918 | 602.2333 | NaN | 16.0172 | NaN | 22.0284
7481.1292 | 13.8713 | 13.7672 | 13.6932 | 14.001 | 13.3766 | 13.7844 | 13.4494 | 13.2406 | NaN | NaN | NaN | 13.3514 | 93.4742 | NaN | NaN | NaN | -15.6484 | NaN | NaN | NaN | NaN | 604.3326 | NaN | 17.276 | NaN | 26.734
7482.1292 | 13.8688 | 13.6987 | 13.6923 | 14.0065 | 13.469 | 13.7501 | 13.4455 | 13.2436 | NaN | NaN | NaN | 13.3774 | 96.4479 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 603.4258 | NaN | 17.9806 | NaN | 26.0599
7483.1292 | 13.8516 | 13.686 | 13.7031 | 13.9934 | 13.4399 | 13.7799 | 13.4335 | 13.2441 | NaN | NaN | NaN | 13.3417 | 92.6885 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 606.5703 | NaN | 16.9143 | NaN | 22.3208
7484.1292 | 13.8716 | 13.7425 | 13.6981 | 13.9601 | 13.4693 | 13.7881 | 13.4338 | 13.2422 | NaN | NaN | NaN | 13.3763 | 95.4892 | NaN | NaN | NaN | -4.1553 | NaN | NaN | NaN | NaN | 597.8435 | NaN | 17.8616 | NaN | 26.5457
7485.1292 | 13.8734 | 13.6804 | 13.6965 | 14.0112 | 13.4451 | 13.7686 | 13.4406 | 13.2432 | NaN | NaN | NaN | 13.394 | 97.9668 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 596.6395 | NaN | 17.0724 | NaN | 20.81
7486.1292 | 13.8583 | 13.6565 | 13.7036 | 14.0027 | 13.4585 | 13.7329 | 13.4257 | 13.246 | NaN | NaN | NaN | 13.3534 | 92.7417 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 590.0699 | NaN | 18.6071 | NaN | 23.5182
7487.1292 | 13.9013 | 13.669 | 13.7054 | 14.07 | 13.4513 | 13.7452 | 13.4237 | 13.2463 | NaN | NaN | NaN | 13.3699 | 91.7992 | NaN | NaN | NaN | -3.6288 | NaN | NaN | NaN | NaN | 592.1564 | NaN | 14.8394 | NaN | 25.1389
7488.1292 | 13.8716 | 13.6497 | 13.7068 | 13.9907 | 13.4127 | 13.7343 | 13.4275 | 13.2445 | NaN | NaN | NaN | 13.3471 | 93.7916 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 591.9056 | NaN | 20.4678 | NaN | 25.1487
7489.1292 | 13.8997 | 13.8468 | 13.7113 | 13.9821 | 13.4172 | 13.7789 | 13.4575 | 13.253 | NaN | NaN | NaN | 13.3628 | 93.8188 | NaN | NaN | NaN | -4.0403 | NaN | NaN | NaN | NaN | 582.9762 | NaN | 12.9233 | NaN | 22.0953
7490.1292 | 13.8855 | 13.7214 | 13.7034 | 14.0044 | 13.3055 | 13.7762 | 13.4346 | 13.2465 | NaN | NaN | NaN | 13.3954 | 92.3255 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 574.9547 | NaN | 16.7198 | NaN | 24.6683
7491.1292 | 13.8823 | 13.6567 | 13.7081 | 13.9341 | 13.3896 | 13.7184 | 13.4221 | 13.2474 | NaN | NaN | NaN | 13.3691 | 95.7728 | NaN | NaN | NaN | -18.8158 | NaN | NaN | NaN | NaN | 570.6806 | NaN | 16.4915 | NaN | 25.0821
7492.1292 | 13.8785 | 13.659 | 13.7014 | 13.9557 | 13.3917 | 13.7379 | 13.4302 | 13.2512 | NaN | NaN | NaN | 13.3784 | 92.4568 | NaN | NaN | NaN | -2.6799 | NaN | NaN | NaN | -13.4284 | 575.4709 | NaN | 15.7983 | NaN | 23.3216
7493.1292 | 13.8777 | 13.6999 | 13.7034 | 13.9837 | 13.3184 | 13.77 | 13.4312 | 13.2522 | NaN | NaN | NaN | 13.3446 | 92.2256 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 575.7019 | NaN | 17.0193 | NaN | 26.6142
7494.1292 | 13.8785 | 13.671 | 13.7002 | 14.0122 | 13.4552 | 13.7162 | 13.4206 | 13.2519 | NaN | NaN | NaN | 13.3495 | 93.7507 | NaN | NaN | NaN | -14.9419 | NaN | NaN | NaN | NaN | 576.5879 | NaN | 16.4963 | NaN | 24.4787
7495.1292 | 13.8802 | 13.6562 | 13.6949 | 14.0072 | 13.421 | 13.7367 | 13.4387 | 13.2528 | NaN | NaN | NaN | 13.4466 | 91.9582 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 583.7931 | NaN | 16.1952 | NaN | 24.1414
7496.1292 | 13.8751 | 13.6721 | 13.6999 | 14.0152 | 13.3408 | 13.7247 | 13.421 | 13.2523 | NaN | NaN | NaN | 13.4057 | 91.6457 | NaN | NaN | NaN | -16.3487 | NaN | NaN | NaN | NaN | 598.1336 | NaN | 15.6966 | NaN | 22.3389
7497.1292 | 13.8682 | 13.6452 | 13.6937 | 14.0041 | 13.4039 | 13.7059 | 13.4177 | 13.2564 | NaN | NaN | NaN | 13.3869 | 92.0679 | NaN | NaN | NaN | -13.9073 | NaN | NaN | NaN | NaN | 604.4107 | NaN | 16.2927 | NaN | 22.6638
7498.1292 | 13.868 | 13.7808 | 13.6954 | 13.9717 | 13.4329 | 13.8056 | 13.4359 | 13.2578 | NaN | NaN | NaN | 13.4315 | 93.8473 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 604.1811 | NaN | 17.6306 | NaN | 24.1648
7499.1292 | 13.8534 | 13.7877 | 13.697 | 14.0086 | 13.3499 | 13.8528 | 13.4413 | 13.2542 | NaN | NaN | NaN | 13.441 | 91.0769 | NaN | NaN | NaN | 16.684 | NaN | NaN | NaN | NaN | 604.7751 | NaN | 14.883 | NaN | 24.2591
7500.1292 | 13.8739 | 13.6831 | 13.6935 | 14.0267 | 13.5073 | 13.7312 | 13.4194 | 13.2537 | NaN | NaN | NaN | 13.4017 | 102.7311 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 601.2666 | NaN | 15.6214 | NaN | 23.6435
7501.1292 | 13.8991 | 13.6503 | 13.6858 | 13.9978 | 13.5039 | 13.7175 | 13.4219 | 13.2563 | NaN | NaN | NaN | 13.3613 | 93.2996 | NaN | NaN | NaN | 26.3279 | NaN | NaN | NaN | NaN | 601.7826 | NaN | 15.0766 | NaN | 23.8063
7502.1292 | 13.9291 | 13.7099 | 13.685 | 14.0256 | 13.3035 | 13.7859 | 13.4354 | 13.2531 | NaN | NaN | NaN | 13.3786 | 95.0798 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 600.8073 | NaN | 14.8114 | NaN | 25.5553
7503.1292 | 13.8806 | 13.6643 | 13.6835 | 13.9645 | 13.4043 | 13.7415 | 13.4261 | 13.2545 | NaN | NaN | NaN | 13.4046 | 91.3237 | NaN | NaN | NaN | 4.4112 | NaN | NaN | NaN | NaN | 604.0283 | NaN | 16.9457 | NaN | 25.4752
7504.1292 | 13.8883 | 13.6865 | 13.6828 | 13.9751 | 13.4258 | 13.7401 | 13.4249 | 13.2564 | NaN | NaN | NaN | 13.3655 | 92.6713 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 598.2903 | NaN | 15.8803 | NaN | 23.4593
7505.1292 | 13.8797 | 13.7491 | 13.6818 | 14.0098 | 13.4299 | 13.7877 | 13.4309 | 13.2557 | NaN | NaN | NaN | 13.3633 | 92.4593 | NaN | NaN | NaN | -14.5926 | NaN | NaN | NaN | NaN | 600.7783 | NaN | 16.2056 | NaN | 24.8359
7506.1292 | 13.8762 | 13.7097 | 13.6865 | 13.9801 | 13.4712 | 13.7721 | 13.4319 | 13.2587 | NaN | NaN | NaN | 13.3685 | 94.4348 | NaN | NaN | NaN | -11.0578 | NaN | NaN | NaN | NaN | 603.0689 | NaN | 15.6622 | NaN | 23.6238
7507.1292 | 13.8355 | 13.7004 | 13.6851 | 13.9835 | 13.2793 | 13.7655 | 13.4286 | 13.2525 | NaN | NaN | NaN | 13.3814 | 92.9905 | NaN | NaN | NaN | -11.5901 | NaN | NaN | NaN | NaN | 601.3839 | NaN | 16.5097 | NaN | 24.9181
7508.1292 | 13.9069 | 13.7077 | 13.6866 | 13.9908 | 13.3658 | 13.7833 | 13.4333 | 13.2491 | NaN | NaN | NaN | 13.3505 | 92.0381 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 601.7269 | NaN | 15.9548 | NaN | 25.0413
7509.1292 | 13.8782 | 13.8133 | 13.6916 | 14.032 | 13.4377 | 13.8233 | 13.4514 | 13.2538 | NaN | NaN | NaN | 13.364 | 90.4271 | NaN | NaN | NaN | -16.1921 | NaN | NaN | NaN | NaN | 601.7199 | NaN | 14.9521 | NaN | 23.8703
7510.1292 | 13.8775 | 13.7415 | 13.689 | 13.9719 | 13.355 | 13.7749 | 13.449 | 13.2545 | NaN | NaN | NaN | 13.3889 | 92.0242 | NaN | NaN | NaN | -13.4778 | NaN | NaN | NaN | NaN | 597.7015 | NaN | 17.7581 | NaN | 24.8759
7511.1292 | 13.8807 | 13.7287 | 13.6923 | 13.9672 | 13.4387 | 13.7752 | 13.4331 | 13.2483 | NaN | NaN | NaN | 13.3994 | 96.9158 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 593.972 | NaN | 16.6995 | NaN | 25.0238
7512.1292 | 13.8726 | 13.7978 | 13.6957 | 13.9646 | 13.4611 | 13.758 | 13.4419 | 13.2526 | NaN | NaN | NaN | 13.3767 | 95.131 | NaN | NaN | NaN | 3.5787 | NaN | NaN | NaN | NaN | 595.7644 | NaN | 15.3869 | NaN | 27.0505
7513.1292 | 13.8592 | 13.7049 | 13.6905 | 14.0058 | 13.3519 | 13.7816 | 13.4357 | 13.2474 | NaN | NaN | NaN | 13.4163 | 92.0008 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 595.9824 | NaN | 14.8421 | NaN | 26.6667
7514.1292 | 13.8386 | 13.6871 | 13.6937 | 13.999 | 13.472 | 13.76 | 13.4299 | 13.2511 | NaN | NaN | NaN | 13.3816 | 94.4351 | NaN | NaN | NaN | -14.4795 | NaN | NaN | NaN | NaN | 590.9099 | NaN | 19.7124 | NaN | 23.7179
7515.1292 | 13.8903 | 13.74 | 13.6943 | 13.9487 | 13.3339 | 13.7864 | 13.4322 | 13.2494 | NaN | NaN | NaN | 13.3625 | 91.489 | NaN | NaN | NaN | -12.3407 | NaN | NaN | NaN | NaN | 590.9946 | NaN | 15.9027 | NaN | 23.295
7516.1292 | 13.8866 | 13.6991 | 13.6995 | 13.9908 | 13.3273 | 13.7553 | 13.4328 | 13.2502 | NaN | NaN | NaN | 13.3691 | 96.5671 | NaN | NaN | NaN | -18.8279 | NaN | NaN | NaN | NaN | 596.0032 | NaN | 15.9352 | NaN | 24.7769
7517.1292 | 13.889 | 13.7177 | 13.7035 | 13.9903 | 13.4843 | 13.7794 | 13.4359 | 13.2476 | NaN | NaN | NaN | 13.4139 | 96.0449 | NaN | NaN | NaN | 6.9618 | NaN | NaN | NaN | NaN | 605.0903 | NaN | 15.4831 | NaN | 27.6522
7518.1292 | 13.8915 | 13.6876 | 13.7051 | 14.0052 | 13.4565 | 13.7514 | 13.4213 | 13.2523 | NaN | NaN | NaN | 13.3895 | 95.1083 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 604.5305 | NaN | 17.1452 | NaN | 24.1893
7519.1292 | 13.882 | 13.7446 | 13.7037 | 13.9631 | 13.4885 | 13.7512 | 13.437 | 13.2476 | NaN | NaN | NaN | 13.3729 | 93.6798 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 608.6255 | NaN | 16.5985 | NaN | 25.0785
7520.1292 | 13.8781 | 13.7718 | 13.7 | 13.9627 | 13.3815 | 13.798 | 13.4266 | 13.2581 | NaN | NaN | NaN | 13.3987 | 108.9391 | NaN | NaN | NaN | 17.4719 | NaN | NaN | NaN | NaN | 605.618 | NaN | 18.9121 | NaN | 23.3909
7521.1292 | 13.9049 | 13.6814 | 13.7025 | 13.9947 | 13.3678 | 13.7393 | 13.4301 | 13.2587 | NaN | NaN | NaN | 13.3769 | 95.837 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -19.6204 | 607.1 | NaN | 17.3241 | NaN | 25.3519
7522.1292 | 13.9205 | 13.737 | 13.7005 | 13.9651 | 13.4521 | 13.7718 | 13.4293 | 13.2598 | NaN | NaN | NaN | 13.4287 | 99.1397 | NaN | NaN | NaN | -17.0355 | NaN | NaN | NaN | NaN | 606.8224 | NaN | 13.5585 | NaN | 22.7417
7523.1292 | 13.9111 | 13.7312 | 13.702 | 13.9682 | 13.5505 | 13.7261 | 13.4162 | 13.2659 | NaN | NaN | NaN | 13.3876 | 103.1966 | NaN | NaN | NaN | -12.4478 | NaN | NaN | NaN | NaN | 603.6335 | NaN | 16.4238 | NaN | 27.2531
7524.1292 | 13.9023 | 13.7322 | 13.7073 | 13.9933 | 13.3325 | 13.7662 | 13.4289 | 13.2587 | NaN | NaN | NaN | 13.4029 | 93.354 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 603.2456 | NaN | 15.593 | NaN | 22.7738
7525.1292 | 13.8854 | 13.7003 | 13.7173 | 13.9588 | 13.4396 | 13.7429 | 13.4139 | 13.2597 | NaN | NaN | NaN | 13.3931 | 93.6609 | NaN | NaN | NaN | 8.1915 | NaN | NaN | NaN | NaN | 601.5772 | NaN | 17.2314 | NaN | 22.3877
7526.1292 | 13.873 | 13.69 | 13.7187 | 13.9406 | 13.3769 | 13.7059 | 13.4096 | 13.2637 | NaN | NaN | NaN | 13.3864 | 89.5109 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 595.4058 | NaN | 17.0463 | NaN | 25.4757
7527.1292 | 13.8828 | 13.6793 | 13.7166 | 13.9662 | 13.4124 | 13.7224 | 13.4139 | 13.259 | NaN | NaN | NaN | 13.3993 | 92.6988 | NaN | NaN | NaN | -14.4472 | NaN | NaN | NaN | NaN | 594.465 | NaN | 13.5938 | NaN | 24.9621
7528.1292 | 13.9982 | 13.696 | 13.7191 | 13.9393 | 13.3944 | 13.7499 | 13.4226 | 13.2572 | NaN | NaN | NaN | 13.4137 | 92.5293 | NaN | NaN | NaN | -18.3338 | NaN | NaN | NaN | NaN | 591.3442 | NaN | 13.7691 | NaN | 25.3225
7529.1292 | 13.9098 | 13.7175 | 13.7207 | 14.0058 | 13.3476 | 13.7193 | 13.4156 | 13.2657 | NaN | NaN | NaN | 13.4068 | 92.4322 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 584.5134 | NaN | 16.5296 | NaN | 24.1441
7530.1292 | 13.9237 | 13.7192 | 13.7229 | 13.9468 | 13.4615 | 13.7297 | 13.4269 | 13.2661 | NaN | NaN | NaN | 13.4248 | 94.7048 | NaN | NaN | NaN | 33.0541 | NaN | NaN | NaN | NaN | 574.3407 | NaN | 15.9082 | NaN | 22.6691
7531.1292 | 13.9251 | 13.7797 | 13.7277 | 13.9784 | 13.409 | 13.7387 | 13.441 | 13.2586 | NaN | NaN | NaN | 13.4891 | 94.0247 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 566.9958 | NaN | 16.2274 | NaN | 22.2941
7532.1292 | 13.9533 | 13.7348 | 13.7252 | 13.9862 | 13.474 | 13.7589 | 13.4296 | 13.2631 | NaN | NaN | NaN | 13.4148 | 101.373 | NaN | NaN | NaN | -19.4326 | NaN | NaN | NaN | NaN | 567.7866 | NaN | 17.5208 | NaN | 24.2248
7533.1292 | 13.9558 | 13.7287 | 13.7234 | 13.9941 | 13.4409 | 13.7831 | 13.4362 | 13.262 | NaN | NaN | NaN | 13.4442 | 96.7881 | NaN | NaN | NaN | -6.2446 | NaN | NaN | NaN | NaN | 568.4278 | NaN | 15.4043 | NaN | 23.5911
7534.1292 | 13.9162 | 13.6853 | 13.7264 | 13.9843 | 13.2913 | 13.7181 | 13.4147 | 13.2629 | NaN | NaN | NaN | 13.4206 | 93.0961 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 562.6784 | NaN | 16.1174 | NaN | 23.1832
7535.1292 | 13.9092 | 13.7147 | 13.7256 | 13.9747 | 13.41 | 13.7564 | 13.4188 | 13.2623 | NaN | NaN | NaN | 13.4047 | 91.6781 | NaN | NaN | NaN | -3.0432 | NaN | NaN | NaN | NaN | 563.4382 | NaN | 15.493 | NaN | 25.2244
7536.1292 | 13.9128 | 13.7064 | 13.729 | 13.9864 | 13.5181 | 13.7312 | 13.4175 | 13.2633 | NaN | NaN | NaN | 13.431 | 91.6722 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 563.1041 | NaN | 15.2017 | NaN | 24.9895
7537.1292 | 13.8914 | 13.7434 | 13.7269 | 13.9872 | 13.5031 | 13.7761 | 13.4335 | 13.2681 | NaN | NaN | NaN | 13.4771 | 91.1761 | NaN | NaN | NaN | -16.279 | NaN | NaN | NaN | NaN | 560.6177 | NaN | 16.1835 | NaN | 22.9752
7538.1292 | 13.8839 | 13.7135 | 13.7241 | 13.9785 | 13.4894 | 13.7702 | 13.4374 | 13.2651 | NaN | NaN | NaN | 13.5328 | 92.5607 | NaN | NaN | NaN | 9.8048 | NaN | NaN | NaN | NaN | 554.3477 | NaN | 16.3267 | NaN | 22.0734
7539.1292 | 13.9475 | 13.8224 | 13.7246 | 13.9868 | 13.4777 | 13.8327 | 13.4472 | 13.2737 | NaN | NaN | NaN | 13.4457 | 92.8243 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 554.9416 | NaN | 15.6803 | NaN | 25.9349
7540.1292 | 13.9286 | 13.6906 | 13.7243 | 13.9763 | 13.4016 | 13.7086 | 13.4231 | 13.2713 | NaN | NaN | NaN | 13.4364 | 91.2758 | NaN | NaN | NaN | 28.5051 | NaN | NaN | NaN | NaN | 554.2205 | NaN | 17.2414 | NaN | 23.2916
7541.1292 | 13.9372 | 13.7187 | 13.7195 | 13.9818 | 13.4557 | 13.7473 | 13.4314 | 13.2703 | NaN | NaN | NaN | 13.4493 | 91.1408 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 551.4965 | NaN | 15.7379 | NaN | 25.9127
7542.1292 | 13.9356 | 13.7383 | 13.7275 | 13.9458 | 13.2716 | 13.7838 | 13.4365 | 13.2713 | NaN | NaN | NaN | 13.4388 | 93.6007 | NaN | NaN | NaN | 15.3144 | NaN | NaN | NaN | NaN | 552.0594 | NaN | 16.5278 | NaN | 23.242
7543.1292 | 13.9311 | 13.8794 | 13.7256 | 13.9651 | 13.4069 | 13.8849 | 13.4513 | 13.2711 | NaN | NaN | NaN | 13.4476 | 93.5222 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 548.6082 | NaN | 16.0889 | NaN | 25.3065
7544.1292 | 13.9129 | 13.79 | 13.7282 | 13.998 | 13.3818 | 13.8105 | 13.4477 | 13.2701 | NaN | NaN | NaN | 13.476 | 99.1139 | NaN | NaN | NaN | -18.5847 | NaN | NaN | NaN | -18.3133 | 550.0295 | NaN | 14.4092 | NaN | 24.8264
7545.1292 | 13.9236 | 13.8252 | 13.7296 | 13.9622 | 13.4483 | 13.8565 | 13.4381 | 13.2713 | NaN | NaN | NaN | 13.4629 | 97.0982 | NaN | NaN | NaN | 0.4742 | NaN | NaN | NaN | NaN | 557.343 | NaN | 18.46 | NaN | 22.0042
7546.1292 | 13.9222 | 13.6951 | 13.7226 | 13.9763 | 13.4533 | 13.7346 | 13.4169 | 13.2715 | NaN | NaN | NaN | 13.465 | 92.666 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 556.9645 | NaN | 17.3549 | NaN | 26.752
7547.1292 | 13.8968 | 13.7443 | 13.7283 | 13.9759 | 13.4012 | 13.8066 | 13.4471 | 13.2731 | NaN | NaN | NaN | 13.4947 | 94.3228 | NaN | NaN | NaN | 24.0945 | NaN | NaN | NaN | NaN | 560.5286 | NaN | 15.0986 | NaN | 21.081
7548.1292 | 13.8925 | 13.8744 | 13.7318 | 13.9854 | 13.3807 | 13.7879 | 13.4418 | 13.2714 | NaN | NaN | NaN | 13.4606 | 103.8256 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 559.9977 | NaN | 16.4119 | NaN | 25.3538
7549.1292 | 13.9102 | 13.7413 | 13.7276 | 13.9495 | 13.4332 | 13.7835 | 13.4278 | 13.2746 | NaN | NaN | NaN | 13.4344 | 92.6616 | NaN | NaN | NaN | -16.9752 | NaN | NaN | NaN | -13.9387 | 557.0872 | NaN | 17.1303 | NaN | 27.3692
7550.1292 | 13.9015 | 13.6959 | 13.7341 | 13.9649 | 13.3749 | 13.7354 | 13.4279 | 13.2708 | NaN | NaN | NaN | 13.543 | 91.0495 | NaN | NaN | NaN | -12.7274 | NaN | NaN | NaN | NaN | 555.2413 | NaN | 17.2964 | NaN | 23.5128
7551.1292 | 13.8983 | 13.6929 | 13.7317 | 13.9681 | 13.3851 | 13.7444 | 13.43 | 13.2731 | NaN | NaN | NaN | 13.4933 | 89.643 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 555.9346 | NaN | 16.0395 | NaN | 25.2994
7552.1292 | 13.9135 | 13.7143 | 13.7314 | 13.9733 | 13.3821 | 13.7577 | 13.4339 | 13.2759 | NaN | NaN | NaN | 13.4608 | 92.8682 | NaN | NaN | NaN | -4.4263 | NaN | NaN | NaN | NaN | 562.2663 | NaN | 16.2701 | NaN | 26.2172
7553.1292 | 13.9208 | 13.786 | 13.7418 | 13.9282 | 13.3957 | 13.7638 | 13.4484 | 13.2751 | NaN | NaN | NaN | 13.5299 | 95.6519 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 564.7698 | NaN | 16.0518 | NaN | 18.232
7554.1292 | 13.9022 | 13.754 | 13.7336 | 13.9345 | 13.3624 | 13.7857 | 13.4433 | 13.2722 | NaN | NaN | NaN | 13.4826 | 97.0684 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -3.0652 | 563.9757 | NaN | 19.4505 | NaN | 27.8091
7555.1292 | 13.9118 | 13.7324 | 13.7335 | 13.9151 | 13.4439 | 13.7684 | 13.4394 | 13.2702 | NaN | NaN | NaN | 13.5042 | 91.4776 | NaN | NaN | NaN | 4.8555 | NaN | NaN | NaN | NaN | 560.424 | NaN | 16.0835 | NaN | 25.1037
7556.1292 | 13.919 | 13.8139 | 13.7411 | 13.964 | 13.3647 | 13.8244 | 13.4578 | 13.2788 | NaN | NaN | NaN | 13.4649 | 95.3481 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 556.4542 | NaN | 15.2775 | NaN | 25.7813
7557.1292 | 13.9049 | 13.7319 | 13.7347 | 13.9816 | 13.4007 | 13.7643 | 13.4394 | 13.2792 | NaN | NaN | NaN | 13.4947 | 98.1889 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 558.8674 | NaN | 14.1125 | NaN | 25.3767
7558.1292 | 13.8747 | 13.7203 | 13.7402 | 13.9447 | 13.4203 | 13.7374 | 13.4311 | 13.2752 | NaN | NaN | NaN | 13.4625 | 105.2404 | NaN | NaN | NaN | 23.84 | NaN | NaN | NaN | NaN | 564.1162 | NaN | 17.6378 | NaN | 25.8635
7559.1292 | 13.9518 | 13.7292 | 13.7412 | 13.9965 | 13.4199 | 13.7511 | 13.4472 | 13.2767 | NaN | NaN | NaN | 13.4784 | 96.6499 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 573.0861 | NaN | 14.1191 | NaN | 25.6002
7560.1292 | 13.9624 | 13.7386 | 13.7387 | 13.9995 | 13.2858 | 13.791 | 13.4392 | 13.284 | NaN | NaN | NaN | 13.4472 | 90.7465 | NaN | NaN | NaN | -18.7042 | NaN | NaN | NaN | NaN | 573.7087 | NaN | 15.272 | NaN | 23.5538
7561.1292 | 13.9565 | 13.8109 | 13.7372 | 13.9443 | 13.3746 | 13.8181 | 13.4502 | 13.2832 | NaN | NaN | NaN | 13.4907 | 97.794 | NaN | NaN | NaN | 15.5192 | NaN | NaN | NaN | NaN | 573.5809 | NaN | 13.2993 | NaN | 25.7756
7562.1292 | 13.9603 | 13.7422 | 13.7426 | 13.9533 | 13.4342 | 13.7537 | 13.4388 | 13.2803 | NaN | NaN | NaN | 13.4666 | 91.7181 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 572.2796 | NaN | 16.8332 | NaN | 25.3572
7563.1292 | 13.8987 | 13.7677 | 13.7442 | 13.9826 | 13.447 | 13.7296 | 13.4416 | 13.2793 | NaN | NaN | NaN | 13.509 | 91.1361 | NaN | NaN | NaN | -14.1547 | NaN | NaN | NaN | NaN | 566.2443 | NaN | 15.6538 | NaN | 25.1732
7564.1292 | 13.9544 | 13.7928 | 13.7431 | 13.9867 | 13.4838 | 13.8462 | 13.4629 | 13.277 | NaN | NaN | NaN | 13.454 | 92.9438 | NaN | NaN | NaN | -14.4221 | NaN | NaN | NaN | NaN | 562.7449 | NaN | 14.5018 | NaN | 22.1903
7565.1292 | 13.9557 | 13.715 | 13.7435 | 13.9268 | 13.3537 | 13.7059 | 13.4301 | 13.2785 | NaN | NaN | NaN | 13.4847 | 93.0907 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 569.7118 | NaN | 16.8036 | NaN | 23.4971
7566.1292 | 13.9565 | 13.7397 | 13.7529 | 14.0208 | 13.3884 | 13.7387 | 13.43 | 13.2825 | NaN | NaN | NaN | 13.4762 | 94.4758 | NaN | NaN | NaN | 1.3303 | NaN | NaN | NaN | NaN | 574.9708 | NaN | 14.7768 | NaN | 24.7264
7567.1292 | 13.9541 | 13.6977 | 13.7519 | 13.9969 | 13.4647 | 13.7246 | 13.4364 | 13.2741 | NaN | NaN | NaN | 13.6812 | 94.7634 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 576.8063 | NaN | 14.6357 | NaN | 23.9474
7568.1292 | 13.9573 | 13.734 | 13.7534 | 13.9935 | 13.4283 | 13.7407 | 13.4503 | 13.2773 | NaN | NaN | NaN | 13.6317 | 92.4838 | NaN | NaN | NaN | -15.3047 | NaN | NaN | NaN | -5.3223 | 575.7839 | NaN | 14.1994 | NaN | 25.1696
7569.1292 | 13.9522 | 13.7722 | 13.7576 | 13.9922 | 13.4962 | 13.7801 | 13.4547 | 13.2795 | NaN | NaN | NaN | 13.4673 | 94.2823 | NaN | NaN | NaN | 3.6448 | NaN | NaN | NaN | NaN | 579.5361 | NaN | 15.6776 | NaN | 24.6134
7570.1292 | 13.9521 | 13.7505 | 13.7452 | 14.1098 | 13.4007 | 13.7951 | 13.457 | 13.2821 | NaN | NaN | NaN | 13.4911 | 99.7996 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 589.4719 | NaN | 15.8152 | NaN | 25.7051
7571.1292 | 13.9682 | 13.7358 | 13.7508 | 13.9977 | 13.3298 | 13.7475 | 13.4445 | 13.2779 | NaN | NaN | NaN | 13.4946 | 93.1546 | NaN | NaN | NaN | -15.9669 | NaN | NaN | NaN | NaN | 596.6491 | NaN | 14.7902 | NaN | 23.8642
7572.1292 | 13.9504 | 13.7138 | 13.7494 | 14.0021 | 13.5101 | 13.7319 | 13.4429 | 13.2816 | NaN | NaN | NaN | 13.5025 | 90.8242 | NaN | NaN | NaN | 3.6962 | NaN | NaN | NaN | NaN | 605.4004 | NaN | 17.0688 | NaN | 22.1847
7573.1292 | 13.9416 | 13.7703 | 13.7435 | 13.973 | 13.4026 | 13.7374 | 13.4368 | 13.2783 | NaN | NaN | NaN | 13.5137 | 90.0157 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 604.8586 | NaN | 14.7879 | NaN | 23.2801
7574.1292 | 13.9851 | 13.6974 | 13.7431 | 13.97 | 13.3965 | 13.7 | 13.4376 | 13.2843 | NaN | NaN | NaN | 13.4771 | 95.4643 | NaN | NaN | NaN | 24.9155 | NaN | NaN | NaN | NaN | 601.7836 | NaN | 19.726 | NaN | 22.4197
7575.1292 | 13.9758 | 13.738 | 13.7524 | 13.992 | 13.3863 | 13.7258 | 13.4393 | 13.2808 | NaN | NaN | NaN | 13.5175 | 92.9063 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -6.1964 | 598.9538 | NaN | 16.5699 | NaN | 23.9706
7576.1292 | 13.97 | 13.7143 | 13.749 | 14.0074 | 13.4494 | 13.7376 | 13.4385 | 13.2793 | NaN | NaN | NaN | 13.493 | 89.6153 | NaN | NaN | NaN | -12.7689 | NaN | NaN | NaN | 25.0881 | 596.7378 | NaN | 16.0459 | NaN | 24.7119
7577.1292 | 13.9654 | 13.7281 | 13.7511 | 14.0238 | 13.389 | 13.797 | 13.4661 | 13.2845 | NaN | NaN | NaN | 13.5803 | 93.6259 | NaN | NaN | NaN | -18.6989 | NaN | NaN | NaN | 14.4098 | 594.9914 | NaN | 14.5134 | NaN | 22.8381
7578.1292 | 14.1326 | 13.7443 | 13.7535 | 13.9478 | 13.4964 | 13.7255 | 13.4566 | 13.2857 | NaN | NaN | NaN | 13.5073 | 94.04 | NaN | NaN | NaN | -11.3134 | NaN | NaN | NaN | 42.5679 | 584.8369 | NaN | 13.9001 | NaN | 26.2118
7579.1292 | 14.0074 | 13.8466 | 13.7578 | 13.9607 | 13.4553 | 13.7119 | 13.457 | 13.2924 | NaN | NaN | NaN | 13.4854 | 92.1549 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.7656 | 585.1994 | NaN | 13.1287 | NaN | 23.9901
7580.1292 | 14.1008 | 13.724 | 13.7568 | 14.0228 | 13.3923 | 13.7209 | 13.4424 | 13.2834 | NaN | NaN | NaN | 13.4808 | 91.8674 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 37.2159 | 587.0878 | NaN | 15.5875 | NaN | 25.6741
7581.1292 | 13.9978 | 13.7233 | 13.7494 | 14.0259 | 13.3718 | 13.687 | 13.4391 | 13.2856 | NaN | NaN | NaN | 13.5142 | 109.9751 | NaN | NaN | NaN | 10.2223 | NaN | NaN | NaN | 12.2908 | 592.2696 | NaN | 16.6841 | NaN | 21.5651
7582.1292 | 13.9765 | 13.7563 | 13.7579 | 14.0284 | 13.4056 | 13.7187 | 13.4497 | 13.2917 | NaN | NaN | NaN | 13.4986 | 93.0305 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 30.359 | 590.1777 | NaN | 14.5988 | NaN | 23.9467
7583.1292 | 13.9875 | 13.7935 | 13.7574 | 14.0234 | 13.3605 | 13.8264 | 13.4643 | 13.2781 | NaN | NaN | NaN | 13.5947 | 92.5479 | NaN | NaN | NaN | -17.3113 | NaN | NaN | NaN | 14.4418 | 594.2496 | NaN | 14.1586 | NaN | 24.6103
7584.1292 | 14.0097 | 13.7177 | 13.7522 | 14.0132 | 13.3252 | 13.7094 | 13.4417 | 13.2867 | NaN | NaN | NaN | 13.5055 | 94.3673 | NaN | NaN | NaN | 3.5081 | NaN | NaN | NaN | 12.0349 | 602.8759 | NaN | 16.3521 | NaN | 21.6325
7585.1292 | 14.0082 | 13.7365 | 13.7581 | 13.9659 | 13.4862 | 13.7408 | 13.443 | 13.2864 | NaN | NaN | NaN | 13.4859 | 97.7647 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 603.9947 | NaN | 15.3437 | NaN | 24.8005
7586.1292 | 14.0099 | 13.7585 | 13.7608 | 14.0122 | 13.3734 | 13.7566 | 13.4459 | 13.296 | NaN | NaN | NaN | 13.4943 | 94.1898 | NaN | NaN | NaN | -13.2786 | NaN | NaN | NaN | -17.4315 | 609.8265 | NaN | 18.4835 | NaN | 22.5736
7587.1292 | 13.988 | 13.7127 | 13.7572 | 14.0079 | 13.4201 | 13.7091 | 13.4326 | 13.2925 | NaN | NaN | NaN | 13.6195 | 94.7427 | NaN | NaN | NaN | -17.6371 | NaN | NaN | NaN | 21.06 | 609.1116 | NaN | 15.9269 | NaN | 20.8395
7588.1292 | 13.9627 | 13.7887 | 13.7641 | 13.9653 | 13.4554 | 13.7954 | 13.4671 | 13.3032 | NaN | NaN | NaN | 13.5184 | 94.2667 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 18.4213 | 613.9599 | NaN | 18.3569 | NaN | 24.5383
7589.1292 | 14.0775 | 13.7164 | 13.7602 | 14.04 | 13.4938 | 13.7174 | 13.4423 | 13.3019 | NaN | NaN | NaN | 13.4992 | 90.9291 | NaN | NaN | NaN | -18.2549 | NaN | NaN | NaN | 13.7204 | 616.4857 | NaN | 16.1068 | NaN | 22.27
7590.1292 | 14.0147 | 13.738 | 13.7706 | 14.0216 | 13.4538 | 13.7385 | 13.4496 | 13.3071 | NaN | NaN | NaN | 13.5316 | 92.3458 | NaN | NaN | NaN | 22.9999 | NaN | NaN | NaN | 18.4966 | 614.4758 | NaN | 14.4366 | NaN | 25.6684
7591.1292 | 14.0039 | 13.809 | 13.7665 | 14.0191 | 13.4929 | 13.7969 | 13.4719 | 13.3127 | NaN | NaN | NaN | 13.5549 | 89.5421 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 40.385 | 610.7272 | NaN | 15.6269 | NaN | 26.0974
7592.1292 | 14.0085 | 13.7342 | 13.761 | 13.9656 | 13.4319 | 13.7287 | 13.451 | 13.3199 | NaN | NaN | NaN | 13.6303 | 99.2868 | NaN | NaN | NaN | -6.9502 | NaN | NaN | NaN | 15.3337 | 610.2766 | NaN | 13.3802 | NaN | 24.2361
7593.1292 | 14.0163 | 13.7553 | 13.7695 | 13.9881 | 13.4027 | 13.8679 | 13.4804 | 13.3174 | NaN | NaN | NaN | 13.515 | 91.7919 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 21.5316 | 611.0896 | NaN | 14.1733 | NaN | 23.8842
7594.1292 | 14.012 | 13.72 | 13.7659 | 14.075 | 13.368 | 13.7298 | 13.469 | 13.3264 | NaN | NaN | NaN | 13.5271 | 94.6671 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 27.7972 | 602.2644 | NaN | 18.4152 | NaN | 21.3438
7595.1292 | 14.0177 | 13.7243 | 13.7714 | 13.9969 | 13.4224 | 13.7271 | 13.4649 | 13.3312 | NaN | NaN | NaN | 13.5149 | 91.2023 | NaN | NaN | NaN | 22.7757 | NaN | NaN | NaN | 21.141 | 593.3906 | NaN | 15.794 | NaN | 23.2787
7596.1292 | 14.0091 | 13.8863 | 13.7735 | 13.9718 | 13.3895 | 13.8249 | 13.4949 | 13.3257 | NaN | NaN | NaN | 13.5156 | 90.2029 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.883 | 583.1171 | NaN | 16.2068 | NaN | 24.1931
7597.1292 | 13.9868 | 13.7528 | 13.7703 | 14.0187 | 13.5277 | 13.7428 | 13.4755 | 13.3261 | NaN | NaN | NaN | 13.5189 | 93.4822 | NaN | NaN | NaN | -12.9899 | NaN | NaN | NaN | 26.652 | 584.1563 | NaN | 16.2626 | NaN | 26.1565
7598.1292 | 14.0077 | 13.7398 | 13.7747 | 14.082 | 13.3263 | 13.757 | 13.4664 | 13.3241 | NaN | NaN | NaN | 13.4856 | 99.2414 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 29.9886 | 587.4654 | NaN | 13.6457 | NaN | 26.9486
7599.1292 | 14.4522 | 13.7977 | 13.7792 | 13.9749 | 13.4324 | 13.8378 | 13.4959 | 13.3305 | NaN | NaN | NaN | 13.5796 | 95.9743 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.7471 | 587.2613 | NaN | 16.7063 | NaN | 25.2983
7600.1292 | 14.0397 | 13.7582 | 13.7779 | 14.0184 | 13.5112 | 13.7885 | 13.4841 | 13.3268 | NaN | NaN | NaN | 13.5389 | 91.3347 | NaN | NaN | NaN | -10.116 | NaN | NaN | NaN | 16.9535 | 580.8062 | NaN | 15.3495 | NaN | 22.6205
7601.1292 | 14.0482 | 13.735 | 13.7871 | 14.0336 | 13.5224 | 13.7601 | 13.4773 | 13.3353 | NaN | NaN | NaN | 13.509 | 92.5513 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 28.0722 | 581.8412 | NaN | 16.6616 | NaN | 23.4543
7602.1292 | 14.0533 | 13.8221 | 13.7894 | 13.9853 | 13.5048 | 13.7781 | 13.4891 | 13.3344 | NaN | NaN | NaN | 13.5086 | 92.5149 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 57.2757 | 576.3621 | NaN | 15.0382 | NaN | 24.7084
7603.1292 | 14.0368 | 13.7558 | 13.7802 | 13.974 | 13.3724 | 13.7841 | 13.4931 | 13.3377 | NaN | NaN | NaN | 13.5171 | 96.9614 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.0648 | 568.6411 | NaN | 19.8117 | NaN | 24.1605
7604.1292 | 14.0386 | 13.8767 | 13.7777 | 14.0418 | 13.326 | 13.7864 | 13.5025 | 13.3359 | NaN | NaN | NaN | 13.5184 | 101.6753 | NaN | NaN | NaN | 22.219 | NaN | NaN | NaN | 25.6575 | 571.3281 | NaN | 14.2771 | NaN | 21.5885
7605.1292 | 14.0301 | 13.8016 | 13.7814 | 14.087 | 13.4268 | 13.7923 | 13.4976 | 13.3401 | NaN | NaN | NaN | 13.5181 | 92.3514 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.8974 | 571.9345 | NaN | 13.1924 | NaN | 26.1481
7606.1292 | 14.0292 | 13.7856 | 13.7786 | 13.9597 | 13.4265 | 13.7551 | 13.4924 | 13.3451 | NaN | NaN | NaN | 13.5441 | 96.8146 | NaN | NaN | NaN | -18.3077 | NaN | NaN | NaN | 14.4922 | 568.5634 | NaN | 12.3595 | NaN | 23.8766
7607.1292 | 14.0323 | 13.7744 | 13.7853 | 14.0127 | 13.4321 | 13.7468 | 13.4862 | 13.3442 | NaN | NaN | NaN | 13.5344 | 93.0837 | NaN | NaN | NaN | 16.5444 | NaN | NaN | NaN | NaN | 572.7149 | NaN | 16.3671 | NaN | 23.6892
7608.1448 | 14.0445 | 13.8014 | 13.7868 | 14.0199 | 13.4178 | 13.7566 | 13.5032 | 13.3414 | NaN | NaN | NaN | 13.507 | 93.29 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 566.1202 | NaN | 13.0485 | NaN | 24.6461
7609.1448 | 14.038 | 13.7668 | 13.7838 | 13.9805 | 13.3526 | 13.7928 | 13.494 | 13.3415 | NaN | NaN | NaN | 13.5248 | 93.3426 | NaN | NaN | NaN | -14.3944 | NaN | NaN | NaN | NaN | 564.4914 | NaN | 14.7217 | NaN | 23.4484
7610.1292 | 14.0658 | 13.7986 | 13.7851 | 14.0573 | 13.3961 | 13.786 | 13.4932 | 13.345 | NaN | NaN | NaN | 13.5108 | 92.1422 | NaN | NaN | NaN | 2.7048 | NaN | NaN | NaN | NaN | 567.6305 | NaN | 14.4235 | NaN | 24.1139
7611.1292 | 14.0429 | 13.7745 | 13.7859 | 13.9771 | 13.4203 | 13.8087 | 13.5073 | 13.3424 | NaN | NaN | NaN | 13.6602 | 93.482 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 568.5394 | NaN | 16.8559 | NaN | 23.6444
7612.1292 | 14.051 | 13.794 | 13.7868 | 14.0139 | 13.5022 | 13.7681 | 13.4987 | 13.3535 | NaN | NaN | NaN | 13.5621 | 109.2126 | NaN | NaN | NaN | 16.3283 | NaN | NaN | NaN | -18.0597 | 570.2645 | NaN | 15.7222 | NaN | 25.895
7613.1292 | 14.0497 | 13.8261 | 13.7865 | 14.0565 | 13.5081 | 13.7871 | 13.4998 | 13.3466 | NaN | NaN | NaN | 13.5744 | 92.4265 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.7967 | 575.0943 | NaN | 16.6859 | NaN | 24.3651
7614.1292 | 14.0514 | 13.7987 | 13.7967 | 14.0005 | 13.4516 | 13.8324 | 13.501 | 13.3475 | NaN | NaN | NaN | 13.5303 | 100.7354 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -15.5247 | 575.7505 | NaN | 17.1218 | NaN | 23.9642
7615.1292 | 14.0547 | 13.7952 | 13.8005 | 14.0356 | 13.4175 | 13.7778 | 13.4979 | 13.3494 | NaN | NaN | NaN | 13.4995 | 95.9009 | NaN | NaN | NaN | 17.4137 | NaN | NaN | NaN | -3.4273 | 574.3986 | NaN | 13.6096 | NaN | 23.5567
7616.1292 | 14.0458 | 13.7736 | 13.8014 | 14.0941 | 13.4699 | 13.7677 | 13.5021 | 13.3477 | NaN | NaN | NaN | 13.5171 | 93.0544 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 18.8364 | 586.3724 | NaN | 15.3737 | NaN | 24.3475
7617.1292 | 14.0473 | 13.7937 | 13.8046 | 14.057 | 13.3965 | 13.7859 | 13.4929 | 13.3477 | NaN | NaN | NaN | 13.6655 | 94.9343 | NaN | NaN | NaN | -19.0979 | NaN | NaN | NaN | 10.4182 | 591.5896 | NaN | 14.9352 | NaN | 25.0972
7618.1292 | 14.0519 | 13.7768 | 13.7944 | 14.0161 | 13.4891 | 13.7857 | 13.4875 | 13.3573 | NaN | NaN | NaN | 13.5444 | 95.5286 | NaN | NaN | NaN | 9.7601 | NaN | NaN | NaN | 11.6783 | 599.0798 | NaN | 13.7992 | NaN | 26.2237
7619.1292 | 14.0593 | 13.7631 | 13.7935 | 14.0473 | 13.4403 | 13.8048 | 13.4978 | 13.3626 | NaN | NaN | NaN | 13.5345 | 97.3597 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 2.4195 | 604.1007 | NaN | 14.657 | NaN | 25.651
7620.1292 | 14.0766 | 13.7584 | 13.7922 | 14.0837 | 13.526 | 13.7756 | 13.5022 | 13.3551 | NaN | NaN | NaN | 13.5496 | 92.1915 | NaN | NaN | NaN | -13.0683 | NaN | NaN | NaN | 14.6204 | 607.6391 | NaN | 15.3461 | NaN | 24.5201
7621.1292 | 14.0686 | 13.7535 | 13.799 | 14.0461 | 13.5636 | 13.7836 | 13.4985 | 13.3638 | NaN | NaN | NaN | 13.5473 | 94.4013 | NaN | NaN | NaN | 30.1188 | NaN | NaN | NaN | 13.4692 | 602.4443 | NaN | 16.1329 | NaN | 24.273
7622.1292 | 14.0693 | 13.8078 | 13.8032 | 14.0708 | 13.4869 | 13.7926 | 13.4948 | 13.364 | NaN | NaN | NaN | 13.5449 | 94.2472 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 19.2293 | 608.4304 | NaN | 16.2616 | NaN | 23.4889
7623.1292 | 14.09 | 13.8113 | 13.7979 | 14.0355 | 13.4716 | 13.7797 | 13.5093 | 13.3625 | NaN | NaN | NaN | 13.5348 | 94.0523 | NaN | NaN | NaN | 22.9162 | NaN | NaN | NaN | -0.6561 | 609.6819 | NaN | 14.8356 | NaN | 22.8917
7624.1292 | 14.0556 | 13.8518 | 13.7983 | 14.0617 | 13.5503 | 13.7996 | 13.5226 | 13.3617 | NaN | NaN | NaN | 13.5522 | 92.7163 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.8027 | 608.7541 | NaN | 13.871 | NaN | 24.3314
7625.1292 | 14.0453 | 13.7822 | 13.7983 | 14.0629 | 13.4961 | 13.7419 | 13.494 | 13.3653 | NaN | NaN | NaN | 13.5741 | 89.9309 | NaN | NaN | NaN | -8.3976 | NaN | NaN | NaN | 16.2852 | 601.6644 | NaN | 15.3148 | NaN | 23.5197
7626.1292 | 14.0239 | 13.7793 | 13.8012 | 14.0738 | 13.5395 | 13.7813 | 13.5033 | 13.3698 | NaN | NaN | NaN | 13.5808 | 91.9913 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.1179 | 604.7967 | NaN | 16.3072 | NaN | 24.8781
7627.1292 | 14.0736 | 13.9135 | 13.8044 | 14.0816 | 13.5399 | 13.8838 | 13.5261 | 13.3672 | NaN | NaN | NaN | 13.5762 | 92.5418 | NaN | NaN | NaN | -12.3281 | NaN | NaN | NaN | 1.0045 | 601.8815 | NaN | 17.8455 | NaN | 22.0755
7628.1292 | 14.0613 | 13.837 | 13.7983 | 14.0906 | 13.489 | 13.8717 | 13.5179 | 13.3737 | NaN | NaN | NaN | 13.5567 | 88.9621 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 592.7129 | NaN | 13.9464 | NaN | 23.2546
7629.1292 | 14.0379 | 13.754 | 13.8018 | 14.0688 | 13.4827 | 13.7638 | 13.5075 | 13.3681 | NaN | NaN | NaN | 13.6451 | 95.329 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 597.0167 | NaN | 19.0611 | NaN | 22.1752
7630.1292 | 14.0511 | 13.8177 | 13.8043 | 14.0829 | 13.5458 | 13.8226 | 13.5184 | 13.3785 | NaN | NaN | NaN | 13.5734 | 90.7622 | NaN | NaN | NaN | -18.5687 | NaN | NaN | NaN | -16.8775 | 598.5412 | NaN | 14.6671 | NaN | 24.658
7631.1292 | 14.086 | 13.8112 | 13.8061 | 14.1026 | 13.4156 | 13.8444 | 13.5244 | 13.3695 | NaN | NaN | NaN | 13.5606 | 97.8923 | NaN | NaN | NaN | 15.3525 | NaN | NaN | NaN | NaN | 607.4714 | NaN | 15.3443 | NaN | 22.1714
7632.1292 | 14.0733 | 13.7691 | 13.8062 | 14.0756 | 13.4568 | 13.8376 | 13.5262 | 13.3742 | NaN | NaN | NaN | 13.5711 | 96.2177 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 612.4464 | NaN | 15.5233 | NaN | 24.3778
7633.1292 | 14.0571 | 13.7985 | 13.8068 | 14.0713 | 13.4471 | 13.8012 | 13.5249 | 13.3814 | NaN | NaN | NaN | 13.5828 | 99.4912 | NaN | NaN | NaN | -8.8032 | NaN | NaN | NaN | NaN | 606.8606 | NaN | 16.0786 | NaN | 23.5627
7634.1292 | 14.0529 | 13.7754 | 13.8025 | 14.0406 | 13.4259 | 13.7862 | 13.5154 | 13.3769 | NaN | NaN | NaN | 13.5623 | 94.0299 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 601.3711 | NaN | 14.7735 | NaN | 25.3218
7635.1292 | 14.051 | 13.8036 | 13.8042 | 14.0759 | 13.4608 | 13.842 | 13.5218 | 13.3769 | NaN | NaN | NaN | 13.6646 | 92.858 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -16.3776 | 601.0618 | NaN | 15.9696 | NaN | 24.2919
7636.1292 | 14.0455 | 13.8171 | 13.8025 | 14.0888 | 13.4479 | 13.8167 | 13.5323 | 13.3895 | NaN | NaN | NaN | 13.6069 | 97.4745 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 598.0504 | NaN | 13.1684 | NaN | 23.9039
7637.1292 | 14.0974 | 13.8126 | 13.8049 | 14.0361 | 13.5013 | 13.7976 | 13.5351 | 13.3783 | NaN | NaN | NaN | 13.6129 | 92.4447 | NaN | NaN | NaN | 32.8991 | NaN | NaN | NaN | NaN | 600.5819 | NaN | 15.3879 | NaN | 23.3732
7638.1292 | 14.0233 | 13.7747 | 13.8085 | 14.0847 | 13.5686 | 13.7988 | 13.5218 | 13.3817 | NaN | NaN | NaN | 13.6248 | 93.6256 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 599.8966 | NaN | 15.3684 | NaN | 23.0354
7639.1292 | 14.0435 | 13.7877 | 13.8129 | 14.0653 | 13.4647 | 13.8176 | 13.5289 | 13.3861 | NaN | NaN | NaN | 13.5787 | 93.5539 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 603.2548 | NaN | 16.0997 | NaN | 23.8738
7640.1292 | 14.0873 | 13.7822 | 13.8128 | 14.1491 | 13.5374 | 13.8077 | 13.5321 | 13.3867 | NaN | NaN | NaN | 13.5712 | 94.064 | NaN | NaN | NaN | -6.4808 | NaN | NaN | NaN | NaN | 606.8937 | NaN | 16.5262 | NaN | 25.0347
7641.1292 | 14.1241 | 13.8009 | 13.817 | 14.1078 | 13.5427 | 13.7871 | 13.528 | 13.3938 | NaN | NaN | NaN | 13.6238 | 92.9884 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 604.0569 | NaN | 15.5395 | NaN | 21.8474
7642.1292 | 14.0833 | 13.8407 | 13.8165 | 14.1092 | 13.5792 | 13.8171 | 13.5389 | 13.3928 | NaN | NaN | NaN | 13.6059 | 94.7671 | NaN | NaN | NaN | -3.2978 | NaN | NaN | NaN | NaN | 606.8042 | NaN | 15.0727 | NaN | 23.8185
7643.1292 | 14.2648 | 13.7949 | 13.818 | 14.0794 | 13.5127 | 13.7921 | 13.5404 | 13.3917 | NaN | NaN | NaN | 13.636 | 92.2307 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 607.4755 | NaN | 16.2597 | NaN | 22.4692
7644.1292 | 14.0815 | 13.7905 | 13.8152 | 14.059 | 13.4708 | 13.8017 | 13.5361 | 13.391 | NaN | NaN | NaN | 13.6763 | 102.4773 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 606.2191 | NaN | 17.2648 | NaN | 25.6411
7645.1292 | 14.0858 | 13.8305 | 13.8097 | 14.1086 | 13.4751 | 13.8184 | 13.5464 | 13.3898 | NaN | NaN | NaN | 13.5717 | 91.2648 | NaN | NaN | NaN | -11.4513 | NaN | NaN | NaN | NaN | 598.3047 | NaN | 17.0562 | NaN | 24.3148
7646.1292 | 14.0894 | 13.8207 | 13.808 | 14.1029 | 13.5125 | 13.8242 | 13.5369 | 13.3922 | NaN | NaN | NaN | 13.586 | 95.5319 | NaN | NaN | NaN | -15.7773 | NaN | NaN | NaN | NaN | 601.8243 | NaN | 15.0263 | NaN | 26.1485
7647.1292 | 14.1036 | 13.785 | 13.8049 | 14.1007 | 13.6165 | 13.7688 | 13.5287 | 13.3931 | NaN | NaN | NaN | 13.6207 | 125.4007 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 24.5879 | 573.3922 | NaN | 3.4801 | NaN | 19.6031
7648.1292 | 14.0886 | 13.85 | 13.8127 | 14.1112 | 13.5712 | 13.7826 | 13.5292 | 13.3965 | NaN | NaN | NaN | 13.5766 | 123.7506 | NaN | NaN | NaN | 17.1644 | NaN | NaN | NaN | 30.4025 | 561.9457 | NaN | 1.9347 | NaN | 18.9236
7649.1292 | 14.0933 | 13.8158 | 13.8112 | 14.101 | 13.6364 | 13.778 | 13.535 | 13.3956 | NaN | NaN | NaN | 13.6123 | 137.6473 | NaN | NaN | 3.6571 | NaN | NaN | NaN | NaN | 13.9129 | 554.1777 | NaN | 2.2879 | NaN | 17.056
7650.1292 | 14.0816 | 13.8194 | 13.8176 | 14.081 | 13.6199 | 13.7772 | 13.5352 | 13.3961 | NaN | NaN | NaN | 13.5622 | 128.4797 | NaN | NaN | 47.3566 | NaN | NaN | NaN | NaN | 14.7629 | 552.9985 | NaN | 24.6749 | NaN | 15.1005
7651.1292 | 14.09 | 13.9152 | 13.8182 | 14.1156 | 13.6147 | 13.799 | 13.5494 | 13.4045 | NaN | NaN | NaN | 13.592 | 134.0336 | NaN | NaN | 42.0359 | NaN | NaN | NaN | NaN | NaN | 545.4433 | NaN | 7.6059 | NaN | 8.8288
7652.1292 | 14.0823 | 13.8072 | 13.8176 | 14.0762 | 13.5775 | 13.7851 | 13.5312 | 13.4001 | NaN | NaN | NaN | 13.571 | 126.5148 | NaN | NaN | 15.3362 | NaN | NaN | NaN | NaN | NaN | 541.3499 | NaN | 3.5948 | NaN | 23.5198
7653.1292 | 14.0966 | 13.7836 | 13.8114 | 14.1074 | 13.5667 | 13.7758 | 13.5279 | 13.4037 | NaN | NaN | NaN | 13.5798 | 120.2942 | NaN | NaN | 40.6368 | NaN | NaN | NaN | NaN | -16.4824 | 530.5452 | NaN | 14.8382 | NaN | 29.1665
7654.1292 | 14.0824 | 13.8376 | 13.8101 | 14.077 | 13.6279 | 13.7873 | 13.5296 | 13.4007 | NaN | NaN | NaN | 13.5847 | 139.1835 | NaN | NaN | 61.3385 | -1.7384 | NaN | NaN | NaN | NaN | 527.1232 | NaN | 12.9456 | NaN | 23.2059
7655.1292 | 14.0937 | 13.8253 | 13.8192 | 14.1043 | 13.6077 | 13.7896 | 13.533 | 13.4029 | NaN | NaN | NaN | 13.5948 | 133.364 | NaN | NaN | 16.6267 | NaN | NaN | NaN | NaN | NaN | 518.7589 | NaN | 14.906 | NaN | 19.0317
7656.1292 | 14.0999 | 13.8053 | 13.809 | 14.1779 | 13.6272 | 13.7789 | 13.5216 | 13.4034 | NaN | NaN | NaN | 13.6031 | 126.933 | NaN | NaN | 60.466 | NaN | NaN | NaN | NaN | 7.311 | 507.9839 | NaN | 1.225 | NaN | 13.8262
7657.1292 | 14.0865 | 13.7971 | 13.8128 | 14.1045 | 13.6101 | 13.7762 | 13.5244 | 13.3986 | NaN | NaN | NaN | 13.61 | 123.3777 | NaN | NaN | 36.7202 | NaN | NaN | NaN | NaN | NaN | 501.69 | NaN | 15.5146 | NaN | 20.5491
7658.1292 | 14.1214 | 13.802 | 13.8131 | 14.1194 | 13.6314 | 13.7856 | 13.5308 | 13.403 | NaN | NaN | NaN | 13.6066 | 133.5159 | NaN | NaN | 61.561 | NaN | NaN | NaN | NaN | 19.0133 | 499.0866 | NaN | 21.6177 | NaN | 14.6163
7659.1292 | 14.0803 | 13.8072 | 13.8211 | 14.0824 | 13.5924 | 13.7772 | 13.5254 | 13.3984 | NaN | NaN | NaN | 13.6163 | 120.0402 | NaN | NaN | 74.5995 | NaN | NaN | NaN | NaN | 32.3768 | 500.0652 | NaN | 1.6894 | NaN | 20.1777
7660.1292 | 14.0821 | 13.8258 | 13.8155 | 14.1222 | 13.6149 | 13.7861 | 13.5343 | 13.4013 | NaN | NaN | NaN | 13.6654 | 138.616 | NaN | NaN | -1.8041 | 9.019 | NaN | NaN | NaN | 19.4916 | 493.7947 | NaN | 14.8313 | NaN | 20.3427
7661.1292 | 14.0731 | 13.8038 | 13.8237 | 14.1052 | 13.6425 | 13.7838 | 13.529 | 13.3979 | NaN | NaN | NaN | 13.6124 | 135.275 | NaN | NaN | -16.612 | NaN | NaN | NaN | NaN | 17.6159 | 486.4766 | NaN | 11.4029 | NaN | 27.2472
7662.1292 | 14.0872 | 13.8129 | 13.8233 | 14.1186 | 13.6034 | 13.7784 | 13.5264 | 13.3991 | NaN | NaN | NaN | 13.5988 | 132.6484 | NaN | NaN | 45.6466 | NaN | NaN | NaN | NaN | 38.7647 | 483.8145 | NaN | 13.3111 | NaN | 9.5374
7663.1292 | 14.064 | 13.8206 | 13.8186 | 14.1039 | 13.5711 | 13.7677 | 13.5253 | 13.3909 | NaN | NaN | NaN | 13.655 | 133.8766 | NaN | NaN | 43.6654 | NaN | NaN | NaN | NaN | 25.4483 | 483.2847 | NaN | 7.5269 | NaN | 16.1011
7664.1292 | 14.0816 | 13.8122 | 13.8179 | 14.1253 | 13.6223 | 13.7658 | 13.5303 | 13.3889 | NaN | NaN | NaN | 13.5984 | 138.9049 | NaN | NaN | 29.6958 | NaN | NaN | NaN | NaN | 36.5373 | 482.9667 | NaN | 11.9765 | NaN | 22.28
7665.1292 | 14.0853 | 13.8083 | 13.8147 | 14.1209 | 13.6365 | 13.7683 | 13.5261 | 13.3867 | NaN | NaN | NaN | 13.6019 | 124.3228 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 30.9355 | 490.1827 | NaN | 1.9158 | NaN | 15.2349
7666.1292 | 14.071 | 13.8422 | 13.8164 | 14.1107 | 13.6046 | 13.7655 | 13.5283 | 13.3803 | NaN | NaN | NaN | 13.6224 | 129.2403 | NaN | NaN | 17.3995 | -19.7652 | NaN | NaN | NaN | 15.8895 | 494.0825 | NaN | 31.6566 | NaN | 21.5108
7667.1292 | 14.0811 | 13.8058 | 13.826 | 14.1299 | 13.6302 | 13.7601 | 13.5286 | 13.3818 | NaN | NaN | NaN | 13.5808 | 121.1277 | NaN | NaN | 46.7087 | 5.9087 | NaN | NaN | NaN | 34.0611 | 497.9853 | NaN | 15.4233 | NaN | 14.057
7668.1292 | 14.072 | 13.8424 | 13.8194 | 14.1171 | 13.5795 | 13.7683 | 13.5306 | 13.3814 | NaN | NaN | NaN | 13.5988 | 137.4252 | NaN | NaN | 84.8816 | NaN | NaN | NaN | NaN | 37.9007 | 501.2183 | NaN | 22.0325 | NaN | 26.499
7669.1292 | 14.0786 | 13.8093 | 13.8249 | 14.1279 | 13.6129 | 13.7714 | 13.5335 | 13.3817 | NaN | NaN | NaN | 13.5903 | 121.0143 | NaN | NaN | 58.8595 | NaN | NaN | NaN | NaN | 30.5411 | 508.6155 | NaN | 7.0037 | NaN | 12.8339
7670.1292 | 14.0784 | 13.8817 | 13.8206 | 14.1035 | 13.6532 | 13.7821 | 13.5394 | 13.3845 | NaN | NaN | NaN | 13.6248 | 141.5596 | NaN | NaN | 64.4782 | NaN | NaN | NaN | NaN | 40.8157 | 510.5997 | NaN | 21.61 | NaN | 26.9428
7671.1292 | 14.0769 | 13.8163 | 13.82 | 14.1199 | 13.6259 | 13.7806 | 13.5298 | 13.3735 | NaN | NaN | NaN | 13.5968 | 129.2916 | NaN | NaN | 37.4561 | NaN | NaN | NaN | NaN | 53.5651 | 513.0761 | NaN | 5.3378 | NaN | 16.9164
7672.1292 | 14.0811 | 13.8141 | 13.8164 | 14.1265 | 13.6573 | 13.7822 | 13.5395 | 13.3746 | NaN | NaN | NaN | 13.6024 | 129.056 | NaN | NaN | 39.9815 | NaN | NaN | NaN | NaN | 42.3109 | 518.7383 | NaN | 22.3101 | NaN | 16.8647
7673.1292 | 14.0727 | 13.8146 | 13.8214 | 14.0869 | 13.6177 | 13.7787 | 13.5364 | 13.371 | NaN | NaN | NaN | 13.5979 | 132.5521 | NaN | NaN | 42.6179 | -7.1803 | NaN | NaN | NaN | 47.0867 | 528.7232 | NaN | 8.6238 | NaN | 17.2271
7674.1292 | 14.0821 | 13.8235 | 13.8217 | 14.134 | 13.6305 | 13.7842 | 13.5322 | 13.3737 | NaN | NaN | NaN | 13.577 | 139.4194 | NaN | NaN | 23.7551 | NaN | NaN | NaN | NaN | 41.2839 | 528.7782 | NaN | 37.1211 | NaN | 19.0684
7675.1292 | 14.1061 | 13.833 | 13.826 | 14.0982 | 13.5467 | 13.7963 | 13.5407 | 13.3746 | NaN | NaN | NaN | 13.6089 | 122.5107 | NaN | NaN | 39.859 | NaN | NaN | NaN | NaN | 29.8408 | 524.1075 | NaN | 8.9355 | NaN | 16.0113
7676.1292 | 14.0837 | 13.8766 | 13.8233 | 14.132 | 13.6576 | 13.7961 | 13.5393 | 13.367 | NaN | NaN | NaN | 13.5951 | 136.4755 | NaN | NaN | 45.4162 | NaN | NaN | NaN | NaN | 34.8509 | 529.4117 | NaN | 10.1407 | NaN | 22.2307
7677.1292 | 14.0811 | 13.8663 | 13.8221 | 14.0979 | 13.617 | 13.8054 | 13.5417 | 13.3613 | NaN | NaN | NaN | 13.5667 | 126.7229 | NaN | NaN | 21.412 | NaN | NaN | NaN | NaN | 36.4046 | 531.8148 | NaN | 1.559 | NaN | 26.9356
7678.1292 | 14.0852 | 13.8266 | 13.8227 | 14.1316 | 13.6498 | 13.7807 | 13.5268 | 13.3635 | NaN | NaN | NaN | 13.579 | 137.7414 | NaN | NaN | 29.1787 | NaN | NaN | NaN | NaN | 23.9317 | 529.9221 | NaN | 11.6263 | NaN | 21.9035
7679.1292 | 14.0955 | 13.8559 | 13.8277 | 14.1187 | 13.5945 | 13.8017 | 13.5306 | 13.3587 | NaN | NaN | NaN | 13.5875 | 120.1206 | NaN | NaN | 23.3365 | -16.8371 | NaN | NaN | NaN | 41.5649 | 539.5333 | NaN | 8.8864 | NaN | 20.434
7680.1292 | 14.083 | 13.8394 | 13.8341 | 14.1491 | 13.6531 | 13.7956 | 13.54 | 13.3624 | NaN | NaN | NaN | 13.5891 | 131.5745 | NaN | NaN | 9.5512 | -17.0351 | NaN | NaN | NaN | 41.2918 | 541.6039 | NaN | 12.1182 | NaN | 14.109
7681.1292 | 14.0955 | 13.8404 | 13.8329 | 14.1313 | 13.662 | 13.7902 | 13.5253 | 13.3608 | NaN | NaN | NaN | 13.5952 | 135.5913 | NaN | NaN | 73.6073 | NaN | NaN | NaN | NaN | 29.8164 | 538.3908 | NaN | 7.8455 | NaN | 17.2714
7682.1292 | 14.0871 | 13.8809 | 13.8305 | 14.1568 | 13.6438 | 13.8052 | 13.5284 | 13.3589 | NaN | NaN | NaN | 13.5939 | 129.526 | NaN | NaN | -14.7091 | NaN | NaN | NaN | NaN | 38.3251 | 536.2908 | NaN | 14.9378 | NaN | 11.0832
7683.1292 | 14.095 | 13.8399 | 13.8341 | 14.1201 | 13.5909 | 13.798 | 13.5296 | 13.3565 | NaN | NaN | NaN | 13.5937 | 124.2773 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 44.468 | 530.3419 | NaN | 11.368 | NaN | 13.516
7684.1292 | 14.1637 | 13.829 | 13.8334 | 14.1259 | 13.6408 | 13.795 | 13.5282 | 13.363 | NaN | NaN | NaN | 13.6011 | 124.944 | NaN | NaN | 64.2283 | NaN | NaN | NaN | NaN | 33.0726 | 520.3788 | NaN | 21.0987 | NaN | 17.276
7685.1292 | 14.0979 | 13.8431 | 13.8299 | 14.1398 | 13.6113 | 13.7927 | 13.5287 | 13.3655 | NaN | NaN | NaN | 13.605 | 128.4123 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 29.4716 | 510.541 | NaN | 16.568 | NaN | 18.7895
7686.1292 | 14.1033 | 13.8382 | 13.8307 | 14.1201 | 13.6368 | 13.7968 | 13.5426 | 13.3658 | NaN | NaN | NaN | 13.6139 | 131.6253 | NaN | NaN | 28.2607 | -15.6261 | NaN | NaN | NaN | 40.7968 | 511.2177 | NaN | 11.1107 | NaN | 27.8384
7687.1292 | 14.1046 | 13.841 | 13.8464 | 14.0981 | 13.6272 | 13.7819 | 13.5323 | 13.3691 | NaN | NaN | NaN | 13.6208 | 131.5634 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 27.6908 | 513.3964 | NaN | 6.8984 | NaN | 17.4838
7688.1292 | 14.2279 | 13.8536 | 13.8361 | 14.1262 | 13.6535 | 13.7967 | 13.5369 | 13.3681 | NaN | NaN | NaN | 13.5962 | 128.4918 | NaN | NaN | -12.5465 | NaN | NaN | NaN | NaN | 47.9311 | 516.8094 | NaN | 9.1348 | NaN | 20.5069
7689.1292 | 14.1014 | 13.8397 | 13.8439 | 14.1501 | 13.5684 | 13.7868 | 13.5329 | 13.3706 | NaN | NaN | NaN | 13.6149 | 135.9308 | NaN | NaN | 52.207 | NaN | NaN | NaN | NaN | 37.2928 | 521.5479 | NaN | 8.4316 | NaN | 21.6182
7690.1292 | 14.117 | 13.8586 | 13.8402 | 14.1219 | 13.6175 | 13.7927 | 13.53 | 13.3688 | NaN | NaN | NaN | 13.6344 | 131.5898 | NaN | NaN | 53.0573 | NaN | NaN | NaN | NaN | 13.192 | 529.5841 | NaN | 23.1695 | NaN | 19.5941
7691.1292 | 14.1122 | 13.8929 | 13.838 | 14.1345 | 13.652 | 13.8031 | 13.5428 | 13.3705 | NaN | NaN | NaN | 13.611 | 132.2403 | NaN | NaN | 35.7631 | NaN | NaN | NaN | NaN | 40.9607 | 525.5735 | NaN | 20.0332 | NaN | 16.5754
7692.1292 | 14.1176 | 13.8399 | 13.8467 | 14.1089 | 13.6161 | 13.7913 | 13.5357 | 13.3708 | NaN | NaN | NaN | 13.6094 | 127.9235 | NaN | NaN | 24.8097 | -14.6107 | NaN | NaN | NaN | 51.9002 | 532.7129 | NaN | 18.7662 | NaN | 18.7221
7693.1292 | 14.1014 | 13.8385 | 13.8344 | 14.1402 | 13.5532 | 13.7876 | 13.5349 | 13.3683 | NaN | NaN | NaN | 13.6009 | 118.4679 | NaN | NaN | 35.0402 | NaN | NaN | NaN | NaN | 38.1577 | 537.7734 | NaN | 33.866 | NaN | 25.006
7694.1292 | 14.109 | 13.8377 | 13.8359 | 14.1286 | 13.6495 | 13.793 | 13.5398 | 13.3653 | NaN | NaN | NaN | 13.601 | 125.2473 | NaN | NaN | 18.8222 | NaN | NaN | NaN | NaN | 33.8873 | 544.593 | NaN | 5.2803 | NaN | 26.9723
7695.1292 | 14.1278 | 13.8474 | 13.8264 | 14.1165 | 13.6432 | 13.7846 | 13.5302 | 13.3724 | NaN | NaN | NaN | 13.5953 | 130.3146 | NaN | NaN | 15.4743 | NaN | NaN | NaN | NaN | 39.9595 | 541.9237 | NaN | 11.1035 | NaN | 20.1576
7696.1292 | 14.1103 | 13.8831 | 13.8235 | 14.1381 | 13.6303 | 13.8062 | 13.5342 | 13.3676 | NaN | NaN | NaN | 13.5964 | 136.8985 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 42.8221 | 539.4093 | NaN | 21.4403 | NaN | 14.8993
7697.1292 | 14.1241 | 13.8516 | 13.8246 | 14.1061 | 13.5893 | 13.794 | 13.5246 | 13.3616 | NaN | NaN | NaN | 13.5892 | 129.5538 | NaN | NaN | 41.3161 | NaN | NaN | NaN | NaN | 35.5045 | 535.3831 | NaN | 12.7378 | NaN | 24.6552
7698.1292 | 14.1114 | 13.8702 | 13.8264 | 14.1423 | 13.6633 | 13.788 | 13.5272 | 13.3608 | NaN | NaN | NaN | 13.6221 | 132.0184 | NaN | NaN | 26.7827 | -16.5369 | NaN | NaN | NaN | 42.9194 | 537.0866 | NaN | 16.0259 | NaN | 25.7795
7699.1292 | 14.1184 | 13.9003 | 13.8225 | 14.1266 | 13.6498 | 13.7938 | 13.528 | 13.3642 | NaN | NaN | NaN | 13.6059 | 128.5826 | NaN | NaN | 44.5569 | NaN | NaN | NaN | NaN | 51.4268 | 534.5818 | NaN | 10.7075 | NaN | 19.5907
7700.1292 | 14.1081 | 13.8497 | 13.8268 | 14.1728 | 13.6641 | 13.7907 | 13.5313 | 13.3626 | NaN | NaN | NaN | 13.6267 | 129.9835 | NaN | NaN | 48.5079 | NaN | NaN | NaN | NaN | 48.9338 | 532.9868 | NaN | 25.0937 | NaN | 25.446
7701.1292 | 14.1123 | 13.8565 | 13.8192 | 14.1236 | 13.601 | 13.785 | 13.5247 | 13.3667 | NaN | NaN | NaN | 13.6449 | 121.0407 | NaN | NaN | 12.5766 | NaN | NaN | NaN | NaN | 29.0098 | 534.977 | NaN | 11.264 | NaN | 27.8077
7702.1292 | 14.0962 | 13.8816 | 13.816 | 14.1559 | 13.6696 | 13.7973 | 13.5363 | 13.3708 | NaN | NaN | NaN | 13.6145 | 121.7829 | NaN | NaN | 2.1106 | NaN | NaN | NaN | NaN | 7.3316 | 525.6075 | NaN | 1.7398 | NaN | 24.0932
7703.1292 | 14.116 | 13.8464 | 13.8158 | 14.1264 | 13.625 | 13.7867 | 13.5313 | 13.3635 | NaN | NaN | NaN | 13.6245 | 124.0004 | NaN | NaN | 45.7031 | NaN | NaN | NaN | NaN | 22.7712 | 516.9521 | NaN | 3.3977 | NaN | 21.1005
7704.1292 | 14.1045 | 13.8414 | 13.811 | 14.1371 | 13.6651 | 13.8002 | 13.5408 | 13.364 | NaN | NaN | NaN | 13.6188 | 124.5794 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 21.1434 | 519.9212 | NaN | 7.775 | NaN | 15.8246
7705.1292 | 14.1027 | 13.8493 | 13.8128 | 14.104 | 13.6604 | 13.7984 | 13.5349 | 13.3619 | NaN | NaN | NaN | 13.6026 | 128.8697 | NaN | NaN | -13.8604 | -18.7365 | NaN | NaN | NaN | 17.7282 | 523.6016 | NaN | 6.5037 | NaN | 17.433
7706.1292 | 14.0963 | 13.8634 | 13.817 | 14.1233 | 13.6775 | 13.8041 | 13.5297 | 13.3595 | NaN | NaN | NaN | 13.6241 | 136.8974 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 41.8611 | 515.4445 | NaN | 24.0057 | NaN | 26.415
7707.1292 | 14.1103 | 13.848 | 13.817 | 14.1313 | 13.6233 | 13.7952 | 13.5286 | 13.3608 | NaN | NaN | NaN | 13.6426 | 119.0966 | NaN | NaN | 3.2379 | NaN | NaN | NaN | NaN | 36.6625 | 509.7251 | NaN | 11.1808 | NaN | 16.6745
7708.1292 | 14.1712 | 13.8649 | 13.8073 | 14.1248 | 13.674 | 13.8068 | 13.5326 | 13.3581 | NaN | NaN | NaN | 13.6277 | 133.4406 | NaN | NaN | 44.4438 | NaN | NaN | NaN | NaN | 45.9039 | 502.8576 | NaN | 34.9349 | NaN | 27.1824
7709.1292 | 14.1015 | 13.8765 | 13.8158 | 14.114 | 13.6501 | 13.8143 | 13.5392 | 13.3542 | NaN | NaN | NaN | 13.6188 | 130.4166 | NaN | NaN | 72.6068 | NaN | NaN | NaN | NaN | 24.3341 | 504.4787 | NaN | 11.0531 | NaN | 26.9727
7710.1292 | 14.1122 | 13.8564 | 13.8146 | 14.1154 | 13.6701 | 13.7995 | 13.5239 | 13.3551 | NaN | NaN | NaN | 13.6414 | 132.9264 | NaN | NaN | -12.4554 | NaN | NaN | NaN | NaN | 23.0245 | 492.1304 | NaN | 17.0559 | NaN | 17.3894
7711.1292 | 14.1298 | 13.8435 | 13.812 | 14.1659 | 13.6679 | 13.8153 | 13.5248 | 13.3497 | NaN | NaN | NaN | 13.6298 | 131.8751 | NaN | NaN | 13.7496 | NaN | NaN | NaN | NaN | 28.0162 | 486.2169 | NaN | 16.857 | NaN | 8.8902
7712.1292 | 14.1055 | 13.8668 | 13.8174 | 14.1032 | 13.6438 | 13.8238 | 13.5203 | 13.3563 | NaN | NaN | NaN | 13.6132 | 127.4555 | NaN | NaN | 6.712 | -16.1395 | NaN | NaN | NaN | 10.9595 | 473.271 | NaN | 17.288 | NaN | 20.9679
7713.1292 | 14.16 | 13.8325 | 13.8131 | 14.1284 | 13.6252 | 13.8133 | 13.515 | 13.352 | NaN | NaN | NaN | 13.6292 | 131.5015 | NaN | NaN | -9.8352 | NaN | NaN | NaN | NaN | 25.0252 | 459.3419 | NaN | 19.0006 | NaN | 15.1731
7714.1292 | 14.1111 | 13.8565 | 13.8161 | 14.111 | 13.6635 | 13.818 | 13.5211 | 13.3552 | NaN | NaN | NaN | 13.6408 | 130.5834 | NaN | NaN | 54.202 | NaN | NaN | NaN | NaN | 14.7273 | 455.2446 | NaN | 5.516 | NaN | 22.5136
7715.1292 | 14.1098 | 13.8619 | 13.8194 | 14.108 | 13.6496 | 13.8067 | 13.5065 | 13.3542 | NaN | NaN | NaN | 13.636 | 124.6296 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 23.7053 | 445.9147 | NaN | 26.4609 | NaN | 21.7396
7716.1292 | 14.1585 | 13.8662 | 13.8187 | 14.1181 | 13.5993 | 13.8184 | 13.5211 | 13.36 | NaN | NaN | NaN | 13.6518 | 129.8876 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 25.8405 | 443.4259 | NaN | 10.795 | NaN | 16.1181
7717.1292 | 14.1085 | 13.8437 | 13.8204 | 14.1177 | 13.6626 | 13.8125 | 13.5205 | 13.3593 | NaN | NaN | NaN | 13.6523 | 130.8337 | NaN | NaN | 62.9341 | NaN | NaN | NaN | NaN | 43.0786 | 437.8275 | NaN | 22.456 | NaN | 21.4689
7718.1292 | 14.1131 | 13.9352 | 13.8245 | 14.1356 | 13.6416 | 13.8099 | 13.5205 | 13.3574 | NaN | NaN | NaN | 13.6638 | 139.3868 | NaN | NaN | 57.8121 | NaN | NaN | NaN | NaN | 27.2869 | 434.8401 | NaN | 10.9875 | NaN | 21.3651
7719.1292 | 14.1084 | 13.8321 | 13.8132 | 14.1221 | 13.6816 | 13.7996 | 13.5153 | 13.3557 | NaN | NaN | NaN | 13.6725 | 129.0177 | NaN | NaN | NaN | -19.9174 | NaN | NaN | NaN | 36.9829 | 437.236 | NaN | 23.3633 | NaN | 23.8663
7720.1292 | 14.1121 | 13.8451 | 13.8195 | 14.136 | 13.6831 | 13.7982 | 13.5152 | 13.3548 | NaN | NaN | NaN | 13.6788 | 136.6694 | NaN | NaN | 26.7723 | -1.1549 | NaN | NaN | NaN | 17.1611 | 433.8997 | NaN | 0.3721 | NaN | 23.0696
7721.1292 | 14.1033 | 13.852 | 13.8209 | 14.1189 | 13.6366 | 13.7985 | 13.5112 | 13.3546 | NaN | NaN | NaN | 13.6564 | 136.5799 | NaN | NaN | 7.4989 | NaN | NaN | NaN | NaN | 30.3511 | 434.0648 | NaN | 11.8024 | NaN | 30.2635
7722.1292 | 14.1123 | 13.8298 | 13.8264 | 14.1667 | 13.6685 | 13.7987 | 13.5185 | 13.3562 | NaN | NaN | NaN | 13.6752 | 132.4552 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 38.9611 | 433.9795 | NaN | 4.0974 | NaN | 25.2173
7723.1292 | 14.0991 | 13.9155 | 13.8234 | 14.1159 | 13.6353 | 13.8155 | 13.5246 | 13.358 | NaN | NaN | NaN | 13.6965 | 130.5938 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 17.372 | 436.2433 | NaN | 8.078 | NaN | 28.1791
7724.1292 | 14.1091 | 13.8266 | 13.8255 | 14.2355 | 13.6701 | 13.7959 | 13.5151 | 13.3599 | NaN | NaN | NaN | 13.6536 | 129.6631 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 43.3671 | 438.5546 | NaN | 19.9183 | NaN | 15.9538
7725.1292 | 14.1033 | 13.8765 | 13.8257 | 14.1265 | 13.6612 | 13.8068 | 13.5266 | 13.3548 | NaN | NaN | NaN | 13.668 | 134.9385 | NaN | NaN | -2.123 | NaN | NaN | NaN | NaN | 42.6564 | 441.0876 | NaN | 18.2966 | NaN | 23.6529
7726.1292 | 14.1071 | 13.8258 | 13.8274 | 14.1577 | 13.6638 | 13.7942 | 13.5167 | 13.3534 | NaN | NaN | NaN | 13.6678 | 125.9354 | NaN | NaN | NaN | -16.7742 | NaN | NaN | NaN | 43.8677 | 439.3664 | NaN | 5.0525 | NaN | 15.7669
7727.1292 | 14.1071 | 13.8323 | 13.8269 | 14.1211 | 13.6448 | 13.7952 | 13.5153 | 13.3548 | NaN | NaN | NaN | 13.6607 | 129.9121 | NaN | NaN | 19.5971 | NaN | NaN | NaN | NaN | 22.3294 | 437.701 | NaN | 6.9029 | NaN | 25.7004
7728.1292 | 14.11 | 13.8316 | 13.8308 | 14.1504 | 13.6803 | 13.7907 | 13.5093 | 13.3466 | NaN | NaN | NaN | 13.6591 | 130.4051 | NaN | NaN | 45.8889 | NaN | NaN | NaN | NaN | 36.239 | 433.916 | NaN | 14.7215 | NaN | 19.6775
7729.1292 | 14.1028 | 13.8739 | 13.8388 | 14.1296 | 13.6731 | 13.7973 | 13.5109 | 13.3531 | NaN | NaN | NaN | 13.6771 | 128.6997 | NaN | NaN | 65.2868 | NaN | NaN | NaN | NaN | 25.4492 | 431.1842 | NaN | 12.5573 | NaN | 21.3597
7730.1292 | 14.1084 | 13.8238 | 13.8332 | 14.1683 | 13.6649 | 13.7927 | 13.5192 | 13.3476 | NaN | NaN | NaN | 13.6935 | 129.9239 | NaN | NaN | -4.7494 | NaN | NaN | NaN | NaN | 27.8062 | 429.0781 | NaN | 8.4095 | NaN | 26.1487
7731.1292 | 14.0901 | 13.8381 | 13.8335 | 14.135 | 13.6339 | 13.7919 | 13.5163 | 13.3585 | NaN | NaN | NaN | 13.6758 | 131.4464 | NaN | NaN | 63.2067 | NaN | NaN | NaN | NaN | 33.4545 | 428.3949 | NaN | 19.3128 | NaN | 19.6329
7732.1292 | 14.107 | 13.8324 | 13.8352 | 14.1603 | 13.6902 | 13.7956 | 13.5204 | 13.3595 | NaN | NaN | NaN | 13.6628 | 131.9869 | NaN | NaN | NaN | -17.4427 | NaN | NaN | NaN | 22.8494 | 427.3654 | NaN | 18.4568 | NaN | 13.9545
7733.1292 | 14.079 | 13.8332 | 13.8381 | 14.136 | 13.6686 | 13.7842 | 13.5081 | 13.3541 | NaN | NaN | NaN | 13.6764 | 122.0943 | NaN | NaN | -14.7016 | NaN | NaN | NaN | NaN | 26.6033 | 425.9017 | NaN | 32.3064 | NaN | 13.0429
7734.1292 | 14.1063 | 13.8295 | 13.8287 | 14.2084 | 13.6721 | 13.785 | 13.5092 | 13.3557 | NaN | NaN | NaN | 13.6649 | 132.2399 | NaN | NaN | 91.3238 | NaN | NaN | NaN | NaN | 27.3146 | 428.3587 | NaN | 15.5239 | NaN | 10.9282
7735.1292 | 14.1064 | 13.902 | 13.8283 | 14.1308 | 13.6659 | 13.8028 | 13.5235 | 13.3507 | NaN | NaN | NaN | 13.6721 | 134.5723 | NaN | NaN | 5.3361 | NaN | NaN | NaN | NaN | 46.847 | 423.1701 | NaN | 12.1607 | NaN | 14.2143
7736.1292 | 14.1043 | 13.8389 | 13.8267 | 14.1613 | 13.6827 | 13.7871 | 13.5207 | 13.3596 | NaN | NaN | NaN | 13.6595 | 130.9601 | NaN | NaN | 62.0318 | NaN | NaN | NaN | NaN | 54.8431 | 421.4911 | NaN | 6.053 | NaN | 22.7759
7737.1292 | 14.1095 | 13.8332 | 13.8219 | 14.1387 | 13.6586 | 13.7859 | 13.5119 | 13.3639 | NaN | NaN | NaN | 13.6741 | 142.1229 | NaN | NaN | 16.5612 | NaN | NaN | NaN | NaN | 38.0823 | 429.5553 | NaN | 23.3566 | NaN | 12.4152
7738.1292 | 14.0976 | 13.8344 | 13.8205 | 14.1661 | 13.6574 | 13.7911 | 13.5083 | 13.3601 | NaN | NaN | NaN | 13.6602 | 123.0166 | NaN | NaN | 48.7289 | -16.8575 | NaN | NaN | NaN | 44.5269 | 438.2037 | NaN | 13.8439 | NaN | 22.6498
7739.1292 | 14.0966 | 13.8263 | 13.8226 | 14.1387 | 13.639 | 13.7876 | 13.5153 | 13.3618 | NaN | NaN | NaN | 13.7003 | 116.0631 | NaN | NaN | 27.748 | -15.5316 | NaN | NaN | NaN | 38.5878 | 434.3313 | NaN | 12.018 | NaN | 18.0541
7740.1292 | 14.1008 | 13.8579 | 13.8244 | 14.1459 | 13.6263 | 13.7903 | 13.512 | 13.3616 | NaN | NaN | NaN | 13.6584 | 132.4392 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 38.5879 | 429.7424 | NaN | 3.3872 | NaN | 28.2611
7741.1292 | 14.0952 | 13.8342 | 13.825 | 14.138 | 13.6696 | 13.7823 | 13.515 | 13.3644 | NaN | NaN | NaN | 13.6571 | 133.403 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 18.4563 | 427.4226 | NaN | 11.9765 | NaN | 12.9566
7742.1292 | 14.0924 | 13.9372 | 13.8306 | 14.1502 | 13.6823 | 13.7931 | 13.538 | 13.3638 | NaN | NaN | NaN | 13.6579 | 135.9503 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 46.5686 | 415.3662 | NaN | 10.6303 | NaN | 33.8476
7743.1292 | 14.0754 | 13.964 | 13.8353 | 14.1263 | 13.6037 | 13.8185 | 13.5429 | 13.3696 | NaN | NaN | NaN | 13.6388 | 130.4046 | NaN | NaN | 32.03 | NaN | NaN | NaN | NaN | 43.7519 | 404.364 | NaN | 5.2267 | NaN | 12.5389
7744.1292 | 14.0857 | 13.8323 | 13.836 | 14.1463 | 13.6388 | 13.7864 | 13.5193 | 13.3661 | NaN | NaN | NaN | 13.6693 | 129.7086 | NaN | NaN | 19.3275 | -19.7321 | NaN | NaN | NaN | 39.142 | 388.599 | NaN | 11.2209 | NaN | 18.7442
7745.1292 | 14.0843 | 13.8571 | 13.8339 | 14.1585 | 13.6212 | 13.7993 | 13.5222 | 13.3697 | NaN | NaN | NaN | 13.6736 | 141.8841 | NaN | NaN | 42.7595 | -17.3435 | NaN | NaN | NaN | 38.7239 | 382.6412 | NaN | 8.5294 | NaN | 14.0838
7746.1292 | 14.0867 | 13.8409 | 13.8301 | 14.1368 | 13.6188 | 13.7752 | 13.5225 | 13.3649 | NaN | NaN | NaN | 13.6851 | 137.9402 | NaN | NaN | 41.3329 | NaN | NaN | NaN | NaN | 35.7368 | 373.3355 | NaN | 10.5283 | NaN | 26.1708
7747.1292 | 14.0741 | 13.8345 | 13.8294 | 14.1336 | 13.6654 | 13.7767 | 13.5142 | 13.3657 | NaN | NaN | NaN | 13.6382 | 135.9406 | NaN | NaN | 37.5822 | NaN | NaN | NaN | NaN | 30.5826 | 365.9169 | NaN | 32.074 | NaN | 22.4858
7748.1292 | 14.0825 | 13.8245 | 13.8363 | 14.1481 | 13.6647 | 13.7793 | 13.5178 | 13.3647 | NaN | NaN | NaN | 13.682 | 128.877 | NaN | NaN | 75.5571 | NaN | NaN | NaN | NaN | 38.105 | 349.5699 | NaN | 6.2163 | NaN | 29.4466
7749.1292 | 14.1236 | 13.8528 | 13.8327 | 14.1454 | 13.6069 | 13.7924 | 13.5246 | 13.3644 | NaN | NaN | NaN | 13.6541 | 128.9698 | NaN | NaN | 38.7728 | NaN | NaN | NaN | NaN | 29.8934 | 348.8953 | NaN | 18.9427 | NaN | 23.2587
7750.1292 | 14.081 | 13.8388 | 13.8301 | 14.195 | 13.6513 | 13.7848 | 13.5168 | 13.3714 | NaN | NaN | NaN | 13.6605 | 132.7473 | NaN | NaN | 44.0401 | NaN | NaN | NaN | NaN | 36.5343 | 329.7343 | NaN | 7.7191 | NaN | 11.8777
7751.1292 | 14.0831 | 13.8393 | 13.8294 | 14.1369 | 13.6625 | 13.7898 | 13.5208 | 13.3712 | NaN | NaN | NaN | 13.6641 | 133.3904 | NaN | NaN | 27.0798 | -18.3076 | NaN | NaN | NaN | 27.605 | 314.5304 | NaN | 7.0637 | NaN | 18.7246
7752.1292 | 14.0708 | 13.8371 | 13.8301 | 14.18 | 13.6718 | 13.7948 | 13.5185 | 13.3735 | NaN | NaN | NaN | 13.6377 | 134.621 | NaN | NaN | 23.586 | NaN | NaN | NaN | NaN | 54.8144 | 303.0089 | NaN | 11.9821 | NaN | 13.5778
7753.1292 | 14.0904 | 13.8703 | 13.8314 | 14.1479 | 13.5922 | 13.8113 | 13.5223 | 13.3681 | NaN | NaN | NaN | 13.6375 | 129.9543 | NaN | NaN | 27.7722 | NaN | NaN | NaN | NaN | 47.4261 | 287.4888 | NaN | 5.5552 | NaN | 14.1382
7754.1292 | 14.0872 | 13.8326 | 13.8294 | 14.1309 | 13.6296 | 13.8072 | 13.528 | 13.363 | NaN | NaN | NaN | 13.6391 | 122.7549 | NaN | NaN | 56.6513 | NaN | NaN | NaN | NaN | 28.7827 | 282.9962 | NaN | 8.7296 | NaN | 24.6503
7755.1292 | 14.0844 | 13.8503 | 13.8257 | 14.1629 | 13.6559 | 13.808 | 13.5176 | 13.3643 | NaN | NaN | NaN | 13.6518 | 132.5888 | NaN | NaN | -15.0476 | NaN | NaN | NaN | NaN | 31.8316 | 272.7775 | NaN | 19.9927 | NaN | 16.5559
7756.1292 | 14.0932 | 13.8706 | 13.8309 | 14.1405 | 13.6106 | 13.8061 | 13.5231 | 13.3584 | NaN | NaN | NaN | 13.6482 | 120.8989 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 40.5445 | 270.2947 | NaN | 5.7855 | NaN | 22.0483
7757.1292 | 14.0855 | 13.8245 | 13.8301 | 14.1269 | 13.6077 | 13.8043 | 13.5199 | 13.3626 | NaN | NaN | NaN | 13.6975 | 136.67 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 34.8413 | 265.4699 | NaN | 3.927 | NaN | 25.8105
7758.1292 | 14.1098 | 13.8273 | 13.8327 | 14.1378 | 13.6424 | 13.8028 | 13.5162 | 13.3608 | NaN | NaN | NaN | 13.6541 | 114.4704 | NaN | NaN | 40.8633 | -16.8972 | NaN | NaN | NaN | 34.5013 | 255.8997 | NaN | 11.7992 | NaN | 18.4585
7759.1292 | 14.0882 | 13.8457 | 13.8263 | 14.119 | 13.6697 | 13.7979 | 13.5187 | 13.3624 | NaN | NaN | NaN | 13.653 | 116.6867 | NaN | NaN | 23.7589 | NaN | NaN | NaN | NaN | 37.8927 | 250.9915 | NaN | 19.6872 | NaN | 21.1091
7760.1292 | 14.0869 | 13.8214 | 13.836 | 14.1099 | 13.5845 | 13.8086 | 13.5263 | 13.3623 | NaN | NaN | NaN | 13.6403 | 122.8867 | NaN | NaN | 25.7285 | NaN | NaN | NaN | NaN | 34.6193 | 248.9912 | NaN | 13.3849 | NaN | 16.2734
7761.1292 | 14.0658 | 13.8252 | 13.8342 | 14.1398 | 13.6489 | 13.8063 | 13.5263 | 13.365 | NaN | NaN | NaN | 13.6511 | 133.0107 | NaN | NaN | 40.8508 | NaN | NaN | NaN | NaN | 38.3363 | 258.7785 | NaN | 13.8576 | NaN | 26.9072
7762.1292 | 14.0844 | 13.8331 | 13.8368 | 14.1641 | 13.6783 | 13.7913 | 13.5156 | 13.3674 | NaN | NaN | NaN | 13.6561 | 138.0112 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 35.1945 | 263.9364 | NaN | 13.907 | NaN | 31.1449
7763.1292 | 14.1401 | 13.8223 | 13.8411 | 14.1247 | 13.6525 | 13.8101 | 13.5239 | 13.3712 | NaN | NaN | NaN | 13.6393 | 127.5287 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 31.3284 | 261.7579 | NaN | 33.2928 | NaN | 19.4958
7764.1292 | 14.0909 | 13.8518 | 13.8367 | 14.1413 | 13.6569 | 13.8162 | 13.5358 | 13.3663 | NaN | NaN | NaN | 13.6612 | 140.3425 | NaN | NaN | 4.5206 | NaN | NaN | NaN | NaN | 40.4056 | 265.0092 | NaN | 7.8366 | NaN | 21.8136
7765.1292 | 14.0799 | 13.825 | 13.8276 | 14.1443 | 13.6833 | 13.803 | 13.5162 | 13.3736 | NaN | NaN | NaN | 13.6602 | 137.9146 | NaN | NaN | -13.143 | 0.348 | NaN | NaN | NaN | 49.1865 | 267.1749 | NaN | 2.7498 | NaN | 13.8542
7766.1292 | 14.0858 | 13.836 | 13.8344 | 14.1055 | 13.5879 | 13.8134 | 13.5199 | 13.3695 | NaN | NaN | NaN | 13.6568 | 131.6692 | NaN | NaN | -3.6288 | NaN | NaN | NaN | NaN | 33.2613 | 266.754 | NaN | 16.7467 | NaN | 14.791
7767.1292 | 14.0727 | 13.8662 | 13.8254 | 14.1276 | 13.6475 | 13.8242 | 13.527 | 13.3685 | NaN | NaN | NaN | 13.6491 | 134.4 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 27.4588 | 270.5851 | NaN | 3.6704 | NaN | 23.9105
7768.1292 | 14.0876 | 13.8196 | 13.8298 | 14.1449 | 13.6541 | 13.8066 | 13.5217 | 13.3749 | NaN | NaN | NaN | 13.6581 | 134.0237 | NaN | NaN | -14.4885 | NaN | NaN | NaN | NaN | 41.3146 | 272.8523 | NaN | 10.4662 | NaN | 12.1012
7769.1292 | 14.0741 | 13.8095 | 13.8252 | 14.1298 | 13.6692 | 13.8046 | 13.519 | 13.3784 | NaN | NaN | NaN | 13.6439 | 128.9352 | NaN | NaN | 4.163 | NaN | NaN | NaN | NaN | 48.8822 | 267.357 | NaN | 7.905 | NaN | 18.1866
7770.1292 | 14.0812 | 13.8115 | 13.8143 | 14.1213 | 13.6627 | 13.8031 | 13.5072 | 13.3682 | NaN | NaN | NaN | 13.6569 | 132.4774 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 24.6146 | 268.1505 | NaN | 2.6166 | NaN | 13.8831
7771.1292 | 14.1695 | 13.8123 | 13.8084 | 14.1283 | 13.6702 | 13.8075 | 13.5151 | 13.3685 | NaN | NaN | NaN | 13.6611 | 130.0925 | NaN | NaN | 11.5716 | NaN | NaN | NaN | NaN | 35.67 | 274.8755 | NaN | 11.7873 | NaN | 27.9561
7772.1292 | 14.0778 | 13.8153 | 13.8119 | 14.1148 | 13.6591 | 13.8042 | 13.5138 | 13.3646 | NaN | NaN | NaN | 13.6385 | 133.9125 | NaN | NaN | NaN | -19.1588 | NaN | NaN | NaN | 39.62 | 281.3655 | NaN | 14.6562 | NaN | 26.88
7773.1292 | 14.0869 | 13.8333 | 13.8136 | 14.1433 | 13.5833 | 13.8203 | 13.5139 | 13.3613 | NaN | NaN | NaN | 13.6553 | 136.7487 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 42.0084 | 286.0347 | NaN | 6.5749 | NaN | 28.7987
7774.1292 | 14.0792 | 13.8262 | 13.8088 | 14.1212 | 13.6764 | 13.8133 | 13.5145 | 13.3655 | NaN | NaN | NaN | 13.6511 | 131.1851 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 52.8367 | 284.5073 | NaN | 17.0993 | NaN | 9.0596
7775.1292 | 14.0813 | 13.8167 | 13.8166 | 14.1481 | 13.6139 | 13.807 | 13.5199 | 13.3669 | NaN | NaN | NaN | 13.6568 | 127.1273 | NaN | NaN | -6.8118 | NaN | NaN | NaN | NaN | 35.256 | 297.5344 | NaN | 0.7897 | NaN | 18.1652
7776.1292 | 14.0776 | 13.8282 | 13.8122 | 14.1068 | 13.6524 | 13.8086 | 13.5112 | 13.3661 | NaN | NaN | NaN | 13.6569 | 111.307 | NaN | NaN | 37.7243 | NaN | NaN | NaN | NaN | 21.4674 | 309.7714 | NaN | 5.5139 | NaN | 15.5584
7777.1292 | 14.0803 | 13.8154 | 13.8029 | 14.1237 | 13.6744 | 13.8136 | 13.512 | 13.3599 | NaN | NaN | NaN | 13.6415 | 131.084 | NaN | NaN | 41.6074 | NaN | NaN | NaN | NaN | 37.7688 | 317.5368 | NaN | 8.8685 | NaN | 21.7626
7778.1292 | 14.0699 | 13.8232 | 13.8112 | 14.1034 | 13.6462 | 13.8104 | 13.5202 | 13.357 | NaN | NaN | NaN | 13.65 | 130.418 | NaN | NaN | 27.2749 | -17.6555 | NaN | NaN | NaN | 35.4724 | 321.3258 | NaN | 13.3324 | NaN | 29.0364
7779.1292 | 14.0762 | 13.8752 | 13.8122 | 14.1435 | 13.6665 | 13.8253 | 13.5246 | 13.3587 | NaN | NaN | NaN | 13.6429 | 129.9373 | NaN | NaN | 28.4065 | -14.8522 | NaN | NaN | NaN | 11.4312 | 318.2812 | NaN | 8.988 | NaN | 21.9757
7780.1292 | 14.0733 | 13.8318 | 13.8088 | 14.1153 | 13.6648 | 13.8159 | 13.52 | 13.3532 | NaN | NaN | NaN | 13.6502 | 122.085 | NaN | NaN | 11.0094 | NaN | NaN | NaN | NaN | 34.608 | 319.5855 | NaN | 10.205 | NaN | 23.9187
7781.1292 | 14.0765 | 13.8257 | 13.8158 | 14.0973 | 13.6375 | 13.8139 | 13.5137 | 13.3578 | NaN | NaN | NaN | 13.6501 | 122.5698 | NaN | NaN | 40.3221 | NaN | NaN | NaN | NaN | 22.8777 | 320.93 | NaN | 11.8265 | NaN | 21.1852
7782.1292 | 14.0663 | 13.8245 | 13.8115 | 14.1378 | 13.6659 | 13.8142 | 13.5142 | 13.3526 | NaN | NaN | NaN | 13.6384 | 124.8016 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.2066 | 316.811 | NaN | 14.7259 | NaN | 28.1853
7783.1292 | 14.0781 | 13.8513 | 13.8071 | 14.1022 | 13.6271 | 13.8286 | 13.5074 | 13.357 | NaN | NaN | NaN | 13.6402 | 130.6868 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 22.3043 | 316.8199 | NaN | 12.4214 | NaN | 11.8945
7784.1292 | 14.0698 | 13.8248 | 13.8147 | 14.1181 | 13.669 | 13.8134 | 13.5075 | 13.3493 | NaN | NaN | NaN | 13.6384 | 134.4935 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 22.5789 | 315.3453 | NaN | 6.9803 | NaN | 28.0899
7785.1292 | 14.0823 | 13.8275 | 13.8119 | 14.1065 | 13.6581 | 13.8257 | 13.5033 | 13.3508 | NaN | NaN | NaN | 13.6545 | 139.0396 | NaN | NaN | -0.2952 | 14.53 | NaN | NaN | NaN | 30.9863 | 318.1484 | NaN | 31.4297 | NaN | 20.3559
7786.1292 | 14.0695 | 13.8244 | 13.8105 | 14.1211 | 13.6641 | 13.8193 | 13.501 | 13.3506 | NaN | NaN | NaN | 13.6412 | 113.4637 | NaN | NaN | 21.2201 | NaN | NaN | NaN | NaN | 42.9398 | 316.7157 | NaN | 12.2856 | NaN | 13.5215
7787.1292 | 14.076 | 13.8361 | 13.8105 | 14.0939 | 13.6517 | 13.8363 | 13.5031 | 13.3463 | NaN | NaN | NaN | 13.6467 | 123.1359 | NaN | NaN | 48.7142 | NaN | NaN | NaN | NaN | 38.0025 | 325.5567 | NaN | 14.1562 | NaN | 23.1127
7788.1292 | 14.0577 | 13.8276 | 13.8025 | 14.1162 | 13.6652 | 13.828 | 13.497 | 13.3493 | NaN | NaN | NaN | 13.627 | 128.7942 | NaN | NaN | 35.175 | NaN | NaN | NaN | NaN | 45.3647 | 321.528 | NaN | 13.1704 | NaN | 23.303
7789.1292 | 14.0744 | 13.8372 | 13.8125 | 14.1152 | 13.6604 | 13.8383 | 13.502 | 13.3552 | NaN | NaN | NaN | 13.6375 | 135.0729 | NaN | NaN | -11.6454 | NaN | NaN | NaN | NaN | 30.3881 | 311.997 | NaN | 10.043 | NaN | 11.587
7790.1292 | 14.1649 | 13.835 | 13.8087 | 14.0928 | 13.6551 | 13.8325 | 13.4899 | 13.3581 | NaN | NaN | NaN | 13.6162 | 129.8306 | NaN | NaN | 22.4795 | NaN | NaN | NaN | NaN | 9.7186 | 304.7385 | NaN | 5.3235 | NaN | 22.2474
7791.1292 | 14.0876 | 13.831 | 13.8093 | 14.1236 | 13.5677 | 13.8293 | 13.4876 | 13.3591 | NaN | NaN | NaN | 13.644 | 134.0894 | NaN | NaN | NaN | -19.4088 | NaN | NaN | NaN | 23.0478 | 306.6702 | NaN | 17.341 | NaN | 15.7771
7792.1292 | 14.17 | 13.8248 | 13.8174 | 14.1122 | 13.65 | 13.8169 | 13.4835 | 13.3512 | NaN | NaN | NaN | 13.618 | 137.4583 | NaN | NaN | NaN | -4.5461 | NaN | NaN | NaN | 35.5065 | 303.442 | NaN | 19.678 | NaN | 19.348
7793.1292 | 14.0792 | 13.8227 | 13.8181 | 14.1313 | 13.6624 | 13.8317 | 13.4897 | 13.3491 | NaN | NaN | NaN | 13.6278 | 129.9091 | NaN | NaN | 45.8921 | NaN | NaN | NaN | NaN | 32.4786 | 300.7384 | NaN | 13.8093 | NaN | 18.5616
7794.1292 | 14.0912 | 13.8311 | 13.8139 | 14.1242 | 13.6723 | 13.8303 | 13.491 | 13.3473 | NaN | NaN | NaN | 13.6303 | 125.7016 | NaN | NaN | 64.7858 | NaN | NaN | NaN | NaN | 49.8161 | 301.2183 | NaN | 14.6272 | NaN | 30.8019
7795.1292 | 14.0882 | 13.836 | 13.8118 | 14.119 | 13.6525 | 13.8247 | 13.4858 | 13.3514 | NaN | NaN | NaN | 13.6296 | 130.0275 | NaN | NaN | 28.0989 | NaN | NaN | NaN | NaN | 44.7965 | 305.6963 | NaN | 12.1485 | NaN | 26.0854
7796.1292 | 14.1056 | 13.8304 | 13.8132 | 14.1271 | 13.6554 | 13.8308 | 13.4927 | 13.3549 | NaN | NaN | NaN | 13.6179 | 131.383 | NaN | NaN | 26.3316 | -19.0657 | NaN | NaN | NaN | 24.5478 | 309.7318 | NaN | 17.4382 | NaN | 20.2882
7797.1292 | 14.0833 | 13.8396 | 13.8131 | 14.0986 | 13.623 | 13.8216 | 13.4871 | 13.3574 | NaN | NaN | NaN | 13.6328 | 132.7238 | NaN | NaN | 65.5919 | -17.9847 | NaN | NaN | NaN | 36.0922 | 316.3571 | NaN | 5.2351 | NaN | 27.0485
7798.1292 | 14.0961 | 13.8624 | 13.8163 | 14.1193 | 13.6585 | 13.8289 | 13.4987 | 13.3612 | NaN | NaN | NaN | 13.6308 | 129.6755 | NaN | NaN | 8.7898 | NaN | NaN | NaN | NaN | 14.5011 | 321.0781 | NaN | 26.2599 | NaN | 18.4693
7799.1292 | 14.0827 | 13.8426 | 13.8261 | 14.1083 | 13.6721 | 13.8177 | 13.493 | 13.3547 | NaN | NaN | NaN | 13.6408 | 117.329 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 30.2062 | 324.73 | NaN | 19.2829 | NaN | 20.4391
7800.1292 | 14.0944 | 13.8708 | 13.8211 | 14.1188 | 13.6709 | 13.833 | 13.5023 | 13.3593 | NaN | NaN | NaN | 13.6244 | 121.5439 | NaN | NaN | 16.67 | NaN | NaN | NaN | NaN | 47.9257 | 325.2562 | NaN | 22.1507 | NaN | 27.9442
7801.1292 | 14.0821 | 13.8411 | 13.8172 | 14.1084 | 13.6148 | 13.8172 | 13.4874 | 13.3623 | NaN | NaN | NaN | 13.6166 | 130.499 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 43.5235 | 327.1719 | NaN | 2.3109 | NaN | 14.1786
7802.1292 | 14.0893 | 13.8313 | 13.8248 | 14.1509 | 13.6474 | 13.8284 | 13.4974 | 13.3625 | NaN | NaN | NaN | 13.6302 | 130.569 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 39.3782 | 331.8275 | NaN | 15.4293 | NaN | 24.7551
7803.1292 | 14.0845 | 13.8978 | 13.8252 | 14.1246 | 13.6746 | 13.8286 | 13.4985 | 13.3596 | NaN | NaN | NaN | 13.6385 | 141.0181 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 37.7386 | 336.5119 | NaN | -9.5104 | NaN | 23.4376
7804.1292 | 14.0924 | 13.8402 | 13.8251 | 14.1075 | 13.6553 | 13.8313 | 13.5032 | 13.3654 | NaN | NaN | NaN | 13.624 | 128.0815 | NaN | NaN | NaN | -14.7165 | NaN | NaN | NaN | 33.3087 | 341.2446 | NaN | 19.592 | NaN | 21.0111
7805.1292 | 14.1388 | 13.8462 | 13.8264 | 14.1219 | 13.5908 | 13.834 | 13.4963 | 13.3607 | NaN | NaN | NaN | 13.6532 | 129.8074 | NaN | NaN | -8.5643 | NaN | NaN | NaN | NaN | 12.0816 | 345.922 | NaN | 6.1429 | NaN | 13.6639
7806.1292 | 14.0887 | 13.9158 | 13.8237 | 14.0957 | 13.5784 | 13.8552 | 13.5073 | 13.3641 | NaN | NaN | NaN | 13.6029 | 123.9545 | NaN | NaN | 50.1414 | NaN | NaN | NaN | NaN | 33.2924 | 346.4574 | NaN | 12.6909 | NaN | 27.1642
7807.1292 | 14.1232 | 13.8464 | 13.8232 | 14.1307 | 13.6442 | 13.8122 | 13.492 | 13.3688 | NaN | NaN | NaN | 13.6281 | 127.5587 | NaN | NaN | 25.8794 | NaN | NaN | NaN | NaN | 35.3591 | 338.461 | NaN | 13.6349 | NaN | 17.7248
7808.1292 | 14.0849 | 13.835 | 13.8256 | 14.1212 | 13.5939 | 13.8221 | 13.4896 | 13.3729 | NaN | NaN | NaN | 13.6508 | 125.2869 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 28.6912 | 336.8774 | NaN | 15.3251 | NaN | 27.7305
7809.1292 | 14.0883 | 13.8446 | 13.8288 | 14.147 | 13.6455 | 13.8217 | 13.4893 | 13.3646 | NaN | NaN | NaN | 13.6185 | 123.9841 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 46.0855 | 348.647 | NaN | 11.5711 | NaN | 14.9438
7810.1292 | 14.0769 | 13.8469 | 13.8313 | 14.1631 | 13.6825 | 13.807 | 13.4819 | 13.3747 | NaN | NaN | NaN | 13.6319 | 131.7497 | NaN | NaN | 68.2938 | NaN | NaN | NaN | NaN | 29.8161 | 357.6334 | NaN | 3.6174 | NaN | 13.9117
7811.1292 | 14.086 | 13.8909 | 13.8253 | 14.1194 | 13.6613 | 13.8153 | 13.4917 | 13.3725 | NaN | NaN | NaN | 13.6309 | 127.3709 | NaN | NaN | 42.2733 | -18.3116 | NaN | NaN | NaN | 50.6993 | 369.0265 | NaN | 8.4902 | NaN | 10.2176
7812.1292 | 14.0824 | 13.8432 | 13.8284 | 14.1649 | 13.6846 | 13.8067 | 13.4864 | 13.3739 | NaN | NaN | NaN | 13.6419 | 133.1512 | NaN | NaN | 58.321 | NaN | NaN | NaN | NaN | 45.4455 | 370.6148 | NaN | 9.3298 | NaN | 29.9549
7813.1292 | 14.0853 | 13.9112 | 13.827 | 14.1213 | 13.6658 | 13.8132 | 13.4958 | 13.3699 | NaN | NaN | NaN | 13.6434 | 132.7394 | NaN | NaN | 36.1922 | NaN | NaN | NaN | NaN | 39.2923 | 374.3474 | NaN | 23.3777 | NaN | 24.14
7814.1292 | 14.1204 | 13.9235 | 13.829 | 14.1372 | 13.5665 | 13.8464 | 13.4911 | 13.3727 | NaN | NaN | NaN | 13.6292 | 131.5192 | NaN | NaN | 40.9844 | NaN | NaN | NaN | NaN | 33.3095 | 379.0874 | NaN | 5.7328 | NaN | 14.5304
7815.1292 | 14.0785 | 13.8496 | 13.8219 | 14.1313 | 13.671 | 13.8095 | 13.4857 | 13.3656 | NaN | NaN | NaN | 13.6285 | 125.8692 | NaN | NaN | 16.8822 | NaN | NaN | NaN | NaN | 25.0453 | 372.9778 | NaN | 9.0233 | NaN | 25.0142
7816.1292 | 14.0824 | 13.8836 | 13.8258 | 14.1028 | 13.6637 | 13.8168 | 13.4867 | 13.3769 | NaN | NaN | NaN | 13.6355 | 131.8825 | NaN | NaN | 85.5242 | NaN | NaN | NaN | NaN | 32.0228 | 376.4499 | NaN | 16.4021 | NaN | 26.5235
7817.1292 | 14.074 | 13.8475 | 13.8272 | 14.1313 | 13.6713 | 13.8112 | 13.4938 | 13.3813 | NaN | NaN | NaN | 13.6293 | 130.5171 | NaN | NaN | 56.2178 | NaN | NaN | NaN | NaN | 55.6546 | 385.6036 | NaN | 21.963 | NaN | 17.2129
7818.1292 | 14.0799 | 13.8539 | 13.8321 | 14.1134 | 13.6517 | 13.8057 | 13.4887 | 13.3806 | NaN | NaN | NaN | 13.634 | 118.3296 | NaN | NaN | 60.1305 | -18.4285 | NaN | NaN | NaN | 33.6138 | 385.7845 | NaN | 12.5444 | NaN | 22.9775
7819.1292 | 14.0746 | 13.8331 | 13.8261 | 14.1453 | 13.6612 | 13.8061 | 13.4866 | 13.3724 | NaN | NaN | NaN | 13.633 | 133.0138 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 37.0268 | 393.6189 | NaN | 31.7297 | NaN | 22.2325
7820.1292 | 14.0824 | 13.88 | 13.831 | 14.1287 | 13.5535 | 13.8186 | 13.4984 | 13.3759 | NaN | NaN | NaN | 13.6424 | 137.3894 | NaN | NaN | -9.9884 | NaN | NaN | NaN | NaN | 33.889 | 402.1731 | NaN | 8.8627 | NaN | 29.5109
7821.1292 | 14.0972 | 13.8478 | 13.8313 | 14.1578 | 13.5611 | 13.8012 | 13.4939 | 13.3785 | NaN | NaN | NaN | 13.6703 | 127.4975 | NaN | NaN | 28.0658 | NaN | NaN | NaN | NaN | 41.0597 | 405.0531 | NaN | 7.3158 | NaN | 29.9711
7822.1292 | 14.1515 | 13.8644 | 13.83 | 14.1141 | 13.5699 | 13.8212 | 13.5072 | 13.3832 | NaN | NaN | NaN | 13.6002 | 129.4297 | NaN | NaN | 36.8188 | NaN | NaN | NaN | NaN | 48.7318 | 409.7475 | NaN | 9.1672 | NaN | 28.0248
7823.1292 | 14.0929 | 13.8335 | 13.8279 | 14.1447 | 13.6639 | 13.7993 | 13.5041 | 13.3804 | NaN | NaN | NaN | 13.6389 | 122.886 | NaN | NaN | 41.3105 | NaN | NaN | NaN | NaN | 36.8864 | 409.767 | NaN | 13.983 | NaN | 13.3639
7824.1292 | 14.0773 | 13.8818 | 13.8295 | 14.1265 | 13.6686 | 13.8062 | 13.4969 | 13.3837 | NaN | NaN | NaN | 13.6047 | 128.4388 | NaN | NaN | 31.6604 | NaN | NaN | NaN | NaN | 34.5803 | 418.3591 | NaN | 13.8575 | NaN | 15.8376
7825.1292 | 14.093 | 13.8421 | 13.8306 | 14.149 | 13.6463 | 13.8013 | 13.5006 | 13.384 | NaN | NaN | NaN | 13.6313 | 120.6348 | NaN | NaN | 47.5996 | 15.6978 | NaN | NaN | NaN | 16.4211 | 417.8864 | NaN | -0.5963 | NaN | 15.9596
7826.1292 | 14.0885 | 13.8387 | 13.8312 | 14.1498 | 13.66 | 13.8035 | 13.5026 | 13.383 | NaN | NaN | NaN | 13.6335 | 127.9075 | NaN | NaN | 77.4129 | NaN | NaN | NaN | NaN | 33.2772 | 419.8792 | NaN | 7.9127 | NaN | 14.4054
7827.1292 | 14.1026 | 13.8703 | 13.8352 | 14.1353 | 13.5866 | 13.8095 | 13.5038 | 13.3808 | NaN | NaN | NaN | 13.6273 | 131.1509 | NaN | NaN | 36.1704 | NaN | NaN | NaN | NaN | 27.2188 | 422.8625 | NaN | 5.8707 | NaN | 23.6609
7828.1292 | 14.0871 | 13.8389 | 13.8328 | 14.1255 | 13.6366 | 13.8104 | 13.4978 | 13.3827 | NaN | NaN | NaN | 13.6087 | 126.841 | NaN | NaN | 33.9542 | NaN | NaN | NaN | NaN | 48.1216 | 430.8359 | NaN | 9.9011 | NaN | 16.5597
7829.1292 | 14.1041 | 13.8807 | 13.83 | 14.1485 | 13.6675 | 13.8124 | 13.5007 | 13.3833 | NaN | NaN | NaN | 13.6157 | 130.3683 | NaN | NaN | 43.5929 | NaN | NaN | NaN | NaN | 40.6178 | 437.9949 | NaN | 26.8975 | NaN | 16.9637
7830.1292 | 14.0914 | 13.8437 | 13.8326 | 14.1463 | 13.5489 | 13.8055 | 13.4976 | 13.3844 | NaN | NaN | NaN | 13.6388 | 129.6976 | NaN | NaN | 42.9827 | NaN | NaN | NaN | NaN | 24.9376 | 440.6071 | NaN | -3.1601 | NaN | 26.1941
7831.1292 | 14.1025 | 13.8548 | 13.8254 | 14.1357 | 13.6478 | 13.8096 | 13.4963 | 13.3797 | NaN | NaN | NaN | 13.6456 | 122.0931 | NaN | NaN | 36.5865 | NaN | NaN | NaN | NaN | 29.787 | 441.7067 | NaN | 20.6349 | NaN | 27.8687
7832.1292 | 14.0886 | 13.8478 | 13.8215 | 14.1159 | 13.6098 | 13.8065 | 13.4886 | 13.3812 | NaN | NaN | NaN | 13.6248 | 129.8444 | NaN | NaN | 31.8238 | -18.5492 | NaN | NaN | NaN | 32.141 | 446.991 | NaN | 10.2243 | NaN | 19.4165
7833.1292 | 14.0987 | 13.8619 | 13.8192 | 14.2343 | 13.6416 | 13.8115 | 13.5032 | 13.3855 | NaN | NaN | NaN | 13.6079 | 131.5971 | NaN | NaN | 33.866 | -1.9464 | NaN | NaN | NaN | 23.8596 | 456.7591 | NaN | 14.2231 | NaN | 26.832
7834.1292 | 14.1435 | 13.8467 | 13.8189 | 14.1343 | 13.5896 | 13.8075 | 13.4922 | 13.3821 | NaN | NaN | NaN | 13.6224 | 128.2548 | NaN | NaN | 58.2997 | NaN | NaN | NaN | NaN | 22.212 | 455.6551 | NaN | 20.0598 | NaN | 7.417
7835.1292 | 14.1031 | 13.9235 | 13.8157 | 14.1256 | 13.6693 | 13.8167 | 13.4919 | 13.3832 | NaN | NaN | NaN | 13.6283 | 135.8591 | NaN | NaN | 62.0671 | NaN | NaN | NaN | NaN | 25.6608 | 454.1005 | NaN | 32.2424 | NaN | 34.9638
7836.1292 | 14.1364 | 13.8439 | 13.818 | 14.1429 | 13.6469 | 13.7983 | 13.494 | 13.3872 | NaN | NaN | NaN | 13.6299 | 132.7847 | NaN | NaN | 54.8468 | NaN | NaN | NaN | NaN | 20.8669 | 441.2656 | NaN | 17.2611 | NaN | 22.9469
7837.1292 | 14.1115 | 13.8511 | 13.8179 | 14.1773 | 13.6463 | 13.8167 | 13.4941 | 13.3857 | NaN | NaN | NaN | 13.6193 | 127.6272 | NaN | NaN | 52.0845 | NaN | NaN | NaN | NaN | 54.6081 | 444.8875 | NaN | 12.9659 | NaN | 29.5502
7838.1292 | 14.1649 | 13.8454 | 13.8227 | 14.1497 | 13.6017 | 13.8058 | 13.4951 | 13.3933 | NaN | NaN | NaN | 13.6305 | 126.0321 | NaN | NaN | 98.0528 | NaN | NaN | NaN | NaN | 47.1825 | 442.7597 | NaN | 8.7528 | NaN | 9.9411
7839.1292 | 14.1137 | 13.9082 | 13.8192 | 14.1362 | 13.6502 | 13.8159 | 13.4961 | 13.3869 | NaN | NaN | NaN | 13.6494 | 132.9238 | NaN | NaN | 115.6742 | NaN | NaN | NaN | NaN | 43.3729 | 448.3248 | NaN | 23.2878 | NaN | 14.8389
7840.1292 | 14.2503 | 13.8446 | 13.8242 | 14.157 | 13.655 | 13.8188 | 13.4949 | 13.3882 | NaN | NaN | NaN | 13.6065 | 130.3907 | NaN | NaN | 122.4069 | -13.642 | NaN | NaN | NaN | 47.0076 | 459.0751 | NaN | 7.8883 | NaN | 27.9892
7841.1292 | 14.1064 | 13.8423 | 13.8241 | 14.158 | 13.6541 | 13.8079 | 13.4826 | 13.3818 | NaN | NaN | NaN | 13.6283 | 130.0399 | NaN | NaN | 120.2592 | NaN | NaN | NaN | NaN | 51.5268 | 461.9147 | NaN | 20.1501 | NaN | 27.7108
7842.1292 | 14.1199 | 13.8546 | 13.8263 | 14.1364 | 13.6578 | 13.8154 | 13.4801 | 13.3867 | NaN | NaN | NaN | 13.6344 | 133.6415 | NaN | NaN | 114.784 | NaN | NaN | NaN | NaN | 46.946 | 465.3734 | NaN | 32.1048 | NaN | 12.6249
7843.1292 | 14.1092 | 13.841 | 13.8242 | 14.1629 | 13.6602 | 13.7989 | 13.4832 | 13.3848 | NaN | NaN | NaN | 13.6353 | 133.4639 | NaN | NaN | 118.0647 | NaN | NaN | NaN | NaN | 36.9763 | 476.6703 | NaN | 24.3621 | NaN | 11.918
7844.1448 | 14.1135 | 13.842 | 13.8214 | 14.1424 | 13.6242 | 13.8066 | 13.4821 | 13.3848 | NaN | NaN | NaN | 13.623 | 126.6468 | NaN | NaN | 126.1814 | NaN | NaN | NaN | NaN | 31.1463 | 488.6526 | NaN | 5.7458 | NaN | 22.3701
7845.1292 | 14.1089 | 13.8473 | 13.8267 | 14.1323 | 13.6522 | 13.8029 | 13.4762 | 13.3856 | NaN | NaN | NaN | 13.6424 | 129.72 | NaN | NaN | 108.6647 | 13.0533 | NaN | NaN | NaN | 18.5973 | 493.4524 | NaN | 9.1223 | NaN | 19.7909
7846.1292 | 14.1139 | 13.8375 | 13.8339 | 14.154 | 13.653 | 13.8055 | 13.4824 | 13.3926 | NaN | NaN | NaN | 13.6379 | 131.9225 | NaN | NaN | 101.1366 | NaN | NaN | NaN | NaN | 41.0773 | 492.0982 | NaN | 5.7097 | NaN | 27.7158
7847.1292 | 14.138 | 13.8519 | 13.8254 | 14.1312 | 13.673 | 13.8113 | 13.482 | 13.3898 | NaN | NaN | NaN | 13.6518 | 132.2508 | NaN | NaN | 116.2254 | NaN | NaN | NaN | NaN | 44.5288 | 493.8023 | NaN | 8.9505 | NaN | 17.2634
7848.1292 | 14.1159 | 13.8675 | 13.8283 | 14.1382 | 13.6035 | 13.809 | 13.479 | 13.3851 | NaN | NaN | NaN | 13.6304 | 127.7443 | NaN | NaN | 97.9568 | NaN | NaN | NaN | NaN | 40.4255 | 488.9226 | NaN | 12.7687 | NaN | 28.527
7849.1292 | 14.1123 | 13.8687 | 13.8266 | 14.156 | 13.6803 | 13.7985 | 13.484 | 13.3824 | NaN | NaN | NaN | 13.6335 | 129.3745 | NaN | NaN | 110.1621 | NaN | NaN | NaN | NaN | 47.1817 | 484.5608 | NaN | 13.9693 | NaN | 22.7524
7850.1292 | 14.1175 | 13.8995 | 13.8303 | 14.1461 | 13.6556 | 13.8043 | 13.4834 | 13.3849 | NaN | NaN | NaN | 13.6298 | 133.9523 | NaN | NaN | 115.5374 | NaN | NaN | NaN | NaN | 49.7382 | 479.208 | NaN | 10.9786 | NaN | 10.5372
7851.1292 | 14.1013 | 13.8559 | 13.8372 | 14.1557 | 13.6444 | 13.795 | 13.4796 | 13.3823 | NaN | NaN | NaN | 13.6262 | 122.7963 | NaN | NaN | 103.3121 | -19.3887 | NaN | NaN | NaN | 46.4268 | 470.5037 | NaN | 15.8698 | NaN | 29.4752
7852.1292 | 14.1103 | 13.9005 | 13.8363 | 14.1416 | 13.616 | 13.8106 | 13.4877 | 13.3812 | NaN | NaN | NaN | 13.6277 | 132.9886 | NaN | NaN | 114.244 | 14.4384 | NaN | NaN | NaN | 45.9007 | 465.2216 | NaN | 26.9634 | NaN | 25.5865
7853.1292 | 14.0958 | 13.8397 | 13.838 | 14.1643 | 13.6759 | 13.782 | 13.4765 | 13.3807 | NaN | NaN | NaN | 13.6191 | 130.7097 | NaN | NaN | 108.9993 | NaN | NaN | NaN | NaN | 44.0583 | 455.9163 | NaN | 7.8162 | NaN | 14.8772
7854.1292 | 14.1069 | 13.8494 | 13.8334 | 14.1232 | 13.6582 | 13.7869 | 13.4757 | 13.3837 | NaN | NaN | NaN | 13.6352 | 138.4676 | NaN | NaN | 116.9974 | NaN | NaN | NaN | NaN | 41.9295 | 461.1093 | NaN | 22.4786 | NaN | 30.7358
7855.1292 | 14.1326 | 13.8436 | 13.8359 | 14.1436 | 13.6073 | 13.7985 | 13.4897 | 13.3848 | NaN | NaN | NaN | 13.6504 | 130.3055 | NaN | NaN | 106.3687 | NaN | NaN | NaN | NaN | 46.8749 | 468.4155 | NaN | 2.369 | NaN | 21.6823
7856.1292 | 14.104 | 13.8491 | 13.839 | 14.127 | 13.6755 | 13.783 | 13.4821 | 13.3879 | NaN | NaN | NaN | 13.5918 | 135.799 | NaN | NaN | 104.4858 | NaN | NaN | NaN | NaN | 33.0603 | 473.6469 | NaN | 10.4518 | NaN | 18.529
7857.1292 | 14.1063 | 13.8524 | 13.8361 | 14.1471 | 13.6554 | 13.7865 | 13.4834 | 13.3786 | NaN | NaN | NaN | 13.6234 | 132.272 | NaN | NaN | 120.1141 | NaN | NaN | NaN | NaN | 25.3522 | 472.5852 | NaN | 14.7045 | NaN | 20.8782
7858.1292 | 14.1255 | 13.8528 | 13.8305 | 14.1366 | 13.6556 | 13.7957 | 13.4857 | 13.3847 | NaN | NaN | NaN | 13.6524 | 126.7491 | NaN | NaN | 113.8651 | NaN | NaN | NaN | NaN | 44.2016 | 484.8058 | NaN | 20.1357 | NaN | 23.7324
7859.1292 | 14.1105 | 13.8451 | 13.8326 | 14.1632 | 13.6398 | 13.7852 | 13.4721 | 13.3849 | NaN | NaN | NaN | 13.6133 | 127.0625 | NaN | NaN | 113.9108 | -14.5676 | NaN | NaN | NaN | 50.3196 | 488.7325 | NaN | 14.3724 | NaN | 8.4834
7860.1292 | 14.1584 | 13.8477 | 13.8376 | 14.1444 | 13.6579 | 13.7971 | 13.4806 | 13.3825 | NaN | NaN | NaN | 13.6693 | 133.8353 | NaN | NaN | 118.6072 | NaN | NaN | NaN | NaN | 44.3683 | 496.6665 | NaN | 5.9631 | NaN | 6.2868
7861.1292 | 14.1148 | 13.8511 | 13.8303 | 14.1666 | 13.5807 | 13.7812 | 13.4743 | 13.3816 | NaN | NaN | NaN | 13.6147 | 126.2904 | NaN | NaN | 117.4026 | NaN | NaN | NaN | NaN | 46.6409 | 503.8946 | NaN | 10.6733 | NaN | 31.5143
7862.1292 | 14.1187 | 13.8724 | 13.8385 | 14.1512 | 13.6542 | 13.7948 | 13.4896 | 13.3821 | NaN | NaN | NaN | 13.6322 | 129.171 | NaN | NaN | 106.3883 | NaN | NaN | NaN | NaN | 57.5898 | 514.1742 | NaN | 12.278 | NaN | 20.0909
7863.1292 | 14.107 | 13.8335 | 13.8422 | 14.1842 | 13.6117 | 13.7845 | 13.4815 | 13.3818 | NaN | NaN | NaN | 13.5993 | 126.9072 | NaN | NaN | 58.8253 | NaN | NaN | NaN | NaN | 55.0121 | 521.1944 | NaN | 20.3158 | NaN | 17.2236
7864.1292 | 14.1555 | 13.8384 | 13.8433 | 14.1517 | 13.6321 | 13.7775 | 13.4804 | 13.3837 | NaN | NaN | NaN | 13.617 | 128.4144 | NaN | NaN | 48.3141 | NaN | NaN | NaN | NaN | 41.2191 | 524.0697 | NaN | 20.6839 | NaN | 30.1194
7865.1292 | 14.1078 | 13.8572 | 13.8352 | 14.1415 | 13.6114 | 13.7876 | 13.4818 | 13.3829 | NaN | NaN | NaN | 13.638 | 134.8452 | NaN | NaN | 60.0935 | NaN | NaN | NaN | NaN | 43.5789 | 531.1635 | NaN | 11.8671 | NaN | 15.3381
7866.1292 | 14.1072 | 13.8402 | 13.847 | 14.1659 | 13.6461 | 13.7684 | 13.4836 | 13.3769 | NaN | NaN | NaN | 13.6138 | 140.7704 | NaN | NaN | 61.4168 | 10.406 | NaN | NaN | NaN | 41.8466 | 525.7684 | NaN | 16.0434 | NaN | 22.5523
7867.1292 | 14.1011 | 13.8553 | 13.8425 | 14.1424 | 13.6626 | 13.7875 | 13.4939 | 13.375 | NaN | NaN | NaN | 13.6203 | 133.696 | NaN | NaN | 47.4327 | NaN | NaN | NaN | NaN | 51.4935 | 525.1269 | NaN | 6.4884 | NaN | 17.4848
7868.1292 | 14.1074 | 13.8322 | 13.8405 | 14.2094 | 13.6789 | 13.7835 | 13.4852 | 13.3782 | NaN | NaN | NaN | 13.6157 | 127.4441 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 47.497 | 536.4699 | NaN | 19.5734 | NaN | 17.9949
7869.1292 | 14.0923 | 13.8358 | 13.8371 | 14.1472 | 13.6128 | 13.7859 | 13.483 | 13.3715 | NaN | NaN | NaN | 13.6139 | 130.6756 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 46.8631 | 538.0422 | NaN | 23.1656 | NaN | 9.6385
7870.1292 | 14.0981 | 13.8177 | 13.8391 | 14.1947 | 13.6739 | 13.7778 | 13.4859 | 13.3682 | NaN | NaN | NaN | 13.6135 | 122.7848 | NaN | NaN | 18.6821 | NaN | NaN | NaN | NaN | 57.6545 | 543.5188 | NaN | 15.9712 | NaN | 28.3121
7871.1292 | 14.0874 | 13.8696 | 13.8412 | 14.1527 | 13.6035 | 13.7852 | 13.4881 | 13.3653 | NaN | NaN | NaN | 13.6018 | 132.694 | NaN | NaN | 41.5735 | NaN | NaN | NaN | NaN | 44.7441 | 541.6823 | NaN | 10.0954 | NaN | 15.2617
7872.1292 | 14.0985 | 13.8395 | 13.8459 | 14.1493 | 13.6173 | 13.783 | 13.483 | 13.3698 | NaN | NaN | NaN | 13.6301 | 128.1236 | NaN | NaN | 53.8228 | -16.9976 | NaN | NaN | NaN | 29.8789 | 542.3875 | NaN | 6.6382 | NaN | 20.5351
7873.1292 | 14.0814 | 13.8716 | 13.8412 | 14.1282 | 13.635 | 13.7881 | 13.4914 | 13.3687 | NaN | NaN | NaN | 13.5935 | 124.7073 | NaN | NaN | NaN | -1.3158 | NaN | NaN | NaN | 30.4901 | 541.6441 | NaN | 15.485 | NaN | 15.1677
7874.1292 | 14.0915 | 13.8525 | 13.8472 | 14.1483 | 13.6742 | 13.781 | 13.4841 | 13.3671 | NaN | NaN | NaN | 13.6069 | 124.9414 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 34.6071 | 540.9005 | NaN | 6.7087 | NaN | 18.3409
7875.1292 | 14.123 | 13.8798 | 13.8513 | 14.1424 | 13.6816 | 13.7939 | 13.4918 | 13.3626 | NaN | NaN | NaN | 13.6072 | 131.4975 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 57.9306 | 535.0382 | NaN | 22.0221 | NaN | 33.2609
7876.1292 | 14.0893 | 13.8425 | 13.8451 | 14.1547 | 13.6582 | 13.781 | 13.4862 | 13.3616 | NaN | NaN | NaN | 13.6064 | 124.6942 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 39.8187 | 534.3756 | NaN | 11.4385 | NaN | 27.9115
7877.1292 | 14.1038 | 13.8315 | 13.8522 | 14.213 | 13.5625 | 13.799 | 13.4895 | 13.3667 | NaN | NaN | NaN | 13.6185 | 127.0159 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 35.167 | 537.6626 | NaN | 26.4634 | NaN | 25.7476
7878.1292 | 14.092 | 13.8483 | 13.8497 | 14.1431 | 13.6697 | 13.7882 | 13.4775 | 13.3623 | NaN | NaN | NaN | 13.6053 | 129.8168 | NaN | NaN | -8.6849 | NaN | NaN | NaN | NaN | 41.4311 | 536.5985 | NaN | 29.1659 | NaN | 22.3066
7879.1292 | 14.0977 | 13.9601 | 13.8399 | 14.1295 | 13.6425 | 13.8023 | 13.4863 | 13.3566 | NaN | NaN | NaN | 13.6036 | 131.4 | NaN | NaN | 19.0349 | -16.2333 | NaN | NaN | NaN | 42.5577 | 542.4725 | NaN | 26.9648 | NaN | 8.3107
7880.1292 | 14.085 | 13.8306 | 13.8503 | 14.1859 | 13.6582 | 13.7821 | 13.4752 | 13.3575 | NaN | NaN | NaN | 13.5966 | 133.4109 | NaN | NaN | 65.1058 | NaN | NaN | NaN | NaN | 46.1566 | 539.5756 | NaN | 18.0006 | NaN | 13.7825
7881.1292 | 14.1061 | 13.8827 | 13.8454 | 14.1405 | 13.5946 | 13.7985 | 13.4828 | 13.3569 | NaN | NaN | NaN | 13.6051 | 130.7676 | NaN | NaN | 24.8401 | NaN | NaN | NaN | NaN | 35.7121 | 538.8143 | NaN | 7.3123 | NaN | 21.4956
7882.1292 | 14.1 | 13.8737 | 13.8481 | 14.1391 | 13.6388 | 13.7909 | 13.484 | 13.3532 | NaN | NaN | NaN | 13.6118 | 126.0061 | NaN | NaN | 33.6774 | NaN | NaN | NaN | NaN | 32.3862 | 539.8259 | NaN | -1.4095 | NaN | 14.2441
7883.1292 | 14.1004 | 13.8181 | 13.8392 | 14.1217 | 13.6137 | 13.7706 | 13.4744 | 13.3621 | NaN | NaN | NaN | 13.5953 | 193.4118 | NaN | NaN | 142.6041 | NaN | NaN | 160.5688 | NaN | 51.4674 | 436.6268 | NaN | NaN | NaN | -15.8873
7884.1292 | 14.0956 | 13.8291 | 13.8459 | 14.1224 | 13.6791 | 13.7687 | 13.473 | 13.3569 | NaN | NaN | NaN | 13.5815 | 194.3343 | NaN | NaN | 220.0512 | NaN | NaN | NaN | NaN | 60.4007 | 425.1851 | NaN | NaN | NaN | -17.7355
7885.1292 | 14.1021 | 13.8191 | 13.8455 | 14.126 | 13.6738 | 13.7704 | 13.4775 | 13.36 | NaN | NaN | NaN | 13.5951 | 198.6001 | NaN | NaN | 199.2274 | NaN | NaN | 148.31 | NaN | 51.9419 | 422.3102 | NaN | NaN | NaN | -11.1604
7886.1292 | 14.0872 | 13.8838 | 13.8444 | 14.1197 | 13.6435 | 13.7774 | 13.477 | 13.3554 | NaN | NaN | NaN | 13.5757 | 193.4853 | NaN | NaN | 231.2767 | NaN | NaN | -10.0624 | NaN | 63.0052 | 420.1441 | NaN | NaN | NaN | -0.0086
7887.1292 | 14.1031 | 13.8251 | 13.84 | 14.1208 | 13.6777 | 13.7652 | 13.475 | 13.3534 | NaN | NaN | NaN | 13.6224 | 194.8105 | NaN | NaN | 216.5044 | NaN | NaN | 109.4645 | NaN | 61.4687 | 420.9971 | NaN | -12.9936 | NaN | -1.8465
7888.1292 | 14.1041 | 13.8413 | 13.8434 | 14.1594 | 13.6754 | 13.7659 | 13.4848 | 13.3606 | NaN | NaN | NaN | 13.6016 | 203.0935 | NaN | NaN | 203.7236 | NaN | NaN | 134.0234 | NaN | 69.0823 | 417.755 | NaN | -16.9056 | NaN | -13.1618
7889.1292 | 14.1274 | 13.8418 | 13.8434 | 14.1322 | 13.6295 | 13.7552 | 13.4754 | 13.3553 | NaN | NaN | NaN | 13.6178 | 205.2823 | NaN | NaN | 206.2288 | NaN | NaN | 87.13 | NaN | 62.779 | 407.8313 | NaN | NaN | NaN | -17.737
7890.1292 | 14.0983 | 13.8251 | 13.8474 | 14.126 | 13.6744 | 13.7583 | 13.4776 | 13.3555 | NaN | NaN | NaN | 13.6245 | 210.7411 | NaN | NaN | 200.4487 | NaN | NaN | 56.8418 | NaN | 57.6856 | 410.127 | NaN | NaN | NaN | -19.6072
7891.1292 | 14.0951 | 13.896 | 13.8416 | 14.1154 | 13.6518 | 13.7758 | 13.4868 | 13.3523 | NaN | NaN | NaN | 13.6298 | 202.619 | NaN | NaN | 229.2097 | NaN | NaN | 72.6912 | NaN | 54.9053 | 405.9651 | NaN | NaN | NaN | -0.4776
7892.1292 | 14.099 | 13.8198 | 13.8504 | 14.1179 | 13.66 | 13.7565 | 13.4863 | 13.3514 | NaN | NaN | NaN | 13.6649 | 215.743 | NaN | NaN | 194.9856 | 4.3869 | NaN | 242.3803 | NaN | 62.2464 | 400.8333 | NaN | NaN | NaN | -10.0853
7893.1292 | 14.0933 | 13.8226 | 13.8454 | 14.1415 | 13.6085 | 13.762 | 13.4849 | 13.3584 | NaN | NaN | NaN | 13.6895 | 205.0524 | NaN | NaN | 210.7962 | NaN | NaN | 162.7881 | NaN | 64.2013 | 396.1253 | NaN | -13.2549 | NaN | 5.7103
7894.1292 | 14.1102 | 13.8114 | 13.848 | 14.1043 | 13.664 | 13.7541 | 13.4837 | 13.3609 | NaN | NaN | NaN | 13.7307 | 192.9715 | NaN | NaN | 205.0764 | NaN | NaN | -9.1435 | NaN | 71.8055 | 397.3459 | NaN | NaN | NaN | -9.9062
7895.1292 | 14.0947 | 13.8133 | 13.8471 | 14.1431 | 13.6814 | 13.7589 | 13.4847 | 13.3619 | NaN | NaN | NaN | 13.8047 | 193.1502 | NaN | NaN | 209.8829 | NaN | NaN | 179.1246 | NaN | 60.3906 | 406.6258 | NaN | NaN | NaN | -5.7985
7896.1292 | 14.1019 | 13.8177 | 13.8476 | 14.12 | 13.6789 | 13.7573 | 13.4807 | 13.3572 | NaN | NaN | NaN | 13.8917 | 210.0299 | NaN | NaN | 227.5428 | NaN | NaN | 55.0572 | NaN | 64.8828 | 409.8844 | NaN | NaN | NaN | -5.5049
7897.1292 | 14.0929 | 13.853 | 13.8429 | 14.1125 | 13.6716 | 13.7679 | 13.4917 | 13.3647 | NaN | NaN | NaN | 14.0499 | 196.8963 | NaN | NaN | 222.7433 | NaN | NaN | 12.665 | NaN | 73.496 | 403.7854 | NaN | NaN | NaN | -2.2842
7898.1292 | 14.1698 | 13.814 | 13.8464 | 14.1055 | 13.6647 | 13.7489 | 13.4875 | 13.359 | NaN | NaN | NaN | 14.218 | 189.3318 | NaN | NaN | 195.8139 | -7.4573 | NaN | 233.8283 | NaN | 55.923 | 402.3359 | NaN | NaN | NaN | -7.7588
7899.1292 | 14.0945 | 13.8132 | 13.8453 | 14.1608 | 13.6527 | 13.7597 | 13.4876 | 13.3539 | NaN | NaN | NaN | 14.461 | 201.744 | NaN | NaN | 220.8701 | NaN | NaN | 129.4367 | NaN | 60.9309 | 406.1262 | NaN | NaN | NaN | -12.1353
7900.1292 | 14.0883 | 13.8232 | 13.8519 | 14.1284 | 13.6622 | 13.7533 | 13.4862 | 13.3606 | NaN | NaN | NaN | 14.7736 | 205.4535 | NaN | NaN | 227.0868 | NaN | NaN | 37.0776 | NaN | 65.4849 | 407.0415 | NaN | -3.5859 | NaN | NaN
7901.1292 | 14.0918 | 13.8238 | 13.8533 | 14.1259 | 13.6733 | 13.7477 | 13.4842 | 13.3631 | NaN | NaN | NaN | 15.1549 | 214.4604 | NaN | NaN | 227.2694 | NaN | NaN | 117.7434 | NaN | 48.3727 | 402.3386 | NaN | NaN | NaN | NaN
7902.1292 | 14.0913 | 13.8243 | 13.8483 | 14.1171 | 13.6643 | 13.7522 | 13.4828 | 13.3629 | NaN | NaN | NaN | 15.6251 | 204.7263 | NaN | NaN | 237.7304 | NaN | NaN | 82.1966 | NaN | 52.6625 | 403.287 | NaN | NaN | NaN | -15.8934
7903.1292 | 14.1002 | 13.8244 | 13.8574 | 14.1062 | 13.6031 | 13.7592 | 13.479 | 13.3651 | NaN | NaN | NaN | 16.143 | 203.4118 | NaN | NaN | 232.8981 | NaN | NaN | 227.3602 | NaN | 59.0168 | 401.2595 | NaN | NaN | NaN | -16.3602
7904.1292 | 14.0932 | 13.8431 | 13.8573 | 14.1145 | 13.6886 | 13.7529 | 13.4877 | 13.3612 | NaN | NaN | NaN | 16.8102 | 206.9232 | NaN | NaN | 200.8621 | 5.102 | NaN | 201.5879 | NaN | 66.9487 | 403.0145 | NaN | NaN | NaN | -14.1222
7905.1292 | 14.0881 | 13.8317 | 13.8512 | 14.1372 | 13.6789 | 13.753 | 13.4847 | 13.3651 | NaN | NaN | NaN | 17.468 | 204.9073 | NaN | NaN | 198.5396 | NaN | NaN | 185.8648 | NaN | 67.366 | 399.097 | NaN | NaN | NaN | 0.2951
7906.1292 | 14.1043 | 13.8322 | 13.8493 | 14.1329 | 13.6739 | 13.7561 | 13.483 | 13.3608 | NaN | NaN | NaN | 18.1474 | 199.3053 | NaN | NaN | 232.9949 | NaN | NaN | 536.0212 | NaN | 84.4091 | 402.5754 | NaN | -9.1619 | NaN | -9.8914
7907.1292 | 14.1043 | 13.8396 | 13.8538 | 14.1229 | 13.6352 | 13.7597 | 13.4847 | 13.3663 | NaN | NaN | NaN | 18.9816 | 196.6477 | NaN | NaN | 209.8887 | NaN | NaN | 37.5261 | NaN | 76.1488 | 406.6348 | NaN | NaN | NaN | -3.2447
7908.1292 | 14.1036 | 13.8192 | 13.8575 | 14.1301 | 13.6556 | 13.7421 | 13.4865 | 13.3621 | NaN | NaN | NaN | 19.9033 | 204.9045 | NaN | NaN | 220.8424 | NaN | NaN | 131.3209 | NaN | 57.291 | 405.5755 | NaN | NaN | NaN | -2.2441
7909.1292 | 14.0991 | 13.8218 | 13.8567 | 14.1113 | 13.6267 | 13.7538 | 13.4771 | 13.3575 | NaN | NaN | NaN | 20.7491 | 202.6365 | NaN | NaN | 238.6106 | NaN | NaN | 142.1955 | NaN | 65.3934 | 409.5074 | NaN | NaN | NaN | -6.1251
7910.1292 | 14.1061 | 13.8641 | 13.8576 | 14.1822 | 13.6538 | 13.7689 | 13.4973 | 13.355 | NaN | NaN | NaN | 21.7135 | 207.0359 | NaN | NaN | 198.8569 | NaN | NaN | 110.8886 | NaN | 69.3159 | 411.3589 | NaN | -14.9546 | NaN | -7.2533
7911.1292 | 14.1051 | 13.8064 | 13.854 | 14.1207 | 13.6764 | 13.7632 | 13.5018 | 13.3566 | NaN | NaN | NaN | 22.5779 | 206.2223 | NaN | NaN | 231.504 | NaN | NaN | 79.963 | NaN | 71.4149 | 401.2002 | NaN | NaN | NaN | NaN
7912.1292 | 14.1083 | 13.8078 | 13.8583 | 14.1252 | 13.6795 | 13.763 | 13.4978 | 13.3543 | NaN | NaN | NaN | 23.46 | 208.7051 | NaN | NaN | 199.5003 | NaN | NaN | 290.4909 | NaN | 74.8609 | 390.9194 | NaN | -18.1717 | NaN | 1.1578
7913.1292 | 14.1135 | 13.8033 | 13.8597 | 14.1274 | 13.6783 | 13.7742 | 13.5002 | 13.3552 | NaN | NaN | NaN | 24.3625 | 192.343 | NaN | NaN | 221.0455 | NaN | NaN | 247.6151 | NaN | 74.7713 | 392.8582 | NaN | NaN | NaN | 3.3386
7914.1292 | 14.1094 | 13.8213 | 13.857 | 14.1275 | 13.6773 | 13.7805 | 13.4944 | 13.3571 | NaN | NaN | NaN | 25.3981 | 207.4126 | NaN | NaN | 196.0254 | NaN | NaN | 401.9898 | NaN | 95.9138 | 389.6465 | NaN | NaN | NaN | -1.0024
7915.1292 | 14.1157 | 13.7928 | 13.8616 | 14.1341 | 13.6805 | 13.7739 | 13.4975 | 13.365 | NaN | NaN | NaN | 26.3758 | 201.3226 | NaN | NaN | 225.8773 | NaN | NaN | 155.4929 | NaN | 68.5359 | 389.1279 | NaN | NaN | NaN | NaN
7916.1292 | 14.1105 | 13.7869 | 13.8662 | 14.1324 | 13.6793 | 13.784 | 13.4973 | 13.3615 | NaN | NaN | NaN | 27.5474 | 194.3458 | NaN | NaN | 208.4526 | NaN | NaN | 281.977 | NaN | 60.4579 | 398.3955 | NaN | NaN | NaN | -18.0429
7917.1292 | 14.1128 | 13.7947 | 13.8597 | 14.1505 | 13.6879 | 13.7964 | 13.5164 | 13.366 | NaN | NaN | NaN | 28.4589 | 197.6094 | NaN | NaN | 202.7226 | NaN | NaN | 837.4642 | NaN | 70.7605 | 414.0317 | NaN | NaN | NaN | -13.7679
7918.1292 | 14.1048 | 13.7877 | 13.8574 | 14.1963 | 13.692 | 13.7878 | 13.5095 | 13.3703 | NaN | NaN | NaN | 29.4911 | 206.306 | NaN | NaN | 224.2529 | NaN | NaN | 420.344 | NaN | 79.4915 | 420.8097 | NaN | -15.8289 | NaN | -0.1737
7919.1292 | 14.1071 | 13.7726 | 13.8667 | 14.1205 | 13.6827 | 13.7979 | 13.5148 | 13.3722 | NaN | NaN | NaN | 30.6177 | 204.0142 | NaN | NaN | 200.4184 | NaN | NaN | 532.8512 | NaN | 114.2807 | 430.3273 | NaN | NaN | NaN | 1.7906
7920.1292 | 14.1057 | 13.7719 | 13.8616 | 14.1539 | 13.6621 | 13.8019 | 13.5307 | 13.3784 | NaN | NaN | NaN | 31.9006 | 197.8109 | NaN | NaN | 197.7699 | NaN | NaN | 210.8198 | NaN | 118.4656 | 438.4055 | NaN | NaN | NaN | 6.824
7921.1292 | 14.1037 | 13.7695 | 13.869 | 14.1264 | 13.6791 | 13.8023 | 13.5455 | 13.3757 | NaN | NaN | NaN | 32.7138 | 211.0892 | NaN | NaN | 195.724 | NaN | NaN | 272.1234 | NaN | 120.1332 | 449.7422 | NaN | -3.7169 | NaN | -9.0908
7922.1292 | 14.1025 | 13.7751 | 13.8692 | 14.1254 | 13.6332 | 13.8106 | 13.5535 | 13.3845 | NaN | NaN | NaN | 33.7723 | 198.8351 | NaN | NaN | 229.8741 | NaN | NaN | 29.9893 | NaN | 111.6109 | 459.1191 | NaN | NaN | NaN | NaN
7923.1292 | 14.1049 | 13.7583 | 13.8736 | 14.1245 | 13.69 | 13.8109 | 13.5464 | 13.3798 | NaN | NaN | NaN | 35.1024 | 209.4869 | NaN | NaN | 226.9788 | NaN | NaN | 91.2319 | NaN | 127.1953 | 460.9426 | NaN | NaN | NaN | NaN
7924.1292 | 14.1205 | 13.7638 | 13.8762 | 14.1262 | 13.6965 | 13.8128 | 13.5627 | 13.3817 | NaN | NaN | NaN | 36.3783 | 201.0788 | NaN | NaN | 232.3952 | NaN | NaN | 562.0509 | NaN | 109.5891 | 473.1033 | NaN | NaN | NaN | 9.892
7925.1292 | 14.1306 | 13.7808 | 13.8785 | 14.1233 | 13.6523 | 13.8137 | 13.5716 | 13.3752 | NaN | NaN | NaN | 37.3313 | 198.2222 | NaN | NaN | 227.0227 | 6.2914 | NaN | 253.3381 | NaN | 80.8407 | 478.7976 | NaN | -7.8145 | NaN | -19.1286
7926.1292 | 14.1404 | 13.7656 | 13.8804 | 14.1552 | 13.6099 | 13.8078 | 13.5812 | 13.3781 | NaN | NaN | NaN | 38.3193 | 211.8899 | NaN | NaN | 212.4083 | NaN | NaN | 280.3823 | NaN | 69.5045 | 486.8868 | NaN | NaN | NaN | 3.1873
7927.1292 | 14.1443 | 13.7954 | 13.8762 | 14.1443 | 13.6953 | 13.8273 | 13.5853 | 13.3755 | NaN | NaN | NaN | 39.373 | 206.2385 | NaN | NaN | 223.0053 | NaN | NaN | 307.0285 | NaN | 70.5934 | 490.8671 | NaN | NaN | NaN | NaN
7928.1292 | 14.1438 | 13.7881 | 13.8759 | 14.1333 | 13.6865 | 13.8133 | 13.5898 | 13.3715 | NaN | NaN | NaN | 40.5479 | 210.7732 | NaN | NaN | 198.8905 | NaN | NaN | 416.9699 | NaN | 65.4965 | 496.839 | NaN | NaN | NaN | -18.3766
7929.1292 | 14.1502 | 13.7683 | 13.8764 | 14.1331 | 13.6598 | 13.8202 | 13.5912 | 13.3695 | NaN | NaN | NaN | 41.3892 | 198.1627 | NaN | NaN | 196.9202 | NaN | NaN | 0.5962 | NaN | 73.7874 | 503.3183 | NaN | NaN | NaN | -8.9096
7930.1292 | 14.1405 | 13.7671 | 13.8726 | 14.1639 | 13.6068 | 13.8274 | 13.5989 | 13.3708 | NaN | NaN | NaN | 42.2872 | 194.9179 | NaN | NaN | 204.273 | 0.7352 | NaN | 325.8575 | NaN | 85.2249 | 502.3173 | NaN | NaN | NaN | -0.8084
7931.1292 | 14.1395 | 13.7623 | 13.873 | 14.1474 | 13.6931 | 13.8242 | 13.5967 | 13.3728 | NaN | NaN | NaN | 42.9636 | 203.5748 | NaN | NaN | 229.8335 | NaN | NaN | 89.3223 | NaN | 64.7589 | 505.12 | NaN | NaN | NaN | -19.1026
7932.1292 | 14.1416 | 13.7542 | 13.8756 | 14.1438 | 13.6983 | 13.829 | 13.601 | 13.3688 | NaN | NaN | NaN | 43.6816 | 203.1718 | NaN | NaN | 208.0615 | NaN | NaN | 226.1913 | NaN | 75.9618 | 506.342 | NaN | NaN | NaN | NaN
7933.1292 | 14.1437 | 13.7548 | 13.8679 | 14.157 | 13.6956 | 13.827 | 13.6049 | 13.3666 | NaN | NaN | NaN | 44.2126 | 207.9096 | NaN | NaN | 213.3857 | NaN | NaN | 112.8771 | NaN | 67.256 | 507.4014 | NaN | NaN | NaN | -13.9075
7934.1292 | 14.1421 | 13.7571 | 13.8676 | 14.1445 | 13.6977 | 13.8348 | 13.6175 | 13.3688 | NaN | NaN | NaN | 44.8132 | 206.694 | NaN | NaN | 210.5512 | NaN | NaN | 89.4546 | NaN | 92.753 | 503.7244 | NaN | NaN | NaN | -6.4574
7935.1292 | 14.1405 | 13.7559 | 13.8664 | 14.1913 | 13.6934 | 13.8372 | 13.6163 | 13.3689 | NaN | NaN | NaN | 45.4005 | 206.4912 | NaN | NaN | 218.2209 | NaN | NaN | 57.5613 | NaN | 79.0461 | 500.8564 | NaN | -2.5186 | NaN | -2.4736
7936.1292 | 14.1431 | 13.7483 | 13.8698 | 14.1658 | 13.7125 | 13.8379 | 13.6216 | 13.3727 | NaN | NaN | NaN | 45.9828 | 195.1958 | NaN | NaN | 206.6452 | NaN | NaN | 228.2905 | NaN | 62.1188 | 498.8759 | NaN | NaN | NaN | -4.5247
7937.1292 | 14.1392 | 13.7448 | 13.8687 | 14.148 | 13.7133 | 13.8418 | 13.63 | 13.3749 | NaN | NaN | NaN | 46.6041 | 198.2368 | NaN | NaN | 218.8526 | NaN | NaN | 125.244 | NaN | 63.8137 | 496.1859 | NaN | 1.8808 | NaN | 14.5729
7938.1292 | 14.136 | 13.7418 | 13.874 | 14.136 | 13.7196 | 13.8422 | 13.6296 | 13.3789 | NaN | NaN | NaN | 47.1035 | 194.8933 | NaN | NaN | 218.2131 | NaN | NaN | 111.2541 | NaN | 66.6876 | 488.6981 | NaN | NaN | NaN | NaN
7939.1292 | 14.1391 | 13.8236 | 13.8757 | 14.166 | 13.7018 | 13.8486 | 13.6294 | 13.3724 | NaN | NaN | NaN | 47.4774 | 214.3611 | NaN | NaN | 225.0511 | NaN | NaN | 147.9099 | NaN | 78.2391 | 478.8382 | NaN | NaN | NaN | -0.9306
7940.1292 | 14.1428 | 13.7777 | 13.8787 | 14.1559 | 13.7133 | 13.8421 | 13.6231 | 13.3709 | NaN | NaN | NaN | 47.8957 | 203.6335 | NaN | NaN | 209.9521 | NaN | NaN | 244.8553 | NaN | 81.7036 | 473.0329 | NaN | NaN | NaN | -9.2496
7941.1292 | 14.1451 | 13.7526 | 13.8779 | 14.1503 | 13.7118 | 13.8449 | 13.6278 | 13.3696 | NaN | NaN | NaN | 48.328 | 206.4495 | NaN | NaN | 220.2724 | NaN | NaN | 254.7262 | NaN | 50.0363 | 472.7263 | NaN | NaN | NaN | -19.667
7942.1292 | 14.1365 | 13.7662 | 13.8798 | 14.1465 | 13.725 | 13.8442 | 13.6385 | 13.3706 | NaN | NaN | NaN | 48.7531 | 201.8902 | NaN | NaN | 212.0127 | NaN | NaN | 228.3564 | NaN | 69.1144 | 470.9122 | NaN | -18.3488 | NaN | -18.5131
7943.1292 | 14.138 | 13.7941 | 13.8732 | 14.1845 | 13.7066 | 13.859 | 13.651 | 13.3697 | NaN | NaN | NaN | 49.2242 | 204.6482 | NaN | NaN | 215.0571 | NaN | NaN | 154.9221 | NaN | 61.8335 | 465.641 | NaN | NaN | NaN | -14.1604
7944.1292 | 14.1383 | 13.7945 | 13.8762 | 14.1836 | 13.7234 | 13.8555 | 13.6501 | 13.3753 | NaN | NaN | NaN | 49.7451 | 206.2121 | NaN | NaN | 211.4379 | NaN | NaN | 405.4904 | NaN | 69.9549 | 461.7581 | NaN | NaN | NaN | -15.489
7945.1292 | 14.1313 | 13.7801 | 13.8844 | 14.1649 | 13.7288 | 13.853 | 13.6607 | 13.379 | NaN | NaN | NaN | 50.2638 | 192.7685 | NaN | NaN | 222.7423 | NaN | NaN | 357.066 | NaN | 64.8196 | 461.0974 | NaN | NaN | NaN | -8.5926
7946.1292 | 14.1306 | 13.833 | 13.8761 | 14.1668 | 13.7303 | 13.869 | 13.6622 | 13.3787 | NaN | NaN | NaN | 50.7269 | 212.2912 | NaN | NaN | 231.1441 | NaN | NaN | -2.4193 | NaN | 66.5527 | 459.4833 | NaN | -19.2839 | NaN | -6.4282
7947.1292 | 14.1361 | 13.7828 | 13.8811 | 14.1652 | 13.7396 | 13.8669 | 13.6608 | 13.3738 | NaN | NaN | NaN | 52.5294 | 202.4888 | NaN | NaN | 204.227 | NaN | NaN | 138.2146 | NaN | 73.488 | 459.1355 | NaN | NaN | NaN | -14.4547
7948.1292 | 14.1249 | 13.7546 | 13.8873 | 14.1552 | 13.7479 | 13.8647 | 13.6803 | 13.3697 | NaN | NaN | NaN | 53.9683 | 199.6913 | NaN | NaN | 229.4608 | NaN | NaN | 44.7535 | NaN | 81.2595 | 452.1182 | NaN | NaN | NaN | -4.6444
7949.1292 | 14.1275 | 13.7563 | 13.8859 | 14.1786 | 13.7322 | 13.8657 | 13.6792 | 13.3712 | NaN | NaN | NaN | 56.5741 | 213.3409 | NaN | NaN | 211.6706 | NaN | NaN | 160.6956 | NaN | 102.8773 | 440.5558 | NaN | NaN | NaN | -8.835
7950.1292 | 14.13 | 13.7724 | 13.8958 | 14.1534 | 13.7829 | 13.8627 | 13.6914 | 13.3694 | NaN | NaN | NaN | 69.2744 | 205.3486 | NaN | NaN | 226.7885 | NaN | NaN | 196.3687 | NaN | 86.4736 | 430.2936 | NaN | NaN | NaN | -6.9272
7951.1292 | 14.9014 | 13.7966 | 13.8985 | 14.1645 | 13.7856 | 13.8927 | 13.7164 | 13.3735 | NaN | NaN | NaN | 90.8356 | 198.4409 | NaN | NaN | 194.8393 | NaN | NaN | 71.2825 | NaN | 82.524 | 422.5895 | NaN | NaN | NaN | NaN
7952.1292 | 16.3343 | 13.8906 | 13.9193 | 14.151 | 13.8329 | 13.8632 | 13.9248 | 13.4571 | NaN | NaN | NaN | 123.1939 | 188.9906 | NaN | NaN | 198.0954 | NaN | NaN | 51.1845 | NaN | 87.5412 | 413.7756 | NaN | NaN | NaN | NaN
7953.1292 | 18.3271 | 14.2047 | 14.0857 | 14.1415 | 13.9045 | 14.0485 | 14.6782 | 13.8355 | NaN | NaN | NaN | 180.8053 | 201.4826 | NaN | NaN | 210.2021 | NaN | NaN | NaN | NaN | 115.6239 | 397.1426 | NaN | 11.4461 | NaN | -13.4482
7954.1292 | 22.7502 | 15.0359 | 14.1373 | 14.1312 | 14.2937 | 14.9506 | 16.0409 | 14.8593 | NaN | NaN | NaN | 211.5683 | 244.7149 | NaN | NaN | 272.7659 | 29.1131 | NaN | NaN | NaN | 172.4386 | 367.9647 | NaN | NaN | NaN | -6.9694
7955.1292 | 30.8875 | 16.3714 | 14.2192 | 14.1933 | 14.5157 | 16.667 | 19.3255 | 17.7258 | NaN | NaN | NaN | 253.349 | 361.1684 | NaN | NaN | 396.3579 | 1345.4243 | NaN | NaN | NaN | 242.7037 | 343.613 | NaN | 17.2484 | NaN | 23.8497
7956.1292 | 43.4813 | 18.1006 | 14.7516 | 14.4582 | 14.8579 | 17.863 | 23.0924 | 20.4005 | NaN | NaN | NaN | 288.6845 | 626.1754 | NaN | NaN | 709.2058 | NaN | NaN | NaN | NaN | 278.8907 | 262.2725 | NaN | -13.2596 | NaN | 21.842
7957.1292 | 54.7134 | 20.8924 | 15.4476 | 14.8328 | 15.7091 | 19.8433 | 28.4009 | 24.4665 | NaN | NaN | NaN | 301.8963 | 761.4549 | NaN | NaN | 925.7651 | NaN | NaN | NaN | NaN | 274.0173 | 220.8339 | NaN | -4.9105 | NaN | 28.2349
7958.1292 | 71.9048 | 23.3311 | 16.0015 | 15.1585 | 16.6339 | 21.0134 | 35.0865 | 29.9164 | NaN | NaN | NaN | 332.518 | 862.8573 | NaN | NaN | 1110.9696 | NaN | NaN | NaN | NaN | 266.7704 | 192.5786 | NaN | 17.4179 | NaN | 15.4998
7959.1292 | 116.4795 | 26.4924 | 17.1265 | 16.6387 | 18.1755 | 23.1818 | 40.4745 | 34.1206 | NaN | NaN | NaN | 352.7749 | 867.3526 | NaN | NaN | 1178.2274 | NaN | NaN | NaN | NaN | 285.6507 | 201.6365 | NaN | 9.5588 | NaN | 26.1976
7960.1292 | 140.2946 | 29.8732 | 18.5071 | 17.9464 | 19.8144 | 25.7888 | 46.1515 | 38.1307 | NaN | NaN | NaN | 352.3762 | 747.1775 | NaN | NaN | 1074.8504 | NaN | NaN | NaN | NaN | 338.9358 | 243.3381 | NaN | 19.0814 | NaN | 15.1483
7961.1292 | 141.6507 | 33.2908 | 20.2798 | 19.3318 | 21.4963 | 29.0381 | 51.9939 | 43.8155 | NaN | NaN | NaN | 375.0238 | 628.0613 | NaN | NaN | 969.9609 | NaN | NaN | NaN | NaN | 390.1569 | 287.8469 | NaN | 9.1331 | NaN | 21.9537
7962.1292 | 143.8121 | 35.6068 | 21.8163 | 20.8369 | 23.045 | 30.5266 | 55.0672 | 46.8591 | NaN | NaN | NaN | 389.9084 | 511.3967 | NaN | NaN | 862.6357 | NaN | NaN | NaN | NaN | 446.4086 | 324.8182 | NaN | 5.7436 | NaN | 18.9761
7963.1292 | 147.0585 | 37.5578 | 23.1153 | 22.7556 | 24.7912 | 32.1277 | 57.9959 | 48.3883 | NaN | NaN | NaN | 413.8706 | 436.2257 | NaN | NaN | 807.9928 | NaN | NaN | NaN | NaN | 487.5144 | 345.8159 | NaN | -3.3279 | NaN | 9.6189
7964.1448 | 149.7323 | 39.5921 | 25.0757 | 24.7705 | 26.4964 | 33.4671 | 62.4385 | 51.2609 | NaN | NaN | NaN | 428.3753 | 361.2715 | NaN | NaN | 752.2606 | NaN | NaN | NaN | NaN | 475.935 | 370.0687 | NaN | 6.2545 | NaN | 24.8958
7965.1292 | 150.8402 | 41.4415 | 27.765 | 25.8486 | 28.5946 | 34.6939 | 64.3751 | 53.6767 | NaN | NaN | NaN | 439.9948 | 319.8929 | NaN | NaN | 736.5627 | NaN | NaN | NaN | NaN | 446.0523 | 379.6502 | NaN | 10.5019 | NaN | 18.2272
7966.1292 | 153.3873 | 43.0797 | 30.251 | 28.4426 | 31.0514 | 37.0047 | 66.9537 | 56.3411 | NaN | NaN | NaN | 456.2909 | 239.6583 | NaN | NaN | 674.8533 | NaN | NaN | NaN | NaN | 374.4995 | 386.9832 | NaN | 18.5442 | NaN | 29.4592
7967.1292 | 155.3825 | 44.4431 | 32.4243 | 30.153 | 33.2067 | 38.6482 | 69.7505 | 57.5981 | NaN | NaN | NaN | 482.3005 | 196.2779 | NaN | NaN | 654.6 | NaN | NaN | NaN | NaN | 342.8362 | 393.3216 | NaN | 11.4381 | NaN | 17.5677
7968.1292 | 156.6462 | 46.1314 | 33.7703 | 32.0507 | 35.1146 | 39.9561 | 73.6011 | 60.9881 | NaN | NaN | NaN | 492.9719 | 128.019 | NaN | NaN | 593.0666 | NaN | NaN | NaN | NaN | 276.2187 | 405.0308 | NaN | 11.8348 | NaN | 9.007
7969.1292 | 158.9038 | 47.3893 | 35.3046 | 34.1065 | 37.1326 | 42.3501 | 76.7189 | 63.8434 | NaN | NaN | NaN | 509.7922 | 125.04 | NaN | NaN | 558.8937 | NaN | NaN | NaN | NaN | 243.2094 | 421.5802 | NaN | 5.0131 | NaN | 26.8109
7970.1292 | 161.2015 | 49.1759 | 36.9986 | 35.4837 | 39.4616 | 43.8935 | 79.7633 | 66.5986 | NaN | NaN | NaN | 524.9501 | 128.6997 | NaN | NaN | 545.0086 | NaN | NaN | NaN | NaN | 229.8784 | 429.7425 | NaN | 12.4352 | NaN | 14.4763
7971.1292 | 163.0453 | 50.8247 | 39.1624 | 37.5587 | 41.1883 | 45.1137 | 83.106 | 69.6039 | NaN | NaN | NaN | 544.6682 | 130.4929 | NaN | NaN | 521.7339 | NaN | NaN | NaN | NaN | 215.3148 | 447.9341 | NaN | 18.7231 | NaN | 10.441
7972.1292 | 165.468 | 53.0537 | 41.0651 | 38.3734 | 43.2842 | 47.1881 | 86.542 | 72.9646 | NaN | NaN | NaN | 550.4701 | 133.4667 | NaN | NaN | 493.9865 | 1096.6544 | NaN | NaN | NaN | 199.4807 | 462.0378 | NaN | 19.3374 | NaN | 26.7023
7973.1292 | 167.7521 | 54.961 | 42.7504 | 41.0733 | 45.2877 | 49.0493 | 89.1495 | 75.7717 | NaN | NaN | NaN | 565.5011 | 123.8901 | NaN | NaN | 475.4229 | 826.0481 | NaN | NaN | NaN | 201.1399 | 473.7913 | NaN | 18.7353 | NaN | 7.5945
7974.1292 | 168.9482 | 56.4574 | 43.9282 | 42.619 | 47.4825 | 50.3455 | 91.5288 | 77.8041 | NaN | NaN | NaN | 588.9726 | 129.1441 | NaN | NaN | 465.6927 | 674.0795 | NaN | NaN | NaN | 199.2211 | 490.3447 | NaN | 15.7303 | NaN | 18.8815
7975.1292 | 170.2154 | 57.585 | 45.7631 | 44.9501 | 49.6424 | 51.8382 | 93.7208 | 80.0172 | NaN | NaN | NaN | 617.0954 | 134.508 | NaN | NaN | 448.9284 | 464.049 | NaN | NaN | NaN | 198.342 | 511.2673 | NaN | 18.5985 | NaN | 7.5072
7976.1292 | 171.2549 | 58.6379 | 48.761 | 46.9208 | 51.7606 | 53.7533 | 95.1221 | 81.3054 | NaN | NaN | NaN | 629.8353 | 130.401 | NaN | NaN | 431.1493 | 316.9995 | NaN | NaN | NaN | 195.2858 | 529.5009 | NaN | 19.5705 | NaN | 8.1205
7977.1292 | 172.7093 | 60.2297 | 50.0071 | 45.9368 | 54.29 | 55.6936 | 96.9875 | 82.3802 | NaN | NaN | NaN | 651.6789 | 132.1742 | NaN | NaN | 408.3833 | 163.1573 | NaN | NaN | NaN | 189.4113 | 553.8757 | NaN | 13.8125 | NaN | 13.9915
7978.1292 | 173.259 | 61.6156 | 52.0753 | 49.8007 | 56.0912 | 57.5003 | 99.705 | 83.9898 | NaN | NaN | NaN | 657.2818 | 129.7988 | NaN | NaN | 385.6092 | 65.7401 | NaN | NaN | NaN | 182.9419 | 570.4911 | NaN | 25.2775 | NaN | 7.9446
7979.1292 | 172.7941 | 62.954 | 53.9315 | 51.9102 | 58.0003 | 59.3262 | 102.1444 | 85.4682 | NaN | NaN | NaN | 664.7867 | 131.3155 | NaN | NaN | 388.0934 | 86.2743 | NaN | NaN | NaN | 197.5745 | 579.2654 | NaN | 15.1049 | NaN | 29.9482
7980.1292 | 174.7715 | 63.8523 | 56.4689 | 53.2698 | 59.5206 | 61.5475 | 103.4823 | 87.492 | NaN | NaN | NaN | 668.0727 | 128.6665 | NaN | NaN | 352.7601 | -15.3522 | NaN | NaN | NaN | 176.2752 | 604.8566 | NaN | 13.3561 | NaN | 14.5222
7981.1292 | 175.0454 | 64.7835 | 58.4247 | 55.0318 | 61.3567 | 63.2037 | 105.2495 | 88.5329 | NaN | NaN | NaN | 681.5777 | 136.1369 | NaN | NaN | 346.8353 | -14.7669 | NaN | NaN | NaN | 183.901 | 605.2325 | NaN | 0.9648 | NaN | 8.7958
7982.1292 | 175.7197 | 65.775 | 59.5431 | 56.3853 | 63.5243 | 65.6195 | 106.6556 | 90.2873 | NaN | NaN | NaN | 689.0399 | 123.071 | NaN | NaN | 317.4809 | NaN | NaN | NaN | NaN | 171.5275 | 602.9879 | NaN | 20.5786 | NaN | 21.7461
7983.1292 | 176.5519 | 66.4592 | 61.5232 | 58.2024 | 65.2247 | 67.8906 | 108.1867 | 91.686 | NaN | NaN | NaN | 694.2083 | 124.4848 | NaN | NaN | 304.7566 | NaN | NaN | NaN | NaN | 174.4645 | 611.1743 | NaN | 18.9785 | NaN | 36.4025
7984.1292 | 175.6631 | 67.4337 | 64.0183 | 59.999 | 66.8853 | 70.1432 | 108.8826 | 93.1486 | NaN | NaN | NaN | 682.5505 | 128.4662 | NaN | NaN | 290.6123 | NaN | NaN | NaN | NaN | 175.8606 | 621.1466 | NaN | 10.0241 | NaN | 8.4356
7985.1292 | 177.08 | 68.0382 | 65.3514 | 60.0826 | 68.1877 | 71.2965 | 110.9026 | 94.4373 | NaN | NaN | NaN | 688.01 | 130.5656 | NaN | NaN | 278.6703 | NaN | NaN | NaN | NaN | 177.4951 | 623.9262 | NaN | 17.823 | NaN | 13.1795
7986.1292 | 178.3612 | 68.9545 | 67.2778 | 58.7217 | 69.5793 | 73.4003 | 112.0524 | 97.0642 | NaN | NaN | NaN | 683.6471 | 135.3645 | NaN | NaN | 272.713 | NaN | NaN | NaN | NaN | 179.5908 | 621.7004 | NaN | 21.5113 | NaN | 19.5551
7987.1292 | 179.8775 | 69.9164 | 69.0506 | 61.346 | 71.8312 | 74.5293 | 113.1769 | 98.019 | NaN | NaN | NaN | 689.3672 | 127.6404 | NaN | NaN | 256.9536 | NaN | NaN | NaN | NaN | 177.8942 | 624.2391 | NaN | 10.4837 | NaN | 34.0153
7988.1292 | 180.8363 | 71.1869 | 71.8252 | 58.84 | 73.6489 | 79.3794 | 115.8054 | 98.5555 | NaN | NaN | NaN | 666.1089 | 122.9782 | NaN | NaN | 247.0214 | NaN | NaN | NaN | NaN | 181.7708 | 624.4383 | NaN | 13.6651 | NaN | 9.7195
7989.1448 | 184.3451 | 72.1189 | 73.872 | 63.3047 | 75.2221 | 81.3678 | 116.8706 | 99.6278 | NaN | NaN | NaN | 668.9752 | 132.3818 | NaN | NaN | 247.7851 | NaN | NaN | NaN | NaN | 192.108 | 631.4277 | NaN | 7.3426 | NaN | 28.5739
7990.1292 | 184.7619 | 73.3237 | 75.1775 | 64.5711 | 76.6773 | 83.0368 | 119.7829 | 101.8065 | NaN | NaN | NaN | 675.2869 | 130.9806 | NaN | NaN | 245.7333 | NaN | NaN | NaN | NaN | 201.3725 | 641.6055 | NaN | 3.4047 | NaN | 16.6673
7991.1292 | 184.957 | 74.0965 | 76.7269 | 67.075 | 78.3028 | 85.3966 | 121.6094 | 103.3135 | NaN | NaN | NaN | 642.2674 | 131.7182 | NaN | NaN | 237.9956 | NaN | NaN | NaN | NaN | 202.4168 | 646.1106 | NaN | 30.757 | NaN | 31.9072
7992.1292 | 189.0155 | 75.5821 | 77.6256 | 70.8277 | 80.0027 | 87.1247 | 124.3148 | 106.7412 | NaN | NaN | NaN | 637.9768 | 132.6979 | NaN | NaN | 231.9304 | NaN | NaN | NaN | NaN | 209.0345 | 651.35 | NaN | 4.0144 | NaN | 7.9683
7993.1448 | 189.4488 | 76.9872 | 78.8767 | 73.2847 | 82.0823 | 90.7235 | 127.9274 | 108.0103 | NaN | NaN | NaN | 608.0978 | 131.4858 | NaN | NaN | 224.7037 | NaN | NaN | NaN | NaN | 213.1843 | 660.0632 | NaN | 12.0389 | NaN | 29.0609
7994.1448 | 188.3403 | 77.993 | 80.105 | 75.4407 | 83.7169 | 92.9654 | 130.8353 | 109.7173 | NaN | NaN | NaN | 584.2325 | 128.1863 | NaN | NaN | 220.0185 | NaN | NaN | NaN | NaN | 218.892 | 667.0513 | NaN | 21.3458 | NaN | 22.99
7995.1448 | 190.6886 | 79.2296 | 81.7561 | 66.7549 | 85.5288 | 97.131 | 132.8194 | 110.0606 | NaN | NaN | NaN | 572.2763 | 127.7225 | NaN | NaN | 209.5566 | NaN | NaN | NaN | NaN | 219.9334 | 670.0114 | NaN | 15.2826 | NaN | 31.9999
7996.1292 | 189.4222 | 80.6962 | 83.6717 | 75.7546 | 87.1052 | 100.5195 | 134.2327 | 110.4011 | NaN | NaN | NaN | 551.3524 | 131.2299 | NaN | NaN | 205.802 | NaN | NaN | NaN | NaN | 226.6037 | 677.3922 | NaN | 2.2898 | NaN | 9.3037
7997.1292 | 190.0095 | 82.0365 | 84.7185 | 80.442 | 88.7357 | 102.451 | 135.4517 | 110.5442 | NaN | NaN | NaN | 545.1365 | 123.9477 | NaN | NaN | 203.016 | NaN | NaN | NaN | NaN | 236.3231 | 681.0395 | NaN | 21.2023 | NaN | 22.65
7998.1292 | 191.9411 | 83.801 | 85.9548 | 76.1323 | 90.5836 | 104.7376 | 136.3556 | 111.3771 | NaN | NaN | NaN | 528.5708 | 123.6302 | NaN | NaN | 192.6692 | NaN | NaN | NaN | NaN | 238.345 | 687.7709 | NaN | 22.0756 | NaN | 21.4214
7999.1292 | 192.1884 | 84.659 | 87.1876 | 83.0599 | 92.0161 | 106.4011 | 137.8119 | 113.0703 | NaN | NaN | NaN | 522.3119 | 124.5155 | NaN | NaN | 195.1222 | NaN | NaN | NaN | NaN | 249.3609 | 690.0791 | NaN | 6.5387 | NaN | 35.7263
8000.1292 | 196.1308 | 85.3419 | 88.4775 | 80.4567 | 93.7634 | 111.4876 | 139.2336 | 113.9978 | NaN | NaN | NaN | 516.9543 | 131.4754 | NaN | NaN | 187.7133 | NaN | NaN | NaN | NaN | 253.7148 | 694.817 | NaN | 0.4143 | NaN | 9.3019
8001.1292 | 199.2467 | 86.178 | 89.0456 | 82.7239 | 94.9487 | 115.0705 | 141.907 | 117.3639 | NaN | NaN | NaN | 510.0324 | 125.4592 | NaN | NaN | 189.377 | NaN | NaN | NaN | NaN | 265.1831 | 687.9693 | NaN | 5.4599 | NaN | 27.5567
8002.1292 | 201.6291 | 87.5743 | 89.3072 | 84.8754 | 96.1237 | 117.9628 | 143.6742 | 118.4061 | NaN | NaN | NaN | 499.8019 | 129.393 | NaN | NaN | 180.2033 | NaN | NaN | NaN | NaN | 269.4021 | 687.1317 | NaN | 14.7788 | NaN | 20.6254
8003.1292 | 202.2085 | 88.3365 | 90.1474 | 86.3047 | 97.3307 | 119.5452 | 145.072 | 119.4222 | NaN | NaN | NaN | 498.8456 | 134.6833 | NaN | NaN | 179.9364 | NaN | NaN | NaN | NaN | 277.6117 | 690.4678 | NaN | 18.0611 | NaN | 8.9961
8004.1292 | 204.341 | 88.7796 | 90.5026 | 90.0938 | 98.5743 | 120.5941 | 145.4631 | 120.1231 | NaN | NaN | NaN | 521.9839 | 131.9539 | NaN | NaN | 185.5362 | NaN | NaN | NaN | NaN | 291.4102 | 690.2669 | NaN | 10.1407 | NaN | 9.588
8005.1292 | 205.3412 | 89.1557 | 91.5678 | 90.7112 | 99.5772 | 121.401 | 145.3593 | 121.7216 | NaN | NaN | NaN | 504.6692 | 129.4607 | NaN | NaN | 179.6734 | NaN | NaN | NaN | NaN | 296.0319 | 691.7327 | NaN | 8.3763 | NaN | 32.6983
8006.1292 | 203.8423 | 89.8128 | 92.8309 | 93.7644 | 100.7351 | 122.5174 | 146.5865 | 123.5707 | NaN | NaN | NaN | 510.5984 | 129.9597 | NaN | NaN | 181.1762 | NaN | NaN | NaN | NaN | 305.9236 | 691.9091 | NaN | 27.3005 | NaN | 16.692
8007.1292 | 204.3093 | 91.5214 | 93.5679 | 95.3383 | 101.6744 | 122.9088 | 147.4614 | 124.6351 | NaN | NaN | NaN | 523.0821 | 131.4999 | NaN | NaN | 178.1389 | NaN | NaN | NaN | NaN | 313.1855 | 701.517 | NaN | 29.7173 | NaN | 10.4647
8008.1292 | 207.5984 | 92.3539 | 94.1646 | 96.3708 | 102.7445 | 125.9878 | 150.8364 | 126.9917 | NaN | NaN | NaN | 532.2668 | 124.1393 | NaN | NaN | 176.1392 | NaN | NaN | NaN | NaN | 321.4888 | 715.7673 | NaN | 8.638 | NaN | 9.3678
8009.1292 | 209.6753 | 93.182 | 94.7775 | 97.4223 | 103.5816 | 127.4463 | 151.5929 | 128.0802 | NaN | NaN | NaN | 550.6872 | 130.5435 | NaN | NaN | 186.222 | -11.7563 | NaN | NaN | NaN | 336.6877 | 719.2944 | NaN | 5.8832 | NaN | 31.3424
8010.1292 | 211.4738 | 94.2908 | 95.2744 | 98.9502 | 104.4685 | 129.4713 | 153.3059 | 128.7739 | NaN | NaN | NaN | 575.2132 | 121.4335 | NaN | NaN | 186.5691 | 1.5419 | NaN | NaN | NaN | 342.9639 | 724.5931 | NaN | 8.7989 | NaN | 27.2576
8011.1292 | 211.5898 | 94.8365 | 96.1755 | 99.7368 | 105.7959 | 132.3337 | 154.8178 | 130.5611 | NaN | NaN | NaN | 585.7826 | 121.9027 | NaN | NaN | 184.4276 | 8.2283 | NaN | NaN | NaN | 347.4519 | 738.8931 | NaN | 10.5011 | NaN | 23.4367
8012.1292 | 212.768 | 96.1212 | 97.3166 | 99.8851 | 106.7936 | 132.4041 | 155.6808 | 134.1249 | NaN | NaN | NaN | 600.7909 | 132.9501 | NaN | NaN | 194.2795 | 60.0981 | NaN | NaN | NaN | 361.8673 | 740.8927 | NaN | 33.6342 | NaN | 10.3031
8013.1292 | 212.883 | 97.3474 | 97.8508 | 100.418 | 107.7754 | 132.8679 | 156.6246 | 135.8726 | NaN | NaN | NaN | 601.8519 | 125.7042 | NaN | NaN | 196.9002 | 100.7534 | NaN | NaN | NaN | 371.5772 | 739.6303 | NaN | 13.1599 | NaN | 32.8636
8014.1292 | 211.5232 | 98.5962 | 99.1638 | 100.5104 | 108.5715 | 133.9631 | 158.7264 | 136.8925 | NaN | NaN | NaN | 602.4868 | 113.5761 | NaN | NaN | 201.5552 | 152.3781 | NaN | NaN | NaN | 382.053 | 728.3647 | NaN | 32.0908 | NaN | 18.4007
8015.1292 | 210.8913 | 99.6286 | 99.5367 | 100.3924 | 109.2104 | 133.9807 | 160.0051 | 136.6802 | NaN | NaN | NaN | 583.8182 | 130.9867 | NaN | NaN | 202.5876 | 199.9188 | NaN | NaN | NaN | 389.4733 | 715.2578 | NaN | 6.5159 | NaN | 30.5378
8016.1292 | 212.2061 | 100.6856 | 100.6093 | 101.1411 | 109.8073 | 134.5635 | 160.9996 | 137.6614 | NaN | NaN | NaN | 594.3427 | 132.1243 | NaN | NaN | 211.5475 | 300.2791 | NaN | NaN | NaN | 400.6785 | 701.7008 | NaN | 8.0786 | NaN | 9.525
8017.1292 | 212.2589 | 101.5456 | 100.4291 | 101.7866 | 110.1758 | 136.6729 | 162.5201 | 140.6902 | NaN | NaN | NaN | 578.3841 | 129.7867 | NaN | NaN | 217.9676 | 426.2907 | NaN | NaN | NaN | 412.3812 | 691.7389 | NaN | 0.9037 | NaN | 7.1932
8018.1292 | 213.3907 | 101.861 | 100.9625 | 102.343 | 110.5998 | 136.6771 | 163.5035 | 142.1184 | NaN | NaN | NaN | 585.2813 | 133.9735 | NaN | NaN | 229.2184 | 610.1415 | NaN | NaN | NaN | 425.1251 | 688.1196 | NaN | 4.1913 | NaN | 23.5272
8019.1292 | 213.8571 | 103.0578 | 102.0687 | 102.7728 | 111.1955 | 136.6447 | 165.2586 | 143.2883 | NaN | NaN | NaN | 582.3552 | 138.9766 | NaN | NaN | 241.2881 | 927.6074 | NaN | NaN | NaN | 439.5482 | 684.5089 | NaN | 5.1274 | NaN | 9.2039
8020.1292 | 214.438 | 103.7934 | 103.6693 | 103.9459 | 112.2235 | 137.6821 | 166.0604 | 147.1035 | NaN | NaN | NaN | 569.1446 | 126.6557 | NaN | NaN | 247.6349 | 1124.1624 | NaN | NaN | NaN | 450.0451 | 674.4956 | NaN | 28.5328 | NaN | 27.7857
8021.1292 | 215.202 | 105.2822 | 104.5161 | 104.754 | 112.989 | 138.9539 | 167.9867 | 151.0719 | NaN | NaN | NaN | 584.385 | 129.5526 | NaN | NaN | 263.5341 | NaN | NaN | NaN | NaN | 466.7873 | 659.5936 | NaN | 8.5874 | NaN | 14.2558
8022.1292 | 220.1109 | 106.368 | 105.608 | 105.7796 | 113.9177 | 138.9083 | 169.6869 | 152.9394 | NaN | NaN | NaN | 602.8882 | 122.5876 | NaN | NaN | 281.2424 | NaN | NaN | NaN | NaN | 485.1637 | 642.0913 | NaN | 4.5155 | NaN | 28.6374
8023.1292 | 219.7638 | 107.7405 | 106.698 | 106.8487 | 115.066 | 138.8087 | 169.8596 | 153.212 | NaN | NaN | NaN | 615.9034 | 122.7705 | NaN | NaN | 293.996 | NaN | NaN | NaN | NaN | 496.9244 | 620.2093 | NaN | 11.2872 | NaN | 18.2968
8024.1292 | 220.4826 | 108.406 | 107.9049 | 107.4705 | 116.3386 | 139.1847 | 170.5579 | 155.1969 | NaN | NaN | NaN | 605.8183 | 124.7444 | NaN | NaN | 303.7743 | NaN | NaN | NaN | NaN | 507.1015 | 597.4982 | NaN | 24.3344 | NaN | 9.1347
8025.1292 | 219.8908 | 109.3903 | 109.2801 | 108.4437 | 117.2868 | 139.3225 | 170.4005 | 156.4763 | NaN | NaN | NaN | 596.1818 | 129.5086 | NaN | NaN | 321.7484 | NaN | NaN | NaN | NaN | 525.1257 | 577.061 | NaN | 15.801 | NaN | 14.3536
8026.1292 | 219.7824 | 110.2467 | 109.911 | 109.1886 | 118.1435 | 139.7529 | 171.0925 | 156.7751 | NaN | NaN | NaN | 604.7307 | 136.122 | NaN | NaN | 336.6478 | NaN | NaN | NaN | NaN | 540.238 | 565.2818 | NaN | 15.5333 | NaN | 15.0975
8027.1292 | 219.5907 | 110.9988 | 111.0146 | 109.8946 | 118.7467 | 139.8461 | 172.5311 | 157.8255 | NaN | NaN | NaN | 584.21 | 136.641 | NaN | NaN | 353.4557 | NaN | NaN | NaN | NaN | 556.0396 | 555.1505 | NaN | 29.5066 | NaN | 16.2833
8028.1292 | 219.4006 | 111.2907 | 111.6812 | 110.8651 | 119.8125 | 142.701 | 173.8458 | 160.5741 | NaN | NaN | NaN | 567.0773 | 124.7796 | NaN | NaN | 363.5371 | NaN | NaN | NaN | NaN | 566.6838 | 537.9797 | NaN | 23.6248 | NaN | 8.8444
8029.1292 | 221.8656 | 111.5094 | 112.3024 | 112.1074 | 120.676 | 141.9201 | 173.5223 | 163.4426 | NaN | NaN | NaN | 546.3523 | 133.4853 | NaN | NaN | 381.9548 | NaN | NaN | NaN | NaN | 583.5104 | 528.9549 | NaN | 17.3663 | NaN | 24.5998
8030.1292 | 222.7063 | 112.212 | 113.7217 | 113.0562 | 121.512 | 142.2485 | 174.3379 | 163.7407 | NaN | NaN | NaN | 526.9435 | 118.4156 | NaN | NaN | 390.8169 | NaN | NaN | NaN | NaN | 595.0098 | 524.483 | NaN | 14.5489 | NaN | 32.8739
8031.1292 | 222.1708 | 112.6778 | 114.227 | 114.8406 | 122.4503 | 143.8958 | 173.6944 | 163.1548 | NaN | NaN | NaN | 517.311 | 119.215 | NaN | NaN | 402.9832 | NaN | NaN | NaN | NaN | 607.6092 | 514.6882 | NaN | 15.5173 | NaN | 29.4905
8032.1292 | 222.0818 | 113.5584 | 114.6002 | 115.7798 | 122.792 | 145.8279 | 174.5415 | 163.4184 | NaN | NaN | NaN | 538.2617 | 137.7969 | NaN | NaN | 421.3255 | NaN | NaN | NaN | NaN | 627.6511 | 498.1716 | NaN | 9.9087 | NaN | 30.2184
8033.1292 | 221.8388 | 114.4802 | 115.0497 | 115.8195 | 123.6465 | 145.5298 | 175.7794 | 163.6273 | NaN | NaN | NaN | 518.1898 | 133.7238 | NaN | NaN | 432.6051 | NaN | NaN | NaN | NaN | 636.7036 | 483.1571 | NaN | 27.1449 | NaN | 9.1399
8034.1292 | 222.9701 | 115.0693 | 115.5769 | 117.2147 | 124.5194 | 145.7819 | 175.2479 | 164.4574 | NaN | NaN | NaN | 504.6443 | 136.2568 | NaN | NaN | 442.5074 | NaN | NaN | NaN | NaN | 646.0537 | 461.7185 | NaN | 19.28 | NaN | 20.2345
8035.1292 | 223.0931 | 116.1392 | 116.1972 | 118.0005 | 124.7797 | 145.5679 | 175.802 | 166.5513 | NaN | NaN | NaN | 502.7335 | 113.8726 | NaN | NaN | 451.8833 | NaN | NaN | NaN | NaN | 661.7327 | 439.8181 | NaN | 12.8199 | NaN | 15.5557
8036.1292 | 222.9144 | 116.1047 | 116.1345 | 117.9783 | 124.8535 | 145.5632 | 176.8101 | 167.4002 | NaN | NaN | NaN | 488.3235 | 130.1838 | NaN | NaN | 465.3681 | NaN | NaN | NaN | NaN | 673.6219 | 430.0824 | NaN | 22.0231 | NaN | 15.772
8037.1292 | 223.2986 | 116.6315 | 117.2891 | 118.4123 | 125.7583 | 146.8394 | 177.2952 | 170.1505 | NaN | NaN | NaN | 493.6299 | 132.5747 | NaN | NaN | 475.4121 | NaN | NaN | NaN | NaN | 683.2524 | 422.5792 | NaN | 1.3728 | NaN | 31.8431
8038.1292 | 223.9123 | 116.9591 | 117.8006 | 118.2092 | 126.5177 | 147.4351 | 178.2126 | 172.321 | NaN | NaN | NaN | 484.6295 | 125.5928 | NaN | NaN | 482.2282 | NaN | NaN | NaN | NaN | 696.0698 | 419.1517 | NaN | 11.5556 | NaN | 15.2266
8039.1292 | 227.2164 | 117.5515 | 118.732 | 118.0661 | 127.6556 | 147.5804 | 178.5876 | 171.8911 | NaN | NaN | NaN | 473.421 | 132.2622 | NaN | NaN | 489.3805 | NaN | NaN | NaN | NaN | 704.9618 | 414.2031 | NaN | 20.7815 | NaN | 7.5872
8040.1292 | 226.7691 | 118.7735 | 119.5122 | 118.7367 | 128.2871 | 147.1129 | 178.9402 | 173.0359 | NaN | NaN | NaN | 465.7153 | 136.2792 | NaN | NaN | 501.7051 | NaN | NaN | NaN | NaN | 716.1143 | 406.8847 | NaN | 24.1599 | NaN | 13.9355
8041.1292 | 228.1695 | 119.4279 | 120.2822 | 119.4333 | 129.3399 | 147.601 | 179.0723 | 173.9314 | NaN | NaN | NaN | 457.5881 | 118.5461 | NaN | NaN | 506.4108 | NaN | NaN | NaN | NaN | 726.1545 | 407.3837 | NaN | 5.7242 | NaN | 13.5192
8042.1292 | 228.263 | 120.3523 | 120.6638 | 119.5786 | 130.8266 | 146.6612 | 179.2088 | 173.7459 | NaN | NaN | NaN | 449.5927 | 117.7633 | NaN | NaN | 513.877 | NaN | NaN | NaN | NaN | 736.2697 | 412.4316 | NaN | 11.201 | NaN | 20.0736
8043.1292 | 230.3339 | 120.6767 | 121.5891 | 119.8669 | 131.8131 | 146.9132 | 179.423 | 175.2755 | NaN | NaN | NaN | 442.6964 | 134.4807 | NaN | NaN | 524.8638 | NaN | NaN | NaN | NaN | 747.0866 | 421.0353 | NaN | 13.8398 | NaN | 8.9373
8044.1292 | 231.5615 | 121.7584 | 121.8263 | 120.6632 | 132.1886 | 146.3232 | 181.5555 | 175.3851 | NaN | NaN | NaN | 445.514 | 123.5123 | NaN | NaN | 529.9271 | NaN | NaN | NaN | NaN | 756.5058 | 427.014 | NaN | 29.3745 | NaN | 29.0752
8045.1292 | 232.7609 | 122.3117 | 122.5562 | 121.4334 | 132.6963 | 147.4527 | 181.7047 | 175.8848 | NaN | NaN | NaN | 453.982 | 133.666 | NaN | NaN | 537.7233 | NaN | NaN | NaN | NaN | 766.9513 | 437.4826 | NaN | 8.9309 | NaN | 26.7696
8046.1292 | 231.6764 | 123.895 | 123.0494 | 121.1988 | 133.0719 | 148.533 | 182.9443 | 176.581 | NaN | NaN | NaN | 474.5322 | 127.4098 | NaN | NaN | 548.893 | NaN | NaN | NaN | NaN | 778.8503 | 439.1719 | NaN | 19.4362 | NaN | 19.8919
8047.1292 | 230.9237 | 124.1472 | 123.9757 | 122.3219 | 133.0928 | 149.1775 | 182.4292 | 177.2235 | NaN | NaN | NaN | 498.9805 | 133.4458 | NaN | NaN | 554.2281 | NaN | NaN | NaN | NaN | 786.6047 | 436.3787 | NaN | 31.5697 | NaN | 8.2428
8048.1292 | 232.4569 | 124.7034 | 125.2601 | 122.8118 | 133.753 | 148.5561 | 183.4724 | 177.058 | NaN | NaN | NaN | 517.0351 | 131.9394 | NaN | NaN | 561.0086 | NaN | NaN | NaN | NaN | 794.8216 | 438.9128 | NaN | 7.6577 | NaN | 24.4681
8049.1292 | 232.3531 | 124.5054 | 125.9701 | 122.9685 | 133.7619 | 148.6416 | 184.3039 | 177.8885 | NaN | NaN | NaN | 532.0435 | 125.645 | NaN | NaN | 567.0175 | NaN | NaN | NaN | NaN | 804.7348 | 442.0888 | NaN | 9.5058 | NaN | 21.8171
8050.1292 | 231.523 | 125.2389 | 125.9439 | 123.4374 | 133.7625 | 148.5832 | 183.9904 | 177.76 | NaN | NaN | NaN | 542.8597 | 131.2058 | NaN | NaN | 571.0657 | NaN | NaN | NaN | NaN | 810.561 | 446.2181 | NaN | 18.545 | NaN | 16.8392
8051.1292 | 231.9836 | 125.1245 | 125.88 | 123.4298 | 133.8995 | 148.6002 | 183.1807 | 175.8918 | NaN | NaN | NaN | 551.2651 | 130.443 | NaN | NaN | 575.9569 | NaN | NaN | NaN | NaN | 818.9621 | 451.9083 | NaN | 19.9177 | NaN | 24.793
8052.1292 | 231.2808 | 125.3826 | 125.8507 | 124.4246 | 134.6808 | 147.9094 | 183.183 | 174.7547 | NaN | NaN | NaN | 567.5149 | 130.5732 | NaN | NaN | 581.4585 | NaN | NaN | NaN | NaN | 827.6411 | 452.2664 | NaN | 24.6783 | NaN | 27.7673
8053.1292 | 229.7336 | 125.5057 | 126.186 | 124.6177 | 135.1334 | 147.5103 | 182.6422 | 173.6859 | NaN | NaN | NaN | 582.8776 | 117.7915 | NaN | NaN | 586.8171 | NaN | NaN | NaN | NaN | 838.4574 | 456.0084 | NaN | 15.9356 | NaN | 24.3995
8054.1292 | 230.0158 | 125.2789 | 126.7449 | 124.983 | 135.589 | 146.9908 | 181.9682 | 171.4019 | NaN | NaN | NaN | 587.7346 | 121.0496 | NaN | NaN | 584.3844 | NaN | NaN | NaN | NaN | 839.0803 | 464.9975 | NaN | 5.6057 | NaN | 16.4902
8055.1292 | 230.8829 | 125.542 | 126.8945 | 124.8769 | 135.8804 | 146.8585 | 181.2112 | 171.3226 | NaN | NaN | NaN | 590.8363 | 124.7838 | NaN | NaN | 584.9149 | NaN | NaN | NaN | NaN | 843.8857 | 471.1126 | NaN | 11.1437 | NaN | 17.8819
8056.1292 | 228.7062 | 126.2802 | 126.9786 | 124.6083 | 135.8675 | 147.0228 | 180.5239 | 170.6776 | NaN | NaN | NaN | 585.6795 | 124.4911 | NaN | NaN | 586.1914 | NaN | NaN | NaN | NaN | 848.9435 | 474.0044 | NaN | 29.9301 | NaN | 24.5348
8057.1292 | 229.3229 | 126.8319 | 127.4604 | 124.8574 | 135.9015 | 147.1424 | 179.9167 | 170.2454 | NaN | NaN | NaN | 577.0535 | 125.5894 | NaN | NaN | 587.5566 | NaN | NaN | NaN | NaN | 855.7756 | 477.5733 | NaN | 19.9936 | NaN | 15.2974
8058.1292 | 228.9784 | 127.3929 | 127.1571 | 124.9126 | 135.6668 | 148.234 | 180.0828 | 170.1589 | NaN | NaN | NaN | 588.1679 | 127.5568 | NaN | NaN | 586.6861 | NaN | NaN | NaN | NaN | 858.9257 | 480.4826 | NaN | 8.0032 | NaN | 29.7472
8059.1292 | 229.6248 | 127.3641 | 127.0949 | 125.0821 | 135.5824 | 148.3764 | 179.8399 | 170.6301 | NaN | NaN | NaN | 584.6352 | 117.1739 | NaN | NaN | 583.5923 | NaN | NaN | NaN | NaN | 861.7925 | 484.6164 | NaN | 5.5679 | NaN | 25.6933
8060.1448 | 229.7696 | 127.3337 | 127.3073 | 124.811 | 135.8246 | 149.456 | 179.5574 | 172.0881 | NaN | NaN | NaN | 587.995 | 125.6673 | NaN | NaN | 580.2474 | NaN | NaN | NaN | NaN | 863.2043 | 495.0352 | NaN | 18.6505 | NaN | 30.8992
8061.1292 | 230.1557 | 128.0319 | 127.5455 | 125.118 | 136.0758 | 148.7698 | 179.3377 | 172.6844 | NaN | NaN | NaN | 589.0014 | 124.4278 | NaN | NaN | 577.958 | NaN | NaN | NaN | NaN | 866.2475 | 505.025 | NaN | 3.0582 | NaN | 29.7086
8062.1292 | 230.013 | 128.958 | 127.8439 | 126.5767 | 136.7783 | 149.4248 | 179.3579 | 172.2785 | NaN | NaN | NaN | 591.0288 | 118.147 | NaN | NaN | 574.6848 | NaN | NaN | NaN | NaN | 870.2566 | 516.76 | NaN | 23.4866 | NaN | 31.931
8063.1292 | 229.1622 | 129.1652 | 127.6104 | 126.8684 | 136.6191 | 150.1844 | 179.9192 | 173.0446 | NaN | NaN | NaN | 604.1143 | 120.8272 | NaN | NaN | 573.7907 | NaN | NaN | NaN | NaN | 874.1236 | 532.0108 | NaN | 29.2281 | NaN | 15.6792
8064.1292 | 228.9655 | 128.9896 | 127.6403 | 127.1465 | 137.0321 | 150.2034 | 180.4678 | 174.6356 | NaN | NaN | NaN | 608.4512 | 126.4431 | NaN | NaN | 569.8575 | NaN | NaN | NaN | NaN | 874.8046 | 546.599 | NaN | 13.3238 | NaN | 30.6424
8065.1292 | 227.4789 | 128.8527 | 127.8518 | 127.8263 | 137.5212 | 150.3834 | 180.2589 | 176.6699 | NaN | NaN | NaN | 612.1167 | 125.0429 | NaN | NaN | 565.4544 | NaN | NaN | NaN | NaN | 876.719 | 549.9191 | NaN | 30.6983 | NaN | 32.0011
8066.1292 | 228.6423 | 128.7459 | 127.9394 | 128.8846 | 138.0406 | 150.8594 | 180.1578 | 177.1268 | NaN | NaN | NaN | 614.8325 | 126.762 | NaN | NaN | 563.2477 | NaN | NaN | NaN | NaN | 880.1612 | 551.1769 | NaN | 6.7074 | NaN | 21.2847
8067.1292 | 228.4627 | 128.8999 | 128.7712 | 129.0269 | 138.5168 | 152.2395 | 179.9979 | 177.2148 | NaN | NaN | NaN | 612.7553 | 123.6114 | NaN | NaN | 556.388 | NaN | NaN | NaN | NaN | 879.4485 | 551.6795 | NaN | 25.6042 | NaN | 28.9024
8068.1292 | 228.0959 | 128.8716 | 129.304 | 128.9939 | 138.7462 | 152.0787 | 180.0345 | 175.1165 | NaN | NaN | NaN | 621.8968 | 122.8784 | NaN | NaN | 552.7667 | NaN | NaN | NaN | NaN | 882.527 | 559.2637 | NaN | 16.4636 | NaN | 19.4559
8069.1292 | 228.3025 | 128.5817 | 129.4435 | 129.0391 | 138.7705 | 154.0389 | 180.3354 | 175.0077 | NaN | NaN | NaN | 637.661 | 123.8266 | NaN | NaN | 548.5943 | NaN | NaN | NaN | NaN | 883.3672 | 561.4063 | NaN | 16.8739 | NaN | 29.2248
8070.1292 | 228.4066 | 128.0683 | 129.5327 | 128.8319 | 138.5205 | 154.4739 | 180.6704 | 176.0762 | NaN | NaN | NaN | 627.5566 | 124.142 | NaN | NaN | 541.1323 | NaN | NaN | NaN | NaN | 881.013 | 563.9475 | NaN | 18.8455 | NaN | 32.6917
8071.1292 | 229.469 | 127.6089 | 129.4793 | 128.9407 | 138.477 | 154.4806 | 179.8801 | 175.1343 | NaN | NaN | NaN | 622.5394 | 117.4147 | NaN | NaN | 535.0617 | NaN | NaN | NaN | NaN | 881.5767 | 563.5673 | NaN | 14.8304 | NaN | 30.1094
8072.1292 | 227.5402 | 127.3938 | 129.5118 | 129.2326 | 138.7067 | 153.6312 | 179.2072 | 176.6219 | NaN | NaN | NaN | 619.5977 | 124.1207 | NaN | NaN | 528.9861 | NaN | NaN | NaN | NaN | 881.9019 | 563.2603 | NaN | 26.9374 | NaN | 24.5814
8073.1292 | 228.9645 | 127.1383 | 129.6192 | 128.7125 | 138.7008 | 153.9867 | 178.6784 | 175.9418 | NaN | NaN | NaN | 622.9013 | 127.9914 | NaN | NaN | 522.7964 | NaN | NaN | NaN | NaN | 881.0736 | 566.7197 | NaN | 25.0597 | NaN | 32.4719
8074.1292 | 228.2829 | 127.0737 | 129.4522 | 128.6154 | 138.4306 | 155.2192 | 179.651 | 176.3043 | NaN | NaN | NaN | 612.3078 | 123.9894 | NaN | NaN | 514.381 | NaN | NaN | NaN | NaN | 880.2 | 574.7807 | NaN | 20.1933 | NaN | 32.6909
8075.1292 | 228.906 | 127.0393 | 129.2103 | 128.5913 | 138.1993 | 154.9056 | 179.6992 | 177.6214 | NaN | NaN | NaN | 608.7575 | 122.6358 | NaN | NaN | 509.5182 | NaN | NaN | NaN | NaN | 883.2074 | 585.6891 | NaN | 7.2196 | NaN | 31.8699
8076.1292 | 229.3876 | 127.1782 | 128.8914 | 128.4928 | 138.5696 | 154.9252 | 179.5731 | 177.3918 | NaN | NaN | NaN | 615.0052 | 123.4865 | NaN | NaN | 500.9969 | NaN | NaN | NaN | NaN | 879.4819 | 593.993 | NaN | 16.039 | NaN | 28.071
8077.1292 | 228.3706 | 127.7086 | 129.6279 | 128.3967 | 138.5439 | 154.6562 | 181.4692 | 177.9753 | NaN | NaN | NaN | 619.8007 | 118.4697 | NaN | NaN | 495.2355 | NaN | NaN | NaN | NaN | 880.9528 | 604.6037 | NaN | 10.2351 | NaN | 19.4573
8078.1292 | 227.3145 | 127.8393 | 130.043 | 128.2248 | 138.5463 | 155.3851 | 181.5262 | 176.9607 | NaN | NaN | NaN | 626.7867 | 119.2894 | NaN | NaN | 487.4084 | NaN | NaN | NaN | NaN | 878.2006 | 618.6487 | NaN | 21.0751 | NaN | 32.3782
8079.1292 | 227.6358 | 128.1924 | 130.0886 | 127.9262 | 138.3927 | 155.2221 | 182.3469 | 176.5376 | NaN | NaN | NaN | 631.3035 | 123.2165 | NaN | NaN | 482.7077 | NaN | NaN | NaN | NaN | 881.2982 | 632.0472 | NaN | 6.3204 | NaN | 28.4804
8080.1292 | 227.0988 | 128.4024 | 130.1959 | 128.4394 | 138.6042 | 155.4212 | 182.2809 | 177.4288 | NaN | NaN | NaN | 626.0473 | 124.0892 | NaN | NaN | 473.5389 | NaN | NaN | NaN | NaN | 878.3679 | 645.0664 | NaN | 7.7995 | NaN | 24.2779
8081.1292 | 227.1882 | 128.5703 | 130.114 | 128.7252 | 138.6119 | 155.3105 | 182.1023 | 177.0339 | NaN | NaN | NaN | 632.719 | 125.1749 | NaN | NaN | 468.7102 | NaN | NaN | NaN | NaN | 879.2484 | 657.9053 | NaN | 14.9937 | NaN | 30.7114
8082.1292 | 226.2556 | 128.3921 | 130.6094 | 128.8422 | 138.3987 | 154.523 | 182.0024 | 178.5463 | NaN | NaN | NaN | 628.6321 | 121.8693 | NaN | NaN | 458.0441 | NaN | NaN | NaN | NaN | 875.9163 | 672.1942 | NaN | 18.636 | NaN | 27.2287
8083.1292 | 226.049 | 128.9038 | 130.4137 | 129.0472 | 138.5429 | 154.4211 | 183.0338 | 180.5618 | NaN | NaN | NaN | 619.5109 | 124.1125 | NaN | NaN | 452.6666 | NaN | NaN | NaN | NaN | 877.2911 | 682.7003 | NaN | 16.4031 | NaN | 18.5253
8084.1292 | 225.596 | 128.4445 | 130.4939 | 129.0723 | 138.793 | 155.3143 | 183.8365 | 181.5895 | NaN | NaN | NaN | 603.1061 | 125.0033 | NaN | NaN | 443.2917 | NaN | NaN | NaN | NaN | 873.4137 | 686.7621 | NaN | 17.666 | NaN | 20.2744
8085.1292 | 224.8195 | 128.6475 | 130.7279 | 129.2313 | 139.3659 | 155.9995 | 185.0257 | 181.0797 | NaN | NaN | NaN | 593.7058 | 122.1515 | NaN | NaN | 436.6332 | NaN | NaN | NaN | NaN | 873.2292 | 695.9238 | NaN | 16.9423 | NaN | 31.2146
8086.1292 | 224.2147 | 128.4232 | 130.6258 | 129.4488 | 139.4456 | 156.4258 | 184.1958 | 180.1112 | NaN | NaN | NaN | 585.3552 | 123.3543 | NaN | NaN | 428.2811 | NaN | NaN | NaN | NaN | 871.3307 | 709.0075 | NaN | 26.078 | NaN | 21.7085
8087.1292 | 224.0454 | 128.4077 | 130.8779 | 129.3964 | 139.2611 | 156.4081 | 184.6883 | 179.8561 | NaN | NaN | NaN | 570.7047 | 125.729 | NaN | NaN | 422.2171 | NaN | NaN | NaN | NaN | 870.4194 | 721.4825 | NaN | 8.4785 | NaN | 30.8476
8088.1292 | 224.8669 | 129.1877 | 130.8091 | 129.3661 | 139.3812 | 156.7805 | 185.0503 | 179.8727 | NaN | NaN | NaN | 557.7328 | 123.5412 | NaN | NaN | 414.1253 | NaN | NaN | NaN | NaN | 868.5316 | 743.0096 | NaN | 21.5669 | NaN | 29.1586
8089.1292 | 226.515 | 129.1843 | 130.4243 | 129.6923 | 139.3618 | 156.5267 | 184.9302 | 180.7782 | NaN | NaN | NaN | 541.9803 | 121.1145 | NaN | NaN | 406.6338 | NaN | NaN | NaN | NaN | 866.9649 | 760.5073 | NaN | 14.7085 | NaN | 30.455
8090.1448 | 226.7878 | 129.8991 | 130.7463 | 129.9561 | 139.5721 | 157.1021 | 184.7053 | 181.0679 | NaN | NaN | NaN | 524.5882 | 122.9685 | NaN | NaN | 399.7136 | NaN | NaN | NaN | NaN | 866.222 | 771.6526 | NaN | 15.028 | NaN | 32.4322
8091.1292 | 226.4792 | 130.3599 | 131.1191 | 130.2863 | 140.0631 | 156.605 | 183.9947 | 180.9179 | NaN | NaN | NaN | 510.3793 | 126.9547 | NaN | NaN | 392.7179 | NaN | NaN | NaN | NaN | 863.29 | 777.2953 | NaN | 17.2566 | NaN | 30.3891
8092.1292 | 227.0473 | 130.6583 | 130.9146 | 130.2474 | 140.7938 | 155.7004 | 185.1619 | 181.715 | NaN | NaN | NaN | 520.6454 | 119.228 | NaN | NaN | 393.1013 | NaN | NaN | NaN | NaN | 871.5653 | 790.7702 | NaN | 22.3269 | NaN | 21.9996
8093.1292 | 226.0968 | 130.9209 | 130.9376 | 130.3922 | 140.8424 | 155.8524 | 184.7488 | 181.5299 | NaN | NaN | NaN | 513.05 | 123.4645 | NaN | NaN | 382.3604 | NaN | NaN | NaN | NaN | 865.2021 | 812.1709 | NaN | 8.2966 | NaN | 29.2886
8094.1292 | 226.5138 | 131.285 | 131.5385 | 130.8751 | 141.3488 | 154.5139 | 183.8632 | 180.6077 | NaN | NaN | NaN | 498.5031 | 124.6817 | NaN | NaN | 373.1739 | NaN | NaN | NaN | NaN | 861.1242 | 828.1725 | NaN | 19.076 | NaN | 30.1328
8095.1292 | 225.4948 | 131.6555 | 131.5495 | 130.9751 | 141.1092 | 153.8134 | 183.0149 | 180.1641 | NaN | NaN | NaN | 492.39 | 121.4038 | NaN | NaN | 365.373 | NaN | NaN | NaN | NaN | 858.7728 | 847.1599 | NaN | 16.2842 | NaN | 26.645
8096.1292 | 226.3324 | 131.7339 | 131.8155 | 131.8336 | 140.9183 | 153.6694 | 182.2843 | 180.9745 | NaN | NaN | NaN | 502.2987 | 118.4943 | NaN | NaN | 360.5542 | NaN | NaN | NaN | NaN | 860.9052 | 858.9512 | NaN | 6.6326 | NaN | 13.0743
8097.1292 | 228.8993 | 132.2375 | 131.7906 | 131.7392 | 141.1279 | 153.9743 | 182.8208 | 182.5684 | NaN | NaN | NaN | 522.1285 | 125.2724 | NaN | NaN | 356.8445 | NaN | NaN | NaN | NaN | 862.6883 | 872.3479 | NaN | 11.786 | NaN | 29.7138
8098.1292 | 229.0231 | 132.3824 | 132.2954 | 132.5042 | 141.3365 | 154.0895 | 182.7626 | 184.0875 | NaN | NaN | NaN | 509.5511 | 121.1647 | NaN | NaN | 344.6605 | NaN | NaN | NaN | NaN | 854.0716 | 891.41 | NaN | 8.2241 | NaN | 23.9664
8099.1292 | 232.9637 | 132.9893 | 132.1452 | 133.5793 | 141.4421 | 154.4022 | 182.9859 | 184.5902 | NaN | NaN | NaN | 517.6055 | 125.5659 | NaN | NaN | 335.5862 | NaN | NaN | NaN | NaN | 849.7523 | 909.4084 | NaN | 20.8536 | NaN | 34.0036
8100.1292 | 233.406 | 133.2288 | 132.4724 | 133.5352 | 141.4646 | 154.6373 | 184.2985 | 185.5948 | NaN | NaN | NaN | 533.3407 | 120.912 | NaN | NaN | 330.7363 | NaN | NaN | NaN | NaN | 850.6436 | 918.4239 | NaN | 22.8636 | NaN | 21.5958
8101.1292 | 236.3033 | 133.898 | 132.9815 | 133.2322 | 141.7827 | 153.8531 | 184.7972 | 187.2704 | NaN | NaN | NaN | 546.2499 | 121.9811 | NaN | NaN | 324.3011 | NaN | NaN | NaN | NaN | 850.2617 | 926.4969 | NaN | 21.7673 | NaN | 31.1478
8102.1292 | 239.6531 | 133.9663 | 133.6481 | 133.5236 | 141.7365 | 152.6581 | 184.655 | 188.6635 | NaN | NaN | NaN | 544.7978 | 123.5389 | NaN | NaN | 315.3474 | NaN | NaN | NaN | NaN | 846.0072 | 938.7751 | NaN | 14.9247 | NaN | 21.0756
8103.1292 | 239.1702 | 134.816 | 133.9378 | 133.8513 | 142.0341 | 152.5783 | 185.3576 | 188.9162 | NaN | NaN | NaN | 545.9601 | 124.2702 | NaN | NaN | 308.5546 | NaN | NaN | NaN | NaN | 844.7366 | 949.2781 | NaN | 26.3016 | NaN | 23.7586
8104.1292 | 242.054 | 134.94 | 134.164 | 134.8042 | 142.536 | 153.5236 | 186.3484 | 192.8039 | NaN | NaN | NaN | 550.8394 | 122.7115 | NaN | NaN | 300.6659 | NaN | NaN | NaN | NaN | 842.7615 | 956.6806 | NaN | 2.9802 | NaN | 32.5895
8105.1292 | 244.172 | 135.1707 | 134.9982 | 134.9244 | 142.6357 | 153.7807 | 186.3157 | 193.1237 | NaN | NaN | NaN | 552.453 | 123.9468 | NaN | NaN | 293.4559 | NaN | NaN | NaN | NaN | 842.2927 | 962.8902 | NaN | 13.3491 | NaN | 31.1944
8106.1292 | 246.5182 | 135.7998 | 134.7891 | 135.0301 | 143.0848 | 155.3951 | 188.0926 | 192.8556 | NaN | NaN | NaN | 555.5554 | 120.1236 | NaN | NaN | 286.642 | NaN | NaN | NaN | NaN | 840.8081 | 975.1321 | NaN | 7.6491 | NaN | 19.1449
8107.1292 | 249.9901 | 136.6739 | 135.1034 | 135.3422 | 143.5778 | 155.4375 | 188.8387 | 193.1378 | NaN | NaN | NaN | 571.0081 | 124.6062 | NaN | NaN | 282.0306 | NaN | NaN | NaN | NaN | 840.5416 | 988.0443 | NaN | 11.7252 | NaN | 17.269
8108.1292 | 249.8197 | 137.6291 | 135.8563 | 135.9758 | 144.0546 | 157.104 | 189.2038 | 194.7475 | NaN | NaN | NaN | 573.3291 | 120.5011 | NaN | NaN | 275.0223 | NaN | NaN | NaN | NaN | 839.3321 | 996.8514 | NaN | 19.7591 | NaN | 17.1667
8109.1292 | 251.1725 | 138.0949 | 136.1628 | 136.8006 | 144.9144 | 157.6844 | 189.4668 | 193.0167 | NaN | NaN | NaN | 567.0192 | 121.9088 | NaN | NaN | 266.9429 | NaN | NaN | NaN | NaN | 837.6405 | 1003.6898 | NaN | 25.1139 | NaN | 32.5886
8110.1292 | 252.4966 | 138.7047 | 136.2451 | 137.0334 | 145.0021 | 158.6151 | 189.7832 | 193.6461 | NaN | NaN | NaN | 571.8998 | 120.9096 | NaN | NaN | 262.3924 | NaN | NaN | NaN | NaN | 839.3432 | 1011.4598 | NaN | 16.8077 | NaN | 24.0089
8111.1292 | 255.721 | 139.4018 | 136.2297 | 137.1118 | 145.2389 | 157.6077 | 190.0367 | 192.2217 | NaN | NaN | NaN | 577.4168 | 116.957 | NaN | NaN | 261.0337 | NaN | NaN | NaN | NaN | 843.3956 | 1018.8878 | NaN | 19.1721 | NaN | 30.8205
8112.1292 | 256.5393 | 140.009 | 136.9227 | 137.3178 | 145.8281 | 157.7143 | 190.5939 | 191.1698 | NaN | NaN | NaN | 576.5596 | 119.1847 | NaN | NaN | 257.5824 | NaN | NaN | NaN | NaN | 843.9827 | 1029.0333 | NaN | 14.1764 | NaN | 19.261
8113.1292 | 255.9738 | 140.6256 | 136.6409 | 137.6413 | 146.2219 | 157.614 | 190.3533 | 190.7674 | NaN | NaN | NaN | 590.044 | 120.2848 | NaN | NaN | 253.7068 | NaN | NaN | NaN | NaN | 844.2539 | 1034.3387 | NaN | 26.3607 | NaN | 30.1044
8114.1292 | 258.4925 | 140.9513 | 137.0823 | 137.8005 | 146.4152 | 158.1493 | 190.9453 | 190.9727 | NaN | NaN | NaN | 603.9242 | 118.7973 | NaN | NaN | 250.4636 | NaN | NaN | NaN | NaN | 846.6006 | 1037.6055 | NaN | 25.3078 | NaN | 29.9295
8115.1292 | 259.6123 | 140.8603 | 136.5471 | 137.701 | 146.9858 | 159.3077 | 191.32 | 191.7282 | NaN | NaN | NaN | 608.1747 | 123.3657 | NaN | NaN | 247.973 | 1371.1325 | NaN | NaN | NaN | 847.7786 | 1044.0646 | NaN | 12.8764 | NaN | 24.072
8116.1292 | 260.8999 | 141.2379 | 136.9769 | 137.9784 | 147.0738 | 158.6582 | 192.3115 | 190.94 | NaN | NaN | NaN | 612.1328 | 113.5473 | NaN | NaN | 247.3298 | 1368.975 | NaN | NaN | NaN | 852.2182 | 1062.4774 | NaN | 25.796 | NaN | 21.412
8117.1292 | 260.5919 | 141.8764 | 136.8029 | 137.8326 | 146.9798 | 158.5075 | 192.2235 | 190.3355 | NaN | NaN | NaN | 623.0592 | 121.6429 | NaN | NaN | 242.6087 | 1325.6262 | NaN | NaN | NaN | 850.4407 | 1073.4498 | NaN | 18.3033 | NaN | 26.1798
8118.1292 | 260.3509 | 142.485 | 137.1082 | 138.4221 | 147.5502 | 158.5317 | 193.7488 | 189.999 | NaN | NaN | NaN | 629.4342 | 115.3282 | NaN | NaN | 239.3439 | 1299.7456 | NaN | NaN | NaN | 853.7225 | 1084.2413 | NaN | 15.3073 | NaN | 28.3402
8119.1292 | 259.7403 | 142.6339 | 137.1621 | 139.038 | 148.0619 | 158.3115 | 195.2616 | 189.899 | NaN | NaN | NaN | 631.063 | 117.8882 | NaN | NaN | 236.8818 | 1273.7526 | NaN | NaN | NaN | 854.9909 | 1094.9196 | NaN | 15.7258 | NaN | 30.6672
8120.1292 | 261.5125 | 142.7455 | 137.8281 | 139.4777 | 148.2427 | 158.9124 | 194.8304 | 189.8674 | NaN | NaN | NaN | 629.7619 | 114.0805 | NaN | NaN | 233.0225 | 1209.4314 | NaN | NaN | NaN | 856.6611 | 1113.5089 | NaN | 4.0004 | NaN | 28.7017
8121.1292 | 258.8964 | 143.0743 | 138.1361 | 139.1933 | 148.0693 | 159.2901 | 194.5655 | 189.9792 | NaN | NaN | NaN | 620.4703 | 116.0728 | NaN | NaN | 226.8724 | 1106.2872 | NaN | NaN | NaN | 854.802 | 1127.4361 | NaN | 24.9906 | NaN | 23.9805
8122.1292 | 258.3462 | 143.3668 | 138.2942 | 139.5856 | 148.523 | 159.1156 | 194.8578 | 192.5238 | NaN | NaN | NaN | 613.2054 | 120.9603 | NaN | NaN | 217.3852 | 984.3014 | NaN | NaN | NaN | 850.7961 | 1140.127 | NaN | 21.948 | NaN | 30.1585
8123.1292 | 257.1811 | 143.3093 | 139.0596 | 140.019 | 148.5655 | 159.9948 | 194.6386 | 194.5524 | NaN | NaN | NaN | 618.9173 | 121.4583 | NaN | NaN | 211.1818 | 899.0842 | NaN | NaN | NaN | 849.3833 | 1146.6553 | NaN | 18.3888 | NaN | 23.6271
8124.1292 | 257.5133 | 143.4453 | 139.4592 | 139.8017 | 148.5744 | 162.0791 | 196.0535 | 195.9085 | NaN | NaN | NaN | 623.0694 | 121.7345 | NaN | NaN | 204.9094 | 827.8916 | NaN | NaN | NaN | 849.4067 | 1157.2985 | NaN | 17.4036 | NaN | 30.2756
8125.1292 | 255.9671 | 143.4277 | 139.7559 | 139.7757 | 148.2906 | 161.3208 | 195.7204 | 195.5458 | NaN | NaN | NaN | 614.2015 | 123.522 | NaN | NaN | 196.6857 | 710.6407 | NaN | NaN | NaN | 847.4518 | 1160.106 | NaN | 26.0648 | NaN | 28.7576
8126.1292 | 256.0642 | 143.5775 | 140.5869 | 140.3103 | 148.4673 | 160.2606 | 195.2963 | 195.089 | NaN | NaN | NaN | 603.5926 | 121.361 | NaN | NaN | 188.6261 | 613.5522 | NaN | NaN | NaN | 844.8194 | 1167.8981 | NaN | 13.4316 | NaN | 32.3108
8127.1292 | 256.7756 | 144.0453 | 140.8385 | 140.1334 | 148.9129 | 160.4767 | 195.0674 | 194.6063 | NaN | NaN | NaN | 595.9022 | 122.6906 | NaN | NaN | 180.4924 | 541.3882 | NaN | NaN | NaN | 843.4113 | 1175.0188 | NaN | 20.8325 | NaN | 25.7941
8128.1292 | 255.7411 | 143.8834 | 140.5716 | 140.7249 | 148.7764 | 160.83 | 194.4097 | 194.0796 | NaN | NaN | NaN | 590.7698 | 117.6163 | NaN | NaN | 172.5805 | 481.6908 | NaN | NaN | NaN | 842.3584 | 1183.3645 | NaN | 9.7933 | NaN | 17.8394
8129.1292 | 256.2792 | 144.1474 | 140.7828 | 140.826 | 148.8544 | 163.5573 | 196.1612 | 194.9656 | NaN | NaN | NaN | 578.191 | 123.5823 | NaN | NaN | 164.5144 | 433.6192 | NaN | NaN | NaN | 839.8204 | 1196.9309 | NaN | 13.8371 | NaN | 22.7352
8130.1292 | 257.5003 | 144.5398 | 140.6364 | 140.6928 | 149.2249 | 162.7978 | 197.3852 | 194.9933 | NaN | NaN | NaN | 579.1683 | 118.3351 | NaN | NaN | 154.0581 | 350.5584 | NaN | NaN | NaN | 836.5891 | 1207.3648 | NaN | 15.8887 | NaN | 28.7063
8131.1292 | 255.3158 | 144.9413 | 141.2601 | 140.7485 | 149.3723 | 163.1434 | 198.495 | 195.0289 | NaN | NaN | NaN | 575.3845 | 123.436 | NaN | NaN | 144.873 | 312.5568 | NaN | NaN | NaN | 836.3028 | 1218.4394 | NaN | 20.1489 | NaN | 26.4662
8132.1292 | 255.7266 | 144.7613 | 141.3014 | 141.2948 | 149.1563 | 162.9523 | 198.3326 | 195.2606 | NaN | NaN | NaN | 569.4176 | 115.8831 | NaN | NaN | 129.1552 | 246.3007 | NaN | NaN | NaN | 834.0655 | 1239.127 | NaN | 15.4375 | NaN | 19.8622
8133.1292 | 252.9794 | 144.8457 | 140.7377 | 141.1102 | 149.6611 | 163.8156 | 198.6491 | 196.1339 | NaN | NaN | NaN | 552.7475 | 117.5903 | NaN | NaN | 87.062 | 131.9097 | NaN | NaN | NaN | 828.5057 | 1254.2933 | NaN | 9.4663 | NaN | 25.2225
8134.1292 | 254.5533 | 144.4958 | 141.0561 | 140.7674 | 149.5249 | 164.0965 | 198.3176 | 198.6832 | NaN | NaN | NaN | 544.4426 | 123.6735 | NaN | NaN | 16.6429 | 109.51 | NaN | NaN | NaN | 825.0613 | 1254.2928 | NaN | 9.3142 | NaN | 28.28
8135.1292 | 253.929 | 144.7675 | 141.3404 | 140.7946 | 149.6098 | 163.2959 | 198.1338 | 199.5214 | NaN | NaN | NaN | 550.8858 | 126.6132 | NaN | NaN | 35.8284 | 125.3005 | NaN | NaN | NaN | 827.6202 | 1254.292 | NaN | 9.5122 | NaN | 14.9359
8136.1292 | 254.2589 | 145.1295 | 141.7085 | 141.6549 | 150.2584 | 165.033 | 197.7512 | 200.2754 | NaN | NaN | NaN | 534.011 | 120.0224 | NaN | NaN | 5.4291 | 90.6839 | NaN | NaN | NaN | 822.4926 | 1254.2911 | NaN | 10.9286 | NaN | 27.7074
8137.1292 | 254.2358 | 146.4768 | 141.3975 | 141.7689 | 150.7737 | 164.4746 | 198.1874 | 201.4104 | NaN | NaN | NaN | 521.0924 | 122.5321 | NaN | NaN | NaN | 89.291 | NaN | NaN | NaN | 819.6549 | 1254.2919 | NaN | 24.3194 | NaN | 19.1091
8138.1292 | 256.2497 | 146.5086 | 141.4485 | 142.0045 | 151.1682 | 166.2379 | 198.9924 | 204.0649 | NaN | NaN | NaN | 534.6504 | 123.0188 | NaN | NaN | NaN | 73.1275 | NaN | NaN | NaN | 817.8811 | 1254.2904 | NaN | 8.6357 | NaN | 21.5732
8139.1292 | 258.3055 | 147.2562 | 142.5417 | 142.7197 | 151.4913 | 168.4732 | 200.4581 | 205.7512 | NaN | NaN | NaN | 523.0015 | 122.5219 | NaN | NaN | NaN | 67.5789 | NaN | NaN | NaN | 816.5942 | 1254.2896 | NaN | 20.8887 | NaN | 30.0202
8140.1292 | 257.4342 | 147.4818 | 142.5325 | 143.077 | 152.47 | 167.749 | 201.2182 | 203.9768 | NaN | NaN | NaN | 524.5438 | 118.7896 | NaN | NaN | NaN | 51.2822 | NaN | NaN | NaN | 815.9953 | 1254.2889 | NaN | 19.5973 | NaN | 20.5071
8141.1292 | 257.0394 | 147.653 | 142.9213 | 143.1397 | 152.8269 | 167.9965 | 201.2129 | 203.3951 | NaN | NaN | NaN | 546.6925 | 121.4142 | NaN | NaN | NaN | 47.5353 | NaN | NaN | NaN | 815.8173 | 1254.2877 | NaN | 16.182 | NaN | 24.869
8142.1292 | 255.758 | 147.7218 | 143.1902 | 143.2077 | 153.0197 | 168.4786 | 201.6889 | 203.9221 | NaN | NaN | NaN | 540.2393 | 122.0315 | NaN | NaN | 8.857 | 12.6413 | NaN | NaN | NaN | 809.422 | 1254.2869 | NaN | 20.5027 | NaN | 27.2142
8143.1292 | 256.031 | 147.4397 | 143.8644 | 143.8739 | 153.2322 | 168.6632 | 200.3912 | 203.014 | NaN | NaN | NaN | 552.4492 | 121.163 | NaN | NaN | 46.4206 | 9.5344 | NaN | NaN | NaN | 810.6381 | 1254.2868 | NaN | 22.7975 | NaN | 23.7408
8144.1448 | 258.3624 | 147.7963 | 144.0551 | 144.2885 | 153.471 | 169.652 | 200.134 | 203.5049 | NaN | NaN | NaN | 535.4161 | 122.9713 | NaN | NaN | 30.059 | -3.3953 | NaN | NaN | NaN | 806.9265 | 1254.2863 | NaN | 13.5428 | NaN | 28.0226
8145.1292 | 259.3857 | 147.6912 | 144.0501 | 144.4043 | 153.5993 | 168.4728 | 200.1406 | 204.06 | NaN | NaN | NaN | 520.5719 | 122.5947 | NaN | NaN | -11.5841 | -17.8306 | NaN | NaN | NaN | 803.0027 | 1254.2852 | NaN | 8.8741 | NaN | 30.4343
8146.1292 | 260.7093 | 147.6199 | 144.4826 | 144.2884 | 153.7625 | 168.5144 | 200.4374 | 204.6482 | NaN | NaN | NaN | 505.7998 | 126.2153 | NaN | NaN | 29.13 | -17.7696 | NaN | NaN | NaN | 802.0907 | 1254.2849 | NaN | 13.3922 | NaN | 22.8396
8147.1292 | 267.204 | 147.5196 | 145.1309 | 144.6618 | 153.8752 | 170.0084 | 201.7743 | 204.167 | NaN | NaN | NaN | 492.1811 | 121.5824 | NaN | NaN | 39.3985 | NaN | NaN | NaN | NaN | 797.4305 | 1254.2844 | NaN | 11.7941 | NaN | 20.0987
8148.1292 | 268.9529 | 148.0698 | 144.7658 | 145.2011 | 154.1607 | 169.3509 | 202.1729 | 204.9896 | NaN | NaN | NaN | 479.7132 | 120.8672 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 797.0171 | 1254.2836 | NaN | 22.596 | NaN | 29.792
8149.1292 | 271.0681 | 149.129 | 144.5202 | 145.0508 | 154.4541 | 168.5114 | 203.7777 | 206.2 | NaN | NaN | NaN | 467.9337 | 116.0883 | NaN | NaN | 10.4895 | NaN | NaN | NaN | NaN | 794.4042 | 1254.2812 | NaN | 28.399 | NaN | 28.4055
8150.1292 | 270.8785 | 149.6197 | 144.9445 | 145.014 | 154.5869 | 168.3509 | 204.7537 | 207.3819 | NaN | NaN | NaN | 459.7316 | 113.2378 | NaN | NaN | 39.1854 | NaN | NaN | NaN | NaN | 793.251 | 1254.2813 | NaN | 25.7947 | NaN | 28.098
8151.1292 | 272.4046 | 149.7265 | 145.3907 | 145.0459 | 154.5591 | 170.5418 | 204.7144 | 207.2376 | NaN | NaN | NaN | 458.3314 | 115.914 | NaN | NaN | 34.4026 | NaN | NaN | NaN | NaN | 791.0091 | 1254.2824 | NaN | 21.3637 | NaN | 19.5144
8152.1292 | 274.223 | 150.9003 | 145.6731 | 145.1295 | 154.605 | 171.8175 | 205.0697 | 210.4115 | NaN | NaN | NaN | 450.7852 | 117.5168 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 789.4502 | 1254.2814 | NaN | 20.6011 | NaN | 28.0077
8153.1292 | 276.9775 | 151.824 | 145.9965 | 145.545 | 154.8049 | 170.8555 | 204.6068 | 210.73 | NaN | NaN | NaN | 446.3834 | 114.8783 | NaN | NaN | -16.7361 | NaN | NaN | NaN | NaN | 786.4295 | 1254.2795 | NaN | 21.6392 | NaN | 19.1109
8154.1292 | 276.5528 | 152.2727 | 145.9216 | 145.8294 | 155.0544 | 171.0274 | 204.5022 | 209.9582 | NaN | NaN | NaN | 446.0326 | 123.914 | NaN | NaN | 50.4067 | NaN | NaN | NaN | NaN | 783.4296 | 1254.2792 | NaN | 14.3115 | NaN | 27.8015
8155.1292 | 276.5298 | 152.5 | 146.0048 | 146.6187 | 155.5826 | 170.3225 | 203.8832 | 210.4554 | NaN | NaN | NaN | 442.8305 | 123.9809 | NaN | NaN | 8.2919 | NaN | NaN | NaN | NaN | 779.6017 | 1254.28 | NaN | 8.7296 | NaN | 27.1044
8156.1292 | 276.1972 | 152.3363 | 146.2436 | 146.9544 | 155.5271 | 171.3457 | 203.7972 | 211.1832 | NaN | NaN | NaN | 441.5265 | 122.4062 | NaN | NaN | 26.304 | NaN | NaN | NaN | NaN | 776.6985 | 1254.2787 | NaN | 16.6918 | NaN | 27.2565
8157.1292 | 275.7427 | 151.9537 | 146.0898 | 147.1441 | 155.6722 | 171.3243 | 204.0379 | 211.0715 | NaN | NaN | NaN | 446.9707 | 125.7704 | NaN | NaN | -6.7704 | NaN | NaN | NaN | NaN | 776.4739 | 1254.2775 | NaN | 22.4708 | NaN | 34.1556
8158.1292 | 276.8225 | 152.0161 | 145.9295 | 147.2286 | 155.6383 | 172.3937 | 205.7227 | 211.7977 | NaN | NaN | NaN | 450.0536 | 129.9354 | NaN | NaN | 37.3107 | NaN | NaN | NaN | NaN | 773.9782 | 1254.2775 | NaN | 9.5838 | NaN | 17.6736
8159.1292 | 275.0674 | 152.2195 | 146.5604 | 147.9388 | 155.2127 | 172.9899 | 206.222 | 212.5497 | NaN | NaN | NaN | 456.124 | 128.8732 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 773.3902 | 1254.2759 | NaN | 1.6489 | NaN | 29.1119
8160.1292 | 276.1612 | 152.4363 | 146.4153 | 147.6735 | 155.457 | 172.2333 | 206.1301 | 211.5661 | NaN | NaN | NaN | 454.5769 | 127.9369 | NaN | NaN | 29.692 | NaN | NaN | NaN | NaN | 768.5821 | 1254.2768 | NaN | 26.3135 | NaN | 16.7394
8161.1292 | 274.4568 | 152.9387 | 146.4314 | 147.8681 | 155.3493 | 172.5778 | 206.4231 | 210.7237 | NaN | NaN | NaN | 462.5913 | 128.7129 | NaN | NaN | 27.1366 | NaN | NaN | NaN | NaN | 769.7914 | 1254.2756 | NaN | 15.9345 | NaN | 14.3367
8162.1292 | 276.8033 | 153.1145 | 146.4263 | 148.7852 | 155.9692 | 172.6435 | 205.8354 | 211.3099 | NaN | NaN | NaN | 470.4354 | 129.4175 | NaN | NaN | 44.1625 | NaN | NaN | NaN | NaN | 770.7146 | 1254.2743 | NaN | 22.6913 | NaN | 19.4225
8163.1292 | 278.1766 | 153.5302 | 146.8363 | 148.5526 | 155.9622 | 172.4368 | 205.3715 | 211.1385 | NaN | NaN | NaN | 484.9358 | 131.9702 | NaN | NaN | 25.801 | NaN | NaN | NaN | NaN | 766.8876 | 1254.2734 | NaN | 9.736 | NaN | 20.7485
8164.1292 | 277.2251 | 153.8979 | 148.043 | 148.685 | 156.2829 | 171.6394 | 205.7425 | 210.767 | NaN | NaN | NaN | 473.8852 | 121.28 | NaN | NaN | 6.6186 | NaN | NaN | NaN | NaN | 760.4584 | 1254.2737 | NaN | 7.4806 | NaN | 15.584
8165.1292 | 276.3443 | 154.9647 | 147.8264 | 149.4659 | 156.7062 | 171.1032 | 204.796 | 209.9147 | NaN | NaN | NaN | 470.5846 | 123.1509 | NaN | NaN | 53.8757 | NaN | NaN | NaN | NaN | 755.5381 | 1254.2725 | NaN | 20.5588 | NaN | 20.1793
8166.1292 | 276.9167 | 155.0785 | 148.0796 | 149.7146 | 156.8373 | 170.9594 | 205.7619 | 210.2848 | NaN | NaN | NaN | 488.1333 | 124.9704 | NaN | NaN | 69.8525 | NaN | NaN | NaN | NaN | 756.0333 | 1254.2722 | NaN | 11.5536 | NaN | 28.6424
8167.1292 | 278.9867 | 155.595 | 148.3156 | 149.9266 | 157.3548 | 170.2458 | 204.7902 | 210.4464 | NaN | NaN | NaN | 477.6478 | 129.1046 | NaN | NaN | 49.2358 | NaN | NaN | NaN | NaN | 750.8189 | 1254.2717 | NaN | 21.9712 | NaN | 17.7364
8168.1292 | 278.8724 | 156.3211 | 148.3151 | 150.0094 | 157.3446 | 171.5038 | 206.5114 | 211.0112 | NaN | NaN | NaN | 498.28 | 131.3967 | NaN | NaN | 25.5587 | NaN | NaN | NaN | NaN | 753.4468 | 1254.2717 | NaN | 13.073 | NaN | 12.2985
8169.1292 | 279.4953 | 156.9833 | 148.8443 | 150.3725 | 157.3916 | 172.2438 | 206.5583 | 210.9298 | NaN | NaN | NaN | 517.7278 | 123.9177 | NaN | NaN | 47.4659 | NaN | NaN | NaN | NaN | 747.5721 | 1254.2711 | NaN | 9.4596 | NaN | 16.6007
8170.1292 | 279.4933 | 157.1218 | 149.3307 | 151.2455 | 158.3474 | 172.6505 | 206.3612 | 211.4565 | NaN | NaN | NaN | 522.974 | 123.5997 | NaN | NaN | 37.4028 | NaN | NaN | NaN | NaN | 744.2467 | 1254.2704 | NaN | 24.9868 | NaN | 11.6397
8171.1292 | 279.8027 | 156.6708 | 149.4914 | 151.2909 | 158.7597 | 172.2681 | 206.7688 | 211.5235 | NaN | NaN | NaN | 538.1041 | 129.5031 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 744.7112 | 1254.269 | NaN | 14.5581 | NaN | 30.7928
8172.1292 | 281.0989 | 155.6927 | 149.9113 | 151.4094 | 158.9944 | 172.416 | 206.6007 | 210.1152 | NaN | NaN | NaN | 546.9277 | 122.5915 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 739.8144 | 1254.269 | NaN | 10.2097 | NaN | 32.1144
8173.1292 | 279.0473 | 154.8338 | 149.8218 | 150.9864 | 159.0609 | 172.9348 | 206.4678 | 208.6359 | NaN | NaN | NaN | 547.4793 | 132.042 | NaN | NaN | -13.1265 | NaN | NaN | NaN | NaN | 735.3259 | 1254.269 | NaN | 16.6841 | NaN | 14.7858
8174.1292 | 282.7861 | 153.9547 | 149.9787 | 151.4751 | 159.4243 | 173.4637 | 205.7898 | 206.6038 | NaN | NaN | NaN | 545.3108 | 123.9601 | NaN | NaN | 51.8541 | NaN | NaN | NaN | NaN | 731.4131 | 1254.2688 | NaN | 15.0357 | NaN | 11.5473
8175.1292 | 281.0696 | 153.8017 | 149.7617 | 151.6161 | 159.453 | 172.9601 | 205.8803 | 205.3487 | NaN | NaN | NaN | 544.1764 | 128.5745 | NaN | NaN | 45.8931 | NaN | NaN | NaN | NaN | 728.9643 | 1254.2669 | NaN | 18.3306 | NaN | 26.6555
8176.1292 | 280.5262 | 154.0224 | 149.6768 | 151.3006 | 159.2468 | 173.7549 | 206.7447 | 206.0712 | NaN | NaN | NaN | 535.4067 | 127.9652 | NaN | NaN | 16.5556 | NaN | NaN | NaN | NaN | 724.8794 | 1254.2682 | NaN | 3.8329 | NaN | 21.5507
8177.1292 | 280.3419 | 154.0211 | 150.0734 | 151.2042 | 158.8009 | 173.488 | 207.3416 | 206.2504 | NaN | NaN | NaN | 518.9525 | 128.7325 | NaN | NaN | 29.7508 | NaN | NaN | NaN | NaN | 722.0992 | 1254.2661 | NaN | 6.7037 | NaN | 27.7707
8178.1292 | 279.6378 | 154.669 | 149.7247 | 151.4239 | 158.6545 | 174.6343 | 208.237 | 206.3308 | NaN | NaN | NaN | 528.5925 | 123.9156 | NaN | NaN | 14.3957 | -17.3412 | NaN | NaN | NaN | 721.9352 | 1254.2661 | NaN | 11.7544 | NaN | 29.115
8179.1292 | 280.0934 | 154.9921 | 149.2908 | 151.6722 | 158.4372 | 174.0075 | 208.0912 | 207.2616 | NaN | NaN | NaN | 544.4867 | 135.857 | NaN | NaN | NaN | 9.7602 | NaN | NaN | NaN | 726.3648 | 1254.2652 | NaN | 22.813 | NaN | 19.8691
8180.1292 | 278.6541 | 155.0354 | 148.9088 | 151.2898 | 158.2476 | 175.1084 | 207.9283 | 207.1491 | NaN | NaN | NaN | 538.7654 | 124.5316 | NaN | NaN | 51.8613 | NaN | NaN | NaN | NaN | 715.9864 | 1254.2648 | NaN | 17.2499 | NaN | 24.4234
8181.1292 | 277.7897 | 155.4491 | 148.9773 | 152.2887 | 158.4174 | 176.7676 | 208.2413 | 207.2434 | NaN | NaN | NaN | 538.1204 | 126.6372 | NaN | NaN | 44.0654 | NaN | NaN | NaN | NaN | 710.7454 | 1254.2649 | NaN | 2.7649 | NaN | 24.1413
8182.1292 | 276.6369 | 155.1916 | 148.964 | 152.2486 | 158.1146 | 176.4703 | 208.3126 | 206.6701 | NaN | NaN | NaN | 529.4596 | 127.2513 | NaN | NaN | 48.4523 | NaN | NaN | NaN | NaN | 706.8707 | 1254.2638 | NaN | 17.3106 | NaN | 16.8563
8183.1292 | 277.443 | 154.8356 | 149.2225 | 151.9757 | 157.6951 | 176.5528 | 208.4239 | 206.2659 | NaN | NaN | NaN | 514.4427 | 128.4255 | NaN | NaN | 44.4397 | NaN | NaN | NaN | NaN | 705.6873 | 1254.2635 | NaN | 15.0347 | NaN | 13.8841
8184.1292 | 278.3856 | 154.7408 | 149.7972 | 151.8445 | 157.4961 | 175.425 | 208.0863 | 205.2517 | NaN | NaN | NaN | 504.7195 | 133.4824 | NaN | NaN | 37.8882 | NaN | NaN | NaN | NaN | 703.5208 | 1254.2639 | NaN | 7.6988 | NaN | 16.3716
8185.1292 | 277.6694 | 155.7069 | 149.7479 | 151.6973 | 157.6073 | 174.8594 | 208.0867 | 205.1116 | NaN | NaN | NaN | 496.1936 | 129.035 | NaN | NaN | 2.3821 | -17.0217 | NaN | NaN | NaN | 700.2503 | 1254.2623 | NaN | 12.7249 | NaN | 15.5002
8186.1292 | 274.4642 | 155.5635 | 149.9394 | 151.7143 | 157.7217 | 174.5022 | 207.5907 | 204.0152 | NaN | NaN | NaN | 486.7479 | 129.8466 | NaN | NaN | 52.7158 | NaN | NaN | NaN | NaN | 698.0558 | 1254.2611 | NaN | -3.4543 | NaN | 25.1728
8187.1292 | 274.5177 | 155.8619 | 149.6114 | 151.836 | 157.9117 | 173.7396 | 207.9541 | 202.9769 | NaN | NaN | NaN | 490.8912 | 128.2803 | NaN | NaN | 30.6824 | NaN | NaN | NaN | NaN | 696.8822 | 1254.2615 | NaN | 11.1135 | NaN | 20.0976
8188.1292 | 274.448 | 155.596 | 149.6557 | 152.0276 | 158.3772 | 173.6297 | 207.4959 | 202.6012 | NaN | NaN | NaN | 488.8949 | 125.7385 | NaN | NaN | 53.2119 | NaN | NaN | NaN | NaN | 692.8989 | 1254.2606 | NaN | 16.3867 | NaN | 11.4132
8189.1292 | 274.4277 | 155.3002 | 150.3638 | 151.8759 | 158.5913 | 173.4477 | 208.0313 | 202.9064 | NaN | NaN | NaN | 498.3646 | 135.5432 | NaN | NaN | -15.273 | NaN | NaN | NaN | NaN | 699.9653 | 1254.2602 | NaN | 24.0339 | NaN | 17.1501
8190.1292 | 274.2158 | 154.8705 | 151.1495 | 151.6576 | 158.6001 | 173.5443 | 208.4289 | 203.3876 | NaN | NaN | NaN | 491.1045 | 125.2733 | NaN | NaN | 15.7764 | NaN | NaN | NaN | NaN | 690.8375 | 1254.2606 | NaN | 1.755 | NaN | 21.7938
8191.1292 | 274.9417 | 154.2125 | 151.6756 | 151.6768 | 158.5026 | 173.7804 | 208.4539 | 204.4232 | NaN | NaN | NaN | 485.7208 | 130.4317 | NaN | NaN | 43.0508 | NaN | NaN | NaN | NaN | 685.6299 | 1254.2602 | NaN | 11.9368 | NaN | 15.6662
8192.1292 | 277.2626 | 154.4175 | 151.2905 | 151.7185 | 158.4829 | 174.1088 | 209.1197 | 204.5905 | NaN | NaN | NaN | 488.4289 | 119.8247 | NaN | NaN | 47.5106 | NaN | NaN | NaN | NaN | 683.6996 | 1254.2592 | NaN | 8.2563 | NaN | 16.2006
8193.1292 | 278.5762 | 154.912 | 152.2409 | 152.19 | 158.1858 | 173.6168 | 209.7277 | 206.3787 | NaN | NaN | NaN | 480.1666 | 130.602 | NaN | NaN | 43.373 | -18.4709 | NaN | NaN | NaN | 680.8821 | 1254.2586 | NaN | 6.9205 | NaN | 20.7944
8194.1292 | 278.59 | 155.1845 | 152.8202 | 152.1761 | 157.8784 | 173.183 | 208.9529 | 207.2356 | NaN | NaN | NaN | 471.6332 | 130.7676 | NaN | NaN | 21.4512 | NaN | NaN | NaN | NaN | 678.1842 | 1254.2585 | NaN | 9.698 | NaN | 22.4529
8195.1292 | 278.9352 | 155.7868 | 153.3193 | 152.2803 | 157.7668 | 172.9713 | 209.49 | 207.9061 | NaN | NaN | NaN | 473.1311 | 129.6827 | NaN | NaN | 48.5325 | NaN | NaN | NaN | NaN | 675.4848 | 1254.2565 | NaN | 22.9205 | NaN | 21.813
8196.1292 | 278.294 | 155.8268 | 153.7272 | 152.3553 | 157.6954 | 172.9364 | 210.8355 | 208.8779 | NaN | NaN | NaN | 469.9183 | 131.8329 | NaN | NaN | 32.3787 | NaN | NaN | NaN | NaN | 672.5588 | 1254.2583 | NaN | 8.3171 | NaN | 10.3279
8197.1292 | 277.8165 | 156.559 | 153.8542 | 152.6203 | 157.8478 | 173.5994 | 213.0114 | 209.4363 | NaN | NaN | NaN | 465.8125 | 127.4228 | NaN | NaN | 38.9549 | NaN | NaN | NaN | NaN | 669.8154 | 1254.2567 | NaN | 11.8017 | NaN | 15.3667
8198.1292 | 279.7897 | 156.8286 | 154.0991 | 152.4184 | 157.8824 | 173.5773 | 212.1152 | 208.5511 | NaN | NaN | NaN | 481.4551 | 132.3691 | NaN | NaN | 56.0081 | NaN | NaN | NaN | NaN | 673.7204 | 1254.2571 | NaN | 18.7553 | NaN | 9.6368
8199.1292 | 276.4246 | 157.5327 | 154.1605 | 152.3254 | 158.2714 | 175.0383 | 211.0617 | 208.2804 | NaN | NaN | NaN | 496.5495 | 124.6658 | NaN | NaN | 37.9486 | NaN | NaN | NaN | NaN | 673.429 | 1254.2563 | NaN | 31.7363 | NaN | 21.0136
8200.1292 | 275.1322 | 157.6207 | 154.595 | 152.5358 | 158.4588 | 175.0179 | 210.2397 | 207.9756 | NaN | NaN | NaN | 496.0942 | 122.1858 | NaN | NaN | 77.1166 | NaN | NaN | NaN | NaN | 669.0107 | 1254.2559 | NaN | 13.3656 | NaN | 16.1181
8201.1292 | 274.977 | 157.6521 | 154.303 | 152.6347 | 158.3572 | 174.4682 | 210.4863 | 208.4939 | NaN | NaN | NaN | 488.1403 | 120.7931 | NaN | NaN | 22.2886 | NaN | NaN | NaN | NaN | 663.7295 | 1254.2554 | NaN | 11.6386 | NaN | 21.7379
8202.1292 | 277.015 | 158.7474 | 154.0574 | 152.5668 | 158.5952 | 174.549 | 212.5179 | 207.6675 | NaN | NaN | NaN | 480.0944 | 135.6154 | NaN | NaN | 60.3255 | -18.1773 | NaN | NaN | NaN | 662.3518 | 1254.254 | NaN | 27.5546 | NaN | 20.4593
8203.1292 | 279.7996 | 159.3654 | 154.2554 | 152.6227 | 158.7473 | 175.3127 | 213.426 | 208.4033 | NaN | NaN | NaN | 470.4158 | 128.5429 | NaN | NaN | 31.6009 | -17.3511 | NaN | NaN | NaN | 660.8 | 1254.2539 | NaN | 7.7953 | NaN | 25.1903
8204.1292 | 283.3913 | 159.2171 | 154.4289 | 152.6325 | 158.619 | 176.1052 | 214.0767 | 208.8405 | NaN | NaN | NaN | 466.618 | 129.8213 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 659.7379 | 1254.2542 | NaN | 16.5177 | NaN | 12.8888
8205.1292 | 284.7642 | 159.712 | 154.0145 | 152.5695 | 158.9295 | 176.9876 | 215.9359 | 208.9882 | NaN | NaN | NaN | 461.7616 | 129.601 | NaN | NaN | 25.176 | NaN | NaN | NaN | NaN | 658.0393 | 1254.2533 | NaN | 8.6101 | NaN | 16.8824
8206.1292 | 284.3319 | 160.2501 | 154.3079 | 152.9403 | 158.9019 | 177.4044 | 216.5626 | 209.4258 | NaN | NaN | NaN | 455.0012 | 133.0142 | NaN | NaN | 58.3595 | NaN | NaN | NaN | NaN | 655.0612 | 1254.2532 | NaN | 16.9353 | NaN | 19.5526
8207.1292 | 285.2606 | 160.9132 | 153.973 | 153.0822 | 158.9231 | 177.7045 | 216.9139 | 208.595 | NaN | NaN | NaN | 458.1565 | 126.5591 | NaN | NaN | 39.4806 | NaN | NaN | NaN | NaN | 654.2414 | 1254.2516 | NaN | 6.4223 | NaN | 19.0406
8208.1292 | 285.5377 | 162.2036 | 154.2632 | 153.1558 | 158.7311 | 177.0879 | 217.8213 | 209.6637 | NaN | NaN | NaN | 470.7146 | 132.151 | NaN | NaN | 57.2202 | NaN | NaN | NaN | NaN | 653.7233 | 1254.252 | NaN | 1.2981 | NaN | 20.7409
8209.1292 | 288.5577 | 162.1491 | 154.8974 | 153.4413 | 158.8259 | 178.1353 | 216.6876 | 209.394 | NaN | NaN | NaN | 478.012 | 121.1359 | NaN | NaN | 49.3526 | -15.3319 | NaN | NaN | NaN | 653.1455 | 1254.2509 | NaN | 10.2071 | NaN | 27.6724
8210.1448 | 289.4956 | 162.2221 | 155.2215 | 153.4998 | 158.6984 | 178.6754 | 216.5643 | 208.2417 | NaN | NaN | NaN | 505.5695 | 126.2096 | NaN | NaN | 71.2059 | NaN | NaN | NaN | NaN | 660.6966 | 1254.2506 | NaN | 5.5736 | NaN | 29.4622
8211.1292 | 289.0124 | 162.9319 | 155.7977 | 154.0485 | 159.4445 | 178.7397 | 216.4144 | 208.4086 | NaN | NaN | NaN | 521.3698 | 123.9372 | NaN | NaN | 39.6107 | NaN | NaN | NaN | NaN | 649.3852 | 1254.252 | NaN | 7.3508 | NaN | 16.537
8212.1292 | 294.1134 | 163.8778 | 155.8996 | 153.5119 | 160.0766 | 180.956 | 217.5086 | 208.6321 | NaN | NaN | NaN | 519.6257 | 123.9956 | NaN | NaN | 61.7538 | NaN | NaN | NaN | NaN | 643.2347 | 1254.2505 | NaN | 17.6609 | NaN | 20.6988
8213.1292 | 295.4153 | 164.5996 | 155.8263 | 153.8031 | 160.6091 | 182.3373 | 218.6096 | 209.8379 | NaN | NaN | NaN | 537.7292 | 123.0632 | NaN | NaN | 54.2797 | NaN | NaN | NaN | NaN | 641.8851 | 1254.2502 | NaN | 13.2134 | NaN | 12.0452
8214.1292 | 297.5641 | 165.1798 | 155.4486 | 153.6835 | 160.8417 | 182.6524 | 219.4731 | 209.598 | NaN | NaN | NaN | 545.7521 | 133.1667 | NaN | NaN | 35.9705 | NaN | NaN | NaN | NaN | 644.3372 | 1254.2491 | NaN | 3.7921 | NaN | 21.2117
8215.1292 | 302.1988 | 165.3363 | 155.8602 | 153.7455 | 161.2338 | 182.7776 | 220.0614 | 209.2587 | NaN | NaN | NaN | 550.1833 | 121.1565 | NaN | NaN | 57.8438 | NaN | NaN | NaN | NaN | 641.9313 | 1254.2494 | NaN | 8.145 | NaN | 14.7193
8216.1292 | 301.7677 | 165.3651 | 155.3442 | 153.8747 | 161.6786 | 183.4807 | 219.1798 | 209.1835 | NaN | NaN | NaN | 553.4324 | 135.2135 | NaN | NaN | 41.1952 | 16.6581 | NaN | NaN | NaN | 637.6488 | 1254.2489 | NaN | 16.1721 | NaN | 14.7884
8217.1292 | 302.8223 | 164.8112 | 155.9555 | 154.2549 | 161.7434 | 183.3053 | 219.0968 | 208.9608 | NaN | NaN | NaN | 574.6575 | 128.6371 | NaN | NaN | 29.8554 | NaN | NaN | NaN | NaN | 639.4962 | 1254.2493 | NaN | 20.1547 | NaN | 9.202
8218.1292 | 311.1337 | 164.8076 | 155.7724 | 153.6508 | 162.1128 | 186.1503 | 219.8068 | 207.7727 | NaN | NaN | NaN | 592.5855 | 125.4642 | NaN | NaN | 41.2426 | NaN | NaN | NaN | NaN | 632.1491 | 1254.2483 | NaN | 23.1209 | NaN | 21.2655
8219.1292 | 312.3816 | 165.5895 | 155.4754 | 154.1518 | 162.6742 | 186.0426 | 219.4852 | 207.6699 | NaN | NaN | NaN | 605.2612 | 129.8234 | NaN | NaN | 31.3448 | NaN | NaN | NaN | NaN | 629.7862 | 1254.247 | NaN | 24.7227 | NaN | 24.8611
8220.1292 | 318.1215 | 166.3936 | 155.1615 | 154.9042 | 162.8682 | 184.9761 | 220.0356 | 207.2625 | NaN | NaN | NaN | 621.2105 | 121.3448 | NaN | NaN | 31.6275 | NaN | NaN | NaN | NaN | 631.0154 | 1254.2476 | NaN | 35.6826 | NaN | 18.8693
8221.1292 | 322.6033 | 166.8517 | 155.1195 | 154.9119 | 163.2504 | 183.2635 | 220.663 | 209.0167 | NaN | NaN | NaN | 629.985 | 126.7875 | NaN | NaN | 51.3577 | NaN | NaN | NaN | NaN | 630.4628 | 1254.2465 | NaN | 4.4519 | NaN | 21.0442
8222.1292 | 326.3961 | 167.0291 | 155.18 | 154.8914 | 163.7062 | 183.2618 | 221.9972 | 209.3701 | NaN | NaN | NaN | 622.5451 | 129.3649 | NaN | NaN | 42.8363 | -18.0518 | NaN | NaN | NaN | 626.4987 | 1254.2473 | NaN | 18.7508 | NaN | 15.5588
8223.1292 | 325.7523 | 167.0732 | 155.7668 | 155.2361 | 163.6978 | 182.9143 | 221.6769 | 208.8745 | NaN | NaN | NaN | 630.656 | 129.8304 | NaN | NaN | 75.4463 | 10.9786 | NaN | NaN | NaN | 632.8246 | 1254.2461 | NaN | 11.6513 | NaN | 20.4713
8224.1292 | 325.0085 | 167.5954 | 156.3913 | 155.9018 | 164.0278 | 183.7935 | 223.4888 | 209.7746 | NaN | NaN | NaN | 638.7263 | 132.9622 | NaN | NaN | 48.0329 | NaN | NaN | NaN | NaN | 629.8498 | 1254.2451 | NaN | 18.8919 | NaN | 29.2972
8225.1292 | 326.3798 | 168.1317 | 156.7286 | 155.756 | 165.004 | 185.0789 | 223.6054 | 209.5575 | NaN | NaN | NaN | 641.3673 | 131.4367 | NaN | NaN | 39.416 | NaN | NaN | NaN | NaN | 627.169 | 1254.2445 | NaN | 7.286 | NaN | 26.3376
8226.1292 | 326.4095 | 168.3387 | 157.3513 | 156.2621 | 165.5171 | 184.876 | 222.9464 | 208.6339 | NaN | NaN | NaN | 618.6589 | 127.2893 | NaN | NaN | 42.9941 | NaN | NaN | NaN | NaN | 624.093 | 1254.2453 | NaN | 15.2494 | NaN | 15.9895
8227.1292 | 325.5891 | 168.4313 | 157.8172 | 156.7397 | 166.0818 | 185.5258 | 223.8201 | 209.0301 | NaN | NaN | NaN | 625.5087 | 127.8215 | NaN | NaN | 53.902 | NaN | NaN | NaN | NaN | 621.6154 | 1254.2458 | NaN | 14.9506 | NaN | 10.8519
8228.1292 | 326.868 | 168.232 | 157.729 | 156.9585 | 166.4137 | 185.4674 | 223.4672 | 208.5903 | NaN | NaN | NaN | 635.7144 | 130.7131 | NaN | NaN | 50.4876 | NaN | NaN | NaN | NaN | 619.7641 | 1254.2437 | NaN | 4.8376 | NaN | 27.2068
8229.1292 | 329.2671 | 168.4456 | 158.0233 | 156.9265 | 166.792 | 185.322 | 223.946 | 209.3698 | NaN | NaN | NaN | 624.5124 | 130.1752 | NaN | NaN | 45.621 | -15.8481 | NaN | NaN | NaN | 612.289 | 1245.3453 | NaN | 15.8592 | NaN | 12.5588
8230.1292 | 330.8342 | 168.5464 | 157.6512 | 156.9364 | 167.4085 | 188.7384 | 224.3732 | 213.3807 | NaN | NaN | NaN | 606.4521 | 127.7472 | NaN | NaN | 54.1099 | NaN | NaN | NaN | NaN | 610.7063 | 1242.9486 | NaN | 34.3444 | NaN | 18.1478
8231.1292 | 333.3429 | 169.3137 | 157.4648 | 157.0097 | 167.7478 | 188.1546 | 225.1555 | 213.7863 | NaN | NaN | NaN | 585.3893 | 130.6996 | NaN | NaN | 55.2712 | NaN | NaN | NaN | NaN | 607.6329 | 1230.0495 | NaN | 6.2415 | NaN | 30.0259
8232.1292 | 334.0416 | 169.6311 | 157.2985 | 157.058 | 168.1929 | 187.4997 | 224.8149 | 213.1734 | NaN | NaN | NaN | 565.3719 | 122.03 | NaN | NaN | 55.5933 | NaN | NaN | NaN | NaN | 606.4105 | 1225.0562 | NaN | 14.714 | NaN | 18.0851
8233.1292 | 341.667 | 169.9582 | 157.3035 | 158.1135 | 168.5275 | 189.3338 | 225.3981 | 215.4423 | NaN | NaN | NaN | 551.4808 | 129.5407 | NaN | NaN | 69.146 | NaN | NaN | NaN | NaN | 604.4723 | 1218.6869 | NaN | 7.9549 | NaN | 11.7869
8234.1292 | 345.6933 | 170.3376 | 157.7007 | 158.9578 | 169.0781 | 189.5846 | 225.8477 | 215.003 | NaN | NaN | NaN | 537.3941 | 129.6546 | NaN | NaN | 41.9764 | NaN | NaN | NaN | NaN | 604.3955 | 1214.6198 | NaN | 15.5476 | NaN | 17.9024
8235.1448 | 349.7282 | 170.7177 | 158.0945 | 159.4642 | 169.9719 | 189.2458 | 226.9828 | 214.0286 | NaN | NaN | NaN | 522.9041 | 128.6167 | NaN | NaN | 45.5686 | -15.3709 | NaN | NaN | NaN | 601.9093 | 1206.3541 | NaN | -0.7876 | NaN | 20.3684
8236.1292 | 349.4708 | 171.5769 | 158.8195 | 158.9462 | 170.2805 | 189.3855 | 228.6726 | 213.9231 | NaN | NaN | NaN | 508.7691 | 130.2471 | NaN | NaN | 24.2163 | NaN | NaN | NaN | NaN | 599.4068 | 1199.1715 | NaN | 6.3093 | NaN | 16.2
8237.1292 | 349.7343 | 171.9188 | 159.0294 | 158.6996 | 170.0302 | 189.7024 | 228.2201 | 212.5573 | NaN | NaN | NaN | 499.5389 | 128.5284 | NaN | NaN | 28.7195 | NaN | NaN | NaN | NaN | 596.4688 | 1193.5266 | NaN | 9.2177 | NaN | 24.7655
8238.1292 | 347.8885 | 172.0003 | 159.8919 | 159.0064 | 169.8069 | 189.3113 | 227.9553 | 212.6745 | NaN | NaN | NaN | 486.9158 | 123.6485 | NaN | NaN | 50.8252 | NaN | NaN | NaN | NaN | 595.9058 | 1187.797 | NaN | 12.583 | NaN | 26.0629
8239.1292 | 347.8133 | 171.8807 | 159.3322 | 158.8869 | 169.3569 | 189.0248 | 227.2282 | 213.9904 | NaN | NaN | NaN | 477.849 | 127.9064 | NaN | NaN | 55.6653 | NaN | NaN | NaN | NaN | 594.7497 | 1183.9725 | NaN | 18.5836 | NaN | 28.3262
8240.1448 | 357.2102 | 171.9318 | 159.6638 | 159.6282 | 169.9267 | 189.8777 | 227.0498 | 214.69 | NaN | NaN | NaN | 469.6533 | 128.4554 | NaN | NaN | 62.3388 | NaN | NaN | NaN | NaN | 592.4237 | 1173.8453 | NaN | 12.8959 | NaN | 25.6679
8241.1292 | 362.4219 | 172.0989 | 160.444 | 159.8654 | 170.3085 | 188.9168 | 229.1628 | 214.4409 | NaN | NaN | NaN | 475.6047 | 121.8366 | NaN | NaN | 45.7285 | NaN | NaN | NaN | NaN | 593.2559 | 1165.9374 | NaN | 30.0698 | NaN | 27.6769
8242.1292 | 362.4375 | 172.4045 | 160.0529 | 160.1809 | 170.4676 | 188.7516 | 228.8966 | 215.4756 | NaN | NaN | NaN | 485.5155 | 119.6674 | NaN | NaN | 21.3556 | NaN | NaN | NaN | NaN | 599.0022 | 1165.6707 | NaN | 5.1994 | NaN | 14.1622
8243.1292 | 367.3358 | 172.5008 | 160.527 | 160.1756 | 170.633 | 189.3637 | 229.6973 | 215.5711 | NaN | NaN | NaN | 498.9322 | 118.6754 | NaN | NaN | 53.4928 | -15.7618 | NaN | NaN | NaN | 593.6916 | 1164.39 | NaN | 5.506 | NaN | 19.492
8244.1292 | 369.6751 | 172.7584 | 160.384 | 160.0065 | 170.3545 | 191.9978 | 230.7057 | 215.6233 | NaN | NaN | NaN | 515.3552 | 128.8536 | NaN | NaN | 79.0792 | NaN | NaN | NaN | NaN | 591.2487 | 1161.0441 | NaN | 6.9846 | NaN | 15.5955
8245.1292 | 370.0224 | 173.3155 | 160.1814 | 159.8278 | 170.2257 | 192.628 | 230.8761 | 216.0203 | NaN | NaN | NaN | 516.0368 | 128.2313 | NaN | NaN | 44.5837 | NaN | NaN | NaN | NaN | 586.6855 | 1153.59 | NaN | 2.7722 | NaN | 27.6589
8246.1292 | 369.9969 | 173.6532 | 160.5824 | 159.6736 | 170.2099 | 192.2099 | 230.4762 | 217.3516 | NaN | NaN | NaN | 503.7989 | 129.3782 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 582.5619 | 1143.2433 | NaN | 3.2176 | NaN | 12.6294
8247.1292 | 370.146 | 173.4327 | 161.0144 | 159.371 | 170.4218 | 191.5906 | 229.3621 | 217.6515 | NaN | NaN | NaN | 495.6546 | 129.1663 | NaN | NaN | 25.262 | NaN | NaN | NaN | NaN | 580.0037 | 1139.0982 | NaN | 8.9037 | NaN | 19.3381
8248.1292 | 371.447 | 173.4766 | 161.3366 | 159.279 | 170.4113 | 191.5427 | 230.0785 | 218.072 | NaN | NaN | NaN | 486.3983 | 121.6766 | NaN | NaN | 28.9563 | NaN | NaN | NaN | NaN | 577.4885 | 1133.5573 | NaN | 4.0448 | NaN | 14.0745
8249.1292 | 374.2591 | 173.8403 | 161.5809 | 159.5204 | 170.1306 | 190.8249 | 229.9098 | 218.6405 | NaN | NaN | NaN | 493.3771 | 138.5803 | NaN | NaN | 44.6797 | NaN | NaN | NaN | NaN | 577.7117 | 1122.9759 | NaN | 9.009 | NaN | 16.0499
8250.1292 | 381.5244 | 174.1225 | 161.6244 | 159.7799 | 170.2321 | 190.2836 | 229.8172 | 218.3517 | NaN | NaN | NaN | 493.4669 | 121.5577 | NaN | NaN | -19.5708 | 5.9173 | NaN | NaN | NaN | 578.0777 | 1123.311 | NaN | 17.277 | NaN | 11.6777
8251.1292 | 384.5748 | 174.8945 | 161.7247 | 159.6724 | 170.2763 | 190.125 | 228.9884 | 218.9014 | NaN | NaN | NaN | 484.4549 | 128.8205 | NaN | NaN | 36.9414 | NaN | NaN | NaN | NaN | 573.954 | 1119.4694 | NaN | 18.4644 | NaN | 20.2834
8252.1292 | 383.4511 | 176.0958 | 162.0536 | 159.5502 | 170.2129 | 189.0153 | 228.4745 | 221.4064 | NaN | NaN | NaN | 479.024 | 124.7928 | NaN | NaN | 51.8109 | NaN | NaN | NaN | NaN | 573.3562 | 1112.874 | NaN | 0.9029 | NaN | 24.1698
8253.1292 | 382.1927 | 176.4807 | 162.2514 | 159.9024 | 170.3418 | 189.8275 | 229.4597 | 222.3371 | NaN | NaN | NaN | 476.5632 | 130.1796 | NaN | NaN | 30.929 | NaN | NaN | NaN | NaN | 568.3987 | 1102.5237 | NaN | 3.3151 | NaN | 30.287
8254.1292 | 379.9518 | 176.8797 | 162.6553 | 160.0469 | 170.8911 | 190.7602 | 230.5995 | 223.9183 | NaN | NaN | NaN | 475.1649 | 132.6272 | NaN | NaN | 38.6162 | -19.978 | NaN | NaN | NaN | 565.6462 | 1094.3115 | NaN | 34.6021 | NaN | 8.01
8255.1292 | 389.4799 | 177.0166 | 161.7243 | 161.3781 | 171.6748 | 191.6946 | 231.4382 | 224.6405 | NaN | NaN | NaN | 470.8694 | 140.8826 | NaN | NaN | 115.3886 | 16.1108 | NaN | NaN | NaN | 564.2592 | 1088.9565 | NaN | 19.6942 | NaN | 21.865
8256.1292 | 399.5093 | 177.3601 | 161.6097 | 162.6682 | 172.3564 | 191.0359 | 231.7624 | 222.8389 | NaN | NaN | NaN | 477.7492 | 129.9983 | NaN | NaN | 111.7983 | NaN | NaN | NaN | NaN | 563.3626 | 1088.4779 | NaN | 16.3699 | NaN | 25.8396
8257.1292 | 403.8267 | 177.4965 | 161.6936 | 162.5552 | 172.9753 | 192.104 | 233.3457 | 222.7463 | NaN | NaN | NaN | 487.3563 | 131.5829 | NaN | NaN | 113.1352 | NaN | NaN | NaN | NaN | 566.4671 | 1087.8288 | NaN | 27.9738 | NaN | 18.8769
8258.1292 | 405.1314 | 177.7375 | 161.4557 | 162.6992 | 172.9656 | 191.8787 | 232.6407 | 223.0725 | NaN | NaN | NaN | 483.82 | 132.2296 | NaN | NaN | 115.2639 | NaN | NaN | NaN | NaN | 559.7546 | 1081.4249 | NaN | 11.6909 | NaN | 12.5156
8259.1292 | 402.4105 | 177.9656 | 161.7834 | 163.3982 | 173.3291 | 191.4075 | 232.6072 | 223.3347 | NaN | NaN | NaN | 485.611 | 129.7665 | NaN | NaN | 116.8144 | NaN | NaN | NaN | NaN | 557.6178 | 1075.0742 | NaN | 19.4671 | NaN | 11.9544
8260.1292 | 408.4902 | 178.1509 | 162.3116 | 163.8386 | 173.7007 | 192.7087 | 231.7849 | 224.3662 | NaN | NaN | NaN | 490.2432 | 127.8135 | NaN | NaN | 105.8031 | NaN | NaN | NaN | NaN | 558.8888 | 1070.9542 | NaN | 17.2008 | NaN | 21.7359
8261.1292 | 406.0251 | 178.1287 | 163.0857 | 163.4845 | 173.9149 | 193.0985 | 231.8428 | 224.6197 | NaN | NaN | NaN | 502.0471 | 129.6031 | NaN | NaN | 109.7024 | -17.3699 | NaN | NaN | NaN | 558.4511 | 1071.2238 | NaN | 18.7737 | NaN | 21.8226
8262.1292 | 401.8075 | 177.9517 | 163.1076 | 163.92 | 174.1904 | 194.7349 | 230.7579 | 224.7303 | NaN | NaN | NaN | 523.9414 | 128.9952 | NaN | NaN | 115.7668 | 10.1695 | NaN | NaN | NaN | 559.9349 | 1068.1338 | NaN | 9.1637 | NaN | 18.3124
8263.1292 | 396.8622 | 178.3886 | 162.9885 | 163.1769 | 174.4121 | 195.9437 | 232.1845 | 225.5412 | NaN | NaN | NaN | 529.3032 | 127.9559 | NaN | NaN | 110.3921 | NaN | NaN | NaN | NaN | 556.198 | 1065.4925 | NaN | 14.9554 | NaN | 11.0567
8264.1292 | 393.2622 | 178.4359 | 162.9288 | 163.1775 | 174.1044 | 196.0697 | 232.9257 | 224.8726 | NaN | NaN | NaN | 524.811 | 125.4817 | NaN | NaN | 105.1851 | NaN | NaN | NaN | NaN | 552.0287 | 1057.253 | NaN | 35.0606 | NaN | 24.4447
8265.1292 | 392.3047 | 178.6606 | 162.4557 | 163.4021 | 174.0496 | 195.4956 | 232.6281 | 223.4711 | NaN | NaN | NaN | 515.6817 | 129.2424 | NaN | NaN | 112.4458 | NaN | NaN | NaN | NaN | 548.3767 | 1049.1184 | NaN | 7.8582 | NaN | 20.4526
8266.1292 | 391.6179 | 178.7859 | 162.4678 | 163.4336 | 174.4372 | 196.0219 | 233.2362 | 223.2988 | NaN | NaN | NaN | 518.83 | 125.2086 | NaN | NaN | 107.3362 | NaN | NaN | NaN | NaN | 547.0476 | 1046.1719 | NaN | 17.1541 | NaN | 18.1154
8267.1292 | 390.746 | 179.0813 | 163.2025 | 163.4205 | 174.516 | 195.2179 | 233.0246 | 223.5634 | NaN | NaN | NaN | 510.0048 | 118.8528 | NaN | NaN | 122.7992 | -16.7604 | NaN | NaN | NaN | 545.2138 | 1039.6608 | NaN | 18.5822 | NaN | 15.2317
8268.1292 | 394.5503 | 179.6607 | 163.6547 | 163.4304 | 174.5228 | 194.5813 | 232.8369 | 223.5917 | NaN | NaN | NaN | 504.4426 | 129.8123 | NaN | NaN | 106.4974 | -14.1236 | NaN | NaN | NaN | 544.2841 | 1033.85 | NaN | 11.5506 | NaN | 26.8543
8269.1292 | 391.8754 | 180.1116 | 163.5774 | 163.8237 | 174.5319 | 193.6652 | 233.5523 | 224.4805 | NaN | NaN | NaN | 500.2952 | 130.4243 | NaN | NaN | 112.5077 | NaN | NaN | NaN | NaN | 536.029 | 1027.9759 | NaN | 21.1005 | NaN | 14.9157
8270.1292 | 391.5413 | 180.2012 | 164.0216 | 164.014 | 174.4254 | 194.0764 | 233.8195 | 225.1065 | NaN | NaN | NaN | 498.6991 | 127.4122 | NaN | NaN | 113.8654 | NaN | NaN | NaN | NaN | 540.9116 | 1025.6543 | NaN | 9.4223 | NaN | 18.1914
8271.1292 | 393.2829 | 180.092 | 163.9516 | 163.8089 | 174.5232 | 195.1134 | 233.7296 | 225.4362 | NaN | NaN | NaN | 498.1052 | 123.428 | NaN | NaN | 119.4696 | NaN | NaN | NaN | NaN | 538.1569 | 1019.7619 | NaN | 18.8875 | NaN | 26.9198
8272.1292 | 391.0909 | 180.2177 | 164.2357 | 164.4471 | 174.6737 | 194.0358 | 233.8353 | 225.2432 | NaN | NaN | NaN | 499.9856 | 130.944 | NaN | NaN | 115.9191 | NaN | NaN | NaN | NaN | 540.496 | 1016.9593 | NaN | 26.9176 | NaN | 14.832
8273.1292 | 392.1906 | 180.303 | 164.3801 | 164.5032 | 174.3935 | 193.2853 | 234.0877 | 226.1757 | NaN | NaN | NaN | 492.8226 | 133.5954 | NaN | NaN | 111.3948 | -18.5513 | NaN | NaN | NaN | 534.7458 | 1015.5693 | NaN | 6.0758 | NaN | 23.9514
8274.1292 | 391.8969 | 179.957 | 164.5056 | 164.7231 | 174.5197 | 192.7155 | 233.8636 | 225.6173 | NaN | NaN | NaN | 482.771 | 123.0545 | NaN | NaN | 87.8512 | -11.5495 | NaN | NaN | NaN | 533.4747 | 1012.6903 | NaN | 13.0789 | NaN | 23.667
8275.1292 | 389.4342 | 179.7468 | 164.2611 | 164.9885 | 174.8759 | 192.9005 | 233.1416 | 225.9754 | NaN | NaN | NaN | 475.2246 | 122.0696 | NaN | NaN | 91.426 | NaN | NaN | NaN | NaN | 534.3753 | 1007.8803 | NaN | 11.6397 | NaN | 26.1996
8276.1292 | 388.9734 | 179.8227 | 163.9584 | 165.4894 | 175.2576 | 193.3609 | 233.3613 | 227.5832 | NaN | NaN | NaN | 468.1813 | 124.5663 | NaN | NaN | 100.7501 | NaN | NaN | NaN | NaN | 529.5573 | 1001.4086 | NaN | 6.6926 | NaN | 22.1936
8277.1292 | 384.7048 | 180.7457 | 163.9335 | 165.1845 | 175.8172 | 192.56 | 232.832 | 229.1588 | NaN | NaN | NaN | 460.6613 | 125.8295 | NaN | NaN | 109.2989 | NaN | NaN | NaN | NaN | 527.5366 | 994.472 | NaN | 10.2001 | NaN | 20.7337
8278.1292 | 381.699 | 180.6867 | 163.8737 | 164.8665 | 175.9747 | 192.3511 | 232.7139 | 229.0192 | NaN | NaN | NaN | 450.8823 | 128.6023 | NaN | NaN | 101.1602 | -16.7651 | NaN | NaN | NaN | 526.1997 | 986.5498 | NaN | 10.1248 | NaN | 13.6921
8279.1292 | 380.2029 | 181.1548 | 164.2956 | 165.0026 | 175.988 | 192.4372 | 233.5615 | 229.6105 | NaN | NaN | NaN | 449.1729 | 127.3313 | NaN | NaN | 105.9506 | 17.1774 | NaN | NaN | NaN | 526.0163 | 982.8795 | NaN | 27.6012 | NaN | 24.1864
8280.1292 | 377.0511 | 180.7637 | 164.5427 | 164.6327 | 175.9097 | 192.4228 | 234.4571 | 230.4742 | NaN | NaN | NaN | 447.1497 | 122.0226 | NaN | NaN | 104.3047 | NaN | NaN | NaN | NaN | 522.3154 | 979.5143 | NaN | 9.8218 | NaN | 12.4395
8281.1292 | 374.9459 | 180.0258 | 164.0244 | 165.1186 | 176.817 | 191.8627 | 234.1876 | 230.527 | NaN | NaN | NaN | 444.6453 | 129.2798 | NaN | NaN | 122.894 | NaN | NaN | NaN | NaN | 520.7905 | 970.9506 | NaN | 12.1272 | NaN | 26.2657
8282.1292 | 372.0965 | 180.8153 | 164.1605 | 166.4296 | 177.1999 | 192.0216 | 234.8053 | 230.7544 | NaN | NaN | NaN | 440.0583 | 125.8845 | NaN | NaN | 107.8353 | NaN | NaN | NaN | NaN | 518.3169 | 969.323 | NaN | 31.777 | NaN | 21.9614
8283.1292 | 368.1776 | 181.1537 | 164.6742 | 166.6964 | 177.4575 | 191.3241 | 234.6406 | 230.8573 | NaN | NaN | NaN | 454.7585 | 147.5501 | NaN | NaN | 134.3762 | NaN | NaN | NaN | NaN | 526.0527 | 961.1676 | NaN | 1.989 | NaN | 12.3996
8284.1292 | 365.99 | 180.7359 | 164.936 | 167.2259 | 177.6182 | 191.1673 | 234.7976 | 230.5074 | NaN | NaN | NaN | 482.5617 | 123.6768 | NaN | NaN | 108.402 | NaN | NaN | NaN | NaN | 524.9214 | 972.9944 | NaN | 9.0748 | NaN | 13.9541
8285.1292 | 363.724 | 181.1421 | 164.7216 | 167.0623 | 178.0082 | 193.3019 | 235.9771 | 231.301 | NaN | NaN | NaN | 479.9886 | 129.0478 | NaN | NaN | 119.8613 | -18.4268 | NaN | NaN | NaN | 519.6843 | 968.9218 | NaN | 9.3763 | NaN | 25.3605
8286.1292 | 363.2299 | 181.0058 | 164.5543 | 166.8982 | 177.7062 | 194.092 | 236.1741 | 230.5198 | NaN | NaN | NaN | 485.9382 | 131.0712 | NaN | NaN | 112.1925 | -1.6898 | NaN | NaN | NaN | 517.5624 | 961.2594 | NaN | 15.7549 | NaN | 17.715
8287.1292 | 361.6605 | 181.009 | 164.4205 | 166.7301 | 177.4383 | 195.6244 | 235.4078 | 230.924 | NaN | NaN | NaN | 491.7397 | 126.0675 | NaN | NaN | 109.7166 | NaN | NaN | NaN | NaN | 515.013 | 956.5979 | NaN | 10.2702 | NaN | 17.3278
8288.1292 | 378.2869 | 181.1587 | 164.5606 | 166.9652 | 177.2095 | 194.8659 | 236.6064 | 229.7429 | NaN | NaN | NaN | 495.0579 | 127.7033 | NaN | NaN | 113.91 | NaN | NaN | NaN | NaN | 514.5568 | 953.7555 | NaN | 28.7746 | NaN | 17.7565
8289.1292 | 375.8996 | 181.063 | 164.4785 | 166.5923 | 176.9397 | 194.7931 | 235.3544 | 230.0783 | NaN | NaN | NaN | 486.0339 | 128.8488 | NaN | NaN | 110.0735 | NaN | NaN | NaN | NaN | 510.3759 | 945.9273 | NaN | 12.3222 | NaN | 22.0502
8290.1292 | 390.1669 | 181.0371 | 164.2061 | 167.2645 | 177.052 | 194.5694 | 235.7084 | 229.702 | NaN | NaN | NaN | 483.2488 | 128.8942 | NaN | NaN | 111.0204 | NaN | NaN | NaN | NaN | 507.1999 | 938.0919 | NaN | 4.6037 | NaN | 16.6884
8291.1292 | 389.3205 | 181.4328 | 163.892 | 167.3762 | 177.1749 | 196.915 | 235.3243 | 231.3686 | NaN | NaN | NaN | 477.0148 | 126.8317 | NaN | NaN | 106.9121 | -15.0905 | NaN | NaN | NaN | 506.874 | 937.7699 | NaN | 7.0409 | NaN | 23.7897
8292.1292 | 388.6019 | 181.6911 | 164.2346 | 167.0573 | 176.9863 | 197.963 | 235.4936 | 232.5126 | NaN | NaN | NaN | 470.1555 | 125.388 | NaN | NaN | 114.3014 | -4.4679 | NaN | NaN | NaN | 508.4496 | 935.7689 | NaN | 33.3793 | NaN | 14.7578
8293.1292 | 387.9207 | 181.9766 | 164.5182 | 167.1898 | 177.0603 | 198.726 | 235.8378 | 231.8375 | NaN | NaN | NaN | 475.1299 | 112.4405 | NaN | NaN | 120.0833 | NaN | NaN | NaN | NaN | 509.8701 | 930.9225 | NaN | 32.0183 | NaN | 14.8896
8294.1292 | 385.6077 | 182.5867 | 164.7876 | 167.2491 | 177.1878 | 199.1297 | 238.1253 | 233.8444 | NaN | NaN | NaN | 481.5682 | 125.493 | NaN | NaN | 111.0559 | NaN | NaN | NaN | NaN | 509.177 | 932.3012 | NaN | 11.4129 | NaN | 21.4589
8295.1292 | 382.0059 | 183.2258 | 164.5109 | 167.2158 | 177.3451 | 198.8738 | 238.3908 | 236.687 | NaN | NaN | NaN | 493.5305 | 127.3623 | NaN | NaN | 116.0426 | NaN | NaN | NaN | NaN | 508.7591 | 927.6903 | NaN | 11.0944 | NaN | 24.3387
8296.1292 | 380.8268 | 183.6727 | 165.2585 | 167.1341 | 177.4419 | 198.5367 | 238.9734 | 238.5256 | NaN | NaN | NaN | 501.9433 | 124.4723 | NaN | NaN | 109.6365 | NaN | NaN | NaN | NaN | 506.466 | 924.0172 | NaN | 35.7909 | NaN | 20.9088
8297.1292 | 388.7316 | 183.4405 | 165.7743 | 168.1562 | 178.2871 | 198.8751 | 238.0772 | 240.4111 | NaN | NaN | NaN | 514.3512 | 132.2905 | NaN | NaN | 110.7854 | NaN | NaN | NaN | NaN | 507.863 | 920.1707 | NaN | 13.4287 | NaN | 19.0736
8298.1292 | 398.1162 | 183.8092 | 166.0839 | 168.0367 | 178.838 | 199.0223 | 237.688 | 240.2505 | NaN | NaN | NaN | 512.3432 | 128.9468 | NaN | NaN | 111.3354 | -15.3342 | NaN | NaN | NaN | 502.564 | 916.4539 | NaN | 0.5538 | NaN | 13.2896
8299.1292 | 414.0638 | 184.0265 | 166.6888 | 168.6415 | 179.1027 | 198.1727 | 237.9011 | 239.5563 | NaN | NaN | NaN | 514.7767 | 128.4743 | NaN | NaN | 115.9385 | NaN | NaN | NaN | NaN | 499.7125 | 907.3947 | NaN | 6.6023 | NaN | 20.0979
8300.1292 | 425.0274 | 184.2164 | 167.419 | 168.2862 | 179.5375 | 197.0038 | 237.3517 | 239.4434 | NaN | NaN | NaN | 527.2563 | 128.9532 | NaN | NaN | 118.096 | NaN | NaN | NaN | NaN | 498.5133 | 904.965 | NaN | 13.23 | NaN | 9.198
8301.1292 | 419.7699 | 183.9893 | 168.3104 | 168.4574 | 180.0954 | 196.5821 | 239.0965 | 240.3461 | NaN | NaN | NaN | 545.8313 | 127.1543 | NaN | NaN | 110.0961 | NaN | NaN | NaN | NaN | 499.9721 | 900.1652 | NaN | 12.2006 | NaN | 23.2393
8302.1292 | 419.8986 | 183.9421 | 168.5768 | 168.4984 | 180.6263 | 197.809 | 240.6579 | 239.6599 | NaN | NaN | NaN | 554.7665 | 130.4345 | NaN | NaN | 111.3359 | NaN | NaN | NaN | NaN | 498.7272 | 898.1469 | NaN | 2.7901 | NaN | 24.4365
8303.1292 | 417.1763 | 184.0945 | 168.1977 | 168.2477 | 180.874 | 198.9726 | 241.3813 | 239.1059 | NaN | NaN | NaN | 569.3551 | 134.1161 | NaN | NaN | 116.3047 | NaN | NaN | NaN | NaN | 499.8362 | 897.8201 | NaN | 8.1298 | NaN | 22.3989
8304.1292 | 425.5503 | 185.6214 | 168.7983 | 168.8648 | 181.2758 | 201.1653 | 240.9793 | 239.3894 | NaN | NaN | NaN | 577.2036 | 130.6728 | NaN | NaN | 111.5094 | -19.2283 | NaN | NaN | NaN | 493.8238 | 890.8355 | NaN | 10.6456 | NaN | 21.8571
8305.1292 | 433.9703 | 185.3477 | 168.7695 | 169.7781 | 181.5242 | 200.9445 | 241.9861 | 239.4043 | NaN | NaN | NaN | 584.9185 | 126.0866 | NaN | NaN | 123.8557 | 17.4077 | NaN | NaN | NaN | 494.7746 | 885.2551 | NaN | 9.2908 | NaN | 17.3579
8306.1292 | 442.0614 | 185.3007 | 169.4526 | 169.9563 | 181.5785 | 200.9905 | 243.0397 | 239.7267 | NaN | NaN | NaN | 587.8248 | 129.7591 | NaN | NaN | 118.7821 | NaN | NaN | NaN | NaN | 496.2574 | 883.3758 | NaN | 15.6905 | NaN | 25.3929
8307.1292 | 447.4174 | 185.8357 | 170.5034 | 170.0504 | 181.589 | 202.1496 | 243.4474 | 240.1705 | NaN | NaN | NaN | 583.2933 | 132.6704 | NaN | NaN | 118.6858 | NaN | NaN | NaN | NaN | 493.4842 | 878.3699 | NaN | 4.8701 | NaN | 14.9625
8308.1292 | 450.1437 | 185.6935 | 170.5216 | 170.0257 | 181.707 | 202.9259 | 243.9448 | 240.2934 | NaN | NaN | NaN | 589.1776 | 132.382 | NaN | NaN | 122.1052 | NaN | NaN | NaN | NaN | 492.137 | 867.7843 | NaN | 12.076 | NaN | 9.6411
8309.1292 | 457.4328 | 185.5815 | 170.3254 | 169.6649 | 181.3369 | 203.4348 | 245.0704 | 240.5251 | NaN | NaN | NaN | 578.0668 | 130.2473 | NaN | NaN | 116.946 | NaN | NaN | NaN | NaN | 492.2279 | 868.1873 | NaN | 5.4 | NaN | 19.3619
8310.1292 | 457.5686 | 186.018 | 170.6483 | 169.6362 | 181.0344 | 202.7625 | 245.7049 | 239.6155 | NaN | NaN | NaN | 570.8309 | 125.3794 | NaN | NaN | 110.634 | NaN | NaN | NaN | NaN | 490.894 | 863.2363 | NaN | 9.5598 | NaN | 18.3856
8311.1292 | 476.897 | 186.459 | 170.7637 | 169.4035 | 180.9211 | 203.4958 | 246.5111 | 240.6033 | NaN | NaN | NaN | 550.009 | 135.1036 | NaN | NaN | 115.4014 | -18.6518 | NaN | NaN | NaN | 487.9702 | 859.7511 | NaN | 16.3913 | NaN | 23.083
8312.1292 | 475.1152 | 186.7754 | 170.6313 | 169.8166 | 181.0423 | 204.2873 | 245.9603 | 240.1367 | NaN | NaN | NaN | 533.2602 | 140.9075 | NaN | NaN | 108.0459 | 15.1619 | NaN | NaN | NaN | 488.7674 | 853.5257 | NaN | 12.9578 | NaN | 9.1884
8313.1292 | 489.8835 | 186.5353 | 170.9445 | 169.7099 | 180.9375 | 205.0757 | 247.1308 | 239.7528 | NaN | NaN | NaN | 520.991 | 130.2109 | NaN | NaN | 113.5545 | NaN | NaN | NaN | NaN | 487.7635 | 854.7771 | NaN | 8.2704 | NaN | 25.7736
8314.1292 | 486.6006 | 186.9145 | 170.6816 | 169.5423 | 180.8855 | 204.7506 | 247.406 | 241.2356 | NaN | NaN | NaN | 516.9217 | 129.2503 | NaN | NaN | 117.1798 | NaN | NaN | NaN | NaN | 488.2177 | 854.7938 | NaN | 4.6267 | NaN | 22.5613
8315.1292 | 483.0973 | 187.3618 | 171.0742 | 169.7592 | 180.6199 | 205.04 | 247.9276 | 241.1243 | NaN | NaN | NaN | 514.514 | 133.1479 | NaN | NaN | 103.8879 | NaN | NaN | NaN | NaN | 486.9736 | 849.5704 | NaN | 0.1544 | NaN | 29.7431
8316.1292 | 499.9493 | 187.466 | 171.181 | 169.8662 | 180.5828 | 205.1174 | 247.8097 | 240.0566 | NaN | NaN | NaN | 511.0995 | 133.5509 | NaN | NaN | 128.7466 | NaN | NaN | NaN | NaN | 484.8608 | 842.0911 | NaN | 13.2749 | NaN | 21.8535
8317.1292 | 499.9579 | 187.7343 | 171.5686 | 170.0455 | 180.8245 | 207.0294 | 248.3586 | 239.253 | NaN | NaN | NaN | 504.8191 | 122.3893 | NaN | NaN | 107.4223 | -13.7149 | NaN | NaN | NaN | 484.5282 | 839.7084 | NaN | 7.7272 | NaN | 15.7778
8318.1292 | 495.3354 | 187.3217 | 171.8835 | 169.9856 | 180.9894 | 207.4874 | 248.2187 | 238.1759 | NaN | NaN | NaN | 491.7256 | 127.9949 | NaN | NaN | 113.7364 | -17.0529 | NaN | NaN | NaN | 487.7521 | 836.7893 | NaN | 3.8347 | NaN | 17.8226
8319.1292 | 488.4267 | 187.332 | 171.8287 | 169.8453 | 181.0866 | 206.8253 | 248.6853 | 237.439 | NaN | NaN | NaN | 481.2405 | 128.7024 | NaN | NaN | 124.307 | NaN | NaN | NaN | NaN | 486.1348 | 835.95 | NaN | 2.3389 | NaN | 15.4569
8320.1292 | 481.5864 | 187.4313 | 171.3258 | 169.9976 | 181.1363 | 206.6557 | 249.542 | 238.4479 | NaN | NaN | NaN | 471.7521 | 130.265 | NaN | NaN | 116.0311 | NaN | NaN | NaN | NaN | 484.4812 | 832.8045 | NaN | 12.1802 | NaN | 17.2555
8321.1292 | 475.4349 | 186.8773 | 171.14 | 169.9622 | 181.0557 | 205.5187 | 250.6025 | 237.3288 | NaN | NaN | NaN | 462.2619 | 130.2494 | NaN | NaN | 110.5756 | NaN | NaN | NaN | NaN | 483.4107 | 829.7257 | NaN | 16.2259 | NaN | 27.7012
8322.1292 | 469.0461 | 187.0512 | 170.9604 | 170.012 | 181.2225 | 206.1752 | 250.2741 | 237.4511 | NaN | NaN | NaN | 461.5867 | 129.2254 | NaN | NaN | 114.7009 | NaN | NaN | NaN | NaN | 484.2247 | 827.0285 | NaN | 6.519 | NaN | 30.0832
8323.1292 | 468.6983 | 187.1771 | 171.7081 | 169.8677 | 180.7214 | 206.5916 | 250.688 | 237.4487 | NaN | NaN | NaN | 457.1346 | 131.4347 | NaN | NaN | 108.3538 | -15.8189 | NaN | NaN | NaN | 483.5402 | 826.1885 | NaN | 10.2424 | NaN | 18.9888
8324.1448 | 464.972 | 187.6068 | 171.9838 | 169.4747 | 180.5153 | 206.7761 | 249.9728 | 239.2605 | NaN | NaN | NaN | 450.9076 | 123.8074 | NaN | NaN | 103.5256 | -7.7892 | NaN | NaN | NaN | 486.3856 | 823.705 | NaN | 17.2266 | NaN | 22.3639
8325.1292 | 460.3559 | 188.3638 | 172.1417 | 169.3123 | 180.4349 | 208.1491 | 250.5015 | 241.315 | NaN | NaN | NaN | 451.6919 | 128.5371 | NaN | NaN | 110.2851 | NaN | NaN | NaN | NaN | 487.4471 | 821.9421 | NaN | 6.3031 | NaN | 20.8714
8326.1292 | 455.5191 | 189.1838 | 171.8986 | 169.675 | 180.2354 | 207.8791 | 251.8151 | 241.727 | NaN | NaN | NaN | 447.0858 | 130.7271 | NaN | NaN | 116.5717 | NaN | NaN | NaN | NaN | 484.4706 | 816.5685 | NaN | 28.192 | NaN | 16.0449
8327.1292 | 448.4784 | 189.2857 | 172.8193 | 169.7675 | 180.3147 | 208.2182 | 251.1288 | 240.366 | NaN | NaN | NaN | 444.1812 | 130.3385 | NaN | NaN | 113.6041 | NaN | NaN | NaN | NaN | 484.7305 | 816.8251 | NaN | 20.7452 | NaN | 24.5021
8328.1292 | 448.0672 | 188.9087 | 172.6932 | 169.6953 | 180.3813 | 207.247 | 251.4019 | 239.4291 | NaN | NaN | NaN | 457.4668 | 132.837 | NaN | NaN | 130.5671 | NaN | NaN | NaN | NaN | 491.8583 | 813.0636 | NaN | 5.1888 | NaN | 13.1891
8329.1292 | 463.6117 | 189.1905 | 172.5429 | 170.27 | 180.6271 | 206.5687 | 251.9105 | 242.3979 | NaN | NaN | NaN | 464.701 | 128.7726 | NaN | NaN | 112.1632 | 13.0725 | NaN | NaN | NaN | 488.3102 | 810.1858 | NaN | 9.3449 | NaN | 15.8126
8330.1292 | 457.0895 | 189.3968 | 172.8089 | 170.4863 | 180.4606 | 207.209 | 251.6404 | 242.8107 | NaN | NaN | NaN | 462.7741 | 133.5089 | NaN | NaN | 113.696 | NaN | NaN | NaN | NaN | 487.935 | 807.9617 | NaN | 26.6581 | NaN | 17.087
8331.1292 | 458.1954 | 190.0922 | 173.138 | 170.5762 | 180.3576 | 208.0943 | 252.3391 | 242.375 | NaN | NaN | NaN | 460.2199 | 126.0843 | NaN | NaN | 119.3807 | NaN | NaN | NaN | NaN | 487.0461 | 807.0738 | NaN | 25.4971 | NaN | 19.0355
8332.1292 | 465.9369 | 190.482 | 173.2767 | 170.6281 | 180.6537 | 208.3702 | 252.1452 | 243.0511 | NaN | NaN | NaN | 461.2457 | 128.6902 | NaN | NaN | 115.1731 | NaN | NaN | NaN | NaN | 484.0678 | 801.7401 | NaN | 18.3948 | NaN | 18.4358
8333.1292 | 463.5496 | 190.8714 | 172.9042 | 170.8785 | 181.1698 | 207.7639 | 252.8333 | 243.4285 | NaN | NaN | NaN | 453.9444 | 124.5178 | NaN | NaN | 104.8725 | NaN | NaN | NaN | NaN | 484.7521 | 800.6369 | NaN | 11.4262 | NaN | 24.5794
8334.1292 | 467.4692 | 191.0257 | 172.9573 | 171.0352 | 181.0209 | 207.5549 | 251.7197 | 245.1992 | NaN | NaN | NaN | 455.2386 | 126.8479 | NaN | NaN | 107.7684 | NaN | NaN | NaN | NaN | 483.5507 | 796.1673 | NaN | 9.0222 | NaN | 9.0077
8335.1292 | 465.1295 | 191.5854 | 172.891 | 171.1284 | 181.1954 | 210.2378 | 252.0077 | 245.9938 | NaN | NaN | NaN | 458.8089 | 124.0084 | NaN | NaN | 100.7437 | NaN | NaN | NaN | NaN | 485.7344 | 797.6924 | NaN | 2.1462 | NaN | 11.6775
8336.1292 | 469.3273 | 191.6082 | 173.4965 | 171.1607 | 181.1965 | 211.4076 | 252.5278 | 246.2145 | NaN | NaN | NaN | 455.7677 | 124.6774 | NaN | NaN | 105.9855 | -16.4749 | NaN | NaN | NaN | 484.6265 | 788.2469 | NaN | 6.9671 | NaN | 16.8489
8337.1292 | 467.3792 | 192.1273 | 173.4287 | 171.256 | 181.5648 | 209.9741 | 253.2028 | 245.8816 | NaN | NaN | NaN | 455.4697 | 123.8433 | NaN | NaN | 117.291 | -2.3261 | NaN | NaN | NaN | 483.8627 | 789.5454 | NaN | 17.9731 | NaN | 24.7511
8338.1292 | 475.5104 | 192.6759 | 173.7356 | 171.9249 | 181.905 | 210.2179 | 252.5433 | 246.7269 | NaN | NaN | NaN | 455.3835 | 130.7251 | NaN | NaN | 110.6785 | NaN | NaN | NaN | NaN | 483.6085 | 785.8311 | NaN | -3.4852 | NaN | 19.5299
8339.1292 | 467.7134 | 192.7203 | 174.8009 | 172.3834 | 181.8313 | 209.8269 | 253.4901 | 248.5102 | NaN | NaN | NaN | 448.8414 | 129.493 | NaN | NaN | 105.2222 | NaN | NaN | NaN | NaN | 481.8117 | 784.3572 | NaN | 1.3103 | NaN | 23.3323
8340.1292 | 479.2509 | 193.6219 | 174.343 | 172.3825 | 182.3343 | 209.5662 | 253.4911 | 248.1753 | NaN | NaN | NaN | 448.5106 | 124.5214 | NaN | NaN | 109.2039 | NaN | NaN | NaN | NaN | 480.4096 | 779.1438 | NaN | 14.9298 | NaN | 13.9607
8341.1292 | 477.2586 | 194.2287 | 174.3341 | 173.3592 | 182.6849 | 208.895 | 253.8809 | 246.8137 | NaN | NaN | NaN | 440.4162 | 133.1803 | NaN | NaN | 114.0744 | -19.3193 | NaN | NaN | NaN | 479.9118 | 773.6034 | NaN | 12.0275 | NaN | 22.5419
8342.1292 | 475.3427 | 195.0033 | 173.9944 | 173.5965 | 183.5046 | 209.2908 | 255.1477 | 247.0214 | NaN | NaN | NaN | 439.0883 | 135.925 | NaN | NaN | 116.9095 | 15.8455 | NaN | NaN | NaN | 480.9307 | 771.2104 | NaN | 15.6331 | NaN | 13.0896
8343.1292 | 493.5684 | 195.4699 | 173.7507 | 173.688 | 183.8094 | 209.2951 | 254.8891 | 246.6567 | NaN | NaN | NaN | 448.9708 | 130.4502 | NaN | NaN | 107.6172 | NaN | NaN | NaN | NaN | 482.7032 | 770.6975 | NaN | 35.2748 | NaN | 26.8247
8344.1292 | 503.5373 | 195.6758 | 173.768 | 173.8965 | 183.8045 | 208.9794 | 255.1513 | 246.9994 | NaN | NaN | NaN | 443.265 | 128.1497 | NaN | NaN | 119.833 | NaN | NaN | NaN | NaN | 480.1704 | 772.1154 | NaN | 6.7912 | NaN | 12.2378
8345.1292 | 497.2397 | 196.4578 | 174.0574 | 174.1438 | 184.2413 | 209.8436 | 255.7058 | 245.5996 | NaN | NaN | NaN | 442.7947 | 135.1338 | NaN | NaN | 116.5642 | NaN | NaN | NaN | NaN | 477.7284 | 763.8088 | NaN | 32.1882 | NaN | 11.8472
8346.1292 | 515.8358 | 197.0923 | 174.7486 | 174.1201 | 184.1135 | 210.0565 | 257.4592 | 244.8966 | NaN | NaN | NaN | 439.8117 | 129.6936 | NaN | NaN | 123.2087 | NaN | NaN | NaN | NaN | 478.1415 | 757.947 | NaN | 7.9024 | NaN | 18.3094
8347.1292 | 510.4992 | 197.1308 | 175.2071 | 174.4385 | 183.9746 | 209.8017 | 257.3311 | 244.6849 | NaN | NaN | NaN | 440.4673 | 128.4207 | NaN | NaN | 111.0235 | NaN | NaN | NaN | NaN | 477.8984 | 745.0823 | NaN | 3.3005 | NaN | 17.0582
8348.1292 | 502.9002 | 196.9163 | 175.7112 | 174.3549 | 183.9645 | 209.7547 | 257.0231 | 245.1544 | NaN | NaN | NaN | 447.0259 | 119.6478 | NaN | NaN | 108.3634 | NaN | NaN | NaN | NaN | 478.4519 | 735.2249 | NaN | 20.842 | NaN | 25.9875
8349.1292 | 498.7233 | 197.4549 | 175.8864 | 174.43 | 183.8269 | 208.3272 | 255.6579 | 244.2769 | NaN | NaN | NaN | 442.1672 | 134.6763 | NaN | NaN | 114.0492 | -18.1555 | NaN | NaN | NaN | 475.8002 | 731.5972 | NaN | 31.6695 | NaN | 16.7491
8350.1292 | 498.6891 | 197.2288 | 175.8448 | 174.5415 | 183.6571 | 207.4248 | 255.6953 | 245.4325 | NaN | NaN | NaN | 445.2813 | 122.2549 | NaN | NaN | 110.018 | 17.061 | NaN | NaN | NaN | 481.744 | 726.1717 | NaN | 34.3644 | NaN | 23.3101
8351.1292 | 492.5774 | 197.2001 | 176.4187 | 174.6271 | 183.8503 | 207.5186 | 256.1858 | 245.8481 | NaN | NaN | NaN | 441.8654 | 133.8913 | NaN | NaN | 110.0774 | NaN | NaN | NaN | NaN | 480.7746 | 719.7465 | NaN | 25.4354 | NaN | 31.3928
8352.1292 | 506.8549 | 197.2847 | 176.3155 | 174.917 | 183.6226 | 207.4909 | 257.3282 | 245.3924 | NaN | NaN | NaN | 447.8275 | 132.0315 | NaN | NaN | 105.8645 | NaN | NaN | NaN | NaN | 478.6561 | 710.581 | NaN | 37.6042 | NaN | 22.4874
8353.1292 | 515.9301 | 197.636 | 177.1967 | 174.6146 | 183.6454 | 208.4466 | 259.2036 | 245.9811 | NaN | NaN | NaN | 446.4104 | 131 | NaN | NaN | 30.3975 | NaN | NaN | NaN | NaN | 476.4692 | 702.7151 | NaN | 9.3242 | NaN | 20.5538
8354.1292 | 512.4313 | 198.5665 | 177.4489 | 174.4442 | 183.8956 | 210.5027 | 260.2582 | 246.5874 | NaN | NaN | NaN | 442.6165 | 123.7322 | NaN | NaN | 26.4456 | NaN | NaN | NaN | NaN | 476.8857 | 700.0811 | NaN | 2.8236 | NaN | 22.6151
8355.1292 | 520.2197 | 199.3165 | 177.9007 | 174.7742 | 184.1876 | 211.2509 | 259.8691 | 246.7609 | NaN | NaN | NaN | 438.5419 | 128.2739 | NaN | NaN | 45.9654 | NaN | NaN | NaN | NaN | 477.7859 | 696.6014 | NaN | 32.1612 | NaN | 20.6366
8356.1292 | 519.8668 | 199.9984 | 178.3386 | 175.0085 | 184.3228 | 210.9306 | 261.0063 | 247.5662 | NaN | NaN | NaN | 434.8255 | 132.5748 | NaN | NaN | 64.7423 | -18.2683 | NaN | NaN | NaN | 477.0026 | 698.6997 | NaN | 23.1555 | NaN | 15.5976
8357.1292 | 517.6353 | 200.0922 | 178.7505 | 175.5082 | 184.6323 | 211.4328 | 261.9479 | 247.6194 | NaN | NaN | NaN | 433.3789 | 128.3358 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 476.9309 | 706.0858 | NaN | 3.332 | NaN | 12.393
8358.1292 | 528.2801 | 200.964 | 178.4872 | 176.2002 | 184.931 | 210.8968 | 262.4445 | 246.7124 | NaN | NaN | NaN | 431.2109 | 130.3821 | NaN | NaN | 23.5856 | NaN | NaN | NaN | NaN | 475.595 | 708.2017 | NaN | 6.6364 | NaN | 21.7463
8359.1292 | 518.7525 | 200.5202 | 178.2899 | 176.3637 | 185.3909 | 210.5308 | 261.904 | 246.9583 | NaN | NaN | NaN | 429.1589 | 126.59 | NaN | NaN | 32.7493 | NaN | NaN | NaN | NaN | 475.2126 | 714.3561 | NaN | 27.1063 | NaN | 24.1529
8360.1292 | 507.9409 | 200.5362 | 178.0564 | 176.2628 | 185.7653 | 211.5817 | 262.5885 | 246.471 | NaN | NaN | NaN | 426.7795 | 122.6013 | NaN | NaN | 57.9745 | NaN | NaN | NaN | NaN | 475.1426 | 719.6631 | NaN | 12.4434 | NaN | 14.8995
8361.1292 | 513.2269 | 201.9724 | 178.5918 | 177.3665 | 186.1461 | 212.1076 | 262.4887 | 248.8076 | NaN | NaN | NaN | 423.8329 | 122.5927 | NaN | NaN | 48.3257 | NaN | NaN | NaN | NaN | 474.8453 | 729.8273 | NaN | 10.7123 | NaN | 25.9216
8362.1292 | 507.2099 | 202.2332 | 178.5472 | 177.464 | 186.5325 | 211.9535 | 263.0503 | 249.5381 | NaN | NaN | NaN | 421.1609 | 125.9826 | NaN | NaN | 11.7085 | NaN | NaN | NaN | NaN | 472.5157 | 721.6984 | NaN | 23.3767 | NaN | 17.4955
8363.1292 | 501.1205 | 202.8229 | 178.6235 | 177.722 | 186.8626 | 213.0515 | 263.7261 | 251.0578 | NaN | NaN | NaN | 423.1888 | 129.3632 | NaN | NaN | -14.0948 | NaN | NaN | NaN | NaN | 474.1371 | 713.2884 | NaN | 28.3172 | NaN | 18.3153
8364.1292 | 510.3656 | 202.985 | 178.1916 | 177.953 | 187.2533 | 212.972 | 263.6956 | 250.774 | NaN | NaN | NaN | 419.947 | 132.1108 | NaN | NaN | 41.2687 | 16.3301 | NaN | NaN | NaN | 474.821 | 704.6444 | NaN | 2.85 | NaN | 19.5907
8365.1292 | 526.9701 | 203.2729 | 177.6585 | 177.8062 | 187.3873 | 213.0631 | 264.9538 | 251.0184 | NaN | NaN | NaN | 418.1415 | 126.0632 | NaN | NaN | 17.2937 | NaN | NaN | NaN | NaN | 474.056 | 698.6865 | NaN | 8.5938 | NaN | 16.796
8366.1292 | 513.3134 | 203.9427 | 177.7934 | 177.9881 | 187.523 | 212.7122 | 264.1556 | 250.7721 | NaN | NaN | NaN | 416.292 | 129.7741 | NaN | NaN | 9.6315 | NaN | NaN | NaN | NaN | 474.399 | 684.6056 | NaN | 9.2838 | NaN | 22.2618
8367.1292 | 511.9916 | 203.821 | 177.64 | 177.8903 | 187.8869 | 211.8374 | 263.0736 | 251.2319 | NaN | NaN | NaN | 419.7927 | 128.9372 | NaN | NaN | 38.8517 | NaN | NaN | NaN | NaN | 475.0299 | 668.8954 | NaN | 4.5574 | NaN | 21.0823
8368.1292 | 504.4597 | 204.2953 | 177.2079 | 178.1803 | 188.1855 | 211.6696 | 264.4185 | 250.8316 | NaN | NaN | NaN | 455.4543 | 136.2905 | NaN | NaN | 73.8602 | NaN | NaN | NaN | NaN | 486.2852 | 660.7467 | NaN | 9.1683 | NaN | 9.5082
8369.1292 | 509.4387 | 204.2266 | 177.0964 | 178.5094 | 188.2186 | 210.9721 | 263.6614 | 250.6104 | NaN | NaN | NaN | 486.5407 | 133.4351 | NaN | NaN | 37.4586 | NaN | NaN | NaN | NaN | 482.9412 | 658.4152 | NaN | 7.1508 | NaN | 26.0249
8370.1292 | 523.7761 | 204.4866 | 177.8005 | 178.9016 | 188.5513 | 210.8865 | 264.3626 | 249.5512 | NaN | NaN | NaN | 489.7044 | 129.2084 | NaN | NaN | 64.3692 | NaN | NaN | NaN | NaN | 481.3286 | 667.0901 | NaN | 19.8976 | NaN | 30.356
8371.1292 | 527.0537 | 205.7509 | 177.5323 | 179.032 | 188.5011 | 211.0909 | 264.9459 | 249.3665 | NaN | NaN | NaN | 503.0259 | 129.9219 | NaN | NaN | 41.9259 | -17.6354 | NaN | NaN | NaN | 482.9133 | 668.1157 | NaN | 14.7374 | NaN | 16.2375
8372.1292 | 544.3815 | 207.0529 | 177.2985 | 178.7903 | 189.486 | 211.3481 | 265.3369 | 248.5486 | NaN | NaN | NaN | 525.0515 | 126.4582 | NaN | NaN | 35.1861 | 6.3238 | NaN | NaN | NaN | 486.9014 | 671.7934 | NaN | 15.4887 | NaN | 17.8374
8373.1292 | 544.3733 | 207.9497 | 177.3933 | 178.7098 | 189.236 | 213.4084 | 265.0854 | 249.2813 | NaN | NaN | NaN | 533.5576 | 130.3992 | NaN | NaN | 39.2284 | NaN | NaN | NaN | NaN | 481.8597 | 674.6844 | NaN | 31.5971 | NaN | 19.2264
8374.1292 | 536.4666 | 207.4584 | 178.6355 | 178.9734 | 189.3451 | 214.5389 | 265.1411 | 249.2381 | NaN | NaN | NaN | 524.2394 | 133.5249 | NaN | NaN | 30.6663 | NaN | NaN | NaN | NaN | 481.3575 | 676.8207 | NaN | 13.0825 | NaN | 22.0978
8375.1292 | 531.7627 | 207.6702 | 178.3124 | 179.2778 | 189.249 | 217.8461 | 266.3566 | 250.6694 | NaN | NaN | NaN | 510.3819 | 131.1863 | NaN | NaN | 39.3309 | NaN | NaN | NaN | NaN | 482.4055 | 676.256 | NaN | 22.3016 | NaN | 28.1546
8376.1292 | 530.3525 | 208.1792 | 178.1606 | 179.6897 | 189.4666 | 217.2718 | 267.155 | 251.6374 | NaN | NaN | NaN | 497.2636 | 135.7426 | NaN | NaN | 29.939 | NaN | NaN | NaN | NaN | 482.6624 | 674.9572 | NaN | 7.394 | NaN | 17.2297
8377.1292 | 529.9293 | 209.0191 | 179.4663 | 179.5687 | 190.177 | 216.5999 | 267.1962 | 253.3867 | NaN | NaN | NaN | 519.9235 | 123.8723 | NaN | NaN | 72.6689 | NaN | NaN | NaN | NaN | 480.4532 | 678.0904 | NaN | 9.1667 | NaN | 26.9666
8378.1292 | 523.3011 | 210.9293 | 179.4463 | 179.9789 | 190.2353 | 217.0918 | 267.579 | 255.4242 | NaN | NaN | NaN | 528.3092 | 132.3478 | NaN | NaN | 48.9523 | -16.7309 | NaN | NaN | NaN | 484.6677 | 674.7779 | NaN | 30.3436 | NaN | 22.5148
8379.1292 | 521.5841 | 211.3654 | 180.147 | 180.4107 | 190.895 | 216.8448 | 267.2073 | 257.032 | NaN | NaN | NaN | 539.7054 | 127.0997 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 486.3417 | 667.4738 | NaN | 22.6687 | NaN | 12.6416
8380.1292 | 521.4634 | 211.3964 | 180.7052 | 180.877 | 191.0927 | 216.6082 | 267.4134 | 256.1358 | NaN | NaN | NaN | 544.0071 | 129.452 | NaN | NaN | 52.4648 | NaN | NaN | NaN | NaN | 485.5539 | 669.1842 | NaN | 12.2087 | NaN | 14.7384
8381.1292 | 541.826 | 212.223 | 180.8087 | 182.171 | 191.8625 | 216.2707 | 269.2451 | 257.0221 | NaN | NaN | NaN | 544.7854 | 130.3175 | NaN | NaN | 29.4003 | NaN | NaN | NaN | NaN | 485.9817 | 670.4915 | NaN | 10.2488 | NaN | 20.6158
8382.1292 | 540.2962 | 212.8677 | 181.0506 | 183.0217 | 192.4534 | 216.3845 | 270.2261 | 256.4767 | NaN | NaN | NaN | 543.4457 | 128.7037 | NaN | NaN | 64.6261 | NaN | NaN | NaN | NaN | 484.6025 | 673.4653 | NaN | 7.1724 | NaN | 16.1987
8383.1292 | 551.7997 | 213.5695 | 180.5426 | 183.0005 | 192.5108 | 216.1269 | 270.5326 | 257.402 | NaN | NaN | NaN | 566.8444 | 124.1377 | NaN | NaN | 50.9062 | NaN | NaN | NaN | NaN | 488.2261 | 674.9308 | NaN | 1.2704 | NaN | 12.5035
8384.1292 | 556.5701 | 214.3887 | 180.2448 | 183.3312 | 192.9731 | 216.816 | 271.5519 | 258.7234 | NaN | NaN | NaN | 556.357 | 128.0952 | NaN | NaN | 44.3821 | NaN | NaN | NaN | NaN | 483.6296 | 679.7239 | NaN | 10.2747 | NaN | 13.2762
8385.1292 | 558.2543 | 214.7613 | 181.1687 | 183.4975 | 193.1721 | 217.1997 | 271.9532 | 258.5578 | NaN | NaN | NaN | 544.692 | 130.4374 | NaN | NaN | NaN | -16.1138 | NaN | NaN | NaN | 481.6578 | 684.0281 | NaN | 9.2902 | NaN | 16.5948
8386.1292 | 546.5165 | 214.7742 | 181.5117 | 183.7485 | 193.2648 | 217.1494 | 273.7077 | 259.7576 | NaN | NaN | NaN | 536.5337 | 130.3607 | NaN | NaN | NaN | 10.983 | NaN | NaN | NaN | 482.2275 | 691.7274 | NaN | 28.4322 | NaN | 30.485
8387.1292 | 552.4686 | 214.7741 | 181.4426 | 183.743 | 193.6527 | 216.7235 | 273.4062 | 260.1024 | NaN | NaN | NaN | 532.9215 | 129.8432 | NaN | NaN | 14.058 | NaN | NaN | NaN | NaN | 484.2708 | 696.4499 | NaN | 15.6448 | NaN | 18.3316
8388.1292 | 565.6355 | 215.5592 | 181.2492 | 184.3062 | 193.8617 | 218.9139 | 272.7917 | 261.9143 | NaN | NaN | NaN | 526.0805 | 131.068 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 482.2827 | 693.1764 | NaN | 3.3165 | NaN | 17.3293
8389.1292 | 558.5185 | 215.907 | 181.9362 | 184.5797 | 193.9348 | 221.3626 | 272.4631 | 261.9072 | NaN | NaN | NaN | 536.7717 | 127.6754 | NaN | NaN | 32.0344 | NaN | NaN | NaN | NaN | 487.4874 | 695.844 | NaN | 7.5808 | NaN | 23.2912
8390.1292 | 571.471 | 216.2839 | 181.8681 | 185.0419 | 194.0359 | 223.6439 | 274.4021 | 261.9304 | NaN | NaN | NaN | 553.6219 | 128.8593 | NaN | NaN | 70.5476 | NaN | NaN | NaN | NaN | 489.858 | 696.0023 | NaN | 20.5531 | NaN | 16.1832
8391.1292 | 569.7334 | 216.6367 | 181.3922 | 184.7218 | 193.9055 | 225.5816 | 275.7736 | 261.4802 | NaN | NaN | NaN | 567.2139 | 128.9805 | NaN | NaN | 18.6985 | -17.5322 | NaN | NaN | NaN | 486.2423 | 695.3621 | NaN | 6.7666 | NaN | 24.7286
8392.1292 | 565.8331 | 217.2687 | 181.2391 | 184.5963 | 193.696 | 225.6118 | 276.8963 | 263.3421 | NaN | NaN | NaN | 555.7732 | 129.0882 | NaN | NaN | 8.6296 | 13.4236 | NaN | NaN | NaN | 484.0879 | 693.4712 | NaN | 30.4346 | NaN | 22.4377
8393.1292 | 564.6053 | 217.1546 | 180.8085 | 184.8714 | 194.1985 | 227.7664 | 277.1576 | 262.3134 | NaN | NaN | NaN | 539.2794 | 128.7407 | NaN | NaN | 43.8784 | NaN | NaN | NaN | NaN | 483.6824 | 690.7094 | NaN | 16.685 | NaN | 14.4039
8394.1292 | 553.3484 | 217.6257 | 181.0346 | 184.7774 | 194.1702 | 227.6128 | 277.3352 | 262.0153 | NaN | NaN | NaN | 546.4025 | 133.2247 | NaN | NaN | 58.7733 | NaN | NaN | NaN | NaN | 488.6755 | 685.7026 | NaN | 12.4093 | NaN | 17.6268
8395.1292 | 545.5348 | 218.0909 | 181.2306 | 184.729 | 194.1555 | 227.9398 | 277.2333 | 262.7808 | NaN | NaN | NaN | 541.7658 | 132.1571 | NaN | NaN | 29.9131 | NaN | NaN | NaN | NaN | 487.8583 | 686.9978 | NaN | 11.5704 | NaN | 18.6128
8396.1292 | 534.8897 | 218.973 | 181.3736 | 185.3778 | 194.6159 | 226.9943 | 276.5124 | 262.1387 | NaN | NaN | NaN | 545.8254 | 126.0658 | NaN | NaN | -14.3122 | NaN | NaN | NaN | NaN | 489.4385 | 691.6706 | NaN | 8.7506 | NaN | 20.8039
8397.1292 | 530.5047 | 219.5482 | 180.9147 | 185.0381 | 194.8676 | 226.3922 | 276.6494 | 262.5839 | NaN | NaN | NaN | 545.9166 | 123.4939 | NaN | NaN | NaN | -18.8146 | NaN | NaN | NaN | 488.3008 | 687.522 | NaN | 7.3481 | NaN | 13.5571
8398.1292 | 523.206 | 220.0471 | 181.4126 | 184.7171 | 195.3219 | 226.0285 | 277.5451 | 263.1464 | NaN | NaN | NaN | 554.0701 | 124.9979 | NaN | NaN | -17.3261 | -13.2891 | NaN | NaN | NaN | 492.1249 | 688.9157 | NaN | 26.1019 | NaN | 19.2828
8399.1292 | 516.0887 | 220.1376 | 181.7437 | 185.1702 | 195.2645 | 225.3167 | 277.0924 | 262.9901 | NaN | NaN | NaN | 544.3305 | 127.3574 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 489.8904 | 688.612 | NaN | 3.2738 | NaN | 18.554
8400.1292 | 514.1911 | 221.1536 | 182.0693 | 184.9257 | 195.1723 | 224.5919 | 277.3017 | 264.0355 | NaN | NaN | NaN | 533.616 | 123.2397 | NaN | NaN | 49.9816 | NaN | NaN | NaN | NaN | 488.7124 | 688.314 | NaN | 15.1782 | NaN | 23.9687
8401.1292 | 513.6495 | 222.2153 | 182.5104 | 185.2427 | 195.5736 | 223.5812 | 277.6501 | 263.9149 | NaN | NaN | NaN | 527.4041 | 121.1171 | NaN | NaN | 12.2853 | NaN | NaN | NaN | NaN | 489.8993 | 685.0246 | NaN | 10.2472 | NaN | 26.3366
8402.1292 | 528.9457 | 222.9409 | 182.7125 | 185.0503 | 195.9474 | 223.1248 | 278.8287 | 263.5819 | NaN | NaN | NaN | 527.1168 | 127.2648 | NaN | NaN | 23.7833 | NaN | NaN | NaN | NaN | 487.8257 | 684.2617 | NaN | 3.9241 | NaN | 26.896
8403.1292 | 519.0688 | 222.8637 | 182.6527 | 185.18 | 196.2083 | 222.9434 | 279.0475 | 262.7996 | NaN | NaN | NaN | 534.4872 | 121.5535 | NaN | NaN | 14.619 | -17.2446 | NaN | NaN | NaN | 492.297 | 683.6024 | NaN | 19.8883 | NaN | 27.1198
8404.1292 | 516.1816 | 222.9266 | 183.1737 | 185.5395 | 196.457 | 223.5581 | 278.4976 | 262.1747 | NaN | NaN | NaN | 549.6748 | 130.0912 | NaN | NaN | NaN | -14.3554 | NaN | NaN | NaN | 493.8177 | 685.247 | NaN | 28.0916 | NaN | 16.0878
8405.1292 | 540.7478 | 223.4682 | 183.6402 | 185.809 | 196.3631 | 223.8641 | 280.3454 | 261.4781 | NaN | NaN | NaN | 551.6336 | 123.8571 | NaN | NaN | 32.5655 | NaN | NaN | NaN | NaN | 493.0704 | 685.9363 | NaN | 4.9234 | NaN | 18.3608
8406.1292 | 558.8431 | 223.9022 | 183.7479 | 185.5958 | 196.7576 | 224.4234 | 280.4578 | 262.4346 | NaN | NaN | NaN | 563.4235 | 126.1322 | NaN | NaN | -10.8267 | NaN | NaN | NaN | NaN | 490.2684 | 685.3999 | NaN | 18.7678 | NaN | 21.6726
8407.1292 | 559.1471 | 223.9727 | 183.4037 | 185.5212 | 196.8868 | 224.1372 | 282.0813 | 261.6981 | NaN | NaN | NaN | 561.6614 | 129.5902 | NaN | NaN | 14.0345 | NaN | NaN | NaN | NaN | 488.4288 | 682.0115 | NaN | 25.5914 | NaN | 17.4808
8408.1292 | 560.423 | 224.6354 | 183.6799 | 185.6845 | 197.5435 | 224.5326 | 282.2411 | 260.4446 | NaN | NaN | NaN | 554.218 | 131.1543 | NaN | NaN | 35.8636 | NaN | NaN | NaN | NaN | 494.4189 | 684.9181 | NaN | 12.2865 | NaN | 16.1444
8409.1292 | 551.6307 | 224.7522 | 184.9903 | 185.9595 | 197.7782 | 224.1458 | 282.3846 | 262.3702 | NaN | NaN | NaN | 539.3014 | 127.6552 | NaN | NaN | NaN | -16.0306 | NaN | NaN | NaN | 493.2809 | 685.1057 | NaN | 1.2182 | NaN | 14.4958
8410.1292 | 542.4368 | 225.6406 | 186.148 | 186.1485 | 198.5037 | 223.9765 | 283.4501 | 261.3036 | NaN | NaN | NaN | 548.2248 | 126.3205 | NaN | NaN | 26.086 | NaN | NaN | NaN | NaN | 493.5983 | 680.5393 | NaN | 10.2139 | NaN | 12.6927
8411.1292 | 536.3945 | 226.7995 | 185.7693 | 186.6203 | 198.4526 | 222.3797 | 282.5508 | 260.2489 | NaN | NaN | NaN | 564.4496 | 127.7098 | NaN | NaN | 29.2702 | NaN | NaN | NaN | NaN | 500.0022 | 678.8319 | NaN | 17.6202 | NaN | 25.2285
8412.1292 | 538.6586 | 226.9268 | 185.7244 | 186.9752 | 198.3997 | 221.8233 | 282.9915 | 260.0322 | NaN | NaN | NaN | 600.646 | 129.0348 | NaN | NaN | 33.9459 | NaN | NaN | NaN | NaN | 499.0892 | 677.3072 | NaN | 37.1229 | NaN | 19.772
8413.1292 | 535.0387 | 226.781 | 186.7838 | 187.1874 | 198.1817 | 223.1679 | 283.4894 | 259.6313 | NaN | NaN | NaN | 603.028 | 127.9293 | NaN | NaN | 14.6579 | NaN | NaN | NaN | NaN | 492.3676 | 676.6354 | NaN | 16.2314 | NaN | 22.6828
8414.1292 | 538.4074 | 227.3724 | 187.293 | 187.4202 | 198.4473 | 222.7772 | 283.3845 | 260.5435 | NaN | NaN | NaN | 592.9978 | 126.0443 | NaN | NaN | 45.655 | NaN | NaN | NaN | NaN | 492.2007 | 675.0132 | NaN | 25.1417 | NaN | 14.6287
8415.1292 | 547.6758 | 228.3261 | 187.4173 | 187.746 | 198.7297 | 222.9598 | 284.1852 | 260.6348 | NaN | NaN | NaN | 579.4444 | 132.3492 | NaN | NaN | 40.4556 | -17.5068 | NaN | NaN | NaN | 489.4096 | 672.6734 | NaN | 5.8608 | NaN | 10.4361
8416.1292 | 563.327 | 229.2619 | 186.914 | 187.8486 | 199.1496 | 223.7001 | 284.9402 | 260.8174 | NaN | NaN | NaN | 562.3161 | 125.8197 | NaN | NaN | 30.6435 | 3.2687 | NaN | NaN | NaN | 491.1065 | 676.1721 | NaN | 6.6853 | NaN | 15.142
8417.1292 | 572.7112 | 230.1765 | 186.789 | 187.9636 | 199.4494 | 223.4238 | 286.0052 | 261.0786 | NaN | NaN | NaN | 566.7633 | 127.6312 | NaN | NaN | 50.5437 | NaN | NaN | NaN | NaN | 503.1269 | 675.5125 | NaN | 10.2465 | NaN | 15.1179
8418.1292 | 564.4897 | 230.7152 | 187.7672 | 188.3008 | 199.5247 | 223.2057 | 287.1777 | 261.4949 | NaN | NaN | NaN | 587.5921 | 128.3892 | NaN | NaN | 27.5435 | NaN | NaN | NaN | NaN | 499.0944 | 680.5292 | NaN | 8.1663 | NaN | 16.1084
8419.1292 | 572.0588 | 231.4397 | 187.8058 | 188.48 | 199.8479 | 222.8955 | 287.676 | 261.1999 | NaN | NaN | NaN | 573.1461 | 130.6304 | NaN | NaN | 41.8336 | NaN | NaN | NaN | NaN | 496.9951 | 680.3257 | NaN | 15.266 | NaN | 12.7045
8420.1292 | 561.2738 | 231.8302 | 188.068 | 188.8957 | 200.0236 | 223.769 | 289.0582 | 261.8229 | NaN | NaN | NaN | 556.4977 | 127.6923 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 494.3416 | 676.8979 | NaN | 13.8678 | NaN | 18.3256
8421.1292 | 554.4949 | 232.6258 | 187.8926 | 189.4405 | 199.9441 | 223.6923 | 288.7933 | 261.6852 | NaN | NaN | NaN | 539.5877 | 128.3389 | NaN | NaN | 40.7477 | NaN | NaN | NaN | NaN | 495.6988 | 674.8109 | NaN | 8.4751 | NaN | 27.9312
8422.1292 | 549.0865 | 233.1495 | 188.0426 | 189.8818 | 200.103 | 224.1217 | 288.6703 | 262.967 | NaN | NaN | NaN | 535.9845 | 128.0231 | NaN | NaN | 31.8983 | -19.9763 | NaN | NaN | NaN | 498.6585 | 674.8835 | NaN | 35.5264 | NaN | 13.6359
8423.1292 | 542.1078 | 233.1217 | 188.9908 | 189.9907 | 199.9915 | 224.2302 | 289.2494 | 262.3837 | NaN | NaN | NaN | 523.0403 | 127.4751 | NaN | NaN | NaN | -14.4124 | NaN | NaN | NaN | 498.9824 | 676.2127 | NaN | 3.8064 | NaN | 29.9051
8424.1292 | 537.1668 | 233.4511 | 189.0667 | 190.3057 | 200.014 | 224.4156 | 290.003 | 263.3323 | NaN | NaN | NaN | 528.1645 | 126.7352 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 505.9108 | 680.7304 | NaN | 5.7901 | NaN | 25.3544
8425.1292 | 531.3702 | 234.0233 | 190.0927 | 191.1171 | 200.4109 | 224.696 | 290.6135 | 263.982 | NaN | NaN | NaN | 542.369 | 125.9801 | NaN | NaN | -17.993 | NaN | NaN | NaN | NaN | 508.0992 | 681.08 | NaN | 13.3604 | NaN | 16.5032
8426.1292 | 525.0297 | 234.5355 | 189.9935 | 191.2424 | 200.4052 | 224.3209 | 291.1262 | 264.534 | NaN | NaN | NaN | 548.1236 | 129.0046 | NaN | NaN | 21.1992 | NaN | NaN | NaN | NaN | 502.4602 | 679.0932 | NaN | 3.0959 | NaN | 26.6762
8427.1292 | 521.769 | 234.9186 | 190.5453 | 191.2588 | 200.3023 | 224.6348 | 290.6513 | 265.3786 | NaN | NaN | NaN | 533.5948 | 130.5882 | NaN | NaN | 49.9021 | NaN | NaN | NaN | NaN | 503.9336 | 676.5672 | NaN | 18.8662 | NaN | 16.8014
8428.1292 | 537.6338 | 235.3552 | 190.3151 | 191.1346 | 200.2499 | 225.288 | 289.9826 | 265.8052 | NaN | NaN | NaN | 522.622 | 127.0764 | NaN | NaN | -11.4385 | NaN | NaN | NaN | NaN | 501.1938 | 677.0433 | NaN | 0.1023 | NaN | 17.1708
8429.1292 | 532.9989 | 235.3073 | 190.1905 | 192.0582 | 200.3861 | 226.4581 | 290.263 | 265.572 | NaN | NaN | NaN | 523.8372 | 127.8965 | NaN | NaN | 19.808 | -16.578 | NaN | NaN | NaN | 503.4124 | 669.9955 | NaN | 5.1926 | NaN | 22.8116
8430.1292 | 530.7017 | 234.965 | 190.3555 | 192.5381 | 200.1656 | 227.0973 | 289.5848 | 267.6695 | NaN | NaN | NaN | 520.453 | 128.2366 | NaN | NaN | 22.7589 | -0.0632 | NaN | NaN | NaN | 503.8009 | 674.1707 | NaN | 24.6741 | NaN | 20.7748
8431.1292 | 528.0459 | 234.3728 | 190.5577 | 192.8362 | 200.5723 | 228.1366 | 288.8783 | 268.4795 | NaN | NaN | NaN | 534.0188 | 131.0088 | NaN | NaN | 19.9534 | NaN | NaN | NaN | NaN | 508.4901 | 676.0173 | NaN | 16.0779 | NaN | 15.0256
8432.1292 | 545.0636 | 234.1432 | 190.3653 | 192.5761 | 200.7045 | 228.7604 | 289.3454 | 268.6297 | NaN | NaN | NaN | 558.6158 | 126.1486 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 506.0295 | 677.8442 | NaN | 4.6327 | NaN | 26.1507
8433.1292 | 538.7981 | 234.3744 | 190.2659 | 192.5587 | 201.0878 | 230.2728 | 290.2599 | 269.1649 | NaN | NaN | NaN | 574.1322 | 126.723 | NaN | NaN | -11.4589 | NaN | NaN | NaN | NaN | 505.2202 | 675.9815 | NaN | 16.6238 | NaN | 21.1852
8434.1292 | 549.3125 | 234.3742 | 190.4936 | 192.7602 | 201.297 | 231.5391 | 290.4127 | 268.9997 | NaN | NaN | NaN | 574.775 | 124.2038 | NaN | NaN | 29.5069 | NaN | NaN | NaN | NaN | 503.2681 | 674.3329 | NaN | 14.0378 | NaN | 13.2661
8435.1292 | 546.0856 | 234.6167 | 190.0207 | 193.0525 | 201.9787 | 231.7999 | 290.8666 | 270.4182 | NaN | NaN | NaN | 563.6 | 126.5017 | NaN | NaN | -11.6458 | NaN | NaN | NaN | NaN | 502.2144 | 672.6567 | NaN | 11.7067 | NaN | 14.8569
8436.1448 | 547.0282 | 234.6044 | 190.4815 | 193.1804 | 202.0488 | 231.7347 | 291.0311 | 269.8306 | NaN | NaN | NaN | 557.9304 | 127.758 | NaN | NaN | 28.5178 | -17.0985 | NaN | NaN | NaN | 503.4012 | 670.6493 | NaN | 16.4412 | NaN | 17.8343
8437.1292 | 556.5362 | 235.3474 | 191.9782 | 193.8999 | 202.6497 | 233.2402 | 291.9127 | 271.789 | NaN | NaN | NaN | 542.8002 | 128.9436 | NaN | NaN | 56.6947 | 2.0867 | NaN | NaN | NaN | 504.3209 | 669.4037 | NaN | 4.8451 | NaN | 18.0643
8438.1292 | 554.5097 | 235.7126 | 191.7377 | 194.612 | 203.0557 | 235.2335 | 292.0282 | 274.8478 | NaN | NaN | NaN | 544.5033 | 122.1117 | NaN | NaN | 41.2283 | NaN | NaN | NaN | NaN | 505.2507 | 671.2405 | NaN | 14.3129 | NaN | 19.5946
8439.1292 | 550.9597 | 235.9286 | 192.0786 | 195.0289 | 203.6801 | 234.4604 | 291.8649 | 275.1218 | NaN | NaN | NaN | 558.8761 | 125.8426 | NaN | NaN | 58.822 | NaN | NaN | NaN | NaN | 508.8315 | 671.7022 | NaN | 5.4216 | NaN | 12.6247
8440.1292 | 547.9084 | 236.627 | 191.8777 | 195.0086 | 204.0426 | 234.1793 | 291.9033 | 274.6263 | NaN | NaN | NaN | 578.4274 | 125.6215 | NaN | NaN | 51.2851 | NaN | NaN | NaN | NaN | 507.9879 | 670.7905 | NaN | 34.1405 | NaN | 9.9402
8441.1292 | 543.504 | 236.8551 | 192.1432 | 195.7372 | 204.6673 | 232.9164 | 291.417 | 274.8778 | NaN | NaN | NaN | 568.6484 | 128.5918 | NaN | NaN | 17.0862 | NaN | NaN | NaN | NaN | 507.5285 | 671.4361 | NaN | 16.1075 | NaN | 15.2393
8442.1292 | 537.8309 | 237.1434 | 192.4979 | 195.9515 | 205.1554 | 233.44 | 293.7766 | 274.8846 | NaN | NaN | NaN | 552.7177 | 127.2826 | NaN | NaN | 22.256 | NaN | NaN | NaN | NaN | 506.2801 | 670.6893 | NaN | 4.9118 | NaN | 20.2218
8443.1292 | 530.7842 | 237.7825 | 192.3987 | 196.1739 | 204.7898 | 232.6037 | 293.9641 | 274.6417 | NaN | NaN | NaN | 537.3946 | 132.9902 | NaN | NaN | 26.8572 | NaN | NaN | NaN | NaN | 506.4676 | 666.2166 | NaN | 23.66 | NaN | 14.9295
8444.1292 | 526.2361 | 236.9861 | 192.2499 | 196.2788 | 204.8037 | 231.7145 | 294.3214 | 274.7024 | NaN | NaN | NaN | 526.0771 | 126.2447 | NaN | NaN | 1.0194 | NaN | NaN | NaN | NaN | 507.1063 | 666.5101 | NaN | 15.8353 | NaN | 23.4272
8445.1292 | 519.914 | 236.9764 | 192.6703 | 196.3818 | 204.6288 | 231.1631 | 294.6527 | 275.696 | NaN | NaN | NaN | 517.3149 | 128.4183 | NaN | NaN | NaN | -3.012 | NaN | NaN | NaN | 509.0887 | 667.3522 | NaN | 0.9355 | NaN | 19.369
8446.1292 | 524.5954 | 236.8598 | 192.4834 | 196.6474 | 204.3858 | 230.8227 | 293.9081 | 276.6921 | NaN | NaN | NaN | 541.7477 | 129.159 | NaN | NaN | 27.9162 | NaN | NaN | NaN | NaN | 516.6417 | 672.1327 | NaN | 33.4496 | NaN | 17.4338
8447.1292 | 519.0037 | 236.4881 | 192.097 | 196.4813 | 204.2549 | 231.771 | 295.32 | 277.5282 | NaN | NaN | NaN | 539.0325 | 121.6748 | NaN | NaN | 60.2012 | NaN | NaN | NaN | NaN | 512.2174 | 668.5304 | NaN | 1.5347 | NaN | 19.4066
8448.1292 | 520.6898 | 236.5188 | 192.7952 | 196.6292 | 203.9935 | 232.2442 | 295.6199 | 279.4194 | NaN | NaN | NaN | 537.8433 | 121.5681 | NaN | NaN | 39.3727 | NaN | NaN | NaN | NaN | 512.1002 | 666.785 | NaN | 3.7876 | NaN | 9.9373
8449.1292 | 519.2639 | 236.0495 | 192.8458 | 196.5071 | 203.9338 | 234.9382 | 296.687 | 280.1468 | NaN | NaN | NaN | 525.8828 | 127.3755 | NaN | NaN | 8.7897 | -15.3334 | NaN | NaN | NaN | 510.7204 | 661.9935 | NaN | 17.597 | NaN | 27.826
8450.1292 | 515.9378 | 236.1044 | 193.4983 | 196.2974 | 203.739 | 237.1189 | 297.3533 | 281.7278 | NaN | NaN | NaN | 515.1796 | 129.8847 | NaN | NaN | 18.0782 | -9.3693 | NaN | NaN | NaN | 512.4964 | 661.8794 | NaN | 21.5429 | NaN | 20.4877
8451.1292 | 512.2433 | 236.4348 | 193.3046 | 195.9929 | 203.4068 | 236.9826 | 299.1333 | 283.8878 | NaN | NaN | NaN | 507.792 | 131.9513 | NaN | NaN | 33.812 | NaN | NaN | NaN | NaN | 512.8692 | 657.127 | NaN | 5.4336 | NaN | 19.6864
8452.1292 | 519.964 | 237.0509 | 193.2171 | 196.0435 | 203.6252 | 236.4066 | 298.8354 | 284.6334 | NaN | NaN | NaN | 506.877 | 124.5892 | NaN | NaN | -5.3562 | NaN | NaN | NaN | NaN | 512.4495 | 660.5058 | NaN | 13.2901 | NaN | 17.149
8453.1292 | 516.4414 | 237.2614 | 193.4333 | 195.4596 | 204.0714 | 238.2766 | 300.1181 | 284.801 | NaN | NaN | NaN | 518.4002 | 126.1774 | NaN | NaN | -3.2799 | NaN | NaN | NaN | NaN | 517.0445 | 665.1036 | NaN | 15.8219 | NaN | 23.7386
8454.1292 | 514.4251 | 238.1423 | 193.9572 | 195.2628 | 204.46 | 238.415 | 300.0175 | 285.3583 | NaN | NaN | NaN | 543.9025 | 127.0868 | NaN | NaN | -9.2096 | NaN | NaN | NaN | NaN | 522.0593 | 667.1075 | NaN | 5.2358 | NaN | 14.1834
8455.1292 | 513.4077 | 239.4688 | 194.1712 | 195.5935 | 205.0741 | 236.5328 | 298.7708 | 285.2411 | NaN | NaN | NaN | 550.5355 | 124.2018 | NaN | NaN | 57.6558 | NaN | NaN | NaN | NaN | 520.4091 | 665.3057 | NaN | 25.1361 | NaN | 17.3426
8456.1292 | 514.3929 | 239.5788 | 194.927 | 196.9132 | 205.449 | 235.541 | 297.714 | 284.4466 | NaN | NaN | NaN | 560.0613 | 126.1772 | NaN | NaN | 17.5148 | -18.2443 | NaN | NaN | NaN | 518.0653 | 664.6325 | NaN | 14.1987 | NaN | 18.5076
8457.1292 | 520.0893 | 239.8589 | 195.6519 | 197.2335 | 205.9229 | 234.8021 | 297.9177 | 283.9 | NaN | NaN | NaN | 584.4978 | 128.5577 | NaN | NaN | 34.7131 | -14.7935 | NaN | NaN | NaN | 523.6567 | 665.6797 | NaN | 1.4665 | NaN | 24.0248
8458.1292 | 521.2603 | 239.9033 | 195.3069 | 197.0323 | 205.8667 | 234.4454 | 298.1277 | 283.9956 | NaN | NaN | NaN | 587.9748 | 125.5235 | NaN | NaN | 39.6887 | NaN | NaN | NaN | NaN | 520.6437 | 666.9834 | NaN | 14.6814 | NaN | 11.8315
8459.1292 | 523.8746 | 240.3436 | 195.4042 | 196.8125 | 206.3625 | 234.6856 | 298.5648 | 283.3283 | NaN | NaN | NaN | 572.2195 | 129.419 | NaN | NaN | 1.695 | NaN | NaN | NaN | NaN | 519.5383 | 662.5834 | NaN | 9.4998 | NaN | 26.9335
8460.1292 | 533.3634 | 240.656 | 195.4061 | 196.7237 | 206.5775 | 234.966 | 299.8102 | 284.0651 | NaN | NaN | NaN | 558.2646 | 128.4937 | NaN | NaN | 37.0021 | NaN | NaN | NaN | NaN | 517.5854 | 661.2238 | NaN | 11.1532 | NaN | 17.7485
8461.1292 | 537.061 | 241.2568 | 195.6155 | 196.5181 | 206.7867 | 235.9006 | 301.5611 | 283.8251 | NaN | NaN | NaN | 545.8256 | 124.0557 | NaN | NaN | 39.4834 | NaN | NaN | NaN | NaN | 517.6022 | 659.3492 | NaN | 31.2314 | NaN | 19.6281
8462.1292 | 534.0906 | 241.4102 | 195.4946 | 196.1601 | 207.1283 | 235.6292 | 301.7246 | 283.6624 | NaN | NaN | NaN | 533.2242 | 129.2419 | NaN | NaN | 47.1601 | NaN | NaN | NaN | NaN | 518.2443 | 658.2591 | NaN | 7.7043 | NaN | 15.7108
8463.1292 | 532.4875 | 242.1 | 195.8694 | 196.3479 | 207.4665 | 235.5166 | 301.5 | 283.2148 | NaN | NaN | NaN | 533.7438 | 128.4439 | NaN | NaN | 26.3974 | -17.1661 | NaN | NaN | NaN | 520.7373 | 660.1393 | NaN | 17.2206 | NaN | 24.0677
8464.1292 | 531.4333 | 242.2893 | 195.3839 | 196.7316 | 207.34 | 236.0865 | 302.0563 | 282.7021 | NaN | NaN | NaN | 528.0654 | 125.1399 | NaN | NaN | NaN | -12.7151 | NaN | NaN | NaN | 520.0459 | 657.6809 | NaN | 4.698 | NaN | 20.4077
8465.1292 | 546.4128 | 242.5543 | 195.0013 | 196.7256 | 207.596 | 237.2372 | 302.3076 | 282.0396 | NaN | NaN | NaN | 541.1225 | 120.5335 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 523.8321 | 660.4585 | NaN | 3.7851 | NaN | 16.138
8466.1292 | 543.1518 | 243.2555 | 194.2974 | 196.8982 | 207.5304 | 237.4977 | 302.3708 | 281.3021 | NaN | NaN | NaN | 550.3381 | 120.4147 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 524.9387 | 658.6046 | NaN | 19.6194 | NaN | 24.3564
8467.1292 | 542.8386 | 243.1495 | 194.5974 | 196.949 | 207.378 | 236.4154 | 302.9439 | 281.7102 | NaN | NaN | NaN | 576.0519 | 126.2054 | NaN | NaN | 31.7106 | NaN | NaN | NaN | NaN | 524.3519 | 662.0495 | NaN | 16.8749 | NaN | 14.9323
8468.1292 | 539.2833 | 244.6327 | 194.3396 | 196.808 | 207.2472 | 235.535 | 302.7609 | 281.208 | NaN | NaN | NaN | 560.285 | 127.7346 | NaN | NaN | 49.5297 | NaN | NaN | NaN | NaN | 522.0682 | 657.0065 | NaN | 13.7599 | NaN | 19.3165
8469.1292 | 539.8326 | 244.8509 | 194.2323 | 196.7493 | 206.8971 | 235.2697 | 304.6896 | 282.0529 | NaN | NaN | NaN | 551.2144 | 126.559 | NaN | NaN | 13.4187 | -17.7118 | NaN | NaN | NaN | 520.6263 | 647.4825 | NaN | 22.0871 | NaN | 11.9099
8470.1448 | 538.0236 | 245.1337 | 193.4595 | 196.8547 | 207.1209 | 234.406 | 303.4324 | 282.1947 | NaN | NaN | NaN | 540.4171 | 137.9019 | NaN | NaN | NaN | 16.0088 | NaN | NaN | NaN | 524.9141 | 653.7253 | NaN | 16.0754 | NaN | 14.074
8471.1292 | 534.3108 | 244.7779 | 193.2596 | 197.2064 | 206.791 | 234.0801 | 303.2784 | 282.1993 | NaN | NaN | NaN | 525.3476 | 126.7016 | NaN | NaN | -1.9403 | NaN | NaN | NaN | NaN | 522.2054 | 656.5291 | NaN | 6.3238 | NaN | 12.0931
8472.1292 | 532.0407 | 245.0951 | 192.8539 | 197.0492 | 206.8464 | 234.6588 | 302.3279 | 282.1339 | NaN | NaN | NaN | 524.4538 | 122.6714 | NaN | NaN | 34.2112 | NaN | NaN | NaN | NaN | 522.7513 | 654.2133 | NaN | 16.8011 | NaN | 23.579
8473.1292 | 529.8952 | 244.8553 | 193.7134 | 197.0823 | 206.8737 | 233.7561 | 301.3712 | 282.9095 | NaN | NaN | NaN | 532.9113 | 127.6784 | NaN | NaN | 32.077 | NaN | NaN | NaN | NaN | 525.9713 | 654.0264 | NaN | 8.6441 | NaN | 19.3275
8474.1292 | 528.8825 | 244.6899 | 194.1172 | 197.9013 | 207.1542 | 233.3366 | 300.7005 | 281.9423 | NaN | NaN | NaN | 520.9799 | 127.6611 | NaN | NaN | 30.2218 | NaN | NaN | NaN | NaN | 525.8255 | 655.5153 | NaN | 0.6726 | NaN | 22.7179
8475.1292 | 533.8823 | 244.2772 | 194.4905 | 197.9025 | 207.5141 | 233.7926 | 301.1658 | 282.2904 | NaN | NaN | NaN | 526.7594 | 132.0035 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 528.7763 | 655.1401 | NaN | 7.2661 | NaN | 16.0849
8476.1292 | 533.8011 | 244.9772 | 194.5624 | 198.1584 | 207.8235 | 234.3993 | 301.2571 | 280.2994 | NaN | NaN | NaN | 541.2765 | 119.9798 | NaN | NaN | NaN | -16.2796 | NaN | NaN | NaN | 533.3359 | 657.0796 | NaN | 9.0923 | NaN | 23.8655
8477.1292 | 532.4257 | 244.3147 | 195.0756 | 198.3848 | 207.9143 | 234.5253 | 301.9757 | 278.9071 | NaN | NaN | NaN | 542.9582 | 126.879 | NaN | NaN | NaN | -3.92 | NaN | NaN | NaN | 533.6128 | 658.4176 | NaN | 9.0943 | NaN | 21.2141
8478.1292 | 532.0646 | 244.4079 | 195.022 | 198.6405 | 207.9931 | 235.4272 | 302.5647 | 278.2567 | NaN | NaN | NaN | 530.2762 | 123.5919 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 532.1446 | 651.4315 | NaN | 1.9425 | NaN | 16.3439
8479.1292 | 535.0339 | 244.5238 | 194.9016 | 199.2817 | 208.0209 | 235.876 | 303.5226 | 278.7372 | NaN | NaN | NaN | 527.117 | 121.208 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 532.01 | 650.6686 | NaN | 6.0187 | NaN | 21.8729
8480.1292 | 547.5452 | 244.4331 | 195.8465 | 199.688 | 207.8378 | 236.6932 | 302.3807 | 277.2997 | NaN | NaN | NaN | 532.6249 | 126.2811 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 531.9378 | 648.3287 | NaN | 12.1597 | NaN | 15.9852
8481.1292 | 556.5693 | 244.7849 | 195.7531 | 199.7175 | 207.9403 | 238.4505 | 302.8702 | 277.2117 | NaN | NaN | NaN | 520.8023 | 122.4405 | NaN | NaN | -16.0109 | NaN | NaN | NaN | NaN | 531.3381 | 648.8678 | NaN | 4.5294 | NaN | 21.78
8482.1292 | 560.7586 | 244.6253 | 195.9284 | 199.4523 | 208.1141 | 238.4125 | 303.634 | 277.0234 | NaN | NaN | NaN | 516.0637 | 127.6968 | NaN | NaN | 22.4774 | -17.3816 | NaN | NaN | NaN | 535.5565 | 646.1095 | NaN | 3.465 | NaN | 14.7977
8483.1292 | 568.2446 | 244.3459 | 196.2341 | 199.8778 | 208.4069 | 238.4623 | 302.5459 | 276.4897 | NaN | NaN | NaN | 525.0743 | 129.6755 | NaN | NaN | 19.7739 | -4.9986 | NaN | NaN | NaN | 537.8716 | 643.5008 | NaN | 17.1076 | NaN | 19.6072
8484.1292 | 566.7497 | 244.8727 | 196.455 | 200.3599 | 208.7367 | 238.3762 | 302.9358 | 276.4819 | NaN | NaN | NaN | 520.9189 | 122.2143 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 538.4552 | 641.5033 | NaN | 12.3388 | NaN | 20.2876
8485.1292 | 561.8182 | 246.0695 | 197.0004 | 201.0516 | 209.0376 | 237.8644 | 303.9377 | 278.5349 | NaN | NaN | NaN | 525.5243 | 126.2298 | NaN | NaN | -6.9109 | NaN | NaN | NaN | NaN | 534.9397 | 645.6771 | NaN | 13.6429 | NaN | 21.1885
8486.1292 | 558.8625 | 245.9384 | 197.1446 | 201.6121 | 209.432 | 238.2346 | 304.7031 | 278.6141 | NaN | NaN | NaN | 527.3369 | 131.883 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 537.6414 | 647.9147 | NaN | 8.0226 | NaN | 14.7687
8487.1292 | 556.6361 | 246.6348 | 197.6183 | 201.6064 | 209.4311 | 239.1115 | 306.5293 | 279.833 | NaN | NaN | NaN | 521.7668 | 127.454 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 535.5917 | 649.5719 | NaN | -0.0728 | NaN | 14.4312
8488.1292 | 560.1297 | 247.0745 | 198.4075 | 201.7863 | 209.8061 | 239.1501 | 306.925 | 280.8956 | NaN | NaN | NaN | 535.6939 | 120.0572 | NaN | NaN | 41.0598 | NaN | NaN | NaN | NaN | 540.5965 | 653.0706 | NaN | 1.6149 | NaN | 16.3889
8489.1292 | 568.8109 | 247.149 | 197.7091 | 201.8233 | 209.6829 | 238.7205 | 307.1643 | 280.2309 | NaN | NaN | NaN | 532.7744 | 128.8447 | NaN | NaN | 31.8385 | -17.2886 | NaN | NaN | NaN | 537.5736 | 647.6543 | NaN | 10.9087 | NaN | 22.0271
8490.1292 | 572.9302 | 247.1291 | 197.4509 | 201.3667 | 209.6142 | 240.181 | 307.9796 | 282.026 | NaN | NaN | NaN | 528.1696 | 125.8671 | NaN | NaN | NaN | -4.7008 | NaN | NaN | NaN | 541.1756 | 649.2622 | NaN | 5.8884 | NaN | 28.659
8491.1292 | 573.8031 | 247.6129 | 197.9624 | 201.5337 | 209.5789 | 240.4408 | 309.7459 | 284.8192 | NaN | NaN | NaN | 518.5047 | 125.5903 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 539.3848 | 651.1658 | NaN | 13.696 | NaN | 27.6069
8492.1292 | 577.1517 | 247.7961 | 198.4863 | 201.5457 | 209.6804 | 242.2767 | 310.8304 | 285.4441 | NaN | NaN | NaN | 515.3183 | 125.5737 | NaN | NaN | -8.0246 | NaN | NaN | NaN | NaN | 539.6638 | 648.2412 | NaN | 10.8548 | NaN | 22.084
8493.1292 | 580.7519 | 248.0477 | 198.9174 | 201.8567 | 210.0064 | 243.7035 | 311.5105 | 287.3339 | NaN | NaN | NaN | 517.8034 | 128.4261 | NaN | NaN | 32.1488 | NaN | NaN | NaN | NaN | 542.608 | 648.8828 | NaN | 12.4352 | NaN | 21.6077
8494.1292 | 594.314 | 248.1457 | 198.7023 | 202.2465 | 209.9387 | 246.872 | 311.824 | 289.9809 | NaN | NaN | NaN | 523.0866 | 128.2576 | NaN | NaN | 25.104 | NaN | NaN | NaN | NaN | 548.3737 | 651.7892 | NaN | 10.7589 | NaN | 22.6812
8495.1292 | 596.6338 | 248.5736 | 198.8387 | 202.6014 | 209.8884 | 248.3651 | 312.9431 | 289.7244 | NaN | NaN | NaN | 550.8872 | 128.5375 | NaN | NaN | -10.0771 | NaN | NaN | NaN | NaN | 550.0612 | 653.2677 | NaN | 3.6133 | NaN | 27.0819
8496.1292 | 603.0824 | 249.6663 | 199.6062 | 202.8111 | 210.6002 | 251.2505 | 313.4883 | 291.7044 | NaN | NaN | NaN | 570.1873 | 124.311 | NaN | NaN | 10.897 | -14.0051 | NaN | NaN | NaN | 548.3429 | 652.5894 | NaN | 15.3618 | NaN | 13.3072
8497.1292 | 606.6531 | 249.8834 | 201.1182 | 203.1137 | 211.3814 | 251.3964 | 313.7179 | 291.3354 | NaN | NaN | NaN | 558.2828 | 125.212 | NaN | NaN | 0.105 | NaN | NaN | NaN | NaN | 549.8055 | 654.0275 | NaN | 7.1741 | NaN | 17.1081
8498.1292 | 610.2112 | 250.1573 | 201.7932 | 203.9923 | 212.0728 | 251.5253 | 313.3727 | 291.6239 | NaN | NaN | NaN | 545.6211 | 126.993 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 550.871 | 649.138 | NaN | 15.732 | NaN | 24.0572
8499.1292 | 611.9658 | 251.2476 | 202.1085 | 204.4807 | 213.1136 | 251.5337 | 313.8765 | 293.2005 | NaN | NaN | NaN | 564.456 | 127.0889 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 555.6301 | 651.5986 | NaN | 3.8904 | NaN | 22.6318
8500.1292 | 618.6104 | 251.5596 | 202.8766 | 205.1439 | 213.245 | 251.6001 | 314.1556 | 294.4356 | NaN | NaN | NaN | 571.9621 | 126.8703 | NaN | NaN | -19.4361 | NaN | NaN | NaN | NaN | 550.9616 | 650.1699 | NaN | 7.5709 | NaN | 21.4794
8501.1292 | 623.2504 | 251.2891 | 202.9433 | 205.3792 | 213.6768 | 252.4757 | 313.4172 | 294.7717 | NaN | NaN | NaN | 595.0473 | 124.449 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 555.3161 | 655.0376 | NaN | 9.0325 | NaN | 18.3699
8502.1292 | 624.4415 | 251.5282 | 203.6452 | 205.63 | 214.1569 | 252.6353 | 313.4899 | 295.325 | NaN | NaN | NaN | 608.3553 | 123.1414 | NaN | NaN | 12.4829 | NaN | NaN | NaN | NaN | 553.5496 | 651.7342 | NaN | 29.2224 | NaN | 11.3807
8503.1292 | 623.5877 | 252.3179 | 203.8057 | 205.4984 | 214.8167 | 254.1894 | 313.1623 | 297.721 | NaN | NaN | NaN | 617.0015 | 125.6799 | NaN | NaN | 22.8719 | -18.1376 | NaN | NaN | NaN | 554.9417 | 652.4466 | NaN | 12.062 | NaN | 23.2631
8504.1292 | 621.1611 | 252.6188 | 203.3691 | 205.5907 | 215.0757 | 253.3431 | 313.7855 | 298.4265 | NaN | NaN | NaN | 603.2684 | 124.3323 | NaN | NaN | -13.3432 | 12.1369 | NaN | NaN | NaN | 553.7723 | 647.2181 | NaN | 5.8687 | NaN | 23.1574
8505.1292 | 621.7211 | 252.7187 | 202.6649 | 205.5935 | 215.1652 | 253.6153 | 314.0897 | 299.9287 | NaN | NaN | NaN | 600.2118 | 110.3298 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 554.6951 | 646.8182 | NaN | 4.6586 | NaN | 18.5143
8506.1292 | 619.449 | 253.2946 | 202.5919 | 206.1031 | 215.3789 | 255.6258 | 315.3615 | 301.8342 | NaN | NaN | NaN | 629.0674 | 127.0595 | NaN | NaN | 25.4576 | NaN | NaN | NaN | NaN | 558.039 | 651.8117 | NaN | 8.917 | NaN | 15.8018
8507.1292 | 624.8964 | 253.537 | 203.0319 | 206.477 | 215.8512 | 256.8409 | 316.7958 | 300.8861 | NaN | NaN | NaN | 632.191 | 121.4576 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 554.3206 | 646.3742 | NaN | 8.5381 | NaN | 22.8249
8508.1292 | 626.1655 | 254.7671 | 203.8903 | 207.1474 | 216.6037 | 261.1324 | 318.2863 | 299.8277 | NaN | NaN | NaN | 638.9914 | 124.0445 | NaN | NaN | 26.1602 | NaN | NaN | NaN | NaN | 557.8529 | 648.6696 | NaN | 23.6287 | NaN | 23.983
8509.1292 | 629.0789 | 255.8195 | 203.4744 | 206.613 | 217.411 | 260.7161 | 318.7384 | 299.5934 | NaN | NaN | NaN | 646.8822 | 129.7398 | NaN | NaN | 11.6856 | NaN | NaN | NaN | NaN | 559.7363 | 650.9016 | NaN | 10.58 | NaN | 13.1705
8510.1292 | 629.235 | 256.9625 | 203.6368 | 206.5839 | 218.6395 | 259.9969 | 319.4834 | 299.9908 | NaN | NaN | NaN | 661.5499 | 125.5794 | NaN | NaN | 8.0238 | -16.5582 | NaN | NaN | NaN | 557.8449 | 649.9156 | NaN | 5.9476 | NaN | 18.4756
8511.1292 | 627.7481 | 257.7373 | 205.7142 | 207.7624 | 219.0273 | 259.2434 | 321.2364 | 300.0583 | NaN | NaN | NaN | 681.2523 | 116.1315 | NaN | NaN | 6.3781 | 15.0501 | NaN | NaN | NaN | 562.6162 | 648.4715 | NaN | 14.6563 | NaN | 20.3308
8512.1292 | 633.9162 | 258.2686 | 205.1619 | 207.5565 | 219.0436 | 262.203 | 321.67 | 301.0489 | NaN | NaN | NaN | 673.895 | 128.4513 | NaN | NaN | 31.6193 | NaN | NaN | NaN | NaN | 560.8497 | 652.2223 | NaN | 10.5059 | NaN | 25.7903
8513.1292 | 637.9724 | 258.4418 | 204.9068 | 207.4748 | 218.6199 | 262.1139 | 322.6863 | 303.7967 | NaN | NaN | NaN | 697.1518 | 129.1456 | NaN | NaN | 27.3658 | NaN | NaN | NaN | NaN | 563.269 | 644.8316 | NaN | 18.0489 | NaN | 14.6382
8514.1292 | 637.911 | 257.8754 | 205.5352 | 207.7639 | 218.5468 | 263.0091 | 321.7378 | 304.6024 | NaN | NaN | NaN | 714.2064 | 123.7929 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 564.1301 | 650.8217 | NaN | 5.1063 | NaN | 9.1362
8515.1292 | 636.4909 | 258.7108 | 205.54 | 207.3262 | 218.4936 | 262.1808 | 321.9785 | 307.195 | NaN | NaN | NaN | 708.4593 | 121.7154 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 563.484 | 651.1401 | NaN | 9.3266 | NaN | 14.5659
8516.1292 | 635.9077 | 258.3689 | 205.8981 | 207.0575 | 218.3373 | 261.6595 | 322.9349 | 307.8197 | NaN | NaN | NaN | 700.3151 | 126.2781 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 563.513 | 648.4517 | NaN | 1.8287 | NaN | 22.873
8517.1292 | 631.6963 | 258.6186 | 205.6874 | 207.3088 | 218.5711 | 262.375 | 322.3459 | 307.918 | NaN | NaN | NaN | 695.5671 | 126.4674 | NaN | NaN | NaN | -17.808 | NaN | NaN | NaN | 560.3053 | 646.7098 | NaN | 8.9832 | NaN | 25.6491
8518.1292 | 630.9534 | 258.7824 | 205.8151 | 207.7733 | 219.1253 | 262.6492 | 322.4241 | 309.116 | NaN | NaN | NaN | 682.1038 | 124.1275 | NaN | NaN | NaN | 0.2041 | NaN | NaN | NaN | 560.8392 | 644.9637 | NaN | 12.8974 | NaN | 20.0928
8519.1292 | 628.0461 | 258.5034 | 206.1525 | 208.6451 | 219.8497 | 261.8071 | 323.6869 | 308.1942 | NaN | NaN | NaN | 663.3437 | 124.9108 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 562.4535 | 646.4521 | NaN | 15.6795 | NaN | 14.3221
8520.1292 | 628.1325 | 258.1345 | 206.1618 | 209.0143 | 220.6866 | 262.8886 | 323.0523 | 309.1749 | NaN | NaN | NaN | 660.71 | 121.9589 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 565.001 | 645.947 | NaN | 13.4452 | NaN | 14.7141
8521.1292 | 625.0201 | 257.4093 | 206.9429 | 209.0203 | 221.281 | 262.0394 | 322.842 | 310.5342 | NaN | NaN | NaN | 665.5909 | 128.3971 | NaN | NaN | 32.5884 | NaN | NaN | NaN | NaN | 573.3183 | 647.2435 | NaN | 14.6839 | NaN | 23.4227
8522.1292 | 623.172 | 257.4765 | 207.3783 | 209.3462 | 221.7926 | 262.5614 | 323.0034 | 311.0805 | NaN | NaN | NaN | 662.7625 | 121.001 | NaN | NaN | -14.2562 | NaN | NaN | NaN | NaN | 568.7263 | 646.8416 | NaN | 10.7542 | NaN | 23.1885
8523.1292 | 621.7597 | 257.8867 | 207.6585 | 208.9478 | 222.397 | 263.4788 | 324.1551 | 313.6485 | NaN | NaN | NaN | 650.0339 | 126.0263 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 571.2123 | 647.7925 | NaN | 6.5911 | NaN | 22.0539
8524.1292 | 619.771 | 258.3584 | 208.129 | 209.2298 | 222.7597 | 265.9862 | 324.8425 | 314.6524 | NaN | NaN | NaN | 619.8243 | 125.4999 | NaN | NaN | 14.0555 | -17.0866 | NaN | NaN | NaN | 572.0339 | 646.4324 | NaN | 4.8514 | NaN | 17.512
8525.1292 | 616.6856 | 258.9873 | 208.2227 | 209.6026 | 223.4999 | 267.6216 | 325.7353 | 314.4854 | NaN | NaN | NaN | 596.242 | 134.5777 | NaN | NaN | 1.2817 | 11.3259 | NaN | NaN | NaN | 577.4846 | 645.7689 | NaN | 4.0007 | NaN | 15.4115
8526.1292 | 616.5892 | 259.4521 | 209.18 | 209.5358 | 224.3749 | 266.802 | 326.1323 | 314.0952 | NaN | NaN | NaN | 589.1501 | 120.7891 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 575.823 | 646.0586 | NaN | 3.7733 | NaN | 25.001
8527.1292 | 614.2898 | 259.9327 | 208.0709 | 209.3423 | 224.3405 | 269.6124 | 325.8642 | 313.4948 | NaN | NaN | NaN | 613.4512 | 128.1207 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 587.5166 | 652.2524 | NaN | 19.0041 | NaN | 20.1584
8528.1292 | 611.5982 | 260.3525 | 207.5482 | 209.7369 | 224.3685 | 270.6862 | 325.9741 | 314.2437 | NaN | NaN | NaN | 603.1546 | 126.3202 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 582.2452 | 650.8213 | NaN | 2.4338 | NaN | 22.9551
8529.1292 | 612.068 | 260.9153 | 207.6669 | 209.843 | 225.0467 | 268.6246 | 326.8261 | 312.7812 | NaN | NaN | NaN | 601.8022 | 121.3451 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 583.3531 | 652.723 | NaN | 20.1315 | NaN | 18.1306
8530.1292 | 610.6845 | 261.3902 | 207.3398 | 209.699 | 225.2666 | 268.6001 | 326.2342 | 312.7929 | NaN | NaN | NaN | 627.3232 | 124.3255 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 585.2444 | 651.8653 | NaN | 2.5375 | NaN | 19.2854
8531.1292 | 609.983 | 261.3733 | 207.1457 | 209.4814 | 225.6233 | 268.4196 | 325.6476 | 313.8492 | NaN | NaN | NaN | 606.0453 | 130.2135 | NaN | NaN | 31.9891 | 9.5362 | NaN | NaN | NaN | 558.2872 | 621.4451 | NaN | 22.2666 | NaN | NaN
8532.1292 | 611.0899 | 261.7093 | 207.7061 | 209.6699 | 225.6614 | 267.5556 | 325.5976 | 312.6848 | NaN | NaN | NaN | 589.2296 | 188.9416 | NaN | NaN | 189.7026 | NaN | NaN | NaN | NaN | 525.4544 | 567.4729 | NaN | NaN | NaN | -12.5408
8533.1292 | 612.6538 | 262.8753 | 206.7342 | 209.8723 | 225.8376 | 266.7385 | 327.0521 | 312.5603 | NaN | NaN | NaN | 571.2509 | 194.2707 | NaN | NaN | 209.2121 | NaN | NaN | NaN | NaN | 522.9724 | 565.3678 | NaN | -7.9465 | NaN | 0.306
8534.1292 | 611.8797 | 264.1227 | 207.048 | 210.0037 | 226.0951 | 267.2997 | 327.9784 | 311.3646 | NaN | NaN | NaN | 563.2597 | 198.9008 | NaN | NaN | 220.7343 | NaN | NaN | NaN | NaN | 518.6936 | 557.8309 | NaN | -11.2425 | NaN | -19.6833
8535.1292 | 611.0174 | 264.3579 | 207.2269 | 210.0239 | 225.4928 | 268.6268 | 329.0144 | 309.7945 | NaN | NaN | NaN | 584.7877 | 196.8768 | NaN | NaN | 215.5884 | NaN | NaN | NaN | NaN | 521.5413 | 559.4764 | NaN | -19.2545 | NaN | -15.139
8536.1292 | 610.8699 | 264.7738 | 207.7744 | 210.5714 | 225.2857 | 268.0174 | 329.3938 | 310.2009 | NaN | NaN | NaN | 607.2787 | 207.4251 | NaN | NaN | 199.5671 | 10.6579 | NaN | NaN | NaN | 527.7686 | 560.9584 | NaN | -6.7619 | NaN | -8.7964
8537.1292 | 609.5896 | 265.4062 | 207.8623 | 210.6035 | 225.2376 | 268.6317 | 330.835 | 309.6435 | NaN | NaN | NaN | 589.4147 | 193.8961 | NaN | NaN | 204.318 | NaN | NaN | NaN | NaN | 526.8102 | 566.8624 | NaN | -4.5826 | NaN | -10.0324
8538.1292 | 609.7404 | 265.7785 | 207.2949 | 210.242 | 225.1967 | 268.7021 | 333.1362 | 311.0889 | NaN | NaN | NaN | 585.1634 | 199.958 | NaN | NaN | 216.5638 | NaN | NaN | NaN | NaN | 527.1685 | 562.737 | NaN | 8.0499 | NaN | -17.2682
8539.1292 | 609.4136 | 265.8063 | 207.8859 | 210.1353 | 224.7431 | 268.9091 | 333.7325 | 312.3676 | NaN | NaN | NaN | 590.0081 | 197.4674 | NaN | NaN | 206.0018 | NaN | NaN | NaN | NaN | 525.1035 | 557.9077 | NaN | -3.1207 | NaN | -6.3561
8540.1292 | 609.2212 | 266.4828 | 207.908 | 210.4686 | 224.4648 | 269.4581 | 334.0132 | 314.0829 | NaN | NaN | NaN | 615.1736 | 202.3254 | NaN | NaN | 230.0597 | NaN | NaN | NaN | NaN | 527.2027 | 561.052 | NaN | -18.7123 | NaN | -17.1613
8541.1292 | 609.1398 | 266.8683 | 208.4732 | 210.9607 | 224.5673 | 271.3624 | 332.9425 | 314.8302 | NaN | NaN | NaN | 623.5523 | 204.4763 | NaN | NaN | 232.1976 | NaN | NaN | NaN | NaN | 525.0239 | 561.4424 | NaN | 1.081 | NaN | -19.5232
8542.1292 | 610.9036 | 267.9254 | 208.758 | 211.0829 | 225.0936 | 273.3101 | 333.7332 | 317.0379 | NaN | NaN | NaN | 633.8051 | 207.2371 | NaN | NaN | 210.5358 | NaN | NaN | NaN | NaN | 522.9253 | 557.517 | NaN | -5.15 | NaN | -2.3679
8543.1292 | 610.7538 | 269.0162 | 209.8859 | 211.5313 | 225.6763 | 274.228 | 335.0674 | 317.2427 | NaN | NaN | NaN | 640.816 | 206.0132 | NaN | NaN | 220.7289 | NaN | NaN | NaN | NaN | 521.9404 | 551.2897 | NaN | -15.8831 | NaN | -13.2021
8544.1292 | 611.2579 | 270.5633 | 210.4667 | 212.5038 | 225.9457 | 274.2765 | 337.0692 | 317.2691 | NaN | NaN | NaN | 642.4252 | 206.9025 | NaN | NaN | 248.1603 | NaN | NaN | NaN | NaN | 516.0385 | 545.3812 | NaN | NaN | NaN | -14.1499
8545.1292 | 614.4608 | 271.9728 | 210.6579 | 212.8882 | 226.7087 | 273.4478 | 338.7166 | 315.994 | NaN | NaN | NaN | 633.8206 | 214.233 | NaN | NaN | 241.3252 | NaN | NaN | NaN | NaN | 517.2442 | 546.6705 | NaN | NaN | NaN | -15.3119
8546.1292 | 618.1564 | 272.4267 | 210.7119 | 213.8431 | 227.724 | 274.0245 | 338.4181 | 317.422 | NaN | NaN | NaN | 621.1234 | 213.5859 | NaN | NaN | 206.3318 | NaN | NaN | NaN | NaN | 516.6342 | 543.0306 | NaN | NaN | NaN | -4.0213
8547.1292 | 619.9394 | 273.2667 | 210.6371 | 214.7749 | 228.4028 | 276.1574 | 339.1322 | 317.6726 | NaN | NaN | NaN | 628.7612 | 208.4456 | NaN | NaN | 223.1511 | NaN | NaN | NaN | NaN | 514.5743 | 542.2205 | NaN | NaN | NaN | NaN
8548.1292 | 617.884 | 273.7178 | 211.5041 | 215.5571 | 228.916 | 278.309 | 339.7323 | 320.2466 | NaN | NaN | NaN | 615.3954 | 216.6555 | NaN | NaN | 223.6229 | NaN | NaN | NaN | NaN | 509.3047 | 539.1079 | NaN | NaN | NaN | NaN
8549.1292 | 617.2529 | 274.3824 | 211.2393 | 215.0614 | 228.9621 | 276.6294 | 339.7007 | 320.6684 | NaN | NaN | NaN | 593.7818 | 218.1265 | NaN | NaN | 225.9734 | NaN | NaN | NaN | NaN | 511.8826 | 537.5608 | NaN | -10.6876 | NaN | NaN
8550.1292 | 616.8366 | 274.2085 | 212.1948 | 214.7721 | 229.0732 | 277.1191 | 339.0741 | 320.6562 | NaN | NaN | NaN | 598.2732 | 218.5947 | NaN | NaN | 212.5984 | NaN | NaN | NaN | NaN | 517.3392 | 538.3769 | NaN | NaN | NaN | -16.5921
8551.1292 | 616.6587 | 274.4631 | 212.532 | 214.8536 | 229.9497 | 278.7159 | 339.9984 | 321.5238 | NaN | NaN | NaN | 585.8398 | 216.3568 | NaN | NaN | 252.6595 | NaN | NaN | NaN | NaN | 512.9527 | 539.6575 | NaN | NaN | NaN | -6.1975
8552.1292 | 618.7508 | 275.4834 | 213.1962 | 214.9007 | 230.0318 | 279.8031 | 340.246 | 321.1197 | NaN | NaN | NaN | 588.9285 | 208.1352 | NaN | NaN | 237.3691 | NaN | NaN | NaN | NaN | 514.4615 | 538.1743 | NaN | NaN | NaN | NaN
8553.1292 | 617.5464 | 276.5535 | 213.9316 | 216.3564 | 229.7964 | 281.1742 | 340.6961 | 319.6661 | NaN | NaN | NaN | 593.8629 | 214.9814 | NaN | NaN | 239.6525 | NaN | NaN | NaN | NaN | 514.3192 | 536.1945 | NaN | NaN | NaN | NaN
8554.1292 | 616.776 | 278.5829 | 214.4529 | 216.0551 | 230.4679 | 283.4119 | 341.0331 | 319.4799 | NaN | NaN | NaN | 596.0367 | 210.4479 | NaN | NaN | 246.689 | NaN | NaN | NaN | NaN | 517.0832 | 535.5191 | NaN | NaN | NaN | NaN
8555.1292 | 619.9922 | 280.6343 | 214.8516 | 216.2156 | 230.8183 | 283.2047 | 340.2879 | 317.2374 | NaN | NaN | NaN | 584.5604 | 225.7215 | NaN | NaN | 262.6452 | NaN | NaN | NaN | NaN | 506.1282 | 523.6996 | NaN | 4.8519 | NaN | NaN
8556.1292 | 620.2884 | 280.3299 | 214.3779 | 216.9335 | 231.0402 | 282.2073 | 340.2595 | 316.9653 | NaN | NaN | NaN | 580.8768 | 219.7564 | NaN | NaN | 246.0822 | NaN | NaN | NaN | NaN | 502.6356 | 514.8735 | NaN | NaN | NaN | NaN
8557.1292 | 621.9826 | 280.8245 | 214.7589 | 217.5987 | 231.4152 | 280.9701 | 339.5227 | 316.2946 | NaN | NaN | NaN | 573.6141 | 229.2744 | NaN | NaN | 247.0397 | NaN | NaN | NaN | NaN | 500.5018 | 515.7935 | NaN | NaN | NaN | NaN
8558.1292 | 622.9211 | 280.8587 | 214.9556 | 217.5691 | 231.2137 | 279.9535 | 338.7757 | 315.3592 | NaN | NaN | NaN | 570.9816 | 225.0209 | NaN | NaN | 275.4959 | NaN | NaN | NaN | NaN | 500.1887 | 514.6849 | NaN | -9.0145 | NaN | -17.8486
8559.1292 | 623.2828 | 280.505 | 215.4423 | 217.8138 | 231.0672 | 278.5853 | 339.5683 | 314.0074 | NaN | NaN | NaN | 558.5629 | 226.7238 | NaN | NaN | 260.3786 | NaN | NaN | NaN | NaN | 500.428 | 510.4952 | NaN | -15.5717 | NaN | -7.7997
8560.1292 | 624.298 | 280.9649 | 215.4419 | 217.7356 | 230.82 | 277.6401 | 338.4697 | 313.6508 | NaN | NaN | NaN | 567.5347 | 228.3758 | NaN | NaN | 283.1224 | NaN | NaN | NaN | NaN | 501.7124 | 510.6396 | NaN | NaN | NaN | NaN
8561.1292 | 626.3098 | 281.9879 | 215.2017 | 217.8753 | 230.9588 | 277.1105 | 339.6047 | 312.1177 | NaN | NaN | NaN | 585.8606 | 247.913 | NaN | NaN | 297.0749 | NaN | NaN | NaN | NaN | 493.5685 | 499.9121 | NaN | NaN | NaN | -19.295
8562.1292 | 627.1213 | 282.0516 | 215.3158 | 217.9825 | 230.7434 | 278.9419 | 340.738 | 313.8538 | NaN | NaN | NaN | 585.9347 | 234.6501 | NaN | NaN | 243.8627 | -19.4054 | NaN | NaN | NaN | 502.8354 | 510.4696 | NaN | NaN | NaN | NaN
8563.1292 | 627.0346 | 281.8379 | 215.1486 | 218.2995 | 230.5073 | 278.968 | 342.4484 | 311.6183 | NaN | NaN | NaN | 597.8605 | 232.4862 | NaN | NaN | 293.0135 | NaN | NaN | NaN | NaN | 500.029 | 503.5234 | NaN | NaN | NaN | -18.4661
8564.1292 | 626.5151 | 281.2584 | 216.2474 | 218.0209 | 230.5028 | 277.967 | 341.5464 | 311.4766 | NaN | NaN | NaN | 585.5394 | 240.0275 | NaN | NaN | 269.4696 | NaN | NaN | NaN | NaN | 492.7663 | 498.0211 | NaN | -14.9786 | NaN | NaN
8565.1292 | 626.2035 | 281.1979 | 216.202 | 217.9562 | 230.2935 | 278.3323 | 341.1752 | 314.5896 | NaN | NaN | NaN | 596.2501 | 246.4107 | NaN | NaN | 275.8477 | NaN | NaN | NaN | NaN | 494.746 | 490.591 | NaN | NaN | NaN | NaN
8566.1292 | 624.6194 | 281.8717 | 215.215 | 217.6802 | 229.8035 | 277.7924 | 341.6754 | 315.6434 | NaN | NaN | NaN | 630.5527 | 250.6277 | NaN | NaN | 267.2575 | NaN | NaN | NaN | NaN | 499.59 | 489.9028 | NaN | NaN | NaN | NaN
8567.1292 | 620.7325 | 281.3358 | 215.7883 | 217.4141 | 229.5632 | 278.5863 | 341.1186 | 316.6055 | NaN | NaN | NaN | 656.4487 | 249.0552 | NaN | NaN | 329.7374 | 4.1959 | NaN | NaN | NaN | 478.5971 | 472.1178 | NaN | NaN | NaN | NaN
8568.1292 | 618.4088 | 281.4445 | 216.08 | 217.4731 | 229.4472 | 280.2794 | 341.2033 | 317.7642 | NaN | NaN | NaN | 647.5493 | 263.6667 | NaN | NaN | 327.095 | NaN | NaN | NaN | NaN | 464.0827 | 453.4579 | NaN | NaN | NaN | NaN
8569.1292 | 619.5243 | 281.4614 | 215.6142 | 217.4487 | 229.4527 | 283.072 | 342.1335 | 320.1391 | NaN | NaN | NaN | 639.3354 | 265.8011 | NaN | NaN | 335.8196 | NaN | NaN | NaN | NaN | 455.8333 | 441.8648 | NaN | NaN | NaN | NaN
8570.1292 | 620.8502 | 280.5775 | 216.2122 | 217.8929 | 229.7391 | 282.152 | 341.7966 | 319.3764 | NaN | NaN | NaN | 644.9638 | 273.8908 | NaN | NaN | 352.574 | NaN | NaN | NaN | NaN | 451.328 | 436.196 | NaN | NaN | NaN | NaN
8571.1292 | 621.4646 | 280.4186 | 216.9655 | 217.9503 | 230.372 | 280.6743 | 341.3505 | 319.015 | NaN | NaN | NaN | 636.9538 | 285.687 | NaN | NaN | 353.5277 | NaN | NaN | NaN | NaN | 436.3996 | 421.0794 | NaN | NaN | NaN | NaN
8572.1292 | 621.8532 | 280.633 | 217.4217 | 218.6543 | 230.9394 | 280.3416 | 341.2109 | 317.5294 | NaN | NaN | NaN | 624.6327 | 290.6037 | NaN | 1256.8482 | 365.3254 | NaN | NaN | NaN | NaN | 429.7634 | 408.6845 | NaN | NaN | NaN | NaN
8573.1292 | 622.4785 | 280.0851 | 217.5461 | 219.0388 | 231.3061 | 283.5503 | 341.5895 | 317.1683 | NaN | NaN | NaN | 634.4011 | 271.5979 | NaN | NaN | 341.6998 | NaN | NaN | NaN | NaN | 498.399 | 422.715 | NaN | NaN | NaN | NaN
8574.1292 | 622.2241 | 280.1278 | 218.2917 | 219.3 | 231.939 | 285.7475 | 341.0032 | 315.1893 | NaN | NaN | NaN | 619.7116 | 252.9835 | NaN | NaN | 340.3891 | NaN | NaN | NaN | NaN | 487.7365 | 431.2847 | NaN | -16.3957 | NaN | NaN
8575.1292 | 621.397 | 280.5902 | 218.0317 | 219.804 | 232.3087 | 284.6352 | 340.9824 | 314.0127 | NaN | NaN | NaN | 605.6855 | 227.4866 | NaN | NaN | 323.8169 | NaN | NaN | NaN | NaN | 544.1923 | 442.4851 | NaN | NaN | NaN | NaN
8576.1292 | 621.6512 | 280.6745 | 217.4566 | 219.7686 | 232.2876 | 284.9698 | 340.9664 | 313.8177 | NaN | NaN | NaN | 602.0734 | 207.0553 | NaN | NaN | 315.9726 | NaN | NaN | NaN | NaN | 552.2765 | 458.5029 | NaN | NaN | NaN | NaN
8577.1292 | 621.3685 | 280.014 | 217.2528 | 219.5065 | 232.1074 | 283.9899 | 342.7074 | 314.1097 | NaN | NaN | NaN | 614.7058 | 225.2115 | NaN | NaN | 310.6365 | NaN | NaN | NaN | NaN | 538.4947 | 470.8046 | NaN | NaN | NaN | NaN
8578.1292 | 623.0669 | 279.8351 | 218.6477 | 219.4798 | 232.1851 | 283.2292 | 342.5705 | 314.1786 | NaN | NaN | NaN | 614.9288 | 223.6881 | NaN | NaN | 305.0237 | NaN | NaN | NaN | NaN | 532.7053 | 485.0206 | NaN | NaN | NaN | NaN
8579.1292 | 624.0967 | 280.2481 | 218.0734 | 219.1237 | 232.2289 | 282.4297 | 343.0228 | 313.871 | NaN | NaN | NaN | 611.9055 | 230.568 | NaN | NaN | 300.8247 | NaN | NaN | NaN | NaN | 532.0421 | 491.4197 | NaN | NaN | NaN | NaN
8580.1292 | 627.8321 | 280.3822 | 217.4563 | 218.7896 | 232.6269 | 281.4452 | 342.0912 | 312.2867 | NaN | NaN | NaN | 602.3425 | 227.3951 | NaN | NaN | 296.6871 | NaN | NaN | NaN | NaN | 521.0391 | 497.2314 | NaN | -11.0514 | NaN | NaN
8581.1292 | 629.1579 | 281.3355 | 216.5036 | 218.6279 | 232.6706 | 281.5992 | 342.165 | 312.9429 | NaN | NaN | NaN | 592.9919 | 241.3119 | NaN | NaN | 286.3447 | NaN | NaN | NaN | NaN | 501.2836 | 488.2662 | NaN | NaN | NaN | NaN
8582.1292 | 627.2675 | 282.3759 | 216.774 | 218.3929 | 232.2964 | 281.1911 | 342.819 | 311.7736 | NaN | NaN | NaN | 572.2052 | 248.4394 | NaN | NaN | 268.7572 | NaN | NaN | NaN | NaN | 500.5239 | 489.6041 | NaN | -17.0884 | NaN | NaN
8583.1292 | 625.8554 | 282.8777 | 216.5663 | 218.4013 | 231.5388 | 280.5248 | 342.5791 | 311.0521 | NaN | NaN | NaN | 558.1933 | 244.8965 | NaN | NaN | 278.7844 | NaN | NaN | NaN | NaN | 505.8126 | 490.5165 | NaN | -10.9172 | NaN | NaN
8584.1292 | 625.7582 | 283.2865 | 216.1819 | 218.1707 | 231.1723 | 280.6066 | 343.6961 | 309.3627 | NaN | NaN | NaN | 579.1749 | 254.7728 | NaN | NaN | 302.9583 | NaN | NaN | NaN | NaN | 518.1752 | 497.8369 | NaN | NaN | NaN | NaN
8585.1292 | 624.6251 | 283.6727 | 217.7444 | 218.2721 | 231.2187 | 278.7326 | 342.7142 | 308.0504 | NaN | NaN | NaN | 612.4564 | 242.8378 | NaN | NaN | 327.221 | 2.3649 | NaN | NaN | NaN | 518.4641 | 495.6753 | NaN | NaN | NaN | NaN
8586.1292 | 623.7935 | 284.9608 | 217.053 | 218.145 | 231.1313 | 278.1928 | 343.0782 | 307.2242 | NaN | NaN | NaN | 651.8566 | 257.3993 | NaN | NaN | 294.7112 | NaN | NaN | NaN | NaN | 518.3741 | 496.9156 | NaN | NaN | NaN | NaN
8587.1292 | 623.4645 | 285.0926 | 216.8617 | 218.2118 | 230.9997 | 278.1667 | 342.2504 | 305.6667 | NaN | NaN | NaN | 655.4209 | 236.3437 | NaN | NaN | 257.4653 | NaN | NaN | NaN | NaN | 525.8782 | 507.6197 | NaN | 5.2119 | NaN | 1.3253
8588.1292 | 626.2819 | 286.9069 | 216.3905 | 218.7454 | 230.856 | 277.6885 | 341.6966 | 304.3373 | NaN | NaN | NaN | 666.0029 | 217.6859 | NaN | NaN | 248.2853 | NaN | NaN | NaN | NaN | 588.7639 | 524.731 | NaN | 6.5997 | NaN | 5.8989
8589.1292 | 628.6319 | 286.9012 | 215.9528 | 218.9031 | 230.801 | 277.1911 | 341.7439 | 304.6094 | NaN | NaN | NaN | 692.1089 | 195.053 | NaN | NaN | 241.8084 | NaN | NaN | NaN | NaN | 596.7213 | 538.174 | NaN | 23.3379 | NaN | NaN
8590.1292 | 627.4955 | 286.2372 | 215.4735 | 218.4409 | 230.5337 | 277.9438 | 341.5706 | 303.6826 | NaN | NaN | NaN | 720.7032 | 192.832 | NaN | NaN | 233.6276 | NaN | NaN | NaN | NaN | 589.0619 | 552.4326 | NaN | -11.9054 | NaN | 7.4124
8591.1292 | 626.2256 | 285.5879 | 215.1004 | 218.7791 | 230.2287 | 278.6048 | 341.5584 | 303.2618 | NaN | NaN | NaN | 723.5325 | 185.0714 | NaN | NaN | 227.5156 | NaN | NaN | NaN | NaN | 593.7988 | 564.3662 | NaN | -12.7715 | NaN | NaN
8592.1292 | 626.6499 | 285.6354 | 215.0828 | 218.4909 | 229.714 | 278.6101 | 341.4668 | 303.2595 | NaN | NaN | NaN | 684.3931 | 177.3641 | NaN | NaN | 221.517 | NaN | NaN | NaN | NaN | 598.6536 | 575.8189 | NaN | -6.8857 | NaN | NaN
8593.1292 | 625.3229 | 285.8406 | 214.7311 | 218.1291 | 229.4254 | 279.2033 | 342.1875 | 303.1051 | NaN | NaN | NaN | 694.6639 | 179.4716 | NaN | NaN | 216.5426 | NaN | NaN | NaN | NaN | 600.7239 | 594.993 | NaN | 24.5741 | NaN | -13.5515
8594.1292 | 623.2522 | 287.4489 | 214.628 | 217.8832 | 229.2317 | 278.6073 | 343.4508 | 302.9707 | NaN | NaN | NaN | 708.5756 | 181.0172 | NaN | NaN | 214.9097 | NaN | NaN | NaN | NaN | 606.7335 | 603.3042 | NaN | 2.6038 | NaN | 25.5958
8595.1292 | 624.8195 | 286.583 | 214.185 | 217.8625 | 228.9352 | 277.5435 | 343.0548 | 301.772 | NaN | NaN | NaN | 680.6623 | 176.862 | NaN | NaN | 206.5345 | NaN | NaN | NaN | NaN | 604.5923 | 601.183 | NaN | -4.7437 | NaN | -18.6475
8596.1292 | 625.5741 | 285.9176 | 214.3286 | 218.0465 | 228.6709 | 277.168 | 343.0003 | 300.8797 | NaN | NaN | NaN | 664.1247 | 183.238 | NaN | NaN | 200.7588 | NaN | NaN | NaN | NaN | 602.4939 | 597.0793 | NaN | -3.7578 | NaN | -6.61
8597.1292 | 622.0393 | 286.8647 | 214.3751 | 217.6642 | 228.2489 | 276.3576 | 342.6177 | 299.8645 | NaN | NaN | NaN | 641.5124 | 186.7523 | NaN | NaN | 191.0364 | NaN | NaN | NaN | NaN | 594.8342 | 586.2773 | NaN | 5.5532 | NaN | 4.2104
8598.1292 | 620.3686 | 285.8486 | 214.3864 | 217.3918 | 228.0341 | 277.0458 | 342.4795 | 299.6929 | NaN | NaN | NaN | 636.5062 | 194.9626 | NaN | NaN | 197.332 | NaN | NaN | NaN | NaN | 589.9194 | 578.7314 | NaN | 25.4394 | NaN | NaN
8599.1292 | 617.0469 | 286.2687 | 214.8098 | 217.2589 | 227.7776 | 275.8445 | 342.7824 | 300.2374 | NaN | NaN | NaN | 662.1845 | 217.6986 | NaN | NaN | 209.9727 | NaN | NaN | NaN | NaN | 579.9005 | 556.4801 | NaN | -3.7414 | NaN | -8.3885
8600.1292 | 616.0624 | 286.6854 | 214.7163 | 217.331 | 227.5408 | 275.9669 | 342.5444 | 299.6038 | NaN | NaN | NaN | 689.2064 | 217.9993 | NaN | NaN | 232.1065 | NaN | NaN | NaN | NaN | 583.7382 | 552.781 | NaN | NaN | NaN | -8.9766
8601.1292 | 616.9583 | 286.3854 | 214.169 | 217.4987 | 227.5285 | 276.7413 | 341.6192 | 297.9512 | NaN | NaN | NaN | 666.355 | 211.4703 | NaN | NaN | 256.1393 | NaN | NaN | NaN | NaN | 573.9072 | 546.1204 | NaN | -18.8738 | NaN | NaN
8602.1292 | 618.8727 | 285.9546 | 214.0173 | 217.7047 | 227.7067 | 275.3449 | 342.1777 | 299.1453 | NaN | NaN | NaN | 674.1336 | 209.9874 | NaN | NaN | 253.4322 | NaN | NaN | NaN | NaN | 628.841 | 548.0943 | NaN | -4.0501 | NaN | -4.3808
8603.1292 | 618.149 | 285.5668 | 214.0624 | 218.1823 | 227.9874 | 275.1724 | 342.1025 | 298.8837 | NaN | NaN | NaN | 660.2644 | 213.0245 | NaN | NaN | 221.5365 | NaN | NaN | NaN | NaN | 596.6275 | 557.2055 | NaN | -16.9406 | NaN | NaN
8604.1292 | 615.4238 | 285.0583 | 213.2967 | 217.9617 | 228.3272 | 274.8415 | 340.8639 | 297.4863 | NaN | NaN | NaN | 644.8081 | 204.214 | NaN | NaN | 211.7093 | NaN | NaN | NaN | NaN | 590.1726 | 555.6048 | NaN | -3.8957 | NaN | NaN
8605.1292 | 614.7476 | 285.5566 | 213.4367 | 217.9501 | 228.1758 | 274.7491 | 341.4825 | 297.9556 | NaN | NaN | NaN | 634.9474 | 208.2514 | NaN | NaN | 201.1692 | NaN | NaN | NaN | NaN | 599.0794 | 561.8325 | NaN | 12.6312 | NaN | NaN
8606.1292 | 613.1193 | 286.3267 | 213.4636 | 217.7186 | 227.6981 | 275.634 | 341.0877 | 297.1002 | NaN | NaN | NaN | 616.489 | 205.5776 | NaN | NaN | 197.7868 | NaN | NaN | NaN | NaN | 604.5337 | 572.0627 | NaN | -12.3345 | NaN | NaN
8607.1292 | 614.747 | 286.5701 | 213.9448 | 217.756 | 227.6362 | 274.3831 | 341.533 | 295.7097 | NaN | NaN | NaN | 611.1245 | 197.6179 | NaN | NaN | 210.2564 | NaN | NaN | NaN | NaN | 609.1895 | 577.6123 | NaN | -12.7268 | NaN | -16.024
8608.1292 | 617.0289 | 287.2315 | 214.0547 | 217.8308 | 227.6102 | 274.4196 | 341.4392 | 294.5877 | NaN | NaN | NaN | 632.7002 | 133.5552 | NaN | NaN | 224.1737 | 30.5323 | NaN | NaN | NaN | 560.5417 | 513.5608 | NaN | NaN | NaN | NaN
8609.1292 | 614.0713 | 287.3301 | 214.3815 | 217.7976 | 227.5683 | 273.635 | 340.2203 | 293.6116 | NaN | NaN | NaN | 611.8103 | 266.5914 | NaN | NaN | 328.8015 | NaN | NaN | NaN | NaN | 516.0506 | 453.1335 | NaN | NaN | NaN | NaN
8610.1292 | 611.1659 | 286.7026 | 214.4264 | 218.257 | 227.4793 | 273.9925 | 340.0279 | 293.5796 | NaN | NaN | NaN | 612.4304 | 317.9208 | NaN | 182.1973 | 402.5068 | 4.3617 | NaN | NaN | NaN | 464.4333 | 387.5961 | NaN | NaN | NaN | NaN
8611.1292 | 608.7832 | 285.9659 | 214.3167 | 218.6069 | 227.5523 | 277.1981 | 340.3508 | 296.6204 | NaN | NaN | NaN | 609.623 | 305.3565 | NaN | 813.8163 | 317.0852 | NaN | NaN | NaN | NaN | 482.1648 | 392.2612 | NaN | -17.6517 | NaN | -18.0561
8612.1292 | 607.2984 | 285.6981 | 214.3474 | 218.2578 | 227.5282 | 276.2068 | 339.8484 | 300.0125 | NaN | NaN | NaN | 618.073 | 291.7814 | NaN | 898.2931 | 308.9369 | NaN | NaN | NaN | NaN | 482.4986 | 404.9047 | NaN | NaN | NaN | -18.8952
8613.1292 | 605.0111 | 285.0731 | 214.5773 | 217.9947 | 227.3387 | 275.8313 | 339.787 | 299.7877 | NaN | NaN | NaN | 628.9909 | 308.753 | NaN | 254.9983 | 401.8115 | NaN | NaN | NaN | NaN | 472.5322 | 388.7014 | NaN | NaN | NaN | -18.3025
8614.1292 | 603.0133 | 283.9594 | 214.4057 | 218.1297 | 227.6561 | 276.4464 | 338.853 | 300.1113 | NaN | NaN | NaN | 608.9907 | 325.191 | NaN | 172.3291 | 391.662 | NaN | NaN | NaN | NaN | 466.4166 | 373.7583 | NaN | NaN | NaN | NaN
8615.1292 | 601.9009 | 284.7893 | 215.2357 | 218.1574 | 227.8217 | 277.3141 | 338.0199 | 301.3886 | NaN | NaN | NaN | 613.016 | 305.5747 | NaN | 472.0297 | 400.1632 | NaN | NaN | NaN | NaN | 480.3044 | 385.5061 | NaN | NaN | NaN | NaN
8616.1292 | 598.5451 | 283.7926 | 215.1563 | 218.55 | 228.1552 | 277.3093 | 337.26 | 302.7101 | NaN | NaN | NaN | 617.2533 | 285.0868 | NaN | 552.0076 | 399.6632 | NaN | NaN | NaN | NaN | 483.9785 | 394.7376 | NaN | NaN | NaN | NaN
8617.1292 | 597.3323 | 283.4485 | 215.3742 | 218.9654 | 228.6456 | 279.5723 | 337.0486 | 303.8921 | NaN | NaN | NaN | 635.9024 | 294.3418 | NaN | 1004.1166 | 379.4191 | NaN | NaN | NaN | NaN | 496.0588 | 406.5452 | NaN | NaN | NaN | NaN
8618.1292 | 595.4618 | 283.5702 | 215.2245 | 219.1045 | 228.9487 | 279.4925 | 336.9799 | 302.7117 | NaN | NaN | NaN | 653.9196 | 286.4036 | NaN | 917.0643 | 397.8242 | NaN | NaN | NaN | NaN | 494.6205 | 409.1025 | NaN | NaN | NaN | NaN
8619.1292 | 593.8333 | 283.5328 | 215.9323 | 219.7998 | 229.6538 | 280.4514 | 335.5323 | 301.7514 | NaN | NaN | NaN | 656.0476 | 280.5247 | NaN | 145.3061 | 394.9563 | NaN | NaN | NaN | NaN | 477.8853 | 387.5322 | NaN | NaN | NaN | -18.64
8620.1292 | 592.8419 | 283.5421 | 215.6651 | 219.2166 | 230.0352 | 279.8727 | 334.8644 | 301.7485 | NaN | NaN | NaN | 629.1663 | 317.9419 | NaN | NaN | 426.1655 | NaN | NaN | NaN | NaN | 458.2013 | 362.0181 | NaN | NaN | NaN | NaN
8621.1292 | 588.7571 | 283.752 | 216.2292 | 219.4645 | 230.4327 | 278.7586 | 334.6959 | 299.8757 | NaN | NaN | NaN | 605.8166 | 315.6582 | NaN | NaN | 425.7438 | NaN | NaN | NaN | NaN | 456.0447 | 363.1985 | NaN | NaN | NaN | NaN
8622.1292 | 584.9251 | 283.9107 | 216.3559 | 219.5949 | 230.4578 | 278.69 | 335.4322 | 300.296 | NaN | NaN | NaN | 592.6245 | 316.0488 | NaN | -11.4637 | 410.1717 | NaN | NaN | NaN | NaN | 462.1131 | 369.5096 | NaN | NaN | NaN | NaN
8623.1292 | 585.9148 | 283.844 | 216.3313 | 219.306 | 231.3966 | 277.5684 | 335.7748 | 301.4645 | NaN | NaN | NaN | 575.0662 | 224.7356 | NaN | -16.7351 | 280.6392 | 7.5515 | NaN | NaN | NaN | 457.8826 | 365.4004 | NaN | NaN | NaN | NaN
8624.1292 | 584.5486 | 283.8833 | 216.3121 | 219.2312 | 231.2479 | 277.7592 | 335.9628 | 302.1727 | NaN | NaN | NaN | 571.168 | 293.9156 | NaN | NaN | 470.4679 | NaN | NaN | NaN | NaN | 440.3134 | 332.5044 | NaN | NaN | NaN | NaN
8625.1292 | 584.3749 | 284.588 | 217.0214 | 219.277 | 231.2878 | 280.2778 | 335.321 | 302.8121 | NaN | NaN | NaN | 556.4167 | 290.623 | NaN | NaN | 450.9187 | NaN | NaN | NaN | NaN | 460.4394 | 355.7846 | NaN | NaN | NaN | NaN
8626.1292 | 585.181 | 284.8436 | 217.3767 | 218.9231 | 231.2855 | 281.092 | 335.7419 | 302.2134 | NaN | NaN | NaN | 542.5624 | 314.1851 | NaN | NaN | 365.6174 | NaN | NaN | NaN | NaN | 449.0922 | 344.0418 | NaN | NaN | NaN | NaN
8627.1292 | 584.3799 | 285.3568 | 217.4316 | 218.9348 | 230.9962 | 281.9449 | 336.9323 | 301.959 | NaN | NaN | NaN | 544.6656 | 319.1991 | NaN | NaN | 382.6313 | NaN | NaN | NaN | NaN | 446.5281 | 326.1796 | NaN | NaN | NaN | NaN
8628.1292 | 585.5813 | 285.059 | 217.8252 | 218.8082 | 230.8596 | 281.4768 | 336.6642 | 303.8378 | NaN | NaN | NaN | 545.829 | 286.9649 | NaN | 2.0596 | 363.1867 | NaN | NaN | NaN | NaN | 428.4388 | 314.3464 | NaN | NaN | NaN | NaN
8629.1292 | 588.1189 | 284.1333 | 217.7318 | 218.7312 | 230.7205 | 281.3376 | 336.4166 | 304.6077 | NaN | NaN | NaN | 556.2924 | 328.5221 | NaN | NaN | 363.2532 | NaN | NaN | NaN | NaN | 462.5358 | 319.4985 | NaN | NaN | NaN | NaN
8630.1292 | 587.3211 | 283.6985 | 216.4203 | 218.3532 | 230.5548 | 279.5166 | 335.9614 | 303.972 | NaN | NaN | NaN | 545.9588 | 309.5895 | NaN | NaN | 349.0306 | NaN | NaN | NaN | NaN | 443.6829 | 325.3991 | NaN | NaN | NaN | NaN
8631.1292 | 585.1736 | 283.7094 | 216.6928 | 218.013 | 230.2347 | 279.3145 | 336.3649 | 304.037 | NaN | NaN | NaN | 539.33 | 293.5378 | NaN | NaN | 366.7379 | -3.2701 | NaN | NaN | NaN | 436.4619 | 317.3558 | NaN | NaN | NaN | NaN
8632.1292 | 583.2047 | 283.347 | 217.1894 | 217.9003 | 230.3087 | 278.9787 | 337.1996 | 302.5414 | NaN | NaN | NaN | 536.0284 | 304.2264 | NaN | NaN | 363.3329 | NaN | NaN | NaN | NaN | 456.8464 | 330.6282 | NaN | NaN | NaN | NaN
8633.1292 | 583.3936 | 282.7334 | 217.4746 | 217.5112 | 230.1319 | 278.3927 | 338.0496 | 301.1484 | NaN | NaN | NaN | 549.6697 | 339.5677 | NaN | NaN | 355.2901 | NaN | NaN | NaN | NaN | 457.8267 | 330.7591 | NaN | NaN | NaN | NaN
8634.1292 | 583.501 | 283.0906 | 217.4711 | 217.3104 | 230.0608 | 278.5509 | 337.2132 | 300.3676 | NaN | NaN | NaN | 549.4937 | 298.2821 | NaN | 120.5771 | 396.5657 | -11.2171 | NaN | NaN | NaN | 393.613 | 263.2455 | NaN | NaN | NaN | NaN
8635.1292 | 582.6147 | 282.8433 | 217.6061 | 217.2866 | 230.0131 | 279.4636 | 338.1185 | 301.556 | NaN | NaN | NaN | 545.6518 | 331.8352 | NaN | 360.1468 | 437.3747 | NaN | NaN | NaN | NaN | 365.2123 | 220.6528 | NaN | NaN | NaN | NaN
8636.1292 | 583.2514 | 282.6305 | 217.6485 | 217.5663 | 229.6513 | 280.4327 | 338.7684 | 302.8148 | NaN | NaN | NaN | 546.6399 | 404.3525 | NaN | 224.1009 | 520.648 | 5.7607 | NaN | NaN | NaN | 354.5937 | 205.4692 | NaN | NaN | NaN | NaN
8637.1292 | 584.6706 | 282.7282 | 217.6582 | 217.5358 | 229.3681 | 281.8123 | 338.8446 | 303.2795 | NaN | NaN | NaN | 550.6287 | 395.4294 | NaN | 220.061 | 507.532 | NaN | NaN | NaN | NaN | 352.6999 | 190.0419 | NaN | NaN | NaN | NaN
8638.1292 | 584.8591 | 282.0407 | 216.7432 | 217.2329 | 229.1338 | 282.692 | 339.1391 | 304.6842 | NaN | NaN | NaN | 575.2733 | 360.7713 | NaN | 11.591 | 460.3604 | 25.0486 | NaN | NaN | NaN | 430.9742 | 202.9753 | NaN | NaN | NaN | NaN
8639.1292 | 584.2193 | 281.7831 | 217.2775 | 216.9729 | 228.8106 | 282.5602 | 338.7148 | 304.7177 | NaN | NaN | NaN | 577.2746 | 330.6101 | NaN | -3.0247 | 434.775 | NaN | NaN | NaN | NaN | 429.1182 | 222.3533 | NaN | NaN | NaN | NaN
8640.1292 | 583.9461 | 281.5413 | 216.2129 | 216.9273 | 228.6379 | 282.6073 | 337.9714 | 305.2194 | NaN | NaN | NaN | 560.7185 | 358.2728 | NaN | 23.0489 | 418.4814 | NaN | NaN | NaN | NaN | 409.4224 | 232.4153 | NaN | NaN | NaN | NaN
8641.1292 | 584.8443 | 281.9867 | 215.8308 | 216.9165 | 228.5514 | 281.2323 | 335.8667 | 304.8022 | NaN | NaN | NaN | 552.985 | 382.6923 | NaN | 50.9912 | 407.2173 | NaN | NaN | NaN | NaN | 403.0583 | 236.8293 | NaN | -19.9258 | NaN | NaN
8642.1292 | 585.9297 | 283.0616 | 215.7892 | 217.2283 | 228.386 | 280.426 | 336.0221 | 303.0364 | NaN | NaN | NaN | 545.7026 | 321.4067 | NaN | 13.1874 | 407.4615 | NaN | NaN | NaN | NaN | 413.9014 | 250.2818 | NaN | NaN | NaN | NaN
8643.1292 | 585.8795 | 282.4138 | 216.003 | 217.437 | 228.447 | 282.8455 | 335.7204 | 301.8417 | NaN | NaN | NaN | 540.2017 | 336.706 | NaN | 3.9223 | 398.3563 | NaN | NaN | NaN | NaN | 416.474 | 261.2163 | NaN | NaN | NaN | NaN
8644.1292 | 586.8848 | 282.3978 | 216.1474 | 217.4945 | 228.4789 | 281.1996 | 336.1657 | 301.858 | NaN | NaN | NaN | 536.0243 | 379.4255 | NaN | -19.9823 | 397.2097 | NaN | NaN | NaN | NaN | 429.2793 | 271.6156 | NaN | NaN | NaN | NaN
8645.1292 | 588.8961 | 283.1218 | 216.4689 | 217.8059 | 228.4855 | 280.3551 | 336.959 | 301.2181 | NaN | NaN | NaN | 532.6384 | 342.9689 | NaN | -11.1822 | 393.7865 | NaN | NaN | NaN | NaN | 429.6518 | 278.0234 | NaN | NaN | NaN | NaN
8646.1292 | 591.1466 | 284.967 | 216.8558 | 217.8824 | 228.2434 | 279.4484 | 339.6369 | 302.0508 | NaN | NaN | NaN | 526.1116 | 291.9883 | NaN | -18.6189 | 385.5941 | NaN | NaN | NaN | NaN | 431.2862 | 288.1391 | NaN | NaN | NaN | NaN
8647.1292 | 592.7441 | 285.6025 | 217.2795 | 217.8655 | 228.2571 | 278.6564 | 339.2523 | 300.313 | NaN | NaN | NaN | 520.4043 | 346.2233 | NaN | 23.4606 | 372.6947 | NaN | NaN | NaN | NaN | 419.003 | 278.9826 | NaN | NaN | NaN | NaN
8648.1292 | 596.3318 | 287.0935 | 217.2388 | 217.9825 | 228.2384 | 278.2601 | 339.4123 | 299.2785 | NaN | NaN | NaN | 516.5858 | 363.1641 | NaN | 40.9331 | 373.0193 | NaN | NaN | NaN | NaN | 413.7311 | 270.3701 | NaN | NaN | NaN | NaN
8649.1292 | 597.6321 | 288.9679 | 217.8077 | 218.0701 | 228.7398 | 278.0143 | 338.8541 | 297.998 | NaN | NaN | NaN | 547.4691 | 341.2556 | NaN | 68.6829 | 491.4739 | NaN | NaN | NaN | NaN | 416.8674 | 265.4132 | NaN | NaN | NaN | NaN
8650.1292 | 602.1491 | 292.1887 | 218.5202 | 218.0841 | 228.6379 | 278.719 | 338.7046 | 297.1029 | NaN | NaN | NaN | 564.84 | 341.9805 | NaN | 109.8802 | 534.2277 | -2.4716 | NaN | NaN | NaN | 413.5264 | 254.3039 | NaN | NaN | NaN | NaN
8651.1292 | 604.0435 | 294.2375 | 219.0956 | 218.1548 | 228.6827 | 280.0387 | 338.7631 | 295.6095 | NaN | NaN | NaN | 587.1619 | 361.5358 | NaN | 172.4933 | 594.966 | NaN | NaN | NaN | NaN | 400.0563 | 225.9762 | NaN | NaN | NaN | NaN
8652.1292 | 604.0599 | 294.4886 | 219.3647 | 218.3081 | 229.2045 | 282.0782 | 340.915 | 296.1523 | NaN | NaN | NaN | 580.1763 | 310.7443 | NaN | 352.2974 | 416.4806 | 8.5774 | NaN | NaN | NaN | 382.2077 | 209.9464 | NaN | NaN | NaN | NaN
8653.1292 | 606.7222 | 296.1649 | 219.2122 | 218.526 | 229.2603 | 280.9959 | 341.2606 | 296.3197 | NaN | NaN | NaN | 570.3028 | 376.7924 | NaN | 215.6396 | 414.6978 | NaN | NaN | NaN | NaN | 389.6368 | 209.1635 | NaN | NaN | NaN | NaN
8654.1292 | 608.2339 | 297.3631 | 219.3227 | 219.0992 | 229.3847 | 281.6032 | 341.0987 | 296.8909 | NaN | NaN | NaN | 562.1443 | 343.2353 | NaN | 194.0628 | 491.7997 | NaN | NaN | NaN | NaN | 371.7775 | 196.8433 | NaN | NaN | NaN | NaN
8655.1292 | 606.7012 | 298.1179 | 220.123 | 219.4421 | 229.5318 | 282.1223 | 341.1151 | 296.3019 | NaN | NaN | NaN | 604.5892 | 395.3861 | NaN | 217.142 | 493.6511 | NaN | NaN | NaN | NaN | 382.1175 | 195.362 | NaN | NaN | NaN | NaN
8656.1292 | 604.9497 | 300.1492 | 221.0686 | 219.7556 | 229.2606 | 282.5412 | 342.1553 | 296.4712 | NaN | NaN | NaN | 615.6571 | 341.7892 | NaN | 302.6893 | 618.7696 | 0.2305 | NaN | NaN | NaN | 361.5945 | 181.6518 | NaN | NaN | NaN | NaN
8657.1292 | 603.6984 | 301.6685 | 221.356 | 220.0747 | 228.9309 | 282.9425 | 341.6742 | 295.8609 | NaN | NaN | NaN | 599.8013 | 386.2386 | NaN | 232.1277 | 616.8499 | NaN | NaN | NaN | NaN | 356.5882 | 174.3322 | NaN | NaN | NaN | NaN
8658.1292 | 603.2282 | 303.2286 | 222.4275 | 220.2188 | 228.7441 | 283.5191 | 341.5522 | 294.9948 | NaN | NaN | NaN | 589.1408 | 354.3418 | NaN | 262.6413 | 623.1385 | NaN | NaN | NaN | NaN | 348.5254 | 168.8283 | NaN | NaN | NaN | NaN
8659.1292 | 600.078 | 303.3555 | 222.1715 | 220.3086 | 228.7087 | 282.7953 | 341.0422 | 294.3945 | NaN | NaN | NaN | 594.3733 | 389.0114 | NaN | 375.567 | 521.7488 | NaN | NaN | NaN | NaN | 344.9749 | 159.4018 | NaN | NaN | NaN | NaN
8660.1292 | 597.9223 | 304.092 | 222.137 | 220.5642 | 229.2291 | 282.8738 | 341.886 | 292.3001 | NaN | NaN | NaN | 585.5107 | 411.1674 | NaN | 273.1222 | 706.8546 | 3.7402 | NaN | NaN | NaN | 336.9408 | 152.1552 | NaN | NaN | NaN | NaN
8661.1292 | 597.8503 | 303.4442 | 221.8477 | 220.5331 | 229.2343 | 282.8011 | 340.7947 | 290.4399 | NaN | NaN | NaN | 582.1457 | 398.9273 | NaN | 238.5238 | 702.6009 | NaN | NaN | NaN | NaN | 348.1116 | 167.3965 | NaN | NaN | NaN | NaN
8662.1292 | 599.6598 | 305.304 | 221.0927 | 221.051 | 229.418 | 281.5064 | 339.4764 | 290.0844 | NaN | NaN | NaN | 579.2555 | 430.5008 | NaN | 232.5165 | 695.8157 | NaN | NaN | NaN | NaN | 348.2997 | 160.2383 | NaN | NaN | NaN | NaN
8663.1292 | 603.0972 | 306.8812 | 221.6685 | 221.457 | 229.6262 | 281.1824 | 338.165 | 289.4608 | NaN | NaN | NaN | 590.7304 | 346.3798 | NaN | 434.9884 | 504.53 | -6.3081 | NaN | NaN | NaN | 340.4944 | 150.1986 | NaN | NaN | NaN | NaN
8664.1292 | 604.7616 | 306.5687 | 221.8839 | 221.7097 | 229.7424 | 280.1265 | 336.4479 | 289.3543 | NaN | NaN | NaN | 572.4601 | 395.4848 | NaN | 296.9216 | 456.1094 | NaN | NaN | NaN | NaN | 336.4078 | 152.4384 | NaN | NaN | NaN | NaN
8665.1292 | 602.8691 | 308.9514 | 221.4008 | 222.084 | 229.6387 | 280.3583 | 336.4967 | 287.9004 | NaN | NaN | NaN | 570.5915 | 354.4199 | NaN | 232.5999 | 515.7945 | NaN | NaN | NaN | NaN | 326.9543 | 142.5595 | NaN | NaN | NaN | NaN
8666.1448 | 601.4772 | 314.3262 | 221.8049 | 221.8174 | 229.5727 | 279.2822 | 335.8095 | 287.1768 | NaN | NaN | NaN | 582.9624 | 409.6421 | NaN | 374.1331 | 535.4496 | NaN | NaN | NaN | NaN | 310.8965 | 109.4308 | NaN | NaN | NaN | NaN
8667.1292 | 601.2317 | 319.7356 | 222.0772 | 221.9919 | 229.7472 | 279.9624 | 336.5264 | 285.9007 | NaN | NaN | NaN | 607.8136 | 421.4188 | NaN | 429.734 | 609.8501 | 1.7436 | NaN | NaN | NaN | 289.5647 | 89.0154 | NaN | NaN | NaN | NaN
8668.1448 | 604.196 | 326.0269 | 221.7959 | 221.9249 | 229.8758 | 280.0437 | 336.494 | 284.8968 | NaN | NaN | NaN | 605.4094 | 395.7273 | NaN | 338.2855 | 507.6533 | NaN | NaN | NaN | NaN | 284.6204 | 89.8641 | NaN | NaN | NaN | NaN
8669.1448 | 605.5098 | 329.6567 | 222.3788 | 222.2764 | 229.808 | 280.0491 | 336.3658 | 285.2374 | NaN | NaN | NaN | 607.2839 | 402.1172 | NaN | 430.1953 | 526.6422 | NaN | NaN | NaN | NaN | 257.651 | 62.2944 | NaN | NaN | NaN | NaN
8670.1448 | 604.5143 | 332.0326 | 222.8287 | 222.2673 | 230.2375 | 279.9274 | 336.1569 | 284.8041 | NaN | NaN | NaN | 608.4565 | 447.6854 | NaN | 291.1535 | 818.5532 | NaN | NaN | NaN | NaN | 272.9556 | 66.7452 | NaN | NaN | NaN | NaN
8671.1292 | 605.896 | 334.0207 | 222.7998 | 222.7832 | 230.714 | 280.158 | 336.8846 | 285.781 | NaN | NaN | NaN | 616.6504 | 399.2801 | NaN | 369.2021 | 767.452 | NaN | NaN | NaN | NaN | 265.4085 | 71.4591 | NaN | NaN | NaN | NaN
8672.1292 | 607.0693 | 334.8745 | 222.1321 | 222.5162 | 230.7319 | 279.5135 | 337.365 | 285.1652 | NaN | NaN | NaN | 614.479 | 399.8275 | NaN | 295.1026 | 796.6166 | NaN | NaN | NaN | NaN | 272.8471 | 81.7936 | NaN | NaN | NaN | NaN
8673.1292 | 606.766 | 335.2686 | 221.6243 | 222.3553 | 230.8885 | 280.4492 | 336.9838 | 284.5071 | NaN | NaN | NaN | 621.3214 | 664.832 | NaN | 265.597 | 509.4558 | NaN | NaN | NaN | NaN | 301.5952 | 87.771 | NaN | NaN | NaN | NaN
8674.1292 | 609.4537 | 333.6979 | 221.6146 | 222.1806 | 230.9247 | 280.8896 | 336.8629 | 285.1544 | NaN | NaN | NaN | 631.6982 | 497.6117 | NaN | 270.7537 | 491.1167 | NaN | NaN | NaN | NaN | 288.2523 | 91.9713 | NaN | NaN | NaN | NaN
8675.1292 | 609.8774 | 332.7612 | 222.1882 | 221.9837 | 231.3243 | 280.3594 | 336.1488 | 285.5236 | NaN | NaN | NaN | 640.0194 | 415.8581 | NaN | 366.9976 | 744.1046 | 1.4727 | NaN | NaN | NaN | 271.284 | 76.6691 | NaN | NaN | NaN | NaN
8676.1292 | 612.7029 | 334.0358 | 222.8688 | 222.4509 | 231.6656 | 282.2942 | 337.7369 | 287.2537 | NaN | NaN | NaN | 620.542 | 440.3266 | NaN | 346.4483 | 800.945 | NaN | NaN | NaN | NaN | 257.058 | 65.8164 | NaN | NaN | NaN | NaN
8677.1292 | 613.0575 | 334.6182 | 222.9171 | 222.5082 | 232.0847 | 283.8762 | 339.1833 | 287.7437 | NaN | NaN | NaN | 611.2953 | 443.1183 | NaN | 303.6883 | 508.6988 | NaN | NaN | NaN | NaN | 258.7633 | 66.1209 | NaN | NaN | NaN | NaN
8678.1292 | 614.4142 | 333.8324 | 223.5167 | 222.8114 | 232.6978 | 286.1654 | 340.2434 | 291.538 | NaN | NaN | NaN | 609.504 | 446.3621 | NaN | 282.6963 | 715.0391 | NaN | NaN | NaN | NaN | 262.1069 | 66.8987 | NaN | NaN | NaN | NaN
8679.1292 | 612.8848 | 334.9111 | 224.6536 | 223.3258 | 233.9563 | 285.5538 | 340.5535 | 292.5815 | NaN | NaN | NaN | 622.1469 | 426.2099 | NaN | 275.5074 | 555.6405 | 2.6538 | NaN | NaN | NaN | 293.1362 | 84.4073 | NaN | NaN | NaN | NaN
8680.1292 | 611.1293 | 336.653 | 225.3301 | 223.7741 | 234.7208 | 286.704 | 340.9761 | 291.8455 | NaN | NaN | NaN | 605.4164 | 412.4736 | NaN | 137.7614 | 520.5708 | NaN | NaN | NaN | NaN | 340.3108 | 112.9427 | NaN | NaN | NaN | NaN
8681.1292 | 611.3565 | 337.1514 | 225.5406 | 223.4006 | 235.3521 | 287.8982 | 341.7895 | 294.203 | NaN | NaN | NaN | 616.2967 | 409.8686 | NaN | 19.6269 | 546.1774 | 105.8344 | NaN | NaN | NaN | 391.6485 | 137.7478 | NaN | NaN | NaN | NaN
8682.1292 | 611.7357 | 337.5894 | 226.0803 | 223.7434 | 235.2469 | 289.2621 | 343.1458 | 293.5816 | NaN | NaN | NaN | 602.6828 | 383.0347 | NaN | NaN | 528.3814 | 41.7181 | NaN | NaN | NaN | 400.2742 | 169.4825 | NaN | NaN | NaN | NaN
8683.1292 | 610.6768 | 338.7197 | 226.5246 | 224.058 | 235.9614 | 289.0563 | 343.5255 | 292.2218 | NaN | NaN | NaN | 594.6618 | 407.5521 | NaN | NaN | 523.4014 | -7.1443 | NaN | NaN | NaN | 402.2123 | 197.6146 | NaN | NaN | NaN | NaN
8684.1292 | 608.6009 | 339.5444 | 226.7405 | 224.1444 | 236.1707 | 290.17 | 344.2104 | 293.9283 | NaN | NaN | NaN | 591.5962 | 392.7449 | NaN | NaN | 526.5578 | -8.0717 | NaN | NaN | NaN | 411.1834 | 214.6018 | NaN | NaN | NaN | NaN
8685.1292 | 608.8351 | 340.0914 | 226.9578 | 223.7191 | 235.7261 | 289.7933 | 345.9722 | 295.0029 | NaN | NaN | NaN | 588.3953 | 398.3614 | NaN | NaN | 505.4183 | NaN | NaN | NaN | NaN | 400.4317 | 217.3934 | NaN | NaN | NaN | NaN
8686.1292 | 605.7337 | 339.1544 | 227.0783 | 223.9345 | 235.9402 | 289.28 | 346.9782 | 295.3927 | NaN | NaN | NaN | 579.0688 | 463.065 | NaN | NaN | 583.0497 | NaN | NaN | NaN | NaN | 414.8127 | 219.1924 | NaN | -13.4959 | NaN | NaN
8687.1292 | 606.5429 | 340.0658 | 227.4495 | 224.1991 | 235.5474 | 289.9451 | 347.7623 | 296.9723 | NaN | NaN | NaN | 599.9948 | 369.4724 | NaN | -3.1638 | 496.917 | NaN | NaN | NaN | NaN | 405.3591 | 214.4236 | NaN | NaN | NaN | NaN
8688.1292 | 607.8489 | 340.5261 | 227.7691 | 224.6637 | 235.6225 | 292.8896 | 347.2846 | 298.1194 | NaN | NaN | NaN | 595.8935 | 398.2663 | NaN | NaN | 534.6162 | NaN | NaN | NaN | NaN | 420.2597 | 227.5647 | NaN | NaN | NaN | NaN
8689.1292 | 609.0976 | 340.1709 | 227.4225 | 224.5343 | 235.3108 | 293.7683 | 347.2085 | 297.0821 | NaN | NaN | NaN | 594.9968 | 485.4418 | NaN | 117.4624 | 643.5988 | -1.9329 | NaN | NaN | NaN | 457.798 | 234.9467 | NaN | NaN | NaN | NaN
8690.1292 | 611.2482 | 339.7 | 226.5972 | 224.4163 | 235.0885 | 293.5838 | 346.1768 | 296.4821 | NaN | NaN | NaN | 591.2989 | 458.4914 | NaN | NaN | 666.9154 | 974.6368 | NaN | NaN | NaN | 540.8312 | 254.9905 | NaN | NaN | NaN | NaN
8691.1292 | 611.8481 | 336.9822 | 225.9102 | 224.6926 | 235.8649 | 292.4256 | 346.7691 | 295.9169 | NaN | NaN | NaN | 596.1893 | 432.1947 | NaN | NaN | 654.0335 | NaN | NaN | NaN | NaN | 626.6044 | 272.7077 | NaN | NaN | NaN | -10.9496
8692.1292 | 611.0726 | 336.3945 | 225.7261 | 225.3432 | 236.1124 | 291.9593 | 345.5981 | 295.0077 | NaN | NaN | NaN | 627.0304 | 409.5983 | NaN | NaN | 646.3637 | NaN | NaN | NaN | NaN | 708.6928 | 286.6908 | NaN | NaN | NaN | NaN
8693.1292 | 610.4822 | 336.6569 | 225.8965 | 226.4937 | 236.1578 | 291.8916 | 344.875 | 294.3162 | NaN | NaN | NaN | 655.4689 | 422.3539 | NaN | 713.9846 | 559.269 | -18.0988 | NaN | NaN | NaN | 498.5647 | 267.9314 | NaN | NaN | NaN | NaN
8694.1292 | 609.3567 | 338.813 | 226.02 | 226.5013 | 236.1652 | 292.5336 | 345.494 | 293.9881 | NaN | NaN | NaN | 652.5858 | 425.9252 | NaN | NaN | 619.0411 | 1027.0784 | NaN | NaN | NaN | 576.9298 | 280.5005 | NaN | NaN | NaN | NaN
8695.1292 | 608.9601 | 338.1895 | 225.779 | 226.4249 | 235.8901 | 291.8994 | 345.4548 | 293.9665 | NaN | NaN | NaN | 647.2484 | 393.766 | NaN | NaN | 599.8408 | NaN | NaN | NaN | NaN | 660.0715 | 295.4528 | NaN | NaN | NaN | NaN
8696.1292 | 607.216 | 338.9404 | 226.2051 | 226.0257 | 235.3458 | 291.4014 | 345.4828 | 293.7823 | NaN | NaN | NaN | 627.5586 | 357.834 | NaN | NaN | 575.2698 | NaN | NaN | NaN | NaN | 684.9657 | 306.4027 | NaN | NaN | NaN | NaN
8697.1292 | 605.2394 | 339.3181 | 226.4934 | 226.0367 | 234.7834 | 290.965 | 344.6779 | 294.3844 | NaN | NaN | NaN | 615.1123 | 330.632 | NaN | NaN | 562.5507 | NaN | NaN | NaN | NaN | 670.4231 | 316.1908 | NaN | NaN | NaN | NaN
8698.1292 | 603.6332 | 340.5141 | 225.656 | 226.0221 | 234.4029 | 290.9629 | 344.7775 | 294.001 | NaN | NaN | NaN | 620.1347 | 312.3475 | NaN | NaN | 552.8982 | 1276.7556 | NaN | NaN | NaN | 661.2613 | 323.9027 | NaN | NaN | NaN | NaN
8699.1292 | 603.3446 | 340.9528 | 225.7978 | 226.1838 | 234.0137 | 291.4498 | 345.0363 | 294.1443 | NaN | NaN | NaN | 601.6161 | 281.201 | NaN | NaN | 526.2512 | 331.7628 | NaN | NaN | NaN | 619.2297 | 336.085 | NaN | NaN | NaN | NaN
8700.1292 | 601.5257 | 340.8753 | 226.0651 | 226.1042 | 233.9284 | 291.2968 | 345.3296 | 295.0451 | NaN | NaN | NaN | 596.592 | 281.0082 | NaN | NaN | 501.2093 | 15.1691 | NaN | NaN | NaN | 580.4669 | 342.1155 | NaN | NaN | NaN | NaN
8701.1292 | 600.3045 | 338.6492 | 225.7092 | 225.5202 | 233.7153 | 290.7914 | 347.2524 | 294.5396 | NaN | NaN | NaN | 597.5574 | 301.122 | NaN | NaN | 547.497 | 717.5413 | NaN | NaN | NaN | 640.4478 | 353.4061 | NaN | NaN | NaN | NaN
8702.1292 | 602.4827 | 336.3715 | 225.3977 | 225.3579 | 233.2553 | 290.4153 | 347.5014 | 294.528 | NaN | NaN | NaN | 615.4182 | 288.7765 | NaN | NaN | 554.5282 | NaN | NaN | NaN | NaN | 703.802 | 363.7567 | NaN | NaN | NaN | -19.5171
8703.1292 | 600.8935 | 335.3946 | 224.8549 | 225.2393 | 233.0113 | 291.0228 | 346.5003 | 296.2526 | NaN | NaN | NaN | 624.0395 | 277.4771 | NaN | NaN | 557.2409 | NaN | NaN | NaN | NaN | 720.7076 | 372.2214 | NaN | NaN | NaN | NaN
8704.1292 | 598.8313 | 335.4388 | 224.5424 | 225.1384 | 232.6718 | 292.1183 | 348.4755 | 299.2705 | NaN | NaN | NaN | 636.5819 | 286.3918 | NaN | NaN | 513.8228 | 181.9164 | NaN | NaN | NaN | 654.5189 | 379.0365 | NaN | NaN | NaN | NaN
8705.1292 | 598.4253 | 337.5483 | 224.6366 | 225.3072 | 232.86 | 294.5011 | 349.295 | 300.8462 | NaN | NaN | NaN | 624.6959 | 256.9512 | NaN | NaN | 532.8789 | 524.1419 | NaN | NaN | NaN | 684.7814 | 390.0579 | NaN | NaN | NaN | -17.6789
8706.1292 | 596.073 | 340.5873 | 224.3355 | 225.6622 | 232.8426 | 295.4811 | 350.3543 | 300.2143 | NaN | NaN | NaN | 614.2923 | 262.2301 | NaN | NaN | 516.8293 | 246.5219 | NaN | NaN | NaN | 674.6051 | 397.6366 | NaN | -11.2539 | NaN | NaN
8707.1292 | 595.1724 | 340.481 | 224.7064 | 225.8586 | 233.2599 | 295.5591 | 350.3239 | 300.7268 | NaN | NaN | NaN | 627.6701 | 274.2239 | NaN | NaN | 515.5518 | 245.3586 | NaN | NaN | NaN | 683.4495 | 405.996 | NaN | NaN | NaN | NaN
8708.1292 | 595.5423 | 339.216 | 224.859 | 226.0645 | 233.4816 | 296.2137 | 349.0756 | 301.9601 | NaN | NaN | NaN | 670.2788 | 284.4156 | NaN | NaN | 517.4373 | 212.5115 | NaN | NaN | NaN | 693.8376 | 424.4919 | NaN | NaN | NaN | NaN
8709.1292 | 596.0863 | 337.6647 | 225.2715 | 226.5556 | 234.6469 | 295.933 | 348.09 | 301.6096 | NaN | NaN | NaN | 673.6006 | 273.3893 | NaN | NaN | 509.2086 | 132.8045 | NaN | NaN | NaN | 693.5212 | 439.2447 | NaN | NaN | NaN | NaN
8710.1292 | 597.4299 | 337.5477 | 224.8794 | 226.7591 | 235.2139 | 296.7143 | 348.2569 | 303.5689 | NaN | NaN | NaN | 684.1872 | 284.7041 | NaN | NaN | 497.5236 | 38.4919 | NaN | NaN | NaN | 675.8749 | 444.6956 | NaN | NaN | NaN | -18.865
8711.1292 | 597.592 | 337.2636 | 226.3861 | 227.3533 | 235.6263 | 297.4822 | 347.4308 | 304.9661 | NaN | NaN | NaN | 700.3072 | 297.0614 | NaN | NaN | 492.0378 | 8.8813 | NaN | NaN | NaN | 675.8125 | 452.1866 | NaN | NaN | NaN | NaN
8712.1292 | 598.2506 | 339.2511 | 225.96 | 227.538 | 236.2097 | 297.3564 | 347.8094 | 305.8333 | NaN | NaN | NaN | 672.1813 | 275.5497 | NaN | NaN | 505.7057 | 132.7821 | NaN | NaN | NaN | 709.9116 | 463.8258 | NaN | NaN | NaN | NaN
8713.1292 | 600.1122 | 339.9186 | 226.2807 | 228.1289 | 236.9445 | 298.1469 | 349.4164 | 305.5454 | NaN | NaN | NaN | 657.7822 | 265.367 | NaN | NaN | 502.185 | 100.6687 | NaN | NaN | NaN | 712.5087 | 476.4117 | NaN | NaN | NaN | -7.9171
8714.1292 | 601.0096 | 341.1506 | 226.9977 | 227.9718 | 237.7836 | 297.7716 | 349.87 | 305.0528 | NaN | NaN | NaN | 668.8265 | 255.9038 | NaN | NaN | 501.8445 | 90.0445 | NaN | NaN | NaN | 717.3167 | 480.1459 | NaN | NaN | NaN | NaN
8715.1292 | 601.1123 | 342.3067 | 226.8343 | 228.5019 | 238.1212 | 297.1721 | 348.9714 | 304.085 | NaN | NaN | NaN | 698.5753 | 248.8186 | NaN | NaN | 493.1644 | 38.1698 | NaN | NaN | NaN | 716.5368 | 493.9732 | NaN | -12.8656 | NaN | -17.1879
8716.1292 | 601.9517 | 342.8453 | 226.704 | 228.6868 | 238.1786 | 298.4223 | 350.2407 | 304.8487 | NaN | NaN | NaN | 706.6091 | 260.5519 | NaN | NaN | 482.2995 | -18.1828 | NaN | NaN | NaN | 698.5641 | 486.2457 | NaN | NaN | NaN | NaN
8717.1292 | 602.1292 | 345.4006 | 226.7164 | 228.3507 | 238.3812 | 300.1858 | 350.4823 | 306.536 | NaN | NaN | NaN | 710.6848 | 271.9892 | NaN | NaN | 488.3589 | 10.5575 | NaN | NaN | NaN | 720.0426 | 495.5171 | NaN | NaN | NaN | NaN
8718.1292 | 604.478 | 345.3091 | 226.6786 | 228.4336 | 238.8746 | 300.2857 | 350.8281 | 309.0796 | NaN | NaN | NaN | 702.5825 | 235.1203 | NaN | NaN | 501.3142 | 134.4065 | NaN | NaN | NaN | 756.2392 | 510.9122 | NaN | NaN | NaN | NaN
8719.1292 | 603.9124 | 344.4316 | 226.9118 | 228.0083 | 238.9942 | 299.7559 | 349.9931 | 308.9629 | NaN | NaN | NaN | 697.4747 | 236.1839 | NaN | NaN | 502.2647 | 151.2181 | NaN | NaN | NaN | 770.8053 | 524.8596 | NaN | -15.2598 | NaN | NaN
8720.1292 | 603.5805 | 342.9785 | 227.3722 | 228.0383 | 239.2497 | 299.5266 | 350.5441 | 309.643 | NaN | NaN | NaN | 700.2812 | 237.9567 | NaN | NaN | 503.6807 | 159.5456 | NaN | NaN | NaN | 778.8736 | 539.8977 | NaN | NaN | NaN | NaN
8721.1292 | 605.127 | 344.756 | 228.2576 | 227.6588 | 239.3246 | 298.4757 | 349.4084 | 308.021 | NaN | NaN | NaN | 700.5844 | 224.3795 | NaN | NaN | 499.048 | 155.6985 | NaN | NaN | NaN | 781.4008 | 552.6264 | NaN | NaN | NaN | NaN
8722.1292 | 605.9749 | 344.8605 | 227.7986 | 227.5949 | 239.9394 | 298.0364 | 349.0014 | 306.4985 | NaN | NaN | NaN | 683.482 | 230.4514 | NaN | NaN | 501.0938 | 173.6149 | NaN | NaN | NaN | 791.9368 | 551.9226 | NaN | NaN | NaN | -19.0169
8723.1292 | 607.8653 | 343.27 | 227.8837 | 228.086 | 240.0507 | 298.9026 | 350.315 | 306.0142 | NaN | NaN | NaN | 692.2055 | 214.2043 | NaN | NaN | 503.5196 | 232.4231 | NaN | NaN | NaN | 807.1574 | 560.2584 | NaN | -17.9208 | NaN | -13.8345
8724.1292 | 610.1213 | 343.9005 | 228.1841 | 228.1399 | 240.3176 | 297.8721 | 350.9316 | 305.7274 | NaN | NaN | NaN | 699.0698 | 218.3238 | NaN | NaN | 497.5076 | 170.4626 | NaN | NaN | NaN | 803.1312 | 565.3831 | NaN | NaN | NaN | NaN
8725.1292 | 609.8523 | 343.4436 | 227.555 | 228.1096 | 239.9878 | 297.9046 | 350.6862 | 305.7205 | NaN | NaN | NaN | 689.3633 | 213.3578 | NaN | NaN | 496.2402 | 161.4147 | NaN | NaN | NaN | 807.1131 | 569.6249 | NaN | NaN | NaN | NaN
8726.1292 | 611.0132 | 343.2875 | 227.3429 | 228.0961 | 240.1697 | 297.6833 | 351.6335 | 304.9261 | NaN | NaN | NaN | 697.5802 | 376.3487 | NaN | 82.0282 | 453.0001 | -18.6541 | NaN | NaN | NaN | 580.142 | 314.2639 | NaN | NaN | NaN | NaN
8727.1292 | 614.8512 | 342.3123 | 227.3113 | 229.3136 | 240.2551 | 298.3207 | 351.5601 | 306.4854 | NaN | NaN | NaN | 672.5613 | 405.7618 | NaN | 34.6241 | 560.0583 | NaN | NaN | NaN | NaN | 523.5873 | 257.0596 | NaN | NaN | NaN | NaN
8728.1292 | 616.0781 | 345.3667 | 227.0715 | 229.1636 | 240.1092 | 297.6509 | 351.0396 | 307.5762 | NaN | NaN | NaN | 662.124 | 366.972 | NaN | 449.3684 | 498.8194 | 12.4277 | NaN | NaN | NaN | 405.6811 | 132.8604 | NaN | NaN | NaN | NaN
8729.1292 | 615.6567 | 343.3267 | 226.7767 | 229.0348 | 239.8358 | 297.4792 | 350.4788 | 307.112 | NaN | NaN | NaN | 655.1512 | 426.6196 | NaN | 314.0733 | 662.7378 | NaN | NaN | NaN | NaN | 409.4927 | 131.0206 | NaN | NaN | NaN | NaN
8730.1292 | 615.7715 | 342.108 | 226.8809 | 228.8028 | 240.1899 | 296.9125 | 349.533 | 306.6708 | NaN | NaN | NaN | 671.5713 | 421.5597 | NaN | 290.3921 | 716.3767 | NaN | NaN | NaN | NaN | 420.0875 | 142.458 | NaN | NaN | NaN | NaN
8731.1292 | 614.3417 | 341.7244 | 226.4506 | 228.8137 | 240.2345 | 298.5184 | 349.173 | 306.1864 | NaN | NaN | NaN | 683.2438 | 408.5561 | NaN | 267.3131 | 793.9638 | NaN | NaN | NaN | NaN | 435.6112 | 152.7692 | NaN | NaN | NaN | NaN
8732.1292 | 614.113 | 342.5273 | 226.0329 | 228.7229 | 240.3318 | 298.2281 | 348.2284 | 305.8377 | NaN | NaN | NaN | 672.051 | 428.544 | NaN | 273.4782 | 590.7794 | NaN | NaN | NaN | NaN | 433.1468 | 150.5288 | NaN | NaN | NaN | NaN
8733.1292 | 612.8311 | 344.1648 | 225.7376 | 229.2667 | 240.3073 | 298.3563 | 347.7672 | 305.0013 | NaN | NaN | NaN | 681.7103 | 444.4131 | NaN | 246.8599 | 756.6129 | NaN | NaN | NaN | NaN | 450.8999 | 166.5538 | NaN | NaN | NaN | NaN
8734.1292 | 608.5875 | 343.9375 | 225.7758 | 229.108 | 240.9067 | 297.6373 | 347.185 | 304.2208 | NaN | NaN | NaN | 689.635 | 395.7948 | NaN | 245.3481 | 679.5682 | NaN | NaN | NaN | NaN | 447.8234 | 167.5985 | NaN | NaN | NaN | NaN
8735.1292 | 605.7282 | 346.9796 | 225.9896 | 229.2163 | 241.0784 | 298.2781 | 347.533 | 305.7217 | NaN | NaN | NaN | 706.0636 | 410.5032 | NaN | 242.9785 | 620.8031 | NaN | NaN | NaN | NaN | 451.02 | 166.9772 | NaN | NaN | NaN | NaN
8736.1292 | 602.198 | 347.3563 | 225.5599 | 229.1008 | 240.9773 | 299.0219 | 347.7293 | 306.1186 | NaN | NaN | NaN | 692.7949 | 456.3753 | NaN | 237.9084 | 515.2341 | NaN | NaN | NaN | NaN | 449.479 | 167.7702 | NaN | NaN | NaN | NaN
8737.1292 | 600.1569 | 349.2892 | 224.8928 | 228.4491 | 240.7425 | 298.5676 | 346.8613 | 306.5278 | NaN | NaN | NaN | 694.2136 | 444.1905 | NaN | 216.552 | 479.1174 | NaN | NaN | NaN | NaN | 456.3269 | 176.0765 | NaN | NaN | NaN | NaN
8738.1292 | 599.8789 | 350.1446 | 226.2906 | 228.3504 | 240.5509 | 298.9485 | 347.2711 | 307.287 | NaN | NaN | NaN | 719.0829 | 422.1688 | NaN | 222.3591 | 483.7451 | -9.1268 | NaN | NaN | NaN | 467.7855 | 183.487 | NaN | NaN | NaN | NaN
8739.1292 | 598.8058 | 351.2377 | 226.6158 | 228.54 | 240.6561 | 301.0441 | 347.0463 | 306.2296 | NaN | NaN | NaN | 705.2418 | 411.0077 | NaN | 227.8708 | 598.9192 | NaN | NaN | NaN | NaN | 465.5204 | 178.7606 | NaN | NaN | NaN | NaN
8740.1292 | 599.2174 | 351.389 | 226.4122 | 228.4343 | 240.4246 | 299.9451 | 346.9796 | 305.806 | NaN | NaN | NaN | 698.857 | 402.701 | NaN | 222.3536 | 631.4856 | NaN | NaN | NaN | NaN | 471.0257 | 179.0986 | NaN | NaN | NaN | NaN
8741.1292 | 597.1323 | 348.4574 | 226.957 | 228.6406 | 240.297 | 300.4845 | 346.4239 | 307.1312 | NaN | NaN | NaN | 679.0262 | 410.2281 | NaN | 219.7674 | 672.1274 | NaN | NaN | NaN | NaN | 476.605 | 181.5492 | NaN | NaN | NaN | NaN
8742.1292 | 595.3298 | 346.3943 | 227.0981 | 228.8309 | 239.845 | 300.312 | 347.1314 | 306.097 | NaN | NaN | NaN | 647.7435 | 441.5325 | NaN | 206.2705 | 559.1566 | NaN | NaN | NaN | NaN | 476.46 | 179.5511 | NaN | NaN | NaN | NaN
8743.1292 | 595.4249 | 344.5825 | 227.2901 | 228.8021 | 240.1206 | 299.7819 | 347.4163 | 307.0677 | NaN | NaN | NaN | 621.1444 | 414.6175 | NaN | 204.1977 | 561.7722 | NaN | NaN | NaN | NaN | 470.9969 | 183.6411 | NaN | NaN | NaN | NaN
8744.1292 | 595.5573 | 343.8186 | 227.7356 | 228.7442 | 239.8856 | 297.7421 | 347.2098 | 305.1839 | NaN | NaN | NaN | 598.4468 | 433.2371 | NaN | 207.6708 | 749.1361 | NaN | NaN | NaN | NaN | 468.9676 | 179.5491 | NaN | NaN | NaN | NaN
8745.1292 | 596.4916 | 346.8518 | 227.0542 | 228.7887 | 239.4231 | 297.1991 | 346.8083 | 304.3051 | NaN | NaN | NaN | 621.3268 | 404.2338 | NaN | 169.6808 | 756.51 | NaN | NaN | NaN | NaN | 504.0703 | 192.4665 | NaN | NaN | NaN | NaN
8746.1292 | 596.685 | 347.2621 | 226.5388 | 228.7929 | 239.4803 | 295.8651 | 346.3291 | 302.841 | NaN | NaN | NaN | 614.3876 | 438.9718 | NaN | 246.138 | 720.1281 | -18.0696 | NaN | NaN | NaN | 471.8735 | 169.9671 | NaN | NaN | NaN | NaN
8747.1292 | 596.1751 | 344.9333 | 227.0402 | 228.4742 | 239.2029 | 295.4476 | 346.0815 | 301.9858 | NaN | NaN | NaN | 608.3281 | 628.8568 | NaN | 182.8727 | 497.1734 | NaN | NaN | NaN | NaN | 510.5196 | 164.5565 | NaN | NaN | NaN | NaN
8748.1292 | 595.1878 | 343.6154 | 226.4168 | 227.981 | 238.758 | 295.9716 | 345.3532 | 302.3778 | NaN | NaN | NaN | 642.0044 | 606.8804 | NaN | 156.4164 | 489.7026 | NaN | NaN | NaN | NaN | 529.4235 | 174.3884 | NaN | NaN | NaN | NaN
8749.1292 | 593.6447 | 343.2756 | 225.8424 | 228.0993 | 238.3368 | 295.6944 | 346.0643 | 301.5027 | NaN | NaN | NaN | 649.1392 | 383.4208 | NaN | 151.7915 | 486.9983 | NaN | NaN | NaN | NaN | 517.9915 | 181.85 | NaN | NaN | NaN | NaN
8750.1292 | 593.4356 | 344.669 | 225.8145 | 228.2426 | 237.7387 | 294.7009 | 346.1601 | 300.8022 | NaN | NaN | NaN | 658.4913 | 407.0667 | NaN | 139.9021 | 484.7138 | NaN | NaN | NaN | NaN | 525.6458 | 196.1136 | NaN | NaN | NaN | NaN
8751.1292 | 594.542 | 341.7134 | 225.5358 | 228.0862 | 237.3422 | 294.699 | 346.6174 | 299.5034 | NaN | NaN | NaN | 683.1933 | 374.6284 | NaN | 137.7552 | 485.4344 | NaN | NaN | NaN | NaN | 537.7409 | 213.9644 | NaN | NaN | NaN | NaN
8752.1292 | 595.9864 | 343.2532 | 225.2558 | 227.6152 | 236.8331 | 293.5861 | 347.055 | 299.6974 | NaN | NaN | NaN | 664.9332 | 432.8499 | NaN | 130.1516 | 475.9042 | NaN | NaN | NaN | NaN | 534.1684 | 221.0224 | NaN | NaN | NaN | NaN
8753.1292 | 597.344 | 341.4732 | 225.1988 | 227.6186 | 236.799 | 293.6314 | 348.2084 | 299.9701 | NaN | NaN | NaN | 665.4854 | 433.5374 | NaN | 120.812 | 475.4314 | NaN | NaN | NaN | NaN | 538.7824 | 230.4318 | NaN | NaN | NaN | NaN
8754.1292 | 598.8432 | 341.1473 | 224.8991 | 227.4075 | 236.9155 | 292.4728 | 348.6663 | 300.3056 | NaN | NaN | NaN | 670.5586 | 412.2004 | NaN | 110.9468 | 474.4867 | NaN | NaN | NaN | NaN | 545.0523 | 234.2737 | NaN | NaN | NaN | NaN
8755.1292 | 599.1582 | 340.6791 | 224.7692 | 227.4623 | 236.5012 | 292.6861 | 348.7432 | 299.2456 | NaN | NaN | NaN | 693.0537 | 443.101 | NaN | 146.8512 | 513.7275 | NaN | NaN | NaN | NaN | 537.1633 | 218.4953 | NaN | NaN | NaN | NaN
8756.1292 | 599.8359 | 341.5142 | 224.2157 | 227.4056 | 236.5055 | 294.6197 | 348.5784 | 297.8195 | NaN | NaN | NaN | 688.6674 | 366.3433 | NaN | 137.1719 | 487.9547 | 39.9985 | NaN | NaN | NaN | 551.6218 | 211.8249 | NaN | NaN | NaN | NaN
8757.1292 | 601.5102 | 341.6676 | 224.2854 | 227.421 | 236.5676 | 293.126 | 347.9696 | 296.8152 | NaN | NaN | NaN | 666.836 | 450.7158 | NaN | 178.3154 | 491.9312 | NaN | NaN | NaN | NaN | 533.675 | 206.2628 | NaN | NaN | NaN | NaN
8758.1292 | 603.4455 | 342.7451 | 223.7634 | 227.373 | 236.4708 | 292.2413 | 347.2343 | 296.2538 | NaN | NaN | NaN | 685.454 | 464.3763 | NaN | 292.2333 | 537.3131 | NaN | NaN | NaN | NaN | 538.0081 | 84.5507 | NaN | NaN | NaN | NaN
8759.1292 | 605.1792 | 342.417 | 224.2915 | 227.4759 | 236.6929 | 292.5631 | 346.7506 | 295.2552 | NaN | NaN | NaN | 672.1878 | 439.0179 | NaN | 180.0132 | 519.9715 | 38.2343 | NaN | NaN | NaN | 550.0394 | 102.1266 | NaN | NaN | NaN | NaN
8760.1292 | 604.4226 | 341.8671 | 224.3583 | 227.2281 | 236.4859 | 292.8842 | 346.0826 | 296.3778 | NaN | NaN | NaN | 675.7609 | 421.1069 | NaN | 171.0547 | 516.927 | 37.9393 | NaN | NaN | NaN | 551.0357 | 121.1672 | NaN | NaN | NaN | NaN
8761.1292 | 607.0091 | 341.5731 | 224.2822 | 227.1291 | 236.5191 | 292.0518 | 346.5219 | 296.516 | NaN | NaN | NaN | 676.8396 | 412.7571 | NaN | 174.4533 | 511.6193 | -13.997 | NaN | NaN | NaN | 551.0097 | 141.2711 | NaN | NaN | NaN | NaN
8762.1292 | 609.0016 | 341.8423 | 224.6147 | 227.19 | 236.4836 | 291.3678 | 346.1594 | 297.1844 | NaN | NaN | NaN | 707.7846 | 428.4203 | NaN | 178.0162 | 506.8345 | NaN | NaN | NaN | NaN | 551.1261 | 155.6146 | NaN | NaN | NaN | NaN
8763.1292 | 611.3509 | 341.2576 | 224.9022 | 227.052 | 236.4744 | 291.0877 | 345.5581 | 296.5966 | NaN | NaN | NaN | 713.4394 | 398.9614 | NaN | 162.7266 | 502.7719 | NaN | NaN | NaN | NaN | 552.4054 | 168.8534 | NaN | NaN | NaN | NaN
8764.1292 | 614.365 | 339.7475 | 225.5986 | 227.1039 | 236.9788 | 290.3891 | 345.5242 | 297.6835 | NaN | NaN | NaN | 713.9829 | 398.5871 | NaN | 147.5508 | 502.9797 | NaN | NaN | NaN | NaN | 559.2175 | 180.7339 | NaN | NaN | NaN | NaN
8765.1292 | 615.5039 | 341.8448 | 225.3408 | 227.5279 | 237.2747 | 290.3168 | 345.4635 | 299.6135 | NaN | NaN | NaN | 706.6978 | 412.9972 | NaN | 112.4676 | 499.8617 | NaN | NaN | NaN | NaN | 566.1258 | 196.7177 | NaN | NaN | NaN | NaN
8766.1292 | 615.3652 | 339.372 | 225.3675 | 228.096 | 237.2317 | 290.1438 | 344.9589 | 301.4318 | NaN | NaN | NaN | 709.4672 | 381.3424 | NaN | 80.1384 | 501.8169 | NaN | NaN | NaN | NaN | 580.3296 | 209.9682 | NaN | NaN | NaN | NaN
8767.1292 | 618.0933 | 340.8508 | 224.9538 | 227.7913 | 237.2309 | 290.4532 | 344.6181 | 304.175 | NaN | NaN | NaN | 701.4969 | 404.268 | NaN | 88.9351 | 495.2322 | NaN | NaN | NaN | NaN | 577.881 | 220.1867 | NaN | NaN | NaN | NaN
8768.1292 | 619.1773 | 342.3682 | 224.7959 | 227.7383 | 237.5042 | 289.9401 | 344.65 | 303.574 | NaN | NaN | NaN | 674.1089 | 398.5402 | NaN | 93.3587 | 486.1213 | NaN | NaN | NaN | NaN | 571.1372 | 225.8304 | NaN | NaN | NaN | NaN
8769.1292 | 618.2098 | 343.2951 | 225.0847 | 227.3124 | 237.4253 | 290.3974 | 344.541 | 304.0584 | NaN | NaN | NaN | 676.8423 | 410.6316 | NaN | 92.8694 | 490.8756 | NaN | NaN | NaN | NaN | 584.5283 | 233.9694 | NaN | NaN | NaN | NaN
8770.1292 | 619.1939 | 342.1562 | 225.1653 | 227.2576 | 237.7711 | 290.4742 | 344.2709 | 303.3127 | NaN | NaN | NaN | 646.244 | 413.0125 | NaN | 94.6433 | 479.607 | NaN | NaN | NaN | NaN | 578.3545 | 244.3467 | NaN | NaN | NaN | NaN
8771.1292 | 619.3791 | 340.4424 | 225.3669 | 227.6475 | 237.9692 | 290.6743 | 342.8296 | 304.5864 | NaN | NaN | NaN | 625.4501 | 404.042 | NaN | 101.4007 | 472.7875 | NaN | NaN | NaN | NaN | 573.4425 | 239.9334 | NaN | NaN | NaN | NaN
8772.1292 | 618.0411 | 344.1644 | 225.0684 | 227.6573 | 237.5786 | 291.037 | 343.1291 | 305.7984 | NaN | NaN | NaN | 632.7755 | 429.6807 | NaN | 121.5031 | 468.686 | NaN | NaN | NaN | NaN | 570.9378 | 232.6845 | NaN | NaN | NaN | NaN
8773.1292 | 618.3113 | 344.8947 | 225.6248 | 227.7409 | 237.7143 | 294.8645 | 344.1659 | 309.9977 | NaN | NaN | NaN | 628.742 | 419.2197 | NaN | 126.2746 | 469.4802 | NaN | NaN | NaN | NaN | 578.8874 | 229.206 | NaN | NaN | NaN | NaN
8774.1292 | 617.6149 | 343.1346 | 226.5506 | 227.9934 | 238.3377 | 293.9943 | 343.8433 | 309.8642 | NaN | NaN | NaN | 621.6531 | 388.4244 | NaN | 89.0003 | 467.5616 | NaN | NaN | NaN | NaN | 585.0643 | 246.0161 | NaN | NaN | NaN | NaN
8775.1292 | 617.7175 | 342.4116 | 226.627 | 228.59 | 239.1716 | 294.1796 | 344.3697 | 310.8177 | NaN | NaN | NaN | 626.0661 | 538.9721 | NaN | -14.7948 | 495.1773 | NaN | NaN | NaN | NaN | 646.2553 | 264.649 | NaN | NaN | NaN | NaN
8776.1292 | 617.03 | 343.7067 | 226.3627 | 228.9017 | 239.1699 | 293.3668 | 344.4642 | 312.2425 | NaN | NaN | NaN | 625.0932 | 513.3481 | NaN | NaN | 491.2356 | NaN | NaN | NaN | NaN | 674.4579 | 279.6626 | NaN | NaN | NaN | NaN
8777.1292 | 615.9968 | 341.1139 | 226.9352 | 229.1012 | 239.1778 | 291.9417 | 343.2123 | 312.5385 | NaN | NaN | NaN | 630.8287 | 359.1341 | NaN | NaN | 486.9907 | NaN | NaN | NaN | NaN | 657.5319 | 289.7291 | NaN | NaN | NaN | NaN
8778.1292 | 616.073 | 340.258 | 226.574 | 229.1083 | 239.5596 | 291.1079 | 342.997 | 313.569 | NaN | NaN | NaN | 639.3859 | 360.5001 | NaN | NaN | 506.7427 | NaN | NaN | NaN | NaN | 670.2252 | 306.2022 | NaN | NaN | NaN | NaN
8779.1292 | 617.445 | 342.6535 | 226.7395 | 229.2962 | 240.0339 | 292.6521 | 342.5958 | 313.822 | NaN | NaN | NaN | 628.9329 | 415.723 | NaN | 551.7458 | 577.7427 | NaN | NaN | NaN | NaN | 699.9411 | 318.2321 | NaN | NaN | NaN | NaN
8780.1292 | 618.2911 | 341.7804 | 226.83 | 229.7046 | 240.2738 | 292.5914 | 343.5765 | 315.5372 | NaN | NaN | NaN | 654.2456 | 386.218 | NaN | NaN | 600.1128 | 857.0372 | NaN | NaN | NaN | 785.7312 | 325.0535 | NaN | NaN | NaN | -19.6853
8781.1292 | 615.516 | 343.4157 | 227.5024 | 230.2793 | 240.5644 | 291.529 | 343.7542 | 315.8638 | NaN | NaN | NaN | 681.05 | 373.8546 | NaN | NaN | 600.4982 | NaN | NaN | NaN | NaN | 866.9371 | 331.4728 | NaN | NaN | NaN | NaN
8782.1292 | 614.3563 | 344.6887 | 227.9457 | 230.3378 | 240.887 | 291.5684 | 344.2772 | 313.9992 | NaN | NaN | NaN | 707.8896 | 359.8693 | NaN | NaN | 598.5973 | 1352.8242 | NaN | NaN | NaN | 874.3924 | 340.8915 | NaN | NaN | NaN | NaN
8783.1292 | 614.722 | 346.6883 | 228.6878 | 229.9789 | 241.6685 | 291.0187 | 343.6887 | 313.7192 | NaN | NaN | NaN | 734.0472 | 339.1144 | NaN | NaN | 590.503 | 1033.7763 | NaN | NaN | NaN | 870.1666 | 354.2117 | NaN | NaN | NaN | NaN
8784.1292 | 615.6891 | 343.8117 | 229.2796 | 230.7023 | 241.7327 | 290.0528 | 344.2205 | 315.7489 | NaN | NaN | NaN | 748.1536 | 320.4086 | NaN | NaN | 586.9246 | 741.1633 | NaN | NaN | NaN | 865.9093 | 367.6738 | NaN | NaN | NaN | NaN
8785.1292 | 613.6642 | 344.9034 | 229.9335 | 231.6403 | 242.558 | 289.6414 | 345.1435 | 314.7231 | NaN | NaN | NaN | 725.0764 | 298.0577 | NaN | NaN | 576.7435 | 538.9881 | NaN | NaN | NaN | 858.5665 | 376.287 | NaN | NaN | NaN | NaN
8786.1292 | 612.1453 | 347.2523 | 230.3323 | 232.2293 | 243.1491 | 289.7689 | 345.6426 | 312.6888 | NaN | NaN | NaN | 718.6478 | 285.9967 | NaN | NaN | 576.7071 | 429.3279 | NaN | NaN | NaN | 861.0855 | 381.6828 | NaN | NaN | NaN | -18.5907
8787.1292 | 611.2087 | 347.8915 | 230.4809 | 232.3868 | 243.9909 | 290.2154 | 345.6778 | 311.9403 | NaN | NaN | NaN | 731.0293 | 281.9428 | NaN | NaN | 576.3688 | 365.979 | NaN | NaN | NaN | 863.8082 | 393.4102 | NaN | NaN | NaN | NaN
8788.1292 | 610.8512 | 347.93 | 230.8837 | 232.2781 | 244.7285 | 290.5215 | 345.8853 | 310.5061 | NaN | NaN | NaN | 742.3572 | 268.9978 | NaN | NaN | 569.4414 | 244.2283 | NaN | NaN | NaN | 859.1763 | 411.4255 | NaN | NaN | NaN | NaN
8789.1292 | 610.2161 | 350.591 | 231.1173 | 231.9664 | 244.8557 | 290.207 | 346.0355 | 309.4202 | NaN | NaN | NaN | 753.7321 | 291.4287 | NaN | NaN | 551.754 | 27.1965 | NaN | NaN | NaN | 830.081 | 423.9913 | NaN | NaN | NaN | -18.5459
8790.1292 | 609.2545 | 352.4716 | 230.6933 | 231.6042 | 244.7168 | 291.1 | 345.903 | 307.8224 | NaN | NaN | NaN | 750.3304 | 302.6963 | NaN | NaN | 540.438 | NaN | NaN | NaN | NaN | 812.9367 | 436.8866 | NaN | NaN | NaN | NaN
8791.1292 | 607.099 | 353.6884 | 230.5853 | 231.5141 | 244.6538 | 291.0243 | 346.182 | 307.2539 | NaN | NaN | NaN | 746.0085 | 338.7076 | NaN | NaN | 531.6665 | NaN | NaN | NaN | NaN | 802.0368 | 433.5155 | NaN | -19.5336 | NaN | NaN
8792.1292 | 606.4478 | 354.3183 | 229.6593 | 231.1505 | 244.1708 | 292.9982 | 346.7371 | 306.9549 | NaN | NaN | NaN | 751.3516 | 308.4454 | NaN | NaN | 513.1964 | NaN | NaN | NaN | NaN | 768.1662 | 403.149 | NaN | NaN | NaN | NaN
8793.1292 | 607.3141 | 355.3808 | 229.7319 | 231.0402 | 243.9171 | 294.4608 | 347.1882 | 309.2028 | NaN | NaN | NaN | 744.9699 | 322.9108 | NaN | NaN | 499.8476 | NaN | NaN | NaN | NaN | 748.1471 | 381.3907 | NaN | NaN | NaN | NaN
8794.1292 | 606.9816 | 355.7814 | 229.0029 | 230.9455 | 243.3126 | 296.4735 | 347.8387 | 310.7007 | NaN | NaN | NaN | 748.9914 | 368.1402 | NaN | 473.7905 | 494.3689 | NaN | NaN | NaN | NaN | 739.0807 | 359.3705 | NaN | NaN | NaN | NaN
8795.1292 | 606.4073 | 356.6887 | 229.17 | 230.8946 | 243.2297 | 296.2656 | 346.7931 | 311.6714 | NaN | NaN | NaN | 754.6054 | 441.2302 | NaN | 28.109 | 484.7464 | 8.0931 | NaN | NaN | NaN | 737.5937 | 353.0853 | NaN | NaN | NaN | NaN
8796.1292 | 607.7857 | 356.3211 | 229.1161 | 230.7932 | 243.1629 | 295.6339 | 348.2478 | 311.0159 | NaN | NaN | NaN | 754.0401 | 400.7975 | NaN | -11.3254 | 487.2569 | NaN | NaN | NaN | NaN | 728.3491 | 344.5423 | NaN | NaN | NaN | NaN
8797.1292 | 607.7458 | 358.2349 | 229.2102 | 231.2702 | 243.4113 | 295.5655 | 349.1157 | 311.1599 | NaN | NaN | NaN | 745.1502 | 382.2972 | NaN | NaN | 478.4783 | NaN | NaN | NaN | NaN | 714.3756 | 327.3264 | NaN | NaN | NaN | NaN
8798.1292 | 608.2716 | 357.6603 | 229.512 | 231.5268 | 243.4177 | 296.4318 | 349.6692 | 312.4025 | NaN | NaN | NaN | 719.4539 | 340.6815 | NaN | 6.1263 | 466.9912 | -14.818 | NaN | NaN | NaN | 679.394 | 295.5968 | NaN | NaN | NaN | NaN
8799.1292 | 606.2508 | 359.1608 | 229.5336 | 232.0547 | 243.5617 | 295.6013 | 349.898 | 312.4878 | NaN | NaN | NaN | 694.1709 | 465.7919 | NaN | 7.8037 | 463.8786 | NaN | NaN | NaN | NaN | 693.3158 | 292.248 | NaN | NaN | NaN | NaN
8800.1292 | 607.5331 | 361.9523 | 229.7282 | 232.4112 | 243.2797 | 295.4047 | 349.5884 | 311.3838 | NaN | NaN | NaN | 662.4055 | 374.5696 | NaN | 1.7879 | 460.9548 | NaN | NaN | NaN | NaN | 685.449 | 298.6473 | NaN | NaN | NaN | NaN
8801.1292 | 609.4982 | 364.0635 | 230.0884 | 233.2188 | 243.6063 | 296.0133 | 350.5441 | 311.0837 | NaN | NaN | NaN | 643.4202 | 401.4924 | NaN | NaN | 461.8141 | NaN | NaN | NaN | NaN | 693.5146 | 303.6285 | NaN | NaN | NaN | NaN
8802.1292 | 611.7755 | 363.8093 | 230.3457 | 233.5612 | 243.9594 | 296.6648 | 351.8887 | 310.2458 | NaN | NaN | NaN | 636.0367 | 396.5875 | NaN | 28.4902 | 461.4492 | -9.7906 | NaN | NaN | NaN | 679.7281 | 288.7088 | NaN | NaN | NaN | NaN
8803.1292 | 610.2442 | 363.1133 | 230.6191 | 234.2541 | 244.496 | 295.8228 | 352.4412 | 310.2795 | NaN | NaN | NaN | 651.7383 | 398.9653 | NaN | NaN | 475.5022 | NaN | NaN | NaN | NaN | 715.7949 | 294.7425 | NaN | NaN | NaN | NaN
8804.1292 | 610.0677 | 364.6475 | 231.0949 | 235.2627 | 244.8501 | 295.4022 | 351.4066 | 309.4725 | NaN | NaN | NaN | 656.071 | 354.1611 | NaN | NaN | 486.4282 | NaN | NaN | NaN | NaN | 719.1456 | 292.6389 | NaN | NaN | NaN | NaN
8805.1292 | 611.2138 | 367.6598 | 231.0706 | 235.3276 | 244.9129 | 294.9335 | 350.8422 | 308.3236 | NaN | NaN | NaN | 642.4465 | 372.1004 | NaN | 82.7995 | 460.6106 | 4.7434 | NaN | NaN | NaN | 677.9616 | 275.4049 | NaN | NaN | NaN | NaN
8806.1292 | 612.2769 | 367.2203 | 231.3943 | 235.3918 | 244.8609 | 295.7538 | 351.2833 | 309.027 | NaN | NaN | NaN | 633.2882 | 535.8113 | NaN | 95.7628 | 453.7829 | NaN | NaN | NaN | NaN | 684.3051 | 261.8966 | NaN | NaN | NaN | NaN
8807.1292 | 613.0286 | 368.9512 | 232.7225 | 236.971 | 244.7572 | 294.9862 | 351.9464 | 309.3112 | NaN | NaN | NaN | 646.6283 | 361.2556 | NaN | 84.7873 | 458.5203 | NaN | NaN | NaN | NaN | 676.352 | 261.243 | NaN | NaN | NaN | NaN
8808.1292 | 613.5808 | 370.621 | 232.039 | 237.3771 | 245.2149 | 294.2202 | 352.0244 | 309.0921 | NaN | NaN | NaN | 666.9194 | 388.216 | NaN | 112.9362 | 459.6604 | NaN | NaN | NaN | NaN | 677.0722 | 260.511 | NaN | NaN | NaN | NaN
8809.1292 | 614.1142 | 368.7572 | 232.2216 | 237.6571 | 245.7258 | 294.0731 | 352.8274 | 310.5412 | NaN | NaN | NaN | 684.028 | 417.4378 | NaN | 103.8584 | 456.9927 | NaN | NaN | NaN | NaN | 684.754 | 265.3435 | NaN | NaN | NaN | NaN
8810.1292 | 613.2094 | 370.2406 | 231.6808 | 237.895 | 245.8401 | 292.8169 | 352.5853 | 309.8607 | NaN | NaN | NaN | 677.4544 | 410.1208 | NaN | 65.6014 | 460.8187 | NaN | NaN | NaN | NaN | 700.6515 | 269.6539 | NaN | NaN | NaN | NaN
8811.1292 | 611.7026 | 369.4526 | 231.5122 | 238.0761 | 245.9497 | 293.0652 | 351.8822 | 311.1939 | NaN | NaN | NaN | 686.9868 | 334.7559 | NaN | 630.7291 | 488.1296 | 28.306 | NaN | NaN | NaN | 658.4176 | 12.5848 | NaN | 1.7113 | NaN | NaN
8812.1292 | 615.1512 | 368.8644 | 231.3432 | 238.2234 | 245.4718 | 293.5108 | 351.2743 | 312.0061 | NaN | NaN | NaN | 664.4946 | 680.1335 | NaN | 572.1383 | 870.5628 | NaN | NaN | NaN | NaN | 739.8435 | -13.7492 | NaN | NaN | NaN | NaN
8813.1292 | 610.4773 | 369.4135 | 231.8405 | 238.2422 | 245.6655 | 293.0863 | 351.2322 | 310.9712 | NaN | NaN | NaN | 669.647 | 660.0957 | NaN | 380.4458 | 910.2788 | -3.8359 | NaN | NaN | NaN | 834.7919 | -2.1694 | NaN | NaN | NaN | NaN
8814.1292 | 608.6038 | 371.5056 | 231.5847 | 238.0091 | 245.6265 | 294.4962 | 351.3296 | 310.4729 | NaN | NaN | NaN | 667.5241 | 607.9446 | NaN | 186.9235 | 861.1603 | 1109.4146 | NaN | NaN | NaN | 813.9666 | 9.9769 | NaN | NaN | NaN | NaN
8815.1292 | 605.9057 | 371.7662 | 232.0803 | 238.421 | 245.5526 | 296.9308 | 352.8016 | 309.935 | NaN | NaN | NaN | 685.0203 | 584.3626 | NaN | -0.6292 | 848.9886 | NaN | NaN | NaN | NaN | 812.3256 | 25.2922 | NaN | NaN | NaN | NaN
8816.1292 | 185.0158 | 372.7174 | 232.1221 | 238.6307 | 245.3887 | 296.9326 | 353.3227 | 309.7051 | NaN | NaN | NaN | 598.499 | 1091.3425 | NaN | 1210.6624 | 1253.6181 | 26.2849 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 124.6473
8817.1292 | 90.6962 | 374.718 | 232.1468 | 239.0399 | 245.0795 | 297.9957 | 354.0463 | 310.283 | NaN | NaN | 52.7511 | 340.0706 | 1254.8892 | NaN | 35.6526 | 1253.6186 | 25.1686 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN
8818.1292 | 88.7068 | 375.9244 | 232.3365 | 239.2938 | 244.9363 | 298.1946 | 355.6905 | 309.9766 | NaN | NaN | 82.3482 | 343.7422 | 1254.8908 | NaN | 32.386 | 1253.6202 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN
8819.1292 | 83.2982 | 376.8923 | 232.4765 | 239.6719 | 244.9671 | 296.7397 | 354.8152 | 309.1437 | NaN | NaN | 74.8747 | 316.2818 | 1254.8913 | NaN | 33.6014 | 1253.6207 | NaN | NaN | 255.4837 | NaN | NaN | NaN | NaN | NaN | NaN | NaN
8820.1292 | 73.4001 | 378.1082 | 232.5624 | 239.6072 | 244.9766 | 296.7891 | 355.5957 | 309.8019 | NaN | NaN | 50.1513 | 305.5968 | 1254.8904 | NaN | 26.1249 | 1253.6197 | 14.4125 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN
8821.1292 | 89.6643 | 378.5874 | 232.7551 | 239.704 | 245.2352 | 296.9899 | 355.8325 | 309.9021 | NaN | NaN | 83.8684 | 343.8263 | 1254.8909 | 30.3508 | 33.9508 | 1253.6202 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN
8822.1292 | 103.3645 | 378.6588 | 233.1441 | 239.7667 | 245.0488 | 298.0205 | 355.8978 | 310.385 | NaN | NaN | 287.9194 | 385.5919 | 1254.8926 | 194.5371 | 34.8207 | 1253.6219 | 1293.304 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN
8823.1292 | 32.3904 | 379.6283 | 233.5017 | 240.781 | 245.413 | 296.9012 | 356.6577 | 310.011 | NaN | NaN | NaN | 375.6067 | 1254.8902 | 86.8057 | 46.4931 | 1253.6196 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN
8824.1292 | 82.2224 | 379.4895 | 233.5245 | 239.8795 | 245.9018 | 297.3877 | 356.4461 | 310.1111 | 698.0405 | 750.3381 | 61.774 | 313.6066 | 1254.892 | 371.9479 | 29.9136 | 1253.6213 | NaN | 1253.7964 | 208.324 | NaN | NaN | NaN | NaN | NaN | NaN | NaN
8825.1292 | 111.4765 | 380.2877 | 233.3118 | 239.677 | 245.681 | 296.9543 | 357.4654 | 310.5412 | NaN | 272.3738 | -8.9015 | 440.5023 | 1254.8929 | NaN | 27.6101 | 1253.6222 | 387.9129 | 706.5615 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN
8826.1292 | 104.3758 | 379.9596 | 232.9879 | 239.3861 | 245.4229 | 296.2873 | 357.0106 | 311.5996 | NaN | 1103.309 | NaN | 425.2493 | 1254.8926 | NaN | 28.2858 | 1253.622 | NaN | 33.7205 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN
8827.1292 | 109.977 | 377.0997 | 233.4799 | 239.5236 | 245.4896 | 296.7253 | 357.102 | 312.6967 | NaN | NaN | NaN | 413.6189 | 1254.8931 | NaN | 30.7037 | 1253.6224 | NaN | 156.6544 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN
8828.1292 | 163.429 | 376.2673 | 233.5206 | 239.44 | 245.3051 | 295.8681 | 356.6174 | 313.01 | NaN | NaN | NaN | 566.935 | 1254.8931 | NaN | 29.2198 | 1253.6224 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN
8829.1292 | NaN | 376.5152 | 237.9876 | 240.6225 | 244.3303 | 290.8234 | 356.8283 | 310.5547 | 1253.8419 | 485.9249 | 44.9878 | 290.9671 | 1254.8937 | 25.8182 | NaN | 1253.6231 | 210.5072 | 1201.9198 | NaN | 338.5851 | NaN | NaN | NaN | NaN | NaN | NaN
8830.1292 | NaN | 376.9535 | 241.7967 | 241.66 | 244.4477 | 289.0615 | 358.1424 | 309.5199 | 1253.842 | 972.6915 | 44.98 | 269.1068 | 1254.8938 | 4.363 | NaN | 1253.6231 | 33.9686 | 880.3204 | 498.1266 | NaN | NaN | NaN | NaN | NaN | NaN | NaN
8831.1292 | NaN | 377.9046 | 241.6875 | 241.3491 | 244.3798 | 290.8304 | 358.9641 | 309.948 | 1193.0533 | 1058.4965 | 57.562 | 294.3891 | 1254.8941 | 15.5146 | 10.4986 | 1253.6234 | 155.8038 | 842.8057 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN
8832.1292 | NaN | 378.8321 | 240.2171 | 240.8928 | 244.4183 | 290.9561 | 357.9311 | 310.1018 | 1253.8412 | 1057.6485 | 56.237 | 296.1582 | 1254.8929 | -16.2809 | 13.5221 | 1253.6223 | -0.8828 | 1253.7974 | NaN | 96.3049 | NaN | NaN | NaN | NaN | NaN | NaN
8833.1292 | NaN | 379.7764 | 241.6775 | 241.2811 | 244.5346 | 290.3995 | 358.9792 | 310.0253 | 1253.8426 | 1103.0287 | 38.8887 | 285.5566 | 1254.8944 | NaN | -12.0074 | 1253.6237 | 54.5477 | 1253.7988 | -16.3485 | NaN | NaN | NaN | NaN | NaN | NaN | NaN
8834.1292 | NaN | 380.2211 | 241.1777 | 241.0984 | 244.4324 | 292.8382 | 359.6692 | 311.0485 | 1253.8433 | 1043.9372 | 39.8279 | 301.5481 | 1254.8951 | 13.6868 | NaN | 1253.6244 | 43.495 | 1253.7995 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN
8835.1292 | NaN | 378.2872 | 241.1217 | 241.2542 | 244.4708 | 294.2908 | 360.0725 | 312.8928 | 1253.8434 | 1123.2011 | 35.0475 | 301.3018 | 1254.8951 | NaN | 21.4228 | 1253.6245 | 15.4784 | 1250.7123 | NaN | 282.8119 | NaN | NaN | NaN | NaN | NaN | NaN
8836.1292 | 486.7172 | 377.4666 | 242.9644 | 241.6235 | 244.1161 | 292.9805 | 360.4828 | 312.587 | 1253.8433 | 1136.1829 | 17.0963 | 274.8494 | 1254.8951 | NaN | 10.4727 | 1253.6244 | 34.7844 | 1253.7995 | 12.476 | 497.3978 | NaN | NaN | NaN | NaN | NaN | NaN
8837.1292 | 1248.8897 | 375.5411 | 240.3771 | 240.72 | 243.9613 | 294.7303 | 360.9521 | 314.302 | 1253.8432 | 1128.4924 | 16.7778 | 261.2761 | 1254.895 | NaN | 24.0724 | 1253.6244 | 125.8284 | 1253.7994 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN
8838.1292 | 410.361 | 374.6247 | 241.5587 | 240.9331 | 244.2158 | 298.0793 | 360.8419 | 316.0287 | 1253.8433 | 1205.9386 | 62.0771 | 253.0191 | 1254.8951 | NaN | -16.6577 | 1253.6244 | 54.3116 | 1249.5909 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN
8839.1292 | -19.66 | 374.4356 | 243.2891 | 241.6204 | 244.6313 | 295.1472 | 361.2396 | 317.368 | 1253.8441 | 1181.0497 | 23.2024 | 231.1314 | 1254.8959 | NaN | 5.0833 | 1253.6252 | 54.4779 | 1253.8003 | 196.7894 | NaN | NaN | NaN | NaN | NaN | NaN | NaN
8840.1292 | NaN | 373.3805 | 243.9778 | 241.6495 | 244.8325 | 295.0229 | 360.4188 | 317.8688 | 1253.8445 | 1130.3366 | 16.245 | 230.426 | 1254.8963 | NaN | 14.4535 | 1253.6256 | 54.9821 | 1253.8007 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN
8841.1292 | NaN | 373.8565 | 241.7826 | 241.044 | 244.8512 | 298.0922 | 360.5983 | 317.9992 | 1253.8441 | 1062.4529 | 64.004 | 244.1847 | 1254.8959 | 16.2559 | -0.7372 | 1253.6253 | 12.4087 | 1253.8003 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN
8842.1292 | NaN | 377.2124 | 232.2368 | 229.7126 | 233.531 | 299.6818 | 362.185 | 301.7119 | 158.7775 | 182.6095 | 36.2759 | 236.3752 | 365.8051 | -0.3768 | 16.1027 | 311.6508 | NaN | 315.5712 | 56.2145 | -10.7981 | NaN | 672.8613 | NaN | NaN | NaN | NaN
8843.1292 | NaN | 376.7218 | 242.1023 | 241.53 | 245.6117 | 298.8871 | 362.806 | 317.2338 | 1252.3023 | NaN | 46.439 | 252.6102 | NaN | 22.4139 | -15.8747 | 1253.6255 | 187.378 | 1253.8006 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN
8844.1292 | NaN | 376.1083 | 242.1878 | 241.5599 | 245.6928 | 299.1845 | 363.746 | 317.6196 | 1253.8449 | 1079.665 | 9.432 | 246.8535 | 1254.8967 | NaN | -10.7221 | 1253.626 | 22.3117 | 1253.8011 | NaN | 690.8312 | NaN | NaN | NaN | NaN | NaN | NaN
8845.1292 | NaN | 376.5773 | 242.2681 | 241.7086 | 245.4 | 299.3696 | 361.9245 | 316.8044 | 1253.8453 | 1026.7969 | 40.6613 | 245.9965 | 1254.8971 | 12.2821 | 4.8679 | 1253.6264 | 22.1322 | 1253.8015 | NaN | 227.6271 | NaN | NaN | NaN | NaN | NaN | NaN
8846.1292 | 0.6044 | 376.643 | 239.8191 | 240.6601 | 245.707 | 303.5953 | 361.1277 | 316.8893 | 1178.8084 | 1255.2037 | 59.1697 | 287.1992 | 649.3976 | NaN | NaN | 245.9611 | NaN | 111.5937 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN
8847.1292 | 690.5788 | 377.2151 | 236.615 | 239.6059 | 246.2824 | 308.9358 | 361.0298 | 319.3003 | 429.339 | 78.2696 | 1254.2838 | 661.3115 | 1033.3127 | NaN | NaN | 1253.6271 | NaN | 971.3613 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN
8848.1448 | 678.8527 | 377.8927 | 236.6366 | 239.3825 | 246.4306 | 310.1933 | 360.9389 | 318.8254 | NaN | NaN | 219.8502 | 695.9101 | 1254.8971 | NaN | NaN | 1253.6265 | NaN | 322.5977 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN
8849.1292 | 670.1459 | 378.039 | 236.9874 | 239.3718 | 246.551 | 309.8501 | 360.8374 | 317.7535 | NaN | NaN | NaN | 674.8342 | 1254.8975 | NaN | NaN | 1253.6268 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN
8850.1292 | 663.4642 | 378.6636 | 237.2252 | 239.265 | 246.4541 | 310.0299 | 361.9106 | 321.5689 | NaN | NaN | NaN | 656.7989 | 1254.8977 | NaN | NaN | 1253.627 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN
8851.1292 | 656.7822 | 379.6409 | 237.0762 | 239.1145 | 247.188 | 309.6718 | 362.3958 | 321.3667 | NaN | NaN | NaN | 643.5552 | 1254.8982 | NaN | NaN | 1253.6275 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN
8852.1448 | 651.0517 | 379.3241 | 236.6036 | 238.979 | 247.7756 | 312.3135 | 364.0431 | 324.6911 | NaN | NaN | NaN | 617.5171 | 1254.898 | NaN | NaN | 1253.6273 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN
8853.1448 | 645.4211 | 378.6098 | 237.5691 | 238.7831 | 248.5024 | 311.9501 | 364.8011 | 324.6061 | NaN | NaN | NaN | 619.1962 | 1254.8994 | NaN | NaN | 1253.6288 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN
8854.1292 | 640.8605 | 378.7161 | 237.7723 | 238.8491 | 248.7196 | 311.0623 | 365.8764 | 322.9194 | NaN | NaN | NaN | 628.9379 | 1254.8995 | NaN | NaN | 1253.6288 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN
8855.1292 | 636.3422 | 380.6097 | 238.8357 | 239.2221 | 249.2163 | 312.06 | 366.6568 | 321.5303 | NaN | NaN | NaN | 632.0112 | 1254.899 | NaN | NaN | 1253.6283 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN
8856.1292 | 634.5337 | 380.6798 | 239.0333 | 239.0713 | 249.4757 | 312.4273 | 366.2148 | 320.4029 | NaN | NaN | NaN | 621.5747 | 1254.8994 | NaN | NaN | 1253.6288 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN
8857.1448 | 632.7278 | 380.1226 | 238.9062 | 238.8443 | 249.3442 | 314.1784 | 365.8715 | 322.2462 | NaN | NaN | NaN | 632.9206 | 1254.8988 | NaN | NaN | 1253.6281 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 823.6353 | NaN | NaN
8858.1292 | 630.7646 | 380.9395 | 239.1897 | 239.066 | 249.5597 | 313.9244 | 365.2892 | 321.7298 | NaN | NaN | NaN | 639.8052 | 1254.8994 | NaN | NaN | 1253.6287 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.8061 | NaN | NaN
8859.1292 | 629.45 | 382.1689 | 238.8894 | 239.2767 | 249.4575 | 313.5194 | 364.0499 | 320.1659 | NaN | NaN | NaN | 644.2912 | 1254.9 | NaN | NaN | 1253.6293 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -11.0325 | NaN | NaN
8860.1292 | 629.9274 | 382.9499 | 239.4241 | 239.7063 | 249.3062 | 312.2856 | 362.6281 | 318.5833 | NaN | NaN | NaN | 632.4786 | 1254.8994 | NaN | NaN | 1253.6287 | NaN | NaN | NaN | NaN | 117.1862 | NaN | NaN | -16.3892 | NaN | NaN
8861.1292 | 630.1583 | 382.7942 | 239.4334 | 239.3991 | 249.0234 | 312.3098 | 361.3714 | 317.7187 | NaN | NaN | NaN | 629.2114 | 1254.9004 | NaN | NaN | 1253.6297 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN
8862.1292 | 630.4337 | 383.4526 | 239.1522 | 239.2043 | 248.7899 | 311.9386 | 361.4447 | 316.6564 | NaN | NaN | NaN | 624.0366 | 1254.9002 | NaN | NaN | 1253.6295 | NaN | NaN | NaN | NaN | 11.7013 | NaN | NaN | NaN | NaN | NaN
8863.1292 | 634.4788 | 384.8675 | 239.0018 | 239.0855 | 248.7347 | 311.68 | 362.6165 | 315.2859 | NaN | NaN | NaN | 631.2659 | 1254.9001 | NaN | NaN | 1253.6294 | NaN | NaN | NaN | NaN | 95.4825 | NaN | NaN | NaN | NaN | NaN
8864.1292 | 642.6142 | 386.2497 | 238.8336 | 239.2523 | 249.1241 | 311.4519 | 363.6585 | 315.4126 | NaN | NaN | NaN | 641.7729 | 1254.9009 | NaN | 1152.7591 | 1253.6303 | NaN | NaN | NaN | NaN | 175.6959 | NaN | NaN | NaN | NaN | NaN
8865.1292 | 408.328 | 387.4008 | 239.1203 | 238.9076 | 249.7229 | 311.613 | 365.2777 | 315.7918 | NaN | NaN | NaN | 656.1784 | 1254.9001 | NaN | 738.9608 | 1253.6294 | NaN | NaN | NaN | NaN | 260.2386 | NaN | NaN | NaN | NaN | 19.8596
8866.1292 | 436.8394 | 387.297 | 239.1775 | 239.4175 | 249.621 | 312.3769 | 365.0441 | 316.7538 | NaN | NaN | NaN | 656.5921 | 1254.9018 | NaN | 779.9941 | 1253.6312 | NaN | NaN | NaN | NaN | 420.3802 | NaN | NaN | -0.8873 | NaN | 18.5948
8867.1292 | 678.8241 | 388.5359 | 239.8531 | 239.2329 | 249.7226 | 314.6937 | 366.39 | 319.4641 | NaN | NaN | NaN | 679.7584 | 1254.9027 | NaN | 772.021 | 1253.6321 | NaN | NaN | NaN | NaN | 675.9039 | NaN | NaN | NaN | NaN | NaN
8868.1292 | 672.3275 | 389.0176 | 240.0509 | 238.9704 | 249.7587 | 314.2598 | 366.7224 | 319.0915 | NaN | NaN | NaN | 685.7063 | 1254.9026 | NaN | 588.3152 | 1253.632 | NaN | NaN | NaN | NaN | 731.3474 | NaN | NaN | NaN | NaN | -13.6722
8869.1292 | 666.3678 | 389.1736 | 240.1126 | 239.1271 | 249.9117 | 314.0911 | 367.8742 | 318.3953 | NaN | NaN | NaN | 673.2238 | 1254.903 | NaN | 413.8836 | 1253.6323 | NaN | NaN | NaN | NaN | 797.1058 | NaN | NaN | NaN | NaN | 23.2823
8870.1292 | 662.0044 | 388.2084 | 240.1732 | 239.2186 | 250.0458 | 312.8909 | 366.9339 | 317.4545 | NaN | NaN | NaN | 663.1616 | 1254.9031 | NaN | 239.0557 | 1253.6324 | NaN | NaN | NaN | NaN | 867.4844 | NaN | NaN | 16.0576 | NaN | 24.0734
8871.1292 | 660.3871 | 387.7642 | 240.0754 | 239.1226 | 250.292 | 312.2856 | 368.4495 | 319.1233 | NaN | NaN | NaN | 661.3997 | 1254.9032 | NaN | 54.3596 | 1253.6325 | NaN | NaN | NaN | NaN | 933.4927 | NaN | NaN | 17.2098 | NaN | 23.8783
8872.1292 | 659.7472 | 387.6397 | 240.9519 | 239.6163 | 250.7851 | 311.9384 | 369.4829 | 319.0106 | NaN | NaN | NaN | 642.3226 | 1254.9028 | NaN | 51.8336 | 1253.6322 | NaN | NaN | NaN | NaN | 1000.2312 | NaN | NaN | 16.4411 | NaN | 24.2347
8873.1292 | 658.6336 | 387.7506 | 241.5131 | 239.9814 | 251.1321 | 311.6242 | 368.6675 | 319.7405 | NaN | NaN | NaN | 628.5193 | 1254.9035 | NaN | NaN | 1253.6328 | NaN | NaN | NaN | NaN | 1068.4368 | NaN | NaN | 16.5742 | NaN | 23.6988
8874.1292 | 657.1515 | 388.7276 | 242.3926 | 240.6833 | 251.6109 | 311.8764 | 369.5959 | 321.0321 | NaN | NaN | NaN | 620.9748 | 1254.9038 | NaN | NaN | 1253.6332 | NaN | NaN | NaN | NaN | 1137.4499 | NaN | NaN | 17.0682 | NaN | 23.4806
8875.1292 | 656.5303 | 390.1265 | 242.399 | 241.4066 | 252.2949 | 313.5234 | 368.7463 | 321.7478 | NaN | NaN | NaN | 636.4856 | 1254.9041 | NaN | NaN | 1253.6334 | NaN | NaN | NaN | NaN | 1213.2674 | 1236.3255 | NaN | 15.629 | NaN | 23.5347
8876.1292 | 656.3962 | 390.0792 | 242.1151 | 241.8304 | 252.7092 | 313.3867 | 370.0827 | 321.2026 | NaN | NaN | NaN | 661.3382 | 1254.9043 | NaN | NaN | 1253.6336 | NaN | NaN | NaN | NaN | 1253.765 | 601.6972 | NaN | 15.8922 | NaN | 23.5027
8877.1292 | 655.8772 | 389.1894 | 242.3123 | 241.4701 | 252.9606 | 313.7337 | 369.4377 | 321.3758 | NaN | NaN | NaN | 672.6455 | 1254.9048 | NaN | NaN | 1253.6341 | NaN | NaN | NaN | NaN | 1253.7655 | 203.1735 | NaN | 15.334 | NaN | 23.2383
8878.1292 | 655.1164 | 388.4217 | 241.6969 | 241.2335 | 253.1156 | 313.9979 | 368.1794 | 321.173 | NaN | NaN | NaN | 681.4242 | 1254.9039 | NaN | NaN | 1253.6332 | NaN | NaN | NaN | NaN | 1253.7646 | 44.6667 | NaN | 16.7758 | NaN | 23.5838
8879.1292 | 653.9695 | 388.0986 | 241.3551 | 241.6359 | 253.0872 | 314.0809 | 368.591 | 322.9615 | NaN | NaN | NaN | 675.0937 | 1254.9041 | NaN | NaN | 1253.6334 | NaN | NaN | NaN | NaN | 1253.7648 | NaN | NaN | 16.8519 | NaN | 23.9803
8880.1292 | 652.2792 | 388.9511 | 241.1966 | 241.419 | 253.0683 | 313.7848 | 367.0614 | 321.7582 | NaN | NaN | NaN | 662.1648 | 1254.9048 | NaN | NaN | 1253.6341 | NaN | NaN | NaN | NaN | 1253.7655 | NaN | NaN | 14.0113 | NaN | 23.1422
8881.1292 | 650.6473 | 389.5574 | 240.9205 | 241.6669 | 252.9042 | 314.3536 | 366.087 | 320.7139 | NaN | NaN | NaN | 660.6025 | 1254.9046 | NaN | NaN | 1253.6339 | NaN | NaN | NaN | NaN | 1253.7653 | NaN | NaN | 15.5266 | NaN | 22.8868
8882.1292 | 649.036 | 390.6353 | 241.0685 | 241.9014 | 252.8164 | 314.5508 | 364.3444 | 318.6905 | NaN | NaN | NaN | 687.4631 | 1254.9053 | NaN | NaN | 1253.6346 | NaN | NaN | NaN | NaN | 1253.766 | NaN | NaN | 14.4504 | NaN | 23.6429
8883.1292 | 647.6417 | 390.8871 | 241.5154 | 242.0186 | 252.4686 | 315.1265 | 362.4877 | 317.001 | NaN | NaN | NaN | 689.694 | 1254.9055 | NaN | NaN | 1253.6348 | NaN | NaN | NaN | NaN | 1253.7662 | -8.8897 | NaN | 14.5688 | NaN | 23.5937
8884.1292 | 646.6809 | 390.1243 | 241.5782 | 242.6221 | 252.4684 | 313.9205 | 361.3237 | 315.1663 | NaN | NaN | NaN | 680.1058 | 1254.906 | NaN | NaN | 1253.6353 | NaN | NaN | NaN | NaN | 1253.7667 | 18.0748 | NaN | 15.7776 | NaN | 23.2905
8885.1292 | 646.4801 | 389.3209 | 241.8627 | 242.7373 | 252.5028 | 312.7821 | 361.197 | 313.9486 | NaN | NaN | NaN | 674.1832 | 1254.9062 | NaN | NaN | 1253.6355 | NaN | NaN | NaN | NaN | 1253.7669 | 51.6987 | NaN | 16.3341 | NaN | 22.6235
8886.1292 | 645.9709 | 388.5963 | 242.5048 | 242.3858 | 252.6834 | 312.8142 | 360.9913 | 312.5699 | NaN | NaN | NaN | 673.2402 | 1254.9054 | NaN | NaN | 1253.6347 | NaN | NaN | NaN | NaN | 1253.7661 | 83.0593 | NaN | 15.7525 | NaN | 22.7277
8887.1292 | 644.5727 | 387.918 | 242.4639 | 242.1395 | 252.65 | 312.3759 | 361.1441 | 311.2156 | NaN | NaN | NaN | 666.6374 | 1254.9063 | NaN | NaN | 1253.6356 | NaN | NaN | NaN | NaN | 1253.767 | 106.7526 | NaN | 15.3549 | NaN | 22.7065
8888.1292 | 643.3774 | 388.7221 | 242.4681 | 241.9251 | 252.6581 | 313.1137 | 361.7818 | 309.9221 | NaN | NaN | NaN | 670.0031 | 1254.907 | NaN | NaN | 1253.6363 | NaN | NaN | NaN | NaN | 1253.7677 | 122.1872 | NaN | 16.4519 | NaN | 24.3218
8889.1292 | 641.9412 | 388.8696 | 242.4066 | 241.4917 | 252.4818 | 312.9067 | 360.688 | 308.8611 | NaN | NaN | NaN | 659.4342 | 1254.9077 | NaN | NaN | 1253.637 | NaN | NaN | NaN | NaN | 1253.7684 | 138.302 | NaN | 17.0219 | NaN | 23.3586
8890.1292 | 641.2445 | 389.3291 | 243.29 | 241.3645 | 252.485 | 313.8033 | 361.1777 | 308.2851 | NaN | NaN | NaN | 643.2724 | 1254.907 | NaN | NaN | 1253.6363 | NaN | NaN | NaN | NaN | 1253.7677 | 160.2263 | NaN | 16.4367 | NaN | 23.866
8891.1292 | 641.7111 | 388.7049 | 243.2782 | 241.1915 | 252.5904 | 312.5526 | 360.0524 | 308.1056 | NaN | NaN | NaN | 629.0813 | 1254.9072 | NaN | NaN | 1253.6366 | NaN | NaN | NaN | NaN | 1253.7679 | 192.6861 | NaN | 15.782 | NaN | 24.4225
8892.1292 | 642.3217 | 386.2501 | 242.9678 | 241.5543 | 252.6369 | 311.5358 | 359.3014 | 308.1417 | NaN | NaN | NaN | 622.1488 | 1254.9074 | NaN | NaN | 1253.6367 | NaN | NaN | NaN | NaN | 1253.7681 | 216.0217 | NaN | 15.106 | NaN | 23.4137
8893.1292 | 643.415 | 385.8798 | 243.2504 | 241.5737 | 252.6604 | 309.7545 | 357.9581 | 307.5417 | NaN | NaN | NaN | 599.4203 | 1254.9072 | NaN | NaN | 1253.6365 | NaN | NaN | NaN | NaN | 1253.7679 | 237.4418 | NaN | 15.9287 | NaN | 23.04
8894.1292 | 644.8243 | 385.1964 | 243.0815 | 241.294 | 252.4546 | 307.877 | 356.3053 | 307.5006 | NaN | NaN | NaN | 578.1063 | 1254.908 | NaN | NaN | 1253.6373 | NaN | NaN | NaN | NaN | 1253.7687 | 255.0249 | NaN | 15.0149 | NaN | 23.7643
8895.1292 | 646.1387 | 384.3655 | 243.2027 | 241.0205 | 252.5842 | 306.6807 | 355.8559 | 306.8868 | NaN | NaN | NaN | 575.2398 | 1254.908 | NaN | NaN | 1253.6373 | NaN | NaN | NaN | NaN | 1253.7687 | 262.2422 | NaN | 16.2388 | NaN | 23.0639
8896.1292 | 647.6192 | 382.2278 | 243.3475 | 241.0511 | 252.5076 | 306.6637 | 355.1537 | 307.4744 | NaN | NaN | NaN | 569.9609 | 1254.9085 | NaN | NaN | 1253.6378 | NaN | NaN | NaN | NaN | 1253.7692 | 280.5988 | NaN | 16.4678 | NaN | 23.6751
8897.1292 | 649.0681 | 382.3547 | 243.2197 | 240.6755 | 252.1878 | 305.765 | 354.7157 | 308.0813 | NaN | NaN | NaN | 574.7189 | 1254.9086 | NaN | NaN | 1253.638 | NaN | NaN | NaN | NaN | 1253.7693 | 308.3455 | NaN | 16.6749 | NaN | 22.834
8898.1292 | 650.0113 | 381.9785 | 243.3355 | 241.2629 | 252.2048 | 305.4532 | 355.3887 | 307.3108 | NaN | NaN | NaN | 570.6011 | 1254.9096 | NaN | NaN | 1253.6389 | NaN | NaN | NaN | NaN | 1253.7703 | 326.5215 | NaN | 16.2971 | NaN | 23.7245
8899.1292 | 650.7671 | 382.187 | 243.0578 | 241.5311 | 252.2834 | 305.4666 | 357.0904 | 308.8004 | NaN | NaN | NaN | 553.3457 | 1254.9091 | NaN | NaN | 1253.6384 | NaN | NaN | NaN | NaN | 1253.7698 | 340.417 | NaN | 15.9753 | NaN | 22.8514
8900.1292 | 650.9666 | 382.6856 | 242.7762 | 241.092 | 252.9137 | 305.954 | 357.4832 | 309.1417 | NaN | NaN | NaN | 558.1881 | 1254.9096 | NaN | NaN | 1253.6389 | NaN | NaN | NaN | NaN | 1253.7703 | 348.4155 | NaN | 15.7072 | NaN | 23.2974
8901.1292 | 650.586 | 383.2973 | 242.7888 | 241.3203 | 253.0954 | 307.2051 | 359.2657 | 309.3187 | NaN | NaN | NaN | 548.3007 | 1254.91 | NaN | NaN | 1253.6394 | NaN | NaN | NaN | NaN | 1253.7707 | 360.7452 | NaN | 15.193 | NaN | 22.2557
8902.1292 | 649.5729 | 383.7669 | 243.2454 | 241.6319 | 253.5527 | 308.9523 | 359.4621 | 309.3022 | NaN | NaN | NaN | 536.5724 | 1254.9095 | NaN | NaN | 1253.6388 | NaN | NaN | NaN | NaN | 1253.7702 | 371.5038 | NaN | 15.0298 | NaN | 22.577
8903.1292 | 649.0536 | 384.6152 | 243.4031 | 241.1401 | 253.666 | 310.0285 | 360.0151 | 310.229 | NaN | NaN | NaN | 556.2829 | 1254.9102 | NaN | NaN | 1253.6395 | NaN | NaN | NaN | NaN | 1253.7709 | 380.1406 | NaN | 14.9339 | NaN | 22.4581
8904.1292 | 649.0629 | 385.3285 | 243.1296 | 241.0444 | 253.7016 | 311.4752 | 360.8543 | 311.2002 | NaN | NaN | NaN | 556.0433 | 1254.9105 | NaN | NaN | 1253.6398 | NaN | NaN | NaN | NaN | 1253.7712 | 391.1677 | NaN | 16.8912 | NaN | 22.7556
8905.1292 | 649.1804 | 385.8143 | 243.1274 | 240.4625 | 253.4485 | 311.1205 | 361.2953 | 310.78 | NaN | NaN | NaN | 570.9304 | 1254.9106 | NaN | NaN | 1253.6399 | NaN | NaN | NaN | NaN | 1253.7713 | 402.6801 | NaN | 15.7688 | NaN | 22.8466
8906.1292 | 649.1044 | 386.2246 | 242.9287 | 240.8574 | 253.6653 | 311.0893 | 362.6009 | 311.4365 | NaN | NaN | NaN | 577.3549 | 1254.9107 | NaN | NaN | 1253.64 | NaN | NaN | NaN | NaN | 1253.7714 | 414.5415 | NaN | 14.6232 | NaN | 22.3669
8907.1292 | 649.2212 | 386.3208 | 243.6793 | 241.0214 | 254.3558 | 311.7216 | 364.2013 | 310.926 | NaN | NaN | NaN | 591.2149 | 1254.9108 | NaN | NaN | 1253.6402 | NaN | NaN | NaN | NaN | 1253.7715 | 431.0524 | NaN | 17.171 | NaN | 22.7337
8908.1292 | 648.7486 | 386.6843 | 243.5266 | 241.3824 | 254.393 | 311.9828 | 363.359 | 310.4013 | NaN | NaN | NaN | 597.433 | 1254.9116 | NaN | NaN | 1253.6409 | NaN | NaN | NaN | NaN | 1253.7723 | 442.2376 | NaN | 16.4798 | NaN | 23.4951
8909.1292 | 648.6941 | 386.5952 | 244.0213 | 241.472 | 254.8911 | 312.5092 | 362.8763 | 309.7051 | NaN | NaN | NaN | 605.253 | 1254.9107 | NaN | NaN | 1253.64 | NaN | NaN | NaN | NaN | 1253.7714 | 454.1085 | NaN | 16.8307 | NaN | 22.4983
8910.1292 | 648.4134 | 386.9553 | 244.2372 | 241.7035 | 255.7365 | 312.7104 | 363.6994 | 309.452 | NaN | NaN | NaN | 625.9587 | 1254.9116 | NaN | NaN | 1253.6409 | NaN | NaN | NaN | NaN | 1253.7723 | 470.0238 | NaN | 16.3687 | NaN | 22.4896
8911.1292 | 648.2657 | 387.1749 | 244.724 | 241.5522 | 256.3711 | 312.4924 | 363.9573 | 311.2771 | NaN | NaN | NaN | 612.6379 | 1254.9119 | NaN | NaN | 1253.6412 | NaN | NaN | NaN | NaN | 1253.7726 | 495.0299 | NaN | 14.8023 | NaN | 22.3694
8912.1292 | 648.0245 | 387.1288 | 244.4171 | 241.4395 | 256.0658 | 312.5555 | 365.6915 | 310.8625 | NaN | NaN | NaN | 604.8333 | 1254.9117 | NaN | NaN | 1253.641 | NaN | NaN | NaN | NaN | 1253.7724 | 516.3691 | NaN | 16.7331 | NaN | 22.6438
8913.1292 | 647.742 | 387.6407 | 244.7321 | 241.0954 | 256.1683 | 313.8793 | 367.3281 | 310.8163 | NaN | NaN | NaN | 590.0714 | 1254.9123 | NaN | NaN | 1253.6416 | NaN | NaN | NaN | NaN | 1253.773 | 543.6872 | NaN | 15.4868 | NaN | 22.9593
8914.1292 | 647.3131 | 388.6952 | 244.4621 | 240.8238 | 256.1387 | 315.0856 | 368.5881 | 311.1023 | NaN | NaN | NaN | 573.951 | 1254.9124 | NaN | NaN | 1253.6417 | NaN | NaN | NaN | NaN | 1253.7731 | 565.6019 | NaN | 16.0583 | NaN | 22.9694
8915.1292 | 646.8507 | 388.8905 | 244.4552 | 241.1453 | 256.1321 | 314.9909 | 370.0532 | 311.0676 | NaN | NaN | NaN | 556.0258 | 1254.9123 | NaN | NaN | 1253.6416 | NaN | NaN | NaN | NaN | 1253.773 | 592.5111 | NaN | 16.4766 | NaN | 24.0901
8916.1292 | 648.049 | 388.9644 | 244.6251 | 241.6659 | 256.044 | 314.6649 | 369.5439 | 310.6139 | NaN | NaN | NaN | 568.133 | 1254.9127 | NaN | NaN | 1253.6421 | NaN | NaN | NaN | NaN | 1253.7734 | 612.5386 | NaN | 16.6545 | NaN | 22.9962
8917.1292 | 649.1422 | 389.5491 | 244.6893 | 241.6367 | 256.3674 | 315.0131 | 371.4297 | 310.3369 | NaN | NaN | NaN | 579.2708 | 1254.9125 | NaN | NaN | 1253.6418 | NaN | NaN | NaN | NaN | 1253.7732 | 633.7935 | NaN | 16.7459 | NaN | 22.9311
8918.1292 | 650.4428 | 390.4779 | 245.1804 | 241.4217 | 256.2784 | 316.1378 | 373.3244 | 310.5845 | NaN | NaN | NaN | 598.4172 | 1254.914 | NaN | NaN | 1253.6433 | NaN | NaN | NaN | NaN | 1253.7747 | 661.9069 | NaN | 16.7292 | NaN | 23.1279
8919.1292 | 651.4751 | 390.8167 | 245.3165 | 241.0826 | 255.8077 | 315.7207 | 373.0501 | 310.9318 | NaN | NaN | NaN | 594.6349 | 1254.9135 | NaN | NaN | 1253.6429 | NaN | NaN | NaN | NaN | 1253.7742 | 693.4769 | NaN | 16.2607 | NaN | 23.8593
8920.1292 | 652.6504 | 390.7061 | 245.7816 | 241.1596 | 255.6919 | 315.9473 | 372.5151 | 309.8101 | NaN | NaN | NaN | 586.5795 | 1254.9141 | NaN | NaN | 1253.6434 | NaN | NaN | NaN | NaN | 1253.7748 | 716.243 | NaN | 16.126 | NaN | 22.618
8921.1292 | 652.86 | 390.9052 | 246.2474 | 241.36 | 255.6814 | 315.7033 | 372.3032 | 309.9528 | NaN | NaN | NaN | 607.6266 | 1254.9142 | NaN | NaN | 1253.6435 | NaN | NaN | NaN | NaN | 1253.7749 | 738.6252 | NaN | 17.2327 | NaN | 23.6979
8922.1292 | 653.4301 | 391.4062 | 245.9548 | 241.2628 | 255.597 | 316.508 | 373.235 | 310.0772 | NaN | NaN | NaN | 619.0105 | 1254.9135 | NaN | NaN | 1253.6428 | NaN | NaN | NaN | NaN | 1253.7742 | 760.7321 | NaN | 16.9883 | NaN | 23.2244
8923.1292 | 654.4588 | 392.8738 | 245.754 | 241.3358 | 255.1497 | 317.1829 | 375.1833 | 310.3121 | NaN | NaN | NaN | 615.1681 | 1254.9132 | NaN | NaN | 1253.6425 | NaN | NaN | NaN | NaN | 1253.7739 | 787.3563 | NaN | 18.2529 | NaN | 23.3252
8924.1292 | 656.0948 | 392.7384 | 245.8263 | 241.1335 | 255.2886 | 317.388 | 374.3892 | 312.3001 | NaN | NaN | NaN | 624.8657 | 1254.9126 | NaN | NaN | 1253.6419 | NaN | NaN | NaN | NaN | 1253.7733 | 804.5117 | NaN | 16.167 | NaN | 22.6919
8925.1292 | 657.8659 | 392.3875 | 246.2525 | 242.0927 | 256.0091 | 316.0822 | 371.829 | 311.8059 | NaN | NaN | NaN | 658.4467 | 1254.9135 | NaN | NaN | 1253.6428 | NaN | NaN | NaN | NaN | 1253.7742 | 826.773 | NaN | 16.7875 | NaN | 23.0607
8926.1292 | 659.1342 | 392.6903 | 246.4603 | 243.103 | 256.1461 | 314.6976 | 370.9827 | 310.8548 | NaN | NaN | NaN | 638.4824 | 1254.9139 | NaN | NaN | 1253.6433 | NaN | NaN | NaN | NaN | 1253.7746 | 845.2634 | NaN | 16.8454 | NaN | 24.6389
8927.1292 | 660.5471 | 392.7135 | 246.0667 | 242.9545 | 256.406 | 314.7257 | 371.9494 | 309.6323 | NaN | NaN | NaN | 611.6725 | 1254.9135 | NaN | NaN | 1253.6429 | NaN | NaN | NaN | NaN | 1253.7742 | 865.4364 | NaN | 16.4261 | NaN | 22.9022
8928.1292 | 660.8473 | 394.2577 | 246.2115 | 242.6485 | 256.3985 | 314.6068 | 371.7575 | 308.8561 | NaN | NaN | NaN | 594.9845 | 1254.9139 | NaN | NaN | 1253.6432 | NaN | NaN | NaN | NaN | 1253.7746 | 881.6121 | NaN | 16.2481 | NaN | 22.2781
8929.1292 | 661.1481 | 393.7949 | 246.3316 | 242.5374 | 256.0931 | 313.8104 | 371.7353 | 308.4099 | NaN | NaN | NaN | 609.2383 | 1254.9143 | NaN | NaN | 1253.6436 | NaN | NaN | NaN | NaN | 1253.775 | 902.1434 | NaN | 15.5002 | NaN | 22.5602
8930.1292 | 662.5019 | 394.1431 | 246.5097 | 242.5237 | 255.6246 | 314.6589 | 372.1531 | 309.1982 | NaN | NaN | NaN | 598.9212 | 1254.9135 | NaN | NaN | 1253.6428 | NaN | NaN | NaN | NaN | 1253.7742 | 924.426 | NaN | 15.076 | NaN | 22.8349
8931.1292 | 663.3702 | 394.4103 | 246.7624 | 242.5534 | 256.4263 | 315.283 | 372.8725 | 310.9377 | NaN | NaN | NaN | 633.1408 | 1254.9144 | NaN | NaN | 1253.6437 | NaN | NaN | NaN | NaN | 1253.7751 | 950.8256 | NaN | 16.8073 | NaN | 23.3681
8932.1292 | 665.2969 | 394.911 | 247.2385 | 242.4533 | 256.2306 | 315.6992 | 373.4512 | 311.7231 | NaN | NaN | NaN | 631.4211 | 1254.915 | NaN | NaN | 1253.6443 | NaN | NaN | NaN | NaN | 1253.7757 | 974.452 | NaN | 17.4327 | NaN | 22.7975
8933.1292 | 666.0758 | 395.5292 | 247.6727 | 243.4583 | 256.2185 | 316.5612 | 374.3594 | 312.4226 | NaN | NaN | NaN | 604.704 | 1254.9146 | NaN | NaN | 1253.6439 | NaN | NaN | NaN | NaN | 1253.7753 | 988.8955 | NaN | 15.9267 | NaN | 23.1781
8934.1292 | 665.8921 | 395.5743 | 248.3073 | 243.2542 | 256.0165 | 316.7577 | 376.8724 | 314.9358 | NaN | NaN | NaN | 591.3531 | 1254.9161 | NaN | NaN | 1253.6454 | NaN | NaN | NaN | NaN | 1253.7768 | 1003.7193 | NaN | 15.8963 | NaN | 22.9816
8935.1292 | 665.9653 | 395.6076 | 249.0906 | 243.2875 | 256.0126 | 316.1312 | 376.8498 | 315.6718 | NaN | NaN | NaN | 572.7615 | 1254.9156 | NaN | NaN | 1253.645 | NaN | NaN | NaN | NaN | 1253.7763 | 1026.9135 | NaN | 15.1263 | NaN | 25.2312
8936.1292 | 665.0444 | 395.7464 | 249.1445 | 243.1712 | 256.8063 | 316.7602 | 378.0298 | 316.8711 | NaN | NaN | NaN | 568.0134 | 1254.9156 | NaN | NaN | 1253.6449 | NaN | NaN | NaN | NaN | 1253.7763 | 1052.3452 | NaN | 15.4356 | NaN | 23.0271
8937.1292 | 664.3823 | 396.0812 | 249.4633 | 243.1045 | 257.1502 | 318.6286 | 378.281 | 318.8982 | NaN | NaN | NaN | 598.2726 | 1254.9161 | NaN | NaN | 1253.6455 | NaN | NaN | NaN | NaN | 1253.7768 | 1073.6203 | NaN | 17.0877 | NaN | 23.7136
8938.1292 | 663.7365 | 395.6672 | 248.8174 | 243.5277 | 258.3541 | 318.0174 | 377.2447 | 318.0842 | NaN | NaN | NaN | 600.2542 | 1254.9158 | NaN | NaN | 1253.6451 | NaN | NaN | NaN | NaN | 1253.7765 | 1106.2924 | NaN | 15.0466 | NaN | 23.1231
8939.1292 | 663.579 | 395.9375 | 249.1688 | 243.2624 | 258.4954 | 317.8016 | 377.8211 | 318.6147 | NaN | NaN | NaN | 609.9213 | 1254.916 | NaN | NaN | 1253.6453 | NaN | NaN | NaN | NaN | 1253.7767 | 1122.5047 | NaN | 17.2968 | NaN | 22.8213
8940.1292 | 664.5816 | 396.8844 | 248.9326 | 243.8501 | 258.1074 | 320.6172 | 378.159 | 318.8004 | NaN | NaN | NaN | 593.3215 | 1254.9171 | NaN | NaN | 1253.6464 | NaN | NaN | NaN | NaN | 1253.7778 | 1139.6752 | NaN | 15.4901 | NaN | 24.8716
8941.1292 | 665.2832 | 397.361 | 249.4657 | 243.7485 | 258.1885 | 322.6175 | 377.6882 | 318.2995 | NaN | NaN | NaN | 596.3368 | 1254.9165 | NaN | NaN | 1253.6458 | NaN | NaN | NaN | NaN | 1253.7772 | 1157.1653 | NaN | 15.5343 | NaN | 23.4289
8942.1292 | 664.9989 | 398.5004 | 250.0398 | 243.7869 | 258.1002 | 323.6621 | 379.4635 | 319.0796 | NaN | NaN | NaN | 586.168 | 1254.9166 | NaN | NaN | 1253.646 | NaN | NaN | NaN | NaN | 1253.7773 | 1182.7531 | NaN | 18.1148 | NaN | 22.9459
8943.1292 | 665.1372 | 398.2279 | 250.2183 | 243.5213 | 258.3294 | 323.664 | 379.6846 | 318.489 | NaN | NaN | NaN | 603.0344 | 1254.917 | NaN | NaN | 1253.6463 | NaN | NaN | NaN | NaN | 1253.7777 | 1205.7653 | NaN | 18.6137 | NaN | 24.2455
8944.1292 | 665.0593 | 398.1877 | 250.8302 | 243.8015 | 258.8069 | 324.8186 | 380.1272 | 317.9771 | NaN | NaN | NaN | 607.8467 | 1254.9183 | NaN | NaN | 1253.6476 | NaN | NaN | NaN | NaN | 1253.779 | 1223.8233 | NaN | 15.2098 | NaN | 21.7834
8945.1292 | 666.1508 | 398.6979 | 250.3866 | 244.1664 | 258.9328 | 325.4785 | 379.884 | 317.9224 | NaN | NaN | NaN | 628.4975 | 1254.9182 | NaN | NaN | 1253.6475 | NaN | NaN | NaN | NaN | 1253.7789 | 1231.1003 | NaN | 15.0535 | NaN | 24.011
8946.1292 | 667.4575 | 399.123 | 249.9811 | 244.2876 | 258.5889 | 325.7957 | 380.4569 | 317.9827 | NaN | NaN | NaN | 653.9244 | 1254.9181 | NaN | NaN | 1253.6474 | NaN | NaN | NaN | NaN | 1253.7788 | 1240.9846 | NaN | 16.6726 | NaN | 24.6055
8947.1292 | 667.6035 | 400.2967 | 250.0988 | 244.3301 | 258.8442 | 326.5108 | 379.7817 | 316.8554 | NaN | NaN | NaN | 674.9888 | 1254.9189 | NaN | NaN | 1253.6482 | NaN | NaN | NaN | NaN | 1253.7796 | 1239.6178 | NaN | 17.2096 | NaN | 25.4244
8948.1292 | 667.5102 | 401.1839 | 250.8497 | 244.6658 | 258.9937 | 328.1466 | 379.2555 | 315.4623 | NaN | NaN | NaN | 667.0863 | 1254.9186 | NaN | NaN | 1253.6479 | NaN | NaN | NaN | NaN | 1253.7793 | 1249.3914 | NaN | 16.5855 | NaN | 22.6447
8949.1292 | 667.9895 | 402.8585 | 251.0605 | 245.3276 | 259.2669 | 330.1026 | 379.6908 | 314.547 | NaN | NaN | NaN | 665.9557 | 1254.9184 | NaN | NaN | 1253.6477 | NaN | NaN | NaN | NaN | 1253.7791 | 1254.3484 | NaN | 17.3796 | NaN | 23.734
8950.1292 | 669.019 | 403.7738 | 252.0888 | 245.6372 | 259.1638 | 331.3193 | 380.851 | 314.2878 | NaN | NaN | NaN | 646.3976 | 1254.9188 | NaN | NaN | 1253.6482 | NaN | NaN | NaN | NaN | 1253.7795 | 1254.3488 | NaN | 15.9516 | NaN | 22.9727
8951.1292 | 670.254 | 404.3481 | 252.4141 | 246.3276 | 259.3223 | 332.092 | 382.2572 | 316.811 | NaN | NaN | NaN | 632.5598 | 1254.9176 | NaN | NaN | 1253.647 | NaN | NaN | NaN | NaN | 1253.7783 | 1254.3476 | NaN | 15.0601 | NaN | 22.4071
8952.1292 | 672.0372 | 404.7616 | 253.1287 | 246.816 | 259.9276 | 332.0257 | 385.0423 | 319.6743 | NaN | NaN | NaN | 609.7368 | 1254.9192 | NaN | NaN | 1253.6485 | NaN | NaN | NaN | NaN | 1253.7799 | 1254.3492 | NaN | 15.6169 | NaN | 24.0388
8953.1292 | 675.0245 | 406.1117 | 252.607 | 246.5834 | 259.8946 | 333.0639 | 386.6264 | 320.2369 | NaN | NaN | NaN | 613.5486 | 1254.9199 | NaN | NaN | 1253.6492 | NaN | NaN | NaN | NaN | 1253.7806 | 1254.3499 | NaN | 14.6188 | NaN | 22.6456
8954.1292 | 676.5435 | 405.7452 | 252.3473 | 246.805 | 261.3404 | 334.5311 | 387.0827 | 321.3412 | NaN | NaN | NaN | 623.6127 | 1254.92 | NaN | NaN | 1253.6493 | NaN | NaN | NaN | NaN | 1253.7807 | 1254.3499 | NaN | 16.7704 | NaN | 24.1922
8955.1292 | 677.3524 | 406.3266 | 253.0336 | 247.1536 | 261.8602 | 335.4312 | 387.1252 | 321.5827 | NaN | NaN | NaN | 636.8396 | 1254.9204 | NaN | NaN | 1253.6497 | NaN | NaN | NaN | NaN | 1253.7811 | 1254.3504 | NaN | 18.2104 | NaN | 23.1021
8956.1292 | 678.1672 | 406.5797 | 254.0579 | 247.1707 | 262.539 | 336.2078 | 388.8833 | 322.3246 | NaN | NaN | NaN | 639.0201 | 1254.9198 | NaN | NaN | 1253.6491 | NaN | NaN | NaN | NaN | 1253.7805 | 1254.3498 | NaN | 17.7813 | NaN | 23.1013
8957.1292 | 679.1835 | 407.8284 | 254.3654 | 247.071 | 262.8799 | 337.1437 | 389.3453 | 322.1674 | NaN | NaN | NaN | 653.1932 | 1254.9203 | NaN | NaN | 1253.6496 | NaN | NaN | NaN | NaN | 1253.781 | 1254.3502 | NaN | 14.8264 | NaN | 22.622
8958.1292 | 680.8831 | 408.8512 | 254.7233 | 246.7225 | 263.0863 | 337.6328 | 391.549 | 322.8299 | NaN | NaN | NaN | 650.0125 | 1254.9202 | NaN | NaN | 1253.6495 | NaN | NaN | NaN | NaN | 1253.7809 | 1254.3502 | NaN | 15.4926 | NaN | 22.0599
8959.1292 | 682.5186 | 408.8521 | 255.1791 | 246.7115 | 263.0004 | 338.803 | 392.3232 | 324.3409 | NaN | NaN | NaN | 639.8518 | 1254.921 | NaN | NaN | 1253.6503 | NaN | NaN | NaN | NaN | 1253.7817 | 1254.351 | NaN | 16.6531 | NaN | 22.3907
8960.1292 | 684.0828 | 409.4012 | 255.272 | 247.3185 | 262.769 | 338.5461 | 393.1874 | 325.1142 | NaN | NaN | NaN | 634.0242 | 1250.6214 | NaN | NaN | 1253.6498 | NaN | NaN | NaN | NaN | 1253.7812 | 1254.3504 | NaN | 17.323 | NaN | 22.8435
8961.1292 | 685.0013 | 409.6625 | 255.0644 | 247.7814 | 263.32 | 340.2776 | 395.4708 | 328.7372 | NaN | NaN | NaN | 606.4661 | 1222.3202 | NaN | NaN | 1253.6497 | NaN | NaN | NaN | NaN | 1253.7811 | 1254.3504 | NaN | 15.248 | NaN | 23.1606
8962.1292 | 685.3943 | 410.7876 | 255.2875 | 247.8378 | 263.2762 | 340.4647 | 398.3747 | 330.7174 | NaN | NaN | NaN | 580.9713 | 1195.407 | NaN | NaN | 1253.6509 | NaN | NaN | NaN | NaN | 1253.7823 | 1254.3516 | NaN | 15.9648 | NaN | 23.8893
8963.1292 | 685.9135 | 411.1606 | 256.6704 | 248.2877 | 264.054 | 341.0147 | 399.1102 | 332.1784 | NaN | NaN | NaN | 562.324 | 1169.8086 | NaN | NaN | 1253.6509 | NaN | NaN | NaN | NaN | 1253.7823 | 1254.3516 | NaN | 14.9255 | NaN | 22.8696
8964.1292 | 686.7644 | 412.426 | 256.9203 | 249.667 | 264.3816 | 341.4312 | 400.8598 | 332.8544 | NaN | NaN | NaN | 547.0433 | 1145.324 | NaN | NaN | 1253.6503 | NaN | NaN | NaN | NaN | 1253.7817 | 1254.351 | NaN | 16.0364 | NaN | 22.8466
8965.1292 | 689.2259 | 412.9583 | 257.4833 | 250.3436 | 265.5769 | 341.3922 | 402.03 | 335.75 | NaN | NaN | NaN | 563.7845 | 1130.4599 | NaN | NaN | 1253.6509 | NaN | NaN | NaN | NaN | 1253.7822 | 1254.3515 | NaN | 16.4318 | NaN | 24.9471
8966.1292 | 691.6502 | 412.5264 | 257.7891 | 250.146 | 266.0334 | 341.1921 | 400.4389 | 338.1441 | NaN | NaN | NaN | 565.5363 | 1105.6928 | NaN | NaN | 1253.6507 | NaN | NaN | NaN | NaN | 1253.782 | 1254.3513 | NaN | 14.9539 | NaN | 24.3695
8967.1292 | 692.4835 | 411.2295 | 258.6444 | 249.9322 | 266.6316 | 338.8387 | 398.9268 | 340.7593 | NaN | NaN | NaN | 564.8365 | 1081.8565 | NaN | NaN | 1253.65 | NaN | NaN | NaN | NaN | 1253.7814 | 1254.3506 | NaN | 14.6216 | NaN | 23.3569
8968.1292 | 693.0066 | 410.0121 | 258.1722 | 250.2548 | 267.0841 | 337.0338 | 398.1054 | 343.0142 | NaN | NaN | NaN | 559.6602 | 1059.1058 | NaN | NaN | 1253.6502 | NaN | NaN | NaN | NaN | 1253.7816 | 1254.3509 | NaN | 16.8807 | NaN | 25.2878
8969.1292 | 693.1458 | 410.7246 | 258.2572 | 250.957 | 267.6495 | 336.266 | 397.8859 | 344.6928 | NaN | NaN | NaN | 551.8351 | 1037.1873 | NaN | NaN | 1253.6513 | NaN | NaN | NaN | NaN | 1253.7827 | 1254.3519 | NaN | 15.9499 | NaN | 23.3462
8970.1292 | 693.0574 | 411.0947 | 258.1286 | 251.1583 | 267.9827 | 335.8608 | 399.1332 | 344.1735 | NaN | NaN | NaN | 553.3293 | 1017.3359 | NaN | NaN | 1253.6517 | NaN | NaN | NaN | NaN | 1253.7831 | 1254.3523 | NaN | 17.4198 | NaN | 23.5188
8971.1292 | 693.3597 | 410.438 | 258.3693 | 251.7766 | 268.6157 | 335.1465 | 398.5474 | 343.172 | NaN | NaN | NaN | 547.5932 | 996.1596 | NaN | NaN | 1253.6514 | NaN | NaN | NaN | NaN | 1253.7828 | 1254.3521 | NaN | 15.3507 | NaN | 25.1091
8972.1292 | 695.0745 | 410.2025 | 257.7903 | 251.7134 | 268.8667 | 335.4228 | 397.6375 | 344.0162 | NaN | NaN | NaN | 543.8174 | 975.8891 | NaN | NaN | 1253.6521 | NaN | NaN | NaN | NaN | 1253.7835 | 1254.3528 | NaN | 15.8809 | NaN | 25.3919
8973.1292 | 696.6686 | 410.2803 | 258.0147 | 252.51 | 269.7355 | 334.7611 | 397.0826 | 344.6288 | NaN | NaN | NaN | 558.6462 | 958.9003 | NaN | NaN | 1253.6518 | NaN | NaN | NaN | NaN | 1253.7832 | 1254.3525 | NaN | 16.7634 | NaN | 22.9028
8974.1292 | 697.4342 | 410.383 | 258.4983 | 254.0317 | 269.9743 | 333.5382 | 396.2139 | 344.7351 | NaN | NaN | NaN | 543.171 | 938.5106 | NaN | NaN | 1253.6528 | NaN | NaN | NaN | NaN | 1253.7842 | 1254.3535 | NaN | 16.9148 | NaN | 23.1197
8975.1292 | 697.2198 | 411.1523 | 259.6539 | 253.7603 | 270.1394 | 333.7146 | 396.6642 | 343.2773 | NaN | NaN | NaN | 535.036 | 919.1399 | NaN | NaN | 1253.6525 | NaN | NaN | NaN | NaN | 1253.7839 | 1254.3532 | NaN | 15.8358 | NaN | 22.4054
8976.1292 | 696.9486 | 412.6997 | 259.4839 | 255.1682 | 270.6027 | 334.8272 | 397.3119 | 342.5115 | NaN | NaN | NaN | 529.7543 | 900.3685 | NaN | NaN | 1253.6528 | NaN | NaN | NaN | NaN | 1253.7841 | 1254.3534 | NaN | 15.1708 | NaN | 22.9806
8977.1292 | 698.1349 | 413.8715 | 260.1072 | 255.806 | 271.064 | 336.7389 | 398.5877 | 341.8429 | NaN | NaN | NaN | 562.7786 | 892.158 | NaN | NaN | 1253.6533 | NaN | NaN | NaN | NaN | 1253.7847 | 1254.354 | NaN | 15.1139 | NaN | 23.0435
8978.1292 | 699.0163 | 414.7059 | 260.3537 | 255.7115 | 270.7694 | 336.9922 | 398.6516 | 342.7614 | NaN | NaN | NaN | 568.7072 | 874.3843 | NaN | NaN | 1253.6523 | NaN | NaN | NaN | NaN | 1253.7836 | 1254.3529 | NaN | 15.4598 | NaN | 22.9893
8979.1292 | 699.5202 | 414.2984 | 259.695 | 255.9833 | 271.6264 | 336.5958 | 398.1709 | 343.3422 | NaN | NaN | NaN | 601.7665 | 859.2516 | NaN | NaN | 1253.6525 | NaN | NaN | NaN | NaN | 1253.7839 | 1254.3532 | NaN | 14.9529 | NaN | 25.1132
8980.1292 | 699.9779 | 414.6125 | 259.4843 | 255.4419 | 271.3041 | 335.9244 | 397.7766 | 343.2649 | NaN | NaN | NaN | 597.3157 | 840.2572 | NaN | NaN | 1253.6529 | NaN | NaN | NaN | NaN | 1253.7843 | 1254.3536 | NaN | 15.5478 | NaN | 22.1591
8981.1292 | 701.0765 | 415.6456 | 259.5002 | 255.2776 | 271.3095 | 335.9395 | 399.365 | 342.9929 | NaN | NaN | NaN | 586.7443 | 821.6034 | NaN | NaN | 1253.654 | NaN | NaN | NaN | NaN | 1253.7854 | 1254.3547 | NaN | 15.9031 | NaN | 25.1525
8982.1292 | 701.1704 | 417.1494 | 259.1648 | 255.8415 | 271.8874 | 338.1214 | 399.8085 | 341.9853 | NaN | NaN | NaN | 574.0869 | 804.1595 | NaN | NaN | 1253.6538 | NaN | NaN | NaN | NaN | 1253.7852 | 1254.3545 | NaN | 14.7842 | NaN | 22.9302
8983.1292 | 701.5533 | 419.2832 | 259.7391 | 255.419 | 272.2258 | 340.0393 | 399.4803 | 341.1847 | NaN | NaN | NaN | 587.7094 | 795.1672 | NaN | NaN | 1253.6535 | NaN | NaN | NaN | NaN | 1253.7849 | 1254.3542 | NaN | 16.1471 | NaN | 22.4807
8984.1292 | 702.8384 | 420.7787 | 259.8872 | 255.5818 | 272.1858 | 341.4583 | 401.0949 | 340.6789 | NaN | NaN | NaN | 618.8835 | 781.7563 | NaN | NaN | 1253.6535 | NaN | NaN | NaN | NaN | 1253.7849 | 1254.3542 | NaN | 16.7958 | NaN | 22.9067
8985.1292 | 703.3265 | 422.0848 | 260.229 | 255.3672 | 272.4237 | 341.3842 | 400.6001 | 341.349 | NaN | NaN | NaN | 660.1922 | 769.4973 | NaN | NaN | 1253.6546 | NaN | NaN | NaN | NaN | 1253.786 | 1254.3552 | NaN | 17.292 | NaN | 22.7727
8986.1292 | 703.9261 | 422.877 | 259.4936 | 255.7369 | 271.8718 | 341.6325 | 401.6389 | 341.9515 | NaN | NaN | NaN | 636.2955 | 750.6412 | NaN | NaN | 1253.654 | NaN | NaN | NaN | NaN | 1253.7854 | 1254.3547 | NaN | 16.9759 | NaN | 22.8967
8987.1292 | 705.1967 | 423.3217 | 260.6008 | 255.8757 | 271.4347 | 342.5668 | 402.0102 | 342.0013 | NaN | NaN | NaN | 658.6873 | 741.2075 | NaN | NaN | 1253.6542 | NaN | NaN | NaN | NaN | 1253.7856 | 1254.3548 | NaN | 17.2627 | NaN | 22.8529
8988.1292 | 706.3384 | 423.5601 | 260.5346 | 256.2092 | 271.149 | 343.5092 | 404.1741 | 341.6092 | NaN | NaN | NaN | 661.3144 | 724.0578 | NaN | NaN | 1253.6538 | NaN | NaN | NaN | NaN | 1253.7851 | 1254.3544 | NaN | 18.2373 | NaN | 22.7618
8989.1292 | 706.6712 | 424.543 | 260.8472 | 256.4057 | 271.0512 | 344.064 | 404.4648 | 340.7284 | NaN | NaN | NaN | 662.4065 | 711.8554 | NaN | NaN | 1253.6552 | NaN | NaN | NaN | NaN | 1253.7865 | 1254.3558 | NaN | 18.4645 | NaN | 22.2304
8990.1292 | 706.143 | 424.6681 | 260.7312 | 256.5965 | 271.0242 | 344.074 | 403.8815 | 339.2396 | NaN | NaN | NaN | 639.7028 | 694.9421 | NaN | NaN | 1253.6541 | NaN | NaN | NaN | NaN | 1253.7854 | 1254.3547 | NaN | 17.9015 | NaN | 23.1561
8991.1292 | 703.9636 | 425.3653 | 261.5261 | 256.7483 | 271.1284 | 346.003 | 403.7632 | 339.6032 | NaN | NaN | NaN | 616.1989 | 679.3778 | NaN | NaN | 1253.6541 | NaN | NaN | NaN | NaN | 1253.7855 | 1254.3548 | NaN | 15.3338 | NaN | 23.0045
8992.1292 | 702.7109 | 425.3312 | 261.8457 | 256.422 | 271.408 | 349.3317 | 403.4433 | 341.0232 | NaN | NaN | NaN | 610.7751 | 669.6139 | NaN | NaN | 1253.6545 | NaN | NaN | NaN | NaN | 1253.7859 | 1254.3552 | NaN | 16.4181 | NaN | 24.5964
8993.1292 | 701.8025 | 425.3427 | 261.9475 | 256.7975 | 271.3994 | 350.8129 | 404.2552 | 340.7785 | NaN | NaN | NaN | 591.1178 | 655.3004 | NaN | NaN | 1253.6562 | NaN | NaN | NaN | NaN | 1253.7875 | 1254.3568 | NaN | 15.6831 | NaN | 22.5003
8994.1292 | 700.8625 | 425.1138 | 262.2964 | 256.6534 | 271.55 | 351.5332 | 404.8295 | 341.2752 | NaN | NaN | NaN | 591.1801 | 645.0878 | NaN | NaN | 1253.6547 | NaN | NaN | NaN | NaN | 1253.7861 | 1254.3554 | NaN | 16.2446 | NaN | 21.7933
8995.1292 | 700.4559 | 424.5571 | 262.9346 | 256.8648 | 271.9561 | 353.1978 | 405.4152 | 341.583 | NaN | NaN | NaN | 580.5765 | 632.3933 | NaN | NaN | 1253.655 | NaN | NaN | NaN | NaN | 1253.7864 | 1254.3557 | NaN | 16.8295 | NaN | 22.6886
8996.1292 | 700.3599 | 424.3737 | 262.4854 | 256.6675 | 271.5877 | 352.1961 | 405.59 | 342.389 | NaN | NaN | NaN | 598.1006 | 623.6849 | NaN | NaN | 1253.6562 | NaN | NaN | NaN | NaN | 1253.7875 | 1254.3568 | NaN | 16.4767 | NaN | 21.9142
8997.1292 | 700.1288 | 424.3998 | 262.7193 | 256.9822 | 271.5028 | 352.0014 | 406.0279 | 342.9098 | NaN | NaN | NaN | 616.4017 | 613.1232 | NaN | NaN | 1253.6553 | NaN | NaN | NaN | NaN | 1253.7866 | 1254.3559 | NaN | 17.1266 | NaN | 22.9894
8998.1292 | 700.473 | 425.0904 | 263.0304 | 257.0476 | 271.6213 | 353.1461 | 406.6579 | 344.3223 | NaN | NaN | NaN | 596.995 | 600.4008 | NaN | NaN | 1253.656 | NaN | NaN | NaN | NaN | 1253.7874 | 1254.3567 | NaN | 15.8732 | NaN | 22.3098
8999.1292 | 700.6664 | 424.9951 | 263.4905 | 256.5939 | 271.385 | 352.7823 | 407.3561 | 346.0253 | NaN | NaN | NaN | 583.5598 | 588.1465 | NaN | NaN | 1253.6559 | NaN | NaN | NaN | NaN | 1253.7873 | 1254.3565 | NaN | 15.568 | NaN | 23.1324
9000.1292 | 701.3403 | 425.3079 | 264.175 | 257.1195 | 271.4459 | 351.5435 | 409.0627 | 346.4969 | NaN | NaN | NaN | 568.7268 | 577.0631 | NaN | NaN | 1253.6562 | NaN | NaN | NaN | NaN | 1253.7875 | 1254.3568 | NaN | 17.6637 | NaN | 22.9677
9001.1292 | 701.0214 | 424.2955 | 264.1387 | 257.0543 | 271.5713 | 351.6428 | 409.972 | 347.4971 | NaN | NaN | NaN | 562.7463 | 571.6307 | NaN | NaN | 1253.6568 | NaN | NaN | NaN | NaN | 1253.7882 | 1254.3574 | NaN | 17.3185 | NaN | 22.2996
9002.1292 | 700.5307 | 424.4347 | 264.595 | 257.061 | 271.4894 | 350.9183 | 409.877 | 348.4075 | NaN | NaN | NaN | 560.4712 | 562.2735 | NaN | NaN | 1253.658 | NaN | NaN | NaN | NaN | 1253.7894 | 1254.3587 | NaN | 16.9354 | NaN | 22.3075
9003.1292 | 700.5852 | 423.9759 | 264.1173 | 257.9403 | 271.3067 | 351.8948 | 410.6934 | 350.4075 | NaN | NaN | NaN | 563.6048 | 553.3147 | NaN | NaN | 1253.6573 | NaN | NaN | NaN | NaN | 1253.7887 | 1254.358 | NaN | 15.3731 | NaN | 23.787
9004.1292 | 700.4056 | 423.5414 | 264.4124 | 258.0152 | 271.5256 | 351.8717 | 410.4749 | 348.9431 | NaN | NaN | NaN | 570.9802 | 542.485 | NaN | NaN | 1253.6566 | NaN | NaN | NaN | NaN | 1253.788 | 1254.3573 | NaN | 16.4312 | NaN | 23.1815
9005.1292 | 700.532 | 423.0754 | 264.3532 | 258.3685 | 271.8817 | 352.2118 | 408.7236 | 347.4997 | NaN | NaN | NaN | 610.9093 | 542.9825 | NaN | NaN | 1253.6577 | NaN | NaN | NaN | NaN | 1253.7891 | 1254.3584 | NaN | 16.3836 | NaN | 22.1858
9006.1292 | 699.7738 | 423.9757 | 264.4236 | 258.9685 | 271.9679 | 351.9875 | 407.7229 | 345.9639 | NaN | NaN | NaN | 613.6484 | 530.4859 | NaN | NaN | 1253.6574 | NaN | NaN | NaN | NaN | 1253.7888 | 1254.3581 | NaN | 16.6296 | NaN | 22.8171
9007.1292 | 699.1992 | 424.3858 | 264.0521 | 258.4578 | 272.0962 | 352.6709 | 406.9089 | 344.4771 | NaN | NaN | NaN | 605.7706 | 515.8875 | NaN | NaN | 1253.6574 | NaN | NaN | NaN | NaN | 1253.7888 | 1254.3581 | NaN | 17.5916 | NaN | 23.0957
9008.1292 | 698.4541 | 425.4533 | 264.1156 | 258.4065 | 271.9664 | 352.2943 | 405.3444 | 342.8851 | NaN | NaN | NaN | 595.9588 | 506.5881 | NaN | NaN | 1253.6578 | NaN | NaN | NaN | NaN | 1253.7892 | 1254.3585 | NaN | 14.8595 | NaN | 24.285
9009.1292 | 698.359 | 426.5589 | 264.4649 | 258.5963 | 271.7557 | 352.708 | 403.9209 | 342.4437 | NaN | NaN | NaN | 594.859 | 497.3733 | NaN | NaN | 1253.658 | NaN | NaN | NaN | NaN | 1253.7894 | 1254.3586 | NaN | 17.3103 | NaN | 22.2296
9010.1292 | 698.6609 | 427.6974 | 264.8668 | 259.096 | 272.1278 | 352.9747 | 404.7719 | 341.8402 | NaN | NaN | NaN | 596.5575 | 492.8958 | NaN | NaN | 1253.6582 | NaN | NaN | NaN | NaN | 1253.7895 | 1254.3588 | NaN | 15.5505 | NaN | 22.4883
9011.1292 | 698.5506 | 427.6847 | 265.0394 | 259.4276 | 272.2827 | 351.6162 | 403.8136 | 340.7291 | NaN | NaN | NaN | 577.4589 | 481.9844 | NaN | NaN | 1253.6573 | NaN | NaN | NaN | NaN | 1253.7887 | 1254.358 | NaN | 17.123 | NaN | 22.8223
9012.1292 | 697.7947 | 428.303 | 265.2371 | 259.4868 | 272.6451 | 351.9391 | 406.7597 | 340.2095 | NaN | NaN | NaN | 575.0272 | 474.0329 | NaN | NaN | 1253.6582 | NaN | NaN | NaN | NaN | 1253.7896 | 1254.3589 | NaN | 17.986 | NaN | 23.2788
9013.1292 | 697.3228 | 428.6487 | 265.0193 | 259.5226 | 273.4831 | 352.1397 | 407.1829 | 340.3075 | NaN | NaN | NaN | 590.224 | 470.5683 | NaN | NaN | 1253.658 | NaN | NaN | NaN | NaN | 1253.7894 | 1254.3587 | NaN | 15.6145 | NaN | 23.0829
9014.1292 | 697.5025 | 429.635 | 264.7619 | 259.2739 | 272.9705 | 352.9084 | 407.8948 | 341.0005 | NaN | NaN | NaN | 593.8433 | 461.7376 | NaN | NaN | 1253.6584 | NaN | NaN | NaN | NaN | 1253.7897 | 1254.359 | NaN | 18.114 | NaN | 24.5967
9015.1292 | 697.8042 | 430.1799 | 264.5297 | 260.041 | 273.1372 | 352.8523 | 408.8483 | 340.8283 | NaN | NaN | NaN | 616.02 | 459.388 | NaN | NaN | 1253.6588 | NaN | NaN | NaN | NaN | 1253.7902 | 1254.3594 | NaN | 15.5678 | NaN | 23.4224
9016.1292 | 697.9851 | 429.4902 | 264.9152 | 259.6013 | 273.1663 | 353.0431 | 410.4532 | 343.4449 | NaN | NaN | NaN | 611.6174 | 450.1414 | NaN | NaN | 1253.6591 | NaN | NaN | NaN | NaN | 1253.7905 | 1254.3598 | NaN | 17.5403 | NaN | 22.6935
9017.1292 | 697.2028 | 430.9604 | 264.7233 | 259.5291 | 273.5488 | 353.6255 | 409.638 | 344.2372 | NaN | NaN | NaN | 608.5201 | 441.5503 | NaN | NaN | 1253.6598 | NaN | NaN | NaN | NaN | 1253.7912 | 1254.3605 | NaN | 15.1145 | NaN | 22.5296
9018.1292 | 696.7341 | 431.6536 | 265.2632 | 260.1309 | 274.0679 | 353.6173 | 408.9354 | 344.0509 | NaN | NaN | NaN | 628.2048 | 439.0875 | NaN | NaN | 1253.6585 | NaN | NaN | NaN | NaN | 1253.7899 | 1254.3592 | NaN | 17.5065 | NaN | 23.377
9019.1292 | 696.5052 | 432.2057 | 265.4462 | 259.5016 | 273.8404 | 352.5563 | 408.8784 | 344.6191 | NaN | NaN | NaN | 609.3371 | 429.8055 | NaN | NaN | 1253.6591 | NaN | NaN | NaN | NaN | 1253.7905 | 1254.3598 | NaN | 16.9298 | NaN | 25.3993
9020.1292 | 696.9499 | 431.4654 | 264.9237 | 259.9821 | 273.7042 | 351.9532 | 408.7192 | 343.8146 | NaN | NaN | NaN | 587.5531 | 422.1507 | NaN | NaN | 1253.659 | NaN | NaN | NaN | NaN | 1253.7904 | 1254.3597 | NaN | 17.0248 | NaN | 22.4855
9021.1292 | 697.0916 | 431.4538 | 264.7761 | 261.097 | 274.0188 | 350.6402 | 409.0308 | 343.8159 | NaN | NaN | NaN | 572.2154 | 415.4374 | NaN | NaN | 1253.6605 | NaN | NaN | NaN | NaN | 1253.7919 | 1254.3612 | NaN | 15.6076 | NaN | 23.3494
9022.1292 | 696.7348 | 431.8742 | 265.1383 | 260.5796 | 274.1912 | 350.7095 | 409.6965 | 343.0516 | NaN | NaN | NaN | 569.1756 | 412.1263 | NaN | NaN | 1253.6599 | NaN | NaN | NaN | NaN | 1253.7912 | 1254.3605 | NaN | 17.2135 | NaN | 23.2634
9023.1292 | 695.4246 | 432.7719 | 265.0952 | 260.1175 | 274.4192 | 351.4359 | 409.6921 | 343.7886 | NaN | NaN | NaN | 559.243 | 405.2455 | NaN | NaN | 1253.6603 | NaN | NaN | NaN | NaN | 1253.7917 | 1254.361 | NaN | 17.0619 | NaN | 24.2501
9024.1292 | 694.2991 | 434.1823 | 265.2069 | 260.3326 | 275.0479 | 351.4048 | 411.3107 | 344.5322 | NaN | NaN | NaN | 556.9737 | 400.0128 | NaN | NaN | 1253.6607 | NaN | NaN | NaN | NaN | 1253.7921 | 1254.3613 | NaN | 16.6088 | NaN | 23.7029
9025.1292 | 693.5356 | 435.8052 | 266.5079 | 260.029 | 275.2976 | 351.3599 | 411.5228 | 343.4049 | NaN | NaN | NaN | 542.2602 | 393.8285 | NaN | NaN | 1253.6611 | NaN | NaN | NaN | NaN | 1253.7925 | 1254.3618 | NaN | 18.0144 | NaN | 23.2326
9026.1292 | 692.4302 | 436.3297 | 266.3292 | 260.2501 | 275.3293 | 351.0657 | 410.8784 | 343.3388 | NaN | NaN | NaN | 567.7006 | 397.1054 | NaN | NaN | 1253.66 | NaN | NaN | NaN | NaN | 1253.7914 | 1254.3606 | NaN | 15.97 | NaN | 23.5121
9027.1292 | 692.5241 | 436.8729 | 266.403 | 259.8253 | 275.7419 | 352.1577 | 411.6545 | 342.6001 | NaN | NaN | NaN | 590.0672 | 394.9472 | NaN | NaN | 1253.6613 | NaN | NaN | NaN | NaN | 1253.7927 | 1254.362 | NaN | 15.8138 | NaN | 24.8545
9028.1292 | 692.7743 | 437.1138 | 266.4543 | 259.7836 | 275.9492 | 353.1743 | 412.0979 | 342.8792 | NaN | NaN | NaN | 574.7087 | 385.7654 | NaN | NaN | 1253.6616 | NaN | NaN | NaN | NaN | 1253.793 | 1254.3623 | NaN | 15.4755 | NaN | 22.8937
9029.1292 | 693.1702 | 436.6837 | 267.0692 | 259.9988 | 275.9325 | 354.2164 | 413.1248 | 341.7494 | NaN | NaN | NaN | 572.7025 | 381.7869 | NaN | NaN | 1253.6621 | NaN | NaN | NaN | NaN | 1253.7935 | 1254.3628 | NaN | 15.1372 | NaN | 23.326
9030.1292 | 694.0032 | 436.8852 | 267.3636 | 260.1174 | 276.5661 | 353.2065 | 412.4999 | 341.8993 | NaN | NaN | NaN | 553.195 | 374.0199 | NaN | NaN | 1253.6613 | NaN | NaN | NaN | NaN | 1253.7926 | 1254.3619 | NaN | 17.2875 | NaN | 25.3917
9031.1292 | 694.8823 | 437.6636 | 266.7674 | 259.9138 | 276.6772 | 352.9387 | 414.3928 | 342.9569 | NaN | NaN | NaN | 537.7972 | 367.9013 | NaN | NaN | 1253.6621 | NaN | NaN | NaN | NaN | 1253.7934 | 1254.3627 | NaN | 16.7161 | NaN | 23.1107
9032.1292 | 696.1493 | 437.3742 | 267.0669 | 260.4812 | 276.7385 | 354.1484 | 417.3988 | 345.423 | NaN | NaN | NaN | 525.0984 | 362.3162 | NaN | NaN | 1253.6619 | NaN | NaN | NaN | NaN | 1253.7933 | 1254.3625 | NaN | 16.1548 | NaN | 22.8571
9033.1292 | 696.9126 | 436.1933 | 266.698 | 260.9219 | 276.3035 | 353.5914 | 419.0615 | 346.6595 | NaN | NaN | NaN | 549.3318 | 362.2479 | NaN | NaN | 1253.6618 | NaN | NaN | NaN | NaN | 1253.7932 | 1254.3625 | NaN | 16.6426 | NaN | 22.2498
9034.1292 | 698.0027 | 435.4423 | 266.8569 | 260.9283 | 276.3254 | 352.2616 | 418.6311 | 348.5961 | NaN | NaN | NaN | 553.4067 | 356.5183 | NaN | NaN | 1253.6608 | NaN | NaN | NaN | NaN | 1253.7922 | 1254.3615 | NaN | 17.094 | NaN | 22.6855
9035.1292 | 698.4576 | 436.3595 | 267.0346 | 261.3184 | 276.4087 | 350.6988 | 417.6918 | 348.3588 | NaN | NaN | NaN | 558.3795 | 354.216 | NaN | NaN | 1253.6625 | NaN | NaN | NaN | NaN | 1253.7939 | 1254.3632 | NaN | 16.5483 | NaN | 22.731
9036.1292 | 698.9442 | 436.897 | 267.0041 | 261.9001 | 276.7462 | 351.326 | 418.5335 | 347.8697 | NaN | NaN | NaN | 607.5203 | 357.4851 | NaN | NaN | 1253.6619 | NaN | NaN | NaN | NaN | 1253.7933 | 1254.3626 | NaN | 15.7777 | NaN | 22.8701
9037.1292 | 699.4404 | 437.8372 | 266.081 | 261.8954 | 276.9 | 352.9643 | 418.0275 | 347.5896 | NaN | NaN | NaN | 615.9184 | 351.7573 | NaN | NaN | 1253.6622 | NaN | NaN | NaN | NaN | 1253.7936 | 1254.3629 | NaN | 17.407 | NaN | 23.1981
9038.1292 | 700.0461 | 437.9682 | 266.2119 | 262.8555 | 277.0028 | 352.1747 | 417.3966 | 347.4043 | NaN | NaN | NaN | 612.1181 | 345.1363 | NaN | NaN | 1253.6638 | NaN | NaN | NaN | NaN | 1253.7952 | 1254.3645 | NaN | 17.5116 | NaN | 23.2116
9039.1292 | 700.9907 | 437.948 | 267.6256 | 263.484 | 277.3611 | 352.7408 | 418.8798 | 347.0413 | NaN | NaN | NaN | 613.1831 | 341.8916 | NaN | NaN | 1253.6628 | NaN | NaN | NaN | NaN | 1253.7941 | 1254.3634 | NaN | 15.9458 | NaN | 23.6965
9040.1292 | 701.3019 | 438.5083 | 267.7215 | 264.1113 | 277.5262 | 352.3431 | 420.0487 | 347.0106 | NaN | NaN | NaN | 591.9087 | 335.9367 | NaN | NaN | 1253.6633 | NaN | NaN | NaN | NaN | 1253.7947 | 1254.364 | NaN | 16.4455 | NaN | 22.9878
9041.1292 | 701.899 | 439.3185 | 267.029 | 264.1157 | 277.4701 | 353.0148 | 421.3108 | 346.7439 | NaN | NaN | NaN | 572.0218 | 331.1634 | NaN | NaN | 1253.6625 | NaN | NaN | NaN | NaN | 1253.7938 | 1254.3631 | NaN | 17.7651 | NaN | 23.7924
9042.1292 | 703.3811 | 439.0264 | 267.0623 | 264.357 | 277.5568 | 353.6509 | 421.6705 | 347.2882 | NaN | NaN | NaN | 581.3725 | 331.8767 | NaN | NaN | 1253.6628 | NaN | NaN | NaN | NaN | 1253.7941 | 1254.3634 | NaN | 16.8954 | NaN | 23.7842
9043.1292 | 705.3003 | 438.4871 | 267.9851 | 264.0867 | 277.9943 | 353.7016 | 423.8305 | 349.8781 | NaN | NaN | NaN | 593.4514 | 331.9764 | NaN | NaN | 1253.6631 | NaN | NaN | NaN | NaN | 1253.7945 | 1254.3638 | NaN | 19.2859 | NaN | 22.4598
9044.1292 | 707.396 | 439.5289 | 268.4796 | 263.6958 | 277.9046 | 353.4665 | 428.4486 | 351.925 | NaN | NaN | NaN | 589.334 | 328.1622 | NaN | NaN | 1253.6635 | NaN | NaN | NaN | NaN | 1253.7948 | 1254.3641 | NaN | 18.8755 | NaN | 23.2938
9045.1292 | 708.1369 | 439.7665 | 268.7023 | 264.0978 | 278.3588 | 352.7603 | 429.6826 | 352.9499 | NaN | NaN | NaN | 581.0437 | 324.524 | NaN | NaN | 1253.663 | NaN | NaN | NaN | NaN | 1253.7944 | 1254.3637 | NaN | 15.3386 | NaN | 20.8973
9046.1292 | 708.1568 | 441.0002 | 269.0817 | 264.4062 | 278.7124 | 352.909 | 429.6466 | 352.9535 | NaN | NaN | NaN | 561.9656 | 318.7663 | NaN | NaN | 1253.6628 | NaN | NaN | NaN | NaN | 1253.7941 | 1254.3634 | NaN | 15.6051 | NaN | 24.6699
9047.1292 | 709.2954 | 442.1626 | 269.2456 | 264.5892 | 279.0444 | 353.1456 | 429.44 | 352.6212 | NaN | NaN | NaN | 561.5492 | 319.4985 | NaN | NaN | 1253.6637 | NaN | NaN | NaN | NaN | 1253.7951 | 1254.3644 | NaN | 16.2214 | NaN | 21.0788
9048.1292 | 710.1403 | 443.3179 | 269.4513 | 264.5211 | 279.3189 | 354.1821 | 430.5486 | 352.8289 | NaN | NaN | NaN | 589.7787 | 319.1663 | NaN | NaN | 1253.6639 | NaN | NaN | NaN | NaN | 1253.7953 | 1254.3645 | NaN | 16.3703 | NaN | 24.4769
9049.1292 | 711.4791 | 444.4374 | 269.2355 | 264.4199 | 279.6672 | 355.4002 | 429.2037 | 351.3048 | NaN | NaN | NaN | 624.4946 | 319.1938 | NaN | NaN | 1253.6641 | NaN | NaN | NaN | NaN | 1253.7955 | 1254.3648 | NaN | 15.5647 | NaN | 24.5404
9050.1292 | 711.948 | 446.2182 | 269.222 | 264.2428 | 279.5156 | 355.2807 | 428.0567 | 350.3726 | NaN | NaN | NaN | 633.1662 | 313.3652 | NaN | NaN | 1253.6638 | NaN | NaN | NaN | NaN | 1253.7952 | 1254.3645 | NaN | 17.1316 | NaN | 25.313
9051.1448 | 713.1016 | 447.0215 | 268.9764 | 263.9843 | 279.6195 | 356.8793 | 428.246 | 350.3872 | NaN | NaN | NaN | 617.8547 | 308.126 | NaN | NaN | 1253.6639 | NaN | NaN | NaN | NaN | 1253.7953 | 1254.3646 | NaN | 16.1804 | NaN | 22.2145
9052.1292 | 712.877 | 447.9844 | 268.4838 | 263.7038 | 279.3613 | 357.0855 | 428.2691 | 352.0291 | NaN | NaN | NaN | 651.3256 | 315.7839 | NaN | NaN | 1253.6646 | NaN | NaN | NaN | NaN | 1253.796 | 1254.3653 | NaN | 16.2439 | NaN | 22.7681
9053.1292 | 711.8883 | 447.9982 | 268.6612 | 263.8764 | 279.0777 | 356.6871 | 426.9574 | 352.1036 | NaN | NaN | NaN | 648.235 | 308.3956 | NaN | NaN | 1253.6637 | NaN | NaN | NaN | NaN | 1253.7951 | 1254.3644 | NaN | 15.8095 | NaN | 23.4286
9054.1292 | 712.3974 | 447.7941 | 268.8987 | 264.6514 | 279.0956 | 355.9468 | 425.8867 | 351.7604 | NaN | NaN | NaN | 635.6187 | 304.55 | NaN | NaN | 1253.6642 | NaN | NaN | NaN | NaN | 1253.7956 | 1254.3649 | NaN | 16.7201 | NaN | 23.5003
9055.1292 | 713.0087 | 448.6686 | 268.7862 | 264.3219 | 279.2242 | 356.2996 | 428.9293 | 351.8588 | NaN | NaN | NaN | 610.4044 | 301.0462 | NaN | NaN | 1253.6637 | NaN | NaN | NaN | NaN | 1253.7951 | 1254.3644 | NaN | 15.6464 | NaN | 24.2139
9056.1292 | 713.3187 | 449.3197 | 269.1283 | 264.5029 | 279.6401 | 357.0032 | 428.4028 | 352.377 | NaN | NaN | NaN | 593.1853 | 298.1301 | NaN | NaN | 1253.6641 | NaN | NaN | NaN | NaN | 1253.7955 | 1254.3648 | NaN | 16.1173 | NaN | 23.3138
9057.1292 | 713.3653 | 449.3444 | 269.2602 | 264.5199 | 279.5831 | 357.7766 | 429.5704 | 351.6225 | NaN | NaN | NaN | 589.8621 | 302.7339 | NaN | NaN | 1253.6642 | NaN | NaN | NaN | NaN | 1253.7955 | 1254.3648 | NaN | 15.2517 | NaN | 21.3032
9058.1292 | 713.2235 | 450.0052 | 268.7394 | 265.2594 | 279.6381 | 359.4941 | 427.6725 | 351.2304 | NaN | NaN | NaN | 592.4248 | 303.2891 | NaN | NaN | 1253.6653 | NaN | NaN | NaN | NaN | 1253.7967 | 1254.3659 | NaN | 16.1459 | NaN | 23.0887
9059.1292 | 713.122 | 449.5457 | 269.725 | 265.0875 | 279.2746 | 361.2214 | 428.8037 | 350.6248 | NaN | NaN | NaN | 613.6857 | 304.9577 | NaN | NaN | 1253.6654 | NaN | NaN | NaN | NaN | 1253.7968 | 1254.3661 | NaN | 18.2807 | NaN | 23.0964
9060.1292 | 713.421 | 449.8278 | 270.0297 | 265.9428 | 279.8206 | 361.4638 | 427.4538 | 350.6888 | NaN | NaN | NaN | 616.888 | 303.4331 | NaN | NaN | 1253.6653 | NaN | NaN | NaN | NaN | 1253.7967 | 1254.3659 | NaN | 15.0024 | NaN | 24.9244
9061.1292 | 712.6542 | 450.1241 | 271.2057 | 265.2402 | 279.9432 | 361.7571 | 426.5359 | 349.8956 | NaN | NaN | NaN | 629.7155 | 305.2005 | NaN | NaN | 1253.6647 | NaN | NaN | NaN | NaN | 1253.7961 | 1254.3654 | NaN | 16.5374 | NaN | 22.737
9062.1292 | 712.9996 | 450.2441 | 271.3185 | 264.9167 | 279.3283 | 361.1922 | 424.0003 | 348.4344 | NaN | NaN | NaN | 648.2097 | 303.9206 | NaN | NaN | 1253.6664 | NaN | NaN | NaN | NaN | 1253.7978 | 1254.3671 | NaN | 16.5646 | NaN | 22.2579
9063.1292 | 713.9013 | 450.1645 | 271.3068 | 264.8038 | 279.2768 | 361.2935 | 423.5858 | 347.765 | NaN | NaN | NaN | 643.1615 | 300.503 | NaN | NaN | 1253.6655 | NaN | NaN | NaN | NaN | 1253.7969 | 1254.3662 | NaN | 16.7446 | NaN | 24.0663
9064.1292 | 714.9237 | 451.3749 | 271.3508 | 265.1173 | 279.3065 | 362.4995 | 431.1911 | 348.1175 | NaN | NaN | NaN | 618.9946 | 295.2464 | NaN | NaN | 1253.6656 | NaN | NaN | NaN | NaN | 1253.797 | 1254.3662 | NaN | 16.6226 | NaN | 25.0409
9065.1292 | 716.1153 | 451.494 | 271.0597 | 265.3397 | 279.4035 | 362.8395 | 434.4452 | 350.1486 | NaN | NaN | NaN | 619.5218 | 296.3432 | NaN | NaN | 1253.6655 | NaN | NaN | NaN | NaN | 1253.7968 | 1254.3661 | NaN | 17.6475 | NaN | 23.0327
9066.1292 | 715.7136 | 452.8547 | 271.139 | 265.5102 | 279.8283 | 363.0209 | 437.1423 | 352.0965 | NaN | NaN | NaN | 618.5918 | 294.5509 | NaN | NaN | 1253.666 | NaN | NaN | NaN | NaN | 1253.7974 | 1254.3667 | NaN | 16.0952 | NaN | 24.4192
9067.1292 | 716.6071 | 454.385 | 272.1954 | 266.3863 | 280.8453 | 363.0089 | 438.6138 | 352.2431 | NaN | NaN | NaN | 599.7818 | 291.7116 | NaN | NaN | 1253.6659 | NaN | NaN | NaN | NaN | 1253.7973 | 1254.3666 | NaN | 15.505 | NaN | 22.924
9068.1292 | 717.2537 | 454.707 | 272.5467 | 267.1256 | 281.4623 | 364.9464 | 439.4019 | 352.7922 | NaN | NaN | NaN | 580.979 | 289.578 | NaN | NaN | 1253.666 | NaN | NaN | NaN | NaN | 1253.7973 | 1254.3666 | NaN | 17.0329 | NaN | 23.3244
9069.1292 | 717.57 | 454.2969 | 272.6255 | 267.4173 | 281.9045 | 364.4044 | 437.3261 | 354.6192 | NaN | NaN | NaN | 571.1928 | 290.0242 | NaN | NaN | 1253.666 | NaN | NaN | NaN | NaN | 1253.7973 | 1254.3666 | NaN | 14.7948 | NaN | 24.2003
9070.1292 | 715.9294 | 453.6986 | 272.7824 | 267.471 | 281.6812 | 362.861 | 434.6728 | 352.9908 | NaN | NaN | NaN | 581.21 | 292.4849 | NaN | NaN | 1253.6659 | NaN | NaN | NaN | NaN | 1253.7973 | 1254.3666 | NaN | 15.667 | NaN | 25.124
9071.1292 | 715.2194 | 454.6551 | 272.3507 | 267.4047 | 281.4171 | 361.6561 | 433.0143 | 352.2812 | NaN | NaN | NaN | 570.2797 | 291.7737 | NaN | NaN | 1253.6657 | NaN | NaN | NaN | NaN | 1253.7971 | 1254.3664 | NaN | 17.1245 | NaN | 22.9206
9072.1292 | 716.8922 | 454.6729 | 272.1405 | 267.0528 | 281.9052 | 360.5234 | 435.2233 | 352.0905 | NaN | NaN | NaN | 562.8727 | 290.8585 | NaN | NaN | 1253.666 | NaN | NaN | NaN | NaN | 1253.7974 | 1254.3667 | NaN | 17.0061 | NaN | 22.7192
9073.1292 | 718.1507 | 453.9246 | 271.5075 | 266.2648 | 281.4372 | 360.5618 | 434.5418 | 351.2972 | NaN | NaN | NaN | 577.3049 | 295.7782 | NaN | NaN | 1253.6656 | NaN | NaN | NaN | NaN | 1253.797 | 1254.3663 | NaN | 17.1078 | NaN | 22.2307
9074.1292 | 719.6578 | 453.2418 | 271.022 | 266.6057 | 281.4083 | 360.9003 | 435.3498 | 351.7473 | NaN | NaN | NaN | 562.3337 | 293.0586 | NaN | NaN | 1253.6662 | NaN | NaN | NaN | NaN | 1253.7976 | 1254.3669 | NaN | 16.5946 | NaN | 22.8029
9075.1292 | 720.6986 | 452.8775 | 271.6892 | 266.116 | 281.4266 | 360.3736 | 433.2214 | 352.3906 | NaN | NaN | NaN | 550.2389 | 292.0706 | NaN | NaN | 1253.6668 | NaN | NaN | NaN | NaN | 1253.7982 | 1254.3674 | NaN | 17.4303 | NaN | 22.6652
9076.1292 | 721.1404 | 453.6003 | 271.5468 | 266.4595 | 281.9998 | 359.2225 | 431.6454 | 354.1328 | NaN | NaN | NaN | 537.7948 | 291.4873 | NaN | NaN | 1253.6662 | NaN | NaN | NaN | NaN | 1253.7976 | 1254.3669 | NaN | 15.506 | NaN | 23.9823
9077.1292 | 720.7565 | 451.5825 | 271.2691 | 267.1699 | 282.358 | 357.136 | 428.4145 | 355.6912 | NaN | NaN | NaN | 532.4283 | 291.3186 | NaN | NaN | 1253.6663 | NaN | NaN | NaN | NaN | 1253.7977 | 1254.3669 | NaN | 15.5678 | NaN | 25.1345
9078.1292 | 721.7888 | 450.0451 | 271.4869 | 267.3142 | 282.6207 | 355.1506 | 424.7234 | 359.2966 | NaN | NaN | NaN | 551.8456 | 293.054 | NaN | NaN | 1253.6668 | NaN | NaN | NaN | NaN | 1253.7982 | 1254.3675 | NaN | 16.1356 | NaN | 22.3016
9079.1292 | 722.4364 | 449.8103 | 271.5564 | 267.9143 | 282.9376 | 353.9264 | 422.6284 | 361.5257 | NaN | NaN | NaN | 553.1811 | 296.6718 | NaN | NaN | 1253.6676 | NaN | NaN | NaN | NaN | 1253.799 | 1254.3683 | NaN | 15.6449 | NaN | 24.708
9080.1292 | 723.4248 | 448.9337 | 271.4641 | 267.5109 | 282.8382 | 352.3818 | 420.6922 | 361.7681 | NaN | NaN | NaN | 540.6247 | 294.5202 | NaN | NaN | 1253.6667 | NaN | NaN | NaN | NaN | 1253.7981 | 1254.3674 | NaN | 18.0877 | NaN | 22.7198
9081.1448 | 724.8768 | 449.1827 | 270.8557 | 267.9261 | 283.2916 | 351.5414 | 422.5001 | 363.278 | NaN | NaN | NaN | 530.9093 | 293.7055 | NaN | NaN | 1253.6674 | NaN | NaN | NaN | NaN | 1253.7987 | 1254.368 | NaN | 15.7261 | NaN | 23.7308
9082.1292 | 724.2379 | 451.0191 | 271.1965 | 267.6249 | 283.9037 | 352.901 | 426.2201 | 364.7349 | NaN | NaN | NaN | 522.5385 | 294.0458 | NaN | NaN | 1253.667 | NaN | NaN | NaN | NaN | 1253.7984 | 1254.3676 | NaN | 14.5421 | NaN | 24.5571
9083.1292 | 723.6251 | 452.0873 | 270.4491 | 267.1026 | 283.8166 | 352.9595 | 424.9438 | 363.6628 | NaN | NaN | NaN | 537.4056 | 302.8275 | NaN | NaN | 1253.6679 | NaN | NaN | NaN | NaN | 1253.7992 | 1254.3685 | NaN | 14.7657 | NaN | 25.6436
9084.1292 | 724.8553 | 453.1735 | 271.0331 | 267.3513 | 284.0494 | 353.395 | 423.4937 | 362.6146 | NaN | NaN | NaN | 557.7787 | 301.4717 | NaN | NaN | 1253.6669 | NaN | NaN | NaN | NaN | 1253.7983 | 1254.3676 | NaN | 17.619 | NaN | 23.4977
9085.1292 | 726.3135 | 453.4804 | 271.7912 | 268.2516 | 284.2974 | 354.4392 | 422.9866 | 362.2989 | NaN | NaN | NaN | 565.539 | 306.9216 | NaN | NaN | 1253.667 | NaN | NaN | NaN | NaN | 1253.7984 | 1254.3677 | NaN | 16.5411 | NaN | 24.1554
9086.1292 | 728.4871 | 452.6417 | 272.312 | 268.9234 | 284.7578 | 355.0028 | 424.1995 | 362.1379 | NaN | NaN | NaN | 573.5655 | 304.4813 | NaN | NaN | 1253.6685 | NaN | NaN | NaN | NaN | 1253.7999 | 1254.3691 | NaN | 16.6883 | NaN | 24.3186
9087.1292 | 731.3213 | 452.8445 | 271.9288 | 268.5537 | 284.5405 | 354.3846 | 425.3651 | 363.5467 | NaN | NaN | NaN | 573.0411 | 305.9949 | NaN | NaN | 1253.6678 | NaN | NaN | NaN | NaN | 1253.7992 | 1254.3685 | NaN | 15.3253 | NaN | 22.0624
9088.1292 | 731.3225 | 453.6147 | 271.6869 | 268.932 | 284.2327 | 353.5617 | 424.3909 | 363.4181 | NaN | NaN | NaN | 561.9502 | 305.0499 | NaN | NaN | 1253.6679 | NaN | NaN | NaN | NaN | 1253.7992 | 1254.3685 | NaN | 15.8513 | NaN | 24.7122
9089.1292 | 732.037 | 454.1935 | 271.5006 | 269.5405 | 284.5429 | 354.722 | 426.2114 | 364.4243 | NaN | NaN | NaN | 560.8259 | 306.5653 | NaN | NaN | 1253.6674 | NaN | NaN | NaN | NaN | 1253.7988 | 1254.3681 | NaN | 17.1191 | NaN | 22.3544
9090.1292 | 732.1214 | 454.0606 | 271.6691 | 269.8321 | 284.8038 | 353.722 | 426.4437 | 364.5899 | NaN | NaN | NaN | 584.782 | 316.4388 | NaN | NaN | 1253.6677 | NaN | NaN | NaN | NaN | 1253.799 | 1254.3683 | NaN | 17.8353 | NaN | 24.4854
9091.1292 | 733.0144 | 454.2624 | 271.7546 | 269.4833 | 284.8588 | 352.7078 | 426.4774 | 364.6544 | NaN | NaN | NaN | 569.4529 | 312.2016 | NaN | NaN | 1253.6674 | NaN | NaN | NaN | NaN | 1253.7988 | 1254.3681 | NaN | 16.8103 | NaN | 24.1682
9092.1448 | 733.8969 | 454.9226 | 271.7191 | 269.6624 | 284.6332 | 352.8053 | 426.6168 | 364.6293 | NaN | NaN | NaN | 579.5283 | 314.1684 | NaN | NaN | 1253.6669 | NaN | NaN | NaN | NaN | 1253.7983 | 1254.3676 | NaN | 15.2635 | NaN | 22.2141
9093.1448 | 732.5809 | 455.1392 | 271.6957 | 269.6138 | 285.4465 | 351.4461 | 426.9849 | 363.6075 | NaN | NaN | NaN | 568.4439 | 312.8656 | NaN | NaN | 1253.6677 | NaN | NaN | NaN | NaN | 1253.7991 | 1254.3684 | NaN | 16.528 | NaN | 25.3186
9094.1292 | 731.6729 | 455.4731 | 271.8031 | 269.5176 | 285.4142 | 351.2684 | 425.6114 | 361.9872 | NaN | NaN | NaN | 568.4908 | 313.8115 | NaN | NaN | 1253.6684 | NaN | NaN | NaN | NaN | 1253.7998 | 1254.3691 | NaN | 16.0309 | NaN | 24.8294
9095.1292 | 731.4825 | 457.3699 | 271.6093 | 269.4514 | 285.3319 | 352.0959 | 423.6384 | 360.2896 | NaN | NaN | NaN | 591.7532 | 317.1152 | NaN | NaN | 1253.6687 | NaN | NaN | NaN | NaN | 1253.8001 | 1254.3693 | NaN | 16.5102 | NaN | 22.9293
9096.1448 | 732.4089 | 458.9629 | 271.835 | 270.1435 | 285.6626 | 355.9825 | 430.0104 | 360.4463 | NaN | NaN | NaN | 594.2374 | 316.4883 | NaN | NaN | 1253.6687 | NaN | NaN | NaN | NaN | 1253.8001 | 1254.3694 | NaN | 14.3264 | NaN | 24.987
9097.1448 | 732.3111 | 459.0775 | 271.316 | 271.0787 | 285.6042 | 356.1484 | 432.4143 | 361.0591 | NaN | NaN | NaN | 590.6083 | 319.3822 | NaN | NaN | 1253.6678 | NaN | NaN | NaN | NaN | 1253.7992 | 1254.3684 | NaN | 17.4153 | NaN | 23.6345
9098.1448 | 731.8107 | 458.9062 | 272.2222 | 270.8254 | 285.5913 | 355.2605 | 431.0816 | 363.9808 | NaN | NaN | NaN | 587.7203 | 324.9848 | NaN | NaN | 1253.6686 | NaN | NaN | NaN | NaN | 1253.8 | 1254.3693 | NaN | 17.276 | NaN | 24.2764
9099.1448 | 732.3385 | 459.7581 | 272.4873 | 271.3624 | 286.3872 | 354.6689 | 435.3723 | 366.39 | NaN | NaN | NaN | 587.187 | 323.7109 | NaN | NaN | 1253.6671 | NaN | NaN | NaN | NaN | 1253.7985 | 1254.3678 | NaN | 16.3858 | NaN | 22.3168
9100.1292 | 732.852 | 458.7254 | 272.7781 | 271.9911 | 287.5105 | 353.2609 | 431.6549 | 365.5506 | NaN | NaN | NaN | 587.6454 | 326.1218 | NaN | NaN | 1253.6687 | NaN | NaN | NaN | NaN | 1253.8001 | 1254.3693 | NaN | 16.7279 | NaN | 23.5068
9101.1292 | 733.7055 | 458.6719 | 273.2975 | 271.9534 | 287.8475 | 352.5109 | 431.5548 | 364.9639 | NaN | NaN | NaN | 572.1619 | 324.8672 | NaN | NaN | 1253.6681 | NaN | NaN | NaN | NaN | 1253.7995 | 1254.3688 | NaN | 15.8642 | NaN | 23.0038
9102.1292 | 734.1969 | 457.4966 | 272.5964 | 273.3173 | 287.9075 | 352.3283 | 431.1239 | 365.6982 | NaN | NaN | NaN | 575.4366 | 328.1701 | NaN | NaN | 1253.6683 | NaN | NaN | NaN | NaN | 1253.7997 | 1254.369 | NaN | 17.1342 | NaN | 25.4117
9103.1292 | 734.2648 | 456.971 | 272.1753 | 272.7767 | 287.318 | 351.7624 | 430.0126 | 365.1397 | NaN | NaN | NaN | 562.5228 | 328.1456 | NaN | NaN | 1253.6689 | NaN | NaN | NaN | NaN | 1253.8003 | 1254.3696 | NaN | 17.5335 | NaN | 22.9144
9104.1292 | 735.093 | 456.3485 | 272.1943 | 271.8937 | 287.3516 | 351.2474 | 427.8879 | 363.3429 | NaN | NaN | NaN | 547.4193 | 329.3329 | NaN | NaN | 1253.6683 | NaN | NaN | NaN | NaN | 1253.7997 | 1254.3689 | NaN | 15.7667 | NaN | 22.7766
9105.1292 | 736.0082 | 456.2564 | 272.1633 | 272.7845 | 287.3056 | 351.378 | 428.1975 | 364.1025 | NaN | NaN | NaN | 548.0555 | 330.5502 | NaN | NaN | 1253.6685 | NaN | NaN | NaN | NaN | 1253.7999 | 1254.3692 | NaN | 17.224 | NaN | 23.2335
9106.1292 | 735.8545 | 455.3489 | 271.9308 | 272.3395 | 286.7287 | 351.1038 | 426.7478 | 364.3808 | NaN | NaN | NaN | 541.7831 | 332.1716 | NaN | NaN | 1253.6683 | NaN | NaN | NaN | NaN | 1253.7997 | 1254.369 | NaN | 17.2039 | NaN | 23.199
9107.1292 | 736.3448 | 454.6345 | 271.5112 | 272.4083 | 286.8861 | 349.3551 | 424.9896 | 363.78 | NaN | NaN | NaN | 534.3916 | 334.279 | NaN | NaN | 1253.6689 | NaN | NaN | NaN | NaN | 1253.8002 | 1254.3695 | NaN | 16.4716 | NaN | 24.9512
9108.1292 | 737.0543 | 456.3996 | 271.7968 | 272.6008 | 286.7779 | 348.8684 | 424.5358 | 366.3429 | NaN | NaN | NaN | 530.4619 | 336.3526 | NaN | NaN | 1253.6694 | NaN | NaN | NaN | NaN | 1253.8007 | 1254.37 | NaN | 15.9908 | NaN | 22.8171
9109.1292 | 737.3102 | 457.1743 | 272.1009 | 272.4296 | 286.5366 | 349.7385 | 425.1301 | 367.3593 | NaN | NaN | NaN | 537.2092 | 338.9165 | NaN | NaN | 1253.6691 | NaN | NaN | NaN | NaN | 1253.8005 | 1254.3698 | NaN | 16.1581 | NaN | 22.7023
9110.1292 | 737.2153 | 458.0372 | 271.7599 | 272.8557 | 286.8961 | 349.845 | 427.0852 | 365.8343 | NaN | NaN | NaN | 528.0831 | 341.6301 | NaN | NaN | 1253.6684 | NaN | NaN | NaN | NaN | 1253.7998 | 1254.3691 | NaN | 17.4834 | NaN | 25.2878
9111.1448 | 737.7015 | 459.6439 | 272.2197 | 273.469 | 286.8406 | 350.7246 | 432.8799 | 365.6267 | NaN | NaN | NaN | 555.7318 | 353.6341 | NaN | NaN | 1253.6692 | NaN | NaN | NaN | NaN | 1253.8006 | 1254.3699 | NaN | 17.6896 | NaN | 24.3599
9112.1448 | 738.3051 | 460.0478 | 271.9564 | 273.4425 | 286.5254 | 353.1056 | 434.7359 | 366.3098 | NaN | NaN | NaN | 545.2024 | 353.6334 | NaN | NaN | 1253.6694 | NaN | NaN | NaN | NaN | 1253.8008 | 1254.3701 | NaN | 15.8675 | NaN | 24.9815
9113.1292 | 738.436 | 461.1883 | 271.864 | 273.198 | 286.2506 | 354.3637 | 436.7217 | 366.6734 | NaN | NaN | NaN | 538.4601 | 353.839 | NaN | NaN | 1253.6695 | NaN | NaN | NaN | NaN | 1253.8009 | 1254.3701 | NaN | 16.2472 | NaN | 23.0697
9114.1292 | 738.4442 | 461.8374 | 272.0155 | 273.455 | 286.5718 | 357.0396 | 437.8061 | 366.7638 | NaN | NaN | NaN | 538.0737 | 357.1069 | NaN | NaN | 1253.6697 | NaN | NaN | NaN | NaN | 1253.8011 | 1254.3704 | NaN | 16.7817 | NaN | 25.0941
9115.1292 | 738.2781 | 461.3053 | 273.0269 | 273.371 | 286.9687 | 359.3313 | 437.4315 | 366.0921 | NaN | NaN | NaN | 530.9747 | 359.4417 | NaN | NaN | 1253.6695 | NaN | NaN | NaN | NaN | 1253.8009 | 1254.3702 | NaN | 17.2834 | NaN | 24.7321
9116.1292 | 738.0086 | 461.837 | 272.6813 | 274.0696 | 287.6602 | 361.223 | 436.78 | 366.7102 | NaN | NaN | NaN | 529.7412 | 362.0771 | NaN | NaN | 1253.669 | NaN | NaN | NaN | NaN | 1253.8004 | 1254.3696 | NaN | 15.5261 | NaN | 22.1363
9117.1292 | 737.5313 | 461.8315 | 273.2874 | 273.84 | 287.4053 | 361.3417 | 437.6437 | 365.8206 | NaN | NaN | NaN | 534.5864 | 367.5692 | NaN | NaN | 1253.6703 | NaN | NaN | NaN | NaN | 1253.8016 | 1254.3709 | NaN | 14.9099 | NaN | 21.4806
9118.1292 | 737.1576 | 462.0007 | 273.6399 | 273.7405 | 287.9255 | 362.0877 | 435.7878 | 364.2663 | NaN | NaN | NaN | 548.804 | 370.6336 | NaN | NaN | 1253.6699 | NaN | NaN | NaN | NaN | 1253.8012 | 1254.3705 | NaN | 17.2336 | NaN | 24.0787
9119.1292 | 736.0185 | 462.931 | 273.3602 | 273.8485 | 288.0345 | 363.2232 | 436.8877 | 363.6361 | NaN | NaN | NaN | 546.5407 | 370.7308 | NaN | NaN | 1253.6696 | NaN | NaN | NaN | NaN | 1253.801 | 1254.3703 | NaN | 15.4247 | NaN | 24.7964
9120.1292 | 737.2762 | 462.8403 | 273.2398 | 273.5891 | 287.8884 | 364.617 | 435.8692 | 363.6177 | NaN | NaN | NaN | 533.5549 | 371.8764 | NaN | NaN | 1253.6695 | NaN | NaN | NaN | NaN | 1253.8009 | 1254.3702 | NaN | 16.2787 | NaN | 23.7677
9121.1292 | 737.7808 | 461.403 | 273.4758 | 273.2116 | 287.7774 | 363.311 | 434.0771 | 364.6727 | NaN | NaN | NaN | 534.197 | 375.0326 | NaN | NaN | 1253.6702 | NaN | NaN | NaN | NaN | 1253.8016 | 1254.3708 | NaN | 16.4994 | NaN | 20.4285
9122.1292 | 739.5013 | 460.741 | 274.3544 | 273.6782 | 287.8884 | 361.7343 | 435.1761 | 365.8082 | NaN | NaN | NaN | 523.4521 | 376.8553 | NaN | NaN | 1253.6695 | NaN | NaN | NaN | NaN | 1253.8009 | 1254.3702 | NaN | 16.9735 | NaN | 22.5218
9123.1292 | 739.3763 | 461.4145 | 274.1046 | 273.7852 | 288.2236 | 361.7895 | 439.2191 | 368.2462 | NaN | NaN | NaN | 526.3944 | 381.2453 | NaN | NaN | 1253.6689 | NaN | NaN | NaN | NaN | 1253.8003 | 1254.3696 | NaN | 15.9433 | NaN | 22.3146
9124.1292 | 739.4366 | 460.915 | 274.3942 | 274.6126 | 288.1452 | 360.3083 | 437.1257 | 368.5256 | NaN | NaN | NaN | 531.8632 | 384.7312 | NaN | NaN | 1253.6699 | NaN | NaN | NaN | NaN | 1253.8013 | 1254.3706 | NaN | 17.6628 | NaN | 22.7193
9125.1292 | 738.0485 | 461.4181 | 274.2961 | 275.085 | 288.1635 | 359.5148 | 435.5079 | 367.7956 | NaN | NaN | NaN | 519.8931 | 385.3952 | NaN | NaN | 1253.6708 | NaN | NaN | NaN | NaN | 1253.8022 | 1254.3715 | NaN | 17.0253 | NaN | 22.7575
9126.1292 | 737.5128 | 462.2231 | 274.9061 | 275.3117 | 288.4077 | 360.2855 | 435.247 | 366.2702 | NaN | NaN | NaN | 512.4795 | 386.9741 | NaN | NaN | 1253.6701 | NaN | NaN | NaN | NaN | 1253.8015 | 1254.3708 | NaN | 15.6455 | NaN | 23.6436
9127.1292 | 738.6317 | 462.3149 | 274.4165 | 274.553 | 287.9412 | 360.6761 | 432.811 | 363.8515 | NaN | NaN | NaN | 505.7699 | 389.6721 | NaN | NaN | 1253.6704 | NaN | NaN | NaN | NaN | 1253.8018 | 1254.3711 | NaN | 15.2666 | NaN | 22.1829
9128.1292 | 739.037 | 463.1855 | 276.0327 | 274.6253 | 288.0444 | 360.1597 | 432.9174 | 361.688 | NaN | NaN | NaN | 512.1351 | 398.214 | NaN | NaN | 1253.6703 | NaN | NaN | NaN | NaN | 1253.8017 | 1254.371 | NaN | 22.6081 | NaN | 22.4619
9129.1292 | 739.7058 | 463.3508 | 274.8419 | 273.8711 | 288.2533 | 362.045 | 432.1836 | 362.2428 | NaN | NaN | NaN | 528.9814 | 407.3951 | NaN | NaN | 1253.671 | NaN | NaN | NaN | NaN | 1253.8024 | 1254.3717 | NaN | 18.0549 | NaN | 22.7556
9130.1292 | 740.2402 | 463.396 | 274.5932 | 273.1251 | 288.1067 | 362.8004 | 432.4386 | 361.8824 | NaN | NaN | NaN | 544.4487 | 413.7401 | NaN | NaN | 1253.67 | NaN | NaN | NaN | NaN | 1253.8014 | 1254.3706 | NaN | 16.9147 | NaN | 22.0828
9131.1292 | 741.1372 | 463.4945 | 274.6525 | 273.6375 | 287.9579 | 362.3159 | 429.9149 | 360.9409 | NaN | NaN | NaN | 558.5605 | 423.4095 | NaN | NaN | 1253.6699 | NaN | NaN | NaN | NaN | 1253.8013 | 1254.3706 | NaN | 16.5133 | NaN | 22.8344
9132.1292 | 741.3759 | 463.3993 | 274.7008 | 274.3715 | 288.7595 | 361.4207 | 429.6657 | 360.2029 | NaN | NaN | NaN | 558.7003 | 422.891 | NaN | NaN | 1253.6702 | NaN | NaN | NaN | NaN | 1253.8016 | 1254.3708 | NaN | 16.9439 | NaN | 23.0913
9133.1292 | 740.5559 | 464.1976 | 274.225 | 274.3056 | 287.9532 | 361.4271 | 428.2776 | 359.3065 | NaN | NaN | NaN | 584.8388 | 513.2631 | NaN | NaN | 1253.6697 | NaN | NaN | NaN | NaN | 1253.8011 | 1254.3703 | NaN | 20.5054 | NaN | 31.3178
9134.1292 | 739.593 | 464.2342 | 273.6588 | 274.0138 | 287.124 | 361.716 | 428.6277 | 357.8129 | NaN | NaN | NaN | 571.5299 | 500.0109 | NaN | NaN | 1253.6709 | NaN | NaN | NaN | NaN | 1253.8023 | 1254.3716 | NaN | 22.5743 | NaN | -11.9404
9135.1292 | 741.2894 | 465.3703 | 273.6849 | 273.5937 | 287.663 | 361.7375 | 428.6384 | 356.4513 | NaN | NaN | NaN | 561.0251 | 504.6174 | NaN | NaN | 1253.6693 | NaN | NaN | NaN | NaN | 1253.8007 | 1254.37 | NaN | 58.0295 | NaN | 30.9016
9136.1292 | 743.6622 | 465.9047 | 273.6081 | 273.1981 | 287.5057 | 364.32 | 431.646 | 355.1372 | NaN | NaN | NaN | 560.8293 | 508.488 | NaN | NaN | 1253.6706 | NaN | NaN | NaN | NaN | 1253.802 | 1254.3713 | NaN | 17.2942 | NaN | 19.0602
9137.1292 | 743.6792 | 465.5 | 273.6316 | 273.1333 | 288.0804 | 364.5731 | 435.6779 | 356.3032 | NaN | NaN | NaN | 568.4965 | 518.7063 | NaN | NaN | 1253.6696 | NaN | NaN | NaN | NaN | 1253.8009 | 1254.3702 | NaN | 20.9417 | NaN | 31.9503
9138.1292 | 742.6983 | 466.2409 | 274.0083 | 273.1641 | 287.7844 | 363.8511 | 436.0451 | 355.7346 | NaN | NaN | NaN | 559.1938 | 518.2082 | NaN | NaN | 1253.6695 | NaN | NaN | NaN | NaN | 1253.8009 | 1254.3701 | NaN | 13.5317 | NaN | 24.9265
9139.1292 | 744.7039 | 466.9808 | 274.5954 | 273.2028 | 287.2687 | 363.8964 | 436.1934 | 356.026 | NaN | NaN | NaN | 567.2012 | 520.1838 | NaN | NaN | 1253.6707 | NaN | NaN | NaN | NaN | 1253.8021 | 1254.3713 | NaN | 29.8862 | NaN | 17.5747
9140.1292 | 746.166 | 466.853 | 274.2551 | 273.0123 | 287.1037 | 364.1207 | 436.9531 | 356.4492 | NaN | NaN | NaN | 566.2113 | 518.1152 | NaN | NaN | 1253.6701 | NaN | NaN | NaN | NaN | 1253.8015 | 1254.3708 | NaN | 33.3091 | NaN | 14.4025
9141.1292 | 745.9671 | 467.3917 | 274.862 | 272.9414 | 286.6394 | 363.4189 | 437.3909 | 356.5467 | NaN | NaN | NaN | 591.5567 | 523.289 | NaN | NaN | 1253.6706 | NaN | NaN | NaN | NaN | 1253.802 | 1254.3713 | NaN | 18.3041 | NaN | 23.0759
9142.1292 | 745.8658 | 468.2366 | 274.3069 | 272.4426 | 286.725 | 365.6766 | 437.6164 | 356.095 | NaN | NaN | NaN | 571.1728 | 452.3229 | NaN | NaN | 1253.6723 | NaN | NaN | NaN | NaN | 1253.8037 | 1254.373 | NaN | NaN | NaN | -16.6343
9143.1292 | 747.2905 | 470.6291 | 274.9552 | 272.6341 | 286.7912 | 368.7426 | 441.2322 | 354.8877 | NaN | NaN | NaN | 592.5695 | 458.0562 | NaN | NaN | 1253.6716 | NaN | NaN | NaN | NaN | 1253.803 | 1254.3723 | NaN | 13.7232 | NaN | 31.2684
9144.1292 | 747.7188 | 472.6313 | 274.5022 | 272.6367 | 286.3151 | 371.7749 | 441.7221 | 356.908 | NaN | NaN | NaN | 604.9297 | 466.8514 | NaN | NaN | 1253.6708 | NaN | NaN | NaN | NaN | 1253.8022 | 1254.3715 | NaN | 17.183 | NaN | 23.1676
9145.1292 | 748.4642 | 472.4723 | 275.2936 | 273.2965 | 286.2472 | 373.1694 | 440.6269 | 356.5049 | NaN | NaN | NaN | 615.3196 | 467.8839 | NaN | NaN | 1253.6709 | NaN | NaN | NaN | NaN | 1253.8023 | 1254.3716 | NaN | 16.3877 | NaN | 27.62
9146.1292 | 748.5714 | 472.8774 | 275.1036 | 273.2199 | 286.1829 | 373.4313 | 440.9111 | 356.3787 | NaN | NaN | NaN | 621.667 | 475.1571 | NaN | NaN | 1253.6698 | NaN | NaN | NaN | NaN | 1253.8012 | 1254.3705 | NaN | 24.2608 | NaN | 24.7276
9147.1292 | 747.8936 | 473.5408 | 275.2107 | 273.6587 | 286.132 | 373.4916 | 440.0772 | 355.2243 | NaN | NaN | NaN | 624.2884 | 479.6007 | NaN | NaN | 1253.6708 | NaN | NaN | NaN | NaN | 1253.8022 | 1254.3715 | NaN | 19.6115 | NaN | 24.5681
9148.1292 | 746.0043 | 474.0092 | 275.2522 | 274.0285 | 285.6052 | 374.058 | 438.7395 | 353.6806 | NaN | NaN | NaN | 621.0786 | 480.1539 | NaN | NaN | 1253.6705 | NaN | NaN | NaN | NaN | 1253.8019 | 1254.3712 | NaN | 16.2886 | NaN | 21.6465
9149.1292 | 745.0264 | 475.4697 | 275.4106 | 274.1247 | 285.2458 | 377.2953 | 440.8096 | 353.7172 | NaN | NaN | NaN | 646.9861 | 479.814 | NaN | NaN | 1253.6704 | NaN | NaN | NaN | NaN | 1253.8018 | 1254.3711 | NaN | 15.5195 | NaN | 31.9801
9150.1292 | 745.0896 | 476.6359 | 275.5818 | 274.8955 | 284.9801 | 382.9429 | 444.8462 | 354.0561 | NaN | NaN | NaN | 633.9895 | 478.9132 | NaN | NaN | 1253.6701 | NaN | NaN | NaN | NaN | 1253.8015 | 1254.3708 | NaN | 17.5113 | NaN | 22.3251
9151.1292 | 745.9134 | 476.8997 | 276.031 | 274.7333 | 284.8964 | 382.6628 | 442.7039 | 353.8933 | NaN | NaN | NaN | 618.8897 | 478.5157 | NaN | NaN | 1253.6713 | NaN | NaN | NaN | NaN | 1253.8027 | 1254.372 | NaN | 16.2129 | NaN | 25.4016
9152.1292 | 746.6777 | 476.9943 | 277.0265 | 274.5906 | 285.4858 | 382.9291 | 444.5984 | 354.5552 | NaN | NaN | NaN | 638.1 | 490.3866 | NaN | NaN | 1253.6696 | NaN | NaN | NaN | NaN | 1253.801 | 1254.3703 | NaN | 15.158 | NaN | 22.6912
9153.1292 | 746.5136 | 478.1618 | 276.7439 | 274.7273 | 286.1123 | 383.427 | 443.4398 | 355.2101 | NaN | NaN | NaN | 627.7134 | 486.4088 | NaN | NaN | 1253.6703 | NaN | NaN | NaN | NaN | 1253.8016 | 1254.3709 | NaN | 18.4116 | NaN | 23.073
9154.1292 | 747.2658 | 478.9661 | 277.6995 | 275.0171 | 286.168 | 383.807 | 442.1314 | 357.0562 | NaN | NaN | NaN | 626.6514 | 489.3442 | NaN | NaN | 1253.6708 | NaN | NaN | NaN | NaN | 1253.8021 | 1254.3714 | NaN | 16.1208 | NaN | 23.2894
9155.1292 | 747.4642 | 478.6823 | 277.8408 | 275.3214 | 286.4952 | 383.297 | 441.8487 | 357.6211 | NaN | NaN | NaN | 605.197 | 488.6413 | NaN | NaN | 1253.6709 | NaN | NaN | NaN | NaN | 1253.8023 | 1254.3715 | NaN | 15.5921 | NaN | 23.1097
9156.1292 | 747.2393 | 479.2756 | 278.1284 | 274.908 | 286.9312 | 384.9702 | 445.9674 | 360.7785 | NaN | NaN | NaN | 592.8368 | 490.4527 | NaN | NaN | 1253.6709 | NaN | NaN | NaN | NaN | 1253.8023 | 1254.3715 | NaN | 18.5688 | NaN | 25.2848
9157.1292 | 746.5995 | 480.6541 | 278.1692 | 274.8641 | 287.5995 | 383.3884 | 447.7543 | 362.3745 | NaN | NaN | NaN | 572.4654 | 492.3886 | NaN | NaN | 1253.6706 | NaN | NaN | NaN | NaN | 1253.802 | 1254.3713 | NaN | 16.8929 | NaN | 22.96
9158.1292 | 746.5 | 481.425 | 278.3517 | 274.4762 | 288.6755 | 382.5631 | 450.5767 | 363.4733 | NaN | NaN | NaN | 554.3645 | 495.0017 | NaN | NaN | 1253.6705 | NaN | NaN | NaN | NaN | 1253.8019 | 1254.3712 | NaN | 16.4181 | NaN | 23.7534
9159.1292 | 747.3627 | 481.5426 | 277.8527 | 274.462 | 289.0782 | 383.1748 | 451.3056 | 362.9655 | NaN | NaN | NaN | 541.724 | 498.0929 | NaN | NaN | 1253.6705 | NaN | NaN | NaN | NaN | 1253.8019 | 1254.3712 | NaN | 14.1124 | NaN | 22.8947
9160.1292 | 747.2486 | 480.5095 | 278.8052 | 274.3388 | 288.9549 | 383.8562 | 450.4427 | 364.0079 | NaN | NaN | NaN | 537.9659 | 504.3485 | NaN | NaN | 1253.6705 | NaN | NaN | NaN | NaN | 1253.8019 | 1254.3712 | NaN | 16.6109 | NaN | 24.3814
9161.1292 | 747.8505 | 479.3199 | 279.7459 | 274.2914 | 288.808 | 382.4646 | 449.3815 | 362.774 | NaN | NaN | NaN | 547.7628 | 510.8319 | NaN | NaN | 1253.6707 | NaN | NaN | NaN | NaN | 1253.8021 | 1254.3713 | NaN | 16.7464 | NaN | 23.8338
9162.1292 | 748.3484 | 478.3723 | 279.5127 | 274.9606 | 288.9219 | 382.0549 | 448.9462 | 364.7981 | NaN | NaN | NaN | 550.6916 | 515.3898 | NaN | NaN | 1253.6713 | NaN | NaN | NaN | NaN | 1253.8027 | 1254.372 | NaN | 17.414 | NaN | 23.6362
9163.1292 | 748.8187 | 478.5993 | 279.7458 | 274.7683 | 288.7315 | 382.026 | 448.2176 | 365.8405 | NaN | NaN | NaN | 559.2836 | 522.5102 | NaN | NaN | 1253.6706 | NaN | NaN | NaN | NaN | 1253.802 | 1254.3713 | NaN | 14.5328 | NaN | 23.2091
9164.1292 | 747.854 | 477.664 | 279.9697 | 274.6781 | 289.0891 | 381.2454 | 446.5573 | 367.2283 | NaN | NaN | NaN | 557.4138 | 521.264 | NaN | NaN | 1253.6713 | NaN | NaN | NaN | NaN | 1253.8027 | 1254.372 | NaN | 16.6134 | NaN | 22.4805
9165.1292 | 747.6661 | 477.3562 | 280.6633 | 274.5925 | 289.2986 | 378.9729 | 444.2987 | 366.792 | NaN | NaN | NaN | 552.8696 | 523.6097 | NaN | NaN | 1253.6708 | NaN | NaN | NaN | NaN | 1253.8022 | 1254.3715 | NaN | 16.9728 | NaN | 25.1142
9166.1292 | 747.781 | 478.8794 | 280.9801 | 274.6632 | 289.6854 | 379.8622 | 452.1615 | 369.2693 | NaN | NaN | NaN | 548.834 | 529.7967 | NaN | NaN | 1253.6713 | NaN | NaN | NaN | NaN | 1253.8026 | 1254.3719 | NaN | 18.0228 | NaN | 23.647
9167.1292 | 746.6879 | 480.565 | 280.1344 | 274.5895 | 290.0236 | 379.3559 | 457.5694 | 370.33 | NaN | NaN | NaN | 540.604 | 531.2445 | NaN | NaN | 1253.6711 | NaN | NaN | NaN | NaN | 1253.8024 | 1254.3717 | NaN | 16.6447 | NaN | 22.7774
9168.1292 | 746.393 | 481.914 | 280.7716 | 274.8502 | 290.7475 | 378.2365 | 459.0294 | 370.3494 | NaN | NaN | NaN | 534.5692 | 534.0468 | NaN | NaN | 1253.6703 | NaN | NaN | NaN | NaN | 1253.8017 | 1254.371 | NaN | 15.9143 | NaN | 25.6637
9169.1292 | 744.5005 | 482.0835 | 281.0783 | 275.1789 | 291.1108 | 377.4977 | 458.6979 | 372.874 | NaN | NaN | NaN | 545.8755 | 546.0643 | NaN | NaN | 1253.6713 | NaN | NaN | NaN | NaN | 1253.8026 | 1254.3719 | NaN | 15.9389 | NaN | 22.9667
9170.1292 | 744.6819 | 483.1055 | 281.1955 | 275.5228 | 291.2537 | 374.6919 | 457.5452 | 372.889 | NaN | NaN | NaN | 570.3697 | 550.9486 | NaN | NaN | 1253.6708 | NaN | NaN | NaN | NaN | 1253.8022 | 1254.3715 | NaN | 16.776 | NaN | 22.7762
9171.1292 | 745.151 | 484.2186 | 281.8854 | 276.3949 | 291.3801 | 373.404 | 458.9036 | 373.5138 | NaN | NaN | NaN | 590.2464 | 554.9871 | NaN | NaN | 1253.6713 | NaN | NaN | NaN | NaN | 1253.8027 | 1254.372 | NaN | 15.7027 | NaN | 22.4718
9172.1292 | 745.6569 | 484.0776 | 282.4031 | 276.2266 | 291.3825 | 373.0397 | 460.8564 | 372.9936 | NaN | NaN | NaN | 570.837 | 554.0132 | NaN | NaN | 1253.6703 | NaN | NaN | NaN | NaN | 1253.8017 | 1254.371 | NaN | 16.2613 | NaN | 22.5547
9173.1292 | 747.2243 | 485.5275 | 281.6767 | 276.7866 | 292.5857 | 373.0951 | 462.6995 | 373.0601 | NaN | NaN | NaN | 588.5857 | 562.2773 | NaN | NaN | 1253.6714 | NaN | NaN | NaN | NaN | 1253.8028 | 1254.372 | NaN | 17.2247 | NaN | 21.941
9174.1292 | 748.9707 | 486.302 | 282.1934 | 277.716 | 293.2375 | 375.2014 | 469.9808 | 374.2336 | NaN | NaN | NaN | 589.0042 | 566.1312 | NaN | NaN | 1253.6715 | NaN | NaN | NaN | NaN | 1253.8029 | 1254.3722 | NaN | 16.0667 | NaN | 24.6039
9175.1292 | 750.1047 | 487.2914 | 283.0894 | 278.8337 | 293.7844 | 376.3998 | 472.9565 | 375.1293 | NaN | NaN | NaN | 608.0141 | 569.2747 | NaN | NaN | 1253.6705 | NaN | NaN | NaN | NaN | 1253.8019 | 1254.3712 | NaN | 18.1918 | NaN | 24.5732
9176.1292 | 750.5183 | 488.0797 | 283.8226 | 279.7147 | 294.1274 | 376.2385 | 470.9058 | 376.8374 | NaN | NaN | NaN | 618.4939 | 573.4291 | NaN | NaN | 1253.6705 | NaN | NaN | NaN | NaN | 1253.8019 | 1254.3712 | NaN | 17.6232 | NaN | 22.7665
9177.1292 | 751.6037 | 488.4811 | 283.8657 | 280.3512 | 294.6514 | 375.9911 | 470.0676 | 376.1425 | NaN | NaN | NaN | 631.776 | 580.7191 | NaN | NaN | 1253.6714 | NaN | NaN | NaN | NaN | 1253.8028 | 1254.3721 | NaN | 14.6033 | NaN | 22.2233
9178.1292 | 751.969 | 489.1278 | 284.747 | 281.3679 | 295.244 | 377.4952 | 471.7979 | 377.5517 | NaN | NaN | NaN | 643.9602 | 582.1132 | NaN | NaN | 1253.6718 | NaN | NaN | NaN | NaN | 1253.8032 | 1254.3725 | NaN | 18.5677 | NaN | 25.3076
9179.1292 | 752.6172 | 489.53 | 284.5134 | 281.2581 | 295.4038 | 377.2903 | 471.8175 | 377.0024 | NaN | NaN | NaN | 649.0009 | 584.0433 | NaN | NaN | 1253.672 | NaN | NaN | NaN | NaN | 1253.8033 | 1254.3726 | NaN | 16.1166 | NaN | 23.3498
9180.1292 | 752.085 | 489.1764 | 284.1189 | 280.8751 | 294.9514 | 376.8787 | 470.0482 | 376.9957 | NaN | NaN | NaN | 624.6986 | 584.8219 | NaN | NaN | 1253.67 | NaN | NaN | NaN | NaN | 1253.8014 | 1254.3706 | NaN | 17.027 | NaN | 25.8166
9181.1292 | 752.5582 | 488.6882 | 284.4456 | 281.1306 | 295.3166 | 376.6532 | 467.0339 | 375.2479 | NaN | NaN | NaN | 629.6553 | 591.2586 | NaN | NaN | 1253.6713 | NaN | NaN | NaN | NaN | 1253.8027 | 1254.372 | NaN | 18.6946 | NaN | 23.3623
9182.1292 | 751.1773 | 488.4558 | 283.4707 | 281.6453 | 295.6466 | 378.7271 | 469.7746 | 376.945 | NaN | NaN | NaN | 651.7196 | 601.6421 | NaN | NaN | 1253.6708 | NaN | NaN | NaN | NaN | 1253.8022 | 1254.3715 | NaN | 16.5143 | NaN | 22.1446
9183.1292 | 749.6237 | 488.0306 | 283.0295 | 281.4077 | 295.1594 | 377.4955 | 466.6333 | 376.0623 | NaN | NaN | NaN | 649.7278 | 600.7757 | NaN | NaN | 1253.6708 | NaN | NaN | NaN | NaN | 1253.8021 | 1254.3714 | NaN | 17.2103 | NaN | 23.6075
9184.1292 | 749.2088 | 488.2147 | 283.8381 | 281.0454 | 295.0052 | 375.8503 | 466.0784 | 376.039 | NaN | NaN | NaN | 633.2569 | 605.6245 | NaN | NaN | 1253.6705 | NaN | NaN | NaN | NaN | 1253.8019 | 1254.3712 | NaN | 15.0273 | NaN | 23.5957
9185.1292 | 749.2801 | 487.4532 | 283.7157 | 281.4546 | 295.3013 | 374.2753 | 462.5627 | 376.8795 | NaN | NaN | NaN | 659.1965 | 615.2738 | NaN | NaN | 1253.6709 | NaN | NaN | NaN | NaN | 1253.8023 | 1254.3716 | NaN | 18.7767 | NaN | 23.2228
9186.1292 | 749.9098 | 488.8445 | 283.8588 | 281.7001 | 294.7698 | 373.1712 | 462.9407 | 376.9069 | NaN | NaN | NaN | 673.6218 | 616.4397 | NaN | NaN | 1253.6714 | NaN | NaN | NaN | NaN | 1253.8028 | 1254.372 | NaN | 16.0076 | NaN | 23.0581
9187.1292 | 750.2996 | 489.83 | 284.0685 | 281.5628 | 293.8125 | 374.4332 | 464.5967 | 376.2724 | NaN | NaN | NaN | 641.7287 | 617.3228 | NaN | NaN | 1253.6708 | NaN | NaN | NaN | NaN | 1253.8022 | 1254.3715 | NaN | 18.4554 | NaN | 23.8727
9188.1292 | 751.4444 | 490.9093 | 283.4458 | 281.8684 | 293.6314 | 375.2966 | 465.8383 | 375.1367 | NaN | NaN | NaN | 626.2187 | 619.9028 | NaN | NaN | 1253.6709 | NaN | NaN | NaN | NaN | 1253.8023 | 1254.3715 | NaN | 18.1733 | NaN | 24.9752
9189.1292 | 751.8533 | 490.8863 | 283.5124 | 282.1811 | 293.9952 | 376.5706 | 469.8982 | 376.6605 | NaN | NaN | NaN | 600.7979 | 623.4505 | NaN | NaN | 1253.6715 | NaN | NaN | NaN | NaN | 1253.8029 | 1254.3722 | NaN | 15.66 | NaN | 22.22
9190.1292 | 752.7578 | 491.2724 | 283.8073 | 282.2057 | 294.0785 | 376.9272 | 472.7185 | 378.6541 | NaN | NaN | NaN | 583.9788 | 627.37 | NaN | NaN | 1253.6713 | NaN | NaN | NaN | NaN | 1253.8026 | 1254.3719 | NaN | 17.597 | NaN | 25.2367
9191.1292 | 752.8462 | 491.9895 | 284.1632 | 282.3581 | 294.0738 | 378.1221 | 471.3666 | 379.5293 | NaN | NaN | NaN | 574.2829 | 632.2409 | NaN | NaN | 1253.6704 | NaN | NaN | NaN | NaN | 1253.8018 | 1254.3711 | NaN | 19.018 | NaN | 25.0817
9192.1292 | 752.951 | 492.6433 | 284.0904 | 282.7297 | 294.3936 | 377.385 | 468.4987 | 377.6602 | NaN | NaN | NaN | 584.7953 | 648.3658 | NaN | NaN | 1253.6713 | NaN | NaN | NaN | NaN | 1253.8026 | 1254.3719 | NaN | 17.5525 | NaN | 23.617
9193.1292 | 752.1507 | 494.5552 | 284.1866 | 282.6481 | 294.7449 | 379.2495 | 474.332 | 377.232 | NaN | NaN | NaN | 604.5184 | 654.3162 | NaN | NaN | 1253.6713 | NaN | NaN | NaN | NaN | 1253.8027 | 1254.372 | NaN | 16.9939 | NaN | 22.1808
9194.1292 | 752.2256 | 494.5367 | 284.1566 | 282.7715 | 295.4577 | 381.4405 | 472.7559 | 378.4106 | NaN | NaN | NaN | 620.4814 | 657.4362 | NaN | NaN | 1253.6709 | NaN | NaN | NaN | NaN | 1253.8023 | 1254.3715 | NaN | 16.228 | NaN | 24.0479
9195.1448 | 752.8238 | 494.4638 | 284.6721 | 282.5092 | 295.7199 | 381.2898 | 470.8316 | 377.2049 | NaN | NaN | NaN | 620.0935 | 661.7184 | NaN | NaN | 1253.6709 | NaN | NaN | NaN | NaN | 1253.8023 | 1254.3716 | NaN | 15.1835 | NaN | 23.1325
9196.1292 | 754.5135 | 493.6015 | 285.4677 | 282.6073 | 296.0446 | 381.7402 | 468.1247 | 375.9292 | NaN | NaN | NaN | 632.0597 | 671.3201 | NaN | NaN | 1253.6715 | NaN | NaN | NaN | NaN | 1253.8029 | 1254.3722 | NaN | 19.2081 | NaN | 23.247
9197.1292 | 753.7921 | 492.9383 | 285.1333 | 282.3723 | 296.3251 | 380.2846 | 465.5553 | 375.7927 | NaN | NaN | NaN | 638.1705 | 671.2722 | NaN | NaN | 1253.6718 | NaN | NaN | NaN | NaN | 1253.8032 | 1254.3725 | NaN | 18.4513 | NaN | 21.9446
9198.1292 | 754.5512 | 493.0152 | 285.2827 | 281.8159 | 296.2357 | 379.3253 | 464.12 | 374.5873 | NaN | NaN | NaN | 647.4682 | 682.9115 | NaN | NaN | 1253.6714 | NaN | NaN | NaN | NaN | 1253.8028 | 1254.3721 | NaN | 17.3401 | NaN | 22.3968
9199.1292 | 753.6151 | 493.614 | 285.5619 | 281.715 | 295.8457 | 378.9786 | 470.1145 | 375.3724 | NaN | NaN | NaN | 647.2789 | 682.3249 | NaN | NaN | 1253.6712 | NaN | NaN | NaN | NaN | 1253.8026 | 1254.3718 | NaN | 16.1002 | NaN | 23.6949
9200.1292 | 753.2298 | 495.6449 | 284.847 | 281.1359 | 295.6333 | 378.6686 | 472.784 | 375.6277 | NaN | NaN | NaN | 632.2046 | 693.5192 | NaN | NaN | 1253.6709 | NaN | NaN | NaN | NaN | 1253.8023 | 1254.3716 | NaN | 19.0434 | NaN | 23.2051
9201.1292 | 754.0958 | 496.5664 | 285.0879 | 280.7956 | 295.6471 | 384.8887 | 475.0978 | 375.8212 | NaN | NaN | NaN | 623.7114 | 700.829 | NaN | NaN | 1253.6712 | NaN | NaN | NaN | NaN | 1253.8026 | 1254.3718 | NaN | 18.4072 | NaN | 22.4714
9202.1292 | 754.4492 | 497.3956 | 285.5846 | 280.3779 | 295.6663 | 386.9516 | 474.0217 | 376.0208 | NaN | NaN | NaN | 644.7177 | 712.2481 | NaN | NaN | 1253.6718 | NaN | NaN | NaN | NaN | 1253.8031 | 1254.3724 | NaN | 18.445 | NaN | 24.8541
9203.1292 | 755.0486 | 498.4387 | 286.2912 | 280.2248 | 295.7572 | 387.3631 | 472.4419 | 375.3195 | NaN | NaN | NaN | 660.7256 | 719.8329 | NaN | NaN | 1253.672 | NaN | NaN | NaN | NaN | 1253.8033 | 1254.3726 | NaN | 16.9226 | NaN | 24.3992
9204.1292 | 756.1713 | 497.959 | 286.1159 | 280.6789 | 295.546 | 387.1129 | 472.0253 | 375.1037 | NaN | NaN | NaN | 666.1737 | 723.8184 | NaN | NaN | 1253.671 | NaN | NaN | NaN | NaN | 1253.8024 | 1254.3717 | NaN | 17.5977 | NaN | 23.0932
9205.1292 | 756.2316 | 498.6316 | 285.9478 | 280.7013 | 295.2128 | 386.7218 | 471.2967 | 375.2077 | NaN | NaN | NaN | 686.2048 | 727.6963 | NaN | NaN | 1253.672 | NaN | NaN | NaN | NaN | 1253.8033 | 1254.3726 | NaN | 17.7353 | NaN | 22.4728
9206.1292 | 757.6032 | 499.4731 | 285.71 | 280.6251 | 295.2137 | 385.9165 | 470.5983 | 374.9981 | NaN | NaN | NaN | 694.4529 | 737.7555 | NaN | NaN | 1253.6711 | NaN | NaN | NaN | NaN | 1253.8025 | 1254.3718 | NaN | 16.0661 | NaN | 24.151
9207.1292 | 756.5278 | 500.2148 | 286.1029 | 280.5425 | 294.8964 | 386.4983 | 471.046 | 374.914 | NaN | NaN | NaN | 673.5514 | 735.6662 | NaN | NaN | 1253.6712 | NaN | NaN | NaN | NaN | 1253.8026 | 1254.3719 | NaN | 18.528 | NaN | 23.8652
9208.1292 | 756.657 | 500.8486 | 285.8762 | 281.3044 | 295.151 | 385.5285 | 468.3406 | 373.3338 | NaN | NaN | NaN | 686.4794 | 745.9902 | NaN | NaN | 1253.6712 | NaN | NaN | NaN | NaN | 1253.8026 | 1254.3718 | NaN | 18.3157 | NaN | 23.9231
9209.1292 | 756.2097 | 501.1393 | 285.861 | 281.5645 | 294.9805 | 385.9005 | 465.9083 | 372.3158 | NaN | NaN | NaN | 686.2573 | 752.5955 | NaN | NaN | 1253.6709 | NaN | NaN | NaN | NaN | 1253.8023 | 1254.3716 | NaN | 15.6143 | NaN | 24.5835
9210.1292 | 755.0642 | 501.11 | 285.5577 | 281.4703 | 295.7875 | 385.1947 | 466.0178 | 371.089 | NaN | NaN | NaN | 690.1246 | 759.4821 | NaN | NaN | 1253.6721 | NaN | NaN | NaN | NaN | 1253.8035 | 1254.3728 | NaN | 16.6485 | NaN | 25.2741
9211.1292 | 753.5718 | 501.842 | 286.0424 | 282.0756 | 295.7434 | 384.789 | 466.8777 | 369.9073 | NaN | NaN | NaN | 702.3169 | 762.104 | NaN | NaN | 1253.6717 | NaN | NaN | NaN | NaN | 1253.8031 | 1254.3724 | NaN | 18.5854 | NaN | 23.3943
9212.1292 | 753.7214 | 503.7861 | 286.1672 | 282.531 | 295.9389 | 386.7435 | 478.6761 | 372.288 | NaN | NaN | NaN | 690.1514 | 766.569 | NaN | NaN | 1253.6713 | NaN | NaN | NaN | NaN | 1253.8027 | 1254.372 | NaN | 15.481 | NaN | 24.3579
9213.1292 | 755.0402 | 505.6494 | 285.8435 | 282.2397 | 296.2885 | 390.8309 | 488.8118 | 371.8879 | NaN | NaN | NaN | 703.9414 | 770.7429 | NaN | NaN | 1253.6721 | NaN | NaN | NaN | NaN | 1253.8035 | 1254.3727 | NaN | 17.0797 | NaN | 23.6964
9214.1292 | 753.3195 | 506.0324 | 285.6873 | 282.3448 | 295.8233 | 392.9724 | 490.3591 | 371.3515 | NaN | NaN | NaN | 692.5326 | 775.4451 | NaN | NaN | 1253.6719 | NaN | NaN | NaN | NaN | 1253.8033 | 1254.3725 | NaN | 17.9634 | NaN | 25.2521
9215.1292 | 749.2661 | 505.8623 | 285.9474 | 283.3085 | 295.6921 | 392.3199 | 486.9139 | 370.5642 | NaN | NaN | NaN | 681.1676 | 782.5356 | NaN | NaN | 1253.6709 | NaN | NaN | NaN | NaN | 1253.8023 | 1254.3716 | NaN | 15.7053 | NaN | 23.2158
9216.1292 | 745.2464 | 506.5168 | 286.5225 | 283.8732 | 295.9554 | 393.4532 | 483.8077 | 368.3371 | NaN | NaN | NaN | 667.0317 | 786.0042 | NaN | NaN | 1253.6707 | NaN | NaN | NaN | NaN | 1253.8021 | 1254.3713 | NaN | 16.1138 | NaN | 23.5188
9217.1292 | 742.1641 | 507.7521 | 286.3756 | 284.0817 | 295.603 | 396.6299 | 479.6347 | 367.0069 | NaN | NaN | NaN | 663.3279 | 792.5284 | NaN | NaN | 1253.6713 | NaN | NaN | NaN | NaN | 1253.8027 | 1254.372 | NaN | 18.4912 | NaN | 24.0655
9218.1292 | 741.7545 | 508.2033 | 287.4327 | 283.902 | 295.2163 | 402.3628 | 479.6767 | 366.2578 | NaN | NaN | NaN | 674.7735 | 799.7343 | NaN | NaN | 1253.671 | NaN | NaN | NaN | NaN | 1253.8024 | 1254.3717 | NaN | 18.2267 | NaN | 24.3272
9219.1292 | 743.0728 | 508.8598 | 288.8071 | 283.3943 | 295.4833 | 407.2586 | 484.2459 | 366.4571 | NaN | NaN | NaN | 695.7587 | 809.9848 | NaN | NaN | 1253.6709 | NaN | NaN | NaN | NaN | 1253.8023 | 1254.3716 | NaN | 19.7714 | NaN | 24.6218
9220.1292 | 742.8597 | 509.7147 | 288.985 | 283.9086 | 295.4823 | 411.9793 | 490.6992 | 367.4718 | NaN | NaN | NaN | 685.1494 | 806.5824 | NaN | NaN | 1253.6717 | NaN | NaN | NaN | NaN | 1253.8031 | 1254.3723 | NaN | 18.3597 | NaN | 23.6325
9221.1292 | 742.2068 | 510.9176 | 289.4382 | 284.7473 | 295.8425 | 415.5155 | 495.1983 | 367.3325 | NaN | NaN | NaN | 678.5901 | 809.9841 | NaN | NaN | 1253.6721 | NaN | NaN | NaN | NaN | 1253.8035 | 1254.3727 | NaN | 15.7191 | NaN | 23.454
9222.1292 | 741.2857 | 509.8196 | 290.1114 | 285.0957 | 296.1716 | 416.1065 | 495.9002 | 367.6925 | NaN | NaN | NaN | 702.9341 | 821.899 | NaN | NaN | 1253.6721 | NaN | NaN | NaN | NaN | 1253.8035 | 1254.3728 | NaN | 16.3819 | NaN | 24.6295
9223.1292 | 740.5986 | 510.2829 | 289.6145 | 285.7571 | 297.2392 | 414.6246 | 491.6062 | 366.488 | NaN | NaN | NaN | 709.6588 | 825.7185 | NaN | NaN | 1253.671 | NaN | NaN | NaN | NaN | 1253.8024 | 1254.3717 | NaN | 18.4831 | NaN | 23.5978
9224.1292 | 739.8691 | 509.8521 | 290.4598 | 286.046 | 297.257 | 413.3832 | 488.3452 | 365.3096 | NaN | NaN | NaN | 703.5866 | 829.5101 | NaN | NaN | 1253.6713 | NaN | NaN | NaN | NaN | 1253.8027 | 1254.372 | NaN | 16.7165 | NaN | 22.7083
9225.1292 | 739.5069 | 509.2191 | 290.0419 | 286.2292 | 297.2079 | 413.2708 | 484.6296 | 364.3397 | NaN | NaN | NaN | 714.9091 | 838.1691 | NaN | NaN | 1253.6718 | NaN | NaN | NaN | NaN | 1253.8032 | 1254.3725 | NaN | 17.1083 | NaN | 25.3139
9226.1292 | 739.525 | 509.3728 | 289.8286 | 286.1963 | 296.9679 | 413.4219 | 482.3725 | 364.6951 | NaN | NaN | NaN | 706.7008 | 838.9981 | NaN | NaN | 1253.672 | NaN | NaN | NaN | NaN | 1253.8034 | 1254.3727 | NaN | 18.7643 | NaN | 25.7872
9227.1292 | 740.1641 | 510.6997 | 289.7175 | 286.115 | 296.8915 | 422.8863 | 490.3598 | 364.6998 | NaN | NaN | NaN | 703.0929 | 847.442 | NaN | NaN | 1253.671 | NaN | NaN | NaN | NaN | 1253.8024 | 1254.3717 | NaN | 15.5084 | NaN | 24.461
9228.1292 | 739.3761 | 509.82 | 289.3231 | 285.9801 | 296.7128 | 423.1318 | 486.4311 | 365.832 | NaN | NaN | NaN | 699.3179 | 853.1614 | NaN | NaN | 1253.6716 | NaN | NaN | NaN | NaN | 1253.803 | 1254.3723 | NaN | 15.8404 | NaN | 24.8036
9229.1292 | 740.1824 | 509.0499 | 289.4445 | 285.8591 | 296.9361 | 421.391 | 482.3948 | 366.3001 | NaN | NaN | NaN | 708.8854 | 859.9962 | NaN | NaN | 1253.6722 | NaN | NaN | NaN | NaN | 1253.8036 | 1254.3729 | NaN | 16.8705 | NaN | 23.7691
9230.1292 | 741.1044 | 509.0908 | 289.2975 | 286.7532 | 296.933 | 420.1876 | 480.1626 | 366.5903 | NaN | NaN | NaN | 718.0574 | 862.2115 | NaN | NaN | 1253.6718 | NaN | NaN | NaN | NaN | 1253.8032 | 1254.3725 | NaN | 15.0654 | NaN | 25.3839
9231.1292 | 741.3289 | 510.5067 | 288.7161 | 287.0336 | 296.91 | 422.8974 | 489.9725 | 369.8931 | NaN | NaN | NaN | 703.8113 | 861.8075 | NaN | NaN | 1253.6716 | NaN | NaN | NaN | NaN | 1253.803 | 1254.3723 | NaN | 16.6049 | NaN | 23.381
9232.1292 | 742.9274 | 512.6866 | 288.3122 | 286.6506 | 297.7028 | 422.7775 | 491.3148 | 372.0792 | NaN | NaN | NaN | 670.9075 | 865.8336 | NaN | NaN | 1253.6721 | NaN | NaN | NaN | NaN | 1253.8035 | 1254.3728 | NaN | 16.5973 | NaN | 23.5127
9233.1292 | 743.017 | 512.5506 | 289.0835 | 286.7578 | 298.2749 | 421.658 | 490.197 | 373.228 | NaN | NaN | NaN | 652.054 | 870.6401 | NaN | NaN | 1253.6713 | NaN | NaN | NaN | NaN | 1253.8027 | 1254.372 | NaN | 16.1163 | NaN | 23.704
9234.1292 | 743.5416 | 513.9526 | 289.4633 | 286.7813 | 298.2879 | 421.1137 | 488.2767 | 373.7324 | NaN | NaN | NaN | 639.8007 | 876.5048 | NaN | NaN | 1253.672 | NaN | NaN | NaN | NaN | 1253.8034 | 1254.3727 | NaN | 16.8094 | NaN | 23.2733
9235.1292 | 743.3807 | 514.1568 | 290.013 | 286.4817 | 298.5701 | 422.5229 | 491.4025 | 374.3817 | NaN | NaN | NaN | 629.3136 | 881.1398 | NaN | NaN | 1253.6715 | NaN | NaN | NaN | NaN | 1253.8029 | 1254.3722 | NaN | 15.7589 | NaN | 24.9226
9236.1292 | 744.7017 | 514.3526 | 290.0681 | 286.2078 | 298.9733 | 420.9859 | 492.8007 | 376.8217 | NaN | NaN | NaN | 608.2984 | 886.4336 | NaN | NaN | 1253.6722 | NaN | NaN | NaN | NaN | 1253.8036 | 1254.3729 | NaN | 14.7434 | NaN | 23.5835
9237.1292 | 745.1274 | 514.2066 | 290.8459 | 285.499 | 299.1573 | 419.9456 | 494.8519 | 380.324 | NaN | NaN | NaN | 586.6441 | 891.1762 | NaN | NaN | 1253.6716 | NaN | NaN | NaN | NaN | 1253.8029 | 1254.3722 | NaN | 18.341 | NaN | 23.604
9238.1292 | 745.6263 | 513.9375 | 291.7307 | 285.6929 | 299.5721 | 418.6378 | 495.6431 | 381.9072 | NaN | NaN | NaN | 589.9159 | 899.3552 | NaN | NaN | 1253.6716 | NaN | NaN | NaN | NaN | 1253.803 | 1254.3723 | NaN | 15.6278 | NaN | 22.0762
9239.1292 | 745.0466 | 513.9753 | 292.3737 | 285.6304 | 300.0459 | 417.1206 | 495.0942 | 383.1037 | NaN | NaN | NaN | 572.4088 | 902.9547 | NaN | NaN | 1253.6712 | NaN | NaN | NaN | NaN | 1253.8026 | 1254.3719 | NaN | 18.1784 | NaN | 22.6552
9240.1292 | 744.1925 | 514.5949 | 292.916 | 285.6175 | 300.5188 | 416.1939 | 498.2148 | 383.2465 | NaN | NaN | NaN | 556.3042 | 907.7958 | NaN | NaN | 1253.6713 | NaN | NaN | NaN | NaN | 1253.8027 | 1254.372 | NaN | 15.0027 | NaN | 23.6023
9241.1292 | 744.0201 | 513.7113 | 293.3391 | 285.7118 | 300.452 | 415.6541 | 494.9675 | 381.6596 | NaN | NaN | NaN | 545.8723 | 912.7054 | NaN | NaN | 1253.672 | NaN | NaN | NaN | NaN | 1253.8034 | 1254.3727 | NaN | 18.9259 | NaN | 24.5122
9242.1292 | 744.4612 | 511.7755 | 292.9266 | 285.3006 | 300.0278 | 412.7417 | 490.9418 | 382.2021 | NaN | NaN | NaN | 550.5286 | 918.7076 | NaN | NaN | 1253.6726 | NaN | NaN | NaN | NaN | 1253.804 | 1254.3733 | NaN | 18.8525 | NaN | 23.6461
9243.1292 | 743.0349 | 510.7414 | 291.5685 | 286.2266 | 300.1714 | 409.2861 | 486.3415 | 382.0151 | NaN | NaN | NaN | 540.319 | 923.9496 | NaN | NaN | 1253.6713 | NaN | NaN | NaN | NaN | 1253.8026 | 1254.3719 | NaN | 16.4104 | NaN | 25.0832
9244.1292 | 741.1023 | 509.6074 | 291.1596 | 286.5607 | 300.4274 | 406.2523 | 482.6961 | 380.7971 | NaN | NaN | NaN | 550.0189 | 929.7893 | NaN | NaN | 1253.6712 | NaN | NaN | NaN | NaN | 1253.8026 | 1254.3719 | NaN | 18.7273 | NaN | 23.8778
9245.1292 | 740.5581 | 508.8034 | 290.8238 | 286.6798 | 300.5529 | 403.4618 | 479.6148 | 381.333 | NaN | NaN | NaN | 550.9541 | 935.6761 | NaN | NaN | 1253.6708 | NaN | NaN | NaN | NaN | 1253.8022 | 1254.3715 | NaN | 16.9273 | NaN | 23.1196
9246.1292 | 739.2933 | 507.903 | 290.6133 | 286.3945 | 300.8844 | 400.4426 | 475.4743 | 380.7819 | NaN | NaN | NaN | 564.4344 | 944.3194 | NaN | NaN | 1253.6712 | NaN | NaN | NaN | NaN | 1253.8026 | 1254.3718 | NaN | 16.1731 | NaN | 24.7857
9247.1292 | 737.3125 | 506.3181 | 290.1434 | 287.0063 | 300.9008 | 397.1991 | 471.3047 | 380.2979 | NaN | NaN | NaN | 584.0684 | 950.1176 | NaN | NaN | 1253.671 | NaN | NaN | NaN | NaN | 1253.8024 | 1254.3717 | NaN | 15.6272 | NaN | 24.0241
9248.1292 | 735.7663 | 506.6654 | 290.2983 | 287.0337 | 300.4772 | 394.523 | 467.8688 | 381.9473 | NaN | NaN | NaN | 576.5224 | 952.4715 | NaN | NaN | 1253.6719 | NaN | NaN | NaN | NaN | 1253.8033 | 1254.3726 | NaN | 17.6125 | NaN | 22.9859
9249.1292 | 735.1705 | 508.4684 | 290.2566 | 286.8466 | 300.2255 | 392.8344 | 468.369 | 386.5276 | NaN | NaN | NaN | 557.5513 | 956.6794 | NaN | NaN | 1253.6716 | NaN | NaN | NaN | NaN | 1253.803 | 1254.3723 | NaN | 17.478 | NaN | 24.8105
9250.1292 | 735.4477 | 511.7799 | 289.9828 | 286.6166 | 300.6894 | 393.7177 | 477.241 | 391.8861 | NaN | NaN | NaN | 560.0163 | 968.4033 | NaN | NaN | 1253.6718 | NaN | NaN | NaN | NaN | 1253.8031 | 1254.3724 | NaN | 18.6278 | NaN | 24.2721
9251.1292 | 736.2578 | 511.5093 | 289.8217 | 287.273 | 300.3289 | 396.0561 | 480.1118 | 392.1401 | NaN | NaN | NaN | 575.9945 | 973.7781 | NaN | NaN | 1253.6712 | NaN | NaN | NaN | NaN | 1253.8026 | 1254.3719 | NaN | 18.301 | NaN | 23.0596
9252.1292 | 736.9518 | 512.1815 | 290.4026 | 288.0024 | 301.1863 | 399.8116 | 482.6277 | 390.1328 | NaN | NaN | NaN | 559.7667 | 975.5252 | NaN | NaN | 1253.6711 | NaN | NaN | NaN | NaN | 1253.8024 | 1254.3717 | NaN | 17.4401 | NaN | 24.9904
9253.1292 | 737.6505 | 512.4269 | 291.188 | 289.0402 | 301.6208 | 403.8555 | 485.6421 | 391.807 | NaN | NaN | NaN | 575.955 | 982.5632 | NaN | NaN | 1253.6724 | NaN | NaN | NaN | NaN | 1253.8038 | 1254.3731 | NaN | 19.5194 | NaN | 24.8962
9254.1292 | 737.7114 | 512.3809 | 291.8213 | 288.8012 | 301.376 | 403.927 | 489.7025 | 391.7931 | NaN | NaN | NaN | 598.9807 | 990.278 | NaN | NaN | 1253.671 | NaN | NaN | NaN | NaN | 1253.8024 | 1254.3717 | NaN | 18.8252 | NaN | 23.9565
9255.1292 | 739.8146 | 511.9109 | 292.8985 | 289.2661 | 301.7946 | 404.4949 | 490.7879 | 392.5691 | NaN | NaN | NaN | 582.788 | 994.5576 | NaN | NaN | 1253.6721 | NaN | NaN | NaN | NaN | 1253.8035 | 1254.3728 | NaN | 18.0589 | NaN | 23.2293
9256.1292 | 740.1647 | 512.0442 | 293.6656 | 289.656 | 301.9575 | 404.795 | 490.6307 | 392.1446 | NaN | NaN | NaN | 603.4549 | 994.0165 | NaN | NaN | 1253.6712 | NaN | NaN | NaN | NaN | 1253.8026 | 1254.3718 | NaN | 16.8244 | NaN | 24.4422
9257.1292 | 741.1357 | 511.4445 | 294.0801 | 290.1811 | 302.4081 | 406.4394 | 493.2572 | 393.272 | NaN | NaN | NaN | 585.5112 | 996.9229 | NaN | NaN | 1253.6714 | NaN | NaN | NaN | NaN | 1253.8028 | 1254.372 | NaN | 16.8481 | NaN | 23.5019
9258.1292 | 742.9259 | 512.0511 | 294.6601 | 289.9677 | 303.2419 | 405.5278 | 492.768 | 392.5169 | NaN | NaN | NaN | 585.6288 | 999.8956 | NaN | NaN | 1253.6709 | NaN | NaN | NaN | NaN | 1253.8023 | 1254.3715 | NaN | 17.5058 | NaN | 25.1261
9259.1292 | 742.8154 | 512.4532 | 294.4793 | 289.8155 | 303.2997 | 406.0737 | 495.3084 | 392.9307 | NaN | NaN | NaN | 574.5907 | 1000.1633 | NaN | NaN | 1253.6715 | NaN | NaN | NaN | NaN | 1253.8029 | 1254.3722 | NaN | 18.6002 | NaN | 23.145
9260.1292 | 741.7512 | 511.9767 | 293.7454 | 289.2381 | 303.0415 | 405.3399 | 492.3236 | 390.8858 | NaN | NaN | NaN | 574.8441 | 1007.2168 | NaN | NaN | 1253.6712 | NaN | NaN | NaN | NaN | 1253.8026 | 1254.3718 | NaN | 18.1097 | NaN | 24.3221
9261.1292 | 742.5793 | 512.5495 | 294.0186 | 289.2461 | 302.8677 | 407.338 | 491.8423 | 390.1987 | NaN | NaN | NaN | 561.1537 | 1012.9477 | NaN | NaN | 1253.6719 | NaN | NaN | NaN | NaN | 1253.8033 | 1254.3725 | NaN | 17.6862 | NaN | 25.1187
9262.1292 | 742.3739 | 512.6304 | 293.7688 | 289.9811 | 303.0628 | 407.4199 | 489.1024 | 388.9967 | NaN | NaN | NaN | 543.8356 | 1017.9726 | NaN | NaN | 1253.6711 | NaN | NaN | NaN | NaN | 1253.8025 | 1254.3718 | NaN | 19.3205 | NaN | 23.1849
9263.1292 | 740.9476 | 513.6972 | 294.3409 | 291.1505 | 303.4078 | 407.9296 | 488.8183 | 388.7412 | NaN | NaN | NaN | 529.3467 | 1021.8168 | NaN | NaN | 1253.6711 | NaN | NaN | NaN | NaN | 1253.8024 | 1254.3717 | NaN | 18.5663 | NaN | 24.8983
9264.1292 | 740.9537 | 513.7543 | 294.33 | 290.3132 | 303.3023 | 409.6195 | 484.9975 | 386.4193 | NaN | NaN | NaN | 555.6608 | 1032.8331 | NaN | NaN | 1253.6713 | NaN | NaN | NaN | NaN | 1253.8026 | 1254.3719 | NaN | 17.6567 | NaN | 20.9886
9265.1292 | 740.6397 | 513.9446 | 295.0702 | 289.6969 | 303.3832 | 415.4686 | 481.6596 | 384.6977 | NaN | NaN | NaN | 608.0664 | 1043.0866 | NaN | NaN | 1253.6715 | NaN | NaN | NaN | NaN | 1253.8029 | 1254.3722 | NaN | 18.101 | NaN | 26.4048
9266.1292 | 739.8925 | 513.5444 | 295.1613 | 289.772 | 303.0527 | 416.534 | 482.0158 | 383.5472 | NaN | NaN | NaN | 623.9846 | 1048.5842 | NaN | NaN | 1253.6711 | NaN | NaN | NaN | NaN | 1253.8025 | 1254.3718 | NaN | 19.4228 | NaN | 25.4684
9267.1292 | 738.9269 | 512.8412 | 296.0824 | 290.2133 | 303.6596 | 415.8762 | 478.8147 | 382.8713 | NaN | NaN | NaN | 622.0147 | 1048.5292 | NaN | NaN | 1253.6712 | NaN | NaN | NaN | NaN | 1253.8026 | 1254.3719 | NaN | 19.1525 | NaN | 24.7607
9268.1292 | 738.1928 | 513.2922 | 295.2078 | 291.0531 | 303.274 | 414.7139 | 475.4723 | 382.0817 | NaN | NaN | NaN | 602.5228 | 1053.0772 | NaN | NaN | 1253.6713 | NaN | NaN | NaN | NaN | 1253.8026 | 1254.3719 | NaN | 17.9557 | NaN | 25.1241
9269.1292 | 737.9344 | 513.3989 | 295.0083 | 291.177 | 303.3876 | 415.1406 | 474.3897 | 380.1513 | NaN | NaN | NaN | 593.2128 | 1059.5601 | NaN | NaN | 1253.6721 | NaN | NaN | NaN | NaN | 1253.8035 | 1254.3728 | NaN | 17.4513 | NaN | 22.4687
9270.1292 | 736.1672 | 512.5172 | 294.4079 | 290.7813 | 302.8876 | 415.3784 | 472.9639 | 379.6889 | NaN | NaN | NaN | 606.4009 | 1070.2009 | NaN | NaN | 1253.6713 | NaN | NaN | NaN | NaN | 1253.8026 | 1254.3719 | NaN | 18.1872 | NaN | 23.8062
9271.1292 | 735.368 | 512.9456 | 294.5516 | 290.3134 | 302.4281 | 414.3724 | 470.1691 | 379.5331 | NaN | NaN | NaN | 626.151 | 1083.1953 | NaN | NaN | 1253.6703 | NaN | NaN | NaN | NaN | 1253.8017 | 1254.371 | NaN | 17.0936 | NaN | 24.803
9272.1292 | 735.4431 | 513.0468 | 294.6426 | 290.3169 | 302.362 | 414.5542 | 468.5691 | 378.2834 | NaN | NaN | NaN | 648.3302 | 1091.5109 | NaN | NaN | 1253.6715 | NaN | NaN | NaN | NaN | 1253.8029 | 1254.3722 | NaN | 17.9985 | NaN | 23.6366
9273.1292 | 735.9867 | 512.9363 | 295.1884 | 290.1543 | 302.5954 | 412.8136 | 466.6699 | 378.0065 | NaN | NaN | NaN | 657.1593 | 1097.3861 | NaN | NaN | 1253.6708 | NaN | NaN | NaN | NaN | 1253.8021 | 1254.3714 | NaN | 17.4405 | NaN | 23.6913
9274.1292 | 737.2075 | 512.422 | 295.7147 | 289.9508 | 303.355 | 411.7484 | 462.9215 | 377.3882 | NaN | NaN | NaN | 645.7113 | 1098.9858 | NaN | NaN | 1253.6708 | NaN | NaN | NaN | NaN | 1253.8022 | 1254.3715 | NaN | 53.8983 | NaN | 24.1873
9275.1292 | 739.3765 | 511.4378 | 295.8098 | 289.8776 | 303.425 | 409.7307 | 462.3025 | 378.4541 | NaN | NaN | NaN | 645.1099 | 1099.0235 | NaN | NaN | 1253.6712 | NaN | NaN | NaN | NaN | 1253.8026 | 1254.3719 | NaN | 16.4647 | NaN | 23.0317
9276.1292 | 740.9594 | 511.0022 | 295.7745 | 289.758 | 303.29 | 408.827 | 461.0062 | 379.0548 | NaN | NaN | NaN | 652.1853 | 1111.6841 | NaN | NaN | 1253.6712 | NaN | NaN | NaN | NaN | 1253.8026 | 1254.3718 | NaN | 14.3078 | NaN | 21.999
9277.1292 | 741.3832 | 509.6332 | 295.7064 | 289.7479 | 302.7354 | 407.9754 | 460.1929 | 379.3709 | NaN | NaN | NaN | 651.2802 | 1117.3245 | NaN | NaN | 1253.6718 | NaN | NaN | NaN | NaN | 1253.8032 | 1254.3725 | NaN | -4.0591 | NaN | 27.9897
9278.1292 | 740.9949 | 510.3839 | 295.6289 | 289.4226 | 302.7463 | 407.4714 | 463.9437 | 379.0491 | NaN | NaN | NaN | 650.0285 | 1118.1687 | NaN | NaN | 1253.6714 | NaN | NaN | NaN | NaN | 1253.8028 | 1254.372 | NaN | 28.0977 | NaN | 25.4869
9279.1292 | 742.7988 | 510.9894 | 295.6639 | 289.9193 | 303.1598 | 408.508 | 465.867 | 378.3414 | NaN | NaN | NaN | 662.3099 | 1120.9326 | NaN | NaN | 1253.6716 | NaN | NaN | NaN | NaN | 1253.803 | 1254.3723 | NaN | 60.0152 | NaN | 16.5835
9280.1292 | 744.2712 | 511.3622 | 295.4154 | 290.5932 | 302.761 | 409.1235 | 469.8469 | 378.6776 | NaN | NaN | NaN | 667.5414 | 1127.9826 | NaN | NaN | 1253.6711 | NaN | NaN | NaN | NaN | 1253.8025 | 1254.3718 | NaN | 16.2611 | NaN | 19.5354
9281.1292 | 745.3476 | 510.972 | 295.0986 | 290.4314 | 302.8579 | 406.9985 | 469.3515 | 378.6231 | NaN | NaN | NaN | 676.1128 | 1131.1715 | NaN | NaN | 1253.6707 | NaN | NaN | NaN | NaN | 1253.8021 | 1254.3714 | NaN | 42.4866 | NaN | 18.7658
9282.1292 | 746.8814 | 510.2891 | 295.3744 | 290.9261 | 302.6291 | 405.1997 | 468.8459 | 379.1829 | NaN | NaN | NaN | 680.6688 | 1130.4179 | NaN | NaN | 1253.6715 | NaN | NaN | NaN | NaN | 1253.8028 | 1254.3721 | NaN | 37.1374 | NaN | 22.1504
9283.1292 | 747.194 | 509.4468 | 295.4536 | 290.9388 | 302.5964 | 403.6769 | 468.7217 | 378.7195 | NaN | NaN | NaN | 664.9152 | 1129.4306 | NaN | NaN | 1253.6709 | NaN | NaN | NaN | NaN | 1253.8023 | 1254.3715 | NaN | 2.2649 | NaN | 22.1532
9284.1292 | 745.1422 | 508.4176 | 294.9419 | 290.9593 | 302.8431 | 401.2611 | 466.2785 | 378.7459 | NaN | NaN | NaN | 640.8582 | 1131.8101 | NaN | NaN | 1253.6706 | NaN | NaN | NaN | NaN | 1253.802 | 1254.3713 | NaN | -5.9282 | NaN | 38.5219
9285.1292 | 744.7093 | 509.5627 | 294.8577 | 291.174 | 303.002 | 399.7974 | 463.1905 | 379.3155 | NaN | NaN | NaN | 645.4962 | 1139.0503 | NaN | NaN | 1253.6703 | NaN | NaN | NaN | NaN | 1253.8017 | 1254.371 | NaN | -0.2572 | NaN | 23.859
9286.1292 | 744.5905 | 509.6066 | 294.6924 | 291.0837 | 302.8808 | 399.0745 | 463.2189 | 381.1082 | NaN | NaN | NaN | 643.7621 | 1145.1336 | NaN | NaN | 1253.6704 | NaN | NaN | NaN | NaN | 1253.8018 | 1254.371 | NaN | NaN | NaN | 23.3868
9287.1292 | 745.1855 | 510.0173 | 294.6554 | 290.1292 | 303.1283 | 398.5147 | 464.5805 | 382.582 | NaN | NaN | NaN | 634.4465 | 1157.5791 | NaN | NaN | 1253.6716 | NaN | NaN | NaN | NaN | 1253.8029 | 1254.3722 | NaN | NaN | NaN | 17.1338
9288.1292 | 745.1916 | 510.7181 | 294.4698 | 290.2444 | 302.7812 | 397.684 | 464.0203 | 382.9666 | NaN | NaN | NaN | 630.3335 | 1155.5185 | NaN | NaN | 1253.6708 | NaN | NaN | NaN | NaN | 1253.8022 | 1254.3715 | NaN | 19.088 | NaN | 19.8842
9289.1292 | 744.2085 | 511.8626 | 293.8378 | 290.2742 | 302.9431 | 399.1008 | 468.4654 | 382.2407 | NaN | NaN | NaN | 614.5533 | 1254.9421 | NaN | NaN | 1253.6715 | NaN | NaN | NaN | NaN | 1253.8028 | 1254.3721 | NaN | 23.3833 | NaN | -12.0989
9290.1292 | 744.3222 | 511.5088 | 294.1751 | 291.0458 | 303.0753 | 397.9655 | 468.4236 | 381.652 | NaN | NaN | NaN | 602.1516 | 1254.9421 | NaN | NaN | 1253.6714 | NaN | NaN | NaN | NaN | 1253.8028 | 1254.372 | NaN | 36.8888 | NaN | 31.6477
9291.1292 | 745.1535 | 512.5369 | 295.4139 | 291.2825 | 303.2848 | 398.3331 | 470.3094 | 381.6691 | NaN | NaN | NaN | 611.4776 | 1254.943 | NaN | NaN | 1253.6723 | NaN | NaN | NaN | NaN | 1253.8037 | 1254.373 | NaN | 18.7138 | NaN | 14.4316
9292.1292 | 745.5311 | 512.2899 | 295.4837 | 291.7547 | 303.2184 | 399.038 | 472.8867 | 383.0238 | NaN | NaN | NaN | 607.7901 | 1254.9425 | NaN | NaN | 1253.6718 | NaN | NaN | NaN | NaN | 1253.8032 | 1254.3725 | NaN | -15.1788 | NaN | NaN
9293.1292 | 744.7852 | 512.0349 | 294.7695 | 291.8655 | 303.3336 | 399.2875 | 471.5609 | 382.67 | NaN | NaN | NaN | 616.1748 | 1254.9416 | NaN | NaN | 1253.6709 | NaN | NaN | NaN | NaN | 1253.8023 | 1254.3715 | NaN | 35.5487 | NaN | 20.8443
9294.1292 | 743.6747 | 511.5346 | 294.5635 | 292.1059 | 303.2966 | 399.0894 | 470.4077 | 381.2917 | NaN | NaN | NaN | 607.5028 | 1254.9413 | NaN | NaN | 1253.6706 | NaN | NaN | NaN | NaN | 1253.8019 | 1254.3712 | NaN | NaN | NaN | 23.4099
9295.1292 | 743.7325 | 511.198 | 294.7602 | 292.0235 | 303.2236 | 398.8574 | 469.0725 | 380.7391 | NaN | NaN | NaN | 619.9732 | 1254.9409 | NaN | NaN | 1253.6702 | NaN | NaN | NaN | NaN | 1253.8016 | 1254.3708 | NaN | 47.9703 | NaN | 24.7818
9296.1292 | 743.593 | 511.2071 | 294.7354 | 293.0237 | 303.341 | 398.2005 | 467.8253 | 379.8468 | NaN | NaN | 1170.8252 | 617.7891 | 57.1457 | NaN | NaN | 1079.3556 | NaN | NaN | NaN | NaN | 1182.1851 | NaN | NaN | NaN | NaN | 18.5392
9297.1292 | 742.5295 | 511.0459 | 294.3398 | 292.9746 | 302.8613 | 398.2697 | 468.7426 | 379.9071 | NaN | NaN | NaN | 624.9368 | 317.5722 | NaN | NaN | 828.0318 | -7.01 | NaN | NaN | NaN | 956.7743 | NaN | NaN | 40.8539 | NaN | 27.7253
9298.1292 | 742.6274 | 511.0283 | 294.633 | 293.5507 | 303.0627 | 398.3753 | 468.5658 | 380.815 | NaN | NaN | NaN | 617.0916 | 329.6547 | NaN | NaN | 884.2899 | NaN | NaN | NaN | NaN | 1061.5799 | 7.6164 | NaN | 59.571 | NaN | 26.4493
9299.1292 | 743.6667 | 510.7747 | 294.1493 | 293.4711 | 302.9491 | 397.883 | 467.639 | 381.7454 | NaN | NaN | NaN | 646.9379 | 313.6535 | NaN | 131.5453 | 409.6692 | -3.2232 | NaN | 164.4014 | NaN | 281.0157 | NaN | NaN | 13.1325 | NaN | 10.9336
9300.1292 | 743.6661 | 510.6503 | 294.3867 | 294.0065 | 303.06 | 397.97 | 467.2877 | 382.3033 | NaN | NaN | NaN | 649.0145 | 354.8124 | NaN | 213.6836 | 488.9808 | NaN | NaN | NaN | NaN | 520.1093 | NaN | NaN | 7.7973 | NaN | 35.4595
9301.1292 | 744.7344 | 511.0119 | 293.9325 | 294.6661 | 303.3654 | 397.2124 | 465.1318 | 380.335 | NaN | NaN | NaN | 634.7966 | 388.4753 | NaN | 285.8491 | 559.6282 | NaN | NaN | NaN | NaN | 607.4761 | -11.278 | NaN | 39.5352 | NaN | 33.9194
9302.1292 | 746.2234 | 511.4083 | 294.0851 | 294.9871 | 303.7252 | 396.4461 | 464.7615 | 381.2443 | NaN | NaN | NaN | 632.2554 | 402.4799 | NaN | 341.0068 | 605.8518 | 127.4149 | NaN | NaN | NaN | 656.0248 | 23.5725 | NaN | 15.0964 | NaN | 23.3817
9303.1292 | 746.4749 | 511.3218 | 293.5355 | 294.7312 | 303.8961 | 396.5048 | 464.1214 | 382.5088 | NaN | NaN | NaN | 646.2843 | 432.0014 | NaN | 385.2491 | 664.4694 | 651.2616 | NaN | NaN | NaN | 718.734 | 53.3369 | NaN | 14.9765 | NaN | 23.8558
9304.1292 | 746.344 | 510.9018 | 293.6378 | 295.1471 | 304.619 | 396.0135 | 465.315 | 383.9212 | NaN | NaN | NaN | 639.301 | 456.9997 | NaN | 432.5276 | 718.8544 | NaN | NaN | NaN | NaN | 774.6717 | 79.3306 | NaN | 18.3226 | NaN | 23.4887
9305.1292 | 746.5938 | 511.8382 | 294.1132 | 296.2722 | 304.7845 | 394.5776 | 468.9577 | 385.422 | NaN | NaN | NaN | 629.6262 | 483.2905 | NaN | 482.1802 | 773.3626 | NaN | NaN | NaN | NaN | 831.1021 | 100.2606 | NaN | 18.3314 | NaN | 24.8467
9306.1292 | 746.1256 | 513.7079 | 293.6709 | 295.5848 | 304.7095 | 394.4106 | 474.5997 | 389.1946 | NaN | NaN | NaN | 636.1588 | 506.3113 | NaN | 522.5987 | 825.1328 | NaN | NaN | NaN | NaN | 883.1523 | 122.9459 | NaN | 16.4308 | NaN | 25.0565
9307.1292 | 746.2115 | 513.8068 | 293.8624 | 295.6542 | 305.2533 | 395.0006 | 476.8063 | 391.5713 | NaN | NaN | NaN | 623.2996 | 530.2191 | NaN | 568.9887 | 876.2395 | NaN | NaN | NaN | NaN | 935.8357 | 144.9687 | NaN | 17.7312 | NaN | 25.43
9308.1292 | 747.9875 | 513.6204 | 293.6416 | 295.1132 | 305.16 | 393.9909 | 475.5733 | 389.8176 | NaN | NaN | NaN | 597.0227 | 554.4209 | NaN | 611.366 | 927.1135 | NaN | NaN | NaN | NaN | 989.1027 | 173.2291 | NaN | 15.6833 | NaN | 24.3327
9309.1292 | 748.1859 | 513.4466 | 294.413 | 295.3296 | 305.8111 | 394.5736 | 475.0434 | 390.4763 | NaN | NaN | NaN | 596.6488 | 581.595 | NaN | 642.0688 | 979.9187 | NaN | NaN | NaN | NaN | 1046.0518 | 193.5938 | NaN | 17.2125 | NaN | 24.6838
9310.1292 | 747.6565 | 514.0239 | 294.9663 | 295.5 | 305.8184 | 395.097 | 475.8775 | 390.507 | NaN | NaN | NaN | 613.6241 | 604.2817 | NaN | 670.7559 | 1028.1489 | NaN | NaN | NaN | NaN | 1098.1541 | 216.9986 | NaN | 18.1377 | NaN | 24.0699
9311.1292 | 747.2599 | 514.331 | 294.9337 | 295.4052 | 305.8477 | 396.2586 | 478.0709 | 389.5428 | NaN | NaN | NaN | 635.2753 | 630.5604 | NaN | 696.1629 | 1079.3342 | NaN | NaN | NaN | NaN | 1154.9043 | 243.314 | NaN | 16.7024 | NaN | 25.2044
9312.1292 | 747.5979 | 513.4134 | 295.0014 | 295.4344 | 305.7553 | 398.1327 | 477.1775 | 389.5955 | NaN | NaN | NaN | 629.6224 | 647.9778 | NaN | 715.6966 | 1122.8631 | NaN | NaN | NaN | NaN | 1199.8419 | 272.0333 | NaN | 16.1341 | NaN | 23.7291
9313.1292 | 746.5093 | 512.466 | 296.4713 | 296.6654 | 306.6433 | 397.805 | 476.4472 | 388.3945 | NaN | NaN | NaN | 608.0772 | 669.7693 | NaN | 735.8263 | 1171.2436 | NaN | NaN | NaN | NaN | 1250.5823 | 295.7608 | NaN | 14.241 | NaN | 23.9188
9314.1292 | 745.3494 | 511.6154 | 296.5874 | 296.3588 | 306.5596 | 398.2847 | 475.4371 | 386.2515 | NaN | NaN | NaN | 614.5898 | 695.239 | NaN | 755.7257 | 1221.9141 | NaN | NaN | NaN | NaN | 1253.8024 | 318.718 | NaN | 17.5171 | NaN | 24.4491
9315.1292 | 745.6949 | 512.7305 | 297.2959 | 295.9535 | 306.4633 | 400.2274 | 477.0356 | 385.6038 | NaN | NaN | NaN | 612.0441 | 712.404 | NaN | 770.3953 | 1253.6706 | NaN | NaN | NaN | NaN | 1253.802 | 343.004 | NaN | 18.9717 | NaN | 24.2051
9316.1292 | 746.8052 | 512.9381 | 296.9273 | 295.4651 | 306.3994 | 401.6068 | 476.9744 | 384.7984 | NaN | NaN | NaN | 616.1797 | 737.7122 | NaN | 786.0273 | 1253.6705 | NaN | NaN | NaN | NaN | 1253.8019 | 364.3311 | NaN | 17.0151 | NaN | 23.6116
9317.1292 | 747.304 | 512.9621 | 297.122 | 294.9383 | 306.0378 | 401.8786 | 475.6095 | 385.3625 | NaN | NaN | NaN | 596.6562 | 752.8811 | NaN | 798.1908 | 1253.6708 | NaN | NaN | NaN | NaN | 1253.8021 | 385.3554 | NaN | 15.3784 | NaN | 24.5723
9318.1292 | 747.7111 | 512.3479 | 297.3406 | 294.7701 | 306.6967 | 402.4588 | 473.1832 | 383.945 | NaN | NaN | NaN | 591.2015 | 771.9156 | NaN | 804.2727 | 1253.6701 | NaN | NaN | NaN | NaN | 1253.8015 | 396.978 | NaN | 17.9757 | NaN | 23.4346
9319.1292 | 748.3279 | 512.7739 | 297.2383 | 295.1224 | 306.7535 | 403.5273 | 474.9007 | 384.7436 | NaN | NaN | NaN | 598.1934 | 793.4324 | NaN | 809.2611 | 1253.6692 | NaN | NaN | NaN | NaN | 1253.8006 | 409.2435 | NaN | 16.4074 | NaN | 22.9809
9320.1292 | 749.9851 | 512.9409 | 297.3166 | 294.8997 | 307.1616 | 404.1548 | 474.0212 | 385.5172 | NaN | NaN | NaN | 620.3099 | 810.5757 | NaN | 824.8759 | 1253.6698 | NaN | NaN | NaN | NaN | 1253.8012 | 427.5066 | NaN | 18.0471 | NaN | 24.0689
9321.1448 | 750.8507 | 514.9231 | 297.9767 | 294.7599 | 307.1838 | 405.5145 | 478.1139 | 387.7692 | NaN | NaN | NaN | 626.874 | 830.0589 | NaN | 835.3651 | 1253.6703 | NaN | NaN | NaN | NaN | 1253.8017 | 445.3422 | NaN | 16.9985 | NaN | 24.0611
9322.1292 | 750.9818 | 514.65 | 298.1344 | 295.2718 | 307.3607 | 405.615 | 475.3778 | 387.4252 | NaN | NaN | NaN | 628.1232 | 845.7463 | NaN | 835.9225 | 1253.6696 | NaN | NaN | NaN | NaN | 1253.801 | 465.9513 | NaN | 18.2506 | NaN | 25.1649
9323.1292 | 750.2856 | 514.8083 | 297.7096 | 295.1829 | 307.3862 | 404.8075 | 473.9609 | 386.7021 | NaN | NaN | NaN | 603.7164 | 858.913 | NaN | 841.4598 | 1253.6702 | NaN | NaN | NaN | NaN | 1253.8016 | 493.9835 | NaN | 18.2462 | NaN | 23.0187
9324.1292 | 750.0243 | 514.4712 | 297.8003 | 295.4282 | 307.6231 | 404.1012 | 472.8844 | 386.17 | NaN | NaN | NaN | 590.49 | 874.1613 | NaN | 839.4463 | 1253.6704 | NaN | NaN | NaN | NaN | 1253.8018 | 521.7387 | NaN | 17.2051 | NaN | 23.3601
9325.1292 | 752.0066 | 513.9348 | 298.0345 | 295.8159 | 307.9525 | 406.8986 | 472.4926 | 385.9319 | NaN | NaN | NaN | 612.0092 | 901.3162 | NaN | 831.156 | 1253.669 | NaN | NaN | NaN | NaN | 1253.8004 | 548.5143 | NaN | 16.5183 | NaN | 22.7479
9326.1292 | 752.2771 | 513.809 | 297.8234 | 296.1281 | 307.875 | 408.5068 | 470.752 | 386.2078 | NaN | NaN | NaN | 618.2128 | 917.5295 | NaN | 825.4608 | 1253.6697 | NaN | NaN | NaN | NaN | 1253.8011 | 574.5177 | NaN | 18.5627 | NaN | 24.2235
9327.1292 | 750.6725 | 512.976 | 297.804 | 295.893 | 307.5171 | 408.11 | 467.6342 | 385.0339 | NaN | NaN | NaN | 626.5583 | 927.647 | NaN | 818.9154 | 1253.6697 | NaN | NaN | NaN | NaN | 1253.8011 | 603.0683 | NaN | 17.763 | NaN | 24.4969
9328.1292 | 749.603 | 512.8823 | 298.5116 | 296.0178 | 307.1534 | 407.558 | 466.5945 | 383.8977 | NaN | NaN | NaN | 601.0108 | 937.4459 | NaN | 811.9618 | 1253.6686 | NaN | NaN | NaN | NaN | 1253.8 | 628.934 | NaN | 16.7605 | NaN | 23.6328
9329.1292 | 751.1339 | 513.0987 | 298.0322 | 296.0318 | 307.3892 | 406.5519 | 466.5421 | 384.1013 | NaN | NaN | NaN | 582.5889 | 950.6602 | NaN | 804.412 | 1253.6686 | NaN | NaN | NaN | NaN | 1253.7999 | 655.5908 | NaN | 16.5727 | NaN | 23.8931
9330.1292 | 751.7848 | 513.7876 | 298.6815 | 295.7019 | 306.9526 | 407.5091 | 466.5373 | 384.5411 | NaN | NaN | NaN | 590.1368 | 969.2762 | NaN | 793.1413 | 1253.6687 | NaN | NaN | NaN | NaN | 1253.8001 | 674.7038 | NaN | 17.783 | NaN | 24.5035
9331.1292 | 751.524 | 515.2005 | 299.1568 | 295.6229 | 306.976 | 408.2177 | 467.4059 | 385.0312 | NaN | NaN | NaN | 575.1026 | 981.5358 | NaN | 780.0634 | 1253.6684 | NaN | NaN | NaN | NaN | 1253.7998 | 706.8583 | NaN | 17.7609 | NaN | 24.5232
9332.1292 | 751.6842 | 515.2845 | 298.9513 | 294.9605 | 307.1911 | 408.4766 | 467.9909 | 385.8614 | NaN | NaN | NaN | 567.2515 | 996.5809 | NaN | 760.2066 | 1253.6679 | NaN | NaN | NaN | NaN | 1253.7992 | 730.1881 | NaN | 16.1934 | NaN | 24.3313
9333.1292 | 751.7586 | 515.1162 | 299.6081 | 294.8646 | 307.8643 | 406.974 | 468.659 | 386.4673 | NaN | NaN | NaN | 549.0071 | 1009.6435 | NaN | 752.1012 | 1253.6679 | NaN | NaN | NaN | NaN | 1253.7992 | 744.3367 | NaN | 16.2655 | NaN | 25.2096
9334.1292 | 753.2309 | 515.055 | 299.6123 | 295.2926 | 308.6656 | 406.2856 | 467.319 | 386.4911 | NaN | NaN | NaN | 537.1071 | 1023.52 | NaN | 736.4516 | 1253.6687 | NaN | NaN | NaN | NaN | 1253.8001 | 769.5998 | NaN | 15.4465 | NaN | 25.191
9335.1292 | 752.0724 | 514.7846 | 299.3298 | 294.7442 | 307.8588 | 404.237 | 466.2549 | 388.8526 | NaN | NaN | NaN | 555.9149 | 1049.9421 | NaN | 730.2437 | 1253.6684 | NaN | NaN | NaN | NaN | 1253.7998 | 784.0181 | NaN | 18.0279 | NaN | 23.5702
9336.1448 | 751.6448 | 515.3221 | 299.58 | 294.8941 | 308.0915 | 401.7922 | 465.668 | 390.8802 | NaN | NaN | NaN | 567.3416 | 1061.8404 | NaN | 715.4607 | 1253.6691 | NaN | NaN | NaN | NaN | 1253.8005 | 801.1029 | NaN | 17.2748 | NaN | 24.9507
9337.1448 | 751.8984 | 517.536 | 300.1445 | 294.7308 | 308.5387 | 401.0798 | 471.3524 | 392.8671 | NaN | NaN | NaN | 559.843 | 1071.133 | NaN | 703.1021 | 1253.669 | NaN | NaN | NaN | NaN | 1253.8004 | 831.956 | NaN | 15.1593 | NaN | 24.2706
9338.1292 | 752.9472 | 517.0844 | 299.8173 | 294.9075 | 308.5252 | 401.5806 | 475.7921 | 394.2083 | NaN | NaN | NaN | 558.1014 | 1083.6038 | NaN | 689.2534 | 1253.6682 | NaN | NaN | NaN | NaN | 1253.7996 | 863.4355 | NaN | 18.8645 | NaN | 24.1323
9339.1292 | 754.246 | 516.6439 | 299.7312 | 295.7775 | 308.5362 | 405.4101 | 477.8867 | 394.0785 | NaN | NaN | NaN | 547.7891 | 1095.6172 | NaN | 672.4517 | 1253.6677 | NaN | NaN | NaN | NaN | 1253.799 | 899.5969 | NaN | 17.2111 | NaN | 25.5962
9340.1448 | 754.5378 | 516.09 | 300.1636 | 295.2516 | 308.7666 | 407.3461 | 476.927 | 394.3752 | NaN | NaN | NaN | 557.3013 | 1119.5607 | NaN | 660.8325 | 1253.6684 | NaN | NaN | NaN | NaN | 1253.7998 | 932.7191 | NaN | 19.5434 | NaN | 23.8675
9341.1448 | 754.8386 | 516.0958 | 300.7424 | 295.4425 | 308.8797 | 405.9525 | 476.7638 | 394.0633 | NaN | NaN | NaN | 575.1736 | 1131.1789 | NaN | 645.0901 | 1253.6681 | NaN | NaN | NaN | NaN | 1253.7995 | 962.1647 | NaN | 19.262 | NaN | 23.7594
9342.1448 | 754.3081 | 515.9844 | 301.2733 | 295.654 | 308.5834 | 406.599 | 475.8726 | 393.6824 | NaN | NaN | NaN | 596.3459 | 1150.6124 | NaN | 633.3767 | 1253.6689 | NaN | NaN | NaN | NaN | 1253.8003 | 987.6853 | NaN | 18.4515 | NaN | 23.866
9343.1448 | 754.3977 | 516.2977 | 301.131 | 296.3964 | 308.8026 | 405.0269 | 473.1883 | 393.6895 | NaN | NaN | NaN | 597.3659 | 1163.0427 | NaN | 617.5075 | 1253.6682 | NaN | NaN | NaN | NaN | 1253.7995 | 1017.1079 | NaN | 16.9043 | NaN | 23.7928
9344.1292 | 753.4205 | 516.8839 | 301.1274 | 296.589 | 308.7823 | 406.0852 | 474.4464 | 393.8714 | NaN | NaN | NaN | 593.3712 | 1171.0332 | NaN | 601.6515 | 1253.6675 | NaN | NaN | NaN | NaN | 1253.7989 | 1050.7882 | NaN | 16.3902 | NaN | 25.4617
9345.1292 | 753.1938 | 517.1639 | 301.4363 | 296.232 | 309.0491 | 405.547 | 475.2639 | 393.5501 | NaN | NaN | NaN | 573.7763 | 1181.6913 | NaN | 582.8789 | 1253.6676 | NaN | NaN | NaN | NaN | 1253.799 | 1073.1957 | NaN | 18.6438 | NaN | 23.3867
9346.1292 | 752.2475 | 517.3822 | 301.5888 | 295.8963 | 309.291 | 404.9824 | 474.4502 | 395.1723 | NaN | NaN | NaN | 568.1404 | 1196.7862 | NaN | 568.5272 | 1253.6669 | NaN | NaN | NaN | NaN | 1253.7983 | 1093.1091 | NaN | 18.2582 | NaN | 25.3486
9347.1292 | 751.474 | 517.8159 | 300.9295 | 295.6864 | 309.5958 | 405.6704 | 476.417 | 394.7597 | NaN | NaN | NaN | 595.4476 | 1213.0804 | NaN | 555.7089 | 1253.6672 | NaN | NaN | NaN | NaN | 1253.7986 | 1116.1204 | NaN | 16.7276 | NaN | 24.9965
9348.1292 | 751.0373 | 517.8171 | 301.9027 | 296.1691 | 310.3276 | 405.782 | 475.3786 | 396.2781 | NaN | NaN | NaN | 615.4069 | 1230.865 | NaN | 536.8157 | 1253.6676 | NaN | NaN | NaN | NaN | 1253.799 | 1140.2141 | NaN | 18.602 | NaN | 24.6727
9349.1292 | 751.4994 | 517.4543 | 301.123 | 295.8461 | 310.6121 | 404.4065 | 473.0246 | 396.0111 | NaN | NaN | NaN | 625.224 | 1244.9109 | NaN | 530.7602 | 1253.6669 | NaN | NaN | NaN | NaN | 1253.7982 | 1149.8117 | NaN | 18.6298 | NaN | 25.2257
9350.1292 | 751.7488 | 517.2933 | 301.404 | 296.3323 | 310.6009 | 404.6146 | 472.4956 | 395.8378 | NaN | NaN | NaN | 635.0037 | 1254.9382 | NaN | 517.2796 | 1253.6675 | NaN | NaN | NaN | NaN | 1253.7989 | 1158.3196 | NaN | 17.3361 | NaN | 22.8509
9351.1292 | 751.6012 | 517.5744 | 301.3914 | 295.6569 | 310.6234 | 403.6555 | 470.9594 | 396.5149 | NaN | NaN | NaN | 632.4055 | 1254.9392 | NaN | 505.961 | 1253.6686 | NaN | NaN | NaN | NaN | 1253.7999 | 1167.206 | NaN | 15.0944 | NaN | 25.0376
9352.1292 | 751.2146 | 517.0391 | 301.5976 | 295.6699 | 310.0194 | 401.8538 | 468.4608 | 394.8801 | NaN | NaN | NaN | 620.096 | 1254.9375 | NaN | 496.1724 | 1253.6668 | NaN | NaN | NaN | NaN | 1253.7982 | 1179.5074 | NaN | 18.8607 | NaN | 24.6127
9353.1292 | 749.6568 | 516.5129 | 301.6444 | 296.1276 | 309.9425 | 402.1915 | 467.2415 | 393.0581 | NaN | NaN | NaN | 613.7429 | 1254.9384 | NaN | 484.781 | 1253.6677 | NaN | NaN | NaN | NaN | 1253.7991 | 1201.7592 | NaN | 17.1608 | NaN | 23.6245
9354.1292 | 747.5072 | 516.4772 | 301.2926 | 296.7828 | 310.3914 | 402.7964 | 466.1624 | 392.2009 | NaN | NaN | NaN | 590.2736 | 1254.9375 | NaN | 476.8631 | 1253.6668 | NaN | NaN | NaN | NaN | 1253.7982 | 1234.2053 | NaN | 19.522 | NaN | 23.7944
9355.1292 | 746.2447 | 518.0182 | 300.7219 | 296.8916 | 310.188 | 401.5834 | 463.5397 | 390.565 | NaN | NaN | NaN | 596.0505 | 1254.9385 | NaN | 470.208 | 1253.6678 | NaN | NaN | NaN | NaN | 1253.7992 | 1254.3684 | NaN | 16.2957 | NaN | 23.1025
9356.1292 | 746.5101 | 517.1208 | 300.9617 | 296.6381 | 309.6805 | 401.1812 | 462.4341 | 389.4117 | NaN | NaN | NaN | 617.8498 | 1254.9379 | NaN | 459.4643 | 1253.6672 | NaN | NaN | NaN | NaN | 1253.7986 | 1254.3679 | NaN | 16.0817 | NaN | 25.0468
9357.1292 | 747.7574 | 516.6714 | 301.1537 | 296.193 | 309.6436 | 402.9427 | 462.741 | 388.3803 | NaN | NaN | NaN | 620.236 | 1254.9387 | NaN | 446.4457 | 1253.6681 | NaN | NaN | NaN | NaN | 1253.7994 | 1254.3687 | NaN | 17.3064 | NaN | 24.5517
9358.1292 | 746.1276 | 516.535 | 300.5362 | 296.1379 | 309.3392 | 402.8999 | 461.6958 | 388.813 | NaN | NaN | NaN | 642.9573 | 1254.9381 | NaN | 434.1377 | 1253.6674 | NaN | NaN | NaN | NaN | 1253.7988 | 1254.3681 | NaN | 18.3164 | NaN | 23.4944
9359.1292 | 744.8856 | 517.2476 | 300.4338 | 296.1783 | 309.0243 | 400.1988 | 459.0767 | 388.6662 | NaN | NaN | NaN | 659.8672 | 1254.9385 | NaN | 414.6068 | 1253.6679 | NaN | NaN | NaN | NaN | 1253.7992 | 1254.3685 | NaN | 16.3134 | NaN | 25.1279
9360.1292 | 743.1361 | 517.262 | 300.8707 | 295.5808 | 308.9798 | 398.2439 | 458.5478 | 388.1744 | NaN | NaN | NaN | 644.2778 | 1254.9378 | NaN | 390.6114 | 1253.6671 | NaN | NaN | NaN | NaN | 1253.7985 | 1254.3678 | NaN | 16.1478 | NaN | 23.6637
9361.1292 | 741.7167 | 518.7739 | 300.9802 | 296.0722 | 309.2681 | 396.9815 | 461.2709 | 386.9311 | NaN | NaN | NaN | 625.1116 | 1254.9381 | NaN | 373.2964 | 1253.6674 | NaN | NaN | NaN | NaN | 1253.7988 | 1254.3681 | NaN | 17.6822 | NaN | 24.7614
9362.1292 | 740.9544 | 517.8146 | 300.6812 | 296.2324 | 309.496 | 399.6402 | 461.4578 | 386.2151 | NaN | NaN | NaN | 632.1656 | 1254.938 | NaN | 355.5559 | 1253.6673 | NaN | NaN | NaN | NaN | 1253.7987 | 1254.3679 | NaN | 15.1728 | NaN | 25.3387
9363.1292 | 740.4502 | 518.77 | 300.2596 | 296.0965 | 309.4382 | 400.4738 | 459.6646 | 385.7069 | NaN | NaN | NaN | 632.0527 | 1254.9377 | NaN | 338.6769 | 1253.667 | NaN | NaN | NaN | NaN | 1253.7984 | 1254.3676 | NaN | 17.7727 | NaN | 23.361
9364.1292 | 739.4813 | 518.3246 | 300.0026 | 295.7047 | 309.3032 | 398.9644 | 457.82 | 384.66 | NaN | NaN | NaN | 606.0085 | 1254.9373 | NaN | 320.7838 | 1253.6666 | NaN | NaN | NaN | NaN | 1253.798 | 1254.3672 | NaN | 17.9166 | NaN | 23.3503
9365.1292 | 739.0599 | 519.4667 | 299.9653 | 296.1663 | 309.6537 | 399.2813 | 459.8739 | 384.3811 | NaN | NaN | NaN | 586.7812 | 1254.938 | NaN | 298.6107 | 1253.6673 | NaN | NaN | NaN | NaN | 1253.7987 | 1254.3679 | NaN | 14.7526 | NaN | 24.3499
9366.1292 | 738.2607 | 520.2342 | 300.1115 | 296.2096 | 309.602 | 399.6739 | 460.5024 | 384.9548 | NaN | NaN | NaN | 569.3769 | 1254.9379 | NaN | 278.3221 | 1253.6672 | NaN | NaN | NaN | NaN | 1253.7986 | 1254.3679 | NaN | 18.1187 | NaN | 25.1495
9367.1292 | 738.8624 | 521.1525 | 300.1104 | 296.421 | 309.6658 | 398.8971 | 461.1118 | 384.9215 | NaN | NaN | NaN | 560.0168 | 1254.9379 | NaN | 263.4166 | 1253.6672 | NaN | NaN | NaN | NaN | 1253.7986 | 1254.3679 | NaN | 16.2395 | NaN | 24.6407
9368.1292 | 740.102 | 521.4959 | 300.148 | 296.4821 | 309.7109 | 399.0869 | 463.3881 | 385.5152 | NaN | NaN | NaN | 544.6354 | 1254.9372 | NaN | 243.7733 | 1253.6665 | NaN | NaN | NaN | NaN | 1253.7979 | 1254.3672 | NaN | 17.5291 | NaN | 24.2351
9369.1292 | 740.8461 | 522.4153 | 300.4341 | 296.449 | 309.7174 | 399.4772 | 464.642 | 386.6137 | NaN | NaN | NaN | 539.1132 | 1254.9381 | NaN | 224.0336 | 1253.6674 | NaN | NaN | NaN | NaN | 1253.7988 | 1254.3681 | NaN | 17.0951 | NaN | 24.7692
9370.1292 | 740.3213 | 522.0007 | 300.6327 | 296.3867 | 309.4137 | 398.1672 | 465.5044 | 386.9356 | NaN | NaN | NaN | 553.0101 | 1254.937 | NaN | 204.0927 | 1253.6663 | NaN | NaN | NaN | NaN | 1253.7977 | 1254.3669 | NaN | 14.7798 | NaN | 24.0857
9371.1292 | 740.4748 | 521.8862 | 300.729 | 296.6618 | 309.1745 | 397.4062 | 463.9943 | 386.2322 | NaN | NaN | NaN | 548.9233 | 1254.9371 | NaN | 180.2277 | 1253.6664 | NaN | NaN | NaN | NaN | 1253.7978 | 1254.3671 | NaN | 18.5959 | NaN | 25.4421
9372.1292 | 740.59 | 521.5416 | 300.331 | 296.6145 | 309.1304 | 396.2487 | 463.1488 | 385.5037 | NaN | NaN | NaN | 536.5627 | 1254.9375 | NaN | 158.1464 | 1253.6669 | NaN | NaN | NaN | NaN | 1253.7982 | 1254.3675 | NaN | 17.7205 | NaN | 24.5804
9373.1292 | 740.1696 | 522.2978 | 300.2716 | 296.7553 | 309.2776 | 396.7215 | 463.0694 | 386.4664 | NaN | NaN | NaN | 523.5978 | 1254.9372 | NaN | 137.7046 | 1253.6665 | NaN | NaN | NaN | NaN | 1253.7978 | 1254.3671 | NaN | 19.309 | NaN | 23.6719
9374.1292 | 739.537 | 522.4603 | 299.5754 | 296.7442 | 308.6744 | 398.5962 | 461.8394 | 385.1163 | NaN | NaN | NaN | 518.4653 | 1254.9374 | NaN | 120.1685 | 1253.6667 | NaN | NaN | NaN | NaN | 1253.7981 | 1254.3674 | NaN | 17.6041 | NaN | 23.5727
9375.1292 | 740.4193 | 522.2875 | 299.1045 | 296.7576 | 308.433 | 399.2173 | 460.1898 | 384.3363 | NaN | NaN | NaN | 531.3698 | 1254.9358 | NaN | 102.7115 | 1253.6652 | NaN | NaN | NaN | NaN | 1253.7965 | 1254.3658 | NaN | 17.7128 | NaN | 22.4966
9376.1292 | 741.1869 | 522.2106 | 299.0395 | 296.7736 | 308.39 | 400.2841 | 458.758 | 384.5943 | NaN | NaN | NaN | 516.7801 | 1254.9365 | NaN | 81.0306 | 1253.6658 | NaN | NaN | NaN | NaN | 1253.7972 | 1254.3664 | NaN | 15.1529 | NaN | 24.4287
9377.1292 | 741.3528 | 522.9594 | 299.3531 | 297.4538 | 308.6369 | 401.0233 | 458.0263 | 384.9676 | NaN | NaN | NaN | 521.4462 | 1254.9365 | NaN | 60.6581 | 1253.6658 | NaN | NaN | NaN | NaN | 1253.7972 | 1254.3664 | NaN | 15.7183 | NaN | 22.8747
9378.1292 | 742.9598 | 524.4099 | 299.5823 | 297.1936 | 308.6151 | 401.6036 | 456.7122 | 384.6156 | NaN | NaN | NaN | 541.0764 | 1254.9372 | NaN | 44.4871 | 1253.6665 | NaN | NaN | NaN | NaN | 1253.7979 | 1254.3672 | NaN | -3.1846 | NaN | 20.1904
9379.1292 | 743.5039 | 524.58 | 299.4783 | 297.2544 | 308.4709 | 401.8781 | 457.1845 | 385.7445 | NaN | NaN | NaN | 543.2677 | 1254.9363 | NaN | 14.2575 | 1253.6657 | NaN | NaN | NaN | NaN | 1253.797 | 1254.3663 | NaN | 17.641 | NaN | 25.5694
9380.1292 | 745.1515 | 524.8606 | 299.7438 | 296.9664 | 308.0502 | 401.6752 | 459.3035 | 385.5901 | NaN | NaN | NaN | 562.2666 | 1254.9369 | NaN | -7.1843 | 1253.6662 | NaN | NaN | NaN | NaN | 1253.7976 | 1254.3669 | NaN | -11.7478 | NaN | 32.8155
9381.1292 | 745.6082 | 525.4383 | 299.0505 | 296.8286 | 308.1303 | 400.6547 | 458.1931 | 385.4746 | NaN | NaN | NaN | 574.2626 | 1254.9351 | NaN | NaN | 1253.6644 | NaN | NaN | NaN | NaN | 1253.7958 | 1254.3651 | NaN | 41.1568 | NaN | 26.3886
9382.1292 | 746.5117 | 525.6448 | 299.0631 | 297.6123 | 308.4103 | 400.606 | 458.9386 | 386.1718 | NaN | NaN | NaN | 573.9489 | 1254.9363 | NaN | NaN | 1253.6657 | NaN | NaN | NaN | NaN | 1253.797 | 1254.3663 | NaN | 66.0233 | NaN | 30.3624
9383.1292 | 746.2286 | 525.0403 | 299.3115 | 297.1218 | 308.495 | 399.413 | 458.1888 | 385.5955 | NaN | NaN | NaN | 585.846 | 1254.9355 | NaN | NaN | 1253.6648 | NaN | NaN | NaN | NaN | 1253.7962 | 1254.3655 | NaN | -5.6866 | NaN | 21.3839
9384.1292 | 746.5348 | 525.3657 | 298.5559 | 296.8654 | 308.1317 | 399.5343 | 458.1832 | 385.2076 | NaN | NaN | NaN | 611.0932 | 1254.9367 | NaN | NaN | 1253.666 | NaN | NaN | NaN | NaN | 1253.7974 | 1254.3667 | NaN | 17.8353 | NaN | 24.3369
9385.1292 | 746.4273 | 526.1786 | 298.6349 | 297.143 | 308.1091 | 399.5347 | 460.6801 | 386.122 | NaN | NaN | NaN | 620.6914 | 1254.9366 | NaN | 44.6314 | 1253.6659 | NaN | NaN | NaN | NaN | 1253.7973 | 1254.3666 | NaN | 38.2785 | NaN | 36.6956
9386.1292 | 744.3865 | 525.9767 | 298.5317 | 297.2427 | 308.0128 | 397.4373 | 459.9051 | 386.6611 | NaN | NaN | NaN | 607.4253 | 1254.9367 | NaN | 204.8571 | 1253.666 | NaN | NaN | NaN | NaN | 1253.7973 | 1254.3666 | NaN | 37.1228 | NaN | 33.5608
9387.1292 | 743.8028 | 525.5872 | 298.511 | 297.2202 | 308.1549 | 396.3412 | 457.6429 | 387.3902 | NaN | NaN | NaN | 610.8065 | 1254.9359 | NaN | 479.905 | 1253.6652 | NaN | NaN | NaN | NaN | 1253.7966 | 1254.3659 | NaN | 24.0042 | NaN | 26.8405
9388.1292 | 741.6997 | 525.8297 | 298.2361 | 297.5153 | 308.6528 | 395.1266 | 457.5185 | 387.7882 | NaN | NaN | NaN | 615.8042 | 1254.936 | NaN | 944.9697 | 1253.6653 | NaN | NaN | NaN | NaN | 1253.7967 | 1254.3659 | NaN | 15.409 | NaN | 22.9734
9389.1292 | 741.0889 | 526.0154 | 298.2199 | 297.0134 | 308.3812 | 393.6038 | 457.2926 | 387.3094 | NaN | NaN | NaN | 619.124 | 1254.9359 | NaN | NaN | 1253.6652 | NaN | NaN | NaN | NaN | 1253.7966 | 1254.3659 | NaN | 14.8639 | NaN | 23.1061
9390.1292 | 741.4951 | 526.841 | 298.0772 | 296.8195 | 308.2366 | 393.6806 | 459.7805 | 388.355 | NaN | NaN | NaN | 598.2813 | 1254.9348 | NaN | NaN | 1253.6641 | NaN | NaN | NaN | NaN | 1253.7955 | 1254.3647 | NaN | 17.421 | NaN | 22.8159
9391.1292 | 741.1681 | 526.9698 | 298.2241 | 296.7538 | 307.9497 | 394.1326 | 460.2983 | 387.7722 | NaN | NaN | NaN | 609.7672 | 1254.9349 | NaN | NaN | 1253.6642 | NaN | NaN | NaN | NaN | 1253.7956 | 1254.3649 | NaN | 19.0838 | NaN | 23.8124
9392.1292 | 741.6422 | 526.7687 | 298.45 | 297.2111 | 308.1186 | 395.7447 | 460.494 | 387.9152 | NaN | NaN | NaN | 626.7865 | 1254.9353 | NaN | NaN | 1253.6647 | NaN | NaN | NaN | NaN | 1253.796 | 1254.3653 | NaN | 15.2248 | NaN | 23.7112
9393.1292 | 742.3906 | 526.9059 | 298.6686 | 296.901 | 307.9923 | 396.7403 | 461.7577 | 388.8647 | NaN | NaN | NaN | 615.1119 | 1254.935 | NaN | NaN | 1253.6643 | NaN | NaN | NaN | NaN | 1253.7957 | 1254.365 | NaN | 17.3561 | NaN | 24.7001
9394.1292 | 743.7725 | 526.7711 | 298.9543 | 297.8809 | 308.6845 | 398.4124 | 461.7128 | 389.0147 | NaN | NaN | NaN | 593.8487 | 1254.9345 | NaN | NaN | 1253.6638 | NaN | NaN | NaN | NaN | 1253.7951 | 1254.3644 | NaN | 19.1142 | NaN | 23.9861
9395.1292 | 743.975 | 528.0807 | 299.3907 | 297.6433 | 308.8587 | 399.6881 | 460.6529 | 387.6776 | NaN | NaN | NaN | 586.2999 | 1254.9358 | NaN | NaN | 1253.6651 | NaN | NaN | NaN | NaN | 1253.7965 | 1254.3657 | NaN | 18.2428 | NaN | 23.8309
9396.1292 | 743.6144 | 528.4834 | 299.7679 | 297.6751 | 308.7417 | 399.6727 | 458.8512 | 386.5146 | NaN | NaN | NaN | 581.2925 | 1254.9352 | NaN | NaN | 1253.6645 | NaN | NaN | NaN | NaN | 1253.7959 | 1254.3652 | NaN | 15.6674 | NaN | 21.6949
9397.1292 | 741.6384 | 528.3816 | 299.6304 | 297.8236 | 308.7091 | 398.064 | 456.3859 | 386.5293 | NaN | NaN | NaN | 616.2475 | 1254.9347 | NaN | NaN | 1253.664 | NaN | NaN | NaN | NaN | 1253.7954 | 1254.3647 | NaN | 20.5295 | NaN | 25.2332
9398.1292 | 740.7176 | 528.5117 | 299.713 | 298.0498 | 308.4709 | 397.5219 | 455.2329 | 385.2955 | NaN | NaN | NaN | 600.3722 | 1254.9343 | NaN | NaN | 1253.6636 | NaN | NaN | NaN | NaN | 1253.795 | 1254.3642 | NaN | 18.3021 | NaN | 24.5229
9399.1292 | 740.0314 | 530.6341 | 300.2576 | 298.3996 | 308.4893 | 397.1015 | 454.7486 | 384.9238 | NaN | NaN | NaN | 586.6311 | 1254.9353 | NaN | NaN | 1253.6647 | NaN | NaN | NaN | NaN | 1253.796 | 1254.3653 | NaN | 19.1944 | NaN | 23.3919
9400.1292 | 739.1184 | 530.5622 | 299.2628 | 297.9329 | 308.1966 | 396.5458 | 455.3168 | 384.3696 | NaN | NaN | NaN | 569.2012 | 1254.934 | NaN | NaN | 1253.6633 | NaN | NaN | NaN | NaN | 1253.7946 | 1254.3639 | NaN | 19.3802 | NaN | 24.0918
9401.1292 | 738.7904 | 530.3612 | 299.1855 | 297.4956 | 307.8114 | 396.3766 | 454.399 | 383.4982 | NaN | NaN | NaN | 556.7067 | 1254.9337 | NaN | NaN | 1253.663 | NaN | NaN | NaN | NaN | 1253.7944 | 1254.3637 | NaN | 19.3026 | NaN | 25.0865
9402.1292 | 736.3579 | 529.9117 | 299.148 | 297.3013 | 307.3835 | 397.1552 | 452.9157 | 381.8321 | NaN | NaN | NaN | 566.7612 | 1254.935 | NaN | NaN | 1253.6643 | NaN | NaN | NaN | NaN | 1253.7957 | 1254.365 | NaN | 19.4809 | NaN | 25.0858
9403.1292 | 735.7817 | 529.7069 | 299.72 | 297.2251 | 307.0741 | 397.6992 | 450.357 | 379.9032 | NaN | NaN | NaN | 571.8095 | 1254.9349 | NaN | NaN | 1253.6642 | NaN | NaN | NaN | NaN | 1253.7956 | 1254.3649 | NaN | 16.6171 | NaN | 24.7834
9404.1292 | 738.0708 | 531.8226 | 299.8127 | 297.5931 | 307.4461 | 397.9579 | 447.8102 | 378.7849 | NaN | NaN | NaN | 582.6029 | 1254.9339 | NaN | NaN | 1253.6632 | NaN | NaN | NaN | NaN | 1253.7946 | 1254.3638 | NaN | 17.1555 | NaN | 22.7955
9405.1292 | 739.0593 | 531.8969 | 300.0958 | 296.9879 | 307.1326 | 398.3766 | 448.7057 | 378.9761 | NaN | NaN | NaN | 601.755 | 1254.9341 | NaN | NaN | 1253.6634 | NaN | NaN | NaN | NaN | 1253.7948 | 1254.364 | NaN | 17.5441 | NaN | 23.1809
9406.1292 | 741.0779 | 531.954 | 299.8222 | 296.895 | 307.011 | 398.3482 | 450.274 | 378.7618 | NaN | NaN | NaN | 626.2773 | 1254.9342 | NaN | NaN | 1253.6635 | NaN | NaN | NaN | NaN | 1253.7949 | 1254.3642 | NaN | 17.1427 | NaN | 25.0284
9407.1292 | 739.7585 | 531.4958 | 299.6142 | 296.7577 | 306.949 | 397.8406 | 449.0197 | 378.093 | NaN | NaN | NaN | 639.8022 | 1254.9344 | NaN | NaN | 1253.6637 | NaN | NaN | NaN | NaN | 1253.7951 | 1254.3644 | NaN | 17.414 | NaN | 22.9815
9408.1292 | 739.801 | 530.527 | 299.4769 | 296.423 | 306.7566 | 396.7213 | 448.8466 | 377.0607 | NaN | NaN | NaN | 635.3489 | 1254.9334 | NaN | NaN | 1253.6627 | NaN | NaN | NaN | NaN | 1253.7941 | 1254.3633 | NaN | 18.5826 | NaN | 25.473
9409.1292 | 740.3359 | 530.0223 | 299.6918 | 297.2169 | 307.173 | 397.844 | 448.5008 | 376.6379 | NaN | NaN | NaN | 642.623 | 1254.9345 | NaN | NaN | 1253.6638 | NaN | NaN | NaN | NaN | 1253.7952 | 1254.3645 | NaN | 15.3265 | NaN | 23.9116
9410.1292 | 741.0101 | 530.2147 | 299.4628 | 297.1474 | 307.4823 | 397.9373 | 448.684 | 376.7464 | NaN | NaN | NaN | 658.2984 | 1254.9333 | NaN | NaN | 1253.6626 | NaN | NaN | NaN | NaN | 1253.7939 | 1254.3632 | NaN | 15.7612 | NaN | 22.6042
9411.1448 | 742.1393 | 530.6521 | 299.1397 | 297.0553 | 307.3077 | 396.8045 | 449.113 | 377.2651 | NaN | NaN | NaN | 669.9643 | 1254.9337 | NaN | NaN | 1253.663 | NaN | NaN | NaN | NaN | 1253.7944 | 1254.3637 | NaN | 18.7998 | NaN | 23.6546
9412.1292 | 742.9032 | 530.7571 | 299.419 | 297.2454 | 306.8372 | 396.3933 | 450.3579 | 378.5444 | NaN | NaN | NaN | 663.9177 | 1254.9336 | NaN | NaN | 1253.663 | NaN | NaN | NaN | NaN | 1253.7943 | 1254.3636 | NaN | 19.1546 | NaN | 25.0095
9413.1292 | 743.1224 | 531.5282 | 299.476 | 297.2983 | 306.8356 | 395.9279 | 451.5324 | 379.613 | NaN | NaN | NaN | 659.1485 | 1254.9342 | NaN | NaN | 1253.6635 | NaN | NaN | NaN | NaN | 1253.7949 | 1254.3642 | NaN | 19.2062 | NaN | 23.7024
9414.1292 | 742.0791 | 531.5835 | 299.3801 | 297.5196 | 306.9326 | 395.219 | 451.3146 | 379.817 | NaN | NaN | NaN | 648.8272 | 1254.9337 | NaN | NaN | 1253.663 | NaN | NaN | NaN | NaN | 1253.7944 | 1254.3637 | NaN | 18.3838 | NaN | 23.6925
9415.1292 | 742.0175 | 530.8847 | 299.312 | 297.3492 | 307.133 | 395.164 | 448.9985 | 378.7668 | NaN | NaN | NaN | 653.6618 | 1254.9334 | NaN | NaN | 1253.6627 | NaN | NaN | NaN | NaN | 1253.7941 | 1254.3633 | NaN | 17.3775 | NaN | 23.9861
9416.1292 | 742.3789 | 530.6772 | 299.3983 | 297.1176 | 307.4361 | 395.4785 | 447.9585 | 377.8947 | NaN | NaN | NaN | 659.5201 | 1254.9331 | NaN | NaN | 1253.6625 | NaN | NaN | NaN | NaN | 1253.7938 | 1254.3631 | NaN | 19.555 | NaN | 25.3205
9417.1292 | 741.1767 | 530.8017 | 299.8234 | 297.215 | 307.2928 | 395.8904 | 448.2163 | 378.942 | NaN | NaN | NaN | 649.1558 | 1254.9334 | NaN | NaN | 1253.6627 | NaN | NaN | NaN | NaN | 1253.7941 | 1254.3634 | NaN | 20.7874 | NaN | 24.0757
9418.1292 | 741.002 | 530.5551 | 300.5049 | 296.8175 | 307.4281 | 394.4694 | 446.2236 | 378.111 | NaN | NaN | NaN | 654.9279 | 1254.9322 | NaN | NaN | 1253.6615 | NaN | NaN | NaN | NaN | 1253.7929 | 1254.3621 | NaN | 18.6737 | NaN | 22.4115
9419.1292 | 741.1275 | 531.8842 | 300.5986 | 296.6143 | 307.2916 | 395.1065 | 447.6665 | 378.349 | NaN | NaN | NaN | 678.0285 | 1254.9326 | NaN | NaN | 1253.6619 | NaN | NaN | NaN | NaN | 1253.7933 | 1254.3625 | NaN | 19.307 | NaN | 23.6463
9420.1292 | 740.0402 | 531.3537 | 300.8167 | 296.5671 | 307.3866 | 394.8158 | 448.6348 | 379.0893 | NaN | NaN | NaN | 673.8405 | 1254.9328 | NaN | NaN | 1253.6621 | NaN | NaN | NaN | NaN | 1253.7934 | 1254.3627 | NaN | 19.2965 | NaN | 22.6125
9421.1292 | 738.4507 | 531.0554 | 300.4661 | 296.4287 | 307.1845 | 394.1065 | 447.6291 | 380.2688 | NaN | NaN | NaN | 696.5768 | 1254.933 | NaN | NaN | 1253.6623 | NaN | NaN | NaN | NaN | 1253.7937 | 1254.363 | NaN | 19.0531 | NaN | 24.4103
9422.1292 | 738.4207 | 532.4464 | 300.3351 | 296.4585 | 307.6225 | 392.2066 | 446.721 | 379.6418 | NaN | NaN | NaN | 694.4227 | 1254.9321 | NaN | NaN | 1253.6614 | NaN | NaN | NaN | NaN | 1253.7928 | 1254.362 | NaN | 18.0004 | NaN | 22.3508
9423.1292 | 739.3928 | 532.546 | 300.5248 | 296.5516 | 307.9733 | 392.313 | 449.1588 | 380.9073 | NaN | NaN | NaN | 701.4786 | 1254.9326 | NaN | NaN | 1253.6619 | NaN | NaN | NaN | NaN | 1253.7933 | 1254.3626 | NaN | 19.092 | NaN | 23.0964
9424.1292 | 739.7626 | 531.8069 | 300.6435 | 296.8818 | 308.0693 | 392.0659 | 451.0423 | 380.8106 | NaN | NaN | NaN | 679.2251 | 1254.9324 | NaN | NaN | 1253.6618 | NaN | NaN | NaN | NaN | 1253.7931 | 1254.3624 | NaN | 17.8584 | NaN | 24.5411
9425.1292 | 740.4486 | 531.7743 | 299.8955 | 297.4226 | 307.9957 | 391.4956 | 452.1197 | 381.9245 | NaN | NaN | NaN | 674.9555 | 1254.9328 | NaN | NaN | 1253.6621 | NaN | NaN | NaN | NaN | 1253.7935 | 1254.3628 | NaN | 16.9332 | NaN | 25.0019
9426.1292 | 741.9183 | 533.1481 | 300.2487 | 297.4904 | 308.4262 | 392.3703 | 454.5441 | 383.2035 | NaN | NaN | NaN | 650.1858 | 1254.9324 | NaN | NaN | 1253.6618 | NaN | NaN | NaN | NaN | 1253.7931 | 1254.3624 | NaN | 19.2103 | NaN | 23.81
9427.1292 | 742.6021 | 533.3806 | 300.1171 | 296.766 | 308.4997 | 391.5843 | 453.8115 | 383.8965 | NaN | NaN | NaN | 620.6347 | 1254.9319 | NaN | NaN | 1253.6612 | NaN | NaN | NaN | NaN | 1253.7926 | 1254.3619 | NaN | 16.5778 | NaN | 22.998
9428.1292 | 743.4921 | 533.9551 | 299.9302 | 297.1424 | 308.4481 | 391.9844 | 454.0425 | 383.9405 | NaN | NaN | NaN | 598.8541 | 1254.9325 | NaN | NaN | 1253.6618 | NaN | NaN | NaN | NaN | 1253.7932 | 1254.3625 | NaN | 15.9664 | NaN | 24.545
9429.1292 | 744.235 | 532.7176 | 300.0704 | 297.604 | 308.2214 | 393.8166 | 454.6655 | 384.2896 | NaN | NaN | NaN | 602.1562 | 1254.9318 | NaN | NaN | 1253.6611 | NaN | NaN | NaN | NaN | 1253.7925 | 1254.3618 | NaN | 18.1395 | NaN | 23.8116
9430.1292 | 745.3351 | 533.561 | 300.1312 | 299.372 | 309.0593 | 393.8563 | 454.4335 | 385.9455 | NaN | NaN | NaN | 637.4573 | 1254.9317 | NaN | NaN | 1253.661 | NaN | NaN | NaN | NaN | 1253.7924 | 1254.3617 | NaN | 17.2428 | NaN | 23.7373
9431.1292 | 744.4713 | 535.3515 | 299.5193 | 299.4802 | 309.4249 | 392.8481 | 454.3051 | 387.5742 | NaN | NaN | NaN | 636.058 | 1254.9323 | NaN | NaN | 1253.6616 | NaN | NaN | NaN | NaN | 1253.793 | 1254.3623 | NaN | 18.9703 | NaN | 23.498
9432.1292 | 745.179 | 540.4344 | 299.4597 | 299.1374 | 309.4723 | 392.4086 | 455.9759 | 389.619 | NaN | NaN | NaN | 628.5429 | 1254.932 | NaN | NaN | 1253.6613 | NaN | NaN | NaN | NaN | 1253.7927 | 1254.362 | NaN | 19.2106 | NaN | 22.6611
9433.1292 | 745.937 | 541.0413 | 299.8309 | 298.9908 | 309.446 | 394.2595 | 458.3632 | 390.0791 | NaN | NaN | NaN | 666.3398 | 1254.9317 | NaN | NaN | 1253.6611 | NaN | NaN | NaN | NaN | 1253.7924 | 1254.3617 | NaN | 15.6615 | NaN | 23.8936
9434.1292 | 747.291 | 542.9431 | 299.6466 | 299.545 | 309.6102 | 395.0191 | 460.7776 | 392.3482 | NaN | NaN | NaN | 693.5759 | 1254.9314 | NaN | NaN | 1253.6607 | NaN | NaN | NaN | NaN | 1253.7921 | 1254.3614 | NaN | 17.2994 | NaN | 24.466
9435.1292 | 747.3556 | 542.1672 | 299.9212 | 299.3938 | 309.8733 | 395.1347 | 462.1048 | 394.4625 | NaN | NaN | NaN | 703.2493 | 1254.9305 | NaN | NaN | 1253.6599 | NaN | NaN | NaN | NaN | 1253.7912 | 1254.3605 | NaN | 16.6749 | NaN | 22.7561
9436.1292 | 748.4923 | 541.1567 | 300.5461 | 299.0265 | 311.0397 | 396.0753 | 462.8435 | 393.3199 | NaN | NaN | NaN | 670.9765 | 1254.9301 | NaN | NaN | 1253.6594 | NaN | NaN | NaN | NaN | 1253.7908 | 1254.3601 | NaN | 16.3192 | NaN | 23.4208
9437.1292 | 748.0763 | 541.1095 | 300.0861 | 299.2038 | 311.5662 | 396.5171 | 463.6471 | 393.1147 | NaN | NaN | NaN | 640.3926 | 1254.9305 | NaN | NaN | 1253.6599 | NaN | NaN | NaN | NaN | 1253.7912 | 1254.3605 | NaN | 19.0702 | NaN | 23.6374
9438.1292 | 747.8027 | 540.0841 | 300.9916 | 299.555 | 311.976 | 397.0454 | 463.9394 | 392.4135 | NaN | NaN | NaN | 621.7146 | 1254.9313 | NaN | NaN | 1253.6606 | NaN | NaN | NaN | NaN | 1253.792 | 1254.3613 | NaN | 17.4843 | NaN | 23.7234
9439.1292 | 748.8422 | 540.1111 | 301.8299 | 299.6444 | 312.4109 | 397.8462 | 463.8767 | 392.7656 | NaN | NaN | NaN | 639.6505 | 1254.9307 | NaN | NaN | 1253.66 | NaN | NaN | NaN | NaN | 1253.7914 | 1254.3606 | NaN | 17.4574 | NaN | 23.747
9440.1292 | 749.0426 | 539.9229 | 302.4988 | 300.5238 | 313.0728 | 398.1289 | 462.9111 | 393.3702 | NaN | NaN | NaN | 660.4755 | 1254.9301 | NaN | NaN | 1253.6594 | NaN | NaN | NaN | NaN | 1253.7908 | 1254.3601 | NaN | 15.7062 | NaN | 24.8179
9441.1292 | 750.3618 | 540.5007 | 302.8096 | 300.7509 | 313.3509 | 396.3403 | 463.5566 | 393.4599 | NaN | NaN | NaN | 635.7803 | 1254.9311 | NaN | NaN | 1253.6604 | NaN | NaN | NaN | NaN | 1253.7917 | 1254.361 | NaN | 18.9274 | NaN | 24.3346
9442.1292 | 751.0693 | 540.7769 | 303.6059 | 300.4726 | 313.5015 | 395.8876 | 463.205 | 394.0956 | NaN | NaN | NaN | 614.3182 | 1254.9318 | NaN | NaN | 1253.6611 | NaN | NaN | NaN | NaN | 1253.7925 | 1254.3618 | NaN | 18.1571 | NaN | 23.9695
9443.1292 | 749.4938 | 542.2997 | 303.3669 | 300.6921 | 313.7723 | 396.4426 | 461.8754 | 395.6476 | NaN | NaN | NaN | 608.8196 | 1254.9298 | NaN | NaN | 1253.6591 | NaN | NaN | NaN | NaN | 1253.7905 | 1254.3598 | NaN | 15.4583 | NaN | 25.1214
9444.1292 | 749.3806 | 543.5667 | 302.9828 | 300.6301 | 313.8531 | 395.7005 | 460.2122 | 397.5543 | NaN | NaN | NaN | 588.0395 | 1254.9307 | NaN | NaN | 1253.66 | NaN | NaN | NaN | NaN | 1253.7914 | 1254.3606 | NaN | 16.0219 | NaN | 24.4524
9445.1292 | 749.2043 | 544.1923 | 303.1088 | 300.9544 | 313.6872 | 394.0144 | 458.8657 | 397.6676 | NaN | NaN | NaN | 599.4964 | 1254.9303 | NaN | NaN | 1253.6596 | NaN | NaN | NaN | NaN | 1253.791 | 1254.3603 | NaN | 18.0312 | NaN | 24.8268
9446.1292 | 748.1663 | 545.7214 | 303.2994 | 301.4603 | 314.0052 | 393.0782 | 458.6725 | 397.3877 | NaN | NaN | NaN | 587.5732 | 1254.9301 | NaN | NaN | 1253.6594 | NaN | NaN | NaN | NaN | 1253.7908 | 1254.3601 | NaN | 16.9833 | NaN | 24.3049
9447.1292 | 748.8442 | 545.9931 | 302.4541 | 301.3673 | 313.9586 | 392.251 | 458.0193 | 397.2689 | NaN | NaN | NaN | 570.7573 | 1254.9308 | NaN | NaN | 1253.6601 | NaN | NaN | NaN | NaN | 1253.7915 | 1254.3608 | NaN | 17.9399 | NaN | 24.7942
9448.1292 | 749.7108 | 544.9493 | 302.7678 | 301.635 | 313.9112 | 393.2882 | 459.6073 | 397.0432 | NaN | NaN | NaN | 586.5158 | 1254.9293 | NaN | NaN | 1253.6586 | NaN | NaN | NaN | NaN | 1253.79 | 1254.3593 | NaN | 17.9949 | NaN | 23.0106
9449.1292 | 750.0585 | 543.5917 | 302.7219 | 301.8945 | 314.0435 | 393.4585 | 458.5735 | 397.2586 | NaN | NaN | NaN | 604.3753 | 1254.9301 | NaN | NaN | 1253.6594 | NaN | NaN | NaN | NaN | 1253.7908 | 1254.3601 | NaN | 19.0327 | NaN | 23.9562
9450.1292 | 749.7178 | 543.0725 | 302.7431 | 301.358 | 313.6988 | 393.7025 | 459.0394 | 397.3188 | NaN | NaN | NaN | 648.6847 | 1254.9307 | NaN | NaN | 1253.66 | NaN | NaN | NaN | NaN | 1253.7914 | 1254.3606 | NaN | 17.9875 | NaN | 24.2929
9451.1292 | 749.9903 | 543.6385 | 303.6064 | 301.2404 | 314.1133 | 393.079 | 460.615 | 397.3464 | NaN | NaN | NaN | 677.5051 | 1254.9294 | NaN | NaN | 1253.6587 | NaN | NaN | NaN | NaN | 1253.7901 | 1254.3594 | NaN | 16.7679 | NaN | 24.9061
9452.1292 | 749.2723 | 543.6953 | 303.5682 | 301.2559 | 313.8473 | 393.7975 | 461.8968 | 398.0068 | NaN | NaN | NaN | 674.3127 | 1254.9301 | NaN | NaN | 1253.6594 | NaN | NaN | NaN | NaN | 1253.7908 | 1254.3601 | NaN | 15.3428 | NaN | 22.4011
9453.1292 | 749.6144 | 542.7163 | 303.3385 | 302.0879 | 314.2216 | 394.0417 | 460.6971 | 396.8508 | NaN | NaN | NaN | 671.4835 | 1254.9283 | NaN | NaN | 1253.6576 | NaN | NaN | NaN | NaN | 1253.789 | 1254.3582 | NaN | 15.3059 | NaN | 23.8234
9454.1292 | 749.9309 | 542.4268 | 303.5227 | 301.859 | 314.1137 | 395.1749 | 461.6815 | 397.3635 | NaN | NaN | NaN | 656.0669 | 1254.9294 | NaN | NaN | 1253.6587 | NaN | NaN | NaN | NaN | 1253.79 | 1254.3593 | NaN | 17.2236 | NaN | 23.6895
9455.1292 | 750.2949 | 544.5641 | 303.99 | 301.7918 | 314.3726 | 394.0812 | 462.2908 | 397.2769 | NaN | NaN | NaN | 634.371 | 1254.9304 | NaN | NaN | 1253.6597 | NaN | NaN | NaN | NaN | 1253.7911 | 1254.3603 | NaN | 16.7287 | NaN | 24.0304
9456.1292 | 749.564 | 545.4003 | 304.4668 | 301.8446 | 314.7599 | 394.1972 | 463.0502 | 398.3034 | NaN | NaN | NaN | 615.7913 | 1254.929 | NaN | NaN | 1253.6583 | NaN | NaN | NaN | NaN | 1253.7897 | 1254.3589 | NaN | 17.4532 | NaN | 24.517
9457.1292 | 747.6195 | 543.5561 | 303.5602 | 301.5265 | 314.875 | 394.4247 | 461.7531 | 397.7722 | NaN | NaN | NaN | 622.621 | 1254.9299 | NaN | NaN | 1253.6592 | NaN | NaN | NaN | NaN | 1253.7905 | 1254.3598 | NaN | 17.868 | NaN | 24.9374
9458.1292 | 746.8119 | 543.8744 | 303.791 | 301.8699 | 315.0988 | 395.4073 | 462.453 | 396.9798 | NaN | NaN | NaN | 637.7204 | 1254.9287 | NaN | NaN | 1253.658 | NaN | NaN | NaN | NaN | 1253.7894 | 1254.3587 | NaN | 19.4523 | NaN | 23.4177
9459.1292 | 744.9616 | 542.2032 | 304.0034 | 301.5406 | 315.1885 | 394.6435 | 461.5994 | 396.463 | NaN | NaN | NaN | 658.2226 | 1254.9289 | NaN | NaN | 1253.6582 | NaN | NaN | NaN | NaN | 1253.7896 | 1254.3589 | NaN | 15.6275 | NaN | 22.7738
9460.1292 | 743.5925 | 541.8677 | 303.9816 | 301.2009 | 314.643 | 392.8577 | 459.0267 | 394.4419 | NaN | NaN | NaN | 666.3875 | 1254.929 | NaN | NaN | 1253.6583 | NaN | NaN | NaN | NaN | 1253.7897 | 1254.3589 | NaN | 16.3329 | NaN | 23.5814
9461.1292 | 744.1002 | 540.3837 | 304.0384 | 301.4414 | 314.6989 | 393.4764 | 460.2334 | 393.1724 | NaN | NaN | NaN | 676.9294 | 1254.9282 | NaN | NaN | 1253.6575 | NaN | NaN | NaN | NaN | 1253.7888 | 1254.3581 | NaN | 17.6874 | NaN | 22.5168
9462.1292 | 743.2546 | 540.5834 | 304.0537 | 301.9813 | 314.9566 | 393.9566 | 461.0121 | 392.1189 | NaN | NaN | NaN | 662.1802 | 1254.9286 | NaN | NaN | 1253.6579 | NaN | NaN | NaN | NaN | 1253.7893 | 1254.3586 | NaN | 17.4698 | NaN | 24.7747
9463.1292 | 742.3594 | 542.5755 | 303.7551 | 301.9809 | 314.731 | 393.203 | 460.376 | 391.645 | NaN | NaN | NaN | 662.8439 | 1254.9287 | NaN | NaN | 1253.658 | NaN | NaN | NaN | NaN | 1253.7894 | 1254.3587 | NaN | 16.9162 | NaN | 23.3938
9464.1292 | 741.3649 | 541.3079 | 303.0683 | 301.9025 | 314.7673 | 393.4729 | 460.0858 | 393.0466 | NaN | NaN | NaN | 654.0939 | 1254.9286 | NaN | NaN | 1253.6579 | NaN | NaN | NaN | NaN | 1253.7893 | 1254.3586 | NaN | 17.0488 | NaN | 24.4938
9465.1292 | 739.4934 | 541.8564 | 303.4265 | 302.3679 | 315.0939 | 393.3593 | 460.5811 | 391.8802 | NaN | NaN | NaN | 647.4153 | 1254.9292 | NaN | NaN | 1253.6585 | NaN | NaN | NaN | NaN | 1253.7899 | 1254.3591 | NaN | 15.6956 | NaN | 24.5742
9466.1292 | 738.7781 | 541.7129 | 303.3239 | 301.8262 | 315.0339 | 393.061 | 460.3904 | 390.6988 | NaN | NaN | NaN | 644.8416 | 1254.9279 | NaN | NaN | 1253.6572 | NaN | NaN | NaN | NaN | 1253.7886 | 1254.3579 | NaN | 18.7296 | NaN | 24.6766
9467.1292 | 739.5899 | 541.2792 | 303.5543 | 302.0399 | 315.3517 | 394.2845 | 460.2201 | 390.3858 | NaN | NaN | NaN | 651.7367 | 1254.9281 | NaN | NaN | 1253.6574 | NaN | NaN | NaN | NaN | 1253.7888 | 1254.3581 | NaN | 19.1666 | NaN | 23.9958
9468.1292 | 738.865 | 541.7526 | 303.9124 | 303.1821 | 315.6997 | 397.0388 | 461.3442 | 390.3727 | NaN | NaN | NaN | 665.9155 | 1254.9273 | NaN | NaN | 1253.6566 | NaN | NaN | NaN | NaN | 1253.788 | 1254.3573 | NaN | 19.2573 | NaN | 23.3968
9469.1292 | 737.8896 | 540.1125 | 304.7003 | 303.1536 | 315.3801 | 396.5949 | 460.1613 | 390.3172 | NaN | NaN | NaN | 660.9687 | 1254.927 | NaN | NaN | 1253.6563 | NaN | NaN | NaN | NaN | 1253.7877 | 1254.357 | NaN | 17.8148 | NaN | 25.2738
9470.1292 | 738.6454 | 540.4913 | 305.1765 | 303.1642 | 315.2063 | 395.3822 | 459.6517 | 389.6282 | NaN | NaN | NaN | 675.6348 | 1254.9279 | NaN | NaN | 1253.6572 | NaN | NaN | NaN | NaN | 1253.7886 | 1254.3579 | NaN | 15.2308 | NaN | 22.7396
9471.1292 | 737.6607 | 541.9971 | 304.9823 | 302.9024 | 315.1859 | 395.5712 | 460.5862 | 390.2497 | NaN | NaN | NaN | 654.9222 | 1254.9283 | NaN | NaN | 1253.6576 | NaN | NaN | NaN | NaN | 1253.789 | 1254.3582 | NaN | 17.3703 | NaN | 23.2089
9472.1292 | 737.0419 | 541.831 | 304.8242 | 302.624 | 314.9375 | 394.176 | 460.5159 | 389.4444 | NaN | NaN | NaN | 660.5408 | 1254.9287 | NaN | NaN | 1253.658 | NaN | NaN | NaN | NaN | 1253.7894 | 1254.3587 | NaN | 16.2085 | NaN | 24.1127
9473.1292 | 736.3344 | 540.2339 | 304.6646 | 302.7966 | 314.759 | 393.7595 | 460.6241 | 389.7125 | NaN | NaN | NaN | 672.7646 | 1254.9266 | NaN | NaN | 1253.656 | NaN | NaN | NaN | NaN | 1253.7873 | 1254.3566 | NaN | 17.955 | NaN | 23.5079
9474.1292 | 735.2278 | 539.9262 | 304.3524 | 302.8317 | 314.8151 | 393.2089 | 460.0655 | 389.1493 | NaN | NaN | NaN | 665.3573 | 1254.9268 | NaN | NaN | 1253.6561 | NaN | NaN | NaN | NaN | 1253.7875 | 1254.3568 | NaN | 18.3853 | NaN | 24.4792
9475.1292 | 735.6864 | 539.3825 | 304.0855 | 302.4201 | 314.6666 | 394.2017 | 460.166 | 389.0302 | NaN | NaN | NaN | 671.359 | 1254.9265 | NaN | NaN | 1253.6558 | NaN | NaN | NaN | NaN | 1253.7872 | 1254.3565 | NaN | 16.2182 | NaN | 24.5279
9476.1292 | 736.3906 | 539.2136 | 303.5472 | 301.9487 | 314.7285 | 395.222 | 460.1665 | 388.7858 | NaN | NaN | NaN | 665.1025 | 1254.9266 | NaN | NaN | 1253.6559 | NaN | NaN | NaN | NaN | 1253.7873 | 1254.3565 | NaN | 18.2491 | NaN | 22.874
9477.1292 | 736.3082 | 539.1357 | 303.7818 | 302.3595 | 314.3801 | 395.2035 | 459.5184 | 388.0323 | NaN | NaN | NaN | 654.2968 | 1254.9266 | NaN | NaN | 1253.6559 | NaN | NaN | NaN | NaN | 1253.7873 | 1254.3565 | NaN | 18.7555 | NaN | 23.3448
9478.1292 | 736.7701 | 539.7244 | 304.0855 | 302.299 | 314.2692 | 395.3225 | 459.1246 | 387.6153 | NaN | NaN | NaN | 625.805 | 1254.926 | NaN | NaN | 1253.6553 | NaN | NaN | NaN | NaN | 1253.7867 | 1254.356 | NaN | 18.1225 | NaN | 24.9808
9479.1292 | 736.6071 | 539.3553 | 303.548 | 301.8808 | 314.1799 | 396.4214 | 459.2971 | 389.1485 | NaN | NaN | NaN | 617.0865 | 1254.9267 | NaN | NaN | 1253.656 | NaN | NaN | NaN | NaN | 1253.7874 | 1254.3567 | NaN | 14.5693 | NaN | 22.2901
9480.1292 | 737.57 | 538.8532 | 304.0862 | 301.5012 | 314.1251 | 395.8383 | 459.5169 | 389.4126 | NaN | NaN | NaN | 625.4362 | 1254.9266 | NaN | NaN | 1253.656 | NaN | NaN | NaN | NaN | 1253.7873 | 1254.3566 | NaN | 17.4804 | NaN | 24.4661
9481.1292 | 737.7837 | 540.3464 | 304.4062 | 301.9005 | 314.5053 | 395.3336 | 460.4396 | 389.1559 | NaN | NaN | NaN | 620.4704 | 1254.9256 | NaN | NaN | 1253.6549 | NaN | NaN | NaN | NaN | 1253.7863 | 1254.3555 | NaN | 18.9313 | NaN | 24.9776
9482.1292 | 736.6621 | 540.3911 | 303.8397 | 302.5401 | 314.6751 | 394.6169 | 459.8298 | 389.5615 | NaN | NaN | NaN | 604.5763 | 1254.9266 | NaN | NaN | 1253.6559 | NaN | NaN | NaN | NaN | 1253.7873 | 1254.3566 | NaN | 18.4664 | NaN | 23.9836
9483.1292 | 735.298 | 540.3295 | 303.509 | 302.5773 | 314.5799 | 393.8616 | 456.9785 | 388.5997 | NaN | NaN | NaN | 587.0248 | 1254.9257 | NaN | NaN | 1253.655 | NaN | NaN | NaN | NaN | 1253.7864 | 1254.3557 | NaN | 19.3031 | NaN | 24.0814
9484.1292 | 734.8351 | 541.0718 | 303.3266 | 302.0287 | 314.4557 | 394.0838 | 456.4583 | 388.091 | NaN | NaN | NaN | 573.0151 | 1254.9265 | NaN | NaN | 1253.6558 | NaN | NaN | NaN | NaN | 1253.7872 | 1254.3565 | NaN | 19.38 | NaN | 24.4995
9485.1292 | 735.0997 | 540.8271 | 303.1356 | 301.5636 | 314.3424 | 393.1629 | 454.8707 | 386.5022 | NaN | NaN | NaN | 565.3611 | 1254.9262 | NaN | NaN | 1253.6555 | NaN | NaN | NaN | NaN | 1253.7869 | 1254.3562 | NaN | 16.0108 | NaN | 23.5765
9486.1292 | 734.0723 | 539.9786 | 302.7638 | 301.4672 | 313.8253 | 393.4989 | 453.1126 | 385.6758 | NaN | NaN | NaN | 555.0017 | 1254.9261 | NaN | NaN | 1253.6555 | NaN | NaN | NaN | NaN | 1253.7868 | 1254.3561 | NaN | 17.0545 | NaN | 22.9037
9487.1292 | 733.1641 | 541.1345 | 302.5501 | 301.2719 | 313.965 | 392.3148 | 452.8783 | 386.5667 | NaN | NaN | NaN | 542.0096 | 1254.9249 | NaN | NaN | 1253.6542 | NaN | NaN | NaN | NaN | 1253.7856 | 1254.3549 | NaN | 18.5288 | NaN | 23.6438
9488.1292 | 732.3724 | 542.5673 | 302.948 | 301.0175 | 313.5814 | 391.4607 | 451.9818 | 387.1125 | NaN | NaN | NaN | 543.6416 | 1254.9255 | NaN | NaN | 1253.6548 | NaN | NaN | NaN | NaN | 1253.7862 | 1254.3555 | NaN | 19.2692 | NaN | 23.7465
9489.1292 | 732.5368 | 543.2285 | 302.7476 | 300.7417 | 313.0555 | 390.3726 | 451.7197 | 385.6119 | NaN | NaN | NaN | 546.1605 | 1254.9252 | NaN | NaN | 1253.6545 | NaN | NaN | NaN | NaN | 1253.7859 | 1254.3552 | NaN | 19.3957 | NaN | 24.6373
9490.1292 | 734.6197 | 541.3361 | 302.7777 | 300.5852 | 312.9755 | 390.9036 | 451.6728 | 385.9722 | NaN | NaN | NaN | 573.7217 | 1254.9255 | NaN | NaN | 1253.6548 | NaN | NaN | NaN | NaN | 1253.7862 | 1254.3555 | NaN | 19.234 | NaN | 24.1013
9491.1292 | 735.6824 | 539.9334 | 303.1296 | 300.4863 | 312.8428 | 390.6461 | 451.9259 | 386.2575 | NaN | NaN | NaN | 595.6567 | 1254.9248 | NaN | NaN | 1253.6541 | NaN | NaN | NaN | NaN | 1253.7854 | 1254.3547 | NaN | 16.6007 | NaN | 23.6817
9492.1292 | 736.3163 | 539.2251 | 303.0048 | 300.484 | 312.796 | 390.0387 | 452.5656 | 386.7883 | NaN | NaN | NaN | 606.5999 | 1254.9253 | NaN | NaN | 1253.6546 | NaN | NaN | NaN | NaN | 1253.786 | 1254.3553 | NaN | 19.2476 | NaN | 23.3572
9493.1292 | 738.1736 | 538.7368 | 302.7614 | 300.512 | 312.8592 | 390.2446 | 454.7513 | 388.3349 | NaN | NaN | NaN | 608.2844 | 1254.9241 | NaN | NaN | 1253.6535 | NaN | NaN | NaN | NaN | 1253.7848 | 1254.3541 | NaN | 19.12 | NaN | 23.784
9494.1292 | 738.4921 | 540.3446 | 303.2817 | 300.9048 | 312.8162 | 390.8903 | 455.3841 | 390.4828 | NaN | NaN | NaN | 594.039 | 1254.925 | NaN | NaN | 1253.6543 | NaN | NaN | NaN | NaN | 1253.7857 | 1254.355 | NaN | 17.372 | NaN | 22.8814
9495.1292 | 739.4795 | 541.9483 | 303.1592 | 300.6209 | 312.6832 | 390.1335 | 456.0201 | 393.0578 | NaN | NaN | NaN | 584.0217 | 1254.9248 | NaN | NaN | 1253.6541 | NaN | NaN | NaN | NaN | 1253.7854 | 1254.3547 | NaN | 18.5954 | NaN | 24.2522
9496.1292 | 740.5249 | 542.4869 | 303.5044 | 301.7073 | 312.8177 | 390.3211 | 457.3693 | 395.6789 | NaN | NaN | NaN | 565.2772 | 1254.9243 | NaN | NaN | 1253.6536 | NaN | NaN | NaN | NaN | 1253.785 | 1254.3543 | NaN | 15.5313 | NaN | 22.6387
9497.1292 | 740.9748 | 542.4333 | 303.5726 | 302.6282 | 313.1984 | 390.4487 | 458.0289 | 395.5911 | NaN | NaN | NaN | 567.3358 | 1254.924 | NaN | NaN | 1253.6533 | NaN | NaN | NaN | NaN | 1253.7847 | 1254.354 | NaN | 18.7779 | NaN | 23.5997
9498.1292 | 742.1497 | 542.614 | 304.3172 | 302.6479 | 313.4209 | 392.1433 | 459.0159 | 396.119 | NaN | NaN | NaN | 578.1358 | 1254.9239 | NaN | NaN | 1253.6532 | NaN | NaN | NaN | NaN | 1253.7846 | 1254.3538 | NaN | 18.5808 | NaN | 25.2396
9499.1292 | 743.6476 | 541.3023 | 304.5079 | 302.4185 | 314.3471 | 392.4796 | 458.1064 | 396.4816 | NaN | NaN | NaN | 560.7476 | 1254.9247 | NaN | NaN | 1253.654 | NaN | NaN | NaN | NaN | 1253.7854 | 1254.3547 | NaN | 17.8636 | NaN | 25.0682
9500.1292 | 743.401 | 541.2304 | 304.8496 | 302.5538 | 314.5098 | 392.2853 | 458.8416 | 395.7343 | NaN | NaN | NaN | 552.1901 | 1254.9235 | NaN | NaN | 1253.6528 | NaN | NaN | NaN | NaN | 1253.7842 | 1254.3535 | NaN | 18.4061 | NaN | 25.2958
9501.1292 | 743.3653 | 541.8993 | 305.589 | 302.9933 | 315.179 | 392.8413 | 458.7612 | 394.9714 | NaN | NaN | NaN | 552.8591 | 1254.924 | NaN | NaN | 1253.6533 | NaN | NaN | NaN | NaN | 1253.7847 | 1254.354 | NaN | 19.1968 | NaN | 23.3482
9502.1292 | 743.1467 | 545.392 | 304.5784 | 302.598 | 315.2319 | 392.3216 | 458.0829 | 394.9977 | NaN | NaN | NaN | 540.4238 | 1254.9242 | NaN | NaN | 1253.6535 | NaN | NaN | NaN | NaN | 1253.7849 | 1254.3542 | NaN | 19.6251 | NaN | 25.0356
9503.1292 | 742.8692 | 547.945 | 304.5856 | 303.0465 | 315.9936 | 392.1909 | 460.5638 | 396.3461 | NaN | NaN | NaN | 540.7737 | 1254.9237 | NaN | NaN | 1253.6531 | NaN | NaN | NaN | NaN | 1253.7844 | 1254.3537 | NaN | 18.374 | NaN | 23.2886
9504.1292 | 742.5347 | 549.3711 | 305.1399 | 303.7508 | 316.9846 | 391.9305 | 460.8876 | 396.1327 | NaN | NaN | NaN | 566.5431 | 1254.9241 | NaN | NaN | 1253.6535 | NaN | NaN | NaN | NaN | 1253.7848 | 1254.3541 | NaN | 17.938 | NaN | 25.0753
9505.1292 | 742.2294 | 548.3887 | 305.1298 | 303.7283 | 317.1369 | 392.0908 | 460.9004 | 397.1597 | NaN | NaN | NaN | 575.4488 | 1254.9231 | NaN | NaN | 1253.6524 | NaN | NaN | NaN | NaN | 1253.7837 | 1254.353 | NaN | 18.0692 | NaN | 23.0843
9506.1292 | 740.3528 | 548.4411 | 305.0854 | 304.104 | 317.3239 | 391.7038 | 459.3575 | 397.3617 | NaN | NaN | NaN | 603.4114 | 1254.9229 | NaN | NaN | 1253.6522 | NaN | NaN | NaN | NaN | 1253.7836 | 1254.3529 | NaN | 18.781 | NaN | 24.6017
9507.1292 | 739.155 | 548.0295 | 305.0497 | 304.4296 | 317.0421 | 392.9734 | 460.6602 | 396.4619 | NaN | NaN | NaN | 612.7658 | 1254.9234 | NaN | NaN | 1253.6527 | NaN | NaN | NaN | NaN | 1253.7841 | 1254.3533 | NaN | 17.9663 | NaN | 23.2443
9508.1292 | 738.9374 | 545.1167 | 304.9903 | 304.5004 | 317.3113 | 394.8269 | 460.5291 | 395.7754 | NaN | NaN | NaN | 632.5369 | 1254.9215 | NaN | NaN | 1253.6509 | NaN | NaN | NaN | NaN | 1253.7822 | 1254.3515 | NaN | 17.9454 | NaN | 23.4125
9509.1292 | 737.8229 | 544.3856 | 305.2371 | 304.2101 | 317.1642 | 394.7812 | 461.0944 | 394.65 | NaN | NaN | NaN | 608.7945 | 1254.9226 | NaN | NaN | 1253.6519 | NaN | NaN | NaN | NaN | 1253.7833 | 1254.3526 | NaN | 19.7768 | NaN | 23.8846
9510.1292 | 736.0268 | 543.3678 | 305.5936 | 304.4499 | 317.37 | 397.0022 | 459.9253 | 394.7975 | NaN | NaN | NaN | 619.906 | 1254.923 | NaN | NaN | 1253.6523 | NaN | NaN | NaN | NaN | 1253.7837 | 1254.353 | NaN | 19.1048 | NaN | 24.4184
9511.1292 | 735.5468 | 542.553 | 305.2994 | 305.0695 | 317.1487 | 397.467 | 459.0892 | 394.2156 | NaN | NaN | NaN | 635.8678 | 1254.9224 | NaN | NaN | 1253.6517 | NaN | NaN | NaN | NaN | 1253.7831 | 1254.3523 | NaN | 18.2903 | NaN | 23.8491
9512.1292 | 734.6833 | 541.7744 | 304.8434 | 304.7537 | 317.0165 | 397.1189 | 460.6391 | 393.9147 | NaN | NaN | NaN | 642.792 | 1254.922 | NaN | NaN | 1253.6513 | NaN | NaN | NaN | NaN | 1253.7827 | 1254.352 | NaN | 17.8936 | NaN | 24.5099
9513.1292 | 733.2244 | 542.1318 | 305.5872 | 305.2538 | 317.6402 | 395.2993 | 458.1457 | 393.7932 | NaN | NaN | NaN | 633.2742 | 1254.9222 | NaN | NaN | 1253.6515 | NaN | NaN | NaN | NaN | 1253.7829 | 1254.3522 | NaN | 15.712 | NaN | 23.1238
9514.1292 | 733.8419 | 541.5313 | 305.2453 | 305.0081 | 317.8298 | 393.2715 | 455.8449 | 393.1766 | NaN | NaN | NaN | 632.7185 | 1254.9232 | NaN | NaN | 1253.6526 | NaN | NaN | NaN | NaN | 1253.7839 | 1254.3532 | NaN | 17.6762 | NaN | 24.8172
9515.1292 | 733.5453 | 542.2796 | 305.3632 | 304.8782 | 317.8183 | 393.0445 | 456.2601 | 394.5351 | NaN | NaN | NaN | 653.495 | 1254.9229 | NaN | NaN | 1253.6522 | NaN | NaN | NaN | NaN | 1253.7836 | 1254.3528 | NaN | 19.6315 | NaN | 24.0855
9516.1292 | 733.0935 | 540.6278 | 305.5274 | 304.6019 | 317.4223 | 393.4925 | 456.1939 | 393.5106 | NaN | NaN | NaN | 662.6537 | 1254.922 | NaN | NaN | 1253.6514 | NaN | NaN | NaN | NaN | 1253.7827 | 1254.352 | NaN | 18.9032 | NaN | 23.47
9517.1292 | 733.1581 | 540.8723 | 305.5758 | 304.3917 | 316.9431 | 395.9313 | 456.4028 | 393.1093 | NaN | NaN | NaN | 668.3569 | 1254.9225 | NaN | NaN | 1253.6518 | NaN | NaN | NaN | NaN | 1253.7832 | 1254.3525 | NaN | 19.5944 | NaN | 24.8289
9518.1292 | 733.0352 | 530.8901 | 305.5675 | 304.4126 | 317.0214 | 398.1792 | 452.1357 | 392.1979 | NaN | NaN | NaN | 665.1117 | 1254.9209 | NaN | NaN | 1253.6502 | NaN | NaN | NaN | NaN | 1253.7816 | 1254.3509 | NaN | 19.163 | NaN | 23.4815
9519.1292 | 734.6842 | 531.3136 | 305.7639 | 303.9865 | 316.8658 | 398.7972 | 451.2347 | 391.0758 | NaN | NaN | NaN | 664.4948 | 1254.9207 | NaN | NaN | 1253.6501 | NaN | NaN | NaN | NaN | 1253.7814 | 1254.3507 | NaN | 17.7624 | NaN | 23.3811
9520.1292 | 735.0042 | 543.0525 | 306.184 | 304.8093 | 316.7798 | 399.9864 | 459.2797 | 392.8374 | NaN | NaN | NaN | 658.951 | 1254.9217 | NaN | NaN | 1253.6511 | NaN | NaN | NaN | NaN | 1253.7824 | 1254.3517 | NaN | 16.162 | NaN | 22.7609
9521.1292 | 733.431 | 543.2846 | 307.2375 | 305.4513 | 316.6813 | 400.3712 | 460.9452 | 393.3533 | NaN | NaN | NaN | 651.7369 | 1254.9217 | NaN | NaN | 1253.651 | NaN | NaN | NaN | NaN | 1253.7824 | 1254.3516 | NaN | 17.065 | NaN | 25.1529
9522.1292 | 731.6394 | 543.4074 | 307.4803 | 305.0204 | 316.7222 | 398.9733 | 461.6458 | 393.6866 | NaN | NaN | NaN | 669.7802 | 1254.9224 | NaN | NaN | 1253.6517 | NaN | NaN | NaN | NaN | 1253.7831 | 1254.3524 | NaN | 19.6221 | NaN | 24.6681
9523.1292 | 731.1188 | 547.0123 | 307.4334 | 305.0378 | 316.8566 | 397.3892 | 463.3073 | 395.0143 | NaN | NaN | NaN | 678.8245 | 1254.922 | NaN | NaN | 1253.6514 | NaN | NaN | NaN | NaN | 1253.7827 | 1254.352 | NaN | 18.335 | NaN | 23.8668
9524.1292 | 731.8575 | 548.5754 | 307.6509 | 305.6988 | 317.2109 | 396.8776 | 464.3273 | 396.9531 | NaN | NaN | NaN | 662.2273 | 1254.9206 | NaN | NaN | 1253.6499 | NaN | NaN | NaN | NaN | 1253.7813 | 1254.3506 | NaN | 18.2051 | NaN | 24.6618
9525.1292 | 731.8437 | 550.0225 | 307.5448 | 306.0099 | 317.1529 | 396.3898 | 465.4253 | 397.1782 | NaN | NaN | NaN | 648.1509 | 1254.9208 | NaN | NaN | 1253.6502 | NaN | NaN | NaN | NaN | 1253.7815 | 1254.3508 | NaN | 19.0984 | NaN | 23.4734
9526.1292 | 732.5977 | 549.3863 | 307.3328 | 305.8977 | 317.2145 | 396.3439 | 464.1226 | 395.8634 | NaN | NaN | NaN | 639.931 | 1254.9201 | NaN | NaN | 1253.6494 | NaN | NaN | NaN | NaN | 1253.7808 | 1254.3501 | NaN | 18.0656 | NaN | 22.7778
9527.1292 | 734.1694 | 549.37 | 308.2782 | 305.9537 | 317.627 | 397.6349 | 462.8472 | 395.2358 | NaN | NaN | NaN | 652.4554 | 1254.9203 | NaN | NaN | 1253.6497 | NaN | NaN | NaN | NaN | 1253.781 | 1254.3503 | NaN | 17.642 | NaN | 24.2109
9528.1292 | 734.334 | 548.0226 | 307.9473 | 306.0087 | 317.877 | 398.4502 | 463.6389 | 395.108 | NaN | NaN | NaN | 675.4656 | 1254.9197 | NaN | NaN | 1253.649 | NaN | NaN | NaN | NaN | 1253.7804 | 1254.3497 | NaN | 18.5769 | NaN | 24.2685
9529.1292 | 735.389 | 549.2089 | 307.9747 | 306.1149 | 317.9324 | 399.5652 | 462.6804 | 394.4911 | NaN | NaN | NaN | 656.7781 | 1254.9195 | NaN | NaN | 1253.6489 | NaN | NaN | NaN | NaN | 1253.7802 | 1254.3495 | NaN | 17.4137 | NaN | 24.0603
9530.1292 | 737.2539 | 547.7818 | 308.2395 | 305.8972 | 317.709 | 401.1191 | 464.1118 | 395.7235 | NaN | NaN | NaN | 637.1826 | 1254.9207 | NaN | NaN | 1253.65 | NaN | NaN | NaN | NaN | 1253.7814 | 1254.3506 | NaN | 16.3148 | NaN | 22.2038
9531.1292 | 738.4174 | 549.1162 | 308.6943 | 305.7545 | 317.7303 | 401.744 | 463.9087 | 397.2301 | NaN | NaN | NaN | 643.6454 | 1254.9199 | NaN | NaN | 1253.6492 | NaN | NaN | NaN | NaN | 1253.7806 | 1254.3499 | NaN | 18.3689 | NaN | 23.4458
9532.1292 | 740.4237 | 548.7549 | 308.1788 | 305.9473 | 317.9195 | 402.3042 | 464.6193 | 397.0985 | NaN | NaN | NaN | 638.2822 | 1254.9194 | NaN | NaN | 1253.6487 | NaN | NaN | NaN | NaN | 1253.7801 | 1254.3494 | NaN | 18.9282 | NaN | 25.4404
9533.1292 | 740.4264 | 548.7171 | 308.5339 | 305.9034 | 318.2272 | 403.7437 | 465.0954 | 397.919 | NaN | NaN | NaN | 614.2383 | 1254.9193 | NaN | NaN | 1253.6486 | NaN | NaN | NaN | NaN | 1253.78 | 1254.3493 | NaN | 19.0267 | NaN | 25.0908
9534.1292 | 740.7954 | 548.7693 | 308.5538 | 305.9357 | 318.7668 | 402.7747 | 464.1187 | 396.9214 | NaN | NaN | NaN | 617.4806 | 1254.9192 | NaN | NaN | 1253.6485 | NaN | NaN | NaN | NaN | 1253.7799 | 1254.3492 | NaN | 18.3065 | NaN | 23.0838
9535.1292 | 741.8271 | 548.329 | 309.113 | 305.8654 | 318.7882 | 402.5522 | 464.7676 | 396.9737 | NaN | NaN | NaN | 634.0117 | 1254.9202 | NaN | NaN | 1253.6495 | NaN | NaN | NaN | NaN | 1253.7809 | 1254.3501 | NaN | 17.3167 | NaN | 23.7682
9536.1292 | 742.9421 | 549.0986 | 308.8975 | 306.1982 | 319.1491 | 401.6919 | 464.4777 | 397.8484 | NaN | NaN | NaN | 654.0144 | 1254.9193 | NaN | NaN | 1253.6486 | NaN | NaN | NaN | NaN | 1253.78 | 1254.3492 | NaN | 14.8622 | NaN | 24.7377
9537.1292 | 743.5077 | 550.1378 | 309.4213 | 306.6719 | 319.073 | 401.3743 | 466.6927 | 398.9928 | NaN | NaN | NaN | 657.0277 | 1254.9186 | NaN | NaN | 1253.6479 | NaN | NaN | NaN | NaN | 1253.7793 | 1254.3486 | NaN | 17.0207 | NaN | 25.1601
9538.1292 | 743.7293 | 551.0926 | 309.5322 | 307.182 | 319.1605 | 401.0971 | 466.4919 | 398.8516 | NaN | NaN | NaN | 656.5301 | 1254.9184 | NaN | NaN | 1253.6477 | NaN | NaN | NaN | NaN | 1253.7791 | 1254.3484 | NaN | 16.3562 | NaN | 24.4855
9539.1292 | 744.469 | 549.7966 | 309.5726 | 307.1464 | 319.055 | 401.6716 | 467.3935 | 399.603 | NaN | NaN | NaN | 646.8456 | 1254.919 | NaN | NaN | 1253.6483 | NaN | NaN | NaN | NaN | 1253.7797 | 1254.349 | NaN | 19.2166 | NaN | 23.8766
9540.1292 | 744.5964 | 550.874 | 309.447 | 307.5043 | 318.9587 | 400.984 | 467.52 | 401.3565 | NaN | NaN | NaN | 664.3932 | 1254.9188 | NaN | NaN | 1253.6482 | NaN | NaN | NaN | NaN | 1253.7795 | 1254.3488 | NaN | 18.9011 | NaN | 25.4444
9541.1292 | 743.6883 | 552.455 | 309.1574 | 307.3372 | 318.9788 | 399.8277 | 468.4231 | 403.1484 | NaN | NaN | NaN | 655.3804 | 1254.918 | NaN | NaN | 1253.6473 | NaN | NaN | NaN | NaN | 1253.7787 | 1254.348 | NaN | 18.7901 | NaN | 24.042
9542.1292 | 744.4769 | 554.6979 | 309.2263 | 307.7035 | 319.0908 | 399.9552 | 467.7177 | 406.9778 | NaN | NaN | NaN | 668.416 | 1254.9185 | NaN | NaN | 1253.6478 | NaN | NaN | NaN | NaN | 1253.7792 | 1254.3485 | NaN | 17.316 | NaN | 23.1442
9543.1292 | 747.1446 | 557.4202 | 309.2395 | 307.4285 | 319.2116 | 399.0163 | 468.1559 | 407.0398 | NaN | NaN | NaN | 682.8161 | 1254.9179 | NaN | NaN | 1253.6472 | NaN | NaN | NaN | NaN | 1253.7786 | 1254.3479 | NaN | 18.1563 | NaN | 24.3886
9544.1292 | 749.1472 | 560.5096 | 309.3127 | 307.6777 | 319.6092 | 400.1115 | 469.6133 | 409.6838 | NaN | NaN | NaN | 702.3528 | 1254.9185 | NaN | NaN | 1253.6478 | NaN | NaN | NaN | NaN | 1253.7792 | 1254.3484 | NaN | 19.4871 | NaN | 23.2305
9545.1292 | 750.8309 | 560.1702 | 309.1895 | 308.1833 | 319.8663 | 401.7055 | 472.2063 | 411.6545 | NaN | NaN | NaN | 687.8511 | 1254.9182 | NaN | NaN | 1253.6475 | NaN | NaN | NaN | NaN | 1253.7789 | 1254.3482 | NaN | 18.3363 | NaN | 25.1843
9546.1292 | 751.6619 | 558.912 | 309.1733 | 308.7897 | 320.5724 | 401.6911 | 473.8546 | 411.503 | NaN | NaN | NaN | 683.0904 | 1254.9172 | NaN | NaN | 1253.6465 | NaN | NaN | NaN | NaN | 1253.7779 | 1254.3472 | NaN | 15.6685 | NaN | 22.612
9547.1292 | 752.7623 | 561.3246 | 309.9477 | 308.9864 | 321.0546 | 400.8364 | 474.8217 | 413.5015 | NaN | NaN | NaN | 663.9834 | 1254.918 | NaN | NaN | 1253.6473 | NaN | NaN | NaN | NaN | 1253.7787 | 1254.348 | NaN | 16.6038 | NaN | 22.99
9548.1292 | 751.6641 | 563.7729 | 310.6446 | 308.9743 | 321.6228 | 400.203 | 476.2728 | 415.0193 | NaN | NaN | NaN | 658.6701 | 1254.9181 | NaN | NaN | 1253.6474 | NaN | NaN | NaN | NaN | 1253.7788 | 1254.3481 | NaN | 15.6467 | NaN | 23.1474
9549.1292 | 751.6171 | 568.515 | 310.1525 | 309.0089 | 322.0767 | 399.3033 | 475.2934 | 415.4137 | NaN | NaN | NaN | 644.3191 | 1254.9173 | NaN | NaN | 1253.6466 | NaN | NaN | NaN | NaN | 1253.778 | 1254.3472 | NaN | 17.0811 | NaN | 23.2436
9550.1292 | 751.7412 | 570.481 | 310.6118 | 309.3544 | 322.5608 | 397.9643 | 474.0172 | 416.659 | NaN | NaN | NaN | 642.0451 | 1254.9176 | NaN | NaN | 1253.6469 | NaN | NaN | NaN | NaN | 1253.7783 | 1254.3475 | NaN | 17.722 | NaN | 24.0711
9551.1292 | 750.8017 | 575.5233 | 310.9734 | 309.9481 | 323.2314 | 397.1411 | 474.1404 | 420.3188 | NaN | NaN | NaN | 638.4703 | 1254.918 | NaN | NaN | 1253.6473 | NaN | NaN | NaN | NaN | 1253.7787 | 1254.348 | NaN | 18.2539 | NaN | 23.2034
9552.1292 | 750.7228 | 580.8805 | 311.6622 | 310.0044 | 323.9379 | 396.8196 | 473.8719 | 423.0477 | NaN | NaN | NaN | 617.3401 | 1254.9165 | NaN | NaN | 1253.6458 | NaN | NaN | NaN | NaN | 1253.7772 | 1254.3465 | NaN | 17.01 | NaN | 23.5708
9553.1292 | 748.549 | 584.2009 | 311.4933 | 310.7988 | 324.9654 | 396.6987 | 472.2128 | 425.8095 | NaN | NaN | NaN | 613.1918 | 1254.9166 | NaN | NaN | 1253.6459 | NaN | NaN | NaN | NaN | 1253.7773 | 1254.3466 | NaN | 14.9311 | NaN | 23.4706
9554.1292 | 747.589 | 584.623 | 312.0776 | 310.9866 | 325.1076 | 395.7947 | 469.8477 | 425.3949 | NaN | NaN | NaN | 625.7842 | 1254.9174 | NaN | NaN | 1253.6467 | NaN | NaN | NaN | NaN | 1253.7781 | 1254.3473 | NaN | 19.376 | NaN | 24.0057
9555.1292 | 747.4571 | 587.0845 | 312.6723 | 311.6005 | 325.2891 | 395.3056 | 469.4473 | 425.0091 | NaN | NaN | NaN | 616.3492 | 1254.917 | NaN | NaN | 1253.6463 | NaN | NaN | NaN | NaN | 1253.7777 | 1254.347 | NaN | 19.3165 | NaN | 25.0291
9556.1292 | 748.0452 | 586.894 | 312.3101 | 311.9587 | 325.6493 | 394.5863 | 469.9844 | 425.0506 | NaN | NaN | NaN | 631.0776 | 1254.9174 | NaN | NaN | 1253.6467 | NaN | NaN | NaN | NaN | 1253.7781 | 1254.3474 | NaN | 15.5837 | NaN | 23.0126
9557.1292 | 749.9773 | 586.0609 | 312.8096 | 311.6631 | 326.1239 | 393.8255 | 469.1581 | 424.8362 | NaN | NaN | NaN | 615.4292 | 1254.9154 | NaN | NaN | 1253.6447 | NaN | NaN | NaN | NaN | 1253.7761 | 1254.3453 | NaN | 19.9828 | NaN | 24.4559
9558.1292 | 751.5773 | 584.877 | 312.8214 | 311.8651 | 325.8833 | 393.6675 | 469.3758 | 426.5377 | NaN | NaN | NaN | 628.3947 | 1254.9166 | NaN | NaN | 1253.6459 | NaN | NaN | NaN | NaN | 1253.7773 | 1254.3465 | NaN | 16.9615 | NaN | 25.0069
9559.1292 | 754.4177 | 580.337 | 312.7767 | 312.209 | 326.0896 | 394.406 | 471.5272 | 427.5734 | NaN | NaN | NaN | 632.5445 | 1254.9156 | NaN | NaN | 1253.6449 | NaN | NaN | NaN | NaN | 1253.7763 | 1254.3455 | NaN | 17.8938 | NaN | 23.7984
9560.1292 | 756.1398 | 576.9057 | 313.2248 | 312.3374 | 326.2871 | 395.033 | 475.0109 | 428.4868 | NaN | NaN | NaN | 642.0448 | 1254.9162 | NaN | NaN | 1253.6455 | NaN | NaN | NaN | NaN | 1253.7769 | 1254.3462 | NaN | 16.969 | NaN | 24.176
9561.1292 | 756.3268 | 578.1906 | 313.7226 | 312.8628 | 326.8547 | 396.0113 | 478.267 | 430.292 | NaN | NaN | NaN | 640.9858 | 1254.9165 | NaN | NaN | 1253.6458 | NaN | NaN | NaN | NaN | 1253.7772 | 1254.3465 | NaN | 19.387 | NaN | 23.5173
9562.1292 | 756.6123 | 577.3207 | 314.0002 | 313.4331 | 327.3067 | 395.7466 | 478.355 | 429.3641 | NaN | NaN | NaN | 636.6704 | 1254.9154 | NaN | NaN | 1253.6447 | NaN | NaN | NaN | NaN | 1253.7761 | 1254.3453 | NaN | 17.9497 | NaN | 22.4087
9563.1292 | 756.941 | 578.2655 | 314.0642 | 314.3149 | 327.6841 | 396.325 | 479.8831 | 429.8906 | NaN | NaN | NaN | 642.1188 | 1254.9149 | NaN | NaN | 1253.6443 | NaN | NaN | NaN | NaN | 1253.7756 | 1254.3449 | NaN | 18.0346 | NaN | 24.7095
9564.1292 | 758.1214 | 581.029 | 314.104 | 313.8311 | 327.8533 | 396.4547 | 479.7151 | 430.5469 | NaN | NaN | NaN | 659.6866 | 1254.9151 | NaN | NaN | 1253.6444 | NaN | NaN | NaN | NaN | 1253.7758 | 1254.345 | NaN | 18.7008 | NaN | 24.2124
9565.1292 | 757.926 | 579.0846 | 314.9432 | 314.122 | 328.278 | 397.8535 | 482.4318 | 430.2495 | NaN | NaN | NaN | 638.9585 | 1254.9149 | NaN | NaN | 1253.6443 | NaN | NaN | NaN | NaN | 1253.7756 | 1254.3449 | NaN | 19.3097 | NaN | 24.9816
9566.1292 | 755.8259 | 575.8657 | 314.75 | 314.3441 | 328.534 | 398.4801 | 483.467 | 430.0958 | NaN | NaN | NaN | 631.8543 | 1254.9142 | NaN | NaN | 1253.6436 | NaN | NaN | NaN | NaN | 1253.7749 | 1254.3442 | NaN | 17.6772 | NaN | 23.0543
9567.1292 | 753.5619 | 571.8181 | 315.2295 | 314.5801 | 328.5099 | 400.7334 | 482.6848 | 428.1307 | NaN | NaN | NaN | 614.7703 | 1254.9146 | NaN | NaN | 1253.6439 | NaN | NaN | NaN | NaN | 1253.7753 | 1254.3446 | NaN | 18.8864 | NaN | 24.8096
9568.1292 | 750.7619 | 569.8296 | 315.5362 | 314.926 | 328.3356 | 402.9314 | 481.6005 | 425.2515 | NaN | NaN | NaN | 647.7171 | 1254.9149 | NaN | NaN | 1253.6442 | NaN | NaN | NaN | NaN | 1253.7756 | 1254.3449 | NaN | 18.9589 | NaN | 24.7017
9569.1292 | 750.1184 | 569.1892 | 315.4686 | 314.9837 | 327.9487 | 405.2476 | 480.9222 | 423.7025 | NaN | NaN | NaN | 645.6742 | 1254.9146 | NaN | NaN | 1253.6439 | NaN | NaN | NaN | NaN | 1253.7753 | 1254.3446 | NaN | 19.5675 | NaN | 23.689
9570.1292 | 749.4351 | 566.5094 | 316.0545 | 314.6329 | 327.7557 | 407.9267 | 481.0781 | 422.7227 | NaN | NaN | NaN | 648.2588 | 1254.9153 | NaN | NaN | 1253.6446 | NaN | NaN | NaN | NaN | 1253.776 | 1254.3453 | NaN | 16.9309 | NaN | 24.9682
9571.1292 | 748.4945 | 565.0129 | 316.1174 | 314.7384 | 327.5803 | 409.426 | 481.2658 | 420.2699 | NaN | NaN | NaN | 623.2119 | 1254.9145 | NaN | NaN | 1253.6439 | NaN | NaN | NaN | NaN | 1253.7753 | 1254.3445 | NaN | 18.2123 | NaN | 23.4527
9572.1292 | 747.4135 | 562.3004 | 316.0335 | 314.9525 | 327.6254 | 409.59 | 480.5271 | 418.3735 | NaN | NaN | NaN | 652.352 | 1254.9139 | NaN | NaN | 1253.6433 | NaN | NaN | NaN | NaN | 1253.7746 | 1254.3439 | NaN | 17.5012 | NaN | 23.7934
9573.1292 | 746.3936 | 560.0654 | 316.1906 | 314.7106 | 327.2951 | 413.0221 | 480.3095 | 417.4532 | NaN | NaN | NaN | 659.9159 | 1254.9143 | NaN | NaN | 1253.6436 | NaN | NaN | NaN | NaN | 1253.775 | 1254.3443 | NaN | 17.356 | NaN | 22.4551
9574.1292 | 746.1469 | 558.8408 | 316.4663 | 314.2515 | 326.9591 | 414.8741 | 481.7072 | 416.8171 | NaN | NaN | NaN | 680.0316 | 1254.9142 | NaN | NaN | 1253.6436 | NaN | NaN | NaN | NaN | 1253.7749 | 1254.3442 | NaN | 16.6816 | NaN | 22.1718
9575.1292 | 746.0061 | 557.603 | 316.6865 | 314.6093 | 326.7241 | 415.3273 | 481.0299 | 415.4911 | NaN | NaN | NaN | 686.0909 | 1254.9147 | NaN | NaN | 1253.6441 | NaN | NaN | NaN | NaN | 1253.7754 | 1254.3447 | NaN | 17.3733 | NaN | 23.0455
9576.1292 | 747.8063 | 557.2566 | 317.1668 | 314.2823 | 326.47 | 415.1691 | 482.4925 | 414.657 | NaN | NaN | NaN | 690.3423 | 1254.9138 | NaN | NaN | 1253.6431 | NaN | NaN | NaN | NaN | 1253.7745 | 1254.3438 | NaN | 17.7569 | NaN | 22.6563
9577.1292 | 747.9972 | 555.839 | 317.1638 | 314.6408 | 326.3582 | 415.7154 | 484.2833 | 414.0601 | NaN | NaN | NaN | 677.5411 | 1254.9138 | NaN | NaN | 1253.6431 | NaN | NaN | NaN | NaN | 1253.7745 | 1254.3438 | NaN | 18.3057 | NaN | 23.9668
9578.1292 | 748.3745 | 557.3027 | 317.4019 | 314.6853 | 326.5164 | 415.9294 | 483.7433 | 414.9943 | NaN | NaN | NaN | 670.0476 | 1254.9144 | NaN | NaN | 1253.6437 | NaN | NaN | NaN | NaN | 1253.7751 | 1254.3443 | NaN | 17.8192 | NaN | 23.8333
9579.1292 | 748.576 | 557.3497 | 317.7405 | 314.3707 | 326.5013 | 415.8776 | 482.51 | 419.2909 | NaN | NaN | NaN | 692.8836 | 1254.9141 | NaN | NaN | 1253.6434 | NaN | NaN | NaN | NaN | 1253.7748 | 1254.3441 | NaN | 17.1798 | NaN | 22.2115
9580.1448 | 747.6655 | 559.1182 | 317.6931 | 314.096 | 326.55 | 414.8329 | 481.8123 | 420.9633 | NaN | NaN | NaN | 673.5353 | 1254.9138 | NaN | NaN | 1253.6431 | NaN | NaN | NaN | NaN | 1253.7745 | 1254.3438 | NaN | 17.1653 | NaN | 23.0657
9581.1448 | 747.7146 | 560.5022 | 317.6847 | 314.516 | 327.2586 | 413.6344 | 481.3395 | 421.4442 | NaN | NaN | NaN | 664.2521 | 1254.9136 | NaN | NaN | 1253.6429 | NaN | NaN | NaN | NaN | 1253.7743 | 1254.3436 | NaN | 18.6727 | NaN | 23.7913
9582.1292 | 747.5161 | 560.9863 | 316.8367 | 314.9257 | 327.321 | 413.7952 | 481.5254 | 422.4944 | NaN | NaN | NaN | 677.667 | 1254.9134 | NaN | NaN | 1253.6427 | NaN | NaN | NaN | NaN | 1253.7741 | 1254.3434 | NaN | 18.0608 | NaN | 25.0254
9583.1292 | 746.9787 | 564.6816 | 316.6237 | 315.9317 | 327.8102 | 411.6633 | 481.0598 | 424.6589 | NaN | NaN | NaN | 668.4595 | 1254.9127 | NaN | NaN | 1253.6421 | NaN | NaN | NaN | NaN | 1253.7734 | 1254.3427 | NaN | 18.243 | NaN | 23.9758
9584.1448 | 747.7232 | 564.8923 | 316.9602 | 316.1797 | 327.9304 | 410.9343 | 481.0549 | 425.9532 | NaN | NaN | NaN | 680.9211 | 1254.9127 | NaN | NaN | 1253.642 | NaN | NaN | NaN | NaN | 1253.7734 | 1254.3427 | NaN | 19.0208 | NaN | 24.5452
9585.1448 | 745.9226 | 566.3501 | 317.097 | 316.9059 | 328.3482 | 409.7922 | 483.1654 | 430.5874 | NaN | NaN | NaN | 680.7717 | 1254.9126 | NaN | NaN | 1253.6419 | NaN | NaN | NaN | NaN | 1253.7733 | 1254.3426 | NaN | 16.3005 | NaN | 23.7695
9586.1448 | 744.2184 | 568.0749 | 317.1704 | 317.4317 | 329.0347 | 408.0428 | 480.5627 | 430.3059 | NaN | NaN | NaN | 676.6719 | 1254.913 | NaN | NaN | 1253.6423 | NaN | NaN | NaN | NaN | 1253.7737 | 1254.343 | NaN | 15.5912 | NaN | 22.6483
9587.1448 | 743.6823 | 567.7611 | 316.7244 | 317.5007 | 329.7515 | 407.5403 | 480.6957 | 430.887 | NaN | NaN | NaN | 675.373 | 1254.9129 | NaN | NaN | 1253.6422 | NaN | NaN | NaN | NaN | 1253.7736 | 1254.3429 | NaN | 17.5519 | NaN | 24.1942
9588.1292 | 743.6399 | 566.2985 | 316.704 | 317.4021 | 330.0229 | 407.5098 | 480.6262 | 431.1434 | NaN | NaN | NaN | 647.6593 | 1254.9116 | NaN | NaN | 1253.641 | NaN | NaN | NaN | NaN | 1253.7724 | 1254.3416 | NaN | 18.0938 | NaN | 22.8785
9589.1292 | 742.6854 | 566.3841 | 317.1774 | 317.5563 | 329.7023 | 408.2116 | 483.0729 | 430.8096 | NaN | NaN | NaN | 618.9727 | 1254.9107 | NaN | NaN | 1253.64 | NaN | NaN | NaN | NaN | 1253.7714 | 1254.3407 | NaN | 16.3831 | NaN | 25.525
9590.1292 | 742.6249 | 565.7634 | 317.4768 | 318.2121 | 329.7877 | 408.7932 | 485.9539 | 429.8195 | NaN | NaN | NaN | 595.4387 | 1254.9109 | NaN | NaN | 1253.6402 | NaN | NaN | NaN | NaN | 1253.7716 | 1254.3409 | NaN | 17.9674 | NaN | 23.4933
9591.1292 | 742.8754 | 564.0152 | 317.4683 | 317.9182 | 329.7721 | 410.5505 | 487.0281 | 428.6012 | NaN | NaN | NaN | 616.3374 | 1254.9106 | NaN | NaN | 1253.64 | NaN | NaN | NaN | NaN | 1253.7713 | 1254.3406 | NaN | 17.537 | NaN | 23.7778
9592.1292 | 744.026 | 563.2108 | 316.8991 | 318.3875 | 329.6062 | 411.3196 | 486.4847 | 427.2906 | NaN | NaN | NaN | 642.9041 | 1254.91 | NaN | NaN | 1253.6394 | NaN | NaN | NaN | NaN | 1253.7707 | 1254.34 | NaN | 19.0018 | NaN | 23.3882
9593.1292 | 744.7397 | 560.7934 | 317.2002 | 317.4452 | 329.5386 | 414.0049 | 486.5707 | 427.056 | NaN | NaN | NaN | 651.4341 | 1254.9109 | NaN | NaN | 1253.6402 | NaN | NaN | NaN | NaN | 1253.7716 | 1254.3409 | NaN | 18.5942 | NaN | 24.2385
9594.1292 | 744.261 | 560.3546 | 318.1343 | 317.934 | 330.1283 | 414.707 | 486.887 | 425.8644 | NaN | NaN | NaN | 648.999 | 1254.9102 | NaN | NaN | 1253.6395 | NaN | NaN | NaN | NaN | 1253.7709 | 1254.3402 | NaN | 17.8921 | NaN | 24.8598
9595.1292 | 743.6702 | 558.8724 | 318.0717 | 317.9282 | 330.4336 | 415.4825 | 485.8197 | 424.2612 | NaN | NaN | NaN | 642.9113 | 1254.9095 | NaN | NaN | 1253.6388 | NaN | NaN | NaN | NaN | 1253.7702 | 1254.3395 | NaN | 18.1734 | NaN | 25.1613
9596.1292 | 743.4761 | 558.6262 | 318.3096 | 318.2309 | 329.9287 | 416.4316 | 485.6773 | 423.2423 | NaN | NaN | NaN | 679.9206 | 1254.9096 | NaN | NaN | 1253.639 | NaN | NaN | NaN | NaN | 1253.7703 | 1254.3396 | NaN | 17.1542 | NaN | 23.3327
9597.1448 | 743.7896 | 557.9999 | 318.5403 | 317.6655 | 329.5698 | 418.0978 | 484.7721 | 422.041 | NaN | NaN | NaN | 656.4593 | 1254.9097 | NaN | NaN | 1253.639 | NaN | NaN | NaN | NaN | 1253.7704 | 1254.3397 | NaN | 17.9404 | NaN | 24.5335
9598.1292 | 744.0978 | 556.242 | 318.5449 | 316.9979 | 329.5049 | 418.0786 | 484.4418 | 421.3345 | NaN | NaN | NaN | 645.0944 | 1254.9101 | NaN | NaN | 1253.6395 | NaN | NaN | NaN | NaN | 1253.7708 | 1254.3401 | NaN | 19.436 | NaN | 24.373
9599.1292 | 745.3996 | 555.4115 | 317.7982 | 317.2106 | 329.3838 | 418.233 | 485.9532 | 421.9047 | NaN | NaN | NaN | 628.955 | 1254.9096 | NaN | NaN | 1253.639 | NaN | NaN | NaN | NaN | 1253.7703 | 1254.3396 | NaN | 18.1117 | NaN | 24.7714
9600.1292 | 745.4192 | 554.7677 | 318.3689 | 317.8132 | 329.8908 | 418.8062 | 488.4587 | 422.5275 | NaN | NaN | NaN | 622.5076 | 1254.9094 | NaN | NaN | 1253.6388 | NaN | NaN | NaN | NaN | 1253.7702 | 1254.3394 | NaN | 18.0569 | NaN | 24.5891
9601.1292 | 744.2752 | 554.1811 | 318.3024 | 317.3557 | 329.8706 | 418.2386 | 486.7782 | 420.6121 | NaN | NaN | NaN | 603.7033 | 1254.9106 | NaN | NaN | 1253.64 | NaN | NaN | NaN | NaN | 1253.7713 | 1254.3406 | NaN | 18.1471 | NaN | 24.1825
9602.1292 | 745.0302 | 553.2484 | 318.7306 | 317.9341 | 329.7697 | 419.0493 | 485.9223 | 419.1431 | NaN | NaN | NaN | 587.4275 | 1254.9094 | NaN | NaN | 1253.6388 | NaN | NaN | NaN | NaN | 1253.7702 | 1254.3394 | NaN | 17.9682 | NaN | 23.7925
9603.1292 | 745.671 | 552.564 | 318.5141 | 318.1063 | 329.7147 | 421.2831 | 485.2279 | 417.8798 | NaN | NaN | NaN | 599.6795 | 1254.9084 | NaN | NaN | 1253.6378 | NaN | NaN | NaN | NaN | 1253.7691 | 1254.3384 | NaN | 18.8928 | NaN | 24.9225
9604.1292 | 746.2841 | 551.2622 | 318.9394 | 318.3542 | 329.7566 | 423.3507 | 486.4252 | 417.1783 | NaN | NaN | NaN | 644.5271 | 1254.9086 | NaN | NaN | 1253.6379 | NaN | NaN | NaN | NaN | 1253.7693 | 1254.3385 | NaN | 18.1923 | NaN | 23.5375
9605.1292 | 747.6295 | 551.6821 | 318.7108 | 318.0652 | 329.6121 | 423.3505 | 488.7435 | 417.8677 | NaN | NaN | NaN | 660.0693 | 1254.9091 | NaN | NaN | 1253.6385 | NaN | NaN | NaN | NaN | 1253.7698 | 1254.3391 | NaN | 19.0664 | NaN | 23.7887
9606.1448 | 748.1536 | 551.8975 | 318.8434 | 318.0918 | 329.5861 | 423.857 | 491.862 | 419.0045 | NaN | NaN | NaN | 669.9898 | 1254.9084 | NaN | NaN | 1253.6377 | NaN | NaN | NaN | NaN | 1253.7691 | 1254.3383 | NaN | 18.0825 | NaN | 23.0761
9607.1292 | 748.4543 | 554.3101 | 318.6024 | 318.6803 | 329.7387 | 424.5378 | 492.4222 | 421.8307 | NaN | NaN | NaN | 676.2558 | 1254.9079 | NaN | NaN | 1253.6372 | NaN | NaN | NaN | NaN | 1253.7686 | 1254.3379 | NaN | 17.9877 | NaN | 23.0222
9608.1292 | 748.3772 | 554.9673 | 319.026 | 319.6885 | 329.9436 | 425.5858 | 494.1568 | 423.7324 | NaN | NaN | NaN | 687.9406 | 1254.9084 | NaN | NaN | 1253.6377 | NaN | NaN | NaN | NaN | 1253.7691 | 1254.3383 | NaN | 16.5659 | NaN | 24.9817
9609.1292 | 748.3846 | 554.8096 | 319.1356 | 319.708 | 330.1914 | 424.3745 | 492.4849 | 423.5089 | NaN | NaN | NaN | 677.8025 | 1254.9079 | NaN | NaN | 1253.6372 | NaN | NaN | NaN | NaN | 1253.7686 | 1254.3378 | NaN | 17.7733 | NaN | 22.8096
9610.1292 | 748.4419 | 554.9175 | 319.2785 | 320.0265 | 330.9085 | 425.1728 | 493.4524 | 424.0778 | NaN | NaN | NaN | 707.078 | 1254.9072 | NaN | NaN | 1253.6365 | NaN | NaN | NaN | NaN | 1253.7679 | 1254.3371 | NaN | 19.9959 | NaN | 23.9605
9611.1292 | 747.0272 | 555.0433 | 319.5514 | 320.2396 | 330.8937 | 426.3244 | 495.2964 | 426.0483 | NaN | NaN | NaN | 677.2326 | 1254.907 | NaN | NaN | 1253.6363 | NaN | NaN | NaN | NaN | 1253.7677 | 1254.337 | NaN | 17.3112 | NaN | 22.9464
9612.1292 | 746.1954 | 554.2217 | 320.4805 | 320.0825 | 330.8286 | 426.3582 | 493.8766 | 425.2244 | NaN | NaN | NaN | 676.0163 | 1254.9076 | NaN | NaN | 1253.6369 | NaN | NaN | NaN | NaN | 1253.7683 | 1254.3375 | NaN | 17.7616 | NaN | 24.8698
9613.1292 | 744.7441 | 554.4332 | 320.5916 | 320.0922 | 330.869 | 426.9242 | 493.7644 | 423.1357 | NaN | NaN | NaN | 675.3339 | 1254.9069 | NaN | NaN | 1253.6363 | NaN | NaN | NaN | NaN | 1253.7676 | 1254.3369 | NaN | 17.6153 | NaN | 24.6731
9614.1292 | 744.1717 | 554.024 | 320.2383 | 319.5886 | 330.6588 | 430.6844 | 496.4263 | 422.1629 | NaN | NaN | NaN | 691.2919 | 1254.9069 | NaN | NaN | 1253.6362 | NaN | NaN | NaN | NaN | 1253.7676 | 1254.3368 | NaN | 18.3362 | NaN | 23.6056
9615.1292 | 743.9972 | 554.6342 | 319.8887 | 319.6473 | 330.7704 | 434.0639 | 499.7635 | 422.1419 | NaN | NaN | NaN | 674.7646 | 1254.9071 | NaN | NaN | 1253.6364 | NaN | NaN | NaN | NaN | 1253.7678 | 1254.337 | NaN | 18.5673 | NaN | 23.8718
9616.1292 | 743.7845 | 554.3424 | 320.6383 | 319.7108 | 331.1129 | 434.3274 | 503.0318 | 421.7993 | NaN | NaN | NaN | 684.7048 | 1254.9072 | NaN | NaN | 1253.6365 | NaN | NaN | NaN | NaN | 1253.7679 | 1254.3372 | NaN | 17.285 | NaN | 24.894
9617.1292 | 744.7056 | 554.6057 | 320.742 | 319.8212 | 331.0874 | 433.48 | 504.1205 | 420.4072 | NaN | NaN | NaN | 693.9118 | 1254.9065 | NaN | NaN | 1253.6358 | NaN | NaN | NaN | NaN | 1253.7672 | 1254.3365 | NaN | 17.6425 | NaN | 24.1876
9618.1292 | 745.3382 | 553.7351 | 321.228 | 319.6051 | 331.4155 | 432.9437 | 502.4635 | 420.4637 | NaN | NaN | NaN | 667.3602 | 1254.9064 | NaN | NaN | 1253.6357 | NaN | NaN | NaN | NaN | 1253.7671 | 1254.3364 | NaN | 19.854 | NaN | 25.3423
9619.1292 | 744.961 | 553.0675 | 321.3436 | 319.2595 | 331.5622 | 433.505 | 501.7478 | 419.5764 | NaN | NaN | NaN | 637.0189 | 1254.9055 | NaN | NaN | 1253.6348 | NaN | NaN | NaN | NaN | 1253.7662 | 1254.3354 | NaN | 16.8146 | NaN | 24.6047
9620.1292 | 743.678 | 552.0126 | 321.9479 | 319.276 | 331.9739 | 433.3985 | 500.133 | 418.2026 | NaN | NaN | NaN | 614.8299 | 1254.9058 | NaN | NaN | 1253.6351 | NaN | NaN | NaN | NaN | 1253.7665 | 1254.3358 | NaN | 18.4436 | NaN | 23.4104
9621.1292 | 743.6657 | 551.2403 | 321.8092 | 319.4088 | 332.0704 | 432.7643 | 498.3063 | 416.7292 | NaN | NaN | NaN | 629.1207 | 1254.9054 | NaN | NaN | 1253.6347 | NaN | NaN | NaN | NaN | 1253.7661 | 1254.3354 | NaN | 17.5754 | NaN | 24.5475
9622.1292 | 744.6878 | 551.8281 | 321.2191 | 319.3546 | 332.3437 | 431.8148 | 497.0355 | 416.9635 | NaN | NaN | NaN | 610.6432 | 1254.9056 | NaN | NaN | 1253.6349 | NaN | NaN | NaN | NaN | 1253.7663 | 1254.3356 | NaN | 17.2294 | NaN | 24.7504
9623.1292 | 746.0388 | 552.5818 | 321.315 | 319.1892 | 332.5826 | 432.5399 | 497.3371 | 417.1229 | NaN | NaN | NaN | 602.0368 | 1254.9055 | NaN | NaN | 1253.6348 | NaN | NaN | NaN | NaN | 1253.7662 | 1254.3354 | NaN | 17.6646 | NaN | 24.957
9624.1292 | 747.4409 | 552.0802 | 320.8493 | 319.1951 | 332.2693 | 433.8149 | 496.7971 | 419.3975 | NaN | NaN | NaN | 582.0509 | 1254.9046 | NaN | NaN | 1253.6339 | NaN | NaN | NaN | NaN | 1253.7653 | 1254.3346 | NaN | 15.4561 | NaN | 24.1613
9625.1292 | 748.8743 | 553.946 | 321.0279 | 319.461 | 332.8295 | 432.8414 | 496.498 | 419.8149 | NaN | NaN | NaN | 562.5555 | 1254.9048 | NaN | NaN | 1253.6341 | NaN | NaN | NaN | NaN | 1253.7655 | 1254.3348 | NaN | 16.8635 | NaN | 22.3733
9626.1292 | 750.4679 | 555.9714 | 321.7796 | 320.3094 | 333.0851 | 432.5552 | 497.5536 | 420.0039 | NaN | NaN | NaN | 560.0057 | 1254.9038 | NaN | NaN | 1253.6332 | NaN | NaN | NaN | NaN | 1253.7646 | 1254.3338 | NaN | 17.2554 | NaN | 25.1551
9627.1292 | 752.0781 | 555.7942 | 322.0951 | 320.2023 | 333.2145 | 434.3639 | 498.8577 | 421.9322 | NaN | NaN | NaN | 596.8589 | 1254.9038 | NaN | NaN | 1253.6331 | NaN | NaN | NaN | NaN | 1253.7645 | 1254.3337 | NaN | 17.7259 | NaN | 24.0407
9628.1292 | 754.4712 | 555.5361 | 322.1223 | 320.656 | 333.445 | 436.7994 | 501.1782 | 422.8776 | NaN | NaN | NaN | 616.6473 | 1254.9048 | NaN | NaN | 1253.6342 | NaN | NaN | NaN | NaN | 1253.7656 | 1254.3348 | NaN | 17.0998 | NaN | 24.5446
9629.1292 | 755.8502 | 556.6169 | 322.8487 | 320.7421 | 333.6495 | 435.8774 | 503.8567 | 425.603 | NaN | NaN | NaN | 608.1776 | 1254.9042 | NaN | NaN | 1253.6335 | NaN | NaN | NaN | NaN | 1253.7649 | 1254.3342 | NaN | 16.2062 | NaN | 23.4738
9630.1292 | 755.4292 | 557.3069 | 323.2382 | 320.6491 | 334.4521 | 436.1942 | 504.5191 | 425.519 | NaN | NaN | NaN | 607.9546 | 1254.9038 | NaN | NaN | 1253.6331 | NaN | NaN | NaN | NaN | 1253.7645 | 1254.3338 | NaN | 15.1803 | NaN | 22.6879
9631.1292 | 754.3007 | 556.5163 | 323.5979 | 320.64 | 334.5836 | 436.5071 | 506.8094 | 424.9505 | NaN | NaN | NaN | 609.295 | 1254.9033 | NaN | NaN | 1253.6326 | NaN | NaN | NaN | NaN | 1253.764 | 1254.3332 | NaN | 17.2912 | NaN | 24.7405
9632.1292 | 753.0195 | 556.5998 | 323.8688 | 320.6951 | 334.676 | 438.1551 | 507.813 | 424.1038 | NaN | NaN | NaN | 629.9435 | 1254.903 | NaN | NaN | 1253.6323 | NaN | NaN | NaN | NaN | 1253.7637 | 1254.333 | NaN | 17.0172 | NaN | 24.8787
9633.1292 | 753.0107 | 556.2486 | 323.4344 | 321.1568 | 334.8192 | 438.3161 | 506.8417 | 422.6516 | NaN | NaN | NaN | 630.5176 | 1254.9028 | NaN | NaN | 1253.6321 | NaN | NaN | NaN | NaN | 1253.7635 | 1254.3327 | NaN | 18.2482 | NaN | 22.156
9634.1292 | 751.998 | 556.8727 | 323.3601 | 321.2892 | 334.7796 | 436.5921 | 504.9984 | 423.6587 | NaN | NaN | NaN | 645.0971 | 1254.9025 | NaN | NaN | 1253.6318 | NaN | NaN | NaN | NaN | 1253.7632 | 1254.3324 | NaN | 17.0665 | NaN | 23.2182
9635.1292 | 752.0458 | 556.4109 | 323.6371 | 321.2815 | 335.0619 | 436.2962 | 503.8321 | 424.1825 | NaN | NaN | NaN | 664.2143 | 1254.9016 | NaN | NaN | 1253.6309 | NaN | NaN | NaN | NaN | 1253.7623 | 1254.3315 | NaN | 16.8321 | NaN | 24.765
9636.1292 | 752.0068 | 558.0538 | 323.3281 | 320.9006 | 335.3548 | 435.8953 | 503.2258 | 425.8843 | NaN | NaN | NaN | 675.8168 | 1254.9017 | NaN | NaN | 1253.631 | NaN | NaN | NaN | NaN | 1253.7624 | 1254.3317 | NaN | 18.0371 | NaN | 25.3804
9637.1292 | 752.2896 | 561.8677 | 323.3355 | 320.7186 | 335.2248 | 433.845 | 502.6605 | 429.8883 | NaN | NaN | NaN | 673.4945 | 1254.9021 | NaN | NaN | 1253.6314 | NaN | NaN | NaN | NaN | 1253.7628 | 1254.332 | NaN | 16.7521 | NaN | 25.0038
9638.1292 | 752.2601 | 562.181 | 323.5433 | 321.3636 | 335.7336 | 434.5389 | 503.5613 | 432.225 | NaN | NaN | NaN | 647.9594 | 1254.9023 | NaN | NaN | 1253.6316 | NaN | NaN | NaN | NaN | 1253.763 | 1254.3322 | NaN | 17.4333 | NaN | 24.8065
9639.1292 | 750.7158 | 563.6794 | 323.3978 | 321.6986 | 335.8944 | 435.1258 | 503.8194 | 431.4674 | NaN | NaN | NaN | 633.5969 | 1254.9014 | NaN | NaN | 1253.6307 | NaN | NaN | NaN | NaN | 1253.7621 | 1254.3314 | NaN | 18.4993 | NaN | 24.8955
9640.1292 | 749.886 | 562.9768 | 323.8629 | 321.3204 | 335.5664 | 436.0881 | 502.1018 | 430.2488 | NaN | NaN | NaN | 607.2165 | 1254.9013 | NaN | NaN | 1253.6306 | NaN | NaN | NaN | NaN | 1253.762 | 1254.3312 | NaN | 18.4353 | NaN | 24.1134
9641.1292 | 748.8443 | 561.1837 | 324.035 | 321.0008 | 335.1885 | 436.8204 | 500.5247 | 429.1169 | NaN | NaN | NaN | 586.7865 | 1254.9007 | NaN | NaN | 1253.63 | NaN | NaN | NaN | NaN | 1253.7614 | 1254.3307 | NaN | 15.949 | NaN | 22.3869
9642.1292 | 748.0735 | 559.9548 | 324.4277 | 320.7779 | 335.0836 | 437.1509 | 499.9618 | 428.1716 | NaN | NaN | NaN | 590.5792 | 1254.9014 | NaN | NaN | 1253.6307 | NaN | NaN | NaN | NaN | 1253.7621 | 1254.3314 | NaN | 17.9558 | NaN | 23.5716
9643.1292 | 745.6398 | 561.4724 | 324.9561 | 320.494 | 335.0156 | 437.7037 | 497.6409 | 426.539 | NaN | NaN | NaN | 612.4767 | 1254.9003 | NaN | NaN | 1253.6296 | NaN | NaN | NaN | NaN | 1253.761 | 1254.3303 | NaN | 19.1649 | NaN | 24.7722
9644.1292 | 743.4756 | 561.9661 | 325.8352 | 320.8167 | 334.8023 | 439.6533 | 500.0016 | 425.414 | NaN | NaN | NaN | 610.7085 | 1254.9007 | NaN | NaN | 1253.63 | NaN | NaN | NaN | NaN | 1253.7614 | 1254.3307 | NaN | 16.7716 | NaN | 25.21
9645.1292 | 743.7991 | 564.0764 | 325.2727 | 321.5514 | 335.0659 | 438.195 | 500.3736 | 424.062 | NaN | NaN | NaN | 604.2456 | 1254.8999 | NaN | NaN | 1253.6292 | NaN | NaN | NaN | NaN | 1253.7606 | 1254.3298 | NaN | 18.6237 | NaN | 24.003
9646.1292 | 745.6042 | 563.6933 | 325.0978 | 321.5689 | 335.2514 | 438.8828 | 502.6146 | 424.4767 | NaN | NaN | NaN | 608.2548 | 1254.8998 | NaN | NaN | 1253.6291 | NaN | NaN | NaN | NaN | 1253.7605 | 1254.3298 | NaN | 17.8113 | NaN | 24.5144
9647.1292 | 748.4236 | 565.9116 | 324.9689 | 321.9526 | 335.7036 | 437.2886 | 503.6809 | 426.2969 | NaN | NaN | NaN | 616.7075 | 1254.8992 | NaN | NaN | 1253.6285 | NaN | NaN | NaN | NaN | 1253.7599 | 1254.3292 | NaN | 15.9101 | NaN | 23.4155
9648.1292 | 749.5915 | 571.0815 | 324.7506 | 321.8106 | 336.0051 | 437.4978 | 506.0437 | 429.5238 | NaN | NaN | NaN | 662.7113 | 1254.8992 | NaN | NaN | 1253.6286 | NaN | NaN | NaN | NaN | 1253.76 | 1254.3292 | NaN | 18.3244 | NaN | 23.9894
9649.1292 | 749.8203 | 573.571 | 324.5216 | 322.1322 | 336.6127 | 436.7677 | 510.2394 | 431.457 | NaN | NaN | NaN | 665.8741 | 1254.899 | NaN | NaN | 1253.6283 | NaN | NaN | NaN | NaN | 1253.7597 | 1254.329 | NaN | 17.1193 | NaN | 24.0443
9650.1292 | 746.4318 | 574.109 | 325.038 | 321.8429 | 336.6193 | 437.8447 | 516.5903 | 432.272 | NaN | NaN | NaN | 669.4861 | 1254.8998 | NaN | NaN | 1253.6292 | NaN | NaN | NaN | NaN | 1253.7605 | 1254.3298 | NaN | 17.6183 | NaN | 24.474
9651.1292 | 743.1393 | 574.8294 | 325.4393 | 321.8417 | 336.9738 | 438.4107 | 516.7843 | 430.7106 | NaN | NaN | NaN | 701.4919 | 1254.8987 | NaN | NaN | 1253.628 | NaN | NaN | NaN | NaN | 1253.7594 | 1254.3287 | NaN | 16.2905 | NaN | 23.7871
9652.1292 | 741.3768 | 575.839 | 326.637 | 321.8901 | 337.3807 | 437.858 | 513.494 | 428.2745 | NaN | NaN | NaN | 711.6663 | 1254.8989 | NaN | NaN | 1253.6282 | NaN | NaN | NaN | NaN | 1253.7596 | 1254.3288 | NaN | 17.4008 | NaN | 23.0068
9653.1292 | 740.1218 | 573.6396 | 326.637 | 322.2851 | 337.6244 | 439.4951 | 511.5019 | 425.9933 | NaN | NaN | NaN | 694.9205 | 1254.8984 | NaN | NaN | 1253.6277 | NaN | NaN | NaN | NaN | 1253.7591 | 1254.3283 | NaN | 15.9408 | NaN | 24.6963
9654.1292 | 738.6517 | 573.1332 | 327.4785 | 322.6906 | 338.0588 | 445.3956 | 517.0967 | 426.7926 | NaN | NaN | NaN | 687.5537 | 1254.8979 | NaN | NaN | 1253.6272 | NaN | NaN | NaN | NaN | 1253.7586 | 1254.3279 | NaN | 18.0725 | NaN | 25.2346
9655.1292 | 738.8427 | 572.6148 | 327.4508 | 323.4741 | 338.0304 | 446.5234 | 520.0392 | 425.6625 | NaN | NaN | NaN | 667.1425 | 1254.8968 | NaN | NaN | 1253.6261 | NaN | NaN | NaN | NaN | 1253.7575 | 1254.3268 | NaN | 16.9275 | NaN | 24.7423
9656.1292 | 740.4771 | 571.5035 | 327.7384 | 324.002 | 338.1766 | 445.9761 | 518.7951 | 425.175 | NaN | NaN | NaN | 651.5001 | 1254.896 | NaN | NaN | 1253.6253 | NaN | NaN | NaN | NaN | 1253.7567 | 1254.3259 | NaN | 17.8167 | NaN | 24.1456
9657.1292 | 741.4255 | 569.2711 | 327.2278 | 324.154 | 338.2384 | 447.8658 | 520.191 | 426.284 | NaN | NaN | NaN | 627.082 | 1254.8967 | NaN | NaN | 1253.6261 | NaN | NaN | NaN | NaN | 1253.7574 | 1254.3267 | NaN | 16.0865 | NaN | 22.4227
9658.1292 | 743.4414 | 567.7104 | 327.2162 | 324.3131 | 338.2496 | 449.4538 | 519.8889 | 428.3335 | NaN | NaN | NaN | 611.9568 | 1254.8965 | NaN | NaN | 1253.6258 | NaN | NaN | NaN | NaN | 1253.7572 | 1254.3265 | NaN | 15.4693 | NaN | 25.0272
9659.1292 | 745.1065 | 566.1112 | 326.9309 | 324.7088 | 338.1304 | 450.1906 | 519.8831 | 428.0235 | NaN | NaN | NaN | 602.3691 | 1254.8968 | NaN | NaN | 1253.6261 | NaN | NaN | NaN | NaN | 1253.7575 | 1254.3268 | NaN | 15.8261 | NaN | 21.0666
9660.1292 | 744.9644 | 564.875 | 327.2074 | 325.2487 | 338.2301 | 449.8827 | 518.9594 | 429.0959 | NaN | NaN | NaN | 593.6183 | 1254.8958 | NaN | NaN | 1253.6251 | NaN | NaN | NaN | NaN | 1253.7565 | 1254.3258 | NaN | 15.9763 | NaN | 24.942
9661.1292 | 745.2443 | 563.0549 | 327.297 | 325.6264 | 337.9711 | 451.7489 | 516.8308 | 428.2914 | NaN | NaN | NaN | 574.3028 | 1254.8954 | NaN | NaN | 1253.6247 | NaN | NaN | NaN | NaN | 1253.7561 | 1254.3254 | NaN | 16.7935 | NaN | 24.464
9662.1292 | 746.7937 | 562.1038 | 327.1879 | 325.793 | 337.9618 | 452.2636 | 516.6337 | 428.7421 | NaN | NaN | NaN | 586.7669 | 1254.8952 | NaN | NaN | 1253.6246 | NaN | NaN | NaN | NaN | 1253.7559 | 1254.3252 | NaN | 14.988 | NaN | 22.6685
9663.1292 | 747.2339 | 561.223 | 327.0589 | 326.6767 | 338.0047 | 452.0988 | 516.456 | 429.6167 | NaN | NaN | NaN | 614.0869 | 1254.8955 | NaN | NaN | 1253.6249 | NaN | NaN | NaN | NaN | 1253.7562 | 1254.3255 | NaN | 15.8314 | NaN | 23.7975
9664.1292 | 745.9796 | 561.8928 | 326.9825 | 326.4685 | 337.9442 | 453.4124 | 516.4403 | 430.5451 | NaN | NaN | NaN | 611.7273 | 1254.8949 | NaN | NaN | 1253.6242 | NaN | NaN | NaN | NaN | 1253.7556 | 1254.3249 | NaN | 16.8683 | NaN | 24.8019
9665.1292 | 745.9843 | 560.9023 | 326.8008 | 326.156 | 337.6784 | 453.0821 | 514.7389 | 429.4341 | NaN | NaN | NaN | 653.7857 | 1254.895 | NaN | NaN | 1253.6244 | NaN | NaN | NaN | NaN | 1253.7557 | 1254.325 | NaN | 17.321 | NaN | 23.3453
9666.1292 | 747.847 | 560.1157 | 326.9623 | 326.7919 | 337.8296 | 453.7454 | 513.3781 | 428.9781 | NaN | NaN | NaN | 692.0936 | 1254.8943 | NaN | NaN | 1253.6236 | NaN | NaN | NaN | NaN | 1253.755 | 1254.3242 | NaN | 18.6816 | NaN | 25.0255
9667.1292 | 748.8668 | 560.0334 | 326.9109 | 326.8483 | 337.9211 | 451.8834 | 513.2184 | 429.421 | NaN | NaN | NaN | 661.2531 | 1254.8948 | NaN | NaN | 1253.6241 | NaN | NaN | NaN | NaN | 1253.7555 | 1254.3247 | NaN | 17.6867 | NaN | 23.9498
9668.1292 | 747.5647 | 561.6206 | 327.5498 | 327.1976 | 338.0912 | 451.758 | 515.6311 | 429.0667 | NaN | NaN | NaN | 652.8385 | 1254.8934 | NaN | NaN | 1253.6227 | NaN | NaN | NaN | NaN | 1253.7541 | 1254.3234 | NaN | 15.7104 | NaN | 23.7495
9669.1292 | 747.3441 | 561.6083 | 328.1924 | 327.443 | 338.0828 | 452.0473 | 515.1885 | 429.5454 | NaN | NaN | NaN | 636.9164 | 1254.8934 | NaN | NaN | 1253.6227 | NaN | NaN | NaN | NaN | 1253.7541 | 1254.3234 | NaN | 15.5938 | NaN | 25.2451
9670.1292 | 747.8656 | 561.5696 | 328.8982 | 327.4768 | 338.5951 | 453.2371 | 514.9083 | 428.9253 | NaN | NaN | NaN | 663.6251 | 1254.8937 | NaN | NaN | 1253.6231 | NaN | NaN | NaN | NaN | 1253.7544 | 1254.3237 | NaN | 15.8302 | NaN | 24.2448
9671.1292 | 747.1913 | 560.4757 | 328.3168 | 327.3345 | 338.9696 | 452.3154 | 515.0922 | 428.1978 | NaN | NaN | NaN | 684.4087 | 1254.893 | NaN | NaN | 1253.6223 | NaN | NaN | NaN | NaN | 1253.7537 | 1254.323 | NaN | 16.4071 | NaN | 23.1874
9672.1292 | 745.5926 | 560.2518 | 328.9651 | 327.6966 | 339.5876 | 453.0229 | 519.2373 | 428.4941 | NaN | NaN | NaN | 682.5872 | 1254.8929 | NaN | NaN | 1253.6223 | NaN | NaN | NaN | NaN | 1253.7537 | 1254.3229 | NaN | 15.9341 | NaN | 24.2248
9673.1292 | 744.0757 | 560.9284 | 329.3119 | 327.6341 | 339.7494 | 452.5088 | 520.334 | 428.5153 | NaN | NaN | NaN | 679.9978 | 1254.8931 | NaN | NaN | 1253.6224 | NaN | NaN | NaN | NaN | 1253.7538 | 1254.323 | NaN | 16.559 | NaN | 24.4248
9674.1292 | 746.4107 | 560.628 | 329.5865 | 327.5181 | 340.7843 | 451.0445 | 520.4311 | 427.8709 | NaN | NaN | NaN | 666.4674 | 1254.8924 | NaN | NaN | 1253.6217 | NaN | NaN | NaN | NaN | 1253.7531 | 1254.3224 | NaN | 16.6278 | NaN | 24.4336
9675.1292 | 747.6233 | 560.4979 | 329.9764 | 327.1822 | 340.765 | 450.2299 | 518.9652 | 429.9401 | NaN | NaN | NaN | 642.0255 | 1254.8925 | NaN | NaN | 1253.6219 | NaN | NaN | NaN | NaN | 1253.7532 | 1254.3225 | NaN | 18.5116 | NaN | 24.4016
9676.1292 | 747.7047 | 562.4527 | 331.1613 | 327.1815 | 340.9499 | 452.4991 | 522.0235 | 430.5336 | NaN | NaN | NaN | 619.6206 | 1254.8922 | NaN | NaN | 1253.6215 | NaN | NaN | NaN | NaN | 1253.7529 | 1254.3222 | NaN | 16.0848 | NaN | 24.8742
9677.1292 | 748.1856 | 564.2077 | 330.9322 | 326.9833 | 340.8739 | 451.6206 | 521.2255 | 429.9163 | NaN | NaN | NaN | 605.4683 | 1254.8918 | NaN | NaN | 1253.6212 | NaN | NaN | NaN | NaN | 1253.7525 | 1254.3218 | NaN | 18.9961 | NaN | 24.4379
9678.1292 | 749.5115 | 563.4878 | 331.1685 | 327.1332 | 340.2769 | 450.3207 | 521.9132 | 429.0434 | NaN | NaN | NaN | 619.974 | 1254.8921 | NaN | NaN | 1253.6214 | NaN | NaN | NaN | NaN | 1253.7528 | 1254.3221 | NaN | 17.1234 | NaN | 23.5596
9679.1292 | 749.6265 | 564.7551 | 331.6695 | 326.9906 | 339.8605 | 449.2971 | 524.4687 | 429.8369 | NaN | NaN | NaN | 654.5365 | 1254.8923 | NaN | NaN | 1253.6217 | NaN | NaN | NaN | NaN | 1253.753 | 1254.3223 | NaN | 16.187 | NaN | 24.3438
9680.1292 | 748.4057 | 566.2464 | 331.0324 | 327.1423 | 339.6097 | 449.5669 | 525.5918 | 428.9934 | NaN | NaN | NaN | 668.8317 | 1254.8907 | NaN | NaN | 1253.6201 | NaN | NaN | NaN | NaN | 1253.7515 | 1254.3207 | NaN | 17.0404 | NaN | 23.7916
9681.1292 | 747.5799 | 567.1959 | 330.8564 | 327.2483 | 339.4058 | 447.8077 | 530.4931 | 429.2064 | NaN | NaN | NaN | 668.0182 | 1254.891 | NaN | NaN | 1253.6203 | NaN | NaN | NaN | NaN | 1253.7517 | 1254.321 | NaN | 19.1089 | NaN | 24.2833
9682.1292 | 747.7174 | 565.9951 | 331.234 | 327.7815 | 339.7255 | 448.9581 | 530.3674 | 431.0057 | NaN | NaN | NaN | 675.1565 | 1254.8897 | NaN | NaN | 1253.619 | NaN | NaN | NaN | NaN | 1253.7504 | 1254.3196 | NaN | 18.3746 | NaN | 24.8317
9683.1292 | 747.6167 | 566.7021 | 331.0897 | 327.4816 | 339.6583 | 450.2702 | 531.1612 | 430.8389 | NaN | NaN | NaN | 677.351 | 1254.8905 | NaN | NaN | 1253.6198 | NaN | NaN | NaN | NaN | 1253.7512 | 1254.3205 | NaN | 16.6561 | NaN | 22.2202
9684.1292 | 748.1206 | 565.3773 | 331.4978 | 328.325 | 339.8848 | 450.4249 | 530.3207 | 431.3837 | NaN | NaN | NaN | 678.2939 | 1254.8906 | NaN | NaN | 1253.62 | NaN | NaN | NaN | NaN | 1253.7513 | 1254.3206 | NaN | 16.7407 | NaN | 24.5711
9685.1292 | 748.15 | 565.7281 | 332.0164 | 328.1816 | 340.3112 | 449.2858 | 528.3304 | 431.6362 | NaN | NaN | NaN | 666.8068 | 1254.8904 | NaN | NaN | 1253.6197 | NaN | NaN | NaN | NaN | 1253.7511 | 1254.3203 | NaN | 16.126 | NaN | 22.7269
9686.1292 | 748.5422 | 565.3356 | 332.2104 | 328.9225 | 340.8502 | 449.4039 | 529.6994 | 431.1086 | NaN | NaN | NaN | 674.9093 | 1254.889 | NaN | NaN | 1253.6183 | NaN | NaN | NaN | NaN | 1253.7497 | 1254.319 | NaN | 17.3608 | NaN | 24.2669
9687.1292 | 747.6027 | 566.7632 | 333.1383 | 329.66 | 340.9498 | 449.2207 | 529.0288 | 431.7182 | NaN | NaN | NaN | 651.8567 | 1254.89 | NaN | NaN | 1253.6193 | NaN | NaN | NaN | NaN | 1253.7507 | 1254.32 | NaN | 17.2316 | NaN | 22.4629
9688.1292 | 746.7732 | 565.7303 | 333.6768 | 329.0867 | 340.9984 | 448.7288 | 530.53 | 432.3886 | NaN | NaN | NaN | 659.6288 | 1254.889 | NaN | NaN | 1253.6183 | NaN | NaN | NaN | NaN | 1253.7497 | 1254.319 | NaN | 16.6312 | NaN | 23.1313
9689.1292 | 746.0797 | 563.9687 | 333.6788 | 328.8664 | 341.0676 | 447.998 | 528.7751 | 431.086 | NaN | NaN | NaN | 675.4065 | 1254.8894 | NaN | NaN | 1253.6187 | NaN | NaN | NaN | NaN | 1253.7501 | 1254.3194 | NaN | 17.3412 | NaN | 24.8976
9690.1292 | 746.4764 | 565.088 | 333.9341 | 329.1087 | 340.9458 | 447.1218 | 527.633 | 429.7631 | NaN | NaN | NaN | 704.1826 | 1254.888 | NaN | NaN | 1253.6173 | NaN | NaN | NaN | NaN | 1253.7487 | 1254.318 | NaN | 18.993 | NaN | 23.8547
9691.1292 | 746.6143 | 565.4467 | 334.0242 | 328.445 | 340.7983 | 448.9484 | 530.1448 | 432.0797 | NaN | NaN | NaN | 712.6946 | 1254.8885 | NaN | NaN | 1253.6179 | NaN | NaN | NaN | NaN | 1253.7493 | 1254.3185 | NaN | 15.8185 | NaN | 21.3557
9692.1292 | 746.0159 | 566.1223 | 333.668 | 328.0854 | 340.4508 | 448.8857 | 530.7805 | 431.718 | NaN | NaN | NaN | 683.4267 | 1254.8879 | NaN | NaN | 1253.6173 | NaN | NaN | NaN | NaN | 1253.7486 | 1254.3179 | NaN | 16.5213 | NaN | 24.4836
9693.1292 | 745.6408 | 568.6543 | 333.5307 | 328.1028 | 340.54 | 447.6677 | 530.7125 | 434.1778 | NaN | NaN | NaN | 676.6201 | 1254.8877 | NaN | NaN | 1253.6171 | NaN | NaN | NaN | NaN | 1253.7484 | 1254.3177 | NaN | 18.5502 | NaN | 24.7717
9694.1292 | 743.9559 | 568.4107 | 333.2106 | 327.8304 | 340.6484 | 447.6179 | 532.8685 | 434.9681 | NaN | NaN | NaN | 670.8433 | 1254.8868 | NaN | NaN | 1253.6161 | NaN | NaN | NaN | NaN | 1253.7475 | 1254.3167 | NaN | 18.2002 | NaN | 24.0349
9695.1292 | 741.4681 | 568.1777 | 333.1946 | 328.4023 | 340.4783 | 446.9989 | 533.7386 | 431.78 | NaN | NaN | NaN | 676.4229 | 1254.887 | NaN | NaN | 1253.6163 | NaN | NaN | NaN | NaN | 1253.7477 | 1254.317 | NaN | 18.6607 | NaN | 24.1443
9696.1292 | 739.982 | 566.8436 | 332.6333 | 327.9201 | 340.4446 | 447.1743 | 529.3459 | 429.7075 | NaN | NaN | NaN | 705.6134 | 1254.8871 | NaN | NaN | 1253.6165 | NaN | NaN | NaN | NaN | 1253.7479 | 1254.3171 | NaN | 17.1803 | NaN | 24.7211
9697.1292 | 740.3914 | 565.7738 | 331.857 | 327.3397 | 339.9885 | 448.4293 | 525.5886 | 427.591 | NaN | NaN | NaN | 671.4512 | 1254.8857 | NaN | NaN | 1253.615 | NaN | NaN | NaN | NaN | 1253.7464 | 1254.3157 | NaN | 17.8572 | NaN | 23.5081
9698.1292 | 739.1416 | 565.6039 | 332.1814 | 327.277 | 339.4274 | 446.4241 | 524.1387 | 426.8389 | NaN | NaN | NaN | 647.8374 | 1254.8866 | NaN | NaN | 1253.6159 | NaN | NaN | NaN | NaN | 1253.7473 | 1254.3166 | NaN | 16.76 | NaN | 22.374
9699.1292 | 738.663 | 564.2168 | 331.5761 | 327.3122 | 338.8865 | 447.3657 | 524.1593 | 427.2599 | NaN | NaN | NaN | 640.9345 | 1254.8861 | NaN | NaN | 1253.6154 | NaN | NaN | NaN | NaN | 1253.7468 | 1254.3161 | NaN | 17.3245 | NaN | 24.7306
9700.1292 | 737.0983 | 563.5204 | 331.2376 | 327.2049 | 338.3824 | 448.6532 | 528.057 | 428.0852 | NaN | NaN | NaN | 675.0061 | 1254.8859 | NaN | NaN | 1253.6152 | NaN | NaN | NaN | NaN | 1253.7466 | 1254.3159 | NaN | 18.6081 | NaN | 23.8038
9701.1292 | 736.2769 | 564.2479 | 331.0775 | 327.2078 | 338.3655 | 452.8606 | 527.5718 | 428.9787 | NaN | NaN | NaN | 662.6084 | 1254.8853 | NaN | NaN | 1253.6146 | NaN | NaN | NaN | NaN | 1253.746 | 1254.3153 | NaN | 17.8096 | NaN | 25.3288
9702.1292 | 734.2862 | 563.9291 | 331.0328 | 327.1596 | 337.9029 | 454.099 | 525.6065 | 428.7884 | NaN | NaN | NaN | 634.3612 | 1254.8856 | NaN | NaN | 1253.6149 | NaN | NaN | NaN | NaN | 1253.7463 | 1254.3156 | NaN | 16.3602 | NaN | 23.9911
9703.1292 | 733.1323 | 565.8734 | 331.3534 | 327.2118 | 338.4249 | 456.8636 | 525.0669 | 429.7107 | NaN | NaN | NaN | 614.8406 | 1254.8854 | NaN | NaN | 1253.6147 | NaN | NaN | NaN | NaN | 1253.7461 | 1254.3154 | NaN | 17.8125 | NaN | 24.7349
9704.1292 | 732.5897 | 566.0984 | 331.8454 | 327.0997 | 338.3491 | 456.9117 | 522.4517 | 429.3903 | NaN | NaN | NaN | 649.7357 | 1254.8848 | NaN | NaN | 1253.6141 | NaN | NaN | NaN | NaN | 1253.7455 | 1254.3147 | NaN | 17.8723 | NaN | 24.1329
9705.1292 | 733.0304 | 566.9054 | 332.0306 | 326.7673 | 338.5943 | 457.2455 | 521.959 | 427.9259 | NaN | NaN | NaN | 677.1343 | 1254.8858 | NaN | NaN | 1253.6152 | NaN | NaN | NaN | NaN | 1253.7465 | 1254.3158 | NaN | 18.7925 | NaN | 24.4231
9706.1292 | 734.4496 | 568.008 | 331.9435 | 326.3658 | 338.8524 | 457.9135 | 521.131 | 429.6345 | NaN | NaN | NaN | 687.3084 | 1254.8844 | NaN | NaN | 1253.6137 | NaN | NaN | NaN | NaN | 1253.7451 | 1254.3144 | NaN | 17.6072 | NaN | 24.6995
9707.1292 | 735.8591 | 571.1504 | 331.4151 | 326.1837 | 338.6538 | 460.0582 | 526.0847 | 431.6492 | NaN | NaN | NaN | 668.1012 | 1254.885 | NaN | NaN | 1253.6143 | NaN | NaN | NaN | NaN | 1253.7457 | 1254.315 | NaN | 16.9337 | NaN | 24.1622
9708.1292 | 735.8249 | 569.9825 | 331.5911 | 326.5507 | 338.6818 | 463.4149 | 528.0075 | 431.9793 | NaN | NaN | NaN | 639.9774 | 1254.8844 | NaN | NaN | 1253.6138 | NaN | NaN | NaN | NaN | 1253.7452 | 1254.3144 | NaN | 18.2243 | NaN | 25.0078
9709.1292 | 735.6041 | 571.5032 | 331.6137 | 326.9964 | 339.2606 | 465.3985 | 527.6512 | 433.7845 | NaN | NaN | NaN | 641.2524 | 1254.8841 | NaN | NaN | 1253.6135 | NaN | NaN | NaN | NaN | 1253.7449 | 1254.3141 | NaN | 17.0183 | NaN | 24.0189
9710.1292 | 735.3415 | 575.3795 | 331.7141 | 326.9596 | 339.8189 | 464.1759 | 527.2748 | 434.615 | NaN | NaN | NaN | 626.6601 | 1254.8841 | NaN | NaN | 1253.6135 | NaN | NaN | NaN | NaN | 1253.7449 | 1254.3141 | NaN | 17.4723 | NaN | 23.7292
9711.1292 | 736.1527 | 577.8642 | 331.662 | 327.2196 | 340.3479 | 462.727 | 532.7546 | 434.6882 | NaN | NaN | NaN | 642.507 | 1254.8838 | NaN | NaN | 1253.6132 | NaN | NaN | NaN | NaN | 1253.7445 | 1254.3138 | NaN | 19.4041 | NaN | 25.1988
9712.1292 | 737.0804 | 579.2645 | 332.4906 | 327.6886 | 340.7179 | 464.0461 | 536.0719 | 434.8717 | NaN | NaN | NaN | 633.4824 | 1254.8836 | NaN | NaN | 1253.6129 | NaN | NaN | NaN | NaN | 1253.7443 | 1254.3135 | NaN | 18.6443 | NaN | 23.751
9713.1292 | 740.0278 | 579.3837 | 332.548 | 327.7134 | 340.9442 | 465.5722 | 535.7758 | 437.7838 | NaN | NaN | NaN | 617.1715 | 1254.8832 | NaN | NaN | 1253.6125 | NaN | NaN | NaN | NaN | 1253.7439 | 1254.3132 | NaN | 18.0618 | NaN | 23.64
9714.1292 | 741.9714 | 581.6159 | 332.6975 | 327.8987 | 341.0722 | 468.0918 | 538.0684 | 439.9127 | NaN | NaN | NaN | 626.6965 | 1254.8827 | NaN | NaN | 1253.612 | NaN | NaN | NaN | NaN | 1253.7434 | 1254.3127 | NaN | 17.1633 | NaN | 24.9628
9715.1292 | 741.2727 | 582.7987 | 332.8191 | 328.2748 | 341.518 | 471.4075 | 540.0318 | 443.4286 | NaN | NaN | NaN | 634.3217 | 1254.8823 | NaN | NaN | 1253.6117 | NaN | NaN | NaN | NaN | 1253.743 | 1254.3123 | NaN | 18.4375 | NaN | 24.2284
9716.1292 | 739.4821 | 585.1043 | 333.6009 | 328.3883 | 341.5299 | 472.4861 | 542.801 | 443.1018 | NaN | NaN | NaN | 632.9248 | 1254.8824 | NaN | NaN | 1253.6117 | NaN | NaN | NaN | NaN | 1253.7431 | 1254.3123 | NaN | 17.4772 | NaN | 24.0135
9717.1292 | 737.8307 | 586.1023 | 333.6825 | 328.4008 | 341.7481 | 471.8332 | 545.4497 | 441.5817 | NaN | NaN | NaN | 622.6945 | 1254.8814 | NaN | NaN | 1253.6107 | NaN | NaN | NaN | NaN | 1253.7421 | 1254.3114 | NaN | 17.8708 | NaN | 23.8822
9718.1292 | 735.9542 | 584.6352 | 334.286 | 328.2866 | 342.1469 | 470.7285 | 548.3019 | 441.9992 | NaN | NaN | NaN | 615.8507 | 1254.8814 | NaN | NaN | 1253.6108 | NaN | NaN | NaN | NaN | 1253.7421 | 1254.3114 | NaN | 17.6188 | NaN | 23.6554
9719.1292 | 735.1303 | 583.4546 | 334.6065 | 328.5921 | 342.2699 | 471.461 | 549.1787 | 439.9003 | NaN | NaN | NaN | 661.9071 | 1254.8814 | NaN | NaN | 1253.6107 | NaN | NaN | NaN | NaN | 1253.7421 | 1254.3113 | NaN | 16.777 | NaN | 24.0422
9720.1292 | 735.9417 | 581.6691 | 334.997 | 329.5282 | 342.6327 | 475.9039 | 550.3455 | 440.8767 | NaN | NaN | NaN | 687.1558 | 1254.8808 | NaN | NaN | 1253.6101 | NaN | NaN | NaN | NaN | 1253.7415 | 1254.3108 | NaN | 17.9368 | NaN | 23.7156
9721.1292 | 736.8623 | 579.2155 | 335.3976 | 329.7487 | 342.3573 | 477.3178 | 550.0353 | 441.2341 | NaN | NaN | NaN | 683.6345 | 1254.8804 | NaN | NaN | 1253.6098 | NaN | NaN | NaN | NaN | 1253.7411 | 1254.3104 | NaN | 15.8715 | NaN | 22.113
9722.1292 | 739.5618 | 577.9514 | 335.9275 | 329.8111 | 342.9885 | 477.8206 | 549.205 | 441.2851 | NaN | NaN | NaN | 676.9255 | 1254.8802 | NaN | NaN | 1253.6095 | NaN | NaN | NaN | NaN | 1253.7409 | 1254.3102 | NaN | 17.1142 | NaN | 24.4479
9723.1292 | 739.6739 | 578.3822 | 336.407 | 330.1826 | 343.6005 | 478.7913 | 557.3692 | 443.9304 | NaN | NaN | NaN | 709.7556 | 1254.8805 | NaN | NaN | 1253.6099 | NaN | NaN | NaN | NaN | 1253.7413 | 1254.3105 | NaN | 17.7787 | NaN | 23.6189
9724.1292 | 741.9805 | 577.9196 | 336.6673 | 331.5423 | 343.7574 | 481.9995 | 557.9229 | 444.7472 | NaN | NaN | NaN | 680.9865 | 1254.8793 | NaN | NaN | 1253.6087 | NaN | NaN | NaN | NaN | 1253.7401 | 1254.3093 | NaN | 17.7294 | NaN | 24.8564
9725.1292 | 743.8023 | 577.7908 | 336.9412 | 331.5287 | 344.4394 | 484.1855 | 559.0221 | 447.4244 | NaN | NaN | NaN | 646.1662 | 1254.8793 | NaN | NaN | 1253.6086 | NaN | NaN | NaN | NaN | 1253.74 | 1254.3093 | NaN | 16.7963 | NaN | 22.2976
9726.1292 | 744.9875 | 577.9908 | 336.3063 | 331.5569 | 344.5459 | 484.8801 | 558.6339 | 447.5882 | NaN | NaN | NaN | 619.0798 | 1254.8796 | NaN | NaN | 1253.609 | NaN | NaN | NaN | NaN | 1253.7403 | 1254.3096 | NaN | 17.4617 | NaN | 24.1848
9727.1292 | 746.3661 | 578.1255 | 336.3117 | 331.1553 | 344.4887 | 487.0639 | 561.5058 | 449.4771 | NaN | NaN | NaN | 595.8612 | 1254.8796 | NaN | NaN | 1253.6089 | NaN | NaN | NaN | NaN | 1253.7403 | 1254.3096 | NaN | 17.5767 | NaN | 23.9352
9728.1292 | 746.3073 | 577.5992 | 336.9177 | 331.3252 | 344.5447 | 488.1221 | 562.7945 | 451.0872 | NaN | NaN | NaN | 576.257 | 1254.8793 | NaN | NaN | 1253.6087 | NaN | NaN | NaN | NaN | 1253.7401 | 1254.3093 | NaN | 16.7764 | NaN | 22.5093
9729.1292 | 747.8118 | 577.1464 | 337.1599 | 331.3432 | 344.6835 | 489.0038 | 565.3089 | 451.0617 | NaN | NaN | NaN | 581.3014 | 1254.8802 | NaN | NaN | 1253.6095 | NaN | NaN | NaN | NaN | 1253.7409 | 1254.3101 | NaN | 17.2229 | NaN | 24.2803
9730.1292 | 747.6951 | 575.9557 | 337.5949 | 331.3132 | 345.0564 | 489.247 | 571.6722 | 451.1859 | NaN | NaN | NaN | 569.3222 | 1254.8787 | NaN | NaN | 1253.608 | NaN | NaN | NaN | NaN | 1253.7394 | 1254.3087 | NaN | 16.5162 | NaN | 24.8528
9731.1292 | 748.0761 | 574.3523 | 338.2777 | 331.5933 | 345.4271 | 488.8364 | 576.8761 | 450.9376 | NaN | NaN | NaN | 550.0539 | 1254.879 | NaN | NaN | 1253.6083 | NaN | NaN | NaN | NaN | 1253.7397 | 1254.309 | NaN | 18.7878 | NaN | 23.929
9732.1292 | 748.5725 | 575.6856 | 338.0271 | 331.8077 | 345.537 | 487.9428 | 575.6259 | 451.0757 | NaN | NaN | NaN | 539.6193 | 1254.8785 | NaN | NaN | 1253.6078 | NaN | NaN | NaN | NaN | 1253.7392 | 1254.3084 | NaN | 15.7071 | NaN | 23.8836
9733.1292 | 750.8854 | 577.4507 | 338.1711 | 331.8152 | 345.657 | 489.6245 | 584.9988 | 452.5827 | NaN | NaN | NaN | 570.6939 | 1254.8784 | NaN | NaN | 1253.6078 | NaN | NaN | NaN | NaN | 1253.7391 | 1254.3084 | NaN | 18.9738 | NaN | 24.6888
9734.1292 | 752.9758 | 580.2325 | 338.218 | 331.6621 | 345.5017 | 487.2254 | 586.2233 | 452.1847 | NaN | NaN | NaN | 609.4902 | 1254.8783 | NaN | NaN | 1253.6076 | NaN | NaN | NaN | NaN | 1253.739 | 1254.3082 | NaN | 16.995 | NaN | 24.1877
9735.1292 | 752.2511 | 582.0599 | 338.4224 | 331.7006 | 345.4827 | 485.516 | 586.7761 | 451.3173 | NaN | NaN | NaN | 635.3236 | 1254.8771 | NaN | NaN | 1253.6064 | NaN | NaN | NaN | NaN | 1253.7378 | 1254.3071 | NaN | 17.0285 | NaN | 24.1327
9736.1292 | 750.3481 | 581.1965 | 338.1653 | 332.0017 | 345.2902 | 481.4552 | 584.9092 | 449.5128 | NaN | NaN | NaN | 620.8847 | 1254.8766 | NaN | NaN | 1253.6059 | NaN | NaN | NaN | NaN | 1253.7373 | 1254.3066 | NaN | 17.2787 | NaN | 24.6522
9737.1292 | 750.7371 | 582.128 | 337.945 | 331.7685 | 345.3734 | 480.6222 | 584.0664 | 448.3353 | NaN | NaN | NaN | 625.4603 | 1254.8769 | NaN | NaN | 1253.6062 | NaN | NaN | NaN | NaN | 1253.7376 | 1254.3069 | NaN | 17.4902 | NaN | 24.6116
9738.1292 | 749.1746 | 584.3666 | 338.34 | 331.5519 | 345.3523 | 482.675 | 587.0444 | 448.0533 | NaN | NaN | NaN | 659.1309 | 1254.8765 | NaN | NaN | 1253.6058 | NaN | NaN | NaN | NaN | 1253.7372 | 1254.3065 | NaN | 19.048 | NaN | 25.3704
9739.1292 | 747.9211 | 586.7768 | 337.8212 | 331.5242 | 345.0114 | 480.1027 | 591.2984 | 447.837 | NaN | NaN | NaN | 639.6864 | 1254.8764 | NaN | NaN | 1253.6057 | NaN | NaN | NaN | NaN | 1253.7371 | 1254.3064 | NaN | 15.5226 | NaN | 24.7227
9740.1292 | 745.6315 | 587.5672 | 337.8338 | 332.1116 | 344.8421 | 479.2962 | 591.3009 | 449.1879 | NaN | NaN | NaN | 632.146 | 1254.8764 | NaN | NaN | 1253.6058 | NaN | NaN | NaN | NaN | 1253.7372 | 1254.3064 | NaN | 15.9439 | NaN | 23.0712
9741.1292 | 744.4897 | 587.4734 | 338.1676 | 332.1655 | 344.6553 | 478.5683 | 588.0629 | 448.5936 | NaN | NaN | NaN | 609.9739 | 1254.8749 | NaN | NaN | 1253.6042 | NaN | NaN | NaN | NaN | 1253.7356 | 1254.3048 | NaN | 17.4004 | NaN | 24.4392
9742.1292 | 743.1351 | 585.8593 | 338.8056 | 332.2929 | 344.8383 | 478.3252 | 586.341 | 447.4569 | NaN | NaN | NaN | 603.6262 | 1254.8757 | NaN | NaN | 1253.6051 | NaN | NaN | NaN | NaN | 1253.7364 | 1254.3057 | NaN | 15.1669 | NaN | 24.6571
9743.1292 | 741.0948 | 584.5544 | 338.8843 | 332.5387 | 345.2189 | 479.4124 | 581.9698 | 447.0078 | NaN | NaN | NaN | 639.1497 | 1254.8763 | NaN | NaN | 1253.6056 | NaN | NaN | NaN | NaN | 1253.737 | 1254.3063 | NaN | 16.9283 | NaN | 24.9517
9744.1292 | 740.6314 | 583.651 | 338.4343 | 332.3096 | 345.2695 | 477.9222 | 593.5034 | 445.6572 | NaN | NaN | NaN | 622.0602 | 1254.8752 | NaN | NaN | 1253.6046 | NaN | NaN | NaN | NaN | 1253.736 | 1254.3052 | NaN | 17.1234 | NaN | 24.6191
9745.1292 | 741.0001 | 582.3842 | 338.638 | 332.4482 | 345.268 | 478.5714 | 600.8948 | 445.6128 | NaN | NaN | NaN | 615.0602 | 1254.874 | NaN | NaN | 1253.6034 | NaN | NaN | NaN | NaN | 1253.7347 | 1254.304 | NaN | 16.2886 | NaN | 24.6955
9746.1292 | 741.3624 | 580.9488 | 338.2632 | 332.7126 | 345.1402 | 477.3599 | 601.3825 | 445.7304 | NaN | NaN | NaN | 603.4337 | 1254.8752 | NaN | NaN | 1253.6045 | NaN | NaN | NaN | NaN | 1253.7359 | 1254.3052 | NaN | 17.2817 | NaN | 24.4463
9747.1292 | 740.0479 | 580.5827 | 337.2804 | 332.7256 | 345.3812 | 475.7588 | 596.5282 | 445.3921 | NaN | NaN | NaN | 609.0676 | 1254.8746 | NaN | NaN | 1253.6039 | NaN | NaN | NaN | NaN | 1253.7353 | 1254.3046 | NaN | 16.2993 | NaN | 24.6578
9748.1292 | 739.9807 | 580.4147 | 337.3489 | 333.0298 | 346.4227 | 475.0109 | 592.8175 | 446.2559 | NaN | NaN | NaN | 641.2674 | 1254.8736 | NaN | NaN | 1253.6029 | NaN | NaN | NaN | NaN | 1253.7343 | 1254.3036 | NaN | 15.3391 | NaN | 24.5305
9749.1292 | 738.7953 | 579.0164 | 337.8784 | 332.8074 | 346.6965 | 475.5739 | 585.8115 | 446.98 | NaN | NaN | NaN | 626.4077 | 1254.8737 | NaN | NaN | 1253.603 | NaN | NaN | NaN | NaN | 1253.7344 | 1254.3037 | NaN | 18.1125 | NaN | 24.7593
9750.1292 | 738.4758 | 578.8869 | 337.323 | 333.0838 | 346.5964 | 474.9001 | 580.42 | 446.8507 | NaN | NaN | NaN | 600.7488 | 1254.8735 | NaN | NaN | 1253.6028 | NaN | NaN | NaN | NaN | 1253.7342 | 1254.3035 | NaN | 17.3432 | NaN | 25.0409
9751.1292 | 738.2635 | 577.0746 | 337.0571 | 333.0026 | 346.315 | 474.4604 | 577.3132 | 444.3025 | NaN | NaN | NaN | 580.1086 | 1254.8737 | NaN | NaN | 1253.6031 | NaN | NaN | NaN | NaN | 1253.7345 | 1254.3037 | NaN | 16.7421 | NaN | 24.4058
9752.1292 | 737.7135 | 575.7866 | 336.6439 | 333.3611 | 345.6733 | 471.6599 | 569.6682 | 443.3342 | NaN | NaN | NaN | 563.2873 | 1254.8724 | NaN | NaN | 1253.6018 | NaN | NaN | NaN | NaN | 1253.7331 | 1254.3024 | NaN | 16.0922 | NaN | 24.6913
9753.1292 | 738.4029 | 575.5662 | 336.7794 | 333.791 | 344.9663 | 470.763 | 566.3464 | 443.0847 | NaN | NaN | NaN | 566.073 | 1254.8716 | NaN | NaN | 1253.601 | NaN | NaN | NaN | NaN | 1253.7324 | 1254.3016 | NaN | 17.8676 | NaN | 23.2927
9754.1292 | 739.3644 | 576.5108 | 336.0634 | 333.7351 | 344.5751 | 470.6638 | 567.3767 | 443.4257 | NaN | NaN | NaN | 569.1878 | 1254.873 | NaN | NaN | 1253.6023 | NaN | NaN | NaN | NaN | 1253.7337 | 1254.303 | NaN | 15.8385 | NaN | 24.3416
9755.1292 | 739.8122 | 575.7192 | 336.4641 | 333.8815 | 344.4604 | 468.6493 | 569.0818 | 442.7526 | NaN | NaN | NaN | 581.7345 | 1254.8713 | NaN | NaN | 1253.6006 | NaN | NaN | NaN | NaN | 1253.732 | 1254.3013 | NaN | 15.5102 | NaN | 24.7519
9756.1292 | 739.6846 | 576.9275 | 337.196 | 334.4865 | 344.9096 | 467.8032 | 572.1359 | 442.4816 | NaN | NaN | NaN | 619.8267 | 1254.8708 | NaN | NaN | 1253.6002 | NaN | NaN | NaN | NaN | 1253.7316 | 1254.3008 | NaN | 14.9179 | NaN | 24.2194
9757.1292 | 739.7373 | 577.051 | 336.6483 | 334.3362 | 344.6807 | 465.8231 | 573.046 | 441.8877 | NaN | NaN | NaN | 629.9201 | 1254.871 | NaN | NaN | 1253.6003 | NaN | NaN | NaN | NaN | 1253.7317 | 1254.3009 | NaN | 15.9438 | NaN | 24.1294
9758.1292 | 738.3374 | 576.2415 | 337.3734 | 334.1483 | 344.3071 | 464.9811 | 570.0557 | 441.5365 | NaN | NaN | NaN | 631.2957 | 1254.8711 | NaN | NaN | 1253.6005 | NaN | NaN | NaN | NaN | 1253.7318 | 1254.3011 | NaN | 17.6476 | NaN | 23.0147
9759.1292 | 738.5261 | 574.9388 | 337.1273 | 334.5186 | 344.2216 | 465.3626 | 570.5248 | 441.6838 | NaN | NaN | NaN | 649.932 | 1254.8705 | NaN | NaN | 1253.5999 | NaN | NaN | NaN | NaN | 1253.7313 | 1254.3005 | NaN | 16.4211 | NaN | 24.3066
9760.1292 | 739.2583 | 574.2335 | 337.6029 | 334.5488 | 344.286 | 463.947 | 568.317 | 440.0623 | NaN | NaN | NaN | 669.269 | 1254.8701 | NaN | NaN | 1253.5995 | NaN | NaN | NaN | NaN | 1253.7309 | 1254.3001 | NaN | 16.5136 | NaN | 25.089
9761.1292 | 739.8566 | 574.1189 | 336.9802 | 334.3792 | 344.4337 | 462.9055 | 563.763 | 439.4732 | NaN | NaN | NaN | 692.8213 | 1254.8697 | NaN | NaN | 1253.599 | NaN | NaN | NaN | NaN | 1253.7304 | 1254.2997 | NaN | 16.5686 | NaN | 24.6163
9762.1292 | 740.6268 | 577.6747 | 337.193 | 334.1232 | 344.2784 | 465.9572 | 562.2252 | 442.289 | NaN | NaN | NaN | 677.9625 | 1254.8689 | NaN | NaN | 1253.5983 | NaN | NaN | NaN | NaN | 1253.7296 | 1254.2989 | NaN | 16.7143 | NaN | 24.5771
9763.1292 | 740.08 | 579.5219 | 337.756 | 333.7745 | 344.3435 | 465.2345 | 562.6622 | 442.9112 | NaN | NaN | NaN | 695.1441 | 1254.8689 | NaN | NaN | 1253.5982 | NaN | NaN | NaN | NaN | 1253.7296 | 1254.2989 | NaN | 15.1034 | NaN | 23.3974
9764.1292 | 738.0747 | 579.5427 | 337.6755 | 333.3996 | 344.1835 | 462.398 | 563.728 | 441.2214 | NaN | NaN | NaN | 703.7735 | 1254.8686 | NaN | NaN | 1253.5979 | NaN | NaN | NaN | NaN | 1253.7293 | 1254.2986 | NaN | 16.2792 | NaN | 23.7892
9765.1292 | 737.6691 | 577.7767 | 337.6187 | 333.4961 | 343.9946 | 460.8098 | 562.2561 | 439.8824 | NaN | NaN | NaN | 696.1434 | 1254.8691 | NaN | NaN | 1253.5984 | NaN | NaN | NaN | NaN | 1253.7298 | 1254.2991 | NaN | 17.2625 | NaN | 24.3375
9766.1292 | 737.9814 | 576.8664 | 337.6414 | 333.09 | 343.4469 | 460.6242 | 561.5502 | 439.0531 | NaN | NaN | NaN | 686.7735 | 1254.8687 | NaN | NaN | 1253.5981 | NaN | NaN | NaN | NaN | 1253.7294 | 1254.2987 | NaN | 14.887 | NaN | 22.5174
9767.1292 | 737.0338 | 575.8089 | 337.9014 | 333.0284 | 343.1957 | 459.6368 | 558.2413 | 437.5599 | NaN | NaN | NaN | 681.0731 | 1254.8682 | NaN | NaN | 1253.5976 | NaN | NaN | NaN | NaN | 1253.7289 | 1254.2982 | NaN | 16.4864 | NaN | 24.4225
9768.1292 | 736.2205 | 577.5469 | 337.9013 | 332.7607 | 342.9753 | 457.236 | 555.7743 | 437.6071 | NaN | NaN | NaN | 663.189 | 1254.8681 | NaN | NaN | 1253.5975 | NaN | NaN | NaN | NaN | 1253.7289 | 1254.2981 | NaN | 16.6805 | NaN | 24.0827
9769.1292 | 735.7162 | 578.285 | 337.4351 | 332.3413 | 342.9184 | 456.2951 | 556.8989 | 438.6555 | NaN | NaN | NaN | 692.8271 | 1254.868 | NaN | NaN | 1253.5973 | NaN | NaN | NaN | NaN | 1253.7287 | 1254.298 | NaN | 16.5197 | NaN | 24.8147
9770.1292 | 735.7825 | 577.5519 | 337.0202 | 332.0365 | 342.6065 | 455.6802 | 556.8009 | 438.6013 | NaN | NaN | NaN | 701.2706 | 1254.8682 | NaN | NaN | 1253.5976 | NaN | NaN | NaN | NaN | 1253.7289 | 1254.2982 | NaN | 16.6485 | NaN | 24.6524
9771.1292 | 736.7696 | 576.1148 | 336.9869 | 331.9872 | 342.4094 | 455.8167 | 552.7883 | 439.0783 | NaN | NaN | NaN | 726.1385 | 1254.8679 | NaN | NaN | 1253.5973 | NaN | NaN | NaN | NaN | 1253.7287 | 1254.2979 | NaN | 16.9473 | NaN | 23.8679
9772.1292 | 736.6382 | 577.1011 | 337.0915 | 332.1069 | 342.3409 | 456.1413 | 550.5543 | 439.4732 | NaN | NaN | NaN | 718.6495 | 1254.8675 | NaN | NaN | 1253.5969 | NaN | NaN | NaN | NaN | 1253.7282 | 1254.2975 | NaN | 16.6985 | NaN | 24.1545
9773.1292 | 733.783 | 577.1103 | 337.0255 | 332.1603 | 342.2011 | 455.9564 | 548.4676 | 439.308 | NaN | NaN | NaN | 691.8202 | 1254.8664 | NaN | NaN | 1253.5957 | NaN | NaN | NaN | NaN | 1253.7271 | 1254.2964 | NaN | 15.694 | NaN | 24.488
9774.1292 | 733.2038 | 575.7934 | 336.9552 | 331.7524 | 342.1924 | 455.2752 | 542.5124 | 435.8811 | NaN | NaN | NaN | 688.4132 | 1254.8666 | NaN | NaN | 1253.596 | NaN | NaN | NaN | NaN | 1253.7274 | 1254.2966 | NaN | 15.2531 | NaN | 24.4359
9775.1292 | 734.5086 | 574.4739 | 336.5038 | 331.9981 | 342.2744 | 457.0945 | 539.8405 | 434.9358 | NaN | NaN | NaN | 704.8583 | 1254.8665 | NaN | NaN | 1253.5959 | NaN | NaN | NaN | NaN | 1253.7272 | 1254.2965 | NaN | 17.3637 | NaN | 24.3801
9776.1292 | 736.201 | 574.9798 | 336.1552 | 332.0975 | 342.1103 | 458.9813 | 540.5636 | 435.4189 | NaN | NaN | NaN | 707.8664 | 1254.8669 | NaN | NaN | 1253.5962 | NaN | NaN | NaN | NaN | 1253.7276 | 1254.2969 | NaN | 15.7933 | NaN | 24.4704
9777.1292 | 736.1032 | 575.7497 | 336.8145 | 331.6236 | 341.6361 | 458.1395 | 542.9858 | 435.6126 | NaN | NaN | NaN | 680.1003 | 1254.8657 | NaN | NaN | 1253.5951 | NaN | NaN | NaN | NaN | 1253.7265 | 1254.2957 | NaN | 17.1563 | NaN | 24.658
9778.1292 | 735.1711 | 576.4582 | 337.259 | 331.3997 | 341.1503 | 458.4463 | 546.8689 | 437.0637 | NaN | NaN | NaN | 699.3345 | 1254.8661 | NaN | NaN | 1253.5954 | NaN | NaN | NaN | NaN | 1253.7268 | 1254.2961 | NaN | 16.8881 | NaN | 23.6061
9779.1292 | 734.3169 | 576.4385 | 337.6562 | 331.3056 | 341.3795 | 458.703 | 548.4586 | 437.555 | NaN | NaN | NaN | 732.9615 | 1254.8655 | NaN | NaN | 1253.5949 | NaN | NaN | NaN | NaN | 1253.7263 | 1254.2955 | NaN | 15.2012 | NaN | 23.1754
9780.1292 | 734.7695 | 578.5431 | 338.1146 | 331.4671 | 341.2701 | 460.2995 | 548.5509 | 437.1202 | NaN | NaN | NaN | 755.309 | 1254.8648 | NaN | NaN | 1253.5941 | NaN | NaN | NaN | NaN | 1253.7255 | 1254.2948 | NaN | 16.48 | NaN | 25.1515
9781.1292 | 735.2807 | 578.7915 | 338.4649 | 332.0209 | 341.962 | 462.2049 | 553.0499 | 440.1628 | NaN | NaN | NaN | 764.7589 | 1254.8643 | NaN | NaN | 1253.5937 | NaN | NaN | NaN | NaN | 1253.7251 | 1254.2943 | NaN | 18.59 | NaN | 25.5315
9782.1292 | 734.368 | 577.5657 | 338.967 | 331.9922 | 342.2087 | 464.2209 | 551.0027 | 441.2711 | NaN | NaN | NaN | 754.4023 | 1254.8649 | NaN | NaN | 1253.5943 | NaN | NaN | NaN | NaN | 1253.7257 | 1254.2949 | NaN | 16.4306 | NaN | 22.6272
9783.1292 | 733.203 | 576.498 | 339.342 | 332.1483 | 342.3786 | 464.0226 | 548.3145 | 440.6547 | NaN | NaN | NaN | 760.0755 | 1254.8642 | NaN | NaN | 1253.5935 | NaN | NaN | NaN | NaN | 1253.7249 | 1254.2941 | NaN | 15.4331 | NaN | 22.1007
9784.1292 | 733.9964 | 574.8841 | 339.2338 | 332.6392 | 342.448 | 466.6731 | 544.0455 | 438.3857 | NaN | NaN | NaN | 777.9257 | 1254.8635 | NaN | NaN | 1253.5928 | NaN | NaN | NaN | NaN | 1253.7242 | 1254.2935 | NaN | 17.8154 | NaN | 25.2
9785.1292 | 732.0956 | 573.4825 | 338.4672 | 332.8702 | 342.5226 | 465.0147 | 540.3724 | 437.5383 | NaN | NaN | NaN | 777.8429 | 1254.8641 | NaN | NaN | 1253.5935 | NaN | NaN | NaN | NaN | 1253.7248 | 1254.2941 | NaN | 18.3405 | NaN | 24.8585
9786.1292 | 729.981 | 572.6224 | 337.8568 | 332.7803 | 342.1725 | 465.1124 | 540.1312 | 436.1498 | NaN | NaN | NaN | 790.6268 | 1254.8633 | NaN | NaN | 1253.5927 | NaN | NaN | NaN | NaN | 1253.7241 | 1254.2933 | NaN | 19.1898 | NaN | 25.1843
9787.1292 | 728.2674 | 571.1632 | 339.1957 | 332.6636 | 341.6971 | 466.4155 | 540.9123 | 435.5945 | NaN | NaN | NaN | 787.4908 | 1254.8626 | NaN | NaN | 1253.592 | NaN | NaN | NaN | NaN | 1253.7234 | 1254.2926 | NaN | 15.8716 | NaN | 24.4735
9788.1292 | 727.2509 | 570.1603 | 338.298 | 332.1466 | 341.4862 | 466.5518 | 540.1718 | 435.8018 | NaN | NaN | NaN | 776.0384 | 1254.8635 | NaN | NaN | 1253.5928 | NaN | NaN | NaN | NaN | 1253.7242 | 1254.2935 | NaN | 18.0688 | NaN | 24.9773
9789.1292 | 728.063 | 571.4044 | 338.6043 | 331.7784 | 341.4754 | 467.8486 | 536.7041 | 437.3664 | NaN | NaN | NaN | 771.7893 | 1254.8623 | NaN | NaN | 1253.5916 | NaN | NaN | NaN | NaN | 1253.723 | 1254.2923 | NaN | 16.0506 | NaN | 24.6965
9790.1292 | 727.8638 | 570.5488 | 338.8832 | 331.4918 | 341.4236 | 467.9129 | 538.9209 | 438.0153 | NaN | NaN | NaN | 732.4663 | 1254.8622 | NaN | NaN | 1253.5915 | NaN | NaN | NaN | NaN | 1253.7229 | 1254.2922 | NaN | 15.8203 | NaN | 24.7862
9791.1292 | 726.0028 | 569.3105 | 339.326 | 331.196 | 341.3527 | 466.443 | 536.7522 | 437.2017 | NaN | NaN | NaN | 693.8594 | 1254.862 | NaN | NaN | 1253.5913 | NaN | NaN | NaN | NaN | 1253.7227 | 1254.292 | NaN | 17.0117 | NaN | 25.001
9792.1292 | 724.4242 | 568.9806 | 339.1489 | 331.8577 | 341.404 | 468.0387 | 539.2257 | 435.8873 | NaN | NaN | NaN | 664.329 | 1254.8614 | NaN | NaN | 1253.5908 | NaN | NaN | NaN | NaN | 1253.7221 | 1254.2914 | NaN | 15.4862 | NaN | 25.0727
9793.1292 | 722.5539 | 568.3541 | 338.1872 | 331.7867 | 341.9481 | 466.5959 | 535.8439 | 434.4291 | NaN | NaN | NaN | 641.2845 | 1254.8611 | NaN | NaN | 1253.5905 | NaN | NaN | NaN | NaN | 1253.7219 | 1254.2911 | NaN | 15.0536 | NaN | 23.6469
9794.1292 | 724.9491 | 568.571 | 337.5921 | 331.8238 | 341.7768 | 467.8394 | 533.7105 | 431.685 | NaN | NaN | NaN | 616.5579 | 1254.8613 | NaN | NaN | 1253.5906 | NaN | NaN | NaN | NaN | 1253.722 | 1254.2912 | NaN | 16.8797 | NaN | 23.3336
9795.1292 | 727.0888 | 568.1487 | 337.0744 | 331.7863 | 341.551 | 467.5568 | 533.3346 | 433.1397 | NaN | NaN | NaN | 596.9801 | 1254.8603 | NaN | NaN | 1253.5897 | NaN | NaN | NaN | NaN | 1253.7211 | 1254.2903 | NaN | 16.1662 | NaN | 24.2779
9796.1292 | 727.2525 | 569.1826 | 336.6882 | 332.3878 | 341.6845 | 468.2102 | 537.4713 | 435.5985 | NaN | NaN | NaN | 577.9114 | 1254.8608 | NaN | NaN | 1253.5901 | NaN | NaN | NaN | NaN | 1253.7215 | 1254.2907 | NaN | 16.7853 | NaN | 24.3814
9797.1292 | 727.2188 | 569.7071 | 336.8971 | 332.6629 | 341.4144 | 468.5354 | 539.1247 | 436.8141 | NaN | NaN | NaN | 591.2241 | 1254.8602 | NaN | NaN | 1253.5896 | NaN | NaN | NaN | NaN | 1253.721 | 1254.2902 | NaN | 14.5101 | NaN | 24.236
9798.1292 | 725.9164 | 569.9079 | 336.5542 | 332.7672 | 342.6372 | 467.4829 | 537.9913 | 436.5541 | NaN | NaN | NaN | 569.3077 | 1254.8598 | NaN | NaN | 1253.5891 | NaN | NaN | NaN | NaN | 1253.7205 | 1254.2898 | NaN | 16.1331 | NaN | 23.5159
9799.1292 | 724.5293 | 571.6418 | 336.6658 | 332.9568 | 342.8351 | 467.3303 | 534.7471 | 433.6763 | NaN | NaN | NaN | 561.8754 | 1254.8602 | NaN | NaN | 1253.5895 | NaN | NaN | NaN | NaN | 1253.7209 | 1254.2902 | NaN | 16.1408 | NaN | 22.9037
9800.1292 | 723.7462 | 570.873 | 336.0556 | 332.9891 | 342.7514 | 465.8222 | 535.4359 | 432.7377 | NaN | NaN | NaN | 603.7397 | 1254.8598 | NaN | NaN | 1253.5891 | NaN | NaN | NaN | NaN | 1253.7205 | 1254.2898 | NaN | 17.308 | NaN | 25.0635
9801.1292 | 723.8825 | 572.6435 | 336.0659 | 333.0617 | 343.3684 | 466.3148 | 534.5995 | 433.4269 | NaN | NaN | NaN | 632.8387 | 1254.8599 | NaN | NaN | 1253.5892 | NaN | NaN | NaN | NaN | 1253.7206 | 1254.2899 | NaN | 15.3826 | NaN | 23.8265
9802.1292 | 723.8458 | 573.1689 | 336.0874 | 332.5404 | 342.8542 | 464.7082 | 531.4718 | 432.7436 | NaN | NaN | NaN | 679.3114 | 1254.8591 | NaN | NaN | 1253.5884 | NaN | NaN | NaN | NaN | 1253.7198 | 1254.289 | NaN | 13.8547 | NaN | 25.0376
9803.1292 | 723.7615 | 572.5682 | 336.3826 | 332.8065 | 342.9471 | 463.2897 | 531.5012 | 433.0138 | NaN | NaN | NaN | 712.9981 | 1254.8595 | NaN | NaN | 1253.5888 | NaN | NaN | NaN | NaN | 1253.7202 | 1254.2895 | NaN | 16.1199 | NaN | 23.0032
9804.1292 | 724.6611 | 574.0454 | 335.6025 | 332.3802 | 342.4691 | 463.3889 | 542.1168 | 434.1963 | NaN | NaN | NaN | 702.3266 | 1254.8591 | NaN | NaN | 1253.5884 | NaN | NaN | NaN | NaN | 1253.7198 | 1254.2891 | NaN | 15.5518 | NaN | 24.3593
9805.1292 | 723.5517 | 575.3966 | 336.196 | 332.2226 | 342.3472 | 462.596 | 543.9714 | 434.0502 | NaN | NaN | NaN | 710.4983 | 1254.8576 | NaN | NaN | 1253.5869 | NaN | NaN | NaN | NaN | 1253.7183 | 1254.2876 | NaN | 15.5083 | NaN | 24.6231
9806.1292 | 722.3864 | 577.7243 | 335.6526 | 332.3069 | 342.3689 | 461.5999 | 543.6177 | 432.8501 | NaN | NaN | NaN | 735.5865 | 1254.8577 | NaN | NaN | 1253.587 | NaN | NaN | NaN | NaN | 1253.7184 | 1254.2877 | NaN | 16.1866 | NaN | 23.92
9807.1292 | 722.4448 | 577.7056 | 335.4986 | 332.5945 | 342.7013 | 462.0823 | 541.2904 | 432.3767 | NaN | NaN | NaN | 741.5569 | 1254.8575 | NaN | NaN | 1253.5868 | NaN | NaN | NaN | NaN | 1253.7182 | 1254.2875 | NaN | 16.2831 | NaN | 24.9691
9808.1292 | 721.8957 | 579.7575 | 335.3234 | 333.0503 | 343.1833 | 460.9648 | 540.9844 | 431.911 | NaN | NaN | NaN | 762.0059 | 1254.8569 | NaN | NaN | 1253.5862 | NaN | NaN | NaN | NaN | 1253.7176 | 1254.2869 | NaN | 16.1238 | NaN | 25.2848
9809.1292 | 720.5395 | 581.0629 | 336.3566 | 333.3528 | 343.3175 | 461.7638 | 542.9871 | 432.2869 | NaN | NaN | NaN | 769.5855 | 1254.8571 | NaN | NaN | 1253.5864 | NaN | NaN | NaN | NaN | 1253.7178 | 1254.2871 | NaN | 16.303 | NaN | 24.3722
9810.1292 | 720.0096 | 581.7706 | 335.5197 | 333.313 | 343.1741 | 460.6993 | 542.5319 | 432.7089 | NaN | NaN | NaN | 765.0498 | 1254.856 | NaN | NaN | 1253.5853 | NaN | NaN | NaN | NaN | 1253.7167 | 1254.286 | NaN | 14.3082 | NaN | 24.4561
9811.1292 | 719.4169 | 580.521 | 335.3837 | 333.106 | 343.2347 | 462.0871 | 540.8715 | 433.2556 | NaN | NaN | NaN | 731.3631 | 1254.8567 | NaN | NaN | 1253.586 | NaN | NaN | NaN | NaN | 1253.7174 | 1254.2867 | NaN | 14.9654 | NaN | 24.3492
9812.1292 | 718.364 | 579.9337 | 334.9728 | 332.5669 | 343.1802 | 460.0526 | 537.5214 | 434.6458 | NaN | NaN | NaN | 709.9315 | 1254.8567 | NaN | NaN | 1253.586 | NaN | NaN | NaN | NaN | 1253.7174 | 1254.2867 | NaN | 17.8837 | NaN | 24.1348
9813.1292 | 717.6323 | 581.6963 | 335.1539 | 332.4947 | 343.3093 | 457.5389 | 546.0479 | 436.5285 | NaN | NaN | NaN | 721.1435 | 1254.855 | NaN | NaN | 1253.5843 | NaN | NaN | NaN | NaN | 1253.7157 | 1254.285 | NaN | 15.6374 | NaN | 25.1995
9814.1292 | 716.5169 | 582.6388 | 335.5467 | 332.6689 | 343.6211 | 455.1487 | 555.0788 | 437.483 | NaN | NaN | NaN | 720.7237 | 1254.8561 | NaN | NaN | 1253.5854 | NaN | NaN | NaN | NaN | 1253.7168 | 1254.2861 | NaN | 16.0698 | NaN | 24.2491
9815.1292 | 715.4006 | 582.1928 | 335.1083 | 332.446 | 343.7748 | 453.1238 | 556.1305 | 436.4076 | NaN | NaN | NaN | 685.4379 | 1254.8551 | NaN | NaN | 1253.5844 | NaN | NaN | NaN | NaN | 1253.7158 | 1254.2851 | NaN | 14.6963 | NaN | 20.1809
9816.1292 | 715.6262 | 582.4045 | 335.1005 | 333.0422 | 343.5776 | 450.5467 | 550.4427 | 435.6701 | NaN | NaN | NaN | 670.9611 | 1254.855 | NaN | NaN | 1253.5843 | NaN | NaN | NaN | NaN | 1253.7157 | 1254.285 | NaN | 15.5576 | NaN | 21.7873
9817.1292 | 715.5129 | 580.6701 | 335.3152 | 333.5626 | 343.6861 | 449.8197 | 546.7796 | 433.8017 | NaN | NaN | NaN | 672.6745 | 1254.854 | NaN | NaN | 1253.5833 | NaN | NaN | NaN | NaN | 1253.7147 | 1254.284 | NaN | 15.7501 | NaN | 24.0173
9818.1448 | 716.6092 | 579.8164 | 335.4161 | 333.2443 | 343.6014 | 449.0566 | 544.8126 | 433.4795 | NaN | NaN | NaN | 681.5228 | 1254.854 | NaN | NaN | 1253.5833 | NaN | NaN | NaN | NaN | 1253.7147 | 1254.284 | NaN | 15.6163 | NaN | 24.7912
9819.1448 | 716.931 | 579.3479 | 335.5888 | 332.9545 | 343.3949 | 447.2802 | 542.8393 | 433.4566 | NaN | NaN | NaN | 660.4575 | 1254.8538 | NaN | NaN | 1253.5831 | NaN | NaN | NaN | NaN | 1253.7145 | 1254.2838 | NaN | 17.8538 | NaN | 23.9376
9820.1292 | 716.9849 | 580.2364 | 335.9576 | 332.7173 | 343.0053 | 446.3567 | 544.1787 | 433.1485 | NaN | NaN | NaN | 635.5237 | 1254.8545 | NaN | NaN | 1253.5838 | NaN | NaN | NaN | NaN | 1253.7152 | 1254.2845 | NaN | 17.5463 | NaN | 22.6608
9821.1292 | 718.3861 | 580.8097 | 336.0246 | 332.636 | 342.4154 | 448.6187 | 548.5122 | 432.5691 | NaN | NaN | NaN | 628.1617 | 1254.8526 | NaN | NaN | 1253.5819 | NaN | NaN | NaN | NaN | 1253.7133 | 1254.2826 | NaN | 18.1278 | NaN | 24.0345
9822.1448 | 719.6155 | 580.4305 | 336.1172 | 332.6158 | 342.5076 | 448.4523 | 546.9615 | 432.0068 | NaN | NaN | NaN | 612.3195 | 1254.8534 | NaN | NaN | 1253.5828 | NaN | NaN | NaN | NaN | 1253.7142 | 1254.2834 | NaN | 16.1798 | NaN | 23.0435
9823.1292 | 723.281 | 581.7388 | 336.0656 | 332.7186 | 342.3562 | 451.3042 | 543.3921 | 431.3697 | NaN | NaN | NaN | 587.9595 | 1254.8536 | NaN | NaN | 1253.583 | NaN | NaN | NaN | NaN | 1253.7144 | 1254.2836 | NaN | 17.7196 | NaN | 23.4852
9824.1448 | 724.7128 | 581.2982 | 336.6356 | 332.8286 | 342.2572 | 452.4034 | 542.8947 | 433.9158 | NaN | NaN | NaN | 595.6106 | 1254.852 | NaN | NaN | 1253.5814 | NaN | NaN | NaN | NaN | 1253.7128 | 1254.282 | NaN | 16.2302 | NaN | 23.9642
9825.1292 | 724.7091 | 580.0612 | 337.2627 | 333.199 | 342.6003 | 453.5999 | 542.9126 | 432.3559 | NaN | NaN | NaN | 587.7024 | 1254.8517 | NaN | NaN | 1253.5811 | NaN | NaN | NaN | NaN | 1253.7125 | 1254.2817 | NaN | 15.8572 | NaN | 22.3535
9826.1292 | 724.7391 | 579.6804 | 337.3403 | 332.9989 | 342.6937 | 452.431 | 543.566 | 431.9505 | NaN | NaN | NaN | 593.7574 | 1254.8526 | NaN | NaN | 1253.5819 | NaN | NaN | NaN | NaN | 1253.7133 | 1254.2826 | NaN | 15.59 | NaN | 23.9921
9827.1292 | 723.2199 | 580.2269 | 337.486 | 332.7645 | 342.6967 | 450.8828 | 544.7454 | 431.5615 | NaN | NaN | NaN | 577.7193 | 1254.851 | NaN | NaN | 1253.5803 | NaN | NaN | NaN | NaN | 1253.7117 | 1254.281 | NaN | 15.5986 | NaN | 23.6126
9828.1292 | 723.9503 | 582.067 | 337.2385 | 332.5441 | 342.8069 | 453.1762 | 547.4889 | 430.9209 | NaN | NaN | NaN | 562.3006 | 1254.8516 | NaN | NaN | 1253.581 | NaN | NaN | NaN | NaN | 1253.7124 | 1254.2816 | NaN | 16.6737 | NaN | 23.5179
9829.1292 | 724.4134 | 582.613 | 337.6406 | 332.3001 | 342.895 | 453.1273 | 547.6857 | 432.21 | NaN | NaN | NaN | 548.7939 | 1254.8507 | NaN | NaN | 1253.5801 | NaN | NaN | NaN | NaN | 1253.7114 | 1254.2807 | NaN | 15.3693 | NaN | 23.8571
9830.1292 | 725.2806 | 581.7996 | 338.2445 | 332.511 | 343.1795 | 453.43 | 543.6162 | 432.957 | NaN | NaN | NaN | 554.4475 | 1254.8508 | NaN | NaN | 1253.5802 | NaN | NaN | NaN | NaN | 1253.7116 | 1254.2808 | NaN | 15.0609 | NaN | 24.4588
9831.1292 | 725.574 | 580.9318 | 338.3913 | 332.3499 | 343.5804 | 453.8023 | 544.0814 | 432.7632 | NaN | NaN | NaN | 570.3744 | 1254.8505 | NaN | NaN | 1253.5799 | NaN | NaN | NaN | NaN | 1253.7113 | 1254.2805 | NaN | 13.9189 | NaN | 23.7568
9832.1292 | 723.8836 | 580.8491 | 339.2412 | 331.9755 | 343.4844 | 453.4182 | 541.6503 | 431.4594 | NaN | NaN | NaN | 613.1394 | 1254.8504 | NaN | NaN | 1253.5798 | NaN | NaN | NaN | NaN | 1253.7112 | 1254.2804 | NaN | 15.3495 | NaN | 24.9142
9833.1292 | 723.3114 | 580.1727 | 339.3435 | 332.172 | 343.2475 | 452.9431 | 537.6479 | 430.7231 | NaN | NaN | NaN | 623.8526 | 1254.849 | NaN | NaN | 1253.5784 | NaN | NaN | NaN | NaN | 1253.7098 | 1254.279 | NaN | 14.8511 | NaN | 24.8145
9834.1292 | 722.7739 | 579.416 | 339.2917 | 332.6809 | 343.1903 | 452.7928 | 534.855 | 429.4617 | NaN | NaN | NaN | 640.5987 | 1254.8495 | NaN | NaN | 1253.5789 | NaN | NaN | NaN | NaN | 1253.7103 | 1254.2795 | NaN | 14.8777 | NaN | 23.4945
9835.1292 | 722.1483 | 579.4768 | 338.4421 | 332.5324 | 342.9734 | 452.9499 | 532.919 | 428.6777 | NaN | NaN | NaN | 633.5901 | 1254.8489 | NaN | NaN | 1253.5782 | NaN | NaN | NaN | NaN | 1253.7096 | 1254.2789 | NaN | 15.0677 | NaN | 23.8333
9836.1292 | 721.5887 | 579.3942 | 338.7884 | 332.2184 | 342.6204 | 454.5605 | 531.7753 | 429.2295 | NaN | NaN | NaN | 628.716 | 1254.8486 | NaN | NaN | 1253.578 | NaN | NaN | NaN | NaN | 1253.7094 | 1254.2786 | NaN | 15.8625 | NaN | 24.636
9837.1292 | 721.3781 | 578.3859 | 338.1783 | 332.4487 | 342.6083 | 455.206 | 531.5886 | 429.1903 | NaN | NaN | NaN | 650.334 | 1254.8492 | NaN | NaN | 1253.5785 | NaN | NaN | NaN | NaN | 1253.7099 | 1254.2792 | NaN | 15.9006 | NaN | 21.9809
9838.1292 | 723.391 | 578.2349 | 337.5468 | 332.4073 | 342.6811 | 456.4876 | 530.7867 | 429.2381 | NaN | NaN | NaN | 635.4369 | 1254.8498 | NaN | NaN | 1253.5792 | NaN | NaN | NaN | NaN | 1253.7106 | 1254.2798 | NaN | 14.3211 | NaN | 23.3467
9839.1292 | 725.472 | 577.817 | 337.4515 | 332.0364 | 342.7331 | 457.9975 | 531.2754 | 430.6236 | NaN | NaN | NaN | 633.2862 | 1254.8477 | NaN | NaN | 1253.577 | NaN | NaN | NaN | NaN | 1253.7084 | 1254.2777 | NaN | 14.9216 | NaN | 22.0688
9840.1292 | 726.6943 | 579.61 | 337.3898 | 332.1159 | 342.9577 | 455.5891 | 530.3807 | 432.188 | NaN | NaN | NaN | 648.629 | 1254.8481 | NaN | NaN | 1253.5774 | NaN | NaN | NaN | NaN | 1253.7088 | 1254.2781 | NaN | 15.2862 | NaN | 24.1976
9841.1292 | 726.0848 | 582.0942 | 337.167 | 332.877 | 343.0856 | 455.0384 | 532.3674 | 433.5256 | NaN | NaN | NaN | 667.8569 | 1254.8465 | NaN | NaN | 1253.5758 | NaN | NaN | NaN | NaN | 1253.7072 | 1254.2765 | NaN | 15.188 | NaN | 22.3296
9842.1292 | 725.4045 | 583.1853 | 337.2525 | 332.9924 | 343.0809 | 455.5655 | 532.2543 | 433.447 | NaN | NaN | NaN | 643.5352 | 1254.8464 | NaN | NaN | 1253.5757 | NaN | NaN | NaN | NaN | 1253.7071 | 1254.2764 | NaN | 15.1896 | NaN | 23.5927
9843.1292 | 724.1351 | 583.0933 | 337.0742 | 333.1826 | 343.1058 | 456.1421 | 534.2902 | 433.9637 | NaN | NaN | NaN | 631.5892 | 1254.8465 | NaN | NaN | 1253.5758 | NaN | NaN | NaN | NaN | 1253.7072 | 1254.2765 | NaN | 15.1592 | NaN | 24.7843
9844.1292 | 723.6478 | 584.4458 | 337.2016 | 332.9295 | 343.4449 | 459.4258 | 535.5981 | 433.2463 | NaN | NaN | NaN | 669.0446 | 1254.8456 | NaN | NaN | 1253.5749 | NaN | NaN | NaN | NaN | 1253.7063 | 1254.2756 | NaN | 15.4728 | NaN | 21.8529
9845.1292 | 722.8823 | 584.7901 | 336.9683 | 332.8073 | 343.5002 | 460.5897 | 538.992 | 432.8953 | NaN | NaN | NaN | 658.0713 | 1254.8455 | NaN | NaN | 1253.5749 | NaN | NaN | NaN | NaN | 1253.7063 | 1254.2755 | NaN | 15.6264 | NaN | 22.0425
9846.1292 | 722.8915 | 583.825 | 337.6528 | 332.947 | 343.3681 | 461.2358 | 536.9385 | 433.0131 | NaN | NaN | NaN | 690.1762 | 1254.8455 | NaN | NaN | 1253.5749 | NaN | NaN | NaN | NaN | 1253.7063 | 1254.2755 | NaN | 15.4294 | NaN | 21.141
9847.1292 | 723.696 | 583.329 | 338.2019 | 333.1724 | 343.386 | 458.9262 | 533.989 | 433.2788 | NaN | NaN | NaN | 718.2881 | 1254.8455 | NaN | NaN | 1253.5748 | NaN | NaN | NaN | NaN | 1253.7062 | 1254.2755 | NaN | 16.6663 | NaN | 22.0768
9848.1292 | 723.1653 | 587.6127 | 338.8769 | 333.1678 | 343.3304 | 456.5809 | 534.8862 | 434.9291 | NaN | NaN | NaN | 714.1079 | 1254.8446 | NaN | NaN | 1253.574 | NaN | NaN | NaN | NaN | 1253.7054 | 1254.2746 | NaN | 15.9287 | NaN | 24.6181
9849.1292 | 722.6161 | 589.0214 | 338.4179 | 333.2673 | 343.2959 | 457.1832 | 536.7928 | 435.9677 | NaN | NaN | NaN | 703.2045 | 1254.8451 | NaN | NaN | 1253.5745 | NaN | NaN | NaN | NaN | 1253.7058 | 1254.2751 | NaN | 15.716 | NaN | 24.0553
9850.1292 | 724.0343 | 587.7181 | 337.6253 | 333.2444 | 343.2266 | 457.7262 | 533.35 | 435.3338 | NaN | NaN | NaN | 696.1962 | 1254.8445 | NaN | NaN | 1253.5738 | NaN | NaN | NaN | NaN | 1253.7052 | 1254.2745 | NaN | 16.5538 | NaN | 24.4847
9851.1292 | 724.7365 | 586.8289 | 337.8077 | 333.2193 | 342.9902 | 456.0504 | 530.0918 | 436.6545 | NaN | NaN | NaN | 681.5266 | 1254.8437 | NaN | NaN | 1253.5731 | NaN | NaN | NaN | NaN | 1253.7044 | 1254.2737 | NaN | 17.0611 | NaN | 23.5618
9852.1292 | 723.3345 | 585.8907 | 338.0526 | 333.5762 | 343.2729 | 455.886 | 530.4352 | 435.9218 | NaN | NaN | NaN | 712.349 | 1254.8443 | NaN | NaN | 1253.5736 | NaN | NaN | NaN | NaN | 1253.705 | 1254.2742 | NaN | 15.7579 | NaN | 24.6071
9853.1292 | 722.4783 | 584.2482 | 338.0687 | 333.9973 | 343.4499 | 457.0533 | 531.9344 | 435.6644 | NaN | NaN | NaN | 728.6542 | 1254.8439 | NaN | NaN | 1253.5733 | NaN | NaN | NaN | NaN | 1253.7046 | 1254.2739 | NaN | 16.1661 | NaN | 23.3706
9854.1292 | 722.2453 | 583.8979 | 338.4296 | 333.9708 | 343.5879 | 457.1154 | 530.5584 | 435.03 | NaN | NaN | NaN | 729.3935 | 1254.8436 | NaN | NaN | 1253.5729 | NaN | NaN | NaN | NaN | 1253.7043 | 1254.2736 | NaN | 17.1468 | NaN | 23.9591
9855.1292 | 722.0251 | 584.7039 | 338.7557 | 333.6282 | 343.3027 | 458.6682 | 527.6169 | 433.1565 | NaN | NaN | NaN | 738.7176 | 1254.8426 | NaN | NaN | 1253.572 | NaN | NaN | NaN | NaN | 1253.7033 | 1254.2726 | NaN | 18.2501 | NaN | 24.045
9856.1292 | 722.7049 | 584.062 | 338.9389 | 333.8129 | 343.2182 | 458.59 | 524.8609 | 430.4528 | NaN | NaN | NaN | 720.9904 | 1254.8436 | NaN | NaN | 1253.5729 | NaN | NaN | NaN | NaN | 1253.7043 | 1254.2736 | NaN | 15.746 | NaN | 23.2456
9857.1292 | 722.887 | 582.6624 | 338.7124 | 333.9082 | 343.1438 | 458.653 | 524.6521 | 430.2445 | NaN | NaN | NaN | 680.1866 | 1254.8434 | NaN | NaN | 1253.5728 | NaN | NaN | NaN | NaN | 1253.7042 | 1254.2734 | NaN | 15.6545 | NaN | 24.5279
9858.1292 | 722.4581 | 582.7707 | 338.7721 | 333.854 | 343.4683 | 459.6316 | 524.97 | 430.9229 | NaN | NaN | NaN | 652.9708 | 1254.8423 | NaN | NaN | 1253.5716 | NaN | NaN | NaN | NaN | 1253.703 | 1254.2723 | NaN | 15.5313 | NaN | 24.8983
9859.1292 | 721.8304 | 582.3169 | 338.8465 | 333.6129 | 343.1327 | 461.3488 | 526.3119 | 431.2513 | NaN | NaN | NaN | 686.0715 | 1254.8421 | NaN | NaN | 1253.5714 | NaN | NaN | NaN | NaN | 1253.7028 | 1254.2721 | NaN | 17.6392 | NaN | 25.1006
9860.1292 | 721.0139 | 581.3059 | 338.7844 | 334.1625 | 343.2748 | 462.0648 | 527.7467 | 431.4774 | NaN | NaN | NaN | 706.0647 | 1254.8406 | NaN | NaN | 1253.57 | NaN | NaN | NaN | NaN | 1253.7014 | 1254.2706 | NaN | 15.1604 | NaN | 21.6703
9861.1292 | 720.3175 | 580.1134 | 339.127 | 334.2032 | 343.3595 | 460.9116 | 525.1504 | 430.9428 | NaN | NaN | NaN | 707.1172 | 1254.8414 | NaN | NaN | 1253.5707 | NaN | NaN | NaN | NaN | 1253.7021 | 1254.2714 | NaN | 15.9429 | NaN | 24.4916
9862.1292 | 719.0065 | 579.4601 | 339.3332 | 334.0562 | 343.3783 | 459.1964 | 522.9439 | 429.6171 | NaN | NaN | NaN | 696.6484 | 1254.8407 | NaN | NaN | 1253.5701 | NaN | NaN | NaN | NaN | 1253.7014 | 1254.2707 | NaN | 15.653 | NaN | 25.148
9863.1292 | 718.8073 | 579.8699 | 339.5134 | 333.6002 | 343.0083 | 458.2776 | 520.6331 | 427.3161 | NaN | NaN | NaN | 701.5492 | 1254.8395 | NaN | NaN | 1253.5689 | NaN | NaN | NaN | NaN | 1253.7003 | 1254.2695 | NaN | 16.3021 | NaN | 24.9266
9864.1292 | 717.6025 | 578.9664 | 339.6831 | 333.0996 | 342.3401 | 457.3659 | 519.2289 | 427.3272 | NaN | NaN | NaN | 703.9795 | 1254.8399 | NaN | NaN | 1253.5692 | NaN | NaN | NaN | NaN | 1253.7006 | 1254.2699 | NaN | 15.8537 | NaN | 24.7596
9865.1292 | 718.2479 | 581.1241 | 339.8385 | 333.3786 | 342.0364 | 456.8623 | 517.316 | 429.7187 | NaN | NaN | NaN | 720.0525 | 1254.8406 | NaN | NaN | 1253.5699 | NaN | NaN | NaN | NaN | 1253.7013 | 1254.2706 | NaN | 15.857 | NaN | 24.4354
9866.1292 | 718.1449 | 588.7411 | 339.5285 | 333.5645 | 342.0301 | 456.4644 | 523.3179 | 432.3167 | NaN | NaN | NaN | 734.4491 | 1254.8386 | NaN | NaN | 1253.5679 | NaN | NaN | NaN | NaN | 1253.6993 | 1254.2686 | NaN | 15.8083 | NaN | 23.3585
9867.1292 | 718.3532 | 590.5256 | 339.5071 | 333.9629 | 343.3405 | 456.7854 | 524.9775 | 432.8831 | NaN | NaN | NaN | 749.8373 | 1254.8397 | NaN | NaN | 1253.569 | NaN | NaN | NaN | NaN | 1253.7004 | 1254.2697 | NaN | 14.4021 | NaN | 22.41
9868.1292 | 718.1198 | 592.3508 | 339.6665 | 334.1055 | 343.9659 | 457.8971 | 525.1199 | 435.1537 | NaN | NaN | NaN | 762.0554 | 1254.8389 | NaN | NaN | 1253.5682 | NaN | NaN | NaN | NaN | 1253.6996 | 1254.2689 | NaN | 14.9821 | NaN | 24.7075
9869.1292 | 718.1717 | 593.537 | 339.9742 | 334.6449 | 344.4312 | 458.2467 | 527.7087 | 435.4394 | NaN | NaN | NaN | 760.6412 | 1254.8389 | NaN | NaN | 1253.5682 | NaN | NaN | NaN | NaN | 1253.6996 | 1254.2689 | NaN | 16.2225 | NaN | 24.994
9870.1292 | 717.5233 | 593.7312 | 340.3558 | 335.0962 | 344.743 | 460.9688 | 527.589 | 434.1206 | NaN | NaN | NaN | 742.5677 | 1254.8376 | NaN | NaN | 1253.567 | NaN | NaN | NaN | NaN | 1253.6983 | 1254.2676 | NaN | 15.4214 | NaN | 22.7422
9871.1292 | 716.8941 | 591.7904 | 340.6793 | 334.8681 | 345.0383 | 463.109 | 526.6743 | 432.2588 | NaN | NaN | NaN | 747.2438 | 1254.8376 | NaN | NaN | 1253.567 | NaN | NaN | NaN | NaN | 1253.6983 | 1254.2676 | NaN | 15.4645 | NaN | 24.0716
9872.1292 | 716.4741 | 590.9585 | 340.7219 | 334.7686 | 344.9031 | 463.6363 | 529.6989 | 430.8643 | NaN | NaN | NaN | 736.6758 | 1254.8389 | NaN | NaN | 1253.5683 | NaN | NaN | NaN | NaN | 1253.6997 | 1254.2689 | NaN | 15.1401 | NaN | 25.1209
9873.1292 | 715.8712 | 591.1605 | 341.0552 | 334.9581 | 344.6216 | 465.2292 | 529.6191 | 430.7716 | NaN | NaN | NaN | 706.2747 | 1254.838 | NaN | NaN | 1253.5674 | NaN | NaN | NaN | NaN | 1253.6987 | 1254.268 | NaN | 15.422 | NaN | 22.9347
9874.1292 | 715.8082 | 589.7975 | 340.975 | 335.1716 | 344.5731 | 465.2875 | 529.5921 | 430.6637 | NaN | NaN | NaN | 718.3475 | 1254.837 | NaN | NaN | 1253.5664 | NaN | NaN | NaN | NaN | 1253.6977 | 1254.267 | NaN | 15.2213 | NaN | 23.1217
9875.1292 | 715.6191 | 589.0866 | 340.7766 | 335.1768 | 344.4269 | 464.3233 | 529.4218 | 430.8693 | NaN | NaN | NaN | 734.2623 | 1254.8366 | NaN | NaN | 1253.5659 | NaN | NaN | NaN | NaN | 1253.6973 | 1254.2666 | NaN | 14.4654 | NaN | 24.4188
9876.1292 | 716.0216 | 590.6062 | 340.9836 | 335.0801 | 344.2208 | 464.0339 | 529.5309 | 431.3783 | NaN | NaN | NaN | 731.8078 | 1254.8353 | NaN | NaN | 1253.5647 | NaN | NaN | NaN | NaN | 1253.6961 | 1254.2653 | NaN | 15.8204 | NaN | 25.0714
9877.1292 | 715.8482 | 591.4339 | 340.9369 | 334.975 | 344.173 | 465.2578 | 527.2615 | 432.7374 | NaN | NaN | NaN | 751.4047 | 1254.8361 | NaN | NaN | 1253.5655 | NaN | NaN | NaN | NaN | 1253.6969 | 1254.2661 | NaN | 17.9209 | NaN | 22.4604
9878.1292 | 715.7531 | 590.4014 | 341.0376 | 334.7883 | 344.2426 | 466.494 | 527.0946 | 433.0541 | NaN | NaN | NaN | 728.9481 | 1254.8347 | NaN | NaN | 1253.5641 | NaN | NaN | NaN | NaN | 1253.6955 | 1254.2647 | NaN | 15.1604 | NaN | 25.1241
9879.1292 | 717.3814 | 588.8415 | 340.9117 | 335.2313 | 344.7045 | 467.4735 | 526.7699 | 431.5561 | NaN | NaN | NaN | 707.2185 | 1254.8347 | NaN | NaN | 1253.564 | NaN | NaN | NaN | NaN | 1253.6954 | 1254.2647 | NaN | 16.8739 | NaN | 23.7323
9880.1292 | 718.5506 | 592.9258 | 340.4076 | 335.4021 | 344.6386 | 466.8375 | 523.0582 | 433.0678 | NaN | NaN | NaN | 703.1434 | 1254.8339 | NaN | NaN | 1253.5633 | NaN | NaN | NaN | NaN | 1253.6946 | 1254.2639 | NaN | 14.3067 | NaN | 25.2362
9881.1292 | 719.6034 | 598.8172 | 340.6331 | 335.1998 | 344.6539 | 467.5582 | 525.7981 | 437.1291 | NaN | NaN | NaN | 728.9703 | 1254.8345 | NaN | NaN | 1253.5638 | NaN | NaN | NaN | NaN | 1253.6952 | 1254.2645 | NaN | 13.6392 | NaN | 23.8567
9882.1292 | 721.6255 | 599.1601 | 340.7875 | 335.1381 | 344.9876 | 468.4368 | 530.4865 | 440.6319 | NaN | NaN | NaN | 749.255 | 1254.8346 | NaN | NaN | 1253.564 | NaN | NaN | NaN | NaN | 1253.6953 | 1254.2646 | NaN | 17.1008 | NaN | 25.0543
9883.1292 | 724.1581 | 598.0723 | 341.1548 | 335.2902 | 345.2072 | 469.5717 | 532.4165 | 439.6444 | NaN | NaN | NaN | 720.8557 | 1254.8337 | NaN | NaN | 1253.5631 | NaN | NaN | NaN | NaN | 1253.6945 | 1254.2637 | NaN | 14.6487 | NaN | 24.861
9884.1292 | 725.2408 | 596.4837 | 341.612 | 335.7675 | 345.7311 | 470.2516 | 530.5818 | 440.0769 | NaN | NaN | NaN | 694.94 | 1254.8335 | NaN | NaN | 1253.5629 | NaN | NaN | NaN | NaN | 1253.6943 | 1254.2635 | NaN | 17.2214 | NaN | 23.2831
9885.1292 | 725.8274 | 599.9725 | 341.4965 | 335.8216 | 346.0389 | 469.8589 | 532.3177 | 438.3841 | NaN | NaN | NaN | 716.6929 | 1254.8331 | NaN | NaN | 1253.5625 | NaN | NaN | NaN | NaN | 1253.6938 | 1254.2631 | NaN | 14.4239 | NaN | 22.9815
9886.1292 | 725.6062 | 598.2481 | 341.8401 | 335.8532 | 346.5357 | 471.5387 | 533.5075 | 437.5069 | NaN | NaN | NaN | 725.4011 | 1254.8332 | NaN | NaN | 1253.5626 | NaN | NaN | NaN | NaN | 1253.694 | 1254.2632 | NaN | 14.6385 | NaN | 25.2536
9887.1292 | 724.7178 | 596.3798 | 341.767 | 335.5447 | 346.3804 | 470.1189 | 532.6212 | 436.9263 | NaN | NaN | NaN | 712.1884 | 1254.832 | NaN | NaN | 1253.5614 | NaN | NaN | NaN | NaN | 1253.6927 | 1254.262 | NaN | 14.2435 | NaN | 24.0711
9888.1292 | 723.3467 | 595.5063 | 342.0664 | 335.8421 | 346.3674 | 470.8611 | 530.5658 | 435.4786 | NaN | NaN | NaN | 686.8459 | 1254.8328 | NaN | NaN | 1253.5621 | NaN | NaN | NaN | NaN | 1253.6935 | 1254.2628 | NaN | 14.5454 | NaN | 23.6275
9889.1292 | 723.0171 | 592.9636 | 341.573 | 335.6817 | 346.576 | 471.7413 | 529.0362 | 436.042 | NaN | NaN | NaN | 678.7726 | 1254.8327 | NaN | NaN | 1253.5621 | NaN | NaN | NaN | NaN | 1253.6934 | 1254.2627 | NaN | 14.989 | NaN | 24.5014
9890.1292 | 723.0898 | 591.689 | 341.1506 | 335.3828 | 346.3435 | 470.1441 | 530.607 | 435.5931 | NaN | NaN | NaN | 656.578 | 1254.8312 | NaN | NaN | 1253.5606 | NaN | NaN | NaN | NaN | 1253.692 | 1254.2612 | NaN | 14.581 | NaN | 21.8456
9891.1292 | 722.9694 | 590.4193 | 341.0385 | 335.5151 | 346.1041 | 468.6348 | 531.7933 | 435.046 | NaN | NaN | NaN | 625.7822 | 1254.8315 | NaN | NaN | 1253.5609 | NaN | NaN | NaN | NaN | 1253.6923 | 1254.2615 | NaN | 14.8579 | NaN | 24.5167
9892.1292 | 722.8138 | 590.2062 | 341.3992 | 335.369 | 346.2125 | 471.5435 | 529.572 | 435.3244 | NaN | NaN | NaN | 600.8409 | 1254.8306 | NaN | NaN | 1253.56 | NaN | NaN | NaN | NaN | 1253.6914 | 1254.2607 | NaN | 14.4611 | NaN | 23.4639
9893.1292 | 724.716 | 589.5385 | 341.3646 | 335.2799 | 346.4871 | 472.9072 | 537.7787 | 437.196 | NaN | NaN | NaN | 592.8461 | 1254.831 | NaN | NaN | 1253.5604 | NaN | NaN | NaN | NaN | 1253.6917 | 1254.261 | NaN | 15.4879 | NaN | 25.1928
9894.1292 | 724.5249 | 590.996 | 341.5893 | 335.2821 | 346.4032 | 471.5182 | 536.7154 | 438.7998 | NaN | NaN | NaN | 628.9048 | 1254.8299 | NaN | NaN | 1253.5592 | NaN | NaN | NaN | NaN | 1253.6906 | 1254.2599 | NaN | 14.1012 | NaN | 25.1417
9895.1292 | 723.1578 | 590.4857 | 342.3389 | 335.269 | 346.2003 | 468.7069 | 542.4887 | 438.8062 | NaN | NaN | NaN | 660.3804 | 1254.8295 | NaN | NaN | 1253.5588 | NaN | NaN | NaN | NaN | 1253.6902 | 1254.2595 | NaN | 15.5863 | NaN | 23.8594
9896.1292 | 723.1941 | 590.1487 | 342.4812 | 335.4149 | 346.2654 | 466.7273 | 544.3682 | 438.1599 | NaN | NaN | NaN | 688.615 | 1254.8294 | NaN | NaN | 1253.5587 | NaN | NaN | NaN | NaN | 1253.6901 | 1254.2594 | NaN | 14.9127 | NaN | 24.9273
9897.1292 | 722.8499 | 590.3202 | 342.4633 | 335.2045 | 346.0518 | 465.8157 | 541.137 | 436.4066 | NaN | NaN | NaN | 704.1432 | 1254.8293 | NaN | NaN | 1253.5586 | NaN | NaN | NaN | NaN | 1253.69 | 1254.2593 | NaN | 14.9078 | NaN | 22.1037
9898.1292 | 723.0227 | 590.6789 | 342.3312 | 335.031 | 345.6466 | 467.2004 | 538.3218 | 435.6915 | NaN | NaN | NaN | 666.3572 | 1254.8291 | NaN | NaN | 1253.5584 | NaN | NaN | NaN | NaN | 1253.6898 | 1254.2591 | NaN | 17.4117 | NaN | 24.7961
9899.1292 | 722.1567 | 589.8207 | 342.5998 | 334.8731 | 345.4771 | 468.5112 | 541.4626 | 435.8261 | NaN | NaN | NaN | 671.6968 | 1254.8293 | NaN | NaN | 1253.5587 | NaN | NaN | NaN | NaN | 1253.69 | 1254.2593 | NaN | 17.6354 | NaN | 24.9624
9900.1292 | 721.5742 | 590.5599 | 342.4068 | 335.0929 | 345.2025 | 469.8996 | 538.4377 | 434.7851 | NaN | NaN | NaN | 706.7703 | 1254.8287 | NaN | NaN | 1253.558 | NaN | NaN | NaN | NaN | 1253.6894 | 1254.2587 | NaN | 16.723 | NaN | 23.824
9901.1292 | 721.859 | 589.2672 | 341.99 | 335.1864 | 345.4884 | 471.5591 | 533.5615 | 433.3755 | NaN | NaN | NaN | 676.7378 | 1254.8292 | NaN | NaN | 1253.5585 | NaN | NaN | NaN | NaN | 1253.6899 | 1254.2592 | NaN | 18.2714 | NaN | 24.6597
9902.1292 | 720.2986 | 589.9341 | 341.5534 | 335.4305 | 345.713 | 470.046 | 530.2572 | 431.1087 | NaN | NaN | NaN | 660.9188 | 1254.8281 | NaN | NaN | 1253.5575 | NaN | NaN | NaN | NaN | 1253.6888 | 1254.2581 | NaN | 15.4625 | NaN | 23.7932
9903.1292 | 719.8847 | 590.0905 | 341.6404 | 335.2966 | 345.1896 | 472.3047 | 531.4926 | 429.9493 | NaN | NaN | NaN | 652.9482 | 1254.8278 | NaN | NaN | 1253.5572 | NaN | NaN | NaN | NaN | 1253.6885 | 1254.2578 | NaN | 15.932 | NaN | 23.8955
9904.1292 | 719.082 | 589.227 | 341.2435 | 334.9634 | 345.3096 | 470.4512 | 527.7414 | 430.2091 | NaN | NaN | NaN | 645.2975 | 1254.8279 | NaN | NaN | 1253.5573 | NaN | NaN | NaN | NaN | 1253.6887 | 1254.2579 | NaN | 15.4797 | NaN | 23.6147
9905.1292 | 718.6933 | 588.0804 | 341.1354 | 334.7908 | 345.2099 | 468.2825 | 523.779 | 429.4378 | NaN | NaN | NaN | 640.4758 | 1254.827 | NaN | NaN | 1253.5564 | NaN | NaN | NaN | NaN | 1253.6878 | 1254.257 | NaN | 16.864 | NaN | 22.4954
9906.1292 | 718.2422 | 594.8795 | 340.9581 | 334.9813 | 344.9782 | 467.0069 | 520.8495 | 430.3242 | NaN | NaN | NaN | 623.0634 | 1254.8272 | NaN | NaN | 1253.5566 | NaN | NaN | NaN | NaN | 1253.688 | 1254.2573 | NaN | 16.1436 | NaN | 24.1846
9907.1292 | 719.0879 | 596.4785 | 340.7988 | 334.9795 | 345.1247 | 464.3914 | 521.2099 | 430.5131 | NaN | NaN | NaN | 610.6165 | 1254.8267 | NaN | NaN | 1253.5561 | NaN | NaN | NaN | NaN | 1253.6875 | 1254.2567 | NaN | 14.4707 | NaN | 24.3201
9908.1292 | 718.7276 | 600.4251 | 340.9192 | 334.923 | 344.9751 | 464.4168 | 523.3325 | 432.5627 | NaN | NaN | NaN | 612.8817 | 1254.8257 | NaN | NaN | 1253.5551 | NaN | NaN | NaN | NaN | 1253.6865 | 1254.2557 | NaN | 14.8139 | NaN | 23.3053
9909.1292 | 718.837 | 600.1862 | 340.8637 | 334.6678 | 344.9814 | 461.7053 | 526.6687 | 436.654 | NaN | NaN | NaN | 631.668 | 1254.827 | NaN | NaN | 1253.5563 | NaN | NaN | NaN | NaN | 1253.6877 | 1254.257 | NaN | 15.7358 | NaN | 24.9722
9910.1292 | 718.3908 | 600.9984 | 340.9153 | 334.5057 | 344.9789 | 463.2299 | 525.7785 | 437.6642 | NaN | NaN | NaN | 658.4631 | 1254.8249 | NaN | NaN | 1253.5543 | NaN | NaN | NaN | NaN | 1253.6856 | 1254.2549 | NaN | 16.7879 | NaN | 24.5562
9911.1292 | 718.475 | 599.4908 | 340.6032 | 334.6309 | 344.8351 | 465.8491 | 528.7601 | 438.2166 | NaN | NaN | NaN | 658.3716 | 1254.8252 | NaN | NaN | 1253.5545 | NaN | NaN | NaN | NaN | 1253.6859 | 1254.2552 | NaN | 17.1302 | NaN | 23.6274
9912.1292 | 719.6321 | 598.8769 | 340.9652 | 334.6722 | 344.8559 | 467.1615 | 526.6614 | 437.7218 | NaN | NaN | NaN | 696.4338 | 1254.8255 | NaN | NaN | 1253.5548 | NaN | NaN | NaN | NaN | 1253.6862 | 1254.2555 | NaN | 15.7128 | NaN | 24.4752
9913.1292 | 719.9199 | 598.003 | 341.3603 | 335.0559 | 344.8711 | 468.1241 | 525.471 | 438.9167 | NaN | NaN | NaN | 719.1492 | 1254.8246 | NaN | NaN | 1253.554 | NaN | NaN | NaN | NaN | 1253.6853 | 1254.2546 | NaN | 15.3346 | NaN | 25.1977
9914.1292 | 720.1638 | 601.6966 | 341.4779 | 335.458 | 345.733 | 465.6657 | 525.5327 | 438.2266 | NaN | NaN | NaN | 694.9387 | 1254.8245 | NaN | NaN | 1253.5539 | NaN | NaN | NaN | NaN | 1253.6853 | 1254.2545 | NaN | 15.2412 | NaN | 23.8104
9915.1292 | 720.6496 | 603.3993 | 341.7199 | 335.8515 | 345.8936 | 464.5216 | 530.3912 | 440.0602 | NaN | NaN | NaN | 663.0146 | 1254.8246 | NaN | NaN | 1253.554 | NaN | NaN | NaN | NaN | 1253.6853 | 1254.2546 | NaN | 15.4984 | NaN | 25.1692
9916.1292 | 720.8079 | 602.5061 | 341.5545 | 336.3591 | 346.9917 | 466.0815 | 531.6201 | 439.1197 | NaN | NaN | NaN | 634.5069 | 1254.8236 | NaN | NaN | 1253.5529 | NaN | NaN | NaN | NaN | 1253.6843 | 1254.2536 | NaN | 15.7683 | NaN | 23.4131
9917.1292 | 721.4708 | 600.7146 | 341.885 | 336.4186 | 346.9953 | 466.5041 | 529.5016 | 440.3335 | NaN | NaN | NaN | 665.5465 | 1254.8236 | NaN | NaN | 1253.5529 | NaN | NaN | NaN | NaN | 1253.6843 | 1254.2536 | NaN | 15.2229 | NaN | 25.2724
9918.1292 | 720.8944 | 599.9759 | 342.1285 | 336.4765 | 347.0188 | 465.88 | 527.8228 | 438.435 | NaN | NaN | NaN | 671.5567 | 1254.823 | NaN | NaN | 1253.5524 | NaN | NaN | NaN | NaN | 1253.6837 | 1254.253 | NaN | 15.1824 | NaN | 22.4417
9919.1292 | 720.7899 | 599.1982 | 342.4125 | 336.8422 | 347.4122 | 464.6861 | 526.9154 | 436.6231 | NaN | NaN | NaN | 693.2714 | 1254.8228 | NaN | NaN | 1253.5522 | NaN | NaN | NaN | NaN | 1253.6836 | 1254.2528 | NaN | 14.9995 | NaN | 24.6933
9920.1292 | 719.7026 | 599.2978 | 342.1459 | 337.271 | 347.9901 | 466.3778 | 529.1589 | 440.3497 | NaN | NaN | NaN | 703.0841 | 1254.8223 | NaN | NaN | 1253.5517 | NaN | NaN | NaN | NaN | 1253.6831 | 1254.2523 | NaN | 15.7838 | NaN | 24.9546
9921.1292 | 719.5201 | 598.8765 | 342.1323 | 336.9934 | 347.9983 | 464.2132 | 525.1271 | 439.0101 | NaN | NaN | NaN | 682.7513 | 1254.8221 | NaN | NaN | 1253.5514 | NaN | NaN | NaN | NaN | 1253.6828 | 1254.2521 | NaN | 18.7662 | NaN | 24.407
9922.1292 | 719.5748 | 602.5638 | 342.169 | 337.0831 | 347.6141 | 462.9765 | 522.1542 | 436.562 | NaN | NaN | NaN | 691.2403 | 1254.8221 | NaN | NaN | 1253.5515 | NaN | NaN | NaN | NaN | 1253.6829 | 1254.2521 | NaN | 15.2326 | NaN | 23.9137
9923.1292 | 720.2971 | 601.1073 | 341.8176 | 337.2404 | 347.3259 | 463.5267 | 520.253 | 435.2954 | NaN | NaN | NaN | 712.9986 | 1254.8207 | NaN | NaN | 1253.5501 | NaN | NaN | NaN | NaN | 1253.6815 | 1254.2507 | NaN | 15.3178 | NaN | 25.5577
9924.1292 | 721.0963 | 601.0717 | 341.6192 | 337.521 | 347.7073 | 462.7634 | 519.767 | 435.0152 | NaN | NaN | NaN | 714.921 | 1254.8208 | NaN | NaN | 1253.5502 | NaN | NaN | NaN | NaN | 1253.6816 | 1254.2508 | NaN | 15.1704 | NaN | 24.8146
9925.1292 | 721.5783 | 599.4504 | 340.8645 | 337.3122 | 347.6839 | 463.3616 | 523.1157 | 433.4958 | NaN | NaN | NaN | 705.9341 | 1254.8204 | NaN | NaN | 1253.5498 | NaN | NaN | NaN | NaN | 1253.6812 | 1254.2504 | NaN | 15.1446 | NaN | 24.1892
9926.1292 | 721.8233 | 601.7705 | 341.5962 | 337.067 | 347.1953 | 465.0195 | 523.2187 | 435.6158 | NaN | NaN | NaN | 739.5075 | 1254.8209 | NaN | NaN | 1253.5502 | NaN | NaN | NaN | NaN | 1253.6816 | 1254.2509 | NaN | 16.5345 | NaN | 24.6353
9927.1292 | 722.3871 | 601.8393 | 341.2267 | 336.8669 | 347.1196 | 463.6527 | 519.2642 | 435.3535 | NaN | NaN | NaN | 755.9549 | 1254.82 | NaN | NaN | 1253.5494 | NaN | NaN | NaN | NaN | 1253.6808 | 1254.25 | NaN | 15.7027 | NaN | 21.3557
9928.1292 | 723.7787 | 598.8878 | 341.2807 | 336.533 | 346.866 | 462.4413 | 516.7586 | 434.1409 | NaN | NaN | NaN | 757.2902 | 1254.8199 | NaN | NaN | 1253.5493 | NaN | NaN | NaN | NaN | 1253.6807 | 1254.2499 | NaN | 15.535 | NaN | 25.0652
9929.1292 | 722.9504 | 598.478 | 341.116 | 336.5178 | 347.3096 | 461.3188 | 516.2099 | 434.0222 | NaN | NaN | NaN | 750.57 | 1254.8198 | NaN | NaN | 1253.5491 | NaN | NaN | NaN | NaN | 1253.6805 | 1254.2498 | NaN | 18.2143 | NaN | 24.5006
9930.1292 | 722.7796 | 599.0267 | 340.5807 | 336.589 | 347.1538 | 460.8567 | 516.2615 | 434.5166 | NaN | NaN | NaN | 757.5079 | 1254.8182 | NaN | NaN | 1253.5476 | NaN | NaN | NaN | NaN | 1253.679 | 1254.2482 | NaN | 15.9209 | NaN | 25.1843
9931.1292 | 722.9621 | 599.1952 | 341.0413 | 336.6672 | 346.8078 | 463.0078 | 519.8057 | 435.9386 | NaN | NaN | NaN | 770.5056 | 1254.8182 | NaN | NaN | 1253.5475 | NaN | NaN | NaN | NaN | 1253.6789 | 1254.2482 | NaN | 16.1601 | NaN | 23.9662
9932.1292 | 722.7021 | 597.5265 | 341.0945 | 336.8495 | 346.9669 | 463.7881 | 520.118 | 436.9559 | NaN | NaN | NaN | 757.984 | 1254.8186 | NaN | NaN | 1253.548 | NaN | NaN | NaN | NaN | 1253.6793 | 1254.2486 | NaN | 17.1524 | NaN | 21.86
9933.1292 | 721.7311 | 595.3153 | 341.5885 | 336.9952 | 347.2266 | 463.285 | 520.2109 | 435.5152 | NaN | NaN | NaN | 714.1788 | 1254.8175 | NaN | NaN | 1253.5468 | NaN | NaN | NaN | NaN | 1253.6782 | 1254.2475 | NaN | 16.6873 | NaN | 24.4263
9934.1292 | 722.3506 | 595.4854 | 341.7526 | 337.589 | 347.5661 | 462.7979 | 518.4149 | 434.9786 | NaN | NaN | NaN | 701.032 | 1254.8185 | NaN | NaN | 1253.5479 | NaN | NaN | NaN | NaN | 1253.6793 | 1254.2485 | NaN | 17.4461 | NaN | 24.5205
9935.1292 | 722.7989 | 593.4407 | 341.9147 | 337.6634 | 347.5665 | 462.0587 | 515.3472 | 434.3351 | NaN | NaN | NaN | 671.1767 | 1254.8175 | NaN | NaN | 1253.5469 | NaN | NaN | NaN | NaN | 1253.6783 | 1254.2476 | NaN | 18.8209 | NaN | 24.1106
9936.1292 | 722.4679 | 593.0612 | 342.0064 | 337.6654 | 347.4057 | 461.2744 | 515.0203 | 433.2408 | NaN | NaN | NaN | 641.1545 | 1254.8171 | NaN | NaN | 1253.5465 | NaN | NaN | NaN | NaN | 1253.6779 | 1254.2471 | NaN | 17.699 | NaN | 22.8306
9937.1292 | 723.8552 | 594.4234 | 341.9169 | 337.725 | 347.2346 | 460.5568 | 516.6417 | 433.8897 | NaN | NaN | NaN | 616.9184 | 1254.8165 | NaN | NaN | 1253.5458 | NaN | NaN | NaN | NaN | 1253.6772 | 1254.2465 | NaN | 16.7499 | NaN | 23.7843
9938.1292 | 723.9308 | 593.5708 | 341.3116 | 337.62 | 346.9853 | 461.0893 | 521.2411 | 433.7757 | NaN | NaN | NaN | 595.1002 | 1254.8166 | NaN | NaN | 1253.546 | NaN | NaN | NaN | NaN | 1253.6774 | 1254.2466 | NaN | 15.8464 | NaN | 24.9099
9939.1292 | 722.6102 | 592.7566 | 340.961 | 337.5351 | 347.0911 | 460.7436 | 522.7146 | 433.3003 | NaN | NaN | NaN | 585.2628 | 1254.8157 | NaN | NaN | 1253.5451 | NaN | NaN | NaN | NaN | 1253.6764 | 1254.2457 | NaN | 15.9234 | NaN | 22.9358
9940.1292 | 722.2532 | 592.3994 | 341.3925 | 337.4481 | 347.1498 | 461.0957 | 522.4906 | 432.9726 | NaN | NaN | NaN | 595.5834 | 1254.8158 | NaN | NaN | 1253.5452 | NaN | NaN | NaN | NaN | 1253.6766 | 1254.2459 | NaN | 15.6664 | NaN | 25.0875
9941.1292 | 721.7755 | 591.0003 | 341.9112 | 337.5635 | 347.5315 | 460.5684 | 520.4539 | 432.6805 | NaN | NaN | NaN | 613.9596 | 1254.8158 | NaN | NaN | 1253.5452 | NaN | NaN | NaN | NaN | 1253.6766 | 1254.2459 | NaN | 16.0821 | NaN | 23.6189
9942.1292 | 721.1086 | 591.5227 | 341.9122 | 337.3825 | 347.2572 | 459.5244 | 523.3913 | 431.6294 | NaN | NaN | NaN | 647.0872 | 1254.8152 | NaN | NaN | 1253.5446 | NaN | NaN | NaN | NaN | 1253.6759 | 1254.2452 | NaN | 16.3578 | NaN | 24.9863
9943.1292 | 719.8553 | 593.9843 | 342.2077 | 337.3736 | 346.9332 | 459.1934 | 525.2003 | 431.6887 | NaN | NaN | NaN | 666.8047 | 1254.8143 | NaN | NaN | 1253.5437 | NaN | NaN | NaN | NaN | 1253.6751 | 1254.2443 | NaN | 16.3444 | NaN | 24.3512
9944.1292 | 718.1013 | 595.6329 | 342.1605 | 337.1941 | 346.951 | 458.5446 | 527.9886 | 432.8604 | NaN | NaN | NaN | 665.2485 | 1254.8138 | NaN | NaN | 1253.5431 | NaN | NaN | NaN | NaN | 1253.6745 | 1254.2438 | NaN | 15.5659 | NaN | 24.4268
9945.1292 | 716.1882 | 595.5744 | 341.7522 | 336.8422 | 346.7924 | 459.1897 | 526.9479 | 431.7771 | NaN | NaN | NaN | 656.2329 | 1254.8127 | NaN | NaN | 1253.5421 | NaN | NaN | NaN | NaN | 1253.6734 | 1254.2427 | NaN | 14.9843 | NaN | 24.1788
9946.1292 | 715.6375 | 595.4818 | 341.7649 | 336.664 | 346.4279 | 459.5086 | 527.9814 | 431.5112 | NaN | NaN | NaN | 666.3343 | 1254.8134 | NaN | NaN | 1253.5428 | NaN | NaN | NaN | NaN | 1253.6742 | 1254.2434 | NaN | 15.5297 | NaN | 24.4655
9947.1292 | 716.5335 | 595.2062 | 342.1417 | 336.5011 | 346.0232 | 458.1821 | 530.859 | 430.3358 | NaN | NaN | NaN | 686.6196 | 1254.8128 | NaN | NaN | 1253.5421 | NaN | NaN | NaN | NaN | 1253.6735 | 1254.2428 | NaN | 15.2004 | NaN | 22.7224
9948.1292 | 717.6032 | 595.5114 | 341.3857 | 336.5503 | 345.6753 | 458.5899 | 534.6008 | 429.4982 | NaN | NaN | NaN | 676.605 | 1254.8124 | NaN | NaN | 1253.5418 | NaN | NaN | NaN | NaN | 1253.6732 | 1254.2424 | NaN | 15.914 | NaN | 24.7427
9949.1292 | 719.2486 | 594.7606 | 341.5224 | 336.5297 | 347.1261 | 458.7453 | 533.7728 | 429.8722 | NaN | NaN | NaN | 660.5116 | 1254.8118 | NaN | NaN | 1253.5412 | NaN | NaN | NaN | NaN | 1253.6726 | 1254.2418 | NaN | 17.5348 | NaN | 24.0242
9950.1292 | 720.5821 | 594.7898 | 341.5661 | 336.5538 | 346.9198 | 459.4301 | 533.3342 | 429.9657 | NaN | NaN | NaN | 657.3075 | 1254.8114 | NaN | NaN | 1253.5408 | NaN | NaN | NaN | NaN | 1253.6722 | 1254.2414 | NaN | 15.8363 | NaN | 24.1558
9951.1292 | 721.8996 | 594.4669 | 341.3368 | 336.2235 | 346.5905 | 458.5002 | 535.0207 | 429.4814 | NaN | NaN | NaN | 664.6955 | 1254.8114 | NaN | NaN | 1253.5408 | NaN | NaN | NaN | NaN | 1253.6722 | 1254.2414 | NaN | 15.4793 | NaN | 23.8841
9952.1292 | 721.2165 | 593.2433 | 341.5662 | 335.9083 | 346.5761 | 459.415 | 535.3101 | 430.4204 | NaN | NaN | NaN | 692.4931 | 1254.8106 | NaN | NaN | 1253.54 | NaN | NaN | NaN | NaN | 1253.6713 | 1254.2406 | NaN | 16.4537 | NaN | 25.0042
9953.1292 | 720.2471 | 593.8096 | 341.0408 | 335.9421 | 346.7073 | 459.5327 | 532.8764 | 429.6136 | NaN | NaN | NaN | 692.3299 | 1254.8109 | NaN | NaN | 1253.5403 | NaN | NaN | NaN | NaN | 1253.6717 | 1254.2409 | NaN | 18.2588 | NaN | 25.1195
9954.1292 | 719.9521 | 595.0631 | 341.3767 | 336.1891 | 347.0096 | 461.8625 | 532.6063 | 430.0251 | NaN | NaN | NaN | 706.1393 | 1254.8099 | NaN | NaN | 1253.5393 | NaN | NaN | NaN | NaN | 1253.6707 | 1254.2399 | NaN | 16.2167 | NaN | 22.4043
9955.1292 | 720.0466 | 595.0293 | 341.1701 | 336.0916 | 347.0858 | 462.7783 | 530.5343 | 429.4531 | NaN | NaN | NaN | 709.1827 | 1254.8099 | NaN | NaN | 1253.5393 | NaN | NaN | NaN | NaN | 1253.6707 | 1254.2399 | NaN | 16.1539 | NaN | 24.4305
9956.1292 | 719.8048 | 595.3095 | 341.3281 | 336.3289 | 347.0369 | 465.6064 | 532.9283 | 429.6629 | NaN | NaN | NaN | 711.1093 | 1254.8101 | NaN | NaN | 1253.5394 | NaN | NaN | NaN | NaN | 1253.6708 | 1254.2401 | NaN | 15.9993 | NaN | 24.9549
9957.1292 | 722.6343 | 594.7218 | 341.5643 | 336.0195 | 346.9692 | 466.5634 | 531.2695 | 429.4403 | NaN | NaN | NaN | 726.7966 | 1254.8089 | NaN | NaN | 1253.5383 | NaN | NaN | NaN | NaN | 1253.6696 | 1254.2389 | NaN | 15.423 | NaN | 25.0804
9958.1292 | 723.1151 | 594.8506 | 342.0863 | 336.0353 | 346.8405 | 468.2669 | 533.3682 | 430.2137 | NaN | NaN | NaN | 701.5389 | 1254.8082 | NaN | NaN | 1253.5376 | NaN | NaN | NaN | NaN | 1253.669 | 1254.2382 | NaN | 15.6055 | NaN | 22.1044
9959.1292 | 722.7334 | 594.2978 | 341.9522 | 336.0556 | 346.8441 | 467.9722 | 532.1408 | 430.3061 | NaN | NaN | NaN | 709.9633 | 1254.8081 | NaN | NaN | 1253.5375 | NaN | NaN | NaN | NaN | 1253.6689 | 1254.2381 | NaN | 14.3757 | NaN | 23.3143
9960.1292 | 723.0434 | 594.3675 | 342.1335 | 336.5935 | 346.8135 | 471.0671 | 534.0962 | 430.638 | NaN | NaN | NaN | 711.0026 | 1254.8075 | NaN | NaN | 1253.5369 | NaN | NaN | NaN | NaN | 1253.6683 | 1254.2375 | NaN | 14.9744 | NaN | 23.988
9961.1292 | 722.6296 | 593.5525 | 342.3788 | 336.7195 | 347.356 | 470.3234 | 534.3514 | 430.7593 | NaN | NaN | NaN | 726.6473 | 1254.8076 | NaN | NaN | 1253.537 | NaN | NaN | NaN | NaN | 1253.6684 | 1254.2376 | NaN | 15.7283 | NaN | 24.7481
9962.1292 | 722.8694 | 592.4752 | 342.7003 | 336.5467 | 347.3257 | 471.2343 | 532.73 | 431.0157 | NaN | NaN | NaN | 748.4928 | 1254.8077 | NaN | NaN | 1253.537 | NaN | NaN | NaN | NaN | 1253.6684 | 1254.2377 | NaN | 16.1776 | NaN | 24.5781
9963.1292 | 722.0596 | 596.8018 | 343.0527 | 336.5886 | 347.542 | 471.7404 | 537.5837 | 431.1175 | NaN | NaN | NaN | 743.3987 | 1254.8065 | NaN | NaN | 1253.5359 | NaN | NaN | NaN | NaN | 1253.6673 | 1254.2365 | NaN | 17.6877 | NaN | 25.5175
9964.1292 | 720.6504 | 598.3672 | 343.5431 | 337.1275 | 347.8188 | 470.2974 | 539.2971 | 431.5765 | NaN | NaN | NaN | 703.2833 | 1254.8058 | NaN | NaN | 1253.5351 | NaN | NaN | NaN | NaN | 1253.6665 | 1254.2358 | NaN | 15.1696 | NaN | 24.3533
9965.1292 | 719.7445 | 599.6412 | 343.8453 | 337.8188 | 348.5698 | 470.5645 | 540.2447 | 430.9067 | NaN | NaN | NaN | 681.7623 | 1254.8059 | NaN | NaN | 1253.5353 | NaN | NaN | NaN | NaN | 1253.6667 | 1254.2359 | NaN | 15.9887 | NaN | 24.5708
9966.1292 | 720.8337 | 603.0578 | 343.9077 | 338.7192 | 348.7809 | 470.6898 | 540.566 | 430.868 | NaN | NaN | NaN | 686.6086 | 1254.8059 | NaN | NaN | 1253.5353 | NaN | NaN | NaN | NaN | 1253.6666 | 1254.2359 | NaN | 15.2179 | NaN | 21.947
9967.1292 | 722.6873 | 604.2225 | 344.2468 | 339.4056 | 349.0288 | 471.3718 | 541.1872 | 431.8591 | NaN | NaN | NaN | 707.7735 | 1254.8048 | NaN | NaN | 1253.5342 | NaN | NaN | NaN | NaN | 1253.6656 | 1254.2348 | NaN | 15.9572 | NaN | 22.7397
9968.1292 | 723.6936 | 605.9971 | 343.6952 | 339.2685 | 349.0388 | 470.9754 | 540.2258 | 433.1123 | NaN | NaN | NaN | 722.2577 | 1254.8041 | NaN | NaN | 1253.5335 | NaN | NaN | NaN | NaN | 1253.6649 | 1254.2341 | NaN | 16.7668 | NaN | 24.8644
9969.1292 | 724.7168 | 608.0951 | 343.4434 | 339.1148 | 348.8034 | 470.2349 | 540.225 | 433.6012 | NaN | NaN | NaN | 745.7963 | 1254.8048 | NaN | NaN | 1253.5342 | NaN | NaN | NaN | NaN | 1253.6656 | 1254.2348 | NaN | 16.2998 | NaN | 24.136
9970.1292 | 725.2416 | 609.0613 | 343.6386 | 338.7114 | 348.6232 | 470.3026 | 542.0227 | 435.0302 | NaN | NaN | NaN | 754.2114 | 1254.8037 | NaN | NaN | 1253.5331 | NaN | NaN | NaN | NaN | 1253.6644 | 1254.2337 | NaN | 15.5774 | NaN | 22.4208
9971.1292 | 726.2598 | 612.4063 | 343.966 | 338.4817 | 348.5696 | 472.1401 | 541.3878 | 438.0373 | NaN | NaN | NaN | 729.9095 | 1254.803 | NaN | NaN | 1253.5324 | NaN | NaN | NaN | NaN | 1253.6638 | 1254.233 | NaN | 15.0183 | NaN | 22.0371
9972.1292 | 725.3588 | 613.8207 | 344.3833 | 338.486 | 348.3951 | 471.531 | 538.0934 | 438.9779 | NaN | NaN | NaN | 758.466 | 1254.8021 | NaN | NaN | 1253.5315 | NaN | NaN | NaN | NaN | 1253.6629 | 1254.2321 | NaN | 17.4405 | NaN | 25.1866
9973.1292 | 725.2816 | 613.0983 | 344.9371 | 338.9776 | 348.7204 | 470.4083 | 537.2711 | 439.4921 | NaN | NaN | NaN | 761.7938 | 1254.8022 | NaN | NaN | 1253.5316 | NaN | NaN | NaN | NaN | 1253.663 | 1254.2323 | NaN | 15.2751 | NaN | 22.4477
9974.1292 | 724.104 | 613.8507 | 345.3688 | 339.1879 | 349.0238 | 468.6595 | 538.1173 | 439.0162 | NaN | NaN | NaN | 781.9112 | 1254.8016 | NaN | NaN | 1253.5309 | NaN | NaN | NaN | NaN | 1253.6623 | 1254.2316 | NaN | 15.4284 | NaN | 24.1241
9975.1292 | 722.8219 | 611.9151 | 345.1851 | 339.4998 | 348.897 | 468.0662 | 540.7777 | 440.1393 | NaN | NaN | NaN | 767.9784 | 1254.8019 | NaN | NaN | 1253.5313 | NaN | NaN | NaN | NaN | 1253.6627 | 1254.2319 | NaN | 18.7908 | NaN | 24.4309
9976.1292 | 721.9904 | 609.6367 | 345.0194 | 339.7127 | 348.8227 | 470.4857 | 540.7291 | 441.4455 | NaN | NaN | NaN | 772.0156 | 1254.8024 | NaN | NaN | 1253.5317 | NaN | NaN | NaN | NaN | 1253.6631 | 1254.2324 | NaN | 15.158 | NaN | 22.6242
9977.1292 | 720.7928 | 608.9451 | 344.8821 | 339.4788 | 348.8243 | 469.3154 | 539.2428 | 440.4635 | NaN | NaN | NaN | 763.5921 | 1254.8005 | NaN | NaN | 1253.5299 | NaN | NaN | NaN | NaN | 1253.6613 | 1254.2305 | NaN | 15.7268 | NaN | 22.0259
9978.1292 | 719.256 | 607.9493 | 345.1797 | 339.7463 | 348.6901 | 469.1606 | 539.4676 | 440.7321 | NaN | NaN | NaN | 726.5415 | 1254.8009 | NaN | NaN | 1253.5303 | NaN | NaN | NaN | NaN | 1253.6617 | 1254.2309 | NaN | 15.3828 | NaN | 24.1408
9979.1292 | 718.7048 | 607.3486 | 345.089 | 339.7506 | 348.4935 | 469.8529 | 536.9937 | 439.9082 | NaN | NaN | NaN | 702.9886 | 1254.7995 | NaN | NaN | 1253.5289 | NaN | NaN | NaN | NaN | 1253.6603 | 1254.2296 | NaN | 15.6495 | NaN | 22.6067
9980.1292 | 720.3365 | 608.2588 | 344.9431 | 340.3554 | 348.6711 | 471.3464 | 534.5789 | 440.1815 | NaN | NaN | NaN | 718.9301 | 1254.7989 | NaN | NaN | 1253.5283 | NaN | NaN | NaN | NaN | 1253.6596 | 1254.2289 | NaN | 15.9655 | NaN | 25.1977
9981.1292 | 721.3188 | 607.1523 | 344.9907 | 340.5321 | 348.6592 | 472.5889 | 535.5353 | 439.5393 | NaN | NaN | NaN | 684.529 | 1254.7988 | NaN | NaN | 1253.5282 | NaN | NaN | NaN | NaN | 1253.6596 | 1254.2289 | NaN | 16.5137 | NaN | 22.9389
9982.1292 | 721.9752 | 606.6241 | 345.5368 | 341.3942 | 349.0226 | 470.0524 | 533.7489 | 439.508 | NaN | NaN | NaN | 702.9248 | 1254.7988 | NaN | NaN | 1253.5282 | NaN | NaN | NaN | NaN | 1253.6595 | 1254.2288 | NaN | 15.6397 | NaN | 24.0722
9983.1292 | 721.8046 | 606.5674 | 344.8178 | 341.1426 | 348.988 | 468.8818 | 535.7228 | 440.1154 | NaN | NaN | NaN | 720.8533 | 1254.798 | NaN | NaN | 1253.5274 | NaN | NaN | NaN | NaN | 1253.6588 | 1254.228 | NaN | 16.0798 | NaN | 22.1757
9984.1292 | 719.7346 | 610.0397 | 344.2672 | 340.8169 | 348.791 | 467.4869 | 534.6601 | 439.3899 | NaN | NaN | NaN | 708.1247 | 1254.798 | NaN | NaN | 1253.5274 | NaN | NaN | NaN | NaN | 1253.6588 | 1254.228 | NaN | 16.303 | NaN | 24.1867
9985.1292 | 719.6772 | 609.2648 | 344.2356 | 340.7064 | 348.6667 | 466.31 | 537.2527 | 441.0219 | NaN | NaN | NaN | 679.1812 | 1254.797 | NaN | NaN | 1253.5263 | NaN | NaN | NaN | NaN | 1253.6577 | 1254.227 | NaN | 15.6288 | NaN | 23.0671
9986.1292 | 719.3455 | 608.5638 | 344.4468 | 340.4038 | 348.5151 | 466.7172 | 533.5099 | 441.359 | NaN | NaN | NaN | 668.7392 | 1254.7962 | NaN | NaN | 1253.5256 | NaN | NaN | NaN | NaN | 1253.657 | 1254.2262 | NaN | 15.912 | NaN | 22.1715
9987.1292 | 718.7223 | 606.8279 | 344.3643 | 340.3787 | 348.5274 | 466.6154 | 530.47 | 439.6052 | NaN | NaN | NaN | 639.5282 | 1254.7954 | NaN | NaN | 1253.5248 | NaN | NaN | NaN | NaN | 1253.6562 | 1254.2254 | NaN | 14.4714 | NaN | 23.7754
9988.1292 | 718.4256 | 605.1263 | 344.8081 | 340.1911 | 348.8002 | 468.9548 | 528.9403 | 438.9149 | NaN | NaN | NaN | 650.3729 | 1254.7957 | NaN | NaN | 1253.5251 | NaN | NaN | NaN | NaN | 1253.6565 | 1254.2257 | NaN | 15.8049 | NaN | 24.3525
9989.1292 | 717.9731 | 604.401 | 344.4252 | 340.0368 | 348.9616 | 468.2806 | 530.0299 | 438.1147 | NaN | NaN | NaN | 644.9766 | 1254.7949 | NaN | NaN | 1253.5243 | NaN | NaN | NaN | NaN | 1253.6556 | 1254.2249 | NaN | 16.0608 | NaN | 23.0078
9990.1292 | 717.1948 | 605.6899 | 344.5344 | 340.0506 | 348.8237 | 467.3241 | 532.6119 | 437.0444 | NaN | NaN | NaN | 641.8245 | 1254.7953 | NaN | NaN | 1253.5246 | NaN | NaN | NaN | NaN | 1253.656 | 1254.2253 | NaN | 14.9649 | NaN | 24.3138
9991.1292 | 717.0455 | 606.6162 | 344.7452 | 339.9338 | 349.1541 | 468.7585 | 534.3952 | 438.3721 | NaN | NaN | NaN | 656.0064 | 1254.7931 | NaN | NaN | 1253.5224 | NaN | NaN | NaN | NaN | 1253.6538 | 1254.2231 | NaN | 18.261 | NaN | 24.0575
9992.1292 | 715.7647 | 605.69 | 344.9431 | 339.9386 | 349.1094 | 470.4461 | 532.7551 | 438.45 | NaN | NaN | NaN | 635.6309 | 1254.793 | NaN | NaN | 1253.5224 | NaN | NaN | NaN | NaN | 1253.6538 | 1254.223 | NaN | 16.726 | NaN | 23.7255
9993.1292 | 716.3571 | 604.1011 | 345.113 | 339.8327 | 349.0283 | 469.734 | 531.0531 | 436.8955 | NaN | NaN | NaN | 623.4472 | 1254.7927 | NaN | NaN | 1253.5221 | NaN | NaN | NaN | NaN | 1253.6534 | 1254.2227 | NaN | 16.6005 | NaN | 23.8169
9994.1292 | 717.4148 | 602.8604 | 345.3255 | 339.8745 | 349.098 | 469.4886 | 529.3985 | 435.5234 | NaN | NaN | NaN | 640.8398 | 1254.7927 | NaN | NaN | 1253.5221 | NaN | NaN | NaN | NaN | 1253.6535 | 1254.2228 | NaN | 14.2805 | NaN | 22.4741
9995.1292 | 718.0966 | 601.4206 | 345.3633 | 339.8998 | 349.1588 | 467.8717 | 528.0326 | 433.9309 | NaN | NaN | NaN | 653.6315 | 1254.7911 | NaN | NaN | 1253.5205 | NaN | NaN | NaN | NaN | 1253.6519 | 1254.2211 | NaN | 16.3545 | NaN | 22.7787
9996.1292 | 717.9248 | 600.5973 | 345.2988 | 339.9095 | 349.3243 | 467.8815 | 528.2494 | 434.275 | NaN | NaN | NaN | 628.0404 | 1254.791 | NaN | NaN | 1253.5204 | NaN | NaN | NaN | NaN | 1253.6518 | 1254.2211 | NaN | 16.0476 | NaN | 24.7585
9997.1292 | 717.5298 | 599.8621 | 344.9302 | 340.4048 | 349.6173 | 468.1853 | 527.4872 | 433.8892 | NaN | NaN | NaN | 617.4164 | 1254.791 | NaN | NaN | 1253.5204 | NaN | NaN | NaN | NaN | 1253.6517 | 1254.221 | NaN | 17.1728 | NaN | 24.1093
9998.1292 | 718.1483 | 599.3925 | 344.7047 | 340.4749 | 349.6075 | 467.9845 | 525.3772 | 432.2616 | NaN | NaN | NaN | 633.6086 | 1254.7907 | NaN | NaN | 1253.52 | NaN | NaN | NaN | NaN | 1253.6514 | 1254.2207 | NaN | 17.5977 | NaN | 24.611
9999.1292 | 716.9086 | 600.4792 | 344.55 | 340.4003 | 349.2504 | 467.2541 | 524.7857 | 431.0159 | NaN | NaN | NaN | 605.1583 | 1254.7906 | NaN | NaN | 1253.52 | NaN | NaN | NaN | NaN | 1253.6513 | 1254.2206 | NaN | 16.843 | NaN | 24.6709
10000.1292 | 717.754 | 600.0922 | 344.5789 | 340.9927 | 349.2747 | 467.41 | 522.3189 | 430.0846 | NaN | NaN | NaN | 585.1672 | 1254.7893 | NaN | NaN | 1253.5187 | NaN | NaN | NaN | NaN | 1253.65 | 1254.2193 | NaN | 16.6436 | NaN | 22.1547
10001.1292 | 717.4995 | 600.2886 | 344.9199 | 341.1071 | 348.9614 | 467.0192 | 519.7656 | 428.9941 | NaN | NaN | NaN | 617.9143 | 1254.7887 | NaN | NaN | 1253.5181 | NaN | NaN | NaN | NaN | 1253.6494 | 1254.2187 | NaN | 16.7473 | NaN | 24.1706
10002.1292 | 717.6131 | 599.6193 | 344.6119 | 340.9184 | 348.7573 | 465.3174 | 517.4452 | 428.6151 | NaN | NaN | NaN | 651.3607 | 1254.7871 | NaN | NaN | 1253.5165 | NaN | NaN | NaN | NaN | 1253.6478 | 1254.2171 | NaN | 16.0283 | NaN | 22.331
10003.1292 | 717.7345 | 600.1937 | 344.359 | 340.7039 | 348.5216 | 466.7926 | 518.2761 | 429.2584 | NaN | NaN | NaN | 679.83 | 1254.7876 | NaN | NaN | 1253.517 | NaN | NaN | NaN | NaN | 1253.6483 | 1254.2176 | NaN | 16.7466 | NaN | 24.3408
10004.1292 | 719.1641 | 601.1399 | 344.4638 | 340.851 | 348.5928 | 465.2654 | 527.2277 | 430.0946 | NaN | NaN | NaN | 671.6272 | 1254.7856 | NaN | NaN | 1253.515 | NaN | NaN | NaN | NaN | 1253.6464 | 1254.2156 | NaN | 15.6888 | NaN | 24.9711
10005.1292 | 721.4797 | 600.7369 | 343.9042 | 340.8733 | 349.3536 | 465.6932 | 529.6661 | 432.4889 | NaN | NaN | NaN | 664.5015 | 1254.7866 | NaN | NaN | 1253.516 | NaN | NaN | NaN | NaN | 1253.6474 | 1254.2166 | NaN | 16.9335 | NaN | 24.6871
10006.1292 | 720.8702 | 599.3744 | 344.123 | 340.601 | 349.7202 | 466.2574 | 529.6135 | 432.2355 | NaN | NaN | NaN | 660.2728 | 1254.7856 | NaN | NaN | 1253.515 | NaN | NaN | NaN | NaN | 1253.6464 | 1254.2156 | NaN | 16.2094 | NaN | 22.8375
10007.1292 | 720.6981 | 599.0152 | 344.3152 | 340.5788 | 349.8326 | 465.8692 | 530.7772 | 431.9926 | NaN | NaN | NaN | 647.5854 | 1254.7845 | NaN | NaN | 1253.5139 | NaN | NaN | NaN | NaN | 1253.6452 | 1254.2145 | NaN | 16.2586 | NaN | 23.0627
10008.1292 | 719.9536 | 599.0733 | 344.3792 | 340.4285 | 349.9254 | 465.574 | 533.0809 | 431.6932 | NaN | NaN | NaN | 658.7055 | 1254.7843 | NaN | NaN | 1253.5137 | NaN | NaN | NaN | NaN | 1253.645 | 1254.2143 | NaN | 17.414 | NaN | 23.8119
10009.1292 | 718.9913 | 599.6263 | 344.4807 | 340.3176 | 350.0503 | 465.4299 | 530.2114 | 430.3188 | NaN | NaN | NaN | 677.6727 | 1254.7839 | NaN | NaN | 1253.5133 | NaN | NaN | NaN | NaN | 1253.6447 | 1254.2139 | NaN | 16.22 | NaN | 23.4864
10010.1292 | 718.5835 | 600.8768 | 343.7992 | 340.4099 | 350.0967 | 466.798 | 531.5922 | 429.9191 | NaN | NaN | NaN | 694.1938 | 1254.7828 | NaN | NaN | 1253.5122 | NaN | NaN | NaN | NaN | 1253.6436 | 1254.2129 | NaN | 16.434 | NaN | 23.3863
10011.1292 | 718.7318 | 602.3171 | 343.9559 | 340.5544 | 350.2267 | 468.9217 | 528.4438 | 428.9861 | NaN | NaN | NaN | 687.3768 | 1254.7834 | NaN | NaN | 1253.5127 | NaN | NaN | NaN | NaN | 1253.6441 | 1254.2134 | NaN | 16.2578 | NaN | 23.3865
10012.1292 | 719.1263 | 602.4915 | 343.7414 | 340.942 | 350.1537 | 468.7952 | 527.0768 | 429.2091 | NaN | NaN | NaN | 682.4292 | 1254.7816 | NaN | NaN | 1253.511 | NaN | NaN | NaN | NaN | 1253.6424 | 1254.2116 | NaN | 16.5645 | NaN | 22.1126
10013.1292 | 719.006 | 605.1628 | 343.9317 | 341.057 | 350.1475 | 468.5283 | 526.8776 | 429.2315 | NaN | NaN | NaN | 670.661 | 1254.7812 | NaN | NaN | 1253.5106 | NaN | NaN | NaN | NaN | 1253.642 | 1254.2112 | NaN | 16.7486 | NaN | 24.4377
10014.1292 | 717.5629 | 605.3807 | 344.2097 | 340.7712 | 350.0453 | 469.9314 | 527.4198 | 429.2466 | NaN | NaN | NaN | 651.4556 | 1254.7815 | NaN | NaN | 1253.5109 | NaN | NaN | NaN | NaN | 1253.6423 | 1254.2115 | NaN | 17.7399 | NaN | 23.5564
10015.1292 | 717.8818 | 605.6165 | 344.1184 | 340.3936 | 349.7864 | 470.6943 | 526.9373 | 429.2633 | NaN | NaN | NaN | 626.8263 | 1254.781 | NaN | NaN | 1253.5104 | NaN | NaN | NaN | NaN | 1253.6418 | 1254.211 | NaN | 16.9763 | NaN | 22.5868
10016.1292 | 718.023 | 605.0549 | 344.35 | 340.6178 | 349.7265 | 470.9119 | 528.0373 | 428.8032 | NaN | NaN | NaN | 604.7333 | 1254.7791 | NaN | NaN | 1253.5085 | NaN | NaN | NaN | NaN | 1253.6399 | 1254.2092 | NaN | 16.4988 | NaN | 23.1999
10017.1292 | 717.8359 | 605.3164 | 344.4193 | 340.1755 | 350.1253 | 470.8154 | 526.7349 | 427.4413 | NaN | NaN | NaN | 649.0074 | 1254.7792 | NaN | NaN | 1253.5086 | NaN | NaN | NaN | NaN | 1253.64 | 1254.2092 | NaN | 17.758 | NaN | 22.4382
10018.1292 | 719.4857 | 604.9213 | 344.8214 | 340.0494 | 350.1184 | 470.276 | 526.0839 | 427.7615 | NaN | NaN | NaN | 661.4023 | 1254.7789 | NaN | NaN | 1253.5083 | NaN | NaN | NaN | NaN | 1253.6397 | 1254.209 | NaN | 18.261 | NaN | 23.7764
10019.1292 | 721.6586 | 606.9757 | 344.9047 | 339.9717 | 349.8694 | 469.3793 | 524.6319 | 429.7278 | NaN | NaN | NaN | 671.5606 | 1254.7776 | NaN | NaN | 1253.507 | NaN | NaN | NaN | NaN | 1253.6384 | 1254.2076 | NaN | 17.8674 | NaN | 23.2573
10020.1292 | 722.5687 | 607.4397 | 345.0266 | 340.3337 | 350.1688 | 469.7458 | 525.7089 | 431.2054 | NaN | NaN | NaN | 650.5843 | 1254.7771 | NaN | NaN | 1253.5065 | NaN | NaN | NaN | NaN | 1253.6379 | 1254.2071 | NaN | 17.9473 | NaN | 22.5757
10021.1292 | 722.3549 | 606.7086 | 345.4709 | 340.6518 | 350.2079 | 468.6003 | 529.8495 | 431.797 | NaN | NaN | NaN | 629.8926 | 1254.7757 | NaN | NaN | 1253.5051 | NaN | NaN | NaN | NaN | 1253.6365 | 1254.2057 | NaN | 18.4962 | NaN | 23.8984
10022.1292 | 723.8904 | 604.4516 | 345.4994 | 341.1362 | 350.2651 | 467.314 | 534.218 | 431.9232 | NaN | NaN | NaN | 631.4707 | 1254.775 | NaN | NaN | 1253.5044 | NaN | NaN | NaN | NaN | 1253.6357 | 1254.205 | NaN | 18.5676 | NaN | 23.0285
10023.1292 | 724.3789 | 603.6349 | 345.3415 | 341.4552 | 350.0995 | 466.185 | 531.1513 | 433.6679 | NaN | NaN | NaN | 615.8189 | 1254.7749 | NaN | NaN | 1253.5043 | NaN | NaN | NaN | NaN | 1253.6357 | 1254.2049 | NaN | 17.5614 | NaN | 23.8582
10024.1292 | 723.1884 | 602.0214 | 345.5991 | 341.6591 | 350.1521 | 465.008 | 530.2634 | 434.0618 | NaN | NaN | NaN | 661.4543 | 1254.774 | NaN | NaN | 1253.5034 | NaN | NaN | NaN | NaN | 1253.6348 | 1254.2041 | NaN | 18.7354 | NaN | 22.6396
10025.1292 | 723.5112 | 600.5482 | 345.9877 | 341.3925 | 350.2521 | 465.6636 | 528.5584 | 433.6723 | NaN | NaN | NaN | 694.494 | 1254.7731 | NaN | NaN | 1253.5025 | NaN | NaN | NaN | NaN | 1253.6338 | 1254.2031 | NaN | 17.7236 | NaN | 23.6624
10026.1292 | 721.1074 | 600.2908 | 346.5313 | 341.4074 | 350.2865 | 465.8932 | 525.0817 | 433.1894 | NaN | NaN | NaN | 679.0516 | 1254.7726 | NaN | NaN | 1253.502 | NaN | NaN | NaN | NaN | 1253.6334 | 1254.2026 | NaN | 18.5455 | NaN | 24.9374
10027.1292 | 720.6315 | 599.3045 | 346.7535 | 342.1405 | 350.1538 | 463.9675 | 520.7058 | 431.9347 | NaN | NaN | NaN | 676.098 | 1254.7715 | NaN | NaN | 1253.5009 | NaN | NaN | NaN | NaN | 1253.6323 | 1254.2015 | NaN | 19.3982 | NaN | 23.7058
10028.1292 | 718.7305 | 599.2582 | 347.0171 | 341.9729 | 349.7493 | 462.8751 | 517.971 | 430.2576 | NaN | NaN | NaN | 673.6492 | 1254.7714 | NaN | NaN | 1253.5008 | NaN | NaN | NaN | NaN | 1253.6322 | 1254.2014 | NaN | 17.9636 | NaN | 22.6133
10029.1292 | 717.669 | 599.0051 | 346.3559 | 341.5315 | 349.7095 | 462.4585 | 515.7991 | 429.5354 | NaN | NaN | NaN | 667.638 | 1254.7701 | NaN | NaN | 1253.4995 | NaN | NaN | NaN | NaN | 1253.6308 | 1254.2001 | NaN | 18.0554 | NaN | 23.8
10030.1292 | 717.0078 | 597.7855 | 346.2527 | 341.0893 | 349.287 | 461.4715 | 514.9539 | 429.4364 | NaN | NaN | NaN | 673.2789 | 1254.7695 | NaN | NaN | 1253.4989 | NaN | NaN | NaN | NaN | 1253.6303 | 1254.1995 | NaN | 16.1898 | NaN | 21.8238
10031.1292 | 715.2292 | 597.4269 | 346.4146 | 340.6342 | 349.1302 | 460.7978 | 521.1783 | 431.0765 | NaN | NaN | NaN | 701.0772 | 1254.769 | NaN | NaN | 1253.4984 | NaN | NaN | NaN | NaN | 1253.6298 | 1254.199 | NaN | 16.7239 | NaN | 24.4259
10032.1292 | 714.4136 | 598.3423 | 346.1563 | 340.4858 | 348.9397 | 462.3742 | 520.7546 | 429.6154 | NaN | NaN | NaN | 719.5812 | 1254.7691 | NaN | NaN | 1253.4985 | NaN | NaN | NaN | NaN | 1253.6299 | 1254.1991 | NaN | 17.3867 | NaN | 22.5931
10033.1292 | 712.9774 | 602.4582 | 346.6447 | 340.3999 | 348.4649 | 462.4883 | 518.534 | 428.7172 | NaN | NaN | NaN | 696.2109 | 1254.7684 | NaN | NaN | 1253.4978 | NaN | NaN | NaN | NaN | 1253.6291 | 1254.1984 | NaN | 17.6117 | NaN | 22.7697
10034.1292 | 712.8116 | 604.1185 | 346.7166 | 340.5081 | 348.2829 | 461.1355 | 515.8626 | 428.3602 | NaN | NaN | NaN | 681.6891 | 1254.7672 | NaN | NaN | 1253.4966 | NaN | NaN | NaN | NaN | 1253.628 | 1254.1973 | NaN | 18.5362 | NaN | 25.0117
10035.1292 | 712.221 | 602.7403 | 346.7023 | 340.3444 | 347.9088 | 461.5545 | 512.9822 | 426.7974 | NaN | NaN | NaN | 673.4959 | 1254.7657 | NaN | NaN | 1253.4951 | NaN | NaN | NaN | NaN | 1253.6264 | 1254.1957 | NaN | 17.0452 | NaN | 23.4326
10036.1292 | 711.1005 | 603.8383 | 346.5337 | 340.5889 | 347.5839 | 462.7945 | 513.3002 | 426.805 | NaN | NaN | NaN | 673.8788 | 1254.765 | NaN | NaN | 1253.4944 | NaN | NaN | NaN | NaN | 1253.6258 | 1254.1951 | NaN | 17.2173 | NaN | 22.9007
10037.1292 | 709.4218 | 603.8339 | 346.6928 | 340.2006 | 347.3854 | 461.6116 | 514.582 | 426.6206 | NaN | NaN | NaN | 687.26 | 1254.7652 | NaN | NaN | 1253.4946 | NaN | NaN | NaN | NaN | 1253.6259 | 1254.1952 | NaN | 18.9722 | NaN | 21.2411
10038.1292 | 708.312 | 604.6808 | 346.7935 | 340.2641 | 347.1951 | 461.4431 | 514.2966 | 426.7926 | NaN | NaN | NaN | 671.2471 | 1254.7634 | NaN | NaN | 1253.4928 | NaN | NaN | NaN | NaN | 1253.6242 | 1254.1934 | NaN | 16.8412 | NaN | 22.6614
10039.1292 | 708.023 | 603.6841 | 346.6181 | 340.3622 | 347.7553 | 462.7358 | 514.7938 | 427.8113 | NaN | NaN | NaN | 665.2804 | 1254.7643 | NaN | NaN | 1253.4937 | NaN | NaN | NaN | NaN | 1253.6251 | 1254.1944 | NaN | 18.8159 | NaN | 25.7253
10040.1292 | 707.2031 | 602.0745 | 346.3756 | 340.2064 | 347.708 | 460.7681 | 513.8901 | 426.9109 | NaN | NaN | NaN | 689.4429 | 1254.7628 | NaN | NaN | 1253.4922 | NaN | NaN | NaN | NaN | 1253.6236 | 1254.1928 | NaN | 19.6062 | NaN | 24.0607
10041.1292 | 705.9814 | 601.7284 | 346.1426 | 340.0315 | 347.7138 | 461.0941 | 513.355 | 427.6238 | NaN | NaN | NaN | 713.9564 | 1254.7611 | NaN | NaN | 1253.4905 | NaN | NaN | NaN | NaN | 1253.6219 | 1254.1911 | NaN | 19.2626 | NaN | 22.4397
10042.1292 | 706.4876 | 600.9855 | 345.6876 | 339.5035 | 347.8015 | 460.0472 | 516.3667 | 427.5154 | NaN | NaN | NaN | 716.0963 | 1254.7608 | NaN | NaN | 1253.4902 | NaN | NaN | NaN | NaN | 1253.6216 | 1254.1908 | NaN | 19.5012 | NaN | 22.5145
10043.1292 | 705.6362 | 601.7697 | 345.4521 | 339.4359 | 347.7544 | 459.9087 | 516.6639 | 427.4005 | NaN | NaN | NaN | 720.5282 | 1254.7609 | NaN | NaN | 1253.4903 | NaN | NaN | NaN | NaN | 1253.6217 | 1254.1909 | NaN | 19.0107 | NaN | 22.3607
10044.1292 | 705.0434 | 602.1935 | 345.3207 | 339.5644 | 347.9436 | 459.7835 | 517.708 | 427.0548 | NaN | NaN | NaN | 702.2887 | 1254.7603 | NaN | NaN | 1253.4897 | NaN | NaN | NaN | NaN | 1253.6211 | 1254.1903 | NaN | 17.7013 | NaN | 26.282
10045.1292 | 704.5353 | 602.9443 | 345.2641 | 339.5543 | 348.0621 | 461.4724 | 518.5484 | 427.7994 | NaN | NaN | NaN | 717.1829 | 1254.7591 | NaN | NaN | 1253.4885 | NaN | NaN | NaN | NaN | 1253.6199 | 1254.1891 | NaN | 17.9066 | NaN | 21.4445
10046.1292 | 705.385 | 603.4871 | 345.3903 | 339.5947 | 348.0713 | 461.8403 | 516.644 | 427.4361 | NaN | NaN | NaN | 736.7797 | 1254.7575 | NaN | NaN | 1253.487 | NaN | NaN | NaN | NaN | 1253.6183 | 1254.1876 | NaN | 18.2824 | NaN | 25.7257
10047.1292 | 706.6852 | 603.3092 | 344.9609 | 339.9525 | 347.9437 | 461.4026 | 518.6244 | 427.8975 | NaN | NaN | NaN | 699.7672 | 1254.7575 | NaN | NaN | 1253.4869 | NaN | NaN | NaN | NaN | 1253.6183 | 1254.1875 | NaN | 20.0162 | NaN | 23.5484
10048.1292 | 706.1772 | 602.5422 | 345.6199 | 340.0011 | 347.9939 | 462.197 | 518.9413 | 429.2638 | NaN | NaN | NaN | 716.4258 | 1254.7563 | NaN | NaN | 1253.4857 | NaN | NaN | NaN | NaN | 1253.617 | 1254.1863 | NaN | 18.2116 | NaN | 25.298
10049.1292 | 706.1575 | 602.4134 | 345.7771 | 340.0035 | 348.3577 | 460.8423 | 520.3311 | 429.2547 | NaN | NaN | NaN | 698.8414 | 1254.7556 | NaN | NaN | 1253.485 | NaN | NaN | NaN | NaN | 1253.6164 | 1254.1856 | NaN | 19.2282 | NaN | 24.3543
10050.1292 | 705.668 | 603.59 | 345.7242 | 339.827 | 348.0986 | 460.492 | 519.1597 | 429.053 | NaN | NaN | NaN | 696.2385 | 1254.7557 | NaN | NaN | 1253.4851 | NaN | NaN | NaN | NaN | 1253.6165 | 1254.1857 | NaN | 19.6756 | NaN | 25.9169
10051.1292 | 706.4144 | 602.1168 | 345.2485 | 339.7903 | 347.8115 | 460.5118 | 517.1582 | 427.9579 | NaN | NaN | NaN | 712.8598 | 1254.7536 | NaN | NaN | 1253.483 | NaN | NaN | NaN | NaN | 1253.6144 | 1254.1836 | NaN | 19.0116 | NaN | 23.5312
10052.1292 | 706.9945 | 600.0168 | 344.8886 | 339.9174 | 347.9064 | 460.775 | 516.2526 | 427.5192 | NaN | NaN | NaN | 722.2678 | 1254.7527 | NaN | NaN | 1253.4822 | NaN | NaN | NaN | NaN | 1253.6135 | 1254.1828 | NaN | 19.226 | NaN | 21.9629
10053.1292 | 706.8034 | 599.1764 | 344.7213 | 339.8951 | 347.8531 | 461.3433 | 516.443 | 427.1519 | NaN | NaN | NaN | 734.0245 | 1254.7524 | NaN | NaN | 1253.4819 | NaN | NaN | NaN | NaN | 1253.6132 | 1254.1825 | NaN | 19.9431 | NaN | 23.1342
10054.1292 | 706.5805 | 597.4831 | 344.6926 | 340.4218 | 347.9209 | 462.0311 | 517.6812 | 427.5976 | NaN | NaN | NaN | 724.8445 | 1254.7513 | NaN | NaN | 1253.4807 | NaN | NaN | NaN | NaN | 1253.6121 | 1254.1813 | NaN | 19.4609 | NaN | 21.671
10055.1292 | 705.4435 | 596.2174 | 344.5695 | 340.2993 | 347.7732 | 461.2147 | 515.1809 | 427.3104 | NaN | NaN | NaN | 748.6517 | 1254.7501 | NaN | NaN | 1253.4795 | NaN | NaN | NaN | NaN | 1253.6109 | 1254.1801 | NaN | 20.4218 | NaN | 22.0355
10056.1292 | 706.2234 | 596.4014 | 345.249 | 340.4464 | 347.7622 | 461.1771 | 520.6723 | 427.0347 | NaN | NaN | NaN | 736.9529 | 1254.7497 | NaN | NaN | 1253.4791 | NaN | NaN | NaN | NaN | 1253.6105 | 1254.1798 | NaN | 19.1692 | NaN | 21.3976
10057.1292 | 705.2419 | 594.9762 | 345.3163 | 340.4059 | 347.6882 | 461.4449 | 518.3025 | 429.3148 | NaN | NaN | NaN | 714.7975 | 1254.7487 | NaN | NaN | 1253.4781 | NaN | NaN | NaN | NaN | 1253.6095 | 1254.1788 | NaN | 19.2737 | NaN | 21.3993
10058.1292 | 705.1214 | 594.9001 | 344.8354 | 340.1312 | 347.6988 | 461.3343 | 516.2883 | 428.7249 | NaN | NaN | NaN | 725.2795 | 1254.7486 | NaN | NaN | 1253.478 | NaN | NaN | NaN | NaN | 1253.6094 | 1254.1786 | NaN | 19.1043 | NaN | 21.4499
10059.1292 | 704.9698 | 595.2305 | 344.8568 | 340.5672 | 347.8786 | 461.7915 | 516.8226 | 427.3517 | NaN | NaN | NaN | 704.0236 | 1254.7473 | NaN | NaN | 1253.4767 | NaN | NaN | NaN | NaN | 1253.6081 | 1254.1773 | NaN | 19.9575 | NaN | 22.6869
10060.1292 | 706.1345 | 597.1009 | 344.401 | 340.1718 | 347.954 | 462.8592 | 514.4292 | 426.656 | NaN | NaN | NaN | 717.8489 | 1254.7463 | NaN | NaN | 1253.4757 | NaN | NaN | NaN | NaN | 1253.607 | 1254.1763 | NaN | 18.8507 | NaN | 22.7515
10061.1292 | 706.695 | 595.9656 | 344.7224 | 340.1925 | 347.8829 | 462.9254 | 512.9536 | 427.3319 | NaN | NaN | NaN | 692.2278 | 1254.7457 | NaN | NaN | 1253.4751 | NaN | NaN | NaN | NaN | 1253.6065 | 1254.1757 | NaN | 18.5829 | NaN | 24.0532
10062.1292 | 707.7999 | 595.0336 | 344.5638 | 340.17 | 348.4455 | 463.135 | 512.788 | 427.4614 | NaN | NaN | NaN | 660.2313 | 1254.7434 | NaN | NaN | 1253.4728 | NaN | NaN | NaN | NaN | 1253.6042 | 1254.1734 | NaN | 19.2668 | NaN | 21.4768
10063.1292 | 707.5653 | 594.5012 | 345.0622 | 340.3224 | 349.0507 | 465.1472 | 511.0465 | 428.3346 | NaN | NaN | NaN | 674.8429 | 1254.7451 | NaN | NaN | 1253.4746 | NaN | NaN | NaN | NaN | 1253.6059 | 1254.1752 | NaN | 19.8524 | NaN | 21.7681
10064.1448 | 706.474 | 595.9143 | 345.5421 | 340.5724 | 349.3603 | 463.1207 | 511.0893 | 428.1449 | NaN | NaN | NaN | 683.468 | 1254.7438 | NaN | NaN | 1253.4732 | NaN | NaN | NaN | NaN | 1253.6046 | 1254.1738 | NaN | 17.7646 | NaN | 22.0831
10065.1292 | 705.6132 | 598.3751 | 345.5884 | 340.7892 | 349.5626 | 462.3806 | 510.4559 | 427.4219 | NaN | NaN | NaN | 707.2359 | 1254.7428 | NaN | NaN | 1253.4722 | NaN | NaN | NaN | NaN | 1253.6036 | 1254.1728 | NaN | 19.2931 | NaN | 22.1225
10066.1448 | 705.0491 | 601.7219 | 345.7564 | 340.9938 | 349.5161 | 461.0187 | 510.7931 | 428.5539 | NaN | NaN | NaN | 711.8156 | 1254.7411 | NaN | NaN | 1253.4705 | NaN | NaN | NaN | NaN | 1253.6019 | 1254.1711 | NaN | 18.8366 | NaN | 22.1951
10067.1292 | 704.6216 | 605.3868 | 345.2533 | 340.9186 | 349.6272 | 459.3881 | 510.4096 | 428.6801 | NaN | NaN | NaN | 677.4417 | 1254.7413 | NaN | NaN | 1253.4707 | NaN | NaN | NaN | NaN | 1243.0995 | 1254.1713 | NaN | 19.5157 | NaN | 22.1243
10068.1448 | 704.2207 | 606.0502 | 344.5185 | 340.6567 | 349.9377 | 462.654 | 509.9672 | 429.3652 | NaN | NaN | NaN | 657.9323 | 1254.7405 | NaN | NaN | 1253.4699 | NaN | NaN | NaN | NaN | 1230.0698 | 1254.1705 | NaN | 19.2286 | NaN | 21.7806
10069.1292 | 703.8514 | 607.6906 | 343.924 | 340.4746 | 349.4999 | 462.7686 | 509.614 | 427.9912 | NaN | NaN | NaN | 628.9945 | 1254.74 | NaN | NaN | 1253.4694 | NaN | NaN | NaN | NaN | 1212.9399 | 1254.17 | NaN | 14.625 | NaN | 21.4978
10070.1448 | 703.5678 | 609.2531 | 343.936 | 340.6231 | 349.4172 | 466.7582 | 508.6866 | 428.4018 | NaN | NaN | NaN | 607.1334 | 1254.7381 | NaN | NaN | 1253.4675 | NaN | NaN | NaN | NaN | 1198.4315 | 1254.1681 | NaN | 18.6636 | NaN | 22.228
10071.1292 | 703.1243 | 609.0144 | 343.7192 | 340.5781 | 349.426 | 484.4103 | 507.3172 | 428.7953 | NaN | NaN | NaN | 616.1116 | 1254.738 | NaN | NaN | 1253.4674 | NaN | NaN | NaN | NaN | 1186.6666 | 1254.168 | NaN | 19.4427 | NaN | 21.7516
10072.1292 | 703.8948 | 607.7938 | 343.6536 | 340.6214 | 348.9933 | 483.1475 | 505.7189 | 427.7852 | NaN | NaN | NaN | 597.5854 | 1254.7363 | NaN | NaN | 1253.4657 | NaN | NaN | NaN | NaN | 1176.9754 | 1254.1663 | NaN | 18.4814 | NaN | 21.4904
10073.1292 | 703.7683 | 609.1512 | 343.5167 | 340.7579 | 349.3786 | 480.7306 | 505.1665 | 428.1137 | NaN | NaN | NaN | 638.8424 | 1254.7355 | NaN | NaN | 1253.4649 | NaN | NaN | NaN | NaN | 1172.6179 | 1254.1655 | NaN | 19.6228 | NaN | 22.0135
10074.1292 | 702.6795 | 609.3374 | 343.3236 | 340.6904 | 349.6515 | 477.2704 | 506.8715 | 428.3741 | NaN | NaN | NaN | 663.4574 | 1254.7346 | NaN | NaN | 1253.464 | NaN | NaN | NaN | NaN | 1155.7053 | 1254.1646 | NaN | 18.7075 | NaN | 21.8443
10075.1292 | 704.0099 | 610.0861 | 343.237 | 340.6602 | 349.7776 | 473.0101 | 508.423 | 428.0804 | NaN | NaN | NaN | 672.3846 | 1254.734 | NaN | NaN | 1253.4634 | NaN | NaN | NaN | NaN | 1137.9892 | 1254.164 | NaN | 18.8865 | NaN | 22.8961
10076.1292 | 704.7693 | 616.4096 | 343.5769 | 340.4738 | 349.871 | 469.2962 | 508.2641 | 428.5174 | NaN | NaN | NaN | 677.7451 | 1254.7338 | NaN | NaN | 1253.4632 | NaN | NaN | NaN | NaN | 1123.38 | 1254.1638 | NaN | 19.4504 | NaN | 21.6105
10077.1292 | 705.2467 | 617.2478 | 344.0314 | 340.4485 | 349.8682 | 466.7764 | 509.0721 | 429.8551 | NaN | NaN | NaN | 672.6565 | 1254.7327 | NaN | NaN | 1253.4621 | NaN | NaN | NaN | NaN | 1106.6937 | 1254.1627 | NaN | 19.1262 | NaN | 22.2452
10078.1292 | 705.7437 | 616.6413 | 344.0892 | 340.1034 | 350.3215 | 465.4112 | 509.3464 | 430.4841 | NaN | NaN | NaN | 689.1036 | 1254.7318 | NaN | NaN | 1253.4613 | NaN | NaN | NaN | NaN | 1100.9422 | 1254.1619 | NaN | 18.3613 | NaN | 20.9604
10079.1292 | 704.6788 | 616.178 | 344.3854 | 339.9001 | 350.5535 | 463.3582 | 509.988 | 430.6691 | NaN | NaN | NaN | 702.2693 | 1254.7311 | NaN | NaN | 1253.4605 | NaN | NaN | NaN | NaN | 1088.0909 | 1254.1611 | NaN | 19.1099 | NaN | 20.5963
10080.1292 | 704.4721 | 615.0976 | 344.8647 | 339.9975 | 350.9081 | 462.3623 | 508.5183 | 431.1844 | NaN | NaN | NaN | 704.2543 | 1254.7288 | NaN | NaN | 1253.4582 | NaN | NaN | NaN | NaN | 1082.9333 | 1254.1588 | NaN | 19.3987 | NaN | 21.8429
10081.1292 | 704.7459 | 615.0018 | 345.3508 | 340.2002 | 351.7335 | 464.1414 | 508.5874 | 432.7177 | NaN | NaN | NaN | 679.5142 | 1254.728 | NaN | NaN | 1253.4574 | NaN | NaN | NaN | NaN | 1073.8812 | 1254.158 | NaN | 19.3788 | NaN | 22.1906
10082.1292 | 703.566 | 614.688 | 344.9371 | 340.9194 | 351.9661 | 464.9729 | 507.4777 | 432.151 | NaN | NaN | NaN | 654.178 | 1254.7279 | NaN | NaN | 1253.4573 | NaN | NaN | NaN | NaN | 1068.4168 | 1254.1579 | NaN | 16.9892 | NaN | 21.3468
10083.1292 | 703.7349 | 614.0015 | 344.8455 | 341.3141 | 352.3705 | 463.9949 | 505.1721 | 432.4199 | NaN | NaN | NaN | 647.843 | 1254.7271 | NaN | NaN | 1253.4565 | NaN | NaN | NaN | NaN | 1064.6344 | 1254.1571 | NaN | 15.8431 | NaN | 21.8976
10084.1292 | 702.8208 | 612.8019 | 344.5831 | 341.7897 | 352.3214 | 463.5439 | 504.851 | 433.2626 | NaN | NaN | NaN | 649.429 | 1254.7266 | NaN | NaN | 1253.456 | NaN | NaN | NaN | NaN | 1058.9036 | 1254.1566 | NaN | 15.3942 | NaN | 19.8839
10085.1292 | 702.9615 | 613.6572 | 344.5766 | 341.5474 | 352.1128 | 463.1578 | 503.2244 | 434.9524 | NaN | NaN | NaN | 658.5752 | 1254.7246 | NaN | NaN | 1253.454 | NaN | NaN | NaN | NaN | 1049.7729 | 1254.1546 | NaN | 19.3736 | NaN | 21.8248
10086.1292 | 702.0061 | 612.2681 | 343.755 | 341.1602 | 351.8626 | 463.7994 | 511.2519 | 435.6938 | NaN | NaN | NaN | 656.9581 | 1254.7256 | NaN | NaN | 1253.4551 | NaN | NaN | NaN | NaN | 1042.7578 | 1254.1557 | NaN | 17.8773 | NaN | 20.1149
10087.1292 | 704.5049 | 610.0816 | 343.3651 | 341.1038 | 351.9808 | 466.442 | 512.9059 | 436.6736 | NaN | NaN | NaN | 644.9857 | 1254.7225 | NaN | NaN | 1253.452 | NaN | NaN | NaN | NaN | 1036.4841 | 1254.1526 | NaN | 18.5198 | NaN | 22.8389
10088.1292 | 706.5537 | 608.8536 | 343.4143 | 340.9471 | 352.2144 | 467.0848 | 512.5309 | 436.7505 | NaN | NaN | NaN | 639.5525 | 1254.7226 | NaN | NaN | 1253.452 | NaN | NaN | NaN | NaN | 1031.0627 | 1254.1526 | NaN | 18.88 | NaN | 22.1541
10089.1292 | 707.2168 | 607.65 | 342.9367 | 341.1026 | 352.1351 | 467.1691 | 512.1015 | 436.2006 | NaN | NaN | NaN | 673.6455 | 1254.7216 | NaN | NaN | 1253.4511 | NaN | NaN | NaN | NaN | 1019.6588 | 1254.1517 | NaN | 18.1115 | NaN | 24.0017
10090.1292 | 706.6701 | 608.0401 | 343.16 | 341.2188 | 352.0716 | 468.967 | 511.9701 | 436.2622 | NaN | NaN | NaN | 699.1769 | 1254.7201 | NaN | NaN | 1253.4495 | NaN | NaN | NaN | NaN | 1002.1473 | 1254.1501 | NaN | 16.1965 | NaN | 22.7397
10091.1292 | 705.7408 | 611.9681 | 342.8985 | 341.6369 | 352.0585 | 468.0908 | 512.3596 | 437.2254 | NaN | NaN | NaN | 712.547 | 1254.7178 | NaN | NaN | 1253.4472 | NaN | NaN | NaN | NaN | 990.9526 | 1254.1478 | NaN | 18.7192 | NaN | 24.1056
10092.1292 | 705.568 | 614.7691 | 343.3979 | 342.0575 | 352.0574 | 466.3443 | 511.1193 | 437.6713 | NaN | NaN | NaN | 680.4682 | 1254.7186 | NaN | NaN | 1253.448 | NaN | NaN | NaN | NaN | 975.9174 | 1254.1486 | NaN | 18.1327 | NaN | 22.8369
10093.1292 | 706.2749 | 615 | 343.7422 | 342.11 | 351.8981 | 465.0417 | 509.3169 | 437.0645 | NaN | NaN | NaN | 701.3606 | 1254.7173 | NaN | NaN | 1253.4468 | NaN | NaN | NaN | NaN | 965.5817 | 1254.1473 | NaN | 17.9735 | NaN | 23.2429
10094.1292 | 704.9737 | 615.9682 | 344.2712 | 342.0909 | 351.7611 | 464.7902 | 509.012 | 437.1779 | NaN | NaN | NaN | 693.4269 | 1254.7166 | NaN | NaN | 1253.446 | NaN | NaN | NaN | NaN | 951.8949 | 1254.1466 | NaN | 15.8387 | NaN | 24.9004
10095.1292 | 706.0057 | 615.4793 | 344.2918 | 342.0727 | 351.8301 | 464.709 | 508.1407 | 436.821 | NaN | NaN | NaN | 689.1846 | 1254.715 | NaN | NaN | 1253.4445 | NaN | NaN | NaN | NaN | 945.6053 | 1254.1451 | NaN | 16.6116 | NaN | 22.3117
10096.1292 | 705.6119 | 615.0506 | 344.6473 | 342.1764 | 352.5387 | 464.7184 | 507.551 | 435.4782 | NaN | NaN | NaN | 656.0146 | 1254.7147 | NaN | NaN | 1253.4442 | NaN | NaN | NaN | NaN | 931.3659 | 1254.1448 | NaN | 16.6758 | NaN | 21.9797
10097.1292 | 706.1455 | 614.0536 | 344.5815 | 342.0097 | 352.7192 | 464.1083 | 507.6966 | 435.6422 | NaN | NaN | NaN | 629.0312 | 1254.713 | NaN | NaN | 1253.4424 | NaN | NaN | NaN | NaN | 919.0407 | 1254.143 | NaN | 16.5315 | NaN | 22.6981
10098.1292 | 707.2237 | 613.3501 | 344.3703 | 341.982 | 352.4909 | 464.5525 | 506.8625 | 435.389 | NaN | NaN | NaN | 605.7995 | 1254.7113 | NaN | NaN | 1253.4407 | NaN | NaN | NaN | NaN | 907.3907 | 1254.1413 | NaN | 19.6856 | NaN | 22.2433
10099.1292 | 709.1361 | 613.6477 | 343.8392 | 341.836 | 352.1891 | 464.0333 | 507.6681 | 436.0133 | NaN | NaN | NaN | 587.2879 | 1254.7121 | NaN | NaN | 1253.4416 | NaN | NaN | NaN | NaN | 894.1475 | 1254.1422 | NaN | 17.7735 | NaN | 21.4444
10100.1292 | 711.95 | 614.1257 | 344.2224 | 342.1975 | 352.2866 | 465.2624 | 509.3736 | 436.7561 | NaN | NaN | NaN | 571.559 | 1254.7101 | NaN | NaN | 1253.4395 | NaN | NaN | NaN | NaN | 884.1902 | 1254.1401 | NaN | 15.0186 | NaN | 21.2198
10101.1292 | 712.699 | 615.367 | 344.3653 | 342.2776 | 352.9477 | 465.0205 | 512.2975 | 437.03 | NaN | NaN | NaN | 556.2809 | 1254.7092 | NaN | NaN | 1253.4386 | NaN | NaN | NaN | NaN | 873.2267 | 1254.1392 | NaN | 18.3772 | NaN | 22.5236
10102.1292 | 714.0398 | 614.3119 | 344.887 | 343.2996 | 353.2193 | 463.0771 | 513.2176 | 436.2239 | NaN | NaN | NaN | 577.5928 | 1254.7085 | NaN | NaN | 1253.4379 | NaN | NaN | NaN | NaN | 865.0151 | 1254.1385 | NaN | 16.3466 | NaN | 21.9846
10103.1292 | 715.7689 | 612.5062 | 345.2964 | 343.5639 | 353.6076 | 463.4754 | 511.9802 | 436.2079 | NaN | NaN | NaN | 612.0169 | 1254.707 | NaN | NaN | 1253.4364 | NaN | NaN | NaN | NaN | 859.9425 | 1254.137 | NaN | 18.5889 | NaN | 23.2367
10104.1292 | 716.1606 | 611.305 | 345.3846 | 343.3765 | 353.62 | 462.6295 | 511.539 | 434.7534 | NaN | NaN | NaN | 599.1154 | 1254.7063 | NaN | NaN | 1253.4357 | NaN | NaN | NaN | NaN | 849.9193 | 1254.1363 | NaN | 18.2152 | NaN | 22.2876
10105.1292 | 715.6266 | 611.1499 | 345.658 | 343.3209 | 353.5561 | 462.5671 | 511.4527 | 433.349 | NaN | NaN | NaN | 582.1939 | 1254.7047 | NaN | NaN | 1253.4341 | NaN | NaN | NaN | NaN | 839.4061 | 1254.1347 | NaN | 15.7998 | NaN | 23.6618
10106.1292 | 716.8283 | 612.1632 | 345.9317 | 343.6759 | 353.369 | 462.7584 | 509.4949 | 433.6979 | NaN | NaN | NaN | 631.6173 | 1254.705 | NaN | NaN | 1253.4344 | NaN | NaN | NaN | NaN | 835.0727 | 1254.135 | NaN | 16.6371 | NaN | 20.982
10107.1292 | 716.8755 | 610.4369 | 345.9594 | 344.002 | 353.0851 | 462.2659 | 521.821 | 433.5967 | NaN | NaN | NaN | 632.1762 | 1254.703 | NaN | NaN | 1253.4324 | NaN | NaN | NaN | NaN | 827.1951 | 1254.133 | NaN | 17.349 | NaN | 22.3399
10108.1292 | 715.985 | 612.8087 | 347.4431 | 344.1006 | 353.1773 | 459.8034 | 518.884 | 433.7055 | NaN | NaN | NaN | 657.725 | 1254.7021 | NaN | NaN | 1253.4316 | NaN | NaN | NaN | NaN | 819.6219 | 1254.1322 | NaN | 18.967 | NaN | 22.5094
10109.1292 | 715.6711 | 611.1635 | 347.8504 | 343.8567 | 353.119 | 461.4505 | 519.3971 | 433.5908 | NaN | NaN | NaN | 678.049 | 1254.7016 | NaN | NaN | 1253.4311 | NaN | NaN | NaN | NaN | 808.0189 | 1254.1317 | NaN | 18.3822 | NaN | 21.2787
10110.1292 | 714.1968 | 609.1372 | 347.5911 | 344.2571 | 353.0284 | 462.3815 | 519.9337 | 434.9502 | NaN | NaN | NaN | 702.2795 | 1254.7008 | NaN | NaN | 1253.4303 | NaN | NaN | NaN | NaN | 795.0609 | 1254.1309 | NaN | 19.1723 | NaN | 21.6488
10111.1292 | 712.4782 | 609.8206 | 347.6139 | 344.6143 | 353.3191 | 460.7851 | 517.8965 | 435.7143 | NaN | NaN | NaN | 716.527 | 1254.7001 | NaN | NaN | 1253.4295 | NaN | NaN | NaN | NaN | 783.0002 | 1254.1301 | NaN | 17.3779 | NaN | 22.0617
10112.1292 | 711.2081 | 612.3289 | 347.8442 | 345.0189 | 353.3014 | 460.12 | 518.4347 | 436.6006 | NaN | NaN | NaN | 725.1661 | 1254.6989 | NaN | NaN | 1253.4283 | NaN | NaN | NaN | NaN | 770.7406 | 1254.1289 | NaN | 20.0825 | NaN | 22.407
10113.1292 | 710.1027 | 614.2157 | 347.3861 | 344.4372 | 353.0663 | 461.263 | 519.5276 | 437.8047 | NaN | NaN | NaN | 743.1361 | 1254.6969 | NaN | NaN | 1253.4264 | NaN | NaN | NaN | NaN | 754.6211 | 1254.127 | NaN | 18.2385 | NaN | 22.5684
10114.1292 | 708.4027 | 614.2396 | 347.2445 | 343.9698 | 352.9867 | 461.2047 | 520.6595 | 439.5883 | NaN | NaN | NaN | 716.9425 | 1254.696 | NaN | NaN | 1253.4254 | NaN | NaN | NaN | NaN | 745.0688 | 1254.126 | NaN | 18.7815 | NaN | 22.3204
10115.1292 | 707.9531 | 614.9165 | 346.7928 | 344.579 | 352.8423 | 460.0247 | 519.3382 | 440.6289 | NaN | NaN | NaN | 693.3393 | 1254.6958 | NaN | NaN | 1253.4252 | NaN | NaN | NaN | NaN | 736.6139 | 1254.1258 | NaN | 20.128 | NaN | 22.6157
10116.1292 | 707.1975 | 612.7085 | 347.1041 | 344.5765 | 353.1357 | 460.8628 | 521.0474 | 440.6934 | NaN | NaN | NaN | 712.307 | 1254.6931 | NaN | NaN | 1253.4226 | NaN | NaN | NaN | NaN | 731.228 | 1254.1232 | NaN | 15.3818 | NaN | 21.5465
10117.1292 | 707.5411 | 609.9622 | 347.7675 | 344.1931 | 352.9303 | 460.9469 | 522.2866 | 439.6146 | NaN | NaN | NaN | 729.9276 | 1254.6936 | NaN | NaN | 1253.423 | NaN | NaN | NaN | NaN | 718.677 | 1254.1236 | NaN | 18.2391 | NaN | 22.5543
10118.1292 | 707.4141 | 608.7335 | 347.7953 | 344.2282 | 352.6614 | 461.2719 | 520.4658 | 439.6023 | NaN | NaN | NaN | 752.3763 | 1254.6928 | NaN | NaN | 1253.4223 | NaN | NaN | NaN | NaN | 709.0638 | 1254.1229 | NaN | 16.1711 | NaN | 23.7407
10119.1292 | 708.9008 | 609.2602 | 347.4575 | 343.7257 | 352.2439 | 461.0323 | 519.7285 | 438.9905 | NaN | NaN | NaN | 746.5429 | 1254.6909 | NaN | NaN | 1253.4204 | NaN | NaN | NaN | NaN | 698.6829 | 1254.121 | NaN | 18.3541 | NaN | 22.069
10120.1292 | 709.4089 | 608.641 | 346.9834 | 343.625 | 351.8035 | 460.0119 | 517.6759 | 438.6703 | NaN | NaN | NaN | 745.826 | 1254.6896 | NaN | NaN | 1253.4191 | NaN | NaN | NaN | NaN | 690.8596 | 1254.1197 | NaN | 17.798 | NaN | 22.4971
10121.1292 | 709.4289 | 607.1166 | 347.0011 | 343.6324 | 351.8152 | 458.7018 | 517.4253 | 438.5805 | NaN | NaN | NaN | 716.493 | 1254.689 | NaN | NaN | 1253.4184 | NaN | NaN | NaN | NaN | 678.6699 | 1254.119 | NaN | 20.0135 | NaN | 24.346
10122.1292 | 710.0183 | 607.6338 | 347.2365 | 343.895 | 352.4589 | 460.5997 | 516.7268 | 440.3922 | NaN | NaN | NaN | 714.8453 | 1254.6881 | NaN | NaN | 1253.4176 | NaN | NaN | NaN | NaN | 665.6557 | 1254.1181 | NaN | 16.2626 | NaN | 25.0911
10123.1292 | 710.3938 | 609.9561 | 346.873 | 344.1355 | 352.5717 | 459.1109 | 515.1071 | 442.5038 | NaN | NaN | NaN | 744.8377 | 1254.6861 | NaN | NaN | 1253.4156 | NaN | NaN | NaN | NaN | 654.0551 | 1254.1162 | NaN | 19.8081 | NaN | 22.5293
10124.1292 | 711.5445 | 610.0256 | 347.3039 | 344.4985 | 352.5415 | 458.5552 | 514.9548 | 442.5136 | NaN | NaN | NaN | 747.626 | 1254.6863 | NaN | NaN | 1253.4157 | NaN | NaN | NaN | NaN | 643.3896 | 1254.1163 | NaN | 19.2747 | NaN | 22.7422
10125.1292 | 710.1675 | 611.0053 | 347.2376 | 344.2057 | 352.8565 | 457.744 | 515.3689 | 442.4531 | NaN | NaN | NaN | 736.7965 | 1254.6844 | NaN | NaN | 1253.4138 | NaN | NaN | NaN | NaN | 634.0649 | 1254.1144 | NaN | 17.9093 | NaN | 22.443
10126.1292 | 710.1653 | 611.4103 | 346.7001 | 343.8076 | 352.8513 | 458.3461 | 516.9352 | 440.565 | NaN | NaN | NaN | 735.8976 | 1254.6841 | NaN | NaN | 1253.4136 | NaN | NaN | NaN | NaN | 625.6244 | 1254.1142 | NaN | 16.906 | NaN | 21.6546
10127.1292 | 709.1518 | 610.4349 | 346.6558 | 343.8093 | 352.5 | 461.2399 | 516.915 | 440.4941 | NaN | NaN | NaN | 746.1006 | 1254.6824 | NaN | NaN | 1253.4119 | NaN | NaN | NaN | NaN | 615.9986 | 1254.1125 | NaN | 18.4623 | NaN | 24.1601
10128.1292 | 709.175 | 609.9139 | 346.4924 | 343.6602 | 352.6886 | 460.7652 | 518.4437 | 441.5441 | NaN | NaN | NaN | 740.0335 | 1254.6818 | NaN | NaN | 1253.4112 | NaN | NaN | NaN | NaN | 608.0706 | 1254.1118 | NaN | 18.706 | NaN | 24.8651
10129.1292 | 708.467 | 608.3237 | 346.6762 | 343.7851 | 352.8386 | 461.1861 | 516.3818 | 441.9936 | NaN | NaN | NaN | 725.3635 | 1254.6805 | NaN | NaN | 1253.4099 | NaN | NaN | NaN | NaN | 598.6991 | 1254.1105 | NaN | 15.0056 | NaN | 21.4483
10130.1292 | 709.1501 | 607.5912 | 347.0799 | 344.2523 | 353.3711 | 462.0388 | 515.4011 | 442.3108 | NaN | NaN | NaN | 711.1368 | 1254.6802 | NaN | NaN | 1253.4096 | NaN | NaN | NaN | NaN | 589.0508 | 1254.1102 | NaN | 18.2935 | NaN | 22.7733
10131.1292 | 711.9672 | 606.6583 | 346.8293 | 344.464 | 353.5701 | 462.8448 | 515.1425 | 443.5578 | NaN | NaN | NaN | 725.9379 | 1254.6784 | NaN | NaN | 1253.4078 | NaN | NaN | NaN | NaN | 584.7067 | 1254.1084 | NaN | 19.0616 | NaN | 22.5155
10132.1292 | 713.0954 | 605.5167 | 346.4208 | 344.164 | 353.3626 | 462.2949 | 513.8374 | 442.2889 | NaN | NaN | NaN | 690.8035 | 1254.6774 | NaN | NaN | 1253.4069 | NaN | NaN | NaN | NaN | 574.0923 | 1254.1075 | NaN | 14.9579 | NaN | 23.6268
10133.1292 | 712.3967 | 605.2376 | 346.4186 | 344.1782 | 353.9006 | 462.3428 | 513.7912 | 442.8595 | NaN | NaN | NaN | 669.8211 | 1254.6771 | NaN | NaN | 1253.4066 | NaN | NaN | NaN | NaN | 565.4522 | 1254.1072 | NaN | 18.5505 | NaN | 23.9772
10134.1292 | 713.9666 | 604.6736 | 346.6984 | 344.0795 | 354.278 | 462.4458 | 514.0633 | 441.7758 | NaN | NaN | NaN | 665.6547 | 1254.6752 | NaN | NaN | 1253.4047 | NaN | NaN | NaN | NaN | 555.6571 | 1254.1052 | NaN | 18.7555 | NaN | 22.5892
10135.1292 | 714.1542 | 604.6403 | 347.2431 | 344.2417 | 354.2897 | 462.8535 | 514.5576 | 442.4549 | NaN | NaN | NaN | 665.2417 | 1254.6753 | NaN | NaN | 1253.4047 | NaN | NaN | NaN | NaN | 548.3671 | 1254.1053 | NaN | 17.9806 | NaN | 22.3075
10136.1292 | 714.6591 | 604.7729 | 347.727 | 344.6113 | 354.5626 | 461.4356 | 513.3356 | 441.2669 | NaN | NaN | NaN | 638.7528 | 1254.6735 | NaN | NaN | 1253.403 | NaN | NaN | NaN | NaN | 542.6727 | 1254.1035 | NaN | 17.6301 | NaN | 21.6284
10137.1292 | 713.1724 | 605.3126 | 347.8581 | 345.0686 | 355.0569 | 460.1429 | 526.112 | 440.5193 | NaN | NaN | NaN | 618.6096 | 1254.6726 | NaN | NaN | 1253.4021 | NaN | NaN | NaN | NaN | 538.1125 | 1254.1027 | NaN | 19.0513 | NaN | 22.8163
10138.1292 | 712.8925 | 604.8642 | 348.3164 | 345.3009 | 355.3234 | 461.4263 | 528.8894 | 441.1394 | NaN | NaN | NaN | 605.3928 | 1254.6716 | NaN | NaN | 1253.401 | NaN | NaN | NaN | NaN | 533.5883 | 1254.1016 | NaN | 16.7764 | NaN | 25.1814
10139.1292 | 715.1848 | 602.7115 | 348.059 | 345.4644 | 355.3577 | 460.3818 | 526.575 | 441.2303 | NaN | NaN | NaN | 588.0874 | 1254.6699 | NaN | NaN | 1253.3993 | NaN | NaN | NaN | NaN | 531.1985 | 1254.0999 | NaN | 17.0806 | NaN | 25.3619
10140.1292 | 714.6267 | 602.1275 | 347.845 | 345.6003 | 355.4659 | 460.3279 | 526.3179 | 441.9085 | NaN | NaN | NaN | 567.9062 | 1254.6696 | NaN | NaN | 1253.399 | NaN | NaN | NaN | NaN | 524.1259 | 1254.0996 | NaN | 19.4432 | NaN | 23.699
10141.1292 | 717.3769 | 602.0488 | 347.9522 | 345.4655 | 355.794 | 458.8614 | 525.5133 | 443.1979 | NaN | NaN | NaN | 551.3544 | 1254.668 | NaN | NaN | 1253.3974 | NaN | NaN | NaN | NaN | 516.1989 | 1254.098 | NaN | 19.1329 | NaN | 21.6521
10142.1292 | 718.676 | 602.507 | 348.4657 | 345.6721 | 355.8494 | 460.0504 | 526.4351 | 443.8566 | NaN | NaN | NaN | 537.9859 | 1254.6667 | NaN | NaN | 1253.3962 | NaN | NaN | NaN | NaN | 509.021 | 1254.0968 | NaN | 19.2764 | NaN | 21.7494
10143.1292 | 719.7769 | 602.6894 | 348.5212 | 345.9675 | 356.1883 | 459.7692 | 524.4419 | 444.0741 | NaN | NaN | NaN | 539.9949 | 1254.666 | NaN | NaN | 1253.3954 | NaN | NaN | NaN | NaN | 495.9806 | 1254.096 | NaN | 19.4752 | NaN | 22.4624
10144.1292 | 722.5428 | 601.5926 | 348.6147 | 345.716 | 356.6206 | 460.4303 | 523.3618 | 445.6684 | NaN | NaN | NaN | 546.9029 | 1254.6656 | NaN | NaN | 1253.395 | NaN | NaN | NaN | NaN | 488.2459 | 1254.0956 | NaN | 19.3703 | NaN | 24.732
10145.1292 | 723.2973 | 600.955 | 348.9492 | 345.6432 | 356.7575 | 460.4223 | 521.3144 | 447.4547 | NaN | NaN | NaN | 533.8267 | 1254.6638 | NaN | NaN | 1253.3933 | NaN | NaN | NaN | NaN | 481.9476 | 1254.0939 | NaN | 19.3982 | NaN | 24.0533
10146.1292 | 724.3477 | 602.8941 | 348.7078 | 345.6611 | 357.1047 | 459.8386 | 521.0171 | 447.3804 | NaN | NaN | NaN | 522.8574 | 1254.6624 | NaN | NaN | 1253.3919 | NaN | NaN | NaN | NaN | 474.0871 | 1254.0925 | NaN | 19.3383 | NaN | 23.311
10147.1292 | 725.2884 | 603.1522 | 349.4376 | 345.7123 | 357.0806 | 458.4509 | 519.289 | 449.5733 | NaN | NaN | NaN | 510.9585 | 1254.6613 | NaN | NaN | 1253.3908 | NaN | NaN | NaN | NaN | 466.8984 | 1254.0913 | NaN | 18.7141 | NaN | 23.2925
10148.1292 | 725.1805 | 603.4872 | 349.2898 | 346.5164 | 357.0198 | 458.3594 | 519.5774 | 449.95 | NaN | NaN | NaN | 502.0089 | 1254.6604 | NaN | NaN | 1253.3899 | NaN | NaN | NaN | NaN | 460.0835 | 1254.0905 | NaN | 19.1022 | NaN | 22.0441
10149.1292 | 723.9476 | 604.9512 | 349.2514 | 346.6918 | 357.4393 | 456.5557 | 517.484 | 448.6352 | NaN | NaN | NaN | 517.5477 | 1254.6592 | NaN | NaN | 1253.3887 | NaN | NaN | NaN | NaN | 456.8656 | 1254.0893 | NaN | 16.5136 | NaN | 23.385
10150.1292 | 724.2372 | 605.3028 | 349.9787 | 346.7721 | 357.3621 | 457.9435 | 519.6751 | 448.8486 | NaN | NaN | NaN | 569.9307 | 1254.6591 | NaN | NaN | 1253.3885 | NaN | NaN | NaN | NaN | 452.1917 | 1254.0891 | NaN | 17.1116 | NaN | 21.5371
10151.1292 | 724.0697 | 606.3229 | 350.2528 | 346.738 | 357.5013 | 457.3745 | 518.582 | 450.1982 | NaN | NaN | NaN | 616.8628 | 1254.6575 | NaN | NaN | 1253.387 | NaN | NaN | NaN | NaN | 445.5879 | 1254.0876 | NaN | 18.9949 | NaN | 22.2421
10152.1292 | 723.4773 | 607.4324 | 350.3725 | 346.5624 | 357.5389 | 455.4413 | 515.4751 | 450.5444 | NaN | NaN | NaN | 601.4618 | 1254.6567 | NaN | NaN | 1253.3862 | NaN | NaN | NaN | NaN | 434.8513 | 1254.0868 | NaN | 18.955 | NaN | 24.365
10153.1292 | 722.0072 | 608.6255 | 349.9433 | 346.9611 | 357.7868 | 453.5313 | 512.9485 | 450.3019 | NaN | NaN | NaN | 588.5704 | 1254.6559 | NaN | NaN | 1253.3854 | NaN | NaN | NaN | NaN | 425.5611 | 1254.086 | NaN | 19.3995 | NaN | 23.8204
10154.1292 | 722.1621 | 608.5474 | 350.0908 | 347.3544 | 358.9723 | 453.2627 | 513.0032 | 451.4908 | NaN | NaN | NaN | 569.3345 | 1254.6548 | NaN | NaN | 1253.3843 | NaN | NaN | NaN | NaN | 416.9278 | 1254.0849 | NaN | 17.7554 | NaN | 24.6604
10155.1292 | 723.3386 | 608.1952 | 349.9174 | 347.5741 | 359.0958 | 453.0444 | 512.9882 | 453.4138 | NaN | NaN | NaN | 587.2814 | 1254.6533 | NaN | NaN | 1253.3828 | NaN | NaN | NaN | NaN | 413.4665 | 1254.0833 | NaN | 15.4199 | NaN | 22.1124
10156.1292 | 723.3714 | 607.6481 | 349.7943 | 347.5543 | 359.4906 | 452.1175 | 513.4005 | 453.2277 | NaN | NaN | NaN | 574.9032 | 1254.6523 | NaN | NaN | 1253.3817 | NaN | NaN | NaN | NaN | 402.7773 | 1254.0823 | NaN | 18.8325 | NaN | 24.315
10157.1292 | 723.0651 | 606.1279 | 349.6253 | 348.2518 | 359.772 | 452.2511 | 512.731 | 453.0536 | NaN | NaN | NaN | 559.5583 | 1254.6506 | NaN | NaN | 1253.38 | NaN | NaN | NaN | NaN | 389.9613 | 1254.0806 | NaN | 19.1811 | NaN | 23.5195
10158.1292 | 721.9871 | 604.4244 | 349.6149 | 348.3668 | 359.5769 | 451.2377 | 512.3473 | 451.7459 | NaN | NaN | NaN | 592.4212 | 1254.6504 | NaN | NaN | 1253.3798 | NaN | NaN | NaN | NaN | 383.6145 | 1254.0804 | NaN | 15.6164 | NaN | 25.2642
10159.1292 | 722.1857 | 604.5458 | 349.1792 | 348.6104 | 359.9275 | 449.6943 | 512.1822 | 452.6814 | NaN | NaN | NaN | 629.6356 | 1254.6482 | NaN | NaN | 1253.3777 | NaN | NaN | NaN | NaN | 375.9007 | 1254.0783 | NaN | 18.073 | NaN | 24.4723
10160.1292 | 721.7414 | 605.3593 | 349.6883 | 348.4619 | 359.7924 | 448.5533 | 512.1546 | 453.9795 | NaN | NaN | NaN | 646.9643 | 1254.6479 | NaN | NaN | 1253.3773 | NaN | NaN | NaN | NaN | 374.5362 | 1254.0779 | NaN | 18.6929 | NaN | 24.5772
10161.1292 | 722.4053 | 607.003 | 349.2623 | 348.4426 | 360.1924 | 449.1502 | 511.3646 | 456.5325 | NaN | NaN | NaN | 643.1047 | 1254.6453 | NaN | NaN | 1253.3747 | NaN | NaN | NaN | NaN | 373.5402 | 1254.0753 | NaN | 17.5538 | NaN | 21.8753
10162.1292 | 722.3296 | 607.6624 | 348.8264 | 348.4105 | 360.3551 | 447.9989 | 508.5545 | 456.2476 | NaN | NaN | NaN | 615.6059 | 1254.6452 | NaN | NaN | 1253.3747 | NaN | NaN | NaN | NaN | 369.0408 | 1254.0753 | NaN | 16.5747 | NaN | 24.2593
10163.1292 | 722.8365 | 608.2498 | 349.2019 | 348.8885 | 360.6952 | 448.7175 | 507.8732 | 458.347 | NaN | NaN | NaN | 603.6062 | 1254.6438 | NaN | NaN | 1253.3733 | NaN | NaN | NaN | NaN | 359.8096 | 1254.0739 | NaN | 18.394 | NaN | 23.5408
10164.1292 | 720.8058 | 610.1374 | 348.8042 | 348.9584 | 360.8298 | 449.2269 | 507.2597 | 458.4379 | NaN | NaN | NaN | 620.858 | 1254.643 | NaN | NaN | 1253.3725 | NaN | NaN | NaN | NaN | 352.6598 | 1254.0731 | NaN | 14.6008 | NaN | 21.9266
10165.1292 | 719.8822 | 609.5169 | 348.6879 | 349.5049 | 361.8316 | 449.9759 | 509.225 | 458.2927 | NaN | NaN | NaN | 643.8828 | 1254.6414 | NaN | NaN | 1253.3709 | NaN | NaN | NaN | NaN | 340.5456 | 1254.0715 | NaN | 16.5687 | NaN | 25.2308
10166.1292 | 720.2017 | 609.7715 | 348.7176 | 349.7968 | 362.3704 | 450.6811 | 509.9389 | 457.3064 | NaN | NaN | NaN | 658.0528 | 1254.641 | NaN | NaN | 1253.3705 | NaN | NaN | NaN | NaN | 332.4928 | 1254.0711 | NaN | 15.2218 | NaN | 23.1797
10167.1292 | 721.4495 | 608.3548 | 349.3009 | 350.0552 | 362.5078 | 455.3269 | 512.498 | 460.0775 | NaN | NaN | NaN | 667.2774 | 1254.6398 | NaN | NaN | 1253.3693 | NaN | NaN | NaN | NaN | 328.7651 | 1254.0699 | NaN | 18.2921 | NaN | 25.3486
10168.1292 | 721.3572 | 606.2326 | 349.8016 | 350.1086 | 362.679 | 457.5329 | 514.1297 | 463.2699 | NaN | NaN | NaN | 687.2595 | 1254.6386 | NaN | NaN | 1253.3681 | NaN | NaN | NaN | NaN | 329.4277 | 1254.0687 | NaN | 18.5636 | NaN | 23.3278
10169.1292 | 723.2173 | 604.9421 | 349.6096 | 350.1527 | 362.8851 | 458.7121 | 514.4212 | 463.0066 | NaN | NaN | NaN | 688.8332 | 1254.6375 | NaN | NaN | 1253.367 | NaN | NaN | NaN | NaN | 324.5228 | 1254.0676 | NaN | 14.8451 | NaN | 23.6868
10170.1292 | 723.783 | 604.3686 | 349.4922 | 350.612 | 362.7942 | 460.6335 | 516.4083 | 463.4778 | NaN | NaN | NaN | 722.7013 | 1254.638 | NaN | NaN | 1253.3675 | NaN | NaN | NaN | NaN | 317.9042 | 1254.0681 | NaN | 18.2798 | NaN | 23.5406
10171.1292 | 723.2816 | 604.1437 | 350.0018 | 350.9025 | 363.1348 | 459.3981 | 517.7041 | 462.1273 | NaN | NaN | NaN | 725.7431 | 1254.635 | NaN | NaN | 1253.3645 | NaN | NaN | NaN | NaN | 310.6306 | 1254.0651 | NaN | 18.4185 | NaN | 22.7685
10172.1292 | 724.4015 | 603.9566 | 350.1717 | 351.3039 | 363.22 | 459.3161 | 519.7027 | 461.8576 | NaN | NaN | NaN | 736.0821 | 1254.6345 | NaN | NaN | 1253.3639 | NaN | NaN | NaN | NaN | 306.6433 | 1254.0645 | NaN | 15.0015 | NaN | 23.47
10173.1292 | 724.6117 | 603.5763 | 350.2901 | 351.6316 | 363.2712 | 459.9458 | 521.6126 | 462.6512 | NaN | NaN | NaN | 763.7493 | 1254.6329 | NaN | NaN | 1253.3623 | NaN | NaN | NaN | NaN | 301.68 | 1254.0629 | NaN | 20.0095 | NaN | 24.4394
10174.1292 | 724.0482 | 603.3094 | 350.8698 | 351.4639 | 363.4985 | 462.1017 | 522.4983 | 464.2205 | NaN | NaN | NaN | 779.8835 | 1254.6326 | NaN | NaN | 1253.3621 | NaN | NaN | NaN | NaN | 298.5104 | 1254.0627 | NaN | 16.7205 | NaN | 23.8094
10175.1292 | 725.4582 | 603.7676 | 350.8695 | 351.8157 | 363.4818 | 462.8371 | 521.1404 | 464.3565 | NaN | NaN | NaN | 773.8728 | 1254.6323 | NaN | NaN | 1253.3618 | NaN | NaN | NaN | NaN | 295.4644 | 1254.0624 | NaN | 19.2822 | NaN | 23.594
10176.1292 | 728.1889 | 602.6683 | 351.1098 | 351.959 | 363.9206 | 463.092 | 522.6799 | 467.2464 | NaN | NaN | NaN | 796.1275 | 1254.6299 | NaN | NaN | 1253.3594 | NaN | NaN | NaN | NaN | 287.3453 | 1254.0599 | NaN | 18.3804 | NaN | 25.6024
10177.1292 | 730.3548 | 603.2941 | 351.6109 | 352.6757 | 363.9402 | 461.529 | 523.7588 | 467.3434 | NaN | NaN | NaN | 809.5488 | 1254.6286 | NaN | NaN | 1253.3581 | NaN | NaN | NaN | NaN | 278.3799 | 1254.0586 | NaN | 15.966 | NaN | 22.2508
10178.1292 | 732.8989 | 603.4535 | 351.9713 | 353.1814 | 364.1408 | 461.8609 | 526.0173 | 467.824 | NaN | NaN | NaN | 781.9204 | 1254.628 | NaN | NaN | 1253.3575 | NaN | NaN | NaN | NaN | 268.5148 | 1254.0581 | NaN | 18.7639 | NaN | 23.0868
10179.1292 | 735.0056 | 604.1468 | 352.5507 | 353.5413 | 364.6663 | 463.0336 | 527.0995 | 467.113 | NaN | NaN | NaN | 751.1182 | 1254.6269 | NaN | NaN | 1253.3564 | NaN | NaN | NaN | NaN | 254.8442 | 1254.0569 | NaN | 18.6745 | NaN | 22.7772
10180.1292 | 735.3928 | 605.3746 | 353.0584 | 353.5432 | 365.0648 | 463.2767 | 528.1553 | 469.3467 | NaN | NaN | NaN | 764.693 | 1254.6257 | NaN | NaN | 1253.3552 | NaN | NaN | NaN | NaN | 248.5447 | 1254.0558 | NaN | 18.16 | NaN | 25.2743
10181.1292 | 735.8828 | 606.0532 | 353.1137 | 353.4897 | 365.48 | 464.3523 | 530.8896 | 470.1391 | NaN | NaN | NaN | 756.9102 | 1254.6251 | NaN | NaN | 1253.3546 | NaN | NaN | NaN | NaN | 245.5279 | 1254.0552 | NaN | 19.3363 | NaN | 23.6472
10182.1292 | 734.6445 | 605.2533 | 353.5492 | 353.4839 | 365.6144 | 465.8033 | 531.7824 | 468.9265 | NaN | NaN | NaN | 728.0789 | 1254.6231 | NaN | NaN | 1253.3526 | NaN | NaN | NaN | NaN | 241.2537 | 1254.0531 | NaN | 18.2361 | NaN | 22.7807
10183.1292 | 735.784 | 604.7392 | 354.1481 | 353.5763 | 365.7271 | 465.1438 | 530.9707 | 468.3261 | NaN | NaN | NaN | 737.7937 | 1254.6234 | NaN | NaN | 1253.3529 | NaN | NaN | NaN | NaN | 233.3735 | 1254.0535 | NaN | 20.325 | NaN | 24.2949
10184.1292 | 737.1466 | 604.1372 | 354.3003 | 353.9023 | 365.8996 | 466.3296 | 532.9028 | 468.9513 | NaN | NaN | NaN | 759.8921 | 1254.6221 | NaN | NaN | 1253.3516 | NaN | NaN | NaN | NaN | 228.8891 | 1254.0522 | NaN | 19.3605 | NaN | 22.8317
10185.1292 | 738.6752 | 603.4902 | 354.8659 | 354.5595 | 366.3983 | 466.3818 | 535.38 | 469.4077 | NaN | NaN | NaN | 755.0753 | 1254.6204 | NaN | NaN | 1253.3498 | NaN | NaN | NaN | NaN | 223.9844 | 1254.0504 | NaN | 19.4482 | NaN | 23.7955
10186.1292 | 740.9905 | 603.7508 | 355.6457 | 355.7003 | 366.583 | 467.5554 | 537.6985 | 469.8246 | NaN | NaN | NaN | 710.3807 | 1254.6198 | NaN | NaN | 1253.3493 | NaN | NaN | NaN | NaN | 218.8649 | 1254.0499 | NaN | 19.523 | NaN | 23.8598
10187.1292 | 742.5508 | 604.5653 | 355.4529 | 355.7931 | 366.978 | 468.8024 | 539.3035 | 470.1786 | NaN | NaN | NaN | 718.1374 | 1254.6185 | NaN | NaN | 1253.348 | NaN | NaN | NaN | NaN | 221.1219 | 1254.0486 | NaN | 19.4691 | NaN | 23.7844
10188.1292 | 744.3507 | 603.9106 | 355.3097 | 355.6192 | 367.1773 | 468.5568 | 538.9123 | 469.5611 | NaN | NaN | NaN | 712.3755 | 1254.6178 | NaN | NaN | 1253.3473 | NaN | NaN | NaN | NaN | 218.8545 | 1254.0478 | NaN | 19.396 | NaN | 23.2608
10189.1292 | 743.5491 | 603.7901 | 355.7104 | 356.0572 | 367.5891 | 469.5366 | 539.0614 | 470.0139 | NaN | NaN | NaN | 718.4326 | 1254.6162 | NaN | NaN | 1253.3457 | NaN | NaN | NaN | NaN | 218.2922 | 1254.0462 | NaN | 16.259 | NaN | 22.9163
10190.1292 | 742.2189 | 603.1975 | 356.0117 | 355.9485 | 368.1693 | 470.1757 | 539.982 | 471.3421 | NaN | NaN | NaN | 726.4916 | 1254.6153 | NaN | NaN | 1253.3448 | NaN | NaN | NaN | NaN | 213.2982 | 1254.0454 | NaN | 17.9511 | NaN | 22.3103
10191.1292 | 742.8051 | 603.4083 | 356.7663 | 355.8076 | 368.3364 | 470.7069 | 542.1751 | 470.9382 | NaN | NaN | NaN | 711.9992 | 1254.6142 | NaN | NaN | 1253.3437 | NaN | NaN | NaN | NaN | 204.3105 | 1254.0442 | NaN | 17.2872 | NaN | 24.7777
10192.1292 | 741.2355 | 602.9926 | 356.8456 | 356.2505 | 368.5023 | 472.2514 | 542.1055 | 470.6034 | NaN | NaN | NaN | 715.5679 | 1254.6141 | NaN | NaN | 1253.3436 | NaN | NaN | NaN | NaN | 193.0026 | 1254.0441 | NaN | 19.2676 | NaN | 22.0156
10193.1292 | 739.5266 | 602.6716 | 356.9312 | 356.1822 | 368.418 | 471.9089 | 542.3699 | 470.2168 | NaN | NaN | NaN | 713.2114 | 1254.6129 | NaN | NaN | 1253.3424 | NaN | NaN | NaN | NaN | 180.7053 | 1254.043 | NaN | 19.4076 | NaN | 24.6458
10194.1292 | 738.3341 | 602.3554 | 357.4662 | 356.6184 | 369.0449 | 471.6028 | 541.6012 | 471.1591 | NaN | NaN | NaN | 697.8216 | 1254.6113 | NaN | NaN | 1253.3408 | NaN | NaN | NaN | NaN | 174.0044 | 1254.0414 | NaN | 19.7376 | NaN | 24.6242
10195.1292 | 738.8166 | 602.2712 | 357.6739 | 356.6685 | 369.0887 | 471.1138 | 541.2429 | 472.1939 | NaN | NaN | NaN | 670.7265 | 1254.611 | NaN | NaN | 1253.3405 | NaN | NaN | NaN | NaN | 168.264 | 1254.041 | NaN | 19.7333 | NaN | 24.1759
10196.1292 | 738.8886 | 603.6433 | 358.1411 | 356.4621 | 368.9577 | 471.5675 | 540.0307 | 470.8731 | NaN | NaN | NaN | 693.6907 | 1254.6099 | NaN | NaN | 1253.3394 | NaN | NaN | NaN | NaN | 165.1589 | 1254.0399 | NaN | 16.8692 | NaN | 21.8247
10197.1292 | 736.8187 | 604.027 | 357.7823 | 356.7644 | 369.1361 | 470.3357 | 546.2842 | 471.0501 | NaN | NaN | NaN | 685.1127 | 1254.6082 | NaN | NaN | 1253.3377 | NaN | NaN | NaN | NaN | 161.6368 | 1254.0383 | NaN | 18.9064 | NaN | 22.0772
10198.1292 | 736.7393 | 604.6448 | 358.0526 | 357.3767 | 369.9058 | 471.5867 | 545.1979 | 470.4867 | NaN | NaN | NaN | 685.4033 | 1254.6082 | NaN | NaN | 1253.3377 | NaN | NaN | NaN | NaN | 162.0445 | 1254.0383 | NaN | 16.5656 | NaN | 23.6573
10199.1292 | 736.8227 | 605.0215 | 357.9172 | 357.435 | 369.9615 | 473.2284 | 546.7385 | 472.7266 | NaN | NaN | NaN | 713.3952 | 1254.6062 | NaN | NaN | 1253.3357 | NaN | NaN | NaN | NaN | 154.0233 | 1254.0362 | NaN | 19.466 | NaN | 23.8593
10200.1292 | 736.9 | 605.9166 | 358.5121 | 357.1776 | 370.2195 | 474.4504 | 546.9492 | 472.1526 | NaN | NaN | NaN | 687.3428 | 1254.6046 | NaN | NaN | 1253.334 | NaN | NaN | NaN | NaN | 149.3686 | 1254.0346 | NaN | 19.7162 | NaN | 23.9286
10201.1292 | 735.4004 | 606.94 | 359.5474 | 357.6065 | 370.5665 | 476.1908 | 544.5294 | 471.2357 | NaN | NaN | NaN | 674.9974 | 1254.6047 | NaN | NaN | 1253.3342 | NaN | NaN | NaN | NaN | 139.7709 | 1254.0347 | NaN | 17.9198 | NaN | 23.4893
10202.1292 | 733.8761 | 608.8991 | 360.3621 | 358.0334 | 370.8422 | 477.8775 | 541.9449 | 470.3694 | NaN | NaN | NaN | 648.6043 | 1254.6024 | NaN | NaN | 1253.3319 | NaN | NaN | NaN | NaN | 135.1645 | 1254.0325 | NaN | 17.7316 | NaN | 21.9363
10203.1292 | 732.8611 | 610.6141 | 360.0786 | 358.2429 | 370.7629 | 480.0407 | 540.0371 | 468.857 | NaN | NaN | NaN | 623.0624 | 1254.6026 | NaN | NaN | 1253.3321 | NaN | NaN | NaN | NaN | 133.0739 | 1254.0326 | NaN | 18.0795 | NaN | 22.4281
10204.1292 | 731.7965 | 611.3208 | 359.7348 | 358.5418 | 370.7017 | 480.1305 | 537.4344 | 467.9619 | NaN | NaN | NaN | 631.2055 | 1254.6006 | NaN | NaN | 1253.3301 | NaN | NaN | NaN | NaN | 127.0204 | 1254.0307 | NaN | 18.7738 | NaN | 23.8703
10205.1292 | 731.525 | 612.2595 | 360.5613 | 358.9289 | 370.4035 | 481.8419 | 536.3358 | 468.5225 | NaN | NaN | NaN | 677.3501 | 1254.6001 | NaN | NaN | 1253.3296 | NaN | NaN | NaN | NaN | 120.2378 | 1254.0302 | NaN | 18.0258 | NaN | 22.8018
10206.1292 | 730.9065 | 613.6505 | 361.2693 | 359.2164 | 370.4245 | 482.9112 | 540.035 | 470.2242 | NaN | NaN | NaN | 711.45 | 1254.5993 | NaN | NaN | 1253.3288 | NaN | NaN | NaN | NaN | 114.6999 | 1254.0293 | NaN | 15.7447 | NaN | 21.9432
10207.1292 | 730.6358 | 613.5396 | 361.8562 | 359.9992 | 371.0692 | 485.468 | 542.2895 | 471.1881 | NaN | NaN | NaN | 734.147 | 1254.5974 | NaN | NaN | 1253.3269 | NaN | NaN | NaN | NaN | 104.3675 | 1254.0274 | NaN | 19.1616 | NaN | 24.8042
10208.1292 | 731.5665 | 613.1829 | 361.8777 | 360.9631 | 371.1742 | 485.4291 | 543.1979 | 471.4934 | NaN | NaN | NaN | 749.8236 | 1254.5969 | NaN | NaN | 1253.3264 | NaN | NaN | NaN | NaN | 94.6693 | 1254.027 | NaN | 17.1976 | NaN | 22.4991
10209.1292 | 732.2906 | 612.2311 | 361.8374 | 361.2532 | 371.5968 | 486.8449 | 544.891 | 470.3813 | NaN | NaN | NaN | 763.1379 | 1254.595 | NaN | NaN | 1253.3245 | NaN | NaN | NaN | NaN | 89.5224 | 1254.0251 | NaN | 18.779 | NaN | 25.0693
10210.1292 | 733.3829 | 611.1264 | 362.058 | 361.612 | 371.649 | 489.0033 | 544.4627 | 471.3364 | NaN | NaN | NaN | 783.2029 | 1254.5942 | NaN | NaN | 1253.3237 | NaN | NaN | NaN | NaN | 90.4524 | 1254.0242 | NaN | 17.2572 | NaN | 22.4781
10211.1292 | 733.496 | 610.2902 | 362.233 | 361.3169 | 371.961 | 490.278 | 545.469 | 472.9702 | NaN | NaN | NaN | 756.2411 | 1254.5929 | NaN | NaN | 1253.3224 | NaN | NaN | NaN | NaN | 87.4127 | 1254.023 | NaN | 18.2176 | NaN | 24.8998
10212.1292 | 735.2457 | 609.8305 | 362.1509 | 361.5677 | 372.1152 | 491.2919 | 547.094 | 472.8676 | NaN | NaN | NaN | 758.138 | 1254.5931 | NaN | NaN | 1253.3226 | NaN | NaN | NaN | NaN | 84.0413 | 1254.0232 | NaN | 15.3387 | NaN | 20.7797
10213.1292 | 734.8673 | 609.2919 | 362.7633 | 361.6846 | 371.9773 | 490.0722 | 549.8911 | 471.741 | NaN | NaN | NaN | 779.8651 | 1254.5911 | NaN | NaN | 1253.3206 | NaN | NaN | NaN | NaN | 77.7542 | 1254.0211 | NaN | 17.0966 | NaN | 24.9702
10214.1292 | 735.2753 | 608.639 | 362.4974 | 361.9683 | 372.4668 | 491.1207 | 550.2989 | 471.1205 | NaN | NaN | NaN | 780.9025 | 1254.5905 | NaN | NaN | 1253.32 | NaN | NaN | NaN | NaN | 74.8709 | 1254.0205 | NaN | 18.8132 | NaN | 22.8268
10215.1292 | 734.0873 | 608.2473 | 362.7452 | 362.1206 | 372.5028 | 491.6888 | 548.044 | 470.4982 | NaN | NaN | NaN | 760.2817 | 1254.5898 | NaN | NaN | 1253.3193 | NaN | NaN | NaN | NaN | 73.2041 | 1254.0199 | NaN | 17.3342 | NaN | 23.0156
10216.1292 | 733.9098 | 608.7392 | 362.8731 | 362.3144 | 372.5461 | 491.0334 | 547.1807 | 469.989 | NaN | NaN | NaN | 759.6901 | 1254.5874 | NaN | NaN | 1253.3169 | NaN | NaN | NaN | NaN | 71.6186 | 1254.0174 | NaN | 19.0917 | NaN | 21.4447
10217.1292 | 735.5374 | 609.308 | 363.5202 | 362.4852 | 373.1734 | 491.0855 | 548.6482 | 471.3706 | NaN | NaN | NaN | 736.5992 | 1254.5881 | NaN | NaN | 1253.3176 | NaN | NaN | NaN | NaN | 64.8848 | 1254.0182 | NaN | 15.7619 | NaN | 22.3586
10218.1292 | 735.501 | 608.5528 | 363.6006 | 362.7816 | 373.6061 | 491.6308 | 548.8285 | 471.7427 | NaN | NaN | NaN | 704.1835 | 1254.5867 | NaN | NaN | 1253.3162 | NaN | NaN | NaN | NaN | 62.0404 | 1254.0167 | NaN | 17.9192 | NaN | 25.6754
10219.1292 | 735.6685 | 607.5136 | 363.1812 | 362.8782 | 373.518 | 490.0106 | 548.2731 | 470.9454 | NaN | NaN | NaN | 696.9035 | 1254.5856 | NaN | NaN | 1253.3151 | NaN | NaN | NaN | NaN | 56.5418 | 1254.0156 | NaN | 19.8138 | NaN | 24.4382
10220.1292 | 736.5404 | 606.3648 | 362.3869 | 363.0399 | 373.714 | 489.7217 | 550.1874 | 471.7478 | NaN | NaN | NaN | 713.0106 | 1254.5845 | NaN | NaN | 1253.314 | NaN | NaN | NaN | NaN | 53.143 | 1254.0145 | NaN | 17.5552 | NaN | 22.755
10221.1292 | 736.3227 | 606.2092 | 362.4757 | 362.7794 | 373.7287 | 489.7688 | 551.1582 | 473.2138 | NaN | NaN | NaN | 699.2531 | 1254.583 | NaN | NaN | 1253.3125 | NaN | NaN | NaN | NaN | 49.0495 | 1254.0131 | NaN | 18.0598 | NaN | 23.5965
10222.1292 | 735.717 | 607.3903 | 362.39 | 362.712 | 373.7913 | 494.0385 | 556.9913 | 474.8394 | NaN | NaN | NaN | 704.1567 | 1254.5825 | NaN | NaN | 1253.312 | NaN | NaN | NaN | NaN | 41.811 | 1254.0126 | NaN | 15.6114 | NaN | 22.0594
10223.1292 | 736.1164 | 608.1135 | 362.7483 | 362.308 | 373.8875 | 492.4732 | 556.1785 | 474.0432 | NaN | NaN | NaN | 677.0979 | 1254.5809 | NaN | NaN | 1253.3104 | NaN | NaN | NaN | NaN | 32.3633 | 1254.0109 | NaN | 17.2288 | NaN | 22.298
10224.1292 | 736.4274 | 608.6337 | 362.6297 | 362.4412 | 374.0932 | 492.8403 | 556.4859 | 474.5658 | NaN | NaN | NaN | 651.8069 | 1254.5807 | NaN | NaN | 1253.3102 | NaN | NaN | NaN | NaN | 22.9704 | 1254.0107 | NaN | 18.842 | NaN | 24.5164
10225.1292 | 736.438 | 608.5296 | 363.7206 | 362.47 | 373.9641 | 495.1279 | 558.0126 | 475.3858 | NaN | NaN | NaN | 632.7959 | 1254.5796 | NaN | NaN | 1253.3091 | NaN | NaN | NaN | NaN | 13.7476 | 1254.0097 | NaN | 17.9716 | NaN | 24.6581
10226.1292 | 734.1182 | 607.5552 | 363.8106 | 362.6815 | 374.1651 | 494.4231 | 556.5803 | 473.9608 | NaN | NaN | NaN | 646.1888 | 1254.5774 | NaN | NaN | 1253.3069 | NaN | NaN | NaN | NaN | 7.1057 | 1254.0075 | NaN | 18.6384 | NaN | 23.7121
10227.1292 | 733.2564 | 606.7345 | 363.881 | 362.8492 | 374.2023 | 492.9243 | 556.3794 | 472.5045 | NaN | NaN | NaN | 638.5222 | 1254.5774 | NaN | NaN | 1253.3069 | NaN | NaN | NaN | NaN | 1.2784 | 1254.0075 | NaN | 18.7266 | NaN | 24.969
10228.1292 | 733.1702 | 606.3287 | 364.0291 | 362.692 | 374.2502 | 493.156 | 565.7181 | 472.2111 | NaN | NaN | NaN | 626.1342 | 1254.5759 | NaN | NaN | 1253.3054 | NaN | NaN | NaN | NaN | -4.212 | 1254.006 | NaN | 17.9358 | NaN | 24.0905
10229.1292 | 734.3842 | 606.1587 | 363.7623 | 362.7548 | 374.3613 | 494.9797 | 568.0672 | 472.8054 | NaN | NaN | NaN | 640.2313 | 1254.5744 | NaN | NaN | 1253.3039 | NaN | NaN | NaN | NaN | -5.1397 | 1254.0044 | NaN | 18.1015 | NaN | 23.5862
10230.1292 | 737.4727 | 606.3515 | 364.0543 | 362.7702 | 374.2191 | 495.3558 | 567.2558 | 474.3618 | NaN | NaN | NaN | 637.8366 | 1254.5748 | NaN | NaN | 1253.3043 | NaN | NaN | NaN | NaN | -6.9798 | 1254.0049 | NaN | 13.6294 | NaN | 24.4911
10231.1292 | 737.8694 | 606.6366 | 364.4035 | 362.6371 | 374.6914 | 496.9318 | 569.7377 | 476.323 | NaN | NaN | NaN | 659.8616 | 1254.5733 | NaN | NaN | 1253.3028 | NaN | NaN | NaN | NaN | -7.9139 | 1254.0034 | NaN | 16.3158 | NaN | 22.8114
10232.1292 | 736.9294 | 605.4599 | 364.1346 | 363.2421 | 374.7971 | 497.7579 | 568.7764 | 477.4844 | NaN | NaN | NaN | 677.4412 | 1254.572 | NaN | NaN | 1253.3015 | NaN | NaN | NaN | NaN | -14.1203 | 1254.0021 | NaN | 14.6449 | NaN | 24.6901
10233.1292 | 735.0294 | 607.0575 | 363.9247 | 363.3921 | 374.8019 | 496.0698 | 566.4619 | 477.8136 | NaN | NaN | NaN | 717.7413 | 1254.5712 | NaN | NaN | 1253.3007 | NaN | NaN | NaN | NaN | -17.6155 | 1254.0012 | NaN | 17.953 | NaN | 23.4675
10234.1292 | 734.5776 | 608.381 | 364.2238 | 363.163 | 374.7001 | 494.5387 | 562.6584 | 477.6869 | NaN | NaN | NaN | 743.0364 | 1254.5692 | NaN | NaN | 1253.2987 | NaN | NaN | NaN | NaN | NaN | 1253.9992 | NaN | 18.5059 | NaN | 23.8531
10235.1292 | 731.9473 | 609.5213 | 364.2663 | 363.2144 | 374.5259 | 501.5197 | 566.219 | 478.4981 | NaN | NaN | NaN | 717.9936 | 1254.569 | NaN | NaN | 1253.2985 | NaN | NaN | NaN | NaN | NaN | 1253.999 | NaN | 15.351 | NaN | 24.7539
10236.1292 | 731.016 | 608.9637 | 364.1012 | 362.6764 | 374.1371 | 498.8572 | 563.8244 | 476.5223 | NaN | NaN | NaN | 718.831 | 1254.5674 | NaN | NaN | 1253.2969 | NaN | NaN | NaN | NaN | -18.1221 | 1253.9975 | NaN | 19.1058 | NaN | 24.8909
10237.1292 | 730.126 | 609.1099 | 363.7383 | 363.4987 | 374.038 | 499.0361 | 564.6605 | 477.6175 | NaN | NaN | NaN | 718.9086 | 1254.567 | NaN | NaN | 1253.2965 | NaN | NaN | NaN | NaN | -19.8244 | 1253.9971 | NaN | 17.058 | NaN | 24.2956
10238.1292 | 727.2654 | 606.9368 | 363.1515 | 363.2369 | 374.0784 | 498.1965 | 562.6167 | 478.0942 | NaN | NaN | NaN | 735.3628 | 1254.5653 | NaN | NaN | 1253.2949 | NaN | NaN | NaN | NaN | NaN | 1253.9954 | NaN | 15.8636 | NaN | 22.4521
10239.1292 | 727.2482 | 606.7053 | 363.2133 | 363.4932 | 373.8998 | 496.4109 | 566.2603 | 478.711 | NaN | NaN | NaN | 736.1331 | 1254.5651 | NaN | NaN | 1253.2946 | NaN | NaN | NaN | NaN | NaN | 1253.9951 | NaN | 18.1786 | NaN | 23.8469
10240.1292 | 727.4478 | 607.3453 | 363.2707 | 362.9933 | 373.7065 | 501.7447 | 574.536 | 478.0568 | NaN | NaN | NaN | 743.2488 | 1254.5636 | NaN | NaN | 1253.2931 | NaN | NaN | NaN | NaN | NaN | 1253.9937 | NaN | 16.2084 | NaN | 24.5306
10241.1292 | 727.7706 | 608.8098 | 363.0718 | 363.0321 | 374.3811 | 505.0614 | 582.1167 | 480.2863 | NaN | NaN | NaN | 751.594 | 1254.5627 | NaN | NaN | 1253.2922 | NaN | NaN | NaN | NaN | NaN | 1253.9928 | NaN | 18.6113 | NaN | 22.2774
10242.1292 | 727.7137 | 610.165 | 363.16 | 363.3733 | 374.7022 | 507.6978 | 587.7657 | 479.9827 | NaN | NaN | NaN | 758.9513 | 1254.562 | NaN | NaN | 1253.2915 | NaN | NaN | NaN | NaN | NaN | 1253.9921 | NaN | 19.5298 | NaN | 23.5902
10243.1292 | 729.0776 | 610.9203 | 363.7275 | 363.8529 | 374.9849 | 507.5143 | 587.8153 | 480.5211 | NaN | NaN | NaN | 764.5288 | 1254.5599 | NaN | NaN | 1253.2894 | NaN | NaN | NaN | NaN | NaN | 1253.9899 | NaN | 17.1078 | NaN | 23.6833
10244.1292 | 729.8463 | 610.086 | 363.4344 | 364.4832 | 375.0943 | 507.5069 | 589.1589 | 498.0277 | NaN | NaN | NaN | 775.7563 | 1254.5609 | NaN | NaN | 1253.2904 | NaN | NaN | NaN | NaN | NaN | 1253.991 | NaN | 18.2457 | NaN | 23.0702
10245.1292 | 730.5017 | 611.472 | 364.1813 | 364.5797 | 374.6444 | 508.4546 | 593.9038 | 499.0294 | NaN | NaN | NaN | 745.3829 | 1254.559 | NaN | NaN | 1253.2886 | NaN | NaN | NaN | NaN | NaN | 1253.9891 | NaN | 18.3814 | NaN | 24.1151
10246.1292 | 731.6792 | 609.457 | 364.591 | 364.5978 | 374.3516 | 508.527 | 598.3339 | 501.1472 | NaN | NaN | NaN | 734.7042 | 1254.5579 | NaN | NaN | 1253.2874 | NaN | NaN | NaN | NaN | NaN | 1253.988 | NaN | 18.7042 | NaN | 22.2999
10247.1292 | 731.5428 | 608.2658 | 364.9913 | 365.0441 | 374.5938 | 513.4415 | 599.2656 | 507.0512 | NaN | NaN | NaN | 740.7602 | 1254.5562 | NaN | NaN | 1253.2857 | NaN | NaN | NaN | NaN | NaN | 1253.9863 | NaN | 18.7742 | NaN | 23.873
10248.1292 | 729.5952 | 607.2082 | 364.9622 | 365.5691 | 375.7779 | 513.186 | 611.3321 | 505.9985 | NaN | NaN | NaN | 768.9519 | 1254.5559 | NaN | NaN | 1253.2854 | NaN | NaN | NaN | NaN | NaN | 1253.986 | NaN | 16.3172 | NaN | 24.4443
10249.1292 | 728.8161 | 609.1516 | 364.7586 | 365.8185 | 375.7682 | 511.8457 | 610.6609 | 507.501 | NaN | NaN | NaN | 779.1078 | 1254.556 | NaN | NaN | 1253.2855 | NaN | NaN | NaN | NaN | NaN | 1253.9861 | NaN | 15.6759 | NaN | 22.8936
10250.1292 | 727.1048 | 609.6738 | 364.7484 | 365.3854 | 376.1636 | 513.1455 | 612.6296 | 517.7216 | NaN | NaN | NaN | 778.2302 | 1254.553 | NaN | NaN | 1253.2825 | NaN | NaN | NaN | NaN | NaN | 1253.9831 | NaN | 17.1034 | NaN | 23.7433
10251.1292 | 726.3795 | 610.2474 | 364.4669 | 365.2071 | 376.3119 | 512.747 | 607.3596 | 516.1755 | NaN | NaN | NaN | 796.0713 | 1254.5532 | NaN | NaN | 1253.2827 | NaN | NaN | NaN | NaN | NaN | 1253.9833 | NaN | 17.9327 | NaN | 23.8309
10252.1292 | 728.1339 | 611.6102 | 364.4949 | 365.018 | 376.3365 | 514.0618 | 602.3998 | 517.1474 | NaN | NaN | NaN | 799.0994 | 1254.5515 | NaN | NaN | 1253.281 | NaN | NaN | NaN | NaN | -19.9453 | 1253.9815 | NaN | 17.1631 | NaN | 22.838
10253.1292 | 728.4728 | 611.7058 | 364.3238 | 365.2448 | 376.4895 | 514.3421 | 598.1141 | 523.0054 | NaN | NaN | NaN | 776.8851 | 1254.55 | NaN | NaN | 1253.2795 | NaN | NaN | NaN | NaN | 2.7675 | 1253.9801 | NaN | 18.4698 | NaN | 21.9818
10254.1292 | 731.0942 | 611.7044 | 364.7168 | 365.9718 | 377.0092 | 513.5294 | 595.6519 | 520.3067 | NaN | NaN | NaN | 794.0288 | 1254.5503 | NaN | NaN | 1253.2798 | NaN | NaN | NaN | NaN | 21.5015 | 1253.9804 | NaN | 16.6982 | NaN | 22.6123
10255.1292 | 731.8519 | 611.4094 | 365.5776 | 366.2231 | 377.274 | 517.0581 | 600.0311 | 522.3587 | NaN | NaN | NaN | 804.4355 | 1254.5491 | NaN | NaN | 1253.2786 | NaN | NaN | NaN | NaN | 49.2182 | 1253.9792 | NaN | 17.9785 | NaN | 22.7916
10256.1292 | 731.7703 | 610.7847 | 365.0244 | 366.0321 | 377.7365 | 515.3593 | 595.9238 | 520.4112 | NaN | NaN | NaN | 812.7617 | 1254.5484 | NaN | NaN | 1253.2779 | NaN | NaN | NaN | NaN | 106.8914 | 1253.9784 | NaN | 17.1111 | NaN | 23.1438
10257.1292 | 731.2766 | 609.8652 | 365.2039 | 365.9146 | 377.4628 | 514.8906 | 607.4137 | 519.3853 | NaN | NaN | NaN | 809.2207 | 1254.5471 | NaN | NaN | 1253.2766 | NaN | NaN | NaN | NaN | 101.4635 | 1253.9772 | NaN | 18.0307 | NaN | 24.6289
10258.1292 | 731.508 | 609.9367 | 365.5368 | 366.1701 | 377.804 | 514.0217 | 607.0599 | 527.0386 | NaN | NaN | NaN | 793.6259 | 1254.5454 | NaN | NaN | 1253.2749 | NaN | NaN | NaN | NaN | 164.9499 | 1253.9754 | NaN | 16.7445 | NaN | 24.7099
10259.1292 | 732.3016 | 609.3623 | 366.0892 | 366.1246 | 378.1985 | 513.3435 | 599.384 | 525.5762 | NaN | NaN | NaN | 789.2607 | 1254.545 | NaN | NaN | 1253.2745 | NaN | NaN | NaN | NaN | 176.8703 | 1253.9751 | NaN | 15.155 | NaN | 22.0448
10260.1292 | 733.7579 | 610.0334 | 366.7694 | 365.7484 | 377.9875 | 515.4653 | 600.1609 | 522.8234 | NaN | NaN | NaN | 772.8767 | 1254.5435 | NaN | NaN | 1253.273 | NaN | NaN | NaN | NaN | 185.368 | 1253.9736 | NaN | 18.6057 | NaN | 22.7467
10261.1292 | 733.1823 | 609.4786 | 367.7674 | 366.7262 | 378.0646 | 516.2127 | 595.6607 | 518.9291 | NaN | NaN | NaN | 728.0068 | 1254.5429 | NaN | NaN | 1253.2725 | NaN | NaN | NaN | NaN | 285.0082 | 1253.973 | NaN | 17.572 | NaN | 24.5605
10262.1292 | 733.5376 | 609.0086 | 368.7657 | 367.6943 | 378.2867 | 515.5307 | 591.9009 | 516.4814 | NaN | NaN | NaN | 712.2259 | 1254.5426 | NaN | NaN | 1253.2721 | NaN | NaN | NaN | NaN | 308.076 | 1253.9726 | NaN | 18.6348 | NaN | 23.1569
10263.1292 | 734.1658 | 608.1479 | 368.4529 | 367.9446 | 378.5692 | 516.0225 | 588.8201 | 514.445 | NaN | NaN | NaN | 692.521 | 1254.5414 | NaN | NaN | 1253.271 | NaN | NaN | NaN | NaN | 393.3291 | 1253.9715 | NaN | 17.6786 | NaN | 23.291
10264.1292 | 734.0285 | 608.6278 | 368.5426 | 367.7994 | 378.621 | 515.7159 | 593.2302 | 515.1609 | NaN | NaN | NaN | 685.7741 | 1254.5402 | NaN | NaN | 1253.2697 | NaN | NaN | NaN | NaN | 432.0649 | 1253.9703 | NaN | 15.362 | NaN | 23.0985
10265.1292 | 734.4257 | 608.2957 | 368.5951 | 367.7978 | 378.626 | 517.5928 | 593.8315 | 514.0165 | NaN | NaN | NaN | 701.6926 | 1254.5402 | NaN | NaN | 1253.2697 | NaN | NaN | NaN | NaN | 476.5018 | 1253.9703 | NaN | 18.426 | NaN | 22.9849
10266.1292 | 735.335 | 607.708 | 369.5348 | 367.6841 | 378.3464 | 517.3102 | 610.7907 | 512.107 | NaN | NaN | NaN | 697.2801 | 1254.5389 | NaN | NaN | 1253.2684 | NaN | NaN | NaN | NaN | 550.2675 | 1253.969 | NaN | 17.9226 | NaN | 24.4088
10267.1292 | 735.0703 | 607.3077 | 369.4477 | 367.9906 | 378.4712 | 518.1324 | 621.8541 | 507.6051 | NaN | NaN | NaN | 706.6771 | 1254.5368 | NaN | NaN | 1253.2663 | NaN | NaN | NaN | NaN | 617.6305 | 1253.9668 | NaN | 18.4267 | NaN | 23.1894
10268.1292 | 734.8458 | 607.8056 | 369.2189 | 368.1384 | 378.3435 | 519.2678 | 622.3042 | 510.9625 | NaN | NaN | NaN | 709.5677 | 1254.5363 | NaN | NaN | 1253.2658 | NaN | NaN | NaN | NaN | 792.7187 | 1253.9663 | NaN | 17.4195 | NaN | 23.4257
10269.1292 | 735.8346 | 607.8203 | 369.5901 | 368.5982 | 378.7821 | 521.109 | 625.4622 | 518.85 | NaN | NaN | NaN | 706.3843 | 1254.5347 | NaN | NaN | 1253.2642 | NaN | NaN | NaN | NaN | 915.6034 | 1253.9648 | NaN | 19.0926 | NaN | 23.6914
10270.1292 | 736.0354 | 608.2664 | 369.4998 | 369.1855 | 378.7983 | 521.6814 | 619.614 | 522.1948 | NaN | NaN | NaN | 718.9716 | 1254.5337 | NaN | NaN | 1253.2632 | NaN | NaN | NaN | NaN | 961.3928 | 1253.9638 | NaN | 15.8461 | NaN | 21.3151
10271.1292 | 736.9903 | 607.8229 | 369.4745 | 369.3633 | 379.225 | 521.1467 | 612.0367 | 519.3715 | NaN | NaN | NaN | 714.1752 | 1254.5328 | NaN | NaN | 1253.2624 | NaN | NaN | NaN | NaN | 994.5489 | 1253.9629 | NaN | 16.6888 | NaN | 24.215
10272.1292 | 737.3205 | 607.1331 | 369.7949 | 369.7755 | 379.4396 | 519.941 | 607.1775 | 518.6152 | NaN | NaN | NaN | 717.5899 | 1254.5325 | NaN | NaN | 1253.262 | NaN | NaN | NaN | NaN | 1185.6183 | 1253.9626 | NaN | 17.8827 | NaN | 23.1846
10273.1292 | 736.7618 | 607.1111 | 370.0972 | 369.7204 | 379.1795 | 521.4138 | 602.9798 | 515.7919 | NaN | NaN | NaN | 716.7881 | 1254.5305 | NaN | NaN | 1253.26 | NaN | NaN | NaN | NaN | 1118.8372 | 1253.9606 | NaN | 17.7093 | NaN | 22.2972
10274.1292 | 736.8606 | 606.9227 | 369.9355 | 369.5233 | 379.1299 | 520.9734 | 598.3068 | 512.4327 | NaN | NaN | NaN | 730.7829 | 1254.5298 | NaN | NaN | 1253.2594 | NaN | NaN | NaN | NaN | 1176.431 | 1253.9599 | NaN | 19.0221 | NaN | 24.4253
10275.1292 | 734.613 | 608.0442 | 370.125 | 369.791 | 378.8332 | 519.6861 | 606.8236 | 511.7762 | NaN | NaN | NaN | 745.1983 | 1254.5286 | NaN | NaN | 1253.2581 | NaN | NaN | NaN | NaN | 1257.7978 | 1253.9587 | NaN | 17.8856 | NaN | 22.9528
10276.1292 | 733.0332 | 609.1935 | 370.2116 | 369.4517 | 378.5208 | 520.0458 | 604.3227 | 510.4284 | NaN | NaN | NaN | 744.2088 | 1254.5279 | NaN | NaN | 1253.2574 | NaN | NaN | NaN | NaN | 1320.7715 | 1253.958 | NaN | 16.2454 | NaN | 25.4221
10277.1292 | 732.4687 | 609.729 | 370.0411 | 369.2647 | 378.2543 | 520.0014 | 600.0675 | 506.7006 | NaN | NaN | NaN | 714.0424 | 1254.5273 | NaN | NaN | 1253.2568 | NaN | NaN | NaN | NaN | NaN | 1253.9574 | NaN | 17.4834 | NaN | 23.6139
10278.1292 | 731.4501 | 609.3499 | 370.2233 | 369.6203 | 378.1474 | 519.3871 | 593.98 | 505.2624 | NaN | NaN | NaN | 681.5507 | 1254.5265 | NaN | NaN | 1253.256 | NaN | NaN | NaN | NaN | NaN | 1253.9565 | NaN | 16.7886 | NaN | 23.0899
10279.1448 | 730.9922 | 608.8281 | 370.4837 | 369.471 | 378.1293 | 516.9181 | 588.7009 | 505.5341 | NaN | NaN | NaN | 662.6102 | 1254.5251 | NaN | NaN | 1253.2547 | NaN | NaN | NaN | NaN | NaN | 1253.9552 | NaN | 17.875 | NaN | 20.6163
10280.1292 | 731.244 | 609.326 | 370.1958 | 369.3776 | 378.1485 | 516.2105 | 586.9563 | 505.0701 | NaN | NaN | NaN | 699.2538 | 1254.5242 | NaN | NaN | 1253.2538 | NaN | NaN | NaN | NaN | NaN | 1253.9543 | NaN | 15.4355 | NaN | 24.6082
10281.1292 | 732.5107 | 609.0988 | 369.9652 | 369.6794 | 378.2585 | 517.0784 | 585.2875 | 503.5806 | NaN | NaN | NaN | 709.8408 | 1254.5229 | NaN | NaN | 1253.2524 | NaN | NaN | NaN | NaN | NaN | 1253.9529 | NaN | 18.5609 | NaN | 24.5453
10282.1448 | 734.0002 | 608.6972 | 370.1364 | 369.3475 | 378.2586 | 517.1267 | 582.4413 | 502.7952 | NaN | NaN | NaN | 734.1541 | 1254.523 | NaN | NaN | 1253.2525 | NaN | NaN | NaN | NaN | NaN | 1253.9531 | NaN | 15.7403 | NaN | 23.2389
10283.1292 | 734.0363 | 608.1344 | 370.2689 | 369.9823 | 378.1562 | 516.7104 | 579.6449 | 502.3268 | NaN | NaN | NaN | 740.3979 | 1254.5216 | NaN | NaN | 1253.2511 | NaN | NaN | NaN | NaN | NaN | 1253.9517 | NaN | 18.1594 | NaN | 23.7448
10284.1292 | 734.0074 | 608.4986 | 370.7831 | 369.995 | 378.3726 | 515.325 | 576.3986 | 500.0672 | NaN | NaN | NaN | 732.3875 | 1254.52 | NaN | NaN | 1253.2495 | NaN | NaN | NaN | NaN | NaN | 1253.95 | NaN | 18.5558 | NaN | 24.3937
10285.1292 | 734.5779 | 608.5505 | 370.5342 | 369.9365 | 378.3676 | 514.5033 | 576.0982 | 499.4145 | NaN | NaN | NaN | 747.1024 | 1254.5192 | NaN | NaN | 1253.2488 | NaN | NaN | NaN | NaN | NaN | 1253.9493 | NaN | 17.0395 | NaN | 24.1881
10286.1292 | 737.0616 | 608.2833 | 370.0318 | 369.9417 | 378.0196 | 514.3525 | 574.6814 | 501.9462 | NaN | NaN | NaN | 726.8309 | 1254.518 | NaN | NaN | 1253.2475 | NaN | NaN | NaN | NaN | NaN | 1253.948 | NaN | 16.301 | NaN | 21.8274
10287.1292 | 737.843 | 607.9322 | 370.1565 | 369.8688 | 377.9492 | 513.7405 | 575.2832 | 501.4858 | NaN | NaN | NaN | 716.1107 | 1254.5181 | NaN | NaN | 1253.2476 | NaN | NaN | NaN | NaN | NaN | 1253.9482 | NaN | 15.1956 | NaN | 23.9989
10288.1292 | 736.8623 | 609.0979 | 370.3822 | 369.8986 | 377.9604 | 511.6445 | 573.2003 | 500.4604 | NaN | NaN | NaN | 717.321 | 1254.5163 | NaN | NaN | 1253.2459 | NaN | NaN | NaN | NaN | NaN | 1253.9464 | NaN | 15.3041 | NaN | 24.7132
10289.1292 | 738.0002 | 610.4181 | 370.7216 | 370.16 | 378.3696 | 514.4611 | 575.6994 | 498.8734 | NaN | NaN | NaN | 724.3515 | 1254.5159 | NaN | NaN | 1253.2455 | NaN | NaN | NaN | NaN | NaN | 1253.946 | NaN | 14.8299 | NaN | 25.4486
10290.1292 | 738.21 | 610.2541 | 370.6972 | 370.4194 | 378.7767 | 514.3343 | 574.4539 | 501.1413 | NaN | NaN | NaN | 702.9161 | 1254.5144 | NaN | NaN | 1253.244 | NaN | NaN | NaN | NaN | NaN | 1253.9445 | NaN | 18.2533 | NaN | 22.8636
10291.1292 | 738.4886 | 611.4623 | 371.1403 | 371.0609 | 378.5911 | 515.8154 | 573.6344 | 502.9497 | NaN | NaN | NaN | 706.3815 | 1254.5132 | NaN | NaN | 1253.2427 | NaN | NaN | NaN | NaN | NaN | 1253.9433 | NaN | 16.7527 | NaN | 21.9032
10292.1292 | 738.7295 | 611.2798 | 371.5551 | 371.8444 | 378.9882 | 517.9262 | 576.815 | 502.1189 | NaN | NaN | NaN | 719.3459 | 1254.5122 | NaN | NaN | 1253.2417 | NaN | NaN | NaN | NaN | NaN | 1253.9423 | NaN | 18.1689 | NaN | 23.5241
10293.1292 | 738.5824 | 610.7457 | 371.7079 | 371.7781 | 379.2629 | 516.8479 | 575.7911 | 499.1965 | NaN | NaN | NaN | 719.9487 | 1254.512 | NaN | NaN | 1253.2416 | NaN | NaN | NaN | NaN | NaN | 1253.9421 | NaN | 17.0643 | NaN | 24.1926
10294.1292 | 738.5566 | 610.8091 | 371.472 | 371.7342 | 379.6505 | 517.7016 | 580.3709 | 500.5936 | NaN | NaN | NaN | 701.6835 | 1254.5106 | NaN | NaN | 1253.2401 | NaN | NaN | NaN | NaN | NaN | 1253.9407 | NaN | 16.7825 | NaN | 23.4517
10295.1292 | 737.4992 | 610.1416 | 371.7392 | 371.8613 | 380.1954 | 517.6331 | 581.7273 | 500.7289 | NaN | NaN | NaN | 701.5258 | 1254.5088 | NaN | NaN | 1253.2383 | NaN | NaN | NaN | NaN | NaN | 1253.9389 | NaN | 18.724 | NaN | 24.5863
10296.1292 | 737.2099 | 610.1835 | 371.4938 | 372.1569 | 380.3762 | 524.1465 | 589.9959 | 502.4253 | NaN | NaN | NaN | 696.1954 | 1254.5076 | NaN | NaN | 1253.2372 | NaN | NaN | NaN | NaN | NaN | 1253.9377 | NaN | 15.1311 | NaN | 22.5824
10297.1292 | 737.6393 | 610.7913 | 371.4128 | 372.4783 | 380.3107 | 528.0272 | 590.8597 | 502.5224 | NaN | NaN | NaN | 703.2452 | 1254.5076 | NaN | NaN | 1253.2371 | NaN | NaN | NaN | NaN | NaN | 1253.9377 | NaN | 17.7643 | NaN | 23.5678
10298.1292 | 738.4734 | 613.6644 | 371.3227 | 372.407 | 380.4521 | 530.7704 | 592.1833 | 503.2538 | NaN | NaN | NaN | 724.2521 | 1254.5068 | NaN | NaN | 1253.2363 | NaN | NaN | NaN | NaN | NaN | 1253.9368 | NaN | 15.2375 | NaN | 23.5647
10299.1292 | 739.2568 | 614.3717 | 371.1986 | 372.0223 | 380.0159 | 529.4619 | 590.107 | 503.0056 | NaN | NaN | NaN | 724.383 | 1254.5065 | NaN | NaN | 1253.2361 | NaN | NaN | NaN | NaN | NaN | 1253.9366 | NaN | 14.6466 | NaN | 21.8566
10300.1292 | 738.7214 | 613.302 | 371.3551 | 372.044 | 380.0429 | 529.8025 | 588.7115 | 503.6672 | NaN | NaN | NaN | 730.6435 | 1254.5046 | NaN | NaN | 1253.2342 | NaN | NaN | NaN | NaN | NaN | 1253.9347 | NaN | 17.7012 | NaN | 24.0156
10301.1292 | 739.1583 | 613.5522 | 371.7606 | 372.0386 | 380.4567 | 529.1155 | 587.8745 | 505.8815 | NaN | NaN | NaN | 707.1243 | 1254.5044 | NaN | NaN | 1253.2339 | NaN | NaN | NaN | NaN | NaN | 1253.9345 | NaN | 17.9487 | NaN | 24.1733
10302.1292 | 738.0126 | 613.4281 | 371.731 | 372.2783 | 380.4067 | 537.1146 | 595.4732 | 515.5559 | NaN | NaN | NaN | 730.3891 | 1254.5035 | NaN | NaN | 1253.233 | NaN | NaN | NaN | NaN | NaN | 1253.9336 | NaN | 16.4876 | NaN | 22.5129
10303.1292 | 736.4113 | 615.0315 | 371.4997 | 372.0502 | 380.6501 | 542.9216 | 597.9303 | 515.9925 | NaN | NaN | NaN | 745.4683 | 1254.5023 | NaN | NaN | 1253.2318 | NaN | NaN | NaN | NaN | NaN | 1253.9324 | NaN | 16.3225 | NaN | 23.8055
10304.1292 | 735.0257 | 614.9456 | 371.3601 | 371.6848 | 380.9063 | 541.2543 | 594.6254 | 514.3264 | NaN | NaN | NaN | 726.6475 | 1254.5011 | NaN | NaN | 1253.2306 | NaN | NaN | NaN | NaN | NaN | 1253.9312 | NaN | 17.378 | NaN | 23.5968
10305.1292 | 735.558 | 615.6489 | 371.7427 | 371.9563 | 381.5901 | 538.664 | 593.6733 | 514.3588 | NaN | NaN | NaN | 739.5666 | 1254.5012 | NaN | NaN | 1253.2307 | NaN | NaN | NaN | NaN | NaN | 1253.9313 | NaN | 18.2784 | NaN | 23.6716
10306.1292 | 733.6332 | 615.8333 | 372.1544 | 372.4374 | 382.0254 | 540.1136 | 592.3566 | 513.5641 | NaN | NaN | NaN | 743.3253 | 1254.5 | NaN | NaN | 1253.2295 | NaN | NaN | NaN | NaN | NaN | 1253.93 | NaN | 17.9346 | NaN | 23.285
10307.1448 | 733.1019 | 616.3273 | 371.8869 | 372.6328 | 382.5655 | 538.5843 | 593.0438 | 514.7428 | NaN | NaN | NaN | 755.1546 | 1254.4995 | NaN | NaN | 1253.229 | NaN | NaN | NaN | NaN | NaN | 1253.9296 | NaN | 14.9735 | NaN | 23.3208
10308.1292 | 734.7149 | 617.7496 | 372.3408 | 372.9012 | 382.2895 | 551.943 | 592.6546 | 531.2429 | NaN | NaN | NaN | 766.9812 | 1254.4971 | NaN | NaN | 1253.2267 | NaN | NaN | NaN | NaN | NaN | 1253.9272 | NaN | 16.0792 | NaN | 25.159
10309.1448 | 735.0335 | 616.2006 | 372.1207 | 372.8272 | 382.496 | 550.1209 | 590.8436 | 532.7645 | NaN | NaN | NaN | 745.5644 | 1254.4966 | NaN | NaN | 1253.2261 | NaN | NaN | NaN | NaN | NaN | 1253.9267 | NaN | 15.6128 | NaN | 23.2761
10310.1292 | 735.4818 | 617.2489 | 372.0243 | 373.7499 | 382.8031 | 555.8017 | 590.7217 | 530.6918 | NaN | NaN | NaN | 720.934 | 1254.4964 | NaN | NaN | 1253.2259 | NaN | NaN | NaN | NaN | NaN | 1253.9264 | NaN | 16.9336 | NaN | 22.8368
10311.1448 | 736.1127 | 616.9626 | 372.573 | 373.8945 | 383.5993 | 555.0344 | 586.5293 | 529.6208 | NaN | NaN | NaN | 739.4478 | 1254.4954 | NaN | NaN | 1253.225 | NaN | NaN | NaN | NaN | NaN | 1253.9255 | NaN | 15.8763 | NaN | 25.0971
10312.1292 | 735.2547 | 616.9227 | 372.9776 | 373.8249 | 383.8878 | 552.6522 | 583.2786 | 533.4391 | NaN | NaN | NaN | 710.2844 | 1254.4934 | NaN | NaN | 1253.2229 | NaN | NaN | NaN | NaN | NaN | 1253.9235 | NaN | 16.0806 | NaN | 24.1215
10313.1292 | 734.1085 | 616.9616 | 373.2746 | 374.0799 | 384.3697 | 551.3011 | 579.8708 | 531.3266 | NaN | NaN | NaN | 691.8382 | 1254.4934 | NaN | NaN | 1253.2229 | NaN | NaN | NaN | NaN | NaN | 1253.9235 | NaN | 17.008 | NaN | 24.2754
10314.1292 | 732.9112 | 616.0293 | 373.5699 | 374.4387 | 384.7452 | 548.8076 | 576.2951 | 529.9256 | NaN | NaN | NaN | 730.7377 | 1254.4926 | NaN | NaN | 1253.2222 | NaN | NaN | NaN | NaN | NaN | 1253.9227 | NaN | 16.3151 | NaN | 22.3749
10315.1292 | 731.8087 | 615.9756 | 373.7632 | 374.6061 | 384.6566 | 547.8573 | 580.5139 | 529.5607 | NaN | NaN | NaN | 742.1842 | 1254.4907 | NaN | NaN | 1253.2203 | NaN | NaN | NaN | NaN | NaN | 1253.9208 | NaN | 17.7129 | NaN | 23.7293
10316.1292 | 732.8408 | 616.5434 | 373.9678 | 374.4859 | 384.8172 | 547.1422 | 585.072 | 532.112 | NaN | NaN | NaN | 726.4254 | 1254.491 | NaN | NaN | 1253.2206 | NaN | NaN | NaN | NaN | NaN | 1253.9211 | NaN | 17.8225 | NaN | 24.0062
10317.1292 | 732.5146 | 616.0268 | 373.8952 | 374.1146 | 384.3967 | 545.6634 | 581.2475 | 531.4307 | NaN | NaN | NaN | 699.6722 | 1254.4896 | NaN | NaN | 1253.2192 | NaN | NaN | NaN | NaN | NaN | 1253.9197 | NaN | 17.4646 | NaN | 24.4094
10318.1292 | 732.4081 | 616.2954 | 374.0374 | 373.687 | 384.1531 | 542.7823 | 576.456 | 528.7999 | NaN | NaN | NaN | 715.554 | 1254.4893 | NaN | NaN | 1253.2189 | NaN | NaN | NaN | NaN | NaN | 1253.9194 | NaN | 17.5236 | NaN | 24.9587
10319.1448 | 732.1387 | 616.5276 | 373.2475 | 373.6268 | 384.3332 | 539.0987 | 572.5529 | 526.0029 | NaN | NaN | NaN | 724.8636 | 1254.4874 | NaN | NaN | 1253.217 | NaN | NaN | NaN | NaN | NaN | 1253.9175 | NaN | 16.6768 | NaN | 24.8181
10320.1292 | 734.0614 | 615.658 | 373.4333 | 373.5576 | 384.5414 | 536.1756 | 569.7242 | 524.3866 | NaN | NaN | NaN | 712.1156 | 1254.4872 | NaN | NaN | 1253.2167 | NaN | NaN | NaN | NaN | NaN | 1253.9173 | NaN | 17.5359 | NaN | 22.9282
10321.1292 | 735.7304 | 615.0377 | 372.7938 | 373.6951 | 384.6683 | 534.5319 | 569.2182 | 524.3009 | NaN | NaN | NaN | 716.8454 | 1254.4856 | NaN | NaN | 1253.2151 | NaN | NaN | NaN | NaN | NaN | 1253.9157 | NaN | 18.858 | NaN | 24.4443
10322.1292 | 737.884 | 615.1788 | 372.717 | 374.0545 | 384.7722 | 532.6832 | 572.885 | 521.8551 | NaN | NaN | NaN | 691.8939 | 1254.4841 | NaN | NaN | 1253.2136 | NaN | NaN | NaN | NaN | NaN | 1253.9142 | NaN | 17.7296 | NaN | 22.8046
10323.1292 | 739.9682 | 614.5591 | 373.4539 | 374.3989 | 384.9775 | 531.5623 | 571.0843 | 522.6124 | NaN | NaN | NaN | 679.3872 | 1254.4849 | NaN | NaN | 1253.2145 | NaN | NaN | NaN | NaN | NaN | 1253.915 | NaN | 19.2736 | NaN | 23.2913
10324.1292 | 741.1067 | 614.3348 | 373.5449 | 374.5462 | 385.0777 | 535.9934 | 572.5702 | 523.5616 | NaN | NaN | NaN | 668.7395 | 1254.4834 | NaN | NaN | 1253.213 | NaN | NaN | NaN | NaN | NaN | 1253.9135 | NaN | 17.3236 | NaN | 23.6382
10325.1292 | 740.7277 | 614.8483 | 374.7001 | 374.5799 | 384.8543 | 534.8502 | 570.7754 | 522.9267 | NaN | NaN | NaN | 659.6894 | 1254.482 | NaN | NaN | 1253.2116 | NaN | NaN | NaN | NaN | NaN | 1253.9121 | NaN | 18.1673 | NaN | 24.6654
10326.1292 | 741.5484 | 614.2714 | 375.0999 | 374.498 | 385.0876 | 534.1257 | 567.3856 | 520.8872 | NaN | NaN | NaN | 695.5384 | 1254.4815 | NaN | NaN | 1253.2111 | NaN | NaN | NaN | NaN | NaN | 1253.9116 | NaN | 16.9865 | NaN | 22.8816
10327.1292 | 742.8945 | 613.9292 | 375.0947 | 374.4202 | 385.2931 | 532.7175 | 566.4098 | 520.2299 | NaN | NaN | NaN | 717.3184 | 1254.4807 | NaN | NaN | 1253.2102 | NaN | NaN | NaN | NaN | NaN | 1253.9108 | NaN | 15.8436 | NaN | 23.1113
10328.1292 | 742.9449 | 612.9948 | 375.0819 | 374.509 | 385.1611 | 531.3969 | 567.2019 | 520.7573 | NaN | NaN | NaN | 713.8254 | 1254.4805 | NaN | NaN | 1253.2101 | NaN | NaN | NaN | NaN | NaN | 1253.9106 | NaN | 18.5425 | NaN | 24.8552
10329.1292 | 743.9666 | 612.6884 | 375.0542 | 374.4038 | 385.5539 | 534.9013 | 572.2956 | 521.1601 | NaN | NaN | NaN | 739.6116 | 1254.4792 | NaN | NaN | 1253.2088 | NaN | NaN | NaN | NaN | NaN | 1253.9093 | NaN | 18.0885 | NaN | 23.69
10330.1292 | 743.2577 | 612.1718 | 375.3917 | 375.2359 | 385.7064 | 536.1059 | 579.5638 | 525.2725 | NaN | NaN | NaN | 728.999 | 1254.4774 | NaN | NaN | 1253.2069 | NaN | NaN | NaN | NaN | NaN | 1253.9074 | NaN | 16.0754 | NaN | 23.9773
10331.1292 | 741.9796 | 613.0071 | 375.0011 | 375.4785 | 386.1381 | 537.6749 | 581.0692 | 526.6667 | NaN | NaN | NaN | 724.707 | 1254.4767 | NaN | NaN | 1253.2063 | NaN | NaN | NaN | NaN | NaN | 1253.9068 | NaN | 15.8704 | NaN | 22.2993
10332.1292 | 741.327 | 615.4087 | 375.0717 | 375.1241 | 386.0928 | 540.8944 | 583.3531 | 531.0143 | NaN | NaN | NaN | 752.9206 | 1254.4768 | NaN | NaN | 1253.2063 | NaN | NaN | NaN | NaN | NaN | 1253.9069 | NaN | 18.4159 | NaN | 22.9595
10333.1292 | 739.7762 | 616.1652 | 375.6918 | 375.4274 | 386.6456 | 541.5097 | 581.0371 | 529.4128 | NaN | NaN | NaN | 756.599 | 1254.4748 | NaN | NaN | 1253.2043 | NaN | NaN | NaN | NaN | NaN | 1253.9049 | NaN | 17.8658 | NaN | 23.2987
10334.1292 | 738.7251 | 616.5832 | 376.6542 | 376.2982 | 386.7951 | 542.5458 | 582.0809 | 530.7253 | NaN | NaN | NaN | 728.0634 | 1254.4743 | NaN | NaN | 1253.2038 | NaN | NaN | NaN | NaN | NaN | 1253.9044 | NaN | 15.1011 | NaN | 23.8018
10335.1292 | 739.0282 | 616.6013 | 376.6019 | 376.7974 | 387.5432 | 541.4912 | 580.4249 | 530.5729 | NaN | NaN | NaN | 745.5305 | 1254.473 | NaN | NaN | 1253.2026 | NaN | NaN | NaN | NaN | NaN | 1253.9031 | NaN | 16.6751 | NaN | 23.9118
10336.1292 | 739.405 | 616.9146 | 376.8869 | 377.2216 | 387.9874 | 539.575 | 580.0297 | 531.3603 | NaN | NaN | NaN | 737.7635 | 1254.473 | NaN | NaN | 1253.2025 | NaN | NaN | NaN | NaN | NaN | 1253.903 | NaN | 15.5084 | NaN | 24.3403
10337.1292 | 739.9431 | 617.6757 | 377.1593 | 377.3698 | 388.0349 | 538.0464 | 579.47 | 531.1821 | NaN | NaN | NaN | 717.573 | 1254.4718 | NaN | NaN | 1253.2014 | NaN | NaN | NaN | NaN | NaN | 1253.9019 | NaN | 17.0033 | NaN | 24.2998
10338.1292 | 740.6591 | 618.1041 | 377.0974 | 377.995 | 388.3519 | 538.3898 | 579.4704 | 532.6242 | NaN | NaN | NaN | 680.9538 | 1254.4707 | NaN | NaN | 1253.2002 | NaN | NaN | NaN | NaN | NaN | 1253.9008 | NaN | 16.5412 | NaN | 23.9407
10339.1292 | 740.6273 | 618.3644 | 377.8155 | 378.0509 | 388.7154 | 537.7577 | 578.6853 | 532.1945 | NaN | NaN | NaN | 654.6301 | 1254.4706 | NaN | NaN | 1253.2001 | NaN | NaN | NaN | NaN | NaN | 1253.9007 | NaN | 17.5345 | NaN | 24.3684
10340.1292 | 742.0191 | 618.7499 | 378.3029 | 378.4841 | 388.9509 | 536.2376 | 577.3974 | 531.098 | NaN | NaN | NaN | 630.6132 | 1254.4692 | NaN | NaN | 1253.1988 | NaN | NaN | NaN | NaN | NaN | 1253.8993 | NaN | 17.5994 | NaN | 23.3532
10341.1292 | 743.7876 | 618.7355 | 377.9802 | 378.8328 | 389.193 | 534.1092 | 575.9957 | 531.5551 | NaN | NaN | NaN | 621.3113 | 1254.4687 | NaN | NaN | 1253.1983 | NaN | NaN | NaN | NaN | NaN | 1253.8988 | NaN | 17.4011 | NaN | 24.4888
10342.1448 | 743.9237 | 619.1461 | 378.5878 | 379.9874 | 389.6354 | 535.2119 | 578.0585 | 532.1307 | NaN | NaN | NaN | 605.5395 | 1254.4672 | NaN | NaN | 1253.1968 | NaN | NaN | NaN | NaN | NaN | 1253.8973 | NaN | 16.8601 | NaN | 22.9248
10343.1292 | 742.8705 | 619.3286 | 378.7657 | 380.1619 | 389.9247 | 536.5355 | 577.593 | 529.4419 | NaN | NaN | NaN | 605.9316 | 1254.4665 | NaN | NaN | 1253.196 | NaN | NaN | NaN | NaN | NaN | 1253.8966 | NaN | 18.5548 | NaN | 24.0582
10344.1292 | 741.7203 | 619.1181 | 379.5589 | 380.8802 | 390.3094 | 535.0956 | 582.9325 | 527.3986 | NaN | NaN | NaN | 618.571 | 1254.4655 | NaN | NaN | 1253.1951 | NaN | NaN | NaN | NaN | NaN | 1253.8956 | NaN | 17.8951 | NaN | 24.9272
10345.1292 | 741.5493 | 619.3576 | 379.8227 | 381.3659 | 390.8044 | 540.4267 | 598.9954 | 525.1114 | NaN | NaN | NaN | 657.2083 | 1254.4657 | NaN | NaN | 1253.1953 | NaN | NaN | NaN | NaN | NaN | 1253.8958 | NaN | 17.4369 | NaN | 24.3306
10346.1292 | 740.9621 | 618.9472 | 379.9026 | 381.7551 | 391.1547 | 546.941 | 600.2882 | 524.9915 | NaN | NaN | NaN | 699.3443 | 1254.4637 | NaN | NaN | 1253.1933 | NaN | NaN | NaN | NaN | NaN | 1253.8938 | NaN | 15.6992 | NaN | 23.1337
10347.1292 | 740.7565 | 618.0861 | 379.433 | 381.8038 | 391.513 | 552.3347 | 603.7239 | 527.8745 | NaN | NaN | NaN | 727.7605 | 1254.4632 | NaN | NaN | 1253.1928 | NaN | NaN | NaN | NaN | NaN | 1253.8933 | NaN | 18.2513 | NaN | 22.8043
10348.1292 | 741.7448 | 618.1188 | 380.0233 | 381.7876 | 392.2094 | 562.1237 | 602.4723 | 534.6428 | NaN | NaN | NaN | 747.9649 | 1254.4625 | NaN | NaN | 1253.1921 | NaN | NaN | NaN | NaN | NaN | 1253.8926 | NaN | 18.3141 | NaN | 23.6582
10349.1292 | 743.1861 | 616.6068 | 379.4918 | 381.3755 | 392.1099 | 565.3177 | 599.9277 | 533.9215 | NaN | NaN | NaN | 734.3274 | 1254.462 | NaN | NaN | 1253.1916 | NaN | NaN | NaN | NaN | NaN | 1253.8921 | NaN | 18.8613 | NaN | 22.7389
10350.1292 | 743.8058 | 615.1288 | 379.8818 | 381.5644 | 392.3667 | 566.0508 | 597.6146 | 534.9384 | NaN | NaN | NaN | 756.7018 | 1254.4603 | NaN | NaN | 1253.1899 | NaN | NaN | NaN | NaN | NaN | 1253.8904 | NaN | 17.8371 | NaN | 23.5125
10351.1292 | 742.0937 | 614.6426 | 379.562 | 382.276 | 392.642 | 566.5184 | 598.9288 | 535.2562 | NaN | NaN | NaN | 769.0135 | 1254.4595 | NaN | NaN | 1253.1891 | NaN | NaN | NaN | NaN | NaN | 1253.8896 | NaN | 17.9055 | NaN | 24.1032
10352.1292 | 742.4879 | 614.8544 | 379.5172 | 382.1794 | 392.4532 | 568.1758 | 608.1496 | 537.0672 | NaN | NaN | NaN | 795.915 | 1254.4586 | NaN | NaN | 1253.1882 | NaN | NaN | NaN | NaN | NaN | 1253.8887 | NaN | 16.598 | NaN | 24.0326
10353.1292 | 741.4771 | 615.0618 | 379.5765 | 382.2083 | 392.7153 | 571.3952 | 606.2374 | 539.6584 | NaN | NaN | NaN | 785.5331 | 1254.4584 | NaN | NaN | 1253.188 | NaN | NaN | NaN | NaN | NaN | 1253.8885 | NaN | 14.5201 | NaN | 24.1778
10354.1292 | 740.4359 | 616.1258 | 380.0771 | 382.2952 | 392.2589 | 574.7575 | 607.5138 | 539.3831 | NaN | NaN | NaN | 794.592 | 1254.4573 | NaN | NaN | 1253.1869 | NaN | NaN | NaN | NaN | NaN | 1253.8874 | NaN | 19.2611 | NaN | 24.2452
10355.1292 | 740.0978 | 616.4936 | 379.8136 | 381.9689 | 392.24 | 573.129 | 607.902 | 542.0302 | NaN | NaN | NaN | 787.5821 | 1254.4558 | NaN | NaN | 1253.1854 | NaN | NaN | NaN | NaN | NaN | 1253.8859 | NaN | 18.0979 | NaN | 24.7413
10356.1292 | 739.5157 | 617.299 | 380.306 | 382.1024 | 392.3849 | 571.2792 | 604.233 | 556.7864 | NaN | NaN | NaN | 793.8899 | 1254.4557 | NaN | NaN | 1253.1853 | NaN | NaN | NaN | NaN | NaN | 1253.8858 | NaN | 16.1249 | NaN | 23.3667
10357.1292 | 738.272 | 618.5495 | 380.2889 | 382.2181 | 392.567 | 575.9067 | 607.8709 | 569.8641 | NaN | NaN | NaN | 802.6471 | 1254.454 | NaN | NaN | 1253.1836 | NaN | NaN | NaN | NaN | NaN | 1253.8841 | NaN | 16.5756 | NaN | 22.5642
10358.1292 | 738.0112 | 619.0695 | 380.2109 | 381.8411 | 392.9016 | 576.6024 | 605.7422 | 565.3663 | NaN | NaN | NaN | 795.7852 | 1254.4545 | NaN | NaN | 1253.184 | NaN | NaN | NaN | NaN | NaN | 1253.8846 | NaN | 15.2921 | NaN | 22.846
10359.1292 | 738.0881 | 619.1718 | 379.6849 | 382.4054 | 392.6905 | 573.9046 | 600.0365 | 561.7865 | NaN | NaN | NaN | 746.269 | 1254.4534 | NaN | NaN | 1253.183 | NaN | NaN | NaN | NaN | NaN | 1253.8835 | NaN | 14.4756 | NaN | 22.9251
10360.1292 | 739.1555 | 619.3489 | 380.4075 | 382.1239 | 392.9033 | 571.2785 | 595.8243 | 558.4957 | NaN | NaN | NaN | 709.1401 | 1254.4522 | NaN | NaN | 1253.1818 | NaN | NaN | NaN | NaN | NaN | 1253.8823 | NaN | 16.7016 | NaN | 23.9603
10361.1292 | 741.3053 | 619.642 | 381.4941 | 381.726 | 392.9941 | 568.9492 | 599.2724 | 553.2394 | NaN | NaN | NaN | 685.4058 | 1254.451 | NaN | NaN | 1253.1806 | NaN | NaN | NaN | NaN | NaN | 1252.9924 | NaN | 16.7357 | NaN | 23.3174
10362.1292 | 742.1781 | 618.8238 | 381.313 | 381.5554 | 393.0132 | 567.2504 | 595.9348 | 551.9189 | NaN | NaN | NaN | 720.8285 | 1254.4506 | NaN | NaN | 1253.1801 | NaN | NaN | NaN | NaN | NaN | 1224.3154 | NaN | 16.7762 | NaN | 22.5853
10363.1292 | 743.1522 | 619.4 | 382.0736 | 381.4139 | 393.2581 | 565.4383 | 593.1486 | 548.6323 | NaN | NaN | NaN | 720.3817 | 1254.4498 | NaN | NaN | 1253.1794 | NaN | NaN | NaN | NaN | NaN | 1197.4531 | NaN | 18.9666 | NaN | 25.0043
10364.1292 | 744.7452 | 619.3701 | 381.8897 | 381.2374 | 393.0129 | 569.3137 | 595.5813 | 548.02 | NaN | NaN | NaN | 731.0041 | 1254.4491 | NaN | NaN | 1253.1786 | NaN | NaN | NaN | NaN | NaN | 1177.0035 | NaN | 19.2479 | NaN | 22.0489
10365.1292 | 744.3661 | 619.6569 | 381.6585 | 381.1727 | 393.2178 | 566.7809 | 595.1874 | 547.64 | NaN | NaN | NaN | 734.955 | 1254.4476 | NaN | NaN | 1253.1772 | NaN | NaN | NaN | NaN | NaN | 1156.1494 | NaN | 15.4022 | NaN | 24.3895
10366.1292 | 743.953 | 620.5589 | 381.9569 | 380.9957 | 393.5818 | 568.9347 | 594.3716 | 547.2724 | NaN | NaN | NaN | 711.8245 | 1254.4465 | NaN | NaN | 1253.1761 | NaN | NaN | NaN | NaN | NaN | 1136.1947 | NaN | 17.699 | NaN | 21.9853
10367.1292 | 745.263 | 620.9851 | 381.5361 | 380.9674 | 393.6116 | 568.5011 | 592.6161 | 545.2201 | NaN | NaN | NaN | 742.8262 | 1254.4462 | NaN | NaN | 1253.1758 | NaN | NaN | NaN | NaN | NaN | 1116.2482 | NaN | 16.0605 | NaN | 22.7921
10368.1292 | 744.3211 | 620.4154 | 381.6883 | 380.9272 | 393.2729 | 564.2213 | 589.2206 | 545.5995 | NaN | NaN | NaN | 749.6163 | 1254.4448 | NaN | NaN | 1253.1744 | NaN | NaN | NaN | NaN | NaN | 1091.8755 | NaN | 15.2556 | NaN | 23.6366
10369.1292 | 744.8198 | 620.5498 | 382.0393 | 380.9531 | 393.7125 | 562.1226 | 587.5724 | 542.3359 | NaN | NaN | NaN | 758.1722 | 1254.4443 | NaN | NaN | 1253.1739 | NaN | NaN | NaN | NaN | NaN | 1069.3019 | NaN | 18.307 | NaN | 23.9093
10370.1292 | 745.9093 | 620.7054 | 382.8159 | 381.0515 | 393.6761 | 558.3384 | 586.0446 | 542.4489 | NaN | NaN | NaN | 770.4536 | 1254.4436 | NaN | NaN | 1253.1732 | NaN | NaN | NaN | NaN | NaN | 1042.9594 | NaN | 16.2217 | NaN | 23.1592
10371.1292 | 746.2235 | 620.9697 | 382.6359 | 381.103 | 393.6255 | 557.1858 | 584.3877 | 542.1838 | NaN | NaN | NaN | 742.1605 | 1254.4431 | NaN | NaN | 1253.1727 | NaN | NaN | NaN | NaN | NaN | 1019.8651 | NaN | 18.1526 | NaN | 23.1065
10372.1292 | 744.9576 | 619.873 | 382.8687 | 381.4035 | 393.953 | 554.054 | 582.0592 | 539.5346 | NaN | NaN | NaN | 710.5903 | 1254.4421 | NaN | NaN | 1253.1717 | NaN | NaN | NaN | NaN | NaN | 995.2083 | NaN | 15.4445 | NaN | 24.2277
10373.1292 | 745.1029 | 619.7683 | 382.6299 | 382.2978 | 393.7296 | 552.9659 | 580.5263 | 537.7158 | NaN | NaN | NaN | 723.959 | 1254.4411 | NaN | NaN | 1253.1706 | NaN | NaN | NaN | NaN | NaN | 976.8491 | NaN | 14.7013 | NaN | 21.7204
10374.1292 | 745.7596 | 620.4083 | 383.4566 | 382.4184 | 393.8669 | 551.9197 | 580.7284 | 539.6182 | NaN | NaN | NaN | 726.6756 | 1254.4396 | NaN | NaN | 1253.1692 | NaN | NaN | NaN | NaN | NaN | 959.9505 | NaN | 15.1126 | NaN | 23.1388
10375.1292 | 745.9452 | 620.6203 | 383.4892 | 382.7558 | 393.4775 | 552.9991 | 583.4922 | 538.4441 | NaN | NaN | NaN | 700.3231 | 1254.4394 | NaN | NaN | 1253.1689 | NaN | NaN | NaN | NaN | NaN | 942.3879 | NaN | 16.8276 | NaN | 21.7411
10376.1292 | 745.7396 | 621.7573 | 383.51 | 383.2781 | 393.4937 | 555.1183 | 584.3607 | 551.3647 | NaN | NaN | NaN | 699.0525 | 1254.4392 | NaN | NaN | 1253.1688 | NaN | NaN | NaN | NaN | NaN | 913.9746 | NaN | 16.007 | NaN | 22.4986
10377.1292 | 745.668 | 621.3869 | 384.3761 | 383.4099 | 394.0677 | 554.599 | 583.9138 | 550.3702 | NaN | NaN | NaN | 722.9949 | 1254.4371 | NaN | NaN | 1253.1667 | NaN | NaN | NaN | NaN | NaN | 888.4121 | NaN | 18.2376 | NaN | 22.2987
10378.1292 | 745.4866 | 621.5347 | 383.8501 | 383.5867 | 393.8717 | 552.6899 | 581.0659 | 547.0539 | NaN | NaN | NaN | 740.3492 | 1254.4365 | NaN | NaN | 1253.166 | NaN | NaN | NaN | NaN | NaN | 874.6717 | NaN | 17.2991 | NaN | 23.0625
10379.1292 | 744.579 | 622.1213 | 384.1296 | 384.0673 | 393.9074 | 551.8533 | 580.771 | 545.9945 | NaN | NaN | NaN | 709.1857 | 1254.4359 | NaN | NaN | 1253.1655 | NaN | NaN | NaN | NaN | NaN | 858.9502 | NaN | 17.0996 | NaN | 24.4342
10380.1292 | 743.4031 | 622.3638 | 384.717 | 384.2455 | 394.3584 | 550.622 | 577.3329 | 544.384 | NaN | NaN | NaN | 712.1971 | 1254.4345 | NaN | NaN | 1253.1641 | NaN | NaN | NaN | NaN | NaN | 839.1783 | NaN | 16.0184 | NaN | 23.374
10381.1292 | 746.4161 | 622.8398 | 384.6878 | 384.3962 | 394.8276 | 551.0623 | 584.8059 | 553.1113 | NaN | NaN | NaN | 674.3898 | 1254.4343 | NaN | NaN | 1253.1638 | NaN | NaN | NaN | NaN | NaN | 815.546 | NaN | 17.3811 | NaN | 24.1283
10382.1292 | 746.2197 | 622.8598 | 384.8229 | 385.1047 | 395.2577 | 550.0702 | 588.7849 | 550.9868 | NaN | NaN | NaN | 654.3001 | 1254.4341 | NaN | NaN | 1253.1637 | NaN | NaN | NaN | NaN | NaN | 795.1554 | NaN | 18.9278 | NaN | 22.9173
10383.1292 | 745.6547 | 623.5789 | 385.2276 | 385.6264 | 395.1166 | 556.9381 | 588.9464 | 549.6165 | NaN | NaN | NaN | 636.1776 | 1254.4331 | NaN | NaN | 1253.1627 | NaN | NaN | NaN | NaN | NaN | 769.2479 | NaN | 17.2343 | NaN | 23.1776
10384.1292 | 744.7475 | 624.1462 | 385.9332 | 385.8571 | 395.2179 | 560.0199 | 590.466 | 550.3243 | NaN | NaN | NaN | 624.4072 | 1254.4312 | NaN | NaN | 1253.1608 | NaN | NaN | NaN | NaN | NaN | 744.0617 | NaN | 17.4333 | NaN | 22.8851
10385.1292 | 744.0506 | 623.8535 | 385.8322 | 385.5679 | 395.1613 | 563.5645 | 591.6842 | 548.3656 | NaN | NaN | NaN | 620.1539 | 1254.4314 | NaN | NaN | 1253.161 | NaN | NaN | NaN | NaN | NaN | 713.8538 | NaN | 17.2316 | NaN | 22.9106
10386.1292 | 744.5944 | 624.8016 | 386.2379 | 385.6596 | 395.2669 | 567.7152 | 593.9974 | 555.5888 | NaN | NaN | NaN | 651.4875 | 1254.4298 | NaN | NaN | 1253.1594 | NaN | NaN | NaN | NaN | NaN | 684.3493 | NaN | 18.1192 | NaN | 24.4477
10387.1292 | 745.3424 | 625.4628 | 386.669 | 385.7149 | 395.4503 | 564.8497 | 590.4283 | 554.0646 | NaN | NaN | NaN | 653.1427 | 1254.4297 | NaN | NaN | 1253.1593 | NaN | NaN | NaN | NaN | NaN | 665.1611 | NaN | 15.4785 | NaN | 23.8087
10388.1292 | 744.4829 | 624.9972 | 386.5243 | 385.8514 | 395.6607 | 563.5785 | 587.6148 | 549.9245 | NaN | NaN | NaN | 666.17 | 1254.4282 | NaN | NaN | 1253.1577 | NaN | NaN | NaN | NaN | NaN | 648.2516 | NaN | 17.0349 | NaN | 23.5337
10389.1292 | 744.0537 | 624.4554 | 386.7794 | 386.4765 | 396.2975 | 563.604 | 585.5376 | 563.6546 | NaN | NaN | NaN | 700.3533 | 1254.4283 | NaN | NaN | 1253.1579 | NaN | NaN | NaN | NaN | NaN | 628.7857 | NaN | 16.146 | NaN | 24.4889
10390.1292 | 744.3889 | 624.4011 | 386.8178 | 386.5839 | 396.4486 | 561.4313 | 585.7313 | 581.5958 | NaN | NaN | NaN | 717.0128 | 1254.4271 | NaN | NaN | 1253.1567 | NaN | NaN | NaN | NaN | NaN | 619.1023 | NaN | 16.7834 | NaN | 22.6365
10391.1292 | 745.0823 | 624.6531 | 386.7783 | 387.3544 | 396.8253 | 562.7959 | 585.7618 | 589.3354 | NaN | NaN | NaN | 723.6744 | 1254.4259 | NaN | NaN | 1253.1555 | NaN | NaN | NaN | NaN | NaN | 607.5757 | NaN | 15.2505 | NaN | 21.1961
10392.1292 | 748.7732 | 625.9427 | 387.4141 | 387.7263 | 396.6992 | 561.665 | 585.6242 | 586.6307 | NaN | NaN | NaN | 746.1024 | 1254.4247 | NaN | NaN | 1253.1543 | NaN | NaN | NaN | NaN | NaN | 595.3967 | NaN | 19.2752 | NaN | 23.6333
10393.1292 | 751.0996 | 626.3461 | 387.4811 | 388.3198 | 397.4915 | 562.5975 | 585.3926 | 582.9703 | NaN | NaN | NaN | 756.8527 | 1254.4247 | NaN | NaN | 1253.1543 | NaN | NaN | NaN | NaN | NaN | 579.1474 | NaN | 16.4099 | NaN | 23.1978
10394.1292 | 752.7927 | 626.4595 | 387.568 | 388.9775 | 397.5408 | 565.8115 | 588.0551 | 578.7341 | NaN | NaN | NaN | 739.5744 | 1254.4242 | NaN | NaN | 1253.1538 | NaN | NaN | NaN | NaN | NaN | 559.2853 | NaN | 18.6935 | NaN | 24.6668
10395.1292 | 753.2252 | 626.8968 | 388.2548 | 389.1255 | 397.8998 | 566.2171 | 587.7705 | 575.0988 | NaN | NaN | NaN | 712.6976 | 1254.4239 | NaN | NaN | 1253.1535 | NaN | NaN | NaN | NaN | NaN | 541.1335 | NaN | 18.502 | NaN | 23.6477
10396.1292 | 755.5584 | 629.081 | 387.8619 | 389.4653 | 398.1842 | 567.3177 | 588.0241 | 575.0574 | NaN | NaN | NaN | 696.6483 | 1254.4227 | NaN | NaN | 1253.1523 | NaN | NaN | NaN | NaN | NaN | 526.5995 | NaN | 17.8512 | NaN | 22.9147
10397.1292 | 757.2844 | 629.1111 | 388.6779 | 389.6519 | 398.3973 | 565.6835 | 588.7501 | 572.9443 | NaN | NaN | NaN | 680.7975 | 1254.4207 | NaN | NaN | 1253.1503 | NaN | NaN | NaN | NaN | NaN | 512.1519 | NaN | 18.532 | NaN | 24.9552
10398.1292 | 757.3523 | 629.2135 | 388.0566 | 389.6428 | 398.6634 | 567.2566 | 586.8822 | 568.7876 | NaN | NaN | NaN | 672.7122 | 1254.4206 | NaN | NaN | 1253.1502 | NaN | NaN | NaN | NaN | NaN | 505.2157 | NaN | 18.9704 | NaN | 24.4441
10399.1292 | 756.7143 | 626.8036 | 388.4848 | 389.5228 | 399.0253 | 579.1438 | 589.8683 | 567.8544 | NaN | NaN | NaN | 670.2438 | 1254.4203 | NaN | NaN | 1253.1499 | NaN | NaN | NaN | NaN | NaN | 494.5988 | NaN | 18.0898 | NaN | 23.8358
10400.1292 | 756.0631 | 627.0867 | 388.1176 | 388.932 | 399.1563 | 579.7526 | 595.3825 | 576.0001 | NaN | NaN | NaN | 653.4049 | 1254.4186 | NaN | NaN | 1253.1482 | NaN | NaN | NaN | NaN | NaN | 487.9002 | NaN | 16.7751 | NaN | 21.1853
10401.1292 | 756.3608 | 627.7029 | 388.3269 | 388.5531 | 399.2544 | 584.5944 | 600.806 | 575.2336 | NaN | NaN | NaN | 660.7748 | 1254.418 | NaN | NaN | 1253.1476 | NaN | NaN | NaN | NaN | NaN | 475.9101 | NaN | 14.7 | NaN | 24.4429
10402.1448 | 757.4218 | 628.2751 | 388.4257 | 388.464 | 399.2899 | 586.6505 | 598.7653 | 569.6245 | NaN | NaN | NaN | 665.4404 | 1254.417 | NaN | NaN | 1253.1466 | NaN | NaN | NaN | NaN | NaN | 463.0389 | NaN | 17.8178 | NaN | 23.9461
10403.1292 | 756.5438 | 627.8949 | 388.9973 | 389.0041 | 400.1345 | 583.8639 | 598.278 | 567.1966 | NaN | NaN | NaN | 673.5411 | 1254.4163 | NaN | NaN | 1253.1459 | NaN | NaN | NaN | NaN | NaN | 449.1299 | NaN | 16.0292 | NaN | 23.3946
10404.1292 | 754.6925 | 627.5801 | 389.1511 | 388.9538 | 400.3326 | 580.8721 | 594.1532 | 574.8554 | NaN | NaN | NaN | 665.8215 | 1254.4167 | NaN | NaN | 1253.1463 | NaN | NaN | NaN | NaN | NaN | 434.6523 | NaN | 15.051 | NaN | 21.9338
10405.1292 | 753.8827 | 628.1089 | 389.0664 | 388.9994 | 400.7784 | 578.4012 | 595.6268 | 592.2439 | NaN | NaN | NaN | 655.8197 | 1254.4153 | NaN | NaN | 1253.1449 | NaN | NaN | NaN | NaN | NaN | 421.4323 | NaN | 16.7232 | NaN | 24.4387
10406.1292 | 751.7745 | 628.7542 | 389.0593 | 389.3047 | 401.2698 | 578.7795 | 598.4473 | 600.4721 | NaN | NaN | NaN | 693.3436 | 1254.4147 | NaN | NaN | 1253.1443 | NaN | NaN | NaN | NaN | NaN | 406.5032 | NaN | 18.3722 | NaN | 24.8299
10407.1292 | 750.5444 | 627.1004 | 389.4761 | 389.451 | 401.3343 | 575.4114 | 595.9705 | 595.2976 | NaN | NaN | NaN | 728.7922 | 1254.4138 | NaN | NaN | 1253.1434 | NaN | NaN | NaN | NaN | NaN | 396.9025 | NaN | 16.3518 | NaN | 25.3978
10408.1292 | 749.554 | 626.4863 | 389.7416 | 389.7464 | 401.4777 | 577.3877 | 603.8466 | 601.0302 | NaN | NaN | NaN | 746.5969 | 1254.4126 | NaN | NaN | 1253.1422 | NaN | NaN | NaN | NaN | NaN | 383.5451 | NaN | 15.3879 | NaN | 23.2621
10409.1292 | 748.7859 | 626.0752 | 389.4286 | 389.5875 | 401.2779 | 580.2623 | 598.0351 | 597.2016 | NaN | NaN | NaN | 745.2735 | 1254.4123 | NaN | NaN | 1253.1419 | NaN | NaN | NaN | NaN | NaN | 364.1641 | NaN | 16.2322 | NaN | 23.794
10410.1292 | 748.2881 | 626.8945 | 389.3694 | 389.8469 | 401.1252 | 581.0075 | 602.9409 | 599.0338 | NaN | NaN | NaN | 745.4144 | 1254.4107 | NaN | NaN | 1253.1403 | NaN | NaN | NaN | NaN | NaN | 346.3552 | NaN | 16.7058 | NaN | 24.8462
10411.1292 | 748.3569 | 626.7571 | 390.1523 | 389.6846 | 401.1754 | 583.7113 | 604.4763 | 593.9975 | NaN | NaN | NaN | 766.0214 | 1254.4102 | NaN | NaN | 1253.1398 | NaN | NaN | NaN | NaN | NaN | 329.9135 | NaN | 16.8381 | NaN | 23.8727
10412.1292 | 747.2663 | 627.6925 | 389.6312 | 389.6994 | 401.2567 | 583.8178 | 603.8026 | 601.7432 | NaN | NaN | NaN | 776.4515 | 1254.4088 | NaN | NaN | 1253.1385 | NaN | NaN | NaN | NaN | NaN | 310.0431 | NaN | 15.9189 | NaN | 23.2205
10413.1292 | 746.2508 | 628.6804 | 389.943 | 390.406 | 401.5073 | 581.277 | 599.6918 | 598.8089 | NaN | NaN | NaN | 753.049 | 1254.4094 | NaN | NaN | 1253.139 | NaN | NaN | NaN | NaN | NaN | 290.6106 | NaN | 15.496 | NaN | 24.3788
10414.1292 | 748.0569 | 628.9829 | 389.871 | 390.5311 | 401.9824 | 578.5731 | 596.5779 | 595.4642 | NaN | NaN | NaN | 777.1341 | 1254.4082 | NaN | NaN | 1253.1378 | NaN | NaN | NaN | NaN | NaN | 275.8843 | NaN | 14.5598 | NaN | 22.5223
10415.1292 | 750.4229 | 630.5509 | 389.6229 | 390.7034 | 401.7605 | 578.5677 | 597.185 | 593.0969 | NaN | NaN | NaN | 756.9177 | 1254.4073 | NaN | NaN | 1253.1369 | NaN | NaN | NaN | NaN | NaN | 266.6833 | NaN | 16.0426 | NaN | 23.6219
10416.1448 | 748.8927 | 630.7493 | 390.0607 | 390.8094 | 402.4221 | 577.5095 | 593.4396 | 588.5714 | NaN | NaN | NaN | 723.9238 | 1254.4058 | NaN | NaN | 1253.1354 | NaN | NaN | NaN | NaN | NaN | 256.78 | NaN | 15.6717 | NaN | 24.4116
10417.1292 | 749.0264 | 631.7923 | 390.7045 | 391.1131 | 402.534 | 578.1513 | 591.4565 | 582.6294 | NaN | NaN | NaN | 756.6869 | 1254.4054 | NaN | NaN | 1253.135 | NaN | NaN | NaN | NaN | NaN | 239.8629 | NaN | 16.7546 | NaN | 24.1725
10418.1292 | 749.1454 | 631.7795 | 391.0013 | 391.2244 | 402.44 | 579.6519 | 590.7772 | 578.5199 | NaN | NaN | NaN | 767.5247 | 1254.4056 | NaN | NaN | 1253.1352 | NaN | NaN | NaN | NaN | NaN | 222.2347 | NaN | 15.5501 | NaN | 24.6627
10419.1292 | 747.2842 | 631.8353 | 391.4495 | 391.1956 | 402.2883 | 578.2905 | 588.6516 | 577.1896 | NaN | NaN | NaN | 743.9444 | 1254.4037 | NaN | NaN | 1253.1333 | NaN | NaN | NaN | NaN | NaN | 204.9313 | NaN | 15.2028 | NaN | 23.4799
10420.1292 | 748.4522 | 632.0413 | 391.6989 | 391.4172 | 402.7595 | 577.8778 | 587.3623 | 576.8259 | NaN | NaN | NaN | 748.3377 | 1254.4027 | NaN | NaN | 1253.1324 | NaN | NaN | NaN | NaN | NaN | 189.0737 | NaN | 15.4821 | NaN | 23.2106
10421.1292 | 750.1314 | 630.8075 | 391.1766 | 392.0711 | 403.1188 | 577.4976 | 591.4732 | 578.1986 | NaN | NaN | NaN | 749.988 | 1254.4026 | NaN | NaN | 1253.1322 | NaN | NaN | NaN | NaN | NaN | 172.725 | NaN | 15.9653 | NaN | 23.2895
10422.1292 | 750.7798 | 630.2694 | 391.0876 | 392.3189 | 403.4107 | 579.3151 | 592.0781 | 579.2299 | NaN | NaN | NaN | 728.1911 | 1254.4019 | NaN | NaN | 1253.1315 | NaN | NaN | NaN | NaN | NaN | 160.1659 | NaN | 14.6542 | NaN | 23.9328
10423.1292 | 751.4956 | 631.3244 | 390.8723 | 392.2815 | 403.5511 | 587.6008 | 591.4774 | 579.4927 | NaN | NaN | NaN | 696.8998 | 1254.4013 | NaN | NaN | 1253.1309 | NaN | NaN | NaN | NaN | NaN | 139.2586 | NaN | 17.498 | NaN | 22.6392
10424.1292 | 752.569 | 632.2187 | 390.7046 | 392.7844 | 404.5253 | 593.3154 | 593.9181 | 576.1235 | NaN | NaN | NaN | 663.8749 | 1254.3997 | NaN | NaN | 1253.1293 | NaN | NaN | NaN | NaN | NaN | 122.5049 | NaN | 17.0172 | NaN | 22.2019
10425.1292 | 753.9573 | 632.2825 | 390.1395 | 393.0839 | 404.4484 | 592.9996 | 595.011 | 576.4594 | NaN | NaN | NaN | 671.7054 | 1254.3995 | NaN | NaN | 1253.1291 | NaN | NaN | NaN | NaN | NaN | 107.9214 | NaN | 16.9164 | NaN | 23.6188
10426.1292 | 755.3508 | 632.6367 | 389.8027 | 393.2739 | 404.3537 | 592.2913 | 595.3811 | 585.1769 | NaN | NaN | NaN | 686.2474 | 1254.3987 | NaN | NaN | 1253.1283 | NaN | NaN | NaN | NaN | NaN | 88.3149 | NaN | 16.4419 | NaN | 23.9361
10427.1292 | 755.1223 | 632.6415 | 390.0159 | 393.8664 | 404.4063 | 588.2501 | 593.5448 | 583.1205 | NaN | NaN | NaN | 708.8145 | 1254.3979 | NaN | NaN | 1253.1275 | NaN | NaN | NaN | NaN | NaN | 74.9947 | NaN | 17.7031 | NaN | 24.0617
10428.1292 | 753.658 | 631.4348 | 390.7136 | 393.8256 | 404.5704 | 585.4199 | 592.5363 | 583.0259 | NaN | NaN | NaN | 702.2064 | 1254.3967 | NaN | NaN | 1253.1263 | NaN | NaN | NaN | NaN | NaN | 54.8465 | NaN | 17.3677 | NaN | 23.7279
10429.1292 | 752.5552 | 631.3578 | 390.4382 | 394.0202 | 405.0025 | 584.0053 | 592.4867 | 582.0033 | NaN | NaN | NaN | 745.4043 | 1254.396 | NaN | NaN | 1253.1256 | NaN | NaN | NaN | NaN | NaN | 43.8262 | NaN | 18.1814 | NaN | 25.2673
10430.1292 | 750.7905 | 628.5397 | 390.789 | 394.0956 | 405.1406 | 588.1003 | 591.0063 | 580.6981 | NaN | NaN | NaN | 735.1236 | 1254.3959 | NaN | NaN | 1253.1255 | NaN | NaN | NaN | NaN | NaN | 32.3148 | NaN | 18.1133 | NaN | 23.9185
10431.1292 | 750.2731 | 628.2026 | 390.4666 | 394.0466 | 405.4796 | 586.3575 | 589.1822 | 577.0776 | NaN | NaN | NaN | 754.9455 | 1254.3946 | NaN | NaN | 1253.1242 | NaN | NaN | NaN | NaN | NaN | 22.8078 | NaN | 15.0599 | NaN | 24.0122
10432.1448 | 750.1822 | 628.7724 | 390.6049 | 394.1031 | 405.138 | 590.1193 | 588.3288 | 572.8259 | NaN | NaN | NaN | 721.6194 | 1254.3949 | NaN | NaN | 1253.1245 | NaN | NaN | NaN | NaN | NaN | -2.1615 | NaN | 17.2952 | NaN | 23.3465
10433.1292 | 750.1637 | 629.2629 | 390.9283 | 394.6878 | 404.8845 | 587.6106 | 586.8085 | 571.4372 | NaN | NaN | NaN | 688.0061 | 1254.3942 | NaN | NaN | 1253.1238 | NaN | NaN | NaN | NaN | NaN | -18.882 | NaN | 16.3801 | NaN | 23.9913
10434.1292 | 751.4691 | 629.8195 | 390.7833 | 394.4337 | 404.8777 | 583.812 | 586.7631 | 569.9436 | NaN | NaN | NaN | 723.6301 | 1254.3916 | NaN | NaN | 1253.1212 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 17.6654 | NaN | 22.1914
10435.1292 | 752.046 | 629.8546 | 391.3451 | 394.5542 | 404.7479 | 582.6065 | 585.8417 | 571.0315 | NaN | NaN | NaN | 746.2246 | 1254.3921 | NaN | NaN | 1253.1217 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 16.1233 | NaN | 24.1097
10436.1292 | 753.389 | 629.8809 | 391.5557 | 394.3796 | 405.076 | 578.5209 | 584.4782 | 572.2965 | NaN | NaN | NaN | 760.6398 | 1254.3919 | NaN | NaN | 1253.1215 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 17.6138 | NaN | 21.6746
10437.1292 | 753.5877 | 630.244 | 392.1959 | 394.6961 | 405.1078 | 578.2256 | 586.876 | 570.6767 | NaN | NaN | NaN | 753.5528 | 1254.3902 | NaN | NaN | 1253.1198 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 17.418 | NaN | 24.7518
10438.1292 | 753.7943 | 630.7766 | 392.6255 | 395.5079 | 405.074 | 579.2089 | 589.8525 | 572.4538 | NaN | NaN | NaN | 745.6054 | 1254.3902 | NaN | NaN | 1253.1198 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 16.7727 | NaN | 23.8804
10439.1292 | 755.8242 | 631.4891 | 393.0973 | 395.2708 | 404.8624 | 577.4564 | 589.6242 | 571.2887 | NaN | NaN | NaN | 759.106 | 1254.3892 | NaN | NaN | 1253.1188 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 17.3582 | NaN | 24.9512
10440.1292 | 757.6475 | 631.2324 | 392.7524 | 395.3791 | 404.8821 | 577.075 | 589.57 | 569.7494 | NaN | NaN | NaN | 766.1826 | 1254.3885 | NaN | NaN | 1253.1181 | NaN | NaN | NaN | NaN | NaN | 43.5324 | NaN | 18.6865 | NaN | 23.4267
10441.1292 | 758.8925 | 633.8875 | 393.2932 | 395.7429 | 405.1269 | 575.2574 | 588.7289 | 569.5212 | NaN | NaN | NaN | 770.2055 | 1254.3879 | NaN | NaN | 1253.1175 | NaN | NaN | NaN | NaN | NaN | 174.9566 | NaN | 18.4515 | NaN | 23.8753
10442.1292 | 757.8842 | 633.882 | 393.6701 | 396.9068 | 406.4865 | 575.6734 | 587.8227 | 568.7403 | NaN | NaN | NaN | 776.259 | 1254.3873 | NaN | NaN | 1253.1169 | NaN | NaN | NaN | NaN | NaN | 466.3554 | NaN | 15.9742 | NaN | 24.542
10443.1292 | 757.242 | 633.1806 | 393.7615 | 397.1828 | 407.2221 | 574.1415 | 589.3403 | 567.3457 | NaN | NaN | NaN | 795.0033 | 1254.3857 | NaN | NaN | 1253.1153 | NaN | NaN | NaN | NaN | NaN | 811.0343 | NaN | 17.5481 | NaN | 24.1655
10444.1292 | 755.6632 | 634.1482 | 393.7854 | 397.2844 | 407.5222 | 577.6392 | 594.0701 | 573.8097 | NaN | NaN | NaN | 809.9321 | 1254.3848 | NaN | NaN | 1253.1144 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 17.0541 | NaN | 23.7424
10445.1292 | 754.7954 | 635.3721 | 394.1217 | 398.4746 | 408.645 | 581.7719 | 595.7853 | 573.0299 | NaN | NaN | NaN | 789.9472 | 1254.3846 | NaN | NaN | 1253.1142 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 18.5067 | NaN | 23.5226
10446.1292 | 755.4249 | 635.091 | 393.649 | 398.3246 | 408.3819 | 583.9804 | 594.4052 | 571.1909 | NaN | NaN | NaN | 742.5422 | 1254.3834 | NaN | NaN | 1253.113 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 16.0553 | NaN | 24.3083
10447.1292 | 753.6431 | 635.0913 | 393.5102 | 398.4648 | 408.4416 | 584.7191 | 598.6376 | 575.3143 | NaN | NaN | NaN | 728.257 | 1254.3818 | NaN | NaN | 1253.1114 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.4329 | NaN | 25.4767
10448.1292 | 752.2836 | 635.8241 | 393.7957 | 398.2918 | 408.4776 | 587.4676 | 597.8428 | 577.162 | NaN | NaN | NaN | 713.7561 | 1254.382 | NaN | NaN | 1253.1116 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 17.3234 | NaN | 22.9026
10449.1292 | 751.8504 | 635.8034 | 395.0173 | 398.9156 | 408.7871 | 586.758 | 597.4478 | 575.5943 | NaN | NaN | NaN | 713.642 | 1254.3818 | NaN | NaN | 1253.1114 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 16.2448 | NaN | 23.1433
10450.1292 | 752.4639 | 635.7733 | 395.5119 | 399.0467 | 408.7755 | 588.6827 | 597.035 | 575.1293 | NaN | NaN | NaN | 723.9273 | 1254.3806 | NaN | NaN | 1253.1102 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.2961 | NaN | 21.6675
10451.1292 | 753.1052 | 636.5209 | 395.8942 | 399.1242 | 409.0715 | 588.5431 | 597.141 | 574.5453 | NaN | NaN | NaN | 747.7304 | 1254.3795 | NaN | NaN | 1253.1091 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 16.9695 | NaN | 24.021
10452.1292 | 753.1615 | 636.7058 | 396.6178 | 399.0779 | 408.9259 | 589.1509 | 598.6121 | 575.2396 | NaN | NaN | NaN | 733.3171 | 1254.3794 | NaN | NaN | 1253.109 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 16.5049 | NaN | 23.895
10453.1292 | 753.4134 | 637.2239 | 396.1943 | 399.1273 | 409.2132 | 589.5946 | 599.6036 | 578.0309 | NaN | NaN | NaN | 758.6794 | 1254.3788 | NaN | NaN | 1253.1085 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 17.8015 | NaN | 23.1056
10454.1292 | 752.715 | 637.0666 | 396.1363 | 398.5401 | 408.7479 | 589.4456 | 599.4337 | 578.9706 | NaN | NaN | NaN | 723.4653 | 1254.3792 | NaN | NaN | 1253.1088 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 18.0749 | NaN | 24.0465
10455.1292 | 750.7006 | 637.2528 | 396.715 | 398.4361 | 408.672 | 587.7981 | 598.7024 | 579.2659 | NaN | NaN | NaN | 743.2266 | 1254.3776 | NaN | NaN | 1253.1072 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 18.8858 | NaN | 24.007
10456.1292 | 750.048 | 637.2849 | 397.0445 | 398.4394 | 408.4052 | 593.1114 | 597.359 | 584.7692 | NaN | NaN | NaN | 751.2439 | 1254.3759 | NaN | NaN | 1253.1055 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 16.8627 | NaN | 23.337
10457.1292 | 748.6932 | 637.3588 | 396.8395 | 399.3722 | 409.1583 | 590.9974 | 598.3178 | 584.2447 | NaN | NaN | NaN | 748.8904 | 1254.3759 | NaN | NaN | 1253.1055 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 18.8836 | NaN | 23.5601
10458.1292 | 748.0572 | 636.4295 | 397.2962 | 399.2088 | 408.5956 | 591.4792 | 599.3315 | 581.0402 | NaN | NaN | NaN | 750.1584 | 1254.3747 | NaN | NaN | 1253.1043 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.8959 | NaN | 24.6819
10459.1292 | 747.2029 | 636.4191 | 398.4004 | 399.0013 | 408.3617 | 593.5402 | 600.4645 | 593.5672 | NaN | NaN | NaN | 729.973 | 1254.3744 | NaN | NaN | 1253.104 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 16.301 | NaN | 25.0588
10460.1292 | 746.5187 | 635.9751 | 398.1819 | 400.105 | 408.3712 | 591.7181 | 600.2247 | 608.1795 | NaN | NaN | NaN | 739.4827 | 1254.3728 | NaN | NaN | 1253.1024 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 18.2422 | NaN | 24.3997
10461.1292 | 745.1186 | 636.2979 | 397.9065 | 399.8654 | 408.2203 | 595.4442 | 600.6097 | 607.0896 | NaN | NaN | NaN | 757.1088 | 1254.3721 | NaN | NaN | 1253.1017 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 17.3482 | NaN | 24.4806
10462.1292 | 742.2464 | 635.9591 | 397.5832 | 399.5156 | 408.4405 | 599.0357 | 601.9569 | 599.7092 | NaN | NaN | NaN | 739.3792 | 1254.3722 | NaN | NaN | 1253.1019 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 17.2663 | NaN | 25.0879
10463.1292 | 741.2103 | 636.1004 | 397.7883 | 399.5806 | 408.8263 | 596.5361 | 613.9131 | 596.5144 | NaN | NaN | NaN | 708.1759 | 1254.3716 | NaN | NaN | 1253.1012 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 16.0927 | NaN | 23.9878
10464.1292 | 742.3674 | 636.2279 | 398.408 | 399.6452 | 409.4183 | 594.2952 | 610.6098 | 605.9386 | NaN | NaN | NaN | 681.0388 | 1254.3706 | NaN | NaN | 1253.1002 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 17.8989 | NaN | 23.6244
10465.1292 | 744.1943 | 635.3342 | 398.9928 | 399.8232 | 409.6397 | 591.2818 | 606.4744 | 606.2967 | NaN | NaN | NaN | 677.6271 | 1254.3692 | NaN | NaN | 1253.0989 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 18.1749 | NaN | 23.0581
10466.1292 | 743.3871 | 634.7287 | 399.0684 | 399.9838 | 409.9823 | 594.542 | 606.3123 | 610.7985 | NaN | NaN | NaN | 671.1364 | 1254.3697 | NaN | NaN | 1253.0993 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 16.4834 | NaN | 24.1447
10467.1292 | 742.9271 | 635.2547 | 399.5195 | 399.7906 | 410.3457 | 598.4232 | 617.4776 | 610.4259 | NaN | NaN | NaN | 675.8897 | 1254.3681 | NaN | NaN | 1253.0977 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.2897 | NaN | 24.1334
10468.1292 | 744.6126 | 636.691 | 399.1365 | 399.691 | 410.8285 | 597.0281 | 618.8246 | 608.2608 | NaN | NaN | NaN | 697.9771 | 1254.3673 | NaN | NaN | 1253.0969 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 16.213 | NaN | 23.1737
10469.1292 | 744.6189 | 636.4702 | 399.001 | 399.5655 | 410.7763 | 596.8654 | 616.6028 | 603.8625 | NaN | NaN | NaN | 668.2172 | 1254.3672 | NaN | NaN | 1253.0968 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 16.137 | NaN | 22.6118
10470.1292 | 745.6922 | 637.6054 | 398.7955 | 399.8523 | 410.565 | 596.3966 | 613.7826 | 605.9504 | NaN | NaN | NaN | 662.5 | 1254.3659 | NaN | NaN | 1253.0956 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 17.3182 | NaN | 22.6453
10471.1292 | 746.3931 | 637.2694 | 398.9244 | 400.1214 | 410.6587 | 599.2429 | 612.536 | 604.3782 | NaN | NaN | NaN | 668.2434 | 1254.3655 | NaN | NaN | 1253.0951 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.4789 | NaN | 23.7355
10472.1292 | 746.4233 | 635.8388 | 398.623 | 400.3723 | 410.7776 | 598.6155 | 608.6647 | 599.6881 | NaN | NaN | NaN | 684.7567 | 1254.3645 | NaN | NaN | 1253.0941 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 17.6208 | NaN | 23.109
10473.1292 | 745.9016 | 636.4839 | 398.7465 | 400.9121 | 411.0379 | 604.2149 | 614.7486 | 597.6208 | NaN | NaN | NaN | 702.9456 | 1254.3641 | NaN | NaN | 1253.0937 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 16.5506 | NaN | 22.7454
10474.1292 | 745.2052 | 635.3816 | 398.8802 | 400.7884 | 411.2262 | 605.8055 | 622.294 | 609.6427 | NaN | NaN | NaN | 682.1357 | 1254.3635 | NaN | NaN | 1253.0931 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.7881 | NaN | 23.6184
10475.1292 | 746.4582 | 635.4697 | 399.6463 | 400.7913 | 411.0093 | 612.6508 | 631.5748 | 605.9404 | NaN | NaN | NaN | 693.7528 | 1254.362 | NaN | NaN | 1253.0917 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 16.042 | NaN | 23.5537
10476.1292 | 746.8035 | 635.0437 | 400.0226 | 400.5504 | 410.979 | 611.0127 | 627.6685 | 605.409 | NaN | NaN | NaN | 716.639 | 1254.3614 | NaN | NaN | 1253.091 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 17.78 | NaN | 22.1654
10477.1292 | 745.9177 | 635.0657 | 399.6665 | 401.2739 | 411.2395 | 608.2109 | 623.0517 | 604.1636 | NaN | NaN | NaN | 731.0272 | 1254.36 | NaN | NaN | 1253.0897 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 16.0897 | NaN | 24.4224
10478.1292 | 744.8958 | 634.5751 | 400.2031 | 401.563 | 411.526 | 605.8046 | 618.4671 | 599.7526 | NaN | NaN | NaN | 745.0042 | 1254.3595 | NaN | NaN | 1253.0891 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.4169 | NaN | 21.5689
10479.1292 | 743.2244 | 634.5112 | 400.6136 | 401.5131 | 411.5391 | 601.1999 | 614.0792 | 594.7038 | NaN | NaN | NaN | 716.4162 | 1254.3587 | NaN | NaN | 1253.0883 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 16.8786 | NaN | 22.4822
10480.1292 | 741.8645 | 635.4927 | 401.0915 | 401.5134 | 411.7869 | 599.8277 | 612.4939 | 589.8247 | NaN | NaN | NaN | 703.4609 | 1254.358 | NaN | NaN | 1253.0877 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.3565 | NaN | 22.0852
10481.1292 | 740.8961 | 636.0894 | 401.4509 | 401.5964 | 412.0493 | 598.9589 | 611.485 | 588.9411 | NaN | NaN | NaN | 728.9921 | 1254.3581 | NaN | NaN | 1253.0877 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 16.6732 | NaN | 23.4265
10482.1292 | 741.7128 | 636.0834 | 401.7353 | 401.8544 | 412.6608 | 597.4827 | 614.3024 | 595.3334 | NaN | NaN | NaN | 703.3024 | 1254.3573 | NaN | NaN | 1253.087 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 17.537 | NaN | 24.4848
10483.1292 | 743.3236 | 637.0476 | 402.2904 | 402.0745 | 412.6026 | 596.1392 | 611.5196 | 595.0171 | NaN | NaN | NaN | 723.9175 | 1254.3565 | NaN | NaN | 1253.0861 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 17.2894 | NaN | 23.4064
10484.1292 | 743.5327 | 638.2679 | 403.0237 | 402.4429 | 412.9132 | 600.9169 | 609.2017 | 596.2168 | NaN | NaN | NaN | 747.3 | 1254.3559 | NaN | NaN | 1253.0856 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 17.4423 | NaN | 23.4525
10485.1292 | 743.1135 | 638.6593 | 402.8852 | 402.4588 | 413.0117 | 605.1497 | 612.0492 | 594.9902 | NaN | NaN | NaN | 740.7048 | 1254.3551 | NaN | NaN | 1253.0847 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.5958 | NaN | 23.9181
10486.1292 | 742.7059 | 638.7827 | 402.8624 | 403.1732 | 412.9046 | 606.7464 | 609.6327 | 594.2064 | NaN | NaN | NaN | 757.747 | 1254.3544 | NaN | NaN | 1253.084 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 17.8118 | NaN | 24.4167
10487.1292 | 742.8343 | 639.6551 | 403.4931 | 402.7836 | 413.103 | 607.1561 | 605.8154 | 588.8929 | NaN | NaN | NaN | 743.4329 | 1254.354 | NaN | NaN | 1253.0836 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.0344 | NaN | 22.9538
10488.1292 | 743.2233 | 638.7596 | 403.694 | 402.8251 | 413.2708 | 606.7106 | 604.4206 | 590.1749 | NaN | NaN | NaN | 758.4371 | 1254.3532 | NaN | NaN | 1253.0828 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 17.5259 | NaN | 24.8242
10489.1292 | 742.3202 | 638.7149 | 403.3265 | 403.2545 | 413.4522 | 602.8765 | 602.249 | 593.0159 | NaN | NaN | NaN | 772.4024 | 1254.353 | NaN | NaN | 1253.0827 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 16.4165 | NaN | 24.3012
10490.1292 | 743.0706 | 639.0145 | 403.1822 | 403.5936 | 413.9423 | 608.8636 | 604.1654 | 592.1325 | NaN | NaN | NaN | 723.6051 | 1254.3512 | NaN | NaN | 1253.0808 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.4236 | NaN | 22.6033
10491.1292 | 742.7493 | 639.6331 | 404.5382 | 403.7203 | 414.1001 | 605.1085 | 602.5692 | 588.4225 | NaN | NaN | NaN | 685.1775 | 1254.3511 | NaN | NaN | 1253.0808 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.5482 | NaN | 23.5542
10492.1292 | 742.2127 | 639.2558 | 404.6322 | 403.9021 | 414.338 | 603.9794 | 602.2286 | 597.7711 | NaN | NaN | NaN | 682.7969 | 1254.3501 | NaN | NaN | 1253.0797 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.6626 | NaN | 22.9811
10493.1292 | 742.0805 | 640.1384 | 403.8616 | 404.2427 | 414.3711 | 604.4361 | 603.061 | 598.4529 | NaN | NaN | NaN | 712.5417 | 1254.3506 | NaN | NaN | 1253.0802 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.2081 | NaN | 23.6692
10494.1292 | 742.784 | 640.06 | 403.8758 | 404.5999 | 414.4665 | 604.1196 | 604.7777 | 600.7903 | NaN | NaN | NaN | 730.0699 | 1254.3487 | NaN | NaN | 1253.0784 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.7578 | NaN | 22.5576
10495.1292 | 743.1158 | 640.1088 | 404.0078 | 404.6249 | 414.6509 | 603.1001 | 603.5239 | 615.4858 | NaN | NaN | NaN | 718.0708 | 1254.3478 | NaN | NaN | 1253.0775 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 16.8706 | NaN | 23.324
10496.1292 | 743.2058 | 639.8984 | 404.1665 | 405.3064 | 415.5004 | 602.5525 | 603.1019 | 619.8649 | NaN | NaN | NaN | 688.0884 | 1254.3475 | NaN | NaN | 1253.0772 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 17.0728 | NaN | 22.8782
10497.1292 | 743.3852 | 639.8165 | 404.6559 | 405.4106 | 415.5228 | 601.0251 | 600.9473 | 614.7339 | NaN | NaN | NaN | 716.816 | 1254.3466 | NaN | NaN | 1253.0762 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 17.1053 | NaN | 23.0892
10498.1292 | 744.7249 | 640.0654 | 405.192 | 405.4717 | 415.6189 | 604.2281 | 600.508 | 612.4836 | NaN | NaN | NaN | 741.3889 | 1254.3463 | NaN | NaN | 1253.076 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 17.6468 | NaN | 23.404
10499.1292 | 744.2325 | 639.6603 | 404.6215 | 405.7593 | 415.4324 | 614.526 | 612.4582 | 622.9927 | NaN | NaN | NaN | 722.5773 | 1254.3447 | NaN | NaN | 1253.0743 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.0056 | NaN | 22.6452
10500.1292 | 743.0615 | 640.2692 | 404.893 | 405.8849 | 416.2253 | 627.5392 | 619.5242 | 623.7664 | NaN | NaN | NaN | 710.8039 | 1254.3437 | NaN | NaN | 1253.0734 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.1973 | NaN | 22.8218
10501.1292 | 741.9422 | 641.1733 | 405.9802 | 405.9802 | 416.145 | 624.1111 | 614.4127 | 621.6345 | NaN | NaN | NaN | 734.1108 | 1254.3436 | NaN | NaN | 1253.0733 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.9175 | NaN | 24.1314
10502.1292 | 741.2594 | 640.5155 | 406.4098 | 406.239 | 416.6728 | 620.5562 | 611.253 | 628.1235 | NaN | NaN | NaN | 749.7774 | 1254.3422 | NaN | NaN | 1253.0718 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.1789 | NaN | 22.0148
10503.1292 | 740.4819 | 640.467 | 406.8502 | 406.5597 | 417.265 | 617.1954 | 606.388 | 627.2766 | NaN | NaN | NaN | 735.795 | 1254.3419 | NaN | NaN | 1253.0716 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.7217 | NaN | 24.4052
10504.1292 | 740.3711 | 640.2752 | 406.8311 | 406.9446 | 417.2734 | 619.2144 | 602.257 | 618.0065 | NaN | NaN | NaN | 747.9866 | 1254.3402 | NaN | NaN | 1253.0698 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 16.0613 | NaN | 24.4292
10505.1292 | 740.9505 | 640.2983 | 406.3259 | 407.2209 | 417.4099 | 613.6787 | 600.3038 | 611.358 | NaN | NaN | NaN | 758.1574 | 1254.3403 | NaN | NaN | 1253.0699 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 17.0307 | NaN | 23.2438
10506.1292 | 741.8357 | 639.7192 | 406.7535 | 407.2994 | 417.2381 | 618.1288 | 600.4183 | 605.1877 | NaN | NaN | NaN | 768.9019 | 1254.3395 | NaN | NaN | 1253.0691 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.7076 | NaN | 24.2879
10507.1292 | 745.7816 | 640.8636 | 407.4709 | 407.7593 | 417.2115 | 618.2681 | 601.1344 | 605.0762 | NaN | NaN | NaN | 774.6776 | 1254.3378 | NaN | NaN | 1253.0675 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 17.3289 | NaN | 23.4055
10508.1292 | 747.8723 | 641.2541 | 407.6842 | 407.7943 | 417.3393 | 619.7743 | 602.5996 | 603.9624 | NaN | NaN | NaN | 727.1051 | 1254.3376 | NaN | NaN | 1253.0672 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 17.7391 | NaN | 23.1131
10509.1292 | 748.3561 | 641.7152 | 408.3105 | 407.2999 | 417.1011 | 627.9867 | 603.2354 | 600.642 | NaN | NaN | NaN | 694.1383 | 1254.3374 | NaN | NaN | 1253.067 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 17.4716 | NaN | 21.0839
10510.1292 | 751.2465 | 641.9189 | 408.3988 | 407.1611 | 416.6368 | 633.0004 | 602.5198 | 597.3405 | NaN | NaN | NaN | 684.4026 | 1254.3363 | NaN | NaN | 1253.0659 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.8174 | NaN | 23.6083
10511.1292 | 753.2281 | 640.9595 | 409.1418 | 407.4465 | 416.5361 | 635.4842 | 602.0885 | 598.8423 | NaN | NaN | NaN | 692.1592 | 1254.3367 | NaN | NaN | 1253.0663 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 17.4622 | NaN | 22.8336
10512.1292 | 752.5419 | 640.519 | 408.9641 | 407.8067 | 417.0063 | 637.9956 | 606.9683 | 601.0099 | NaN | NaN | NaN | 710.4446 | 1254.3354 | NaN | NaN | 1253.065 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 17.2209 | NaN | 23.3646
10513.1292 | 751.0684 | 641.7628 | 408.8342 | 407.9309 | 416.8717 | 634.9025 | 608.7762 | 607.1188 | NaN | NaN | NaN | 685.0084 | 1254.3347 | NaN | NaN | 1253.0644 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 16.8338 | NaN | 24.6616
10514.1292 | 751.0569 | 641.5255 | 409.3459 | 407.9918 | 416.9463 | 631.5282 | 609.8948 | 603.2628 | NaN | NaN | NaN | 699.3094 | 1254.3337 | NaN | NaN | 1253.0633 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 17.9296 | NaN | 24.8535
10515.1292 | 751.5638 | 641.2067 | 408.689 | 408.3488 | 416.7198 | 628.079 | 608.4641 | 601.3164 | NaN | NaN | NaN | 668.0985 | 1254.3324 | NaN | NaN | 1253.062 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 16.3493 | NaN | 23.4014
10516.1292 | 753.6414 | 641.1439 | 409.0869 | 408.3286 | 416.782 | 624.2016 | 604.7276 | 598.6959 | NaN | NaN | NaN | 672.6328 | 1254.3326 | NaN | NaN | 1253.0622 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.3733 | NaN | 22.8867
10517.1292 | 753.2627 | 640.8295 | 409.0834 | 408.7353 | 416.7228 | 625.0266 | 608.4071 | 603.9461 | NaN | NaN | NaN | 665.2023 | 1254.3311 | NaN | NaN | 1253.0607 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 16.3053 | NaN | 24.4443
10518.1292 | 753.1659 | 639.9541 | 409.3209 | 408.786 | 416.6416 | 622.6772 | 608.0798 | 607.7905 | NaN | NaN | NaN | 662.3277 | 1254.3302 | NaN | NaN | 1253.0599 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.4339 | NaN | 24.1992
10519.1292 | 753.7987 | 640.4868 | 409.5684 | 408.7435 | 416.937 | 627.4321 | 607.7634 | 604.3792 | NaN | NaN | NaN | 702.4944 | 1254.3293 | NaN | NaN | 1253.0589 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 16.7292 | NaN | 23.3471
10520.1292 | 754.1414 | 640.6979 | 409.1946 | 408.7753 | 417.2626 | 635.5266 | 611.5262 | 606.8423 | NaN | NaN | NaN | 706.0874 | 1254.3298 | NaN | NaN | 1253.0594 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.0134 | NaN | 23.2889
10521.1292 | 752.3761 | 642.2497 | 410.0975 | 409.5061 | 417.7357 | 633.325 | 613.2168 | 605.0959 | NaN | NaN | NaN | 723.1886 | 1254.3284 | NaN | NaN | 1253.0581 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 16.9535 | NaN | 22.8464
10522.1292 | 750.7846 | 642.4159 | 410.1791 | 409.8422 | 418.3362 | 637.8049 | 613.9219 | 608.2874 | NaN | NaN | NaN | 729.1048 | 1254.3278 | NaN | NaN | 1253.0574 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 17.3014 | NaN | 24.738
10523.1292 | 751.4809 | 642.9532 | 409.9253 | 410.5208 | 419.1108 | 640.6099 | 622.4751 | 625.4551 | NaN | NaN | NaN | 745.9333 | 1254.3269 | NaN | NaN | 1253.0566 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 17.1099 | NaN | 24.0098
10524.1292 | 750.8765 | 641.6105 | 409.5325 | 410.4528 | 419.2349 | 631.7188 | 617.7554 | 628.4114 | NaN | NaN | NaN | 775.136 | 1254.3271 | NaN | NaN | 1253.0567 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.8818 | NaN | 24.1406
10525.1292 | 749.825 | 640.8093 | 409.6574 | 409.9942 | 419.1469 | 635.6578 | 616.9092 | 622.6594 | NaN | NaN | NaN | 764.696 | 1254.3256 | NaN | NaN | 1253.0553 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 16.8751 | NaN | 24.049
10526.1292 | 747.7973 | 640.625 | 410.4716 | 410.0217 | 419.6604 | 638.7701 | 618.8979 | 621.5581 | NaN | NaN | NaN | 752.8687 | 1254.3248 | NaN | NaN | 1253.0544 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 16.1338 | NaN | 24.2568
10527.1292 | 749.6539 | 641.3267 | 411.2561 | 410.0628 | 419.738 | 638.5412 | 616.3747 | 613.4314 | NaN | NaN | NaN | 726.3587 | 1254.3235 | NaN | NaN | 1253.0532 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.8732 | NaN | 21.9424
10528.1292 | 749.3511 | 640.6888 | 411.4106 | 410.1388 | 419.6012 | 638.6726 | 616.0623 | 614.2131 | NaN | NaN | NaN | 734.6784 | 1254.3233 | NaN | NaN | 1253.053 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 16.958 | NaN | 23.5365
10529.1292 | 748.5629 | 640.2207 | 411.1353 | 410.4077 | 419.4476 | 633.0956 | 621.9822 | 613.9556 | NaN | NaN | NaN | 755.1526 | 1254.3223 | NaN | NaN | 1253.052 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 17.6898 | NaN | 23.5888
10530.1292 | 747.1666 | 640.0355 | 411.2814 | 410.2291 | 419.6507 | 631.7458 | 630.5344 | 627.6194 | NaN | NaN | NaN | 729.2092 | 1254.3224 | NaN | NaN | 1253.052 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.5452 | NaN | 23.9397
10531.1292 | 745.4731 | 640.9542 | 411.6542 | 410.5957 | 420.5888 | 631.6513 | 629.1498 | 634.3271 | NaN | NaN | NaN | 691.6763 | 1254.3202 | NaN | NaN | 1253.0499 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 18.4576 | NaN | 23.4999
10532.1292 | 742.8682 | 640.5566 | 411.4273 | 410.7122 | 421.1821 | 639.031 | 626.5014 | 634.9143 | NaN | NaN | NaN | 673.0431 | 1254.3204 | NaN | NaN | 1253.0501 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.7854 | NaN | 22.1334
10533.1292 | 741.7963 | 639.5992 | 411.3519 | 410.5188 | 421.0115 | 646.5537 | 628.1682 | 630.845 | NaN | NaN | NaN | 692.8498 | 1254.3201 | NaN | NaN | 1253.0497 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.3889 | NaN | 24.544
10534.1292 | 740.3836 | 639.0226 | 411.9298 | 410.9967 | 421.7793 | 649.7832 | 639.1573 | 631.9958 | NaN | NaN | NaN | 676.5436 | 1254.3189 | NaN | NaN | 1253.0486 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.6355 | NaN | 22.9908
10535.1292 | 740.5891 | 639.1271 | 411.9329 | 411.4689 | 422.3849 | 648.2442 | 633.3564 | 629.6133 | NaN | NaN | NaN | 712.945 | 1254.3186 | NaN | NaN | 1253.0483 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 18.0362 | NaN | 25.0705
10536.1292 | 743.1217 | 639.6197 | 411.9341 | 411.3717 | 422.6315 | 647.7332 | 628.0105 | 622.1925 | NaN | NaN | NaN | 740.6765 | 1254.3176 | NaN | NaN | 1253.0473 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.582 | NaN | 22.0731
10537.1292 | 743.2278 | 639.4108 | 413.0846 | 411.631 | 422.3968 | 649.6073 | 623.6624 | 619.9941 | NaN | NaN | NaN | 760.5928 | 1254.317 | NaN | NaN | 1253.0466 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.4614 | NaN | 24.0255
10538.1292 | 741.5957 | 639.9626 | 413.1843 | 412.0058 | 422.5959 | 655.8889 | 630.9553 | 619.2411 | NaN | NaN | NaN | 760.37 | 1254.3168 | NaN | NaN | 1253.0464 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 17.0842 | NaN | 23.0992
10539.1292 | 739.311 | 639.6027 | 413.1956 | 411.9909 | 422.7651 | 653.8859 | 624.4816 | 631.7904 | NaN | NaN | NaN | 767.2028 | 1254.3152 | NaN | NaN | 1253.0448 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.2304 | NaN | 23.8757
10540.1292 | 738.2098 | 640.0962 | 413.6122 | 411.8536 | 422.7883 | 651.4527 | 620.9103 | 621.4089 | NaN | NaN | NaN | 773.8926 | 1254.3157 | NaN | NaN | 1253.0454 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 16.0519 | NaN | 23.4358
10541.1292 | 738.4086 | 639.8923 | 413.3519 | 412.0059 | 422.6545 | 643.0837 | 616.8184 | 616.3533 | NaN | NaN | NaN | 789.1967 | 1254.3139 | NaN | NaN | 1253.0435 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 16.24 | NaN | 22.313
10542.1292 | 739.2646 | 639.1708 | 413.3294 | 412.2962 | 422.826 | 636.0497 | 613.6513 | 610.9123 | NaN | NaN | NaN | 800.8714 | 1254.3137 | NaN | NaN | 1253.0434 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.9338 | NaN | 25.622
10543.1292 | 739.8569 | 639.3099 | 413.3836 | 412.467 | 422.9353 | 639.6262 | 614.0483 | 609.0053 | NaN | NaN | NaN | 803.653 | 1254.3128 | NaN | NaN | 1253.0425 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.7915 | NaN | 22.8631
10544.1448 | 739.1153 | 639.2794 | 413.0902 | 412.0046 | 422.8562 | 637.7702 | 616.0987 | 605.469 | NaN | NaN | NaN | 806.672 | 1254.3118 | NaN | NaN | 1253.0415 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.6337 | NaN | 23.8368
10545.1448 | 737.4431 | 640.3253 | 413.3101 | 411.7323 | 422.7385 | 639.0951 | 620.4949 | 614.9584 | NaN | NaN | NaN | 780.5392 | 1254.3109 | NaN | NaN | 1253.0405 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 16.9096 | NaN | 22.9847
10546.1292 | 736.2017 | 639.8099 | 413.7398 | 411.984 | 422.9986 | 635.9367 | 619.4128 | 624.2955 | NaN | NaN | NaN | 736.1803 | 1254.3115 | NaN | NaN | 1253.0412 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 16.0275 | NaN | 22.5791
10547.1292 | 736.4332 | 638.576 | 413.2761 | 412.7312 | 423.0162 | 628.8212 | 613.8963 | 624.1772 | NaN | NaN | NaN | 715.7601 | 1254.3101 | NaN | NaN | 1253.0398 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.8225 | NaN | 23.2424
10548.1448 | 736.529 | 638.3685 | 413.7799 | 412.9875 | 422.8125 | 628.8538 | 611.8785 | 624.9657 | NaN | NaN | NaN | 737.3668 | 1254.3093 | NaN | NaN | 1253.0389 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 16.6612 | NaN | 23.1489
10549.1448 | 735.2115 | 638.148 | 414.0655 | 413.0969 | 422.807 | 630.3971 | 617.8591 | 630.2292 | NaN | NaN | NaN | 700.4982 | 1254.3096 | NaN | NaN | 1253.0393 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.3622 | NaN | 24.3528
10550.1448 | 734.725 | 638.7794 | 413.7 | 413.6344 | 423.1545 | 628.711 | 626.2903 | 627.9369 | NaN | NaN | NaN | 690.5522 | 1254.3081 | NaN | NaN | 1253.0377 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 16.0894 | NaN | 22.322
10551.1292 | 733.2556 | 638.4715 | 413.5422 | 413.8905 | 423.9235 | 629.8427 | 619.9313 | 621.8003 | NaN | NaN | NaN | 684.2918 | 1254.307 | NaN | NaN | 1253.0366 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 16.4183 | NaN | 24.1588
10552.1292 | 733.1102 | 638.942 | 414.1825 | 413.9511 | 423.792 | 627.0497 | 615.6157 | 624.7913 | NaN | NaN | NaN | 675.0009 | 1254.3067 | NaN | NaN | 1253.0363 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 16.1893 | NaN | 23.3145
10553.1292 | 733.0602 | 638.7351 | 414.5872 | 413.6188 | 423.7575 | 624.7924 | 615.6381 | 622.4061 | NaN | NaN | NaN | 648.8505 | 1254.3059 | NaN | NaN | 1253.0356 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.9441 | NaN | 22.5838
10554.1292 | 732.5599 | 639.0157 | 414.7309 | 414.7337 | 423.7683 | 623.3933 | 613.8367 | 628.5838 | NaN | NaN | NaN | 633.3021 | 1254.3056 | NaN | NaN | 1253.0353 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 16.1439 | NaN | 24.0521
10555.1292 | 732.02 | 639.1964 | 414.7663 | 414.703 | 424.431 | 621.5778 | 610.3638 | 630.8341 | NaN | NaN | NaN | 662.2911 | 1254.3043 | NaN | NaN | 1253.0339 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 16.2612 | NaN | 25.012
10556.1292 | 733.0107 | 640.1447 | 415.1583 | 415.155 | 424.7874 | 619.9761 | 613.2242 | 647.3347 | NaN | NaN | NaN | 689.8025 | 1254.3033 | NaN | NaN | 1253.0329 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.2015 | NaN | 23.1779
10557.1292 | 733.4487 | 640.6965 | 416.2054 | 415.6456 | 425.3771 | 620.2785 | 614.9437 | 644.1169 | NaN | NaN | NaN | 714.0351 | 1254.3025 | NaN | NaN | 1253.0322 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 16.4229 | NaN | 22.9053
10558.1292 | 733.3256 | 640.4534 | 416.1076 | 416.2807 | 426.1148 | 622.0164 | 617.9451 | 639.0203 | NaN | NaN | NaN | 706.28 | 1254.302 | NaN | NaN | 1253.0317 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.74 | NaN | 23.1744
10559.1292 | 732.8609 | 640.7338 | 417.2908 | 416.7668 | 426.4775 | 628.1194 | 619.304 | 630.6649 | NaN | NaN | NaN | 734.5664 | 1254.3029 | NaN | NaN | 1253.0326 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 16.4078 | NaN | 23.2118
10560.1292 | 735.541 | 640.3342 | 416.4834 | 416.515 | 426.4927 | 627.1875 | 631.6118 | 632.6109 | NaN | NaN | NaN | 760.6121 | 1254.3012 | NaN | NaN | 1253.0309 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 16.2111 | NaN | 23.7404
10561.1292 | 736.219 | 640.5875 | 416.5339 | 416.3205 | 426.5593 | 631.0577 | 634.2077 | 641.2053 | NaN | NaN | NaN | 749.5336 | 1254.3003 | NaN | NaN | 1253.03 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 16.0083 | NaN | 22.3448
10562.1292 | 738.3382 | 640.8959 | 416.8818 | 416.7703 | 427.2397 | 636.5084 | 636.6412 | 653.0731 | NaN | NaN | NaN | 742.1591 | 1254.2993 | NaN | NaN | 1253.0289 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.8422 | NaN | 22.3701
10563.1292 | 740.9976 | 642.3915 | 416.5892 | 417.118 | 427.5459 | 641.45 | 637.6751 | 646.3313 | NaN | NaN | NaN | 730.5196 | 1254.2989 | NaN | NaN | 1253.0285 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.0733 | NaN | 23.748
10564.1292 | 740.9965 | 642.4489 | 417.0688 | 417.8526 | 428.3564 | 644.8206 | 633.3791 | 636.3467 | NaN | NaN | NaN | 721.7466 | 1254.2987 | NaN | NaN | 1253.0284 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.904 | NaN | 23.8725
10565.1292 | 742.6608 | 642.9415 | 417.2881 | 418.2479 | 428.5244 | 642.2058 | 630.8826 | 631.421 | NaN | NaN | NaN | 735.7861 | 1254.2973 | NaN | NaN | 1253.027 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.8019 | NaN | 22.9308
10566.1292 | 746.2828 | 643.2977 | 417.4132 | 418.589 | 428.9113 | 636.9939 | 627.067 | 636.5845 | NaN | NaN | NaN | 728.676 | 1254.2974 | NaN | NaN | 1253.027 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.3365 | NaN | 23.4813
10567.1292 | 748.6995 | 643.5468 | 417.3112 | 418.9638 | 429.1347 | 638.3397 | 624.6053 | 635.1288 | NaN | NaN | NaN | 739.0052 | 1254.2966 | NaN | NaN | 1253.0262 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.4531 | NaN | 23.2666
10568.1292 | 746.053 | 642.8419 | 417.5673 | 419.2608 | 428.839 | 640.4469 | 626.8299 | 630.0843 | NaN | NaN | NaN | 732.3855 | 1254.2952 | NaN | NaN | 1253.0248 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.5665 | NaN | 23.8176
10569.1292 | 744.1784 | 642.7943 | 417.7238 | 419.8347 | 429.4866 | 645.7748 | 626.9981 | 628.1786 | NaN | NaN | NaN | 719.2522 | 1254.2946 | NaN | NaN | 1253.0243 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 16.4451 | NaN | 21.8253
10570.1292 | 744.6999 | 642.2927 | 418.2579 | 420.398 | 429.9342 | 645.0216 | 639.5353 | 623.7258 | NaN | NaN | NaN | 705.8746 | 1254.2942 | NaN | NaN | 1253.0239 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.5861 | NaN | 23.5665
10571.1292 | 746.7562 | 642.6724 | 418.2098 | 420.9035 | 430.6389 | 649.5315 | 635.3139 | 623.3912 | NaN | NaN | NaN | 705.7901 | 1254.2925 | NaN | NaN | 1253.0221 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.7246 | NaN | 22.0655
10572.1292 | 745.6329 | 643.0405 | 420.1993 | 421.0695 | 431.3249 | 655.4533 | 633.3869 | 625.4821 | NaN | NaN | NaN | 704.9769 | 1254.293 | NaN | NaN | 1253.0227 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.728 | NaN | 24.1377
10573.1292 | 743.1025 | 644.1925 | 420.3498 | 420.852 | 431.5888 | 658.3968 | 630.42 | 622.8173 | NaN | NaN | NaN | 721.8642 | 1254.2918 | NaN | NaN | 1253.0215 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.9873 | NaN | 24.3387
10574.1292 | 741.3352 | 644.0269 | 421.1441 | 421.0322 | 431.781 | 657.4445 | 632.4411 | 633.3806 | NaN | NaN | NaN | 693.1763 | 1254.2913 | NaN | NaN | 1253.021 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 17.0047 | NaN | 23.6744
10575.1292 | 741.1192 | 643.6196 | 420.3692 | 421.0015 | 431.5686 | 654.9522 | 648.8774 | 636.3521 | NaN | NaN | NaN | 662.0964 | 1254.2896 | NaN | NaN | 1253.0193 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 16.0263 | NaN | 23.2756
10576.1292 | 743.4526 | 644.588 | 420.5573 | 420.9543 | 431.8121 | 656.4112 | 648.4316 | 636.917 | NaN | NaN | NaN | 640.5868 | 1254.2898 | NaN | NaN | 1253.0194 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.9336 | NaN | 23.5983
10577.1292 | 745.6335 | 644.8285 | 420.6951 | 421.1083 | 431.767 | 662.1469 | 643.0477 | 633.788 | NaN | NaN | NaN | 670.431 | 1254.2891 | NaN | NaN | 1253.0188 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.6931 | NaN | 22.7851
10578.1292 | 747.4765 | 645.1068 | 421.6908 | 421.1286 | 431.7398 | 657.0236 | 640.1218 | 630.4362 | NaN | NaN | NaN | 688.2654 | 1254.2892 | NaN | NaN | 1253.0189 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.2113 | NaN | 22.8323
10579.1292 | 747.6244 | 645.3519 | 421.6476 | 421.391 | 432.1105 | 654.9008 | 637.7377 | 628.6661 | NaN | NaN | NaN | 678.363 | 1254.2871 | NaN | NaN | 1253.0168 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.5881 | NaN | 23.5352
10580.1292 | 745.7434 | 645.3861 | 421.6944 | 421.5206 | 432.153 | 660.9157 | 635.7063 | 628.7736 | NaN | NaN | NaN | 686.921 | 1254.2875 | NaN | NaN | 1253.0172 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.6768 | NaN | 23.0198
10581.1292 | 745.4713 | 645.1754 | 421.9766 | 421.7112 | 431.9136 | 667.5042 | 634.6127 | 626.5362 | NaN | NaN | NaN | 690.5446 | 1254.2869 | NaN | NaN | 1253.0166 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 16.1458 | NaN | 23.5646
10582.1292 | 746.5127 | 645.5116 | 421.6824 | 421.7954 | 431.9035 | 670.3834 | 638.3999 | 623.7689 | NaN | NaN | NaN | 659.5753 | 1254.2864 | NaN | NaN | 1253.0161 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.6532 | NaN | 23.0572
10583.1292 | 745.5441 | 645.6937 | 422.2755 | 421.8333 | 432.0844 | 672.5278 | 636.7742 | 625.0343 | NaN | NaN | NaN | 663.1441 | 1254.2846 | NaN | NaN | 1253.0143 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.0669 | NaN | 24.7997
10584.1292 | 747.0052 | 645.7693 | 422.6497 | 421.8847 | 432.6223 | 669.7996 | 633.0964 | 621.0547 | NaN | NaN | NaN | 656.1449 | 1254.2839 | NaN | NaN | 1253.0136 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.8644 | NaN | 20.7833
10585.1292 | 748.3173 | 646.7684 | 422.889 | 422.9715 | 433.9049 | 666.949 | 633.601 | 620.1546 | NaN | NaN | NaN | 678.3463 | 1254.2839 | NaN | NaN | 1253.0136 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.8281 | NaN | 22.851
10586.1292 | 748.5012 | 646.1749 | 423.7421 | 423.5517 | 434.0595 | 670.1332 | 635.3348 | 619.188 | NaN | NaN | NaN | 701.353 | 1254.2835 | NaN | NaN | 1253.0132 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.4338 | NaN | 22.5259
10587.1292 | 747.7532 | 645.0473 | 424.2949 | 424.148 | 434.4538 | 669.978 | 637.3597 | 618.5396 | NaN | NaN | NaN | 696.5272 | 1254.2812 | NaN | NaN | 1253.0109 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.9152 | NaN | 22.8656
10588.1292 | 746.3773 | 644.4515 | 424.4004 | 424.1281 | 435.0514 | 676.4052 | 637.6216 | 615.3089 | NaN | NaN | NaN | 675.2276 | 1254.2811 | NaN | NaN | 1253.0107 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.8568 | NaN | 22.5294
10589.1292 | 745.6424 | 644.2754 | 423.7513 | 424.3196 | 435.3052 | 674.8717 | 640.686 | 610.6491 | NaN | NaN | NaN | 701.3677 | 1254.2816 | NaN | NaN | 1253.0113 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 16.539 | NaN | 23.465
10590.1292 | 745.1961 | 644.957 | 424.2809 | 424.0846 | 435.4136 | 678.8098 | 639.0414 | 609.0083 | NaN | NaN | NaN | 693.4508 | 1254.2805 | NaN | NaN | 1253.0102 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.453 | NaN | 23.1282
10591.1292 | 749.5967 | 645.7688 | 424.0883 | 424.4896 | 435.954 | 677.5223 | 638.2148 | 620.4033 | NaN | NaN | NaN | 699.5821 | 1254.2788 | NaN | NaN | 1253.0085 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 16.9476 | NaN | 21.8577
10592.1292 | 752.8871 | 646.3197 | 423.8699 | 424.6208 | 436.0048 | 671.8045 | 635.7359 | 617.8361 | NaN | NaN | NaN | 704.9009 | 1254.2788 | NaN | NaN | 1253.0084 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 16.5453 | NaN | 24.4148
10593.1292 | 752.9559 | 646.0684 | 424.8834 | 424.7614 | 435.631 | 667.9043 | 638.1852 | 621.8574 | NaN | NaN | NaN | 702.7728 | 1254.2771 | NaN | NaN | 1253.0067 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 16.4836 | NaN | 23.8328
10594.1292 | 751.7869 | 646.6016 | 425.917 | 425.3317 | 436.0268 | 671.2949 | 640.7816 | 618.0789 | NaN | NaN | NaN | 684.974 | 1254.2776 | NaN | NaN | 1253.0073 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.8864 | NaN | 23.0989
10595.1292 | 750.8834 | 647.4609 | 425.7966 | 425.7642 | 436.5021 | 670.4691 | 642.2206 | 616.3709 | NaN | NaN | NaN | 666.9004 | 1254.2752 | NaN | NaN | 1253.0049 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.7504 | NaN | 22.666
10596.1292 | 750.2937 | 646.6577 | 426.0219 | 426.2521 | 436.4193 | 669.9467 | 647.6094 | 617.4853 | NaN | NaN | NaN | 676.2676 | 1254.2755 | NaN | NaN | 1253.0052 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 17.7188 | NaN | 23.3958
10597.1292 | 749.4984 | 648.0494 | 427.1827 | 426.9055 | 436.9034 | 675.5758 | 652.0963 | 619.1148 | NaN | NaN | NaN | 661.5821 | 1254.2745 | NaN | NaN | 1253.0041 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.8683 | NaN | 22.4679
10598.1292 | 748.6211 | 648.3043 | 427.399 | 426.7831 | 436.8989 | 674.2537 | 649.0904 | 627.4346 | NaN | NaN | NaN | 678.5475 | 1254.2731 | NaN | NaN | 1253.0028 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.9554 | NaN | 22.5036
10599.1292 | 746.7578 | 648.1702 | 427.5559 | 427.1742 | 437.0116 | 674.1167 | 653.0971 | 635.5723 | NaN | NaN | NaN | 686.3695 | 1254.2735 | NaN | NaN | 1253.0031 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 16.2754 | NaN | 22.4299
10600.1292 | 745.2257 | 649.0412 | 428.1438 | 427.3175 | 437.3043 | 678.054 | 660.4372 | 629.2284 | NaN | NaN | NaN | 695.7193 | 1254.2732 | NaN | NaN | 1253.0029 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.5038 | NaN | 22.1256
10601.1292 | 745.3242 | 649.189 | 428.5415 | 427.6741 | 438.195 | 676.4976 | 660.7827 | 633.6486 | NaN | NaN | NaN | 696.9121 | 1254.2714 | NaN | NaN | 1253.0011 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 16.0356 | NaN | 24.4856
10602.1292 | 747.1901 | 649.8963 | 428.4215 | 427.6574 | 438.8249 | 673.0581 | 655.0478 | 643.1675 | NaN | NaN | NaN | 688.2415 | 1254.272 | NaN | NaN | 1253.0017 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.7933 | NaN | 23.5713
10603.1292 | 746.8969 | 650.3165 | 428.5982 | 427.6977 | 438.8252 | 668.7068 | 657.5177 | 643.5013 | NaN | NaN | NaN | 700.5369 | 1254.2708 | NaN | NaN | 1253.0005 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.3035 | NaN | 22.473
10604.1292 | 745.9182 | 649.8417 | 429.3274 | 427.5827 | 438.6252 | 665.2974 | 651.0362 | 649.0812 | NaN | NaN | NaN | 722.0999 | 1254.2697 | NaN | NaN | 1252.9994 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 16.1938 | NaN | 24.6982
10605.1292 | 747.3777 | 650.1431 | 429.7972 | 427.2904 | 438.9906 | 666.5296 | 659.8403 | 650.7148 | NaN | NaN | NaN | 750.4445 | 1254.2683 | NaN | NaN | 1252.998 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.6781 | NaN | 23.237
10606.1292 | 748.4824 | 651.4502 | 429.9874 | 427.9887 | 439.1661 | 666.2245 | 653.2119 | 642.4678 | NaN | NaN | NaN | 765.3957 | 1254.2691 | NaN | NaN | 1252.9988 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.7884 | NaN | 23.4965
10607.1292 | 748.7546 | 652.0821 | 429.5858 | 428.3053 | 439.5094 | 660.5852 | 647.741 | 638.8291 | NaN | NaN | NaN | 772.4788 | 1254.2671 | NaN | NaN | 1252.9967 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.5486 | NaN | 23.0869
10608.1292 | 749.0895 | 651.8978 | 430.1788 | 428.527 | 439.9281 | 657.7093 | 643.2682 | 632.1054 | NaN | NaN | NaN | 740.3246 | 1254.2667 | NaN | NaN | 1252.9964 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.0259 | NaN | 20.4223
10609.1292 | 748.8057 | 651.1678 | 430.2509 | 429.1808 | 440.3983 | 664.1763 | 639.428 | 628.6729 | NaN | NaN | NaN | 747.8816 | 1254.2655 | NaN | NaN | 1252.9952 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.0575 | NaN | 22.442
10610.1292 | 750.2236 | 650.0938 | 430.0449 | 429.8036 | 440.5718 | 664.0631 | 635.1416 | 622.2561 | NaN | NaN | NaN | 746.4975 | 1254.2649 | NaN | NaN | 1252.9946 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.1555 | NaN | 21.1867
10611.1292 | 747.663 | 648.8048 | 430.223 | 430.1308 | 440.5822 | 669.4644 | 640.8745 | 620.6252 | NaN | NaN | NaN | 750.5884 | 1254.2641 | NaN | NaN | 1252.9938 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.2239 | NaN | 23.8584
10612.1292 | 744.6695 | 648.0544 | 431.2369 | 430.6455 | 440.4625 | 665.7871 | 640.8844 | 618.3198 | NaN | NaN | NaN | 716.9965 | 1254.2632 | NaN | NaN | 1252.9929 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.4269 | NaN | 23.5996
10613.1292 | 745.088 | 648.5444 | 430.7679 | 430.411 | 440.833 | 665.4029 | 644.7996 | 616.2795 | NaN | NaN | NaN | 730.8794 | 1254.2625 | NaN | NaN | 1252.9922 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 16.2197 | NaN | 23.7062
10614.1292 | 746.6325 | 649.1441 | 430.421 | 430.3009 | 440.6362 | 672.6766 | 641.9117 | 617.3821 | NaN | NaN | NaN | 742.2739 | 1254.2626 | NaN | NaN | 1252.9923 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 16.2496 | NaN | 23.5111
10615.1292 | 746.7499 | 650.8448 | 431.5243 | 430.3062 | 441.046 | 668.137 | 639.7997 | 617.281 | NaN | NaN | NaN | 761.4706 | 1254.2612 | NaN | NaN | 1252.9908 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.7667 | NaN | 21.8466
10616.1292 | 749.6409 | 651.8608 | 431.4274 | 430.6462 | 441.4161 | 675.4202 | 638.4921 | 622.3727 | NaN | NaN | NaN | 750.8825 | 1254.2606 | NaN | NaN | 1252.9903 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.2013 | NaN | 21.7056
10617.1292 | 747.9528 | 653.036 | 431.9297 | 430.9705 | 442.2428 | 680.122 | 636.6703 | 618.1113 | NaN | NaN | NaN | 736.4528 | 1254.2606 | NaN | NaN | 1252.9903 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.3137 | NaN | 23.8773
10618.1292 | 748.0397 | 653.7685 | 432.4216 | 431.7707 | 443.0357 | 677.0651 | 635.6333 | 615.6716 | NaN | NaN | NaN | 712.9992 | 1254.2586 | NaN | NaN | 1252.9883 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.3503 | NaN | 23.2446
10619.1292 | 749.8175 | 655.538 | 432.7508 | 433.2965 | 444.492 | 670.5588 | 635.8279 | 614.8855 | NaN | NaN | NaN | 726.6221 | 1254.2584 | NaN | NaN | 1252.9881 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.6452 | NaN | 23.4213
10620.1292 | 750.0786 | 655.3289 | 433.1169 | 434.1766 | 444.865 | 672.4184 | 638.6158 | 613.3618 | NaN | NaN | NaN | 745.0161 | 1254.2571 | NaN | NaN | 1252.9868 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.428 | NaN | 23.2238
10621.1292 | 750.7819 | 654.3798 | 433.444 | 434.7015 | 445.3129 | 670.4564 | 634.1663 | 610.1513 | NaN | NaN | NaN | 738.7383 | 1254.2571 | NaN | NaN | 1252.9868 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.9871 | NaN | 23.6292
10622.1292 | 750.2732 | 654.1291 | 434.0079 | 434.6949 | 445.2573 | 672.8509 | 633.1363 | 613.2519 | NaN | NaN | NaN | 735.8784 | 1254.2556 | NaN | NaN | 1252.9853 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.6342 | NaN | 24.0126
10623.1292 | 750.3867 | 654.405 | 433.9981 | 434.5419 | 445.2909 | 675.9807 | 634.7848 | 610.1899 | NaN | NaN | NaN | 758.9675 | 1254.2549 | NaN | NaN | 1252.9846 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.6054 | NaN | 23.2718
10624.1292 | 750.5526 | 654.5305 | 434.8043 | 434.4836 | 445.5009 | 675.5768 | 633.3032 | 614.9964 | NaN | NaN | NaN | 776.855 | 1254.2545 | NaN | NaN | 1252.9842 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 17.2831 | NaN | 23.8512
10625.1292 | 750.0864 | 653.2805 | 434.7474 | 434.7948 | 445.4875 | 666.869 | 627.9893 | 612.6557 | NaN | NaN | NaN | 777.8577 | 1254.2531 | NaN | NaN | 1252.9828 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.6688 | NaN | 22.6711
10626.1292 | 749.2347 | 652.2311 | 435.3643 | 435.1687 | 446.0614 | 663.872 | 625.5177 | 608.2515 | NaN | NaN | NaN | 786.5477 | 1254.2525 | NaN | NaN | 1252.9822 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.1027 | NaN | 21.4305
10627.1292 | 748.6235 | 652.1505 | 435.804 | 435.2516 | 446.089 | 662.997 | 624.1034 | 608.4247 | NaN | NaN | NaN | 795.3242 | 1254.2508 | NaN | NaN | 1252.9805 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.7482 | NaN | 22.7071
10628.1292 | 752.3552 | 653.0127 | 436.0669 | 435.5696 | 446.1287 | 661.7192 | 623.8746 | 608.8158 | NaN | NaN | NaN | 797.8991 | 1254.2515 | NaN | NaN | 1252.9811 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.1222 | NaN | 23.1088
10629.1292 | 754.5787 | 654.3722 | 436.222 | 436.0301 | 447.0477 | 661.8694 | 624.1874 | 609.0232 | NaN | NaN | NaN | 796.7888 | 1254.2507 | NaN | NaN | 1252.9804 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.8405 | NaN | 23.1884
10630.1292 | 755.2939 | 652.3391 | 436.0399 | 436.5616 | 447.3918 | 658.045 | 623.1272 | 608.8258 | NaN | NaN | NaN | 748.2328 | 1254.2496 | NaN | NaN | 1252.9793 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.5875 | NaN | 23.3222
10631.1292 | 756.5807 | 651.5673 | 435.7639 | 436.3227 | 447.379 | 664.6767 | 622.7785 | 608.2284 | NaN | NaN | NaN | 735.3478 | 1254.2493 | NaN | NaN | 1252.979 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.2622 | NaN | 23.943
10632.1292 | 758.0753 | 651.5393 | 436.5539 | 436.6784 | 447.8184 | 666.6745 | 623.6369 | 610.5883 | NaN | NaN | NaN | 714.4142 | 1254.2471 | NaN | NaN | 1252.9768 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.6175 | NaN | 23.0702
10633.1292 | 756.9899 | 651.9353 | 437.1376 | 436.2821 | 447.546 | 677.7836 | 624.8162 | 609.1247 | NaN | NaN | NaN | 695.7544 | 1254.2462 | NaN | NaN | 1252.9759 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.6856 | NaN | 22.4296
10634.1292 | 754.8351 | 652.6537 | 437.1123 | 435.9565 | 447.5517 | 676.6832 | 624.1547 | 605.6736 | NaN | NaN | NaN | 687.8672 | 1254.2471 | NaN | NaN | 1252.9767 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.1156 | NaN | 22.9057
10635.1292 | 754.7414 | 652.2034 | 437.7067 | 435.6549 | 447.2902 | 676.9286 | 621.3581 | 601.1982 | NaN | NaN | NaN | 679.8884 | 1254.245 | NaN | NaN | 1252.9747 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.4227 | NaN | 23.5516
10636.1292 | 752.4003 | 650.742 | 437.2317 | 435.799 | 447.2229 | 680.7295 | 623.0033 | 602.7911 | NaN | NaN | NaN | 660.7979 | 1254.245 | NaN | NaN | 1252.9747 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.9504 | NaN | 22.1307
10637.1292 | 749.2227 | 649.9511 | 437.1328 | 435.1438 | 446.8298 | 679.702 | 622.4738 | 605.4437 | NaN | NaN | NaN | 644.8937 | 1254.2434 | NaN | NaN | 1252.9731 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.8465 | NaN | 22.9739
10638.1292 | 747.5539 | 650.1598 | 436.905 | 435.1738 | 446.6611 | 674.1196 | 619.6862 | 599.9304 | NaN | NaN | NaN | 620.3915 | 1254.2427 | NaN | NaN | 1252.9724 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.2125 | NaN | 23.3551
10639.1292 | 749.002 | 649.7244 | 436.5817 | 435.1145 | 446.1876 | 670.8627 | 620.3463 | 599.6744 | NaN | NaN | NaN | 617.6833 | 1254.2425 | NaN | NaN | 1252.9722 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.5505 | NaN | 23.2341
10640.1292 | 748.5642 | 648.971 | 436.4568 | 435.4801 | 446.4858 | 666.2559 | 618.8003 | 598.4556 | NaN | NaN | NaN | 671.4002 | 1254.2405 | NaN | NaN | 1252.9702 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.7679 | NaN | 23.8941
10641.1292 | 748.8965 | 649.153 | 437.1292 | 435.6637 | 446.7613 | 669.9311 | 625.1321 | 599.585 | NaN | NaN | NaN | 671.8039 | 1254.2402 | NaN | NaN | 1252.9699 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.1979 | NaN | 23.2434
10642.1292 | 748.6473 | 648.4708 | 436.6564 | 435.7943 | 446.6728 | 670.6581 | 630.7335 | 602.1156 | NaN | NaN | NaN | 684.6802 | 1254.2392 | NaN | NaN | 1252.9689 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.3992 | NaN | 23.2042
10643.1292 | 747.405 | 648.2798 | 437.6201 | 435.7632 | 446.545 | 672.6213 | 632.2653 | 606.7784 | NaN | NaN | NaN | 692.9321 | 1254.2393 | NaN | NaN | 1252.969 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.9324 | NaN | 23.1217
10644.1292 | 747.6855 | 647.9804 | 437.6632 | 435.6761 | 446.6849 | 668.2198 | 639.2195 | 620.6955 | NaN | NaN | NaN | 672.8412 | 1254.2386 | NaN | NaN | 1252.9683 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.0563 | NaN | 22.3924
10645.1292 | 747.396 | 648.5219 | 437.2689 | 435.8385 | 447.8924 | 674.5828 | 638.8104 | 621.426 | NaN | NaN | NaN | 687.8033 | 1254.2374 | NaN | NaN | 1252.9671 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.9866 | NaN | 23.2769
10646.1292 | 747.3315 | 648.8731 | 437.6686 | 435.7615 | 448.7124 | 671.6608 | 638.4789 | 621.962 | NaN | NaN | NaN | 701.0035 | 1254.2362 | NaN | NaN | 1252.9659 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.5272 | NaN | 21.9891
10647.1292 | 747.8626 | 649.007 | 437.6114 | 435.7722 | 448.3137 | 675.4893 | 638.3551 | 626.2771 | NaN | NaN | NaN | 695.2734 | 1254.2354 | NaN | NaN | 1252.9651 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.5499 | NaN | 23.0591
10648.1292 | 749.5271 | 649.891 | 438.1926 | 435.8181 | 448.4305 | 677.2793 | 636.8859 | 622.3329 | NaN | NaN | NaN | 665.6058 | 1254.2351 | NaN | NaN | 1252.9648 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 16.0278 | NaN | 23.2995
10649.1292 | 749.9919 | 650.94 | 437.6143 | 436.143 | 448.6464 | 676.7305 | 637.0786 | 632.7276 | NaN | NaN | NaN | 637.5308 | 1254.2344 | NaN | NaN | 1252.9641 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.9348 | NaN | 22.1251
10650.1292 | 750.9808 | 651.804 | 437.7522 | 437.6642 | 449.3546 | 681.3131 | 644.0922 | 634.2384 | NaN | NaN | NaN | 620.1519 | 1254.2334 | NaN | NaN | 1252.9631 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.9941 | NaN | 23.0566
10651.1292 | 752.0076 | 652.5746 | 437.4583 | 437.9107 | 449.7935 | 679.6943 | 642.9731 | 630.8728 | NaN | NaN | NaN | 618.2221 | 1254.2323 | NaN | NaN | 1252.962 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.0284 | NaN | 22.221
10652.1292 | 752.8141 | 652.9901 | 438.4561 | 438.0867 | 450.4661 | 675.0449 | 639.4995 | 625.0569 | NaN | NaN | NaN | 594.3016 | 1254.2322 | NaN | NaN | 1252.9619 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.2186 | NaN | 22.7647
10653.1292 | 757.6755 | 652.4393 | 438.3191 | 438.2014 | 450.8882 | 670.2684 | 636.6331 | 618.471 | NaN | NaN | NaN | 618.1675 | 1254.2314 | NaN | NaN | 1252.9611 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.6016 | NaN | 23.9947
10654.1292 | 759.8095 | 652.2672 | 439.267 | 437.9483 | 450.8789 | 669.8302 | 632.2908 | 615.9882 | NaN | NaN | NaN | 659.9391 | 1254.2305 | NaN | NaN | 1252.9602 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.6827 | NaN | 24.0136
10655.1292 | 759.1085 | 652.1763 | 439.8705 | 438.0616 | 451.489 | 671.0171 | 630.26 | 615.5503 | NaN | NaN | NaN | 682.3481 | 1254.23 | NaN | NaN | 1252.9597 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.9049 | NaN | 22.9701
10656.1292 | 762.2974 | 651.3209 | 439.476 | 438.624 | 451.0339 | 666.7773 | 629.4573 | 613.2475 | NaN | NaN | NaN | 680.0284 | 1254.2284 | NaN | NaN | 1252.9582 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.4611 | NaN | 24.0943
10657.1292 | 765.7723 | 651.5696 | 439.4589 | 438.8824 | 450.8792 | 665.8928 | 629.0772 | 611.2034 | NaN | NaN | NaN | 685.1323 | 1254.2276 | NaN | NaN | 1252.9573 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.9423 | NaN | 23.1005
10658.1292 | 764.9771 | 651.3035 | 439.3414 | 439.0278 | 451.1806 | 671.9404 | 631.9516 | 611.4441 | NaN | NaN | NaN | 684.0231 | 1254.2269 | NaN | NaN | 1252.9566 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 16.2727 | NaN | 23.4826
10659.1292 | 762.655 | 651.2299 | 440.2392 | 438.9875 | 451.2174 | 669.3956 | 631.4039 | 611.1014 | NaN | NaN | NaN | 691.6105 | 1254.226 | NaN | NaN | 1252.9557 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.2781 | NaN | 22.1221
10660.1292 | 759.6751 | 651.1823 | 439.9732 | 438.8384 | 451.0604 | 672.4027 | 634.6402 | 610.4566 | NaN | NaN | NaN | 701.9658 | 1249.7745 | NaN | NaN | 1252.9552 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.5285 | NaN | 23.047
10661.1292 | 757.4203 | 650.6892 | 439.8813 | 438.8321 | 451.0429 | 677.3348 | 644.4986 | 611.4268 | NaN | NaN | NaN | 688.3744 | 1234.9474 | NaN | NaN | 1252.9544 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.2712 | NaN | 23.8063
10662.1292 | 753.9326 | 650.3781 | 439.9684 | 438.9713 | 451.5093 | 678.4367 | 650.154 | 613.2627 | NaN | NaN | NaN | 676.209 | 1220.2447 | NaN | NaN | 1249.9876 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.1126 | NaN | 22.6486
10663.1292 | 752.0806 | 649.5563 | 440.9313 | 439.1847 | 451.6546 | 678.8303 | 656.0705 | 617.5263 | NaN | NaN | NaN | 690.7565 | 1206.4263 | NaN | NaN | 1240.3688 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.8288 | NaN | 23.7672
10664.1292 | 749.8249 | 649.1052 | 440.6263 | 439.2606 | 452.0367 | 677.8169 | 669.8117 | 626.5151 | NaN | NaN | NaN | 679.31 | 1186.8094 | NaN | NaN | 1221.1715 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.7946 | NaN | 22.5401
10665.1292 | 749.9504 | 648.6664 | 440.8461 | 438.8814 | 452.0108 | 677.207 | 664.6283 | 633.6636 | NaN | NaN | NaN | 683.5343 | 1166.3382 | NaN | NaN | 1203.6752 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.5362 | NaN | 23.3343
10666.1292 | 748.9723 | 648.4771 | 441.5491 | 438.6817 | 451.8294 | 684.9804 | 658.4473 | 637.7305 | NaN | NaN | NaN | 682.7228 | 1152.3912 | NaN | NaN | 1182.1676 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.8606 | NaN | 23.6346
10667.1292 | 748.4759 | 648.3037 | 442.2736 | 439.3979 | 452.2508 | 684.6164 | 657 | 638.269 | NaN | NaN | NaN | 674.5005 | 1143.8363 | NaN | NaN | 1172.3259 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.4267 | NaN | 23.3501
10668.1292 | 747.9894 | 647.8836 | 442.2058 | 439.7041 | 452.6861 | 684.8428 | 661.3822 | 633.1118 | NaN | NaN | NaN | 708.3384 | 1129.8101 | NaN | NaN | 1163.529 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.8684 | NaN | 23.6245
10669.1292 | 748.6917 | 648.5247 | 441.7737 | 440.2268 | 453.2297 | 685.5015 | 658.4841 | 630.7853 | NaN | NaN | NaN | 704.9521 | 1115.3649 | NaN | NaN | 1149.9112 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.5525 | NaN | 25.7456
10670.1292 | 748.4242 | 648.8939 | 442.0843 | 440.4651 | 452.7584 | 682.341 | 660.293 | 631.8655 | NaN | NaN | NaN | 697.6566 | 1097.8829 | NaN | NaN | 1129.3751 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.8435 | NaN | 23.4812
10671.1292 | 747.4615 | 649.2573 | 442.9537 | 440.6838 | 452.4397 | 679.6929 | 662.8218 | 631.4497 | NaN | NaN | NaN | 702.2335 | 1085.7399 | NaN | NaN | 1115.0333 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.7651 | NaN | 23.2924
10672.1292 | 749.2729 | 649.0251 | 442.8194 | 441.2619 | 453.3149 | 680.6131 | 662.7339 | 631.2256 | NaN | NaN | NaN | 707.4764 | 1073.589 | NaN | NaN | 1103.7179 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.0514 | NaN | 24.1468
10673.1292 | 750.9037 | 649.7751 | 442.3349 | 440.9545 | 453.349 | 684.104 | 660.2572 | 628.4829 | NaN | NaN | NaN | 723.9355 | 1055.8954 | NaN | NaN | 1086.76 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.9485 | NaN | 22.1134
10674.1292 | 751.352 | 649.1326 | 442.8894 | 440.6588 | 453.0258 | 680.3386 | 656.6083 | 627.6098 | NaN | NaN | NaN | 752.0175 | 1036.9172 | NaN | NaN | 1077.842 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.3399 | NaN | 22.5904
10675.1292 | 749.7552 | 649.1075 | 443.8823 | 440.8845 | 452.6814 | 682.7569 | 666.5091 | 634.8469 | NaN | NaN | NaN | 742.6164 | 1017.2169 | NaN | NaN | 1063.6387 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.6307 | NaN | 24.0163
10676.1292 | 747.0147 | 648.78 | 443.5585 | 441.2939 | 452.705 | 681.7703 | 670.1707 | 640.8773 | NaN | NaN | NaN | 747.1121 | 998.5591 | NaN | NaN | 1046.377 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.498 | NaN | 23.0902
10677.1292 | 746.3334 | 648.749 | 443.628 | 440.9195 | 452.5845 | 682.8295 | 661.9367 | 637.0949 | NaN | NaN | NaN | 732.3434 | 987.9651 | NaN | NaN | 1035.9138 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.083 | NaN | 23.6403
10678.1292 | 746.1908 | 648.2407 | 443.3843 | 440.4053 | 452.0756 | 683.3178 | 661.7472 | 637.403 | NaN | NaN | NaN | 715.3789 | 972.592 | NaN | NaN | 1026.566 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.5146 | NaN | 23.615
10679.1292 | 745.4091 | 648.3348 | 443.8041 | 440.2114 | 452.3719 | 683.641 | 667.7951 | 642.079 | NaN | NaN | NaN | 694.7175 | 956.4562 | NaN | NaN | 1014.8766 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.3145 | NaN | 23.7595
10680.1292 | 743.6305 | 648.1306 | 443.5946 | 440.6814 | 453.0434 | 686.9569 | 669.967 | 644.3607 | NaN | NaN | NaN | 733.4834 | 940.4069 | NaN | NaN | 999.3275 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.8954 | NaN | 24.7579
10681.1292 | 739.9103 | 648.7756 | 443.2593 | 441.2341 | 453.8883 | 697.2383 | 666.3294 | 654.2015 | NaN | NaN | NaN | 718.8633 | 922.6006 | NaN | NaN | 988.097 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.2437 | NaN | 24.2551
10682.1292 | 738.046 | 649.0248 | 443.1983 | 441.0754 | 454.2104 | 693.3205 | 659.4815 | 643.2784 | NaN | NaN | NaN | 707.2633 | 911.868 | NaN | NaN | 982.0267 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.948 | NaN | 22.3923
10683.1292 | 737.7522 | 648.7315 | 443.0952 | 440.9024 | 453.7573 | 690.2398 | 660.6225 | 645.943 | NaN | NaN | NaN | 705.1523 | 897.8846 | NaN | NaN | 964.9425 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.8549 | NaN | 24.2793
10684.1292 | 737.9639 | 646.8256 | 442.8805 | 440.7504 | 453.4988 | 691.6208 | 658.4175 | 646.0429 | NaN | NaN | NaN | 670.4292 | 885.7211 | NaN | NaN | 950.5454 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.3121 | NaN | 23.943
10685.1292 | 737.1443 | 646.204 | 443.202 | 440.5212 | 453.0207 | 694.3405 | 655.0155 | 640.1766 | NaN | NaN | NaN | 678.1225 | 868.3094 | NaN | NaN | 939.4594 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.8577 | NaN | 23.0475
10686.1292 | 737.7346 | 646.4248 | 442.7872 | 440.3548 | 452.4267 | 695.6736 | 654.7141 | 633.8701 | NaN | NaN | NaN | 710.7487 | 855.2348 | NaN | NaN | 925.2366 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.6563 | NaN | 23.3831
10687.1292 | 736.2829 | 646.8288 | 442.8934 | 440.3386 | 452.2769 | 698.6902 | 651.1584 | 631.678 | NaN | NaN | NaN | 731.946 | 846.3698 | NaN | NaN | 913.8156 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.3505 | NaN | 24.2135
10688.1292 | 735.3914 | 647.2944 | 443.0157 | 440.3814 | 452.527 | 697.225 | 646.0552 | 627.5805 | NaN | NaN | NaN | 721.6 | 834.5843 | NaN | NaN | 898.0222 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.8758 | NaN | 23.5996
10689.1292 | 735.9164 | 648.2529 | 443.9304 | 440.4253 | 452.2938 | 693.9041 | 647.1557 | 631.0472 | NaN | NaN | NaN | 691.027 | 824.3235 | NaN | NaN | 888.1288 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.2028 | NaN | 23.1659
10690.1292 | 734.9692 | 647.7673 | 444.1434 | 440.5921 | 452.4721 | 697.3037 | 644.405 | 630.4802 | NaN | NaN | NaN | 697.2385 | 809.7338 | NaN | NaN | 882.9115 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.6727 | NaN | 23.6634
10691.1292 | 733.2632 | 647.596 | 443.6686 | 440.8029 | 452.4576 | 699.4594 | 643.6844 | 634.4715 | NaN | NaN | NaN | 683.8602 | 795.5516 | NaN | NaN | 873.8619 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.4329 | NaN | 24.3432
10692.1292 | 733.7759 | 647.7191 | 443.7237 | 440.9653 | 453.2755 | 697.5784 | 644.7961 | 641.1659 | NaN | NaN | NaN | 679.4508 | 787.1653 | NaN | NaN | 871.1438 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.9545 | NaN | 24.8268
10693.1292 | 734.5703 | 648.4156 | 444.4806 | 440.7762 | 452.9498 | 693.4796 | 644.3199 | 650.0777 | NaN | NaN | NaN | 648.5719 | 776.0891 | NaN | NaN | 855.9262 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.1667 | NaN | 24.3387
10694.1292 | 734.5228 | 648.5343 | 445.3035 | 440.7466 | 452.502 | 693.1798 | 640.6077 | 640.9733 | NaN | NaN | NaN | 624.5782 | 762.3877 | NaN | NaN | 844.8826 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.4642 | NaN | 24.5309
10695.1292 | 733.8046 | 647.4047 | 445.603 | 440.8453 | 452.7842 | 691.9589 | 637.6855 | 646.0548 | NaN | NaN | NaN | 607.3946 | 752.2475 | NaN | NaN | 833.526 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.9869 | NaN | 23.6968
10696.1292 | 733.3465 | 646.6113 | 445.5802 | 441.0321 | 452.8932 | 694.3251 | 642.1471 | 645.6179 | NaN | NaN | NaN | 643.7646 | 743.8405 | NaN | NaN | 830.4127 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.1635 | NaN | 23.9851
10697.1292 | 735.0575 | 647.3175 | 445.9761 | 441.1694 | 453.0331 | 689.6952 | 644.0879 | 646.0355 | NaN | NaN | NaN | 625.3744 | 728.704 | NaN | NaN | 824.5515 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.309 | NaN | 22.947
10698.1292 | 735.0304 | 647.8527 | 446.1582 | 441.3985 | 453.2807 | 696.3065 | 642.8056 | 642.6788 | NaN | NaN | NaN | 621.2055 | 716.7033 | NaN | NaN | 815.2231 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.3361 | NaN | 23.4684
10699.1448 | 735.0936 | 647.6568 | 446.1305 | 441.7351 | 452.9321 | 694.8813 | 638.5288 | 635.9917 | NaN | NaN | NaN | 599.7218 | 709.6811 | NaN | NaN | 810.6959 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.1303 | NaN | 24.7098
10700.1292 | 733.7422 | 647.8784 | 446.7937 | 442.3886 | 453.3649 | 697.1463 | 635.8549 | 629.8646 | NaN | NaN | NaN | 603.6195 | 719.8932 | NaN | NaN | 846.4724 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.4888 | NaN | 22.7673
10701.1292 | 732.0051 | 647.2621 | 447.0871 | 443.0469 | 453.5688 | 690.5358 | 632.4445 | 626.3205 | NaN | NaN | NaN | 608.6763 | 724.0153 | NaN | NaN | 864.1565 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.6945 | NaN | 22.4212
10702.1292 | 731.1127 | 647.4015 | 447.4541 | 443.2179 | 453.8893 | 686.6944 | 627.8951 | 622.8319 | NaN | NaN | NaN | 649.6869 | 721.6923 | NaN | NaN | 871.9332 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.7033 | NaN | 22.5178
10703.1292 | 734.0469 | 647.1008 | 447.4547 | 443.6845 | 453.8681 | 678.2974 | 625.6708 | 628.2902 | NaN | NaN | NaN | 634.8843 | 709.1932 | NaN | NaN | 857.7008 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.0352 | NaN | 24.0407
10704.1292 | 734.5869 | 647.9738 | 447.3784 | 443.9141 | 454.1511 | 682.3747 | 623.7212 | 623.4483 | NaN | NaN | NaN | 611.0759 | 699.1867 | NaN | NaN | 845.9472 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.7438 | NaN | 23.5863
10705.1292 | 734.2826 | 649.3506 | 447.8565 | 443.5692 | 454.4835 | 683.5079 | 627.1114 | 619.2023 | NaN | NaN | NaN | 593.6334 | 686.4435 | NaN | NaN | 833.1284 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.6652 | NaN | 24.0096
10706.1292 | 733.2353 | 650.8628 | 448.0814 | 445.7087 | 454.9817 | 682.2105 | 633.9608 | 617.7851 | NaN | NaN | NaN | 594.7228 | 675.202 | NaN | NaN | 818.701 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.801 | NaN | 24.4014
10707.1292 | 732.0389 | 651.3672 | 448.3606 | 445.9647 | 455.8474 | 685.4411 | 632.9948 | 614.733 | NaN | NaN | NaN | 627.5805 | 664.6834 | NaN | NaN | 811.7761 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.2006 | NaN | 24.648
10708.1292 | 732.2102 | 651.2776 | 448.424 | 445.6671 | 455.3727 | 686.73 | 640.1411 | 616.1355 | NaN | NaN | NaN | 620.2303 | 649.6192 | NaN | NaN | 786.4253 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.9648 | NaN | 24.3579
10709.1292 | 732.7417 | 650.0225 | 448.6183 | 445.1334 | 455.196 | 685.881 | 635.0459 | 631.6058 | NaN | NaN | NaN | 607.9454 | 633.7701 | NaN | NaN | 766.3513 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.6101 | NaN | 24.0592
10710.1448 | 733.1585 | 649.9841 | 449.4932 | 444.7989 | 455.2472 | 691.0812 | 631.5551 | 639.8423 | NaN | NaN | NaN | 585.5516 | 618.2969 | NaN | NaN | 746.2669 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.31 | NaN | 23.009
10711.1292 | 731.8696 | 650.2687 | 450.0324 | 444.8646 | 456.1062 | 683.7904 | 628.7381 | 631.104 | NaN | NaN | NaN | 567.3864 | 602.0736 | NaN | NaN | 725.8371 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.3897 | NaN | 24.6772
10712.1292 | 733.5361 | 650.2189 | 449.5477 | 445.1041 | 456.332 | 688.8341 | 627.1301 | 642.3711 | NaN | NaN | NaN | 553.169 | 587.6447 | NaN | NaN | 705.6037 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.436 | NaN | 24.3215
10713.1292 | 735.5277 | 650.3832 | 449.9202 | 445.7839 | 456.762 | 694.6738 | 625.8979 | 637.7031 | NaN | NaN | NaN | 572.7139 | 575.0458 | NaN | NaN | 687.0013 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.8728 | NaN | 24.2697
10714.1292 | 737.3561 | 649.5122 | 449.3719 | 446.0958 | 456.835 | 692.2523 | 627.8297 | 630.8745 | NaN | NaN | NaN | 600.2541 | 563.7619 | NaN | NaN | 676.1121 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.8921 | NaN | 23.5651
10715.1292 | 737.2737 | 649.0854 | 448.9824 | 446.2811 | 457.8582 | 691.1387 | 629.8359 | 630.8345 | NaN | NaN | NaN | 631.1847 | 546.8657 | NaN | NaN | 661.7143 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.8819 | NaN | 23.6638
10716.1292 | 737.2075 | 649.1126 | 449.2598 | 446.0944 | 458.2568 | 689.2104 | 640.0502 | 647.4894 | NaN | NaN | NaN | 666.6246 | 527.9638 | NaN | NaN | 638.6574 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.6023 | NaN | 24.1323
10717.1292 | 735.6247 | 648.1482 | 448.6053 | 445.8748 | 458.6889 | 693.4067 | 639.8179 | 649.5681 | NaN | NaN | NaN | 650.07 | 510.5025 | NaN | NaN | 616.536 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.8038 | NaN | 23.3508
10718.1292 | 736.4552 | 648.1647 | 448.0481 | 445.5645 | 458.8724 | 693.6661 | 639.9111 | 656.7857 | NaN | NaN | NaN | 668.0937 | 498.6115 | NaN | NaN | 606.3525 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.9172 | NaN | 22.1348
10719.1292 | 736.7265 | 647.8603 | 447.2747 | 445.2565 | 458.8055 | 686.001 | 636.0896 | 648.7528 | NaN | NaN | NaN | 697.0542 | 477.015 | NaN | NaN | 591.4913 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.2641 | NaN | 23.3671
10720.1292 | 736.1932 | 647.1076 | 447.3135 | 444.8273 | 458.355 | 681.155 | 632.3926 | 640.7627 | NaN | NaN | NaN | 693.7938 | 462.7132 | NaN | NaN | 575.6659 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.8227 | NaN | 23.1944
10721.1292 | 738.078 | 646.7703 | 448.7316 | 445.0873 | 458.5071 | 674.6812 | 629.1887 | 635.2933 | NaN | NaN | NaN | 692.2282 | 452.0833 | NaN | NaN | 570.3991 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.8826 | NaN | 23.5193
10722.1292 | 738.9188 | 646.3068 | 448.3033 | 445.0493 | 457.8251 | 677.1246 | 629.3637 | 632.511 | NaN | NaN | NaN | 706.877 | 436.8206 | NaN | NaN | 557.3822 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.5327 | NaN | 23.6327
10723.1292 | 739.8429 | 646.3016 | 447.9416 | 445.0577 | 457.4812 | 682.6914 | 629.0086 | 632.9492 | NaN | NaN | NaN | 712.6994 | 422.4372 | NaN | NaN | 539.3125 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.4434 | NaN | 23.8526
10724.1292 | 739.3553 | 646.7523 | 447.4054 | 445.0293 | 457.4809 | 692.2533 | 630.9184 | 650.9387 | NaN | NaN | NaN | 712.5879 | 407.951 | NaN | NaN | 525.0144 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.7423 | NaN | 22.618
10725.1448 | 738.843 | 645.9335 | 446.8287 | 445.2473 | 457.5045 | 693.6292 | 630.6243 | 651.869 | NaN | NaN | NaN | 710.3587 | 391.5492 | NaN | NaN | 517.1558 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.0916 | NaN | 23.24
10726.1292 | 739.1089 | 646.2623 | 446.9003 | 445.4359 | 458.0785 | 695.1009 | 631.1663 | 648.0459 | NaN | NaN | NaN | 712.5165 | 379.6922 | NaN | NaN | 512.2687 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.5746 | NaN | 22.1525
10727.1292 | 739.4908 | 646.3062 | 447.1187 | 445.4365 | 458.1631 | 688.4802 | 628.6238 | 640.489 | NaN | NaN | NaN | 742.133 | 365.4902 | NaN | NaN | 498.5981 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.3636 | NaN | 23.8948
10728.1292 | 739.6127 | 646.0495 | 447.3084 | 445.7517 | 458.0761 | 684.9571 | 626.3338 | 635.8359 | NaN | NaN | NaN | 726.0531 | 349.3871 | NaN | NaN | 478.4971 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.1036 | NaN | 24.4465
10729.1292 | 741.5708 | 645.6565 | 447.8545 | 445.4814 | 458.3164 | 683.914 | 628.875 | 632.0799 | NaN | NaN | NaN | 720.8709 | 341.5899 | NaN | NaN | 474.471 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.8435 | NaN | 24.3718
10730.1292 | 743.2115 | 645.6373 | 447.7842 | 445.1991 | 457.9919 | 689.5576 | 627.25 | 629.1327 | NaN | NaN | NaN | 741.2417 | 331.3188 | NaN | NaN | 466.7344 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.4195 | NaN | 23.6311
10731.1292 | 741.1381 | 646.359 | 447.9114 | 445.5839 | 458.1077 | 687.5303 | 631.3165 | 626.4032 | NaN | NaN | NaN | 722.6708 | 320.7009 | NaN | NaN | 456.4075 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.0377 | NaN | 22.4479
10732.1292 | 739.2079 | 645.4439 | 448.5994 | 445.1749 | 457.8009 | 684.0466 | 627.7024 | 639.3824 | NaN | NaN | NaN | 730.4493 | 315.4284 | NaN | NaN | 450.2869 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.7115 | NaN | 25.2516
10733.1292 | 741.8876 | 643.685 | 448.5236 | 445.4955 | 457.6838 | 680.8748 | 628.5445 | 654.147 | NaN | NaN | NaN | 725.275 | 308.948 | NaN | NaN | 435.3873 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.6159 | NaN | 23.1689
10734.1292 | 745.0301 | 644.2609 | 448.3912 | 445.9286 | 457.5584 | 684.0758 | 628.7966 | 660.4088 | NaN | NaN | NaN | 727.7595 | 296.8422 | NaN | NaN | 420.5029 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.4829 | NaN | 23.7128
10735.1292 | 746.9544 | 644.8777 | 448.3387 | 446.0348 | 458.2412 | 678.8501 | 626.1586 | 654.3178 | NaN | NaN | NaN | 730.1727 | 286.9208 | NaN | NaN | 416.4224 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.6434 | NaN | 21.8231
10736.1292 | 747.3775 | 645.318 | 448.2623 | 446.2357 | 458.448 | 676.3406 | 623.0074 | 647.9235 | NaN | NaN | NaN | 738.8335 | 273.6789 | NaN | NaN | 401.2414 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.0967 | NaN | 24.5258
10737.1292 | 748.5429 | 645.8272 | 448.6371 | 446.52 | 458.5361 | 675.7241 | 626.0534 | 643.7551 | NaN | NaN | NaN | 732.8412 | 266.3058 | NaN | NaN | 394.1524 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.4789 | NaN | 22.3534
10738.1292 | 745.9522 | 644.6844 | 448.7037 | 447.1304 | 458.4451 | 668.567 | 623.3242 | 641.0097 | NaN | NaN | NaN | 728.5854 | 250.9395 | NaN | NaN | 384.0019 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 16.4039 | NaN | 22.0481
10739.1292 | 741.7291 | 645.8892 | 449.3295 | 446.7684 | 458.5897 | 666.1496 | 623.5393 | 637.2154 | NaN | NaN | NaN | 729.6775 | 239.3283 | NaN | NaN | 373.6039 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.9142 | NaN | 22.8423
10740.1292 | 740.6055 | 644.4322 | 449.6194 | 446.5176 | 458.5316 | 670.6789 | 634.7993 | 648.0413 | NaN | NaN | NaN | 713.7221 | 228.4546 | NaN | NaN | 365.935 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.7629 | NaN | 22.8963
10741.1292 | 742.48 | 644.3261 | 449.3902 | 446.603 | 458.1663 | 670.6981 | 639.0887 | 651.3406 | NaN | NaN | NaN | 707.9161 | 215.4795 | NaN | NaN | 359.7114 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.2896 | NaN | 23.7809
10742.1292 | 745.8446 | 644.0426 | 449.2826 | 446.56 | 457.9625 | 669.0014 | 632.4903 | 642.5857 | NaN | NaN | NaN | 695.8401 | 199.7399 | NaN | NaN | 348.5655 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.1956 | NaN | 22.3488
10743.1292 | 746.4746 | 644.6077 | 449.3755 | 446.4535 | 458.3662 | 667.0623 | 629.3522 | 636.1629 | NaN | NaN | NaN | 666.3852 | 183.8018 | NaN | NaN | 344.0468 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.8663 | NaN | 24.6435
10744.1292 | 747.2759 | 645.1054 | 449.7846 | 446.9936 | 458.7458 | 664.7099 | 626.8516 | 631.0058 | NaN | NaN | NaN | 639.3533 | 172.7559 | NaN | NaN | 339.3119 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.8767 | NaN | 23.857
10745.1292 | 747.8143 | 645.7471 | 449.2199 | 447.0378 | 459.756 | 657.8924 | 622.0507 | 624.4696 | NaN | NaN | NaN | 615.105 | 162.8849 | NaN | NaN | 334.8983 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.1709 | NaN | 25.017
10746.1292 | 748.0287 | 644.8938 | 449.3914 | 447.1934 | 459.4879 | 660.1417 | 621.941 | 640.3476 | NaN | NaN | NaN | 611.6506 | 155.1153 | NaN | NaN | 333.014 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.8504 | NaN | 22.8719
10747.1292 | 749.9405 | 644.3521 | 449.3665 | 447.0946 | 459.3018 | 655.6597 | 620.3121 | 645.8537 | NaN | NaN | NaN | 629.0775 | 144.0881 | NaN | NaN | 319.395 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.9021 | NaN | 23.1303
10748.1292 | 751.0442 | 643.9346 | 449.347 | 446.9139 | 458.9616 | 665.8499 | 617.8788 | 641.2746 | NaN | NaN | NaN | 610.519 | 131.5623 | NaN | NaN | 316.6991 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.0832 | NaN | 22.0055
10749.1292 | 750.9395 | 644.083 | 448.9697 | 446.6955 | 458.8822 | 663.5722 | 618.5465 | 649.2469 | NaN | NaN | NaN | 637.6113 | 119.1519 | NaN | NaN | 311.7802 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.5967 | NaN | 23.059
10750.1292 | 752.0943 | 644.3724 | 448.7405 | 446.5447 | 458.9876 | 663.4096 | 616.2454 | 654.8272 | NaN | NaN | NaN | 646.7735 | 106.3656 | NaN | NaN | 305.3315 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.3585 | NaN | 24.0441
10751.1292 | 752.2779 | 644.6995 | 448.6265 | 446.6462 | 458.8021 | 662.5492 | 621.4413 | 657.9576 | NaN | NaN | NaN | 655.9349 | 95.1936 | NaN | NaN | 294.0746 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.238 | NaN | 21.9507
10752.1292 | 751.1464 | 645.0017 | 449.0321 | 446.183 | 458.5604 | 661.0509 | 623.2806 | 667.4752 | NaN | NaN | NaN | 668.5477 | 85.826 | NaN | NaN | 285.2022 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.0995 | NaN | 23.8868
10753.1292 | 749.482 | 644.7953 | 450.0935 | 446.5947 | 458.6992 | 663.7659 | 628.5651 | 662.3309 | NaN | NaN | NaN | 655.246 | 73.351 | NaN | NaN | 276.0027 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 19.367 | NaN | 23.9034
10754.1292 | 749.549 | 644.3149 | 450.0441 | 446.7695 | 458.88 | 670.4997 | 630.1331 | 657.5337 | NaN | NaN | NaN | 672.6708 | 63.5985 | NaN | NaN | 265.79 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.5116 | NaN | 21.3459
10755.1292 | 750.909 | 644.1921 | 449.7175 | 446.7334 | 459.3615 | 669.051 | 634.9278 | 664.8322 | NaN | NaN | NaN | 684.6954 | 50.7944 | NaN | NaN | 253.3683 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.599 | NaN | 23.2874
10756.1292 | 752.0996 | 644.084 | 450.0032 | 446.705 | 459.2363 | 674.0132 | 633.9496 | 658.6967 | NaN | NaN | NaN | 689.6093 | 41.6331 | NaN | NaN | 244.383 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 16.2386 | NaN | 24.9744
10757.1292 | 752.5069 | 644.1836 | 450.932 | 446.8749 | 459.4267 | 676.6458 | 638.1273 | 671.0564 | NaN | NaN | NaN | 685.2272 | 37.515 | NaN | NaN | 228.2917 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.8475 | NaN | 22.7701
10758.1292 | 751.2734 | 644.2351 | 451.3138 | 447.1728 | 459.8124 | 679.1531 | 642.7274 | 663.8987 | NaN | NaN | NaN | 693.6323 | 33.6727 | NaN | NaN | 222.7665 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.3755 | NaN | 24.4408
10759.1292 | 753.3866 | 644.4538 | 451.42 | 447.6098 | 459.9287 | 681.5103 | 643.6592 | 662.9019 | NaN | NaN | NaN | 687.7085 | 24.9298 | NaN | NaN | 204.8839 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.1258 | NaN | 22.3751
10760.1292 | 755.1829 | 644.8425 | 451.4137 | 447.5781 | 459.9702 | 681.2611 | 644.0765 | 653.5287 | NaN | NaN | NaN | 676.8068 | 21.2864 | NaN | NaN | 194.3603 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 16.1321 | NaN | 24.0739
10761.1292 | 755.8948 | 644.8672 | 451.71 | 447.2035 | 459.4616 | 676.7776 | 641.9441 | 659.6636 | NaN | NaN | NaN | 652.7976 | 17.4505 | NaN | NaN | 182.1641 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.9266 | NaN | 21.9393
10762.1292 | 752.967 | 644.7556 | 452.1763 | 447.419 | 459.3565 | 678.2521 | 649.6557 | 652.5003 | NaN | NaN | NaN | 679.0999 | 12.0982 | NaN | NaN | 176.8619 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.7642 | NaN | 22.5954
10763.1292 | 751.3134 | 644.6364 | 452.1007 | 447.2296 | 459.8667 | 678.1125 | 645.6258 | 651.3163 | NaN | NaN | NaN | 684.2803 | 0.8435 | NaN | NaN | 166.9776 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.1362 | NaN | 20.7166
10764.1292 | 753.4426 | 644.4111 | 452.1729 | 447.1067 | 460.2927 | 674.9518 | 640.6943 | 645.7776 | NaN | NaN | NaN | 690.3549 | -2.4263 | NaN | NaN | 164.488 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.5361 | NaN | 23.5005
10765.1292 | 755.1622 | 644.4179 | 451.726 | 446.9386 | 460.2328 | 679.6723 | 645.0108 | 652.9112 | NaN | NaN | NaN | 707.5218 | -13.4934 | NaN | NaN | 155.0586 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.5683 | NaN | 23.15
10766.1292 | 755.5788 | 644.6116 | 452.0132 | 447.0322 | 460.4841 | 679.2008 | 642.2668 | 646.6625 | NaN | NaN | NaN | 707.6934 | NaN | NaN | NaN | 142.2185 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 22.6115 | NaN | 29.3029
10767.1292 | 755.7662 | 643.9534 | 452.5639 | 446.9537 | 460.0451 | 677.3824 | 637.5075 | 639.4104 | NaN | NaN | NaN | 687.9494 | NaN | NaN | NaN | 108.6841 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 48.2918 | NaN | 23.9984
10768.1292 | 755.2936 | 644.3601 | 452.8852 | 446.7433 | 460.1215 | 673.767 | 635.1752 | 636.813 | NaN | NaN | NaN | 682.8041 | NaN | NaN | NaN | 83.5311 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 18.3641 | NaN | -1.3066
10769.1292 | 755.4368 | 644.1566 | 452.4879 | 446.8687 | 460.4404 | 676.8524 | 631.3553 | 636.6423 | NaN | NaN | NaN | 662.7507 | NaN | NaN | NaN | 87.7786 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.3751 | NaN | 24.1826
10770.1292 | 755.5051 | 644.9298 | 452.5417 | 447.0471 | 460.7578 | 678.0515 | 638.216 | 646.8604 | NaN | NaN | NaN | 649.9672 | NaN | NaN | NaN | 86.4167 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.2762 | NaN | 23.9348
10771.1292 | 752.9485 | 643.9 | 452.5063 | 447.157 | 461.3911 | 678.413 | 637.5591 | 645.9276 | NaN | NaN | NaN | 672.0515 | NaN | NaN | NaN | 76.6883 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 16.321 | NaN | 25.1556
10772.1292 | 752.1094 | 644.2852 | 452.8559 | 447.5081 | 461.2451 | 680.9164 | 634.0992 | 642.8689 | NaN | NaN | NaN | 687.1419 | NaN | NaN | NaN | 73.5698 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.8595 | NaN | 24.6301
10773.1448 | 751.9637 | 644.5682 | 453.7174 | 448.1517 | 461.4203 | 681.9133 | 639.0341 | 642.3919 | NaN | NaN | NaN | 684.9755 | NaN | NaN | NaN | 69.8272 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.4803 | NaN | 22.0354
10774.1292 | 753.2307 | 644.0286 | 453.9256 | 448.0049 | 460.9394 | 675.4817 | 639.1315 | 641.7341 | NaN | NaN | NaN | 727.6277 | 12.3355 | NaN | NaN | 57.4547 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.1462 | NaN | 22.1932
10775.1292 | 756.4861 | 644.751 | 454.6228 | 448.1795 | 460.6853 | 679.1818 | 644.8975 | 637.2292 | NaN | NaN | NaN | 701.8224 | 64.0005 | NaN | NaN | 50.9643 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.6832 | NaN | 24.512
10776.1292 | 755.6172 | 644.5128 | 454.2239 | 448.1502 | 461.3723 | 674.1372 | 642.01 | 632.899 | NaN | NaN | NaN | 670.2613 | 146.6781 | NaN | NaN | 48.5002 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.1485 | NaN | 22.1797
10777.1292 | 757.2006 | 645.4476 | 453.7255 | 448.3132 | 461.1441 | 671.712 | 637.7459 | 630.6834 | NaN | NaN | NaN | 652.224 | 194.8707 | NaN | NaN | 50.6007 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.942 | NaN | 24.7384
10778.1292 | 757.3003 | 646.0227 | 453.751 | 448.5421 | 461.1734 | 669.0035 | 638.2283 | 632.4759 | NaN | NaN | NaN | 652.9271 | 255.6376 | NaN | NaN | 52.0857 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.0651 | NaN | 25.0416
10779.1292 | 755.2238 | 645.9332 | 453.8743 | 448.4851 | 461.0201 | 666.2728 | 637.698 | 628.2603 | NaN | NaN | NaN | 677.6652 | 334.0941 | NaN | NaN | 45.784 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.4134 | NaN | 23.9556
10780.1292 | 753.7533 | 646.2376 | 454.2478 | 448.8771 | 461.5091 | 664.7832 | 636.9386 | 627.95 | NaN | NaN | NaN | 707.533 | 491.914 | NaN | NaN | 45.0049 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.666 | NaN | 22.5238
10781.1292 | 753.2548 | 646.7271 | 454.0297 | 449.1511 | 462.1617 | 663.5726 | 640.5352 | 643.8 | NaN | NaN | NaN | 740.2032 | 816.9806 | NaN | NaN | 39.455 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.8495 | NaN | 23.2175
10782.1292 | 751.2598 | 646.1126 | 455.1688 | 449.0172 | 461.7247 | 669.9649 | 645.8356 | 642.0048 | NaN | NaN | NaN | 751.6681 | 1146.901 | NaN | NaN | 27.0101 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 16.3618 | NaN | 23.1547
10783.1292 | 749.6561 | 646.3844 | 455.3464 | 449.2759 | 461.854 | 675.2899 | 650.8308 | 640.4387 | NaN | NaN | NaN | 741.9111 | NaN | NaN | NaN | 22.7353 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.2608 | NaN | 23.528
10784.1292 | 747.4767 | 646.234 | 455.5447 | 449.9782 | 462.5138 | 676.7911 | 652.9458 | 659.4483 | NaN | NaN | NaN | 736.6695 | NaN | NaN | NaN | 12.2223 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.7539 | NaN | 23.2279
10785.1448 | 747.8868 | 645.9823 | 455.5155 | 450.0482 | 462.935 | 680.2033 | 649.5958 | 651.5572 | NaN | NaN | NaN | 719.7655 | NaN | NaN | NaN | 8.0094 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.8105 | NaN | 25.4674
10786.1292 | 746.9517 | 645.8241 | 455.5117 | 449.9891 | 462.7148 | 684.9331 | 656.6327 | 647.987 | NaN | NaN | NaN | 699.2743 | NaN | NaN | NaN | -0.588 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.8963 | NaN | 23.4593
10787.1292 | 745.321 | 645.9768 | 455.2136 | 449.7861 | 462.4811 | 695.5986 | 668.6313 | 646.2435 | NaN | NaN | NaN | 681.3796 | NaN | NaN | NaN | -9.4602 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.5486 | NaN | 21.5697
10788.1292 | 743.1615 | 645.5609 | 455.7431 | 449.7811 | 462.9369 | 695.3177 | 669.1456 | 649.6781 | NaN | NaN | NaN | 681.1093 | NaN | NaN | NaN | -14.6097 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.8653 | NaN | 25.0679
10789.1292 | 743.5812 | 645.2085 | 455.5809 | 449.8826 | 463.39 | 698.4192 | 680.0989 | 645.9718 | NaN | NaN | NaN | 687.1683 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.8065 | NaN | 22.6368
10790.1292 | 742.7234 | 644.4219 | 455.7284 | 449.9069 | 463.5306 | 694.4569 | 682.421 | 640.8776 | NaN | NaN | NaN | 653.1415 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.2838 | NaN | 21.7517
10791.1292 | 741.8329 | 643.9643 | 455.5087 | 449.821 | 463.8453 | 693.5876 | 684.0059 | 638.054 | NaN | NaN | NaN | 653.4293 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.2775 | NaN | 23.6162
10792.1292 | 739.6886 | 643.755 | 455.8368 | 450.0973 | 463.3485 | 696.5309 | 677.8736 | 637.4946 | NaN | NaN | NaN | 686.9484 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.6547 | NaN | 23.3006
10793.1292 | 740.306 | 643.5214 | 455.9907 | 450.5766 | 463.2838 | 695.53 | 679.1064 | 637.7937 | NaN | NaN | NaN | 708.1781 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.3843 | NaN | 23.1825
10794.1292 | 743.4542 | 642.7991 | 456.192 | 451.0693 | 464.3669 | 693.2669 | 679.6146 | 641.9845 | NaN | NaN | NaN | 712.3557 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 56.9652 | NaN | 28.2598
10795.1292 | 742.9252 | 643.1177 | 456.0814 | 450.8022 | 464.0575 | 696.1427 | 681.1617 | 658.2487 | NaN | NaN | NaN | 715.1752 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.8778 | NaN | 23.4561
10796.1292 | 743.9251 | 643.4792 | 455.9127 | 451.193 | 463.6921 | 692.0267 | 674.4608 | 658.3632 | NaN | NaN | NaN | 734.426 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.9035 | NaN | 24.195
10797.1292 | 744.5945 | 644.6286 | 456.1697 | 451.2495 | 464.0322 | 687.7798 | 668.6446 | 651.5044 | NaN | NaN | NaN | 747.4375 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.113 | NaN | 24.197
10798.1292 | 745.1068 | 644.7225 | 455.8445 | 451.0722 | 463.6151 | 685.0334 | 662.4975 | 643.9304 | NaN | NaN | NaN | 739.8394 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.0357 | NaN | 24.1087
10799.1292 | 745.8922 | 645.1296 | 455.7826 | 451.0676 | 463.4578 | 687.3835 | 662.2269 | 639.0636 | NaN | NaN | NaN | 737.9514 | NaN | NaN | NaN | -9.5229 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.4179 | NaN | 22.0657
10800.1292 | 744.873 | 645.4726 | 455.576 | 450.9626 | 463.6367 | 692.0685 | 659.1516 | 635.2281 | NaN | NaN | NaN | 751.1099 | NaN | NaN | NaN | 21.9946 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.5673 | NaN | 22.3575
10801.1292 | 745.8783 | 645.2426 | 455.9405 | 450.7854 | 463.3517 | 691.8374 | 655.4957 | 633.91 | NaN | NaN | NaN | 739.1337 | NaN | NaN | NaN | 54.882 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.2033 | NaN | 24.6023
10802.1292 | 746.2587 | 645.3884 | 455.8275 | 450.6668 | 464.1631 | 693.2039 | 657.4379 | 633.3959 | NaN | NaN | NaN | 733.295 | NaN | NaN | NaN | 75.1701 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.4152 | NaN | 22.0851
10803.1292 | 745.1096 | 645.2866 | 455.5345 | 450.5442 | 463.7932 | 695.0605 | 659.9681 | 634.7596 | NaN | NaN | NaN | 745.4686 | NaN | NaN | NaN | 146.7028 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.2382 | NaN | 23.5985
10804.1292 | 743.8775 | 644.7358 | 455.5345 | 450.4227 | 463.5089 | 695.2823 | 661.0195 | 633.1383 | NaN | NaN | NaN | 731.169 | NaN | NaN | NaN | 187.0242 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.2908 | NaN | 24.4495
10805.1292 | 741.9033 | 644.5106 | 455.2452 | 450.7993 | 463.7836 | 700.9693 | 669.9062 | 647.2226 | NaN | NaN | NaN | 726.3612 | NaN | NaN | NaN | 359.0951 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.9434 | NaN | 22.3993
10806.1292 | 741.5939 | 644.4478 | 455.6338 | 450.6206 | 464.9793 | 703.6418 | 673.5381 | 653.9249 | NaN | NaN | NaN | 705.6458 | NaN | NaN | NaN | 466.4661 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.5539 | NaN | 23.2383
10807.1292 | 740.2835 | 644.2011 | 455.7294 | 450.2429 | 464.7979 | 709.1671 | 675.826 | 658.1027 | NaN | NaN | NaN | 715.8372 | NaN | NaN | NaN | 402.6359 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.492 | NaN | 22.8933
10808.1292 | 739.3737 | 643.89 | 455.5195 | 450.3163 | 465.3085 | 709.1598 | 668.7111 | 653.3066 | NaN | NaN | NaN | 720.3166 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.6748 | NaN | 22.698
10809.1292 | 739.9309 | 643.7339 | 455.7735 | 450.1492 | 465.1521 | 700.9484 | 662.0393 | 645.5575 | NaN | NaN | NaN | 748.8318 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.1077 | NaN | 22.8882
10810.1292 | 741.3195 | 643.5574 | 455.5953 | 450.5495 | 465.8511 | 701.4301 | 659.7831 | 644.428 | NaN | NaN | NaN | 735.6667 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.8851 | NaN | 22.0622
10811.1292 | 742.3738 | 644.0735 | 455.5175 | 450.1311 | 465.2128 | 712.9704 | 656.9125 | 643.6139 | NaN | NaN | NaN | 762.5638 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.3705 | NaN | 18.3368
10812.1292 | 740.6533 | 643.675 | 455.3813 | 450.4298 | 464.8711 | 705.9335 | 654.4047 | 657.0946 | NaN | NaN | NaN | 778.4837 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.4845 | NaN | 24.4036
10813.1292 | 740.1232 | 643.4671 | 456.0291 | 450.566 | 465.1782 | 707.9158 | 652.1867 | 650.7078 | NaN | NaN | NaN | 734.2217 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.7806 | NaN | 22.7896
10814.1292 | 741.5997 | 643.5936 | 455.549 | 450.5416 | 465.2484 | 700.3372 | 651.4079 | 661.7585 | NaN | NaN | NaN | 748.1214 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.8002 | NaN | 22.3471
10815.1292 | 743.8603 | 643.7087 | 455.9931 | 450.8136 | 464.7817 | 698.4979 | 649.0397 | 653.8097 | NaN | NaN | NaN | 761.1651 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.0162 | NaN | 22.6499
10816.1292 | 747.4431 | 644.5329 | 455.794 | 450.9562 | 464.0775 | 687.5082 | 645.936 | 649.718 | NaN | NaN | NaN | 734.021 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.498 | NaN | 24.6868
10817.1292 | 751.5737 | 645.4489 | 455.943 | 451.001 | 464.0888 | 679.654 | 643.3998 | 644.3736 | NaN | NaN | NaN | 707.7934 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.1611 | NaN | 23.3458
10818.1292 | 753.3237 | 645.5294 | 456.07 | 451.4471 | 464.048 | 675.5236 | 640.3229 | 640.4296 | NaN | NaN | NaN | 679.925 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.6564 | NaN | 23.6544
10819.1292 | 752.983 | 645.1616 | 456.8808 | 451.3197 | 463.8481 | 674.7953 | 638.232 | 637.0646 | NaN | NaN | NaN | 659.9786 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.983 | NaN | 23.5579
10820.1292 | 752.7033 | 645.1017 | 456.7992 | 451.1642 | 463.2731 | 681.4009 | 653.2374 | 632.5307 | NaN | NaN | NaN | 649.5795 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.9497 | NaN | 22.8856
10821.1292 | 750.2949 | 644.7523 | 456.726 | 451.5956 | 463.458 | 683.5 | 664.1772 | 653.7781 | NaN | NaN | NaN | 680.591 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.5189 | NaN | 23.5247
10822.1292 | 747.7069 | 645.005 | 456.5917 | 451.1525 | 463.0382 | 682.0889 | 660.5519 | 661.3921 | NaN | NaN | NaN | 680.337 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.9928 | NaN | 22.2734
10823.1292 | 748.0871 | 646.005 | 456.5527 | 450.8465 | 462.8938 | 675.0227 | 656.454 | 660.9862 | NaN | NaN | NaN | 677.8435 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.2784 | NaN | 23.8396
10824.1292 | 752.4291 | 647.4203 | 456.6021 | 451.0441 | 462.7309 | 670.3384 | 652.9617 | 655.9963 | NaN | NaN | NaN | 673.85 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.0372 | NaN | 24.0096
10825.1292 | 754.8126 | 647.3261 | 456.9565 | 451.2187 | 463.2816 | 674.1553 | 648.6587 | 648.4635 | NaN | NaN | NaN | 655.1513 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.2863 | NaN | 24.6697
10826.1292 | 756.0792 | 647.3115 | 457.6345 | 451.03 | 463.3661 | 676.5123 | 652.8524 | 643.6332 | NaN | NaN | NaN | 636.9695 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.5713 | NaN | 22.7446
10827.1292 | 755.9588 | 647.098 | 458.5041 | 451.2864 | 463.7079 | 675.8974 | 660.8783 | 640.4858 | NaN | NaN | NaN | 671.7032 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.677 | NaN | 23.3359
10828.1292 | 755.3776 | 647.5833 | 458.366 | 451.3841 | 463.912 | 684.7731 | 657.8498 | 640.6577 | NaN | NaN | NaN | 650.0427 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.5587 | NaN | 24.7992
10829.1292 | 753.5829 | 647.7751 | 458.6047 | 451.1378 | 464.0914 | 689.9164 | 660.2337 | 645.6773 | NaN | NaN | NaN | 635.3043 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.0226 | NaN | 22.9271
10830.1292 | 751.5798 | 647.3819 | 459.1555 | 451.4382 | 464.3011 | 695.7503 | 660.9689 | 644.003 | NaN | NaN | NaN | 647.5424 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 16.0116 | NaN | 24.2564
10831.1292 | 748.6267 | 647.1506 | 458.7986 | 451.4018 | 464.4384 | 701.6651 | 659.1684 | 653.9931 | NaN | NaN | NaN | 648.6604 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.4015 | NaN | 23.1569
10832.1292 | 750.1717 | 645.8395 | 458.948 | 451.0546 | 464.6466 | 698.4106 | 668.2491 | 645.2682 | NaN | NaN | NaN | 637.9924 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.9654 | NaN | 23.9027
10833.1292 | 754.268 | 645.7964 | 459.4245 | 450.696 | 463.9997 | 695.9147 | 667.652 | 660.1701 | NaN | NaN | NaN | 660.623 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.9646 | NaN | 22.7951
10834.1292 | 757.3327 | 645.7528 | 460.3309 | 451.1556 | 463.9795 | 694.5406 | 662.4621 | 658.6051 | NaN | NaN | NaN | 690.3557 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.25 | NaN | 25.4271
10835.1292 | 756.0498 | 646.9029 | 460.1369 | 451.1156 | 463.9464 | 694.6413 | 663.4864 | 651.1504 | NaN | NaN | NaN | 690.1286 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 16.2854 | NaN | 23.755
10836.1292 | 756.9336 | 646.2865 | 460.0704 | 451.2249 | 463.947 | 689.093 | 658.7886 | 642.4617 | NaN | NaN | NaN | 675.2817 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.8847 | NaN | 22.7747
10837.1292 | 756.5882 | 645.3406 | 460.2968 | 451.2247 | 463.6666 | 690.6333 | 658.5602 | 636.2017 | NaN | NaN | NaN | 662.0809 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.3398 | NaN | 24.2958
10838.1292 | 753.6311 | 645.1043 | 460.4503 | 451.2431 | 463.434 | 693.7558 | 673.4414 | 644.8112 | NaN | NaN | NaN | 659.9257 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.3501 | NaN | 25.2955
10839.1292 | 751.0981 | 645.2275 | 460.4232 | 451.1204 | 463.1702 | 696.983 | 675.3426 | 648.0567 | NaN | NaN | NaN | 659.924 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.5172 | NaN | 23.3472
10840.1292 | 748.9525 | 644.702 | 460.0642 | 451.1028 | 463.1115 | 692.514 | 669.9664 | 649.2297 | NaN | NaN | NaN | 681.1699 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.8561 | NaN | 22.4551
10841.1292 | 748.3997 | 644.7761 | 460.1925 | 451.3265 | 463.6018 | 690.453 | 665.7143 | 652.2761 | NaN | NaN | NaN | 699.5385 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.7372 | NaN | 23.7932
10842.1292 | 748.0009 | 644.4571 | 460.0219 | 451.602 | 463.9757 | 690.4476 | 670.8008 | 663.0763 | NaN | NaN | NaN | 695.4958 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.6059 | NaN | 23.312
10843.1292 | 745.9447 | 644.4852 | 459.9949 | 451.4993 | 464.5377 | 693.76 | 672.9726 | 657.6556 | NaN | NaN | NaN | 691.2799 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.8712 | NaN | 24.4985
10844.1292 | 744.2613 | 644.6681 | 459.9967 | 452.0054 | 465.673 | 693.032 | 680.986 | 658.6762 | NaN | NaN | NaN | 687.247 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.5158 | NaN | 24.2107
10845.1448 | 741.9475 | 644.7015 | 460.1951 | 452.4037 | 465.8531 | 700.298 | 685.4088 | 670.1483 | NaN | NaN | NaN | 689.7939 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.0226 | NaN | 22.5862
10846.1292 | 741.7317 | 644.7399 | 459.9794 | 453.4482 | 466.8458 | 698.069 | 687.8234 | 661.6748 | NaN | NaN | NaN | 690.5676 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.0401 | NaN | 24.2246
10847.1292 | 740.8577 | 644.7156 | 460.0925 | 453.1065 | 466.5366 | 702.0977 | 686.7616 | 668.6053 | NaN | NaN | NaN | 676.5048 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.6942 | NaN | 24.0468
10848.1292 | 741.2156 | 644.8836 | 459.7343 | 452.9575 | 466.7618 | 702.7053 | 689.2692 | 678.3756 | NaN | NaN | NaN | 687.1749 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.7073 | NaN | 22.1088
10849.1292 | 740.8961 | 644.8204 | 459.7055 | 452.5531 | 467.126 | 707.6428 | 684.7434 | 679.6563 | NaN | NaN | NaN | 685.0511 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.1134 | NaN | 21.1808
10850.1292 | 740.8112 | 644.5202 | 459.7954 | 452.5106 | 466.8234 | 704.8566 | 684.502 | 683.0947 | NaN | NaN | NaN | 715.0931 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.7365 | NaN | 24.0538
10851.1292 | 740.212 | 644.2209 | 460.2749 | 452.3243 | 467.0011 | 705.3006 | 680.6332 | 674.3519 | NaN | NaN | NaN | 706.6105 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.4877 | NaN | 23.5114
10852.1292 | 738.9998 | 643.6773 | 460.1236 | 452.5016 | 467.0515 | 702.1502 | 683.0014 | 674.6564 | NaN | NaN | NaN | 677.1679 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.4123 | NaN | 23.425
10853.1292 | 738.2904 | 643.1475 | 460.3087 | 453.1842 | 467.1963 | 704.8932 | 690.1503 | 672.5957 | NaN | NaN | NaN | 700.7262 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.7054 | NaN | 23.9627
10854.1292 | 737.0651 | 642.78 | 460.1239 | 452.9951 | 467.2845 | 702.3244 | 687.3161 | 676.9618 | NaN | NaN | NaN | 712.9048 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.5807 | NaN | 22.0408
10855.1292 | 735.6354 | 642.3606 | 460.4286 | 452.8583 | 467.3194 | 702.1939 | 687.2777 | 679.7153 | NaN | NaN | NaN | 729.527 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.2252 | NaN | 23.3646
10856.1292 | 734.3741 | 642.1029 | 460.7057 | 452.8391 | 467.2535 | 699.8229 | 687.4203 | 680.5418 | NaN | NaN | NaN | 730.9995 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.0058 | NaN | 22.7176
10857.1292 | 735.0106 | 641.686 | 460.9853 | 452.8081 | 467.2097 | 698.78 | 685.7847 | 682.6857 | NaN | NaN | NaN | 734.2099 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.1409 | NaN | 21.707
10858.1292 | 738.4105 | 642.4696 | 461.232 | 452.9017 | 466.7644 | 697.2052 | 679.2687 | 681.4192 | NaN | NaN | NaN | 723.4056 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.5549 | NaN | 21.7633
10859.1292 | 741.6338 | 642.2481 | 461.1699 | 452.8299 | 466.2518 | 699.5251 | 674.4808 | 675.1367 | NaN | NaN | NaN | 724.1684 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.8964 | NaN | 23.3904
10860.1292 | 739.6771 | 642.2096 | 461.2986 | 453.1625 | 465.825 | 701.6281 | 670.3322 | 682.1957 | NaN | NaN | NaN | 733.9482 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.4009 | NaN | 22.7476
10861.1292 | 737.8585 | 642.1346 | 462.746 | 453.3881 | 466.1015 | 695.3665 | 678.7765 | 685.7834 | NaN | NaN | NaN | 730.2384 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.291 | NaN | 21.7081
10862.1292 | 737.1484 | 642.1446 | 462.6434 | 453.6717 | 465.9531 | 691.6779 | 672.9446 | 681.9375 | NaN | NaN | NaN | 698.0779 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.2444 | NaN | 22.9881
10863.1292 | 736.7334 | 642.3297 | 464.3854 | 453.9096 | 466.0527 | 687.9657 | 681.0628 | 695.2693 | NaN | NaN | NaN | 694.6807 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.8669 | NaN | 23.6376
10864.1292 | 735.4913 | 641.8884 | 464.4192 | 454.4247 | 465.8435 | 688.1456 | 678.2134 | 693.7951 | NaN | NaN | NaN | 711.5681 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.5807 | NaN | 23.013
10865.1292 | 735.1918 | 640.8961 | 464.291 | 454.764 | 466.044 | 690.9012 | 681.2149 | 688.1146 | NaN | NaN | NaN | 713.907 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.9944 | NaN | 23.3992
10866.1292 | 733.1231 | 641.3563 | 464.1065 | 454.9342 | 466.3638 | 688.8343 | 678.7391 | 689.1321 | NaN | NaN | NaN | 701.8685 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.5816 | NaN | 22.7174
10867.1292 | 732.9083 | 641.1233 | 463.9999 | 454.4361 | 465.9926 | 691.7404 | 680.3742 | 694.8484 | NaN | NaN | NaN | 704.2542 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.885 | NaN | 22.1331
10868.1292 | 732.1796 | 640.9578 | 463.952 | 453.9998 | 466.0462 | 692.9394 | 673.3159 | 692.4986 | NaN | NaN | NaN | 707.5963 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.9041 | NaN | 22.0994
10869.1292 | 733.1049 | 641.0258 | 464.068 | 453.97 | 465.8866 | 695.4844 | 672.8462 | 689.3787 | NaN | NaN | NaN | 708.8943 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.1188 | NaN | 22.7563
10870.1292 | 732.7209 | 642.5893 | 464.0481 | 454.4601 | 466.0371 | 694.5628 | 670.9621 | 688.6059 | NaN | NaN | NaN | 701.3404 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.8933 | NaN | 24.0926
10871.1292 | 731.9775 | 642.7631 | 464.2634 | 454.3414 | 465.9778 | 697.7053 | 671.754 | 685.855 | NaN | NaN | NaN | 694.7004 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.5864 | NaN | 24.5972
10872.1292 | 729.0205 | 641.7847 | 464.933 | 454.745 | 465.8314 | 697.82 | 681.6947 | 676.1752 | NaN | NaN | NaN | 695.4867 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.2719 | NaN | 23.4107
10873.1292 | 727.2534 | 640.7176 | 465.1511 | 454.9681 | 465.5767 | 696.7513 | 686.136 | 675.7011 | NaN | NaN | NaN | 681.1305 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.2093 | NaN | 23.1515
10874.1292 | 727.1601 | 638.9034 | 465.3479 | 454.8807 | 465.708 | 693.1791 | 685.1195 | 678.8176 | NaN | NaN | NaN | 668.9167 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.8793 | NaN | 22.4433
10875.1292 | 729.0055 | 638.8292 | 465.1704 | 454.5957 | 466.2769 | 693.753 | 684.9467 | 674.4552 | NaN | NaN | NaN | 643.9469 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.3989 | NaN | 22.7784
10876.1292 | 733.416 | 639.5412 | 464.6379 | 454.2768 | 466.2123 | 700.6472 | 683.5724 | 679.4328 | NaN | NaN | NaN | 669.0872 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.6663 | NaN | 23.9147
10877.1292 | 734.4149 | 640.1949 | 464.5377 | 454.3157 | 465.9369 | 701.8692 | 675.1375 | 675.8113 | NaN | NaN | NaN | 691.7518 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.0205 | NaN | 22.5495
10878.1292 | 735.3662 | 640.7449 | 464.374 | 454.5631 | 465.7645 | 698.3494 | 678.3689 | 671.8013 | NaN | NaN | NaN | 704.1172 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.7957 | NaN | 23.4106
10879.1292 | 738.9525 | 640.4673 | 463.9668 | 454.3766 | 465.8751 | 695.8984 | 675.7221 | 676.181 | NaN | NaN | NaN | 678.7204 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.1188 | NaN | 24.7828
10880.1292 | 741.6252 | 640.9858 | 463.7655 | 454.1595 | 465.4559 | 698.5175 | 677.8621 | 685.8591 | NaN | NaN | NaN | 643.5726 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.5006 | NaN | 23.0804
10881.1292 | 742.4283 | 641.6166 | 463.7378 | 454.1495 | 465.3929 | 708.9018 | 680.9596 | 689.4578 | NaN | NaN | NaN | 652.1442 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.8385 | NaN | 21.0836
10882.1292 | 746.3813 | 641.8114 | 463.4586 | 454.0997 | 465.7457 | 715.744 | 672.3922 | 679.6231 | NaN | NaN | NaN | 647.0351 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.5605 | NaN | 24.4893
10883.1292 | 748.5768 | 642.1097 | 463.3598 | 454.4573 | 465.8524 | 714.4387 | 668.77 | 670.0183 | NaN | NaN | NaN | 642.6597 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.3943 | NaN | 24.1908
10884.1292 | 749.0944 | 642.3558 | 463.1982 | 454.1778 | 465.9925 | 711.4351 | 663.2666 | 664.0808 | NaN | NaN | NaN | 673.8628 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.1939 | NaN | 23.1595
10885.1292 | 746.182 | 642.6187 | 463.2173 | 454.5786 | 466.4558 | 723.9427 | 662.3748 | 658.7667 | NaN | NaN | NaN | 689.57 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.9451 | NaN | 24.2582
10886.1292 | 743.7863 | 641.6797 | 463.4563 | 454.3427 | 466.4793 | 713.6168 | 661.3551 | 669.9308 | NaN | NaN | NaN | 699.591 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 16.2054 | NaN | 22.4454
10887.1292 | 741.1739 | 641.3317 | 464.0423 | 454.6608 | 466.1779 | 712.8217 | 670.1545 | 677.0713 | NaN | NaN | NaN | 689.2564 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.9107 | NaN | 21.6911
10888.1292 | 739.8992 | 640.9511 | 464.032 | 454.4879 | 465.9751 | 718.1936 | 673.2514 | 668.5944 | NaN | NaN | NaN | 700.9258 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.7248 | NaN | 24.4535
10889.1292 | 741.3481 | 641.2291 | 463.8714 | 454.4726 | 465.5839 | 712.9616 | 674.7274 | 659.619 | NaN | NaN | NaN | 711.6636 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.0405 | NaN | 23.9329
10890.1292 | 742.4472 | 641.2687 | 463.8979 | 454.3419 | 465.3366 | 713.2352 | 669.2819 | 663.8266 | NaN | NaN | NaN | 740.1876 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.2059 | NaN | 23.5522
10891.1292 | 745.3353 | 641.7087 | 463.9718 | 454.3404 | 464.9826 | 711.4824 | 671.7512 | 659.3759 | NaN | NaN | NaN | 735.8087 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.3805 | NaN | 23.205
10892.1292 | 749.5146 | 642.3173 | 464.022 | 454.7301 | 465.1882 | 706.0612 | 666.9326 | 655.3005 | NaN | NaN | NaN | 746.9718 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.5996 | NaN | 22.2906
10893.1292 | 751.9593 | 642.7172 | 464.1578 | 454.7846 | 464.824 | 702.2552 | 661.5139 | 653.0526 | NaN | NaN | NaN | 744.0885 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.5824 | NaN | 22.037
10894.1292 | 754.3127 | 644.9792 | 464.1567 | 454.7703 | 464.7865 | 704.1758 | 656.6033 | 645.9001 | NaN | NaN | NaN | 756.5304 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.185 | NaN | 23.6355
10895.1292 | 754.5835 | 645.3814 | 463.8376 | 454.77 | 464.9315 | 701.9582 | 652.2275 | 640.8545 | NaN | NaN | NaN | 760.6581 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.494 | NaN | 23.9868
10896.1292 | 754.2167 | 645.3237 | 463.9497 | 454.6392 | 465.1673 | 704.4746 | 649.0238 | 638.0598 | NaN | NaN | NaN | 774.9427 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.754 | NaN | 24.3502
10897.1292 | 755.8048 | 645.1876 | 463.948 | 455.095 | 465.5159 | 710.4132 | 649.0943 | 633.0825 | NaN | NaN | NaN | 761.0675 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.4989 | NaN | 20.5188
10898.1292 | 753.3675 | 645.2088 | 463.9497 | 455.2002 | 466.3878 | 707.3356 | 651.0201 | 630.9642 | NaN | NaN | NaN | 713.8355 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.1698 | NaN | 22.4024
10899.1292 | 750.2663 | 643.7823 | 464.2739 | 455.1088 | 466.4349 | 707.3814 | 662.3278 | 628.1978 | NaN | NaN | NaN | 715.1986 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.4365 | NaN | 21.2818
10900.1292 | 748.9789 | 643.9431 | 464.8194 | 454.897 | 466.3025 | 707.9562 | 664.0222 | 633.1858 | NaN | NaN | NaN | 677.7086 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.2773 | NaN | 23.2439
10901.1292 | 747.3421 | 643.6417 | 464.9617 | 455.1271 | 466.3854 | 714.6173 | 673.8104 | 640.2302 | NaN | NaN | NaN | 683.7761 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 16.0614 | NaN | 23.6358
10902.1292 | 746.9057 | 643.9746 | 464.7304 | 455.1734 | 466.4652 | 716.4673 | 675.8873 | 651.3189 | NaN | NaN | NaN | 692.8223 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.5474 | NaN | 24.1868
10903.1292 | 747.1636 | 643.9406 | 464.5529 | 455.0397 | 466.9526 | 723.3996 | 683.2044 | 654.8762 | NaN | NaN | NaN | 697.5849 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.6636 | NaN | 24.8693
10904.1292 | 747.2727 | 644.9549 | 464.3474 | 454.8283 | 466.6775 | 720.0639 | 682.5053 | 654.2127 | NaN | NaN | NaN | 709.5969 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.1652 | NaN | 23.8259
10905.1448 | 747.3738 | 644.5704 | 464.3158 | 454.8794 | 466.7237 | 715.6371 | 678.1498 | 653.4636 | NaN | NaN | NaN | 687.9663 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.4144 | NaN | 22.1922
10906.1292 | 747.8159 | 644.6266 | 464.1512 | 454.7921 | 466.8315 | 710.4698 | 671.6592 | 648.2027 | NaN | NaN | NaN | 703.1832 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.4608 | NaN | 22.919
10907.1292 | 746.6867 | 643.8453 | 464.1712 | 454.9387 | 467.1102 | 712.5662 | 664.2265 | 650.6013 | NaN | NaN | NaN | 713.0541 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.5702 | NaN | 22.5266
10908.1292 | 748.9247 | 643.1791 | 464.4368 | 454.6964 | 467.1481 | 704.3417 | 665.8695 | 656.6737 | NaN | NaN | NaN | 689.5402 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.9187 | NaN | 23.6627
10909.1292 | 750.3189 | 642.7185 | 464.2439 | 454.3805 | 467.7037 | 707.0898 | 663.7499 | 655.9031 | NaN | NaN | NaN | 661.7061 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.3807 | NaN | 24.5348
10910.1292 | 751.2379 | 642.0542 | 464.001 | 454.3943 | 467.4349 | 704.7287 | 661.585 | 650.9903 | NaN | NaN | NaN | 662.6281 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.7747 | NaN | 21.7335
10911.1292 | 750.4695 | 642.4909 | 463.6776 | 454.3206 | 467.5747 | 712.5067 | 668.2131 | 647.57 | NaN | NaN | NaN | 642.7206 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.5545 | NaN | 21.3993
10912.1292 | 748.287 | 642.3283 | 463.7229 | 454.8141 | 467.657 | 714.5741 | 673.2537 | 646.648 | NaN | NaN | NaN | 629.8103 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.1196 | NaN | 22.728
10913.1292 | 747.4655 | 642.4 | 463.9149 | 454.884 | 467.8048 | 713.2943 | 682.3068 | 653.5785 | NaN | NaN | NaN | 668.009 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.6942 | NaN | 22.8043
10914.1292 | 746.759 | 642.3162 | 463.9818 | 455.056 | 468.4457 | 713.1966 | 682.6655 | 660.4927 | NaN | NaN | NaN | 687.0513 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.7404 | NaN | 23.5796
10915.1292 | 747.2896 | 642.7522 | 463.8979 | 455.0918 | 468.6954 | 708.8368 | 681.0307 | 665.2606 | NaN | NaN | NaN | 673.4559 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.3433 | NaN | 23.8573
10916.1292 | 749.8599 | 643.0727 | 463.7686 | 455.0545 | 468.4352 | 705.5034 | 675.2329 | 665.4452 | NaN | NaN | NaN | 660.8005 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.6325 | NaN | 22.4138
10917.1292 | 749.8575 | 643.8312 | 463.7582 | 455.1072 | 468.3976 | 704.4732 | 670.0224 | 662.3127 | NaN | NaN | NaN | 672.3863 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.1491 | NaN | 22.5918
10918.1292 | 747.865 | 643.2482 | 464.2275 | 455.5332 | 468.0767 | 701.0531 | 663.3292 | 664.1269 | NaN | NaN | NaN | 697.5685 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 22.3126 | NaN | 21.8195
10919.1292 | 750.1963 | 642.6108 | 464.9099 | 455.9779 | 467.8491 | 700.2511 | 674.9024 | 677.5103 | NaN | NaN | NaN | 692.0773 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.4801 | NaN | 21.8461
10920.1292 | 748.8001 | 642.656 | 464.9666 | 455.8409 | 467.8602 | 711.1565 | 668.6918 | 673.6707 | NaN | NaN | NaN | 701.8088 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.7651 | NaN | 24.0975
10921.1292 | 747.1874 | 642.3006 | 465.1487 | 455.5707 | 467.1262 | 708.3776 | 667.6034 | 677.8522 | NaN | NaN | NaN | 691.3662 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.8199 | NaN | 22.2958
10922.1292 | 743.5787 | 641.3711 | 465.2685 | 455.7289 | 466.7179 | 704.3179 | 662.3437 | 670.6506 | NaN | NaN | NaN | 691.8275 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.0921 | NaN | 25.2444
10923.1292 | 744.0271 | 640.3314 | 465.5071 | 455.7401 | 466.3189 | 696.5422 | 660.6363 | 663.5394 | NaN | NaN | NaN | 681.372 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.4013 | NaN | 22.2896
10924.1292 | 748.3408 | 640.6531 | 465.1688 | 455.8085 | 466.3563 | 695.8546 | 655.5702 | 665.6097 | NaN | NaN | NaN | 685.7588 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.1284 | NaN | 24.6205
10925.1292 | 750.6867 | 642.1282 | 464.8809 | 455.7247 | 466.6643 | 690.9489 | 652.4531 | 669.0177 | NaN | NaN | NaN | 655.5906 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.4832 | NaN | 23.163
10926.1292 | 749.8899 | 642.5147 | 465.1654 | 455.8477 | 466.586 | 684.4096 | 647.4501 | 664.6067 | NaN | NaN | NaN | 659.0827 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.1389 | NaN | 23.4452
10927.1292 | 748.822 | 642.8505 | 465.339 | 455.7588 | 466.4896 | 679.4522 | 643.4308 | 662.5559 | NaN | NaN | NaN | 641.3818 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.7034 | NaN | 23.4596
10928.1292 | 750.0704 | 642.849 | 465.2779 | 455.9892 | 466.7926 | 674.8688 | 642.5264 | 665.4911 | NaN | NaN | NaN | 634.7663 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.0714 | NaN | 20.7876
10929.1292 | 749.6914 | 643.099 | 465.3766 | 455.9939 | 466.396 | 687.1786 | 646.8828 | 667.5784 | NaN | NaN | NaN | 663.5632 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.5207 | NaN | 22.691
10930.1292 | 748.0184 | 643.3038 | 465.3644 | 455.9911 | 466.1166 | 688.7971 | 646.3456 | 665.7345 | NaN | NaN | NaN | 678.439 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.4704 | NaN | 23.0314
10931.1292 | 748.5737 | 643.1266 | 465.3628 | 455.9915 | 465.914 | 687.944 | 644.0898 | 665.1652 | NaN | NaN | NaN | 655.7772 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.5804 | NaN | 22.2486
10932.1292 | 745.0972 | 643.3092 | 465.4546 | 456.0252 | 465.7167 | 687.7307 | 649.2256 | 664.1246 | NaN | NaN | NaN | 659.9505 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.1505 | NaN | 21.6317
10933.1292 | 744.7419 | 643.0587 | 465.7576 | 456.0206 | 465.9703 | 686.6274 | 648.0535 | 663.2791 | NaN | NaN | NaN | 658.8766 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.693 | NaN | 23.4049
10934.1292 | 743.2152 | 643.5371 | 465.5502 | 456.6098 | 466.2639 | 697.1591 | 650.928 | 667.3741 | NaN | NaN | NaN | 623.1937 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.9671 | NaN | 22.8125
10935.1292 | 740.9116 | 643.3541 | 465.9426 | 456.8868 | 467.2609 | 700.4466 | 654.4036 | 682.3256 | NaN | NaN | NaN | 611.7454 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.6002 | NaN | 24.6456
10936.1292 | 739.4927 | 643.2942 | 466.0049 | 456.8525 | 466.9884 | 700.0089 | 665.6309 | 675.0794 | NaN | NaN | NaN | 623.5828 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.9206 | NaN | 23.0305
10937.1292 | 740.1787 | 643.1816 | 465.9473 | 456.8199 | 467.0218 | 701.8561 | 665.9354 | 676.5478 | NaN | NaN | NaN | 617.1105 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.5769 | NaN | 23.3141
10938.1292 | 738.9814 | 642.6782 | 465.7827 | 456.8067 | 467.2772 | 698.2853 | 660.4479 | 667.3399 | NaN | NaN | NaN | 617.7887 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.3177 | NaN | 23.8615
10939.1292 | 739.1907 | 642.6105 | 465.8302 | 456.4702 | 466.7227 | 690.5269 | 661.406 | 657.529 | NaN | NaN | NaN | 620.0445 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.7107 | NaN | 23.1181
10940.1292 | 740.7978 | 642.1208 | 465.8364 | 456.4631 | 466.2764 | 695.1865 | 665.6629 | 659.9025 | NaN | NaN | NaN | 643.7469 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.4597 | NaN | 23.148
10941.1292 | 742.254 | 641.578 | 465.7724 | 456.6887 | 466.5906 | 693.3849 | 664.2486 | 664.1861 | NaN | NaN | NaN | 674.4148 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.5339 | NaN | 22.8813
10942.1292 | 740.8561 | 641.8521 | 465.6475 | 456.6724 | 466.6066 | 690.4213 | 660.0348 | 666.7706 | NaN | NaN | NaN | 676.6563 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.3262 | NaN | 23.3799
10943.1292 | 741.0692 | 643.0953 | 465.8235 | 456.3959 | 466.4265 | 684.5667 | 663.8101 | 672.9889 | NaN | NaN | NaN | 649.3291 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.3148 | NaN | 23.6529
10944.1292 | 742.7617 | 643.7306 | 465.9472 | 456.4529 | 466.705 | 677.6315 | 658.1364 | 671.2534 | NaN | NaN | NaN | 657.159 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.6396 | NaN | 24.2596
10945.1292 | 744.9216 | 643.6826 | 465.7151 | 456.2567 | 466.5923 | 671.4505 | 653.628 | 675.0771 | NaN | NaN | NaN | 672.9437 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.1395 | NaN | 22.2598
10946.1292 | 746.9845 | 644.6307 | 465.7615 | 456.4814 | 466.6239 | 674.6655 | 651.692 | 676.4433 | NaN | NaN | NaN | 679.7996 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.6946 | NaN | 24.9282
10947.1292 | 747.3045 | 645.1537 | 465.8159 | 456.5432 | 466.6078 | 677.0168 | 650.4555 | 674.2319 | NaN | NaN | NaN | 675.5569 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.9157 | NaN | 23.5895
10948.1292 | 747.8918 | 645.6111 | 466.2508 | 456.794 | 466.4736 | 681.8472 | 648.6418 | 667.5355 | NaN | NaN | NaN | 661.2355 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.165 | NaN | 24.2524
10949.1292 | 748.1771 | 645.4192 | 466.1606 | 457.4675 | 467.4149 | 687.6532 | 649.3694 | 666.9068 | NaN | NaN | NaN | 636.465 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.9365 | NaN | 22.9602
10950.1292 | 748.2566 | 645.3738 | 466.1596 | 457.455 | 468.0424 | 687.631 | 652.005 | 659.7526 | NaN | NaN | NaN | 622.7228 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.4246 | NaN | 24.2128
10951.1292 | 748.0238 | 645.7357 | 466.2251 | 457.2952 | 468.0373 | 696.6907 | 660.0672 | 655.0952 | NaN | NaN | NaN | 615.7517 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.3644 | NaN | 24.3858
10952.1292 | 746.6438 | 646.021 | 466.13 | 457.4587 | 468.1523 | 699.1847 | 659.9212 | 650.4141 | NaN | NaN | NaN | 616.3804 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.2183 | NaN | 24.2254
10953.1292 | 743.9879 | 645.7889 | 466.147 | 457.4182 | 468.2333 | 704.1643 | 666.2055 | 648.2453 | NaN | NaN | NaN | 641.3461 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.993 | NaN | 23.9173
10954.1292 | 739.7945 | 645.2685 | 466.1739 | 457.3967 | 468.0458 | 710.1981 | 677.8398 | 654.5945 | NaN | NaN | NaN | 663.1983 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.7072 | NaN | 21.911
10955.1292 | 736.7458 | 644.4492 | 466.4454 | 457.2823 | 467.7075 | 704.9033 | 678.955 | 650.4134 | NaN | NaN | NaN | 671.301 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.2172 | NaN | 23.8902
10956.1292 | 734.5854 | 643.5635 | 466.2946 | 457.3223 | 467.977 | 701.6551 | 686.7511 | 657.6117 | NaN | NaN | NaN | 674.2458 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.5783 | NaN | 24.1356
10957.1292 | 735.4773 | 643.5202 | 466.2506 | 457.4228 | 468.1256 | 700.3936 | 683.0153 | 657.8539 | NaN | NaN | NaN | 683.6746 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.522 | NaN | 23.8238
10958.1292 | 734.1285 | 642.9346 | 466.5128 | 457.586 | 468.3747 | 700.02 | 685.4702 | 660.2532 | NaN | NaN | NaN | 681.3941 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.7015 | NaN | 23.646
10959.1292 | 732.8164 | 642.656 | 467.069 | 457.7025 | 468.1158 | 696.8029 | 682.1043 | 652.4893 | NaN | NaN | NaN | 675.1305 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.4736 | NaN | 23.2647
10960.1292 | 732.439 | 642.2767 | 467.3081 | 457.7246 | 468.0956 | 694.9652 | 675.804 | 653.4683 | NaN | NaN | NaN | 680.2446 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.5724 | NaN | 21.5602
10961.1292 | 732.9353 | 641.961 | 467.2913 | 457.7877 | 468.4585 | 691.6103 | 685.7274 | 658.5516 | NaN | NaN | NaN | 695.6027 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.4078 | NaN | 23.0013
10962.1292 | 732.2707 | 640.592 | 466.9383 | 457.9499 | 469.3209 | 692.7076 | 677.6647 | 662.7565 | NaN | NaN | NaN | 694.3417 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.3684 | NaN | 23.017
10963.1292 | 733.7936 | 640.6795 | 466.5744 | 457.7258 | 469.6044 | 695.9592 | 684.8489 | 659.5427 | NaN | NaN | NaN | 690.3633 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 66.3524 | NaN | 21.7254
10964.1292 | 735.0751 | 640.6349 | 466.2292 | 457.6109 | 469.8319 | 695.8174 | 687.1624 | 651.1034 | NaN | NaN | NaN | 693.3532 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.5461 | NaN | 20.0309
10965.1448 | 739.5324 | 641.0368 | 466.0518 | 457.5284 | 469.958 | 698.5966 | 681.2071 | 646.1878 | NaN | NaN | NaN | 711.3205 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.77 | NaN | 23.674
10966.1292 | 739.2444 | 641.5726 | 466.0691 | 457.5406 | 469.4221 | 704.0878 | 675.9528 | 645.901 | NaN | NaN | NaN | 711.1117 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 30.2804 | NaN | 22.9982
10967.1292 | 737.3485 | 641.6519 | 466.1285 | 457.5878 | 469.0802 | 715.4499 | 670.9549 | 653.8029 | NaN | NaN | NaN | 714.3229 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.5879 | NaN | 23.2881
10968.1292 | 738.6447 | 641.6393 | 466.288 | 457.5626 | 469.1228 | 709.3934 | 678.8019 | 657.4797 | NaN | NaN | NaN | 692.3427 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.7131 | NaN | 23.5414
10969.1292 | 737.4147 | 642.0457 | 466.6201 | 457.6675 | 469.7819 | 710.4882 | 678.8115 | 657.3743 | NaN | NaN | NaN | 661.9814 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.8612 | NaN | 19.3788
10970.1292 | 735.3902 | 642.655 | 466.5954 | 457.3246 | 469.4533 | 707.9803 | 681.666 | 659.3349 | NaN | NaN | NaN | 667.5291 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.3332 | NaN | 23.9407
10971.1292 | 734.5599 | 643.2294 | 466.835 | 457.4026 | 469.3869 | 707.6395 | 685.6507 | 667.4588 | NaN | NaN | NaN | 680.0745 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.5375 | NaN | 20.5987
10972.1292 | 732.463 | 642.8755 | 466.9264 | 457.8888 | 469.8066 | 711.9182 | 680.5886 | 672.7303 | NaN | NaN | NaN | 656.3868 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.0146 | NaN | 21.3068
10973.1292 | 731.5342 | 642.7809 | 466.7884 | 457.7937 | 470.0893 | 711.5429 | 681.1565 | 668.8505 | NaN | NaN | NaN | 648.0186 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.6257 | NaN | 24.0562
10974.1292 | 730.4729 | 642.3562 | 466.7096 | 457.753 | 470.6461 | 714.4039 | 685.0042 | 668.2605 | NaN | NaN | NaN | 650.6579 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.8414 | NaN | 23.4686
10975.1292 | 731.9188 | 642.159 | 467.3626 | 457.5784 | 470.3287 | 715.3009 | 681.7469 | 670.0902 | NaN | NaN | NaN | 679.3658 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.2129 | NaN | 22.5356
10976.1292 | 733.4046 | 642.4616 | 467.4152 | 457.4424 | 469.9223 | 714.6101 | 681.3651 | 677.5223 | NaN | NaN | NaN | 686.6669 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.2242 | NaN | 22.3955
10977.1292 | 734.1822 | 643.3875 | 468.1298 | 457.4552 | 469.184 | 706.112 | 675.3282 | 674.8156 | NaN | NaN | NaN | 681.9122 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.9308 | NaN | 20.5777
10978.1292 | 735.6526 | 644.1832 | 468.2515 | 457.7403 | 469.009 | 697.7495 | 672.7752 | 675.0297 | NaN | NaN | NaN | 688.352 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.4287 | NaN | 22.3654
10979.1292 | 733.5723 | 644.6843 | 468.5847 | 458.1559 | 469.2023 | 688.9131 | 664.8531 | 663.9047 | NaN | NaN | NaN | 689.3225 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.0119 | NaN | 24.2752
10980.1292 | 733.015 | 644.0712 | 468.9339 | 458.8011 | 468.7937 | 690.2227 | 665.4917 | 668.0829 | NaN | NaN | NaN | 698.6313 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.1796 | NaN | 22.7153
10981.1292 | 732.5072 | 643.3538 | 468.9622 | 459.2059 | 468.9458 | 684.1762 | 665.2416 | 672.9661 | NaN | NaN | NaN | 691.5266 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.0947 | NaN | 23.5506
10982.1292 | 730.7611 | 642.8593 | 468.8822 | 459.1632 | 468.8045 | 682.1435 | 658.2376 | 675.5179 | NaN | NaN | NaN | 687.445 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.8956 | NaN | 22.9259
10983.1292 | 730.8479 | 642.8442 | 469.0865 | 459.0063 | 468.4317 | 676.1947 | 654.5887 | 673.5566 | NaN | NaN | NaN | 690.4102 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 27.5362 | NaN | 22.4286
10984.1292 | 733.1652 | 642.829 | 469.1142 | 459.0589 | 468.0247 | 671.2496 | 659.6406 | 672.9429 | NaN | NaN | NaN | 671.1116 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.5813 | NaN | 23.6681
10985.1292 | 733.9364 | 642.6202 | 469.1619 | 459.0972 | 467.6422 | 671.2472 | 655.4631 | 669.4149 | NaN | NaN | NaN | 654.3936 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.0251 | NaN | 22.7231
10986.1292 | 731.5306 | 642.5236 | 469.4672 | 459.3549 | 467.5942 | 677.0225 | 663.479 | 672.7039 | NaN | NaN | NaN | 655.907 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.0191 | NaN | 23.2719
10987.1292 | 730.4088 | 642.2985 | 470.7508 | 459.7326 | 467.8394 | 681.1824 | 668.784 | 675.1634 | NaN | NaN | NaN | 644.6971 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.2685 | NaN | 24.3292
10988.1292 | 730.7117 | 641.9783 | 471.1544 | 459.9454 | 468.2134 | 681.7367 | 670.3037 | 676.0333 | NaN | NaN | NaN | 649.5238 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.6293 | NaN | 23.588
10989.1292 | 735.3912 | 642.5969 | 471.1303 | 460.1487 | 468.1954 | 679.5373 | 673.4036 | 674.3761 | NaN | NaN | NaN | 662.2638 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.2712 | NaN | 22.4688
10990.1292 | 736.2101 | 645.0456 | 470.9666 | 460.3192 | 468.8792 | 677.9563 | 668.5925 | 667.488 | NaN | NaN | NaN | 640.2771 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.9723 | NaN | 24.7206
10991.1292 | 735.9327 | 645.944 | 471.2054 | 460.1154 | 469.0715 | 685.4056 | 663.8606 | 658.3899 | NaN | NaN | NaN | 615.2131 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.1607 | NaN | 20.9454
10992.1292 | 736.9763 | 645.8016 | 471.3692 | 460.6116 | 468.885 | 688.0286 | 669.3642 | 662.7832 | NaN | NaN | NaN | 596.9664 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 57.0435 | NaN | 23.8713
10993.1292 | 739.1403 | 645.1097 | 471.4595 | 460.6966 | 468.9114 | 683.3682 | 667.5134 | 658.1484 | NaN | NaN | NaN | 599.5457 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.3132 | NaN | 22.8831
10994.1292 | 739.0373 | 644.8435 | 471.6749 | 460.9303 | 468.8637 | 684.1386 | 672.2004 | 665.8996 | NaN | NaN | NaN | 622.809 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.6072 | NaN | 23.0955
10995.1292 | 737.9759 | 644.7049 | 471.8312 | 461.5015 | 470.0487 | 691.0278 | 676.5052 | 660.0981 | NaN | NaN | NaN | 656.983 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.6222 | NaN | 23.0748
10996.1292 | 736.6487 | 644.209 | 471.6609 | 461.0999 | 469.9428 | 700.4898 | 675.1418 | 666.6107 | NaN | NaN | NaN | 669.9472 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.5097 | NaN | 21.4455
10997.1292 | 735.9401 | 644.2349 | 471.3307 | 460.9006 | 469.7802 | 695.6279 | 669.4984 | 673.2515 | NaN | NaN | NaN | 675.6911 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.9855 | NaN | 21.7378
10998.1292 | 733.6222 | 643.6557 | 471.1293 | 461.4482 | 470.3588 | 694.0375 | 664.8887 | 669.0431 | NaN | NaN | NaN | 647.2507 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.4467 | NaN | 22.884
10999.1292 | 732.1492 | 643.6938 | 471.4067 | 461.6379 | 470.6866 | 691.071 | 669.3423 | 671.9491 | NaN | NaN | NaN | 646.3442 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.704 | NaN | 22.1331
11000.1292 | 730.678 | 643.2562 | 472.0892 | 462.0856 | 471.4689 | 693.5612 | 666.5851 | 666.3327 | NaN | NaN | NaN | 631.3131 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.1404 | NaN | 22.152
11001.1292 | 729.124 | 643.3978 | 471.9977 | 461.9701 | 471.221 | 702.4618 | 679.7768 | 660.7595 | NaN | NaN | NaN | 646.1416 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.9887 | NaN | 21.824
11002.1292 | 727.3187 | 642.3821 | 471.7685 | 461.5557 | 471.6934 | 698.5147 | 672.5413 | 651.3625 | NaN | NaN | NaN | 647.7863 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.669 | NaN | 22.2746
11003.1292 | 729.6209 | 642.3048 | 471.3539 | 461.0722 | 471.2001 | 692.758 | 678.693 | 645.132 | NaN | NaN | NaN | 639.8993 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.3061 | NaN | 20.8334
11004.1292 | 732.0396 | 642.0107 | 471.3064 | 460.7288 | 470.9096 | 692.0668 | 676.9688 | 656.8067 | NaN | NaN | NaN | 651.1419 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.4209 | NaN | 22.9405
11005.1292 | 734.2041 | 642.5072 | 471.2226 | 460.4259 | 470.6044 | 703.0726 | 671.1829 | 659.3144 | NaN | NaN | NaN | 634.1554 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.4493 | NaN | 21.7995
11006.1292 | 733.6327 | 643.2872 | 471.2047 | 460.7261 | 470.5952 | 702.2987 | 673.3018 | 659.0376 | NaN | NaN | NaN | 641.8717 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.1376 | NaN | 22.3417
11007.1292 | 732.9213 | 644.0177 | 471.3593 | 461.0264 | 470.7916 | 703.1093 | 675.6511 | 656.6573 | NaN | NaN | NaN | 659.1318 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.3867 | NaN | 24.5286
11008.1292 | 732.0756 | 644.2706 | 471.489 | 461.2511 | 470.9823 | 711.6722 | 682.2863 | 651.6386 | NaN | NaN | NaN | 654.8236 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.4542 | NaN | 22.8073
11009.1292 | 730.743 | 643.9948 | 471.9186 | 461.1006 | 471.0936 | 708.3122 | 686.8673 | 658.0501 | NaN | NaN | NaN | 663.61 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.2543 | NaN | 23.2418
11010.1292 | 730.0611 | 643.4947 | 472.0717 | 461.0553 | 471.3485 | 708.044 | 685.7803 | 649.311 | NaN | NaN | NaN | 662.1378 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.6779 | NaN | 22.1553
11011.1292 | 732.5659 | 643.4859 | 471.7851 | 460.8091 | 471.4904 | 710.0793 | 687.7903 | 656.1262 | NaN | NaN | NaN | 653.4408 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.3178 | NaN | 21.7197
11012.1292 | 733.6598 | 644.1371 | 471.7084 | 460.4687 | 471.2579 | 711.3788 | 682.78 | 663.4887 | NaN | NaN | NaN | 670.5417 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.7488 | NaN | 22.7305
11013.1292 | 732.622 | 645.2955 | 471.7522 | 460.3197 | 471.0597 | 709.762 | 693.6543 | 665.7269 | NaN | NaN | NaN | 655.5848 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.7776 | NaN | 23.3975
11014.1292 | 730.8296 | 645.7365 | 472.4316 | 460.5681 | 471.319 | 708.014 | 698.5011 | 669.517 | NaN | NaN | NaN | 674.8653 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.9639 | NaN | 22.654
11015.1292 | 730.2951 | 645.848 | 472.6281 | 460.6632 | 471.3332 | 708.9126 | 693.175 | 668.0549 | NaN | NaN | NaN | 648.9932 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.0572 | NaN | 21.5775
11016.1292 | 729.0883 | 646.4342 | 472.6204 | 460.6294 | 471.6679 | 705.9451 | 691.128 | 675.7955 | NaN | NaN | NaN | 631.939 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.9927 | NaN | 23.2446
11017.1292 | 728.5984 | 646.9964 | 472.5702 | 460.4607 | 471.9182 | 704.4132 | 703.764 | 677.4986 | NaN | NaN | NaN | 628.0057 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.7096 | NaN | 21.0707
11018.1292 | 727.4458 | 646.9185 | 472.4631 | 460.3087 | 471.9689 | 714.4198 | 698.8327 | 675.479 | NaN | NaN | NaN | 628.6015 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.3116 | NaN | 21.6038
11019.1292 | 726.8991 | 646.3466 | 472.3888 | 460.3669 | 471.9368 | 714.6353 | 694.493 | 677.1145 | NaN | NaN | NaN | 618.0362 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.603 | NaN | 22.4003
11020.1292 | 726.7842 | 645.4166 | 472.1677 | 460.1489 | 471.8294 | 710.0096 | 698.2126 | 678.052 | NaN | NaN | NaN | 619.5053 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.2231 | NaN | 22.0034
11021.1292 | 728.3511 | 645.2089 | 471.9324 | 459.9028 | 471.464 | 708.3432 | 697.5993 | 687.4467 | NaN | NaN | NaN | 621.1541 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.6789 | NaN | 23.6122
11022.1292 | 730.2887 | 644.2439 | 471.9852 | 459.6135 | 471.1357 | 699.6089 | 686.4668 | 686.1214 | NaN | NaN | NaN | 650.2405 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 37.5226 | NaN | 23.9385
11023.1292 | 732.809 | 645.5565 | 471.8615 | 459.5495 | 470.8312 | 697.831 | 681.7108 | 690.1465 | NaN | NaN | NaN | 681.5091 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.3572 | NaN | 23.0101
11024.1292 | 737.1938 | 646.7562 | 471.647 | 459.4888 | 471.4444 | 695.5448 | 676.5058 | 687.5354 | NaN | NaN | NaN | 704.2713 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.1349 | NaN | 23.741
11025.1292 | 741.0145 | 648.2776 | 471.6298 | 459.6013 | 471.5967 | 697.7349 | 671.2058 | 676.4179 | NaN | NaN | NaN | 713.9333 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 40.6698 | NaN | 35.9121
11026.1292 | 741.5164 | 650.1954 | 471.3517 | 459.5981 | 471.8553 | 701.0189 | 664.9412 | 675.4741 | NaN | NaN | NaN | 697.4556 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 19.0576 | NaN | 24.8457
11027.1292 | 739.6012 | 649.0638 | 471.5209 | 460.2168 | 472.1201 | 698.5667 | 663.5565 | 681.6101 | NaN | NaN | NaN | 702.7936 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.6212 | NaN | 21.6702
11028.1292 | 736.5657 | 648.085 | 472.1007 | 460.1937 | 471.8282 | 693.9988 | 657.8667 | 682.3998 | NaN | NaN | NaN | 701.1575 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.2515 | NaN | 23.1059
11029.1292 | 733.6797 | 646.9766 | 472.4561 | 460.6298 | 471.5538 | 695.0467 | 668.8308 | 675.8621 | NaN | NaN | NaN | 706.7163 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.4649 | NaN | 22.5211
11030.1292 | 732.6665 | 647.3098 | 472.4815 | 461.0523 | 471.3273 | 699.7684 | 672.7596 | 671.1347 | NaN | NaN | NaN | 697.9485 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.7574 | NaN | 24.0537
11031.1292 | 733.8897 | 648.2656 | 472.2519 | 461.1083 | 471.1293 | 708.535 | 677.2199 | 671.4894 | NaN | NaN | NaN | 704.0435 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 58.223 | NaN | 21.164
11032.1292 | 735.4698 | 648.4613 | 471.9477 | 460.8848 | 471.6241 | 704.5747 | 678.4355 | 673.7943 | NaN | NaN | NaN | 708.7728 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.7078 | NaN | 23.0028
11033.1292 | 735.887 | 648.4615 | 471.5459 | 460.6255 | 472.0157 | 706.3697 | 674.8808 | 674.6424 | NaN | NaN | NaN | 704.3272 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.3287 | NaN | 21.5106
11034.1292 | 734.3291 | 648.3581 | 471.524 | 460.5965 | 472.0432 | 704.3176 | 675.2395 | 678.4546 | NaN | NaN | NaN | 709.5749 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.5995 | NaN | 22.0309
11035.1292 | 732.7396 | 647.6186 | 471.4308 | 460.4218 | 472.8513 | 697.6307 | 678.3019 | 679.2144 | NaN | NaN | NaN | 716.1162 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 21.3369 | NaN | 23.6065
11036.1292 | 732.3818 | 647.6769 | 471.3353 | 460.2989 | 472.7683 | 699.5883 | 676.382 | 678.311 | NaN | NaN | NaN | 734.8755 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.9264 | NaN | 24.4733
11037.1292 | 734.804 | 647.704 | 471.277 | 460.9324 | 473.2981 | 707.2071 | 676.2807 | 678.5145 | NaN | NaN | NaN | 757.1487 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.1987 | NaN | 23.1961
11038.1292 | 737.4073 | 648.9826 | 471.0974 | 460.553 | 472.7396 | 703.1038 | 666.8508 | 673.3327 | NaN | NaN | NaN | 766.2973 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.6038 | NaN | 22.8778
11039.1292 | 736.456 | 649.0322 | 470.9772 | 460.2308 | 472.4063 | 697.2433 | 661.7175 | 672.0774 | NaN | NaN | NaN | 776.1418 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.5543 | NaN | 23.3512
11040.1292 | 735.923 | 650.2157 | 470.9627 | 460.41 | 472.072 | 690.6971 | 659.2553 | 676.2726 | NaN | NaN | NaN | 784.6986 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.5752 | NaN | 22.2271
11041.1292 | 736.8155 | 650.2557 | 471.3266 | 460.6395 | 471.8022 | 684.8468 | 663.5627 | 682.1718 | NaN | NaN | NaN | 789.89 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.8154 | NaN | 23.5805
11042.1292 | 740.5126 | 651.0059 | 471.6075 | 460.6532 | 471.5247 | 677.2509 | 657.1494 | 678.2187 | NaN | NaN | NaN | 747.835 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 19.3997 | NaN | 24.2575
11043.1292 | 744.5883 | 651.0349 | 471.7755 | 460.8287 | 471.2413 | 670.4495 | 653.1442 | 672.6529 | NaN | NaN | NaN | 708.7484 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.4388 | NaN | 23.0974
11044.1292 | 748.5257 | 651.7387 | 471.5798 | 461.0898 | 471.5271 | 674.8513 | 651.6403 | 665.5755 | NaN | NaN | NaN | 679.6377 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.6136 | NaN | 24.17
11045.1292 | 746.4462 | 653.4481 | 471.8148 | 461.0493 | 471.5408 | 683.1418 | 652.3241 | 662.6274 | NaN | NaN | NaN | 660.6804 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.6336 | NaN | 22.7536
11046.1292 | 745.296 | 654.3201 | 472.219 | 461.4466 | 471.624 | 683.493 | 654.4357 | 660.4771 | NaN | NaN | NaN | 671.8078 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.0989 | NaN | 20.6918
11047.1292 | 742.2323 | 653.273 | 472.7483 | 461.789 | 471.5891 | 688.3726 | 668.2907 | 663.8354 | NaN | NaN | NaN | 693.2134 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.6969 | NaN | 21.3341
11048.1292 | 740.1315 | 652.233 | 472.9643 | 461.9735 | 472.0366 | 686.267 | 680.621 | 664.0426 | NaN | NaN | NaN | 688.794 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.0365 | NaN | 23.0244
11049.1292 | 737.9067 | 651.4013 | 472.8342 | 461.7024 | 471.9586 | 682.1611 | 674.5706 | 661.9089 | NaN | NaN | NaN | 690.941 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.6893 | NaN | 26.689
11050.1292 | 737.4616 | 651.2187 | 472.8202 | 461.2553 | 471.9509 | 686.6919 | 676.8462 | 667.4186 | NaN | NaN | NaN | 692.717 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.6553 | NaN | 22.9994
11051.1292 | 736.9022 | 651.2854 | 472.6322 | 461.303 | 472.2083 | 683.1715 | 669.3812 | 676.7224 | NaN | NaN | NaN | 706.5961 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.5061 | NaN | 24.0586
11052.1292 | 735.4427 | 650.4358 | 472.3263 | 461.2397 | 471.8761 | 677.7764 | 666.4379 | 680.1847 | NaN | NaN | NaN | 685.0566 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.4689 | NaN | 23.3941
11053.1292 | 735.3676 | 650.128 | 472.1681 | 461.3777 | 471.5976 | 675.1573 | 663.8151 | 682.1288 | NaN | NaN | NaN | 665.3402 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.8919 | NaN | 22.2422
11054.1292 | 736.3522 | 650.1374 | 472.1454 | 461.2911 | 471.3744 | 667.648 | 656.1435 | 686.5622 | NaN | NaN | NaN | 672.4393 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.0468 | NaN | 23.8425
11055.1292 | 739.272 | 650.5181 | 472.0637 | 461.0682 | 471.1068 | 665.4865 | 651.2132 | 681.6678 | NaN | NaN | NaN | 674.5996 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.807 | NaN | 22.3682
11056.1292 | 741.9718 | 650.9093 | 471.9065 | 461.2137 | 471.0985 | 665.8716 | 644.985 | 678.2103 | NaN | NaN | NaN | 674.4402 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.8424 | NaN | 23.7712
11057.1292 | 740.5096 | 651.8918 | 472.0728 | 461.2144 | 471.0945 | 662.8917 | 642.6966 | 672.3721 | NaN | NaN | NaN | 671.4061 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.2119 | NaN | 23.284
11058.1292 | 739.9496 | 652.3295 | 472.0116 | 461.1548 | 470.8359 | 660.5298 | 644.1487 | 673.2905 | NaN | NaN | NaN | 672.8491 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.0308 | NaN | 22.1259
11059.1292 | 738.0412 | 652.8219 | 472.3259 | 461.3099 | 470.8862 | 662.5144 | 640.4778 | 671.4218 | NaN | NaN | NaN | 662.1835 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.816 | NaN | 22.7048
11060.1292 | 735.7345 | 652.2117 | 472.2987 | 461.0399 | 471.1667 | 665.5822 | 648.0441 | 667.2886 | NaN | NaN | NaN | 669.9538 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.7705 | NaN | 24.003
11061.1292 | 735.8285 | 651.3506 | 472.2469 | 461.114 | 470.9877 | 669.275 | 660.3302 | 676.3889 | NaN | NaN | NaN | 674.6393 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.7083 | NaN | 22.3258
11062.1292 | 735.2323 | 651.7664 | 472.1784 | 461.2177 | 471.2673 | 673.5018 | 662.4505 | 677.8063 | NaN | NaN | NaN | 677.4989 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.0143 | NaN | 22.5507
11063.1292 | 734.396 | 652.81 | 471.9473 | 461.0418 | 471.339 | 684.0199 | 659.5364 | 685.062 | NaN | NaN | NaN | 697.0644 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.7331 | NaN | 22.9122
11064.1292 | 734.3507 | 652.1862 | 471.6699 | 460.7665 | 471.8789 | 680.5364 | 661.8254 | 686.8485 | NaN | NaN | NaN | 682.3647 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.6986 | NaN | 19.8344
11065.1292 | 732.7514 | 651.3986 | 471.4138 | 460.7736 | 471.9116 | 683.1792 | 670.4337 | 684.2497 | NaN | NaN | NaN | 683.8773 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.0255 | NaN | 23.4377
11066.1292 | 731.9295 | 651.3284 | 471.4421 | 460.6524 | 472.186 | 687.5052 | 672.7207 | 683.3025 | NaN | NaN | NaN | 703.216 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.236 | NaN | 20.1224
11067.1292 | 731.6922 | 650.3829 | 471.3101 | 460.8791 | 471.9822 | 685.8205 | 680.6622 | 683.7145 | NaN | NaN | NaN | 703.5984 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 16.3784 | NaN | 23.8138
11068.1292 | 731.1737 | 649.6323 | 471.3273 | 460.7643 | 471.7189 | 679.9765 | 675.1322 | 672.6262 | NaN | NaN | NaN | 704.0011 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.4864 | NaN | 21.947
11069.1292 | 730.482 | 649.5073 | 471.4219 | 460.7096 | 471.5566 | 675.9538 | 666.0474 | 660.6805 | NaN | NaN | NaN | 726.6722 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.6694 | NaN | 21.2837
11070.1292 | 728.1136 | 648.2795 | 471.6496 | 460.4999 | 471.4389 | 686.5351 | 660.6495 | 662.2954 | NaN | NaN | NaN | 728.0616 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.094 | NaN | 23.5708
11071.1292 | 728.8833 | 648.7857 | 471.2575 | 460.473 | 471.22 | 677.1352 | 659.58 | 672.3926 | NaN | NaN | NaN | 716.7387 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.8822 | NaN | 22.3988
11072.1292 | 732.2263 | 648.5399 | 471.7031 | 460.578 | 471.5903 | 670.8195 | 653.9003 | 663.3202 | NaN | NaN | NaN | 718.0763 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.2398 | NaN | 22.6576
11073.1292 | 733.8402 | 649.3332 | 471.8906 | 460.5344 | 471.3474 | 673.482 | 648.3967 | 656.8147 | NaN | NaN | NaN | 685.0994 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.1502 | NaN | 22.847
11074.1292 | 732.9626 | 649.6568 | 471.8437 | 460.718 | 471.3726 | 672.7559 | 646.3047 | 669.564 | NaN | NaN | NaN | 686.2152 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.7933 | NaN | 21.2757
11075.1292 | 731.7359 | 649.2949 | 471.8476 | 460.4961 | 471.2485 | 680.3738 | 648.5284 | 675.6256 | NaN | NaN | NaN | 717.1233 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.0775 | NaN | 22.5219
11076.1292 | 733.2418 | 648.9493 | 472.1645 | 460.554 | 471.3024 | 675.1703 | 656.033 | 674.6798 | NaN | NaN | NaN | 733.8348 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.3566 | NaN | 23.9243
11077.1292 | 737.3355 | 649.2909 | 472.1598 | 460.5208 | 471.7658 | 670.5506 | 651.3839 | 672.1935 | NaN | NaN | NaN | 744.711 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.3193 | NaN | 21.8449
11078.1292 | 740.6271 | 649.3428 | 472.228 | 461.1697 | 471.769 | 665.204 | 647.3044 | 670.9904 | NaN | NaN | NaN | 725.8 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.5131 | NaN | 23.3023
11079.1292 | 740.3517 | 649.6107 | 472.1546 | 461.2913 | 471.9548 | 661.9161 | 643.7047 | 660.5719 | NaN | NaN | NaN | 700.1751 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.2046 | NaN | 23.5249
11080.1292 | 739.1138 | 649.338 | 472.1982 | 461.1939 | 471.6819 | 658.6425 | 638.2148 | 651.9558 | NaN | NaN | NaN | 686.0032 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.305 | NaN | 20.2127
11081.1292 | 737.1964 | 648.8428 | 472.6334 | 461.2345 | 471.6012 | 656.1281 | 645.6139 | 653.7392 | NaN | NaN | NaN | 705.8772 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.9336 | NaN | 22.7784
11082.1292 | 736.8734 | 648.7838 | 472.8712 | 461.1397 | 471.7379 | 661.0307 | 649.5022 | 659.3047 | NaN | NaN | NaN | 679.7571 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.0062 | NaN | 22.8269
11083.1292 | 738.396 | 648.654 | 473.2108 | 461.0584 | 471.4715 | 663.5598 | 652.035 | 667.15 | NaN | NaN | NaN | 678.1742 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.6737 | NaN | 22.8782
11084.1292 | 740.0969 | 648.507 | 473.0431 | 460.8342 | 471.6568 | 659.3143 | 654.03 | 672.4034 | NaN | NaN | NaN | 674.5098 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.6563 | NaN | 21.2294
11085.1292 | 744.5035 | 648.2006 | 473.2826 | 460.8883 | 471.3231 | 654.7753 | 647.1901 | 677.0254 | NaN | NaN | NaN | 668.1262 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.7763 | NaN | 22.4772
11086.1292 | 743.7508 | 647.3119 | 473.2631 | 461.0328 | 471.4329 | 653.4311 | 652.1371 | 673.9131 | NaN | NaN | NaN | 675.932 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.4571 | NaN | 23.4522
11087.1292 | 744.5267 | 648.3614 | 473.6843 | 461.9571 | 472.0097 | 652.704 | 650.2984 | 668.0129 | NaN | NaN | NaN | 687.3598 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.6412 | NaN | 22.9955
11088.1292 | 743.4744 | 648.6553 | 473.8798 | 462.173 | 472.1383 | 659.1 | 661.06 | 671.8385 | NaN | NaN | NaN | 679.0734 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.6529 | NaN | 23.6939
11089.1292 | 740.659 | 648.9725 | 474.0308 | 461.8601 | 472.0855 | 670.2851 | 669.4727 | 671.2066 | NaN | NaN | NaN | 656.4325 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.0413 | NaN | 24.0172
11090.1292 | 736.6664 | 649.3128 | 474.0686 | 461.7619 | 472.0708 | 671.1857 | 667.1108 | 673.389 | NaN | NaN | NaN | 663.5277 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.3811 | NaN | 21.9162
11091.1292 | 733.6113 | 648.5735 | 474.2628 | 461.7521 | 472.182 | 676.1941 | 671.3258 | 665.2988 | NaN | NaN | NaN | 657.2735 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.4232 | NaN | 22.4017
11092.1292 | 731.2734 | 648.3391 | 474.6399 | 461.882 | 472.1431 | 679.3316 | 671.8397 | 664.8172 | NaN | NaN | NaN | 677.2954 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.7818 | NaN | 23.3757
11093.1292 | 730.077 | 647.7793 | 474.9338 | 462.0451 | 472.0139 | 681.7333 | 676.336 | 672.4598 | NaN | NaN | NaN | 664.7392 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.6948 | NaN | 22.9095
11094.1292 | 727.3906 | 648.3328 | 475.0689 | 462.3193 | 472.6583 | 687.8995 | 687.256 | 676.7164 | NaN | NaN | NaN | 658.9808 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.129 | NaN | 23.4855
11095.1292 | 726.4416 | 647.5625 | 475.3395 | 462.5415 | 473.0182 | 690.4493 | 687.9709 | 674.8698 | NaN | NaN | NaN | 669.0326 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.3225 | NaN | 22.147
11096.1292 | 726.876 | 647.4407 | 475.9121 | 462.4872 | 473.0391 | 691.1653 | 690.9609 | 675.7465 | NaN | NaN | NaN | 684.5696 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.6767 | NaN | 23.6241
11097.1292 | 729.0106 | 647.0181 | 475.7127 | 462.9113 | 472.959 | 692.8848 | 686.4059 | 676.4622 | NaN | NaN | NaN | 661.6053 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.227 | NaN | 22.6019
11098.1292 | 729.4778 | 647.2705 | 475.5125 | 462.6175 | 473.0087 | 698.3215 | 684.955 | 673.6871 | NaN | NaN | NaN | 664.5089 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.1987 | NaN | 23.5734
11099.1292 | 727.9131 | 646.9838 | 475.4606 | 462.2713 | 473.0827 | 699.7891 | 683.3415 | 676.9894 | NaN | NaN | NaN | 673.7943 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.151 | NaN | 24.497
11100.1292 | 727.6011 | 646.4531 | 475.8423 | 462.3164 | 473.2933 | 695.1374 | 683.6213 | 673.3397 | NaN | NaN | NaN | 679.4937 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.5537 | NaN | 22.5845
11101.1292 | 728.4957 | 646.3979 | 476.1447 | 462.3477 | 473.2132 | 698.061 | 688.0683 | 668.1277 | NaN | NaN | NaN | 684.0797 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.4524 | NaN | 24.2219
11102.1292 | 727.0826 | 646.2295 | 476.005 | 462.0867 | 473.055 | 697.488 | 683.9296 | 665.152 | NaN | NaN | NaN | 705.4151 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.1093 | NaN | 24.1669
11103.1292 | 726.3796 | 645.6169 | 475.8708 | 461.7976 | 472.7429 | 698.5063 | 684.6071 | 670.8825 | NaN | NaN | NaN | 678.0062 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.0552 | NaN | 22.2983
11104.1292 | 724.5421 | 645.387 | 476.3079 | 461.9663 | 472.8989 | 698.2416 | 684.9491 | 675.5059 | NaN | NaN | NaN | 671.4067 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.238 | NaN | 24.4554
11105.1292 | 724.3429 | 644.3892 | 476.3828 | 462.1563 | 473.3297 | 699.92 | 695.7318 | 678.4435 | NaN | NaN | NaN | 677.1195 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.2508 | NaN | 22.7253
11106.1292 | 726.3004 | 644.9524 | 476.5689 | 463.0643 | 473.8064 | 695.802 | 691.0235 | 671.9309 | NaN | NaN | NaN | 714.251 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.3991 | NaN | 21.8896
11107.1292 | 729.0463 | 645.6778 | 476.5592 | 463.0311 | 474.1883 | 691.4834 | 687.7528 | 665.5747 | NaN | NaN | NaN | 734.2195 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.9219 | NaN | 22.5197
11108.1292 | 731.9983 | 646.0837 | 476.528 | 462.9584 | 474.1223 | 687.6125 | 684.4284 | 665.7433 | NaN | NaN | NaN | 770.5931 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.9941 | NaN | 22.5635
11109.1292 | 732.4825 | 645.6712 | 476.4313 | 462.7949 | 474.2261 | 683.7728 | 675.7384 | 665.6885 | NaN | NaN | NaN | 778.5137 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.3066 | NaN | 23.0912
11110.1292 | 732.9141 | 645.5498 | 476.6269 | 462.5683 | 474.0252 | 685.9292 | 670.2714 | 670.8518 | NaN | NaN | NaN | 777.4215 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.3668 | NaN | 22.6497
11111.1292 | 733.1326 | 645.0486 | 476.7135 | 462.2395 | 473.8703 | 696.6208 | 669.4787 | 674.054 | NaN | NaN | NaN | 772.0781 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.6542 | NaN | 24.6128
11112.1292 | 732.2055 | 644.9993 | 476.7857 | 461.8612 | 473.4651 | 691.8748 | 672.1891 | 672.3882 | NaN | NaN | NaN | 779.6426 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.9631 | NaN | 22.9603
11113.1292 | 729.6787 | 643.9888 | 477.0902 | 461.3556 | 472.9621 | 681.0743 | 664.3176 | 661.5725 | NaN | NaN | NaN | 772.1709 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.5766 | NaN | 21.9056
11114.1292 | 727.6525 | 643.8556 | 477.2662 | 461.0895 | 472.2333 | 682.225 | 668.8537 | 654.5761 | NaN | NaN | NaN | 745.2026 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.3459 | NaN | 23.3042
11115.1292 | 726.5182 | 643.5335 | 477.1067 | 460.8613 | 471.7465 | 675.6884 | 670.7651 | 661.0725 | NaN | NaN | NaN | 751.513 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.4691 | NaN | 23.255
11116.1292 | 726.5682 | 643.1326 | 477.3671 | 460.4773 | 471.4342 | 672.015 | 674.2923 | 668.1216 | NaN | NaN | NaN | 773.7312 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.9292 | NaN | 20.3591
11117.1292 | 726.7582 | 642.4804 | 478.3462 | 460.446 | 471.1409 | 670.4104 | 670.0103 | 671.2916 | NaN | NaN | NaN | 792.8333 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.1371 | NaN | 24.1387
11118.1292 | 727.5672 | 642.2957 | 478.4027 | 460.8508 | 471.0552 | 664.3547 | 677.8811 | 674.4442 | NaN | NaN | NaN | 775.0519 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.2832 | NaN | 23.366
11119.1292 | 729.2038 | 642.4315 | 478.7383 | 461.2855 | 470.992 | 662.9504 | 678.3817 | 672.2326 | NaN | NaN | NaN | 763.4858 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.1572 | NaN | 23.3737
11120.1292 | 732.867 | 643.1858 | 478.6751 | 461.7904 | 471.0941 | 657.8331 | 679.9124 | 679.9482 | NaN | NaN | NaN | 760.7272 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.0984 | NaN | 22.9572
11121.1292 | 735.8405 | 643.8539 | 478.5721 | 461.8653 | 470.9303 | 652.7239 | 676.0244 | 676.4701 | NaN | NaN | NaN | 745.9425 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.4479 | NaN | 23.0826
11122.1292 | 740.4301 | 644.1678 | 478.1109 | 461.8375 | 470.8212 | 650.6231 | 667.7086 | 667.8724 | NaN | NaN | NaN | 721.6208 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.7165 | NaN | 22.2042
11123.1292 | 742.5999 | 645.0298 | 477.6278 | 461.9564 | 471.0589 | 657.1182 | 663.4893 | 662.9754 | NaN | NaN | NaN | 736.6524 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.1576 | NaN | 19.7155
11124.1292 | 741.1371 | 644.9814 | 477.3193 | 461.8279 | 471.0606 | 663.1401 | 659.7808 | 654.8902 | NaN | NaN | NaN | 743.4738 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.1597 | NaN | 21.424
11125.1292 | 742.2081 | 644.4277 | 477.2556 | 461.7945 | 470.7721 | 659.2126 | 663.0195 | 657.7696 | NaN | NaN | NaN | 766.3656 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.032 | NaN | 23.4496
11126.1292 | 744.0301 | 644.4291 | 477.1304 | 461.8888 | 470.9603 | 660.7501 | 665.3873 | 666.1283 | NaN | NaN | NaN | 765.5675 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.6929 | NaN | 21.7209
11127.1292 | 748.0162 | 644.1822 | 477.03 | 461.9738 | 471.877 | 666.3929 | 666.944 | 661.3135 | NaN | NaN | NaN | 776.7214 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.1197 | NaN | 24.8749
11128.1448 | 750.7215 | 645.2813 | 477.1597 | 461.7955 | 472.1186 | 668.8392 | 663.5453 | 658.5554 | NaN | NaN | NaN | 767.0123 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.6938 | NaN | 22.8956
11129.1292 | 747.9395 | 645.596 | 477.1814 | 461.6145 | 472.6152 | 662.8029 | 660.8884 | 658.0704 | NaN | NaN | NaN | 762.1328 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.4157 | NaN | 22.9512
11130.1292 | 746.856 | 645.3433 | 477.1768 | 461.6674 | 472.8439 | 656.1496 | 657.0717 | 655.1774 | NaN | NaN | NaN | 750.3196 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.4805 | NaN | 21.8288
11131.1292 | 749.5521 | 645.044 | 476.9334 | 461.723 | 472.7599 | 654.0139 | 657.6838 | 655.6618 | NaN | NaN | NaN | 723.1544 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.0601 | NaN | 23.743
11132.1292 | 752.6092 | 645.4153 | 476.9588 | 461.4424 | 472.6756 | 651.2172 | 660.432 | 656.9458 | NaN | NaN | NaN | 697.9018 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.5208 | NaN | 22.1001
11133.1292 | 751.0606 | 645.974 | 477.0395 | 461.5843 | 472.4306 | 659.5142 | 663.8742 | 655.4993 | NaN | NaN | NaN | 703.7678 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.1431 | NaN | 23.779
11134.1448 | 751.4697 | 645.6281 | 477.3112 | 461.7626 | 472.8579 | 657.848 | 664.0536 | 658.1109 | NaN | NaN | NaN | 699.5481 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.9891 | NaN | 22.9276
11135.1292 | 748.3944 | 645.3024 | 477.3956 | 462.0736 | 473.273 | 664.2467 | 662.7208 | 661.2997 | NaN | NaN | NaN | 716.2803 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.3922 | NaN | 20.8764
11136.1292 | 747.9587 | 644.7494 | 477.4042 | 462.4957 | 473.4976 | 672.0592 | 666.0195 | 665.6665 | NaN | NaN | NaN | 712.7419 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.8157 | NaN | 22.717
11137.1292 | 746.8905 | 644.2353 | 477.5477 | 462.7555 | 473.5341 | 675.0696 | 672.4549 | 673.6402 | NaN | NaN | NaN | 707.6512 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.8049 | NaN | 23.1402
11138.1292 | 744.5772 | 644.0321 | 477.7106 | 462.6913 | 473.5976 | 673.75 | 679.0891 | 672.0315 | NaN | NaN | NaN | 709.437 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.2461 | NaN | 23.4061
11139.1292 | 745.6283 | 643.7166 | 477.6793 | 462.3944 | 473.1805 | 677.5118 | 679.7102 | 674.9393 | NaN | NaN | NaN | 699.7826 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.2335 | NaN | 22.3489
11140.1292 | 746.6646 | 643.8048 | 477.3591 | 462.2288 | 473.8874 | 675.7078 | 680.3959 | 681.4548 | NaN | NaN | NaN | 704.6937 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.1993 | NaN | 21.8528
11141.1292 | 744.5217 | 644.0543 | 477.054 | 461.8867 | 473.8824 | 671.6493 | 689.0803 | 682.5669 | NaN | NaN | NaN | 717.8067 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.9774 | NaN | 23.6853
11142.1292 | 744.7591 | 644.4736 | 477.1013 | 461.8471 | 474.0108 | 676.8864 | 691.5844 | 690.8988 | NaN | NaN | NaN | 702.471 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.5478 | NaN | 20.5734
11143.1292 | 744.1258 | 645.0591 | 477.023 | 461.5744 | 474.0939 | 671.6028 | 685.1894 | 683.5739 | NaN | NaN | NaN | 712.2692 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.9758 | NaN | 22.8864
11144.1292 | 745.9396 | 644.7989 | 477.0647 | 461.4038 | 474.328 | 674.569 | 682.2287 | 672.0591 | NaN | NaN | NaN | 720.7984 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.4961 | NaN | 22.2586
11145.1448 | 747.0692 | 645.454 | 477.0861 | 461.3023 | 474.1568 | 681.16 | 680.685 | 666.1642 | NaN | NaN | NaN | 707.9982 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.2061 | NaN | 21.5997
11146.1292 | 745.5087 | 645.267 | 477.3358 | 461.3211 | 474.0734 | 678.6348 | 676.1562 | 673.6327 | NaN | NaN | NaN | 692.5236 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.8286 | NaN | 21.2759
11147.1292 | 745.9003 | 644.5306 | 477.8144 | 461.1308 | 474.2975 | 673.8035 | 682.1062 | 669.6825 | NaN | NaN | NaN | 690.1032 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.4152 | NaN | 22.9614
11148.1292 | 746.7154 | 644.5797 | 477.4444 | 460.8484 | 474.3931 | 677.0174 | 677.5013 | 666.4897 | NaN | NaN | NaN | 681.8965 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.0607 | NaN | 23.627
11149.1292 | 747.8231 | 644.5218 | 477.3993 | 460.6976 | 474.1897 | 671.208 | 672.8187 | 671.6806 | NaN | NaN | NaN | 658.2196 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.2639 | NaN | 21.2726
11150.1292 | 745.9575 | 645.0286 | 477.3564 | 460.8136 | 473.8771 | 672.2578 | 672.4007 | 668.5009 | NaN | NaN | NaN | 660.4404 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.7135 | NaN | 22.8662
11151.1292 | 742.9339 | 645.521 | 477.805 | 460.939 | 473.986 | 673.1465 | 673.1752 | 660.766 | NaN | NaN | NaN | 690.742 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.236 | NaN | 23.3545
11152.1292 | 738.2209 | 644.7851 | 478.2629 | 461.1617 | 474.0805 | 675.1282 | 675.9034 | 660.736 | NaN | NaN | NaN | 676.0982 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.2906 | NaN | 22.948
11153.1292 | 736.2442 | 643.8803 | 478.3207 | 461.2672 | 474.5165 | 669.5019 | 666.655 | 673.4282 | NaN | NaN | NaN | 660.593 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.8708 | NaN | 23.9476
11154.1292 | 737.5633 | 643.282 | 478.5066 | 461.0849 | 474.4478 | 664.359 | 662.2751 | 683.1166 | NaN | NaN | NaN | 668.5847 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.133 | NaN | 21.2308
11155.1292 | 739.3364 | 643.2036 | 478.4155 | 460.9238 | 474.2599 | 658.9505 | 654.5953 | 677.2979 | NaN | NaN | NaN | 659.7352 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.69 | NaN | 23.9511
11156.1292 | 741.9338 | 643.643 | 478.6438 | 460.8928 | 473.9164 | 654.5664 | 653.7329 | 680.0867 | NaN | NaN | NaN | 685.0213 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.6533 | NaN | 23.289
11157.1292 | 744.2413 | 644.3186 | 478.6307 | 461.2957 | 474.3271 | 665.1297 | 652.7666 | 676.2726 | NaN | NaN | NaN | 685.4553 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.4678 | NaN | 23.3335
11158.1292 | 746.291 | 645.0752 | 478.4756 | 461.2635 | 474.6589 | 664.9352 | 653.5503 | 674.2051 | NaN | NaN | NaN | 669.5232 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.9167 | NaN | 23.5202
11159.1292 | 750.3037 | 645.1806 | 478.5962 | 461.7743 | 474.6922 | 658.1602 | 653.2216 | 680.5805 | NaN | NaN | NaN | 653.9395 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.3161 | NaN | 22.8704
11160.1292 | 747.2583 | 645.0237 | 478.8721 | 461.9225 | 474.7415 | 657.203 | 657.1485 | 677.4427 | NaN | NaN | NaN | 661.6354 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.5989 | NaN | 21.4919
11161.1292 | 745.7373 | 644.3032 | 479.494 | 462.0781 | 474.4709 | 653.1334 | 657.4347 | 676.0938 | NaN | NaN | NaN | 653.6609 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.2164 | NaN | 22.0377
11162.1292 | 744.3388 | 644.1982 | 479.716 | 462.0504 | 474.2476 | 651.2605 | 662.8218 | 681.2781 | NaN | NaN | NaN | 658.4732 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.9156 | NaN | 24.3681
11163.1292 | 743.6937 | 643.5229 | 479.8729 | 461.7831 | 474.4702 | 647.5633 | 654.8326 | 688.8112 | NaN | NaN | NaN | 675.8183 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.0756 | NaN | 23.148
11164.1292 | 743.1003 | 643.3222 | 479.6287 | 461.6266 | 474.4151 | 646.2423 | 653.9133 | 694.7328 | NaN | NaN | NaN | 700.1125 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.8033 | NaN | 23.2552
11165.1292 | 742.0953 | 642.8446 | 479.708 | 461.6136 | 475.0926 | 643.455 | 650.1234 | 684.4793 | NaN | NaN | NaN | 729.3931 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.2873 | NaN | 22.3547
11166.1292 | 742.6527 | 642.236 | 479.6153 | 461.985 | 475.5423 | 651.4437 | 651.207 | 683.638 | NaN | NaN | NaN | 738.2004 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.0812 | NaN | 23.3796
11167.1292 | 742.7172 | 642.6419 | 479.4211 | 461.9401 | 476.0467 | 661.628 | 655.1765 | 678.5119 | NaN | NaN | NaN | 750.1362 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.0034 | NaN | 20.6875
11168.1292 | 745.1302 | 642.4525 | 479.7 | 461.877 | 475.8898 | 655.824 | 650.3788 | 676.3183 | NaN | NaN | NaN | 760.2006 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.4333 | NaN | 22.1119
11169.1292 | 746.7435 | 642.6276 | 479.4935 | 461.7862 | 475.7702 | 649.4553 | 646.2157 | 666.5447 | NaN | NaN | NaN | 725.4332 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.2003 | NaN | 20.9636
11170.1292 | 744.975 | 642.9668 | 479.277 | 461.9762 | 475.7397 | 648.4809 | 647.6855 | 667.0325 | NaN | NaN | NaN | 691.5222 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.9734 | NaN | 23.0135
11171.1292 | 742.285 | 642.9919 | 479.2364 | 462.0233 | 475.7923 | 645.4719 | 653.264 | 674.9976 | NaN | NaN | NaN | 658.0418 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.1976 | NaN | 22.1459
11172.1292 | 738.7546 | 643.0194 | 479.4684 | 462.4826 | 475.9531 | 659.2973 | 657.4163 | 678.2733 | NaN | NaN | NaN | 682.7642 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.9757 | NaN | 23.7125
11173.1292 | 736.9533 | 642.2795 | 479.8892 | 462.8957 | 476.2592 | 661.5525 | 669.9599 | 681.6012 | NaN | NaN | NaN | 681.0202 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.0864 | NaN | 22.9693
11174.1292 | 737.2596 | 641.386 | 479.8748 | 462.9667 | 476.0498 | 660.9133 | 679.3235 | 682.5821 | NaN | NaN | NaN | 687.1306 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.3619 | NaN | 22.5593
11175.1292 | 735.8028 | 641.4135 | 479.6442 | 462.7806 | 476.3288 | 663.6606 | 677.3372 | 674.8751 | NaN | NaN | NaN | 685.2134 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.2997 | NaN | 20.4799
11176.1292 | 734.3502 | 641.5585 | 479.7429 | 462.5811 | 475.9477 | 670.6111 | 673.7924 | 670.1247 | NaN | NaN | NaN | 667.3555 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.4997 | NaN | 22.225
11177.1292 | 733.8888 | 641.8227 | 479.9305 | 462.7774 | 476.2554 | 668.0446 | 680.1858 | 670.5996 | NaN | NaN | NaN | 642.0369 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.9741 | NaN | 22.2301
11178.1292 | 730.2607 | 641.5484 | 480.2759 | 463.3266 | 476.6875 | 677.7318 | 688.9286 | 666.6797 | NaN | NaN | NaN | 647.9964 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.7924 | NaN | 23.6669
11179.1292 | 727.2925 | 641.1543 | 480.5419 | 463.6987 | 477.1161 | 681.5477 | 691.4472 | 658.9863 | NaN | NaN | NaN | 654.7927 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.8658 | NaN | 23.7384
11180.1292 | 725.2162 | 640.4387 | 480.5646 | 463.7007 | 476.7236 | 674.0068 | 697.1602 | 656.5814 | NaN | NaN | NaN | 666.4061 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.4042 | NaN | 22.7242
11181.1292 | 723.1284 | 639.7328 | 480.1651 | 463.7761 | 476.9384 | 668.4817 | 692.1229 | 649.9925 | NaN | NaN | NaN | 649.5766 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.9484 | NaN | 21.4733
11182.1292 | 720.5461 | 639.6858 | 480.678 | 463.7391 | 476.6949 | 662.8862 | 684.8306 | 651.4978 | NaN | NaN | NaN | 651.9995 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.2575 | NaN | 22.8684
11183.1292 | 718.0231 | 639.3317 | 480.8997 | 464.0487 | 476.6873 | 658.6087 | 681.5099 | 655.3436 | NaN | NaN | NaN | 667.689 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.8598 | NaN | 23.9851
11184.1292 | 715.7274 | 639.1572 | 481.1825 | 464.0441 | 476.4063 | 655.8322 | 689.0688 | 658.0093 | NaN | NaN | NaN | 671.3063 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.6512 | NaN | 22.629
11185.1292 | 716.1283 | 638.718 | 481.3409 | 464.411 | 476.9747 | 651.1706 | 695.8446 | 652.12 | NaN | NaN | NaN | 691.7085 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.6732 | NaN | 20.9734
11186.1292 | 717.9105 | 638.0962 | 481.214 | 464.2396 | 476.6172 | 652.5246 | 686.8268 | 653.7557 | NaN | NaN | NaN | 696.9358 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.9962 | NaN | 19.7512
11187.1292 | 719.015 | 638.5304 | 481.072 | 464.5663 | 477.1451 | 650.4659 | 683.2313 | 668.6866 | NaN | NaN | NaN | 696.0166 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.4756 | NaN | 22.4107
11188.1292 | 717.957 | 638.4952 | 481.2856 | 464.4743 | 477.4761 | 648.8856 | 676.865 | 662.5418 | NaN | NaN | NaN | 698.5225 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.6369 | NaN | 19.7693
11189.1292 | 717.7565 | 638.0305 | 481.2946 | 464.3312 | 477.5137 | 644.5429 | 667.9568 | 655.9489 | NaN | NaN | NaN | 703.5516 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.8971 | NaN | 21.775
11190.1292 | 719.614 | 638.0252 | 480.8088 | 464.5459 | 478.0271 | 640.2212 | 660.6758 | 654.8391 | NaN | NaN | NaN | 732.9058 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.7559 | NaN | 22.1221
11191.1292 | 722.8119 | 638.4597 | 480.65 | 464.5361 | 478.0235 | 641.7142 | 661.0521 | 654.2217 | NaN | NaN | NaN | 737.1382 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.1838 | NaN | 21.346
11192.1292 | 723.1511 | 638.2949 | 480.4176 | 464.4875 | 477.9652 | 644.2483 | 656.7639 | 646.3646 | NaN | NaN | NaN | 722.7996 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.948 | NaN | 20.1671
11193.1292 | 723.7488 | 637.8029 | 480.1732 | 464.291 | 477.4883 | 648.1693 | 652.3688 | 643.6574 | NaN | NaN | NaN | 744.5534 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.2809 | NaN | 22.7668
11194.1292 | 724.6342 | 637.4616 | 479.7664 | 464.3632 | 477.4862 | 644.6761 | 647.2487 | 641.1414 | NaN | NaN | NaN | 727.8161 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.1577 | NaN | 23.8097
11195.1292 | 725.6153 | 637.2835 | 479.4213 | 464.2936 | 477.2875 | 642.0567 | 647.2239 | 655.3647 | NaN | NaN | NaN | 732.2244 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.7227 | NaN | 20.8276
11196.1292 | 727.3902 | 637.5946 | 479.421 | 463.986 | 477.1057 | 645.743 | 644.6956 | 656.6734 | NaN | NaN | NaN | 751.5517 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.8039 | NaN | 23.1367
11197.1292 | 726.707 | 637.5808 | 479.2341 | 463.7704 | 477.1323 | 649.0046 | 648.5235 | 660.6735 | NaN | NaN | NaN | 738.7366 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.683 | NaN | 23.5732
11198.1292 | 727.0712 | 637.4739 | 479.0282 | 463.8587 | 477.2232 | 644.9877 | 646.3028 | 669.478 | NaN | NaN | NaN | 704.2112 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.1266 | NaN | 21.0003
11199.1292 | 728.2609 | 637.547 | 479.4612 | 464.1912 | 477.5443 | 643.1103 | 646.6026 | 669.735 | NaN | NaN | NaN | 683.3952 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.4837 | NaN | 21.5002
11200.1292 | 729.1812 | 637.4195 | 479.7671 | 464.5488 | 478.2163 | 650.1539 | 654.8234 | 672.966 | NaN | NaN | NaN | 716.9389 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.3266 | NaN | 22.9571
11201.1292 | 728.3902 | 637.5389 | 480.3096 | 465.1047 | 478.4216 | 649.3424 | 661.3092 | 669.5198 | NaN | NaN | NaN | 715.6453 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.1256 | NaN | 21.3826
11202.1292 | 726.4044 | 637.6072 | 480.6326 | 465.6095 | 478.6565 | 652.5815 | 659.0467 | 663.1419 | NaN | NaN | NaN | 693.1516 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.7581 | NaN | 21.8614
11203.1292 | 726.2218 | 638.017 | 480.5435 | 465.7083 | 478.6067 | 649.1023 | 672.0068 | 666.5025 | NaN | NaN | NaN | 675.2845 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.1866 | NaN | 21.947
11204.1292 | 725.3185 | 637.8018 | 480.8291 | 465.4836 | 478.4874 | 653.4742 | 675.2699 | 665.0082 | NaN | NaN | NaN | 699.5393 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.067 | NaN | 22.4479
11205.1292 | 726.2408 | 637.8871 | 480.9702 | 465.7403 | 478.3133 | 652.3366 | 677.0589 | 661.0343 | NaN | NaN | NaN | 696.7142 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.5523 | NaN | 22.1017
11206.1292 | 726.4951 | 637.537 | 481.0933 | 465.7896 | 478.7811 | 648.7131 | 679.6805 | 668.6589 | NaN | NaN | NaN | 679.5735 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.596 | NaN | 22.4954
11207.1292 | 727.9925 | 637.6062 | 480.9515 | 465.5063 | 478.7495 | 647.7474 | 680.2352 | 666.7851 | NaN | NaN | NaN | 698.1696 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.9587 | NaN | 21.63
11208.1292 | 729.9896 | 637.8432 | 480.4655 | 465.2817 | 478.6703 | 652.1076 | 674.7877 | 669.7706 | NaN | NaN | NaN | 711.4762 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.0485 | NaN | 23.0937
11209.1292 | 730.5246 | 637.7967 | 480.112 | 464.8064 | 478.736 | 651.4738 | 671.9807 | 667.8977 | NaN | NaN | NaN | 733.0267 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 45.2779 | NaN | 22.9529
11210.1292 | 733.1043 | 638.2696 | 480.4198 | 464.7655 | 478.8277 | 654.8407 | 673.2532 | 665.1416 | NaN | NaN | NaN | 708.6217 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.0385 | NaN | 22.9532
11211.1292 | 735.3058 | 639.4853 | 480.6158 | 464.9775 | 478.8108 | 655.7393 | 666.7246 | 666.6003 | NaN | NaN | NaN | 675.0043 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.5343 | NaN | 22.7442
11212.1292 | 738.8853 | 640.1707 | 480.6576 | 465.0552 | 478.4774 | 650.0853 | 659.5938 | 660.5105 | NaN | NaN | NaN | 666.9467 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.2589 | NaN | 23.124
11213.1292 | 741.0364 | 640.2888 | 481.0127 | 465.1013 | 478.2411 | 645.0286 | 654.9982 | 658.1619 | NaN | NaN | NaN | 663.4482 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.8161 | NaN | 20.842
11214.1292 | 743.9673 | 640.3559 | 480.9717 | 465.2662 | 478.5367 | 642.1311 | 652.1863 | 650.3982 | NaN | NaN | NaN | 649.7962 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.0666 | NaN | 22.6183
11215.1292 | 745.8803 | 640.2285 | 480.717 | 465.2354 | 478.619 | 642.1071 | 650.2426 | 645.37 | NaN | NaN | NaN | 666.0563 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.8755 | NaN | 22.099
11216.1292 | 744.4182 | 640.0785 | 480.4536 | 465.0599 | 478.6348 | 654.6748 | 653.3164 | 639.3946 | NaN | NaN | NaN | 663.3456 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.9504 | NaN | 24.976
11217.1292 | 743.8492 | 640.2615 | 480.5138 | 464.8108 | 478.3102 | 654.5228 | 654.2968 | 645.8482 | NaN | NaN | NaN | 699.3359 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.1011 | NaN | 23.2182
11218.1292 | 744.143 | 640.2728 | 480.806 | 465.2068 | 477.6973 | 648.8266 | 650.2863 | 649.0858 | NaN | NaN | NaN | 704.3458 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.5697 | NaN | 23.0997
11219.1292 | 742.9243 | 640.0317 | 481.0587 | 465.3004 | 477.2283 | 653.0534 | 650.5757 | 651.3063 | NaN | NaN | NaN | 712.084 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.2498 | NaN | 23.174
11220.1292 | 741.7391 | 640.4171 | 481.3237 | 465.0881 | 477.3236 | 662.9362 | 659.1672 | 659.4485 | NaN | NaN | NaN | 699.2953 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.7334 | NaN | 22.3886
11221.1292 | 740.6202 | 640.8159 | 481.7139 | 464.6849 | 477.3356 | 662.5138 | 659.1037 | 661.1097 | NaN | NaN | NaN | 695.0792 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.0439 | NaN | 21.8031
11222.1292 | 740.6014 | 640.9585 | 481.987 | 464.4895 | 477.152 | 657.0484 | 661.1191 | 666.2621 | NaN | NaN | NaN | 677.0944 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.7436 | NaN | 23.5403
11223.1292 | 741.1886 | 641.0441 | 482.1427 | 464.3186 | 477.4308 | 651.9602 | 662.0366 | 662.4722 | NaN | NaN | NaN | 669.3809 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.3646 | NaN | 21.5221
11224.1292 | 741.1791 | 640.8653 | 482.4165 | 464.1708 | 477.4549 | 647.6573 | 658.0741 | 668.0528 | NaN | NaN | NaN | 701.1419 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.02 | NaN | 19.4614
11225.1292 | 742.3488 | 641.1713 | 482.2406 | 464.2496 | 477.3483 | 652.634 | 655.5819 | 666.9268 | NaN | NaN | NaN | 713.7562 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.3907 | NaN | 22.0159
11226.1292 | 741.2769 | 640.7604 | 482.2558 | 463.9976 | 477.108 | 649.7592 | 649.4168 | 669.7139 | NaN | NaN | NaN | 714.4632 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.3534 | NaN | 22.9079
11227.1292 | 743.5705 | 640.6031 | 482.0424 | 463.8833 | 476.9811 | 657.3858 | 644.8967 | 672.5663 | NaN | NaN | NaN | 722.3161 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.372 | NaN | 21.5422
11228.1292 | 744.9885 | 640.1828 | 482.0732 | 464.3382 | 476.8844 | 649.1818 | 641.5363 | 675.0139 | NaN | NaN | NaN | 743.97 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.8636 | NaN | 22.1554
11229.1292 | 744.9441 | 639.941 | 482.4198 | 464.399 | 477.0759 | 643.3664 | 639.9099 | 675.8331 | NaN | NaN | NaN | 741.9718 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.5767 | NaN | 21.8053
11230.1292 | 745.1792 | 639.5766 | 482.5029 | 464.1529 | 476.776 | 652.6917 | 645.1641 | 673.832 | NaN | NaN | NaN | 715.3763 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.2236 | NaN | 23.604
11231.1292 | 745.2569 | 639.1774 | 482.6643 | 464.1161 | 476.7282 | 651.1709 | 653.1369 | 671.8346 | NaN | NaN | NaN | 698.3245 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.6769 | NaN | 22.6046
11232.1292 | 746.7018 | 638.2489 | 482.6762 | 463.7996 | 476.404 | 645.1903 | 652.4347 | 674.0357 | NaN | NaN | NaN | 714.6445 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.4048 | NaN | 24.2197
11233.1292 | 745.4662 | 637.7162 | 482.6174 | 463.8852 | 476.391 | 652.0833 | 652.6939 | 669.3989 | NaN | NaN | NaN | 694.2186 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.2809 | NaN | 19.7948
11234.1292 | 741.5182 | 636.943 | 482.693 | 463.794 | 476.3441 | 654.456 | 654.8831 | 657.3421 | NaN | NaN | NaN | 681.2143 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.3445 | NaN | 22.7
11235.1292 | 737.6689 | 636.6516 | 482.9849 | 463.3855 | 476.2569 | 650.2835 | 657.7442 | 662.1013 | NaN | NaN | NaN | 691.6228 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.4714 | NaN | 22.2035
11236.1292 | 734.3392 | 635.8659 | 483.7833 | 463.2442 | 475.8768 | 645.3756 | 672.4715 | 661.5039 | NaN | NaN | NaN | 664.2551 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.5143 | NaN | 22.7589
11237.1292 | 734.9936 | 636.8099 | 484.2527 | 463.4047 | 475.7825 | 647.6317 | 672.0635 | 662.6506 | NaN | NaN | NaN | 655.4371 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.2043 | NaN | 23.7991
11238.1292 | 734.6502 | 637.0979 | 484.507 | 463.3717 | 475.7005 | 656.1869 | 678.4287 | 657.8501 | NaN | NaN | NaN | 664.544 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.3787 | NaN | 21.7959
11239.1292 | 733.2467 | 637.4069 | 484.3837 | 463.236 | 475.9691 | 652.1756 | 674.1707 | 664.7957 | NaN | NaN | NaN | 650.622 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.8434 | NaN | 22.5641
11240.1292 | 735.6491 | 637.5959 | 484.4609 | 463.4357 | 475.827 | 648.7665 | 671.6148 | 671.5141 | NaN | NaN | NaN | 634.8366 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.0493 | NaN | 21.4972
11241.1292 | 735.2006 | 637.7999 | 484.7958 | 463.4903 | 475.4688 | 645.9593 | 671.095 | 671.6285 | NaN | NaN | NaN | 625.179 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.8934 | NaN | 23.1905
11242.1292 | 735.0304 | 637.8192 | 485.0628 | 463.6131 | 475.3852 | 643.7381 | 668.2001 | 672.9901 | NaN | NaN | NaN | 643.0967 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.2985 | NaN | 22.7029
11243.1292 | 736.262 | 638.4355 | 485.1185 | 463.6251 | 475.6064 | 650.9461 | 665.6275 | 674.0745 | NaN | NaN | NaN | 650.0607 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.7416 | NaN | 20.455
11244.1292 | 736.3771 | 638.8607 | 484.8945 | 463.4524 | 476.1477 | 657.1451 | 661.4614 | 676.8384 | NaN | NaN | NaN | 652.7037 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.727 | NaN | 22.9353
11245.1292 | 733.3608 | 638.5233 | 485.0153 | 463.2592 | 476.0532 | 655.3698 | 654.4044 | 666.7754 | NaN | NaN | NaN | 668.0747 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.7347 | NaN | 22.6954
11246.1292 | 730.4395 | 637.8092 | 485.019 | 463.0964 | 475.6023 | 650.303 | 655.1262 | 661.281 | NaN | NaN | NaN | 687.8189 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.5392 | NaN | 23.0311
11247.1292 | 727.8992 | 637.3298 | 484.8385 | 463.1586 | 475.169 | 647.7475 | 657.3464 | 667.8857 | NaN | NaN | NaN | 673.5886 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.2806 | NaN | 22.4586
11248.1292 | 725.8623 | 637.5976 | 484.9762 | 463.1279 | 474.7473 | 644.7105 | 661.5899 | 666.459 | NaN | NaN | NaN | 672.0528 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.6369 | NaN | 21.3615
11249.1292 | 722.1798 | 637.4808 | 485.4091 | 463.4077 | 474.9345 | 649.6598 | 667.3498 | 660.3883 | NaN | NaN | NaN | 665.4779 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.1683 | NaN | 22.6654
11250.1292 | 718.8624 | 636.7377 | 485.537 | 463.4125 | 474.8805 | 649.5048 | 673.6852 | 658.5418 | NaN | NaN | NaN | 663.3899 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.5233 | NaN | 22.2986
11251.1292 | 718.0882 | 636.5144 | 485.6786 | 463.7122 | 475.3657 | 647.3324 | 672.8756 | 658.7373 | NaN | NaN | NaN | 654.3099 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.1169 | NaN | 21.8262
11252.1292 | 716.6504 | 635.9879 | 485.4821 | 463.9176 | 475.3632 | 643.1001 | 677.4178 | 662.1157 | NaN | NaN | NaN | 675.2351 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.1827 | NaN | 21.5511
11253.1292 | 717.5586 | 635.9676 | 485.6989 | 463.779 | 475.5226 | 643.4699 | 682.5119 | 655.0036 | NaN | NaN | NaN | 689.5088 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.4269 | NaN | 22.7337
11254.1292 | 719.2418 | 635.9857 | 485.7435 | 463.7877 | 475.3698 | 644.9944 | 674.4755 | 666.4254 | NaN | NaN | NaN | 698.4183 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.8628 | NaN | 22.4678
11255.1292 | 720.2121 | 636.7859 | 485.6714 | 464.4756 | 475.5725 | 640.2985 | 665.8981 | 657.3711 | NaN | NaN | NaN | 688.6631 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.8936 | NaN | 21.891
11256.1292 | 720.3126 | 636.7972 | 486.0513 | 464.751 | 475.5844 | 637.1305 | 657.6625 | 650.3449 | NaN | NaN | NaN | 698.8442 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.0395 | NaN | 22.8329
11257.1292 | 720.5371 | 637.9924 | 486.527 | 465.3263 | 475.458 | 635.5031 | 657.1636 | 640.8867 | NaN | NaN | NaN | 684.9453 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.7894 | NaN | 22.5141
11258.1292 | 719.8125 | 638.5536 | 487.4333 | 465.6368 | 475.4141 | 631.9796 | 652.4439 | 641.8411 | NaN | NaN | NaN | 696.0128 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.4855 | NaN | 22.0974
11259.1292 | 720.1635 | 638.1916 | 488.0375 | 465.5849 | 475.1059 | 628.7018 | 646.0741 | 645.9029 | NaN | NaN | NaN | 693.6131 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.0668 | NaN | 21.3843
11260.1292 | 725.6114 | 638.7115 | 488.2864 | 465.4594 | 474.9081 | 628.2457 | 645.3558 | 653.8651 | NaN | NaN | NaN | 696.2472 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.5889 | NaN | 22.3685
11261.1292 | 730.9596 | 638.911 | 488.3976 | 465.531 | 474.6012 | 625.3866 | 642.2394 | 657.2681 | NaN | NaN | NaN | 691.7098 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.9671 | NaN | 22.3375
11262.1292 | 735.7442 | 639.3514 | 488.715 | 465.4926 | 474.1426 | 623.8929 | 641.1936 | 647.9057 | NaN | NaN | NaN | 678.7096 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.445 | NaN | 22.945
11263.1292 | 735.8025 | 639.1334 | 488.6015 | 465.3616 | 473.9799 | 626.4738 | 637.6033 | 642.863 | NaN | NaN | NaN | 693.2327 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.5863 | NaN | 22.2989
11264.1292 | 740.0182 | 639.5584 | 488.3811 | 465.4847 | 474.0152 | 623.9084 | 634.4914 | 634.6435 | NaN | NaN | NaN | 700.1341 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.6717 | NaN | 23.4707
11265.1292 | 741.9166 | 638.9389 | 488.3379 | 465.8492 | 474.2243 | 626.9131 | 637.3468 | 634.0971 | NaN | NaN | NaN | 695.4362 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.9679 | NaN | 23.4707
11266.1292 | 742.8172 | 638.9136 | 488.3419 | 465.693 | 474.7515 | 633.8179 | 635.1275 | 630.1105 | NaN | NaN | NaN | 679.5078 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.5638 | NaN | 24.6843
11267.1292 | 743.2492 | 639.4772 | 488.0946 | 465.6968 | 474.674 | 637.595 | 635.4266 | 627.3171 | NaN | NaN | NaN | 682.9894 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.6259 | NaN | 21.0967
11268.1292 | 745.7749 | 640.4359 | 488.3101 | 465.7967 | 474.7138 | 633.7265 | 634.2937 | 621.8194 | NaN | NaN | NaN | 675.9867 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.0626 | NaN | 23.4349
11269.1292 | 747.2798 | 640.8898 | 488.0852 | 466.2984 | 474.7089 | 633.188 | 635.7311 | 626.1166 | NaN | NaN | NaN | 686.8952 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.8747 | NaN | 22.6837
11270.1292 | 745.1631 | 640.8586 | 488.3784 | 466.4858 | 475.9521 | 631.3816 | 634.1647 | 622.5605 | NaN | NaN | NaN | 674.3416 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.0979 | NaN | 23.3145
11271.1292 | 742.6119 | 640.4847 | 488.651 | 466.4298 | 476.4008 | 627.6614 | 633.7271 | 634.484 | NaN | NaN | NaN | 682.7317 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 15.5325 | NaN | 21.9619
11272.1292 | 736.7756 | 639.9009 | 488.8173 | 466.3119 | 476.8627 | 628.1937 | 637.2423 | 644.9582 | NaN | NaN | NaN | 664.6381 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.3421 | NaN | 21.7032
11273.1292 | 732.5457 | 639.4778 | 488.7857 | 466.0194 | 476.4569 | 627.0135 | 640.9568 | 653.4324 | NaN | NaN | NaN | 644.8012 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.5923 | NaN | 23.1975
11274.1292 | 730.6052 | 638.5208 | 489.2575 | 465.9938 | 476.2058 | 629.8749 | 635.1636 | 643.8229 | NaN | NaN | NaN | 641.6436 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.3498 | NaN | 22.5642
11275.1292 | 728.5825 | 637.9297 | 489.6054 | 466.2598 | 476.0105 | 630.0165 | 643.263 | 637.068 | NaN | NaN | NaN | 651.4269 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.1758 | NaN | 22.1761
11276.1292 | 730.6466 | 638.1853 | 489.6156 | 466.426 | 476.0053 | 627.4772 | 643.389 | 637.8302 | NaN | NaN | NaN | 640.5834 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.4044 | NaN | 22.1709
11277.1292 | 733.6511 | 638.4375 | 489.7656 | 466.2822 | 476.4436 | 624.5344 | 640.2626 | 633.266 | NaN | NaN | NaN | 673.8862 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.843 | NaN | 23.1319
11278.1292 | 735.4574 | 639.0854 | 489.7038 | 466.3496 | 476.4407 | 623.1185 | 638.1547 | 631.7027 | NaN | NaN | NaN | 684.9051 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.2988 | NaN | 21.9811
11279.1292 | 738.5528 | 639.3268 | 489.4525 | 466.1911 | 476.7138 | 623.0178 | 638.7801 | 628.8917 | NaN | NaN | NaN | 693.8262 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.6603 | NaN | 22.6542
11280.1292 | 739.9142 | 639.7335 | 489.0356 | 466.0613 | 477.0557 | 633.2317 | 638.2396 | 625.4848 | NaN | NaN | NaN | 705.3587 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.8282 | NaN | 23.7171
11281.1292 | 739.7935 | 639.4096 | 488.7359 | 466.1364 | 477.3034 | 642.1518 | 641.5904 | 624.5506 | NaN | NaN | NaN | 721.2891 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.9683 | NaN | 20.9743
11282.1292 | 741.2257 | 639.2807 | 488.6359 | 466.0116 | 477.2315 | 637.8412 | 639.9665 | 628.1903 | NaN | NaN | NaN | 723.4991 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.1045 | NaN | 22.9886
11283.1292 | 742.0432 | 638.76 | 488.482 | 465.7805 | 477.1989 | 634.4284 | 635.7845 | 632.0239 | NaN | NaN | NaN | 725.9413 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.8326 | NaN | 20.4087
11284.1292 | 742.776 | 638.6606 | 488.2651 | 465.4186 | 476.9422 | 631.5191 | 632.9695 | 632.2358 | NaN | NaN | NaN | 726.8041 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.221 | NaN | 21.8707
11285.1292 | 745.1479 | 638.6928 | 488.2374 | 465.3239 | 476.8506 | 627.3658 | 630.3056 | 626.6126 | NaN | NaN | NaN | 736.4078 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.5896 | NaN | 23.5106
11286.1292 | 748.0873 | 638.9313 | 488.0786 | 465.2945 | 476.6418 | 626.9974 | 631.1451 | 624.8735 | NaN | NaN | NaN | 722.1508 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.1446 | NaN | 21.3355
11287.1292 | 747.3281 | 638.7641 | 488.0592 | 465.4124 | 476.3408 | 645.6939 | 632.6317 | 624.5226 | NaN | NaN | NaN | 717.1283 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.7939 | NaN | 22.4207
11288.1292 | 744.8353 | 638.3585 | 487.8284 | 465.5937 | 476.3302 | 649.9607 | 634.0131 | 633.543 | NaN | NaN | NaN | 703.3295 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.5917 | NaN | 22.2966
11289.1292 | 743.678 | 637.756 | 487.6929 | 465.6431 | 476.6276 | 647.1428 | 635.061 | 636.8618 | NaN | NaN | NaN | 706.0246 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.7971 | NaN | 21.644
11290.1292 | 742.2279 | 636.9835 | 487.871 | 465.8267 | 477.3241 | 647.1501 | 639.4472 | 635.3593 | NaN | NaN | NaN | 681.5511 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.8282 | NaN | 22.5383
11291.1292 | 741.3075 | 636.3418 | 487.6756 | 465.5943 | 477.6339 | 646.589 | 637.6996 | 649.6067 | NaN | NaN | NaN | 701.1323 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.9891 | NaN | 22.4918
11292.1292 | 739.2906 | 635.1426 | 487.3155 | 465.3752 | 477.6778 | 650.5196 | 639.4029 | 651.4337 | NaN | NaN | NaN | 741.6706 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.0709 | NaN | 22.2716
11293.1292 | 737.2004 | 634.3938 | 487.216 | 465.4235 | 477.8741 | 644.5179 | 634.8561 | 639.3366 | NaN | NaN | NaN | 757.7193 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.4909 | NaN | 22.3761
11294.1292 | 736.7098 | 634.4022 | 487.1333 | 465.3614 | 477.6436 | 636.2314 | 631.0125 | 631.5277 | NaN | NaN | NaN | 766.8707 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.5904 | NaN | 23.2821
11295.1292 | 737.9726 | 633.4947 | 487.4789 | 465.1336 | 477.3756 | 629.5636 | 627.8657 | 625.6594 | NaN | NaN | NaN | 745.3035 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.2704 | NaN | 22.4148
11296.1292 | 738.1839 | 634.1989 | 487.29 | 465.0076 | 477.0598 | 627.2753 | 625.6924 | 620.8468 | NaN | NaN | NaN | 734.8452 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.2304 | NaN | 21.8205
11297.1292 | 738.6962 | 634.7887 | 487.1816 | 464.669 | 476.5624 | 631.7931 | 624.5492 | 623.5345 | NaN | NaN | NaN | 708.339 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.1403 | NaN | 21.0096
11298.1292 | 737.5132 | 635.2036 | 487.1276 | 464.7512 | 476.386 | 631.4227 | 625.0906 | 635.0298 | NaN | NaN | NaN | 698.7527 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.1654 | NaN | 21.7132
11299.1292 | 734.3406 | 634.718 | 487.2023 | 464.5034 | 476.2062 | 630.4094 | 626.1342 | 636.656 | NaN | NaN | NaN | 678.6963 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.2376 | NaN | 23.0928
11300.1292 | 731.7604 | 634.4739 | 487.6433 | 464.047 | 476.1823 | 630.6961 | 631.4396 | 634.368 | NaN | NaN | NaN | 708.6875 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.0715 | NaN | 23.5215
11301.1292 | 730.9269 | 634.3394 | 487.7532 | 463.7252 | 476.0034 | 628.8547 | 632.9409 | 637.4813 | NaN | NaN | NaN | 720.1882 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.3549 | NaN | 21.6139
11302.1292 | 730.304 | 633.9186 | 488.2819 | 463.4191 | 475.6911 | 625.7786 | 632.3284 | 641.6826 | NaN | NaN | NaN | 757.8758 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 17.7354 | NaN | 34.1873
11303.1448 | 729.1876 | 633.3139 | 488.1713 | 463.6116 | 475.6062 | 622.8462 | 630.9206 | 646.6977 | NaN | NaN | NaN | 772.4647 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 22.0114 | NaN | 22.0618
11304.1292 | 730.6498 | 634.4048 | 487.8519 | 464.4287 | 475.7712 | 621.7623 | 632.8067 | 654.1907 | NaN | NaN | NaN | 776.1277 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.8549 | NaN | 23.8435
11305.1292 | 734.2128 | 634.3762 | 487.955 | 464.6264 | 475.8154 | 618.8478 | 632.2079 | 659.159 | NaN | NaN | NaN | 790.4671 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.4634 | NaN | 23.488
11306.1292 | 734.7963 | 634.2853 | 487.6727 | 465.0825 | 475.8579 | 616.6353 | 632.0143 | 647.2689 | NaN | NaN | NaN | 795.436 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.2962 | NaN | 25.4345
11307.1292 | 734.4622 | 634.0078 | 487.4347 | 465.3598 | 476.0641 | 615.5876 | 637.8543 | 642.2955 | NaN | NaN | NaN | 789.4378 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.3168 | NaN | 23.0128
11308.1292 | 735.3755 | 633.9456 | 487.1305 | 465.4717 | 475.8464 | 623.426 | 637.8474 | 647.3338 | NaN | NaN | NaN | 790.9039 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.7221 | NaN | 23.8266
11309.1292 | 736.7078 | 634.7877 | 486.79 | 465.4663 | 475.5113 | 629.5046 | 639.1728 | 648.7465 | NaN | NaN | NaN | 790.3674 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.5882 | NaN | 20.0166
11310.1292 | 737.0815 | 634.684 | 486.525 | 465.3243 | 475.6747 | 639.0612 | 638.1074 | 643.2393 | NaN | NaN | NaN | 771.4364 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.7085 | NaN | 22.5221
11311.1292 | 736.3609 | 634.5183 | 486.6032 | 465.4612 | 475.6699 | 640.6903 | 636.8535 | 641.8403 | NaN | NaN | NaN | 768.4007 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 20.3094 | NaN | -0.9961
11312.1292 | 734.2467 | 635.2685 | 486.6964 | 465.36 | 475.6821 | 641.9972 | 643.9569 | 660.6364 | NaN | NaN | NaN | 777.0809 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.1153 | NaN | 22.0438
11313.1292 | 734.1768 | 635.6796 | 486.6425 | 465.3813 | 475.8428 | 647.4158 | 644.2611 | 657.2439 | NaN | NaN | NaN | 757.2545 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.3573 | NaN | 18.6492
11314.1292 | 734.0527 | 635.9264 | 486.9031 | 465.0315 | 475.8677 | 648.1385 | 646.5164 | 656.6235 | NaN | NaN | NaN | 749.036 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.0821 | NaN | 20.8254
11315.1292 | 735.1926 | 636.2492 | 487.1593 | 464.7569 | 475.8521 | 648.655 | 646.1554 | 652.2736 | NaN | NaN | NaN | 744.6136 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.1403 | NaN | 22.5615
11316.1292 | 737.3239 | 636.9871 | 487.2657 | 464.5097 | 476.1644 | 641.6544 | 641.8598 | 655.4337 | NaN | NaN | NaN | 702.6354 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.5923 | NaN | 22.7842
11317.1292 | 736.4068 | 637.0726 | 487.4222 | 464.3364 | 476.5119 | 636.7625 | 638.0348 | 653.7435 | NaN | NaN | NaN | 670.1 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 33.5271 | NaN | 22.2062
11318.1292 | 736.6325 | 637.3536 | 487.5325 | 464.196 | 476.7732 | 632.7313 | 633.0844 | 657.437 | NaN | NaN | NaN | 641.2265 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.5208 | NaN | 20.1969
11319.1292 | 735.7144 | 637.3381 | 488.0983 | 464.8987 | 476.7627 | 629.4183 | 634.4501 | 656.8381 | NaN | NaN | NaN | 616.9281 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 17.7116 | NaN | 21.7056
11320.1292 | 734.2855 | 638.585 | 489.1369 | 465.2728 | 476.7535 | 627.3986 | 641.5543 | 657.571 | NaN | NaN | NaN | 606.3203 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 40.8496 | NaN | 22.18
11321.1292 | 733.3571 | 639.4762 | 490.0227 | 465.4129 | 476.7333 | 625.816 | 642.4108 | 663.805 | NaN | NaN | NaN | 624.1293 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 56.5946 | NaN | 22.5005
11322.1292 | 732.5537 | 641.3529 | 491.2665 | 465.7449 | 477.0452 | 626.2596 | 651.1977 | 661.706 | NaN | NaN | NaN | 601.0196 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.6424 | NaN | 23.6962
11323.1292 | 731.5664 | 642.8828 | 492.6467 | 466.5153 | 477.1984 | 629.4928 | 656.4361 | 658.8422 | NaN | NaN | NaN | 625.1172 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.3971 | NaN | 22.7115
11324.1292 | 732.3198 | 643.535 | 493.2363 | 467.7639 | 477.6051 | 630.0266 | 652.041 | 659.0696 | NaN | NaN | NaN | 668.0366 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.4357 | NaN | 23.1433
11325.1448 | 733.2183 | 644.5064 | 493.8091 | 468.3984 | 478.0956 | 630.761 | 649.9013 | 651.6891 | NaN | NaN | NaN | 684.9752 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.9137 | NaN | 21.5835
11326.1292 | 732.4259 | 643.6349 | 494.2515 | 469.0507 | 477.767 | 628.212 | 645.2984 | 645.3843 | NaN | NaN | NaN | 655.693 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.0215 | NaN | 22.5703
11327.1292 | 731.1473 | 643.4794 | 494.7903 | 469.2885 | 477.8808 | 626.6333 | 640.6618 | 642.7329 | NaN | NaN | NaN | 630.3586 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.807 | NaN | 23.1237
11328.1292 | 729.9717 | 642.9042 | 495.3618 | 469.3366 | 477.9447 | 623.7767 | 635.9682 | 635.1983 | NaN | NaN | NaN | 653.715 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.3916 | NaN | 22.19
11329.1292 | 730.5284 | 641.8927 | 496.2952 | 469.1229 | 478.1088 | 624.8225 | 634.1279 | 628.6103 | NaN | NaN | NaN | 635.4828 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.8448 | NaN | 22.8751
11330.1292 | 731.7543 | 642.4362 | 496.7136 | 469.2696 | 478.1801 | 621.8133 | 632.6302 | 636.5586 | NaN | NaN | NaN | 643.264 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.1212 | NaN | 22.493
11331.1292 | 733.37 | 641.9468 | 497.0149 | 469.2789 | 477.8326 | 619.4904 | 630.0675 | 632.9763 | NaN | NaN | NaN | 684.0605 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.0739 | NaN | 21.1362
11332.1292 | 733.7342 | 641.1384 | 497.1135 | 468.9382 | 477.375 | 616.4495 | 627.287 | 625.8486 | NaN | NaN | NaN | 708.2829 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.0841 | NaN | 22.9714
11333.1448 | 736.0646 | 641.246 | 497.1523 | 468.7016 | 477.0657 | 614.3365 | 626.2442 | 627.5792 | NaN | NaN | NaN | 704.8966 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.7692 | NaN | 22.9497
11334.1292 | 737.0408 | 639.5721 | 497.3386 | 468.648 | 477.2696 | 613.2697 | 624.108 | 625.512 | NaN | NaN | NaN | 711.4752 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.7307 | NaN | 21.723
11335.1292 | 738.8377 | 639.4427 | 497.4977 | 468.606 | 477.0971 | 609.7724 | 620.9887 | 617.4007 | NaN | NaN | NaN | 720.3051 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.2707 | NaN | 21.6109
11336.1292 | 739.5157 | 639.1635 | 497.717 | 468.4194 | 476.4659 | 607.9424 | 619.7736 | 611.8118 | NaN | NaN | NaN | 696.5757 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.807 | NaN | 21.9322
11337.1292 | 738.7349 | 639.2823 | 497.9859 | 468.2674 | 475.9486 | 620.8418 | 623.7404 | 613.5074 | NaN | NaN | NaN | 715.1237 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.7002 | NaN | 22.5259
11338.1292 | 738.7067 | 638.8771 | 497.9158 | 468.4825 | 476.1274 | 616.6431 | 622.6251 | 607.5901 | NaN | NaN | NaN | 712.7801 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.7089 | NaN | 21.414
11339.1292 | 736.5156 | 638.5416 | 497.4999 | 468.522 | 476.3719 | 618.7508 | 624.3269 | 605.7058 | NaN | NaN | NaN | 732.3654 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.1205 | NaN | 24.0329
11340.1292 | 736.3882 | 637.744 | 497.1338 | 468.3574 | 476.6695 | 616.9007 | 622.4283 | 613.2385 | NaN | NaN | NaN | 746.613 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.7014 | NaN | 23.1604
11341.1292 | 736.431 | 636.8898 | 497.1498 | 468.2008 | 476.8346 | 614.4189 | 623.9932 | 609.4048 | NaN | NaN | NaN | 759.345 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.4006 | NaN | 21.9768
11342.1292 | 736.9253 | 637.1139 | 496.8777 | 467.7328 | 477.0271 | 618.9115 | 624.6485 | 615.8773 | NaN | NaN | NaN | 729.9281 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.8081 | NaN | 21.2953
11343.1292 | 735.576 | 636.3621 | 496.4219 | 467.3662 | 476.831 | 624.5306 | 622.7855 | 617.484 | NaN | NaN | NaN | 731.8137 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.4459 | NaN | 22.031
11344.1292 | 733.639 | 636.2034 | 495.8032 | 467.3243 | 476.7414 | 622.846 | 624.5466 | 630.5978 | NaN | NaN | NaN | 721.8015 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.8084 | NaN | 21.7319
11345.1292 | 731.3173 | 636.1497 | 495.4569 | 467.303 | 476.5821 | 626.7396 | 623.591 | 635.623 | NaN | NaN | NaN | 696.323 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.0138 | NaN | 22.979
11346.1292 | 728.7702 | 635.6619 | 495.33 | 466.8893 | 476.569 | 623.6958 | 623.6861 | 633.9619 | NaN | NaN | NaN | 683.0121 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.8093 | NaN | 22.983
11347.1292 | 726.6646 | 634.8287 | 494.9492 | 466.6109 | 476.5353 | 623.7935 | 629.2114 | 633.3049 | NaN | NaN | NaN | 679.3455 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.6818 | NaN | 22.8669
11348.1292 | 726.9007 | 634.4463 | 494.6516 | 466.6394 | 476.5234 | 619.6735 | 635.39 | 625.2962 | NaN | NaN | NaN | 694.6568 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.7512 | NaN | 23.2581
11349.1292 | 728.7515 | 634.1402 | 494.1798 | 466.7138 | 476.0826 | 615.9741 | 636.6275 | 624.6364 | NaN | NaN | NaN | 687.6167 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.9179 | NaN | 15.5754
11350.1292 | 730.53 | 634.5548 | 493.8898 | 466.692 | 476.0273 | 614.1033 | 631.8235 | 631.7287 | NaN | NaN | NaN | 703.1611 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 19.5456 | NaN | 21.9364
11351.1292 | 730.578 | 633.9836 | 493.6846 | 467.1347 | 475.6695 | 613.4962 | 629.9274 | 637.1372 | NaN | NaN | NaN | 709.7247 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.6331 | NaN | 22.7554
11352.1292 | 730.9441 | 633.6314 | 493.5549 | 467.132 | 475.4372 | 614.8834 | 626.9075 | 633.4158 | NaN | NaN | NaN | 691.4787 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.5409 | NaN | 23.4056
11353.1292 | 729.6097 | 632.8587 | 493.1579 | 466.9805 | 475.0439 | 615.8512 | 624.3859 | 637.4653 | NaN | NaN | NaN | 693.7076 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 23.1999 | NaN | 22.7521
11354.1292 | 729.061 | 632.9461 | 492.591 | 466.8676 | 474.648 | 618.0444 | 622.4287 | 630.7109 | NaN | NaN | NaN | 686.8899 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 50.1219 | NaN | 22.304
11355.1292 | 728.9089 | 633.1367 | 492.4214 | 466.5802 | 474.1935 | 616.7276 | 621.3651 | 634.4881 | NaN | NaN | NaN | 711.4001 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.2142 | NaN | 22.4952
11356.1292 | 726.2708 | 632.6565 | 492.0636 | 466.2111 | 473.5052 | 619.3912 | 618.97 | 638.8804 | NaN | NaN | NaN | 718.3045 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.3237 | NaN | 21.7871
11357.1292 | 723.8901 | 632.296 | 492.2144 | 465.9086 | 472.6444 | 617.4714 | 629.8812 | 640.626 | NaN | NaN | NaN | 747.028 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 31.2565 | NaN | 22.3157
11358.1292 | 723.5766 | 632.0115 | 492.132 | 465.988 | 472.1418 | 616.6223 | 637.1874 | 637.7218 | NaN | NaN | NaN | 751.3709 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 23.1511 | NaN | 24.3846
11359.1292 | 726.5563 | 632.357 | 492.298 | 465.6439 | 471.7105 | 615.1292 | 639.1853 | 640.3678 | NaN | NaN | NaN | 728.8196 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.9579 | NaN | 21.9974
11360.1292 | 729.8436 | 632.6653 | 492.3347 | 466.0165 | 472.0434 | 612.3133 | 635.1434 | 639.4076 | NaN | NaN | NaN | 704.9136 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.8748 | NaN | 19.7585
11361.1292 | 731.728 | 634.3236 | 492.3547 | 466.1605 | 472.4014 | 613.2274 | 634.996 | 646.4062 | NaN | NaN | NaN | 694.4811 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.794 | NaN | 23.5345
11362.1292 | 733.9886 | 635.296 | 492.154 | 466.7172 | 472.8314 | 611.908 | 634.361 | 653.2753 | NaN | NaN | NaN | 685.3554 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 35.4924 | NaN | 22.5146
11363.1292 | 735.844 | 635.1102 | 491.827 | 467.1267 | 473.4255 | 611.1514 | 635.7415 | 649.3075 | NaN | NaN | NaN | 703.275 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.5039 | NaN | 20.7552
11364.1292 | 737.4945 | 635.6131 | 491.5225 | 467.4442 | 474.1244 | 618.4256 | 634.6513 | 651.8864 | NaN | NaN | NaN | 720.1826 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.5278 | NaN | 20.8926
11365.1292 | 739.1124 | 635.7043 | 491.3291 | 467.7917 | 474.3972 | 624.6349 | 632.7523 | 662.543 | NaN | NaN | NaN | 742.871 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.6067 | NaN | 21.8175
11366.1292 | 739.9057 | 635.8729 | 491.216 | 468.0227 | 474.5117 | 622.0336 | 628.4772 | 667.4805 | NaN | NaN | NaN | 748.6741 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.9035 | NaN | 20.4559
11367.1292 | 741.9959 | 635.8964 | 491.2792 | 468.167 | 474.3849 | 620.9417 | 629.4148 | 660.7195 | NaN | NaN | NaN | 753.3168 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.6735 | NaN | 22.7729
11368.1292 | 744.461 | 637.4627 | 491.4014 | 468.0766 | 474.1317 | 617.6597 | 627.1333 | 667.7918 | NaN | NaN | NaN | 755.2006 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.0191 | NaN | 22.2915
11369.1292 | 746.5071 | 638.3352 | 491.6524 | 468.508 | 474.4659 | 616.0404 | 628.414 | 664.4207 | NaN | NaN | NaN | 771.5288 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.6953 | NaN | 20.9633
11370.1292 | 747.7823 | 638.5959 | 491.8224 | 468.9332 | 474.8658 | 615.4918 | 627.5477 | 655.2827 | NaN | NaN | NaN | 742.2129 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.5427 | NaN | 20.1688
11371.1292 | 748.0992 | 638.3947 | 492.1595 | 469.2321 | 475.3019 | 612.3465 | 624.4213 | 643.5715 | NaN | NaN | NaN | 733.6993 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.4395 | NaN | 19.8646
11372.1292 | 750.9725 | 638.2184 | 492.2167 | 469.1559 | 475.1911 | 609.4037 | 622.0536 | 637.9832 | NaN | NaN | NaN | 720.7872 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.5141 | NaN | 21.4007
11373.1292 | 750.9506 | 638.7202 | 492.4139 | 469.0939 | 475.6468 | 609.2406 | 619.9889 | 630.6778 | NaN | NaN | NaN | 741.5891 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.912 | NaN | 18.9932
11374.1292 | 752.1396 | 638.4208 | 492.5833 | 469.3807 | 475.7528 | 608.0903 | 619.5617 | 625.5737 | NaN | NaN | NaN | 728.7135 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.1505 | NaN | 22.7633
11375.1292 | 751.6931 | 637.4918 | 492.529 | 469.4933 | 475.8964 | 607.7638 | 619.9902 | 636.8529 | NaN | NaN | NaN | 710.6772 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.4234 | NaN | 21.3114
11376.1292 | 750.6958 | 636.4434 | 492.3548 | 469.01 | 475.5016 | 604.9501 | 618.5431 | 639.466 | NaN | NaN | NaN | 720.1168 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.6183 | NaN | 20.4254
11377.1292 | 751.9336 | 637.1523 | 492.0768 | 468.4919 | 475.3372 | 603.88 | 618.6482 | 636.7665 | NaN | NaN | NaN | 726.0956 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.3559 | NaN | 23.7472
11378.1292 | 750.8263 | 637.8889 | 492.1878 | 468.3079 | 475.686 | 605.3264 | 621.941 | 635.5471 | NaN | NaN | NaN | 692.5256 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.7246 | NaN | 22.9319
11379.1292 | 747.5529 | 638.7233 | 492.3216 | 468.1884 | 475.6239 | 612.9829 | 625.3125 | 629.843 | NaN | NaN | NaN | 680.6934 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.9191 | NaN | 21.2861
11380.1292 | 744.7316 | 638.0053 | 492.7227 | 468.5025 | 475.6622 | 618.2413 | 625.5604 | 622.3757 | NaN | NaN | NaN | 677.3889 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.5814 | NaN | 22.3361
11381.1292 | 741.3219 | 637.7998 | 492.8428 | 468.6059 | 475.7492 | 620.8606 | 627.378 | 616.8478 | NaN | NaN | NaN | 697.58 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.9993 | NaN | 21.8737
11382.1292 | 738.8574 | 637.4928 | 492.971 | 468.9197 | 475.7816 | 623.142 | 630.6733 | 619.6415 | NaN | NaN | NaN | 681.8608 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.3377 | NaN | 21.4087
11383.1292 | 736.0099 | 637.2188 | 493.0733 | 469.1462 | 475.9904 | 621.291 | 632.0654 | 627.2127 | NaN | NaN | NaN | 687.8954 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.0023 | NaN | 21.7409
11384.1292 | 734.9879 | 636.6042 | 493.027 | 469.0403 | 476.3449 | 619.6511 | 629.4536 | 625.2916 | NaN | NaN | NaN | 666.5058 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.0213 | NaN | 21.807
11385.1448 | 733.2187 | 635.9305 | 493.0089 | 469.1729 | 476.4909 | 625.2726 | 630.7251 | 628.3984 | NaN | NaN | NaN | 636.4622 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.0764 | NaN | 23.1204
11386.1292 | 730.5647 | 636.1258 | 493.0708 | 469.578 | 476.4524 | 626.4373 | 637.6187 | 627.6458 | NaN | NaN | NaN | 646.7745 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.671 | NaN | 21.3061
11387.1292 | 728.1541 | 635.5075 | 493.3458 | 469.7879 | 476.4903 | 624.006 | 634.5867 | 627.3869 | NaN | NaN | NaN | 652.0726 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.8071 | NaN | 23.4967
11388.1292 | 727.5318 | 634.6713 | 493.2811 | 469.7939 | 476.7128 | 620.5584 | 631.2406 | 632.8895 | NaN | NaN | NaN | 671.6047 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.501 | NaN | 20.817
11389.1292 | 728.771 | 634.7301 | 493.1837 | 469.7488 | 476.8736 | 617.0014 | 628.0682 | 637.8242 | NaN | NaN | NaN | 653.833 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.2286 | NaN | 22.8595
11390.1292 | 731.1187 | 634.4854 | 492.9856 | 469.5404 | 476.5921 | 619.9018 | 627.1493 | 635.3158 | NaN | NaN | NaN | 668.0587 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.2668 | NaN | 20.7813
11391.1292 | 734.3178 | 635.0522 | 493.015 | 469.892 | 476.2822 | 616.5409 | 625.6264 | 630.155 | NaN | NaN | NaN | 677.0136 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.7886 | NaN | 22.3459
11392.1292 | 737.0167 | 635.1959 | 493.0061 | 469.8734 | 476.2824 | 613.7822 | 622.7852 | 626.8909 | NaN | NaN | NaN | 684.0788 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.3567 | NaN | 24.3008
11393.1292 | 737.5055 | 634.9051 | 492.8747 | 469.8008 | 476.0751 | 612.3278 | 621.6629 | 645.7025 | NaN | NaN | NaN | 697.2441 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.3345 | NaN | 22.9359
11394.1292 | 737.4138 | 634.9958 | 492.8271 | 469.7304 | 476.1446 | 611.4382 | 618.2987 | 643.4752 | NaN | NaN | NaN | 684.6199 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.5584 | NaN | 21.503
11395.1292 | 738.4845 | 635.9882 | 492.9637 | 470.1294 | 475.8881 | 610.2748 | 616.8897 | 641.0376 | NaN | NaN | NaN | 676.8728 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.2229 | NaN | 22.7651
11396.1292 | 741.82 | 637.4884 | 493.1685 | 470.1796 | 476.2448 | 608.7646 | 618.2934 | 641.662 | NaN | NaN | NaN | 688.5594 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.2172 | NaN | 22.6971
11397.1292 | 745.8109 | 638.3773 | 493.1707 | 470.2734 | 476.377 | 607.0406 | 619.3403 | 635.2684 | NaN | NaN | NaN | 706.9362 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.2188 | NaN | 22.2576
11398.1292 | 747.942 | 638.714 | 492.9742 | 470.1303 | 476.1997 | 609.8338 | 618.4481 | 626.8396 | NaN | NaN | NaN | 704.2139 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.3324 | NaN | 19.6063
11399.1292 | 746.6299 | 638.6888 | 492.8426 | 470.404 | 476.143 | 608.2394 | 617.3775 | 619.5063 | NaN | NaN | NaN | 712.3139 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.8354 | NaN | 23.1087
11400.1292 | 744.5455 | 638.3741 | 493.0701 | 470.6325 | 476.2763 | 608.2265 | 614.6865 | 623.1455 | NaN | NaN | NaN | 716.5263 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.2332 | NaN | 23.1101
11401.1292 | 743.8496 | 637.7117 | 493.7872 | 470.3776 | 476.0865 | 609.1919 | 616.1421 | 619.6066 | NaN | NaN | NaN | 705.0651 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.2983 | NaN | 20.3874
11402.1292 | 743.1814 | 636.9425 | 494.0112 | 470.4686 | 475.6746 | 607.8327 | 616.0517 | 625.9267 | NaN | NaN | NaN | 689.2148 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.2784 | NaN | 21.4223
11403.1292 | 740.2648 | 636.9807 | 494.1132 | 470.1796 | 475.7708 | 616.5693 | 623.5176 | 626.3276 | NaN | NaN | NaN | 648.3204 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.7066 | NaN | 22.8109
11404.1292 | 736.7259 | 637.6563 | 494.2747 | 470.3649 | 476.7274 | 624.446 | 629.8216 | 630.9485 | NaN | NaN | NaN | 673.4442 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.3329 | NaN | 22.2869
11405.1292 | 733.8523 | 637.2951 | 494.5555 | 471.0144 | 477.294 | 633.0258 | 636.1377 | 631.619 | NaN | NaN | NaN | 698.7782 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.4931 | NaN | 20.3969
11406.1292 | 734.1708 | 637.3201 | 494.8293 | 471.3973 | 477.9098 | 633.1341 | 632.9109 | 622.6645 | NaN | NaN | NaN | 687.0768 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.4434 | NaN | 22.3154
11407.1292 | 733.0849 | 636.6874 | 494.5924 | 471.3847 | 477.7456 | 632.9838 | 632.3782 | 618.7861 | NaN | NaN | NaN | 697.0495 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.209 | NaN | 21.6273
11408.1292 | 731.9604 | 636.206 | 494.4008 | 470.9138 | 478.1426 | 628.8603 | 627.3182 | 625.8002 | NaN | NaN | NaN | 682.3837 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.7312 | NaN | 20.8047
11409.1292 | 731.2508 | 635.323 | 494.0062 | 470.6863 | 477.5518 | 629.2862 | 627.8701 | 629.1073 | NaN | NaN | NaN | 681.879 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.2102 | NaN | 22.9728
11410.1292 | 731.911 | 636.1798 | 493.678 | 470.32 | 477.6326 | 630.4736 | 625.3058 | 630.5823 | NaN | NaN | NaN | 682.1039 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.584 | NaN | 21.595
11411.1292 | 736.0533 | 636.6159 | 493.57 | 469.9635 | 477.5594 | 626.5966 | 622.7956 | 625.6099 | NaN | NaN | NaN | 685.4927 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.178 | NaN | 21.0999
11412.1292 | 737.6082 | 637.9196 | 493.8337 | 469.6671 | 477.3341 | 628.6924 | 622.8042 | 618.3449 | NaN | NaN | NaN | 678.8137 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.2694 | NaN | 20.1893
11413.1292 | 740.3688 | 638.0365 | 494.247 | 469.6039 | 477.7778 | 624.6967 | 622.0196 | 616.292 | NaN | NaN | NaN | 691.8908 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.837 | NaN | 23.0283
11414.1292 | 745.1735 | 638.896 | 494.1379 | 469.2935 | 477.5267 | 622.665 | 624.6289 | 612.605 | NaN | NaN | NaN | 676.1102 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.9013 | NaN | 21.7033
11415.1292 | 748.7458 | 638.8665 | 494.099 | 469.0305 | 477.7795 | 619.4959 | 623.3324 | 607.1419 | NaN | NaN | NaN | 718.3608 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.4774 | NaN | 21.2136
11416.1292 | 748.8032 | 640.0989 | 494.0558 | 468.8056 | 477.7951 | 618.5322 | 623.0512 | 602.5718 | NaN | NaN | NaN | 736.538 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.8455 | NaN | 21.9232
11417.1292 | 748.3581 | 641.1024 | 494.205 | 469.1622 | 478.436 | 616.5957 | 621.1747 | 599.4196 | NaN | NaN | NaN | 742.1146 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.2486 | NaN | 20.6951
11418.1292 | 749.8381 | 641.2259 | 494.644 | 469.4636 | 478.3511 | 615.8608 | 622.42 | 596.6747 | NaN | NaN | NaN | 741.0717 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.9333 | NaN | 21.7888
11419.1292 | 749.4271 | 642.027 | 495.1068 | 469.1337 | 477.7197 | 615.2516 | 620.3803 | 593.6238 | NaN | NaN | NaN | 737.7365 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.2496 | NaN | 20.6187
11420.1292 | 753.213 | 641.7766 | 495.6632 | 469.0232 | 477.2725 | 613.7021 | 620.1164 | 596.7854 | NaN | NaN | NaN | 733.1149 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.566 | NaN | 21.4675
11421.1292 | 757.1621 | 642.4623 | 495.8899 | 469.2559 | 476.9832 | 611.7026 | 619.4097 | 594.9122 | NaN | NaN | NaN | 721.2104 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.2386 | NaN | 23.0834
11422.1292 | 759.4994 | 641.1787 | 496.0137 | 469.3516 | 477.1856 | 609.6258 | 618.213 | 598.0079 | NaN | NaN | NaN | 737.6511 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.6561 | NaN | 18.9985
11423.1448 | 759.6279 | 640.5301 | 496.0702 | 469.9227 | 477.077 | 606.4362 | 616.9834 | 595.2244 | NaN | NaN | NaN | 737.1944 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.0565 | NaN | 22.065
11424.1292 | 757.7764 | 640.2509 | 496.4176 | 470.1678 | 477.0112 | 603.1165 | 614.1506 | 592.4237 | NaN | NaN | NaN | 734.9012 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.2722 | NaN | 23.1371
11425.1292 | 758.5471 | 641.1959 | 496.314 | 470.4637 | 477.3944 | 603.2653 | 614.6303 | 589.4355 | NaN | NaN | NaN | 735.0127 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.888 | NaN | 21.9911
11426.1292 | 759.8932 | 640.8801 | 496.3693 | 470.5793 | 477.6224 | 601.9268 | 614.1558 | 588.8748 | NaN | NaN | NaN | 736.7027 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.4212 | NaN | 22.8598
11427.1292 | 756.4835 | 639.832 | 496.3265 | 470.7817 | 477.4979 | 606.5661 | 614.5948 | 587.5187 | NaN | NaN | NaN | 740.0678 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.8597 | NaN | 22.0273
11428.1292 | 752.6124 | 639.2956 | 496.4547 | 470.7362 | 477.6686 | 609.3871 | 613.261 | 584.01 | NaN | NaN | NaN | 717.3819 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 21.1513 | NaN | 22.0939
11429.1292 | 748.5116 | 638.2438 | 496.1708 | 470.5442 | 477.5693 | 606.2635 | 611.7749 | 588.8537 | NaN | NaN | NaN | 720.3787 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 56.6005 | NaN | 22.7042
11430.1292 | 744.7975 | 637.4849 | 495.8307 | 470.3073 | 478.0162 | 604.2286 | 613.0435 | 590.8709 | NaN | NaN | NaN | 736.3611 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 49.0415 | NaN | 23.654
11431.1292 | 741.9832 | 637.6038 | 495.6453 | 470.2082 | 478.0898 | 610.9346 | 616.4819 | 597.96 | NaN | NaN | NaN | 731.2475 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.1077 | NaN | 22.3011
11432.1292 | 738.2682 | 637.4287 | 495.4027 | 470.2232 | 478.0313 | 611.8704 | 617.1197 | 595.3747 | NaN | NaN | NaN | 700.7745 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.5921 | NaN | 22.3076
11433.1292 | 734.9322 | 636.4319 | 495.2033 | 470.7859 | 477.8008 | 610.0531 | 615.5359 | 597.0336 | NaN | NaN | NaN | 709.9076 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.6106 | NaN | 25.0185
11434.1292 | 731.722 | 635.8502 | 494.7645 | 471.1389 | 477.307 | 610.5239 | 617.0857 | 597.2864 | NaN | NaN | NaN | 705.0252 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.7398 | NaN | 22.8331
11435.1292 | 730.2849 | 635.9917 | 494.598 | 471.5057 | 477.4161 | 617.5314 | 615.889 | 592.8839 | NaN | NaN | NaN | 717.1176 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.392 | NaN | 22.353
11436.1292 | 728.4245 | 635.722 | 495.0977 | 471.6083 | 477.6409 | 615.9062 | 619.086 | 610.9889 | NaN | NaN | NaN | 734.7399 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.7136 | NaN | 22.0417
11437.1292 | 726.9195 | 635.2108 | 494.7449 | 471.4119 | 477.8052 | 614.8112 | 618.4309 | 615.7247 | NaN | NaN | NaN | 732.2493 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.6302 | NaN | 20.3578
11438.1292 | 725.0497 | 635.7894 | 494.5057 | 471.0053 | 478.048 | 617.2106 | 623.0051 | 614.7824 | NaN | NaN | NaN | 740.1428 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.8285 | NaN | 22.9367
11439.1292 | 725.0208 | 635.2435 | 494.6393 | 471.0043 | 478.0271 | 614.6931 | 620.138 | 614.235 | NaN | NaN | NaN | 706.4512 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.0053 | NaN | 22.7489
11440.1292 | 724.5845 | 635.1012 | 494.6397 | 471.1457 | 478.0261 | 612.4971 | 617.9885 | 615.1946 | NaN | NaN | NaN | 673.5173 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.4322 | NaN | 18.2527
11441.1292 | 724.5943 | 634.6636 | 494.5648 | 470.8487 | 477.6682 | 615.4915 | 615.1074 | 610.2697 | NaN | NaN | NaN | 661.1424 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.3585 | NaN | 22.9861
11442.1292 | 726.2484 | 634.7945 | 494.5531 | 470.6025 | 477.393 | 613.1811 | 612.3732 | 616.1793 | NaN | NaN | NaN | 656.4093 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.2859 | NaN | 21.2286
11443.1292 | 726.3123 | 634.5154 | 494.5979 | 470.062 | 476.9159 | 609.9532 | 610.9771 | 618.4546 | NaN | NaN | NaN | 640.3239 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.634 | NaN | 20.0675
11444.1292 | 726.4653 | 634.66 | 494.3244 | 469.6567 | 476.497 | 608.6179 | 610.9621 | 611.215 | NaN | NaN | NaN | 624.6638 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.2292 | NaN | 18.9939
11445.1448 | 727.2197 | 634.6531 | 493.9744 | 469.3863 | 476.7796 | 614.6928 | 609.5793 | 616.9201 | NaN | NaN | NaN | 644.824 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.4933 | NaN | 26.4519
11446.1292 | 726.6812 | 634.9844 | 493.6538 | 469.0017 | 476.6167 | 618.7462 | 611.7325 | 624.5291 | NaN | NaN | NaN | 649.267 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 33.6696 | NaN | 23.6917
11447.1292 | 724.2468 | 634.9928 | 493.4609 | 468.993 | 476.6343 | 617.3217 | 613.343 | 627.5558 | NaN | NaN | NaN | 665.5088 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 1.0488 | NaN | 38.9884
11448.1292 | 722.7222 | 634.3013 | 493.1972 | 468.7157 | 476.5717 | 614.5646 | 615.2614 | 631.2097 | NaN | NaN | NaN | 661.5039 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.964 | NaN | 21.5694
11449.1292 | 724.1947 | 633.4551 | 493.3098 | 468.5238 | 476.2217 | 611.5304 | 611.7353 | 628.8652 | NaN | NaN | NaN | 645.7391 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 27.7449 | NaN | 9.8719
11450.1292 | 725.4509 | 633.3191 | 493.1727 | 468.5832 | 476.2073 | 633.4188 | 613.129 | 623.1656 | NaN | NaN | NaN | 673.9202 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 2.9928
11451.1292 | 724.7133 | 633.159 | 493.2289 | 468.8139 | 475.8046 | 631.3729 | 611.7152 | 614.8652 | NaN | NaN | NaN | 693.5783 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.4339 | NaN | 7.5566
11452.1292 | 722.839 | 633.6376 | 493.1933 | 468.7614 | 475.5341 | 626.5077 | 613.1997 | 618.002 | NaN | NaN | NaN | 701.356 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.3383 | NaN | 10.4966
11453.1448 | 721.6545 | 633.5067 | 493.2621 | 468.9161 | 475.1489 | 624.2959 | 611.8343 | 622.961 | NaN | NaN | NaN | 679.5701 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.2032 | NaN | 26.0289
11454.1292 | 721.6049 | 633.386 | 493.0474 | 468.8847 | 474.9259 | 622.2962 | 612.1936 | 622.4858 | NaN | NaN | NaN | 671.3558 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -12.0073 | NaN | 23.3007
11455.1292 | 721.8652 | 633.4565 | 492.9513 | 468.663 | 474.727 | 621.8465 | 612.0751 | 617.7398 | NaN | NaN | NaN | 663.2335 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -9.6089 | NaN | 22.494
11456.1292 | 721.2324 | 633.9958 | 492.9624 | 468.9828 | 474.572 | 620.1119 | 611.1017 | 615.9924 | NaN | NaN | NaN | 683.1809 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 30.1776 | NaN | 37.3149
11457.1292 | 721.7425 | 633.7959 | 492.8646 | 468.7947 | 474.61 | 619.331 | 610.2912 | 615.4313 | NaN | NaN | NaN | 681.157 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.6048 | NaN | 23.1067
11458.1292 | 723.9036 | 633.9868 | 492.7033 | 468.7857 | 474.5051 | 616.8668 | 609.4242 | 614.8855 | NaN | NaN | NaN | 670.0301 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 51.5258 | NaN | 22.0556
11459.1292 | 726.2911 | 634.4593 | 492.514 | 468.7235 | 474.3924 | 624.2171 | 612.8517 | 613.5989 | NaN | NaN | NaN | 646.3136 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 17.5414 | NaN | 19.9426
11460.1292 | 728.0469 | 635.511 | 492.3307 | 468.3802 | 473.8105 | 621.5263 | 613.6185 | 612.1748 | NaN | NaN | NaN | 640.8212 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.201 | NaN | 29.7444
11461.1292 | 728.1421 | 636.1147 | 492.1421 | 468.5328 | 473.6043 | 621.6162 | 615.6065 | 613.6008 | NaN | NaN | NaN | 649.3909 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 31.8527 | NaN | 14.1106
11462.1292 | 726.7707 | 635.8811 | 492.1198 | 468.4878 | 473.8831 | 622.2629 | 615.1241 | 605.6068 | NaN | NaN | NaN | 658.8452 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 40.0667 | NaN | 15.1469
11463.1292 | 726.5757 | 635.8655 | 492.2457 | 468.5589 | 474.0625 | 620.7884 | 613.2364 | 601.3494 | NaN | NaN | NaN | 677.7756 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.1365 | NaN | 21.2579
11464.1292 | 727.3121 | 635.8591 | 491.9784 | 468.3932 | 474.5582 | 629.1627 | 614.2584 | 603.5371 | NaN | NaN | NaN | 695.0722 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.8464 | NaN | 22.1924
11465.1292 | 728.1134 | 635.3717 | 491.85 | 468.0866 | 474.1226 | 625.8768 | 611.1306 | 598.9024 | NaN | NaN | NaN | 724.3343 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.5372 | NaN | 22.7182
11466.1292 | 728.3368 | 635.0994 | 491.8327 | 467.5339 | 473.4604 | 621.9877 | 608.1884 | 607.7471 | NaN | NaN | NaN | 740.9049 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.7136 | NaN | 22.6497
11467.1292 | 730.3248 | 635.4762 | 491.6476 | 467.6301 | 473.3051 | 619.5339 | 607.2834 | 607.0897 | NaN | NaN | NaN | 716.377 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.1129 | NaN | 22.2905
11468.1292 | 732.4639 | 636.1219 | 491.5681 | 467.4491 | 473.1837 | 617.7427 | 608.1251 | 610.2326 | NaN | NaN | NaN | 709.4862 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.7919 | NaN | 20.2198
11469.1292 | 731.9244 | 637.5627 | 491.5591 | 467.2764 | 472.9517 | 620.3881 | 610.7402 | 607.1427 | NaN | NaN | NaN | 671.5055 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 36.4674 | NaN | 20.2584
11470.1292 | 728.4059 | 636.9579 | 491.6428 | 467.1827 | 473.2813 | 623.173 | 614.3081 | 605.4623 | NaN | NaN | NaN | 686.0095 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 22.0346 | NaN | 21.447
11471.1292 | 725.4855 | 637.2625 | 491.9041 | 467.3456 | 474.1034 | 631.7148 | 616.2979 | 606.1518 | NaN | NaN | NaN | 682.6246 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 3.2432 | NaN | 15.0721
11472.1292 | 726.3994 | 635.8949 | 492.2241 | 467.5961 | 474.1792 | 627.8787 | 615.4243 | 609.1763 | NaN | NaN | NaN | 658.5837 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.83 | NaN | 20.1779
11473.1292 | 728.6003 | 636.1686 | 492.1603 | 467.6734 | 474.2818 | 628.2375 | 614.7343 | 609.2888 | NaN | NaN | NaN | 660.2542 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.6024 | NaN | 20.8867
11474.1292 | 730.1665 | 636.9505 | 491.9572 | 467.6344 | 474.8861 | 629.2216 | 618.0152 | 613.3151 | NaN | NaN | NaN | 682.8522 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -18.5177 | NaN | 26.1435
11475.1292 | 732.1386 | 636.9222 | 491.6985 | 467.6127 | 475.1711 | 629.6196 | 622.7775 | 613.4726 | NaN | NaN | NaN | 686.0594 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.5531 | NaN | 17.3134
11476.1292 | 733.2467 | 636.8978 | 491.5302 | 467.3767 | 475.0229 | 632.2856 | 623.2312 | 616.0075 | NaN | NaN | NaN | 670.951 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.466 | NaN | 19.629
11477.1292 | 732.2244 | 637.497 | 491.5577 | 467.2604 | 475.1113 | 635.5604 | 628.1861 | 610.6574 | NaN | NaN | NaN | 671.5068 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.8866 | NaN | 18.8533
11478.1292 | 729.1843 | 637.609 | 491.9383 | 467.2963 | 474.9637 | 634.8327 | 628.6885 | 606.7136 | NaN | NaN | NaN | 671.087 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 14.0304 | NaN | 24.8369
11479.1292 | 726.2715 | 637.2417 | 492.1339 | 467.0697 | 474.2603 | 632.9587 | 625.1645 | 608.0166 | NaN | NaN | NaN | 652.6794 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.6888 | NaN | 23.969
11480.1292 | 725.3028 | 636.908 | 492.3551 | 466.8643 | 474.3028 | 630.346 | 623.2355 | 606.0033 | NaN | NaN | NaN | 662.2497 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 35.0014 | NaN | 21.7921
11481.1292 | 724.0046 | 636.767 | 492.2424 | 466.6812 | 473.8055 | 626.8917 | 622.5108 | 605.0713 | NaN | NaN | NaN | 678.3761 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.9602 | NaN | 21.6497
11482.1292 | 725.2155 | 636.4032 | 492.1506 | 466.9569 | 473.6879 | 629.4175 | 620.4141 | 608.0793 | NaN | NaN | NaN | 708.9715 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.5782 | NaN | 23.3895
11483.1292 | 727.6737 | 636.8233 | 491.8804 | 467.2004 | 473.5792 | 634.5328 | 620.092 | 611.1344 | NaN | NaN | NaN | 718.7736 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.1285 | NaN | 22.8031
11484.1292 | 731.2193 | 636.6487 | 491.9097 | 467.5558 | 473.6444 | 630.0139 | 619.9467 | 623.0826 | NaN | NaN | NaN | 686.3403 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.6328 | NaN | 19.496
11485.1292 | 733.2948 | 636.8228 | 491.8897 | 467.6927 | 473.8 | 626.3327 | 617.069 | 614.6506 | NaN | NaN | NaN | 692.9938 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.2592 | NaN | 22.2929
11486.1292 | 734.4976 | 636.7288 | 491.919 | 467.6249 | 473.7555 | 624.0915 | 616.9614 | 608.5158 | NaN | NaN | NaN | 695.3248 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.313 | NaN | 21.2223
11487.1292 | 737.0805 | 636.8982 | 492.1549 | 467.6265 | 473.6192 | 621.3222 | 616.8513 | 611.5289 | NaN | NaN | NaN | 707.4163 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.4016 | NaN | 22.0006
11488.1292 | 737.1525 | 636.6833 | 492.3065 | 468.0773 | 473.9963 | 625.5658 | 617.1698 | 613.5218 | NaN | NaN | NaN | 707.8491 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.4466 | NaN | 19.9477
11489.1292 | 736.7137 | 637.1071 | 492.4545 | 468.3817 | 474.4252 | 631.09 | 616.7222 | 609.5697 | NaN | NaN | NaN | 681.4475 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.2245 | NaN | 20.2878
11490.1292 | 736.1759 | 637.1823 | 492.3372 | 468.3157 | 474.5741 | 626.0263 | 614.7673 | 602.66 | NaN | NaN | NaN | 679.6854 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.0931 | NaN | 21.0751
11491.1292 | 734.1431 | 636.9748 | 492.329 | 468.08 | 474.3311 | 624.5626 | 614.7065 | 598.8682 | NaN | NaN | NaN | 682.8865 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.5481 | NaN | 21.3793
11492.1292 | 733.0055 | 637.2434 | 492.5164 | 467.843 | 474.4095 | 623.2442 | 615.6462 | 603.0369 | NaN | NaN | NaN | 667.0043 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.6363 | NaN | 21.1856
11493.1292 | 735.7938 | 637.5012 | 492.7132 | 468.0075 | 474.2882 | 621.1948 | 617.7687 | 602.6346 | NaN | NaN | NaN | 669.3842 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.8341 | NaN | 19.992
11494.1292 | 736.8686 | 637.521 | 493.0158 | 468.0564 | 474.094 | 618.2792 | 616.5423 | 603.2548 | NaN | NaN | NaN | 671.8725 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.7026 | NaN | 20.4875
11495.1292 | 736.0131 | 637.6306 | 493.3884 | 467.9998 | 474.3355 | 617.1457 | 614.9918 | 597.6836 | NaN | NaN | NaN | 694.8575 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.8542 | NaN | 19.7165
11496.1292 | 736.2854 | 638.7897 | 493.5869 | 468.7254 | 474.3467 | 616.4494 | 614.1483 | 593.2995 | NaN | NaN | NaN | 715.2364 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.7557 | NaN | 16.443
11497.1292 | 739.6193 | 638.8614 | 494.2468 | 469.0674 | 474.3693 | 621.7666 | 615.1603 | 604.0034 | NaN | NaN | NaN | 716.9337 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.0664 | NaN | 19.8264
11498.1292 | 740.7817 | 638.5435 | 494.1462 | 469.0372 | 474.2596 | 620.7661 | 613.4876 | 597.4966 | NaN | NaN | NaN | 685.0556 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.687 | NaN | 19.5683
11499.1292 | 739.7404 | 638.5568 | 493.9427 | 469.0235 | 474.17 | 624.0749 | 612.3918 | 593.225 | NaN | NaN | NaN | 681.4129 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.6622 | NaN | 19.6891
11500.1292 | 738.8052 | 638.6923 | 493.989 | 468.8427 | 474.1127 | 622.9621 | 610.1911 | 590.0771 | NaN | NaN | NaN | 655.0271 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.0976 | NaN | 18.9249
11501.1292 | 740.9132 | 639.221 | 494.2505 | 469.3485 | 474.0716 | 620.3706 | 612.2008 | 596.6299 | NaN | NaN | NaN | 644.4197 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.7731 | NaN | 20.6185
11502.1292 | 742.5324 | 640.5581 | 494.5277 | 469.5216 | 474.3961 | 622.6031 | 617.3483 | 602.465 | NaN | NaN | NaN | 621.9634 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.2037 | NaN | 21.2565
11503.1292 | 740.8076 | 640.1815 | 494.7528 | 469.6983 | 474.7783 | 620.9145 | 618.0234 | 601.1906 | NaN | NaN | NaN | 633.5702 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.113 | NaN | 20.2882
11504.1292 | 741.6905 | 639.5972 | 495.2843 | 469.869 | 475.4076 | 615.8465 | 616.3934 | 601.9176 | NaN | NaN | NaN | 662.1984 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.5168 | NaN | 19.4907
11505.1448 | 741.1837 | 637.9606 | 495.1546 | 469.9688 | 475.7443 | 626.3127 | 619.1102 | 606.2891 | NaN | NaN | NaN | 681.2793 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.7891 | NaN | 17.89
11506.1292 | 739.6868 | 639.3376 | 495.1383 | 470.2267 | 476.0889 | 632.1615 | 622.076 | 610.1272 | NaN | NaN | NaN | 702.3924 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.5458 | NaN | 22.2306
11507.1292 | 739.2702 | 638.2325 | 494.9807 | 470.6572 | 476.2191 | 632.4898 | 621.7633 | 607.984 | NaN | NaN | NaN | 714.842 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.4774 | NaN | 20.0849
11508.1292 | 739.2462 | 638.3129 | 494.7162 | 470.4914 | 476.2078 | 637.1027 | 620.979 | 604.0611 | NaN | NaN | NaN | 701.6099 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.9128 | NaN | 22.5013
11509.1292 | 737.7383 | 638.5809 | 494.223 | 470.1104 | 476.0956 | 642.8225 | 622.1859 | 602.8358 | NaN | NaN | NaN | 683.2987 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.9503 | NaN | 22.5786
11510.1292 | 733.015 | 637.6943 | 494.1838 | 469.7737 | 476.0323 | 648.3134 | 621.8332 | 595.8754 | NaN | NaN | NaN | 692.9598 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.4015 | NaN | 22.6988
11511.1292 | 730.4441 | 636.0915 | 494.0924 | 469.4536 | 475.8859 | 647.6774 | 616.355 | 590.4113 | NaN | NaN | NaN | 698.2369 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.9798 | NaN | 19.9591
11512.1292 | 729.5352 | 635.4495 | 493.9321 | 469.447 | 475.728 | 646.1846 | 613.5221 | 587.581 | NaN | NaN | NaN | 697.8842 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.9371 | NaN | 19.7391
11513.1292 | 729.1876 | 635.7658 | 493.8104 | 469.0476 | 475.4766 | 639.3957 | 612.8133 | 584.4544 | NaN | NaN | NaN | 712.6012 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.0163 | NaN | 21.7934
11514.1292 | 729.443 | 635.0916 | 493.7139 | 468.8738 | 474.9155 | 634.1541 | 610.653 | 581.9311 | NaN | NaN | NaN | 713.0903 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.5464 | NaN | 21.674
11515.1292 | 731.1448 | 635.4411 | 493.6716 | 468.4375 | 474.4352 | 643.5846 | 610.4057 | 579.0987 | NaN | NaN | NaN | 725.2184 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.3649 | NaN | 20.5871
11516.1292 | 733.5791 | 636.0799 | 493.3924 | 468.1085 | 473.8137 | 636.7644 | 610.3426 | 575.6636 | NaN | NaN | NaN | 700.4365 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.3678 | NaN | 20.5038
11517.1292 | 735.8526 | 636.7297 | 493.4599 | 468.0612 | 473.8693 | 631.9399 | 610.395 | 574.1711 | NaN | NaN | NaN | 688.0582 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.9917 | NaN | 20.9466
11518.1292 | 735.6949 | 636.9075 | 493.6275 | 468.0937 | 474.0221 | 633.2454 | 610.956 | 586.4165 | NaN | NaN | NaN | 709.3839 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.9739 | NaN | 19.305
11519.1292 | 734.408 | 637.6378 | 493.8344 | 468.2016 | 474.0454 | 631.137 | 611.1959 | 588.0985 | NaN | NaN | NaN | 719.7575 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.1226 | NaN | 20.2069
11520.1292 | 733.333 | 637.4214 | 493.895 | 468.2072 | 473.9556 | 627.0786 | 609.2417 | 590.3692 | NaN | NaN | NaN | 728.4743 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.4205 | NaN | 21.3437
11521.1292 | 732.3384 | 636.8915 | 493.8546 | 468.0831 | 473.7771 | 624.6812 | 607.0866 | 590.6836 | NaN | NaN | NaN | 713.4634 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.7811 | NaN | 21.5918
11522.1448 | 732.337 | 636.7951 | 494.082 | 467.8613 | 473.16 | 620.9254 | 606.3763 | 592.3956 | NaN | NaN | NaN | 695.2877 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.8355 | NaN | 20.7796
11523.1292 | 731.7734 | 637.2287 | 494.0604 | 467.7402 | 472.5324 | 627.3589 | 609.7619 | 591.118 | NaN | NaN | NaN | 699.5365 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.5921 | NaN | 21.2348
11524.1292 | 729.685 | 636.9154 | 493.7957 | 467.656 | 472.7629 | 632.9938 | 610.0097 | 593.3501 | NaN | NaN | NaN | 707.0806 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.8822 | NaN | 19.8817
11525.1292 | 728.0011 | 636.5522 | 493.8047 | 467.736 | 472.5191 | 632.5555 | 613.3991 | 589.412 | NaN | NaN | NaN | 729.8184 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.7013 | NaN | 18.8112
11526.1292 | 727.2119 | 636.3625 | 493.5583 | 467.4036 | 472.4671 | 633.3676 | 611.2978 | 592.0706 | NaN | NaN | NaN | 738.3183 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.4461 | NaN | 21.1705
11527.1292 | 727.1056 | 636.5351 | 493.272 | 467.3972 | 472.4587 | 633.9824 | 609.8086 | 594.4535 | NaN | NaN | NaN | 755.6088 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.448 | NaN | 21.0616
11528.1292 | 728.6378 | 636.0746 | 493.2982 | 467.3321 | 472.3035 | 629.194 | 608.273 | 602.2107 | NaN | NaN | NaN | 743.8163 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.6396 | NaN | 21.7985
11529.1292 | 730.5117 | 636.1568 | 493.1247 | 467.4417 | 472.4058 | 632.8219 | 607.5766 | 606.6408 | NaN | NaN | NaN | 728.9006 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.388 | NaN | 18.9034
11530.1292 | 731.9527 | 636.4017 | 493.1575 | 467.6136 | 472.8179 | 631.3118 | 606.9991 | 603.9251 | NaN | NaN | NaN | 724.6592 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.6997 | NaN | 20.3825
11531.1292 | 731.7112 | 636.9059 | 493.2632 | 467.7607 | 473.064 | 638.3015 | 607.3745 | 601.1617 | NaN | NaN | NaN | 737.9512 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.0913 | NaN | 18.1205
11532.1292 | 731.2516 | 637.1545 | 493.0903 | 467.5248 | 473.2072 | 640.0861 | 606.0152 | 596.2874 | NaN | NaN | NaN | 735.8439 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.1219 | NaN | 20.7594
11533.1292 | 730.7673 | 637.1844 | 493.2047 | 467.7257 | 473.1396 | 636.822 | 608.516 | 597.4623 | NaN | NaN | NaN | 748.8897 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.3014 | NaN | 20.2891
11534.1292 | 728.8509 | 636.8033 | 493.2212 | 467.92 | 473.0856 | 639.2189 | 609.5936 | 600.4052 | NaN | NaN | NaN | 766.5938 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.6719 | NaN | 20.0262
11535.1292 | 727.184 | 636.8985 | 493.2903 | 468.0458 | 472.6616 | 646.4061 | 611.096 | 603.2012 | NaN | NaN | NaN | 762.5041 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.6367 | NaN | 20.9795
11536.1292 | 727.14 | 637.1505 | 493.2959 | 468.1468 | 472.4503 | 641.0574 | 611.8861 | 599.1399 | NaN | NaN | NaN | 762.4818 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.5161 | NaN | 22.022
11537.1292 | 727.2998 | 636.9387 | 493.3824 | 468.1169 | 472.6105 | 636.069 | 614.9946 | 597.3555 | NaN | NaN | NaN | 769.02 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.621 | NaN | 20.1181
11538.1292 | 728.3489 | 637.9638 | 493.5051 | 468.442 | 473.1851 | 638.6385 | 617.0891 | 594.4658 | NaN | NaN | NaN | 762.8524 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.9863 | NaN | 21.1132
11539.1292 | 729.46 | 638.3223 | 493.8619 | 469.1013 | 473.9433 | 638.6833 | 614.0105 | 591.9812 | NaN | NaN | NaN | 750.2619 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.6175 | NaN | 20.9482
11540.1292 | 727.8262 | 637.3682 | 494.2318 | 469.5874 | 473.7342 | 633.2902 | 611.4826 | 597.3574 | NaN | NaN | NaN | 756.0545 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.0133 | NaN | 20.8066
11541.1292 | 728.4621 | 636.7404 | 494.6518 | 469.6463 | 473.7242 | 627.1113 | 608.8472 | 598.5906 | NaN | NaN | NaN | 734.0335 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.076 | NaN | 20.484
11542.1292 | 731.4513 | 636.5004 | 494.7122 | 469.6353 | 473.5264 | 622.2949 | 607.9951 | 606.8591 | NaN | NaN | NaN | 747.6738 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.4683 | NaN | 20.6609
11543.1292 | 734.8497 | 636.9979 | 494.6673 | 470.065 | 473.2518 | 619.9965 | 607.2319 | 606.6054 | NaN | NaN | NaN | 760.5367 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.1982 | NaN | 17.7701
11544.1292 | 738.329 | 637.2754 | 494.6866 | 470.4882 | 473.6909 | 623.0687 | 607.317 | 601.7354 | NaN | NaN | NaN | 757.3191 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.6808 | NaN | 18.9552
11545.1292 | 740.5323 | 639.4518 | 494.5405 | 471.1367 | 474.0396 | 620.9544 | 610.8489 | 598.7527 | NaN | NaN | NaN | 756.6484 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.1776 | NaN | 19.6346
11546.1292 | 741.9296 | 639.8842 | 494.5219 | 471.6334 | 474.5437 | 617.1206 | 609.5984 | 594.8405 | NaN | NaN | NaN | 764.8705 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.2413 | NaN | 19.3344
11547.1292 | 743.68 | 640.4486 | 494.4619 | 471.6177 | 474.7368 | 617.6006 | 609.7176 | 589.7397 | NaN | NaN | NaN | 757.5127 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.1522 | NaN | 21.9251
11548.1292 | 747.2946 | 640.4681 | 494.5789 | 471.6513 | 474.6986 | 618.1606 | 607.7885 | 591.0779 | NaN | NaN | NaN | 714.1733 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.1884 | NaN | 18.972
11549.1292 | 746.9328 | 639.9164 | 494.8191 | 471.23 | 474.4006 | 618.5586 | 607.3505 | 587.6458 | NaN | NaN | NaN | 730.7663 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.0337 | NaN | 19.4476
11550.1292 | 745.6406 | 640.41 | 495.2229 | 471.1288 | 474.2936 | 616.9451 | 607.6052 | 589.258 | NaN | NaN | NaN | 721.6427 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.8735 | NaN | 21.8242
11551.1292 | 742.9067 | 639.7802 | 495.3262 | 470.9063 | 474.2533 | 615.6971 | 605.9041 | 586.0562 | NaN | NaN | NaN | 712.8247 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.755 | NaN | 19.9034
11552.1292 | 742.4414 | 638.9881 | 495.5468 | 470.9045 | 474.4543 | 612.2364 | 603.7645 | 583.7114 | NaN | NaN | NaN | 701.1398 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.9544 | NaN | 19.9923
11553.1292 | 742.3718 | 639.0657 | 495.9349 | 470.7571 | 474.3877 | 610.9821 | 603.5479 | 588.0267 | NaN | NaN | NaN | 691.1669 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.1263 | NaN | 20.3115
11554.1292 | 742.8984 | 638.8654 | 496.0968 | 470.5665 | 474.0355 | 609.6162 | 603.535 | 585.8587 | NaN | NaN | NaN | 699.5118 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.6396 | NaN | 19.592
11555.1292 | 741.4595 | 638.0954 | 496.0346 | 470.1036 | 473.6163 | 610.4932 | 603.9303 | 588.2618 | NaN | NaN | NaN | 722.8542 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.7142 | NaN | 21.0569
11556.1292 | 738.6984 | 638.3224 | 495.7955 | 470.0279 | 473.2014 | 611.2092 | 604.8929 | 588.548 | NaN | NaN | NaN | 725.155 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.8929 | NaN | 19.8582
11557.1292 | 737.4086 | 637.6302 | 495.6013 | 469.9181 | 473.2535 | 609.9545 | 604.1797 | 589.0102 | NaN | NaN | NaN | 744.2582 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.3825 | NaN | 16.6582
11558.1292 | 736.4108 | 636.6568 | 495.6105 | 469.6532 | 473.1861 | 616.91 | 602.7008 | 586.0115 | NaN | NaN | NaN | 765.3413 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.6187 | NaN | 18.8769
11559.1292 | 737.0631 | 636.3464 | 495.4119 | 469.4971 | 473.1266 | 614.2335 | 601.382 | 584.6926 | NaN | NaN | NaN | 761.3951 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.758 | NaN | 18.5011
11560.1292 | 736.732 | 636.7055 | 494.8682 | 469.2131 | 473.2035 | 615.9136 | 601.5732 | 582.4207 | NaN | NaN | NaN | 760.0041 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.3151 | NaN | 19.4526
11561.1292 | 735.8512 | 637.2106 | 494.6712 | 468.7482 | 473.3337 | 619.942 | 603.3971 | 584.8658 | NaN | NaN | NaN | 729.8256 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.3296 | NaN | 21.1039
11562.1292 | 735.7562 | 637.6717 | 495.0262 | 468.6694 | 473.0757 | 619.7833 | 605.1251 | 584.8457 | NaN | NaN | NaN | 691.1713 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.0098 | NaN | 21.6892
11563.1292 | 735.8131 | 637.9791 | 495.7177 | 468.5287 | 472.9323 | 626.3589 | 606.2462 | 583.8554 | NaN | NaN | NaN | 695.7024 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.1302 | NaN | 21.8049
11564.1292 | 737.604 | 637.1772 | 495.7214 | 468.3369 | 472.944 | 637.137 | 606.889 | 583.7903 | NaN | NaN | NaN | 664.2543 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.9124 | NaN | 21.9982
11565.1292 | 738.8156 | 637.9045 | 495.7433 | 468.1349 | 472.9533 | 640.0372 | 610.3421 | 583.8035 | NaN | NaN | NaN | 640.407 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.9548 | NaN | 19.8225
11566.1292 | 736.644 | 638.4181 | 495.6799 | 468.0596 | 473.3991 | 645.2379 | 612.378 | 583.8386 | NaN | NaN | NaN | 652.0468 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.8263 | NaN | 21.4649
11567.1292 | 735.2535 | 638.1854 | 495.6239 | 468.1197 | 473.2955 | 639.9985 | 613.0696 | 584.0069 | NaN | NaN | NaN | 644.9262 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.765 | NaN | 19.3987
11568.1292 | 733.1148 | 636.8205 | 495.5523 | 468.0384 | 473.2225 | 638.7013 | 611.5774 | 582.7295 | NaN | NaN | NaN | 663.6356 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.8649 | NaN | 18.5484
11569.1292 | 731.173 | 636.4374 | 495.2226 | 467.8303 | 473.1908 | 649.4888 | 612.7924 | 581.2622 | NaN | NaN | NaN | 660.623 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.2569 | NaN | 20.5856
11570.1292 | 730.4824 | 637.3501 | 494.9209 | 467.7775 | 473.3457 | 657.4329 | 616.4678 | 582.3321 | NaN | NaN | NaN | 648.2207 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.6033 | NaN | 18.2471
11571.1292 | 729.377 | 638.2769 | 494.9607 | 468.0839 | 473.3661 | 662.5719 | 618.6998 | 582.8893 | NaN | NaN | NaN | 678.8461 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.3269 | NaN | 21.0661
11572.1292 | 728.6643 | 638.2593 | 495.0694 | 468.3183 | 474.0641 | 665.8221 | 616.5577 | 579.8436 | NaN | NaN | NaN | 693.3857 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.4474 | NaN | 20.6693
11573.1292 | 727.8909 | 637.4976 | 495.3006 | 468.2048 | 474.2485 | 663.9828 | 618.0521 | 578.6534 | NaN | NaN | NaN | 710.3323 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.4635 | NaN | 20.3979
11574.1292 | 728.3676 | 636.8851 | 495.2678 | 468.0372 | 474.1835 | 657.0837 | 617.3355 | 582.8645 | NaN | NaN | NaN | 728.4878 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.3599 | NaN | 21.3003
11575.1292 | 730.9216 | 637.6153 | 495.3156 | 467.7859 | 474.0282 | 647.7096 | 614.802 | 585.284 | NaN | NaN | NaN | 742.9407 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.7024 | NaN | 21.2658
11576.1292 | 733.0201 | 637.4 | 495.4402 | 467.8171 | 473.8443 | 643.2731 | 614.0287 | 582.9321 | NaN | NaN | NaN | 715.9143 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.1801 | NaN | 19.1629
11577.1292 | 734.1061 | 637.2918 | 495.5616 | 468.0237 | 473.6984 | 637.5318 | 612.285 | 588.6758 | NaN | NaN | NaN | 693.896 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.4112 | NaN | 18.8938
11578.1292 | 735.2614 | 637.5222 | 495.4756 | 467.97 | 473.5163 | 634.7376 | 611.4383 | 590.1746 | NaN | NaN | NaN | 694.8289 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.4688 | NaN | 23.1628
11579.1292 | 734.9605 | 637.497 | 495.6507 | 467.9506 | 473.4389 | 644.9499 | 611.5005 | 587.9529 | NaN | NaN | NaN | 690.5846 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.7712 | NaN | 21.3278
11580.1292 | 733.9688 | 637.3484 | 495.5606 | 468.0321 | 473.5355 | 648.6652 | 610.4578 | 584.5839 | NaN | NaN | NaN | 703.9975 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.7205 | NaN | 20.1827
11581.1292 | 733.6581 | 637.0327 | 495.0784 | 467.867 | 473.7408 | 650.3382 | 610.7059 | 581.5353 | NaN | NaN | NaN | 699.0711 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.0051 | NaN | 19.2266
11582.1292 | 734.3014 | 636.7564 | 494.8763 | 468.0755 | 473.874 | 646.6009 | 610.2764 | 582.0125 | NaN | NaN | NaN | 710.8296 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.1201 | NaN | 21.5369
11583.1292 | 734.5445 | 637.534 | 494.8595 | 468.2238 | 473.9802 | 647.3611 | 614.9002 | 579.4825 | NaN | NaN | NaN | 706.088 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.8246 | NaN | 19.1732
11584.1292 | 735.598 | 638.1571 | 494.8152 | 468.2021 | 474.0229 | 645.1233 | 614.6089 | 584.3743 | NaN | NaN | NaN | 731.3298 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 13.569 | NaN | 21.6843
11585.1292 | 738.2332 | 638.1074 | 494.7472 | 468.0401 | 474.1092 | 640.487 | 613.8173 | 582.6717 | NaN | NaN | NaN | 742.879 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.4292 | NaN | 19.3595
11586.1292 | 741.009 | 637.7899 | 494.8848 | 468.1357 | 474.165 | 637.7368 | 616.3147 | 588.7105 | NaN | NaN | NaN | 747.677 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.2349 | NaN | 21.0492
11587.1292 | 743.603 | 638.3115 | 495.1313 | 468.1317 | 473.9873 | 640.2575 | 614.7534 | 585.9734 | NaN | NaN | NaN | 738.2138 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.5284 | NaN | 20.7072
11588.1292 | 745.0567 | 639.1331 | 494.8938 | 468.1653 | 473.9802 | 641.3222 | 616.27 | 584.018 | NaN | NaN | NaN | 738.7541 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.1559 | NaN | 22.0019
11589.1292 | 742.2541 | 639.0131 | 494.5891 | 468.2003 | 474.2917 | 643.469 | 617.6043 | 583.3376 | NaN | NaN | NaN | 697.9751 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.2748 | NaN | 21.6919
11590.1292 | 738.7286 | 639.0774 | 494.8768 | 468.6213 | 474.8302 | 650.8895 | 617.1964 | 581.681 | NaN | NaN | NaN | 697.7345 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.9416 | NaN | 21.3598
11591.1292 | 736.2751 | 638.0351 | 495.1127 | 469.0888 | 475.0909 | 655.6699 | 614.9506 | 581.5094 | NaN | NaN | NaN | 694.4168 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.921 | NaN | 19.1484
11592.1292 | 733.8656 | 638.0594 | 495.4075 | 469.36 | 475.0125 | 652.2325 | 620.358 | 584.6405 | NaN | NaN | NaN | 662.0726 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.4858 | NaN | 19.679
11593.1292 | 732.8144 | 637.9146 | 495.2826 | 469.1666 | 474.9562 | 656.9667 | 620.7666 | 597.2821 | NaN | NaN | NaN | 689.5107 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.253 | NaN | 19.6289
11594.1292 | 731.8285 | 637.9357 | 495.5728 | 469.357 | 474.7165 | 663.9546 | 618.1506 | 593.5801 | NaN | NaN | NaN | 701.4617 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.7506 | NaN | 19.3715
11595.1292 | 731.5342 | 637.2729 | 496.0192 | 469.9135 | 474.3959 | 660.0611 | 617.0225 | 589.1776 | NaN | NaN | NaN | 701.7421 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.3348 | NaN | 16.6381
11596.1292 | 731.689 | 637.1491 | 495.7785 | 469.6287 | 474.1811 | 656.1931 | 616.1165 | 590.8416 | NaN | NaN | NaN | 676.4595 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.9227 | NaN | 20.9339
11597.1292 | 731.8149 | 637.4699 | 495.6146 | 469.5635 | 473.7635 | 652.0442 | 616.0333 | 589.4953 | NaN | NaN | NaN | 659.5089 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.9127 | NaN | 19.2077
11598.1292 | 731.1449 | 638.3222 | 495.8305 | 469.7067 | 473.4673 | 649.8732 | 617.7353 | 588.2476 | NaN | NaN | NaN | 679.3474 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.7618 | NaN | 18.7843
11599.1292 | 730.8242 | 638.1554 | 495.8622 | 470.1466 | 473.6494 | 648.9848 | 616.6883 | 587.7639 | NaN | NaN | NaN | 712.2396 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.5031 | NaN | 23.539
11600.1292 | 729.2859 | 638.1189 | 496.2058 | 470.3331 | 473.8016 | 649.0055 | 616.6875 | 583.6192 | NaN | NaN | NaN | 730.7007 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.4703 | NaN | 20.7274
11601.1292 | 728.1137 | 637.9091 | 496.4435 | 470.8411 | 473.7833 | 645.1366 | 615.5476 | 585.6798 | NaN | NaN | NaN | 716.1998 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.6072 | NaN | 18.6606
11602.1292 | 726.2119 | 636.9682 | 496.7732 | 470.9671 | 473.4133 | 640.9647 | 615.0703 | 588.3548 | NaN | NaN | NaN | 706.6657 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.7738 | NaN | 19.4176
11603.1448 | 723.6458 | 636.7749 | 497.0285 | 471.3774 | 473.2352 | 640.415 | 611.6038 | 587.5079 | NaN | NaN | NaN | 733.3825 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.6233 | NaN | 19.3268
11604.1292 | 723.2063 | 636.5994 | 496.7554 | 471.3611 | 473.1282 | 640.0136 | 611.8307 | 586.8676 | NaN | NaN | NaN | 750.2628 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.3514 | NaN | 19.4951
11605.1292 | 722.6741 | 636.6073 | 496.3866 | 470.9829 | 472.9711 | 635.3857 | 610.6102 | 590.6442 | NaN | NaN | NaN | 779.2666 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.6696 | NaN | 19.9941
11606.1292 | 723.9846 | 635.8857 | 496.0608 | 470.7023 | 472.79 | 630.5416 | 608.2175 | 593.3874 | NaN | NaN | NaN | 786.1387 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.2713 | NaN | 21.6538
11607.1292 | 727.6284 | 635.8787 | 495.9921 | 470.6192 | 472.9465 | 626.1682 | 607.3241 | 593.3833 | NaN | NaN | NaN | 797.153 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.7649 | NaN | 18.7468
11608.1292 | 729.8981 | 635.884 | 495.9436 | 470.1594 | 473.1529 | 622.2843 | 607.6791 | 592.6697 | NaN | NaN | NaN | 798.9646 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.787 | NaN | 19.5836
11609.1292 | 730.287 | 636.1657 | 495.7844 | 470.2424 | 473.4577 | 624.3099 | 609.9251 | 589.0776 | NaN | NaN | NaN | 780.7669 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.3031 | NaN | 18.1816
11610.1292 | 731.8583 | 636.3351 | 495.7723 | 469.7327 | 473.3699 | 624.5142 | 609.2802 | 585.7918 | NaN | NaN | NaN | 746.83 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.2903 | NaN | 21.1784
11611.1292 | 730.9526 | 636.0674 | 495.44 | 469.711 | 473.3443 | 626.1787 | 609.3242 | 582.4689 | NaN | NaN | NaN | 718.116 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.6543 | NaN | 20.2969
11612.1292 | 730.1742 | 635.5867 | 495.4417 | 469.4478 | 472.8112 | 634.8948 | 607.8871 | 579.3273 | NaN | NaN | NaN | 716.7586 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.4478 | NaN | 18.6674
11613.1292 | 730.833 | 635.3333 | 495.4647 | 469.7079 | 472.8371 | 645.3594 | 605.3765 | 577.2325 | NaN | NaN | NaN | 726.346 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.7137 | NaN | 21.5673
11614.1292 | 733.7021 | 635.6435 | 495.2122 | 469.5194 | 472.4207 | 642.0597 | 606.142 | 577.0262 | NaN | NaN | NaN | 708.5667 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.4864 | NaN | 20.3777
11615.1292 | 733.553 | 636.3992 | 494.8322 | 469.3976 | 472.5119 | 645.0127 | 610.2654 | 586.5283 | NaN | NaN | NaN | 740.2194 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.82 | NaN | 20.2565
11616.1292 | 732.5873 | 636.2797 | 494.8908 | 469.3363 | 472.5223 | 645.8757 | 610.8294 | 582.9936 | NaN | NaN | NaN | 763.2517 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.968 | NaN | 21.2303
11617.1292 | 729.9142 | 635.9595 | 495.02 | 469.3386 | 472.8216 | 651.4727 | 608.9325 | 578.2992 | NaN | NaN | NaN | 781.0158 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.5441 | NaN | 20.0065
11618.1292 | 728.5684 | 635.3308 | 494.7932 | 469.2375 | 472.9134 | 644.8526 | 610.2036 | 574.8322 | NaN | NaN | NaN | 742.9405 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.4327 | NaN | 17.0002
11619.1292 | 728.6938 | 635.1906 | 494.5475 | 469.1826 | 472.94 | 638.3846 | 608.7159 | 578.7777 | NaN | NaN | NaN | 723.9798 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.6449 | NaN | 19.2709
11620.1292 | 729.1964 | 635.7885 | 494.2412 | 469.4568 | 472.5386 | 637.9744 | 610.2569 | 588.4342 | NaN | NaN | NaN | 682.7494 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.5907 | NaN | 19.426
11621.1292 | 729.5264 | 636.0267 | 494.6996 | 469.4644 | 472.3809 | 640.4399 | 610.048 | 586.2489 | NaN | NaN | NaN | 663.4625 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.2618 | NaN | 22.2163
11622.1292 | 729.214 | 636.6771 | 494.6076 | 469.3946 | 472.3255 | 650.8397 | 611.8224 | 586.2158 | NaN | NaN | NaN | 672.5114 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.3753 | NaN | 20.6032
11623.1292 | 728.5523 | 636.8381 | 494.5082 | 469.4007 | 472.6917 | 654.8574 | 612.0433 | 583.3265 | NaN | NaN | NaN | 684.5178 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.4786 | NaN | 18.8108
11624.1292 | 725.9833 | 637.2591 | 494.3979 | 469.5201 | 472.8624 | 659.8716 | 614.2194 | 584.9174 | NaN | NaN | NaN | 681.7807 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.3459 | NaN | 21.4781
11625.1292 | 724.2803 | 637.0236 | 494.3842 | 469.5544 | 473.0964 | 659.6036 | 617.988 | 585.0658 | NaN | NaN | NaN | 681.9697 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.6455 | NaN | 20.065
11626.1292 | 722.4606 | 636.9067 | 494.6268 | 469.7402 | 473.2326 | 659.0059 | 616.9066 | 582.606 | NaN | NaN | NaN | 677.1395 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.2875 | NaN | 18.6704
11627.1292 | 720.7154 | 637.8737 | 494.8304 | 470.142 | 473.1562 | 664.4083 | 616.5556 | 583.2716 | NaN | NaN | NaN | 667.0946 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.8156 | NaN | 19.7182
11628.1292 | 718.661 | 637.6481 | 494.9473 | 470.049 | 473.1212 | 662.3833 | 617.8419 | 581.4693 | NaN | NaN | NaN | 690.9401 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.8738 | NaN | 20.4755
11629.1292 | 715.736 | 636.1823 | 495.0769 | 470.1954 | 473.0164 | 658.8307 | 615.8624 | 579.6136 | NaN | NaN | NaN | 679.6261 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.7373 | NaN | 19.5989
11630.1292 | 714.4262 | 635.9259 | 495.2442 | 470.6368 | 472.7275 | 656.9367 | 615.2605 | 579.8096 | NaN | NaN | NaN | 698.1415 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.4724 | NaN | 18.0108
11631.1292 | 715.8346 | 635.9764 | 495.2955 | 470.1734 | 473.088 | 658.1081 | 613.4483 | 583.0526 | NaN | NaN | NaN | 679.7057 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.0258 | NaN | 20.4008
11632.1292 | 718.6049 | 636.1385 | 495.7293 | 469.8034 | 472.902 | 651.8485 | 612.6636 | 583.5994 | NaN | NaN | NaN | 711.1216 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.242 | NaN | 18.6542
11633.1292 | 719.7562 | 635.9592 | 495.6261 | 469.7607 | 472.5574 | 648.327 | 613.1894 | 581.767 | NaN | NaN | NaN | 746.8021 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.9842 | NaN | 20.7487
11634.1292 | 720.4976 | 636.0441 | 495.6613 | 469.7374 | 472.5694 | 644.3608 | 611.5624 | 580.7567 | NaN | NaN | NaN | 749.9899 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.9899 | NaN | 19.6348
11635.1292 | 721.9839 | 636.5795 | 495.6062 | 469.5676 | 472.9079 | 642.5179 | 610.9377 | 578.8996 | NaN | NaN | NaN | 734.9566 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.3132 | NaN | 20.2344
11636.1292 | 724.9206 | 636.8566 | 495.8612 | 469.6544 | 473.394 | 638.9304 | 609.4423 | 575.2075 | NaN | NaN | NaN | 701.1639 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.7296 | NaN | 19.8568
11637.1292 | 724.3866 | 636.6943 | 496.0146 | 469.5954 | 473.3208 | 633.9635 | 608.2495 | 572.6166 | NaN | NaN | NaN | 666.734 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.9119 | NaN | 19.2457
11638.1292 | 722.4363 | 636.3522 | 496.4386 | 469.614 | 473.1894 | 630.0679 | 604.9215 | 569.3345 | NaN | NaN | NaN | 663.0356 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.6915 | NaN | 18.5566
11639.1292 | 721.5091 | 635.1793 | 496.5848 | 469.7258 | 472.7837 | 626.8756 | 604.726 | 576.6974 | NaN | NaN | NaN | 665.9138 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.856 | NaN | 20.1688
11640.1292 | 722.4591 | 634.8033 | 496.8362 | 469.5558 | 472.2268 | 630.4778 | 605.3166 | 578.6814 | NaN | NaN | NaN | 689.1423 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.2621 | NaN | 20.1173
11641.1292 | 721.624 | 634.7453 | 496.8016 | 469.3182 | 471.5505 | 627.3376 | 602.7298 | 577.1582 | NaN | NaN | NaN | 698.1049 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.2439 | NaN | 22.1888
11642.1292 | 721.4862 | 634.4096 | 496.8942 | 469.2039 | 471.3547 | 625.5513 | 602.1026 | 575.1269 | NaN | NaN | NaN | 695.345 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.7673 | NaN | 20.0186
11643.1292 | 724.3588 | 635.3026 | 497.3032 | 469.3795 | 471.4351 | 625.8978 | 599.9787 | 578.1144 | NaN | NaN | NaN | 687.4984 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.9219 | NaN | 19.2085
11644.1292 | 729.8494 | 636.3722 | 497.8473 | 469.4806 | 471.7137 | 624.2498 | 601.9487 | 576.5984 | NaN | NaN | NaN | 700.1316 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.1221 | NaN | 20.2045
11645.1292 | 732.5965 | 636.3569 | 498.1064 | 469.6288 | 472.2477 | 621.9196 | 602.5486 | 575.6191 | NaN | NaN | NaN | 672.1782 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.0073 | NaN | 18.667
11646.1292 | 732.9363 | 636.0117 | 498.1471 | 469.5083 | 472.3045 | 618.4992 | 603.6913 | 574.2114 | NaN | NaN | NaN | 661.9117 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.6815 | NaN | 21.612
11647.1292 | 732.3016 | 635.8577 | 497.9944 | 469.4137 | 472.1554 | 631.0095 | 603.0788 | 574.4036 | NaN | NaN | NaN | 665.4956 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.7338 | NaN | 22.3964
11648.1292 | 732.7392 | 636.2922 | 497.7142 | 469.259 | 472.2206 | 643.0973 | 606.3202 | 575.3864 | NaN | NaN | NaN | 672.2729 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.2244 | NaN | 21.3748
11649.1292 | 733.1072 | 635.7232 | 497.4895 | 469.0489 | 472.1737 | 646.6017 | 609.4825 | 578.5042 | NaN | NaN | NaN | 666.3983 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.2144 | NaN | 20.6987
11650.1292 | 733.0248 | 635.6827 | 497.3586 | 469.1359 | 471.8826 | 649.2145 | 609.4429 | 577.0068 | NaN | NaN | NaN | 662.0207 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.6593 | NaN | 19.6731
11651.1292 | 732.3431 | 635.796 | 497.1567 | 468.7493 | 471.656 | 647.4812 | 607.5889 | 577.4098 | NaN | NaN | NaN | 675.193 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.4753 | NaN | 19.6192
11652.1292 | 730.5939 | 635.2596 | 496.8782 | 468.5064 | 471.6157 | 643.6575 | 606.6651 | 576.3528 | NaN | NaN | NaN | 664.3562 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.0616 | NaN | 19.6234
11653.1292 | 728.5467 | 635.0762 | 496.7608 | 468.344 | 471.9286 | 636.9669 | 604.536 | 572.9577 | NaN | NaN | NaN | 671.9138 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.6998 | NaN | 18.4518
11654.1292 | 727.0805 | 634.714 | 496.8488 | 468.2794 | 471.8728 | 636.3569 | 604.3492 | 571.9714 | NaN | NaN | NaN | 686.7773 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.4969 | NaN | 19.142
11655.1292 | 724.9798 | 633.7965 | 496.9732 | 468.1975 | 471.4864 | 631.8619 | 603.3648 | 570.6293 | NaN | NaN | NaN | 707.0234 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.9479 | NaN | 18.2324
11656.1292 | 726.1509 | 633.8778 | 496.8103 | 468.0764 | 471.1995 | 625.6982 | 600.9347 | 568.7575 | NaN | NaN | NaN | 690.0551 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.2018 | NaN | 18.9133
11657.1292 | 728.0886 | 634.0544 | 496.4918 | 468.0659 | 471.5853 | 620.9119 | 600.4194 | 569.3298 | NaN | NaN | NaN | 684.1181 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.6946 | NaN | 18.3782
11658.1292 | 728.6783 | 633.9776 | 496.4558 | 467.9097 | 471.6826 | 617.8721 | 599.9877 | 573.2485 | NaN | NaN | NaN | 710.628 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.7714 | NaN | 19.8524
11659.1292 | 728.8956 | 634.4645 | 496.5661 | 468.1786 | 471.3488 | 619.4617 | 600.3817 | 571.1676 | NaN | NaN | NaN | 697.7998 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.0251 | NaN | 18.7
11660.1292 | 728.0402 | 634.1721 | 496.675 | 468.2342 | 471.3645 | 624.1228 | 600.8407 | 571.3048 | NaN | NaN | NaN | 702.115 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.0429 | NaN | 20.2596
11661.1292 | 728.3371 | 633.996 | 496.9769 | 468.647 | 471.6969 | 621.277 | 600.4 | 576.1517 | NaN | NaN | NaN | 695.1411 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.4923 | NaN | 18.1596
11662.1292 | 730.9162 | 634.484 | 496.9391 | 468.8681 | 471.7206 | 616.4624 | 599.4702 | 574.0849 | NaN | NaN | NaN | 682.3309 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.5552 | NaN | 20.1528
11663.1292 | 732.2667 | 634.4126 | 496.9036 | 468.9669 | 471.7605 | 615.4826 | 597.9024 | 572.9911 | NaN | NaN | NaN | 680.7458 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.9815 | NaN | 20.2896
11664.1292 | 734.3637 | 634.5661 | 498.0189 | 469.1726 | 471.6436 | 614.0472 | 597.5778 | 576.8498 | NaN | NaN | NaN | 694.4394 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.0699 | NaN | 20.6162
11665.1292 | 734.8403 | 635.2361 | 497.9149 | 469.1593 | 471.418 | 611.5937 | 596.7266 | 586.8608 | NaN | NaN | NaN | 700.1554 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.2844 | NaN | 20.6301
11666.1292 | 736.7104 | 635.9168 | 498.1273 | 469.3575 | 471.4531 | 610.6149 | 597.1827 | 586.0318 | NaN | NaN | NaN | 676.0856 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.3817 | NaN | 21.1927
11667.1292 | 739.5677 | 637.9854 | 498.3444 | 469.8348 | 471.6621 | 612.2524 | 599.1646 | 582.0956 | NaN | NaN | NaN | 654.9761 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.7876 | NaN | 20.9904
11668.1292 | 741.9154 | 638.6647 | 498.819 | 470.2947 | 471.8347 | 615.8577 | 600.0694 | 587.7601 | NaN | NaN | NaN | 630.2122 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.4002 | NaN | 20.9375
11669.1292 | 742.6492 | 637.964 | 499.7081 | 470.6532 | 472.1142 | 616.9687 | 600.3544 | 583.9514 | NaN | NaN | NaN | 607.6249 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.615 | NaN | 20.8687
11670.1292 | 742.9056 | 637.3486 | 499.9815 | 470.8017 | 472.4405 | 620.5248 | 599.6266 | 585.2197 | NaN | NaN | NaN | 606.2097 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.0167 | NaN | 18.0751
11671.1292 | 741.959 | 637.0157 | 500.3514 | 471.1537 | 472.0857 | 621.0743 | 598.8635 | 580.247 | NaN | NaN | NaN | 641.5555 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.3029 | NaN | 21.6434
11672.1292 | 740.0596 | 636.749 | 500.6122 | 471.7756 | 472.2551 | 620.9258 | 597.3181 | 578.2364 | NaN | NaN | NaN | 636.7619 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.0756 | NaN | 20.6396
11673.1292 | 737.6931 | 635.8883 | 500.8145 | 471.9713 | 473.1079 | 619.6299 | 596.9232 | 575.1672 | NaN | NaN | NaN | 664.76 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.6363 | NaN | 20.7448
11674.1292 | 736.7659 | 635.2106 | 500.7995 | 472.1787 | 472.9501 | 616.0722 | 595.6967 | 575.2999 | NaN | NaN | NaN | 647.4707 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.703 | NaN | 19.3357
11675.1292 | 736.2048 | 635.4836 | 501.1751 | 471.8837 | 472.5552 | 612.8433 | 595.1528 | 575.3587 | NaN | NaN | NaN | 668.2666 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.5752 | NaN | 20.8917
11676.1292 | 735.7659 | 635.9253 | 501.2098 | 471.6622 | 472.4341 | 612.5276 | 594.9145 | 576.0572 | NaN | NaN | NaN | 687.5426 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.8259 | NaN | 21.4042
11677.1292 | 738.4462 | 635.7035 | 501.2383 | 472.102 | 473.3451 | 610.6192 | 596.2641 | 575.5545 | NaN | NaN | NaN | 712.0925 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.1553 | NaN | 22.2163
11678.1292 | 741.5111 | 635.3844 | 500.8505 | 471.9773 | 473.2408 | 608.3826 | 595.873 | 572.9502 | NaN | NaN | NaN | 726.5919 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.5417 | NaN | 19.3016
11679.1292 | 740.9746 | 636.0134 | 500.5254 | 471.8993 | 473.2658 | 618.3462 | 599.8603 | 571.799 | NaN | NaN | NaN | 719.1562 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.2108 | NaN | 20.0808
11680.1292 | 739.7877 | 635.5445 | 500.0259 | 471.664 | 473.1016 | 616.6658 | 599.1695 | 569.0204 | NaN | NaN | NaN | 708.7248 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.4931 | NaN | 18.3669
11681.1292 | 739.8325 | 636.0681 | 499.6334 | 472.196 | 473.1805 | 615.7212 | 600.4514 | 567.5984 | NaN | NaN | NaN | 729.7497 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.6295 | NaN | 21.2737
11682.1292 | 741.3757 | 636.5754 | 499.2517 | 472.0818 | 472.8497 | 616.198 | 600.8166 | 567.2692 | NaN | NaN | NaN | 733.9036 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.2445 | NaN | 19.5965
11683.1292 | 739.8394 | 636.6905 | 498.9827 | 471.8104 | 472.5439 | 616.3897 | 600.7296 | 565.9434 | NaN | NaN | NaN | 725.8902 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.7612 | NaN | 19.8331
11684.1292 | 740.6472 | 636.4138 | 499.0438 | 472.0087 | 472.0727 | 614.9513 | 600.8335 | 567.0357 | NaN | NaN | NaN | 714.3283 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.8048 | NaN | 19.9644
11685.1292 | 740.0348 | 636.2464 | 498.8783 | 472.4184 | 471.8047 | 616.3697 | 600.9821 | 568.5313 | NaN | NaN | NaN | 711.9288 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.0099 | NaN | 20.2499
11686.1292 | 737.1582 | 636.5005 | 498.6822 | 472.4432 | 471.9242 | 617.2647 | 602.0651 | 570.8763 | NaN | NaN | NaN | 722.4894 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.2609 | NaN | 21.1064
11687.1292 | 733.6823 | 636.1802 | 498.3133 | 472.5776 | 471.9325 | 623.2106 | 601.4184 | 573.8847 | NaN | NaN | NaN | 722.6131 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.7682 | NaN | 21.6737
11688.1292 | 730.5359 | 635.3359 | 498.3327 | 472.4807 | 472.1695 | 622.7548 | 599.907 | 572.8799 | NaN | NaN | NaN | 738.3422 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.3927 | NaN | 18.0105
11689.1292 | 728.1325 | 635.4386 | 498.316 | 472.3243 | 472.7425 | 620.9959 | 599.9849 | 570.8923 | NaN | NaN | NaN | 742.6372 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.656 | NaN | 20.8251
11690.1448 | 725.3593 | 635.203 | 497.9399 | 471.8959 | 472.6672 | 627.4225 | 598.8186 | 579.7468 | NaN | NaN | NaN | 762.8209 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.027 | NaN | 19.906
11691.1292 | 724.1809 | 635.3119 | 498.0385 | 471.7471 | 473.1596 | 631.1399 | 597.5436 | 580.5324 | NaN | NaN | NaN | 755.8321 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.8613 | NaN | 21.5293
11692.1292 | 723.6875 | 634.0474 | 498.2629 | 472.1947 | 473.1682 | 625.2339 | 597.0735 | 576.982 | NaN | NaN | NaN | 765.5921 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.272 | NaN | 21.3069
11693.1292 | 722.939 | 633.8398 | 498.2577 | 471.8398 | 472.7942 | 625.9986 | 597.2069 | 584.2348 | NaN | NaN | NaN | 787.5034 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.2126 | NaN | 19.1982
11694.1292 | 723.1321 | 634.2651 | 498.0732 | 471.4602 | 472.3659 | 622.1149 | 596.1989 | 581.2808 | NaN | NaN | NaN | 779.2579 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.3057 | NaN | 20.4643
11695.1292 | 722.7083 | 634.3316 | 497.8449 | 471.3327 | 472.2382 | 618.4484 | 595.2528 | 577.018 | NaN | NaN | NaN | 789.0028 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.7575 | NaN | 20.4942
11696.1292 | 723.3882 | 635.2859 | 497.6026 | 471.5561 | 472.1196 | 616.6491 | 593.955 | 571.7659 | NaN | NaN | NaN | 803.8899 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.6359 | NaN | 22.042
11697.1292 | 726.5973 | 636.1016 | 497.8109 | 471.7592 | 472.5468 | 613.6063 | 594.8124 | 579.2231 | NaN | NaN | NaN | 774.5062 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.1084 | NaN | 20.7652
11698.1292 | 730.579 | 636.2974 | 497.7825 | 471.7665 | 472.9318 | 611.7656 | 595.8215 | 578.2871 | NaN | NaN | NaN | 770.0584 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.4289 | NaN | 20.7111
11699.1292 | 732.0781 | 635.923 | 497.6068 | 471.3681 | 473.2687 | 609.9335 | 594.7984 | 575.4828 | NaN | NaN | NaN | 725.449 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.1104 | NaN | 20.8617
11700.1292 | 733.1284 | 635.8858 | 497.3364 | 471.0864 | 473.0017 | 610.883 | 595.192 | 571.4167 | NaN | NaN | NaN | 696.4209 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.5982 | NaN | 20.2387
11701.1292 | 731.891 | 635.468 | 497.2424 | 471.2262 | 472.6619 | 610.3116 | 594.3209 | 571.6451 | NaN | NaN | NaN | 691.9773 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.7777 | NaN | 19.0713
11702.1292 | 731.7199 | 635.4948 | 496.938 | 471.0553 | 472.1999 | 609.9691 | 592.9531 | 576.1992 | NaN | NaN | NaN | 686.6942 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.6235 | NaN | 20.2274
11703.1292 | 733.0052 | 635.8511 | 497.1532 | 471.0781 | 472.0105 | 614.9924 | 593.4718 | 572.3336 | NaN | NaN | NaN | 656.6046 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.8272 | NaN | 18.2714
11704.1292 | 731.8776 | 634.7016 | 497.5136 | 471.0961 | 471.7899 | 616.3398 | 592.8522 | 569.5021 | NaN | NaN | NaN | 650.5959 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.2674 | NaN | 21.6109
11705.1292 | 731.3608 | 634.2503 | 497.9183 | 470.7236 | 472.2638 | 613.3703 | 591.7445 | 570.7091 | NaN | NaN | NaN | 623.9515 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.3084 | NaN | 21.5418
11706.1292 | 733.7901 | 634.7029 | 498.1896 | 470.7024 | 472.7056 | 609.9915 | 591.6924 | 571.6954 | NaN | NaN | NaN | 657.4675 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.0089 | NaN | 21.6571
11707.1292 | 736.9366 | 636.0381 | 498.3992 | 470.8438 | 473.1818 | 608.8569 | 594.4703 | 576.2175 | NaN | NaN | NaN | 684.0013 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.7485 | NaN | 19.8207
11708.1292 | 739.8013 | 637.0087 | 498.3778 | 470.9727 | 473.454 | 608.9836 | 597.9818 | 576.8197 | NaN | NaN | NaN | 684.4357 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.4682 | NaN | 20.0737
11709.1292 | 741.0102 | 637.2282 | 498.5438 | 471.0382 | 474.3306 | 608.0172 | 598.0053 | 574.5995 | NaN | NaN | NaN | 650.7096 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.0718 | NaN | 20.15
11710.1292 | 740.5558 | 638.3912 | 498.669 | 471.0498 | 474.6012 | 609.1147 | 598.7537 | 572.0256 | NaN | NaN | NaN | 631.2748 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.1514 | NaN | 20.1172
11711.1292 | 740.0169 | 639.0227 | 499.4549 | 470.9484 | 474.58 | 611.0387 | 598.4425 | 571.0127 | NaN | NaN | NaN | 620.5959 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.4879 | NaN | 20.8269
11712.1292 | 741.3088 | 637.6674 | 499.8623 | 471.0407 | 474.4319 | 610.9392 | 597.4082 | 572.9284 | NaN | NaN | NaN | 599.5719 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.987 | NaN | 19.2203
11713.1292 | 744.8319 | 638.222 | 500.3588 | 471.231 | 474.3099 | 611.1568 | 596.7228 | 573.3675 | NaN | NaN | NaN | 592.5488 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.9014 | NaN | 20.6358
11714.1448 | 745.3213 | 638.0396 | 500.8013 | 470.8529 | 474.0671 | 608.767 | 596.0217 | 569.7446 | NaN | NaN | NaN | 593.9759 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.7838 | NaN | 18.7505
11715.1292 | 744.4402 | 638.028 | 500.9417 | 470.9354 | 473.7016 | 608.4253 | 594.833 | 570.6338 | NaN | NaN | NaN | 617.6815 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.128 | NaN | 20.336
11716.1448 | 742.3597 | 637.8074 | 500.9946 | 470.9259 | 473.3528 | 608.8693 | 594.4619 | 567.4953 | NaN | NaN | NaN | 653.6849 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 12.7494 | NaN | 23.4033
11717.1292 | 741.8461 | 637.5993 | 500.928 | 470.9257 | 473.3412 | 607.604 | 593.8164 | 564.9869 | NaN | NaN | NaN | 655.5059 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.7119 | NaN | 23.2756
11718.1292 | 742.3821 | 637.4186 | 500.8607 | 470.748 | 473.0907 | 605.6139 | 593.92 | 564.2685 | NaN | NaN | NaN | 686.0868 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.6299 | NaN | 23.0407
11719.1292 | 740.6704 | 637.043 | 500.7616 | 470.6996 | 472.8833 | 605.8539 | 593.8822 | 562.5715 | NaN | NaN | NaN | 669.0806 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.1786 | NaN | 21.0719
11720.1292 | 737.8223 | 635.8082 | 500.5352 | 470.7105 | 472.5129 | 605.3658 | 592.4555 | 559.2455 | NaN | NaN | NaN | 643.3451 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.9939 | NaN | 20.2032
11721.1292 | 735.465 | 635.4052 | 500.15 | 470.5552 | 472.2841 | 604.1406 | 591.9719 | 558.8032 | NaN | NaN | NaN | 634.7503 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.0448 | NaN | 22.8782
11722.1292 | 733.8544 | 635.4566 | 499.7602 | 470.277 | 472.1313 | 603.2915 | 592.4352 | 562.5612 | NaN | NaN | NaN | 637.9291 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.0162 | NaN | 20.3338
11723.1292 | 733.0128 | 635.4933 | 500.0731 | 470.1266 | 471.9306 | 603.4686 | 592.0701 | 569.6251 | NaN | NaN | NaN | 666.7636 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.646 | NaN | 18.8339
11724.1292 | 733.0957 | 635.1383 | 500.2099 | 470.0957 | 471.6935 | 603.249 | 591.4434 | 574.1509 | NaN | NaN | NaN | 699.4127 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.1241 | NaN | 18.7361
11725.1292 | 732.2405 | 635.7889 | 500.2951 | 469.9016 | 471.6579 | 604.9715 | 593.1584 | 575.3725 | NaN | NaN | NaN | 712.0606 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.5555 | NaN | 19.5168
11726.1292 | 729.6543 | 634.5983 | 500.3799 | 469.8515 | 472.0035 | 604.7437 | 591.5775 | 573.1576 | NaN | NaN | NaN | 701.294 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.5677 | NaN | 23.8459
11727.1292 | 727.0514 | 634.02 | 500.1694 | 470.0433 | 471.8951 | 607.9257 | 591.9901 | 569.1911 | NaN | NaN | NaN | 685.7007 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.8229 | NaN | 20.2854
11728.1292 | 726.9104 | 633.5846 | 499.8586 | 470.2673 | 472.0514 | 610.2164 | 589.1633 | 566.0222 | NaN | NaN | NaN | 689.4148 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.0461 | NaN | 21.9715
11729.1292 | 727.4043 | 633.9569 | 499.7091 | 470.2059 | 471.7347 | 612.1954 | 589.8822 | 566.9425 | NaN | NaN | NaN | 706.5711 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.9565 | NaN | 18.8107
11730.1292 | 728.8716 | 634.7155 | 499.3917 | 470.4971 | 472.0001 | 614.166 | 592.9701 | 567.3187 | NaN | NaN | NaN | 713.5556 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.9518 | NaN | 18.5008
11731.1292 | 728.1659 | 634.2956 | 499.0637 | 470.8722 | 472.0705 | 612.7849 | 591.6175 | 563.253 | NaN | NaN | NaN | 707.2424 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.9724 | NaN | 16.6724
11732.1292 | 725.9314 | 633.7527 | 498.685 | 470.7457 | 472.0117 | 612.5326 | 590.9764 | 560.1438 | NaN | NaN | NaN | 716.9797 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.6044 | NaN | 20.6488
11733.1292 | 726.4924 | 633.506 | 498.5174 | 470.4503 | 472.3708 | 611.6345 | 591.4436 | 559.8285 | NaN | NaN | NaN | 689.5187 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.164 | NaN | 19.9576
11734.1292 | 729.5599 | 633.7473 | 498.1952 | 471.1401 | 472.1184 | 608.7083 | 590.5932 | 567.3048 | NaN | NaN | NaN | 660.3575 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.6184 | NaN | 21.1945
11735.1292 | 731.7151 | 634.8103 | 497.8916 | 471.1969 | 472.2049 | 607.1832 | 591.4331 | 564.9541 | NaN | NaN | NaN | 638.1982 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.8968 | NaN | 20.5113
11736.1292 | 735.2224 | 636.0596 | 497.5747 | 471.507 | 472.1248 | 609.7399 | 592.5793 | 563.5747 | NaN | NaN | NaN | 642.7351 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.4786 | NaN | 19.538
11737.1292 | 738.0733 | 636.9502 | 497.627 | 471.7256 | 471.8149 | 611.6713 | 592.6069 | 566.7716 | NaN | NaN | NaN | 631.5168 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.5389 | NaN | 21.1697
11738.1292 | 739.6146 | 638.8105 | 498.4457 | 472.2956 | 471.8431 | 610.8222 | 594.4624 | 564.6059 | NaN | NaN | NaN | 626.1511 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.6519 | NaN | 21.6843
11739.1292 | 740.4147 | 639.8966 | 499.2344 | 472.9329 | 472.1575 | 612.1822 | 595.5673 | 565.2828 | NaN | NaN | NaN | 657.1902 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.6528 | NaN | 18.8765
11740.1292 | 742.0981 | 638.9759 | 500.0945 | 473.6125 | 472.5639 | 611.3396 | 594.8119 | 567.1682 | NaN | NaN | NaN | 682.6907 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.4999 | NaN | 21.3497
11741.1292 | 742.8557 | 640.2849 | 500.7142 | 473.4474 | 472.0264 | 610.2732 | 595.2143 | 565.8544 | NaN | NaN | NaN | 674.281 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.8473 | NaN | 18.9207
11742.1292 | 742.9023 | 639.7118 | 501.4028 | 473.279 | 471.5536 | 611.1101 | 595.7227 | 565.031 | NaN | NaN | NaN | 654.832 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.6793 | NaN | 19.8957
11743.1292 | 740.388 | 638.7868 | 502.2318 | 473.1351 | 471.1728 | 611.8795 | 594.6697 | 563.8722 | NaN | NaN | NaN | 640.8626 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.6074 | NaN | 21.0107
11744.1292 | 739.4615 | 638.1204 | 502.2903 | 473.0557 | 470.6973 | 611.4435 | 593.2216 | 568.7798 | NaN | NaN | NaN | 669.0705 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.7024 | NaN | 22.8985
11745.1292 | 738.2296 | 638.1621 | 502.0598 | 472.3237 | 470.5511 | 609.9862 | 591.7249 | 565.0707 | NaN | NaN | NaN | 676.6162 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.2545 | NaN | 20.4176
11746.1292 | 739.6046 | 638.0355 | 502.293 | 471.8214 | 470.3802 | 608.7474 | 591.1273 | 564.768 | NaN | NaN | NaN | 650.7235 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.2046 | NaN | 21.5093
11747.1292 | 740.0977 | 637.4687 | 502.3611 | 471.8435 | 470.4652 | 610.0209 | 591.3414 | 564.7636 | NaN | NaN | NaN | 656.5728 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.9962 | NaN | 20.6262
11748.1292 | 740.9148 | 637.4657 | 502.5132 | 472.6358 | 470.4993 | 613.8389 | 591.1257 | 567.276 | NaN | NaN | NaN | 653.1049 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.2085 | NaN | 20.9149
11749.1292 | 742.6422 | 637.1302 | 503.1095 | 472.9147 | 470.7226 | 612.3829 | 592.8535 | 566.1678 | NaN | NaN | NaN | 626.9002 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.3694 | NaN | 19.4581
11750.1292 | 744.3619 | 637.7388 | 503.0369 | 472.743 | 471.8954 | 609.9057 | 593.3135 | 564.7657 | NaN | NaN | NaN | 615.6982 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.1021 | NaN | 21.1931
11751.1292 | 747.4565 | 639.6832 | 503.1454 | 473.0897 | 471.941 | 607.6456 | 594.6812 | 567.3862 | NaN | NaN | NaN | 646.4074 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.3818 | NaN | 19.0339
11752.1292 | 749.5019 | 640.8249 | 503.3896 | 473.3319 | 472.4446 | 612.6895 | 596.4562 | 565.1861 | NaN | NaN | NaN | 660.9336 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.9734 | NaN | 21.9739
11753.1292 | 751.7771 | 640.2697 | 503.5435 | 473.3027 | 472.2794 | 612.38 | 594.8123 | 562.8241 | NaN | NaN | NaN | 648.9813 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.5578 | NaN | 19.53
11754.1292 | 754.0394 | 641.1415 | 503.5247 | 473.4096 | 472.1878 | 609.9068 | 595.3835 | 561.6748 | NaN | NaN | NaN | 620.5585 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.8409 | NaN | 20.8121
11755.1292 | 754.5785 | 642.7421 | 504.1014 | 473.3616 | 472.7389 | 609.9417 | 595.9705 | 561.1021 | NaN | NaN | NaN | 603.2102 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.2495 | NaN | 19.3036
11756.1292 | 753.4825 | 642.3379 | 504.9998 | 473.5444 | 472.8802 | 611.2277 | 595.3944 | 558.8458 | NaN | NaN | NaN | 624.1557 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.5822 | NaN | 21.3368
11757.1292 | 753.2499 | 642.2627 | 505.5298 | 473.936 | 472.9252 | 610.9837 | 595.6696 | 563.8832 | NaN | NaN | NaN | 668.8665 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.4183 | NaN | 19.2362
11758.1292 | 754.9903 | 643.9479 | 505.723 | 474.2732 | 472.8772 | 609.2001 | 598.2245 | 565.4487 | NaN | NaN | NaN | 672.0307 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.9156 | NaN | 16.5251
11759.1292 | 755.6525 | 645.3012 | 506.3225 | 474.9221 | 473.29 | 609.7608 | 599.986 | 563.5806 | NaN | NaN | NaN | 665.9457 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.9635 | NaN | 20.7476
11760.1292 | 755.2387 | 645.1404 | 506.7677 | 475.5358 | 473.9679 | 611.7935 | 600.8782 | 563.0078 | NaN | NaN | NaN | 637.4199 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.0792 | NaN | 21.9562
11761.1292 | 755.83 | 644.9937 | 506.6875 | 475.7029 | 474.208 | 611.6105 | 600.0473 | 561.8111 | NaN | NaN | NaN | 633.833 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.3189 | NaN | 19.3812
11762.1292 | 757.4765 | 644.0849 | 506.7539 | 475.5767 | 474.2415 | 612.2707 | 601.9851 | 562.5224 | NaN | NaN | NaN | 646.3914 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.4402 | NaN | 20.8103
11763.1292 | 757.7188 | 643.2792 | 507.0042 | 475.449 | 474.2037 | 617.3986 | 602.8898 | 562.8184 | NaN | NaN | NaN | 652.1155 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.5225 | NaN | 18.8166
11764.1292 | 757.2689 | 643.0411 | 506.8962 | 475.0256 | 474.3004 | 614.2505 | 601.2255 | 560.9354 | NaN | NaN | NaN | 662.4196 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.5877 | NaN | 16.1835
11765.1292 | 755.9332 | 642.0312 | 506.7234 | 474.9583 | 474.3054 | 612.8632 | 600.9594 | 558.8333 | NaN | NaN | NaN | 653.7516 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.0788 | NaN | 19.5898
11766.1292 | 754.5851 | 641.9058 | 506.4683 | 475.0294 | 474.2584 | 612.4952 | 600.7647 | 558.0885 | NaN | NaN | NaN | 668.0495 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.9197 | NaN | 21.0155
11767.1292 | 752.2982 | 641.5151 | 506.235 | 474.7967 | 474.4082 | 616.1654 | 602.1147 | 557.2193 | NaN | NaN | NaN | 676.4887 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.486 | NaN | 16.6278
11768.1292 | 748.9146 | 640.1788 | 506.1192 | 474.1897 | 474.147 | 614.0971 | 599.0196 | 555.3243 | NaN | NaN | NaN | 681.4627 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.7246 | NaN | 21.7322
11769.1292 | 745.0314 | 639.2133 | 505.5661 | 473.6731 | 473.9234 | 614.3117 | 598.1158 | 552.6673 | NaN | NaN | NaN | 678.6615 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.1387 | NaN | 22.728
11770.1292 | 741.3179 | 638.2531 | 505.0128 | 473.2573 | 473.7781 | 615.8741 | 596.1414 | 550.1007 | NaN | NaN | NaN | 672.441 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.5676 | NaN | 22.2545
11771.1292 | 739.6203 | 637.3175 | 504.5368 | 472.7234 | 473.4038 | 613.4521 | 594.405 | 548.2608 | NaN | NaN | NaN | 689.5546 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.9614 | NaN | 18.7728
11772.1292 | 740.5794 | 636.2108 | 504.0841 | 472.9248 | 472.9531 | 609.8901 | 593.0475 | 547.0247 | NaN | NaN | NaN | 696.2355 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.7669 | NaN | 19.5555
11773.1292 | 742.8004 | 636.7068 | 503.8105 | 472.7671 | 473.0854 | 608.353 | 593.8444 | 545.6726 | NaN | NaN | NaN | 677.3435 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.4775 | NaN | 19.6405
11774.1292 | 743.7126 | 637.4097 | 503.2787 | 472.8307 | 473.4306 | 611.9301 | 596.2735 | 547.0215 | NaN | NaN | NaN | 664.7055 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.2325 | NaN | 20.1602
11775.1292 | 742.4673 | 637.5664 | 503.0965 | 472.9292 | 473.105 | 615.4372 | 598.0855 | 549.3967 | NaN | NaN | NaN | 657.3237 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.1514 | NaN | 19.1219
11776.1292 | 740.3823 | 637.8269 | 503.1964 | 473.1897 | 472.7462 | 614.6387 | 598.9899 | 549.3594 | NaN | NaN | NaN | 647.0578 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.1072 | NaN | 19.9477
11777.1292 | 738.3167 | 637.5934 | 502.9003 | 472.9469 | 472.5369 | 613.6065 | 598.5451 | 549.5052 | NaN | NaN | NaN | 649.2859 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.124 | NaN | 21.1705
11778.1292 | 736.3651 | 637.0902 | 503.0118 | 472.5195 | 472.5236 | 615.9905 | 598.8987 | 556.1489 | NaN | NaN | NaN | 675.4031 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.7892 | NaN | 21.356
11779.1292 | 736.6208 | 637.3482 | 503.1115 | 472.3402 | 472.9428 | 616.0229 | 599.2926 | 556.5052 | NaN | NaN | NaN | 690.6561 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.4755 | NaN | 21.4641
11780.1292 | 735.7654 | 637.259 | 502.7132 | 471.9461 | 472.5923 | 616.6472 | 599.5018 | 558.5726 | NaN | NaN | NaN | 685.8323 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.8629 | NaN | 23.6892
11781.1292 | 734.4477 | 637.1925 | 502.9626 | 472.0712 | 472.4005 | 617.4773 | 599.0732 | 559.3802 | NaN | NaN | NaN | 688.8775 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.8982 | NaN | 21.3969
11782.1292 | 732.1502 | 636.5871 | 502.3331 | 472.0301 | 472.2018 | 621.2834 | 597.4838 | 558.8632 | NaN | NaN | NaN | 690.5196 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.1358 | NaN | 22.7736
11783.1292 | 730.2037 | 635.4913 | 501.7852 | 471.8715 | 472.2836 | 620.4374 | 595.7872 | 558.4972 | NaN | NaN | NaN | 681.7088 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.0993 | NaN | 19.4319
11784.1292 | 729.2649 | 634.3953 | 501.4422 | 471.7284 | 472.2578 | 618.4596 | 593.4625 | 556.0097 | NaN | NaN | NaN | 688.4042 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.7807 | NaN | 20.1687
11785.1292 | 729.7287 | 634.2979 | 501.0591 | 471.4826 | 472.5066 | 619.6726 | 593.2267 | 555.8891 | NaN | NaN | NaN | 698.7442 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.0861 | NaN | 21.7044
11786.1292 | 729.7033 | 634.1867 | 500.8254 | 471.2905 | 472.4833 | 617.6887 | 593.0055 | 555.7269 | NaN | NaN | NaN | 695.7421 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.3533 | NaN | 20.5976
11787.1292 | 730.4575 | 634.4285 | 501.0415 | 471.2423 | 472.2294 | 615.5925 | 592.171 | 555.7404 | NaN | NaN | NaN | 708.2573 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.8358 | NaN | 20.0628
11788.1292 | 733.4431 | 634.6376 | 500.8099 | 470.9888 | 472.06 | 615.0109 | 592.5781 | 554.9289 | NaN | NaN | NaN | 689.1319 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.1753 | NaN | 19.5449
11789.1292 | 734.8102 | 634.9905 | 500.7351 | 470.7721 | 472.1877 | 615.1412 | 594.3985 | 555.9785 | NaN | NaN | NaN | 689.0487 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.9579 | NaN | 18.779
11790.1292 | 733.569 | 634.9902 | 500.5783 | 470.7004 | 472.2794 | 614.938 | 595.9077 | 558.4837 | NaN | NaN | NaN | 709.466 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.4232 | NaN | 21.2507
11791.1292 | 733.1599 | 634.4046 | 500.5242 | 470.5626 | 472.5327 | 616.8556 | 594.4938 | 558.5602 | NaN | NaN | NaN | 694.0653 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.4615 | NaN | 19.2027
11792.1292 | 733.4573 | 634.8039 | 500.1744 | 470.6388 | 472.7832 | 615.2046 | 594.6397 | 557.0305 | NaN | NaN | NaN | 714.4972 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.9492 | NaN | 20.5667
11793.1292 | 734.1948 | 634.5286 | 500.1784 | 471.5025 | 473.18 | 612.7001 | 595.6144 | 558.6885 | NaN | NaN | NaN | 725.0997 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.0491 | NaN | 19.9025
11794.1292 | 735.0568 | 635.5825 | 499.6874 | 471.8516 | 473.4731 | 611.6815 | 598.4051 | 560.9805 | NaN | NaN | NaN | 729.4074 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.2153 | NaN | 19.3432
11795.1292 | 735.2209 | 635.2144 | 499.3461 | 471.9464 | 474.0237 | 609.7351 | 598.6383 | 560.7347 | NaN | NaN | NaN | 739.9215 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.6453 | NaN | 20.9999
11796.1292 | 735.1457 | 635.2937 | 499.3212 | 471.7211 | 473.9276 | 607.9129 | 599.1846 | 559.876 | NaN | NaN | NaN | 750.4388 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.1719 | NaN | 21.5367
11797.1292 | 735.2957 | 634.0382 | 499.4849 | 471.262 | 473.7828 | 611.4392 | 598.2487 | 558.6466 | NaN | NaN | NaN | 750.6536 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.535 | NaN | 20.6069
11798.1292 | 735.0999 | 633.7438 | 499.424 | 470.795 | 473.7723 | 610.196 | 600.733 | 561.5073 | NaN | NaN | NaN | 771.2103 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.091 | NaN | 21.733
11799.1292 | 733.8997 | 634.1603 | 499.0722 | 470.416 | 473.3844 | 609.7877 | 604.1551 | 564.5627 | NaN | NaN | NaN | 757.7086 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.725 | NaN | 20.3637
11800.1292 | 732.4242 | 634.3367 | 498.8898 | 470.1683 | 473.19 | 610.7633 | 604.896 | 562.7789 | NaN | NaN | NaN | 762.8709 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.1865 | NaN | 18.5457
11801.1292 | 732.1151 | 633.8499 | 498.5818 | 470.3778 | 472.8625 | 609.952 | 604.5632 | 565.9675 | NaN | NaN | NaN | 755.7063 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.708 | NaN | 19.0251
11802.1292 | 731.7645 | 633.7076 | 498.352 | 470.7385 | 472.8674 | 611.8034 | 604.8447 | 562.9055 | NaN | NaN | NaN | 719.5363 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.6331 | NaN | 21.6659
11803.1292 | 731.3765 | 634.6901 | 498.5494 | 470.8557 | 472.6805 | 611.664 | 605.8399 | 561.2578 | NaN | NaN | NaN | 744.6381 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.4427 | NaN | 19.1557
11804.1292 | 731.4807 | 634.1429 | 498.3725 | 470.8718 | 472.4578 | 614.923 | 606.5256 | 559.2818 | NaN | NaN | NaN | 751.1377 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.8135 | NaN | 20.8791
11805.1292 | 732.5559 | 635.3967 | 498.5571 | 470.5724 | 471.9594 | 612.0226 | 604.9169 | 558.1229 | NaN | NaN | NaN | 771.6832 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.1846 | NaN | 18.8792
11806.1292 | 734.8098 | 635.9951 | 498.9454 | 470.5449 | 472.1335 | 611.4179 | 606.05 | 556.6447 | NaN | NaN | NaN | 753.6978 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.1605 | NaN | 19.4373
11807.1292 | 736.0307 | 635.5343 | 499.6264 | 470.5015 | 472.4839 | 610.5615 | 606.6432 | 557.5599 | NaN | NaN | NaN | 776.8415 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.4473 | NaN | 19.4756
11808.1292 | 736.4693 | 634.8122 | 499.7902 | 470.5714 | 472.1228 | 610.9771 | 605.607 | 556.1659 | NaN | NaN | NaN | 782.2659 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.633 | NaN | 19.7036
11809.1292 | 738.2448 | 635.5509 | 499.5147 | 470.219 | 471.6903 | 608.4462 | 604.1438 | 554.3062 | NaN | NaN | NaN | 796.4041 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.5032 | NaN | 19.6737
11810.1292 | 737.3265 | 634.9329 | 499.3465 | 470.2318 | 471.6198 | 607.0917 | 603.761 | 553.4878 | NaN | NaN | NaN | 817.0022 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.0371 | NaN | 19.1321
11811.1292 | 736.0445 | 634.3612 | 499.0881 | 470.4537 | 471.5054 | 605.6491 | 601.7153 | 552.2033 | NaN | NaN | NaN | 818.8809 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.2156 | NaN | 22.5579
11812.1292 | 736.4568 | 634.1734 | 498.9375 | 470.5601 | 471.112 | 602.8563 | 600.4126 | 550.0281 | NaN | NaN | NaN | 761.8231 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.1055 | NaN | 22.125
11813.1292 | 735.8197 | 633.5269 | 498.8368 | 470.6248 | 471.0564 | 602.8425 | 599.8814 | 549.987 | NaN | NaN | NaN | 739.775 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.5131 | NaN | 21.9188
11814.1292 | 738.4583 | 633.5309 | 499.856 | 470.9647 | 470.8869 | 600.9623 | 598.3943 | 549.5213 | NaN | NaN | NaN | 736.2566 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.8378 | NaN | 17.972
11815.1292 | 741.7398 | 634.8769 | 499.9924 | 471.3331 | 470.6149 | 600.5689 | 600.2328 | 550.046 | NaN | NaN | NaN | 747.7261 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.5658 | NaN | 20.2511
11816.1292 | 742.2242 | 635.5795 | 499.8057 | 471.7312 | 470.9579 | 601.6841 | 600.8308 | 550.0902 | NaN | NaN | NaN | 714.8969 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.3419 | NaN | 19.7473
11817.1292 | 741.477 | 634.7817 | 499.9043 | 471.9864 | 471.128 | 600.4935 | 600.3413 | 548.6059 | NaN | NaN | NaN | 683.1049 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.951 | NaN | 20.5139
11818.1292 | 742.1619 | 634.6667 | 499.9825 | 471.5 | 471.3065 | 599.0195 | 599.2768 | 547.392 | NaN | NaN | NaN | 655.1924 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.3865 | NaN | 18.9903
11819.1292 | 741.407 | 634.2272 | 499.9367 | 471.2371 | 471.4677 | 597.5409 | 598.5715 | 547.7113 | NaN | NaN | NaN | 633.3931 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.8867 | NaN | 19.5125
11820.1292 | 739.4301 | 633.2937 | 499.727 | 471.5686 | 470.5902 | 596.0089 | 596.7426 | 545.5572 | NaN | NaN | NaN | 623.8747 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.6799 | NaN | 20.9878
11821.1292 | 736.179 | 632.4887 | 499.3598 | 470.8785 | 470.5586 | 596.997 | 595.7813 | 543.7128 | NaN | NaN | NaN | 603.6343 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.5835 | NaN | 22.3929
11822.1292 | 736.4869 | 632.1567 | 499.3169 | 470.3357 | 470.4371 | 597.5247 | 594.5037 | 542.6761 | NaN | NaN | NaN | 601.4361 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.0529 | NaN | 20.0718
11823.1292 | 736.6021 | 631.9487 | 499.5762 | 469.7785 | 470.4404 | 597.8277 | 594.117 | 542.381 | NaN | NaN | NaN | 616.5594 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.4248 | NaN | 20.0979
11824.1292 | 737.802 | 632.4387 | 499.0735 | 469.4451 | 470.355 | 596.7288 | 594.9938 | 542.3475 | NaN | NaN | NaN | 638.1949 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.1741 | NaN | 22.9679
11825.1292 | 739.2026 | 632.2587 | 498.4659 | 469.4281 | 470.0541 | 595.5002 | 595.6773 | 543.7216 | NaN | NaN | NaN | 665.7316 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.9377 | NaN | 21.2181
11826.1292 | 739.6108 | 632.0239 | 498.0253 | 469.247 | 470.0794 | 594.402 | 596.8316 | 544.5585 | NaN | NaN | NaN | 682.6393 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.8355 | NaN | 18.7815
11827.1292 | 740.0602 | 631.5977 | 497.5749 | 469.169 | 470.0274 | 596.7452 | 599.0661 | 546.3408 | NaN | NaN | NaN | 694.8897 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.6364 | NaN | 21.0436
11828.1292 | 740.3082 | 631.7894 | 497.394 | 469.4919 | 470.5384 | 596.701 | 600.0121 | 547.8706 | NaN | NaN | NaN | 700.913 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.3296 | NaN | 22.4699
11829.1292 | 740.8894 | 632.4915 | 497.1835 | 469.6696 | 471.077 | 596.1647 | 598.6583 | 548.7795 | NaN | NaN | NaN | 713.4287 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.879 | NaN | 21.5459
11830.1292 | 741.4443 | 632.1782 | 497.2765 | 470.3854 | 470.7981 | 596.2044 | 599.0866 | 555.8965 | NaN | NaN | NaN | 703.0119 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.8974 | NaN | 22.1473
11831.1292 | 741.1367 | 632.1624 | 497.1458 | 470.7398 | 470.5532 | 600.7121 | 596.8054 | 559.4599 | NaN | NaN | NaN | 668.0279 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.0624 | NaN | 21.732
11832.1292 | 739.8765 | 632.3392 | 497.18 | 470.6145 | 470.4221 | 600.6372 | 596.2292 | 556.4264 | NaN | NaN | NaN | 644.8071 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.0843 | NaN | 21.9864
11833.1292 | 740.1419 | 632.2323 | 497.396 | 470.6744 | 470.7618 | 599.0163 | 595.3827 | 555.0851 | NaN | NaN | NaN | 631.221 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.5265 | NaN | 22.176
11834.1292 | 741.2304 | 632.1677 | 497.58 | 470.3478 | 470.9329 | 598.618 | 596.2754 | 561.5585 | NaN | NaN | NaN | 621.7769 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.1657 | NaN | 18.8939
11835.1292 | 742.2667 | 633.0667 | 497.6727 | 470.5596 | 471.0933 | 597.5753 | 598.0763 | 560.2746 | NaN | NaN | NaN | 625.0405 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.9737 | NaN | 19.1815
11836.1292 | 741.7707 | 632.335 | 497.3576 | 470.5552 | 470.7111 | 595.7748 | 597.3836 | 559.2491 | NaN | NaN | NaN | 617.3908 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.2675 | NaN | 20.3204
11837.1292 | 741.819 | 632.9819 | 496.6998 | 470.1608 | 470.7482 | 596.6924 | 597.0522 | 557.2324 | NaN | NaN | NaN | 607.9808 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.9552 | NaN | 18.9757
11838.1292 | 741.8927 | 632.7617 | 496.9298 | 470.103 | 470.5254 | 597.087 | 597.85 | 556.283 | NaN | NaN | NaN | 602.581 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.2498 | NaN | 21.7284
11839.1292 | 741.8323 | 631.9556 | 497.081 | 469.8119 | 470.119 | 596.7325 | 596.3185 | 556.751 | NaN | NaN | NaN | 603.5668 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.3443 | NaN | 21.6742
11840.1292 | 742.1361 | 632.2334 | 496.9467 | 469.7429 | 470.0549 | 596.6153 | 597.7365 | 556.3865 | NaN | NaN | NaN | 621.584 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.1511 | NaN | 22.5861
11841.1292 | 743.7329 | 632.8704 | 497.0333 | 469.8309 | 469.7511 | 595.9641 | 596.6269 | 554.7379 | NaN | NaN | NaN | 622.1514 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.1799 | NaN | 21.7805
11842.1292 | 743.9118 | 633.4068 | 497.3871 | 469.9899 | 470.1224 | 594.1732 | 595.7381 | 553.5257 | NaN | NaN | NaN | 619.2188 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.6379 | NaN | 22.6421
11843.1292 | 743.7898 | 632.7217 | 497.4668 | 470.6478 | 470.0326 | 594.675 | 595.3122 | 555.858 | NaN | NaN | NaN | 630.5175 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.1627 | NaN | 20.7533
11844.1292 | 743.4929 | 632.2101 | 497.4844 | 470.8141 | 470.0422 | 593.0427 | 593.7335 | 554.6687 | NaN | NaN | NaN | 604.5234 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.9275 | NaN | 20.8341
11845.1292 | 744.3322 | 632.5754 | 497.4623 | 470.679 | 470.0301 | 592.4168 | 592.552 | 554.4338 | NaN | NaN | NaN | 618.708 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.698 | NaN | 21.184
11846.1292 | 745.7351 | 632.2206 | 497.4564 | 470.654 | 470.2838 | 596.9334 | 593.4061 | 556.9107 | NaN | NaN | NaN | 640.387 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.355 | NaN | 20.8329
11847.1292 | 748.2411 | 632.9294 | 496.9755 | 471.0927 | 470.1309 | 598.185 | 593.6398 | 557.0574 | NaN | NaN | NaN | 663.1229 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.4378 | NaN | 19.1347
11848.1292 | 749.6158 | 633.3364 | 496.8241 | 471.3596 | 470.2223 | 600.8493 | 594.2774 | 557.0728 | NaN | NaN | NaN | 655.1539 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.0639 | NaN | 19.4891
11849.1292 | 750.9884 | 633.9355 | 496.6619 | 471.2071 | 470.083 | 601.2093 | 598.2238 | 557.5983 | NaN | NaN | NaN | 658.9826 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.2772 | NaN | 20.124
11850.1292 | 751.8192 | 634.4886 | 496.7314 | 471.0888 | 470.29 | 599.0816 | 597.9157 | 557.9812 | NaN | NaN | NaN | 651.396 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.9842 | NaN | 20.3237
11851.1292 | 752.3589 | 634.4621 | 496.8643 | 471.4311 | 470.6554 | 597.5937 | 597.2243 | 558.1699 | NaN | NaN | NaN | 631.5277 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.9873 | NaN | 19.3189
11852.1292 | 752.8356 | 634.2149 | 496.6612 | 471.8919 | 470.7717 | 599.0698 | 597.0738 | 556.1454 | NaN | NaN | NaN | 637.3638 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.7611 | NaN | 20.1741
11853.1292 | 752.8217 | 633.9855 | 496.4887 | 471.7527 | 470.6976 | 598.4953 | 595.6771 | 555.2766 | NaN | NaN | NaN | 646.713 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.4279 | NaN | 19.8894
11854.1292 | 754.6137 | 634.835 | 496.541 | 471.4532 | 470.3564 | 597.3094 | 595.2542 | 553.8722 | NaN | NaN | NaN | 656.2581 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.1979 | NaN | 19.2468
11855.1292 | 758.0585 | 635.8301 | 496.3993 | 471.5189 | 470.6058 | 597.3719 | 595.7071 | 554.37 | NaN | NaN | NaN | 627.9936 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.0978 | NaN | 20.0258
11856.1292 | 757.9408 | 636.1056 | 496.5403 | 471.5131 | 470.8118 | 597.7584 | 596.0489 | 555.0318 | NaN | NaN | NaN | 624.7507 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.4063 | NaN | 19.7657
11857.1292 | 757.8016 | 636.5263 | 497.0338 | 471.7274 | 471.1729 | 596.9381 | 596.6619 | 554.9719 | NaN | NaN | NaN | 617.8766 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.2027 | NaN | 21.1846
11858.1292 | 757.3666 | 636.4902 | 497.4532 | 472.2344 | 471.767 | 595.7512 | 596.6558 | 556.7299 | NaN | NaN | NaN | 617.3474 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.3196 | NaN | 20.0343
11859.1292 | 756.5162 | 636.2732 | 497.5704 | 472.2145 | 472.0242 | 594.5996 | 596.2647 | 558.8661 | NaN | NaN | NaN | 593.3274 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.789 | NaN | 21.2048
11860.1292 | 754.847 | 635.4951 | 497.8133 | 472.1653 | 472.0775 | 592.788 | 594.2395 | 556.4262 | NaN | NaN | NaN | 587.8059 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.4612 | NaN | 20.841
11861.1292 | 754.6911 | 635.7159 | 497.9583 | 472.5729 | 471.9281 | 593.4574 | 595.9358 | 555.3187 | NaN | NaN | NaN | 569.3296 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.7345 | NaN | 22.5916
11862.1292 | 754.6544 | 636.3214 | 498.2694 | 472.2454 | 472.1427 | 595.4615 | 596.6206 | 556.8476 | NaN | NaN | NaN | 558.0973 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.1649 | NaN | 22.4878
11863.1292 | 754.7177 | 635.9441 | 498.4329 | 472.1513 | 472.6459 | 596.0479 | 597.0746 | 563.9543 | NaN | NaN | NaN | 542.809 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.8781 | NaN | 21.7499
11864.1292 | 755.0847 | 636.5868 | 498.6232 | 471.9796 | 472.972 | 596.3235 | 597.5775 | 562.0263 | NaN | NaN | NaN | 565.1545 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.6895 | NaN | 21.2286
11865.1292 | 755.6063 | 636.7341 | 498.8037 | 471.9369 | 473.3042 | 597.9838 | 599.6077 | 561.8063 | NaN | NaN | NaN | 600.1593 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.3929 | NaN | 21.9254
11866.1292 | 755.1767 | 636.8815 | 499.2305 | 471.5995 | 473.2783 | 599.3964 | 601.9494 | 562.0076 | NaN | NaN | NaN | 610.6281 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.2281 | NaN | 21.311
11867.1292 | 752.7676 | 635.996 | 499.2818 | 471.0585 | 473.1406 | 604.4922 | 601.0409 | 561.024 | NaN | NaN | NaN | 613.6067 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.024 | NaN | 20.9132
11868.1292 | 752.2265 | 635.9226 | 499.5886 | 470.5189 | 472.6597 | 601.9374 | 599.498 | 559.1489 | NaN | NaN | NaN | 632.7625 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.8409 | NaN | 19.7361
11869.1292 | 751.4687 | 635.9693 | 499.4844 | 469.9592 | 472.3984 | 601.4544 | 598.9762 | 563.4876 | NaN | NaN | NaN | 661.3163 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.3661 | NaN | 18.4755
11870.1292 | 753.1352 | 635.7383 | 499.5335 | 470.4177 | 472.1642 | 601.8259 | 597.6326 | 561.1919 | NaN | NaN | NaN | 676.2268 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.8801 | NaN | 20.7535
11871.1292 | 753.308 | 636.4127 | 499.5617 | 470.6355 | 472.6962 | 603.6117 | 598.367 | 559.7931 | NaN | NaN | NaN | 706.7745 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.0548 | NaN | 20.9932
11872.1292 | 752.748 | 636.6765 | 500.0558 | 470.9559 | 472.9294 | 602.6884 | 598.6938 | 562.045 | NaN | NaN | NaN | 724.1205 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.1944 | NaN | 17.5021
11873.1292 | 752.1903 | 635.7217 | 500.553 | 471.2218 | 473.1536 | 601.3975 | 598.7756 | 559.3804 | NaN | NaN | NaN | 737.7592 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.8597 | NaN | 21.3348
11874.1292 | 751.1224 | 635.2922 | 500.9226 | 471.4536 | 473.2438 | 600.2938 | 597.4747 | 562.1128 | NaN | NaN | NaN | 732.193 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.664 | NaN | 22.8979
11875.1292 | 749.4793 | 635.4227 | 501.4648 | 471.9359 | 472.9933 | 599.4354 | 596.5014 | 559.2252 | NaN | NaN | NaN | 709.7428 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.951 | NaN | 20.152
11876.1292 | 750.2602 | 635.7036 | 501.7026 | 471.9501 | 473.0121 | 597.9726 | 596.191 | 557.1592 | NaN | NaN | NaN | 720.1371 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.6067 | NaN | 20.5254
11877.1292 | 750.7667 | 635.8785 | 501.4383 | 471.7918 | 472.6547 | 597.1965 | 596.4904 | 557.7775 | NaN | NaN | NaN | 691.9171 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.7596 | NaN | 20.6173
11878.1292 | 750.0283 | 635.5276 | 501.3938 | 471.3122 | 472.429 | 596.4639 | 596.3594 | 556.863 | NaN | NaN | NaN | 669.0607 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.9127 | NaN | 20.1393
11879.1292 | 749.6947 | 634.8982 | 500.9196 | 470.67 | 471.8729 | 595.3557 | 594.7663 | 557.0134 | NaN | NaN | NaN | 647.2714 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.2389 | NaN | 19.9271
11880.1292 | 749.5674 | 634.9652 | 500.5223 | 470.5126 | 471.5347 | 593.5081 | 593.7688 | 555.2903 | NaN | NaN | NaN | 650.338 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.9634 | NaN | 19.7537
11881.1292 | 750.4351 | 634.49 | 500.4706 | 470.5609 | 471.2103 | 594.5382 | 594.1857 | 554.3621 | NaN | NaN | NaN | 656.3418 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.0786 | NaN | 21.3003
11882.1292 | 751.0004 | 634.3387 | 500.8758 | 470.4951 | 470.9356 | 595.068 | 593.8981 | 556.112 | NaN | NaN | NaN | 669.103 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.2943 | NaN | 19.998
11883.1292 | 750.9203 | 634.1274 | 500.62 | 470.2786 | 471.0309 | 595.7094 | 593.4253 | 554.728 | NaN | NaN | NaN | 657.3235 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.9753 | NaN | 18.9462
11884.1292 | 750.2987 | 634.3193 | 500.6719 | 469.7936 | 471.0377 | 596.4072 | 594.8169 | 556.0777 | NaN | NaN | NaN | 635.8985 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.0264 | NaN | 17.9267
11885.1292 | 748.7277 | 634.6342 | 500.8227 | 469.501 | 471.8602 | 599.2525 | 600.3112 | 559.3998 | NaN | NaN | NaN | 630.021 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.5057 | NaN | 21.2357
11886.1292 | 748.4521 | 634.0104 | 500.4313 | 469.8259 | 472.1836 | 599.8394 | 598.4639 | 557.3829 | NaN | NaN | NaN | 665.7967 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.4914 | NaN | 18.8017
11887.1292 | 748.4294 | 634.2234 | 499.9666 | 469.9812 | 472.2168 | 597.5115 | 597.5125 | 556.0715 | NaN | NaN | NaN | 697.2622 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.5602 | NaN | 18.4117
11888.1292 | 748.4093 | 634.4775 | 499.6249 | 470.2636 | 472.1791 | 597.993 | 598.486 | 555.4884 | NaN | NaN | NaN | 704.3069 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.8728 | NaN | 19.8667
11889.1292 | 748.3805 | 634.3094 | 499.2593 | 470.5404 | 472.1855 | 597.521 | 597.9812 | 553.9021 | NaN | NaN | NaN | 688.5355 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.2614 | NaN | 21.3358
11890.1292 | 749.8946 | 634.9422 | 498.9943 | 470.5073 | 471.856 | 595.8073 | 597.7984 | 553.1508 | NaN | NaN | NaN | 670.1895 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.1276 | NaN | 21.2568
11891.1292 | 748.3613 | 635.466 | 498.9677 | 470.3052 | 472.0179 | 598.2919 | 597.3143 | 552.466 | NaN | NaN | NaN | 650.2163 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.5669 | NaN | 20.872
11892.1292 | 747.495 | 634.4767 | 499.4494 | 470.964 | 472.7587 | 597.4898 | 594.6087 | 559.1073 | NaN | NaN | NaN | 647.712 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.4308 | NaN | 18.8302
11893.1292 | 748.192 | 634.1273 | 499.4315 | 471.8847 | 473.2457 | 597.403 | 594.5172 | 558.7137 | NaN | NaN | NaN | 649.6091 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.4035 | NaN | 20.2801
11894.1292 | 750.1416 | 634.3675 | 499.1277 | 471.5193 | 472.9186 | 595.8684 | 595.0368 | 556.4273 | NaN | NaN | NaN | 661.213 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.1406 | NaN | 20.3332
11895.1292 | 752.7283 | 634.553 | 498.5993 | 471.9186 | 472.73 | 594.1025 | 595.2422 | 556.025 | NaN | NaN | NaN | 661.7352 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.6537 | NaN | 21.9037
11896.1292 | 753.9519 | 635.5926 | 497.9541 | 471.6069 | 472.5838 | 594.4003 | 596.2779 | 555.3132 | NaN | NaN | NaN | 633.2182 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.0597 | NaN | 21.3728
11897.1292 | 753.8076 | 635.263 | 497.7885 | 471.4629 | 472.7526 | 595.3812 | 595.228 | 557.3541 | NaN | NaN | NaN | 607.9539 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.0645 | NaN | 20.8755
11898.1292 | 753.5573 | 635.3633 | 498.0222 | 471.4423 | 472.99 | 595.9038 | 594.5553 | 554.041 | NaN | NaN | NaN | 604.5758 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.7381 | NaN | 21.6832
11899.1292 | 753.9494 | 635.2233 | 497.9702 | 471.8605 | 472.6088 | 595.2795 | 595.4437 | 553.3594 | NaN | NaN | NaN | 644.1628 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.4191 | NaN | 18.1464
11900.1292 | 755.143 | 635.0496 | 498.0369 | 471.3374 | 472.3183 | 593.913 | 596.2491 | 553.0797 | NaN | NaN | NaN | 675.51 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.4549 | NaN | 19.8494
11901.1292 | 754.5375 | 634.9802 | 498.6499 | 471.4119 | 472.0367 | 591.1142 | 595.6147 | 553.8799 | NaN | NaN | NaN | 709.4945 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.6348 | NaN | 22.1438
11902.1292 | 753.3157 | 634.2279 | 498.7747 | 471.3839 | 472.3087 | 589.6028 | 595.4224 | 557.226 | NaN | NaN | NaN | 724.0616 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.2389 | NaN | 19.8476
11903.1292 | 752.0041 | 634.2278 | 498.1807 | 471.6484 | 472.3912 | 589.5984 | 595.763 | 556.9387 | NaN | NaN | NaN | 752.1942 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.7914 | NaN | 19.5968
11904.1292 | 750.6284 | 633.8022 | 497.6448 | 471.7963 | 472.9141 | 591.203 | 597.8303 | 556.887 | NaN | NaN | NaN | 753.289 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.9362 | NaN | 19.9202
11905.1292 | 748.6952 | 634.476 | 497.1519 | 471.581 | 472.8304 | 591.9126 | 597.661 | 556.225 | NaN | NaN | NaN | 762.1733 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.2975 | NaN | 20.4876
11906.1292 | 746.9176 | 633.3604 | 497.2729 | 471.3133 | 472.8079 | 590.954 | 597.7671 | 557.5649 | NaN | NaN | NaN | 776.4284 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.0568 | NaN | 20.7189
11907.1292 | 745.269 | 632.8433 | 497.4749 | 471.0582 | 472.4236 | 589.0491 | 596.6773 | 556.3661 | NaN | NaN | NaN | 775.4032 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.2282 | NaN | 18.3558
11908.1292 | 743.6092 | 632.3214 | 497.088 | 470.9969 | 472.3767 | 588.2824 | 595.8962 | 556.448 | NaN | NaN | NaN | 752.1379 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.8958 | NaN | 21.326
11909.1292 | 740.5403 | 631.5573 | 496.774 | 470.8644 | 472.1618 | 587.9692 | 595.1152 | 555.2723 | NaN | NaN | NaN | 740.651 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.1897 | NaN | 22.0433
11910.1292 | 737.0005 | 629.6425 | 497.1531 | 471.0323 | 471.9029 | 587.0829 | 592.0155 | 553.1481 | NaN | NaN | NaN | 714.7492 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.4367 | NaN | 20.0012
11911.1292 | 735.5746 | 629.5547 | 497.4429 | 471.3755 | 471.8483 | 585.0346 | 589.6451 | 550.4294 | NaN | NaN | NaN | 691.8751 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.785 | NaN | 19.7794
11912.1292 | 735.0848 | 629.5835 | 497.5596 | 471.8271 | 472.1005 | 582.9112 | 588.7614 | 549.0271 | NaN | NaN | NaN | 677.1583 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.8286 | NaN | 19.2197
11913.1292 | 733.8697 | 629.3555 | 497.9701 | 472.6545 | 472.1804 | 584.4223 | 589.2761 | 548.3055 | NaN | NaN | NaN | 710.7743 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.9519 | NaN | 18.6091
11914.1292 | 733.5058 | 628.9555 | 498.3297 | 472.9262 | 471.9238 | 584.7317 | 589.6109 | 549.3785 | NaN | NaN | NaN | 699.9653 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.3881 | NaN | 20.0846
11915.1292 | 735.4269 | 630.137 | 498.3316 | 473.812 | 471.7984 | 585.5448 | 590.1813 | 549.1907 | NaN | NaN | NaN | 672.6366 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.9151 | NaN | 19.9345
11916.1292 | 736.6137 | 629.8404 | 499.0031 | 473.7819 | 471.7045 | 584.8333 | 590.6809 | 550.5193 | NaN | NaN | NaN | 671.1556 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.2235 | NaN | 18.6498
11917.1292 | 738.2939 | 629.5136 | 498.7273 | 473.8884 | 472.0215 | 584.8247 | 590.1218 | 555.0815 | NaN | NaN | NaN | 665.1647 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.8895 | NaN | 18.3504
11918.1292 | 739.0647 | 630.1066 | 498.6764 | 473.8923 | 472.6568 | 583.8578 | 590.4925 | 555.0044 | NaN | NaN | NaN | 677.271 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.7718 | NaN | 20.9367
11919.1292 | 741.0706 | 630.3395 | 498.891 | 473.9754 | 473.7832 | 584.6404 | 590.4428 | 555.087 | NaN | NaN | NaN | 665.9068 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.7927 | NaN | 19.2344
11920.1292 | 743.0861 | 630.87 | 499.254 | 474.0757 | 473.4405 | 584.629 | 591.6428 | 555.2217 | NaN | NaN | NaN | 671.5836 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.9338 | NaN | 18.3738
11921.1292 | 744.6787 | 631.6442 | 499.2454 | 473.8567 | 472.9737 | 586.3605 | 594.0428 | 559.2737 | NaN | NaN | NaN | 656.2441 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.8458 | NaN | 19.0016
11922.1292 | 745.4078 | 631.8449 | 499.2489 | 473.0857 | 472.7611 | 587.6385 | 595.1604 | 560.1674 | NaN | NaN | NaN | 681.4851 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.3503 | NaN | 22.3561
11923.1292 | 746.5058 | 632.2534 | 499.6921 | 472.215 | 472.5192 | 586.5915 | 595.3151 | 557.7201 | NaN | NaN | NaN | 695.2442 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.3242 | NaN | 19.7398
11924.1292 | 747.2219 | 632.3303 | 499.3885 | 471.4334 | 471.9967 | 586.4012 | 595.8119 | 556.5103 | NaN | NaN | NaN | 698.0714 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.8019 | NaN | 19.7499
11925.1292 | 745.7447 | 631.3942 | 498.9261 | 470.8584 | 472.14 | 589.5288 | 594.4551 | 554.8555 | NaN | NaN | NaN | 694.6721 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.3131 | NaN | 17.1727
11926.1292 | 743.8139 | 630.8529 | 498.8786 | 470.7849 | 472.0184 | 588.4461 | 593.65 | 555.8125 | NaN | NaN | NaN | 706.5288 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.0543 | NaN | 22.2952
11927.1292 | 742.3499 | 630.4362 | 498.6041 | 471.0395 | 471.8283 | 586.2638 | 591.3656 | 554.3058 | NaN | NaN | NaN | 706.8926 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.7714 | NaN | 16.5554
11928.1292 | 741.1505 | 630.5196 | 498.4786 | 470.97 | 471.5141 | 586.752 | 589.7192 | 552.0139 | NaN | NaN | NaN | 695.8483 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.7608 | NaN | 21.0718
11929.1448 | 739.712 | 629.9876 | 498.2072 | 471.0528 | 471.2418 | 586.7549 | 588.5432 | 552.1268 | NaN | NaN | NaN | 675.3822 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.903 | NaN | 20.8135
11930.1292 | 738.8314 | 629.8453 | 497.9114 | 471.4583 | 470.7603 | 586.3456 | 588.0224 | 555.9512 | NaN | NaN | NaN | 683.7384 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.2451 | NaN | 20.1044
11931.1292 | 739.2253 | 629.6131 | 497.7394 | 471.5868 | 470.9091 | 585.3887 | 588.4725 | 555.2176 | NaN | NaN | NaN | 700.4117 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.0035 | NaN | 23.0308
11932.1292 | 739.0208 | 629.8148 | 497.6074 | 471.6828 | 471.3334 | 587.0551 | 589.6077 | 554.3011 | NaN | NaN | NaN | 716.7578 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.0469 | NaN | 21.2084
11933.1292 | 738.6141 | 629.9766 | 497.1645 | 471.6389 | 471.4945 | 588.7439 | 589.7084 | 553.8564 | NaN | NaN | NaN | 731.3186 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.1718 | NaN | 18.3829
11934.1292 | 737.6725 | 629.4764 | 497.0667 | 471.571 | 472.1844 | 588.0818 | 588.5342 | 552.676 | NaN | NaN | NaN | 725.5306 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.3679 | NaN | 21.5326
11935.1292 | 735.9631 | 628.8583 | 497.0044 | 471.1238 | 472.0642 | 585.87 | 586.3623 | 552.6944 | NaN | NaN | NaN | 747.2092 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.3032 | NaN | 18.9838
11936.1292 | 734.79 | 627.4836 | 496.195 | 471.2771 | 471.733 | 584.691 | 584.7542 | 553.1144 | NaN | NaN | NaN | 761.2742 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.9682 | NaN | 19.3568
11937.1292 | 734.0569 | 626.6982 | 496.5884 | 470.6616 | 472.0217 | 587.2878 | 584.0676 | 553.2199 | NaN | NaN | NaN | 766.5399 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.7636 | NaN | 17.9961
11938.1292 | 734.8687 | 626.9057 | 496.9654 | 470.8375 | 472.4254 | 587.6373 | 584.0411 | 556.3864 | NaN | NaN | NaN | 758.6469 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.4352 | NaN | 18.842
11939.1292 | 734.8125 | 627.2434 | 496.8312 | 470.4744 | 472.9552 | 585.8461 | 582.6506 | 553.8652 | NaN | NaN | NaN | 776.5824 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.8251 | NaN | 20.2362
11940.1292 | 734.5557 | 628.7188 | 497.0999 | 470.7291 | 472.9255 | 586.7056 | 582.8306 | 552.2915 | NaN | NaN | NaN | 729.8219 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.0694 | NaN | 21.8489
11941.1292 | 735.321 | 629.7155 | 498.2565 | 470.7828 | 472.9085 | 587.6503 | 582.187 | 551.9074 | NaN | NaN | NaN | 694.6612 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.0692 | NaN | 19.2674
11942.1292 | 736.4066 | 630.7013 | 498.9701 | 470.894 | 472.8262 | 587.2147 | 583.715 | 551.2871 | NaN | NaN | NaN | 663.7966 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.7508 | NaN | 18.4059
11943.1292 | 736.72 | 630.8511 | 499.3871 | 471.1326 | 473.0064 | 586.5854 | 583.568 | 550.6689 | NaN | NaN | NaN | 645.694 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.9623 | NaN | 19.5873
11944.1292 | 738.9099 | 631.2304 | 499.8204 | 471.1103 | 472.9844 | 587.6204 | 584.286 | 550.1731 | NaN | NaN | NaN | 620.7913 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.6626 | NaN | 19.1045
11945.1292 | 740.6036 | 631.2723 | 499.6877 | 471.2771 | 472.7538 | 587.7195 | 584.6263 | 551.3663 | NaN | NaN | NaN | 601.036 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.5225 | NaN | 18.9651
11946.1292 | 739.8156 | 631.8373 | 499.7618 | 471.7691 | 472.3621 | 589.2094 | 584.5738 | 550.0194 | NaN | NaN | NaN | 583.2972 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.1489 | NaN | 19.385
11947.1292 | 739.4169 | 630.65 | 499.9938 | 471.9921 | 471.9226 | 590.6436 | 583.4514 | 549.7661 | NaN | NaN | NaN | 598.0514 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.5304 | NaN | 16.219
11948.1292 | 738.6526 | 630.0352 | 500.0704 | 471.6733 | 471.7692 | 592.2735 | 583.9073 | 551.7084 | NaN | NaN | NaN | 608.0333 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.514 | NaN | 19.4433
11949.1292 | 737.1486 | 630.3733 | 500.1044 | 471.5978 | 471.1101 | 594.3525 | 584.422 | 549.3733 | NaN | NaN | NaN | 613.2628 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.0252 | NaN | 19.7852
11950.1292 | 735.7107 | 630.0612 | 499.9286 | 471.6995 | 471.0431 | 595.2705 | 583.6871 | 548.5155 | NaN | NaN | NaN | 647.7682 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.9445 | NaN | 20.4555
11951.1292 | 736.762 | 630.5384 | 499.6353 | 471.2031 | 470.7435 | 593.2307 | 583.4733 | 547.5217 | NaN | NaN | NaN | 660.5201 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.2103 | NaN | 18.5434
11952.1292 | 736.2089 | 631.4154 | 499.9555 | 471.1254 | 471.5406 | 592.4555 | 583.9333 | 547.1663 | NaN | NaN | NaN | 634.5914 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.2528 | NaN | 17.6444
11953.1292 | 735.5757 | 632.0631 | 500.2754 | 471.2336 | 471.6271 | 592.6836 | 583.411 | 546.4668 | NaN | NaN | NaN | 612.6567 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.2243 | NaN | 19.5935
11954.1292 | 735.6511 | 633.269 | 500.8107 | 471.9058 | 471.6766 | 592.0275 | 584.3179 | 546.9511 | NaN | NaN | NaN | 593.9143 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.9135 | NaN | 19.0157
11955.1292 | 735.7872 | 633.3059 | 501.0305 | 472.5166 | 471.744 | 591.8498 | 584.0654 | 547.4701 | NaN | NaN | NaN | 576.29 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.7674 | NaN | 18.6509
11956.1292 | 737.8552 | 633.4382 | 501.7756 | 473.1576 | 472.1475 | 591.9862 | 583.9431 | 546.2691 | NaN | NaN | NaN | 596.2003 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.8389 | NaN | 19.2006
11957.1292 | 739.7632 | 633.4593 | 502.2733 | 473.2912 | 471.734 | 592.4442 | 585.8613 | 550.6193 | NaN | NaN | NaN | 604.1007 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.4335 | NaN | 19.5897
11958.1292 | 741.6951 | 633.3818 | 502.9878 | 472.9848 | 471.1813 | 592.5847 | 586.5301 | 549.4593 | NaN | NaN | NaN | 617.5978 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.9239 | NaN | 20.5192
11959.1292 | 742.7909 | 633.4287 | 503.2545 | 473.0251 | 470.8347 | 592.8762 | 587.7281 | 549.2873 | NaN | NaN | NaN | 646.7269 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.1072 | NaN | 19.5658
11960.1292 | 741.8097 | 633.3209 | 503.1989 | 472.7315 | 470.6639 | 594.4617 | 586.6233 | 547.9717 | NaN | NaN | NaN | 681.696 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.651 | NaN | 20.7261
11961.1292 | 740.7258 | 632.2602 | 502.9333 | 472.9541 | 470.426 | 592.1 | 585.4623 | 547.5104 | NaN | NaN | NaN | 693.8168 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.0256 | NaN | 20.821
11962.1292 | 741.3401 | 632.3375 | 502.9641 | 473.2942 | 470.6876 | 591.6827 | 585.569 | 546.2872 | NaN | NaN | NaN | 689.7963 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.9263 | NaN | 20.8972
11963.1292 | 743.1469 | 632.82 | 502.4918 | 472.8694 | 470.3 | 592.5098 | 587.409 | 547.8274 | NaN | NaN | NaN | 669.9065 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.1609 | NaN | 18.8699
11964.1292 | 743.5752 | 633.3477 | 502.2 | 472.7414 | 469.4765 | 592.6767 | 589.6875 | 549.1822 | NaN | NaN | NaN | 659.3336 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.3223 | NaN | 19.1998
11965.1292 | 743.4255 | 633.7445 | 502.2962 | 472.2706 | 469.6455 | 592.5108 | 590.3706 | 547.9409 | NaN | NaN | NaN | 638.8956 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.0104 | NaN | 21.5861
11966.1292 | 742.5198 | 633.1924 | 502.4401 | 472.0157 | 469.507 | 591.8605 | 589.5423 | 546.6071 | NaN | NaN | NaN | 621.099 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.4489 | NaN | 20.7298
11967.1292 | 740.4194 | 632.6104 | 501.8237 | 471.8014 | 469.5176 | 591.6742 | 589.6136 | 546.1772 | NaN | NaN | NaN | 622.2324 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.6457 | NaN | 21.5183
11968.1292 | 738.4621 | 632.4446 | 501.3257 | 471.6015 | 469.9107 | 592.278 | 588.1815 | 557.1095 | NaN | NaN | NaN | 607.9045 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.1145 | NaN | 20.6425
11969.1292 | 737.9021 | 632.1069 | 500.8421 | 471.8468 | 470.4324 | 592.7811 | 587.2275 | 555.902 | NaN | NaN | NaN | 601.0019 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.0167 | NaN | 20.4395
11970.1292 | 737.7471 | 632.0427 | 500.9386 | 471.9077 | 470.2392 | 590.5612 | 586.7072 | 557.6478 | NaN | NaN | NaN | 607.4127 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.6084 | NaN | 18.7679
11971.1292 | 738.2107 | 631.9339 | 500.2848 | 471.7519 | 470.3413 | 588.8941 | 588.8113 | 556.753 | NaN | NaN | NaN | 609.1788 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.1397 | NaN | 19.9321
11972.1292 | 737.5347 | 631.9799 | 500.0431 | 471.4897 | 470.2879 | 590.7828 | 588.0895 | 554.7931 | NaN | NaN | NaN | 613.4992 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.8286 | NaN | 20.3167
11973.1292 | 736.9395 | 631.838 | 500.0339 | 471.6003 | 469.8993 | 591.3435 | 589.5836 | 553.2477 | NaN | NaN | NaN | 597.7664 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.9032 | NaN | 19.295
11974.1292 | 738.7877 | 631.5385 | 500.2342 | 471.8423 | 469.9912 | 590.0193 | 588.943 | 552.3296 | NaN | NaN | NaN | 596.4027 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.4593 | NaN | 19.5966
11975.1292 | 738.2339 | 632.3109 | 499.8162 | 471.56 | 470.1359 | 594.6235 | 595.0914 | 553.1619 | NaN | NaN | NaN | 599.7912 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.1871 | NaN | 21.6204
11976.1292 | 735.2556 | 631.8154 | 499.1998 | 471.6651 | 470.2182 | 594.52 | 595.1134 | 556.0818 | NaN | NaN | NaN | 619.9551 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.8875 | NaN | 19.5571
11977.1292 | 733.4993 | 631.3358 | 499.1103 | 472.0264 | 469.9643 | 593.0282 | 592.5928 | 556.0472 | NaN | NaN | NaN | 604.7079 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 3.0345 | NaN | 17.5313
11978.1292 | 732.0185 | 630.5221 | 498.6726 | 472.0104 | 469.896 | 593.6575 | 592.5379 | 556.4494 | NaN | NaN | NaN | 600.6006 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.372 | NaN | 20.2433
11979.1292 | 730.5301 | 630.2785 | 498.2373 | 472.1142 | 469.8049 | 592.1612 | 590.724 | 557.2799 | NaN | NaN | NaN | 611.498 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.0256 | NaN | 19.5821
11980.1292 | 731.0882 | 629.9916 | 497.8741 | 472.2644 | 470.0007 | 589.8051 | 589.5806 | 555.0188 | NaN | NaN | NaN | 627.4867 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.7706 | NaN | 20.3238
11981.1292 | 732.3433 | 630.0864 | 497.5683 | 472.5946 | 470.1748 | 588.5538 | 589.2618 | 553.8754 | NaN | NaN | NaN | 639.9727 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.6616 | NaN | 19.169
11982.1292 | 733.449 | 630.6385 | 497.9592 | 472.4645 | 470.1267 | 589.1445 | 588.5131 | 551.9357 | NaN | NaN | NaN | 682.7173 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.3504 | NaN | 22.7597
11983.1292 | 734.8335 | 630.7905 | 498.0219 | 472.5419 | 469.9128 | 589.0714 | 589.3194 | 551.2358 | NaN | NaN | NaN | 697.812 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.9973 | NaN | 20.4389
11984.1292 | 736.782 | 631.1779 | 497.9837 | 472.097 | 469.5786 | 589.5205 | 589.6396 | 550.8019 | NaN | NaN | NaN | 699.5827 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.2833 | NaN | 18.2282
11985.1292 | 737.1826 | 630.8344 | 497.6471 | 471.7264 | 469.9728 | 590.5211 | 589.6022 | 550.2436 | NaN | NaN | NaN | 695.3977 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.648 | NaN | 18.5193
11986.1292 | 737.0011 | 630.9764 | 497.331 | 471.4728 | 470.1116 | 589.2149 | 589.3078 | 552.5345 | NaN | NaN | NaN | 689.8128 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 11.6654 | NaN | 18.6592
11987.1292 | 738.8021 | 631.6193 | 497.1255 | 471.7813 | 469.7901 | 587.2454 | 589.1427 | 551.448 | NaN | NaN | NaN | 715.1955 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.2636 | NaN | 17.742
11988.1292 | 739.0458 | 631.9521 | 496.7341 | 472.2185 | 470.0642 | 587.4638 | 590.6639 | 550.8978 | NaN | NaN | NaN | 730.1257 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.8058 | NaN | 21.5489
11989.1292 | 738.937 | 631.9989 | 496.5739 | 472.4948 | 470.3202 | 586.5686 | 589.9166 | 550.7175 | NaN | NaN | NaN | 732.3409 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.1978 | NaN | 21.1604
11990.1292 | 739.0175 | 631.8382 | 496.5947 | 472.3693 | 470.4737 | 588.4257 | 591.4097 | 551.4038 | NaN | NaN | NaN | 694.6453 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.5721 | NaN | 18.4618
11991.1292 | 737.9097 | 632.1189 | 496.8086 | 472.0134 | 470.6059 | 588.6938 | 589.2292 | 549.2072 | NaN | NaN | NaN | 691.6556 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.7218 | NaN | 18.6683
11992.1292 | 736.6189 | 630.7135 | 496.6871 | 471.8267 | 470.7513 | 589.633 | 588.0976 | 549.0127 | NaN | NaN | NaN | 712.3195 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.5182 | NaN | 20.007
11993.1292 | 734.8568 | 630.2832 | 496.4975 | 472.0001 | 470.4877 | 587.3195 | 585.9578 | 548.0214 | NaN | NaN | NaN | 692.8506 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.1538 | NaN | 20.3797
11994.1292 | 732.7228 | 629.7409 | 496.0337 | 472.029 | 470.207 | 587.2892 | 585.563 | 546.9701 | NaN | NaN | NaN | 694.0904 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.7423 | NaN | 20.1958
11995.1292 | 731.1797 | 629.4187 | 495.7446 | 471.8892 | 470.1908 | 588.5317 | 585.486 | 548.5024 | NaN | NaN | NaN | 717.5219 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.9898 | NaN | 18.9226
11996.1292 | 730.6916 | 629.9141 | 495.5728 | 472.3554 | 469.9129 | 589.5439 | 586.0543 | 549.8747 | NaN | NaN | NaN | 712.2077 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.8979 | NaN | 14.1531
11997.1292 | 730.3208 | 629.4257 | 495.6198 | 471.8711 | 469.6349 | 588.9325 | 585.8422 | 549.1808 | NaN | NaN | NaN | 694.9896 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.0571 | NaN | 19.0608
11998.1292 | 729.6814 | 629.1832 | 495.5146 | 471.2667 | 469.342 | 587.7309 | 585.0057 | 547.8323 | NaN | NaN | NaN | 700.3393 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.3537 | NaN | 21.0002
11999.1292 | 729.8149 | 628.6258 | 495.1268 | 471.1624 | 469.0008 | 589.5336 | 584.1849 | 546.6149 | NaN | NaN | NaN | 727.1342 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.1215 | NaN | 21.1662
12000.1292 | 730.3796 | 629.142 | 494.9262 | 471.3497 | 468.7844 | 589.4203 | 584.1335 | 545.6975 | NaN | NaN | NaN | 743.8438 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.9579 | NaN | 20.6497
12001.1292 | 729.9991 | 628.7154 | 494.455 | 471.6624 | 468.598 | 588.9908 | 583.808 | 545.2683 | NaN | NaN | NaN | 749.5493 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.8165 | NaN | 22.5699
12002.1292 | 730.0293 | 628.7225 | 494.4623 | 472.1776 | 468.4473 | 588.0203 | 583.6206 | 545.2454 | NaN | NaN | NaN | 716.6913 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.9559 | NaN | 19.2332
12003.1292 | 730.299 | 628.8959 | 494.3107 | 471.9327 | 467.975 | 587.1014 | 583.9252 | 544.7357 | NaN | NaN | NaN | 723.6317 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.6612 | NaN | 17.3777
12004.1292 | 730.3043 | 628.3381 | 495.0516 | 471.7646 | 467.9468 | 586.8256 | 583.482 | 544.6686 | NaN | NaN | NaN | 697.339 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.1415 | NaN | 18.5562
12005.1292 | 729.6641 | 628.5961 | 495.3977 | 471.6491 | 468.058 | 585.3281 | 583.4563 | 544.1255 | NaN | NaN | NaN | 686.2482 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.9769 | NaN | 19.4986
12006.1292 | 729.2905 | 629.0151 | 495.2337 | 471.6086 | 468.0776 | 584.7665 | 582.9005 | 544.7815 | NaN | NaN | NaN | 670.1755 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.3676 | NaN | 19.2288
12007.1292 | 729.7701 | 628.9177 | 495.0646 | 471.9395 | 468.8146 | 584.728 | 583.7944 | 545.1364 | NaN | NaN | NaN | 685.0179 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.004 | NaN | 20.2032
12008.1292 | 730.5904 | 628.8346 | 494.8275 | 472.1957 | 469.0352 | 583.6114 | 583.6362 | 543.9378 | NaN | NaN | NaN | 654.7928 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.8702 | NaN | 19.2627
12009.1292 | 730.954 | 629.1634 | 494.5833 | 472.4274 | 468.9266 | 584.5126 | 583.522 | 543.8497 | NaN | NaN | NaN | 642.5676 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 3.9732 | NaN | 20.2461
12010.1292 | 731.2422 | 628.4864 | 494.3211 | 473.6232 | 469.606 | 586.4494 | 583.7892 | 543.2052 | NaN | NaN | NaN | 657.5828 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.1921 | NaN | 21.0691
12011.1292 | 730.9423 | 628.4894 | 494.3266 | 473.3262 | 469.715 | 585.8537 | 583.8227 | 543.0689 | NaN | NaN | NaN | 682.0964 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.0208 | NaN | 19.8799
12012.1292 | 730.1662 | 628.7174 | 494.2408 | 472.9699 | 469.518 | 587.3075 | 585.2951 | 543.1831 | NaN | NaN | NaN | 701.8821 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.9426 | NaN | 20.5748
12013.1292 | 729.8436 | 628.8598 | 493.8519 | 472.7779 | 469.8308 | 589.1159 | 586.1503 | 544.7271 | NaN | NaN | NaN | 699.7095 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.7364 | NaN | 21.0482
12014.1292 | 729.065 | 629.6033 | 493.7043 | 472.544 | 470.0351 | 591.643 | 591.2007 | 545.9571 | NaN | NaN | NaN | 682.8533 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.1952 | NaN | 19.9661
12015.1292 | 727.4724 | 630.1186 | 493.9144 | 472.7668 | 470.3849 | 594.795 | 593.5657 | 548.8841 | NaN | NaN | NaN | 685.1257 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 3.6097 | NaN | 18.0166
12016.1292 | 725.381 | 629.9958 | 494.0253 | 472.5114 | 470.3362 | 595.7292 | 594.3603 | 548.4349 | NaN | NaN | NaN | 687.0487 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.4949 | NaN | 18.9468
12017.1292 | 724.4422 | 630.0954 | 494.3297 | 472.3457 | 470.6074 | 594.9512 | 593.4451 | 547.2618 | NaN | NaN | NaN | 700.942 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.8313 | NaN | 15.6676
12018.1292 | 722.939 | 629.3067 | 494.1856 | 472.8908 | 470.4767 | 594.3019 | 591.849 | 546.4245 | NaN | NaN | NaN | 718.3912 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.8242 | NaN | 19.7821
12019.1292 | 721.9727 | 628.6275 | 493.9744 | 472.9735 | 470.6163 | 592.7089 | 589.8787 | 547.3482 | NaN | NaN | NaN | 714.2105 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.4014 | NaN | 21.2825
12020.1292 | 721.115 | 628.2402 | 493.9189 | 473.0016 | 470.5546 | 592.4699 | 588.6154 | 545.1637 | NaN | NaN | NaN | 720.7668 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.1542 | NaN | 20.373
12021.1292 | 721.0478 | 627.9648 | 495.066 | 473.2287 | 470.4357 | 592.5987 | 589.9568 | 544.7696 | NaN | NaN | NaN | 729.3529 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.3862 | NaN | 21.1691
12022.1292 | 720.7017 | 627.7035 | 495.2049 | 472.8871 | 469.9928 | 592.5042 | 588.4741 | 545.4 | NaN | NaN | NaN | 710.4327 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.053 | NaN | 18.6644
12023.1292 | 720.7076 | 627.6237 | 495.3918 | 472.6575 | 469.9755 | 592.3365 | 586.9166 | 544.1209 | NaN | NaN | NaN | 680.458 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.0894 | NaN | 20.0189
12024.1292 | 721.2961 | 628.1679 | 495.8996 | 473.0795 | 469.3865 | 592.084 | 586.2637 | 543.0702 | NaN | NaN | NaN | 660.8729 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.5602 | NaN | 20.3865
12025.1292 | 722.0237 | 628.5888 | 495.8781 | 472.9665 | 469.6364 | 593.5729 | 583.9077 | 542.1734 | NaN | NaN | NaN | 637.9238 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.3232 | NaN | 21.549
12026.1292 | 722.3292 | 628.3113 | 496.0601 | 473.2429 | 469.9782 | 593.4003 | 583.2773 | 541.1775 | NaN | NaN | NaN | 620.4953 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.9332 | NaN | 19.5984
12027.1292 | 721.7766 | 627.6987 | 496.2452 | 473.5124 | 470.0327 | 593.0995 | 582.3163 | 540.9584 | NaN | NaN | NaN | 635.6589 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.4051 | NaN | 22.0303
12028.1292 | 722.2828 | 628.3336 | 496.9112 | 473.6018 | 469.7901 | 592.9721 | 581.3609 | 540.993 | NaN | NaN | NaN | 648.5942 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.2093 | NaN | 19.4473
12029.1292 | 724.794 | 629.5737 | 497.153 | 473.1504 | 470.1875 | 592.8078 | 581.1199 | 541.651 | NaN | NaN | NaN | 659.3661 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.1949 | NaN | 20.1352
12030.1292 | 728.0045 | 630.2559 | 497.3222 | 473.7261 | 470.4572 | 593.1445 | 582.6179 | 541.7736 | NaN | NaN | NaN | 690.0571 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.3179 | NaN | 18.5279
12031.1292 | 728.2661 | 629.7634 | 497.8789 | 474.0612 | 470.4818 | 591.5456 | 582.7966 | 541.9425 | NaN | NaN | NaN | 711.0309 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.985 | NaN | 21.4118
12032.1292 | 727.0263 | 629.6864 | 498.275 | 474.6473 | 470.8339 | 591.5416 | 582.3595 | 542.3985 | NaN | NaN | NaN | 746.3645 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 3.8443 | NaN | 19.3689
12033.1292 | 726.8911 | 628.9475 | 498.6928 | 474.6474 | 471.3175 | 592.1835 | 581.8776 | 541.5945 | NaN | NaN | NaN | 734.4584 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.2902 | NaN | 20.7666
12034.1292 | 725.4491 | 628.9505 | 498.1998 | 474.669 | 471.5598 | 591.1405 | 582.2651 | 539.6732 | NaN | NaN | NaN | 698.1555 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.9044 | NaN | 19.3795
12035.1292 | 723.1633 | 629.3853 | 498.4434 | 474.7215 | 471.538 | 592.7 | 581.4114 | 538.2477 | NaN | NaN | NaN | 669.5578 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.4843 | NaN | 18.5038
12036.1292 | 721.7307 | 628.6559 | 499.7469 | 475.6446 | 471.486 | 594.1589 | 579.1646 | 542.8599 | NaN | NaN | NaN | 654.1464 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.5601 | NaN | 18.6402
12037.1292 | 722.78 | 628.3138 | 500.1281 | 476.3173 | 471.2461 | 593.6905 | 578.9645 | 541.7652 | NaN | NaN | NaN | 636.9025 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.4049 | NaN | 18.8576
12038.1292 | 723.0557 | 628.6048 | 500.2307 | 475.8356 | 470.9265 | 595.076 | 584.5547 | 542.7315 | NaN | NaN | NaN | 666.7082 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.9372 | NaN | 20.4995
12039.1292 | 722.2578 | 628.428 | 500.8354 | 475.8062 | 470.6581 | 595.0277 | 585.5599 | 542.7968 | NaN | NaN | NaN | 683.8008 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 2.7894 | NaN | 17.173
12040.1292 | 722.5302 | 628.8119 | 500.3318 | 476.257 | 470.312 | 593.7865 | 585.0995 | 541.7368 | NaN | NaN | NaN | 691.243 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.6843 | NaN | 17.8147
12041.1292 | 722.3422 | 628.9707 | 499.9183 | 476.4175 | 471.0656 | 593.4675 | 586.2014 | 543.7425 | NaN | NaN | NaN | 685.7143 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.1419 | NaN | 21.1106
12042.1292 | 723.5432 | 629.0729 | 499.2141 | 476.7191 | 471.0245 | 594.3258 | 585.8092 | 542.8752 | NaN | NaN | NaN | 702.9049 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.5032 | NaN | 19.0331
12043.1292 | 725.1487 | 629.8701 | 498.365 | 476.8668 | 470.4701 | 595.1588 | 585.8979 | 542.3877 | NaN | NaN | NaN | 708.602 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.8054 | NaN | 21.981
12044.1292 | 724.9686 | 628.7582 | 498.2606 | 476.8125 | 470.5379 | 595.9414 | 586.6138 | 542.8712 | NaN | NaN | NaN | 692.5499 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.7858 | NaN | 17.4741
12045.1292 | 724.1356 | 628.8292 | 498.1054 | 476.1557 | 470.2448 | 595.5285 | 586.2865 | 542.5315 | NaN | NaN | NaN | 707.3453 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.2285 | NaN | 21.2814
12046.1292 | 725.1706 | 628.5284 | 497.6797 | 475.8787 | 470.0065 | 594.0824 | 584.9941 | 542.6536 | NaN | NaN | NaN | 721.6373 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.3509 | NaN | 18.5089
12047.1292 | 727.8005 | 629.5972 | 497.2087 | 475.7142 | 469.7187 | 592.0113 | 584.8855 | 541.2801 | NaN | NaN | NaN | 730.1316 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.9725 | NaN | 17.3597
12048.1292 | 729.6815 | 631.6562 | 497.2773 | 476.4 | 469.9587 | 593.96 | 588.1644 | 541.5769 | NaN | NaN | NaN | 754.9401 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.7027 | NaN | 20.2504
12049.1292 | 731.1474 | 632.5384 | 497.434 | 476.4909 | 470.5158 | 594.5965 | 589.9921 | 544.8925 | NaN | NaN | NaN | 728.2596 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.7612 | NaN | 20.0115
12050.1292 | 732.795 | 632.3612 | 497.3669 | 476.0025 | 471.1328 | 594.3054 | 590.1066 | 549.2046 | NaN | NaN | NaN | 721.9333 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.2714 | NaN | 18.7454
12051.1292 | 734.8665 | 632.1968 | 497.113 | 476.1521 | 471.26 | 593.4468 | 592.9958 | 552.0601 | NaN | NaN | NaN | 733.1916 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.3038 | NaN | 18.4498
12052.1292 | 738.7923 | 632.9319 | 497.0806 | 476.0543 | 471.3079 | 591.4243 | 592.8621 | 551.8018 | NaN | NaN | NaN | 740.4699 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.9902 | NaN | 20.846
12053.1292 | 740.5163 | 632.9432 | 497.2399 | 475.9778 | 471.5812 | 591.726 | 592.8554 | 552.151 | NaN | NaN | NaN | 757.8011 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.486 | NaN | 22.47
12054.1292 | 740.5142 | 633.3605 | 496.8706 | 476.0188 | 471.582 | 593.3794 | 592.456 | 550.852 | NaN | NaN | NaN | 746.023 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.4305 | NaN | 20.741
12055.1292 | 740.5448 | 634.0429 | 496.8401 | 476.2519 | 471.6888 | 594.5503 | 591.9623 | 549.6798 | NaN | NaN | NaN | 731.7398 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.8591 | NaN | 19.7382
12056.1292 | 742.3684 | 633.7918 | 497.0504 | 476.6619 | 471.7489 | 596.5451 | 593.9036 | 552.0514 | NaN | NaN | NaN | 712.3001 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.6424 | NaN | 18.9116
12057.1292 | 743.3998 | 633.8108 | 497.5642 | 476.8333 | 471.8656 | 596.6157 | 594.3279 | 551.7889 | NaN | NaN | NaN | 730.2916 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.0003 | NaN | 20.1324
12058.1292 | 743.4484 | 633.9933 | 497.2779 | 477.0754 | 472.2845 | 595.1623 | 593.4214 | 550.7904 | NaN | NaN | NaN | 728.2802 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.494 | NaN | 19.3371
12059.1292 | 742.6626 | 634.0283 | 497.0821 | 477.8957 | 472.0075 | 595.5359 | 593.6985 | 549.9904 | NaN | NaN | NaN | 700.676 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.0117 | NaN | 19.1076
12060.1292 | 740.9376 | 633.8139 | 496.722 | 477.9294 | 471.9066 | 599.2316 | 594.9606 | 551.3365 | NaN | NaN | NaN | 668.0995 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.4739 | NaN | 20.8708
12061.1292 | 739.4107 | 633.5997 | 496.5324 | 478.0879 | 472.1506 | 599.4962 | 597.0878 | 552.5205 | NaN | NaN | NaN | 654.0972 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.0996 | NaN | 18.0661
12062.1292 | 737.7478 | 633.5651 | 496.6763 | 478.3404 | 471.9901 | 599.3565 | 598.1203 | 556.2211 | NaN | NaN | NaN | 681.7141 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.9482 | NaN | 17.7213
12063.1292 | 737.5616 | 634.6948 | 496.5833 | 478.2167 | 471.9693 | 596.9333 | 598.6086 | 554.3272 | NaN | NaN | NaN | 713.4017 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 3.3577 | NaN | 20.981
12064.1292 | 738.8593 | 635.7475 | 497.0439 | 478.0457 | 472.3688 | 597.3449 | 600.4337 | 555.2271 | NaN | NaN | NaN | 752.3822 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.8764 | NaN | 19.3311
12065.1292 | 739.8832 | 636.1047 | 497.7555 | 478.1306 | 473.0908 | 599.3352 | 600.981 | 556.072 | NaN | NaN | NaN | 761.6885 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.0071 | NaN | 21.0206
12066.1292 | 740.0361 | 635.4312 | 497.4934 | 477.6544 | 472.816 | 599.7002 | 601.5832 | 556.3596 | NaN | NaN | NaN | 772.8936 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.8046 | NaN | 19.5718
12067.1292 | 739.3917 | 635.4167 | 497.0799 | 477.5921 | 472.6455 | 598.8959 | 601.3113 | 554.474 | NaN | NaN | NaN | 784.2594 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.2202 | NaN | 19.2435
12068.1292 | 739.4194 | 635.015 | 496.7554 | 477.8542 | 472.6825 | 598.0215 | 599.8407 | 554.0726 | NaN | NaN | NaN | 800.2505 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.4885 | NaN | 21.1837
12069.1292 | 741.1279 | 636.9822 | 496.8693 | 478.1717 | 472.6489 | 599.7816 | 602.0096 | 553.809 | NaN | NaN | NaN | 806.6815 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.8372 | NaN | 19.1015
12070.1292 | 743.2518 | 637.4391 | 497.2719 | 479.1388 | 473.1834 | 597.74 | 601.996 | 555.2418 | NaN | NaN | NaN | 828.3626 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.2619 | NaN | 18.402
12071.1292 | 742.9779 | 636.7903 | 497.7087 | 479.3846 | 473.5434 | 596.7914 | 600.2188 | 554.7143 | NaN | NaN | NaN | 830.0963 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.5262 | NaN | 17.8494
12072.1292 | 743.1161 | 636.3044 | 497.6037 | 479.0676 | 473.8224 | 597.066 | 600.9231 | 553.2289 | NaN | NaN | NaN | 834.4165 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.4919 | NaN | 18.9259
12073.1292 | 743.8784 | 636.2801 | 497.488 | 478.8416 | 473.6503 | 596.013 | 601.764 | 552.7888 | NaN | NaN | NaN | 815.1295 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.2472 | NaN | 20.5449
12074.1292 | 746.3641 | 636.5732 | 497.526 | 478.6882 | 473.2717 | 593.9672 | 601.4833 | 552.7997 | NaN | NaN | NaN | 778.2319 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.8477 | NaN | 17.9036
12075.1292 | 746.996 | 636.518 | 497.2746 | 478.5304 | 473.0141 | 598.0825 | 604.251 | 553.5417 | NaN | NaN | NaN | 785.6546 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.5845 | NaN | 18.8789
12076.1292 | 746.9798 | 635.9367 | 497.0641 | 478.2839 | 473.0149 | 597.0886 | 603.3327 | 552.0434 | NaN | NaN | NaN | 802.3957 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.3858 | NaN | 21.4907
12077.1292 | 747.1322 | 636.3484 | 496.4156 | 478.6501 | 473.1446 | 595.3043 | 603.0295 | 551.5869 | NaN | NaN | NaN | 819.299 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.6413 | NaN | 19.6854
12078.1292 | 747.6027 | 638.2068 | 497.0641 | 479.5577 | 473.5413 | 594.1039 | 602.275 | 552.7891 | NaN | NaN | NaN | 772.4149 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.5843 | NaN | 20.1875
12079.1292 | 745.9515 | 640.1183 | 498.7157 | 481.2509 | 474.8809 | 595.9045 | 604.0381 | 553.6663 | NaN | NaN | NaN | 727.7603 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.5714 | NaN | 19.976
12080.1292 | 742.9117 | 638.3004 | 499.7154 | 482.0832 | 475.8918 | 595.6054 | 601.9469 | 555.1847 | NaN | NaN | NaN | 698.6947 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.1825 | NaN | 19.4898
12081.1292 | 741.147 | 638.4507 | 500.1239 | 482.4872 | 476.2186 | 596.0096 | 600.7504 | 552.5174 | NaN | NaN | NaN | 670.3777 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.2116 | NaN | 19.8062
12082.1292 | 739.9508 | 637.6634 | 500.1407 | 483.2596 | 475.9479 | 597.5234 | 600.0916 | 552.0833 | NaN | NaN | NaN | 670.6338 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.1258 | NaN | 20.7264
12083.1292 | 740.2771 | 637.175 | 500.0395 | 483.0644 | 475.4232 | 597.7338 | 598.5152 | 550.0641 | NaN | NaN | NaN | 684.9233 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.4365 | NaN | 18.1714
12084.1292 | 741.5321 | 637.5238 | 500.3692 | 482.8463 | 474.9622 | 600.8864 | 599.5117 | 550.2132 | NaN | NaN | NaN | 683.7575 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.167 | NaN | 20.1399
12085.1292 | 741.7378 | 637.9358 | 500.33 | 483.1473 | 474.5824 | 600.6432 | 599.9401 | 549.9936 | NaN | NaN | NaN | 673.0892 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.7911 | NaN | 21.0361
12086.1292 | 741.2933 | 637.8701 | 500.509 | 483.2164 | 474.4183 | 602.7205 | 600.1945 | 550.6038 | NaN | NaN | NaN | 690.3972 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.4079 | NaN | 20.6374
12087.1292 | 740.7472 | 637.3814 | 500.1738 | 483.0405 | 474.6301 | 602.6155 | 599.5713 | 549.738 | NaN | NaN | NaN | 670.6672 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.8968 | NaN | 19.2675
12088.1292 | 740.2987 | 636.5588 | 500.3701 | 482.678 | 475.0011 | 602.2036 | 598.3551 | 548.7938 | NaN | NaN | NaN | 667.2031 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.2631 | NaN | 20.3755
12089.1292 | 739.1246 | 636.7173 | 500.2571 | 481.9223 | 474.6144 | 604.3828 | 600.3618 | 549.4519 | NaN | NaN | NaN | 688.5844 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.0456 | NaN | 20.4831
12090.1292 | 738.7567 | 636.6856 | 500.017 | 481.339 | 474.5586 | 606.011 | 601.1305 | 549.6386 | NaN | NaN | NaN | 687.7763 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.2391 | NaN | 19.3978
12091.1292 | 738.4384 | 636.4281 | 499.822 | 481.1619 | 474.7648 | 603.3992 | 599.6135 | 548.7951 | NaN | NaN | NaN | 658.8921 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.2346 | NaN | 19.1696
12092.1292 | 739.2462 | 636.9467 | 499.5968 | 481.37 | 474.7556 | 604.4727 | 598.7592 | 547.2761 | NaN | NaN | NaN | 629.2339 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.6774 | NaN | 21.3211
12093.1292 | 740.4799 | 637.6125 | 499.5354 | 481.0957 | 474.4833 | 604.4861 | 598.8147 | 546.7122 | NaN | NaN | NaN | 617.6388 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.1756 | NaN | 19.504
12094.1292 | 740.7371 | 637.7677 | 499.5372 | 480.9276 | 474.6824 | 604.0269 | 598.3929 | 546.6207 | NaN | NaN | NaN | 600.9538 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.222 | NaN | 20.402
12095.1292 | 740.3625 | 637.7947 | 499.5827 | 481.3909 | 474.686 | 604.5614 | 599.4988 | 547.6285 | NaN | NaN | NaN | 581.5392 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.9739 | NaN | 19.8051
12096.1292 | 739.2659 | 638.1547 | 500.0723 | 481.7182 | 475.1006 | 604.8852 | 598.7208 | 548.273 | NaN | NaN | NaN | 580.8531 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.2276 | NaN | 20.0783
12097.1292 | 737.1165 | 638.6137 | 501.1539 | 482.4657 | 475.5388 | 606.2875 | 597.7343 | 547.7458 | NaN | NaN | NaN | 601.2882 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.0246 | NaN | 19.095
12098.1292 | 734.847 | 638.7399 | 503.02 | 482.4932 | 475.6615 | 607.0463 | 596.6071 | 546.5621 | NaN | NaN | NaN | 591.4642 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 3.3171 | NaN | 20.0866
12099.1292 | 733.5949 | 638.2579 | 504.0391 | 482.261 | 476.4875 | 605.5174 | 594.8565 | 545.1607 | NaN | NaN | NaN | 600.5496 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 1.8866 | NaN | 16.3534
12100.1292 | 733.1523 | 637.326 | 504.9673 | 482.2712 | 477.029 | 603.8747 | 594.8044 | 545.1989 | NaN | NaN | NaN | 597.7854 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.1282 | NaN | 19.3785
12101.1292 | 733.4714 | 637.9628 | 505.652 | 482.0079 | 477.1944 | 604.0104 | 596.0597 | 546.1793 | NaN | NaN | NaN | 579.1042 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.4188 | NaN | 19.604
12102.1292 | 733.898 | 638.4431 | 506.3975 | 482.7307 | 476.4977 | 605.5321 | 596.5067 | 545.5673 | NaN | NaN | NaN | 568.6876 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.2844 | NaN | 19.4467
12103.1292 | 735.1027 | 637.7024 | 507.3096 | 482.936 | 475.875 | 605.5959 | 596.39 | 546.0625 | NaN | NaN | NaN | 569.0105 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.4169 | NaN | 19.6927
12104.1292 | 737.0681 | 637.3235 | 507.2223 | 483.2194 | 475.196 | 605.3124 | 596.3598 | 546.1837 | NaN | NaN | NaN | 568.924 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.8388 | NaN | 19.344
12105.1292 | 737.0566 | 637.2496 | 506.9235 | 483.8107 | 474.6235 | 605.3826 | 595.3381 | 544.5777 | NaN | NaN | NaN | 563.9241 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.1611 | NaN | 21.044
12106.1292 | 737.3674 | 636.9873 | 506.835 | 484.3652 | 474.3591 | 604.7617 | 593.7976 | 544.312 | NaN | NaN | NaN | 625.0183 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.5772 | NaN | 19.0706
12107.1292 | 737.7821 | 638.3008 | 506.2605 | 484.9813 | 474.7031 | 603.3229 | 593.1354 | 543.5257 | NaN | NaN | NaN | 644.7997 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.3839 | NaN | 20.9597
12108.1292 | 739.5126 | 638.9529 | 506.2907 | 484.7547 | 475.2134 | 602.7306 | 593.4532 | 543.7425 | NaN | NaN | NaN | 618.2421 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.4954 | NaN | 20.396
12109.1448 | 740.6712 | 638.5283 | 506.147 | 484.1859 | 475.3489 | 601.8339 | 593.7025 | 543.0535 | NaN | NaN | NaN | 601.5955 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 2.967 | NaN | 17.5349
12110.1292 | 741.1084 | 637.8552 | 505.8091 | 483.8738 | 475.7534 | 600.806 | 594.1379 | 543.6181 | NaN | NaN | NaN | 628.0723 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.0362 | NaN | 20.0025
12111.1292 | 743.1695 | 636.9082 | 505.3138 | 483.1684 | 475.597 | 598.7642 | 593.1733 | 543.9786 | NaN | NaN | NaN | 658.565 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.2303 | NaN | 19.5116
12112.1292 | 744.1794 | 636.6952 | 504.9276 | 482.359 | 475.8038 | 597.7715 | 592.7031 | 544.7566 | NaN | NaN | NaN | 685.6177 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.9689 | NaN | 19.7755
12113.1292 | 744.3582 | 636.5707 | 504.689 | 482.4945 | 475.6333 | 597.8452 | 592.9227 | 544.7431 | NaN | NaN | NaN | 668.4749 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.946 | NaN | 18.7153
12114.1292 | 743.5523 | 636.4379 | 504.0289 | 482.0811 | 475.5955 | 598.2784 | 592.5826 | 548.2752 | NaN | NaN | NaN | 673.1957 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.4349 | NaN | 19.535
12115.1292 | 742.1791 | 635.4751 | 503.5478 | 482.0492 | 476.4685 | 599.3599 | 592.1382 | 546.7244 | NaN | NaN | NaN | 662.4492 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.7431 | NaN | 21.0407
12116.1292 | 741.7439 | 635.5175 | 503.6823 | 482.6253 | 476.2605 | 601.0981 | 591.7911 | 546.9126 | NaN | NaN | NaN | 676.1202 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.6783 | NaN | 19.4456
12117.1292 | 744.8614 | 636.5874 | 503.5177 | 483.0117 | 475.8373 | 599.5886 | 592.2852 | 546.0292 | NaN | NaN | NaN | 706.8156 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.5671 | NaN | 21.0539
12118.1292 | 748.2743 | 636.8792 | 503.5358 | 482.9017 | 476.7396 | 598.0435 | 592.0366 | 545.8408 | NaN | NaN | NaN | 722.8645 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.0693 | NaN | 16.9754
12119.1292 | 750.1751 | 636.4858 | 504.3894 | 483.1364 | 477.8142 | 597.5963 | 592.4223 | 544.8307 | NaN | NaN | NaN | 737.2613 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.1515 | NaN | 18.3643
12120.1292 | 751.0426 | 636.1602 | 503.9522 | 483.0386 | 477.9514 | 595.3021 | 593.731 | 544.685 | NaN | NaN | NaN | 746.9637 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 2.9599 | NaN | 17.8011
12121.1292 | 753.0435 | 636.3265 | 503.2371 | 483.0336 | 477.7859 | 594.1403 | 594.2864 | 544.9176 | NaN | NaN | NaN | 764.0649 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.6301 | NaN | 20.2808
12122.1292 | 753.9114 | 635.9539 | 502.7811 | 483.0653 | 477.9105 | 591.9542 | 594.6101 | 547.3753 | NaN | NaN | NaN | 742.3651 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.3189 | NaN | 18.588
12123.1292 | 753.8291 | 635.2684 | 502.2662 | 483.3947 | 477.7988 | 590.4945 | 594.5266 | 548.6817 | NaN | NaN | NaN | 734.4871 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.832 | NaN | 17.7052
12124.1292 | 751.7942 | 634.9401 | 502.6869 | 483.1409 | 477.4887 | 588.3723 | 595.8984 | 549.5985 | NaN | NaN | NaN | 740.874 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.7051 | NaN | 18.8911
12125.1292 | 751.808 | 635.3444 | 502.6029 | 482.7823 | 477.2982 | 585.3619 | 595.6428 | 549.2926 | NaN | NaN | NaN | 758.1883 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 3.4096 | NaN | 18.5737
12126.1292 | 750.8774 | 635.4435 | 502.1046 | 483.0436 | 476.9615 | 585.9516 | 596.5708 | 549.0607 | NaN | NaN | NaN | 745.7625 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 2.8592 | NaN | 17.354
12127.1292 | 749.2561 | 635.3862 | 501.6201 | 483.0176 | 476.3991 | 588.783 | 598.5289 | 548.9941 | NaN | NaN | NaN | 736.5397 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.1674 | NaN | 14.6801
12128.1292 | 747.1485 | 634.9564 | 501.3755 | 483.2169 | 476.37 | 588.2312 | 600.4502 | 549.1742 | NaN | NaN | NaN | 754.6075 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.7196 | NaN | 18.5478
12129.1292 | 744.8221 | 634.3945 | 501.2803 | 483.361 | 476.5456 | 586.1725 | 598.8849 | 547.086 | NaN | NaN | NaN | 771.9536 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.1165 | NaN | 21.082
12130.1292 | 743.2036 | 633.5747 | 500.9838 | 483.3082 | 476.4399 | 584.493 | 597.3779 | 546.8757 | NaN | NaN | NaN | 780.2204 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.0437 | NaN | 22.8406
12131.1292 | 741.675 | 632.7248 | 501.1666 | 483.09 | 476.455 | 586.1732 | 597.5192 | 547.6776 | NaN | NaN | NaN | 771.5684 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 3.7137 | NaN | 21.616
12132.1292 | 740.8214 | 632.3457 | 500.9586 | 482.7507 | 476.3377 | 584.9579 | 595.9311 | 547.4972 | NaN | NaN | NaN | 762.099 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 3.6324 | NaN | 19.5723
12133.1292 | 739.5236 | 632.1751 | 500.5923 | 482.8952 | 476.0222 | 584.5878 | 594.3572 | 546.7726 | NaN | NaN | NaN | 724.5103 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.1695 | NaN | 20.2611
12134.1292 | 740.2111 | 632.0074 | 500.7882 | 482.739 | 475.8015 | 584.0433 | 594.5995 | 547.2661 | NaN | NaN | NaN | 716.4038 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.0527 | NaN | 21.4933
12135.1292 | 741.0512 | 632.8162 | 501.3695 | 482.946 | 475.7632 | 585.4497 | 596.0032 | 547.445 | NaN | NaN | NaN | 740.6593 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.6653 | NaN | 21.9616
12136.1292 | 741.8321 | 632.9197 | 501.4951 | 483.0938 | 476.2445 | 587.2438 | 598.0075 | 548.4572 | NaN | NaN | NaN | 718.605 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.8423 | NaN | 20.1639
12137.1292 | 743.2301 | 633.1602 | 501.1974 | 482.9748 | 476.0231 | 587.9006 | 598.0157 | 549.7624 | NaN | NaN | NaN | 722.778 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.3847 | NaN | 20.8269
12138.1292 | 745.3609 | 634.1667 | 500.8042 | 482.6142 | 476.0238 | 587.7803 | 599.2501 | 550.9913 | NaN | NaN | NaN | 714.8999 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.9922 | NaN | 20.2732
12139.1292 | 746.8262 | 634.4309 | 500.8677 | 482.5588 | 475.8865 | 590.7032 | 600.2642 | 551.3581 | NaN | NaN | NaN | 731.2644 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.1266 | NaN | 18.9071
12140.1292 | 745.6622 | 634.4705 | 500.7538 | 482.3923 | 475.6279 | 592.0587 | 599.5726 | 549.7601 | NaN | NaN | NaN | 708.1328 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.4677 | NaN | 18.7943
12141.1292 | 746.8135 | 634.3723 | 500.5244 | 482.3238 | 475.5955 | 590.6865 | 597.2396 | 546.8608 | NaN | NaN | NaN | 707.217 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.5327 | NaN | 18.9621
12142.1292 | 745.8641 | 633.7265 | 500.8493 | 482.2783 | 475.3405 | 592.3042 | 596.3626 | 545.1375 | NaN | NaN | NaN | 677.0115 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.1745 | NaN | 18.7138
12143.1292 | 744.3559 | 636.4725 | 502.0942 | 482.5174 | 475.5851 | 594.2764 | 599.0511 | 544.7698 | NaN | NaN | NaN | 671.7485 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.3152 | NaN | 17.9632
12144.1292 | 742.9492 | 635.9717 | 503.0625 | 482.9538 | 475.8011 | 592.1705 | 596.84 | 543.8493 | NaN | NaN | NaN | 676.45 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 3.1775 | NaN | 18.317
12145.1292 | 742.4679 | 635.2002 | 503.8871 | 483.5949 | 476.5305 | 591.8707 | 597.3085 | 548.2314 | NaN | NaN | NaN | 650.8696 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 3.3631 | NaN | 19.3976
12146.1292 | 743.4981 | 634.8593 | 503.824 | 483.7829 | 476.3087 | 591.1674 | 597.909 | 547.7034 | NaN | NaN | NaN | 624.1879 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 3.2755 | NaN | 20.5516
12147.1292 | 745.4158 | 634.9159 | 503.549 | 483.0859 | 475.9935 | 590.4455 | 598.6021 | 549.6373 | NaN | NaN | NaN | 635.754 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 3.6999 | NaN | 20.5355
12148.1292 | 747.5454 | 635.2304 | 503.8384 | 482.6546 | 476.2813 | 589.4305 | 599.0144 | 551.7886 | NaN | NaN | NaN | 610.6711 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 3.5067 | NaN | 19.5144
12149.1292 | 750.2587 | 636.3341 | 503.848 | 482.9415 | 476.3941 | 587.6556 | 599.3278 | 553.4257 | NaN | NaN | NaN | 611.2355 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 2.2923 | NaN | 20.2268
12150.1292 | 751.5172 | 637.4041 | 504.5032 | 482.8437 | 476.8455 | 588.9748 | 600.3225 | 553.2766 | NaN | NaN | NaN | 596.7787 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 3.3124 | NaN | 19.2782
12151.1292 | 749.6436 | 637.8018 | 504.6052 | 483.3104 | 477.2202 | 590.1825 | 599.9655 | 552.5687 | NaN | NaN | NaN | 579.197 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.3537 | NaN | 17.2602
12152.1292 | 747.67 | 636.246 | 505.361 | 484.0416 | 478.1207 | 590.2285 | 597.6613 | 550.4472 | NaN | NaN | NaN | 592.0288 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 1.8099 | NaN | 21.4467
12153.1292 | 746.989 | 635.7725 | 505.7397 | 484.7663 | 478.9682 | 590.6554 | 596.4017 | 549.0287 | NaN | NaN | NaN | 578.2241 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 2.7876 | NaN | 20.6817
12154.1292 | 747.3231 | 636.4946 | 506.1912 | 484.7422 | 478.9258 | 591.3556 | 596.269 | 549.9092 | NaN | NaN | NaN | 568.5207 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.4712 | NaN | 18.8139
12155.1292 | 748.841 | 636.5614 | 506.205 | 484.4263 | 478.3673 | 590.2278 | 596.9697 | 553.1642 | NaN | NaN | NaN | 570.9634 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 3.299 | NaN | 18.9467
12156.1292 | 748.1457 | 636.4313 | 506.3449 | 484.3651 | 477.5333 | 592.8092 | 595.8197 | 552.2021 | NaN | NaN | NaN | 552.191 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 3.4877 | NaN | 19.6649
12157.1292 | 746.556 | 635.7408 | 507.1395 | 484.7603 | 477.3954 | 593.6214 | 594.9124 | 550.9107 | NaN | NaN | NaN | 562.0202 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 3.7528 | NaN | 18.719
12158.1292 | 746.3837 | 635.577 | 507.7981 | 485.1182 | 476.8066 | 593.3247 | 594.5974 | 549.5285 | NaN | NaN | NaN | 552.9433 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.1491 | NaN | 20.3269
12159.1292 | 745.5687 | 635.5828 | 507.3017 | 485.4191 | 476.5333 | 591.9194 | 593.4564 | 548.4447 | NaN | NaN | NaN | 540.0087 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.2387 | NaN | 19.8872
12160.1292 | 743.7648 | 636.9277 | 507.0759 | 484.8419 | 476.6456 | 594.4507 | 593.6638 | 548.2969 | NaN | NaN | NaN | 527.2899 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 3.8564 | NaN | 19.3598
12161.1292 | 742.2456 | 636.7328 | 506.9973 | 485.1841 | 477.7677 | 595.7606 | 592.8893 | 546.9985 | NaN | NaN | NaN | 553.6031 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 3.3129 | NaN | 18.497
12162.1292 | 740.4734 | 637.5994 | 507.9504 | 486.2189 | 478.7591 | 599.2796 | 593.6002 | 546.8871 | NaN | NaN | NaN | 558.1723 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.4015 | NaN | 19.2704
12163.1292 | 739.4388 | 640.1302 | 509.519 | 488.3299 | 479.3196 | 600.0842 | 593.5081 | 546.3725 | NaN | NaN | NaN | 541.0316 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.9414 | NaN | 19.3669
12164.1292 | 739.0428 | 641.2208 | 509.972 | 488.9084 | 480.666 | 599.2518 | 593.9981 | 546.1564 | NaN | NaN | NaN | 527.7773 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.4533 | NaN | 19.4985
12165.1292 | 737.6977 | 639.6083 | 511.1166 | 490.1623 | 481.0639 | 598.8015 | 592.6903 | 545.0571 | NaN | NaN | NaN | 516.9591 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.3391 | NaN | 20.1883
12166.1292 | 735.792 | 639.5117 | 512.4648 | 491.3407 | 481.6325 | 598.7522 | 591.9585 | 543.8469 | NaN | NaN | NaN | 535.8321 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.7624 | NaN | 20.2121
12167.1292 | 734.777 | 638.7694 | 512.6311 | 491.2725 | 481.8192 | 599.2882 | 590.1204 | 543.2307 | NaN | NaN | NaN | 521.5382 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.871 | NaN | 20.2783
12168.1292 | 732.9681 | 638.0422 | 512.7556 | 491.254 | 481.9064 | 599.4523 | 589.8821 | 543.095 | NaN | NaN | NaN | 515.3107 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.0549 | NaN | 19.9501
12169.1292 | 731.0019 | 638.3818 | 513.6598 | 491.1792 | 482.301 | 601.554 | 591.2418 | 543.2248 | NaN | NaN | NaN | 539.3437 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.8853 | NaN | 19.4273
12170.1292 | 729.4817 | 639.912 | 515.601 | 491.1053 | 482.6625 | 603.326 | 592.186 | 543.4027 | NaN | NaN | NaN | 526.4995 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 3.8771 | NaN | 19.584
12171.1292 | 729.111 | 638.1503 | 516.7265 | 491.7929 | 483.0011 | 600.8354 | 589.4584 | 542.0596 | NaN | NaN | NaN | 538.6007 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.1198 | NaN | 18.8684
12172.1292 | 730.647 | 637.9044 | 516.6528 | 491.7537 | 483.4835 | 600.647 | 590.5483 | 541.9213 | NaN | NaN | NaN | 537.1571 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.8633 | NaN | 21.2508
12173.1292 | 732.0654 | 638.3523 | 516.628 | 491.9328 | 483.232 | 601.9879 | 595.006 | 543.2167 | NaN | NaN | NaN | 573.4143 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.5404 | NaN | 19.4225
12174.1292 | 732.8726 | 638.0442 | 516.0368 | 492.4407 | 482.904 | 601.2292 | 595.5623 | 542.9355 | NaN | NaN | NaN | 596.0135 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.857 | NaN | 19.6243
12175.1292 | 732.9862 | 637.9897 | 515.546 | 492.9365 | 482.8049 | 599.9008 | 594.3944 | 541.9152 | NaN | NaN | NaN | 582.8726 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.4375 | NaN | 20.414
12176.1292 | 732.9634 | 638.2296 | 514.4081 | 492.8226 | 482.5197 | 599.941 | 594.1008 | 540.7305 | NaN | NaN | NaN | 593.7007 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.312 | NaN | 19.8241
12177.1292 | 732.5175 | 639.2472 | 514.034 | 492.6659 | 482.9844 | 602.6998 | 593.5163 | 538.5216 | NaN | NaN | NaN | 576.837 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.1555 | NaN | 19.9407
12178.1292 | 733.9789 | 640.5678 | 514.7568 | 493.0299 | 482.9833 | 603.3291 | 593.5108 | 538.0414 | NaN | NaN | NaN | 577.816 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 3.8813 | NaN | 18.7563
12179.1292 | 737.0348 | 641.7546 | 515.3203 | 493.6088 | 483.9049 | 602.7261 | 595.6156 | 538.5136 | NaN | NaN | NaN | 584.3095 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.2403 | NaN | 22.2098
12180.1292 | 740.1264 | 640.8903 | 514.8646 | 494.0123 | 483.7651 | 603.8047 | 598.0157 | 540.8947 | NaN | NaN | NaN | 591.2938 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.9875 | NaN | 20.9653
12181.1292 | 742.9959 | 640.3095 | 514.3867 | 493.8597 | 483.5846 | 601.9544 | 597.4477 | 541.5746 | NaN | NaN | NaN | 580.8903 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.7707 | NaN | 21.1831
12182.1292 | 744.5889 | 640.6293 | 513.9281 | 493.6923 | 483.6605 | 600.1572 | 598.2586 | 543.3474 | NaN | NaN | NaN | 593.7065 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 3.3732 | NaN | 19.9494
12183.1292 | 743.4391 | 639.7351 | 514.0021 | 492.69 | 484.4831 | 600.8451 | 596.9079 | 542.9228 | NaN | NaN | NaN | 605.7022 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.0088 | NaN | 19.7662
12184.1292 | 741.7021 | 638.8421 | 513.706 | 492.2806 | 484.1168 | 602.7173 | 597.2312 | 543.494 | NaN | NaN | NaN | 617.3318 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.8971 | NaN | 18.4588
12185.1292 | 740.5589 | 638.1881 | 513.0533 | 492.4566 | 483.6899 | 601.5908 | 595.7508 | 542.341 | NaN | NaN | NaN | 636.931 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.0434 | NaN | 20.0711
12186.1292 | 738.7326 | 638.0234 | 512.3832 | 492.713 | 482.8055 | 600.7337 | 594.9285 | 541.3842 | NaN | NaN | NaN | 648.1225 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 3.9727 | NaN | 21.3196
12187.1292 | 735.3054 | 637.2732 | 512.8519 | 493.0525 | 482.1472 | 602.2428 | 593.0613 | 542.036 | NaN | NaN | NaN | 682.5147 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 3.9909 | NaN | 19.9433
12188.1292 | 732.605 | 635.7886 | 513.1273 | 493.3227 | 482.4782 | 600.6136 | 590.2227 | 540.146 | NaN | NaN | NaN | 701.2386 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.1351 | NaN | 17.9707
12189.1292 | 732.1653 | 634.6114 | 512.8534 | 493.1286 | 481.5631 | 599.456 | 589.2855 | 539.5943 | NaN | NaN | NaN | 696.8725 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.7585 | NaN | 18.523
12190.1292 | 732.7792 | 634.638 | 512.6709 | 492.7569 | 481.2319 | 599.8656 | 589.9213 | 541.751 | NaN | NaN | NaN | 710.8057 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.5728 | NaN | 20.7837
12191.1292 | 733.6026 | 634.7758 | 512.0233 | 491.6459 | 480.908 | 598.7585 | 590.2265 | 540.8338 | NaN | NaN | NaN | 720.379 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.4534 | NaN | 17.5369
12192.1292 | 731.6655 | 635.9645 | 511.6611 | 491.4752 | 480.8167 | 599.3885 | 590.3265 | 540.6898 | NaN | NaN | NaN | 733.0785 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.5812 | NaN | 21.0175
12193.1292 | 729.4971 | 635.9383 | 512.512 | 491.1904 | 480.7908 | 600.5225 | 589.3141 | 540.6723 | NaN | NaN | NaN | 733.8678 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 3.8589 | NaN | 19.0218
12194.1292 | 728.7602 | 637.9212 | 513.3326 | 491.4422 | 480.9195 | 600.4924 | 590.2162 | 540.1364 | NaN | NaN | NaN | 701.3853 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 3.9704 | NaN | 21.2253
12195.1292 | 728.783 | 638.5493 | 514.1155 | 491.7078 | 481.5447 | 600.2726 | 590.0068 | 540.4976 | NaN | NaN | NaN | 694.164 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.5806 | NaN | 20.5526
12196.1292 | 728.3117 | 639.6172 | 514.8307 | 492.4167 | 481.9093 | 601.6092 | 590.6376 | 541.5326 | NaN | NaN | NaN | 719.6355 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 3.8703 | NaN | 21.1322
12197.1292 | 729.4149 | 639.5503 | 516.5552 | 493.1873 | 481.6851 | 600.6126 | 590.8492 | 541.7189 | NaN | NaN | NaN | 715.1068 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.1262 | NaN | 19.964
12198.1292 | 732.1918 | 641.3802 | 517.1903 | 492.348 | 481.8189 | 599.8909 | 592.8223 | 544.1824 | NaN | NaN | NaN | 681.8579 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.0822 | NaN | 19.1377
12199.1292 | 733.1899 | 644.0682 | 517.4183 | 493.1751 | 482.0117 | 602.7673 | 595.7445 | 546.2096 | NaN | NaN | NaN | 651.4173 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.1925 | NaN | 19.3162
12200.1292 | 735.4549 | 644.2358 | 517.9272 | 494.2376 | 482.6329 | 603.583 | 596.1445 | 545.0937 | NaN | NaN | NaN | 626.7857 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.0784 | NaN | 16.6833
12201.1292 | 739.5378 | 644.8388 | 517.9119 | 494.3908 | 482.747 | 601.9743 | 596.6599 | 544.9473 | NaN | NaN | NaN | 615.7902 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.0891 | NaN | 21.3801
12202.1292 | 741.6179 | 644.8785 | 517.5171 | 494.9867 | 482.6352 | 600.9433 | 597.7121 | 545.7521 | NaN | NaN | NaN | 595.3679 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.8039 | NaN | 20.8591
12203.1292 | 741.3157 | 643.8819 | 518.1002 | 495.7912 | 483.2019 | 601.3636 | 597.8591 | 545.7582 | NaN | NaN | NaN | 577.5505 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.3469 | NaN | 20.4509
12204.1292 | 742.1694 | 643.9727 | 518.0856 | 496.0928 | 483.3235 | 602.1213 | 599.8088 | 546.7849 | NaN | NaN | NaN | 580.6217 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.6843 | NaN | 20.5868
12205.1292 | 741.8579 | 643.5181 | 518.8222 | 496.1193 | 482.6168 | 600.6789 | 599.342 | 546.7541 | NaN | NaN | NaN | 584.0342 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.2532 | NaN | 19.763
12206.1292 | 741.3564 | 643.0465 | 518.2724 | 495.9029 | 481.9081 | 598.4962 | 599.1459 | 546.5091 | NaN | NaN | NaN | 621.8575 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.8519 | NaN | 21.5484
12207.1292 | 740.5408 | 641.6915 | 517.4812 | 495.8604 | 481.3782 | 596.4021 | 599.2516 | 546.1001 | NaN | NaN | NaN | 632.2669 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.2369 | NaN | 21.6823
12208.1292 | 740.036 | 641.3557 | 516.3638 | 495.4804 | 481.0724 | 594.8159 | 598.2665 | 544.6948 | NaN | NaN | NaN | 632.5651 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 3.0774 | NaN | 19.3545
12209.1292 | 739.0806 | 639.7155 | 515.3998 | 494.7009 | 480.6182 | 593.0722 | 597.4084 | 543.8216 | NaN | NaN | NaN | 645.3424 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 1.5273 | NaN | 20.7226
12210.1292 | 738.0382 | 638.7606 | 515.2091 | 494.5212 | 482.0017 | 592.7259 | 596.0868 | 542.5302 | NaN | NaN | NaN | 647.1994 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.1594 | NaN | 20.1352
12211.1292 | 735.2353 | 638.19 | 514.2082 | 494.5111 | 481.3866 | 591.4473 | 594.2913 | 541.6275 | NaN | NaN | NaN | 654.2569 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 2.6367 | NaN | 16.8334
12212.1292 | 733.074 | 636.6592 | 514.0996 | 494.4362 | 480.746 | 591.1691 | 593.1081 | 541.404 | NaN | NaN | NaN | 638.568 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.134 | NaN | 19.1328
12213.1292 | 732.459 | 635.7773 | 513.4942 | 494.734 | 480.088 | 590.6338 | 592.3776 | 540.7211 | NaN | NaN | NaN | 652.7073 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.5997 | NaN | 21.5483
12214.1292 | 732.2702 | 635.5147 | 512.9822 | 494.6281 | 479.4335 | 591.1627 | 593.7427 | 541.1083 | NaN | NaN | NaN | 631.0589 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.4294 | NaN | 19.8883
12215.1292 | 732.773 | 635.4395 | 512.1138 | 494.1016 | 479.2092 | 590.8016 | 592.117 | 540.8929 | NaN | NaN | NaN | 613.1535 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.0968 | NaN | 20.8226
12216.1292 | 733.1709 | 635.1138 | 511.8388 | 494.5617 | 479.4852 | 590.9211 | 592.9202 | 540.8694 | NaN | NaN | NaN | 611.3848 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.8455 | NaN | 20.3666
12217.1292 | 734.6787 | 635.8362 | 511.0057 | 494.2408 | 479.3852 | 590.5485 | 591.9607 | 540.3178 | NaN | NaN | NaN | 652.6754 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.4492 | NaN | 18.452
12218.1292 | 735.3335 | 636.4016 | 511.0188 | 494.0388 | 479.1819 | 592.8016 | 592.8837 | 540.7909 | NaN | NaN | NaN | 671.594 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.4542 | NaN | 14.4912
12219.1292 | 734.6243 | 635.9051 | 510.0837 | 493.5355 | 478.856 | 593.5074 | 593.027 | 540.268 | NaN | NaN | NaN | 661.4818 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.9343 | NaN | 19.9986
12220.1292 | 732.7949 | 635.2949 | 509.9326 | 493.3988 | 478.3452 | 594.074 | 592.1849 | 539.7182 | NaN | NaN | NaN | 643.4412 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.0593 | NaN | 20.3982
12221.1292 | 730.8121 | 634.206 | 508.9239 | 493.3235 | 478.0797 | 593.3835 | 590.6549 | 538.6288 | NaN | NaN | NaN | 641.1518 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.7338 | NaN | 19.875
12222.1292 | 728.851 | 633.8162 | 508.5242 | 493.5704 | 477.8616 | 595.1496 | 591.6821 | 538.2101 | NaN | NaN | NaN | 660.2888 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.2893 | NaN | 18.5728
12223.1292 | 727.2909 | 633.7115 | 508.3766 | 494.4007 | 477.5685 | 596.6704 | 591.7819 | 538.2031 | NaN | NaN | NaN | 644.0915 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.2461 | NaN | 19.6492
12224.1292 | 724.8234 | 633.1211 | 507.6269 | 495.0966 | 477.9368 | 595.6301 | 590.5588 | 537.3185 | NaN | NaN | NaN | 652.3738 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.5927 | NaN | 19.3957
12225.1292 | 723.2127 | 632.3264 | 506.9936 | 494.5463 | 477.6086 | 597.2857 | 591.0416 | 536.4391 | NaN | NaN | NaN | 673.4379 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.8227 | NaN | 17.5689
12226.1292 | 722.827 | 631.8383 | 507.2721 | 493.6756 | 477.7693 | 596.1464 | 590.3254 | 535.9586 | NaN | NaN | NaN | 684.7196 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.5238 | NaN | 19.7575
12227.1292 | 722.8956 | 632.5621 | 506.4268 | 493.7041 | 477.5374 | 595.3539 | 589.6722 | 535.7829 | NaN | NaN | NaN | 712.9916 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.4176 | NaN | 19.1128
12228.1292 | 723.3652 | 632.3341 | 506.1081 | 494.2497 | 477.3904 | 595.2708 | 588.9622 | 538.1034 | NaN | NaN | NaN | 724.968 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.5442 | NaN | 19.3892
12229.1292 | 725.4539 | 633.3257 | 505.8117 | 493.765 | 477.6926 | 595.0902 | 589.618 | 538.7838 | NaN | NaN | NaN | 704.0227 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.2 | NaN | 18.4042
12230.1292 | 727.1948 | 634.0938 | 505.4606 | 493.0952 | 477.6957 | 594.9532 | 590.4325 | 539.0356 | NaN | NaN | NaN | 696.1231 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.6929 | NaN | 17.7624
12231.1292 | 728.3135 | 634.2166 | 504.9288 | 492.2814 | 478.2672 | 595.389 | 592.2864 | 542.9852 | NaN | NaN | NaN | 706.6971 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.2599 | NaN | 21.5109
12232.1292 | 731.2896 | 635.4844 | 505.1371 | 491.2292 | 478.6878 | 595.1382 | 594.5623 | 543.9771 | NaN | NaN | NaN | 723.1661 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.4892 | NaN | 17.6703
12233.1292 | 732.812 | 635.5643 | 504.7392 | 492.0619 | 478.7335 | 595.6426 | 595.8849 | 544.1314 | NaN | NaN | NaN | 716.7737 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.0055 | NaN | 19.899
12234.1292 | 730.4192 | 634.8266 | 504.1109 | 491.8965 | 479.1162 | 597.6204 | 594.5588 | 542.2527 | NaN | NaN | NaN | 715.6363 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.8779 | NaN | 16.4698
12235.1292 | 727.3077 | 632.5512 | 503.714 | 491.924 | 478.6369 | 601.371 | 592.3618 | 540.5587 | NaN | NaN | NaN | 711.6019 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.5392 | NaN | 21.5948
12236.1292 | 725.4554 | 631.3444 | 503.4915 | 491.4928 | 478.6724 | 601.1472 | 590.2809 | 538.6418 | NaN | NaN | NaN | 713.7574 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.7727 | NaN | 21.198
12237.1292 | 725.1066 | 631.7004 | 502.9107 | 490.8203 | 477.8816 | 600.8986 | 591.9167 | 537.2588 | NaN | NaN | NaN | 686.0968 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.7069 | NaN | 17.9266
12238.1292 | 724.7126 | 631.9926 | 503.128 | 489.931 | 477.3072 | 600.3758 | 593.1796 | 536.9303 | NaN | NaN | NaN | 715.6805 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.7534 | NaN | 20.8129
12239.1292 | 724.8118 | 632.1257 | 502.8238 | 489.1766 | 476.9714 | 600.2233 | 591.281 | 536.568 | NaN | NaN | NaN | 706.6679 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.1288 | NaN | 18.8327
12240.1292 | 724.2869 | 632.3506 | 502.9049 | 489.1003 | 477.5524 | 599.7375 | 590.0959 | 536.1199 | NaN | NaN | NaN | 717.5529 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.1473 | NaN | 18.8072
12241.1292 | 723.7942 | 631.814 | 503.3008 | 489.4319 | 477.9406 | 598.8717 | 588.3904 | 535.9474 | NaN | NaN | NaN | 708.2149 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.5631 | NaN | 19.6317
12242.1292 | 723.2841 | 631.9462 | 502.9723 | 489.2677 | 478.538 | 600.1391 | 589.0645 | 536.4014 | NaN | NaN | NaN | 694.3007 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.2447 | NaN | 20.4648
12243.1292 | 723.1043 | 631.8975 | 502.5842 | 489.1 | 478.1798 | 601.803 | 592.6066 | 536.6381 | NaN | NaN | NaN | 679.0615 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.4193 | NaN | 19.4336
12244.1292 | 724.5006 | 632.0927 | 502.6805 | 489.4533 | 477.6347 | 600.4556 | 592.2557 | 537.2146 | NaN | NaN | NaN | 679.1426 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.7051 | NaN | 18.5414
12245.1292 | 726.4709 | 632.795 | 502.7112 | 490.0745 | 477.4113 | 601.4261 | 592.2175 | 536.1486 | NaN | NaN | NaN | 696.482 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.4068 | NaN | 17.8387
12246.1292 | 728.4601 | 632.7262 | 502.8912 | 490.5042 | 477.9178 | 600.3339 | 591.3596 | 536.0354 | NaN | NaN | NaN | 715.8995 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.1434 | NaN | 20.9842
12247.1292 | 731.6195 | 633.1058 | 502.4959 | 490.472 | 477.6124 | 599.0828 | 591.1769 | 536.0929 | NaN | NaN | NaN | 699.7962 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.6631 | NaN | 18.9129
12248.1292 | 732.6774 | 633.7231 | 501.9445 | 490.198 | 477.6313 | 604.754 | 595.3804 | 538.2121 | NaN | NaN | NaN | 730.528 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.5467 | NaN | 18.1453
12249.1292 | 733.3187 | 633.9799 | 502.1793 | 489.6837 | 477.4479 | 603.8486 | 594.9978 | 541.5426 | NaN | NaN | NaN | 755.9898 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.1693 | NaN | 21.07
12250.1292 | 736.6281 | 634.0948 | 501.6512 | 489.1872 | 477.121 | 601.8758 | 595.491 | 541.9214 | NaN | NaN | NaN | 721.0749 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.804 | NaN | 18.3126
12251.1292 | 738.366 | 634.4091 | 502.031 | 489.67 | 477.1763 | 601.7616 | 599.2086 | 543.0518 | NaN | NaN | NaN | 690.3708 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.5102 | NaN | 19.6624
12252.1292 | 737.2642 | 633.8138 | 501.2626 | 489.8728 | 476.9429 | 600.4815 | 602.3584 | 546.2865 | NaN | NaN | NaN | 657.7984 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.9987 | NaN | 21.9398
12253.1292 | 735.1057 | 634.2623 | 500.951 | 489.4712 | 476.8685 | 601.854 | 605.5348 | 552.1495 | NaN | NaN | NaN | 658.862 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.7265 | NaN | 19.5077
12254.1292 | 731.3593 | 633.6032 | 500.9654 | 489.3209 | 476.9709 | 602.6186 | 604.3235 | 549.0642 | NaN | NaN | NaN | 687.2489 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.2925 | NaN | 20.4544
12255.1292 | 727.6817 | 632.5022 | 500.9641 | 489.4792 | 476.8665 | 603.0806 | 601.469 | 546.5151 | NaN | NaN | NaN | 703.1159 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.5099 | NaN | 19.2752
12256.1292 | 724.3662 | 632.3407 | 501.3679 | 489.2161 | 477.1385 | 603.0982 | 599.6591 | 544.5043 | NaN | NaN | NaN | 690.5567 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.4954 | NaN | 20.7877
12257.1292 | 722.6797 | 632.054 | 501.229 | 488.95 | 477.1543 | 601.0983 | 597.0327 | 542.2517 | NaN | NaN | NaN | 729.8362 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.543 | NaN | 17.9882
12258.1292 | 724.4133 | 632.5222 | 501.2444 | 488.9849 | 477.0397 | 599.8742 | 597.1568 | 541.6224 | NaN | NaN | NaN | 752.3046 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.7332 | NaN | 19.2816
12259.1292 | 726.3964 | 632.7679 | 500.6383 | 489.3105 | 476.6186 | 599.8324 | 596.7799 | 541.2574 | NaN | NaN | NaN | 768.1821 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.6347 | NaN | 19.8884
12260.1292 | 728.9577 | 632.6866 | 500.1421 | 489.1957 | 477.3391 | 599.9113 | 597.9892 | 541.928 | NaN | NaN | NaN | 755.3876 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.8911 | NaN | 19.5251
12261.1292 | 732.3687 | 632.3975 | 500.1254 | 488.6446 | 477.6604 | 597.9704 | 596.2513 | 541.3456 | NaN | NaN | NaN | 722.0231 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.6513 | NaN | 18.3562
12262.1292 | 736.3316 | 634.6417 | 499.8501 | 487.8895 | 478.3172 | 598.3323 | 598.5017 | 542.5042 | NaN | NaN | NaN | 710.8115 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.1125 | NaN | 20.3928
12263.1292 | 741.402 | 636.1066 | 500.0512 | 488.2184 | 478.1749 | 599.4252 | 602.3808 | 543.5814 | NaN | NaN | NaN | 702.8265 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.9513 | NaN | 18.8149
12264.1292 | 744.2441 | 636.2872 | 500.6451 | 488.715 | 478.0813 | 600.3225 | 603.7898 | 544.6164 | NaN | NaN | NaN | 691.2206 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.5662 | NaN | 19.9158
12265.1292 | 745.2096 | 636.0991 | 500.445 | 488.4864 | 478.122 | 599.277 | 602.9583 | 544.0168 | NaN | NaN | NaN | 690.3281 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.6192 | NaN | 19.9067
12266.1292 | 743.6625 | 635.7051 | 500.0048 | 488.7488 | 477.6972 | 597.3904 | 601.4617 | 543.605 | NaN | NaN | NaN | 698.506 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.9166 | NaN | 16.5839
12267.1292 | 742.9257 | 635.2065 | 499.9751 | 488.7644 | 477.6929 | 599.726 | 600.8056 | 543.2382 | NaN | NaN | NaN | 738.9205 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 2.7606 | NaN | 16.9884
12268.1292 | 741.801 | 635.9085 | 500.5125 | 488.2162 | 477.6772 | 600.0103 | 601.0348 | 543.7376 | NaN | NaN | NaN | 754.7604 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.7271 | NaN | 17.686
12269.1292 | 741.7134 | 635.8686 | 501.1821 | 488.7484 | 477.8309 | 597.7435 | 600.1233 | 543.8615 | NaN | NaN | NaN | 769.5618 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.9126 | NaN | 19.2582
12270.1292 | 741.5417 | 635.7462 | 500.895 | 489.0919 | 477.7791 | 597.6366 | 599.6717 | 543.8991 | NaN | NaN | NaN | 763.8204 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.2485 | NaN | 20.7569
12271.1292 | 739.1389 | 634.8047 | 500.8752 | 488.0901 | 477.4068 | 596.4238 | 597.6911 | 542.4205 | NaN | NaN | NaN | 747.604 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.9917 | NaN | 18.0385
12272.1292 | 736.7355 | 633.6315 | 501.0113 | 487.3032 | 477.3976 | 599.3462 | 598.4114 | 542.0816 | NaN | NaN | NaN | 734.72 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.2367 | NaN | 20.0226
12273.1292 | 733.6114 | 632.0333 | 501.6912 | 486.7895 | 477.6552 | 600.8859 | 597.892 | 541.9244 | NaN | NaN | NaN | 717.0364 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.4093 | NaN | 17.8826
12274.1292 | 729.6806 | 630.9825 | 502.3502 | 486.3993 | 477.3398 | 601.3385 | 595.7011 | 540.6558 | NaN | NaN | NaN | 710.7298 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.0479 | NaN | 21.2102
12275.1292 | 727.5602 | 630.459 | 502.2234 | 486.9566 | 476.8261 | 600.6113 | 592.4931 | 539.9117 | NaN | NaN | NaN | 712.8183 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.455 | NaN | 19.7695
12276.1292 | 727.015 | 630.5167 | 501.7127 | 486.7304 | 476.4721 | 599.0682 | 591.5333 | 538.4959 | NaN | NaN | NaN | 691.3947 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.7143 | NaN | 20.097
12277.1292 | 727.6833 | 630.4418 | 501.4541 | 487.2982 | 476.456 | 596.896 | 590.2298 | 538.5783 | NaN | NaN | NaN | 694.8826 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.1559 | NaN | 19.192
12278.1292 | 729.4688 | 631.1732 | 501.2519 | 486.8957 | 476.354 | 596.2172 | 591.0697 | 538.8781 | NaN | NaN | NaN | 670.6958 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.6334 | NaN | 20.5456
12279.1292 | 729.5495 | 633.3184 | 501.6189 | 486.8684 | 477.0418 | 597.9744 | 591.48 | 540.0139 | NaN | NaN | NaN | 647.2707 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.2906 | NaN | 16.2131
12280.1292 | 729.069 | 633.6911 | 502.3034 | 487.4083 | 477.9196 | 597.5336 | 590.5271 | 537.5361 | NaN | NaN | NaN | 623.0884 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.6916 | NaN | 19.7317
12281.1292 | 729.1528 | 633.556 | 503.4874 | 487.6157 | 477.7676 | 599.1041 | 590.4762 | 536.3017 | NaN | NaN | NaN | 612.0992 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.3868 | NaN | 20.1701
12282.1292 | 730.3222 | 632.6646 | 504.3242 | 488.2596 | 478.7415 | 601.3722 | 592.7753 | 537.3422 | NaN | NaN | NaN | 624.7196 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.0479 | NaN | 18.9777
12283.1292 | 732.6727 | 633.3478 | 504.1961 | 488.4486 | 478.5852 | 601.7547 | 594.8872 | 542.8609 | NaN | NaN | NaN | 631.3826 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.1711 | NaN | 20.6245
12284.1292 | 733.8158 | 633.9904 | 503.6475 | 488.6679 | 478.3344 | 601.2324 | 596.5172 | 542.348 | NaN | NaN | NaN | 630.3415 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.5825 | NaN | 18.2961
12285.1292 | 733.1335 | 633.9917 | 503.9239 | 489.0763 | 478.3945 | 601.7488 | 594.8835 | 541.8723 | NaN | NaN | NaN | 643.3203 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.0294 | NaN | 20.0445
12286.1292 | 732.3327 | 633.2527 | 503.8995 | 489.5244 | 479.142 | 601.8898 | 595.8078 | 541.6834 | NaN | NaN | NaN | 649.137 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.9218 | NaN | 15.6796
12287.1292 | 731.718 | 633.031 | 503.5254 | 488.8792 | 479.6279 | 600.5615 | 594.6622 | 542.0488 | NaN | NaN | NaN | 666.316 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.037 | NaN | 20.3561
12288.1292 | 731.7331 | 632.782 | 503.1766 | 488.5325 | 479.6272 | 597.4416 | 593.1985 | 540.6874 | NaN | NaN | NaN | 647.0306 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.1199 | NaN | 17.7056
12289.1292 | 733.2027 | 633.2954 | 502.9663 | 488.5372 | 479.4611 | 596.9729 | 592.9549 | 539.3804 | NaN | NaN | NaN | 677.0967 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.7926 | NaN | 18.5534
12290.1292 | 734.9764 | 633.0586 | 502.2289 | 489.1376 | 479.4777 | 598.0625 | 593.82 | 540.1689 | NaN | NaN | NaN | 662.5693 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.9536 | NaN | 19.8621
12291.1292 | 735.5536 | 633.2738 | 501.9939 | 489.7195 | 479.2157 | 599.5006 | 594.5624 | 540.8485 | NaN | NaN | NaN | 667.2546 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.6157 | NaN | 18.1638
12292.1292 | 735.9956 | 633.5035 | 501.7209 | 489.4087 | 479.7876 | 599.4883 | 594.2965 | 539.5356 | NaN | NaN | NaN | 700.3934 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.033 | NaN | 19.2996
12293.1292 | 738.0396 | 634.4051 | 501.5459 | 489.5697 | 479.9163 | 599.0981 | 594.0973 | 539.1477 | NaN | NaN | NaN | 716.6631 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.1426 | NaN | 16.9976
12294.1448 | 739.638 | 633.9845 | 501.7029 | 489.6811 | 480.8017 | 599.6249 | 594.7894 | 539.0592 | NaN | NaN | NaN | 703.1391 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.6056 | NaN | 19.2502
12295.1292 | 740.4996 | 634.0979 | 501.2472 | 489.0199 | 480.5928 | 598.702 | 594.9144 | 539.7763 | NaN | NaN | NaN | 726.3217 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.999 | NaN | 18.5131
12296.1292 | 741.8714 | 634.8628 | 500.8902 | 488.7555 | 480.0559 | 597.2278 | 595.0037 | 540.7706 | NaN | NaN | NaN | 720.8527 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.7738 | NaN | 19.8517
12297.1292 | 744.6158 | 636.3174 | 500.4478 | 488.9881 | 479.6308 | 597.7897 | 598.2466 | 543.4798 | NaN | NaN | NaN | 732.3092 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.5635 | NaN | 16.402
12298.1292 | 746.5669 | 636.6395 | 500.5581 | 488.7529 | 479.535 | 597.3702 | 598.9119 | 543.5154 | NaN | NaN | NaN | 702.4376 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.3964 | NaN | 19.0811
12299.1292 | 747.2565 | 636.4932 | 501.061 | 489.14 | 479.6543 | 598.9419 | 599.1184 | 543.3929 | NaN | NaN | NaN | 712.3711 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.9597 | NaN | 16.6265
12300.1292 | 748.1447 | 636.503 | 501.1922 | 489.0296 | 479.3828 | 598.6304 | 598.9853 | 542.415 | NaN | NaN | NaN | 726.5454 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.7015 | NaN | 18.865
12301.1292 | 748.4981 | 636.997 | 501.3728 | 489.0676 | 479.2769 | 600.5957 | 599.912 | 542.1419 | NaN | NaN | NaN | 730.7209 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.6017 | NaN | 20.572
12302.1292 | 747.024 | 637.3583 | 501.3282 | 489.8693 | 478.9571 | 601.1066 | 599.6504 | 541.6115 | NaN | NaN | NaN | 749.4066 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.1334 | NaN | 18.6974
12303.1292 | 746.7794 | 637.2838 | 501.8066 | 489.8856 | 478.6745 | 601.6458 | 598.8099 | 541.0963 | NaN | NaN | NaN | 744.7453 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.8084 | NaN | 16.4496
12304.1292 | 748.3403 | 638.1034 | 501.9201 | 489.5887 | 478.5468 | 601.0753 | 601.5003 | 542.7878 | NaN | NaN | NaN | 734.8299 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.5686 | NaN | 20.0134
12305.1292 | 748.9802 | 637.7429 | 501.7389 | 489.2844 | 478.4458 | 600.6139 | 603.2801 | 546.1876 | NaN | NaN | NaN | 746.6236 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.859 | NaN | 19.1729
12306.1292 | 748.8929 | 638.5664 | 501.2123 | 490.2076 | 478.1533 | 600.0907 | 603.1621 | 545.5072 | NaN | NaN | NaN | 763.2331 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.7913 | NaN | 18.9673
12307.1292 | 748.1537 | 639.0405 | 501.9356 | 490.4031 | 478.2739 | 599.364 | 603.1882 | 546.5792 | NaN | NaN | NaN | 777.1533 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.5545 | NaN | 17.8689
12308.1292 | 748.8729 | 639.6862 | 502.4048 | 490.1506 | 479.223 | 601.794 | 605.2528 | 547.625 | NaN | NaN | NaN | 794.6207 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.0295 | NaN | 17.095
12309.1292 | 750.8194 | 640.3239 | 503.3005 | 490.1023 | 479.3641 | 602.3391 | 605.281 | 549.9462 | NaN | NaN | NaN | 800.3081 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.2973 | NaN | 19.0013
12310.1292 | 750.5559 | 640.1473 | 503.9714 | 491.1762 | 479.3315 | 603.1621 | 604.8172 | 550.309 | NaN | NaN | NaN | 820.4034 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.5183 | NaN | 20.5406
12311.1292 | 750.1178 | 639.1886 | 504.8342 | 492.1824 | 480.4254 | 602.4572 | 601.6672 | 548.5362 | NaN | NaN | NaN | 775.8318 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.1082 | NaN | 19.222
12312.1292 | 749.0349 | 641.7223 | 505.7507 | 492.6471 | 480.7582 | 604.6677 | 605.0415 | 547.6221 | NaN | NaN | NaN | 736.6032 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.5341 | NaN | 19.8723
12313.1292 | 746.6262 | 642.3316 | 507.423 | 493.7364 | 482.0115 | 604.9069 | 605.6351 | 547.2775 | NaN | NaN | NaN | 722.5563 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.5541 | NaN | 18.6274
12314.1292 | 743.7904 | 640.8154 | 508.0069 | 493.7162 | 482.1975 | 604.6236 | 603.0655 | 545.9735 | NaN | NaN | NaN | 688.8461 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.4903 | NaN | 18.964
12315.1292 | 741.9203 | 639.7663 | 507.9836 | 493.2908 | 481.4963 | 604.8941 | 602.0274 | 545.1531 | NaN | NaN | NaN | 678.4831 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.1717 | NaN | 20.1934
12316.1292 | 740.5553 | 639.1719 | 507.2631 | 493.4631 | 480.4645 | 606.1688 | 602.4483 | 546.1247 | NaN | NaN | NaN | 712.7612 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.6697 | NaN | 18.4987
12317.1292 | 740.1483 | 638.732 | 506.6849 | 493.5323 | 480.3105 | 604.5647 | 601.1601 | 545.5616 | NaN | NaN | NaN | 691.1773 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.5251 | NaN | 18.6282
12318.1292 | 741.6934 | 638.4799 | 506.6604 | 493.893 | 480.2914 | 603.1307 | 600.3309 | 544.9568 | NaN | NaN | NaN | 669.7979 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.8366 | NaN | 15.8924
12319.1292 | 743.9711 | 638.851 | 506.0051 | 493.6762 | 480.0803 | 604.089 | 601.5886 | 544.8115 | NaN | NaN | NaN | 662.8014 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.1877 | NaN | 19.9522
12320.1292 | 744.6478 | 638.7819 | 505.4849 | 492.8588 | 479.3606 | 606.3088 | 606.8155 | 547.0634 | NaN | NaN | NaN | 649.8455 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.6264 | NaN | 18.5508
12321.1292 | 743.5361 | 638.0755 | 505.395 | 492.5755 | 478.9255 | 605.1092 | 604.2156 | 545.8108 | NaN | NaN | NaN | 648.9177 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 2.2214 | NaN | 21.0483
12322.1292 | 742.2099 | 636.9977 | 504.5545 | 492.5266 | 478.4142 | 605.2841 | 603.8211 | 544.4083 | NaN | NaN | NaN | 621.2023 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.3339 | NaN | 18.8824
12323.1292 | 740.5542 | 636.7919 | 504.3744 | 492.8438 | 477.9592 | 604.3283 | 605.7024 | 545.5422 | NaN | NaN | NaN | 650.9601 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.2475 | NaN | 19.0049
12324.1448 | 739.8007 | 636.6633 | 504.7665 | 494.0637 | 477.7353 | 601.8569 | 605.2054 | 544.5889 | NaN | NaN | NaN | 679.1933 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.0545 | NaN | 19.4813
12325.1292 | 739.1698 | 636.4798 | 504.5316 | 493.924 | 477.5799 | 599.5116 | 603.8399 | 542.8873 | NaN | NaN | NaN | 701.9701 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.4083 | NaN | 16.8518
12326.1292 | 739.1739 | 637.2747 | 503.935 | 493.6855 | 477.5209 | 599.5878 | 603.3558 | 541.7959 | NaN | NaN | NaN | 710.3729 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.3351 | NaN | 17.4727
12327.1292 | 738.6454 | 637.1581 | 503.7585 | 494.2907 | 477.2768 | 598.7724 | 601.7844 | 541.4603 | NaN | NaN | NaN | 727.0734 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.2872 | NaN | 18.3658
12328.1292 | 736.1181 | 636.3753 | 504.1668 | 493.4122 | 477.1255 | 598.4712 | 600.0525 | 540.6698 | NaN | NaN | NaN | 729.7597 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.4131 | NaN | 16.5207
12329.1292 | 733.2599 | 635.767 | 505.1342 | 492.3292 | 477.1908 | 599.1485 | 597.9678 | 539.7657 | NaN | NaN | NaN | 736.365 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.6103 | NaN | 19.7724
12330.1292 | 730.9083 | 634.5008 | 506.3433 | 492.2214 | 477.4047 | 599.4303 | 595.5642 | 538.7462 | NaN | NaN | NaN | 738.5437 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.54 | NaN | 13.9646
12331.1292 | 728.7691 | 634.3172 | 506.8772 | 492.5804 | 477.8943 | 599.2707 | 594.5779 | 537.335 | NaN | NaN | NaN | 737.1896 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.8774 | NaN | 16.5424
12332.1292 | 727.0195 | 633.3137 | 507.2438 | 492.0529 | 477.7547 | 599.0276 | 593.0534 | 536.1976 | NaN | NaN | NaN | 702.6863 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.5729 | NaN | 16.4968
12333.1292 | 726.6376 | 632.7218 | 507.7601 | 492.3316 | 477.86 | 598.3479 | 591.8147 | 535.182 | NaN | NaN | NaN | 699.4006 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.1321 | NaN | 19.2319
12334.1292 | 725.7447 | 632.7423 | 507.9618 | 492.6426 | 477.5999 | 602.305 | 595.1481 | 536.7811 | NaN | NaN | NaN | 699.7182 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.2716 | NaN | 15.4347
12335.1292 | 725.1577 | 632.6454 | 508.7543 | 492.6977 | 477.0606 | 599.8442 | 593.5296 | 536.353 | NaN | NaN | NaN | 690.2453 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.6228 | NaN | 17.7415
12336.1292 | 724.4552 | 632.5352 | 508.8146 | 492.6481 | 476.7561 | 598.1463 | 591.6511 | 535.0605 | NaN | NaN | NaN | 712.6311 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.833 | NaN | 20.7745
12337.1292 | 725.5632 | 632.6708 | 509.0477 | 493.1629 | 476.6172 | 598.4703 | 590.9 | 533.3805 | NaN | NaN | NaN | 731.4996 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.4409 | NaN | 19.4989
12338.1292 | 727.2784 | 632.9784 | 508.1479 | 492.822 | 477.2197 | 598.3911 | 590.978 | 532.4399 | NaN | NaN | NaN | 733.1721 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.2084 | NaN | 20.041
12339.1292 | 728.809 | 633.0258 | 507.5135 | 492.7813 | 477.1042 | 598.3976 | 594.1301 | 533.7862 | NaN | NaN | NaN | 724.0678 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.8776 | NaN | 18.8899
12340.1292 | 730.0697 | 633.0369 | 506.6454 | 492.1224 | 476.9062 | 597.3931 | 592.6701 | 533.5994 | NaN | NaN | NaN | 739.1991 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.8856 | NaN | 18.7392
12341.1292 | 730.6972 | 633.832 | 506.073 | 491.9775 | 476.5147 | 597.0137 | 591.5151 | 532.9148 | NaN | NaN | NaN | 736.7353 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.241 | NaN | 20.4419
12342.1292 | 732.4127 | 634.3407 | 506.6216 | 491.3972 | 477.2031 | 598.5469 | 592.5809 | 533.526 | NaN | NaN | NaN | 738.8832 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.3207 | NaN | 19.6414
12343.1292 | 732.7946 | 633.2792 | 506.5933 | 491.5011 | 478.293 | 597.6624 | 591.6683 | 533.0027 | NaN | NaN | NaN | 764.5571 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.2958 | NaN | 18.8268
12344.1292 | 733.7666 | 634.6197 | 507.3179 | 491.6274 | 478.3182 | 599.3404 | 592.919 | 532.5741 | NaN | NaN | NaN | 774.3113 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.7711 | NaN | 19.7687
12345.1292 | 733.6356 | 635.0015 | 507.6439 | 493.3017 | 478.7835 | 599.4866 | 593.8538 | 532.5301 | NaN | NaN | NaN | 781.5482 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.6088 | NaN | 17.6887
12346.1292 | 731.9208 | 634.3858 | 508.2419 | 494.1244 | 478.782 | 599.0683 | 592.0551 | 531.1158 | NaN | NaN | NaN | 750.7011 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.4527 | NaN | 18.289
12347.1292 | 730.7042 | 632.6021 | 508.7305 | 494.7265 | 479.2817 | 597.9557 | 589.6024 | 529.5896 | NaN | NaN | NaN | 755.7207 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.4768 | NaN | 16.4895
12348.1292 | 730.6842 | 632.0399 | 508.498 | 493.4634 | 478.6641 | 597.9892 | 588.6884 | 528.9191 | NaN | NaN | NaN | 731.4837 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.9174 | NaN | 18.571
12349.1292 | 732.2085 | 634.1748 | 508.0248 | 493.0565 | 478.317 | 600.0205 | 590.6615 | 529.5685 | NaN | NaN | NaN | 707.1696 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.2123 | NaN | 18.4524
12350.1292 | 733.3196 | 634.1782 | 508.4316 | 492.721 | 478.3359 | 599.2002 | 591.8988 | 529.9376 | NaN | NaN | NaN | 733.8124 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.2561 | NaN | 18.1315
12351.1292 | 735.7689 | 634.6482 | 508.8098 | 491.5876 | 477.8093 | 599.0614 | 592.788 | 531.6544 | NaN | NaN | NaN | 740.9197 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.5863 | NaN | 19.9268
12352.1292 | 738.1999 | 636.2315 | 509.295 | 491.9167 | 477.2868 | 599.3923 | 594.3074 | 532.5153 | NaN | NaN | NaN | 703.2571 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.2041 | NaN | 19.4781
12353.1292 | 740.967 | 635.8883 | 509.7677 | 492.5023 | 477.4536 | 598.2804 | 594.5141 | 532.4349 | NaN | NaN | NaN | 674.2463 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.7533 | NaN | 19.713
12354.1292 | 742.889 | 636.7012 | 509.5148 | 493.4998 | 477.4875 | 599.1209 | 595.4426 | 533.5305 | NaN | NaN | NaN | 673.9426 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.0354 | NaN | 17.5398
12355.1292 | 742.8876 | 635.9437 | 509.0834 | 493.3377 | 476.937 | 600.4519 | 595.897 | 533.9354 | NaN | NaN | NaN | 647.514 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.0623 | NaN | 19.3108
12356.1292 | 742.2452 | 635.3866 | 508.819 | 492.8586 | 476.7295 | 599.5919 | 593.5328 | 532.4649 | NaN | NaN | NaN | 633.0969 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.7409 | NaN | 19.291
12357.1292 | 743.7535 | 636.4945 | 508.5941 | 493.2147 | 476.5935 | 599.8547 | 594.0517 | 532.4726 | NaN | NaN | NaN | 671.1047 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.6119 | NaN | 18.6395
12358.1292 | 745.8241 | 638.5502 | 509.5427 | 493.4188 | 476.5725 | 600.4544 | 596.0991 | 533.1917 | NaN | NaN | NaN | 697.5315 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.1599 | NaN | 19.8389
12359.1292 | 746.5623 | 638.489 | 509.5627 | 494.6097 | 476.238 | 601.517 | 596.518 | 534.722 | NaN | NaN | NaN | 723.4168 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.6962 | NaN | 19.1792
12360.1292 | 747.6942 | 637.8287 | 509.0763 | 494.5586 | 476.175 | 601.0099 | 594.8249 | 533.2197 | NaN | NaN | NaN | 694.5417 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.6848 | NaN | 18.8754
12361.1292 | 747.4358 | 637.5466 | 508.6842 | 494.0111 | 476.1682 | 601.8157 | 595.4786 | 533.0533 | NaN | NaN | NaN | 672.6735 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.4296 | NaN | 18.9479
12362.1292 | 745.8416 | 637.7851 | 508.1541 | 493.9505 | 475.4807 | 602.3302 | 596.414 | 532.5271 | NaN | NaN | NaN | 686.7157 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.4095 | NaN | 19.4163
12363.1292 | 744.3738 | 637.9045 | 508.7591 | 493.9543 | 475.5161 | 603.2583 | 596.8592 | 534.0007 | NaN | NaN | NaN | 701.0395 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.5115 | NaN | 18.6264
12364.1292 | 744.7882 | 637.8779 | 508.6772 | 494.4102 | 476.6309 | 605.2469 | 598.8285 | 534.5333 | NaN | NaN | NaN | 709.5564 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.603 | NaN | 16.7376
12365.1292 | 746.8377 | 638.5426 | 508.1971 | 494.9602 | 476.6724 | 604.0729 | 599.8174 | 534.7267 | NaN | NaN | NaN | 731.3833 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.6733 | NaN | 18.5829
12366.1292 | 747.2787 | 638.3337 | 507.4945 | 495.5495 | 476.7707 | 606.0858 | 601.0538 | 534.9123 | NaN | NaN | NaN | 724.5728 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.9452 | NaN | 18.6438
12367.1292 | 746.2869 | 637.9064 | 506.4278 | 495.7493 | 476.6577 | 605.6584 | 601.2258 | 533.8439 | NaN | NaN | NaN | 719.4443 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.8051 | NaN | 16.7758
12368.1292 | 745.7901 | 637.0029 | 506.3299 | 495.6851 | 477.9821 | 604.1142 | 599.4327 | 532.8765 | NaN | NaN | NaN | 713.4692 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.003 | NaN | 20.939
12369.1292 | 744.7674 | 636.5148 | 506.7333 | 495.0377 | 478.3362 | 602.2914 | 597.5613 | 531.9803 | NaN | NaN | NaN | 719.6907 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.5062 | NaN | 17.7283
12370.1292 | 744.428 | 636.6302 | 505.9022 | 494.5173 | 478.7142 | 600.769 | 595.391 | 530.3529 | NaN | NaN | NaN | 716.7868 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.572 | NaN | 17.4958
12371.1292 | 744.3086 | 636.8062 | 505.6582 | 494.6528 | 478.5832 | 601.608 | 595.403 | 530.3078 | NaN | NaN | NaN | 696.9381 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.1051 | NaN | 19.4086
12372.1292 | 744.2937 | 635.4326 | 505.9034 | 494.7965 | 478.3023 | 600.9872 | 594.6516 | 529.8989 | NaN | NaN | NaN | 705.2017 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.466 | NaN | 16.9759
12373.1292 | 744.7643 | 635.6309 | 506.5387 | 494.9049 | 478.2697 | 600.7217 | 594.2845 | 531.8379 | NaN | NaN | NaN | 696.9434 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.0161 | NaN | 18.4194
12374.1292 | 746.3585 | 635.9265 | 506.5369 | 495.1851 | 479.5442 | 600.2095 | 594.6111 | 531.5473 | NaN | NaN | NaN | 669.1976 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.4147 | NaN | 19.6296
12375.1292 | 747.5394 | 636.3682 | 506.136 | 495.5086 | 481.056 | 600.2744 | 596.3551 | 532.4273 | NaN | NaN | NaN | 687.6638 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.2177 | NaN | 18.5452
12376.1292 | 748.8609 | 636.6679 | 506.3845 | 496.1713 | 480.3547 | 599.8757 | 598.0536 | 533.0459 | NaN | NaN | NaN | 694.3555 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.684 | NaN | 17.0999
12377.1292 | 750.5704 | 636.9006 | 505.6526 | 496.5481 | 479.7671 | 600.5098 | 598.8417 | 533.313 | NaN | NaN | NaN | 697.9873 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.0067 | NaN | 18.8201
12378.1292 | 752.1685 | 636.8887 | 505.7552 | 496.6083 | 479.852 | 599.2819 | 599.7349 | 533.7301 | NaN | NaN | NaN | 718.5628 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.3818 | NaN | 19.7877
12379.1292 | 753.258 | 637.2804 | 506.574 | 496.9306 | 480.5327 | 598.317 | 598.3241 | 533.2942 | NaN | NaN | NaN | 704.8412 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.4307 | NaN | 20.2224
12380.1292 | 754.4108 | 637.2386 | 505.9377 | 497.0848 | 480.4746 | 599.1851 | 598.2503 | 533.2421 | NaN | NaN | NaN | 706.7025 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 1.529 | NaN | 15.8879
12381.1292 | 755.3592 | 636.7696 | 505.4135 | 495.3538 | 480.9129 | 598.9626 | 597.9963 | 532.8227 | NaN | NaN | NaN | 714.9395 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.6328 | NaN | 19.3502
12382.1292 | 755.5428 | 636.5964 | 505.024 | 494.3887 | 479.8838 | 598.5026 | 598.3486 | 533.0984 | NaN | NaN | NaN | 719.352 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.2695 | NaN | 16.6341
12383.1292 | 755.4086 | 636.81 | 504.5889 | 494.466 | 479.5416 | 598.589 | 598.448 | 534.0094 | NaN | NaN | NaN | 741.7317 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.4129 | NaN | 18.7288
12384.1448 | 755.9857 | 636.3802 | 504.8435 | 494.9141 | 479.7186 | 598.6444 | 596.3159 | 533.2195 | NaN | NaN | NaN | 737.935 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.2178 | NaN | 19.3111
12385.1292 | 754.679 | 636.8755 | 505.1514 | 494.0855 | 479.4069 | 597.4384 | 596.0457 | 533.5247 | NaN | NaN | NaN | 746.6824 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.1907 | NaN | 17.7514
12386.1292 | 754.6952 | 637.0592 | 505.8186 | 494.0231 | 479.4669 | 597.0586 | 597.0347 | 535.2924 | NaN | NaN | NaN | 748.792 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 10.5647 | NaN | 19.4644
12387.1292 | 752.386 | 636.2086 | 505.2636 | 493.8957 | 479.9933 | 600.2449 | 599.1439 | 537.786 | NaN | NaN | NaN | 725.8381 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.0141 | NaN | 17.9886
12388.1292 | 750.7131 | 635.201 | 504.9394 | 493.7947 | 479.4146 | 598.2715 | 596.4022 | 536.7544 | NaN | NaN | NaN | 719.2612 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.6925 | NaN | 17.6671
12389.1292 | 749.9388 | 635.2143 | 504.4984 | 495.0065 | 479.1151 | 597.6904 | 596.4038 | 536.2023 | NaN | NaN | NaN | 719.8465 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 3.8492 | NaN | 16.3232
12390.1292 | 752.0573 | 636.2841 | 503.9231 | 494.712 | 478.8952 | 597.2363 | 596.7699 | 537.6628 | NaN | NaN | NaN | 744.9288 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.9006 | NaN | 19.7583
12391.1292 | 753.9243 | 636.8611 | 503.4507 | 494.3676 | 480.1426 | 597.1294 | 599.1517 | 539.398 | NaN | NaN | NaN | 739.4379 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.8551 | NaN | 19.0363
12392.1292 | 755.9047 | 637.657 | 503.4092 | 494.6959 | 480.5141 | 596.1762 | 598.8111 | 538.6954 | NaN | NaN | NaN | 741.9862 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.2742 | NaN | 15.2746
12393.1292 | 759.0392 | 638.5489 | 503.2619 | 494.2415 | 481.5278 | 597.435 | 602.5879 | 539.6485 | NaN | NaN | NaN | 771.2215 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.8372 | NaN | 21.5826
12394.1292 | 762.051 | 638.8656 | 504.154 | 493.8282 | 481.299 | 596.7644 | 604.1073 | 539.3359 | NaN | NaN | NaN | 784.7053 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.209 | NaN | 19.6534
12395.1292 | 762.7876 | 639.5631 | 504.8105 | 493.8351 | 481.0914 | 597.9694 | 603.7854 | 540.2271 | NaN | NaN | NaN | 741.6408 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.0597 | NaN | 18.499
12396.1292 | 764.0265 | 640.1343 | 505.232 | 495.0552 | 481.1795 | 598.2212 | 603.1715 | 539.6835 | NaN | NaN | NaN | 717.7307 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.0155 | NaN | 18.7856
12397.1292 | 766.5896 | 639.7913 | 506.1745 | 495.1355 | 481.5166 | 596.8404 | 603.2317 | 539.7781 | NaN | NaN | NaN | 738.1724 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.4658 | NaN | 16.4255
12398.1292 | 768.8309 | 639.3111 | 505.8029 | 495.0359 | 481.5407 | 595.2425 | 602.501 | 540.4993 | NaN | NaN | NaN | 714.0519 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 2.1623 | NaN | 18.6357
12399.1292 | 768.3439 | 639.2325 | 505.2668 | 494.9767 | 480.9209 | 595.7637 | 601.1433 | 539.6735 | NaN | NaN | NaN | 716.0032 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.0472 | NaN | 17.8724
12400.1292 | 767.7121 | 639.0452 | 505.1453 | 495.2404 | 480.893 | 597.616 | 602.9101 | 540.3805 | NaN | NaN | NaN | 742.1277 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.5501 | NaN | 17.5307
12401.1292 | 765.5199 | 638.3359 | 505.59 | 495.1098 | 480.9905 | 597.5378 | 603.4517 | 540.9891 | NaN | NaN | NaN | 731.1744 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.3925 | NaN | 17.8702
12402.1292 | 762.5147 | 637.267 | 505.557 | 494.2908 | 482.1559 | 596.7248 | 602.7542 | 540.8048 | NaN | NaN | NaN | 722.9181 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 2.5037 | NaN | 16.4354
12403.1292 | 761.1924 | 636.838 | 504.7194 | 493.7807 | 481.9369 | 595.7148 | 602.3844 | 541.4345 | NaN | NaN | NaN | 744.1727 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 3.9613 | NaN | 19.1138
12404.1292 | 759.3914 | 636.6716 | 504.8665 | 493.6516 | 481.2172 | 594.1539 | 602.8931 | 542.203 | NaN | NaN | NaN | 737.072 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.8233 | NaN | 17.4733
12405.1292 | 757.5828 | 635.7584 | 504.2537 | 492.8069 | 480.6484 | 592.4721 | 602.1306 | 543.9144 | NaN | NaN | NaN | 749.7008 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 2.7174 | NaN | 20.1638
12406.1292 | 756.4426 | 635.11 | 503.6587 | 491.872 | 480.1981 | 590.1134 | 599.766 | 542.2959 | NaN | NaN | NaN | 762.6225 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.2615 | NaN | 22.1266
12407.1292 | 754.7318 | 634.4094 | 503.2187 | 491.2245 | 479.3241 | 589.8375 | 598.923 | 541.4409 | NaN | NaN | NaN | 759.8421 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 1.0481 | NaN | 13.4376
12408.1292 | 753.1379 | 633.4043 | 502.7724 | 490.7744 | 478.5146 | 588.7397 | 597.9383 | 540.5451 | NaN | NaN | NaN | 764.8001 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.0979 | NaN | 18.6289
12409.1292 | 752.0214 | 632.9497 | 502.3983 | 490.8262 | 478.3498 | 587.6378 | 597.628 | 540.3068 | NaN | NaN | NaN | 767.8678 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 3.2662 | NaN | 18.7299
12410.1292 | 749.6901 | 632.5934 | 501.7609 | 490.3179 | 478.1047 | 589.4729 | 596.8794 | 539.0943 | NaN | NaN | NaN | 780.8142 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.8421 | NaN | 18.8014
12411.1292 | 748.0479 | 632.3078 | 502.2925 | 490.2059 | 477.6597 | 588.7481 | 596.027 | 538.1084 | NaN | NaN | NaN | 779.3484 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 2.8928 | NaN | 17.9502
12412.1292 | 746.3937 | 631.7609 | 501.9887 | 490.2466 | 477.593 | 586.8075 | 593.9778 | 538.2582 | NaN | NaN | NaN | 780.6411 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.7174 | NaN | 16.6969
12413.1292 | 745.6659 | 631.5718 | 501.8816 | 490.2578 | 478.0673 | 585.6503 | 593.5145 | 537.6446 | NaN | NaN | NaN | 756.0695 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.0044 | NaN | 17.9061
12414.1448 | 745.051 | 631.8499 | 501.5245 | 490.3931 | 478.0351 | 586.9176 | 595.3982 | 538.0471 | NaN | NaN | NaN | 745.0327 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.2299 | NaN | 18.0774
12415.1292 | 744.4109 | 631.741 | 502.0329 | 491.264 | 478.7867 | 588.6368 | 598.1984 | 538.5303 | NaN | NaN | NaN | 743.9344 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.6166 | NaN | 17.6723
12416.1292 | 743.2553 | 630.9203 | 501.8093 | 491.3977 | 479.1295 | 588.2944 | 596.8033 | 538.221 | NaN | NaN | NaN | 759.9937 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.809 | NaN | 18.0758
12417.1292 | 743.9468 | 631.04 | 501.1655 | 492.3022 | 479.5077 | 587.983 | 595.6639 | 536.4531 | NaN | NaN | NaN | 787.5164 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 3.706 | NaN | 13.9355
12418.1292 | 745.8441 | 632.0284 | 501.3851 | 493.1579 | 479.4831 | 589.097 | 596.8723 | 538.8176 | NaN | NaN | NaN | 798.4213 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.9233 | NaN | 19.3286
12419.1292 | 746.9045 | 633.4413 | 501.884 | 494.524 | 479.7894 | 589.661 | 597.7662 | 539.6884 | NaN | NaN | NaN | 817.2765 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 1.8097 | NaN | 19.1236
12420.1292 | 744.7124 | 632.6155 | 502.2655 | 495.3989 | 479.9553 | 589.2807 | 595.1027 | 537.8835 | NaN | NaN | NaN | 779.401 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.5097 | NaN | 19.0106
12421.1292 | 742.4096 | 632.2629 | 502.7138 | 495.5317 | 480.4473 | 588.4094 | 592.64 | 537.2919 | NaN | NaN | NaN | 763.6295 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.9313 | NaN | 19.51
12422.1292 | 741.1318 | 631.7444 | 504.2511 | 496.3579 | 480.9997 | 588.2206 | 591.5659 | 536.0065 | NaN | NaN | NaN | 739.9899 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.0534 | NaN | 16.8079
12423.1292 | 739.2128 | 630.689 | 505.4475 | 496.1145 | 480.418 | 589.9567 | 591.2688 | 535.3812 | NaN | NaN | NaN | 721.5116 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 3.155 | NaN | 16.2822
12424.1292 | 736.939 | 631.4352 | 506.313 | 496.2089 | 480.4401 | 591.4458 | 591.038 | 535.1738 | NaN | NaN | NaN | 696.5883 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.8738 | NaN | 16.563
12425.1292 | 734.7804 | 631.2456 | 508.0525 | 496.5757 | 479.7517 | 592.8094 | 589.4286 | 534.6759 | NaN | NaN | NaN | 678.5099 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 2.4622 | NaN | 16.775
12426.1292 | 733.7154 | 629.9054 | 509.5413 | 496.5199 | 479.0487 | 591.9168 | 588.7802 | 533.2063 | NaN | NaN | NaN | 685.8767 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.2106 | NaN | 19.8251
12427.1292 | 733.8604 | 629.8764 | 509.1241 | 496.4286 | 478.7539 | 592.2296 | 590.4615 | 534.5046 | NaN | NaN | NaN | 673.2366 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.439 | NaN | 19.6325
12428.1292 | 733.5278 | 630.9205 | 508.769 | 495.1828 | 478.7554 | 594.942 | 593.3324 | 533.8949 | NaN | NaN | NaN | 687.2923 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 9.5482 | NaN | 16.7399
12429.1292 | 734.0941 | 631.5167 | 508.1975 | 494.3775 | 478.9138 | 596.894 | 594.9085 | 536.3682 | NaN | NaN | NaN | 654.3025 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 3.7313 | NaN | 17.1065
12430.1292 | 735.1675 | 632.9111 | 508.4672 | 493.6729 | 479.9718 | 596.6369 | 595.3824 | 536.4574 | NaN | NaN | NaN | 629.3902 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.9834 | NaN | 15.8845
12431.1292 | 736.0098 | 633.5666 | 508.831 | 493.6468 | 480.8717 | 597.7212 | 594.4244 | 535.6261 | NaN | NaN | NaN | 641.5721 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.222 | NaN | 18.8396
12432.1292 | 736.8506 | 632.8154 | 509.1051 | 493.9031 | 481.0473 | 597.4645 | 593.3871 | 534.9763 | NaN | NaN | NaN | 653.7408 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.1084 | NaN | 18.134
12433.1292 | 738.4938 | 633.5202 | 509.4682 | 494.2863 | 480.0856 | 598.8137 | 593.1258 | 535.4904 | NaN | NaN | NaN | 649.5418 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 3.1809 | NaN | 17.6758
12434.1292 | 740.2974 | 635.2521 | 509.0377 | 495.2379 | 479.8301 | 598.8626 | 593.7207 | 536.2538 | NaN | NaN | NaN | 642.1207 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.4359 | NaN | 18.6593
12435.1292 | 742.0666 | 635.3632 | 510.2466 | 496.4567 | 479.8583 | 598.2023 | 593.3346 | 535.2025 | NaN | NaN | NaN | 645.9203 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 3.5779 | NaN | 16.3254
12436.1292 | 743.2205 | 635.6105 | 511.0881 | 495.8009 | 480.5809 | 599.6267 | 594.0249 | 535.5965 | NaN | NaN | NaN | 663.4619 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.1212 | NaN | 17.5076
12437.1292 | 743.4137 | 635.4428 | 510.5769 | 495.6767 | 481.2098 | 600.9163 | 593.4833 | 536.0517 | NaN | NaN | NaN | 672.2647 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 3.6824 | NaN | 17.5527
12438.1292 | 743.2104 | 635.4431 | 510.501 | 495.2511 | 481.3309 | 600.2434 | 594.7028 | 535.1371 | NaN | NaN | NaN | 676.0973 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.1497 | NaN | 18.4869
12439.1292 | 743.3745 | 635.363 | 511.4341 | 496.1784 | 481.8627 | 600.9266 | 594.5293 | 534.5439 | NaN | NaN | NaN | 702.1978 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 3.3653 | NaN | 19.3527
12440.1292 | 742.5744 | 634.8681 | 511.8211 | 495.6379 | 482.443 | 601.3883 | 594.6578 | 534.2111 | NaN | NaN | NaN | 694.4454 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.7817 | NaN | 17.8181
12441.1292 | 740.875 | 634.6504 | 511.7547 | 495.8552 | 482.0204 | 602.1254 | 595.1682 | 534.6032 | NaN | NaN | NaN | 684.6037 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.8185 | NaN | 17.8329
12442.1292 | 739.0976 | 634.1875 | 511.0062 | 496.1165 | 481.2515 | 602.9817 | 595.059 | 534.597 | NaN | NaN | NaN | 699.2911 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.0533 | NaN | 16.4189
12443.1292 | 740.214 | 634.3856 | 510.6345 | 496.2256 | 480.6627 | 601.0913 | 594.7649 | 533.6809 | NaN | NaN | NaN | 704.2848 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.104 | NaN | 18.7523
12444.1448 | 743.4608 | 635.6663 | 511.0071 | 495.942 | 480.7658 | 600.4582 | 597.4075 | 535.2268 | NaN | NaN | NaN | 723.3588 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.8863 | NaN | 18.5675
12445.1292 | 746.7174 | 637.7428 | 510.5321 | 495.3318 | 480.8289 | 600.7835 | 598.7181 | 535.906 | NaN | NaN | NaN | 718.6345 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.0471 | NaN | 19.48
12446.1292 | 747.4591 | 638.7549 | 510.5588 | 496.1986 | 481.4031 | 602.6844 | 598.5495 | 536.2238 | NaN | NaN | NaN | 719.4941 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.0124 | NaN | 18.4951
12447.1292 | 746.5651 | 638.3221 | 510.8679 | 495.3071 | 482.0398 | 603.7006 | 598.8162 | 537.996 | NaN | NaN | NaN | 688.9131 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.3801 | NaN | 18.5599
12448.1292 | 745.7783 | 638.3492 | 511.2688 | 497.1659 | 482.5615 | 603.6913 | 599.1336 | 538.016 | NaN | NaN | NaN | 669.7863 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.2072 | NaN | 19.1486
12449.1292 | 744.8132 | 639.1081 | 511.9469 | 497.5999 | 481.7993 | 603.4103 | 601.333 | 538.8109 | NaN | NaN | NaN | 646.5647 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.358 | NaN | 18.8008
12450.1292 | 742.9261 | 638.9435 | 512.1888 | 499.1412 | 481.8373 | 604.8763 | 601.2256 | 541.0606 | NaN | NaN | NaN | 625.5755 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.7228 | NaN | 17.3131
12451.1292 | 741.252 | 638.0731 | 512.5067 | 498.92 | 482.0544 | 605.209 | 601.1133 | 541.3933 | NaN | NaN | NaN | 606.1804 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.7305 | NaN | 19.2052
12452.1292 | 741.073 | 637.9181 | 513.2533 | 499.5678 | 481.9944 | 604.6348 | 600.0962 | 540.3544 | NaN | NaN | NaN | 593.6383 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.0867 | NaN | 18.5852
12453.1292 | 740.2025 | 637.9491 | 513.6674 | 498.9099 | 481.4976 | 605.7774 | 601.4016 | 542.1759 | NaN | NaN | NaN | 582.8785 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.5688 | NaN | 17.4456
12454.1292 | 738.0341 | 636.6641 | 513.3225 | 497.9456 | 482.0323 | 605.0565 | 600.2731 | 542.4413 | NaN | NaN | NaN | 568.2359 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.2372 | NaN | 18.6799
12455.1292 | 732.4035 | 633.8874 | 512.6952 | 498.5695 | 480.7581 | 600.4316 | 595.1157 | 539.7835 | NaN | NaN | NaN | 550.4214 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.7142 | NaN | 17.5844
12456.1292 | 725.8059 | 628.5233 | 511.7081 | 498.4511 | 479.1689 | 594.3749 | 588.6379 | 535.8354 | NaN | NaN | NaN | 535.2227 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.0301 | NaN | 17.9809
12457.1292 | 719.2502 | 623.7924 | 510.4596 | 497.9518 | 477.547 | 589.0236 | 582.3837 | 531.5006 | NaN | NaN | NaN | 521.0787 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.5063 | NaN | 18.3869
12458.1292 | 712.7772 | 620.4639 | 508.8234 | 495.8808 | 476.5193 | 583.4736 | 577.0157 | 527.4035 | NaN | NaN | NaN | 506.6238 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.8531 | NaN | 18.0954
12459.1292 | 706.6264 | 613.2007 | 507.3057 | 494.8914 | 475.3602 | 577.3708 | 571.8131 | 523.3854 | NaN | NaN | NaN | 493.4687 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.2752 | NaN | 18.8043
12460.1292 | 700.7906 | 607.0177 | 506.0786 | 492.9342 | 473.1057 | 572.0126 | 567.6907 | 520.5544 | NaN | NaN | NaN | 482.0016 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 2.9186 | NaN | 17.9247
12461.1292 | 695.4869 | 603.4848 | 504.7917 | 491.9554 | 472.6407 | 567.9153 | 563.7761 | 517.9462 | NaN | NaN | NaN | 470.1657 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.261 | NaN | 18.324
12462.1292 | 690.5141 | 599.8292 | 504.316 | 489.7719 | 470.9323 | 564.0284 | 559.7058 | 515.3959 | NaN | NaN | NaN | 460.168 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 2.6074 | NaN | 18.8875
12463.1292 | 685.8698 | 597.0399 | 503.3397 | 488.5121 | 469.353 | 560.0004 | 556.1956 | 512.3039 | NaN | NaN | NaN | 451.3093 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.9636 | NaN | 19.5375
12464.1292 | 681.416 | 594.3275 | 501.3398 | 486.7532 | 468.1996 | 556.2414 | 552.2571 | 509.3099 | NaN | NaN | NaN | 442.1579 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.316 | NaN | 19.7672
12465.1292 | 676.9969 | 592.6875 | 500.0694 | 484.4411 | 467.2404 | 552.5672 | 548.6825 | 506.6806 | NaN | NaN | NaN | 468.7326 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.1677 | NaN | 19.4648
12466.1292 | 672.7107 | 593.5708 | 499.106 | 481.9803 | 465.1696 | 549.0061 | 545.6413 | 503.994 | NaN | NaN | NaN | 497.9187 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.4903 | NaN | 18.3102
12467.1292 | 668.6147 | 592.6839 | 497.7148 | 480.5813 | 463.8628 | 545.7575 | 542.5816 | 501.1461 | NaN | NaN | NaN | 525.18 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.6268 | NaN | 17.9455
12468.1292 | 664.9602 | 589.5316 | 496.5576 | 478.9963 | 462.4747 | 542.9478 | 539.1183 | 499.199 | NaN | NaN | NaN | 526.367 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.8616 | NaN | 19.1187
12469.1292 | 661.3334 | 582.9811 | 495.551 | 477.2878 | 462.0333 | 539.8488 | 536.6716 | 497.5753 | NaN | NaN | NaN | 520.7269 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.3761 | NaN | 19.5708
12470.1292 | 658.0524 | 577.7216 | 493.7925 | 475.3793 | 460.4832 | 537.3238 | 534.3445 | 495.8818 | NaN | NaN | NaN | 528.9443 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 8.3846 | NaN | 17.7077
12471.1292 | 655.0552 | 576.35 | 492.9152 | 473.7595 | 459.2411 | 534.8453 | 531.7535 | 497.7088 | NaN | NaN | NaN | 520.7542 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.6629 | NaN | 18.9711
12472.1292 | 652.2914 | 574.3883 | 491.9245 | 473.0489 | 458.371 | 532.107 | 529.2074 | 497.0387 | NaN | NaN | NaN | 508.0408 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.717 | NaN | 18.3627
12473.1292 | 649.8077 | 573.2204 | 491.4168 | 472.3872 | 458.0074 | 529.7904 | 527.2371 | 495.1425 | NaN | NaN | NaN | 494.6443 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.1612 | NaN | 16.7024
12474.1292 | 647.2904 | 573.3086 | 490.909 | 472.1245 | 456.7422 | 527.122 | 524.259 | 493.7929 | NaN | NaN | NaN | 495.6853 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 1.806 | NaN | 15.3537
12475.1292 | 644.7066 | 568.4397 | 490.2368 | 471.2241 | 455.7304 | 525.4386 | 522.0928 | 491.9257 | NaN | NaN | NaN | 489.0632 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.5849 | NaN | 18.3886
12476.1292 | 642.4488 | 565.5085 | 488.7909 | 469.8522 | 455.2011 | 523.3388 | 520.5575 | 489.8972 | NaN | NaN | NaN | 492.9818 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.4171 | NaN | 19.0154
12477.1292 | 640.2686 | 565.4158 | 488.0886 | 468.6917 | 453.8258 | 521.9261 | 518.7125 | 488.6781 | NaN | NaN | NaN | 497.1334 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 1.931 | NaN | 19.7161
12478.1292 | 637.8711 | 564.2659 | 493.6658 | 468.0041 | 452.6765 | 519.2228 | 516.9154 | 487.0785 | NaN | NaN | NaN | 506.9259 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 3.9254 | NaN | 16.4555
12479.1292 | 635.5764 | 561.0654 | 498.5575 | 468.5562 | 452.2363 | 517.9397 | 514.4871 | 485.9197 | NaN | NaN | NaN | 511.3388 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.7762 | NaN | 18.2517
12480.1292 | 633.2482 | 560.5695 | 501.4988 | 469.8687 | 452.1048 | 517.1745 | 512.7786 | 485.1034 | NaN | NaN | NaN | 523.0242 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 3.9458 | NaN | 17.9692
12481.1292 | 631.1956 | 557.8579 | 506.904 | 471.722 | 452.0908 | 515.5467 | 510.8627 | 483.6967 | NaN | NaN | NaN | 504.3458 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.4856 | NaN | 18.5531
12482.1292 | 629.435 | 557.0303 | 511.9588 | 487.474 | 452.6785 | 514.9134 | 510.059 | 482.1272 | NaN | NaN | NaN | 488.8588 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.4717 | NaN | 16.2596
12483.1292 | 627.4836 | 555.37 | 516.831 | 493.4321 | 452.5495 | 513.6099 | 508.8721 | 481.3374 | NaN | NaN | NaN | 512.3098 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.0753 | NaN | 19.0761
12484.1292 | 625.8032 | 554.9912 | 521.106 | 519.1602 | 452.899 | 512.2945 | 507.8287 | 478.6689 | NaN | NaN | NaN | 508.6546 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 3.8798 | NaN | 18.3461
12485.1292 | 624.2528 | 554.2671 | 525.2968 | 530.8673 | 460.1634 | 511.5639 | 506.7029 | 478.6 | NaN | NaN | NaN | 524.9128 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.5288 | NaN | 16.3545
12486.1292 | 622.8979 | 553.9155 | 530.0096 | 536.4894 | 483.1378 | 510.0903 | 505.2386 | 478.2946 | NaN | NaN | NaN | 518.0714 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 2.5526 | NaN | 14.6695
12487.1292 | 621.6168 | 550.974 | 537.8307 | 552.398 | 497.1387 | 508.9133 | 504.5783 | 477.5544 | NaN | NaN | NaN | 516.6432 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 3.1267 | NaN | 16.224
12488.1292 | 619.9994 | 546.9333 | 548.9892 | 569.3604 | 523.7731 | 508.2522 | 503.3657 | 476.9738 | NaN | NaN | NaN | 516.8318 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 2.9154 | NaN | 17.1066
12489.1292 | 618.5856 | 549.2402 | 552.6616 | 580.7374 | 546.3105 | 506.7766 | 502.2281 | 475.5521 | NaN | NaN | NaN | 512.9354 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.5625 | NaN | 18.6409
12490.1292 | 617.2852 | 549.2931 | 554.7546 | 594.4244 | 572.0043 | 505.923 | 501.2376 | 473.446 | NaN | NaN | NaN | 517.1256 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 3.9019 | NaN | 16.8377
12491.1292 | 615.9006 | 549.3959 | 556.2829 | 602.0375 | 593.7483 | 505.2458 | 500.0561 | 472.9496 | NaN | NaN | NaN | 508.5951 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 1.4976 | NaN | 19.4916
12492.1292 | 614.6044 | 549.8824 | 558.0289 | 626.1697 | 607.9031 | 504.1488 | 498.7448 | 473.1789 | NaN | NaN | NaN | 515.7605 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 3.6391 | NaN | 16.8337
12493.1292 | 613.3497 | 549.2863 | 560.5914 | 632.4464 | 617.292 | 503.0966 | 498.15 | 473.2809 | NaN | NaN | NaN | 505.7433 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.5629 | NaN | 16.1326
12494.1292 | 612.0257 | 550.4467 | 562.6866 | 624.7347 | 608.1369 | 502.7609 | 496.8083 | 471.8303 | NaN | NaN | NaN | 500.3691 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.8052 | NaN | 20.0944
12495.1448 | 610.8985 | 551.4371 | 564.5674 | 619.4668 | 597.9098 | 500.8906 | 496.6285 | 471.3385 | NaN | NaN | NaN | 490.0105 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 1.1005 | NaN | 17.3843
12496.1292 | 609.8187 | 550.6227 | 567.0378 | 630.678 | 589.2955 | 500.1609 | 494.7557 | 471.2151 | NaN | NaN | NaN | 478.9707 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.4576 | NaN | 17.5008
12497.1292 | 608.5113 | 548.7784 | 570.732 | 644.4972 | 581.719 | 499.4051 | 494.0613 | 470.7698 | NaN | NaN | NaN | 464.16 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.6804 | NaN | 19.0331
12498.1292 | 607.4523 | 545.3212 | 574.1565 | 652.4375 | 575.2573 | 499.4611 | 493.9487 | 470.7879 | NaN | NaN | NaN | 452.7549 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.5984 | NaN | 16.3142
12499.1292 | 606.5838 | 545.5799 | 577.1993 | 656.5331 | 569.1938 | 498.5774 | 493.6965 | 470.1366 | NaN | NaN | NaN | 441.5305 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.0876 | NaN | 16.4739
12500.1292 | 605.7412 | 547.3555 | 579.592 | 678.2034 | 566.5403 | 498.1879 | 492.7262 | 469.491 | NaN | NaN | NaN | 428.827 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 1.7045 | NaN | 14.8502
12501.1292 | 604.5594 | 548.9083 | 581.732 | 683.9478 | 569.9827 | 498.059 | 491.7433 | 468.406 | NaN | NaN | NaN | 420.5337 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 1.8751 | NaN | 16.2117
12502.1292 | 603.1703 | 549.0982 | 582.9253 | 686.4061 | 577.195 | 497.4822 | 490.6179 | 467.7059 | NaN | NaN | NaN | 410.0656 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.4672 | NaN | 19.6245
12503.1292 | 601.8276 | 547.7953 | 583.8471 | 707.2891 | 594.5073 | 497.1973 | 490.6531 | 466.8116 | NaN | NaN | NaN | 400.5794 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 3.5663 | NaN | 18.5657
12504.1448 | 600.6544 | 544.2876 | 585.4011 | 708.1525 | 601.7046 | 495.806 | 490.9187 | 465.9326 | NaN | NaN | NaN | 391.4969 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.7485 | NaN | 17.7514
12505.1292 | 599.402 | 541.6365 | 585.863 | 697.848 | 607.4063 | 495.0944 | 491.1996 | 465.1636 | NaN | NaN | NaN | 383.5669 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 3.4948 | NaN | 15.8063
12506.1292 | 598.1788 | 543.0088 | 585.6709 | 706.3196 | 603.7283 | 494.1491 | 490.8529 | 464.248 | NaN | NaN | NaN | 376.0452 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 1.5883 | NaN | 15.953
12507.1448 | 597.0959 | 541.7244 | 586.6714 | 713.0715 | 592.5012 | 493.9019 | 489.7873 | 463.7135 | NaN | NaN | NaN | 370.403 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 2.7246 | NaN | 16.1243
12508.1292 | 596.2667 | 538.3719 | 587.7558 | 719.2967 | 582.3905 | 493.0289 | 489.0128 | 462.6161 | NaN | NaN | NaN | 362.0828 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.0409 | NaN | 17.3946
12509.1292 | 595.2527 | 537.2561 | 590.6116 | 734.5359 | 572.7795 | 492.2869 | 488.432 | 462.3305 | NaN | NaN | NaN | 354.9607 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.824 | NaN | 16.1055
12510.1292 | 594.5257 | 538.5119 | 590.8709 | 741.3548 | 570.7358 | 491.9476 | 486.9885 | 461.6883 | NaN | NaN | NaN | 348.0678 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.8011 | NaN | 16.5541
12511.1292 | 593.8685 | 538.8646 | 592.8628 | 734.1427 | 561.2312 | 491.4779 | 486.9509 | 461.7584 | NaN | NaN | NaN | 342.6039 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 3.2161 | NaN | 14.5298
12512.1292 | 592.8983 | 537.7323 | 593.7745 | 744.0433 | 557.6554 | 491.4443 | 487.4096 | 461.1791 | NaN | NaN | NaN | 338.1554 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.3577 | NaN | 16.4279
12513.1292 | 592.0064 | 536.6616 | 596.1561 | 757.0995 | 562.4791 | 491.6317 | 486.9703 | 460.5984 | NaN | NaN | NaN | 333.5137 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 2.4765 | NaN | 16.6225
12514.1292 | 591.1161 | 538.333 | 597.2089 | 764.626 | 569.0025 | 491.7917 | 486.1349 | 460.5875 | NaN | NaN | NaN | 332.0357 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 1.6645 | NaN | 16.137
12515.1292 | 590.1553 | 535.8547 | 600.6759 | 773.3942 | 562.9054 | 491.9648 | 485.4844 | 460.5761 | NaN | NaN | NaN | 325.9402 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.0067 | NaN | 17.788
12516.1292 | 589.3695 | 534.0383 | 601.2082 | 765.7375 | 567.6408 | 490.5897 | 485.2129 | 460.2241 | NaN | NaN | NaN | 319.5559 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.4852 | NaN | 17.3316
12517.1292 | 588.6276 | 536.1217 | 601.7131 | 766.5274 | 576.9815 | 489.7729 | 484.4306 | 459.7002 | NaN | NaN | NaN | 313.6468 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 3.7859 | NaN | 16.9588
12518.1292 | 587.7423 | 534.9469 | 601.063 | 758.063 | 578.4112 | 489.1239 | 484.1652 | 458.7897 | NaN | NaN | NaN | 308.4239 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.4261 | NaN | 17.649
12519.1292 | 586.9279 | 533.9584 | 603.5741 | 762.0928 | 594.5631 | 488.3637 | 484.3991 | 457.7987 | NaN | NaN | NaN | 303.4713 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.7442 | NaN | 17.5888
12520.1292 | 586.1426 | 533.9351 | 606.1524 | 773.1767 | 598.6544 | 488.2459 | 483.2796 | 457.028 | NaN | NaN | NaN | 298.753 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.2526 | NaN | 17.279
12521.1292 | 585.2094 | 533.5351 | 607.8898 | 760.6836 | 613.5705 | 487.2954 | 483.4517 | 455.9796 | NaN | NaN | NaN | 295.1384 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.3146 | NaN | 17.6738
12522.1292 | 584.4143 | 531.0484 | 609.1139 | 771.6874 | 622.1504 | 487.0304 | 483.4642 | 455.1312 | NaN | NaN | NaN | 290.1633 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.1954 | NaN | 17.7084
12523.1292 | 583.4651 | 528.2942 | 609.4728 | 772.1578 | 622.5407 | 486.885 | 482.9286 | 454.3138 | NaN | NaN | NaN | 286.8481 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.197 | NaN | 17.0813
12524.1292 | 582.4664 | 531.2813 | 610.1092 | 774.1346 | 619.5515 | 486.6389 | 482.4202 | 453.7212 | NaN | NaN | NaN | 283.5524 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.429 | NaN | 18.5112
12525.1292 | 581.5596 | 529.0539 | 609.7875 | 765.0718 | 634.011 | 486.3236 | 481.5581 | 452.9158 | NaN | NaN | NaN | 280.7189 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.2459 | NaN | 17.8824
12526.1292 | 580.9376 | 526.6352 | 610.0961 | 752.5778 | 632.5507 | 486.2852 | 480.1686 | 452.709 | NaN | NaN | NaN | 277.5956 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.068 | NaN | 17.8657
12527.1292 | 580.2482 | 530.4162 | 610.8404 | 746.9453 | 619.3527 | 485.5833 | 479.5811 | 452.2638 | NaN | NaN | NaN | 274.4874 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.8428 | NaN | 17.9689
12528.1292 | 579.3541 | 532.363 | 612.3004 | 742.7735 | 623.4253 | 484.7556 | 479.7332 | 451.871 | NaN | NaN | NaN | 271.6786 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.5167 | NaN | 18.3338
12529.1292 | 578.5673 | 533.5824 | 613.6406 | 739.9078 | 615.0476 | 484.7762 | 479.2056 | 452.0283 | NaN | NaN | NaN | 268.8206 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.7969 | NaN | 18.3045
12530.1292 | 577.9569 | 530.4765 | 616.2683 | 743.9275 | 617.7108 | 484.2536 | 478.9831 | 451.8897 | NaN | NaN | NaN | 266.5776 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.6662 | NaN | 18.6804
12531.1292 | 577.3716 | 530.6951 | 616.4786 | 758.4361 | 624.7558 | 483.9718 | 478.3555 | 451.5207 | NaN | NaN | NaN | 263.8417 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.4976 | NaN | 17.8582
12532.1292 | 576.7455 | 528.6738 | 616.5542 | 749.7344 | 617.4726 | 483.6319 | 477.889 | 452.2482 | NaN | NaN | NaN | 260.7956 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.4204 | NaN | 18.7901
12533.1292 | 576.2056 | 526.6402 | 616.6267 | 755.6491 | 623.78 | 482.7831 | 477.8524 | 451.4844 | NaN | NaN | NaN | 258.3503 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.374 | NaN | 17.9935
12534.1292 | 575.5195 | 525.2761 | 615.6865 | 741.2751 | 628.6655 | 482.1294 | 476.561 | 450.8649 | NaN | NaN | NaN | 255.9504 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.457 | NaN | 18.4606
12535.1292 | 574.6296 | 524.3354 | 614.7015 | 739.7647 | 632.3541 | 481.4947 | 475.9525 | 450.6804 | NaN | NaN | NaN | 253.5515 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.7173 | NaN | 18.6156
12536.1292 | 573.5661 | 525.8446 | 615.247 | 734.8757 | 622.572 | 480.1632 | 475.3444 | 450.2614 | NaN | NaN | NaN | 250.6828 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.3143 | NaN | 19.0751
12537.1292 | 572.4578 | 524.0297 | 617.481 | 721.2691 | 614.1656 | 480.0953 | 474.9351 | 450.3124 | NaN | NaN | NaN | 247.6938 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.0343 | NaN | 18.8756
12538.1292 | 571.5406 | 519.9281 | 617.1871 | 710.1121 | 608.2062 | 480.6406 | 475.3784 | 450.0074 | NaN | NaN | NaN | 245.2418 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.3558 | NaN | 18.6523
12539.1292 | 570.9848 | 522.7145 | 615.7611 | 707.2855 | 601.0484 | 479.63 | 474.5948 | 449.3811 | NaN | NaN | NaN | 243.3433 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.4172 | NaN | 18.9675
12540.1292 | 570.4585 | 523.7637 | 615.4311 | 699.2087 | 596.5145 | 479.3173 | 474.2643 | 449.6969 | NaN | NaN | NaN | 242.2945 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.3477 | NaN | 18.4803
12541.1292 | 569.482 | 525.0569 | 615.0444 | 689.1507 | 596.9872 | 479.1667 | 473.369 | 448.851 | NaN | NaN | NaN | 239.8684 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 3.0624 | NaN | 18.1221
12542.1292 | 568.7602 | 525.7513 | 615.8627 | 679.646 | 596.2486 | 479.0332 | 472.7271 | 448.243 | NaN | NaN | NaN | 238.5656 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 2.723 | NaN | 15.253
12543.1292 | 568.2907 | 525.268 | 615.4904 | 693.5655 | 589.96 | 478.2649 | 472.5404 | 447.8198 | NaN | NaN | NaN | 237.0935 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 3.1952 | NaN | 16.5683
12544.1292 | 567.7528 | 524.7094 | 614.8249 | 721.238 | 593.9519 | 477.8069 | 472.2723 | 447.8378 | NaN | NaN | NaN | 236.2551 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 3.6107 | NaN | 18.8534
12545.1292 | 567.0786 | 523.3458 | 614.6017 | 734.979 | 601.7462 | 477.3185 | 473.3402 | 448.238 | NaN | NaN | NaN | 234.9661 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 3.6895 | NaN | 18.8546
12546.1292 | 566.4598 | 521.5228 | 615.2176 | 721.5058 | 605.5154 | 477.5534 | 473.4418 | 448.9157 | NaN | NaN | NaN | 233.5082 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.4248 | NaN | 15.9495
12547.1292 | 565.6129 | 520.3643 | 616.9493 | 727.6001 | 598.8716 | 477.4535 | 472.9008 | 449.1071 | NaN | NaN | NaN | 232.0765 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.8994 | NaN | 20.1492
12548.1292 | 565.113 | 520.5368 | 617.192 | 724.5501 | 607.7311 | 476.1719 | 473.1018 | 449.4658 | NaN | NaN | NaN | 230.0913 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.8723 | NaN | 19.6975
12549.1292 | 564.7168 | 521.1213 | 617.9262 | 727.771 | 601.0855 | 475.1244 | 472.9305 | 449.6771 | NaN | NaN | NaN | 228.9535 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.9178 | NaN | 15.7682
12550.1292 | 564.0154 | 522.0299 | 620.9654 | 739.2013 | 600.3663 | 475.7419 | 471.9423 | 449.9014 | NaN | NaN | NaN | 227.2998 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.0142 | NaN | 16.3675
12551.1292 | 563.2537 | 522.2941 | 632.2147 | 738.8638 | 593.7921 | 475.7229 | 471.3904 | 449.1513 | NaN | NaN | NaN | 225.3811 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.1472 | NaN | 17.4509
12552.1292 | 562.517 | 522.3076 | 635.2509 | 749.9567 | 588.9696 | 475.3803 | 471.4834 | 449.4004 | NaN | NaN | NaN | 224.8066 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 0.707 | NaN | 17.7208
12553.1292 | 561.7208 | 523.6824 | 633.3563 | 754.0662 | 584.6807 | 474.791 | 472.0151 | 448.5858 | NaN | NaN | NaN | 223.8289 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 0.6968 | NaN | 17.6351
12554.1292 | 561.1723 | 520.1877 | 631.2361 | 751.5008 | 585.4492 | 474.89 | 472.3395 | 448.6357 | NaN | NaN | NaN | 223.474 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 1.4792 | NaN | 16.0213
12555.1292 | 560.8716 | 518.6685 | 628.9648 | 753.7476 | 587.0122 | 474.0835 | 471.408 | 448.5907 | NaN | NaN | NaN | 223.1747 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.8309 | NaN | 18.993
12556.1292 | 560.6112 | 518.8652 | 628.449 | 763.4872 | 583.9084 | 473.0032 | 470.1894 | 448.6873 | NaN | NaN | NaN | 222.3167 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.9461 | NaN | 20.0615
12557.1292 | 560.4391 | 520.1019 | 626.2298 | 756.1308 | 579.4101 | 472.9949 | 470.72 | 448.0527 | NaN | NaN | NaN | 221.6472 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.8023 | NaN | 16.4656
12558.1292 | 559.9684 | 519.4436 | 625.2472 | 744.1015 | 576.6707 | 473.2082 | 470.0862 | 447.3316 | NaN | NaN | NaN | 221.3312 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 2.0273 | NaN | 17.5906
12559.1292 | 559.0186 | 520.1358 | 623.7353 | 743.0704 | 575.3016 | 473.4417 | 469.4286 | 447.438 | NaN | NaN | NaN | 221.3116 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 1.1602 | NaN | 17.9363
12560.1292 | 558.3921 | 518.9927 | 623.0005 | 744.7585 | 575.3995 | 472.7472 | 469.5459 | 446.6366 | NaN | NaN | NaN | 220.4491 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 1.698 | NaN | 17.1456
12561.1292 | 557.8315 | 522.1032 | 622.76 | 749.5505 | 573.7961 | 472.7328 | 468.5998 | 446.0102 | NaN | NaN | NaN | 219.4641 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.6891 | NaN | 19.7694
12562.1292 | 557.4241 | 523.6379 | 623.5901 | 750.4094 | 570.4735 | 472.6445 | 467.3634 | 445.4385 | NaN | NaN | NaN | 218.4683 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 2.7354 | NaN | 18.2566
12563.1292 | 556.9164 | 523.4436 | 623.9826 | 760.1986 | 568.4917 | 472.5232 | 467.7823 | 444.6352 | NaN | NaN | NaN | 217.9661 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 1.9616 | NaN | 17.1642
12564.1292 | 556.6046 | 520.2021 | 622.4427 | 760.6925 | 566.8238 | 471.1639 | 467.965 | 443.6622 | NaN | NaN | NaN | 217.3698 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 0.4616 | NaN | 20.0329
12565.1292 | 556.2738 | 521.1946 | 622.8776 | 740.1588 | 564.6679 | 470.5308 | 467.1026 | 442.7914 | NaN | NaN | NaN | 217.0784 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.72 | NaN | 17.366
12566.1292 | 555.8921 | 520.3996 | 622.694 | 726.0228 | 563.4136 | 469.4962 | 466.5381 | 442.4694 | NaN | NaN | NaN | 216.4891 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -0.8081 | NaN | 19.7731
12567.1292 | 555.5166 | 520.4439 | 624.016 | 712.2491 | 562.6368 | 468.5762 | 465.7552 | 442.2735 | NaN | NaN | NaN | 215.2518 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 2.2825 | NaN | 14.5491
12568.1292 | 555.0994 | 521.5886 | 624.2651 | 705.1635 | 561.1262 | 469.304 | 465.7891 | 441.9062 | NaN | NaN | NaN | 214.8532 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.4643 | NaN | 18.1278
12569.1292 | 554.4145 | 521.4792 | 628.8078 | 695.086 | 560.341 | 469.3571 | 464.471 | 441.1714 | NaN | NaN | NaN | 213.4138 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 0.3492 | NaN | 18.5899
12570.1292 | 553.6949 | 519.3389 | 633.1092 | 698.1508 | 558.2164 | 468.4417 | 464.4645 | 441.0961 | NaN | NaN | NaN | 211.8809 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -0.9721 | NaN | 13.4657
12571.1292 | 553.2221 | 516.0958 | 631.5185 | 708.6942 | 555.9954 | 468.0949 | 464.3968 | 441.265 | NaN | NaN | NaN | 210.4706 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.6969 | NaN | 17.6541
12572.1292 | 552.6857 | 515.6391 | 629.5561 | 706.5393 | 557.4446 | 467.5572 | 464.403 | 441.1072 | NaN | NaN | NaN | 210.3768 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 0.921 | NaN | 16.8599
12573.1292 | 552.0828 | 516.4282 | 628.5232 | 710.9226 | 557.7894 | 466.717 | 464.0264 | 440.2498 | NaN | NaN | NaN | 209.6573 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 2.611 | NaN | 17.8981
12574.1292 | 551.5546 | 516.2388 | 625.6896 | 699.8837 | 556.4014 | 466.0572 | 463.0438 | 440.063 | NaN | NaN | NaN | 208.7124 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.1245 | NaN | 19.0287
12575.1292 | 551.0568 | 515.2821 | 623.7713 | 717.9297 | 555.0986 | 466.2673 | 462.5677 | 439.9474 | NaN | NaN | NaN | 208.0057 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -0.4007 | NaN | 19.0203
12576.1292 | 550.5614 | 513.6207 | 622.7775 | 720.0968 | 553.8089 | 466.8029 | 463.4392 | 439.9928 | NaN | NaN | NaN | 207.9297 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.2943 | NaN | 18.3056
12577.1292 | 549.8717 | 511.7931 | 620.7661 | 720.2075 | 552.2977 | 466.6001 | 462.0833 | 439.0235 | NaN | NaN | NaN | 207.038 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 0.8494 | NaN | 19.0915
12578.1292 | 549.1398 | 508.578 | 619.3052 | 712.9749 | 552.1423 | 465.979 | 460.8458 | 439.4293 | NaN | NaN | NaN | 207.0427 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 0.081 | NaN | 19.44
12579.1292 | 548.5066 | 509.0655 | 618.2006 | 707.5839 | 551.5299 | 466.1432 | 460.4028 | 439.5656 | NaN | NaN | NaN | 207.3874 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.5756 | NaN | 19.0518
12580.1292 | 548.0982 | 509.9057 | 618.1278 | 719.9886 | 549.8112 | 466.013 | 459.9529 | 439.1088 | NaN | NaN | NaN | 207.5739 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 2.6158 | NaN | 18.6595
12581.1292 | 547.4814 | 508.9079 | 617.7667 | 721.1721 | 548.4787 | 465.2339 | 459.7856 | 438.3104 | NaN | NaN | NaN | 207.2311 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -0.098 | NaN | 17.9172
12582.1292 | 546.8407 | 507.693 | 617.5028 | 714.5227 | 548.2035 | 465.0231 | 459.0751 | 437.663 | NaN | NaN | NaN | 206.838 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 3.3815 | NaN | 16.4682
12583.1292 | 545.9654 | 508.7484 | 617.3793 | 716.1406 | 547.3487 | 464.7647 | 459.6905 | 437.2357 | NaN | NaN | NaN | 206.4975 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 0.0884 | NaN | 19.787
12584.1292 | 545.4012 | 507.953 | 617.132 | 713.1239 | 546.0549 | 464.0818 | 459.6575 | 436.3458 | NaN | NaN | NaN | 206.6745 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.0478 | NaN | 15.5777
12585.1292 | 544.9608 | 507.7592 | 617.2544 | 716.2671 | 545.3779 | 463.1091 | 459.4673 | 435.8925 | NaN | NaN | NaN | 207.0026 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -0.3778 | NaN | 16.3391
12586.1292 | 544.0334 | 510.4371 | 619.0578 | 706.6284 | 549.5524 | 462.6043 | 459.2217 | 435.4099 | NaN | NaN | NaN | 205.8336 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 2.1876 | NaN | 14.2275
12587.1292 | 543.5246 | 511.4803 | 618.5059 | 706.3162 | 549.8043 | 462.4071 | 459.445 | 434.7071 | NaN | NaN | NaN | 204.7145 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 2.0594 | NaN | 17.05
12588.1292 | 542.9738 | 508.1976 | 617.7049 | 709.6526 | 550.0206 | 462.4292 | 458.9548 | 434.3482 | NaN | NaN | NaN | 203.4764 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 1.9667 | NaN | 16.8285
12589.1292 | 542.5727 | 504.864 | 618.4301 | 710.5501 | 548.7929 | 462.2302 | 458.4908 | 434.0803 | NaN | NaN | NaN | 202.6699 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.5219 | NaN | 16.2045
12590.1292 | 542.078 | 501.7461 | 621.4119 | 714.3779 | 547.1559 | 461.5416 | 458.0697 | 433.5975 | NaN | NaN | NaN | 201.1277 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -0.1223 | NaN | 18.1288
12591.1292 | 541.6616 | 501.8561 | 620.2033 | 701.4787 | 546.2664 | 460.8228 | 456.8017 | 433.1389 | NaN | NaN | NaN | 200.4951 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 3.9168 | NaN | 18.7547
12592.1292 | 541.1974 | 499.6125 | 618.9751 | 691.5477 | 545.5073 | 460.4007 | 456.978 | 432.6483 | NaN | NaN | NaN | 199.7197 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 1.9415 | NaN | 17.9114
12593.1292 | 540.8645 | 496.7023 | 619.1593 | 683.6766 | 544.9383 | 460.289 | 457.5484 | 432.8333 | NaN | NaN | NaN | 199.6996 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 0.7397 | NaN | 16.5422
12594.1292 | 540.6988 | 496.9736 | 619.682 | 684.968 | 544.4335 | 460.1265 | 457.3922 | 432.8006 | NaN | NaN | NaN | 200.0757 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 3.7935 | NaN | 17.4405
12595.1292 | 540.3071 | 496.8443 | 618.6302 | 691.2529 | 544.685 | 459.7718 | 457.1385 | 432.4857 | NaN | NaN | NaN | 200.2102 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -0.6678 | NaN | 17.9161
12596.1292 | 540.091 | 497.7245 | 617.9711 | 703.6053 | 544.8619 | 459.1276 | 456.083 | 432.4807 | NaN | NaN | NaN | 199.9267 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 3.6421 | NaN | 17.8744
12597.1292 | 539.8681 | 499.9971 | 617.7267 | 712.533 | 544.1589 | 459.1613 | 456.2246 | 432.2079 | NaN | NaN | NaN | 199.6489 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 0.4536 | NaN | 17.0357
12598.1292 | 539.5848 | 501.0645 | 621.4445 | 718.7726 | 543.8779 | 458.8728 | 455.9818 | 431.9352 | NaN | NaN | NaN | 199.5055 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 3.8117 | NaN | 15.321
12599.1292 | 539.3722 | 503.3239 | 619.4213 | 725.9656 | 544.0445 | 459.0229 | 455.3119 | 432.1921 | NaN | NaN | NaN | 199.5358 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -0.072 | NaN | 16.3293
12600.1292 | 538.8273 | 502.3724 | 619.0467 | 734.0289 | 543.4862 | 458.8737 | 454.7417 | 431.9662 | NaN | NaN | NaN | 198.9931 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 0.8655 | NaN | 19.839
12601.1292 | 537.7296 | 502.064 | 621.0315 | 733.5977 | 556.9514 | 458.2609 | 454.1691 | 431.4917 | NaN | NaN | NaN | 198.3669 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.2921 | NaN | 15.9765
12602.1292 | 536.7707 | 503.4825 | 620.4812 | 730.5255 | 578.8926 | 457.3245 | 454.7377 | 431.0584 | NaN | NaN | NaN | 198.4479 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 0.7894 | NaN | 17.2426
12603.1292 | 535.9521 | 504.8611 | 622.7638 | 729.0527 | 604.1165 | 457.3453 | 454.9727 | 431.001 | NaN | NaN | NaN | 199.3124 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.2043 | NaN | 19.4241
12604.1292 | 535.3845 | 502.4963 | 622.6766 | 723.9639 | 622.4748 | 456.7164 | 455.017 | 430.3954 | NaN | NaN | NaN | 199.276 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 0.8212 | NaN | 18.2608
12605.1292 | 535.0894 | 500.9942 | 620.3535 | 720.7391 | 613.7658 | 456.2139 | 455.7271 | 429.7447 | NaN | NaN | NaN | 198.7036 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 0.844 | NaN | 15.9013
12606.1292 | 534.6764 | 502.9581 | 618.9098 | 723.3794 | 606.6088 | 456.7233 | 455.981 | 429.5454 | NaN | NaN | NaN | 198.5232 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 2.4625 | NaN | 18.0027
12607.1292 | 534.3909 | 500.241 | 618.6354 | 716.8817 | 601.1304 | 456.5986 | 456.2206 | 429.3638 | NaN | NaN | NaN | 198.6987 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -0.2354 | NaN | 16.3215
12608.1292 | 533.9346 | 499.8666 | 618.1651 | 714.2576 | 601.2749 | 455.936 | 455.1499 | 428.8664 | NaN | NaN | NaN | 197.7481 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.3164 | NaN | 15.352
12609.1292 | 533.5607 | 501.0602 | 618.1307 | 707.679 | 600.564 | 456.2654 | 453.9835 | 428.9548 | NaN | NaN | NaN | 196.7901 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -0.0663 | NaN | 16.7251
12610.1292 | 533.0591 | 498.641 | 617.7943 | 702.567 | 593.5048 | 456.211 | 454.0946 | 428.631 | NaN | NaN | NaN | 197.1459 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.7819 | NaN | 17.7173
12611.1292 | 532.4315 | 500.4647 | 617.6861 | 711.5166 | 593.1732 | 455.5073 | 453.9281 | 428.2556 | NaN | NaN | NaN | 195.8701 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 1.7684 | NaN | 18.0962
12612.1292 | 531.6982 | 501.3191 | 618.8069 | 718.5755 | 594.6614 | 455.5397 | 453.3723 | 427.8438 | NaN | NaN | NaN | 196.2622 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 1.3858 | NaN | 20.2434
12613.1292 | 531.2469 | 500.4212 | 617.4271 | 734.8825 | 589.8557 | 455.3321 | 452.5567 | 427.5886 | NaN | NaN | NaN | 195.5346 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 2.5616 | NaN | 16.4758
12614.1292 | 530.7825 | 501.1681 | 616.5972 | 726.7823 | 588.8377 | 455.1434 | 452.097 | 427.1946 | NaN | NaN | NaN | 195.1671 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -0.854 | NaN | 15.5071
12615.1292 | 530.4829 | 501.3977 | 615.3567 | 724.2362 | 588.4274 | 453.9382 | 452.332 | 427.0883 | NaN | NaN | NaN | 193.9556 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 3.942 | NaN | 18.3677
12616.1292 | 530.1959 | 501.8273 | 620.659 | 733.9853 | 585.1578 | 453.1337 | 452.6653 | 427.1597 | NaN | NaN | NaN | 192.7253 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -0.6858 | NaN | 17.7416
12617.1292 | 529.8042 | 501.4266 | 623.0005 | 729.8354 | 580.799 | 453.5831 | 452.3002 | 426.8953 | NaN | NaN | NaN | 192.1431 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 3.1605 | NaN | 18.5484
12618.1292 | 529.4647 | 499.1991 | 622.1137 | 737.0611 | 577.0834 | 453.3937 | 451.855 | 426.5422 | NaN | NaN | NaN | 192.3363 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 0.7792 | NaN | 17.061
12619.1292 | 528.8813 | 499.358 | 620.0738 | 732.8295 | 573.6603 | 453.7069 | 451.6769 | 426.09 | NaN | NaN | NaN | 193.6374 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 3.1227 | NaN | 17.1356
12620.1292 | 528.1994 | 498.9809 | 621.5617 | 739.9414 | 571.0553 | 453.7071 | 450.7304 | 425.7733 | NaN | NaN | NaN | 193.5872 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 2.8038 | NaN | 17.5932
12621.1292 | 527.5359 | 498.5996 | 622.0947 | 740.9427 | 568.2367 | 453.2748 | 451.0222 | 425.5646 | NaN | NaN | NaN | 192.3835 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -1.0396 | NaN | 16.8355
12622.1292 | 526.9987 | 494.3538 | 620.9108 | 744.7076 | 565.6075 | 453.2178 | 450.8075 | 425.3315 | NaN | NaN | NaN | 191.1864 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.1076 | NaN | 18.4659
12623.1292 | 526.4155 | 492.5818 | 620.6716 | 739.4803 | 563.1955 | 452.1783 | 450.0986 | 425.1962 | NaN | NaN | NaN | 191.9021 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -1.3455 | NaN | 17.4357
12624.1292 | 525.755 | 489.7439 | 623.2065 | 739.7857 | 562.041 | 451.5242 | 450.4124 | 424.5276 | NaN | NaN | NaN | 191.6887 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 3.8303 | NaN | 16.6882
12625.1292 | 525.0744 | 491.1264 | 621.3515 | 747.4218 | 560.1691 | 450.7266 | 450.4866 | 424.7323 | NaN | NaN | NaN | 191.9059 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -0.1263 | NaN | 17.9605
12626.1292 | 524.7984 | 492.5132 | 619.7891 | 738.3019 | 558.429 | 450.533 | 449.7734 | 424.4095 | NaN | NaN | NaN | 193.1221 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 2.5475 | NaN | 17.0919
12627.1292 | 524.4901 | 492.3217 | 618.3422 | 737.2714 | 557.0004 | 449.4569 | 448.973 | 424.2449 | NaN | NaN | NaN | 192.7194 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 1.8762 | NaN | 16.8825
12628.1292 | 524.3848 | 489.6582 | 617.3526 | 723.9901 | 556.6419 | 448.933 | 448.5855 | 424.0895 | NaN | NaN | NaN | 192.9468 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -0.5218 | NaN | 17.625
12629.1292 | 524.268 | 488.0708 | 617.2871 | 709.5697 | 555.9102 | 449.1829 | 448.0929 | 424.0759 | NaN | NaN | NaN | 191.7138 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.0098 | NaN | 16.7132
12630.1292 | 523.857 | 488.2611 | 616.9446 | 716.2611 | 554.9734 | 449.4316 | 447.2698 | 424.2956 | NaN | NaN | NaN | 190.3373 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 0.2438 | NaN | 16.9974
12631.1292 | 523.4559 | 488.1337 | 618.7851 | 718.6495 | 555.2906 | 448.9676 | 446.9778 | 424.1657 | NaN | NaN | NaN | 189.2804 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.1567 | NaN | 17.4156
12632.1292 | 523.0159 | 487.5592 | 619.5669 | 719.8225 | 554.531 | 449.1242 | 446.3947 | 423.7661 | NaN | NaN | NaN | 188.2948 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -0.35 | NaN | 18.5018
12633.1292 | 522.7916 | 489.2817 | 618.7377 | 724.4602 | 553.3126 | 448.6231 | 445.4795 | 423.1631 | NaN | NaN | NaN | 188.7382 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 2.2988 | NaN | 16.3761
12634.1292 | 522.5545 | 488.7033 | 617.4759 | 726.6364 | 551.983 | 448.3894 | 445.0228 | 422.9987 | NaN | NaN | NaN | 189.098 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 1.9253 | NaN | 17.6533
12635.1292 | 522.2961 | 489.6014 | 616.5768 | 730.465 | 550.844 | 448.3246 | 444.7619 | 422.7768 | NaN | NaN | NaN | 188.1357 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 2.3177 | NaN | 13.426
12636.1292 | 522.2543 | 490.4227 | 617.1385 | 720.1016 | 551.3365 | 448.584 | 444.8097 | 422.4095 | NaN | NaN | NaN | 188.3705 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.9083 | NaN | 16.6708
12637.1292 | 522.1822 | 490.0908 | 617.3403 | 721.1517 | 550.2556 | 448.0879 | 444.3101 | 421.7579 | NaN | NaN | NaN | 189.0472 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 1.4822 | NaN | 17.6866
12638.1292 | 521.8354 | 489.3002 | 618.8473 | 731.6513 | 548.9716 | 447.5719 | 444.3087 | 421.9258 | NaN | NaN | NaN | 189.4246 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.0362 | NaN | 17.1388
12639.1292 | 521.5657 | 486.4605 | 618.4308 | 725.508 | 547.8702 | 445.7555 | 443.6436 | 421.7492 | NaN | NaN | NaN | 187.726 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 0.2229 | NaN | 15.048
12640.1292 | 521.381 | 487.4783 | 619.5678 | 723.6684 | 547.3948 | 446.3665 | 443.9493 | 422.0931 | NaN | NaN | NaN | 186.9899 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 7.4554 | NaN | 14.8817
12641.1292 | 520.8833 | 487.627 | 618.9806 | 718.7065 | 546.7029 | 446.7832 | 442.9097 | 421.7904 | NaN | NaN | NaN | 185.2608 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 3.0856 | NaN | 17.7936
12642.1292 | 520.0882 | 487.8897 | 619.1836 | 731.589 | 546.1966 | 446.593 | 442.9881 | 421.8932 | NaN | NaN | NaN | 184.4812 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 2.0962 | NaN | 18.9122
12643.1292 | 519.6639 | 487.5575 | 619.3423 | 720.1131 | 546.0212 | 446.1073 | 442.7441 | 421.3571 | NaN | NaN | NaN | 184.2397 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.1332 | NaN | 18.8208
12644.1292 | 519.0344 | 489.3702 | 619.3566 | 733.8864 | 544.9567 | 445.9871 | 442.8832 | 420.593 | NaN | NaN | NaN | 184.4965 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -0.1784 | NaN | 17.7942
12645.1292 | 518.3172 | 490.3569 | 619.0408 | 717.4061 | 544.7885 | 445.3853 | 442.2875 | 420.3548 | NaN | NaN | NaN | 184.6604 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.6813 | NaN | 17.7872
12646.1292 | 517.6594 | 488.4263 | 617.6117 | 714.0602 | 544.6788 | 445.3605 | 441.0675 | 420.2832 | NaN | NaN | NaN | 184.6233 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -0.1353 | NaN | 18.5088
12647.1292 | 517.2707 | 487.1397 | 616.6823 | 710.516 | 545.4858 | 444.861 | 441.4168 | 420.0067 | NaN | NaN | NaN | 184.3055 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 2.8463 | NaN | 15.3723
12648.1292 | 516.8264 | 486.6525 | 615.6437 | 708.9293 | 545.8395 | 444.7775 | 440.8715 | 419.9886 | NaN | NaN | NaN | 184.2517 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 2.1984 | NaN | 18.6268
12649.1292 | 516.3341 | 486.4948 | 616.2216 | 711.5216 | 546.1301 | 444.8007 | 441.5911 | 419.6067 | NaN | NaN | NaN | 184.7653 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 2.8446 | NaN | 18.0794
12650.1292 | 515.7239 | 489.4284 | 616.3817 | 708.185 | 545.5967 | 444.1383 | 441.6706 | 419.3262 | NaN | NaN | NaN | 185.474 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.5266 | NaN | 16.9844
12651.1292 | 515.3116 | 488.8143 | 615.1251 | 701.2665 | 545.6208 | 443.5278 | 441.6109 | 418.892 | NaN | NaN | NaN | 185.84 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 0.8723 | NaN | 18.3859
12652.1292 | 514.8846 | 486.9819 | 614.5922 | 706.6145 | 546.1116 | 442.7331 | 441.4283 | 418.5233 | NaN | NaN | NaN | 185.7959 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.3481 | NaN | 19.2539
12653.1292 | 514.4885 | 486.5126 | 621.8164 | 711.1055 | 546.7595 | 442.6308 | 441.0679 | 418.3722 | NaN | NaN | NaN | 185.8263 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 0.8629 | NaN | 17.0884
12654.1292 | 514.0326 | 486.4678 | 619.8921 | 714.2944 | 547.111 | 442.7024 | 440.8553 | 418.081 | NaN | NaN | NaN | 185.3079 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.5409 | NaN | 17.7555
12655.1292 | 513.5626 | 487.5001 | 618.7822 | 731.4328 | 545.9639 | 442.8335 | 440.7897 | 418.0225 | NaN | NaN | NaN | 184.8594 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 1.0459 | NaN | 17.0523
12656.1292 | 513.2315 | 488.5532 | 617.7299 | 731.9282 | 545.2124 | 442.1273 | 440.2863 | 417.6972 | NaN | NaN | NaN | 182.9973 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.7976 | NaN | 14.2471
12657.1292 | 512.7357 | 489.918 | 617.9587 | 724.6258 | 545.6452 | 441.7874 | 440.3062 | 417.2315 | NaN | NaN | NaN | 181.5758 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 3.1746 | NaN | 17.6293
12658.1292 | 512.3982 | 491.5134 | 616.7959 | 716.5515 | 551.5352 | 441.6678 | 439.5826 | 416.9464 | NaN | NaN | NaN | 180.3875 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 3.5295 | NaN | 14.9543
12659.1292 | 512.0406 | 488.2788 | 617.4957 | 737.2335 | 549.9421 | 441.782 | 439.7301 | 416.8376 | NaN | NaN | NaN | 180.5513 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.2857 | NaN | 18.6876
12660.1292 | 511.8811 | 485.4977 | 620.1269 | 745.2297 | 547.6455 | 441.4884 | 439.73 | 416.7661 | NaN | NaN | NaN | 180.8675 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 2.2621 | NaN | 16.5753
12661.1292 | 511.5505 | 485.2498 | 620.3691 | 746.6118 | 546.1798 | 440.9908 | 439.0291 | 416.6665 | NaN | NaN | NaN | 179.8371 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.0238 | NaN | 17.4343
12662.1292 | 511.1796 | 485.1349 | 620.4196 | 746.2108 | 544.5206 | 440.8498 | 438.3962 | 416.6581 | NaN | NaN | NaN | 179.364 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 1.5333 | NaN | 17.7991
12663.1292 | 510.8358 | 483.6113 | 619.2152 | 743.0583 | 543.6458 | 440.2551 | 437.4576 | 416.4059 | NaN | NaN | NaN | 179.2153 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.6888 | NaN | 18.0424
12664.1292 | 510.7141 | 485.2738 | 618.8787 | 734.9741 | 573.2103 | 440.2583 | 437.3872 | 415.8737 | NaN | NaN | NaN | 178.7104 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 1.0097 | NaN | 16.7093
12665.1292 | 510.3366 | 483.3915 | 617.7206 | 726.0674 | 562.9772 | 439.8127 | 436.8795 | 415.3631 | NaN | NaN | NaN | 178.292 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.3462 | NaN | 18.4784
12666.1292 | 509.8858 | 482.3651 | 617.4738 | 738.2514 | 557.5063 | 439.4639 | 437.5662 | 415.5662 | NaN | NaN | NaN | 178.1068 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 2.7421 | NaN | 17.4409
12667.1292 | 509.4508 | 481.6928 | 615.787 | 734.1381 | 553.6001 | 440.1711 | 437.3407 | 414.8861 | NaN | NaN | NaN | 178.9527 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 3.4986 | NaN | 16.8841
12668.1292 | 509.303 | 479.9226 | 615.4353 | 726.4548 | 552.3388 | 440.1262 | 436.514 | 414.9269 | NaN | NaN | NaN | 179.6837 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.5612 | NaN | 15.2811
12669.1292 | 508.8858 | 480.9631 | 617.2877 | 719.4536 | 551.546 | 439.0466 | 436.8345 | 414.7279 | NaN | NaN | NaN | 180.1661 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.4238 | NaN | 17.649
12670.1292 | 508.6872 | 477.997 | 616.6511 | 714.072 | 548.7927 | 438.6303 | 436.4551 | 414.569 | NaN | NaN | NaN | 180.3002 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 3.2849 | NaN | 17.5363
12671.1292 | 508.5943 | 477.2729 | 617.9047 | 717.2443 | 547.6691 | 438.7639 | 436.168 | 414.859 | NaN | NaN | NaN | 180.7791 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 3.6747 | NaN | 19.3606
12672.1292 | 508.5602 | 475.6819 | 619.7159 | 725.3403 | 548.635 | 439.4302 | 436.1448 | 415.1611 | NaN | NaN | NaN | 180.692 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 3.365 | NaN | 15.0288
12673.1292 | 508.4664 | 476.5839 | 618.0026 | 722.4691 | 547.9066 | 438.8303 | 435.9124 | 414.735 | NaN | NaN | NaN | 180.0774 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.0781 | NaN | 18.4998
12674.1292 | 507.9168 | 479.9407 | 616.7446 | 719.7152 | 546.7213 | 438.3265 | 435.3614 | 414.3735 | NaN | NaN | NaN | 179.5764 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 3.5081 | NaN | 15.4924
12675.1292 | 507.31 | 480.0845 | 616.6968 | 721.0457 | 548.3488 | 437.5608 | 434.6326 | 413.765 | NaN | NaN | NaN | 179.0156 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.1264 | NaN | 17.2685
12676.1292 | 506.8083 | 479.9953 | 615.5906 | 732.3053 | 547.1388 | 437.0444 | 435.4757 | 413.5996 | NaN | NaN | NaN | 178.4933 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 6.1159 | NaN | 17.3482
12677.1292 | 506.4871 | 479.1525 | 615.217 | 731.3104 | 550.7988 | 437.6005 | 435.7988 | 413.4798 | NaN | NaN | NaN | 177.6729 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 2.0584 | NaN | 16.9872
12678.1292 | 506.1596 | 479.5385 | 615.4731 | 723.839 | 547.8401 | 437.529 | 435.4644 | 413.8703 | NaN | NaN | NaN | 176.9956 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 3.5589 | NaN | 16.756
12679.1292 | 505.5638 | 477.9185 | 614.8508 | 723.3639 | 547.0405 | 437.603 | 436.0016 | 413.4048 | NaN | NaN | NaN | 176.5005 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 3.1689 | NaN | 15.6295
12680.1292 | 504.7804 | 476.3366 | 615.5398 | 722.5734 | 546.4103 | 437.3912 | 435.5595 | 413.109 | NaN | NaN | NaN | 176.3678 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 1.7555 | NaN | 18.0769
12681.1292 | 504.1673 | 474.9635 | 617.0023 | 717.7372 | 552.5569 | 437.721 | 435.2243 | 412.4463 | NaN | NaN | NaN | 175.1396 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.169 | NaN | 16.2224
12682.1292 | 503.6298 | 476.6403 | 617.1985 | 730.7174 | 551.6328 | 437.4988 | 434.6985 | 412.2495 | NaN | NaN | NaN | 174.5047 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.0099 | NaN | 19.2724
12683.1448 | 503.2183 | 477.8827 | 616.7108 | 732.3209 | 547.3841 | 436.9284 | 434.2097 | 412.0653 | NaN | NaN | NaN | 173.4364 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -1.0699 | NaN | 17.4362
12684.1292 | 502.6931 | 479.5429 | 615.9839 | 745.0337 | 545.7338 | 436.4892 | 434.4276 | 411.5829 | NaN | NaN | NaN | 172.9355 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 2.7001 | NaN | 17.9805
12685.1292 | 502.3412 | 478.6411 | 618.2479 | 743.2646 | 544.4047 | 436.24 | 434.6827 | 410.8974 | NaN | NaN | NaN | 172.2503 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.899 | NaN | 16.9898
12686.1292 | 502.0808 | 479.3575 | 618.2958 | 744.9219 | 541.888 | 435.892 | 434.1017 | 410.3803 | NaN | NaN | NaN | 172.4816 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 1.9864 | NaN | 15.9744
12687.1448 | 501.8777 | 474.3426 | 618.0863 | 738.8804 | 539.784 | 436.2561 | 434.6442 | 409.9448 | NaN | NaN | NaN | 172.6165 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -1.8044 | NaN | 16.2463
12688.1292 | 501.8198 | 472.8144 | 616.0498 | 739.5178 | 539.8406 | 435.7149 | 434.6424 | 409.5974 | NaN | NaN | NaN | 172.1503 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 2.4759 | NaN | 16.5352
12689.1448 | 501.4969 | 471.1447 | 614.8369 | 738.5494 | 540.5931 | 435.5858 | 434.8831 | 409.4302 | NaN | NaN | NaN | 171.3317 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.5123 | NaN | 17.1447
12690.1292 | 501.2037 | 473.8909 | 614.3794 | 732.7733 | 541.4473 | 435.852 | 434.2129 | 409.2533 | NaN | NaN | NaN | 171.1615 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 2.4401 | NaN | 15.0041
12691.1448 | 501.0361 | 473.7761 | 618.0704 | 726.85 | 551.3947 | 436.0959 | 433.5929 | 409.0312 | NaN | NaN | NaN | 171.1752 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 0.4826 | NaN | 17.2309
12692.1292 | 500.749 | 472.8304 | 618.7693 | 722.0741 | 557.5435 | 436.2415 | 433.4687 | 409.1363 | NaN | NaN | NaN | 171.573 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.1767 | NaN | 17.2403
12693.1292 | 500.5146 | 474.9591 | 616.6005 | 728.0785 | 558.9313 | 436.0481 | 433.404 | 409.0506 | NaN | NaN | NaN | 172.0032 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 3.17 | NaN | 15.7756
12694.1292 | 499.9825 | 472.7643 | 616.1711 | 726.6643 | 581.2822 | 435.5778 | 433.4391 | 408.9173 | NaN | NaN | NaN | 171.9379 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 0.4151 | NaN | 11.2579
12695.1292 | 499.5232 | 472.9582 | 614.8828 | 728.4621 | 605.4655 | 435.1042 | 433.0172 | 408.6977 | NaN | NaN | NaN | 171.6262 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -1.6463 | NaN | 15.3097
12696.1292 | 499.1618 | 472.6208 | 610.9764 | 735.5614 | 630.8737 | 435.2442 | 432.6963 | 408.5438 | NaN | NaN | NaN | 171.5718 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.5214 | NaN | 17.1652
12697.1292 | 498.9948 | 474.9506 | 609.5159 | 738.0256 | 645.2576 | 434.9203 | 432.0497 | 408.4033 | NaN | NaN | NaN | 171.7832 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 3.4253 | NaN | 16.1362
12698.1292 | 498.6041 | 474.631 | 609.1872 | 735.2324 | 652.2334 | 434.3246 | 431.8491 | 408.4 | NaN | NaN | NaN | 171.3509 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 1.3356 | NaN | 13.0676
12699.1292 | 498.2654 | 472.0932 | 608.0015 | 739.0757 | 657.5556 | 433.4643 | 431.4996 | 408.2722 | NaN | NaN | NaN | 171.524 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 0.7442 | NaN | 16.9056
12700.1292 | 498.1746 | 470.7688 | 609.3216 | 728.087 | 677.6652 | 433.1597 | 431.5176 | 408.0301 | NaN | NaN | NaN | 171.8068 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -1.8017 | NaN | 15.1909
12701.1292 | 497.7961 | 469.8204 | 608.612 | 723.9601 | 687.8774 | 432.4643 | 431.92 | 407.7342 | NaN | NaN | NaN | 173.0483 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 2.6833 | NaN | 16.8574
12702.1292 | 497.3715 | 468.9606 | 607.8475 | 724.7479 | 674.907 | 432.764 | 431.1381 | 407.6796 | NaN | NaN | NaN | 173.6408 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 3.9334 | NaN | 14.4036
12703.1292 | 497.067 | 467.9453 | 606.6755 | 724.118 | 663.6073 | 432.9437 | 430.2815 | 407.5119 | NaN | NaN | NaN | 173.7975 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 3.3509 | NaN | 18.7374
12704.1292 | 496.9259 | 467.7328 | 607.5943 | 716.7336 | 670.9115 | 432.4997 | 428.9775 | 406.9895 | NaN | NaN | NaN | 174.1002 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 0.0611 | NaN | 16.2867
12705.1292 | 496.7087 | 465.7763 | 608.1774 | 721.0317 | 682.2373 | 431.8217 | 429.0059 | 406.5318 | NaN | NaN | NaN | 174.3142 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -0.6138 | NaN | 16.1799
12706.1292 | 496.5469 | 464.9772 | 612.3314 | 725.3236 | 687.9467 | 432.1899 | 428.6695 | 406.1727 | NaN | NaN | NaN | 174.1889 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -1.0639 | NaN | 17.4792
12707.1292 | 496.3058 | 463.6174 | 623.0738 | 735.2804 | 692.6668 | 432.1588 | 428.3531 | 406.0674 | NaN | NaN | NaN | 174.336 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -0.3384 | NaN | 17.7038
12708.1292 | 496.2173 | 463.6673 | 625.3892 | 738.2058 | 678.1607 | 431.8876 | 428.1127 | 405.9009 | NaN | NaN | NaN | 174.0388 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 3.3691 | NaN | 17.3047
12709.1292 | 495.9334 | 465.5059 | 621.7347 | 736.1253 | 663.7198 | 432.037 | 428.127 | 405.3254 | NaN | NaN | NaN | 173.8841 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 2.7653 | NaN | 15.4416
12710.1292 | 495.6333 | 464.9978 | 620.0686 | 741.9689 | 677.124 | 431.8945 | 428.227 | 405.7072 | NaN | NaN | NaN | 173.1275 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 2.2507 | NaN | 17.9833
12711.1292 | 495.3099 | 466.3349 | 617.5145 | 744.1917 | 671.67 | 431.8952 | 428.5975 | 405.6205 | NaN | NaN | NaN | 172.6443 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 2.8674 | NaN | 16.2527
12712.1292 | 494.824 | 466.6811 | 619.0969 | 748.7507 | 660.893 | 431.4726 | 428.4906 | 405.6272 | NaN | NaN | NaN | 172.3364 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -0.3334 | NaN | 15.5109
12713.1292 | 494.5278 | 467.1307 | 617.7366 | 744.8063 | 653.8446 | 430.7518 | 427.6613 | 405.6532 | NaN | NaN | NaN | 172.4613 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -0.9504 | NaN | 16.7103
12714.1292 | 494.1722 | 465.7338 | 617.5753 | 749.7309 | 638.2575 | 429.9801 | 426.9403 | 405.2875 | NaN | NaN | NaN | 172.1817 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -0.98 | NaN | 17.3679
12715.1292 | 493.7823 | 465.9878 | 617.5112 | 744.4266 | 625.4611 | 430.4586 | 427.037 | 404.9727 | NaN | NaN | NaN | 171.5824 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -2.3342 | NaN | 14.9965
12716.1292 | 493.3103 | 465.3647 | 617.9383 | 735.6418 | 629.3887 | 430.3214 | 425.7134 | 404.7822 | NaN | NaN | NaN | 170.7131 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -0.8999 | NaN | 16.9315
12717.1292 | 492.8935 | 465.6977 | 615.0266 | 728.3855 | 641.0736 | 430.2087 | 425.2403 | 404.4793 | NaN | NaN | NaN | 169.8918 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 0.6337 | NaN | 16.6559
12718.1292 | 492.3095 | 466.7385 | 613.7281 | 725.4709 | 626.8253 | 430.1231 | 425.4869 | 404.2868 | NaN | NaN | NaN | 169.4235 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 0.3682 | NaN | 15.9667
12719.1292 | 491.6362 | 466.0572 | 614.9687 | 724.3817 | 616.943 | 429.7824 | 425.7612 | 404.3019 | NaN | NaN | NaN | 168.393 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.5575 | NaN | 15.2522
12720.1292 | 491.1767 | 464.5371 | 614.8935 | 718.3944 | 610.0219 | 429.169 | 425.8276 | 403.8583 | NaN | NaN | NaN | 167.5856 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 3.9348 | NaN | 16.3857
12721.1292 | 490.6638 | 463.3399 | 615.8532 | 719.5747 | 603.9511 | 428.9905 | 425.8161 | 403.485 | NaN | NaN | NaN | 168.2034 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.8342 | NaN | 16.8217
12722.1292 | 490.3381 | 464.4738 | 612.1505 | 715.1283 | 595.3112 | 428.522 | 425.3367 | 403.0132 | NaN | NaN | NaN | 168.6454 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 3.7857 | NaN | 15.6758
12723.1292 | 490.1925 | 466.0197 | 615.3473 | 713.4657 | 587.9389 | 427.973 | 424.8842 | 402.3492 | NaN | NaN | NaN | 168.6117 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 2.91 | NaN | 17.3011
12724.1292 | 490.0426 | 463.0114 | 613.0125 | 725.9522 | 590.9268 | 427.7697 | 424.4502 | 402.2895 | NaN | NaN | NaN | 168.5451 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 1.7248 | NaN | 16.253
12725.1292 | 489.7156 | 463.015 | 612.0532 | 732.5807 | 588.9657 | 427.6394 | 424.4482 | 401.8778 | NaN | NaN | NaN | 168.5207 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 0.9613 | NaN | 16.902
12726.1292 | 489.6057 | 460.3398 | 610.2699 | 729.471 | 609.9919 | 427.4896 | 423.8328 | 401.5876 | NaN | NaN | NaN | 169.049 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 1.5728 | NaN | 16.4972
12727.1292 | 489.4246 | 462.359 | 608.2302 | 738.3751 | 629.7468 | 427.3297 | 423.5412 | 401.2577 | NaN | NaN | NaN | 169.2687 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -0.6274 | NaN | 13.6558
12728.1292 | 489.2641 | 460.3226 | 607.4573 | 740.2877 | 644.9569 | 426.8329 | 423.5179 | 400.8978 | NaN | NaN | NaN | 169.492 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -0.3758 | NaN | 17.1069
12729.1292 | 489.2161 | 461.046 | 610.7654 | 744.4718 | 636.3036 | 426.3778 | 423.5284 | 400.939 | NaN | NaN | NaN | 169.7214 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -1.2371 | NaN | 14.4464
12730.1292 | 489.0449 | 461.3695 | 608.6238 | 731.9481 | 630.6892 | 425.8656 | 423.7638 | 400.6701 | NaN | NaN | NaN | 168.4465 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -0.2064 | NaN | 17.3619
12731.1292 | 488.6696 | 459.9082 | 606.5276 | 728.4638 | 646.4225 | 426.4285 | 423.5973 | 400.7016 | NaN | NaN | NaN | 167.5886 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 0.061 | NaN | 15.7955
12732.1292 | 488.2066 | 461.0696 | 607.0484 | 729.7678 | 636.8275 | 425.8014 | 423.5742 | 400.5361 | NaN | NaN | NaN | 167.1027 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 0.4098 | NaN | 17.976
12733.1292 | 487.7388 | 460.8134 | 606.4762 | 730.2158 | 640.9442 | 425.4136 | 423.4751 | 400.4379 | NaN | NaN | NaN | 166.2055 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -1.4362 | NaN | 14.2789
12734.1292 | 487.2785 | 459.82 | 605.6878 | 744.1154 | 644.595 | 425.5451 | 423.4775 | 400.4113 | NaN | NaN | NaN | 166.0569 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -1.7554 | NaN | 17.0005
12735.1292 | 486.8966 | 461.92 | 604.1401 | 744.31 | 641.0229 | 425.7252 | 423.553 | 400.3623 | NaN | NaN | NaN | 166.2577 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -0.2409 | NaN | 16.4782
12736.1292 | 486.5446 | 458.5718 | 604.3653 | 741.4809 | 647.3688 | 425.1704 | 423.9341 | 400.82 | NaN | NaN | NaN | 166.7264 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -1.8124 | NaN | 17.3926
12737.1292 | 486.0456 | 459.0108 | 604.5997 | 738.7639 | 647.2869 | 424.8877 | 423.5269 | 400.5699 | NaN | NaN | NaN | 166.964 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -2.9637 | NaN | 14.3168
12738.1292 | 485.7714 | 460.6976 | 604.2679 | 734.6252 | 649.5205 | 424.8879 | 423.7702 | 400.5929 | NaN | NaN | NaN | 166.9015 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -1.8205 | NaN | 18.3677
12739.1292 | 485.3686 | 457.3148 | 603.1023 | 735.5665 | 636.2254 | 424.5697 | 424.0455 | 400.423 | NaN | NaN | NaN | 167.2628 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 0.0452 | NaN | 15.0156
12740.1292 | 484.9846 | 456.2457 | 605.2781 | 741.4547 | 643.3613 | 424.2586 | 423.1543 | 399.7324 | NaN | NaN | NaN | 166.3554 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 0.1211 | NaN | 17.9377
12741.1292 | 484.5296 | 457.6976 | 608.8672 | 745.4678 | 641.9184 | 424.4583 | 423.0507 | 399.4662 | NaN | NaN | NaN | 165.6783 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 1.3091 | NaN | 15.1972
12742.1292 | 484.1345 | 458.4101 | 606.9134 | 737.1388 | 655.7939 | 424.1511 | 422.2898 | 399.0951 | NaN | NaN | NaN | 165.8382 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.4004 | NaN | 18.1213
12743.1292 | 483.7759 | 458.3906 | 606.4997 | 743.8936 | 668.7466 | 423.6595 | 421.8566 | 399.025 | NaN | NaN | NaN | 165.853 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 0.5262 | NaN | 15.8177
12744.1292 | 483.5142 | 460.2776 | 606.3437 | 742.6716 | 669.8565 | 424.1222 | 421.1051 | 398.8264 | NaN | NaN | NaN | 165.6308 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 2.8704 | NaN | 17.2026
12745.1292 | 483.1635 | 460.217 | 604.0797 | 739.2851 | 666.4944 | 423.7036 | 421.1355 | 398.3432 | NaN | NaN | NaN | 165.175 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -0.0144 | NaN | 15.9553
12746.1292 | 482.6052 | 456.1526 | 602.195 | 744.4539 | 663.6308 | 423.3909 | 420.5555 | 397.9485 | NaN | NaN | NaN | 164.6363 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -1.5841 | NaN | 17.5222
12747.1292 | 482.4642 | 454.1696 | 601.1476 | 739.8413 | 659.7858 | 423.2323 | 420.2475 | 397.3953 | NaN | NaN | NaN | 163.8397 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -1.4905 | NaN | 16.6723
12748.1292 | 482.3831 | 452.9539 | 600.2393 | 744.8393 | 667.2097 | 422.2534 | 419.8017 | 396.8808 | NaN | NaN | NaN | 163.4114 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -3.1225 | NaN | 16.3463
12749.1292 | 482.0018 | 452.836 | 598.5941 | 753.8988 | 649.4474 | 422.2754 | 419.736 | 396.7993 | NaN | NaN | NaN | 162.7661 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 0.4181 | NaN | 16.7889
12750.1292 | 481.609 | 451.8307 | 596.4436 | 750.4839 | 638.0559 | 422.4141 | 419.5727 | 396.6652 | NaN | NaN | NaN | 162.0844 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -1.1465 | NaN | 17.9911
12751.1292 | 481.1153 | 450.9087 | 599.1655 | 748.2731 | 636.0557 | 422.338 | 419.579 | 396.6124 | NaN | NaN | NaN | 161.9018 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 0.9267 | NaN | 15.0667
12752.1292 | 480.6692 | 452.105 | 601.9211 | 737.7659 | 636.1261 | 422.2826 | 420.2966 | 396.1875 | NaN | NaN | NaN | 162.5265 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 0.4566 | NaN | 16.831
12753.1292 | 480.4185 | 452.3176 | 603.6322 | 733.7973 | 634.6696 | 422.5961 | 420.5327 | 396.3501 | NaN | NaN | NaN | 163.2835 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 2.9263 | NaN | 16.6245
12754.1292 | 479.9923 | 450.7426 | 603.0825 | 742.7712 | 634.4627 | 422.5192 | 420.358 | 396.4693 | NaN | NaN | NaN | 163.7575 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 2.1654 | NaN | 17.4536
12755.1292 | 479.7967 | 448.4764 | 606.3342 | 739.3862 | 644.8562 | 422.1482 | 420.2843 | 396.4833 | NaN | NaN | NaN | 164.0233 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 5.7487 | NaN | 17.8001
12756.1292 | 479.5823 | 447.5526 | 605.8661 | 739.0418 | 655.1129 | 422.3625 | 419.8673 | 396.1918 | NaN | NaN | NaN | 164.2011 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 1.7703 | NaN | 17.1694
12757.1292 | 479.4019 | 446.6216 | 603.6989 | 735.7027 | 661.7836 | 422.2039 | 420.1206 | 396.078 | NaN | NaN | NaN | 164.0896 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -0.0951 | NaN | 15.0065
12758.1292 | 479.2744 | 446.088 | 601.7443 | 725.1205 | 660.5812 | 422.3338 | 419.8046 | 395.9566 | NaN | NaN | NaN | 163.2812 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -0.0851 | NaN | 14.8979
12759.1292 | 479.1744 | 446.2615 | 601.6675 | 715.7001 | 672.834 | 422.4531 | 419.3745 | 395.7862 | NaN | NaN | NaN | 162.2455 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -1.6279 | NaN | 13.6008
12760.1292 | 478.8891 | 442.755 | 602.5832 | 707.6555 | 670.7695 | 421.6863 | 419.1897 | 395.6994 | NaN | NaN | NaN | 162.0954 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 1.2895 | NaN | 14.6553
12761.1292 | 478.5325 | 442.4734 | 603.9912 | 703.3035 | 665.0564 | 421.5035 | 419.5435 | 395.3979 | NaN | NaN | NaN | 162.1128 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 3.649 | NaN | 16.6394
12762.1292 | 478.0637 | 441.8041 | 602.1608 | 708.1819 | 667.9527 | 420.7011 | 418.9781 | 395.2833 | NaN | NaN | NaN | 162.1443 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 2.2277 | NaN | 16.0617
12763.1292 | 477.6407 | 440.8363 | 601.6882 | 722.589 | 675.3629 | 420.5087 | 419.0799 | 395.0451 | NaN | NaN | NaN | 162.1535 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -5.9346 | NaN | 15.6073
12764.1292 | 477.1815 | 443.2239 | 600.9399 | 719.4651 | 670.354 | 420.5282 | 419.4172 | 395.1551 | NaN | NaN | NaN | 162.5291 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -0.178 | NaN | 16.0955
12765.1292 | 476.9077 | 443.6184 | 602.2942 | 718.3092 | 655.4601 | 420.6655 | 419.3516 | 394.8032 | NaN | NaN | NaN | 162.4952 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 3.3663 | NaN | 13.0077
12766.1292 | 476.7418 | 444.2951 | 604.6725 | 719.9633 | 640.5375 | 420.6081 | 418.8303 | 394.4192 | NaN | NaN | NaN | 162.4871 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -0.4384 | NaN | 13.912
12767.1292 | 476.4767 | 446.6978 | 608.1853 | 720.1401 | 641.7741 | 419.4969 | 418.836 | 394.1375 | NaN | NaN | NaN | 162.3556 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -2.2076 | NaN | 16.1198
12768.1292 | 476.1355 | 445.8368 | 606.3206 | 714.964 | 637.3855 | 419.2981 | 417.9895 | 393.7657 | NaN | NaN | NaN | 162.004 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -0.0474 | NaN | 14.4771
12769.1292 | 475.7105 | 444.9253 | 603.7464 | 707.886 | 623.8829 | 418.7359 | 417.3634 | 393.4767 | NaN | NaN | NaN | 161.718 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.7842 | NaN | 14.0403
12770.1292 | 475.2573 | 445.7631 | 602.4958 | 706.8447 | 622.1539 | 418.5938 | 416.8484 | 393.3078 | NaN | NaN | NaN | 161.6967 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -1.5066 | NaN | 15.0191
12771.1292 | 474.8556 | 446.1381 | 601.55 | 705.7838 | 633.6157 | 418.2183 | 416.6334 | 393.0694 | NaN | NaN | NaN | 161.7464 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -0.2827 | NaN | 11.8278
12772.1292 | 474.4634 | 446.8241 | 600.7466 | 703.5779 | 640.3903 | 418.3383 | 416.7387 | 392.8745 | NaN | NaN | NaN | 161.502 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -0.197 | NaN | 13.1745
12773.1292 | 474.1534 | 445.9547 | 602.1969 | 706.532 | 630.0286 | 418.014 | 416.4955 | 392.3597 | NaN | NaN | NaN | 161.1107 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -1.6111 | NaN | 15.2909
12774.1292 | 473.8233 | 446.2069 | 599.8382 | 711.3948 | 629.9069 | 417.7179 | 416.1386 | 392.1561 | NaN | NaN | NaN | 161.3754 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -3.2355 | NaN | 16.8961
12775.1292 | 473.3264 | 445.2733 | 598.0613 | 705.9203 | 638.4098 | 416.9422 | 414.9705 | 392.2775 | NaN | NaN | NaN | 161.1869 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 3.2648 | NaN | 18.5571
12776.1292 | 473.1065 | 445.7064 | 598.9696 | 707.0982 | 629.7225 | 416.755 | 415.1976 | 392.1708 | NaN | NaN | NaN | 161.1076 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 1.3838 | NaN | 14.6529
12777.1292 | 472.6531 | 444.6956 | 599.838 | 710.8643 | 643.1881 | 416.8255 | 414.9221 | 391.9256 | NaN | NaN | NaN | 161.3505 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -3.3067 | NaN | 18.5625
12778.1292 | 472.3685 | 444.4399 | 602.5983 | 713.2063 | 662.4787 | 416.3098 | 415.2975 | 391.5875 | NaN | NaN | NaN | 161.1494 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -0.0444 | NaN | 16.0293
12779.1292 | 471.9302 | 444.8908 | 603.1247 | 715.3608 | 659.3624 | 416.0647 | 415.1255 | 391.3277 | NaN | NaN | NaN | 160.8199 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 1.1864 | NaN | 14.3409
12780.1292 | 471.7141 | 444.0223 | 604.1324 | 712.4953 | 659.3806 | 416.5361 | 414.6349 | 391.3667 | NaN | NaN | NaN | 160.5744 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -3.5645 | NaN | 15.9677
12781.1292 | 471.6595 | 443.3709 | 604.3185 | 708.1441 | 661.325 | 416.5051 | 414.7577 | 391.3036 | NaN | NaN | NaN | 160.3116 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 1.0843 | NaN | 15.9191
12782.1292 | 471.5595 | 442.9971 | 600.3865 | 700.4866 | 659.5032 | 416.3787 | 414.6507 | 391.0674 | NaN | NaN | NaN | 160.3599 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.5362 | NaN | 15.3631
12783.1292 | 471.2391 | 442.0809 | 597.8521 | 706.2166 | 658.4694 | 416.7199 | 414.3787 | 390.6274 | NaN | NaN | NaN | 160.3074 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 1.6462 | NaN | 16.5717
12784.1292 | 470.9462 | 440.696 | 595.1827 | 706.2113 | 656.8978 | 416.3482 | 414.3917 | 390.4196 | NaN | NaN | NaN | 159.5436 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -1.5842 | NaN | 17.3733
12785.1292 | 470.5296 | 440.8503 | 594.5315 | 704.2833 | 659.4655 | 416.3903 | 414.2394 | 390.3663 | NaN | NaN | NaN | 158.8097 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.5148 | NaN | 15.1387
12786.1292 | 470.2743 | 441.1842 | 595.3583 | 711.3495 | 669.3876 | 415.9678 | 413.9445 | 390.3006 | NaN | NaN | NaN | 158.5232 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -0.0208 | NaN | 15.1434
12787.1292 | 469.9425 | 441.4364 | 595.6314 | 715.153 | 663.9233 | 415.6074 | 413.3777 | 389.7456 | NaN | NaN | NaN | 158.5008 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -1.7359 | NaN | 13.3931
12788.1292 | 469.5659 | 441.4898 | 596.4031 | 711.3733 | 649.2843 | 415.45 | 413.0411 | 389.8288 | NaN | NaN | NaN | 158.1606 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 4.3393 | NaN | 12.9075
12789.1292 | 469.3244 | 440.295 | 593.9847 | 711.7622 | 636.8501 | 415.5736 | 412.1666 | 389.444 | NaN | NaN | NaN | 157.2944 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 0.2227 | NaN | 14.2597
12790.1292 | 469.0122 | 441.2928 | 592.3828 | 714.1418 | 625.1992 | 415.1697 | 411.5971 | 389.031 | NaN | NaN | NaN | 157.2575 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -0.4832 | NaN | 11.9499
12791.1292 | 468.6959 | 441.001 | 595.4556 | 716.1006 | 615.3202 | 414.7005 | 411.5942 | 388.9564 | NaN | NaN | NaN | 157.0425 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 1.1266 | NaN | 13.9518
12792.1292 | 468.5292 | 441.5243 | 595.7781 | 705.4701 | 624.4808 | 414.3955 | 411.8803 | 388.8217 | NaN | NaN | NaN | 156.1986 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -5.751 | NaN | 10.8318
12793.1292 | 468.2796 | 441.4523 | 598.5416 | 708.2471 | 628.7432 | 413.531 | 411.6483 | 388.8138 | NaN | NaN | NaN | 155.1758 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 1.4036 | NaN | 14.6542
12794.1292 | 467.9218 | 442.7214 | 597.824 | 709.3563 | 614.3025 | 413.5324 | 411.9959 | 388.7808 | NaN | NaN | NaN | 154.8032 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -1.4244 | NaN | 15.2126
12795.1292 | 467.5602 | 440.7056 | 600.616 | 709.8505 | 613.9922 | 413.8893 | 411.561 | 388.8674 | NaN | NaN | NaN | 155.4746 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 1.1297 | NaN | 12.8009
12796.1292 | 467.5008 | 439.7105 | 601.9116 | 711.1901 | 615.8069 | 413.6837 | 411.3595 | 388.6341 | NaN | NaN | NaN | 156.4262 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -5.0146 | NaN | 15.6185
12797.1292 | 467.4216 | 440.2662 | 599.3767 | 715.6643 | 622.8096 | 413.3687 | 411.5497 | 388.6105 | NaN | NaN | NaN | 157.2294 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 1.9002 | NaN | 13.0971
12798.1292 | 467.3293 | 439.3486 | 599.7345 | 712.2491 | 610.4956 | 413.0558 | 411.4475 | 388.6285 | NaN | NaN | NaN | 157.0973 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -5.5972 | NaN | 14.4711
12799.1292 | 467.0844 | 439.4197 | 597.4708 | 712.0584 | 604.1253 | 412.8919 | 411.1983 | 388.4414 | NaN | NaN | NaN | 156.8902 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | 2.299 | NaN | 14.8007
12800.1292 | 466.5851 | 436.674 | 596.2464 | 727.4674 | 603.7868 | 412.5832 | 410.6316 | 388.0666 | NaN | NaN | NaN | 156.478 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -2.5445 | NaN | 14.7743
12801.1292 | 466.3721 | 437.6052 | 593.721 | 713.2283 | 612.813 | 412.4492 | 410.2393 | 387.9551 | NaN | NaN | NaN | 156.4393 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -2.489 | NaN | 12.8769
12802.1292 | 465.9456 | 436.871 | 594.7514 | 712.8189 | 616.189 | 412.9713 | 410.0944 | 387.595 | NaN | NaN | NaN | 156.1561 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -2.1458 | NaN | 14.3638
12803.1292 | 465.5358 | 436.9899 | 594.1595 | 712.5784 | 616.7933 | 412.691 | 409.4749 | 387.3053 | NaN | NaN | NaN | 156.7818 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -2.9053 | NaN | 13.2126
12804.1292 | 465.2593 | 436.93 | 592.6718 | 703.8058 | 611.2099 | 412.5413 | 409.4206 | 387.0162 | NaN | NaN | NaN | 156.5638 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -1.7363 | NaN | 14.9023
12805.1292 | 465.1751 | 437.4509 | 588.9368 | 695.7451 | 615.9078 | 411.7202 | 409.3396 | 387.0556 | NaN | NaN | NaN | 155.9584 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -1.1072 | NaN | 12.3292
12806.1292 | 464.9553 | 435.4373 | 588.7663 | 694.9992 | 612.3627 | 411.5839 | 408.4872 | 386.8054 | NaN | NaN | NaN | 155.3425 | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | NaN | -2.1414 | NaN | 13.811

## Input for Plots
Fire Time | B Position - Middle
-0.8708 | 13.7945
0.1292 | 13.7801
1.1292 | 13.833
2.1292 | 13.7828
3.1292 | 13.7546
4.1292 | 13.7563
5.1292 | 13.7724
6.1292 | 13.7966
7.1292 | 13.8906
8.1292 | 14.2047
9.1292 | 15.0359
10.1292 | 16.3714
11.1292 | 18.1006
12.1292 | 20.8924
13.1292 | 23.3311
14.1292 | 26.4924
15.1292 | 29.8732
16.1292 | 33.2908
17.1292 | 35.6068
18.1292 | 37.5578
19.1448 | 39.5921
20.1292 | 41.4415
21.1292 | 43.0797
22.1292 | 44.4431
23.1292 | 46.1314
24.1292 | 47.3893
25.1292 | 49.1759
26.1292 | 50.8247
27.1292 | 53.0537
28.1292 | 54.961
29.1292 | 56.4574
30.1292 | 57.585
31.1292 | 58.6379
32.1292 | 60.2297
33.1292 | 61.6156
34.1292 | 62.954
35.1292 | 63.8523
36.1292 | 64.7835
37.1292 | 65.775
38.1292 | 66.4592
39.1292 | 67.4337
40.1292 | 68.0382
41.1292 | 68.9545
42.1292 | 69.9164
43.1292 | 71.1869
44.1448 | 72.1189
45.1292 | 73.3237
46.1292 | 74.0965
47.1292 | 75.5821
48.1448 | 76.9872
49.1448 | 77.993
50.1448 | 79.2296
51.1292 | 80.6962
52.1292 | 82.0365
53.1292 | 83.801
54.1292 | 84.659
55.1292 | 85.3419
56.1292 | 86.178
57.1292 | 87.5743
58.1292 | 88.3365
59.1292 | 88.7796
60.1292 | 89.1557
61.1292 | 89.8128
62.1292 | 91.5214
63.1292 | 92.3539
64.1292 | 93.182
65.1292 | 94.2908
66.1292 | 94.8365
67.1292 | 96.1212
68.1292 | 97.3474
69.1292 | 98.5962
70.1292 | 99.6286
71.1292 | 100.6856
72.1292 | 101.5456
73.1292 | 101.861
74.1292 | 103.0578
75.1292 | 103.7934
76.1292 | 105.2822
77.1292 | 106.368
78.1292 | 107.7405
79.1292 | 108.406
80.1292 | 109.3903
81.1292 | 110.2467
82.1292 | 110.9988
83.1292 | 111.2907
84.1292 | 111.5094
85.1292 | 112.212
86.1292 | 112.6778
87.1292 | 113.5584
88.1292 | 114.4802
89.1292 | 115.0693
90.1292 | 116.1392
91.1292 | 116.1047
92.1292 | 116.6315
93.1292 | 116.9591
94.1292 | 117.5515
95.1292 | 118.7735
96.1292 | 119.4279
97.1292 | 120.3523
98.1292 | 120.6767
99.1292 | 121.7584
100.1292 | 122.3117
101.1292 | 123.895
102.1292 | 124.1472
103.1292 | 124.7034
104.1292 | 124.5054
105.1292 | 125.2389
106.1292 | 125.1245
107.1292 | 125.3826
108.1292 | 125.5057
109.1292 | 125.2789
110.1292 | 125.542
111.1292 | 126.2802
112.1292 | 126.8319
113.1292 | 127.3929
114.1292 | 127.3641
115.1448 | 127.3337
116.1292 | 128.0319
117.1292 | 128.958
118.1292 | 129.1652
119.1292 | 128.9896
120.1292 | 128.8527
121.1292 | 128.7459
122.1292 | 128.8999
123.1292 | 128.8716
124.1292 | 128.5817
125.1292 | 128.0683
126.1292 | 127.6089
127.1292 | 127.3938
128.1292 | 127.1383
129.1292 | 127.0737
130.1292 | 127.0393
131.1292 | 127.1782
132.1292 | 127.7086
133.1292 | 127.8393
134.1292 | 128.1924
135.1292 | 128.4024
136.1292 | 128.5703
137.1292 | 128.3921
138.1292 | 128.9038
139.1292 | 128.4445
140.1292 | 128.6475
141.1292 | 128.4232
142.1292 | 128.4077
143.1292 | 129.1877
144.1292 | 129.1843
145.1448 | 129.8991
146.1292 | 130.3599
147.1292 | 130.6583
148.1292 | 130.9209
149.1292 | 131.285
150.1292 | 131.6555
151.1292 | 131.7339
152.1292 | 132.2375
153.1292 | 132.3824
154.1292 | 132.9893
155.1292 | 133.2288
156.1292 | 133.898
157.1292 | 133.9663
158.1292 | 134.816
159.1292 | 134.94
160.1292 | 135.1707
161.1292 | 135.7998
162.1292 | 136.6739
163.1292 | 137.6291
164.1292 | 138.0949
165.1292 | 138.7047
166.1292 | 139.4018
167.1292 | 140.009
168.1292 | 140.6256
169.1292 | 140.9513
170.1292 | 140.8603
171.1292 | 141.2379
172.1292 | 141.8764
173.1292 | 142.485
174.1292 | 142.6339
175.1292 | 142.7455
176.1292 | 143.0743
177.1292 | 143.3668
178.1292 | 143.3093
179.1292 | 143.4453
180.1292 | 143.4277
181.1292 | 143.5775
182.1292 | 144.0453
183.1292 | 143.8834
184.1292 | 144.1474
185.1292 | 144.5398
186.1292 | 144.9413
187.1292 | 144.7613
188.1292 | 144.8457
189.1292 | 144.4958
190.1292 | 144.7675
191.1292 | 145.1295
192.1292 | 146.4768
193.1292 | 146.5086
194.1292 | 147.2562
195.1292 | 147.4818
196.1292 | 147.653
197.1292 | 147.7218
198.1292 | 147.4397
199.1448 | 147.7963
200.1292 | 147.6912
201.1292 | 147.6199
202.1292 | 147.5196
203.1292 | 148.0698
204.1292 | 149.129
205.1292 | 149.6197
206.1292 | 149.7265
207.1292 | 150.9003
208.1292 | 151.824
209.1292 | 152.2727
210.1292 | 152.5
211.1292 | 152.3363
212.1292 | 151.9537
213.1292 | 152.0161
214.1292 | 152.2195
215.1292 | 152.4363
216.1292 | 152.9387
217.1292 | 153.1145
218.1292 | 153.5302
219.1292 | 153.8979
220.1292 | 154.9647
221.1292 | 155.0785
222.1292 | 155.595
223.1292 | 156.3211
224.1292 | 156.9833
225.1292 | 157.1218
226.1292 | 156.6708
227.1292 | 155.6927
228.1292 | 154.8338
229.1292 | 153.9547
230.1292 | 153.8017
231.1292 | 154.0224
232.1292 | 154.0211
233.1292 | 154.669
234.1292 | 154.9921
235.1292 | 155.0354
236.1292 | 155.4491
237.1292 | 155.1916
238.1292 | 154.8356
239.1292 | 154.7408
240.1292 | 155.7069
241.1292 | 155.5635
242.1292 | 155.8619
243.1292 | 155.596
244.1292 | 155.3002
245.1292 | 154.8705
246.1292 | 154.2125
247.1292 | 154.4175
248.1292 | 154.912
249.1292 | 155.1845
250.1292 | 155.7868
251.1292 | 155.8268
252.1292 | 156.559
253.1292 | 156.8286
254.1292 | 157.5327
255.1292 | 157.6207
256.1292 | 157.6521
257.1292 | 158.7474
258.1292 | 159.3654
259.1292 | 159.2171
260.1292 | 159.712
261.1292 | 160.2501
262.1292 | 160.9132
263.1292 | 162.2036
264.1292 | 162.1491
265.1448 | 162.2221
266.1292 | 162.9319
267.1292 | 163.8778
268.1292 | 164.5996
269.1292 | 165.1798
270.1292 | 165.3363
271.1292 | 165.3651
272.1292 | 164.8112
273.1292 | 164.8076
274.1292 | 165.5895
275.1292 | 166.3936
276.1292 | 166.8517
277.1292 | 167.0291
278.1292 | 167.0732
279.1292 | 167.5954
280.1292 | 168.1317
281.1292 | 168.3387
282.1292 | 168.4313
283.1292 | 168.232
284.1292 | 168.4456
285.1292 | 168.5464
286.1292 | 169.3137
287.1292 | 169.6311
288.1292 | 169.9582
289.1292 | 170.3376
290.1448 | 170.7177
291.1292 | 171.5769
292.1292 | 171.9188
293.1292 | 172.0003
294.1292 | 171.8807
295.1448 | 171.9318
296.1292 | 172.0989
297.1292 | 172.4045
298.1292 | 172.5008
299.1292 | 172.7584
300.1292 | 173.3155
301.1292 | 173.6532
302.1292 | 173.4327
303.1292 | 173.4766
304.1292 | 173.8403
305.1292 | 174.1225
306.1292 | 174.8945
307.1292 | 176.0958
308.1292 | 176.4807
309.1292 | 176.8797
310.1292 | 177.0166
311.1292 | 177.3601
312.1292 | 177.4965
313.1292 | 177.7375
314.1292 | 177.9656
315.1292 | 178.1509
316.1292 | 178.1287
317.1292 | 177.9517
318.1292 | 178.3886
319.1292 | 178.4359
320.1292 | 178.6606
321.1292 | 178.7859
322.1292 | 179.0813
323.1292 | 179.6607
324.1292 | 180.1116
325.1292 | 180.2012
326.1292 | 180.092
327.1292 | 180.2177
328.1292 | 180.303
329.1292 | 179.957
330.1292 | 179.7468
331.1292 | 179.8227
332.1292 | 180.7457
333.1292 | 180.6867
334.1292 | 181.1548
335.1292 | 180.7637
336.1292 | 180.0258
337.1292 | 180.8153
338.1292 | 181.1537
339.1292 | 180.7359
340.1292 | 181.1421
341.1292 | 181.0058
342.1292 | 181.009
343.1292 | 181.1587
344.1292 | 181.063
345.1292 | 181.0371
346.1292 | 181.4328
347.1292 | 181.6911
348.1292 | 181.9766
349.1292 | 182.5867
350.1292 | 183.2258
351.1292 | 183.6727
352.1292 | 183.4405
353.1292 | 183.8092
354.1292 | 184.0265
355.1292 | 184.2164
356.1292 | 183.9893
357.1292 | 183.9421
358.1292 | 184.0945
359.1292 | 185.6214
360.1292 | 185.3477
361.1292 | 185.3007
362.1292 | 185.8357
363.1292 | 185.6935
364.1292 | 185.5815
365.1292 | 186.018
366.1292 | 186.459
367.1292 | 186.7754
368.1292 | 186.5353
369.1292 | 186.9145
370.1292 | 187.3618
371.1292 | 187.466
372.1292 | 187.7343
373.1292 | 187.3217
374.1292 | 187.332
375.1292 | 187.4313
376.1292 | 186.8773
377.1292 | 187.0512
378.1292 | 187.1771
379.1448 | 187.6068
380.1292 | 188.3638
381.1292 | 189.1838
382.1292 | 189.2857
383.1292 | 188.9087
384.1292 | 189.1905
385.1292 | 189.3968
386.1292 | 190.0922
387.1292 | 190.482
388.1292 | 190.8714
389.1292 | 191.0257
390.1292 | 191.5854
391.1292 | 191.6082
392.1292 | 192.1273
393.1292 | 192.6759
394.1292 | 192.7203
395.1292 | 193.6219
396.1292 | 194.2287
397.1292 | 195.0033
398.1292 | 195.4699
399.1292 | 195.6758
400.1292 | 196.4578
401.1292 | 197.0923
402.1292 | 197.1308
403.1292 | 196.9163
404.1292 | 197.4549
405.1292 | 197.2288
406.1292 | 197.2001
407.1292 | 197.2847
408.1292 | 197.636
409.1292 | 198.5665
410.1292 | 199.3165
411.1292 | 199.9984
412.1292 | 200.0922
413.1292 | 200.964
414.1292 | 200.5202
415.1292 | 200.5362
416.1292 | 201.9724
417.1292 | 202.2332
418.1292 | 202.8229
419.1292 | 202.985
420.1292 | 203.2729
421.1292 | 203.9427
422.1292 | 203.821
423.1292 | 204.2953
424.1292 | 204.2266
425.1292 | 204.4866
426.1292 | 205.7509
427.1292 | 207.0529
428.1292 | 207.9497
429.1292 | 207.4584
430.1292 | 207.6702
431.1292 | 208.1792
432.1292 | 209.0191
433.1292 | 210.9293
434.1292 | 211.3654
435.1292 | 211.3964
436.1292 | 212.223
437.1292 | 212.8677
438.1292 | 213.5695
439.1292 | 214.3887
440.1292 | 214.7613
441.1292 | 214.7742
442.1292 | 214.7741
443.1292 | 215.5592
444.1292 | 215.907
445.1292 | 216.2839
446.1292 | 216.6367
447.1292 | 217.2687
448.1292 | 217.1546
449.1292 | 217.6257
450.1292 | 218.0909
451.1292 | 218.973
452.1292 | 219.5482
453.1292 | 220.0471
454.1292 | 220.1376
455.1292 | 221.1536
456.1292 | 222.2153
457.1292 | 222.9409
458.1292 | 222.8637
459.1292 | 222.9266
460.1292 | 223.4682
461.1292 | 223.9022
462.1292 | 223.9727
463.1292 | 224.6354
464.1292 | 224.7522
465.1292 | 225.6406
466.1292 | 226.7995
467.1292 | 226.9268
468.1292 | 226.781
469.1292 | 227.3724
470.1292 | 228.3261
471.1292 | 229.2619
472.1292 | 230.1765
473.1292 | 230.7152
474.1292 | 231.4397
475.1292 | 231.8302
476.1292 | 232.6258
477.1292 | 233.1495
478.1292 | 233.1217
479.1292 | 233.4511
480.1292 | 234.0233
481.1292 | 234.5355
482.1292 | 234.9186
483.1292 | 235.3552
484.1292 | 235.3073
485.1292 | 234.965
486.1292 | 234.3728
487.1292 | 234.1432
488.1292 | 234.3744
489.1292 | 234.3742
490.1292 | 234.6167
491.1448 | 234.6044
492.1292 | 235.3474
493.1292 | 235.7126
494.1292 | 235.9286
495.1292 | 236.627
496.1292 | 236.8551
497.1292 | 237.1434
498.1292 | 237.7825
499.1292 | 236.9861
500.1292 | 236.9764
501.1292 | 236.8598
502.1292 | 236.4881
503.1292 | 236.5188
504.1292 | 236.0495
505.1292 | 236.1044
506.1292 | 236.4348
507.1292 | 237.0509
508.1292 | 237.2614
509.1292 | 238.1423
510.1292 | 239.4688
511.1292 | 239.5788
512.1292 | 239.8589
513.1292 | 239.9033
514.1292 | 240.3436
515.1292 | 240.656
516.1292 | 241.2568
517.1292 | 241.4102
518.1292 | 242.1
519.1292 | 242.2893
520.1292 | 242.5543
521.1292 | 243.2555
522.1292 | 243.1495
523.1292 | 244.6327
524.1292 | 244.8509
525.1448 | 245.1337
526.1292 | 244.7779
527.1292 | 245.0951
528.1292 | 244.8553
529.1292 | 244.6899
530.1292 | 244.2772
531.1292 | 244.9772
532.1292 | 244.3147
533.1292 | 244.4079
534.1292 | 244.5238
535.1292 | 244.4331
536.1292 | 244.7849
537.1292 | 244.6253
538.1292 | 244.3459
539.1292 | 244.8727
540.1292 | 246.0695
541.1292 | 245.9384
542.1292 | 246.6348
543.1292 | 247.0745
544.1292 | 247.149
545.1292 | 247.1291
546.1292 | 247.6129
547.1292 | 247.7961
548.1292 | 248.0477
549.1292 | 248.1457
550.1292 | 248.5736
551.1292 | 249.6663
552.1292 | 249.8834
553.1292 | 250.1573
554.1292 | 251.2476
555.1292 | 251.5596
556.1292 | 251.2891
557.1292 | 251.5282
558.1292 | 252.3179
559.1292 | 252.6188
560.1292 | 252.7187
561.1292 | 253.2946
562.1292 | 253.537
563.1292 | 254.7671
564.1292 | 255.8195
565.1292 | 256.9625
566.1292 | 257.7373
567.1292 | 258.2686
568.1292 | 258.4418
569.1292 | 257.8754
570.1292 | 258.7108
571.1292 | 258.3689
572.1292 | 258.6186
573.1292 | 258.7824
574.1292 | 258.5034
575.1292 | 258.1345
576.1292 | 257.4093
577.1292 | 257.4765
578.1292 | 257.8867
579.1292 | 258.3584
580.1292 | 258.9873
581.1292 | 259.4521
582.1292 | 259.9327
583.1292 | 260.3525
584.1292 | 260.9153
585.1292 | 261.3902
586.1292 | 261.3733
587.1292 | 261.7093
588.1292 | 262.8753
589.1292 | 264.1227
590.1292 | 264.3579
591.1292 | 264.7738
592.1292 | 265.4062
593.1292 | 265.7785
594.1292 | 265.8063
595.1292 | 266.4828
596.1292 | 266.8683
597.1292 | 267.9254
598.1292 | 269.0162
599.1292 | 270.5633
600.1292 | 271.9728
601.1292 | 272.4267
602.1292 | 273.2667
603.1292 | 273.7178
604.1292 | 274.3824
605.1292 | 274.2085
606.1292 | 274.4631
607.1292 | 275.4834
608.1292 | 276.5535
609.1292 | 278.5829
610.1292 | 280.6343
611.1292 | 280.3299
612.1292 | 280.8245
613.1292 | 280.8587
614.1292 | 280.505
615.1292 | 280.9649
616.1292 | 281.9879
617.1292 | 282.0516
618.1292 | 281.8379
619.1292 | 281.2584
620.1292 | 281.1979
621.1292 | 281.8717
622.1292 | 281.3358
623.1292 | 281.4445
624.1292 | 281.4614
625.1292 | 280.5775
626.1292 | 280.4186
627.1292 | 280.633
628.1292 | 280.0851
629.1292 | 280.1278
630.1292 | 280.5902
631.1292 | 280.6745
632.1292 | 280.014
633.1292 | 279.8351
634.1292 | 280.2481
635.1292 | 280.3822
636.1292 | 281.3355
637.1292 | 282.3759
638.1292 | 282.8777
639.1292 | 283.2865
640.1292 | 283.6727
641.1292 | 284.9608
642.1292 | 285.0926
643.1292 | 286.9069
644.1292 | 286.9012
645.1292 | 286.2372
646.1292 | 285.5879
647.1292 | 285.6354
648.1292 | 285.8406
649.1292 | 287.4489
650.1292 | 286.583
651.1292 | 285.9176
652.1292 | 286.8647
653.1292 | 285.8486
654.1292 | 286.2687
655.1292 | 286.6854
656.1292 | 286.3854
657.1292 | 285.9546
658.1292 | 285.5668
659.1292 | 285.0583
660.1292 | 285.5566
661.1292 | 286.3267
662.1292 | 286.5701
663.1292 | 287.2315
664.1292 | 287.3301
665.1292 | 286.7026
666.1292 | 285.9659
667.1292 | 285.6981
668.1292 | 285.0731
669.1292 | 283.9594
670.1292 | 284.7893
671.1292 | 283.7926
672.1292 | 283.4485
673.1292 | 283.5702
674.1292 | 283.5328
675.1292 | 283.5421
676.1292 | 283.752
677.1292 | 283.9107
678.1292 | 283.844
679.1292 | 283.8833
680.1292 | 284.588
681.1292 | 284.8436
682.1292 | 285.3568
683.1292 | 285.059
684.1292 | 284.1333
685.1292 | 283.6985
686.1292 | 283.7094
687.1292 | 283.347
688.1292 | 282.7334
689.1292 | 283.0906
690.1292 | 282.8433
691.1292 | 282.6305
692.1292 | 282.7282
693.1292 | 282.0407
694.1292 | 281.7831
695.1292 | 281.5413
696.1292 | 281.9867
697.1292 | 283.0616
698.1292 | 282.4138
699.1292 | 282.3978
700.1292 | 283.1218
701.1292 | 284.967
702.1292 | 285.6025
703.1292 | 287.0935
704.1292 | 288.9679
705.1292 | 292.1887
706.1292 | 294.2375
707.1292 | 294.4886
708.1292 | 296.1649
709.1292 | 297.3631
710.1292 | 298.1179
711.1292 | 300.1492
712.1292 | 301.6685
713.1292 | 303.2286
714.1292 | 303.3555
715.1292 | 304.092
716.1292 | 303.4442
717.1292 | 305.304
718.1292 | 306.8812
719.1292 | 306.5687
720.1292 | 308.9514
721.1448 | 314.3262
722.1292 | 319.7356
723.1448 | 326.0269
724.1448 | 329.6567
725.1448 | 332.0326
726.1292 | 334.0207
727.1292 | 334.8745
728.1292 | 335.2686
729.1292 | 333.6979
730.1292 | 332.7612
731.1292 | 334.0358
732.1292 | 334.6182
733.1292 | 333.8324
734.1292 | 334.9111
735.1292 | 336.653
736.1292 | 337.1514
737.1292 | 337.5894
738.1292 | 338.7197
739.1292 | 339.5444
740.1292 | 340.0914
741.1292 | 339.1544
742.1292 | 340.0658
743.1292 | 340.5261
744.1292 | 340.1709
745.1292 | 339.7
746.1292 | 336.9822
747.1292 | 336.3945
748.1292 | 336.6569
749.1292 | 338.813
750.1292 | 338.1895
751.1292 | 338.9404
752.1292 | 339.3181
753.1292 | 340.5141
754.1292 | 340.9528
755.1292 | 340.8753
756.1292 | 338.6492
757.1292 | 336.3715
758.1292 | 335.3946
759.1292 | 335.4388
760.1292 | 337.5483
761.1292 | 340.5873
762.1292 | 340.481
763.1292 | 339.216
764.1292 | 337.6647
765.1292 | 337.5477
766.1292 | 337.2636
767.1292 | 339.2511
768.1292 | 339.9186
769.1292 | 341.1506
770.1292 | 342.3067
771.1292 | 342.8453
772.1292 | 345.4006
773.1292 | 345.3091
774.1292 | 344.4316
775.1292 | 342.9785
776.1292 | 344.756
777.1292 | 344.8605
778.1292 | 343.27
779.1292 | 343.9005
780.1292 | 343.4436
781.1292 | 343.2875
782.1292 | 342.3123
783.1292 | 345.3667
784.1292 | 343.3267
785.1292 | 342.108
786.1292 | 341.7244
787.1292 | 342.5273
788.1292 | 344.1648
789.1292 | 343.9375
790.1292 | 346.9796
791.1292 | 347.3563
792.1292 | 349.2892
793.1292 | 350.1446
794.1292 | 351.2377
795.1292 | 351.389
796.1292 | 348.4574
797.1292 | 346.3943
798.1292 | 344.5825
799.1292 | 343.8186
800.1292 | 346.8518
801.1292 | 347.2621
802.1292 | 344.9333
803.1292 | 343.6154
804.1292 | 343.2756
805.1292 | 344.669
806.1292 | 341.7134
807.1292 | 343.2532
808.1292 | 341.4732
809.1292 | 341.1473
810.1292 | 340.6791
811.1292 | 341.5142
812.1292 | 341.6676
813.1292 | 342.7451
814.1292 | 342.417
815.1292 | 341.8671
816.1292 | 341.5731
817.1292 | 341.8423
818.1292 | 341.2576
819.1292 | 339.7475
820.1292 | 341.8448
821.1292 | 339.372
822.1292 | 340.8508
823.1292 | 342.3682
824.1292 | 343.2951
825.1292 | 342.1562
826.1292 | 340.4424
827.1292 | 344.1644
828.1292 | 344.8947
829.1292 | 343.1346
830.1292 | 342.4116
831.1292 | 343.7067
832.1292 | 341.1139
833.1292 | 340.258
834.1292 | 342.6535
835.1292 | 341.7804
836.1292 | 343.4157
837.1292 | 344.6887
838.1292 | 346.6883
839.1292 | 343.8117
840.1292 | 344.9034
841.1292 | 347.2523
842.1292 | 347.8915
843.1292 | 347.93
844.1292 | 350.591
845.1292 | 352.4716
846.1292 | 353.6884
847.1292 | 354.3183
848.1292 | 355.3808
849.1292 | 355.7814
850.1292 | 356.6887
851.1292 | 356.3211
852.1292 | 358.2349
853.1292 | 357.6603
854.1292 | 359.1608
855.1292 | 361.9523
856.1292 | 364.0635
857.1292 | 363.8093
858.1292 | 363.1133
859.1292 | 364.6475
860.1292 | 367.6598
861.1292 | 367.2203
862.1292 | 368.9512
863.1292 | 370.621
864.1292 | 368.7572
865.1292 | 370.2406
866.1292 | 369.4526
867.1292 | 368.8644
868.1292 | 369.4135
869.1292 | 371.5056
870.1292 | 371.7662
871.1292 | 372.7174
872.1292 | 374.718
873.1292 | 375.9244
874.1292 | 376.8923
875.1292 | 378.1082
876.1292 | 378.5874
877.1292 | 378.6588
878.1292 | 379.6283
879.1292 | 379.4895
880.1292 | 380.2877
881.1292 | 379.9596
882.1292 | 377.0997
883.1292 | 376.2673
884.1292 | 376.5152
885.1292 | 376.9535
886.1292 | 377.9046
887.1292 | 378.8321
888.1292 | 379.7764
889.1292 | 380.2211
890.1292 | 378.2872
891.1292 | 377.4666
892.1292 | 375.5411
893.1292 | 374.6247
894.1292 | 374.4356
895.1292 | 373.3805
896.1292 | 373.8565
897.1292 | 377.2124
898.1292 | 376.7218
899.1292 | 376.1083
900.1292 | 376.5773
901.1292 | 376.643
902.1292 | 377.2151
903.1448 | 377.8927
904.1292 | 378.039
905.1292 | 378.6636
906.1292 | 379.6409
907.1448 | 379.3241
908.1448 | 378.6098
909.1292 | 378.7161
910.1292 | 380.6097
911.1292 | 380.6798
912.1448 | 380.1226
913.1292 | 380.9395
914.1292 | 382.1689
915.1292 | 382.9499
916.1292 | 382.7942
917.1292 | 383.4526
918.1292 | 384.8675
919.1292 | 386.2497
920.1292 | 387.4008
921.1292 | 387.297
922.1292 | 388.5359
923.1292 | 389.0176
924.1292 | 389.1736
925.1292 | 388.2084
926.1292 | 387.7642
927.1292 | 387.6397
928.1292 | 387.7506
929.1292 | 388.7276
930.1292 | 390.1265
931.1292 | 390.0792
932.1292 | 389.1894
933.1292 | 388.4217
934.1292 | 388.0986
935.1292 | 388.9511
936.1292 | 389.5574
937.1292 | 390.6353
938.1292 | 390.8871
939.1292 | 390.1243
940.1292 | 389.3209
941.1292 | 388.5963
942.1292 | 387.918
943.1292 | 388.7221
944.1292 | 388.8696
945.1292 | 389.3291
946.1292 | 388.7049
947.1292 | 386.2501
948.1292 | 385.8798
949.1292 | 385.1964
950.1292 | 384.3655
951.1292 | 382.2278
952.1292 | 382.3547
953.1292 | 381.9785
954.1292 | 382.187
955.1292 | 382.6856
956.1292 | 383.2973
957.1292 | 383.7669
958.1292 | 384.6152
959.1292 | 385.3285
960.1292 | 385.8143
961.1292 | 386.2246
962.1292 | 386.3208
963.1292 | 386.6843
964.1292 | 386.5952
965.1292 | 386.9553
966.1292 | 387.1749
967.1292 | 387.1288
968.1292 | 387.6407
969.1292 | 388.6952
970.1292 | 388.8905
971.1292 | 388.9644
972.1292 | 389.5491
973.1292 | 390.4779
974.1292 | 390.8167
975.1292 | 390.7061
976.1292 | 390.9052
977.1292 | 391.4062
978.1292 | 392.8738
979.1292 | 392.7384
980.1292 | 392.3875
981.1292 | 392.6903
982.1292 | 392.7135
983.1292 | 394.2577
984.1292 | 393.7949
985.1292 | 394.1431
986.1292 | 394.4103
987.1292 | 394.911
988.1292 | 395.5292
989.1292 | 395.5743
990.1292 | 395.6076
991.1292 | 395.7464
992.1292 | 396.0812
993.1292 | 395.6672
994.1292 | 395.9375
995.1292 | 396.8844
996.1292 | 397.361
997.1292 | 398.5004
998.1292 | 398.2279
999.1292 | 398.1877
1000.1292 | 398.6979
1001.1292 | 399.123
1002.1292 | 400.2967
1003.1292 | 401.1839
1004.1292 | 402.8585
1005.1292 | 403.7738
1006.1292 | 404.3481
1007.1292 | 404.7616
1008.1292 | 406.1117
1009.1292 | 405.7452
1010.1292 | 406.3266
1011.1292 | 406.5797
1012.1292 | 407.8284
1013.1292 | 408.8512
1014.1292 | 408.8521
1015.1292 | 409.4012
1016.1292 | 409.6625
1017.1292 | 410.7876
1018.1292 | 411.1606
1019.1292 | 412.426
1020.1292 | 412.9583
1021.1292 | 412.5264
1022.1292 | 411.2295
1023.1292 | 410.0121
1024.1292 | 410.7246
1025.1292 | 411.0947
1026.1292 | 410.438
1027.1292 | 410.2025
1028.1292 | 410.2803
1029.1292 | 410.383
1030.1292 | 411.1523
1031.1292 | 412.6997
1032.1292 | 413.8715
1033.1292 | 414.7059
1034.1292 | 414.2984
1035.1292 | 414.6125
1036.1292 | 415.6456
1037.1292 | 417.1494
1038.1292 | 419.2832
1039.1292 | 420.7787
1040.1292 | 422.0848
1041.1292 | 422.877
1042.1292 | 423.3217
1043.1292 | 423.5601
1044.1292 | 424.543
1045.1292 | 424.6681
1046.1292 | 425.3653
1047.1292 | 425.3312
1048.1292 | 425.3427
1049.1292 | 425.1138
1050.1292 | 424.5571
1051.1292 | 424.3737
1052.1292 | 424.3998
1053.1292 | 425.0904
1054.1292 | 424.9951
1055.1292 | 425.3079
1056.1292 | 424.2955
1057.1292 | 424.4347
1058.1292 | 423.9759
1059.1292 | 423.5414
1060.1292 | 423.0754
1061.1292 | 423.9757
1062.1292 | 424.3858
1063.1292 | 425.4533
1064.1292 | 426.5589
1065.1292 | 427.6974
1066.1292 | 427.6847
1067.1292 | 428.303
1068.1292 | 428.6487
1069.1292 | 429.635
1070.1292 | 430.1799
1071.1292 | 429.4902
1072.1292 | 430.9604
1073.1292 | 431.6536
1074.1292 | 432.2057
1075.1292 | 431.4654
1076.1292 | 431.4538
1077.1292 | 431.8742
1078.1292 | 432.7719
1079.1292 | 434.1823
1080.1292 | 435.8052
1081.1292 | 436.3297
1082.1292 | 436.8729
1083.1292 | 437.1138
1084.1292 | 436.6837
1085.1292 | 436.8852
1086.1292 | 437.6636
1087.1292 | 437.3742
1088.1292 | 436.1933
1089.1292 | 435.4423
1090.1292 | 436.3595
1091.1292 | 436.897
1092.1292 | 437.8372
1093.1292 | 437.9682
1094.1292 | 437.948
1095.1292 | 438.5083
1096.1292 | 439.3185
1097.1292 | 439.0264
1098.1292 | 438.4871
1099.1292 | 439.5289
1100.1292 | 439.7665
1101.1292 | 441.0002
1102.1292 | 442.1626
1103.1292 | 443.3179
1104.1292 | 444.4374
1105.1292 | 446.2182
1106.1448 | 447.0215
1107.1292 | 447.9844
1108.1292 | 447.9982
1109.1292 | 447.7941
1110.1292 | 448.6686
1111.1292 | 449.3197
1112.1292 | 449.3444
1113.1292 | 450.0052
1114.1292 | 449.5457
1115.1292 | 449.8278
1116.1292 | 450.1241
1117.1292 | 450.2441
1118.1292 | 450.1645
1119.1292 | 451.3749
1120.1292 | 451.494
1121.1292 | 452.8547
1122.1292 | 454.385
1123.1292 | 454.707
1124.1292 | 454.2969
1125.1292 | 453.6986
1126.1292 | 454.6551
1127.1292 | 454.6729
1128.1292 | 453.9246
1129.1292 | 453.2418
1130.1292 | 452.8775
1131.1292 | 453.6003
1132.1292 | 451.5825
1133.1292 | 450.0451
1134.1292 | 449.8103
1135.1292 | 448.9337
1136.1448 | 449.1827
1137.1292 | 451.0191
1138.1292 | 452.0873
1139.1292 | 453.1735
1140.1292 | 453.4804
1141.1292 | 452.6417
1142.1292 | 452.8445
1143.1292 | 453.6147
1144.1292 | 454.1935
1145.1292 | 454.0606
1146.1292 | 454.2624
1147.1448 | 454.9226
1148.1448 | 455.1392
1149.1292 | 455.4731
1150.1292 | 457.3699
1151.1448 | 458.9629
1152.1448 | 459.0775
1153.1448 | 458.9062
1154.1448 | 459.7581
1155.1292 | 458.7254
1156.1292 | 458.6719
1157.1292 | 457.4966
1158.1292 | 456.971
1159.1292 | 456.3485
1160.1292 | 456.2564
1161.1292 | 455.3489
1162.1292 | 454.6345
1163.1292 | 456.3996
1164.1292 | 457.1743
1165.1292 | 458.0372
1166.1448 | 459.6439
1167.1448 | 460.0478
1168.1292 | 461.1883
1169.1292 | 461.8374
1170.1292 | 461.3053
1171.1292 | 461.837
1172.1292 | 461.8315
1173.1292 | 462.0007
1174.1292 | 462.931
1175.1292 | 462.8403
1176.1292 | 461.403
1177.1292 | 460.741
1178.1292 | 461.4145
1179.1292 | 460.915
1180.1292 | 461.4181
1181.1292 | 462.2231
1182.1292 | 462.3149
1183.1292 | 463.1855
1184.1292 | 463.3508
1185.1292 | 463.396
1186.1292 | 463.4945
1187.1292 | 463.3993
1188.1292 | 464.1976
1189.1292 | 464.2342
1190.1292 | 465.3703
1191.1292 | 465.9047
1192.1292 | 465.5
1193.1292 | 466.2409
1194.1292 | 466.9808
1195.1292 | 466.853
1196.1292 | 467.3917
1197.1292 | 468.2366
1198.1292 | 470.6291
1199.1292 | 472.6313
1200.1292 | 472.4723
1201.1292 | 472.8774
1202.1292 | 473.5408
1203.1292 | 474.0092
1204.1292 | 475.4697
1205.1292 | 476.6359
1206.1292 | 476.8997
1207.1292 | 476.9943
1208.1292 | 478.1618
1209.1292 | 478.9661
1210.1292 | 478.6823
1211.1292 | 479.2756
1212.1292 | 480.6541
1213.1292 | 481.425
1214.1292 | 481.5426
1215.1292 | 480.5095
1216.1292 | 479.3199
1217.1292 | 478.3723
1218.1292 | 478.5993
1219.1292 | 477.664
1220.1292 | 477.3562
1221.1292 | 478.8794
1222.1292 | 480.565
1223.1292 | 481.914
1224.1292 | 482.0835
1225.1292 | 483.1055
1226.1292 | 484.2186
1227.1292 | 484.0776
1228.1292 | 485.5275
1229.1292 | 486.302
1230.1292 | 487.2914
1231.1292 | 488.0797
1232.1292 | 488.4811
1233.1292 | 489.1278
1234.1292 | 489.53
1235.1292 | 489.1764
1236.1292 | 488.6882
1237.1292 | 488.4558
1238.1292 | 488.0306
1239.1292 | 488.2147
1240.1292 | 487.4532
1241.1292 | 488.8445
1242.1292 | 489.83
1243.1292 | 490.9093
1244.1292 | 490.8863
1245.1292 | 491.2724
1246.1292 | 491.9895
1247.1292 | 492.6433
1248.1292 | 494.5552
1249.1292 | 494.5367
1250.1448 | 494.4638
1251.1292 | 493.6015
1252.1292 | 492.9383
1253.1292 | 493.0152
1254.1292 | 493.614
1255.1292 | 495.6449
1256.1292 | 496.5664
1257.1292 | 497.3956
1258.1292 | 498.4387
1259.1292 | 497.959
1260.1292 | 498.6316
1261.1292 | 499.4731
1262.1292 | 500.2148
1263.1292 | 500.8486
1264.1292 | 501.1393
1265.1292 | 501.11
1266.1292 | 501.842
1267.1292 | 503.7861
1268.1292 | 505.6494
1269.1292 | 506.0324
1270.1292 | 505.8623
1271.1292 | 506.5168
1272.1292 | 507.7521
1273.1292 | 508.2033
1274.1292 | 508.8598
1275.1292 | 509.7147
1276.1292 | 510.9176
1277.1292 | 509.8196
1278.1292 | 510.2829
1279.1292 | 509.8521
1280.1292 | 509.2191
1281.1292 | 509.3728
1282.1292 | 510.6997
1283.1292 | 509.82
1284.1292 | 509.0499
1285.1292 | 509.0908
1286.1292 | 510.5067
1287.1292 | 512.6866
1288.1292 | 512.5506
1289.1292 | 513.9526
1290.1292 | 514.1568
1291.1292 | 514.3526
1292.1292 | 514.2066
1293.1292 | 513.9375
1294.1292 | 513.9753
1295.1292 | 514.5949
1296.1292 | 513.7113
1297.1292 | 511.7755
1298.1292 | 510.7414
1299.1292 | 509.6074
1300.1292 | 508.8034
1301.1292 | 507.903
1302.1292 | 506.3181
1303.1292 | 506.6654
1304.1292 | 508.4684
1305.1292 | 511.7799
1306.1292 | 511.5093
1307.1292 | 512.1815
1308.1292 | 512.4269
1309.1292 | 512.3809
1310.1292 | 511.9109
1311.1292 | 512.0442
1312.1292 | 511.4445
1313.1292 | 512.0511
1314.1292 | 512.4532
1315.1292 | 511.9767
1316.1292 | 512.5495
1317.1292 | 512.6304
1318.1292 | 513.6972
1319.1292 | 513.7543
1320.1292 | 513.9446
1321.1292 | 513.5444
1322.1292 | 512.8412
1323.1292 | 513.2922
1324.1292 | 513.3989
1325.1292 | 512.5172
1326.1292 | 512.9456
1327.1292 | 513.0468
1328.1292 | 512.9363
1329.1292 | 512.422
1330.1292 | 511.4378
1331.1292 | 511.0022
1332.1292 | 509.6332
1333.1292 | 510.3839
1334.1292 | 510.9894
1335.1292 | 511.3622
1336.1292 | 510.972
1337.1292 | 510.2891
1338.1292 | 509.4468
1339.1292 | 508.4176
1340.1292 | 509.5627
1341.1292 | 509.6066
1342.1292 | 510.0173
1343.1292 | 510.7181
1344.1292 | 511.8626
1345.1292 | 511.5088
1346.1292 | 512.5369
1347.1292 | 512.2899
1348.1292 | 512.0349
1349.1292 | 511.5346
1350.1292 | 511.198
1351.1292 | 511.2071
1352.1292 | 511.0459
1353.1292 | 511.0283
1354.1292 | 510.7747
1355.1292 | 510.6503
1356.1292 | 511.0119
1357.1292 | 511.4083
1358.1292 | 511.3218
1359.1292 | 510.9018
1360.1292 | 511.8382
1361.1292 | 513.7079
1362.1292 | 513.8068
1363.1292 | 513.6204
1364.1292 | 513.4466
1365.1292 | 514.0239
1366.1292 | 514.331
1367.1292 | 513.4134
1368.1292 | 512.466
1369.1292 | 511.6154
1370.1292 | 512.7305
1371.1292 | 512.9381
1372.1292 | 512.9621
1373.1292 | 512.3479
1374.1292 | 512.7739
1375.1292 | 512.9409
1376.1448 | 514.9231
1377.1292 | 514.65
1378.1292 | 514.8083
1379.1292 | 514.4712
1380.1292 | 513.9348
1381.1292 | 513.809
1382.1292 | 512.976
1383.1292 | 512.8823
1384.1292 | 513.0987
1385.1292 | 513.7876
1386.1292 | 515.2005
1387.1292 | 515.2845
1388.1292 | 515.1162
1389.1292 | 515.055
1390.1292 | 514.7846
1391.1448 | 515.3221
1392.1448 | 517.536
1393.1292 | 517.0844
1394.1292 | 516.6439
1395.1448 | 516.09
1396.1448 | 516.0958
1397.1448 | 515.9844
1398.1448 | 516.2977
1399.1292 | 516.8839
1400.1292 | 517.1639
1401.1292 | 517.3822
1402.1292 | 517.8159
1403.1292 | 517.8171
1404.1292 | 517.4543
1405.1292 | 517.2933
1406.1292 | 517.5744
1407.1292 | 517.0391
1408.1292 | 516.5129
1409.1292 | 516.4772
1410.1292 | 518.0182
1411.1292 | 517.1208
1412.1292 | 516.6714
1413.1292 | 516.535
1414.1292 | 517.2476
1415.1292 | 517.262
1416.1292 | 518.7739
1417.1292 | 517.8146
1418.1292 | 518.77
1419.1292 | 518.3246
1420.1292 | 519.4667
1421.1292 | 520.2342
1422.1292 | 521.1525
1423.1292 | 521.4959
1424.1292 | 522.4153
1425.1292 | 522.0007
1426.1292 | 521.8862
1427.1292 | 521.5416
1428.1292 | 522.2978
1429.1292 | 522.4603
1430.1292 | 522.2875
1431.1292 | 522.2106
1432.1292 | 522.9594
1433.1292 | 524.4099
1434.1292 | 524.58
1435.1292 | 524.8606
1436.1292 | 525.4383
1437.1292 | 525.6448
1438.1292 | 525.0403
1439.1292 | 525.3657
1440.1292 | 526.1786
1441.1292 | 525.9767
1442.1292 | 525.5872
1443.1292 | 525.8297
1444.1292 | 526.0154
1445.1292 | 526.841
1446.1292 | 526.9698
1447.1292 | 526.7687
1448.1292 | 526.9059
1449.1292 | 526.7711
1450.1292 | 528.0807
1451.1292 | 528.4834
1452.1292 | 528.3816
1453.1292 | 528.5117
1454.1292 | 530.6341
1455.1292 | 530.5622
1456.1292 | 530.3612
1457.1292 | 529.9117
1458.1292 | 529.7069
1459.1292 | 531.8226
1460.1292 | 531.8969
1461.1292 | 531.954
1462.1292 | 531.4958
1463.1292 | 530.527
1464.1292 | 530.0223
1465.1292 | 530.2147
1466.1448 | 530.6521
1467.1292 | 530.7571
1468.1292 | 531.5282
1469.1292 | 531.5835
1470.1292 | 530.8847
1471.1292 | 530.6772
1472.1292 | 530.8017
1473.1292 | 530.5551
1474.1292 | 531.8842
1475.1292 | 531.3537
1476.1292 | 531.0554
1477.1292 | 532.4464
1478.1292 | 532.546
1479.1292 | 531.8069
1480.1292 | 531.7743
1481.1292 | 533.1481
1482.1292 | 533.3806
1483.1292 | 533.9551
1484.1292 | 532.7176
1485.1292 | 533.561
1486.1292 | 535.3515
1487.1292 | 540.4344
1488.1292 | 541.0413
1489.1292 | 542.9431
1490.1292 | 542.1672
1491.1292 | 541.1567
1492.1292 | 541.1095
1493.1292 | 540.0841
1494.1292 | 540.1111
1495.1292 | 539.9229
1496.1292 | 540.5007
1497.1292 | 540.7769
1498.1292 | 542.2997
1499.1292 | 543.5667
1500.1292 | 544.1923
1501.1292 | 545.7214
1502.1292 | 545.9931
1503.1292 | 544.9493
1504.1292 | 543.5917
1505.1292 | 543.0725
1506.1292 | 543.6385
1507.1292 | 543.6953
1508.1292 | 542.7163
1509.1292 | 542.4268
1510.1292 | 544.5641
1511.1292 | 545.4003
1512.1292 | 543.5561
1513.1292 | 543.8744
1514.1292 | 542.2032
1515.1292 | 541.8677
1516.1292 | 540.3837
1517.1292 | 540.5834
1518.1292 | 542.5755
1519.1292 | 541.3079
1520.1292 | 541.8564
1521.1292 | 541.7129
1522.1292 | 541.2792
1523.1292 | 541.7526
1524.1292 | 540.1125
1525.1292 | 540.4913
1526.1292 | 541.9971
1527.1292 | 541.831
1528.1292 | 540.2339
1529.1292 | 539.9262
1530.1292 | 539.3825
1531.1292 | 539.2136
1532.1292 | 539.1357
1533.1292 | 539.7244
1534.1292 | 539.3553
1535.1292 | 538.8532
1536.1292 | 540.3464
1537.1292 | 540.3911
1538.1292 | 540.3295
1539.1292 | 541.0718
1540.1292 | 540.8271
1541.1292 | 539.9786
1542.1292 | 541.1345
1543.1292 | 542.5673
1544.1292 | 543.2285
1545.1292 | 541.3361
1546.1292 | 539.9334
1547.1292 | 539.2251
1548.1292 | 538.7368
1549.1292 | 540.3446
1550.1292 | 541.9483
1551.1292 | 542.4869
1552.1292 | 542.4333
1553.1292 | 542.614
1554.1292 | 541.3023
1555.1292 | 541.2304
1556.1292 | 541.8993
1557.1292 | 545.392
1558.1292 | 547.945
1559.1292 | 549.3711
1560.1292 | 548.3887
1561.1292 | 548.4411
1562.1292 | 548.0295
1563.1292 | 545.1167
1564.1292 | 544.3856
1565.1292 | 543.3678
1566.1292 | 542.553
1567.1292 | 541.7744
1568.1292 | 542.1318
1569.1292 | 541.5313
1570.1292 | 542.2796
1571.1292 | 540.6278
1572.1292 | 540.8723
1573.1292 | 530.8901
1574.1292 | 531.3136
1575.1292 | 543.0525
1576.1292 | 543.2846
1577.1292 | 543.4074
1578.1292 | 547.0123
1579.1292 | 548.5754
1580.1292 | 550.0225
1581.1292 | 549.3863
1582.1292 | 549.37
1583.1292 | 548.0226
1584.1292 | 549.2089
1585.1292 | 547.7818
1586.1292 | 549.1162
1587.1292 | 548.7549
1588.1292 | 548.7171
1589.1292 | 548.7693
1590.1292 | 548.329
1591.1292 | 549.0986
1592.1292 | 550.1378
1593.1292 | 551.0926
1594.1292 | 549.7966
1595.1292 | 550.874
1596.1292 | 552.455
1597.1292 | 554.6979
1598.1292 | 557.4202
1599.1292 | 560.5096
1600.1292 | 560.1702
1601.1292 | 558.912
1602.1292 | 561.3246
1603.1292 | 563.7729
1604.1292 | 568.515
1605.1292 | 570.481
1606.1292 | 575.5233
1607.1292 | 580.8805
1608.1292 | 584.2009
1609.1292 | 584.623
1610.1292 | 587.0845
1611.1292 | 586.894
1612.1292 | 586.0609
1613.1292 | 584.877
1614.1292 | 580.337
1615.1292 | 576.9057
1616.1292 | 578.1906
1617.1292 | 577.3207
1618.1292 | 578.2655
1619.1292 | 581.029
1620.1292 | 579.0846
1621.1292 | 575.8657
1622.1292 | 571.8181
1623.1292 | 569.8296
1624.1292 | 569.1892
1625.1292 | 566.5094
1626.1292 | 565.0129
1627.1292 | 562.3004
1628.1292 | 560.0654
1629.1292 | 558.8408
1630.1292 | 557.603
1631.1292 | 557.2566
1632.1292 | 555.839
1633.1292 | 557.3027
1634.1292 | 557.3497
1635.1448 | 559.1182
1636.1448 | 560.5022
1637.1292 | 560.9863
1638.1292 | 564.6816
1639.1448 | 564.8923
1640.1448 | 566.3501
1641.1448 | 568.0749
1642.1448 | 567.7611
1643.1292 | 566.2985
1644.1292 | 566.3841
1645.1292 | 565.7634
1646.1292 | 564.0152
1647.1292 | 563.2108
1648.1292 | 560.7934
1649.1292 | 560.3546
1650.1292 | 558.8724
1651.1292 | 558.6262
1652.1448 | 557.9999
1653.1292 | 556.242
1654.1292 | 555.4115
1655.1292 | 554.7677
1656.1292 | 554.1811
1657.1292 | 553.2484
1658.1292 | 552.564
1659.1292 | 551.2622
1660.1292 | 551.6821
1661.1448 | 551.8975
1662.1292 | 554.3101
1663.1292 | 554.9673
1664.1292 | 554.8096
1665.1292 | 554.9175
1666.1292 | 555.0433
1667.1292 | 554.2217
1668.1292 | 554.4332
1669.1292 | 554.024
1670.1292 | 554.6342
1671.1292 | 554.3424
1672.1292 | 554.6057
1673.1292 | 553.7351
1674.1292 | 553.0675
1675.1292 | 552.0126
1676.1292 | 551.2403
1677.1292 | 551.8281
1678.1292 | 552.5818
1679.1292 | 552.0802
1680.1292 | 553.946
1681.1292 | 555.9714
1682.1292 | 555.7942
1683.1292 | 555.5361
1684.1292 | 556.6169
1685.1292 | 557.3069
1686.1292 | 556.5163
1687.1292 | 556.5998
1688.1292 | 556.2486
1689.1292 | 556.8727
1690.1292 | 556.4109
1691.1292 | 558.0538
1692.1292 | 561.8677
1693.1292 | 562.181
1694.1292 | 563.6794
1695.1292 | 562.9768
1696.1292 | 561.1837
1697.1292 | 559.9548
1698.1292 | 561.4724
1699.1292 | 561.9661
1700.1292 | 564.0764
1701.1292 | 563.6933
1702.1292 | 565.9116
1703.1292 | 571.0815
1704.1292 | 573.571
1705.1292 | 574.109
1706.1292 | 574.8294
1707.1292 | 575.839
1708.1292 | 573.6396
1709.1292 | 573.1332
1710.1292 | 572.6148
1711.1292 | 571.5035
1712.1292 | 569.2711
1713.1292 | 567.7104
1714.1292 | 566.1112
1715.1292 | 564.875
1716.1292 | 563.0549
1717.1292 | 562.1038
1718.1292 | 561.223
1719.1292 | 561.8928
1720.1292 | 560.9023
1721.1292 | 560.1157
1722.1292 | 560.0334
1723.1292 | 561.6206
1724.1292 | 561.6083
1725.1292 | 561.5696
1726.1292 | 560.4757
1727.1292 | 560.2518
1728.1292 | 560.9284
1729.1292 | 560.628
1730.1292 | 560.4979
1731.1292 | 562.4527
1732.1292 | 564.2077
1733.1292 | 563.4878
1734.1292 | 564.7551
1735.1292 | 566.2464
1736.1292 | 567.1959
1737.1292 | 565.9951
1738.1292 | 566.7021
1739.1292 | 565.3773
1740.1292 | 565.7281
1741.1292 | 565.3356
1742.1292 | 566.7632
1743.1292 | 565.7303
1744.1292 | 563.9687
1745.1292 | 565.088
1746.1292 | 565.4467
1747.1292 | 566.1223
1748.1292 | 568.6543
1749.1292 | 568.4107
1750.1292 | 568.1777
1751.1292 | 566.8436
1752.1292 | 565.7738
1753.1292 | 565.6039
1754.1292 | 564.2168
1755.1292 | 563.5204
1756.1292 | 564.2479
1757.1292 | 563.9291
1758.1292 | 565.8734
1759.1292 | 566.0984
1760.1292 | 566.9054
1761.1292 | 568.008
1762.1292 | 571.1504
1763.1292 | 569.9825
1764.1292 | 571.5032
1765.1292 | 575.3795
1766.1292 | 577.8642
1767.1292 | 579.2645
1768.1292 | 579.3837
1769.1292 | 581.6159
1770.1292 | 582.7987
1771.1292 | 585.1043
1772.1292 | 586.1023
1773.1292 | 584.6352
1774.1292 | 583.4546
1775.1292 | 581.6691
1776.1292 | 579.2155
1777.1292 | 577.9514
1778.1292 | 578.3822
1779.1292 | 577.9196
1780.1292 | 577.7908
1781.1292 | 577.9908
1782.1292 | 578.1255
1783.1292 | 577.5992
1784.1292 | 577.1464
1785.1292 | 575.9557
1786.1292 | 574.3523
1787.1292 | 575.6856
1788.1292 | 577.4507
1789.1292 | 580.2325
1790.1292 | 582.0599
1791.1292 | 581.1965
1792.1292 | 582.128
1793.1292 | 584.3666
1794.1292 | 586.7768
1795.1292 | 587.5672
1796.1292 | 587.4734
1797.1292 | 585.8593
1798.1292 | 584.5544
1799.1292 | 583.651
1800.1292 | 582.3842
1801.1292 | 580.9488
1802.1292 | 580.5827
1803.1292 | 580.4147
1804.1292 | 579.0164
1805.1292 | 578.8869
1806.1292 | 577.0746
1807.1292 | 575.7866
1808.1292 | 575.5662
1809.1292 | 576.5108
1810.1292 | 575.7192
1811.1292 | 576.9275
1812.1292 | 577.051
1813.1292 | 576.2415
1814.1292 | 574.9388
1815.1292 | 574.2335
1816.1292 | 574.1189
1817.1292 | 577.6747
1818.1292 | 579.5219
1819.1292 | 579.5427
1820.1292 | 577.7767
1821.1292 | 576.8664
1822.1292 | 575.8089
1823.1292 | 577.5469
1824.1292 | 578.285
1825.1292 | 577.5519
1826.1292 | 576.1148
1827.1292 | 577.1011
1828.1292 | 577.1103
1829.1292 | 575.7934
1830.1292 | 574.4739
1831.1292 | 574.9798
1832.1292 | 575.7497
1833.1292 | 576.4582
1834.1292 | 576.4385
1835.1292 | 578.5431
1836.1292 | 578.7915
1837.1292 | 577.5657
1838.1292 | 576.498
1839.1292 | 574.8841
1840.1292 | 573.4825
1841.1292 | 572.6224
1842.1292 | 571.1632
1843.1292 | 570.1603
1844.1292 | 571.4044
1845.1292 | 570.5488
1846.1292 | 569.3105
1847.1292 | 568.9806
1848.1292 | 568.3541
1849.1292 | 568.571
1850.1292 | 568.1487
1851.1292 | 569.1826
1852.1292 | 569.7071
1853.1292 | 569.9079
1854.1292 | 571.6418
1855.1292 | 570.873
1856.1292 | 572.6435
1857.1292 | 573.1689
1858.1292 | 572.5682
1859.1292 | 574.0454
1860.1292 | 575.3966
1861.1292 | 577.7243
1862.1292 | 577.7056
1863.1292 | 579.7575
1864.1292 | 581.0629
1865.1292 | 581.7706
1866.1292 | 580.521
1867.1292 | 579.9337
1868.1292 | 581.6963
1869.1292 | 582.6388
1870.1292 | 582.1928
1871.1292 | 582.4045
1872.1292 | 580.6701
1873.1448 | 579.8164
1874.1448 | 579.3479
1875.1292 | 580.2364
1876.1292 | 580.8097
1877.1448 | 580.4305
1878.1292 | 581.7388
1879.1448 | 581.2982
1880.1292 | 580.0612
1881.1292 | 579.6804
1882.1292 | 580.2269
1883.1292 | 582.067
1884.1292 | 582.613
1885.1292 | 581.7996
1886.1292 | 580.9318
1887.1292 | 580.8491
1888.1292 | 580.1727
1889.1292 | 579.416
1890.1292 | 579.4768
1891.1292 | 579.3942
1892.1292 | 578.3859
1893.1292 | 578.2349
1894.1292 | 577.817
1895.1292 | 579.61
1896.1292 | 582.0942
1897.1292 | 583.1853
1898.1292 | 583.0933
1899.1292 | 584.4458
1900.1292 | 584.7901
1901.1292 | 583.825
1902.1292 | 583.329
1903.1292 | 587.6127
1904.1292 | 589.0214
1905.1292 | 587.7181
1906.1292 | 586.8289
1907.1292 | 585.8907
1908.1292 | 584.2482
1909.1292 | 583.8979
1910.1292 | 584.7039
1911.1292 | 584.062
1912.1292 | 582.6624
1913.1292 | 582.7707
1914.1292 | 582.3169
1915.1292 | 581.3059
1916.1292 | 580.1134
1917.1292 | 579.4601
1918.1292 | 579.8699
1919.1292 | 578.9664
1920.1292 | 581.1241
1921.1292 | 588.7411
1922.1292 | 590.5256
1923.1292 | 592.3508
1924.1292 | 593.537
1925.1292 | 593.7312
1926.1292 | 591.7904
1927.1292 | 590.9585
1928.1292 | 591.1605
1929.1292 | 589.7975
1930.1292 | 589.0866
1931.1292 | 590.6062
1932.1292 | 591.4339
1933.1292 | 590.4014
1934.1292 | 588.8415
1935.1292 | 592.9258
1936.1292 | 598.8172
1937.1292 | 599.1601
1938.1292 | 598.0723
1939.1292 | 596.4837
1940.1292 | 599.9725
1941.1292 | 598.2481
1942.1292 | 596.3798
1943.1292 | 595.5063
1944.1292 | 592.9636
1945.1292 | 591.689
1946.1292 | 590.4193
1947.1292 | 590.2062
1948.1292 | 589.5385
1949.1292 | 590.996
1950.1292 | 590.4857
1951.1292 | 590.1487
1952.1292 | 590.3202
1953.1292 | 590.6789
1954.1292 | 589.8207
1955.1292 | 590.5599
1956.1292 | 589.2672
1957.1292 | 589.9341
1958.1292 | 590.0905
1959.1292 | 589.227
1960.1292 | 588.0804
1961.1292 | 594.8795
1962.1292 | 596.4785
1963.1292 | 600.4251
1964.1292 | 600.1862
1965.1292 | 600.9984
1966.1292 | 599.4908
1967.1292 | 598.8769
1968.1292 | 598.003
1969.1292 | 601.6966
1970.1292 | 603.3993
1971.1292 | 602.5061
1972.1292 | 600.7146
1973.1292 | 599.9759
1974.1292 | 599.1982
1975.1292 | 599.2978
1976.1292 | 598.8765
1977.1292 | 602.5638
1978.1292 | 601.1073
1979.1292 | 601.0717
1980.1292 | 599.4504
1981.1292 | 601.7705
1982.1292 | 601.8393
1983.1292 | 598.8878
1984.1292 | 598.478
1985.1292 | 599.0267
1986.1292 | 599.1952
1987.1292 | 597.5265
1988.1292 | 595.3153
1989.1292 | 595.4854
1990.1292 | 593.4407
1991.1292 | 593.0612
1992.1292 | 594.4234
1993.1292 | 593.5708
1994.1292 | 592.7566
1995.1292 | 592.3994
1996.1292 | 591.0003
1997.1292 | 591.5227
1998.1292 | 593.9843
1999.1292 | 595.6329
2000.1292 | 595.5744
2001.1292 | 595.4818
2002.1292 | 595.2062
2003.1292 | 595.5114
2004.1292 | 594.7606
2005.1292 | 594.7898
2006.1292 | 594.4669
2007.1292 | 593.2433
2008.1292 | 593.8096
2009.1292 | 595.0631
2010.1292 | 595.0293
2011.1292 | 595.3095
2012.1292 | 594.7218
2013.1292 | 594.8506
2014.1292 | 594.2978
2015.1292 | 594.3675
2016.1292 | 593.5525
2017.1292 | 592.4752
2018.1292 | 596.8018
2019.1292 | 598.3672
2020.1292 | 599.6412
2021.1292 | 603.0578
2022.1292 | 604.2225
2023.1292 | 605.9971
2024.1292 | 608.0951
2025.1292 | 609.0613
2026.1292 | 612.4063
2027.1292 | 613.8207
2028.1292 | 613.0983
2029.1292 | 613.8507
2030.1292 | 611.9151
2031.1292 | 609.6367
2032.1292 | 608.9451
2033.1292 | 607.9493
2034.1292 | 607.3486
2035.1292 | 608.2588
2036.1292 | 607.1523
2037.1292 | 606.6241
2038.1292 | 606.5674
2039.1292 | 610.0397
2040.1292 | 609.2648
2041.1292 | 608.5638
2042.1292 | 606.8279
2043.1292 | 605.1263
2044.1292 | 604.401
2045.1292 | 605.6899
2046.1292 | 606.6162
2047.1292 | 605.69
2048.1292 | 604.1011
2049.1292 | 602.8604
2050.1292 | 601.4206
2051.1292 | 600.5973
2052.1292 | 599.8621
2053.1292 | 599.3925
2054.1292 | 600.4792
2055.1292 | 600.0922
2056.1292 | 600.2886
2057.1292 | 599.6193
2058.1292 | 600.1937
2059.1292 | 601.1399
2060.1292 | 600.7369
2061.1292 | 599.3744
2062.1292 | 599.0152
2063.1292 | 599.0733
2064.1292 | 599.6263
2065.1292 | 600.8768
2066.1292 | 602.3171
2067.1292 | 602.4915
2068.1292 | 605.1628
2069.1292 | 605.3807
2070.1292 | 605.6165
2071.1292 | 605.0549
2072.1292 | 605.3164
2073.1292 | 604.9213
2074.1292 | 606.9757
2075.1292 | 607.4397
2076.1292 | 606.7086
2077.1292 | 604.4516
2078.1292 | 603.6349
2079.1292 | 602.0214
2080.1292 | 600.5482
2081.1292 | 600.2908
2082.1292 | 599.3045
2083.1292 | 599.2582
2084.1292 | 599.0051
2085.1292 | 597.7855
2086.1292 | 597.4269
2087.1292 | 598.3423
2088.1292 | 602.4582
2089.1292 | 604.1185
2090.1292 | 602.7403
2091.1292 | 603.8383
2092.1292 | 603.8339
2093.1292 | 604.6808
2094.1292 | 603.6841
2095.1292 | 602.0745
2096.1292 | 601.7284
2097.1292 | 600.9855
2098.1292 | 601.7697
2099.1292 | 602.1935
2100.1292 | 602.9443
2101.1292 | 603.4871
2102.1292 | 603.3092
2103.1292 | 602.5422
2104.1292 | 602.4134
2105.1292 | 603.59
2106.1292 | 602.1168
2107.1292 | 600.0168
2108.1292 | 599.1764
2109.1292 | 597.4831
2110.1292 | 596.2174
2111.1292 | 596.4014
2112.1292 | 594.9762
2113.1292 | 594.9001
2114.1292 | 595.2305
2115.1292 | 597.1009
2116.1292 | 595.9656
2117.1292 | 595.0336
2118.1292 | 594.5012
2119.1448 | 595.9143
2120.1292 | 598.3751
2121.1448 | 601.7219
2122.1292 | 605.3868
2123.1448 | 606.0502
2124.1292 | 607.6906
2125.1448 | 609.2531
2126.1292 | 609.0144
2127.1292 | 607.7938
2128.1292 | 609.1512
2129.1292 | 609.3374
2130.1292 | 610.0861
2131.1292 | 616.4096
2132.1292 | 617.2478
2133.1292 | 616.6413
2134.1292 | 616.178
2135.1292 | 615.0976
2136.1292 | 615.0018
2137.1292 | 614.688
2138.1292 | 614.0015
2139.1292 | 612.8019
2140.1292 | 613.6572
2141.1292 | 612.2681
2142.1292 | 610.0816
2143.1292 | 608.8536
2144.1292 | 607.65
2145.1292 | 608.0401
2146.1292 | 611.9681
2147.1292 | 614.7691
2148.1292 | 615
2149.1292 | 615.9682
2150.1292 | 615.4793
2151.1292 | 615.0506
2152.1292 | 614.0536
2153.1292 | 613.3501
2154.1292 | 613.6477
2155.1292 | 614.1257
2156.1292 | 615.367
2157.1292 | 614.3119
2158.1292 | 612.5062
2159.1292 | 611.305
2160.1292 | 611.1499
2161.1292 | 612.1632
2162.1292 | 610.4369
2163.1292 | 612.8087
2164.1292 | 611.1635
2165.1292 | 609.1372
2166.1292 | 609.8206
2167.1292 | 612.3289
2168.1292 | 614.2157
2169.1292 | 614.2396
2170.1292 | 614.9165
2171.1292 | 612.7085
2172.1292 | 609.9622
2173.1292 | 608.7335
2174.1292 | 609.2602
2175.1292 | 608.641
2176.1292 | 607.1166
2177.1292 | 607.6338
2178.1292 | 609.9561
2179.1292 | 610.0256
2180.1292 | 611.0053
2181.1292 | 611.4103
2182.1292 | 610.4349
2183.1292 | 609.9139
2184.1292 | 608.3237
2185.1292 | 607.5912
2186.1292 | 606.6583
2187.1292 | 605.5167
2188.1292 | 605.2376
2189.1292 | 604.6736
2190.1292 | 604.6403
2191.1292 | 604.7729
2192.1292 | 605.3126
2193.1292 | 604.8642
2194.1292 | 602.7115
2195.1292 | 602.1275
2196.1292 | 602.0488
2197.1292 | 602.507
2198.1292 | 602.6894
2199.1292 | 601.5926
2200.1292 | 600.955
2201.1292 | 602.8941
2202.1292 | 603.1522
2203.1292 | 603.4872
2204.1292 | 604.9512
2205.1292 | 605.3028
2206.1292 | 606.3229
2207.1292 | 607.4324
2208.1292 | 608.6255
2209.1292 | 608.5474
2210.1292 | 608.1952
2211.1292 | 607.6481
2212.1292 | 606.1279
2213.1292 | 604.4244
2214.1292 | 604.5458
2215.1292 | 605.3593
2216.1292 | 607.003
2217.1292 | 607.6624
2218.1292 | 608.2498
2219.1292 | 610.1374
2220.1292 | 609.5169
2221.1292 | 609.7715
2222.1292 | 608.3548
2223.1292 | 606.2326
2224.1292 | 604.9421
2225.1292 | 604.3686
2226.1292 | 604.1437
2227.1292 | 603.9566
2228.1292 | 603.5763
2229.1292 | 603.3094
2230.1292 | 603.7676
2231.1292 | 602.6683
2232.1292 | 603.2941
2233.1292 | 603.4535
2234.1292 | 604.1468
2235.1292 | 605.3746
2236.1292 | 606.0532
2237.1292 | 605.2533
2238.1292 | 604.7392
2239.1292 | 604.1372
2240.1292 | 603.4902
2241.1292 | 603.7508
2242.1292 | 604.5653
2243.1292 | 603.9106
2244.1292 | 603.7901
2245.1292 | 603.1975
2246.1292 | 603.4083
2247.1292 | 602.9926
2248.1292 | 602.6716
2249.1292 | 602.3554
2250.1292 | 602.2712
2251.1292 | 603.6433
2252.1292 | 604.027
2253.1292 | 604.6448
2254.1292 | 605.0215
2255.1292 | 605.9166
2256.1292 | 606.94
2257.1292 | 608.8991
2258.1292 | 610.6141
2259.1292 | 611.3208
2260.1292 | 612.2595
2261.1292 | 613.6505
2262.1292 | 613.5396
2263.1292 | 613.1829
2264.1292 | 612.2311
2265.1292 | 611.1264
2266.1292 | 610.2902
2267.1292 | 609.8305
2268.1292 | 609.2919
2269.1292 | 608.639
2270.1292 | 608.2473
2271.1292 | 608.7392
2272.1292 | 609.308
2273.1292 | 608.5528
2274.1292 | 607.5136
2275.1292 | 606.3648
2276.1292 | 606.2092
2277.1292 | 607.3903
2278.1292 | 608.1135
2279.1292 | 608.6337
2280.1292 | 608.5296
2281.1292 | 607.5552
2282.1292 | 606.7345
2283.1292 | 606.3287
2284.1292 | 606.1587
2285.1292 | 606.3515
2286.1292 | 606.6366
2287.1292 | 605.4599
2288.1292 | 607.0575
2289.1292 | 608.381
2290.1292 | 609.5213
2291.1292 | 608.9637
2292.1292 | 609.1099
2293.1292 | 606.9368
2294.1292 | 606.7053
2295.1292 | 607.3453
2296.1292 | 608.8098
2297.1292 | 610.165
2298.1292 | 610.9203
2299.1292 | 610.086
2300.1292 | 611.472
2301.1292 | 609.457
2302.1292 | 608.2658
2303.1292 | 607.2082
2304.1292 | 609.1516
2305.1292 | 609.6738
2306.1292 | 610.2474
2307.1292 | 611.6102
2308.1292 | 611.7058
2309.1292 | 611.7044
2310.1292 | 611.4094
2311.1292 | 610.7847
2312.1292 | 609.8652
2313.1292 | 609.9367
2314.1292 | 609.3623
2315.1292 | 610.0334
2316.1292 | 609.4786
2317.1292 | 609.0086
2318.1292 | 608.1479
2319.1292 | 608.6278
2320.1292 | 608.2957
2321.1292 | 607.708
2322.1292 | 607.3077
2323.1292 | 607.8056
2324.1292 | 607.8203
2325.1292 | 608.2664
2326.1292 | 607.8229
2327.1292 | 607.1331
2328.1292 | 607.1111
2329.1292 | 606.9227
2330.1292 | 608.0442
2331.1292 | 609.1935
2332.1292 | 609.729
2333.1292 | 609.3499
2334.1448 | 608.8281
2335.1292 | 609.326
2336.1292 | 609.0988
2337.1448 | 608.6972
2338.1292 | 608.1344
2339.1292 | 608.4986
2340.1292 | 608.5505
2341.1292 | 608.2833
2342.1292 | 607.9322
2343.1292 | 609.0979
2344.1292 | 610.4181
2345.1292 | 610.2541
2346.1292 | 611.4623
2347.1292 | 611.2798
2348.1292 | 610.7457
2349.1292 | 610.8091
2350.1292 | 610.1416
2351.1292 | 610.1835
2352.1292 | 610.7913
2353.1292 | 613.6644
2354.1292 | 614.3717
2355.1292 | 613.302
2356.1292 | 613.5522
2357.1292 | 613.4281
2358.1292 | 615.0315
2359.1292 | 614.9456
2360.1292 | 615.6489
2361.1292 | 615.8333
2362.1448 | 616.3273
2363.1292 | 617.7496
2364.1448 | 616.2006
2365.1292 | 617.2489
2366.1448 | 616.9626
2367.1292 | 616.9227
2368.1292 | 616.9616
2369.1292 | 616.0293
2370.1292 | 615.9756
2371.1292 | 616.5434
2372.1292 | 616.0268
2373.1292 | 616.2954
2374.1448 | 616.5276
2375.1292 | 615.658
2376.1292 | 615.0377
2377.1292 | 615.1788
2378.1292 | 614.5591
2379.1292 | 614.3348
2380.1292 | 614.8483
2381.1292 | 614.2714
2382.1292 | 613.9292
2383.1292 | 612.9948
2384.1292 | 612.6884
2385.1292 | 612.1718
2386.1292 | 613.0071
2387.1292 | 615.4087
2388.1292 | 616.1652
2389.1292 | 616.5832
2390.1292 | 616.6013
2391.1292 | 616.9146
2392.1292 | 617.6757
2393.1292 | 618.1041
2394.1292 | 618.3644
2395.1292 | 618.7499
2396.1292 | 618.7355
2397.1448 | 619.1461
2398.1292 | 619.3286
2399.1292 | 619.1181
2400.1292 | 619.3576
2401.1292 | 618.9472
2402.1292 | 618.0861
2403.1292 | 618.1188
2404.1292 | 616.6068
2405.1292 | 615.1288
2406.1292 | 614.6426
2407.1292 | 614.8544
2408.1292 | 615.0618
2409.1292 | 616.1258
2410.1292 | 616.4936
2411.1292 | 617.299
2412.1292 | 618.5495
2413.1292 | 619.0695
2414.1292 | 619.1718
2415.1292 | 619.3489
2416.1292 | 619.642
2417.1292 | 618.8238
2418.1292 | 619.4
2419.1292 | 619.3701
2420.1292 | 619.6569
2421.1292 | 620.5589
2422.1292 | 620.9851
2423.1292 | 620.4154
2424.1292 | 620.5498
2425.1292 | 620.7054
2426.1292 | 620.9697
2427.1292 | 619.873
2428.1292 | 619.7683
2429.1292 | 620.4083
2430.1292 | 620.6203
2431.1292 | 621.7573
2432.1292 | 621.3869
2433.1292 | 621.5347
2434.1292 | 622.1213
2435.1292 | 622.3638
2436.1292 | 622.8398
2437.1292 | 622.8598
2438.1292 | 623.5789
2439.1292 | 624.1462
2440.1292 | 623.8535
2441.1292 | 624.8016
2442.1292 | 625.4628
2443.1292 | 624.9972
2444.1292 | 624.4554
2445.1292 | 624.4011
2446.1292 | 624.6531
2447.1292 | 625.9427
2448.1292 | 626.3461
2449.1292 | 626.4595
2450.1292 | 626.8968
2451.1292 | 629.081
2452.1292 | 629.1111
2453.1292 | 629.2135
2454.1292 | 626.8036
2455.1292 | 627.0867
2456.1292 | 627.7029
2457.1448 | 628.2751
2458.1292 | 627.8949
2459.1292 | 627.5801
2460.1292 | 628.1089
2461.1292 | 628.7542
2462.1292 | 627.1004
2463.1292 | 626.4863
2464.1292 | 626.0752
2465.1292 | 626.8945
2466.1292 | 626.7571
2467.1292 | 627.6925
2468.1292 | 628.6804
2469.1292 | 628.9829
2470.1292 | 630.5509
2471.1448 | 630.7493
2472.1292 | 631.7923
2473.1292 | 631.7795
2474.1292 | 631.8353
2475.1292 | 632.0413
2476.1292 | 630.8075
2477.1292 | 630.2694
2478.1292 | 631.3244
2479.1292 | 632.2187
2480.1292 | 632.2825
2481.1292 | 632.6367
2482.1292 | 632.6415
2483.1292 | 631.4348
2484.1292 | 631.3578
2485.1292 | 628.5397
2486.1292 | 628.2026
2487.1448 | 628.7724
2488.1292 | 629.2629
2489.1292 | 629.8195
2490.1292 | 629.8546
2491.1292 | 629.8809
2492.1292 | 630.244
2493.1292 | 630.7766
2494.1292 | 631.4891
2495.1292 | 631.2324
2496.1292 | 633.8875
2497.1292 | 633.882
2498.1292 | 633.1806
2499.1292 | 634.1482
2500.1292 | 635.3721
2501.1292 | 635.091
2502.1292 | 635.0913
2503.1292 | 635.8241
2504.1292 | 635.8034
2505.1292 | 635.7733
2506.1292 | 636.5209
2507.1292 | 636.7058
2508.1292 | 637.2239
2509.1292 | 637.0666
2510.1292 | 637.2528
2511.1292 | 637.2849
2512.1292 | 637.3588
2513.1292 | 636.4295
2514.1292 | 636.4191
2515.1292 | 635.9751
2516.1292 | 636.2979
2517.1292 | 635.9591
2518.1292 | 636.1004
2519.1292 | 636.2279
2520.1292 | 635.3342
2521.1292 | 634.7287
2522.1292 | 635.2547
2523.1292 | 636.691
2524.1292 | 636.4702
2525.1292 | 637.6054
2526.1292 | 637.2694
2527.1292 | 635.8388
2528.1292 | 636.4839
2529.1292 | 635.3816
2530.1292 | 635.4697
2531.1292 | 635.0437
2532.1292 | 635.0657
2533.1292 | 634.5751
2534.1292 | 634.5112
2535.1292 | 635.4927
2536.1292 | 636.0894
2537.1292 | 636.0834
2538.1292 | 637.0476
2539.1292 | 638.2679
2540.1292 | 638.6593
2541.1292 | 638.7827
2542.1292 | 639.6551
2543.1292 | 638.7596
2544.1292 | 638.7149
2545.1292 | 639.0145
2546.1292 | 639.6331
2547.1292 | 639.2558
2548.1292 | 640.1384
2549.1292 | 640.06
2550.1292 | 640.1088
2551.1292 | 639.8984
2552.1292 | 639.8165
2553.1292 | 640.0654
2554.1292 | 639.6603
2555.1292 | 640.2692
2556.1292 | 641.1733
2557.1292 | 640.5155
2558.1292 | 640.467
2559.1292 | 640.2752
2560.1292 | 640.2983
2561.1292 | 639.7192
2562.1292 | 640.8636
2563.1292 | 641.2541
2564.1292 | 641.7152
2565.1292 | 641.9189
2566.1292 | 640.9595
2567.1292 | 640.519
2568.1292 | 641.7628
2569.1292 | 641.5255
2570.1292 | 641.2067
2571.1292 | 641.1439
2572.1292 | 640.8295
2573.1292 | 639.9541
2574.1292 | 640.4868
2575.1292 | 640.6979
2576.1292 | 642.2497
2577.1292 | 642.4159
2578.1292 | 642.9532
2579.1292 | 641.6105
2580.1292 | 640.8093
2581.1292 | 640.625
2582.1292 | 641.3267
2583.1292 | 640.6888
2584.1292 | 640.2207
2585.1292 | 640.0355
2586.1292 | 640.9542
2587.1292 | 640.5566
2588.1292 | 639.5992
2589.1292 | 639.0226
2590.1292 | 639.1271
2591.1292 | 639.6197
2592.1292 | 639.4108
2593.1292 | 639.9626
2594.1292 | 639.6027
2595.1292 | 640.0962
2596.1292 | 639.8923
2597.1292 | 639.1708
2598.1292 | 639.3099
2599.1448 | 639.2794
2600.1448 | 640.3253
2601.1292 | 639.8099
2602.1292 | 638.576
2603.1448 | 638.3685
2604.1448 | 638.148
2605.1448 | 638.7794
2606.1292 | 638.4715
2607.1292 | 638.942
2608.1292 | 638.7351
2609.1292 | 639.0157
2610.1292 | 639.1964
2611.1292 | 640.1447
2612.1292 | 640.6965
2613.1292 | 640.4534
2614.1292 | 640.7338
2615.1292 | 640.3342
2616.1292 | 640.5875
2617.1292 | 640.8959
2618.1292 | 642.3915
2619.1292 | 642.4489
2620.1292 | 642.9415
2621.1292 | 643.2977
2622.1292 | 643.5468
2623.1292 | 642.8419
2624.1292 | 642.7943
2625.1292 | 642.2927
2626.1292 | 642.6724
2627.1292 | 643.0405
2628.1292 | 644.1925
2629.1292 | 644.0269
2630.1292 | 643.6196
2631.1292 | 644.588
2632.1292 | 644.8285
2633.1292 | 645.1068
2634.1292 | 645.3519
2635.1292 | 645.3861
2636.1292 | 645.1754
2637.1292 | 645.5116
2638.1292 | 645.6937
2639.1292 | 645.7693
2640.1292 | 646.7684
2641.1292 | 646.1749
2642.1292 | 645.0473
2643.1292 | 644.4515
2644.1292 | 644.2754
2645.1292 | 644.957
2646.1292 | 645.7688
2647.1292 | 646.3197
2648.1292 | 646.0684
2649.1292 | 646.6016
2650.1292 | 647.4609
2651.1292 | 646.6577
2652.1292 | 648.0494
2653.1292 | 648.3043
2654.1292 | 648.1702
2655.1292 | 649.0412
2656.1292 | 649.189
2657.1292 | 649.8963
2658.1292 | 650.3165
2659.1292 | 649.8417
2660.1292 | 650.1431
2661.1292 | 651.4502
2662.1292 | 652.0821
2663.1292 | 651.8978
2664.1292 | 651.1678
2665.1292 | 650.0938
2666.1292 | 648.8048
2667.1292 | 648.0544
2668.1292 | 648.5444
2669.1292 | 649.1441
2670.1292 | 650.8448
2671.1292 | 651.8608
2672.1292 | 653.036
2673.1292 | 653.7685
2674.1292 | 655.538
2675.1292 | 655.3289
2676.1292 | 654.3798
2677.1292 | 654.1291
2678.1292 | 654.405
2679.1292 | 654.5305
2680.1292 | 653.2805
2681.1292 | 652.2311
2682.1292 | 652.1505
2683.1292 | 653.0127
2684.1292 | 654.3722
2685.1292 | 652.3391
2686.1292 | 651.5673
2687.1292 | 651.5393
2688.1292 | 651.9353
2689.1292 | 652.6537
2690.1292 | 652.2034
2691.1292 | 650.742
2692.1292 | 649.9511
2693.1292 | 650.1598
2694.1292 | 649.7244
2695.1292 | 648.971
2696.1292 | 649.153
2697.1292 | 648.4708
2698.1292 | 648.2798
2699.1292 | 647.9804
2700.1292 | 648.5219
2701.1292 | 648.8731
2702.1292 | 649.007
2703.1292 | 649.891
2704.1292 | 650.94
2705.1292 | 651.804
2706.1292 | 652.5746
2707.1292 | 652.9901
2708.1292 | 652.4393
2709.1292 | 652.2672
2710.1292 | 652.1763
2711.1292 | 651.3209
2712.1292 | 651.5696
2713.1292 | 651.3035
2714.1292 | 651.2299
2715.1292 | 651.1823
2716.1292 | 650.6892
2717.1292 | 650.3781
2718.1292 | 649.5563
2719.1292 | 649.1052
2720.1292 | 648.6664
2721.1292 | 648.4771
2722.1292 | 648.3037
2723.1292 | 647.8836
2724.1292 | 648.5247
2725.1292 | 648.8939
2726.1292 | 649.2573
2727.1292 | 649.0251
2728.1292 | 649.7751
2729.1292 | 649.1326
2730.1292 | 649.1075
2731.1292 | 648.78
2732.1292 | 648.749
2733.1292 | 648.2407
2734.1292 | 648.3348
2735.1292 | 648.1306
2736.1292 | 648.7756
2737.1292 | 649.0248
2738.1292 | 648.7315
2739.1292 | 646.8256
2740.1292 | 646.204
2741.1292 | 646.4248
2742.1292 | 646.8288
2743.1292 | 647.2944
2744.1292 | 648.2529
2745.1292 | 647.7673
2746.1292 | 647.596
2747.1292 | 647.7191
2748.1292 | 648.4156
2749.1292 | 648.5343
2750.1292 | 647.4047
2751.1292 | 646.6113
2752.1292 | 647.3175
2753.1292 | 647.8527
2754.1448 | 647.6568
2755.1292 | 647.8784
2756.1292 | 647.2621
2757.1292 | 647.4015
2758.1292 | 647.1008
2759.1292 | 647.9738
2760.1292 | 649.3506
2761.1292 | 650.8628
2762.1292 | 651.3672
2763.1292 | 651.2776
2764.1292 | 650.0225
2765.1448 | 649.9841
2766.1292 | 650.2687
2767.1292 | 650.2189
2768.1292 | 650.3832
2769.1292 | 649.5122
2770.1292 | 649.0854
2771.1292 | 649.1126
2772.1292 | 648.1482
2773.1292 | 648.1647
2774.1292 | 647.8603
2775.1292 | 647.1076
2776.1292 | 646.7703
2777.1292 | 646.3068
2778.1292 | 646.3016
2779.1292 | 646.7523
2780.1448 | 645.9335
2781.1292 | 646.2623
2782.1292 | 646.3062
2783.1292 | 646.0495
2784.1292 | 645.6565
2785.1292 | 645.6373
2786.1292 | 646.359
2787.1292 | 645.4439
2788.1292 | 643.685
2789.1292 | 644.2609
2790.1292 | 644.8777
2791.1292 | 645.318
2792.1292 | 645.8272
2793.1292 | 644.6844
2794.1292 | 645.8892
2795.1292 | 644.4322
2796.1292 | 644.3261
2797.1292 | 644.0426
2798.1292 | 644.6077
2799.1292 | 645.1054
2800.1292 | 645.7471
2801.1292 | 644.8938
2802.1292 | 644.3521
2803.1292 | 643.9346
2804.1292 | 644.083
2805.1292 | 644.3724
2806.1292 | 644.6995
2807.1292 | 645.0017
2808.1292 | 644.7953
2809.1292 | 644.3149
2810.1292 | 644.1921
2811.1292 | 644.084
2812.1292 | 644.1836
2813.1292 | 644.2351
2814.1292 | 644.4538
2815.1292 | 644.8425
2816.1292 | 644.8672
2817.1292 | 644.7556
2818.1292 | 644.6364
2819.1292 | 644.4111
2820.1292 | 644.4179
2821.1292 | 644.6116
2822.1292 | 643.9534
2823.1292 | 644.3601
2824.1292 | 644.1566
2825.1292 | 644.9298
2826.1292 | 643.9
2827.1292 | 644.2852
2828.1448 | 644.5682
2829.1292 | 644.0286
2830.1292 | 644.751
2831.1292 | 644.5128
2832.1292 | 645.4476
2833.1292 | 646.0227
2834.1292 | 645.9332
2835.1292 | 646.2376
2836.1292 | 646.7271
2837.1292 | 646.1126
2838.1292 | 646.3844
2839.1292 | 646.234
2840.1448 | 645.9823
2841.1292 | 645.8241
2842.1292 | 645.9768
2843.1292 | 645.5609
2844.1292 | 645.2085
2845.1292 | 644.4219
2846.1292 | 643.9643
2847.1292 | 643.755
2848.1292 | 643.5214
2849.1292 | 642.7991
2850.1292 | 643.1177
2851.1292 | 643.4792
2852.1292 | 644.6286
2853.1292 | 644.7225
2854.1292 | 645.1296
2855.1292 | 645.4726
2856.1292 | 645.2426
2857.1292 | 645.3884
2858.1292 | 645.2866
2859.1292 | 644.7358
2860.1292 | 644.5106
2861.1292 | 644.4478
2862.1292 | 644.2011
2863.1292 | 643.89
2864.1292 | 643.7339
2865.1292 | 643.5574
2866.1292 | 644.0735
2867.1292 | 643.675
2868.1292 | 643.4671
2869.1292 | 643.5936
2870.1292 | 643.7087
2871.1292 | 644.5329
2872.1292 | 645.4489
2873.1292 | 645.5294
2874.1292 | 645.1616
2875.1292 | 645.1017
2876.1292 | 644.7523
2877.1292 | 645.005
2878.1292 | 646.005
2879.1292 | 647.4203
2880.1292 | 647.3261
2881.1292 | 647.3115
2882.1292 | 647.098
2883.1292 | 647.5833
2884.1292 | 647.7751
2885.1292 | 647.3819
2886.1292 | 647.1506
2887.1292 | 645.8395
2888.1292 | 645.7964
2889.1292 | 645.7528
2890.1292 | 646.9029
2891.1292 | 646.2865
2892.1292 | 645.3406
2893.1292 | 645.1043
2894.1292 | 645.2275
2895.1292 | 644.702
2896.1292 | 644.7761
2897.1292 | 644.4571
2898.1292 | 644.4852
2899.1292 | 644.6681
2900.1448 | 644.7015
2901.1292 | 644.7399
2902.1292 | 644.7156
2903.1292 | 644.8836
2904.1292 | 644.8204
2905.1292 | 644.5202
2906.1292 | 644.2209
2907.1292 | 643.6773
2908.1292 | 643.1475
2909.1292 | 642.78
2910.1292 | 642.3606
2911.1292 | 642.1029
2912.1292 | 641.686
2913.1292 | 642.4696
2914.1292 | 642.2481
2915.1292 | 642.2096
2916.1292 | 642.1346
2917.1292 | 642.1446
2918.1292 | 642.3297
2919.1292 | 641.8884
2920.1292 | 640.8961
2921.1292 | 641.3563
2922.1292 | 641.1233
2923.1292 | 640.9578
2924.1292 | 641.0258
2925.1292 | 642.5893
2926.1292 | 642.7631
2927.1292 | 641.7847
2928.1292 | 640.7176
2929.1292 | 638.9034
2930.1292 | 638.8292
2931.1292 | 639.5412
2932.1292 | 640.1949
2933.1292 | 640.7449
2934.1292 | 640.4673
2935.1292 | 640.9858
2936.1292 | 641.6166
2937.1292 | 641.8114
2938.1292 | 642.1097
2939.1292 | 642.3558
2940.1292 | 642.6187
2941.1292 | 641.6797
2942.1292 | 641.3317
2943.1292 | 640.9511
2944.1292 | 641.2291
2945.1292 | 641.2687
2946.1292 | 641.7087
2947.1292 | 642.3173
2948.1292 | 642.7172
2949.1292 | 644.9792
2950.1292 | 645.3814
2951.1292 | 645.3237
2952.1292 | 645.1876
2953.1292 | 645.2088
2954.1292 | 643.7823
2955.1292 | 643.9431
2956.1292 | 643.6417
2957.1292 | 643.9746
2958.1292 | 643.9406
2959.1292 | 644.9549
2960.1448 | 644.5704
2961.1292 | 644.6266
2962.1292 | 643.8453
2963.1292 | 643.1791
2964.1292 | 642.7185
2965.1292 | 642.0542
2966.1292 | 642.4909
2967.1292 | 642.3283
2968.1292 | 642.4
2969.1292 | 642.3162
2970.1292 | 642.7522
2971.1292 | 643.0727
2972.1292 | 643.8312
2973.1292 | 643.2482
2974.1292 | 642.6108
2975.1292 | 642.656
2976.1292 | 642.3006
2977.1292 | 641.3711
2978.1292 | 640.3314
2979.1292 | 640.6531
2980.1292 | 642.1282
2981.1292 | 642.5147
2982.1292 | 642.8505
2983.1292 | 642.849
2984.1292 | 643.099
2985.1292 | 643.3038
2986.1292 | 643.1266
2987.1292 | 643.3092
2988.1292 | 643.0587
2989.1292 | 643.5371
2990.1292 | 643.3541
2991.1292 | 643.2942
2992.1292 | 643.1816
2993.1292 | 642.6782
2994.1292 | 642.6105
2995.1292 | 642.1208
2996.1292 | 641.578
2997.1292 | 641.8521
2998.1292 | 643.0953
2999.1292 | 643.7306
3000.1292 | 643.6826
3001.1292 | 644.6307
3002.1292 | 645.1537
3003.1292 | 645.6111
3004.1292 | 645.4192
3005.1292 | 645.3738
3006.1292 | 645.7357
3007.1292 | 646.021
3008.1292 | 645.7889
3009.1292 | 645.2685
3010.1292 | 644.4492
3011.1292 | 643.5635
3012.1292 | 643.5202
3013.1292 | 642.9346
3014.1292 | 642.656
3015.1292 | 642.2767
3016.1292 | 641.961
3017.1292 | 640.592
3018.1292 | 640.6795
3019.1292 | 640.6349
3020.1448 | 641.0368
3021.1292 | 641.5726
3022.1292 | 641.6519
3023.1292 | 641.6393
3024.1292 | 642.0457
3025.1292 | 642.655
3026.1292 | 643.2294
3027.1292 | 642.8755
3028.1292 | 642.7809
3029.1292 | 642.3562
3030.1292 | 642.159
3031.1292 | 642.4616
3032.1292 | 643.3875
3033.1292 | 644.1832
3034.1292 | 644.6843
3035.1292 | 644.0712
3036.1292 | 643.3538
3037.1292 | 642.8593
3038.1292 | 642.8442
3039.1292 | 642.829
3040.1292 | 642.6202
3041.1292 | 642.5236
3042.1292 | 642.2985
3043.1292 | 641.9783
3044.1292 | 642.5969
3045.1292 | 645.0456
3046.1292 | 645.944
3047.1292 | 645.8016
3048.1292 | 645.1097
3049.1292 | 644.8435
3050.1292 | 644.7049
3051.1292 | 644.209
3052.1292 | 644.2349
3053.1292 | 643.6557
3054.1292 | 643.6938
3055.1292 | 643.2562
3056.1292 | 643.3978
3057.1292 | 642.3821
3058.1292 | 642.3048
3059.1292 | 642.0107
3060.1292 | 642.5072
3061.1292 | 643.2872
3062.1292 | 644.0177
3063.1292 | 644.2706
3064.1292 | 643.9948
3065.1292 | 643.4947
3066.1292 | 643.4859
3067.1292 | 644.1371
3068.1292 | 645.2955
3069.1292 | 645.7365
3070.1292 | 645.848
3071.1292 | 646.4342
3072.1292 | 646.9964
3073.1292 | 646.9185
3074.1292 | 646.3466
3075.1292 | 645.4166
3076.1292 | 645.2089
3077.1292 | 644.2439
3078.1292 | 645.5565
3079.1292 | 646.7562
3080.1292 | 648.2776
3081.1292 | 650.1954
3082.1292 | 649.0638
3083.1292 | 648.085
3084.1292 | 646.9766
3085.1292 | 647.3098
3086.1292 | 648.2656
3087.1292 | 648.4613
3088.1292 | 648.4615
3089.1292 | 648.3581
3090.1292 | 647.6186
3091.1292 | 647.6769
3092.1292 | 647.704
3093.1292 | 648.9826
3094.1292 | 649.0322
3095.1292 | 650.2157
3096.1292 | 650.2557
3097.1292 | 651.0059
3098.1292 | 651.0349
3099.1292 | 651.7387
3100.1292 | 653.4481
3101.1292 | 654.3201
3102.1292 | 653.273
3103.1292 | 652.233
3104.1292 | 651.4013
3105.1292 | 651.2187
3106.1292 | 651.2854
3107.1292 | 650.4358
3108.1292 | 650.128
3109.1292 | 650.1374
3110.1292 | 650.5181
3111.1292 | 650.9093
3112.1292 | 651.8918
3113.1292 | 652.3295
3114.1292 | 652.8219
3115.1292 | 652.2117
3116.1292 | 651.3506
3117.1292 | 651.7664
3118.1292 | 652.81
3119.1292 | 652.1862
3120.1292 | 651.3986
3121.1292 | 651.3284
3122.1292 | 650.3829
3123.1292 | 649.6323
3124.1292 | 649.5073
3125.1292 | 648.2795
3126.1292 | 648.7857
3127.1292 | 648.5399
3128.1292 | 649.3332
3129.1292 | 649.6568
3130.1292 | 649.2949
3131.1292 | 648.9493
3132.1292 | 649.2909
3133.1292 | 649.3428
3134.1292 | 649.6107
3135.1292 | 649.338
3136.1292 | 648.8428
3137.1292 | 648.7838
3138.1292 | 648.654
3139.1292 | 648.507
3140.1292 | 648.2006
3141.1292 | 647.3119
3142.1292 | 648.3614
3143.1292 | 648.6553
3144.1292 | 648.9725
3145.1292 | 649.3128
3146.1292 | 648.5735
3147.1292 | 648.3391
3148.1292 | 647.7793
3149.1292 | 648.3328
3150.1292 | 647.5625
3151.1292 | 647.4407
3152.1292 | 647.0181
3153.1292 | 647.2705
3154.1292 | 646.9838
3155.1292 | 646.4531
3156.1292 | 646.3979
3157.1292 | 646.2295
3158.1292 | 645.6169
3159.1292 | 645.387
3160.1292 | 644.3892
3161.1292 | 644.9524
3162.1292 | 645.6778
3163.1292 | 646.0837
3164.1292 | 645.6712
3165.1292 | 645.5498
3166.1292 | 645.0486
3167.1292 | 644.9993
3168.1292 | 643.9888
3169.1292 | 643.8556
3170.1292 | 643.5335
3171.1292 | 643.1326
3172.1292 | 642.4804
3173.1292 | 642.2957
3174.1292 | 642.4315
3175.1292 | 643.1858
3176.1292 | 643.8539
3177.1292 | 644.1678
3178.1292 | 645.0298
3179.1292 | 644.9814
3180.1292 | 644.4277
3181.1292 | 644.4291
3182.1292 | 644.1822
3183.1448 | 645.2813
3184.1292 | 645.596
3185.1292 | 645.3433
3186.1292 | 645.044
3187.1292 | 645.4153
3188.1292 | 645.974
3189.1448 | 645.6281
3190.1292 | 645.3024
3191.1292 | 644.7494
3192.1292 | 644.2353
3193.1292 | 644.0321
3194.1292 | 643.7166
3195.1292 | 643.8048
3196.1292 | 644.0543
3197.1292 | 644.4736
3198.1292 | 645.0591
3199.1292 | 644.7989
3200.1448 | 645.454
3201.1292 | 645.267
3202.1292 | 644.5306
3203.1292 | 644.5797
3204.1292 | 644.5218
3205.1292 | 645.0286
3206.1292 | 645.521
3207.1292 | 644.7851
3208.1292 | 643.8803
3209.1292 | 643.282
3210.1292 | 643.2036
3211.1292 | 643.643
3212.1292 | 644.3186
3213.1292 | 645.0752
3214.1292 | 645.1806
3215.1292 | 645.0237
3216.1292 | 644.3032
3217.1292 | 644.1982
3218.1292 | 643.5229
3219.1292 | 643.3222
3220.1292 | 642.8446
3221.1292 | 642.236
3222.1292 | 642.6419
3223.1292 | 642.4525
3224.1292 | 642.6276
3225.1292 | 642.9668
3226.1292 | 642.9919
3227.1292 | 643.0194
3228.1292 | 642.2795
3229.1292 | 641.386
3230.1292 | 641.4135
3231.1292 | 641.5585
3232.1292 | 641.8227
3233.1292 | 641.5484
3234.1292 | 641.1543
3235.1292 | 640.4387
3236.1292 | 639.7328
3237.1292 | 639.6858
3238.1292 | 639.3317
3239.1292 | 639.1572
3240.1292 | 638.718
3241.1292 | 638.0962
3242.1292 | 638.5304
3243.1292 | 638.4952
3244.1292 | 638.0305
3245.1292 | 638.0252
3246.1292 | 638.4597
3247.1292 | 638.2949
3248.1292 | 637.8029
3249.1292 | 637.4616
3250.1292 | 637.2835
3251.1292 | 637.5946
3252.1292 | 637.5808
3253.1292 | 637.4739
3254.1292 | 637.547
3255.1292 | 637.4195
3256.1292 | 637.5389
3257.1292 | 637.6072
3258.1292 | 638.017
3259.1292 | 637.8018
3260.1292 | 637.8871
3261.1292 | 637.537
3262.1292 | 637.6062
3263.1292 | 637.8432
3264.1292 | 637.7967
3265.1292 | 638.2696
3266.1292 | 639.4853
3267.1292 | 640.1707
3268.1292 | 640.2888
3269.1292 | 640.3559
3270.1292 | 640.2285
3271.1292 | 640.0785
3272.1292 | 640.2615
3273.1292 | 640.2728
3274.1292 | 640.0317
3275.1292 | 640.4171
3276.1292 | 640.8159
3277.1292 | 640.9585
3278.1292 | 641.0441
3279.1292 | 640.8653
3280.1292 | 641.1713
3281.1292 | 640.7604
3282.1292 | 640.6031
3283.1292 | 640.1828
3284.1292 | 639.941
3285.1292 | 639.5766
3286.1292 | 639.1774
3287.1292 | 638.2489
3288.1292 | 637.7162
3289.1292 | 636.943
3290.1292 | 636.6516
3291.1292 | 635.8659
3292.1292 | 636.8099
3293.1292 | 637.0979
3294.1292 | 637.4069
3295.1292 | 637.5959
3296.1292 | 637.7999
3297.1292 | 637.8192
3298.1292 | 638.4355
3299.1292 | 638.8607
3300.1292 | 638.5233
3301.1292 | 637.8092
3302.1292 | 637.3298
3303.1292 | 637.5976
3304.1292 | 637.4808
3305.1292 | 636.7377
3306.1292 | 636.5144
3307.1292 | 635.9879
3308.1292 | 635.9676
3309.1292 | 635.9857
3310.1292 | 636.7859
3311.1292 | 636.7972
3312.1292 | 637.9924
3313.1292 | 638.5536
3314.1292 | 638.1916
3315.1292 | 638.7115
3316.1292 | 638.911
3317.1292 | 639.3514
3318.1292 | 639.1334
3319.1292 | 639.5584
3320.1292 | 638.9389
3321.1292 | 638.9136
3322.1292 | 639.4772
3323.1292 | 640.4359
3324.1292 | 640.8898
3325.1292 | 640.8586
3326.1292 | 640.4847
3327.1292 | 639.9009
3328.1292 | 639.4778
3329.1292 | 638.5208
3330.1292 | 637.9297
3331.1292 | 638.1853
3332.1292 | 638.4375
3333.1292 | 639.0854
3334.1292 | 639.3268
3335.1292 | 639.7335
3336.1292 | 639.4096
3337.1292 | 639.2807
3338.1292 | 638.76
3339.1292 | 638.6606
3340.1292 | 638.6928
3341.1292 | 638.9313
3342.1292 | 638.7641
3343.1292 | 638.3585
3344.1292 | 637.756
3345.1292 | 636.9835
3346.1292 | 636.3418
3347.1292 | 635.1426
3348.1292 | 634.3938
3349.1292 | 634.4022
3350.1292 | 633.4947
3351.1292 | 634.1989
3352.1292 | 634.7887
3353.1292 | 635.2036
3354.1292 | 634.718
3355.1292 | 634.4739
3356.1292 | 634.3394
3357.1292 | 633.9186
3358.1448 | 633.3139
3359.1292 | 634.4048
3360.1292 | 634.3762
3361.1292 | 634.2853
3362.1292 | 634.0078
3363.1292 | 633.9456
3364.1292 | 634.7877
3365.1292 | 634.684
3366.1292 | 634.5183
3367.1292 | 635.2685
3368.1292 | 635.6796
3369.1292 | 635.9264
3370.1292 | 636.2492
3371.1292 | 636.9871
3372.1292 | 637.0726
3373.1292 | 637.3536
3374.1292 | 637.3381
3375.1292 | 638.585
3376.1292 | 639.4762
3377.1292 | 641.3529
3378.1292 | 642.8828
3379.1292 | 643.535
3380.1448 | 644.5064
3381.1292 | 643.6349
3382.1292 | 643.4794
3383.1292 | 642.9042
3384.1292 | 641.8927
3385.1292 | 642.4362
3386.1292 | 641.9468
3387.1292 | 641.1384
3388.1448 | 641.246
3389.1292 | 639.5721
3390.1292 | 639.4427
3391.1292 | 639.1635
3392.1292 | 639.2823
3393.1292 | 638.8771
3394.1292 | 638.5416
3395.1292 | 637.744
3396.1292 | 636.8898
3397.1292 | 637.1139
3398.1292 | 636.3621
3399.1292 | 636.2034
3400.1292 | 636.1497
3401.1292 | 635.6619
3402.1292 | 634.8287
3403.1292 | 634.4463
3404.1292 | 634.1402
3405.1292 | 634.5548
3406.1292 | 633.9836
3407.1292 | 633.6314
3408.1292 | 632.8587
3409.1292 | 632.9461
3410.1292 | 633.1367
3411.1292 | 632.6565
3412.1292 | 632.296
3413.1292 | 632.0115
3414.1292 | 632.357
3415.1292 | 632.6653
3416.1292 | 634.3236
3417.1292 | 635.296
3418.1292 | 635.1102
3419.1292 | 635.6131
3420.1292 | 635.7043
3421.1292 | 635.8729
3422.1292 | 635.8964
3423.1292 | 637.4627
3424.1292 | 638.3352
3425.1292 | 638.5959
3426.1292 | 638.3947
3427.1292 | 638.2184
3428.1292 | 638.7202
3429.1292 | 638.4208
3430.1292 | 637.4918
3431.1292 | 636.4434
3432.1292 | 637.1523
3433.1292 | 637.8889
3434.1292 | 638.7233
3435.1292 | 638.0053
3436.1292 | 637.7998
3437.1292 | 637.4928
3438.1292 | 637.2188
3439.1292 | 636.6042
3440.1448 | 635.9305
3441.1292 | 636.1258
3442.1292 | 635.5075
3443.1292 | 634.6713
3444.1292 | 634.7301
3445.1292 | 634.4854
3446.1292 | 635.0522
3447.1292 | 635.1959
3448.1292 | 634.9051
3449.1292 | 634.9958
3450.1292 | 635.9882
3451.1292 | 637.4884
3452.1292 | 638.3773
3453.1292 | 638.714
3454.1292 | 638.6888
3455.1292 | 638.3741
3456.1292 | 637.7117
3457.1292 | 636.9425
3458.1292 | 636.9807
3459.1292 | 637.6563
3460.1292 | 637.2951
3461.1292 | 637.3201
3462.1292 | 636.6874
3463.1292 | 636.206
3464.1292 | 635.323
3465.1292 | 636.1798
3466.1292 | 636.6159
3467.1292 | 637.9196
3468.1292 | 638.0365
3469.1292 | 638.896
3470.1292 | 638.8665
3471.1292 | 640.0989
3472.1292 | 641.1024
3473.1292 | 641.2259
3474.1292 | 642.027
3475.1292 | 641.7766
3476.1292 | 642.4623
3477.1292 | 641.1787
3478.1448 | 640.5301
3479.1292 | 640.2509
3480.1292 | 641.1959
3481.1292 | 640.8801
3482.1292 | 639.832
3483.1292 | 639.2956
3484.1292 | 638.2438
3485.1292 | 637.4849
3486.1292 | 637.6038
3487.1292 | 637.4287
3488.1292 | 636.4319
3489.1292 | 635.8502
3490.1292 | 635.9917
3491.1292 | 635.722
3492.1292 | 635.2108
3493.1292 | 635.7894
3494.1292 | 635.2435
3495.1292 | 635.1012
3496.1292 | 634.6636
3497.1292 | 634.7945
3498.1292 | 634.5154
3499.1292 | 634.66
3500.1448 | 634.6531
3501.1292 | 634.9844
3502.1292 | 634.9928
3503.1292 | 634.3013
3504.1292 | 633.4551
3505.1292 | 633.3191
3506.1292 | 633.159
3507.1292 | 633.6376
3508.1448 | 633.5067
3509.1292 | 633.386
3510.1292 | 633.4565
3511.1292 | 633.9958
3512.1292 | 633.7959
3513.1292 | 633.9868
3514.1292 | 634.4593
3515.1292 | 635.511
3516.1292 | 636.1147
3517.1292 | 635.8811
3518.1292 | 635.8655
3519.1292 | 635.8591
3520.1292 | 635.3717
3521.1292 | 635.0994
3522.1292 | 635.4762
3523.1292 | 636.1219
3524.1292 | 637.5627
3525.1292 | 636.9579
3526.1292 | 637.2625
3527.1292 | 635.8949
3528.1292 | 636.1686
3529.1292 | 636.9505
3530.1292 | 636.9222
3531.1292 | 636.8978
3532.1292 | 637.497
3533.1292 | 637.609
3534.1292 | 637.2417
3535.1292 | 636.908
3536.1292 | 636.767
3537.1292 | 636.4032
3538.1292 | 636.8233
3539.1292 | 636.6487
3540.1292 | 636.8228
3541.1292 | 636.7288
3542.1292 | 636.8982
3543.1292 | 636.6833
3544.1292 | 637.1071
3545.1292 | 637.1823
3546.1292 | 636.9748
3547.1292 | 637.2434
3548.1292 | 637.5012
3549.1292 | 637.521
3550.1292 | 637.6306
3551.1292 | 638.7897
3552.1292 | 638.8614
3553.1292 | 638.5435
3554.1292 | 638.5568
3555.1292 | 638.6923
3556.1292 | 639.221
3557.1292 | 640.5581
3558.1292 | 640.1815
3559.1292 | 639.5972
3560.1448 | 637.9606
3561.1292 | 639.3376
3562.1292 | 638.2325
3563.1292 | 638.3129
3564.1292 | 638.5809
3565.1292 | 637.6943
3566.1292 | 636.0915
3567.1292 | 635.4495
3568.1292 | 635.7658
3569.1292 | 635.0916
3570.1292 | 635.4411
3571.1292 | 636.0799
3572.1292 | 636.7297
3573.1292 | 636.9075
3574.1292 | 637.6378
3575.1292 | 637.4214
3576.1292 | 636.8915
3577.1448 | 636.7951
3578.1292 | 637.2287
3579.1292 | 636.9154
3580.1292 | 636.5522
3581.1292 | 636.3625
3582.1292 | 636.5351
3583.1292 | 636.0746
3584.1292 | 636.1568
3585.1292 | 636.4017
3586.1292 | 636.9059
3587.1292 | 637.1545
3588.1292 | 637.1844
3589.1292 | 636.8033
3590.1292 | 636.8985
3591.1292 | 637.1505
3592.1292 | 636.9387
3593.1292 | 637.9638
3594.1292 | 638.3223
3595.1292 | 637.3682
3596.1292 | 636.7404
3597.1292 | 636.5004
3598.1292 | 636.9979
3599.1292 | 637.2754
3600.1292 | 639.4518
3601.1292 | 639.8842
3602.1292 | 640.4486
3603.1292 | 640.4681
3604.1292 | 639.9164
3605.1292 | 640.41
3606.1292 | 639.7802
3607.1292 | 638.9881
3608.1292 | 639.0657
3609.1292 | 638.8654
3610.1292 | 638.0954
3611.1292 | 638.3224
3612.1292 | 637.6302
3613.1292 | 636.6568
3614.1292 | 636.3464
3615.1292 | 636.7055
3616.1292 | 637.2106
3617.1292 | 637.6717
3618.1292 | 637.9791
3619.1292 | 637.1772
3620.1292 | 637.9045
3621.1292 | 638.4181
3622.1292 | 638.1854
3623.1292 | 636.8205
3624.1292 | 636.4374
3625.1292 | 637.3501
3626.1292 | 638.2769
3627.1292 | 638.2593
3628.1292 | 637.4976
3629.1292 | 636.8851
3630.1292 | 637.6153
3631.1292 | 637.4
3632.1292 | 637.2918
3633.1292 | 637.5222
3634.1292 | 637.497
3635.1292 | 637.3484
3636.1292 | 637.0327
3637.1292 | 636.7564
3638.1292 | 637.534
3639.1292 | 638.1571
3640.1292 | 638.1074
3641.1292 | 637.7899
3642.1292 | 638.3115
3643.1292 | 639.1331
3644.1292 | 639.0131
3645.1292 | 639.0774
3646.1292 | 638.0351
3647.1292 | 638.0594
3648.1292 | 637.9146
3649.1292 | 637.9357
3650.1292 | 637.2729
3651.1292 | 637.1491
3652.1292 | 637.4699
3653.1292 | 638.3222
3654.1292 | 638.1554
3655.1292 | 638.1189
3656.1292 | 637.9091
3657.1292 | 636.9682
3658.1448 | 636.7749
3659.1292 | 636.5994
3660.1292 | 636.6073
3661.1292 | 635.8857
3662.1292 | 635.8787
3663.1292 | 635.884
3664.1292 | 636.1657
3665.1292 | 636.3351
3666.1292 | 636.0674
3667.1292 | 635.5867
3668.1292 | 635.3333
3669.1292 | 635.6435
3670.1292 | 636.3992
3671.1292 | 636.2797
3672.1292 | 635.9595
3673.1292 | 635.3308
3674.1292 | 635.1906
3675.1292 | 635.7885
3676.1292 | 636.0267
3677.1292 | 636.6771
3678.1292 | 636.8381
3679.1292 | 637.2591
3680.1292 | 637.0236
3681.1292 | 636.9067
3682.1292 | 637.8737
3683.1292 | 637.6481
3684.1292 | 636.1823
3685.1292 | 635.9259
3686.1292 | 635.9764
3687.1292 | 636.1385
3688.1292 | 635.9592
3689.1292 | 636.0441
3690.1292 | 636.5795
3691.1292 | 636.8566
3692.1292 | 636.6943
3693.1292 | 636.3522
3694.1292 | 635.1793
3695.1292 | 634.8033
3696.1292 | 634.7453
3697.1292 | 634.4096
3698.1292 | 635.3026
3699.1292 | 636.3722
3700.1292 | 636.3569
3701.1292 | 636.0117
3702.1292 | 635.8577
3703.1292 | 636.2922
3704.1292 | 635.7232
3705.1292 | 635.6827
3706.1292 | 635.796
3707.1292 | 635.2596
3708.1292 | 635.0762
3709.1292 | 634.714
3710.1292 | 633.7965
3711.1292 | 633.8778
3712.1292 | 634.0544
3713.1292 | 633.9776
3714.1292 | 634.4645
3715.1292 | 634.1721
3716.1292 | 633.996
3717.1292 | 634.484
3718.1292 | 634.4126
3719.1292 | 634.5661
3720.1292 | 635.2361
3721.1292 | 635.9168
3722.1292 | 637.9854
3723.1292 | 638.6647
3724.1292 | 637.964
3725.1292 | 637.3486
3726.1292 | 637.0157
3727.1292 | 636.749
3728.1292 | 635.8883
3729.1292 | 635.2106
3730.1292 | 635.4836
3731.1292 | 635.9253
3732.1292 | 635.7035
3733.1292 | 635.3844
3734.1292 | 636.0134
3735.1292 | 635.5445
3736.1292 | 636.0681
3737.1292 | 636.5754
3738.1292 | 636.6905
3739.1292 | 636.4138
3740.1292 | 636.2464
3741.1292 | 636.5005
3742.1292 | 636.1802
3743.1292 | 635.3359
3744.1292 | 635.4386
3745.1448 | 635.203
3746.1292 | 635.3119
3747.1292 | 634.0474
3748.1292 | 633.8398
3749.1292 | 634.2651
3750.1292 | 634.3316
3751.1292 | 635.2859
3752.1292 | 636.1016
3753.1292 | 636.2974
3754.1292 | 635.923
3755.1292 | 635.8858
3756.1292 | 635.468
3757.1292 | 635.4948
3758.1292 | 635.8511
3759.1292 | 634.7016
3760.1292 | 634.2503
3761.1292 | 634.7029
3762.1292 | 636.0381
3763.1292 | 637.0087
3764.1292 | 637.2282
3765.1292 | 638.3912
3766.1292 | 639.0227
3767.1292 | 637.6674
3768.1292 | 638.222
3769.1448 | 638.0396
3770.1292 | 638.028
3771.1448 | 637.8074
3772.1292 | 637.5993
3773.1292 | 637.4186
3774.1292 | 637.043
3775.1292 | 635.8082
3776.1292 | 635.4052
3777.1292 | 635.4566
3778.1292 | 635.4933
3779.1292 | 635.1383
3780.1292 | 635.7889
3781.1292 | 634.5983
3782.1292 | 634.02
3783.1292 | 633.5846
3784.1292 | 633.9569
3785.1292 | 634.7155
3786.1292 | 634.2956
3787.1292 | 633.7527
3788.1292 | 633.506
3789.1292 | 633.7473
3790.1292 | 634.8103
3791.1292 | 636.0596
3792.1292 | 636.9502
3793.1292 | 638.8105
3794.1292 | 639.8966
3795.1292 | 638.9759
3796.1292 | 640.2849
3797.1292 | 639.7118
3798.1292 | 638.7868
3799.1292 | 638.1204
3800.1292 | 638.1621
3801.1292 | 638.0355
3802.1292 | 637.4687
3803.1292 | 637.4657
3804.1292 | 637.1302
3805.1292 | 637.7388
3806.1292 | 639.6832
3807.1292 | 640.8249
3808.1292 | 640.2697
3809.1292 | 641.1415
3810.1292 | 642.7421
3811.1292 | 642.3379
3812.1292 | 642.2627
3813.1292 | 643.9479
3814.1292 | 645.3012
3815.1292 | 645.1404
3816.1292 | 644.9937
3817.1292 | 644.0849
3818.1292 | 643.2792
3819.1292 | 643.0411
3820.1292 | 642.0312
3821.1292 | 641.9058
3822.1292 | 641.5151
3823.1292 | 640.1788
3824.1292 | 639.2133
3825.1292 | 638.2531
3826.1292 | 637.3175
3827.1292 | 636.2108
3828.1292 | 636.7068
3829.1292 | 637.4097
3830.1292 | 637.5664
3831.1292 | 637.8269
3832.1292 | 637.5934
3833.1292 | 637.0902
3834.1292 | 637.3482
3835.1292 | 637.259
3836.1292 | 637.1925
3837.1292 | 636.5871
3838.1292 | 635.4913
3839.1292 | 634.3953
3840.1292 | 634.2979
3841.1292 | 634.1867
3842.1292 | 634.4285
3843.1292 | 634.6376
3844.1292 | 634.9905
3845.1292 | 634.9902
3846.1292 | 634.4046
3847.1292 | 634.8039
3848.1292 | 634.5286
3849.1292 | 635.5825
3850.1292 | 635.2144
3851.1292 | 635.2937
3852.1292 | 634.0382
3853.1292 | 633.7438
3854.1292 | 634.1603
3855.1292 | 634.3367
3856.1292 | 633.8499
3857.1292 | 633.7076
3858.1292 | 634.6901
3859.1292 | 634.1429
3860.1292 | 635.3967
3861.1292 | 635.9951
3862.1292 | 635.5343
3863.1292 | 634.8122
3864.1292 | 635.5509
3865.1292 | 634.9329
3866.1292 | 634.3612
3867.1292 | 634.1734
3868.1292 | 633.5269
3869.1292 | 633.5309
3870.1292 | 634.8769
3871.1292 | 635.5795
3872.1292 | 634.7817
3873.1292 | 634.6667
3874.1292 | 634.2272
3875.1292 | 633.2937
3876.1292 | 632.4887
3877.1292 | 632.1567
3878.1292 | 631.9487
3879.1292 | 632.4387
3880.1292 | 632.2587
3881.1292 | 632.0239
3882.1292 | 631.5977
3883.1292 | 631.7894
3884.1292 | 632.4915
3885.1292 | 632.1782
3886.1292 | 632.1624
3887.1292 | 632.3392
3888.1292 | 632.2323
3889.1292 | 632.1677
3890.1292 | 633.0667
3891.1292 | 632.335
3892.1292 | 632.9819
3893.1292 | 632.7617
3894.1292 | 631.9556
3895.1292 | 632.2334
3896.1292 | 632.8704
3897.1292 | 633.4068
3898.1292 | 632.7217
3899.1292 | 632.2101
3900.1292 | 632.5754
3901.1292 | 632.2206
3902.1292 | 632.9294
3903.1292 | 633.3364
3904.1292 | 633.9355
3905.1292 | 634.4886
3906.1292 | 634.4621
3907.1292 | 634.2149
3908.1292 | 633.9855
3909.1292 | 634.835
3910.1292 | 635.8301
3911.1292 | 636.1056
3912.1292 | 636.5263
3913.1292 | 636.4902
3914.1292 | 636.2732
3915.1292 | 635.4951
3916.1292 | 635.7159
3917.1292 | 636.3214
3918.1292 | 635.9441
3919.1292 | 636.5868
3920.1292 | 636.7341
3921.1292 | 636.8815
3922.1292 | 635.996
3923.1292 | 635.9226
3924.1292 | 635.9693
3925.1292 | 635.7383
3926.1292 | 636.4127
3927.1292 | 636.6765
3928.1292 | 635.7217
3929.1292 | 635.2922
3930.1292 | 635.4227
3931.1292 | 635.7036
3932.1292 | 635.8785
3933.1292 | 635.5276
3934.1292 | 634.8982
3935.1292 | 634.9652
3936.1292 | 634.49
3937.1292 | 634.3387
3938.1292 | 634.1274
3939.1292 | 634.3193
3940.1292 | 634.6342
3941.1292 | 634.0104
3942.1292 | 634.2234
3943.1292 | 634.4775
3944.1292 | 634.3094
3945.1292 | 634.9422
3946.1292 | 635.466
3947.1292 | 634.4767
3948.1292 | 634.1273
3949.1292 | 634.3675
3950.1292 | 634.553
3951.1292 | 635.5926
3952.1292 | 635.263
3953.1292 | 635.3633
3954.1292 | 635.2233
3955.1292 | 635.0496
3956.1292 | 634.9802
3957.1292 | 634.2279
3958.1292 | 634.2278
3959.1292 | 633.8022
3960.1292 | 634.476
3961.1292 | 633.3604
3962.1292 | 632.8433
3963.1292 | 632.3214
3964.1292 | 631.5573
3965.1292 | 629.6425
3966.1292 | 629.5547
3967.1292 | 629.5835
3968.1292 | 629.3555
3969.1292 | 628.9555
3970.1292 | 630.137
3971.1292 | 629.8404
3972.1292 | 629.5136
3973.1292 | 630.1066
3974.1292 | 630.3395
3975.1292 | 630.87
3976.1292 | 631.6442
3977.1292 | 631.8449
3978.1292 | 632.2534
3979.1292 | 632.3303
3980.1292 | 631.3942
3981.1292 | 630.8529
3982.1292 | 630.4362
3983.1292 | 630.5196
3984.1448 | 629.9876
3985.1292 | 629.8453
3986.1292 | 629.6131
3987.1292 | 629.8148
3988.1292 | 629.9766
3989.1292 | 629.4764
3990.1292 | 628.8583
3991.1292 | 627.4836
3992.1292 | 626.6982
3993.1292 | 626.9057
3994.1292 | 627.2434
3995.1292 | 628.7188
3996.1292 | 629.7155
3997.1292 | 630.7013
3998.1292 | 630.8511
3999.1292 | 631.2304
4000.1292 | 631.2723
4001.1292 | 631.8373
4002.1292 | 630.65
4003.1292 | 630.0352
4004.1292 | 630.3733
4005.1292 | 630.0612
4006.1292 | 630.5384
4007.1292 | 631.4154
4008.1292 | 632.0631
4009.1292 | 633.269
4010.1292 | 633.3059
4011.1292 | 633.4382
4012.1292 | 633.4593
4013.1292 | 633.3818
4014.1292 | 633.4287
4015.1292 | 633.3209
4016.1292 | 632.2602
4017.1292 | 632.3375
4018.1292 | 632.82
4019.1292 | 633.3477
4020.1292 | 633.7445
4021.1292 | 633.1924
4022.1292 | 632.6104
4023.1292 | 632.4446
4024.1292 | 632.1069
4025.1292 | 632.0427
4026.1292 | 631.9339
4027.1292 | 631.9799
4028.1292 | 631.838
4029.1292 | 631.5385
4030.1292 | 632.3109
4031.1292 | 631.8154
4032.1292 | 631.3358
4033.1292 | 630.5221
4034.1292 | 630.2785
4035.1292 | 629.9916
4036.1292 | 630.0864
4037.1292 | 630.6385
4038.1292 | 630.7905
4039.1292 | 631.1779
4040.1292 | 630.8344
4041.1292 | 630.9764
4042.1292 | 631.6193
4043.1292 | 631.9521
4044.1292 | 631.9989
4045.1292 | 631.8382
4046.1292 | 632.1189
4047.1292 | 630.7135
4048.1292 | 630.2832
4049.1292 | 629.7409
4050.1292 | 629.4187
4051.1292 | 629.9141
4052.1292 | 629.4257
4053.1292 | 629.1832
4054.1292 | 628.6258
4055.1292 | 629.142
4056.1292 | 628.7154
4057.1292 | 628.7225
4058.1292 | 628.8959
4059.1292 | 628.3381
4060.1292 | 628.5961
4061.1292 | 629.0151
4062.1292 | 628.9177
4063.1292 | 628.8346
4064.1292 | 629.1634
4065.1292 | 628.4864
4066.1292 | 628.4894
4067.1292 | 628.7174
4068.1292 | 628.8598
4069.1292 | 629.6033
4070.1292 | 630.1186
4071.1292 | 629.9958
4072.1292 | 630.0954
4073.1292 | 629.3067
4074.1292 | 628.6275
4075.1292 | 628.2402
4076.1292 | 627.9648
4077.1292 | 627.7035
4078.1292 | 627.6237
4079.1292 | 628.1679
4080.1292 | 628.5888
4081.1292 | 628.3113
4082.1292 | 627.6987
4083.1292 | 628.3336
4084.1292 | 629.5737
4085.1292 | 630.2559
4086.1292 | 629.7634
4087.1292 | 629.6864
4088.1292 | 628.9475
4089.1292 | 628.9505
4090.1292 | 629.3853
4091.1292 | 628.6559
4092.1292 | 628.3138
4093.1292 | 628.6048
4094.1292 | 628.428
4095.1292 | 628.8119
4096.1292 | 628.9707
4097.1292 | 629.0729
4098.1292 | 629.8701
4099.1292 | 628.7582
4100.1292 | 628.8292
4101.1292 | 628.5284
4102.1292 | 629.5972
4103.1292 | 631.6562
4104.1292 | 632.5384
4105.1292 | 632.3612
4106.1292 | 632.1968
4107.1292 | 632.9319
4108.1292 | 632.9432
4109.1292 | 633.3605
4110.1292 | 634.0429
4111.1292 | 633.7918
4112.1292 | 633.8108
4113.1292 | 633.9933
4114.1292 | 634.0283
4115.1292 | 633.8139
4116.1292 | 633.5997
4117.1292 | 633.5651
4118.1292 | 634.6948
4119.1292 | 635.7475
4120.1292 | 636.1047
4121.1292 | 635.4312
4122.1292 | 635.4167
4123.1292 | 635.015
4124.1292 | 636.9822
4125.1292 | 637.4391
4126.1292 | 636.7903
4127.1292 | 636.3044
4128.1292 | 636.2801
4129.1292 | 636.5732
4130.1292 | 636.518
4131.1292 | 635.9367
4132.1292 | 636.3484
4133.1292 | 638.2068
4134.1292 | 640.1183
4135.1292 | 638.3004
4136.1292 | 638.4507
4137.1292 | 637.6634
4138.1292 | 637.175
4139.1292 | 637.5238
4140.1292 | 637.9358
4141.1292 | 637.8701
4142.1292 | 637.3814
4143.1292 | 636.5588
4144.1292 | 636.7173
4145.1292 | 636.6856
4146.1292 | 636.4281
4147.1292 | 636.9467
4148.1292 | 637.6125
4149.1292 | 637.7677
4150.1292 | 637.7947
4151.1292 | 638.1547
4152.1292 | 638.6137
4153.1292 | 638.7399
4154.1292 | 638.2579
4155.1292 | 637.326
4156.1292 | 637.9628
4157.1292 | 638.4431
4158.1292 | 637.7024
4159.1292 | 637.3235
4160.1292 | 637.2496
4161.1292 | 636.9873
4162.1292 | 638.3008
4163.1292 | 638.9529
4164.1448 | 638.5283
4165.1292 | 637.8552
4166.1292 | 636.9082
4167.1292 | 636.6952
4168.1292 | 636.5707
4169.1292 | 636.4379
4170.1292 | 635.4751
4171.1292 | 635.5175
4172.1292 | 636.5874
4173.1292 | 636.8792
4174.1292 | 636.4858
4175.1292 | 636.1602
4176.1292 | 636.3265
4177.1292 | 635.9539
4178.1292 | 635.2684
4179.1292 | 634.9401
4180.1292 | 635.3444
4181.1292 | 635.4435
4182.1292 | 635.3862
4183.1292 | 634.9564
4184.1292 | 634.3945
4185.1292 | 633.5747
4186.1292 | 632.7248
4187.1292 | 632.3457
4188.1292 | 632.1751
4189.1292 | 632.0074
4190.1292 | 632.8162
4191.1292 | 632.9197
4192.1292 | 633.1602
4193.1292 | 634.1667
4194.1292 | 634.4309
4195.1292 | 634.4705
4196.1292 | 634.3723
4197.1292 | 633.7265
4198.1292 | 636.4725
4199.1292 | 635.9717
4200.1292 | 635.2002
4201.1292 | 634.8593
4202.1292 | 634.9159
4203.1292 | 635.2304
4204.1292 | 636.3341
4205.1292 | 637.4041
4206.1292 | 637.8018
4207.1292 | 636.246
4208.1292 | 635.7725
4209.1292 | 636.4946
4210.1292 | 636.5614
4211.1292 | 636.4313
4212.1292 | 635.7408
4213.1292 | 635.577
4214.1292 | 635.5828
4215.1292 | 636.9277
4216.1292 | 636.7328
4217.1292 | 637.5994
4218.1292 | 640.1302
4219.1292 | 641.2208
4220.1292 | 639.6083
4221.1292 | 639.5117
4222.1292 | 638.7694
4223.1292 | 638.0422
4224.1292 | 638.3818
4225.1292 | 639.912
4226.1292 | 638.1503
4227.1292 | 637.9044
4228.1292 | 638.3523
4229.1292 | 638.0442
4230.1292 | 637.9897
4231.1292 | 638.2296
4232.1292 | 639.2472
4233.1292 | 640.5678
4234.1292 | 641.7546
4235.1292 | 640.8903
4236.1292 | 640.3095
4237.1292 | 640.6293
4238.1292 | 639.7351
4239.1292 | 638.8421
4240.1292 | 638.1881
4241.1292 | 638.0234
4242.1292 | 637.2732
4243.1292 | 635.7886
4244.1292 | 634.6114
4245.1292 | 634.638
4246.1292 | 634.7758
4247.1292 | 635.9645
4248.1292 | 635.9383
4249.1292 | 637.9212
4250.1292 | 638.5493
4251.1292 | 639.6172
4252.1292 | 639.5503
4253.1292 | 641.3802
4254.1292 | 644.0682
4255.1292 | 644.2358
4256.1292 | 644.8388
4257.1292 | 644.8785
4258.1292 | 643.8819
4259.1292 | 643.9727
4260.1292 | 643.5181
4261.1292 | 643.0465
4262.1292 | 641.6915
4263.1292 | 641.3557
4264.1292 | 639.7155
4265.1292 | 638.7606
4266.1292 | 638.19
4267.1292 | 636.6592
4268.1292 | 635.7773
4269.1292 | 635.5147
4270.1292 | 635.4395
4271.1292 | 635.1138
4272.1292 | 635.8362
4273.1292 | 636.4016
4274.1292 | 635.9051
4275.1292 | 635.2949
4276.1292 | 634.206
4277.1292 | 633.8162
4278.1292 | 633.7115
4279.1292 | 633.1211
4280.1292 | 632.3264
4281.1292 | 631.8383
4282.1292 | 632.5621
4283.1292 | 632.3341
4284.1292 | 633.3257
4285.1292 | 634.0938
4286.1292 | 634.2166
4287.1292 | 635.4844
4288.1292 | 635.5643
4289.1292 | 634.8266
4290.1292 | 632.5512
4291.1292 | 631.3444
4292.1292 | 631.7004
4293.1292 | 631.9926
4294.1292 | 632.1257
4295.1292 | 632.3506
4296.1292 | 631.814
4297.1292 | 631.9462
4298.1292 | 631.8975
4299.1292 | 632.0927
4300.1292 | 632.795
4301.1292 | 632.7262
4302.1292 | 633.1058
4303.1292 | 633.7231
4304.1292 | 633.9799
4305.1292 | 634.0948
4306.1292 | 634.4091
4307.1292 | 633.8138
4308.1292 | 634.2623
4309.1292 | 633.6032
4310.1292 | 632.5022
4311.1292 | 632.3407
4312.1292 | 632.054
4313.1292 | 632.5222
4314.1292 | 632.7679
4315.1292 | 632.6866
4316.1292 | 632.3975
4317.1292 | 634.6417
4318.1292 | 636.1066
4319.1292 | 636.2872
4320.1292 | 636.0991
4321.1292 | 635.7051
4322.1292 | 635.2065
4323.1292 | 635.9085
4324.1292 | 635.8686
4325.1292 | 635.7462
4326.1292 | 634.8047
4327.1292 | 633.6315
4328.1292 | 632.0333
4329.1292 | 630.9825
4330.1292 | 630.459
4331.1292 | 630.5167
4332.1292 | 630.4418
4333.1292 | 631.1732
4334.1292 | 633.3184
4335.1292 | 633.6911
4336.1292 | 633.556
4337.1292 | 632.6646
4338.1292 | 633.3478
4339.1292 | 633.9904
4340.1292 | 633.9917
4341.1292 | 633.2527
4342.1292 | 633.031
4343.1292 | 632.782
4344.1292 | 633.2954
4345.1292 | 633.0586
4346.1292 | 633.2738
4347.1292 | 633.5035
4348.1292 | 634.4051
4349.1448 | 633.9845
4350.1292 | 634.0979
4351.1292 | 634.8628
4352.1292 | 636.3174
4353.1292 | 636.6395
4354.1292 | 636.4932
4355.1292 | 636.503
4356.1292 | 636.997
4357.1292 | 637.3583
4358.1292 | 637.2838
4359.1292 | 638.1034
4360.1292 | 637.7429
4361.1292 | 638.5664
4362.1292 | 639.0405
4363.1292 | 639.6862
4364.1292 | 640.3239
4365.1292 | 640.1473
4366.1292 | 639.1886
4367.1292 | 641.7223
4368.1292 | 642.3316
4369.1292 | 640.8154
4370.1292 | 639.7663
4371.1292 | 639.1719
4372.1292 | 638.732
4373.1292 | 638.4799
4374.1292 | 638.851
4375.1292 | 638.7819
4376.1292 | 638.0755
4377.1292 | 636.9977
4378.1292 | 636.7919
4379.1448 | 636.6633
4380.1292 | 636.4798
4381.1292 | 637.2747
4382.1292 | 637.1581
4383.1292 | 636.3753
4384.1292 | 635.767
4385.1292 | 634.5008
4386.1292 | 634.3172
4387.1292 | 633.3137
4388.1292 | 632.7218
4389.1292 | 632.7423
4390.1292 | 632.6454
4391.1292 | 632.5352
4392.1292 | 632.6708
4393.1292 | 632.9784
4394.1292 | 633.0258
4395.1292 | 633.0369
4396.1292 | 633.832
4397.1292 | 634.3407
4398.1292 | 633.2792
4399.1292 | 634.6197
4400.1292 | 635.0015
4401.1292 | 634.3858
4402.1292 | 632.6021
4403.1292 | 632.0399
4404.1292 | 634.1748
4405.1292 | 634.1782
4406.1292 | 634.6482
4407.1292 | 636.2315
4408.1292 | 635.8883
4409.1292 | 636.7012
4410.1292 | 635.9437
4411.1292 | 635.3866
4412.1292 | 636.4945
4413.1292 | 638.5502
4414.1292 | 638.489
4415.1292 | 637.8287
4416.1292 | 637.5466
4417.1292 | 637.7851
4418.1292 | 637.9045
4419.1292 | 637.8779
4420.1292 | 638.5426
4421.1292 | 638.3337
4422.1292 | 637.9064
4423.1292 | 637.0029
4424.1292 | 636.5148
4425.1292 | 636.6302
4426.1292 | 636.8062
4427.1292 | 635.4326
4428.1292 | 635.6309
4429.1292 | 635.9265
4430.1292 | 636.3682
4431.1292 | 636.6679
4432.1292 | 636.9006
4433.1292 | 636.8887
4434.1292 | 637.2804
4435.1292 | 637.2386
4436.1292 | 636.7696
4437.1292 | 636.5964
4438.1292 | 636.81
4439.1448 | 636.3802
4440.1292 | 636.8755
4441.1292 | 637.0592
4442.1292 | 636.2086
4443.1292 | 635.201
4444.1292 | 635.2143
4445.1292 | 636.2841
4446.1292 | 636.8611
4447.1292 | 637.657
4448.1292 | 638.5489
4449.1292 | 638.8656
4450.1292 | 639.5631
4451.1292 | 640.1343
4452.1292 | 639.7913
4453.1292 | 639.3111
4454.1292 | 639.2325
4455.1292 | 639.0452
4456.1292 | 638.3359
4457.1292 | 637.267
4458.1292 | 636.838
4459.1292 | 636.6716
4460.1292 | 635.7584
4461.1292 | 635.11
4462.1292 | 634.4094
4463.1292 | 633.4043
4464.1292 | 632.9497
4465.1292 | 632.5934
4466.1292 | 632.3078
4467.1292 | 631.7609
4468.1292 | 631.5718
4469.1448 | 631.8499
4470.1292 | 631.741
4471.1292 | 630.9203
4472.1292 | 631.04
4473.1292 | 632.0284
4474.1292 | 633.4413
4475.1292 | 632.6155
4476.1292 | 632.2629
4477.1292 | 631.7444
4478.1292 | 630.689
4479.1292 | 631.4352
4480.1292 | 631.2456
4481.1292 | 629.9054
4482.1292 | 629.8764
4483.1292 | 630.9205
4484.1292 | 631.5167
4485.1292 | 632.9111
4486.1292 | 633.5666
4487.1292 | 632.8154
4488.1292 | 633.5202
4489.1292 | 635.2521
4490.1292 | 635.3632
4491.1292 | 635.6105
4492.1292 | 635.4428
4493.1292 | 635.4431
4494.1292 | 635.363
4495.1292 | 634.8681
4496.1292 | 634.6504
4497.1292 | 634.1875
4498.1292 | 634.3856
4499.1448 | 635.6663
4500.1292 | 637.7428