## Test Conditions
DESIREE-FIRE Intermediate Scale Test Number 11 - Circuit Simulator Data Only
Test Date: | 2009-11-25
DCSim DAQ Start Time | 13:25
DCSim Time for Synchronization | 13:28
Heat Source Synchronization | 0:02 | hour:minutes:seconds
Heat Source DAQ Start Time | 13:26
Fire Time | 15:38
Offset | 2:13 | hour:minutes:seconds | This is the time after the DCSim DAQ was started and the heat source was initiated.
| 7980 | seconds
Heat Source Offset | 2:12 | hour:minutes:seconds | This is the time after the Heat Source DAQ was started and the heat source was initiated.
| 7945 | seconds
Heat Source Stop Time | 16:53
Test Duration | 1:15 | hour:minutes:seconds
| 4500 | seconds
CT500 turns | 2 | 1 or 2 | This is the number of times the lead conductor within the DCSim Panels were wrapped around the Hall Effect Device of the current transducer.
CT35 turns | 5 | 1 or 5
Pre-Test Baseline: | Gathered | Gathered or Not Gathered
Cable Information: | Record info about cable type on each circuit and which of the cable thermocouples corresponds to cable and air temperature
Unit number | Cable Type |  | Cable TC channel | Air TC Channel
MOV 1 | EPR/CPE, 7c, 12AWG |  | Cable thermocouples were not used for this test. | Channel 1 which is defined as "B Position - Middle" in the Temperature Data File respresents the temperature in the center of the cable tray.
MOV 2 | EPR/CPE, 7c, 12AWG |  | Cable thermocouples were not used for this test. | Channel 5, 6, and 7 represents the air temperature 3', 5', and 7' down the cable tray located in D-Position. These are labeled as "D-Position - 3'", "D-Position - Middle", " D-Position - 7'", respectively.
A Note on Data Conversion and Accuracy:
Two different types of voltage transducers were used for each circuit. A bidirectional transducer (Ohio Semitronics, model number VT7-005X5-11) produces a 0 - 5V output signal which is directly proportional to the DC input ranging from 0 - 150VDC. The accuracy of this device is +/-0.25% full scale at DC and the response time is 50 mircoseconds. The unidirectional DC voltage isolator (Ohio Semitronics, model number VTU-005X5) used throughout tests also produces a 0 - 5V output over a 0 - 150VDC range. The accuracy of this device is +/-0.25% Rdg., +/-1% full scale at DC and the response time is 500 microseconds. Two different current transducers were for each circuit. One current transducer (Ohio Semitronics, model number CTL-51/35) was used to detect lower (0 - 35A) amperage transient behavior through a paired and calibrated signal conditioner (CTA201RX5). The other transducer (Ohio Semitronics, model number CTL-601/500) was set to detect transient current increases from 0 - 500A. These were also paired and calibrated with a signal conditioner (CTA2-1X5).
The readings were monitored using a National Instruments SCXI-1100 modules attached to SCXI-1300 multiplexers and housed within a SCXI-1001, 12-slot chassis. The "Raw Data" worksheet has been previously converted by LabView program created for this test series. The nominal zero point readings for each current transducer was taken before each test due to an electromagnetic effect created by direct current power. Zero Point values are provided, and the full run is documented in a separate data sheet (see "Current Offsets" worksheet). The converted data are presented as nominal indications of circuit path voltage and current. The data gathering equipment (transducers and DAQ card) have not been subject to specific calibration beyond that provided by the manufacturers. The accuracy of the converted data is estimated at +/-2%.

## Electrical Data
Fire Time (s) | Ground_VT7_1 | Ground_VTU_1 | Ground_VTU_2 | MOV-1_CT500 | MOV-1a_CT35_1_P | MOV-1a_CT35_2_N | MOV-1b_CT35_1_G | MOV-1b_CT35_2_R | MOV-1b_CT35_3_YO | MOV-1b_CT35_4_YC | MOV-2_CT500 | MOV-2a_CT35_1_P | MOV-2a_CT35_2_N | MOV-2b_CT35_1_G | MOV-2b_CT35_2_R | MOV-2b_CT35_3_YO | 2b_CT35_4_YC1 | MOV-1a_VT7_1_SP | MOV-1a_VTU_1_P | MOV-1a_VTU_2_N | MOV-1b_VT7_1_G | MOV-1b_VT7_2_R | MOV-1b_VT7_3_YO1 | MOV-1b_VT7_4_YC1 | MOV-2a_VT7_1_SP | MOV-2a_VTU_1_P | MOV-2a_VTU_2_N | MOV-2b_VT7_1_G | MOV-2b_VT7_2_R | 2b_VT7_3_YO1 | MOV-2b_VT7_4_YC1 | {MOV1} V(N) - V(Batt -) | {MOV1} V(P) - V(Batt +) | {MOV1} V(G) - V(Batt +) | {MOV1} V(R) - V(Batt -) | {MOV1} V(YC1) - V(Batt -) | {MOV1} V(YO1) - V(Batt -) | {MOV1} V(YC1) - V(N) | {MOV1} V(YO1) - V(N) | {MOV2} V(N) - V(Batt -) | {MOV2} V(P) - V(Batt +) | {MOV2} V(G) - V(Batt +) | {MOV2} V(R) - V(Batt -) | {MOV2} V(YC1) - V(Batt -) | {MOV2} V(YO1) - V(Batt -) | {MOV2} V(YC1) - V(N) | {MOV2} V(YO1) - V(N) | {MOV-1} V(R) - V(N) | {MOV-1} V(G) - V(N) | {MOV-2} V(R) - V(N) | {MOV-2} V(G) - V(N) | {MOV-1} V(P) - V(N) | {MOV-2} V(P) - V(N) | {MOV-1} V(P) - V(Batt -) | {MOV-2} V(P) - V(Batt -) | {MOV-1} V(N) - V(Batt +) | {MOV-2} V(N) - V(Batt +) | {MOV-1} V(G) - V(Batt -) | {MOV2} V(G) - V(Batt-) | {MOV1} V(SP) - V(Batt -) | {MOV2} V(SP) - V(Batt -)
-0.42188 | 122.9324 | -62.3428 | 60.2417 | 0.0025177 | -0.026547 | -0.023469 | 0.064157 | -0.033861 | -0.047604 | -0.038683 | 0.00094606 | -0.020108 | 0.054918 | 0.047544 | -0.21381 | -0.017701 | -0.018126 | -0.09613 | 60.2097 | -62.4573 | 60.379 | -62.0956 | -62.59 | -62.5397 | 0.068665 | 60.173 | -62.352 | 60.4294 | -62.233 | -62.3657 | -62.3657 | -0.11444 | -0.032043 | 0.13733 | 0.24719 | -0.19684 | -0.24719 | -0.082398 | -0.13275 | -0.009156 | -0.068664 | 0.18768 | 0.10986 | -0.022889 | -0.022889 | -0.013733 | -0.013733 | 0.36163 | 122.8363 | 0.11902 | 122.7814 | 122.6669 | 122.525 | 122.5525 | 122.5159 | -122.699 | -122.5937 | 122.7219 | 122.7722 | 62.2467 | 62.4115
1.3125 | 122.8409 | -62.3932 | 60.2921 | -0.0051118 | -0.025906 | -0.022614 | 0.067575 | -0.02788 | -0.045254 | -0.039965 | 0.00094606 | -0.019895 | 0.057268 | 0.051603 | -0.2136 | -0.021546 | -0.022185 | -0.14191 | 60.3058 | -62.4573 | 60.2737 | -62.2375 | -62.6999 | -62.6541 | -0.082397 | 60.2325 | -62.3932 | 60.3287 | -62.3657 | -62.5031 | -62.4619 | -0.064087 | 0.013733 | -0.01831 | 0.15564 | -0.26093 | -0.3067 | -0.19684 | -0.24262 | 0 | -0.059509 | 0.036621 | 0.027465 | -0.068665 | -0.10986 | -0.068665 | -0.10986 | 0.21973 | 122.731 | 0.027465 | 122.7219 | 122.7631 | 122.6257 | 122.699 | 122.6257 | -122.7493 | -122.6852 | 122.6669 | 122.7219 | 62.2513 | 62.3108
3.0781 | 122.8317 | -62.3611 | 60.3195 | -0.0051118 | -0.029538 | -0.026032 | 0.065439 | -0.030657 | -0.045681 | -0.038469 | 0.00094606 | -0.020322 | 0.055559 | 0.050535 | -0.21424 | -0.021119 | -0.02133 | 0.009155 | 60.2646 | -62.4023 | 60.347 | -62.1277 | -62.5809 | -62.5534 | 0.068665 | 60.2692 | -62.352 | 60.3561 | -62.2879 | -62.4252 | -62.4344 | -0.041199 | -0.054932 | 0.027466 | 0.23346 | -0.19226 | -0.21973 | -0.15106 | -0.17853 | 0.009155 | -0.050354 | 0.036621 | 0.073242 | -0.073242 | -0.064087 | -0.082397 | -0.073242 | 0.27466 | 122.7493 | 0.064087 | 122.7081 | 122.6669 | 122.6212 | 122.6257 | 122.6303 | -122.7219 | -122.6715 | 122.7081 | 122.7173 | 62.3703 | 62.4298
4.7969 | 122.8363 | -62.3657 | 60.3699 | 0.0025177 | -0.027615 | -0.024323 | 0.064798 | -0.031298 | -0.046536 | -0.037615 | 0.00094606 | -0.021176 | 0.055559 | 0.049253 | -0.2136 | -0.018555 | -0.02368 | -0.041199 | 60.3333 | -62.4619 | 60.2875 | -62.1964 | -62.6266 | -62.59 | 0.022888 | 60.2829 | -62.3795 | 60.379 | -62.2971 | -62.4115 | -62.3886 | -0.09613 | -0.036621 | -0.082397 | 0.16937 | -0.2243 | -0.26093 | -0.12817 | -0.1648 | -0.013733 | -0.086975 | 0.009155 | 0.068665 | -0.022888 | -0.045776 | -0.009155 | -0.032043 | 0.2655 | 122.7493 | 0.082398 | 122.7585 | 122.7951 | 122.6624 | 122.699 | 122.6486 | -122.8317 | -122.7493 | 122.6532 | 122.7448 | 62.3245 | 62.3886
6.5625 | 122.8546 | -62.3566 | 60.3149 | -0.0051118 | -0.028042 | -0.024964 | 0.066934 | -0.031084 | -0.047604 | -0.037828 | -0.0021057 | -0.021817 | 0.0562 | 0.04968 | -0.21531 | -0.017701 | -0.020262 | -0.004578 | 60.2783 | -62.4298 | 60.3516 | -62.1231 | -62.5854 | -62.5671 | 0.073242 | 60.2325 | -62.3337 | 60.3882 | -62.2742 | -62.4161 | -62.3886 | -0.073243 | -0.036621 | 0.036621 | 0.23346 | -0.21057 | -0.22888 | -0.13733 | -0.15564 | 0.022888 | -0.082397 | 0.073243 | 0.082397 | -0.032044 | -0.05951 | -0.054932 | -0.082398 | 0.3067 | 122.7814 | 0.059509 | 122.7219 | 122.7081 | 122.5662 | 122.6349 | 122.5891 | -122.7448 | -122.6486 | 122.7081 | 122.7448 | 62.352 | 62.4298
8.2812 | 122.9416 | -62.3474 | 60.2463 | -0.0051118 | -0.02676 | -0.024109 | 0.065012 | -0.028307 | -0.045681 | -0.039537 | 0.0039979 | -0.023099 | 0.057909 | 0.053098 | -0.21296 | -0.019196 | -0.02133 | -0.09613 | 60.2097 | -62.4435 | 60.3516 | -62.1002 | -62.59 | -62.5442 | 0.032043 | 60.1685 | -62.384 | 60.4431 | -62.2467 | -62.3657 | -62.3337 | -0.09613 | -0.036621 | 0.10529 | 0.24719 | -0.19684 | -0.24262 | -0.10071 | -0.14648 | -0.036621 | -0.07782 | 0.19684 | 0.10071 | 0.013733 | -0.018311 | 0.050354 | 0.01831 | 0.34332 | 122.7951 | 0.13733 | 122.8271 | 122.6532 | 122.5525 | 122.5571 | 122.5159 | -122.6898 | -122.6303 | 122.699 | 122.7905 | 62.2513 | 62.3795
10.0469 | 122.9004 | -62.3657 | 60.2737 | 0.0025177 | -0.030819 | -0.023255 | 0.064585 | -0.031511 | -0.048672 | -0.039965 | -0.0021057 | -0.022245 | 0.054277 | 0.041563 | -0.21402 | -0.019837 | -0.019621 | -0.10071 | 60.2325 | -62.4252 | 60.3287 | -62.1185 | -62.5854 | -62.5534 | 0.045776 | 60.1868 | -62.3611 | 60.3973 | -62.2467 | -62.3474 | -62.3703 | -0.059509 | -0.041199 | 0.054931 | 0.24719 | -0.18768 | -0.21973 | -0.12817 | -0.16022 | 0.004578 | -0.086975 | 0.1236 | 0.11902 | -0.004577 | 0.018311 | -0.009155 | 0.013733 | 0.3067 | 122.7539 | 0.11444 | 122.7585 | 122.6578 | 122.5479 | 122.5983 | 122.5525 | -122.699 | -122.6349 | 122.6944 | 122.7631 | 62.265 | 62.4115
11.8281 | 122.7997 | -62.3474 | 60.2875 | -0.0051118 | -0.025906 | -0.021973 | 0.066934 | -0.032366 | -0.048886 | -0.039324 | 0.0039979 | -0.018827 | 0.055345 | 0.04968 | -0.21402 | -0.018555 | -0.024321 | -0.064087 | 60.2875 | -62.4527 | 60.2966 | -62.1689 | -62.645 | -62.6175 | -0.022888 | 60.2371 | -62.4023 | 60.3195 | -62.3474 | -62.4756 | -62.439 | -0.10529 | 0 | 0.009155 | 0.17853 | -0.27008 | -0.29755 | -0.1648 | -0.19226 | -0.054932 | -0.050354 | 0.032043 | 0 | -0.091553 | -0.12817 | -0.036621 | -0.073242 | 0.28381 | 122.7493 | 0.054932 | 122.7219 | 122.7402 | 122.6395 | 122.6349 | 122.5845 | -122.7402 | -122.6898 | 122.644 | 122.6669 | 62.2833 | 62.3245
13.6094 | 122.8271 | -62.3703 | 60.2692 | 0.0025177 | -0.026333 | -0.027741 | 0.069498 | -0.029802 | -0.044827 | -0.037401 | -0.0021057 | -0.020322 | 0.055345 | 0.051603 | -0.21595 | -0.019623 | -0.019408 | -0.13733 | 60.2921 | -62.4344 | 60.2554 | -62.2147 | -62.6862 | -62.6404 | -0.073242 | 60.2051 | -62.3886 | 60.347 | -62.3245 | -62.4756 | -62.4298 | -0.064087 | 0.022888 | -0.013733 | 0.15564 | -0.27008 | -0.31586 | -0.20599 | -0.25177 | -0.018311 | -0.064087 | 0.07782 | 0.045776 | -0.05951 | -0.10529 | -0.041199 | -0.086975 | 0.21973 | 122.6898 | 0.064087 | 122.7356 | 122.7264 | 122.5937 | 122.6624 | 122.5754 | -122.7036 | -122.6578 | 122.6257 | 122.7173 | 62.233 | 62.2971
15.3281 | 122.9599 | -62.3291 | 60.2737 | 0.0025177 | -0.031033 | -0.024109 | 0.065012 | -0.033648 | -0.047817 | -0.03911 | 0.00094606 | -0.022031 | 0.054918 | 0.046903 | -0.21573 | -0.020905 | -0.021544 | -0.032043 | 60.228 | -62.4069 | 60.3882 | -62.027 | -62.5168 | -62.4985 | 0.16479 | 60.1776 | -62.352 | 60.4614 | -62.1735 | -62.2787 | -62.3154 | -0.077819 | -0.045777 | 0.11444 | 0.30212 | -0.16937 | -0.18768 | -0.091553 | -0.10986 | -0.022888 | -0.096131 | 0.18768 | 0.15564 | 0.013733 | 0.050354 | 0.036621 | 0.073242 | 0.37994 | 122.7951 | 0.17853 | 122.8134 | 122.6349 | 122.5296 | 122.5571 | 122.5067 | -122.6807 | -122.6257 | 122.7173 | 122.7905 | 62.2971 | 62.4939
17.0312 | 122.7997 | -62.3245 | 60.3424 | 0.0025177 | -0.027829 | -0.028168 | 0.063944 | -0.029375 | -0.051235 | -0.04146 | -0.0021057 | -0.020536 | 0.055132 | 0.048826 | -0.2136 | -0.017487 | -0.020476 | -0.045776 | 60.3149 | -62.4252 | 60.2875 | -62.1735 | -62.5992 | -62.59 | 0.027466 | 60.2692 | -62.3474 | 60.3241 | -62.3062 | -62.4298 | -62.4252 | -0.10071 | -0.027466 | -0.054931 | 0.15106 | -0.2655 | -0.27466 | -0.16479 | -0.17395 | -0.022888 | -0.073242 | -0.01831 | 0.018311 | -0.10071 | -0.10529 | -0.07782 | -0.082398 | 0.25177 | 122.7127 | 0.041199 | 122.6715 | 122.7402 | 122.6166 | 122.6395 | 122.5937 | -122.7676 | -122.6898 | 122.612 | 122.6486 | 62.2787 | 62.352
18.8125 | 122.8043 | -62.3337 | 60.3378 | -0.02037 | -0.029751 | -0.024109 | 0.065225 | -0.033861 | -0.048886 | -0.040819 | -0.0021057 | -0.019681 | 0.055559 | 0.04968 | -0.21381 | -0.018342 | -0.019621 | -0.064087 | 60.3058 | -62.4344 | 60.2966 | -62.1826 | -62.6129 | -62.59 | 0.018311 | 60.2783 | -62.3428 | 60.3287 | -62.3108 | -62.4481 | -62.4161 | -0.10071 | -0.032044 | -0.041199 | 0.15106 | -0.25635 | -0.27924 | -0.15564 | -0.17853 | -0.009155 | -0.05951 | -0.009156 | 0.022888 | -0.082398 | -0.11444 | -0.073243 | -0.10529 | 0.25177 | 122.731 | 0.032043 | 122.6715 | 122.7402 | 122.6212 | 122.6395 | 122.612 | -122.7722 | -122.6807 | 122.6303 | 122.6624 | 62.2696 | 62.352
20.5938 | 122.9004 | -62.3245 | 60.2829 | -0.0051118 | -0.028897 | -0.023896 | 0.064798 | -0.035357 | -0.047817 | -0.038256 | -0.0021057 | -0.022885 | 0.055345 | 0.04199 | -0.21338 | -0.018769 | -0.023253 | -0.11902 | 60.2463 | -62.4161 | 60.2966 | -62.1552 | -62.5946 | -62.5626 | 0.004578 | 60.1868 | -62.3703 | 60.379 | -62.2696 | -62.3749 | -62.3795 | -0.091553 | -0.036621 | 0.013733 | 0.16937 | -0.23804 | -0.27008 | -0.14648 | -0.17853 | -0.045776 | -0.09613 | 0.09613 | 0.054932 | -0.054932 | -0.050354 | -0.009156 | -0.004578 | 0.26093 | 122.7127 | 0.10071 | 122.7493 | 122.6624 | 122.5571 | 122.5708 | 122.5113 | -122.699 | -122.6532 | 122.6212 | 122.7036 | 62.2055 | 62.3291
22.3594 | 122.9599 | -62.3108 | 60.2692 | -0.0051118 | -0.028256 | -0.025177 | 0.061594 | -0.029375 | -0.047817 | -0.041246 | 0.00094606 | -0.022458 | 0.056627 | 0.050962 | -0.21702 | -0.019623 | -0.02368 | -0.009155 | 60.2371 | -62.4023 | 60.3928 | -62.027 | -62.4985 | -62.4756 | 0.19684 | 60.1822 | -62.3428 | 60.4614 | -62.1506 | -62.3016 | -62.3062 | -0.091553 | -0.032043 | 0.1236 | 0.28381 | -0.16479 | -0.18768 | -0.073242 | -0.09613 | -0.032043 | -0.086975 | 0.19226 | 0.16022 | 0.004578 | 0.009155 | 0.036621 | 0.041198 | 0.37537 | 122.7951 | 0.19226 | 122.8043 | 122.6395 | 122.525 | 122.5479 | 122.493 | -122.6715 | -122.612 | 122.7036 | 122.7722 | 62.3016 | 62.5076
24.125 | 122.8683 | -62.3337 | 60.2646 | -0.0051118 | -0.02612 | -0.028168 | 0.06373 | -0.031511 | -0.049526 | -0.043169 | 0.0039979 | -0.022245 | 0.052996 | 0.046903 | -0.21274 | -0.01941 | -0.02133 | -0.11444 | 60.2097 | -62.4252 | 60.3241 | -62.1094 | -62.5992 | -62.558 | 0.022888 | 60.1547 | -62.3657 | 60.3836 | -62.2787 | -62.3886 | -62.3795 | -0.091553 | -0.054931 | 0.05951 | 0.2243 | -0.2243 | -0.2655 | -0.13275 | -0.17395 | -0.032044 | -0.10986 | 0.11902 | 0.054931 | -0.045777 | -0.054932 | -0.013733 | -0.022888 | 0.31586 | 122.7493 | 0.086975 | 122.7493 | 122.6349 | 122.5204 | 122.5433 | 122.4884 | -122.6898 | -122.6303 | 122.6578 | 122.7173 | 62.2192 | 62.3566
25.8438 | 122.7722 | -62.3611 | 60.3058 | 0.0025177 | -0.027829 | -0.025391 | 0.065653 | -0.03258 | -0.044613 | -0.038896 | -0.0021057 | -0.019467 | 0.057482 | 0.058225 | -0.2136 | -0.018982 | -0.022612 | -0.07782 | 60.2875 | -62.4344 | 60.2692 | -62.2009 | -62.6678 | -62.6404 | -0.050354 | 60.2371 | -62.352 | 60.3012 | -62.352 | -62.4847 | -62.4435 | -0.073242 | -0.01831 | -0.036621 | 0.16022 | -0.27924 | -0.3067 | -0.20599 | -0.23346 | 0.009155 | -0.068664 | -0.004578 | 0.009155 | -0.082397 | -0.1236 | -0.091552 | -0.13275 | 0.23346 | 122.7036 | 0 | 122.6532 | 122.7219 | 122.5891 | 122.6486 | 122.5983 | -122.7402 | -122.6578 | 122.6303 | 122.6624 | 62.2833 | 62.3108
27.6406 | 122.7905 | -62.3566 | 60.3378 | 0.0025177 | -0.029324 | -0.025818 | 0.063516 | -0.029162 | -0.048245 | -0.03911 | -0.0021057 | -0.021176 | 0.055132 | 0.050321 | -0.21637 | -0.018982 | -0.02133 | -0.050354 | 60.2875 | -62.4573 | 60.2875 | -62.1597 | -62.6129 | -62.5946 | 0.018311 | 60.2646 | -62.3383 | 60.3241 | -62.3154 | -62.4207 | -62.4207 | -0.10071 | -0.050354 | -0.050354 | 0.19684 | -0.23804 | -0.25635 | -0.13733 | -0.15564 | 0.01831 | -0.073243 | -0.013733 | 0.041198 | -0.064087 | -0.064087 | -0.082397 | -0.082397 | 0.29755 | 122.7448 | 0.022888 | 122.6624 | 122.7448 | 122.6028 | 122.644 | 122.6212 | -122.7951 | -122.6761 | 122.644 | 122.6807 | 62.3062 | 62.3749
29.3594 | 122.9141 | -62.3291 | 60.2829 | -0.0051118 | -0.027401 | -0.026246 | 0.062662 | -0.034075 | -0.048458 | -0.04146 | -0.0051575 | -0.022458 | 0.053209 | 0.047117 | -0.21467 | -0.018769 | -0.020476 | -0.073242 | 60.2371 | -62.4069 | 60.3424 | -62.0956 | -62.5305 | -62.5122 | 0.082397 | 60.2005 | -62.3611 | 60.4294 | -62.1918 | -62.3062 | -62.3154 | -0.077819 | -0.045776 | 0.059509 | 0.23346 | -0.1831 | -0.20142 | -0.10529 | -0.1236 | -0.032043 | -0.082398 | 0.14648 | 0.13733 | 0.013733 | 0.022889 | 0.045776 | 0.054932 | 0.31128 | 122.7493 | 0.16937 | 122.7905 | 122.644 | 122.5616 | 122.5662 | 122.5296 | -122.6898 | -122.644 | 122.6715 | 122.7585 | 62.2559 | 62.4115
31.1094 | 122.7997 | -62.3566 | 60.3241 | 0.0025177 | -0.027615 | -0.026246 | 0.066507 | -0.032152 | -0.050808 | -0.036974 | -0.0021057 | -0.021817 | 0.055345 | 0.050535 | -0.21488 | -0.01941 | -0.023039 | -0.054932 | 60.2737 | -62.4344 | 60.2875 | -62.178 | -62.6038 | -62.5763 | 0.032043 | 60.2875 | -62.3703 | 60.3149 | -62.3154 | -62.4298 | -62.4252 | -0.07782 | -0.050354 | -0.036621 | 0.17853 | -0.21973 | -0.24719 | -0.14191 | -0.16937 | -0.013733 | -0.036621 | -0.009156 | 0.041198 | -0.068665 | -0.073243 | -0.054932 | -0.05951 | 0.25635 | 122.7219 | 0.054931 | 122.6852 | 122.7081 | 122.6578 | 122.6303 | 122.644 | -122.7585 | -122.6944 | 122.644 | 122.6715 | 62.3016 | 62.3886
32.8906 | 122.8226 | -62.3291 | 60.3241 | 0.0025177 | -0.027401 | -0.022828 | 0.067362 | -0.024675 | -0.046536 | -0.041887 | -0.0051575 | -0.019254 | 0.054918 | 0.050962 | -0.21531 | -0.019623 | -0.023894 | -0.013733 | 60.2875 | -62.4344 | 60.3333 | -62.1094 | -62.5809 | -62.558 | 0.054932 | 60.2188 | -62.3428 | 60.3836 | -62.2742 | -62.4207 | -62.3795 | -0.10529 | -0.036621 | 0.009155 | 0.21973 | -0.22888 | -0.25177 | -0.1236 | -0.14648 | -0.013732 | -0.10529 | 0.059509 | 0.054932 | -0.050354 | -0.091552 | -0.036622 | -0.07782 | 0.32501 | 122.7676 | 0.068664 | 122.7264 | 122.7219 | 122.5616 | 122.6166 | 122.5479 | -122.7585 | -122.6669 | 122.6624 | 122.7127 | 62.3154 | 62.384
34.6719 | 122.7859 | -62.3428 | 60.3378 | 0.010147 | -0.027829 | -0.025818 | 0.063089 | -0.034075 | -0.047817 | -0.037401 | -0.0051575 | -0.019895 | 0.057054 | 0.050321 | -0.2121 | -0.019196 | -0.020903 | 0.004578 | 60.2509 | -62.4115 | 60.3287 | -62.1277 | -62.5809 | -62.5488 | 0.045776 | 60.228 | -62.3428 | 60.3378 | -62.2879 | -62.4115 | -62.4252 | -0.068665 | -0.086976 | -0.009156 | 0.21515 | -0.20599 | -0.23804 | -0.13733 | -0.16937 | 0 | -0.10986 | 0 | 0.054931 | -0.082398 | -0.068665 | -0.082398 | -0.068665 | 0.28381 | 122.7402 | 0.054931 | 122.6807 | 122.6624 | 122.5708 | 122.5937 | 122.5708 | -122.7493 | -122.6807 | 122.6715 | 122.6807 | 62.3474 | 62.3886
36.4531 | 122.7722 | -62.3611 | 60.3149 | -0.012741 | -0.02612 | -0.024323 | 0.067575 | -0.027239 | -0.04739 | -0.039537 | 0.00094606 | -0.021817 | 0.055559 | 0.047758 | -0.21531 | -0.019837 | -0.022185 | -0.10071 | 60.2829 | -62.4619 | 60.2509 | -62.2101 | -62.677 | -62.6358 | -0.09613 | 60.2142 | -62.384 | 60.3104 | -62.3611 | -62.4985 | -62.4298 | -0.10071 | -0.032043 | -0.064087 | 0.15106 | -0.27466 | -0.31586 | -0.17395 | -0.21515 | -0.022888 | -0.10071 | -0.004577 | 0 | -0.068665 | -0.13733 | -0.045777 | -0.11444 | 0.25177 | 122.7127 | 0.022888 | 122.6944 | 122.7448 | 122.5983 | 122.644 | 122.5754 | -122.7768 | -122.699 | 122.612 | 122.6715 | 62.2604 | 62.265
38.2344 | 122.8683 | -62.3291 | 60.2966 | 0.0025177 | -0.028897 | -0.023682 | 0.063516 | -0.033861 | -0.047817 | -0.041887 | 0.0039979 | -0.022672 | 0.056841 | 0.04434 | -0.21189 | -0.017701 | -0.020689 | -0.11444 | 60.228 | -62.4435 | 60.3149 | -62.1231 | -62.5992 | -62.558 | 0.022888 | 60.1685 | -62.384 | 60.3836 | -62.2559 | -62.3474 | -62.3657 | -0.11444 | -0.068665 | 0.01831 | 0.20599 | -0.22888 | -0.27008 | -0.11444 | -0.15564 | -0.054931 | -0.12817 | 0.086975 | 0.073243 | -0.036621 | -0.01831 | 0.01831 | 0.036621 | 0.32043 | 122.7585 | 0.12817 | 122.7676 | 122.6715 | 122.5525 | 122.5571 | 122.4976 | -122.7402 | -122.6807 | 122.644 | 122.7127 | 62.2147 | 62.352
40 | 122.7768 | -62.3474 | 60.3149 | 0.010147 | -0.02911 | -0.027314 | 0.065439 | -0.032152 | -0.049526 | -0.039965 | -0.0021057 | -0.021817 | 0.058763 | 0.055234 | -0.21488 | -0.018555 | -0.020476 | -0.004578 | 60.26 | -62.4207 | 60.2921 | -62.1323 | -62.59 | -62.558 | 0.054932 | 60.2188 | -62.3383 | 60.3378 | -62.2971 | -62.4115 | -62.4298 | -0.073242 | -0.054931 | -0.022888 | 0.21515 | -0.21057 | -0.24262 | -0.13733 | -0.16937 | 0.009155 | -0.09613 | 0.022889 | 0.050354 | -0.082398 | -0.064087 | -0.091553 | -0.073242 | 0.28839 | 122.7127 | 0.041199 | 122.6761 | 122.6807 | 122.5571 | 122.6074 | 122.5662 | -122.7356 | -122.6532 | 122.6395 | 122.6852 | 62.3428 | 62.4023
41.7188 | 122.7997 | -62.3199 | 60.3333 | 0.0025177 | -0.027401 | -0.026673 | 0.066721 | -0.03322 | -0.048886 | -0.038683 | -0.0021057 | -0.020108 | 0.057909 | 0.047971 | -0.21488 | -0.021332 | -0.021758 | -0.045776 | 60.3012 | -62.4115 | 60.2783 | -62.1826 | -62.6175 | -62.59 | 0.032043 | 60.2463 | -62.3337 | 60.3333 | -62.2925 | -62.4161 | -62.384 | -0.091553 | -0.032044 | -0.054932 | 0.13733 | -0.27008 | -0.29755 | -0.17853 | -0.20599 | -0.013733 | -0.086975 | 0 | 0.027466 | -0.064087 | -0.096131 | -0.050354 | -0.082398 | 0.22888 | 122.6898 | 0.041199 | 122.6669 | 122.7127 | 122.58 | 122.6212 | 122.5662 | -122.7448 | -122.6669 | 122.5983 | 122.6532 | 62.2742 | 62.352
43.4844 | 122.7631 | -62.352 | 60.3378 | 0.010147 | -0.027829 | -0.025818 | 0.066934 | -0.028521 | -0.048458 | -0.04146 | 0.00094606 | -0.019895 | 0.055559 | 0.047971 | -0.21317 | -0.01941 | -0.020476 | -0.036621 | 60.2646 | -62.4115 | 60.2783 | -62.1506 | -62.6038 | -62.5763 | 0.041199 | 60.2417 | -62.3566 | 60.3287 | -62.2879 | -62.4069 | -62.4207 | -0.059509 | -0.073243 | -0.05951 | 0.20142 | -0.2243 | -0.25177 | -0.16479 | -0.19226 | -0.004577 | -0.096131 | -0.009156 | 0.064087 | -0.068664 | -0.054931 | -0.064087 | -0.050354 | 0.26093 | 122.6898 | 0.068664 | 122.6852 | 122.6761 | 122.5983 | 122.6166 | 122.5937 | -122.7493 | -122.6944 | 122.6303 | 122.6807 | 62.3154 | 62.3932
45.1875 | 122.8867 | -62.2925 | 60.2783 | -0.012741 | -0.027829 | -0.02176 | 0.065012 | -0.034075 | -0.048031 | -0.039537 | 0.00094606 | -0.021817 | 0.057695 | 0.049467 | -0.21381 | -0.018982 | -0.019408 | -0.091553 | 60.2417 | -62.4207 | 60.3058 | -62.1185 | -62.5626 | -62.5397 | 0.054932 | 60.1868 | -62.3703 | 60.3882 | -62.233 | -62.3199 | -62.3428 | -0.12817 | -0.036621 | 0.027466 | 0.17395 | -0.24719 | -0.27008 | -0.11902 | -0.14191 | -0.07782 | -0.091552 | 0.10986 | 0.059509 | -0.050354 | -0.027466 | 0.027466 | 0.050354 | 0.30212 | 122.7264 | 0.13733 | 122.7585 | 122.6624 | 122.5571 | 122.5342 | 122.4792 | -122.699 | -122.6486 | 122.5983 | 122.6807 | 62.2009 | 62.3474
46.9688 | 122.8363 | -62.3383 | 60.3149 | -0.0051118 | -0.028897 | -0.022828 | 0.066507 | -0.03023 | -0.047817 | -0.03911 | 0.00094606 | -0.020322 | 0.055773 | 0.044767 | -0.21509 | -0.018342 | -0.017699 | -0.027466 | 60.2692 | -62.4023 | 60.3287 | -62.114 | -62.5717 | -62.5534 | 0.068665 | 60.2417 | -62.3337 | 60.3745 | -62.2879 | -62.384 | -62.3703 | -0.064087 | -0.045776 | 0.013733 | 0.2243 | -0.21515 | -0.23346 | -0.15106 | -0.16937 | 0.004578 | -0.073242 | 0.05951 | 0.050354 | -0.032043 | -0.045776 | -0.036621 | -0.050354 | 0.28839 | 122.731 | 0.045776 | 122.7081 | 122.6715 | 122.5754 | 122.6074 | 122.58 | -122.7173 | -122.6486 | 122.6669 | 122.7127 | 62.3108 | 62.4069
48.7344 | 122.8088 | -62.3245 | 60.3195 | -0.0051118 | -0.025265 | -0.024537 | 0.06608 | -0.036638 | -0.048245 | -0.040392 | 0.00094606 | -0.019467 | 0.055345 | 0.050962 | -0.21445 | -0.016205 | -0.017271 | -0.022888 | 60.2829 | -62.4115 | 60.3058 | -62.1277 | -62.5763 | -62.5671 | 0.050354 | 60.2325 | -62.3474 | 60.3745 | -62.2604 | -62.3886 | -62.384 | -0.086975 | -0.036621 | -0.013733 | 0.19684 | -0.24262 | -0.25177 | -0.15564 | -0.16479 | -0.022888 | -0.086975 | 0.054932 | 0.064087 | -0.059509 | -0.064087 | -0.036621 | -0.041199 | 0.28381 | 122.7173 | 0.086975 | 122.7219 | 122.6944 | 122.58 | 122.6074 | 122.5571 | -122.731 | -122.6669 | 122.6303 | 122.699 | 62.3016 | 62.3749
50.4531 | 122.8134 | -62.3245 | 60.3241 | 0.0025177 | -0.029324 | -0.025818 | 0.065012 | -0.03557 | -0.049099 | -0.040392 | 0.00094606 | -0.021604 | 0.055773 | 0.038572 | -0.21167 | -0.017273 | -0.021758 | 0.004578 | 60.2097 | -62.3795 | 60.3607 | -62.0636 | -62.5259 | -62.4939 | 0.10529 | 60.2188 | -62.3428 | 60.3516 | -62.2559 | -62.3749 | -62.3749 | -0.054932 | -0.11444 | 0.036621 | 0.26092 | -0.16937 | -0.20142 | -0.11444 | -0.14648 | -0.01831 | -0.10529 | 0.027465 | 0.068665 | -0.050354 | -0.050354 | -0.032044 | -0.032044 | 0.31586 | 122.7402 | 0.086975 | 122.6944 | 122.5891 | 122.5616 | 122.5342 | 122.5433 | -122.7036 | -122.6669 | 122.6852 | 122.6761 | 62.3291 | 62.4298
52.2188 | 122.8592 | -62.3199 | 60.26 | -0.0051118 | -0.028897 | -0.026246 | 0.064157 | -0.033861 | -0.046963 | -0.037828 | -0.0021057 | -0.02139 | 0.055986 | 0.043485 | -0.21381 | -0.01706 | -0.022612 | -0.1236 | 60.2051 | -62.439 | 60.3058 | -62.1231 | -62.5717 | -62.5442 | 0.004578 | 60.1913 | -62.3611 | 60.3745 | -62.2375 | -62.3474 | -62.3383 | -0.11902 | -0.054932 | 0.045776 | 0.19684 | -0.2243 | -0.25177 | -0.10528 | -0.13275 | -0.041199 | -0.068665 | 0.11444 | 0.082397 | -0.018311 | -0.027466 | 0.022888 | 0.013733 | 0.31586 | 122.7448 | 0.1236 | 122.7356 | 122.644 | 122.5525 | 122.525 | 122.5113 | -122.699 | -122.6212 | 122.6257 | 122.6944 | 62.1964 | 62.3245
53.9844 | 122.9004 | -62.2925 | 60.2783 | -0.012741 | -0.028042 | -0.026032 | 0.063944 | -0.03258 | -0.047604 | -0.041674 | -0.0021057 | -0.023099 | 0.055132 | 0.051176 | -0.21595 | -0.018769 | -0.021544 | -0.009155 | 60.228 | -62.352 | 60.3928 | -61.9995 | -62.471 | -62.471 | 0.17395 | 60.1776 | -62.3245 | 60.4248 | -62.1689 | -62.2742 | -62.2971 | -0.05951 | -0.050354 | 0.11444 | 0.29297 | -0.17853 | -0.17853 | -0.11902 | -0.11902 | -0.032044 | -0.10071 | 0.14648 | 0.1236 | -0.004578 | 0.01831 | 0.027466 | 0.050354 | 0.35248 | 122.7448 | 0.15564 | 122.7493 | 122.58 | 122.5021 | 122.5204 | 122.4701 | -122.6303 | -122.6028 | 122.6852 | 122.7173 | 62.2833 | 62.4664
55.75 | 122.8134 | -62.3108 | 60.3149 | -0.0051118 | -0.027829 | -0.026032 | 0.065439 | -0.031298 | -0.048245 | -0.042101 | -0.0082091 | -0.018827 | 0.058123 | 0.05438 | -0.21296 | -0.018769 | -0.022398 | -0.022888 | 60.2463 | -62.4115 | 60.3149 | -62.114 | -62.5763 | -62.5671 | 0.073242 | 60.2325 | -62.3474 | 60.3882 | -62.2375 | -62.384 | -62.3566 | -0.10071 | -0.068664 | 0 | 0.19684 | -0.25635 | -0.2655 | -0.15564 | -0.16479 | -0.036621 | -0.082397 | 0.073243 | 0.073242 | -0.045776 | -0.073242 | -0.009155 | -0.036621 | 0.29755 | 122.7264 | 0.10986 | 122.7356 | 122.6578 | 122.58 | 122.5571 | 122.5433 | -122.7264 | -122.6624 | 122.6257 | 122.699 | 62.2879 | 62.384
57.5312 | 122.8043 | -62.3062 | 60.2692 | -0.012741 | -0.025692 | -0.024537 | 0.067148 | -0.03258 | -0.04974 | -0.041246 | -0.0051575 | -0.02139 | 0.056841 | 0.04434 | -0.21552 | -0.020478 | -0.022398 | -0.022888 | 60.2921 | -62.4069 | 60.3195 | -62.1094 | -62.5671 | -62.5534 | 0.045776 | 60.2509 | -62.3703 | 60.3653 | -62.2833 | -62.4069 | -62.3703 | -0.10071 | 0.022888 | 0.050354 | 0.19684 | -0.24719 | -0.26093 | -0.14649 | -0.16022 | -0.064087 | -0.018311 | 0.09613 | 0.022888 | -0.064087 | -0.10071 | 0 | -0.036621 | 0.29755 | 122.7264 | 0.086975 | 122.7356 | 122.699 | 122.6212 | 122.5983 | 122.5571 | -122.6761 | -122.6395 | 122.6257 | 122.6715 | 62.2833 | 62.352
59.2344 | 122.818 | -62.3199 | 60.2509 | -0.0051118 | -0.028897 | -0.023041 | 0.064585 | -0.028307 | -0.050595 | -0.040178 | 0.00094606 | -0.021817 | 0.056841 | 0.045408 | -0.21509 | -0.019623 | -0.021971 | -0.16022 | 60.2463 | -62.4573 | 60.2325 | -62.1872 | -62.6633 | -62.6266 | -0.068665 | 60.2051 | -62.3611 | 60.3241 | -62.3245 | -62.4435 | -62.3932 | -0.13733 | -0.004577 | -0.01831 | 0.13275 | -0.3067 | -0.34332 | -0.16937 | -0.20599 | -0.041199 | -0.045776 | 0.073243 | -0.004578 | -0.073242 | -0.1236 | -0.032043 | -0.082397 | 0.27008 | 122.6898 | 0.036621 | 122.6852 | 122.7036 | 122.5662 | 122.5662 | 122.525 | -122.7081 | -122.612 | 122.5525 | 122.644 | 62.1597 | 62.2513
61.0312 | 122.7585 | -62.3611 | 60.3149 | -0.012741 | -0.025265 | -0.024537 | 0.067362 | -0.03322 | -0.048245 | -0.039324 | 0.00094606 | -0.020963 | 0.055132 | 0.051816 | -0.21424 | -0.016846 | -0.023467 | -0.10529 | 60.3012 | -62.439 | 60.2371 | -62.2101 | -62.6816 | -62.6404 | -0.10986 | 60.2142 | -62.3932 | 60.2875 | -62.3795 | -62.5031 | -62.4435 | -0.07782 | -0.013733 | -0.077819 | 0.15106 | -0.27924 | -0.32043 | -0.20142 | -0.24261 | -0.032043 | -0.10071 | -0.027465 | -0.018311 | -0.082397 | -0.14191 | -0.050354 | -0.10986 | 0.22888 | 122.6761 | 0.013732 | 122.6807 | 122.7402 | 122.6074 | 122.6624 | 122.5754 | -122.7539 | -122.7081 | 122.5983 | 122.6486 | 62.2559 | 62.2513
62.8281 | 122.8226 | -62.3154 | 60.3058 | 0.0025177 | -0.026547 | -0.025391 | 0.065225 | -0.029589 | -0.047817 | -0.038256 | 0.00094606 | -0.01904 | 0.054064 | 0.053525 | -0.2136 | -0.019196 | -0.01834 | -0.013733 | 60.2737 | -62.4252 | 60.3104 | -62.1048 | -62.5671 | -62.5488 | 0.082397 | 60.228 | -62.3108 | 60.3653 | -62.2375 | -62.3749 | -62.352 | -0.10986 | -0.032043 | 0.004578 | 0.21057 | -0.23346 | -0.25177 | -0.1236 | -0.14191 | 0.004578 | -0.07782 | 0.059509 | 0.07782 | -0.036621 | -0.059509 | -0.041199 | -0.064087 | 0.32044 | 122.7356 | 0.073242 | 122.6761 | 122.699 | 122.5388 | 122.5891 | 122.5433 | -122.731 | -122.6166 | 122.6257 | 122.6807 | 62.3016 | 62.3978
64.5469 | 122.7631 | -62.3291 | 60.3058 | 0.0025177 | -0.022488 | -0.025391 | 0.064798 | -0.029589 | -0.049526 | -0.040178 | -0.0021057 | -0.020749 | 0.058336 | 0.047117 | -0.21488 | -0.01941 | -0.020903 | -0.050354 | 60.2829 | -62.4069 | 60.2829 | -62.1552 | -62.6495 | -62.59 | -0.009155 | 60.2234 | -62.3383 | 60.3195 | -62.3245 | -62.4527 | -62.4115 | -0.077819 | -0.022888 | -0.022888 | 0.17395 | -0.26093 | -0.32043 | -0.18311 | -0.24262 | -0.009155 | -0.082397 | 0.013733 | 0.004578 | -0.082397 | -0.1236 | -0.073242 | -0.11444 | 0.25177 | 122.6898 | 0.013733 | 122.6578 | 122.6898 | 122.5616 | 122.612 | 122.5525 | -122.7127 | -122.644 | 122.612 | 122.6486 | 62.2787 | 62.3199
66.3281 | 122.8363 | -62.3016 | 60.3012 | -0.0051118 | -0.028683 | -0.024964 | 0.062662 | -0.03023 | -0.049526 | -0.036974 | -0.0021057 | -0.020749 | 0.055986 | 0.04968 | -0.21402 | -0.020051 | -0.016203 | 0 | 60.2188 | -62.3978 | 60.3607 | -62.0544 | -62.4939 | -62.4847 | 0.13733 | 60.2188 | -62.3016 | 60.3882 | -62.2101 | -62.3245 | -62.3337 | -0.09613 | -0.082397 | 0.05951 | 0.24719 | -0.1831 | -0.19226 | -0.086975 | -0.09613 | 0 | -0.082397 | 0.086976 | 0.091553 | -0.032043 | -0.022888 | -0.032043 | -0.022888 | 0.34332 | 122.7585 | 0.091553 | 122.6898 | 122.6166 | 122.5204 | 122.5204 | 122.5204 | -122.699 | -122.6028 | 122.6624 | 122.6898 | 62.3016 | 62.439
68.1094 | 122.8226 | -62.3108 | 60.2966 | -0.0051118 | -0.026547 | -0.024109 | 0.065012 | -0.028948 | -0.047817 | -0.03911 | 0.00094606 | -0.019467 | 0.0562 | 0.048398 | -0.21402 | -0.018342 | -0.020689 | -0.027466 | 60.26 | -62.4069 | 60.3104 | -62.1002 | -62.5671 | -62.5442 | 0.07782 | 60.2097 | -62.3245 | 60.379 | -62.2513 | -62.3795 | -62.3428 | -0.09613 | -0.036621 | 0.013733 | 0.21057 | -0.23346 | -0.25635 | -0.13733 | -0.16022 | -0.013733 | -0.086975 | 0.082397 | 0.059509 | -0.032043 | -0.068665 | -0.01831 | -0.054932 | 0.3067 | 122.7173 | 0.073242 | 122.7036 | 122.6669 | 122.5342 | 122.5708 | 122.5204 | -122.7036 | -122.6212 | 122.6212 | 122.6898 | 62.2833 | 62.3886
69.8125 | 122.85 | -62.3199 | 60.2325 | -0.012741 | -0.02377 | -0.025177 | 0.061808 | -0.030443 | -0.046322 | -0.042955 | -0.0021057 | -0.02139 | 0.056841 | 0.04498 | -0.21573 | -0.018342 | -0.020689 | -0.10071 | 60.2097 | -62.3886 | 60.3378 | -62.0499 | -62.5488 | -62.5031 | 0.054932 | 60.1501 | -62.352 | 60.4065 | -62.2284 | -62.3383 | -62.3337 | -0.068665 | -0.022888 | 0.10529 | 0.27008 | -0.18311 | -0.22888 | -0.11444 | -0.16022 | -0.032044 | -0.082398 | 0.17395 | 0.091552 | -0.013733 | -0.018311 | 0.018311 | 0.013733 | 0.33874 | 122.7264 | 0.1236 | 122.7585 | 122.5983 | 122.5021 | 122.5296 | 122.4701 | -122.6212 | -122.5845 | 122.6578 | 122.7264 | 62.2192 | 62.3749
71.5938 | 122.8409 | -62.3428 | 60.2646 | 0.0025177 | -0.029538 | -0.023896 | 0.061808 | -0.030871 | -0.050167 | -0.040605 | 0.00094606 | -0.023099 | 0.056627 | 0.041776 | -0.21338 | -0.017273 | -0.021544 | -0.12817 | 60.2142 | -62.4207 | 60.2783 | -62.1002 | -62.5763 | -62.5305 | -0.004578 | 60.1639 | -62.3474 | 60.3516 | -62.2559 | -62.3703 | -62.352 | -0.07782 | -0.050354 | 0.013733 | 0.24261 | -0.18768 | -0.23346 | -0.10986 | -0.15564 | -0.004578 | -0.10071 | 0.086975 | 0.086975 | -0.009156 | -0.027466 | -0.004578 | -0.022888 | 0.32043 | 122.699 | 0.091553 | 122.699 | 122.6349 | 122.5113 | 122.5571 | 122.5067 | -122.6852 | -122.612 | 122.6212 | 122.6944 | 62.2147 | 62.3383
73.375 | 122.8912 | -62.2833 | 60.2737 | 0.0025177 | -0.027615 | -0.024537 | 0.06373 | -0.032366 | -0.050381 | -0.038896 | 0.0039979 | -0.02139 | 0.053209 | 0.046049 | -0.21467 | -0.018555 | -0.021971 | -0.004578 | 60.2097 | -62.3795 | 60.3882 | -62.0041 | -62.471 | -62.4481 | 0.17395 | 60.2051 | -62.3016 | 60.4248 | -62.1597 | -62.2787 | -62.2971 | -0.096131 | -0.064087 | 0.11444 | 0.27924 | -0.1648 | -0.18768 | -0.068664 | -0.091552 | -0.018311 | -0.068665 | 0.15106 | 0.1236 | -0.013733 | 0.004577 | 0.004578 | 0.022888 | 0.37537 | 122.7676 | 0.14191 | 122.7264 | 122.5891 | 122.5067 | 122.493 | 122.4884 | -122.6532 | -122.5754 | 122.6715 | 122.7081 | 62.2787 | 62.4573
75.1562 | 122.8638 | -62.3108 | 60.2463 | -0.0051118 | -0.024411 | -0.025818 | 0.065866 | -0.028948 | -0.048031 | -0.041887 | 0.0039979 | -0.021176 | 0.055773 | 0.047544 | -0.21424 | -0.017487 | -0.02133 | -0.15106 | 60.2325 | -62.4435 | 60.2737 | -62.1506 | -62.6038 | -62.5671 | -0.004578 | 60.173 | -62.3749 | 60.4019 | -62.2467 | -62.3566 | -62.3062 | -0.13275 | -0.013733 | 0.027466 | 0.16022 | -0.25635 | -0.29297 | -0.1236 | -0.16022 | -0.064087 | -0.073242 | 0.15564 | 0.064087 | 0.004578 | -0.045776 | 0.068665 | 0.018311 | 0.29297 | 122.7173 | 0.12817 | 122.7768 | 122.6761 | 122.5479 | 122.5433 | 122.4838 | -122.6898 | -122.6212 | 122.5845 | 122.7127 | 62.1597 | 62.3062
76.875 | 122.7997 | -62.3154 | 60.3149 | -0.0051118 | -0.028897 | -0.024323 | 0.065866 | -0.03322 | -0.04739 | -0.03911 | -0.0021057 | -0.020108 | 0.054705 | 0.053525 | -0.21744 | -0.014924 | -0.021544 | -0.041199 | 60.2554 | -62.439 | 60.2692 | -62.1597 | -62.5763 | -62.5671 | 0.027466 | 60.2509 | -62.3108 | 60.3333 | -62.265 | -62.3978 | -62.3611 | -0.1236 | -0.059509 | -0.045776 | 0.15564 | -0.25177 | -0.26093 | -0.12817 | -0.13733 | 0.004578 | -0.064087 | 0.018311 | 0.050354 | -0.045776 | -0.082397 | -0.050354 | -0.086975 | 0.27924 | 122.7081 | 0.045776 | 122.644 | 122.6944 | 122.5616 | 122.5708 | 122.5662 | -122.7539 | -122.6257 | 122.5845 | 122.6486 | 62.2742 | 62.3428
78.6562 | 122.8546 | -62.3016 | 60.2875 | -0.0051118 | -0.028897 | -0.026459 | 0.063303 | -0.031939 | -0.047604 | -0.04146 | 0.0039979 | -0.021817 | 0.055986 | 0.051176 | -0.21253 | -0.018982 | -0.023253 | -0.13733 | 60.2051 | -62.4115 | 60.2783 | -62.1094 | -62.5809 | -62.5488 | 0.009155 | 60.1685 | -62.3611 | 60.3516 | -62.265 | -62.3703 | -62.3566 | -0.10986 | -0.082398 | -0.009156 | 0.19226 | -0.24719 | -0.27924 | -0.13733 | -0.16937 | -0.059509 | -0.11902 | 0.064086 | 0.036621 | -0.054931 | -0.068664 | 0.004578 | -0.009155 | 0.30212 | 122.6898 | 0.09613 | 122.7127 | 122.6166 | 122.5296 | 122.5067 | 122.4701 | -122.699 | -122.6486 | 122.58 | 122.6532 | 62.1643 | 62.3108
80.4375 | 122.8958 | -62.2787 | 60.2463 | -0.0051118 | -0.029538 | -0.023682 | 0.062448 | -0.036425 | -0.051876 | -0.038896 | 0.0039979 | -0.023099 | 0.055345 | 0.043058 | -0.21531 | -0.019196 | -0.024962 | -0.009155 | 60.2142 | -62.384 | 60.3745 | -61.9949 | -62.471 | -62.4481 | 0.19684 | 60.1776 | -62.3199 | 60.4111 | -62.1689 | -62.2604 | -62.2787 | -0.10529 | -0.032044 | 0.12817 | 0.28381 | -0.16937 | -0.19226 | -0.064087 | -0.086975 | -0.041198 | -0.068665 | 0.16479 | 0.10986 | 0 | 0.018311 | 0.041198 | 0.059509 | 0.3891 | 122.7585 | 0.15106 | 122.731 | 122.5983 | 122.4976 | 122.493 | 122.4564 | -122.6303 | -122.5662 | 122.6532 | 122.6898 | 62.2696 | 62.4756
82.1875 | 122.7905 | -62.3245 | 60.2783 | -0.0051118 | -0.027188 | -0.023896 | 0.066721 | -0.03557 | -0.049313 | -0.039751 | -0.0051575 | -0.019895 | 0.055132 | 0.050107 | -0.21338 | -0.018769 | -0.024962 | -0.018311 | 60.2554 | -62.4115 | 60.3149 | -62.1002 | -62.558 | -62.5534 | 0.082397 | 60.228 | -62.3383 | 60.3653 | -62.2375 | -62.3749 | -62.3337 | -0.086975 | -0.022888 | 0.036621 | 0.2243 | -0.22888 | -0.23346 | -0.14191 | -0.14648 | -0.013733 | -0.050354 | 0.086975 | 0.086975 | -0.009155 | -0.050354 | 0.004578 | -0.036621 | 0.31128 | 122.7264 | 0.10071 | 122.7036 | 122.6669 | 122.5662 | 122.58 | 122.5525 | -122.6898 | -122.6166 | 122.6395 | 122.6898 | 62.3062 | 62.4069
83.9219 | 122.7448 | -62.352 | 60.2829 | -0.0051118 | -0.024838 | -0.025605 | 0.066507 | -0.028948 | -0.048245 | -0.038469 | 0.0070497 | -0.01904 | 0.056414 | 0.053953 | -0.21573 | -0.016846 | -0.020689 | -0.1236 | 60.2692 | -62.439 | 60.2234 | -62.2147 | -62.6678 | -62.6266 | -0.10529 | 60.2097 | -62.3703 | 60.2966 | -62.352 | -62.4802 | -62.4069 | -0.086975 | -0.013733 | -0.059509 | 0.13733 | -0.27466 | -0.31586 | -0.18768 | -0.22888 | -0.01831 | -0.073242 | 0.013733 | 0 | -0.054931 | -0.12817 | -0.036621 | -0.10986 | 0.2243 | 122.6624 | 0.01831 | 122.6669 | 122.7081 | 122.58 | 122.6212 | 122.5616 | -122.7219 | -122.6532 | 122.5754 | 122.6486 | 62.2284 | 62.2467
85.7031 | 122.7997 | -62.3062 | 60.2966 | 0.010147 | -0.026333 | -0.023041 | 0.063516 | -0.029802 | -0.046963 | -0.03911 | -0.0021057 | -0.020963 | 0.057482 | 0.05438 | -0.21338 | -0.017273 | -0.023467 | -0.013733 | 60.2875 | -62.3978 | 60.3241 | -62.0911 | -62.5442 | -62.5351 | 0.073242 | 60.2234 | -62.352 | 60.379 | -62.2559 | -62.3886 | -62.3428 | -0.091553 | -0.009155 | 0.027466 | 0.21515 | -0.22888 | -0.23804 | -0.13733 | -0.14648 | -0.045777 | -0.073242 | 0.082397 | 0.050354 | -0.036621 | -0.082398 | 0.009156 | -0.036621 | 0.3067 | 122.7219 | 0.096131 | 122.731 | 122.6852 | 122.5754 | 122.5937 | 122.5296 | -122.6944 | -122.6486 | 122.6303 | 122.6852 | 62.2925 | 62.3795
87.4844 | 122.8317 | -62.2787 | 60.2966 | -0.0051118 | -0.029324 | -0.024964 | 0.060526 | -0.029589 | -0.047604 | -0.038256 | -0.0021057 | -0.022245 | 0.055132 | 0.045621 | -0.2136 | -0.018128 | -0.022612 | 0.009155 | 60.2234 | -62.4023 | 60.347 | -62.0407 | -62.4847 | -62.4664 | 0.12817 | 60.1822 | -62.3383 | 60.379 | -62.1872 | -62.3108 | -62.3016 | -0.1236 | -0.073242 | 0.050354 | 0.23804 | -0.18768 | -0.20599 | -0.064087 | -0.082397 | -0.059509 | -0.11444 | 0.082397 | 0.091553 | -0.022888 | -0.032043 | 0.036621 | 0.027466 | 0.36163 | 122.7493 | 0.15106 | 122.7173 | 122.6257 | 122.5204 | 122.5021 | 122.4609 | -122.699 | -122.6349 | 122.6257 | 122.6578 | 62.2879 | 62.4069
89.25 | 122.8775 | -62.2879 | 60.2783 | -0.012741 | -0.025906 | -0.025391 | 0.063516 | -0.033434 | -0.048031 | -0.041887 | -0.0021057 | -0.020963 | 0.056414 | 0.046903 | -0.21488 | -0.017273 | -0.022185 | 0.009155 | 60.2188 | -62.3795 | 60.3745 | -62.0087 | -62.4664 | -62.4435 | 0.17853 | 60.1685 | -62.3154 | 60.4111 | -62.1552 | -62.265 | -62.2787 | -0.091553 | -0.059509 | 0.096131 | 0.27924 | -0.15564 | -0.17853 | -0.064086 | -0.086975 | -0.027466 | -0.10986 | 0.13275 | 0.13275 | 0.009155 | 0.022888 | 0.036621 | 0.050354 | 0.37079 | 122.7539 | 0.16022 | 122.7264 | 122.5983 | 122.4838 | 122.5067 | 122.4564 | -122.6578 | -122.5937 | 122.6624 | 122.699 | 62.2971 | 62.4664
90.9531 | 122.8043 | -62.2925 | 60.3058 | 0.010147 | -0.028469 | -0.025177 | 0.065225 | -0.033434 | -0.046322 | -0.041246 | -0.0021057 | -0.021176 | 0.057695 | 0.048826 | -0.21402 | -0.017701 | -0.021544 | -0.009155 | 60.2692 | -62.4298 | 60.3012 | -62.0911 | -62.5671 | -62.5397 | 0.086975 | 60.2417 | -62.3108 | 60.3699 | -62.2284 | -62.3657 | -62.3383 | -0.13733 | -0.036621 | -0.004578 | 0.20142 | -0.24719 | -0.27466 | -0.10986 | -0.13733 | -0.018311 | -0.064087 | 0.064087 | 0.064086 | -0.045777 | -0.073243 | -0.027466 | -0.054932 | 0.33875 | 122.731 | 0.082397 | 122.6807 | 122.699 | 122.5525 | 122.5616 | 122.5342 | -122.7356 | -122.6166 | 122.5937 | 122.6624 | 62.2833 | 62.3795
92.7188 | 122.7493 | -62.3108 | 60.3149 | 0.0025177 | -0.025906 | -0.023896 | 0.065439 | -0.028734 | -0.048672 | -0.039537 | -0.0021057 | -0.020322 | 0.053636 | 0.049039 | -0.21253 | -0.01941 | -0.020476 | -0.050354 | 60.2737 | -62.384 | 60.2554 | -62.1414 | -62.5717 | -62.5717 | 0.009155 | 60.2371 | -62.3474 | 60.3058 | -62.2925 | -62.4115 | -62.384 | -0.073242 | -0.041198 | -0.059509 | 0.16937 | -0.26093 | -0.26093 | -0.18768 | -0.18768 | -0.036621 | -0.077819 | -0.009155 | 0.018311 | -0.073242 | -0.10071 | -0.036621 | -0.064087 | 0.24262 | 122.6395 | 0.054932 | 122.6532 | 122.6578 | 122.5845 | 122.5845 | 122.5479 | -122.699 | -122.6624 | 122.5662 | 122.6166 | 62.2604 | 62.3199
94.5 | 122.7448 | -62.3383 | 60.2646 | -0.0051118 | -0.025051 | -0.025177 | 0.064798 | -0.028307 | -0.047817 | -0.040392 | -0.0051575 | -0.019254 | 0.055986 | 0.053098 | -0.21232 | -0.018128 | -0.019621 | -0.13733 | 60.2692 | -62.4298 | 60.2051 | -62.2147 | -62.6724 | -62.6129 | -0.091553 | 60.2005 | -62.3383 | 60.2875 | -62.3291 | -62.4573 | -62.3886 | -0.091553 | 0.004578 | -0.059509 | 0.1236 | -0.27466 | -0.33417 | -0.1831 | -0.24261 | 0 | -0.064087 | 0.022889 | 0.009155 | -0.050354 | -0.11902 | -0.050354 | -0.11902 | 0.21515 | 122.6349 | 0.009155 | 122.6257 | 122.699 | 122.5388 | 122.6074 | 122.5388 | -122.6944 | -122.6028 | 122.5433 | 122.6257 | 62.2009 | 62.2467
96.2188 | 122.7356 | -62.3062 | 60.2966 | 0.0025177 | -0.024197 | -0.026032 | 0.065653 | -0.027239 | -0.047604 | -0.038896 | 0.0039979 | -0.019681 | 0.055345 | 0.056303 | -0.21424 | -0.018769 | -0.022612 | -0.064087 | 60.2509 | -62.4252 | 60.26 | -62.1277 | -62.6083 | -62.5763 | -0.013733 | 60.1913 | -62.3428 | 60.2921 | -62.3108 | -62.4344 | -62.3932 | -0.11902 | -0.045777 | -0.036621 | 0.17853 | -0.27008 | -0.30212 | -0.15106 | -0.1831 | -0.036621 | -0.10529 | -0.004578 | -0.004578 | -0.086975 | -0.12817 | -0.050354 | -0.091553 | 0.29755 | 122.6852 | 0.032043 | 122.6349 | 122.6761 | 122.5342 | 122.5571 | 122.4976 | -122.7219 | -122.6395 | 122.5662 | 122.5983 | 62.2421 | 62.2925
98.0156 | 122.7676 | -62.2879 | 60.3149 | -0.0051118 | -0.029538 | -0.024964 | 0.062662 | -0.033861 | -0.049099 | -0.041246 | -0.0051575 | -0.022458 | 0.057054 | 0.055021 | -0.21274 | -0.019837 | -0.021117 | 0.009155 | 60.2737 | -62.3886 | 60.3241 | -62.0544 | -62.5214 | -62.4985 | 0.09613 | 60.2005 | -62.3199 | 60.3195 | -62.265 | -62.3703 | -62.3795 | -0.10071 | -0.041198 | 0.009156 | 0.23346 | -0.21057 | -0.23346 | -0.10986 | -0.13275 | -0.032043 | -0.11444 | 0.004578 | 0.022888 | -0.091553 | -0.082397 | -0.05951 | -0.050354 | 0.33417 | 122.7127 | 0.054931 | 122.6395 | 122.6624 | 122.5204 | 122.5616 | 122.4884 | -122.7036 | -122.6349 | 122.612 | 122.6074 | 62.2971 | 62.384
99.7344 | 122.7493 | -62.3245 | 60.2829 | -0.0051118 | -0.025692 | -0.023255 | 0.066721 | -0.03023 | -0.048031 | -0.038042 | 0.0039979 | -0.018399 | 0.054277 | 0.044553 | -0.21509 | -0.018555 | -0.022398 | -0.064087 | 60.2783 | -62.3978 | 60.2554 | -62.1323 | -62.5946 | -62.5763 | 0.004578 | 60.2051 | -62.3291 | 60.3058 | -62.3199 | -62.4435 | -62.3886 | -0.073242 | -0.004578 | -0.027466 | 0.19226 | -0.25177 | -0.27008 | -0.17853 | -0.19684 | -0.004578 | -0.07782 | 0.022888 | 0.004578 | -0.064087 | -0.11902 | -0.059509 | -0.11444 | 0.2655 | 122.6532 | 0.009156 | 122.6349 | 122.6761 | 122.5342 | 122.6028 | 122.5296 | -122.6807 | -122.612 | 122.58 | 122.6303 | 62.2604 | 62.3291
101.5156 | 122.8271 | -62.3062 | 60.2554 | 0.0025177 | -0.028683 | -0.026459 | 0.063089 | -0.029589 | -0.048672 | -0.035692 | -0.0051575 | -0.022885 | 0.056414 | 0.042844 | -0.21488 | -0.020691 | -0.023894 | -0.11902 | 60.2234 | -62.4207 | 60.2737 | -62.0911 | -62.5717 | -62.5351 | 0 | 60.1639 | -62.3337 | 60.3333 | -62.2421 | -62.3428 | -62.3337 | -0.11444 | -0.032043 | 0.018311 | 0.21515 | -0.22888 | -0.2655 | -0.11444 | -0.15106 | -0.027466 | -0.091553 | 0.07782 | 0.064087 | -0.027466 | -0.036621 | 0 | -0.009155 | 0.32959 | 122.6944 | 0.091553 | 122.6669 | 122.644 | 122.4976 | 122.5296 | 122.4701 | -122.6761 | -122.5891 | 122.58 | 122.6395 | 62.1872 | 62.3062
103.2812 | 122.7539 | -62.2925 | 60.3287 | 0.0025177 | -0.027401 | -0.024323 | 0.065866 | -0.029802 | -0.045254 | -0.038256 | 0.00094606 | -0.020108 | 0.055773 | 0.045835 | -0.21659 | -0.018769 | -0.021758 | -0.018311 | 60.3104 | -62.384 | 60.2509 | -62.1597 | -62.59 | -62.5763 | 0.027466 | 60.2417 | -62.3383 | 60.3149 | -62.2833 | -62.4069 | -62.3703 | -0.091553 | -0.01831 | -0.07782 | 0.13275 | -0.28381 | -0.29755 | -0.19226 | -0.20599 | -0.045777 | -0.086975 | -0.013733 | 0.009155 | -0.07782 | -0.11444 | -0.032043 | -0.068664 | 0.2243 | 122.6349 | 0.054932 | 122.6532 | 122.6944 | 122.58 | 122.6028 | 122.5342 | -122.7127 | -122.6669 | 122.5433 | 122.6074 | 62.2742 | 62.3199
104.9844 | 122.7676 | -62.3062 | 60.2921 | 0.0025177 | -0.02676 | -0.025177 | 0.065866 | -0.030871 | -0.046963 | -0.037187 | -0.0021057 | -0.020108 | 0.056841 | 0.052244 | -0.2136 | -0.01706 | -0.022612 | -0.022888 | 60.2829 | -62.4069 | 60.2783 | -62.1277 | -62.5488 | -62.5488 | 0.036621 | 60.2234 | -62.3337 | 60.3424 | -62.2421 | -62.384 | -62.3428 | -0.10071 | -0.009155 | -0.013733 | 0.17853 | -0.24262 | -0.24262 | -0.14191 | -0.14191 | -0.027466 | -0.068664 | 0.050354 | 0.064087 | -0.036621 | -0.07782 | -0.009155 | -0.050354 | 0.27923 | 122.6852 | 0.091553 | 122.6761 | 122.6898 | 122.5571 | 122.5891 | 122.5296 | -122.699 | -122.6257 | 122.5845 | 122.6486 | 62.2833 | 62.3428
106.7812 | 122.7859 | -62.2971 | 60.3012 | 0.0025177 | -0.025479 | -0.024109 | 0.065225 | -0.028948 | -0.048245 | -0.038683 | -0.0021057 | -0.020536 | 0.055559 | 0.050748 | -0.21445 | -0.018982 | -0.024321 | -0.009155 | 60.2783 | -62.3978 | 60.2966 | -62.0865 | -62.5626 | -62.5168 | 0.07782 | 60.2371 | -62.3337 | 60.3561 | -62.233 | -62.3657 | -62.3245 | -0.10071 | -0.022888 | -0.004577 | 0.21057 | -0.21973 | -0.2655 | -0.11902 | -0.1648 | -0.036621 | -0.064086 | 0.054932 | 0.064087 | -0.027466 | -0.068665 | 0.009155 | -0.032044 | 0.31128 | 122.6944 | 0.10071 | 122.6898 | 122.6761 | 122.5708 | 122.5754 | 122.5342 | -122.699 | -122.6349 | 122.5937 | 122.6532 | 62.2879 | 62.3749
108.5781 | 122.8729 | -62.2879 | 60.2509 | 0.0025177 | -0.030178 | -0.024537 | 0.060739 | -0.029162 | -0.048245 | -0.037401 | -0.0021057 | -0.022458 | 0.057268 | 0.04498 | -0.21402 | -0.019196 | -0.028594 | -0.009155 | 60.2234 | -62.3703 | 60.3424 | -61.9904 | -62.4527 | -62.4573 | 0.17395 | 60.1685 | -62.3108 | 60.3928 | -62.146 | -62.2696 | -62.2696 | -0.082397 | -0.027465 | 0.091553 | 0.29755 | -0.16937 | -0.16479 | -0.086975 | -0.082398 | -0.022888 | -0.082397 | 0.14191 | 0.14191 | 0.018311 | 0.018311 | 0.041199 | 0.041199 | 0.37994 | 122.7127 | 0.1648 | 122.7036 | 122.5937 | 122.4792 | 122.5113 | 122.4564 | -122.6212 | -122.5616 | 122.6303 | 122.6807 | 62.2787 | 62.4619
110.2969 | 122.8363 | -62.3154 | 60.2371 | 0.0025177 | -0.024838 | -0.021973 | 0.063944 | -0.027025 | -0.048672 | -0.039537 | 0.00094606 | -0.021817 | 0.055345 | 0.053739 | -0.21488 | -0.017914 | -0.025816 | -0.13733 | 60.2417 | -62.3886 | 60.2371 | -62.1323 | -62.6312 | -62.5671 | -0.009155 | 60.1685 | -62.352 | 60.3745 | -62.2284 | -62.3703 | -62.3199 | -0.073242 | 0.004577 | 0 | 0.18311 | -0.25177 | -0.31586 | -0.17853 | -0.24262 | -0.036621 | -0.068665 | 0.13733 | 0.086975 | -0.004577 | -0.054931 | 0.032044 | -0.01831 | 0.25635 | 122.6257 | 0.1236 | 122.7264 | 122.6303 | 122.5204 | 122.5571 | 122.4838 | -122.6257 | -122.5891 | 122.5525 | 122.6898 | 62.178 | 62.3062
112.0469 | 122.85 | -62.3199 | 60.2371 | -0.0051118 | -0.02676 | -0.021973 | 0.062662 | -0.033007 | -0.046963 | -0.039537 | 0.00094606 | -0.021176 | 0.0562 | 0.043699 | -0.21488 | -0.021546 | -0.02133 | -0.086975 | 60.2325 | -62.4069 | 60.2783 | -62.0819 | -62.5534 | -62.5031 | 0.054932 | 60.1639 | -62.3291 | 60.3745 | -62.2101 | -62.3108 | -62.3062 | -0.086975 | -0.004578 | 0.041198 | 0.23804 | -0.18311 | -0.23346 | -0.096131 | -0.14649 | -0.009156 | -0.073243 | 0.13733 | 0.10986 | 0.013733 | 0.009155 | 0.022889 | 0.018311 | 0.32501 | 122.6852 | 0.11902 | 122.7036 | 122.6395 | 122.493 | 122.5525 | 122.4838 | -122.644 | -122.5662 | 122.5983 | 122.6944 | 62.233 | 62.3749
113.7656 | 122.7585 | -62.3108 | 60.2829 | 0.0025177 | -0.024197 | -0.024537 | 0.066721 | -0.027239 | -0.046749 | -0.038683 | -0.0021057 | -0.018827 | 0.0562 | 0.050321 | -0.21637 | -0.016633 | -0.02133 | -0.013733 | 60.2692 | -62.3795 | 60.2966 | -62.1094 | -62.5626 | -62.5442 | 0.045776 | 60.2142 | -62.3291 | 60.3424 | -62.2696 | -62.4069 | -62.352 | -0.068665 | -0.013733 | 0.013733 | 0.20142 | -0.23346 | -0.25177 | -0.16479 | -0.18311 | -0.018311 | -0.068665 | 0.059509 | 0.041199 | -0.041199 | -0.09613 | -0.022888 | -0.077819 | 0.27008 | 122.6761 | 0.05951 | 122.6715 | 122.6486 | 122.5433 | 122.58 | 122.525 | -122.6624 | -122.612 | 122.6074 | 122.6532 | 62.2971 | 62.3566
115.5469 | 122.7859 | -62.2925 | 60.2737 | 0.010147 | -0.022702 | -0.022614 | 0.067148 | -0.031084 | -0.048672 | -0.037615 | -0.0021057 | -0.018399 | 0.056841 | 0.049467 | -0.21424 | -0.017273 | -0.018767 | -0.013733 | 60.2921 | -62.3932 | 60.2966 | -62.0819 | -62.5534 | -62.5214 | 0.091553 | 60.2142 | -62.3154 | 60.3607 | -62.2421 | -62.3611 | -62.3428 | -0.10071 | 0.01831 | 0.022888 | 0.21057 | -0.22888 | -0.26093 | -0.12817 | -0.16022 | -0.022889 | -0.05951 | 0.086975 | 0.050354 | -0.050354 | -0.068665 | -0.027465 | -0.045776 | 0.31128 | 122.6898 | 0.073243 | 122.6761 | 122.6852 | 122.5296 | 122.5845 | 122.5067 | -122.6669 | -122.5891 | 122.5891 | 122.6532 | 62.2787 | 62.384
117.3281 | 122.7448 | -62.3199 | 60.3149 | 0.010147 | -0.024624 | -0.023896 | 0.065012 | -0.031939 | -0.048886 | -0.042528 | -0.0021057 | -0.02139 | 0.057482 | 0.048185 | -0.2136 | -0.018128 | -0.02133 | -0.13275 | 60.2737 | -62.4252 | 60.1959 | -62.2009 | -62.6633 | -62.6129 | -0.10071 | 60.1959 | -62.352 | 60.2875 | -62.3337 | -62.4573 | -62.4069 | -0.10529 | -0.041198 | -0.11902 | 0.11902 | -0.29297 | -0.34332 | -0.18768 | -0.23804 | -0.032044 | -0.11902 | -0.027465 | -0.013733 | -0.086975 | -0.13733 | -0.054931 | -0.10529 | 0.2243 | 122.6212 | 0.018311 | 122.6395 | 122.699 | 122.5479 | 122.5937 | 122.5159 | -122.7402 | -122.6669 | 122.5159 | 122.6074 | 62.1872 | 62.2192
119.0312 | 122.8638 | -62.265 | 60.2463 | 0.0025177 | -0.030819 | -0.025177 | 0.062876 | -0.031725 | -0.048886 | -0.037401 | -0.0021057 | -0.023099 | 0.054918 | 0.048398 | -0.2136 | -0.019196 | -0.021758 | -0.050354 | 60.2142 | -62.4115 | 60.3012 | -62.0499 | -62.4939 | -62.4664 | 0.11444 | 60.1547 | -62.3108 | 60.3973 | -62.146 | -62.2604 | -62.2742 | -0.14648 | -0.032044 | 0.054931 | 0.21515 | -0.20142 | -0.22888 | -0.054932 | -0.082397 | -0.045776 | -0.091553 | 0.15106 | 0.11902 | -0.009155 | 0.004578 | 0.036621 | 0.050354 | 0.36163 | 122.7127 | 0.1648 | 122.7081 | 122.6257 | 122.4655 | 122.4792 | 122.4197 | -122.6578 | -122.5571 | 122.5662 | 122.6624 | 62.2147 | 62.3795
120.8125 | 122.7951 | -62.3062 | 60.228 | 0.0025177 | -0.026333 | -0.025605 | 0.067575 | -0.03023 | -0.045681 | -0.041033 | -0.0021057 | -0.020749 | 0.055559 | 0.046049 | -0.2136 | -0.016205 | -0.020689 | -0.15106 | 60.26 | -62.4161 | 60.2325 | -62.1643 | -62.6266 | -62.5854 | -0.059509 | 60.1822 | -62.3611 | 60.3378 | -62.265 | -62.3703 | -62.3199 | -0.10986 | 0.032044 | 0.004578 | 0.14191 | -0.27924 | -0.32044 | -0.16937 | -0.21057 | -0.054932 | -0.045776 | 0.10986 | 0.041198 | -0.013733 | -0.064087 | 0.041199 | -0.009155 | 0.25177 | 122.6486 | 0.09613 | 122.699 | 122.6761 | 122.5433 | 122.5662 | 122.4884 | -122.644 | -122.5891 | 122.5388 | 122.644 | 62.1552 | 62.2467
122.5781 | 122.8317 | -62.2971 | 60.2142 | -0.012741 | -0.026974 | -0.02475 | 0.061808 | -0.03557 | -0.048886 | -0.038042 | -0.0021057 | -0.022672 | 0.057695 | 0.043058 | -0.21573 | -0.021546 | -0.019835 | -0.091553 | 60.2188 | -62.4023 | 60.2829 | -62.1002 | -62.5397 | -62.5168 | 0.045776 | 60.141 | -62.3337 | 60.3745 | -62.2192 | -62.3062 | -62.3062 | -0.10529 | 0.004578 | 0.068665 | 0.19684 | -0.21973 | -0.24262 | -0.11444 | -0.13733 | -0.036621 | -0.073242 | 0.16022 | 0.07782 | -0.009155 | -0.009155 | 0.027466 | 0.027466 | 0.30212 | 122.6852 | 0.11444 | 122.7081 | 122.6212 | 122.4747 | 122.5159 | 122.438 | -122.6166 | -122.5479 | 122.58 | 122.6715 | 62.2055 | 62.3428
124.3594 | 122.8363 | -62.3291 | 60.2051 | -0.0051118 | -0.025692 | -0.023682 | 0.065653 | -0.033861 | -0.048886 | -0.039751 | -0.0021057 | -0.022458 | 0.054277 | 0.053739 | -0.21509 | -0.020478 | -0.023253 | -0.10071 | 60.1868 | -62.4023 | 60.3104 | -62.0453 | -62.5305 | -62.4847 | 0.068665 | 60.141 | -62.3154 | 60.3745 | -62.2192 | -62.3428 | -62.2971 | -0.073242 | -0.01831 | 0.10529 | 0.28381 | -0.15564 | -0.20142 | -0.082397 | -0.12817 | 0.013733 | -0.064087 | 0.16937 | 0.10986 | 0.032044 | -0.013732 | 0.018311 | -0.027465 | 0.35706 | 122.7127 | 0.096131 | 122.6898 | 122.5891 | 122.4564 | 122.5159 | 122.4701 | -122.6074 | -122.5204 | 122.6395 | 122.7036 | 62.2284 | 62.3978
126.125 | 122.7264 | -62.3108 | 60.2737 | -0.0051118 | -0.024411 | -0.02475 | 0.066507 | -0.03023 | -0.048245 | -0.041887 | 0.00094606 | -0.020108 | 0.055132 | 0.049039 | -0.21573 | -0.018769 | -0.019835 | -0.068665 | 60.2646 | -62.4069 | 60.2554 | -62.1323 | -62.6175 | -62.5763 | -0.013733 | 60.1959 | -62.3428 | 60.2875 | -62.3062 | -62.4435 | -62.3886 | -0.09613 | -0.009156 | -0.018311 | 0.17853 | -0.2655 | -0.3067 | -0.16937 | -0.21057 | -0.032043 | -0.07782 | 0.013733 | 0.004578 | -0.07782 | -0.13275 | -0.045777 | -0.10071 | 0.27466 | 122.6624 | 0.036621 | 122.6303 | 122.6715 | 122.5388 | 122.5754 | 122.5067 | -122.6807 | -122.6166 | 122.5662 | 122.5983 | 62.2421 | 62.2971
127.8281 | 122.8455 | -62.3016 | 60.2188 | -0.0051118 | -0.026333 | -0.025391 | 0.065439 | -0.035357 | -0.047604 | -0.038256 | -0.0021057 | -0.020322 | 0.057054 | 0.04498 | -0.21573 | -0.020051 | -0.022612 | -0.082397 | 60.173 | -62.3886 | 60.3058 | -62.0453 | -62.5442 | -62.4939 | 0.054932 | 60.1227 | -62.3383 | 60.3928 | -62.1872 | -62.3108 | -62.2879 | -0.086975 | -0.045776 | 0.086975 | 0.25635 | -0.19226 | -0.24261 | -0.10529 | -0.15564 | -0.036621 | -0.09613 | 0.17395 | 0.11444 | 0.013733 | -0.009155 | 0.050354 | 0.027466 | 0.34332 | 122.6944 | 0.15106 | 122.731 | 122.5616 | 122.4609 | 122.4747 | 122.4243 | -122.6074 | -122.5571 | 122.6074 | 122.6944 | 62.2192 | 62.3566
129.6094 | 122.8409 | -62.2833 | 60.2005 | -0.0051118 | -0.022915 | -0.023041 | 0.06373 | -0.031511 | -0.047604 | -0.040605 | -0.0021057 | -0.020536 | 0.054491 | 0.050962 | -0.2168 | -0.017487 | -0.020689 | -0.10071 | 60.2051 | -62.3886 | 60.3195 | -62.0407 | -62.5351 | -62.4847 | 0.064087 | 60.1456 | -62.3108 | 60.3928 | -62.1918 | -62.3154 | -62.2925 | -0.10529 | 0.004578 | 0.11902 | 0.24262 | -0.20142 | -0.25177 | -0.09613 | -0.14648 | -0.027466 | -0.054931 | 0.19226 | 0.091553 | -0.009155 | -0.032044 | 0.018311 | -0.004578 | 0.3479 | 122.7081 | 0.11902 | 122.7036 | 122.5937 | 122.4564 | 122.4884 | 122.4289 | -122.5891 | -122.5113 | 122.6028 | 122.6761 | 62.1826 | 62.3474
131.3906 | 122.7997 | -62.3154 | 60.228 | 0.0025177 | -0.027829 | -0.025391 | 0.063944 | -0.032366 | -0.048031 | -0.039751 | 0.0039979 | -0.021176 | 0.053423 | 0.050962 | -0.21616 | -0.017701 | -0.023039 | -0.13733 | 60.1913 | -62.3886 | 60.26 | -62.1002 | -62.5671 | -62.5168 | -0.013733 | 60.1547 | -62.3383 | 60.3333 | -62.2604 | -62.3383 | -62.3383 | -0.073242 | -0.036621 | 0.032044 | 0.21515 | -0.20142 | -0.25177 | -0.12817 | -0.17853 | -0.022888 | -0.073242 | 0.10529 | 0.054932 | -0.022888 | -0.022888 | 0 | 0 | 0.28839 | 122.6486 | 0.07782 | 122.6715 | 122.58 | 122.493 | 122.5067 | 122.4701 | -122.6166 | -122.5662 | 122.5754 | 122.6486 | 62.178 | 62.3016
133.1562 | 122.7127 | -62.3245 | 60.2783 | 0.0025177 | -0.02612 | -0.023682 | 0.065012 | -0.038134 | -0.049099 | -0.039965 | -0.0021057 | -0.019467 | 0.056841 | 0.053525 | -0.21573 | -0.01941 | -0.024748 | -0.14648 | 60.2737 | -62.4207 | 60.2097 | -62.2055 | -62.6541 | -62.6038 | -0.10986 | 60.1868 | -62.3474 | 60.2829 | -62.3383 | -62.4619 | -62.3932 | -0.09613 | -0.004577 | -0.068664 | 0.11902 | -0.27924 | -0.32959 | -0.18311 | -0.23346 | -0.022888 | -0.091552 | 0.004578 | -0.013733 | -0.068664 | -0.13733 | -0.045776 | -0.11444 | 0.21515 | 122.6303 | 0.009155 | 122.6303 | 122.6944 | 122.5342 | 122.5983 | 122.5113 | -122.699 | -122.6257 | 122.5342 | 122.6074 | 62.178 | 62.2147
134.8906 | 122.7173 | -62.3383 | 60.26 | 0.0025177 | -0.024197 | -0.02475 | 0.065225 | -0.030443 | -0.045681 | -0.039537 | -0.0021057 | -0.020108 | 0.054064 | 0.050962 | -0.21445 | -0.017273 | -0.022185 | -0.13275 | 60.2646 | -62.3978 | 60.2005 | -62.2101 | -62.6495 | -62.6129 | -0.091553 | 60.2142 | -62.3474 | 60.2829 | -62.3245 | -62.4527 | -62.3886 | -0.059509 | 0.004577 | -0.05951 | 0.12817 | -0.27466 | -0.31128 | -0.21515 | -0.25177 | -0.009155 | -0.045777 | 0.022888 | 0.013733 | -0.050354 | -0.11444 | -0.041199 | -0.10529 | 0.18768 | 122.5983 | 0.022888 | 122.6303 | 122.6624 | 122.5616 | 122.6028 | 122.5525 | -122.6578 | -122.6074 | 122.5388 | 122.6212 | 62.2055 | 62.2467
136.6875 | 122.7585 | -62.3062 | 60.2554 | 0.0025177 | -0.027401 | -0.023682 | 0.065439 | -0.029162 | -0.047817 | -0.042314 | 0.00094606 | -0.021176 | 0.05385 | 0.057584 | -0.21424 | -0.017273 | -0.02133 | -0.013733 | 60.26 | -62.4023 | 60.2875 | -62.0773 | -62.5488 | -62.5305 | 0.068665 | 60.228 | -62.3474 | 60.3516 | -62.2421 | -62.3657 | -62.3337 | -0.096131 | 0.004578 | 0.032044 | 0.22888 | -0.22431 | -0.24262 | -0.12817 | -0.14648 | -0.041199 | -0.027466 | 0.09613 | 0.064087 | -0.027466 | -0.05951 | 0.013733 | -0.018311 | 0.32501 | 122.6898 | 0.10529 | 122.699 | 122.6624 | 122.5754 | 122.5662 | 122.5342 | -122.6578 | -122.6028 | 122.5937 | 122.6578 | 62.2925 | 62.3749
138.4062 | 122.7173 | -62.2833 | 60.3104 | -0.0051118 | -0.028683 | -0.0224 | 0.063516 | -0.03023 | -0.050381 | -0.040392 | -0.0021057 | -0.020108 | 0.058336 | 0.050748 | -0.21445 | -0.020051 | -0.021117 | -0.059509 | 60.2875 | -62.4252 | 60.2325 | -62.1094 | -62.5671 | -62.5442 | 0.036621 | 60.2188 | -62.3245 | 60.2829 | -62.2559 | -62.3749 | -62.3703 | -0.14191 | -0.022888 | -0.07782 | 0.17395 | -0.26093 | -0.28381 | -0.11902 | -0.14191 | -0.041199 | -0.091553 | -0.027466 | 0.027466 | -0.086975 | -0.091553 | -0.045776 | -0.050354 | 0.31586 | 122.6578 | 0.068665 | 122.6074 | 122.7127 | 122.5433 | 122.5708 | 122.5021 | -122.7356 | -122.6349 | 122.5159 | 122.5662 | 62.2238 | 62.3199
140.1719 | 122.7127 | -62.3016 | 60.2554 | -0.012741 | -0.025265 | -0.024537 | 0.06608 | -0.032366 | -0.048672 | -0.040178 | 0.00094606 | -0.018827 | 0.056841 | 0.051389 | -0.21531 | -0.017914 | -0.022612 | -0.054932 | 60.2463 | -62.3886 | 60.2463 | -62.1323 | -62.6221 | -62.5946 | -0.050354 | 60.1959 | -62.3657 | 60.2829 | -62.3108 | -62.4344 | -62.3886 | -0.086975 | -0.009155 | -0.009155 | 0.16937 | -0.29297 | -0.32043 | -0.20599 | -0.23346 | -0.064087 | -0.059509 | 0.027466 | -0.009155 | -0.086975 | -0.13275 | -0.022888 | -0.068664 | 0.25635 | 122.6349 | 0.054932 | 122.6486 | 122.6349 | 122.5616 | 122.5479 | 122.4976 | -122.644 | -122.6212 | 122.5479 | 122.5845 | 62.2467 | 62.2513
141.9531 | 122.8226 | -62.3016 | 60.2051 | -0.0051118 | -0.025051 | -0.022187 | 0.063089 | -0.031939 | -0.048672 | -0.039751 | -0.0021057 | -0.023313 | 0.056841 | 0.047117 | -0.21424 | -0.018342 | -0.022185 | -0.10986 | 60.1868 | -62.384 | 60.3058 | -62.0178 | -62.5214 | -62.4847 | 0.054932 | 60.1135 | -62.3154 | 60.3928 | -62.178 | -62.3108 | -62.2925 | -0.082397 | -0.01831 | 0.10071 | 0.28381 | -0.1831 | -0.21973 | -0.10071 | -0.13733 | -0.013733 | -0.091553 | 0.18768 | 0.1236 | 0.009156 | -0.009155 | 0.022889 | 0.004578 | 0.36621 | 122.6898 | 0.13733 | 122.7081 | 122.5708 | 122.4289 | 122.4884 | 122.4152 | -122.5891 | -122.5204 | 122.6074 | 122.6944 | 62.1918 | 62.3566
143.7188 | 122.8363 | -62.2787 | 60.2371 | 0.0025177 | -0.028256 | -0.025605 | 0.062662 | -0.03023 | -0.04739 | -0.038683 | -0.0021057 | -0.023313 | 0.055132 | 0.046262 | -0.21659 | -0.017273 | -0.024107 | -0.004578 | 60.2051 | -62.3978 | 60.3424 | -61.9583 | -62.4435 | -62.4207 | 0.17395 | 60.173 | -62.3016 | 60.4019 | -62.1368 | -62.2421 | -62.2604 | -0.11902 | -0.032044 | 0.10529 | 0.32044 | -0.14191 | -0.16479 | -0.022888 | -0.045776 | -0.022888 | -0.064087 | 0.16479 | 0.14191 | 0.018311 | 0.036622 | 0.041199 | 0.05951 | 0.43945 | 122.7402 | 0.1648 | 122.7036 | 122.6028 | 122.4747 | 122.4838 | 122.4518 | -122.6349 | -122.5388 | 122.6212 | 122.6807 | 62.2742 | 62.4527
145.4375 | 122.7905 | -62.2971 | 60.2554 | 0.0025177 | -0.025692 | -0.022187 | 0.06373 | -0.028521 | -0.050167 | -0.042742 | 0.0039979 | -0.020108 | 0.056841 | 0.046903 | -0.21253 | -0.020478 | -0.023039 | -0.11444 | 60.1822 | -62.4069 | 60.2737 | -62.0728 | -62.558 | -62.5076 | 0.018311 | 60.1456 | -62.3337 | 60.3424 | -62.233 | -62.3291 | -62.3154 | -0.10986 | -0.073242 | 0.018311 | 0.2243 | -0.21057 | -0.26093 | -0.10071 | -0.15106 | -0.036621 | -0.10986 | 0.086975 | 0.064087 | -0.018311 | -0.032044 | 0.01831 | 0.004577 | 0.33417 | 122.6807 | 0.10071 | 122.6761 | 122.5891 | 122.4792 | 122.4792 | 122.4426 | -122.6624 | -122.5891 | 122.5708 | 122.6395 | 62.1826 | 62.3154
147.1875 | 122.7127 | -62.2971 | 60.2966 | 0.010147 | -0.027401 | -0.025605 | 0.063089 | -0.034929 | -0.047817 | -0.038683 | 0.00094606 | -0.019895 | 0.055559 | 0.049467 | -0.21467 | -0.020691 | -0.023039 | -0.045776 | 60.2692 | -62.3978 | 60.2325 | -62.1277 | -62.5626 | -62.5351 | 0.041199 | 60.2509 | -62.3016 | 60.2875 | -62.265 | -62.3795 | -62.3657 | -0.10071 | -0.027466 | -0.064087 | 0.16937 | -0.23804 | -0.2655 | -0.13733 | -0.1648 | -0.004578 | -0.045777 | -0.009155 | 0.032043 | -0.068665 | -0.082398 | -0.064087 | -0.07782 | 0.27008 | 122.6303 | 0.036621 | 122.5891 | 122.6669 | 122.5525 | 122.5662 | 122.5479 | -122.6944 | -122.5983 | 122.5296 | 122.5845 | 62.2513 | 62.3383
148.9844 | 122.7219 | -62.3016 | 60.3287 | 0.0025177 | -0.029538 | -0.02475 | 0.06608 | -0.033434 | -0.052517 | -0.036333 | 0.0039979 | -0.019467 | 0.056841 | 0.052671 | -0.21488 | -0.01941 | -0.019621 | -0.050354 | 60.2509 | -62.4115 | 60.2371 | -62.1277 | -62.5717 | -62.5442 | 0.032043 | 60.2188 | -62.3062 | 60.2875 | -62.2559 | -62.384 | -62.3611 | -0.10986 | -0.07782 | -0.091552 | 0.17395 | -0.24261 | -0.27008 | -0.13275 | -0.16022 | -0.004577 | -0.10986 | -0.041198 | 0.045777 | -0.059509 | -0.082397 | -0.054932 | -0.07782 | 0.28381 | 122.6486 | 0.050354 | 122.5937 | 122.6624 | 122.525 | 122.5525 | 122.5204 | -122.7402 | -122.6349 | 122.5388 | 122.5891 | 62.2513 | 62.3337
150.7031 | 122.7402 | -62.2833 | 60.3058 | -0.0051118 | -0.025479 | -0.025818 | 0.062662 | -0.031084 | -0.049313 | -0.038896 | 0.00094606 | -0.019895 | 0.055132 | 0.047544 | -0.21381 | -0.016846 | -0.022398 | 0.009155 | 60.2142 | -62.3795 | 60.3104 | -62.027 | -62.4756 | -62.4573 | 0.14191 | 60.1868 | -62.3016 | 60.3378 | -62.2055 | -62.3154 | -62.3016 | -0.096131 | -0.091553 | 0.004578 | 0.25635 | -0.17395 | -0.19226 | -0.077819 | -0.09613 | -0.018311 | -0.11902 | 0.032044 | 0.07782 | -0.018311 | -0.032044 | 0 | -0.013733 | 0.35248 | 122.6898 | 0.096131 | 122.6395 | 122.5937 | 122.4884 | 122.4976 | 122.4701 | -122.6852 | -122.6074 | 122.5937 | 122.6212 | 62.2925 | 62.4252
152.4844 | 122.8409 | -62.2742 | 60.2646 | -0.0051118 | -0.028897 | -0.027741 | 0.060099 | -0.03258 | -0.05209 | -0.038469 | -0.0021057 | -0.022245 | 0.054277 | 0.050962 | -0.21531 | -0.019196 | -0.02368 | 0.013733 | 60.173 | -62.3795 | 60.3653 | -61.9812 | -62.4664 | -62.4298 | 0.16022 | 60.1456 | -62.3016 | 60.3973 | -62.1368 | -62.2604 | -62.2604 | -0.10529 | -0.091552 | 0.10071 | 0.29297 | -0.15564 | -0.19226 | -0.050354 | -0.086975 | -0.027466 | -0.11902 | 0.13275 | 0.13733 | 0.013733 | 0.013733 | 0.041199 | 0.041199 | 0.39825 | 122.7448 | 0.1648 | 122.699 | 122.5525 | 122.4472 | 122.4472 | 122.4197 | -122.644 | -122.5662 | 122.6395 | 122.6715 | 62.2879 | 62.4344
154.2656 | 122.7493 | -62.2833 | 60.2783 | 0.010147 | -0.026547 | -0.023255 | 0.067789 | -0.032793 | -0.051022 | -0.041887 | -0.0021057 | -0.019467 | 0.0562 | 0.05438 | -0.2136 | -0.019837 | -0.022612 | -0.018311 | 60.2371 | -62.3978 | 60.2737 | -62.0682 | -62.5397 | -62.5122 | 0.082397 | 60.2005 | -62.3199 | 60.3516 | -62.2192 | -62.3337 | -62.3108 | -0.11444 | -0.041198 | -0.004577 | 0.21515 | -0.22888 | -0.25635 | -0.11444 | -0.14191 | -0.036621 | -0.07782 | 0.073242 | 0.064087 | -0.027466 | -0.050354 | 0.009155 | -0.013733 | 0.32959 | 122.6715 | 0.10071 | 122.6715 | 122.6349 | 122.5204 | 122.5204 | 122.4838 | -122.6761 | -122.5983 | 122.5571 | 122.6349 | 62.265 | 62.3657
155.9688 | 122.7173 | -62.3062 | 60.2921 | 0.0025177 | -0.027829 | -0.026673 | 0.066934 | -0.031725 | -0.047604 | -0.038896 | 0.00094606 | -0.01904 | 0.0562 | 0.053312 | -0.2136 | -0.018128 | -0.018126 | -0.12817 | 60.2188 | -62.4207 | 60.1776 | -62.1872 | -62.6587 | -62.6083 | -0.09613 | 60.2188 | -62.3566 | 60.2692 | -62.3108 | -62.4481 | -62.3795 | -0.11444 | -0.073242 | -0.11444 | 0.11902 | -0.30212 | -0.35248 | -0.18768 | -0.23804 | -0.050354 | -0.073242 | -0.022888 | -0.004578 | -0.073243 | -0.14191 | -0.022889 | -0.091553 | 0.23346 | 122.5983 | 0.045776 | 122.6257 | 122.6395 | 122.5754 | 122.525 | 122.525 | -122.7127 | -122.6486 | 122.4838 | 122.5754 | 62.178 | 62.2101
157.7344 | 122.8088 | -62.3154 | 60.1822 | -0.0051118 | -0.027188 | -0.025177 | 0.061594 | -0.035784 | -0.046749 | -0.03911 | -0.0051575 | -0.021604 | 0.057268 | 0.047758 | -0.21402 | -0.018769 | -0.02368 | -0.09613 | 60.1685 | -62.3749 | 60.2875 | -62.0361 | -62.5351 | -62.4847 | 0.050354 | 60.1318 | -62.3199 | 60.3561 | -62.2238 | -62.3245 | -62.3108 | -0.059509 | -0.013733 | 0.10529 | 0.27924 | -0.16937 | -0.21973 | -0.10986 | -0.16022 | -0.004577 | -0.050354 | 0.17395 | 0.091553 | 0.004578 | -0.009155 | 0.009155 | -0.004578 | 0.33875 | 122.6624 | 0.09613 | 122.6761 | 122.5433 | 122.4518 | 122.4838 | 122.4472 | -122.5571 | -122.5021 | 122.6028 | 122.6715 | 62.2192 | 62.3657
159.5156 | 122.7539 | -62.2559 | 60.2646 | 0.0025177 | -0.027615 | -0.026032 | 0.068857 | -0.03023 | -0.050595 | -0.040605 | -0.0051575 | -0.021176 | 0.055986 | 0.043272 | -0.21317 | -0.017487 | -0.024535 | -0.013733 | 60.2692 | -62.384 | 60.2829 | -62.0682 | -62.5351 | -62.5214 | 0.086975 | 60.2097 | -62.3016 | 60.3516 | -62.2009 | -62.3337 | -62.3062 | -0.12817 | 0.004578 | 0.018311 | 0.18768 | -0.2655 | -0.27924 | -0.13733 | -0.15106 | -0.045777 | -0.054931 | 0.086975 | 0.054931 | -0.050354 | -0.07782 | -0.004577 | -0.032043 | 0.31586 | 122.6669 | 0.10071 | 122.6532 | 122.6532 | 122.5113 | 122.525 | 122.4655 | -122.6486 | -122.5662 | 122.5388 | 122.6074 | 62.2421 | 62.3428
161.2344 | 122.8226 | -62.2787 | 60.2325 | 0.0025177 | -0.028683 | -0.025818 | 0.062021 | -0.026812 | -0.048886 | -0.040605 | 0.00094606 | -0.022672 | 0.056627 | 0.04498 | -0.21509 | -0.018769 | -0.023467 | -0.082397 | 60.2234 | -62.3657 | 60.2783 | -62.059 | -62.5122 | -62.4756 | 0.064087 | 60.141 | -62.3199 | 60.3745 | -62.1872 | -62.2742 | -62.265 | -0.086975 | -0.009155 | 0.045776 | 0.21973 | -0.19684 | -0.23346 | -0.10986 | -0.14648 | -0.041198 | -0.091553 | 0.14191 | 0.091553 | 0.013733 | 0.004578 | 0.054931 | 0.045776 | 0.3067 | 122.644 | 0.13275 | 122.6944 | 122.5891 | 122.4609 | 122.5021 | 122.4197 | -122.5983 | -122.5525 | 122.5571 | 122.6532 | 62.1964 | 62.3428
163.0156 | 122.6898 | -62.3199 | 60.2783 | -0.0051118 | -0.027829 | -0.024964 | 0.066934 | -0.028948 | -0.046536 | -0.041246 | -0.0021057 | -0.019254 | 0.054705 | 0.049894 | -0.21381 | -0.017273 | -0.022612 | -0.12817 | 60.26 | -62.3795 | 60.1959 | -62.1964 | -62.645 | -62.6129 | -0.11902 | 60.2051 | -62.3428 | 60.2646 | -62.3245 | -62.4344 | -62.3657 | -0.05951 | -0.01831 | -0.082397 | 0.1236 | -0.29297 | -0.32501 | -0.23346 | -0.2655 | -0.022888 | -0.073242 | -0.013733 | -0.004578 | -0.045777 | -0.11444 | -0.022889 | -0.091553 | 0.18311 | 122.5754 | 0.01831 | 122.6074 | 122.6395 | 122.5479 | 122.58 | 122.525 | -122.6578 | -122.6212 | 122.5159 | 122.5845 | 62.1918 | 62.2009
164.7969 | 122.7631 | -62.2925 | 60.228 | 0.0025177 | -0.028897 | -0.027314 | 0.064798 | -0.034716 | -0.046536 | -0.041246 | 0.00094606 | -0.023099 | 0.054705 | 0.051389 | -0.21488 | -0.020051 | -0.022398 | -0.1236 | 60.2005 | -62.384 | 60.2417 | -62.0865 | -62.5488 | -62.5076 | -0.013733 | 60.1685 | -62.352 | 60.3287 | -62.233 | -62.3337 | -62.3154 | -0.091553 | -0.027466 | 0.013733 | 0.20599 | -0.21515 | -0.25635 | -0.1236 | -0.16479 | -0.05951 | -0.059509 | 0.10071 | 0.059509 | -0.022889 | -0.041199 | 0.036621 | 0.018311 | 0.29755 | 122.6257 | 0.11902 | 122.6807 | 122.5845 | 122.5204 | 122.493 | 122.4609 | -122.612 | -122.58 | 122.5342 | 122.6212 | 62.1689 | 62.2787
166.5938 | 122.7631 | -62.2879 | 60.2783 | 0.0025177 | -0.02676 | -0.023896 | 0.066721 | -0.03322 | -0.050381 | -0.041246 | 0.0039979 | -0.020963 | 0.055986 | 0.045621 | -0.21317 | -0.017487 | -0.020476 | -0.004578 | 60.2325 | -62.3795 | 60.2737 | -62.0865 | -62.5351 | -62.5397 | 0.082397 | 60.228 | -62.2925 | 60.3424 | -62.2147 | -62.3611 | -62.3154 | -0.091553 | -0.045776 | -0.004577 | 0.20142 | -0.25177 | -0.24719 | -0.16022 | -0.15564 | -0.004577 | -0.050354 | 0.064087 | 0.073242 | -0.027466 | -0.073242 | -0.022889 | -0.068665 | 0.29297 | 122.6532 | 0.077819 | 122.6349 | 122.612 | 122.5204 | 122.5204 | 122.5159 | -122.6578 | -122.5708 | 122.5616 | 122.6303 | 62.2833 | 62.3703
168.375 | 122.7631 | -62.2833 | 60.2692 | -0.0051118 | -0.028683 | -0.02475 | 0.065225 | -0.028093 | -0.047604 | -0.038469 | 0.00094606 | -0.020322 | 0.057268 | 0.051389 | -0.21467 | -0.017914 | -0.020476 | 0 | 60.3012 | -62.3703 | 60.26 | -62.0956 | -62.5351 | -62.5168 | 0.068665 | 60.1959 | -62.2971 | 60.3241 | -62.2147 | -62.3428 | -62.3016 | -0.086975 | 0.032043 | -0.009155 | 0.18768 | -0.23346 | -0.25177 | -0.14648 | -0.16479 | -0.013733 | -0.073242 | 0.054932 | 0.068664 | -0.018311 | -0.059509 | -0.004578 | -0.045776 | 0.27466 | 122.6303 | 0.082397 | 122.6212 | 122.6715 | 122.493 | 122.5845 | 122.4792 | -122.6395 | -122.5662 | 122.5433 | 122.6074 | 62.2833 | 62.352
170.0781 | 122.7356 | -62.2971 | 60.2692 | 0.0025177 | -0.026547 | -0.0271 | 0.065012 | -0.028521 | -0.048886 | -0.038469 | -0.0051575 | -0.020963 | 0.057482 | 0.047758 | -0.21317 | -0.016846 | -0.021971 | -0.036621 | 60.2463 | -62.3886 | 60.2371 | -62.1185 | -62.5534 | -62.5351 | 0.027466 | 60.2188 | -62.3108 | 60.3333 | -62.233 | -62.3611 | -62.3108 | -0.091553 | -0.022888 | -0.032043 | 0.17853 | -0.23804 | -0.25635 | -0.14648 | -0.1648 | -0.013733 | -0.050354 | 0.064087 | 0.064087 | -0.013733 | -0.064087 | 0 | -0.050354 | 0.27008 | 122.6257 | 0.07782 | 122.644 | 122.6349 | 122.5296 | 122.5433 | 122.5159 | -122.6578 | -122.58 | 122.5342 | 122.6303 | 62.2604 | 62.3245
171.8438 | 122.7264 | -62.2879 | 60.2875 | 0.0025177 | -0.02911 | -0.026032 | 0.059458 | -0.028521 | -0.048031 | -0.039324 | -0.0021057 | -0.022245 | 0.053423 | 0.050107 | -0.21402 | -0.018342 | -0.021971 | 0.013733 | 60.228 | -62.3657 | 60.3012 | -62.027 | -62.471 | -62.471 | 0.11902 | 60.1868 | -62.2879 | 60.3149 | -62.2238 | -62.3291 | -62.3245 | -0.07782 | -0.05951 | 0.013732 | 0.26093 | -0.1831 | -0.1831 | -0.10528 | -0.10528 | 0 | -0.10071 | 0.027465 | 0.064087 | -0.036621 | -0.041199 | -0.036621 | -0.041199 | 0.33875 | 122.6669 | 0.064087 | 122.6028 | 122.5937 | 122.4747 | 122.5159 | 122.4747 | -122.6532 | -122.5754 | 122.5891 | 122.6028 | 62.3016 | 62.4069
173.625 | 122.8134 | -62.265 | 60.2234 | -0.0051118 | -0.024624 | -0.025391 | 0.063303 | -0.027239 | -0.048031 | -0.039537 | -0.0021057 | -0.019681 | 0.055986 | 0.05438 | -0.21488 | -0.016419 | -0.023894 | -0.13275 | 60.2234 | -62.3886 | 60.2646 | -62.0865 | -62.5534 | -62.5076 | 0.018311 | 60.1501 | -62.3199 | 60.3561 | -62.1918 | -62.3199 | -62.2604 | -0.1236 | 0 | 0.041198 | 0.17853 | -0.24261 | -0.28839 | -0.11902 | -0.1648 | -0.054931 | -0.073243 | 0.13275 | 0.073243 | 0.004578 | -0.054931 | 0.059509 | 0 | 0.30212 | 122.6532 | 0.12817 | 122.6761 | 122.612 | 122.4701 | 122.4884 | 122.4152 | -122.612 | -122.5433 | 122.5296 | 122.6212 | 62.1323 | 62.2833
175.3281 | 122.7859 | -62.2833 | 60.2692 | 0.0025177 | -0.028897 | -0.025818 | 0.060312 | -0.029375 | -0.049313 | -0.03911 | 0.00094606 | -0.022885 | 0.055986 | 0.04733 | -0.21338 | -0.019196 | -0.020049 | 0.018311 | 60.1913 | -62.3566 | 60.3333 | -61.9995 | -62.4481 | -62.439 | 0.15106 | 60.1822 | -62.2971 | 60.3607 | -62.1689 | -62.2742 | -62.2742 | -0.073242 | -0.07782 | 0.064087 | 0.28381 | -0.15564 | -0.1648 | -0.082398 | -0.091553 | -0.013733 | -0.086975 | 0.091553 | 0.11444 | 0.009155 | 0.009155 | 0.022888 | 0.022888 | 0.35705 | 122.6898 | 0.12817 | 122.6578 | 122.5479 | 122.4792 | 122.4747 | 122.4655 | -122.6257 | -122.5662 | 122.6166 | 122.644 | 62.3016 | 62.4344
177.0938 | 122.7219 | -62.2925 | 60.2783 | -0.0051118 | -0.027401 | -0.023469 | 0.066934 | -0.034502 | -0.048031 | -0.039537 | -0.0021057 | -0.01904 | 0.055132 | 0.045408 | -0.21723 | -0.015351 | -0.018767 | -0.013733 | 60.2417 | -62.3886 | 60.2875 | -62.059 | -62.5397 | -62.4893 | 0.082397 | 60.2142 | -62.3016 | 60.3378 | -62.2238 | -62.3566 | -62.3108 | -0.096131 | -0.036621 | 0.009156 | 0.23346 | -0.19684 | -0.24719 | -0.10071 | -0.15106 | -0.009156 | -0.064087 | 0.05951 | 0.068664 | -0.018311 | -0.064087 | -0.009155 | -0.054931 | 0.32959 | 122.6761 | 0.07782 | 122.6395 | 122.6303 | 122.5159 | 122.5342 | 122.5067 | -122.6669 | -122.58 | 122.58 | 122.6303 | 62.2787 | 62.3749
178.8906 | 122.6807 | -62.3245 | 60.2692 | 0.010147 | -0.025692 | -0.024964 | 0.06373 | -0.029375 | -0.04974 | -0.038256 | 0.0039979 | -0.02139 | 0.055773 | 0.048612 | -0.21552 | -0.015992 | -0.021971 | -0.12817 | 60.2509 | -62.4069 | 60.1776 | -62.1918 | -62.6404 | -62.6266 | -0.12817 | 60.1959 | -62.3337 | 60.26 | -62.3199 | -62.4344 | -62.3703 | -0.082397 | -0.018311 | -0.091553 | 0.13275 | -0.30212 | -0.31586 | -0.21973 | -0.23346 | -0.009155 | -0.073242 | -0.009155 | 0.004578 | -0.045776 | -0.10986 | -0.036621 | -0.10071 | 0.21515 | 122.5845 | 0.013733 | 122.5937 | 122.6578 | 122.5296 | 122.5754 | 122.5204 | -122.6761 | -122.6028 | 122.5021 | 122.5845 | 62.1963 | 62.1963
180.5938 | 122.818 | -62.2559 | 60.2051 | 0.0025177 | -0.027829 | -0.026246 | 0.062235 | -0.034716 | -0.051022 | -0.039751 | 0.0039979 | -0.022885 | 0.057482 | 0.046903 | -0.21595 | -0.020051 | -0.023467 | -0.050354 | 60.2097 | -62.3932 | 60.3058 | -62.0087 | -62.4573 | -62.4435 | 0.1236 | 60.1181 | -62.3062 | 60.3836 | -62.1414 | -62.233 | -62.2513 | -0.13733 | 0.004578 | 0.10071 | 0.24719 | -0.18768 | -0.20142 | -0.050354 | -0.064087 | -0.050354 | -0.086975 | 0.17853 | 0.11444 | 0.004577 | 0.022888 | 0.054931 | 0.073242 | 0.38452 | 122.699 | 0.16479 | 122.6898 | 122.6028 | 122.4243 | 122.4655 | 122.374 | -122.5983 | -122.5113 | 122.5616 | 122.6395 | 62.2055 | 62.3795
182.3594 | 122.7814 | -62.2879 | 60.2097 | -0.0051118 | -0.025906 | -0.024537 | 0.063303 | -0.030657 | -0.047817 | -0.03911 | 0.00094606 | -0.021176 | 0.057268 | 0.047758 | -0.21467 | -0.020051 | -0.021758 | -0.11902 | 60.1776 | -62.384 | 60.2417 | -62.0819 | -62.5534 | -62.4985 | 0.022888 | 60.1685 | -62.3199 | 60.3287 | -62.2055 | -62.3108 | -62.2787 | -0.09613 | -0.032044 | 0.032043 | 0.20599 | -0.21057 | -0.2655 | -0.11444 | -0.16937 | -0.032043 | -0.041199 | 0.11902 | 0.082398 | 0.009155 | -0.022888 | 0.041198 | 0.009155 | 0.30212 | 122.6257 | 0.11444 | 122.6486 | 122.5616 | 122.4884 | 122.4655 | 122.4564 | -122.5937 | -122.5296 | 122.5296 | 122.6166 | 62.1689 | 62.3108
184.1562 | 122.8134 | -62.2742 | 60.2005 | -0.0051118 | -0.026333 | -0.022187 | 0.064371 | -0.034716 | -0.046536 | -0.040392 | -0.0051575 | -0.021604 | 0.055345 | 0.051389 | -0.21637 | -0.017701 | -0.02133 | -0.09613 | 60.1501 | -62.384 | 60.3012 | -62.0178 | -62.5168 | -62.4573 | 0.054932 | 60.1318 | -62.3154 | 60.3561 | -62.1872 | -62.2925 | -62.2696 | -0.10986 | -0.050354 | 0.10071 | 0.25635 | -0.18311 | -0.24262 | -0.073242 | -0.13275 | -0.041199 | -0.068664 | 0.15564 | 0.086975 | 0.004578 | -0.01831 | 0.045777 | 0.022889 | 0.36621 | 122.6852 | 0.12817 | 122.6715 | 122.5342 | 122.4472 | 122.4243 | 122.406 | -122.5845 | -122.5159 | 122.5754 | 122.6303 | 62.178 | 62.3291
185.875 | 122.7676 | -62.2513 | 60.2737 | 0.0025177 | -0.028897 | -0.026246 | 0.06373 | -0.034929 | -0.051022 | -0.039751 | 0.00094606 | -0.023099 | 0.055132 | 0.043912 | -0.21381 | -0.017487 | -0.026885 | 0.013733 | 60.2005 | -62.3657 | 60.3241 | -62.0041 | -62.4573 | -62.439 | 0.13733 | 60.1822 | -62.3016 | 60.3653 | -62.1552 | -62.2742 | -62.265 | -0.11444 | -0.073243 | 0.050354 | 0.24719 | -0.18768 | -0.20599 | -0.073242 | -0.091552 | -0.050354 | -0.091553 | 0.091552 | 0.096131 | -0.013733 | -0.022888 | 0.036621 | 0.027466 | 0.36163 | 122.6898 | 0.14649 | 122.6669 | 122.5662 | 122.4838 | 122.4518 | 122.4335 | -122.6395 | -122.5754 | 122.5754 | 122.6166 | 62.265 | 62.3886
187.6562 | 122.7631 | -62.2971 | 60.2051 | -0.0051118 | -0.030392 | -0.026886 | 0.063303 | -0.032152 | -0.048458 | -0.038042 | -0.0082091 | -0.021176 | 0.055345 | 0.04968 | -0.21467 | -0.018342 | -0.021758 | -0.13275 | 60.1913 | -62.3886 | 60.2463 | -62.0911 | -62.5397 | -62.4985 | 0.004578 | 60.141 | -62.3474 | 60.3012 | -62.2238 | -62.3474 | -62.2879 | -0.091553 | -0.013733 | 0.041199 | 0.20599 | -0.20142 | -0.24262 | -0.10986 | -0.15106 | -0.050354 | -0.064087 | 0.09613 | 0.073242 | 0.009155 | -0.050354 | 0.059509 | 0 | 0.29755 | 122.6349 | 0.1236 | 122.6486 | 122.58 | 122.4884 | 122.4884 | 122.438 | -122.5937 | -122.5525 | 122.5433 | 122.5983 | 62.1643 | 62.3016
189.375 | 122.6898 | -62.2787 | 60.2829 | 0.0025177 | -0.027401 | -0.026673 | 0.063516 | -0.030657 | -0.050595 | -0.042314 | -0.0021057 | -0.018399 | 0.055345 | 0.050962 | -0.21424 | -0.018555 | -0.027739 | -0.013733 | 60.228 | -62.3795 | 60.26 | -62.0773 | -62.5259 | -62.5031 | 0.064087 | 60.1959 | -62.3062 | 60.2875 | -62.2513 | -62.3566 | -62.352 | -0.10071 | -0.054932 | -0.022888 | 0.20142 | -0.2243 | -0.24719 | -0.1236 | -0.14648 | -0.027465 | -0.086975 | 0.004578 | 0.027466 | -0.073242 | -0.077819 | -0.045777 | -0.050354 | 0.30212 | 122.6395 | 0.054931 | 122.5937 | 122.6074 | 122.5021 | 122.5067 | 122.4747 | -122.6624 | -122.5891 | 122.5388 | 122.5662 | 62.265 | 62.3428
191.1406 | 122.7493 | -62.3108 | 60.2097 | -0.0051118 | -0.026547 | -0.025605 | 0.06608 | -0.035784 | -0.051235 | -0.039965 | -0.0021057 | -0.019467 | 0.054277 | 0.050107 | -0.2136 | -0.017273 | -0.019621 | -0.14648 | 60.2646 | -62.3886 | 60.1822 | -62.1506 | -62.6129 | -62.5717 | -0.073242 | 60.1593 | -62.3291 | 60.2966 | -62.2742 | -62.384 | -62.3245 | -0.07782 | 0.054931 | -0.027466 | 0.16022 | -0.26093 | -0.30212 | -0.18311 | -0.2243 | -0.018311 | -0.050354 | 0.086975 | 0.036621 | -0.013733 | -0.073242 | 0.004578 | -0.054931 | 0.23804 | 122.5708 | 0.054932 | 122.6257 | 122.6532 | 122.4884 | 122.5754 | 122.4701 | -122.5983 | -122.5388 | 122.493 | 122.6074 | 62.1643 | 62.2375
192.9219 | 122.7905 | -62.2833 | 60.2097 | -0.0051118 | -0.026547 | -0.025605 | 0.062448 | -0.028093 | -0.050381 | -0.037615 | 0.00094606 | -0.023526 | 0.056627 | 0.047971 | -0.21552 | -0.019837 | -0.020476 | -0.10071 | 60.2005 | -62.384 | 60.2646 | -62.0636 | -62.5259 | -62.4847 | 0.032043 | 60.1364 | -62.3016 | 60.3607 | -62.1735 | -62.2742 | -62.2696 | -0.10071 | -0.009156 | 0.054931 | 0.21973 | -0.20142 | -0.24262 | -0.10071 | -0.14191 | -0.018311 | -0.073242 | 0.15106 | 0.10986 | 0.013733 | 0.009155 | 0.032044 | 0.027466 | 0.32043 | 122.6486 | 0.12817 | 122.6624 | 122.5845 | 122.4381 | 122.4838 | 122.4197 | -122.5937 | -122.5113 | 122.5479 | 122.644 | 62.1826 | 62.3154
194.7031 | 122.6807 | -62.2925 | 60.2692 | 0.0025177 | -0.025906 | -0.022187 | 0.067789 | -0.032366 | -0.048245 | -0.038469 | 0.00094606 | -0.02139 | 0.055986 | 0.050535 | -0.21445 | -0.018769 | -0.020903 | -0.07782 | 60.2325 | -62.3795 | 60.2234 | -62.1094 | -62.5854 | -62.558 | -0.032043 | 60.1913 | -62.3154 | 60.2737 | -62.2971 | -62.4252 | -62.3611 | -0.086976 | -0.036621 | -0.045776 | 0.1831 | -0.2655 | -0.29297 | -0.17853 | -0.20599 | -0.022889 | -0.07782 | 0.004578 | -0.004578 | -0.068665 | -0.13275 | -0.045776 | -0.10986 | 0.27008 | 122.6028 | 0.018311 | 122.5891 | 122.612 | 122.5067 | 122.525 | 122.4838 | -122.6486 | -122.5845 | 122.5159 | 122.5662 | 62.2147 | 62.2604
196.4219 | 122.7997 | -62.265 | 60.2188 | 0.0025177 | -0.028897 | -0.026459 | 0.063089 | -0.037493 | -0.048458 | -0.037615 | -0.0021057 | -0.023954 | 0.054705 | 0.050107 | -0.21531 | -0.017487 | -0.021117 | -0.091553 | 60.1822 | -62.3795 | 60.2692 | -62.0544 | -62.5031 | -62.4619 | 0.059509 | 60.1501 | -62.3291 | 60.3516 | -62.1552 | -62.265 | -62.2604 | -0.11444 | -0.036621 | 0.050354 | 0.21057 | -0.19684 | -0.23804 | -0.082397 | -0.1236 | -0.064087 | -0.068665 | 0.13275 | 0.10986 | 0.004578 | 0 | 0.068665 | 0.064087 | 0.32501 | 122.6486 | 0.17395 | 122.6807 | 122.5616 | 122.4792 | 122.4472 | 122.4152 | -122.5983 | -122.5479 | 122.5342 | 122.6166 | 62.1735 | 62.3245
198.1875 | 122.7081 | -62.2696 | 60.2875 | -0.0051118 | -0.027615 | -0.026459 | 0.065012 | -0.028734 | -0.050167 | -0.039751 | 0.00094606 | -0.020749 | 0.055986 | 0.048398 | -0.21467 | -0.016846 | -0.020689 | -0.027466 | 60.2463 | -62.3749 | 60.228 | -62.1323 | -62.5534 | -62.5351 | 0.013733 | 60.2188 | -62.2833 | 60.3149 | -62.2192 | -62.352 | -62.3016 | -0.10529 | -0.041199 | -0.05951 | 0.13733 | -0.2655 | -0.28381 | -0.16022 | -0.17853 | -0.013733 | -0.068665 | 0.027465 | 0.050354 | -0.032044 | -0.082398 | -0.018311 | -0.068665 | 0.24262 | 122.6028 | 0.064087 | 122.5983 | 122.6212 | 122.5021 | 122.5159 | 122.4884 | -122.6624 | -122.5708 | 122.4976 | 122.5845 | 62.2421 | 62.2833
199.9688 | 122.7814 | -62.2925 | 60.1959 | -0.0051118 | -0.025692 | -0.023041 | 0.064371 | -0.033007 | -0.048031 | -0.041033 | 0.00094606 | -0.021817 | 0.055345 | 0.046049 | -0.21595 | -0.017273 | -0.026244 | -0.14191 | 60.228 | -62.4115 | 60.2325 | -62.1048 | -62.5763 | -62.5351 | -0.004578 | 60.1318 | -62.3108 | 60.3653 | -62.1964 | -62.3245 | -62.265 | -0.11902 | 0.032043 | 0.036621 | 0.18768 | -0.24262 | -0.28381 | -0.1236 | -0.16479 | -0.018311 | -0.064087 | 0.16937 | 0.09613 | 0.027465 | -0.032044 | 0.045776 | -0.013733 | 0.3067 | 122.644 | 0.11444 | 122.6761 | 122.6395 | 122.4426 | 122.5204 | 122.4243 | -122.6074 | -122.5067 | 122.525 | 122.6578 | 62.1506 | 62.2879
201.6875 | 122.7264 | -62.265 | 60.2692 | 0.0025177 | -0.027615 | -0.025605 | 0.064585 | -0.031511 | -0.049099 | -0.038683 | 0.00094606 | -0.020108 | 0.058123 | 0.049039 | -0.21317 | -0.018769 | -0.024748 | -0.018311 | 60.2646 | -62.3886 | 60.2692 | -62.0728 | -62.5397 | -62.5305 | 0.064087 | 60.2097 | -62.2879 | 60.3333 | -62.2055 | -62.3383 | -62.2925 | -0.1236 | -0.004578 | 0 | 0.19226 | -0.2655 | -0.27466 | -0.14191 | -0.15106 | -0.022888 | -0.059509 | 0.064087 | 0.05951 | -0.027465 | -0.073242 | -0.004577 | -0.050354 | 0.31586 | 122.6578 | 0.082398 | 122.6212 | 122.6532 | 122.4976 | 122.5296 | 122.4747 | -122.6578 | -122.5571 | 122.5342 | 122.5983 | 62.2467 | 62.3291
203.4531 | 122.6761 | -62.2833 | 60.2829 | -0.0051118 | -0.028683 | -0.025391 | 0.064371 | -0.030016 | -0.048672 | -0.041887 | 0.0039979 | -0.020108 | 0.056414 | 0.046903 | -0.21274 | -0.01941 | -0.023467 | -0.059509 | 60.26 | -62.3978 | 60.228 | -62.1048 | -62.558 | -62.5214 | 0.032043 | 60.2142 | -62.3016 | 60.2692 | -62.2467 | -62.3657 | -62.3428 | -0.11444 | -0.022888 | -0.054932 | 0.17853 | -0.23804 | -0.27466 | -0.1236 | -0.16022 | -0.018311 | -0.068665 | -0.013733 | 0.036621 | -0.059509 | -0.082398 | -0.041198 | -0.064087 | 0.29297 | 122.6257 | 0.054932 | 122.5708 | 122.6578 | 122.5159 | 122.5433 | 122.4976 | -122.6807 | -122.5845 | 122.5113 | 122.5525 | 62.2238 | 62.3154
205.2188 | 122.7951 | -62.2559 | 60.2325 | 0.010147 | -0.028897 | -0.026032 | 0.063516 | -0.029375 | -0.049099 | -0.039324 | -0.0021057 | -0.022672 | 0.055559 | 0.046262 | -0.21573 | -0.016633 | -0.024321 | 0.013733 | 60.2051 | -62.3566 | 60.3333 | -61.9812 | -62.439 | -62.4161 | 0.17395 | 60.1593 | -62.2833 | 60.379 | -62.1231 | -62.233 | -62.2421 | -0.10071 | -0.027466 | 0.10071 | 0.27466 | -0.16022 | -0.18311 | -0.05951 | -0.082398 | -0.027466 | -0.073242 | 0.14648 | 0.13275 | 0.013733 | 0.022888 | 0.041199 | 0.050354 | 0.37537 | 122.6898 | 0.16022 | 122.6624 | 122.5616 | 122.4426 | 122.4609 | 122.4152 | -122.5891 | -122.5159 | 122.5891 | 122.6349 | 62.2696 | 62.4298
207 | 122.6715 | -62.2879 | 60.2692 | -0.0051118 | -0.027829 | -0.026459 | 0.064371 | -0.033648 | -0.046536 | -0.038683 | 0.00094606 | -0.021604 | 0.055986 | 0.050535 | -0.21488 | -0.017273 | -0.019408 | -0.045776 | 60.2417 | -62.384 | 60.2142 | -62.0956 | -62.5351 | -62.5214 | 0.036621 | 60.2142 | -62.2971 | 60.2737 | -62.2467 | -62.3566 | -62.3337 | -0.09613 | -0.027466 | -0.054932 | 0.19226 | -0.23346 | -0.24719 | -0.13733 | -0.15106 | -0.009155 | -0.054932 | 0.004578 | 0.041199 | -0.045776 | -0.068664 | -0.036621 | -0.059509 | 0.28839 | 122.5983 | 0.050354 | 122.5708 | 122.6257 | 122.5113 | 122.5296 | 122.5021 | -122.6532 | -122.5662 | 122.5021 | 122.5616 | 62.2421 | 62.3245
208.7812 | 122.7676 | -62.2833 | 60.1959 | 0.0025177 | -0.026547 | -0.023469 | 0.06373 | -0.030871 | -0.049099 | -0.039324 | -0.0021057 | -0.021817 | 0.056414 | 0.053098 | -0.21402 | -0.018982 | -0.022826 | -0.09613 | 60.141 | -62.352 | 60.2829 | -62.0041 | -62.5122 | -62.4756 | 0.054932 | 60.1135 | -62.3016 | 60.347 | -62.2101 | -62.3108 | -62.2787 | -0.068665 | -0.054932 | 0.086975 | 0.27924 | -0.19226 | -0.22888 | -0.1236 | -0.16022 | -0.018311 | -0.082398 | 0.15106 | 0.073242 | 0.004577 | -0.027466 | 0.022888 | -0.009155 | 0.3479 | 122.6349 | 0.091553 | 122.6486 | 122.493 | 122.4152 | 122.4243 | 122.3969 | -122.5479 | -122.4976 | 122.5662 | 122.6303 | 62.1872 | 62.3383
210.5625 | 122.818 | -62.2559 | 60.2234 | 0.010147 | -0.028256 | -0.025391 | 0.064371 | -0.035784 | -0.048458 | -0.038683 | -0.0051575 | -0.021604 | 0.056414 | 0.047117 | -0.21402 | -0.018982 | -0.024748 | -0.022888 | 60.1639 | -62.3657 | 60.3241 | -61.9629 | -62.4252 | -62.3978 | 0.17853 | 60.1639 | -62.2787 | 60.3836 | -62.1094 | -62.2147 | -62.233 | -0.10986 | -0.05951 | 0.10071 | 0.29297 | -0.14191 | -0.16937 | -0.032043 | -0.059509 | -0.022889 | -0.05951 | 0.16022 | 0.14648 | 0.022888 | 0.041198 | 0.045777 | 0.064087 | 0.40283 | 122.6898 | 0.16937 | 122.6624 | 122.5296 | 122.4426 | 122.4197 | 122.4197 | -122.5891 | -122.5021 | 122.58 | 122.6395 | 62.233 | 62.4344
212.2812 | 122.8363 | -62.2559 | 60.2371 | 0.0025177 | -0.029751 | -0.026032 | 0.064371 | -0.029162 | -0.04974 | -0.038042 | -0.0051575 | -0.020108 | 0.057268 | 0.04733 | -0.21467 | -0.019623 | -0.022398 | -0.027466 | 60.1593 | -62.3703 | 60.3058 | -61.9537 | -62.4298 | -62.4207 | 0.16937 | 60.141 | -62.2559 | 60.4065 | -62.0911 | -62.2101 | -62.2055 | -0.11444 | -0.07782 | 0.068664 | 0.30212 | -0.16479 | -0.17395 | -0.050354 | -0.05951 | 0 | -0.096131 | 0.16937 | 0.16479 | 0.050354 | 0.045776 | 0.050354 | 0.045776 | 0.41656 | 122.6761 | 0.16479 | 122.6624 | 122.5296 | 122.3969 | 122.4152 | 122.3969 | -122.6074 | -122.493 | 122.5616 | 122.6624 | 62.2284 | 62.4252
214.0781 | 122.7951 | -62.2696 | 60.1822 | -0.0051118 | -0.022915 | -0.023255 | 0.067148 | -0.034075 | -0.048245 | -0.038896 | -0.0021057 | -0.019254 | 0.055559 | 0.050321 | -0.21766 | -0.016419 | -0.022398 | -0.09613 | 60.2005 | -62.3886 | 60.2692 | -62.0453 | -62.5122 | -62.4756 | 0.022888 | 60.1227 | -62.3199 | 60.3699 | -62.1918 | -62.3108 | -62.2513 | -0.11902 | 0.01831 | 0.086975 | 0.2243 | -0.20599 | -0.24261 | -0.086975 | -0.1236 | -0.050354 | -0.059509 | 0.18768 | 0.07782 | 0.01831 | -0.041199 | 0.068664 | 0.009155 | 0.34332 | 122.6578 | 0.12817 | 122.6898 | 122.5891 | 122.4426 | 122.4701 | 122.3923 | -122.5708 | -122.5021 | 122.5388 | 122.6395 | 62.1735 | 62.2925
215.7969 | 122.7219 | -62.2696 | 60.2554 | -0.0051118 | -0.022488 | -0.024964 | 0.063303 | -0.035143 | -0.051022 | -0.038042 | 0.00094606 | -0.020322 | 0.055345 | 0.050748 | -0.21573 | -0.017914 | -0.021971 | -0.013733 | 60.2417 | -62.3703 | 60.2554 | -62.0728 | -62.5168 | -62.4985 | 0.073242 | 60.2005 | -62.2879 | 60.3287 | -62.1964 | -62.3291 | -62.2925 | -0.10071 | -0.013733 | 0 | 0.19684 | -0.22888 | -0.24719 | -0.12817 | -0.14648 | -0.018311 | -0.054932 | 0.073242 | 0.073242 | -0.022888 | -0.05951 | -0.004577 | -0.041199 | 0.29755 | 122.6257 | 0.091553 | 122.6166 | 122.612 | 122.4884 | 122.5113 | 122.4701 | -122.6257 | -122.5433 | 122.525 | 122.5983 | 62.2559 | 62.3428
217.5781 | 122.6578 | -62.2971 | 60.2783 | 0.010147 | -0.025265 | -0.0224 | 0.065439 | -0.031511 | -0.046963 | -0.04146 | 0.0070497 | -0.019681 | 0.056627 | 0.043912 | -0.21552 | -0.015992 | -0.024321 | -0.11444 | 60.2554 | -62.4161 | 60.173 | -62.178 | -62.6038 | -62.5763 | -0.082397 | 60.2005 | -62.3245 | 60.2417 | -62.3199 | -62.439 | -62.3657 | -0.11902 | -0.022888 | -0.10529 | 0.11902 | -0.27924 | -0.3067 | -0.16022 | -0.18768 | -0.027466 | -0.07782 | -0.036621 | -0.022888 | -0.068665 | -0.14191 | -0.041199 | -0.11444 | 0.23804 | 122.5891 | 0.004578 | 122.5662 | 122.6715 | 122.525 | 122.5525 | 122.4976 | -122.6944 | -122.6028 | 122.4701 | 122.5388 | 62.1826 | 62.2147
219.2812 | 122.731 | -62.265 | 60.2417 | -0.0051118 | -0.025265 | -0.025177 | 0.065866 | -0.030016 | -0.048245 | -0.038683 | 0.0039979 | -0.022031 | 0.057482 | 0.053739 | -0.21424 | -0.017487 | -0.023039 | -0.013733 | 60.2325 | -62.3886 | 60.26 | -62.0544 | -62.4985 | -62.4847 | 0.082397 | 60.1868 | -62.2971 | 60.3333 | -62.1918 | -62.3245 | -62.2833 | -0.1236 | -0.009155 | 0.018311 | 0.21057 | -0.21973 | -0.23346 | -0.09613 | -0.10986 | -0.032043 | -0.054931 | 0.091553 | 0.073243 | -0.01831 | -0.059509 | 0.013733 | -0.027466 | 0.33417 | 122.6486 | 0.10529 | 122.6303 | 122.6212 | 122.4838 | 122.4976 | 122.4518 | -122.6303 | -122.5388 | 122.525 | 122.5983 | 62.2513 | 62.3474
221.0625 | 122.8088 | -62.2787 | 60.1959 | -0.012741 | -0.024197 | -0.023896 | 0.065653 | -0.030443 | -0.046749 | -0.041674 | -0.0051575 | -0.023313 | 0.055986 | 0.043699 | -0.21424 | -0.017914 | -0.021544 | -0.086975 | 60.173 | -62.384 | 60.2829 | -62.0178 | -62.5259 | -62.471 | 0.050354 | 60.1135 | -62.3199 | 60.3561 | -62.1735 | -62.2879 | -62.2421 | -0.10529 | -0.022888 | 0.086975 | 0.26093 | -0.19226 | -0.24719 | -0.086975 | -0.14191 | -0.041198 | -0.082398 | 0.16022 | 0.10529 | 0.036622 | -0.009155 | 0.07782 | 0.032043 | 0.36621 | 122.6669 | 0.14648 | 122.6761 | 122.5571 | 122.4335 | 122.4518 | 122.3923 | -122.58 | -122.5159 | 122.5616 | 122.6349 | 62.1918 | 62.3291
222.8281 | 122.6669 | -62.2879 | 60.2646 | 0.0025177 | -0.023129 | -0.024323 | 0.066507 | -0.029162 | -0.049526 | -0.038256 | 0.0039979 | -0.01904 | 0.055986 | 0.055662 | -0.21253 | -0.016633 | -0.020262 | -0.13275 | 60.2509 | -62.4252 | 60.1685 | -62.1597 | -62.6358 | -62.5809 | -0.082397 | 60.1868 | -62.3383 | 60.2463 | -62.3062 | -62.4161 | -62.3566 | -0.13733 | -0.013733 | -0.09613 | 0.12817 | -0.29297 | -0.3479 | -0.15564 | -0.21057 | -0.050354 | -0.077819 | -0.01831 | -0.01831 | -0.068664 | -0.12817 | -0.01831 | -0.07782 | 0.2655 | 122.5937 | 0.032044 | 122.5845 | 122.6761 | 122.525 | 122.5388 | 122.4747 | -122.6898 | -122.6028 | 122.4564 | 122.5342 | 62.1552 | 62.2055
224.6094 | 122.8043 | -62.265 | 60.1913 | 0.0025177 | -0.026333 | -0.023896 | 0.060953 | -0.033861 | -0.046963 | -0.039324 | -0.0021057 | -0.022458 | 0.054918 | 0.050748 | -0.21509 | -0.017487 | -0.020689 | -0.09613 | 60.1868 | -62.3795 | 60.2875 | -62.0178 | -62.5031 | -62.471 | 0.054932 | 60.1135 | -62.3108 | 60.3653 | -62.1597 | -62.2925 | -62.2421 | -0.11444 | -0.004577 | 0.096131 | 0.24719 | -0.20599 | -0.23804 | -0.091552 | -0.1236 | -0.045776 | -0.07782 | 0.17395 | 0.10529 | 0.022889 | -0.027465 | 0.068665 | 0.018311 | 0.36163 | 122.6669 | 0.15106 | 122.6761 | 122.5662 | 122.4243 | 122.4518 | 122.3785 | -122.5708 | -122.5021 | 122.5525 | 122.6303 | 62.1689 | 62.3199
226.3125 | 122.7951 | -62.2604 | 60.1776 | 0.010147 | -0.023343 | -0.024109 | 0.066507 | -0.027239 | -0.04504 | -0.041246 | 0.00094606 | -0.021817 | 0.054491 | 0.051816 | -0.21317 | -0.019623 | -0.022612 | -0.086975 | 60.1868 | -62.384 | 60.2829 | -62.027 | -62.4985 | -62.4573 | 0.036621 | 60.0952 | -62.3108 | 60.3653 | -62.1689 | -62.2833 | -62.2375 | -0.1236 | 0.009156 | 0.10529 | 0.23346 | -0.19684 | -0.23804 | -0.073242 | -0.11444 | -0.050354 | -0.082397 | 0.18768 | 0.091553 | 0.022888 | -0.022888 | 0.073242 | 0.027466 | 0.35706 | 122.6669 | 0.14191 | 122.6761 | 122.5708 | 122.406 | 122.4472 | 122.3557 | -122.5616 | -122.4884 | 122.5433 | 122.6257 | 62.1735 | 62.2971
228.0781 | 122.7859 | -62.2879 | 60.2005 | -0.0051118 | -0.02377 | -0.022187 | 0.064585 | -0.029802 | -0.046322 | -0.039965 | -0.0021057 | -0.022885 | 0.0562 | 0.055021 | -0.21637 | -0.016419 | -0.023894 | -0.10986 | 60.1685 | -62.3703 | 60.2783 | -62.0087 | -62.4893 | -62.4527 | 0.059509 | 60.1044 | -62.2971 | 60.3607 | -62.1735 | -62.2742 | -62.2421 | -0.082397 | -0.032043 | 0.07782 | 0.27924 | -0.16479 | -0.20142 | -0.082398 | -0.11902 | -0.009155 | -0.09613 | 0.16022 | 0.11444 | 0.045777 | 0.013733 | 0.054932 | 0.022888 | 0.36163 | 122.6486 | 0.1236 | 122.6578 | 122.5388 | 122.4014 | 122.4564 | 122.3923 | -122.5708 | -122.4976 | 122.5662 | 122.6486 | 62.178 | 62.3474
229.8594 | 122.7127 | -62.2742 | 60.2509 | -0.0051118 | -0.02676 | -0.026246 | 0.065439 | -0.02553 | -0.047177 | -0.043383 | -0.0051575 | -0.01904 | 0.057054 | 0.056089 | -0.21595 | -0.018128 | -0.021544 | -0.009155 | 60.26 | -62.3886 | 60.26 | -62.0499 | -62.5259 | -62.4893 | 0.068665 | 60.173 | -62.3245 | 60.3287 | -62.2192 | -62.3474 | -62.2879 | -0.11444 | 0.009156 | 0.009156 | 0.2243 | -0.21515 | -0.25177 | -0.10071 | -0.13733 | -0.050354 | -0.077819 | 0.07782 | 0.054932 | -0.013733 | -0.073242 | 0.036621 | -0.022888 | 0.33874 | 122.6486 | 0.10529 | 122.6532 | 122.6486 | 122.4976 | 122.5342 | 122.4472 | -122.6395 | -122.5754 | 122.5342 | 122.6028 | 62.265 | 62.3428
231.625 | 122.6715 | -62.3016 | 60.2554 | 0.010147 | -0.025692 | -0.023896 | 0.06608 | -0.029589 | -0.047604 | -0.042314 | 0.00094606 | -0.019467 | 0.056414 | 0.046476 | -0.21274 | -0.018128 | -0.020903 | -0.14191 | 60.26 | -62.3795 | 60.1593 | -62.1552 | -62.6221 | -62.5809 | -0.091553 | 60.1685 | -62.3108 | 60.2509 | -62.2787 | -62.4069 | -62.3428 | -0.07782 | 0.004578 | -0.09613 | 0.14649 | -0.27924 | -0.32043 | -0.20142 | -0.24261 | -0.009155 | -0.086975 | -0.004578 | 0.022888 | -0.041198 | -0.10528 | -0.032043 | -0.09613 | 0.22431 | 122.5388 | 0.032043 | 122.5616 | 122.6395 | 122.4792 | 122.5616 | 122.4701 | -122.6349 | -122.5662 | 122.4609 | 122.5525 | 62.1597 | 62.2101
233.3281 | 122.7905 | -62.2696 | 60.1639 | 0.0025177 | -0.027188 | -0.024109 | 0.065225 | -0.030871 | -0.049954 | -0.040605 | 0.00094606 | -0.020963 | 0.054277 | 0.046903 | -0.21573 | -0.018555 | -0.022185 | -0.09613 | 60.1822 | -62.3932 | 60.2692 | -62.0178 | -62.4985 | -62.4573 | 0.045776 | 60.1089 | -62.3062 | 60.3653 | -62.1689 | -62.2696 | -62.2375 | -0.1236 | 0.018311 | 0.10529 | 0.25177 | -0.18768 | -0.22888 | -0.064087 | -0.10529 | -0.036621 | -0.054931 | 0.20142 | 0.10071 | 0.032043 | 0 | 0.068664 | 0.036621 | 0.37537 | 122.6624 | 0.13733 | 122.6715 | 122.5754 | 122.4152 | 122.4518 | 122.3785 | -122.5571 | -122.4701 | 122.5388 | 122.6349 | 62.1735 | 62.3154
235.1094 | 122.7127 | -62.2787 | 60.2188 | -0.0051118 | -0.024624 | -0.026032 | 0.066934 | -0.025744 | -0.046536 | -0.037615 | -0.0021057 | -0.019895 | 0.056841 | 0.045621 | -0.21445 | -0.017273 | -0.019621 | -0.16022 | 60.2325 | -62.3932 | 60.1822 | -62.1414 | -62.5992 | -62.558 | -0.068665 | 60.173 | -62.3337 | 60.2966 | -62.265 | -62.3795 | -62.3062 | -0.11444 | 0.013733 | -0.036621 | 0.13733 | -0.27923 | -0.32043 | -0.16479 | -0.20599 | -0.054931 | -0.045776 | 0.07782 | 0.013733 | -0.027465 | -0.10071 | 0.027466 | -0.045777 | 0.25177 | 122.5754 | 0.068664 | 122.6303 | 122.6257 | 122.5067 | 122.5113 | 122.4518 | -122.612 | -122.5525 | 122.4609 | 122.5754 | 62.1185 | 62.2101
236.9062 | 122.6532 | -62.2833 | 60.2692 | 0.010147 | -0.024838 | -0.024109 | 0.066507 | -0.030443 | -0.047817 | -0.038683 | -0.0021057 | -0.018399 | 0.055559 | 0.047117 | -0.21723 | -0.016846 | -0.021117 | -0.073242 | 60.26 | -62.4069 | 60.2142 | -62.1048 | -62.59 | -62.558 | -0.041199 | 60.1639 | -62.2879 | 60.2646 | -62.2787 | -62.4115 | -62.3337 | -0.1236 | -0.009155 | -0.054932 | 0.17853 | -0.27466 | -0.3067 | -0.15106 | -0.18311 | -0.004578 | -0.10529 | -0.004578 | 0.004577 | -0.050354 | -0.12817 | -0.045776 | -0.1236 | 0.30212 | 122.6212 | 0.009155 | 122.5525 | 122.6669 | 122.4518 | 122.5433 | 122.4472 | -122.6761 | -122.5571 | 122.4976 | 122.5479 | 62.2101 | 62.2421
238.6875 | 122.7905 | -62.2513 | 60.2325 | -0.012741 | -0.027188 | -0.026246 | 0.06138 | -0.029162 | -0.04974 | -0.042528 | -0.0021057 | -0.021817 | 0.055132 | 0.052457 | -0.21424 | -0.017701 | -0.025603 | -0.027466 | 60.1913 | -62.3611 | 60.3104 | -61.9675 | -62.4298 | -62.4115 | 0.1831 | 60.1456 | -62.2833 | 60.3745 | -62.1231 | -62.2284 | -62.2147 | -0.10986 | -0.041199 | 0.07782 | 0.28381 | -0.16022 | -0.17853 | -0.050354 | -0.068665 | -0.032043 | -0.086975 | 0.14191 | 0.12817 | 0.036621 | 0.022888 | 0.068664 | 0.054931 | 0.39368 | 122.6715 | 0.16022 | 122.6578 | 122.5525 | 122.4289 | 122.4426 | 122.3969 | -122.5937 | -122.5159 | 122.5616 | 122.6257 | 62.2238 | 62.4344
240.4688 | 122.7905 | -62.2559 | 60.2188 | -0.0051118 | -0.028897 | -0.026246 | 0.064157 | -0.032152 | -0.04974 | -0.042101 | 0.0039979 | -0.021604 | 0.055773 | 0.045621 | -0.21467 | -0.019196 | -0.023894 | -0.064087 | 60.1776 | -62.3749 | 60.2554 | -62.027 | -62.4893 | -62.4481 | 0.086975 | 60.1089 | -62.2925 | 60.3561 | -62.1323 | -62.2467 | -62.2238 | -0.11902 | -0.041199 | 0.036621 | 0.22888 | -0.19226 | -0.23346 | -0.073242 | -0.11444 | -0.036621 | -0.10986 | 0.13733 | 0.1236 | 0.032043 | 0.009155 | 0.068664 | 0.045776 | 0.3479 | 122.6303 | 0.16022 | 122.6486 | 122.5525 | 122.4014 | 122.4335 | 122.3648 | -122.5937 | -122.5113 | 122.5113 | 122.612 | 62.1918 | 62.3428
242.25 | 122.7814 | -62.2284 | 60.228 | -0.0051118 | -0.02676 | -0.023682 | 0.061594 | -0.030443 | -0.048886 | -0.040392 | -0.0021057 | -0.021604 | 0.054064 | 0.047117 | -0.2168 | -0.017701 | -0.025176 | 0.018311 | 60.1913 | -62.3474 | 60.3058 | -61.9858 | -62.4435 | -62.4161 | 0.1831 | 60.1547 | -62.2559 | 60.3516 | -62.1323 | -62.2421 | -62.233 | -0.11902 | -0.036621 | 0.07782 | 0.24262 | -0.18768 | -0.21515 | -0.068665 | -0.09613 | -0.027465 | -0.073242 | 0.1236 | 0.096131 | -0.004577 | -0.013732 | 0.022888 | 0.013733 | 0.36163 | 122.6532 | 0.1236 | 122.6074 | 122.5388 | 122.4106 | 122.4197 | 122.3831 | -122.5754 | -122.4838 | 122.5342 | 122.58 | 62.2467 | 62.4115
243.9688 | 122.7173 | -62.265 | 60.2554 | -0.0051118 | -0.026333 | -0.024323 | 0.064371 | -0.033434 | -0.048886 | -0.037615 | -0.0021057 | -0.020108 | 0.0562 | 0.048826 | -0.21702 | -0.018128 | -0.020903 | -0.013733 | 60.26 | -62.3566 | 60.2371 | -62.0682 | -62.5122 | -62.4802 | 0.07782 | 60.2142 | -62.2925 | 60.3287 | -62.1918 | -62.3291 | -62.2833 | -0.091552 | 0.004578 | -0.01831 | 0.19684 | -0.21515 | -0.24719 | -0.1236 | -0.15564 | -0.027465 | -0.041199 | 0.073242 | 0.073243 | -0.01831 | -0.064087 | 0.009155 | -0.036622 | 0.28839 | 122.5937 | 0.10071 | 122.6212 | 122.6166 | 122.5067 | 122.525 | 122.4792 | -122.612 | -122.5479 | 122.5021 | 122.5937 | 62.2513 | 62.3428
245.75 | 122.7814 | -62.2513 | 60.228 | -0.012741 | -0.029538 | -0.024964 | 0.061594 | -0.030871 | -0.050167 | -0.040178 | -0.0021057 | -0.022458 | 0.055773 | 0.043699 | -0.21338 | -0.018982 | -0.026671 | -0.050354 | 60.1959 | -62.3566 | 60.2829 | -61.9949 | -62.4527 | -62.4252 | 0.13275 | 60.1364 | -62.2925 | 60.3973 | -62.1185 | -62.2284 | -62.2147 | -0.10528 | -0.032043 | 0.054932 | 0.25635 | -0.17395 | -0.20142 | -0.068665 | -0.096131 | -0.041198 | -0.091552 | 0.16937 | 0.13275 | 0.036621 | 0.022888 | 0.077819 | 0.064086 | 0.36163 | 122.6395 | 0.17395 | 122.6898 | 122.5525 | 122.4289 | 122.4472 | 122.3877 | -122.5845 | -122.5204 | 122.5342 | 122.6486 | 62.2009 | 62.384
247.5312 | 122.6532 | -62.2604 | 60.26 | -0.0051118 | -0.024624 | -0.022828 | 0.065225 | -0.03023 | -0.046749 | -0.038683 | 0.00094606 | -0.020108 | 0.0562 | 0.04968 | -0.2136 | -0.018128 | -0.021544 | -0.068665 | 60.2509 | -62.384 | 60.2234 | -62.1002 | -62.5763 | -62.5305 | 0 | 60.1776 | -62.2925 | 60.2737 | -62.265 | -62.4069 | -62.3199 | -0.1236 | -0.009156 | -0.036621 | 0.16022 | -0.27008 | -0.31586 | -0.14648 | -0.19226 | -0.032043 | -0.082398 | 0.013733 | -0.004578 | -0.059509 | -0.14648 | -0.027466 | -0.11444 | 0.28381 | 122.6074 | 0.027465 | 122.5662 | 122.6349 | 122.4701 | 122.5113 | 122.438 | -122.644 | -122.5525 | 122.4838 | 122.5342 | 62.1918 | 62.2604
249.2344 | 122.7585 | -62.233 | 60.228 | -0.0051118 | -0.028256 | -0.026032 | 0.063089 | -0.034075 | -0.048672 | -0.038042 | -0.0051575 | -0.021817 | 0.056841 | 0.043699 | -0.21659 | -0.016846 | -0.022185 | 0 | 60.1959 | -62.3703 | 60.3012 | -61.9583 | -62.4344 | -62.4023 | 0.16022 | 60.1639 | -62.2513 | 60.3653 | -62.114 | -62.2192 | -62.2192 | -0.13733 | -0.032043 | 0.073242 | 0.27466 | -0.16937 | -0.20142 | -0.032044 | -0.064087 | -0.018311 | -0.064087 | 0.13733 | 0.11902 | 0.013733 | 0.013733 | 0.032044 | 0.032044 | 0.41199 | 122.6715 | 0.13733 | 122.6166 | 122.5662 | 122.4152 | 122.4289 | 122.3969 | -122.5983 | -122.4792 | 122.5342 | 122.5983 | 62.233 | 62.3932
251.0156 | 122.7676 | -62.2513 | 60.1822 | 0.0025177 | -0.022915 | -0.023896 | 0.06373 | -0.03258 | -0.047177 | -0.038469 | 0.00094606 | -0.022672 | 0.056414 | 0.051816 | -0.21573 | -0.017914 | -0.021544 | -0.07782 | 60.1593 | -62.3657 | 60.2783 | -62.027 | -62.5168 | -62.4527 | 0.059509 | 60.1044 | -62.3199 | 60.3516 | -62.146 | -62.2696 | -62.2284 | -0.11444 | -0.022888 | 0.09613 | 0.2243 | -0.20142 | -0.2655 | -0.086975 | -0.15106 | -0.068664 | -0.07782 | 0.16937 | 0.10529 | 0.022888 | -0.01831 | 0.091552 | 0.050354 | 0.33875 | 122.644 | 0.17395 | 122.6715 | 122.525 | 122.4243 | 122.4106 | 122.3557 | -122.5479 | -122.5021 | 122.5296 | 122.6028 | 62.1735 | 62.3108
252.7969 | 122.7356 | -62.2742 | 60.1913 | -0.0051118 | -0.027615 | -0.024537 | 0.06138 | -0.031511 | -0.050381 | -0.039324 | -0.0021057 | -0.02139 | 0.054918 | 0.047971 | -0.21573 | -0.018769 | -0.023253 | -0.11902 | 60.173 | -62.3703 | 60.2463 | -62.0407 | -62.5351 | -62.471 | 0.032043 | 60.1227 | -62.2971 | 60.3104 | -62.2055 | -62.3062 | -62.2604 | -0.09613 | -0.01831 | 0.054932 | 0.23346 | -0.19684 | -0.26093 | -0.10071 | -0.16479 | -0.022888 | -0.068664 | 0.11902 | 0.068665 | 0.013733 | -0.032043 | 0.036621 | -0.009155 | 0.32959 | 122.6166 | 0.091553 | 122.6074 | 122.5433 | 122.4197 | 122.4472 | 122.3969 | -122.5616 | -122.4884 | 122.5204 | 122.5845 | 62.1552 | 62.3062
254.5781 | 122.6395 | -62.2787 | 60.26 | 0.010147 | -0.028683 | -0.026459 | 0.063516 | -0.037706 | -0.048245 | -0.036333 | -0.0021057 | -0.022031 | 0.056841 | 0.050535 | -0.21424 | -0.016633 | -0.021117 | -0.032043 | 60.2646 | -62.3749 | 60.2051 | -62.0956 | -62.5259 | -62.5168 | 0.041199 | 60.2142 | -62.2696 | 60.2737 | -62.2467 | -62.3474 | -62.3199 | -0.09613 | 0.004577 | -0.054932 | 0.18311 | -0.23804 | -0.24719 | -0.14191 | -0.15106 | 0.009156 | -0.045777 | 0.013733 | 0.032044 | -0.041198 | -0.068664 | -0.050354 | -0.07782 | 0.27924 | 122.58 | 0.022888 | 122.5433 | 122.6395 | 122.4838 | 122.5433 | 122.493 | -122.6349 | -122.5296 | 122.4838 | 122.5525 | 62.2467 | 62.3199
256.3594 | 122.644 | -62.2696 | 60.2325 | -0.0051118 | -0.025051 | -0.023041 | 0.066721 | -0.027666 | -0.046963 | -0.038683 | 0.00094606 | -0.02139 | 0.054918 | 0.058225 | -0.21616 | -0.016846 | -0.021117 | -0.082397 | 60.2554 | -62.3657 | 60.1913 | -62.1277 | -62.5946 | -62.5534 | -0.050354 | 60.1913 | -62.3016 | 60.2509 | -62.2925 | -62.4252 | -62.3291 | -0.096131 | 0.022888 | -0.041199 | 0.14191 | -0.28381 | -0.32501 | -0.18768 | -0.22888 | -0.032044 | -0.041199 | 0.01831 | -0.022888 | -0.05951 | -0.15564 | -0.027466 | -0.1236 | 0.23804 | 122.5571 | 0.009156 | 122.5525 | 122.6212 | 122.493 | 122.525 | 122.4609 | -122.5983 | -122.5342 | 122.4609 | 122.5204 | 62.1872 | 62.2192
258.0625 | 122.7402 | -62.2742 | 60.228 | -0.0051118 | -0.027188 | -0.026246 | 0.062662 | -0.031725 | -0.046963 | -0.042955 | -0.0021057 | -0.021817 | 0.055345 | 0.044126 | -0.21573 | -0.018982 | -0.022826 | -0.11444 | 60.173 | -62.3703 | 60.228 | -62.0819 | -62.5214 | -62.4802 | -0.004578 | 60.1181 | -62.3108 | 60.2921 | -62.2238 | -62.3199 | -62.265 | -0.09613 | -0.054931 | 0 | 0.19226 | -0.20599 | -0.24719 | -0.10986 | -0.15106 | -0.036621 | -0.10986 | 0.064087 | 0.050354 | 0.009155 | -0.045776 | 0.045776 | -0.009155 | 0.28839 | 122.5983 | 0.086975 | 122.6028 | 122.5433 | 122.4289 | 122.4472 | 122.3923 | -122.5983 | -122.5388 | 122.5021 | 122.5662 | 62.1597 | 62.2696
259.8438 | 122.7631 | -62.2742 | 60.1639 | -0.0051118 | -0.025906 | -0.0224 | 0.06373 | -0.031084 | -0.048245 | -0.039324 | 0.00094606 | -0.022245 | 0.055559 | 0.049894 | -0.21488 | -0.016633 | -0.020262 | -0.10986 | 60.173 | -62.384 | 60.2783 | -61.9995 | -62.4985 | -62.4435 | 0.059509 | 60.1135 | -62.2787 | 60.3241 | -62.1964 | -62.2971 | -62.2559 | -0.10986 | 0.009156 | 0.11444 | 0.27466 | -0.16937 | -0.2243 | -0.059509 | -0.11444 | -0.004578 | -0.050354 | 0.16022 | 0.07782 | 0.018311 | -0.022888 | 0.022889 | -0.01831 | 0.38452 | 122.6624 | 0.082398 | 122.6028 | 122.5571 | 122.3923 | 122.4472 | 122.3877 | -122.5479 | -122.4426 | 122.5525 | 122.5983 | 62.1643 | 62.3337
261.6406 | 122.7036 | -62.2421 | 60.2646 | -0.012741 | -0.02612 | -0.024109 | 0.064798 | -0.028948 | -0.048886 | -0.036547 | -0.0021057 | -0.020322 | 0.056841 | 0.049467 | -0.21637 | -0.017273 | -0.022398 | -0.009155 | 60.2692 | -62.3383 | 60.228 | -62.0544 | -62.5031 | -62.4893 | 0.068665 | 60.1868 | -62.2742 | 60.3149 | -62.1826 | -62.3108 | -62.2696 | -0.096131 | 0.004578 | -0.036621 | 0.18768 | -0.24719 | -0.26093 | -0.15106 | -0.16479 | -0.032044 | -0.077819 | 0.050354 | 0.059509 | -0.027466 | -0.068665 | 0.004578 | -0.036621 | 0.28381 | 122.5662 | 0.091553 | 122.5891 | 122.6074 | 122.4609 | 122.5113 | 122.4289 | -122.6028 | -122.5388 | 122.4701 | 122.5571 | 62.233 | 62.3108
263.3438 | 122.7081 | -62.2375 | 60.26 | -0.012741 | -0.027829 | -0.023682 | 0.062448 | -0.031511 | -0.049099 | -0.041033 | -0.0051575 | -0.021817 | 0.0562 | 0.047971 | -0.21296 | -0.01941 | -0.023467 | 0.022888 | 60.2051 | -62.3566 | 60.2875 | -61.9858 | -62.4344 | -62.439 | 0.1236 | 60.1639 | -62.2696 | 60.3012 | -62.178 | -62.2971 | -62.2787 | -0.11902 | -0.054932 | 0.027466 | 0.25177 | -0.20142 | -0.19684 | -0.082398 | -0.07782 | -0.032043 | -0.096131 | 0.041198 | 0.059509 | -0.041199 | -0.059509 | -0.009156 | -0.027466 | 0.37079 | 122.644 | 0.091552 | 122.5708 | 122.5616 | 122.4335 | 122.4426 | 122.4014 | -122.6166 | -122.5296 | 122.525 | 122.5388 | 62.2604 | 62.3611
265.1094 | 122.6852 | -62.2421 | 60.2509 | 0.0025177 | -0.028256 | -0.024964 | 0.061594 | -0.03023 | -0.047817 | -0.039965 | 0.00094606 | -0.020963 | 0.056414 | 0.043272 | -0.21531 | -0.017487 | -0.022398 | 0.022888 | 60.2005 | -62.3749 | 60.2783 | -61.9812 | -62.4435 | -62.4344 | 0.13275 | 60.1685 | -62.2787 | 60.3149 | -62.1643 | -62.2879 | -62.2696 | -0.13275 | -0.050354 | 0.027466 | 0.26093 | -0.19226 | -0.20142 | -0.059509 | -0.068664 | -0.036622 | -0.082397 | 0.064087 | 0.077819 | -0.027466 | -0.045777 | 0.009156 | -0.009155 | 0.39368 | 122.6532 | 0.11444 | 122.5937 | 122.5754 | 122.4472 | 122.4426 | 122.4106 | -122.6257 | -122.5296 | 122.5204 | 122.5571 | 62.265 | 62.3749
266.8906 | 122.7585 | -62.2467 | 60.2234 | 0.010147 | -0.028042 | -0.027741 | 0.061594 | -0.030657 | -0.048886 | -0.039751 | -0.0051575 | -0.021817 | 0.0562 | 0.045621 | -0.21445 | -0.017487 | -0.023039 | -0.064087 | 60.1868 | -62.3611 | 60.2509 | -62.0087 | -62.4664 | -62.4252 | 0.09613 | 60.1135 | -62.2742 | 60.3653 | -62.1185 | -62.233 | -62.2147 | -0.11444 | -0.036621 | 0.027465 | 0.23804 | -0.17853 | -0.21973 | -0.064087 | -0.10529 | -0.027466 | -0.10986 | 0.14191 | 0.12817 | 0.032043 | 0.013733 | 0.059509 | 0.041199 | 0.35248 | 122.612 | 0.15564 | 122.6395 | 122.5479 | 122.3877 | 122.4335 | 122.3602 | -122.5845 | -122.4976 | 122.4976 | 122.612 | 62.1826 | 62.3428
268.6719 | 122.6212 | -62.2604 | 60.2692 | -0.0051118 | -0.024411 | -0.023255 | 0.066507 | -0.029802 | -0.04974 | -0.041033 | -0.0021057 | -0.018613 | 0.054918 | 0.054594 | -0.21509 | -0.019196 | -0.021971 | -0.10529 | 60.2737 | -62.3749 | 60.1547 | -62.1597 | -62.6083 | -62.5717 | -0.11444 | 60.1913 | -62.3245 | 60.2142 | -62.3016 | -62.4161 | -62.3474 | -0.11444 | 0.004578 | -0.11444 | 0.10071 | -0.31128 | -0.3479 | -0.19684 | -0.23346 | -0.064087 | -0.07782 | -0.054932 | -0.041199 | -0.086975 | -0.15564 | -0.022888 | -0.091553 | 0.21515 | 122.5296 | 0.022888 | 122.5388 | 122.6486 | 122.5159 | 122.5342 | 122.4518 | -122.644 | -122.5937 | 122.4152 | 122.4747 | 62.1552 | 62.146
270.4531 | 122.7905 | -62.2467 | 60.1959 | -0.0051118 | -0.027829 | -0.0271 | 0.060526 | -0.030871 | -0.050595 | -0.039965 | 0.00094606 | -0.022245 | 0.055986 | 0.046262 | -0.21637 | -0.018342 | -0.023894 | -0.041199 | 60.2051 | -62.3428 | 60.2875 | -61.9766 | -62.4344 | -62.4115 | 0.15564 | 60.1456 | -62.2787 | 60.379 | -62.1094 | -62.2101 | -62.2009 | -0.09613 | 0.009155 | 0.091553 | 0.27008 | -0.16479 | -0.18768 | -0.068665 | -0.091553 | -0.032044 | -0.050354 | 0.1831 | 0.13733 | 0.045776 | 0.036621 | 0.07782 | 0.068665 | 0.36621 | 122.6303 | 0.16937 | 122.6578 | 122.5479 | 122.4243 | 122.4518 | 122.3923 | -122.5388 | -122.4747 | 122.5342 | 122.6257 | 62.2055 | 62.4023
272.1562 | 122.7722 | -62.2559 | 60.2097 | -0.0051118 | -0.027615 | -0.025177 | 0.063303 | -0.034716 | -0.047604 | -0.040819 | -0.0021057 | -0.022458 | 0.054064 | 0.046049 | -0.21424 | -0.020051 | -0.023894 | -0.073242 | 60.1776 | -62.3749 | 60.26 | -62.0132 | -62.4573 | -62.4252 | 0.10071 | 60.1456 | -62.2696 | 60.3699 | -62.1323 | -62.2284 | -62.2147 | -0.11902 | -0.032044 | 0.050354 | 0.24261 | -0.16937 | -0.20142 | -0.050354 | -0.082397 | -0.013733 | -0.064087 | 0.16022 | 0.1236 | 0.041198 | 0.027465 | 0.054931 | 0.041198 | 0.36163 | 122.6349 | 0.13733 | 122.6395 | 122.5525 | 122.4152 | 122.4335 | 122.4014 | -122.5845 | -122.4792 | 122.5159 | 122.6257 | 62.1826 | 62.3566
273.9219 | 122.7722 | -62.2421 | 60.2325 | 0.0025177 | -0.029965 | -0.026886 | 0.061594 | -0.03258 | -0.049954 | -0.039324 | 0.00094606 | -0.019895 | 0.054277 | 0.049253 | -0.21659 | -0.017914 | -0.021758 | 0.013733 | 60.1913 | -62.3566 | 60.3149 | -61.9583 | -62.4207 | -62.3932 | 0.1831 | 60.1456 | -62.2513 | 60.3745 | -62.1094 | -62.2055 | -62.2101 | -0.11444 | -0.041199 | 0.082397 | 0.28381 | -0.15106 | -0.17853 | -0.036621 | -0.064087 | -0.009156 | -0.086975 | 0.14191 | 0.13275 | 0.032043 | 0.036621 | 0.041199 | 0.045777 | 0.39825 | 122.6715 | 0.14191 | 122.6257 | 122.5479 | 122.3969 | 122.4335 | 122.3877 | -122.5891 | -122.4838 | 122.5571 | 122.6166 | 62.2559 | 62.4252
275.7031 | 122.6669 | -62.2467 | 60.2737 | -0.012741 | -0.027188 | -0.026459 | 0.067575 | -0.033861 | -0.048031 | -0.039751 | -0.0051575 | -0.018827 | 0.055132 | 0.055234 | -0.21509 | -0.017914 | -0.021117 | -0.022888 | 60.26 | -62.3749 | 60.1913 | -62.1185 | -62.5534 | -62.5259 | 0.004578 | 60.2188 | -62.2742 | 60.2875 | -62.2147 | -62.3428 | -62.2879 | -0.12817 | -0.013733 | -0.082398 | 0.12817 | -0.27924 | -0.3067 | -0.15106 | -0.17853 | -0.027466 | -0.054932 | 0.013733 | 0.032043 | -0.041199 | -0.09613 | -0.013733 | -0.068664 | 0.25635 | 122.5662 | 0.059509 | 122.5616 | 122.6349 | 122.493 | 122.5067 | 122.4655 | -122.6486 | -122.5479 | 122.438 | 122.5342 | 62.2238 | 62.2513
277.4219 | 122.6166 | -62.2833 | 60.2509 | -0.0051118 | -0.024411 | -0.024964 | 0.066294 | -0.025316 | -0.050808 | -0.037615 | 0.00094606 | -0.017331 | 0.055986 | 0.05438 | -0.21488 | -0.016419 | -0.020689 | -0.07782 | 60.2325 | -62.4069 | 60.1639 | -62.1323 | -62.5946 | -62.5534 | -0.068665 | 60.1776 | -62.2971 | 60.2371 | -62.2879 | -62.4115 | -62.3428 | -0.1236 | -0.01831 | -0.086975 | 0.15106 | -0.27008 | -0.31128 | -0.14649 | -0.18768 | -0.013733 | -0.073242 | -0.013732 | -0.004578 | -0.059509 | -0.12817 | -0.045776 | -0.11444 | 0.27466 | 122.5708 | 0.009155 | 122.5342 | 122.6395 | 122.4747 | 122.5159 | 122.4609 | -122.6578 | -122.5479 | 122.4472 | 122.5204 | 62.2055 | 62.2147
279.2031 | 122.7814 | -62.2513 | 60.2005 | -0.0051118 | -0.027615 | -0.026032 | 0.062662 | -0.034716 | -0.048886 | -0.040392 | 0.00094606 | -0.020963 | 0.055986 | 0.044767 | -0.21467 | -0.018128 | -0.022185 | -0.009155 | 60.1685 | -62.3611 | 60.3104 | -61.9354 | -62.4207 | -62.3978 | 0.20142 | 60.1547 | -62.2696 | 60.3745 | -62.0956 | -62.1964 | -62.1964 | -0.10986 | -0.032043 | 0.10986 | 0.31586 | -0.14648 | -0.16937 | -0.036621 | -0.059509 | -0.01831 | -0.045776 | 0.17395 | 0.15564 | 0.054932 | 0.054932 | 0.073242 | 0.073242 | 0.42572 | 122.6715 | 0.17395 | 122.644 | 122.5296 | 122.4243 | 122.4197 | 122.406 | -122.5616 | -122.4701 | 122.5616 | 122.6257 | 62.2421 | 62.4527
280.9844 | 122.7585 | -62.2513 | 60.1959 | -0.012741 | -0.026333 | -0.025391 | 0.063089 | -0.030871 | -0.047817 | -0.04146 | 0.00094606 | -0.020963 | 0.056627 | 0.043912 | -0.21531 | -0.015992 | -0.023253 | -0.13275 | 60.228 | -62.3749 | 60.228 | -62.059 | -62.5351 | -62.4939 | 0.018311 | 60.0998 | -62.3016 | 60.3378 | -62.1643 | -62.2787 | -62.2101 | -0.1236 | 0.032043 | 0.032043 | 0.19226 | -0.24261 | -0.28381 | -0.11902 | -0.16022 | -0.050354 | -0.096131 | 0.14191 | 0.086975 | 0.041199 | -0.027466 | 0.091553 | 0.022888 | 0.31586 | 122.6028 | 0.13733 | 122.6395 | 122.6028 | 122.4014 | 122.4792 | 122.3511 | -122.5708 | -122.4976 | 122.4792 | 122.5891 | 62.1185 | 62.2696
282.7031 | 122.7493 | -62.2467 | 60.1959 | -0.0051118 | -0.027615 | -0.025391 | 0.062662 | -0.031511 | -0.047177 | -0.038683 | 0.0039979 | -0.021176 | 0.055986 | 0.042417 | -0.21595 | -0.019837 | -0.021544 | -0.086975 | 60.1776 | -62.3749 | 60.2417 | -62.0178 | -62.4664 | -62.439 | 0.068665 | 60.1089 | -62.2742 | 60.3378 | -62.1277 | -62.2238 | -62.2238 | -0.12817 | -0.018311 | 0.045776 | 0.22888 | -0.19226 | -0.21973 | -0.064087 | -0.091553 | -0.027466 | -0.086975 | 0.14191 | 0.11902 | 0.022888 | 0.022888 | 0.050354 | 0.050354 | 0.35706 | 122.6166 | 0.14648 | 122.612 | 122.5525 | 122.3831 | 122.4243 | 122.3557 | -122.5708 | -122.4701 | 122.4884 | 122.5845 | 62.1597 | 62.3154
284.5 | 122.7493 | -62.2513 | 60.1868 | 0.0025177 | -0.024411 | -0.024537 | 0.065012 | -0.031939 | -0.047604 | -0.037828 | -0.0021057 | -0.022245 | 0.053636 | 0.049467 | -0.21659 | -0.017487 | -0.023253 | -0.07782 | 60.1364 | -62.3703 | 60.2783 | -62.0087 | -62.4893 | -62.4435 | 0.064087 | 60.0906 | -62.3154 | 60.3424 | -62.146 | -62.2742 | -62.233 | -0.11902 | -0.050354 | 0.091552 | 0.24262 | -0.19226 | -0.23804 | -0.073242 | -0.11902 | -0.064087 | -0.096131 | 0.15564 | 0.10529 | 0.018311 | -0.022888 | 0.082398 | 0.041199 | 0.36163 | 122.6486 | 0.16937 | 122.6578 | 122.5067 | 122.406 | 122.3877 | 122.3419 | -122.5571 | -122.5021 | 122.5296 | 122.5937 | 62.1735 | 62.3154
286.2812 | 122.6486 | -62.2742 | 60.2692 | 0.0025177 | -0.025479 | -0.025177 | 0.06373 | -0.030871 | -0.047604 | -0.039324 | 0.00094606 | -0.021176 | 0.055773 | 0.04733 | -0.21637 | -0.018342 | -0.025816 | 0.018311 | 60.2188 | -62.3566 | 60.2417 | -62.0407 | -62.4939 | -62.4619 | 0.10529 | 60.1913 | -62.265 | 60.2692 | -62.2147 | -62.3337 | -62.3062 | -0.082397 | -0.050354 | -0.027466 | 0.23346 | -0.18768 | -0.21973 | -0.10529 | -0.13733 | 0.009155 | -0.07782 | 0 | 0.059509 | -0.032043 | -0.059509 | -0.041198 | -0.068664 | 0.31586 | 122.5983 | 0.050354 | 122.5342 | 122.5754 | 122.4564 | 122.493 | 122.4655 | -122.6257 | -122.5342 | 122.5159 | 122.5433 | 62.2925 | 62.3795
288.0469 | 122.7173 | -62.265 | 60.2188 | 0.010147 | -0.027829 | -0.026032 | 0.062021 | -0.033648 | -0.048031 | -0.039324 | 0.00094606 | -0.022458 | 0.055345 | 0.046049 | -0.21509 | -0.018128 | -0.021758 | -0.1236 | 60.1639 | -62.352 | 60.2188 | -62.0544 | -62.5122 | -62.4619 | -0.013733 | 60.1181 | -62.3016 | 60.2875 | -62.2009 | -62.2971 | -62.265 | -0.086975 | -0.054932 | 0 | 0.21057 | -0.19684 | -0.24719 | -0.10986 | -0.16022 | -0.036621 | -0.10071 | 0.068665 | 0.064087 | 0 | -0.032043 | 0.036621 | 0.004578 | 0.29755 | 122.5708 | 0.10071 | 122.5891 | 122.5159 | 122.4197 | 122.4289 | 122.3831 | -122.5708 | -122.5204 | 122.4838 | 122.5525 | 62.1414 | 62.2513
289.8281 | 122.7722 | -62.2238 | 60.1959 | -0.0051118 | -0.027829 | -0.026032 | 0.063944 | -0.031511 | -0.048031 | -0.037828 | -0.0021057 | -0.020536 | 0.055986 | 0.047971 | -0.21381 | -0.017701 | -0.02133 | 0.004578 | 60.2051 | -62.3428 | 60.3012 | -61.9492 | -62.4115 | -62.4023 | 0.17395 | 60.1456 | -62.2467 | 60.3699 | -62.0956 | -62.2101 | -62.2101 | -0.11902 | 0.009155 | 0.10529 | 0.27466 | -0.17853 | -0.18768 | -0.05951 | -0.068665 | -0.022888 | -0.050354 | 0.17395 | 0.12817 | 0.013733 | 0.013733 | 0.036621 | 0.036621 | 0.39368 | 122.644 | 0.15106 | 122.6166 | 122.5479 | 122.3923 | 122.4289 | 122.3694 | -122.5388 | -122.4426 | 122.525 | 122.5937 | 62.2284 | 62.3978
291.5469 | 122.6349 | -62.2559 | 60.2463 | 0.0025177 | -0.027188 | -0.026459 | 0.064371 | -0.029802 | -0.048031 | -0.036547 | -0.0051575 | -0.018399 | 0.058336 | 0.048185 | -0.21402 | -0.018982 | -0.019194 | -0.041199 | 60.2325 | -62.352 | 60.1822 | -62.1002 | -62.5351 | -62.4985 | 0.032043 | 60.1868 | -62.265 | 60.2737 | -62.233 | -62.3474 | -62.2971 | -0.096131 | -0.013733 | -0.064087 | 0.15564 | -0.24262 | -0.27924 | -0.14648 | -0.1831 | -0.009156 | -0.059509 | 0.027466 | 0.022888 | -0.041199 | -0.091553 | -0.032043 | -0.082397 | 0.25177 | 122.5342 | 0.032044 | 122.5388 | 122.5845 | 122.4518 | 122.4884 | 122.4426 | -122.5983 | -122.5113 | 122.438 | 122.5296 | 62.2147 | 62.2879
293.3125 | 122.7905 | -62.2421 | 60.1959 | -0.0051118 | -0.030819 | -0.026032 | 0.062235 | -0.035998 | -0.049099 | -0.038256 | -0.0021057 | -0.022885 | 0.057909 | 0.046049 | -0.21552 | -0.01706 | -0.025603 | -0.027466 | 60.1639 | -62.3474 | 60.2829 | -61.9583 | -62.4207 | -62.4069 | 0.1831 | 60.1364 | -62.2559 | 60.3928 | -62.0911 | -62.1872 | -62.1735 | -0.10529 | -0.032044 | 0.086975 | 0.28381 | -0.16479 | -0.17853 | -0.059509 | -0.073242 | -0.013733 | -0.059509 | 0.19684 | 0.15106 | 0.068664 | 0.054931 | 0.082397 | 0.068664 | 0.3891 | 122.6303 | 0.16479 | 122.6486 | 122.5113 | 122.3923 | 122.406 | 122.3785 | -122.5433 | -122.4518 | 122.525 | 122.6349 | 62.2147 | 62.4252
295.0156 | 122.6669 | -62.2559 | 60.26 | -0.0051118 | -0.024411 | -0.024537 | 0.069712 | -0.031511 | -0.048245 | -0.039537 | -0.0051575 | -0.018399 | 0.055773 | 0.056943 | -0.21616 | -0.016846 | -0.021758 | -0.032043 | 60.2325 | -62.352 | 60.2463 | -62.0407 | -62.5259 | -62.4802 | 0.068665 | 60.1868 | -62.2833 | 60.3104 | -62.2055 | -62.3337 | -62.2833 | -0.096131 | -0.027466 | -0.013733 | 0.21515 | -0.22431 | -0.27008 | -0.12817 | -0.17395 | -0.027466 | -0.073242 | 0.050354 | 0.050354 | -0.027466 | -0.07782 | 0 | -0.050354 | 0.31128 | 122.5983 | 0.07782 | 122.5937 | 122.5845 | 122.4701 | 122.4884 | 122.4426 | -122.612 | -122.5433 | 122.5021 | 122.5662 | 62.2238 | 62.3245
296.8125 | 122.6212 | -62.2787 | 60.2463 | 0.0025177 | -0.024411 | -0.023255 | 0.066507 | -0.030871 | -0.047604 | -0.041887 | 0.00094606 | -0.020963 | 0.055773 | 0.04733 | -0.21424 | -0.018555 | -0.020689 | -0.082397 | 60.2188 | -62.3657 | 60.1913 | -62.1002 | -62.5671 | -62.5305 | -0.022888 | 60.1776 | -62.3016 | 60.2554 | -62.2559 | -62.3932 | -62.3108 | -0.086975 | -0.027466 | -0.054932 | 0.17853 | -0.25177 | -0.28839 | -0.16479 | -0.20142 | -0.022888 | -0.068665 | 0.009155 | 0.022889 | -0.032043 | -0.11444 | -0.009155 | -0.091552 | 0.2655 | 122.5571 | 0.045777 | 122.5571 | 122.5845 | 122.4792 | 122.4976 | 122.4564 | -122.612 | -122.5479 | 122.4701 | 122.5342 | 62.1964 | 62.2559
298.5938 | 122.6852 | -62.2787 | 60.2051 | -0.0051118 | -0.02377 | -0.023896 | 0.065225 | -0.032366 | -0.049954 | -0.043383 | 0.00094606 | -0.020749 | 0.055773 | 0.042203 | -0.21317 | -0.019196 | -0.017912 | -0.14648 | 60.2188 | -62.3657 | 60.1639 | -62.1094 | -62.6038 | -62.5534 | -0.068665 | 60.1456 | -62.3062 | 60.2783 | -62.2375 | -62.352 | -62.2879 | -0.086975 | 0.013733 | -0.041199 | 0.16937 | -0.27466 | -0.32501 | -0.18768 | -0.23804 | -0.027465 | -0.059509 | 0.073242 | 0.041199 | -0.009155 | -0.073242 | 0.01831 | -0.045777 | 0.25635 | 122.5296 | 0.068664 | 122.5845 | 122.5845 | 122.4518 | 122.4976 | 122.4243 | -122.5708 | -122.5113 | 122.4426 | 122.5571 | 62.1323 | 62.2101
300.375 | 122.7585 | -62.233 | 60.1685 | 0.010147 | -0.02612 | -0.023041 | 0.065012 | -0.029162 | -0.049954 | -0.040392 | -0.0051575 | -0.019895 | 0.056414 | 0.048185 | -0.21573 | -0.016633 | -0.027312 | -0.09613 | 60.1639 | -62.352 | 60.2737 | -62.0041 | -62.4802 | -62.4435 | 0.054932 | 60.0906 | -62.2879 | 60.347 | -62.1552 | -62.2604 | -62.2147 | -0.11902 | -0.004578 | 0.10529 | 0.22888 | -0.21057 | -0.24719 | -0.091552 | -0.12817 | -0.054932 | -0.07782 | 0.17853 | 0.07782 | 0.01831 | -0.027466 | 0.073242 | 0.027466 | 0.3479 | 122.6257 | 0.13275 | 122.6349 | 122.5159 | 122.3785 | 122.3969 | 122.3236 | -122.5204 | -122.4564 | 122.5067 | 122.58 | 62.1368 | 62.2879
302.0938 | 122.6486 | -62.2696 | 60.2692 | 0.0025177 | -0.024411 | -0.023255 | 0.067362 | -0.031084 | -0.047604 | -0.037828 | 0.00094606 | -0.020963 | 0.053636 | 0.050321 | -0.21488 | -0.016419 | -0.021117 | -0.032043 | 60.2234 | -62.352 | 60.2509 | -62.0316 | -62.5168 | -62.4756 | 0.054932 | 60.1913 | -62.2833 | 60.2921 | -62.2101 | -62.3245 | -62.2696 | -0.082398 | -0.045776 | -0.018311 | 0.23804 | -0.20599 | -0.24719 | -0.1236 | -0.16479 | -0.013733 | -0.07782 | 0.022888 | 0.059509 | 0 | -0.054932 | 0.013733 | -0.041199 | 0.32044 | 122.6028 | 0.073242 | 122.5754 | 122.5754 | 122.4747 | 122.493 | 122.4609 | -122.6212 | -122.5525 | 122.5204 | 122.5616 | 62.2375 | 62.3245
303.875 | 122.7493 | -62.2192 | 60.2142 | 0.0025177 | -0.026974 | -0.024537 | 0.063303 | -0.033434 | -0.049954 | -0.038683 | 0.00094606 | -0.021817 | 0.055986 | 0.046262 | -0.21296 | -0.017914 | -0.024748 | -0.004578 | 60.1685 | -62.3337 | 60.2966 | -61.9446 | -62.4252 | -62.3932 | 0.16022 | 60.1318 | -62.265 | 60.3516 | -62.0956 | -62.2009 | -62.1872 | -0.11444 | -0.045776 | 0.082398 | 0.27466 | -0.17395 | -0.20599 | -0.059509 | -0.091553 | -0.045777 | -0.082397 | 0.13733 | 0.1236 | 0.032043 | 0.01831 | 0.07782 | 0.064087 | 0.3891 | 122.6303 | 0.16937 | 122.6166 | 122.5021 | 122.3969 | 122.3877 | 122.3511 | -122.5479 | -122.4792 | 122.5159 | 122.5708 | 62.2147 | 62.3795
305.5938 | 122.6532 | -62.2375 | 60.2509 | -0.0051118 | -0.023556 | -0.024109 | 0.066507 | -0.031298 | -0.046322 | -0.040605 | -0.0021057 | -0.020322 | 0.056841 | 0.05203 | -0.21637 | -0.016846 | -0.020262 | -0.032043 | 60.2463 | -62.3749 | 60.2234 | -62.0499 | -62.5214 | -62.4893 | 0.059509 | 60.173 | -62.2833 | 60.2783 | -62.2238 | -62.352 | -62.2971 | -0.13733 | -0.004577 | -0.027465 | 0.18768 | -0.25177 | -0.28381 | -0.11444 | -0.14648 | -0.045776 | -0.077819 | 0.027466 | 0.013733 | -0.059509 | -0.11444 | -0.013733 | -0.068665 | 0.32501 | 122.5983 | 0.059509 | 122.5616 | 122.6212 | 122.4564 | 122.4838 | 122.4106 | -122.6257 | -122.5342 | 122.4609 | 122.5159 | 62.2055 | 62.2971
307.375 | 122.6395 | -62.2467 | 60.2371 | -0.0051118 | -0.023343 | -0.024109 | 0.065012 | -0.03322 | -0.047177 | -0.03676 | -0.0021057 | -0.018827 | 0.05385 | 0.050321 | -0.21488 | -0.015351 | -0.022398 | -0.041199 | 60.2417 | -62.3291 | 60.2051 | -62.0728 | -62.5397 | -62.5031 | 0.027466 | 60.1456 | -62.3016 | 60.2692 | -62.2421 | -62.3657 | -62.3062 | -0.082398 | 0.004577 | -0.032044 | 0.17395 | -0.25635 | -0.29297 | -0.17395 | -0.21057 | -0.054932 | -0.091553 | 0.032043 | 0.004578 | -0.059509 | -0.11902 | -0.004577 | -0.064087 | 0.25635 | 122.5342 | 0.05951 | 122.5708 | 122.5708 | 122.4472 | 122.4884 | 122.3923 | -122.5662 | -122.5388 | 122.4518 | 122.5159 | 62.2055 | 62.2742
309.1719 | 122.731 | -62.2467 | 60.1868 | -0.0051118 | -0.027401 | -0.025177 | 0.065653 | -0.031939 | -0.050381 | -0.03676 | 0.00094606 | -0.019254 | 0.055986 | 0.049039 | -0.21381 | -0.01706 | -0.019835 | -0.16479 | 60.2234 | -62.384 | 60.1593 | -62.0911 | -62.59 | -62.5259 | -0.050354 | 60.141 | -62.3108 | 60.3012 | -62.1964 | -62.3245 | -62.2421 | -0.13733 | 0.036621 | -0.027466 | 0.15564 | -0.27924 | -0.34332 | -0.14191 | -0.20599 | -0.064087 | -0.045777 | 0.11444 | 0.050354 | 0.004578 | -0.07782 | 0.068665 | -0.013733 | 0.29297 | 122.5433 | 0.11444 | 122.612 | 122.6074 | 122.4518 | 122.4701 | 122.3877 | -122.5708 | -122.4976 | 122.406 | 122.5479 | 62.0819 | 62.1964
310.8906 | 122.6578 | -62.2604 | 60.2509 | -0.0051118 | -0.025479 | -0.023041 | 0.06373 | -0.031939 | -0.047604 | -0.038896 | -0.0051575 | -0.020749 | 0.056627 | 0.052671 | -0.21723 | -0.016419 | -0.019194 | -0.022888 | 60.2371 | -62.3566 | 60.2417 | -62.0178 | -62.5076 | -62.471 | 0.059509 | 60.1685 | -62.2879 | 60.2921 | -62.2101 | -62.3291 | -62.2604 | -0.09613 | -0.013732 | -0.009155 | 0.24262 | -0.21057 | -0.24719 | -0.11444 | -0.15106 | -0.027466 | -0.082397 | 0.041199 | 0.050354 | 0 | -0.068665 | 0.027466 | -0.041199 | 0.33874 | 122.5983 | 0.07782 | 122.58 | 122.5937 | 122.4564 | 122.4976 | 122.4289 | -122.6074 | -122.5388 | 122.5021 | 122.5525 | 62.2375 | 62.3199
312.6875 | 122.7631 | -62.2467 | 60.2005 | 0.017777 | -0.028683 | -0.026032 | 0.062448 | -0.029802 | -0.048245 | -0.037828 | -0.0021057 | -0.021604 | 0.056414 | 0.050107 | -0.21381 | -0.017273 | -0.02368 | -0.082397 | 60.2005 | -62.3611 | 60.2463 | -61.9949 | -62.4573 | -62.4161 | 0.10071 | 60.1456 | -62.2833 | 60.3378 | -62.114 | -62.2055 | -62.1918 | -0.11444 | 0 | 0.045777 | 0.25177 | -0.16937 | -0.21057 | -0.054932 | -0.09613 | -0.036621 | -0.054931 | 0.13733 | 0.13275 | 0.054932 | 0.041199 | 0.091553 | 0.07782 | 0.36621 | 122.6074 | 0.16937 | 122.6212 | 122.5616 | 122.4289 | 122.4472 | 122.3923 | -122.5616 | -122.4838 | 122.493 | 122.5845 | 62.1643 | 62.3474
314.4062 | 122.6715 | -62.2375 | 60.26 | 0.010147 | -0.027829 | -0.024537 | 0.064157 | -0.029589 | -0.048886 | -0.041674 | 0.00094606 | -0.019254 | 0.053636 | 0.046903 | -0.21552 | -0.016633 | -0.021971 | -0.022888 | 60.2554 | -62.352 | 60.2142 | -62.0499 | -62.4939 | -62.4893 | 0.073242 | 60.1776 | -62.265 | 60.2921 | -62.1826 | -62.3062 | -62.2604 | -0.11444 | -0.004578 | -0.045777 | 0.18768 | -0.25177 | -0.25635 | -0.13733 | -0.14191 | -0.027466 | -0.082398 | 0.032043 | 0.054932 | -0.022888 | -0.068664 | 0.004578 | -0.041198 | 0.30212 | 122.5662 | 0.082398 | 122.5571 | 122.6074 | 122.4426 | 122.493 | 122.4152 | -122.612 | -122.525 | 122.4518 | 122.5296 | 62.2147 | 62.3108
316.1875 | 122.6486 | -62.2421 | 60.2188 | 0.010147 | -0.024838 | -0.025605 | 0.066507 | -0.033007 | -0.04974 | -0.037828 | 0.0039979 | -0.019254 | 0.056841 | 0.040922 | -0.21573 | -0.016205 | -0.021971 | -0.032043 | 60.2463 | -62.3245 | 60.228 | -62.0499 | -62.5122 | -62.4802 | 0.050354 | 60.1868 | -62.2559 | 60.2783 | -62.2147 | -62.3337 | -62.2833 | -0.082398 | 0.027466 | 0.009155 | 0.19226 | -0.23804 | -0.27008 | -0.15564 | -0.18768 | -0.013733 | -0.032043 | 0.059509 | 0.027465 | -0.041199 | -0.091553 | -0.027466 | -0.07782 | 0.27466 | 122.5525 | 0.041198 | 122.5342 | 122.5708 | 122.4426 | 122.4884 | 122.4289 | -122.5433 | -122.4747 | 122.4701 | 122.5204 | 62.2101 | 62.2925
317.9531 | 122.7768 | -62.233 | 60.1593 | 0.0025177 | -0.023983 | -0.02176 | 0.062448 | -0.028093 | -0.046322 | -0.039965 | 0.00094606 | -0.021604 | 0.0562 | 0.04199 | -0.21488 | -0.014924 | -0.022826 | -0.14648 | 60.1959 | -62.352 | 60.2142 | -62.0499 | -62.5305 | -62.4893 | 0.018311 | 60.1181 | -62.3016 | 60.3333 | -62.1735 | -62.2787 | -62.1964 | -0.11902 | 0.036621 | 0.054931 | 0.1831 | -0.25635 | -0.29755 | -0.13733 | -0.17853 | -0.068665 | -0.041199 | 0.17395 | 0.059509 | 0.036621 | -0.045777 | 0.10529 | 0.022888 | 0.30212 | 122.5662 | 0.12817 | 122.6349 | 122.5479 | 122.4197 | 122.4289 | 122.3511 | -122.5113 | -122.4609 | 122.4472 | 122.5662 | 62.0865 | 62.2513
319.6719 | 122.6257 | -62.2284 | 60.2554 | 0.010147 | -0.029324 | -0.026886 | 0.063516 | -0.028307 | -0.050381 | -0.038256 | -0.0021057 | -0.01904 | 0.054705 | 0.048398 | -0.21274 | -0.018128 | -0.024535 | -0.045776 | 60.2646 | -62.352 | 60.1822 | -62.0956 | -62.5259 | -62.5122 | 0.013733 | 60.1913 | -62.2787 | 60.2463 | -62.2147 | -62.3428 | -62.2696 | -0.1236 | 0.009155 | -0.073242 | 0.13275 | -0.28381 | -0.29755 | -0.16022 | -0.17395 | -0.050354 | -0.064087 | -0.009155 | 0.013733 | -0.041198 | -0.11444 | 0.009156 | -0.064086 | 0.25635 | 122.5342 | 0.064087 | 122.525 | 122.6166 | 122.4701 | 122.493 | 122.4197 | -122.6074 | -122.5342 | 122.4106 | 122.4747 | 62.1826 | 62.2421
321.4531 | 122.6532 | -62.2513 | 60.2646 | -0.0051118 | -0.028683 | -0.024964 | 0.062235 | -0.034502 | -0.050595 | -0.038469 | -0.0021057 | -0.020322 | 0.055132 | 0.046049 | -0.21167 | -0.017273 | -0.021544 | 0.004578 | 60.2051 | -62.3337 | 60.2371 | -62.0041 | -62.4527 | -62.4207 | 0.10071 | 60.173 | -62.2696 | 60.2692 | -62.1964 | -62.3016 | -62.2833 | -0.082397 | -0.059509 | -0.027465 | 0.24719 | -0.16937 | -0.20142 | -0.086975 | -0.11902 | -0.01831 | -0.091552 | 0.004578 | 0.054932 | -0.032043 | -0.050354 | -0.013733 | -0.032044 | 0.32959 | 122.5708 | 0.073242 | 122.5388 | 122.5388 | 122.4426 | 122.4564 | 122.4243 | -122.5983 | -122.5342 | 122.4884 | 122.5204 | 62.2559 | 62.352
323.2344 | 122.7631 | -62.233 | 60.2234 | 0.0025177 | -0.02911 | -0.025391 | 0.06373 | -0.029589 | -0.051022 | -0.039324 | -0.0021057 | -0.023099 | 0.054918 | 0.042844 | -0.21595 | -0.018342 | -0.019621 | -0.004578 | 60.1822 | -62.3566 | 60.3012 | -61.9263 | -62.3886 | -62.3566 | 0.17395 | 60.141 | -62.2375 | 60.3516 | -62.0773 | -62.1918 | -62.1826 | -0.1236 | -0.041199 | 0.077819 | 0.3067 | -0.1236 | -0.15564 | 0 | -0.032044 | -0.004578 | -0.082398 | 0.12817 | 0.15564 | 0.050354 | 0.041199 | 0.054932 | 0.045777 | 0.4303 | 122.6578 | 0.16022 | 122.5891 | 122.5388 | 122.3785 | 122.4152 | 122.374 | -122.58 | -122.4609 | 122.5342 | 122.5845 | 62.2284 | 62.4069
325.0156 | 122.7493 | -62.2421 | 60.1685 | 0.0025177 | -0.025265 | -0.023896 | 0.062876 | -0.034289 | -0.048886 | -0.039537 | 0.00094606 | -0.019467 | 0.054918 | 0.046689 | -0.21552 | -0.018128 | -0.023253 | -0.11444 | 60.141 | -62.3611 | 60.2646 | -61.9904 | -62.471 | -62.4207 | 0.059509 | 60.0861 | -62.2742 | 60.3195 | -62.1506 | -62.2604 | -62.2284 | -0.11902 | -0.027466 | 0.09613 | 0.25177 | -0.17853 | -0.22888 | -0.059509 | -0.10986 | -0.032044 | -0.082397 | 0.15106 | 0.091552 | 0.013732 | -0.018311 | 0.045776 | 0.013733 | 0.37079 | 122.6257 | 0.1236 | 122.5937 | 122.5021 | 122.3602 | 122.3831 | 122.3282 | -122.5296 | -122.4426 | 122.5067 | 122.5616 | 62.1277 | 62.3016
326.7969 | 122.6578 | -62.2421 | 60.2966 | 0.017777 | -0.027401 | -0.023041 | 0.064585 | -0.034289 | -0.047177 | -0.039324 | 0.00094606 | -0.020322 | 0.057695 | 0.052244 | -0.21531 | -0.015565 | -0.025603 | -0.032043 | 60.2325 | -62.3703 | 60.173 | -62.0773 | -62.5031 | -62.4802 | 0.027466 | 60.2005 | -62.2604 | 60.2829 | -62.1964 | -62.3199 | -62.265 | -0.12817 | -0.064087 | -0.1236 | 0.16479 | -0.23804 | -0.26093 | -0.10986 | -0.13275 | -0.018311 | -0.096131 | -0.013733 | 0.045776 | -0.022889 | -0.07782 | -0.004578 | -0.059509 | 0.29297 | 122.5433 | 0.064087 | 122.5433 | 122.6028 | 122.4609 | 122.4747 | 122.4426 | -122.6669 | -122.5571 | 122.4152 | 122.525 | 62.2101 | 62.2696
328.5 | 122.7448 | -62.2467 | 60.1868 | -0.0051118 | -0.025051 | -0.026886 | 0.061808 | -0.03258 | -0.047604 | -0.039324 | -0.0021057 | -0.020322 | 0.056414 | 0.046903 | -0.21509 | -0.018128 | -0.024962 | -0.086975 | 60.1822 | -62.3474 | 60.2142 | -62.0178 | -62.4893 | -62.4481 | 0.054932 | 60.1181 | -62.2604 | 60.3287 | -62.1506 | -62.2421 | -62.2101 | -0.10071 | -0.004578 | 0.027465 | 0.22888 | -0.20142 | -0.24262 | -0.10071 | -0.14191 | -0.013733 | -0.068665 | 0.14191 | 0.09613 | 0.036621 | 0.004578 | 0.050354 | 0.018311 | 0.32959 | 122.5616 | 0.10986 | 122.5891 | 122.5296 | 122.3785 | 122.4289 | 122.3648 | -122.5342 | -122.4472 | 122.4609 | 122.5754 | 62.1597 | 62.3016
330.2812 | 122.6212 | -62.2696 | 60.2371 | 0.0025177 | -0.026333 | -0.02176 | 0.065012 | -0.029589 | -0.049954 | -0.039324 | -0.0021057 | -0.019467 | 0.055986 | 0.048398 | -0.21595 | -0.01706 | -0.020903 | -0.12817 | 60.2371 | -62.3795 | 60.1273 | -62.1643 | -62.6266 | -62.5763 | -0.086975 | 60.1685 | -62.2833 | 60.2325 | -62.2971 | -62.4115 | -62.3199 | -0.10986 | 0 | -0.10986 | 0.10529 | -0.3067 | -0.35706 | -0.19684 | -0.24719 | -0.013733 | -0.068665 | -0.004578 | -0.027466 | -0.050354 | -0.14191 | -0.036621 | -0.12817 | 0.21515 | 122.5067 | -0.013733 | 122.5159 | 122.6166 | 122.4518 | 122.5067 | 122.438 | -122.6166 | -122.5204 | 122.3969 | 122.5021 | 62.1414 | 62.1826
332.0625 | 122.7493 | -62.2559 | 60.1822 | 0.0025177 | -0.023983 | -0.02475 | 0.067575 | -0.03258 | -0.049526 | -0.040605 | 0.00094606 | -0.022458 | 0.0562 | 0.046476 | -0.21531 | -0.016846 | -0.02368 | -0.13275 | 60.1639 | -62.3749 | 60.2325 | -62.0224 | -62.4985 | -62.4573 | 0.022888 | 60.1135 | -62.2787 | 60.3424 | -62.1506 | -62.2787 | -62.1964 | -0.11902 | -0.018311 | 0.050354 | 0.23346 | -0.20142 | -0.24262 | -0.082397 | -0.1236 | -0.022889 | -0.068665 | 0.16022 | 0.10529 | 0.059509 | -0.022889 | 0.082398 | 0 | 0.35248 | 122.6074 | 0.12817 | 122.6212 | 122.5388 | 122.3923 | 122.4197 | 122.3694 | -122.5571 | -122.4609 | 122.4884 | 122.5983 | 62.1231 | 62.2787
333.8438 | 122.7173 | -62.2284 | 60.1959 | 0.0025177 | -0.02911 | -0.026032 | 0.061594 | -0.023821 | -0.049099 | -0.038896 | 0.00094606 | -0.022458 | 0.054705 | 0.048185 | -0.21573 | -0.019623 | -0.022612 | -0.091553 | 60.1868 | -62.3611 | 60.2005 | -62.0544 | -62.5031 | -62.4573 | 0.022888 | 60.1318 | -62.2925 | 60.3149 | -62.1552 | -62.2696 | -62.2467 | -0.13275 | -0.009155 | 0.004577 | 0.17395 | -0.22888 | -0.27466 | -0.09613 | -0.14191 | -0.064086 | -0.064087 | 0.11902 | 0.073243 | -0.01831 | -0.041198 | 0.045776 | 0.022888 | 0.3067 | 122.5616 | 0.13733 | 122.6074 | 122.5479 | 122.4243 | 122.4152 | 122.3602 | -122.5571 | -122.4884 | 122.4289 | 122.5433 | 62.1368 | 62.2513
335.6094 | 122.7127 | -62.233 | 60.2371 | -0.0051118 | -0.026974 | -0.0271 | 0.063303 | -0.029375 | -0.051876 | -0.038042 | -0.0021057 | -0.019681 | 0.055132 | 0.046262 | -0.21552 | -0.018982 | -0.023039 | 0.009155 | 60.1593 | -62.3703 | 60.2921 | -61.94 | -62.4115 | -62.3795 | 0.15564 | 60.1547 | -62.265 | 60.3241 | -62.1094 | -62.2147 | -62.2055 | -0.13733 | -0.07782 | 0.054931 | 0.29297 | -0.14648 | -0.17853 | -0.009156 | -0.041199 | -0.032044 | -0.082398 | 0.086975 | 0.1236 | 0.027466 | 0.01831 | 0.05951 | 0.050354 | 0.4303 | 122.6624 | 0.15564 | 122.5891 | 122.5296 | 122.4197 | 122.3923 | 122.3877 | -122.6074 | -122.5021 | 122.525 | 122.5571 | 62.2421 | 62.3886
337.3281 | 122.7036 | -62.265 | 60.1868 | -0.0051118 | -0.024411 | -0.023896 | 0.062448 | -0.03023 | -0.046536 | -0.038256 | 0.0039979 | -0.020963 | 0.053209 | 0.047971 | -0.21616 | -0.018342 | -0.022398 | -0.10986 | 60.1685 | -62.352 | 60.228 | -62.0132 | -62.5214 | -62.4527 | 0.036621 | 60.0952 | -62.3016 | 60.3058 | -62.1735 | -62.2742 | -62.2421 | -0.086975 | -0.018311 | 0.041198 | 0.25177 | -0.18768 | -0.25635 | -0.10071 | -0.16937 | -0.036621 | -0.091553 | 0.11902 | 0.091553 | 0.022889 | -0.009155 | 0.05951 | 0.027466 | 0.33875 | 122.58 | 0.12817 | 122.6074 | 122.5204 | 122.3969 | 122.4335 | 122.3602 | -122.5388 | -122.4884 | 122.493 | 122.5708 | 62.1552 | 62.3016
339.1094 | 122.644 | -62.2559 | 60.2371 | 0.0025177 | -0.022488 | -0.024323 | 0.067789 | -0.028948 | -0.049313 | -0.039537 | -0.0051575 | -0.018186 | 0.055132 | 0.058225 | -0.21573 | -0.016205 | -0.022398 | -0.036621 | 60.2142 | -62.352 | 60.2188 | -62.0407 | -62.5351 | -62.4893 | 0.045776 | 60.1776 | -62.2742 | 60.2646 | -62.2101 | -62.352 | -62.2787 | -0.096131 | -0.022889 | -0.018311 | 0.21515 | -0.23346 | -0.27924 | -0.13733 | -0.1831 | -0.018311 | -0.05951 | 0.027465 | 0.045776 | -0.022889 | -0.096131 | -0.004578 | -0.07782 | 0.31128 | 122.5708 | 0.064087 | 122.5388 | 122.5662 | 122.4518 | 122.4701 | 122.4335 | -122.5891 | -122.5113 | 122.4747 | 122.5204 | 62.2192 | 62.3016
340.8281 | 122.612 | -62.233 | 60.26 | -0.0051118 | -0.028256 | -0.025605 | 0.063516 | -0.033434 | -0.049526 | -0.039537 | -0.0051575 | -0.020108 | 0.055773 | 0.04733 | -0.2136 | -0.018342 | -0.020903 | -0.050354 | 60.228 | -62.3566 | 60.1776 | -62.059 | -62.5259 | -62.4847 | 0.036621 | 60.2005 | -62.2467 | 60.2417 | -62.2192 | -62.3291 | -62.2879 | -0.1236 | -0.032044 | -0.082398 | 0.17395 | -0.25177 | -0.29297 | -0.12817 | -0.16937 | -0.013733 | -0.05951 | -0.018311 | 0.013733 | -0.054932 | -0.096131 | -0.041199 | -0.082398 | 0.29755 | 122.5342 | 0.027466 | 122.4884 | 122.5845 | 122.4472 | 122.4609 | 122.4335 | -122.6166 | -122.5067 | 122.4106 | 122.4747 | 62.1826 | 62.2696
342.6094 | 122.7493 | -62.2421 | 60.173 | 0.010147 | -0.027188 | -0.022828 | 0.064585 | -0.031084 | -0.04974 | -0.041246 | -0.0021057 | -0.021176 | 0.054918 | 0.054594 | -0.21595 | -0.018342 | -0.023467 | -0.086975 | 60.1456 | -62.3383 | 60.2417 | -61.9904 | -62.4893 | -62.4298 | 0.059509 | 60.0998 | -62.2787 | 60.3333 | -62.1368 | -62.2604 | -62.2009 | -0.096131 | -0.027466 | 0.068664 | 0.25177 | -0.18768 | -0.24719 | -0.091553 | -0.15106 | -0.036622 | -0.073243 | 0.16022 | 0.10529 | 0.041198 | -0.018311 | 0.07782 | 0.018311 | 0.3479 | 122.58 | 0.14191 | 122.612 | 122.4838 | 122.3785 | 122.3877 | 122.3419 | -122.5113 | -122.4518 | 122.4838 | 122.5754 | 62.1552 | 62.3016
344.375 | 122.644 | -62.2375 | 60.26 | 0.0025177 | -0.025051 | -0.024537 | 0.065653 | -0.03258 | -0.049954 | -0.041887 | 0.00094606 | -0.020536 | 0.054705 | 0.048826 | -0.21616 | -0.018769 | -0.021758 | -0.036621 | 60.2463 | -62.3749 | 60.1639 | -62.0819 | -62.5305 | -62.5122 | 0.036621 | 60.1959 | -62.265 | 60.2646 | -62.1872 | -62.3016 | -62.2604 | -0.13733 | -0.013733 | -0.096131 | 0.15564 | -0.27466 | -0.29297 | -0.13733 | -0.15564 | -0.027466 | -0.064087 | 0.004577 | 0.050354 | -0.022888 | -0.064087 | 0.004578 | -0.036621 | 0.29297 | 122.5388 | 0.07782 | 122.5296 | 122.6212 | 122.4609 | 122.4838 | 122.4335 | -122.6349 | -122.525 | 122.4014 | 122.5021 | 62.2009 | 62.2742
346.0938 | 122.7081 | -62.2238 | 60.1959 | -0.0051118 | -0.028256 | -0.026459 | 0.062876 | -0.033861 | -0.050167 | -0.038256 | 0.00094606 | -0.023526 | 0.057482 | 0.054166 | -0.21531 | -0.018769 | -0.022185 | 0.013733 | 60.1776 | -62.3245 | 60.2875 | -61.9629 | -62.4207 | -62.384 | 0.14648 | 60.1318 | -62.2421 | 60.3241 | -62.1094 | -62.2192 | -62.1918 | -0.10071 | -0.018311 | 0.091553 | 0.26093 | -0.16022 | -0.19684 | -0.059509 | -0.09613 | -0.01831 | -0.064087 | 0.12817 | 0.11444 | 0.032044 | 0.004578 | 0.050354 | 0.022888 | 0.36163 | 122.612 | 0.13275 | 122.5662 | 122.5021 | 122.374 | 122.4014 | 122.3557 | -122.5204 | -122.438 | 122.5113 | 122.5479 | 62.2375 | 62.3703
347.875 | 122.6761 | -62.2238 | 60.2325 | 0.0025177 | -0.028042 | -0.025605 | 0.062448 | -0.030871 | -0.048245 | -0.037828 | -0.0021057 | -0.018827 | 0.0562 | 0.052671 | -0.21274 | -0.016419 | -0.025603 | 0.013733 | 60.1822 | -62.3383 | 60.2646 | -61.9583 | -62.4115 | -62.3886 | 0.16937 | 60.1501 | -62.2513 | 60.3149 | -62.1277 | -62.2284 | -62.2192 | -0.11444 | -0.050354 | 0.032043 | 0.2655 | -0.16479 | -0.18768 | -0.050354 | -0.073242 | -0.027466 | -0.082398 | 0.082397 | 0.09613 | 0.004578 | -0.004578 | 0.032044 | 0.022888 | 0.37994 | 122.6028 | 0.1236 | 122.5662 | 122.5204 | 122.4014 | 122.406 | 122.374 | -122.5708 | -122.4838 | 122.4884 | 122.5388 | 62.2375 | 62.3932
349.6719 | 122.6852 | -62.2284 | 60.2005 | -0.012741 | -0.028897 | -0.023469 | 0.06373 | -0.028521 | -0.052731 | -0.042742 | -0.0021057 | -0.020963 | 0.0562 | 0.045621 | -0.21744 | -0.017487 | -0.019621 | -0.1236 | 60.1593 | -62.3291 | 60.1959 | -62.0407 | -62.4985 | -62.4664 | 0.004578 | 60.0998 | -62.2742 | 60.2737 | -62.1872 | -62.2879 | -62.2421 | -0.10071 | -0.041198 | -0.004577 | 0.18768 | -0.23804 | -0.27008 | -0.13733 | -0.16937 | -0.045776 | -0.10071 | 0.073243 | 0.041199 | -0.013732 | -0.059509 | 0.032044 | -0.013733 | 0.28839 | 122.525 | 0.086975 | 122.5479 | 122.4884 | 122.374 | 122.3877 | 122.3282 | -122.5296 | -122.4747 | 122.4243 | 122.5021 | 62.1048 | 62.233
351.4531 | 122.6944 | -62.2604 | 60.1822 | -0.0051118 | -0.028683 | -0.02475 | 0.064798 | -0.031939 | -0.047817 | -0.041674 | 0.00094606 | -0.020536 | 0.057695 | 0.050962 | -0.21467 | -0.018555 | -0.023253 | -0.11902 | 60.1593 | -62.3749 | 60.2005 | -62.0407 | -62.5031 | -62.4527 | 0.009155 | 60.1227 | -62.2879 | 60.2875 | -62.1918 | -62.2971 | -62.2513 | -0.11444 | -0.022888 | 0.01831 | 0.21973 | -0.19226 | -0.24261 | -0.07782 | -0.12817 | -0.027466 | -0.059509 | 0.10529 | 0.068665 | 0.009155 | -0.036621 | 0.036621 | -0.009155 | 0.33417 | 122.5754 | 0.096131 | 122.5754 | 122.5342 | 122.4106 | 122.4197 | 122.3831 | -122.5571 | -122.4701 | 122.4609 | 122.5479 | 62.1414 | 62.2696
353.1719 | 122.7539 | -62.2147 | 60.173 | 0.0025177 | -0.023556 | -0.024537 | 0.066294 | -0.029589 | -0.049313 | -0.038469 | 0.00094606 | -0.020108 | 0.054705 | 0.053953 | -0.21573 | -0.019623 | -0.019621 | -0.15106 | 60.173 | -62.3932 | 60.1959 | -62.059 | -62.5351 | -62.4893 | 0.004578 | 60.0998 | -62.2742 | 60.3287 | -62.1643 | -62.2787 | -62.1964 | -0.17853 | 0 | 0.022888 | 0.15564 | -0.27466 | -0.32043 | -0.096131 | -0.14191 | -0.059509 | -0.073243 | 0.15564 | 0.050354 | 0.018311 | -0.064087 | 0.07782 | -0.004578 | 0.33417 | 122.5891 | 0.10986 | 122.6028 | 122.5662 | 122.374 | 122.3877 | 122.3145 | -122.5662 | -122.4472 | 122.4106 | 122.5433 | 62.0636 | 62.2192
354.9531 | 122.6669 | -62.2375 | 60.2188 | 0.010147 | -0.024197 | -0.025391 | 0.066507 | -0.032366 | -0.049526 | -0.039324 | 0.00094606 | -0.018613 | 0.056627 | 0.045408 | -0.21467 | -0.01706 | -0.020262 | 0 | 60.2554 | -62.3428 | 60.2234 | -62.0178 | -62.5031 | -62.4802 | 0.07782 | 60.2005 | -62.2696 | 60.3058 | -62.1643 | -62.2925 | -62.2421 | -0.10529 | 0.036621 | 0.004578 | 0.21973 | -0.24262 | -0.2655 | -0.13733 | -0.16022 | -0.032043 | -0.018311 | 0.086975 | 0.073242 | -0.004577 | -0.054931 | 0.027466 | -0.022888 | 0.32501 | 122.5662 | 0.10529 | 122.5754 | 122.5983 | 122.4701 | 122.493 | 122.438 | -122.5616 | -122.4884 | 122.4609 | 122.5433 | 62.2375 | 62.3154
356.6719 | 122.6349 | -62.2513 | 60.2417 | 0.010147 | -0.027188 | -0.0271 | 0.064371 | -0.032366 | -0.050595 | -0.039324 | 0.00094606 | -0.020108 | 0.055559 | 0.054166 | -0.21531 | -0.016846 | -0.020262 | -0.032043 | 60.2463 | -62.3383 | 60.173 | -62.0773 | -62.5031 | -62.4756 | 0.036621 | 60.1913 | -62.2513 | 60.2737 | -62.1735 | -62.3108 | -62.2467 | -0.086975 | 0.004578 | -0.068664 | 0.17395 | -0.2243 | -0.25177 | -0.13733 | -0.16479 | 0 | -0.050354 | 0.032044 | 0.07782 | 0.004578 | -0.059509 | 0.004578 | -0.059509 | 0.26093 | 122.5113 | 0.07782 | 122.525 | 122.5845 | 122.4426 | 122.4976 | 122.4426 | -122.58 | -122.493 | 122.4243 | 122.525 | 62.2192 | 62.2879
358.4375 | 122.7493 | -62.2101 | 60.1868 | -0.0051118 | -0.028042 | -0.024964 | 0.063303 | -0.032366 | -0.045895 | -0.040178 | 0.0039979 | -0.022458 | 0.055132 | 0.049894 | -0.21552 | -0.015992 | -0.019621 | -0.041199 | 60.1456 | -62.3474 | 60.2783 | -61.94 | -62.4115 | -62.3703 | 0.16022 | 60.1227 | -62.2375 | 60.3561 | -62.0819 | -62.2009 | -62.178 | -0.13733 | -0.041199 | 0.091552 | 0.27008 | -0.16022 | -0.20142 | -0.022888 | -0.064087 | -0.027466 | -0.064087 | 0.16937 | 0.12817 | 0.032043 | 0.009155 | 0.059509 | 0.036621 | 0.40741 | 122.6257 | 0.15564 | 122.5937 | 122.493 | 122.3602 | 122.3557 | 122.3328 | -122.5342 | -122.4243 | 122.4884 | 122.5662 | 62.1689 | 62.3703
360.2188 | 122.699 | -62.2147 | 60.1959 | 0.0025177 | -0.028469 | -0.025391 | 0.062021 | -0.031939 | -0.048458 | -0.038042 | -0.0021057 | -0.022245 | 0.055345 | 0.047117 | -0.21552 | -0.017701 | -0.022612 | -0.11902 | 60.1639 | -62.3657 | 60.1776 | -62.0407 | -62.5122 | -62.471 | 0.013733 | 60.1227 | -62.2742 | 60.2646 | -62.1872 | -62.2833 | -62.2375 | -0.15106 | -0.032044 | -0.018311 | 0.17395 | -0.25635 | -0.29755 | -0.10528 | -0.14648 | -0.059509 | -0.073242 | 0.068664 | 0.027466 | -0.022888 | -0.068664 | 0.036621 | -0.009155 | 0.32501 | 122.5433 | 0.086975 | 122.5388 | 122.5296 | 122.3969 | 122.3785 | 122.3373 | -122.5616 | -122.4701 | 122.3923 | 122.4792 | 62.0956 | 62.2284
362.0156 | 122.6715 | -62.2513 | 60.173 | -0.0051118 | -0.024197 | -0.026246 | 0.067362 | -0.031084 | -0.048245 | -0.039965 | -0.0021057 | -0.018827 | 0.0562 | 0.050748 | -0.21467 | -0.015992 | -0.021971 | -0.15564 | 60.1959 | -62.3566 | 60.1456 | -62.1094 | -62.5717 | -62.5305 | -0.064087 | 60.1227 | -62.2971 | 60.2737 | -62.2101 | -62.3291 | -62.265 | -0.10528 | 0.022888 | -0.027466 | 0.14191 | -0.27924 | -0.32043 | -0.17395 | -0.21515 | -0.045776 | -0.050354 | 0.10071 | 0.041199 | -0.013733 | -0.07782 | 0.032043 | -0.032044 | 0.24719 | 122.5021 | 0.086975 | 122.5708 | 122.5525 | 122.4197 | 122.4472 | 122.374 | -122.5296 | -122.4701 | 122.3969 | 122.525 | 62.0956 | 62.1872
363.75 | 122.7356 | -62.2147 | 60.2051 | 0.0025177 | -0.027188 | -0.025177 | 0.063303 | -0.031084 | -0.048886 | -0.041246 | 0.00094606 | -0.02374 | 0.054918 | 0.053525 | -0.21509 | -0.01706 | -0.022612 | -0.050354 | 60.1547 | -62.3657 | 60.2509 | -61.9675 | -62.4207 | -62.3703 | 0.15106 | 60.1089 | -62.2513 | 60.3607 | -62.1002 | -62.1826 | -62.1826 | -0.15106 | -0.050354 | 0.045776 | 0.24719 | -0.15564 | -0.20599 | -0.004577 | -0.054931 | -0.036621 | -0.09613 | 0.15564 | 0.11444 | 0.032044 | 0.032044 | 0.068665 | 0.068665 | 0.39826 | 122.6166 | 0.15106 | 122.612 | 122.5204 | 122.3602 | 122.3694 | 122.3236 | -122.5708 | -122.4564 | 122.4655 | 122.5754 | 62.1643 | 62.3657
365.5156 | 122.6715 | -62.2559 | 60.1868 | -0.012741 | -0.026974 | -0.0271 | 0.064371 | -0.035357 | -0.049954 | -0.040819 | 0.00094606 | -0.022458 | 0.054918 | 0.046689 | -0.21573 | -0.016846 | -0.024321 | -0.13733 | 60.173 | -62.3657 | 60.2005 | -62.0499 | -62.4985 | -62.4619 | -0.009155 | 60.1044 | -62.2696 | 60.2737 | -62.1872 | -62.2742 | -62.233 | -0.10986 | -0.013733 | 0.013732 | 0.20599 | -0.20599 | -0.24262 | -0.09613 | -0.13275 | -0.013733 | -0.082398 | 0.086975 | 0.068664 | 0.022888 | -0.018311 | 0.036621 | -0.004578 | 0.31586 | 122.5662 | 0.082397 | 122.5433 | 122.5388 | 122.374 | 122.4289 | 122.3602 | -122.5525 | -122.4564 | 122.4564 | 122.5296 | 62.1185 | 62.2467
367.2969 | 122.6028 | -62.2375 | 60.2646 | -0.012741 | -0.027615 | -0.025391 | 0.062876 | -0.034716 | -0.051022 | -0.038683 | 0.0039979 | -0.018186 | 0.057695 | 0.044553 | -0.2136 | -0.016205 | -0.023467 | -0.041199 | 60.2325 | -62.3383 | 60.1776 | -62.0544 | -62.5214 | -62.4893 | 0.041199 | 60.1776 | -62.2925 | 60.2325 | -62.2055 | -62.2925 | -62.2925 | -0.10071 | -0.032043 | -0.086975 | 0.18311 | -0.25177 | -0.28381 | -0.15106 | -0.18311 | -0.054931 | -0.086975 | -0.032043 | 0.032044 | -0.054931 | -0.054931 | 0 | 0 | 0.28381 | 122.5159 | 0.086975 | 122.525 | 122.5708 | 122.4701 | 122.4701 | 122.4152 | -122.6028 | -122.5571 | 122.4152 | 122.4701 | 62.1964 | 62.2787
369.0781 | 122.5937 | -62.2513 | 60.2646 | 0.0025177 | -0.028469 | -0.02475 | 0.064798 | -0.025316 | -0.049526 | -0.038896 | 0.0039979 | -0.020108 | 0.055986 | 0.050321 | -0.21424 | -0.018128 | -0.024535 | -0.064087 | 60.2325 | -62.3566 | 60.173 | -62.0682 | -62.5122 | -62.4939 | 0.018311 | 60.2142 | -62.2421 | 60.2371 | -62.1918 | -62.3245 | -62.2925 | -0.10528 | -0.032043 | -0.091552 | 0.18311 | -0.24261 | -0.26092 | -0.13733 | -0.15564 | 0.009156 | -0.050354 | -0.027465 | 0.05951 | -0.041198 | -0.073242 | -0.050354 | -0.082398 | 0.28839 | 122.5296 | 0.050354 | 122.4792 | 122.5891 | 122.4564 | 122.4838 | 122.4655 | -122.6212 | -122.5067 | 122.4243 | 122.4884 | 62.1872 | 62.2696
370.7969 | 122.7173 | -62.2238 | 60.1639 | -0.0051118 | -0.027401 | -0.026886 | 0.06373 | -0.03792 | -0.050167 | -0.042314 | -0.0021057 | -0.020536 | 0.057482 | 0.045408 | -0.21381 | -0.016205 | -0.02368 | -0.091553 | 60.1776 | -62.352 | 60.1959 | -62.027 | -62.4802 | -62.439 | 0.036621 | 60.1135 | -62.2742 | 60.2921 | -62.146 | -62.2421 | -62.2009 | -0.12817 | 0.013733 | 0.032044 | 0.19684 | -0.21515 | -0.25635 | -0.086975 | -0.12817 | -0.050354 | -0.050354 | 0.12817 | 0.07782 | 0.022888 | -0.01831 | 0.073242 | 0.032044 | 0.32501 | 122.5479 | 0.12817 | 122.5662 | 122.5296 | 122.3877 | 122.4014 | 122.3373 | -122.5159 | -122.438 | 122.4197 | 122.5159 | 62.1323 | 62.2604
372.5781 | 122.6028 | -62.233 | 60.26 | 0.0025177 | -0.027401 | -0.026032 | 0.066507 | -0.029375 | -0.049526 | -0.039324 | -0.0082091 | -0.020322 | 0.055773 | 0.050321 | -0.21445 | -0.018555 | -0.021758 | -0.032043 | 60.2509 | -62.3474 | 60.1593 | -62.0865 | -62.5076 | -62.4893 | 0.027466 | 60.1822 | -62.2833 | 60.2463 | -62.2101 | -62.3291 | -62.2742 | -0.11444 | -0.009156 | -0.10071 | 0.14648 | -0.25635 | -0.27466 | -0.14191 | -0.16022 | -0.050354 | -0.07782 | -0.013733 | 0.022888 | -0.041199 | -0.096131 | 0.009155 | -0.045777 | 0.26093 | 122.5067 | 0.073242 | 122.5296 | 122.5983 | 122.4655 | 122.4838 | 122.4152 | -122.6074 | -122.5433 | 122.3923 | 122.4792 | 62.2009 | 62.2604
374.3594 | 122.7448 | -62.2147 | 60.2142 | -0.0051118 | -0.030392 | -0.02475 | 0.060526 | -0.03258 | -0.046963 | -0.039965 | 0.00094606 | -0.022245 | 0.054277 | 0.047971 | -0.21702 | -0.01706 | -0.023467 | -0.013733 | 60.173 | -62.3383 | 60.2966 | -61.9034 | -62.384 | -62.352 | 0.17853 | 60.1089 | -62.2467 | 60.3561 | -62.0819 | -62.1872 | -62.1689 | -0.1236 | -0.041198 | 0.082398 | 0.31128 | -0.13733 | -0.16937 | -0.013733 | -0.045776 | -0.032043 | -0.10529 | 0.14191 | 0.13275 | 0.045777 | 0.027466 | 0.07782 | 0.059509 | 0.43488 | 122.6349 | 0.16479 | 122.6028 | 122.5113 | 122.3557 | 122.3877 | 122.3236 | -122.5525 | -122.4609 | 122.5113 | 122.5708 | 62.2009 | 62.3932
376.0625 | 122.6715 | -62.2284 | 60.2554 | 0.0025177 | -0.025265 | -0.026032 | 0.065225 | -0.028734 | -0.051449 | -0.039965 | 0.00094606 | -0.018399 | 0.055559 | 0.053312 | -0.21616 | -0.014496 | -0.022185 | -0.018311 | 60.2051 | -62.352 | 60.2142 | -62.0087 | -62.4893 | -62.4664 | 0.07782 | 60.1913 | -62.2604 | 60.3012 | -62.1552 | -62.2787 | -62.2192 | -0.1236 | -0.050354 | -0.041199 | 0.21973 | -0.23804 | -0.26093 | -0.11444 | -0.13733 | -0.032043 | -0.064087 | 0.045776 | 0.073243 | 0.009156 | -0.050354 | 0.041199 | -0.018311 | 0.34332 | 122.5662 | 0.10529 | 122.5616 | 122.5571 | 122.4518 | 122.4335 | 122.4197 | -122.6074 | -122.5159 | 122.4426 | 122.5296 | 62.2101 | 62.3062
377.8438 | 122.6578 | -62.2559 | 60.2005 | 0.010147 | -0.025692 | -0.025605 | 0.066934 | -0.030443 | -0.048245 | -0.039965 | 0.00094606 | -0.019254 | 0.057054 | 0.046689 | -0.21445 | -0.014283 | -0.022398 | -0.13733 | 60.2097 | -62.3657 | 60.1456 | -62.1048 | -62.5854 | -62.5351 | -0.064087 | 60.1318 | -62.2925 | 60.26 | -62.2147 | -62.3337 | -62.2604 | -0.10986 | 0.009156 | -0.054931 | 0.15106 | -0.27924 | -0.32959 | -0.16937 | -0.21973 | -0.036621 | -0.068664 | 0.05951 | 0.041198 | -0.004578 | -0.07782 | 0.032043 | -0.041199 | 0.26093 | 122.5113 | 0.077819 | 122.5525 | 122.5754 | 122.4243 | 122.4655 | 122.3877 | -122.5662 | -122.493 | 122.4014 | 122.5159 | 62.1185 | 62.1918
379.5469 | 122.6257 | -62.2284 | 60.2554 | 0.0025177 | -0.027188 | -0.023469 | 0.064371 | -0.030871 | -0.046963 | -0.041887 | 0.00094606 | -0.019254 | 0.056414 | 0.04733 | -0.21467 | -0.017273 | -0.019835 | -0.041199 | 60.2325 | -62.3474 | 60.1685 | -62.0819 | -62.5122 | -62.4939 | 0.022888 | 60.1776 | -62.2604 | 60.2646 | -62.1918 | -62.3016 | -62.265 | -0.11902 | -0.022888 | -0.086975 | 0.14648 | -0.2655 | -0.28381 | -0.14648 | -0.16479 | -0.032043 | -0.07782 | 0.009155 | 0.036622 | -0.036621 | -0.073242 | -0.004578 | -0.041199 | 0.2655 | 122.5159 | 0.068665 | 122.525 | 122.58 | 122.438 | 122.4609 | 122.406 | -122.6028 | -122.5159 | 122.3969 | 122.493 | 62.1872 | 62.2513
381.3125 | 122.7448 | -62.2375 | 60.1913 | 0.0025177 | -0.027829 | -0.025391 | 0.061808 | -0.032366 | -0.048031 | -0.039537 | 0.00094606 | -0.022458 | 0.056841 | 0.046476 | -0.21573 | -0.017914 | -0.023039 | -0.018311 | 60.141 | -62.3383 | 60.2737 | -61.9263 | -62.3749 | -62.3657 | 0.17853 | 60.1364 | -62.2513 | 60.347 | -62.0682 | -62.1735 | -62.1643 | -0.10071 | -0.050354 | 0.082398 | 0.31128 | -0.12817 | -0.13733 | -0.027466 | -0.036621 | -0.013733 | -0.054931 | 0.15564 | 0.16937 | 0.073242 | 0.064087 | 0.086975 | 0.07782 | 0.41199 | 122.612 | 0.18311 | 122.5983 | 122.4792 | 122.3877 | 122.3785 | 122.374 | -122.5296 | -122.4426 | 122.5113 | 122.5845 | 62.2192 | 62.4161
383.0312 | 122.7356 | -62.2238 | 60.1776 | 0.0025177 | -0.025692 | -0.023255 | 0.061594 | -0.033007 | -0.047604 | -0.041887 | -0.0021057 | -0.021176 | 0.057054 | 0.045835 | -0.21659 | -0.017701 | -0.021758 | -0.073242 | 60.1593 | -62.3383 | 60.2234 | -61.9949 | -62.4481 | -62.4069 | 0.07782 | 60.1364 | -62.2742 | 60.3241 | -62.1002 | -62.1964 | -62.1689 | -0.11444 | -0.01831 | 0.045777 | 0.22888 | -0.1831 | -0.2243 | -0.068664 | -0.10986 | -0.050354 | -0.041198 | 0.14648 | 0.1236 | 0.054932 | 0.027466 | 0.10529 | 0.07782 | 0.34332 | 122.5616 | 0.17395 | 122.5983 | 122.4976 | 122.4106 | 122.3831 | 122.3602 | -122.5159 | -122.4518 | 122.4472 | 122.5479 | 62.1506 | 62.3016
384.8125 | 122.6074 | -62.2238 | 60.2234 | 0.0025177 | -0.02612 | -0.026246 | 0.062876 | -0.028948 | -0.050381 | -0.03676 | -0.0021057 | -0.019254 | 0.055559 | 0.04968 | -0.21509 | -0.016633 | -0.021971 | 0.004578 | 60.1913 | -62.3383 | 60.2142 | -62.0087 | -62.4756 | -62.4344 | 0.07782 | 60.1913 | -62.2421 | 60.2463 | -62.1872 | -62.3108 | -62.2879 | -0.11444 | -0.032044 | -0.009156 | 0.21515 | -0.21057 | -0.25177 | -0.09613 | -0.13733 | -0.01831 | -0.032044 | 0.022888 | 0.036621 | -0.064087 | -0.086975 | -0.045777 | -0.068665 | 0.32959 | 122.5525 | 0.054931 | 122.4884 | 122.5296 | 122.4335 | 122.4152 | 122.4152 | -122.5616 | -122.4655 | 122.438 | 122.4701 | 62.2284 | 62.3016
386.5156 | 122.6532 | -62.2421 | 60.2371 | 0.017777 | -0.027829 | -0.027527 | 0.066294 | -0.030657 | -0.049526 | -0.041033 | 0.00094606 | -0.018613 | 0.056414 | 0.042203 | -0.21488 | -0.015565 | -0.021758 | -0.009155 | 60.2417 | -62.3428 | 60.2051 | -62.0453 | -62.4939 | -62.4664 | 0.059509 | 60.1822 | -62.265 | 60.2829 | -62.1735 | -62.3016 | -62.2375 | -0.10071 | 0.004577 | -0.032044 | 0.19684 | -0.22431 | -0.25177 | -0.1236 | -0.15106 | -0.022889 | -0.054932 | 0.045776 | 0.068664 | 0.004577 | -0.05951 | 0.027466 | -0.036621 | 0.29755 | 122.5479 | 0.091553 | 122.5479 | 122.5845 | 122.4472 | 122.4838 | 122.4243 | -122.58 | -122.5021 | 122.4472 | 122.525 | 62.233 | 62.3016
388.2969 | 122.5754 | -62.2604 | 60.2417 | -0.0051118 | -0.023983 | -0.023896 | 0.065866 | -0.031298 | -0.04974 | -0.038042 | 0.00094606 | -0.019895 | 0.056414 | 0.055021 | -0.21445 | -0.015992 | -0.022185 | -0.10986 | 60.2325 | -62.352 | 60.1227 | -62.1414 | -62.5854 | -62.558 | -0.11444 | 60.1776 | -62.3199 | 60.2005 | -62.265 | -62.384 | -62.3016 | -0.091553 | -0.009155 | -0.11902 | 0.11902 | -0.29755 | -0.32501 | -0.20599 | -0.23346 | -0.059509 | -0.064087 | -0.041199 | -0.004578 | -0.041199 | -0.1236 | 0.01831 | -0.064087 | 0.21057 | 122.4747 | 0.054931 | 122.5204 | 122.5845 | 122.4976 | 122.493 | 122.438 | -122.5937 | -122.5616 | 122.3831 | 122.4609 | 62.1506 | 62.146
390.0625 | 122.5983 | -62.2513 | 60.2463 | -0.0051118 | -0.028469 | -0.023896 | 0.063089 | -0.03258 | -0.049313 | -0.039537 | -0.0021057 | -0.020322 | 0.055986 | 0.053098 | -0.21573 | -0.017487 | -0.019621 | -0.050354 | 60.2371 | -62.352 | 60.1685 | -62.0544 | -62.5076 | -62.4756 | 0.018311 | 60.2051 | -62.2375 | 60.228 | -62.2009 | -62.3108 | -62.2833 | -0.10071 | -0.009155 | -0.07782 | 0.19684 | -0.2243 | -0.25635 | -0.1236 | -0.15564 | 0.013733 | -0.041199 | -0.018311 | 0.050354 | -0.032043 | -0.059509 | -0.045776 | -0.073242 | 0.29755 | 122.5204 | 0.036621 | 122.4655 | 122.5891 | 122.4426 | 122.4884 | 122.4564 | -122.5983 | -122.4838 | 122.4197 | 122.4792 | 62.2009 | 62.2696
391.8438 | 122.6486 | -62.2238 | 60.2371 | 0.0025177 | -0.025906 | -0.026246 | 0.065866 | -0.03322 | -0.049313 | -0.037401 | -0.0021057 | -0.020749 | 0.057054 | 0.044126 | -0.21531 | -0.014283 | -0.021758 | -0.032043 | 60.2325 | -62.3474 | 60.1822 | -62.0636 | -62.4802 | -62.4756 | 0.027466 | 60.1822 | -62.2696 | 60.2783 | -62.178 | -62.2971 | -62.2375 | -0.1236 | -0.004578 | -0.054932 | 0.16022 | -0.25177 | -0.25635 | -0.12817 | -0.13275 | -0.045776 | -0.054932 | 0.041198 | 0.045776 | -0.013733 | -0.073242 | 0.032043 | -0.027466 | 0.28381 | 122.5296 | 0.091552 | 122.5479 | 122.58 | 122.4518 | 122.4564 | 122.406 | -122.5845 | -122.5067 | 122.406 | 122.5021 | 62.1918 | 62.2513
393.6406 | 122.7219 | -62.2101 | 60.1547 | -0.012741 | -0.027401 | -0.026886 | 0.061808 | -0.032366 | -0.048886 | -0.040819 | -0.0021057 | -0.021176 | 0.052782 | 0.039213 | -0.21445 | -0.016205 | -0.021971 | -0.073242 | 60.1593 | -62.3383 | 60.2234 | -61.972 | -62.4115 | -62.384 | 0.1236 | 60.1044 | -62.2559 | 60.3378 | -62.0819 | -62.1918 | -62.1735 | -0.12817 | 0.004578 | 0.068665 | 0.23804 | -0.17395 | -0.20142 | -0.045776 | -0.073242 | -0.045776 | -0.050354 | 0.18311 | 0.12817 | 0.036621 | 0.018311 | 0.082397 | 0.064087 | 0.36621 | 122.5616 | 0.17395 | 122.5937 | 122.4976 | 122.3602 | 122.3694 | 122.3145 | -122.493 | -122.4106 | 122.4335 | 122.5479 | 62.1368 | 62.3337
395.3594 | 122.7127 | -62.233 | 60.2097 | 0.0025177 | -0.028042 | -0.025605 | 0.062662 | -0.030657 | -0.049313 | -0.039537 | -0.0021057 | -0.020749 | 0.055773 | 0.042417 | -0.21424 | -0.01706 | -0.020903 | 0.004578 | 60.173 | -62.3016 | 60.2692 | -61.9446 | -62.3932 | -62.3657 | 0.16479 | 60.1318 | -62.2559 | 60.3058 | -62.0956 | -62.2101 | -62.1689 | -0.068665 | -0.036621 | 0.059509 | 0.28839 | -0.13275 | -0.16022 | -0.064087 | -0.091552 | -0.022888 | -0.07782 | 0.09613 | 0.13733 | 0.064087 | 0.022888 | 0.086975 | 0.045776 | 0.35706 | 122.5708 | 0.16022 | 122.5616 | 122.4747 | 122.3877 | 122.406 | 122.3648 | -122.5113 | -122.4655 | 122.5021 | 122.5388 | 62.2375 | 62.3978
397.1406 | 122.7539 | -62.2192 | 60.173 | 0.010147 | -0.028469 | -0.025818 | 0.061594 | -0.033434 | -0.051235 | -0.041246 | 0.0039979 | -0.022672 | 0.056627 | 0.046049 | -0.21637 | -0.016846 | -0.022185 | -0.045776 | 60.1547 | -62.3291 | 60.2509 | -61.9537 | -62.4023 | -62.3749 | 0.16937 | 60.0906 | -62.2467 | 60.3607 | -62.0728 | -62.1735 | -62.1643 | -0.10986 | -0.018311 | 0.077819 | 0.2655 | -0.15564 | -0.18311 | -0.045776 | -0.073242 | -0.027466 | -0.082398 | 0.18768 | 0.14648 | 0.054931 | 0.045776 | 0.082397 | 0.073242 | 0.37537 | 122.58 | 0.17395 | 122.6074 | 122.4838 | 122.3373 | 122.374 | 122.3099 | -122.5021 | -122.4197 | 122.4701 | 122.58 | 62.1735 | 62.3886
398.875 | 122.6349 | -62.2055 | 60.228 | 0.0025177 | -0.024624 | -0.025177 | 0.066507 | -0.032793 | -0.048672 | -0.041033 | 0.00094606 | -0.018186 | 0.055986 | 0.052244 | -0.21595 | -0.016419 | -0.021544 | 0.004578 | 60.2371 | -62.3337 | 60.2142 | -62.0224 | -62.4847 | -62.4527 | 0.082397 | 60.1776 | -62.2787 | 60.2829 | -62.1552 | -62.2971 | -62.2192 | -0.12817 | 0.009156 | -0.013733 | 0.18311 | -0.24719 | -0.27924 | -0.11902 | -0.15106 | -0.073243 | -0.050354 | 0.054932 | 0.050354 | -0.013733 | -0.091553 | 0.05951 | -0.01831 | 0.31128 | 122.5479 | 0.1236 | 122.5616 | 122.5708 | 122.4564 | 122.4426 | 122.3831 | -122.5616 | -122.5067 | 122.4197 | 122.4884 | 62.2101 | 62.2879
400.6406 | 122.6532 | -62.2467 | 60.2234 | 0.010147 | -0.027188 | -0.024109 | 0.065653 | -0.032366 | -0.047817 | -0.039965 | 0.00094606 | -0.018613 | 0.056841 | 0.049039 | -0.21488 | -0.015992 | -0.023253 | -0.009155 | 60.2509 | -62.352 | 60.2051 | -62.0087 | -62.4847 | -62.4573 | 0.068665 | 60.1685 | -62.2467 | 60.2829 | -62.1506 | -62.2971 | -62.233 | -0.10529 | 0.027465 | -0.018311 | 0.23804 | -0.21057 | -0.23804 | -0.10529 | -0.13275 | 0 | -0.054932 | 0.059509 | 0.09613 | 0.013733 | -0.050354 | 0.013733 | -0.050354 | 0.34332 | 122.5571 | 0.09613 | 122.5296 | 122.6028 | 122.4152 | 122.4976 | 122.4152 | -122.5754 | -122.4701 | 122.4518 | 122.5296 | 62.2375 | 62.3154
402.4219 | 122.6303 | -62.2742 | 60.173 | 0.0025177 | -0.024624 | -0.024537 | 0.065653 | -0.027025 | -0.048458 | -0.04146 | 0.0039979 | -0.018827 | 0.054491 | 0.053953 | -0.21381 | -0.017914 | -0.020049 | -0.15564 | 60.2234 | -62.3428 | 60.1318 | -62.1048 | -62.5671 | -62.5305 | -0.068665 | 60.141 | -62.3016 | 60.2554 | -62.2375 | -62.3428 | -62.2513 | -0.068664 | 0.050354 | -0.041199 | 0.16937 | -0.25635 | -0.29297 | -0.18768 | -0.2243 | -0.027466 | -0.032044 | 0.082397 | 0.036621 | 0.022888 | -0.068664 | 0.050354 | -0.041198 | 0.23804 | 122.4747 | 0.064087 | 122.5571 | 122.5662 | 122.4426 | 122.4976 | 122.4152 | -122.5159 | -122.4747 | 122.406 | 122.5296 | 62.1185 | 62.2055
404.2031 | 122.6303 | -62.2421 | 60.2188 | 0.0025177 | -0.02377 | -0.023682 | 0.065439 | -0.030016 | -0.049526 | -0.039324 | 0.00094606 | -0.01904 | 0.055773 | 0.050748 | -0.21509 | -0.016205 | -0.019408 | -0.027466 | 60.228 | -62.3199 | 60.2142 | -62.0041 | -62.471 | -62.4527 | 0.07782 | 60.1639 | -62.265 | 60.2737 | -62.1643 | -62.2879 | -62.2238 | -0.07782 | 0.009155 | -0.004578 | 0.23804 | -0.21057 | -0.22888 | -0.13275 | -0.15106 | -0.022889 | -0.054932 | 0.054932 | 0.077819 | 0.01831 | -0.045777 | 0.041199 | -0.022888 | 0.31586 | 122.5342 | 0.10071 | 122.5388 | 122.5479 | 122.4289 | 122.4701 | 122.406 | -122.5388 | -122.4838 | 122.4564 | 122.5159 | 62.2147 | 62.3199
405.9688 | 122.6257 | -62.2421 | 60.2463 | -0.0051118 | -0.025479 | -0.027527 | 0.067575 | -0.030443 | -0.050167 | -0.041033 | 0.00094606 | -0.020963 | 0.056414 | 0.051603 | -0.21488 | -0.017273 | -0.02133 | -0.018311 | 60.2142 | -62.3474 | 60.2188 | -61.9995 | -62.4939 | -62.4619 | 0.07782 | 60.1685 | -62.2604 | 60.2692 | -62.1735 | -62.3016 | -62.2375 | -0.10529 | -0.032044 | -0.027466 | 0.24261 | -0.21973 | -0.25177 | -0.11444 | -0.14648 | -0.018311 | -0.07782 | 0.022888 | 0.068664 | 0.004577 | -0.05951 | 0.022888 | -0.041199 | 0.3479 | 122.5662 | 0.086975 | 122.5296 | 122.5616 | 122.4289 | 122.4564 | 122.4106 | -122.5937 | -122.5067 | 122.4609 | 122.5113 | 62.2238 | 62.3199
407.7031 | 122.5983 | -62.2421 | 60.2417 | 0.0025177 | -0.028683 | -0.028382 | 0.061808 | -0.03023 | -0.051876 | -0.039965 | -0.0021057 | -0.020536 | 0.056414 | 0.044126 | -0.21467 | -0.018342 | -0.022612 | -0.050354 | 60.2234 | -62.3566 | 60.1547 | -62.0544 | -62.5031 | -62.4847 | 0.045776 | 60.173 | -62.2513 | 60.2234 | -62.1872 | -62.3154 | -62.2742 | -0.11444 | -0.01831 | -0.086975 | 0.18768 | -0.24262 | -0.26093 | -0.12817 | -0.14648 | -0.009156 | -0.068664 | -0.01831 | 0.054931 | -0.032044 | -0.073243 | -0.022888 | -0.064087 | 0.30212 | 122.5113 | 0.064087 | 122.4747 | 122.58 | 122.4243 | 122.4655 | 122.4152 | -122.5983 | -122.493 | 122.3969 | 122.4655 | 62.1918 | 62.2879
409.4688 | 122.6395 | -62.2238 | 60.2463 | 0.0025177 | -0.027401 | -0.025605 | 0.063303 | -0.031725 | -0.049954 | -0.042314 | -0.0021057 | -0.01904 | 0.055986 | 0.04968 | -0.2168 | -0.015778 | -0.023039 | -0.009155 | 60.228 | -62.3611 | 60.2005 | -61.9949 | -62.4756 | -62.4481 | 0.068665 | 60.1639 | -62.2604 | 60.2966 | -62.1506 | -62.2925 | -62.2192 | -0.13733 | -0.018311 | -0.045777 | 0.22888 | -0.2243 | -0.25177 | -0.086975 | -0.11444 | -0.036621 | -0.082398 | 0.050354 | 0.073242 | 0.004578 | -0.068664 | 0.041199 | -0.032043 | 0.36621 | 122.5616 | 0.10986 | 122.5571 | 122.5891 | 122.4243 | 122.4518 | 122.3877 | -122.6074 | -122.5067 | 122.4243 | 122.5204 | 62.2147 | 62.2925
411.2344 | 122.6578 | -62.2101 | 60.2325 | 0.0025177 | -0.025479 | -0.025818 | 0.065439 | -0.024889 | -0.04974 | -0.035906 | 0.0039979 | -0.019467 | 0.059191 | 0.050321 | -0.21552 | -0.015778 | -0.021544 | -0.013733 | 60.2371 | -62.3474 | 60.1868 | -62.0224 | -62.4802 | -62.4619 | 0.073242 | 60.1593 | -62.2375 | 60.2829 | -62.1643 | -62.2787 | -62.2238 | -0.13733 | 0.004578 | -0.045776 | 0.18768 | -0.25177 | -0.27008 | -0.11444 | -0.13275 | -0.027466 | -0.073242 | 0.050354 | 0.045776 | -0.013733 | -0.068665 | 0.013733 | -0.041199 | 0.32501 | 122.5342 | 0.073242 | 122.5204 | 122.5845 | 122.3969 | 122.4472 | 122.3694 | -122.58 | -122.4701 | 122.3969 | 122.493 | 62.1963 | 62.2833
413.0312 | 122.5754 | -62.2696 | 60.228 | -0.0051118 | -0.024197 | -0.026032 | 0.066294 | -0.031511 | -0.048245 | -0.040819 | -0.0021057 | -0.018613 | 0.057909 | 0.044767 | -0.21659 | -0.016633 | -0.02368 | -0.11902 | 60.2325 | -62.3657 | 60.1227 | -62.1368 | -62.5763 | -62.5488 | -0.10071 | 60.1593 | -62.2787 | 60.1959 | -62.2696 | -62.3795 | -62.2879 | -0.096131 | 0.004578 | -0.10529 | 0.13275 | -0.27924 | -0.3067 | -0.1831 | -0.21057 | -0.009156 | -0.068664 | -0.032043 | 0 | -0.018311 | -0.10986 | -0.009155 | -0.10071 | 0.22888 | 122.4884 | 0.009156 | 122.4747 | 122.5983 | 122.4381 | 122.5021 | 122.4289 | -122.5937 | -122.5067 | 122.3923 | 122.4655 | 62.1506 | 62.1689
414.75 | 122.6669 | -62.2375 | 60.228 | -0.0051118 | -0.028042 | -0.025177 | 0.063089 | -0.032366 | -0.050595 | -0.038896 | 0.00094606 | -0.023099 | 0.0562 | 0.050107 | -0.21445 | -0.017701 | -0.024748 | 0.004578 | 60.1776 | -62.3245 | 60.2417 | -61.9446 | -62.4069 | -62.3611 | 0.13275 | 60.1318 | -62.2467 | 60.2966 | -62.1002 | -62.2238 | -62.1689 | -0.086975 | -0.050354 | 0.013733 | 0.29297 | -0.1236 | -0.16937 | -0.036621 | -0.082397 | -0.009155 | -0.09613 | 0.068665 | 0.13733 | 0.068665 | 0.013733 | 0.07782 | 0.022888 | 0.37994 | 122.5662 | 0.14648 | 122.5433 | 122.5021 | 122.3785 | 122.4152 | 122.3694 | -122.5525 | -122.4747 | 122.4792 | 122.5342 | 62.2421 | 62.3703
416.5156 | 122.7081 | -62.2009 | 60.2097 | 0.0025177 | -0.029751 | -0.026032 | 0.062021 | -0.03258 | -0.04974 | -0.039751 | 0.00094606 | -0.022245 | 0.055559 | 0.043485 | -0.21488 | -0.016419 | -0.024962 | -0.013733 | 60.1593 | -62.3474 | 60.2737 | -61.9263 | -62.3795 | -62.3566 | 0.1831 | 60.1089 | -62.2467 | 60.3424 | -62.0911 | -62.1826 | -62.1552 | -0.14648 | -0.050354 | 0.064087 | 0.27466 | -0.15564 | -0.17853 | -0.009155 | -0.032044 | -0.045776 | -0.10071 | 0.13275 | 0.10986 | 0.045777 | 0.018311 | 0.091553 | 0.064087 | 0.42114 | 122.6212 | 0.15564 | 122.5891 | 122.5067 | 122.3557 | 122.3602 | 122.3099 | -122.5571 | -122.4564 | 122.4747 | 122.5433 | 62.1872 | 62.384
418.3125 | 122.5891 | -62.2238 | 60.2737 | -0.0051118 | -0.028469 | -0.02475 | 0.062021 | -0.031939 | -0.04974 | -0.039324 | 0.00094606 | -0.02139 | 0.056627 | 0.047971 | -0.21573 | -0.016633 | -0.022185 | -0.027466 | 60.2142 | -62.3383 | 60.1639 | -62.0361 | -62.4847 | -62.4619 | 0.045776 | 60.1639 | -62.2421 | 60.228 | -62.1918 | -62.3016 | -62.2559 | -0.11444 | -0.05951 | -0.10986 | 0.18768 | -0.23804 | -0.26093 | -0.1236 | -0.14648 | -0.01831 | -0.10986 | -0.045777 | 0.032044 | -0.032043 | -0.07782 | -0.013733 | -0.05951 | 0.30212 | 122.5021 | 0.050354 | 122.4701 | 122.5525 | 122.406 | 122.438 | 122.3877 | -122.612 | -122.5159 | 122.3877 | 122.4518 | 62.1964 | 62.2696
420.0312 | 122.6074 | -62.2192 | 60.26 | -0.0051118 | -0.028897 | -0.024537 | 0.064585 | -0.033007 | -0.047604 | -0.040178 | -0.0051575 | -0.019254 | 0.057909 | 0.051176 | -0.21467 | -0.016205 | -0.020476 | -0.036621 | 60.2463 | -62.3428 | 60.1547 | -62.0682 | -62.5168 | -62.4756 | 0.036621 | 60.1913 | -62.2559 | 60.2325 | -62.2192 | -62.3154 | -62.2696 | -0.1236 | -0.013733 | -0.10529 | 0.15106 | -0.25635 | -0.29755 | -0.13275 | -0.17395 | -0.036621 | -0.068665 | -0.027466 | 0 | -0.050354 | -0.096131 | -0.013733 | -0.05951 | 0.27466 | 122.4976 | 0.036621 | 122.4884 | 122.5891 | 122.4472 | 122.4655 | 122.4106 | -122.6028 | -122.5159 | 122.374 | 122.4518 | 62.1826 | 62.2559
421.8281 | 122.7036 | -62.2238 | 60.1456 | 0.0025177 | -0.024197 | -0.02475 | 0.065653 | -0.027666 | -0.048672 | -0.037615 | -0.0021057 | -0.02139 | 0.055559 | 0.046476 | -0.21637 | -0.017701 | -0.02368 | -0.086975 | 60.1776 | -62.3428 | 60.2142 | -61.9904 | -62.471 | -62.4344 | 0.032043 | 60.1044 | -62.2879 | 60.3241 | -62.1323 | -62.2375 | -62.1597 | -0.11902 | 0.032043 | 0.068664 | 0.23346 | -0.21057 | -0.24719 | -0.091553 | -0.12817 | -0.064087 | -0.041199 | 0.17853 | 0.091553 | 0.064087 | -0.013733 | 0.12817 | 0.050354 | 0.35248 | 122.5571 | 0.15564 | 122.612 | 122.5204 | 122.3923 | 122.4014 | 122.3282 | -122.4884 | -122.4335 | 122.438 | 122.5479 | 62.1368 | 62.2559
423.5938 | 122.6669 | -62.233 | 60.2325 | 0.010147 | -0.025265 | -0.026459 | 0.063089 | -0.029589 | -0.049313 | -0.039537 | -0.0051575 | -0.02139 | 0.055345 | 0.048612 | -0.21616 | -0.016633 | -0.024535 | 0.022888 | 60.1822 | -62.3199 | 60.2463 | -61.9446 | -62.4023 | -62.3703 | 0.14191 | 60.1501 | -62.2513 | 60.2875 | -62.1094 | -62.2284 | -62.1918 | -0.086975 | -0.050354 | 0.013733 | 0.28839 | -0.13733 | -0.16937 | -0.050354 | -0.082398 | -0.018311 | -0.082398 | 0.054932 | 0.1236 | 0.041199 | 0.004577 | 0.05951 | 0.022888 | 0.37537 | 122.5662 | 0.14191 | 122.5388 | 122.5021 | 122.4014 | 122.4152 | 122.3831 | -122.5525 | -122.4838 | 122.4792 | 122.5204 | 62.2559 | 62.3749
425.375 | 122.612 | -62.2284 | 60.2509 | 0.010147 | -0.028683 | -0.026032 | 0.062235 | -0.037493 | -0.049526 | -0.038256 | -0.0082091 | -0.020963 | 0.054918 | 0.047544 | -0.21445 | -0.016846 | -0.024535 | 0.022888 | 60.2005 | -62.3383 | 60.2142 | -61.9904 | -62.4481 | -62.4115 | 0.11444 | 60.1685 | -62.2604 | 60.2463 | -62.1735 | -62.2833 | -62.2375 | -0.10986 | -0.050354 | -0.036621 | 0.23804 | -0.1831 | -0.21973 | -0.073242 | -0.10986 | -0.032043 | -0.082397 | -0.004577 | 0.054932 | -0.009155 | -0.054931 | 0.022888 | -0.022888 | 0.3479 | 122.5525 | 0.086975 | 122.5067 | 122.5388 | 122.4289 | 122.4289 | 122.3969 | -122.5891 | -122.5113 | 122.4426 | 122.4747 | 62.2513 | 62.3428
427.0938 | 122.7264 | -62.2101 | 60.1822 | 0.010147 | -0.027615 | -0.026886 | 0.063516 | -0.033648 | -0.049313 | -0.041887 | -0.0021057 | -0.021176 | 0.057268 | 0.037931 | -0.21616 | -0.016419 | -0.021544 | -0.009155 | 60.1501 | -62.3291 | 60.2737 | -61.9034 | -62.3566 | -62.3383 | 0.1831 | 60.1135 | -62.2147 | 60.347 | -62.0682 | -62.1689 | -62.1506 | -0.11902 | -0.032044 | 0.091553 | 0.3067 | -0.12817 | -0.14648 | -0.009155 | -0.027465 | -0.004578 | -0.068665 | 0.16479 | 0.14191 | 0.059509 | 0.041199 | 0.064087 | 0.045777 | 0.42572 | 122.6028 | 0.14648 | 122.5616 | 122.4792 | 122.3282 | 122.3602 | 122.3236 | -122.5113 | -122.3969 | 122.4838 | 122.5571 | 62.2009 | 62.3932
428.875 | 122.5845 | -62.2513 | 60.2417 | 0.010147 | -0.024838 | -0.024537 | 0.066721 | -0.028734 | -0.047817 | -0.04146 | 0.00094606 | -0.017331 | 0.057482 | 0.045621 | -0.2183 | -0.01706 | -0.020689 | -0.11444 | 60.2325 | -62.352 | 60.1044 | -62.1506 | -62.6038 | -62.5534 | -0.091553 | 60.141 | -62.2879 | 60.2142 | -62.265 | -62.3749 | -62.2787 | -0.10071 | -0.009155 | -0.13733 | 0.10071 | -0.30212 | -0.35248 | -0.20142 | -0.25177 | -0.036621 | -0.10071 | -0.027466 | -0.013733 | -0.027466 | -0.1236 | 0.009155 | -0.086975 | 0.20142 | 122.4564 | 0.022888 | 122.5021 | 122.5845 | 122.4289 | 122.4838 | 122.3923 | -122.5937 | -122.5296 | 122.3557 | 122.4655 | 62.1368 | 62.1597
430.6406 | 122.731 | -62.233 | 60.1593 | 0.0025177 | -0.02676 | -0.023896 | 0.065012 | -0.031725 | -0.04974 | -0.037401 | 0.00094606 | -0.020963 | 0.055773 | 0.047758 | -0.21424 | -0.01706 | -0.024321 | -0.073242 | 60.1593 | -62.3428 | 60.2234 | -61.9812 | -62.4619 | -62.4161 | 0.054932 | 60.0769 | -62.2787 | 60.3104 | -62.114 | -62.2284 | -62.1826 | -0.10986 | 0 | 0.064087 | 0.25177 | -0.18311 | -0.22888 | -0.073243 | -0.11902 | -0.045777 | -0.082398 | 0.15106 | 0.11902 | 0.050354 | 0.004577 | 0.096131 | 0.050354 | 0.36163 | 122.5662 | 0.16479 | 122.5891 | 122.5021 | 122.3557 | 122.3923 | 122.3099 | -122.5021 | -122.4381 | 122.4564 | 122.5433 | 62.1597 | 62.2879
432.3438 | 122.731 | -62.1964 | 60.1776 | 0.010147 | -0.029538 | -0.026246 | 0.062448 | -0.032152 | -0.050808 | -0.039324 | -0.0021057 | -0.022672 | 0.054705 | 0.03964 | -0.21573 | -0.017487 | -0.025389 | -0.032043 | 60.1639 | -62.3199 | 60.2509 | -61.9217 | -62.3978 | -62.3657 | 0.17395 | 60.1135 | -62.2375 | 60.347 | -62.0453 | -62.1643 | -62.146 | -0.1236 | -0.013733 | 0.073242 | 0.27466 | -0.16937 | -0.20142 | -0.045777 | -0.07782 | -0.041199 | -0.064087 | 0.16937 | 0.15106 | 0.050354 | 0.032043 | 0.091553 | 0.073242 | 0.39825 | 122.5708 | 0.19226 | 122.5845 | 122.4838 | 122.3511 | 122.3602 | 122.3099 | -122.4976 | -122.4152 | 122.4472 | 122.5433 | 62.1643 | 62.3703
434.1406 | 122.644 | -62.2101 | 60.2234 | -0.0051118 | -0.028683 | -0.025818 | 0.062876 | -0.030016 | -0.049313 | -0.039751 | 0.00094606 | -0.021817 | 0.052568 | 0.047544 | -0.21659 | -0.018342 | -0.022826 | 0.018311 | 60.1639 | -62.3428 | 60.26 | -61.9354 | -62.4023 | -62.3749 | 0.14648 | 60.1501 | -62.2284 | 60.2875 | -62.1277 | -62.2238 | -62.2055 | -0.13275 | -0.05951 | 0.036621 | 0.27466 | -0.1648 | -0.19226 | -0.032044 | -0.05951 | -0.018311 | -0.073243 | 0.064087 | 0.082397 | 0.004578 | -0.013733 | 0.022889 | 0.004578 | 0.40741 | 122.6028 | 0.10071 | 122.5159 | 122.5067 | 122.3785 | 122.374 | 122.3602 | -122.5662 | -122.4518 | 122.4701 | 122.4976 | 62.2284 | 62.3566
435.8594 | 122.58 | -62.2559 | 60.26 | 0.0025177 | -0.028683 | -0.026673 | 0.063944 | -0.031939 | -0.052517 | -0.040605 | -0.0021057 | -0.018827 | 0.055773 | 0.04434 | -0.21552 | -0.017273 | -0.020689 | -0.036621 | 60.228 | -62.3611 | 60.1501 | -62.0453 | -62.4985 | -62.471 | 0.041199 | 60.1822 | -62.2742 | 60.2325 | -62.1918 | -62.3108 | -62.2696 | -0.10529 | -0.032044 | -0.10986 | 0.21057 | -0.21515 | -0.24262 | -0.10986 | -0.13733 | -0.018311 | -0.07782 | -0.027466 | 0.064087 | -0.013733 | -0.054932 | 0.004578 | -0.036621 | 0.31586 | 122.5113 | 0.082398 | 122.5067 | 122.5891 | 122.4564 | 122.4838 | 122.438 | -122.6212 | -122.5342 | 122.406 | 122.4884 | 62.2192 | 62.2971
437.6406 | 122.7081 | -62.2055 | 60.1547 | 0.0025177 | -0.023343 | -0.023255 | 0.064798 | -0.028734 | -0.049954 | -0.038469 | 0.0039979 | -0.020322 | 0.056414 | 0.049039 | -0.2168 | -0.017487 | -0.022398 | -0.11444 | 60.1685 | -62.352 | 60.2005 | -62.0224 | -62.4893 | -62.4435 | 0.027466 | 60.0861 | -62.2696 | 60.3058 | -62.146 | -62.2604 | -62.1735 | -0.14648 | 0.013733 | 0.045776 | 0.18311 | -0.23804 | -0.28381 | -0.091552 | -0.13733 | -0.064087 | -0.068664 | 0.15106 | 0.059509 | 0.032043 | -0.054932 | 0.09613 | 0.009155 | 0.32959 | 122.5525 | 0.1236 | 122.5754 | 122.5204 | 122.3557 | 122.374 | 122.2916 | -122.5067 | -122.4243 | 122.406 | 122.5113 | 62.0911 | 62.233
439.3594 | 122.6395 | -62.2192 | 60.2371 | 0.0025177 | -0.026547 | -0.023469 | 0.066294 | -0.033861 | -0.049954 | -0.038896 | -0.0021057 | -0.020108 | 0.056414 | 0.049467 | -0.21467 | -0.017273 | -0.021971 | -0.004578 | 60.2463 | -62.3337 | 60.1822 | -62.0407 | -62.471 | -62.4619 | 0.07782 | 60.1593 | -62.2513 | 60.2737 | -62.146 | -62.2925 | -62.2147 | -0.11444 | 0.009155 | -0.054932 | 0.17853 | -0.24262 | -0.25177 | -0.12817 | -0.13733 | -0.032044 | -0.07782 | 0.036621 | 0.073242 | 0.004577 | -0.073242 | 0.036621 | -0.041198 | 0.29297 | 122.5159 | 0.10529 | 122.525 | 122.58 | 122.4106 | 122.4655 | 122.3785 | -122.5708 | -122.4884 | 122.4014 | 122.493 | 62.2147 | 62.2971
441.1406 | 122.6852 | -62.2192 | 60.173 | 0.0025177 | -0.029324 | -0.026459 | 0.05903 | -0.031725 | -0.050167 | -0.038683 | -0.0051575 | -0.022885 | 0.055345 | 0.041563 | -0.21296 | -0.016633 | -0.024107 | -0.10529 | 60.1593 | -62.3474 | 60.173 | -62.027 | -62.4847 | -62.4481 | 0.032043 | 60.1135 | -62.2742 | 60.2875 | -62.146 | -62.233 | -62.1918 | -0.12817 | -0.013733 | 0 | 0.19226 | -0.22888 | -0.2655 | -0.10071 | -0.13733 | -0.054932 | -0.05951 | 0.11444 | 0.073242 | 0.027466 | -0.013733 | 0.082398 | 0.041199 | 0.32043 | 122.5204 | 0.12817 | 122.5616 | 122.5067 | 122.3877 | 122.3785 | 122.3328 | -122.5204 | -122.4472 | 122.3923 | 122.5067 | 62.114 | 62.2513
442.9219 | 122.5754 | -62.2696 | 60.2188 | 0.0025177 | -0.023129 | -0.023896 | 0.063089 | -0.033434 | -0.048458 | -0.039324 | -0.0021057 | -0.020322 | 0.055986 | 0.046049 | -0.21552 | -0.017487 | -0.021117 | -0.10986 | 60.2188 | -62.3657 | 60.1135 | -62.1185 | -62.5809 | -62.5168 | -0.068665 | 60.1593 | -62.2787 | 60.1913 | -62.2833 | -62.3886 | -62.3154 | -0.096131 | 0 | -0.10529 | 0.15106 | -0.24719 | -0.31128 | -0.15106 | -0.21515 | -0.009156 | -0.059509 | -0.027466 | -0.013733 | -0.045777 | -0.11902 | -0.036621 | -0.10986 | 0.24719 | 122.4792 | -0.004577 | 122.4701 | 122.5845 | 122.4381 | 122.4884 | 122.4289 | -122.5845 | -122.4976 | 122.3831 | 122.4609 | 62.1597 | 62.2009
444.7031 | 122.5983 | -62.2467 | 60.2097 | 0.010147 | -0.029538 | -0.025605 | 0.062448 | -0.027453 | -0.051022 | -0.040605 | 0.0039979 | -0.020963 | 0.054491 | 0.046476 | -0.21381 | -0.018555 | -0.022398 | 0.018311 | 60.1868 | -62.3428 | 60.1959 | -61.9858 | -62.4435 | -62.4023 | 0.091553 | 60.1868 | -62.2604 | 60.2371 | -62.1643 | -62.265 | -62.2513 | -0.09613 | -0.022888 | -0.013733 | 0.26093 | -0.15564 | -0.19684 | -0.05951 | -0.10071 | -0.013733 | -0.022888 | 0.027466 | 0.082397 | -0.004578 | -0.018311 | 0.009155 | -0.004578 | 0.35706 | 122.5388 | 0.09613 | 122.4976 | 122.5296 | 122.4472 | 122.4335 | 122.4335 | -122.5525 | -122.4701 | 122.4426 | 122.4838 | 62.265 | 62.3383
446.4062 | 122.6303 | -62.2009 | 60.2234 | 0.0025177 | -0.027401 | -0.025391 | 0.064157 | -0.030016 | -0.048031 | -0.039751 | 0.0039979 | -0.017972 | 0.055345 | 0.050748 | -0.21659 | -0.01471 | -0.024535 | -0.013733 | 60.1913 | -62.3337 | 60.2051 | -62.0087 | -62.471 | -62.4481 | 0.082397 | 60.1501 | -62.2742 | 60.2737 | -62.1414 | -62.2833 | -62.2147 | -0.13275 | -0.032044 | -0.018311 | 0.19226 | -0.24719 | -0.27008 | -0.11444 | -0.13733 | -0.073242 | -0.073243 | 0.050354 | 0.05951 | -0.013733 | -0.082397 | 0.059509 | -0.009155 | 0.32501 | 122.5388 | 0.13275 | 122.5479 | 122.525 | 122.4243 | 122.3923 | 122.3511 | -122.5571 | -122.4976 | 122.406 | 122.4747 | 62.1872 | 62.2833
448.1719 | 122.5983 | -62.2375 | 60.1959 | -0.0051118 | -0.025479 | -0.023682 | 0.064157 | -0.02788 | -0.048458 | -0.04146 | -0.0021057 | -0.019467 | 0.056627 | 0.045621 | -0.21573 | -0.015992 | -0.021758 | -0.13275 | 60.2142 | -62.3978 | 60.1089 | -62.1094 | -62.5717 | -62.5259 | -0.07782 | 60.1364 | -62.2742 | 60.2234 | -62.2421 | -62.3795 | -62.2742 | -0.16022 | 0.01831 | -0.086975 | 0.12817 | -0.28839 | -0.33417 | -0.12817 | -0.17395 | -0.036621 | -0.059509 | 0.027466 | -0.004577 | -0.036621 | -0.14191 | 0 | -0.10529 | 0.28839 | 122.5067 | 0.032044 | 122.4976 | 122.612 | 122.4106 | 122.4518 | 122.374 | -122.5937 | -122.4701 | 122.3465 | 122.4609 | 62.1048 | 62.1597
449.9375 | 122.6303 | -62.2101 | 60.2188 | 0.0025177 | -0.025051 | -0.024964 | 0.06373 | -0.029589 | -0.050381 | -0.040605 | -0.0021057 | -0.019254 | 0.058336 | 0.055448 | -0.2168 | -0.016633 | -0.018126 | -0.018311 | 60.2463 | -62.3474 | 60.1913 | -61.9995 | -62.471 | -62.4298 | 0.073242 | 60.1501 | -62.2559 | 60.2966 | -62.1597 | -62.2696 | -62.2101 | -0.13733 | 0.027466 | -0.027466 | 0.21057 | -0.21973 | -0.26093 | -0.082398 | -0.1236 | -0.045776 | -0.068665 | 0.07782 | 0.050354 | 0 | -0.059509 | 0.045776 | -0.013733 | 0.3479 | 122.5388 | 0.09613 | 122.5525 | 122.5937 | 122.406 | 122.4564 | 122.3602 | -122.5662 | -122.4747 | 122.4014 | 122.5067 | 62.1918 | 62.2833
451.6562 | 122.6257 | -62.2147 | 60.228 | -0.0051118 | -0.024624 | -0.023255 | 0.065439 | -0.028948 | -0.049099 | -0.038042 | -0.0051575 | -0.019895 | 0.055986 | 0.046049 | -0.21488 | -0.01471 | -0.025816 | -0.013733 | 60.2188 | -62.352 | 60.2005 | -62.0041 | -62.4619 | -62.4435 | 0.064087 | 60.1593 | -62.2742 | 60.2783 | -62.1368 | -62.2787 | -62.2009 | -0.13733 | -0.009155 | -0.027466 | 0.21057 | -0.22888 | -0.24719 | -0.091552 | -0.10986 | -0.059509 | -0.068664 | 0.050354 | 0.07782 | 0.013733 | -0.064087 | 0.073242 | -0.004578 | 0.3479 | 122.5525 | 0.13733 | 122.5525 | 122.5708 | 122.4335 | 122.4335 | 122.374 | -122.58 | -122.5021 | 122.4152 | 122.493 | 62.2009 | 62.2787
453.4219 | 122.5708 | -62.2604 | 60.2142 | -0.0051118 | -0.023129 | -0.022614 | 0.064371 | -0.027239 | -0.047604 | -0.039965 | -0.0021057 | -0.01904 | 0.056841 | 0.050107 | -0.21531 | -0.016205 | -0.025176 | -0.12817 | 60.2417 | -62.3428 | 60.0861 | -62.1368 | -62.5992 | -62.5626 | -0.086975 | 60.1593 | -62.2971 | 60.2051 | -62.2513 | -62.3886 | -62.2833 | -0.082397 | 0.027466 | -0.12817 | 0.1236 | -0.30212 | -0.33874 | -0.21973 | -0.25635 | -0.036621 | -0.054931 | -0.009155 | 0.009155 | -0.022888 | -0.12817 | 0.013733 | -0.091553 | 0.20599 | 122.4289 | 0.045776 | 122.5021 | 122.5845 | 122.4564 | 122.5021 | 122.4197 | -122.5571 | -122.5113 | 122.3465 | 122.4655 | 62.1323 | 62.1735
455.1406 | 122.699 | -62.2192 | 60.1639 | -0.0051118 | -0.023556 | -0.02475 | 0.06138 | -0.033434 | -0.04974 | -0.041674 | 0.00094606 | -0.020963 | 0.055986 | 0.040494 | -0.21573 | -0.016846 | -0.023039 | -0.10071 | 60.1456 | -62.3566 | 60.2142 | -61.9629 | -62.4573 | -62.3978 | 0.041199 | 60.0998 | -62.2559 | 60.3195 | -62.1094 | -62.2284 | -62.1643 | -0.13733 | -0.01831 | 0.050354 | 0.25635 | -0.17853 | -0.23804 | -0.041199 | -0.10071 | -0.036621 | -0.064087 | 0.15564 | 0.10986 | 0.054931 | -0.009156 | 0.091552 | 0.027465 | 0.39368 | 122.5708 | 0.14648 | 122.5754 | 122.5021 | 122.3557 | 122.3648 | 122.319 | -122.5204 | -122.4197 | 122.4335 | 122.5388 | 62.1185 | 62.2604
456.9219 | 122.5891 | -62.233 | 60.2554 | 0.010147 | -0.028683 | -0.026886 | 0.062448 | -0.032366 | -0.051663 | -0.038469 | 0.00094606 | -0.019681 | 0.057268 | 0.042417 | -0.21467 | -0.018128 | -0.027525 | -0.054932 | 60.2234 | -62.3337 | 60.1364 | -62.059 | -62.5031 | -62.4802 | 0.036621 | 60.173 | -62.2375 | 60.2142 | -62.2009 | -62.3016 | -62.2696 | -0.10071 | -0.032043 | -0.11902 | 0.17395 | -0.24719 | -0.27008 | -0.14649 | -0.16937 | -0.004578 | -0.082397 | -0.041199 | 0.032043 | -0.036621 | -0.068665 | -0.032043 | -0.064087 | 0.27466 | 122.4701 | 0.036621 | 122.4518 | 122.5571 | 122.4106 | 122.4564 | 122.406 | -122.5891 | -122.493 | 122.3694 | 122.4472 | 62.178 | 62.2696
458.7031 | 122.5662 | -62.2513 | 60.2234 | -0.0051118 | -0.02377 | -0.0224 | 0.065439 | -0.027239 | -0.048458 | -0.037187 | -0.0051575 | -0.019254 | 0.057482 | 0.046049 | -0.21573 | -0.018342 | -0.024321 | -0.082397 | 60.2417 | -62.3474 | 60.1318 | -62.0865 | -62.5259 | -62.5168 | -0.064087 | 60.1593 | -62.265 | 60.2097 | -62.2421 | -62.3703 | -62.2604 | -0.09613 | 0.01831 | -0.091553 | 0.1648 | -0.2655 | -0.27466 | -0.16937 | -0.17853 | -0.013733 | -0.064087 | -0.013733 | 0.009156 | -0.009155 | -0.11902 | 0.004578 | -0.10529 | 0.26093 | 122.4792 | 0.022889 | 122.4747 | 122.5891 | 122.4243 | 122.493 | 122.4106 | -122.5708 | -122.4884 | 122.3831 | 122.4609 | 62.1689 | 62.1872
460.4219 | 122.6578 | -62.2101 | 60.173 | 0.0025177 | -0.027188 | -0.024964 | 0.065012 | -0.031725 | -0.049099 | -0.041887 | -0.0051575 | -0.022245 | 0.055773 | 0.041349 | -0.21552 | -0.018342 | -0.025816 | -0.1236 | 60.1501 | -62.3474 | 60.1776 | -61.9812 | -62.4893 | -62.4207 | 0.027466 | 60.0906 | -62.2787 | 60.2692 | -62.1643 | -62.265 | -62.2147 | -0.13733 | -0.022889 | 0.004577 | 0.22888 | -0.21057 | -0.27924 | -0.073242 | -0.14191 | -0.068665 | -0.082398 | 0.09613 | 0.045776 | -0.004578 | -0.054932 | 0.064087 | 0.013733 | 0.36621 | 122.525 | 0.11444 | 122.5479 | 122.4976 | 122.3694 | 122.3602 | 122.3007 | -122.5204 | -122.4518 | 122.3877 | 122.4792 | 62.0865 | 62.2375
462.2031 | 122.5845 | -62.2009 | 60.2509 | 0.0025177 | -0.025479 | -0.025391 | 0.065225 | -0.029162 | -0.048672 | -0.039751 | -0.0051575 | -0.016904 | 0.056841 | 0.050535 | -0.21595 | -0.016846 | -0.021117 | -0.013733 | 60.26 | -62.3291 | 60.1364 | -62.0728 | -62.4939 | -62.4802 | 0.022888 | 60.1501 | -62.2467 | 60.2325 | -62.1872 | -62.3108 | -62.2421 | -0.12817 | 0.009156 | -0.11444 | 0.12817 | -0.27924 | -0.29297 | -0.15106 | -0.16479 | -0.045776 | -0.10071 | -0.01831 | 0.013733 | -0.041198 | -0.10986 | 0.004578 | -0.064087 | 0.25635 | 122.4655 | 0.059509 | 122.4792 | 122.5891 | 122.3969 | 122.4609 | 122.3511 | -122.58 | -122.4976 | 122.3373 | 122.4335 | 62.1872 | 62.2238
463.9844 | 122.5937 | -62.2284 | 60.2646 | 0.0025177 | -0.027615 | -0.027741 | 0.061594 | -0.029589 | -0.04974 | -0.040605 | 0.0039979 | -0.020322 | 0.058123 | 0.046903 | -0.21637 | -0.018555 | -0.021117 | -0.022888 | 60.2142 | -62.3337 | 60.1593 | -62.0316 | -62.4847 | -62.471 | 0.059509 | 60.173 | -62.2604 | 60.2188 | -62.1918 | -62.2879 | -62.265 | -0.10528 | -0.050354 | -0.10529 | 0.19684 | -0.24261 | -0.25635 | -0.13733 | -0.15106 | -0.032043 | -0.091552 | -0.045776 | 0.036622 | -0.036621 | -0.059509 | -0.004578 | -0.027466 | 0.30212 | 122.493 | 0.068665 | 122.4792 | 122.5479 | 122.4335 | 122.4426 | 122.4014 | -122.5983 | -122.525 | 122.3877 | 122.4472 | 62.2055 | 62.2879
465.7656 | 122.7264 | -62.2147 | 60.1959 | 0.010147 | -0.027401 | -0.026886 | 0.061594 | -0.031725 | -0.050381 | -0.038683 | 0.00094606 | -0.022458 | 0.057482 | 0.037717 | -0.21402 | -0.017273 | -0.022398 | -0.059509 | 60.1364 | -62.3291 | 60.2142 | -61.9537 | -62.3978 | -62.3611 | 0.13275 | 60.1044 | -62.2375 | 60.3424 | -62.0819 | -62.1826 | -62.1506 | -0.11444 | -0.059509 | 0.01831 | 0.26093 | -0.14648 | -0.1831 | -0.032043 | -0.068664 | -0.022888 | -0.091553 | 0.14648 | 0.13275 | 0.064087 | 0.032044 | 0.086975 | 0.054932 | 0.37537 | 122.5433 | 0.15564 | 122.58 | 122.4655 | 122.3419 | 122.3511 | 122.319 | -122.525 | -122.4335 | 122.4289 | 122.5571 | 62.1552 | 62.3474
467.5312 | 122.6807 | -62.2421 | 60.1593 | 0.0025177 | -0.024411 | -0.023896 | 0.063303 | -0.028521 | -0.050167 | -0.040605 | 0.0039979 | -0.020536 | 0.054277 | 0.051816 | -0.21787 | -0.016419 | -0.022612 | -0.09613 | 60.1364 | -62.3291 | 60.2234 | -61.9537 | -62.4527 | -62.3932 | 0.073242 | 60.0998 | -62.2559 | 60.3012 | -62.1368 | -62.2559 | -62.1872 | -0.086976 | -0.022888 | 0.064087 | 0.28839 | -0.15106 | -0.21057 | -0.064086 | -0.1236 | -0.013733 | -0.05951 | 0.14191 | 0.10529 | 0.054931 | -0.013733 | 0.068664 | 0 | 0.37537 | 122.5525 | 0.11902 | 122.5571 | 122.4655 | 122.3557 | 122.3785 | 122.3419 | -122.4884 | -122.4152 | 122.4655 | 122.5433 | 62.146 | 62.3154
469.3438 | 122.5525 | -62.2467 | 60.2142 | 0.010147 | -0.02377 | -0.024323 | 0.067362 | -0.030016 | -0.048886 | -0.039537 | -0.0021057 | -0.017545 | 0.056841 | 0.044553 | -0.21659 | -0.016205 | -0.026671 | -0.14191 | 60.2234 | -62.3428 | 60.1044 | -62.1231 | -62.5809 | -62.5214 | -0.09613 | 60.141 | -62.2513 | 60.1959 | -62.2559 | -62.384 | -62.2833 | -0.09613 | 0.009156 | -0.10986 | 0.1236 | -0.27466 | -0.33417 | -0.17853 | -0.23804 | -0.004578 | -0.073242 | -0.01831 | -0.009155 | -0.036621 | -0.13733 | -0.032043 | -0.13275 | 0.21973 | 122.4472 | -0.004577 | 122.4472 | 122.5662 | 122.3923 | 122.4701 | 122.3877 | -122.5571 | -122.4655 | 122.3511 | 122.4426 | 62.1048 | 62.1506
471.0469 | 122.6166 | -62.233 | 60.1868 | -0.012741 | -0.024838 | -0.024323 | 0.064798 | -0.026598 | -0.049954 | -0.039537 | -0.0021057 | -0.018613 | 0.057482 | 0.047971 | -0.21531 | -0.016419 | -0.02133 | -0.15564 | 60.2005 | -62.3428 | 60.1181 | -62.0956 | -62.5534 | -62.5122 | -0.045776 | 60.141 | -62.2925 | 60.2371 | -62.2055 | -62.3383 | -62.2513 | -0.10986 | 0.013732 | -0.068665 | 0.13733 | -0.27924 | -0.32044 | -0.16937 | -0.21057 | -0.059509 | -0.045777 | 0.050354 | 0.027466 | -0.018311 | -0.10529 | 0.041198 | -0.045777 | 0.24719 | 122.4609 | 0.086975 | 122.5296 | 122.5433 | 122.4335 | 122.4335 | 122.374 | -122.5296 | -122.4792 | 122.3511 | 122.4701 | 62.0773 | 62.1872
472.8281 | 122.5754 | -62.2192 | 60.2371 | 0.0025177 | -0.027188 | -0.027314 | 0.062876 | -0.034502 | -0.049313 | -0.040178 | -0.0021057 | -0.018399 | 0.055559 | 0.048826 | -0.21424 | -0.016846 | -0.023894 | -0.054932 | 60.2325 | -62.3291 | 60.1135 | -62.059 | -62.4893 | -62.471 | 0.013733 | 60.2005 | -62.2559 | 60.2234 | -62.2101 | -62.3062 | -62.2467 | -0.10986 | -0.004578 | -0.1236 | 0.16022 | -0.25177 | -0.27008 | -0.14191 | -0.16022 | -0.036621 | -0.036622 | -0.013733 | 0.009155 | -0.027466 | -0.086975 | 0.009155 | -0.050354 | 0.27008 | 122.4426 | 0.045776 | 122.4792 | 122.5616 | 122.4564 | 122.4518 | 122.4197 | -122.5662 | -122.493 | 122.3328 | 122.4426 | 62.1643 | 62.233
474.5312 | 122.5525 | -62.2192 | 60.2371 | 0.0025177 | -0.025479 | -0.024537 | 0.06608 | -0.030657 | -0.049313 | -0.041887 | -0.0021057 | -0.020536 | 0.055132 | 0.053953 | -0.21402 | -0.015778 | -0.022612 | -0.07782 | 60.2463 | -62.3383 | 60.1135 | -62.0773 | -62.5534 | -62.4985 | -0.068665 | 60.1364 | -62.265 | 60.2188 | -62.2375 | -62.3428 | -62.2742 | -0.11902 | 0.009155 | -0.1236 | 0.14191 | -0.27924 | -0.33417 | -0.16022 | -0.21515 | -0.045777 | -0.10071 | -0.018311 | -0.018311 | -0.054932 | -0.1236 | -0.009155 | -0.077819 | 0.26093 | 122.4518 | 0.027466 | 122.4838 | 122.5845 | 122.4014 | 122.4655 | 122.3557 | -122.5754 | -122.5021 | 122.3328 | 122.438 | 62.1414 | 62.1506
476.2969 | 122.6395 | -62.2421 | 60.1685 | 0.0025177 | -0.02612 | -0.025605 | 0.065439 | -0.030657 | -0.048031 | -0.040605 | 0.00094606 | -0.023313 | 0.058763 | 0.048185 | -0.2183 | -0.01706 | -0.020049 | -0.16022 | 60.1959 | -62.3703 | 60.1135 | -62.0773 | -62.5442 | -62.5168 | -0.082397 | 60.1135 | -62.2559 | 60.2554 | -62.1964 | -62.3062 | -62.2055 | -0.12817 | 0.027466 | -0.054932 | 0.16479 | -0.27466 | -0.30212 | -0.14648 | -0.17395 | -0.013733 | -0.054932 | 0.086975 | 0.045776 | 0.036621 | -0.064087 | 0.050354 | -0.050354 | 0.29297 | 122.4838 | 0.059509 | 122.5113 | 122.5662 | 122.3694 | 122.438 | 122.3557 | -122.5388 | -122.4243 | 122.3557 | 122.4976 | 62.0819 | 62.1597
478.0625 | 122.6303 | -62.2192 | 60.228 | 0.0025177 | -0.025479 | -0.025605 | 0.06373 | -0.029162 | -0.050595 | -0.040178 | 0.0039979 | -0.020749 | 0.057695 | 0.043699 | -0.21616 | -0.014283 | -0.023467 | -0.009155 | 60.2005 | -62.3291 | 60.173 | -62.0178 | -62.4664 | -62.4481 | 0.091553 | 60.1593 | -62.2559 | 60.2737 | -62.1552 | -62.2787 | -62.1918 | -0.10986 | -0.027466 | -0.054931 | 0.20142 | -0.22888 | -0.24719 | -0.11902 | -0.13733 | -0.036621 | -0.068664 | 0.045777 | 0.064087 | 0.027466 | -0.05951 | 0.064087 | -0.022889 | 0.31128 | 122.5021 | 0.10071 | 122.5296 | 122.5296 | 122.4152 | 122.4197 | 122.3785 | -122.5571 | -122.4838 | 122.3923 | 122.493 | 62.2101 | 62.3108
479.8438 | 122.6166 | -62.233 | 60.2188 | 0.0025177 | -0.025265 | -0.025391 | 0.064371 | -0.02788 | -0.047817 | -0.041246 | -0.0021057 | -0.018613 | 0.057909 | 0.045408 | -0.21531 | -0.01706 | -0.021117 | -0.027466 | 60.2188 | -62.3154 | 60.1822 | -61.9995 | -62.4664 | -62.4207 | 0.091553 | 60.1181 | -62.2513 | 60.2829 | -62.146 | -62.2787 | -62.1964 | -0.082398 | 0 | -0.036621 | 0.23346 | -0.18768 | -0.23346 | -0.10529 | -0.15106 | -0.018311 | -0.10071 | 0.064087 | 0.086975 | 0.036621 | -0.045777 | 0.054932 | -0.027466 | 0.31586 | 122.4976 | 0.10529 | 122.5342 | 122.5342 | 122.3694 | 122.4518 | 122.3511 | -122.5342 | -122.4701 | 122.4152 | 122.5159 | 62.2055 | 62.3245
481.625 | 122.58 | -62.2238 | 60.2371 | 0.0025177 | -0.025265 | -0.024537 | 0.061167 | -0.032366 | -0.051876 | -0.041033 | 0.0039979 | -0.019467 | 0.055986 | 0.044553 | -0.21552 | -0.017273 | -0.02133 | 0.022888 | 60.1868 | -62.3016 | 60.1959 | -61.9904 | -62.4298 | -62.4069 | 0.07782 | 60.1685 | -62.233 | 60.228 | -62.1735 | -62.2833 | -62.2421 | -0.07782 | -0.050354 | -0.041199 | 0.23346 | -0.1831 | -0.20599 | -0.10528 | -0.12817 | -0.009155 | -0.068665 | -0.009156 | 0.050354 | -0.01831 | -0.059509 | -0.009155 | -0.050354 | 0.31128 | 122.4976 | 0.059509 | 122.4609 | 122.4884 | 122.4014 | 122.4106 | 122.3923 | -122.5388 | -122.4701 | 122.4197 | 122.4518 | 62.2467 | 62.3016
483.4062 | 122.58 | -62.2559 | 60.2371 | 0.0025177 | -0.025479 | -0.024964 | 0.06608 | -0.031725 | -0.048886 | -0.038469 | 0.00094606 | -0.019254 | 0.058123 | 0.045835 | -0.21702 | -0.015351 | -0.021971 | -0.054932 | 60.2051 | -62.3474 | 60.141 | -62.0407 | -62.5214 | -62.4756 | 0.004578 | 60.1593 | -62.2559 | 60.2142 | -62.2192 | -62.3428 | -62.2604 | -0.091553 | -0.032044 | -0.096131 | 0.21515 | -0.21973 | -0.2655 | -0.12817 | -0.17395 | 0 | -0.07782 | -0.022889 | 0.036621 | -0.004578 | -0.086975 | -0.004578 | -0.086975 | 0.3067 | 122.4884 | 0.036621 | 122.4701 | 122.5525 | 122.4152 | 122.4609 | 122.4152 | -122.5845 | -122.493 | 122.3969 | 122.4701 | 62.2009 | 62.2604
485.125 | 122.6578 | -62.2192 | 60.1776 | 0.010147 | -0.027615 | -0.023469 | 0.062235 | -0.030443 | -0.049526 | -0.039751 | 0.00094606 | -0.020963 | 0.0562 | 0.04733 | -0.21872 | -0.018555 | -0.020689 | -0.1236 | 60.1456 | -62.352 | 60.1639 | -61.9766 | -62.4664 | -62.4161 | 0.027466 | 60.0952 | -62.2696 | 60.2646 | -62.146 | -62.2559 | -62.2055 | -0.13275 | -0.032043 | -0.013733 | 0.24261 | -0.19684 | -0.24719 | -0.064087 | -0.11444 | -0.050354 | -0.082397 | 0.086975 | 0.073242 | 0.013733 | -0.036621 | 0.064087 | 0.013733 | 0.37537 | 122.5159 | 0.1236 | 122.5342 | 122.4976 | 122.3648 | 122.3648 | 122.3145 | -122.5296 | -122.4472 | 122.3831 | 122.4838 | 62.0956 | 62.2467
486.9062 | 122.5616 | -62.2467 | 60.2417 | -0.0051118 | -0.022702 | -0.025177 | 0.065012 | -0.03557 | -0.046108 | -0.039537 | -0.0021057 | -0.017972 | 0.054918 | 0.049467 | -0.2168 | -0.015992 | -0.023467 | -0.091553 | 60.2142 | -62.3611 | 60.1227 | -62.0636 | -62.5488 | -62.5122 | -0.054932 | 60.1456 | -62.2421 | 60.1913 | -62.233 | -62.3566 | -62.2604 | -0.11444 | -0.027466 | -0.11902 | 0.1831 | -0.2655 | -0.30212 | -0.15106 | -0.18768 | 0.004578 | -0.09613 | -0.050354 | 0.013733 | -0.013733 | -0.10986 | -0.018311 | -0.11444 | 0.29755 | 122.4838 | 0.009155 | 122.4335 | 122.5754 | 122.3877 | 122.4609 | 122.3923 | -122.6028 | -122.4838 | 122.3694 | 122.438 | 62.1552 | 62.1918
488.6719 | 122.5845 | -62.2467 | 60.1868 | -0.0051118 | -0.027829 | -0.024109 | 0.065653 | -0.029162 | -0.050595 | -0.037828 | 0.00094606 | -0.019467 | 0.0562 | 0.04498 | -0.21702 | -0.015351 | -0.020689 | -0.16479 | 60.1959 | -62.3749 | 60.1044 | -62.0819 | -62.5671 | -62.5122 | -0.07782 | 60.1318 | -62.2833 | 60.2371 | -62.2147 | -62.3428 | -62.2513 | -0.12817 | 0.009155 | -0.082398 | 0.16479 | -0.2655 | -0.32043 | -0.13733 | -0.19226 | -0.036621 | -0.054932 | 0.050354 | 0.032043 | -0.004578 | -0.09613 | 0.032043 | -0.059509 | 0.29297 | 122.4792 | 0.068664 | 122.5204 | 122.5708 | 122.4152 | 122.4426 | 122.3785 | -122.5616 | -122.4701 | 122.3511 | 122.4838 | 62.0819 | 62.1689
490.3906 | 122.6257 | -62.1872 | 60.2234 | -0.0051118 | -0.02612 | -0.02475 | 0.064157 | -0.031511 | -0.048031 | -0.039324 | 0.00094606 | -0.020322 | 0.057482 | 0.052671 | -0.21573 | -0.017273 | -0.016417 | -0.022888 | 60.2371 | -62.3062 | 60.1822 | -61.9858 | -62.4664 | -62.4344 | 0.073242 | 60.1501 | -62.2559 | 60.2783 | -62.1368 | -62.2604 | -62.2055 | -0.11902 | 0.013733 | -0.041199 | 0.20142 | -0.24719 | -0.27924 | -0.12817 | -0.16022 | -0.068664 | -0.073243 | 0.054931 | 0.050354 | -0.01831 | -0.073242 | 0.050354 | -0.004578 | 0.32043 | 122.4884 | 0.11902 | 122.5342 | 122.5433 | 122.406 | 122.4243 | 122.3373 | -122.5296 | -122.4792 | 122.3694 | 122.4655 | 62.1643 | 62.2604
492.1719 | 122.5891 | -62.2284 | 60.228 | 0.0025177 | -0.02377 | -0.026032 | 0.065439 | -0.03557 | -0.048245 | -0.03911 | 0.00094606 | -0.019895 | 0.054491 | 0.047758 | -0.21573 | -0.015565 | -0.021117 | -0.13733 | 60.2097 | -62.3657 | 60.0952 | -62.0956 | -62.5534 | -62.5168 | -0.082397 | 60.1135 | -62.2787 | 60.2005 | -62.2375 | -62.3657 | -62.2696 | -0.13733 | -0.01831 | -0.13275 | 0.13275 | -0.28839 | -0.32501 | -0.15106 | -0.18768 | -0.050354 | -0.11444 | -0.027466 | -0.009155 | -0.041198 | -0.13733 | 0.009156 | -0.086975 | 0.27008 | 122.4609 | 0.041199 | 122.4792 | 122.5754 | 122.3923 | 122.4381 | 122.3419 | -122.5937 | -122.5067 | 122.3236 | 122.4289 | 62.0911 | 62.146
493.9531 | 122.5708 | -62.233 | 60.2463 | 0.0025177 | -0.028256 | -0.026673 | 0.06138 | -0.033434 | -0.050381 | -0.038683 | 0.00094606 | -0.018186 | 0.057695 | 0.043699 | -0.21552 | -0.015992 | -0.021544 | -0.050354 | 60.2325 | -62.3566 | 60.1273 | -62.0407 | -62.4847 | -62.4664 | 0.041199 | 60.1685 | -62.2467 | 60.2097 | -62.1872 | -62.3016 | -62.2513 | -0.1236 | -0.013733 | -0.11902 | 0.19226 | -0.23346 | -0.25177 | -0.10986 | -0.12817 | -0.013733 | -0.07782 | -0.036621 | 0.045776 | -0.018311 | -0.068665 | -0.004578 | -0.054932 | 0.31586 | 122.4838 | 0.059509 | 122.4564 | 122.5891 | 122.4152 | 122.4655 | 122.4014 | -122.6028 | -122.493 | 122.3602 | 122.4426 | 62.1826 | 62.2742
495.6562 | 122.6257 | -62.2375 | 60.1776 | 0.010147 | -0.024838 | -0.024323 | 0.065866 | -0.028734 | -0.048886 | -0.039324 | 0.00094606 | -0.018827 | 0.057695 | 0.051176 | -0.21338 | -0.015778 | -0.022185 | -0.16022 | 60.1959 | -62.3611 | 60.1089 | -62.0819 | -62.5626 | -62.5214 | -0.068665 | 60.1227 | -62.2742 | 60.2417 | -62.2055 | -62.3199 | -62.2375 | -0.1236 | 0.018311 | -0.068664 | 0.15564 | -0.28381 | -0.32501 | -0.16022 | -0.20142 | -0.036621 | -0.054931 | 0.064087 | 0.032044 | 0 | -0.082397 | 0.036621 | -0.045776 | 0.27924 | 122.4701 | 0.068665 | 122.5159 | 122.5571 | 122.3969 | 122.4335 | 122.3602 | -122.5388 | -122.4518 | 122.3465 | 122.4792 | 62.0773 | 62.1689
497.4375 | 122.6212 | -62.2009 | 60.2325 | -0.0051118 | -0.025479 | -0.024964 | 0.065012 | -0.027453 | -0.049954 | -0.03911 | -0.0021057 | -0.018399 | 0.054277 | 0.043485 | -0.21616 | -0.016633 | -0.024321 | -0.018311 | 60.228 | -62.3245 | 60.1776 | -61.9995 | -62.4664 | -62.4298 | 0.086975 | 60.173 | -62.265 | 60.2646 | -62.1506 | -62.2559 | -62.1826 | -0.1236 | -0.004578 | -0.054932 | 0.20142 | -0.22888 | -0.2655 | -0.10529 | -0.14191 | -0.064087 | -0.059509 | 0.032043 | 0.050354 | 0.018311 | -0.054931 | 0.082398 | 0.009156 | 0.32501 | 122.5021 | 0.11444 | 122.5296 | 122.5525 | 122.4381 | 122.4289 | 122.374 | -122.5571 | -122.4976 | 122.3785 | 122.4655 | 62.1826 | 62.2879
499.1562 | 122.7219 | -62.1826 | 60.1822 | 0.010147 | -0.02676 | -0.025818 | 0.062876 | -0.028093 | -0.04739 | -0.040819 | 0.00094606 | -0.020963 | 0.0562 | 0.034727 | -0.21552 | -0.017914 | -0.024962 | -0.027466 | 60.1593 | -62.2971 | 60.228 | -61.9125 | -62.384 | -62.3337 | 0.17853 | 60.0952 | -62.2238 | 60.3424 | -62.0407 | -62.146 | -62.1094 | -0.11444 | -0.022888 | 0.045776 | 0.27008 | -0.15106 | -0.20142 | -0.036621 | -0.086975 | -0.041199 | -0.086975 | 0.16022 | 0.14191 | 0.073242 | 0.036621 | 0.11444 | 0.07782 | 0.38452 | 122.525 | 0.18311 | 122.5662 | 122.4564 | 122.319 | 122.3419 | 122.2778 | -122.4792 | -122.406 | 122.4106 | 122.525 | 62.1552 | 62.3611
500.9219 | 122.5891 | -62.1918 | 60.2234 | -0.0051118 | -0.026974 | -0.025605 | 0.062021 | -0.038561 | -0.049954 | -0.04146 | -0.0021057 | -0.02139 | 0.054705 | 0.050107 | -0.21552 | -0.01706 | -0.02133 | 0.009155 | 60.1868 | -62.3154 | 60.2097 | -61.9766 | -62.4298 | -62.4023 | 0.086975 | 60.1501 | -62.2421 | 60.2417 | -62.1597 | -62.2879 | -62.2375 | -0.1236 | -0.036621 | -0.013733 | 0.21515 | -0.21057 | -0.23804 | -0.086975 | -0.11444 | -0.050354 | -0.073243 | 0.01831 | 0.032043 | -0.045777 | -0.096131 | 0.004577 | -0.045777 | 0.33874 | 122.525 | 0.082397 | 122.4838 | 122.5021 | 122.3923 | 122.3785 | 122.3419 | -122.5388 | -122.4655 | 122.4014 | 122.4335 | 62.2009 | 62.2787
502.7031 | 122.6028 | -62.1964 | 60.228 | 0.010147 | -0.027829 | -0.026459 | 0.060953 | -0.033434 | -0.050167 | -0.040178 | 0.00094606 | -0.020963 | 0.055345 | 0.046049 | -0.21595 | -0.019196 | -0.024107 | 0.018311 | 60.173 | -62.3108 | 60.2097 | -61.9675 | -62.4115 | -62.4023 | 0.1236 | 60.1547 | -62.2284 | 60.2509 | -62.1414 | -62.2559 | -62.2147 | -0.11444 | -0.054931 | -0.01831 | 0.22888 | -0.20599 | -0.21515 | -0.091553 | -0.10071 | -0.032044 | -0.073242 | 0.022888 | 0.054932 | -0.018311 | -0.059509 | 0.013733 | -0.027465 | 0.34332 | 122.5204 | 0.086976 | 122.4792 | 122.4838 | 122.3831 | 122.3694 | 122.3511 | -122.5388 | -122.4564 | 122.406 | 122.4472 | 62.2147 | 62.3199
504.4844 | 122.6761 | -62.2192 | 60.1501 | -0.0051118 | -0.024197 | -0.024323 | 0.06373 | -0.032793 | -0.048245 | -0.038896 | -0.0021057 | -0.019895 | 0.0562 | 0.048826 | -0.2168 | -0.015992 | -0.022612 | -0.15106 | 60.1959 | -62.3428 | 60.1318 | -62.0544 | -62.5305 | -62.4893 | -0.027466 | 60.1135 | -62.2787 | 60.2783 | -62.1552 | -62.2742 | -62.2009 | -0.1236 | 0.045777 | -0.01831 | 0.16479 | -0.27008 | -0.31128 | -0.14648 | -0.18768 | -0.05951 | -0.036621 | 0.12817 | 0.064087 | 0.01831 | -0.054932 | 0.07782 | 0.004578 | 0.28839 | 122.4747 | 0.1236 | 122.5571 | 122.5388 | 122.3923 | 122.4152 | 122.3328 | -122.493 | -122.4289 | 122.3511 | 122.4976 | 62.0682 | 62.1918
506.25 | 122.612 | -62.2055 | 60.1776 | -0.0051118 | -0.025479 | -0.027527 | 0.065439 | -0.031298 | -0.04974 | -0.040605 | -0.0082091 | -0.01904 | 0.055559 | 0.04498 | -0.21573 | -0.015351 | -0.02133 | -0.15106 | 60.1776 | -62.3657 | 60.1044 | -62.0819 | -62.558 | -62.5076 | -0.068665 | 60.1318 | -62.2742 | 60.2417 | -62.2009 | -62.3245 | -62.2375 | -0.16022 | 0 | -0.073242 | 0.1236 | -0.30212 | -0.35248 | -0.14191 | -0.19226 | -0.068665 | -0.045776 | 0.064087 | 0.004577 | -0.032044 | -0.11902 | 0.036621 | -0.050354 | 0.28381 | 122.4701 | 0.073242 | 122.5159 | 122.5433 | 122.406 | 122.3831 | 122.3373 | -122.5433 | -122.4518 | 122.3099 | 122.4472 | 62.0544 | 62.1368
508.0156 | 122.5754 | -62.2467 | 60.1822 | 0.0025177 | -0.027188 | -0.026032 | 0.065012 | -0.032366 | -0.048886 | -0.040605 | -0.0021057 | -0.020963 | 0.057695 | 0.051389 | -0.21467 | -0.016633 | -0.021971 | -0.12817 | 60.2234 | -62.3611 | 60.0861 | -62.1048 | -62.5717 | -62.5168 | -0.068665 | 60.1501 | -62.2833 | 60.2097 | -62.2284 | -62.3795 | -62.2604 | -0.11444 | 0.041199 | -0.09613 | 0.14191 | -0.27008 | -0.32501 | -0.15564 | -0.21057 | -0.036621 | -0.032044 | 0.027466 | 0.01831 | -0.013733 | -0.13275 | 0.022888 | -0.096131 | 0.25635 | 122.4472 | 0.054931 | 122.493 | 122.5845 | 122.4335 | 122.4701 | 122.3969 | -122.5433 | -122.4655 | 122.3328 | 122.4564 | 62.1185 | 62.178
509.7656 | 122.5616 | -62.2467 | 60.1959 | 0.010147 | -0.023556 | -0.023469 | 0.064585 | -0.031511 | -0.047177 | -0.039324 | 0.00094606 | -0.019895 | 0.056841 | 0.050748 | -0.21595 | -0.015778 | -0.022826 | -0.16022 | 60.2371 | -62.352 | 60.0906 | -62.1048 | -62.5717 | -62.5214 | -0.086975 | 60.1364 | -62.2696 | 60.1959 | -62.2513 | -62.3795 | -62.265 | -0.10529 | 0.041199 | -0.10529 | 0.14191 | -0.27466 | -0.32501 | -0.16937 | -0.21973 | -0.022888 | -0.059509 | 0 | -0.004578 | -0.018311 | -0.13275 | 0.004577 | -0.10986 | 0.24719 | 122.4426 | 0.01831 | 122.4655 | 122.5891 | 122.406 | 122.4838 | 122.3831 | -122.5479 | -122.4655 | 122.3373 | 122.4426 | 62.0865 | 62.1597
511.5469 | 122.612 | -62.2055 | 60.2097 | -0.0051118 | -0.025265 | -0.023896 | 0.064585 | -0.032366 | -0.049526 | -0.041674 | 0.00094606 | -0.019681 | 0.054918 | 0.051389 | -0.21552 | -0.014496 | -0.022826 | -0.018311 | 60.2417 | -62.3383 | 60.1639 | -62.0224 | -62.4756 | -62.4435 | 0.059509 | 60.1639 | -62.2421 | 60.2554 | -62.1506 | -62.2833 | -62.2147 | -0.13275 | 0.032043 | -0.045777 | 0.18311 | -0.23804 | -0.27008 | -0.10529 | -0.13733 | -0.036621 | -0.045777 | 0.045776 | 0.054931 | -0.009156 | -0.07782 | 0.027465 | -0.041199 | 0.31586 | 122.5021 | 0.091552 | 122.4976 | 122.58 | 122.406 | 122.4472 | 122.3694 | -122.5479 | -122.4518 | 122.3694 | 122.4609 | 62.1872 | 62.265
513.3125 | 122.6028 | -62.2055 | 60.2234 | -0.0051118 | -0.026333 | -0.023896 | 0.064371 | -0.026598 | -0.047817 | -0.04146 | -0.0021057 | -0.018827 | 0.056414 | 0.054166 | -0.21531 | -0.014069 | -0.021544 | -0.032043 | 60.2097 | -62.3428 | 60.1776 | -62.0132 | -62.4619 | -62.4435 | 0.050354 | 60.173 | -62.2559 | 60.2509 | -62.1689 | -62.3062 | -62.2238 | -0.13733 | -0.013733 | -0.045777 | 0.19226 | -0.23804 | -0.25635 | -0.10071 | -0.11902 | -0.050354 | -0.050354 | 0.027465 | 0.036621 | -0.018311 | -0.10071 | 0.032043 | -0.050354 | 0.32959 | 122.5204 | 0.086975 | 122.5067 | 122.5525 | 122.4289 | 122.4152 | 122.3785 | -122.5662 | -122.4792 | 122.3831 | 122.4564 | 62.1735 | 62.2559
515.0156 | 122.6807 | -62.2101 | 60.1593 | -0.0051118 | -0.024838 | -0.024109 | 0.063944 | -0.033434 | -0.04739 | -0.040392 | -0.0021057 | -0.02139 | 0.057695 | 0.047544 | -0.21509 | -0.016633 | -0.021117 | -0.10529 | 60.1456 | -62.3245 | 60.2051 | -61.9583 | -62.4573 | -62.3886 | 0.068665 | 60.0449 | -62.2559 | 60.3195 | -62.1094 | -62.2192 | -62.146 | -0.11444 | -0.013733 | 0.045776 | 0.25177 | -0.17853 | -0.24719 | -0.064087 | -0.13275 | -0.045776 | -0.11444 | 0.16022 | 0.10071 | 0.064087 | -0.009155 | 0.10986 | 0.036621 | 0.36621 | 122.5296 | 0.14648 | 122.5754 | 122.4701 | 122.3007 | 122.3557 | 122.2549 | -122.4838 | -122.4152 | 122.4152 | 122.5296 | 62.1048 | 62.2787
516.8281 | 122.7036 | -62.2147 | 60.1959 | 0.0025177 | -0.028042 | -0.02475 | 0.062235 | -0.033648 | -0.049954 | -0.038683 | -0.0021057 | -0.020322 | 0.056841 | 0.041349 | -0.21531 | -0.017914 | -0.017485 | -0.036621 | 60.1822 | -62.2971 | 60.2417 | -61.8988 | -62.3932 | -62.3428 | 0.1831 | 60.0769 | -62.2284 | 60.3378 | -62.0407 | -62.1506 | -62.114 | -0.082397 | -0.013733 | 0.045776 | 0.31586 | -0.12817 | -0.17853 | -0.045776 | -0.09613 | -0.013733 | -0.11902 | 0.14191 | 0.17395 | 0.10071 | 0.064087 | 0.11444 | 0.07782 | 0.39825 | 122.5388 | 0.18768 | 122.5662 | 122.4792 | 122.3053 | 122.3969 | 122.2916 | -122.493 | -122.4243 | 122.4564 | 122.5525 | 62.178 | 62.3978
518.625 | 122.5662 | -62.2147 | 60.2417 | 0.010147 | -0.028897 | -0.026032 | 0.062448 | -0.033861 | -0.04974 | -0.038469 | -0.0021057 | -0.020536 | 0.054705 | 0.047544 | -0.21766 | -0.01706 | -0.02368 | 0.004578 | 60.1822 | -62.3337 | 60.1868 | -61.9812 | -62.4252 | -62.3886 | 0.091553 | 60.1456 | -62.2284 | 60.2371 | -62.1689 | -62.2696 | -62.2375 | -0.11902 | -0.059509 | -0.054931 | 0.23346 | -0.17395 | -0.21057 | -0.054932 | -0.091553 | -0.013733 | -0.09613 | -0.004577 | 0.045777 | -0.022888 | -0.054931 | -0.009155 | -0.041198 | 0.35248 | 122.5204 | 0.05951 | 122.4655 | 122.5159 | 122.374 | 122.3969 | 122.3602 | -122.5754 | -122.4701 | 122.4014 | 122.4518 | 62.2192 | 62.3062
520.75 | 122.5708 | -62.2467 | 60.2142 | -0.012741 | -0.023129 | -0.02475 | 0.066294 | -0.030871 | -0.048886 | -0.04146 | 0.00094606 | -0.017972 | 0.055132 | 0.050535 | -0.21637 | -0.017487 | -0.021758 | -0.1236 | 60.1822 | -62.352 | 60.0998 | -62.114 | -62.5854 | -62.5122 | -0.082397 | 60.141 | -62.2559 | 60.2005 | -62.2513 | -62.3611 | -62.2696 | -0.10529 | -0.032043 | -0.11444 | 0.13275 | -0.2655 | -0.33874 | -0.16022 | -0.23346 | -0.009155 | -0.073242 | -0.013733 | -0.004578 | -0.022888 | -0.11444 | -0.013733 | -0.10529 | 0.23804 | 122.4518 | 0.004577 | 122.4564 | 122.5342 | 122.3969 | 122.4289 | 122.3877 | -122.5662 | -122.4701 | 122.3465 | 122.4472 | 62.1231 | 62.1643
522.5469 | 122.699 | -62.1689 | 60.141 | -0.0051118 | -0.025051 | -0.022614 | 0.063944 | -0.029802 | -0.045468 | -0.038683 | -0.0021057 | -0.022245 | 0.053209 | 0.045621 | -0.21744 | -0.015351 | -0.02133 | -0.091553 | 60.1456 | -62.3383 | 60.2097 | -61.9629 | -62.4481 | -62.4115 | 0.050354 | 60.0723 | -62.265 | 60.3149 | -62.1048 | -62.2375 | -62.146 | -0.16937 | 0.004578 | 0.068665 | 0.20599 | -0.24262 | -0.27924 | -0.073242 | -0.10986 | -0.096131 | -0.068664 | 0.17395 | 0.064087 | 0.022888 | -0.068665 | 0.11902 | 0.027466 | 0.37537 | 122.5479 | 0.16022 | 122.58 | 122.4838 | 122.3373 | 122.3145 | 122.2412 | -122.4792 | -122.406 | 122.3785 | 122.4838 | 62.0773 | 62.2192
524.4688 | 122.5571 | -62.2559 | 60.1913 | -0.0051118 | -0.024838 | -0.025177 | 0.064371 | -0.030657 | -0.048245 | -0.03676 | 0.00094606 | -0.018186 | 0.057909 | 0.045408 | -0.21595 | -0.01471 | -0.019194 | -0.14648 | 60.228 | -62.3703 | 60.0906 | -62.1048 | -62.558 | -62.5305 | -0.082397 | 60.1593 | -62.2925 | 60.2051 | -62.233 | -62.352 | -62.2696 | -0.11444 | 0.036621 | -0.10071 | 0.15106 | -0.27466 | -0.30212 | -0.16022 | -0.18768 | -0.036621 | -0.032043 | 0.013733 | 0.022888 | -0.013733 | -0.096131 | 0.022888 | -0.05951 | 0.2655 | 122.4609 | 0.059509 | 122.4976 | 122.5983 | 122.4518 | 122.4838 | 122.4152 | -122.5616 | -122.4838 | 122.3465 | 122.4609 | 62.1094 | 62.1735
528.8594 | 122.5708 | -62.2009 | 60.1913 | 0.0025177 | -0.024197 | -0.023469 | 0.065439 | -0.029589 | -0.050595 | -0.037828 | 0.00094606 | -0.017972 | 0.057695 | 0.052244 | -0.2168 | -0.015137 | -0.020903 | -0.036621 | 60.2097 | -62.3428 | 60.1639 | -62.0178 | -62.4985 | -62.4619 | 0.032043 | 60.1685 | -62.2559 | 60.2188 | -62.2055 | -62.3199 | -62.2238 | -0.14191 | 0.018311 | -0.027466 | 0.18311 | -0.26093 | -0.29755 | -0.11902 | -0.15564 | -0.054931 | -0.022888 | 0.027466 | -0.004577 | -0.022888 | -0.11902 | 0.032043 | -0.064087 | 0.32501 | 122.5067 | 0.050354 | 122.4747 | 122.5525 | 122.4243 | 122.4106 | 122.3694 | -122.5342 | -122.4472 | 122.3648 | 122.4197 | 62.1643 | 62.233
530.9062 | 122.5983 | -62.1964 | 60.2188 | 0.017777 | -0.026333 | -0.026459 | 0.06608 | -0.031084 | -0.049313 | -0.040392 | -0.0021057 | -0.019895 | 0.055345 | 0.048185 | -0.2168 | -0.017487 | -0.022185 | -0.041199 | 60.2234 | -62.3428 | 60.1318 | -62.059 | -62.4847 | -62.4664 | 0.027466 | 60.1639 | -62.2375 | 60.2371 | -62.1552 | -62.2787 | -62.1918 | -0.14648 | 0.004578 | -0.086975 | 0.13733 | -0.27008 | -0.28839 | -0.1236 | -0.14191 | -0.041199 | -0.054932 | 0.018311 | 0.041199 | 0.004578 | -0.082398 | 0.045777 | -0.041199 | 0.28381 | 122.4747 | 0.082398 | 122.4747 | 122.5662 | 122.4014 | 122.4197 | 122.3602 | -122.5616 | -122.4564 | 122.3282 | 122.4335 | 62.1552 | 62.2238
532.6875 | 122.7081 | -62.1826 | 60.173 | -0.0051118 | -0.027615 | -0.02475 | 0.059458 | -0.033434 | -0.050808 | -0.041674 | 0.00094606 | -0.022245 | 0.054705 | 0.040281 | -0.21637 | -0.01706 | -0.027525 | -0.045776 | 60.1776 | -62.3337 | 60.2188 | -61.908 | -62.384 | -62.3566 | 0.15106 | 60.0952 | -62.233 | 60.3241 | -62.059 | -62.1735 | -62.1323 | -0.15106 | 0.004577 | 0.045776 | 0.27466 | -0.17395 | -0.20142 | -0.022888 | -0.050354 | -0.050354 | -0.07782 | 0.15106 | 0.1236 | 0.050354 | 0.009155 | 0.10071 | 0.059509 | 0.42572 | 122.5525 | 0.17395 | 122.5571 | 122.5113 | 122.3282 | 122.3602 | 122.2778 | -122.5067 | -122.406 | 122.4014 | 122.5067 | 62.1368 | 62.3337
534.4375 | 122.58 | -62.2238 | 60.2097 | 0.010147 | -0.025265 | -0.023041 | 0.067362 | -0.025957 | -0.050167 | -0.041887 | 0.00094606 | -0.01904 | 0.054491 | 0.052457 | -0.21445 | -0.016633 | -0.019621 | -0.032043 | 60.2097 | -62.3474 | 60.1639 | -61.9995 | -62.4802 | -62.4527 | 0.045776 | 60.1547 | -62.2375 | 60.2417 | -62.1735 | -62.3016 | -62.2284 | -0.1236 | 0 | -0.045777 | 0.2243 | -0.22888 | -0.25635 | -0.10529 | -0.13275 | -0.013733 | -0.054932 | 0.032043 | 0.050354 | -0.004578 | -0.07782 | 0.009155 | -0.064087 | 0.3479 | 122.5113 | 0.064087 | 122.4792 | 122.5571 | 122.3923 | 122.4335 | 122.3785 | -122.5571 | -122.4472 | 122.3877 | 122.4655 | 62.1918 | 62.2696
536.375 | 122.644 | -62.2192 | 60.1868 | -0.0051118 | -0.027401 | -0.025605 | 0.062235 | -0.03258 | -0.051876 | -0.039751 | -0.0021057 | -0.023313 | 0.058123 | 0.053098 | -0.21274 | -0.016205 | -0.025389 | -0.13275 | 60.1364 | -62.3154 | 60.1364 | -62.0316 | -62.4619 | -62.4207 | 0.036621 | 60.1044 | -62.2467 | 60.26 | -62.1368 | -62.2467 | -62.1872 | -0.096131 | -0.050354 | -0.050354 | 0.18768 | -0.20142 | -0.24262 | -0.10529 | -0.14648 | -0.027466 | -0.082398 | 0.073242 | 0.082397 | 0.032043 | -0.027466 | 0.059509 | 0 | 0.28381 | 122.4518 | 0.10986 | 122.5067 | 122.4518 | 122.3511 | 122.3557 | 122.3236 | -122.5021 | -122.4335 | 122.3557 | 122.4792 | 62.0865 | 62.2559
538.875 | 122.6669 | -62.2238 | 60.1685 | -0.0051118 | -0.026974 | -0.024323 | 0.060526 | -0.032366 | -0.051235 | -0.041674 | -0.0021057 | -0.022885 | 0.053209 | 0.04434 | -0.21616 | -0.01706 | -0.024962 | -0.10986 | 60.1547 | -62.3245 | 60.173 | -62.0041 | -62.4573 | -62.4069 | 0.041199 | 60.0998 | -62.2375 | 60.2783 | -62.1231 | -62.2147 | -62.1597 | -0.10071 | -0.013733 | 0.004578 | 0.21973 | -0.1831 | -0.23346 | -0.082397 | -0.13275 | -0.013733 | -0.068665 | 0.10986 | 0.10071 | 0.064087 | 0.009155 | 0.07782 | 0.022888 | 0.32043 | 122.4976 | 0.11444 | 122.5159 | 122.4792 | 122.3373 | 122.3785 | 122.3236 | -122.493 | -122.406 | 122.3969 | 122.5021 | 62.114 | 62.265
540.6562 | 122.5525 | -62.2192 | 60.228 | -0.012741 | -0.027188 | -0.025391 | 0.062876 | -0.034075 | -0.052731 | -0.038256 | -0.0021057 | -0.019467 | 0.056414 | 0.04733 | -0.21637 | -0.017273 | -0.022826 | -0.059509 | 60.228 | -62.3154 | 60.1364 | -62.0499 | -62.4802 | -62.4527 | 0.032043 | 60.1959 | -62.233 | 60.2142 | -62.1872 | -62.3108 | -62.233 | -0.096131 | 0 | -0.091552 | 0.16937 | -0.23346 | -0.26093 | -0.13733 | -0.1648 | -0.013733 | -0.032043 | -0.013733 | 0.032043 | -0.013733 | -0.091553 | 0 | -0.07782 | 0.2655 | 122.4518 | 0.045776 | 122.4472 | 122.5433 | 122.4289 | 122.4472 | 122.4152 | -122.5433 | -122.4609 | 122.3557 | 122.4335 | 62.1597 | 62.2513
542.5781 | 122.644 | -62.2101 | 60.1776 | 0.0025177 | -0.025692 | -0.02475 | 0.063089 | -0.029375 | -0.04974 | -0.042314 | -0.0021057 | -0.022885 | 0.05855 | 0.049894 | -0.21573 | -0.01941 | -0.022398 | -0.10071 | 60.1776 | -62.3428 | 60.1685 | -61.9995 | -62.4435 | -62.4115 | 0.050354 | 60.0906 | -62.2513 | 60.2692 | -62.1002 | -62.2284 | -62.1597 | -0.13275 | 0 | -0.009155 | 0.21057 | -0.20142 | -0.23346 | -0.068665 | -0.10071 | -0.041199 | -0.086975 | 0.091553 | 0.10986 | 0.050354 | -0.018311 | 0.091553 | 0.022888 | 0.34332 | 122.5113 | 0.15106 | 122.5204 | 122.5204 | 122.3419 | 122.3877 | 122.3007 | -122.5204 | -122.4289 | 122.3785 | 122.4792 | 62.1094 | 62.2604
544.4062 | 122.6624 | -62.2009 | 60.1685 | -0.0051118 | -0.025265 | -0.023896 | 0.064585 | -0.031725 | -0.047817 | -0.040392 | -0.0021057 | -0.019254 | 0.054918 | 0.049467 | -0.21787 | -0.018555 | -0.021117 | -0.10986 | 60.1135 | -62.3337 | 60.2051 | -61.9675 | -62.4481 | -62.3886 | 0.054932 | 60.0723 | -62.2421 | 60.3195 | -62.1094 | -62.2192 | -62.1506 | -0.13275 | -0.054932 | 0.036621 | 0.23346 | -0.18768 | -0.24719 | -0.054932 | -0.11444 | -0.041198 | -0.09613 | 0.15106 | 0.091553 | 0.050354 | -0.01831 | 0.091552 | 0.022888 | 0.36621 | 122.5388 | 0.13275 | 122.5616 | 122.4472 | 122.3145 | 122.3145 | 122.2733 | -122.5021 | -122.4106 | 122.406 | 122.5204 | 62.0911 | 62.2559
546.2812 | 122.525 | -62.2238 | 60.2005 | 0.0025177 | -0.024197 | -0.023041 | 0.064371 | -0.030871 | -0.048672 | -0.040819 | 0.00094606 | -0.019895 | 0.057268 | 0.045194 | -0.21702 | -0.015137 | -0.022185 | -0.12817 | 60.2005 | -62.3611 | 60.0906 | -62.1048 | -62.5442 | -62.5031 | -0.082397 | 60.1593 | -62.2833 | 60.1868 | -62.2513 | -62.3703 | -62.2787 | -0.13733 | 0 | -0.10986 | 0.11902 | -0.27924 | -0.32043 | -0.14191 | -0.1831 | -0.059509 | -0.041198 | -0.013732 | -0.027466 | -0.054932 | -0.14648 | 0.004577 | -0.086975 | 0.25635 | 122.4518 | 0.032043 | 122.4701 | 122.5616 | 122.4426 | 122.4243 | 122.3831 | -122.5616 | -122.4838 | 122.3145 | 122.4106 | 62.0956 | 62.1414
548.0938 | 122.6257 | -62.2238 | 60.1547 | -0.0051118 | -0.025265 | -0.026032 | 0.061594 | -0.028307 | -0.047604 | -0.040819 | 0.00094606 | -0.020536 | 0.054064 | 0.043912 | -0.21573 | -0.016205 | -0.023253 | -0.12817 | 60.1501 | -62.3474 | 60.1456 | -62.0224 | -62.4847 | -62.4115 | 0 | 60.0952 | -62.2559 | 60.228 | -62.146 | -62.2513 | -62.1872 | -0.1236 | -0.004578 | -0.009155 | 0.20142 | -0.18768 | -0.26093 | -0.064087 | -0.13733 | -0.032043 | -0.059509 | 0.073242 | 0.07782 | 0.036621 | -0.027466 | 0.068664 | 0.004577 | 0.32501 | 122.493 | 0.10986 | 122.4838 | 122.4976 | 122.3511 | 122.374 | 122.319 | -122.5021 | -122.4106 | 122.3694 | 122.4518 | 62.0956 | 62.2238
549.9062 | 122.5342 | -62.2101 | 60.2234 | 0.010147 | -0.025692 | -0.022614 | 0.065866 | -0.02553 | -0.048672 | -0.038042 | -0.0021057 | -0.019895 | 0.056414 | 0.056516 | -0.21637 | -0.016846 | -0.02133 | -0.11444 | 60.2234 | -62.3474 | 60.1181 | -62.0911 | -62.558 | -62.5168 | -0.068665 | 60.1364 | -62.2604 | 60.1868 | -62.2467 | -62.3566 | -62.2696 | -0.13733 | 0 | -0.10529 | 0.11902 | -0.3067 | -0.3479 | -0.16937 | -0.21057 | -0.050354 | -0.086975 | -0.036621 | -0.036621 | -0.059509 | -0.14648 | -0.009155 | -0.09613 | 0.25635 | 122.4655 | 0.013733 | 122.4472 | 122.5708 | 122.3969 | 122.4335 | 122.3465 | -122.5708 | -122.4838 | 122.3282 | 122.3969 | 62.0956 | 62.1414
551.625 | 122.5433 | -62.2375 | 60.2005 | -0.0051118 | -0.024624 | -0.024964 | 0.066507 | -0.029162 | -0.047817 | -0.040392 | 0.00094606 | -0.018827 | 0.055559 | 0.046476 | -0.21552 | -0.014496 | -0.021971 | -0.09613 | 60.2234 | -62.3428 | 60.1135 | -62.0544 | -62.5351 | -62.5031 | -0.064087 | 60.1593 | -62.2421 | 60.2051 | -62.2284 | -62.3566 | -62.2467 | -0.10529 | 0.022889 | -0.086975 | 0.18311 | -0.2655 | -0.29755 | -0.16022 | -0.19226 | -0.004577 | -0.041198 | 0.004578 | 0.009155 | -0.009155 | -0.11902 | -0.004578 | -0.11444 | 0.28839 | 122.4564 | 0.013732 | 122.4472 | 122.5662 | 122.4014 | 122.4609 | 122.3969 | -122.5433 | -122.4426 | 122.3511 | 122.4426 | 62.1414 | 62.1735
553.3438 | 122.5845 | -62.2147 | 60.2005 | 0.010147 | -0.024411 | -0.025177 | 0.065653 | -0.032366 | -0.048672 | -0.040392 | 0.00094606 | -0.020322 | 0.054277 | 0.050748 | -0.21402 | -0.015778 | -0.022398 | -0.041199 | 60.2463 | -62.3383 | 60.1547 | -62.0178 | -62.4664 | -62.4344 | 0.036621 | 60.173 | -62.2375 | 60.2463 | -62.1277 | -62.2787 | -62.2009 | -0.1236 | 0.045777 | -0.045776 | 0.19684 | -0.21973 | -0.25177 | -0.09613 | -0.12817 | -0.022888 | -0.027465 | 0.045777 | 0.086975 | 0.013733 | -0.064087 | 0.036621 | -0.041199 | 0.32043 | 122.493 | 0.10986 | 122.4838 | 122.5845 | 122.4106 | 122.4609 | 122.3877 | -122.5388 | -122.438 | 122.3694 | 122.4609 | 62.1735 | 62.2513
555.0625 | 122.6852 | -62.2147 | 60.141 | 0.0025177 | -0.025906 | -0.025177 | 0.063089 | -0.033007 | -0.046536 | -0.041674 | -0.0021057 | -0.020322 | 0.0562 | 0.045408 | -0.2168 | -0.015565 | -0.018767 | -0.10529 | 60.1593 | -62.3337 | 60.1959 | -61.9766 | -62.4527 | -62.3978 | 0.050354 | 60.0906 | -62.2421 | 60.3149 | -62.1048 | -62.233 | -62.146 | -0.11902 | 0.018311 | 0.054932 | 0.23804 | -0.1831 | -0.23804 | -0.064087 | -0.11902 | -0.027465 | -0.050354 | 0.17395 | 0.10986 | 0.068665 | -0.01831 | 0.09613 | 0.009155 | 0.35705 | 122.5296 | 0.13733 | 122.5571 | 122.493 | 122.3328 | 122.374 | 122.3053 | -122.4747 | -122.3831 | 122.4106 | 122.5296 | 62.1094 | 62.265
556.8906 | 122.5845 | -62.2101 | 60.1776 | 0.0025177 | -0.025906 | -0.026673 | 0.065225 | -0.025957 | -0.048031 | -0.040819 | -0.0082091 | -0.01904 | 0.057268 | 0.046903 | -0.21573 | -0.015351 | -0.024535 | -0.041199 | 60.2005 | -62.3291 | 60.1822 | -61.9858 | -62.4573 | -62.4207 | 0.054932 | 60.1364 | -62.233 | 60.2646 | -62.146 | -62.265 | -62.1964 | -0.11902 | 0.022888 | 0.004578 | 0.2243 | -0.21057 | -0.24719 | -0.091552 | -0.12817 | -0.022888 | -0.041198 | 0.086975 | 0.064087 | 0.013733 | -0.054932 | 0.036621 | -0.032044 | 0.34332 | 122.5113 | 0.086975 | 122.4976 | 122.5296 | 122.3694 | 122.4106 | 122.3465 | -122.5067 | -122.4106 | 122.3923 | 122.4747 | 62.1689 | 62.265
558.6562 | 122.612 | -62.178 | 60.2051 | 0.0025177 | -0.027615 | -0.025605 | 0.063303 | -0.028734 | -0.049313 | -0.037615 | -0.0051575 | -0.020322 | 0.054277 | 0.052671 | -0.21467 | -0.015778 | -0.020903 | -0.032043 | 60.2371 | -62.352 | 60.1639 | -62.0041 | -62.471 | -62.4435 | 0.064087 | 60.141 | -62.233 | 60.2692 | -62.1414 | -62.2604 | -62.1826 | -0.17395 | 0.032044 | -0.041199 | 0.17395 | -0.2655 | -0.29297 | -0.091552 | -0.11902 | -0.054931 | -0.064087 | 0.064087 | 0.036622 | -0.004577 | -0.082397 | 0.050354 | -0.027466 | 0.3479 | 122.5159 | 0.091553 | 122.5021 | 122.5891 | 122.374 | 122.4152 | 122.319 | -122.5571 | -122.438 | 122.3419 | 122.4472 | 62.146 | 62.2421
560.375 | 122.6349 | -62.1964 | 60.2005 | -0.0051118 | -0.028469 | -0.024964 | 0.062021 | -0.034075 | -0.050595 | -0.03911 | 0.00094606 | -0.023099 | 0.055132 | 0.050962 | -0.21659 | -0.016419 | -0.026244 | 0.009155 | 60.1639 | -62.3062 | 60.2188 | -61.9171 | -62.3932 | -62.3611 | 0.15564 | 60.0952 | -62.2238 | 60.2875 | -62.0728 | -62.178 | -62.1506 | -0.10986 | -0.036621 | 0.018311 | 0.27924 | -0.16479 | -0.19684 | -0.054932 | -0.086975 | -0.027466 | -0.10528 | 0.086976 | 0.1236 | 0.045776 | 0.01831 | 0.073242 | 0.045776 | 0.3891 | 122.525 | 0.15106 | 122.5113 | 122.4701 | 122.319 | 122.3602 | 122.2916 | -122.5067 | -122.4243 | 122.4152 | 122.4838 | 62.2055 | 62.352
562.1562 | 122.7036 | -62.2009 | 60.1868 | 0.010147 | -0.026547 | -0.026673 | 0.06138 | -0.033434 | -0.048458 | -0.041033 | -0.0021057 | -0.021817 | 0.056841 | 0.043058 | -0.21766 | -0.017914 | -0.02133 | -0.050354 | 60.1639 | -62.3154 | 60.228 | -61.8988 | -62.3795 | -62.3428 | 0.17395 | 60.0861 | -62.2147 | 60.3287 | -62.0361 | -62.1277 | -62.1185 | -0.11444 | -0.022889 | 0.041198 | 0.30212 | -0.14191 | -0.17853 | -0.027465 | -0.064087 | -0.013733 | -0.10071 | 0.14191 | 0.16479 | 0.082398 | 0.073242 | 0.096131 | 0.086975 | 0.41656 | 122.5433 | 0.17853 | 122.5433 | 122.4792 | 122.3007 | 122.3648 | 122.287 | -122.5021 | -122.4014 | 122.4289 | 122.5296 | 62.1506 | 62.3749
563.875 | 122.7036 | -62.178 | 60.1639 | -0.0051118 | -0.028897 | -0.025818 | 0.060526 | -0.03258 | -0.049099 | -0.037187 | -0.0021057 | -0.020536 | 0.056841 | 0.04498 | -0.21744 | -0.017487 | -0.026244 | -0.054932 | 60.1318 | -62.3016 | 60.2188 | -61.908 | -62.3795 | -62.352 | 0.16022 | 60.0861 | -62.2284 | 60.3149 | -62.0544 | -62.1597 | -62.1231 | -0.1236 | -0.032043 | 0.054932 | 0.27008 | -0.17395 | -0.20142 | -0.050354 | -0.07782 | -0.050354 | -0.077819 | 0.15106 | 0.1236 | 0.054932 | 0.018311 | 0.10529 | 0.068665 | 0.39368 | 122.5204 | 0.17395 | 122.5433 | 122.4335 | 122.3145 | 122.3099 | 122.2641 | -122.4655 | -122.3923 | 122.3969 | 122.493 | 62.1231 | 62.3383
565.6562 | 122.6944 | -62.1918 | 60.1639 | 0.0025177 | -0.027401 | -0.026459 | 0.06373 | -0.028521 | -0.04974 | -0.043169 | 0.00094606 | -0.02139 | 0.054705 | 0.040494 | -0.21595 | -0.016205 | -0.023039 | -0.032043 | 60.1364 | -62.3154 | 60.2325 | -61.8988 | -62.3795 | -62.3337 | 0.17395 | 60.0998 | -62.2421 | 60.3241 | -62.027 | -62.1368 | -62.1094 | -0.1236 | -0.027465 | 0.068665 | 0.29297 | -0.14191 | -0.18768 | -0.01831 | -0.064087 | -0.050354 | -0.064087 | 0.16022 | 0.16479 | 0.082397 | 0.054931 | 0.13275 | 0.10529 | 0.41656 | 122.5479 | 0.21515 | 122.5662 | 122.4518 | 122.3419 | 122.3282 | 122.2916 | -122.4792 | -122.406 | 122.4243 | 122.5159 | 62.1597 | 62.3657
567.3906 | 122.5571 | -62.2009 | 60.2188 | 0.0025177 | -0.026547 | -0.027527 | 0.064371 | -0.033648 | -0.049954 | -0.038256 | 0.00094606 | -0.019681 | 0.056841 | 0.056516 | -0.21616 | -0.015351 | -0.024962 | -0.050354 | 60.2234 | -62.3383 | 60.1318 | -62.0453 | -62.4939 | -62.4573 | 0.032043 | 60.173 | -62.233 | 60.2005 | -62.1735 | -62.2971 | -62.2101 | -0.13733 | 0.004578 | -0.086975 | 0.15564 | -0.25635 | -0.29297 | -0.11902 | -0.15564 | -0.032043 | -0.045776 | -0.018311 | 0.027466 | -0.009155 | -0.09613 | 0.022888 | -0.064087 | 0.29297 | 122.4701 | 0.059509 | 122.4335 | 122.5616 | 122.406 | 122.4243 | 122.374 | -122.5571 | -122.4518 | 122.3328 | 122.4014 | 62.1506 | 62.233
569.1562 | 122.5433 | -62.1918 | 60.2325 | -0.0051118 | -0.025692 | -0.0271 | 0.063516 | -0.027453 | -0.047817 | -0.04146 | -0.0021057 | -0.018613 | 0.055986 | 0.047117 | -0.21488 | -0.015778 | -0.021117 | -0.054932 | 60.2051 | -62.352 | 60.1135 | -62.0453 | -62.4939 | -62.471 | 0.009155 | 60.2005 | -62.2284 | 60.2234 | -62.178 | -62.3016 | -62.2101 | -0.16022 | -0.027466 | -0.11902 | 0.14648 | -0.27924 | -0.30212 | -0.11902 | -0.14191 | -0.036622 | -0.032044 | -0.009155 | 0.013732 | -0.018311 | -0.10986 | 0.018311 | -0.073242 | 0.3067 | 122.4655 | 0.050354 | 122.4518 | 122.5571 | 122.4289 | 122.3969 | 122.3923 | -122.5845 | -122.4609 | 122.3053 | 122.4152 | 62.1368 | 62.2009
570.9375 | 122.5342 | -62.2147 | 60.2325 | -0.0051118 | -0.024624 | -0.023469 | 0.065866 | -0.030443 | -0.047817 | -0.039537 | 0.00094606 | -0.02139 | 0.055773 | 0.050748 | -0.21637 | -0.014496 | -0.021971 | -0.14191 | 60.2097 | -62.3337 | 60.0815 | -62.1002 | -62.5717 | -62.5076 | -0.086975 | 60.1318 | -62.2696 | 60.2005 | -62.2238 | -62.3566 | -62.2421 | -0.11902 | -0.022888 | -0.15106 | 0.11444 | -0.29297 | -0.35706 | -0.17395 | -0.23804 | -0.054931 | -0.10071 | -0.032044 | -0.009155 | -0.027465 | -0.14191 | 0.027466 | -0.086975 | 0.23346 | 122.4152 | 0.045776 | 122.4701 | 122.5433 | 122.4014 | 122.4243 | 122.3465 | -122.5662 | -122.5021 | 122.2961 | 122.4152 | 62.0728 | 62.1277
572.6562 | 122.6807 | -62.1735 | 60.1501 | 0.0025177 | -0.029965 | -0.024537 | 0.061594 | -0.031511 | -0.051235 | -0.039537 | -0.0021057 | -0.022672 | 0.055773 | 0.046903 | -0.21616 | -0.016846 | -0.021758 | -0.091553 | 60.1593 | -62.3291 | 60.1959 | -61.9446 | -62.3978 | -62.352 | 0.11902 | 60.1089 | -62.233 | 60.3058 | -62.059 | -62.1643 | -62.1231 | -0.15564 | 0.009156 | 0.045777 | 0.22888 | -0.17853 | -0.2243 | -0.022888 | -0.068664 | -0.059509 | -0.041198 | 0.15564 | 0.11444 | 0.050354 | 0.009155 | 0.10986 | 0.068664 | 0.38452 | 122.525 | 0.17395 | 122.5388 | 122.4884 | 122.3419 | 122.3328 | 122.2824 | -122.4792 | -122.3831 | 122.3694 | 122.4792 | 62.0819 | 62.2925
574.3906 | 122.5067 | -62.2284 | 60.228 | 0.0025177 | -0.024624 | -0.023896 | 0.064798 | -0.030871 | -0.049099 | -0.04146 | 0.00094606 | -0.017545 | 0.054064 | 0.04733 | -0.21552 | -0.015992 | -0.02133 | -0.13733 | 60.2188 | -62.352 | 60.0998 | -62.1048 | -62.5534 | -62.5168 | -0.086975 | 60.1501 | -62.2787 | 60.1822 | -62.2513 | -62.384 | -62.2604 | -0.1236 | -0.009155 | -0.12817 | 0.1236 | -0.28839 | -0.32501 | -0.16479 | -0.20142 | -0.050354 | -0.07782 | -0.045776 | -0.022888 | -0.032043 | -0.15564 | 0.018311 | -0.10529 | 0.24719 | 122.4518 | 0.027466 | 122.4609 | 122.5708 | 122.4289 | 122.4472 | 122.3785 | -122.58 | -122.5067 | 122.3282 | 122.4106 | 62.0911 | 62.1414
576.1562 | 122.5616 | -62.1964 | 60.2371 | -0.0051118 | -0.028683 | -0.026673 | 0.065012 | -0.031298 | -0.050167 | -0.038896 | 0.00094606 | -0.020322 | 0.057268 | 0.044767 | -0.21595 | -0.015778 | -0.02368 | -0.068665 | 60.2234 | -62.3337 | 60.1089 | -62.059 | -62.4939 | -62.471 | 0.018311 | 60.1456 | -62.2192 | 60.2417 | -62.1506 | -62.2787 | -62.2009 | -0.13733 | -0.013733 | -0.12817 | 0.13733 | -0.27466 | -0.29755 | -0.13733 | -0.16022 | -0.022888 | -0.091553 | 0.004577 | 0.045776 | -0.004578 | -0.082398 | 0.01831 | -0.05951 | 0.27466 | 122.4426 | 0.068664 | 122.4609 | 122.5571 | 122.3648 | 122.4197 | 122.3419 | -122.5708 | -122.4564 | 122.3053 | 122.438 | 62.1277 | 62.2147
577.8594 | 122.6669 | -62.1872 | 60.1547 | -0.0051118 | -0.024197 | -0.026032 | 0.066721 | -0.028521 | -0.04739 | -0.038896 | -0.0051575 | -0.020322 | 0.054705 | 0.04199 | -0.21808 | -0.016633 | -0.02603 | -0.17853 | 60.1868 | -62.3062 | 60.1456 | -62.0132 | -62.4893 | -62.4481 | 0.004578 | 60.0952 | -62.2696 | 60.2966 | -62.1231 | -62.233 | -62.1323 | -0.11902 | 0.032044 | -0.009155 | 0.17395 | -0.26093 | -0.30212 | -0.14191 | -0.18311 | -0.082397 | -0.059509 | 0.14191 | 0.064087 | 0.054932 | -0.045776 | 0.13733 | 0.036621 | 0.29297 | 122.4518 | 0.14648 | 122.5662 | 122.493 | 122.3648 | 122.374 | 122.2824 | -122.4609 | -122.4243 | 122.3328 | 122.4838 | 62.0087 | 62.1918
579.625 | 122.6669 | -62.2147 | 60.2005 | 0.0025177 | -0.028897 | -0.027314 | 0.062235 | -0.031298 | -0.049526 | -0.042314 | 0.00094606 | -0.02139 | 0.056627 | 0.044126 | -0.21467 | -0.018769 | -0.025389 | -0.13275 | 60.1639 | -62.3428 | 60.1593 | -61.972 | -62.4298 | -62.4023 | 0.054932 | 60.1044 | -62.2238 | 60.2921 | -62.0956 | -62.178 | -62.146 | -0.12817 | -0.036621 | -0.041198 | 0.24262 | -0.18768 | -0.21515 | -0.05951 | -0.086976 | -0.009155 | -0.09613 | 0.091553 | 0.11902 | 0.068665 | 0.036621 | 0.07782 | 0.045776 | 0.37079 | 122.5021 | 0.12817 | 122.5159 | 122.5067 | 122.3282 | 122.3785 | 122.319 | -122.5433 | -122.4243 | 122.374 | 122.5067 | 62.0819 | 62.2696
581.4219 | 122.525 | -62.2284 | 60.2097 | -0.0051118 | -0.022915 | -0.021332 | 0.067362 | -0.026598 | -0.050167 | -0.039751 | -0.0082091 | -0.019681 | 0.057054 | 0.048612 | -0.21744 | -0.015992 | -0.023467 | -0.17395 | 60.2051 | -62.3474 | 60.0723 | -62.114 | -62.558 | -62.5031 | -0.091553 | 60.1593 | -62.2375 | 60.2097 | -62.2375 | -62.3749 | -62.233 | -0.11902 | -0.004578 | -0.13733 | 0.11444 | -0.27466 | -0.32959 | -0.15564 | -0.21057 | -0.009155 | -0.050354 | 0 | -0.009155 | -0.004577 | -0.14648 | 0.004578 | -0.13733 | 0.23346 | 122.4197 | 0 | 122.4472 | 122.5525 | 122.3969 | 122.4335 | 122.3877 | -122.5571 | -122.4472 | 122.3007 | 122.4381 | 62.0544 | 62.1368
583.2031 | 122.6669 | -62.1964 | 60.1318 | -0.0051118 | -0.02612 | -0.024537 | 0.064371 | -0.027453 | -0.050167 | -0.042528 | 0.00094606 | -0.02139 | 0.054705 | 0.04498 | -0.21573 | -0.016205 | -0.019408 | -0.13275 | 60.1181 | -62.3199 | 60.2051 | -61.9492 | -62.439 | -62.384 | 0.045776 | 60.0677 | -62.2513 | 60.2966 | -62.0865 | -62.2055 | -62.1231 | -0.1236 | -0.013733 | 0.073242 | 0.24719 | -0.18768 | -0.24262 | -0.064087 | -0.11902 | -0.054932 | -0.064087 | 0.16479 | 0.10986 | 0.073242 | -0.009155 | 0.12817 | 0.045777 | 0.37079 | 122.525 | 0.1648 | 122.5479 | 122.438 | 122.319 | 122.3145 | 122.2641 | -122.4518 | -122.3831 | 122.4014 | 122.493 | 62.0636 | 62.2421
584.9844 | 122.6624 | -62.1826 | 60.1639 | -0.0051118 | -0.027188 | -0.025605 | 0.061808 | -0.030657 | -0.048886 | -0.040392 | 0.00094606 | -0.020749 | 0.05385 | 0.041349 | -0.21787 | -0.015351 | -0.023467 | -0.022888 | 60.173 | -62.3199 | 60.228 | -61.8988 | -62.3703 | -62.3337 | 0.1831 | 60.1181 | -62.1964 | 60.3058 | -62.0544 | -62.1689 | -62.1277 | -0.13733 | 0.009156 | 0.064087 | 0.28381 | -0.15106 | -0.18768 | -0.013733 | -0.050354 | -0.013733 | -0.045776 | 0.14191 | 0.12817 | 0.054931 | 0.013733 | 0.068664 | 0.027466 | 0.42114 | 122.5479 | 0.14191 | 122.5021 | 122.493 | 122.3145 | 122.3557 | 122.3007 | -122.4838 | -122.3602 | 122.4106 | 122.4884 | 62.1597 | 62.3657
586.7031 | 122.5296 | -62.2101 | 60.2234 | 0.0025177 | -0.023556 | -0.023041 | 0.06373 | -0.033007 | -0.047817 | -0.042742 | 0.00094606 | -0.018827 | 0.057268 | 0.050107 | -0.21595 | -0.015137 | -0.025603 | -0.10986 | 60.228 | -62.3291 | 60.1044 | -62.0728 | -62.5351 | -62.4847 | -0.064087 | 60.173 | -62.233 | 60.2005 | -62.233 | -62.3657 | -62.2421 | -0.11902 | 0.004577 | -0.11902 | 0.13733 | -0.27466 | -0.32501 | -0.15564 | -0.20599 | -0.022888 | -0.050354 | -0.022889 | -0.022888 | -0.032043 | -0.15564 | -0.009155 | -0.13275 | 0.25635 | 122.4335 | 0 | 122.4335 | 122.5571 | 122.406 | 122.438 | 122.3831 | -122.5525 | -122.4564 | 122.3145 | 122.4106 | 62.1002 | 62.146
588.4375 | 122.5983 | -62.2238 | 60.2188 | -0.012741 | -0.025051 | -0.024537 | 0.066507 | -0.03023 | -0.048245 | -0.040605 | -0.0021057 | -0.020536 | 0.057695 | 0.049253 | -0.21573 | -0.014924 | -0.024321 | -0.050354 | 60.2142 | -62.3291 | 60.1639 | -61.9675 | -62.4527 | -62.4344 | 0.086975 | 60.1593 | -62.2467 | 60.2554 | -62.1368 | -62.2421 | -62.1689 | -0.10529 | -0.004578 | -0.054932 | 0.25635 | -0.21057 | -0.22888 | -0.10529 | -0.1236 | -0.022888 | -0.059509 | 0.036621 | 0.086975 | 0.054932 | -0.01831 | 0.07782 | 0.004578 | 0.36163 | 122.493 | 0.10986 | 122.5021 | 122.5433 | 122.406 | 122.438 | 122.3831 | -122.5479 | -122.4655 | 122.3877 | 122.4792 | 62.1735 | 62.3108
590.2031 | 122.5479 | -62.1964 | 60.2463 | -0.0051118 | -0.029965 | -0.024323 | 0.062662 | -0.030657 | -0.048886 | -0.042742 | -0.0021057 | -0.019467 | 0.057909 | 0.048398 | -0.21424 | -0.017273 | -0.022185 | -0.073242 | 60.2188 | -62.3154 | 60.1089 | -62.0407 | -62.4756 | -62.4527 | 0.018311 | 60.1822 | -62.2375 | 60.2051 | -62.1735 | -62.2879 | -62.2101 | -0.11902 | -0.027466 | -0.13733 | 0.15564 | -0.25635 | -0.27924 | -0.13733 | -0.16022 | -0.041199 | -0.064087 | -0.041199 | 0.022888 | -0.013733 | -0.091553 | 0.027466 | -0.050354 | 0.27466 | 122.4243 | 0.064087 | 122.4426 | 122.5342 | 122.4197 | 122.4152 | 122.3785 | -122.5616 | -122.4838 | 122.3053 | 122.4014 | 62.1231 | 62.2147
592 | 122.644 | -62.2055 | 60.1685 | 0.0025177 | -0.027401 | -0.022614 | 0.062235 | -0.03023 | -0.048031 | -0.039324 | -0.0021057 | -0.023313 | 0.054918 | 0.041776 | -0.21531 | -0.015565 | -0.022398 | -0.14648 | 60.1364 | -62.3291 | 60.1547 | -62.0041 | -62.4527 | -62.4115 | 0 | 60.0815 | -62.2742 | 60.2554 | -62.1368 | -62.2559 | -62.1826 | -0.1236 | -0.032043 | -0.013733 | 0.20142 | -0.20599 | -0.24719 | -0.082397 | -0.1236 | -0.068665 | -0.086975 | 0.086975 | 0.068664 | 0.022888 | -0.050354 | 0.091553 | 0.018311 | 0.32501 | 122.4838 | 0.13733 | 122.5296 | 122.4655 | 122.3557 | 122.3419 | 122.287 | -122.4976 | -122.4426 | 122.3602 | 122.4609 | 62.059 | 62.2055
593.7031 | 122.644 | -62.2055 | 60.1456 | -0.0051118 | -0.027829 | -0.02475 | 0.061167 | -0.030016 | -0.051022 | -0.039751 | -0.0051575 | -0.022031 | 0.054918 | 0.042417 | -0.2168 | -0.019196 | -0.025816 | -0.14191 | 60.1456 | -62.3199 | 60.1501 | -61.9904 | -62.4619 | -62.4023 | 0.041199 | 60.1135 | -62.2284 | 60.2692 | -62.1185 | -62.2009 | -62.1643 | -0.11444 | 0 | 0.004577 | 0.21515 | -0.19684 | -0.25635 | -0.082398 | -0.14191 | -0.022889 | -0.032044 | 0.1236 | 0.086975 | 0.041198 | 0.004577 | 0.064087 | 0.027466 | 0.32959 | 122.4701 | 0.10986 | 122.4976 | 122.4655 | 122.3419 | 122.3511 | 122.319 | -122.4655 | -122.374 | 122.3557 | 122.4747 | 62.0636 | 62.2467
595.4844 | 122.6349 | -62.178 | 60.1547 | -0.0051118 | -0.025692 | -0.026246 | 0.064157 | -0.031084 | -0.051022 | -0.041674 | -0.0021057 | -0.020963 | 0.0562 | 0.046049 | -0.21616 | -0.015565 | -0.020903 | -0.14191 | 60.1364 | -62.3383 | 60.1639 | -61.9675 | -62.4527 | -62.4207 | 0.045776 | 60.1181 | -62.2513 | 60.26 | -62.1414 | -62.2284 | -62.1735 | -0.16022 | -0.01831 | 0.009155 | 0.21057 | -0.24261 | -0.27466 | -0.082397 | -0.11444 | -0.073242 | -0.036621 | 0.10529 | 0.036622 | 0.004578 | -0.050354 | 0.07782 | 0.022888 | 0.37079 | 122.5021 | 0.10986 | 122.5113 | 122.4747 | 122.3694 | 122.3145 | 122.2961 | -122.493 | -122.406 | 122.3419 | 122.4381 | 62.0361 | 62.2238
597.25 | 122.5204 | -62.2009 | 60.2325 | 0.0025177 | -0.026333 | -0.026032 | 0.06373 | -0.034289 | -0.050595 | -0.039324 | -0.0021057 | -0.018186 | 0.057695 | 0.044767 | -0.21659 | -0.017914 | -0.022398 | -0.07782 | 60.228 | -62.3337 | 60.1318 | -62.0407 | -62.4802 | -62.4298 | 0.036621 | 60.1822 | -62.2467 | 60.2097 | -62.1735 | -62.2879 | -62.2284 | -0.13275 | -0.004578 | -0.10071 | 0.16022 | -0.22888 | -0.27924 | -0.096131 | -0.14649 | -0.045776 | -0.050354 | -0.022888 | 0.027466 | -0.027466 | -0.086975 | 0.01831 | -0.041199 | 0.29297 | 122.4655 | 0.073242 | 122.4564 | 122.5616 | 122.4289 | 122.4289 | 122.3831 | -122.5662 | -122.4792 | 122.3328 | 122.4106 | 62.1231 | 62.2375
599.8906 | 122.5342 | -62.178 | 60.2188 | 0.0025177 | -0.026547 | -0.025391 | 0.062448 | -0.03322 | -0.05209 | -0.038042 | -0.0021057 | -0.021604 | 0.055345 | 0.043272 | -0.21488 | -0.01706 | -0.026457 | -0.036621 | 60.1776 | -62.3383 | 60.1501 | -62.0041 | -62.4527 | -62.4252 | 0.045776 | 60.1776 | -62.2192 | 60.2188 | -62.1643 | -62.2696 | -62.2238 | -0.16022 | -0.041199 | -0.068665 | 0.17395 | -0.24719 | -0.27466 | -0.086975 | -0.11444 | -0.041198 | -0.041199 | 0 | 0.013733 | -0.045776 | -0.091552 | -0.004578 | -0.050354 | 0.33417 | 122.4884 | 0.054931 | 122.438 | 122.5159 | 122.3969 | 122.3557 | 122.3557 | -122.5571 | -122.438 | 122.3282 | 122.3969 | 62.1414 | 62.2238
602.0938 | 122.5296 | -62.2101 | 60.2051 | -0.012741 | -0.026547 | -0.026246 | 0.066721 | -0.030016 | -0.049099 | -0.038469 | -0.0051575 | -0.017331 | 0.0562 | 0.054166 | -0.21851 | -0.01471 | -0.020049 | -0.17853 | 60.1776 | -62.352 | 60.0677 | -62.1231 | -62.5717 | -62.5168 | -0.09613 | 60.1593 | -62.2879 | 60.2005 | -62.233 | -62.3749 | -62.233 | -0.14191 | -0.027466 | -0.13733 | 0.086975 | -0.3067 | -0.36163 | -0.16479 | -0.21973 | -0.07782 | -0.045776 | -0.004578 | -0.022888 | -0.022888 | -0.1648 | 0.054932 | -0.086975 | 0.22888 | 122.4197 | 0.054932 | 122.4884 | 122.5296 | 122.4472 | 122.3877 | 122.3694 | -122.5571 | -122.493 | 122.2778 | 122.4106 | 62.0316 | 62.114
604.4688 | 122.6624 | -62.1872 | 60.1364 | -0.0051118 | -0.025692 | -0.021546 | 0.062235 | -0.034502 | -0.048031 | -0.040819 | -0.0021057 | -0.019467 | 0.054491 | 0.048398 | -0.21509 | -0.016419 | -0.023467 | -0.15564 | 60.173 | -62.3291 | 60.1822 | -61.972 | -62.4435 | -62.384 | 0.041199 | 60.0815 | -62.2513 | 60.2966 | -62.1185 | -62.2238 | -62.1231 | -0.14191 | 0.036621 | 0.045776 | 0.21515 | -0.19684 | -0.25635 | -0.054931 | -0.11444 | -0.064087 | -0.054932 | 0.16022 | 0.068665 | 0.064087 | -0.036621 | 0.12817 | 0.027466 | 0.35706 | 122.5113 | 0.13275 | 122.5479 | 122.5021 | 122.3328 | 122.3602 | 122.2687 | -122.4655 | -122.3877 | 122.3694 | 122.4838 | 62.0316 | 62.2284
606.7656 | 122.612 | -62.1872 | 60.2097 | -0.0051118 | -0.03146 | -0.025177 | 0.061594 | -0.036852 | -0.04974 | -0.037615 | -0.0082091 | -0.022245 | 0.055132 | 0.045835 | -0.2168 | -0.017914 | -0.025816 | -0.027466 | 60.1639 | -62.3154 | 60.2325 | -61.9034 | -62.3657 | -62.3474 | 0.15564 | 60.1318 | -62.2375 | 60.2829 | -62.0865 | -62.1918 | -62.1506 | -0.12817 | -0.045777 | 0.022888 | 0.28381 | -0.16022 | -0.17853 | -0.032043 | -0.050354 | -0.050354 | -0.07782 | 0.073242 | 0.10071 | 0.036621 | -0.004577 | 0.086975 | 0.045777 | 0.41199 | 122.5479 | 0.15106 | 122.5204 | 122.4792 | 122.3694 | 122.3511 | 122.319 | -122.525 | -122.4472 | 122.4197 | 122.4701 | 62.1597 | 62.3428
608.8281 | 122.525 | -62.2055 | 60.2097 | -0.012741 | -0.023983 | -0.025391 | 0.065012 | -0.030871 | -0.04974 | -0.042314 | -0.0021057 | -0.018186 | 0.05855 | 0.050321 | -0.21808 | -0.014924 | -0.024748 | -0.14191 | 60.1959 | -62.3474 | 60.1044 | -62.0636 | -62.5397 | -62.4939 | -0.064087 | 60.1501 | -62.2421 | 60.1868 | -62.2147 | -62.3474 | -62.2421 | -0.14191 | -0.013733 | -0.10529 | 0.14191 | -0.28839 | -0.33417 | -0.14648 | -0.19226 | -0.036621 | -0.05951 | -0.022888 | -0.009156 | -0.036621 | -0.14191 | 0 | -0.10529 | 0.28381 | 122.4518 | 0.027465 | 122.4289 | 122.5433 | 122.3923 | 122.4014 | 122.3557 | -122.5571 | -122.4518 | 122.3099 | 122.3923 | 62.0636 | 62.1414
611.1406 | 122.6257 | -62.2101 | 60.1501 | 0.010147 | -0.025692 | -0.023041 | 0.061594 | -0.03258 | -0.048886 | -0.037187 | -0.0021057 | -0.021817 | 0.056627 | 0.041349 | -0.21381 | -0.017487 | -0.021544 | -0.15564 | 60.1364 | -62.3474 | 60.1547 | -61.9766 | -62.4619 | -62.4115 | 0.022888 | 60.0723 | -62.265 | 60.2554 | -62.1368 | -62.2284 | -62.1597 | -0.13733 | -0.013732 | 0.004578 | 0.23346 | -0.20142 | -0.25177 | -0.064087 | -0.11444 | -0.054932 | -0.077819 | 0.10529 | 0.073242 | 0.050354 | -0.018311 | 0.10529 | 0.036621 | 0.37079 | 122.5021 | 0.12817 | 122.5204 | 122.4838 | 122.3373 | 122.3465 | 122.2824 | -122.4976 | -122.4152 | 122.3648 | 122.4655 | 62.0544 | 62.233
612.9375 | 122.6761 | -62.1643 | 60.1776 | -0.0051118 | -0.026547 | -0.026673 | 0.061594 | -0.032152 | -0.048672 | -0.038683 | 0.00094606 | -0.020963 | 0.052996 | 0.043485 | -0.21659 | -0.018342 | -0.02368 | -0.10071 | 60.1364 | -62.3108 | 60.1776 | -61.9537 | -62.3932 | -62.3611 | 0.10986 | 60.1044 | -62.2238 | 60.2966 | -62.0544 | -62.1552 | -62.1231 | -0.14648 | -0.041198 | 0 | 0.21057 | -0.19684 | -0.22888 | -0.050354 | -0.082397 | -0.059509 | -0.073242 | 0.11902 | 0.10986 | 0.041199 | 0.009156 | 0.10071 | 0.068665 | 0.35706 | 122.4884 | 0.16937 | 122.5204 | 122.4472 | 122.3282 | 122.3007 | 122.2687 | -122.4884 | -122.4014 | 122.3419 | 122.4609 | 62.0636 | 62.2742
615.0625 | 122.5525 | -62.1826 | 60.2509 | -0.0051118 | -0.027188 | -0.026246 | 0.064157 | -0.031725 | -0.049313 | -0.038256 | -0.0051575 | -0.017972 | 0.055773 | 0.048826 | -0.21872 | -0.015778 | -0.023894 | -0.086975 | 60.2325 | -62.3291 | 60.1135 | -62.0453 | -62.4802 | -62.4481 | 0.036621 | 60.1685 | -62.233 | 60.2234 | -62.1643 | -62.265 | -62.2009 | -0.14648 | -0.01831 | -0.13733 | 0.13733 | -0.2655 | -0.29755 | -0.11902 | -0.15106 | -0.050354 | -0.082397 | -0.027465 | 0.01831 | -0.018311 | -0.082398 | 0.032043 | -0.032044 | 0.28381 | 122.4426 | 0.068664 | 122.4564 | 122.5616 | 122.4014 | 122.4152 | 122.3511 | -122.58 | -122.4838 | 122.2961 | 122.406 | 62.0956 | 62.2192
618.0625 | 122.5754 | -62.1964 | 60.2234 | -0.0051118 | -0.026547 | -0.025605 | 0.065866 | -0.033648 | -0.047817 | -0.039751 | 0.00094606 | -0.020749 | 0.0562 | 0.045408 | -0.21573 | -0.016205 | -0.020476 | -0.086975 | 60.2051 | -62.3383 | 60.1181 | -62.0453 | -62.471 | -62.4481 | 0.032043 | 60.1639 | -62.233 | 60.2325 | -62.1414 | -62.2513 | -62.2009 | -0.14191 | -0.018311 | -0.10529 | 0.15106 | -0.25177 | -0.27466 | -0.10986 | -0.13275 | -0.036621 | -0.05951 | 0.009155 | 0.054932 | -0.004578 | -0.054932 | 0.032043 | -0.018311 | 0.29297 | 122.4564 | 0.091553 | 122.4655 | 122.5433 | 122.3969 | 122.4014 | 122.3602 | -122.5616 | -122.4564 | 122.3145 | 122.4289 | 62.1094 | 62.2284
620.125 | 122.5021 | -62.2147 | 60.1868 | -0.0051118 | -0.021206 | -0.021546 | 0.06608 | -0.034502 | -0.048031 | -0.039537 | -0.0021057 | -0.017545 | 0.05855 | 0.048612 | -0.21808 | -0.013642 | -0.022826 | -0.16937 | 60.2142 | -62.3428 | 60.0815 | -62.0956 | -62.5488 | -62.4939 | -0.10071 | 60.1456 | -62.2696 | 60.1776 | -62.233 | -62.3566 | -62.2513 | -0.12817 | 0.027465 | -0.10529 | 0.11902 | -0.27923 | -0.33417 | -0.15106 | -0.20599 | -0.054931 | -0.041199 | -0.009156 | -0.01831 | -0.036621 | -0.14191 | 0.01831 | -0.086975 | 0.24719 | 122.4243 | 0.036621 | 122.4472 | 122.5571 | 122.4152 | 122.4289 | 122.3602 | -122.5296 | -122.4564 | 122.2961 | 122.3923 | 62.0453 | 62.114
622.1094 | 122.6028 | -62.1964 | 60.1913 | -0.0051118 | -0.02676 | -0.023469 | 0.063303 | -0.031084 | -0.049526 | -0.039751 | -0.0021057 | -0.023313 | 0.056841 | 0.043485 | -0.21595 | -0.017701 | -0.017271 | -0.041199 | 60.1822 | -62.265 | 60.2142 | -61.9125 | -62.3703 | -62.352 | 0.15106 | 60.1181 | -62.2101 | 60.2692 | -62.0819 | -62.1964 | -62.1414 | -0.068665 | -0.009155 | 0.022888 | 0.28381 | -0.15564 | -0.17395 | -0.086975 | -0.10529 | -0.013733 | -0.073242 | 0.07782 | 0.11444 | 0.054932 | 0 | 0.068665 | 0.013733 | 0.35248 | 122.4792 | 0.12817 | 122.4792 | 122.4472 | 122.3282 | 122.3785 | 122.3145 | -122.4564 | -122.4014 | 122.4106 | 122.4655 | 62.1552 | 62.3474
624.1406 | 122.6028 | -62.2147 | 60.1547 | 0.0025177 | -0.025479 | -0.02475 | 0.06138 | -0.03322 | -0.047177 | -0.039965 | 0.00094606 | -0.019681 | 0.0562 | 0.041563 | -0.21573 | -0.01706 | -0.021971 | -0.17853 | 60.1593 | -62.3245 | 60.1501 | -61.972 | -62.4619 | -62.4023 | 0.004578 | 60.0906 | -62.233 | 60.2417 | -62.1368 | -62.2375 | -62.1689 | -0.10986 | 0.004578 | -0.004578 | 0.24262 | -0.18768 | -0.24719 | -0.07782 | -0.13733 | -0.01831 | -0.064087 | 0.086975 | 0.07782 | 0.045777 | -0.022888 | 0.064087 | -0.004578 | 0.35248 | 122.4747 | 0.09613 | 122.4747 | 122.4838 | 122.3236 | 122.374 | 122.3053 | -122.4792 | -122.3877 | 122.3648 | 122.4564 | 62.0361 | 62.2192
626.3594 | 122.5342 | -62.2055 | 60.2325 | -0.012741 | -0.023129 | -0.024109 | 0.068003 | -0.031298 | -0.047817 | -0.041033 | -0.0051575 | -0.019895 | 0.055986 | 0.048826 | -0.21595 | -0.015137 | -0.018126 | -0.15564 | 60.1913 | -62.3337 | 60.1044 | -62.0865 | -62.5214 | -62.4939 | -0.068665 | 60.1501 | -62.2513 | 60.1868 | -62.233 | -62.3474 | -62.2238 | -0.12817 | -0.041199 | -0.12817 | 0.11902 | -0.28839 | -0.31586 | -0.16022 | -0.18768 | -0.045777 | -0.082398 | -0.045776 | -0.027466 | -0.018311 | -0.14191 | 0.027466 | -0.09613 | 0.24719 | 122.438 | 0.018311 | 122.4381 | 122.525 | 122.4014 | 122.3969 | 122.3557 | -122.5662 | -122.4838 | 122.3099 | 122.3923 | 62.0499 | 62.1368
628.2812 | 122.644 | -62.2009 | 60.1547 | -0.0051118 | -0.027829 | -0.02475 | 0.064585 | -0.029162 | -0.050381 | -0.037615 | -0.0021057 | -0.020536 | 0.0562 | 0.041135 | -0.21702 | -0.015137 | -0.020903 | -0.20599 | 60.141 | -62.3657 | 60.1776 | -61.9675 | -62.439 | -62.4115 | 0.018311 | 60.0815 | -62.2604 | 60.2966 | -62.114 | -62.2192 | -62.1231 | -0.1648 | -0.013733 | 0.022888 | 0.23346 | -0.21057 | -0.23804 | -0.045776 | -0.073242 | -0.059509 | -0.073242 | 0.14191 | 0.086975 | 0.07782 | -0.01831 | 0.13733 | 0.041199 | 0.39826 | 122.5433 | 0.14648 | 122.5571 | 122.5067 | 122.3419 | 122.3419 | 122.2824 | -122.5204 | -122.4152 | 122.3785 | 122.4976 | 61.9949 | 62.2192
630 | 122.644 | -62.1872 | 60.1273 | 0.0025177 | -0.023556 | -0.024109 | 0.06373 | -0.02788 | -0.047817 | -0.040392 | -0.0021057 | -0.02139 | 0.054918 | 0.045408 | -0.21424 | -0.015992 | -0.025603 | -0.16937 | 60.1547 | -62.3383 | 60.1913 | -61.9492 | -62.4298 | -62.3932 | 0.041199 | 60.0906 | -62.2421 | 60.3195 | -62.0911 | -62.2009 | -62.1185 | -0.15106 | 0.027466 | 0.064087 | 0.23804 | -0.20599 | -0.24262 | -0.054931 | -0.091553 | -0.054931 | -0.036621 | 0.19226 | 0.096131 | 0.068665 | -0.013733 | 0.1236 | 0.041198 | 0.3891 | 122.5296 | 0.15106 | 122.5616 | 122.493 | 122.3328 | 122.3419 | 122.2778 | -122.4655 | -122.3694 | 122.3785 | 122.5067 | 62.0178 | 62.2284
631.7812 | 122.6395 | -62.178 | 60.1822 | 0.0025177 | -0.028683 | -0.024964 | 0.060953 | -0.034075 | -0.052304 | -0.037828 | 0.00094606 | -0.022245 | 0.054277 | 0.047117 | -0.21424 | -0.015992 | -0.022398 | -0.17853 | 60.173 | -62.3154 | 60.1639 | -61.9766 | -62.4298 | -62.4069 | 0.036621 | 60.0906 | -62.2467 | 60.2783 | -62.1048 | -62.1964 | -62.1368 | -0.13733 | -0.009155 | -0.018311 | 0.20142 | -0.22888 | -0.25177 | -0.091552 | -0.11444 | -0.068664 | -0.091553 | 0.09613 | 0.073243 | 0.041199 | -0.01831 | 0.10986 | 0.050354 | 0.33874 | 122.4792 | 0.14191 | 122.525 | 122.4884 | 122.3373 | 122.3511 | 122.2687 | -122.4976 | -122.4289 | 122.3419 | 122.4564 | 61.9995 | 62.2147
633.5156 | 122.5891 | -62.1918 | 60.2097 | -0.0051118 | -0.026333 | -0.026032 | 0.063303 | -0.029162 | -0.050808 | -0.039751 | -0.0021057 | -0.020108 | 0.0562 | 0.047544 | -0.21595 | -0.016633 | -0.026457 | -0.082397 | 60.2005 | -62.3199 | 60.1685 | -61.9766 | -62.4527 | -62.4161 | 0.082397 | 60.1639 | -62.2192 | 60.2646 | -62.1094 | -62.2375 | -62.1597 | -0.12817 | -0.009156 | -0.041199 | 0.21515 | -0.22431 | -0.26093 | -0.096131 | -0.13275 | -0.027466 | -0.045777 | 0.054931 | 0.082397 | 0.032043 | -0.045777 | 0.059509 | -0.018311 | 0.34332 | 122.4884 | 0.10986 | 122.4838 | 122.5204 | 122.3831 | 122.3923 | 122.3557 | -122.5296 | -122.4289 | 122.3602 | 122.4564 | 62.1094 | 62.2742
635.2812 | 122.5342 | -62.2101 | 60.2371 | 0.0025177 | -0.026974 | -0.027527 | 0.063516 | -0.032366 | -0.050167 | -0.041033 | -0.0051575 | -0.021176 | 0.055132 | 0.042844 | -0.21702 | -0.017273 | -0.017912 | -0.13275 | 60.2142 | -62.3428 | 60.1227 | -62.0407 | -62.4664 | -62.439 | 0.032043 | 60.1822 | -62.2375 | 60.2188 | -62.1689 | -62.2833 | -62.2009 | -0.13275 | -0.022889 | -0.11444 | 0.16937 | -0.22888 | -0.25635 | -0.096131 | -0.1236 | -0.027466 | -0.054932 | -0.018311 | 0.041199 | 0.009155 | -0.073242 | 0.036621 | -0.045776 | 0.30212 | 122.4655 | 0.068665 | 122.4564 | 122.5571 | 122.4197 | 122.4243 | 122.3923 | -122.58 | -122.4747 | 122.3328 | 122.4289 | 62.0773 | 62.2421
637.0469 | 122.5891 | -62.2009 | 60.2051 | 0.0025177 | -0.025051 | -0.024964 | 0.065012 | -0.029375 | -0.050167 | -0.038896 | 0.00094606 | -0.018613 | 0.055559 | 0.049467 | -0.21702 | -0.017701 | -0.020476 | -0.10071 | 60.2188 | -62.3062 | 60.173 | -61.9904 | -62.439 | -62.3978 | 0.091553 | 60.1776 | -62.2513 | 60.2692 | -62.1231 | -62.2513 | -62.1689 | -0.10529 | 0.013733 | -0.032043 | 0.21057 | -0.19684 | -0.23804 | -0.091553 | -0.13275 | -0.050354 | -0.027466 | 0.064087 | 0.07782 | 0.032044 | -0.050354 | 0.082398 | 0 | 0.31586 | 122.4792 | 0.12817 | 122.5204 | 122.525 | 122.4289 | 122.4197 | 122.3785 | -122.5113 | -122.4564 | 122.374 | 122.4701 | 62.1002 | 62.2925
638.7656 | 122.6761 | -62.2055 | 60.1547 | -0.0051118 | -0.02377 | -0.024964 | 0.061594 | -0.029802 | -0.049526 | -0.038042 | 0.00094606 | -0.021604 | 0.055132 | 0.041776 | -0.2168 | -0.015351 | -0.020476 | -0.17853 | 60.1318 | -62.3016 | 60.2005 | -61.9583 | -62.439 | -62.3932 | 0.054932 | 60.0723 | -62.2559 | 60.2966 | -62.0865 | -62.1918 | -62.1094 | -0.096131 | -0.022888 | 0.045776 | 0.24719 | -0.18768 | -0.23346 | -0.091552 | -0.13733 | -0.050354 | -0.082397 | 0.14191 | 0.11902 | 0.09613 | 0.013733 | 0.14648 | 0.064087 | 0.34332 | 122.5021 | 0.16937 | 122.5525 | 122.4335 | 122.3282 | 122.3373 | 122.2778 | -122.4564 | -122.4106 | 122.406 | 122.5021 | 62.027 | 62.2604
640.5625 | 122.5342 | -62.1964 | 60.2051 | 0.010147 | -0.02377 | -0.023469 | 0.063516 | -0.028734 | -0.048458 | -0.039751 | -0.0021057 | -0.018186 | 0.055559 | 0.052244 | -0.21616 | -0.016419 | -0.024962 | -0.16022 | 60.228 | -62.3383 | 60.1227 | -62.0224 | -62.4985 | -62.4619 | -0.004578 | 60.1456 | -62.2421 | 60.2097 | -62.2009 | -62.3337 | -62.2238 | -0.14191 | 0.022888 | -0.082397 | 0.17395 | -0.2655 | -0.30212 | -0.1236 | -0.16022 | -0.045776 | -0.059509 | 0.004578 | -0.004578 | -0.027466 | -0.13733 | 0.01831 | -0.091553 | 0.31586 | 122.4609 | 0.041198 | 122.4518 | 122.5662 | 122.3877 | 122.4243 | 122.3419 | -122.5433 | -122.4472 | 122.319 | 122.406 | 62.0361 | 62.1918
642.2812 | 122.612 | -62.2055 | 60.1593 | 0.0025177 | -0.027188 | -0.026246 | 0.061167 | -0.030443 | -0.048886 | -0.040819 | 0.00094606 | -0.022245 | 0.055559 | 0.045408 | -0.21509 | -0.017701 | -0.022612 | -0.22888 | 60.1501 | -62.3611 | 60.1273 | -61.9995 | -62.4527 | -62.4207 | -0.009155 | 60.0906 | -62.2467 | 60.2463 | -62.1414 | -62.2421 | -62.1735 | -0.15564 | -0.009156 | -0.032044 | 0.20599 | -0.21515 | -0.24719 | -0.059509 | -0.091553 | -0.041199 | -0.068665 | 0.086975 | 0.064087 | 0.032043 | -0.036621 | 0.073242 | 0.004578 | 0.36163 | 122.4884 | 0.10529 | 122.493 | 122.5113 | 122.3373 | 122.3557 | 122.2961 | -122.5204 | -122.406 | 122.3328 | 122.4518 | 61.9766 | 62.1964
644.2812 | 122.5662 | -62.178 | 60.2142 | -0.0051118 | -0.025051 | -0.027955 | 0.063303 | -0.03322 | -0.048672 | -0.040605 | 0.00094606 | -0.019254 | 0.056841 | 0.04968 | -0.21787 | -0.015565 | -0.021117 | -0.11902 | 60.2142 | -62.3245 | 60.1593 | -61.972 | -62.439 | -62.4115 | 0.068665 | 60.1593 | -62.2238 | 60.2737 | -62.1277 | -62.2559 | -62.1552 | -0.14648 | 0 | -0.054931 | 0.20599 | -0.23346 | -0.26093 | -0.086975 | -0.11444 | -0.045776 | -0.054931 | 0.05951 | 0.050354 | 0.022889 | -0.077819 | 0.068665 | -0.032043 | 0.35248 | 122.4838 | 0.09613 | 122.4976 | 122.5388 | 122.3831 | 122.3923 | 122.3373 | -122.5388 | -122.438 | 122.3373 | 122.4518 | 62.059 | 62.2467
646.25 | 122.6212 | -62.1826 | 60.1318 | -0.0051118 | -0.026547 | -0.024323 | 0.06138 | -0.032152 | -0.04739 | -0.039324 | 0.00094606 | -0.02139 | 0.056414 | 0.050107 | -0.21552 | -0.015778 | -0.022612 | -0.20142 | 60.1318 | -62.3154 | 60.1959 | -61.9308 | -62.4161 | -62.3657 | 0.059509 | 60.0723 | -62.2375 | 60.2737 | -62.1094 | -62.2101 | -62.1231 | -0.13275 | 0 | 0.064087 | 0.25177 | -0.18311 | -0.23346 | -0.050354 | -0.10071 | -0.054932 | -0.059509 | 0.14191 | 0.073242 | 0.059509 | -0.027466 | 0.11444 | 0.027466 | 0.38452 | 122.5113 | 0.12817 | 122.5113 | 122.4472 | 122.3099 | 122.3145 | 122.2549 | -122.4472 | -122.3694 | 122.3785 | 122.4564 | 61.9812 | 62.2421
648.4844 | 122.6257 | -62.2055 | 60.1273 | -0.0051118 | -0.027188 | -0.023682 | 0.061808 | -0.03023 | -0.050808 | -0.040178 | -0.0021057 | -0.022672 | 0.054491 | 0.049467 | -0.2168 | -0.016633 | -0.022185 | -0.23346 | 60.1318 | -62.3016 | 60.1501 | -61.9492 | -62.4573 | -62.4023 | 0.041199 | 60.0815 | -62.2467 | 60.2554 | -62.1231 | -62.2192 | -62.1506 | -0.096131 | 0.004578 | 0.022888 | 0.25635 | -0.19684 | -0.25177 | -0.10071 | -0.15564 | -0.041199 | -0.045776 | 0.12817 | 0.082397 | 0.054931 | -0.013733 | 0.09613 | 0.027466 | 0.35248 | 122.4518 | 0.1236 | 122.5021 | 122.4335 | 122.3282 | 122.3373 | 122.287 | -122.4289 | -122.374 | 122.3557 | 122.4609 | 61.972 | 62.2467
650.6875 | 122.5891 | -62.2101 | 60.1639 | 0.0025177 | -0.026333 | -0.024537 | 0.06608 | -0.033434 | -0.050595 | -0.039751 | 0.0039979 | -0.017545 | 0.055345 | 0.053098 | -0.21702 | -0.015137 | -0.025816 | -0.27466 | 60.1913 | -62.3428 | 60.0815 | -62.0682 | -62.5534 | -62.4847 | -0.07782 | 60.1273 | -62.2467 | 60.2097 | -62.1918 | -62.3062 | -62.1964 | -0.13275 | 0.027466 | -0.082397 | 0.14191 | -0.27466 | -0.34332 | -0.14191 | -0.21057 | -0.036621 | -0.036621 | 0.045777 | 0.018311 | 0.013733 | -0.09613 | 0.050354 | -0.059509 | 0.27466 | 122.4243 | 0.054932 | 122.4564 | 122.5342 | 122.374 | 122.4014 | 122.3373 | -122.5067 | -122.4106 | 122.2916 | 122.4197 | 61.9354 | 62.1323
652.9531 | 122.6532 | -62.146 | 60.173 | -0.012741 | -0.031033 | -0.025391 | 0.060312 | -0.031511 | -0.050595 | -0.041033 | -0.0021057 | -0.022245 | 0.054705 | 0.040494 | -0.2168 | -0.018769 | -0.023894 | -0.21515 | 60.1318 | -62.3428 | 60.1593 | -61.972 | -62.4252 | -62.384 | 0.045776 | 60.0906 | -62.233 | 60.2646 | -62.0956 | -62.178 | -62.1323 | -0.19684 | -0.041199 | -0.013733 | 0.17395 | -0.23804 | -0.27924 | -0.041199 | -0.082398 | -0.086975 | -0.082398 | 0.091552 | 0.050354 | 0.013733 | -0.032044 | 0.10071 | 0.054931 | 0.37079 | 122.5021 | 0.13733 | 122.4976 | 122.4747 | 122.3236 | 122.2778 | 122.2366 | -122.5159 | -122.406 | 122.3053 | 122.4106 | 61.9308 | 62.1918
655.4688 | 122.5388 | -62.2055 | 60.2371 | 0.0025177 | -0.028469 | -0.027527 | 0.064585 | -0.03322 | -0.050381 | -0.038256 | -0.0021057 | -0.020108 | 0.054491 | 0.04434 | -0.2183 | -0.016846 | -0.022398 | -0.15106 | 60.2188 | -62.3108 | 60.1273 | -62.0178 | -62.4802 | -62.4344 | 0.045776 | 60.1822 | -62.2238 | 60.1959 | -62.1689 | -62.2833 | -62.2238 | -0.10529 | -0.018311 | -0.10986 | 0.18768 | -0.22888 | -0.27466 | -0.1236 | -0.16937 | -0.018311 | -0.054932 | -0.041199 | 0.036621 | -0.018311 | -0.07782 | 0 | -0.059509 | 0.29297 | 122.438 | 0.054932 | 122.4197 | 122.5296 | 122.406 | 122.4243 | 122.3877 | -122.5479 | -122.4609 | 122.3328 | 122.4014 | 62.0544 | 62.2513
657.3906 | 122.5525 | -62.2055 | 60.2554 | 0.0025177 | -0.026547 | -0.026459 | 0.063516 | -0.028734 | -0.048245 | -0.040819 | 0.0039979 | -0.017118 | 0.055559 | 0.051176 | -0.21744 | -0.017701 | -0.023894 | -0.14648 | 60.2463 | -62.2971 | 60.0952 | -62.0361 | -62.4756 | -62.4344 | 0.032043 | 60.1822 | -62.2101 | 60.2097 | -62.146 | -62.2604 | -62.1918 | -0.091553 | -0.009155 | -0.16022 | 0.16937 | -0.22888 | -0.27008 | -0.13733 | -0.17853 | -0.004578 | -0.073242 | -0.045776 | 0.059509 | 0.013733 | -0.054932 | 0.018311 | -0.050354 | 0.26093 | 122.3923 | 0.064087 | 122.4197 | 122.5433 | 122.3923 | 122.4518 | 122.3877 | -122.5525 | -122.4655 | 122.3007 | 122.4152 | 62.059 | 62.2375
659.4062 | 122.5525 | -62.2101 | 60.2142 | 0.0025177 | -0.029324 | -0.025605 | 0.062876 | -0.030657 | -0.051449 | -0.039324 | 0.00094606 | -0.020322 | 0.056627 | 0.045408 | -0.21467 | -0.016419 | -0.023467 | -0.10071 | 60.1822 | -62.2925 | 60.1685 | -61.972 | -62.4023 | -62.3932 | 0.091553 | 60.141 | -62.2055 | 60.2325 | -62.1506 | -62.2421 | -62.2101 | -0.082397 | -0.032043 | -0.045776 | 0.23804 | -0.18311 | -0.19226 | -0.10071 | -0.10986 | 0.004578 | -0.073242 | 0.018311 | 0.059509 | 0 | -0.032043 | -0.004578 | -0.036621 | 0.32043 | 122.4609 | 0.054931 | 122.438 | 122.4747 | 122.3465 | 122.3923 | 122.3511 | -122.5067 | -122.4197 | 122.3785 | 122.4426 | 62.1094 | 62.3016
661.3438 | 122.6624 | -62.1918 | 60.1456 | -0.0051118 | -0.024838 | -0.025605 | 0.065439 | -0.030871 | -0.048458 | -0.040819 | -0.0021057 | -0.020749 | 0.053636 | 0.04733 | -0.21787 | -0.016846 | -0.022398 | -0.26093 | 60.1639 | -62.352 | 60.1593 | -61.9858 | -62.4664 | -62.4115 | 0.013733 | 60.0861 | -62.2375 | 60.2875 | -62.0911 | -62.2192 | -62.114 | -0.16022 | 0.01831 | 0.013733 | 0.20599 | -0.21973 | -0.27466 | -0.059509 | -0.11444 | -0.045777 | -0.059509 | 0.14191 | 0.10071 | 0.077819 | -0.027466 | 0.1236 | 0.018311 | 0.36621 | 122.5113 | 0.14648 | 122.525 | 122.5159 | 122.3236 | 122.3557 | 122.2778 | -122.4976 | -122.3831 | 122.3511 | 122.4792 | 61.9308 | 62.2055
663.2188 | 122.6807 | -62.1872 | 60.1593 | -0.012741 | -0.028042 | -0.025605 | 0.062662 | -0.034289 | -0.049099 | -0.041887 | 0.00094606 | -0.021604 | 0.056414 | 0.04498 | -0.21766 | -0.016846 | -0.024321 | -0.1831 | 60.1501 | -62.3199 | 60.1868 | -61.9125 | -62.3978 | -62.3337 | 0.11444 | 60.1181 | -62.2147 | 60.3058 | -62.0453 | -62.146 | -62.1277 | -0.13275 | -0.009156 | 0.027466 | 0.27466 | -0.14648 | -0.21057 | -0.013733 | -0.07782 | -0.027466 | -0.041199 | 0.14648 | 0.14191 | 0.059509 | 0.041199 | 0.086975 | 0.068665 | 0.40741 | 122.5067 | 0.16937 | 122.5204 | 122.4701 | 122.3328 | 122.3373 | 122.3053 | -122.4792 | -122.374 | 122.374 | 122.493 | 62.0041 | 62.3016
664.9375 | 122.612 | -62.1689 | 60.1959 | -0.0051118 | -0.025051 | -0.024323 | 0.062235 | -0.034289 | -0.049526 | -0.042101 | 0.00094606 | -0.02139 | 0.057268 | 0.048826 | -0.21595 | -0.016205 | -0.019194 | -0.10071 | 60.173 | -62.2879 | 60.228 | -61.908 | -62.3657 | -62.3337 | 0.15106 | 60.1181 | -62.2055 | 60.2966 | -62.0636 | -62.1552 | -62.1231 | -0.11902 | -0.022888 | 0.032043 | 0.26093 | -0.16479 | -0.19684 | -0.045776 | -0.07782 | -0.036621 | -0.07782 | 0.10071 | 0.10528 | 0.045776 | 0.013733 | 0.082397 | 0.050354 | 0.37994 | 122.5159 | 0.14191 | 122.5021 | 122.4609 | 122.3236 | 122.3419 | 122.287 | -122.4838 | -122.4014 | 122.3969 | 122.4655 | 62.0682 | 62.3199
666.7188 | 122.58 | -62.1689 | 60.2325 | -0.0051118 | -0.027615 | -0.025177 | 0.063303 | -0.03322 | -0.052517 | -0.042528 | -0.0021057 | -0.019467 | 0.055773 | 0.046903 | -0.21637 | -0.016633 | -0.025389 | -0.11902 | 60.1547 | -62.3199 | 60.2097 | -61.94 | -62.3932 | -62.3749 | 0.13733 | 60.1593 | -62.2101 | 60.2417 | -62.1094 | -62.2192 | -62.1689 | -0.15106 | -0.07782 | -0.022888 | 0.22888 | -0.20599 | -0.2243 | -0.054932 | -0.073242 | -0.041199 | -0.073242 | 0.009155 | 0.059509 | 0 | -0.050354 | 0.041199 | -0.009155 | 0.37994 | 122.5296 | 0.10071 | 122.4518 | 122.4747 | 122.3694 | 122.3236 | 122.3282 | -122.5525 | -122.4426 | 122.3785 | 122.4106 | 62.0499 | 62.3062
668.5625 | 122.5342 | -62.1918 | 60.2463 | -0.0051118 | -0.027615 | -0.025818 | 0.063303 | -0.033648 | -0.049954 | -0.041246 | -0.0051575 | -0.021604 | 0.054918 | 0.047117 | -0.21702 | -0.018128 | -0.024535 | -0.12817 | 60.1822 | -62.2971 | 60.1501 | -61.9766 | -62.4207 | -62.3932 | 0.073242 | 60.1776 | -62.2147 | 60.2325 | -62.1506 | -62.2559 | -62.1918 | -0.10529 | -0.064087 | -0.096131 | 0.21515 | -0.20142 | -0.22888 | -0.09613 | -0.1236 | -0.022889 | -0.068665 | -0.013733 | 0.041198 | 0 | -0.064087 | 0.022889 | -0.041198 | 0.32043 | 122.4472 | 0.064087 | 122.4472 | 122.4792 | 122.3923 | 122.374 | 122.3694 | -122.5433 | -122.4609 | 122.3419 | 122.4243 | 62.0636 | 62.265
671.3906 | 122.5204 | -62.178 | 60.228 | 0.0025177 | -0.027188 | -0.026032 | 0.063303 | -0.028307 | -0.048245 | -0.039751 | -0.0021057 | -0.020963 | 0.057909 | 0.046262 | -0.21637 | -0.017487 | -0.021758 | -0.14191 | 60.1822 | -62.3062 | 60.1318 | -61.9812 | -62.4481 | -62.3978 | 0.07782 | 60.1501 | -62.2192 | 60.2234 | -62.146 | -62.2559 | -62.1964 | -0.12817 | -0.045776 | -0.09613 | 0.19684 | -0.21973 | -0.27008 | -0.091553 | -0.14191 | -0.041198 | -0.07782 | -0.004577 | 0.032044 | -0.01831 | -0.077819 | 0.022888 | -0.036621 | 0.32501 | 122.438 | 0.073242 | 122.4426 | 122.4884 | 122.3694 | 122.3602 | 122.3282 | -122.5342 | -122.4472 | 122.3099 | 122.4014 | 62.0361 | 62.2559
673.75 | 122.6578 | -62.1552 | 60.1776 | 0.010147 | -0.027829 | -0.026673 | 0.063944 | -0.03557 | -0.050808 | -0.040178 | -0.0021057 | -0.019467 | 0.055559 | 0.045835 | -0.21659 | -0.015992 | -0.023467 | -0.16479 | 60.1318 | -62.2879 | 60.228 | -61.8576 | -62.3245 | -62.2971 | 0.15564 | 60.1044 | -62.2055 | 60.3058 | -62.027 | -62.1323 | -62.1002 | -0.13275 | -0.045776 | 0.050354 | 0.29755 | -0.14191 | -0.16937 | -0.009155 | -0.036621 | -0.050354 | -0.073242 | 0.12817 | 0.12817 | 0.054931 | 0.022888 | 0.10529 | 0.073242 | 0.4303 | 122.5159 | 0.17853 | 122.5113 | 122.4197 | 122.3099 | 122.287 | 122.2595 | -122.4655 | -122.3831 | 122.3831 | 122.4609 | 61.9904 | 62.3108
675.6719 | 122.6669 | -62.1735 | 60.173 | -0.0051118 | -0.026974 | -0.027741 | 0.063944 | -0.032152 | -0.049313 | -0.040178 | 0.0039979 | -0.020749 | 0.054491 | 0.046262 | -0.21787 | -0.015137 | -0.025176 | -0.17853 | 60.1456 | -62.3016 | 60.228 | -61.8713 | -62.3337 | -62.3154 | 0.17853 | 60.0769 | -62.2147 | 60.3104 | -62.0316 | -62.1414 | -62.0956 | -0.12817 | -0.027466 | 0.054931 | 0.30212 | -0.14191 | -0.16022 | -0.013733 | -0.032043 | -0.041199 | -0.096131 | 0.13733 | 0.14191 | 0.07782 | 0.032044 | 0.11902 | 0.073243 | 0.4303 | 122.5296 | 0.18311 | 122.525 | 122.4472 | 122.2916 | 122.319 | 122.2504 | -122.4747 | -122.3877 | 122.4014 | 122.4838 | 61.9949 | 62.352
677.3906 | 122.5708 | -62.2147 | 60.1959 | -0.0051118 | -0.023983 | -0.024964 | 0.063944 | -0.028307 | -0.049099 | -0.040392 | -0.0021057 | -0.017972 | 0.056841 | 0.053312 | -0.21808 | -0.015565 | -0.023039 | -0.17853 | 60.2371 | -62.3108 | 60.1685 | -61.972 | -62.439 | -62.4115 | 0.10529 | 60.1593 | -62.2192 | 60.2646 | -62.114 | -62.2375 | -62.146 | -0.09613 | 0.041199 | -0.027466 | 0.24262 | -0.19684 | -0.2243 | -0.10071 | -0.12817 | -0.004577 | -0.036621 | 0.068664 | 0.10071 | 0.068665 | -0.022888 | 0.073242 | -0.018311 | 0.33875 | 122.4792 | 0.10528 | 122.4838 | 122.5479 | 122.3785 | 122.4518 | 122.374 | -122.5067 | -122.4152 | 122.3831 | 122.4792 | 62.0361 | 62.3199
679.2812 | 122.5433 | -62.1964 | 60.2417 | 0.010147 | -0.028897 | -0.026886 | 0.064585 | -0.031298 | -0.047177 | -0.040819 | 0.0039979 | -0.019467 | 0.057482 | 0.055021 | -0.21424 | -0.016633 | -0.022612 | -0.20599 | 60.228 | -62.352 | 60.0952 | -62.0224 | -62.4619 | -62.4573 | 0.032043 | 60.1822 | -62.2238 | 60.2188 | -62.1414 | -62.2787 | -62.1918 | -0.15564 | -0.013733 | -0.14648 | 0.17395 | -0.26093 | -0.2655 | -0.10529 | -0.10986 | -0.027466 | -0.059509 | -0.022888 | 0.054932 | 0.004578 | -0.082398 | 0.032044 | -0.054932 | 0.32959 | 122.4472 | 0.082398 | 122.4426 | 122.58 | 122.406 | 122.4243 | 122.3785 | -122.5937 | -122.4655 | 122.2916 | 122.4152 | 61.9904 | 62.2284
681.0469 | 122.5479 | -62.2055 | 60.1868 | -0.012741 | -0.024624 | -0.023469 | 0.06373 | -0.031939 | -0.048886 | -0.038042 | 0.00094606 | -0.016904 | 0.0562 | 0.050535 | -0.21467 | -0.015137 | -0.023467 | -0.20142 | 60.2051 | -62.3108 | 60.1593 | -61.9812 | -62.4527 | -62.4207 | 0.032043 | 60.1456 | -62.2238 | 60.2417 | -62.1506 | -62.2833 | -62.178 | -0.10529 | 0.01831 | -0.027466 | 0.2243 | -0.21515 | -0.24719 | -0.10986 | -0.14191 | -0.018311 | -0.041199 | 0.054931 | 0.054931 | 0.027465 | -0.07782 | 0.045776 | -0.059509 | 0.32959 | 122.4701 | 0.073242 | 122.4655 | 122.5159 | 122.3694 | 122.4106 | 122.3511 | -122.4976 | -122.4106 | 122.3648 | 122.4472 | 62.0041 | 62.2375
682.8438 | 122.644 | -62.1918 | 60.1273 | -0.0051118 | -0.027829 | -0.024537 | 0.060099 | -0.029589 | -0.048672 | -0.041033 | 0.0039979 | -0.022458 | 0.0562 | 0.046049 | -0.21637 | -0.017273 | -0.020262 | -0.2655 | 60.1639 | -62.2971 | 60.1639 | -61.9263 | -62.3932 | -62.3474 | 0.091553 | 60.1135 | -62.2421 | 60.3058 | -62.0407 | -62.1552 | -62.1002 | -0.10529 | 0.036621 | 0.036621 | 0.2655 | -0.15564 | -0.20142 | -0.050354 | -0.09613 | -0.050354 | -0.013733 | 0.17853 | 0.15106 | 0.091552 | 0.036621 | 0.14191 | 0.086975 | 0.37079 | 122.4609 | 0.20142 | 122.5479 | 122.4609 | 122.3557 | 122.3557 | 122.3053 | -122.4243 | -122.3694 | 122.3557 | 122.4976 | 61.9263 | 62.2833
684.7188 | 122.5113 | -62.2284 | 60.2142 | -0.0051118 | -0.023556 | -0.024537 | 0.063944 | -0.029162 | -0.050595 | -0.037615 | 0.00094606 | -0.017972 | 0.057054 | 0.045621 | -0.21424 | -0.017273 | -0.020476 | -0.31128 | 60.1959 | -62.3291 | 60.054 | -62.1048 | -62.5626 | -62.5351 | -0.10071 | 60.1456 | -62.2559 | 60.1868 | -62.2101 | -62.3383 | -62.233 | -0.10071 | -0.01831 | -0.16022 | 0.1236 | -0.3067 | -0.33417 | -0.20599 | -0.23346 | -0.027465 | -0.068664 | -0.027465 | 0.018311 | -0.004577 | -0.10986 | 0.022888 | -0.082398 | 0.22431 | 122.3831 | 0.045776 | 122.4426 | 122.525 | 122.4014 | 122.4243 | 122.374 | -122.5433 | -122.4701 | 122.2824 | 122.4152 | 61.9171 | 62.1277
687.2969 | 122.5754 | -62.1872 | 60.2097 | 0.0025177 | -0.024838 | -0.025818 | 0.06373 | -0.03322 | -0.049954 | -0.039751 | 0.00094606 | -0.017972 | 0.057909 | 0.045621 | -0.21702 | -0.016205 | -0.02133 | -0.21973 | 60.2051 | -62.3199 | 60.1685 | -61.9537 | -62.4298 | -62.4023 | 0.086975 | 60.173 | -62.2055 | 60.2692 | -62.1094 | -62.2375 | -62.1597 | -0.13275 | -0.004578 | -0.041199 | 0.23346 | -0.21515 | -0.24262 | -0.082398 | -0.10986 | -0.01831 | -0.036621 | 0.059509 | 0.07782 | 0.027466 | -0.050354 | 0.045776 | -0.032044 | 0.36621 | 122.4884 | 0.09613 | 122.4747 | 122.525 | 122.3785 | 122.3923 | 122.3602 | -122.5296 | -122.4152 | 122.3557 | 122.4564 | 61.9675 | 62.2742
689.0781 | 122.525 | -62.1918 | 60.2371 | -0.012741 | -0.028683 | -0.024109 | 0.063089 | -0.033434 | -0.048886 | -0.03911 | 0.0070497 | -0.019467 | 0.057054 | 0.049253 | -0.21445 | -0.01706 | -0.022826 | -0.25177 | 60.2051 | -62.3154 | 60.1044 | -62.0041 | -62.4527 | -62.4207 | 0.041199 | 60.1639 | -62.2284 | 60.2051 | -62.1506 | -62.265 | -62.1918 | -0.1236 | -0.032044 | -0.13275 | 0.18768 | -0.22888 | -0.26093 | -0.10529 | -0.13733 | -0.036622 | -0.073243 | -0.032044 | 0.041198 | 0 | -0.073243 | 0.036622 | -0.036621 | 0.31128 | 122.4197 | 0.07782 | 122.4335 | 122.5204 | 122.3923 | 122.3969 | 122.3557 | -122.5525 | -122.4655 | 122.2961 | 122.3969 | 61.94 | 62.233
690.9688 | 122.5525 | -62.178 | 60.2371 | 0.010147 | -0.026547 | -0.025391 | 0.064371 | -0.031511 | -0.04974 | -0.038896 | -0.0051575 | -0.019681 | 0.054918 | 0.048398 | -0.2168 | -0.016205 | -0.025816 | -0.24261 | 60.2097 | -62.3062 | 60.1135 | -62.027 | -62.4619 | -62.439 | 0.013733 | 60.173 | -62.233 | 60.2234 | -62.1368 | -62.2559 | -62.1689 | -0.12817 | -0.027466 | -0.1236 | 0.15106 | -0.26093 | -0.28381 | -0.13275 | -0.15564 | -0.054931 | -0.064087 | -0.013733 | 0.041199 | 0.009156 | -0.077819 | 0.064087 | -0.022888 | 0.27923 | 122.4197 | 0.09613 | 122.4564 | 122.5159 | 122.406 | 122.3877 | 122.3511 | -122.5433 | -122.4701 | 122.2916 | 122.4014 | 61.9354 | 62.1918
692.8125 | 122.5525 | -62.2055 | 60.1959 | -0.0051118 | -0.02377 | -0.026032 | 0.063516 | -0.031939 | -0.046536 | -0.041246 | 0.0039979 | -0.021176 | 0.056414 | 0.045408 | -0.21445 | -0.013428 | -0.024535 | -0.36163 | 60.2142 | -62.3474 | 60.0769 | -62.0636 | -62.5305 | -62.4985 | -0.073242 | 60.141 | -62.2787 | 60.2188 | -62.1872 | -62.3154 | -62.2055 | -0.14191 | 0.01831 | -0.11902 | 0.14191 | -0.29297 | -0.32501 | -0.15106 | -0.18311 | -0.073243 | -0.054932 | 0.022888 | 0.01831 | 0 | -0.10986 | 0.073243 | -0.036621 | 0.28381 | 122.4243 | 0.091553 | 122.4976 | 122.5616 | 122.4197 | 122.4197 | 122.3465 | -122.5433 | -122.4747 | 122.2824 | 122.4243 | 61.8439 | 62.1323
694.5312 | 122.5388 | -62.2192 | 60.2005 | 0.010147 | -0.024411 | -0.023682 | 0.065866 | -0.029802 | -0.049099 | -0.040392 | 0.00094606 | -0.018827 | 0.058123 | 0.047117 | -0.21616 | -0.014924 | -0.020903 | -0.37537 | 60.1959 | -62.3566 | 60.0677 | -62.0682 | -62.5305 | -62.4893 | -0.09613 | 60.1364 | -62.2696 | 60.2005 | -62.2009 | -62.3245 | -62.2192 | -0.13733 | -0.004577 | -0.13275 | 0.15106 | -0.27008 | -0.31128 | -0.13275 | -0.17395 | -0.050354 | -0.064086 | 0 | 0.01831 | 0 | -0.10529 | 0.050354 | -0.054932 | 0.28839 | 122.4243 | 0.068664 | 122.4701 | 122.5525 | 122.406 | 122.4152 | 122.3557 | -122.5571 | -122.4701 | 122.287 | 122.4197 | 61.8439 | 62.1231
696.25 | 122.5433 | -62.2009 | 60.1822 | -0.0051118 | -0.022702 | -0.023896 | 0.065439 | -0.029589 | -0.048458 | -0.039751 | -0.0051575 | -0.021176 | 0.057054 | 0.046262 | -0.2183 | -0.01706 | -0.022612 | -0.36621 | 60.2188 | -62.352 | 60.0677 | -62.0819 | -62.5351 | -62.4802 | -0.09613 | 60.1318 | -62.233 | 60.2142 | -62.2055 | -62.3337 | -62.2101 | -0.15106 | 0.036621 | -0.11444 | 0.11902 | -0.27924 | -0.33417 | -0.12817 | -0.1831 | -0.032043 | -0.050354 | 0.032043 | -0.004577 | -0.009155 | -0.13275 | 0.022888 | -0.10071 | 0.27008 | 122.4197 | 0.027466 | 122.4472 | 122.5708 | 122.3648 | 122.4197 | 122.3328 | -122.5342 | -122.4152 | 122.2687 | 122.4152 | 61.8347 | 62.1048
697.9844 | 122.6532 | -62.1918 | 60.1273 | 0.0025177 | -0.022061 | -0.021332 | 0.063089 | -0.032152 | -0.048672 | -0.039751 | -0.0021057 | -0.020963 | 0.055986 | 0.049039 | -0.21659 | -0.014283 | -0.023894 | -0.31586 | 60.1547 | -62.3154 | 60.1685 | -61.9492 | -62.4252 | -62.3703 | 0.041199 | 60.0586 | -62.2284 | 60.3104 | -62.0819 | -62.1964 | -62.114 | -0.1236 | 0.027466 | 0.041199 | 0.24261 | -0.17853 | -0.23346 | -0.054931 | -0.10986 | -0.036622 | -0.068664 | 0.18311 | 0.10986 | 0.077819 | -0.004578 | 0.11444 | 0.032044 | 0.36621 | 122.4838 | 0.14648 | 122.5388 | 122.4701 | 122.287 | 122.3465 | 122.2504 | -122.4426 | -122.3557 | 122.3602 | 122.5021 | 61.8759 | 62.233
699.8438 | 122.6166 | -62.1918 | 60.173 | -0.0051118 | -0.027401 | -0.024964 | 0.060739 | -0.035143 | -0.049313 | -0.039324 | -0.0021057 | -0.022031 | 0.056841 | 0.048826 | -0.21595 | -0.016846 | -0.019194 | -0.33417 | 60.1547 | -62.3154 | 60.1318 | -61.9995 | -62.4573 | -62.3978 | 0.032043 | 60.0769 | -62.2375 | 60.26 | -62.1002 | -62.2009 | -62.1323 | -0.1236 | -0.018311 | -0.041199 | 0.19226 | -0.20599 | -0.2655 | -0.082397 | -0.14191 | -0.045777 | -0.096131 | 0.086975 | 0.091552 | 0.059509 | -0.009156 | 0.10529 | 0.036621 | 0.31586 | 122.4472 | 0.13733 | 122.4976 | 122.4701 | 122.3145 | 122.3465 | 122.2687 | -122.4884 | -122.4106 | 122.3236 | 122.4518 | 61.8576 | 62.2238
701.6406 | 122.6349 | -62.1643 | 60.1501 | -0.0051118 | -0.024624 | -0.025391 | 0.062662 | -0.026384 | -0.04974 | -0.039537 | -0.0051575 | -0.019681 | 0.055345 | 0.051389 | -0.2168 | -0.017273 | -0.022826 | -0.34332 | 60.141 | -62.3108 | 60.1913 | -61.9125 | -62.4207 | -62.3474 | 0.073242 | 60.0815 | -62.2284 | 60.2921 | -62.0911 | -62.2147 | -62.1231 | -0.14648 | -0.009155 | 0.041199 | 0.25177 | -0.1831 | -0.25635 | -0.036621 | -0.10986 | -0.064087 | -0.068664 | 0.14191 | 0.073243 | 0.041199 | -0.050354 | 0.10529 | 0.013733 | 0.39825 | 122.5021 | 0.13733 | 122.5204 | 122.4518 | 122.3099 | 122.3053 | 122.2458 | -122.4609 | -122.3785 | 122.3557 | 122.4564 | 61.821 | 62.2375
703.375 | 122.5891 | -62.1735 | 60.2051 | -0.0051118 | -0.02612 | -0.024537 | 0.064798 | -0.031084 | -0.048245 | -0.037401 | 0.00094606 | -0.018613 | 0.05855 | 0.046903 | -0.21744 | -0.01471 | -0.022185 | -0.27924 | 60.2142 | -62.3154 | 60.1639 | -61.9675 | -62.4298 | -62.3978 | 0.091553 | 60.1547 | -62.2009 | 60.26 | -62.1094 | -62.233 | -62.1368 | -0.14191 | 0.009155 | -0.041199 | 0.20599 | -0.2243 | -0.25635 | -0.082397 | -0.11444 | -0.027466 | -0.050354 | 0.054932 | 0.064087 | 0.036621 | -0.059509 | 0.064087 | -0.032043 | 0.3479 | 122.4792 | 0.091553 | 122.4609 | 122.5296 | 122.3557 | 122.3877 | 122.3282 | -122.5204 | -122.406 | 122.3373 | 122.4335 | 61.8942 | 62.265
705.1562 | 122.5159 | -62.1826 | 60.2188 | 0.0025177 | -0.023983 | -0.024109 | 0.066721 | -0.029802 | -0.049313 | -0.039965 | 0.0039979 | -0.019681 | 0.054064 | 0.055662 | -0.21702 | -0.01471 | -0.018553 | -0.3891 | 60.2234 | -62.3383 | 60.0998 | -62.0544 | -62.5214 | -62.4756 | -0.082397 | 60.1501 | -62.233 | 60.1822 | -62.2147 | -62.3337 | -62.2055 | -0.15564 | 0.004578 | -0.11902 | 0.12817 | -0.29297 | -0.33875 | -0.13733 | -0.18311 | -0.050354 | -0.068665 | -0.036621 | -0.032044 | -0.022888 | -0.15106 | 0.027466 | -0.10071 | 0.28381 | 122.438 | 0.01831 | 122.4152 | 122.5616 | 122.3831 | 122.406 | 122.3328 | -122.5571 | -122.4518 | 122.2824 | 122.3648 | 61.7935 | 62.1002
706.9375 | 122.5342 | -62.2192 | 60.1868 | -0.012741 | -0.025692 | -0.024323 | 0.064585 | -0.02788 | -0.047817 | -0.039751 | 0.00094606 | -0.018827 | 0.058336 | 0.049039 | -0.21445 | -0.019623 | -0.022612 | -0.40283 | 60.228 | -62.3291 | 60.0632 | -62.0682 | -62.5305 | -62.4802 | -0.082397 | 60.1364 | -62.2421 | 60.2097 | -62.2009 | -62.3199 | -62.2147 | -0.10986 | 0.041198 | -0.1236 | 0.15106 | -0.26093 | -0.31128 | -0.15106 | -0.20142 | -0.022888 | -0.050354 | 0.022888 | 0.01831 | 0.004577 | -0.10071 | 0.027465 | -0.07782 | 0.26093 | 122.3923 | 0.041198 | 122.4518 | 122.5571 | 122.3785 | 122.4472 | 122.3557 | -122.5159 | -122.4289 | 122.2824 | 122.4289 | 61.8164 | 62.1368
708.6562 | 122.525 | -62.1689 | 60.2463 | 0.0025177 | -0.02676 | -0.026673 | 0.062021 | -0.028948 | -0.049313 | -0.039324 | -0.0051575 | -0.019681 | 0.058763 | 0.04434 | -0.21531 | -0.017701 | -0.022185 | -0.20599 | 60.2097 | -62.2971 | 60.1181 | -61.9858 | -62.4435 | -62.4161 | 0.045776 | 60.1639 | -62.2101 | 60.2051 | -62.1552 | -62.2513 | -62.1964 | -0.12817 | -0.036621 | -0.12817 | 0.1831 | -0.24719 | -0.27466 | -0.11902 | -0.14648 | -0.041199 | -0.082398 | -0.041199 | 0.013733 | -0.027466 | -0.082398 | 0.013733 | -0.041199 | 0.31128 | 122.4152 | 0.054932 | 122.4152 | 122.5067 | 122.374 | 122.3785 | 122.3328 | -122.5433 | -122.4564 | 122.287 | 122.374 | 61.9629 | 62.2147
710.4531 | 122.5342 | -62.178 | 60.2142 | -0.0051118 | -0.025265 | -0.026459 | 0.065439 | -0.028521 | -0.047817 | -0.037615 | 0.00094606 | -0.017331 | 0.055345 | 0.047544 | -0.21744 | -0.014924 | -0.027953 | -0.25177 | 60.2417 | -62.3245 | 60.1318 | -61.9858 | -62.4664 | -62.439 | 0.013733 | 60.1593 | -62.2101 | 60.2234 | -62.1643 | -62.2833 | -62.2009 | -0.14648 | 0.027466 | -0.082397 | 0.19226 | -0.26093 | -0.28839 | -0.11444 | -0.14191 | -0.032043 | -0.054931 | 0.009156 | 0.013733 | -0.022888 | -0.10528 | 0.009155 | -0.073242 | 0.33874 | 122.4564 | 0.045776 | 122.4335 | 122.5662 | 122.3694 | 122.4197 | 122.3373 | -122.5388 | -122.4243 | 122.3099 | 122.4014 | 61.9263 | 62.1918
712.2188 | 122.5983 | -62.2009 | 60.1776 | 0.010147 | -0.023343 | -0.025177 | 0.065439 | -0.030657 | -0.046536 | -0.040819 | 0.00094606 | -0.021176 | 0.057482 | 0.047544 | -0.21595 | -0.015351 | -0.018767 | -0.36621 | 60.2234 | -62.3154 | 60.0998 | -62.027 | -62.5031 | -62.4435 | -0.054932 | 60.1089 | -62.2421 | 60.2554 | -62.146 | -62.2513 | -62.1323 | -0.11444 | 0.045777 | -0.07782 | 0.17395 | -0.24261 | -0.30212 | -0.12817 | -0.18768 | -0.041198 | -0.068664 | 0.07782 | 0.054932 | 0.068665 | -0.050354 | 0.10986 | -0.009156 | 0.28839 | 122.4152 | 0.09613 | 122.4976 | 122.5388 | 122.3511 | 122.4243 | 122.3099 | -122.493 | -122.4197 | 122.3007 | 122.4564 | 61.8347 | 62.146
714 | 122.6074 | -62.1918 | 60.1776 | 0.0025177 | -0.028042 | -0.027955 | 0.061167 | -0.029802 | -0.048886 | -0.040819 | -0.0021057 | -0.022458 | 0.057482 | 0.039854 | -0.2168 | -0.015137 | -0.02368 | -0.3479 | 60.1868 | -62.3108 | 60.1364 | -61.9492 | -62.4435 | -62.3795 | 0.004578 | 60.0906 | -62.233 | 60.2417 | -62.1368 | -62.2284 | -62.1506 | -0.11902 | 0.009156 | -0.041198 | 0.24261 | -0.18768 | -0.25177 | -0.068665 | -0.13275 | -0.041199 | -0.086975 | 0.064087 | 0.054931 | 0.041198 | -0.036622 | 0.082397 | 0.004577 | 0.36163 | 122.4472 | 0.09613 | 122.4747 | 122.4976 | 122.3236 | 122.3785 | 122.2824 | -122.4884 | -122.4106 | 122.3282 | 122.4335 | 61.8439 | 62.1964
715.7969 | 122.5937 | -62.1597 | 60.2142 | 0.010147 | -0.027401 | -0.025605 | 0.062021 | -0.036211 | -0.050381 | -0.038042 | -0.0021057 | -0.020749 | 0.055986 | 0.046689 | -0.21851 | -0.017487 | -0.022612 | -0.21973 | 60.1776 | -62.3016 | 60.2051 | -61.9034 | -62.3474 | -62.3337 | 0.14191 | 60.1318 | -62.2055 | 60.2783 | -62.059 | -62.1826 | -62.1231 | -0.14191 | -0.036621 | -0.009155 | 0.25635 | -0.17395 | -0.18768 | -0.032043 | -0.045776 | -0.045776 | -0.082397 | 0.064087 | 0.10071 | 0.036621 | -0.022888 | 0.082397 | 0.022888 | 0.39825 | 122.5067 | 0.14648 | 122.4838 | 122.4792 | 122.3373 | 122.3373 | 122.2916 | -122.5159 | -122.4197 | 122.3648 | 122.438 | 61.94 | 62.3016
717.5781 | 122.6349 | -62.1689 | 60.1776 | -0.0051118 | -0.028042 | -0.026673 | 0.062448 | -0.033861 | -0.051022 | -0.038683 | -0.0021057 | -0.02139 | 0.055773 | 0.045835 | -0.2168 | -0.01706 | -0.019408 | -0.35248 | 60.1776 | -62.3154 | 60.1318 | -61.9766 | -62.439 | -62.3886 | 0.013733 | 60.1227 | -62.2101 | 60.2646 | -62.0911 | -62.1964 | -62.1231 | -0.14648 | 0 | -0.045776 | 0.19226 | -0.21973 | -0.27008 | -0.073242 | -0.1236 | -0.041199 | -0.054931 | 0.086975 | 0.07782 | 0.045776 | -0.027466 | 0.086975 | 0.013733 | 0.33874 | 122.4472 | 0.11902 | 122.4747 | 122.493 | 122.3328 | 122.3465 | 122.2916 | -122.493 | -122.3877 | 122.3007 | 122.4335 | 61.8164 | 62.1826
719.2812 | 122.5571 | -62.178 | 60.2097 | -0.012741 | -0.027401 | -0.025605 | 0.06608 | -0.029375 | -0.049526 | -0.038683 | -0.0021057 | -0.016904 | 0.055132 | 0.051816 | -0.21894 | -0.015992 | -0.024535 | -0.26093 | 60.2234 | -62.3108 | 60.1501 | -61.9629 | -62.4298 | -62.4023 | 0.068665 | 60.1364 | -62.2055 | 60.2646 | -62.114 | -62.2238 | -62.1414 | -0.13275 | 0.013733 | -0.05951 | 0.21515 | -0.2243 | -0.25177 | -0.091553 | -0.11902 | -0.027465 | -0.073242 | 0.054931 | 0.064087 | 0.036622 | -0.045776 | 0.064087 | -0.018311 | 0.3479 | 122.4609 | 0.091552 | 122.4701 | 122.5342 | 122.3419 | 122.4014 | 122.3145 | -122.5204 | -122.4152 | 122.3282 | 122.4426 | 61.9171 | 62.2467
721.0781 | 122.612 | -62.1735 | 60.141 | -0.012741 | -0.026974 | -0.026246 | 0.061167 | -0.03322 | -0.048031 | -0.040819 | -0.0021057 | -0.020963 | 0.055986 | 0.048612 | -0.21702 | -0.018128 | -0.026671 | -0.35248 | 60.1639 | -62.2742 | 60.1364 | -61.9675 | -62.439 | -62.3795 | 0 | 60.0769 | -62.2192 | 60.2417 | -62.1185 | -62.2101 | -62.1597 | -0.10071 | 0.022888 | -0.004577 | 0.20599 | -0.20599 | -0.2655 | -0.10529 | -0.1648 | -0.045776 | -0.064087 | 0.10071 | 0.054932 | 0.013733 | -0.036621 | 0.059509 | 0.009155 | 0.3067 | 122.4106 | 0.10071 | 122.4609 | 122.438 | 122.2961 | 122.3373 | 122.2504 | -122.4152 | -122.3602 | 122.3099 | 122.4152 | 61.821 | 62.1735
722.875 | 122.5388 | -62.1826 | 60.228 | 0.0025177 | -0.025906 | -0.026459 | 0.06608 | -0.029162 | -0.046108 | -0.041887 | 0.00094606 | -0.019681 | 0.057268 | 0.042844 | -0.21872 | -0.017701 | -0.023253 | -0.28381 | 60.2554 | -62.3199 | 60.1181 | -62.027 | -62.4619 | -62.439 | 0.027466 | 60.1868 | -62.2009 | 60.2234 | -62.1185 | -62.2284 | -62.1689 | -0.13733 | 0.027466 | -0.10986 | 0.15564 | -0.25635 | -0.27924 | -0.11902 | -0.14191 | -0.018311 | -0.041198 | -0.004577 | 0.064087 | 0.013733 | -0.045777 | 0.032044 | -0.027466 | 0.29297 | 122.438 | 0.082398 | 122.4243 | 122.5754 | 122.3877 | 122.438 | 122.3694 | -122.5479 | -122.4289 | 122.3007 | 122.406 | 61.8988 | 62.2101
724.5938 | 122.6486 | -62.1643 | 60.1959 | -0.0051118 | -0.027188 | -0.026246 | 0.062021 | -0.027239 | -0.049313 | -0.042742 | 0.00094606 | -0.021604 | 0.054918 | 0.038358 | -0.21552 | -0.018982 | -0.022826 | -0.26093 | 60.1364 | -62.2971 | 60.228 | -61.8713 | -62.3245 | -62.2971 | 0.17395 | 60.1181 | -62.1689 | 60.3195 | -62.0132 | -62.1277 | -62.0819 | -0.13275 | -0.059509 | 0.032043 | 0.29297 | -0.13275 | -0.16022 | 0 | -0.027466 | -0.004577 | -0.07782 | 0.1236 | 0.15106 | 0.082398 | 0.036621 | 0.086975 | 0.041198 | 0.42572 | 122.525 | 0.15564 | 122.4884 | 122.4335 | 122.287 | 122.3007 | 122.2824 | -122.493 | -122.3648 | 122.3923 | 122.4838 | 61.9034 | 62.3383
726.3125 | 122.5388 | -62.1872 | 60.2417 | -0.0051118 | -0.026974 | -0.028595 | 0.062662 | -0.03258 | -0.050595 | -0.039537 | -0.0021057 | -0.018613 | 0.056627 | 0.047544 | -0.21616 | -0.01471 | -0.021758 | -0.31586 | 60.2371 | -62.3154 | 60.1227 | -62.0224 | -62.4573 | -62.4252 | 0.018311 | 60.1776 | -62.2284 | 60.2188 | -62.1368 | -62.2513 | -62.1689 | -0.12817 | -0.004577 | -0.11902 | 0.1648 | -0.23804 | -0.27008 | -0.10986 | -0.14191 | -0.041199 | -0.064087 | -0.022888 | 0.050354 | 0.018311 | -0.064087 | 0.05951 | -0.022888 | 0.29297 | 122.4381 | 0.091553 | 122.4472 | 122.5525 | 122.406 | 122.4243 | 122.3648 | -122.5571 | -122.4701 | 122.3099 | 122.406 | 61.8713 | 62.2055
728.0156 | 122.6532 | -62.1643 | 60.1501 | 0.0025177 | -0.024197 | -0.024537 | 0.061594 | -0.030016 | -0.049313 | -0.037187 | -0.0021057 | -0.020963 | 0.057054 | 0.047544 | -0.21744 | -0.015778 | -0.023467 | -0.40741 | 60.1501 | -62.2833 | 60.1868 | -61.9171 | -62.4207 | -62.3566 | 0.068665 | 60.0632 | -62.2284 | 60.3195 | -62.0636 | -62.1735 | -62.1048 | -0.11902 | 0 | 0.036622 | 0.24719 | -0.19226 | -0.25635 | -0.073242 | -0.13733 | -0.064087 | -0.086975 | 0.16937 | 0.10071 | 0.05951 | -0.009155 | 0.1236 | 0.054932 | 0.36621 | 122.4701 | 0.16479 | 122.5479 | 122.4335 | 122.2916 | 122.3145 | 122.2275 | -122.4335 | -122.3785 | 122.3511 | 122.4838 | 61.7569 | 62.233
729.8125 | 122.6532 | -62.1506 | 60.1639 | -0.0051118 | -0.023983 | -0.025177 | 0.062876 | -0.031084 | -0.048245 | -0.036333 | -0.0051575 | -0.020749 | 0.053423 | 0.041563 | -0.21702 | -0.013642 | -0.020689 | -0.44403 | 60.1593 | -62.2925 | 60.1868 | -61.9354 | -62.4207 | -62.3657 | 0.032043 | 60.0952 | -62.2147 | 60.3195 | -62.059 | -62.178 | -62.0865 | -0.14191 | -0.004577 | 0.022889 | 0.21515 | -0.21515 | -0.27008 | -0.073243 | -0.12817 | -0.064087 | -0.068664 | 0.15564 | 0.091553 | 0.064087 | -0.027466 | 0.12817 | 0.036621 | 0.35705 | 122.4792 | 0.15564 | 122.5342 | 122.4518 | 122.3099 | 122.3099 | 122.2458 | -122.4564 | -122.3785 | 122.3373 | 122.4701 | 61.7065 | 62.1826
731.6094 | 122.6166 | -62.1643 | 60.1685 | 0.0025177 | -0.023343 | -0.024109 | 0.066507 | -0.03023 | -0.049313 | -0.03911 | -0.0021057 | -0.020108 | 0.056841 | 0.044553 | -0.21595 | -0.015565 | -0.021971 | -0.55389 | 60.1913 | -62.3108 | 60.1044 | -62.0041 | -62.4802 | -62.4298 | -0.054932 | 60.0998 | -62.2284 | 60.2692 | -62.1185 | -62.233 | -62.114 | -0.14648 | 0.022888 | -0.064087 | 0.16022 | -0.2655 | -0.31586 | -0.11902 | -0.16937 | -0.064087 | -0.068665 | 0.10071 | 0.045777 | 0.050354 | -0.068664 | 0.11444 | -0.004577 | 0.3067 | 122.4152 | 0.10986 | 122.4976 | 122.5021 | 122.3282 | 122.3557 | 122.2641 | -122.4792 | -122.3969 | 122.2687 | 122.4335 | 61.6104 | 62.1094
733.4062 | 122.5159 | -62.146 | 60.2371 | 0.0025177 | -0.028256 | -0.0271 | 0.062235 | -0.03023 | -0.049954 | -0.038469 | 0.00094606 | -0.018613 | 0.055986 | 0.046689 | -0.21552 | -0.016633 | -0.021544 | -0.50812 | 60.2417 | -62.3108 | 60.1364 | -61.9949 | -62.4527 | -62.4115 | 0.027466 | 60.1913 | -62.1964 | 60.2234 | -62.146 | -62.2421 | -62.1735 | -0.1648 | 0.004577 | -0.10071 | 0.15106 | -0.2655 | -0.3067 | -0.10071 | -0.14191 | -0.050354 | -0.045777 | -0.013733 | 0 | -0.027466 | -0.09613 | 0.022888 | -0.045776 | 0.31586 | 122.4472 | 0.050354 | 122.4197 | 122.5525 | 122.3877 | 122.3877 | 122.3373 | -122.5479 | -122.4335 | 122.2824 | 122.3694 | 61.6379 | 62.1735
735.1875 | 122.5021 | -62.1918 | 60.2234 | 0.010147 | -0.022915 | -0.023896 | 0.067789 | -0.03023 | -0.049526 | -0.039537 | 0.0039979 | -0.019895 | 0.055559 | 0.04733 | -0.21552 | -0.014924 | -0.02368 | -0.63171 | 60.2234 | -62.3245 | 60.0952 | -62.0316 | -62.5214 | -62.4619 | -0.086975 | 60.1685 | -62.2284 | 60.1959 | -62.1735 | -62.3199 | -62.1918 | -0.13275 | 0 | -0.12817 | 0.16022 | -0.27008 | -0.32959 | -0.13733 | -0.19684 | -0.036622 | -0.054932 | -0.027466 | 0.01831 | 0 | -0.12817 | 0.036622 | -0.091552 | 0.29297 | 122.4197 | 0.054932 | 122.4243 | 122.5479 | 122.3969 | 122.4152 | 122.3602 | -122.5479 | -122.4518 | 122.287 | 122.3877 | 61.5601 | 62.1048
736.9688 | 122.5479 | -62.1597 | 60.2554 | -0.0051118 | -0.02911 | -0.026246 | 0.061808 | -0.035143 | -0.050381 | -0.040392 | -0.0021057 | -0.019467 | 0.055132 | 0.050321 | -0.21637 | -0.01706 | -0.02368 | -0.57678 | 60.1685 | -62.2971 | 60.2051 | -61.8896 | -62.3474 | -62.3245 | 0.11902 | 60.1547 | -62.178 | 60.26 | -62.1002 | -62.1872 | -62.1552 | -0.13733 | -0.086975 | -0.050354 | 0.27008 | -0.16479 | -0.18768 | -0.027466 | -0.050354 | -0.018311 | -0.10071 | 0.004578 | 0.059509 | 0.004578 | -0.027466 | 0.022889 | -0.009155 | 0.40741 | 122.5021 | 0.07782 | 122.4381 | 122.4655 | 122.3328 | 122.3282 | 122.3145 | -122.5525 | -122.4335 | 122.3648 | 122.4197 | 61.5829 | 62.2787
738.7031 | 122.6532 | -62.1277 | 60.1776 | 0.0025177 | -0.025692 | -0.028595 | 0.062021 | -0.03557 | -0.050381 | -0.038256 | -0.0021057 | -0.022245 | 0.054064 | 0.050748 | -0.21595 | -0.014924 | -0.022826 | -0.6134 | 60.1547 | -62.2971 | 60.2325 | -61.8439 | -62.3245 | -62.2879 | 0.16937 | 60.0998 | -62.1735 | 60.3424 | -61.9904 | -62.0956 | -62.0636 | -0.16937 | -0.022888 | 0.054932 | 0.28381 | -0.16022 | -0.19684 | 0.009155 | -0.027466 | -0.045776 | -0.07782 | 0.16479 | 0.13733 | 0.064087 | 0.032044 | 0.10986 | 0.07782 | 0.45319 | 122.5296 | 0.18311 | 122.5159 | 122.4518 | 122.2733 | 122.2824 | 122.2275 | -122.4747 | -122.3511 | 122.3602 | 122.4701 | 61.5143 | 62.2971
740.5 | 122.644 | -62.178 | 60.1501 | -0.012741 | -0.025051 | -0.023255 | 0.062235 | -0.030871 | -0.049099 | -0.039965 | -0.0021057 | -0.021176 | 0.054277 | 0.049039 | -0.21872 | -0.015778 | -0.020049 | -0.78278 | 60.141 | -62.2925 | 60.2051 | -61.9034 | -62.3978 | -62.3566 | 0.050354 | 60.0952 | -62.2055 | 60.3012 | -62.0453 | -62.1597 | -62.0865 | -0.11444 | -0.009155 | 0.054932 | 0.27466 | -0.17853 | -0.21973 | -0.064087 | -0.10529 | -0.027465 | -0.054931 | 0.15106 | 0.13275 | 0.091553 | 0.018311 | 0.11902 | 0.045776 | 0.3891 | 122.4976 | 0.16022 | 122.5067 | 122.4335 | 122.3007 | 122.319 | 122.2733 | -122.4426 | -122.3557 | 122.3831 | 122.4792 | 61.3953 | 62.2284
742.2969 | 122.6532 | -62.1552 | 60.1685 | 0.010147 | -0.026547 | -0.022828 | 0.06373 | -0.028734 | -0.04739 | -0.039324 | -0.0021057 | -0.021604 | 0.0562 | 0.049039 | -0.21766 | -0.015137 | -0.020903 | -0.86975 | 60.173 | -62.3199 | 60.1639 | -61.94 | -62.4252 | -62.3886 | 0.018311 | 60.1135 | -62.2192 | 60.3012 | -62.0728 | -62.1826 | -62.0865 | -0.1648 | 0.004578 | -0.004578 | 0.21515 | -0.23346 | -0.27008 | -0.068665 | -0.10529 | -0.064087 | -0.054932 | 0.13275 | 0.082397 | 0.068664 | -0.027466 | 0.13275 | 0.036621 | 0.37994 | 122.4838 | 0.14648 | 122.5204 | 122.493 | 122.3328 | 122.3282 | 122.2687 | -122.4884 | -122.3877 | 122.319 | 122.4564 | 61.2854 | 62.1735
744.0781 | 122.5204 | -62.1414 | 60.2554 | -0.0051118 | -0.028256 | -0.026246 | 0.062876 | -0.032152 | -0.048458 | -0.040392 | 0.00094606 | -0.019467 | 0.0562 | 0.046262 | -0.21488 | -0.015992 | -0.021544 | -0.86975 | 60.2509 | -62.2879 | 60.1364 | -61.9812 | -62.4344 | -62.3978 | 0.045776 | 60.2142 | -62.178 | 60.2371 | -62.1323 | -62.2375 | -62.178 | -0.14648 | -0.004578 | -0.11902 | 0.16022 | -0.25635 | -0.29297 | -0.10986 | -0.14648 | -0.036622 | -0.041199 | -0.01831 | 0.009155 | -0.036622 | -0.096131 | 0 | -0.059509 | 0.3067 | 122.4243 | 0.045777 | 122.4152 | 122.5388 | 122.3923 | 122.3923 | 122.3557 | -122.5433 | -122.4335 | 122.2778 | 122.3785 | 61.2717 | 62.1872
745.875 | 122.5204 | -62.146 | 60.2417 | -0.0051118 | -0.027829 | -0.026886 | 0.060739 | -0.029375 | -0.04974 | -0.039537 | -0.0021057 | -0.019254 | 0.056414 | 0.051603 | -0.21531 | -0.01471 | -0.023253 | -0.93384 | 60.2646 | -62.2787 | 60.1273 | -61.9904 | -62.4252 | -62.4115 | 0.027466 | 60.173 | -62.1918 | 60.2417 | -62.1323 | -62.2467 | -62.1643 | -0.13275 | 0.022888 | -0.11444 | 0.15564 | -0.2655 | -0.27924 | -0.13275 | -0.14648 | -0.045776 | -0.068664 | 0 | 0.013733 | -0.018311 | -0.10071 | 0.027465 | -0.054932 | 0.28839 | 122.406 | 0.059509 | 122.4335 | 122.5433 | 122.3648 | 122.4106 | 122.319 | -122.5204 | -122.4335 | 122.2733 | 122.3877 | 61.2122 | 62.1735
747.6094 | 122.5388 | -62.178 | 60.2417 | -0.0051118 | -0.024197 | -0.023896 | 0.065439 | -0.031939 | -0.050381 | -0.037828 | -0.0021057 | -0.019681 | 0.055345 | 0.048826 | -0.21808 | -0.015778 | -0.021971 | -1.0025 | 60.2142 | -62.2833 | 60.1776 | -61.9492 | -62.4298 | -62.4115 | 0.036621 | 60.1776 | -62.1918 | 60.2646 | -62.1323 | -62.2604 | -62.1597 | -0.10528 | -0.027466 | -0.064087 | 0.22888 | -0.23346 | -0.25177 | -0.12817 | -0.14649 | -0.013732 | -0.064087 | 0.022888 | 0.045777 | 0.018311 | -0.082397 | 0.032043 | -0.068665 | 0.33417 | 122.4609 | 0.059509 | 122.4564 | 122.4976 | 122.3694 | 122.3923 | 122.3557 | -122.525 | -122.4335 | 122.3557 | 122.4426 | 61.1755 | 62.2147
749.3906 | 122.5479 | -62.1597 | 60.2371 | 0.0025177 | -0.030392 | -0.026246 | 0.06138 | -0.027666 | -0.051022 | -0.03911 | -0.0021057 | -0.020536 | 0.055132 | 0.047971 | -0.21702 | -0.016633 | -0.024321 | -1.0071 | 60.2005 | -62.265 | 60.1868 | -61.8896 | -62.352 | -62.3383 | 0.07782 | 60.1913 | -62.1735 | 60.2509 | -62.0819 | -62.1964 | -62.146 | -0.10529 | -0.036622 | -0.050354 | 0.27008 | -0.17853 | -0.19226 | -0.073242 | -0.086975 | -0.013733 | -0.045777 | 0.013732 | 0.07782 | 0.013733 | -0.036621 | 0.027466 | -0.022888 | 0.37537 | 122.4518 | 0.091553 | 122.4243 | 122.4655 | 122.3648 | 122.3602 | 122.3511 | -122.5021 | -122.4106 | 122.3465 | 122.4106 | 61.1526 | 62.2375
751.0938 | 122.6624 | -62.1231 | 60.1776 | -0.0051118 | -0.028897 | -0.025177 | 0.061167 | -0.035143 | -0.049313 | -0.038896 | -0.0051575 | -0.020322 | 0.056627 | 0.039854 | -0.21723 | -0.01706 | -0.022612 | -1.0941 | 60.2051 | -62.2696 | 60.2188 | -61.8622 | -62.3245 | -62.2742 | 0.16022 | 60.1181 | -62.2009 | 60.347 | -62.0041 | -62.0956 | -62.0453 | -0.14648 | 0.027466 | 0.041199 | 0.26093 | -0.15106 | -0.20142 | -0.004578 | -0.054932 | -0.07782 | -0.059509 | 0.16937 | 0.11902 | 0.07782 | 0.027466 | 0.15564 | 0.10529 | 0.40741 | 122.4884 | 0.19684 | 122.5479 | 122.4747 | 122.319 | 122.3282 | 122.2412 | -122.4472 | -122.3785 | 122.3419 | 122.4701 | 61.0291 | 62.2833
752.8906 | 122.644 | -62.1368 | 60.1593 | -0.012741 | -0.02612 | -0.023896 | 0.060953 | -0.028521 | -0.048886 | -0.041033 | -0.0021057 | -0.020749 | 0.057268 | 0.046476 | -0.21766 | -0.014924 | -0.023039 | -1.1902 | 60.1639 | -62.2604 | 60.1959 | -61.9034 | -62.3978 | -62.3383 | 0.036621 | 60.1135 | -62.2009 | 60.3287 | -62.0453 | -62.1597 | -62.0819 | -0.1236 | 0.004577 | 0.036621 | 0.23346 | -0.20142 | -0.26093 | -0.07782 | -0.13733 | -0.064087 | -0.045777 | 0.16937 | 0.091553 | 0.054932 | -0.022888 | 0.11902 | 0.041199 | 0.35706 | 122.4564 | 0.15564 | 122.5296 | 122.4243 | 122.3145 | 122.3007 | 122.2504 | -122.4197 | -122.3602 | 122.3328 | 122.4655 | 60.9467 | 62.1735
754.5938 | 122.5113 | -62.146 | 60.2554 | 0.0025177 | -0.02911 | -0.026673 | 0.062021 | -0.029802 | -0.050595 | -0.039751 | 0.0039979 | -0.018186 | 0.055986 | 0.049894 | -0.21659 | -0.015565 | -0.024535 | -1.2039 | 60.2463 | -62.2833 | 60.1181 | -61.972 | -62.4069 | -62.3886 | 0.027466 | 60.228 | -62.1918 | 60.2371 | -62.1185 | -62.2421 | -62.1643 | -0.13733 | -0.009155 | -0.13733 | 0.17395 | -0.24262 | -0.26093 | -0.10529 | -0.1236 | -0.045776 | -0.027466 | -0.01831 | 0.027466 | -0.018311 | -0.09613 | 0.027465 | -0.050354 | 0.31128 | 122.4014 | 0.073242 | 122.4289 | 122.5296 | 122.4197 | 122.3923 | 122.374 | -122.5388 | -122.4472 | 122.2641 | 122.3831 | 60.9421 | 62.1735
756.375 | 122.6624 | -62.114 | 60.2005 | -0.02037 | -0.028042 | -0.025605 | 0.06138 | -0.037066 | -0.049099 | -0.038896 | 0.00094606 | -0.020108 | 0.054705 | 0.046903 | -0.21723 | -0.016419 | -0.023467 | -1.2039 | 60.1822 | -62.265 | 60.2325 | -61.8484 | -62.3199 | -62.2833 | 0.16022 | 60.1273 | -62.1918 | 60.3561 | -61.9904 | -62.1002 | -62.0499 | -0.15106 | -0.01831 | 0.032044 | 0.2655 | -0.16937 | -0.20599 | -0.01831 | -0.054931 | -0.077819 | -0.073242 | 0.15564 | 0.1236 | 0.064087 | 0.013733 | 0.14191 | 0.091552 | 0.41656 | 122.4976 | 0.20142 | 122.5479 | 122.4472 | 122.319 | 122.2961 | 122.2412 | -122.4655 | -122.3923 | 122.3465 | 122.4701 | 60.91 | 62.2742
758.1406 | 122.5662 | -62.1323 | 60.2417 | -0.0051118 | -0.02612 | -0.025177 | 0.066294 | -0.033861 | -0.050167 | -0.042528 | 0.00094606 | -0.017758 | 0.056841 | 0.055021 | -0.21915 | -0.01706 | -0.021971 | -1.2497 | 60.2554 | -62.2879 | 60.1776 | -61.9537 | -62.3932 | -62.3703 | 0.068665 | 60.1959 | -62.1643 | 60.3012 | -62.0636 | -62.2101 | -62.114 | -0.15564 | 0.013733 | -0.064087 | 0.17853 | -0.23804 | -0.26093 | -0.082397 | -0.10529 | -0.032044 | -0.045776 | 0.059509 | 0.068664 | 0.01831 | -0.07782 | 0.050354 | -0.045776 | 0.33417 | 122.4655 | 0.10071 | 122.4655 | 122.5433 | 122.3602 | 122.3877 | 122.3282 | -122.5296 | -122.406 | 122.3099 | 122.4335 | 60.8826 | 62.2009
759.9219 | 122.6349 | -62.1368 | 60.2097 | 0.0025177 | -0.02377 | -0.023682 | 0.065439 | -0.028734 | -0.047177 | -0.041246 | 0.00094606 | -0.020963 | 0.056414 | 0.047971 | -0.21872 | -0.016419 | -0.022612 | -1.3687 | 60.1593 | -62.2467 | 60.2188 | -61.8805 | -62.3795 | -62.3337 | 0.045776 | 60.1044 | -62.1964 | 60.3378 | -62.0499 | -62.146 | -62.0682 | -0.10986 | -0.050354 | 0.009155 | 0.25635 | -0.19684 | -0.24262 | -0.086975 | -0.13275 | -0.059509 | -0.10529 | 0.12817 | 0.086975 | 0.068665 | -0.009155 | 0.12817 | 0.050354 | 0.36621 | 122.4655 | 0.14648 | 122.5342 | 122.406 | 122.3007 | 122.2961 | 122.2412 | -122.4564 | -122.406 | 122.3557 | 122.4747 | 60.7681 | 62.1826
761.6406 | 122.6532 | -62.1231 | 60.1593 | -0.0051118 | -0.021847 | -0.023041 | 0.06373 | -0.026598 | -0.050808 | -0.042528 | -0.0051575 | -0.019254 | 0.054277 | 0.046476 | -0.21702 | -0.015137 | -0.023894 | -1.4282 | 60.1776 | -62.2879 | 60.2234 | -61.8851 | -62.3886 | -62.3245 | 0.045776 | 60.1044 | -62.2147 | 60.3424 | -62.0178 | -62.1597 | -62.0728 | -0.16479 | 0.01831 | 0.064087 | 0.23804 | -0.20142 | -0.2655 | -0.036621 | -0.10071 | -0.091553 | -0.054932 | 0.18311 | 0.10529 | 0.050354 | -0.036621 | 0.14191 | 0.054932 | 0.40283 | 122.5113 | 0.19684 | 122.5571 | 122.4655 | 122.319 | 122.3007 | 122.2275 | -122.4472 | -122.374 | 122.3465 | 122.4655 | 60.6949 | 62.1689
763.4219 | 122.644 | -62.1231 | 60.2097 | 0.0025177 | -0.026333 | -0.026673 | 0.06138 | -0.033434 | -0.049954 | -0.03911 | -0.0051575 | -0.023099 | 0.055773 | 0.048185 | -0.2168 | -0.016419 | -0.022612 | -1.442 | 60.2097 | -62.2879 | 60.1959 | -61.8759 | -62.3337 | -62.2879 | 0.11902 | 60.1547 | -62.1964 | 60.3561 | -61.9995 | -62.0911 | -62.0407 | -0.16479 | 0 | -0.013733 | 0.24719 | -0.16479 | -0.21057 | 0 | -0.045776 | -0.073242 | -0.054932 | 0.14648 | 0.1236 | 0.082398 | 0.032044 | 0.15564 | 0.10529 | 0.41199 | 122.4838 | 0.19684 | 122.5525 | 122.4976 | 122.3511 | 122.3328 | 122.2778 | -122.4976 | -122.406 | 122.319 | 122.4792 | 60.6812 | 62.2421
765.125 | 122.6349 | -62.1185 | 60.2325 | 0.0025177 | -0.027401 | -0.025391 | 0.062662 | -0.032793 | -0.049526 | -0.043383 | 0.0039979 | -0.020536 | 0.054491 | 0.041563 | -0.21573 | -0.016846 | -0.023894 | -1.5106 | 60.2005 | -62.265 | 60.1959 | -61.9217 | -62.3566 | -62.3199 | 0.082397 | 60.1318 | -62.1597 | 60.3287 | -62.0132 | -62.1048 | -62.0316 | -0.14648 | -0.032044 | -0.036621 | 0.19684 | -0.20142 | -0.23804 | -0.054931 | -0.091552 | -0.041199 | -0.10071 | 0.09613 | 0.10529 | 0.086975 | 0.013733 | 0.12817 | 0.054932 | 0.34332 | 122.4609 | 0.14648 | 122.4884 | 122.4655 | 122.2916 | 122.319 | 122.2504 | -122.4976 | -122.3923 | 122.3145 | 122.4472 | 60.6079 | 62.2009
766.9219 | 122.6303 | -62.1368 | 60.2097 | 0.0025177 | -0.026547 | -0.027314 | 0.062448 | -0.032793 | -0.04974 | -0.043169 | -0.0021057 | -0.021176 | 0.055773 | 0.053312 | -0.21702 | -0.017273 | -0.022185 | -1.6113 | 60.2097 | -62.2925 | 60.1822 | -61.9217 | -62.3749 | -62.3154 | 0.036621 | 60.1547 | -62.178 | 60.3241 | -62.0499 | -62.1368 | -62.0682 | -0.15564 | 0 | -0.027466 | 0.21515 | -0.17853 | -0.23804 | -0.022889 | -0.082398 | -0.041199 | -0.054932 | 0.11444 | 0.086975 | 0.068665 | 0 | 0.10986 | 0.041199 | 0.37079 | 122.4747 | 0.12817 | 122.5021 | 122.5021 | 122.3328 | 122.3465 | 122.2916 | -122.5021 | -122.3877 | 122.319 | 122.4609 | 60.5255 | 62.1735
768.7031 | 122.5662 | -62.1368 | 60.2646 | -0.0051118 | -0.025479 | -0.026246 | 0.063944 | -0.033007 | -0.050167 | -0.037828 | -0.0021057 | -0.019895 | 0.056627 | 0.04498 | -0.2168 | -0.01471 | -0.024535 | -1.6159 | 60.2646 | -62.2604 | 60.173 | -61.9537 | -62.384 | -62.3474 | 0.032043 | 60.2097 | -62.1735 | 60.3058 | -62.0728 | -62.2055 | -62.0956 | -0.1236 | 0 | -0.091552 | 0.18311 | -0.21057 | -0.24719 | -0.086975 | -0.1236 | -0.036621 | -0.054931 | 0.041199 | 0.064087 | 0.041199 | -0.068664 | 0.07782 | -0.032043 | 0.3067 | 122.4335 | 0.10071 | 122.4792 | 122.525 | 122.3831 | 122.4014 | 122.3465 | -122.525 | -122.438 | 122.3099 | 122.4426 | 60.5209 | 62.1689
770.4844 | 122.4884 | -62.1689 | 60.2646 | 0.0025177 | -0.023983 | -0.023255 | 0.065653 | -0.028521 | -0.050808 | -0.040392 | 0.0039979 | -0.018613 | 0.054064 | 0.056516 | -0.21808 | -0.016419 | -0.026244 | -1.6067 | 60.2554 | -62.2787 | 60.1227 | -62.0361 | -62.4847 | -62.439 | -0.09613 | 60.2051 | -62.2192 | 60.2142 | -62.1689 | -62.3154 | -62.1918 | -0.10986 | -0.009155 | -0.14191 | 0.13275 | -0.27008 | -0.31586 | -0.16022 | -0.20599 | -0.050354 | -0.059509 | -0.050354 | 0 | -0.022888 | -0.14648 | 0.027466 | -0.096131 | 0.24262 | 122.4014 | 0.050354 | 122.4335 | 122.5342 | 122.4243 | 122.4243 | 122.374 | -122.5433 | -122.4838 | 122.2916 | 122.3831 | 60.5621 | 62.0728
772.2656 | 122.5113 | -62.1506 | 60.2966 | -0.0051118 | -0.027615 | -0.026459 | 0.063089 | -0.030871 | -0.05209 | -0.03911 | -0.0021057 | -0.020322 | 0.056841 | 0.043699 | -0.21552 | -0.017487 | -0.021758 | -1.5472 | 60.228 | -62.2375 | 60.1639 | -61.9492 | -62.4115 | -62.3566 | 0.041199 | 60.2005 | -62.1689 | 60.26 | -62.1048 | -62.2101 | -62.146 | -0.086975 | -0.068665 | -0.13275 | 0.20142 | -0.20599 | -0.26093 | -0.11902 | -0.17395 | -0.01831 | -0.096131 | -0.036621 | 0.045777 | 0.004578 | -0.059509 | 0.022888 | -0.041199 | 0.28839 | 122.4014 | 0.064087 | 122.4289 | 122.4655 | 122.3694 | 122.3785 | 122.3511 | -122.5342 | -122.4655 | 122.3145 | 122.4106 | 60.6033 | 62.1918
773.9688 | 122.6669 | -62.1094 | 60.2188 | 0.0025177 | -0.028897 | -0.026246 | 0.062876 | -0.029589 | -0.04974 | -0.040605 | -0.0021057 | -0.020536 | 0.056841 | 0.03964 | -0.21744 | -0.016846 | -0.021117 | -1.5884 | 60.2188 | -62.265 | 60.2554 | -61.7981 | -62.3108 | -62.2467 | 0.20142 | 60.1639 | -62.1735 | 60.3699 | -61.9675 | -62.0728 | -62.0316 | -0.15564 | 0 | 0.036621 | 0.31128 | -0.13733 | -0.20142 | 0.018311 | -0.045776 | -0.064087 | -0.054932 | 0.15106 | 0.14191 | 0.07782 | 0.036621 | 0.14191 | 0.10071 | 0.46692 | 122.5204 | 0.20599 | 122.5433 | 122.4838 | 122.3373 | 122.3282 | 122.2733 | -122.4838 | -122.3923 | 122.3648 | 122.4792 | 60.5209 | 62.3108
775.7656 | 122.6303 | -62.1231 | 60.1959 | 0.010147 | -0.023343 | -0.024964 | 0.063944 | -0.025316 | -0.048458 | -0.042955 | -0.0021057 | -0.020963 | 0.055132 | 0.052671 | -0.21937 | -0.016633 | -0.022612 | -1.3687 | 60.1959 | -62.2238 | 60.2371 | -61.8668 | -62.3703 | -62.3199 | 0.041199 | 60.1181 | -62.1872 | 60.347 | -62.0178 | -62.1368 | -62.0453 | -0.10071 | 0 | 0.041199 | 0.25635 | -0.19684 | -0.24719 | -0.09613 | -0.14648 | -0.064087 | -0.07782 | 0.15106 | 0.10529 | 0.07782 | -0.013733 | 0.14191 | 0.050354 | 0.35706 | 122.4609 | 0.16937 | 122.5342 | 122.4197 | 122.3053 | 122.319 | 122.2412 | -122.4197 | -122.3831 | 122.3602 | 122.4701 | 60.7544 | 62.1643
777.5781 | 122.5342 | -62.1277 | 60.2646 | -0.0051118 | -0.026547 | -0.025818 | 0.064371 | -0.028307 | -0.051235 | -0.038683 | -0.0021057 | -0.018399 | 0.057695 | 0.053098 | -0.21851 | -0.014283 | -0.020689 | -1.4282 | 60.26 | -62.2604 | 60.1868 | -61.9217 | -62.3978 | -62.3749 | 0.027466 | 60.2234 | -62.1552 | 60.2921 | -62.114 | -62.233 | -62.114 | -0.13275 | -0.004577 | -0.077819 | 0.20599 | -0.24719 | -0.27008 | -0.11444 | -0.13733 | -0.027465 | -0.041198 | 0.027466 | 0.013733 | 0.013733 | -0.10529 | 0.041198 | -0.07782 | 0.33875 | 122.4472 | 0.041198 | 122.4472 | 122.5204 | 122.3785 | 122.3877 | 122.3511 | -122.525 | -122.4197 | 122.3145 | 122.4197 | 60.6995 | 62.1552
779.2969 | 122.6532 | -62.0911 | 60.2234 | -0.0051118 | -0.026974 | -0.026673 | 0.06138 | -0.034716 | -0.051449 | -0.039324 | -0.0021057 | -0.020536 | 0.053636 | 0.035367 | -0.21573 | -0.01706 | -0.025176 | -1.474 | 60.2234 | -62.2604 | 60.2966 | -61.7615 | -62.2513 | -62.2375 | 0.16022 | 60.1913 | -62.1552 | 60.3882 | -61.9766 | -62.0636 | -62.0132 | -0.16937 | 0 | 0.073242 | 0.32959 | -0.14648 | -0.16022 | 0.022888 | 0.009155 | -0.064087 | -0.032044 | 0.1648 | 0.11444 | 0.077819 | 0.027465 | 0.14191 | 0.091552 | 0.49896 | 122.5571 | 0.17853 | 122.5433 | 122.4838 | 122.3465 | 122.3145 | 122.2824 | -122.4838 | -122.3785 | 122.3877 | 122.4792 | 60.6171 | 62.2513
781.0625 | 122.5021 | -62.114 | 60.3149 | 0.0025177 | -0.026547 | -0.0271 | 0.061594 | -0.032793 | -0.049954 | -0.040178 | 0.00094606 | -0.018613 | 0.0562 | 0.047971 | -0.21851 | -0.017273 | -0.024962 | -1.6388 | 60.2783 | -62.265 | 60.1639 | -61.9217 | -62.3978 | -62.3428 | 0.045776 | 60.228 | -62.1643 | 60.2783 | -62.0819 | -62.1918 | -62.1231 | -0.15106 | -0.036621 | -0.15106 | 0.19226 | -0.22888 | -0.28381 | -0.077819 | -0.13275 | -0.050354 | -0.086975 | -0.036621 | 0.032044 | -0.009155 | -0.077819 | 0.041199 | -0.027465 | 0.34332 | 122.4289 | 0.082398 | 122.4426 | 122.5433 | 122.3923 | 122.3923 | 122.3419 | -122.58 | -122.4792 | 122.2778 | 122.3923 | 60.4752 | 62.1597
782.875 | 122.5525 | -62.0911 | 60.2417 | -0.02037 | -0.02377 | -0.027741 | 0.063516 | -0.027239 | -0.049954 | -0.039965 | -0.0051575 | -0.017972 | 0.056627 | 0.043699 | -0.21723 | -0.015778 | -0.021117 | -1.6388 | 60.26 | -62.2421 | 60.2325 | -61.8713 | -62.352 | -62.3199 | 0.082397 | 60.2234 | -62.1323 | 60.3287 | -62.0316 | -62.1597 | -62.0773 | -0.15106 | 0.018311 | -0.009155 | 0.21973 | -0.22888 | -0.26093 | -0.07782 | -0.10986 | -0.041199 | -0.01831 | 0.086975 | 0.059509 | 0.013732 | -0.068665 | 0.054931 | -0.027466 | 0.37079 | 122.4747 | 0.10071 | 122.4609 | 122.5021 | 122.3557 | 122.3511 | 122.3145 | -122.4838 | -122.374 | 122.3236 | 122.4197 | 60.4523 | 62.1735
784.5938 | 122.6303 | -62.1185 | 60.2005 | -0.0051118 | -0.023129 | -0.024964 | 0.062448 | -0.028307 | -0.048672 | -0.040392 | 0.00094606 | -0.022031 | 0.054705 | 0.047758 | -0.21702 | -0.015992 | -0.01898 | -1.6891 | 60.2051 | -62.233 | 60.2325 | -61.8622 | -62.352 | -62.3062 | 0.041199 | 60.1501 | -62.1323 | 60.379 | -62.0087 | -62.1048 | -62.0224 | -0.11444 | 0.004578 | 0.032044 | 0.25635 | -0.18768 | -0.23346 | -0.073242 | -0.11902 | -0.013733 | -0.050354 | 0.17853 | 0.10986 | 0.09613 | 0.013733 | 0.10986 | 0.027466 | 0.37079 | 122.4655 | 0.1236 | 122.5113 | 122.438 | 122.2824 | 122.3236 | 122.2687 | -122.4335 | -122.3328 | 122.3511 | 122.4976 | 60.4294 | 62.1597
786.375 | 122.6578 | -62.0911 | 60.2417 | -0.0051118 | -0.027615 | -0.025177 | 0.061594 | -0.032366 | -0.048886 | -0.03911 | -0.0021057 | -0.021817 | 0.054705 | 0.045194 | -0.21531 | -0.016205 | -0.019194 | -1.7715 | 60.2051 | -62.2559 | 60.26 | -61.8256 | -62.3062 | -62.2604 | 0.10529 | 60.1959 | -62.1368 | 60.3836 | -61.972 | -62.059 | -62.0041 | -0.16479 | -0.036621 | 0.018311 | 0.2655 | -0.16937 | -0.21515 | -0.004578 | -0.050354 | -0.045777 | -0.045776 | 0.14191 | 0.11902 | 0.086975 | 0.032043 | 0.13275 | 0.07782 | 0.4303 | 122.5159 | 0.16479 | 122.5204 | 122.4609 | 122.3328 | 122.2961 | 122.287 | -122.4976 | -122.3785 | 122.3511 | 122.4747 | 60.3195 | 62.1964
788.1562 | 122.5433 | -62.1048 | 60.2829 | -0.0051118 | -0.023129 | -0.026032 | 0.064371 | -0.027239 | -0.050167 | -0.039751 | -0.0021057 | -0.019254 | 0.056627 | 0.045194 | -0.21744 | -0.013428 | -0.022826 | -1.8219 | 60.2783 | -62.2238 | 60.2142 | -61.8896 | -62.3703 | -62.3245 | 0.050354 | 60.2142 | -62.1597 | 60.3058 | -62.0773 | -62.1826 | -62.0911 | -0.11902 | -0.004578 | -0.068665 | 0.21515 | -0.21973 | -0.2655 | -0.10071 | -0.14648 | -0.054932 | -0.068665 | 0.022888 | 0.027465 | 0.013733 | -0.07782 | 0.068665 | -0.022888 | 0.33417 | 122.438 | 0.082397 | 122.4655 | 122.5021 | 122.374 | 122.3831 | 122.319 | -122.5067 | -122.4426 | 122.319 | 122.4106 | 60.2829 | 62.1552
789.875 | 122.6532 | -62.0636 | 60.2371 | -0.0051118 | -0.028897 | -0.026459 | 0.060953 | -0.032366 | -0.050381 | -0.040819 | -0.0021057 | -0.021176 | 0.055773 | 0.042417 | -0.21531 | -0.015565 | -0.019835 | -1.8997 | 60.2417 | -62.2284 | 60.2463 | -61.8393 | -62.2971 | -62.2696 | 0.11902 | 60.1776 | -62.1323 | 60.3745 | -61.9537 | -62.0544 | -61.9995 | -0.16479 | 0.004577 | 0.009155 | 0.22431 | -0.20599 | -0.23346 | -0.041198 | -0.068664 | -0.068664 | -0.05951 | 0.13733 | 0.10986 | 0.064087 | 0.009156 | 0.13275 | 0.07782 | 0.3891 | 122.4747 | 0.17853 | 122.5067 | 122.4701 | 122.3099 | 122.3053 | 122.2412 | -122.4655 | -122.3694 | 122.3099 | 122.4381 | 60.1639 | 62.1826
791.6562 | 122.6028 | -62.0773 | 60.2554 | 0.0025177 | -0.026333 | -0.023682 | 0.062235 | -0.032366 | -0.051235 | -0.039537 | 0.00094606 | -0.020749 | 0.055132 | 0.041563 | -0.21616 | -0.016633 | -0.02133 | -2.1286 | 60.2371 | -62.2513 | 60.2051 | -61.8896 | -62.3566 | -62.3108 | 0.009155 | 60.1639 | -62.146 | 60.3195 | -62.0453 | -62.1323 | -62.0499 | -0.17395 | -0.01831 | -0.050354 | 0.18768 | -0.23346 | -0.27923 | -0.059509 | -0.10528 | -0.068664 | -0.091553 | 0.064087 | 0.032044 | 0.027466 | -0.054931 | 0.09613 | 0.013733 | 0.36163 | 122.4564 | 0.10071 | 122.4655 | 122.4884 | 122.3099 | 122.3145 | 122.2412 | -122.5067 | -122.4014 | 122.2824 | 122.3969 | 59.9487 | 62.0865
793.4375 | 122.6486 | -62.0865 | 60.2142 | -0.012741 | -0.025051 | -0.024109 | 0.063303 | -0.029162 | -0.047604 | -0.039751 | 0.00094606 | -0.021176 | 0.056627 | 0.04199 | -0.2183 | -0.01706 | -0.022826 | -2.1881 | 60.228 | -62.2009 | 60.2646 | -61.8256 | -62.3245 | -62.2742 | 0.059509 | 60.1776 | -62.1368 | 60.3836 | -61.9904 | -62.1002 | -61.9904 | -0.11444 | 0.013733 | 0.050354 | 0.26093 | -0.18768 | -0.23804 | -0.073242 | -0.1236 | -0.050354 | -0.036621 | 0.16937 | 0.096131 | 0.096131 | -0.013733 | 0.14648 | 0.036621 | 0.37537 | 122.4655 | 0.14648 | 122.5204 | 122.4289 | 122.3145 | 122.3145 | 122.2641 | -122.4152 | -122.3511 | 122.3511 | 122.4701 | 59.8984 | 62.146
795.1562 | 122.6349 | -62.0728 | 60.228 | 0.0025177 | -0.022702 | -0.022614 | 0.066934 | -0.029162 | -0.049099 | -0.038896 | -0.0021057 | -0.020108 | 0.056414 | 0.043272 | -0.21552 | -0.015137 | -0.019621 | -2.2385 | 60.2737 | -62.2467 | 60.2188 | -61.8851 | -62.3703 | -62.3337 | -0.009155 | 60.1685 | -62.1643 | 60.3836 | -61.9949 | -62.114 | -61.9949 | -0.17395 | 0.045777 | -0.009155 | 0.18768 | -0.26092 | -0.29755 | -0.086975 | -0.1236 | -0.091553 | -0.059509 | 0.15564 | 0.07782 | 0.07782 | -0.041199 | 0.16937 | 0.050354 | 0.36163 | 122.4655 | 0.16937 | 122.5479 | 122.5204 | 122.3328 | 122.3465 | 122.2412 | -122.4747 | -122.3923 | 122.2916 | 122.4564 | 59.8343 | 62.0636
796.9375 | 122.5616 | -62.0453 | 60.3241 | 0.0025177 | -0.026974 | -0.025391 | 0.066721 | -0.029589 | -0.04739 | -0.039965 | 0.00094606 | -0.018827 | 0.0562 | 0.043485 | -0.2168 | -0.015992 | -0.020689 | -2.1881 | 60.3287 | -62.2238 | 60.2417 | -61.8713 | -62.3245 | -62.3199 | 0.064087 | 60.2371 | -62.114 | 60.3607 | -62.0041 | -62.1323 | -62.0453 | -0.17853 | 0.004577 | -0.082398 | 0.17395 | -0.27466 | -0.27924 | -0.09613 | -0.10071 | -0.068665 | -0.086975 | 0.036621 | 0.041199 | 0 | -0.086975 | 0.068665 | -0.01831 | 0.35248 | 122.4655 | 0.10986 | 122.4747 | 122.5525 | 122.3511 | 122.374 | 122.2824 | -122.5479 | -122.4381 | 122.287 | 122.406 | 59.8572 | 62.1094
798.6719 | 122.5525 | -62.0911 | 60.2829 | -0.0051118 | -0.025479 | -0.022828 | 0.066507 | -0.026384 | -0.049954 | -0.041033 | 0.0039979 | -0.020108 | 0.056414 | 0.052671 | -0.21488 | -0.015137 | -0.02838 | -2.211 | 60.3058 | -62.1826 | 60.2234 | -61.8622 | -62.3337 | -62.3016 | 0.036621 | 60.26 | -62.1185 | 60.3424 | -62.0361 | -62.1643 | -62.0636 | -0.091553 | 0.022888 | -0.059509 | 0.22888 | -0.21057 | -0.24261 | -0.11902 | -0.15106 | -0.027466 | -0.022888 | 0.059509 | 0.054931 | 0.027465 | -0.073243 | 0.054931 | -0.045777 | 0.32043 | 122.406 | 0.082397 | 122.4609 | 122.4884 | 122.3785 | 122.3969 | 122.3511 | -122.4655 | -122.4014 | 122.3145 | 122.4335 | 59.8801 | 62.1277
800.4688 | 122.6074 | -62.1002 | 60.2875 | -0.0051118 | -0.029324 | -0.026032 | 0.061594 | -0.034289 | -0.051235 | -0.038683 | -0.0051575 | -0.020536 | 0.056627 | 0.047117 | -0.21296 | -0.016846 | -0.020903 | -2.2797 | 60.2325 | -62.1826 | 60.3104 | -61.7706 | -62.233 | -62.2147 | 0.14191 | 60.228 | -62.1094 | 60.3836 | -61.9446 | -62.0453 | -61.9995 | -0.082397 | -0.054932 | 0.022888 | 0.32959 | -0.11444 | -0.13275 | -0.032044 | -0.050354 | -0.009155 | -0.05951 | 0.09613 | 0.15564 | 0.10071 | 0.054932 | 0.10986 | 0.064087 | 0.41199 | 122.493 | 0.16479 | 122.493 | 122.4152 | 122.3373 | 122.3328 | 122.3282 | -122.4701 | -122.3969 | 122.4106 | 122.4838 | 59.8206 | 62.2421
802.1875 | 122.6028 | -62.0773 | 60.2554 | -0.0051118 | -0.025906 | -0.023469 | 0.066721 | -0.032793 | -0.050167 | -0.040605 | 0.00094606 | -0.019681 | 0.057909 | 0.044767 | -0.21744 | -0.016419 | -0.017271 | -2.4582 | 60.26 | -62.2421 | 60.1868 | -61.9125 | -62.384 | -62.3383 | -0.054932 | 60.2051 | -62.1323 | 60.3745 | -62.0224 | -62.1231 | -62.027 | -0.16479 | 0.004578 | -0.068664 | 0.16479 | -0.26093 | -0.3067 | -0.096131 | -0.14191 | -0.054931 | -0.050354 | 0.11902 | 0.054932 | 0.050354 | -0.045776 | 0.10529 | 0.009155 | 0.32959 | 122.4289 | 0.10986 | 122.5067 | 122.5021 | 122.3373 | 122.3373 | 122.2824 | -122.4976 | -122.3877 | 122.2641 | 122.4518 | 59.6191 | 62.0224
803.9688 | 122.5204 | -62.0911 | 60.3333 | 0.010147 | -0.028897 | -0.028168 | 0.061167 | -0.033861 | -0.049099 | -0.042742 | -0.0021057 | -0.020963 | 0.0562 | 0.050107 | -0.21616 | -0.018342 | -0.022612 | -2.3621 | 60.2829 | -62.1918 | 60.2829 | -61.8027 | -62.2696 | -62.2375 | 0.091553 | 60.2783 | -62.0865 | 60.347 | -62.0178 | -62.1231 | -62.0544 | -0.10071 | -0.050354 | -0.050354 | 0.28839 | -0.14648 | -0.17853 | -0.045777 | -0.07782 | 0.004577 | -0.054932 | 0.013733 | 0.073242 | 0.036621 | -0.032044 | 0.032044 | -0.036621 | 0.3891 | 122.4747 | 0.068665 | 122.4335 | 122.4747 | 122.3648 | 122.374 | 122.3694 | -122.525 | -122.4197 | 122.374 | 122.438 | 59.729 | 62.1826
805.7656 | 122.5983 | -62.0499 | 60.2783 | -0.0051118 | -0.027188 | -0.023896 | 0.062021 | -0.029162 | -0.051449 | -0.037187 | -0.0021057 | -0.022031 | 0.054918 | 0.045408 | -0.21637 | -0.01706 | -0.021758 | -2.4857 | 60.2783 | -62.2009 | 60.228 | -61.8439 | -62.3108 | -62.265 | 0 | 60.2142 | -62.1094 | 60.3561 | -61.9812 | -62.0865 | -62.0132 | -0.15106 | 0 | -0.050354 | 0.20599 | -0.21515 | -0.26093 | -0.064087 | -0.10986 | -0.059509 | -0.064087 | 0.07782 | 0.068665 | 0.036621 | -0.036621 | 0.09613 | 0.022888 | 0.35706 | 122.4289 | 0.12817 | 122.4655 | 122.4792 | 122.3236 | 122.3282 | 122.2641 | -122.4792 | -122.3877 | 122.2778 | 122.406 | 59.5642 | 62.0499
807.5781 | 122.6669 | -62.0224 | 60.2921 | -0.0051118 | -0.027615 | -0.0271 | 0.063303 | -0.029589 | -0.052517 | -0.03911 | -0.0051575 | -0.020749 | 0.053636 | 0.042631 | -0.21659 | -0.016205 | -0.026244 | -2.449 | 60.2463 | -62.1826 | 60.3287 | -61.734 | -62.2192 | -62.178 | 0.15106 | 60.228 | -62.0865 | 60.4385 | -61.8896 | -61.9812 | -61.94 | -0.16022 | -0.045776 | 0.036621 | 0.28839 | -0.15564 | -0.19684 | 0.004577 | -0.036621 | -0.064087 | -0.064087 | 0.14648 | 0.13275 | 0.082398 | 0.041199 | 0.14648 | 0.10529 | 0.44861 | 122.5113 | 0.19684 | 122.525 | 122.4289 | 122.3145 | 122.2687 | 122.2504 | -122.4747 | -122.3785 | 122.3511 | 122.4609 | 59.5734 | 62.1735
809.2812 | 122.5571 | -62.0224 | 60.347 | -0.0051118 | -0.027188 | -0.025818 | 0.066721 | -0.03258 | -0.050167 | -0.042101 | 0.00094606 | -0.01904 | 0.057909 | 0.047117 | -0.21744 | -0.014496 | -0.021971 | -2.4811 | 60.347 | -62.1826 | 60.2509 | -61.8439 | -62.2925 | -62.2742 | 0.045776 | 60.3195 | -62.0819 | 60.3653 | -61.972 | -62.114 | -62.0041 | -0.16022 | 0 | -0.096131 | 0.17853 | -0.25177 | -0.27008 | -0.091553 | -0.10986 | -0.059509 | -0.027466 | 0.01831 | 0.050354 | 0.018311 | -0.091553 | 0.07782 | -0.032044 | 0.33875 | 122.4335 | 0.10986 | 122.4472 | 122.5296 | 122.4014 | 122.3694 | 122.3419 | -122.5296 | -122.4289 | 122.2733 | 122.3877 | 59.5413 | 62.0682
811.0625 | 122.4884 | -62.0361 | 60.3424 | 0.0025177 | -0.022488 | -0.02176 | 0.06608 | -0.029375 | -0.050595 | -0.038683 | -0.0021057 | -0.019254 | 0.055986 | 0.040281 | -0.21787 | -0.017701 | -0.019835 | -2.6047 | 60.347 | -62.1643 | 60.2142 | -61.8896 | -62.3795 | -62.3383 | -0.086975 | 60.3333 | -62.1094 | 60.3241 | -62.0544 | -62.1872 | -62.0682 | -0.12817 | 0.004578 | -0.12817 | 0.14648 | -0.30212 | -0.34332 | -0.17395 | -0.21515 | -0.073242 | -0.009155 | -0.01831 | -0.01831 | -0.032043 | -0.15106 | 0.041199 | -0.07782 | 0.27466 | 122.3785 | 0.054932 | 122.4335 | 122.5113 | 122.4426 | 122.3831 | 122.3694 | -122.5067 | -122.4518 | 122.2504 | 122.3602 | 59.4315 | 61.9492
812.875 | 122.5937 | -62.0316 | 60.2692 | -0.0051118 | -0.022702 | -0.022614 | 0.061594 | -0.035143 | -0.049313 | -0.041887 | -0.0021057 | -0.021176 | 0.055986 | 0.052457 | -0.21573 | -0.015565 | -0.022398 | -2.5681 | 60.2921 | -62.1643 | 60.3149 | -61.734 | -62.2604 | -62.2055 | 0.036621 | 60.2325 | -62.0728 | 60.4248 | -61.9675 | -62.0682 | -61.9675 | -0.13275 | 0.022888 | 0.045776 | 0.29755 | -0.17395 | -0.22888 | -0.041198 | -0.09613 | -0.041199 | -0.036621 | 0.15564 | 0.064087 | 0.064087 | -0.036621 | 0.10529 | 0.004578 | 0.4303 | 122.4792 | 0.10529 | 122.4976 | 122.4564 | 122.3053 | 122.3236 | 122.2641 | -122.4335 | -122.3419 | 122.3465 | 122.4564 | 59.4635 | 62.0682
814.6562 | 122.5388 | -62.0224 | 60.3882 | 0.010147 | -0.02676 | -0.025818 | 0.064157 | -0.033434 | -0.046749 | -0.037401 | 0.0039979 | -0.020963 | 0.057909 | 0.042203 | -0.21595 | -0.016633 | -0.024962 | -2.4811 | 60.3424 | -62.1597 | 60.3058 | -61.7706 | -62.2238 | -62.2147 | 0.064087 | 60.2921 | -62.0636 | 60.3699 | -61.9766 | -62.0819 | -62.0178 | -0.13733 | -0.045777 | -0.082398 | 0.25177 | -0.19226 | -0.20142 | -0.054932 | -0.064087 | -0.041199 | -0.096131 | -0.018311 | 0.045776 | 0.004578 | -0.059509 | 0.045777 | -0.01831 | 0.3891 | 122.4655 | 0.086975 | 122.4335 | 122.5021 | 122.3557 | 122.3648 | 122.3145 | -122.5479 | -122.4518 | 122.3282 | 122.3923 | 59.5413 | 62.0865
816.4531 | 122.6212 | -62.027 | 60.3058 | 0.010147 | -0.026974 | -0.025177 | 0.062448 | -0.033434 | -0.051876 | -0.04146 | -0.0021057 | -0.022031 | 0.055986 | 0.042417 | -0.21467 | -0.014924 | -0.021971 | -2.9251 | 60.2966 | -62.146 | 60.2875 | -61.7844 | -62.265 | -62.2147 | 0.045776 | 60.2509 | -62.0728 | 60.4294 | -61.9217 | -62.0087 | -61.9537 | -0.11902 | -0.009155 | -0.01831 | 0.24262 | -0.18768 | -0.23804 | -0.068665 | -0.11902 | -0.045776 | -0.054932 | 0.1236 | 0.10529 | 0.073243 | 0.018311 | 0.11902 | 0.064087 | 0.36163 | 122.4335 | 0.15106 | 122.5021 | 122.4426 | 122.3236 | 122.3236 | 122.2778 | -122.4518 | -122.3785 | 122.3145 | 122.4564 | 59.1019 | 62.0728
818.2344 | 122.5433 | -62.0178 | 60.3516 | 0.017777 | -0.024838 | -0.025818 | 0.065653 | -0.029589 | -0.050167 | -0.040392 | 0.00094606 | -0.019681 | 0.054064 | 0.051176 | -0.21787 | -0.015137 | -0.023894 | -3.2867 | 60.3928 | -62.1414 | 60.2325 | -61.8484 | -62.3474 | -62.2879 | -0.086975 | 60.3333 | -62.0636 | 60.3973 | -62.0178 | -62.1323 | -62.0178 | -0.1236 | 0.041199 | -0.11902 | 0.16937 | -0.27008 | -0.32959 | -0.14648 | -0.20599 | -0.045777 | -0.01831 | 0.045777 | 0 | 0 | -0.11444 | 0.045777 | -0.068664 | 0.29297 | 122.374 | 0.045777 | 122.4609 | 122.5342 | 122.3969 | 122.4106 | 122.3511 | -122.493 | -122.4152 | 122.2504 | 122.4152 | 58.7311 | 61.9308
819.9375 | 122.5891 | -61.9949 | 60.3653 | -0.0051118 | -0.027401 | -0.024323 | 0.062021 | -0.032366 | -0.050167 | -0.037615 | -0.0051575 | -0.021604 | 0.056627 | 0.04498 | -0.21915 | -0.015351 | -0.023894 | -3.4607 | 60.3424 | -62.1231 | 60.3058 | -61.7477 | -62.233 | -62.1826 | 0.004578 | 60.3058 | -62.0453 | 60.4568 | -61.9034 | -61.9858 | -61.9263 | -0.12817 | -0.022888 | -0.059509 | 0.24719 | -0.18768 | -0.23804 | -0.059509 | -0.10986 | -0.050354 | -0.059509 | 0.091553 | 0.091553 | 0.068664 | 0.009155 | 0.11902 | 0.059509 | 0.37537 | 122.4289 | 0.14191 | 122.5021 | 122.4655 | 122.3511 | 122.3373 | 122.3007 | -122.4884 | -122.4106 | 122.3007 | 122.4518 | 58.5342 | 61.9995
821.7344 | 122.6349 | -61.9492 | 60.3561 | -0.0051118 | -0.026333 | -0.024964 | 0.064798 | -0.029802 | -0.04739 | -0.03911 | 0.00094606 | -0.020108 | 0.056627 | 0.046476 | -0.21872 | -0.014069 | -0.025176 | -4.2206 | 60.3561 | -62.1048 | 60.3882 | -61.6837 | -62.1735 | -62.1643 | 0.036621 | 60.2783 | -62.0132 | 60.5255 | -61.8713 | -61.9766 | -61.8805 | -0.15564 | 0 | 0.032044 | 0.2655 | -0.21515 | -0.2243 | -0.05951 | -0.068665 | -0.064087 | -0.07782 | 0.16937 | 0.07782 | 0.068665 | -0.027466 | 0.13275 | 0.036621 | 0.42114 | 122.493 | 0.14191 | 122.5388 | 122.4609 | 122.2916 | 122.3053 | 122.2275 | -122.4609 | -122.3694 | 122.3373 | 122.4747 | 57.7286 | 61.9858
823.4688 | 122.5525 | -61.9446 | 60.4431 | -0.012741 | -0.025479 | -0.024964 | 0.064157 | -0.032152 | -0.048886 | -0.040605 | -0.0021057 | -0.017331 | 0.054705 | 0.047544 | -0.21595 | -0.014924 | -0.020049 | -4.3167 | 60.4156 | -62.0911 | 60.3653 | -61.7249 | -62.2009 | -62.1872 | 0.068665 | 60.3699 | -61.9812 | 60.4797 | -61.8713 | -62.0178 | -61.9125 | -0.14648 | -0.027466 | -0.07782 | 0.21973 | -0.24262 | -0.25635 | -0.096131 | -0.10986 | -0.036621 | -0.073242 | 0.036621 | 0.073242 | 0.032043 | -0.073242 | 0.068664 | -0.036621 | 0.36621 | 122.4564 | 0.10986 | 122.4609 | 122.5067 | 122.3511 | 122.3602 | 122.3145 | -122.5342 | -122.4243 | 122.3099 | 122.4243 | 57.6279 | 62.0132
825.2344 | 122.6349 | -61.9308 | 60.3928 | -0.012741 | -0.025692 | -0.023255 | 0.062021 | -0.029589 | -0.049954 | -0.042101 | -0.0021057 | -0.021817 | 0.057482 | 0.049039 | -0.21488 | -0.014496 | -0.024107 | -4.7012 | 60.3928 | -62.0956 | 60.4019 | -61.6379 | -62.1231 | -62.0865 | 0.13275 | 60.3149 | -61.9858 | 60.5255 | -61.821 | -61.908 | -61.8439 | -0.16479 | 0 | 0.009156 | 0.29297 | -0.15564 | -0.19226 | 0.009155 | -0.027466 | -0.054932 | -0.07782 | 0.13275 | 0.10986 | 0.086975 | 0.022888 | 0.14191 | 0.07782 | 0.45776 | 122.4976 | 0.16479 | 122.5113 | 122.4884 | 122.3007 | 122.3236 | 122.2458 | -122.4884 | -122.3785 | 122.3328 | 122.4564 | 57.2296 | 62.0636
827.0312 | 122.5159 | -61.94 | 60.4614 | 0.010147 | -0.028256 | -0.026246 | 0.062235 | -0.031725 | -0.051876 | -0.040819 | -0.0021057 | -0.01904 | 0.056627 | 0.043058 | -0.21766 | -0.017487 | -0.024962 | -5.0583 | 60.4523 | -62.0865 | 60.347 | -61.7203 | -62.1872 | -62.1689 | 0.036621 | 60.4294 | -61.9766 | 60.434 | -61.9263 | -62.0224 | -61.9492 | -0.14648 | -0.009155 | -0.11444 | 0.21973 | -0.22888 | -0.24719 | -0.082397 | -0.10071 | -0.036622 | -0.032044 | -0.027466 | 0.013732 | -0.009156 | -0.082398 | 0.027466 | -0.045776 | 0.36621 | 122.4335 | 0.050354 | 122.4106 | 122.5388 | 122.406 | 122.3923 | 122.3694 | -122.5479 | -122.4381 | 122.287 | 122.374 | 56.8817 | 61.9766
828.75 | 122.5571 | -61.908 | 60.4294 | -0.02037 | -0.025692 | -0.023255 | 0.06373 | -0.031298 | -0.048886 | -0.042742 | -0.0021057 | -0.019681 | 0.054277 | 0.047117 | -0.2183 | -0.015778 | -0.023894 | -4.7928 | 60.4385 | -62.0865 | 60.3836 | -61.7157 | -62.1826 | -62.1689 | 0.064087 | 60.3973 | -61.972 | 60.498 | -61.8622 | -62.0041 | -61.9034 | -0.17853 | 0.009156 | -0.045776 | 0.19226 | -0.26093 | -0.27466 | -0.082397 | -0.09613 | -0.064087 | -0.032043 | 0.068665 | 0.045776 | 0.004578 | -0.09613 | 0.068665 | -0.032043 | 0.37079 | 122.4701 | 0.10986 | 122.4701 | 122.525 | 122.3694 | 122.3465 | 122.3053 | -122.5159 | -122.4014 | 122.2916 | 122.406 | 57.1152 | 61.972
830.5469 | 122.5708 | -61.9125 | 60.434 | 0.010147 | -0.023556 | -0.024109 | 0.065653 | -0.028521 | -0.050595 | -0.039537 | 0.00094606 | -0.018399 | 0.057054 | 0.046689 | -0.21702 | -0.015351 | -0.021117 | -4.7104 | 60.4431 | -62.0682 | 60.3836 | -61.6974 | -62.1643 | -62.146 | 0.091553 | 60.3836 | -61.9675 | 60.498 | -61.8576 | -61.9766 | -61.8851 | -0.15564 | 0.009155 | -0.050354 | 0.21515 | -0.23346 | -0.25177 | -0.07782 | -0.096131 | -0.054931 | -0.050354 | 0.064087 | 0.054932 | 0.027466 | -0.064087 | 0.082397 | -0.009156 | 0.37079 | 122.4518 | 0.10986 | 122.4655 | 122.5113 | 122.3511 | 122.3557 | 122.2961 | -122.5021 | -122.4014 | 122.2961 | 122.4106 | 57.2021 | 62.0041
832.2656 | 122.5891 | -61.9217 | 60.3928 | 0.0025177 | -0.026547 | -0.025177 | 0.063303 | -0.02788 | -0.049526 | -0.041674 | -0.0021057 | -0.021817 | 0.056627 | 0.04199 | -0.21381 | -0.015992 | -0.023894 | -4.7241 | 60.4248 | -62.0773 | 60.3653 | -61.6974 | -62.1735 | -62.146 | -0.022888 | 60.3333 | -61.9904 | 60.4843 | -61.8576 | -61.9629 | -61.8713 | -0.15564 | 0.032044 | -0.027466 | 0.2243 | -0.2243 | -0.25177 | -0.068664 | -0.09613 | -0.068664 | -0.059509 | 0.091553 | 0.064087 | 0.050354 | -0.041199 | 0.11902 | 0.027465 | 0.37994 | 122.4426 | 0.13275 | 122.4747 | 122.5021 | 122.3236 | 122.3465 | 122.2549 | -122.4701 | -122.3831 | 122.287 | 122.406 | 57.1976 | 61.8988
834.0625 | 122.58 | -61.9263 | 60.434 | -0.012741 | -0.024411 | -0.024964 | 0.066721 | -0.026171 | -0.046322 | -0.039965 | 0.00094606 | -0.017545 | 0.057909 | 0.049894 | -0.21616 | -0.015565 | -0.023039 | -4.6967 | 60.4752 | -62.0728 | 60.3333 | -61.7386 | -62.233 | -62.1918 | -0.064087 | 60.3973 | -61.972 | 60.4935 | -61.8942 | -62.0224 | -61.8942 | -0.14648 | 0.041199 | -0.10071 | 0.18768 | -0.2655 | -0.3067 | -0.11902 | -0.16022 | -0.045776 | -0.036621 | 0.059509 | 0.032044 | 0.032044 | -0.09613 | 0.07782 | -0.050354 | 0.33417 | 122.406 | 0.07782 | 122.4655 | 122.5479 | 122.3694 | 122.4014 | 122.3236 | -122.5067 | -122.406 | 122.2595 | 122.4197 | 57.2296 | 61.8622
835.7812 | 122.5616 | -61.8851 | 60.4752 | 0.0025177 | -0.02612 | -0.026459 | 0.063944 | -0.029802 | -0.048458 | -0.039965 | 0.00094606 | -0.018399 | 0.054491 | 0.050962 | -0.21637 | -0.01471 | -0.028594 | -4.7974 | 60.5026 | -62.0361 | 60.4065 | -61.6425 | -62.146 | -62.1094 | 0.082397 | 60.4294 | -61.9308 | 60.5392 | -61.8301 | -61.9446 | -61.853 | -0.15106 | 0.027466 | -0.068665 | 0.24262 | -0.2243 | -0.26092 | -0.073242 | -0.10986 | -0.045776 | -0.045777 | 0.064087 | 0.054932 | 0.032044 | -0.059509 | 0.07782 | -0.013733 | 0.39368 | 122.4426 | 0.10071 | 122.4701 | 122.5388 | 122.3602 | 122.3877 | 122.3145 | -122.5113 | -122.406 | 122.2916 | 122.4243 | 57.0877 | 61.9675
837.5781 | 122.5891 | -61.9034 | 60.4111 | -0.012741 | -0.027188 | -0.025177 | 0.060953 | -0.029802 | -0.050167 | -0.042742 | -0.0021057 | -0.021176 | 0.052355 | 0.041563 | -0.21232 | -0.016633 | -0.019621 | -4.8706 | 60.4202 | -62.0499 | 60.4156 | -61.6241 | -62.1552 | -62.0911 | 0.041199 | 60.3561 | -61.9629 | 60.5255 | -61.8301 | -61.9308 | -61.8576 | -0.14648 | 0.009155 | 0.004577 | 0.27923 | -0.18768 | -0.25177 | -0.041198 | -0.10528 | -0.05951 | -0.054932 | 0.11444 | 0.073242 | 0.045776 | -0.027466 | 0.10529 | 0.032044 | 0.42572 | 122.4655 | 0.13275 | 122.4884 | 122.4701 | 122.319 | 122.3236 | 122.2595 | -122.4609 | -122.374 | 122.319 | 122.4289 | 57.0328 | 61.9446
839.2969 | 122.5983 | -61.908 | 60.4523 | 0.0025177 | -0.024411 | -0.025391 | 0.064585 | -0.031084 | -0.048672 | -0.039965 | 0.00094606 | -0.018613 | 0.055559 | 0.051816 | -0.21808 | -0.013642 | -0.022612 | -5.072 | 60.498 | -62.0316 | 60.3699 | -61.6928 | -62.1964 | -62.1506 | -0.050354 | 60.3882 | -61.9492 | 60.5392 | -61.8347 | -61.9537 | -61.8393 | -0.1236 | 0.045776 | -0.082398 | 0.21515 | -0.24262 | -0.28839 | -0.11902 | -0.1648 | -0.041199 | -0.064087 | 0.086975 | 0.073242 | 0.068665 | -0.045776 | 0.10986 | -0.004577 | 0.33874 | 122.4014 | 0.11444 | 122.4884 | 122.5296 | 122.3373 | 122.406 | 122.2961 | -122.4838 | -122.4014 | 122.2778 | 122.4472 | 56.8359 | 61.8576
841.0781 | 122.5937 | -61.8896 | 60.4431 | -0.0051118 | -0.025051 | -0.024537 | 0.06373 | -0.030657 | -0.04974 | -0.042101 | -0.0051575 | -0.020749 | 0.054918 | 0.046476 | -0.21573 | -0.016846 | -0.023894 | -5.0446 | 60.4248 | -62.0132 | 60.4477 | -61.5967 | -62.1185 | -62.0773 | 0.032043 | 60.3745 | -61.9354 | 60.5576 | -61.8118 | -61.9034 | -61.8301 | -0.1236 | -0.01831 | 0.004578 | 0.29297 | -0.18768 | -0.22888 | -0.064087 | -0.10529 | -0.045777 | -0.068664 | 0.11444 | 0.077819 | 0.059509 | -0.013733 | 0.10529 | 0.032044 | 0.41656 | 122.4609 | 0.1236 | 122.493 | 122.4381 | 122.3099 | 122.3145 | 122.2641 | -122.4564 | -122.3785 | 122.3373 | 122.4472 | 56.8451 | 61.9217
842.875 | 122.6303 | -61.8301 | 60.4797 | 0.0025177 | -0.024411 | -0.024323 | 0.063944 | -0.02788 | -0.048672 | -0.03676 | 0.00094606 | -0.018186 | 0.0562 | 0.048398 | -0.21851 | -0.013215 | -0.023467 | -4.7745 | 60.5026 | -61.9858 | 60.466 | -61.5967 | -62.0911 | -62.059 | 0.022888 | 60.4248 | -61.8896 | 60.6308 | -61.7523 | -61.8713 | -61.7569 | -0.15564 | 0.022889 | -0.013733 | 0.23346 | -0.22888 | -0.26093 | -0.073242 | -0.10529 | -0.059509 | -0.054931 | 0.15106 | 0.07782 | 0.073242 | -0.041199 | 0.13275 | 0.01831 | 0.3891 | 122.4518 | 0.13733 | 122.5204 | 122.4884 | 122.3145 | 122.3328 | 122.2549 | -122.4655 | -122.3694 | 122.2961 | 122.4609 | 57.0557 | 61.853
844.6719 | 122.58 | -61.8484 | 60.5118 | 0.0025177 | -0.02612 | -0.024537 | 0.061808 | -0.029802 | -0.049526 | -0.042101 | -0.0051575 | -0.021176 | 0.057054 | 0.037504 | -0.2168 | -0.01706 | -0.021971 | -4.6005 | 60.4797 | -61.9766 | 60.4477 | -61.6058 | -62.0911 | -62.0544 | -0.018311 | 60.4431 | -61.8988 | 60.5713 | -61.7844 | -61.8805 | -61.7935 | -0.12817 | -0.032044 | -0.064087 | 0.24262 | -0.20599 | -0.24261 | -0.077819 | -0.11444 | -0.050354 | -0.068665 | 0.059509 | 0.064087 | 0.054932 | -0.032043 | 0.10529 | 0.018311 | 0.37079 | 122.4243 | 0.11444 | 122.4701 | 122.4564 | 122.3419 | 122.3282 | 122.2916 | -122.4884 | -122.4106 | 122.2961 | 122.4197 | 57.2479 | 61.8301
846.4688 | 122.6028 | -61.8118 | 60.5301 | -0.0051118 | -0.023556 | -0.025605 | 0.06373 | -0.031084 | -0.050595 | -0.038042 | -0.0021057 | -0.020963 | 0.057054 | 0.044767 | -0.21915 | -0.016205 | -0.023894 | -4.2023 | 60.498 | -61.972 | 60.5118 | -61.5143 | -62.059 | -62.0041 | 0.022888 | 60.4523 | -61.8576 | 60.6125 | -61.7523 | -61.853 | -61.7569 | -0.16022 | -0.032043 | -0.01831 | 0.29755 | -0.19226 | -0.24719 | -0.032043 | -0.086975 | -0.045776 | -0.077819 | 0.082398 | 0.05951 | 0.054932 | -0.041198 | 0.10071 | 0.004578 | 0.45776 | 122.4838 | 0.10529 | 122.4701 | 122.4701 | 122.3099 | 122.3099 | 122.2641 | -122.5021 | -122.3877 | 122.3236 | 122.4243 | 57.6096 | 61.8347
848.1875 | 122.5983 | -61.7844 | 60.5209 | 0.0025177 | -0.026547 | -0.024323 | 0.06373 | -0.031511 | -0.04974 | -0.039324 | -0.0021057 | -0.019895 | 0.056627 | 0.049894 | -0.2168 | -0.017701 | -0.020903 | -4.5959 | 60.5255 | -61.9308 | 60.5118 | -61.4868 | -62.0499 | -61.9949 | 0.022888 | 60.4614 | -61.8393 | 60.64 | -61.7432 | -61.8256 | -61.7523 | -0.14648 | 0.004578 | -0.009155 | 0.29755 | -0.21057 | -0.2655 | -0.064087 | -0.11902 | -0.054931 | -0.059509 | 0.11902 | 0.041199 | 0.032044 | -0.041199 | 0.086975 | 0.013732 | 0.44403 | 122.4426 | 0.09613 | 122.4792 | 122.4564 | 122.3007 | 122.3099 | 122.2458 | -122.4518 | -122.3602 | 122.2961 | 122.4243 | 57.1884 | 61.8073
849.9688 | 122.4884 | -61.7889 | 60.5988 | -0.012741 | -0.02377 | -0.024964 | 0.068216 | -0.031511 | -0.048886 | -0.038256 | 0.00094606 | -0.017758 | 0.056414 | 0.049894 | -0.21766 | -0.016419 | -0.022612 | -4.6875 | 60.6262 | -61.9308 | 60.4568 | -61.6333 | -62.1368 | -62.0911 | -0.07782 | 60.5484 | -61.8439 | 60.5942 | -61.8073 | -61.908 | -61.7889 | -0.14191 | 0.027466 | -0.14191 | 0.15564 | -0.30212 | -0.3479 | -0.16022 | -0.20599 | -0.054932 | -0.050354 | -0.004578 | -0.018311 | 0 | -0.11902 | 0.054932 | -0.064087 | 0.29755 | 122.3877 | 0.036621 | 122.438 | 122.5571 | 122.3923 | 122.4152 | 122.3373 | -122.5296 | -122.4426 | 122.2458 | 122.3831 | 57.1014 | 61.7111
851.75 | 122.5479 | -61.7477 | 60.6171 | -0.012741 | -0.024197 | -0.023255 | 0.065225 | -0.031298 | -0.048886 | -0.038683 | 0.0039979 | -0.022031 | 0.056627 | 0.04434 | -0.21787 | -0.016419 | -0.022826 | -4.5822 | 60.64 | -61.8851 | 60.5621 | -61.4685 | -61.9812 | -61.9766 | 0.073242 | 60.5759 | -61.7889 | 60.6766 | -61.6837 | -61.8027 | -61.7157 | -0.13733 | 0.022889 | -0.054931 | 0.27924 | -0.22888 | -0.23346 | -0.091553 | -0.09613 | -0.041198 | -0.041198 | 0.05951 | 0.064087 | 0.032044 | -0.054931 | 0.073242 | -0.013733 | 0.41657 | 122.4472 | 0.10528 | 122.4655 | 122.525 | 122.3648 | 122.3877 | 122.3236 | -122.5021 | -122.406 | 122.3099 | 122.4243 | 57.1655 | 61.821
853.5312 | 122.5616 | -61.7523 | 60.6445 | 0.010147 | -0.025906 | -0.026246 | 0.065225 | -0.031725 | -0.048886 | -0.040605 | 0.00094606 | -0.01904 | 0.056841 | 0.045621 | -0.21616 | -0.014069 | -0.020476 | -4.2938 | 60.6491 | -61.908 | 60.5713 | -61.4685 | -61.9766 | -61.9583 | 0.059509 | 60.5896 | -61.7889 | 60.6857 | -61.6653 | -61.7935 | -61.7065 | -0.15564 | 0.004578 | -0.073242 | 0.28381 | -0.20599 | -0.22431 | -0.050354 | -0.068665 | -0.036621 | -0.054931 | 0.041199 | 0.086975 | 0.045776 | -0.041199 | 0.082397 | -0.004578 | 0.43945 | 122.4792 | 0.1236 | 122.4747 | 122.5571 | 122.3785 | 122.4014 | 122.3419 | -122.5525 | -122.4335 | 122.3236 | 122.438 | 57.4585 | 61.8118
855.3125 | 122.5342 | -61.7294 | 60.6445 | -0.0051118 | -0.023129 | -0.022828 | 0.065866 | -0.030443 | -0.051022 | -0.037828 | 0.00094606 | -0.017972 | 0.058336 | 0.049894 | -0.21723 | -0.013856 | -0.024321 | -4.2297 | 60.6628 | -61.8393 | 60.585 | -61.4639 | -61.972 | -61.9354 | 0.054932 | 60.5759 | -61.7752 | 60.6812 | -61.6837 | -61.7889 | -61.6928 | -0.10986 | 0.018311 | -0.059509 | 0.2655 | -0.20599 | -0.24262 | -0.096131 | -0.13275 | -0.045777 | -0.068664 | 0.036621 | 0.045776 | 0.036621 | -0.059509 | 0.082398 | -0.013732 | 0.37537 | 122.4243 | 0.091553 | 122.4564 | 122.5021 | 122.3511 | 122.3923 | 122.3053 | -122.4838 | -122.4197 | 122.3145 | 122.4106 | 57.4997 | 61.7844
857.0938 | 122.6257 | -61.7249 | 60.5804 | -0.0051118 | -0.022702 | -0.024109 | 0.060953 | -0.026171 | -0.047817 | -0.039324 | 0.0039979 | -0.020963 | 0.054491 | 0.042417 | -0.21616 | -0.015137 | -0.020903 | -4.6005 | 60.5942 | -61.8759 | 60.6125 | -61.4044 | -61.9308 | -61.9125 | 0.036621 | 60.5164 | -61.7752 | 60.7452 | -61.6196 | -61.7294 | -61.6287 | -0.15106 | 0.013733 | 0.032044 | 0.32044 | -0.18768 | -0.20599 | -0.036621 | -0.054931 | -0.050354 | -0.064087 | 0.16479 | 0.10529 | 0.096131 | -0.004577 | 0.14648 | 0.045777 | 0.4715 | 122.4884 | 0.15564 | 122.5204 | 122.4701 | 122.2916 | 122.319 | 122.2412 | -122.4564 | -122.3557 | 122.3373 | 122.4701 | 57.1243 | 61.7615
858.875 | 122.5113 | -61.7157 | 60.6995 | 0.0025177 | -0.024838 | -0.027527 | 0.064371 | -0.032793 | -0.050381 | -0.037187 | 0.00094606 | -0.022031 | 0.056841 | 0.046689 | -0.21744 | -0.017487 | -0.018126 | -4.6967 | 60.6903 | -61.8073 | 60.5438 | -61.4685 | -61.9354 | -61.94 | 0.013733 | 60.6354 | -61.7203 | 60.672 | -61.6699 | -61.7935 | -61.7157 | -0.091553 | -0.009155 | -0.15564 | 0.24719 | -0.2243 | -0.21973 | -0.13275 | -0.12817 | -0.004578 | -0.064087 | -0.027466 | 0.045776 | 0 | -0.07782 | 0.004578 | -0.073242 | 0.33875 | 122.3511 | 0.050354 | 122.3923 | 122.4976 | 122.3557 | 122.406 | 122.3511 | -122.5067 | -122.4197 | 122.2595 | 122.3877 | 57.019 | 61.7294
860.6719 | 122.6028 | -61.6837 | 60.6354 | 0.0025177 | -0.024411 | -0.023469 | 0.062662 | -0.032793 | -0.050381 | -0.039324 | -0.0021057 | -0.021604 | 0.055559 | 0.045194 | -0.21851 | -0.015778 | -0.025603 | -4.2343 | 60.6033 | -61.8622 | 60.6125 | -61.3953 | -61.94 | -61.908 | 0.027466 | 60.5438 | -61.7477 | 60.7224 | -61.6241 | -61.7249 | -61.6379 | -0.17853 | -0.032043 | -0.022888 | 0.28839 | -0.2243 | -0.25635 | -0.045776 | -0.077819 | -0.064087 | -0.091553 | 0.086975 | 0.059509 | 0.045777 | -0.041199 | 0.10986 | 0.022888 | 0.46692 | 122.4747 | 0.1236 | 122.4701 | 122.4655 | 122.2916 | 122.287 | 122.2275 | -122.4976 | -122.3831 | 122.2961 | 122.406 | 57.4493 | 61.7111
862.4531 | 122.5616 | -61.6699 | 60.704 | -0.0051118 | -0.023983 | -0.025605 | 0.065866 | -0.033861 | -0.048886 | -0.037401 | -0.0021057 | -0.016904 | 0.055345 | 0.049039 | -0.21808 | -0.015992 | -0.022185 | -4.7745 | 60.6949 | -61.8393 | 60.6354 | -61.3953 | -61.9171 | -61.908 | 0.086975 | 60.6308 | -61.7157 | 60.7407 | -61.6241 | -61.734 | -61.6379 | -0.16937 | -0.009156 | -0.068665 | 0.27466 | -0.23804 | -0.24719 | -0.068665 | -0.07782 | -0.045776 | -0.073243 | 0.036621 | 0.045776 | 0.032044 | -0.064087 | 0.07782 | -0.018311 | 0.44403 | 122.4747 | 0.091552 | 122.4564 | 122.5342 | 122.3465 | 122.3648 | 122.3007 | -122.5433 | -122.4197 | 122.3053 | 122.4106 | 56.8954 | 61.7569
864.1562 | 122.6349 | -61.6791 | 60.6491 | -0.012741 | -0.025692 | -0.023469 | 0.062021 | -0.031084 | -0.047817 | -0.040392 | -0.0051575 | -0.01904 | 0.058763 | 0.053739 | -0.21787 | -0.015778 | -0.021971 | -4.5364 | 60.6537 | -61.8027 | 60.6491 | -61.3403 | -61.8805 | -61.853 | 0.050354 | 60.5759 | -61.7523 | 60.7864 | -61.5784 | -61.6653 | -61.5875 | -0.1236 | 0.004578 | 0 | 0.33875 | -0.17395 | -0.20142 | -0.050354 | -0.07782 | -0.073242 | -0.073242 | 0.13733 | 0.10071 | 0.091553 | 0.013733 | 0.16479 | 0.086975 | 0.46234 | 122.4518 | 0.17395 | 122.5388 | 122.4564 | 122.3282 | 122.3328 | 122.2549 | -122.4518 | -122.4014 | 122.3282 | 122.4655 | 57.1426 | 61.7294
865.9375 | 122.5479 | -61.6562 | 60.7132 | -0.0051118 | -0.024197 | -0.023896 | 0.065012 | -0.032366 | -0.050808 | -0.036974 | -0.0021057 | -0.018613 | 0.057054 | 0.04968 | -0.21787 | -0.01471 | -0.01834 | -4.628 | 60.7498 | -61.7981 | 60.6583 | -61.3495 | -61.8805 | -61.8668 | 0.050354 | 60.6445 | -61.7065 | 60.7636 | -61.615 | -61.7249 | -61.6241 | -0.14191 | 0.036621 | -0.054932 | 0.3067 | -0.21057 | -0.2243 | -0.068664 | -0.082397 | -0.050354 | -0.068665 | 0.050354 | 0.041199 | 0.032043 | -0.068665 | 0.082397 | -0.018311 | 0.44861 | 122.4564 | 0.091553 | 122.4701 | 122.5479 | 122.3511 | 122.406 | 122.3007 | -122.5113 | -122.4197 | 122.3145 | 122.4197 | 57.0282 | 61.7065
867.7188 | 122.6532 | -61.6104 | 60.6766 | -0.0051118 | -0.029538 | -0.026886 | 0.062021 | -0.030016 | -0.050595 | -0.040605 | -0.0021057 | -0.02139 | 0.055986 | 0.043699 | -0.21766 | -0.01706 | -0.021971 | -4.6555 | 60.6812 | -61.7706 | 60.7132 | -61.2579 | -61.7706 | -61.7752 | 0.13733 | 60.6308 | -61.6745 | 60.8459 | -61.4914 | -61.5829 | -61.5234 | -0.16022 | 0.004577 | 0.036621 | 0.35248 | -0.16479 | -0.16022 | -0.004578 | 0 | -0.064087 | -0.045777 | 0.16937 | 0.11902 | 0.086976 | 0.027466 | 0.15106 | 0.091553 | 0.51269 | 122.4838 | 0.18311 | 122.5204 | 122.4518 | 122.3053 | 122.2916 | 122.2412 | -122.4472 | -122.3511 | 122.3236 | 122.4564 | 56.955 | 61.7477
869.5156 | 122.5891 | -61.6013 | 60.7498 | -0.0051118 | -0.027401 | -0.02475 | 0.062448 | -0.029802 | -0.04974 | -0.040178 | -0.0021057 | -0.022672 | 0.054705 | 0.043699 | -0.21958 | -0.019837 | -0.019621 | -4.5639 | 60.7269 | -61.734 | 60.759 | -61.235 | -61.7523 | -61.7477 | 0.1236 | 60.6903 | -61.6379 | 60.8185 | -61.4822 | -61.5967 | -61.5234 | -0.13275 | -0.022888 | 0.009155 | 0.36621 | -0.14649 | -0.15106 | -0.013733 | -0.01831 | -0.036621 | -0.059509 | 0.068664 | 0.11902 | 0.07782 | 0.004577 | 0.11444 | 0.041198 | 0.49896 | 122.493 | 0.15564 | 122.4564 | 122.4609 | 122.3282 | 122.3282 | 122.2916 | -122.4838 | -122.3877 | 122.3602 | 122.4197 | 57.0374 | 61.7249
871.2969 | 122.6074 | -61.5967 | 60.7361 | -0.0051118 | -0.026333 | -0.024537 | 0.063089 | -0.034289 | -0.049099 | -0.038469 | -0.0051575 | -0.022245 | 0.05385 | 0.044553 | -0.21659 | -0.016846 | -0.02368 | -5.2414 | 60.7178 | -61.7798 | 60.6903 | -61.3129 | -61.8164 | -61.8027 | 0.013733 | 60.6766 | -61.6608 | 60.8093 | -61.528 | -61.6241 | -61.5417 | -0.1831 | -0.018311 | -0.045776 | 0.28381 | -0.20599 | -0.21973 | -0.022888 | -0.036621 | -0.064087 | -0.059509 | 0.073242 | 0.068665 | 0.054932 | -0.027466 | 0.11902 | 0.036621 | 0.46692 | 122.4701 | 0.13275 | 122.4701 | 122.4976 | 122.3373 | 122.3145 | 122.2733 | -122.5159 | -122.3969 | 122.287 | 122.406 | 56.3553 | 61.6104
873.0781 | 122.5067 | -61.6058 | 60.7773 | 0.0025177 | -0.02142 | -0.026246 | 0.065012 | -0.032793 | -0.048245 | -0.040178 | -0.0021057 | -0.018186 | 0.055773 | 0.050107 | -0.21787 | -0.015351 | -0.020262 | -4.5136 | 60.7773 | -61.7386 | 60.6949 | -61.3266 | -61.8759 | -61.8484 | 0.013733 | 60.7132 | -61.6287 | 60.791 | -61.5829 | -61.7203 | -61.6013 | -0.13275 | 0 | -0.082398 | 0.27924 | -0.24262 | -0.27008 | -0.10986 | -0.13733 | -0.022888 | -0.064087 | 0.013733 | 0.022888 | 0.004578 | -0.11444 | 0.027466 | -0.091553 | 0.41199 | 122.4335 | 0.045776 | 122.4197 | 122.5159 | 122.3419 | 122.3831 | 122.319 | -122.5159 | -122.406 | 122.3007 | 122.3969 | 57.0923 | 61.6196
874.875 | 122.6532 | -61.6058 | 60.6995 | 0.0025177 | -0.024624 | -0.023255 | 0.066294 | -0.030657 | -0.050595 | -0.039751 | -0.0051575 | -0.022458 | 0.057482 | 0.050748 | -0.21766 | -0.015351 | -0.025176 | -5.0629 | 60.7407 | -61.7249 | 60.7132 | -61.2946 | -61.8347 | -61.7981 | 0.004578 | 60.64 | -61.6608 | 60.8551 | -61.5234 | -61.6333 | -61.5005 | -0.11902 | 0.041199 | 0.013733 | 0.31128 | -0.19226 | -0.22888 | -0.073242 | -0.10986 | -0.054932 | -0.059509 | 0.15564 | 0.082398 | 0.10529 | -0.027466 | 0.16022 | 0.027466 | 0.4303 | 122.4381 | 0.13733 | 122.5159 | 122.4655 | 122.3007 | 122.3465 | 122.2458 | -122.4243 | -122.3602 | 122.319 | 122.4609 | 56.543 | 61.6104
876.6719 | 122.6028 | -61.5829 | 60.7452 | -0.0051118 | -0.026333 | -0.024537 | 0.061594 | -0.037493 | -0.051022 | -0.040392 | 0.0039979 | -0.022031 | 0.0562 | 0.042203 | -0.21723 | -0.016633 | -0.02133 | -5.0171 | 60.7636 | -61.7661 | 60.6903 | -61.2808 | -61.8073 | -61.7889 | 0.009155 | 60.7132 | -61.647 | 60.8368 | -61.5097 | -61.5967 | -61.5326 | -0.18311 | 0.018311 | -0.054931 | 0.30212 | -0.20599 | -0.2243 | -0.022888 | -0.041199 | -0.064087 | -0.032043 | 0.091553 | 0.073242 | 0.050354 | -0.013733 | 0.11444 | 0.050354 | 0.48523 | 122.4564 | 0.13733 | 122.4838 | 122.5296 | 122.3602 | 122.3465 | 122.2961 | -122.5113 | -122.3923 | 122.2733 | 122.4197 | 56.5659 | 61.5921
878.4531 | 122.5021 | -61.615 | 60.7864 | 0.0025177 | -0.024197 | -0.0271 | 0.06608 | -0.028734 | -0.048458 | -0.039751 | -0.0021057 | -0.018827 | 0.057268 | 0.05203 | -0.21937 | -0.015137 | -0.024535 | -4.8706 | 60.8459 | -61.7203 | 60.6445 | -61.3861 | -61.9263 | -61.8713 | -0.10986 | 60.7452 | -61.6608 | 60.7636 | -61.6333 | -61.7203 | -61.5967 | -0.10529 | 0.059509 | -0.14191 | 0.22888 | -0.25635 | -0.31128 | -0.15106 | -0.20599 | -0.045777 | -0.041199 | -0.022888 | -0.018311 | 0.01831 | -0.10529 | 0.064087 | -0.059509 | 0.33417 | 122.3648 | 0.027466 | 122.4243 | 122.5662 | 122.406 | 122.4609 | 122.3602 | -122.5067 | -122.4472 | 122.2595 | 122.3785 | 56.7444 | 61.5051
880.1562 | 122.644 | -61.5692 | 60.7727 | -0.0051118 | -0.02676 | -0.02475 | 0.061594 | -0.034716 | -0.051663 | -0.039965 | -0.0021057 | -0.02139 | 0.054918 | 0.044553 | -0.21637 | -0.015992 | -0.021117 | -4.8569 | 60.7819 | -61.7203 | 60.7361 | -61.2167 | -61.7477 | -61.7432 | 0.064087 | 60.704 | -61.6104 | 60.9009 | -61.4456 | -61.5326 | -61.4868 | -0.15106 | 0.009155 | -0.036621 | 0.35248 | -0.17395 | -0.17853 | -0.022888 | -0.027466 | -0.041199 | -0.068664 | 0.12817 | 0.1236 | 0.082398 | 0.036621 | 0.1236 | 0.07782 | 0.50354 | 122.4564 | 0.16479 | 122.5113 | 122.5021 | 122.3145 | 122.3511 | 122.2733 | -122.493 | -122.3831 | 122.3053 | 122.4701 | 56.7123 | 61.6333
881.9531 | 122.5708 | -61.5967 | 60.7819 | -0.0051118 | -0.021847 | -0.0224 | 0.065653 | -0.031298 | -0.049954 | -0.042955 | -0.0021057 | -0.017545 | 0.056414 | 0.04434 | -0.21595 | -0.016205 | -0.025176 | -4.7791 | 60.8185 | -61.7157 | 60.6628 | -61.3312 | -61.8759 | -61.8576 | -0.09613 | 60.7407 | -61.615 | 60.8185 | -61.5692 | -61.6928 | -61.5601 | -0.11902 | 0.036621 | -0.11902 | 0.2655 | -0.26093 | -0.27924 | -0.14191 | -0.16022 | -0.01831 | -0.041198 | 0.036621 | 0.027466 | 0.036621 | -0.09613 | 0.054931 | -0.07782 | 0.38452 | 122.3785 | 0.045776 | 122.4335 | 122.5342 | 122.3557 | 122.4152 | 122.3373 | -122.4976 | -122.3969 | 122.2595 | 122.4152 | 56.8176 | 61.5005
883.7344 | 122.5067 | -61.528 | 60.8551 | 0.0025177 | -0.024838 | -0.023896 | 0.063089 | -0.027453 | -0.048672 | -0.038683 | -0.0021057 | -0.019467 | 0.057695 | 0.046262 | -0.21766 | -0.015351 | -0.015349 | -4.2435 | 60.8643 | -61.6653 | 60.7636 | -61.2213 | -61.7523 | -61.7661 | 0.068665 | 60.7956 | -61.5646 | 60.8826 | -61.4639 | -61.5829 | -61.4868 | -0.13733 | 0.009155 | -0.091553 | 0.3067 | -0.23804 | -0.2243 | -0.10071 | -0.086975 | -0.036621 | -0.05951 | 0.027465 | 0.064087 | 0.041199 | -0.054932 | 0.07782 | -0.018311 | 0.44403 | 122.4289 | 0.10071 | 122.4472 | 122.5296 | 122.3602 | 122.3923 | 122.3236 | -122.5204 | -122.4197 | 122.2916 | 122.4106 | 57.2845 | 61.5967
885.4531 | 122.5342 | -61.5738 | 60.791 | 0.0025177 | -0.02612 | -0.02475 | 0.065866 | -0.028307 | -0.048886 | -0.03911 | 0.0039979 | -0.018399 | 0.054705 | 0.044126 | -0.21702 | -0.014924 | -0.01834 | -5.1727 | 60.8368 | -61.7111 | 60.6674 | -61.322 | -61.8668 | -61.8347 | -0.10071 | 60.7681 | -61.6379 | 60.8185 | -61.5692 | -61.6928 | -61.5784 | -0.13733 | 0.045776 | -0.1236 | 0.25177 | -0.26093 | -0.29297 | -0.1236 | -0.15564 | -0.064086 | -0.022889 | 0.027465 | 0.004578 | -0.004577 | -0.11902 | 0.059509 | -0.054932 | 0.3891 | 122.3785 | 0.068664 | 122.4564 | 122.5479 | 122.406 | 122.4106 | 122.3419 | -122.5021 | -122.4289 | 122.2412 | 122.3923 | 56.4011 | 61.4731
887.2344 | 122.5983 | -61.528 | 60.7819 | 0.0025177 | -0.027188 | -0.025391 | 0.06138 | -0.033434 | -0.048245 | -0.040605 | 0.00094606 | -0.023526 | 0.057054 | 0.050535 | -0.21637 | -0.017273 | -0.025816 | -5.3467 | 60.7544 | -61.702 | 60.7361 | -61.2579 | -61.8027 | -61.7477 | -0.004578 | 60.7086 | -61.6058 | 60.8551 | -61.496 | -61.6013 | -61.5234 | -0.17395 | -0.027465 | -0.045776 | 0.27008 | -0.21973 | -0.27466 | -0.045777 | -0.10071 | -0.07782 | -0.073242 | 0.073243 | 0.032043 | 0.004578 | -0.073242 | 0.082398 | 0.004578 | 0.44403 | 122.438 | 0.10986 | 122.4609 | 122.4564 | 122.3145 | 122.2824 | 122.2366 | -122.4838 | -122.3877 | 122.2641 | 122.3831 | 56.1813 | 61.5234
889.0312 | 122.5204 | -61.528 | 60.7864 | -0.012741 | -0.022915 | -0.023682 | 0.062662 | -0.033007 | -0.047817 | -0.037615 | 0.00094606 | -0.019254 | 0.055986 | 0.042203 | -0.21595 | -0.013428 | -0.020262 | -5.2689 | 60.8002 | -61.6791 | 60.8002 | -61.1801 | -61.7386 | -61.7065 | 0.009155 | 60.7315 | -61.5875 | 60.9329 | -61.4319 | -61.5417 | -61.4273 | -0.15106 | 0.013733 | 0.013733 | 0.3479 | -0.17853 | -0.21057 | -0.027466 | -0.059509 | -0.059509 | -0.054932 | 0.14648 | 0.09613 | 0.10071 | -0.013733 | 0.16022 | 0.045776 | 0.49896 | 122.4792 | 0.15564 | 122.5204 | 122.4792 | 122.319 | 122.3282 | 122.2595 | -122.4655 | -122.374 | 122.3282 | 122.4609 | 56.2592 | 61.5372
890.7656 | 122.6578 | -61.4456 | 60.8688 | -0.0051118 | -0.027401 | -0.023041 | 0.063303 | -0.031298 | -0.047817 | -0.040605 | -0.0082091 | -0.02139 | 0.056841 | 0.049039 | -0.21979 | -0.015565 | -0.020476 | -5.2917 | 60.8185 | -61.6333 | 60.8734 | -61.0657 | -61.6058 | -61.6013 | 0.17395 | 60.7681 | -61.5051 | 61.0153 | -61.3037 | -61.3998 | -61.3632 | -0.18768 | -0.050354 | 0.004578 | 0.37994 | -0.15564 | -0.16022 | 0.032044 | 0.027466 | -0.059509 | -0.10071 | 0.14649 | 0.14191 | 0.082398 | 0.045777 | 0.14191 | 0.10529 | 0.56763 | 122.5067 | 0.20142 | 122.5204 | 122.4518 | 122.2733 | 122.2641 | 122.2137 | -122.5021 | -122.374 | 122.319 | 122.4609 | 56.1539 | 61.6196
892.5 | 122.5296 | -61.4685 | 60.8826 | 0.010147 | -0.024411 | -0.023255 | 0.06608 | -0.028948 | -0.049954 | -0.041033 | -0.0021057 | -0.018613 | 0.055773 | 0.050962 | -0.21595 | -0.014924 | -0.023467 | -4.9301 | 60.9329 | -61.615 | 60.8414 | -61.1664 | -61.7157 | -61.7111 | 0.009155 | 60.8505 | -61.5143 | 60.9283 | -61.4456 | -61.5738 | -61.4594 | -0.14648 | 0.050354 | -0.041198 | 0.30212 | -0.24262 | -0.24719 | -0.096131 | -0.10071 | -0.045776 | -0.032043 | 0.045777 | 0.022888 | 0.009155 | -0.10529 | 0.054931 | -0.05951 | 0.44861 | 122.4564 | 0.068664 | 122.4426 | 122.5479 | 122.3648 | 122.4014 | 122.319 | -122.4976 | -122.3969 | 122.3099 | 122.3969 | 56.5384 | 61.4777
894.2812 | 122.5433 | -61.4273 | 60.9512 | -0.0051118 | -0.025479 | -0.02475 | 0.06373 | -0.033007 | -0.048672 | -0.044664 | 0.0039979 | -0.019895 | 0.055559 | 0.054166 | -0.2168 | -0.018342 | -0.026244 | -5.1315 | 60.965 | -61.5692 | 60.8368 | -61.1252 | -61.647 | -61.6562 | 0.068665 | 60.9055 | -61.4868 | 60.9924 | -61.3678 | -61.4868 | -61.3998 | -0.14191 | 0.013733 | -0.11444 | 0.30212 | -0.22888 | -0.21973 | -0.086975 | -0.07782 | -0.059509 | -0.045776 | 0.041199 | 0.059509 | 0.027466 | -0.059509 | 0.086975 | 0 | 0.44403 | 122.406 | 0.11902 | 122.4792 | 122.5342 | 122.3923 | 122.3923 | 122.3328 | -122.5204 | -122.438 | 122.2641 | 122.4197 | 56.2958 | 61.496
896 | 122.58 | -61.4594 | 60.8826 | -0.0051118 | -0.024197 | -0.023896 | 0.061594 | -0.037066 | -0.04739 | -0.040178 | -0.0021057 | -0.021817 | 0.055773 | 0.049894 | -0.21702 | -0.015992 | -0.023253 | -5.7816 | 60.9009 | -61.5921 | 60.8505 | -61.1114 | -61.6653 | -61.6425 | -0.018311 | 60.8414 | -61.4868 | 60.965 | -61.3861 | -61.4868 | -61.4044 | -0.13275 | 0.018311 | -0.032043 | 0.3479 | -0.18311 | -0.20599 | -0.050354 | -0.073242 | -0.027465 | -0.041198 | 0.082398 | 0.073243 | 0.054932 | -0.027465 | 0.082397 | 0 | 0.48065 | 122.4426 | 0.10071 | 122.4518 | 122.493 | 122.3282 | 122.3602 | 122.3007 | -122.4747 | -122.3694 | 122.3099 | 122.4243 | 55.6778 | 61.441
897.7969 | 122.5754 | -61.4182 | 60.9238 | 0.0025177 | -0.026333 | -0.024964 | 0.060953 | -0.031725 | -0.047177 | -0.041887 | 0.00094606 | -0.02139 | 0.055559 | 0.043912 | -0.21744 | -0.016633 | -0.020903 | -5.9738 | 60.9146 | -61.5326 | 60.8871 | -61.0657 | -61.6196 | -61.6058 | -0.022888 | 60.8688 | -61.4594 | 60.997 | -61.3678 | -61.441 | -61.3586 | -0.11444 | -0.009155 | -0.036621 | 0.35248 | -0.18768 | -0.20142 | -0.073242 | -0.086975 | -0.041199 | -0.054932 | 0.073242 | 0.050354 | 0.059509 | -0.022888 | 0.10071 | 0.018311 | 0.46692 | 122.4197 | 0.091553 | 122.4564 | 122.4472 | 122.3282 | 122.3328 | 122.287 | -122.4564 | -122.3831 | 122.3053 | 122.4152 | 55.4443 | 61.3953
899.5312 | 122.6074 | -61.3541 | 60.9924 | -0.0051118 | -0.026547 | -0.024537 | 0.062662 | -0.031939 | -0.051022 | -0.03911 | -0.0021057 | -0.022031 | 0.055986 | 0.04434 | -0.21637 | -0.018769 | -0.022398 | -5.9967 | 60.9833 | -61.4822 | 60.9512 | -60.9741 | -61.5417 | -61.5234 | 0.018311 | 60.9421 | -61.3953 | 61.0931 | -61.2488 | -61.3403 | -61.2762 | -0.12817 | -0.009156 | -0.041199 | 0.37994 | -0.16937 | -0.18768 | -0.041198 | -0.059509 | -0.041199 | -0.050354 | 0.10071 | 0.10529 | 0.07782 | 0.013733 | 0.11902 | 0.054932 | 0.50812 | 122.4335 | 0.14648 | 122.4884 | 122.4655 | 122.3373 | 122.3373 | 122.2961 | -122.4747 | -122.3877 | 122.3053 | 122.4472 | 55.3574 | 61.3724
901.3125 | 122.5296 | -61.3495 | 61.0703 | 0.0025177 | -0.025479 | -0.02475 | 0.065225 | -0.026812 | -0.046322 | -0.03911 | -0.0021057 | -0.020108 | 0.0562 | 0.049894 | -0.21723 | -0.01471 | -0.020903 | -6.1615 | 61.0748 | -61.4594 | 60.9924 | -60.9558 | -61.5189 | -61.5234 | 0.064087 | 61.0291 | -61.3495 | 61.1069 | -61.2625 | -61.3815 | -61.2717 | -0.10986 | 0.004578 | -0.077819 | 0.39368 | -0.17395 | -0.16937 | -0.064086 | -0.059509 | 0 | -0.041198 | 0.036622 | 0.086975 | 0.07782 | -0.032044 | 0.07782 | -0.032044 | 0.50354 | 122.4518 | 0.086975 | 122.4564 | 122.5342 | 122.3785 | 122.4243 | 122.3785 | -122.5296 | -122.4197 | 122.3419 | 122.4564 | 55.188 | 61.4136
903.0312 | 122.5296 | -61.3724 | 61.0062 | -0.0051118 | -0.026974 | -0.024964 | 0.062876 | -0.03023 | -0.048458 | -0.03911 | 0.00094606 | -0.020749 | 0.057268 | 0.054807 | -0.21637 | -0.01471 | -0.019621 | -5.928 | 60.997 | -61.5738 | 60.8688 | -61.1252 | -61.6379 | -61.6379 | 0.004578 | 60.9421 | -61.4227 | 61.0016 | -61.3358 | -61.4548 | -61.3678 | -0.20142 | -0.009156 | -0.13733 | 0.24719 | -0.2655 | -0.2655 | -0.064086 | -0.064086 | -0.050354 | -0.064087 | -0.004578 | 0.036621 | 0.004577 | -0.082398 | 0.054931 | -0.032044 | 0.44861 | 122.4426 | 0.086975 | 122.4243 | 122.5708 | 122.3648 | 122.3694 | 122.3145 | -122.58 | -122.4289 | 122.2412 | 122.374 | 55.4443 | 61.377
904.8281 | 122.4792 | -61.4044 | 60.997 | -0.0051118 | -0.022061 | -0.023682 | 0.066721 | -0.029802 | -0.048031 | -0.039965 | 0.00094606 | -0.01904 | 0.055132 | 0.042203 | -0.21616 | -0.013215 | -0.022826 | -6.0928 | 61.0199 | -61.5601 | 60.8688 | -61.084 | -61.6608 | -61.647 | -0.045776 | 60.9558 | -61.4319 | 60.9787 | -61.3861 | -61.5189 | -61.3907 | -0.15564 | 0.022888 | -0.12817 | 0.32043 | -0.24262 | -0.25635 | -0.086975 | -0.10071 | -0.027466 | -0.041198 | -0.01831 | 0.018311 | 0.013733 | -0.11444 | 0.041199 | -0.086975 | 0.47608 | 122.4289 | 0.045777 | 122.4106 | 122.58 | 122.3877 | 122.4243 | 122.3602 | -122.5571 | -122.4289 | 122.2733 | 122.3831 | 55.3116 | 61.3586
906.5469 | 122.5067 | -61.3586 | 61.0336 | -0.0051118 | -0.025906 | -0.028382 | 0.062662 | -0.03322 | -0.050595 | -0.039324 | -0.0021057 | -0.021176 | 0.057054 | 0.044767 | -0.21552 | -0.016846 | -0.023894 | -6.1981 | 61.0611 | -61.5005 | 60.9009 | -61.0565 | -61.5738 | -61.5921 | -0.013733 | 60.9879 | -61.3907 | 61.0153 | -61.3312 | -61.441 | -61.3449 | -0.14191 | 0.027466 | -0.13275 | 0.30212 | -0.23346 | -0.21515 | -0.091553 | -0.073243 | -0.032043 | -0.045776 | -0.01831 | 0.027466 | 0.013733 | -0.082397 | 0.045776 | -0.050354 | 0.44403 | 122.4014 | 0.059509 | 122.406 | 122.5616 | 122.3785 | 122.4197 | 122.3465 | -122.5342 | -122.4243 | 122.2595 | 122.374 | 55.1605 | 61.3449
908.3281 | 122.6166 | -61.3495 | 60.965 | -0.012741 | -0.026547 | -0.022828 | 0.064371 | -0.028093 | -0.049526 | -0.036547 | -0.0051575 | -0.020963 | 0.055132 | 0.049253 | -0.2183 | -0.016419 | -0.020689 | -6.102 | 61.0474 | -61.4822 | 60.91 | -61.0428 | -61.6104 | -61.5921 | -0.027466 | 60.9238 | -61.4227 | 61.0748 | -61.2762 | -61.3907 | -61.2762 | -0.13275 | 0.082397 | -0.054932 | 0.3067 | -0.24261 | -0.26093 | -0.10986 | -0.12817 | -0.073242 | -0.041199 | 0.10986 | 0.073242 | 0.073242 | -0.041199 | 0.14648 | 0.032043 | 0.43945 | 122.3923 | 0.14648 | 122.4976 | 122.5296 | 122.3465 | 122.3969 | 122.2733 | -122.4472 | -122.3877 | 122.2595 | 122.4243 | 55.2475 | 61.322
910.125 | 122.6028 | -61.3358 | 60.9833 | -0.0051118 | -0.025479 | -0.024964 | 0.065653 | -0.029802 | -0.04974 | -0.041246 | 0.00094606 | -0.017331 | 0.055559 | 0.044553 | -0.21552 | -0.015778 | -0.020689 | -6.0425 | 61.0336 | -61.4868 | 60.9283 | -61.0474 | -61.615 | -61.5921 | -0.022888 | 60.9512 | -61.3907 | 61.0886 | -61.2808 | -61.377 | -61.2717 | -0.15106 | 0.050354 | -0.054931 | 0.28839 | -0.25635 | -0.27924 | -0.10529 | -0.12817 | -0.054932 | -0.032043 | 0.10529 | 0.054931 | 0.064087 | -0.041199 | 0.11902 | 0.013733 | 0.43945 | 122.4152 | 0.10986 | 122.4792 | 122.5204 | 122.3419 | 122.3694 | 122.287 | -122.4701 | -122.374 | 122.2641 | 122.4243 | 55.2933 | 61.3129
911.9062 | 122.493 | -61.3266 | 61.0611 | 0.010147 | -0.027188 | -0.026673 | 0.062876 | -0.031084 | -0.049313 | -0.039324 | -0.0021057 | -0.019895 | 0.056841 | 0.045621 | -0.21659 | -0.015992 | -0.023894 | -6.5964 | 61.0519 | -61.4548 | 60.9283 | -60.997 | -61.5692 | -61.5601 | -0.009155 | 61.0153 | -61.3861 | 61.0428 | -61.2854 | -61.409 | -61.3403 | -0.12817 | -0.009155 | -0.13275 | 0.32959 | -0.23346 | -0.24262 | -0.10529 | -0.11444 | -0.059509 | -0.045776 | -0.01831 | 0.041199 | -0.013733 | -0.082398 | 0.045776 | -0.022889 | 0.45776 | 122.3831 | 0.10071 | 122.4289 | 122.5067 | 122.4014 | 122.3785 | 122.3419 | -122.5159 | -122.4472 | 122.2549 | 122.3694 | 54.7302 | 61.3174
913.7031 | 122.5845 | -61.322 | 61.0107 | -0.012741 | -0.02911 | -0.026459 | 0.062876 | -0.033434 | -0.049526 | -0.039324 | -0.0021057 | -0.023099 | 0.057482 | 0.043272 | -0.21637 | -0.016419 | -0.022826 | -6.6147 | 61.0153 | -61.4456 | 60.9604 | -60.9695 | -61.528 | -61.528 | -0.022888 | 60.9741 | -61.3724 | 61.0886 | -61.2534 | -61.322 | -61.2534 | -0.1236 | 0.004578 | -0.050354 | 0.35248 | -0.20599 | -0.20599 | -0.082397 | -0.082397 | -0.050354 | -0.036621 | 0.07782 | 0.068664 | 0.068664 | 0 | 0.11902 | 0.050354 | 0.47608 | 122.406 | 0.11902 | 122.4609 | 122.4609 | 122.3465 | 122.3373 | 122.2961 | -122.4564 | -122.3831 | 122.2824 | 122.4106 | 54.7073 | 61.2991
915.5 | 122.5983 | -61.3129 | 61.0565 | -0.0051118 | -0.027615 | -0.025177 | 0.060526 | -0.031298 | -0.049526 | -0.039965 | 0.00094606 | -0.021176 | 0.055559 | 0.042631 | -0.21851 | -0.015992 | -0.022612 | -6.5643 | 61.0062 | -61.4594 | 61.0565 | -60.8688 | -61.4365 | -61.4319 | 0.11902 | 60.9741 | -61.3586 | 61.1343 | -61.171 | -61.2717 | -61.2076 | -0.14648 | -0.050354 | 0 | 0.44403 | -0.11902 | -0.1236 | 0.027466 | 0.022889 | -0.045777 | -0.082398 | 0.077819 | 0.14191 | 0.10529 | 0.041199 | 0.15106 | 0.086976 | 0.59052 | 122.5159 | 0.18768 | 122.493 | 122.4655 | 122.3328 | 122.319 | 122.287 | -122.5159 | -122.4152 | 122.3694 | 122.4472 | 54.7485 | 61.4319
917.2031 | 122.493 | -61.2717 | 61.1298 | -0.0051118 | -0.02612 | -0.028382 | 0.065653 | -0.033434 | -0.047604 | -0.040178 | -0.0021057 | -0.020749 | 0.055132 | 0.045621 | -0.21744 | -0.016633 | -0.020476 | -6.6742 | 61.1114 | -61.4227 | 60.9695 | -60.9695 | -61.5234 | -61.528 | -0.013733 | 61.0703 | -61.3312 | 61.0748 | -61.2717 | -61.3724 | -61.29 | -0.15106 | -0.018311 | -0.16022 | 0.30212 | -0.25635 | -0.25177 | -0.10529 | -0.10071 | -0.05951 | -0.05951 | -0.054932 | 0 | -0.018311 | -0.10071 | 0.041199 | -0.041198 | 0.45319 | 122.3923 | 0.05951 | 122.406 | 122.5342 | 122.4014 | 122.3831 | 122.3419 | -122.5525 | -122.4609 | 122.2412 | 122.3465 | 54.5975 | 61.2579
919 | 122.6303 | -61.2259 | 61.0886 | -0.012741 | -0.027401 | -0.024323 | 0.062448 | -0.033648 | -0.050167 | -0.038042 | -0.0021057 | -0.02139 | 0.055345 | 0.040067 | -0.21637 | -0.019196 | -0.02368 | -6.5781 | 61.0748 | -61.3815 | 61.116 | -60.7727 | -61.3541 | -61.3495 | 0.11444 | 61.0199 | -61.2625 | 61.1984 | -61.1023 | -61.2122 | -61.1481 | -0.15564 | -0.013733 | 0.027466 | 0.45319 | -0.1236 | -0.12817 | 0.032044 | 0.027466 | -0.036621 | -0.068665 | 0.10986 | 0.1236 | 0.07782 | 0.013733 | 0.11444 | 0.050354 | 0.60883 | 122.4976 | 0.16022 | 122.4609 | 122.4564 | 122.2824 | 122.3007 | 122.2458 | -122.4701 | -122.3511 | 122.3419 | 122.4243 | 54.6478 | 61.3403
920.7812 | 122.6532 | -61.1847 | 61.116 | -0.0051118 | -0.027401 | -0.025177 | 0.063303 | -0.03322 | -0.04739 | -0.041033 | 0.00094606 | -0.021176 | 0.055559 | 0.045194 | -0.21915 | -0.016419 | -0.025389 | -6.8298 | 61.1069 | -61.3403 | 61.1206 | -60.7864 | -61.3495 | -61.3632 | 0.10986 | 61.0474 | -61.2396 | 61.2671 | -61.0657 | -61.1755 | -61.1206 | -0.15564 | -0.009155 | 0.004577 | 0.39825 | -0.17853 | -0.1648 | -0.022888 | -0.009155 | -0.054932 | -0.068665 | 0.15106 | 0.11902 | 0.064087 | 0.009155 | 0.11902 | 0.064087 | 0.55389 | 122.4609 | 0.17395 | 122.5067 | 122.4472 | 122.287 | 122.2916 | 122.2321 | -122.4564 | -122.3557 | 122.3053 | 122.4518 | 54.3549 | 61.2946
922.5 | 122.5891 | -61.2076 | 61.1343 | -0.0051118 | -0.02676 | -0.021546 | 0.062021 | -0.03258 | -0.048458 | -0.040819 | 0.0070497 | -0.021604 | 0.054918 | 0.047117 | -0.21958 | -0.015992 | -0.02368 | -6.8024 | 61.0886 | -61.3495 | 61.1389 | -60.7727 | -61.3541 | -61.3541 | 0.09613 | 61.0611 | -61.2717 | 61.203 | -61.1114 | -61.203 | -61.1343 | -0.14191 | -0.045776 | 0.004578 | 0.43488 | -0.14648 | -0.14648 | -0.004578 | -0.004578 | -0.064086 | -0.073242 | 0.068665 | 0.096131 | 0.073243 | 0.004578 | 0.13733 | 0.068664 | 0.57678 | 122.4884 | 0.16022 | 122.4747 | 122.438 | 122.3328 | 122.2961 | 122.2687 | -122.4838 | -122.406 | 122.3465 | 122.4106 | 54.4052 | 61.3037
924.2812 | 122.5342 | -61.171 | 61.2305 | -0.012741 | -0.027615 | -0.023469 | 0.064585 | -0.033007 | -0.050167 | -0.043383 | 0.00094606 | -0.017972 | 0.057054 | 0.050107 | -0.21937 | -0.015992 | -0.021758 | -6.7612 | 61.2442 | -61.2762 | 61.1435 | -60.8093 | -61.3586 | -61.3632 | 0.032043 | 61.203 | -61.171 | 61.2488 | -61.0931 | -61.203 | -61.1069 | -0.10529 | 0.013733 | -0.086975 | 0.36163 | -0.19226 | -0.18768 | -0.086975 | -0.082398 | 0 | -0.027466 | 0.01831 | 0.077819 | 0.064086 | -0.032044 | 0.064086 | -0.032044 | 0.46692 | 122.4197 | 0.077819 | 122.4197 | 122.5204 | 122.374 | 122.4152 | 122.374 | -122.5067 | -122.4014 | 122.3145 | 122.4197 | 54.4098 | 61.203
926 | 122.6212 | -61.1343 | 61.1847 | -0.02037 | -0.028042 | -0.025391 | 0.060526 | -0.031511 | -0.048886 | -0.038256 | -0.0021057 | -0.021176 | 0.055559 | 0.040281 | -0.21744 | -0.017701 | -0.027098 | -6.9305 | 61.1664 | -61.3129 | 61.1984 | -60.6766 | -61.2854 | -61.2854 | 0.10529 | 61.1023 | -61.1847 | 61.3037 | -61.0107 | -61.1023 | -61.0519 | -0.17853 | -0.01831 | 0.013733 | 0.45776 | -0.15106 | -0.15106 | 0.027466 | 0.027466 | -0.050354 | -0.082397 | 0.11902 | 0.1236 | 0.082397 | 0.032043 | 0.13275 | 0.082397 | 0.63629 | 122.5113 | 0.17395 | 122.4884 | 122.4792 | 122.287 | 122.3007 | 122.2366 | -122.4976 | -122.3694 | 122.3328 | 122.438 | 54.2038 | 61.2396
927.7812 | 122.5983 | -61.0931 | 61.2442 | -0.0051118 | -0.026547 | -0.025605 | 0.06373 | -0.033434 | -0.051876 | -0.041674 | -0.0021057 | -0.021176 | 0.055773 | 0.049467 | -0.21787 | -0.01941 | -0.023253 | -6.9168 | 61.2122 | -61.2534 | 61.2534 | -60.6354 | -61.2167 | -61.2396 | 0.10071 | 61.1801 | -61.1389 | 61.3495 | -60.9787 | -61.0703 | -61.0107 | -0.16022 | -0.032044 | 0.009155 | 0.45776 | -0.14648 | -0.1236 | 0.013733 | 0.036621 | -0.045776 | -0.064087 | 0.10529 | 0.11444 | 0.082398 | 0.022889 | 0.12817 | 0.068665 | 0.61798 | 122.5067 | 0.16022 | 122.4884 | 122.4655 | 122.319 | 122.3053 | 122.2733 | -122.4976 | -122.3831 | 122.3465 | 122.4426 | 54.1763 | 61.1938
929.5 | 122.6257 | -61.0565 | 61.2579 | 0.010147 | -0.022915 | -0.025177 | 0.065866 | -0.03023 | -0.049313 | -0.039537 | 0.00094606 | -0.020108 | 0.0562 | 0.051389 | -0.2183 | -0.016419 | -0.025389 | -6.9763 | 61.2671 | -61.203 | 61.2671 | -60.672 | -61.2442 | -61.2396 | 0.050354 | 61.1893 | -61.1069 | 61.3907 | -60.9604 | -61.0794 | -60.9604 | -0.14648 | 0.009155 | 0.009155 | 0.38452 | -0.1831 | -0.18768 | -0.036621 | -0.041199 | -0.050354 | -0.068665 | 0.13275 | 0.096131 | 0.096131 | -0.022888 | 0.14648 | 0.027466 | 0.53101 | 122.4701 | 0.14648 | 122.4976 | 122.4701 | 122.2961 | 122.3236 | 122.2458 | -122.4609 | -122.3648 | 122.3236 | 122.4472 | 54.0802 | 61.1069
931.2969 | 122.4838 | -61.0703 | 61.3174 | 0.010147 | -0.024197 | -0.025391 | 0.06608 | -0.031298 | -0.050167 | -0.041246 | 0.00094606 | -0.018186 | 0.05385 | 0.056089 | -0.21637 | -0.015992 | -0.021758 | -6.8115 | 61.3266 | -61.203 | 61.1893 | -60.7819 | -61.3586 | -61.3541 | -0.09613 | 61.2579 | -61.1298 | 61.29 | -61.1023 | -61.203 | -61.0748 | -0.13275 | 0.009155 | -0.12817 | 0.28839 | -0.28381 | -0.28839 | -0.15106 | -0.15564 | -0.05951 | -0.059509 | -0.027466 | -0.032044 | -0.004578 | -0.13275 | 0.054932 | -0.073242 | 0.42114 | 122.3923 | 0.027466 | 122.4197 | 122.5296 | 122.3877 | 122.3969 | 122.3282 | -122.5204 | -122.4472 | 122.2595 | 122.3602 | 54.2587 | 60.9741
933.0312 | 122.6074 | -61.0565 | 61.29 | -0.0051118 | -0.023343 | -0.024323 | 0.065012 | -0.033861 | -0.04739 | -0.042314 | -0.0021057 | -0.02139 | 0.058123 | 0.047117 | -0.21723 | -0.01706 | -0.025389 | -7.0862 | 61.3449 | -61.1801 | 61.2579 | -60.6628 | -61.2671 | -61.2625 | -0.004578 | 61.2305 | -61.0748 | 61.4182 | -60.9467 | -61.0565 | -60.9604 | -0.1236 | 0.054932 | -0.032043 | 0.39368 | -0.20599 | -0.21057 | -0.082397 | -0.086975 | -0.01831 | -0.059509 | 0.12817 | 0.10986 | 0.096131 | 0 | 0.11444 | 0.01831 | 0.51727 | 122.4381 | 0.12817 | 122.493 | 122.525 | 122.3053 | 122.4014 | 122.287 | -122.4701 | -122.3648 | 122.3145 | 122.4747 | 53.9703 | 61.0519
934.8125 | 122.5754 | -61.0336 | 61.322 | -0.0051118 | -0.025906 | -0.024109 | 0.060526 | -0.030443 | -0.047177 | -0.039324 | -0.0021057 | -0.020749 | 0.055345 | 0.044767 | -0.21531 | -0.01706 | -0.021117 | -7.3837 | 61.3037 | -61.1801 | 61.2579 | -60.6216 | -61.2213 | -61.2167 | -0.050354 | 61.2488 | -61.1069 | 61.3678 | -60.9695 | -61.0519 | -60.9695 | -0.14648 | -0.01831 | -0.064086 | 0.41199 | -0.18311 | -0.18768 | -0.036621 | -0.041198 | -0.073243 | -0.073242 | 0.045777 | 0.064087 | 0.064087 | -0.018311 | 0.13733 | 0.054932 | 0.55847 | 122.4381 | 0.13733 | 122.4747 | 122.4838 | 122.3557 | 122.3373 | 122.2824 | -122.5021 | -122.4289 | 122.2916 | 122.4014 | 53.6499 | 60.9833
936.5938 | 122.6532 | -61.0016 | 61.2991 | -0.0051118 | -0.026547 | -0.028382 | 0.063516 | -0.034075 | -0.051022 | -0.040392 | -0.0021057 | -0.020536 | 0.055345 | 0.048612 | -0.21787 | -0.015778 | -0.023253 | -6.9122 | 61.3266 | -61.1435 | 61.3449 | -60.4889 | -61.1481 | -61.1206 | 0.1236 | 61.2579 | -61.0291 | 61.4731 | -60.8322 | -60.9421 | -60.8871 | -0.14191 | 0.027466 | 0.045777 | 0.5127 | -0.11902 | -0.14648 | 0.022889 | -0.004577 | -0.027466 | -0.041198 | 0.17395 | 0.16937 | 0.11444 | 0.059509 | 0.14191 | 0.086975 | 0.6546 | 122.4884 | 0.19684 | 122.5021 | 122.4701 | 122.287 | 122.3282 | 122.2595 | -122.4426 | -122.3282 | 122.3465 | 122.4747 | 54.0894 | 61.1252
938.3125 | 122.5342 | -60.9467 | 61.409 | -0.012741 | -0.025479 | -0.024964 | 0.065866 | -0.028948 | -0.04974 | -0.041033 | -0.0021057 | -0.018399 | 0.056414 | 0.054166 | -0.21723 | -0.015565 | -0.023253 | -7.2281 | 61.441 | -61.1023 | 61.3312 | -60.5667 | -61.1664 | -61.1664 | 0.027466 | 61.3724 | -60.9879 | 61.4502 | -60.9009 | -61.0291 | -60.9375 | -0.15564 | 0.032043 | -0.07782 | 0.37994 | -0.21973 | -0.21973 | -0.064087 | -0.064087 | -0.041199 | -0.036622 | 0.041198 | 0.045776 | 0.009155 | -0.082398 | 0.050354 | -0.041199 | 0.53558 | 122.4335 | 0.086975 | 122.438 | 122.5433 | 122.3602 | 122.3877 | 122.319 | -122.5113 | -122.3969 | 122.2778 | 122.3969 | 53.7186 | 60.9741
940.0938 | 122.5433 | -60.9146 | 61.4548 | -0.0051118 | -0.02142 | -0.024964 | 0.064585 | -0.03258 | -0.04974 | -0.038896 | -0.0021057 | -0.018827 | 0.057695 | 0.049467 | -0.21573 | -0.015565 | -0.019194 | -7.1823 | 61.4594 | -61.0565 | 61.3861 | -60.4797 | -61.1206 | -61.1206 | 0.07782 | 61.3953 | -60.9604 | 61.5097 | -60.8597 | -60.9833 | -60.878 | -0.14191 | 0.004578 | -0.068665 | 0.43488 | -0.20599 | -0.20599 | -0.064086 | -0.064086 | -0.045776 | -0.059509 | 0.054932 | 0.054932 | 0.036621 | -0.068664 | 0.082397 | -0.022888 | 0.57678 | 122.4426 | 0.10071 | 122.4701 | 122.5159 | 122.3557 | 122.374 | 122.3099 | -122.5113 | -122.4152 | 122.3007 | 122.4243 | 53.7323 | 60.9924
941.8281 | 122.5845 | -60.878 | 61.4822 | 0.0025177 | -0.027615 | -0.026246 | 0.060953 | -0.031725 | -0.050808 | -0.039965 | -0.0021057 | -0.021176 | 0.055345 | 0.045835 | -0.21787 | -0.01706 | -0.023467 | -7.2876 | 61.4136 | -61.0428 | 61.4594 | -60.3928 | -61.0291 | -61.0336 | 0.07782 | 61.409 | -60.9329 | 61.5509 | -60.7864 | -60.8917 | -60.8231 | -0.16479 | -0.068665 | -0.022888 | 0.48523 | -0.15564 | -0.15106 | 0.009156 | 0.013733 | -0.054931 | -0.073242 | 0.068664 | 0.091553 | 0.054932 | -0.013733 | 0.10986 | 0.041198 | 0.65002 | 122.5021 | 0.14648 | 122.4838 | 122.4564 | 122.3419 | 122.2916 | 122.287 | -122.525 | -122.4152 | 122.3373 | 122.4289 | 53.5904 | 60.9558
943.6094 | 122.5983 | -60.8002 | 61.5189 | -0.012741 | -0.022915 | -0.023469 | 0.064798 | -0.03258 | -0.051449 | -0.042742 | 0.0070497 | -0.020322 | 0.055986 | 0.046476 | -0.21744 | -0.01236 | -0.024748 | -7.4707 | 61.5417 | -60.9467 | 61.4685 | -60.4019 | -61.0382 | -61.0291 | -0.004578 | 61.4639 | -60.878 | 61.6287 | -60.7224 | -60.8505 | -60.7132 | -0.14648 | 0.022888 | -0.050354 | 0.39825 | -0.22888 | -0.23804 | -0.082398 | -0.091553 | -0.07782 | -0.054932 | 0.10986 | 0.07782 | 0.086975 | -0.050354 | 0.16479 | 0.027466 | 0.54474 | 122.4152 | 0.15564 | 122.5067 | 122.4884 | 122.3419 | 122.3419 | 122.2641 | -122.4655 | -122.3969 | 122.2687 | 122.4289 | 53.3295 | 60.7956
945.3906 | 122.4884 | -60.8047 | 61.5738 | -0.0051118 | -0.025051 | -0.024109 | 0.06843 | -0.030443 | -0.04739 | -0.040819 | 0.0039979 | -0.017972 | 0.055559 | 0.050535 | -0.21637 | -0.015778 | -0.019194 | -7.6401 | 61.615 | -60.9512 | 61.441 | -60.4523 | -61.0748 | -61.0657 | -0.091553 | 61.5417 | -60.8505 | 61.5692 | -60.8231 | -60.9375 | -60.8047 | -0.14648 | 0.041198 | -0.13275 | 0.35248 | -0.26093 | -0.27008 | -0.11444 | -0.1236 | -0.045776 | -0.032044 | -0.004578 | -0.01831 | 0 | -0.13275 | 0.045776 | -0.086975 | 0.49896 | 122.3923 | 0.027466 | 122.4197 | 122.5662 | 122.3923 | 122.4197 | 122.3465 | -122.525 | -122.4243 | 122.2458 | 122.374 | 53.1647 | 60.7132
947.1562 | 122.5021 | -60.8002 | 61.5738 | -0.0051118 | -0.026333 | -0.023896 | 0.066294 | -0.032793 | -0.048031 | -0.042101 | 0.0039979 | -0.020322 | 0.057054 | 0.054594 | -0.2168 | -0.01471 | -0.024321 | -7.8552 | 61.6013 | -60.9467 | 61.4319 | -60.4523 | -61.0794 | -61.0611 | -0.09613 | 61.5372 | -60.8597 | 61.5646 | -60.8276 | -60.9238 | -60.8047 | -0.14648 | 0.027465 | -0.14191 | 0.3479 | -0.26093 | -0.27924 | -0.11444 | -0.13275 | -0.059509 | -0.036622 | -0.009156 | -0.027466 | -0.004578 | -0.1236 | 0.054931 | -0.064087 | 0.49438 | 122.3785 | 0.032043 | 122.4243 | 122.5479 | 122.3969 | 122.4014 | 122.3373 | -122.5204 | -122.4335 | 122.2321 | 122.3648 | 52.9449 | 60.704
948.875 | 122.5937 | -60.7636 | 61.5875 | 0.0025177 | -0.030606 | -0.026459 | 0.06373 | -0.031298 | -0.050808 | -0.038469 | -0.0021057 | -0.021817 | 0.054918 | 0.041563 | -0.21637 | -0.016846 | -0.019194 | -7.7454 | 61.5829 | -60.8963 | 61.5555 | -60.2966 | -60.9329 | -60.9329 | -0.004578 | 61.528 | -60.8047 | 61.6791 | -60.6537 | -60.7498 | -60.6674 | -0.13275 | -0.004577 | -0.032043 | 0.46692 | -0.16937 | -0.16937 | -0.036621 | -0.036621 | -0.041199 | -0.059509 | 0.091553 | 0.10986 | 0.096131 | 0.013733 | 0.13733 | 0.054932 | 0.59967 | 122.4518 | 0.15106 | 122.4838 | 122.4792 | 122.3328 | 122.3465 | 122.2916 | -122.4838 | -122.3923 | 122.319 | 122.4426 | 53.0182 | 60.759
950.6562 | 122.5662 | -60.6628 | 61.6699 | -0.0051118 | -0.023983 | -0.026032 | 0.063303 | -0.03023 | -0.048245 | -0.038042 | -0.0021057 | -0.020108 | 0.055986 | 0.049467 | -0.21872 | -0.017487 | -0.021971 | -7.9651 | 61.6745 | -60.7819 | 61.6333 | -60.1959 | -60.8368 | -60.8368 | -0.036621 | 61.615 | -60.6857 | 61.7661 | -60.6033 | -60.6857 | -60.6125 | -0.11902 | 0.004578 | -0.036621 | 0.46692 | -0.17395 | -0.17395 | -0.054932 | -0.054932 | -0.022888 | -0.054932 | 0.09613 | 0.059509 | 0.050354 | -0.022888 | 0.073242 | 0 | 0.58594 | 122.4152 | 0.082397 | 122.4518 | 122.4564 | 122.3007 | 122.3373 | 122.2778 | -122.4518 | -122.3557 | 122.2961 | 122.4289 | 52.6978 | 60.6262
952.4375 | 122.5937 | -60.5621 | 61.7432 | -0.0051118 | -0.023983 | -0.023682 | 0.067362 | -0.031084 | -0.047177 | -0.04146 | -0.0051575 | -0.018399 | 0.0562 | 0.053739 | -0.21787 | -0.014283 | -0.021758 | -8.2214 | 61.8027 | -60.7269 | 61.6928 | -60.1456 | -60.7956 | -60.8093 | -0.022888 | 61.7203 | -60.6308 | 61.8713 | -60.5072 | -60.6216 | -60.498 | -0.16479 | 0.059509 | -0.050354 | 0.41656 | -0.24719 | -0.23346 | -0.082397 | -0.068664 | -0.068664 | -0.022888 | 0.12817 | 0.054932 | 0.064087 | -0.059509 | 0.13275 | 0.009155 | 0.58136 | 122.4197 | 0.1236 | 122.5021 | 122.5296 | 122.3511 | 122.3648 | 122.2824 | -122.4701 | -122.374 | 122.2549 | 122.4335 | 52.3407 | 60.5392
954.2188 | 122.6257 | -60.585 | 61.7569 | 0.010147 | -0.023983 | -0.026886 | 0.065439 | -0.030443 | -0.047604 | -0.038256 | -0.0021057 | -0.020108 | 0.055559 | 0.051389 | -0.21872 | -0.01471 | -0.022398 | -7.6996 | 61.7706 | -60.6903 | 61.7523 | -60.0494 | -60.7407 | -60.7407 | 0.022888 | 61.7111 | -60.6033 | 61.8896 | -60.4706 | -60.5896 | -60.4706 | -0.10529 | 0.013733 | -0.004578 | 0.53558 | -0.15564 | -0.15564 | -0.050354 | -0.050354 | -0.018311 | -0.045776 | 0.13275 | 0.11444 | 0.11444 | -0.004578 | 0.13275 | 0.013733 | 0.64087 | 122.4426 | 0.13275 | 122.493 | 122.4609 | 122.3145 | 122.3557 | 122.2961 | -122.4472 | -122.3602 | 122.3373 | 122.4747 | 52.8854 | 60.6079
955.9688 | 122.5479 | -60.5255 | 61.8256 | -0.0051118 | -0.025265 | -0.023682 | 0.065653 | -0.034289 | -0.051449 | -0.039537 | -0.0051575 | -0.019254 | 0.056627 | 0.050748 | -0.21808 | -0.016419 | -0.018767 | -7.6584 | 61.8851 | -60.6674 | 61.7294 | -60.0815 | -60.7819 | -60.7727 | -0.050354 | 61.7935 | -60.5667 | 61.8942 | -60.5072 | -60.6125 | -60.4843 | -0.14191 | 0.059509 | -0.096131 | 0.44403 | -0.24719 | -0.25635 | -0.10529 | -0.11444 | -0.041198 | -0.032044 | 0.068664 | 0.018311 | 0.041199 | -0.086975 | 0.082397 | -0.045777 | 0.58594 | 122.3969 | 0.059509 | 122.4609 | 122.5525 | 122.3602 | 122.4106 | 122.319 | -122.493 | -122.3923 | 122.2549 | 122.4197 | 52.8671 | 60.4752
957.7656 | 122.4976 | -60.5026 | 61.8851 | -0.0051118 | -0.023983 | -0.022187 | 0.067575 | -0.03322 | -0.049099 | -0.039965 | -0.0021057 | -0.018613 | 0.057482 | 0.050962 | -0.21531 | -0.015992 | -0.02368 | -7.608 | 61.9308 | -60.6216 | 61.7569 | -60.0357 | -60.7361 | -60.7315 | -0.082397 | 61.853 | -60.5255 | 61.9034 | -60.498 | -60.6079 | -60.4568 | -0.11902 | 0.045776 | -0.12817 | 0.46692 | -0.22888 | -0.23346 | -0.10986 | -0.11444 | -0.022888 | -0.032044 | 0.01831 | 0.004578 | 0.045777 | -0.10528 | 0.068665 | -0.082397 | 0.58594 | 122.3785 | 0.027466 | 122.4289 | 122.5525 | 122.3785 | 122.4335 | 122.3557 | -122.5067 | -122.4106 | 122.2595 | 122.406 | 52.8946 | 60.4202
959.5625 | 122.5159 | -60.4431 | 61.9217 | 0.0025177 | -0.025051 | -0.022828 | 0.066934 | -0.030443 | -0.048031 | -0.041033 | -0.0051575 | -0.01904 | 0.055345 | 0.051389 | -0.21766 | -0.014924 | -0.021117 | -7.7774 | 61.9629 | -60.585 | 61.8484 | -59.9075 | -60.6308 | -60.6537 | 0.036621 | 61.8668 | -60.4935 | 61.9583 | -60.4156 | -60.5347 | -60.4111 | -0.14191 | 0.041199 | -0.073242 | 0.53558 | -0.21057 | -0.18768 | -0.068665 | -0.045776 | -0.050354 | -0.054932 | 0.036621 | 0.027466 | 0.032043 | -0.091553 | 0.082397 | -0.041199 | 0.67749 | 122.4335 | 0.07782 | 122.4518 | 122.5479 | 122.3602 | 122.406 | 122.3099 | -122.5067 | -122.4152 | 122.2916 | 122.4014 | 52.6657 | 60.4797
961.2812 | 122.5113 | -60.466 | 61.972 | -0.012741 | -0.026974 | -0.024964 | 0.064371 | -0.031084 | -0.048245 | -0.041246 | 0.00094606 | -0.019681 | 0.058123 | 0.046903 | -0.21616 | -0.016633 | -0.020689 | -7.9147 | 61.9308 | -60.6216 | 61.7844 | -59.9533 | -60.6674 | -60.672 | -0.036621 | 61.8896 | -60.5072 | 61.9171 | -60.4202 | -60.5209 | -60.4477 | -0.15564 | -0.041199 | -0.18768 | 0.5127 | -0.20599 | -0.20142 | -0.050354 | -0.045776 | -0.041199 | -0.082398 | -0.054932 | 0.045776 | 0.01831 | -0.054932 | 0.059509 | -0.013733 | 0.66833 | 122.406 | 0.086975 | 122.4243 | 122.5525 | 122.3969 | 122.3969 | 122.3557 | -122.5937 | -122.4792 | 122.2504 | 122.3831 | 52.5513 | 60.4294
963.0781 | 122.5388 | -60.3745 | 62.0087 | 0.0025177 | -0.025479 | -0.025818 | 0.06373 | -0.030657 | -0.047177 | -0.038683 | -0.0021057 | -0.019681 | 0.055986 | 0.051176 | -0.21595 | -0.013642 | -0.022826 | -8.1253 | 62.0407 | -60.5072 | 61.9034 | -59.8343 | -60.553 | -60.5896 | -0.013733 | 61.9629 | -60.4019 | 62.0361 | -60.3195 | -60.4477 | -60.3378 | -0.13275 | 0.032043 | -0.10529 | 0.54016 | -0.21515 | -0.17853 | -0.082398 | -0.045777 | -0.027466 | -0.045776 | 0.027466 | 0.054932 | 0.036621 | -0.073242 | 0.064087 | -0.045776 | 0.67291 | 122.4106 | 0.082398 | 122.4381 | 122.5479 | 122.3648 | 122.4152 | 122.3373 | -122.5159 | -122.4106 | 122.2778 | 122.4106 | 52.2491 | 60.3607
964.8594 | 122.644 | -60.3195 | 61.9858 | 0.010147 | -0.029965 | -0.025605 | 0.06138 | -0.035357 | -0.049099 | -0.042528 | -0.0021057 | -0.021604 | 0.054918 | 0.050962 | -0.21531 | -0.016205 | -0.024107 | -7.4982 | 61.9858 | -60.4843 | 61.9812 | -59.6603 | -60.4431 | -60.4614 | 0.064087 | 61.94 | -60.3745 | 62.1277 | -60.1913 | -60.2966 | -60.2463 | -0.16479 | 0 | -0.004578 | 0.65918 | -0.14191 | -0.1236 | 0.022888 | 0.041199 | -0.054932 | -0.045777 | 0.14191 | 0.12817 | 0.073242 | 0.022888 | 0.12817 | 0.07782 | 0.82397 | 122.4655 | 0.18311 | 122.5021 | 122.4701 | 122.3145 | 122.3053 | 122.2595 | -122.4701 | -122.3602 | 122.3007 | 122.4472 | 52.8214 | 60.3836
966.6562 | 122.5891 | -60.3195 | 62.0087 | -0.0051118 | -0.028683 | -0.023896 | 0.059671 | -0.034502 | -0.054013 | -0.03911 | 0.00094606 | -0.020749 | 0.0562 | 0.040494 | -0.21702 | -0.015778 | -0.022826 | -7.7591 | 61.9995 | -60.4752 | 61.9537 | -59.7153 | -60.4889 | -60.5164 | -0.027466 | 61.9492 | -60.3516 | 62.0773 | -60.26 | -60.3516 | -60.2646 | -0.15564 | -0.009155 | -0.054932 | 0.60425 | -0.19684 | -0.16937 | -0.041198 | -0.013733 | -0.032043 | -0.059509 | 0.068665 | 0.059509 | 0.054932 | -0.032043 | 0.086975 | 0 | 0.75989 | 122.4289 | 0.091552 | 122.4289 | 122.4747 | 122.3007 | 122.319 | 122.2687 | -122.4838 | -122.3602 | 122.2733 | 122.3969 | 52.5604 | 60.2921
968.4375 | 122.6303 | -60.2921 | 62.0132 | 0.0025177 | -0.025265 | -0.023469 | 0.063516 | -0.032152 | -0.04974 | -0.038042 | 0.0039979 | -0.021176 | 0.056627 | 0.047971 | -0.21744 | -0.014069 | -0.024321 | -7.4066 | 62.0636 | -60.4202 | 62.059 | -59.6008 | -60.4111 | -60.4385 | 0.032043 | 61.9675 | -60.3287 | 62.1826 | -60.1685 | -60.2875 | -60.1776 | -0.12817 | 0.050354 | 0.045776 | 0.69122 | -0.14648 | -0.11902 | -0.018311 | 0.009155 | -0.036621 | -0.045777 | 0.16937 | 0.1236 | 0.11444 | 0.004577 | 0.15106 | 0.041198 | 0.8194 | 122.4792 | 0.16022 | 122.5113 | 122.4838 | 122.2961 | 122.3557 | 122.2595 | -122.4335 | -122.3419 | 122.3511 | 122.4747 | 52.8854 | 60.3241
970.1406 | 122.58 | -60.2646 | 62.0453 | -0.012741 | -0.02612 | -0.025391 | 0.06373 | -0.032366 | -0.048458 | -0.041033 | -0.0021057 | -0.021176 | 0.052568 | 0.048826 | -0.21979 | -0.016419 | -0.024321 | -8.0154 | 62.0544 | -60.3653 | 62.0316 | -59.61 | -60.4294 | -60.4431 | -0.036621 | 62.0087 | -60.3104 | 62.146 | -60.2234 | -60.3058 | -60.2051 | -0.10071 | 0.009155 | -0.013733 | 0.6546 | -0.17853 | -0.16479 | -0.07782 | -0.064087 | -0.045777 | -0.036621 | 0.10071 | 0.041198 | 0.059509 | -0.041199 | 0.10529 | 0.004578 | 0.75531 | 122.3969 | 0.086975 | 122.4564 | 122.4197 | 122.319 | 122.319 | 122.2733 | -122.4106 | -122.3557 | 122.2961 | 122.4106 | 52.2491 | 60.228
971.9375 | 122.58 | -60.2646 | 62.0636 | 0.0025177 | -0.022915 | -0.02475 | 0.063944 | -0.03023 | -0.047817 | -0.042742 | 0.00094606 | -0.019895 | 0.055559 | 0.045621 | -0.21787 | -0.016633 | -0.022398 | -7.9742 | 62.0773 | -60.3836 | 62.0865 | -59.5551 | -60.3973 | -60.379 | 0.036621 | 62.0224 | -60.3058 | 62.1872 | -60.173 | -60.2692 | -60.1868 | -0.11902 | 0.013733 | 0.022888 | 0.70953 | -0.11444 | -0.13275 | 0.004578 | -0.013733 | -0.041199 | -0.041199 | 0.1236 | 0.091552 | 0.077819 | -0.004578 | 0.11902 | 0.036621 | 0.82855 | 122.4701 | 0.13275 | 122.493 | 122.4609 | 122.3282 | 122.3419 | 122.287 | -122.4472 | -122.3694 | 122.3511 | 122.4518 | 52.2903 | 60.3012
973.7344 | 122.5754 | -60.1364 | 62.1872 | -0.0051118 | -0.027401 | -0.024109 | 0.064157 | -0.033648 | -0.051449 | -0.039965 | 0.0039979 | -0.019681 | 0.057054 | 0.044553 | -0.21894 | -0.017914 | -0.023894 | -7.8506 | 62.2009 | -60.2875 | 62.1552 | -59.4772 | -60.3104 | -60.3104 | -0.036621 | 62.1323 | -60.1822 | 62.2787 | -60.0952 | -60.1822 | -60.0815 | -0.15106 | 0.013733 | -0.032044 | 0.65918 | -0.17395 | -0.17395 | -0.022888 | -0.022888 | -0.045776 | -0.054932 | 0.091553 | 0.041199 | 0.054932 | -0.045776 | 0.10071 | 0 | 0.81024 | 122.4426 | 0.086975 | 122.4609 | 122.4884 | 122.3145 | 122.3373 | 122.2687 | -122.4747 | -122.3694 | 122.2916 | 122.4152 | 52.2858 | 60.0998
975.4531 | 122.5754 | -60.0403 | 62.2925 | -0.0051118 | -0.026333 | -0.02475 | 0.066934 | -0.031725 | -0.048886 | -0.039537 | 0.00094606 | -0.019254 | 0.057054 | 0.052885 | -0.21915 | -0.016419 | -0.023894 | -8.3359 | 62.352 | -60.2005 | 62.2192 | -59.436 | -60.2737 | -60.2737 | -0.032043 | 62.2833 | -60.1181 | 62.3795 | -59.9945 | -60.1273 | -60.0082 | -0.16022 | 0.05951 | -0.073242 | 0.60425 | -0.23346 | -0.23346 | -0.073243 | -0.073243 | -0.07782 | -0.009155 | 0.086976 | 0.045776 | 0.032043 | -0.086975 | 0.10986 | -0.009155 | 0.76447 | 122.4197 | 0.1236 | 122.4976 | 122.5525 | 122.4014 | 122.3923 | 122.3236 | -122.493 | -122.4106 | 122.2595 | 122.4197 | 51.7044 | 60.0082
977.2344 | 122.6349 | -60.022 | 62.3199 | -0.0051118 | -0.027401 | -0.026032 | 0.062448 | -0.03557 | -0.048458 | -0.042314 | 0.00094606 | -0.021176 | 0.055132 | 0.040708 | -0.21659 | -0.016419 | -0.023467 | -8.2031 | 62.2879 | -60.1685 | 62.3062 | -59.2941 | -60.1181 | -60.1456 | 0.054932 | 62.2787 | -60.054 | 62.4298 | -59.903 | -59.9716 | -59.9213 | -0.14648 | -0.032043 | -0.013733 | 0.72785 | -0.1236 | -0.09613 | 0.022888 | 0.050354 | -0.032043 | -0.041198 | 0.10986 | 0.11902 | 0.10071 | 0.050354 | 0.13275 | 0.082397 | 0.87433 | 122.4747 | 0.15106 | 122.4838 | 122.4564 | 122.3328 | 122.3099 | 122.3007 | -122.4884 | -122.374 | 122.3282 | 122.4518 | 51.8188 | 60.0769
978.9688 | 122.644 | -59.9945 | 62.3337 | -0.0051118 | -0.02676 | -0.025177 | 0.063944 | -0.033648 | -0.048245 | -0.037828 | 0.0039979 | -0.021817 | 0.055773 | 0.050321 | -0.21808 | -0.017273 | -0.023039 | -8.2123 | 62.3291 | -60.1501 | 62.3657 | -59.2117 | -60.0861 | -60.1181 | 0.1236 | 62.2559 | -60.022 | 62.4985 | -59.8389 | -59.9442 | -59.8755 | -0.15564 | -0.004577 | 0.032044 | 0.78278 | -0.1236 | -0.091553 | 0.032043 | 0.064086 | -0.027466 | -0.07782 | 0.1648 | 0.15564 | 0.11902 | 0.050354 | 0.14649 | 0.07782 | 0.93841 | 122.5159 | 0.18311 | 122.5204 | 122.4792 | 122.2778 | 122.3236 | 122.2504 | -122.4838 | -122.3557 | 122.3602 | 122.493 | 51.7822 | 60.1181
980.7656 | 122.5754 | -59.9579 | 62.3932 | 0.0025177 | -0.027401 | -0.025391 | 0.06373 | -0.032366 | -0.049313 | -0.04146 | -0.0021057 | -0.020536 | 0.054277 | 0.051603 | -0.21702 | -0.016205 | -0.022826 | -8.7021 | 62.3611 | -60.0998 | 62.2971 | -59.2896 | -60.141 | -60.1364 | -0.054932 | 62.3245 | -60.022 | 62.4481 | -59.8938 | -59.9945 | -59.903 | -0.14191 | -0.032043 | -0.09613 | 0.66833 | -0.17853 | -0.1831 | -0.036622 | -0.041199 | -0.064087 | -0.068664 | 0.054932 | 0.064087 | 0.054932 | -0.036621 | 0.11902 | 0.027466 | 0.81024 | 122.3969 | 0.12817 | 122.4701 | 122.4609 | 122.3465 | 122.319 | 122.2824 | -122.493 | -122.4152 | 122.2549 | 122.406 | 51.2558 | 59.903
982.5625 | 122.5433 | -60.022 | 62.3703 | -0.0051118 | -0.025265 | -0.025391 | 0.065012 | -0.030016 | -0.051022 | -0.038469 | 0.00094606 | -0.017331 | 0.055559 | 0.050748 | -0.21766 | -0.016205 | -0.021971 | -8.4595 | 62.3474 | -60.1685 | 62.2925 | -59.3079 | -60.1685 | -60.1822 | 0.041199 | 62.3291 | -60.0586 | 62.4115 | -59.9396 | -60.0723 | -59.9716 | -0.14648 | -0.022888 | -0.07782 | 0.71411 | -0.16022 | -0.14648 | -0.013733 | 0 | -0.036621 | -0.041198 | 0.041199 | 0.082398 | 0.050354 | -0.050354 | 0.086975 | -0.013733 | 0.8606 | 122.4609 | 0.11902 | 122.4701 | 122.5159 | 122.3877 | 122.3694 | 122.3511 | -122.5388 | -122.4289 | 122.3145 | 122.4335 | 51.5625 | 60.0632
984.3594 | 122.6257 | -59.8663 | 62.4252 | 0.0025177 | -0.024197 | -0.023255 | 0.065225 | -0.032152 | -0.049313 | -0.039965 | -0.0021057 | -0.020963 | 0.055132 | 0.047544 | -0.21766 | -0.015565 | -0.025176 | -8.4412 | 62.4435 | -60.0037 | 62.439 | -59.1156 | -60.022 | -60.0311 | 0.013733 | 62.3657 | -59.9487 | 62.5671 | -59.7885 | -59.9075 | -59.7931 | -0.13733 | 0.01831 | 0.013733 | 0.75073 | -0.1648 | -0.15564 | -0.027466 | -0.018311 | -0.082397 | -0.059509 | 0.14191 | 0.07782 | 0.073242 | -0.041199 | 0.15564 | 0.041198 | 0.88806 | 122.4426 | 0.16022 | 122.5159 | 122.4472 | 122.3145 | 122.3099 | 122.2321 | -122.4289 | -122.374 | 122.3053 | 122.4335 | 51.4252 | 59.8801
986.0625 | 122.612 | -59.9213 | 62.384 | -0.012741 | -0.025265 | -0.023682 | 0.064585 | -0.034502 | -0.051022 | -0.04146 | 0.00094606 | -0.022672 | 0.055986 | 0.046903 | -0.21808 | -0.015778 | -0.023467 | -8.2397 | 62.3886 | -60.0677 | 62.4207 | -59.0927 | -60.0174 | -60.0311 | 0.086975 | 62.3291 | -59.9442 | 62.5168 | -59.8022 | -59.8984 | -59.8434 | -0.14648 | 0.004578 | 0.036621 | 0.82855 | -0.10986 | -0.09613 | 0.036621 | 0.050354 | -0.022888 | -0.054931 | 0.13275 | 0.11902 | 0.07782 | 0.022889 | 0.10071 | 0.045777 | 0.97504 | 122.4884 | 0.14191 | 122.4609 | 122.4564 | 122.2733 | 122.3099 | 122.2504 | -122.4518 | -122.3282 | 122.3419 | 122.4381 | 51.6815 | 60.0082
987.8438 | 122.5021 | -59.8251 | 62.5351 | -0.0051118 | -0.022061 | -0.024109 | 0.066934 | -0.034502 | -0.046749 | -0.038256 | -0.0021057 | -0.019254 | 0.053423 | 0.053953 | -0.21808 | -0.015778 | -0.022398 | -8.5281 | 62.5626 | -59.9716 | 62.4435 | -59.0836 | -60.022 | -60.0357 | 0 | 62.4847 | -59.8846 | 62.558 | -59.8206 | -59.9487 | -59.8206 | -0.14648 | 0.027466 | -0.091553 | 0.74158 | -0.21057 | -0.19684 | -0.064087 | -0.050354 | -0.05951 | -0.050354 | 0.022888 | 0.004577 | 0.004577 | -0.1236 | 0.064087 | -0.064086 | 0.88806 | 122.4152 | 0.064087 | 122.4426 | 122.5342 | 122.3694 | 122.3877 | 122.3099 | -122.5067 | -122.4197 | 122.2687 | 122.3831 | 51.297 | 59.8251
989.6406 | 122.5388 | -59.8114 | 62.5809 | 0.0025177 | -0.025051 | -0.024109 | 0.066294 | -0.025957 | -0.049099 | -0.038256 | 0.00094606 | -0.019895 | 0.056627 | 0.04434 | -0.21702 | -0.015778 | -0.024535 | -8.5556 | 62.59 | -59.9533 | 62.4802 | -59.0561 | -59.9762 | -59.9899 | 0 | 62.5351 | -59.848 | 62.59 | -59.7565 | -59.8801 | -59.7794 | -0.14191 | 0.009155 | -0.10071 | 0.75531 | -0.17853 | -0.1648 | -0.036621 | -0.022888 | -0.036621 | -0.045777 | 0.009155 | 0.054931 | 0.032043 | -0.068665 | 0.068664 | -0.032044 | 0.89722 | 122.4335 | 0.091552 | 122.438 | 122.5433 | 122.3831 | 122.4014 | 122.3465 | -122.5342 | -122.4289 | 122.2916 | 122.4014 | 51.2558 | 59.8114
991.3594 | 122.612 | -59.7565 | 62.5763 | -0.012741 | -0.028469 | -0.024537 | 0.064157 | -0.028521 | -0.049099 | -0.038896 | 0.00094606 | -0.023313 | 0.054705 | 0.047544 | -0.21637 | -0.016633 | -0.027953 | -8.5648 | 62.5626 | -59.8755 | 62.5992 | -58.8684 | -59.848 | -59.8389 | 0.07782 | 62.5259 | -59.7931 | 62.6953 | -59.6237 | -59.7382 | -59.6603 | -0.11902 | -0.013733 | 0.022888 | 0.88806 | -0.082397 | -0.091552 | 0.036621 | 0.027466 | -0.036621 | -0.050354 | 0.11902 | 0.13275 | 0.096131 | 0.018311 | 0.13275 | 0.054932 | 1.0071 | 122.4747 | 0.16937 | 122.4884 | 122.438 | 122.319 | 122.319 | 122.2824 | -122.4518 | -122.3694 | 122.3557 | 122.4518 | 51.1917 | 59.8343
993.1562 | 122.5204 | -59.729 | 62.6129 | 0.0025177 | -0.025051 | -0.024537 | 0.065225 | -0.02553 | -0.047817 | -0.040605 | 0.0039979 | -0.018613 | 0.054491 | 0.049894 | -0.2168 | -0.015565 | -0.021971 | -8.4 | 62.645 | -59.8572 | 62.558 | -58.9096 | -59.903 | -59.9167 | 0.018311 | 62.5763 | -59.7977 | 62.6633 | -59.6924 | -59.8114 | -59.6924 | -0.12817 | 0.032043 | -0.054932 | 0.8194 | -0.18768 | -0.17395 | -0.059509 | -0.045776 | -0.068664 | -0.036621 | 0.050354 | 0.036621 | 0.036621 | -0.082397 | 0.10529 | -0.013733 | 0.94757 | 122.4152 | 0.10529 | 122.4609 | 122.5021 | 122.374 | 122.374 | 122.3053 | -122.4701 | -122.4106 | 122.287 | 122.3923 | 51.329 | 59.7473
994.9531 | 122.5021 | -59.6695 | 62.7365 | -0.0051118 | -0.02676 | -0.024537 | 0.06138 | -0.033007 | -0.048672 | -0.039324 | -0.0021057 | -0.01904 | 0.056627 | 0.043272 | -0.21488 | -0.01471 | -0.01834 | -8.8943 | 62.7045 | -59.8114 | 62.645 | -58.8135 | -59.7839 | -59.7931 | 0.022888 | 62.6541 | -59.7061 | 62.7182 | -59.6146 | -59.7244 | -59.6558 | -0.14191 | -0.032043 | -0.091553 | 0.85602 | -0.1236 | -0.11444 | 0.01831 | 0.027465 | -0.036621 | -0.082397 | -0.01831 | 0.054932 | 0.013733 | -0.054931 | 0.050354 | -0.01831 | 0.99792 | 122.4564 | 0.091553 | 122.4243 | 122.5159 | 122.3602 | 122.374 | 122.3236 | -122.5479 | -122.4426 | 122.3145 | 122.3877 | 50.7751 | 59.6924
996.6875 | 122.5891 | -59.6832 | 62.6404 | -0.0051118 | -0.026974 | -0.025818 | 0.062662 | -0.029375 | -0.049099 | -0.03911 | -0.0021057 | -0.022672 | 0.055345 | 0.045194 | -0.2168 | -0.015137 | -0.025176 | -8.4915 | 62.6221 | -59.816 | 62.6633 | -58.7723 | -59.761 | -59.7656 | 0.068665 | 62.5946 | -59.7519 | 62.7411 | -59.5779 | -59.6558 | -59.5963 | -0.13275 | -0.018311 | 0.022888 | 0.91095 | -0.082397 | -0.077819 | 0.050354 | 0.054932 | -0.068664 | -0.045777 | 0.10071 | 0.10529 | 0.086976 | 0.027466 | 0.15564 | 0.09613 | 1.0437 | 122.4792 | 0.17395 | 122.493 | 122.438 | 122.3465 | 122.3053 | 122.2778 | -122.4564 | -122.3923 | 122.3465 | 122.4243 | 51.1917 | 59.7519
998.4844 | 122.58 | -59.523 | 62.7914 | 0.0025177 | -0.025479 | -0.024109 | 0.065225 | -0.029375 | -0.049526 | -0.038469 | 0.00094606 | -0.021176 | 0.05385 | 0.046689 | -0.21766 | -0.016846 | -0.024962 | -8.844 | 62.7594 | -59.6741 | 62.7365 | -58.6349 | -59.6878 | -59.6786 | -0.018311 | 62.7182 | -59.5917 | 62.8784 | -59.4772 | -59.5688 | -59.4772 | -0.15106 | -0.032044 | -0.054932 | 0.88806 | -0.15564 | -0.16479 | -0.004578 | -0.013733 | -0.068665 | -0.073242 | 0.086975 | 0.045776 | 0.045776 | -0.045777 | 0.11444 | 0.022888 | 1.0391 | 122.4106 | 0.11444 | 122.4701 | 122.4335 | 122.3099 | 122.2824 | 122.2412 | -122.4655 | -122.3831 | 122.2595 | 122.4014 | 50.679 | 59.5047
1000.2656 | 122.525 | -59.436 | 62.9425 | -0.012741 | -0.027401 | -0.023255 | 0.065866 | -0.031084 | -0.050381 | -0.042528 | -0.0051575 | -0.018399 | 0.057054 | 0.046476 | -0.21958 | -0.013642 | -0.025176 | -9.1507 | 62.915 | -59.6237 | 62.7686 | -58.6487 | -59.6283 | -59.6741 | -0.045776 | 62.883 | -59.4818 | 62.9333 | -59.4223 | -59.5276 | -59.4315 | -0.18768 | -0.027466 | -0.17395 | 0.78735 | -0.23804 | -0.19226 | -0.050354 | -0.004578 | -0.045777 | -0.059509 | -0.009155 | 0.013733 | 0.004577 | -0.091553 | 0.050354 | -0.045776 | 0.97504 | 122.3923 | 0.05951 | 122.4152 | 122.5388 | 122.3648 | 122.3511 | 122.319 | -122.5662 | -122.4243 | 122.2046 | 122.3694 | 50.2853 | 59.3903
1002.0625 | 122.5983 | -59.5139 | 62.8189 | -0.0051118 | -0.025265 | -0.025605 | 0.064585 | -0.03023 | -0.049954 | -0.041887 | 0.0039979 | -0.02139 | 0.054491 | 0.049894 | -0.21851 | -0.016633 | -0.022398 | -9.05 | 62.8189 | -59.6558 | 62.7594 | -58.6075 | -59.6512 | -59.6466 | -0.022888 | 62.7457 | -59.5688 | 62.9059 | -59.4223 | -59.5276 | -59.4452 | -0.14191 | 0 | -0.05951 | 0.90637 | -0.13275 | -0.13733 | 0.009156 | 0.004578 | -0.054932 | -0.073242 | 0.086975 | 0.091553 | 0.068665 | -0.013733 | 0.1236 | 0.041199 | 1.0483 | 122.4152 | 0.14648 | 122.4747 | 122.4747 | 122.3145 | 122.3328 | 122.2595 | -122.4747 | -122.3877 | 122.2733 | 122.4197 | 50.4639 | 59.491
1003.7812 | 122.4609 | -59.4406 | 62.9562 | -0.012741 | -0.022915 | -0.022187 | 0.066721 | -0.03023 | -0.047604 | -0.041246 | 0.00094606 | -0.018399 | 0.055986 | 0.051816 | -0.2183 | -0.013001 | -0.02133 | -8.8257 | 62.9562 | -59.5963 | 62.7731 | -58.6075 | -59.6832 | -59.6878 | -0.1236 | 62.8876 | -59.5139 | 62.8922 | -59.5001 | -59.6146 | -59.4818 | -0.15564 | 0 | -0.18311 | 0.83313 | -0.24719 | -0.24262 | -0.091553 | -0.086976 | -0.073242 | -0.068665 | -0.064087 | -0.059509 | -0.041199 | -0.17395 | 0.032043 | -0.10071 | 0.98877 | 122.3694 | 0.013733 | 122.406 | 122.5525 | 122.4014 | 122.3969 | 122.3282 | -122.5525 | -122.4701 | 122.2137 | 122.3328 | 50.6149 | 59.317
1005.5781 | 122.5021 | -59.2804 | 63.121 | -0.0051118 | -0.021206 | -0.022828 | 0.066294 | -0.02788 | -0.047604 | -0.040605 | 0.00094606 | -0.017972 | 0.056414 | 0.04733 | -0.2168 | -0.013856 | -0.021544 | -9.2056 | 63.1439 | -59.4086 | 62.915 | -58.4427 | -59.5505 | -59.5367 | -0.10529 | 63.0615 | -59.3216 | 63.0936 | -59.3124 | -59.4223 | -59.2941 | -0.12817 | 0.022888 | -0.20599 | 0.83771 | -0.25635 | -0.27008 | -0.12817 | -0.14191 | -0.041198 | -0.05951 | -0.027466 | -0.032043 | -0.013732 | -0.14191 | 0.027466 | -0.10071 | 0.96588 | 122.3236 | 0.009155 | 122.4152 | 122.5525 | 122.3831 | 122.4243 | 122.3419 | -122.5296 | -122.4426 | 122.1954 | 122.374 | 50.0748 | 59.1751
1007.375 | 122.5342 | -59.3262 | 63.1027 | 0.010147 | -0.02377 | -0.026032 | 0.065012 | -0.033434 | -0.049526 | -0.038896 | -0.0021057 | -0.018827 | 0.057482 | 0.044553 | -0.2168 | -0.01706 | -0.023467 | -9.3109 | 63.1073 | -59.4131 | 62.9791 | -58.342 | -59.436 | -59.4818 | -0.004578 | 63.0157 | -59.3491 | 63.0844 | -59.2392 | -59.3719 | -59.2667 | -0.086975 | 0.004578 | -0.1236 | 0.98419 | -0.15564 | -0.10986 | -0.068665 | -0.022888 | -0.022888 | -0.086975 | -0.01831 | 0.086975 | 0.059509 | -0.045776 | 0.082397 | -0.022888 | 1.0712 | 122.3923 | 0.10986 | 122.4335 | 122.5204 | 122.3648 | 122.4335 | 122.3419 | -122.5159 | -122.4518 | 122.3053 | 122.4106 | 50.0153 | 59.3216
1009.1719 | 122.5662 | -59.2117 | 63.1119 | -0.0051118 | -0.02612 | -0.0224 | 0.064157 | -0.032366 | -0.049099 | -0.039324 | -0.0051575 | -0.023313 | 0.054491 | 0.041776 | -0.21509 | -0.016419 | -0.024748 | -9.3384 | 63.1027 | -59.3536 | 63.0798 | -58.1955 | -59.3491 | -59.3353 | -0.064087 | 63.0569 | -59.2529 | 63.1897 | -59.1568 | -59.2575 | -59.1797 | -0.14191 | -0.009155 | -0.032043 | 1.0162 | -0.1236 | -0.13733 | 0.018311 | 0.004578 | -0.041199 | -0.054931 | 0.07782 | 0.054932 | 0.032044 | -0.045776 | 0.073243 | -0.004577 | 1.1581 | 122.4335 | 0.096131 | 122.4426 | 122.4564 | 122.3099 | 122.3145 | 122.2687 | -122.4655 | -122.3648 | 122.2916 | 122.4014 | 49.8734 | 59.1476
1010.9062 | 122.5342 | -59.166 | 63.2217 | -0.0051118 | -0.023556 | -0.023469 | 0.066721 | -0.031511 | -0.050381 | -0.038683 | -0.0051575 | -0.019681 | 0.057268 | 0.050962 | -0.21894 | -0.013215 | -0.024748 | -9.5947 | 63.2034 | -59.3079 | 63.1302 | -58.1223 | -59.2896 | -59.3353 | 0.032043 | 63.1485 | -59.198 | 63.2492 | -59.111 | -59.2163 | -59.1156 | -0.14191 | -0.018311 | -0.091553 | 1.0437 | -0.16937 | -0.1236 | -0.027466 | 0.01831 | -0.032043 | -0.073242 | 0.027466 | 0.054932 | 0.050354 | -0.050354 | 0.082397 | -0.018311 | 1.1856 | 122.438 | 0.086975 | 122.4472 | 122.5113 | 122.3465 | 122.3694 | 122.3145 | -122.5296 | -122.4197 | 122.2961 | 122.4152 | 49.5712 | 59.198
1012.6875 | 122.6166 | -59.079 | 63.2263 | 0.0025177 | -0.024624 | -0.022187 | 0.064157 | -0.031084 | -0.051663 | -0.039965 | -0.0051575 | -0.020322 | 0.056841 | 0.046049 | -0.21723 | -0.014924 | -0.020476 | -9.6588 | 63.2629 | -59.2255 | 63.2355 | -57.9895 | -59.1888 | -59.2072 | 0.004578 | 63.176 | -59.1156 | 63.3682 | -58.992 | -59.1019 | -58.9691 | -0.14649 | 0.036621 | 0.009156 | 1.0895 | -0.12817 | -0.10986 | 0.018311 | 0.036621 | -0.036622 | -0.050354 | 0.14191 | 0.086975 | 0.10986 | -0.022889 | 0.14648 | 0.013733 | 1.236 | 122.4609 | 0.1236 | 122.4838 | 122.4884 | 122.2916 | 122.3419 | 122.2549 | -122.4518 | -122.3419 | 122.3145 | 122.4472 | 49.4202 | 59.0836
1014.4688 | 122.4838 | -59.0836 | 63.2904 | 0.0025177 | -0.024411 | -0.023469 | 0.065653 | -0.027239 | -0.046963 | -0.039324 | -0.0082091 | -0.019254 | 0.0562 | 0.054807 | -0.21808 | -0.015565 | -0.024535 | -10.0662 | 63.2996 | -59.2484 | 63.1805 | -58.0444 | -59.2621 | -59.2712 | -0.054932 | 63.2446 | -59.1339 | 63.2675 | -59.1064 | -59.2346 | -59.0744 | -0.16479 | 0.009156 | -0.10986 | 1.0391 | -0.18768 | -0.17853 | -0.022888 | -0.013733 | -0.050354 | -0.045776 | -0.022888 | -0.022888 | 0.009155 | -0.15106 | 0.059509 | -0.10071 | 1.2039 | 122.4289 | 0.027466 | 122.4014 | 122.5479 | 122.3785 | 122.3831 | 122.3282 | -122.5388 | -122.4243 | 122.2641 | 122.3511 | 49.0173 | 59.0286
1016.1719 | 122.4747 | -59.1614 | 63.2492 | -0.0051118 | -0.022915 | -0.0224 | 0.06608 | -0.030657 | -0.044613 | -0.038683 | 0.00094606 | -0.01904 | 0.057482 | 0.051176 | -0.21467 | -0.014496 | -0.024321 | -9.9426 | 63.2401 | -59.2667 | 63.089 | -58.168 | -59.3491 | -59.3674 | -0.13733 | 63.1714 | -59.166 | 63.208 | -59.1705 | -59.2941 | -59.1614 | -0.10529 | -0.009156 | -0.16022 | 0.99335 | -0.20599 | -0.18768 | -0.10071 | -0.082397 | -0.004578 | -0.07782 | -0.041199 | -0.009155 | 0 | -0.13275 | 0.004578 | -0.12817 | 1.0986 | 122.3557 | -0.004577 | 122.374 | 122.5067 | 122.3373 | 122.4014 | 122.3328 | -122.5159 | -122.4152 | 122.2504 | 122.3694 | 49.2188 | 59.024
1017.9531 | 122.4655 | -59.0515 | 63.3453 | -0.0051118 | -0.023129 | -0.023682 | 0.063944 | -0.028521 | -0.04974 | -0.041033 | -0.0021057 | -0.019254 | 0.057054 | 0.045621 | -0.21915 | -0.015992 | -0.020903 | -10.0525 | 63.3682 | -59.1843 | 63.1714 | -58.0582 | -59.2392 | -59.2804 | -0.13275 | 63.2858 | -59.1019 | 63.2996 | -59.0652 | -59.1797 | -59.0378 | -0.13275 | 0.022888 | -0.17395 | 0.99335 | -0.22888 | -0.18768 | -0.096131 | -0.054932 | -0.050354 | -0.059509 | -0.045776 | -0.013733 | 0.013733 | -0.12817 | 0.064087 | -0.077819 | 1.1261 | 122.3557 | 0.036621 | 122.4014 | 122.5525 | 122.3877 | 122.4197 | 122.3373 | -122.5296 | -122.4472 | 122.2229 | 122.3511 | 48.999 | 58.9188
1019.75 | 122.6028 | -59.0378 | 63.2492 | 0.0025177 | -0.025265 | -0.023896 | 0.064585 | -0.027666 | -0.047817 | -0.04146 | -0.0021057 | -0.020536 | 0.055986 | 0.052671 | -0.21659 | -0.01471 | -0.023467 | -9.9197 | 63.3316 | -59.1614 | 63.2675 | -57.9163 | -59.1202 | -59.1751 | -0.004578 | 63.208 | -59.079 | 63.4232 | -58.9462 | -59.0561 | -58.9188 | -0.1236 | 0.082397 | 0.01831 | 1.1215 | -0.13733 | -0.082397 | -0.013733 | 0.041199 | -0.041198 | -0.041199 | 0.17395 | 0.091553 | 0.11902 | -0.01831 | 0.16022 | 0.022888 | 1.2451 | 122.4289 | 0.13275 | 122.5021 | 122.493 | 122.287 | 122.3694 | 122.2458 | -122.4106 | -122.3282 | 122.3053 | 122.4609 | 49.118 | 59.0332
1021.4844 | 122.4792 | -58.9966 | 63.4094 | -0.012741 | -0.023129 | -0.023041 | 0.065866 | -0.029802 | -0.046749 | -0.040178 | -0.0021057 | -0.020536 | 0.058123 | 0.046262 | -0.22001 | -0.01471 | -0.019621 | -9.8877 | 63.446 | -59.1019 | 63.2904 | -57.9025 | -59.1476 | -59.166 | -0.064087 | 63.3682 | -58.9874 | 63.3865 | -58.9874 | -59.0927 | -58.9691 | -0.10529 | 0.036621 | -0.11902 | 1.0941 | -0.16937 | -0.15106 | -0.064087 | -0.045776 | 0.009155 | -0.041199 | -0.022888 | 0.009155 | 0.027466 | -0.09613 | 0.018311 | -0.10529 | 1.1993 | 122.3923 | 0 | 122.374 | 122.5479 | 122.3557 | 122.4426 | 122.3648 | -122.5113 | -122.3969 | 122.287 | 122.3831 | 49.1089 | 58.9325
1023.2969 | 122.4976 | -58.9645 | 63.414 | -0.012741 | -0.025692 | -0.024964 | 0.062235 | -0.02788 | -0.050381 | -0.039324 | 0.0039979 | -0.019467 | 0.055773 | 0.047971 | -0.21766 | -0.015778 | -0.018767 | -10.0662 | 63.4323 | -59.1064 | 63.2629 | -57.9163 | -59.1156 | -59.1522 | -0.054932 | 63.3865 | -59.0103 | 63.3774 | -58.9783 | -59.0607 | -58.9645 | -0.14191 | 0.018311 | -0.15106 | 1.0483 | -0.18768 | -0.15106 | -0.045777 | -0.009156 | -0.045776 | -0.027465 | -0.036621 | -0.013732 | 0 | -0.09613 | 0.045776 | -0.050354 | 1.1902 | 122.3694 | 0.032044 | 122.3877 | 122.5388 | 122.3969 | 122.3969 | 122.3511 | -122.5204 | -122.4243 | 122.2275 | 122.3419 | 48.8983 | 58.9096
1025.0156 | 122.525 | -58.9279 | 63.4277 | 0.0025177 | -0.025479 | -0.024964 | 0.062235 | -0.02788 | -0.049954 | -0.039751 | -0.0021057 | -0.021817 | 0.057268 | 0.043058 | -0.21766 | -0.015992 | -0.023894 | -9.9106 | 63.4232 | -59.0652 | 63.3774 | -57.7744 | -58.9828 | -59.0149 | 0.013733 | 63.382 | -58.9554 | 63.4506 | -58.873 | -58.96 | -58.873 | -0.13733 | -0.004577 | -0.050354 | 1.1536 | -0.086976 | -0.054932 | 0.050354 | 0.082398 | -0.027466 | -0.045776 | 0.022889 | 0.054931 | 0.054931 | -0.032044 | 0.082397 | -0.004578 | 1.2909 | 122.4426 | 0.082397 | 122.406 | 122.4884 | 122.3373 | 122.3511 | 122.3099 | -122.493 | -122.3831 | 122.3053 | 122.3785 | 49.0173 | 58.9417
1026.7969 | 122.5983 | -58.7952 | 63.5147 | -0.0051118 | -0.025479 | -0.023255 | 0.062448 | -0.031511 | -0.047604 | -0.039324 | -0.0082091 | -0.020322 | 0.055559 | 0.044126 | -0.2168 | -0.015351 | -0.021758 | -9.9838 | 63.4827 | -58.9508 | 63.4964 | -57.6553 | -58.8821 | -58.9188 | 0.041199 | 63.4277 | -58.873 | 63.5788 | -58.7265 | -58.8272 | -58.7448 | -0.15564 | -0.032043 | -0.01831 | 1.1398 | -0.1236 | -0.086975 | 0.032044 | 0.068665 | -0.07782 | -0.086975 | 0.064087 | 0.068665 | 0.050354 | -0.032043 | 0.12817 | 0.045777 | 1.2955 | 122.4472 | 0.14648 | 122.4518 | 122.4335 | 122.3007 | 122.2778 | 122.2229 | -122.4655 | -122.3877 | 122.2916 | 122.374 | 48.8113 | 58.8364
1028.5938 | 122.5937 | -58.7357 | 63.6063 | 0.0025177 | -0.029965 | -0.02475 | 0.064371 | -0.034075 | -0.048458 | -0.040819 | -0.0051575 | -0.020963 | 0.055345 | 0.047971 | -0.21894 | -0.016205 | -0.023467 | -9.9701 | 63.5284 | -58.9233 | 63.5788 | -57.5546 | -58.8089 | -58.8409 | 0.050354 | 63.5376 | -58.7997 | 63.6658 | -58.6441 | -58.7494 | -58.6807 | -0.18768 | -0.07782 | -0.027466 | 1.181 | -0.10528 | -0.073242 | 0.082398 | 0.11444 | -0.064087 | -0.068664 | 0.059509 | 0.091553 | 0.054932 | -0.013733 | 0.11902 | 0.050354 | 1.3687 | 122.5021 | 0.15564 | 122.4655 | 122.4518 | 122.3373 | 122.2641 | 122.2733 | -122.5296 | -122.406 | 122.3145 | 122.4014 | 48.7656 | 58.786
1030.375 | 122.4884 | -58.8455 | 63.5925 | -0.0051118 | -0.024197 | -0.023255 | 0.06843 | -0.030657 | -0.051022 | -0.040178 | -0.0051575 | -0.017758 | 0.056627 | 0.047971 | -0.21787 | -0.014496 | -0.020476 | -9.993 | 63.5559 | -58.96 | 63.4415 | -57.7423 | -58.9645 | -58.9874 | -0.041199 | 63.5101 | -58.8593 | 63.5376 | -58.8318 | -58.9417 | -58.8043 | -0.11444 | -0.036621 | -0.15106 | 1.1032 | -0.14191 | -0.11902 | -0.027466 | -0.004578 | -0.013733 | -0.082397 | -0.054931 | 0.013733 | 0.041199 | -0.09613 | 0.054932 | -0.082397 | 1.2177 | 122.4014 | 0.027466 | 122.3969 | 122.5159 | 122.3694 | 122.4014 | 122.3557 | -122.5525 | -122.4518 | 122.287 | 122.3831 | 48.8525 | 58.8043
1032.1562 | 122.493 | -58.7219 | 63.6566 | 0.0025177 | -0.022488 | -0.022828 | 0.067575 | -0.030657 | -0.04739 | -0.04381 | -0.0051575 | -0.018186 | 0.056627 | 0.045194 | -0.2168 | -0.015778 | -0.021544 | -10.1898 | 63.6887 | -58.8638 | 63.4872 | -57.6645 | -58.9279 | -58.9279 | -0.13733 | 63.5925 | -58.7814 | 63.62 | -58.7585 | -58.8776 | -58.7311 | -0.14191 | 0.032044 | -0.16937 | 1.0574 | -0.20599 | -0.20599 | -0.064086 | -0.064086 | -0.059509 | -0.064087 | -0.036621 | -0.036621 | -0.009155 | -0.15564 | 0.050354 | -0.09613 | 1.1993 | 122.3511 | 0.022888 | 122.4014 | 122.5525 | 122.374 | 122.4106 | 122.3145 | -122.5204 | -122.438 | 122.2092 | 122.3419 | 48.5321 | 58.5846
1033.875 | 122.5342 | -58.6395 | 63.7115 | -0.0051118 | -0.023983 | -0.023255 | 0.067789 | -0.032152 | -0.049099 | -0.03911 | 0.00094606 | -0.019681 | 0.056841 | 0.052457 | -0.2168 | -0.015137 | -0.021971 | -10.4874 | 63.7253 | -58.7997 | 63.6337 | -57.4997 | -58.754 | -58.7997 | 0.009155 | 63.6932 | -58.699 | 63.7482 | -58.5983 | -58.699 | -58.6075 | -0.16022 | 0.013733 | -0.07782 | 1.1398 | -0.16022 | -0.11444 | 0 | 0.045777 | -0.05951 | -0.018311 | 0.036621 | 0.041198 | 0.032043 | -0.05951 | 0.091553 | 0 | 1.3 | 122.4335 | 0.10071 | 122.4472 | 122.525 | 122.3923 | 122.3648 | 122.3328 | -122.5113 | -122.4106 | 122.2733 | 122.3877 | 48.1522 | 58.6487
1035.6719 | 122.5616 | -58.5846 | 63.7344 | -0.0051118 | -0.025692 | -0.023041 | 0.065012 | -0.029589 | -0.048672 | -0.037401 | 0.00094606 | -0.022031 | 0.055986 | 0.043058 | -0.21659 | -0.016419 | -0.022398 | -10.5011 | 63.8123 | -58.7402 | 63.6475 | -57.486 | -58.754 | -58.7631 | -0.10986 | 63.7161 | -58.6441 | 63.8031 | -58.5526 | -58.6761 | -58.5388 | -0.15564 | 0.07782 | -0.086975 | 1.0986 | -0.17853 | -0.16937 | -0.022889 | -0.013733 | -0.059509 | -0.018311 | 0.068665 | 0.032044 | 0.045777 | -0.091552 | 0.10529 | -0.032043 | 1.2543 | 122.3877 | 0.091553 | 122.4472 | 122.5525 | 122.3602 | 122.3969 | 122.3007 | -122.4747 | -122.3785 | 122.2321 | 122.3877 | 48.0835 | 58.4747
1037.4688 | 122.612 | -58.4702 | 63.8214 | 0.0025177 | -0.022488 | -0.019623 | 0.064371 | -0.032793 | -0.047817 | -0.038683 | -0.0021057 | -0.021604 | 0.056627 | 0.047971 | -0.21787 | -0.015351 | -0.020689 | -10.3043 | 63.8351 | -58.6029 | 63.8351 | -57.2342 | -58.5571 | -58.58 | 0.009155 | 63.7482 | -58.5251 | 63.9542 | -58.3923 | -58.4839 | -58.3923 | -0.13275 | 0.013733 | 0.013733 | 1.236 | -0.10986 | -0.086975 | 0.022888 | 0.045776 | -0.054931 | -0.073242 | 0.13275 | 0.07782 | 0.07782 | -0.013733 | 0.13275 | 0.041198 | 1.3687 | 122.438 | 0.13275 | 122.4792 | 122.438 | 122.2733 | 122.3053 | 122.2183 | -122.4243 | -122.3465 | 122.3053 | 122.4243 | 48.1659 | 58.4793
1039.25 | 122.525 | -58.4106 | 63.945 | -0.0051118 | -0.025692 | -0.023041 | 0.066294 | -0.032366 | -0.048672 | -0.038896 | 0.00094606 | -0.018399 | 0.055773 | 0.051603 | -0.21915 | -0.014496 | -0.018553 | -10.2493 | 63.9771 | -58.5571 | 63.8718 | -57.1838 | -58.5251 | -58.5617 | -0.004578 | 63.858 | -58.4747 | 63.9771 | -58.3923 | -58.5114 | -58.3878 | -0.14648 | 0.032044 | -0.073242 | 1.2268 | -0.15106 | -0.11444 | -0.004578 | 0.032044 | -0.064086 | -0.086975 | 0.032044 | 0.018311 | 0.022889 | -0.10071 | 0.086975 | -0.036622 | 1.3733 | 122.4289 | 0.082397 | 122.4518 | 122.5342 | 122.3328 | 122.3877 | 122.2687 | -122.5021 | -122.4197 | 122.2824 | 122.3877 | 48.1613 | 58.4061
1040.9688 | 122.4884 | -58.4106 | 63.9999 | 0.010147 | -0.023343 | -0.02475 | 0.067575 | -0.028521 | -0.049954 | -0.041674 | -0.0021057 | -0.017118 | 0.057268 | 0.048398 | -0.21723 | -0.014069 | -0.019621 | -10.4965 | 64.0182 | -58.5342 | 63.826 | -57.2479 | -58.5571 | -58.58 | -0.13733 | 63.9267 | -58.429 | 63.9587 | -58.4198 | -58.5434 | -58.4015 | -0.1236 | 0.018311 | -0.17395 | 1.1627 | -0.16937 | -0.14648 | -0.045776 | -0.022888 | -0.01831 | -0.073242 | -0.041199 | -0.009155 | 0.009156 | -0.13275 | 0.027466 | -0.11444 | 1.2863 | 122.3602 | 0.009155 | 122.3877 | 122.5525 | 122.3557 | 122.4289 | 122.3373 | -122.5342 | -122.4289 | 122.2366 | 122.3694 | 47.9141 | 58.2733
1042.7812 | 122.6212 | -58.2733 | 64.0549 | -0.0051118 | -0.02377 | -0.022187 | 0.064585 | -0.031725 | -0.047604 | -0.040605 | -0.0051575 | -0.021176 | 0.055986 | 0.044553 | -0.21979 | -0.016419 | -0.021544 | -10.5011 | 64.0274 | -58.3878 | 64.0503 | -56.9046 | -58.3282 | -58.3603 | 0.009155 | 63.9679 | -58.3099 | 64.183 | -58.1909 | -58.2779 | -58.168 | -0.11444 | -0.027466 | -0.004578 | 1.3687 | -0.086976 | -0.054932 | 0.027465 | 0.059509 | -0.036622 | -0.086975 | 0.12817 | 0.082397 | 0.10528 | -0.004578 | 0.14191 | 0.032044 | 1.4832 | 122.438 | 0.11902 | 122.493 | 122.4152 | 122.2778 | 122.3007 | 122.2412 | -122.4426 | -122.3648 | 122.3236 | 122.4564 | 47.7722 | 58.2825
1044.5 | 122.4792 | -58.0811 | 64.2929 | -0.0051118 | -0.023556 | -0.023041 | 0.067789 | -0.032793 | -0.049099 | -0.039751 | -0.0021057 | -0.018613 | 0.056627 | 0.048612 | -0.21637 | -0.01471 | -0.023894 | -10.4919 | 64.3112 | -58.2275 | 64.1785 | -56.8039 | -58.223 | -58.2642 | -0.07782 | 64.2563 | -58.1177 | 64.2654 | -58.1131 | -58.2184 | -58.0902 | -0.14648 | 0.01831 | -0.11444 | 1.2772 | -0.1831 | -0.14191 | -0.036621 | 0.004578 | -0.036621 | -0.036621 | -0.027466 | -0.032043 | -0.009155 | -0.13733 | 0.027466 | -0.10071 | 1.4236 | 122.406 | 0.004578 | 122.3831 | 122.5388 | 122.374 | 122.3923 | 122.3373 | -122.5204 | -122.4106 | 122.2595 | 122.3465 | 47.5891 | 58.0032
1046.2812 | 122.58 | -57.8934 | 64.4394 | 0.0025177 | -0.024411 | -0.023682 | 0.065439 | -0.035143 | -0.047817 | -0.039965 | 0.00094606 | -0.022672 | 0.052996 | 0.050962 | -0.21637 | -0.015137 | -0.022185 | -10.5881 | 64.4302 | -58.0261 | 64.3845 | -56.4789 | -57.9803 | -57.9987 | -0.050354 | 64.3845 | -57.9391 | 64.5172 | -57.843 | -57.93 | -57.8339 | -0.13275 | -0.009155 | -0.054932 | 1.4145 | -0.10529 | -0.086975 | 0.027466 | 0.045776 | -0.045776 | -0.054932 | 0.07782 | 0.050354 | 0.05951 | -0.036621 | 0.10529 | 0.009155 | 1.5472 | 122.4106 | 0.09613 | 122.4564 | 122.4564 | 122.3236 | 122.3236 | 122.2778 | -122.4655 | -122.3785 | 122.2778 | 122.4106 | 47.3053 | 57.843
1048.0938 | 122.5571 | -57.7515 | 64.6042 | -0.0051118 | -0.026547 | -0.02475 | 0.062662 | -0.032152 | -0.048031 | -0.038042 | -0.0021057 | -0.021176 | 0.055773 | 0.044126 | -0.21766 | -0.014924 | -0.024962 | -10.5606 | 64.5447 | -57.8934 | 64.5767 | -56.2912 | -57.7606 | -57.8018 | 0.032043 | 64.5309 | -57.7789 | 64.65 | -57.6874 | -57.7652 | -57.6782 | -0.14191 | -0.059509 | -0.027466 | 1.4603 | -0.050354 | -0.009155 | 0.091553 | 0.13275 | -0.027466 | -0.073242 | 0.045776 | 0.064087 | 0.073242 | -0.013733 | 0.10071 | 0.013733 | 1.6022 | 122.4701 | 0.091553 | 122.4289 | 122.4381 | 122.3099 | 122.2961 | 122.2824 | -122.4976 | -122.3831 | 122.3282 | 122.4014 | 47.1909 | 57.7835
1049.8125 | 122.5616 | -57.6279 | 64.7278 | 0.0025177 | -0.022915 | -0.023896 | 0.066721 | -0.02788 | -0.048245 | -0.039537 | -0.0051575 | -0.019681 | 0.056414 | 0.050748 | -0.21616 | -0.01471 | -0.02133 | -10.4965 | 64.7552 | -57.7606 | 64.6042 | -56.2592 | -57.7698 | -57.7881 | -0.082397 | 64.6912 | -57.692 | 64.7644 | -57.6279 | -57.7377 | -57.6141 | -0.13275 | 0.027466 | -0.1236 | 1.3687 | -0.16022 | -0.14191 | -0.027466 | -0.009155 | -0.064087 | -0.036621 | 0.036621 | 0 | 0.013733 | -0.10986 | 0.07782 | -0.045776 | 1.5015 | 122.3648 | 0.064087 | 122.4564 | 122.5159 | 122.3831 | 122.3831 | 122.319 | -122.4884 | -122.4197 | 122.2321 | 122.3923 | 47.1313 | 57.5455
1051.5938 | 122.4884 | -57.5729 | 64.8376 | 0.010147 | -0.025051 | -0.02475 | 0.062021 | -0.03258 | -0.050381 | -0.039751 | 0.0039979 | -0.022245 | 0.055345 | 0.048398 | -0.2183 | -0.013856 | -0.024321 | -10.9131 | 64.8285 | -57.724 | 64.65 | -56.1722 | -57.6645 | -57.7103 | -0.10071 | 64.769 | -57.6233 | 64.7736 | -57.5775 | -57.6691 | -57.5775 | -0.15106 | -0.009155 | -0.18768 | 1.4008 | -0.13733 | -0.091553 | 0.013733 | 0.059509 | -0.050354 | -0.068664 | -0.064086 | -0.004578 | -0.004578 | -0.09613 | 0.045776 | -0.045776 | 1.5518 | 122.374 | 0.045776 | 122.3969 | 122.5525 | 122.3923 | 122.4014 | 122.3419 | -122.5616 | -122.4609 | 122.2229 | 122.3465 | 46.6599 | 57.4722
1053.375 | 122.6212 | -57.4448 | 64.856 | 0.010147 | -0.027188 | -0.0224 | 0.061594 | -0.032366 | -0.048031 | -0.039965 | -0.0051575 | -0.02139 | 0.056414 | 0.042844 | -0.21616 | -0.015565 | -0.026244 | -10.7986 | 64.8514 | -57.6096 | 64.8605 | -55.8609 | -57.4631 | -57.4951 | 0.041199 | 64.7598 | -57.5226 | 64.9612 | -57.3578 | -57.4493 | -57.3761 | -0.16479 | -0.004578 | 0.004578 | 1.5839 | -0.050354 | -0.018311 | 0.11444 | 0.14648 | -0.07782 | -0.09613 | 0.10529 | 0.086975 | 0.068664 | -0.004578 | 0.14648 | 0.073242 | 1.7487 | 122.4701 | 0.16479 | 122.4838 | 122.4609 | 122.2824 | 122.2961 | 122.2046 | -122.4655 | -122.3785 | 122.3053 | 122.406 | 46.6461 | 57.486
1055.0938 | 122.4976 | -57.4036 | 65.0391 | 0.0025177 | -0.022488 | -0.023896 | 0.06608 | -0.031939 | -0.047177 | -0.039537 | -0.0051575 | -0.017758 | 0.0562 | 0.048826 | -0.21766 | -0.013642 | -0.02368 | -10.7666 | 65.0299 | -57.4997 | 64.8468 | -55.9158 | -57.5043 | -57.5409 | -0.13275 | 64.9796 | -57.4081 | 64.9933 | -57.4219 | -57.5272 | -57.3578 | -0.096131 | -0.009155 | -0.19226 | 1.4877 | -0.13733 | -0.10071 | -0.041199 | -0.004577 | -0.004578 | -0.059509 | -0.045776 | -0.018311 | 0.045776 | -0.1236 | 0.050354 | -0.11902 | 1.5839 | 122.3465 | -0.013733 | 122.4014 | 122.5296 | 122.3877 | 122.4335 | 122.3831 | -122.5388 | -122.4472 | 122.2504 | 122.3969 | 46.637 | 57.2708
1056.8906 | 122.4976 | -57.106 | 65.2679 | 0.0025177 | -0.02377 | -0.021973 | 0.067148 | -0.033007 | -0.049954 | -0.03911 | 0.0039979 | -0.018399 | 0.058123 | 0.053525 | -0.21808 | -0.016419 | -0.02133 | -10.524 | 65.2542 | -57.2479 | 65.126 | -55.5542 | -57.193 | -57.2662 | -0.027466 | 65.1947 | -57.1793 | 65.2451 | -57.1243 | -57.2479 | -57.1152 | -0.14191 | -0.013733 | -0.14191 | 1.5518 | -0.16022 | -0.086975 | -0.01831 | 0.054932 | -0.073242 | -0.073242 | -0.022888 | -0.018311 | -0.009155 | -0.14191 | 0.064087 | -0.068665 | 1.6937 | 122.374 | 0.054931 | 122.4243 | 122.5021 | 122.374 | 122.3602 | 122.3007 | -122.5159 | -122.4472 | 122.2321 | 122.3511 | 46.582 | 57.0786
1058.625 | 122.4884 | -57.0831 | 65.3229 | -0.0051118 | -0.024197 | -0.022828 | 0.063516 | -0.030657 | -0.048672 | -0.042101 | -0.0021057 | -0.018827 | 0.057054 | 0.04733 | -0.21702 | -0.017273 | -0.02368 | -11.0138 | 65.3091 | -57.2159 | 65.1627 | -55.5405 | -57.1747 | -57.2205 | -0.073242 | 65.2496 | -57.1243 | 65.2679 | -57.1106 | -57.2342 | -57.1106 | -0.13275 | -0.013733 | -0.16022 | 1.5427 | -0.13733 | -0.091553 | -0.004578 | 0.041198 | -0.041199 | -0.073242 | -0.054932 | -0.027466 | -0.027466 | -0.15106 | 0.013733 | -0.10986 | 1.6754 | 122.3785 | 0.013733 | 122.3923 | 122.525 | 122.374 | 122.3923 | 122.3328 | -122.5388 | -122.4472 | 122.2458 | 122.3511 | 46.0693 | 57.0099
1060.4062 | 122.612 | -56.9183 | 65.387 | -0.0051118 | -0.02377 | -0.02176 | 0.066507 | -0.031298 | -0.046749 | -0.042742 | -0.0021057 | -0.021817 | 0.053423 | 0.045194 | -0.21808 | -0.012574 | -0.022612 | -11.0596 | 65.3732 | -57.0786 | 65.3687 | -55.2567 | -56.955 | -56.9916 | -0.018311 | 65.2771 | -56.987 | 65.5014 | -56.8497 | -56.9595 | -56.8451 | -0.16022 | -0.013733 | -0.018311 | 1.6617 | -0.073242 | -0.036621 | 0.086975 | 0.1236 | -0.068665 | -0.10986 | 0.11444 | 0.068665 | 0.073242 | -0.041199 | 0.14191 | 0.027466 | 1.8219 | 122.4472 | 0.13733 | 122.4884 | 122.4518 | 122.2641 | 122.2916 | 122.1954 | -122.4655 | -122.374 | 122.287 | 122.4197 | 45.8588 | 56.9
1062.125 | 122.493 | -56.8497 | 65.5518 | 0.0025177 | -0.024838 | -0.024537 | 0.065866 | -0.029375 | -0.048672 | -0.03911 | 0.00094606 | -0.020749 | 0.055345 | 0.038145 | -0.21872 | -0.015992 | -0.025176 | -11.5082 | 65.5426 | -56.9824 | 65.3641 | -55.2109 | -56.9138 | -56.9687 | -0.07782 | 65.506 | -56.8863 | 65.4968 | -56.8588 | -56.9504 | -56.868 | -0.13275 | -0.009155 | -0.18768 | 1.6388 | -0.11902 | -0.064087 | 0.013733 | 0.068665 | -0.036622 | -0.045777 | -0.054932 | -0.009156 | -0.018311 | -0.10071 | 0.018311 | -0.064086 | 1.7715 | 122.3465 | 0.027466 | 122.3831 | 122.525 | 122.3923 | 122.3923 | 122.3557 | -122.5342 | -122.4381 | 122.2137 | 122.3465 | 45.3415 | 56.7719
1063.9219 | 122.6074 | -56.781 | 65.5655 | -0.0051118 | -0.027401 | -0.023041 | 0.062448 | -0.036852 | -0.046749 | -0.037615 | -0.0021057 | -0.020963 | 0.055773 | 0.047544 | -0.21958 | -0.014924 | -0.02368 | -11.6272 | 65.5289 | -56.9275 | 65.5426 | -54.9957 | -56.7261 | -56.7947 | 0.032043 | 65.4922 | -56.813 | 65.6433 | -56.6711 | -56.7764 | -56.6849 | -0.14648 | -0.036621 | -0.022888 | 1.7853 | -0.013733 | 0.054932 | 0.13275 | 0.20142 | -0.032043 | -0.073242 | 0.07782 | 0.10986 | 0.096131 | 0.004578 | 0.12817 | 0.036621 | 1.9318 | 122.4701 | 0.14191 | 122.4564 | 122.4564 | 122.3053 | 122.3099 | 122.2733 | -122.493 | -122.3785 | 122.3236 | 122.4243 | 45.1538 | 56.813
1065.7188 | 122.5708 | -56.7169 | 65.6021 | -0.012741 | -0.025265 | -0.024109 | 0.06373 | -0.029802 | -0.050595 | -0.040392 | 0.00094606 | -0.02139 | 0.055773 | 0.046903 | -0.21552 | -0.017914 | -0.024321 | -11.9888 | 65.6021 | -56.9046 | 65.538 | -54.9911 | -56.749 | -56.7947 | -0.091553 | 65.538 | -56.7444 | 65.6616 | -56.6895 | -56.7581 | -56.6666 | -0.18768 | 0 | -0.064087 | 1.7258 | -0.07782 | -0.032043 | 0.10986 | 0.15564 | -0.027466 | -0.064087 | 0.059509 | 0.027466 | 0.050354 | -0.041199 | 0.07782 | -0.013733 | 1.9135 | 122.4426 | 0.054932 | 122.406 | 122.5067 | 122.2824 | 122.319 | 122.2549 | -122.5067 | -122.3465 | 122.2549 | 122.3785 | 44.7281 | 56.6254
1067.5 | 122.5342 | -56.575 | 65.8081 | 0.0025177 | -0.023983 | -0.023469 | 0.06608 | -0.030443 | -0.047604 | -0.042742 | -0.0021057 | -0.018613 | 0.057482 | 0.051389 | -0.2183 | -0.014283 | -0.017699 | -11.9431 | 65.8447 | -56.7215 | 65.6662 | -54.8401 | -56.662 | -56.7078 | -0.11444 | 65.7349 | -56.6162 | 65.8127 | -56.5659 | -56.6574 | -56.5384 | -0.14648 | 0.036622 | -0.14191 | 1.7349 | -0.13275 | -0.086975 | 0.013733 | 0.05951 | -0.041199 | -0.073242 | 0.004578 | 0.009155 | 0.036621 | -0.082398 | 0.07782 | -0.041199 | 1.8814 | 122.3877 | 0.050354 | 122.4289 | 122.5662 | 122.3511 | 122.4197 | 122.3099 | -122.5296 | -122.4243 | 122.2412 | 122.3877 | 44.632 | 56.4606
1069.2031 | 122.5891 | -56.5613 | 65.7852 | -0.012741 | -0.026547 | -0.023682 | 0.064371 | -0.03258 | -0.047177 | -0.040819 | -0.0021057 | -0.02139 | 0.055132 | 0.04498 | -0.21573 | -0.017914 | -0.021544 | -12.2269 | 65.7806 | -56.6895 | 65.6891 | -54.7485 | -56.5887 | -56.6483 | -0.09613 | 65.7074 | -56.6025 | 65.831 | -56.5155 | -56.5887 | -56.5063 | -0.12817 | -0.004577 | -0.09613 | 1.8127 | -0.086975 | -0.027466 | 0.041199 | 0.10071 | -0.041199 | -0.07782 | 0.045777 | 0.045776 | 0.054931 | -0.027466 | 0.09613 | 0.013733 | 1.9409 | 122.3785 | 0.086975 | 122.4335 | 122.4701 | 122.3099 | 122.3419 | 122.2687 | -122.4747 | -122.3877 | 122.2504 | 122.3923 | 44.3344 | 56.4651
1070.9844 | 122.6166 | -56.337 | 65.9546 | -0.012741 | -0.021847 | -0.021332 | 0.065012 | -0.034716 | -0.046749 | -0.038683 | -0.0021057 | -0.020108 | 0.05385 | 0.048612 | -0.21958 | -0.015778 | -0.023253 | -11.8835 | 65.9592 | -56.4606 | 65.9637 | -54.4281 | -56.3324 | -56.3965 | 0.004578 | 65.8997 | -56.4011 | 66.0919 | -56.2683 | -56.369 | -56.2775 | -0.1236 | 0.004577 | 0.009155 | 1.9089 | -0.059509 | 0.004578 | 0.064087 | 0.12817 | -0.064087 | -0.054932 | 0.13733 | 0.068664 | 0.059509 | -0.032044 | 0.1236 | 0.032043 | 2.0325 | 122.4243 | 0.13275 | 122.493 | 122.4197 | 122.3007 | 122.2961 | 122.2366 | -122.4152 | -122.3557 | 122.3007 | 122.4289 | 44.4534 | 56.3416
1072.7812 | 122.4884 | -56.2729 | 66.1011 | -0.0051118 | -0.026974 | -0.020905 | 0.066294 | -0.033434 | -0.048672 | -0.038256 | -0.0051575 | -0.019254 | 0.056627 | 0.040708 | -0.21744 | -0.017273 | -0.022612 | -11.8561 | 66.0919 | -56.4194 | 65.9775 | -54.3549 | -56.2729 | -56.3553 | -0.068665 | 66.0507 | -56.3324 | 66.0873 | -56.2683 | -56.3828 | -56.2866 | -0.14648 | -0.009155 | -0.1236 | 1.918 | -0.082398 | 0 | 0.064087 | 0.14648 | -0.059509 | -0.050354 | -0.013733 | 0.004577 | -0.013733 | -0.10986 | 0.045776 | -0.050354 | 2.0645 | 122.3969 | 0.064086 | 122.4197 | 122.5113 | 122.3831 | 122.3648 | 122.3236 | -122.5204 | -122.4335 | 122.2504 | 122.3602 | 44.4168 | 56.2042
1074.5469 | 122.493 | -56.131 | 66.2521 | 0.0025177 | -0.024838 | -0.022187 | 0.067789 | -0.03322 | -0.049099 | -0.040178 | 0.00094606 | -0.018827 | 0.057054 | 0.051176 | -0.21872 | -0.015992 | -0.026885 | -11.7828 | 66.2292 | -56.2775 | 66.1285 | -54.1718 | -56.163 | -56.2408 | -0.054932 | 66.188 | -56.163 | 66.2155 | -56.163 | -56.2546 | -56.1447 | -0.14648 | -0.022888 | -0.1236 | 1.9592 | -0.10986 | -0.032044 | 0.036621 | 0.11444 | -0.032044 | -0.064087 | -0.036621 | -0.032044 | -0.013733 | -0.1236 | 0.018311 | -0.091553 | 2.1057 | 122.406 | 0 | 122.3785 | 122.5067 | 122.3511 | 122.3602 | 122.319 | -122.5296 | -122.4152 | 122.2595 | 122.3465 | 44.3481 | 56.076
1076.3281 | 122.5937 | -56.0028 | 66.3025 | 0.0025177 | -0.024624 | -0.022614 | 0.064585 | -0.032793 | -0.046963 | -0.037828 | 0.00094606 | -0.018399 | 0.055132 | 0.048398 | -0.21659 | -0.015137 | -0.02368 | -11.8332 | 66.3895 | -56.1539 | 66.2384 | -54.0298 | -56.044 | -56.1035 | -0.082397 | 66.2888 | -56.0532 | 66.4261 | -55.9525 | -56.0669 | -55.9296 | -0.15106 | 0.086975 | -0.064087 | 1.973 | -0.10071 | -0.041198 | 0.050354 | 0.10986 | -0.050354 | -0.013733 | 0.1236 | 0.050354 | 0.073243 | -0.064087 | 0.1236 | -0.013733 | 2.124 | 122.3923 | 0.10071 | 122.4792 | 122.5433 | 122.3419 | 122.3923 | 122.2916 | -122.4564 | -122.3557 | 122.2412 | 122.4289 | 44.1696 | 55.9204
1078.1406 | 122.5662 | -55.9479 | 66.3712 | -0.012741 | -0.023129 | -0.021973 | 0.065866 | -0.028734 | -0.046963 | -0.040178 | -0.0021057 | -0.021604 | 0.053636 | 0.049039 | -0.21744 | -0.018769 | -0.023039 | -11.9614 | 66.394 | -56.0669 | 66.3208 | -53.8879 | -55.9296 | -55.9891 | -0.091553 | 66.3208 | -56.0028 | 66.4352 | -55.9204 | -55.9982 | -55.8975 | -0.11902 | 0.022888 | -0.050354 | 2.0599 | -0.041199 | 0.018311 | 0.07782 | 0.13733 | -0.054932 | -0.050354 | 0.064087 | 0.027466 | 0.050354 | -0.050354 | 0.10529 | 0.004578 | 2.179 | 122.3877 | 0.082398 | 122.4381 | 122.4609 | 122.3236 | 122.3419 | 122.2687 | -122.4381 | -122.374 | 122.2687 | 122.3831 | 43.9865 | 55.8563
1079.8594 | 122.5021 | -55.6732 | 66.7053 | 0.0025177 | -0.024197 | -0.021332 | 0.068216 | -0.032152 | -0.04739 | -0.041246 | 0.00094606 | -0.017331 | 0.055345 | 0.044767 | -0.21915 | -0.015565 | -0.024321 | -11.1649 | 66.7328 | -55.8289 | 66.6 | -53.5812 | -55.6641 | -55.7556 | -0.050354 | 66.6687 | -55.7053 | 66.7007 | -55.6732 | -55.7922 | -55.6732 | -0.15564 | 0.027466 | -0.10528 | 2.092 | -0.082397 | 0.009156 | 0.073242 | 0.16479 | -0.032043 | -0.036621 | -0.004577 | 0 | 0 | -0.11902 | 0.032043 | -0.086975 | 2.2476 | 122.4289 | 0.032043 | 122.406 | 122.5616 | 122.374 | 122.406 | 122.3419 | -122.5342 | -122.4106 | 122.2733 | 122.374 | 44.5084 | 55.6229
1081.6406 | 122.612 | -55.5588 | 66.7419 | -0.0051118 | -0.027188 | -0.024537 | 0.065653 | -0.032793 | -0.049099 | -0.040819 | -0.0082091 | -0.022031 | 0.060259 | 0.047758 | -0.21723 | -0.016846 | -0.022826 | -11.1649 | 66.7694 | -55.7098 | 66.7969 | -53.3249 | -55.4489 | -55.545 | 0.022888 | 66.7053 | -55.6183 | 66.8793 | -55.4352 | -55.5267 | -55.4672 | -0.15106 | 0.027466 | 0.054932 | 2.2339 | 0.013733 | 0.10986 | 0.1648 | 0.26093 | -0.059509 | -0.036621 | 0.13733 | 0.1236 | 0.091553 | 0.032044 | 0.15106 | 0.091553 | 2.3849 | 122.5067 | 0.1831 | 122.4976 | 122.4792 | 122.3236 | 122.3282 | 122.2641 | -122.4518 | -122.3602 | 122.3557 | 122.438 | 44.3939 | 55.5817
1083.4375 | 122.5159 | -55.3757 | 67.0074 | 0.010147 | -0.026547 | -0.021973 | 0.062448 | -0.030871 | -0.048886 | -0.038683 | 0.00094606 | -0.023099 | 0.055986 | 0.04968 | -0.21659 | -0.017701 | -0.026244 | -11.055 | 66.9754 | -55.5222 | 66.9205 | -53.1281 | -55.275 | -55.3711 | -0.036621 | 66.9479 | -55.4031 | 67.0029 | -55.3299 | -55.4306 | -55.3574 | -0.14649 | -0.032043 | -0.086975 | 2.2476 | 0.004577 | 0.10071 | 0.15106 | 0.24719 | -0.027466 | -0.059509 | -0.004577 | 0.045776 | 0.01831 | -0.054932 | 0.045776 | -0.027466 | 2.3941 | 122.4426 | 0.073242 | 122.406 | 122.4976 | 122.3511 | 122.3511 | 122.3236 | -122.5296 | -122.4106 | 122.2961 | 122.3785 | 44.3207 | 55.3391
1085.1562 | 122.58 | -55.3207 | 66.9983 | -0.0051118 | -0.023556 | -0.023255 | 0.064157 | -0.030016 | -0.048031 | -0.039324 | -0.0021057 | -0.020536 | 0.056414 | 0.050748 | -0.21637 | -0.016846 | -0.025389 | -11.3846 | 66.9983 | -55.4535 | 66.9388 | -53.0594 | -55.2658 | -55.3436 | -0.07782 | 66.9479 | -55.3665 | 67.0715 | -55.2979 | -55.3848 | -55.2887 | -0.13275 | 0 | -0.059509 | 2.2614 | -0.022888 | 0.054932 | 0.10986 | 0.18768 | -0.045776 | -0.050354 | 0.073242 | 0.022888 | 0.032044 | -0.064087 | 0.07782 | -0.018311 | 2.3941 | 122.3923 | 0.068664 | 122.438 | 122.4518 | 122.3145 | 122.319 | 122.2687 | -122.4518 | -122.3648 | 122.2595 | 122.3923 | 43.9362 | 55.2429
1086.9375 | 122.4701 | -55.1605 | 67.2318 | -0.0051118 | -0.022488 | -0.020905 | 0.067789 | -0.028521 | -0.048245 | -0.036547 | 0.00094606 | -0.018827 | 0.055345 | 0.051603 | -0.21808 | -0.015351 | -0.021971 | -11.1145 | 67.2272 | -55.307 | 67.0807 | -52.9724 | -55.1697 | -55.2658 | -0.13275 | 67.1677 | -55.22 | 67.1814 | -55.2155 | -55.3207 | -55.1834 | -0.14648 | -0.004577 | -0.15106 | 2.1881 | -0.10529 | -0.009156 | 0.041199 | 0.13733 | -0.05951 | -0.064086 | -0.050354 | -0.054932 | -0.022889 | -0.16022 | 0.036621 | -0.10071 | 2.3346 | 122.3877 | 0.004578 | 122.4014 | 122.5342 | 122.3877 | 122.3877 | 122.3282 | -122.5388 | -122.4518 | 122.2412 | 122.3419 | 44.046 | 55.0278
1088.7344 | 122.58 | -55.1239 | 67.1997 | 0.0025177 | -0.02377 | -0.020905 | 0.065012 | -0.03258 | -0.048245 | -0.039324 | 0.00094606 | -0.021817 | 0.054277 | 0.047758 | -0.21616 | -0.015992 | -0.025176 | -11.4853 | 67.2043 | -55.2338 | 67.1951 | -52.7664 | -55.014 | -55.0873 | -0.018311 | 67.1356 | -55.1514 | 67.305 | -55.0598 | -55.1697 | -55.0598 | -0.10986 | 0.004578 | -0.004578 | 2.3575 | 0.036621 | 0.10986 | 0.14648 | 0.21973 | -0.027466 | -0.064087 | 0.10529 | 0.064087 | 0.064087 | -0.045777 | 0.091553 | -0.018311 | 2.4673 | 122.4289 | 0.091553 | 122.4564 | 122.4381 | 122.287 | 122.3282 | 122.2595 | -122.4335 | -122.3511 | 122.319 | 122.4289 | 43.6386 | 55.1056
1090.5312 | 122.4884 | -55.1697 | 67.2409 | 0.0025177 | -0.025051 | -0.024537 | 0.066294 | -0.033648 | -0.049954 | -0.040605 | 0.00094606 | -0.018186 | 0.057268 | 0.040922 | -0.21702 | -0.017701 | -0.020476 | -11.9247 | 67.2363 | -55.2979 | 67.0807 | -52.8671 | -55.0873 | -55.1926 | -0.09613 | 67.218 | -55.1743 | 67.1997 | -55.1514 | -55.2521 | -55.1605 | -0.12817 | -0.004578 | -0.16022 | 2.3026 | -0.022888 | 0.082398 | 0.10529 | 0.21057 | -0.004577 | -0.022888 | -0.041199 | 0.018311 | 0.009156 | -0.082397 | 0.013733 | -0.07782 | 2.4307 | 122.3785 | 0.022888 | 122.374 | 122.5342 | 122.3923 | 122.406 | 122.3877 | -122.5388 | -122.4152 | 122.2504 | 122.3694 | 43.2449 | 55.0735
1092.2344 | 122.5342 | -55.014 | 67.3874 | -0.0051118 | -0.025479 | -0.0224 | 0.066507 | -0.033434 | -0.048031 | -0.042101 | 0.00094606 | -0.01904 | 0.057909 | 0.048398 | -0.2183 | -0.017273 | -0.018126 | -11.8561 | 67.3782 | -55.1468 | 67.2409 | -52.6794 | -54.9271 | -55.0461 | -0.009155 | 67.3141 | -55.0644 | 67.3874 | -55.0003 | -55.101 | -54.9957 | -0.13275 | -0.009155 | -0.14648 | 2.3346 | -0.032044 | 0.086975 | 0.10071 | 0.21973 | -0.050354 | -0.073242 | 0 | 0.013733 | 0.01831 | -0.086975 | 0.068664 | -0.036621 | 2.4673 | 122.3877 | 0.064087 | 122.4518 | 122.525 | 122.3785 | 122.3923 | 122.3282 | -122.5342 | -122.4518 | 122.2549 | 122.4014 | 43.158 | 55.0049
1094.0156 | 122.6028 | -54.9637 | 67.3279 | 0.0025177 | -0.023129 | -0.020264 | 0.065225 | -0.030016 | -0.046963 | -0.037615 | -0.0021057 | -0.019254 | 0.055559 | 0.043699 | -0.21766 | -0.01706 | -0.024107 | -12.0438 | 67.3599 | -55.1102 | 67.3233 | -52.5421 | -54.8447 | -54.9591 | -0.032043 | 67.2775 | -55.0186 | 67.4744 | -54.895 | -54.9957 | -54.8904 | -0.14648 | 0.032043 | -0.004578 | 2.4216 | 0.004578 | 0.11902 | 0.15106 | 0.2655 | -0.054932 | -0.050354 | 0.14648 | 0.068664 | 0.073242 | -0.032044 | 0.12817 | 0.022888 | 2.5681 | 122.4335 | 0.1236 | 122.493 | 122.4701 | 122.2961 | 122.3236 | 122.2412 | -122.438 | -122.3465 | 122.287 | 122.438 | 42.9199 | 54.9316
1095.8125 | 122.5159 | -54.7485 | 67.6117 | 0.0025177 | -0.021206 | -0.0224 | 0.068216 | -0.025957 | -0.047604 | -0.039537 | 0.00094606 | -0.017331 | 0.057054 | 0.048185 | -0.21723 | -0.014283 | -0.024321 | -11.6409 | 67.63 | -54.8767 | 67.5201 | -52.3178 | -54.6478 | -54.7714 | -0.018311 | 67.5522 | -54.8035 | 67.63 | -54.7394 | -54.8538 | -54.744 | -0.12817 | 0.018311 | -0.091552 | 2.4307 | -0.022888 | 0.10071 | 0.10529 | 0.22888 | -0.054932 | -0.059509 | 0.018311 | 0.009155 | 0.004577 | -0.10529 | 0.059509 | -0.050354 | 2.5589 | 122.3969 | 0.064087 | 122.4335 | 122.5067 | 122.3557 | 122.3785 | 122.3007 | -122.4884 | -122.4152 | 122.2687 | 122.3785 | 43.1076 | 54.7302
1097.6094 | 122.612 | -54.4739 | 67.8497 | 0.0025177 | -0.025479 | -0.021973 | 0.063516 | -0.030871 | -0.045681 | -0.042101 | -0.0082091 | -0.021604 | 0.057054 | 0.050962 | -0.21659 | -0.015778 | -0.022185 | -11.2106 | 67.836 | -54.6249 | 67.8635 | -51.8646 | -54.2725 | -54.3823 | 0.027466 | 67.7902 | -54.5197 | 67.9642 | -54.3549 | -54.4464 | -54.3869 | -0.15106 | -0.013732 | 0.013733 | 2.6093 | 0.091553 | 0.20142 | 0.24262 | 0.35248 | -0.045776 | -0.059509 | 0.11444 | 0.11902 | 0.086975 | 0.027466 | 0.13275 | 0.073242 | 2.7603 | 122.4884 | 0.16479 | 122.4838 | 122.4609 | 122.3099 | 122.3099 | 122.2641 | -122.4747 | -122.3694 | 122.3373 | 122.438 | 43.2632 | 54.5013
1099.3281 | 122.4564 | -54.4281 | 67.9413 | 0.0025177 | -0.020993 | -0.020905 | 0.069498 | -0.025957 | -0.045895 | -0.038683 | -0.0021057 | -0.020536 | 0.057482 | 0.044553 | -0.21851 | -0.013428 | -0.02133 | -11.4853 | 68.0099 | -54.5746 | 67.7673 | -52.0203 | -54.3732 | -54.5105 | -0.1831 | 67.9047 | -54.5151 | 67.9092 | -54.5059 | -54.5883 | -54.4647 | -0.14648 | 0.068665 | -0.17395 | 2.4078 | -0.082397 | 0.054932 | 0.064087 | 0.20142 | -0.086975 | -0.036621 | -0.032043 | -0.077819 | -0.036621 | -0.16022 | 0.050354 | -0.073242 | 2.5543 | 122.3419 | 0.009156 | 122.4243 | 122.5845 | 122.4197 | 122.4381 | 122.3328 | -122.5159 | -122.4564 | 122.1954 | 122.3373 | 42.9428 | 54.245
1101.125 | 122.4701 | -54.6433 | 67.7628 | -0.0051118 | -0.025479 | -0.023682 | 0.063944 | -0.03258 | -0.046963 | -0.038256 | -0.0021057 | -0.01904 | 0.057054 | 0.040922 | -0.2168 | -0.013856 | -0.026457 | -11.3297 | 67.7948 | -54.7714 | 67.5842 | -52.2171 | -54.5013 | -54.6524 | -0.10529 | 67.7261 | -54.689 | 67.7078 | -54.6249 | -54.7394 | -54.6478 | -0.12817 | 0.032044 | -0.17853 | 2.4261 | -0.009155 | 0.14191 | 0.11902 | 0.27008 | -0.045776 | -0.036621 | -0.054931 | 0.018311 | -0.004577 | -0.09613 | 0.041199 | -0.050354 | 2.5543 | 122.3557 | 0.064087 | 122.3969 | 122.5662 | 122.4152 | 122.4381 | 122.3694 | -122.5342 | -122.4518 | 122.2275 | 122.3511 | 43.3136 | 54.538
1102.9219 | 122.4655 | -54.3961 | 68.0099 | 0.0025177 | -0.025265 | -0.02176 | 0.06608 | -0.032152 | -0.046108 | -0.040178 | -0.0051575 | -0.019467 | 0.056627 | 0.048398 | -0.21616 | -0.014924 | -0.02133 | -11.1008 | 68.0008 | -54.5288 | 67.8406 | -51.9699 | -54.2862 | -54.4373 | -0.11902 | 67.9184 | -54.4373 | 67.955 | -54.4281 | -54.5425 | -54.4281 | -0.13275 | -0.009156 | -0.16937 | 2.4261 | -0.041199 | 0.10986 | 0.091553 | 0.24262 | -0.041199 | -0.091553 | -0.054932 | -0.032044 | -0.032044 | -0.14648 | 0.009155 | -0.10529 | 2.5589 | 122.3694 | 0.009155 | 122.3923 | 122.5296 | 122.3557 | 122.3969 | 122.3145 | -122.5388 | -122.4472 | 122.2366 | 122.3511 | 43.2953 | 54.277
1104.7188 | 122.5937 | -54.2679 | 68.042 | -0.012741 | -0.023983 | -0.018982 | 0.064371 | -0.026812 | -0.046322 | -0.03911 | -0.0051575 | -0.021817 | 0.056841 | 0.044126 | -0.21808 | -0.015778 | -0.021758 | -10.9222 | 68.0603 | -54.4052 | 68.0557 | -51.7273 | -54.0527 | -54.2175 | -0.027466 | 68.0054 | -54.3137 | 68.161 | -54.2084 | -54.3091 | -54.2038 | -0.13733 | 0.018311 | 0.013733 | 2.5406 | 0.050354 | 0.21515 | 0.18768 | 0.35248 | -0.045777 | -0.036621 | 0.11902 | 0.059509 | 0.064087 | -0.041199 | 0.10986 | 0.004578 | 2.6779 | 122.4609 | 0.10529 | 122.4747 | 122.4655 | 122.319 | 122.3282 | 122.2733 | -122.4472 | -122.3557 | 122.3236 | 122.4289 | 43.3456 | 54.2404
1106.5 | 122.5754 | -53.6682 | 68.6691 | -0.0051118 | -0.022915 | -0.021546 | 0.069071 | -0.032793 | -0.046536 | -0.038042 | -0.0021057 | -0.020108 | 0.058336 | 0.042417 | -0.21702 | -0.015565 | -0.024535 | -10.8444 | 68.7241 | -53.8239 | 68.5501 | -51.178 | -53.5263 | -53.7003 | -0.10071 | 68.6234 | -53.7048 | 68.7515 | -53.6407 | -53.7552 | -53.6316 | -0.15564 | 0.054932 | -0.11902 | 2.4902 | -0.032043 | 0.14191 | 0.1236 | 0.29755 | -0.036621 | -0.045776 | 0.082398 | 0.027466 | 0.036621 | -0.086975 | 0.073242 | -0.050354 | 2.6459 | 122.374 | 0.064087 | 122.4564 | 122.5479 | 122.3282 | 122.3923 | 122.2916 | -122.493 | -122.374 | 122.2183 | 122.4197 | 42.8238 | 53.5675
1108.2188 | 122.5296 | -53.4531 | 68.9438 | -0.012741 | -0.02377 | -0.023041 | 0.068216 | -0.030871 | -0.046322 | -0.039751 | -0.0051575 | -0.018827 | 0.056841 | 0.044553 | -0.2168 | -0.014496 | -0.022612 | -10.7346 | 68.9529 | -53.5767 | 68.7744 | -50.9216 | -53.2928 | -53.4851 | -0.14191 | 68.8751 | -53.4851 | 68.9301 | -53.4714 | -53.5675 | -53.4485 | -0.1236 | 0.009155 | -0.16937 | 2.5314 | -0.032043 | 0.16022 | 0.091553 | 0.28381 | -0.032043 | -0.068665 | -0.013733 | -0.018311 | 0.004578 | -0.11444 | 0.036621 | -0.082398 | 2.655 | 122.3511 | 0.013732 | 122.4152 | 122.5296 | 122.3602 | 122.406 | 122.3282 | -122.5204 | -122.4289 | 122.2275 | 122.3831 | 42.7185 | 53.3112
1110 | 122.4792 | -53.7735 | 68.6325 | 0.010147 | -0.026333 | -0.023255 | 0.066294 | -0.030657 | -0.046749 | -0.038256 | 0.00094606 | -0.021176 | 0.058336 | 0.045194 | -0.21808 | -0.016846 | -0.021117 | -10.6842 | 68.6462 | -53.9246 | 68.4311 | -51.1459 | -53.595 | -53.7918 | -0.10529 | 68.5684 | -53.8055 | 68.5684 | -53.8055 | -53.9062 | -53.7918 | -0.15106 | 0.013733 | -0.20142 | 2.6276 | -0.01831 | 0.17853 | 0.13275 | 0.32959 | -0.032043 | -0.064087 | -0.064087 | -0.032043 | -0.01831 | -0.13275 | 0.013733 | -0.10071 | 2.7786 | 122.3557 | 0 | 122.374 | 122.5708 | 122.374 | 122.4197 | 122.3419 | -122.5571 | -122.438 | 122.2046 | 122.3419 | 43.0893 | 53.6682
1111.7656 | 122.4792 | -53.5675 | 68.8339 | -0.0051118 | -0.022915 | -0.020905 | 0.06843 | -0.029162 | -0.046108 | -0.037401 | -0.0051575 | -0.018613 | 0.055773 | 0.049467 | -0.21723 | -0.015778 | -0.02368 | -10.4599 | 68.8385 | -53.7048 | 68.6371 | -50.9216 | -53.4119 | -53.6041 | -0.16022 | 68.7378 | -53.6362 | 68.7607 | -53.6316 | -53.7231 | -53.595 | -0.13733 | 0.004578 | -0.19684 | 2.6459 | -0.036621 | 0.15564 | 0.10071 | 0.29297 | -0.068664 | -0.09613 | -0.073242 | -0.064087 | -0.027466 | -0.15564 | 0.041198 | -0.086976 | 2.7832 | 122.3419 | 0.004577 | 122.3969 | 122.5433 | 122.374 | 122.406 | 122.3053 | -122.5388 | -122.4701 | 122.2046 | 122.3282 | 43.1076 | 53.4073
1113.5625 | 122.6028 | -53.1967 | 69.104 | 0.0025177 | -0.02377 | -0.023682 | 0.067789 | -0.034502 | -0.04504 | -0.03911 | -0.0021057 | -0.021817 | 0.057054 | 0.047758 | -0.21808 | -0.015351 | -0.019194 | -10.4416 | 69.1177 | -53.3615 | 69.072 | -50.3998 | -52.9678 | -53.1601 | -0.027466 | 69.0216 | -53.2562 | 69.2047 | -53.1418 | -53.2471 | -53.1326 | -0.16479 | 0.013733 | -0.032044 | 2.7969 | 0.036621 | 0.22888 | 0.20142 | 0.39368 | -0.05951 | -0.082398 | 0.10071 | 0.054931 | 0.064087 | -0.050354 | 0.1236 | 0.009156 | 2.9617 | 122.4335 | 0.11444 | 122.4609 | 122.4792 | 122.2778 | 122.3145 | 122.2183 | -122.4655 | -122.3602 | 122.2687 | 122.4014 | 42.7551 | 53.1693
1115.3438 | 122.6303 | -53.0182 | 69.2825 | 0.0025177 | -0.027615 | -0.020905 | 0.063089 | -0.031084 | -0.046322 | -0.037187 | -0.0021057 | -0.021817 | 0.054705 | 0.042631 | -0.21872 | -0.015992 | -0.024107 | -10.405 | 69.3054 | -53.1876 | 69.2825 | -50.148 | -52.7206 | -52.8992 | 0.022888 | 69.2276 | -53.0548 | 69.4382 | -52.9083 | -52.9861 | -52.9449 | -0.16937 | 0.022888 | 0 | 2.8702 | 0.11902 | 0.29755 | 0.28839 | 0.46692 | -0.036622 | -0.054932 | 0.15564 | 0.10986 | 0.073242 | 0.032043 | 0.10986 | 0.068665 | 3.0396 | 122.4701 | 0.14649 | 122.493 | 122.493 | 122.2824 | 122.3236 | 122.2458 | -122.4701 | -122.3373 | 122.3007 | 122.4564 | 42.6132 | 53.0411
1117.0469 | 122.5296 | -52.7115 | 69.6762 | -0.0051118 | -0.024624 | -0.022828 | 0.064798 | -0.033648 | -0.047817 | -0.037187 | 0.00094606 | -0.020749 | 0.054705 | 0.047117 | -0.21766 | -0.016205 | -0.02368 | -10.7986 | 69.635 | -52.8397 | 69.5892 | -49.8459 | -52.3865 | -52.6199 | -0.018311 | 69.5847 | -52.7344 | 69.6579 | -52.6794 | -52.7664 | -52.7023 | -0.12817 | -0.041198 | -0.086975 | 2.8656 | 0.091553 | 0.32501 | 0.21973 | 0.45319 | -0.022888 | -0.091552 | -0.01831 | 0.032044 | 0.009155 | -0.054931 | 0.032043 | -0.032043 | 2.9938 | 122.4289 | 0.054932 | 122.3923 | 122.4747 | 122.319 | 122.3465 | 122.2961 | -122.5159 | -122.4106 | 122.3007 | 122.3694 | 41.9128 | 52.6932
1118.8281 | 122.5021 | -52.4414 | 69.9738 | 0.0025177 | -0.024411 | -0.021546 | 0.069071 | -0.027666 | -0.048886 | -0.037187 | -0.0021057 | -0.018186 | 0.054064 | 0.04498 | -0.2183 | -0.016846 | -0.025816 | -10.6705 | 69.9692 | -52.5696 | 69.8364 | -49.53 | -52.1484 | -52.3865 | -0.036621 | 69.8914 | -52.4643 | 69.9326 | -52.4368 | -52.5558 | -52.4368 | -0.12817 | -0.004578 | -0.13733 | 2.9114 | 0.054931 | 0.29297 | 0.18311 | 0.42114 | -0.022888 | -0.082398 | -0.041199 | 0.004577 | 0.004577 | -0.11444 | 0.027465 | -0.091553 | 3.0396 | 122.406 | 0.027465 | 122.3969 | 122.5388 | 122.3557 | 122.4106 | 122.3328 | -122.5433 | -122.438 | 122.2778 | 122.374 | 41.7709 | 52.4048
1120.625 | 122.4701 | -52.6245 | 69.7906 | -0.0051118 | -0.022274 | -0.021119 | 0.069712 | -0.031511 | -0.045254 | -0.037828 | 0.00094606 | -0.018613 | 0.057909 | 0.047971 | -0.21766 | -0.015137 | -0.017912 | -10.1257 | 69.7998 | -52.771 | 69.5526 | -49.7269 | -52.446 | -52.652 | -0.15564 | 69.7266 | -52.6794 | 69.722 | -52.7023 | -52.7847 | -52.6566 | -0.14648 | 0.009156 | -0.23804 | 2.8976 | -0.027466 | 0.17853 | 0.11902 | 0.32501 | -0.054931 | -0.064087 | -0.068664 | -0.07782 | -0.032043 | -0.16022 | 0.022888 | -0.10529 | 3.0441 | 122.3236 | -0.022889 | 122.4014 | 122.5708 | 122.406 | 122.4243 | 122.3511 | -122.5616 | -122.4701 | 122.1771 | 122.3465 | 42.4988 | 52.4689
1122.4062 | 122.6212 | -52.2858 | 70.0607 | -0.0051118 | -0.026974 | -0.0224 | 0.065653 | -0.031084 | -0.045895 | -0.036974 | -0.0021057 | -0.021176 | 0.055345 | 0.047971 | -0.2183 | -0.01706 | -0.023039 | -9.5032 | 70.0516 | -52.4139 | 69.9829 | -49.1455 | -51.9653 | -52.1713 | -0.045776 | 69.9692 | -52.3361 | 70.1569 | -52.2125 | -52.2903 | -52.2263 | -0.12817 | -0.009155 | -0.07782 | 3.1403 | 0.11444 | 0.32044 | 0.24261 | 0.44861 | -0.050354 | -0.091553 | 0.09613 | 0.073243 | 0.05951 | -0.004577 | 0.10986 | 0.045777 | 3.2684 | 122.3969 | 0.1236 | 122.493 | 122.4655 | 122.3053 | 122.3373 | 122.2549 | -122.4747 | -122.3969 | 122.2687 | 122.4426 | 42.7826 | 52.24
1124.1406 | 122.493 | -51.9836 | 70.4178 | -0.0051118 | -0.026547 | -0.021332 | 0.068857 | -0.034716 | -0.049313 | -0.038256 | -0.0021057 | -0.019895 | 0.059191 | 0.050535 | -0.21958 | -0.013001 | -0.020689 | -9.1049 | 70.4086 | -52.1072 | 70.2393 | -48.8571 | -51.6998 | -51.9333 | -0.10986 | 70.3674 | -52.0248 | 70.3629 | -52.0203 | -52.1072 | -52.0111 | -0.1236 | -0.009156 | -0.17853 | 3.1265 | 0.050354 | 0.28381 | 0.17395 | 0.40741 | -0.041198 | -0.050354 | -0.054932 | -0.036621 | -0.027465 | -0.1236 | 0.013733 | -0.082398 | 3.2501 | 122.3465 | 0.004577 | 122.3877 | 122.5159 | 122.3923 | 122.3923 | 122.3511 | -122.525 | -122.4426 | 122.2229 | 122.3465 | 42.8787 | 51.8738
1125.9375 | 122.5525 | -51.6861 | 70.7062 | -0.0051118 | -0.022061 | -0.020905 | 0.068643 | -0.030657 | -0.044613 | -0.03676 | -0.0021057 | -0.020108 | 0.057695 | 0.048612 | -0.21723 | -0.015778 | -0.023467 | -8.6426 | 70.697 | -51.8234 | 70.5734 | -48.4406 | -51.3702 | -51.6129 | -0.027466 | 70.6558 | -51.7227 | 70.7016 | -51.6632 | -51.7685 | -51.6724 | -0.13733 | -0.009156 | -0.13275 | 3.2455 | 0.073242 | 0.31586 | 0.21057 | 0.45319 | -0.036621 | -0.050354 | -0.004578 | 0.022888 | 0.013733 | -0.082398 | 0.050354 | -0.045777 | 3.3829 | 122.3969 | 0.059509 | 122.4243 | 122.5204 | 122.3785 | 122.3831 | 122.3419 | -122.5296 | -122.4289 | 122.2595 | 122.3877 | 43.0435 | 51.6586
1127.7344 | 122.5662 | -51.3702 | 71.0083 | -0.0051118 | -0.023983 | -0.021119 | 0.065653 | -0.031084 | -0.046322 | -0.03911 | 0.0039979 | -0.020963 | 0.054491 | 0.04199 | -0.21851 | -0.015992 | -0.022826 | -8.3588 | 70.9946 | -51.4984 | 70.8984 | -47.9965 | -50.9995 | -51.2512 | -0.091553 | 70.9076 | -51.4023 | 71.0266 | -51.3336 | -51.4297 | -51.3474 | -0.12817 | -0.013733 | -0.10986 | 3.3737 | 0.11902 | 0.37079 | 0.24719 | 0.49896 | -0.032044 | -0.10071 | 0.01831 | 0.036621 | 0.022888 | -0.05951 | 0.054932 | -0.027466 | 3.5019 | 122.3969 | 0.068665 | 122.4289 | 122.493 | 122.3099 | 122.3648 | 122.2778 | -122.5067 | -122.4106 | 122.2687 | 122.3969 | 43.0115 | 51.2787
1129.5156 | 122.5983 | -50.9628 | 71.3425 | -0.0051118 | -0.024838 | -0.018769 | 0.069071 | -0.028093 | -0.046749 | -0.034838 | -0.0021057 | -0.02139 | 0.057482 | 0.056943 | -0.22022 | -0.016419 | -0.024107 | -7.9285 | 71.3333 | -51.1093 | 71.3104 | -47.525 | -50.6607 | -50.853 | -0.018311 | 71.283 | -51.0315 | 71.4661 | -50.9262 | -51.0406 | -50.9033 | -0.14648 | -0.009155 | -0.032043 | 3.4378 | 0.10986 | 0.30212 | 0.25635 | 0.44861 | -0.068664 | -0.059509 | 0.1236 | 0.036622 | 0.05951 | -0.077819 | 0.12817 | -0.009155 | 3.5843 | 122.4197 | 0.10529 | 122.4976 | 122.4426 | 122.3145 | 122.2961 | 122.2458 | -122.4518 | -122.374 | 122.2733 | 122.4289 | 43.0344 | 50.9445
1131.2969 | 122.5204 | -50.4044 | 71.9513 | -0.0051118 | -0.023129 | -0.020691 | 0.070139 | -0.033434 | -0.046536 | -0.038042 | 0.0039979 | -0.018186 | 0.0562 | 0.045194 | -0.21787 | -0.014924 | -0.023253 | -7.489 | 71.9513 | -50.5508 | 71.8323 | -46.8933 | -50.0519 | -50.3403 | -0.032043 | 71.9147 | -50.4593 | 71.9467 | -50.4181 | -50.528 | -50.4227 | -0.14648 | 0 | -0.11902 | 3.511 | 0.064087 | 0.35248 | 0.21057 | 0.49896 | -0.054932 | -0.036621 | -0.004578 | -0.013733 | -0.01831 | -0.1236 | 0.036622 | -0.068664 | 3.6575 | 122.3831 | 0.041199 | 122.406 | 122.5021 | 122.374 | 122.3557 | 122.319 | -122.5021 | -122.4106 | 122.2366 | 122.3511 | 42.9153 | 50.3723
1133.0938 | 122.5571 | -49.9054 | 72.4319 | 0.0025177 | -0.024411 | -0.019623 | 0.067148 | -0.037706 | -0.043972 | -0.040392 | 0.00094606 | -0.020963 | 0.0562 | 0.045621 | -0.21766 | -0.018555 | -0.021117 | -7.2052 | 72.4457 | -50.0336 | 72.3267 | -46.312 | -49.498 | -49.7955 | -0.10071 | 72.3724 | -49.9695 | 72.464 | -49.9008 | -49.9832 | -49.8917 | -0.12817 | 0.013733 | -0.10529 | 3.5934 | 0.10986 | 0.40741 | 0.23804 | 0.53558 | -0.064086 | -0.059509 | 0.032043 | 0.004578 | 0.013733 | -0.077819 | 0.077819 | -0.013733 | 3.7216 | 122.3602 | 0.068664 | 122.4335 | 122.4792 | 122.3419 | 122.3511 | 122.2778 | -122.4655 | -122.4014 | 122.2321 | 122.3694 | 42.7002 | 49.8047
1134.8125 | 122.5021 | -49.6811 | 72.6974 | 0.0025177 | -0.025479 | -0.020264 | 0.067148 | -0.031939 | -0.046749 | -0.040819 | -0.0021057 | -0.01904 | 0.056841 | 0.045835 | -0.21787 | -0.016846 | -0.022398 | -7.0496 | 72.6608 | -49.7772 | 72.6105 | -45.9915 | -49.1318 | -49.5163 | -0.022888 | 72.6425 | -49.7131 | 72.6974 | -49.6765 | -49.7498 | -49.6857 | -0.096131 | -0.036621 | -0.086975 | 3.6896 | 0.1648 | 0.54932 | 0.26093 | 0.64545 | -0.032044 | -0.054932 | 0 | 0.004577 | -0.004578 | -0.068665 | 0.027466 | -0.036621 | 3.7857 | 122.3877 | 0.036621 | 122.4106 | 122.4381 | 122.3557 | 122.3419 | 122.3236 | -122.4747 | -122.4106 | 122.2916 | 122.3785 | 42.6315 | 49.6582
1136.5938 | 122.5571 | -49.2096 | 73.1461 | -0.0051118 | -0.023129 | -0.021546 | 0.071634 | -0.031511 | -0.043331 | -0.03911 | -0.0021057 | -0.019681 | 0.055773 | 0.043058 | -0.21787 | -0.016205 | -0.026244 | -7.2189 | 73.201 | -49.3378 | 73.0225 | -45.3461 | -48.7427 | -49.1135 | -0.082397 | 73.1049 | -49.2416 | 73.2056 | -49.2004 | -49.2828 | -49.1684 | -0.12817 | 0.054932 | -0.1236 | 3.8635 | 0.096131 | 0.46692 | 0.22431 | 0.59509 | -0.032043 | -0.041199 | 0.059509 | 0.009156 | 0.041199 | -0.073242 | 0.073242 | -0.041199 | 3.9917 | 122.3602 | 0.041199 | 122.4472 | 122.5388 | 122.3465 | 122.4106 | 122.3145 | -122.4838 | -122.3877 | 122.2321 | 122.4152 | 41.9907 | 49.1272
1138.3125 | 122.5708 | -48.8022 | 73.4711 | 0.0025177 | -0.026547 | -0.020478 | 0.068216 | -0.034716 | -0.045895 | -0.039751 | -0.0021057 | -0.021176 | 0.0562 | 0.045194 | -0.21723 | -0.017914 | -0.020476 | -7.2052 | 73.5123 | -48.9395 | 73.494 | -44.5908 | -48.2758 | -48.6282 | 0 | 73.4665 | -48.8434 | 73.6084 | -48.7793 | -48.8754 | -48.761 | -0.13733 | 0.041199 | 0.022889 | 4.2114 | 0.17395 | 0.52643 | 0.31128 | 0.66376 | -0.041199 | -0.004577 | 0.13733 | 0.022888 | 0.041199 | -0.073242 | 0.082398 | -0.032043 | 4.3488 | 122.4335 | 0.064087 | 122.4518 | 122.4518 | 122.3099 | 122.3145 | 122.2687 | -122.4106 | -122.3145 | 122.2961 | 122.4106 | 41.597 | 48.8022
1140.1094 | 122.525 | -48.2071 | 74.1943 | -0.0051118 | -0.025692 | -0.018769 | 0.070993 | -0.029802 | -0.044827 | -0.038256 | 0.00094606 | -0.016904 | 0.057054 | 0.046476 | -0.22022 | -0.016419 | -0.021117 | -6.9168 | 74.2172 | -48.349 | 73.9838 | -43.634 | -47.731 | -48.1064 | -0.091553 | 74.1486 | -48.2803 | 74.1257 | -48.2437 | -48.3398 | -48.2483 | -0.14191 | 0.022888 | -0.21057 | 4.5731 | 0.10071 | 0.47607 | 0.24262 | 0.61798 | -0.073242 | -0.045776 | -0.068665 | -0.036621 | -0.041199 | -0.13275 | 0.032043 | -0.05951 | 4.715 | 122.3328 | 0.036621 | 122.406 | 122.5662 | 122.4289 | 122.4243 | 122.3557 | -122.5433 | -122.4747 | 122.1909 | 122.3328 | 41.2903 | 48.1155
1141.8906 | 122.4518 | -47.7356 | 74.7025 | -0.0051118 | -0.018856 | -0.018128 | 0.071421 | -0.032152 | -0.042904 | -0.037615 | -0.0021057 | -0.01904 | 0.05855 | 0.051816 | -0.2168 | -0.014496 | -0.026885 | -6.2622 | 74.7253 | -47.8363 | 74.4965 | -42.7597 | -47.1542 | -47.6257 | -0.14191 | 74.6887 | -47.7768 | 74.6246 | -47.8088 | -47.8867 | -47.7722 | -0.10071 | 0.022888 | -0.20599 | 4.9759 | 0.10986 | 0.58136 | 0.21057 | 0.68207 | -0.041198 | -0.013733 | -0.07782 | -0.073242 | -0.036621 | -0.15106 | 0.004577 | -0.10986 | 5.0766 | 122.3328 | -0.032044 | 122.4014 | 122.5616 | 122.4655 | 122.4609 | 122.4243 | -122.5388 | -122.4792 | 122.2321 | 122.3602 | 41.4734 | 47.5937
1143.625 | 122.5113 | -47.9645 | 74.4232 | 0.0025177 | -0.025265 | -0.018769 | 0.069284 | -0.033434 | -0.04504 | -0.035265 | 0.00094606 | -0.019467 | 0.056841 | 0.050535 | -0.22001 | -0.016633 | -0.024321 | -6.0974 | 74.4232 | -48.1201 | 74.2401 | -42.6041 | -47.3831 | -47.8363 | -0.064087 | 74.3912 | -48.0011 | 74.3958 | -47.9965 | -48.1064 | -48.0057 | -0.15564 | 0 | -0.18311 | 5.3604 | 0.12817 | 0.58136 | 0.28381 | 0.737 | -0.036621 | -0.032044 | -0.027466 | -0.032043 | -0.041198 | -0.14191 | -0.004577 | -0.10528 | 5.5161 | 122.3602 | 0.004578 | 122.3969 | 122.5433 | 122.3923 | 122.3877 | 122.3557 | -122.5433 | -122.4243 | 122.2046 | 122.3602 | 41.8671 | 47.9004
1145.4219 | 122.525 | -48.3261 | 74.0616 | -0.0051118 | -0.021634 | -0.017914 | 0.071421 | -0.03023 | -0.042904 | -0.037828 | 0.0039979 | -0.020108 | 0.055986 | 0.049894 | -0.21894 | -0.015137 | -0.019408 | -5.9097 | 74.1074 | -48.468 | 73.8556 | -42.6407 | -47.7264 | -48.2162 | -0.12817 | 73.9883 | -48.3765 | 74.0524 | -48.3719 | -48.4772 | -48.3398 | -0.14191 | 0.045777 | -0.20599 | 5.6854 | 0.10986 | 0.59967 | 0.25177 | 0.74158 | -0.050354 | -0.073242 | -0.009155 | -0.045776 | -0.013733 | -0.15106 | 0.036621 | -0.10071 | 5.8273 | 122.3236 | 0.004578 | 122.4289 | 122.5754 | 122.3648 | 122.4335 | 122.3145 | -122.5296 | -122.438 | 122.1817 | 122.3785 | 42.4164 | 48.1979
1147.2031 | 122.5616 | -48.7885 | 73.5535 | -0.0051118 | -0.025479 | -0.021546 | 0.068003 | -0.031725 | -0.04504 | -0.038256 | 0.00094606 | -0.021176 | 0.057909 | 0.04199 | -0.21787 | -0.01706 | -0.016844 | -6.0654 | 73.5306 | -48.9304 | 73.5077 | -42.6361 | -48.0423 | -48.5458 | 0.009155 | 73.4894 | -48.8342 | 73.613 | -48.7427 | -48.8205 | -48.761 | -0.14191 | -0.022888 | -0.045777 | 6.1523 | 0.24262 | 0.74616 | 0.38452 | 0.88806 | -0.045777 | -0.064087 | 0.059509 | 0.045776 | 0.027466 | -0.032044 | 0.073243 | 0.013733 | 6.2943 | 122.438 | 0.091553 | 122.4472 | 122.4609 | 122.3236 | 122.319 | 122.2778 | -122.4838 | -122.3877 | 122.2961 | 122.4014 | 42.7231 | 48.7976
1148.9375 | 122.5845 | -47.7585 | 74.5468 | -0.0051118 | -0.025265 | -0.020264 | 0.066934 | -0.030443 | -0.045681 | -0.035692 | 0.00094606 | -0.021176 | 0.05385 | 0.046476 | -0.21808 | -0.014924 | -0.026671 | -6.4041 | 74.5377 | -47.9187 | 74.4507 | -41.6428 | -47.5204 | -47.5296 | -0.073242 | 74.4873 | -47.8317 | 74.6063 | -47.7676 | -47.8409 | -47.7722 | -0.16022 | -0.009155 | -0.09613 | 6.1157 | 0.22888 | 0.23804 | 0.3891 | 0.39825 | -0.073242 | -0.059509 | 0.059509 | -0.009155 | -0.013733 | -0.082397 | 0.059509 | -0.009155 | 6.2759 | 122.3694 | 0.064087 | 122.438 | 122.4564 | 122.319 | 122.2961 | 122.2458 | -122.4655 | -122.3785 | 122.2092 | 122.3648 | 41.3544 | 47.6852
1150.7344 | 122.5525 | -47.4655 | 74.8764 | 0.0025177 | -0.021206 | -0.019196 | 0.06843 | -0.032152 | -0.045254 | -0.037828 | 0.00094606 | -0.02139 | 0.055986 | 0.040708 | -0.21937 | -0.014924 | -0.02368 | -7.2327 | 74.8993 | -47.6257 | 74.7665 | -41.2582 | -47.0581 | -47.2321 | -0.086975 | 74.794 | -47.5342 | 74.9176 | -47.493 | -47.5571 | -47.4655 | -0.16022 | 0.022888 | -0.10986 | 6.2073 | 0.23346 | 0.40741 | 0.39368 | 0.56763 | -0.068665 | -0.082398 | 0.041199 | -0.027466 | 0 | -0.091553 | 0.068665 | -0.022888 | 6.3675 | 122.3923 | 0.041199 | 122.4518 | 122.525 | 122.3282 | 122.3648 | 122.2595 | -122.5021 | -122.4106 | 122.2321 | 122.3831 | 40.2328 | 47.3785
1152.4531 | 122.6074 | -47.612 | 74.7299 | -0.0051118 | -0.024838 | -0.016846 | 0.066294 | -0.03322 | -0.046749 | -0.038896 | -0.0021057 | -0.019895 | 0.055132 | 0.049253 | -0.22065 | -0.015778 | -0.02368 | -7.0129 | 74.7025 | -47.7448 | 74.6979 | -40.8554 | -47.2824 | -47.3602 | 0.036621 | 74.675 | -47.6532 | 74.794 | -47.5662 | -47.6486 | -47.5983 | -0.13275 | -0.027465 | -0.032043 | 6.7566 | 0.25177 | 0.32959 | 0.38452 | 0.46234 | -0.041198 | -0.054931 | 0.064087 | 0.045777 | 0.013733 | -0.036621 | 0.054931 | 0.004577 | 6.8893 | 122.4426 | 0.086975 | 122.4472 | 122.4472 | 122.3282 | 122.3145 | 122.287 | -122.4747 | -122.3831 | 122.3099 | 122.406 | 40.5991 | 47.6486
1154.25 | 122.5479 | -47.1771 | 75.1877 | -0.0051118 | -0.023983 | -0.017914 | 0.067575 | -0.031939 | -0.04504 | -0.037615 | -0.0021057 | -0.02139 | 0.055345 | 0.035795 | -0.22086 | -0.015778 | -0.02368 | -6.633 | 75.1877 | -47.2778 | 75.0595 | -40.1413 | -46.8842 | -46.962 | -0.12817 | 75.1099 | -47.2 | 75.2151 | -47.1817 | -47.2641 | -47.1863 | -0.10071 | 0 | -0.12817 | 7.0358 | 0.21515 | 0.29297 | 0.31586 | 0.39368 | -0.022888 | -0.07782 | 0.027466 | -0.004578 | -0.009155 | -0.086975 | 0.013733 | -0.064087 | 7.1365 | 122.3373 | 0.01831 | 122.4152 | 122.4655 | 122.3099 | 122.3648 | 122.287 | -122.4655 | -122.3877 | 122.2366 | 122.3923 | 40.5441 | 47.0489
1156.0469 | 122.4976 | -46.7926 | 75.6088 | -0.0051118 | -0.023343 | -0.016633 | 0.070993 | -0.030657 | -0.045681 | -0.037615 | -0.0051575 | -0.018399 | 0.057054 | 0.049039 | -0.22043 | -0.015351 | -0.024107 | -6.8024 | 75.6088 | -46.907 | 75.4715 | -39.4272 | -46.4996 | -46.5866 | -0.018311 | 75.5539 | -46.8246 | 75.5905 | -46.8292 | -46.9299 | -46.8246 | -0.11444 | 0 | -0.13733 | 7.3654 | 0.20599 | 0.29297 | 0.32043 | 0.40741 | -0.032043 | -0.054932 | -0.018311 | -0.036621 | -0.032043 | -0.13733 | 0 | -0.10529 | 7.4799 | 122.3785 | -0.004578 | 122.4152 | 122.5159 | 122.3785 | 122.4014 | 122.3465 | -122.5159 | -122.4335 | 122.2641 | 122.3831 | 39.9902 | 46.7743
1157.7656 | 122.6074 | -46.6141 | 75.7324 | -0.0051118 | -0.023129 | -0.018342 | 0.067362 | -0.032366 | -0.047604 | -0.038683 | -0.0051575 | -0.021176 | 0.054918 | 0.054166 | -0.21937 | -0.016633 | -0.02368 | -6.8848 | 75.7278 | -46.7377 | 75.6866 | -38.6032 | -46.1746 | -46.3348 | 0.041199 | 75.6592 | -46.6278 | 75.8286 | -46.5317 | -46.6049 | -46.5683 | -0.1236 | -0.004578 | -0.045776 | 8.0109 | 0.27924 | 0.43945 | 0.40283 | 0.56305 | -0.013733 | -0.073242 | 0.09613 | 0.082398 | 0.045777 | 0.009156 | 0.05951 | 0.022889 | 8.1345 | 122.4243 | 0.096131 | 122.4564 | 122.4655 | 122.287 | 122.3419 | 122.2733 | -122.4701 | -122.3602 | 122.3007 | 122.4426 | 39.7293 | 46.6553
1159.5469 | 122.6074 | -46.4355 | 75.8698 | -0.0051118 | -0.019925 | -0.016419 | 0.069925 | -0.030016 | -0.046963 | -0.038256 | 0.00094606 | -0.021817 | 0.056627 | 0.047117 | -0.21808 | -0.015351 | -0.023039 | -6.8298 | 75.8881 | -46.5683 | 75.8423 | -37.9852 | -46.0693 | -46.2387 | -0.009155 | 75.8057 | -46.5179 | 75.9888 | -46.4172 | -46.5134 | -46.4172 | -0.13275 | 0.018311 | -0.027466 | 8.4503 | 0.19684 | 0.36621 | 0.32959 | 0.49896 | -0.082397 | -0.064087 | 0.11902 | 0.018311 | 0.018311 | -0.07782 | 0.10071 | 0.004577 | 8.5831 | 122.4106 | 0.10071 | 122.5067 | 122.4564 | 122.3236 | 122.3236 | 122.2412 | -122.438 | -122.3877 | 122.2778 | 122.4243 | 39.6057 | 46.4264
1161.3281 | 122.4655 | -46.2982 | 76.1078 | 0.0025177 | -0.02612 | -0.018128 | 0.069712 | -0.036211 | -0.046963 | -0.036547 | 0.00094606 | -0.019467 | 0.057482 | 0.044126 | -0.21702 | -0.016633 | -0.024535 | -6.8481 | 76.1398 | -46.3943 | 75.9293 | -37.5595 | -45.8954 | -46.1151 | -0.082397 | 76.0757 | -46.3211 | 76.0574 | -46.3257 | -46.4081 | -46.3623 | -0.09613 | 0.032044 | -0.17853 | 8.7387 | 0.18311 | 0.40283 | 0.27924 | 0.49896 | -0.022888 | -0.032043 | -0.050354 | -0.027466 | -0.064087 | -0.10986 | -0.041199 | -0.086975 | 8.8348 | 122.3236 | -0.004578 | 122.3785 | 122.5342 | 122.3969 | 122.4381 | 122.374 | -122.5021 | -122.4289 | 122.2275 | 122.3557 | 39.4501 | 46.2158
1163.0469 | 122.4701 | -46.051 | 76.3275 | -0.0051118 | -0.019284 | -0.01706 | 0.073984 | -0.030871 | -0.044186 | -0.037187 | 0.00094606 | -0.019681 | 0.058123 | 0.039854 | -0.21808 | -0.012574 | -0.023253 | -6.5918 | 76.3229 | -46.1929 | 76.1673 | -37.2162 | -45.6436 | -45.9366 | -0.07782 | 76.2726 | -46.1014 | 76.2726 | -46.1426 | -46.2479 | -46.1243 | -0.14191 | -0.004578 | -0.16022 | 8.8348 | 0.11444 | 0.40741 | 0.25635 | 0.54932 | -0.050354 | -0.054932 | -0.054932 | -0.091553 | -0.073243 | -0.19684 | -0.022889 | -0.14648 | 8.9767 | 122.3602 | -0.041199 | 122.374 | 122.5159 | 122.374 | 122.374 | 122.3236 | -122.5204 | -122.4289 | 122.2183 | 122.3236 | 39.4592 | 45.9732
1164.8438 | 122.525 | -46.9803 | 75.4532 | 0.010147 | -0.024624 | -0.015992 | 0.071421 | -0.030443 | -0.047177 | -0.035692 | -0.0021057 | -0.02139 | 0.056414 | 0.049253 | -0.21766 | -0.015565 | -0.022185 | -6.3904 | 75.4395 | -47.0993 | 75.2701 | -37.706 | -46.4722 | -46.8109 | -0.07782 | 75.412 | -46.9666 | 75.412 | -46.9803 | -47.0718 | -46.9757 | -0.11902 | -0.013733 | -0.1831 | 9.2743 | 0.16937 | 0.50812 | 0.28839 | 0.62714 | 0.013733 | -0.041199 | -0.041199 | 0 | 0.004578 | -0.091552 | -0.009155 | -0.10529 | 9.3933 | 122.3694 | -0.013733 | 122.3785 | 122.5388 | 122.3785 | 122.4197 | 122.3923 | -122.5525 | -122.4197 | 122.2504 | 122.3923 | 40.5899 | 46.9025
1166.6406 | 122.4792 | -46.907 | 75.5127 | -0.0051118 | -0.022061 | -0.015992 | 0.07313 | -0.032366 | -0.044827 | -0.038469 | -0.0021057 | -0.018186 | 0.057695 | 0.049039 | -0.21552 | -0.014069 | -0.025389 | -7.3883 | 75.4852 | -47.0581 | 75.3296 | -37.4039 | -46.431 | -46.7789 | -0.10529 | 75.4395 | -46.9391 | 75.4578 | -46.962 | -47.0718 | -46.962 | -0.15106 | -0.027466 | -0.1831 | 9.5032 | 0.12817 | 0.47607 | 0.27923 | 0.62714 | -0.032044 | -0.073242 | -0.054931 | -0.054932 | -0.054932 | -0.16479 | -0.022888 | -0.13275 | 9.6542 | 122.3877 | -0.022888 | 122.3969 | 122.5433 | 122.3785 | 122.3923 | 122.3465 | -122.5708 | -122.4518 | 122.2366 | 122.3648 | 39.5187 | 46.8018
1168.4219 | 122.5845 | -42.2287 | 80.1132 | -0.0051118 | -0.022274 | -0.011292 | 0.070139 | -0.026171 | -0.04205 | -0.036974 | 0.0039979 | -0.022458 | 0.055986 | 0.041563 | -0.21915 | -0.015992 | -0.023253 | -5.4794 | 80.0949 | -42.3477 | 80.04 | -33.4167 | -41.7297 | -42.0319 | 0.045776 | 80.0217 | -42.2699 | 80.191 | -42.2195 | -42.2974 | -42.215 | -0.11902 | -0.01831 | -0.073242 | 8.812 | 0.19684 | 0.49896 | 0.31586 | 0.61798 | -0.041198 | -0.091553 | 0.07782 | 0.009156 | 0.013733 | -0.068664 | 0.054931 | -0.027466 | 8.931 | 122.3877 | 0.050354 | 122.4609 | 122.4426 | 122.2916 | 122.3236 | 122.2504 | -122.4609 | -122.3831 | 122.2687 | 122.4197 | 36.7493 | 42.2745
1170.2031 | 122.4335 | -38.1134 | 84.3475 | 0.010147 | -0.022488 | -0.01236 | 0.073984 | -0.025744 | -0.044613 | -0.037401 | -0.0082091 | -0.020536 | 0.057909 | 0.049467 | -0.21744 | -0.015992 | -0.02368 | -4.0009 | 84.3521 | -38.1958 | 84.0912 | -29.9423 | -37.7243 | -38.0173 | -0.054932 | 84.2606 | -38.1409 | 84.256 | -38.2141 | -38.2828 | -38.1821 | -0.082398 | 0.004578 | -0.25635 | 8.1711 | 0.09613 | 0.3891 | 0.17853 | 0.4715 | -0.027466 | -0.086975 | -0.091553 | -0.10071 | -0.068665 | -0.16937 | -0.041199 | -0.14191 | 8.2535 | 122.287 | -0.073242 | 122.3969 | 122.5479 | 122.4014 | 122.4655 | 122.374 | -122.5433 | -122.4884 | 122.2046 | 122.3694 | 34.1125 | 38.0585
1171.9844 | 122.5845 | -35.7239 | 86.618 | -0.0051118 | -0.023983 | -0.0072333 | 0.069498 | -0.031511 | -0.043972 | -0.039537 | -0.0051575 | -0.022672 | 0.057054 | 0.035795 | -0.21894 | -0.015137 | -0.021758 | -2.829 | 86.6272 | -35.8612 | 86.5585 | -27.6123 | -35.1746 | -35.5316 | 0.14648 | 86.5448 | -35.7651 | 86.6959 | -35.701 | -35.7697 | -35.7101 | -0.13733 | 0.009155 | -0.059509 | 8.1116 | 0.19226 | 0.54932 | 0.32959 | 0.68665 | -0.041199 | -0.073242 | 0.07782 | 0.022888 | 0.013733 | -0.045776 | 0.054932 | -0.004577 | 8.2489 | 122.4197 | 0.064087 | 122.4609 | 122.4884 | 122.3099 | 122.3511 | 122.2687 | -122.4792 | -122.3831 | 122.2824 | 122.4197 | 32.8949 | 35.8704
1173.7031 | 122.5067 | -34.0347 | 88.3301 | 0.010147 | -0.024197 | -0.0087287 | 0.071207 | -0.031511 | -0.043759 | -0.037187 | 0.0039979 | -0.022031 | 0.054918 | 0.045194 | -0.21702 | -0.013856 | -0.021117 | -1.9226 | 88.3621 | -34.1492 | 88.1836 | -26.2115 | -33.49 | -33.902 | 0.027466 | 88.2797 | -34.0485 | 88.3438 | -34.0897 | -34.1629 | -34.0988 | -0.11444 | 0.032044 | -0.14648 | 7.8232 | 0.13275 | 0.54474 | 0.24719 | 0.65918 | -0.013733 | -0.050354 | 0.013733 | -0.054932 | -0.064087 | -0.12817 | -0.050354 | -0.11444 | 7.9376 | 122.3328 | -0.041199 | 122.3923 | 122.5113 | 122.3282 | 122.3969 | 122.3145 | -122.4792 | -122.3785 | 122.2183 | 122.3785 | 32.1121 | 34.0622
1175.5 | 122.4976 | -33.2703 | 89.1724 | -0.012741 | -0.02142 | -0.010651 | 0.072702 | -0.032152 | -0.044613 | -0.036333 | -0.0021057 | -0.019895 | 0.055345 | 0.045621 | -0.21766 | -0.016633 | -0.027953 | -1.4694 | 89.1083 | -33.4305 | 88.8977 | -25.6577 | -32.6294 | -33.197 | 0.10986 | 89.0991 | -33.284 | 89.0945 | -33.3527 | -33.4305 | -33.3572 | -0.16022 | -0.064087 | -0.27466 | 7.6126 | 0.073243 | 0.64087 | 0.23346 | 0.80109 | -0.013733 | -0.073242 | -0.07782 | -0.082397 | -0.086975 | -0.16022 | -0.073242 | -0.14648 | 7.7728 | 122.3282 | -0.068664 | 122.3785 | 122.5388 | 122.3831 | 122.3785 | 122.3694 | -122.6028 | -122.4564 | 122.168 | 122.3648 | 31.8008 | 33.3801
1177.2188 | 122.5479 | -33.2703 | 89.0945 | -0.0051118 | 0.065311 | -0.0095831 | 0.06608 | -0.03322 | -0.018765 | -0.039537 | -0.0021057 | -0.020749 | 0.054064 | 0.044767 | -0.2183 | -0.016205 | -0.020476 | -4.8386 | 88.8428 | -32.46 | 89.1083 | -24.6872 | -56.0532 | -33.0688 | 0.49439 | 89.3051 | -33.0185 | 89.7034 | -32.666 | -32.9864 | -33.6319 | 0.81024 | -0.25177 | 0.013733 | 8.5831 | 0.20142 | -22.7829 | -0.60883 | -23.5931 | 0.25177 | 0.21057 | 0.60883 | 0.60425 | -0.36163 | 0.28381 | -0.6134 | 0.032044 | 7.7728 | 121.5683 | 0.35248 | 122.7219 | 121.3028 | 122.3236 | 122.113 | 122.5754 | -121.5546 | -122.113 | 122.3785 | 122.9736 | 28.4317 | 33.7646
1179 | 122.4976 | -45.4102 | 76.9363 | -0.0051118 | 0.092014 | 0.021606 | -0.0031337 | 0.06291 | 0.054294 | -0.042742 | -0.0021057 | -0.019467 | 0.0562 | 0.055234 | -0.21851 | -0.014283 | -0.02603 | 7.6675 | 76.9272 | -45.5658 | -33.9523 | 76.8951 | 76.6525 | 22.1649 | -0.068665 | 76.886 | -45.4788 | 76.9043 | -45.4926 | -45.607 | -45.4788 | -0.15564 | -0.009155 | -110.8887 | 122.3053 | 67.5751 | 122.0627 | 67.7307 | 122.2183 | -0.068665 | -0.050354 | -0.032043 | -0.082398 | -0.068665 | -0.19684 | 0 | -0.12817 | 122.4609 | 11.6135 | -0.013733 | 122.3831 | 122.493 | 122.3648 | 122.3373 | 122.2961 | -122.5021 | -122.4152 | 11.4578 | 122.3145 | 53.0777 | 45.3415
1180.7969 | 122.5479 | -75.8743 | 46.2341 | -0.012741 | 0.090305 | 0.27154 | 0.00049768 | 0.33357 | 0.055149 | -0.040819 | 0.00094606 | -0.020536 | 0.057695 | 0.045408 | -0.21872 | -0.014069 | -0.021758 | -5.6671 | 48.111 | -74.3317 | -59.6695 | 47.9095 | 47.6944 | 5.5618 | -1.2222 | 47.6624 | -74.8077 | 46.5591 | -75.8514 | -76.0025 | -75.975 | 1.5427 | 1.8768 | -105.9036 | 123.7839 | 81.4362 | 123.5687 | 79.8935 | 122.0261 | 1.0666 | 1.4282 | 0.32501 | 0.022889 | -0.10071 | -0.12817 | -1.1673 | -1.1948 | 122.2412 | 14.6622 | -1.0437 | 121.3669 | 122.4426 | 122.4701 | 123.9853 | 123.5367 | -120.5658 | -121.0419 | 16.2048 | 122.4335 | 70.2072 | 74.6521
1182.5156 | 122.5388 | -108.4808 | 14.1357 | 0.0025177 | 0.21399 | 0.088256 | -0.0027065 | 0.043684 | 0.055576 | -0.039751 | 0.00094606 | -0.021604 | 0.0562 | 0.044553 | -0.21851 | -0.015351 | -0.022826 | -19.5145 | 12.4146 | -110.2753 | -53.4073 | 11.1237 | 11.3113 | -10.0525 | -3.9505 | 12.5061 | -110.0693 | 11.2976 | -108.1787 | -107.4554 | -106.929 | -1.7944 | -1.7212 | -67.543 | 119.6045 | 98.4283 | 119.7922 | 100.2228 | 121.5866 | -1.5884 | -1.6296 | -2.8381 | 0.30212 | 1.5518 | 1.0254 | 3.1403 | 2.6138 | 121.3989 | 56.868 | 1.8906 | 121.3669 | 122.6898 | 122.5754 | 120.8954 | 120.9869 | -124.411 | -124.205 | 55.0735 | 119.7784 | 88.9664 | 104.5303
1184.3281 | 122.4518 | -107.0892 | 15.2527 | 0.0025177 | 0.46158 | 0.40442 | -0.0065517 | 0.11119 | 0.054935 | -0.038256 | 0.0039979 | -0.020749 | 0.058123 | 0.048612 | -0.2168 | -0.015351 | -0.025176 | -17.8986 | 15.1703 | -107.2632 | -37.088 | 15.0375 | 14.8773 | -6.5872 | -0.75531 | 15.2298 | -107.1808 | 15.1016 | -106.7184 | -107.0023 | -106.8787 | -0.17395 | -0.082398 | -52.3407 | 122.1268 | 100.502 | 121.9666 | 100.676 | 122.1405 | -0.091553 | -0.022889 | -0.15106 | 0.37079 | 0.21057 | 0.086975 | 0.30212 | 0.17853 | 122.3007 | 70.1752 | 0.46234 | 122.2824 | 122.4335 | 122.4106 | 122.2595 | 122.319 | -122.5159 | -122.4335 | 70.0012 | 122.1909 | 89.1907 | 106.3339
1186.0469 | 122.5937 | -118.9499 | 3.3463 | -0.0051118 | 0.14499 | 0.031646 | -0.0059109 | 0.05821 | 0.055362 | -0.038256 | 0.0039979 | -0.022245 | 0.054064 | 0.041776 | -0.21744 | -0.015565 | -0.024962 | -21.4508 | 3.3188 | -119.0506 | -35.1288 | 3.3737 | 3.1723 | -12.3367 | -0.91553 | 3.3371 | -119.0643 | 3.3508 | -118.5425 | -118.7759 | -118.5699 | -0.10071 | -0.027465 | -38.475 | 122.3236 | 106.6132 | 122.1222 | 106.7139 | 122.2229 | -0.11444 | -0.009155 | 0.004578 | 0.40741 | 0.37994 | 0.17395 | 0.49438 | 0.28839 | 122.4243 | 83.9218 | 0.52185 | 122.4152 | 122.3694 | 122.4014 | 122.2687 | 122.287 | -122.3969 | -122.4106 | 83.8211 | 122.3007 | 97.4991 | 118.0344
1187.8438 | 122.6852 | -117.6086 | 4.6509 | -0.0051118 | 0.16101 | 0.047241 | -0.0044155 | 0.051588 | 0.052585 | -0.03911 | -0.0021057 | -0.023954 | 0.054491 | 0.047117 | -0.2168 | -0.015565 | -0.020476 | -21.1029 | 4.4495 | -117.9108 | -33.6594 | 4.4907 | 4.2938 | -11.4349 | -0.88348 | 4.5593 | -117.8513 | 4.5822 | -117.3477 | -117.6407 | -117.1555 | -0.30212 | -0.20142 | -38.3102 | 122.0993 | 106.1737 | 121.9025 | 106.4758 | 122.2046 | -0.24261 | -0.091553 | -0.068665 | 0.26093 | 0.45319 | -0.032043 | 0.6958 | 0.21057 | 122.4014 | 84.2514 | 0.50354 | 122.4335 | 122.3602 | 122.4106 | 122.0581 | 122.168 | -122.5616 | -122.5021 | 83.9493 | 122.1909 | 96.5057 | 116.7252
1189.5625 | 122.2641 | -115.8188 | 6.2347 | -0.012741 | 0.34687 | 0.082702 | -0.0027065 | 0.097944 | 0.053226 | -0.041674 | -0.0051575 | -0.021176 | 0.054277 | 0.052244 | -0.21915 | -0.014069 | -0.021971 | -23.8129 | 11.9705 | -112.944 | -31.9611 | 5.3329 | 4.5181 | -11.2289 | -5.1773 | 7.5897 | -116.2216 | 4.6921 | -117.1967 | -116.6931 | -116.2857 | 2.8748 | 5.7358 | -38.1958 | 121.1517 | 104.5898 | 120.3369 | 101.7151 | 117.4622 | -0.40283 | 1.355 | -1.5427 | -1.3779 | -0.46692 | -0.87433 | -0.064087 | -0.4715 | 118.277 | 80.983 | -0.97504 | 120.9137 | 124.9146 | 123.8113 | 127.7893 | 123.4085 | -119.1788 | -122.4564 | 83.8577 | 120.5109 | 92.0059 | 110.6415
1191.3594 | 122.5159 | -116.7023 | 5.777 | -0.0051118 | 0.18772 | 0.069458 | -0.0076199 | 0.056074 | 0.053867 | -0.039751 | 0.0039979 | -0.022885 | 0.054491 | 0.047117 | -0.21616 | -0.015565 | -0.022612 | -22.3984 | 6.2164 | -117.2104 | -30.9814 | 4.6555 | 4.4769 | -10.8902 | -5.3055 | 4.5731 | -117.3157 | 5.2826 | -116.5604 | -116.6519 | -116.3635 | -0.50812 | 0.43945 | -36.7584 | 121.3577 | 105.8121 | 121.1792 | 106.3202 | 121.6873 | -0.6134 | -1.2039 | -0.49438 | 0.14191 | 0.33875 | 0.050354 | 0.95215 | 0.66376 | 121.8658 | 86.2289 | 0.75531 | 122.5983 | 123.4268 | 121.8887 | 122.9187 | 121.2753 | -122.9874 | -123.0927 | 85.7208 | 121.9849 | 94.3039 | 111.3968
1193.0781 | 122.5662 | -119.0231 | 3.2547 | -0.0051118 | 0.15525 | 0.036132 | -0.0027065 | 0.053297 | 0.053013 | -0.041033 | 0.00094606 | -0.019681 | 0.055986 | 0.045408 | -0.21915 | -0.014283 | -0.023894 | -21.9269 | 3.2913 | -119.1879 | -30.6885 | 3.1998 | 3.0075 | -11.467 | -0.91553 | 3.2639 | -119.0964 | 3.2776 | -118.6523 | -118.895 | -118.6203 | -0.16479 | 0.036621 | -33.9432 | 122.2229 | 107.5562 | 122.0306 | 107.7209 | 122.1954 | -0.073243 | 0.009155 | 0.022888 | 0.37079 | 0.40283 | 0.12817 | 0.47607 | 0.20142 | 122.3877 | 88.4994 | 0.44403 | 122.374 | 122.4792 | 122.3602 | 122.3145 | 122.287 | -122.4426 | -122.3511 | 88.3347 | 122.3007 | 97.0963 | 118.1076
1194.8594 | 122.5616 | -118.8583 | 3.4607 | 0.0025177 | 0.15738 | 0.031646 | -0.0078335 | 0.044966 | 0.051731 | -0.038683 | 0.00094606 | -0.023313 | 0.055132 | 0.042417 | -0.21808 | -0.014283 | -0.023253 | 3.2272 | 3.4287 | -119.0002 | -31.7276 | 3.4882 | 3.2867 | -10.7346 | -0.85144 | 3.447 | -118.9224 | 3.4515 | -118.428 | -118.6569 | -118.4418 | -0.14191 | -0.032043 | -35.1883 | 122.3465 | 108.1238 | 122.1451 | 108.2657 | 122.287 | -0.064087 | -0.013733 | -0.009155 | 0.4303 | 0.41657 | 0.20142 | 0.48065 | 0.2655 | 122.4884 | 87.2726 | 0.49438 | 122.374 | 122.4289 | 122.3694 | 122.287 | 122.3053 | -122.4609 | -122.3831 | 87.1307 | 122.3099 | 122.0856 | 118.0069
1196.6562 | 122.4014 | -118.483 | 3.6896 | -0.0051118 | 0.16123 | 0.036346 | -0.0056973 | 0.049452 | 0.055362 | -0.039324 | 0.00094606 | -0.01904 | 0.056414 | 0.04968 | -0.21937 | -0.01471 | -0.021544 | 3.3142 | 3.5202 | -118.9041 | -30.7938 | 3.479 | 3.2684 | -10.7758 | -0.90637 | 3.5019 | -118.8766 | 3.5477 | -118.3594 | -118.602 | -118.3456 | -0.42114 | -0.16937 | -34.4833 | 121.962 | 107.7072 | 121.7514 | 108.1284 | 122.1725 | -0.39368 | -0.18768 | -0.14191 | 0.1236 | 0.13733 | -0.11902 | 0.53101 | 0.27466 | 122.3831 | 88.1104 | 0.51727 | 122.4243 | 122.4243 | 122.3785 | 122.0032 | 121.9849 | -122.5937 | -122.5662 | 87.6892 | 122.0306 | 121.7972 | 117.5766
1198.375 | 122.4426 | -57.1426 | 65.1993 | -0.0051118 | -0.016293 | -0.08136 | -0.010824 | -0.028734 | -0.048672 | -0.041674 | 0.00094606 | -0.022672 | 0.055132 | 0.045408 | -0.21808 | -0.015992 | -0.023253 | -0.086975 | 0.10986 | -0.14191 | -0.09613 | 0.091553 | -0.068665 | 0.004578 | 0.10071 | 65.1123 | -57.074 | 65.2679 | -56.9962 | -57.0786 | -56.9687 | 57.0007 | -65.0894 | -65.2954 | 57.2342 | 57.1472 | 57.074 | 0.14649 | 0.073242 | 0.068664 | -0.086975 | 0.068664 | 0.14648 | 0.17395 | 0.064087 | 0.10529 | -0.004577 | 0.23346 | 0.045777 | 0.07782 | 122.3419 | 0.25177 | 122.1863 | 57.2525 | 122.2549 | -65.3412 | -122.2733 | 57.0465 | 122.4106 | 57.0557 | 57.2433
1200.1719 | 122.3694 | -56.955 | 65.4419 | -0.012741 | -0.011593 | -0.078156 | -0.0042019 | -0.030016 | -0.049526 | -0.040178 | -0.0082091 | -0.017331 | 0.055559 | 0.048612 | -0.21766 | -0.01471 | -0.022612 | -0.11444 | 0.13275 | -0.16479 | -0.16937 | -0.032043 | -0.19684 | -0.11902 | -0.16937 | 65.3778 | -56.9458 | 65.3915 | -56.9321 | -57.0602 | -56.8954 | 56.7902 | -65.3091 | -65.6113 | 56.9229 | 56.8359 | 56.7581 | 0.045776 | -0.032043 | 0.009155 | -0.064087 | -0.050354 | 0.022888 | 0.059509 | -0.10529 | 0.050354 | -0.11444 | 0.13275 | -0.004578 | 0.013733 | 122.3373 | 0.29755 | 122.3236 | 57.0877 | 122.3328 | -65.6067 | -122.3877 | 56.7856 | 122.3465 | 56.8405 | 56.7856
1201.9062 | 122.3831 | -56.6574 | 65.6982 | 0.0025177 | -0.010525 | -0.077942 | -0.0033475 | -0.027239 | -0.050808 | -0.038469 | 0.00094606 | -0.018827 | 0.055773 | 0.050962 | -0.21766 | -0.013215 | -0.022826 | -0.10986 | 0.12817 | -0.15564 | -0.16479 | -0.050354 | -0.20142 | -0.1236 | -0.23804 | 65.6342 | -56.7078 | 65.6204 | -56.6895 | -56.7902 | -56.6757 | 56.5018 | -65.5701 | -65.863 | 56.6071 | 56.5338 | 56.456 | 0.032044 | -0.045776 | -0.050354 | -0.064087 | -0.07782 | -0.032043 | -0.01831 | -0.13275 | 0.032044 | -0.082397 | 0.10529 | -0.009155 | 0.018311 | 122.3282 | 0.28381 | 122.3419 | 56.7856 | 122.2916 | -65.8539 | -122.406 | 56.4926 | 122.2778 | 56.5475 | 56.4194
1203.7031 | 122.4243 | -56.4835 | 65.8905 | -0.012741 | -0.010311 | -0.078583 | -0.0044155 | -0.030871 | -0.050381 | -0.040819 | 0.00094606 | -0.019681 | 0.057268 | 0.047758 | -0.21723 | -0.013642 | -0.022185 | -0.073242 | 0.10986 | -0.13733 | -0.11902 | 0.018311 | -0.13733 | -0.07782 | -0.16479 | 65.7715 | -56.5109 | 65.831 | -56.4835 | -56.5979 | -56.4697 | 56.3461 | -65.7806 | -66.0095 | 56.5018 | 56.4056 | 56.3461 | 0.059509 | 0 | -0.027466 | -0.11902 | -0.059509 | 0 | 0.013732 | -0.11444 | 0.041198 | -0.086975 | 0.15564 | 0.01831 | 0.027466 | 122.3419 | 0.24719 | 122.2824 | 56.5933 | 122.2549 | -66.0278 | -122.4014 | 56.3644 | 122.3145 | 56.4102 | 56.3187
1205.4375 | 122.4609 | -56.369 | 65.9821 | -0.0051118 | -0.011166 | -0.078156 | -0.0035611 | -0.029802 | -0.046749 | -0.040605 | -0.0021057 | -0.020536 | 0.055132 | 0.04968 | -0.21659 | -0.016846 | -0.024321 | -0.13275 | 0.13275 | -0.20142 | -0.18768 | -0.045776 | -0.19684 | -0.1236 | -0.25177 | 65.9454 | -56.4148 | 65.9729 | -56.3644 | -56.4789 | -56.3461 | 56.1676 | -65.8493 | -66.1697 | 56.3232 | 56.2454 | 56.1722 | 0.07782 | 0.004578 | -0.045776 | -0.036621 | -0.009156 | 0.004578 | 0.022889 | -0.10986 | 0.068665 | -0.064087 | 0.15564 | 0.013733 | 0.050354 | 122.3877 | 0.33417 | 122.3602 | 56.5018 | 122.3145 | -66.1835 | -122.3969 | 56.1813 | 122.3419 | 56.2363 | 56.1172
1207.2344 | 122.4289 | -56.2042 | 66.1926 | 0.0025177 | -0.014157 | -0.08136 | -0.0048427 | -0.030657 | -0.04974 | -0.041674 | -0.0021057 | -0.018613 | 0.057695 | 0.047544 | -0.21723 | -0.015992 | -0.023039 | -0.16937 | 0.091553 | -0.19226 | -0.19226 | -0.036621 | -0.16937 | -0.11902 | -0.24719 | 66.1331 | -56.2317 | 66.0965 | -56.1813 | -56.3049 | -56.1859 | 56.012 | -66.1011 | -66.3849 | 56.1676 | 56.0852 | 56.0349 | 0.073242 | 0.022888 | -0.027465 | -0.059509 | -0.09613 | 0.022889 | 0.018311 | -0.10071 | 0.045776 | -0.073243 | 0.15564 | 0 | 0.050354 | 122.3282 | 0.28381 | 122.3648 | 56.2958 | 122.3373 | -66.3849 | -122.4243 | 56.012 | 122.3007 | 56.0349 | 55.957
1209.0312 | 122.4838 | -56.0394 | 66.3254 | 0.010147 | -0.013729 | -0.077515 | -0.0031337 | -0.028948 | -0.046749 | -0.040178 | -0.0021057 | -0.020749 | 0.057482 | 0.046262 | -0.21808 | -0.015137 | -0.023253 | -0.091553 | 0.10529 | -0.16937 | -0.11444 | 0.041199 | -0.10529 | -0.073242 | -0.14648 | 66.2613 | -56.0898 | 66.3071 | -55.9982 | -56.1356 | -56.0211 | 55.8701 | -66.2201 | -66.4398 | 56.0806 | 55.9662 | 55.9341 | 0.096131 | 0.064087 | -0.050354 | -0.064086 | -0.01831 | 0.041199 | 0.018311 | -0.09613 | 0.068665 | -0.045776 | 0.21057 | 0.054932 | 0.091553 | 122.3969 | 0.27466 | 122.3511 | 56.1447 | 122.3007 | -66.4948 | -122.4152 | 55.925 | 122.3465 | 55.9479 | 55.8929
1210.7656 | 122.4197 | -55.8701 | 66.5405 | -0.0051118 | -0.010311 | -0.079224 | -0.0033475 | -0.027025 | -0.047817 | -0.040178 | -0.0021057 | -0.018827 | 0.057054 | 0.045194 | -0.21872 | -0.014924 | -0.02133 | -0.12817 | 0.1236 | -0.17853 | -0.18768 | -0.050354 | -0.20142 | -0.14191 | -0.29755 | 66.449 | -55.9204 | 66.4444 | -55.8838 | -56.0028 | -55.8517 | 55.6915 | -66.4169 | -66.7282 | 55.8197 | 55.7281 | 55.6686 | 0.036621 | -0.022888 | -0.050354 | -0.091552 | -0.09613 | -0.013733 | 0.01831 | -0.13275 | 0.068664 | -0.082398 | 0.12817 | -0.009155 | 0.036621 | 122.3648 | 0.30212 | 122.3694 | 55.9937 | 122.319 | -66.7191 | -122.4609 | 55.6824 | 122.3145 | 55.7419 | 55.5725
1212.5625 | 122.5388 | -55.8243 | 66.5359 | -0.012741 | -0.015011 | -0.081147 | -0.0071927 | -0.029375 | -0.050167 | -0.039537 | -0.0051575 | -0.023526 | 0.057268 | 0.041563 | -0.2168 | -0.01706 | -0.020689 | -0.068665 | 0.086975 | -0.14648 | -0.059509 | 0.10986 | -0.027466 | 0.022888 | -0.16479 | 66.4673 | -55.8701 | 66.5405 | -55.751 | -55.8472 | -55.7785 | 55.6778 | -66.449 | -66.5955 | 55.9341 | 55.8472 | 55.7968 | 0.16937 | 0.11902 | -0.045776 | -0.068665 | 0.004577 | 0.073242 | 0.045777 | -0.022888 | 0.091553 | 0.022888 | 0.25635 | 0.086975 | 0.11902 | 122.4106 | 0.23346 | 122.3373 | 55.9113 | 122.2916 | -66.6824 | -122.406 | 55.7648 | 122.3648 | 55.7556 | 55.6595
1214.3438 | 122.5571 | -55.7373 | 66.5863 | 0.0025177 | -0.011166 | -0.07837 | -0.0065517 | -0.02788 | -0.048245 | -0.041246 | 0.00094606 | -0.019467 | 0.0562 | 0.053312 | -0.21766 | -0.016633 | -0.026244 | -0.068665 | 0.068665 | -0.13275 | -0.059509 | 0.10529 | -0.064087 | -0.018311 | -0.20142 | 66.4902 | -55.8151 | 66.6458 | -55.6915 | -55.7739 | -55.6641 | 55.6046 | -66.5176 | -66.6458 | 55.8426 | 55.719 | 55.6732 | 0.11444 | 0.068664 | -0.07782 | -0.096131 | 0.059509 | 0.045777 | 0.073243 | -0.036621 | 0.15106 | 0.041199 | 0.23804 | 0.073242 | 0.1236 | 122.4609 | 0.20142 | 122.3053 | 55.806 | 122.2275 | -66.7191 | -122.4014 | 55.6778 | 122.3831 | 55.6686 | 55.5359
1216.1406 | 122.5708 | -55.7098 | 66.6092 | -0.012741 | -0.010952 | -0.076661 | -0.0029201 | -0.03258 | -0.049313 | -0.040178 | 0.00094606 | -0.019681 | 0.056841 | 0.046476 | -0.21872 | -0.016205 | -0.020262 | -0.15106 | 0.059509 | -0.20599 | -0.16937 | -0.022888 | -0.21057 | -0.10529 | -0.24719 | 66.5726 | -55.7556 | 66.687 | -55.6549 | -55.7602 | -55.6366 | 55.5038 | -66.5497 | -66.7786 | 55.687 | 55.6046 | 55.4993 | 0.10071 | -0.004577 | -0.045776 | -0.036621 | 0.07782 | 0.054932 | 0.073242 | -0.050354 | 0.11902 | -0.004578 | 0.18311 | 0.036621 | 0.10071 | 122.4426 | 0.2655 | 122.3282 | 55.7693 | 122.2824 | -66.8152 | -122.3648 | 55.5405 | 122.3969 | 55.5588 | 55.4626
1217.8594 | 122.5204 | -55.5817 | 66.7831 | 0.010147 | -0.013516 | -0.079224 | -0.0027065 | -0.031511 | -0.050808 | -0.039965 | 0.0039979 | -0.01904 | 0.056627 | 0.045408 | -0.21808 | -0.01471 | -0.021758 | -0.13275 | 0.073242 | -0.20142 | -0.16479 | -0.022888 | -0.15564 | -0.091553 | -0.21057 | 66.7557 | -55.6183 | 66.7969 | -55.5496 | -55.6549 | -55.5405 | 55.3802 | -66.7099 | -66.9479 | 55.5588 | 55.4901 | 55.426 | 0.10986 | 0.045776 | -0.036621 | -0.027466 | 0.013733 | 0.032043 | 0.041199 | -0.073242 | 0.07782 | -0.036621 | 0.17853 | 0.036621 | 0.068664 | 122.4152 | 0.27466 | 122.374 | 55.6549 | 122.3373 | -66.9846 | -122.4014 | 55.4169 | 122.3785 | 55.4489 | 55.3711
1219.6406 | 122.4838 | -55.545 | 66.8472 | 0.0025177 | -0.012661 | -0.079651 | -0.0037747 | -0.028948 | -0.046963 | -0.041674 | -0.0021057 | -0.020108 | 0.055986 | 0.041135 | -0.21744 | -0.015137 | -0.021758 | -0.18768 | 0.064087 | -0.21057 | -0.2243 | -0.086975 | -0.24261 | -0.15564 | -0.33417 | 66.7786 | -55.5817 | 66.806 | -55.5588 | -55.6549 | -55.5267 | 55.3345 | -66.7831 | -67.0715 | 55.4581 | 55.3894 | 55.3024 | 0.054931 | -0.032044 | -0.036621 | -0.068665 | -0.041199 | -0.013733 | 0.018311 | -0.10986 | 0.054932 | -0.073242 | 0.1236 | -0.013733 | 0.022888 | 122.3877 | 0.27466 | 122.3602 | 55.6091 | 122.3236 | -67.0578 | -122.4289 | 55.3207 | 122.3511 | 55.3574 | 55.2109
1221.4219 | 122.5296 | -55.4626 | 66.8976 | -0.0051118 | -0.013943 | -0.079224 | -0.0050565 | -0.027025 | -0.047817 | -0.038469 | -0.0021057 | -0.020322 | 0.057482 | 0.044767 | -0.21723 | -0.014496 | -0.022612 | -0.1236 | 0.082397 | -0.19226 | -0.14648 | 0 | -0.13733 | -0.07782 | -0.21057 | 66.8427 | -55.5313 | 66.8976 | -55.4443 | -55.5496 | -55.4352 | 55.2704 | -66.8152 | -67.0441 | 55.4626 | 55.3848 | 55.3253 | 0.11444 | 0.054932 | -0.068665 | -0.054932 | 0 | 0.01831 | 0.027465 | -0.086976 | 0.09613 | -0.018311 | 0.19226 | 0.045777 | 0.086975 | 122.4289 | 0.27466 | 122.374 | 55.545 | 122.3053 | -67.0898 | -122.4289 | 55.3162 | 122.3602 | 55.3391 | 55.2521
1223.1406 | 122.4655 | -55.4855 | 66.9022 | 0.0025177 | -0.013943 | -0.080506 | -0.0065517 | -0.032152 | -0.052304 | -0.040392 | -0.0021057 | -0.017545 | 0.057268 | 0.053312 | -0.2168 | -0.016205 | -0.021544 | -0.18768 | 0.09613 | -0.18768 | -0.21515 | -0.064087 | -0.1831 | -0.13275 | -0.31586 | 66.8701 | -55.5405 | 66.8152 | -55.5176 | -55.6 | -55.4855 | 55.2979 | -66.806 | -67.1173 | 55.4214 | 55.3528 | 55.3024 | 0.054932 | 0.004578 | -0.054931 | -0.032044 | -0.086975 | -0.032043 | 0 | -0.11444 | 0.054931 | -0.05951 | 0.1236 | -0.027466 | 0.022888 | 122.3557 | 0.28381 | 122.4106 | 55.5817 | 122.3557 | -67.0898 | -122.4426 | 55.2704 | 122.3007 | 55.2979 | 55.1697
1224.9219 | 122.6212 | -55.8517 | 66.4856 | 0.0025177 | -0.011807 | -0.079438 | -0.0052701 | -0.028307 | -0.047604 | -0.039324 | -0.0021057 | -0.022245 | 0.053209 | 0.051816 | -0.2168 | -0.01471 | -0.020049 | -0.12817 | 0.036621 | -0.16937 | -0.10071 | 0.054932 | -0.10986 | -0.050354 | -0.36163 | 66.4215 | -55.8792 | 66.5909 | -55.8243 | -55.8929 | -55.7739 | 55.6824 | -66.449 | -66.5863 | 55.9067 | 55.8014 | 55.7419 | 0.11902 | 0.05951 | -0.027465 | -0.064087 | 0.10528 | 0.027466 | 0.07782 | -0.041198 | 0.10528 | -0.013733 | 0.22431 | 0.068665 | 0.054931 | 122.4701 | 0.20599 | 122.3007 | 55.8884 | 122.2733 | -66.655 | -122.3648 | 55.751 | 122.4426 | 55.7236 | 55.4901
1226.6562 | 122.6212 | -55.4535 | 66.9067 | 0.0025177 | -0.012448 | -0.077942 | -0.0037747 | -0.028093 | -0.04739 | -0.042742 | -0.0021057 | -0.018399 | 0.054705 | 0.050535 | -0.21894 | -0.015137 | -0.021117 | -0.07782 | 0.041199 | -0.15564 | -0.07782 | 0.068665 | -0.10071 | -0.032043 | -0.21515 | 66.8152 | -55.4672 | 66.9937 | -55.3757 | -55.4535 | -55.3391 | 55.2979 | -66.8655 | -66.9846 | 55.5222 | 55.4214 | 55.3528 | 0.1236 | 0.054932 | -0.013733 | -0.091552 | 0.086975 | 0.07782 | 0.11444 | 0 | 0.12817 | 0.013733 | 0.22431 | 0.07782 | 0.091553 | 122.4609 | 0.19684 | 122.2824 | 55.4947 | 122.2687 | -67.0624 | -122.374 | 55.3757 | 122.4472 | 55.3757 | 55.2383
1228.4375 | 122.5433 | -55.22 | 67.1585 | 0.0025177 | -0.016293 | -0.079011 | -0.0048427 | -0.029589 | -0.050808 | -0.038683 | 0.00094606 | -0.022031 | 0.057909 | 0.052457 | -0.21872 | -0.016633 | -0.024535 | -0.15106 | 0.10071 | -0.17853 | -0.16937 | -0.036621 | -0.14648 | -0.091553 | -0.24719 | 67.1265 | -55.2429 | 67.1677 | -55.2063 | -55.3024 | -55.1834 | 55.0415 | -67.0578 | -67.3279 | 55.1834 | 55.1285 | 55.0735 | 0.086975 | 0.032044 | -0.022888 | -0.032043 | 0.009156 | 0.013733 | 0.036621 | -0.082397 | 0.059509 | -0.059509 | 0.14191 | 0.009155 | 0.036621 | 122.4106 | 0.27924 | 122.3694 | 55.3207 | 122.3465 | -67.337 | -122.4014 | 55.0507 | 122.3877 | 55.069 | 54.9728
1230.1406 | 122.5021 | -55.0964 | 67.3187 | 0.0025177 | -0.011593 | -0.078583 | -0.0031337 | -0.028093 | -0.050167 | -0.040392 | -0.0021057 | -0.018827 | 0.057482 | 0.045194 | -0.22022 | -0.015778 | -0.019621 | -0.15106 | 0.086975 | -0.18768 | -0.2243 | -0.10529 | -0.23346 | -0.12817 | -0.33875 | 67.2546 | -55.1376 | 67.2501 | -55.1285 | -55.2292 | -55.0964 | 54.9088 | -67.2318 | -67.543 | 54.9911 | 54.9683 | 54.863 | 0.059509 | -0.045776 | -0.041198 | -0.064087 | -0.068665 | -0.032043 | 0 | -0.13275 | 0.041198 | -0.091553 | 0.082397 | -0.036621 | 0.009155 | 122.3877 | 0.27466 | 122.3923 | 55.1834 | 122.3511 | -67.5064 | -122.4564 | 54.8721 | 122.3465 | 54.9454 | 54.7577
1231.9219 | 122.5388 | -55.3162 | 67.0395 | -0.012741 | -0.010311 | -0.076447 | -0.0039883 | -0.029162 | -0.048886 | -0.040819 | -0.0021057 | -0.019254 | 0.057909 | 0.046476 | -0.21872 | -0.014283 | -0.020262 | -0.10529 | 0.082397 | -0.16479 | -0.10986 | 0.041199 | -0.12817 | -0.045776 | -0.21973 | 67.0166 | -55.3482 | 67.099 | -55.2795 | -55.3894 | -55.2567 | 55.1514 | -66.9571 | -67.1494 | 55.3574 | 55.2704 | 55.188 | 0.11902 | 0.036621 | -0.032044 | -0.022888 | 0.059509 | 0.036621 | 0.059509 | -0.073242 | 0.091553 | -0.041198 | 0.20599 | 0.054932 | 0.068665 | 122.4472 | 0.24719 | 122.3648 | 55.3986 | 122.3328 | -67.2043 | -122.3877 | 55.2063 | 122.4152 | 55.2109 | 55.0964
1233.7031 | 122.5571 | -55.4031 | 66.9342 | -0.012741 | -0.013302 | -0.079011 | -0.0054837 | -0.032366 | -0.049954 | -0.041674 | -0.0082091 | -0.020749 | 0.0562 | 0.042417 | -0.21552 | -0.01706 | -0.021544 | -0.11902 | 0.050354 | -0.15564 | -0.12817 | 0.032043 | -0.10071 | -0.032043 | -0.3479 | 66.8564 | -55.4306 | 66.9846 | -55.3528 | -55.4489 | -55.3528 | 55.2475 | -66.8838 | -67.0624 | 55.4352 | 55.3711 | 55.3024 | 0.1236 | 0.054932 | -0.027466 | -0.07782 | 0.050354 | 0.050354 | 0.050354 | -0.045777 | 0.07782 | -0.018311 | 0.18768 | 0.027466 | 0.07782 | 122.4152 | 0.20599 | 122.287 | 55.4535 | 122.2595 | -67.0898 | -122.3648 | 55.275 | 122.3877 | 55.2841 | 55.0552
1235.4062 | 122.5159 | -55.5771 | 66.8106 | 0.010147 | -0.013516 | -0.079011 | -0.0029201 | -0.031939 | -0.048245 | -0.039537 | -0.0082091 | -0.017972 | 0.056414 | 0.046903 | -0.2183 | -0.015351 | -0.022612 | -0.11444 | 0.091553 | -0.17395 | -0.13275 | 0.004578 | -0.11444 | -0.054932 | -0.27924 | 66.7603 | -55.6458 | 66.8106 | -55.5542 | -55.6503 | -55.5222 | 55.4031 | -66.7191 | -66.9434 | 55.5817 | 55.5222 | 55.4626 | 0.11902 | 0.059509 | -0.068665 | -0.050354 | 0 | 0.022888 | 0.054931 | -0.073243 | 0.1236 | -0.004578 | 0.17853 | 0.041199 | 0.091553 | 122.4564 | 0.2655 | 122.406 | 55.6686 | 122.3373 | -66.9846 | -122.4564 | 55.4443 | 122.3877 | 55.4626 | 55.2979
1237.1875 | 122.5021 | -55.7556 | 66.6321 | 0.0025177 | -0.014798 | -0.079224 | -0.0071927 | -0.032152 | -0.051449 | -0.041246 | 0.0039979 | -0.021176 | 0.056627 | 0.046903 | -0.2168 | -0.016633 | -0.023253 | -0.10071 | 0.082397 | -0.15564 | -0.11444 | 0.050354 | -0.073242 | -0.041199 | -0.36163 | 66.5222 | -55.8563 | 66.5634 | -55.7556 | -55.838 | -55.751 | 55.6 | -66.5497 | -66.7465 | 55.806 | 55.7144 | 55.6824 | 0.11444 | 0.082398 | -0.10071 | -0.10986 | -0.068664 | 0 | 0.004577 | -0.082398 | 0.10529 | 0.01831 | 0.20599 | 0.041199 | 0.10071 | 122.4197 | 0.23804 | 122.3785 | 55.838 | 122.2778 | -66.7877 | -122.4884 | 55.6412 | 122.319 | 55.6549 | 55.394
1238.9062 | 122.5159 | -56.1218 | 66.2613 | 0.010147 | -0.014584 | -0.079651 | -0.0063381 | -0.032152 | -0.050595 | -0.041246 | 0.00094606 | -0.018613 | 0.0562 | 0.042203 | -0.21808 | -0.016633 | -0.025389 | -0.073242 | 0.091553 | -0.11902 | -0.09613 | 0.064087 | -0.059509 | 0 | -0.31586 | 66.1926 | -56.1813 | 66.2292 | -56.1218 | -56.1905 | -56.1264 | 56.0028 | -66.1697 | -66.3574 | 56.1859 | 56.1218 | 56.0623 | 0.11902 | 0.05951 | -0.059509 | -0.068665 | -0.032044 | 0 | -0.004578 | -0.068665 | 0.054931 | -0.009156 | 0.18311 | 0.022889 | 0.059509 | 122.4106 | 0.21057 | 122.374 | 56.2134 | 122.3145 | -66.3803 | -122.4426 | 56.0257 | 122.3511 | 56.0486 | 55.806
1240.6875 | 122.4884 | -56.0257 | 66.394 | 0.0025177 | -0.011807 | -0.07837 | -0.00099752 | -0.035143 | -0.048031 | -0.043383 | 0.00094606 | -0.01904 | 0.05855 | 0.047971 | -0.21659 | -0.016419 | -0.020689 | -0.086975 | 0.1236 | -0.13733 | -0.1236 | 0.013733 | -0.15106 | -0.082397 | -0.33875 | 66.3162 | -56.0394 | 66.3666 | -56.0211 | -56.1356 | -56.0028 | 55.8884 | -66.2704 | -66.5176 | 56.0394 | 55.9433 | 55.8746 | 0.054932 | -0.013733 | -0.013733 | -0.07782 | -0.027466 | 0.004578 | 0.022888 | -0.10986 | 0.036621 | -0.09613 | 0.15106 | 0.013733 | 0.018311 | 122.406 | 0.26093 | 122.3557 | 56.1493 | 122.3419 | -66.5314 | -122.4335 | 55.9021 | 122.3923 | 55.9387 | 55.687
1242.4844 | 122.612 | -56.0623 | 66.2521 | -0.0051118 | -0.016507 | -0.082428 | -0.0074063 | -0.033648 | -0.049313 | -0.039965 | 0.00094606 | -0.020963 | 0.054918 | 0.044767 | -0.21851 | -0.017487 | -0.022612 | -0.054932 | 0.07782 | -0.10071 | -0.027466 | 0.15106 | -0.009155 | 0.041199 | -0.24261 | 66.2384 | -56.0898 | 66.3849 | -55.9525 | -56.0532 | -55.9708 | 55.9616 | -66.1743 | -66.2796 | 56.2134 | 56.1035 | 56.0532 | 0.14191 | 0.091553 | -0.027466 | -0.013733 | 0.13275 | 0.10986 | 0.091553 | 0.009155 | 0.11902 | 0.036621 | 0.25177 | 0.073242 | 0.13733 | 122.4747 | 0.17853 | 122.3282 | 56.1401 | 122.3007 | -66.3528 | -122.3419 | 56.0349 | 122.4472 | 56.0074 | 55.8197
1244.2656 | 122.6486 | -56.0394 | 66.3345 | -0.0051118 | -0.013943 | -0.080506 | -0.0054837 | -0.032793 | -0.04739 | -0.043169 | -0.0021057 | -0.018827 | 0.054277 | 0.047117 | -0.21851 | -0.016633 | -0.022826 | -0.059509 | 0.086975 | -0.12817 | -0.009155 | 0.16937 | 0 | 0.064087 | -0.2243 | 66.2201 | -56.0806 | 66.4398 | -55.8929 | -55.9845 | -55.9113 | 55.9113 | -66.2476 | -66.3437 | 56.2088 | 56.1035 | 56.0394 | 0.19226 | 0.12817 | -0.041198 | -0.11444 | 0.10528 | 0.14648 | 0.12817 | 0.054932 | 0.16937 | 0.09613 | 0.29755 | 0.11902 | 0.18768 | 122.5204 | 0.21515 | 122.3007 | 56.1264 | 122.2595 | -66.4627 | -122.4152 | 56.0303 | 122.4792 | 55.9799 | 55.8151
1246 | 122.5204 | -56.1584 | 66.2064 | -0.0051118 | -0.011807 | -0.08136 | -0.0029201 | -0.029589 | -0.053372 | -0.037828 | -0.0021057 | -0.019467 | 0.055345 | 0.049039 | -0.21851 | -0.015992 | -0.021117 | -0.086975 | 0.1236 | -0.13275 | -0.11444 | 0 | -0.11444 | -0.050354 | -0.32044 | 66.1789 | -56.2363 | 66.2292 | -56.1493 | -56.2546 | -56.1401 | 56.0257 | -66.0828 | -66.3208 | 56.1584 | 56.1081 | 56.044 | 0.082397 | 0.01831 | -0.07782 | -0.027466 | 0.022888 | 0.009155 | 0.01831 | -0.096131 | 0.09613 | -0.018311 | 0.13275 | 0.01831 | 0.086975 | 122.4655 | 0.25635 | 122.4152 | 56.282 | 122.3373 | -66.3391 | -122.4426 | 56.044 | 122.3877 | 56.0715 | 55.838
1247.7969 | 122.5433 | -56.4514 | 65.9637 | -0.0051118 | -0.012448 | -0.077942 | -0.0037747 | -0.031298 | -0.049954 | -0.040605 | -0.0021057 | -0.017331 | 0.052568 | 0.05203 | -0.21723 | -0.015137 | -0.022612 | -0.064087 | 0.11444 | -0.12817 | -0.086975 | 0.059509 | -0.082397 | -0.032043 | -0.27466 | 65.8722 | -56.4835 | 65.9729 | -56.3828 | -56.4972 | -56.3782 | 56.3232 | -65.8493 | -66.0507 | 56.5109 | 56.4194 | 56.369 | 0.096131 | 0.045777 | -0.032043 | -0.091553 | 0.009155 | 0.068665 | 0.073242 | -0.045776 | 0.10529 | -0.013733 | 0.18768 | 0.041199 | 0.10071 | 122.4564 | 0.24262 | 122.3557 | 56.5659 | 122.3236 | -66.0919 | -122.4472 | 56.3644 | 122.4243 | 56.3873 | 56.1768
1249.5781 | 122.699 | -104.0817 | 18.1595 | -0.0051118 | -0.01202 | -0.077302 | -0.0056973 | -0.029162 | -0.049954 | -0.040819 | -0.0051575 | -0.022245 | 0.056414 | 0.040708 | -0.21702 | -0.013856 | -0.024107 | 0.07782 | 0.17853 | 0.022888 | 0.091553 | 0.25177 | 0.068665 | 0.14191 | -1.2131 | 18.1503 | -104.2328 | 18.2968 | -103.8345 | -104.0451 | -103.8391 | 104.1046 | -17.981 | -18.0679 | 104.3335 | 104.2236 | 104.1504 | 0.11902 | 0.045777 | -0.15106 | -0.009155 | 0.13733 | 0.24719 | 0.24262 | 0.036621 | 0.39368 | 0.18768 | 0.22888 | 0.068665 | 0.39825 | 122.5296 | 0.15564 | 122.3831 | 104.2603 | 122.2321 | -18.1366 | -122.3923 | 104.1733 | 122.3785 | 104.1595 | 102.8687
1251.3125 | 122.5937 | -105.4138 | 16.9418 | 0.010147 | -0.01437 | -0.079651 | -0.0033475 | -0.031725 | -0.052517 | -0.042742 | -0.0021057 | -0.020322 | 0.057054 | 0.054166 | -0.21552 | -0.015351 | -0.021971 | 0.004578 | 0.26093 | -0.018311 | -0.027466 | 0.1236 | 0.004578 | 0.054932 | -1.2039 | 16.9739 | -105.5099 | 16.9327 | -105.1758 | -105.3818 | -105.1529 | 105.3955 | -16.6809 | -16.9693 | 105.5374 | 105.4688 | 105.4184 | 0.073243 | 0.022889 | -0.096131 | 0.032044 | -0.009155 | 0.23804 | 0.26093 | 0.032043 | 0.35706 | 0.12817 | 0.14191 | -0.009155 | 0.33417 | 122.4426 | 0.27924 | 122.4838 | 105.6747 | 122.3877 | -16.9601 | -122.4518 | 105.3864 | 122.3465 | 105.4184 | 104.2099
1253.0938 | 122.6715 | -106.3568 | 15.9622 | 0.010147 | -0.016934 | -0.080292 | -0.0063381 | -0.030657 | -0.050808 | -0.040605 | 0.0039979 | -0.023099 | 0.056627 | 0.043699 | -0.21659 | -0.014924 | -0.016844 | 0.004578 | 0.19684 | -0.004578 | 0.027466 | 0.19684 | 0.068665 | 0.12817 | -1.1719 | 15.9439 | -106.4484 | 16.0721 | -106.0318 | -106.2195 | -106.0181 | 106.3522 | -15.7654 | -15.9348 | 106.5537 | 106.485 | 106.4255 | 0.13275 | 0.073243 | -0.091552 | -0.01831 | 0.10986 | 0.32501 | 0.33875 | 0.13733 | 0.4303 | 0.22888 | 0.20142 | 0.032044 | 0.41656 | 122.5204 | 0.20142 | 122.3923 | 106.5537 | 122.3007 | -15.9668 | -122.4106 | 106.3843 | 122.4289 | 106.3614 | 105.1849
1254.8125 | 122.6624 | -106.7139 | 15.6052 | -0.0051118 | -0.0090299 | -0.07837 | -0.0044155 | -0.028307 | -0.051449 | -0.041246 | -0.0021057 | -0.019895 | 0.056414 | 0.04733 | -0.21808 | -0.015137 | -0.024535 | 0.073242 | 0.18768 | 0.013733 | 0.09613 | 0.22888 | 0.054932 | 0.13275 | -1.1261 | 15.596 | -106.7734 | 15.77 | -106.3705 | -106.5765 | -106.3385 | 106.7276 | -15.4175 | -15.509 | 106.9427 | 106.8466 | 106.7688 | 0.11902 | 0.041199 | -0.059509 | -0.009156 | 0.16479 | 0.34332 | 0.37537 | 0.13733 | 0.43488 | 0.19684 | 0.21515 | 0.082397 | 0.40283 | 122.5433 | 0.17395 | 122.3694 | 106.9016 | 122.3099 | -15.5914 | -122.3785 | 106.81 | 122.4838 | 106.7871 | 105.5878
1256.5938 | 122.5433 | -106.9153 | 15.5045 | -0.012741 | -0.015438 | -0.080292 | -0.0022793 | -0.035784 | -0.050595 | -0.041033 | 0.00094606 | -0.01904 | 0.055986 | 0.050321 | -0.21723 | -0.015137 | -0.024962 | -0.013733 | 0.2655 | -0.009155 | -0.036621 | 0.10071 | -0.004578 | 0.068665 | -1.2177 | 15.4907 | -106.9794 | 15.4724 | -106.6406 | -106.8512 | -106.6315 | 106.9061 | -15.239 | -15.5411 | 107.016 | 106.9839 | 106.9107 | 0.07782 | 0.004577 | -0.064087 | -0.013733 | -0.032044 | 0.27466 | 0.28381 | 0.064087 | 0.3479 | 0.12817 | 0.10986 | -0.027466 | 0.33875 | 122.4518 | 0.27466 | 122.4701 | 107.1808 | 122.406 | -15.5136 | -122.4838 | 106.8787 | 122.3877 | 106.9016 | 105.6976
1258.375 | 122.5662 | -107.4371 | 14.9826 | -0.012741 | -0.010739 | -0.077942 | -0.0029201 | -0.030657 | -0.050167 | -0.037828 | -0.0021057 | -0.01904 | 0.056841 | 0.049467 | -0.21787 | -0.016419 | -0.022826 | 0.064087 | 0.2655 | 0.027466 | 0.045776 | 0.17853 | 0.050354 | 0.10529 | -1.1398 | 14.9689 | -107.4738 | 15.0055 | -107.0984 | -107.3318 | -107.0984 | 107.4646 | -14.7171 | -14.9368 | 107.6157 | 107.5424 | 107.4875 | 0.07782 | 0.022888 | -0.036621 | -0.013733 | 0.022888 | 0.33875 | 0.33875 | 0.10529 | 0.37537 | 0.14191 | 0.15106 | 0.01831 | 0.37537 | 122.4792 | 0.23804 | 122.4426 | 107.7026 | 122.406 | -14.9551 | -122.4564 | 107.4829 | 122.4426 | 107.5012 | 106.2973
1260.1562 | 122.58 | -107.46 | 14.9323 | -0.0051118 | -0.012234 | -0.080079 | -0.0084743 | -0.030657 | -0.049526 | -0.040819 | 0.00094606 | -0.022458 | 0.056627 | 0.044126 | -0.21659 | -0.016205 | -0.020903 | 0.059509 | 0.24261 | 0.045776 | 0.068665 | 0.21515 | 0.068665 | 0.15106 | -1.2131 | 14.9185 | -107.5333 | 14.978 | -107.1442 | -107.3318 | -107.1075 | 107.5058 | -14.6896 | -14.8636 | 107.6752 | 107.6111 | 107.5287 | 0.10529 | 0.022889 | -0.073242 | -0.013733 | 0.045776 | 0.31586 | 0.35248 | 0.12817 | 0.42572 | 0.20142 | 0.16937 | 0.022889 | 0.3891 | 122.5113 | 0.19684 | 122.4518 | 107.7026 | 122.3785 | -14.8865 | -122.4655 | 107.5287 | 122.438 | 107.5195 | 106.2469
1261.875 | 122.6303 | -107.9224 | 14.4516 | -0.012741 | -0.010098 | -0.078797 | -0.0035611 | -0.03322 | -0.049099 | -0.041887 | -0.0021057 | -0.020108 | 0.055986 | 0.043058 | -0.21894 | -0.015778 | -0.023467 | 0.059509 | 0.25177 | 0.009155 | 0.068665 | 0.19226 | 0.045776 | 0.13733 | -1.1673 | 14.4424 | -107.9636 | 14.5523 | -107.5562 | -107.7896 | -107.5424 | 107.9315 | -14.1998 | -14.3829 | 108.1146 | 108.0597 | 107.9681 | 0.12817 | 0.036621 | -0.041199 | -0.009155 | 0.10071 | 0.36621 | 0.37994 | 0.13275 | 0.42114 | 0.17395 | 0.18311 | 0.05951 | 0.40741 | 122.5159 | 0.24261 | 122.406 | 108.1741 | 122.3648 | -14.4424 | -122.4152 | 107.991 | 122.4747 | 107.9819 | 106.7551
1263.6562 | 122.5067 | -108.1924 | 14.2548 | -0.0051118 | -0.014157 | -0.079224 | -0.0016385 | -0.027025 | -0.050595 | -0.039751 | -0.0021057 | -0.018613 | 0.055132 | 0.055234 | -0.21958 | -0.015565 | -0.024748 | 0.041199 | 0.25635 | 0.009155 | 0 | 0.11902 | -0.027466 | 0.041199 | -1.2909 | 14.241 | -108.2199 | 14.1815 | -107.9361 | -108.1787 | -107.9041 | 108.2016 | -13.9984 | -14.2548 | 108.3115 | 108.2336 | 108.165 | 0.032044 | -0.036621 | -0.027466 | -0.013733 | -0.073242 | 0.25635 | 0.28839 | 0.013733 | 0.31586 | 0.041199 | 0.10986 | -0.009155 | 0.28381 | 122.4014 | 0.24719 | 122.4609 | 108.4488 | 122.4335 | -14.2456 | -122.4747 | 108.1924 | 122.374 | 108.2336 | 106.9016
1265.4375 | 122.6486 | -108.5907 | 13.765 | -0.0051118 | -0.013943 | -0.078583 | -0.0063381 | -0.034075 | -0.050595 | -0.041033 | 0.00094606 | -0.021176 | 0.056627 | 0.047544 | -0.21808 | -0.015565 | -0.026244 | 0.091553 | 0.25177 | 0.064087 | 0.1236 | 0.29297 | 0.15106 | 0.21515 | -1.1307 | 13.7283 | -108.6685 | 13.8519 | -108.2062 | -108.4396 | -108.2291 | 108.6548 | -13.5132 | -13.6414 | 108.8837 | 108.8058 | 108.7418 | 0.15106 | 0.086975 | -0.07782 | -0.036621 | 0.086975 | 0.38452 | 0.36163 | 0.15106 | 0.43945 | 0.22888 | 0.22888 | 0.059509 | 0.46234 | 122.5204 | 0.18768 | 122.3969 | 108.8425 | 122.319 | -13.7009 | -122.4335 | 108.7143 | 122.4426 | 108.6823 | 107.46
1267.1562 | 122.644 | -108.5037 | 13.8519 | 0.0025177 | -0.012875 | -0.079865 | -0.0076199 | -0.034289 | -0.049099 | -0.040605 | -0.0051575 | -0.022458 | 0.054491 | 0.041135 | -0.22129 | -0.016205 | -0.023039 | 0.11902 | 0.24719 | 0.068665 | 0.16022 | 0.32501 | 0.16937 | 0.22888 | -1.1215 | 13.8336 | -108.5587 | 13.9664 | -108.1009 | -108.3206 | -108.1238 | 108.5724 | -13.6047 | -13.6917 | 108.8287 | 108.7326 | 108.6731 | 0.16022 | 0.10071 | -0.054932 | -0.018311 | 0.11444 | 0.40283 | 0.37994 | 0.1831 | 0.43488 | 0.23804 | 0.25635 | 0.091552 | 0.45776 | 122.525 | 0.17853 | 122.3923 | 108.7509 | 122.3373 | -13.7833 | -122.4106 | 108.6639 | 122.4701 | 108.6227 | 107.3822
1268.9375 | 122.6715 | -108.9661 | 13.4033 | 0.010147 | -0.013302 | -0.080079 | -0.0046291 | -0.030871 | -0.051449 | -0.042101 | 0.00094606 | -0.022458 | 0.0562 | 0.050321 | -0.21958 | -0.016205 | -0.026244 | 0.11902 | 0.24719 | 0.059509 | 0.15106 | 0.32501 | 0.17853 | 0.23346 | -1.1032 | 13.3759 | -109.0302 | 13.4995 | -108.5449 | -108.7692 | -108.5632 | 109.0256 | -13.1561 | -13.2523 | 109.2911 | 109.1995 | 109.1446 | 0.17395 | 0.11902 | -0.064087 | -0.027466 | 0.096131 | 0.42114 | 0.40283 | 0.19684 | 0.46692 | 0.26093 | 0.2655 | 0.091553 | 0.48523 | 122.5296 | 0.18768 | 122.406 | 109.2133 | 122.3419 | -13.3438 | -122.4335 | 109.1171 | 122.4655 | 109.0851 | 107.8629
1270.75 | 122.5342 | -108.8882 | 13.4949 | -0.0051118 | -0.010098 | -0.081574 | -0.0018521 | -0.029802 | -0.049954 | -0.041887 | -0.0021057 | -0.019254 | 0.057268 | 0.042844 | -0.21979 | -0.015565 | -0.022398 | 0.068665 | 0.30212 | 0.045776 | 0.018311 | 0.15106 | 0.004578 | 0.068665 | -1.268 | 13.504 | -108.9615 | 13.4903 | -108.6136 | -108.8654 | -108.5953 | 108.934 | -13.1927 | -13.4766 | 109.0393 | 108.9569 | 108.8928 | 0.022889 | -0.041198 | -0.073242 | 0.009155 | -0.004578 | 0.27466 | 0.29297 | 0.022889 | 0.36621 | 0.096131 | 0.10529 | -0.027465 | 0.3479 | 122.4518 | 0.25635 | 122.4655 | 109.1904 | 122.3923 | -13.4491 | -122.4564 | 108.9066 | 122.3785 | 108.9569 | 107.6202
1272.4688 | 122.5296 | -109.1537 | 13.3026 | 0.0025177 | -0.015438 | -0.080506 | -0.0050565 | -0.032152 | -0.052304 | -0.039965 | 0.0039979 | -0.020536 | 0.058763 | 0.047544 | -0.21851 | -0.013428 | -0.022398 | 0.041199 | 0.29755 | 0.027466 | 0.004578 | 0.14191 | 0.036621 | 0.09613 | -1.2726 | 13.3072 | -109.1812 | 13.2385 | -108.8196 | -109.0622 | -108.8242 | 109.1812 | -13.0051 | -13.298 | 109.2957 | 109.2499 | 109.1904 | 0.068664 | 0.009155 | -0.027465 | 0.004578 | -0.064087 | 0.33417 | 0.32959 | 0.091553 | 0.35706 | 0.11902 | 0.11444 | -0.022888 | 0.36163 | 122.4197 | 0.27008 | 122.4884 | 109.4513 | 122.4609 | -13.2751 | -122.4838 | 109.1583 | 122.3923 | 109.1949 | 107.8812
1274.2969 | 122.5571 | -109.2957 | 13.1149 | -0.0051118 | -0.013516 | -0.077942 | -0.0033475 | -0.028521 | -0.050381 | -0.040178 | 0.00094606 | -0.019895 | 0.057268 | 0.050535 | -0.2183 | -0.014924 | -0.02368 | 0.10986 | 0.28839 | 0.054932 | 0.086975 | 0.22888 | 0.082397 | 0.14648 | -1.2039 | 13.0966 | -109.3643 | 13.1241 | -108.9752 | -109.2041 | -108.9844 | 109.3506 | -12.8265 | -13.028 | 109.5245 | 109.4421 | 109.3781 | 0.091552 | 0.027465 | -0.068665 | -0.01831 | 0.009155 | 0.32043 | 0.31128 | 0.091552 | 0.37994 | 0.16022 | 0.17395 | 0.032043 | 0.3891 | 122.4884 | 0.23346 | 122.4609 | 109.584 | 122.3923 | -13.06 | -122.4792 | 109.3826 | 122.4197 | 109.4055 | 108.0917
1276.0625 | 122.644 | -109.2682 | 13.0783 | 0.0025177 | -0.014798 | -0.078797 | -0.0074063 | -0.027453 | -0.049099 | -0.040605 | -0.0021057 | -0.023099 | 0.056841 | 0.035581 | -0.21808 | -0.01706 | -0.023039 | 0.12817 | 0.24261 | 0.07782 | 0.15106 | 0.32044 | 0.16479 | 0.21057 | -1.1536 | 13.0508 | -109.314 | 13.1836 | -108.8562 | -109.0851 | -108.902 | 109.346 | -12.8357 | -12.9272 | 109.5886 | 109.4788 | 109.433 | 0.13275 | 0.086975 | -0.045777 | -0.027466 | 0.10529 | 0.41199 | 0.36621 | 0.1831 | 0.41199 | 0.22888 | 0.24262 | 0.073242 | 0.45776 | 122.4976 | 0.16479 | 122.3648 | 109.5108 | 122.319 | -13.0005 | -122.3923 | 109.4192 | 122.4518 | 109.3964 | 108.1146
1277.7656 | 122.5845 | -109.2819 | 13.092 | -0.0051118 | -0.011807 | -0.080506 | -0.0048427 | -0.029162 | -0.050595 | -0.038256 | 0.00094606 | -0.020749 | 0.056414 | 0.049039 | -0.21659 | -0.013215 | -0.021971 | 0.14648 | 0.29297 | 0.10529 | 0.14191 | 0.31128 | 0.12817 | 0.19226 | -1.2314 | 13.0646 | -109.3369 | 13.1653 | -108.9249 | -109.1446 | -108.9157 | 109.3872 | -12.7991 | -12.9501 | 109.5932 | 109.4742 | 109.4101 | 0.086975 | 0.022888 | -0.054932 | -0.027466 | 0.073242 | 0.35706 | 0.36621 | 0.13733 | 0.42114 | 0.19226 | 0.20599 | 0.036621 | 0.41199 | 122.5021 | 0.18768 | 122.4014 | 109.5749 | 122.3465 | -12.9868 | -122.4289 | 109.4238 | 122.4472 | 109.4284 | 108.0505
1279.4688 | 122.5021 | -109.4879 | 12.9364 | -0.0051118 | -0.014157 | -0.082856 | -0.0046291 | -0.032152 | -0.050595 | -0.03911 | 0.0039979 | -0.018827 | 0.055986 | 0.044126 | -0.21552 | -0.015778 | -0.027739 | 0.004578 | 0.25635 | -0.013733 | -0.022888 | 0.11444 | -0.013733 | 0.068665 | -1.3229 | 12.9364 | -109.5566 | 12.8723 | -109.1995 | -109.433 | -109.1904 | 109.4742 | -12.6801 | -12.9593 | 109.6024 | 109.5566 | 109.4742 | 0.082398 | 0 | -0.068665 | 0 | -0.064087 | 0.28839 | 0.29755 | 0.054932 | 0.36621 | 0.1236 | 0.12817 | -0.009155 | 0.35706 | 122.4289 | 0.27008 | 122.493 | 109.7443 | 122.4243 | -12.9501 | -122.493 | 109.465 | 122.3602 | 109.4925 | 108.165
1281.1719 | 122.58 | -109.5749 | 12.8082 | 0.0025177 | -0.015438 | -0.08136 | -0.0027065 | -0.028093 | -0.050808 | -0.038042 | -0.0082091 | -0.019895 | 0.056414 | 0.042631 | -0.2183 | -0.015137 | -0.023894 | 0.068665 | 0.20599 | 0 | 0.082397 | 0.23804 | 0.082397 | 0.14191 | -1.2451 | 12.7853 | -109.6344 | 12.8357 | -109.2224 | -109.433 | -109.2224 | 109.5749 | -12.6022 | -12.7258 | 109.8129 | 109.7168 | 109.6573 | 0.14191 | 0.082397 | -0.059509 | -0.022889 | 0.027465 | 0.35248 | 0.35248 | 0.14191 | 0.41199 | 0.20142 | 0.23804 | 0.082397 | 0.41199 | 122.4701 | 0.20599 | 122.4197 | 109.7809 | 122.3602 | -12.8082 | -122.4426 | 109.6573 | 122.4106 | 109.6436 | 108.3298
1282.8906 | 122.6212 | -109.227 | 13.1104 | -0.0051118 | -0.01138 | -0.077942 | -0.0046291 | -0.029375 | -0.047177 | -0.040178 | 0.00094606 | -0.023313 | 0.055986 | 0.047971 | -0.21915 | -0.015778 | -0.021117 | 0.009155 | 0.19684 | -0.022888 | 0.036621 | 0.17395 | 0.018311 | 0.086975 | -1.2817 | 13.1149 | -109.2911 | 13.2156 | -108.8837 | -109.1171 | -108.8333 | 109.2041 | -12.9135 | -13.0737 | 109.4009 | 109.314 | 109.2453 | 0.10986 | 0.041199 | -0.064087 | 0.004577 | 0.10528 | 0.34332 | 0.39368 | 0.10986 | 0.45776 | 0.17395 | 0.19684 | 0.059509 | 0.40741 | 122.5067 | 0.21973 | 122.406 | 109.4238 | 122.3419 | -13.1332 | -122.4014 | 109.2636 | 122.4426 | 109.2361 | 107.9453
1284.6406 | 122.5342 | -109.4925 | 12.8998 | 0.0025177 | -0.01202 | -0.077942 | -0.0046291 | -0.027025 | -0.048031 | -0.038896 | -0.0021057 | -0.019467 | 0.055345 | 0.048826 | -0.21787 | -0.012574 | -0.020476 | 0.009155 | 0.19684 | -0.036621 | -0.013733 | 0.13275 | -0.027466 | 0.036621 | -1.2909 | 12.8815 | -109.5566 | 12.886 | -109.2133 | -109.4421 | -109.1766 | 109.4559 | -12.7029 | -12.9135 | 109.6252 | 109.5291 | 109.465 | 0.073242 | 0.009155 | -0.064087 | -0.01831 | -0.013733 | 0.27924 | 0.31586 | 0.050354 | 0.37994 | 0.11444 | 0.16937 | 0.022888 | 0.34332 | 122.4426 | 0.23346 | 122.4381 | 109.6893 | 122.374 | -12.9364 | -122.4564 | 109.4788 | 122.3785 | 109.5016 | 108.2016
1286.4062 | 122.5021 | -109.7992 | 12.6389 | 0.0025177 | -0.014157 | -0.079224 | -0.0063381 | -0.032793 | -0.050381 | -0.041246 | 0.00094606 | -0.020322 | 0.058123 | 0.045408 | -0.21723 | -0.015778 | -0.020262 | -0.022888 | 0.20599 | -0.064087 | -0.068665 | 0.09613 | -0.041199 | 0.022888 | -1.3824 | 12.6251 | -109.8267 | 12.5656 | -109.4788 | -109.726 | -109.5108 | 109.7351 | -12.4329 | -12.7075 | 109.8953 | 109.8221 | 109.758 | 0.086975 | 0.022888 | -0.027466 | -0.013733 | -0.073242 | 0.32043 | 0.28839 | 0.073242 | 0.31586 | 0.10071 | 0.16022 | -0.004578 | 0.3479 | 122.3923 | 0.27008 | 122.4518 | 110.0052 | 122.4243 | -12.7029 | -122.4655 | 109.7305 | 122.3648 | 109.7763 | 108.4167
1288.1562 | 122.6486 | -109.6664 | 12.6709 | -0.0051118 | -0.016507 | -0.080933 | -0.0052701 | -0.032793 | -0.051022 | -0.040819 | -0.0021057 | -0.022458 | 0.0562 | 0.045621 | -0.2183 | -0.016846 | -0.020476 | -0.004578 | 0.15564 | -0.036621 | 0.036621 | 0.21515 | 0.064087 | 0.11444 | -1.2772 | 12.6526 | -109.7397 | 12.7808 | -109.2773 | -109.4925 | -109.2957 | 109.6298 | -12.5153 | -12.6343 | 109.8816 | 109.7809 | 109.7305 | 0.15106 | 0.10071 | -0.073242 | -0.01831 | 0.10986 | 0.3891 | 0.37079 | 0.17395 | 0.44403 | 0.24719 | 0.25177 | 0.073242 | 0.46234 | 122.5204 | 0.19226 | 122.3923 | 109.8221 | 122.319 | -12.7075 | -122.4106 | 109.7031 | 122.4472 | 109.6619 | 108.3893
1289.875 | 122.6532 | -109.9319 | 12.4237 | -0.0051118 | -0.013729 | -0.080933 | -0.0067653 | -0.032793 | -0.050808 | -0.038896 | -0.0021057 | -0.020322 | 0.055986 | 0.042417 | -0.21616 | -0.01706 | -0.023894 | 0.004578 | 0.15564 | -0.036621 | 0.036621 | 0.21973 | 0.068665 | 0.12817 | -1.2817 | 12.3871 | -110.0143 | 12.5061 | -109.5428 | -109.7672 | -109.5428 | 109.8953 | -12.2681 | -12.3871 | 110.1517 | 110.0601 | 110.0006 | 0.1648 | 0.10529 | -0.082397 | -0.036621 | 0.082398 | 0.3891 | 0.3891 | 0.16479 | 0.4715 | 0.24719 | 0.25635 | 0.073242 | 0.4715 | 122.5204 | 0.19226 | 122.4014 | 110.0876 | 122.319 | -12.4603 | -122.438 | 109.9686 | 122.4381 | 109.9365 | 108.6502
1291.5938 | 122.5067 | -110.2386 | 12.2086 | 0.0025177 | -0.016934 | -0.081147 | -0.0065517 | -0.030657 | -0.051449 | -0.042528 | 0.00094606 | -0.022245 | 0.055773 | 0.041563 | -0.2168 | -0.015992 | -0.021971 | -0.059509 | 0.20142 | -0.059509 | -0.07782 | 0.07782 | -0.054932 | 0.022888 | -1.4236 | 12.1811 | -110.2844 | 12.1078 | -109.9319 | -110.1654 | -109.9228 | 110.1791 | -12.0071 | -12.2864 | 110.3165 | 110.2615 | 110.1837 | 0.082397 | 0.004577 | -0.045777 | -0.027466 | -0.10071 | 0.3067 | 0.31586 | 0.073242 | 0.36163 | 0.11902 | 0.13733 | -0.018311 | 0.35248 | 122.3923 | 0.26093 | 122.4655 | 110.4401 | 122.4197 | -12.2681 | -122.493 | 110.1608 | 122.3465 | 110.1791 | 108.815
1293.2969 | 122.6212 | -109.7351 | 12.6297 | -0.0051118 | -0.014798 | -0.077729 | -0.0048427 | -0.033007 | -0.051876 | -0.041674 | -0.0021057 | -0.020749 | 0.056627 | 0.045194 | -0.21915 | -0.016633 | -0.024748 | 0 | 0.16479 | -0.045776 | 0.013733 | 0.16479 | 0.032043 | 0.10529 | -1.3824 | 12.6251 | -109.8038 | 12.6984 | -109.346 | -109.552 | -109.3414 | 109.6893 | -12.4649 | -12.616 | 109.8999 | 109.8404 | 109.7672 | 0.15106 | 0.077819 | -0.068665 | -0.004578 | 0.068664 | 0.3891 | 0.39368 | 0.1831 | 0.46234 | 0.25177 | 0.21057 | 0.059509 | 0.45776 | 122.5021 | 0.21057 | 122.4289 | 109.8999 | 122.3602 | -12.6755 | -122.4335 | 109.7488 | 122.4335 | 109.7351 | 108.3527
1295 | 122.6761 | -108.728 | 13.5086 | -0.012741 | -0.010739 | -0.078583 | -0.0033475 | -0.031939 | -0.051022 | -0.039965 | -0.0021057 | -0.02139 | 0.056414 | 0.050321 | -0.22172 | -0.013642 | -0.020262 | 0.045776 | 0.16022 | -0.013733 | 0.041199 | 0.18768 | 0.009155 | 0.091553 | -1.3321 | 13.5132 | -108.8745 | 13.6597 | -108.4625 | -108.6868 | -108.4167 | 108.7143 | -13.3484 | -13.4674 | 108.9157 | 108.8196 | 108.7372 | 0.10529 | 0.022888 | -0.14648 | 0.004578 | 0.15106 | 0.2655 | 0.31128 | 0.041198 | 0.45776 | 0.18768 | 0.20142 | 0.054932 | 0.41199 | 122.5342 | 0.17395 | 122.3877 | 108.8882 | 122.2412 | -13.5223 | -122.3831 | 108.7692 | 122.3877 | 108.7738 | 107.3959
1296.7188 | 122.5891 | -109.021 | 13.3255 | -0.02037 | -0.01138 | -0.080506 | -0.0031337 | -0.030443 | -0.051235 | -0.039751 | 0.0039979 | -0.019254 | 0.056414 | 0.043272 | -0.22129 | -0.014924 | -0.022826 | -0.041199 | 0.19226 | -0.068665 | -0.045776 | 0.059509 | -0.059509 | 0.009155 | -1.4191 | 13.3347 | -109.1446 | 13.3392 | -108.7692 | -108.989 | -108.7372 | 108.9523 | -13.1332 | -13.3713 | 109.0805 | 109.0302 | 108.9615 | 0.07782 | 0.009156 | -0.1236 | 0.009156 | 0.013733 | 0.25177 | 0.28381 | 0.032043 | 0.40741 | 0.15564 | 0.12817 | 0.022889 | 0.37537 | 122.4838 | 0.26093 | 122.4792 | 109.2133 | 122.3557 | -13.3942 | -122.4701 | 108.9752 | 122.3602 | 108.9798 | 107.6019
1298.4375 | 122.6212 | -109.1812 | 13.1699 | -0.012741 | -0.012234 | -0.080506 | -0.0067653 | -0.034289 | -0.050381 | -0.040178 | 0.00094606 | -0.021604 | 0.055773 | 0.046262 | -0.21808 | -0.017701 | -0.021544 | -0.036621 | 0.16937 | -0.041199 | -0.022888 | 0.11902 | -0.036621 | 0.050354 | -1.4969 | 13.1744 | -109.2636 | 13.2248 | -108.8654 | -109.0713 | -108.8562 | 109.14 | -13.0005 | -13.1927 | 109.3002 | 109.2316 | 109.1446 | 0.091553 | 0.004578 | -0.082398 | 0.004577 | 0.054931 | 0.31586 | 0.32501 | 0.10986 | 0.40741 | 0.19226 | 0.16022 | 0.018311 | 0.39825 | 122.4884 | 0.21057 | 122.438 | 109.3506 | 122.3557 | -13.2111 | -122.4335 | 109.1583 | 122.406 | 109.1446 | 107.6843
1300.1406 | 122.58 | -109.3643 | 13.028 | -0.0051118 | -0.01138 | -0.080079 | -0.0027065 | -0.028734 | -0.051876 | -0.040605 | 0.0039979 | -0.019681 | 0.057909 | 0.046049 | -0.21958 | -0.015778 | -0.024962 | 0 | 0.17395 | -0.054932 | -0.013733 | 0.12817 | -0.032043 | 0.036621 | -1.3962 | 13.0234 | -109.4055 | 13.0783 | -109.0256 | -109.2773 | -109.0073 | 109.3094 | -12.854 | -13.0417 | 109.4925 | 109.4009 | 109.3323 | 0.091553 | 0.022889 | -0.041199 | -0.004578 | 0.050354 | 0.33874 | 0.35706 | 0.086975 | 0.39826 | 0.12817 | 0.18311 | 0.041199 | 0.37994 | 122.4838 | 0.22888 | 122.4289 | 109.5383 | 122.3877 | -13.0829 | -122.4335 | 109.3506 | 122.4426 | 109.3643 | 107.9681
1301.8438 | 122.6624 | -109.2865 | 13.0142 | -0.0051118 | -0.011166 | -0.077729 | -0.0039883 | -0.028521 | -0.049526 | -0.044451 | -0.0051575 | -0.021817 | 0.056627 | 0.048612 | -0.2168 | -0.015351 | -0.02368 | -0.022888 | 0.16022 | -0.054932 | -0.013733 | 0.12817 | -0.032043 | 0.041199 | -1.4648 | 13.0188 | -109.4101 | 13.1332 | -108.989 | -109.2041 | -108.9386 | 109.2316 | -12.854 | -13.028 | 109.4147 | 109.3277 | 109.2545 | 0.096131 | 0.022889 | -0.1236 | 0.004578 | 0.11902 | 0.29755 | 0.3479 | 0.082397 | 0.4715 | 0.20599 | 0.18311 | 0.041199 | 0.42114 | 122.5433 | 0.21515 | 122.4289 | 109.4467 | 122.3053 | -13.0692 | -122.4243 | 109.2728 | 122.4197 | 109.2636 | 107.8217
1303.5469 | 122.5891 | -109.053 | 13.3347 | -0.0051118 | -0.015438 | -0.078156 | -0.0063381 | -0.033648 | -0.049954 | -0.04146 | -0.0021057 | -0.02139 | 0.057054 | 0.051389 | -0.21915 | -0.018342 | -0.02603 | 0.059509 | 0.1831 | 0.004578 | 0.050354 | 0.21973 | 0.073242 | 0.11902 | -1.4511 | 13.2889 | -109.1309 | 13.3621 | -108.7372 | -108.9569 | -108.728 | 109.0576 | -13.1516 | -13.2843 | 109.2728 | 109.1721 | 109.1263 | 0.11444 | 0.068664 | -0.077819 | -0.045777 | 0.027466 | 0.31586 | 0.32501 | 0.096131 | 0.40283 | 0.17395 | 0.21515 | 0.045776 | 0.39368 | 122.493 | 0.17853 | 122.4197 | 109.2361 | 122.3419 | -13.3301 | -122.4655 | 109.1034 | 122.4152 | 109.1125 | 107.6019
1305.2812 | 122.2458 | -78.7582 | 43.7302 | -0.0051118 | -0.01437 | -0.080292 | -0.0018521 | -0.029375 | -0.048245 | -0.041887 | 0.0039979 | -0.018613 | 0.056414 | 0.044767 | -0.21915 | -0.015137 | -0.023253 | 0.45319 | 0.62714 | 0.39825 | 0.4715 | 0.58136 | 0.43488 | 0.48523 | -0.71869 | 43.6523 | -78.6758 | 43.7897 | -78.4973 | -78.6575 | -78.4653 | 79.1565 | -43.103 | -43.2587 | 79.3396 | 79.2435 | 79.1931 | 0.086975 | 0.036621 | 0.082398 | -0.07782 | 0.059509 | 0.26093 | 0.29297 | 0.10071 | 0.21057 | 0.01831 | 0.18311 | 0.073243 | 0.17853 | 122.4655 | 0.22888 | 122.3282 | 79.3854 | 122.4106 | -43.3319 | -122.406 | 79.2297 | 122.5479 | 79.2114 | 78.0396
1307.0312 | 122.4335 | -86.8332 | 35.5453 | 0.0025177 | -0.012875 | -0.079224 | -0.0042019 | -0.029802 | -0.049954 | -0.037615 | -0.0021057 | -0.019254 | 0.055773 | 0.045621 | -0.21787 | -0.013428 | -0.020476 | 0.48523 | 0.68207 | 0.43945 | 0.48065 | 0.62256 | 0.45776 | 0.5127 | -1.0574 | 35.5225 | -86.8607 | 35.5087 | -86.6638 | -86.8149 | -86.6043 | 87.2726 | -34.8633 | -35.0647 | 87.4557 | 87.3459 | 87.291 | 0.073242 | 0.018311 | -0.027466 | -0.022888 | -0.036621 | 0.16937 | 0.22888 | 0.018311 | 0.25635 | 0.045777 | 0.18311 | 0.041199 | 0.19684 | 122.3694 | 0.24262 | 122.3831 | 87.5153 | 122.3557 | -35.1059 | -122.406 | 87.3138 | 122.3419 | 87.3184 | 85.7758
1308.7188 | 122.5479 | -81.2805 | 40.9927 | -0.0051118 | -0.015866 | -0.079651 | -0.0071927 | -0.02553 | -0.049954 | -0.039751 | -0.0051575 | -0.02139 | 0.056841 | 0.042631 | -0.21723 | -0.015351 | -0.019408 | 0.48065 | 0.65002 | 0.46692 | 0.50812 | 0.67291 | 0.53101 | 0.58594 | -0.99335 | 40.9744 | -81.3217 | 41.1301 | -81.0287 | -81.1615 | -81.0059 | 81.7474 | -40.3427 | -40.4846 | 81.9534 | 81.8665 | 81.8115 | 0.11902 | 0.064087 | -0.041198 | -0.018311 | 0.13733 | 0.25177 | 0.27466 | 0.11902 | 0.31586 | 0.16022 | 0.20599 | 0.041199 | 0.29297 | 122.4518 | 0.18311 | 122.2961 | 81.9305 | 122.2549 | -40.5258 | -122.3145 | 81.7886 | 122.4106 | 81.7612 | 80.2872
1310.4219 | 122.5204 | -91.7221 | 30.5191 | -0.0051118 | -0.015011 | -0.080719 | -0.0052701 | -0.034075 | -0.048886 | -0.043383 | 0.00094606 | -0.020749 | 0.055986 | 0.045621 | -0.21766 | -0.017914 | -0.024962 | 0.45319 | 0.65918 | 0.4303 | 0.45319 | 0.61798 | 0.47607 | 0.53101 | -1.2955 | 30.4688 | -91.7999 | 30.6152 | -91.4886 | -91.6626 | -91.4932 | 92.1524 | -29.8599 | -30.0659 | 92.3401 | 92.2531 | 92.1982 | 0.10071 | 0.045776 | -0.07782 | -0.050354 | 0.09613 | 0.23346 | 0.22888 | 0.059509 | 0.3067 | 0.13733 | 0.18768 | 0.022888 | 0.31128 | 122.4152 | 0.22888 | 122.2687 | 92.3813 | 122.1909 | -30.0888 | -122.319 | 92.1753 | 122.3373 | 92.1753 | 90.4266
1312.1406 | 122.5296 | -93.3884 | 28.775 | 0.010147 | -0.012661 | -0.07837 | -0.0061245 | -0.030443 | -0.048458 | -0.039537 | -0.0051575 | -0.019681 | 0.057054 | 0.043058 | -0.21872 | -0.015137 | -0.022398 | 0.63629 | 0.73242 | 0.59509 | 0.6546 | 0.80566 | 0.6134 | 0.70038 | -1.2497 | 28.775 | -93.512 | 28.9444 | -93.1549 | -93.3197 | -93.1274 | 93.9835 | -28.0426 | -28.1204 | 94.194 | 94.0887 | 94.0018 | 0.10528 | 0.01831 | -0.1236 | 0 | 0.16937 | 0.23346 | 0.26093 | 0.068665 | 0.38452 | 0.19226 | 0.21057 | 0.059509 | 0.35706 | 122.4564 | 0.13733 | 122.287 | 94.1208 | 122.1634 | -28.1799 | -122.287 | 94.043 | 122.3328 | 94.0247 | 92.1387
1313.9688 | 122.3877 | -81.4316 | 40.8875 | 0.0025177 | -0.013729 | -0.080719 | -0.0052701 | -0.029375 | -0.049313 | -0.041887 | -0.0082091 | -0.01904 | 0.055986 | 0.046689 | -0.2183 | -0.016419 | -0.023253 | 0.48981 | 0.74158 | 0.47607 | 0.48065 | 0.68665 | 0.59967 | 0.57678 | -1.0345 | 40.7776 | -81.546 | 40.86 | -81.2988 | -81.4041 | -81.1615 | 81.9077 | -40.1459 | -40.4068 | 82.1182 | 82.0084 | 82.0312 | 0.10071 | 0.1236 | -0.11444 | -0.10986 | -0.027466 | 0.13275 | 0.27008 | 0.027466 | 0.38452 | 0.14191 | 0.21057 | 0.004578 | 0.24719 | 122.406 | 0.2655 | 122.3236 | 82.1732 | 122.2092 | -40.4114 | -122.4335 | 81.9122 | 122.2916 | 81.9214 | 80.397
1315.7812 | 122.4564 | -87.7716 | 34.4376 | -0.0051118 | -0.013089 | -0.078583 | -0.0056973 | -0.030443 | -0.050381 | -0.040392 | -0.0051575 | -0.02139 | 0.055986 | 0.04498 | -0.21766 | -0.015992 | -0.022612 | 0.45776 | 0.62714 | 0.44861 | 0.48065 | 0.62256 | 0.47607 | 0.54474 | -1.1719 | 34.4055 | -87.8448 | 34.5337 | -87.5977 | -87.7167 | -87.5473 | 88.2202 | -33.8104 | -33.9569 | 88.3942 | 88.3163 | 88.2477 | 0.096131 | 0.027466 | -0.073243 | -0.032043 | 0.09613 | 0.17395 | 0.2243 | 0.054931 | 0.29755 | 0.12817 | 0.17395 | 0.032044 | 0.24719 | 122.3785 | 0.17853 | 122.2504 | 88.3987 | 122.1771 | -33.989 | -122.2824 | 88.2523 | 122.3053 | 88.2294 | 86.5997
1317.5625 | 122.4197 | -88.06 | 34.1949 | -0.0051118 | -0.012875 | -0.07837 | -0.0031337 | -0.031298 | -0.048031 | -0.041887 | 0.0039979 | -0.018186 | 0.057909 | 0.052457 | -0.21808 | -0.015778 | -0.022398 | 0.68207 | 0.85144 | 0.6134 | 0.65918 | 0.79193 | 0.64087 | 0.70953 | -1.0895 | 34.1721 | -88.092 | 34.2499 | -87.854 | -88.0371 | -87.8357 | 88.6734 | -33.3435 | -33.5358 | 88.8519 | 88.7695 | 88.7009 | 0.096131 | 0.027466 | -0.032043 | -0.022888 | 0.054932 | 0.20599 | 0.2243 | 0.022889 | 0.25635 | 0.054932 | 0.17853 | 0.045777 | 0.23804 | 122.3419 | 0.23804 | 122.2641 | 88.9114 | 122.2321 | -33.5815 | -122.287 | 88.7192 | 122.3099 | 88.7421 | 86.9705
1319.3594 | 122.5067 | -91.7358 | 30.3955 | 0.0025177 | -0.010098 | -0.079011 | -0.0048427 | -0.029375 | -0.04974 | -0.041674 | -0.0021057 | -0.020536 | 0.055559 | 0.052457 | -0.21808 | -0.014924 | -0.021544 | 1.1307 | 1.268 | 1.0803 | 1.149 | 1.2817 | 1.1353 | 1.1993 | -1.2039 | 30.3955 | -91.7999 | 30.6015 | -91.4841 | -91.6534 | -91.4383 | 92.8162 | -29.1275 | -29.2465 | 93.0176 | 92.9352 | 92.8711 | 0.11902 | 0.054932 | -0.064087 | 0 | 0.20599 | 0.25177 | 0.29755 | 0.082398 | 0.36163 | 0.14648 | 0.20142 | 0.068665 | 0.31586 | 122.4014 | 0.18768 | 122.1954 | 93.0038 | 122.1313 | -29.3152 | -122.1954 | 92.8848 | 122.3373 | 92.8665 | 90.5319
1321.1406 | 122.4014 | -94.7296 | 27.4979 | 0.0025177 | -0.010952 | -0.077729 | -0.0035611 | -0.03023 | -0.049313 | -0.039324 | -0.0021057 | -0.018186 | 0.059618 | 0.05203 | -0.21979 | -0.014924 | -0.020903 | 1.2085 | 1.387 | 1.149 | 1.2039 | 1.3275 | 1.1719 | 1.2451 | -1.3184 | 27.4658 | -94.8166 | 27.5482 | -94.5236 | -94.7159 | -94.4962 | 95.8786 | -26.1108 | -26.2939 | 96.0571 | 95.9747 | 95.9015 | 0.09613 | 0.022888 | -0.086975 | -0.032044 | 0.050354 | 0.20599 | 0.23346 | 0.013733 | 0.32043 | 0.10071 | 0.17853 | 0.054931 | 0.29297 | 122.3648 | 0.23804 | 122.2824 | 96.1166 | 122.1954 | -26.3489 | -122.3145 | 95.9335 | 122.2778 | 95.9381 | 93.4113
1322.9375 | 122.4152 | -100.4105 | 21.7987 | -0.0051118 | -0.011593 | -0.078797 | -0.0050565 | -0.029802 | -0.050595 | -0.036974 | -0.0021057 | -0.018827 | 0.058763 | 0.044767 | -0.21808 | -0.016633 | -0.026244 | 1.149 | 1.3458 | 1.0986 | 1.1398 | 1.2497 | 1.1307 | 1.181 | -1.4877 | 21.7667 | -100.4974 | 21.8765 | -100.1312 | -100.3372 | -100.1175 | 101.5091 | -20.4529 | -20.6589 | 101.6602 | 101.5915 | 101.5411 | 0.082397 | 0.032043 | -0.086976 | -0.032043 | 0.07782 | 0.27923 | 0.29297 | 0.073242 | 0.37994 | 0.16022 | 0.15106 | 0.041199 | 0.36621 | 122.374 | 0.24719 | 122.2641 | 101.7563 | 122.1771 | -20.7001 | -122.2961 | 101.5503 | 122.287 | 101.5594 | 98.9227
1324.7188 | 122.406 | -80.5801 | 41.748 | 0.010147 | -0.011166 | -0.079438 | -0.0042019 | -0.029589 | -0.048458 | -0.041674 | 0.00094606 | -0.020108 | 0.057482 | 0.047117 | -0.21851 | -0.015778 | -0.022398 | 1.03 | 1.1902 | 0.9613 | 1.0208 | 1.149 | 1.0025 | 1.0529 | -1.2222 | 40.947 | -81.2027 | 41.6107 | -80.5252 | -80.6122 | -80.2917 | 81.5414 | -40.5579 | -40.7272 | 81.7291 | 81.633 | 81.5826 | 0.091552 | 0.041198 | -0.62256 | -0.80109 | -0.13733 | 0.054931 | 0.28839 | -0.032044 | 0.91095 | 0.59051 | 0.18768 | 0.059509 | 0.67749 | 122.8134 | 0.22888 | 122.1497 | 81.7703 | 121.5271 | -40.7867 | -122.9507 | 81.601 | 122.1909 | 81.6101 | 79.3579
1326.5 | 122.3282 | -90.6876 | 31.8878 | 0.0025177 | -0.0096707 | -0.078797 | -0.0069791 | -0.02788 | -0.049954 | -0.040178 | 0.00094606 | -0.022031 | 0.055132 | 0.044553 | -0.21787 | -0.014283 | -0.02603 | 1.8951 | 1.6296 | 1.4877 | 1.4145 | 1.561 | 1.387 | 1.4832 | -5.1956 | 28.157 | -93.9514 | 29.3838 | -92.1524 | -91.127 | -88.9755 | 92.1753 | -30.2582 | -30.4733 | 92.2485 | 92.1707 | 92.0746 | -0.004578 | -0.10071 | -3.2639 | -3.7308 | -2.504 | -1.4648 | 1.712 | -0.43945 | 4.9759 | 2.8244 | 0.073242 | -0.073242 | 1.799 | 123.3353 | 0.14191 | 122.1085 | 92.3172 | 118.8446 | -30.4001 | -125.8392 | 92.1021 | 120.0714 | 92.5827 | 85.4919
1328.2188 | 122.4472 | -71.7316 | 50.5875 | 0.010147 | -0.015866 | -0.082001 | -0.0069791 | -0.032793 | -0.050808 | -0.036974 | -0.0051575 | -0.021604 | 0.055986 | 0.042631 | -0.21937 | -0.014283 | -0.024535 | 0.28839 | 0.41657 | 0.24261 | 0.32501 | 0.51727 | 0.33417 | 0.39368 | -1.03 | 49.8825 | -72.2214 | 47.8821 | -71.5393 | -71.1365 | -71.434 | 71.9742 | -50.1709 | -50.2625 | 72.2488 | 72.1252 | 72.0657 | 0.15106 | 0.091552 | -0.48981 | -0.70496 | -2.7054 | 0.19226 | 0.29755 | 0.59509 | 0.78735 | 1.0849 | 0.27466 | 0.082397 | 0.68207 | 120.1035 | 0.17395 | 122.1039 | 72.1481 | 121.6141 | -50.3448 | -122.8088 | 72.0566 | 119.6136 | 72.02 | 70.7016
1330 | 122.3145 | -73.5077 | 48.5504 | -0.012741 | -0.012448 | -0.079865 | -0.0035611 | -0.030016 | -0.049313 | -0.038683 | 0.00094606 | -0.018827 | 0.058977 | 0.049467 | -0.22001 | -0.016419 | -0.023894 | 0.1831 | 0.37079 | 0.10071 | 0.20599 | 0.32959 | 0.2243 | 0.28381 | -4.129 | 47.9874 | -74.0021 | 49.0448 | -72.6425 | -73.4116 | -74.025 | 73.6084 | -48.1796 | -48.3444 | 73.8373 | 73.7915 | 73.732 | 0.1831 | 0.1236 | -0.49439 | -0.56305 | 0.49439 | 0.86517 | -0.51727 | 0.09613 | -0.022888 | 0.59052 | 0.22888 | 0.10529 | 1.3596 | 123.0469 | 0.27008 | 121.9894 | 73.8785 | 121.4951 | -48.4497 | -122.5525 | 73.7137 | 122.5525 | 73.6908 | 69.3787
1331.7812 | 122.4106 | -50.4135 | 71.6812 | -0.0051118 | -0.010739 | -0.079865 | -0.0065517 | -0.030016 | -0.049099 | -0.041674 | 0.0039979 | -0.01904 | 0.056627 | 0.046476 | -0.21851 | -0.015351 | -0.024748 | 2.1057 | 2.1881 | 2.0279 | 2.1332 | 2.243 | 2.1011 | 2.1835 | 1.1627 | 71.933 | -50.2304 | 72.1664 | -50.4135 | -50.4501 | -50.1984 | 52.4414 | -69.4931 | -69.548 | 52.6566 | 52.597 | 52.5146 | 0.15564 | 0.073242 | 0.18311 | 0.25177 | 0.48523 | 0 | 0.21515 | -0.036621 | 0.032044 | -0.21973 | 0.21515 | 0.10529 | -0.18311 | 122.3969 | 0.16022 | 122.1634 | 52.6016 | 122.3465 | -69.6533 | -121.9116 | 52.5467 | 122.58 | 52.5192 | 51.5762
1333.5 | 122.081 | -51.3428 | 71.9788 | 0.010147 | -0.015011 | -0.079224 | -0.0044155 | -0.030443 | -0.050167 | -0.043169 | -0.0051575 | -0.017758 | 0.058123 | 0.046689 | -0.2183 | -0.015137 | -0.022826 | -0.064087 | 0.12817 | -0.11902 | -0.1236 | 0.018311 | -0.1236 | -0.045776 | 1.3733 | 71.4661 | -50.6195 | 70.61 | -53.6911 | -53.2883 | -52.066 | 51.2238 | -71.8506 | -72.1024 | 51.3611 | 51.297 | 51.2192 | 0.073243 | -0.004577 | 0.72327 | -0.5127 | -1.3687 | -2.3483 | -0.72327 | -1.9455 | -1.4465 | -2.6688 | 0.13733 | -0.004577 | -3.0716 | 121.2296 | 0.24719 | 122.0856 | 51.4709 | 122.8088 | -72.0978 | -122.5983 | 51.2192 | 121.9528 | 51.2787 | 52.7161
1335.2812 | 122.3648 | -47.7493 | 74.3408 | -0.0051118 | -0.013302 | -0.078583 | -0.0052701 | -0.029162 | -0.049099 | -0.044878 | -0.0021057 | -0.017118 | 0.055986 | 0.045835 | -0.21937 | -0.015137 | -0.022612 | -0.22888 | -0.054932 | -0.27924 | -0.24719 | -0.10071 | -0.27924 | -0.20142 | -0.1831 | 74.7986 | -47.3236 | 75.2151 | -47.6166 | -47.7951 | -47.9599 | 47.4701 | -74.3958 | -74.588 | 47.6486 | 47.5479 | 47.4701 | 0.07782 | 0 | 0.42572 | 0.45776 | 0.87433 | 0.13275 | -0.21057 | -0.045776 | -0.63629 | -0.4715 | 0.17853 | 0.032044 | -0.29297 | 122.5388 | 0.2243 | 122.1222 | 47.6944 | 122.5479 | -74.6201 | -121.6644 | 47.5021 | 122.9645 | 47.5204 | 47.5662
1337.0625 | 122.0856 | -63.9542 | 57.8979 | -0.0051118 | -0.015652 | -0.077515 | -0.0080471 | -0.030016 | -0.046322 | -0.039324 | -0.0021057 | -0.020536 | 0.05855 | 0.038999 | -0.21851 | -0.015351 | -0.020262 | -0.37994 | -0.1831 | -0.37537 | -0.35248 | -0.19226 | -0.35706 | -0.28839 | -1.2634 | 58.1131 | -63.8214 | 57.9803 | -63.8031 | -63.945 | -63.8031 | 63.5788 | -58.0811 | -58.2504 | 63.7619 | 63.6658 | 63.5971 | 0.086975 | 0.01831 | 0.13275 | 0.21515 | 0.082398 | 0.15106 | 0.15106 | 0.009156 | 0.01831 | -0.1236 | 0.1831 | 0.022888 | 0.01831 | 121.8018 | 0.19226 | 121.9345 | 63.7711 | 122.0673 | -58.2733 | -121.7194 | 63.6017 | 121.9345 | 63.5742 | 62.6907
1338.7969 | 121.8246 | -61.4136 | 60.7864 | 0.0025177 | -0.014584 | -0.079651 | -0.0076199 | -0.033648 | -0.049954 | -0.040605 | -0.0021057 | -0.022031 | 0.055773 | 0.044126 | -0.21766 | -0.015565 | -0.024535 | -0.33417 | -0.19226 | -0.35706 | -0.27008 | -0.21057 | -0.19684 | -0.13733 | -1.2634 | 58.0353 | -63.7207 | 58.9417 | -62.6083 | -61.5234 | -60.4065 | 61.0565 | -60.9787 | -61.0565 | 61.203 | 61.2762 | 61.2167 | 0.21973 | 0.16022 | -2.3071 | -2.7512 | -1.8448 | -1.1948 | 1.0071 | -0.10986 | 3.3142 | 2.1973 | 0.14648 | 0.086975 | 1.1124 | 122.6624 | 0.16479 | 121.756 | 61.2213 | 119.4489 | -61.1435 | -124.5071 | 61.1435 | 120.3552 | 61.0794 | 60.1501
1340.5781 | 122.3511 | -65.0162 | 56.7261 | -0.0051118 | -0.012661 | -0.079224 | -0.0018521 | -0.032793 | -0.049954 | -0.039965 | 0.00094606 | -0.021176 | 0.055773 | 0.048398 | -0.22022 | -0.017701 | -0.026671 | 1.3504 | 1.4557 | 1.3 | 1.3596 | 0.85602 | 1.3641 | 1.4374 | -2.4399 | 58.0124 | -64.2426 | 57.0602 | -64.92 | -64.856 | -64.9887 | 66.3162 | -55.2704 | -55.3665 | 65.8722 | 66.4536 | 66.3803 | 0.13733 | 0.064087 | 0.77362 | 1.2863 | 0.33417 | 0.09613 | 0.027466 | 0.16022 | -0.74615 | -0.6134 | -0.44403 | 0.059509 | -0.67749 | 121.3028 | 0.15564 | 122.2549 | 66.4719 | 123.0286 | -55.426 | -120.9686 | 66.3757 | 122.0764 | 66.3666 | 62.5763
1342.3594 | 122.2366 | -66.0919 | 55.838 | -0.012741 | -0.015866 | -0.078797 | -0.0039883 | -0.028521 | -0.051235 | -0.04146 | 0.00094606 | -0.01904 | 0.057482 | 0.043485 | -0.21723 | -0.017273 | -0.022398 | 1.1719 | 1.3641 | 1.1581 | 1.149 | 1.2222 | 1.1536 | 1.1993 | -9.3292 | 55.1743 | -66.9479 | 55.9982 | -66.1423 | -66.1057 | -66.1148 | 67.2501 | -54.4739 | -54.689 | 67.3141 | 67.2913 | 67.2455 | 0.041199 | -0.004578 | -0.85602 | -0.66376 | 0.16022 | -0.050354 | -0.022888 | -0.013733 | 0.83313 | 0.84228 | 0.064087 | -0.009155 | 0.80566 | 122.9462 | 0.20599 | 122.1222 | 67.4561 | 121.2662 | -54.6799 | -122.7859 | 67.2409 | 122.0901 | 67.2638 | 56.7627
1344.0625 | 122.4426 | -38.5941 | 83.2581 | -0.0051118 | -0.011166 | -0.07837 | -0.0067653 | -0.03557 | -0.049954 | -0.040605 | -0.0051575 | -0.02139 | 0.056414 | 0.042844 | -0.21894 | -0.016205 | -0.021544 | 0.33875 | 0.4303 | 0.27008 | 0.35248 | 0.49896 | 0.3479 | 0.40283 | -1.0986 | 83.2901 | -38.6581 | 85.1532 | -38.3286 | -38.9877 | -38.7085 | 38.8641 | -82.8278 | -82.9056 | 39.093 | 38.9969 | 38.942 | 0.13275 | 0.077819 | -0.064087 | 0.032043 | 1.8951 | 0.2655 | -0.11444 | -0.39368 | -0.050354 | -0.32959 | 0.22888 | 0.082397 | 0.32959 | 123.8113 | 0.16022 | 121.9482 | 39.0244 | 121.8842 | -82.988 | -121.9162 | 38.9465 | 123.7473 | 38.9328 | 37.4954
1345.8438 | 121.8338 | -33.5678 | 87.7762 | 0.025406 | -0.017147 | -0.07602 | -0.0084743 | -0.035357 | -0.051235 | -0.041674 | -0.04483 | -0.020749 | 0.055559 | 0.040708 | -0.21787 | -0.015992 | -0.019835 | 0.51727 | 0.63629 | 0.56763 | 0.62256 | 0.70038 | 0.58136 | 0.6134 | 19.931 | 86.4716 | -34.5108 | 88.6734 | -33.5495 | -33.6731 | -33.8287 | 34.1354 | -87.1399 | -87.1536 | 34.2682 | 34.1812 | 34.1492 | 0.045776 | 0.013733 | -0.94299 | -1.3046 | 0.89722 | 0.01831 | -0.26093 | -0.10529 | 0.68207 | 0.83771 | 0.13275 | 0.054932 | 0.9613 | 123.1842 | 0.068665 | 120.9824 | 34.2041 | 120.0394 | -87.2086 | -122.287 | 34.1904 | 122.2412 | 34.0851 | 53.4988
1347.625 | 122.3969 | -27.182 | 94.4733 | 0.010147 | -0.015652 | -0.079224 | -0.0076199 | -0.033861 | -0.051449 | -0.041033 | -0.173 | -0.02139 | 0.054064 | 0.042844 | -0.21744 | -0.016633 | -0.02603 | 0.009155 | 0.16022 | 0.33875 | -0.045776 | -0.054932 | -0.21515 | -0.19684 | 0.64545 | 94.4092 | -27.1362 | 94.8944 | -26.8616 | -26.6647 | -27.2049 | 27.5208 | -94.3131 | -94.519 | 27.1271 | 26.9852 | 26.9669 | -0.53558 | -0.55389 | 0.045777 | -0.064087 | 0.42114 | 0.32043 | -0.022888 | 0.51727 | -0.068665 | 0.4715 | -0.39368 | -0.38452 | 0.27466 | 122.0306 | -0.17853 | 121.5454 | 27.3422 | 121.5912 | -94.1345 | -121.6095 | 27.1362 | 122.0764 | 27.1912 | 27.8275
1349.4062 | 122.5159 | -77.3804 | 44.8288 | -0.012741 | -0.011807 | -0.078797 | -0.0086879 | -0.03258 | -0.050595 | -0.038469 | 0.0070497 | -0.021817 | 0.057482 | 0.045194 | -0.21616 | -0.017273 | -0.02133 | -0.11902 | 0.082397 | -0.022888 | -0.10529 | 0.041199 | -0.11444 | -0.082397 | -7.3746 | 43.2037 | -79.3762 | 44.4122 | -78.2318 | -78.7582 | -77.3209 | 77.3575 | -44.7464 | -44.9341 | 77.4216 | 77.298 | 77.2659 | -0.059509 | -0.091553 | -1.9959 | -1.6251 | -0.41656 | -0.85144 | 0.059509 | -1.3779 | 2.0554 | 0.61798 | 0.064087 | -0.082398 | 1.1444 | 123.7885 | 0.10528 | 122.58 | 77.4628 | 120.5841 | -44.8517 | -124.205 | 77.2751 | 121.7926 | 77.2614 | 70.0058
1351.1094 | 122.2458 | -0.43488 | 99.4263 | 0.09407 | -0.022488 | -0.088196 | 0.0043431 | -0.037493 | -0.064266 | -0.045519 | 0.046722 | 0.011081 | 0.0055712 | 0.0065284 | 0.067744 | 0.011566 | 0.0098587 | -0.2655 | 0.11902 | 0.24719 | -0.1831 | 0.091553 | 0.091553 | 0.082397 | 0.97961 | 104.7318 | -0.60425 | 101.0742 | 0.082397 | 0.082397 | 0.091553 | 0.68207 | -99.3073 | -99.6094 | 0.52643 | 0.51727 | 0.52643 | -0.16479 | -0.15564 | -0.16937 | 5.3055 | 1.6479 | 0.51727 | 0.52643 | 0.51727 | 0.6958 | 0.68664 | -0.15564 | -0.4303 | 0.68664 | 101.6785 | -0.12817 | 105.336 | 0.55389 | 105.1666 | -99.1791 | -100.0305 | 0.25177 | 101.5091 | 0.16937 | 1.4145
1352.8906 | 121.9666 | -1.1398 | 120.3003 | -0.10429 | -0.015225 | -0.078797 | -0.0080471 | -0.032152 | -0.049954 | -0.044878 | -0.099762 | -0.019895 | 0.056841 | 0.039426 | -0.21723 | -0.016846 | -0.02368 | -0.036621 | 0.082397 | -0.050354 | -0.022888 | 0.15106 | -0.018311 | -0.041199 | 0.87891 | 120.4559 | -1.0162 | 121.0739 | -0.84686 | -0.89722 | -0.92468 | 1.0895 | -120.2179 | -120.3232 | 1.2909 | 1.0986 | 1.1215 | 0.009155 | 0.032043 | 0.1236 | 0.15564 | 0.77362 | 0.29297 | 0.21515 | 0.24261 | 0.091552 | 0.11902 | 0.20142 | 0.027466 | 0.16937 | 122.0901 | 0.13275 | 121.4722 | 1.2222 | 121.5958 | -120.3506 | -121.3165 | 1.1169 | 122.2137 | 1.1032 | 2.0187
1354.5938 | 106.9336 | -2.504 | 99.1608 | 0.13222 | 0.013614 | 0.032073 | 0.0039157 | 0.014204 | 0.018406 | 0.016218 | 0.052826 | 0.011294 | 0.0081348 | 0.0075964 | 0.070094 | 0.012206 | 0.010713 | -0.33417 | 0.11902 | 0.004578 | -0.27924 | 0.09613 | 0.09613 | 0.10529 | 0.69122 | 119.22 | -2.504 | 99.9802 | -2.9114 | 0.091553 | 0.10071 | 2.5085 | -99.0417 | -99.44 | 2.6001 | 2.6093 | 2.6001 | 0.10071 | 0.091552 | 0 | 20.0592 | 0.8194 | -0.40741 | 2.6047 | 2.5955 | 2.6047 | 2.5955 | 0.091552 | -0.28381 | -0.40741 | 102.4841 | 0.11444 | 121.7239 | 2.623 | 121.7239 | -99.1562 | -101.6647 | 2.2247 | 102.4841 | 2.1698 | 3.1952
1356.375 | 121.5866 | -3.6804 | 117.7963 | 0.11696 | -0.016934 | -0.096314 | -0.011038 | -0.038134 | -0.060421 | -0.047441 | -0.0784 | -0.031644 | 0.049578 | 0.051176 | -0.21509 | -0.015778 | -0.022185 | -0.20599 | 0.13275 | -0.12817 | -0.15564 | -0.28839 | -0.51727 | -0.70038 | 0.56305 | 117.7185 | -3.6758 | 117.8192 | -3.7491 | -3.9917 | -4.1565 | 3.5522 | -117.6636 | -117.952 | 3.392 | 2.98 | 3.1631 | -0.5722 | -0.3891 | 0.004578 | -0.07782 | 0.022888 | -0.068664 | -0.47607 | -0.31128 | -0.48065 | -0.31586 | -0.16022 | -0.027466 | -0.073242 | 121.4951 | 0.26093 | 121.3943 | 3.8132 | 121.3989 | -117.9245 | -121.4722 | 3.5248 | 121.4996 | 3.4744 | 4.2435
1358.1094 | 104.8004 | -4.3259 | 117.1143 | 0.12459 | 0.014255 | 0.032714 | -0.018301 | 0.01399 | 0.018619 | 0.016432 | 0.058929 | 0.011294 | 0.0072802 | 0.046262 | -0.24201 | 0.011779 | -0.030302 | -0.31128 | 0.13733 | -0.10071 | -0.21057 | -0.33875 | -0.21515 | 0.10071 | 0.88806 | 117.4255 | -4.4083 | 100.0031 | -4.5822 | -4.9484 | 0.068665 | 4.2252 | -116.9769 | -117.3248 | 3.9871 | 4.4266 | 4.1107 | 0.20142 | -0.11444 | -0.082397 | 0.31128 | -17.1112 | -0.25635 | 4.3945 | -0.62256 | 4.4769 | -0.54016 | -0.23804 | -0.10986 | -0.17395 | 104.4113 | 0.23804 | 121.8338 | 4.4632 | 121.7514 | -117.215 | -121.5225 | 4.1153 | 104.3289 | 4.0146 | 5.2139
1359.8906 | 122.4243 | -5.9738 | 107.8766 | -0.11192 | -0.025692 | -0.085846 | -0.0054837 | -0.029375 | -0.050381 | -0.045092 | -0.04483 | -0.034635 | 0.045519 | 0.05673 | -0.22257 | -0.023896 | -0.033293 | -0.2243 | 0.14648 | -0.11444 | -0.11902 | -0.18768 | -0.42114 | -0.13275 | 0.51727 | 115.329 | -6.0883 | 104.4525 | -6.0745 | -6.4774 | -6.8115 | 5.8594 | -107.7301 | -107.9956 | 5.7861 | 5.8411 | 5.5527 | -0.01831 | -0.3067 | -0.11444 | 7.4524 | -3.4241 | -0.10071 | -0.83771 | -0.50354 | -0.72327 | -0.3891 | -0.073242 | -0.004578 | 0.013733 | 110.5408 | 0.26093 | 121.4172 | 6.1203 | 121.3028 | -107.991 | -113.9648 | 5.8548 | 110.4263 | 5.7495 | 6.4911
1361.6562 | 122.0535 | -3.8681 | 118.5242 | -0.31792 | -0.016293 | -0.078156 | -0.0054837 | -0.03023 | -0.04739 | -0.040605 | -0.090607 | -0.022031 | 0.055559 | 0.050107 | -0.2168 | -0.013856 | -0.02368 | -0.032043 | 0.09613 | -0.09613 | -0.022888 | 0.13733 | 0 | -0.036621 | 0.68665 | 117.952 | -3.8269 | 118.2037 | -3.6163 | -3.6438 | -3.6896 | 3.772 | -118.428 | -118.5471 | 4.0054 | 3.8315 | 3.8681 | 0.059509 | 0.09613 | 0.041199 | -0.5722 | -0.32044 | 0.25177 | 0.17853 | 0.2243 | 0.13733 | 0.1831 | 0.23346 | 0.073242 | 0.21057 | 122.0306 | 0.19226 | 121.7789 | 3.9642 | 121.8201 | -118.6203 | -122.3511 | 3.8452 | 122.0718 | 3.8361 | 4.5547
1363.4531 | 122.438 | -11.4349 | 110.8383 | 0.15511 | -0.01437 | -0.079865 | -0.0048427 | -0.031725 | -0.048886 | -0.037828 | -0.011261 | -0.020963 | 0.053423 | 0.041135 | -0.21766 | -0.01706 | -0.023039 | -0.086975 | 0.086975 | -0.10986 | -0.064087 | 0.091553 | -0.082397 | 0 | 0.38452 | 110.7101 | -11.4807 | 110.7834 | -11.3663 | -11.412 | -11.3846 | 11.3251 | -110.7513 | -110.9024 | 11.5265 | 11.4349 | 11.3525 | 0.10986 | 0.027466 | -0.045776 | -0.12817 | -0.054932 | 0.068665 | 0.050354 | 0.022889 | 0.09613 | 0.068665 | 0.20142 | 0.045776 | 0.11444 | 122.2641 | 0.19684 | 122.1909 | 11.5219 | 122.1451 | -110.9482 | -122.319 | 11.3708 | 122.2183 | 11.348 | 11.8195
1365.1719 | 122.2046 | -11.1832 | 110.8978 | -0.21111 | -0.013089 | -0.079011 | -0.0052701 | -0.029375 | -0.049099 | -0.039751 | -0.23099 | -0.023954 | 0.054277 | 0.047117 | -0.21552 | -0.013856 | -0.022185 | -0.13275 | 0.11902 | -0.13733 | -0.14648 | -0.027466 | -0.22888 | -0.35248 | 0.36163 | 110.7834 | -11.2106 | 110.701 | -11.0687 | -11.2473 | -11.3525 | 11.0458 | -110.7788 | -111.0443 | 11.1557 | 10.8307 | 10.9543 | -0.21515 | -0.091553 | -0.027465 | -0.11444 | -0.19684 | 0.11444 | -0.16937 | -0.064086 | -0.14191 | -0.036621 | 0.10986 | -0.009155 | 0.14191 | 121.9116 | 0.25635 | 121.994 | 11.3022 | 121.9666 | -111.0352 | -122.1085 | 11.0367 | 121.8842 | 11.0504 | 11.5448
1366.9531 | 121.669 | -10.7986 | 111.5662 | -0.46288 | 0.013187 | 0.031646 | -0.015738 | -0.045397 | -0.061703 | 0.015364 | -0.24625 | 0.011722 | 0.052996 | 0.034513 | -0.24479 | 0.011352 | -0.04077 | -0.20599 | 0.13733 | -0.12817 | -0.073242 | 0.022888 | -0.26093 | -0.38452 | 0.48981 | 110.9528 | -10.8856 | 110.7056 | -10.6842 | -10.9177 | -11.7279 | 10.6705 | -111.4288 | -111.6394 | 10.8215 | 10.4141 | 10.5377 | -0.25635 | -0.13275 | -0.086975 | -0.6134 | -0.8606 | 0.11444 | -0.92926 | -0.11902 | -0.84229 | -0.032044 | 0.15106 | 0.054932 | 0.20142 | 121.5912 | 0.2655 | 121.8384 | 10.936 | 121.7514 | -111.6943 | -122.4518 | 10.7254 | 121.5042 | 10.5927 | 11.2885
1368.7344 | 121.5317 | -10.6247 | 111.5112 | 0.12459 | 0.013614 | 0.032928 | -0.0035611 | -0.048174 | -0.060635 | -0.062609 | -0.16385 | -0.026944 | 0.043383 | 0.046903 | -0.21595 | -0.016846 | -0.021544 | -0.19226 | 0.10071 | -0.14191 | -0.15106 | -0.050354 | -0.24719 | -0.35248 | 0.3479 | 111.3281 | -10.6476 | 110.9848 | -10.5881 | -10.6293 | -10.6522 | 10.4828 | -111.4105 | -111.6623 | 10.5743 | 10.2722 | 10.3775 | -0.21057 | -0.10528 | -0.022888 | -0.1831 | -0.52643 | 0.036621 | -0.027466 | -0.004577 | -0.004578 | 0.018311 | 0.091553 | -0.009155 | 0.059509 | 121.6324 | 0.24262 | 121.9757 | 10.7254 | 121.9528 | -111.6531 | -122.1588 | 10.4736 | 121.6095 | 10.4324 | 10.9726
1370.5156 | 122.3694 | -10.5698 | 111.7401 | 0.13985 | -0.013089 | -0.078797 | -0.0067653 | -0.030443 | -0.04739 | -0.038469 | 0.00094606 | -0.020536 | 0.055132 | 0.040708 | -0.21595 | -0.016633 | -0.027739 | -0.068665 | 0.064087 | -0.10986 | -0.054932 | 0.1236 | -0.082397 | -0.004578 | 0.44861 | 111.6714 | -10.6064 | 111.6989 | -10.4645 | -10.524 | -10.4874 | 10.4599 | -111.676 | -111.795 | 10.6934 | 10.5652 | 10.4874 | 0.10529 | 0.027466 | -0.036621 | -0.068664 | -0.041198 | 0.10529 | 0.082397 | 0.045776 | 0.11902 | 0.082397 | 0.23346 | 0.054931 | 0.14191 | 122.3053 | 0.17395 | 122.2778 | 10.6339 | 122.2412 | -111.85 | -122.3465 | 10.5148 | 122.2687 | 10.5011 | 11.0184
1372.2969 | 117.1097 | -9.8282 | 112.4359 | -0.4705 | -0.017361 | -0.081147 | -0.0054837 | -0.026598 | -0.049954 | -0.042742 | -0.10281 | -0.025449 | 0.051928 | 0.042631 | -0.21637 | -0.017914 | -0.023894 | -0.14191 | 0.091553 | -0.15106 | -0.16022 | -0.027466 | -0.13733 | -0.20142 | 0.39825 | 112.2025 | -9.9701 | 111.5982 | -9.8602 | -9.8785 | -9.9701 | 9.6771 | -112.3444 | -112.5961 | 9.8007 | 9.6268 | 9.6909 | -0.050354 | 0.013733 | -0.14191 | -0.23346 | -0.83771 | -0.032043 | -0.14191 | -0.050354 | 0 | 0.091553 | 0.1236 | -0.009155 | 0.10986 | 121.5683 | 0.24261 | 122.1725 | 9.9197 | 122.0306 | -112.587 | -122.406 | 9.668 | 121.4264 | 9.6863 | 10.2264
1374.0781 | 121.8201 | -9.5581 | 112.262 | -0.53917 | -0.016079 | -0.081147 | -0.0061245 | -0.03322 | -0.049526 | -0.040392 | -0.023468 | -0.019467 | 0.057054 | 0.049467 | -0.21702 | -0.015992 | -0.024107 | -0.16479 | 0.082397 | -0.16022 | -0.15106 | -0.050354 | -0.15106 | -0.10529 | 0.42572 | 112.4313 | -9.7 | 112.1063 | -9.5581 | -9.5993 | -9.5535 | 9.3979 | -112.1796 | -112.413 | 9.5078 | 9.4528 | 9.407 | 0.054931 | 0.009155 | -0.14191 | 0.16937 | -0.15564 | 0 | 0.004577 | -0.041199 | 0.14648 | 0.10071 | 0.10986 | 0.009155 | 0.14191 | 121.8063 | 0.24261 | 122.1313 | 9.6405 | 121.9894 | -112.4222 | -121.962 | 9.407 | 121.6644 | 9.3933 | 9.9838
1375.7969 | 122.1268 | -1.5152 | 120.7626 | 0.14748 | -0.017575 | -0.079224 | -0.0056973 | -0.033434 | -0.050167 | -0.043383 | 0.0039979 | -0.02139 | 0.056627 | 0.041563 | -0.21851 | -0.018342 | -0.021758 | -0.068665 | 0.10986 | -0.11444 | -0.068665 | 0.07782 | -0.050354 | 0.018311 | 0.72327 | 120.7443 | -1.5884 | 120.7901 | -1.2909 | -1.3367 | -1.3184 | 1.4008 | -120.6528 | -120.8313 | 1.593 | 1.5335 | 1.4648 | 0.13275 | 0.064087 | -0.073242 | -0.01831 | 0.027466 | 0.2243 | 0.19684 | 0.17853 | 0.27008 | 0.25177 | 0.19226 | 0.045776 | 0.29755 | 122.3785 | 0.2243 | 122.3328 | 1.6251 | 122.2595 | -120.8771 | -122.3511 | 1.4465 | 122.3053 | 1.4465 | 2.2385
1377.5781 | 95.9793 | -1.3367 | 120.3094 | -0.37132 | 0.013187 | 0.033142 | -0.020437 | 0.013563 | 0.019474 | 0.017073 | -0.1669 | 0.010653 | 0.0079212 | 0.047117 | -0.24372 | 0.014129 | -0.036498 | -0.036621 | 0.11444 | -0.10986 | -0.059509 | 0.064087 | -0.086975 | -0.1831 | 0.737 | 120.4285 | -1.442 | 110.5774 | -1.2131 | -1.3779 | -1.4786 | 1.2268 | -120.195 | -120.369 | 1.4008 | 1.1536 | 1.2497 | -0.073242 | 0.022888 | -0.10529 | 0.11902 | -9.7321 | 0.1236 | -0.14191 | -0.041199 | -0.036621 | 0.064087 | 0.17395 | 0.050354 | 0.22888 | 112.0193 | 0.2243 | 121.8704 | 1.4511 | 121.7651 | -120.4193 | -121.7514 | 1.2772 | 111.9141 | 1.3 | 2.0737
1379.2969 | 107.0709 | -1.3779 | 120.1355 | -0.51628 | -0.019711 | -0.078583 | -0.0024929 | -0.031298 | -0.050808 | -0.042101 | -0.04483 | -0.025876 | 0.052141 | 0.039854 | -0.21702 | -0.024109 | -0.027739 | -0.091553 | 0.13275 | -0.12817 | -0.14191 | 0 | -0.10071 | -0.086975 | 0.6546 | 120.3415 | -1.6479 | 116.684 | -1.3733 | -1.474 | -1.5564 | 1.2497 | -120.0027 | -120.2774 | 1.3779 | 1.2909 | 1.2772 | 0.041199 | 0.027466 | -0.27008 | 0.20599 | -3.4515 | 0.004578 | -0.17853 | -0.09613 | 0.091553 | 0.17395 | 0.12817 | -0.013733 | 0.27466 | 118.3319 | 0.26093 | 121.9894 | 1.5106 | 121.7194 | -120.2637 | -121.7834 | 1.236 | 118.0618 | 1.2863 | 2.0325
1381.0781 | 121.8658 | -1.8082 | 120.282 | 0.13985 | -0.011593 | -0.078583 | -0.0037747 | -0.027666 | -0.04974 | -0.041246 | 0.00094606 | -0.019895 | 0.058763 | 0.045835 | -0.21702 | -0.016846 | -0.020689 | -0.032043 | 0.10071 | -0.086975 | -0.027466 | 0.10986 | -0.045776 | 0.027466 | 0.71869 | 120.3461 | -1.8723 | 120.314 | -1.5747 | -1.6342 | -1.5701 | 1.7212 | -120.1813 | -120.3094 | 1.918 | 1.8356 | 1.7624 | 0.11444 | 0.041199 | -0.064086 | 0.064087 | 0.032044 | 0.23346 | 0.23804 | 0.17395 | 0.30212 | 0.23804 | 0.19684 | 0.059509 | 0.29755 | 122.1863 | 0.18768 | 122.2183 | 1.9089 | 122.1542 | -120.369 | -122.1542 | 1.7807 | 122.1222 | 1.7761 | 2.5269
1382.7969 | 122.2229 | -2.7603 | 119.22 | 0.0025177 | -0.013089 | -0.079438 | -0.0074063 | -0.033007 | -0.049313 | -0.038683 | -0.0021057 | -0.020108 | 0.054918 | 0.040708 | -0.21702 | -0.016419 | -0.023894 | -0.073242 | 0.082397 | -0.091553 | -0.064087 | 0.068665 | -0.068665 | -0.004578 | 0.59052 | 119.577 | -2.7832 | 119.5724 | -2.5406 | -2.6093 | -2.5772 | 2.6688 | -119.1376 | -119.2841 | 2.829 | 2.7557 | 2.6916 | 0.086975 | 0.022888 | -0.022888 | 0.35706 | 0.35248 | 0.21973 | 0.18311 | 0.15106 | 0.20599 | 0.17395 | 0.16022 | 0.027466 | 0.24261 | 122.3557 | 0.17395 | 122.3602 | 2.8427 | 122.3373 | -119.3115 | -122.0032 | 2.6962 | 122.3328 | 2.6871 | 3.3508
1384.5938 | 103.9673 | -2.7145 | 118.7164 | 0.17036 | 0.014469 | 0.033142 | -0.01467 | 0.013777 | 0.019687 | 0.0175 | -0.014313 | -0.021817 | 0.0077076 | 0.039854 | -0.23453 | 0.011993 | -0.035429 | -0.050354 | 0.11444 | -0.11444 | -0.059509 | 0.068665 | -0.082397 | -0.027466 | 0.69122 | 119.0277 | -3.0304 | 119.3619 | -2.7649 | -2.8748 | -2.9343 | 2.6001 | -118.602 | -118.7759 | 2.7832 | 2.6871 | 2.6321 | 0.086975 | 0.032044 | -0.31586 | 0.31128 | 0.64545 | -0.050354 | -0.21973 | -0.16022 | 0.096131 | 0.15564 | 0.18311 | 0.054932 | 0.2655 | 122.3923 | 0.22888 | 122.0581 | 2.829 | 121.7422 | -118.8309 | -121.7468 | 2.655 | 122.0764 | 2.6642 | 3.4058
1386.3125 | 122.3877 | -4.0421 | 118.3411 | -0.46288 | -0.015652 | -0.080292 | -0.0076199 | -0.031298 | -0.051449 | -0.040178 | 0.0039979 | -0.019895 | 0.056841 | 0.042417 | -0.21937 | -0.015565 | -0.019621 | -0.027466 | 0.086975 | -0.09613 | 0.004578 | 0.15564 | 0.004578 | 0.054932 | 0.71411 | 118.2037 | -4.0924 | 118.3136 | -3.7628 | -3.8223 | -3.8269 | 3.9459 | -118.2541 | -118.3365 | 4.1977 | 4.097 | 4.0466 | 0.15106 | 0.10071 | -0.050354 | -0.13733 | -0.027465 | 0.27924 | 0.21515 | 0.21973 | 0.2655 | 0.27008 | 0.25177 | 0.10071 | 0.32959 | 122.406 | 0.1831 | 122.2961 | 4.129 | 122.2458 | -118.4372 | -122.4335 | 4.0466 | 122.3557 | 4.0146 | 4.7562
1388.0781 | 122.4106 | -3.7949 | 118.2449 | 0.17036 | 0.014682 | 0.033142 | -0.012747 | 0.013777 | 0.01926 | 0.017073 | 0.0039979 | -0.029935 | 0.069872 | 0.035154 | -0.22385 | -0.029236 | -0.030089 | -0.082397 | 0.11902 | -0.1236 | -0.10529 | 0 | -0.14648 | -0.091553 | 0.55389 | 118.1717 | -4.0146 | 117.7643 | -3.8315 | -3.8818 | -3.8864 | 3.6713 | -118.1259 | -118.3502 | 3.7949 | 3.7033 | 3.6484 | 0.032043 | -0.022888 | -0.21973 | -0.073242 | -0.48065 | -0.036621 | -0.091553 | -0.086975 | 0.12817 | 0.13275 | 0.1236 | 0.01831 | 0.1831 | 121.7789 | 0.24261 | 122.1863 | 3.9139 | 121.9666 | -118.3685 | -122.2595 | 3.6896 | 121.5591 | 3.7125 | 4.3488
1389.875 | 122.168 | -3.4378 | 118.396 | -0.15007 | -0.015652 | 0.031005 | -0.0067653 | -0.045183 | -0.08691 | -0.049364 | 0.00094606 | -0.024808 | 0.046373 | 0.041776 | -0.21509 | -0.018769 | -0.022185 | -0.10986 | 0.14648 | -0.10529 | -0.14648 | -0.059509 | -0.17395 | -0.10071 | 0.52643 | 118.8904 | -3.2135 | 117.9245 | -3.4653 | -3.5294 | -3.4149 | 3.3325 | -118.2495 | -118.5425 | 3.3783 | 3.3371 | 3.2639 | 0.004578 | -0.068664 | 0.2243 | 0.49439 | -0.4715 | -0.027466 | 0.022888 | -0.091553 | -0.20142 | -0.31586 | 0.045777 | -0.041198 | -0.25177 | 121.138 | 0.25177 | 122.1039 | 3.5843 | 122.3282 | -118.5013 | -121.6095 | 3.2913 | 121.3623 | 3.3279 | 3.9642
1391.5938 | 122.3007 | -3.3463 | 118.6157 | 0.0025177 | -0.011807 | -0.079011 | -0.0074063 | -0.029802 | -0.048245 | -0.04146 | 0.0039979 | -0.020963 | 0.055986 | 0.041135 | -0.2168 | -0.017487 | -0.021117 | -0.027466 | 0.082397 | -0.07782 | -0.009155 | 0.13733 | -0.050354 | 0.036621 | 0.62714 | 118.9133 | -3.3783 | 119.0186 | -3.1036 | -3.154 | -3.1036 | 3.2684 | -118.5333 | -118.6249 | 3.4836 | 3.3829 | 3.2959 | 0.11444 | 0.027466 | -0.032044 | 0.29755 | 0.40283 | 0.24261 | 0.24261 | 0.19226 | 0.27466 | 0.2243 | 0.21515 | 0.068665 | 0.27466 | 122.3969 | 0.16022 | 122.2916 | 3.4286 | 122.2595 | -118.6935 | -121.994 | 3.3371 | 122.3648 | 3.3188 | 3.9734
1393.3281 | 122.0947 | -5.8044 | 116.0934 | -0.31029 | -0.013089 | -0.079651 | -0.0050565 | -0.033861 | -0.051022 | -0.041033 | -0.0021057 | -0.018186 | 0.0562 | 0.043699 | -0.21979 | -0.015992 | -0.022612 | -0.12817 | 0.1236 | -0.13733 | -0.15106 | -0.009155 | -0.13733 | -0.068665 | 0.52643 | 116.4917 | -5.8502 | 116.2766 | -5.6625 | -5.7495 | -5.6946 | 5.6671 | -115.9698 | -116.2445 | 5.7953 | 5.7358 | 5.6671 | 0.068664 | 0 | -0.045777 | 0.39825 | 0.1831 | 0.14191 | 0.10986 | 0.054931 | 0.15564 | 0.10071 | 0.12817 | -0.013733 | 0.18768 | 122.1268 | 0.26093 | 122.3419 | 5.928 | 122.2961 | -116.2308 | -121.9437 | 5.6534 | 122.081 | 5.6763 | 6.3309
1395.0938 | 122.4792 | -5.484 | 116.478 | 0.0025177 | -0.013729 | -0.08136 | -0.0031337 | -0.02788 | -0.049954 | -0.04146 | 0.00094606 | -0.01904 | 0.057054 | 0.045194 | -0.21744 | -0.015565 | -0.023894 | -0.068665 | 0.09613 | -0.086975 | -0.045776 | 0.1236 | -0.068665 | -0.004578 | 0.59052 | 116.8076 | -5.5252 | 116.8396 | -5.2917 | -5.3513 | -5.3146 | 5.397 | -116.3818 | -116.5237 | 5.6076 | 5.4794 | 5.4153 | 0.082397 | 0.01831 | -0.041199 | 0.32959 | 0.36163 | 0.19226 | 0.16937 | 0.13275 | 0.21057 | 0.17395 | 0.21057 | 0.041199 | 0.23346 | 122.3648 | 0.1831 | 122.3328 | 5.5801 | 122.2916 | -116.5649 | -122.0032 | 5.4382 | 122.3236 | 5.4153 | 6.0745
1396.875 | 121.962 | -5.1132 | 116.89 | -0.10429 | -0.021847 | -0.080719 | -0.0044155 | -0.03258 | -0.050381 | -0.041887 | 0.00094606 | -0.020963 | 0.054705 | 0.047544 | -0.21766 | -0.018769 | -0.022826 | -0.10071 | 0.11444 | -0.13733 | -0.13275 | -0.018311 | -0.13275 | -0.073242 | 0.55847 | 117.1555 | -5.2094 | 116.6885 | -4.9896 | -5.072 | -5.0125 | 4.9759 | -116.7755 | -117.0227 | 5.0949 | 5.04 | 4.9805 | 0.064087 | 0.004578 | -0.096131 | 0.2655 | -0.20142 | 0.1236 | 0.10071 | 0.041199 | 0.19684 | 0.13733 | 0.11902 | 0.004578 | 0.21973 | 121.8979 | 0.25177 | 122.3648 | 5.2277 | 122.2687 | -117.0273 | -122.0993 | 4.9805 | 121.8018 | 5.0125 | 5.6717
1398.5938 | 121.9208 | -4.8843 | 117.5537 | -0.6002 | -0.014584 | -0.082428 | -0.0052701 | -0.030016 | -0.048245 | -0.03911 | 0.0039979 | -0.018827 | 0.056841 | 0.042631 | -0.21915 | -0.014924 | -0.021544 | -0.082397 | 0.086975 | -0.11902 | -0.091553 | 0.045776 | -0.091553 | -0.027466 | 0.59509 | 117.4072 | -4.9301 | 117.4026 | -4.7287 | -4.7974 | -4.7882 | 4.7653 | -117.4667 | -117.6453 | 4.9301 | 4.8569 | 4.7928 | 0.091553 | 0.027466 | -0.045777 | -0.14648 | -0.15106 | 0.15564 | 0.09613 | 0.086975 | 0.14191 | 0.13275 | 0.16479 | 0.027466 | 0.20142 | 122.3328 | 0.20599 | 122.3373 | 4.9713 | 122.2916 | -117.6727 | -122.4838 | 4.7928 | 122.287 | 4.8019 | 5.4794
1400.2969 | 122.4838 | -4.8477 | 117.5766 | 0.16274 | -0.013943 | -0.079224 | -0.0035611 | -0.034075 | -0.047604 | -0.039751 | -0.0021057 | -0.019895 | 0.057909 | 0.043485 | -0.21766 | -0.015778 | -0.02603 | -0.10529 | 0.064087 | -0.13275 | -0.086975 | 0.050354 | -0.082397 | -0.018311 | 0.59509 | 117.4667 | -4.8843 | 117.5034 | -4.6326 | -4.6921 | -4.66 | 4.715 | -117.5125 | -117.6636 | 4.8981 | 4.8294 | 4.7653 | 0.11444 | 0.050354 | -0.036621 | -0.10986 | -0.073242 | 0.21515 | 0.18768 | 0.15564 | 0.2243 | 0.19226 | 0.18311 | 0.045776 | 0.25177 | 122.3877 | 0.19684 | 122.3511 | 4.9118 | 122.3145 | -117.7094 | -122.4609 | 4.7607 | 122.3511 | 4.7424 | 5.4428
1402.0781 | 122.5021 | -4.5776 | 117.8101 | 0.15511 | -0.015438 | -0.080292 | -0.0054837 | -0.034929 | -0.052517 | -0.039751 | 0.0039979 | -0.020108 | 0.055773 | 0.03964 | -0.21787 | -0.016419 | -0.024535 | -0.10071 | 0.059509 | -0.13733 | -0.064087 | 0.068665 | -0.064087 | 0.009155 | 0.62714 | 117.746 | -4.6555 | 117.7826 | -4.3533 | -4.3991 | -4.3945 | 4.4403 | -117.7505 | -117.8741 | 4.6463 | 4.5868 | 4.5136 | 0.14648 | 0.073242 | -0.07782 | -0.064087 | -0.027466 | 0.2243 | 0.18311 | 0.17853 | 0.26093 | 0.25635 | 0.20599 | 0.073242 | 0.30212 | 122.4381 | 0.19684 | 122.4014 | 4.6371 | 122.3236 | -117.9474 | -122.4655 | 4.5136 | 122.3602 | 4.4769 | 5.2048
1403.8594 | 122.0032 | -4.7928 | 117.2287 | -0.27214 | 0.014896 | 0.034851 | -0.013815 | -0.036211 | -0.060635 | 0.0175 | 0.00094606 | -0.031003 | 0.052141 | 0.032377 | -0.22513 | -0.040345 | -0.03073 | -0.091553 | 0.07782 | -0.15564 | -0.10529 | 0.041199 | -0.12817 | -0.073242 | 0.68207 | 117.3981 | -4.9667 | 116.8762 | -4.7333 | -4.8065 | -4.7333 | 4.6371 | -117.1509 | -117.334 | 4.834 | 4.7195 | 4.6646 | 0.082398 | 0.027466 | -0.17395 | 0.16937 | -0.35248 | 0.05951 | 0.05951 | -0.013733 | 0.23346 | 0.16022 | 0.19684 | 0.050354 | 0.23346 | 121.843 | 0.23346 | 122.3648 | 4.8706 | 122.1909 | -117.3843 | -122.1954 | 4.6875 | 121.669 | 4.7012 | 5.4749
1405.6406 | 121.7926 | -5.6625 | 116.4917 | -0.043259 | 0.012973 | 0.032501 | -0.0054837 | -0.031725 | 0.018192 | 0.016005 | 0.00094606 | -0.02139 | 0.04146 | 0.04434 | -0.21766 | -0.029023 | -0.026457 | -0.12817 | 0.068665 | -0.17853 | -0.16937 | -0.041199 | -0.21515 | -0.16479 | 0.52643 | 116.5787 | -5.7266 | 116.0065 | -5.5756 | -5.6534 | -5.571 | 5.484 | -116.423 | -116.6611 | 5.6213 | 5.4977 | 5.4474 | 0.013733 | -0.036621 | -0.064087 | 0.086975 | -0.48523 | 0.086975 | 0.091553 | 0.009156 | 0.15564 | 0.073243 | 0.13733 | 0.009155 | 0.15106 | 121.7331 | 0.24719 | 122.3053 | 5.7312 | 122.2412 | -116.6702 | -122.2183 | 5.4932 | 121.669 | 5.5344 | 6.189
1407.4219 | 122.3694 | -5.4703 | 116.9449 | 0.0025177 | -0.011807 | -0.079865 | -0.0042019 | -0.029162 | -0.049954 | -0.038042 | 0.00094606 | -0.018827 | 0.056841 | 0.040494 | -0.21723 | -0.013856 | -0.02368 | -0.13275 | 0.054932 | -0.17395 | -0.11902 | 0.032043 | -0.13733 | -0.068665 | 0.60883 | 116.8671 | -5.5435 | 116.922 | -5.2643 | -5.3421 | -5.2643 | 5.2963 | -116.89 | -117.0639 | 5.5023 | 5.4016 | 5.3329 | 0.10528 | 0.036621 | -0.073242 | -0.07782 | -0.022888 | 0.20599 | 0.20599 | 0.12817 | 0.27924 | 0.20142 | 0.20599 | 0.054931 | 0.27924 | 122.4655 | 0.22888 | 122.4106 | 5.5252 | 122.3373 | -117.1188 | -122.4884 | 5.3513 | 122.3923 | 5.3375 | 6.0791
1409.1406 | 121.6919 | -5.2368 | 116.5604 | 0.010147 | -0.016079 | 0.032287 | -0.0048427 | -0.049456 | 0.017551 | 0.016005 | 0.00094606 | -0.023526 | 0.049791 | 0.036436 | -0.22513 | -0.032013 | -0.032439 | -0.14191 | 0.054932 | -0.17395 | -0.11902 | 0.041199 | -0.16022 | -0.10529 | 0.65002 | 116.684 | -5.3146 | 116.3635 | -5.1132 | -5.1956 | -5.1453 | 5.0629 | -116.5054 | -116.6794 | 5.278 | 5.1315 | 5.0766 | 0.068664 | 0.013733 | -0.07782 | 0.1236 | -0.19684 | 0.1236 | 0.091552 | 0.041198 | 0.16937 | 0.11902 | 0.21515 | 0.054931 | 0.20142 | 121.6782 | 0.22888 | 121.9986 | 5.2917 | 121.9208 | -116.7343 | -121.875 | 5.1178 | 121.6003 | 5.0949 | 5.8868
1410.9375 | 122.5479 | -4.985 | 117.3111 | -0.0051118 | -0.013943 | -0.081147 | -0.0069791 | -0.031298 | -0.050167 | -0.038896 | 0.00094606 | -0.02139 | 0.055773 | 0.040281 | -0.2183 | -0.015137 | -0.023894 | -0.10529 | -0.004578 | -0.1831 | -0.07782 | 0.15106 | -0.064087 | -0.018311 | 0.74158 | 117.3157 | -5.04 | 117.421 | -4.7241 | -4.8065 | -4.7836 | 4.8019 | -117.3157 | -117.3889 | 5.1361 | 4.9667 | 4.921 | 0.16479 | 0.11902 | -0.054932 | 0.004578 | 0.10986 | 0.26092 | 0.20142 | 0.17853 | 0.25635 | 0.23346 | 0.33417 | 0.10528 | 0.31586 | 122.4609 | 0.17853 | 122.3557 | 4.9805 | 122.3007 | -117.4942 | -122.3511 | 4.9072 | 122.406 | 4.8798 | 5.7266
1412.7188 | 121.6507 | -5.1819 | 116.6977 | -0.0051118 | -0.028897 | 0.031433 | -0.0067653 | -0.046465 | -0.05679 | 0.0175 | 0.00094606 | -0.022245 | 0.046801 | 0.036008 | -0.2183 | -0.024964 | -0.024107 | -0.16022 | 0.041199 | -0.2243 | -0.23346 | -0.054932 | -0.25635 | -0.18768 | 0.55847 | 116.8991 | -5.2185 | 116.5283 | -5.0537 | -5.1361 | -5.0674 | 4.9576 | -116.6565 | -116.9312 | 5.127 | 4.9942 | 4.9255 | 0.036621 | -0.032044 | -0.036621 | 0.20142 | -0.16937 | 0.12817 | 0.11444 | 0.045777 | 0.15106 | 0.082398 | 0.16937 | -0.009155 | 0.16479 | 121.7468 | 0.2655 | 122.1176 | 5.2231 | 122.081 | -116.922 | -121.9162 | 4.9484 | 121.7102 | 5.0217 | 5.7404
1414.4531 | 122.4701 | -5.0903 | 117.2333 | -0.0051118 | -0.010739 | -0.07837 | -0.0071927 | -0.031725 | -0.049954 | -0.042528 | 0.00094606 | -0.020963 | 0.056841 | 0.041776 | -0.21915 | -0.016419 | -0.022185 | -0.16022 | -0.018311 | -0.19226 | -0.16479 | 0.036621 | -0.17395 | -0.082397 | 0.58136 | 117.2699 | -5.1086 | 117.2791 | -4.8843 | -4.9393 | -4.9164 | 4.8981 | -117.2516 | -117.3981 | 5.127 | 5.0079 | 4.9164 | 0.10986 | 0.018311 | -0.018311 | 0.036621 | 0.045777 | 0.20599 | 0.17395 | 0.15106 | 0.19226 | 0.16937 | 0.22888 | 0.027466 | 0.22431 | 122.3877 | 0.17395 | 122.3785 | 5.072 | 122.3602 | -117.4255 | -122.3419 | 4.9255 | 122.3694 | 4.9301 | 5.6717
1416.2344 | 122.4838 | -4.7745 | 117.6224 | -0.0051118 | -0.013302 | -0.080719 | -0.0046291 | -0.029162 | -0.050381 | -0.039537 | 0.0039979 | -0.021817 | 0.058977 | 0.038145 | -0.21894 | -0.015992 | -0.024535 | -0.13733 | -0.013733 | -0.19684 | -0.15564 | 0.032043 | -0.16479 | -0.091553 | 0.59967 | 117.5491 | -4.8157 | 117.5766 | -4.5822 | -4.6417 | -4.6326 | 4.5776 | -117.6361 | -117.778 | 4.8065 | 4.6829 | 4.6097 | 0.10529 | 0.032043 | -0.041199 | -0.073242 | -0.045776 | 0.19226 | 0.14191 | 0.13275 | 0.18311 | 0.17395 | 0.22888 | 0.041198 | 0.23346 | 122.3923 | 0.18311 | 122.3648 | 4.7607 | 122.3236 | -117.8192 | -122.438 | 4.6188 | 122.3511 | 4.6371 | 5.3741
1418.0312 | 121.6919 | -4.5685 | 117.5949 | -0.26451 | 0.014042 | 0.032073 | -0.0056973 | -0.04796 | 0.017338 | -0.050859 | 0.0039979 | -0.021176 | 0.046373 | 0.044767 | -0.21338 | -0.018769 | -0.02368 | -0.15106 | 0.022888 | -0.19226 | -0.21973 | -0.082397 | -0.2655 | -0.18768 | 0.59509 | 117.8604 | -4.5868 | 117.4805 | -4.4266 | -4.5136 | -4.4449 | 4.3762 | -117.572 | -117.8146 | 4.4861 | 4.3808 | 4.303 | 0.004578 | -0.073242 | -0.018311 | 0.2655 | -0.11444 | 0.14191 | 0.1236 | 0.054931 | 0.14191 | 0.073242 | 0.10986 | -0.027466 | 0.16022 | 122.0673 | 0.21515 | 122.4472 | 4.5914 | 122.4289 | -117.7872 | -122.1817 | 4.3488 | 122.049 | 4.4174 | 5.1636
1419.8125 | 121.9666 | -4.1107 | 118.3868 | -0.34843 | -0.015652 | -0.07837 | -0.0031337 | -0.031725 | -0.049526 | -0.038256 | 0.00094606 | -0.017972 | 0.056414 | 0.046903 | -0.21915 | -0.014924 | -0.026671 | -0.16937 | 0.050354 | -0.21057 | -0.20599 | -0.045776 | -0.23804 | -0.16022 | 0.60425 | 118.2587 | -4.1336 | 118.1305 | -3.9459 | -4.0329 | -3.9734 | 3.9001 | -118.3365 | -118.5928 | 4.0649 | 3.9505 | 3.8727 | 0.050354 | -0.027466 | -0.022888 | -0.12817 | -0.25635 | 0.1648 | 0.13733 | 0.07782 | 0.16022 | 0.10071 | 0.1648 | 0.004577 | 0.18768 | 122.2641 | 0.26093 | 122.3923 | 4.1611 | 122.3694 | -118.5974 | -122.5204 | 3.9047 | 122.2412 | 3.9413 | 4.715
1421.5312 | 122.5479 | -3.8727 | 118.5242 | 0.010147 | -0.013943 | -0.079651 | -0.0078335 | -0.028521 | -0.04974 | -0.041033 | 0.00094606 | -0.019895 | 0.054277 | 0.045835 | -0.21915 | -0.015778 | -0.020049 | -0.13733 | 0.009155 | -0.14648 | -0.091553 | 0.10529 | -0.082397 | -0.018311 | 0.75989 | 118.483 | -3.9459 | 118.5287 | -3.598 | -3.6575 | -3.6575 | 3.7262 | -118.515 | -118.6157 | 3.978 | 3.8544 | 3.7903 | 0.12817 | 0.064087 | -0.073242 | -0.041199 | 0.004578 | 0.27466 | 0.21515 | 0.21515 | 0.28839 | 0.28839 | 0.25177 | 0.054931 | 0.3479 | 122.4747 | 0.15564 | 122.4289 | 3.8818 | 122.3557 | -118.6707 | -122.4701 | 3.7811 | 122.4014 | 3.7354 | 4.6326
1423.3125 | 121.9437 | -3.9047 | 118.6295 | -0.29503 | -0.01437 | -0.082001 | -0.0044155 | -0.032366 | -0.051449 | -0.040392 | 0.0039979 | -0.018613 | 0.055986 | 0.04498 | -0.21808 | -0.015565 | -0.020476 | -0.1831 | 0.064087 | -0.21057 | -0.23346 | -0.050354 | -0.19684 | -0.14648 | 0.6546 | 118.4784 | -3.9459 | 118.3044 | -3.7308 | -3.7994 | -3.772 | 3.6942 | -118.5654 | -118.8629 | 3.8544 | 3.7582 | 3.7079 | 0.064087 | 0.013733 | -0.041199 | -0.15106 | -0.32501 | 0.17395 | 0.13275 | 0.10529 | 0.17395 | 0.14649 | 0.16022 | -0.022888 | 0.21515 | 122.2504 | 0.27466 | 122.4243 | 3.9688 | 122.3831 | -118.84 | -122.5754 | 3.6713 | 122.2092 | 3.7216 | 4.5593
1425.0312 | 122.4335 | -3.8956 | 118.4372 | 0.010147 | -0.012448 | -0.079011 | -0.0065517 | -0.03322 | -0.050808 | -0.039751 | 0.00094606 | -0.018186 | 0.055773 | 0.044553 | -0.21787 | -0.013428 | -0.02603 | -0.10529 | -0.004578 | -0.1831 | -0.10071 | 0.073242 | -0.091553 | -0.054932 | 0.74616 | 118.4875 | -3.9047 | 118.5013 | -3.6484 | -3.717 | -3.6987 | 3.7125 | -118.4418 | -118.5379 | 3.9688 | 3.8406 | 3.804 | 0.12817 | 0.091552 | -0.009155 | 0.050354 | 0.064087 | 0.24719 | 0.19684 | 0.17853 | 0.20599 | 0.18768 | 0.25635 | 0.082397 | 0.25635 | 122.406 | 0.17853 | 122.3923 | 3.891 | 122.3831 | -118.6203 | -122.3419 | 3.7949 | 122.3969 | 3.7903 | 4.6417
1426.7969 | 121.6965 | -56.3004 | 65.1352 | -0.0051118 | -0.018429 | -0.082215 | 7.0482e-05 | -0.034075 | -0.049954 | -0.040605 | 0.0070497 | -0.019895 | 0.059404 | 0.04498 | -0.22001 | -0.015778 | -0.025176 | -2.7603 | -2.5406 | -2.7832 | -2.7786 | -1.5976 | -2.8015 | -2.7191 | -3.3417 | 65.5472 | -56.1493 | 65.2496 | -56.3507 | -56.3919 | -56.3873 | 53.5172 | -67.6758 | -67.9138 | 54.7028 | 53.5812 | 53.4988 | 0.064087 | -0.018311 | 0.15106 | 0.41199 | 0.11444 | -0.050354 | -0.086975 | -0.091553 | -0.23804 | -0.24262 | 1.1856 | 0.004578 | -0.20142 | 121.3989 | 0.24261 | 121.6965 | 53.7598 | 121.8475 | -67.9184 | -121.2845 | 53.5217 | 121.55 | 53.54 | 52.9587
1428.5938 | 121.7468 | -61.4685 | 60.0998 | -0.012741 | -0.010311 | -0.083924 | -0.011465 | 0.013563 | 0.01926 | -0.076708 | -0.0021057 | -0.023954 | 0.047869 | 0.046689 | -0.21915 | -0.029236 | -0.024107 | -0.086975 | 0.091553 | -0.13733 | -0.11444 | 0.004578 | -0.15564 | -0.082397 | -1.2589 | 60.0311 | -61.409 | 59.9167 | -61.5555 | -61.7569 | -61.3083 | 61.3312 | -60.0082 | -60.2142 | 61.4731 | 61.3861 | 61.3129 | 0.054932 | -0.018311 | 0.059509 | -0.068664 | -0.1831 | -0.086975 | 0.16022 | -0.28839 | 0.10071 | -0.3479 | 0.14191 | 0.022888 | -0.14648 | 121.3257 | 0.22888 | 121.4401 | 61.5601 | 121.4996 | -60.2371 | -121.5088 | 61.3541 | 121.3852 | 61.3815 | 60.2097
1430.3281 | 121.5134 | -53.8513 | 67.1585 | 0.0025177 | -0.010098 | -0.094391 | -0.0086879 | -0.044115 | 0.020756 | 0.016005 | -0.0021057 | -0.022031 | 0.048723 | 0.044126 | -0.22086 | -0.026459 | -0.030302 | -0.10529 | 0.11902 | -0.13275 | -0.12817 | -0.013733 | -0.16479 | -0.10071 | 0.37537 | 70.047 | -50.9811 | 67.9001 | -53.9017 | -54.3274 | -54.2496 | 53.7186 | -67.0395 | -67.2867 | 53.8376 | 53.7506 | 53.6865 | 0.032043 | -0.032044 | 2.8702 | 2.8885 | 0.74158 | -0.050354 | -0.39825 | -0.47608 | -3.2684 | -3.3463 | 0.11902 | 0.004577 | -2.9205 | 118.8812 | 0.25177 | 121.0281 | 53.9703 | 123.8983 | -67.2913 | -118.1396 | 53.7231 | 121.7514 | 53.746 | 54.2267
1432.1094 | 119.4031 | -80.4977 | 38.9145 | 0.0025177 | -0.016079 | -0.077088 | -0.0076199 | -0.03023 | -0.051663 | -0.040392 | 0.00094606 | -0.020963 | 0.055986 | 0.04498 | -0.21744 | -0.015565 | -0.020476 | -0.16479 | 0.10071 | -0.14191 | -0.17395 | -0.009155 | -0.13275 | -0.073242 | -3.2272 | 39.3173 | -80.8044 | 39.7705 | -79.1061 | -81.0608 | -81.3126 | 80.3558 | -38.8138 | -39.0884 | 80.4886 | 80.4245 | 80.365 | 0.068665 | 0.009156 | -0.3067 | 0.40283 | 0.85602 | 1.3916 | -0.81482 | -0.56305 | -0.50812 | -0.25635 | 0.13275 | -0.032043 | 1.6983 | 120.575 | 0.24262 | 120.1218 | 80.5984 | 119.8151 | -39.0564 | -119.7189 | 80.3238 | 120.2682 | 80.3329 | 77.2705
1433.8281 | 121.0281 | -66.7511 | 54.0894 | 0.0025177 | -0.013089 | -0.07602 | -0.010397 | -0.044115 | -0.050595 | -0.055132 | -0.0021057 | -0.031858 | 0.053636 | 0.030881 | -0.2435 | 0.011352 | 0.010072 | -0.1236 | 0.10071 | -0.13275 | -0.09613 | 0.032043 | -0.11444 | -0.050354 | -3.1815 | 52.5787 | -67.4286 | 53.6224 | -66.7465 | -66.0965 | -65.7532 | 66.6183 | -53.9886 | -54.1855 | 66.7831 | 66.7007 | 66.6367 | 0.082397 | 0.01831 | -0.67749 | -1.5106 | -0.46692 | 0.004578 | 0.99792 | 0.6546 | 1.6754 | 1.3321 | 0.16479 | 0.036621 | 0.68207 | 121.051 | 0.23346 | 120.0073 | 66.8518 | 119.3298 | -54.2221 | -121.5179 | 66.655 | 120.3735 | 66.6275 | 63.5696
1435.625 | 121.3028 | -63.6246 | 57.3578 | 0.0025177 | -0.010952 | -0.075806 | -0.0048427 | -0.033007 | -0.05444 | -0.040605 | 0.00094606 | -0.022672 | 0.054491 | 0.043699 | -0.23111 | -0.032441 | -0.031157 | -0.1236 | 0.086975 | -0.14191 | -0.14191 | -0.009155 | -0.12817 | -0.07782 | -1.1307 | 57.486 | -63.0981 | 57.9208 | -63.6978 | -63.9221 | -63.5376 | 63.4827 | -57.2708 | -57.4997 | 63.6154 | 63.5468 | 63.4964 | 0.064087 | 0.013733 | 0.52643 | 0.12817 | 0.56305 | -0.073242 | 0.086975 | -0.29755 | -0.43945 | -0.82397 | 0.13275 | 0 | -0.59967 | 121.019 | 0.22888 | 120.5841 | 63.7115 | 121.1105 | -57.4997 | -120.4559 | 63.4827 | 121.5454 | 63.501 | 62.4939
1437.3594 | 121.312 | -120.0439 | 0.82855 | -0.0051118 | -0.014798 | -0.076661 | -0.0042019 | -0.03322 | -0.051876 | -0.039751 | 0.0039979 | -0.022672 | 0.053209 | 0.048398 | -0.21744 | -0.018342 | -0.020262 | -0.16479 | 0.050354 | -0.14648 | -0.10071 | 0.07782 | -0.07782 | -0.004578 | -3.7445 | 0.83771 | -120.2271 | 0.8194 | -119.696 | -119.9387 | -119.7006 | 119.8975 | -0.7782 | -0.92926 | 120.1218 | 120.0394 | 119.9661 | 0.14191 | 0.068664 | -0.18311 | 0.009156 | -0.009155 | 0.3479 | 0.34332 | 0.10528 | 0.52643 | 0.28839 | 0.2243 | 0.045776 | 0.53101 | 121.0464 | 0.19684 | 121.0648 | 120.0943 | 120.8817 | -0.97504 | -121.0556 | 119.9432 | 120.8633 | 119.8791 | 116.2994
1439.1406 | 121.4539 | -120.3644 | 0.84686 | -0.0051118 | -0.0096707 | -0.07837 | -0.0022793 | -0.033648 | -0.051449 | -0.036547 | 0.0039979 | -0.019895 | 0.054918 | 0.044767 | -0.21531 | -0.013215 | -0.020476 | -0.16479 | 0.059509 | -0.16022 | -0.20142 | -0.054932 | -0.19684 | -0.11444 | -3.6484 | 0.87433 | -120.4514 | 0.80109 | -120.0302 | -120.282 | -119.9661 | 120.2042 | -0.78735 | -1.0483 | 120.3094 | 120.2499 | 120.1675 | 0.045776 | -0.036621 | -0.086975 | 0.027466 | -0.045777 | 0.33417 | 0.39825 | 0.082398 | 0.48523 | 0.16937 | 0.10528 | -0.041199 | 0.42114 | 121.2524 | 0.21973 | 121.3257 | 120.4239 | 121.2387 | -1.0071 | -121.2982 | 120.163 | 121.1655 | 120.1996 | 116.716
1440.875 | 121.5866 | -120.3598 | 0.92468 | -0.0051118 | -0.015866 | -0.080506 | -0.0035611 | -0.031511 | -0.053799 | -0.039537 | 0.0070497 | -0.020536 | 0.052782 | 0.048826 | -0.21915 | -0.016633 | -0.01599 | -0.091553 | 0.027466 | -0.13733 | -0.068665 | 0.10529 | -0.027466 | 0.018311 | -3.4744 | 0.92468 | -120.4147 | 0.93384 | -119.9112 | -120.1492 | -119.902 | 120.2225 | -0.89722 | -0.99335 | 120.4651 | 120.3781 | 120.3323 | 0.15564 | 0.10986 | -0.054932 | 0 | 0.009155 | 0.44861 | 0.45776 | 0.21057 | 0.51269 | 0.2655 | 0.24262 | 0.068664 | 0.50354 | 121.3486 | 0.16479 | 121.3394 | 120.3873 | 121.2845 | -1.062 | -121.3394 | 120.2911 | 121.2936 | 120.2682 | 116.8854
1442.6562 | 121.463 | -120.1401 | 1.3275 | 0.0025177 | -0.016293 | -0.082001 | -0.0027065 | -0.027239 | -0.052731 | -0.039537 | -0.0051575 | -0.02139 | 0.057695 | 0.047971 | -0.21659 | -0.014496 | -0.023894 | -0.17853 | 0.059509 | -0.17395 | -0.1831 | -0.059509 | -0.16479 | -0.11444 | -3.5843 | 1.3458 | -120.1218 | 1.1581 | -119.7418 | -119.9936 | -119.7189 | 119.9661 | -1.268 | -1.5106 | 120.0806 | 120.0256 | 119.9753 | 0.059509 | 0.009155 | 0.018311 | 0.01831 | -0.16937 | 0.39825 | 0.42114 | 0.14648 | 0.40283 | 0.12817 | 0.11444 | -0.009155 | 0.37994 | 121.2799 | 0.23346 | 121.4676 | 120.1996 | 121.4859 | -1.5015 | -121.4493 | 119.957 | 121.2982 | 119.9615 | 116.5558
1444.3906 | 121.5454 | -119.9158 | 1.506 | -0.0051118 | -0.010098 | -0.079865 | -0.00057032 | -0.028948 | -0.051449 | -0.039965 | 0.00094606 | -0.020536 | 0.054705 | 0.054807 | -0.21787 | -0.015351 | -0.022398 | -0.15564 | 0.068665 | -0.17395 | -0.18768 | -0.054932 | -0.19684 | -0.10529 | -3.5797 | 1.5198 | -119.9341 | 1.4465 | -119.5084 | -119.783 | -119.4809 | 119.7418 | -1.4374 | -1.6937 | 119.8608 | 119.8105 | 119.7189 | 0.068664 | -0.022888 | -0.018311 | 0.013733 | -0.059509 | 0.40741 | 0.43488 | 0.13275 | 0.45319 | 0.15106 | 0.11902 | -0.013733 | 0.42572 | 121.3806 | 0.24261 | 121.4539 | 119.9844 | 121.4355 | -1.68 | -121.4401 | 119.7281 | 121.3623 | 119.7601 | 116.3361
1446.1562 | 121.6415 | -119.7464 | 1.6479 | -0.0051118 | -0.011166 | -0.076447 | -0.0037747 | -0.028307 | -0.04974 | -0.040392 | 0.00094606 | -0.020536 | 0.054277 | 0.044767 | -0.21787 | -0.015351 | -0.024107 | -0.068665 | 0.041199 | -0.13733 | -0.082397 | 0.059509 | -0.10529 | -0.027466 | -3.4927 | 1.6571 | -119.7784 | 1.6846 | -119.2932 | -119.577 | -119.2657 | 119.6091 | -1.6068 | -1.7303 | 119.8059 | 119.7189 | 119.6411 | 0.10986 | 0.032043 | -0.032043 | 0.009155 | 0.036621 | 0.45319 | 0.48065 | 0.16937 | 0.51269 | 0.20142 | 0.19684 | 0.054932 | 0.48523 | 121.463 | 0.17853 | 121.4355 | 119.7876 | 121.4035 | -1.7853 | -121.4264 | 119.664 | 121.431 | 119.6777 | 116.2537
1447.9375 | 121.6187 | -118.2312 | 3.2043 | 0.0025177 | -0.014584 | -0.079011 | -0.0054837 | -0.027666 | -0.049099 | -0.038256 | 0.0039979 | -0.023099 | 0.054277 | 0.045835 | -0.21808 | -0.015137 | -0.019194 | -0.14648 | 0.050354 | -0.14191 | -0.12817 | 0.009155 | -0.12817 | -0.050354 | -3.5339 | 3.2227 | -118.2861 | 3.1494 | -117.8284 | -118.0847 | -117.8055 | 118.0893 | -3.154 | -3.3325 | 118.2404 | 118.1808 | 118.103 | 0.091553 | 0.013733 | -0.054932 | 0.01831 | -0.054932 | 0.40283 | 0.42572 | 0.14648 | 0.48065 | 0.20142 | 0.15106 | 0.013733 | 0.45776 | 121.4355 | 0.19226 | 121.5088 | 118.2816 | 121.4539 | -3.3463 | -121.4905 | 118.103 | 121.3806 | 118.0847 | 114.6973
1449.6562 | 121.6507 | -117.9565 | 3.5385 | 0.0025177 | -0.0086027 | -0.075593 | -0.0031337 | -0.031298 | -0.051663 | -0.042528 | 0.00094606 | -0.022885 | 0.053209 | 0.047544 | -0.2168 | -0.012787 | -0.01898 | -0.082397 | 0.032043 | -0.13733 | -0.068665 | 0.082397 | -0.091553 | -0.022888 | -3.4241 | 3.511 | -117.9657 | 3.5202 | -117.5125 | -117.7734 | -117.4942 | 117.8192 | -3.5065 | -3.6072 | 118.0389 | 117.9337 | 117.865 | 0.11444 | 0.045776 | -0.009155 | -0.027466 | -0.01831 | 0.44403 | 0.46234 | 0.18311 | 0.4715 | 0.19226 | 0.21973 | 0.068664 | 0.45319 | 121.4859 | 0.16937 | 121.4767 | 117.9886 | 121.4676 | -3.6758 | -121.5042 | 117.8879 | 121.4767 | 117.8741 | 114.5325
1451.4375 | 121.5866 | -115.5991 | 5.9647 | 0.0025177 | -0.01138 | -0.078583 | -0.0012111 | -0.02553 | -0.049526 | -0.041033 | 0.00094606 | -0.019895 | 0.055773 | 0.046903 | -0.21937 | -0.02475 | -0.02368 | -0.10986 | 0.073242 | -0.15106 | -0.15106 | -0.013733 | -0.16022 | -0.09613 | -3.3508 | 5.9601 | -115.6036 | 5.8502 | -115.2237 | -115.4892 | -115.2008 | 115.448 | -5.8914 | -6.1157 | 115.5853 | 115.5029 | 115.4388 | 0.054932 | -0.009155 | -0.004578 | -0.004578 | -0.11444 | 0.37537 | 0.39825 | 0.10986 | 0.40283 | 0.11444 | 0.13733 | 0 | 0.37994 | 121.4539 | 0.2243 | 121.5637 | 115.6723 | 121.5591 | -6.1157 | -121.5683 | 115.448 | 121.4493 | 115.4892 | 112.2482
1453.1562 | 121.6049 | -120.3552 | 1.2314 | 0.010147 | -0.015866 | -0.079438 | -0.0039883 | -0.032793 | -0.051235 | -0.040819 | 0.0039979 | -0.02139 | 0.056841 | 0.045408 | -0.21637 | -0.013856 | -0.024962 | -0.11902 | 0.064087 | -0.15106 | -0.16022 | -0.009155 | -0.13733 | -0.086975 | -3.6118 | 1.2222 | -120.4056 | 1.0345 | -119.9707 | -120.2454 | -119.9936 | 120.2042 | -1.1673 | -1.3916 | 120.3461 | 120.2683 | 120.2179 | 0.064087 | 0.013733 | -0.050354 | -0.009155 | -0.19684 | 0.38452 | 0.36163 | 0.10986 | 0.41199 | 0.16022 | 0.14191 | -0.009155 | 0.43488 | 121.4401 | 0.21515 | 121.6278 | 120.4193 | 121.5775 | -1.3824 | -121.637 | 120.195 | 121.3898 | 120.2362 | 116.7435
1454.9531 | 121.6553 | -120.282 | 1.268 | 0.0025177 | -0.012448 | -0.080506 | -0.0039883 | -0.030871 | -0.050381 | -0.041246 | 0.00094606 | -0.019681 | 0.059191 | 0.046903 | -0.21766 | -0.013642 | -0.023253 | -0.1236 | 0.07782 | -0.16479 | -0.15564 | -0.032043 | -0.15564 | -0.086975 | -3.6118 | 1.2863 | -120.3461 | 1.149 | -119.902 | -120.1767 | -119.8975 | 120.1172 | -1.1902 | -1.4236 | 120.2499 | 120.195 | 120.1263 | 0.07782 | 0.009155 | -0.064087 | 0.018311 | -0.11902 | 0.37994 | 0.38452 | 0.10528 | 0.44861 | 0.16937 | 0.13275 | 0.009155 | 0.44403 | 121.4951 | 0.24261 | 121.6324 | 120.3598 | 121.5683 | -1.4328 | -121.6141 | 120.1263 | 121.431 | 120.1584 | 116.6702
1456.6562 | 121.7194 | -120.2362 | 1.3 | -0.0051118 | -0.013089 | -0.079438 | -0.0042019 | -0.029589 | -0.04739 | -0.03911 | -0.0021057 | -0.022245 | 0.054705 | 0.03964 | -0.21637 | -0.015778 | -0.02368 | -0.10071 | 0.032043 | -0.11902 | -0.10986 | 0.054932 | -0.11902 | -0.022888 | -3.653 | 1.3138 | -120.3094 | 1.2405 | -119.8563 | -120.0943 | -119.8151 | 120.1172 | -1.268 | -1.4099 | 120.2911 | 120.2133 | 120.1172 | 0.096131 | 0 | -0.073242 | 0.013733 | -0.059509 | 0.37994 | 0.42114 | 0.14191 | 0.49439 | 0.21515 | 0.17395 | 0.009156 | 0.45319 | 121.55 | 0.15106 | 121.6232 | 120.2682 | 121.55 | -1.4191 | -121.6095 | 120.1263 | 121.4767 | 120.1355 | 116.5833
1458.4375 | 121.7834 | -120.8176 | 0.73242 | 0.010147 | -0.014798 | -0.080719 | -0.0067653 | -0.032793 | -0.050808 | -0.039751 | 0.0039979 | -0.022672 | 0.057268 | 0.046476 | -0.21787 | -0.01471 | -0.022826 | -0.11444 | 0.045776 | -0.14648 | -0.073242 | 0.073242 | -0.068665 | 0.009155 | -3.598 | 0.737 | -120.8771 | 0.71869 | -120.3552 | -120.6024 | -120.3506 | 120.6711 | -0.68665 | -0.80566 | 120.8908 | 120.8267 | 120.7489 | 0.15564 | 0.077819 | -0.059509 | 0.004578 | -0.013733 | 0.46234 | 0.46692 | 0.21515 | 0.52643 | 0.27466 | 0.21973 | 0.073242 | 0.52185 | 121.5958 | 0.19226 | 121.6141 | 120.8633 | 121.5546 | -0.87891 | -121.6095 | 120.7443 | 121.5363 | 120.7031 | 117.2195
1460.1719 | 121.7834 | -120.9412 | 0.61798 | -0.0051118 | -0.013302 | -0.080292 | -0.0020657 | -0.027025 | -0.046749 | -0.042101 | -0.0021057 | -0.022245 | 0.054491 | 0.051176 | -0.21851 | -0.013856 | -0.021544 | -0.041199 | 0.032043 | -0.12817 | -0.059509 | 0.07782 | -0.091553 | -0.018311 | -3.6118 | 0.62714 | -120.9915 | 0.63629 | -120.4926 | -120.7718 | -120.4697 | 120.813 | -0.58594 | -0.67749 | 121.019 | 120.9229 | 120.8496 | 0.10986 | 0.036621 | -0.050354 | 0.009155 | 0.018311 | 0.44861 | 0.4715 | 0.16937 | 0.52185 | 0.21973 | 0.20599 | 0.068665 | 0.49896 | 121.6278 | 0.16022 | 121.6187 | 120.9732 | 121.5683 | -0.74616 | -121.6095 | 120.8817 | 121.5775 | 120.9 | 117.3294
1461.9531 | 121.669 | -121.0831 | 0.58594 | 0.010147 | -0.015866 | -0.080719 | -0.0069791 | -0.029589 | -0.050595 | -0.039537 | -0.0021057 | -0.01904 | 0.057268 | 0.048185 | -0.21808 | -0.015137 | -0.023467 | -0.16479 | 0.082397 | -0.17853 | -0.19684 | -0.054932 | -0.16937 | -0.11444 | -3.7354 | 0.59967 | -121.138 | 0.3891 | -120.7077 | -120.9824 | -120.6985 | 120.9045 | -0.50354 | -0.78277 | 121.0281 | 120.9686 | 120.9137 | 0.064087 | 0.009155 | -0.054931 | 0.013733 | -0.19684 | 0.37537 | 0.38452 | 0.10071 | 0.43945 | 0.15564 | 0.1236 | -0.01831 | 0.4303 | 121.5271 | 0.26092 | 121.7377 | 121.1655 | 121.6827 | -0.76447 | -121.7239 | 120.8862 | 121.4722 | 120.9183 | 117.3477
1463.7188 | 121.7514 | -121.2433 | 0.3891 | -0.0051118 | -0.013943 | -0.080079 | -0.0063381 | -0.035784 | -0.051449 | -0.038896 | -0.0021057 | -0.019254 | 0.056627 | 0.04498 | -0.21787 | -0.014069 | -0.021544 | -0.091553 | 0.036621 | -0.13733 | -0.064087 | 0.07782 | -0.059509 | 0.004578 | -3.6758 | 0.3891 | -121.2936 | 0.29755 | -120.7901 | -121.0693 | -120.7993 | 121.106 | -0.35248 | -0.45319 | 121.3211 | 121.2479 | 121.1838 | 0.14191 | 0.07782 | -0.050354 | 0 | -0.091553 | 0.45319 | 0.44403 | 0.17395 | 0.49438 | 0.2243 | 0.21515 | 0.073242 | 0.50354 | 121.5912 | 0.17395 | 121.6827 | 121.2799 | 121.6324 | -0.52643 | -121.6827 | 121.1792 | 121.5408 | 121.1517 | 117.5674
1465.4375 | 121.7331 | -121.2753 | 0.40283 | 0.0025177 | -0.011593 | -0.080079 | -0.0014249 | -0.028734 | -0.048886 | -0.042742 | 0.0039979 | -0.018613 | 0.05855 | 0.045408 | -0.21766 | -0.013428 | -0.022185 | -0.14191 | 0.068665 | -0.16937 | -0.16479 | -0.045776 | -0.16937 | -0.10986 | -3.7628 | 0.42114 | -121.344 | 0.2655 | -120.8679 | -121.138 | -120.8496 | 121.106 | -0.33417 | -0.56763 | 121.2296 | 121.1655 | 121.106 | 0.05951 | 0 | -0.068664 | 0.018311 | -0.13733 | 0.40741 | 0.42572 | 0.13733 | 0.49438 | 0.20599 | 0.1236 | 0.004578 | 0.47607 | 121.6095 | 0.23804 | 121.7651 | 121.344 | 121.6965 | -0.57221 | -121.7468 | 121.1105 | 121.5408 | 121.1334 | 117.5125
1467.2031 | 121.701 | -121.2845 | 0.39825 | -0.0051118 | -0.0092435 | -0.077515 | -0.0050565 | -0.029375 | -0.046963 | -0.04146 | 0.00094606 | -0.018827 | 0.055773 | 0.04498 | -0.2168 | -0.013001 | -0.022398 | -0.14191 | 0.073242 | -0.17395 | -0.19684 | -0.10529 | -0.22888 | -0.14648 | -3.8269 | 0.43488 | -121.3577 | 0.2243 | -120.9549 | -121.2296 | -120.9 | 121.1105 | -0.32501 | -0.59509 | 121.1792 | 121.138 | 121.0556 | 0.027466 | -0.054932 | -0.073242 | 0.036621 | -0.17395 | 0.32959 | 0.38452 | 0.054932 | 0.45776 | 0.12817 | 0.068664 | -0.022888 | 0.40283 | 121.582 | 0.24719 | 121.7926 | 121.3577 | 121.7194 | -0.5722 | -121.756 | 121.0876 | 121.5088 | 121.1426 | 117.4576
1468.9844 | 121.7697 | -121.2433 | 0.41657 | -0.0051118 | -0.013943 | -0.079438 | -0.0033475 | -0.035784 | -0.050808 | -0.038896 | 0.00094606 | -0.017972 | 0.055986 | 0.048185 | -0.21723 | -0.014496 | -0.023467 | -0.13733 | 0.073242 | -0.16937 | -0.16479 | -0.041199 | -0.15564 | -0.10071 | -3.7582 | 0.42114 | -121.3623 | 0.27008 | -120.8908 | -121.1655 | -120.845 | 121.0739 | -0.34332 | -0.58136 | 121.2021 | 121.1426 | 121.0876 | 0.068665 | 0.013733 | -0.11902 | 0.004578 | -0.14648 | 0.35248 | 0.39825 | 0.07782 | 0.51727 | 0.19684 | 0.12817 | 0.004578 | 0.4715 | 121.6324 | 0.24261 | 121.7834 | 121.3165 | 121.6644 | -0.58594 | -121.7789 | 121.0785 | 121.5134 | 121.106 | 117.485
1470.7656 | 121.7377 | -121.2753 | 0.43488 | 0.0025177 | -0.0096707 | -0.076661 | -0.0042019 | -0.023821 | -0.049313 | -0.04381 | 0.0039979 | -0.020749 | 0.058763 | 0.043272 | -0.21744 | -0.014069 | -0.022398 | -0.15106 | 0.07782 | -0.14648 | -0.19684 | -0.068665 | -0.23346 | -0.12817 | -3.8727 | 0.43945 | -121.344 | 0.2655 | -120.9503 | -121.2158 | -120.8862 | 121.1288 | -0.35706 | -0.63171 | 121.2067 | 121.1472 | 121.0419 | 0.01831 | -0.086975 | -0.068664 | 0.004578 | -0.16937 | 0.32501 | 0.3891 | 0.05951 | 0.45776 | 0.12817 | 0.077819 | -0.050354 | 0.39368 | 121.6095 | 0.2243 | 121.7834 | 121.3531 | 121.7148 | -0.58136 | -121.7789 | 121.0785 | 121.5408 | 121.1243 | 117.4026
1472.4844 | 121.7239 | -121.2799 | 0.46234 | 0.0025177 | -0.014157 | -0.079438 | -0.0076199 | -0.031939 | -0.048886 | -0.04146 | 0.0039979 | -0.022458 | 0.055132 | 0.045408 | -0.21637 | -0.017701 | -0.019621 | -0.17853 | 0.086975 | -0.16022 | -0.17853 | -0.032043 | -0.16022 | -0.11444 | -3.8498 | 0.45776 | -121.3211 | 0.24719 | -120.9274 | -121.1884 | -120.9045 | 121.1197 | -0.37537 | -0.64087 | 121.2479 | 121.1655 | 121.1197 | 0.045776 | 0 | -0.041199 | -0.004577 | -0.21515 | 0.35248 | 0.37537 | 0.091553 | 0.41657 | 0.13275 | 0.12817 | -0.018311 | 0.39368 | 121.5683 | 0.24719 | 121.7789 | 121.3669 | 121.7377 | -0.62256 | -121.7834 | 121.1014 | 121.5271 | 121.1014 | 117.4301
1474.2656 | 121.875 | -121.2387 | 0.42114 | 0.0025177 | -0.010311 | -0.076661 | -0.0071927 | -0.03023 | -0.047177 | -0.040819 | -0.0021057 | -0.021604 | 0.0562 | 0.041563 | -0.22022 | -0.013642 | -0.024321 | -0.064087 | 0.032043 | -0.12817 | -0.073242 | 0.07782 | -0.091553 | -0.032043 | -3.772 | 0.39368 | -121.2891 | 0.40283 | -120.8176 | -121.0785 | -120.7581 | 121.1105 | -0.3891 | -0.49438 | 121.3165 | 121.2067 | 121.1472 | 0.096131 | 0.036621 | -0.050354 | -0.027466 | -0.018311 | 0.42114 | 0.48065 | 0.16022 | 0.53101 | 0.21057 | 0.20599 | 0.054932 | 0.4715 | 121.6919 | 0.16022 | 121.6827 | 121.2708 | 121.6324 | -0.54932 | -121.7102 | 121.1655 | 121.6415 | 121.1746 | 117.4667
1476 | 121.8887 | -121.2799 | 0.40283 | -0.0051118 | -0.014157 | -0.079438 | -0.0071927 | -0.031511 | -0.049313 | -0.04146 | -0.0021057 | -0.020108 | 0.055559 | 0.041349 | -0.21723 | -0.017487 | -0.018126 | -0.1236 | 0.045776 | -0.14191 | -0.11444 | 0.022888 | -0.12817 | -0.050354 | -3.8818 | 0.3891 | -121.3531 | 0.31586 | -120.8496 | -121.0968 | -120.8359 | 121.138 | -0.35706 | -0.51727 | 121.3028 | 121.2296 | 121.1517 | 0.091553 | 0.013733 | -0.073242 | -0.013733 | -0.086975 | 0.4303 | 0.44403 | 0.1831 | 0.51727 | 0.25635 | 0.16479 | 0.027466 | 0.50354 | 121.669 | 0.18768 | 121.7422 | 121.3257 | 121.669 | -0.54474 | -121.756 | 121.1655 | 121.5958 | 121.1563 | 117.3981
1477.7656 | 121.7651 | -121.344 | 0.46234 | 0.010147 | -0.013516 | -0.081147 | -0.0052701 | -0.033861 | -0.050381 | -0.041246 | 0.00094606 | -0.019895 | 0.055986 | 0.038785 | -0.21894 | -0.01471 | -0.021544 | -0.16479 | 0.059509 | -0.16937 | -0.18768 | -0.054932 | -0.1831 | -0.10071 | -3.9322 | 0.45319 | -121.3852 | 0.21515 | -120.9686 | -121.2158 | -120.9366 | 121.1746 | -0.40283 | -0.65002 | 121.2891 | 121.2433 | 121.1609 | 0.068665 | -0.013732 | -0.041199 | -0.009155 | -0.24719 | 0.37537 | 0.40741 | 0.12817 | 0.44861 | 0.16937 | 0.11444 | -0.01831 | 0.41657 | 121.6003 | 0.22888 | 121.8384 | 121.4035 | 121.7972 | -0.63171 | -121.8475 | 121.1563 | 121.5591 | 121.1792 | 117.4118
1479.4844 | 121.907 | -121.2936 | 0.38452 | 0.0025177 | -0.012661 | -0.080292 | -0.0091153 | -0.031084 | -0.049954 | -0.038896 | 0.0039979 | -0.02139 | 0.055773 | 0.040067 | -0.21872 | -0.014496 | -0.022185 | -0.10071 | 0.027466 | -0.12817 | -0.050354 | 0.11444 | -0.041199 | -0.004578 | -3.8361 | 0.41657 | -121.3577 | 0.36163 | -120.8496 | -121.0968 | -120.8267 | 121.1655 | -0.35706 | -0.43488 | 121.4081 | 121.2891 | 121.2524 | 0.1236 | 0.086975 | -0.064087 | 0.032044 | -0.022888 | 0.44403 | 0.46692 | 0.19684 | 0.53101 | 0.26093 | 0.24262 | 0.07782 | 0.50812 | 121.7194 | 0.15564 | 121.7743 | 121.3211 | 121.7102 | -0.5127 | -121.7422 | 121.2433 | 121.6553 | 121.1929 | 117.4576
1481.2656 | 121.7834 | -121.3257 | 0.42572 | 0.010147 | -0.012448 | -0.078797 | -0.0035611 | -0.028521 | -0.048672 | -0.040178 | 0.0039979 | -0.019254 | 0.057909 | 0.050962 | -0.22193 | -0.013215 | -0.020689 | -0.15564 | 0.09613 | -0.19684 | -0.20599 | -0.064087 | -0.22888 | -0.15106 | -4.0375 | 0.44403 | -121.3943 | 0.2655 | -121.0007 | -121.2845 | -120.9549 | 121.1288 | -0.32959 | -0.63171 | 121.2616 | 121.1746 | 121.0968 | 0.045776 | -0.032044 | -0.068664 | 0.018311 | -0.16022 | 0.32501 | 0.37079 | 0.041199 | 0.43945 | 0.10986 | 0.13275 | -0.009156 | 0.39368 | 121.6599 | 0.29297 | 121.8384 | 121.4218 | 121.7697 | -0.62256 | -121.8201 | 121.1197 | 121.5912 | 121.17 | 117.2882
1482.9844 | 121.9208 | -121.3165 | 0.38452 | 0.0025177 | -0.014157 | -0.080292 | -0.0071927 | -0.028948 | -0.049099 | -0.042101 | 0.00094606 | -0.020749 | 0.057482 | 0.040922 | -0.2168 | -0.014283 | -0.022826 | -0.09613 | 0.036621 | -0.11902 | -0.050354 | 0.11902 | -0.059509 | 0.004578 | -3.923 | 0.39825 | -121.3852 | 0.37994 | -120.8496 | -121.1105 | -120.8405 | 121.1975 | -0.3479 | -0.43488 | 121.4355 | 121.3211 | 121.257 | 0.1236 | 0.05951 | -0.068665 | 0.013733 | -0.004577 | 0.46692 | 0.47607 | 0.20599 | 0.54474 | 0.27466 | 0.23804 | 0.068665 | 0.53558 | 121.7651 | 0.15564 | 121.7834 | 121.3531 | 121.7148 | -0.50354 | -121.7697 | 121.2662 | 121.6965 | 121.2204 | 117.3935
1484.7656 | 121.8521 | -121.0327 | 0.76446 | -0.0051118 | -0.013729 | -0.080933 | -0.0048427 | -0.029802 | -0.048245 | -0.040605 | 0.00094606 | -0.019254 | 0.057695 | 0.055234 | -0.21915 | -0.013215 | -0.026244 | -0.15564 | 0.07782 | -0.17395 | -0.16479 | -0.068665 | -0.16479 | -0.1236 | -4.0695 | 0.76904 | -121.0922 | 0.61798 | -120.639 | -120.9137 | -120.6024 | 120.8588 | -0.68664 | -0.92926 | 120.9641 | 120.9091 | 120.8679 | 0.050354 | 0.009155 | -0.059509 | 0.004578 | -0.14648 | 0.39368 | 0.4303 | 0.11902 | 0.48981 | 0.17853 | 0.10528 | 0.009155 | 0.45319 | 121.7102 | 0.25177 | 121.8613 | 121.1105 | 121.8018 | -0.93841 | -121.8567 | 120.8679 | 121.6507 | 120.8771 | 116.9632
1486.5625 | 121.8246 | -121.0236 | 0.79193 | -0.0051118 | -0.011807 | -0.080292 | -0.0039883 | -0.029162 | -0.049954 | -0.038256 | 0.0039979 | -0.018186 | 0.057482 | 0.049894 | -0.21744 | -0.015351 | -0.024535 | -0.15564 | 0.082397 | -0.1831 | -0.19226 | -0.050354 | -0.1831 | -0.10986 | -4.1107 | 0.79651 | -121.0739 | 0.60425 | -120.6573 | -120.9137 | -120.6207 | 120.8405 | -0.70953 | -0.98419 | 120.9732 | 120.9137 | 120.8405 | 0.073242 | 0 | -0.050354 | 0.004578 | -0.18768 | 0.36621 | 0.40283 | 0.10986 | 0.45319 | 0.16022 | 0.13275 | -0.009156 | 0.41657 | 121.6782 | 0.2655 | 121.8704 | 121.106 | 121.8201 | -0.97504 | -121.8658 | 120.8313 | 121.6278 | 120.8679 | 116.9128
1488.2969 | 121.8292 | -120.9183 | 0.88348 | 0.0025177 | -0.011593 | -0.078583 | -0.0052701 | -0.031298 | -0.048031 | -0.039965 | 0.00094606 | -0.020322 | 0.057268 | 0.04434 | -0.21851 | -0.015778 | -0.020903 | -0.15564 | 0.068665 | -0.1831 | -0.19226 | -0.07782 | -0.21973 | -0.15106 | -4.1794 | 0.88348 | -120.9778 | 0.72784 | -120.5887 | -120.8496 | -120.5338 | 120.7352 | -0.81482 | -1.0757 | 120.8405 | 120.7672 | 120.6985 | 0.032043 | -0.036622 | -0.059509 | 0 | -0.15564 | 0.32959 | 0.38452 | 0.068665 | 0.44403 | 0.12817 | 0.10528 | -0.009156 | 0.3891 | 121.7056 | 0.25177 | 121.8613 | 120.9869 | 121.8018 | -1.0666 | -121.8613 | 120.726 | 121.6461 | 120.7626 | 116.7389
1490.0781 | 121.9666 | -120.7993 | 0.97046 | 0.0025177 | -0.013516 | -0.079865 | -0.0076199 | -0.031725 | -0.049954 | -0.043596 | -0.0021057 | -0.022885 | 0.055773 | 0.043699 | -0.21702 | -0.01706 | -0.021544 | -0.068665 | 0.032043 | -0.13275 | -0.036621 | 0.11902 | -0.041199 | 0.027466 | -4.0329 | 0.94757 | -120.8542 | 0.92926 | -120.3278 | -120.6024 | -120.3232 | 120.6665 | -0.93842 | -1.0071 | 120.9183 | 120.8267 | 120.7581 | 0.16022 | 0.091552 | -0.054932 | -0.022888 | -0.041199 | 0.4715 | 0.47607 | 0.19684 | 0.53101 | 0.25177 | 0.25177 | 0.09613 | 0.52643 | 121.7834 | 0.16479 | 121.8018 | 120.8313 | 121.7468 | -1.1032 | -121.8246 | 120.7626 | 121.7285 | 120.7306 | 116.7664
1491.8594 | 121.994 | -120.7535 | 0.99792 | -0.0051118 | -0.01437 | -0.079865 | -0.0050565 | -0.03258 | -0.050167 | -0.041246 | 0.00094606 | -0.023313 | 0.057482 | 0.040281 | -0.21851 | -0.018128 | -0.022398 | -0.10986 | 0.032043 | -0.12817 | -0.082397 | 0.09613 | -0.073242 | 0.004578 | -4.0878 | 0.97504 | -120.8496 | 0.97961 | -120.3094 | -120.5521 | -120.2866 | 120.6253 | -0.96588 | -1.0803 | 120.8496 | 120.7581 | 120.6802 | 0.13275 | 0.054932 | -0.09613 | -0.022888 | -0.018311 | 0.44403 | 0.46692 | 0.20142 | 0.56305 | 0.29755 | 0.2243 | 0.045777 | 0.54016 | 121.8292 | 0.16022 | 121.8246 | 120.7855 | 121.7285 | -1.1261 | -121.8475 | 120.6711 | 121.7331 | 120.6436 | 116.6656
1493.6406 | 121.907 | -120.7123 | 1.0941 | 0.0025177 | -0.013516 | -0.080079 | -0.0037747 | -0.026171 | -0.048245 | -0.03911 | 0.00094606 | -0.01904 | 0.056841 | 0.04498 | -0.22043 | -0.01471 | -0.02368 | -0.10071 | 0.068665 | -0.15564 | -0.12817 | 0.018311 | -0.12817 | -0.068665 | -4.1473 | 1.0849 | -120.7718 | 0.99335 | -120.314 | -120.607 | -120.282 | 120.5566 | -1.0254 | -1.2222 | 120.7306 | 120.6436 | 120.5841 | 0.086975 | 0.027466 | -0.05951 | -0.009155 | -0.10071 | 0.39825 | 0.4303 | 0.10529 | 0.48981 | 0.16479 | 0.17395 | 0.027466 | 0.45776 | 121.7651 | 0.22431 | 121.8567 | 120.7809 | 121.7972 | -1.2497 | -121.8658 | 120.5841 | 121.7056 | 120.6116 | 116.5649
1495.4219 | 121.9666 | -120.6985 | 1.0574 | -0.0051118 | -0.016293 | -0.080719 | -0.0069791 | -0.031511 | -0.051876 | -0.042314 | 0.00094606 | -0.020536 | 0.055345 | 0.049467 | -0.21787 | -0.015778 | -0.023894 | -0.073242 | 0.018311 | -0.12817 | -0.041199 | 0.11902 | -0.045776 | 0.009155 | -4.1473 | 1.062 | -120.7809 | 1.0254 | -120.2774 | -120.52 | -120.2499 | 120.5704 | -1.0391 | -1.0986 | 120.8176 | 120.7077 | 120.6528 | 0.13733 | 0.082398 | -0.082398 | 0.004578 | -0.032043 | 0.42114 | 0.44861 | 0.17853 | 0.53101 | 0.26093 | 0.24719 | 0.086975 | 0.50354 | 121.8063 | 0.14649 | 121.843 | 120.7169 | 121.7606 | -1.1856 | -121.8384 | 120.6573 | 121.7239 | 120.6253 | 116.5512
1497.1875 | 121.9528 | -120.6757 | 1.1169 | 0.010147 | -0.014584 | -0.078797 | -0.0067653 | -0.028734 | -0.053158 | -0.041674 | 0.00094606 | -0.019895 | 0.056841 | 0.053098 | -0.21744 | -0.016846 | -0.022826 | -0.082397 | 0.041199 | -0.12817 | -0.054932 | 0.091553 | -0.073242 | -0.004578 | -4.2206 | 1.1261 | -120.7397 | 1.0208 | -120.2728 | -120.5338 | -120.2499 | 120.5475 | -1.0757 | -1.1719 | 120.7672 | 120.6711 | 120.6024 | 0.1236 | 0.054932 | -0.064087 | 0.009156 | -0.09613 | 0.40283 | 0.42572 | 0.14191 | 0.48981 | 0.20599 | 0.21973 | 0.073242 | 0.46692 | 121.7606 | 0.16937 | 121.8658 | 120.7169 | 121.8018 | -1.2451 | -121.8567 | 120.6207 | 121.6965 | 120.5933 | 116.4551
1498.9688 | 121.8979 | -120.6024 | 1.2543 | -0.012741 | -0.012234 | -0.079011 | -0.0052701 | -0.026598 | -0.048672 | -0.039537 | -0.0051575 | -0.019467 | 0.058123 | 0.046689 | -0.21808 | -0.014069 | -0.020689 | -0.082397 | 0.07782 | -0.14191 | -0.10986 | 0.013733 | -0.14191 | -0.07782 | -4.2801 | 1.236 | -120.6528 | 1.1169 | -120.2499 | -120.5063 | -120.1904 | 120.4605 | -1.1765 | -1.3641 | 120.6162 | 120.5246 | 120.4605 | 0.064087 | 0 | -0.050354 | -0.01831 | -0.13733 | 0.35248 | 0.41199 | 0.09613 | 0.46234 | 0.14648 | 0.15564 | 0.032044 | 0.40283 | 121.7697 | 0.21973 | 121.8887 | 120.6802 | 121.8384 | -1.3962 | -121.907 | 120.4926 | 121.7194 | 120.52 | 116.3223
1500.75 | 121.9894 | -120.4422 | 1.3412 | 0.0025177 | -0.013089 | -0.078156 | -0.0052701 | -0.028734 | -0.046536 | -0.039965 | 0.0039979 | -0.021817 | 0.057268 | 0.041349 | -0.21744 | -0.015137 | -0.021758 | -0.064087 | 0.045776 | -0.10071 | -0.059509 | 0.11444 | -0.082397 | -0.018311 | -4.2938 | 1.3412 | -120.5475 | 1.3229 | -120.0485 | -120.3049 | -120.0027 | 120.3415 | -1.2955 | -1.4008 | 120.5566 | 120.4239 | 120.3598 | 0.082397 | 0.018311 | -0.10528 | 0 | -0.018311 | 0.39368 | 0.43945 | 0.13733 | 0.54474 | 0.24261 | 0.21515 | 0.041199 | 0.49896 | 121.8704 | 0.14648 | 121.8887 | 120.488 | 121.7834 | -1.442 | -121.8887 | 120.3827 | 121.7651 | 120.3781 | 116.1484
1502.5156 | 122.0352 | -120.4514 | 1.3367 | -0.012741 | -0.010952 | -0.077942 | -0.0029201 | -0.027453 | -0.048031 | -0.041887 | -0.0021057 | -0.020536 | 0.0562 | 0.045194 | -0.21851 | -0.016419 | -0.020049 | -0.054932 | 0.045776 | -0.13733 | -0.036621 | 0.10071 | -0.07782 | -0.018311 | -4.3259 | 1.3412 | -120.5109 | 1.355 | -120.0119 | -120.2728 | -119.957 | 120.314 | -1.2909 | -1.3733 | 120.5521 | 120.433 | 120.3735 | 0.11902 | 0.059509 | -0.059509 | 0.004578 | 0.01831 | 0.43945 | 0.49439 | 0.17853 | 0.55389 | 0.23804 | 0.23804 | 0.10071 | 0.49896 | 121.8658 | 0.18311 | 121.8521 | 120.4971 | 121.7926 | -1.474 | -121.8475 | 120.4147 | 121.8063 | 120.3964 | 116.1255
1504.2344 | 121.9254 | -120.3369 | 1.5335 | 0.0025177 | -0.01138 | -0.077302 | -0.0027065 | -0.027025 | -0.048458 | -0.04146 | -0.0021057 | -0.020536 | 0.058977 | 0.044126 | -0.21851 | -0.015778 | -0.023253 | -0.13733 | 0.10071 | -0.14648 | -0.17395 | -0.059509 | -0.21515 | -0.11902 | -4.4769 | 1.5335 | -120.3873 | 1.3824 | -120.0073 | -120.2682 | -119.9387 | 120.1904 | -1.4328 | -1.7075 | 120.2774 | 120.2179 | 120.1218 | 0.027465 | -0.068665 | -0.050354 | 0 | -0.15106 | 0.32959 | 0.39825 | 0.068664 | 0.44861 | 0.11902 | 0.086975 | -0.027466 | 0.37994 | 121.7697 | 0.24719 | 121.9208 | 120.4376 | 121.8704 | -1.68 | -121.9208 | 120.163 | 121.7194 | 120.1996 | 115.86
1506.0156 | 122.0352 | -120.1996 | 1.6296 | 0.010147 | -0.015652 | -0.078797 | -0.0052701 | -0.030871 | -0.049954 | -0.039537 | -0.0021057 | -0.02374 | 0.055132 | 0.053312 | -0.21851 | -0.016846 | -0.023039 | -0.082397 | 0.036621 | -0.1236 | -0.041199 | 0.1236 | -0.041199 | 0.018311 | -4.3533 | 1.6296 | -120.2454 | 1.593 | -119.7556 | -120.0119 | -119.7235 | 120.076 | -1.593 | -1.6708 | 120.3232 | 120.2179 | 120.1584 | 0.14191 | 0.082397 | -0.045776 | 0 | -0.036621 | 0.44403 | 0.47607 | 0.18768 | 0.52185 | 0.23346 | 0.24719 | 0.082397 | 0.48981 | 121.8384 | 0.16022 | 121.875 | 120.2362 | 121.8292 | -1.7532 | -121.875 | 120.1584 | 121.7926 | 120.1172 | 115.8463
1507.7969 | 121.9757 | -119.957 | 1.8951 | 0.010147 | -0.01202 | -0.079651 | -0.0044155 | -0.031084 | -0.050595 | -0.043169 | 0.00094606 | -0.01904 | 0.057695 | 0.043485 | -0.21787 | -0.016846 | -0.020262 | -0.086975 | 0.082397 | -0.15106 | -0.10986 | 0.032043 | -0.11902 | -0.068665 | -4.4128 | 1.9089 | -120.0119 | 1.8127 | -119.5862 | -119.8471 | -119.5267 | 119.8059 | -1.8127 | -2.005 | 119.989 | 119.8883 | 119.838 | 0.082397 | 0.032043 | -0.054932 | 0.013733 | -0.082398 | 0.37079 | 0.4303 | 0.10986 | 0.48523 | 0.1648 | 0.18311 | 0.041199 | 0.42572 | 121.8246 | 0.23346 | 121.9208 | 120.0394 | 121.8658 | -2.0462 | -121.907 | 119.8471 | 121.7697 | 119.87 | 115.5441
1509.5156 | 121.9437 | -119.8563 | 2.0279 | 0.0025177 | -0.01202 | -0.080933 | -0.0024929 | -0.028734 | -0.050595 | -0.041246 | 0.00094606 | -0.018186 | 0.0562 | 0.047544 | -0.21851 | -0.01471 | -0.025176 | -0.10071 | 0.073242 | -0.16022 | -0.11444 | 0.041199 | -0.1236 | -0.073242 | -4.454 | 2.0325 | -119.9158 | 1.9135 | -119.4809 | -119.7693 | -119.4305 | 119.696 | -1.9547 | -2.1423 | 119.8975 | 119.783 | 119.7327 | 0.086975 | 0.036621 | -0.059509 | 0.004578 | -0.11444 | 0.37537 | 0.42572 | 0.086975 | 0.48523 | 0.14648 | 0.20142 | 0.045776 | 0.43488 | 121.8292 | 0.23346 | 121.9482 | 119.9295 | 121.8887 | -2.1881 | -121.9437 | 119.7418 | 121.7697 | 119.7556 | 115.4022
1511.2969 | 122.0764 | -119.7556 | 2.1103 | -0.0051118 | -0.015438 | -0.079438 | -0.0074063 | -0.031725 | -0.050808 | -0.03911 | 0.00094606 | -0.022458 | 0.055773 | 0.047544 | -0.21851 | -0.016419 | -0.022398 | -0.073242 | 0.041199 | -0.11444 | -0.027466 | 0.17395 | -0.022888 | 0.027466 | -4.422 | 2.0966 | -119.8151 | 2.0782 | -119.2657 | -119.5221 | -119.2703 | 119.6411 | -2.0691 | -2.1378 | 119.9295 | 119.783 | 119.7327 | 0.14191 | 0.091553 | -0.059509 | -0.013733 | -0.032044 | 0.48981 | 0.48523 | 0.23346 | 0.54474 | 0.29297 | 0.28839 | 0.086975 | 0.54932 | 121.8933 | 0.15564 | 121.9116 | 119.7968 | 121.8521 | -2.2247 | -121.9254 | 119.7281 | 121.8338 | 119.6823 | 115.3336
1513.0781 | 121.9208 | -119.8563 | 2.0828 | 0.0025177 | -0.0094571 | -0.077515 | -0.0020657 | -0.029162 | -0.049099 | -0.040605 | -0.0051575 | -0.017331 | 0.057695 | 0.049253 | -0.21872 | -0.014496 | -0.025176 | -0.12817 | 0.064087 | -0.15564 | -0.16479 | -0.068665 | -0.19684 | -0.14191 | -4.6097 | 2.0645 | -119.8975 | 1.8906 | -119.5358 | -119.8105 | -119.4717 | 119.7006 | -2.0187 | -2.2476 | 119.7876 | 119.7144 | 119.6594 | 0.013733 | -0.041198 | -0.041199 | -0.018311 | -0.19226 | 0.32043 | 0.38452 | 0.045776 | 0.42572 | 0.086975 | 0.086975 | -0.009155 | 0.36163 | 121.788 | 0.21973 | 121.962 | 119.9203 | 121.9208 | -2.2385 | -121.9803 | 119.6915 | 121.7468 | 119.7281 | 115.2466
1514.8594 | 122.0901 | -119.7601 | 2.0737 | -0.0051118 | -0.015438 | -0.08136 | -0.0091153 | -0.033648 | -0.05209 | -0.043383 | -0.0021057 | -0.022458 | 0.059191 | 0.044126 | -0.21744 | -0.018555 | -0.021544 | -0.064087 | 0.064087 | -0.09613 | -0.032043 | 0.14191 | -0.013733 | 0.018311 | -4.4495 | 2.0691 | -119.8425 | 2.0508 | -119.3161 | -119.577 | -119.3024 | 119.664 | -2.0096 | -2.1057 | 119.902 | 119.7784 | 119.7464 | 0.11444 | 0.082397 | -0.082397 | -0.004577 | -0.022888 | 0.44403 | 0.45776 | 0.18311 | 0.54016 | 0.2655 | 0.23804 | 0.064087 | 0.52643 | 121.8933 | 0.16022 | 121.9116 | 119.8242 | 121.8292 | -2.1698 | -121.9162 | 119.7281 | 121.8109 | 119.696 | 115.3107
1516.5781 | 121.9986 | -119.6503 | 2.2751 | 0.0025177 | -0.013729 | -0.078156 | -0.0031337 | -0.03023 | -0.049313 | -0.039324 | 0.0070497 | -0.017758 | 0.058763 | 0.049467 | -0.22022 | -0.015351 | -0.020262 | -0.086975 | 0.086975 | -0.13275 | -0.086975 | 0.036621 | -0.10529 | -0.054932 | -4.5136 | 2.2614 | -119.6915 | 2.1561 | -119.2612 | -119.5221 | -119.2017 | 119.5175 | -2.1881 | -2.3621 | 119.6869 | 119.5953 | 119.545 | 0.077819 | 0.027465 | -0.041198 | -0.013732 | -0.11902 | 0.3891 | 0.44861 | 0.12817 | 0.48981 | 0.16937 | 0.16937 | 0.045776 | 0.4303 | 121.8475 | 0.21973 | 121.9528 | 119.7372 | 121.9116 | -2.4078 | -121.9666 | 119.5633 | 121.8063 | 119.5633 | 115.1367
1518.375 | 121.9574 | -119.6274 | 2.3346 | 0.0025177 | -0.0094571 | -0.077942 | -0.0044155 | -0.03023 | -0.050167 | -0.03911 | 0.00094606 | -0.017758 | 0.057482 | 0.050535 | -0.2183 | -0.016633 | -0.023894 | -0.12817 | 0.11444 | -0.15564 | -0.16937 | -0.064087 | -0.20142 | -0.11444 | -4.6646 | 2.33 | -119.6594 | 2.1515 | -119.2932 | -119.5541 | -119.22 | 119.4717 | -2.2202 | -2.504 | 119.5633 | 119.5129 | 119.426 | 0.041199 | -0.045776 | -0.032044 | -0.004578 | -0.18311 | 0.33417 | 0.40741 | 0.073242 | 0.43945 | 0.10529 | 0.091553 | -0.013733 | 0.36621 | 121.8109 | 0.27008 | 121.9894 | 119.7418 | 121.9574 | -2.4902 | -121.994 | 119.458 | 121.7789 | 119.4992 | 114.9628
1520.1562 | 121.9803 | -119.577 | 2.3621 | 0.010147 | -0.010739 | -0.076661 | -0.0031337 | -0.027666 | -0.050808 | -0.042742 | -0.0021057 | -0.018186 | 0.055773 | 0.051389 | -0.21702 | -0.014283 | -0.020689 | -0.13733 | 0.10529 | -0.13733 | -0.18768 | -0.050354 | -0.20142 | -0.12817 | -4.6967 | 2.3666 | -119.6594 | 2.1973 | -119.2657 | -119.545 | -119.1834 | 119.4397 | -2.2568 | -2.5497 | 119.5267 | 119.4489 | 119.3756 | 0.009155 | -0.064087 | -0.082398 | 0.004577 | -0.1648 | 0.31128 | 0.39368 | 0.032043 | 0.47607 | 0.11444 | 0.086975 | -0.050354 | 0.39368 | 121.8567 | 0.24262 | 122.0261 | 119.6823 | 121.9437 | -2.4994 | -122.0215 | 119.3893 | 121.7743 | 119.4397 | 114.8804
1521.875 | 121.9757 | -119.5038 | 2.4857 | 0.0025177 | -0.015011 | -0.079224 | -0.0050565 | -0.030657 | -0.050595 | -0.040178 | 0.00094606 | -0.01904 | 0.059832 | 0.043272 | -0.21979 | -0.017273 | -0.019621 | -0.12817 | 0.091553 | -0.14191 | -0.15106 | 0.004578 | -0.12817 | -0.07782 | -4.6967 | 2.4445 | -119.5541 | 2.2751 | -119.1467 | -119.3939 | -119.101 | 119.3619 | -2.3941 | -2.6367 | 119.5084 | 119.426 | 119.3756 | 0.064087 | 0.013733 | -0.050354 | -0.041199 | -0.21057 | 0.35706 | 0.40283 | 0.10986 | 0.45319 | 0.16022 | 0.14649 | -0.009155 | 0.40741 | 121.8292 | 0.23346 | 121.9986 | 119.5953 | 121.9482 | -2.6276 | -122.0398 | 119.3527 | 121.7789 | 119.3756 | 114.8071
1523.6562 | 122.1039 | -119.7372 | 2.1835 | 0.0025177 | -0.01437 | -0.079224 | -0.0050565 | -0.026812 | -0.050167 | -0.039751 | -0.0021057 | -0.02139 | 0.057695 | 0.043699 | -0.2168 | -0.014924 | -0.020476 | -0.091553 | 0.064087 | -0.1236 | -0.086975 | 0.059509 | -0.064087 | -0.004578 | -4.6646 | 2.1744 | -119.7784 | 2.124 | -119.3069 | -119.5358 | -119.2474 | 119.6136 | -2.1194 | -2.2705 | 119.7968 | 119.7327 | 119.6732 | 0.11902 | 0.059509 | -0.041198 | -0.009156 | -0.05951 | 0.4303 | 0.48981 | 0.20142 | 0.531 | 0.24261 | 0.1831 | 0.036621 | 0.4715 | 121.9025 | 0.18768 | 121.9528 | 119.8013 | 121.9116 | -2.3071 | -121.962 | 119.6503 | 121.8613 | 119.6457 | 115.0726
1525.4531 | 122.0215 | -119.9707 | 2.005 | -0.0051118 | -0.013302 | -0.080719 | -0.0037747 | -0.030443 | -0.050167 | -0.042955 | 0.00094606 | -0.018613 | 0.054064 | 0.045835 | -0.21851 | -0.016633 | -0.023039 | -0.13275 | 0.10071 | -0.15106 | -0.17395 | -0.032043 | -0.15106 | -0.09613 | -4.7516 | 1.9913 | -120.0577 | 1.8219 | -119.6045 | -119.8563 | -119.5496 | 119.8196 | -1.9043 | -2.179 | 119.9387 | 119.8746 | 119.8196 | 0.054932 | 0 | -0.086975 | -0.013733 | -0.18311 | 0.36621 | 0.42114 | 0.11444 | 0.50812 | 0.20142 | 0.11902 | -0.022888 | 0.45319 | 121.8796 | 0.25177 | 122.0489 | 120.0714 | 121.962 | -2.1561 | -122.0627 | 119.7968 | 121.7926 | 119.838 | 115.2191
1527.1719 | 122.0856 | -120.0073 | 1.9089 | -0.012741 | -0.012448 | -0.079438 | -0.0069791 | -0.030016 | -0.052517 | -0.042101 | -0.0021057 | -0.02139 | 0.055773 | 0.051389 | -0.22001 | -0.015137 | -0.021758 | -0.045776 | 0.054932 | -0.10071 | -0.050354 | 0.11444 | -0.068665 | -0.009155 | -4.7058 | 1.9089 | -120.0394 | 1.8768 | -119.5999 | -119.8334 | -119.5312 | 119.9066 | -1.8539 | -1.9592 | 120.1218 | 119.9982 | 119.9387 | 0.091553 | 0.032043 | -0.032044 | 0 | -0.032044 | 0.40741 | 0.47607 | 0.17395 | 0.50812 | 0.20599 | 0.21515 | 0.050354 | 0.43945 | 121.9162 | 0.15564 | 121.9482 | 120.0623 | 121.9162 | -2.0096 | -121.9482 | 119.957 | 121.8842 | 119.9615 | 115.3015
1528.9531 | 122.1313 | -119.9982 | 1.9135 | -0.0051118 | -0.015652 | -0.078797 | -0.0065517 | -0.034289 | -0.049099 | -0.038896 | 0.00094606 | -0.021176 | 0.0562 | 0.050321 | -0.2168 | -0.017273 | -0.018767 | -0.068665 | 0.054932 | -0.1236 | -0.027466 | 0.15106 | -0.018311 | 0.032043 | -4.66 | 1.8997 | -120.0531 | 1.9043 | -119.5312 | -119.7784 | -119.5084 | 119.8746 | -1.8585 | -1.9409 | 120.1492 | 120.0302 | 119.9799 | 0.15564 | 0.10528 | -0.054932 | -0.013733 | -0.009155 | 0.46692 | 0.48981 | 0.21973 | 0.54474 | 0.27466 | 0.27466 | 0.09613 | 0.52185 | 121.9574 | 0.17853 | 121.9528 | 120.0531 | 121.8979 | -2.037 | -121.9666 | 119.9707 | 121.9025 | 119.9295 | 115.3381
1530.7344 | 122.0123 | -120.0714 | 1.8951 | 0.0025177 | -0.017147 | -0.080079 | -0.0029201 | -0.02788 | -0.049526 | -0.042955 | -0.0021057 | -0.019467 | 0.057695 | 0.052244 | -0.21958 | -0.014924 | -0.022185 | -0.15564 | 0.10529 | -0.14191 | -0.16937 | -0.041199 | -0.13733 | -0.10071 | -4.8386 | 1.9089 | -120.1767 | 1.7075 | -119.7556 | -120.0073 | -119.696 | 119.9295 | -1.7899 | -2.0645 | 120.0302 | 119.9707 | 119.9341 | 0.041199 | 0.004578 | -0.10529 | 0.013733 | -0.18768 | 0.31586 | 0.37537 | 0.064087 | 0.48065 | 0.16937 | 0.10071 | -0.027466 | 0.42114 | 121.8842 | 0.24719 | 122.0856 | 120.1767 | 121.9803 | -2.037 | -122.0718 | 119.902 | 121.7789 | 119.9158 | 115.2328
1532.4688 | 122.1634 | -120.0485 | 1.8539 | 0.0025177 | -0.01672 | -0.080719 | -0.0056973 | -0.033861 | -0.050808 | -0.040605 | 0.0070497 | -0.022458 | 0.056414 | 0.04434 | -0.2183 | -0.014924 | -0.020262 | -0.073242 | 0.054932 | -0.11902 | -0.013733 | 0.15106 | 0.004578 | 0.036621 | -4.7058 | 1.8494 | -120.1172 | 1.8311 | -119.5908 | -119.8334 | -119.5816 | 119.9295 | -1.799 | -1.8677 | 120.1996 | 120.0851 | 120.0531 | 0.15564 | 0.1236 | -0.068664 | -0.004578 | -0.022888 | 0.45776 | 0.46692 | 0.21515 | 0.53558 | 0.28381 | 0.27008 | 0.10529 | 0.52643 | 121.9482 | 0.17395 | 121.9666 | 120.1035 | 121.8979 | -1.973 | -121.9711 | 120.0348 | 121.8796 | 119.9753 | 115.3427
1534.25 | 122.168 | -120.2133 | 1.7441 | -0.0051118 | -0.01672 | -0.078156 | -0.0061245 | -0.034716 | -0.050167 | -0.040605 | -0.0021057 | -0.022031 | 0.055773 | 0.042417 | -0.21787 | -0.015778 | -0.022612 | -0.073242 | 0.059509 | -0.10529 | -0.036621 | 0.10986 | -0.009155 | 0.027466 | -4.8248 | 1.7441 | -120.2545 | 1.7258 | -119.7464 | -119.989 | -119.7006 | 120.108 | -1.6846 | -1.7807 | 120.3232 | 120.2408 | 120.2042 | 0.13275 | 0.096131 | -0.041199 | 0 | -0.018311 | 0.46692 | 0.5127 | 0.2243 | 0.55389 | 0.2655 | 0.21515 | 0.068665 | 0.50812 | 121.9803 | 0.16479 | 121.9986 | 120.2728 | 121.9574 | -1.8494 | -121.9986 | 120.1767 | 121.9391 | 120.1401 | 115.3885
1536.0469 | 122.1863 | -120.163 | 1.7487 | 0.0025177 | -0.013516 | -0.079865 | -0.0069791 | -0.031725 | -0.049313 | -0.039751 | 0.00094606 | -0.022031 | 0.055986 | 0.04434 | -0.21702 | -0.013856 | -0.021758 | -0.073242 | 0.059509 | -0.11444 | -0.045776 | 0.10071 | -0.054932 | 0.009155 | -4.8065 | 1.7715 | -120.2271 | 1.7578 | -119.7189 | -119.957 | -119.6732 | 120.0485 | -1.6891 | -1.7944 | 120.2637 | 120.1721 | 120.108 | 0.1236 | 0.059509 | -0.064087 | 0.022888 | 0.009155 | 0.44403 | 0.48981 | 0.20599 | 0.55389 | 0.27008 | 0.21515 | 0.068665 | 0.50812 | 121.9849 | 0.17395 | 121.9986 | 120.2225 | 121.9345 | -1.8631 | -121.9757 | 120.1172 | 121.9208 | 120.0897 | 115.3564
1537.7656 | 122.0581 | -120.0897 | 1.8906 | 0.010147 | -0.013516 | -0.079224 | -0.0042019 | -0.027453 | -0.049099 | -0.040819 | -0.0021057 | -0.01904 | 0.055345 | 0.049894 | -0.21851 | -0.01471 | -0.024535 | -0.10529 | 0.10071 | -0.17395 | -0.13275 | -0.022888 | -0.1236 | -0.068665 | -4.8569 | 1.8951 | -120.1492 | 1.7853 | -119.7098 | -119.9799 | -119.6503 | 119.9158 | -1.7899 | -2.0233 | 120.0668 | 120.0211 | 119.9661 | 0.10528 | 0.050354 | -0.059509 | 0.004578 | -0.10529 | 0.37994 | 0.43945 | 0.10986 | 0.49896 | 0.16937 | 0.15106 | 0.041199 | 0.43945 | 121.9345 | 0.27466 | 122.0444 | 120.1904 | 121.9849 | -2.0645 | -122.0398 | 119.957 | 121.875 | 119.9844 | 115.2328
1539.5469 | 122.1451 | -120.076 | 1.8906 | 0.010147 | -0.01672 | -0.082428 | -0.0084743 | -0.030443 | -0.051235 | -0.041033 | -0.0051575 | -0.020536 | 0.054918 | 0.045621 | -0.2183 | -0.018128 | -0.019621 | -0.10529 | 0.064087 | -0.10529 | -0.091553 | 0.050354 | -0.082397 | -0.022888 | -4.9118 | 1.9043 | -120.1172 | 1.8494 | -119.632 | -119.8975 | -119.5953 | 119.9707 | -1.8265 | -1.9821 | 120.1263 | 120.0531 | 119.9936 | 0.082398 | 0.022889 | -0.041198 | 0.013733 | -0.041199 | 0.44403 | 0.48065 | 0.17853 | 0.52185 | 0.21973 | 0.15564 | 0.013733 | 0.48523 | 121.9666 | 0.16937 | 122.0215 | 120.1401 | 121.9803 | -1.9958 | -122.0078 | 119.9844 | 121.9254 | 119.9707 | 115.1642
1541.2812 | 122.0261 | -120.1859 | 1.8585 | 0.010147 | -0.013729 | -0.082428 | -0.0054837 | -0.032793 | -0.04974 | -0.042528 | 0.00094606 | -0.017758 | 0.05855 | 0.049894 | -0.21958 | -0.017487 | -0.024962 | -0.15106 | 0.10071 | -0.13733 | -0.16937 | -0.027466 | -0.16022 | -0.091553 | -4.9805 | 1.8585 | -120.2271 | 1.6663 | -119.8196 | -120.0943 | -119.7784 | 120.0485 | -1.7578 | -2.0279 | 120.1584 | 120.0943 | 120.0256 | 0.045776 | -0.022888 | -0.041199 | 0 | -0.19226 | 0.36621 | 0.40741 | 0.091553 | 0.44861 | 0.13275 | 0.10986 | -0.032044 | 0.40741 | 121.8933 | 0.23804 | 122.0856 | 120.2866 | 122.0444 | -1.9959 | -122.0856 | 120.0165 | 121.8521 | 120.0348 | 115.2054
1543.0469 | 122.049 | -120.1492 | 1.8677 | -0.0051118 | -0.013943 | -0.078583 | -0.0048427 | -0.032152 | -0.050381 | -0.038896 | -0.0051575 | -0.022885 | 0.059404 | 0.046476 | -0.21766 | -0.015778 | -0.025603 | -0.14648 | 0.091553 | -0.14191 | -0.16022 | -0.018311 | -0.14191 | -0.09613 | -4.9942 | 1.8631 | -120.2271 | 1.6754 | -119.8288 | -120.0668 | -119.7784 | 120.0073 | -1.7761 | -2.0279 | 120.1309 | 120.0531 | 120.0073 | 0.045777 | 0 | -0.07782 | -0.004578 | -0.19226 | 0.32044 | 0.37079 | 0.082398 | 0.44861 | 0.16022 | 0.1236 | -0.01831 | 0.39826 | 121.9025 | 0.23346 | 122.0901 | 120.2408 | 122.0123 | -2.0096 | -122.0947 | 119.989 | 121.8246 | 120.0027 | 115.155
1544.8125 | 122.0535 | -120.2179 | 1.8585 | -0.0051118 | -0.013943 | -0.079224 | -0.0046291 | -0.035998 | -0.051876 | -0.042314 | -0.0021057 | -0.017758 | 0.05855 | 0.051603 | -0.21744 | -0.01471 | -0.018553 | -0.13275 | 0.10071 | -0.14191 | -0.15564 | -0.032043 | -0.14191 | -0.10071 | -5.0446 | 1.8082 | -120.282 | 1.6479 | -119.8517 | -120.1309 | -119.7968 | 120.076 | -1.7578 | -2.0142 | 120.1859 | 120.1172 | 120.076 | 0.041199 | 0 | -0.064086 | -0.050354 | -0.21057 | 0.36621 | 0.42114 | 0.086976 | 0.48523 | 0.15106 | 0.10986 | -0.013733 | 0.4303 | 121.9299 | 0.24262 | 122.0901 | 120.3186 | 122.0261 | -2.0004 | -122.1405 | 120.0623 | 121.8658 | 120.0851 | 115.1733
1546.5938 | 122.1817 | -120.163 | 1.8127 | 0.0025177 | -0.015225 | -0.080079 | -0.0046291 | -0.031511 | -0.050381 | -0.040392 | 0.00094606 | -0.021604 | 0.055132 | 0.048612 | -0.21766 | -0.018555 | -0.025176 | -0.073242 | 0.059509 | -0.10071 | -0.009155 | 0.14191 | -0.009155 | 0.027466 | -4.953 | 1.799 | -120.2316 | 1.7624 | -119.7144 | -119.9707 | -119.6686 | 120.0623 | -1.7532 | -1.8219 | 120.3049 | 120.1904 | 120.1538 | 0.12817 | 0.091553 | -0.068664 | -0.013733 | -0.050354 | 0.44861 | 0.49439 | 0.19226 | 0.56305 | 0.26093 | 0.24262 | 0.091553 | 0.51727 | 121.994 | 0.16022 | 122.0306 | 120.2225 | 121.962 | -1.9135 | -122.0444 | 120.1538 | 121.9254 | 120.0897 | 115.21
1548.3125 | 122.1451 | -120.108 | 1.918 | 0.0025177 | -0.014584 | -0.080719 | -0.0071927 | -0.033648 | -0.050808 | -0.039537 | 0.00094606 | -0.02139 | 0.055773 | 0.046903 | -0.22001 | -0.015565 | -0.025176 | -0.059509 | 0.045776 | -0.11444 | -0.036621 | 0.11902 | -0.041199 | 0.013733 | -5.0171 | 1.8997 | -120.1492 | 1.8219 | -119.6869 | -119.9295 | -119.6274 | 119.9936 | -1.8723 | -1.9547 | 120.2271 | 120.1218 | 120.0668 | 0.12817 | 0.073242 | -0.041199 | -0.018311 | -0.096131 | 0.42114 | 0.48065 | 0.17853 | 0.52185 | 0.21973 | 0.23346 | 0.07782 | 0.46234 | 121.9711 | 0.16022 | 122.049 | 120.1538 | 122.0078 | -2.0325 | -122.0673 | 120.0714 | 121.9299 | 120.0485 | 115.0909
1550.0781 | 122.2137 | -119.9982 | 1.9775 | 0.0025177 | -0.013729 | -0.078583 | -0.0056973 | -0.031298 | -0.04974 | -0.042528 | 0.00094606 | -0.020322 | 0.0562 | 0.041135 | -0.21808 | -0.017273 | -0.023467 | -0.086975 | 0.050354 | -0.1236 | -0.045776 | 0.10529 | -0.041199 | 0.027466 | -5.0125 | 1.973 | -120.0623 | 1.9821 | -119.5267 | -119.8013 | -119.5038 | 119.8746 | -1.9272 | -2.0233 | 120.1035 | 120.0256 | 119.957 | 0.15106 | 0.082397 | -0.064087 | -0.004578 | 0.004578 | 0.4715 | 0.49439 | 0.19684 | 0.55847 | 0.26093 | 0.22888 | 0.07782 | 0.53558 | 122.0444 | 0.17395 | 122.0352 | 120.0485 | 121.9711 | -2.1011 | -122.0398 | 119.9524 | 121.9803 | 119.9112 | 114.9857
1551.8438 | 122.1085 | -119.9615 | 2.0691 | 0.0025177 | -0.015225 | -0.080079 | -0.0039883 | -0.031939 | -0.049954 | -0.039324 | 0.00094606 | -0.018186 | 0.056414 | 0.04199 | -0.21851 | -0.015565 | -0.024535 | -0.13733 | 0.09613 | -0.15106 | -0.17395 | -0.041199 | -0.14648 | -0.10529 | -5.1453 | 2.0966 | -120.0439 | 1.9272 | -119.6136 | -119.87 | -119.5587 | 119.8105 | -1.973 | -2.243 | 119.9203 | 119.8563 | 119.8151 | 0.045776 | 0.004578 | -0.082397 | 0.027466 | -0.14191 | 0.3479 | 0.40283 | 0.091553 | 0.48523 | 0.17395 | 0.10986 | -0.022888 | 0.4303 | 121.9711 | 0.24719 | 122.1405 | 120.0577 | 122.0581 | -2.2202 | -122.113 | 119.7876 | 121.8887 | 119.8242 | 114.8163
1553.6406 | 122.1451 | -120.0302 | 1.9775 | -0.0051118 | -0.011166 | -0.079651 | -0.0033475 | -0.031298 | -0.048886 | -0.040819 | 0.00094606 | -0.019681 | 0.055132 | 0.046049 | -0.21787 | -0.015137 | -0.021758 | -0.12817 | 0.09613 | -0.14648 | -0.13733 | -0.009155 | -0.17853 | -0.091553 | -5.191 | 1.973 | -120.108 | 1.9089 | -119.6548 | -119.9158 | -119.5862 | 119.8837 | -1.8814 | -2.1149 | 120.0211 | 119.9387 | 119.8517 | 0.054931 | -0.032044 | -0.07782 | -0.004578 | -0.068664 | 0.37537 | 0.44403 | 0.11444 | 0.52185 | 0.19226 | 0.13733 | 0.009155 | 0.45319 | 122.0169 | 0.24261 | 122.081 | 120.1263 | 122.0032 | -2.124 | -122.0856 | 119.8929 | 121.9391 | 119.902 | 114.8392
1555.3594 | 122.0947 | -120.0668 | 1.9821 | -0.012741 | -0.0094571 | -0.078156 | -0.0024929 | -0.028734 | -0.049526 | -0.037187 | -0.0021057 | -0.020108 | 0.056627 | 0.052885 | -0.21766 | -0.016633 | -0.023894 | -0.086975 | 0.09613 | -0.1236 | -0.11444 | 0.018311 | -0.15564 | -0.086975 | -5.1956 | 1.9867 | -120.1172 | 1.8494 | -119.7052 | -119.9844 | -119.632 | 119.9432 | -1.886 | -2.0966 | 120.0851 | 119.9799 | 119.9112 | 0.036621 | -0.032044 | -0.050354 | 0.004577 | -0.13275 | 0.36163 | 0.43488 | 0.082397 | 0.48523 | 0.13275 | 0.14191 | 0.009155 | 0.41199 | 121.9666 | 0.21973 | 122.1039 | 120.163 | 122.0535 | -2.1057 | -122.0993 | 119.9524 | 121.9162 | 119.9799 | 114.8712
1557.1562 | 122.2412 | -120.0027 | 2.0004 | 0.0025177 | -0.013729 | -0.080079 | -0.0065517 | -0.034716 | -0.049526 | -0.040819 | 0.00094606 | -0.02139 | 0.055773 | 0.042203 | -0.21552 | -0.016205 | -0.022826 | -0.09613 | 0.059509 | -0.10986 | -0.041199 | 0.1236 | -0.036621 | 0.032043 | -5.1727 | 2.005 | -120.0623 | 2.0096 | -119.5312 | -119.7784 | -119.4992 | 119.8929 | -1.9409 | -2.0416 | 120.1263 | 120.0348 | 119.9661 | 0.14191 | 0.073242 | -0.059509 | 0.004578 | 0.009156 | 0.4715 | 0.50354 | 0.22431 | 0.56305 | 0.28381 | 0.23346 | 0.068664 | 0.53101 | 122.0718 | 0.16937 | 122.0673 | 120.0623 | 122.0078 | -2.1103 | -122.0627 | 119.9615 | 122.0123 | 119.9066 | 114.83
1558.875 | 122.2092 | -120.1035 | 1.8951 | 0.010147 | -0.0090299 | -0.077088 | -0.0052701 | -0.031298 | -0.049313 | -0.038683 | -0.0021057 | -0.020536 | 0.058336 | 0.054807 | -0.22043 | -0.01706 | -0.024748 | -0.036621 | 0.054932 | -0.09613 | -0.032043 | 0.11902 | -0.068665 | -0.009155 | -5.2185 | 1.9043 | -120.163 | 1.9043 | -119.6686 | -119.9249 | -119.5816 | 120.0073 | -1.8402 | -1.9272 | 120.2225 | 120.0943 | 120.0348 | 0.086975 | 0.027465 | -0.059509 | 0.009155 | 0.009155 | 0.43488 | 0.52185 | 0.17853 | 0.58136 | 0.23804 | 0.21515 | 0.064087 | 0.49439 | 122.0673 | 0.15106 | 122.0673 | 120.1584 | 122.0078 | -1.9913 | -122.0581 | 120.0714 | 122.0078 | 120.0668 | 114.8849
1560.6562 | 122.2321 | -119.9341 | 2.0782 | 0.0025177 | -0.010525 | -0.078583 | -0.0039883 | -0.029802 | -0.049099 | -0.043383 | 0.00094606 | -0.018613 | 0.059191 | 0.049894 | -0.22086 | -0.01471 | -0.02368 | -0.10529 | 0.064087 | -0.1236 | -0.082397 | 0.054932 | -0.11902 | -0.036621 | -5.2551 | 2.0691 | -119.9936 | 2.0554 | -119.5175 | -119.7922 | -119.4443 | 119.8105 | -2.0142 | -2.1606 | 119.989 | 119.8975 | 119.8151 | 0.086975 | 0.004577 | -0.059509 | -0.009155 | -0.022888 | 0.41657 | 0.48981 | 0.14191 | 0.54932 | 0.20142 | 0.17853 | 0.041199 | 0.47607 | 122.0489 | 0.18768 | 122.0627 | 119.9982 | 122.0032 | -2.2018 | -122.0718 | 119.8517 | 121.9894 | 119.8288 | 114.679
1562.4375 | 122.0901 | -119.9661 | 2.1149 | 0.0025177 | -0.010739 | -0.077729 | -0.0031337 | -0.029802 | -0.048886 | -0.04146 | 0.00094606 | -0.019467 | 0.057482 | 0.052457 | -0.21851 | -0.013642 | -0.021758 | -0.12817 | 0.10071 | -0.13733 | -0.18768 | -0.068665 | -0.21057 | -0.11902 | -5.4062 | 2.1194 | -120.0165 | 1.9455 | -119.632 | -119.9066 | -119.545 | 119.8288 | -2.0142 | -2.3026 | 119.8975 | 119.8471 | 119.7556 | 0.01831 | -0.073242 | -0.050354 | 0.004578 | -0.16937 | 0.33417 | 0.42114 | 0.059509 | 0.4715 | 0.10986 | 0.068664 | -0.050354 | 0.38452 | 121.962 | 0.23804 | 122.1359 | 120.0668 | 122.0856 | -2.2522 | -122.1313 | 119.7784 | 121.9116 | 119.838 | 114.5599
1564.1562 | 122.0993 | -120.0211 | 2.0828 | -0.0051118 | -0.013089 | -0.079651 | -0.0054837 | -0.030871 | -0.051663 | -0.039965 | -0.0021057 | -0.01904 | 0.05855 | 0.040494 | -0.21702 | -0.015778 | -0.022185 | -0.11444 | 0.086975 | -0.11902 | -0.14191 | 0.004578 | -0.13275 | -0.07782 | -5.4016 | 2.0828 | -120.0577 | 1.9043 | -119.6457 | -119.9066 | -119.5908 | 119.902 | -1.9959 | -2.2247 | 120.0256 | 119.9432 | 119.8883 | 0.041199 | -0.013732 | -0.036621 | 0 | -0.17853 | 0.37537 | 0.4303 | 0.11444 | 0.46692 | 0.15106 | 0.1236 | -0.022888 | 0.41199 | 121.962 | 0.20599 | 122.1405 | 120.108 | 122.1039 | -2.2018 | -122.1405 | 119.8791 | 121.9254 | 119.9066 | 114.6194
1565.9375 | 122.2504 | -119.9661 | 2.0508 | -0.012741 | -0.010739 | -0.076661 | -0.0027065 | -0.029802 | -0.048458 | -0.03911 | -0.0021057 | -0.020536 | 0.056414 | 0.040067 | -0.21851 | -0.015137 | -0.022612 | -0.045776 | 0.068665 | -0.091553 | -0.045776 | 0.10071 | -0.064087 | -0.013733 | -5.3375 | 2.0325 | -120.0302 | 2.0416 | -119.5496 | -119.8105 | -119.4534 | 119.8746 | -1.9821 | -2.0966 | 120.0668 | 119.9524 | 119.902 | 0.07782 | 0.027466 | -0.064087 | -0.01831 | -0.009155 | 0.41656 | 0.5127 | 0.15564 | 0.57678 | 0.21973 | 0.19226 | 0.045777 | 0.48065 | 122.0718 | 0.16022 | 122.0627 | 120.0348 | 121.9986 | -2.1423 | -122.081 | 119.9203 | 122.0078 | 119.9203 | 114.6286
1567.6719 | 122.2504 | -119.6274 | 2.417 | -0.0051118 | -0.016293 | -0.080292 | -0.0071927 | -0.035357 | -0.050167 | -0.044451 | 0.00094606 | -0.020108 | 0.057054 | 0.041563 | -0.21894 | -0.016419 | -0.023467 | -0.11902 | 0.064087 | -0.13733 | -0.086975 | 0.064087 | -0.073242 | -0.022888 | -5.365 | 2.4353 | -119.6686 | 2.3804 | -119.1879 | -119.4397 | -119.1467 | 119.4901 | -2.3529 | -2.504 | 119.6915 | 119.6045 | 119.5541 | 0.11444 | 0.064087 | -0.041199 | 0.018311 | -0.036621 | 0.43945 | 0.48065 | 0.18768 | 0.52185 | 0.22888 | 0.20142 | 0.050354 | 0.48065 | 122.0489 | 0.20142 | 122.1039 | 119.6915 | 122.0627 | -2.5543 | -122.0856 | 119.5404 | 122.0078 | 119.5084 | 114.2624
1569.4531 | 122.2275 | -120.4742 | 1.5839 | 0.0025177 | -0.013089 | -0.08136 | -0.0042019 | -0.033434 | -0.04974 | -0.036974 | -0.0021057 | -0.021176 | 0.057482 | 0.051176 | -0.21894 | -0.016419 | -0.02368 | -0.086975 | 0.054932 | -0.073242 | -0.068665 | 0.09613 | -0.082397 | 0.004578 | -5.4611 | 1.6113 | -120.5063 | 1.5381 | -120.0531 | -120.3049 | -119.9661 | 120.401 | -1.5289 | -1.6525 | 120.5704 | 120.4788 | 120.3918 | 0.07782 | -0.009155 | -0.032044 | 0.027466 | -0.045776 | 0.42114 | 0.50812 | 0.16937 | 0.54016 | 0.20142 | 0.16937 | 0.004577 | 0.45319 | 122.0444 | 0.12817 | 122.1176 | 120.5292 | 122.0856 | -1.6571 | -122.0901 | 120.4056 | 122.0123 | 120.3873 | 115.0131
1571.2344 | 122.1634 | -120.0302 | 2.1103 | -0.012741 | -0.014798 | -0.078797 | -0.0044155 | -0.028093 | -0.05209 | -0.045305 | -0.0021057 | -0.021604 | 0.056841 | 0.044126 | -0.21766 | -0.017914 | -0.026244 | -0.10529 | 0.10986 | -0.11902 | -0.11902 | 0.018311 | -0.11902 | -0.050354 | -5.5023 | 2.0828 | -120.0806 | 1.9226 | -119.664 | -119.9112 | -119.6274 | 119.9112 | -2.0004 | -2.2293 | 120.0485 | 119.9799 | 119.9112 | 0.068665 | 0 | -0.050354 | -0.027466 | -0.18768 | 0.36621 | 0.40283 | 0.11902 | 0.45319 | 0.16937 | 0.13733 | 0 | 0.41657 | 122.0032 | 0.22888 | 122.1634 | 120.1401 | 122.113 | -2.2293 | -122.1909 | 119.9112 | 121.9528 | 119.9249 | 114.5279
1573.0156 | 122.2229 | -120.0302 | 2.0782 | 0.0025177 | -0.014798 | -0.081788 | -0.0063381 | -0.033434 | -0.048886 | -0.042101 | -0.0021057 | -0.021176 | 0.056627 | 0.044767 | -0.22043 | -0.017487 | -0.024535 | -0.059509 | 0.07782 | -0.10071 | -0.032043 | 0.11902 | -0.022888 | 0.022888 | -5.4657 | 2.0554 | -120.1035 | 1.9775 | -119.6136 | -119.8517 | -119.5633 | 119.9295 | -2.0004 | -2.1103 | 120.1492 | 120.0531 | 120.0073 | 0.1236 | 0.07782 | -0.073243 | -0.022888 | -0.10071 | 0.41657 | 0.46692 | 0.17853 | 0.54016 | 0.25177 | 0.21973 | 0.068665 | 0.48981 | 122.081 | 0.17853 | 122.1588 | 120.108 | 122.0856 | -2.179 | -122.1817 | 119.9982 | 122.0078 | 119.9707 | 114.5645
1574.7188 | 122.1771 | -119.9524 | 2.1286 | 0.0025177 | -0.010952 | -0.07837 | -0.0031337 | -0.031084 | -0.049526 | -0.041246 | -0.0021057 | -0.020108 | 0.057268 | 0.04968 | -0.21915 | -0.013856 | -0.024107 | -0.064087 | 0.10071 | -0.11444 | -0.086975 | 0.054932 | -0.082397 | -0.041199 | -5.5161 | 2.1286 | -120.0302 | 2.0508 | -119.5862 | -119.8425 | -119.5038 | 119.838 | -2.0279 | -2.2156 | 120.0073 | 119.9112 | 119.87 | 0.073242 | 0.032044 | -0.077819 | 0 | -0.07782 | 0.36621 | 0.44861 | 0.10986 | 0.52643 | 0.18768 | 0.16937 | 0.027466 | 0.44403 | 122.081 | 0.21515 | 122.1588 | 120.0531 | 122.081 | -2.243 | -122.1588 | 119.8654 | 122.0032 | 119.8883 | 114.4363
1576.5 | 122.1725 | -119.8608 | 2.2614 | 0.0025177 | -0.013943 | -0.080079 | -0.0054837 | -0.035784 | -0.052731 | -0.041674 | 0.00094606 | -0.020108 | 0.056414 | 0.049894 | -0.21616 | -0.016419 | -0.022612 | -0.068665 | 0.07782 | -0.09613 | -0.068665 | 0.068665 | -0.054932 | -0.036621 | -5.571 | 2.2659 | -119.9249 | 2.1194 | -119.4763 | -119.7464 | -119.4443 | 119.7647 | -2.1835 | -2.33 | 119.9295 | 119.8242 | 119.8059 | 0.059509 | 0.041198 | -0.064087 | 0.004577 | -0.14191 | 0.38452 | 0.41656 | 0.11444 | 0.48065 | 0.17853 | 0.16479 | 0.027465 | 0.44861 | 122.0444 | 0.17395 | 122.1909 | 119.9387 | 122.1268 | -2.3575 | -122.1863 | 119.7922 | 121.9803 | 119.7922 | 114.2899
1578.2812 | 122.2366 | -119.9982 | 2.0828 | -0.0051118 | -0.010525 | -0.079865 | -0.0054837 | -0.031511 | -0.048672 | -0.041887 | -0.0021057 | -0.022031 | 0.056627 | 0.044767 | -0.21787 | -0.015137 | -0.025176 | -0.09613 | 0.082397 | -0.10071 | -0.086975 | 0.068665 | -0.082397 | -0.009155 | -5.6396 | 2.0782 | -120.0577 | 1.9958 | -119.6228 | -119.8654 | -119.5404 | 119.8975 | -2.0004 | -2.1698 | 120.0668 | 119.989 | 119.9158 | 0.091553 | 0.018311 | -0.059509 | -0.004578 | -0.086975 | 0.37537 | 0.45776 | 0.13275 | 0.51727 | 0.19226 | 0.16937 | 0.013733 | 0.43487 | 122.0535 | 0.18311 | 122.1359 | 120.0806 | 122.0764 | -2.1835 | -122.1405 | 119.9112 | 121.994 | 119.902 | 114.3585
1580.0469 | 122.1497 | -120.0531 | 2.0691 | 0.0025177 | -0.013943 | -0.082001 | -0.0054837 | -0.031298 | -0.050381 | -0.040605 | -0.0051575 | -0.01904 | 0.054705 | 0.046903 | -0.21979 | -0.015351 | -0.022398 | -0.12817 | 0.11902 | -0.12817 | -0.14191 | -0.018311 | -0.13275 | -0.07782 | -5.6854 | 2.0737 | -120.1309 | 1.9043 | -119.7235 | -119.9799 | -119.632 | 119.9249 | -1.9501 | -2.211 | 120.0348 | 119.9753 | 119.9203 | 0.050354 | -0.004577 | -0.077819 | 0.004577 | -0.1648 | 0.32959 | 0.42114 | 0.073243 | 0.49896 | 0.15106 | 0.10986 | -0.013733 | 0.40741 | 122.0352 | 0.24719 | 122.2046 | 120.1721 | 122.1268 | -2.1973 | -122.2 | 119.9112 | 121.9574 | 119.9249 | 114.3677
1581.7656 | 122.2458 | -120.0394 | 2.0737 | 0.0025177 | -0.012661 | -0.079438 | -0.0063381 | -0.032366 | -0.046749 | -0.04146 | -0.0021057 | -0.022031 | 0.055559 | 0.043912 | -0.21766 | -0.014924 | -0.022398 | -0.091553 | 0.07782 | -0.086975 | -0.082397 | 0.054932 | -0.082397 | -0.009155 | -5.7037 | 2.037 | -120.0943 | 1.973 | -119.6503 | -119.902 | -119.5724 | 119.9524 | -1.9958 | -2.1561 | 120.0943 | 120.0302 | 119.957 | 0.07782 | 0.004578 | -0.054931 | -0.036621 | -0.10071 | 0.3891 | 0.46692 | 0.13733 | 0.52185 | 0.19226 | 0.14191 | 0.004578 | 0.44403 | 122.0673 | 0.16479 | 122.1313 | 120.1172 | 122.0764 | -2.1606 | -122.168 | 119.957 | 122.0123 | 119.9478 | 114.3356
1583.5469 | 122.2137 | -120.2637 | 1.8951 | 0.010147 | -0.012875 | -0.079224 | -0.0020657 | -0.029802 | -0.049526 | -0.042528 | 0.00094606 | -0.016904 | 0.056414 | 0.054807 | -0.21766 | -0.015137 | -0.021758 | -0.10529 | 0.11902 | -0.13275 | -0.14648 | -0.013733 | -0.13275 | -0.073242 | -5.7632 | 1.8906 | -120.3094 | 1.7349 | -119.87 | -120.1355 | -119.8059 | 120.1309 | -1.7761 | -2.0416 | 120.2499 | 120.1904 | 120.1309 | 0.059509 | 0 | -0.045776 | -0.004578 | -0.16022 | 0.39368 | 0.45776 | 0.12817 | 0.50354 | 0.17395 | 0.11902 | -0.013733 | 0.43945 | 122.0444 | 0.25177 | 122.2 | 120.3827 | 122.1542 | -2.0279 | -122.2046 | 120.1172 | 121.9986 | 120.1584 | 114.5004
1585.3281 | 122.2641 | -120.0394 | 2.0782 | 0.0025177 | -0.012661 | -0.079438 | -0.0052701 | -0.030016 | -0.048458 | -0.041674 | 0.00094606 | -0.021604 | 0.059191 | 0.047544 | -0.21659 | -0.016846 | -0.021117 | -0.059509 | 0.073242 | -0.10071 | -0.041199 | 0.11902 | -0.064087 | 0.009155 | -5.7449 | 2.0599 | -120.1035 | 2.0325 | -119.6182 | -119.8563 | -119.5496 | 119.9387 | -2.005 | -2.1194 | 120.1584 | 120.0485 | 119.9753 | 0.10986 | 0.036621 | -0.064087 | -0.01831 | -0.045776 | 0.42114 | 0.48981 | 0.18311 | 0.55389 | 0.24719 | 0.21973 | 0.059509 | 0.48523 | 122.1359 | 0.17395 | 122.1634 | 120.1126 | 122.0993 | -2.179 | -122.1817 | 119.9982 | 122.0718 | 119.9799 | 114.2944
1587.0469 | 122.2366 | -120.1126 | 2.005 | -0.0051118 | -0.010952 | -0.078583 | -0.0039883 | -0.029375 | -0.050167 | -0.041033 | -0.0051575 | -0.018399 | 0.058763 | 0.039213 | -0.21872 | -0.013856 | -0.02133 | -0.10986 | 0.10071 | -0.11444 | -0.14648 | -0.009155 | -0.17395 | -0.068665 | -5.8502 | 2.0233 | -120.1859 | 1.9363 | -119.7556 | -120.0165 | -119.6594 | 119.9982 | -1.9043 | -2.1515 | 120.1035 | 120.0439 | 119.9387 | 0.045776 | -0.059509 | -0.073242 | 0.01831 | -0.068665 | 0.35706 | 0.45319 | 0.096131 | 0.52643 | 0.16937 | 0.10529 | -0.032043 | 0.4303 | 122.1222 | 0.21515 | 122.2092 | 120.2133 | 122.1359 | -2.1194 | -122.1909 | 119.9661 | 122.049 | 120.0027 | 114.2624
1588.8125 | 122.2641 | -120.5521 | 1.5472 | 0.017777 | -0.012661 | -0.080079 | -0.0061245 | -0.03258 | -0.049313 | -0.041887 | -0.0021057 | -0.022245 | 0.057268 | 0.043485 | -0.2183 | -0.016633 | -0.023039 | -0.086975 | 0.064087 | -0.086975 | -0.064087 | 0.064087 | -0.082397 | -0.013733 | -5.9189 | 1.5472 | -120.6573 | 1.4969 | -120.163 | -120.4147 | -120.0989 | 120.4651 | -1.4832 | -1.6113 | 120.6162 | 120.5383 | 120.4697 | 0.073242 | 0.004578 | -0.10529 | 0 | -0.050354 | 0.3891 | 0.45319 | 0.13733 | 0.55847 | 0.24262 | 0.15106 | 0.022888 | 0.49438 | 122.1542 | 0.15106 | 122.2046 | 120.6162 | 122.0993 | -1.6342 | -122.2046 | 120.488 | 122.049 | 120.4651 | 114.6332
1590.5312 | 122.3282 | -121.376 | 0.737 | -0.012741 | -0.012448 | -0.079011 | -0.0059109 | -0.029802 | -0.048886 | -0.039751 | 0.0039979 | -0.020108 | 0.057909 | 0.044126 | -0.21979 | -0.015137 | -0.020689 | -0.027466 | 0.068665 | -0.091553 | -0.009155 | 0.1236 | -0.050354 | 0.027466 | -5.9326 | 0.72784 | -121.431 | 0.73242 | -120.9366 | -121.2021 | -120.8496 | 121.2845 | -0.66834 | -0.74616 | 121.4996 | 121.4035 | 121.3257 | 0.11902 | 0.041199 | -0.054931 | -0.009156 | -0.004578 | 0.43945 | 0.52643 | 0.17395 | 0.58136 | 0.22888 | 0.21515 | 0.082398 | 0.49439 | 122.1634 | 0.16022 | 122.1588 | 121.4447 | 122.1039 | -0.82855 | -122.168 | 121.3669 | 122.1085 | 121.3486 | 115.4434
1592.25 | 122.3282 | -121.3989 | 0.70496 | -0.012741 | -0.0098843 | -0.079224 | -0.0054837 | -0.030657 | -0.049313 | -0.041674 | -0.0021057 | -0.022458 | 0.056627 | 0.045194 | -0.21958 | -0.014496 | -0.024962 | -0.036621 | 0.073242 | -0.07782 | -0.009155 | 0.14648 | -0.036621 | 0.032043 | -5.9601 | 0.71411 | -121.4584 | 0.70038 | -120.9549 | -121.2433 | -120.8954 | 121.3211 | -0.63171 | -0.71411 | 121.5454 | 121.431 | 121.3623 | 0.10986 | 0.041199 | -0.059509 | 0.009155 | -0.004578 | 0.44403 | 0.50354 | 0.15564 | 0.56305 | 0.21515 | 0.2243 | 0.068665 | 0.50354 | 122.1588 | 0.15106 | 122.1725 | 121.4722 | 122.113 | -0.78278 | -122.1634 | 121.3898 | 122.0993 | 121.3623 | 115.4388
1594.0156 | 122.3373 | -121.3989 | 0.70496 | -0.0051118 | -0.010739 | -0.076447 | -0.0035611 | -0.028948 | -0.050808 | -0.039537 | 0.00094606 | -0.020749 | 0.0562 | 0.041776 | -0.21958 | -0.015351 | -0.023253 | -0.036621 | 0.064087 | -0.07782 | -0.004578 | 0.14191 | -0.041199 | 0.027466 | -6.0196 | 0.70038 | -121.4493 | 0.72784 | -120.9595 | -121.2158 | -120.8817 | 121.3211 | -0.64087 | -0.70953 | 121.5408 | 121.4264 | 121.3577 | 0.10529 | 0.036621 | -0.050354 | -0.004578 | 0.022888 | 0.43945 | 0.51727 | 0.18311 | 0.56763 | 0.23346 | 0.21973 | 0.073242 | 0.48981 | 122.1771 | 0.14191 | 122.1497 | 121.463 | 122.0993 | -0.78278 | -122.1542 | 121.3943 | 122.1268 | 121.3623 | 115.3793
1595.7812 | 122.2916 | -121.431 | 0.72327 | -0.0051118 | -0.012448 | -0.077942 | -0.0042019 | -0.032793 | -0.050595 | -0.040392 | -0.0021057 | -0.02139 | 0.056414 | 0.046049 | -0.2168 | -0.017701 | -0.020049 | -0.10071 | 0.07782 | -0.07782 | -0.07782 | 0.064087 | -0.07782 | -0.009155 | -6.1523 | 0.71411 | -121.4905 | 0.63171 | -121.0281 | -121.2982 | -120.9549 | 121.3531 | -0.64545 | -0.80109 | 121.4951 | 121.4218 | 121.3531 | 0.068665 | 0 | -0.05951 | -0.009156 | -0.091553 | 0.40283 | 0.47607 | 0.13275 | 0.53558 | 0.19226 | 0.14191 | 0 | 0.46234 | 122.1222 | 0.15564 | 122.2046 | 121.5088 | 122.1451 | -0.80109 | -122.2137 | 121.3531 | 122.0627 | 121.3303 | 115.2786
1597.5781 | 122.3419 | -121.3943 | 0.71869 | 0.0025177 | -0.015652 | -0.08136 | -0.0076199 | -0.030016 | -0.050595 | -0.041033 | 0.00094606 | -0.019681 | 0.0562 | 0.043912 | -0.21894 | -0.015778 | -0.025603 | -0.054932 | 0.050354 | -0.07782 | 0 | 0.16022 | -0.009155 | 0.045776 | -6.1111 | 0.73242 | -121.4676 | 0.71411 | -120.9457 | -121.1929 | -120.8908 | 121.3165 | -0.66834 | -0.71869 | 121.5546 | 121.4401 | 121.3852 | 0.1236 | 0.068665 | -0.073242 | 0.013733 | -0.004578 | 0.44861 | 0.50354 | 0.20142 | 0.57678 | 0.27466 | 0.23804 | 0.07782 | 0.52185 | 122.1817 | 0.12817 | 122.2 | 121.4447 | 122.1268 | -0.79651 | -122.1863 | 121.3943 | 122.1085 | 121.3394 | 115.2832
1599.2969 | 122.3419 | -121.4127 | 0.70953 | -0.012741 | -0.0079617 | -0.076874 | -0.0056973 | -0.028307 | -0.048458 | -0.041033 | -0.0021057 | -0.02139 | 0.057054 | 0.047544 | -0.21915 | -0.01236 | -0.025603 | -0.022888 | 0.064087 | -0.082397 | 0.009155 | 0.12817 | -0.041199 | 0.013733 | -6.2119 | 0.70038 | -121.4539 | 0.70953 | -120.9732 | -121.2387 | -120.8954 | 121.3303 | -0.64545 | -0.70038 | 121.5408 | 121.4264 | 121.3715 | 0.09613 | 0.041198 | -0.041198 | -0.009156 | 0 | 0.43945 | 0.51727 | 0.17395 | 0.55847 | 0.21515 | 0.21057 | 0.091552 | 0.48065 | 122.1634 | 0.14648 | 122.1542 | 121.4767 | 122.113 | -0.79193 | -122.1634 | 121.4218 | 122.1222 | 121.3898 | 115.2008
1601.0625 | 122.3557 | -121.3943 | 0.73242 | 0.0025177 | -0.0094571 | -0.08136 | -0.0042019 | -0.029589 | -0.049099 | -0.03911 | -0.0021057 | -0.020108 | 0.054918 | 0.043485 | -0.21787 | -0.015778 | -0.025176 | -0.032043 | 0.073242 | -0.082397 | -0.013733 | 0.13275 | -0.054932 | 0.027466 | -6.3034 | 0.71411 | -121.4676 | 0.74158 | -120.9457 | -121.2158 | -120.8771 | 121.312 | -0.65918 | -0.74616 | 121.5271 | 121.4218 | 121.3394 | 0.10986 | 0.027465 | -0.073242 | -0.018311 | 0.009155 | 0.44861 | 0.51727 | 0.17853 | 0.59051 | 0.25177 | 0.21515 | 0.068664 | 0.52185 | 122.2092 | 0.15564 | 122.1817 | 121.4676 | 122.1085 | -0.81482 | -122.2 | 121.3806 | 122.1359 | 121.3623 | 115.0909
1602.8438 | 122.2733 | -121.3943 | 0.80109 | 0.0025177 | -0.012661 | -0.078156 | -0.0046291 | -0.031725 | -0.050167 | -0.038683 | 0.00094606 | -0.020108 | 0.056627 | 0.046049 | -0.22129 | -0.015565 | -0.028166 | -0.10986 | 0.11444 | -0.13275 | -0.10986 | 0 | -0.1236 | -0.059509 | -6.4133 | 0.8194 | -121.463 | 0.67749 | -121.0007 | -121.2708 | -120.9412 | 121.2616 | -0.68664 | -0.91095 | 121.3943 | 121.3348 | 121.2708 | 0.073242 | 0.009155 | -0.068665 | 0.018311 | -0.1236 | 0.39368 | 0.45319 | 0.1236 | 0.52185 | 0.19226 | 0.13275 | 0.022888 | 0.46234 | 122.1405 | 0.24719 | 122.2824 | 121.5088 | 122.2137 | -0.93384 | -122.2641 | 121.2845 | 122.0718 | 121.2845 | 114.9811
1604.625 | 122.3602 | -121.3623 | 0.80109 | -0.0051118 | -0.013089 | -0.081574 | -0.0078335 | -0.033434 | -0.051449 | -0.039751 | -0.0021057 | -0.021604 | 0.058123 | 0.049253 | -0.21808 | -0.015778 | -0.022398 | -0.041199 | 0.059509 | -0.10071 | 0 | 0.16937 | -0.013733 | 0.054932 | -6.395 | 0.7782 | -121.431 | 0.76446 | -120.8954 | -121.138 | -120.8313 | 121.2616 | -0.74158 | -0.80109 | 121.5317 | 121.4172 | 121.3486 | 0.15564 | 0.086975 | -0.068664 | -0.022888 | -0.036621 | 0.46692 | 0.53101 | 0.22431 | 0.59967 | 0.29297 | 0.27008 | 0.10071 | 0.53558 | 122.1954 | 0.16022 | 122.2092 | 121.4218 | 122.1405 | -0.90179 | -122.2321 | 121.3623 | 122.1268 | 121.3211 | 114.9673
1606.4062 | 122.2733 | -121.4813 | 0.71869 | -0.0051118 | -0.0086027 | -0.077302 | -0.0024929 | -0.02788 | -0.051663 | -0.042314 | 0.00094606 | -0.017545 | 0.0562 | 0.054594 | -0.21787 | -0.013856 | -0.022826 | -0.11902 | 0.11902 | -0.14191 | -0.14191 | -0.032043 | -0.17853 | -0.09613 | -6.5918 | 0.74616 | -121.5454 | 0.60425 | -121.1197 | -121.4127 | -121.0281 | 121.3394 | -0.59967 | -0.8606 | 121.4493 | 121.3852 | 121.3028 | 0.045777 | -0.036621 | -0.064087 | 0.027466 | -0.11444 | 0.36163 | 0.45319 | 0.068664 | 0.51727 | 0.13275 | 0.10986 | 0 | 0.42572 | 122.1497 | 0.26093 | 122.2916 | 121.6003 | 122.2275 | -0.8606 | -122.2641 | 121.3394 | 122.0856 | 121.3623 | 114.8895
1608.1875 | 122.3648 | -121.4493 | 0.70496 | 0.017777 | -0.015652 | -0.079438 | -0.0082607 | -0.034289 | -0.051022 | -0.040178 | -0.0021057 | -0.02139 | 0.057268 | 0.044553 | -0.21872 | -0.015778 | -0.02603 | -0.059509 | 0.059509 | -0.10529 | -0.004578 | 0.15564 | -0.004578 | 0.064087 | -6.4957 | 0.69122 | -121.5179 | 0.69122 | -120.9595 | -121.225 | -120.9274 | 121.344 | -0.64545 | -0.70953 | 121.6049 | 121.5134 | 121.4447 | 0.16937 | 0.10071 | -0.068664 | -0.013733 | -0.013733 | 0.48981 | 0.52185 | 0.2243 | 0.59051 | 0.29297 | 0.26093 | 0.10071 | 0.55847 | 122.2092 | 0.16479 | 122.2092 | 121.5088 | 122.1405 | -0.81024 | -122.2229 | 121.4447 | 122.1405 | 121.3898 | 114.9536
1609.9062 | 122.2778 | -121.4951 | 0.71869 | 0.017777 | -0.010525 | -0.079865 | -0.0033475 | -0.027025 | -0.048458 | -0.042742 | -0.0051575 | -0.020322 | 0.055986 | 0.048612 | -0.21787 | -0.015351 | -0.023894 | -0.11444 | 0.1236 | -0.14191 | -0.13275 | -0.022888 | -0.1236 | -0.064087 | -6.6879 | 0.72784 | -121.5683 | 0.56305 | -121.1105 | -121.3852 | -121.0464 | 121.3531 | -0.59509 | -0.85144 | 121.4722 | 121.431 | 121.3715 | 0.07782 | 0.018311 | -0.073242 | 0.009155 | -0.15564 | 0.38452 | 0.44861 | 0.10986 | 0.52185 | 0.1831 | 0.11902 | 0.009156 | 0.45776 | 122.1313 | 0.2655 | 122.2961 | 121.6187 | 122.2229 | -0.8606 | -122.287 | 121.3623 | 122.0581 | 121.3806 | 114.8071
1611.6875 | 122.2412 | -121.5363 | 0.70953 | -0.0051118 | -0.010525 | -0.080292 | -0.0067653 | -0.031511 | -0.04974 | -0.041246 | -0.0021057 | -0.020963 | 0.057268 | 0.046689 | -0.21808 | -0.015778 | -0.021971 | -0.082397 | 0.091553 | -0.10071 | -0.1236 | 0.022888 | -0.11444 | -0.050354 | -6.7703 | 0.72784 | -121.5775 | 0.54474 | -121.1334 | -121.4081 | -121.0922 | 121.4355 | -0.61798 | -0.83313 | 121.5591 | 121.4859 | 121.4218 | 0.050354 | -0.013733 | -0.041199 | 0.01831 | -0.1648 | 0.40283 | 0.44403 | 0.12817 | 0.48523 | 0.16937 | 0.1236 | -0.022888 | 0.44403 | 122.1222 | 0.19226 | 122.3053 | 121.6278 | 122.2641 | -0.81024 | -122.287 | 121.4127 | 122.081 | 121.4539 | 114.7659
1613.4688 | 122.3648 | -121.5042 | 0.69122 | 0.0025177 | -0.011166 | -0.079011 | -0.0056973 | -0.031298 | -0.048458 | -0.041887 | -0.0021057 | -0.019895 | 0.055132 | 0.042631 | -0.21766 | -0.01471 | -0.025389 | -0.10529 | 0.10529 | -0.10986 | -0.091553 | 0.050354 | -0.12817 | -0.050354 | -6.8207 | 0.68207 | -121.5637 | 0.65002 | -121.0876 | -121.3531 | -120.9778 | 121.3943 | -0.58594 | -0.78278 | 121.5546 | 121.4539 | 121.376 | 0.059509 | -0.018311 | -0.05951 | -0.009155 | -0.041199 | 0.41656 | 0.52643 | 0.15106 | 0.58594 | 0.21057 | 0.16022 | 0.01831 | 0.47607 | 122.2137 | 0.21515 | 122.2458 | 121.6095 | 122.1863 | -0.80109 | -122.2549 | 121.4127 | 122.1542 | 121.3989 | 114.6835
1615.1875 | 122.3465 | -121.5317 | 0.6546 | -0.012741 | -0.01138 | -0.077302 | -0.0065517 | -0.025103 | -0.046963 | -0.042528 | 0.00094606 | -0.020322 | 0.0562 | 0.042631 | -0.22022 | -0.016846 | -0.021117 | -0.10071 | 0.10071 | -0.11444 | -0.091553 | 0.022888 | -0.1236 | -0.054932 | -6.8756 | 0.66376 | -121.6095 | 0.63629 | -121.0968 | -121.3806 | -120.9961 | 121.4172 | -0.55389 | -0.74616 | 121.5546 | 121.4767 | 121.4081 | 0.059509 | -0.009155 | -0.07782 | 0.009155 | -0.01831 | 0.43488 | 0.53558 | 0.15106 | 0.6134 | 0.22888 | 0.13733 | 0.022888 | 0.5127 | 122.2458 | 0.21515 | 122.2733 | 121.6324 | 122.1954 | -0.76904 | -122.2641 | 121.4401 | 122.168 | 121.431 | 114.6561
1616.9531 | 122.406 | -121.5225 | 0.66376 | -0.0051118 | -0.01672 | -0.078583 | -0.0052701 | -0.033434 | -0.049313 | -0.040819 | -0.0051575 | -0.022885 | 0.055559 | 0.044767 | -0.21894 | -0.015565 | -0.022398 | -0.064087 | 0.068665 | -0.086975 | -0.009155 | 0.14648 | -0.009155 | 0.064087 | -6.7886 | 0.66376 | -121.5637 | 0.67291 | -121.0281 | -121.2662 | -120.9732 | 121.4355 | -0.59509 | -0.67291 | 121.669 | 121.5866 | 121.5134 | 0.15106 | 0.07782 | -0.041199 | 0 | 0.009156 | 0.49438 | 0.54932 | 0.25635 | 0.59051 | 0.29755 | 0.23346 | 0.07782 | 0.53558 | 122.2366 | 0.15564 | 122.2275 | 121.5912 | 122.1863 | -0.75073 | -122.2275 | 121.5134 | 122.1954 | 121.4584 | 114.7339
1618.7344 | 122.2961 | -121.5408 | 0.6958 | 0.010147 | -0.010525 | -0.078797 | -0.0035611 | -0.03322 | -0.048245 | -0.041674 | -0.0021057 | -0.018399 | 0.057054 | 0.054807 | -0.21744 | -0.01471 | -0.019621 | -0.11444 | 0.10529 | -0.13275 | -0.16022 | -0.013733 | -0.15564 | -0.086975 | -6.9534 | 0.70496 | -121.5866 | 0.58594 | -121.1609 | -121.4493 | -121.0602 | 121.4081 | -0.59052 | -0.85602 | 121.5271 | 121.4539 | 121.3852 | 0.045776 | -0.022889 | -0.045776 | 0.009155 | -0.10986 | 0.37994 | 0.48065 | 0.091553 | 0.52643 | 0.13733 | 0.11902 | -0.027466 | 0.42572 | 122.1725 | 0.23804 | 122.2916 | 121.6461 | 122.2458 | -0.82855 | -122.2824 | 121.3806 | 122.1268 | 121.4264 | 114.5874
1620.5312 | 122.3923 | -121.5134 | 0.6546 | 0.010147 | -0.013729 | -0.079224 | -0.0084743 | -0.031725 | -0.051876 | -0.038256 | -0.0021057 | -0.022245 | 0.058977 | 0.040281 | -0.21937 | -0.018128 | -0.022826 | -0.045776 | 0.045776 | -0.082397 | -0.004578 | 0.15106 | 0 | 0.045776 | -6.8115 | 0.63629 | -121.5775 | 0.62714 | -121.0739 | -121.3257 | -121.0052 | 121.431 | -0.60883 | -0.65918 | 121.6644 | 121.5591 | 121.5134 | 0.12817 | 0.082397 | -0.064087 | -0.01831 | -0.027466 | 0.43945 | 0.50812 | 0.18768 | 0.5722 | 0.25177 | 0.23346 | 0.077819 | 0.50354 | 122.2046 | 0.12817 | 122.2137 | 121.5591 | 122.1497 | -0.737 | -122.2321 | 121.5088 | 122.1405 | 121.4676 | 114.7018
1622.2812 | 122.3557 | -121.5775 | 0.62714 | -0.012741 | -0.012448 | -0.080079 | -0.0067653 | -0.034289 | -0.048245 | -0.043169 | -0.0021057 | -0.020749 | 0.056841 | 0.04434 | -0.21851 | -0.013856 | -0.023894 | -0.10071 | 0.082397 | -0.10529 | -0.073242 | 0.059509 | -0.10071 | -0.027466 | -6.9855 | 0.66834 | -121.6415 | 0.57678 | -121.1472 | -121.4218 | -121.0739 | 121.4722 | -0.54474 | -0.70038 | 121.637 | 121.55 | 121.4767 | 0.07782 | 0.004578 | -0.064087 | 0.041199 | -0.050354 | 0.4303 | 0.50354 | 0.15564 | 0.56763 | 0.21973 | 0.16479 | 0.032044 | 0.49439 | 122.2183 | 0.18768 | 122.3099 | 121.6599 | 122.2458 | -0.73242 | -122.2687 | 121.5042 | 122.1542 | 121.4767 | 114.592
1624.0625 | 122.2961 | -121.5866 | 0.68207 | 0.0025177 | -0.013089 | -0.079865 | -0.0050565 | -0.024675 | -0.049313 | -0.041887 | 0.0039979 | -0.016477 | 0.055986 | 0.041563 | -0.2183 | -0.013856 | -0.02368 | -0.086975 | 0.10529 | -0.14191 | -0.10986 | 0.018311 | -0.14648 | -0.082397 | -6.9809 | 0.70038 | -121.6278 | 0.53558 | -121.2112 | -121.4951 | -121.1197 | 121.4447 | -0.57678 | -0.79193 | 121.6049 | 121.5042 | 121.4401 | 0.05951 | -0.004577 | -0.041199 | 0.01831 | -0.14648 | 0.37537 | 0.46692 | 0.091553 | 0.50812 | 0.13275 | 0.16022 | 0.032044 | 0.41657 | 122.1634 | 0.24719 | 122.3282 | 121.6919 | 122.287 | -0.82398 | -122.3099 | 121.4767 | 122.1222 | 121.4996 | 114.6057
1625.8281 | 122.3373 | -121.6049 | 0.66834 | 0.0025177 | -0.01202 | -0.080292 | -0.0050565 | -0.030443 | -0.051449 | -0.03911 | -0.0051575 | -0.019681 | 0.057482 | 0.045194 | -0.21808 | -0.016205 | -0.02133 | -0.073242 | 0.086975 | -0.11902 | -0.09613 | 0.045776 | -0.09613 | -0.050354 | -6.9305 | 0.66376 | -121.6278 | 0.54932 | -121.17 | -121.4584 | -121.0922 | 121.4859 | -0.58136 | -0.76446 | 121.6507 | 121.5546 | 121.5088 | 0.068665 | 0.022889 | -0.022889 | -0.004578 | -0.11902 | 0.43487 | 0.51269 | 0.14648 | 0.53558 | 0.16937 | 0.16479 | 0.022889 | 0.45776 | 122.1771 | 0.20599 | 122.2916 | 121.6919 | 122.2687 | -0.78735 | -122.2961 | 121.5088 | 122.1542 | 121.5317 | 114.6744
1627.6094 | 122.3053 | -121.5775 | 0.68207 | -0.0051118 | -0.0098843 | -0.080079 | -0.0050565 | -0.028521 | -0.048672 | -0.042314 | 0.0039979 | -0.020749 | 0.057054 | 0.042203 | -0.21637 | -0.011719 | -0.022826 | -0.11444 | 0.11444 | -0.1236 | -0.15106 | -0.022888 | -0.17853 | -0.082397 | -7.0908 | 0.67291 | -121.637 | 0.54474 | -121.2296 | -121.4951 | -121.1105 | 121.4539 | -0.56763 | -0.83313 | 121.5546 | 121.4951 | 121.3989 | 0.041199 | -0.054932 | -0.059509 | -0.009155 | -0.13733 | 0.3479 | 0.46692 | 0.082398 | 0.52643 | 0.14191 | 0.10071 | -0.027466 | 0.40741 | 122.1817 | 0.23804 | 122.3099 | 121.6919 | 122.2504 | -0.80566 | -122.319 | 121.4264 | 122.1222 | 121.463 | 114.4867
1629.3906 | 122.4472 | -121.5042 | 0.6958 | 0.0025177 | -0.014798 | -0.080933 | -0.0093289 | -0.027025 | -0.048245 | -0.041246 | 0.0039979 | -0.021604 | 0.057695 | 0.041135 | -0.21872 | -0.015992 | -0.023253 | -0.068665 | 0.054932 | -0.086975 | -0.013733 | 0.14648 | 0 | 0.054932 | -6.9717 | 0.6958 | -121.5317 | 0.70496 | -121.0281 | -121.2799 | -120.9686 | 121.4172 | -0.64087 | -0.70953 | 121.6507 | 121.5591 | 121.5042 | 0.14191 | 0.086975 | -0.027466 | 0 | 0.009155 | 0.47607 | 0.53558 | 0.2243 | 0.56305 | 0.25177 | 0.23346 | 0.073242 | 0.50354 | 122.2366 | 0.14191 | 122.2275 | 121.5591 | 122.2 | -0.78278 | -122.2275 | 121.4905 | 122.2092 | 121.4355 | 114.5325
1631.1562 | 122.374 | -121.5225 | 0.71869 | -0.0051118 | -0.015011 | -0.080292 | -0.0063381 | -0.029589 | -0.050595 | -0.041674 | 0.00094606 | -0.019895 | 0.057054 | 0.050535 | -0.21659 | -0.017273 | -0.01898 | -0.054932 | 0.059509 | -0.086975 | -0.027466 | 0.11902 | -0.022888 | 0.027466 | -7.0633 | 0.70496 | -121.5912 | 0.63629 | -121.0831 | -121.3303 | -121.0236 | 121.4355 | -0.65918 | -0.74616 | 121.6415 | 121.55 | 121.4996 | 0.11444 | 0.064087 | -0.068665 | -0.013733 | -0.082397 | 0.43945 | 0.49896 | 0.19226 | 0.56763 | 0.26093 | 0.20599 | 0.059509 | 0.50812 | 122.2275 | 0.14648 | 122.2961 | 121.582 | 122.2275 | -0.80566 | -122.3099 | 121.4951 | 122.1588 | 121.4676 | 114.4592
1632.9375 | 122.4472 | -121.5042 | 0.70038 | -0.0051118 | -0.011166 | -0.077088 | -0.00099752 | -0.030016 | -0.048245 | -0.040178 | -0.0051575 | -0.022458 | 0.055559 | 0.044767 | -0.21915 | -0.014283 | -0.023894 | -0.032043 | 0.064087 | -0.082397 | -0.027466 | 0.10986 | -0.045776 | 0.032043 | -7.1182 | 0.70038 | -121.5775 | 0.70496 | -121.051 | -121.3348 | -120.9778 | 121.4218 | -0.63629 | -0.72784 | 121.6141 | 121.5363 | 121.4584 | 0.11444 | 0.036621 | -0.073243 | 0 | 0.004578 | 0.45319 | 0.52643 | 0.16937 | 0.59967 | 0.24262 | 0.19226 | 0.054931 | 0.52643 | 122.2824 | 0.14648 | 122.2778 | 121.5683 | 122.2046 | -0.78277 | -122.2778 | 121.4767 | 122.2092 | 121.4722 | 114.386
1634.7188 | 122.3282 | -121.5454 | 0.71869 | -0.0051118 | -0.010525 | -0.07837 | -0.0031337 | -0.030871 | -0.049954 | -0.037615 | 0.00094606 | -0.018827 | 0.055986 | 0.048398 | -0.21744 | -0.01471 | -0.025603 | -0.07782 | 0.09613 | -0.10986 | -0.09613 | 0.045776 | -0.10986 | -0.064087 | -7.2464 | 0.737 | -121.6141 | 0.62714 | -121.1655 | -121.4493 | -121.0693 | 121.4355 | -0.62256 | -0.81482 | 121.5912 | 121.4813 | 121.4355 | 0.045776 | 0 | -0.068665 | 0.018311 | -0.091553 | 0.37994 | 0.47607 | 0.09613 | 0.54474 | 0.16479 | 0.15564 | 0.013733 | 0.44861 | 122.2412 | 0.20599 | 122.3511 | 121.6415 | 122.2824 | -0.82855 | -122.3328 | 121.4493 | 122.1725 | 121.4676 | 114.299
1636.5 | 122.4472 | -121.5271 | 0.70953 | 0.017777 | -0.014584 | -0.08136 | -0.0082607 | -0.030016 | -0.051022 | -0.040392 | -0.0051575 | -0.020536 | 0.057482 | 0.044767 | -0.21808 | -0.018769 | -0.021117 | -0.050354 | 0.07782 | -0.07782 | -0.009155 | 0.16937 | 0.004578 | 0.073242 | -7.2876 | 0.71411 | -121.5637 | 0.6958 | -121.0327 | -121.2891 | -120.9732 | 121.4493 | -0.63171 | -0.71869 | 121.6965 | 121.6003 | 121.5317 | 0.15106 | 0.082398 | -0.036621 | 0.004577 | -0.013733 | 0.49439 | 0.55389 | 0.23804 | 0.59051 | 0.27466 | 0.24719 | 0.068665 | 0.53101 | 122.2595 | 0.15564 | 122.2778 | 121.6049 | 122.2412 | -0.78735 | -122.2733 | 121.5179 | 122.2229 | 121.4767 | 114.2395
1638.2188 | 122.3328 | -121.6141 | 0.6958 | 0.010147 | -0.014798 | -0.078156 | -0.0052701 | -0.03258 | -0.050167 | -0.040178 | -0.0021057 | -0.019467 | 0.058336 | 0.046689 | -0.21808 | -0.014924 | -0.018767 | -0.11444 | 0.11902 | -0.1236 | -0.14648 | -0.013733 | -0.13733 | -0.07782 | -7.4753 | 0.68665 | -121.6736 | 0.51727 | -121.2204 | -121.4813 | -121.1517 | 121.4905 | -0.57678 | -0.84228 | 121.6003 | 121.5363 | 121.4767 | 0.045776 | -0.013733 | -0.059509 | -0.009155 | -0.17853 | 0.39368 | 0.46234 | 0.13275 | 0.52185 | 0.19226 | 0.10986 | -0.022888 | 0.45319 | 122.1909 | 0.24261 | 122.3602 | 121.7331 | 122.3007 | -0.8194 | -122.3694 | 121.4676 | 122.1313 | 121.4996 | 114.1388
1640 | 122.4564 | -121.6415 | 0.62714 | 0.010147 | -0.014584 | -0.08136 | -0.0067653 | -0.034929 | -0.05209 | -0.042742 | 0.00094606 | -0.021176 | 0.057482 | 0.042844 | -0.22129 | -0.016205 | -0.026885 | -0.050354 | 0.073242 | -0.091553 | -0.013733 | 0.15564 | 0.004578 | 0.050354 | -7.37 | 0.62714 | -121.669 | 0.59967 | -121.1288 | -121.376 | -121.0648 | 121.55 | -0.55389 | -0.64087 | 121.7972 | 121.6919 | 121.6461 | 0.14191 | 0.096131 | -0.027465 | 0 | -0.027466 | 0.5127 | 0.57678 | 0.2655 | 0.60425 | 0.29297 | 0.24719 | 0.07782 | 0.54016 | 122.2687 | 0.16479 | 122.2961 | 121.7148 | 122.2687 | -0.71869 | -122.2961 | 121.6278 | 122.2412 | 121.5912 | 114.2715
1641.7344 | 122.4106 | -121.6278 | 0.63629 | 0.0025177 | -0.014584 | -0.079651 | -0.0067653 | -0.034502 | -0.050808 | -0.041033 | 0.0039979 | -0.020322 | 0.056414 | 0.038145 | -0.21958 | -0.01706 | -0.02603 | -0.10071 | 0.082397 | -0.086975 | -0.091553 | 0.054932 | -0.082397 | -0.018311 | -7.5256 | 0.62256 | -121.6599 | 0.55847 | -121.2112 | -121.4539 | -121.1105 | 121.5408 | -0.5539 | -0.72784 | 121.6827 | 121.6095 | 121.5454 | 0.068664 | 0.004578 | -0.032043 | -0.013733 | -0.07782 | 0.41657 | 0.51727 | 0.17395 | 0.54932 | 0.20599 | 0.14191 | -0.004578 | 0.44861 | 122.2183 | 0.16937 | 122.2824 | 121.7102 | 122.2504 | -0.72327 | -122.2961 | 121.5363 | 122.1863 | 121.5271 | 114.1022
1643.5312 | 122.3053 | -121.6553 | 0.67291 | 0.0025177 | -0.01138 | -0.079224 | -0.0052701 | -0.027025 | -0.049313 | -0.041674 | 0.0039979 | -0.01904 | 0.057054 | 0.046903 | -0.21937 | -0.014283 | -0.017485 | -0.10529 | 0.10986 | -0.12817 | -0.15106 | -0.064087 | -0.19684 | -0.10529 | -7.6447 | 0.67291 | -121.7285 | 0.49439 | -121.3348 | -121.6095 | -121.225 | 121.5271 | -0.56305 | -0.82398 | 121.5912 | 121.55 | 121.4584 | 0.022888 | -0.068664 | -0.073243 | 0 | -0.17853 | 0.32043 | 0.4303 | 0.045776 | 0.50354 | 0.11902 | 0.064087 | -0.022888 | 0.39368 | 122.2229 | 0.23804 | 122.4014 | 121.7651 | 122.3282 | -0.80109 | -122.4014 | 121.5042 | 122.1497 | 121.55 | 114.0106
1645.2656 | 122.406 | -121.6278 | 0.61798 | -0.012741 | -0.013089 | -0.077942 | -0.0059109 | -0.029589 | -0.050808 | -0.042742 | -0.0021057 | -0.022885 | 0.059404 | 0.040922 | -0.21808 | -0.016419 | -0.020689 | -0.09613 | 0.064087 | -0.068665 | -0.07782 | 0.064087 | -0.086975 | -0.013733 | -7.5897 | 0.62714 | -121.701 | 0.56305 | -121.2204 | -121.4813 | -121.1243 | 121.5591 | -0.55389 | -0.6958 | 121.6919 | 121.6141 | 121.5408 | 0.054932 | -0.01831 | -0.073242 | 0.009155 | -0.054932 | 0.40741 | 0.50354 | 0.14648 | 0.57678 | 0.21973 | 0.13275 | -0.009155 | 0.48065 | 122.2641 | 0.13275 | 122.3282 | 121.6919 | 122.2549 | -0.68665 | -122.319 | 121.55 | 122.1909 | 121.5317 | 114.0381
1647.0469 | 122.3831 | -121.6553 | 0.65918 | 0.0025177 | -0.012448 | -0.07837 | -0.0048427 | -0.027239 | -0.052517 | -0.040605 | -0.0051575 | -0.020108 | 0.058336 | 0.051176 | -0.22065 | -0.012147 | -0.021117 | -0.09613 | 0.10071 | -0.12817 | -0.11444 | 0.018311 | -0.10529 | -0.050354 | -7.576 | 0.63171 | -121.7056 | 0.53558 | -121.2341 | -121.5225 | -121.1655 | 121.5271 | -0.55847 | -0.77362 | 121.6736 | 121.6049 | 121.55 | 0.07782 | 0.022888 | -0.050354 | -0.027466 | -0.1236 | 0.42114 | 0.48981 | 0.13275 | 0.54016 | 0.18311 | 0.14649 | 0.013733 | 0.4715 | 122.2412 | 0.22888 | 122.3373 | 121.756 | 122.287 | -0.78735 | -122.3648 | 121.5408 | 122.1909 | 121.5591 | 114.0793
1648.7812 | 122.4701 | -121.5729 | 0.64545 | -0.0051118 | -0.010739 | -0.078797 | -0.0039883 | -0.027666 | -0.048031 | -0.042314 | 0.00094606 | -0.022458 | 0.0562 | 0.044767 | -0.2183 | -0.016205 | -0.022185 | -0.041199 | 0.059509 | -0.07782 | -0.036621 | 0.12817 | -0.041199 | 0.018311 | -7.5485 | 0.65918 | -121.6461 | 0.65002 | -121.138 | -121.4081 | -121.0464 | 121.4951 | -0.58594 | -0.68207 | 121.701 | 121.5912 | 121.5317 | 0.096131 | 0.036621 | -0.073242 | 0.013733 | 0.004577 | 0.43488 | 0.52643 | 0.16479 | 0.59967 | 0.23804 | 0.20599 | 0.041199 | 0.50812 | 122.2961 | 0.13733 | 122.3053 | 121.6324 | 122.2321 | -0.72327 | -122.2916 | 121.5363 | 122.2229 | 121.5317 | 114.0244
1650.5156 | 122.4564 | -121.5958 | 0.64545 | -0.02037 | -0.012875 | -0.078583 | -0.0061245 | -0.03322 | -0.04739 | -0.040605 | -0.0051575 | -0.020749 | 0.057482 | 0.043485 | -0.21872 | -0.015137 | -0.025176 | -0.054932 | 0.054932 | -0.07782 | -0.013733 | 0.14648 | -0.036621 | 0.036621 | -7.5897 | 0.62714 | -121.6553 | 0.64545 | -121.1517 | -121.4355 | -121.0602 | 121.5179 | -0.59052 | -0.65918 | 121.7422 | 121.6324 | 121.5591 | 0.11444 | 0.041199 | -0.059509 | -0.018311 | 0 | 0.44403 | 0.53558 | 0.16022 | 0.59509 | 0.21973 | 0.2243 | 0.064087 | 0.50354 | 122.3007 | 0.13275 | 122.2824 | 121.6507 | 122.2229 | -0.72327 | -122.3007 | 121.582 | 122.2412 | 121.5408 | 114.006
1652.2969 | 122.4289 | -121.6049 | 0.67291 | -0.012741 | -0.013089 | -0.077302 | -0.0050565 | -0.030443 | -0.04974 | -0.042101 | -0.0021057 | -0.020963 | 0.055559 | 0.044553 | -0.21894 | -0.018555 | -0.022185 | -0.07782 | 0.073242 | -0.086975 | -0.050354 | 0.10071 | -0.091553 | -0.009155 | -7.6492 | 0.64545 | -121.6827 | 0.6134 | -121.1884 | -121.4401 | -121.106 | 121.5179 | -0.59967 | -0.72327 | 121.7056 | 121.5958 | 121.5134 | 0.07782 | -0.004578 | -0.07782 | -0.027466 | -0.05951 | 0.41656 | 0.49896 | 0.16479 | 0.57678 | 0.24261 | 0.18768 | 0.036621 | 0.49438 | 122.2961 | 0.16022 | 122.3282 | 121.6782 | 122.2504 | -0.75989 | -122.3557 | 121.5546 | 122.2183 | 121.5271 | 113.9557
1654.0156 | 122.3511 | -121.6232 | 0.71869 | -0.0051118 | -0.014798 | -0.07837 | -0.0054837 | -0.032152 | -0.050381 | -0.041674 | 0.00094606 | -0.01904 | 0.056841 | 0.048398 | -0.21915 | -0.015137 | -0.021758 | -0.13275 | 0.10986 | -0.14191 | -0.1236 | -0.004578 | -0.12817 | -0.073242 | -7.7225 | 0.72327 | -121.6736 | 0.52185 | -121.2708 | -121.5179 | -121.1792 | 121.4813 | -0.60883 | -0.84229 | 121.6187 | 121.55 | 121.4951 | 0.068665 | 0.013733 | -0.050354 | 0.004578 | -0.19684 | 0.35248 | 0.44403 | 0.10529 | 0.49439 | 0.15564 | 0.13733 | 0.018311 | 0.40283 | 122.1954 | 0.25177 | 122.3969 | 121.7331 | 122.3465 | -0.8606 | -122.3923 | 121.4996 | 122.1451 | 121.4905 | 113.9008
1655.7969 | 122.3969 | -120.9183 | 1.4008 | -0.0051118 | -0.012234 | -0.077942 | -0.0039883 | -0.030657 | -0.04974 | -0.041246 | 0.00094606 | -0.018827 | 0.057268 | 0.04968 | -0.21787 | -0.012147 | -0.020903 | -0.10529 | 0.11444 | -0.1236 | -0.14648 | -0.009155 | -0.1831 | -0.09613 | -7.7042 | 1.3962 | -120.9778 | 1.2772 | -120.5475 | -120.813 | -120.433 | 120.7947 | -1.2863 | -1.5472 | 120.9091 | 120.8221 | 120.7352 | 0.027466 | -0.059509 | -0.059509 | -0.004578 | -0.1236 | 0.37079 | 0.48523 | 0.10529 | 0.54474 | 0.16479 | 0.11444 | -0.022888 | 0.4303 | 122.2549 | 0.23804 | 122.374 | 121.0327 | 122.3145 | -1.5244 | -122.3785 | 120.7718 | 122.1954 | 120.813 | 113.2141
1657.5938 | 122.438 | -120.9732 | 1.3138 | -0.0051118 | -0.015225 | -0.07837 | -0.0048427 | -0.03258 | -0.048886 | -0.041674 | -0.0021057 | -0.022672 | 0.055773 | 0.043272 | -0.2183 | -0.016633 | -0.021117 | -0.07782 | 0.073242 | -0.09613 | -0.07782 | 0.086975 | -0.082397 | -0.022888 | -7.7774 | 1.3184 | -121.0098 | 1.2451 | -120.5566 | -120.8176 | -120.4605 | 120.8771 | -1.2405 | -1.3916 | 121.0602 | 120.9503 | 120.8908 | 0.073242 | 0.013733 | -0.036621 | 0.004577 | -0.068665 | 0.41657 | 0.5127 | 0.15564 | 0.54932 | 0.19226 | 0.1831 | 0.01831 | 0.45319 | 122.2549 | 0.16937 | 122.3282 | 121.0464 | 122.2916 | -1.4099 | -122.3236 | 120.8954 | 122.2183 | 120.8954 | 113.1958
1659.3125 | 122.3511 | -121.019 | 1.3184 | 0.010147 | -0.010952 | -0.077088 | -0.0037747 | -0.030016 | -0.04974 | -0.041033 | 0.00094606 | -0.01669 | 0.057482 | 0.049467 | -0.21787 | -0.013215 | -0.022826 | -0.064087 | 0.091553 | -0.11902 | -0.12817 | -0.009155 | -0.16479 | -0.10986 | -7.8506 | 1.3275 | -121.0648 | 1.1444 | -120.6757 | -120.9549 | -120.575 | 120.9 | -1.2268 | -1.4465 | 121.0098 | 120.9091 | 120.8542 | 0.009156 | -0.045776 | -0.045776 | 0.009156 | -0.17395 | 0.34332 | 0.44403 | 0.064087 | 0.48981 | 0.10986 | 0.10986 | -0.009155 | 0.3891 | 122.2092 | 0.21057 | 122.3923 | 121.1105 | 122.3465 | -1.4374 | -122.3831 | 120.8908 | 122.1634 | 120.9549 | 113.1683
1661.0938 | 122.438 | -120.9869 | 1.3 | 0.010147 | -0.015011 | -0.079224 | -0.0076199 | -0.03023 | -0.05209 | -0.040605 | -0.0021057 | -0.022245 | 0.055986 | 0.050748 | -0.2183 | -0.015778 | -0.023894 | -0.064087 | 0.064087 | -0.09613 | -0.018311 | 0.13275 | -0.022888 | 0.041199 | -7.8186 | 1.2863 | -121.0556 | 1.2131 | -120.5566 | -120.8084 | -120.488 | 120.8908 | -1.236 | -1.3184 | 121.1197 | 121.0281 | 120.9641 | 0.13733 | 0.073242 | -0.068665 | -0.013733 | -0.086975 | 0.4303 | 0.49896 | 0.17853 | 0.56763 | 0.24719 | 0.22888 | 0.077819 | 0.49896 | 122.2687 | 0.16022 | 122.3419 | 121.051 | 122.2733 | -1.3962 | -122.3557 | 120.9686 | 122.2 | 120.9229 | 113.1683
1662.875 | 122.4243 | -121.051 | 1.2726 | -0.0051118 | -0.011807 | -0.079651 | -0.0031337 | -0.029589 | -0.048672 | -0.039537 | 0.0070497 | -0.020108 | 0.058123 | 0.049253 | -0.21808 | -0.013642 | -0.025389 | -0.11444 | 0.11444 | -0.10986 | -0.13275 | 0.018311 | -0.17395 | -0.082397 | -7.9514 | 1.2589 | -121.0922 | 1.1856 | -120.6207 | -120.9045 | -120.5292 | 120.9412 | -1.1581 | -1.4053 | 121.0693 | 120.9686 | 120.8771 | 0.027466 | -0.064087 | -0.041199 | -0.013733 | -0.086975 | 0.4303 | 0.52185 | 0.14648 | 0.56305 | 0.18768 | 0.12817 | -0.022888 | 0.4715 | 122.2778 | 0.2243 | 122.3511 | 121.1655 | 122.3099 | -1.3824 | -122.3648 | 120.9183 | 122.2366 | 120.9366 | 113.0997
1664.5938 | 122.3877 | -122.0123 | 0.33875 | -0.0051118 | -0.015011 | -0.079865 | -0.0061245 | -0.029802 | -0.050595 | -0.039537 | 0.00094606 | -0.023313 | 0.055773 | 0.040708 | -0.21531 | -0.015992 | -0.022398 | -0.07782 | 0.068665 | -0.10071 | -0.059509 | 0.10071 | -0.054932 | 0.013733 | -8.0383 | 0.33417 | -122.049 | 0.1831 | -121.5912 | -121.8384 | -121.5271 | 121.9116 | -0.27008 | -0.39825 | 122.113 | 122.0261 | 121.9574 | 0.11444 | 0.045776 | -0.036621 | -0.004578 | -0.15564 | 0.42114 | 0.48523 | 0.17395 | 0.52185 | 0.21057 | 0.20142 | 0.041199 | 0.45776 | 122.2321 | 0.16937 | 122.3831 | 122.081 | 122.3465 | -0.43945 | -122.3877 | 121.9528 | 122.1954 | 121.9345 | 113.974
1666.3125 | 122.3877 | -122.0306 | 0.37537 | 0.0025177 | -0.012661 | -0.081574 | -0.0059109 | -0.031511 | -0.050808 | -0.042528 | -0.0021057 | -0.019254 | 0.058336 | 0.044126 | -0.21979 | -0.017273 | -0.023467 | -0.12817 | 0.10529 | -0.13733 | -0.15564 | -0.009155 | -0.14648 | -0.064087 | -8.1619 | 0.36163 | -122.0718 | 0.17395 | -121.6461 | -121.9162 | -121.5454 | 121.8933 | -0.27008 | -0.53101 | 122.0215 | 121.9666 | 121.8842 | 0.073242 | -0.009155 | -0.041198 | -0.013733 | -0.20142 | 0.38452 | 0.48523 | 0.11444 | 0.52643 | 0.15564 | 0.12817 | -0.018311 | 0.42572 | 122.2458 | 0.24262 | 122.4335 | 122.1359 | 122.3923 | -0.5127 | -122.4472 | 121.875 | 122.2046 | 121.9025 | 113.8687
1668.0938 | 122.4243 | -121.9391 | 0.40283 | 0.0025177 | -0.013516 | -0.080933 | -0.0033475 | -0.033648 | -0.049526 | -0.040605 | 0.00094606 | -0.01904 | 0.056841 | 0.050321 | -0.21723 | -0.015351 | -0.027098 | -0.082397 | 0.091553 | -0.13275 | -0.10071 | 0.045776 | -0.091553 | -0.050354 | -8.0887 | 0.43488 | -121.9849 | 0.31586 | -121.5134 | -121.7926 | -121.4081 | 121.8063 | -0.31128 | -0.50354 | 121.9849 | 121.8887 | 121.8475 | 0.082397 | 0.041198 | -0.045776 | 0.032043 | -0.086975 | 0.42572 | 0.53101 | 0.14648 | 0.57678 | 0.19226 | 0.17853 | 0.032043 | 0.4715 | 122.3007 | 0.2243 | 122.4197 | 122.0306 | 122.374 | -0.53558 | -122.3877 | 121.8384 | 122.2549 | 121.8567 | 113.8504
1669.875 | 122.3648 | -121.8521 | 0.53101 | 0.0025177 | -0.01437 | -0.078156 | -0.0056973 | -0.029589 | -0.051663 | -0.040819 | -0.0051575 | -0.018827 | 0.059191 | 0.040281 | -0.21872 | -0.015778 | -0.020476 | -0.13733 | 0.11902 | -0.11902 | -0.16022 | -0.009155 | -0.15106 | -0.07782 | -8.226 | 0.52643 | -121.9299 | 0.35248 | -121.4676 | -121.7331 | -121.3806 | 121.7331 | -0.41199 | -0.69122 | 121.843 | 121.7743 | 121.7011 | 0.041199 | -0.032043 | -0.07782 | -0.004578 | -0.17853 | 0.38452 | 0.4715 | 0.11902 | 0.54932 | 0.19684 | 0.10986 | -0.041198 | 0.46234 | 122.2824 | 0.23804 | 122.4564 | 121.9711 | 122.3785 | -0.65002 | -122.4609 | 121.6919 | 122.2046 | 121.7148 | 113.6261
1671.6562 | 122.5067 | -121.9757 | 0.31586 | -0.012741 | -0.010525 | -0.076447 | -0.0069791 | -0.034716 | -0.049526 | -0.04146 | 0.00094606 | -0.01904 | 0.055986 | 0.042417 | -0.21808 | -0.014924 | -0.024748 | -0.045776 | 0.059509 | -0.09613 | -0.027466 | 0.11902 | -0.059509 | 0 | -8.1528 | 0.3067 | -122.0398 | 0.31128 | -121.5179 | -121.7926 | -121.3898 | 121.8796 | -0.25635 | -0.34332 | 122.0947 | 121.9757 | 121.9162 | 0.09613 | 0.036621 | -0.064087 | -0.009155 | -0.004578 | 0.45776 | 0.58594 | 0.1831 | 0.65002 | 0.24719 | 0.21515 | 0.068664 | 0.52185 | 122.3511 | 0.15564 | 122.3465 | 122.0352 | 122.2824 | -0.41199 | -122.3557 | 121.9482 | 122.287 | 121.9299 | 113.8229
1673.3906 | 122.5204 | -121.8063 | 0.4715 | -0.0051118 | -0.013516 | -0.078797 | -0.0069791 | -0.03322 | -0.050595 | -0.042742 | -0.0021057 | -0.021817 | 0.055986 | 0.045408 | -0.21979 | -0.016846 | -0.024962 | -0.09613 | 0.07782 | -0.09613 | -0.027466 | 0.13275 | -0.032043 | 0.059509 | -8.1894 | 0.48065 | -121.8658 | 0.48523 | -121.3303 | -121.5866 | -121.2433 | 121.7102 | -0.39368 | -0.49896 | 121.9391 | 121.8658 | 121.7743 | 0.15564 | 0.064087 | -0.05951 | 0.009155 | 0.013732 | 0.47607 | 0.56305 | 0.21973 | 0.62256 | 0.27924 | 0.22888 | 0.068664 | 0.53558 | 122.3511 | 0.17395 | 122.3465 | 121.8842 | 122.287 | -0.56763 | -122.3373 | 121.7789 | 122.2916 | 121.7102 | 113.6169
1675.1719 | 122.5113 | -121.7651 | 0.52185 | -0.0051118 | -0.0096707 | -0.078797 | -0.0033475 | -0.030443 | -0.047817 | -0.037615 | -0.0021057 | -0.021817 | 0.057695 | 0.047544 | -0.21872 | -0.011506 | -0.024535 | -0.050354 | 0.082397 | -0.091553 | -0.036621 | 0.10986 | -0.059509 | 0 | -8.2581 | 0.50812 | -121.8384 | 0.52643 | -121.312 | -121.6095 | -121.2158 | 121.6736 | -0.43945 | -0.55847 | 121.875 | 121.7651 | 121.7056 | 0.091553 | 0.032044 | -0.073242 | -0.013733 | 0.004577 | 0.45319 | 0.54932 | 0.15564 | 0.62256 | 0.22888 | 0.20142 | 0.054932 | 0.52643 | 122.3648 | 0.17395 | 122.3465 | 121.8475 | 122.2733 | -0.6134 | -122.3602 | 121.7285 | 122.2916 | 121.7148 | 113.5071
1676.9531 | 122.4701 | -121.8475 | 0.50354 | -0.0051118 | -0.012661 | -0.078797 | -0.0042019 | -0.031725 | -0.052517 | -0.038042 | -0.0021057 | -0.020108 | 0.056414 | 0.047117 | -0.22065 | -0.016205 | -0.020476 | -0.064087 | 0.059509 | -0.086975 | -0.045776 | 0.1236 | -0.050354 | 0.032043 | -8.3679 | 0.48981 | -121.8613 | 0.45776 | -121.3989 | -121.6461 | -121.2891 | 121.7606 | -0.44403 | -0.54932 | 121.9711 | 121.8796 | 121.7972 | 0.11902 | 0.036621 | -0.013733 | -0.013733 | -0.045776 | 0.44861 | 0.55847 | 0.20142 | 0.5722 | 0.21515 | 0.21057 | 0.041199 | 0.46234 | 122.319 | 0.14648 | 122.3511 | 121.907 | 122.3373 | -0.59052 | -122.3648 | 121.8018 | 122.3053 | 121.7834 | 113.4796
1678.7656 | 122.3969 | -121.8567 | 0.51727 | -0.0051118 | -0.014584 | -0.08136 | -0.0052701 | -0.032152 | -0.048886 | -0.040178 | 0.00094606 | -0.01904 | 0.058763 | 0.046903 | -0.22107 | -0.014924 | -0.021544 | -0.12817 | 0.10986 | -0.10986 | -0.12817 | -0.013733 | -0.13733 | -0.054932 | -8.4824 | 0.50812 | -121.9254 | 0.34332 | -121.4813 | -121.7468 | -121.4035 | 121.7468 | -0.40741 | -0.64545 | 121.843 | 121.8018 | 121.7194 | 0.054931 | -0.027466 | -0.068665 | -0.009155 | -0.17395 | 0.37537 | 0.45319 | 0.10986 | 0.52185 | 0.17853 | 0.09613 | -0.018311 | 0.44403 | 122.2687 | 0.21973 | 122.4335 | 121.9666 | 122.3648 | -0.62714 | -122.4426 | 121.7285 | 122.2 | 121.7285 | 113.3743
1680.4844 | 122.5067 | -121.6782 | 0.65002 | -0.0051118 | -0.016293 | -0.080079 | -0.0074063 | -0.031725 | -0.049526 | -0.042314 | -0.0021057 | -0.020963 | 0.0562 | 0.045621 | -0.21659 | -0.015565 | -0.02368 | -0.11444 | 0.082397 | -0.10071 | -0.073242 | 0.073242 | -0.064087 | 0.004578 | -8.4869 | 0.64087 | -121.7331 | 0.59052 | -121.2341 | -121.4767 | -121.138 | 121.5775 | -0.56763 | -0.72327 | 121.7514 | 121.6827 | 121.6141 | 0.10529 | 0.036621 | -0.054931 | -0.009155 | -0.059509 | 0.44403 | 0.54016 | 0.20142 | 0.59509 | 0.25635 | 0.17395 | 0.027466 | 0.49896 | 122.3236 | 0.18311 | 122.374 | 121.7606 | 122.319 | -0.75073 | -122.3831 | 121.6049 | 122.2687 | 121.5637 | 113.1912
1682.25 | 122.5342 | -121.701 | 0.63171 | 0.010147 | -0.013729 | -0.080719 | -0.0067653 | -0.032366 | -0.048458 | -0.040178 | 0.00094606 | -0.022031 | 0.056627 | 0.03964 | -0.21744 | -0.016633 | -0.025603 | -0.073242 | 0.054932 | -0.086975 | -0.032043 | 0.11444 | -0.022888 | 0.054932 | -8.4778 | 0.64087 | -121.756 | 0.61798 | -121.1975 | -121.463 | -121.1288 | 121.6141 | -0.57678 | -0.66376 | 121.8155 | 121.756 | 121.6782 | 0.14191 | 0.064087 | -0.054931 | 0.009155 | -0.013733 | 0.50354 | 0.5722 | 0.23804 | 0.62714 | 0.29297 | 0.20142 | 0.054932 | 0.55847 | 122.374 | 0.14191 | 122.3969 | 121.756 | 122.3419 | -0.71869 | -122.3877 | 121.669 | 122.319 | 121.6278 | 113.2233
1683.9688 | 122.438 | -121.7422 | 0.63629 | 0.0025177 | -0.012661 | -0.080719 | -0.0052701 | -0.034929 | -0.051663 | -0.038683 | -0.0051575 | -0.018186 | 0.055132 | 0.046689 | -0.21915 | -0.015137 | -0.024535 | -0.10071 | 0.091553 | -0.13733 | -0.10071 | 0.022888 | -0.10986 | -0.050354 | -8.606 | 0.66376 | -121.7606 | 0.53101 | -121.2982 | -121.5958 | -121.2158 | 121.6049 | -0.54474 | -0.737 | 121.7651 | 121.6919 | 121.6324 | 0.086975 | 0.027466 | -0.01831 | 0.027465 | -0.10529 | 0.44403 | 0.52643 | 0.14648 | 0.54474 | 0.16479 | 0.16022 | 0.036621 | 0.46234 | 122.2916 | 0.22888 | 122.4243 | 121.8338 | 122.406 | -0.77362 | -122.3969 | 121.6415 | 122.2733 | 121.6415 | 113.1363
1685.7656 | 122.4472 | -121.7194 | 0.6546 | 0.0025177 | -0.0096707 | -0.078583 | -0.0039883 | -0.028093 | -0.051022 | -0.041246 | 0.0039979 | -0.017758 | 0.059404 | 0.048398 | -0.22022 | -0.015992 | -0.023253 | -0.073242 | 0.10071 | -0.1236 | -0.09613 | 0.050354 | -0.10986 | -0.036621 | -8.6472 | 0.67749 | -121.7651 | 0.56305 | -121.2891 | -121.55 | -121.2112 | 121.5958 | -0.55389 | -0.75073 | 121.7697 | 121.6827 | 121.6095 | 0.086975 | 0.013733 | -0.045777 | 0.022888 | -0.091553 | 0.4303 | 0.50812 | 0.16937 | 0.55389 | 0.21515 | 0.17395 | 0.027466 | 0.47607 | 122.3282 | 0.2243 | 122.4426 | 121.8201 | 122.3969 | -0.7782 | -122.4197 | 121.6232 | 122.2824 | 121.6461 | 113.0722
1687.5625 | 122.3923 | -121.7468 | 0.64545 | -0.0051118 | -0.010311 | -0.077729 | -0.0048427 | -0.031725 | -0.048886 | -0.041674 | 0.00094606 | -0.019681 | 0.058336 | 0.052457 | -0.21958 | -0.012787 | -0.023894 | -0.10986 | 0.11444 | -0.10986 | -0.12817 | -0.004578 | -0.16479 | -0.091553 | -8.844 | 0.64087 | -121.8063 | 0.46692 | -121.3943 | -121.669 | -121.2891 | 121.637 | -0.53101 | -0.77362 | 121.7422 | 121.6553 | 121.582 | 0.01831 | -0.054932 | -0.059509 | -0.004578 | -0.17853 | 0.35248 | 0.45776 | 0.07782 | 0.51727 | 0.13733 | 0.10529 | -0.018311 | 0.41199 | 122.2733 | 0.2243 | 122.4472 | 121.8613 | 122.3877 | -0.75531 | -122.4518 | 121.6187 | 122.2137 | 121.637 | 112.9028
1689.3281 | 122.4106 | -121.7468 | 0.64087 | 0.010147 | -0.011593 | -0.080506 | -0.0037747 | -0.030871 | -0.050167 | -0.040819 | -0.0051575 | -0.016904 | 0.058977 | 0.050962 | -0.2168 | -0.014924 | -0.021971 | -0.1236 | 0.10071 | -0.14648 | -0.16937 | -0.064087 | -0.20142 | -0.09613 | -8.8943 | 0.64545 | -121.8201 | 0.46234 | -121.4127 | -121.6919 | -121.2982 | 121.6003 | -0.54016 | -0.81024 | 121.6827 | 121.6507 | 121.5454 | 0.050354 | -0.054932 | -0.073242 | 0.004578 | -0.17853 | 0.33417 | 0.44861 | 0.054931 | 0.52185 | 0.12817 | 0.082397 | -0.022889 | 0.40741 | 122.2824 | 0.24719 | 122.4655 | 121.8475 | 122.3923 | -0.78735 | -122.4609 | 121.5775 | 122.2092 | 121.6232 | 112.8525
1691.0938 | 122.5204 | -121.6965 | 0.61798 | -0.012741 | -0.011807 | -0.079224 | -0.0067653 | -0.031939 | -0.049954 | -0.039965 | -0.0021057 | -0.019895 | 0.057482 | 0.04434 | -0.21787 | -0.011292 | -0.01898 | -0.10986 | 0.10071 | -0.12817 | -0.10071 | 0.036621 | -0.1236 | -0.059509 | -8.8943 | 0.62256 | -121.7743 | 0.58136 | -121.2662 | -121.5591 | -121.1746 | 121.5683 | -0.51727 | -0.71869 | 121.7331 | 121.637 | 121.5729 | 0.068665 | 0.004578 | -0.07782 | 0.004578 | -0.036621 | 0.4303 | 0.52185 | 0.13733 | 0.59967 | 0.21515 | 0.1648 | 0.027466 | 0.50812 | 122.3557 | 0.22888 | 122.3969 | 121.7972 | 122.319 | -0.74616 | -122.3923 | 121.5958 | 122.2778 | 121.5866 | 112.8021
1692.8125 | 122.5525 | -121.7331 | 0.59052 | -0.0051118 | -0.010739 | -0.077942 | -0.0039883 | -0.031298 | -0.048458 | -0.041033 | -0.0021057 | -0.020963 | 0.057482 | 0.048612 | -0.21808 | -0.01471 | -0.024321 | -0.036621 | 0.064087 | -0.10529 | -0.032043 | 0.1236 | -0.045776 | 0.013733 | -8.8303 | 0.59509 | -121.7743 | 0.59967 | -121.257 | -121.5317 | -121.1563 | 121.6278 | -0.52643 | -0.62256 | 121.8567 | 121.7468 | 121.6873 | 0.11902 | 0.05951 | -0.041199 | 0.004578 | 0.009155 | 0.47607 | 0.57678 | 0.20142 | 0.61798 | 0.24262 | 0.22888 | 0.073243 | 0.51727 | 122.374 | 0.16937 | 122.3694 | 121.7972 | 122.3282 | -0.6958 | -122.3648 | 121.701 | 122.3328 | 121.6965 | 112.9028
1694.5312 | 122.5296 | -121.7331 | 0.59967 | 0.010147 | -0.012448 | -0.074952 | -0.0056973 | -0.030443 | -0.049526 | -0.040392 | 0.00094606 | -0.020536 | 0.057054 | 0.046689 | -0.22001 | -0.013856 | -0.019835 | -0.027466 | 0.068665 | -0.082397 | -0.018311 | 0.13733 | -0.045776 | 0.032043 | -8.8394 | 0.60425 | -121.7926 | 0.58136 | -121.2662 | -121.5408 | -121.1746 | 121.6507 | -0.53101 | -0.61798 | 121.8704 | 121.7651 | 121.6873 | 0.11444 | 0.036621 | -0.05951 | 0.004578 | -0.01831 | 0.46692 | 0.55847 | 0.19226 | 0.61798 | 0.25177 | 0.21973 | 0.064086 | 0.52643 | 122.374 | 0.15106 | 122.3969 | 121.8018 | 122.3373 | -0.68207 | -122.3923 | 121.7148 | 122.3145 | 121.7056 | 112.8937
1696.2969 | 122.4884 | -121.7422 | 0.61798 | -0.0051118 | -0.013089 | -0.079011 | -0.0050565 | -0.03322 | -0.049313 | -0.040605 | -0.0021057 | -0.020108 | 0.058336 | 0.04498 | -0.21766 | -0.018769 | -0.023039 | -0.09613 | 0.086975 | -0.09613 | -0.068665 | 0.064087 | -0.10071 | -0.009155 | -9.0363 | 0.62714 | -121.7834 | 0.54932 | -121.3303 | -121.5729 | -121.225 | 121.6461 | -0.53101 | -0.68665 | 121.8063 | 121.7331 | 121.6415 | 0.086975 | -0.004578 | -0.041198 | 0.009155 | -0.068665 | 0.41199 | 0.51727 | 0.16937 | 0.55847 | 0.21057 | 0.16022 | 0.027465 | 0.45319 | 122.3328 | 0.1831 | 122.4106 | 121.8292 | 122.3694 | -0.71411 | -122.4014 | 121.6736 | 122.2916 | 121.6461 | 112.706
1698.0781 | 122.5525 | -121.7239 | 0.6134 | 0.0025177 | -0.012661 | -0.077729 | -0.0039883 | -0.028734 | -0.047817 | -0.040819 | 0.0039979 | -0.020536 | 0.057482 | 0.046476 | -0.21979 | -0.01471 | -0.021117 | -0.032043 | 0.064087 | -0.09613 | -0.022888 | 0.11444 | -0.054932 | 0.009155 | -9.0271 | 0.61798 | -121.7926 | 0.62256 | -121.2753 | -121.5363 | -121.1472 | 121.6278 | -0.54932 | -0.63629 | 121.8384 | 121.7331 | 121.669 | 0.10528 | 0.041198 | -0.068665 | 0.004578 | 0.009156 | 0.44861 | 0.57678 | 0.18768 | 0.64545 | 0.25635 | 0.21057 | 0.073242 | 0.51727 | 122.4152 | 0.16022 | 122.4106 | 121.788 | 122.3419 | -0.70953 | -122.406 | 121.7011 | 122.3465 | 121.6919 | 112.6968
1699.8594 | 122.4335 | -121.7606 | 0.64545 | 0.0025177 | -0.01138 | -0.080079 | -0.0014249 | -0.029589 | -0.047817 | -0.039751 | 0.00094606 | -0.019467 | 0.058763 | 0.052244 | -0.21872 | -0.015351 | -0.020049 | -0.11902 | 0.086975 | -0.13733 | -0.15106 | -0.041199 | -0.20142 | -0.10529 | -9.2148 | 0.65918 | -121.8063 | 0.48981 | -121.4081 | -121.6873 | -121.2753 | 121.6232 | -0.55847 | -0.79651 | 121.7194 | 121.6553 | 121.5591 | 0.032043 | -0.064087 | -0.045776 | 0.013733 | -0.15564 | 0.35248 | 0.48523 | 0.073242 | 0.53101 | 0.11902 | 0.09613 | -0.013733 | 0.39825 | 122.2961 | 0.2243 | 122.4655 | 121.8475 | 122.4197 | -0.78278 | -122.4518 | 121.6095 | 122.2504 | 121.6415 | 112.5458
1701.6406 | 122.4655 | -121.7651 | 0.62714 | -0.0051118 | -0.011166 | -0.078583 | -0.0050565 | -0.030443 | -0.051235 | -0.040178 | 0.00094606 | -0.021604 | 0.057482 | 0.054166 | -0.2183 | -0.015992 | -0.023039 | -0.068665 | 0.10071 | -0.10529 | -0.073242 | 0.059509 | -0.09613 | -0.045776 | -9.1507 | 0.64087 | -121.8063 | 0.52643 | -121.3623 | -121.6324 | -121.2662 | 121.6599 | -0.52643 | -0.70038 | 121.8246 | 121.7194 | 121.669 | 0.05951 | 0.009156 | -0.041198 | 0.013733 | -0.10071 | 0.40283 | 0.49896 | 0.13275 | 0.54016 | 0.17395 | 0.16479 | 0.032044 | 0.44403 | 122.3328 | 0.20599 | 122.4472 | 121.8658 | 122.406 | -0.73242 | -122.4335 | 121.6919 | 122.2916 | 121.6965 | 112.6144
1703.375 | 122.5525 | -121.7285 | 0.59967 | -0.0051118 | -0.011593 | -0.076661 | -0.0056973 | -0.032793 | -0.051663 | -0.039537 | 0.0039979 | -0.021604 | 0.057909 | 0.04434 | -0.21894 | -0.015137 | -0.023894 | -0.086975 | 0.10071 | -0.11444 | -0.068665 | 0.073242 | -0.091553 | -0.004578 | -9.2102 | 0.59509 | -121.8018 | 0.59052 | -121.3028 | -121.5775 | -121.1838 | 121.6141 | -0.49896 | -0.66834 | 121.8018 | 121.7239 | 121.637 | 0.10986 | 0.022888 | -0.073242 | -0.004577 | -0.009155 | 0.42572 | 0.54474 | 0.15106 | 0.61798 | 0.2243 | 0.18768 | 0.045776 | 0.49896 | 122.3923 | 0.21515 | 122.3969 | 121.8292 | 122.3236 | -0.71411 | -122.4014 | 121.6599 | 122.319 | 121.6415 | 112.5183
1705.1406 | 122.5479 | -121.7422 | 0.59967 | 0.0025177 | -0.012661 | -0.081147 | -0.0046291 | -0.032152 | -0.046963 | -0.04146 | 0.00094606 | -0.02139 | 0.057268 | 0.047758 | -0.21872 | -0.014283 | -0.021544 | -0.11444 | 0.09613 | -0.11444 | -0.10071 | 0.041199 | -0.12817 | -0.032043 | -9.3155 | 0.59967 | -121.7926 | 0.58136 | -121.3165 | -121.5958 | -121.2112 | 121.6278 | -0.50354 | -0.70038 | 121.7834 | 121.7102 | 121.6141 | 0.082398 | -0.013733 | -0.050354 | 0 | -0.01831 | 0.42572 | 0.53101 | 0.14648 | 0.58136 | 0.19684 | 0.15564 | 0.013733 | 0.47607 | 122.374 | 0.21057 | 122.3923 | 121.8384 | 122.3419 | -0.71411 | -122.3923 | 121.6415 | 122.3236 | 121.6278 | 112.4268
1706.8594 | 122.4701 | -121.8109 | 0.62256 | 0.0025177 | -0.013729 | -0.079865 | -0.0059109 | -0.030657 | -0.049099 | -0.044878 | 0.0039979 | -0.019681 | 0.055986 | 0.051389 | -0.21702 | -0.01471 | -0.020903 | -0.11444 | 0.11902 | -0.13275 | -0.13275 | -0.004578 | -0.13733 | -0.068665 | -9.3933 | 0.60883 | -121.8475 | 0.45776 | -121.3943 | -121.6736 | -121.3074 | 121.6782 | -0.50354 | -0.75531 | 121.8063 | 121.7422 | 121.6736 | 0.064086 | -0.004578 | -0.036621 | -0.013733 | -0.16479 | 0.41657 | 0.50354 | 0.13733 | 0.54016 | 0.17395 | 0.12817 | 0 | 0.45319 | 122.3053 | 0.25177 | 122.4564 | 121.9299 | 122.4197 | -0.75531 | -122.4701 | 121.6782 | 122.2687 | 121.6965 | 112.4176
1708.6406 | 122.4838 | -121.8018 | 0.62256 | -0.0051118 | -0.012234 | -0.080079 | -0.0037747 | -0.027239 | -0.051449 | -0.042742 | 0.00094606 | -0.018827 | 0.0609 | 0.045835 | -0.21915 | -0.01471 | -0.026885 | -0.10529 | 0.09613 | -0.14191 | -0.12817 | -0.013733 | -0.11444 | -0.064087 | -9.4345 | 0.59967 | -121.8979 | 0.4715 | -121.3898 | -121.6827 | -121.3028 | 121.6599 | -0.52643 | -0.75073 | 121.788 | 121.7377 | 121.6873 | 0.07782 | 0.027466 | -0.09613 | -0.022889 | -0.15106 | 0.41199 | 0.49896 | 0.11902 | 0.59509 | 0.21515 | 0.12817 | 0.013733 | 0.50812 | 122.3694 | 0.23804 | 122.4976 | 121.8979 | 122.4014 | -0.76447 | -122.5204 | 121.6736 | 122.2733 | 121.6965 | 112.3672
1710.3594 | 122.4472 | -121.8292 | 0.61798 | 0.0025177 | -0.011593 | -0.077515 | -0.0039883 | -0.029162 | -0.048672 | -0.041887 | 0.00094606 | -0.019254 | 0.055986 | 0.044126 | -0.21702 | -0.015778 | -0.022826 | -0.082397 | 0.091553 | -0.12817 | -0.13733 | 0.004578 | -0.16022 | -0.09613 | -9.5306 | 0.61798 | -121.8567 | 0.44403 | -121.4493 | -121.7239 | -121.3394 | 121.701 | -0.52643 | -0.75531 | 121.8338 | 121.7331 | 121.669 | 0.032044 | -0.032043 | -0.027465 | 0 | -0.17395 | 0.37994 | 0.48981 | 0.10529 | 0.51727 | 0.13275 | 0.13275 | -0.009155 | 0.40741 | 122.3007 | 0.21973 | 122.4747 | 121.9208 | 122.4472 | -0.74616 | -122.4747 | 121.6919 | 122.2733 | 121.7468 | 112.2986
1712.125 | 122.4976 | -121.8109 | 0.62256 | 0.0025177 | -0.013089 | -0.077302 | -0.0059109 | -0.034075 | -0.050167 | -0.039965 | 0.00094606 | -0.018827 | 0.056627 | 0.042844 | -0.21766 | -0.015992 | -0.027525 | -0.086975 | 0.11444 | -0.1236 | -0.10071 | 0.036621 | -0.10529 | -0.045776 | -9.494 | 0.6134 | -121.8613 | 0.50812 | -121.3715 | -121.6599 | -121.2753 | 121.6873 | -0.50812 | -0.72327 | 121.8475 | 121.7651 | 121.7056 | 0.07782 | 0.01831 | -0.050354 | -0.009156 | -0.11444 | 0.43945 | 0.53558 | 0.15106 | 0.58594 | 0.20142 | 0.16022 | 0.022888 | 0.48981 | 122.3694 | 0.23804 | 122.4747 | 121.9254 | 122.4243 | -0.74616 | -122.4838 | 121.7102 | 122.319 | 121.7239 | 112.3169
1713.9062 | 122.4655 | -121.8018 | 0.63171 | -0.0051118 | -0.011807 | -0.077729 | -0.0061245 | -0.030657 | -0.049313 | -0.041887 | 0.00094606 | -0.020322 | 0.05855 | 0.043912 | -0.21723 | -0.013001 | -0.021758 | -0.09613 | 0.10986 | -0.1236 | -0.13275 | -0.009155 | -0.16022 | -0.086975 | -9.6176 | 0.63629 | -121.8887 | 0.44403 | -121.4584 | -121.7194 | -121.3394 | 121.6782 | -0.52185 | -0.76446 | 121.7926 | 121.7148 | 121.6415 | 0.036621 | -0.036621 | -0.086975 | 0.004578 | -0.18768 | 0.34332 | 0.46234 | 0.082398 | 0.54932 | 0.16937 | 0.11444 | -0.009155 | 0.4303 | 122.3328 | 0.23346 | 122.525 | 121.9116 | 122.4381 | -0.75531 | -122.5204 | 121.669 | 122.2458 | 121.7056 | 112.1841
1715.6406 | 122.4472 | -121.8018 | 0.62714 | 0.0025177 | -0.010098 | -0.078583 | -0.0039883 | -0.029802 | -0.051449 | -0.040178 | 0.00094606 | -0.02139 | 0.058336 | 0.052244 | -0.21872 | -0.015137 | -0.023253 | -0.1236 | 0.11444 | -0.1236 | -0.17853 | -0.050354 | -0.1831 | -0.10986 | -9.6909 | 0.65002 | -121.8796 | 0.46234 | -121.4676 | -121.7331 | -121.3303 | 121.6782 | -0.5127 | -0.80566 | 121.7514 | 121.6919 | 121.6187 | 0.013733 | -0.059509 | -0.07782 | 0.022888 | -0.1648 | 0.33417 | 0.4715 | 0.068665 | 0.54932 | 0.14648 | 0.073242 | -0.054932 | 0.41199 | 122.3419 | 0.23804 | 122.5296 | 121.9162 | 122.4518 | -0.75073 | -122.5067 | 121.6232 | 122.2641 | 121.6782 | 112.1109
1717.4375 | 122.4609 | -121.8521 | 0.62256 | 0.010147 | -0.012234 | -0.081147 | -0.0054837 | -0.028521 | -0.049954 | -0.039537 | -0.0021057 | -0.020322 | 0.059618 | 0.047544 | -0.2183 | -0.015992 | -0.023467 | -0.14648 | 0.10071 | -0.13733 | -0.16479 | -0.022888 | -0.12817 | -0.068665 | -9.7229 | 0.61798 | -121.875 | 0.45319 | -121.4355 | -121.7148 | -121.344 | 121.7148 | -0.52185 | -0.78735 | 121.8292 | 121.7834 | 121.7239 | 0.068664 | 0.009155 | -0.022888 | -0.004578 | -0.16937 | 0.41657 | 0.50812 | 0.13733 | 0.53101 | 0.16022 | 0.11444 | -0.027466 | 0.43945 | 122.3282 | 0.23804 | 122.493 | 121.9528 | 122.4701 | -0.75989 | -122.4976 | 121.6873 | 122.3053 | 121.7056 | 112.1292
1719.2188 | 122.5754 | -121.7834 | 0.5722 | 0.010147 | -0.013729 | -0.079224 | -0.0071927 | -0.029375 | -0.051876 | -0.041246 | -0.0051575 | -0.024381 | 0.054918 | 0.039854 | -0.2183 | -0.016205 | -0.019194 | -0.045776 | 0.068665 | -0.10071 | -0.013733 | 0.16022 | 0.013733 | 0.041199 | -9.6405 | 0.55389 | -121.8658 | 0.53101 | -121.312 | -121.5775 | -121.2296 | 121.6827 | -0.50354 | -0.58594 | 121.9437 | 121.8246 | 121.7972 | 0.14191 | 0.11444 | -0.082398 | -0.018311 | -0.041199 | 0.4715 | 0.55389 | 0.20599 | 0.63629 | 0.28839 | 0.26093 | 0.086975 | 0.55389 | 122.3969 | 0.16937 | 122.4197 | 121.8521 | 122.3373 | -0.67291 | -122.438 | 121.7697 | 122.3145 | 121.7377 | 112.1429
1721.0156 | 122.5296 | -121.8292 | 0.58136 | -0.0051118 | -0.015011 | -0.078797 | -0.0071927 | -0.025957 | -0.050381 | -0.039537 | -0.0051575 | -0.022458 | 0.057909 | 0.046049 | -0.21851 | -0.017487 | -0.024535 | -0.032043 | 0.073242 | -0.10071 | -0.032043 | 0.11902 | -0.018311 | 0.032043 | -9.7916 | 0.57678 | -121.8613 | 0.48981 | -121.376 | -121.6461 | -121.3074 | 121.7285 | -0.50812 | -0.6134 | 121.9482 | 121.8613 | 121.8109 | 0.13275 | 0.082397 | -0.032043 | -0.004578 | -0.091553 | 0.45319 | 0.52185 | 0.18311 | 0.55389 | 0.21515 | 0.21973 | 0.068665 | 0.48523 | 122.3511 | 0.17395 | 122.438 | 121.9025 | 122.406 | -0.68207 | -122.4426 | 121.7972 | 122.319 | 121.7972 | 112.0377
1722.75 | 122.493 | -121.8613 | 0.59052 | -0.0051118 | -0.017147 | -0.078797 | -0.0065517 | -0.030657 | -0.050595 | -0.042101 | -0.0021057 | -0.01904 | 0.057054 | 0.044553 | -0.21937 | -0.016419 | -0.02368 | -0.064087 | 0.068665 | -0.10529 | -0.07782 | 0.07782 | -0.050354 | -0.009155 | -9.8785 | 0.59052 | -121.8842 | 0.45319 | -121.4401 | -121.7056 | -121.3394 | 121.756 | -0.52185 | -0.66834 | 121.9391 | 121.8521 | 121.8109 | 0.096131 | 0.054932 | -0.022888 | 0 | -0.13733 | 0.42114 | 0.52185 | 0.15564 | 0.54474 | 0.17853 | 0.18311 | 0.027466 | 0.44403 | 122.3373 | 0.17395 | 122.4747 | 121.9299 | 122.4518 | -0.6958 | -122.4747 | 121.7834 | 122.3145 | 121.7972 | 111.9827
1724.5312 | 122.4792 | -121.8384 | 0.58136 | -0.0051118 | -0.014584 | -0.079438 | -0.0031337 | -0.027239 | -0.049954 | -0.040819 | -0.0021057 | -0.018186 | 0.057909 | 0.046903 | -0.22043 | -0.016205 | -0.025816 | -0.11902 | 0.11444 | -0.13275 | -0.16479 | -0.041199 | -0.17853 | -0.09613 | -9.9792 | 0.60883 | -121.9025 | 0.42572 | -121.4905 | -121.7834 | -121.3715 | 121.7056 | -0.46692 | -0.74616 | 121.7972 | 121.7422 | 121.6599 | 0.036621 | -0.045777 | -0.064087 | 0.027466 | -0.15564 | 0.3479 | 0.46692 | 0.054932 | 0.53101 | 0.11902 | 0.091552 | -0.032044 | 0.41199 | 122.3282 | 0.24719 | 122.5113 | 121.9528 | 122.4472 | -0.71411 | -122.4838 | 121.6736 | 122.2641 | 121.7194 | 111.8591
1726.2969 | 122.5754 | -121.8109 | 0.55389 | 0.0025177 | -0.010525 | -0.078583 | -0.0048427 | -0.030657 | -0.050595 | -0.041674 | 0.00094606 | -0.020749 | 0.056841 | 0.035795 | -0.21872 | -0.017273 | -0.019835 | -0.11444 | 0.11444 | -0.11902 | -0.11902 | 0.013733 | -0.14191 | -0.059509 | -9.9792 | 0.59052 | -121.8979 | 0.5127 | -121.4035 | -121.6736 | -121.2753 | 121.6919 | -0.43945 | -0.67291 | 121.8246 | 121.7514 | 121.669 | 0.05951 | -0.022888 | -0.086975 | 0.036621 | -0.041199 | 0.40741 | 0.53558 | 0.13733 | 0.62256 | 0.2243 | 0.13275 | 0 | 0.49438 | 122.4106 | 0.23346 | 122.4884 | 121.9254 | 122.4014 | -0.67291 | -122.4518 | 121.6919 | 122.3236 | 121.6965 | 111.8317
1728.0625 | 122.4792 | -121.8567 | 0.58136 | -0.012741 | -0.010952 | -0.079651 | -0.0037747 | -0.03023 | -0.050808 | -0.042314 | 0.00094606 | -0.02139 | 0.057482 | 0.043058 | -0.21894 | -0.016205 | -0.022398 | -0.13275 | 0.10071 | -0.12817 | -0.17853 | -0.041199 | -0.1831 | -0.10071 | -10.1486 | 0.60425 | -121.907 | 0.42114 | -121.4905 | -121.7743 | -121.3852 | 121.7285 | -0.48065 | -0.75989 | 121.8155 | 121.756 | 121.6736 | 0.027466 | -0.054931 | -0.050354 | 0.022888 | -0.16022 | 0.36621 | 0.4715 | 0.082397 | 0.52185 | 0.13275 | 0.086975 | -0.050354 | 0.41656 | 122.3282 | 0.22888 | 122.5113 | 121.9574 | 122.4609 | -0.70953 | -122.4884 | 121.6782 | 122.2778 | 121.7239 | 111.7081
1729.7812 | 122.612 | -121.8109 | 0.55847 | -0.0051118 | -0.012234 | -0.076874 | -0.0065517 | -0.033861 | -0.048245 | -0.042314 | 0.00094606 | -0.021176 | 0.057054 | 0.041349 | -0.21872 | -0.015565 | -0.021758 | -0.041199 | 0.073242 | -0.082397 | -0.036621 | 0.11444 | -0.045776 | 0.009155 | -10.0662 | 0.55389 | -121.8658 | 0.54932 | -121.3623 | -121.6232 | -121.2479 | 121.7285 | -0.48523 | -0.59509 | 121.9254 | 121.8201 | 121.7651 | 0.091552 | 0.036621 | -0.054932 | -0.004578 | -0.009156 | 0.44861 | 0.56305 | 0.18768 | 0.61798 | 0.24261 | 0.19684 | 0.045776 | 0.50354 | 122.4152 | 0.15564 | 122.4197 | 121.8842 | 122.3648 | -0.64087 | -122.4243 | 121.7743 | 122.3602 | 121.7697 | 111.7447
1731.5625 | 122.493 | -121.8887 | 0.58594 | 0.0025177 | -0.014157 | -0.078797 | -0.0065517 | -0.034929 | -0.050808 | -0.039324 | -0.0051575 | -0.020749 | 0.057054 | 0.049467 | -0.21915 | -0.016205 | -0.021971 | -0.15106 | 0.11444 | -0.13275 | -0.16022 | -0.004578 | -0.13275 | -0.073242 | -10.3134 | 0.59509 | -121.9208 | 0.39368 | -121.4996 | -121.7743 | -121.3852 | 121.756 | -0.4715 | -0.74615 | 121.8842 | 121.8155 | 121.756 | 0.059509 | 0 | -0.032043 | 0.009156 | -0.19226 | 0.3891 | 0.50354 | 0.11444 | 0.53558 | 0.14648 | 0.12817 | -0.027466 | 0.42114 | 122.3145 | 0.24719 | 122.5159 | 122.0032 | 122.4838 | -0.71869 | -122.5067 | 121.7285 | 122.2824 | 121.7377 | 111.5753
1733.3438 | 122.4792 | -121.8704 | 0.58136 | -0.0051118 | -0.0098843 | -0.076661 | -0.0029201 | -0.028521 | -0.04974 | -0.042314 | -0.0021057 | -0.020108 | 0.058123 | 0.050535 | -0.22086 | -0.014924 | -0.022185 | -0.13275 | 0.11444 | -0.13275 | -0.16022 | -0.050354 | -0.17853 | -0.10071 | -10.3775 | 0.60425 | -121.9391 | 0.42572 | -121.5271 | -121.8109 | -121.3898 | 121.7377 | -0.46692 | -0.74158 | 121.8201 | 121.7697 | 121.6919 | 0.032043 | -0.045777 | -0.068665 | 0.022888 | -0.15564 | 0.34332 | 0.48065 | 0.059509 | 0.54932 | 0.12817 | 0.082397 | -0.027466 | 0.41199 | 122.3648 | 0.24719 | 122.5433 | 121.9849 | 122.4747 | -0.71411 | -122.5204 | 121.7102 | 122.2961 | 121.7377 | 111.4929
1735.125 | 122.5662 | -121.8246 | 0.56305 | 0.0025177 | -0.013943 | -0.080079 | -0.0069791 | -0.030871 | -0.047817 | -0.040392 | -0.0051575 | -0.020963 | 0.057268 | 0.040922 | -0.21872 | -0.018342 | -0.024535 | -0.054932 | 0.054932 | -0.07782 | -0.054932 | 0.11444 | -0.064087 | 0.018311 | -10.3088 | 0.55389 | -121.8933 | 0.52185 | -121.4127 | -121.6644 | -121.3211 | 121.7468 | -0.50812 | -0.61798 | 121.9391 | 121.843 | 121.7606 | 0.096131 | 0.013733 | -0.068665 | -0.009155 | -0.041198 | 0.41199 | 0.50354 | 0.16022 | 0.5722 | 0.22888 | 0.19226 | 0.022888 | 0.48065 | 122.4152 | 0.13275 | 122.4472 | 121.8796 | 122.3785 | -0.64087 | -122.4564 | 121.7697 | 122.3465 | 121.7697 | 111.5158
1736.8594 | 122.5021 | -121.8842 | 0.59509 | -0.0051118 | -0.014157 | -0.080506 | -0.0044155 | -0.031725 | -0.050167 | -0.041033 | -0.0021057 | -0.018613 | 0.059618 | 0.046049 | -0.2183 | -0.015778 | -0.021544 | -0.1236 | 0.12817 | -0.14648 | -0.15564 | -0.013733 | -0.15106 | -0.073242 | -10.4141 | 0.59052 | -121.9437 | 0.41199 | -121.4905 | -121.7697 | -121.376 | 121.7377 | -0.46692 | -0.75073 | 121.8704 | 121.8109 | 121.7331 | 0.073242 | -0.004578 | -0.05951 | -0.004578 | -0.18311 | 0.39368 | 0.50812 | 0.11444 | 0.56763 | 0.17395 | 0.13275 | -0.009156 | 0.45319 | 122.3557 | 0.27466 | 122.5342 | 122.0123 | 122.4747 | -0.74158 | -122.5388 | 121.7285 | 122.2961 | 121.7606 | 111.47
1738.6406 | 122.5845 | -121.8338 | 0.55847 | 0.0025177 | -0.0096707 | -0.080079 | -0.0052701 | -0.025103 | -0.048245 | -0.041674 | 0.00094606 | -0.01904 | 0.059618 | 0.041563 | -0.21915 | -0.015992 | -0.021544 | -0.10071 | 0.082397 | -0.11902 | -0.11902 | 0.013733 | -0.16022 | -0.050354 | -10.4965 | 0.56305 | -121.9437 | 0.50354 | -121.4355 | -121.7148 | -121.3028 | 121.7148 | -0.47607 | -0.67749 | 121.8475 | 121.7834 | 121.6736 | 0.068665 | -0.041198 | -0.10986 | 0.004577 | -0.054932 | 0.39825 | 0.53101 | 0.11902 | 0.64087 | 0.22888 | 0.13275 | 0 | 0.50812 | 122.4472 | 0.20142 | 122.5067 | 121.9162 | 122.3969 | -0.67749 | -122.5021 | 121.7148 | 122.3373 | 121.7331 | 111.3373
1740.4375 | 122.4838 | -121.9025 | 0.60883 | -0.0051118 | -0.012875 | -0.07602 | -0.0039883 | -0.031511 | -0.04974 | -0.041246 | -0.0051575 | -0.01904 | 0.057482 | 0.043485 | -0.21787 | -0.015351 | -0.022826 | -0.10071 | 0.10529 | -0.11444 | -0.14191 | -0.009155 | -0.16479 | -0.086975 | -10.6018 | 0.60425 | -121.907 | 0.41657 | -121.5225 | -121.8109 | -121.4081 | 121.788 | -0.50354 | -0.75073 | 121.8933 | 121.8155 | 121.7377 | 0.027466 | -0.050354 | -0.004577 | -0.004578 | -0.19226 | 0.37994 | 0.49439 | 0.091553 | 0.49896 | 0.09613 | 0.10529 | -0.027466 | 0.38452 | 122.3236 | 0.21973 | 122.5113 | 122.0078 | 122.5067 | -0.72327 | -122.5159 | 121.7606 | 122.319 | 121.8018 | 111.3007
1742.1562 | 122.644 | -121.843 | 0.56763 | 0.0025177 | -0.010311 | -0.079651 | -0.0065517 | -0.031084 | -0.04974 | -0.043596 | 0.0039979 | -0.021176 | 0.059618 | 0.039426 | -0.21744 | -0.017914 | -0.023467 | -0.050354 | 0.059509 | -0.10071 | -0.032043 | 0.15106 | -0.004578 | 0.064087 | -10.4965 | 0.56763 | -121.8933 | 0.55847 | -121.3348 | -121.5958 | -121.2616 | 121.7422 | -0.50812 | -0.59967 | 121.994 | 121.907 | 121.8384 | 0.1648 | 0.09613 | -0.050354 | 0 | -0.009155 | 0.50812 | 0.58136 | 0.24719 | 0.63171 | 0.29755 | 0.25177 | 0.068665 | 0.55847 | 122.4518 | 0.16022 | 122.4609 | 121.9025 | 122.4106 | -0.66834 | -122.4609 | 121.8109 | 122.4014 | 121.7926 | 111.3464
1743.9375 | 122.6074 | -121.8567 | 0.5722 | -0.0051118 | -0.013729 | -0.077515 | -0.0069791 | -0.028734 | -0.050167 | -0.040392 | 0.0039979 | -0.021817 | 0.058763 | 0.047971 | -0.21979 | -0.013856 | -0.020262 | -0.054932 | 0.054932 | -0.082397 | -0.022888 | 0.13733 | -0.045776 | 0.009155 | -10.6293 | 0.56763 | -121.8796 | 0.54016 | -121.3943 | -121.6736 | -121.3074 | 121.7743 | -0.51727 | -0.59509 | 121.994 | 121.8658 | 121.8109 | 0.091552 | 0.036621 | -0.022889 | -0.004578 | -0.032044 | 0.46234 | 0.54932 | 0.1831 | 0.5722 | 0.20599 | 0.21973 | 0.059509 | 0.48523 | 122.4197 | 0.13733 | 122.4472 | 121.9116 | 122.4243 | -0.6546 | -122.4518 | 121.8338 | 122.3969 | 121.8018 | 111.2274
1745.7031 | 122.6624 | -121.8613 | 0.54932 | 0.010147 | -0.014157 | -0.079865 | -0.0067653 | -0.033648 | -0.049313 | -0.041887 | 0.00094606 | -0.023313 | 0.055773 | 0.046262 | -0.22022 | -0.016633 | -0.023039 | -0.064087 | 0.07782 | -0.10529 | -0.013733 | 0.16937 | -0.009155 | 0.054932 | -10.6247 | 0.54474 | -121.9208 | 0.55847 | -121.344 | -121.6095 | -121.2753 | 121.756 | -0.4715 | -0.56305 | 122.0306 | 121.9162 | 121.8521 | 0.16022 | 0.096131 | -0.059509 | -0.004577 | 0.009156 | 0.51727 | 0.58594 | 0.25177 | 0.64545 | 0.31128 | 0.27466 | 0.091553 | 0.57678 | 122.4792 | 0.18311 | 122.4655 | 121.9391 | 122.406 | -0.6546 | -122.4701 | 121.8475 | 122.4197 | 121.7972 | 111.2366
1747.4844 | 122.5296 | -121.875 | 0.59052 | 0.0025177 | -0.011166 | -0.080292 | -0.0039883 | -0.02788 | -0.047604 | -0.037828 | -0.0021057 | -0.020963 | 0.057909 | 0.047758 | -0.22022 | -0.015992 | -0.022185 | -0.10986 | 0.10986 | -0.1236 | -0.15106 | -0.013733 | -0.17395 | -0.086975 | -10.8261 | 0.60425 | -121.9391 | 0.43488 | -121.5088 | -121.7926 | -121.3806 | 121.7514 | -0.48065 | -0.74158 | 121.8613 | 121.788 | 121.701 | 0.036621 | -0.050354 | -0.064087 | 0.013733 | -0.15564 | 0.36621 | 0.49438 | 0.082397 | 0.55847 | 0.14648 | 0.10986 | -0.027466 | 0.4303 | 122.374 | 0.23346 | 122.5433 | 121.9849 | 122.4792 | -0.71411 | -122.5296 | 121.7239 | 122.3099 | 121.7651 | 111.0489
1749.2031 | 122.5479 | -121.8979 | 0.60425 | -0.0051118 | -0.011807 | -0.080079 | -0.0035611 | -0.034075 | -0.049099 | -0.043169 | 0.00094606 | -0.01904 | 0.057695 | 0.043912 | -0.21979 | -0.012787 | -0.022185 | -0.10071 | 0.10071 | -0.11444 | -0.11902 | 0.004578 | -0.10986 | -0.059509 | -10.7895 | 0.58594 | -121.9437 | 0.46234 | -121.4584 | -121.7651 | -121.376 | 121.7834 | -0.50354 | -0.72327 | 121.9025 | 121.8384 | 121.788 | 0.054932 | 0.004578 | -0.045777 | -0.018311 | -0.14191 | 0.43945 | 0.52185 | 0.13275 | 0.56763 | 0.17853 | 0.11902 | -0.004578 | 0.48523 | 122.406 | 0.21515 | 122.5296 | 121.9986 | 122.4838 | -0.71869 | -122.5479 | 121.7789 | 122.3602 | 121.7972 | 111.1084
1750.9844 | 122.5296 | -121.9162 | 0.5722 | -0.012741 | -0.013943 | -0.079651 | -0.0046291 | -0.031298 | -0.051022 | -0.037828 | 0.00094606 | -0.017758 | 0.057909 | 0.050321 | -0.21958 | -0.017273 | -0.02133 | -0.13733 | 0.1236 | -0.12817 | -0.15106 | -0.022888 | -0.15106 | -0.082397 | -10.9131 | 0.58594 | -121.994 | 0.39825 | -121.5134 | -121.8063 | -121.431 | 121.788 | -0.44861 | -0.72327 | 121.8933 | 121.8338 | 121.7651 | 0.045777 | -0.022888 | -0.07782 | 0.013732 | -0.17395 | 0.40283 | 0.48523 | 0.10986 | 0.56305 | 0.18768 | 0.10529 | -0.022888 | 0.48065 | 122.3923 | 0.25177 | 122.58 | 122.0398 | 122.5021 | -0.70038 | -122.5662 | 121.7651 | 122.3145 | 121.7789 | 111.0031
1752.7812 | 122.6212 | -121.8567 | 0.52643 | 0.0025177 | -0.01202 | -0.076447 | -0.0054837 | -0.028521 | -0.048458 | -0.041033 | -0.0021057 | -0.020963 | 0.056841 | 0.047117 | -0.22001 | -0.014496 | -0.025389 | -0.045776 | 0.07782 | -0.091553 | 0 | 0.15106 | -0.045776 | 0.022888 | -10.8673 | 0.52643 | -121.9208 | 0.52185 | -121.4127 | -121.701 | -121.3165 | 121.7651 | -0.44861 | -0.52643 | 122.0078 | 121.8796 | 121.8109 | 0.11444 | 0.045777 | -0.064087 | 0 | -0.004577 | 0.44403 | 0.54016 | 0.15564 | 0.60425 | 0.21973 | 0.24261 | 0.091553 | 0.50812 | 122.4426 | 0.16937 | 122.4472 | 121.9345 | 122.3831 | -0.61798 | -122.4472 | 121.8567 | 122.3785 | 121.8109 | 110.9894
1754.5781 | 122.6669 | -121.8613 | 0.53101 | -0.012741 | -0.014584 | -0.079011 | -0.0071927 | -0.035998 | -0.050167 | -0.041674 | -0.0082091 | -0.02374 | 0.057054 | 0.047758 | -0.21872 | -0.016205 | -0.025816 | -0.073242 | 0.064087 | -0.09613 | -0.018311 | 0.14191 | -0.009155 | 0.041199 | -10.8902 | 0.53558 | -121.9208 | 0.53101 | -121.3898 | -121.6461 | -121.312 | 121.7651 | -0.46692 | -0.54932 | 122.0032 | 121.9025 | 121.8521 | 0.13733 | 0.086975 | -0.059509 | 0.004577 | 0 | 0.4715 | 0.54932 | 0.21515 | 0.60883 | 0.27466 | 0.23804 | 0.077819 | 0.53101 | 122.4518 | 0.16022 | 122.4564 | 121.9254 | 122.3969 | -0.62714 | -122.4518 | 121.843 | 122.3923 | 121.788 | 110.9711
1756.2812 | 122.4747 | -121.9299 | 0.5722 | -0.0051118 | -0.0090299 | -0.076661 | -0.0046291 | -0.029162 | -0.050595 | -0.038683 | -0.0021057 | -0.018186 | 0.057909 | 0.053525 | -0.22022 | -0.01706 | -0.025176 | -0.11444 | 0.10529 | -0.12817 | -0.16479 | -0.041199 | -0.1831 | -0.11902 | -11.142 | 0.56763 | -121.9894 | 0.3891 | -121.5775 | -121.875 | -121.4539 | 121.8018 | -0.46692 | -0.737 | 121.8887 | 121.8109 | 121.7468 | 0.009155 | -0.054931 | -0.059509 | -0.004578 | -0.18311 | 0.35248 | 0.47607 | 0.054932 | 0.53558 | 0.11444 | 0.086975 | -0.036621 | 0.41199 | 122.3785 | 0.23346 | 122.5571 | 122.0352 | 122.4976 | -0.70038 | -122.5616 | 121.7651 | 122.319 | 121.8155 | 110.788
1758.0469 | 122.493 | -121.9574 | 0.56305 | -0.0051118 | -0.0088163 | -0.079651 | -0.0029201 | -0.032366 | -0.048672 | -0.040392 | 0.00094606 | -0.018186 | 0.057909 | 0.049039 | -0.22022 | -0.013642 | -0.020476 | -0.11902 | 0.11902 | -0.13733 | -0.13733 | -0.013733 | -0.16937 | -0.10529 | -11.2289 | 0.54474 | -122.0078 | 0.37537 | -121.582 | -121.875 | -121.4584 | 121.8201 | -0.44403 | -0.70038 | 121.9437 | 121.8521 | 121.788 | 0.032043 | -0.032044 | -0.050354 | -0.01831 | -0.18768 | 0.37537 | 0.49896 | 0.082397 | 0.54932 | 0.13275 | 0.1236 | 0 | 0.42572 | 122.3831 | 0.25635 | 122.5525 | 122.0764 | 122.5021 | -0.70038 | -122.5708 | 121.8201 | 122.3328 | 121.8384 | 110.7285
1759.8281 | 122.5525 | -121.962 | 0.53101 | 0.0025177 | -0.013943 | -0.079651 | -0.0069791 | -0.032366 | -0.04974 | -0.043383 | 0.0070497 | -0.020749 | 0.056841 | 0.047544 | -0.21808 | -0.015565 | -0.020903 | -0.045776 | 0.068665 | -0.09613 | -0.054932 | 0.10986 | -0.036621 | 0.027466 | -11.2198 | 0.52643 | -121.9849 | 0.42114 | -121.5088 | -121.7743 | -121.431 | 121.8658 | -0.46234 | -0.58594 | 122.0718 | 121.9894 | 121.9254 | 0.1236 | 0.059509 | -0.022888 | -0.004578 | -0.10986 | 0.45319 | 0.53101 | 0.18768 | 0.55389 | 0.21057 | 0.20599 | 0.041198 | 0.47607 | 122.406 | 0.16479 | 122.5113 | 122.0306 | 122.4884 | -0.62714 | -122.5159 | 121.907 | 122.3831 | 121.9162 | 110.7422
1761.6094 | 122.5891 | -121.9391 | 0.52643 | -0.0051118 | -0.011166 | -0.078583 | -0.0050565 | -0.033434 | -0.049526 | -0.041674 | -0.0021057 | -0.020536 | 0.056627 | 0.047758 | -0.21766 | -0.01706 | -0.019194 | -0.082397 | 0.059509 | -0.091553 | -0.068665 | 0.073242 | -0.091553 | 0.004578 | -11.3434 | 0.50354 | -121.994 | 0.44403 | -121.4905 | -121.7651 | -121.4035 | 121.8475 | -0.46692 | -0.59509 | 122.0123 | 121.9437 | 121.8475 | 0.096131 | 0 | -0.054932 | -0.022888 | -0.082397 | 0.44861 | 0.53558 | 0.17395 | 0.59052 | 0.22888 | 0.16479 | 0.022888 | 0.50354 | 122.438 | 0.15106 | 122.4976 | 121.9986 | 122.4426 | -0.61798 | -122.5204 | 121.8704 | 122.3831 | 121.8567 | 110.5957
1763.3906 | 122.5388 | -121.9711 | 0.52643 | 0.0025177 | -0.016079 | -0.080079 | -0.0071927 | -0.034929 | -0.050167 | -0.039965 | -0.0021057 | -0.019895 | 0.057695 | 0.046903 | -0.21915 | -0.017914 | -0.020689 | -0.073242 | 0.064087 | -0.10071 | -0.054932 | 0.091553 | -0.041199 | 0.013733 | -11.3983 | 0.52185 | -121.9986 | 0.39368 | -121.5317 | -121.8063 | -121.4447 | 121.8704 | -0.46234 | -0.58136 | 122.0627 | 121.9849 | 121.9299 | 0.11444 | 0.059509 | -0.027466 | -0.004577 | -0.13275 | 0.43945 | 0.52643 | 0.16479 | 0.55389 | 0.19226 | 0.19226 | 0.045776 | 0.46692 | 122.3923 | 0.1648 | 122.5204 | 122.0352 | 122.493 | -0.62714 | -122.525 | 121.9162 | 122.3648 | 121.8979 | 110.5728
1765.1719 | 122.5571 | -121.9574 | 0.56763 | -0.0051118 | -0.013302 | -0.079438 | -0.0044155 | -0.031084 | -0.05209 | -0.037828 | 0.00094606 | -0.019254 | 0.059404 | 0.048398 | -0.21937 | -0.018342 | -0.016631 | -0.068665 | 0.082397 | -0.09613 | -0.064087 | 0.091553 | -0.068665 | -0.004578 | -11.5036 | 0.56305 | -121.9757 | 0.42114 | -121.5179 | -121.7926 | -121.4447 | 121.8613 | -0.48523 | -0.63171 | 122.049 | 121.9528 | 121.8887 | 0.091552 | 0.027465 | -0.018311 | -0.004578 | -0.14648 | 0.43945 | 0.51269 | 0.16479 | 0.53101 | 0.1831 | 0.18768 | 0.032043 | 0.45776 | 122.3969 | 0.17853 | 122.5388 | 122.0398 | 122.5204 | -0.66376 | -122.5433 | 121.8933 | 122.3785 | 121.8887 | 110.4538
1766.8906 | 122.6486 | -121.8796 | 0.58136 | 0.0025177 | -0.014584 | -0.080292 | -0.0056973 | -0.031725 | -0.051663 | -0.042955 | -0.0082091 | -0.022031 | 0.055773 | 0.040708 | -0.21958 | -0.015992 | -0.019408 | -0.050354 | 0.073242 | -0.086975 | -0.022888 | 0.14648 | 0 | 0.050354 | -11.5952 | 0.55847 | -121.9208 | 0.54016 | -121.3898 | -121.6461 | -121.2936 | 121.7926 | -0.50812 | -0.60425 | 122.0261 | 121.9299 | 121.8796 | 0.13733 | 0.086975 | -0.041198 | -0.022888 | -0.041199 | 0.48981 | 0.58594 | 0.23346 | 0.62714 | 0.27466 | 0.23346 | 0.064087 | 0.53101 | 122.4609 | 0.16022 | 122.4792 | 121.9528 | 122.438 | -0.66834 | -122.5021 | 121.8567 | 122.4197 | 121.8292 | 110.2844
1768.6719 | 122.6303 | -121.8933 | 0.54474 | -0.012741 | -0.010098 | -0.079011 | -0.0048427 | -0.03258 | -0.051235 | -0.039751 | 0.00094606 | -0.021604 | 0.056841 | 0.047544 | -0.21979 | -0.015137 | -0.021117 | -0.032043 | 0.064087 | -0.073242 | -0.027466 | 0.13733 | -0.050354 | 0.018311 | -11.6959 | 0.55389 | -121.9345 | 0.53101 | -121.463 | -121.7148 | -121.3394 | 121.8201 | -0.48065 | -0.5722 | 122.0306 | 121.9116 | 121.843 | 0.091553 | 0.022888 | -0.041198 | 0.009155 | -0.013733 | 0.4303 | 0.55389 | 0.17853 | 0.59509 | 0.21973 | 0.21057 | 0.045776 | 0.4715 | 122.4655 | 0.13733 | 122.4884 | 121.9574 | 122.4472 | -0.61798 | -122.4792 | 121.8658 | 122.4243 | 121.8613 | 110.1974
1770.3906 | 122.5937 | -121.9116 | 0.57678 | -0.0051118 | -0.013516 | -0.080079 | -0.0056973 | -0.029162 | -0.051235 | -0.040392 | 0.00094606 | -0.020963 | 0.0562 | 0.048826 | -0.22001 | -0.015778 | -0.020049 | -0.086975 | 0.064087 | -0.086975 | -0.07782 | 0.059509 | -0.082397 | -0.009155 | -11.8561 | 0.56305 | -121.962 | 0.47607 | -121.4676 | -121.7377 | -121.3806 | 121.8246 | -0.5127 | -0.6546 | 121.9711 | 121.9025 | 121.8292 | 0.07782 | 0.004578 | -0.050354 | -0.013733 | -0.10071 | 0.44403 | 0.53101 | 0.17395 | 0.58136 | 0.2243 | 0.14648 | 0.009155 | 0.49438 | 122.438 | 0.15106 | 122.525 | 121.9757 | 122.4747 | -0.66376 | -122.5388 | 121.8338 | 122.3877 | 121.8246 | 110.0555
1772.1562 | 122.5342 | -121.9345 | 0.59052 | -0.0051118 | -0.0092435 | -0.078583 | -0.0016385 | -0.028948 | -0.049313 | -0.04146 | 0.00094606 | -0.017758 | 0.059191 | 0.048398 | -0.21937 | -0.015565 | -0.022185 | -0.12817 | 0.10529 | -0.1236 | -0.15564 | -0.050354 | -0.19684 | -0.10529 | -12.0804 | 0.59052 | -121.9849 | 0.42572 | -121.5729 | -121.8567 | -121.4447 | 121.8109 | -0.48523 | -0.74616 | 121.8842 | 121.8292 | 121.7377 | 0.01831 | -0.073242 | -0.050354 | 0 | -0.1648 | 0.36163 | 0.48981 | 0.07782 | 0.54016 | 0.12817 | 0.073242 | -0.032044 | 0.41199 | 122.4106 | 0.22888 | 122.5754 | 122.0398 | 122.525 | -0.71411 | -122.5754 | 121.7789 | 122.3602 | 121.8063 | 109.8541
1773.875 | 122.6074 | -121.9116 | 0.55389 | -0.0051118 | -0.012448 | -0.082001 | -0.0069791 | -0.03322 | -0.050381 | -0.04146 | 0.00094606 | -0.022031 | 0.056841 | 0.04498 | -0.21958 | -0.015137 | -0.024748 | -0.082397 | 0.073242 | -0.082397 | -0.059509 | 0.073242 | -0.086975 | -0.009155 | -12.0804 | 0.54932 | -121.9711 | 0.48065 | -121.4813 | -121.7377 | -121.3669 | 121.8292 | -0.48065 | -0.6134 | 121.9849 | 121.9025 | 121.8246 | 0.073242 | -0.004578 | -0.059509 | -0.004578 | -0.073242 | 0.4303 | 0.54474 | 0.17395 | 0.60425 | 0.23346 | 0.15564 | 0.022888 | 0.48981 | 122.4518 | 0.15564 | 122.5204 | 121.9849 | 122.4609 | -0.63629 | -122.525 | 121.8521 | 122.3923 | 121.8292 | 109.8312
1775.6719 | 122.6166 | -121.9162 | 0.5722 | 0.010147 | -0.013729 | -0.080719 | -0.0074063 | -0.031298 | -0.04974 | -0.041033 | -0.0021057 | -0.019895 | 0.0562 | 0.036008 | -0.21808 | -0.015992 | -0.024748 | -0.10071 | 0.059509 | -0.10529 | -0.07782 | 0.068665 | -0.091553 | -0.013733 | -12.2177 | 0.56305 | -121.9849 | 0.46692 | -121.4722 | -121.7651 | -121.3943 | 121.8109 | -0.5127 | -0.65002 | 121.9849 | 121.9025 | 121.8246 | 0.091553 | 0.013733 | -0.068664 | -0.009156 | -0.10529 | 0.44403 | 0.52185 | 0.15106 | 0.59052 | 0.21973 | 0.17395 | 0.027466 | 0.5127 | 122.4518 | 0.16479 | 122.5479 | 121.9757 | 122.4792 | -0.67749 | -122.5571 | 121.8384 | 122.3831 | 121.8155 | 109.6985
1777.4531 | 122.6212 | -121.9208 | 0.53558 | -0.012741 | -0.010952 | -0.080933 | -0.0054837 | -0.027239 | -0.051022 | -0.04146 | 0.00094606 | -0.019895 | 0.055986 | 0.043058 | -0.22065 | -0.016419 | -0.023039 | -0.10986 | 0.10071 | -0.14648 | -0.11444 | 0.009155 | -0.15106 | -0.068665 | -12.2864 | 0.55389 | -121.994 | 0.49439 | -121.4859 | -121.788 | -121.3806 | 121.7743 | -0.43488 | -0.65002 | 121.9299 | 121.8521 | 121.7697 | 0.077819 | -0.004578 | -0.073243 | 0.018311 | -0.041198 | 0.43488 | 0.54016 | 0.13275 | 0.6134 | 0.20599 | 0.15564 | 0.032043 | 0.50812 | 122.4884 | 0.24719 | 122.5479 | 122.0215 | 122.4747 | -0.68207 | -122.5296 | 121.8063 | 122.4152 | 121.8109 | 109.6344
1779.2188 | 122.5433 | -121.9849 | 0.56305 | -0.012741 | -0.010311 | -0.078797 | -0.0039883 | -0.027666 | -0.050808 | -0.042101 | 0.00094606 | -0.019467 | 0.057054 | 0.043912 | -0.21979 | -0.014924 | -0.026671 | -0.11444 | 0.10529 | -0.13733 | -0.16479 | -0.036621 | -0.17853 | -0.10986 | -12.4695 | 0.5722 | -122.0306 | 0.40741 | -121.5866 | -121.8796 | -121.4722 | 121.8475 | -0.45776 | -0.72784 | 121.9482 | 121.875 | 121.8063 | 0.027466 | -0.041199 | -0.045777 | 0.009156 | -0.15564 | 0.39825 | 0.5127 | 0.10529 | 0.55847 | 0.15106 | 0.10071 | -0.027466 | 0.44403 | 122.4381 | 0.24262 | 122.6028 | 122.0901 | 122.5571 | -0.70038 | -122.5937 | 121.8201 | 122.3923 | 121.8704 | 109.5154
1780.9531 | 122.6669 | -121.9574 | 0.48523 | -0.0051118 | -0.010311 | -0.078156 | -0.0033475 | -0.027453 | -0.048672 | -0.041033 | 0.00094606 | -0.02139 | 0.058336 | 0.049467 | -0.21958 | -0.014496 | -0.022826 | -0.041199 | 0.068665 | -0.086975 | -0.009155 | 0.13733 | -0.045776 | 0.022888 | -12.442 | 0.48981 | -122.0123 | 0.46692 | -121.4767 | -121.7789 | -121.3989 | 121.8704 | -0.41656 | -0.49438 | 122.0947 | 121.9803 | 121.9116 | 0.10986 | 0.041199 | -0.054932 | 0.004578 | -0.01831 | 0.48065 | 0.55847 | 0.17853 | 0.6134 | 0.23346 | 0.2243 | 0.07782 | 0.53558 | 122.4792 | 0.15564 | 122.5021 | 122.0261 | 122.4472 | -0.5722 | -122.4976 | 121.9482 | 122.4243 | 121.9162 | 109.5154
1782.7344 | 122.6166 | -121.9849 | 0.51727 | -0.0051118 | -0.011593 | -0.078583 | -0.0044155 | -0.030871 | -0.050808 | -0.042314 | 0.00094606 | -0.022031 | 0.056841 | 0.043485 | -0.21766 | -0.016419 | -0.020903 | -0.073242 | 0.050354 | -0.09613 | -0.045776 | 0.10986 | -0.086975 | 0.004578 | -12.6205 | 0.50354 | -122.0398 | 0.45319 | -121.5088 | -121.7834 | -121.4081 | 121.8887 | -0.46692 | -0.56305 | 122.0947 | 121.9894 | 121.8979 | 0.10071 | 0.009155 | -0.054932 | -0.013733 | -0.064087 | 0.47607 | 0.57678 | 0.20142 | 0.63171 | 0.25635 | 0.20599 | 0.050354 | 0.53101 | 122.493 | 0.14648 | 122.5433 | 122.0352 | 122.4884 | -0.6134 | -122.5571 | 121.9391 | 122.438 | 121.9116 | 109.3643
1784.5156 | 122.5754 | -121.9849 | 0.55389 | -0.0051118 | -0.01437 | -0.080719 | -0.0022793 | -0.032793 | -0.051876 | -0.042101 | -0.0021057 | -0.01904 | 0.057268 | 0.046689 | -0.21958 | -0.016633 | -0.021758 | -0.11444 | 0.091553 | -0.13733 | -0.14191 | -0.018311 | -0.13275 | -0.064087 | -12.7579 | 0.53558 | -122.049 | 0.3891 | -121.55 | -121.8338 | -121.4447 | 121.8475 | -0.46234 | -0.6958 | 121.9666 | 121.9208 | 121.8521 | 0.073242 | 0.004578 | -0.064087 | -0.018311 | -0.1648 | 0.43488 | 0.54016 | 0.15106 | 0.60425 | 0.21515 | 0.11902 | -0.004578 | 0.49896 | 122.438 | 0.22888 | 122.5845 | 122.0764 | 122.5204 | -0.69122 | -122.6028 | 121.843 | 122.374 | 121.8704 | 109.227
1786.2344 | 122.5525 | -122.0261 | 0.50812 | 0.0025177 | -0.014798 | -0.080719 | -0.0069791 | -0.032793 | -0.050381 | -0.041033 | 0.00094606 | -0.020108 | 0.056627 | 0.050962 | -0.21552 | -0.017487 | -0.019835 | -0.064087 | 0.07782 | -0.09613 | -0.082397 | 0.064087 | -0.07782 | -0.027466 | -12.7808 | 0.50354 | -122.0627 | 0.3479 | -121.5958 | -121.8887 | -121.5317 | 121.9299 | -0.4303 | -0.59051 | 122.0901 | 121.9986 | 121.9482 | 0.068664 | 0.01831 | -0.036621 | -0.004578 | -0.16022 | 0.4303 | 0.49438 | 0.13733 | 0.53101 | 0.17395 | 0.16022 | 0.013733 | 0.46692 | 122.4106 | 0.17395 | 122.5662 | 122.1039 | 122.5296 | -0.60425 | -122.5708 | 121.9437 | 122.374 | 121.962 | 109.2453
1788 | 122.5845 | -122.0306 | 0.50354 | -0.0051118 | -0.011166 | -0.078583 | -0.0022793 | -0.028734 | -0.049526 | -0.041674 | -0.0021057 | -0.017331 | 0.057268 | 0.053312 | -0.21851 | -0.014496 | -0.025816 | -0.082397 | 0.091553 | -0.1236 | -0.082397 | 0.059509 | -0.082397 | -0.036621 | -12.8677 | 0.50354 | -122.0764 | 0.41199 | -121.5775 | -121.8796 | -121.4859 | 121.907 | -0.41199 | -0.58594 | 122.0901 | 121.994 | 121.9482 | 0.086975 | 0.041199 | -0.045776 | 0 | -0.091553 | 0.45319 | 0.54474 | 0.15106 | 0.59051 | 0.19684 | 0.1831 | 0.041199 | 0.49896 | 122.4884 | 0.21515 | 122.58 | 122.1222 | 122.5342 | -0.62714 | -122.58 | 121.9482 | 122.4426 | 121.9482 | 109.1629
1789.7812 | 122.6486 | -121.9986 | 0.48065 | -0.0051118 | -0.013302 | -0.081147 | -0.0080471 | -0.034929 | -0.049313 | -0.042528 | 0.00094606 | -0.022458 | 0.059618 | 0.041776 | -0.21787 | -0.015137 | -0.021758 | -0.09613 | 0.07782 | -0.10071 | -0.068665 | 0.059509 | -0.073242 | -0.004578 | -12.9501 | 0.48065 | -122.0535 | 0.40283 | -121.5546 | -121.8155 | -121.4767 | 121.8979 | -0.40283 | -0.54932 | 122.0581 | 121.994 | 121.9254 | 0.09613 | 0.027466 | -0.054932 | 0 | -0.07782 | 0.44403 | 0.52185 | 0.18311 | 0.57678 | 0.23804 | 0.16022 | 0.032043 | 0.49896 | 122.4564 | 0.17853 | 122.5342 | 122.0764 | 122.4792 | -0.58136 | -122.5342 | 121.9299 | 122.4014 | 121.9025 | 109.0485
1791.5625 | 122.5937 | -122.0444 | 0.48065 | -0.0051118 | -0.011166 | -0.075806 | -0.0042019 | -0.029589 | -0.049313 | -0.040605 | -0.0021057 | -0.020749 | 0.056414 | 0.048612 | -0.21958 | -0.01471 | -0.022826 | -0.07782 | 0.10986 | -0.10986 | -0.086975 | 0.054932 | -0.11444 | -0.036621 | -12.973 | 0.48523 | -122.0901 | 0.37537 | -121.5912 | -121.8842 | -121.4951 | 121.9345 | -0.37079 | -0.56763 | 122.0993 | 122.0078 | 121.9299 | 0.073242 | -0.004578 | -0.045776 | 0.004577 | -0.10529 | 0.45319 | 0.54932 | 0.16022 | 0.59509 | 0.20599 | 0.16479 | 0.022888 | 0.49896 | 122.4655 | 0.21973 | 122.5754 | 122.1542 | 122.5296 | -0.59052 | -122.5708 | 121.9574 | 122.4197 | 121.9666 | 109.0714
1793.3438 | 122.6761 | -122.0032 | 0.45776 | -0.0051118 | -0.010098 | -0.076661 | -0.0052701 | -0.030443 | -0.050167 | -0.04146 | 0.00094606 | -0.022458 | 0.058123 | 0.04199 | -0.2183 | -0.014283 | -0.025389 | -0.022888 | 0.059509 | -0.10529 | -0.018311 | 0.13733 | -0.045776 | 0.022888 | -12.9822 | 0.44403 | -122.0581 | 0.46234 | -121.5317 | -121.7972 | -121.4218 | 121.8979 | -0.39826 | -0.47608 | 122.1405 | 122.0261 | 121.9574 | 0.12817 | 0.05951 | -0.054931 | -0.013733 | 0.004577 | 0.4715 | 0.58136 | 0.20599 | 0.63629 | 0.26093 | 0.24262 | 0.086975 | 0.52643 | 122.5204 | 0.16479 | 122.5021 | 122.0627 | 122.4472 | -0.56305 | -122.5159 | 121.9849 | 122.4655 | 121.9803 | 109.021
1795.125 | 122.6303 | -122.0444 | 0.46234 | 0.0025177 | -0.013943 | -0.077515 | -0.0076199 | -0.032152 | -0.048886 | -0.041887 | -0.0021057 | -0.021176 | 0.057054 | 0.035367 | -0.21787 | -0.017273 | -0.023039 | -0.068665 | 0.073242 | -0.09613 | -0.032043 | 0.13275 | -0.013733 | 0.036621 | -13.0508 | 0.45776 | -122.0901 | 0.39825 | -121.5591 | -121.8475 | -121.4859 | 121.9482 | -0.3891 | -0.49438 | 122.1771 | 122.081 | 122.0306 | 0.13275 | 0.082397 | -0.045776 | -0.004577 | -0.064087 | 0.48523 | 0.55847 | 0.19684 | 0.60425 | 0.24262 | 0.22888 | 0.064087 | 0.53101 | 122.4884 | 0.16937 | 122.5479 | 122.1176 | 122.5021 | -0.55847 | -122.5525 | 122.0123 | 122.4426 | 121.9757 | 108.9935
1796.8594 | 122.6074 | -122.0306 | 0.48981 | 0.0025177 | -0.010311 | -0.080079 | -0.0037747 | -0.031939 | -0.048672 | -0.041674 | -0.0021057 | -0.02139 | 0.056841 | 0.040281 | -0.21744 | -0.015137 | -0.023467 | -0.10529 | 0.10986 | -0.12817 | -0.15564 | 0 | -0.16937 | -0.086975 | -13.2385 | 0.48523 | -122.0718 | 0.36163 | -121.6461 | -121.9345 | -121.5317 | 121.9025 | -0.37994 | -0.64545 | 122.0306 | 121.9437 | 121.8613 | 0.041199 | -0.041199 | -0.041198 | -0.004578 | -0.12817 | 0.38452 | 0.49896 | 0.096131 | 0.54016 | 0.13733 | 0.12817 | -0.027466 | 0.42572 | 122.4335 | 0.23804 | 122.5571 | 122.1405 | 122.5159 | -0.61798 | -122.5616 | 121.875 | 122.3923 | 121.9254 | 108.7921
1798.6406 | 122.6395 | -122.0581 | 0.4715 | 0.0025177 | -0.01672 | -0.07837 | -0.0069791 | -0.034289 | -0.049313 | -0.03911 | -0.0021057 | -0.021176 | 0.055986 | 0.043485 | -0.21894 | -0.016846 | -0.024962 | -0.050354 | 0.064087 | -0.10529 | -0.018311 | 0.12817 | -0.036621 | 0.032043 | -13.2156 | 0.44861 | -122.0764 | 0.3891 | -121.5775 | -121.843 | -121.4859 | 121.9528 | -0.40741 | -0.48981 | 122.1863 | 122.0901 | 122.0215 | 0.13733 | 0.068665 | -0.018311 | -0.022889 | -0.082398 | 0.48065 | 0.5722 | 0.21515 | 0.59051 | 0.23346 | 0.23346 | 0.086975 | 0.49896 | 122.4655 | 0.16937 | 122.525 | 122.1222 | 122.5067 | -0.57678 | -122.5479 | 122.0398 | 122.4472 | 122.0078 | 108.8425
1800.375 | 122.6807 | -122.0078 | 0.45319 | -0.0051118 | -0.015225 | -0.07837 | -0.0071927 | -0.031511 | -0.051235 | -0.043169 | 0.00094606 | -0.021817 | 0.058763 | 0.045621 | -0.21851 | -0.01706 | -0.023039 | -0.059509 | 0.054932 | -0.082397 | -0.009155 | 0.16479 | 0 | 0.068665 | -13.2248 | 0.44403 | -122.0581 | 0.43488 | -121.5042 | -121.7651 | -121.4401 | 121.9254 | -0.39825 | -0.46234 | 122.1725 | 122.0764 | 122.0078 | 0.15106 | 0.082397 | -0.050354 | -0.009155 | -0.018311 | 0.50354 | 0.56763 | 0.24261 | 0.61798 | 0.29297 | 0.24719 | 0.073242 | 0.55389 | 122.493 | 0.13733 | 122.5021 | 122.0627 | 122.4518 | -0.53558 | -122.5113 | 121.9986 | 122.4426 | 121.9482 | 108.783
1802.1562 | 122.6486 | -122.081 | 0.43945 | 0.0025177 | -0.013729 | -0.078156 | -0.0069791 | -0.03322 | -0.048031 | -0.041246 | -0.0021057 | -0.020749 | 0.056627 | 0.040494 | -0.21937 | -0.015992 | -0.023467 | -0.09613 | 0.086975 | -0.09613 | -0.086975 | 0.059509 | -0.082397 | -0.009155 | -13.4583 | 0.44403 | -122.113 | 0.37994 | -121.6187 | -121.875 | -121.5134 | 121.9849 | -0.35248 | -0.52643 | 122.1405 | 122.0718 | 121.9986 | 0.086975 | 0.013733 | -0.032043 | 0.004578 | -0.059509 | 0.46234 | 0.56763 | 0.20599 | 0.59967 | 0.23804 | 0.15564 | 0.009155 | 0.49439 | 122.493 | 0.1831 | 122.5571 | 122.168 | 122.525 | -0.53558 | -122.5525 | 121.994 | 122.4609 | 121.9849 | 108.6227
1803.8906 | 122.7081 | -122.0398 | 0.43488 | 0.0025177 | -0.014584 | -0.080719 | -0.0061245 | -0.032366 | -0.048886 | -0.040178 | -0.0021057 | -0.021604 | 0.0562 | 0.047758 | -0.22278 | -0.01706 | -0.019194 | -0.10071 | 0.064087 | -0.09613 | -0.054932 | 0.10529 | -0.027466 | 0.036621 | -13.4949 | 0.43945 | -122.113 | 0.40741 | -121.5591 | -121.8246 | -121.4584 | 121.9437 | -0.37079 | -0.48981 | 122.1451 | 122.0764 | 122.0123 | 0.13275 | 0.068664 | -0.073242 | 0.004578 | -0.027465 | 0.48065 | 0.58136 | 0.21515 | 0.6546 | 0.28839 | 0.20142 | 0.041198 | 0.55389 | 122.5204 | 0.16022 | 122.5525 | 122.1039 | 122.4792 | -0.531 | -122.5479 | 121.9849 | 122.4472 | 121.9391 | 108.5449
1805.6875 | 122.5754 | -122.0993 | 0.48523 | 0.017777 | -0.01437 | -0.079438 | -0.0031337 | -0.032152 | -0.050808 | -0.041033 | 0.00094606 | -0.01904 | 0.0609 | 0.048612 | -0.21744 | -0.015992 | -0.022612 | -0.14648 | 0.11444 | -0.13275 | -0.16937 | -0.027466 | -0.15106 | -0.082397 | -13.6871 | 0.48065 | -122.1313 | 0.29755 | -121.6736 | -121.9803 | -121.5912 | 121.9666 | -0.37079 | -0.6546 | 122.0718 | 122.0169 | 121.9482 | 0.050354 | -0.018311 | -0.032044 | -0.004577 | -0.18768 | 0.42572 | 0.50812 | 0.11902 | 0.54016 | 0.15106 | 0.10529 | -0.036622 | 0.45776 | 122.4289 | 0.24719 | 122.612 | 122.2137 | 122.58 | -0.61798 | -122.6166 | 121.9299 | 122.3969 | 121.9528 | 108.4122
1807.4688 | 122.6624 | -122.0673 | 0.45776 | -0.0051118 | -0.011593 | -0.079651 | -0.0056973 | -0.028521 | -0.04974 | -0.043169 | -0.0082091 | -0.020963 | 0.0562 | 0.047117 | -0.21979 | -0.017701 | -0.024107 | -0.10529 | 0.068665 | -0.09613 | -0.07782 | 0.064087 | -0.073242 | -0.009155 | -13.7329 | 0.45776 | -122.1085 | 0.37537 | -121.6003 | -121.8933 | -121.5134 | 121.9711 | -0.3891 | -0.53558 | 122.1313 | 122.0581 | 121.994 | 0.086975 | 0.022888 | -0.041198 | 0 | -0.082398 | 0.46692 | 0.55389 | 0.17395 | 0.59509 | 0.21515 | 0.16022 | 0.01831 | 0.50812 | 122.4838 | 0.16479 | 122.5662 | 122.1359 | 122.525 | -0.55389 | -122.5662 | 121.9894 | 122.4426 | 121.962 | 108.3344
1809.1875 | 122.5571 | -122.0947 | 0.48981 | 0.0025177 | -0.013729 | -0.079865 | -0.0029201 | -0.029802 | -0.051235 | -0.040178 | -0.0021057 | -0.01904 | 0.055773 | 0.04498 | -0.22001 | -0.016633 | -0.025603 | -0.12817 | 0.10986 | -0.12817 | -0.14648 | -0.004578 | -0.13733 | -0.064087 | -13.7375 | 0.49896 | -122.1451 | 0.29755 | -121.669 | -121.9574 | -121.5866 | 121.9666 | -0.37994 | -0.63629 | 122.0901 | 122.0306 | 121.9574 | 0.064087 | -0.009155 | -0.050354 | 0.009155 | -0.19226 | 0.42572 | 0.50812 | 0.13733 | 0.55847 | 0.18768 | 0.1236 | -0.01831 | 0.47608 | 122.4426 | 0.23804 | 122.644 | 122.2046 | 122.5937 | -0.61798 | -122.6349 | 121.9482 | 122.3923 | 121.9666 | 108.3572
1810.9844 | 122.6532 | -122.0947 | 0.46692 | 0.0025177 | -0.015652 | -0.079224 | -0.0074063 | -0.034075 | -0.050808 | -0.039537 | 0.00094606 | -0.022031 | 0.055345 | 0.051603 | -0.22001 | -0.015351 | -0.025389 | -0.054932 | 0.068665 | -0.09613 | -0.027466 | 0.11444 | -0.022888 | 0.032043 | -13.6459 | 0.45319 | -122.1085 | 0.36621 | -121.6003 | -121.8887 | -121.5134 | 121.9986 | -0.39825 | -0.49438 | 122.2092 | 122.1268 | 122.0718 | 0.12817 | 0.073242 | -0.013732 | -0.013733 | -0.10071 | 0.49439 | 0.58136 | 0.20599 | 0.59509 | 0.21973 | 0.21057 | 0.068664 | 0.50812 | 122.4747 | 0.16479 | 122.5616 | 122.1634 | 122.5479 | -0.56305 | -122.5754 | 122.0673 | 122.4609 | 122.0398 | 108.4488
1812.7656 | 122.7173 | -122.0215 | 0.45776 | -0.0051118 | -0.012875 | -0.076447 | -0.0046291 | -0.032152 | -0.048245 | -0.038896 | -0.0021057 | -0.021604 | 0.054918 | 0.053098 | -0.21766 | -0.014924 | -0.02368 | -0.041199 | 0.064087 | -0.086975 | -0.022888 | 0.13275 | -0.041199 | 0.018311 | -13.8153 | 0.42572 | -122.113 | 0.42572 | -121.5637 | -121.8475 | -121.4676 | 121.9345 | -0.39368 | -0.48065 | 122.1542 | 122.0398 | 121.9803 | 0.10529 | 0.045776 | -0.091553 | -0.032044 | -0.032044 | 0.45776 | 0.55389 | 0.17395 | 0.64545 | 0.2655 | 0.21973 | 0.064087 | 0.54932 | 122.5388 | 0.15106 | 122.5388 | 122.0856 | 122.4472 | -0.54474 | -122.5708 | 121.9986 | 122.4472 | 121.9803 | 108.2062
1814.5 | 122.7127 | -122.0581 | 0.43488 | -0.0051118 | -0.013729 | -0.079651 | -0.0065517 | -0.032366 | -0.048886 | -0.04146 | 0.00094606 | -0.020963 | 0.056627 | 0.049039 | -0.21937 | -0.018128 | -0.023253 | -0.064087 | 0.073242 | -0.091553 | -0.045776 | 0.11444 | -0.032043 | 0.032043 | -13.9297 | 0.44403 | -122.1176 | 0.43488 | -121.5591 | -121.8246 | -121.4722 | 121.9666 | -0.36163 | -0.48065 | 122.1725 | 122.0901 | 122.0261 | 0.1236 | 0.05951 | -0.05951 | 0.009156 | 0 | 0.49896 | 0.58594 | 0.23346 | 0.64545 | 0.29297 | 0.20599 | 0.045777 | 0.55847 | 122.5525 | 0.16479 | 122.5616 | 122.1313 | 122.5021 | -0.52643 | -122.5525 | 122.0123 | 122.493 | 121.994 | 108.1284
1816.2812 | 122.58 | -122.1405 | 0.46234 | -0.0051118 | -0.015011 | -0.08136 | -0.0037747 | -0.030871 | -0.050595 | -0.040178 | -0.0051575 | -0.018186 | 0.058336 | 0.049253 | -0.21808 | -0.014924 | -0.023253 | -0.13733 | 0.11444 | -0.13733 | -0.14648 | -0.013733 | -0.14191 | -0.073242 | -14.0488 | 0.46234 | -122.1451 | 0.28839 | -121.7056 | -122.0032 | -121.6141 | 122.0032 | -0.3479 | -0.60882 | 122.1268 | 122.0673 | 121.9986 | 0.064087 | -0.004578 | -0.004578 | 0 | -0.17395 | 0.43488 | 0.52643 | 0.13733 | 0.53101 | 0.14191 | 0.1236 | -0.009155 | 0.43945 | 122.4335 | 0.25177 | 122.6074 | 122.2549 | 122.6028 | -0.59967 | -122.6074 | 121.994 | 122.4289 | 122.0032 | 108.0917
1818.0469 | 122.6349 | -122.1268 | 0.46234 | -0.012741 | -0.012234 | -0.080292 | -0.0052701 | -0.028307 | -0.051449 | -0.04146 | -0.0021057 | -0.019254 | 0.057054 | 0.04968 | -0.21958 | -0.016205 | -0.020689 | -0.11902 | 0.10986 | -0.13733 | -0.15106 | -0.009155 | -0.13733 | -0.068665 | -14.0854 | 0.45776 | -122.1771 | 0.30212 | -121.6736 | -121.9757 | -121.5637 | 121.9894 | -0.35248 | -0.6134 | 122.1176 | 122.0581 | 121.9894 | 0.068664 | 0 | -0.050354 | -0.004577 | -0.16022 | 0.45319 | 0.56305 | 0.15106 | 0.6134 | 0.20142 | 0.12817 | -0.013733 | 0.50354 | 122.4792 | 0.24719 | 122.6349 | 122.2366 | 122.5845 | -0.59967 | -122.6395 | 121.9757 | 122.4289 | 122.0078 | 108.0414
1819.7656 | 122.7036 | -122.0764 | 0.42114 | -0.0051118 | -0.0098843 | -0.077515 | -0.0054837 | -0.031725 | -0.04739 | -0.040605 | 0.0070497 | -0.020108 | 0.057268 | 0.042631 | -0.21851 | -0.016205 | -0.022398 | -0.022888 | 0.059509 | -0.091553 | -0.018311 | 0.10986 | -0.041199 | 0.018311 | -14.1815 | 0.42114 | -122.1359 | 0.43488 | -121.6141 | -121.8933 | -121.4859 | 121.9849 | -0.36163 | -0.43945 | 122.1863 | 122.0947 | 122.0352 | 0.10986 | 0.050354 | -0.059509 | 0 | 0.013732 | 0.46234 | 0.59051 | 0.1831 | 0.65002 | 0.24261 | 0.20142 | 0.073242 | 0.52185 | 122.5708 | 0.15106 | 122.5571 | 122.1359 | 122.4976 | -0.5127 | -122.5571 | 122.0581 | 122.5113 | 122.0535 | 107.8949
1821.5625 | 122.7356 | -122.0947 | 0.42114 | 0.0025177 | -0.014798 | -0.080292 | -0.0091153 | -0.031084 | -0.051663 | -0.041674 | 0.00094606 | -0.020322 | 0.05855 | 0.036863 | -0.21766 | -0.016846 | -0.020049 | -0.054932 | 0.073242 | -0.086975 | -0.004578 | 0.16022 | -0.004578 | 0.068665 | -14.1678 | 0.39825 | -122.1451 | 0.41199 | -121.5546 | -121.8384 | -121.4813 | 122.0078 | -0.3479 | -0.42572 | 122.2549 | 122.1634 | 122.0901 | 0.15564 | 0.082397 | -0.050354 | -0.022889 | -0.009156 | 0.54016 | 0.6134 | 0.25635 | 0.66376 | 0.3067 | 0.24719 | 0.082397 | 0.59052 | 122.5571 | 0.16022 | 122.5433 | 122.168 | 122.493 | -0.50812 | -122.5662 | 122.0901 | 122.5067 | 122.0398 | 107.9269
1823.2656 | 122.699 | -122.0901 | 0.40283 | -0.0051118 | -0.014157 | -0.079224 | -0.0050565 | -0.028734 | -0.050595 | -0.043383 | -0.0021057 | -0.01904 | 0.057054 | 0.050748 | -0.22043 | -0.015565 | -0.022826 | -0.10529 | 0.091553 | -0.10986 | -0.09613 | 0.050354 | -0.14191 | -0.054932 | -14.3921 | 0.41657 | -122.1725 | 0.38452 | -121.6415 | -121.9254 | -121.5134 | 121.9803 | -0.31128 | -0.49896 | 122.1405 | 122.0352 | 121.9482 | 0.054931 | -0.032044 | -0.082397 | 0.013733 | -0.018311 | 0.44861 | 0.57678 | 0.16479 | 0.65918 | 0.24719 | 0.16022 | 0.013733 | 0.531 | 122.5571 | 0.20142 | 122.5891 | 122.1817 | 122.5067 | -0.5127 | -122.5754 | 121.994 | 122.4747 | 121.9849 | 107.6981
1825.0469 | 122.699 | -122.1268 | 0.3891 | -0.0051118 | -0.012234 | -0.080933 | -0.0069791 | -0.031298 | -0.04974 | -0.040178 | -0.0021057 | -0.020108 | 0.055345 | 0.047544 | -0.22043 | -0.018555 | -0.022826 | -0.10071 | 0.073242 | -0.10071 | -0.068665 | 0.073242 | -0.068665 | 0 | -14.4058 | 0.3891 | -122.2046 | 0.32959 | -121.6415 | -121.9208 | -121.5454 | 122.0261 | -0.31586 | -0.45776 | 122.2 | 122.1268 | 122.0581 | 0.10071 | 0.032043 | -0.07782 | 0 | -0.059509 | 0.48523 | 0.58136 | 0.20599 | 0.65918 | 0.28381 | 0.17395 | 0.032043 | 0.56305 | 122.5342 | 0.17395 | 122.5937 | 122.2 | 122.5159 | -0.48981 | -122.5937 | 122.0581 | 122.4564 | 122.0261 | 107.7209
1826.7656 | 122.7173 | -122.1176 | 0.36163 | 0.0025177 | -0.013089 | -0.079438 | -0.0063381 | -0.030871 | -0.052944 | -0.036974 | -0.0021057 | -0.023099 | 0.057482 | 0.049467 | -0.22001 | -0.018342 | -0.024107 | -0.041199 | 0.073242 | -0.082397 | 0 | 0.16479 | -0.009155 | 0.041199 | -14.3692 | 0.37537 | -122.1771 | 0.37079 | -121.6187 | -121.8887 | -121.5408 | 122.0352 | -0.28839 | -0.36163 | 122.2824 | 122.1588 | 122.1085 | 0.1236 | 0.073242 | -0.059509 | 0.013733 | 0.009156 | 0.49896 | 0.57678 | 0.22888 | 0.63629 | 0.28839 | 0.24719 | 0.082397 | 0.55847 | 122.5479 | 0.15564 | 122.5525 | 122.1909 | 122.493 | -0.44403 | -122.5388 | 122.1176 | 122.4884 | 122.0764 | 107.7484
1828.5625 | 122.6395 | -122.1588 | 0.41657 | -0.0051118 | -0.015438 | -0.079865 | -0.0031337 | -0.032793 | -0.050381 | -0.041674 | -0.0051575 | -0.017118 | 0.056414 | 0.047544 | -0.21915 | -0.014283 | -0.024962 | -0.09613 | 0.11444 | -0.11444 | -0.12817 | 0 | -0.1236 | -0.054932 | -14.5157 | 0.42114 | -122.2046 | 0.29297 | -121.7056 | -122.0123 | -121.6324 | 122.0444 | -0.30212 | -0.54474 | 122.1588 | 122.1039 | 122.0352 | 0.059509 | -0.009155 | -0.045777 | 0.004578 | -0.1236 | 0.45319 | 0.52643 | 0.14648 | 0.5722 | 0.19226 | 0.11444 | -0.013733 | 0.49896 | 122.4976 | 0.22888 | 122.6257 | 122.2733 | 122.58 | -0.53101 | -122.6212 | 122.0306 | 122.4518 | 122.0627 | 107.6431
1830.2812 | 122.7081 | -122.0947 | 0.4303 | 0.0025177 | -0.013729 | -0.079438 | -0.0069791 | -0.035998 | -0.051663 | -0.041033 | -0.0021057 | -0.020963 | 0.057695 | 0.042417 | -0.21937 | -0.01706 | -0.023467 | -0.091553 | 0.064087 | -0.086975 | -0.068665 | 0.082397 | -0.082397 | 0.009155 | -14.6484 | 0.41657 | -122.1588 | 0.37994 | -121.6049 | -121.8933 | -121.5179 | 122.0078 | -0.36621 | -0.49896 | 122.1771 | 122.1039 | 122.0123 | 0.09613 | 0.004578 | -0.064086 | -0.013733 | -0.050354 | 0.48981 | 0.57678 | 0.20142 | 0.64087 | 0.2655 | 0.16937 | 0.01831 | 0.55389 | 122.5388 | 0.15106 | 122.5754 | 122.1588 | 122.5113 | -0.51727 | -122.5891 | 122.0261 | 122.4747 | 122.0032 | 107.4463
1832.0469 | 122.6028 | -122.1405 | 0.45776 | -0.012741 | -0.015438 | -0.082428 | -0.0050565 | -0.034289 | -0.051022 | -0.044237 | 0.00094606 | -0.019895 | 0.056627 | 0.047117 | -0.21958 | -0.014924 | -0.024321 | -0.086975 | 0.10071 | -0.11444 | -0.12817 | 0.027466 | -0.12817 | -0.059509 | -14.7903 | 0.46234 | -122.1817 | 0.29755 | -121.6965 | -121.994 | -121.6324 | 122.0261 | -0.35706 | -0.58594 | 122.168 | 122.081 | 122.0123 | 0.054932 | -0.013733 | -0.041199 | 0.004577 | -0.16022 | 0.44403 | 0.50812 | 0.14648 | 0.54932 | 0.18768 | 0.14191 | -0.013733 | 0.48523 | 122.4792 | 0.21515 | 122.644 | 122.2412 | 122.6028 | -0.5722 | -122.6395 | 122.0123 | 122.438 | 122.0535 | 107.3502
1833.8281 | 122.6028 | -122.1313 | 0.45776 | 0.010147 | -0.011593 | -0.079865 | -0.0048427 | -0.030016 | -0.047817 | -0.039324 | -0.0021057 | -0.019254 | 0.056627 | 0.043272 | -0.21851 | -0.015778 | -0.02133 | -0.082397 | 0.086975 | -0.11444 | -0.1236 | 0 | -0.14191 | -0.073242 | -14.8956 | 0.44403 | -122.1771 | 0.31586 | -121.7422 | -122.0444 | -121.6232 | 122.0169 | -0.37079 | -0.58136 | 122.1313 | 122.0581 | 121.9894 | 0.041199 | -0.027466 | -0.045776 | -0.013733 | -0.14191 | 0.3891 | 0.50812 | 0.086975 | 0.55389 | 0.13275 | 0.11444 | -0.009155 | 0.43488 | 122.493 | 0.20142 | 122.6212 | 122.2183 | 122.5754 | -0.5722 | -122.6349 | 122.0078 | 122.4472 | 122.049 | 107.2357
1835.6094 | 122.7264 | -122.0993 | 0.42114 | -0.0051118 | -0.011593 | -0.077942 | -0.0046291 | -0.030871 | -0.046963 | -0.040605 | -0.0021057 | -0.019467 | 0.057482 | 0.048398 | -0.21915 | -0.014283 | -0.022185 | -0.082397 | 0.091553 | -0.10986 | -0.050354 | 0.086975 | -0.091553 | -0.004578 | -14.8773 | 0.41199 | -122.168 | 0.40741 | -121.6232 | -121.9208 | -121.4905 | 121.9894 | -0.32959 | -0.4715 | 122.1863 | 122.0947 | 122.0078 | 0.10529 | 0.01831 | -0.068665 | -0.009156 | -0.013733 | 0.47607 | 0.60883 | 0.17853 | 0.67749 | 0.24719 | 0.19684 | 0.059509 | 0.54474 | 122.5754 | 0.20142 | 122.58 | 122.1909 | 122.5113 | -0.53101 | -122.5891 | 122.049 | 122.5067 | 122.0169 | 107.222
1837.3906 | 122.6074 | -122.1497 | 0.45776 | -0.012741 | -0.013302 | -0.080292 | -0.0078335 | -0.029589 | -0.052517 | -0.042742 | -0.0021057 | -0.021176 | 0.057482 | 0.050748 | -0.21894 | -0.015778 | -0.021758 | -0.13275 | 0.09613 | -0.15106 | -0.14648 | 0.004578 | -0.1236 | -0.064087 | -15.0284 | 0.44403 | -122.2092 | 0.24719 | -121.7377 | -122.0215 | -121.6507 | 121.9986 | -0.36163 | -0.60425 | 122.1542 | 122.0856 | 122.0261 | 0.086975 | 0.027466 | -0.059509 | -0.013733 | -0.21057 | 0.41199 | 0.49896 | 0.12817 | 0.55847 | 0.18768 | 0.15564 | 0.004578 | 0.4715 | 122.4564 | 0.24719 | 122.6532 | 122.2458 | 122.5937 | -0.60883 | -122.6669 | 122.0032 | 122.3969 | 122.0169 | 107.1213
1839.0938 | 122.7219 | -122.0901 | 0.41199 | -0.0051118 | -0.013516 | -0.080292 | -0.0050565 | -0.026171 | -0.050808 | -0.042101 | -0.0051575 | -0.019467 | 0.058123 | 0.049253 | -0.21851 | -0.01706 | -0.021971 | -0.068665 | 0.091553 | -0.10071 | -0.036621 | 0.10071 | -0.073242 | -0.009155 | -14.9963 | 0.42114 | -122.1634 | 0.40741 | -121.6278 | -121.9116 | -121.5042 | 121.9894 | -0.32043 | -0.44861 | 122.1909 | 122.081 | 122.0169 | 0.091553 | 0.027466 | -0.073242 | 0.009156 | -0.004577 | 0.46234 | 0.58594 | 0.17853 | 0.65918 | 0.25177 | 0.20142 | 0.064087 | 0.53558 | 122.5708 | 0.19226 | 122.5845 | 122.1817 | 122.5113 | -0.5127 | -122.5754 | 122.0535 | 122.4976 | 122.0215 | 107.0938
1840.875 | 122.7356 | -122.0947 | 0.44403 | 0.0025177 | -0.012234 | -0.080506 | -0.0046291 | -0.031725 | -0.052517 | -0.042101 | -0.0021057 | -0.020536 | 0.058123 | 0.040067 | -0.21915 | -0.014496 | -0.023253 | -0.059509 | 0.086975 | -0.09613 | -0.018311 | 0.12817 | -0.064087 | 0.018311 | -15.0833 | 0.41657 | -122.1359 | 0.43488 | -121.6049 | -121.8887 | -121.4951 | 121.9986 | -0.35706 | -0.46234 | 122.2229 | 122.113 | 122.0306 | 0.11444 | 0.032043 | -0.041198 | -0.027466 | -0.009156 | 0.48981 | 0.59967 | 0.20599 | 0.64087 | 0.24719 | 0.2243 | 0.077819 | 0.53101 | 122.5708 | 0.1831 | 122.5525 | 122.1817 | 122.5113 | -0.54016 | -122.58 | 122.0764 | 122.5296 | 122.0352 | 107.0114
1842.6719 | 122.6807 | -122.1176 | 0.42572 | 0.0025177 | -0.012234 | -0.077088 | -0.0082607 | -0.033007 | -0.052517 | -0.040178 | -0.0021057 | -0.022458 | 0.057482 | 0.046476 | -0.21808 | -0.016205 | -0.020262 | -0.07782 | 0.064087 | -0.09613 | -0.045776 | 0.1236 | -0.07782 | 0 | -15.1199 | 0.40283 | -122.1909 | 0.35706 | -121.6644 | -121.9437 | -121.5637 | 122.0215 | -0.36163 | -0.4715 | 122.2412 | 122.1176 | 122.0398 | 0.09613 | 0.01831 | -0.073242 | -0.022888 | -0.068664 | 0.45319 | 0.55389 | 0.17395 | 0.62714 | 0.24719 | 0.21973 | 0.050354 | 0.52643 | 122.5479 | 0.16022 | 122.5937 | 122.1817 | 122.5204 | -0.52185 | -122.6166 | 122.0718 | 122.4747 | 122.0398 | 106.9977
1844.3906 | 122.7402 | -122.0947 | 0.40741 | -0.0051118 | -0.0096707 | -0.077942 | -0.0033475 | -0.03023 | -0.050595 | -0.039965 | 0.0070497 | -0.020963 | 0.057482 | 0.044126 | -0.21851 | -0.016419 | -0.023039 | -0.045776 | 0.064087 | -0.09613 | -0.036621 | 0.10986 | -0.050354 | 0.009155 | -15.1291 | 0.39368 | -122.1588 | 0.42572 | -121.6187 | -121.9208 | -121.4905 | 121.9986 | -0.34332 | -0.44403 | 122.2046 | 122.1039 | 122.0444 | 0.10528 | 0.045776 | -0.064086 | -0.013733 | 0.01831 | 0.47608 | 0.60425 | 0.17395 | 0.66833 | 0.23804 | 0.20599 | 0.059509 | 0.54016 | 122.5845 | 0.16022 | 122.5525 | 122.1588 | 122.4884 | -0.50354 | -122.5662 | 122.0581 | 122.5204 | 122.049 | 106.9656
1846.1719 | 122.699 | -122.1222 | 0.40283 | -0.0051118 | -0.011166 | -0.078156 | -0.0082607 | -0.029802 | -0.048672 | -0.039537 | -0.0021057 | -0.02139 | 0.057695 | 0.048398 | -0.22022 | -0.015778 | -0.024535 | -0.050354 | 0.059509 | -0.082397 | -0.018311 | 0.13275 | -0.050354 | 0.036621 | -15.2481 | 0.40741 | -122.1771 | 0.37994 | -121.6507 | -121.9391 | -121.55 | 122.0398 | -0.34332 | -0.42114 | 122.2549 | 122.1588 | 122.0718 | 0.11902 | 0.032043 | -0.054932 | 0.004578 | -0.022888 | 0.4715 | 0.5722 | 0.1831 | 0.62714 | 0.23804 | 0.21515 | 0.064086 | 0.52643 | 122.5571 | 0.14191 | 122.5845 | 122.1817 | 122.5296 | -0.48523 | -122.58 | 122.1039 | 122.5021 | 122.0718 | 106.8741
1847.9688 | 122.7219 | -122.113 | 0.41657 | -0.0051118 | -0.014157 | -0.079438 | -0.0078335 | -0.031084 | -0.051022 | -0.041674 | 0.00094606 | -0.019681 | 0.058977 | 0.046476 | -0.2183 | -0.015565 | -0.019621 | -0.041199 | 0.07782 | -0.09613 | -0.004578 | 0.15564 | -0.009155 | 0.045776 | -15.3397 | 0.3891 | -122.1909 | 0.37079 | -121.6415 | -121.8979 | -121.5363 | 122.0169 | -0.33875 | -0.42114 | 122.2687 | 122.1588 | 122.1039 | 0.14191 | 0.086975 | -0.07782 | -0.027466 | -0.045776 | 0.4715 | 0.57678 | 0.21515 | 0.6546 | 0.29297 | 0.25177 | 0.091552 | 0.54932 | 122.5616 | 0.17395 | 122.58 | 122.1909 | 122.5021 | -0.5127 | -122.6074 | 122.1085 | 122.4838 | 122.0718 | 106.7734
1849.6875 | 122.7402 | -122.113 | 0.41657 | 0.0025177 | -0.015011 | -0.080719 | -0.0078335 | -0.034929 | -0.052304 | -0.040819 | -0.0051575 | -0.02139 | 0.057482 | 0.042417 | -0.2215 | -0.017487 | -0.026885 | -0.050354 | 0.068665 | -0.082397 | 0.018311 | 0.18768 | 0.004578 | 0.054932 | -15.39 | 0.39825 | -122.1909 | 0.37994 | -121.6003 | -121.8887 | -121.55 | 122.0306 | -0.3479 | -0.39825 | 122.3007 | 122.168 | 122.1176 | 0.13733 | 0.086975 | -0.07782 | -0.018311 | -0.036621 | 0.5127 | 0.56305 | 0.2243 | 0.64087 | 0.30212 | 0.27008 | 0.10071 | 0.59051 | 122.5708 | 0.15106 | 122.5891 | 122.1817 | 122.5113 | -0.49896 | -122.6074 | 122.1313 | 122.493 | 122.0627 | 106.723
1851.4688 | 122.6395 | -122.1588 | 0.4303 | -0.0051118 | -0.0090299 | -0.079011 | -0.0029201 | -0.029802 | -0.049313 | -0.038896 | -0.0021057 | -0.018613 | 0.059191 | 0.051816 | -0.21958 | -0.014283 | -0.023039 | -0.11902 | 0.10529 | -0.13275 | -0.15106 | -0.009155 | -0.1831 | -0.082397 | -15.5777 | 0.4303 | -122.2275 | 0.3067 | -121.7606 | -122.0627 | -121.6507 | 122.0261 | -0.32501 | -0.58136 | 122.1497 | 122.0764 | 121.9757 | 0.050354 | -0.050354 | -0.068665 | 0 | -0.1236 | 0.39825 | 0.50812 | 0.09613 | 0.57678 | 0.16479 | 0.1236 | -0.018311 | 0.46692 | 122.5342 | 0.23804 | 122.6578 | 122.2641 | 122.5891 | -0.56305 | -122.6578 | 122.0078 | 122.4655 | 122.0398 | 106.5811
1853.25 | 122.6212 | -122.168 | 0.43945 | -0.0051118 | -0.011593 | -0.080079 | -0.0024929 | -0.028093 | -0.047604 | -0.039324 | -0.0021057 | -0.017331 | 0.059191 | 0.048826 | -0.22001 | -0.013856 | -0.026457 | -0.07782 | 0.10529 | -0.11444 | -0.086975 | 0.041199 | -0.1236 | -0.045776 | -15.5228 | 0.40741 | -122.2366 | 0.28839 | -121.7468 | -122.0627 | -121.637 | 122.0535 | -0.33417 | -0.52643 | 122.2092 | 122.1222 | 122.0444 | 0.068665 | -0.009155 | -0.068664 | -0.032043 | -0.15106 | 0.42114 | 0.53101 | 0.10529 | 0.59967 | 0.17395 | 0.15564 | 0.027466 | 0.48981 | 122.525 | 0.21973 | 122.644 | 122.2733 | 122.5754 | -0.55389 | -122.6761 | 122.081 | 122.4564 | 122.0901 | 106.6452
1854.9844 | 122.5891 | -122.1725 | 0.42572 | -0.0051118 | -0.0088163 | -0.078583 | -0.0037747 | -0.030657 | -0.051449 | -0.038683 | -0.0051575 | -0.018827 | 0.058977 | 0.050321 | -0.2183 | -0.015992 | -0.024107 | -0.13733 | 0.10071 | -0.1236 | -0.16937 | -0.045776 | -0.18768 | -0.10986 | -15.7288 | 0.42572 | -122.2458 | 0.2655 | -121.8384 | -122.1313 | -121.6965 | 122.0489 | -0.32501 | -0.59509 | 122.1268 | 122.0627 | 121.9849 | 0.013733 | -0.064087 | -0.073243 | 0 | -0.16022 | 0.33417 | 0.47607 | 0.041198 | 0.54932 | 0.11444 | 0.07782 | -0.045777 | 0.40741 | 122.5113 | 0.2243 | 122.6715 | 122.2733 | 122.5983 | -0.54932 | -122.6715 | 122.0032 | 122.438 | 122.0352 | 106.4438
1856.7812 | 122.7448 | -122.1771 | 0.37537 | -0.012741 | -0.0098843 | -0.078583 | -0.0056973 | -0.032366 | -0.048672 | -0.042101 | -0.0021057 | -0.023313 | 0.057482 | 0.040922 | -0.21723 | -0.014496 | -0.02368 | -0.036621 | 0.068665 | -0.086975 | -0.022888 | 0.13733 | -0.045776 | 0.022888 | -15.5823 | 0.37537 | -122.2092 | 0.39368 | -121.6507 | -121.9208 | -121.5317 | 122.0901 | -0.3067 | -0.39825 | 122.3145 | 122.2 | 122.1313 | 0.10986 | 0.041199 | -0.032043 | 0 | 0.018311 | 0.52643 | 0.64545 | 0.25635 | 0.67749 | 0.28839 | 0.2243 | 0.064087 | 0.55847 | 122.6028 | 0.15564 | 122.5845 | 122.2458 | 122.5525 | -0.46234 | -122.5845 | 122.1542 | 122.5708 | 122.1405 | 106.5948
1858.5 | 122.7127 | -122.1588 | 0.37994 | -0.0051118 | -0.012448 | -0.079865 | -0.0067653 | -0.030016 | -0.049099 | -0.039537 | 0.00094606 | -0.021604 | 0.05855 | 0.041563 | -0.21894 | -0.015778 | -0.024535 | -0.10529 | 0.091553 | -0.10986 | -0.10529 | 0.059509 | -0.09613 | -0.013733 | -15.715 | 0.3891 | -122.2229 | 0.32044 | -121.7102 | -121.9894 | -121.6141 | 122.0489 | -0.28839 | -0.48523 | 122.2183 | 122.1451 | 122.0627 | 0.09613 | 0.013733 | -0.064087 | 0.009155 | -0.059509 | 0.44861 | 0.54474 | 0.16937 | 0.60882 | 0.23346 | 0.16937 | 0.004577 | 0.51269 | 122.5433 | 0.20142 | 122.612 | 122.2504 | 122.5479 | -0.48981 | -122.6028 | 122.0535 | 122.4792 | 122.0535 | 106.4438
1860.2812 | 122.7448 | -122.1497 | 0.38452 | 0.0025177 | -0.010739 | -0.077088 | -0.0071927 | -0.028307 | -0.050167 | -0.04146 | -0.0021057 | -0.02139 | 0.056627 | 0.045408 | -0.22022 | -0.015351 | -0.021544 | -0.036621 | 0.07782 | -0.10071 | -0.009155 | 0.12817 | -0.059509 | 0.022888 | -15.6967 | 0.37994 | -122.1725 | 0.39368 | -121.6461 | -121.9437 | -121.5363 | 122.049 | -0.3067 | -0.39368 | 122.2778 | 122.1725 | 122.0901 | 0.1236 | 0.041199 | -0.022888 | -0.004577 | 0.009156 | 0.50354 | 0.6134 | 0.20599 | 0.63629 | 0.22888 | 0.22888 | 0.091553 | 0.52643 | 122.5662 | 0.17853 | 122.5525 | 122.2275 | 122.5296 | -0.48523 | -122.5571 | 122.1405 | 122.5433 | 122.113 | 106.4529
1862.0781 | 122.6212 | -122.2046 | 0.43488 | -0.0051118 | -0.013729 | -0.079651 | -0.0061245 | -0.032366 | -0.051663 | -0.040392 | 0.0039979 | -0.019895 | 0.058763 | 0.042631 | -0.21851 | -0.01706 | -0.023039 | -0.15564 | 0.11444 | -0.13275 | -0.15564 | -0.013733 | -0.13275 | -0.068665 | -15.9302 | 0.41657 | -122.2321 | 0.24719 | -121.7789 | -122.0764 | -121.6965 | 122.0718 | -0.32043 | -0.59052 | 122.1909 | 122.1359 | 122.0718 | 0.064086 | 0 | -0.027466 | -0.01831 | -0.18768 | 0.42572 | 0.50812 | 0.12817 | 0.53558 | 0.15564 | 0.11902 | -0.022889 | 0.45319 | 122.4792 | 0.24719 | 122.6486 | 122.319 | 122.6212 | -0.56763 | -122.6669 | 122.0489 | 122.4518 | 122.0489 | 106.2744
1863.875 | 122.6761 | -122.1909 | 0.4303 | 0.010147 | -0.010952 | -0.080292 | -0.0050565 | -0.030443 | -0.050808 | -0.039965 | -0.0021057 | -0.018827 | 0.058763 | 0.052244 | -0.22001 | -0.014283 | -0.020262 | -0.082397 | 0.09613 | -0.1236 | -0.10529 | 0.045776 | -0.10529 | -0.041199 | -15.8752 | 0.42114 | -122.2137 | 0.32501 | -121.701 | -122.0215 | -121.6141 | 122.0673 | -0.33417 | -0.53558 | 122.2366 | 122.1497 | 122.0856 | 0.082397 | 0.01831 | -0.022888 | -0.009155 | -0.10529 | 0.48981 | 0.57678 | 0.16937 | 0.59967 | 0.19226 | 0.16937 | 0.01831 | 0.5127 | 122.5388 | 0.21973 | 122.6349 | 122.287 | 122.612 | -0.55389 | -122.644 | 122.0856 | 122.5159 | 122.1085 | 106.3156
1865.6562 | 122.6807 | -122.1817 | 0.4303 | -0.0051118 | -0.01138 | -0.07837 | -0.0050565 | -0.030443 | -0.049313 | -0.039965 | 0.00094606 | -0.020322 | 0.058977 | 0.043272 | -0.21958 | -0.014496 | -0.02368 | -0.10071 | 0.10986 | -0.1236 | -0.13275 | 0.036621 | -0.10529 | -0.036621 | -15.9988 | 0.42572 | -122.2321 | 0.32501 | -121.7285 | -122.0306 | -121.6232 | 122.0581 | -0.32044 | -0.56305 | 122.2183 | 122.1451 | 122.0764 | 0.086975 | 0.01831 | -0.050354 | -0.004578 | -0.10529 | 0.45319 | 0.55847 | 0.15106 | 0.60883 | 0.20142 | 0.16022 | -0.009155 | 0.50354 | 122.5571 | 0.23346 | 122.6578 | 122.2916 | 122.6074 | -0.55389 | -122.6624 | 122.049 | 122.5067 | 122.081 | 106.1829
1867.375 | 122.6898 | -122.168 | 0.41199 | -0.012741 | -0.012448 | -0.080079 | -0.0046291 | -0.028948 | -0.049954 | -0.042101 | -0.0021057 | -0.020322 | 0.057482 | 0.038572 | -0.21723 | -0.014069 | -0.022826 | -0.11902 | 0.11902 | -0.1236 | -0.15106 | -0.013733 | -0.16479 | -0.07782 | -16.1041 | 0.41199 | -122.2504 | 0.30212 | -121.7514 | -122.0581 | -121.6324 | 122.0444 | -0.29297 | -0.56305 | 122.1542 | 122.0901 | 122.0032 | 0.045776 | -0.041199 | -0.082397 | 0 | -0.10986 | 0.41657 | 0.53558 | 0.10986 | 0.61798 | 0.19226 | 0.10986 | -0.027466 | 0.49896 | 122.5525 | 0.24261 | 122.6624 | 122.287 | 122.58 | -0.53558 | -122.6624 | 122.0169 | 122.4701 | 122.049 | 106.0638
1869.1406 | 122.6303 | -122.1634 | 0.45319 | 0.0025177 | -0.0094571 | -0.077088 | -0.0056973 | -0.025103 | -0.049954 | -0.039965 | -0.0051575 | -0.019254 | 0.058123 | 0.048398 | -0.21787 | -0.015137 | -0.022185 | -0.11444 | 0.10986 | -0.11902 | -0.14191 | 0 | -0.16937 | -0.10529 | -16.1819 | 0.44861 | -122.2137 | 0.26093 | -121.788 | -122.113 | -121.6782 | 122.0444 | -0.34332 | -0.59509 | 122.1634 | 122.0581 | 121.994 | 0.013733 | -0.050354 | -0.050354 | -0.004578 | -0.19226 | 0.37537 | 0.48523 | 0.050354 | 0.53558 | 0.10071 | 0.11902 | -0.022888 | 0.42572 | 122.4747 | 0.22888 | 122.6624 | 122.2733 | 122.612 | -0.5722 | -122.6669 | 122.0215 | 122.4243 | 122.049 | 105.9814
1870.875 | 122.7219 | -122.1588 | 0.40283 | 0.0025177 | -0.013516 | -0.079438 | -0.0063381 | -0.03258 | -0.049313 | -0.040178 | 0.0039979 | -0.021604 | 0.055345 | 0.045408 | -0.21915 | -0.015565 | -0.019194 | -0.10986 | 0.073242 | -0.09613 | -0.091553 | 0.068665 | -0.086975 | 0 | -16.1682 | 0.39825 | -122.2229 | 0.32959 | -121.7102 | -122.0078 | -121.6095 | 122.0627 | -0.32959 | -0.49439 | 122.2275 | 122.1588 | 122.0718 | 0.09613 | 0.009155 | -0.064087 | -0.004578 | -0.073242 | 0.44861 | 0.54932 | 0.15106 | 0.6134 | 0.21515 | 0.16479 | 0.004577 | 0.51269 | 122.5525 | 0.16937 | 122.6212 | 122.2321 | 122.5571 | -0.49896 | -122.6257 | 122.0673 | 122.4884 | 122.0489 | 105.9906
1872.6719 | 122.7585 | -121.9299 | 0.59052 | -0.012741 | -0.014584 | -0.081147 | -0.0076199 | -0.03557 | -0.047817 | -0.039324 | -0.0021057 | -0.020322 | 0.058123 | 0.043485 | -0.21851 | -0.014283 | -0.024748 | -0.054932 | 0.050354 | -0.09613 | -0.013733 | 0.15564 | 0 | 0.050354 | -16.0767 | 0.57678 | -122.0261 | 0.5722 | -121.4355 | -121.7331 | -121.3669 | 121.8338 | -0.54016 | -0.60425 | 122.0856 | 121.9803 | 121.9299 | 0.14648 | 0.09613 | -0.09613 | -0.013733 | -0.01831 | 0.49438 | 0.56305 | 0.19684 | 0.65918 | 0.29297 | 0.25177 | 0.082397 | 0.59051 | 122.5983 | 0.14648 | 122.6028 | 121.9803 | 122.5067 | -0.68664 | -122.6166 | 121.9162 | 122.5021 | 121.875 | 105.8533
1874.4375 | 122.6669 | -122.0032 | 0.6134 | 0.010147 | -0.013089 | -0.079651 | -0.0033475 | -0.027025 | -0.051876 | -0.040178 | -0.0021057 | -0.017118 | 0.057482 | 0.051603 | -0.21894 | -0.015137 | -0.02368 | -0.11902 | 0.1236 | -0.15106 | -0.14191 | -0.018311 | -0.15106 | -0.07782 | -16.3879 | 0.60425 | -122.0718 | 0.45319 | -121.5637 | -121.8521 | -121.4676 | 121.8521 | -0.48981 | -0.75531 | 121.9849 | 121.9254 | 121.8521 | 0.073242 | 0 | -0.068664 | -0.009155 | -0.16022 | 0.43945 | 0.53558 | 0.15106 | 0.60425 | 0.21973 | 0.13275 | 0.009155 | 0.50812 | 122.525 | 0.27466 | 122.6761 | 122.1268 | 122.6074 | -0.76447 | -122.6852 | 121.8613 | 122.4564 | 121.8842 | 105.6152
1876.1406 | 122.6212 | -122.0123 | 0.61798 | 0.010147 | -0.010525 | -0.079438 | -0.0029201 | -0.026171 | -0.052731 | -0.039751 | -0.0021057 | -0.020322 | 0.055986 | 0.047758 | -0.22022 | -0.013001 | -0.024107 | -0.10071 | 0.09613 | -0.1236 | -0.14648 | -0.022888 | -0.17395 | -0.10529 | -16.4108 | 0.59509 | -122.0673 | 0.43945 | -121.6141 | -121.9254 | -121.5042 | 121.8887 | -0.52185 | -0.76446 | 121.9894 | 121.907 | 121.8384 | 0.01831 | -0.050354 | -0.054932 | -0.022888 | -0.17853 | 0.39825 | 0.50812 | 0.086975 | 0.56305 | 0.14191 | 0.10071 | -0.022888 | 0.45319 | 122.5067 | 0.21973 | 122.6624 | 122.1085 | 122.6074 | -0.74158 | -122.6852 | 121.8658 | 122.4518 | 121.9116 | 105.6015
1877.9375 | 122.6532 | -122.0261 | 0.60425 | 0.0025177 | -0.015438 | -0.079224 | -0.0074063 | -0.029589 | -0.051449 | -0.039751 | -0.0051575 | -0.020108 | 0.056414 | 0.043058 | -0.21744 | -0.017273 | -0.024107 | -0.073242 | 0.082397 | -0.13275 | -0.082397 | 0.068665 | -0.073242 | -0.018311 | -16.452 | 0.58136 | -122.0535 | 0.44861 | -121.5683 | -121.8658 | -121.4905 | 121.8933 | -0.52185 | -0.68664 | 122.0947 | 122.0078 | 121.9528 | 0.11444 | 0.059509 | -0.027466 | -0.022888 | -0.15564 | 0.45776 | 0.53558 | 0.16022 | 0.56305 | 0.18768 | 0.20142 | 0.050354 | 0.48523 | 122.5021 | 0.21515 | 122.6349 | 122.1085 | 122.6074 | -0.737 | -122.6578 | 121.9437 | 122.4747 | 121.9528 | 105.574
1879.7188 | 122.6715 | -122.0444 | 0.60425 | -0.0051118 | -0.012234 | -0.076661 | -0.0050565 | -0.031725 | -0.052944 | -0.038469 | -0.0021057 | -0.02139 | 0.057695 | 0.046689 | -0.22086 | -0.015992 | -0.020476 | -0.1236 | 0.10071 | -0.12817 | -0.15106 | -0.004578 | -0.14648 | -0.064087 | -16.5207 | 0.61798 | -122.0856 | 0.44861 | -121.5775 | -121.8704 | -121.4676 | 121.9162 | -0.50354 | -0.75531 | 122.0398 | 121.9803 | 121.8979 | 0.064087 | -0.01831 | -0.041198 | 0.013733 | -0.15564 | 0.46692 | 0.57678 | 0.17395 | 0.61798 | 0.21515 | 0.1236 | -0.022888 | 0.50812 | 122.5342 | 0.22888 | 122.7036 | 122.1451 | 122.6624 | -0.73242 | -122.6898 | 121.8933 | 122.493 | 121.9208 | 105.5237
1881.5156 | 122.6395 | -122.0352 | 0.62256 | -0.012741 | -0.014798 | -0.078797 | -0.0044155 | -0.030871 | -0.051876 | -0.040178 | 0.00094606 | -0.019467 | 0.058763 | 0.048826 | -0.2183 | -0.01706 | -0.021971 | -0.13733 | 0.11444 | -0.1236 | -0.16479 | -0.013733 | -0.15106 | -0.073242 | -16.5939 | 0.60883 | -122.0764 | 0.42572 | -121.6141 | -121.9025 | -121.4951 | 121.9116 | -0.50812 | -0.78735 | 122.0215 | 121.962 | 121.8842 | 0.050354 | -0.027466 | -0.041199 | -0.013733 | -0.19684 | 0.42114 | 0.54016 | 0.13275 | 0.58136 | 0.17395 | 0.10986 | -0.041199 | 0.46234 | 122.5021 | 0.23804 | 122.6852 | 122.1497 | 122.644 | -0.74616 | -122.699 | 121.8704 | 122.4609 | 121.8979 | 105.4413
1883.2344 | 122.6303 | -122.0169 | 0.60883 | 0.010147 | -0.0096707 | -0.079651 | -0.0039883 | -0.02553 | -0.048458 | -0.041033 | 0.00094606 | -0.017758 | 0.057909 | 0.048612 | -0.21915 | -0.013428 | -0.025816 | -0.07782 | 0.07782 | -0.13275 | -0.11444 | 0.018311 | -0.15106 | -0.09613 | -16.6077 | 0.60883 | -122.0718 | 0.45319 | -121.6187 | -121.9162 | -121.4951 | 121.8842 | -0.53101 | -0.72327 | 122.0352 | 121.9208 | 121.8658 | 0.036621 | -0.018311 | -0.054931 | 0 | -0.15564 | 0.39826 | 0.52185 | 0.10071 | 0.57678 | 0.15564 | 0.15106 | 0.01831 | 0.45319 | 122.525 | 0.21057 | 122.6807 | 122.0947 | 122.6257 | -0.74158 | -122.6807 | 121.9025 | 122.4701 | 121.9391 | 105.4092
1885.0156 | 122.7768 | -121.9849 | 0.59052 | -0.0051118 | -0.01138 | -0.077942 | -0.0063381 | -0.025957 | -0.048458 | -0.041887 | -0.0021057 | -0.023313 | 0.055559 | 0.038358 | -0.21937 | -0.016205 | -0.02603 | -0.041199 | 0.068665 | -0.091553 | -0.018311 | 0.13275 | -0.054932 | 0.032043 | -16.5802 | 0.55389 | -122.0261 | 0.56305 | -121.4859 | -121.7697 | -121.376 | 121.8933 | -0.52185 | -0.60883 | 122.1176 | 122.0169 | 121.9299 | 0.1236 | 0.036621 | -0.041199 | -0.036621 | -0.027466 | 0.49896 | 0.60883 | 0.21515 | 0.65002 | 0.25635 | 0.2243 | 0.073242 | 0.54016 | 122.5891 | 0.16022 | 122.58 | 122.0535 | 122.5388 | -0.68207 | -122.6166 | 121.9666 | 122.5479 | 121.9437 | 105.4047
1886.7969 | 122.7539 | -122.0123 | 0.58594 | 0.0025177 | -0.012661 | -0.079438 | -0.0046291 | -0.029589 | -0.051022 | -0.041033 | -0.0021057 | -0.019467 | 0.057482 | 0.04733 | -0.21894 | -0.015137 | -0.024748 | -0.1236 | 0.09613 | -0.13275 | -0.13275 | 0.004578 | -0.15564 | -0.073242 | -16.6809 | 0.60425 | -122.0901 | 0.52185 | -121.5546 | -121.8613 | -121.4264 | 121.8796 | -0.48981 | -0.71869 | 122.0169 | 121.9391 | 121.8567 | 0.059509 | -0.022889 | -0.07782 | 0.018311 | -0.064086 | 0.45776 | 0.58594 | 0.15106 | 0.66376 | 0.22888 | 0.13733 | 0 | 0.53558 | 122.612 | 0.22888 | 122.6944 | 122.1085 | 122.6166 | -0.71869 | -122.6761 | 121.8796 | 122.5342 | 121.8887 | 105.3314
1888.5156 | 122.6212 | -122.0398 | 0.59509 | 0.010147 | -0.011166 | -0.078797 | -0.0033475 | -0.029162 | -0.049954 | -0.041033 | 0.00094606 | -0.020322 | 0.056841 | 0.044767 | -0.21872 | -0.014283 | -0.023894 | -0.11444 | 0.10071 | -0.1236 | -0.15564 | -0.045776 | -0.1831 | -0.10529 | -16.777 | 0.60883 | -122.0993 | 0.41657 | -121.6461 | -121.9574 | -121.5042 | 121.9162 | -0.49438 | -0.75073 | 121.994 | 121.9345 | 121.8567 | 0.01831 | -0.059509 | -0.059509 | 0.013733 | -0.17853 | 0.39368 | 0.53558 | 0.082398 | 0.59509 | 0.14191 | 0.07782 | -0.032044 | 0.45319 | 122.5159 | 0.2243 | 122.7081 | 122.1405 | 122.6486 | -0.71869 | -122.6944 | 121.8842 | 122.4564 | 121.9254 | 105.2628
1890.2812 | 122.7264 | -122.0032 | 0.56305 | -0.012741 | -0.012661 | -0.079438 | -0.0078335 | -0.028948 | -0.048672 | -0.042528 | 0.00094606 | -0.020536 | 0.057695 | 0.042631 | -0.21702 | -0.015351 | -0.023253 | -0.09613 | 0.064087 | -0.082397 | -0.091553 | 0.059509 | -0.082397 | -0.009155 | -16.832 | 0.56763 | -122.0764 | 0.50354 | -121.5637 | -121.8521 | -121.4493 | 121.9208 | -0.49896 | -0.6546 | 122.0627 | 121.994 | 121.9208 | 0.073242 | 0 | -0.073242 | 0.004578 | -0.059509 | 0.43945 | 0.55389 | 0.15106 | 0.62714 | 0.2243 | 0.14191 | -0.009156 | 0.51269 | 122.58 | 0.14648 | 122.644 | 122.0673 | 122.5708 | -0.64545 | -122.6395 | 121.9116 | 122.5067 | 121.907 | 105.1712
1892.0781 | 122.6852 | -122.0444 | 0.58594 | -0.0051118 | -0.011807 | -0.078156 | -0.0042019 | -0.034716 | -0.049099 | -0.040392 | 0.00094606 | -0.019467 | 0.058763 | 0.042203 | -0.21766 | -0.015565 | -0.021971 | -0.073242 | 0.07782 | -0.12817 | -0.091553 | 0.073242 | -0.10529 | -0.036621 | -16.8457 | 0.58136 | -122.0764 | 0.48523 | -121.5866 | -121.907 | -121.4767 | 121.9162 | -0.50812 | -0.67749 | 122.1176 | 122.0078 | 121.9391 | 0.091553 | 0.022888 | -0.032043 | -0.004577 | -0.10071 | 0.45776 | 0.56763 | 0.13733 | 0.59967 | 0.16937 | 0.20142 | 0.036621 | 0.48981 | 122.5616 | 0.20599 | 122.6578 | 122.1222 | 122.6257 | -0.71411 | -122.6624 | 121.9528 | 122.5296 | 121.9711 | 105.1987
1893.8594 | 122.6257 | -122.0215 | 0.62256 | -0.0051118 | -0.0088163 | -0.080292 | -0.0033475 | -0.028093 | -0.050808 | -0.04146 | 0.00094606 | -0.020108 | 0.0609 | 0.049467 | -0.22043 | -0.015778 | -0.021544 | -0.10071 | 0.10529 | -0.1236 | -0.14191 | 0 | -0.16479 | -0.091553 | -17.0975 | 0.62256 | -122.0856 | 0.43488 | -121.6461 | -121.962 | -121.5225 | 121.8979 | -0.51727 | -0.76447 | 122.0215 | 121.9299 | 121.8567 | 0.032043 | -0.041199 | -0.064087 | 0 | -0.18768 | 0.37537 | 0.49896 | 0.059509 | 0.56305 | 0.1236 | 0.1236 | -0.018311 | 0.43945 | 122.5204 | 0.22888 | 122.7081 | 122.1268 | 122.644 | -0.74616 | -122.7081 | 121.8796 | 122.4564 | 121.9208 | 104.924
1895.5938 | 122.6486 | -122.0306 | 0.61798 | 0.0025177 | -0.011593 | -0.080079 | -0.0035611 | -0.03023 | -0.04974 | -0.04381 | 0.00094606 | -0.018827 | 0.057482 | 0.041776 | -0.21872 | -0.016205 | -0.023894 | -0.14648 | 0.11444 | -0.11444 | -0.15106 | -0.050354 | -0.20142 | -0.10071 | -17.2028 | 0.6134 | -122.0718 | 0.44861 | -121.637 | -121.9482 | -121.4996 | 121.9162 | -0.50354 | -0.76904 | 121.9803 | 121.9299 | 121.8292 | 0.013733 | -0.086975 | -0.041198 | -0.004578 | -0.16937 | 0.39368 | 0.53101 | 0.082398 | 0.5722 | 0.1236 | 0.064087 | -0.036621 | 0.43488 | 122.5204 | 0.22888 | 122.6852 | 122.1451 | 122.644 | -0.73242 | -122.6898 | 121.8796 | 122.4792 | 121.8842 | 104.8279
1897.375 | 122.6532 | -122.0581 | 0.6134 | 0.010147 | -0.01437 | -0.081574 | -0.0059109 | -0.034929 | -0.048672 | -0.040178 | -0.0021057 | -0.021604 | 0.058336 | 0.04733 | -0.21958 | -0.014283 | -0.023253 | -0.15106 | 0.10071 | -0.14648 | -0.15106 | 0 | -0.13275 | -0.068665 | -17.2165 | 0.61798 | -122.0901 | 0.41657 | -121.6187 | -121.9162 | -121.5363 | 121.9116 | -0.5127 | -0.76447 | 122.0581 | 121.9894 | 121.9254 | 0.077819 | 0.013733 | -0.032044 | 0.004578 | -0.19684 | 0.43945 | 0.52185 | 0.14191 | 0.55389 | 0.17395 | 0.14648 | -0.004578 | 0.4715 | 122.5067 | 0.24719 | 122.7081 | 122.1588 | 122.6761 | -0.75989 | -122.7036 | 121.907 | 122.4747 | 121.907 | 104.8416
1899.1406 | 122.6578 | -122.2504 | 0.40741 | -0.0051118 | -0.015438 | -0.079865 | -0.0061245 | -0.032152 | -0.051235 | -0.04146 | -0.0051575 | -0.019895 | 0.056841 | 0.050321 | -0.22129 | -0.015778 | -0.021544 | -0.14191 | 0.11444 | -0.14191 | -0.15564 | -0.013733 | -0.14191 | -0.073242 | -17.3447 | 0.39825 | -122.2824 | 0.22888 | -121.8155 | -122.1085 | -121.7102 | 122.1085 | -0.29297 | -0.56305 | 122.2366 | 122.1771 | 122.1085 | 0.068665 | 0 | -0.032044 | -0.009156 | -0.17853 | 0.43488 | 0.54016 | 0.14191 | 0.5722 | 0.17395 | 0.12817 | -0.013733 | 0.46692 | 122.5113 | 0.25635 | 122.6807 | 122.3648 | 122.6486 | -0.54932 | -122.6898 | 122.0947 | 122.4792 | 122.1085 | 104.9057
1900.9375 | 122.6578 | -122.2595 | 0.41657 | -0.0051118 | -0.014157 | -0.080506 | -0.0071927 | -0.033007 | -0.052731 | -0.042955 | -0.0021057 | -0.022885 | 0.056414 | 0.043272 | -0.22022 | -0.016846 | -0.025389 | -0.13733 | 0.11444 | -0.13275 | -0.16937 | -0.009155 | -0.15106 | -0.050354 | -17.4728 | 0.39825 | -122.319 | 0.20599 | -121.8292 | -122.1359 | -121.7102 | 122.1268 | -0.30212 | -0.58594 | 122.2504 | 122.2092 | 122.1085 | 0.082397 | -0.018311 | -0.05951 | -0.018311 | -0.21057 | 0.4303 | 0.54932 | 0.1236 | 0.60883 | 0.18311 | 0.1236 | -0.036622 | 0.48981 | 122.525 | 0.24719 | 122.7173 | 122.374 | 122.6578 | -0.54932 | -122.7356 | 122.0901 | 122.4655 | 122.1222 | 104.7867
1902.75 | 122.7997 | -122.2 | 0.36621 | -0.0051118 | -0.014798 | -0.078797 | -0.0078335 | -0.035784 | -0.050595 | -0.041674 | -0.0021057 | -0.020536 | 0.05385 | 0.045194 | -0.21979 | -0.015565 | -0.024321 | -0.050354 | 0.07782 | -0.07782 | -0.009155 | 0.1831 | 0.009155 | 0.068665 | -17.4042 | 0.37537 | -122.2321 | 0.3479 | -121.6599 | -121.962 | -121.5866 | 122.1222 | -0.28839 | -0.37537 | 122.3831 | 122.2687 | 122.2092 | 0.14649 | 0.086975 | -0.032044 | 0.009155 | -0.018311 | 0.54016 | 0.6134 | 0.23804 | 0.64545 | 0.27008 | 0.26092 | 0.068665 | 0.5722 | 122.58 | 0.15564 | 122.6074 | 122.2778 | 122.5754 | -0.44403 | -122.5983 | 122.1909 | 122.5479 | 122.1497 | 104.7958
1904.4688 | 122.7722 | -122.1176 | 0.46692 | -0.0051118 | -0.010739 | -0.076661 | -0.0033475 | -0.026171 | -0.050595 | -0.041033 | 0.00094606 | -0.020536 | 0.058977 | 0.055234 | -0.22129 | -0.014496 | -0.023039 | -0.086975 | 0.09613 | -0.11444 | -0.050354 | 0.073242 | -0.082397 | -0.004578 | -17.5095 | 0.46692 | -122.1725 | 0.44403 | -121.637 | -121.9345 | -121.4996 | 122.0032 | -0.37079 | -0.51727 | 122.1909 | 122.113 | 122.0352 | 0.10986 | 0.032044 | -0.054931 | 0 | -0.022888 | 0.48065 | 0.61798 | 0.18311 | 0.67291 | 0.23804 | 0.18768 | 0.064087 | 0.53558 | 122.6166 | 0.21057 | 122.6395 | 122.2137 | 122.5845 | -0.58136 | -122.6395 | 122.0673 | 122.5616 | 122.0306 | 104.6082
1906.2344 | 122.6852 | -122.2733 | 0.39825 | 0.0025177 | -0.011807 | -0.077302 | -0.0016385 | -0.030657 | -0.051876 | -0.038042 | 0.0039979 | -0.019254 | 0.058977 | 0.04434 | -0.22001 | -0.013215 | -0.021117 | -0.068665 | 0.11444 | -0.11444 | -0.10071 | 0.054932 | -0.11444 | -0.041199 | -17.5735 | 0.38452 | -122.3328 | 0.27008 | -121.8338 | -122.1405 | -121.7148 | 122.1588 | -0.28381 | -0.49896 | 122.3282 | 122.2321 | 122.1588 | 0.073242 | 0 | -0.05951 | -0.013733 | -0.12817 | 0.43945 | 0.55847 | 0.13275 | 0.61798 | 0.19226 | 0.16937 | 0.013733 | 0.49896 | 122.6028 | 0.22888 | 122.7173 | 122.3877 | 122.6578 | -0.5127 | -122.731 | 122.1725 | 122.5433 | 122.2046 | 104.6997
1908.0469 | 122.7631 | -121.994 | 0.55389 | 0.0025177 | -0.011166 | -0.07837 | -0.0074063 | -0.033434 | -0.051663 | -0.040605 | -0.0051575 | -0.018613 | 0.055986 | 0.049253 | -0.21979 | -0.014924 | -0.028166 | -0.064087 | 0.064087 | -0.07782 | -0.022888 | 0.13733 | -0.059509 | 0.022888 | -17.5232 | 0.6134 | -122.0444 | 0.53558 | -121.55 | -121.8384 | -121.4447 | 121.9162 | -0.48981 | -0.57678 | 122.1313 | 122.0169 | 121.9345 | 0.10071 | 0.018311 | -0.050354 | 0.059509 | -0.018311 | 0.44403 | 0.54932 | 0.15564 | 0.59967 | 0.20599 | 0.21515 | 0.054932 | 0.49438 | 122.58 | 0.14191 | 122.6578 | 122.0581 | 122.6074 | -0.63171 | -122.5983 | 121.9711 | 122.5296 | 121.9299 | 104.4708
1909.7656 | 122.7219 | -122.2595 | 0.40283 | 0.0025177 | -0.012661 | -0.080506 | -0.0065517 | -0.03023 | -0.047817 | -0.040392 | -0.0021057 | -0.019681 | 0.059404 | 0.055662 | -0.21915 | -0.015778 | -0.021971 | -0.086975 | 0.10071 | -0.13275 | -0.11902 | 0.045776 | -0.10529 | -0.045776 | -17.6834 | 0.3891 | -122.3007 | 0.29297 | -121.7834 | -122.0947 | -121.6782 | 122.1268 | -0.30212 | -0.52185 | 122.3053 | 122.2137 | 122.1542 | 0.086975 | 0.027465 | -0.041199 | -0.013733 | -0.10986 | 0.47607 | 0.58136 | 0.16479 | 0.62256 | 0.20599 | 0.17853 | 0.013732 | 0.51727 | 122.5937 | 0.23346 | 122.6898 | 122.3602 | 122.6486 | -0.53558 | -122.7036 | 122.1405 | 122.5525 | 122.1725 | 104.5761
1911.5469 | 122.7448 | -122.2366 | 0.36621 | -0.0051118 | -0.013729 | -0.080292 | -0.0071927 | -0.028521 | -0.04974 | -0.040392 | 0.0039979 | -0.022672 | 0.057695 | 0.041349 | -0.21915 | -0.016419 | -0.020689 | -0.10529 | 0.082397 | -0.10986 | -0.10529 | 0.050354 | -0.082397 | -0.027466 | -17.8986 | 0.36621 | -122.287 | 0.27008 | -121.7651 | -122.0535 | -121.6644 | 122.1268 | -0.28381 | -0.4715 | 122.287 | 122.2092 | 122.1542 | 0.082397 | 0.027466 | -0.050354 | 0 | -0.09613 | 0.4715 | 0.5722 | 0.1831 | 0.62256 | 0.23346 | 0.16022 | 0.004577 | 0.52185 | 122.5571 | 0.19226 | 122.6532 | 122.319 | 122.6028 | -0.47607 | -122.6532 | 122.1313 | 122.5067 | 122.1313 | 104.3381
1913.3438 | 122.6578 | -122.2824 | 0.39825 | 0.010147 | -0.013729 | -0.080506 | -0.0084743 | -0.033007 | -0.051022 | -0.040819 | -0.0051575 | -0.022031 | 0.056841 | 0.043058 | -0.21808 | -0.015351 | -0.021758 | -0.14191 | 0.10986 | -0.1236 | -0.15564 | -0.013733 | -0.14191 | -0.054932 | -17.9169 | 0.37994 | -122.3053 | 0.20142 | -121.8338 | -122.1451 | -121.7514 | 122.1588 | -0.28839 | -0.55389 | 122.2687 | 122.2275 | 122.1405 | 0.068664 | -0.018311 | -0.022888 | -0.01831 | -0.19684 | 0.44861 | 0.53101 | 0.13733 | 0.55389 | 0.16022 | 0.10986 | -0.032044 | 0.4715 | 122.5067 | 0.23346 | 122.6852 | 122.3923 | 122.6624 | -0.52185 | -122.7036 | 122.1268 | 122.4838 | 122.1405 | 104.3655
1915.0469 | 122.7127 | -122.1451 | 0.50812 | 0.010147 | -0.01138 | -0.077729 | -0.0050565 | -0.029375 | -0.050381 | -0.041246 | -0.0021057 | -0.020108 | 0.057909 | 0.046903 | -0.21894 | -0.012787 | -0.029234 | -0.082397 | 0.10986 | -0.12817 | -0.09613 | 0.041199 | -0.10071 | -0.054932 | -17.8391 | 0.48981 | -122.1771 | 0.39368 | -121.669 | -122.0078 | -121.582 | 122.0169 | -0.39825 | -0.60425 | 122.1863 | 122.0901 | 122.0444 | 0.073242 | 0.027466 | -0.032043 | -0.018311 | -0.11444 | 0.47608 | 0.56305 | 0.13733 | 0.59509 | 0.16937 | 0.16937 | 0.032044 | 0.50812 | 122.5708 | 0.23804 | 122.6669 | 122.2549 | 122.6349 | -0.63629 | -122.6852 | 122.049 | 122.5388 | 122.0627 | 104.306
1916.8281 | 122.7676 | -121.9437 | 0.63171 | -0.012741 | -0.011593 | -0.079011 | -0.0063381 | -0.032793 | -0.048458 | -0.039324 | 0.00094606 | -0.020963 | 0.055773 | 0.041563 | -0.21894 | -0.016205 | -0.019835 | -0.064087 | 0.050354 | -0.082397 | -0.027466 | 0.13275 | -0.054932 | 0.013733 | -17.8619 | 0.61798 | -122.0123 | 0.62256 | -121.4859 | -121.7697 | -121.3577 | 121.8613 | -0.58136 | -0.65918 | 122.0764 | 121.9574 | 121.8887 | 0.09613 | 0.027465 | -0.068664 | -0.013733 | -0.009155 | 0.45776 | 0.58594 | 0.17395 | 0.6546 | 0.24262 | 0.21515 | 0.054931 | 0.52643 | 122.6349 | 0.13275 | 122.6303 | 121.994 | 122.5616 | -0.71411 | -122.644 | 121.9162 | 122.5662 | 121.8796 | 104.0817
1918.5625 | 122.6761 | -122.0627 | 0.60425 | -0.012741 | -0.010311 | -0.077942 | -0.0022793 | -0.026812 | -0.050381 | -0.040178 | -0.0021057 | -0.018613 | 0.058763 | 0.049253 | -0.21915 | -0.015351 | -0.022826 | -0.10529 | 0.082397 | -0.11902 | -0.14191 | -0.027466 | -0.17853 | -0.10986 | -18.1686 | 0.60883 | -122.1176 | 0.42572 | -121.6553 | -121.9803 | -121.5454 | 121.9437 | -0.52185 | -0.74616 | 122.0352 | 121.9528 | 121.8842 | 0.009156 | -0.059509 | -0.054932 | 0.004578 | -0.17853 | 0.40741 | 0.51727 | 0.082397 | 0.5722 | 0.13733 | 0.091553 | -0.022888 | 0.46234 | 122.5433 | 0.20142 | 122.7264 | 122.1451 | 122.6715 | -0.72327 | -122.7219 | 121.9208 | 122.4884 | 121.9574 | 103.894
1920.3438 | 122.6807 | -122.0627 | 0.62714 | 0.0025177 | -0.012875 | -0.080933 | -0.0044155 | -0.028093 | -0.048886 | -0.038683 | -0.0051575 | -0.01904 | 0.058336 | 0.042203 | -0.21979 | -0.015137 | -0.026885 | -0.091553 | 0.086975 | -0.10529 | -0.11444 | 0.018311 | -0.13275 | -0.064087 | -18.1412 | 0.60883 | -122.1085 | 0.48065 | -121.5866 | -121.9299 | -121.5088 | 121.9574 | -0.54016 | -0.74158 | 122.081 | 121.9986 | 121.9299 | 0.041199 | -0.027465 | -0.045776 | -0.01831 | -0.14648 | 0.47607 | 0.55389 | 0.13275 | 0.59967 | 0.17853 | 0.1236 | -0.009155 | 0.52185 | 122.5891 | 0.19226 | 122.7173 | 122.1497 | 122.6715 | -0.73242 | -122.7356 | 121.9482 | 122.5433 | 121.9711 | 103.9215
1922.1406 | 122.8134 | -122.2412 | 0.36621 | -0.0051118 | -0.01138 | -0.078156 | -0.0065517 | -0.03258 | -0.051022 | -0.040178 | 0.00094606 | -0.022031 | 0.061327 | 0.04968 | -0.21915 | -0.018555 | -0.021544 | -0.032043 | 0.059509 | -0.09613 | -0.032043 | 0.10986 | -0.041199 | 0.022888 | -18.1412 | 0.35248 | -122.2961 | 0.36621 | -121.7102 | -122.0261 | -121.6095 | 122.1451 | -0.3067 | -0.39825 | 122.3511 | 122.2641 | 122.2 | 0.11902 | 0.054931 | -0.054932 | -0.013733 | 0 | 0.53101 | 0.63171 | 0.21515 | 0.68665 | 0.27008 | 0.20599 | 0.064087 | 0.58594 | 122.6624 | 0.15564 | 122.6486 | 122.3007 | 122.5937 | -0.46234 | -122.6624 | 122.2092 | 122.6074 | 122.2092 | 104.1
1923.8594 | 122.6715 | -122.2229 | 0.43945 | -0.012741 | -0.010952 | -0.079011 | -0.0044155 | -0.028093 | -0.049313 | -0.042314 | -0.0021057 | -0.017758 | 0.056841 | 0.046689 | -0.21766 | -0.015137 | -0.023467 | -0.091553 | 0.11902 | -0.10986 | -0.11902 | 0.009155 | -0.16022 | -0.068665 | -18.3426 | 0.4303 | -122.2961 | 0.2655 | -121.8155 | -122.1359 | -121.7102 | 122.113 | -0.32043 | -0.55847 | 122.2321 | 122.1542 | 122.0627 | 0.041198 | -0.050354 | -0.073243 | -0.009155 | -0.17395 | 0.40741 | 0.51269 | 0.086975 | 0.58594 | 0.16022 | 0.11902 | -0.009156 | 0.48065 | 122.5616 | 0.22888 | 122.7264 | 122.3419 | 122.6532 | -0.54932 | -122.7356 | 122.1039 | 122.4884 | 122.1313 | 103.8803
1925.6562 | 122.7493 | -121.9437 | 0.66834 | -0.0051118 | -0.012875 | -0.080292 | -0.0071927 | -0.026598 | -0.048245 | -0.040819 | 0.0039979 | -0.022031 | 0.055986 | 0.040067 | -0.2183 | -0.015565 | -0.022612 | -0.059509 | 0.054932 | -0.10071 | -0.045776 | 0.14191 | -0.045776 | 0.013733 | -18.2785 | 0.65002 | -121.9711 | 0.62714 | -121.4539 | -121.7468 | -121.3348 | 121.843 | -0.6134 | -0.71411 | 122.0856 | 121.9574 | 121.8979 | 0.11444 | 0.054932 | -0.027465 | -0.018311 | -0.041199 | 0.48981 | 0.60883 | 0.19684 | 0.63629 | 0.2243 | 0.24262 | 0.054932 | 0.51727 | 122.5983 | 0.15564 | 122.6212 | 121.9986 | 122.5937 | -0.76904 | -122.6395 | 121.8979 | 122.5708 | 121.8842 | 103.6652
1927.375 | 122.7539 | -122.2 | 0.4303 | 0.0025177 | -0.011807 | -0.079011 | -0.0071927 | -0.033007 | -0.049099 | -0.040605 | 0.00094606 | -0.021176 | 0.058763 | 0.051389 | -0.21808 | -0.015565 | -0.024107 | -0.10986 | 0.086975 | -0.10071 | -0.09613 | 0.059509 | -0.082397 | -0.013733 | -18.5577 | 0.41657 | -122.2641 | 0.34332 | -121.7148 | -122.0123 | -121.6187 | 122.0993 | -0.34332 | -0.52643 | 122.2595 | 122.1863 | 122.1176 | 0.086975 | 0.018311 | -0.064087 | -0.013733 | -0.086975 | 0.48523 | 0.58136 | 0.18768 | 0.64545 | 0.25177 | 0.16022 | 0.004578 | 0.54932 | 122.6074 | 0.18768 | 122.6807 | 122.287 | 122.6166 | -0.53101 | -122.6944 | 122.1039 | 122.5433 | 122.0901 | 103.6423
1929.1406 | 122.7905 | -122.0581 | 0.56763 | -0.0051118 | -0.014157 | -0.081147 | -0.0084743 | -0.030871 | -0.05209 | -0.040605 | 0.00094606 | -0.023313 | 0.057482 | 0.046689 | -0.22043 | -0.015778 | -0.023467 | -0.050354 | 0.054932 | -0.091553 | -0.013733 | 0.14648 | -0.009155 | 0.045776 | -18.5211 | 0.54016 | -122.1085 | 0.52185 | -121.5042 | -121.8063 | -121.431 | 121.9666 | -0.5127 | -0.58136 | 122.2046 | 122.1039 | 122.0489 | 0.13733 | 0.082398 | -0.050354 | -0.027466 | -0.045776 | 0.55389 | 0.62714 | 0.25177 | 0.67749 | 0.30212 | 0.23804 | 0.07782 | 0.60425 | 122.6303 | 0.14649 | 122.6486 | 122.113 | 122.5983 | -0.65918 | -122.6761 | 122.0444 | 122.58 | 122.0078 | 103.537
1930.8594 | 122.7951 | -122.2916 | 0.33875 | 0.0025177 | -0.014157 | -0.080292 | -0.0056973 | -0.028948 | -0.050381 | -0.042528 | -0.0021057 | -0.023313 | 0.055986 | 0.036222 | -0.22001 | -0.01471 | -0.024748 | -0.09613 | 0.091553 | -0.09613 | -0.064087 | 0.086975 | -0.059509 | 0.022888 | -18.6996 | 0.32044 | -122.3511 | 0.30212 | -121.756 | -122.0398 | -121.6461 | 122.1954 | -0.24719 | -0.40283 | 122.3785 | 122.3145 | 122.2321 | 0.11902 | 0.036621 | -0.059509 | -0.01831 | -0.036621 | 0.53558 | 0.64545 | 0.25177 | 0.70496 | 0.31128 | 0.1831 | 0.032043 | 0.59509 | 122.6532 | 0.18768 | 122.6715 | 122.3831 | 122.612 | -0.43488 | -122.6898 | 122.2275 | 122.5937 | 122.1954 | 103.5919
1932.6562 | 122.7402 | -122.0261 | 0.64087 | -0.0051118 | -0.011807 | -0.079438 | -0.0044155 | -0.02553 | -0.052731 | -0.039324 | -0.0051575 | -0.018827 | 0.057909 | 0.050107 | -0.22107 | -0.015137 | -0.024107 | -0.068665 | 0.09613 | -0.11902 | -0.10529 | 0.036621 | -0.10071 | -0.050354 | -18.7546 | 0.6546 | -122.0627 | 0.50812 | -121.5591 | -121.8567 | -121.4493 | 121.907 | -0.54474 | -0.74616 | 122.0627 | 121.9757 | 121.9254 | 0.068665 | 0.018311 | -0.036621 | 0.013733 | -0.13275 | 0.46692 | 0.57678 | 0.16937 | 0.6134 | 0.20599 | 0.15564 | 0.013733 | 0.50354 | 122.5708 | 0.21515 | 122.7173 | 122.1222 | 122.6807 | -0.75989 | -122.7036 | 121.9208 | 122.5342 | 121.9574 | 103.2715
1934.4531 | 122.8088 | -122.2366 | 0.36621 | -0.0051118 | -0.018216 | -0.079651 | -0.0078335 | -0.031511 | -0.04974 | -0.042528 | -0.0021057 | -0.022885 | 0.056414 | 0.045621 | -0.21808 | -0.017273 | -0.020689 | -0.082397 | 0.086975 | -0.091553 | -0.045776 | 0.086975 | -0.050354 | 0.032043 | -18.8919 | 0.33417 | -122.3282 | 0.33875 | -121.7056 | -122.0169 | -121.6324 | 122.1451 | -0.27924 | -0.41199 | 122.3236 | 122.2687 | 122.1863 | 0.1236 | 0.041199 | -0.091553 | -0.032044 | -0.027466 | 0.53101 | 0.60425 | 0.21973 | 0.6958 | 0.31128 | 0.17853 | 0.045777 | 0.62256 | 122.6669 | 0.17853 | 122.6624 | 122.3236 | 122.5708 | -0.45776 | -122.6944 | 122.1909 | 122.5754 | 122.1542 | 103.3447
1936.2344 | 122.6852 | -122.2549 | 0.45319 | -0.0051118 | -0.014584 | -0.079224 | -0.0065517 | -0.033007 | -0.051022 | -0.038896 | 0.00094606 | -0.018186 | 0.060045 | 0.048185 | -0.21937 | -0.015137 | -0.022826 | -0.1236 | 0.10071 | -0.13275 | -0.15106 | 0 | -0.14648 | -0.068665 | -19.0338 | 0.43945 | -122.287 | 0.26093 | -121.7972 | -122.1085 | -121.701 | 122.1222 | -0.35248 | -0.60425 | 122.2549 | 122.1863 | 122.1085 | 0.064086 | -0.013733 | -0.032043 | -0.013733 | -0.19226 | 0.45776 | 0.55389 | 0.14648 | 0.58594 | 0.17853 | 0.13275 | -0.018311 | 0.48981 | 122.5479 | 0.23346 | 122.7264 | 122.3557 | 122.6944 | -0.58594 | -122.7402 | 122.1039 | 122.5159 | 122.1313 | 103.2211
1938.0312 | 122.7448 | -122.1497 | 0.49439 | -0.0051118 | -0.010098 | -0.079224 | -0.0052701 | -0.030016 | -0.051022 | -0.039751 | -0.0021057 | -0.018827 | 0.055345 | 0.047758 | -0.22236 | -0.015137 | -0.02368 | -0.07782 | 0.09613 | -0.1236 | -0.082397 | 0.059509 | -0.10071 | -0.036621 | -18.9651 | 0.49439 | -122.2 | 0.41199 | -121.6736 | -122.0032 | -121.5912 | 122.0261 | -0.39826 | -0.57678 | 122.2092 | 122.113 | 122.049 | 0.086975 | 0.022888 | -0.050354 | 0 | -0.082398 | 0.47607 | 0.55847 | 0.14648 | 0.60882 | 0.19684 | 0.1831 | 0.041199 | 0.52643 | 122.612 | 0.21973 | 122.6944 | 122.2458 | 122.644 | -0.61798 | -122.6944 | 122.0673 | 122.5616 | 122.0718 | 103.1845
1939.75 | 122.6944 | -122.0856 | 0.59052 | -0.0051118 | -0.013943 | -0.079224 | -0.0042019 | -0.030657 | -0.04974 | -0.038896 | 0.00094606 | -0.019681 | 0.058977 | 0.045835 | -0.22022 | -0.015778 | -0.020903 | -0.13733 | 0.10529 | -0.14648 | -0.16937 | -0.022888 | -0.14648 | -0.073242 | -19.0887 | 0.58136 | -122.1497 | 0.42114 | -121.6415 | -121.9528 | -121.5454 | 121.9391 | -0.48523 | -0.75989 | 122.0627 | 122.0123 | 121.9391 | 0.073242 | 0 | -0.064087 | -0.009155 | -0.16937 | 0.44403 | 0.54016 | 0.13275 | 0.60425 | 0.19684 | 0.1236 | -0.022889 | 0.50812 | 122.5708 | 0.25177 | 122.731 | 122.1909 | 122.6669 | -0.737 | -122.7402 | 121.9162 | 122.5067 | 121.9482 | 102.9968
1941.5312 | 122.818 | -122.1313 | 0.50354 | 0.0025177 | -0.014157 | -0.082001 | -0.0074063 | -0.033434 | -0.049313 | -0.040605 | -0.0021057 | -0.022885 | 0.0562 | 0.038145 | -0.21744 | -0.01471 | -0.022826 | -0.050354 | 0.082397 | -0.086975 | -0.009155 | 0.15106 | 0.009155 | 0.050354 | -18.9285 | 0.50812 | -122.1588 | 0.48981 | -121.5546 | -121.8613 | -121.5042 | 122.0444 | -0.42114 | -0.5127 | 122.2824 | 122.1817 | 122.1405 | 0.13733 | 0.09613 | -0.027465 | 0.004578 | -0.013733 | 0.57678 | 0.62714 | 0.27008 | 0.6546 | 0.29755 | 0.23804 | 0.07782 | 0.60425 | 122.6486 | 0.16937 | 122.6669 | 122.2137 | 122.6395 | -0.59052 | -122.6624 | 122.1222 | 122.6212 | 122.081 | 103.2028
1943.3125 | 122.8363 | -122.1222 | 0.47607 | 0.010147 | -0.014157 | -0.080079 | -0.0078335 | -0.033007 | -0.051235 | -0.040605 | -0.0021057 | -0.022245 | 0.053636 | 0.039854 | -0.21851 | -0.016633 | -0.026457 | -0.054932 | 0.054932 | -0.09613 | -0.013733 | 0.16937 | 0.013733 | 0.073242 | -19.0475 | 0.46234 | -122.1725 | 0.46692 | -121.5637 | -121.8796 | -121.5179 | 122.0261 | -0.42114 | -0.48981 | 122.2916 | 122.1954 | 122.1359 | 0.16937 | 0.10986 | -0.050354 | -0.013733 | -0.009155 | 0.55847 | 0.60425 | 0.24261 | 0.6546 | 0.29297 | 0.2655 | 0.082397 | 0.60882 | 122.6395 | 0.15106 | 122.6349 | 122.1771 | 122.5845 | -0.5722 | -122.6486 | 122.1085 | 122.5891 | 122.0673 | 103.0746
1945.0938 | 122.8043 | -122.168 | 0.42572 | 0.010147 | -0.013302 | -0.079438 | -0.0076199 | -0.034502 | -0.051876 | -0.042955 | 0.0039979 | -0.02139 | 0.057268 | 0.044553 | -0.22065 | -0.017273 | -0.021971 | -0.050354 | 0.054932 | -0.086975 | 0.004578 | 0.13733 | -0.009155 | 0.036621 | -19.1025 | 0.42572 | -122.2458 | 0.42114 | -121.6599 | -121.9391 | -121.5637 | 122.081 | -0.37079 | -0.42114 | 122.3053 | 122.2046 | 122.1588 | 0.1236 | 0.07782 | -0.07782 | 0 | -0.004577 | 0.50812 | 0.60425 | 0.22888 | 0.68207 | 0.3067 | 0.2243 | 0.091553 | 0.58594 | 122.6669 | 0.14191 | 122.6715 | 122.2229 | 122.5937 | -0.5127 | -122.6715 | 122.1725 | 122.5891 | 122.1176 | 103.0655
1946.875 | 122.7585 | -122.2137 | 0.42114 | -0.0051118 | -0.011166 | -0.080292 | -0.0061245 | -0.029589 | -0.051022 | -0.038896 | 0.0070497 | -0.021817 | 0.056841 | 0.04498 | -0.21894 | -0.015778 | -0.021971 | -0.086975 | 0.064087 | -0.086975 | -0.068665 | 0.059509 | -0.07782 | -0.018311 | -19.3451 | 0.41199 | -122.2458 | 0.33875 | -121.7468 | -122.049 | -121.6278 | 122.1268 | -0.35706 | -0.48981 | 122.2733 | 122.1954 | 122.1359 | 0.068664 | 0.009155 | -0.032044 | -0.009156 | -0.082398 | 0.46692 | 0.58594 | 0.16479 | 0.61798 | 0.19684 | 0.14648 | 0.01831 | 0.49896 | 122.5845 | 0.15106 | 122.6578 | 122.2778 | 122.6257 | -0.50812 | -122.6669 | 122.1451 | 122.5525 | 122.1268 | 102.8687
1948.6094 | 122.7036 | -122.2046 | 0.48065 | 0.0025177 | -0.013302 | -0.082215 | -0.0071927 | -0.031725 | -0.052304 | -0.039965 | -0.0021057 | -0.020749 | 0.056627 | 0.04968 | -0.21958 | -0.015565 | -0.022185 | -0.12817 | 0.10529 | -0.13275 | -0.14648 | -0.004578 | -0.15564 | -0.082397 | -19.4275 | 0.47607 | -122.2961 | 0.29755 | -121.7743 | -122.0673 | -121.6736 | 122.0718 | -0.37537 | -0.62714 | 122.2 | 122.1222 | 122.0489 | 0.050354 | -0.022889 | -0.091553 | -0.004578 | -0.18311 | 0.4303 | 0.53101 | 0.13733 | 0.62256 | 0.22888 | 0.12817 | -0.013733 | 0.52185 | 122.5937 | 0.23804 | 122.7722 | 122.3099 | 122.6807 | -0.6134 | -122.7768 | 122.0581 | 122.5021 | 122.0764 | 102.7771
1950.3906 | 122.7127 | -122.287 | 0.40283 | -0.02037 | -0.010098 | -0.07837 | -0.0048427 | -0.027239 | -0.051235 | -0.040178 | -0.0021057 | -0.017972 | 0.057482 | 0.048185 | -0.21808 | -0.014924 | -0.025389 | -0.068665 | 0.10529 | -0.12817 | -0.09613 | 0.027466 | -0.13275 | -0.073242 | -19.4275 | 0.39368 | -122.3511 | 0.25635 | -121.843 | -122.1725 | -121.7285 | 122.1588 | -0.29755 | -0.49896 | 122.3145 | 122.2137 | 122.1542 | 0.054932 | -0.004577 | -0.064087 | -0.009155 | -0.14648 | 0.44403 | 0.55847 | 0.11444 | 0.62256 | 0.17853 | 0.15564 | 0.032044 | 0.50812 | 122.6074 | 0.23346 | 122.7448 | 122.3923 | 122.6807 | -0.53101 | -122.7539 | 122.1909 | 122.5433 | 122.2183 | 102.8595
1952.1094 | 122.7814 | -122.2778 | 0.36163 | -0.0051118 | -0.015011 | -0.079438 | -0.0082607 | -0.032366 | -0.051022 | -0.042742 | -0.0051575 | -0.02139 | 0.055773 | 0.048185 | -0.2183 | -0.01471 | -0.021971 | -0.09613 | 0.07782 | -0.091553 | -0.086975 | 0.041199 | -0.082397 | -0.013733 | -19.5282 | 0.33875 | -122.3419 | 0.29297 | -121.7834 | -122.0856 | -121.6827 | 122.1863 | -0.28381 | -0.44861 | 122.319 | 122.2641 | 122.1954 | 0.07782 | 0.009156 | -0.064087 | -0.022888 | -0.068664 | 0.49439 | 0.59509 | 0.19226 | 0.65918 | 0.25635 | 0.13275 | 0.004578 | 0.55847 | 122.6349 | 0.16937 | 122.6807 | 122.3557 | 122.6166 | -0.45319 | -122.7036 | 122.1909 | 122.5708 | 122.1817 | 102.7496
1953.9062 | 122.8271 | -122.2641 | 0.34332 | 0.0025177 | -0.014798 | -0.079438 | -0.0067653 | -0.027666 | -0.04974 | -0.043169 | -0.0021057 | -0.022031 | 0.057268 | 0.047544 | -0.21872 | -0.015565 | -0.025389 | -0.054932 | 0.07782 | -0.086975 | -0.004578 | 0.15564 | 0 | 0.059509 | -19.4824 | 0.32501 | -122.3511 | 0.32044 | -121.7239 | -122.0306 | -121.6736 | 122.1771 | -0.2655 | -0.3479 | 122.4197 | 122.3236 | 122.2641 | 0.14648 | 0.086975 | -0.086975 | -0.018311 | -0.022888 | 0.54016 | 0.59051 | 0.23346 | 0.67749 | 0.32043 | 0.24261 | 0.082397 | 0.62714 | 122.6715 | 0.16479 | 122.6761 | 122.3419 | 122.5891 | -0.4303 | -122.6944 | 122.2595 | 122.5845 | 122.2092 | 102.7817
1955.7031 | 122.7127 | -122.3007 | 0.42114 | -0.012741 | -0.011166 | -0.079651 | -0.0050565 | -0.031511 | -0.050595 | -0.040392 | -0.0021057 | -0.017331 | 0.057909 | 0.042417 | -0.21979 | -0.014924 | -0.024107 | -0.068665 | 0.09613 | -0.11902 | -0.10071 | 0.032043 | -0.10986 | -0.064087 | -19.5374 | 0.39825 | -122.3236 | 0.27008 | -121.8292 | -122.1725 | -121.7239 | 122.1817 | -0.32501 | -0.52185 | 122.3328 | 122.2366 | 122.1909 | 0.054932 | 0.009156 | -0.022888 | -0.022889 | -0.15106 | 0.4715 | 0.57678 | 0.12817 | 0.59967 | 0.15106 | 0.15106 | 0.018311 | 0.49438 | 122.5937 | 0.21515 | 122.7219 | 122.3969 | 122.699 | -0.54016 | -122.7448 | 122.2 | 122.5708 | 122.2321 | 102.7634
1957.4844 | 122.7997 | -122.1817 | 0.44403 | 0.0025177 | -0.015866 | -0.07837 | -0.0084743 | -0.035784 | -0.052304 | -0.04146 | -0.0021057 | -0.020108 | 0.055345 | 0.041776 | -0.21894 | -0.018342 | -0.020476 | -0.09613 | 0.073242 | -0.11902 | -0.073242 | 0.073242 | -0.073242 | 0.004578 | -19.606 | 0.44403 | -122.2961 | 0.38452 | -121.6782 | -121.9894 | -121.6003 | 122.0627 | -0.37079 | -0.51727 | 122.2549 | 122.1863 | 122.1085 | 0.1236 | 0.045777 | -0.11444 | 0 | -0.05951 | 0.50354 | 0.58136 | 0.19226 | 0.6958 | 0.3067 | 0.19226 | 0.045777 | 0.61798 | 122.6807 | 0.19226 | 122.7402 | 122.2549 | 122.6257 | -0.56305 | -122.7402 | 122.1085 | 122.5662 | 122.0856 | 102.5757
1959.2031 | 122.6852 | -122.2183 | 0.46234 | 0.0025177 | -0.010098 | -0.079224 | -0.0048427 | -0.028521 | -0.049313 | -0.038683 | 0.00094606 | -0.018613 | 0.057482 | 0.051176 | -0.21808 | -0.013856 | -0.025389 | -0.13275 | 0.11902 | -0.12817 | -0.14191 | -0.041199 | -0.19684 | -0.11902 | -19.8212 | 0.43945 | -122.2961 | 0.2655 | -121.8475 | -122.1771 | -121.7285 | 122.0901 | -0.34332 | -0.60425 | 122.1771 | 122.0993 | 122.0215 | 0.009155 | -0.068664 | -0.07782 | -0.022888 | -0.19684 | 0.37079 | 0.48981 | 0.041199 | 0.56763 | 0.11902 | 0.086975 | -0.013733 | 0.44861 | 122.5616 | 0.24719 | 122.7356 | 122.3373 | 122.6578 | -0.59052 | -122.7585 | 122.0764 | 122.4838 | 122.0856 | 102.3972
1961 | 122.8134 | -122.0581 | 0.54016 | -0.012741 | -0.0090299 | -0.078156 | -0.0042019 | -0.031939 | -0.050595 | -0.040605 | -0.0021057 | -0.01904 | 0.057695 | 0.048185 | -0.21808 | -0.015565 | -0.022398 | -0.073242 | 0.082397 | -0.10529 | -0.054932 | 0.068665 | -0.09613 | -0.009155 | -19.725 | 0.54474 | -122.1451 | 0.54016 | -121.5683 | -121.8933 | -121.4447 | 121.9528 | -0.45776 | -0.59509 | 122.1268 | 122.0489 | 121.962 | 0.096131 | 0.009156 | -0.086976 | 0.004578 | 0 | 0.48981 | 0.6134 | 0.16479 | 0.70038 | 0.25177 | 0.17395 | 0.050354 | 0.57678 | 122.6852 | 0.18768 | 122.6898 | 122.1405 | 122.6028 | -0.64545 | -122.6852 | 122.0032 | 122.5983 | 121.9849 | 102.3331
1962.7344 | 122.8317 | -121.9986 | 0.60425 | -0.0051118 | -0.0092435 | -0.079438 | -0.0046291 | -0.030657 | -0.050167 | -0.042101 | 0.00094606 | -0.022245 | 0.057909 | 0.044126 | -0.21958 | -0.014069 | -0.023894 | -0.041199 | 0.068665 | -0.086975 | -0.022888 | 0.13275 | -0.054932 | 0.032043 | -19.7296 | 0.60425 | -122.0718 | 0.62256 | -121.4859 | -121.7972 | -121.3898 | 121.9116 | -0.53558 | -0.62714 | 122.1313 | 122.0306 | 121.9437 | 0.11902 | 0.032043 | -0.073242 | 0 | 0.018311 | 0.5127 | 0.60883 | 0.20142 | 0.68207 | 0.27466 | 0.21973 | 0.064087 | 0.58594 | 122.6944 | 0.15564 | 122.6761 | 122.0673 | 122.6028 | -0.69122 | -122.6761 | 121.9757 | 122.6212 | 121.9574 | 102.269
1964.5312 | 122.7997 | -122.0718 | 0.56763 | -0.012741 | -0.012661 | -0.077942 | -0.0067653 | -0.031298 | -0.048886 | -0.04146 | 0.00094606 | -0.020749 | 0.0562 | 0.042417 | -0.21744 | -0.015351 | -0.021758 | -0.10529 | 0.064087 | -0.082397 | -0.068665 | 0.086975 | -0.091553 | 0 | -19.8898 | 0.57678 | -122.1313 | 0.5127 | -121.5729 | -121.8704 | -121.4813 | 121.9894 | -0.50354 | -0.63629 | 122.1588 | 122.0718 | 121.9803 | 0.082397 | -0.009156 | -0.05951 | 0.009155 | -0.054932 | 0.49896 | 0.59051 | 0.20142 | 0.65002 | 0.26093 | 0.16937 | 0.013732 | 0.55847 | 122.644 | 0.14648 | 122.7081 | 122.1359 | 122.6486 | -0.65002 | -122.699 | 122.0032 | 122.5845 | 121.9666 | 102.182
1966.25 | 122.7539 | -122.0764 | 0.6134 | -0.0051118 | -0.013729 | -0.077302 | -0.0014249 | -0.031084 | -0.050167 | -0.042101 | -0.0051575 | -0.019467 | 0.057909 | 0.050107 | -0.21915 | -0.015565 | -0.024321 | -0.068665 | 0.10529 | -0.12817 | -0.10071 | 0.054932 | -0.10071 | -0.045776 | -19.8669 | 0.60425 | -122.1222 | 0.50354 | -121.5912 | -121.9116 | -121.4905 | 121.9482 | -0.50812 | -0.71411 | 122.1313 | 122.0306 | 121.9757 | 0.082398 | 0.027466 | -0.045776 | -0.009155 | -0.10986 | 0.48523 | 0.58594 | 0.16479 | 0.63171 | 0.21057 | 0.18311 | 0.027466 | 0.531 | 122.6257 | 0.23346 | 122.7264 | 122.1817 | 122.6807 | -0.74158 | -122.7356 | 121.9757 | 122.58 | 122.0078 | 102.2095
1968.0469 | 122.7448 | -122.168 | 0.52643 | 0.010147 | -0.015652 | -0.080719 | -0.0054837 | -0.031298 | -0.051235 | -0.040605 | 0.00094606 | -0.017545 | 0.057482 | 0.050321 | -0.22086 | -0.014924 | -0.021544 | -0.11902 | 0.10986 | -0.14191 | -0.16479 | -0.027466 | -0.12817 | -0.059509 | -20.0775 | 0.54474 | -122.2092 | 0.37994 | -121.6919 | -121.9894 | -121.5958 | 122.0261 | -0.41657 | -0.69122 | 122.1405 | 122.1085 | 122.0398 | 0.082398 | 0.013733 | -0.041198 | 0.018311 | -0.14648 | 0.47607 | 0.5722 | 0.17853 | 0.6134 | 0.21973 | 0.11444 | -0.022888 | 0.51727 | 122.5891 | 0.25177 | 122.7539 | 122.2778 | 122.7127 | -0.66834 | -122.7356 | 122.0032 | 122.5479 | 122.049 | 102.0905
1969.8281 | 122.731 | -122.1497 | 0.53558 | -0.0051118 | -0.011166 | -0.078583 | -0.0039883 | -0.027239 | -0.048886 | -0.040605 | 0.00094606 | -0.020322 | 0.056414 | 0.046476 | -0.21958 | -0.01471 | -0.019408 | -0.10986 | 0.10071 | -0.10986 | -0.16479 | -0.036621 | -0.18768 | -0.082397 | -20.1691 | 0.53101 | -122.2412 | 0.39825 | -121.7285 | -122.0444 | -121.5912 | 122.0398 | -0.43488 | -0.70038 | 122.113 | 122.0673 | 121.962 | 0.027466 | -0.07782 | -0.091553 | -0.004577 | -0.13733 | 0.42114 | 0.55847 | 0.10529 | 0.65002 | 0.19684 | 0.073242 | -0.054932 | 0.5127 | 122.6395 | 0.21057 | 122.7722 | 122.2504 | 122.6807 | -0.64545 | -122.7768 | 121.9849 | 122.5479 | 122.0398 | 101.9806
1971.5625 | 122.7493 | -122.0581 | 0.66376 | -0.0051118 | -0.010311 | -0.080506 | -0.0056973 | -0.029375 | -0.05209 | -0.041674 | -0.0021057 | -0.02139 | 0.057482 | 0.048185 | -0.21851 | -0.016846 | -0.024962 | -0.10529 | 0.11902 | -0.13275 | -0.13733 | 0 | -0.12817 | -0.054932 | -20.1096 | 0.6546 | -122.113 | 0.53101 | -121.5546 | -121.875 | -121.463 | 121.9254 | -0.54474 | -0.80109 | 122.0581 | 122.0032 | 121.9299 | 0.077819 | 0.004577 | -0.054932 | -0.009155 | -0.13275 | 0.50354 | 0.59509 | 0.1831 | 0.65002 | 0.23804 | 0.13275 | -0.004578 | 0.55847 | 122.644 | 0.25177 | 122.7676 | 122.1771 | 122.7127 | -0.79651 | -122.7768 | 121.9208 | 122.5891 | 121.9528 | 101.9485
1973.3594 | 122.7676 | -122.0581 | 0.65002 | 0.0025177 | -0.0092435 | -0.078156 | -0.0054837 | -0.028521 | -0.051022 | -0.041674 | -0.0021057 | -0.01904 | 0.061754 | 0.048185 | -0.21979 | -0.016633 | -0.021117 | -0.07782 | 0.09613 | -0.11444 | -0.11444 | 0.041199 | -0.091553 | -0.050354 | -20.1645 | 0.64087 | -122.1176 | 0.53558 | -121.5637 | -121.8704 | -121.4676 | 121.9437 | -0.55389 | -0.76447 | 122.0993 | 122.0078 | 121.9666 | 0.064087 | 0.022888 | -0.05951 | -0.009155 | -0.11444 | 0.49438 | 0.59051 | 0.18768 | 0.65002 | 0.24719 | 0.15564 | 0 | 0.55389 | 122.6532 | 0.21057 | 122.7585 | 122.1542 | 122.699 | -0.76447 | -122.7676 | 121.9437 | 122.5937 | 121.9803 | 101.8936
1975.1562 | 122.731 | -122.0673 | 0.63171 | 0.010147 | -0.012448 | -0.078797 | -0.0065517 | -0.034289 | -0.050167 | -0.039537 | -0.0082091 | -0.018186 | 0.05855 | 0.053098 | -0.21744 | -0.014283 | -0.021758 | -0.13733 | 0.10986 | -0.14191 | -0.16479 | -0.009155 | -0.14648 | -0.082397 | -20.3018 | 0.64087 | -122.1405 | 0.4715 | -121.6049 | -121.9162 | -121.5317 | 121.9254 | -0.52185 | -0.79651 | 122.0581 | 121.9849 | 121.9208 | 0.05951 | -0.004577 | -0.073242 | 0.009155 | -0.16022 | 0.46234 | 0.53558 | 0.15106 | 0.60883 | 0.2243 | 0.13275 | -0.022888 | 0.53558 | 122.612 | 0.25177 | 122.7814 | 122.1771 | 122.7081 | -0.77362 | -122.7722 | 121.9025 | 122.5388 | 121.9299 | 101.7654
1976.9531 | 122.7539 | -122.0764 | 0.60883 | 0.010147 | -0.011807 | -0.079011 | -0.0037747 | -0.026384 | -0.051235 | -0.040392 | 0.00094606 | -0.018186 | 0.059618 | 0.045621 | -0.2183 | -0.016205 | -0.019835 | -0.07782 | 0.10529 | -0.11902 | -0.091553 | 0.054932 | -0.10071 | -0.050354 | -20.2972 | 0.63171 | -122.1405 | 0.51727 | -121.5729 | -121.8979 | -121.4767 | 121.9574 | -0.50354 | -0.70038 | 122.1313 | 122.0261 | 121.9757 | 0.068665 | 0.018311 | -0.064087 | 0.022888 | -0.091553 | 0.50354 | 0.59967 | 0.17853 | 0.66376 | 0.24262 | 0.17395 | 0.027466 | 0.56763 | 122.6578 | 0.22431 | 122.7722 | 122.1817 | 122.7081 | -0.72784 | -122.7493 | 121.9849 | 122.5937 | 121.9986 | 101.7792
1978.6875 | 122.8455 | -122.0535 | 0.58594 | -0.0051118 | -0.01437 | -0.080719 | -0.0086879 | -0.031298 | -0.050381 | -0.044023 | 0.00094606 | -0.024381 | 0.056841 | 0.045621 | -0.21808 | -0.015137 | -0.024107 | -0.07782 | 0.073242 | -0.09613 | -0.041199 | 0.13733 | 0 | 0.041199 | -20.3064 | 0.59052 | -122.0993 | 0.58594 | -121.4951 | -121.788 | -121.4172 | 121.9574 | -0.5127 | -0.62714 | 122.1909 | 122.0947 | 122.0535 | 0.13733 | 0.09613 | -0.045776 | 0.004578 | 0 | 0.55847 | 0.63629 | 0.2655 | 0.68207 | 0.31128 | 0.23346 | 0.054931 | 0.60425 | 122.6852 | 0.16937 | 122.6898 | 122.1268 | 122.644 | -0.68207 | -122.6852 | 122.0123 | 122.6395 | 121.9757 | 101.7471
1980.4844 | 122.8088 | -122.0444 | 0.59967 | -0.0051118 | -0.013943 | -0.077729 | -0.0076199 | -0.03258 | -0.049526 | -0.042101 | -0.0021057 | -0.019681 | 0.057482 | 0.040708 | -0.21659 | -0.015992 | -0.020903 | -0.10529 | 0.07782 | -0.091553 | -0.086975 | 0.07782 | -0.086975 | 0.004578 | -20.4895 | 0.57678 | -122.1085 | 0.5127 | -121.5912 | -121.8887 | -121.4722 | 121.9528 | -0.52185 | -0.68665 | 122.1222 | 122.049 | 121.9574 | 0.096131 | 0.004578 | -0.064086 | -0.022888 | -0.086975 | 0.45319 | 0.5722 | 0.15564 | 0.63629 | 0.21973 | 0.16937 | 0.004578 | 0.51727 | 122.6212 | 0.16937 | 122.6852 | 122.1222 | 122.6212 | -0.69122 | -122.7081 | 121.9574 | 122.5571 | 121.9391 | 101.5549
1982.2031 | 122.8638 | -122.0581 | 0.58136 | -0.0051118 | -0.015866 | -0.080292 | -0.0054837 | -0.032152 | -0.052304 | -0.040392 | -0.0051575 | -0.02139 | 0.058977 | 0.043485 | -0.21915 | -0.018555 | -0.027098 | -0.059509 | 0.073242 | -0.10071 | -0.022888 | 0.15106 | -0.009155 | 0.054932 | -20.4758 | 0.56763 | -122.1085 | 0.58594 | -121.4813 | -121.7972 | -121.4127 | 121.9574 | -0.50812 | -0.60425 | 122.2092 | 122.113 | 122.0489 | 0.15564 | 0.091553 | -0.050354 | -0.013733 | 0.004577 | 0.57678 | 0.64545 | 0.26093 | 0.6958 | 0.31128 | 0.25177 | 0.07782 | 0.62714 | 122.6944 | 0.17395 | 122.6761 | 122.1313 | 122.6257 | -0.68207 | -122.6898 | 122.0352 | 122.644 | 121.9986 | 101.5823
1984 | 122.7264 | -122.1085 | 0.62256 | 0.0025177 | -0.016293 | -0.080933 | -0.0054837 | -0.030016 | -0.051449 | -0.040392 | 0.00094606 | -0.022031 | 0.059832 | 0.053739 | -0.22193 | -0.013428 | -0.025603 | -0.13275 | 0.11902 | -0.14648 | -0.15564 | -0.022888 | -0.15564 | -0.07782 | -20.7459 | 0.60425 | -122.1634 | 0.43488 | -121.6599 | -121.9711 | -121.5591 | 121.962 | -0.50354 | -0.7782 | 122.0856 | 122.0306 | 121.9528 | 0.068664 | -0.009156 | -0.054932 | -0.018311 | -0.18768 | 0.44861 | 0.54932 | 0.13733 | 0.60425 | 0.19226 | 0.1236 | -0.009156 | 0.50354 | 122.5983 | 0.2655 | 122.7676 | 122.2275 | 122.7127 | -0.76904 | -122.7859 | 121.9528 | 122.5433 | 121.9757 | 101.3626
1985.7812 | 122.7264 | -122.1405 | 0.59052 | -0.0051118 | -0.013516 | -0.077515 | -0.0056973 | -0.03322 | -0.050167 | -0.040819 | -0.0051575 | -0.020749 | 0.057695 | 0.040067 | -0.21915 | -0.016633 | -0.021544 | -0.14648 | 0.11902 | -0.11444 | -0.15564 | -0.009155 | -0.13733 | -0.059509 | -20.842 | 0.59509 | -122.1542 | 0.41199 | -121.669 | -121.9711 | -121.582 | 122.0261 | -0.4715 | -0.74616 | 122.1313 | 122.081 | 122.0032 | 0.054932 | -0.022888 | -0.013733 | 0.004578 | -0.17853 | 0.4715 | 0.55847 | 0.16937 | 0.5722 | 0.18311 | 0.10529 | -0.041199 | 0.48523 | 122.5662 | 0.23346 | 122.7493 | 122.2595 | 122.7356 | -0.70496 | -122.7448 | 121.9849 | 122.5525 | 121.994 | 101.2985
1987.5625 | 122.8455 | -122.0718 | 0.55389 | 0.017777 | -0.016079 | -0.080506 | -0.0080471 | -0.031725 | -0.049313 | -0.041887 | 0.0039979 | -0.023099 | 0.058763 | 0.042203 | -0.22043 | -0.017487 | -0.022185 | -0.082397 | 0.059509 | -0.086975 | -0.059509 | 0.10986 | -0.036621 | 0.036621 | -20.8054 | 0.55847 | -122.1725 | 0.54016 | -121.5363 | -121.8475 | -121.4539 | 121.9849 | -0.49439 | -0.6134 | 122.1817 | 122.1085 | 122.0352 | 0.1236 | 0.050354 | -0.10071 | 0.004578 | -0.013733 | 0.53558 | 0.61798 | 0.2243 | 0.71869 | 0.32501 | 0.19684 | 0.027466 | 0.63629 | 122.7127 | 0.14648 | 122.731 | 122.1313 | 122.6303 | -0.64087 | -122.7264 | 122.0123 | 122.612 | 121.9894 | 101.2665
1989.3438 | 122.7127 | -122.1588 | 0.59509 | 0.010147 | -0.012875 | -0.079651 | -0.0046291 | -0.033648 | -0.050595 | -0.040392 | 0.00094606 | -0.017545 | 0.058977 | 0.045835 | -0.22129 | -0.015778 | -0.025389 | -0.13733 | 0.09613 | -0.13275 | -0.16022 | -0.018311 | -0.13733 | -0.068665 | -20.9518 | 0.58594 | -122.1863 | 0.40283 | -121.6873 | -122.0215 | -121.5866 | 122.0261 | -0.49896 | -0.75531 | 122.1405 | 122.0901 | 122.0215 | 0.064086 | -0.004578 | -0.027466 | -0.009156 | -0.19226 | 0.4715 | 0.5722 | 0.13733 | 0.59967 | 0.16479 | 0.11444 | -0.027466 | 0.49896 | 122.5891 | 0.22888 | 122.7722 | 122.2549 | 122.7447 | -0.72784 | -122.7814 | 121.9986 | 122.5616 | 122.0215 | 101.207
1991.1406 | 122.8271 | -122.1176 | 0.54932 | -0.0051118 | -0.016934 | -0.079865 | -0.0071927 | -0.03322 | -0.049954 | -0.041033 | 0.0039979 | -0.021176 | 0.056841 | 0.053312 | -0.21979 | -0.014496 | -0.024962 | -0.050354 | 0.073242 | -0.10529 | -0.013733 | 0.14191 | 0 | 0.054932 | -20.8923 | 0.53101 | -122.168 | 0.52643 | -121.5454 | -121.8521 | -121.4767 | 122.0123 | -0.47607 | -0.56305 | 122.2595 | 122.1725 | 122.1176 | 0.16022 | 0.10529 | -0.050354 | -0.01831 | -0.022888 | 0.5722 | 0.64087 | 0.2655 | 0.69122 | 0.31586 | 0.24719 | 0.091553 | 0.62256 | 122.6944 | 0.17853 | 122.699 | 122.1909 | 122.6486 | -0.6546 | -122.7173 | 122.1039 | 122.644 | 122.0673 | 101.2253
1992.8906 | 122.7997 | -122.1268 | 0.54932 | -0.0051118 | -0.012875 | -0.079651 | -0.0074063 | -0.031084 | -0.050808 | -0.044878 | -0.0021057 | -0.020322 | 0.056841 | 0.046689 | -0.22001 | -0.016633 | -0.025816 | -0.10071 | 0.068665 | -0.10529 | -0.082397 | 0.054932 | -0.091553 | -0.027466 | -21.0709 | 0.53558 | -122.1817 | 0.46234 | -121.6324 | -121.9391 | -121.5317 | 122.0215 | -0.48065 | -0.63171 | 122.1817 | 122.0993 | 122.0352 | 0.07782 | 0.013733 | -0.054932 | -0.013733 | -0.086975 | 0.49438 | 0.59509 | 0.18768 | 0.65002 | 0.24262 | 0.16022 | 0.022889 | 0.54932 | 122.644 | 0.17395 | 122.7173 | 122.1954 | 122.6624 | -0.6546 | -122.731 | 122.0444 | 122.5891 | 122.0261 | 101.0559
1994.6875 | 122.7951 | -122.0901 | 0.55389 | 0.010147 | -0.013516 | -0.079011 | -0.0052701 | -0.031298 | -0.051663 | -0.041033 | 0.00094606 | -0.020536 | 0.058123 | 0.048398 | -0.21958 | -0.017701 | -0.023467 | -0.10529 | 0.073242 | -0.10071 | -0.082397 | 0.054932 | -0.09613 | -0.009155 | -21.1441 | 0.55389 | -122.1863 | 0.47607 | -121.6232 | -121.9482 | -121.5271 | 121.9894 | -0.48065 | -0.63629 | 122.1451 | 122.081 | 121.994 | 0.091553 | 0.004578 | -0.09613 | 0 | -0.07782 | 0.46692 | 0.56305 | 0.14191 | 0.65918 | 0.23804 | 0.15564 | 0.018311 | 0.56305 | 122.6624 | 0.17395 | 122.7402 | 122.1634 | 122.644 | -0.6546 | -122.7402 | 122.0078 | 122.5662 | 121.9849 | 100.946
1996.4688 | 122.7631 | -122.1451 | 0.55389 | -0.0051118 | -0.013302 | -0.077729 | -0.0029201 | -0.030443 | -0.052517 | -0.037401 | -0.0021057 | -0.016049 | 0.058336 | 0.05438 | -0.22086 | -0.015565 | -0.022612 | -0.059509 | 0.091553 | -0.11444 | -0.091553 | 0.036621 | -0.10986 | -0.045776 | -21.1075 | 0.55389 | -122.1634 | 0.44861 | -121.6324 | -121.9803 | -121.5637 | 122.0306 | -0.46234 | -0.64545 | 122.1817 | 122.0993 | 122.0352 | 0.068665 | 0.004578 | -0.01831 | 0 | -0.10529 | 0.5127 | 0.58136 | 0.16479 | 0.59967 | 0.1831 | 0.15106 | 0.022888 | 0.53101 | 122.612 | 0.20599 | 122.7173 | 122.2366 | 122.699 | -0.66834 | -122.7173 | 122.0535 | 122.5937 | 122.0856 | 101.0376
1998.1875 | 122.8409 | -122.1268 | 0.54016 | -0.0051118 | -0.014157 | -0.08136 | -0.0069791 | -0.033434 | -0.050167 | -0.039324 | -0.0021057 | -0.021604 | 0.056627 | 0.039426 | -0.22043 | -0.016633 | -0.023253 | -0.091553 | 0.064087 | -0.09613 | -0.064087 | 0.09613 | -0.068665 | 0.004578 | -21.1624 | 0.5127 | -122.2 | 0.50812 | -121.5775 | -121.8933 | -121.4951 | 122.0306 | -0.47607 | -0.60425 | 122.2229 | 122.1313 | 122.0581 | 0.10071 | 0.027465 | -0.073242 | -0.027466 | -0.032043 | 0.54932 | 0.63171 | 0.23346 | 0.70496 | 0.3067 | 0.19226 | 0.032043 | 0.62256 | 122.7081 | 0.16022 | 122.7127 | 122.1909 | 122.6395 | -0.63629 | -122.7402 | 122.0627 | 122.6349 | 122.0352 | 100.9644
1999.9844 | 122.8592 | -122.1176 | 0.49896 | -0.0051118 | -0.010525 | -0.079865 | -0.0037747 | -0.034929 | -0.04974 | -0.038896 | 0.00094606 | -0.019895 | 0.058123 | 0.047758 | -0.22107 | -0.015565 | -0.025176 | -0.041199 | 0.068665 | -0.09613 | -0.027466 | 0.11902 | -0.059509 | 0.027466 | -21.1853 | 0.51727 | -122.1863 | 0.53101 | -121.6095 | -121.907 | -121.4859 | 122.0215 | -0.4303 | -0.52643 | 122.2366 | 122.1451 | 122.0581 | 0.1236 | 0.036621 | -0.068664 | 0.018311 | 0.032044 | 0.50812 | 0.63171 | 0.21057 | 0.70038 | 0.27924 | 0.21515 | 0.068664 | 0.57678 | 122.7173 | 0.16479 | 122.7036 | 122.1863 | 122.6349 | -0.59509 | -122.6852 | 122.0901 | 122.6486 | 122.0764 | 100.9323
2001.7188 | 122.8546 | -122.1405 | 0.5127 | 0.0025177 | -0.013729 | -0.077515 | -0.0042019 | -0.033648 | -0.049526 | -0.040819 | -0.0021057 | -0.020322 | 0.055773 | 0.042417 | -0.21937 | -0.014924 | -0.021971 | -0.032043 | 0.073242 | -0.073242 | -0.004578 | 0.13733 | -0.064087 | 0.018311 | -21.2311 | 0.50354 | -122.168 | 0.52185 | -121.5866 | -121.8933 | -121.4905 | 122.0673 | -0.43945 | -0.51727 | 122.2778 | 122.1588 | 122.0764 | 0.091553 | 0.009155 | -0.027466 | -0.009155 | 0.009156 | 0.55389 | 0.65002 | 0.24719 | 0.67749 | 0.27466 | 0.21057 | 0.068664 | 0.58136 | 122.6898 | 0.14648 | 122.6715 | 122.2137 | 122.644 | -0.58594 | -122.6807 | 122.1359 | 122.6624 | 122.1085 | 100.9094
2003.5156 | 122.7631 | -122.1634 | 0.54932 | 0.0025177 | -0.011593 | -0.078797 | -0.0042019 | -0.034929 | -0.048886 | -0.041887 | -0.0051575 | -0.017758 | 0.058123 | 0.051389 | -0.22129 | -0.013856 | -0.026671 | -0.09613 | 0.12817 | -0.14648 | -0.15106 | 0 | -0.13733 | -0.064087 | -21.3226 | 0.55389 | -122.2137 | 0.42114 | -121.669 | -122.0032 | -121.5775 | 122.0169 | -0.42114 | -0.70038 | 122.1634 | 122.0993 | 122.0261 | 0.082397 | 0.009155 | -0.050354 | 0.004578 | -0.12817 | 0.49439 | 0.58594 | 0.16022 | 0.63629 | 0.21057 | 0.14648 | -0.004578 | 0.54474 | 122.6349 | 0.27466 | 122.7676 | 122.2916 | 122.7173 | -0.6958 | -122.7631 | 122.0123 | 122.5845 | 122.0673 | 100.8408
2005.2344 | 122.731 | -122.1634 | 0.54932 | -0.0051118 | -0.01202 | -0.079224 | -0.0044155 | -0.031084 | -0.04974 | -0.040819 | -0.0051575 | -0.019254 | 0.057695 | 0.04968 | -0.21808 | -0.016419 | -0.023467 | -0.086975 | 0.10529 | -0.13733 | -0.09613 | 0.036621 | -0.1236 | -0.059509 | -21.3684 | 0.55389 | -122.2092 | 0.41657 | -121.7056 | -122.049 | -121.5958 | 122.0261 | -0.44403 | -0.64545 | 122.2 | 122.1039 | 122.0398 | 0.07782 | 0.013733 | -0.045776 | 0.004578 | -0.13275 | 0.45776 | 0.56763 | 0.11444 | 0.6134 | 0.16022 | 0.17395 | 0.041199 | 0.50354 | 122.6257 | 0.24262 | 122.7631 | 122.2687 | 122.7173 | -0.68665 | -122.7585 | 122.0673 | 122.58 | 122.0764 | 100.795
2007.0156 | 122.7631 | -122.1817 | 0.54932 | 0.0025177 | -0.012448 | -0.080506 | -0.0044155 | -0.026598 | -0.050808 | -0.041674 | -0.0021057 | -0.019895 | 0.058977 | 0.042631 | -0.21915 | -0.014496 | -0.02133 | -0.11902 | 0.09613 | -0.13275 | -0.14191 | -0.009155 | -0.13733 | -0.07782 | -21.5057 | 0.53101 | -122.2549 | 0.39368 | -121.6644 | -122.0032 | -121.5958 | 122.049 | -0.45319 | -0.69122 | 122.1725 | 122.1039 | 122.0444 | 0.054931 | -0.004578 | -0.073242 | -0.01831 | -0.15564 | 0.51727 | 0.58594 | 0.17853 | 0.65918 | 0.25177 | 0.1236 | -0.009156 | 0.59051 | 122.6486 | 0.22888 | 122.7859 | 122.2778 | 122.7127 | -0.68207 | -122.8043 | 122.0398 | 122.5754 | 122.0627 | 100.676
2008.7969 | 122.8729 | -122.1451 | 0.50354 | 0.0025177 | -0.01672 | -0.079224 | -0.0074063 | -0.03258 | -0.049526 | -0.041033 | -0.0021057 | -0.02139 | 0.055773 | 0.037076 | -0.2183 | -0.016205 | -0.019408 | -0.082397 | 0.059509 | -0.086975 | -0.050354 | 0.10986 | -0.027466 | 0.045776 | -21.4691 | 0.48981 | -122.2137 | 0.49439 | -121.582 | -121.8887 | -121.5088 | 122.0581 | -0.44403 | -0.55389 | 122.2549 | 122.1909 | 122.1176 | 0.13275 | 0.059509 | -0.068664 | -0.013733 | -0.009155 | 0.56305 | 0.63629 | 0.25635 | 0.70496 | 0.32501 | 0.19684 | 0.036621 | 0.63171 | 122.7081 | 0.14648 | 122.7036 | 122.2046 | 122.6349 | -0.59052 | -122.7173 | 122.0947 | 122.6395 | 122.0627 | 100.676
2010.5938 | 122.8317 | -122.1542 | 0.50354 | -0.0051118 | -0.014798 | -0.080292 | -0.0061245 | -0.030871 | -0.051449 | -0.040605 | -0.0021057 | -0.022458 | 0.057268 | 0.044767 | -0.22022 | -0.01706 | -0.023467 | -0.064087 | 0.073242 | -0.07782 | -0.018311 | 0.13733 | -0.018311 | 0.027466 | -21.5057 | 0.50354 | -122.2137 | 0.46234 | -121.6278 | -121.9345 | -121.55 | 122.0764 | -0.4303 | -0.52185 | 122.2916 | 122.1817 | 122.1359 | 0.10529 | 0.059509 | -0.059509 | 0 | -0.041199 | 0.52643 | 0.60425 | 0.21973 | 0.66376 | 0.27924 | 0.21515 | 0.059509 | 0.58594 | 122.6761 | 0.15106 | 122.7173 | 122.2275 | 122.6578 | -0.58136 | -122.7173 | 122.1359 | 122.6166 | 122.0901 | 100.6485
2012.3125 | 122.7585 | -122.1817 | 0.52643 | -0.012741 | -0.010098 | -0.080292 | -0.0037747 | -0.028948 | -0.050595 | -0.041887 | -0.0021057 | -0.017331 | 0.061113 | 0.049253 | -0.21915 | -0.01471 | -0.024321 | -0.073242 | 0.10071 | -0.11902 | -0.091553 | 0.041199 | -0.10986 | -0.059509 | -21.5973 | 0.52185 | -122.2504 | 0.40741 | -121.7148 | -122.0535 | -121.6232 | 122.0627 | -0.42572 | -0.61798 | 122.2229 | 122.1222 | 122.0718 | 0.05951 | 0.009156 | -0.068664 | -0.004577 | -0.11902 | 0.46692 | 0.55847 | 0.12817 | 0.62714 | 0.19684 | 0.16022 | 0.027466 | 0.53558 | 122.6578 | 0.21973 | 122.7722 | 122.2824 | 122.7036 | -0.64545 | -122.7768 | 122.0901 | 122.5891 | 122.1085 | 100.5844
2014.125 | 122.8683 | -122.1725 | 0.5127 | -0.0051118 | -0.016079 | -0.081574 | -0.0078335 | -0.029589 | -0.048458 | -0.044664 | -0.0051575 | -0.021176 | 0.058977 | 0.036863 | -0.21979 | -0.016633 | -0.022826 | -0.09613 | 0.091553 | -0.09613 | -0.050354 | 0.1236 | -0.036621 | 0.032043 | -21.7072 | 0.48981 | -122.2183 | 0.48065 | -121.5912 | -121.8887 | -121.5134 | 122.0764 | -0.42114 | -0.56305 | 122.2961 | 122.2046 | 122.1359 | 0.12817 | 0.059509 | -0.045777 | -0.022888 | -0.032043 | 0.58136 | 0.65918 | 0.28381 | 0.70496 | 0.32959 | 0.21973 | 0.045776 | 0.62714 | 122.699 | 0.18768 | 122.7081 | 122.2641 | 122.6624 | -0.60882 | -122.731 | 122.1222 | 122.6532 | 122.0764 | 100.4654
2015.8438 | 122.7402 | -122.2137 | 0.53101 | 0.0025177 | -0.014584 | -0.081574 | -0.0063381 | -0.030443 | -0.049954 | -0.04146 | -0.0051575 | -0.018186 | 0.058336 | 0.044553 | -0.21937 | -0.015778 | -0.023039 | -0.11444 | 0.09613 | -0.13275 | -0.1236 | 0.018311 | -0.13275 | -0.045776 | -21.9223 | 0.54016 | -122.2412 | 0.35706 | -121.7239 | -122.049 | -121.6507 | 122.081 | -0.43488 | -0.6546 | 122.2321 | 122.168 | 122.081 | 0.086975 | 0 | -0.027466 | 0.009155 | -0.17395 | 0.48981 | 0.56305 | 0.16479 | 0.59052 | 0.19226 | 0.15106 | 0.009155 | 0.51727 | 122.5983 | 0.22888 | 122.7814 | 122.3099 | 122.7539 | -0.66376 | -122.7722 | 122.0901 | 122.5708 | 122.0993 | 100.2914
2017.6406 | 122.8592 | -122.1542 | 0.5127 | -0.0051118 | -0.013516 | -0.080719 | -0.0076199 | -0.028521 | -0.04974 | -0.042955 | -0.0051575 | -0.02139 | 0.056627 | 0.046903 | -0.21979 | -0.01706 | -0.025176 | -0.059509 | 0.073242 | -0.10071 | -0.009155 | 0.14648 | 0 | 0.054932 | -21.9177 | 0.49896 | -122.2366 | 0.48065 | -121.5866 | -121.9208 | -121.5317 | 122.0535 | -0.43945 | -0.52185 | 122.3007 | 122.2092 | 122.1542 | 0.15564 | 0.10071 | -0.082397 | -0.013733 | -0.032043 | 0.56763 | 0.62256 | 0.23346 | 0.70496 | 0.31586 | 0.24719 | 0.091553 | 0.65002 | 122.7173 | 0.17395 | 122.7356 | 122.2275 | 122.6532 | -0.6134 | -122.7493 | 122.1451 | 122.6349 | 122.0947 | 100.2365
2019.4219 | 122.8592 | -122.1497 | 0.5127 | -0.0051118 | -0.011807 | -0.078797 | -0.0056973 | -0.029375 | -0.050381 | -0.041033 | -0.0021057 | -0.019254 | 0.0562 | 0.047758 | -0.21766 | -0.014924 | -0.023894 | -0.059509 | 0.050354 | -0.091553 | -0.022888 | 0.1236 | -0.045776 | 0.032043 | -22.0413 | 0.49439 | -122.1909 | 0.48981 | -121.6324 | -121.9574 | -121.5363 | 122.0581 | -0.46234 | -0.53558 | 122.2733 | 122.1817 | 122.1039 | 0.1236 | 0.045777 | -0.041199 | -0.01831 | -0.022888 | 0.51727 | 0.6134 | 0.19226 | 0.6546 | 0.23346 | 0.21515 | 0.068665 | 0.55847 | 122.6807 | 0.14191 | 122.6852 | 122.2 | 122.644 | -0.60425 | -122.7036 | 122.1268 | 122.6395 | 122.0901 | 100.1083
2021.1562 | 122.8043 | -122.1771 | 0.5127 | -0.0051118 | -0.01138 | -0.078583 | -0.0044155 | -0.029589 | -0.049313 | -0.042528 | -0.0021057 | -0.019895 | 0.057909 | 0.046903 | -0.21915 | -0.015565 | -0.026671 | -0.11902 | 0.10071 | -0.11444 | -0.12817 | -0.013733 | -0.1831 | -0.073242 | -22.2656 | 0.54016 | -122.2137 | 0.43945 | -121.6919 | -122.0215 | -121.582 | 122.0627 | -0.41199 | -0.64087 | 122.1634 | 122.1039 | 121.994 | 0.041199 | -0.068664 | -0.036621 | 0.027466 | -0.073242 | 0.48523 | 0.59509 | 0.15564 | 0.63171 | 0.19226 | 0.10071 | -0.013733 | 0.52185 | 122.6532 | 0.21515 | 122.7539 | 122.2778 | 122.7173 | -0.62714 | -122.7264 | 122.049 | 122.6166 | 122.0581 | 99.9115
2022.9375 | 122.8821 | -122.1588 | 0.50354 | -0.0051118 | -0.013729 | -0.081788 | -0.0065517 | -0.037066 | -0.050808 | -0.040392 | 0.00094606 | -0.021176 | 0.057482 | 0.043912 | -0.2183 | -0.016419 | -0.023039 | -0.054932 | 0.068665 | -0.086975 | -0.013733 | 0.16479 | 0 | 0.07782 | -22.2107 | 0.49439 | -122.2 | 0.49896 | -121.5683 | -121.8796 | -121.5134 | 122.0718 | -0.43488 | -0.51727 | 122.3236 | 122.2366 | 122.1588 | 0.16479 | 0.086975 | -0.041199 | -0.009155 | -0.004578 | 0.59051 | 0.64545 | 0.27923 | 0.68664 | 0.32043 | 0.25177 | 0.073242 | 0.63171 | 122.699 | 0.15564 | 122.6944 | 122.2275 | 122.6532 | -0.59052 | -122.7036 | 122.1451 | 122.6578 | 122.1039 | 99.9481
2024.7344 | 122.8317 | -122.1954 | 0.49439 | -0.012741 | -0.015438 | -0.080506 | -0.0065517 | -0.030016 | -0.051022 | -0.036974 | -0.0051575 | -0.023526 | 0.058336 | 0.04498 | -0.21915 | -0.016633 | -0.024107 | -0.10529 | 0.07782 | -0.10529 | -0.091553 | 0.059509 | -0.09613 | -0.018311 | -22.4899 | 0.49896 | -122.2549 | 0.41657 | -121.6599 | -121.9803 | -121.5775 | 122.0901 | -0.41657 | -0.58594 | 122.2549 | 122.1771 | 122.0993 | 0.086975 | 0.009156 | -0.059509 | 0.004577 | -0.07782 | 0.53558 | 0.61798 | 0.21515 | 0.67749 | 0.27466 | 0.16479 | 0.013733 | 0.59509 | 122.6715 | 0.18311 | 122.7539 | 122.2733 | 122.6944 | -0.59967 | -122.7493 | 122.1039 | 122.612 | 122.0901 | 99.7055
2026.5156 | 122.7814 | -122.2092 | 0.53558 | 0.017777 | -0.014157 | -0.079224 | -0.0061245 | -0.032793 | -0.053799 | -0.042101 | -0.0021057 | -0.021817 | 0.057482 | 0.04968 | -0.22107 | -0.015992 | -0.022185 | -0.059509 | 0.086975 | -0.10529 | -0.068665 | 0.082397 | -0.054932 | 0.004578 | -22.5037 | 0.5127 | -122.2412 | 0.3891 | -121.6919 | -122.0306 | -121.6324 | 122.1039 | -0.44861 | -0.60425 | 122.2916 | 122.2137 | 122.1542 | 0.10986 | 0.050354 | -0.032044 | -0.022888 | -0.14648 | 0.51727 | 0.57678 | 0.17853 | 0.60883 | 0.21057 | 0.18768 | 0.036621 | 0.54932 | 122.6303 | 0.19226 | 122.7539 | 122.2961 | 122.7219 | -0.64087 | -122.7768 | 122.1405 | 122.5983 | 122.1497 | 99.7055
2028.2812 | 122.7905 | -122.2046 | 0.50812 | 0.0025177 | -0.012875 | -0.079438 | -0.0033475 | -0.03322 | -0.051022 | -0.039965 | -0.0021057 | -0.018186 | 0.058123 | 0.047971 | -0.21979 | -0.015565 | -0.023467 | -0.082397 | 0.09613 | -0.10986 | -0.082397 | 0.045776 | -0.09613 | -0.027466 | -22.554 | 0.50354 | -122.2458 | 0.44861 | -121.6873 | -122.049 | -121.6095 | 122.0947 | -0.41199 | -0.59051 | 122.2504 | 122.1771 | 122.1085 | 0.082397 | 0.013733 | -0.041199 | -0.004578 | -0.05951 | 0.51727 | 0.59509 | 0.15564 | 0.63629 | 0.19684 | 0.15564 | 0.027466 | 0.55847 | 122.6944 | 0.20599 | 122.7493 | 122.3007 | 122.7081 | -0.61798 | -122.7539 | 122.1222 | 122.6532 | 122.1222 | 99.6506
2030.0625 | 122.7768 | -122.2046 | 0.5127 | -0.0051118 | -0.011807 | -0.080079 | -0.0050565 | -0.028734 | -0.048245 | -0.041246 | 0.00094606 | -0.018399 | 0.056414 | 0.048185 | -0.21872 | -0.015778 | -0.02133 | -0.086975 | 0.09613 | -0.11444 | -0.10071 | 0.045776 | -0.11444 | -0.050354 | -22.6547 | 0.49439 | -122.2549 | 0.39825 | -121.7194 | -122.0718 | -121.6232 | 122.0901 | -0.41657 | -0.6134 | 122.2504 | 122.1542 | 122.0901 | 0.064087 | 0 | -0.050354 | -0.01831 | -0.11444 | 0.48523 | 0.58136 | 0.13275 | 0.63171 | 0.18311 | 0.16022 | 0.013733 | 0.53558 | 122.6532 | 0.21057 | 122.7493 | 122.3007 | 122.699 | -0.62714 | -122.7676 | 122.1039 | 122.6028 | 122.1176 | 99.5499
2031.8438 | 122.8958 | -122.1771 | 0.47607 | -0.0051118 | -0.016079 | -0.080933 | -0.0093289 | -0.029375 | -0.04974 | -0.040605 | -0.0021057 | -0.02374 | 0.057482 | 0.040281 | -0.21872 | -0.017914 | -0.027739 | -0.050354 | 0.07782 | -0.091553 | -0.027466 | 0.17853 | 0.013733 | 0.054932 | -22.6593 | 0.4715 | -122.2321 | 0.48523 | -121.6049 | -121.9116 | -121.5408 | 122.0856 | -0.39825 | -0.50354 | 122.3557 | 122.2321 | 122.1909 | 0.14649 | 0.10529 | -0.054932 | -0.004577 | 0.009155 | 0.57221 | 0.63629 | 0.2655 | 0.69122 | 0.32044 | 0.27008 | 0.064087 | 0.62714 | 122.7173 | 0.16937 | 122.7036 | 122.2549 | 122.6486 | -0.56763 | -122.7081 | 122.1497 | 122.6624 | 122.1268 | 99.5178
2033.5625 | 122.7448 | -122.2504 | 0.53101 | 0.0025177 | -0.014584 | -0.080506 | -0.0052701 | -0.033007 | -0.052304 | -0.040819 | 0.00094606 | -0.020536 | 0.059404 | 0.046262 | -0.2183 | -0.015992 | -0.019835 | -0.13275 | 0.09613 | -0.1236 | -0.14648 | -0.009155 | -0.13275 | -0.086975 | -22.8607 | 0.52643 | -122.2824 | 0.33417 | -121.756 | -122.0901 | -121.6919 | 122.1268 | -0.43488 | -0.67749 | 122.2412 | 122.1634 | 122.1176 | 0.036621 | -0.009155 | -0.032044 | -0.004578 | -0.19684 | 0.49438 | 0.55847 | 0.16022 | 0.59051 | 0.19226 | 0.11444 | -0.022888 | 0.52643 | 122.6166 | 0.21973 | 122.8088 | 122.3465 | 122.7768 | -0.6546 | -122.8134 | 122.1039 | 122.5845 | 122.1176 | 99.3896
2035.3438 | 122.8775 | -122.1725 | 0.48065 | 0.0025177 | -0.0096707 | -0.076233 | -0.0046291 | -0.029375 | -0.050167 | -0.040605 | 0.00094606 | -0.018186 | 0.055986 | 0.050748 | -0.2183 | -0.014496 | -0.022398 | -0.032043 | 0.059509 | -0.07782 | -0.022888 | 0.1236 | -0.050354 | 0.022888 | -22.8333 | 0.46234 | -122.2412 | 0.49439 | -121.637 | -121.9711 | -121.5179 | 122.0947 | -0.42114 | -0.50354 | 122.2961 | 122.1954 | 122.1222 | 0.10071 | 0.027466 | -0.068665 | -0.018311 | 0.013733 | 0.53558 | 0.6546 | 0.20142 | 0.72327 | 0.27008 | 0.20142 | 0.054932 | 0.60425 | 122.7356 | 0.13733 | 122.7036 | 122.2321 | 122.6349 | -0.55847 | -122.7219 | 122.1497 | 122.6669 | 122.1405 | 99.3393
2037.125 | 122.7493 | -122.2321 | 0.53101 | 0.0025177 | -0.014157 | -0.080933 | -0.0056973 | -0.031725 | -0.052731 | -0.03911 | -0.0021057 | -0.020108 | 0.059404 | 0.047971 | -0.2183 | -0.014283 | -0.023039 | -0.14191 | 0.11444 | -0.1236 | -0.16022 | -0.018311 | -0.13733 | -0.059509 | -23.0484 | 0.51727 | -122.3053 | 0.31586 | -121.7789 | -122.1039 | -121.6873 | 122.1085 | -0.41656 | -0.69122 | 122.2137 | 122.1725 | 122.0947 | 0.064087 | -0.013733 | -0.073242 | -0.013733 | -0.21515 | 0.45319 | 0.54474 | 0.12817 | 0.61798 | 0.20142 | 0.10528 | -0.036621 | 0.52643 | 122.6212 | 0.23804 | 122.8226 | 122.3465 | 122.7493 | -0.6546 | -122.8363 | 122.0718 | 122.5479 | 122.0901 | 99.1837
2038.8438 | 122.8775 | -122.1909 | 0.48065 | -0.0051118 | -0.013729 | -0.080292 | -0.0084743 | -0.032366 | -0.05209 | -0.04146 | -0.0021057 | -0.02139 | 0.057054 | 0.037717 | -0.21894 | -0.014496 | -0.024535 | -0.082397 | 0.068665 | -0.091553 | -0.068665 | 0.082397 | -0.064087 | 0 | -23.0438 | 0.47607 | -122.2733 | 0.42114 | -121.6553 | -121.9711 | -121.5775 | 122.0993 | -0.41199 | -0.54932 | 122.2733 | 122.1909 | 122.1268 | 0.091553 | 0.027466 | -0.082397 | -0.004578 | -0.059509 | 0.53558 | 0.6134 | 0.21973 | 0.6958 | 0.30212 | 0.17395 | 0.022888 | 0.61798 | 122.6944 | 0.16022 | 122.7493 | 122.2595 | 122.6669 | -0.57221 | -122.7539 | 122.1222 | 122.612 | 122.1085 | 99.147
2040.6406 | 122.818 | -122.2321 | 0.50354 | -0.012741 | -0.011166 | -0.077942 | -0.0016385 | -0.030443 | -0.052731 | -0.041033 | -0.0051575 | -0.017331 | 0.060259 | 0.044767 | -0.22022 | -0.01471 | -0.023039 | -0.064087 | 0.10071 | -0.10529 | -0.10071 | 0.054932 | -0.10986 | -0.050354 | -23.0942 | 0.49439 | -122.287 | 0.40283 | -121.7148 | -122.049 | -121.6232 | 122.1268 | -0.40283 | -0.60425 | 122.287 | 122.1817 | 122.1222 | 0.054932 | -0.004577 | -0.054931 | -0.009155 | -0.10071 | 0.51727 | 0.60883 | 0.18311 | 0.66376 | 0.23804 | 0.16022 | 0.004578 | 0.5722 | 122.6898 | 0.20599 | 122.7814 | 122.3328 | 122.7264 | -0.60883 | -122.7905 | 122.1313 | 122.6349 | 122.168 | 99.1379
2042.4219 | 122.8592 | -122.2321 | 0.48065 | 0.0025177 | -0.013729 | -0.079865 | -0.0056973 | -0.02788 | -0.050595 | -0.042528 | -0.0021057 | -0.022031 | 0.056627 | 0.04199 | -0.21894 | -0.016633 | -0.023253 | -0.09613 | 0.064087 | -0.10529 | -0.082397 | 0.068665 | -0.082397 | 0.004578 | -23.2819 | 0.46692 | -122.2733 | 0.4303 | -121.6736 | -121.9894 | -121.5958 | 122.1268 | -0.41657 | -0.56305 | 122.3007 | 122.2366 | 122.1497 | 0.10986 | 0.022889 | -0.041198 | -0.013733 | -0.050354 | 0.55847 | 0.63629 | 0.24262 | 0.67749 | 0.28381 | 0.17395 | 0.022889 | 0.59967 | 122.7036 | 0.16937 | 122.7402 | 122.2961 | 122.699 | -0.58594 | -122.7539 | 122.1497 | 122.6624 | 122.1359 | 98.9502
2044.1562 | 122.7676 | -122.2595 | 0.48523 | -0.012741 | -0.0083889 | -0.079224 | -0.0035611 | -0.031511 | -0.050595 | -0.040605 | 0.00094606 | -0.01904 | 0.060686 | 0.046049 | -0.22043 | -0.013001 | -0.027525 | -0.054932 | 0.086975 | -0.10986 | -0.091553 | 0.032043 | -0.13275 | -0.07782 | -23.3231 | 0.48523 | -122.2778 | 0.37079 | -121.7697 | -122.1176 | -121.6827 | 122.1497 | -0.39825 | -0.57678 | 122.2916 | 122.1817 | 122.1268 | 0.032043 | -0.022888 | -0.018311 | 0 | -0.11444 | 0.48981 | 0.57678 | 0.14191 | 0.59509 | 0.16022 | 0.14191 | 0.01831 | 0.50812 | 122.6486 | 0.19684 | 122.7631 | 122.3465 | 122.7448 | -0.59509 | -122.7631 | 122.168 | 122.6303 | 122.2046 | 98.9365
2045.9531 | 122.7951 | -122.2549 | 0.48981 | 0.0025177 | -0.010739 | -0.080719 | -0.0039883 | -0.027666 | -0.049954 | -0.04146 | 0.00094606 | -0.020108 | 0.057482 | 0.04968 | -0.21958 | -0.015992 | -0.021758 | -0.09613 | 0.11444 | -0.13733 | -0.11444 | 0.004578 | -0.11444 | -0.064087 | -23.4238 | 0.4715 | -122.2778 | 0.38452 | -121.7331 | -122.0993 | -121.6507 | 122.1176 | -0.37537 | -0.60425 | 122.2595 | 122.1909 | 122.1405 | 0.073242 | 0.022888 | -0.022888 | -0.01831 | -0.10529 | 0.52185 | 0.60425 | 0.15564 | 0.62714 | 0.17853 | 0.14191 | 0.022888 | 0.54474 | 122.6624 | 0.25177 | 122.7493 | 122.3694 | 122.7264 | -0.62714 | -122.7676 | 122.1405 | 122.6395 | 122.1588 | 98.8312
2047.7344 | 122.8363 | -122.2275 | 0.44403 | 0.0025177 | -0.0094571 | -0.077088 | -0.0059109 | -0.032793 | -0.048886 | -0.041033 | 0.00094606 | -0.020963 | 0.05855 | 0.044553 | -0.21979 | -0.014924 | -0.02133 | -0.054932 | 0.068665 | -0.082397 | -0.045776 | 0.1236 | -0.073242 | 0.013733 | -23.4375 | 0.43488 | -122.2595 | 0.40741 | -121.6965 | -122.0444 | -121.6049 | 122.1451 | -0.37537 | -0.48981 | 122.3511 | 122.2412 | 122.1542 | 0.09613 | 0.009155 | -0.032043 | -0.009156 | -0.036621 | 0.53101 | 0.62256 | 0.18311 | 0.6546 | 0.21515 | 0.20599 | 0.036621 | 0.56305 | 122.6669 | 0.15106 | 122.6944 | 122.2961 | 122.6624 | -0.52643 | -122.7036 | 122.1817 | 122.6349 | 122.1725 | 98.79
2049.4531 | 122.8912 | -122.2092 | 0.45776 | -0.012741 | -0.010739 | -0.075806 | -0.0052701 | -0.030016 | -0.048245 | -0.040178 | -0.0051575 | -0.020963 | 0.057909 | 0.038999 | -0.21915 | -0.016205 | -0.024962 | -0.041199 | 0.073242 | -0.07782 | -0.022888 | 0.10986 | -0.059509 | 0.013733 | -23.5199 | 0.44403 | -122.2549 | 0.4715 | -121.6644 | -122.0169 | -121.55 | 122.1313 | -0.38452 | -0.48065 | 122.319 | 122.2229 | 122.1497 | 0.091553 | 0.018311 | -0.045777 | -0.013733 | 0.013733 | 0.54474 | 0.65918 | 0.19226 | 0.70496 | 0.23804 | 0.18768 | 0.054932 | 0.59051 | 122.7264 | 0.15106 | 122.699 | 122.2824 | 122.6532 | -0.53558 | -122.7127 | 122.1863 | 122.6807 | 122.168 | 98.6893
2051.2188 | 122.8775 | -122.2321 | 0.45319 | 0.010147 | -0.013302 | -0.078583 | -0.0061245 | -0.032152 | -0.051022 | -0.043596 | -0.0051575 | -0.021817 | 0.058763 | 0.049894 | -0.22022 | -0.016846 | -0.021971 | -0.10071 | 0.082397 | -0.10071 | -0.059509 | 0.082397 | -0.064087 | 0.009155 | -23.6023 | 0.46692 | -122.3007 | 0.40741 | -121.669 | -122.0032 | -121.6049 | 122.1313 | -0.37079 | -0.5127 | 122.3145 | 122.2412 | 122.168 | 0.10986 | 0.036621 | -0.068664 | 0.013733 | -0.045776 | 0.56305 | 0.62714 | 0.22888 | 0.6958 | 0.29755 | 0.18311 | 0.041199 | 0.63171 | 122.7081 | 0.18311 | 122.7676 | 122.3145 | 122.699 | -0.55389 | -122.7539 | 122.1725 | 122.6395 | 122.1313 | 98.6298
2052.9531 | 122.8775 | -122.2412 | 0.44861 | 0.0025177 | -0.015438 | -0.078797 | -0.0086879 | -0.027239 | -0.051663 | -0.042528 | -0.0051575 | -0.019681 | 0.055986 | 0.049039 | -0.21958 | -0.014496 | -0.024321 | -0.032043 | 0.082397 | -0.09613 | -0.013733 | 0.16479 | 0 | 0.054932 | -23.5657 | 0.4303 | -122.2687 | 0.4303 | -121.6507 | -121.9803 | -121.5958 | 122.1451 | -0.36621 | -0.46234 | 122.406 | 122.2961 | 122.2412 | 0.15106 | 0.09613 | -0.027466 | -0.01831 | -0.01831 | 0.59052 | 0.64545 | 0.26093 | 0.67291 | 0.28839 | 0.26092 | 0.082397 | 0.61798 | 122.699 | 0.17853 | 122.699 | 122.3236 | 122.6715 | -0.54474 | -122.7173 | 122.2275 | 122.6715 | 122.2092 | 98.6755
2054.7344 | 122.8455 | -122.2412 | 0.42572 | -0.0051118 | -0.01202 | -0.076447 | -0.0050565 | -0.03322 | -0.048031 | -0.039751 | -0.0021057 | -0.022031 | 0.055773 | 0.060575 | -0.22001 | -0.015351 | -0.021758 | -0.050354 | 0.054932 | -0.068665 | -0.032043 | 0.12817 | -0.059509 | 0.004578 | -23.735 | 0.43488 | -122.3007 | 0.41199 | -121.7194 | -122.0444 | -121.6324 | 122.1725 | -0.37079 | -0.45776 | 122.3694 | 122.2458 | 122.1817 | 0.073243 | 0.009156 | -0.059509 | 0.009155 | -0.013733 | 0.52185 | 0.60883 | 0.19684 | 0.66833 | 0.25635 | 0.19684 | 0.036622 | 0.58136 | 122.7127 | 0.1236 | 122.7356 | 122.2961 | 122.6761 | -0.49438 | -122.7264 | 122.2092 | 122.6532 | 122.1909 | 98.5062
2056.5156 | 122.8546 | -122.2595 | 0.45776 | -0.0051118 | -0.014157 | -0.080292 | -0.0065517 | -0.034075 | -0.051663 | -0.044023 | -0.0021057 | -0.020536 | 0.0562 | 0.049039 | -0.22043 | -0.016205 | -0.023894 | -0.10986 | 0.09613 | -0.10986 | -0.091553 | 0.045776 | -0.10071 | -0.022888 | -23.8861 | 0.43488 | -122.3053 | 0.37537 | -121.7239 | -122.0581 | -121.637 | 122.1497 | -0.36163 | -0.54932 | 122.3053 | 122.2366 | 122.1588 | 0.086975 | 0.009155 | -0.045777 | -0.022889 | -0.082398 | 0.53558 | 0.62256 | 0.20142 | 0.66833 | 0.24719 | 0.15564 | 0.01831 | 0.58136 | 122.6807 | 0.20599 | 122.7402 | 122.3557 | 122.6944 | -0.56763 | -122.7631 | 122.168 | 122.6349 | 122.1497 | 98.3734
2058.2969 | 122.9004 | -122.2275 | 0.44403 | 0.0025177 | -0.015866 | -0.080506 | -0.0067653 | -0.029375 | -0.050381 | -0.041033 | -0.0051575 | -0.020322 | 0.057268 | 0.050107 | -0.21851 | -0.016633 | -0.020689 | -0.054932 | 0.091553 | -0.091553 | -0.045776 | 0.13733 | 0 | 0.050354 | -23.8724 | 0.43488 | -122.3145 | 0.44861 | -121.6599 | -121.9849 | -121.6003 | 122.1359 | -0.35248 | -0.48981 | 122.3648 | 122.2778 | 122.2275 | 0.14191 | 0.091553 | -0.086975 | -0.009156 | 0.004577 | 0.56763 | 0.62714 | 0.24262 | 0.71411 | 0.32959 | 0.22888 | 0.045777 | 0.6546 | 122.7631 | 0.18311 | 122.7493 | 122.319 | 122.6624 | -0.53558 | -122.7585 | 122.1817 | 122.6761 | 122.1725 | 98.3551
2060.0938 | 122.9004 | -122.2595 | 0.43945 | 0.0025177 | -0.012448 | -0.080506 | -0.0046291 | -0.032366 | -0.048886 | -0.038469 | -0.0082091 | -0.02139 | 0.055773 | 0.048398 | -0.2215 | -0.015992 | -0.025389 | -0.036621 | 0.068665 | -0.086975 | -0.013733 | 0.11902 | -0.068665 | 0.013733 | -23.941 | 0.4303 | -122.287 | 0.43488 | -121.6736 | -122.0352 | -121.582 | 122.1725 | -0.37079 | -0.45319 | 122.3785 | 122.2733 | 122.1909 | 0.10071 | 0.01831 | -0.027466 | -0.009155 | -0.004578 | 0.58594 | 0.67749 | 0.2243 | 0.70496 | 0.25177 | 0.20599 | 0.073242 | 0.6134 | 122.7219 | 0.15564 | 122.7173 | 122.3282 | 122.6898 | -0.52643 | -122.7264 | 122.2458 | 122.6944 | 122.2229 | 98.3185
2061.8125 | 122.7722 | -122.287 | 0.46692 | -0.0051118 | -0.0096707 | -0.07837 | -0.0012111 | -0.030443 | -0.048031 | -0.041246 | -0.0051575 | -0.017972 | 0.05855 | 0.043272 | -0.21937 | -0.015137 | -0.021544 | -0.11902 | 0.10986 | -0.14191 | -0.14648 | -0.027466 | -0.19684 | -0.10529 | -24.147 | 0.46234 | -122.3557 | 0.3067 | -121.8292 | -122.168 | -121.7148 | 122.1451 | -0.35706 | -0.6134 | 122.2595 | 122.1817 | 122.0901 | 0.036621 | -0.054931 | -0.068665 | -0.004578 | -0.16022 | 0.45776 | 0.5722 | 0.11902 | 0.64087 | 0.18768 | 0.11444 | -0.004577 | 0.52643 | 122.6624 | 0.25177 | 122.818 | 122.3969 | 122.7493 | -0.60883 | -122.8226 | 122.1405 | 122.5937 | 122.168 | 98.14
2063.5938 | 122.8683 | -122.2504 | 0.45319 | -0.0051118 | -0.016934 | -0.079651 | -0.0061245 | -0.03557 | -0.050595 | -0.040392 | -0.0021057 | -0.020963 | 0.056414 | 0.044767 | -0.21894 | -0.015565 | -0.020903 | -0.10986 | 0.068665 | -0.10529 | -0.07782 | 0.064087 | -0.082397 | -0.013733 | -24.202 | 0.43488 | -122.3282 | 0.37994 | -121.7148 | -122.0535 | -121.6461 | 122.1451 | -0.38452 | -0.53101 | 122.3145 | 122.2366 | 122.168 | 0.091553 | 0.022889 | -0.07782 | -0.018311 | -0.073242 | 0.53558 | 0.60425 | 0.19684 | 0.68207 | 0.27466 | 0.16937 | 0.027466 | 0.6134 | 122.7081 | 0.17395 | 122.7631 | 122.319 | 122.6852 | -0.55847 | -122.7814 | 122.1725 | 122.6303 | 122.1405 | 98.0484
2065.3906 | 122.7585 | -122.2824 | 0.47607 | -0.0051118 | -0.010098 | -0.076661 | -0.0037747 | -0.031084 | -0.050808 | -0.040605 | 0.00094606 | -0.018827 | 0.056841 | 0.048612 | -0.22022 | -0.015565 | -0.019621 | -0.11444 | 0.10986 | -0.12817 | -0.15106 | -0.054932 | -0.19226 | -0.09613 | -24.3622 | 0.45776 | -122.3053 | 0.30212 | -121.8338 | -122.2 | -121.7422 | 122.1542 | -0.36621 | -0.62714 | 122.2275 | 122.1863 | 122.0901 | 0.032044 | -0.064087 | -0.022888 | -0.01831 | -0.17395 | 0.44861 | 0.54016 | 0.082398 | 0.56305 | 0.10529 | 0.073242 | -0.022888 | 0.4715 | 122.6074 | 0.23804 | 122.7631 | 122.3923 | 122.7402 | -0.60425 | -122.7814 | 122.1313 | 122.5845 | 122.168 | 97.9202
2067.1719 | 122.8317 | -122.2733 | 0.45776 | -0.0051118 | -0.015011 | -0.080292 | -0.0061245 | -0.029162 | -0.048245 | -0.040819 | -0.0021057 | -0.022245 | 0.058977 | 0.052671 | -0.21915 | -0.016846 | -0.020476 | -0.082397 | 0.068665 | -0.09613 | -0.091553 | 0.059509 | -0.09613 | 0 | -24.4034 | 0.42114 | -122.3419 | 0.36621 | -121.7422 | -122.0856 | -121.669 | 122.1771 | -0.3891 | -0.54932 | 122.3328 | 122.2733 | 122.1771 | 0.09613 | 0 | -0.068665 | -0.036621 | -0.091553 | 0.531 | 0.60425 | 0.18768 | 0.67291 | 0.25635 | 0.15564 | 0.004577 | 0.59967 | 122.7081 | 0.16479 | 122.7631 | 122.3419 | 122.6944 | -0.55389 | -122.7997 | 122.1817 | 122.6395 | 122.1909 | 97.8699
2068.8906 | 122.8546 | -122.2595 | 0.45319 | -0.012741 | -0.01202 | -0.079865 | -0.0065517 | -0.030016 | -0.051449 | -0.041674 | -0.0021057 | -0.021817 | 0.054705 | 0.045835 | -0.21808 | -0.015778 | -0.027525 | -0.10071 | 0.082397 | -0.10986 | -0.082397 | 0.059509 | -0.073242 | 0.018311 | -24.4812 | 0.42114 | -122.3328 | 0.38452 | -121.7102 | -122.0398 | -121.637 | 122.1497 | -0.37079 | -0.53558 | 122.319 | 122.2778 | 122.1863 | 0.12817 | 0.036621 | -0.073243 | -0.032043 | -0.068665 | 0.54932 | 0.62256 | 0.21973 | 0.6958 | 0.29297 | 0.16937 | 0.027466 | 0.62256 | 122.7173 | 0.19226 | 122.7539 | 122.3419 | 122.6807 | -0.56305 | -122.7859 | 122.1771 | 122.644 | 122.1588 | 97.7783
2070.6719 | 122.8363 | -122.3007 | 0.4303 | 0.0025177 | -0.012234 | -0.07837 | -0.0039883 | -0.028521 | -0.050595 | -0.040178 | -0.0021057 | -0.018613 | 0.057482 | 0.044553 | -0.21894 | -0.015992 | -0.01898 | -0.10986 | 0.11444 | -0.12817 | -0.14191 | 0 | -0.16022 | -0.068665 | -24.6506 | 0.44403 | -122.3373 | 0.35706 | -121.7926 | -122.1222 | -121.6827 | 122.1725 | -0.31586 | -0.57221 | 122.3007 | 122.2321 | 122.1405 | 0.059509 | -0.032043 | -0.036621 | 0.013733 | -0.073242 | 0.50812 | 0.61798 | 0.17853 | 0.6546 | 0.21515 | 0.12817 | -0.013733 | 0.54474 | 122.6944 | 0.24262 | 122.7814 | 122.4152 | 122.7448 | -0.55847 | -122.7676 | 122.1588 | 122.6578 | 122.1909 | 97.6501
2072.4531 | 122.905 | -122.2733 | 0.3891 | -0.0051118 | -0.016079 | -0.079224 | -0.0069791 | -0.038775 | -0.051663 | -0.043169 | -0.0021057 | -0.019681 | 0.058977 | 0.048185 | -0.21915 | -0.016633 | -0.021971 | -0.091553 | 0.086975 | -0.082397 | -0.032043 | 0.12817 | -0.027466 | 0.036621 | -24.6414 | 0.39825 | -122.3465 | 0.38452 | -121.7102 | -122.049 | -121.6644 | 122.1909 | -0.30212 | -0.42114 | 122.4014 | 122.3099 | 122.2458 | 0.11902 | 0.054931 | -0.073243 | 0.009155 | -0.004578 | 0.56305 | 0.60882 | 0.2243 | 0.68207 | 0.29755 | 0.21057 | 0.050354 | 0.63629 | 122.731 | 0.16937 | 122.7448 | 122.3602 | 122.6715 | -0.4715 | -122.7356 | 122.2412 | 122.6578 | 122.1817 | 97.6318
2074.1719 | 122.7722 | -122.3328 | 0.41199 | 0.0025177 | -0.0081753 | -0.078583 | -0.0027065 | -0.028521 | -0.048245 | -0.042314 | 0.00094606 | -0.019681 | 0.058123 | 0.050107 | -0.22214 | -0.01471 | -0.021971 | -0.1236 | 0.11444 | -0.14191 | -0.16022 | -0.041199 | -0.18768 | -0.082397 | -24.884 | 0.43488 | -122.406 | 0.27466 | -121.8521 | -122.2275 | -121.7606 | 122.1909 | -0.29755 | -0.5722 | 122.2916 | 122.2504 | 122.1451 | 0.05951 | -0.045776 | -0.073242 | 0.022888 | -0.13733 | 0.48065 | 0.5722 | 0.10529 | 0.64545 | 0.17853 | 0.10071 | -0.01831 | 0.55389 | 122.6807 | 0.25635 | 122.8409 | 122.4472 | 122.7676 | -0.55389 | -122.818 | 122.1725 | 122.6074 | 122.2092 | 97.4487
2075.9688 | 122.905 | -122.2687 | 0.42572 | 0.0025177 | -0.015438 | -0.080292 | -0.0074063 | -0.034929 | -0.050808 | -0.041887 | -0.0082091 | -0.020749 | 0.058336 | 0.044767 | -0.2183 | -0.016846 | -0.023039 | -0.091553 | 0.068665 | -0.09613 | -0.054932 | 0.091553 | -0.054932 | 0.022888 | -24.8703 | 0.41199 | -122.3511 | 0.40283 | -121.6919 | -122.0261 | -121.6278 | 122.1725 | -0.35706 | -0.48065 | 122.3602 | 122.2916 | 122.2137 | 0.11902 | 0.041198 | -0.082397 | -0.013733 | -0.022888 | 0.57678 | 0.64087 | 0.24262 | 0.72327 | 0.32501 | 0.18768 | 0.041198 | 0.65918 | 122.7539 | 0.16479 | 122.7631 | 122.3373 | 122.6807 | -0.52185 | -122.7768 | 122.2137 | 122.6715 | 122.1771 | 97.3984
2077.75 | 122.8867 | -122.287 | 0.42114 | -0.012741 | -0.0098843 | -0.079865 | -0.0052701 | -0.028093 | -0.051876 | -0.041033 | -0.0021057 | -0.019681 | 0.056627 | 0.052885 | -0.21979 | -0.015565 | -0.024962 | -0.068665 | 0.082397 | -0.10071 | -0.027466 | 0.10529 | -0.068665 | 0.009155 | -24.9756 | 0.41199 | -122.3373 | 0.42114 | -121.7148 | -122.0627 | -121.6141 | 122.1863 | -0.33875 | -0.44861 | 122.3923 | 122.2961 | 122.2183 | 0.10986 | 0.032043 | -0.050354 | -0.009156 | 0 | 0.5722 | 0.67291 | 0.2243 | 0.72327 | 0.27466 | 0.20599 | 0.073242 | 0.62256 | 122.7585 | 0.18311 | 122.7493 | 122.3694 | 122.699 | -0.52185 | -122.7585 | 122.2595 | 122.7081 | 122.2183 | 97.3114
2079.5156 | 122.8683 | -122.2824 | 0.41657 | -0.012741 | -0.011593 | -0.080079 | -0.0080471 | -0.027666 | -0.049313 | -0.042955 | -0.0021057 | -0.022458 | 0.057482 | 0.048398 | -0.21958 | -0.017487 | -0.020689 | -0.091553 | 0.091553 | -0.091553 | -0.082397 | 0.073242 | -0.082397 | -0.009155 | -25.1358 | 0.40741 | -122.3602 | 0.35248 | -121.7468 | -122.1039 | -121.6919 | 122.1909 | -0.32501 | -0.49896 | 122.3557 | 122.2733 | 122.2 | 0.082398 | 0.009156 | -0.077819 | -0.009155 | -0.064087 | 0.53558 | 0.59051 | 0.17853 | 0.66833 | 0.25635 | 0.16479 | 0.009156 | 0.6134 | 122.7127 | 0.18311 | 122.7676 | 122.374 | 122.6898 | -0.50812 | -122.7768 | 122.2 | 122.6349 | 122.1909 | 97.1466
2081.3125 | 122.7722 | -122.319 | 0.44403 | -0.0051118 | -0.0098843 | -0.081574 | -0.0046291 | -0.030443 | -0.050381 | -0.042955 | -0.0021057 | -0.017331 | 0.057695 | 0.051389 | -0.22022 | -0.014924 | -0.024107 | -0.1236 | 0.10071 | -0.12817 | -0.15106 | -0.041199 | -0.19226 | -0.09613 | -25.2548 | 0.4303 | -122.3877 | 0.28381 | -121.843 | -122.2046 | -121.7606 | 122.1909 | -0.34332 | -0.59509 | 122.2778 | 122.2229 | 122.1268 | 0.032044 | -0.064087 | -0.068664 | -0.013733 | -0.16022 | 0.47607 | 0.55847 | 0.11444 | 0.62714 | 0.1831 | 0.086975 | -0.022888 | 0.54474 | 122.6715 | 0.22888 | 122.818 | 122.4197 | 122.7493 | -0.57221 | -122.8317 | 122.168 | 122.6028 | 122.1954 | 97.0642
2083.0938 | 122.8226 | -122.3145 | 0.43488 | 0.0025177 | -0.013943 | -0.080079 | -0.0071927 | -0.025957 | -0.048458 | -0.041033 | -0.0021057 | -0.019681 | 0.057909 | 0.050107 | -0.2183 | -0.016205 | -0.022185 | -0.07782 | 0.10529 | -0.12817 | -0.10071 | 0.036621 | -0.10071 | -0.045776 | -25.1999 | 0.43488 | -122.3785 | 0.33875 | -121.7789 | -122.1405 | -121.7194 | 122.1863 | -0.32959 | -0.53558 | 122.3511 | 122.2687 | 122.2137 | 0.082398 | 0.027466 | -0.064087 | 0 | -0.09613 | 0.53558 | 0.59509 | 0.17395 | 0.65918 | 0.23804 | 0.1648 | 0.027466 | 0.59967 | 122.7173 | 0.23346 | 122.8134 | 122.4197 | 122.7493 | -0.56305 | -122.8134 | 122.2137 | 122.6532 | 122.2366 | 97.1146
2084.8125 | 122.8363 | -122.4792 | 0.27924 | -0.0051118 | -0.012875 | -0.077088 | -0.0042019 | -0.028948 | -0.050808 | -0.04146 | -0.0021057 | -0.01904 | 0.057482 | 0.045408 | -0.21937 | -0.013856 | -0.023467 | -0.082397 | 0.09613 | -0.10986 | -0.082397 | 0.064087 | -0.10529 | -0.036621 | -25.2777 | 0.27008 | -122.5159 | 0.16937 | -121.9666 | -122.3145 | -121.8933 | 122.3694 | -0.18311 | -0.36163 | 122.5433 | 122.4426 | 122.374 | 0.073242 | 0.004577 | -0.036621 | -0.009155 | -0.10986 | 0.51269 | 0.58594 | 0.16479 | 0.62256 | 0.20142 | 0.17395 | 0.027466 | 0.54932 | 122.6852 | 0.20599 | 122.7859 | 122.5754 | 122.7493 | -0.3891 | -122.7951 | 122.3969 | 122.6486 | 122.3969 | 97.2015
2086.5938 | 122.8958 | -122.4655 | 0.2243 | -0.0051118 | -0.0086027 | -0.07837 | -0.0059109 | -0.03023 | -0.048245 | -0.038256 | -0.0021057 | -0.018613 | 0.056627 | 0.048185 | -0.21937 | -0.014283 | -0.022398 | -0.09613 | 0.11444 | -0.11444 | -0.082397 | 0.045776 | -0.12817 | -0.032043 | -25.3647 | 0.22888 | -122.5296 | 0.21057 | -121.9162 | -122.2595 | -121.8155 | 122.3511 | -0.10986 | -0.3067 | 122.5113 | 122.4335 | 122.3373 | 0.082398 | -0.013733 | -0.064087 | 0.004578 | -0.013733 | 0.54932 | 0.65002 | 0.20599 | 0.71411 | 0.27008 | 0.16022 | 0.032044 | 0.6134 | 122.7402 | 0.22888 | 122.7585 | 122.58 | 122.6944 | -0.33875 | -122.7539 | 122.3831 | 122.6761 | 122.3694 | 97.1008
2088.375 | 122.8271 | -122.3145 | 0.41657 | -0.0051118 | -0.010098 | -0.079224 | -0.0054837 | -0.032366 | -0.050167 | -0.040392 | 0.00094606 | -0.019467 | 0.057268 | 0.047544 | -0.21787 | -0.014924 | -0.02133 | -0.1236 | 0.10986 | -0.13733 | -0.14648 | 0 | -0.16479 | -0.091553 | -25.4929 | 0.41657 | -122.3831 | 0.32044 | -121.8109 | -122.1863 | -121.7239 | 122.1771 | -0.3067 | -0.56305 | 122.3145 | 122.2229 | 122.1497 | 0.045776 | -0.027466 | -0.068665 | 0 | -0.09613 | 0.50354 | 0.59051 | 0.12817 | 0.65918 | 0.19684 | 0.13733 | -0.009155 | 0.5722 | 122.7036 | 0.24719 | 122.7997 | 122.4243 | 122.731 | -0.55389 | -122.7997 | 122.168 | 122.6349 | 122.1909 | 96.8216
2090.1719 | 122.7631 | -122.3419 | 0.4303 | 0.010147 | -0.010952 | -0.077088 | -0.0048427 | -0.030657 | -0.050167 | -0.038683 | 0.00094606 | -0.019467 | 0.057482 | 0.043912 | -0.21659 | -0.014069 | -0.020903 | -0.10071 | 0.11902 | -0.11444 | -0.14191 | 0.004578 | -0.16937 | -0.09613 | -25.5524 | 0.42114 | -122.3877 | 0.27466 | -121.8521 | -122.2412 | -121.756 | 122.2275 | -0.31128 | -0.57221 | 122.3465 | 122.2458 | 122.1725 | 0.018311 | -0.054932 | -0.045776 | -0.009155 | -0.15564 | 0.48981 | 0.58594 | 0.10071 | 0.63171 | 0.14648 | 0.11902 | -0.027466 | 0.53558 | 122.6624 | 0.23346 | 122.8088 | 122.4609 | 122.7631 | -0.54474 | -122.818 | 122.2 | 122.6166 | 122.2412 | 96.7896
2091.9062 | 122.8271 | -122.438 | 0.32959 | -0.012741 | -0.012448 | -0.079011 | -0.0048427 | -0.031939 | -0.049526 | -0.038896 | 0.00094606 | -0.018613 | 0.05855 | 0.047758 | -0.21958 | -0.013642 | -0.022185 | -0.10071 | 0.11902 | -0.13275 | -0.12817 | 0.022888 | -0.10529 | -0.050354 | -25.6302 | 0.32501 | -122.4792 | 0.21515 | -121.8887 | -122.2687 | -121.8155 | 122.3053 | -0.21057 | -0.45776 | 122.4609 | 122.3877 | 122.3328 | 0.082397 | 0.027465 | -0.041199 | -0.004578 | -0.11444 | 0.54932 | 0.62256 | 0.16937 | 0.66376 | 0.21057 | 0.15564 | 0.004577 | 0.59051 | 122.6944 | 0.25177 | 122.8043 | 122.5571 | 122.7631 | -0.46234 | -122.8088 | 122.3099 | 122.6532 | 122.3373 | 96.8079
2093.6875 | 122.9141 | -122.2961 | 0.3891 | -0.012741 | -0.015866 | -0.080506 | -0.0067653 | -0.030871 | -0.053585 | -0.042528 | 0.0070497 | -0.022031 | 0.057268 | 0.040067 | -0.21787 | -0.016205 | -0.019194 | -0.068665 | 0.059509 | -0.10071 | -0.036621 | 0.14648 | -0.009155 | 0.054932 | -25.6348 | 0.37994 | -122.3511 | 0.38452 | -121.7056 | -122.0535 | -121.6461 | 122.1954 | -0.32959 | -0.42572 | 122.4426 | 122.3511 | 122.287 | 0.15564 | 0.091553 | -0.054931 | -0.009155 | -0.004578 | 0.59052 | 0.65002 | 0.24262 | 0.70496 | 0.29755 | 0.24719 | 0.064087 | 0.64545 | 122.7356 | 0.16022 | 122.731 | 122.3557 | 122.6761 | -0.48981 | -122.7402 | 122.2595 | 122.6807 | 122.2275 | 96.6614
2095.4688 | 122.9004 | -122.2961 | 0.3891 | 0.0025177 | -0.010311 | -0.079224 | -0.0069791 | -0.02788 | -0.04739 | -0.040392 | 0.0039979 | -0.018613 | 0.058977 | 0.047544 | -0.21915 | -0.015992 | -0.019621 | -0.018311 | 0.059509 | -0.09613 | -0.027466 | 0.1236 | -0.068665 | 0.032043 | -25.7309 | 0.36163 | -122.3602 | 0.40741 | -121.7194 | -122.0947 | -121.637 | 122.2 | -0.32959 | -0.41656 | 122.4197 | 122.3282 | 122.2275 | 0.12817 | 0.027465 | -0.064086 | -0.027466 | 0.018311 | 0.57678 | 0.65918 | 0.20142 | 0.72327 | 0.2655 | 0.21973 | 0.068664 | 0.64087 | 122.7676 | 0.15564 | 122.7219 | 122.3557 | 122.6578 | -0.48523 | -122.7493 | 122.2687 | 122.7036 | 122.2778 | 96.5652
2097.25 | 122.8638 | -122.3465 | 0.40283 | -0.0051118 | -0.015652 | -0.077515 | -0.0080471 | -0.029375 | -0.051235 | -0.042101 | -0.0082091 | -0.020749 | 0.057482 | 0.044126 | -0.21851 | -0.015992 | -0.020689 | -0.10986 | 0.10071 | -0.09613 | -0.082397 | 0.073242 | -0.091553 | -0.009155 | -25.9277 | 0.39825 | -122.3969 | 0.31128 | -121.7972 | -122.1359 | -121.701 | 122.2504 | -0.30212 | -0.48523 | 122.4197 | 122.3373 | 122.2549 | 0.086975 | 0.004577 | -0.050354 | -0.004578 | -0.091553 | 0.54932 | 0.64545 | 0.21057 | 0.6958 | 0.26093 | 0.16937 | 0.013733 | 0.59967 | 122.7081 | 0.19684 | 122.7951 | 122.4472 | 122.7448 | -0.49896 | -122.7997 | 122.2641 | 122.6578 | 122.2366 | 96.4188
2098.9844 | 122.7814 | -122.3923 | 0.39368 | 0.0025177 | -0.014798 | -0.080933 | -0.0065517 | -0.030871 | -0.052731 | -0.039324 | 0.00094606 | -0.020749 | 0.057909 | 0.048826 | -0.21979 | -0.016419 | -0.028807 | -0.10071 | 0.091553 | -0.12817 | -0.12817 | 0.027466 | -0.12817 | -0.050354 | -26.0559 | 0.40283 | -122.4106 | 0.23346 | -121.8613 | -122.2229 | -121.8155 | 122.2641 | -0.30212 | -0.52185 | 122.4197 | 122.3419 | 122.2641 | 0.07782 | 0 | -0.01831 | 0.009155 | -0.16022 | 0.53101 | 0.57678 | 0.16937 | 0.59509 | 0.18768 | 0.15564 | 0 | 0.54932 | 122.644 | 0.21973 | 122.8134 | 122.4838 | 122.7951 | -0.52185 | -122.8043 | 122.2641 | 122.6257 | 122.2916 | 96.3364
2100.7812 | 122.7951 | -122.4655 | 0.32044 | -0.0051118 | -0.010952 | -0.077302 | -0.00078392 | -0.03258 | -0.051022 | -0.039751 | -0.0021057 | -0.017972 | 0.059404 | 0.051176 | -0.2215 | -0.014283 | -0.025389 | -0.082397 | 0.10071 | -0.10071 | -0.10071 | 0.041199 | -0.13733 | -0.064087 | -26.1291 | 0.29755 | -122.493 | 0.17395 | -121.9666 | -122.3236 | -121.875 | 122.3648 | -0.21973 | -0.42114 | 122.5067 | 122.4014 | 122.3282 | 0.036621 | -0.036621 | -0.027466 | -0.022889 | -0.14649 | 0.49896 | 0.59051 | 0.14191 | 0.61798 | 0.16937 | 0.14191 | 0 | 0.52643 | 122.6669 | 0.20142 | 122.7905 | 122.5662 | 122.7631 | -0.42114 | -122.8134 | 122.3648 | 122.6395 | 122.3831 | 96.3364
2102.5625 | 122.818 | -122.5113 | 0.27466 | -0.012741 | -0.013089 | -0.081147 | -0.0061245 | -0.035143 | -0.05209 | -0.040392 | -0.0021057 | -0.016904 | 0.05855 | 0.047117 | -0.21894 | -0.01471 | -0.025603 | -0.13733 | 0.10529 | -0.15106 | -0.14648 | -0.022888 | -0.12817 | -0.073242 | -26.2894 | 0.26093 | -122.5983 | 0.10529 | -121.9894 | -122.3557 | -121.9345 | 122.3602 | -0.16937 | -0.42114 | 122.4884 | 122.4381 | 122.3831 | 0.07782 | 0.022888 | -0.086975 | -0.013733 | -0.16937 | 0.52185 | 0.57678 | 0.15564 | 0.66376 | 0.24262 | 0.12817 | 0.004578 | 0.60883 | 122.7036 | 0.25635 | 122.8592 | 122.6166 | 122.7722 | -0.42572 | -122.8729 | 122.3648 | 122.6166 | 122.374 | 96.2219
2104.2812 | 122.9233 | -122.4289 | 0.27924 | -0.012741 | -0.011593 | -0.079651 | -0.0076199 | -0.033648 | -0.048886 | -0.042742 | -0.0021057 | -0.020749 | 0.056414 | 0.043485 | -0.2183 | -0.016846 | -0.023467 | -0.050354 | 0.064087 | -0.09613 | -0.018311 | 0.15106 | -0.004578 | 0.054932 | -26.2115 | 0.24719 | -122.5296 | 0.24261 | -121.8338 | -122.1863 | -121.788 | 122.3328 | -0.21515 | -0.29755 | 122.58 | 122.4838 | 122.4243 | 0.15106 | 0.091552 | -0.10071 | -0.032044 | -0.036621 | 0.59509 | 0.64087 | 0.24262 | 0.74158 | 0.34332 | 0.24719 | 0.077819 | 0.6958 | 122.7722 | 0.16022 | 122.7768 | 122.493 | 122.6761 | -0.37537 | -122.8088 | 122.4106 | 122.6715 | 122.3785 | 96.2173
2106.0781 | 122.8592 | -122.3969 | 0.32501 | -0.0051118 | -0.013729 | -0.077302 | -0.0091153 | -0.030016 | -0.049954 | -0.040178 | -0.0021057 | -0.021176 | 0.059191 | 0.041349 | -0.21894 | -0.017273 | -0.024107 | -0.091553 | 0.086975 | -0.12817 | -0.091553 | 0.041199 | -0.091553 | -0.022888 | -26.4221 | 0.3067 | -122.4472 | 0.24719 | -121.8475 | -122.2137 | -121.7789 | 122.2687 | -0.23804 | -0.41657 | 122.4381 | 122.374 | 122.3053 | 0.10529 | 0.036621 | -0.050354 | -0.01831 | -0.07782 | 0.54932 | 0.61798 | 0.18311 | 0.66833 | 0.23346 | 0.16937 | 0.036621 | 0.59967 | 122.6944 | 0.21515 | 122.7539 | 122.4838 | 122.7036 | -0.45319 | -122.7722 | 122.3053 | 122.644 | 122.3053 | 95.9747
2107.8594 | 122.7859 | -122.5571 | 0.25177 | 0.0025177 | -0.015225 | -0.082428 | -0.0042019 | -0.02788 | -0.050595 | -0.040819 | 0.0039979 | -0.019467 | 0.057695 | 0.049039 | -0.21958 | -0.01706 | -0.02603 | -0.1236 | 0.10071 | -0.1236 | -0.14191 | 0.004578 | -0.1236 | -0.045776 | -26.6006 | 0.26093 | -122.5662 | 0.07782 | -121.9986 | -122.3648 | -121.9528 | 122.4335 | -0.15106 | -0.39368 | 122.5616 | 122.5113 | 122.4335 | 0.07782 | 0 | -0.009155 | 0.009155 | -0.17395 | 0.55847 | 0.60425 | 0.19226 | 0.6134 | 0.20142 | 0.12817 | -0.018311 | 0.56763 | 122.644 | 0.2243 | 122.8271 | 122.6578 | 122.818 | -0.37537 | -122.818 | 122.4152 | 122.6349 | 122.4335 | 95.9564
2109.6406 | 122.8638 | -122.3969 | 0.3479 | -0.0051118 | -0.01138 | -0.077515 | -0.0059109 | -0.033007 | -0.051022 | -0.043596 | -0.0021057 | -0.019681 | 0.058336 | 0.044126 | -0.22022 | -0.01706 | -0.024748 | -0.086975 | 0.09613 | -0.091553 | -0.068665 | 0.059509 | -0.10986 | -0.009155 | -26.6556 | 0.32044 | -122.4426 | 0.27008 | -121.8384 | -122.1909 | -121.7697 | 122.3053 | -0.25177 | -0.41656 | 122.4564 | 122.3877 | 122.287 | 0.082398 | -0.01831 | -0.045776 | -0.027465 | -0.077819 | 0.55847 | 0.62714 | 0.20599 | 0.67291 | 0.25177 | 0.15106 | 0.022888 | 0.60425 | 122.7127 | 0.18768 | 122.7631 | 122.493 | 122.7173 | -0.43945 | -122.7905 | 122.3282 | 122.6669 | 122.3099 | 95.7413
2111.4219 | 122.9141 | -122.4792 | 0.21057 | -0.0051118 | -0.0092435 | -0.081147 | -0.0048427 | -0.028734 | -0.048458 | -0.04146 | 0.0039979 | -0.020749 | 0.057054 | 0.045408 | -0.22022 | -0.01706 | -0.023894 | -0.022888 | 0.064087 | -0.091553 | -0.018311 | 0.11444 | -0.064087 | 0.022888 | -26.7014 | 0.19226 | -122.5708 | 0.2243 | -121.8979 | -122.2733 | -121.8201 | 122.3877 | -0.14648 | -0.22888 | 122.5937 | 122.5021 | 122.4152 | 0.11444 | 0.027466 | -0.091553 | -0.01831 | 0.013733 | 0.58136 | 0.65918 | 0.20599 | 0.75073 | 0.29755 | 0.20599 | 0.073242 | 0.67291 | 122.7951 | 0.15564 | 122.7631 | 122.5433 | 122.6715 | -0.30212 | -122.7814 | 122.4609 | 122.7036 | 122.4564 | 95.7779
2113.2031 | 122.9187 | -122.3923 | 0.28839 | -0.0051118 | -0.010311 | -0.078797 | -0.0056973 | -0.025316 | -0.049313 | -0.042528 | -0.0021057 | -0.020536 | 0.057909 | 0.04199 | -0.21958 | -0.01471 | -0.023894 | -0.082397 | 0.091553 | -0.10071 | -0.045776 | 0.09613 | -0.059509 | -0.009155 | -26.8433 | 0.28839 | -122.4564 | 0.30212 | -121.8246 | -122.2 | -121.7514 | 122.2916 | -0.19684 | -0.33417 | 122.4884 | 122.3831 | 122.3328 | 0.091553 | 0.041199 | -0.064087 | 0 | 0.013733 | 0.56763 | 0.64087 | 0.19226 | 0.70496 | 0.25635 | 0.19684 | 0.054932 | 0.63171 | 122.7585 | 0.19226 | 122.7448 | 122.4838 | 122.6807 | -0.3891 | -122.7448 | 122.3465 | 122.6944 | 122.3099 | 95.549
2114.9844 | 122.7722 | -122.5204 | 0.25177 | -0.0051118 | -0.012661 | -0.077302 | -0.0037747 | -0.025744 | -0.054013 | -0.042528 | -0.0051575 | -0.019681 | 0.055773 | 0.049253 | -0.22022 | -0.015351 | -0.024107 | -0.10529 | 0.10529 | -0.13733 | -0.16022 | -0.054932 | -0.20599 | -0.11444 | -27.1317 | 0.24261 | -122.5754 | 0.091553 | -122.0718 | -122.4747 | -121.9894 | 122.3831 | -0.14648 | -0.41199 | 122.4655 | 122.406 | 122.3145 | 0.022888 | -0.068665 | -0.054931 | -0.009155 | -0.16022 | 0.44861 | 0.53101 | 0.045777 | 0.58594 | 0.10071 | 0.082397 | -0.022888 | 0.50354 | 122.6669 | 0.24262 | 122.818 | 122.6257 | 122.7631 | -0.3891 | -122.8271 | 122.3602 | 122.612 | 122.4152 | 95.3888
2116.7656 | 122.9141 | -122.4884 | 0.23804 | -0.0051118 | -0.015011 | -0.07837 | -0.0069791 | -0.029802 | -0.050808 | -0.044023 | -0.0051575 | -0.020108 | 0.054705 | 0.041349 | -0.21958 | -0.015778 | -0.026457 | -0.059509 | 0.068665 | -0.10529 | -0.018311 | 0.17853 | 0.013733 | 0.068665 | -27.063 | 0.2243 | -122.5296 | 0.23346 | -121.8292 | -122.2092 | -121.8155 | 122.3831 | -0.16937 | -0.25635 | 122.6669 | 122.5571 | 122.5021 | 0.17395 | 0.11902 | -0.041199 | -0.013733 | -0.004578 | 0.65918 | 0.67291 | 0.27924 | 0.71411 | 0.32044 | 0.28381 | 0.086975 | 0.70038 | 122.7631 | 0.17395 | 122.7539 | 122.5571 | 122.7127 | -0.34332 | -122.7676 | 122.4701 | 122.7219 | 122.4289 | 95.4254
2118.5469 | 122.85 | -122.4838 | 0.23346 | -0.012741 | -0.012661 | -0.077942 | -0.0078335 | -0.02788 | -0.050167 | -0.041246 | -0.0021057 | -0.020536 | 0.054064 | 0.048185 | -0.2183 | -0.016205 | -0.022185 | -0.10071 | 0.073242 | -0.091553 | -0.091553 | 0.036621 | -0.10529 | -0.013733 | -27.3239 | 0.24261 | -122.5433 | 0.16479 | -121.9299 | -122.3099 | -121.8613 | 122.3923 | -0.16022 | -0.32501 | 122.5204 | 122.4701 | 122.3785 | 0.07782 | -0.013733 | -0.059509 | 0.009156 | -0.068664 | 0.55389 | 0.62256 | 0.17395 | 0.68207 | 0.23346 | 0.12817 | 0 | 0.6134 | 122.7081 | 0.16479 | 122.7859 | 122.5571 | 122.7264 | -0.32501 | -122.7768 | 122.3923 | 122.6486 | 122.3831 | 95.1599
2120.2656 | 122.8683 | -122.4792 | 0.22888 | -0.0051118 | -0.012234 | -0.077942 | -0.0080471 | -0.033861 | -0.050381 | -0.042101 | 0.00094606 | -0.020963 | 0.055773 | 0.039213 | -0.21872 | -0.015778 | -0.022398 | -0.082397 | 0.054932 | -0.09613 | -0.068665 | 0.082397 | -0.07782 | 0 | -27.4475 | 0.23804 | -122.5708 | 0.16022 | -121.9391 | -122.3007 | -121.8842 | 122.3831 | -0.17395 | -0.29755 | 122.5616 | 122.4792 | 122.4014 | 0.09613 | 0.01831 | -0.091553 | 0.009155 | -0.068665 | 0.54016 | 0.59509 | 0.17853 | 0.68665 | 0.27008 | 0.17853 | 0.027465 | 0.63171 | 122.731 | 0.15106 | 122.8088 | 122.5342 | 122.7173 | -0.32501 | -122.7997 | 122.4106 | 122.6395 | 122.3969 | 95.0317
2122.0469 | 122.9095 | -122.4106 | 0.27008 | 0.0025177 | -0.011166 | -0.081574 | -0.0063381 | -0.029375 | -0.050381 | -0.039537 | -0.0021057 | -0.020963 | 0.055132 | 0.050321 | -0.21915 | -0.014924 | -0.024962 | -0.086975 | 0.073242 | -0.09613 | -0.036621 | 0.091553 | -0.068665 | 0 | -27.5162 | 0.29755 | -122.5021 | 0.28839 | -121.843 | -122.2183 | -121.7514 | 122.3145 | -0.19684 | -0.3067 | 122.5021 | 122.4106 | 122.3419 | 0.09613 | 0.027465 | -0.091553 | 0.027465 | 0.01831 | 0.56763 | 0.65918 | 0.19226 | 0.75073 | 0.28381 | 0.18768 | 0.059509 | 0.65918 | 122.7905 | 0.16937 | 122.7997 | 122.4838 | 122.7081 | -0.36621 | -122.7722 | 122.374 | 122.699 | 122.3236 | 94.8944
2123.8281 | 122.7722 | -122.4289 | 0.37079 | -0.0051118 | -0.012875 | -0.077088 | -0.0042019 | -0.028948 | -0.048458 | -0.040819 | -0.0051575 | -0.017545 | 0.057268 | 0.050107 | -0.21937 | -0.015565 | -0.02603 | -0.10529 | 0.091553 | -0.12817 | -0.16937 | -0.050354 | -0.20142 | -0.10986 | -27.8046 | 0.36621 | -122.4792 | 0.19226 | -121.9437 | -122.3328 | -121.8475 | 122.3007 | -0.27924 | -0.54016 | 122.3785 | 122.319 | 122.2275 | 0.018311 | -0.073242 | -0.050354 | -0.004578 | -0.17853 | 0.48523 | 0.58136 | 0.09613 | 0.63171 | 0.14648 | 0.07782 | -0.041199 | 0.53558 | 122.6715 | 0.21973 | 122.8455 | 122.5204 | 122.7951 | -0.49896 | -122.85 | 122.2595 | 122.6212 | 122.3236 | 94.6243
2125.5625 | 122.8226 | -122.3831 | 0.37994 | -0.0051118 | -0.013943 | -0.078797 | -0.0044155 | -0.028948 | -0.050167 | -0.043383 | -0.0021057 | -0.018186 | 0.058123 | 0.046262 | -0.21702 | -0.015137 | -0.021117 | -0.10529 | 0.10986 | -0.14648 | -0.12817 | -0.022888 | -0.12817 | -0.068665 | -27.8229 | 0.3891 | -122.4426 | 0.25177 | -121.8201 | -122.2366 | -121.7697 | 122.2366 | -0.27008 | -0.50812 | 122.3602 | 122.3145 | 122.2549 | 0.077819 | 0.01831 | -0.059509 | 0.009155 | -0.12817 | 0.56305 | 0.6134 | 0.14648 | 0.67291 | 0.20599 | 0.1236 | 0.01831 | 0.62256 | 122.6944 | 0.25635 | 122.8317 | 122.493 | 122.7722 | -0.52643 | -122.8226 | 122.2549 | 122.6349 | 122.2778 | 94.5602
2127.3281 | 122.8409 | -122.3694 | 0.39368 | -0.0051118 | -0.011166 | -0.077088 | -0.0042019 | -0.034929 | -0.049313 | -0.040605 | 0.00094606 | -0.017118 | 0.056627 | 0.052885 | -0.21894 | -0.01471 | -0.02133 | -0.086975 | 0.10529 | -0.10529 | -0.073242 | 0.059509 | -0.09613 | -0.054932 | -27.951 | 0.37079 | -122.4243 | 0.27924 | -121.8201 | -122.2229 | -121.7743 | 122.2641 | -0.28839 | -0.46692 | 122.4289 | 122.3145 | 122.2733 | 0.050354 | 0.009156 | -0.054931 | -0.022888 | -0.11444 | 0.54932 | 0.59509 | 0.14648 | 0.65002 | 0.20142 | 0.16479 | 0.032044 | 0.60425 | 122.7036 | 0.21057 | 122.7951 | 122.4747 | 122.7402 | -0.49896 | -122.818 | 122.2961 | 122.6486 | 122.2824 | 94.4183
2129.1094 | 122.9416 | -122.3373 | 0.36163 | 0.0025177 | -0.015011 | -0.080292 | -0.0091153 | -0.031511 | -0.048886 | -0.038896 | -0.0051575 | -0.021604 | 0.055773 | 0.041135 | -0.2183 | -0.01706 | -0.020262 | -0.073242 | 0.091553 | -0.09613 | -0.032043 | 0.17395 | -0.009155 | 0.050354 | -28.0746 | 0.3479 | -122.4014 | 0.36163 | -121.7102 | -122.1085 | -121.6873 | 122.2412 | -0.27008 | -0.39368 | 122.5113 | 122.3877 | 122.3282 | 0.14648 | 0.086975 | -0.064087 | -0.013733 | 0 | 0.62714 | 0.65002 | 0.22888 | 0.71411 | 0.29297 | 0.27008 | 0.064087 | 0.69122 | 122.7631 | 0.18768 | 122.7493 | 122.4289 | 122.6852 | -0.45776 | -122.7631 | 122.3053 | 122.699 | 122.2641 | 94.2627
2130.8906 | 122.8043 | -122.4655 | 0.3067 | 0.010147 | -0.016293 | -0.080506 | -0.0074063 | -0.030016 | -0.051022 | -0.042314 | 0.00094606 | -0.018613 | 0.055773 | 0.048398 | -0.22065 | -0.016846 | -0.025816 | -0.064087 | 0.082397 | -0.091553 | -0.068665 | 0.10071 | -0.045776 | 0.009155 | -28.3127 | 0.30212 | -122.5021 | 0.17853 | -121.8796 | -122.2687 | -121.8567 | 122.374 | -0.2243 | -0.37537 | 122.5662 | 122.4747 | 122.4197 | 0.10071 | 0.045777 | -0.036621 | -0.004578 | -0.12817 | 0.58594 | 0.60883 | 0.19684 | 0.64545 | 0.23346 | 0.19226 | 0.022888 | 0.62256 | 122.6807 | 0.17395 | 122.8043 | 122.5479 | 122.7676 | -0.39825 | -122.8088 | 122.3969 | 122.644 | 122.4014 | 94.1528
2132.6094 | 122.8317 | -122.3831 | 0.39368 | -0.012741 | -0.013516 | -0.079224 | -0.0080471 | -0.027453 | -0.050381 | -0.040392 | -0.0021057 | -0.01904 | 0.055132 | 0.049039 | -0.21958 | -0.018128 | -0.023039 | -0.054932 | 0.082397 | -0.073242 | -0.059509 | 0.10529 | -0.045776 | 0.013733 | -28.4409 | 0.35706 | -122.4335 | 0.2655 | -121.8201 | -122.1863 | -121.788 | 122.3099 | -0.31128 | -0.45319 | 122.4884 | 122.3969 | 122.3373 | 0.086975 | 0.027466 | -0.050354 | -0.036621 | -0.12817 | 0.56305 | 0.59509 | 0.19684 | 0.64545 | 0.24719 | 0.17853 | 0.013733 | 0.6134 | 122.699 | 0.15564 | 122.7905 | 122.4655 | 122.7402 | -0.46692 | -122.8271 | 122.3236 | 122.6486 | 122.3282 | 93.9423
2134.375 | 122.7997 | -122.4014 | 0.40283 | 0.017777 | -0.013302 | -0.082856 | -0.0074063 | -0.031939 | -0.051235 | -0.040392 | -0.0021057 | -0.01669 | 0.057695 | 0.056943 | -0.21894 | -0.017273 | -0.02368 | -0.1236 | 0.082397 | -0.11902 | -0.14191 | -0.004578 | -0.12817 | -0.073242 | -28.6972 | 0.38452 | -122.4792 | 0.21515 | -121.875 | -122.2549 | -121.8475 | 122.2824 | -0.32044 | -0.54474 | 122.3969 | 122.3282 | 122.2733 | 0.045777 | -0.009155 | -0.07782 | -0.018311 | -0.18768 | 0.52643 | 0.55389 | 0.14648 | 0.63171 | 0.2243 | 0.11444 | -0.022888 | 0.60425 | 122.6944 | 0.20142 | 122.8638 | 122.4838 | 122.7859 | -0.52185 | -122.8821 | 122.2595 | 122.6166 | 122.2778 | 93.7042
2136.0938 | 122.937 | -122.3465 | 0.3479 | 0.0025177 | -0.015011 | -0.082001 | -0.0056973 | -0.033861 | -0.051449 | -0.041887 | -0.0021057 | -0.022458 | 0.059618 | 0.042631 | -0.21872 | -0.017701 | -0.019835 | -0.054932 | 0.068665 | -0.10986 | -0.041199 | 0.14648 | -0.004578 | 0.045776 | -28.7155 | 0.33875 | -122.4289 | 0.3479 | -121.7194 | -122.1039 | -121.7194 | 122.2366 | -0.27924 | -0.3891 | 122.493 | 122.3923 | 122.3419 | 0.15564 | 0.10529 | -0.082397 | -0.009155 | 0 | 0.62714 | 0.62714 | 0.24262 | 0.70953 | 0.32501 | 0.25635 | 0.068664 | 0.70953 | 122.7768 | 0.17853 | 122.7676 | 122.4152 | 122.6852 | -0.45776 | -122.7768 | 122.3053 | 122.6944 | 122.2916 | 93.631
2137.875 | 122.85 | -122.406 | 0.37079 | -0.0051118 | -0.010525 | -0.079224 | -0.0046291 | -0.027453 | -0.050381 | -0.040605 | 0.00094606 | -0.019254 | 0.057695 | 0.045621 | -0.21979 | -0.016633 | -0.021971 | -0.07782 | 0.09613 | -0.11902 | -0.086975 | 0.045776 | -0.10529 | -0.041199 | -28.9764 | 0.37537 | -122.438 | 0.27466 | -121.8246 | -122.2092 | -121.7834 | 122.287 | -0.27466 | -0.45776 | 122.4518 | 122.3648 | 122.3007 | 0.07782 | 0.013733 | -0.032043 | 0.004577 | -0.096131 | 0.58136 | 0.62256 | 0.19684 | 0.6546 | 0.22888 | 0.16479 | 0.032044 | 0.6134 | 122.7127 | 0.21515 | 122.8134 | 122.5021 | 122.7814 | -0.48981 | -122.8088 | 122.319 | 122.6807 | 122.3282 | 93.4296
2139.5938 | 122.9279 | -122.3511 | 0.35706 | 0.0025177 | -0.012234 | -0.080079 | -0.0042019 | -0.029375 | -0.048672 | -0.043169 | -0.0021057 | -0.020749 | 0.0562 | 0.048612 | -0.21894 | -0.014283 | -0.023253 | -0.10071 | 0.086975 | -0.12817 | -0.082397 | 0.045776 | -0.10986 | -0.027466 | -29.1275 | 0.35248 | -122.4426 | 0.32501 | -121.7697 | -122.1588 | -121.7148 | 122.2229 | -0.27008 | -0.43945 | 122.3969 | 122.3236 | 122.2412 | 0.10071 | 0.018311 | -0.091553 | -0.004578 | -0.032044 | 0.58136 | 0.63629 | 0.19226 | 0.72784 | 0.28381 | 0.17395 | 0.045777 | 0.67291 | 122.7676 | 0.21515 | 122.7951 | 122.438 | 122.7036 | -0.48523 | -122.7997 | 122.2687 | 122.6761 | 122.2504 | 93.2236
2141.375 | 122.8134 | -122.4197 | 0.3891 | -0.0051118 | -0.013943 | -0.080292 | -0.0059109 | -0.029375 | -0.050595 | -0.039324 | -0.0021057 | -0.019895 | 0.057054 | 0.044553 | -0.21766 | -0.018342 | -0.022185 | -0.13733 | 0.1236 | -0.13733 | -0.15564 | -0.018311 | -0.14648 | -0.082397 | -29.3838 | 0.38452 | -122.4472 | 0.20142 | -121.8521 | -122.2504 | -121.8246 | 122.2824 | -0.2655 | -0.54474 | 122.4014 | 122.3373 | 122.2733 | 0.054932 | -0.009155 | -0.027466 | -0.004578 | -0.18768 | 0.56763 | 0.59509 | 0.16937 | 0.62256 | 0.19684 | 0.11902 | -0.018311 | 0.59509 | 122.6486 | 0.26093 | 122.8317 | 122.5433 | 122.8043 | -0.52643 | -122.8363 | 122.2641 | 122.6212 | 122.2824 | 93.0359
2143.1562 | 122.7951 | -122.3923 | 0.39825 | -0.0051118 | -0.010525 | -0.079011 | -0.0033475 | -0.02788 | -0.049526 | -0.042314 | -0.0021057 | -0.018613 | 0.057909 | 0.056303 | -0.21937 | -0.013642 | -0.021971 | -0.073242 | 0.09613 | -0.12817 | -0.10529 | 0.027466 | -0.14191 | -0.068665 | -29.4754 | 0.3891 | -122.4747 | 0.24719 | -121.8567 | -122.2916 | -121.8109 | 122.2641 | -0.30212 | -0.50354 | 122.4197 | 122.3236 | 122.2504 | 0.059509 | -0.013733 | -0.082397 | -0.009155 | -0.15106 | 0.53558 | 0.58136 | 0.10071 | 0.66376 | 0.1831 | 0.15564 | 0.022888 | 0.61798 | 122.7219 | 0.2243 | 122.8638 | 122.4884 | 122.7814 | -0.52643 | -122.8729 | 122.287 | 122.6395 | 122.319 | 92.9169
2144.8906 | 122.8043 | -122.406 | 0.39368 | 0.0025177 | -0.010311 | -0.076874 | -0.0039883 | -0.030016 | -0.050808 | -0.038896 | -0.0051575 | -0.019895 | 0.058123 | 0.048398 | -0.2183 | -0.015778 | -0.017699 | -0.10529 | 0.11444 | -0.11444 | -0.12817 | 0.004578 | -0.16479 | -0.082397 | -29.6631 | 0.37994 | -122.4655 | 0.21515 | -121.8796 | -122.2916 | -121.8384 | 122.2916 | -0.27924 | -0.52185 | 122.4106 | 122.3236 | 122.2412 | 0.032044 | -0.050354 | -0.059509 | -0.013733 | -0.17853 | 0.52643 | 0.56763 | 0.11444 | 0.62714 | 0.17395 | 0.11902 | -0.013733 | 0.58594 | 122.6807 | 0.22888 | 122.8455 | 122.5204 | 122.7859 | -0.50812 | -122.8592 | 122.2778 | 122.6212 | 122.3007 | 92.7429
2146.6719 | 122.9416 | -122.3877 | 0.34332 | 0.010147 | -0.016293 | -0.081574 | -0.0091153 | -0.030871 | -0.051022 | -0.041246 | -0.0051575 | -0.023099 | 0.057695 | 0.049467 | -0.21851 | -0.016419 | -0.022185 | -0.091553 | 0.091553 | -0.086975 | -0.073242 | 0.10986 | -0.041199 | 0.022888 | -29.7592 | 0.3479 | -122.4335 | 0.31586 | -121.7468 | -122.1222 | -121.7148 | 122.3007 | -0.25177 | -0.41656 | 122.4976 | 122.4106 | 122.3465 | 0.10986 | 0.045776 | -0.045777 | 0.004577 | -0.027466 | 0.64087 | 0.67291 | 0.2655 | 0.71869 | 0.31128 | 0.19684 | 0.013733 | 0.68665 | 122.7493 | 0.17853 | 122.7814 | 122.4792 | 122.7356 | -0.4303 | -122.7768 | 122.3145 | 122.7036 | 122.2961 | 92.6285
2148.4531 | 122.8455 | -122.4243 | 0.37537 | -0.0051118 | -0.01138 | -0.078156 | -0.0050565 | -0.029162 | -0.049954 | -0.042955 | 0.00094606 | -0.019681 | 0.057909 | 0.05203 | -0.22043 | -0.01706 | -0.020049 | -0.068665 | 0.09613 | -0.12817 | -0.10071 | 0.032043 | -0.11444 | -0.041199 | -29.8965 | 0.36163 | -122.4564 | 0.26093 | -121.8109 | -122.2321 | -121.788 | 122.2961 | -0.27924 | -0.47607 | 122.4564 | 122.3831 | 122.3099 | 0.086975 | 0.013733 | -0.032044 | -0.013733 | -0.11444 | 0.6134 | 0.63629 | 0.19226 | 0.66833 | 0.2243 | 0.16022 | 0.027466 | 0.64545 | 122.7173 | 0.2243 | 122.818 | 122.5204 | 122.7859 | -0.50354 | -122.8317 | 122.3236 | 122.6852 | 122.3557 | 92.5278
2150.2656 | 122.8409 | -122.4106 | 0.36621 | -0.0051118 | -0.01437 | -0.079011 | -0.0054837 | -0.031084 | -0.05209 | -0.038896 | 0.00094606 | -0.017331 | 0.057482 | 0.045835 | -0.21958 | -0.015351 | -0.021758 | -0.073242 | 0.09613 | -0.11902 | -0.10071 | 0.045776 | -0.10071 | -0.054932 | -30.0568 | 0.37537 | -122.4564 | 0.24719 | -121.843 | -122.2275 | -121.788 | 122.2916 | -0.27008 | -0.46692 | 122.4564 | 122.3557 | 122.3099 | 0.064087 | 0.018311 | -0.045777 | 0.009155 | -0.11902 | 0.56763 | 0.62256 | 0.1831 | 0.66833 | 0.22888 | 0.16479 | 0.018311 | 0.6134 | 122.7036 | 0.21515 | 122.8317 | 122.5067 | 122.7859 | -0.48523 | -122.8226 | 122.3099 | 122.6578 | 122.3373 | 92.3538
2152.0469 | 122.7859 | -122.4152 | 0.37079 | 0.010147 | -0.011807 | -0.076874 | -0.0048427 | -0.029589 | -0.051876 | -0.039324 | -0.0021057 | -0.019681 | 0.0562 | 0.046903 | -0.21766 | -0.016846 | -0.025176 | -0.14191 | 0.10071 | -0.11902 | -0.16479 | -0.036621 | -0.1831 | -0.11444 | -30.3543 | 0.37079 | -122.4701 | 0.18768 | -121.9025 | -122.319 | -121.8521 | 122.2961 | -0.27008 | -0.53558 | 122.3785 | 122.3007 | 122.2321 | 0.004578 | -0.064086 | -0.054932 | 0 | -0.18311 | 0.51269 | 0.56305 | 0.09613 | 0.61798 | 0.15106 | 0.082398 | -0.045776 | 0.56763 | 122.6578 | 0.21973 | 122.8409 | 122.5159 | 122.7859 | -0.48981 | -122.8409 | 122.2504 | 122.6028 | 122.2733 | 92.0609
2153.8281 | 122.8134 | -122.4152 | 0.37994 | 0.010147 | -0.013943 | -0.081147 | -0.0050565 | -0.032366 | -0.051022 | -0.039537 | -0.0021057 | -0.019467 | 0.057909 | 0.047971 | -0.21766 | -0.013642 | -0.021544 | -0.14191 | 0.11444 | -0.13733 | -0.17853 | -0.009155 | -0.13275 | -0.073242 | -30.4779 | 0.37994 | -122.4747 | 0.21057 | -121.8567 | -122.2733 | -121.8384 | 122.2778 | -0.2655 | -0.55847 | 122.406 | 122.3419 | 122.2824 | 0.064087 | 0.004578 | -0.059509 | 0 | -0.16937 | 0.55847 | 0.57678 | 0.14191 | 0.63629 | 0.20142 | 0.12817 | -0.041199 | 0.61798 | 122.6852 | 0.25177 | 122.8546 | 122.5296 | 122.7951 | -0.51727 | -122.8546 | 122.2366 | 122.6257 | 122.2733 | 91.9373
2155.5469 | 122.8363 | -122.4014 | 0.37537 | -0.0051118 | -0.011807 | -0.078156 | -0.0052701 | -0.029162 | -0.051876 | -0.042101 | -0.0021057 | -0.020749 | 0.058123 | 0.048398 | -0.22043 | -0.015778 | -0.026244 | -0.091553 | 0.09613 | -0.11444 | -0.11902 | 0.032043 | -0.10986 | -0.032043 | -30.5511 | 0.37537 | -122.4609 | 0.2655 | -121.8155 | -122.2366 | -121.7834 | 122.287 | -0.27924 | -0.49438 | 122.4335 | 122.3694 | 122.2916 | 0.082398 | 0.004578 | -0.059509 | 0 | -0.10986 | 0.58594 | 0.61798 | 0.16479 | 0.67749 | 0.2243 | 0.14648 | -0.004578 | 0.64545 | 122.7264 | 0.21057 | 122.8363 | 122.4976 | 122.7768 | -0.48981 | -122.8363 | 122.2824 | 122.6669 | 122.3099 | 91.8503
2157.3438 | 122.8912 | -122.406 | 0.37079 | 0.0025177 | -0.012448 | -0.077515 | -0.0078335 | -0.030443 | -0.050167 | -0.040605 | 0.00094606 | -0.023313 | 0.056841 | 0.048398 | -0.21851 | -0.01706 | -0.021758 | -0.11444 | 0.082397 | -0.091553 | -0.09613 | 0.041199 | -0.09613 | -0.018311 | -30.7343 | 0.34332 | -122.4609 | 0.25635 | -121.8109 | -122.1954 | -121.7651 | 122.3145 | -0.28839 | -0.46692 | 122.4472 | 122.3877 | 122.3099 | 0.073242 | -0.004577 | -0.054931 | -0.027466 | -0.11444 | 0.59509 | 0.64087 | 0.21057 | 0.6958 | 0.2655 | 0.13275 | -0.004577 | 0.65002 | 122.7173 | 0.17395 | 122.8043 | 122.4884 | 122.7493 | -0.46234 | -122.8317 | 122.3099 | 122.6624 | 122.2916 | 91.6718
2159.125 | 122.7905 | -122.4426 | 0.39368 | 0.0025177 | -0.015225 | -0.082001 | -0.0074063 | -0.029375 | -0.052944 | -0.042528 | 0.00094606 | -0.020749 | 0.058763 | 0.042631 | -0.21723 | -0.016205 | -0.022826 | -0.14191 | 0.11902 | -0.1236 | -0.16022 | -0.009155 | -0.13733 | -0.07782 | -30.9174 | 0.36163 | -122.4792 | 0.1831 | -121.875 | -122.2641 | -121.8521 | 122.319 | -0.27466 | -0.55389 | 122.4335 | 122.3648 | 122.3053 | 0.045776 | -0.013733 | -0.036621 | -0.032044 | -0.21057 | 0.56763 | 0.59051 | 0.17853 | 0.62714 | 0.21515 | 0.11444 | -0.036621 | 0.60425 | 122.6624 | 0.24261 | 122.8409 | 122.5616 | 122.8043 | -0.51727 | -122.8729 | 122.2824 | 122.6257 | 122.3007 | 91.5253
2160.8438 | 122.9233 | -122.3923 | 0.36621 | 0.0025177 | -0.01437 | -0.079011 | -0.0099697 | -0.029162 | -0.050167 | -0.040819 | 0.00094606 | -0.020536 | 0.05855 | 0.049039 | -0.22022 | -0.015992 | -0.022185 | -0.054932 | 0.059509 | -0.086975 | -0.027466 | 0.16022 | -0.004578 | 0.050354 | -30.9036 | 0.31586 | -122.4289 | 0.32501 | -121.7331 | -122.1222 | -121.7331 | 122.3053 | -0.3067 | -0.39368 | 122.5525 | 122.4426 | 122.3877 | 0.13733 | 0.082397 | -0.036621 | -0.050354 | -0.041199 | 0.65918 | 0.65918 | 0.27008 | 0.6958 | 0.3067 | 0.24719 | 0.059509 | 0.6958 | 122.7539 | 0.14648 | 122.7448 | 122.4518 | 122.7081 | -0.45319 | -122.7951 | 122.3648 | 122.7173 | 122.3373 | 91.4886
2162.625 | 122.8592 | -122.3969 | 0.37079 | -0.0051118 | -0.012875 | -0.079865 | -0.0048427 | -0.034289 | -0.051876 | -0.040819 | -0.0051575 | -0.01904 | 0.057482 | 0.053953 | -0.22129 | -0.015137 | -0.027098 | -0.086975 | 0.09613 | -0.11902 | -0.09613 | 0.032043 | -0.11902 | -0.050354 | -31.1462 | 0.37079 | -122.4564 | 0.25177 | -121.8109 | -122.2321 | -121.7926 | 122.2778 | -0.27466 | -0.46692 | 122.4289 | 122.3465 | 122.2778 | 0.068665 | 0 | -0.059509 | 0 | -0.11902 | 0.58594 | 0.60425 | 0.16479 | 0.66376 | 0.2243 | 0.15106 | 0.022889 | 0.64545 | 122.7081 | 0.21515 | 122.8271 | 122.493 | 122.7676 | -0.48981 | -122.8271 | 122.3007 | 122.6486 | 122.3099 | 91.2506
2164.3438 | 122.85 | -122.4197 | 0.35706 | 0.0025177 | -0.012234 | -0.079651 | -0.0078335 | -0.030443 | -0.050167 | -0.042101 | -0.0021057 | -0.022885 | 0.057268 | 0.043485 | -0.22086 | -0.017487 | -0.024748 | -0.050354 | 0.054932 | -0.091553 | -0.054932 | 0.11444 | -0.045776 | 0.027466 | -31.311 | 0.3479 | -122.4609 | 0.24719 | -121.7972 | -122.2046 | -121.7834 | 122.3282 | -0.30212 | -0.41199 | 122.5342 | 122.4472 | 122.374 | 0.11902 | 0.045777 | -0.041198 | -0.009156 | -0.10986 | 0.62256 | 0.63629 | 0.21515 | 0.67749 | 0.25635 | 0.20599 | 0.036621 | 0.66376 | 122.7081 | 0.14649 | 122.8088 | 122.4747 | 122.7676 | -0.44861 | -122.818 | 122.3648 | 122.6669 | 122.3694 | 91.1087
2166.125 | 122.818 | -122.406 | 0.37079 | -0.0051118 | -0.012661 | -0.079438 | -0.0024929 | -0.027239 | -0.051449 | -0.039751 | -0.0021057 | -0.01669 | 0.057909 | 0.051389 | -0.21894 | -0.015137 | -0.018126 | -0.091553 | 0.09613 | -0.11902 | -0.1236 | 0.009155 | -0.16022 | -0.082397 | -31.572 | 0.36163 | -122.4838 | 0.20599 | -121.8887 | -122.3099 | -121.8384 | 122.287 | -0.27466 | -0.49438 | 122.4152 | 122.3236 | 122.2458 | 0.036622 | -0.041198 | -0.07782 | -0.009156 | -0.16479 | 0.51727 | 0.56763 | 0.096131 | 0.64545 | 0.17395 | 0.12817 | -0.004577 | 0.59509 | 122.6898 | 0.21515 | 122.8455 | 122.5021 | 122.7676 | -0.48981 | -122.8546 | 122.2824 | 122.612 | 122.3145 | 90.834
2167.8438 | 122.8409 | -122.4335 | 0.37079 | -0.0051118 | -0.0096707 | -0.076233 | -0.0044155 | -0.031725 | -0.047817 | -0.039751 | -0.0051575 | -0.019681 | 0.059618 | 0.052671 | -0.21958 | -0.014924 | -0.020476 | -0.11902 | 0.10071 | -0.14191 | -0.15106 | -0.027466 | -0.17395 | -0.07782 | -31.7505 | 0.36163 | -122.4792 | 0.24261 | -121.8704 | -122.2824 | -121.8109 | 122.2916 | -0.27008 | -0.52185 | 122.406 | 122.3557 | 122.2595 | 0.064087 | -0.032043 | -0.045776 | -0.009156 | -0.12817 | 0.56305 | 0.62256 | 0.15106 | 0.66833 | 0.19684 | 0.11444 | -0.009155 | 0.60883 | 122.7219 | 0.24262 | 122.8409 | 122.5342 | 122.7951 | -0.5127 | -122.85 | 122.2824 | 122.6761 | 122.3145 | 90.683
2169.625 | 122.9462 | -122.4152 | 0.3479 | -0.0051118 | -0.01138 | -0.078797 | -0.0039883 | -0.029375 | -0.049954 | -0.040605 | -0.0051575 | -0.023099 | 0.057695 | 0.049039 | -0.21872 | -0.017701 | -0.024535 | -0.032043 | 0.064087 | -0.086975 | -0.027466 | 0.11902 | -0.054932 | 0 | -31.81 | 0.32959 | -122.4472 | 0.34332 | -121.7468 | -122.1634 | -121.7056 | 122.3282 | -0.28381 | -0.37537 | 122.5342 | 122.4152 | 122.3602 | 0.086975 | 0.032043 | -0.032044 | -0.01831 | -0.004577 | 0.66833 | 0.70953 | 0.25177 | 0.74158 | 0.28381 | 0.20599 | 0.059509 | 0.70038 | 122.7905 | 0.15106 | 122.7768 | 122.4792 | 122.7448 | -0.43488 | -122.7951 | 122.3877 | 122.7585 | 122.3831 | 90.6052
2171.4062 | 122.8271 | -122.4243 | 0.41199 | -0.0051118 | -0.014157 | -0.080506 | -0.0067653 | -0.031511 | -0.050808 | -0.042101 | 0.0039979 | -0.019895 | 0.057695 | 0.047117 | -0.21851 | -0.014924 | -0.019408 | -0.14191 | 0.1236 | -0.13275 | -0.16479 | -0.009155 | -0.13733 | -0.07782 | -32.1075 | 0.37994 | -122.4792 | 0.19226 | -121.8613 | -122.2916 | -121.8338 | 122.2916 | -0.28839 | -0.57678 | 122.4152 | 122.3465 | 122.287 | 0.054931 | -0.004578 | -0.054932 | -0.032043 | -0.21973 | 0.56305 | 0.59052 | 0.13275 | 0.64545 | 0.18768 | 0.1236 | -0.032044 | 0.61798 | 122.6715 | 0.25635 | 122.8592 | 122.5479 | 122.8043 | -0.54474 | -122.8912 | 122.2595 | 122.6166 | 122.2824 | 90.3168
2173.1719 | 122.8592 | -122.4197 | 0.37537 | -0.0051118 | -0.014584 | -0.078583 | -0.0042019 | -0.025316 | -0.051663 | -0.039965 | -0.0021057 | -0.018399 | 0.058977 | 0.048612 | -0.22022 | -0.015992 | -0.024321 | -0.086975 | 0.10986 | -0.1236 | -0.11444 | 0.022888 | -0.10529 | -0.036621 | -32.2678 | 0.36163 | -122.4838 | 0.25177 | -121.8109 | -122.2366 | -121.7972 | 122.2961 | -0.2655 | -0.48981 | 122.4426 | 122.3831 | 122.3145 | 0.086975 | 0.01831 | -0.064087 | -0.013733 | -0.1236 | 0.60883 | 0.62256 | 0.18311 | 0.68665 | 0.24719 | 0.14648 | 0.009155 | 0.67291 | 122.7356 | 0.23346 | 122.8455 | 122.5296 | 122.7814 | -0.49896 | -122.8592 | 122.3053 | 122.6715 | 122.3328 | 90.152
2174.9688 | 122.937 | -122.3694 | 0.34332 | 0.0025177 | -0.010525 | -0.080719 | -0.0042019 | -0.032366 | -0.04739 | -0.042528 | -0.0021057 | -0.018827 | 0.057695 | 0.053098 | -0.22043 | -0.015778 | -0.020262 | -0.09613 | 0.082397 | -0.11444 | -0.068665 | 0.073242 | -0.10071 | -0.004578 | -32.3959 | 0.35248 | -122.4426 | 0.32044 | -121.7606 | -122.1817 | -121.7102 | 122.2549 | -0.26093 | -0.41199 | 122.4426 | 122.3648 | 122.2687 | 0.10986 | 0.013733 | -0.073242 | 0.009155 | -0.022888 | 0.60883 | 0.65918 | 0.18768 | 0.73242 | 0.26093 | 0.18768 | 0.045776 | 0.68207 | 122.7631 | 0.19684 | 122.7951 | 122.4518 | 122.7219 | -0.45776 | -122.7859 | 122.3007 | 122.6898 | 122.2733 | 89.9734
2176.75 | 122.9507 | -122.3923 | 0.32959 | -0.0051118 | -0.0094571 | -0.075806 | -0.0069791 | -0.029589 | -0.048886 | -0.043169 | -0.0021057 | -0.020322 | 0.0562 | 0.046903 | -0.22129 | -0.015351 | -0.02133 | -0.027466 | 0.073242 | -0.10529 | -0.032043 | 0.10986 | -0.064087 | 0.032043 | -32.4646 | 0.32044 | -122.4609 | 0.33417 | -121.7422 | -122.1588 | -121.6965 | 122.287 | -0.25635 | -0.36163 | 122.5021 | 122.4243 | 122.3282 | 0.13733 | 0.041199 | -0.068664 | -0.009155 | 0.004577 | 0.65002 | 0.6958 | 0.23346 | 0.76447 | 0.30212 | 0.21515 | 0.073243 | 0.71869 | 122.7951 | 0.17853 | 122.7814 | 122.4655 | 122.7127 | -0.43488 | -122.7905 | 122.3602 | 122.7264 | 122.3648 | 89.9277
2178.4688 | 122.8683 | -122.438 | 0.37079 | -0.0051118 | -0.013729 | -0.077729 | -0.0037747 | -0.02788 | -0.050381 | -0.040605 | 0.00094606 | -0.018613 | 0.05855 | 0.046262 | -0.21979 | -0.01706 | -0.027098 | -0.11444 | 0.11444 | -0.14191 | -0.13275 | -0.013733 | -0.1236 | -0.054932 | -32.7072 | 0.37079 | -122.4838 | 0.2243 | -121.8246 | -122.2549 | -121.8018 | 122.2961 | -0.25635 | -0.50354 | 122.4243 | 122.3831 | 122.3145 | 0.086975 | 0.018311 | -0.045777 | 0 | -0.14648 | 0.6134 | 0.63629 | 0.18311 | 0.68207 | 0.22888 | 0.12817 | 0.009156 | 0.65918 | 122.7081 | 0.25635 | 122.8546 | 122.5525 | 122.8088 | -0.5127 | -122.8546 | 122.3053 | 122.6624 | 122.3236 | 89.7308
2180.2656 | 122.85 | -122.4289 | 0.36163 | -0.0051118 | -0.013089 | -0.079438 | -0.0080471 | -0.030657 | -0.04974 | -0.042528 | 0.00094606 | -0.020536 | 0.059191 | 0.046903 | -0.22001 | -0.015351 | -0.02368 | -0.12817 | 0.11902 | -0.15106 | -0.14648 | -0.018311 | -0.12817 | -0.068665 | -32.8949 | 0.35706 | -122.5113 | 0.22888 | -121.8384 | -122.2595 | -121.8246 | 122.2778 | -0.24261 | -0.50812 | 122.4106 | 122.3602 | 122.3007 | 0.082397 | 0.022888 | -0.082398 | -0.004577 | -0.13275 | 0.59051 | 0.60425 | 0.16937 | 0.68665 | 0.25177 | 0.13275 | 0.004578 | 0.67291 | 122.7402 | 0.27008 | 122.8683 | 122.5479 | 122.7859 | -0.5127 | -122.8729 | 122.2824 | 122.6578 | 122.3007 | 89.534
2182.0625 | 122.8363 | -122.4426 | 0.37537 | 0.0025177 | -0.01138 | -0.080719 | -0.0056973 | -0.032793 | -0.049313 | -0.040605 | -0.0021057 | -0.019681 | 0.057909 | 0.043699 | -0.21915 | -0.015992 | -0.027312 | -0.082397 | 0.09613 | -0.12817 | -0.11444 | 0.036621 | -0.13275 | -0.064087 | -33.0688 | 0.35706 | -122.4792 | 0.23804 | -121.8613 | -122.287 | -121.8384 | 122.3145 | -0.27924 | -0.48981 | 122.4792 | 122.3785 | 122.3099 | 0.064087 | -0.004577 | -0.036621 | -0.01831 | -0.13733 | 0.58136 | 0.60425 | 0.15564 | 0.64087 | 0.19226 | 0.1648 | 0.013733 | 0.61798 | 122.7173 | 0.2243 | 122.8363 | 122.5388 | 122.7997 | -0.50354 | -122.8546 | 122.3282 | 122.6807 | 122.3602 | 89.3738
2183.8438 | 122.9782 | -122.4106 | 0.32959 | 0.010147 | -0.014584 | -0.080292 | -0.0091153 | -0.036425 | -0.050381 | -0.042528 | -0.0051575 | -0.020322 | 0.05855 | 0.040281 | -0.21851 | -0.015778 | -0.023039 | -0.073242 | 0.064087 | -0.09613 | -0.027466 | 0.15564 | -0.004578 | 0.059509 | -33.0826 | 0.31128 | -122.4747 | 0.32959 | -121.6919 | -122.1176 | -121.7056 | 122.3145 | -0.2655 | -0.35706 | 122.5662 | 122.4701 | 122.406 | 0.15564 | 0.091552 | -0.064087 | -0.018311 | 0 | 0.71869 | 0.70496 | 0.29297 | 0.76904 | 0.35706 | 0.25177 | 0.068664 | 0.78278 | 122.8043 | 0.16022 | 122.7859 | 122.4747 | 122.7219 | -0.42572 | -122.8043 | 122.3831 | 122.7402 | 122.3373 | 89.328
2185.625 | 122.8043 | -122.4564 | 0.36163 | 0.010147 | -0.010311 | -0.079011 | -0.0061245 | -0.028307 | -0.048245 | -0.039965 | 0.00094606 | -0.019254 | 0.058763 | 0.044553 | -0.21915 | -0.015351 | -0.020049 | -0.11444 | 0.10071 | -0.11902 | -0.15106 | -0.045776 | -0.18768 | -0.10529 | -33.4579 | 0.37537 | -122.5021 | 0.17853 | -121.8979 | -122.3465 | -121.8567 | 122.3373 | -0.26092 | -0.5127 | 122.4106 | 122.3511 | 122.2687 | 0.013733 | -0.068664 | -0.045776 | 0.013733 | -0.1831 | 0.55847 | 0.59967 | 0.10986 | 0.64545 | 0.15564 | 0.073243 | -0.032043 | 0.60425 | 122.6807 | 0.21973 | 122.8775 | 122.5571 | 122.8317 | -0.48065 | -122.8638 | 122.3053 | 122.6349 | 122.3419 | 88.9984
2187.4219 | 122.9645 | -122.3923 | 0.31128 | -0.0051118 | -0.01437 | -0.080079 | -0.0086879 | -0.030871 | -0.051449 | -0.041033 | 0.00094606 | -0.021817 | 0.05855 | 0.041349 | -0.21958 | -0.018342 | -0.025389 | -0.059509 | 0.064087 | -0.09613 | -0.027466 | 0.14191 | -0.018311 | 0.050354 | -33.4763 | 0.32044 | -122.4518 | 0.32044 | -121.7331 | -122.1313 | -121.7422 | 122.2961 | -0.24719 | -0.33874 | 122.5342 | 122.4426 | 122.374 | 0.14648 | 0.077819 | -0.059509 | 0.009156 | 0.009156 | 0.65918 | 0.65002 | 0.26093 | 0.70953 | 0.32043 | 0.23804 | 0.068664 | 0.71869 | 122.7722 | 0.16022 | 122.7722 | 122.4564 | 122.7127 | -0.40741 | -122.7631 | 122.3648 | 122.7127 | 122.3328 | 88.916
2189.125 | 122.8043 | -122.4335 | 0.37537 | -0.0051118 | -0.010098 | -0.079438 | -0.0042019 | -0.031511 | -0.050808 | -0.041246 | 0.00094606 | -0.017972 | 0.057482 | 0.049253 | -0.21787 | -0.013215 | -0.022826 | -0.11902 | 0.10986 | -0.13275 | -0.16022 | -0.050354 | -0.1831 | -0.10529 | -33.8425 | 0.35706 | -122.5067 | 0.19684 | -121.9254 | -122.3602 | -121.8842 | 122.3007 | -0.2655 | -0.53558 | 122.3831 | 122.3282 | 122.2504 | 0.027465 | -0.050354 | -0.073242 | -0.01831 | -0.17853 | 0.50812 | 0.54932 | 0.073243 | 0.62256 | 0.14648 | 0.082397 | -0.027466 | 0.58136 | 122.7036 | 0.24261 | 122.8638 | 122.5433 | 122.7905 | -0.50812 | -122.8821 | 122.2733 | 122.6303 | 122.3145 | 88.591
2190.9062 | 122.8592 | -122.4289 | 0.36163 | -0.0051118 | -0.01437 | -0.080292 | -0.0046291 | -0.026384 | -0.051022 | -0.040178 | -0.0021057 | -0.019254 | 0.058763 | 0.049253 | -0.21766 | -0.016633 | -0.022612 | -0.073242 | 0.10529 | -0.11444 | -0.086975 | 0.068665 | -0.10529 | -0.054932 | -33.8196 | 0.32959 | -122.5021 | 0.23346 | -121.8384 | -122.2687 | -121.8292 | 122.3145 | -0.25635 | -0.44861 | 122.4976 | 122.374 | 122.3236 | 0.059509 | 0.009155 | -0.073242 | -0.032043 | -0.12817 | 0.59051 | 0.59967 | 0.16022 | 0.67291 | 0.23346 | 0.18311 | 0.027466 | 0.66376 | 122.7356 | 0.21973 | 122.8317 | 122.5342 | 122.7585 | -0.47607 | -122.8638 | 122.3419 | 122.6624 | 122.3557 | 88.6093
2192.6406 | 122.9141 | -122.406 | 0.32044 | -0.0051118 | -0.012661 | -0.07837 | -0.0048427 | -0.030657 | -0.049099 | -0.039965 | -0.0021057 | -0.019254 | 0.055559 | 0.045194 | -0.22065 | -0.016846 | -0.020476 | -0.086975 | 0.11444 | -0.11902 | -0.07782 | 0.054932 | -0.086975 | -0.018311 | -33.9935 | 0.32501 | -122.4701 | 0.32044 | -121.7743 | -122.2137 | -121.7331 | 122.287 | -0.20599 | -0.39826 | 122.4609 | 122.3877 | 122.319 | 0.10071 | 0.032044 | -0.064087 | 0.004577 | 0 | 0.63171 | 0.67291 | 0.19226 | 0.737 | 0.25635 | 0.17395 | 0.041199 | 0.6958 | 122.7905 | 0.23346 | 122.7951 | 122.5204 | 122.731 | -0.43945 | -122.7905 | 122.3282 | 122.7264 | 122.319 | 88.4125
2194.4219 | 122.8455 | -122.4243 | 0.36163 | 0.0025177 | -0.013089 | -0.08136 | -0.0050565 | -0.03322 | -0.051663 | -0.040178 | -0.0021057 | -0.021176 | 0.056841 | 0.049039 | -0.21894 | -0.015992 | -0.022398 | -0.11902 | 0.10986 | -0.13733 | -0.14648 | 0 | -0.11444 | -0.064087 | -34.2773 | 0.32959 | -122.4884 | 0.21515 | -121.8246 | -122.2778 | -121.8155 | 122.287 | -0.25177 | -0.50812 | 122.4243 | 122.3602 | 122.3099 | 0.073242 | 0.022888 | -0.064087 | -0.032043 | -0.14648 | 0.59967 | 0.60883 | 0.14648 | 0.67291 | 0.21057 | 0.13733 | -0.009155 | 0.66376 | 122.7036 | 0.24719 | 122.818 | 122.5342 | 122.7539 | -0.49896 | -122.85 | 122.2778 | 122.6395 | 122.3053 | 88.147
2196.2031 | 122.8409 | -122.4518 | 0.35248 | 0.010147 | -0.010098 | -0.079224 | -0.0046291 | -0.030016 | -0.050808 | -0.044664 | -0.0021057 | -0.019467 | 0.055345 | 0.044126 | -0.21702 | -0.016419 | -0.020689 | -0.073242 | 0.11444 | -0.11902 | -0.10529 | 0.045776 | -0.1236 | -0.054932 | -34.4101 | 0.33875 | -122.493 | 0.2243 | -121.8613 | -122.287 | -121.8384 | 122.3328 | -0.23804 | -0.45776 | 122.4976 | 122.3969 | 122.3282 | 0.064087 | -0.004577 | -0.041199 | -0.013733 | -0.12817 | 0.59051 | 0.6134 | 0.16479 | 0.6546 | 0.20599 | 0.16479 | 0.013733 | 0.63171 | 122.7173 | 0.23346 | 122.8317 | 122.5662 | 122.7905 | -0.4715 | -122.8455 | 122.3465 | 122.6761 | 122.3785 | 88.0417
2198.0156 | 122.9095 | -122.406 | 0.32501 | 0.0025177 | -0.013089 | -0.07837 | -0.0078335 | -0.028521 | -0.05209 | -0.038896 | -0.0051575 | -0.022031 | 0.056841 | 0.045194 | -0.21808 | -0.01471 | -0.025603 | -0.082397 | 0.073242 | -0.10529 | -0.064087 | 0.10529 | -0.086975 | -0.004578 | -34.6161 | 0.31128 | -122.493 | 0.2655 | -121.8018 | -122.2321 | -121.7743 | 122.3007 | -0.25177 | -0.3891 | 122.5113 | 122.4014 | 122.319 | 0.10071 | 0.018311 | -0.086975 | -0.013733 | -0.059509 | 0.60425 | 0.63171 | 0.17395 | 0.71869 | 0.26093 | 0.21057 | 0.041199 | 0.69122 | 122.7585 | 0.17853 | 122.8043 | 122.4792 | 122.7173 | -0.4303 | -122.818 | 122.3419 | 122.6715 | 122.3236 | 87.7899
2199.7344 | 122.8912 | -122.4335 | 0.32501 | -0.012741 | -0.012875 | -0.081147 | -0.0082607 | -0.027453 | -0.049526 | -0.041887 | -0.0021057 | -0.021817 | 0.058763 | 0.03729 | -0.22022 | -0.016205 | -0.019835 | -0.10071 | 0.068665 | -0.09613 | -0.068665 | 0.073242 | -0.091553 | 0.004578 | -34.7763 | 0.32044 | -122.4609 | 0.24261 | -121.8063 | -122.2366 | -121.7972 | 122.3373 | -0.25635 | -0.39368 | 122.5067 | 122.438 | 122.3419 | 0.10071 | 0.004577 | -0.027465 | -0.004577 | -0.082397 | 0.62714 | 0.63629 | 0.19684 | 0.66376 | 0.2243 | 0.16937 | 0.027465 | 0.6546 | 122.7036 | 0.16479 | 122.7814 | 122.5021 | 122.7539 | -0.42114 | -122.7859 | 122.3648 | 122.6761 | 122.3328 | 87.6572
2201.4531 | 122.8134 | -122.4701 | 0.37994 | -0.0051118 | -0.015011 | -0.079438 | -0.0071927 | -0.034289 | -0.049526 | -0.040178 | -0.0021057 | -0.019467 | 0.057482 | 0.046049 | -0.22129 | -0.016846 | -0.027098 | -0.15106 | 0.13733 | -0.13275 | -0.15564 | -0.009155 | -0.13733 | -0.068665 | -35.0327 | 0.3479 | -122.5204 | 0.15564 | -121.8842 | -122.3099 | -121.875 | 122.3373 | -0.24261 | -0.53558 | 122.4609 | 122.4014 | 122.3328 | 0.064086 | -0.004578 | -0.050354 | -0.032044 | -0.2243 | 0.58594 | 0.59509 | 0.16022 | 0.64545 | 0.21057 | 0.1236 | -0.022889 | 0.63629 | 122.6761 | 0.27008 | 122.8683 | 122.6074 | 122.818 | -0.5127 | -122.9004 | 122.3145 | 122.6257 | 122.319 | 87.4374
2203.2344 | 122.8958 | -122.4472 | 0.31128 | -0.012741 | -0.013516 | -0.079438 | -0.0065517 | -0.031298 | -0.050595 | -0.039751 | -0.0021057 | -0.020322 | 0.05855 | 0.047117 | -0.22172 | -0.013642 | -0.022826 | -0.073242 | 0.068665 | -0.082397 | -0.050354 | 0.11902 | -0.082397 | 0.004578 | -35.1151 | 0.3067 | -122.4884 | 0.2655 | -121.7926 | -122.2229 | -121.788 | 122.3648 | -0.24261 | -0.36163 | 122.5662 | 122.4518 | 122.3648 | 0.086975 | 0 | -0.041198 | -0.004577 | -0.045776 | 0.6546 | 0.65918 | 0.22431 | 0.70038 | 0.2655 | 0.20142 | 0.032043 | 0.6958 | 122.7539 | 0.15106 | 122.7951 | 122.5159 | 122.7539 | -0.39368 | -122.7997 | 122.3969 | 122.7127 | 122.374 | 87.3322
2205.0312 | 122.905 | -122.4289 | 0.31586 | 0.0025177 | -0.0090299 | -0.079651 | -0.0065517 | -0.030871 | -0.047604 | -0.038683 | -0.0021057 | -0.020963 | 0.057268 | 0.046903 | -0.21979 | -0.016205 | -0.021544 | -0.059509 | 0.064087 | -0.073242 | -0.027466 | 0.11444 | -0.054932 | 0.032043 | -35.289 | 0.30212 | -122.4838 | 0.3067 | -121.7743 | -122.2183 | -121.7972 | 122.3557 | -0.25177 | -0.34332 | 122.5433 | 122.4609 | 122.374 | 0.10529 | 0.01831 | -0.054932 | -0.013733 | -0.009155 | 0.6546 | 0.63171 | 0.21057 | 0.68665 | 0.2655 | 0.18768 | 0.045776 | 0.70953 | 122.7905 | 0.13733 | 122.7859 | 122.493 | 122.731 | -0.3891 | -122.7997 | 122.4014 | 122.7356 | 122.3694 | 87.1399
2206.8125 | 122.8226 | -122.4701 | 0.33875 | -0.0051118 | -0.013729 | -0.078156 | -0.0063381 | -0.032366 | -0.051235 | -0.040819 | -0.0021057 | -0.018186 | 0.057482 | 0.047117 | -0.21872 | -0.018342 | -0.023253 | -0.14191 | 0.09613 | -0.13275 | -0.15564 | -0.009155 | -0.13733 | -0.050354 | -35.5408 | 0.32959 | -122.5296 | 0.15564 | -121.8613 | -122.3145 | -121.8887 | 122.3373 | -0.24262 | -0.49439 | 122.4609 | 122.4197 | 122.3328 | 0.082397 | -0.004578 | -0.059509 | -0.009155 | -0.18311 | 0.60883 | 0.58136 | 0.15564 | 0.64087 | 0.21515 | 0.1236 | -0.022889 | 0.66833 | 122.6852 | 0.22888 | 122.8592 | 122.5662 | 122.7997 | -0.4715 | -122.8683 | 122.3145 | 122.6257 | 122.3282 | 86.9293
2208.5938 | 122.9095 | -122.4197 | 0.32044 | -0.0051118 | -0.013943 | -0.079865 | -0.0080471 | -0.032793 | -0.04974 | -0.039965 | -0.0021057 | -0.02139 | 0.05855 | 0.041776 | -0.21744 | -0.016205 | -0.019621 | -0.082397 | 0.064087 | -0.091553 | -0.050354 | 0.09613 | -0.09613 | 0.004578 | -35.6873 | 0.3067 | -122.4792 | 0.25635 | -121.7926 | -122.2366 | -121.7972 | 122.3282 | -0.25635 | -0.37079 | 122.5159 | 122.4243 | 122.3236 | 0.096131 | -0.004577 | -0.059509 | -0.013733 | -0.064087 | 0.62714 | 0.62256 | 0.18311 | 0.68207 | 0.24262 | 0.18768 | 0.041199 | 0.68664 | 122.7356 | 0.15564 | 122.7859 | 122.4838 | 122.7264 | -0.41199 | -122.7997 | 122.3694 | 122.6761 | 122.3373 | 86.7325
2210.3438 | 122.9233 | -122.438 | 0.31128 | 0.0025177 | -0.014157 | -0.08136 | -0.0063381 | -0.036638 | -0.052731 | -0.041246 | -0.0021057 | -0.022031 | 0.055773 | 0.050321 | -0.2183 | -0.014496 | -0.025389 | -0.054932 | 0.054932 | -0.10986 | -0.022888 | 0.14191 | -0.004578 | 0.059509 | -35.8154 | 0.32501 | -122.4838 | 0.28839 | -121.7377 | -122.1771 | -121.7651 | 122.3282 | -0.25635 | -0.33417 | 122.58 | 122.4976 | 122.4335 | 0.16937 | 0.10529 | -0.045777 | 0.013733 | -0.022888 | 0.70038 | 0.67291 | 0.26093 | 0.71869 | 0.3067 | 0.25177 | 0.086975 | 0.74615 | 122.7722 | 0.16479 | 122.8088 | 122.493 | 122.7631 | -0.42114 | -122.7951 | 122.4152 | 122.7264 | 122.3831 | 86.6226
2212.125 | 122.9645 | -122.4106 | 0.29755 | -0.0051118 | -0.014584 | -0.077729 | -0.0065517 | -0.031511 | -0.048886 | -0.040605 | -0.0021057 | -0.020108 | 0.058336 | 0.049894 | -0.22001 | -0.015992 | -0.026244 | -0.050354 | 0.082397 | -0.10529 | -0.022888 | 0.14191 | -0.027466 | 0.054932 | -35.9985 | 0.31128 | -122.493 | 0.32044 | -121.7148 | -122.1725 | -121.7514 | 122.3053 | -0.21515 | -0.32043 | 122.5525 | 122.4655 | 122.3831 | 0.16022 | 0.07782 | -0.082398 | 0.013733 | 0.022889 | 0.6958 | 0.65918 | 0.23804 | 0.74158 | 0.32044 | 0.24719 | 0.082398 | 0.7782 | 122.8134 | 0.18768 | 122.8043 | 122.493 | 122.7219 | -0.40283 | -122.7905 | 122.3877 | 122.731 | 122.3602 | 86.412
2213.8906 | 122.8226 | -122.4701 | 0.36163 | 0.0025177 | -0.015225 | -0.078583 | -0.0054837 | -0.032366 | -0.051876 | -0.042955 | -0.0021057 | -0.020322 | 0.058123 | 0.045621 | -0.21937 | -0.015992 | -0.021117 | -0.13733 | 0.091553 | -0.11902 | -0.13275 | 0 | -0.14648 | -0.068665 | -36.3464 | 0.34332 | -122.5342 | 0.16479 | -121.8567 | -122.3145 | -121.9025 | 122.3511 | -0.27008 | -0.49438 | 122.4701 | 122.4014 | 122.3236 | 0.050354 | -0.027465 | -0.064087 | -0.01831 | -0.19684 | 0.6134 | 0.56763 | 0.15564 | 0.63171 | 0.21973 | 0.11902 | -0.013732 | 0.67749 | 122.699 | 0.21057 | 122.8775 | 122.5616 | 122.8134 | -0.48065 | -122.8958 | 122.3373 | 122.6349 | 122.3328 | 86.1237
2215.6719 | 122.9187 | -122.4655 | 0.3067 | 0.0025177 | -0.01138 | -0.078583 | -0.0059109 | -0.03322 | -0.049954 | -0.042955 | -0.0051575 | -0.019681 | 0.059191 | 0.04968 | -0.21979 | -0.016633 | -0.024748 | -0.036621 | 0.07782 | -0.091553 | -0.018311 | 0.12817 | -0.013733 | 0.036621 | -36.4014 | 0.31128 | -122.5113 | 0.27466 | -121.7514 | -122.1954 | -121.788 | 122.374 | -0.22888 | -0.32501 | 122.5937 | 122.5021 | 122.4518 | 0.12817 | 0.07782 | -0.045777 | 0.004577 | -0.032044 | 0.71411 | 0.67749 | 0.27008 | 0.72327 | 0.31586 | 0.21973 | 0.073242 | 0.75989 | 122.7859 | 0.16937 | 122.8226 | 122.5433 | 122.7768 | -0.39825 | -122.818 | 122.4472 | 122.7402 | 122.4289 | 86.0641
2217.3906 | 122.8317 | -122.4792 | 0.3479 | -0.0051118 | -0.015438 | -0.080079 | -0.0033475 | -0.03258 | -0.04974 | -0.040605 | 0.00094606 | -0.019254 | 0.055345 | 0.052457 | -0.22001 | -0.017273 | -0.025176 | -0.14648 | 0.12817 | -0.13275 | -0.16479 | -0.018311 | -0.15106 | -0.091553 | -36.731 | 0.32501 | -122.5296 | 0.16937 | -121.8567 | -122.319 | -121.8887 | 122.3465 | -0.21973 | -0.5127 | 122.4609 | 122.3877 | 122.3282 | 0.041198 | -0.018311 | -0.050354 | -0.022888 | -0.17853 | 0.62256 | 0.59051 | 0.16022 | 0.64087 | 0.21057 | 0.11444 | -0.032044 | 0.67291 | 122.699 | 0.26093 | 122.8546 | 122.6074 | 122.8043 | -0.48065 | -122.8775 | 122.3145 | 122.6486 | 122.3328 | 85.7483
2219.1562 | 122.8638 | -122.4701 | 0.35706 | 0.0025177 | -0.013516 | -0.079011 | -0.0052701 | -0.028948 | -0.050595 | -0.040178 | -0.0051575 | -0.019254 | 0.05855 | 0.049039 | -0.21872 | -0.015778 | -0.022398 | -0.10529 | 0.09613 | -0.11902 | -0.10986 | 0.013733 | -0.13733 | -0.050354 | -36.8591 | 0.34332 | -122.5342 | 0.2243 | -121.8109 | -122.2961 | -121.8521 | 122.3511 | -0.26093 | -0.46692 | 122.4838 | 122.4197 | 122.3328 | 0.068665 | -0.01831 | -0.064087 | -0.013733 | -0.13275 | 0.65918 | 0.61798 | 0.17395 | 0.68207 | 0.23804 | 0.13275 | 0.009156 | 0.72327 | 122.7585 | 0.21515 | 122.8775 | 122.5662 | 122.8134 | -0.47607 | -122.8912 | 122.3602 | 122.6944 | 122.3648 | 85.611
2220.9375 | 122.9416 | -122.4609 | 0.31586 | 0.010147 | -0.012661 | -0.080506 | -0.0080471 | -0.030871 | -0.047604 | -0.040605 | -0.0021057 | -0.021604 | 0.056627 | 0.044553 | -0.21808 | -0.016846 | -0.027312 | -0.064087 | 0.07782 | -0.091553 | -0.009155 | 0.16937 | -0.013733 | 0.041199 | -36.9324 | 0.28839 | -122.4884 | 0.27924 | -121.7239 | -122.1634 | -121.7743 | 122.3694 | -0.23804 | -0.32501 | 122.6303 | 122.5021 | 122.4472 | 0.13275 | 0.07782 | -0.027466 | -0.027466 | -0.036621 | 0.737 | 0.68664 | 0.29755 | 0.71411 | 0.32501 | 0.26093 | 0.082398 | 0.76447 | 122.7676 | 0.16937 | 122.7768 | 122.5388 | 122.7493 | -0.40741 | -122.8043 | 122.4518 | 122.7402 | 122.3969 | 85.5286
2222.7344 | 122.9233 | -122.438 | 0.30212 | 0.010147 | -0.0092435 | -0.079865 | -0.0035611 | -0.02788 | -0.050167 | -0.042955 | -0.0021057 | -0.01904 | 0.059618 | 0.046903 | -0.21958 | -0.015778 | -0.021117 | -0.10986 | 0.11444 | -0.13733 | -0.10529 | 0.013733 | -0.14648 | -0.064087 | -37.1933 | 0.31586 | -122.525 | 0.2655 | -121.7743 | -122.2549 | -121.788 | 122.3007 | -0.18768 | -0.40741 | 122.4518 | 122.374 | 122.2916 | 0.073242 | -0.009155 | -0.086975 | 0.013733 | -0.036621 | 0.66376 | 0.65002 | 0.18311 | 0.737 | 0.27008 | 0.15106 | 0.032043 | 0.75073 | 122.7905 | 0.25177 | 122.8409 | 122.5525 | 122.7539 | -0.43945 | -122.8271 | 122.3328 | 122.7036 | 122.3282 | 85.2448
2224.4531 | 122.9187 | -122.4564 | 0.29755 | -0.0051118 | -0.010952 | -0.079224 | -0.0069791 | -0.028093 | -0.049313 | -0.040819 | -0.0051575 | -0.022458 | 0.056627 | 0.045835 | -0.21872 | -0.018128 | -0.020476 | -0.054932 | 0.064087 | -0.082397 | -0.027466 | 0.12817 | -0.059509 | 0.022888 | -37.294 | 0.28839 | -122.5021 | 0.30212 | -121.7789 | -122.2183 | -121.788 | 122.374 | -0.23346 | -0.32501 | 122.5845 | 122.4792 | 122.3969 | 0.10528 | 0.022888 | -0.045776 | -0.009155 | 0.004578 | 0.67749 | 0.66833 | 0.23804 | 0.71411 | 0.28381 | 0.21057 | 0.054931 | 0.72327 | 122.8043 | 0.14648 | 122.7905 | 122.5204 | 122.7448 | -0.37994 | -122.7997 | 122.4289 | 122.7585 | 122.4014 | 85.1624
2226.2344 | 122.8134 | -122.5021 | 0.34332 | -0.0051118 | -0.013729 | -0.080719 | -0.0071927 | -0.031725 | -0.050808 | -0.042742 | 0.00094606 | -0.018399 | 0.05855 | 0.041563 | -0.21766 | -0.015778 | -0.025176 | -0.13275 | 0.1236 | -0.13733 | -0.16022 | -0.032043 | -0.15564 | -0.07782 | -37.6099 | 0.33875 | -122.5433 | 0.15564 | -121.8567 | -122.3145 | -121.875 | 122.3648 | -0.21973 | -0.50354 | 122.4701 | 122.4243 | 122.3465 | 0.059509 | -0.018311 | -0.041199 | -0.004578 | -0.18768 | 0.64545 | 0.62714 | 0.18768 | 0.66833 | 0.22888 | 0.10529 | -0.022888 | 0.68665 | 122.699 | 0.26093 | 122.8821 | 122.6257 | 122.8409 | -0.48065 | -122.8867 | 122.3419 | 122.6578 | 122.3694 | 84.8923
2227.9688 | 122.9416 | -122.4289 | 0.3067 | 0.0025177 | -0.015225 | -0.079865 | -0.0086879 | -0.031511 | -0.049954 | -0.038469 | -0.0082091 | -0.021604 | 0.057695 | 0.041135 | -0.22193 | -0.017914 | -0.019408 | -0.059509 | 0.054932 | -0.10071 | 0 | 0.17853 | 0.018311 | 0.059509 | -37.6373 | 0.28381 | -122.4976 | 0.27466 | -121.7056 | -122.1634 | -121.7743 | 122.3282 | -0.25177 | -0.3067 | 122.6074 | 122.4884 | 122.4472 | 0.16022 | 0.11902 | -0.068665 | -0.022889 | -0.032044 | 0.72327 | 0.6546 | 0.2655 | 0.72327 | 0.33417 | 0.27924 | 0.10071 | 0.79193 | 122.7722 | 0.15564 | 122.7814 | 122.4838 | 122.7127 | -0.40741 | -122.8043 | 122.4289 | 122.7036 | 122.3694 | 84.7916
2229.75 | 122.9279 | -122.4426 | 0.31128 | -0.012741 | -0.010311 | -0.07837 | -0.0056973 | -0.031298 | -0.051022 | -0.043169 | -0.0051575 | -0.018613 | 0.057268 | 0.053739 | -0.22107 | -0.014069 | -0.023467 | -0.10071 | 0.11444 | -0.13275 | -0.10071 | 0.036621 | -0.13275 | -0.041199 | -37.9669 | 0.3067 | -122.5067 | 0.27466 | -121.7789 | -122.2366 | -121.7834 | 122.3099 | -0.19684 | -0.41199 | 122.4792 | 122.4014 | 122.3099 | 0.091552 | 0 | -0.064087 | -0.004577 | -0.036621 | 0.66376 | 0.65918 | 0.20599 | 0.72327 | 0.27008 | 0.16937 | 0.032043 | 0.72784 | 122.7814 | 0.24719 | 122.8134 | 122.5571 | 122.7493 | -0.44403 | -122.818 | 122.3419 | 122.7173 | 122.3419 | 84.4757
2231.4688 | 122.8821 | -122.4701 | 0.32501 | -0.0051118 | -0.011593 | -0.077302 | -0.0037747 | -0.032793 | -0.050167 | -0.040178 | 0.00094606 | -0.018613 | 0.0562 | 0.050107 | -0.21894 | -0.01471 | -0.024107 | -0.073242 | 0.10071 | -0.10529 | -0.09613 | 0.054932 | -0.10071 | -0.027466 | -38.1042 | 0.31128 | -122.5388 | 0.21973 | -121.7834 | -122.2824 | -121.8384 | 122.3648 | -0.2243 | -0.42114 | 122.525 | 122.4426 | 122.3694 | 0.07782 | 0.004578 | -0.068664 | -0.013733 | -0.10529 | 0.68665 | 0.63171 | 0.18768 | 0.70038 | 0.25635 | 0.16022 | 0.009156 | 0.75531 | 122.7585 | 0.20599 | 122.85 | 122.5708 | 122.7814 | -0.4303 | -122.8638 | 122.374 | 122.6898 | 122.3969 | 84.3658
2233.2656 | 122.8226 | -122.5159 | 0.33875 | 0.0025177 | -0.014798 | -0.077515 | -0.0086879 | -0.033007 | -0.050167 | -0.041674 | -0.0082091 | -0.021176 | 0.057695 | 0.044553 | -0.21637 | -0.015351 | -0.022398 | -0.10986 | 0.07782 | -0.12817 | -0.14648 | 0.022888 | -0.14191 | -0.073242 | -38.3743 | 0.32501 | -122.5388 | 0.15106 | -121.843 | -122.3282 | -121.8933 | 122.3877 | -0.26093 | -0.48523 | 122.5388 | 122.4426 | 122.374 | 0.054932 | -0.013733 | -0.022888 | -0.013733 | -0.18768 | 0.67291 | 0.62256 | 0.18768 | 0.64545 | 0.21057 | 0.15106 | -0.01831 | 0.6958 | 122.6898 | 0.20599 | 122.8638 | 122.5937 | 122.8409 | -0.46692 | -122.8775 | 122.3694 | 122.6669 | 122.406 | 84.1415
2235.0625 | 122.9187 | -122.4976 | 0.3067 | -0.0051118 | -0.012875 | -0.079651 | -0.0061245 | -0.03258 | -0.048672 | -0.042101 | -0.0021057 | -0.02139 | 0.058123 | 0.043485 | -0.22001 | -0.018342 | -0.019835 | -0.073242 | 0.073242 | -0.091553 | -0.045776 | 0.12817 | -0.068665 | 0.022888 | -38.5117 | 0.27924 | -122.5388 | 0.25177 | -121.7789 | -122.2549 | -121.7972 | 122.406 | -0.23346 | -0.35248 | 122.6257 | 122.5204 | 122.4289 | 0.11444 | 0.022888 | -0.041198 | -0.027466 | -0.054932 | 0.71869 | 0.70038 | 0.24262 | 0.74158 | 0.28381 | 0.21973 | 0.045777 | 0.75989 | 122.7905 | 0.16479 | 122.818 | 122.5708 | 122.7768 | -0.39825 | -122.8455 | 122.4518 | 122.7493 | 122.4243 | 83.9859
2236.7812 | 122.85 | -122.4747 | 0.33417 | -0.012741 | -0.011166 | -0.077942 | -0.0029201 | -0.02788 | -0.051022 | -0.040605 | 0.0039979 | -0.017331 | 0.057909 | 0.047971 | -0.22043 | -0.014924 | -0.023253 | -0.086975 | 0.10071 | -0.1236 | -0.11444 | 0.032043 | -0.13733 | -0.073242 | -38.7085 | 0.32501 | -122.5479 | 0.1831 | -121.843 | -122.3282 | -121.8796 | 122.3511 | -0.23346 | -0.44861 | 122.5067 | 122.4014 | 122.3373 | 0.050354 | -0.013733 | -0.073243 | -0.009155 | -0.15106 | 0.63171 | 0.59509 | 0.14648 | 0.66833 | 0.21973 | 0.15564 | 0.009155 | 0.70496 | 122.731 | 0.2243 | 122.8729 | 122.5754 | 122.7997 | -0.45776 | -122.8821 | 122.3602 | 122.6578 | 122.3877 | 83.7662
2238.5625 | 122.8683 | -122.4976 | 0.32044 | 0.0025177 | -0.0096707 | -0.078797 | -0.0044155 | -0.030657 | -0.049954 | -0.04146 | -0.0021057 | -0.017118 | 0.058763 | 0.053953 | -0.21787 | -0.016846 | -0.020049 | -0.07782 | 0.082397 | -0.11444 | -0.07782 | 0.054932 | -0.11444 | -0.050354 | -38.8596 | 0.32501 | -122.5433 | 0.20599 | -121.8109 | -122.319 | -121.8246 | 122.3831 | -0.23804 | -0.39826 | 122.5525 | 122.4472 | 122.3831 | 0.064087 | 0 | -0.045776 | 0.004577 | -0.11444 | 0.68665 | 0.67291 | 0.17853 | 0.71869 | 0.2243 | 0.16937 | 0.036621 | 0.73242 | 122.7493 | 0.19684 | 122.8683 | 122.58 | 122.8226 | -0.43488 | -122.8638 | 122.4197 | 122.7036 | 122.4197 | 83.638
2240.3594 | 122.9553 | -122.4518 | 0.27924 | -0.012741 | -0.012661 | -0.080079 | -0.0076199 | -0.028734 | -0.048886 | -0.041246 | -0.0051575 | -0.022458 | 0.056627 | 0.047544 | -0.21851 | -0.015565 | -0.023253 | -0.050354 | 0.064087 | -0.086975 | -0.027466 | 0.13275 | -0.045776 | 0.018311 | -38.9923 | 0.29297 | -122.4976 | 0.28381 | -121.7194 | -122.2046 | -121.7743 | 122.3648 | -0.21515 | -0.3067 | 122.5845 | 122.4701 | 122.406 | 0.10529 | 0.041199 | -0.045777 | 0.013733 | 0.004577 | 0.73242 | 0.67749 | 0.24719 | 0.72327 | 0.29297 | 0.21973 | 0.059509 | 0.7782 | 122.7814 | 0.15106 | 122.7905 | 122.5159 | 122.7448 | -0.36621 | -122.7768 | 122.4243 | 122.7356 | 122.4014 | 83.4595
2242.1406 | 122.8683 | -122.493 | 0.32959 | 0.0025177 | -0.011593 | -0.079865 | -0.0042019 | -0.029375 | -0.050595 | -0.040178 | -0.0021057 | -0.018186 | 0.055345 | 0.046903 | -0.21979 | -0.015351 | -0.022612 | -0.11902 | 0.09613 | -0.11902 | -0.13733 | -0.004578 | -0.1236 | -0.068665 | -39.2624 | 0.32501 | -122.5388 | 0.19684 | -121.7972 | -122.2778 | -121.8338 | 122.374 | -0.23346 | -0.46692 | 122.4884 | 122.4243 | 122.3694 | 0.050354 | -0.004577 | -0.045776 | -0.004578 | -0.13275 | 0.6958 | 0.65918 | 0.21515 | 0.70496 | 0.26093 | 0.11444 | -0.01831 | 0.74158 | 122.7356 | 0.21515 | 122.8638 | 122.5891 | 122.818 | -0.44861 | -122.8683 | 122.3557 | 122.6898 | 122.374 | 83.2306
2243.9375 | 122.8775 | -122.4884 | 0.32959 | 0.010147 | -0.012234 | -0.078156 | -0.0054837 | -0.028734 | -0.047817 | -0.040605 | 0.00094606 | -0.020322 | 0.05855 | 0.052244 | -0.22022 | -0.017273 | -0.022826 | -0.082397 | 0.11444 | -0.11444 | -0.10071 | 0.041199 | -0.10529 | -0.045776 | -39.4043 | 0.31586 | -122.5204 | 0.21973 | -121.7789 | -122.2916 | -121.843 | 122.374 | -0.21515 | -0.4303 | 122.5296 | 122.4426 | 122.3831 | 0.068665 | 0.009155 | -0.032044 | -0.013733 | -0.10986 | 0.70953 | 0.64545 | 0.19684 | 0.67749 | 0.22888 | 0.15564 | 0.013733 | 0.74158 | 122.7402 | 0.22888 | 122.8363 | 122.6028 | 122.8043 | -0.44403 | -122.85 | 122.3877 | 122.7081 | 122.406 | 83.0841
2245.6562 | 122.9691 | -122.4655 | 0.32044 | -0.0051118 | -0.014584 | -0.080933 | -0.010611 | -0.028948 | -0.051022 | -0.042742 | -0.0082091 | -0.023313 | 0.057695 | 0.041776 | -0.21851 | -0.018769 | -0.023253 | -0.054932 | 0.059509 | -0.09613 | -0.018311 | 0.15106 | -0.013733 | 0.045776 | -39.505 | 0.29297 | -122.4884 | 0.28381 | -121.6873 | -122.1771 | -121.7743 | 122.3694 | -0.26093 | -0.33875 | 122.6166 | 122.5113 | 122.4518 | 0.14191 | 0.082397 | -0.022888 | -0.027466 | -0.036622 | 0.7782 | 0.69122 | 0.28839 | 0.71411 | 0.31128 | 0.24719 | 0.077819 | 0.80109 | 122.7722 | 0.15564 | 122.7814 | 122.525 | 122.7585 | -0.41657 | -122.8088 | 122.4472 | 122.7493 | 122.4106 | 82.9605
2247.4375 | 122.9233 | -122.4701 | 0.31128 | 0.0025177 | -0.013302 | -0.079865 | -0.0063381 | -0.032152 | -0.048886 | -0.041246 | 0.0039979 | -0.020749 | 0.05855 | 0.046689 | -0.21937 | -0.016419 | -0.021117 | -0.10986 | 0.073242 | -0.10529 | -0.09613 | 0.054932 | -0.10529 | -0.013733 | -39.798 | 0.28839 | -122.525 | 0.22888 | -121.7651 | -122.2321 | -121.8109 | 122.3648 | -0.23804 | -0.40741 | 122.525 | 122.4564 | 122.3648 | 0.091553 | 0 | -0.054931 | -0.022888 | -0.082397 | 0.70496 | 0.65918 | 0.23804 | 0.71411 | 0.29297 | 0.16022 | 0.009156 | 0.75989 | 122.7539 | 0.17853 | 122.8134 | 122.5433 | 122.7585 | -0.41656 | -122.8363 | 122.374 | 122.699 | 122.3602 | 82.6721
2249.2188 | 122.9553 | -122.4655 | 0.29297 | -0.0051118 | -0.0090299 | -0.077729 | -0.0061245 | -0.029162 | -0.049526 | -0.042101 | -0.0051575 | -0.020322 | 0.057482 | 0.048185 | -0.22065 | -0.016633 | -0.022826 | -0.041199 | 0.064087 | -0.07782 | -0.013733 | 0.13275 | -0.045776 | 0.022888 | -39.8987 | 0.27924 | -122.5204 | 0.27924 | -121.7285 | -122.2046 | -121.7743 | 122.3877 | -0.22888 | -0.3067 | 122.5983 | 122.4884 | 122.4197 | 0.10071 | 0.032044 | -0.054932 | -0.013733 | -0.013733 | 0.737 | 0.69122 | 0.26093 | 0.74616 | 0.31586 | 0.21057 | 0.064087 | 0.79193 | 122.7997 | 0.14191 | 122.7997 | 122.5296 | 122.7448 | -0.37079 | -122.8134 | 122.4518 | 122.7448 | 122.4243 | 82.5668
2250.9375 | 122.9187 | -122.4747 | 0.29297 | -0.0051118 | -0.012875 | -0.080933 | -0.0065517 | -0.031939 | -0.04974 | -0.042314 | -0.0021057 | -0.022031 | 0.0562 | 0.042417 | -0.21894 | -0.015992 | -0.021758 | -0.10071 | 0.082397 | -0.09613 | -0.09613 | 0.050354 | -0.091553 | -0.022888 | -40.1688 | 0.29297 | -122.5342 | 0.21057 | -121.7743 | -122.2595 | -121.8246 | 122.3785 | -0.21057 | -0.3891 | 122.525 | 122.4518 | 122.3831 | 0.073242 | 0.004577 | -0.05951 | 0 | -0.082398 | 0.70038 | 0.65002 | 0.21515 | 0.70953 | 0.27466 | 0.14648 | 0 | 0.75989 | 122.7448 | 0.17853 | 122.8271 | 122.5571 | 122.7676 | -0.3891 | -122.8271 | 122.3785 | 122.6852 | 122.374 | 82.3059
2252.7188 | 122.85 | -122.4884 | 0.31128 | -0.0051118 | -0.012661 | -0.080506 | -0.0054837 | -0.034716 | -0.050595 | -0.041246 | -0.0051575 | -0.018399 | 0.057695 | 0.040708 | -0.2215 | -0.016846 | -0.020262 | -0.068665 | 0.07782 | -0.10986 | -0.086975 | 0.059509 | -0.086975 | -0.018311 | -40.3839 | 0.3067 | -122.5342 | 0.16479 | -121.8246 | -122.3099 | -121.8887 | 122.3785 | -0.23346 | -0.39825 | 122.5479 | 122.4701 | 122.4014 | 0.091552 | 0.022888 | -0.045777 | -0.004577 | -0.14648 | 0.66376 | 0.59967 | 0.17853 | 0.64545 | 0.22431 | 0.16937 | 0.022888 | 0.70953 | 122.699 | 0.18768 | 122.8409 | 122.5662 | 122.7951 | -0.42114 | -122.8455 | 122.4014 | 122.6532 | 122.4197 | 82.1045
2254.5 | 122.8775 | -122.4747 | 0.32501 | -0.012741 | -0.0098843 | -0.077302 | -0.0037747 | -0.026171 | -0.051449 | -0.039965 | -0.0021057 | -0.020536 | 0.0562 | 0.050962 | -0.22065 | -0.015137 | -0.024748 | -0.064087 | 0.10529 | -0.11444 | -0.10529 | 0.032043 | -0.11444 | -0.054932 | -40.4892 | 0.32044 | -122.525 | 0.20599 | -121.8155 | -122.3373 | -121.8658 | 122.3602 | -0.21973 | -0.4303 | 122.5067 | 122.4197 | 122.3602 | 0.059509 | 0 | -0.050354 | -0.004577 | -0.11902 | 0.65918 | 0.60883 | 0.13733 | 0.65918 | 0.18768 | 0.14648 | 0.009155 | 0.70953 | 122.731 | 0.21973 | 122.8455 | 122.58 | 122.7951 | -0.43945 | -122.85 | 122.3694 | 122.6807 | 122.4106 | 81.9855
2256.2812 | 122.9187 | -122.4838 | 0.31128 | 0.0025177 | -0.012875 | -0.077302 | -0.0074063 | -0.031511 | -0.048672 | -0.038042 | 0.0039979 | -0.020963 | 0.061113 | 0.04434 | -0.22172 | -0.016633 | -0.023039 | -0.11444 | 0.10071 | -0.10529 | -0.082397 | 0.059509 | -0.091553 | -0.018311 | -40.7959 | 0.2655 | -122.5479 | 0.21515 | -121.7606 | -122.2687 | -121.8292 | 122.3785 | -0.21057 | -0.39368 | 122.5433 | 122.4655 | 122.3923 | 0.086975 | 0.013733 | -0.064087 | -0.045776 | -0.09613 | 0.72327 | 0.6546 | 0.21515 | 0.71869 | 0.27924 | 0.16479 | 0.022889 | 0.78735 | 122.7631 | 0.20599 | 122.8134 | 122.5845 | 122.7493 | -0.41656 | -122.8592 | 122.4014 | 122.699 | 122.3694 | 81.6879
2258.0156 | 122.8546 | -122.4701 | 0.31128 | -0.0051118 | -0.013089 | -0.078583 | -0.0039883 | -0.028521 | -0.049313 | -0.040178 | -0.0021057 | -0.017758 | 0.055773 | 0.048185 | -0.2183 | -0.016846 | -0.02133 | -0.07782 | 0.091553 | -0.14191 | -0.10529 | 0.041199 | -0.11444 | -0.041199 | -40.9424 | 0.31586 | -122.5433 | 0.21973 | -121.7606 | -122.3053 | -121.843 | 122.3282 | -0.21973 | -0.41656 | 122.5113 | 122.4289 | 122.3557 | 0.10071 | 0.027466 | -0.073242 | 0.004578 | -0.091552 | 0.70953 | 0.62714 | 0.1648 | 0.70038 | 0.23804 | 0.18311 | 0.036621 | 0.78278 | 122.7631 | 0.23346 | 122.8592 | 122.5616 | 122.7859 | -0.45319 | -122.8546 | 122.3648 | 122.6898 | 122.3923 | 81.5277
2259.7969 | 122.9507 | -122.4289 | 0.29755 | -0.0051118 | -0.012661 | -0.07837 | -0.0084743 | -0.03258 | -0.048031 | -0.043169 | 0.00094606 | -0.023099 | 0.057268 | 0.045835 | -0.21766 | -0.016205 | -0.023467 | -0.032043 | 0.073242 | -0.09613 | -0.009155 | 0.1236 | -0.045776 | 0.013733 | -41.0522 | 0.29297 | -122.5021 | 0.29755 | -121.7056 | -122.2092 | -121.756 | 122.3328 | -0.2243 | -0.3067 | 122.5525 | 122.4426 | 122.3831 | 0.10986 | 0.050354 | -0.073242 | -0.004577 | 0 | 0.72327 | 0.67291 | 0.21973 | 0.74615 | 0.29297 | 0.21973 | 0.086975 | 0.79651 | 122.7997 | 0.16937 | 122.7951 | 122.5021 | 122.7219 | -0.39368 | -122.7997 | 122.4197 | 122.7264 | 122.3969 | 81.3766
2261.5 | 122.937 | -122.4838 | 0.30212 | 0.0025177 | -0.016507 | -0.078797 | -0.010397 | -0.033434 | -0.049313 | -0.042314 | -0.0021057 | -0.020322 | 0.057482 | 0.038785 | -0.21894 | -0.016205 | -0.027525 | -0.059509 | 0.064087 | -0.07782 | -0.027466 | 0.13733 | -0.018311 | 0.036621 | -41.2766 | 0.28839 | -122.5296 | 0.24719 | -121.6919 | -122.1909 | -121.7926 | 122.406 | -0.23804 | -0.32959 | 122.6212 | 122.5204 | 122.4655 | 0.11444 | 0.059509 | -0.045776 | -0.013733 | -0.054932 | 0.79193 | 0.69122 | 0.29297 | 0.737 | 0.33875 | 0.21515 | 0.050354 | 0.83771 | 122.7768 | 0.14191 | 122.818 | 122.5479 | 122.7722 | -0.37994 | -122.8317 | 122.4564 | 122.731 | 122.4243 | 81.2073
2263.2812 | 122.9462 | -122.4655 | 0.31128 | -0.02037 | -0.01138 | -0.083497 | -0.0052701 | -0.02788 | -0.050808 | -0.042314 | 0.00094606 | -0.02139 | 0.057482 | 0.048398 | -0.21872 | -0.019623 | -0.025176 | -0.09613 | 0.091553 | -0.10529 | -0.091553 | 0.064087 | -0.07782 | -0.022888 | -41.4917 | 0.28381 | -122.5433 | 0.24261 | -121.7377 | -122.2549 | -121.8018 | 122.3602 | -0.21973 | -0.40283 | 122.5296 | 122.4426 | 122.3877 | 0.082398 | 0.027466 | -0.07782 | -0.027466 | -0.068664 | 0.72784 | 0.66376 | 0.21057 | 0.74158 | 0.28839 | 0.16937 | 0.013733 | 0.80566 | 122.7859 | 0.19684 | 122.8271 | 122.5571 | 122.7493 | -0.41656 | -122.8546 | 122.374 | 122.7081 | 122.3694 | 80.9738
2265.0625 | 122.9095 | -122.5113 | 0.30212 | -0.0051118 | -0.012875 | -0.079865 | -0.0048427 | -0.034289 | -0.051663 | -0.038256 | 0.00094606 | -0.020108 | 0.057695 | 0.041349 | -0.22022 | -0.015778 | -0.023894 | -0.091553 | 0.082397 | -0.082397 | -0.073242 | 0.073242 | -0.091553 | -0.013733 | -41.7114 | 0.2655 | -122.5433 | 0.22888 | -121.7468 | -122.2687 | -121.8246 | 122.4289 | -0.21973 | -0.37537 | 122.5845 | 122.4976 | 122.4197 | 0.068664 | -0.009156 | -0.032043 | -0.036621 | -0.073242 | 0.76447 | 0.68665 | 0.24262 | 0.71869 | 0.27466 | 0.15564 | 0.009155 | 0.79651 | 122.7722 | 0.16479 | 122.8088 | 122.5937 | 122.7768 | -0.38452 | -122.8455 | 122.4381 | 122.7402 | 122.4197 | 80.7999
2266.7812 | 122.9645 | -122.4564 | 0.2655 | 0.0025177 | -0.010311 | -0.078583 | -0.0050565 | -0.028093 | -0.051022 | -0.038042 | -0.0021057 | -0.019467 | 0.056414 | 0.048398 | -0.22214 | -0.014283 | -0.026457 | -0.032043 | 0.068665 | -0.086975 | -0.027466 | 0.10529 | -0.073242 | 0.018311 | -41.8076 | 0.28381 | -122.5159 | 0.29755 | -121.6965 | -122.2183 | -121.7468 | 122.3694 | -0.19684 | -0.29297 | 122.5616 | 122.4747 | 122.3831 | 0.10529 | 0.013733 | -0.059509 | 0.01831 | 0.032043 | 0.75989 | 0.70953 | 0.23804 | 0.76904 | 0.29755 | 0.19226 | 0.059509 | 0.8194 | 122.8134 | 0.15564 | 122.7997 | 122.525 | 122.7402 | -0.35248 | -122.7814 | 122.4289 | 122.7539 | 122.4243 | 80.6488
2268.5469 | 123.0011 | -122.4884 | 0.28839 | -0.0051118 | -0.01672 | -0.080506 | -0.0084743 | -0.031725 | -0.051449 | -0.041674 | -0.0021057 | -0.020749 | 0.055986 | 0.048398 | -0.22257 | -0.015992 | -0.024107 | -0.050354 | 0.064087 | -0.11444 | -0.009155 | 0.16022 | -0.013733 | 0.045776 | -41.9266 | 0.27924 | -122.5388 | 0.27924 | -121.6553 | -122.1634 | -121.7651 | 122.374 | -0.2243 | -0.29755 | 122.6486 | 122.5342 | 122.4747 | 0.16022 | 0.10071 | -0.050354 | -0.009155 | -0.009155 | 0.83313 | 0.72327 | 0.32501 | 0.77362 | 0.37537 | 0.27466 | 0.10529 | 0.88348 | 122.818 | 0.17853 | 122.818 | 122.5525 | 122.7676 | -0.40283 | -122.8271 | 122.4792 | 122.7676 | 122.438 | 80.5618
2270.3281 | 122.8867 | -122.525 | 0.33417 | -0.0051118 | -0.01138 | -0.080292 | -0.0039883 | -0.027453 | -0.050595 | -0.042955 | -0.0051575 | -0.019254 | 0.056414 | 0.055234 | -0.22043 | -0.017273 | -0.02368 | -0.09613 | 0.11444 | -0.1236 | -0.12817 | -0.027466 | -0.14191 | -0.073242 | -42.2424 | 0.32501 | -122.5754 | 0.17853 | -121.7834 | -122.319 | -121.8567 | 122.4014 | -0.21973 | -0.46234 | 122.4976 | 122.4518 | 122.3831 | 0.050354 | -0.018311 | -0.050354 | -0.009155 | -0.15564 | 0.74158 | 0.66833 | 0.20599 | 0.71869 | 0.25635 | 0.09613 | -0.004578 | 0.79193 | 122.7539 | 0.23804 | 122.9004 | 122.6395 | 122.85 | -0.45776 | -122.9095 | 122.3969 | 122.7036 | 122.4289 | 80.2826
2272.0469 | 122.9462 | -122.4792 | 0.29755 | -0.0051118 | -0.013729 | -0.08136 | -0.0067653 | -0.031298 | -0.049099 | -0.04381 | 0.00094606 | -0.020536 | 0.056841 | 0.043272 | -0.21958 | -0.014924 | -0.019835 | -0.054932 | 0.07782 | -0.091553 | -0.013733 | 0.16022 | -0.004578 | 0.045776 | -42.3248 | 0.27466 | -122.5204 | 0.2655 | -121.6782 | -122.1909 | -121.7789 | 122.3877 | -0.21973 | -0.31128 | 122.6395 | 122.525 | 122.4747 | 0.13733 | 0.086975 | -0.041199 | -0.022888 | -0.032043 | 0.80109 | 0.70038 | 0.28839 | 0.74158 | 0.32959 | 0.25177 | 0.07782 | 0.84229 | 122.7859 | 0.16937 | 122.7951 | 122.5571 | 122.7539 | -0.3891 | -122.818 | 122.4655 | 122.7448 | 122.4243 | 80.1544
2273.8438 | 122.9416 | -122.4701 | 0.28381 | -0.012741 | -0.014798 | -0.079651 | -0.0093289 | -0.03023 | -0.052517 | -0.040392 | 0.0039979 | -0.019895 | 0.055773 | 0.042631 | -0.22086 | -0.015351 | -0.022185 | -0.091553 | 0.07782 | -0.1236 | -0.091553 | 0.068665 | -0.091553 | 0 | -42.6819 | 0.27008 | -122.5479 | 0.2243 | -121.7285 | -122.2549 | -121.8109 | 122.3465 | -0.20599 | -0.37537 | 122.5388 | 122.4701 | 122.3785 | 0.1236 | 0.032043 | -0.07782 | -0.013732 | -0.059509 | 0.74158 | 0.65918 | 0.21515 | 0.737 | 0.29297 | 0.19226 | 0.032043 | 0.8194 | 122.7722 | 0.20142 | 122.818 | 122.5479 | 122.7402 | -0.40741 | -122.8317 | 122.3785 | 122.6944 | 122.3785 | 79.7882
2275.625 | 122.9553 | -122.493 | 0.27924 | 0.0025177 | -0.015652 | -0.078583 | -0.010183 | -0.031511 | -0.049313 | -0.040392 | -0.0051575 | -0.020749 | 0.057482 | 0.048185 | -0.22172 | -0.016846 | -0.024748 | -0.050354 | 0.059509 | -0.082397 | 0 | 0.15564 | -0.004578 | 0.036621 | -42.7322 | 0.27466 | -122.5479 | 0.27466 | -121.6827 | -122.2092 | -121.788 | 122.4106 | -0.21973 | -0.27924 | 122.6486 | 122.5296 | 122.4884 | 0.11902 | 0.077819 | -0.054932 | -0.004578 | -0.004578 | 0.81024 | 0.70496 | 0.28381 | 0.75989 | 0.33875 | 0.23804 | 0.082397 | 0.86517 | 122.8226 | 0.14191 | 122.8226 | 122.5525 | 122.7676 | -0.36163 | -122.8271 | 122.493 | 122.7676 | 122.4426 | 79.7607
2277.3594 | 122.85 | -122.5159 | 0.32501 | 0.0025177 | -0.014157 | -0.080079 | -0.0056973 | -0.030871 | -0.051022 | -0.042101 | 0.0039979 | -0.019467 | 0.05855 | 0.044553 | -0.21851 | -0.017701 | -0.02368 | -0.054932 | 0.073242 | -0.11444 | -0.073242 | 0.082397 | -0.068665 | 0 | -42.9703 | 0.31128 | -122.5616 | 0.17395 | -121.7834 | -122.3145 | -121.8887 | 122.4014 | -0.25177 | -0.39825 | 122.5983 | 122.5159 | 122.4472 | 0.11444 | 0.045776 | -0.045777 | -0.013733 | -0.15106 | 0.73242 | 0.62714 | 0.20142 | 0.67291 | 0.24719 | 0.19684 | 0.041199 | 0.7782 | 122.7356 | 0.18768 | 122.8729 | 122.5891 | 122.8271 | -0.43945 | -122.8867 | 122.4426 | 122.6898 | 122.4609 | 79.5456
2279.1406 | 122.8592 | -122.5113 | 0.3067 | -0.0051118 | -0.011593 | -0.079011 | -0.0035611 | -0.031298 | -0.05209 | -0.041887 | -0.0021057 | -0.017758 | 0.059191 | 0.050535 | -0.21851 | -0.016846 | -0.02133 | -0.10071 | 0.11902 | -0.13733 | -0.16022 | -0.050354 | -0.19684 | -0.10071 | -43.2358 | 0.32044 | -122.5845 | 0.16022 | -121.843 | -122.3831 | -121.8979 | 122.374 | -0.18768 | -0.46692 | 122.4609 | 122.4106 | 122.3145 | 0.036621 | -0.059509 | -0.073242 | 0.013733 | -0.14648 | 0.66833 | 0.6134 | 0.12817 | 0.68665 | 0.20142 | 0.086975 | -0.022888 | 0.74158 | 122.7448 | 0.25635 | 122.905 | 122.6303 | 122.8317 | -0.44403 | -122.8912 | 122.3511 | 122.6715 | 122.4106 | 79.2755
2280.9219 | 122.8363 | -122.5296 | 0.32501 | 0.0025177 | -0.013302 | -0.081574 | -0.0052701 | -0.032366 | -0.051022 | -0.040392 | -0.0021057 | -0.019681 | 0.057482 | 0.048826 | -0.21808 | -0.015351 | -0.023467 | -0.15106 | 0.11444 | -0.14648 | -0.16479 | -0.009155 | -0.14648 | -0.064087 | -43.428 | 0.32044 | -122.5845 | 0.12817 | -121.8155 | -122.3648 | -121.907 | 122.3831 | -0.21057 | -0.48981 | 122.5204 | 122.4655 | 122.3831 | 0.082397 | 0 | -0.054932 | -0.004577 | -0.19684 | 0.71411 | 0.62256 | 0.16479 | 0.67749 | 0.21973 | 0.13733 | -0.018311 | 0.76904 | 122.7127 | 0.26093 | 122.905 | 122.644 | 122.85 | -0.4715 | -122.9095 | 122.3648 | 122.6578 | 122.3785 | 79.1016
2282.6406 | 122.9141 | -122.5113 | 0.28381 | 0.0025177 | -0.013089 | -0.077942 | -0.0089017 | -0.030871 | -0.052517 | -0.040605 | -0.0051575 | -0.020108 | 0.058763 | 0.041563 | -0.21979 | -0.01706 | -0.024321 | -0.068665 | 0.068665 | -0.10071 | -0.064087 | 0.10529 | -0.09613 | -0.004578 | -43.5654 | 0.27466 | -122.5662 | 0.2243 | -121.7331 | -122.2687 | -121.8246 | 122.4106 | -0.21515 | -0.3479 | 122.6166 | 122.5067 | 122.4152 | 0.09613 | 0.004578 | -0.054931 | -0.009155 | -0.059509 | 0.7782 | 0.68665 | 0.24262 | 0.74158 | 0.29755 | 0.20599 | 0.036621 | 0.83313 | 122.7905 | 0.16937 | 122.8409 | 122.58 | 122.7859 | -0.38452 | -122.85 | 122.4472 | 122.7356 | 122.4426 | 78.9459
2284.4375 | 122.8912 | -122.4976 | 0.29297 | -0.0051118 | -0.012661 | -0.078797 | -0.0061245 | -0.032793 | -0.051235 | -0.043383 | -0.0021057 | -0.019467 | 0.0609 | 0.050748 | -0.22129 | -0.016846 | -0.024748 | -0.059509 | 0.082397 | -0.09613 | -0.027466 | 0.10986 | -0.027466 | 0.018311 | -43.8309 | 0.26093 | -122.5571 | 0.21057 | -121.7468 | -122.2687 | -121.8475 | 122.4014 | -0.21057 | -0.32043 | 122.6074 | 122.5159 | 122.4701 | 0.11444 | 0.068664 | -0.059509 | -0.032044 | -0.082398 | 0.75073 | 0.65002 | 0.22888 | 0.70953 | 0.28839 | 0.20599 | 0.068664 | 0.81024 | 122.7676 | 0.17853 | 122.818 | 122.58 | 122.7585 | -0.3891 | -122.85 | 122.4701 | 122.7081 | 122.438 | 78.6667
2286.1562 | 122.9279 | -122.4747 | 0.27008 | 0.0025177 | -0.011593 | -0.081788 | -0.0050565 | -0.032793 | -0.049099 | -0.04146 | -0.0051575 | -0.020963 | 0.057909 | 0.042844 | -0.22065 | -0.014283 | -0.023253 | -0.054932 | 0.064087 | -0.07782 | -0.013733 | 0.11902 | -0.054932 | 0.022888 | -43.895 | 0.24719 | -122.5525 | 0.25635 | -121.7377 | -122.2641 | -121.8109 | 122.3969 | -0.20599 | -0.28381 | 122.5937 | 122.4976 | 122.4197 | 0.10071 | 0.022888 | -0.07782 | -0.022889 | -0.013733 | 0.737 | 0.66376 | 0.21057 | 0.74158 | 0.28839 | 0.19684 | 0.064087 | 0.81482 | 122.8088 | 0.14191 | 122.7997 | 122.5388 | 122.7219 | -0.3479 | -122.8226 | 122.4609 | 122.731 | 122.4197 | 78.5797
2287.9531 | 122.9233 | -122.493 | 0.28381 | 0.0025177 | -0.012448 | -0.079224 | -0.0061245 | -0.028948 | -0.050808 | -0.042314 | -0.0082091 | -0.021604 | 0.057268 | 0.047971 | -0.22022 | -0.017273 | -0.024107 | -0.091553 | 0.086975 | -0.10986 | -0.086975 | 0.054932 | -0.09613 | -0.022888 | -44.2291 | 0.27008 | -122.5525 | 0.19684 | -121.7514 | -122.2778 | -121.8475 | 122.3831 | -0.19684 | -0.37079 | 122.5479 | 122.4701 | 122.3969 | 0.086975 | 0.013733 | -0.059509 | -0.013732 | -0.086975 | 0.74158 | 0.64545 | 0.21515 | 0.70496 | 0.27466 | 0.16479 | 0.022888 | 0.80109 | 122.7493 | 0.19684 | 122.8226 | 122.58 | 122.7631 | -0.39368 | -122.8363 | 122.406 | 122.6898 | 122.4014 | 78.2639
2289.7344 | 122.9874 | -122.4747 | 0.27924 | 0.0025177 | -0.013516 | -0.079224 | -0.0084743 | -0.035357 | -0.050381 | -0.041246 | 0.00094606 | -0.021176 | 0.057482 | 0.041349 | -0.22129 | -0.016846 | -0.026244 | -0.050354 | 0.091553 | -0.10986 | -0.013733 | 0.16022 | -0.009155 | 0.050354 | -44.2612 | 0.26093 | -122.5296 | 0.28839 | -121.6553 | -122.2 | -121.7743 | 122.3648 | -0.18768 | -0.29297 | 122.6349 | 122.525 | 122.4655 | 0.16022 | 0.10071 | -0.054932 | -0.018311 | 0.009155 | 0.8194 | 0.70038 | 0.27466 | 0.75531 | 0.32959 | 0.27008 | 0.09613 | 0.87433 | 122.818 | 0.20142 | 122.7905 | 122.5662 | 122.7356 | -0.3891 | -122.8088 | 122.4609 | 122.7631 | 122.4243 | 78.2135
2291.4688 | 122.8867 | -122.5204 | 0.31128 | -0.012741 | -0.011166 | -0.078797 | -0.0037747 | -0.031511 | -0.049313 | -0.041246 | -0.0021057 | -0.017972 | 0.059832 | 0.04434 | -0.22129 | -0.014069 | -0.021971 | -0.11902 | 0.11444 | -0.13275 | -0.13733 | -0.027466 | -0.1831 | -0.082397 | -44.6548 | 0.29297 | -122.5891 | 0.16937 | -121.8155 | -122.374 | -121.8842 | 122.3877 | -0.19684 | -0.44861 | 122.493 | 122.4381 | 122.3373 | 0.050354 | -0.050354 | -0.068664 | -0.01831 | -0.14191 | 0.70496 | 0.63629 | 0.14648 | 0.70496 | 0.21515 | 0.10529 | -0.004578 | 0.77362 | 122.7585 | 0.24719 | 122.8821 | 122.6349 | 122.8134 | -0.44403 | -122.9004 | 122.3831 | 122.6898 | 122.4014 | 77.8656
2293.25 | 122.9691 | -122.5021 | 0.26093 | -0.0051118 | -0.017147 | -0.080079 | -0.0074063 | -0.031725 | -0.051022 | -0.039324 | -0.0021057 | -0.022245 | 0.057695 | 0.046689 | -0.22043 | -0.016205 | -0.020049 | -0.073242 | 0.064087 | -0.082397 | 0 | 0.15564 | 0 | 0.050354 | -44.6365 | 0.2655 | -122.5616 | 0.27466 | -121.6599 | -122.2046 | -121.7972 | 122.4197 | -0.19684 | -0.26093 | 122.6578 | 122.5525 | 122.5021 | 0.13275 | 0.082397 | -0.05951 | 0.004578 | 0.013733 | 0.84228 | 0.70496 | 0.29755 | 0.76447 | 0.35706 | 0.23804 | 0.082397 | 0.90179 | 122.8363 | 0.14648 | 122.8271 | 122.5662 | 122.7676 | -0.34332 | -122.8226 | 122.5021 | 122.7768 | 122.4289 | 77.8656
2295.0312 | 122.9279 | -122.525 | 0.2655 | -0.0051118 | -0.0094571 | -0.083497 | -0.0046291 | -0.035784 | -0.049954 | -0.040605 | -0.0021057 | -0.020322 | 0.057909 | 0.044553 | -0.22065 | -0.017273 | -0.026671 | -0.068665 | 0.064087 | -0.086975 | -0.064087 | 0.10529 | -0.082397 | 0.009155 | -44.9203 | 0.27008 | -122.5616 | 0.21515 | -121.7331 | -122.2778 | -121.8475 | 122.438 | -0.20142 | -0.32959 | 122.6303 | 122.5342 | 122.4426 | 0.09613 | 0.004578 | -0.036622 | 0.004578 | -0.050354 | 0.79193 | 0.67749 | 0.24719 | 0.71411 | 0.28381 | 0.19226 | 0.022888 | 0.82855 | 122.7768 | 0.15106 | 122.8317 | 122.5891 | 122.7951 | -0.35248 | -122.8271 | 122.4609 | 122.7402 | 122.4564 | 77.6047
2296.7344 | 122.9828 | -122.4884 | 0.29297 | -0.0051118 | -0.015652 | -0.075593 | -0.0054837 | -0.033434 | -0.050595 | -0.042314 | 0.00094606 | -0.020963 | 0.057482 | 0.04434 | -0.22043 | -0.016205 | -0.021971 | -0.059509 | 0.064087 | -0.086975 | -0.013733 | 0.16022 | 0 | 0.059509 | -45.0119 | 0.25635 | -122.5525 | 0.2655 | -121.637 | -122.1863 | -121.7834 | 122.4014 | -0.22888 | -0.3067 | 122.6486 | 122.5479 | 122.4884 | 0.14648 | 0.086975 | -0.064087 | -0.036621 | -0.027466 | 0.85144 | 0.70496 | 0.30212 | 0.76904 | 0.36621 | 0.24719 | 0.073242 | 0.91553 | 122.818 | 0.15106 | 122.8088 | 122.5525 | 122.7448 | -0.37994 | -122.8455 | 122.4747 | 122.7539 | 122.4289 | 77.4765
2298.5312 | 122.8455 | -122.5296 | 0.32044 | -0.0051118 | -0.012875 | -0.080719 | -0.0065517 | -0.035784 | -0.051663 | -0.040605 | -0.0021057 | -0.017118 | 0.056414 | 0.046476 | -0.21958 | -0.015137 | -0.02368 | -0.091553 | 0.082397 | -0.10529 | -0.11902 | 0.018311 | -0.11902 | -0.054932 | -45.401 | 0.27924 | -122.5983 | 0.13275 | -121.8018 | -122.3465 | -121.9254 | 122.4243 | -0.23804 | -0.43945 | 122.5479 | 122.4747 | 122.4106 | 0.050354 | -0.013733 | -0.068665 | -0.041199 | -0.18768 | 0.72784 | 0.60425 | 0.1831 | 0.67291 | 0.25177 | 0.1236 | -0.013733 | 0.79651 | 122.731 | 0.18768 | 122.8775 | 122.612 | 122.8088 | -0.42572 | -122.9187 | 122.4106 | 122.6624 | 122.438 | 77.1286
2300.2656 | 122.9599 | -122.5159 | 0.27466 | 0.0025177 | -0.01437 | -0.080079 | -0.0050565 | -0.034502 | -0.049313 | -0.04146 | 0.00094606 | -0.020322 | 0.056627 | 0.052244 | -0.22107 | -0.017273 | -0.022398 | -0.10529 | 0.10529 | -0.10071 | -0.059509 | 0.064087 | -0.07782 | 0 | -45.4742 | 0.27466 | -122.5662 | 0.23804 | -121.701 | -122.2412 | -121.8063 | 122.4152 | -0.16937 | -0.33417 | 122.58 | 122.5159 | 122.438 | 0.10071 | 0.022888 | -0.050354 | 0 | -0.036621 | 0.81482 | 0.70953 | 0.27466 | 0.75989 | 0.32501 | 0.1648 | 0.041199 | 0.86517 | 122.8043 | 0.20599 | 122.8409 | 122.6212 | 122.7905 | -0.37537 | -122.8409 | 122.4564 | 122.7539 | 122.4106 | 77.0416
2302.0312 | 122.9645 | -122.493 | 0.26093 | 0.0025177 | -0.012875 | -0.080506 | -0.0054837 | -0.028734 | -0.048672 | -0.042101 | 0.00094606 | -0.020963 | 0.055559 | 0.043058 | -0.22043 | -0.016633 | -0.026457 | -0.045776 | 0.073242 | -0.10071 | -0.027466 | 0.11444 | -0.068665 | 0.004578 | -45.6116 | 0.24719 | -122.5571 | 0.29297 | -121.6873 | -122.2366 | -121.7743 | 122.3923 | -0.18768 | -0.28839 | 122.6074 | 122.4976 | 122.4243 | 0.10529 | 0.032043 | -0.064087 | -0.013733 | 0.032044 | 0.80566 | 0.71869 | 0.25635 | 0.78278 | 0.32044 | 0.21515 | 0.073242 | 0.86975 | 122.85 | 0.17395 | 122.8043 | 122.5662 | 122.7402 | -0.36163 | -122.818 | 122.4655 | 122.7859 | 122.4472 | 76.8814
2303.8125 | 122.8912 | -122.525 | 0.3067 | 0.017777 | -0.010311 | -0.079438 | -0.0044155 | -0.031725 | -0.049526 | -0.040178 | -0.0021057 | -0.017331 | 0.057482 | 0.048826 | -0.21979 | -0.014496 | -0.022398 | -0.086975 | 0.11444 | -0.1236 | -0.10071 | 0.036621 | -0.10071 | -0.050354 | -45.8542 | 0.28839 | -122.6074 | 0.19684 | -121.7377 | -122.319 | -121.8521 | 122.4014 | -0.19226 | -0.40741 | 122.5616 | 122.4747 | 122.4243 | 0.073242 | 0.022888 | -0.082398 | -0.018311 | -0.10986 | 0.78735 | 0.67291 | 0.20599 | 0.75531 | 0.28839 | 0.16022 | 0.022888 | 0.86975 | 122.8043 | 0.23804 | 122.8958 | 122.6395 | 122.8134 | -0.4303 | -122.9141 | 122.4243 | 122.7219 | 122.438 | 76.6708
2305.5312 | 123.0148 | -122.4655 | 0.25177 | -0.0051118 | -0.015866 | -0.080079 | -0.0071927 | -0.031298 | -0.050595 | -0.037828 | -0.0021057 | -0.021604 | 0.059618 | 0.044767 | -0.21915 | -0.017914 | -0.020262 | -0.064087 | 0.064087 | -0.091553 | -0.018311 | 0.16479 | 0.004578 | 0.054932 | -45.9091 | 0.25635 | -122.5388 | 0.27466 | -121.6461 | -122.2 | -121.7834 | 122.374 | -0.18768 | -0.27008 | 122.6303 | 122.5204 | 122.4701 | 0.14649 | 0.096131 | -0.073242 | 0.004578 | 0.022888 | 0.8194 | 0.68207 | 0.2655 | 0.75531 | 0.33875 | 0.25635 | 0.073242 | 0.89264 | 122.8134 | 0.15564 | 122.7951 | 122.5296 | 122.7219 | -0.34332 | -122.7905 | 122.4472 | 122.7402 | 122.4014 | 76.5564
2307.3125 | 122.8409 | -122.5204 | 0.3067 | -0.012741 | -0.011593 | -0.077515 | -0.0031337 | -0.029162 | -0.051663 | -0.040819 | 0.00094606 | -0.018186 | 0.058763 | 0.055448 | -0.22022 | -0.014069 | -0.023894 | -0.10071 | 0.1236 | -0.14191 | -0.13275 | -0.013733 | -0.16479 | -0.09613 | -46.3074 | 0.28839 | -122.6028 | 0.14191 | -121.8246 | -122.4014 | -121.9116 | 122.3785 | -0.18311 | -0.43945 | 122.5067 | 122.4243 | 122.3557 | 0.045777 | -0.022888 | -0.082397 | -0.018311 | -0.16479 | 0.6958 | 0.60883 | 0.11902 | 0.69122 | 0.20142 | 0.12817 | 0.009156 | 0.7782 | 122.7448 | 0.2655 | 122.8912 | 122.644 | 122.8088 | -0.44861 | -122.9095 | 122.3877 | 122.6624 | 122.4197 | 76.2131
2309.0938 | 122.8729 | -122.525 | 0.29755 | -0.0051118 | -0.01202 | -0.078583 | -0.0056973 | -0.029375 | -0.049526 | -0.04146 | 0.00094606 | -0.019681 | 0.057909 | 0.043912 | -0.21915 | -0.015565 | -0.020262 | -0.082397 | 0.10529 | -0.1236 | -0.086975 | 0.050354 | -0.13275 | -0.059509 | -46.463 | 0.29297 | -122.612 | 0.15564 | -121.7834 | -122.3648 | -121.9025 | 122.4014 | -0.19226 | -0.38452 | 122.5754 | 122.4655 | 122.3923 | 0.064087 | -0.009155 | -0.086976 | -0.004577 | -0.14191 | 0.74158 | 0.62256 | 0.16022 | 0.70953 | 0.24719 | 0.17395 | 0.036621 | 0.82855 | 122.7676 | 0.22888 | 122.905 | 122.6303 | 122.818 | -0.42114 | -122.9095 | 122.438 | 122.6807 | 122.4426 | 76.062
2310.875 | 122.9553 | -122.4838 | 0.26093 | -0.0051118 | -0.011807 | -0.080079 | -0.0059109 | -0.034929 | -0.049313 | -0.042101 | -0.0021057 | -0.022458 | 0.056841 | 0.044767 | -0.21872 | -0.016633 | -0.02368 | -0.041199 | 0.068665 | -0.07782 | -0.022888 | 0.14648 | -0.059509 | 0.013733 | -46.5042 | 0.25177 | -122.58 | 0.25635 | -121.6782 | -122.2412 | -121.8063 | 122.406 | -0.19226 | -0.28381 | 122.6303 | 122.4976 | 122.4243 | 0.091553 | 0.018311 | -0.09613 | -0.009155 | -0.004577 | 0.80566 | 0.67749 | 0.24261 | 0.77362 | 0.33874 | 0.2243 | 0.054932 | 0.90179 | 122.8363 | 0.14649 | 122.8317 | 122.5525 | 122.7356 | -0.33875 | -122.8409 | 122.4609 | 122.7402 | 122.4426 | 75.9796
2312.6719 | 122.8638 | -122.5525 | 0.29755 | -0.012741 | -0.013943 | -0.079438 | -0.0050565 | -0.031511 | -0.050381 | -0.040178 | -0.0021057 | -0.018827 | 0.058123 | 0.04498 | -0.22001 | -0.016205 | -0.022398 | -0.12817 | 0.11902 | -0.14648 | -0.16937 | -0.022888 | -0.14648 | -0.07782 | -46.907 | 0.27466 | -122.6166 | 0.1236 | -121.788 | -122.3557 | -121.9162 | 122.406 | -0.17853 | -0.46692 | 122.5296 | 122.4747 | 122.406 | 0.068664 | 0 | -0.064087 | -0.022888 | -0.17395 | 0.76447 | 0.63629 | 0.19684 | 0.70038 | 0.26093 | 0.1236 | -0.022889 | 0.82855 | 122.7402 | 0.2655 | 122.8912 | 122.6715 | 122.8271 | -0.44403 | -122.9141 | 122.3831 | 122.6761 | 122.4243 | 75.6454
2314.4062 | 122.9416 | -122.5342 | 0.27008 | -0.0051118 | -0.014157 | -0.080506 | -0.0069791 | -0.030443 | -0.050381 | -0.043169 | 0.00094606 | -0.023526 | 0.059404 | 0.046476 | -0.22129 | -0.017701 | -0.024748 | -0.11444 | 0.09613 | -0.086975 | -0.091553 | 0.064087 | -0.09613 | 0 | -47.0261 | 0.25635 | -122.58 | 0.21973 | -121.7148 | -122.2778 | -121.8475 | 122.4472 | -0.17395 | -0.36163 | 122.5983 | 122.5342 | 122.4381 | 0.086975 | -0.009155 | -0.045776 | -0.013733 | -0.050354 | 0.8194 | 0.68665 | 0.25635 | 0.73242 | 0.30212 | 0.15106 | -0.004578 | 0.86517 | 122.7997 | 0.1831 | 122.8363 | 122.6303 | 122.7905 | -0.35706 | -122.85 | 122.4426 | 122.7539 | 122.4197 | 75.5081
2316.1719 | 122.8729 | -122.5525 | 0.28839 | -0.0051118 | -0.016507 | -0.080506 | -0.0067653 | -0.032366 | -0.051449 | -0.042742 | -0.0051575 | -0.020108 | 0.059618 | 0.045194 | -0.22043 | -0.016633 | -0.024321 | -0.064087 | 0.073242 | -0.10071 | -0.064087 | 0.086975 | -0.054932 | 0.013733 | -47.1634 | 0.27466 | -122.5983 | 0.15106 | -121.756 | -122.3282 | -121.8933 | 122.4518 | -0.21515 | -0.35248 | 122.6395 | 122.5662 | 122.4976 | 0.11444 | 0.045776 | -0.045777 | -0.013733 | -0.13733 | 0.79651 | 0.65918 | 0.2243 | 0.70496 | 0.27008 | 0.18768 | 0.036621 | 0.84229 | 122.7493 | 0.17395 | 122.8729 | 122.6257 | 122.8271 | -0.3891 | -122.8867 | 122.4884 | 122.7036 | 122.4884 | 75.3891
2317.9688 | 122.9553 | -122.5021 | 0.26093 | -0.0051118 | -0.011807 | -0.076447 | -0.0039883 | -0.031511 | -0.050381 | -0.039537 | -0.0021057 | -0.022245 | 0.058763 | 0.049039 | -0.21808 | -0.014496 | -0.022612 | -0.050354 | 0.064087 | -0.10071 | -0.018311 | 0.12817 | -0.059509 | 0.036621 | -47.2961 | 0.24261 | -122.5433 | 0.25635 | -121.6782 | -122.2733 | -121.8063 | 122.4014 | -0.19684 | -0.27924 | 122.6303 | 122.5388 | 122.4426 | 0.13733 | 0.041199 | -0.041199 | -0.01831 | -0.004577 | 0.82397 | 0.6958 | 0.22888 | 0.737 | 0.27008 | 0.22888 | 0.082397 | 0.86517 | 122.7997 | 0.1648 | 122.7859 | 122.5662 | 122.7448 | -0.36163 | -122.8043 | 122.4838 | 122.7585 | 122.4518 | 75.206
2319.6875 | 122.9279 | -122.5296 | 0.2655 | 0.0025177 | -0.014798 | -0.080506 | -0.0065517 | -0.031939 | -0.051022 | -0.041674 | 0.0039979 | -0.022672 | 0.059618 | 0.042417 | -0.21958 | -0.016846 | -0.02133 | -0.10071 | 0.082397 | -0.1236 | -0.091553 | 0.064087 | -0.10071 | -0.013733 | -47.6212 | 0.25177 | -122.5708 | 0.1831 | -121.7285 | -122.3007 | -121.8567 | 122.406 | -0.18311 | -0.35706 | 122.5937 | 122.5159 | 122.4289 | 0.10986 | 0.022888 | -0.041199 | -0.013733 | -0.082398 | 0.80109 | 0.67291 | 0.22888 | 0.71411 | 0.27008 | 0.18768 | 0.032043 | 0.84229 | 122.7539 | 0.20599 | 122.8226 | 122.612 | 122.7814 | -0.3891 | -122.8363 | 122.438 | 122.7127 | 122.4289 | 74.9084
2321.4688 | 123.0148 | -122.5159 | 0.24261 | -0.0051118 | -0.013943 | -0.08136 | -0.0080471 | -0.032366 | -0.052304 | -0.039324 | -0.0051575 | -0.022031 | 0.058123 | 0.042417 | -0.22022 | -0.015137 | -0.022398 | -0.045776 | 0.059509 | -0.086975 | -0.013733 | 0.16479 | -0.013733 | 0.059509 | -47.6578 | 0.22888 | -122.58 | 0.26093 | -121.6187 | -122.1817 | -121.7834 | 122.4289 | -0.18311 | -0.25635 | 122.6807 | 122.5754 | 122.5021 | 0.14648 | 0.073242 | -0.064087 | -0.013733 | 0.01831 | 0.89722 | 0.73242 | 0.33417 | 0.79651 | 0.39825 | 0.25177 | 0.073242 | 0.9613 | 122.8409 | 0.14648 | 122.8088 | 122.5754 | 122.7448 | -0.32959 | -122.8226 | 122.5021 | 122.7768 | 122.4701 | 74.8581
2323.25 | 122.8409 | -122.5616 | 0.29297 | -0.0051118 | -0.012875 | -0.079224 | -0.0065517 | -0.03258 | -0.050381 | -0.041246 | 0.00094606 | -0.018827 | 0.058123 | 0.047758 | -0.22086 | -0.015992 | -0.026457 | -0.14191 | 0.10986 | -0.1236 | -0.15564 | -0.009155 | -0.12817 | -0.064087 | -48.0652 | 0.27924 | -122.6028 | 0.091553 | -121.7926 | -122.3694 | -121.9437 | 122.438 | -0.18311 | -0.44861 | 122.5525 | 122.4976 | 122.4335 | 0.059509 | -0.004578 | -0.041198 | -0.013733 | -0.20142 | 0.76904 | 0.61798 | 0.19226 | 0.65918 | 0.23346 | 0.11444 | -0.032044 | 0.81024 | 122.6944 | 0.23346 | 122.8821 | 122.6715 | 122.8409 | -0.41656 | -122.8958 | 122.406 | 122.6532 | 122.4197 | 74.4965
2324.9844 | 122.9279 | -122.5571 | 0.26093 | 0.0025177 | -0.012875 | -0.079651 | -0.0078335 | -0.035784 | -0.053158 | -0.043169 | -0.0051575 | -0.02139 | 0.057695 | 0.049894 | -0.22001 | -0.017273 | -0.020903 | -0.10071 | 0.068665 | -0.09613 | -0.064087 | 0.064087 | -0.10529 | 0 | -48.2254 | 0.24261 | -122.5937 | 0.18768 | -121.7285 | -122.2778 | -121.8475 | 122.4609 | -0.19226 | -0.32501 | 122.6212 | 122.5571 | 122.4518 | 0.09613 | -0.009156 | -0.036621 | -0.01831 | -0.073242 | 0.82855 | 0.70953 | 0.27924 | 0.74616 | 0.31586 | 0.16022 | 0.032043 | 0.86517 | 122.7814 | 0.16479 | 122.8363 | 122.6257 | 122.7997 | -0.35706 | -122.8546 | 122.493 | 122.7448 | 122.4564 | 74.3317
2326.75 | 122.9416 | -122.525 | 0.24261 | 0.0025177 | -0.012661 | -0.077088 | -0.0061245 | -0.029375 | -0.048031 | -0.04146 | 0.00094606 | -0.020322 | 0.056414 | 0.047758 | -0.21979 | -0.015992 | -0.023253 | -0.068665 | 0.064087 | -0.091553 | -0.032043 | 0.1236 | -0.064087 | 0.022888 | -48.3673 | 0.23804 | -122.5662 | 0.25177 | -121.6873 | -122.2687 | -121.8201 | 122.4335 | -0.17853 | -0.27466 | 122.6486 | 122.5479 | 122.4609 | 0.11444 | 0.027466 | -0.041199 | -0.004578 | 0.009155 | 0.83771 | 0.70496 | 0.25635 | 0.74615 | 0.29755 | 0.21515 | 0.05951 | 0.87891 | 122.818 | 0.15564 | 122.8043 | 122.5891 | 122.7631 | -0.33417 | -122.8088 | 122.493 | 122.7768 | 122.4564 | 74.1577
2328.5469 | 122.8683 | -122.5571 | 0.28839 | 0.0025177 | -0.01437 | -0.079011 | -0.0059109 | -0.031725 | -0.050167 | -0.04146 | -0.0021057 | -0.017972 | 0.057482 | 0.04968 | -0.22022 | -0.01706 | -0.022185 | -0.14648 | 0.10071 | -0.13275 | -0.15564 | -0.009155 | -0.15106 | -0.068665 | -48.674 | 0.29755 | -122.6074 | 0.1236 | -121.7789 | -122.3785 | -121.9116 | 122.4243 | -0.18768 | -0.44403 | 122.5479 | 122.4884 | 122.406 | 0.064086 | -0.018311 | -0.050354 | 0.009155 | -0.1648 | 0.7782 | 0.64545 | 0.17853 | 0.6958 | 0.22888 | 0.1236 | -0.022889 | 0.82855 | 122.731 | 0.23346 | 122.905 | 122.6578 | 122.8546 | -0.42114 | -122.8958 | 122.4014 | 122.6807 | 122.4106 | 73.8831
2330.2656 | 122.9279 | -122.525 | 0.27008 | -0.0051118 | -0.012661 | -0.078156 | -0.0061245 | -0.027453 | -0.050167 | -0.042742 | -0.0021057 | -0.022031 | 0.057909 | 0.042203 | -0.21894 | -0.016419 | -0.02368 | -0.091553 | 0.073242 | -0.09613 | -0.07782 | 0.091553 | -0.086975 | -0.009155 | -48.8022 | 0.25177 | -122.612 | 0.19226 | -121.7239 | -122.3007 | -121.8567 | 122.4289 | -0.19684 | -0.3479 | 122.6166 | 122.5159 | 122.438 | 0.086975 | 0.009155 | -0.086976 | -0.018311 | -0.07782 | 0.80109 | 0.66833 | 0.2243 | 0.75531 | 0.31128 | 0.18768 | 0.01831 | 0.88806 | 122.8043 | 0.16937 | 122.8638 | 122.5983 | 122.7768 | -0.36621 | -122.8821 | 122.4472 | 122.7173 | 122.4335 | 73.7228
2332.0469 | 122.8729 | -122.5433 | 0.29297 | 0.0025177 | -0.01138 | -0.079011 | -0.0059109 | -0.031298 | -0.050808 | -0.040819 | -0.0051575 | -0.017331 | 0.057695 | 0.05203 | -0.21872 | -0.018128 | -0.027739 | -0.082397 | 0.086975 | -0.1236 | -0.064087 | 0.064087 | -0.10986 | -0.041199 | -48.9716 | 0.26093 | -122.6028 | 0.17853 | -121.7377 | -122.3465 | -121.8796 | 122.4197 | -0.20599 | -0.35706 | 122.6074 | 122.5021 | 122.4335 | 0.082397 | 0.013733 | -0.059509 | -0.032044 | -0.11444 | 0.80566 | 0.66376 | 0.19684 | 0.72327 | 0.25635 | 0.18768 | 0.059509 | 0.86517 | 122.7814 | 0.21057 | 122.8638 | 122.6303 | 122.8043 | -0.41656 | -122.8958 | 122.4792 | 122.7219 | 122.4609 | 73.5718
2333.8281 | 122.8638 | -122.5479 | 0.31128 | 0.0025177 | -0.0092435 | -0.080079 | -0.0071927 | -0.029375 | -0.05209 | -0.042101 | -0.0021057 | -0.019254 | 0.057268 | 0.046262 | -0.21937 | -0.016419 | -0.020689 | -0.064087 | 0.09613 | -0.10986 | -0.086975 | 0.059509 | -0.082397 | -0.018311 | -49.1821 | 0.27008 | -122.6257 | 0.14648 | -121.7422 | -122.3511 | -121.9162 | 122.438 | -0.21515 | -0.39825 | 122.6074 | 122.5296 | 122.4655 | 0.091552 | 0.027466 | -0.077819 | -0.041198 | -0.16479 | 0.80566 | 0.63171 | 0.19684 | 0.70953 | 0.27466 | 0.16937 | 0.022888 | 0.88348 | 122.7722 | 0.20599 | 122.8958 | 122.644 | 122.818 | -0.42114 | -122.937 | 122.4609 | 122.6944 | 122.4838 | 73.3658
2335.6094 | 122.8638 | -122.5388 | 0.29297 | -0.012741 | -0.0096707 | -0.078583 | -0.0054837 | -0.026384 | -0.049526 | -0.042528 | -0.0021057 | -0.017972 | 0.056414 | 0.059293 | -0.21915 | -0.015565 | -0.025389 | -0.07782 | 0.10071 | -0.13733 | -0.10529 | 0.036621 | -0.13275 | -0.068665 | -49.4064 | 0.25635 | -122.6303 | 0.15564 | -121.7697 | -122.3785 | -121.8887 | 122.4014 | -0.19226 | -0.39825 | 122.5754 | 122.4701 | 122.406 | 0.068664 | 0.004578 | -0.091553 | -0.036621 | -0.13733 | 0.76904 | 0.65002 | 0.16022 | 0.74158 | 0.25177 | 0.17395 | 0.032043 | 0.8606 | 122.7859 | 0.23804 | 122.8867 | 122.6395 | 122.7951 | -0.4303 | -122.9233 | 122.4335 | 122.6944 | 122.4609 | 73.1323
2337.3906 | 122.9782 | -122.5342 | 0.27466 | -0.0051118 | -0.013943 | -0.078156 | -0.0061245 | -0.03258 | -0.051235 | -0.042955 | -0.0051575 | -0.022672 | 0.058763 | 0.043272 | -0.21851 | -0.017487 | -0.025389 | -0.091553 | 0.086975 | -0.09613 | -0.073242 | 0.091553 | -0.064087 | 0.013733 | -49.5667 | 0.23804 | -122.5845 | 0.21057 | -121.6507 | -122.2321 | -121.8063 | 122.4381 | -0.18768 | -0.3479 | 122.6257 | 122.5479 | 122.4701 | 0.10986 | 0.032043 | -0.050354 | -0.036621 | -0.064087 | 0.88348 | 0.72785 | 0.30212 | 0.7782 | 0.35248 | 0.18768 | 0.022888 | 0.93384 | 122.7951 | 0.1831 | 122.8226 | 122.6212 | 122.7722 | -0.37079 | -122.8592 | 122.4609 | 122.7448 | 122.4426 | 72.9675
2339.1094 | 122.8546 | -122.5479 | 0.27924 | 0.010147 | -0.013943 | -0.080719 | -0.0059109 | -0.028734 | -0.04974 | -0.040605 | -0.0021057 | -0.01904 | 0.05855 | 0.046262 | -0.21915 | -0.016419 | -0.025176 | -0.082397 | 0.073242 | -0.11444 | -0.1236 | 0.036621 | -0.091553 | -0.045776 | -49.8367 | 0.27924 | -122.6212 | 0.1236 | -121.756 | -122.3602 | -121.9162 | 122.4335 | -0.20599 | -0.40283 | 122.5845 | 122.5021 | 122.4564 | 0.068665 | 0.022888 | -0.073242 | 0 | -0.15564 | 0.79193 | 0.63171 | 0.18768 | 0.70496 | 0.26093 | 0.15106 | -0.009155 | 0.86517 | 122.7448 | 0.18768 | 122.9004 | 122.6212 | 122.8271 | -0.39368 | -122.9004 | 122.4243 | 122.6715 | 122.4655 | 72.7112
2340.8906 | 122.9233 | -122.5479 | 0.24719 | -0.0051118 | -0.014584 | -0.080506 | -0.0065517 | -0.032793 | -0.051663 | -0.041887 | 0.00094606 | -0.019895 | 0.057482 | 0.050321 | -0.21872 | -0.016205 | -0.023467 | -0.09613 | 0.068665 | -0.10529 | -0.07782 | 0.064087 | -0.086975 | -0.022888 | -50.0198 | 0.24261 | -122.5891 | 0.17853 | -121.701 | -122.3007 | -121.8521 | 122.4426 | -0.17853 | -0.32501 | 122.612 | 122.525 | 122.4609 | 0.082398 | 0.018311 | -0.041198 | -0.004577 | -0.068664 | 0.84686 | 0.6958 | 0.24719 | 0.737 | 0.28839 | 0.16937 | 0.027466 | 0.88806 | 122.7676 | 0.17395 | 122.8317 | 122.6166 | 122.7905 | -0.35248 | -122.8363 | 122.4701 | 122.7264 | 122.4518 | 72.5281
2342.6719 | 122.9965 | -122.5113 | 0.24261 | -0.012741 | -0.01672 | -0.08136 | -0.0078335 | -0.034716 | -0.050808 | -0.03911 | 0.00094606 | -0.022031 | 0.055773 | 0.042844 | -0.21979 | -0.01471 | -0.024107 | -0.059509 | 0.064087 | -0.11444 | -0.004578 | 0.18768 | 0.013733 | 0.068665 | -50.1434 | 0.2243 | -122.58 | 0.23804 | -121.6141 | -122.2321 | -121.7789 | 122.3969 | -0.17853 | -0.24719 | 122.699 | 122.58 | 122.525 | 0.18311 | 0.12817 | -0.068664 | -0.018311 | -0.004578 | 0.89722 | 0.73242 | 0.27924 | 0.80109 | 0.3479 | 0.30212 | 0.10986 | 0.96588 | 122.818 | 0.17853 | 122.8043 | 122.5754 | 122.7356 | -0.35706 | -122.8226 | 122.5067 | 122.7493 | 122.4518 | 72.3679
2344.4844 | 122.8638 | -122.5479 | 0.27924 | -0.0051118 | -0.010098 | -0.078797 | -0.0035611 | -0.030871 | -0.050595 | -0.040605 | -0.0082091 | -0.01904 | 0.05855 | 0.045194 | -0.21894 | -0.014924 | -0.021971 | -0.11902 | 0.11902 | -0.11902 | -0.16022 | -0.022888 | -0.19226 | -0.086975 | -50.528 | 0.28381 | -122.6166 | 0.14191 | -121.7834 | -122.3877 | -121.9025 | 122.4289 | -0.16022 | -0.43945 | 122.525 | 122.4609 | 122.3557 | 0.032044 | -0.073242 | -0.068664 | 0.004577 | -0.13733 | 0.76447 | 0.64545 | 0.16022 | 0.71411 | 0.22888 | 0.096131 | -0.041198 | 0.83313 | 122.7585 | 0.23804 | 122.9004 | 122.6669 | 122.8317 | -0.39825 | -122.8958 | 122.3877 | 122.6898 | 122.4289 | 72.02
2346.2031 | 122.8958 | -122.5662 | 0.30212 | 0.0025177 | -0.012875 | -0.080719 | -0.0071927 | -0.03023 | -0.049313 | -0.04146 | -0.0021057 | -0.018827 | 0.057909 | 0.048826 | -0.21851 | -0.014496 | -0.023467 | -0.09613 | 0.10986 | -0.13275 | -0.11444 | 0.022888 | -0.11444 | -0.054932 | -50.766 | 0.28381 | -122.612 | 0.17395 | -121.6919 | -122.3373 | -121.8704 | 122.4335 | -0.19226 | -0.41657 | 122.5891 | 122.5113 | 122.4518 | 0.077819 | 0.01831 | -0.045777 | -0.018311 | -0.12817 | 0.87433 | 0.6958 | 0.22888 | 0.74158 | 0.27466 | 0.15564 | 0.01831 | 0.9201 | 122.7859 | 0.24261 | 122.8958 | 122.6761 | 122.85 | -0.43488 | -122.9141 | 122.4518 | 122.7402 | 122.4701 | 71.8002
2348 | 122.8363 | -122.5662 | 0.27924 | -0.0051118 | -0.011807 | -0.077515 | -0.0033475 | -0.022539 | -0.050167 | -0.042955 | -0.0021057 | -0.02139 | 0.058123 | 0.045621 | -0.21659 | -0.017701 | -0.020689 | -0.11902 | 0.11444 | -0.14191 | -0.17395 | -0.050354 | -0.19226 | -0.11444 | -51.123 | 0.27008 | -122.6212 | 0.10986 | -121.8063 | -122.4197 | -121.9528 | 122.4243 | -0.16479 | -0.45319 | 122.5159 | 122.4518 | 122.374 | 0.027466 | -0.050354 | -0.054932 | -0.009155 | -0.16937 | 0.75989 | 0.6134 | 0.14648 | 0.66833 | 0.20142 | 0.091553 | -0.032043 | 0.81482 | 122.731 | 0.25635 | 122.8912 | 122.6807 | 122.8363 | -0.42114 | -122.9004 | 122.3923 | 122.6761 | 122.4472 | 71.4432
2349.7812 | 122.9507 | -122.5159 | 0.24719 | -0.0051118 | -0.010739 | -0.076447 | -0.0084743 | -0.035784 | -0.051022 | -0.042742 | -0.0051575 | -0.020963 | 0.058336 | 0.045621 | -0.22065 | -0.013856 | -0.025816 | -0.050354 | 0.073242 | -0.10071 | -0.018311 | 0.14648 | -0.050354 | 0.036621 | -51.1551 | 0.23804 | -122.58 | 0.23804 | -121.6553 | -122.2641 | -121.8201 | 122.4152 | -0.17395 | -0.2655 | 122.6624 | 122.5525 | 122.4655 | 0.13733 | 0.050354 | -0.064087 | -0.009155 | -0.009155 | 0.8606 | 0.6958 | 0.25177 | 0.75989 | 0.31586 | 0.24719 | 0.082397 | 0.92468 | 122.818 | 0.17395 | 122.818 | 122.5891 | 122.7539 | -0.3479 | -122.8271 | 122.4976 | 122.7539 | 122.4655 | 71.3608
2351.5781 | 122.9095 | -122.5388 | 0.27466 | -0.012741 | -0.014798 | -0.079011 | -0.0071927 | -0.030871 | -0.051449 | -0.041887 | -0.0021057 | -0.019895 | 0.058763 | 0.043699 | -0.22065 | -0.01941 | -0.021544 | -0.059509 | 0.073242 | -0.091553 | -0.054932 | 0.10071 | -0.027466 | 0.018311 | -51.3931 | 0.25177 | -122.5937 | 0.16479 | -121.6644 | -122.3007 | -121.8567 | 122.4472 | -0.20142 | -0.32959 | 122.6395 | 122.5571 | 122.5113 | 0.10986 | 0.064087 | -0.054932 | -0.022888 | -0.10986 | 0.87433 | 0.68207 | 0.23804 | 0.737 | 0.29297 | 0.19226 | 0.036621 | 0.92926 | 122.7585 | 0.16479 | 122.8455 | 122.612 | 122.7905 | -0.36621 | -122.8683 | 122.4838 | 122.7036 | 122.4792 | 71.1456
2353.3594 | 122.9782 | -122.5296 | 0.24719 | -0.012741 | -0.013729 | -0.079651 | -0.0059109 | -0.030657 | -0.050167 | -0.040392 | 0.00094606 | -0.021604 | 0.057695 | 0.040494 | -0.21872 | -0.015992 | -0.026885 | -0.10071 | 0.07782 | -0.10986 | -0.073242 | 0.082397 | -0.054932 | 0.013733 | -51.6312 | 0.24719 | -122.5937 | 0.20142 | -121.6461 | -122.2641 | -121.8292 | 122.4197 | -0.16937 | -0.32043 | 122.612 | 122.5433 | 122.4747 | 0.1236 | 0.054931 | -0.064087 | 0 | -0.045776 | 0.88348 | 0.70038 | 0.2655 | 0.76447 | 0.32959 | 0.19226 | 0.036621 | 0.94757 | 122.7951 | 0.18768 | 122.8409 | 122.6074 | 122.7768 | -0.35706 | -122.8409 | 122.4564 | 122.731 | 122.4289 | 70.8984
2355.1562 | 122.9599 | -122.5342 | 0.25177 | 0.0025177 | -0.01437 | -0.080506 | -0.0056973 | -0.031725 | -0.050595 | -0.041246 | 0.00094606 | -0.023099 | 0.055132 | 0.046689 | -0.21872 | -0.013856 | -0.022826 | -0.09613 | 0.082397 | -0.10529 | -0.091553 | 0.073242 | -0.086975 | -0.004578 | -51.8921 | 0.24719 | -122.5891 | 0.18768 | -121.669 | -122.2824 | -121.843 | 122.4289 | -0.16937 | -0.34332 | 122.6074 | 122.5296 | 122.4472 | 0.10071 | 0.018311 | -0.054931 | -0.004578 | -0.064087 | 0.86517 | 0.69122 | 0.25177 | 0.74615 | 0.3067 | 0.17853 | 0.013733 | 0.92011 | 122.7768 | 0.18768 | 122.8363 | 122.6166 | 122.7814 | -0.35706 | -122.8409 | 122.4426 | 122.7219 | 122.4381 | 70.6421
2356.9531 | 122.8821 | -122.5754 | 0.27924 | -0.0051118 | -0.0096707 | -0.078156 | -0.0031337 | -0.031298 | -0.050808 | -0.04146 | -0.0021057 | -0.016904 | 0.058763 | 0.053312 | -0.21937 | -0.015351 | -0.024321 | -0.10986 | 0.11902 | -0.15106 | -0.16937 | -0.032043 | -0.17395 | -0.091553 | -52.2263 | 0.2655 | -122.6028 | 0.12817 | -121.756 | -122.3969 | -121.9162 | 122.4243 | -0.16022 | -0.44861 | 122.5433 | 122.4838 | 122.4014 | 0.059509 | -0.022888 | -0.027466 | -0.013733 | -0.15106 | 0.8194 | 0.65918 | 0.17853 | 0.68664 | 0.20599 | 0.11902 | -0.018311 | 0.84686 | 122.731 | 0.27008 | 122.8683 | 122.6944 | 122.8409 | -0.4303 | -122.8821 | 122.406 | 122.7036 | 122.4655 | 70.3491
2358.7344 | 122.9828 | -122.5204 | 0.25177 | 0.0025177 | -0.015866 | -0.079224 | -0.0080471 | -0.031298 | -0.053372 | -0.039751 | 0.00094606 | -0.019895 | 0.056627 | 0.040067 | -0.22022 | -0.018555 | -0.024321 | -0.054932 | 0.068665 | -0.082397 | 0 | 0.16022 | -0.004578 | 0.059509 | -52.2766 | 0.2243 | -122.5754 | 0.23804 | -121.5912 | -122.2275 | -121.7972 | 122.4381 | -0.1831 | -0.25177 | 122.6807 | 122.58 | 122.5159 | 0.14191 | 0.077819 | -0.054931 | -0.027466 | -0.013733 | 0.92926 | 0.72327 | 0.29297 | 0.7782 | 0.3479 | 0.24261 | 0.082397 | 0.98419 | 122.8134 | 0.15106 | 122.7997 | 122.5891 | 122.7448 | -0.33417 | -122.8271 | 122.5204 | 122.7585 | 122.4655 | 70.2438
2360.4688 | 122.9187 | -122.5433 | 0.25635 | 0.0025177 | -0.013302 | -0.079651 | -0.0074063 | -0.031084 | -0.047817 | -0.039965 | 0.00094606 | -0.021176 | 0.057054 | 0.036436 | -0.21958 | -0.01471 | -0.023039 | -0.10529 | 0.068665 | -0.11444 | -0.073242 | 0.064087 | -0.10986 | 0.004578 | -52.6199 | 0.24261 | -122.612 | 0.18768 | -121.669 | -122.3145 | -121.8658 | 122.4289 | -0.18768 | -0.32959 | 122.6074 | 122.5479 | 122.4335 | 0.11902 | 0.004578 | -0.068665 | -0.013733 | -0.068665 | 0.87433 | 0.67749 | 0.22888 | 0.74616 | 0.29755 | 0.17853 | 0.041199 | 0.94299 | 122.7997 | 0.18311 | 122.8546 | 122.612 | 122.7859 | -0.37079 | -122.8683 | 122.4701 | 122.731 | 122.438 | 69.9234
2362.25 | 122.8867 | -122.5571 | 0.27924 | 0.010147 | -0.012448 | -0.079865 | -0.0037747 | -0.031939 | -0.05209 | -0.042314 | -0.0021057 | -0.016904 | 0.057482 | 0.050321 | -0.21808 | -0.012787 | -0.021971 | -0.07782 | 0.10529 | -0.11902 | -0.07782 | 0.045776 | -0.09613 | -0.036621 | -52.7756 | 0.27466 | -122.6074 | 0.16479 | -121.6965 | -122.3511 | -121.875 | 122.438 | -0.17395 | -0.35706 | 122.6028 | 122.5204 | 122.4609 | 0.082398 | 0.022889 | -0.050354 | -0.004578 | -0.11444 | 0.8606 | 0.68207 | 0.20599 | 0.73242 | 0.25635 | 0.16479 | 0.041199 | 0.91095 | 122.7722 | 0.22431 | 122.8821 | 122.6624 | 122.8317 | -0.39825 | -122.8867 | 122.4792 | 122.7219 | 122.4792 | 69.7815
2363.9844 | 122.8638 | -122.5342 | 0.27466 | -0.012741 | -0.010311 | -0.077515 | -0.0046291 | -0.029375 | -0.051022 | -0.042314 | -0.0082091 | -0.017545 | 0.057695 | 0.049467 | -0.22001 | -0.015565 | -0.018553 | -0.068665 | 0.10071 | -0.1236 | -0.086975 | 0.036621 | -0.12817 | -0.050354 | -53.0182 | 0.26093 | -122.6074 | 0.16479 | -121.7194 | -122.3648 | -121.875 | 122.4106 | -0.17395 | -0.36163 | 122.5708 | 122.4838 | 122.406 | 0.073242 | -0.004578 | -0.073242 | -0.013733 | -0.10986 | 0.81482 | 0.65918 | 0.16937 | 0.73242 | 0.24262 | 0.16022 | 0.036621 | 0.88806 | 122.7722 | 0.2243 | 122.8683 | 122.6349 | 122.7951 | -0.39825 | -122.8821 | 122.4472 | 122.699 | 122.4655 | 69.516
2365.7656 | 122.9507 | -122.58 | 0.25177 | 0.0025177 | -0.014798 | -0.079438 | -0.0082607 | -0.027666 | -0.051663 | -0.041033 | -0.0021057 | -0.021817 | 0.057909 | 0.045835 | -0.21851 | -0.017487 | -0.023253 | -0.11444 | 0.086975 | -0.086975 | -0.09613 | 0.064087 | -0.09613 | -0.009155 | -53.2745 | 0.22888 | -122.6257 | 0.1831 | -121.6415 | -122.2733 | -121.8338 | 122.493 | -0.16479 | -0.3479 | 122.644 | 122.5708 | 122.4838 | 0.07782 | -0.009155 | -0.045776 | -0.022888 | -0.068665 | 0.93841 | 0.74616 | 0.3067 | 0.79193 | 0.35248 | 0.15106 | -0.009155 | 0.98419 | 122.8088 | 0.17395 | 122.8546 | 122.6669 | 122.8088 | -0.33874 | -122.8775 | 122.4838 | 122.7631 | 122.4655 | 69.3054
2367.5625 | 122.9233 | -122.5388 | 0.25177 | -0.012741 | -0.013089 | -0.079651 | -0.0078335 | -0.032152 | -0.051449 | -0.042101 | 0.00094606 | -0.020749 | 0.058336 | 0.040281 | -0.21937 | -0.017273 | -0.022185 | -0.09613 | 0.073242 | -0.082397 | -0.091553 | 0.054932 | -0.091553 | -0.027466 | -53.4897 | 0.25177 | -122.5937 | 0.16022 | -121.6415 | -122.287 | -121.843 | 122.4564 | -0.17853 | -0.34332 | 122.5937 | 122.5113 | 122.4472 | 0.054931 | -0.009156 | -0.054932 | 0 | -0.091553 | 0.89722 | 0.6958 | 0.25177 | 0.75073 | 0.3067 | 0.13733 | -0.009156 | 0.95215 | 122.7539 | 0.15564 | 122.8455 | 122.612 | 122.7905 | -0.33417 | -122.8455 | 122.4472 | 122.699 | 122.4426 | 69.0491
2369.3438 | 122.8546 | -122.5708 | 0.27466 | -0.012741 | -0.012234 | -0.078583 | -0.0024929 | -0.029589 | -0.048672 | -0.040178 | -0.0021057 | -0.016477 | 0.05855 | 0.047971 | -0.21872 | -0.016205 | -0.024321 | -0.13275 | 0.11444 | -0.12817 | -0.16022 | -0.064087 | -0.20142 | -0.09613 | -53.8239 | 0.28381 | -122.5983 | 0.11902 | -121.7514 | -122.406 | -121.9116 | 122.4426 | -0.16022 | -0.43488 | 122.5067 | 122.4747 | 122.3694 | 0.032044 | -0.073242 | -0.027466 | 0.009155 | -0.15564 | 0.8194 | 0.65918 | 0.16479 | 0.68665 | 0.19226 | 0.064087 | -0.032043 | 0.84686 | 122.7173 | 0.24262 | 122.8821 | 122.6852 | 122.8546 | -0.40283 | -122.8729 | 122.4106 | 122.6898 | 122.4381 | 68.7469
2371.0625 | 122.9416 | -122.5479 | 0.25177 | 0.0025177 | -0.013302 | -0.081574 | -0.0069791 | -0.028948 | -0.050595 | -0.041887 | -0.0021057 | -0.022245 | 0.057695 | 0.045835 | -0.2183 | -0.017487 | -0.024962 | -0.10071 | 0.082397 | -0.091553 | -0.07782 | 0.059509 | -0.10071 | -0.009155 | -53.8971 | 0.24261 | -122.5937 | 0.17853 | -121.6461 | -122.3053 | -121.843 | 122.4564 | -0.16937 | -0.32959 | 122.6074 | 122.5388 | 122.4472 | 0.082398 | -0.009155 | -0.045776 | -0.009155 | -0.073242 | 0.90179 | 0.70496 | 0.24262 | 0.75073 | 0.28839 | 0.15106 | 0.013733 | 0.94757 | 122.7722 | 0.17395 | 122.8363 | 122.6303 | 122.7905 | -0.34332 | -122.8455 | 122.4701 | 122.7264 | 122.4472 | 68.6508
2372.8281 | 122.905 | -122.5433 | 0.25635 | 0.010147 | -0.010098 | -0.080506 | -0.0046291 | -0.030657 | -0.050381 | -0.039751 | -0.0021057 | -0.018399 | 0.059618 | 0.047758 | -0.22086 | -0.016846 | -0.023467 | -0.07782 | 0.09613 | -0.13275 | -0.10071 | 0.054932 | -0.09613 | -0.032043 | -54.0802 | 0.26093 | -122.6166 | 0.16937 | -121.6736 | -122.3465 | -121.8796 | 122.4106 | -0.16022 | -0.35706 | 122.5983 | 122.5113 | 122.4472 | 0.10071 | 0.036621 | -0.073242 | 0.004577 | -0.086975 | 0.86975 | 0.66376 | 0.19684 | 0.737 | 0.27008 | 0.18768 | 0.032043 | 0.94299 | 122.7859 | 0.22888 | 122.8775 | 122.6395 | 122.8043 | -0.3891 | -122.8729 | 122.4426 | 122.7127 | 122.4655 | 68.4631
2374.625 | 122.9782 | -122.5433 | 0.24261 | -0.012741 | -0.01138 | -0.076661 | -0.0050565 | -0.031939 | -0.049954 | -0.040178 | -0.0082091 | -0.018399 | 0.059618 | 0.050107 | -0.21937 | -0.013856 | -0.019408 | -0.07782 | 0.09613 | -0.10986 | -0.064087 | 0.082397 | -0.10071 | -0.027466 | -54.3137 | 0.23346 | -122.5754 | 0.23804 | -121.5866 | -122.2687 | -121.7926 | 122.4335 | -0.14649 | -0.3067 | 122.6257 | 122.5159 | 122.4426 | 0.082397 | 0.009155 | -0.032043 | -0.009156 | -0.004578 | 0.95673 | 0.75073 | 0.27466 | 0.78278 | 0.3067 | 0.19226 | 0.045776 | 0.98877 | 122.8134 | 0.20599 | 122.8088 | 122.6395 | 122.7768 | -0.35248 | -122.818 | 122.4792 | 122.7814 | 122.4655 | 68.2297
2376.4062 | 122.8409 | -122.5754 | 0.29297 | 0.0025177 | -0.0088163 | -0.077515 | -0.0044155 | -0.03258 | -0.049526 | -0.038683 | -0.0051575 | -0.019895 | 0.060045 | 0.050535 | -0.21808 | -0.014283 | -0.026671 | -0.1236 | 0.10986 | -0.13733 | -0.16022 | -0.041199 | -0.19226 | -0.10071 | -54.6707 | 0.27924 | -122.612 | 0.1236 | -121.7148 | -122.4106 | -121.9208 | 122.438 | -0.18311 | -0.45319 | 122.5342 | 122.4747 | 122.3831 | 0.036621 | -0.054932 | -0.036622 | -0.013733 | -0.16937 | 0.8606 | 0.6546 | 0.16479 | 0.69122 | 0.20142 | 0.09613 | -0.022888 | 0.89722 | 122.7356 | 0.24719 | 122.8912 | 122.6852 | 122.8546 | -0.4303 | -122.905 | 122.4152 | 122.699 | 122.4518 | 67.9047
2378.125 | 122.9187 | -122.5525 | 0.26093 | -0.012741 | -0.011166 | -0.077302 | -0.0048427 | -0.028093 | -0.048672 | -0.039751 | -0.0021057 | -0.019895 | 0.060045 | 0.043912 | -0.21851 | -0.015137 | -0.020689 | -0.1236 | 0.11444 | -0.1236 | -0.14648 | -0.013733 | -0.17395 | -0.07782 | -54.8538 | 0.24261 | -122.6166 | 0.17395 | -121.6599 | -122.3557 | -121.8475 | 122.4289 | -0.14648 | -0.40741 | 122.5388 | 122.4747 | 122.3785 | 0.045776 | -0.050354 | -0.064087 | -0.01831 | -0.086975 | 0.89264 | 0.70496 | 0.19684 | 0.76904 | 0.26093 | 0.10986 | -0.022888 | 0.95673 | 122.7905 | 0.23804 | 122.8592 | 122.6669 | 122.7951 | -0.38452 | -122.8775 | 122.406 | 122.7264 | 122.4289 | 67.6987
2379.9062 | 122.9691 | -122.5479 | 0.23346 | 0.010147 | -0.015652 | -0.07837 | -0.0080471 | -0.032366 | -0.050808 | -0.04146 | -0.0021057 | -0.021604 | 0.057695 | 0.045621 | -0.21937 | -0.01706 | -0.022826 | -0.10986 | 0.07782 | -0.11444 | -0.09613 | 0.082397 | -0.07782 | 0.013733 | -55.0598 | 0.22888 | -122.612 | 0.19684 | -121.5912 | -122.2687 | -121.8246 | 122.4335 | -0.15564 | -0.32959 | 122.6303 | 122.5616 | 122.4701 | 0.12817 | 0.036621 | -0.064087 | -0.004577 | -0.036621 | 0.95673 | 0.72327 | 0.27924 | 0.78735 | 0.34332 | 0.19684 | 0.018311 | 1.0208 | 122.8088 | 0.19226 | 122.8409 | 122.6257 | 122.7768 | -0.3479 | -122.8455 | 122.4518 | 122.7448 | 122.438 | 67.4881
2381.6875 | 122.8409 | -122.5708 | 0.29755 | -0.0051118 | -0.010098 | -0.078583 | -0.0016385 | -0.029802 | -0.049099 | -0.038896 | -0.0021057 | -0.019895 | 0.059832 | 0.04434 | -0.22086 | -0.01471 | -0.022398 | -0.086975 | 0.10529 | -0.10529 | -0.13275 | 0.009155 | -0.17853 | -0.082397 | -55.3299 | 0.2655 | -122.6212 | 0.10986 | -121.7056 | -122.4014 | -121.907 | 122.4655 | -0.19226 | -0.4303 | 122.58 | 122.4884 | 122.3923 | 0.022889 | -0.073242 | -0.050354 | -0.032043 | -0.18768 | 0.86517 | 0.66376 | 0.16937 | 0.71411 | 0.21973 | 0.11444 | -0.027465 | 0.91553 | 122.731 | 0.21057 | 122.8867 | 122.6761 | 122.8363 | -0.40283 | -122.9187 | 122.4381 | 122.6807 | 122.4838 | 67.2409
2383.4688 | 122.9782 | -122.525 | 0.25635 | -0.0051118 | -0.016079 | -0.079224 | -0.0074063 | -0.031939 | -0.050381 | -0.038683 | 0.00094606 | -0.021176 | 0.059191 | 0.050107 | -0.21979 | -0.017701 | -0.022398 | -0.068665 | 0.068665 | -0.091553 | -0.022888 | 0.15106 | -0.013733 | 0.054932 | -55.4123 | 0.22888 | -122.5891 | 0.2243 | -121.5454 | -122.2321 | -121.788 | 122.4335 | -0.18768 | -0.27924 | 122.6761 | 122.58 | 122.5113 | 0.14649 | 0.07782 | -0.064087 | -0.027466 | -0.032044 | 0.97961 | 0.737 | 0.29297 | 0.80109 | 0.35706 | 0.24261 | 0.068665 | 1.0437 | 122.8134 | 0.16022 | 122.818 | 122.5937 | 122.7539 | -0.3479 | -122.8455 | 122.5021 | 122.7493 | 122.4564 | 67.1127
2385.1875 | 122.9004 | -122.5616 | 0.2655 | -0.0051118 | -0.013302 | -0.080292 | -0.0069791 | -0.03023 | -0.051663 | -0.039324 | -0.0051575 | -0.019681 | 0.058977 | 0.050748 | -0.2215 | -0.015992 | -0.021758 | -0.11444 | 0.11902 | -0.15564 | -0.13275 | 0.009155 | -0.11444 | -0.054932 | -55.7556 | 0.27008 | -122.6349 | 0.16022 | -121.6461 | -122.3373 | -121.8796 | 122.406 | -0.14648 | -0.39825 | 122.5708 | 122.5067 | 122.4472 | 0.10071 | 0.041199 | -0.073242 | 0.004578 | -0.10529 | 0.91553 | 0.68207 | 0.22431 | 0.75531 | 0.29755 | 0.16479 | 0.022889 | 0.98877 | 122.7951 | 0.27466 | 122.905 | 122.6807 | 122.8317 | -0.42114 | -122.9004 | 122.4289 | 122.7219 | 122.4472 | 66.806
2386.9688 | 122.9965 | -122.5479 | 0.24719 | -0.0051118 | -0.0094571 | -0.077729 | -0.0063381 | -0.02553 | -0.048886 | -0.041887 | -0.0051575 | -0.020108 | 0.058123 | 0.047544 | -0.22065 | -0.015778 | -0.020049 | -0.045776 | 0.068665 | -0.07782 | -0.045776 | 0.10529 | -0.068665 | 0.009155 | -55.8334 | 0.21973 | -122.6028 | 0.24719 | -121.5637 | -122.2504 | -121.7606 | 122.4701 | -0.17853 | -0.29297 | 122.6532 | 122.5571 | 122.4792 | 0.086975 | 0.009155 | -0.054931 | -0.027465 | 0 | 0.98419 | 0.78735 | 0.29755 | 0.84229 | 0.35248 | 0.18311 | 0.032044 | 1.0391 | 122.85 | 0.14649 | 122.8226 | 122.6166 | 122.7676 | -0.32501 | -122.85 | 122.5021 | 122.7951 | 122.5021 | 66.7145
2388.75 | 122.9324 | -122.5388 | 0.24261 | 0.0025177 | -0.011593 | -0.079011 | -0.0065517 | -0.032793 | -0.049954 | -0.04381 | -0.0021057 | -0.023313 | 0.057482 | 0.038358 | -0.2183 | -0.015778 | -0.02133 | -0.09613 | 0.086975 | -0.10529 | -0.10071 | 0.054932 | -0.10529 | -0.013733 | -56.1447 | 0.25177 | -122.6028 | 0.17853 | -121.5958 | -122.287 | -121.843 | 122.4335 | -0.15564 | -0.34332 | 122.5937 | 122.525 | 122.4335 | 0.091553 | 0 | -0.064087 | 0.009155 | -0.064087 | 0.94299 | 0.6958 | 0.25177 | 0.75989 | 0.31586 | 0.16022 | 0.004578 | 1.0071 | 122.7814 | 0.19226 | 122.8546 | 122.6257 | 122.7905 | -0.3479 | -122.8455 | 122.438 | 122.7173 | 122.4426 | 66.394
2390.5625 | 122.9095 | -122.5616 | 0.27924 | 0.0025177 | -0.01437 | -0.079438 | -0.0080471 | -0.029162 | -0.049099 | -0.041887 | -0.0021057 | -0.01904 | 0.057909 | 0.041776 | -0.22107 | -0.014283 | -0.023039 | -0.059509 | 0.059509 | -0.10529 | -0.054932 | 0.11444 | -0.032043 | 0.018311 | -56.2729 | 0.25177 | -122.6303 | 0.14648 | -121.6141 | -122.2916 | -121.8521 | 122.4564 | -0.21973 | -0.33417 | 122.6761 | 122.58 | 122.5296 | 0.1236 | 0.073243 | -0.068664 | -0.027466 | -0.13275 | 0.94757 | 0.70953 | 0.27008 | 0.7782 | 0.33874 | 0.21973 | 0.050354 | 1.0162 | 122.7768 | 0.16479 | 122.8821 | 122.6212 | 122.8134 | -0.38452 | -122.9095 | 122.5067 | 122.7081 | 122.5021 | 66.2888
2392.2812 | 122.8729 | -122.58 | 0.27466 | 0.0025177 | -0.012234 | -0.078797 | -0.0065517 | -0.034075 | -0.051235 | -0.043169 | 0.00094606 | -0.020108 | 0.058763 | 0.049467 | -0.21915 | -0.015137 | -0.021971 | -0.059509 | 0.064087 | -0.11444 | -0.082397 | 0.07782 | -0.059509 | 0.013733 | -56.5201 | 0.24261 | -122.5937 | 0.13275 | -121.6187 | -122.3236 | -121.8842 | 122.4655 | -0.21057 | -0.35706 | 122.6578 | 122.5937 | 122.5204 | 0.12817 | 0.054932 | -0.013733 | -0.032043 | -0.14191 | 0.9613 | 0.6958 | 0.25635 | 0.70953 | 0.27008 | 0.19226 | 0.032044 | 0.97504 | 122.7264 | 0.17853 | 122.8363 | 122.644 | 122.8226 | -0.3891 | -122.8683 | 122.4976 | 122.7127 | 122.5204 | 66.0599
2394.0625 | 122.9324 | -122.5296 | 0.24719 | -0.0051118 | -0.013089 | -0.078583 | -0.0056973 | -0.034075 | -0.049526 | -0.043596 | 0.00094606 | -0.020108 | 0.060259 | 0.050321 | -0.22086 | -0.015351 | -0.024107 | -0.073242 | 0.073242 | -0.091553 | -0.064087 | 0.11444 | -0.082397 | -0.009155 | -56.7169 | 0.23804 | -122.6166 | 0.20599 | -121.5866 | -122.287 | -121.8201 | 122.438 | -0.17395 | -0.31128 | 122.644 | 122.5204 | 122.4472 | 0.082398 | 0.009156 | -0.086975 | -0.009155 | -0.041198 | 0.94299 | 0.70953 | 0.24262 | 0.79651 | 0.32959 | 0.20599 | 0.027466 | 1.03 | 122.8226 | 0.16479 | 122.8546 | 122.6028 | 122.7676 | -0.33874 | -122.8638 | 122.4655 | 122.7356 | 122.4564 | 65.8127
2395.8438 | 122.9507 | -122.5342 | 0.25635 | -0.028 | -0.014798 | -0.080933 | -0.0065517 | -0.032366 | -0.052304 | -0.042955 | -0.0021057 | -0.020322 | 0.056841 | 0.045194 | -0.22022 | -0.016633 | -0.025389 | -0.050354 | 0.059509 | -0.086975 | -0.022888 | 0.13275 | -0.009155 | 0.032043 | -56.8405 | 0.22888 | -122.5937 | 0.23804 | -121.5225 | -122.2275 | -121.8109 | 122.4472 | -0.19684 | -0.27924 | 122.6669 | 122.5662 | 122.525 | 0.11902 | 0.07782 | -0.059509 | -0.027466 | -0.018311 | 1.0117 | 0.72327 | 0.3067 | 0.78278 | 0.36621 | 0.21973 | 0.064087 | 1.0712 | 122.8317 | 0.14648 | 122.8226 | 122.5937 | 122.7631 | -0.34332 | -122.85 | 122.5113 | 122.7722 | 122.4838 | 65.6937
2397.6406 | 122.937 | -122.5433 | 0.2655 | 0.0025177 | -0.014584 | -0.077942 | -0.0059109 | -0.033007 | -0.050595 | -0.042528 | -0.0051575 | -0.017972 | 0.057482 | 0.046049 | -0.21937 | -0.016846 | -0.024748 | -0.09613 | 0.059509 | -0.091553 | -0.073242 | 0.068665 | -0.091553 | -0.018311 | -57.0969 | 0.24719 | -122.5845 | 0.17853 | -121.5958 | -122.2916 | -121.8246 | 122.4518 | -0.20599 | -0.33874 | 122.612 | 122.525 | 122.4518 | 0.073242 | 0 | -0.041199 | -0.018311 | -0.086975 | 0.94757 | 0.71869 | 0.25177 | 0.75989 | 0.29297 | 0.16022 | 0.018311 | 0.98877 | 122.7631 | 0.15106 | 122.8317 | 122.6028 | 122.7905 | -0.35706 | -122.85 | 122.4701 | 122.7219 | 122.4472 | 65.4465
2399.375 | 122.9324 | -122.5388 | 0.23804 | -0.0051118 | -0.013943 | -0.077942 | -0.0084743 | -0.02788 | -0.04974 | -0.042314 | -0.0021057 | -0.019467 | 0.059618 | 0.041349 | -0.21872 | -0.016419 | -0.020903 | -0.10529 | 0.082397 | -0.10529 | -0.073242 | 0.054932 | -0.086975 | -0.009155 | -57.2937 | 0.23346 | -122.58 | 0.16479 | -121.5729 | -122.287 | -121.843 | 122.4335 | -0.15564 | -0.31128 | 122.5937 | 122.5296 | 122.4518 | 0.096131 | 0.018311 | -0.041199 | -0.004578 | -0.073242 | 0.96588 | 0.6958 | 0.25177 | 0.737 | 0.29297 | 0.16022 | 0.032044 | 1.0071 | 122.7448 | 0.18768 | 122.8134 | 122.6212 | 122.7722 | -0.34332 | -122.818 | 122.4655 | 122.7036 | 122.4335 | 65.2451
2401.1719 | 122.9691 | -122.5616 | 0.26093 | -0.0051118 | -0.013302 | -0.083283 | -0.0078335 | -0.031939 | -0.05444 | -0.042314 | -0.0051575 | -0.020749 | 0.056414 | 0.04733 | -0.22257 | -0.015992 | -0.023894 | -0.09613 | 0.07782 | -0.091553 | -0.064087 | 0.086975 | -0.07782 | 0 | -57.4768 | 0.22888 | -122.5937 | 0.20142 | -121.5271 | -122.2366 | -121.8018 | 122.4701 | -0.18311 | -0.32501 | 122.6486 | 122.5616 | 122.4838 | 0.091553 | 0.013733 | -0.032043 | -0.032043 | -0.059509 | 1.0345 | 0.75989 | 0.32501 | 0.79193 | 0.35706 | 0.17853 | 0.027466 | 1.0666 | 122.7951 | 0.16937 | 122.8226 | 122.6395 | 122.7905 | -0.35248 | -122.8546 | 122.4976 | 122.7631 | 122.4655 | 65.0848
2402.9062 | 122.9141 | -122.5296 | 0.2655 | -0.0051118 | -0.010098 | -0.079651 | -0.0048427 | -0.028093 | -0.050595 | -0.040605 | -0.0021057 | -0.018186 | 0.058123 | 0.053739 | -0.22022 | -0.014069 | -0.023253 | -0.10986 | 0.11444 | -0.12817 | -0.14191 | -0.004578 | -0.1831 | -0.082397 | -57.7469 | 0.27008 | -122.6303 | 0.15564 | -121.6141 | -122.3648 | -121.8796 | 122.4014 | -0.15106 | -0.40741 | 122.525 | 122.4472 | 122.3465 | 0.045777 | -0.054931 | -0.10071 | 0.004578 | -0.10986 | 0.91553 | 0.65002 | 0.16479 | 0.75073 | 0.2655 | 0.1236 | -0.013733 | 1.0162 | 122.7859 | 0.24262 | 122.9004 | 122.644 | 122.7997 | -0.39368 | -122.8958 | 122.3877 | 122.6852 | 122.4197 | 64.7827
2404.6875 | 122.8958 | -122.5983 | 0.28839 | -0.0051118 | -0.016293 | -0.078797 | -0.0052701 | -0.02788 | -0.051235 | -0.042528 | 0.0039979 | -0.018399 | 0.058336 | 0.049253 | -0.22129 | -0.015778 | -0.024321 | -0.11902 | 0.10986 | -0.15106 | -0.13733 | -0.027466 | -0.14648 | -0.082397 | -57.9391 | 0.27008 | -122.6303 | 0.12817 | -121.6003 | -122.3465 | -121.8796 | 122.4472 | -0.17853 | -0.42572 | 122.5708 | 122.5159 | 122.4518 | 0.068665 | 0.004578 | -0.032043 | -0.01831 | -0.16022 | 0.99793 | 0.71869 | 0.25177 | 0.75073 | 0.28381 | 0.1236 | 0.013733 | 1.03 | 122.7585 | 0.26093 | 122.9004 | 122.7081 | 122.8683 | -0.43945 | -122.9187 | 122.4609 | 122.7264 | 122.4792 | 64.6591
2406.4688 | 122.8546 | -122.5754 | 0.27466 | -0.0051118 | -0.011166 | -0.07837 | -0.0031337 | -0.03023 | -0.048886 | -0.039324 | -0.0021057 | -0.019467 | 0.059618 | 0.04733 | -0.21915 | -0.016419 | -0.024962 | -0.10986 | 0.10529 | -0.13275 | -0.15564 | -0.027466 | -0.18768 | -0.10986 | -58.1497 | 0.27466 | -122.6303 | 0.10529 | -121.6507 | -122.4106 | -121.9116 | 122.4426 | -0.16937 | -0.4303 | 122.5479 | 122.4655 | 122.3877 | 0.022888 | -0.054932 | -0.054932 | 0 | -0.16937 | 0.92468 | 0.66376 | 0.16479 | 0.71869 | 0.21973 | 0.10529 | -0.022889 | 0.97961 | 122.7356 | 0.23804 | 122.905 | 122.6807 | 122.85 | -0.40741 | -122.905 | 122.4197 | 122.6807 | 122.4655 | 64.4257
2408.1875 | 122.8363 | -122.58 | 0.28381 | -0.0051118 | -0.0096707 | -0.077942 | -0.0037747 | -0.028093 | -0.048672 | -0.039965 | -0.0021057 | -0.018827 | 0.059404 | 0.048826 | -0.22129 | -0.016846 | -0.023467 | -0.11902 | 0.1236 | -0.1236 | -0.16022 | -0.050354 | -0.19226 | -0.11902 | -58.3099 | 0.27466 | -122.6395 | 0.10071 | -121.669 | -122.4106 | -121.9345 | 122.4564 | -0.16022 | -0.44403 | 122.5296 | 122.4609 | 122.3877 | 0.004577 | -0.068665 | -0.059509 | -0.009155 | -0.1831 | 0.91095 | 0.64545 | 0.16937 | 0.70496 | 0.22888 | 0.073242 | -0.036621 | 0.97046 | 122.7402 | 0.24719 | 122.9141 | 122.7036 | 122.8546 | -0.40741 | -122.9233 | 122.4197 | 122.6807 | 122.4609 | 64.27
2409.9688 | 122.8409 | -122.58 | 0.27008 | 0.010147 | -0.010952 | -0.078583 | -0.0050565 | -0.032793 | -0.050595 | -0.041887 | 0.00094606 | -0.01904 | 0.0609 | 0.049894 | -0.21787 | -0.014496 | -0.019621 | -0.09613 | 0.11444 | -0.13275 | -0.15106 | 0 | -0.16937 | -0.09613 | -58.5297 | 0.25177 | -122.6212 | 0.10986 | -121.6461 | -122.3877 | -121.9116 | 122.4472 | -0.15564 | -0.42114 | 122.58 | 122.4838 | 122.4106 | 0.036621 | -0.036622 | -0.041199 | -0.018311 | -0.16022 | 0.93384 | 0.66833 | 0.19226 | 0.70953 | 0.23346 | 0.13275 | -0.018311 | 0.97504 | 122.731 | 0.24719 | 122.8729 | 122.6944 | 122.8317 | -0.40283 | -122.8912 | 122.4289 | 122.6898 | 122.4838 | 64.0503
2411.7656 | 122.8317 | -122.58 | 0.27924 | 0.0025177 | -0.0081753 | -0.076874 | -0.0042019 | -0.026812 | -0.052731 | -0.042742 | -0.0021057 | -0.019254 | 0.059618 | 0.046689 | -0.21937 | -0.013001 | -0.020049 | -0.091553 | 0.10529 | -0.10529 | -0.13733 | 0.022888 | -0.15564 | -0.073242 | -58.6212 | 0.25177 | -122.6303 | 0.1236 | -121.6278 | -122.3923 | -121.8979 | 122.4747 | -0.17395 | -0.41656 | 122.6028 | 122.5067 | 122.4243 | 0.032044 | -0.050354 | -0.050354 | -0.027466 | -0.15564 | 0.95215 | 0.68207 | 0.18768 | 0.73242 | 0.23804 | 0.12817 | -0.032043 | 1.0025 | 122.7539 | 0.21057 | 122.8821 | 122.6852 | 122.8317 | -0.38452 | -122.9095 | 122.4426 | 122.7036 | 122.4884 | 63.9587
2413.4844 | 122.8592 | -122.5937 | 0.27008 | 0.0025177 | -0.013516 | -0.080933 | -0.0082607 | -0.031725 | -0.051022 | -0.040392 | 0.00094606 | -0.021817 | 0.057695 | 0.043058 | -0.21894 | -0.017701 | -0.021971 | -0.086975 | 0.10071 | -0.11902 | -0.10986 | 0.036621 | -0.11902 | -0.059509 | -58.8501 | 0.27008 | -122.6166 | 0.10071 | -121.5866 | -122.3465 | -121.9116 | 122.4747 | -0.16937 | -0.37994 | 122.6303 | 122.5342 | 122.4747 | 0.05951 | 0 | -0.022888 | 0 | -0.16937 | 1.0071 | 0.68207 | 0.24719 | 0.70496 | 0.27008 | 0.15564 | 0.009156 | 1.03 | 122.7173 | 0.21973 | 122.8867 | 122.6944 | 122.8638 | -0.3891 | -122.8867 | 122.4838 | 122.6944 | 122.5067 | 63.7436
2415.2812 | 122.937 | -122.5388 | 0.2655 | -0.0051118 | -0.013089 | -0.080292 | -0.0048427 | -0.03023 | -0.050381 | -0.041887 | -0.0021057 | -0.020108 | 0.058977 | 0.040708 | -0.22043 | -0.015351 | -0.021758 | -0.13733 | 0.11444 | -0.13733 | -0.14191 | 0.009155 | -0.16479 | -0.07782 | -59.0057 | 0.25177 | -122.6349 | 0.16479 | -121.5683 | -122.3099 | -121.843 | 122.4014 | -0.15106 | -0.40741 | 122.5479 | 122.4609 | 122.374 | 0.059509 | -0.027466 | -0.096131 | -0.013733 | -0.10071 | 0.97046 | 0.6958 | 0.22888 | 0.79193 | 0.32501 | 0.14648 | -0.004578 | 1.0666 | 122.7997 | 0.25177 | 122.8867 | 122.6532 | 122.7905 | -0.40283 | -122.9004 | 122.3969 | 122.7036 | 122.4014 | 63.533
2417.0156 | 122.9874 | -122.5479 | 0.24261 | -0.0051118 | -0.016079 | -0.082856 | -0.0069791 | -0.027666 | -0.050167 | -0.040605 | -0.0051575 | -0.018613 | 0.058977 | 0.04733 | -0.22022 | -0.015137 | -0.026885 | -0.07782 | 0.086975 | -0.09613 | -0.045776 | 0.14648 | -0.018311 | 0.054932 | -59.1064 | 0.23346 | -122.6166 | 0.24261 | -121.4584 | -122.1909 | -121.788 | 122.4518 | -0.15564 | -0.28839 | 122.6944 | 122.6028 | 122.5296 | 0.15106 | 0.077819 | -0.068664 | -0.009156 | 0 | 1.0895 | 0.75989 | 0.35706 | 0.82855 | 0.42572 | 0.24261 | 0.050354 | 1.1581 | 122.8592 | 0.1831 | 122.85 | 122.6349 | 122.7814 | -0.33874 | -122.8592 | 122.5021 | 122.7905 | 122.4701 | 63.4415
2418.7969 | 122.8409 | -122.5891 | 0.28381 | 0.0025177 | -0.0083889 | -0.079224 | -0.0056973 | -0.029375 | -0.051235 | -0.04146 | -0.0021057 | -0.017758 | 0.058336 | 0.046476 | -0.22065 | -0.015137 | -0.02133 | -0.1236 | 0.11444 | -0.13733 | -0.16479 | -0.041199 | -0.19226 | -0.10529 | -59.4864 | 0.24719 | -122.6578 | 0.10986 | -121.6278 | -122.4106 | -121.8979 | 122.4518 | -0.16937 | -0.44861 | 122.5479 | 122.4838 | 122.3969 | 0.032043 | -0.054932 | -0.068665 | -0.036621 | -0.17395 | 0.9613 | 0.69122 | 0.17853 | 0.75989 | 0.24719 | 0.09613 | -0.027466 | 1.03 | 122.7676 | 0.25177 | 122.905 | 122.7036 | 122.8363 | -0.42114 | -122.9416 | 122.4243 | 122.699 | 122.4655 | 63.1027
2420.6094 | 122.8821 | -122.5937 | 0.28381 | -0.0051118 | -0.010311 | -0.07837 | -0.0035611 | -0.03258 | -0.048886 | -0.039965 | -0.0021057 | -0.018399 | 0.057482 | 0.045621 | -0.22043 | -0.017273 | -0.023039 | -0.1236 | 0.11902 | -0.13275 | -0.16937 | -0.018311 | -0.18768 | -0.091553 | -59.6603 | 0.26093 | -122.6257 | 0.10529 | -121.6049 | -122.3877 | -121.8979 | 122.4609 | -0.16479 | -0.45319 | 122.5754 | 122.5021 | 122.406 | 0.041198 | -0.054932 | -0.032043 | -0.022888 | -0.17853 | 0.98877 | 0.6958 | 0.20599 | 0.72784 | 0.23804 | 0.11444 | -0.036622 | 1.0208 | 122.731 | 0.25177 | 122.8867 | 122.7127 | 122.8546 | -0.41656 | -122.9095 | 122.4243 | 122.699 | 122.4701 | 62.9333
2422.3281 | 122.8912 | -122.58 | 0.27008 | 0.0025177 | -0.0090299 | -0.077729 | -0.0052701 | -0.030443 | -0.050595 | -0.040392 | -0.0051575 | -0.018186 | 0.059191 | 0.048185 | -0.21766 | -0.013215 | -0.017485 | -0.064087 | 0.10986 | -0.1236 | -0.10529 | 0.050354 | -0.1236 | -0.041199 | -59.7565 | 0.26093 | -122.6257 | 0.15106 | -121.5637 | -122.3465 | -121.8567 | 122.4564 | -0.16022 | -0.37537 | 122.6303 | 122.5388 | 122.4564 | 0.082397 | 0 | -0.045776 | -0.009156 | -0.11902 | 1.0162 | 0.72327 | 0.23346 | 0.76904 | 0.27923 | 0.17395 | 0.01831 | 1.062 | 122.7768 | 0.23346 | 122.8867 | 122.6898 | 122.8409 | -0.39368 | -122.8958 | 122.4747 | 122.731 | 122.5159 | 62.8235
2424.125 | 122.8455 | -122.5937 | 0.27924 | 0.0025177 | -0.013729 | -0.080933 | -0.0052701 | -0.031725 | -0.051235 | -0.038896 | -0.0021057 | -0.020536 | 0.059404 | 0.047971 | -0.21872 | -0.013856 | -0.021971 | -0.15106 | 0.11444 | -0.13733 | -0.15106 | -0.009155 | -0.14648 | -0.064087 | -59.9716 | 0.25635 | -122.644 | 0.082397 | -121.582 | -122.374 | -121.907 | 122.4564 | -0.16479 | -0.4303 | 122.5845 | 122.5296 | 122.4472 | 0.073242 | -0.009155 | -0.050354 | -0.022888 | -0.19684 | 1.0117 | 0.68665 | 0.21973 | 0.737 | 0.27008 | 0.12817 | -0.013733 | 1.062 | 122.7264 | 0.25177 | 122.9004 | 122.7081 | 122.85 | -0.41656 | -122.9233 | 122.4426 | 122.6761 | 122.4426 | 62.6221
2425.9219 | 122.8592 | -122.5983 | 0.27466 | -0.0051118 | -0.014798 | -0.080719 | -0.0091153 | -0.032152 | -0.052944 | -0.039324 | -0.0021057 | -0.018186 | 0.058977 | 0.046903 | -0.21872 | -0.017273 | -0.020476 | -0.14648 | 0.12817 | -0.15106 | -0.17395 | -0.018311 | -0.14191 | -0.059509 | -60.2097 | 0.2655 | -122.6212 | 0.091553 | -121.5958 | -122.3648 | -121.9025 | 122.4472 | -0.14648 | -0.44861 | 122.58 | 122.5388 | 122.4564 | 0.091553 | 0.009155 | -0.022888 | -0.009155 | -0.18311 | 1.0025 | 0.6958 | 0.23346 | 0.71869 | 0.25635 | 0.13275 | -0.022888 | 1.0254 | 122.7127 | 0.27924 | 122.8867 | 122.7264 | 122.8638 | -0.42572 | -122.8958 | 122.4243 | 122.6898 | 122.4518 | 62.3886
2427.7031 | 122.8546 | -122.5845 | 0.27924 | 0.0025177 | -0.0090299 | -0.077515 | -0.0037747 | -0.030871 | -0.049954 | -0.041033 | 0.00094606 | -0.018827 | 0.059832 | 0.043272 | -0.21872 | -0.015565 | -0.023253 | -0.12817 | 0.13733 | -0.1236 | -0.17395 | -0.068665 | -0.20142 | -0.10071 | -60.3241 | 0.25177 | -122.6257 | 0.10071 | -121.6141 | -122.4197 | -121.907 | 122.4609 | -0.14191 | -0.45319 | 122.5159 | 122.4838 | 122.3831 | 0.022888 | -0.07782 | -0.041198 | -0.027466 | -0.17853 | 0.97046 | 0.67749 | 0.16479 | 0.71869 | 0.20599 | 0.054931 | -0.050354 | 1.0117 | 122.7264 | 0.26093 | 122.8775 | 122.7219 | 122.8363 | -0.40283 | -122.905 | 122.4106 | 122.6852 | 122.4564 | 62.2604
2429.4219 | 122.8363 | -122.5891 | 0.29297 | -0.0051118 | -0.010098 | -0.077515 | -0.0054837 | -0.028734 | -0.048245 | -0.039751 | 0.00094606 | -0.019254 | 0.058977 | 0.045194 | -0.21979 | -0.015778 | -0.021758 | -0.10986 | 0.13733 | -0.12817 | -0.15564 | -0.018311 | -0.1831 | -0.10071 | -60.4889 | 0.26093 | -122.6349 | 0.091553 | -121.5912 | -122.406 | -121.8979 | 122.4609 | -0.15564 | -0.44861 | 122.5708 | 122.4884 | 122.406 | 0.027466 | -0.054931 | -0.045777 | -0.032044 | -0.20142 | 0.99792 | 0.69122 | 0.1831 | 0.737 | 0.22888 | 0.10986 | -0.027466 | 1.0437 | 122.7264 | 0.2655 | 122.8958 | 122.7264 | 122.85 | -0.42114 | -122.9279 | 122.4335 | 122.6807 | 122.4792 | 62.1002
2431.2188 | 122.9095 | -122.5754 | 0.27466 | -0.02037 | -0.010739 | -0.079865 | -0.0027065 | -0.030016 | -0.04974 | -0.040605 | -0.0021057 | -0.020749 | 0.058977 | 0.049894 | -0.21872 | -0.014924 | -0.023467 | -0.068665 | 0.10071 | -0.11902 | -0.091553 | 0.064087 | -0.10071 | -0.036621 | -60.5713 | 0.23804 | -122.5937 | 0.14648 | -121.5225 | -122.3282 | -121.8613 | 122.4564 | -0.17395 | -0.36621 | 122.6395 | 122.5388 | 122.4747 | 0.082398 | 0.018311 | -0.018311 | -0.036621 | -0.12817 | 1.0529 | 0.71411 | 0.24719 | 0.73242 | 0.2655 | 0.18311 | 0.027466 | 1.0712 | 122.7402 | 0.21973 | 122.8317 | 122.6761 | 122.8134 | -0.39368 | -122.8683 | 122.4838 | 122.7219 | 122.5067 | 62.0041
2433.0156 | 122.905 | -122.58 | 0.25177 | -0.0051118 | -0.01437 | -0.080933 | -0.0082607 | -0.028734 | -0.050808 | -0.038683 | 0.00094606 | -0.02139 | 0.05855 | 0.052244 | -0.21808 | -0.015992 | -0.023039 | -0.073242 | 0.082397 | -0.086975 | -0.086975 | 0.091553 | -0.036621 | 0.004578 | -60.7636 | 0.24261 | -122.612 | 0.11902 | -121.5225 | -122.3145 | -121.8658 | 122.493 | -0.16937 | -0.33874 | 122.6715 | 122.5845 | 122.5433 | 0.091553 | 0.050354 | -0.032044 | -0.009155 | -0.13275 | 1.0574 | 0.71411 | 0.2655 | 0.74616 | 0.29755 | 0.17853 | 0 | 1.0895 | 122.731 | 0.16937 | 122.8546 | 122.6624 | 122.8226 | -0.33874 | -122.8638 | 122.493 | 122.699 | 122.5067 | 61.8164
2434.7344 | 122.8683 | -122.5662 | 0.27466 | -0.012741 | -0.0098843 | -0.07837 | -0.0048427 | -0.031084 | -0.048886 | -0.040392 | 0.00094606 | -0.019254 | 0.057909 | 0.047758 | -0.2215 | -0.013856 | -0.026457 | -0.064087 | 0.10071 | -0.10986 | -0.11444 | 0.041199 | -0.13275 | -0.054932 | -60.8963 | 0.24719 | -122.6349 | 0.12817 | -121.5591 | -122.3557 | -121.8887 | 122.4564 | -0.17395 | -0.3891 | 122.6074 | 122.5113 | 122.4335 | 0.054931 | -0.022888 | -0.068665 | -0.027466 | -0.14648 | 1.0071 | 0.67749 | 0.21057 | 0.74616 | 0.27924 | 0.15106 | -0.004578 | 1.0757 | 122.7631 | 0.21057 | 122.8821 | 122.6669 | 122.8134 | -0.38452 | -122.9095 | 122.4518 | 122.6944 | 122.5021 | 61.6699
2436.5469 | 122.8729 | -122.58 | 0.2655 | 0.0025177 | -0.010739 | -0.076447 | -0.0046291 | -0.029802 | -0.048031 | -0.041246 | -0.0051575 | -0.020322 | 0.057909 | 0.053739 | -0.22065 | -0.017914 | -0.022826 | -0.07782 | 0.10986 | -0.11902 | -0.10986 | 0.022888 | -0.12817 | -0.059509 | -61.0931 | 0.24261 | -122.6395 | 0.12817 | -121.5591 | -122.374 | -121.8887 | 122.4609 | -0.15564 | -0.37537 | 122.6028 | 122.5204 | 122.4518 | 0.05951 | -0.009155 | -0.059509 | -0.022888 | -0.13733 | 1.0208 | 0.69122 | 0.20599 | 0.75073 | 0.2655 | 0.14191 | 0.009156 | 1.0803 | 122.7676 | 0.22888 | 122.8821 | 122.6898 | 122.8226 | -0.38452 | -122.905 | 122.4701 | 122.7081 | 122.5021 | 61.4868
2438.3281 | 122.9919 | -122.5479 | 0.2243 | 0.0025177 | -0.016079 | -0.080719 | -0.0089017 | -0.033648 | -0.053158 | -0.039965 | -0.0051575 | -0.022031 | 0.057268 | 0.046049 | -0.21787 | -0.016846 | -0.019621 | -0.07782 | 0.082397 | -0.10529 | -0.059509 | 0.14648 | -0.018311 | 0.068665 | -61.1572 | 0.21973 | -122.612 | 0.2243 | -121.4081 | -122.2046 | -121.7834 | 122.4426 | -0.14191 | -0.28381 | 122.6944 | 122.6166 | 122.5296 | 0.17395 | 0.086975 | -0.064087 | -0.004577 | 0 | 1.1398 | 0.76447 | 0.34332 | 0.82855 | 0.40741 | 0.25177 | 0.045777 | 1.2039 | 122.8363 | 0.18768 | 122.8317 | 122.6303 | 122.7676 | -0.32959 | -122.8363 | 122.4884 | 122.7722 | 122.4701 | 61.3907
2440.1094 | 122.9416 | -122.5662 | 0.23804 | -0.0051118 | -0.012661 | -0.078156 | -0.0067653 | -0.03023 | -0.04974 | -0.04146 | -0.0051575 | -0.02139 | 0.057909 | 0.055662 | -0.22022 | -0.016846 | -0.019408 | -0.09613 | 0.064087 | -0.10529 | -0.082397 | 0.07782 | -0.091553 | -0.009155 | -61.3358 | 0.23346 | -122.6257 | 0.16479 | -121.4676 | -122.2733 | -121.8246 | 122.4609 | -0.17395 | -0.32043 | 122.644 | 122.5571 | 122.4747 | 0.096131 | 0.013733 | -0.059509 | -0.004578 | -0.073242 | 1.0986 | 0.74158 | 0.29297 | 0.80109 | 0.35248 | 0.18311 | 0.022889 | 1.1581 | 122.7905 | 0.16937 | 122.8592 | 122.6303 | 122.7997 | -0.34332 | -122.8638 | 122.4838 | 122.731 | 122.4701 | 61.2305
2441.8906 | 122.9233 | -122.6028 | 0.28381 | 0.0025177 | -0.011807 | -0.079438 | -0.0039883 | -0.031939 | -0.051235 | -0.042955 | -0.0021057 | -0.019895 | 0.059832 | 0.047117 | -0.21872 | -0.016633 | -0.021544 | -0.10071 | 0.11444 | -0.14191 | -0.10071 | 0.032043 | -0.10986 | -0.041199 | -61.5189 | 0.25177 | -122.6212 | 0.15564 | -121.5134 | -122.3145 | -121.8521 | 122.4609 | -0.16937 | -0.38452 | 122.6349 | 122.5616 | 122.493 | 0.10071 | 0.032044 | -0.018311 | -0.032043 | -0.12817 | 1.0895 | 0.75073 | 0.28839 | 0.76904 | 0.3067 | 0.17395 | 0.041199 | 1.1078 | 122.7768 | 0.25635 | 122.8729 | 122.7173 | 122.8546 | -0.42572 | -122.905 | 122.5021 | 122.7585 | 122.5021 | 61.084
2443.6719 | 123.0057 | -122.5388 | 0.24261 | 0.0025177 | -0.013516 | -0.079651 | -0.0091153 | -0.028948 | -0.04974 | -0.038042 | 0.00094606 | -0.020963 | 0.060045 | 0.043058 | -0.22001 | -0.016846 | -0.023467 | -0.064087 | 0.064087 | -0.091553 | -0.013733 | 0.16937 | 0 | 0.073242 | -61.5097 | 0.2243 | -122.612 | 0.21973 | -121.3898 | -122.1909 | -121.7789 | 122.4472 | -0.17853 | -0.25635 | 122.7081 | 122.612 | 122.5388 | 0.16479 | 0.091553 | -0.073243 | -0.018311 | -0.022888 | 1.149 | 0.75989 | 0.3479 | 0.83313 | 0.42114 | 0.26093 | 0.07782 | 1.2222 | 122.8317 | 0.15564 | 122.8363 | 122.6028 | 122.7631 | -0.33417 | -122.8546 | 122.525 | 122.7585 | 122.4747 | 61.0291
2445.4062 | 122.9095 | -122.58 | 0.27008 | -0.0051118 | -0.015866 | -0.080933 | -0.0078335 | -0.03023 | -0.050167 | -0.042742 | 0.00094606 | -0.021817 | 0.057909 | 0.044553 | -0.22043 | -0.015992 | -0.027098 | -0.050354 | 0.086975 | -0.091553 | -0.054932 | 0.10986 | -0.036621 | 0.013733 | -61.734 | 0.24261 | -122.6166 | 0.13275 | -121.4859 | -122.3007 | -121.8704 | 122.4884 | -0.18311 | -0.32501 | 122.6898 | 122.5937 | 122.5433 | 0.10529 | 0.054932 | -0.036621 | -0.027466 | -0.13733 | 1.0941 | 0.70953 | 0.27924 | 0.74616 | 0.31586 | 0.20142 | 0.036621 | 1.1307 | 122.7493 | 0.17853 | 122.8592 | 122.6669 | 122.8226 | -0.36163 | -122.8867 | 122.525 | 122.7127 | 122.5296 | 60.8459
2447.2031 | 122.9187 | -122.5662 | 0.27008 | 0.0025177 | -0.011166 | -0.077088 | -0.0059109 | -0.030871 | -0.051022 | -0.041674 | 0.00094606 | -0.017545 | 0.058977 | 0.050535 | -0.21872 | -0.016205 | -0.022398 | -0.073242 | 0.10529 | -0.13733 | -0.091553 | 0.045776 | -0.11902 | -0.050354 | -61.8668 | 0.24719 | -122.612 | 0.15564 | -121.4951 | -122.3145 | -121.843 | 122.4289 | -0.1648 | -0.36163 | 122.612 | 122.5159 | 122.4472 | 0.086975 | 0.01831 | -0.045777 | -0.022889 | -0.11444 | 1.0712 | 0.72327 | 0.25177 | 0.76904 | 0.29755 | 0.18311 | 0.045776 | 1.1169 | 122.7676 | 0.24262 | 122.8592 | 122.6715 | 122.8134 | -0.40741 | -122.8821 | 122.4747 | 122.7219 | 122.493 | 60.6995
2448.9844 | 122.8912 | -122.5983 | 0.27466 | -0.0051118 | -0.013089 | -0.079438 | -0.0067653 | -0.029802 | -0.050381 | -0.04146 | 0.00094606 | -0.019681 | 0.058763 | 0.043485 | -0.21937 | -0.015778 | -0.020903 | -0.14648 | 0.11902 | -0.13275 | -0.14648 | -0.022888 | -0.16022 | -0.07782 | -62.1002 | 0.2655 | -122.6715 | 0.082397 | -121.5088 | -122.3557 | -121.8933 | 122.4655 | -0.15564 | -0.42114 | 122.5754 | 122.5204 | 122.4381 | 0.054931 | -0.027466 | -0.073242 | -0.009155 | -0.19226 | 1.0895 | 0.70496 | 0.24262 | 0.7782 | 0.31586 | 0.10986 | -0.013733 | 1.1627 | 122.7539 | 0.25177 | 122.937 | 122.7173 | 122.8638 | -0.40741 | -122.9462 | 122.4518 | 122.6807 | 122.4518 | 60.498
2450.6875 | 122.9187 | -122.5479 | 0.25635 | -0.0051118 | -0.010952 | -0.079011 | -0.0050565 | -0.027453 | -0.049313 | -0.040605 | -0.0051575 | -0.017758 | 0.059618 | 0.047117 | -0.22043 | -0.015565 | -0.021544 | -0.10986 | 0.10986 | -0.1236 | -0.16479 | 0.004578 | -0.17853 | -0.086975 | -62.1918 | 0.25177 | -122.6303 | 0.14648 | -121.4951 | -122.3328 | -121.8521 | 122.4243 | -0.14649 | -0.42114 | 122.5525 | 122.4609 | 122.3694 | 0.036621 | -0.054932 | -0.082397 | -0.004578 | -0.10986 | 1.0529 | 0.6958 | 0.21515 | 0.7782 | 0.29755 | 0.12817 | -0.041199 | 1.1353 | 122.7768 | 0.23346 | 122.8821 | 122.6578 | 122.7997 | -0.37994 | -122.8867 | 122.3831 | 122.6944 | 122.438 | 60.3561
2452.6875 | 122.9828 | -122.5571 | 0.24261 | -0.012741 | -0.011593 | -0.077942 | -0.0093289 | -0.03258 | -0.050381 | -0.043383 | -0.0021057 | -0.02139 | 0.055559 | 0.036436 | -0.21723 | -0.016205 | -0.022398 | -0.041199 | 0.07782 | -0.086975 | -0.022888 | 0.15106 | -0.018311 | 0.032043 | -62.2147 | 0.21515 | -122.6212 | 0.20142 | -121.3852 | -122.2183 | -121.788 | 122.4701 | -0.16479 | -0.2655 | 122.7081 | 122.5891 | 122.5388 | 0.11902 | 0.068664 | -0.064087 | -0.027466 | -0.041199 | 1.1719 | 0.76904 | 0.33875 | 0.83313 | 0.40283 | 0.23804 | 0.064087 | 1.236 | 122.8226 | 0.16479 | 122.8363 | 122.6349 | 122.7722 | -0.32959 | -122.8638 | 122.5342 | 122.7585 | 122.5159 | 60.3424
2456.5938 | 122.9691 | -122.5845 | 0.24261 | 0.0025177 | -0.014584 | -0.079011 | -0.0067653 | -0.030443 | -0.050167 | -0.038896 | 0.00094606 | -0.020749 | 0.05855 | 0.04498 | -0.21851 | -0.015778 | -0.019835 | -0.091553 | 0.07782 | -0.10986 | -0.073242 | 0.07782 | -0.068665 | 0.009155 | -62.5397 | 0.21057 | -122.6395 | 0.18768 | -121.3806 | -122.2321 | -121.7972 | 122.4747 | -0.16479 | -0.31586 | 122.6624 | 122.5937 | 122.5159 | 0.11902 | 0.041198 | -0.054931 | -0.032044 | -0.054932 | 1.2039 | 0.78735 | 0.35248 | 0.84229 | 0.40741 | 0.18768 | 0.036621 | 1.2588 | 122.8271 | 0.18768 | 122.85 | 122.6624 | 122.7951 | -0.35248 | -122.8821 | 122.5113 | 122.7722 | 122.493 | 60.0449
2460.1719 | 122.8683 | -122.5845 | 0.27466 | -0.0051118 | -0.010311 | -0.079651 | -0.0037747 | -0.027453 | -0.04739 | -0.042101 | -0.0021057 | -0.016477 | 0.058763 | 0.050962 | -0.21894 | -0.014924 | -0.022612 | -0.12817 | 0.12817 | -0.13275 | -0.18768 | -0.07782 | -0.22888 | -0.10529 | -62.9837 | 0.25635 | -122.6395 | 0.091553 | -121.5454 | -122.4014 | -121.9116 | 122.4518 | -0.14648 | -0.46234 | 122.5067 | 122.4792 | 122.3557 | 0.027465 | -0.096131 | -0.054931 | -0.01831 | -0.18311 | 1.0391 | 0.67291 | 0.18311 | 0.72784 | 0.23804 | 0.054931 | -0.054932 | 1.0941 | 122.731 | 0.26093 | 122.8958 | 122.7127 | 122.8409 | -0.40741 | -122.9141 | 122.3969 | 122.6761 | 122.4564 | 59.6008
2465.9375 | 122.8683 | -122.5891 | 0.27008 | 0.0025177 | -0.014584 | -0.078156 | -0.0048427 | -0.030016 | -0.051876 | -0.039751 | 0.00094606 | -0.019467 | 0.058123 | 0.043272 | -0.22107 | -0.018128 | -0.023467 | -0.091553 | 0.09613 | -0.1236 | -0.1236 | 0.013733 | -0.16022 | -0.091553 | -63.4048 | 0.24261 | -122.6578 | 0.10986 | -121.4951 | -122.3877 | -121.8933 | 122.4655 | -0.17395 | -0.39368 | 122.6028 | 122.4976 | 122.4289 | 0.032043 | -0.036621 | -0.068665 | -0.027466 | -0.16022 | 1.0941 | 0.6958 | 0.20142 | 0.76447 | 0.27008 | 0.13733 | 0 | 1.1627 | 122.7676 | 0.21973 | 122.9004 | 122.6852 | 122.8317 | -0.39368 | -122.9279 | 122.4655 | 122.699 | 122.4976 | 59.1843
2467.7344 | 122.8729 | -122.6257 | 0.26093 | 0.0025177 | -0.015438 | -0.078156 | -0.0074063 | -0.028948 | -0.049954 | -0.039537 | -0.0021057 | -0.020536 | 0.061541 | 0.050535 | -0.21915 | -0.015565 | -0.023894 | -0.14648 | 0.12817 | -0.15106 | -0.16937 | -0.022888 | -0.15106 | -0.054932 | -63.5422 | 0.25635 | -122.6624 | 0.082397 | -121.4676 | -122.3648 | -121.8933 | 122.4747 | -0.13275 | -0.4303 | 122.6028 | 122.5708 | 122.4747 | 0.09613 | 0 | -0.036622 | -0.004577 | -0.17853 | 1.1581 | 0.73242 | 0.26093 | 0.76904 | 0.29755 | 0.12817 | -0.018311 | 1.1948 | 122.7448 | 0.27924 | 122.9187 | 122.7539 | 122.8821 | -0.41199 | -122.9233 | 122.4564 | 122.7081 | 122.4792 | 59.0836
2469.5156 | 122.8638 | -122.612 | 0.25177 | -0.012741 | -0.013516 | -0.081147 | -0.0084743 | -0.029589 | -0.049954 | -0.043169 | 0.00094606 | -0.018399 | 0.059618 | 0.046903 | -0.21958 | -0.015565 | -0.022185 | -0.12817 | 0.10071 | -0.12817 | -0.15106 | -0.004578 | -0.13275 | -0.073242 | -63.652 | 0.25635 | -122.6669 | 0.07782 | -121.463 | -122.3602 | -121.9208 | 122.4838 | -0.15106 | -0.40283 | 122.6074 | 122.5388 | 122.4792 | 0.054932 | -0.004577 | -0.054931 | 0.004578 | -0.17395 | 1.149 | 0.69122 | 0.25177 | 0.74616 | 0.3067 | 0.1236 | -0.022888 | 1.2039 | 122.7448 | 0.22888 | 122.9233 | 122.7127 | 122.8683 | -0.37994 | -122.9187 | 122.4609 | 122.6898 | 122.4838 | 58.96
2471.2344 | 122.9736 | -122.5937 | 0.21973 | -0.0051118 | -0.015011 | -0.079224 | -0.0074063 | -0.032366 | -0.050167 | -0.043169 | -0.0021057 | -0.021604 | 0.059404 | 0.039426 | -0.21915 | -0.017487 | -0.022185 | -0.09613 | 0.07782 | -0.091553 | -0.07782 | 0.07782 | -0.082397 | 0.013733 | -63.707 | 0.21057 | -122.6166 | 0.18768 | -121.3623 | -122.2321 | -121.7926 | 122.5021 | -0.14191 | -0.29755 | 122.6715 | 122.6074 | 122.5113 | 0.10529 | 0.009156 | -0.022888 | -0.009156 | -0.032044 | 1.2314 | 0.80109 | 0.36163 | 0.82397 | 0.38452 | 0.16937 | 0.013733 | 1.2543 | 122.8043 | 0.16937 | 122.8271 | 122.6715 | 122.8043 | -0.31128 | -122.8363 | 122.5159 | 122.7814 | 122.4976 | 58.8867
2473.0469 | 122.8683 | -122.6349 | 0.26093 | 0.017777 | -0.012661 | -0.080506 | -0.0089017 | -0.031939 | -0.051022 | -0.041674 | -0.0021057 | -0.018399 | 0.057268 | 0.045835 | -0.21958 | -0.015992 | -0.020476 | -0.07782 | 0.091553 | -0.11902 | -0.10986 | 0.032043 | -0.11444 | -0.045776 | -63.858 | 0.23346 | -122.6486 | 0.091553 | -121.4447 | -122.3328 | -121.907 | 122.5159 | -0.16937 | -0.37079 | 122.6669 | 122.5891 | 122.5204 | 0.073243 | 0.004578 | -0.013733 | -0.027466 | -0.16937 | 1.1902 | 0.72785 | 0.30212 | 0.74158 | 0.31586 | 0.15106 | 0.009156 | 1.2039 | 122.7402 | 0.21057 | 122.8821 | 122.7264 | 122.8683 | -0.37994 | -122.9095 | 122.525 | 122.7264 | 122.5571 | 58.7769
2474.8281 | 122.9462 | -122.58 | 0.23346 | -0.012741 | -0.013302 | -0.082001 | -0.0067653 | -0.034716 | -0.050381 | -0.039965 | -0.0021057 | -0.021817 | 0.059191 | 0.037076 | -0.22001 | -0.018342 | -0.023467 | -0.091553 | 0.073242 | -0.11444 | -0.086975 | 0.050354 | -0.09613 | -0.013733 | -63.9862 | 0.21973 | -122.6257 | 0.15106 | -121.3806 | -122.287 | -121.8338 | 122.4655 | -0.16022 | -0.32043 | 122.6303 | 122.5662 | 122.4838 | 0.10071 | 0.018311 | -0.045776 | -0.013732 | -0.082397 | 1.1993 | 0.74616 | 0.29297 | 0.79193 | 0.33875 | 0.16479 | 0.027466 | 1.2451 | 122.7768 | 0.18768 | 122.8455 | 122.6532 | 122.7997 | -0.3479 | -122.8592 | 122.493 | 122.731 | 122.4884 | 58.5938
2476.6094 | 122.8638 | -122.6074 | 0.2655 | -0.0051118 | -0.013302 | -0.079865 | -0.0071927 | -0.030657 | -0.050808 | -0.041033 | -0.0021057 | -0.019681 | 0.057909 | 0.044767 | -0.22065 | -0.016846 | -0.023894 | -0.12817 | 0.11444 | -0.12817 | -0.14191 | -0.009155 | -0.14191 | -0.068665 | -64.1602 | 0.24261 | -122.6486 | 0.07782 | -121.4539 | -122.3648 | -121.9116 | 122.4792 | -0.15106 | -0.40741 | 122.5983 | 122.5388 | 122.4655 | 0.059509 | -0.013733 | -0.041199 | -0.022888 | -0.18768 | 1.1536 | 0.6958 | 0.24262 | 0.737 | 0.28381 | 0.11902 | -0.013733 | 1.1948 | 122.7264 | 0.24262 | 122.8912 | 122.7219 | 122.85 | -0.39368 | -122.9141 | 122.4655 | 122.6852 | 122.4792 | 58.4473
2478.3438 | 122.9874 | -122.5662 | 0.2243 | -0.0051118 | -0.0092435 | -0.077515 | -0.0046291 | -0.028093 | -0.049954 | -0.042101 | -0.0021057 | -0.020322 | 0.057695 | 0.04199 | -0.21979 | -0.017273 | -0.019194 | -0.091553 | 0.10529 | -0.10986 | -0.07782 | 0.07782 | -0.10986 | -0.009155 | -64.1876 | 0.21515 | -122.6257 | 0.21057 | -121.344 | -122.2549 | -121.7606 | 122.4564 | -0.11902 | -0.30212 | 122.644 | 122.5571 | 122.4564 | 0.10071 | 0 | -0.059509 | -0.009155 | -0.013733 | 1.2222 | 0.80566 | 0.31128 | 0.86517 | 0.37079 | 0.18768 | 0.032043 | 1.2817 | 122.8363 | 0.21515 | 122.8409 | 122.6715 | 122.7814 | -0.33417 | -122.85 | 122.4884 | 122.7768 | 122.4747 | 58.3786
2480.0625 | 122.9233 | -122.5845 | 0.24261 | -0.0051118 | -0.012875 | -0.079224 | -0.0035611 | -0.028307 | -0.050381 | -0.037828 | -0.0051575 | -0.017972 | 0.060045 | 0.041135 | -0.22214 | -0.015778 | -0.021117 | -0.10529 | 0.11902 | -0.12817 | -0.12817 | -0.004578 | -0.1236 | -0.064087 | -64.4211 | 0.24719 | -122.6212 | 0.13733 | -121.4035 | -122.3282 | -121.8613 | 122.4564 | -0.1236 | -0.37079 | 122.58 | 122.5204 | 122.4609 | 0.064087 | 0.004578 | -0.036621 | 0.004577 | -0.10529 | 1.181 | 0.72327 | 0.25635 | 0.75989 | 0.29297 | 0.1236 | 0 | 1.2177 | 122.7585 | 0.24719 | 122.8683 | 122.7036 | 122.8317 | -0.37079 | -122.8638 | 122.4564 | 122.7219 | 122.4792 | 58.1635
2481.7812 | 122.9828 | -122.5525 | 0.21515 | -0.012741 | -0.012448 | -0.077729 | -0.0048427 | -0.029375 | -0.050381 | -0.041246 | 0.0039979 | -0.020322 | 0.058763 | 0.048612 | -0.21958 | -0.015778 | -0.022398 | -0.10529 | 0.10529 | -0.11902 | -0.091553 | 0.027466 | -0.14191 | -0.036621 | -64.4806 | 0.21057 | -122.6578 | 0.21515 | -121.3303 | -122.2824 | -121.7743 | 122.4335 | -0.10986 | -0.3067 | 122.58 | 122.5159 | 122.4106 | 0.082398 | -0.022888 | -0.10529 | -0.004578 | 0 | 1.2222 | 0.7782 | 0.27008 | 0.88348 | 0.37537 | 0.14649 | 0.027466 | 1.3275 | 122.8729 | 0.22431 | 122.8683 | 122.6578 | 122.7631 | -0.33417 | -122.8729 | 122.4609 | 122.7676 | 122.4472 | 58.0719
2483.5 | 122.9965 | -122.5983 | 0.21973 | -0.0051118 | -0.015866 | -0.079865 | -0.0086879 | -0.030443 | -0.049954 | -0.043383 | -0.0021057 | -0.021604 | 0.057268 | 0.044126 | -0.21872 | -0.016419 | -0.023894 | -0.10071 | 0.073242 | -0.09613 | -0.082397 | 0.091553 | -0.059509 | 0.013733 | -64.5813 | 0.21973 | -122.6166 | 0.1831 | -121.312 | -122.2321 | -121.7789 | 122.5021 | -0.14649 | -0.30212 | 122.6898 | 122.612 | 122.5388 | 0.10986 | 0.036621 | -0.01831 | 0 | -0.036622 | 1.2863 | 0.8194 | 0.36621 | 0.83771 | 0.38452 | 0.18768 | 0.013733 | 1.3046 | 122.7997 | 0.16937 | 122.8363 | 122.6715 | 122.818 | -0.31586 | -122.8363 | 122.5159 | 122.7814 | 122.4976 | 58.017
2485.2188 | 122.8821 | -122.612 | 0.25635 | -0.0051118 | -0.014584 | -0.081147 | -0.0052701 | -0.031084 | -0.051663 | -0.039751 | 0.00094606 | -0.017545 | 0.058336 | 0.046903 | -0.22107 | -0.01471 | -0.021758 | -0.13275 | 0.11444 | -0.14191 | -0.16937 | -0.027466 | -0.14648 | -0.073242 | -64.8148 | 0.23346 | -122.6624 | 0.09613 | -121.4127 | -122.3557 | -121.8887 | 122.4701 | -0.14191 | -0.42572 | 122.5845 | 122.5388 | 122.4655 | 0.068665 | -0.004577 | -0.050354 | -0.022889 | -0.16022 | 1.1993 | 0.72327 | 0.25635 | 0.77362 | 0.3067 | 0.11444 | -0.027466 | 1.2497 | 122.7585 | 0.25635 | 122.8958 | 122.7264 | 122.8455 | -0.39826 | -122.9187 | 122.4426 | 122.7081 | 122.4792 | 57.7972
2487 | 122.8821 | -122.6212 | 0.26093 | -0.012741 | -0.010098 | -0.077302 | -0.0054837 | -0.032793 | -0.049313 | -0.042101 | 0.00094606 | -0.019467 | 0.060472 | 0.044767 | -0.22001 | -0.015351 | -0.019194 | -0.11444 | 0.11444 | -0.13733 | -0.16022 | -0.036621 | -0.19684 | -0.11902 | -64.9612 | 0.2243 | -122.6349 | 0.091553 | -121.4218 | -122.374 | -121.8887 | 122.4838 | -0.14648 | -0.42114 | 122.5845 | 122.5021 | 122.4243 | 0.01831 | -0.059509 | -0.013733 | -0.036621 | -0.16937 | 1.1993 | 0.73242 | 0.24719 | 0.74616 | 0.26093 | 0.10071 | -0.022888 | 1.2131 | 122.7264 | 0.25177 | 122.8592 | 122.7356 | 122.8455 | -0.39825 | -122.8958 | 122.4609 | 122.7127 | 122.5067 | 57.6599
2488.7188 | 122.937 | -122.58 | 0.2243 | -0.0051118 | -0.015438 | -0.081574 | -0.0099697 | -0.030871 | -0.05209 | -0.040392 | 0.00094606 | -0.020322 | 0.057482 | 0.043272 | -0.22107 | -0.016633 | -0.025176 | -0.059509 | 0.073242 | -0.10986 | -0.022888 | 0.14191 | -0.018311 | 0.027466 | -64.92 | 0.20142 | -122.6624 | 0.16937 | -121.3074 | -122.2366 | -121.8063 | 122.4701 | -0.15106 | -0.24719 | 122.7219 | 122.6074 | 122.5616 | 0.13733 | 0.091552 | -0.082398 | -0.022888 | -0.054931 | 1.2726 | 0.77362 | 0.34332 | 0.85602 | 0.42572 | 0.25177 | 0.086975 | 1.355 | 122.8317 | 0.18311 | 122.8638 | 122.6532 | 122.7814 | -0.33417 | -122.8867 | 122.5571 | 122.7493 | 122.5204 | 57.6599
2490.5156 | 122.8867 | -122.6028 | 0.26093 | -0.0051118 | -0.012448 | -0.080933 | -0.0052701 | -0.031939 | -0.050167 | -0.041674 | 0.00094606 | -0.019681 | 0.057268 | 0.046903 | -0.21787 | -0.015565 | -0.020049 | -0.11902 | 0.11444 | -0.14648 | -0.16479 | -0.004578 | -0.16022 | -0.068665 | -65.1672 | 0.24719 | -122.6807 | 0.086975 | -121.376 | -122.3419 | -121.875 | 122.4564 | -0.14648 | -0.42572 | 122.5983 | 122.5342 | 122.4426 | 0.077819 | -0.013733 | -0.07782 | -0.013733 | -0.17395 | 1.2268 | 0.72784 | 0.26093 | 0.80566 | 0.33874 | 0.14191 | -0.018311 | 1.3046 | 122.7676 | 0.26093 | 122.9279 | 122.7173 | 122.85 | -0.40741 | -122.9416 | 122.438 | 122.6898 | 122.4838 | 57.4356
2492.2969 | 122.9599 | -122.58 | 0.24261 | -0.0051118 | -0.010525 | -0.079011 | -0.0078335 | -0.030871 | -0.051022 | -0.040392 | -0.0021057 | -0.021817 | 0.058336 | 0.045621 | -0.22086 | -0.017273 | -0.02368 | -0.10986 | 0.086975 | -0.11444 | -0.10529 | 0.054932 | -0.091553 | -0.013733 | -65.2588 | 0.19684 | -122.6807 | 0.14648 | -121.3211 | -122.2824 | -121.8246 | 122.4655 | -0.15564 | -0.3479 | 122.6349 | 122.5662 | 122.4884 | 0.10071 | 0.022888 | -0.10071 | -0.045777 | -0.096131 | 1.2588 | 0.75531 | 0.29755 | 0.85602 | 0.39825 | 0.16937 | 0.009155 | 1.3596 | 122.8271 | 0.20142 | 122.8775 | 122.6669 | 122.7768 | -0.35706 | -122.9233 | 122.4747 | 122.7264 | 122.4701 | 57.3212
2494.0781 | 122.9874 | -122.5616 | 0.21515 | -0.0051118 | -0.011593 | -0.079651 | -0.0039883 | -0.028734 | -0.048245 | -0.041674 | -0.0021057 | -0.01904 | 0.057268 | 0.051176 | -0.2215 | -0.013215 | -0.021117 | -0.054932 | 0.073242 | -0.086975 | -0.027466 | 0.11902 | -0.068665 | 0.004578 | -65.3 | 0.19226 | -122.6303 | 0.22888 | -121.2799 | -122.2275 | -121.7514 | 122.4747 | -0.14191 | -0.24261 | 122.6807 | 122.5662 | 122.493 | 0.091553 | 0.01831 | -0.068664 | -0.022888 | 0.013733 | 1.2817 | 0.81024 | 0.33417 | 0.87891 | 0.40283 | 0.20599 | 0.059509 | 1.3504 | 122.8592 | 0.16022 | 122.8226 | 122.6349 | 122.7539 | -0.30212 | -122.8455 | 122.5342 | 122.7905 | 122.5067 | 57.2617
2495.8438 | 122.9645 | -122.6028 | 0.22888 | 0.0025177 | -0.013729 | -0.077302 | -0.0052701 | -0.031725 | -0.051876 | -0.042742 | -0.0051575 | -0.022458 | 0.058763 | 0.049467 | -0.22022 | -0.015778 | -0.021758 | -0.09613 | 0.07782 | -0.10529 | -0.091553 | 0.050354 | -0.10986 | -0.018311 | -65.4831 | 0.21057 | -122.6395 | 0.15106 | -121.3074 | -122.2733 | -121.8155 | 122.4976 | -0.15106 | -0.32044 | 122.6532 | 122.5845 | 122.493 | 0.086975 | -0.004577 | -0.036621 | -0.018311 | -0.07782 | 1.2955 | 0.78735 | 0.32959 | 0.82397 | 0.36621 | 0.15564 | 0.013733 | 1.3321 | 122.7905 | 0.18311 | 122.85 | 122.6807 | 122.8134 | -0.33417 | -122.8683 | 122.5113 | 122.7539 | 122.5067 | 57.1198
2497.6562 | 123.0148 | -122.5891 | 0.21973 | -0.0051118 | -0.012661 | -0.079865 | -0.0076199 | -0.030443 | -0.049954 | -0.040392 | -0.0021057 | -0.018186 | 0.057054 | 0.046049 | -0.22129 | -0.016846 | -0.025816 | -0.073242 | 0.068665 | -0.10529 | -0.041199 | 0.11444 | -0.013733 | 0.041199 | -65.5106 | 0.1831 | -122.6257 | 0.19684 | -121.2387 | -122.2137 | -121.7697 | 122.4838 | -0.15106 | -0.26093 | 122.7036 | 122.6303 | 122.5754 | 0.14649 | 0.091553 | -0.036621 | -0.036622 | -0.022889 | 1.3504 | 0.8194 | 0.37537 | 0.85602 | 0.41199 | 0.21973 | 0.064087 | 1.387 | 122.8226 | 0.17395 | 122.8088 | 122.6578 | 122.7722 | -0.32501 | -122.8455 | 122.5479 | 122.7859 | 122.5159 | 57.0786
2499.3906 | 122.9095 | -122.5937 | 0.25177 | 0.0025177 | -0.015011 | -0.079651 | -0.0050565 | -0.024675 | -0.049954 | -0.042101 | 0.00094606 | -0.018613 | 0.057909 | 0.04968 | -0.22086 | -0.015351 | -0.025389 | -0.10529 | 0.10529 | -0.13733 | -0.13733 | 0 | -0.1236 | -0.050354 | -65.7257 | 0.23346 | -122.6486 | 0.11444 | -121.3303 | -122.3328 | -121.8704 | 122.4564 | -0.14648 | -0.3891 | 122.5937 | 122.5433 | 122.4701 | 0.086975 | 0.013733 | -0.054932 | -0.018311 | -0.13733 | 1.2634 | 0.72327 | 0.26093 | 0.7782 | 0.31586 | 0.13733 | 0 | 1.3184 | 122.7631 | 0.24262 | 122.8821 | 122.699 | 122.8271 | -0.3891 | -122.9004 | 122.4564 | 122.7081 | 122.4884 | 56.868
2501.1562 | 122.85 | -122.612 | 0.25635 | -0.0051118 | -0.0092435 | -0.079011 | -0.0037747 | -0.027666 | -0.051876 | -0.039965 | -0.0021057 | -0.018186 | 0.059404 | 0.052244 | -0.22022 | -0.014283 | -0.024321 | -0.1236 | 0.10986 | -0.13275 | -0.16022 | -0.054932 | -0.20142 | -0.10529 | -65.8676 | 0.24261 | -122.6761 | 0.091553 | -121.4172 | -122.4106 | -121.9116 | 122.4792 | -0.14649 | -0.41657 | 122.5571 | 122.5067 | 122.4106 | 0.027465 | -0.068665 | -0.064086 | -0.013733 | -0.1648 | 1.1948 | 0.70038 | 0.20142 | 0.76447 | 0.2655 | 0.077819 | -0.027466 | 1.2588 | 122.7676 | 0.24261 | 122.9187 | 122.7219 | 122.8546 | -0.3891 | -122.9324 | 122.4518 | 122.7036 | 122.4884 | 56.7444
2502.9531 | 122.9874 | -122.58 | 0.21515 | -0.012741 | -0.011166 | -0.080506 | -0.0050565 | -0.028521 | -0.047817 | -0.042742 | 0.00094606 | -0.022031 | 0.059832 | 0.044553 | -0.2215 | -0.015351 | -0.021544 | -0.041199 | 0.059509 | -0.091553 | -0.022888 | 0.11444 | -0.064087 | 0.027466 | -65.7578 | 0.1831 | -122.6257 | 0.21057 | -121.2296 | -122.2366 | -121.7514 | 122.4884 | -0.15564 | -0.23804 | 122.6944 | 122.6074 | 122.5159 | 0.11902 | 0.027466 | -0.045776 | -0.032044 | -0.004578 | 1.3504 | 0.82855 | 0.34332 | 0.87433 | 0.3891 | 0.20599 | 0.068665 | 1.3962 | 122.8363 | 0.15106 | 122.8088 | 122.6395 | 122.7631 | -0.3067 | -122.8409 | 122.5571 | 122.7905 | 122.5388 | 56.8222
2504.7344 | 122.9233 | -122.6074 | 0.27008 | 0.0025177 | -0.013089 | -0.077942 | -0.0048427 | -0.029375 | -0.051022 | -0.042314 | -0.0021057 | -0.018399 | 0.059404 | 0.042631 | -0.22065 | -0.014496 | -0.024535 | -0.073242 | 0.11902 | -0.1236 | -0.10529 | 0.032043 | -0.10071 | -0.050354 | -65.9775 | 0.2243 | -122.6578 | 0.12817 | -121.2982 | -122.319 | -121.8475 | 122.4838 | -0.15106 | -0.37537 | 122.6395 | 122.5571 | 122.5067 | 0.073242 | 0.022888 | -0.050354 | -0.045777 | -0.14191 | 1.3092 | 0.75989 | 0.28839 | 0.81024 | 0.33875 | 0.15564 | 0.01831 | 1.3596 | 122.7859 | 0.24261 | 122.8821 | 122.7264 | 122.8317 | -0.39368 | -122.9279 | 122.5021 | 122.7356 | 122.5342 | 56.6299
2506.4531 | 122.9187 | -122.5891 | 0.24261 | -0.0051118 | -0.010952 | -0.077729 | -0.0063381 | -0.02553 | -0.052517 | -0.039537 | 0.00094606 | -0.016904 | 0.057695 | 0.048185 | -0.22043 | -0.015992 | -0.023894 | -0.07782 | 0.10986 | -0.1236 | -0.10071 | 0.059509 | -0.10071 | -0.050354 | -66.0416 | 0.21515 | -122.6761 | 0.14191 | -121.2891 | -122.2961 | -121.8521 | 122.4655 | -0.13275 | -0.34332 | 122.6486 | 122.5388 | 122.4884 | 0.073242 | 0.022888 | -0.086975 | -0.027466 | -0.10071 | 1.3 | 0.737 | 0.29297 | 0.82397 | 0.37994 | 0.1831 | 0.022888 | 1.387 | 122.818 | 0.23346 | 122.8912 | 122.699 | 122.8043 | -0.36621 | -122.9187 | 122.4884 | 122.731 | 122.5113 | 56.5475
2508.1719 | 122.8683 | -122.6028 | 0.24719 | 0.0025177 | -0.01202 | -0.079865 | -0.0044155 | -0.031939 | -0.049526 | -0.042955 | -0.0021057 | -0.018613 | 0.059618 | 0.050962 | -0.21744 | -0.015137 | -0.018767 | -0.086975 | 0.086975 | -0.11902 | -0.11902 | 0.041199 | -0.13733 | -0.064087 | -66.156 | 0.21057 | -122.644 | 0.10071 | -121.3348 | -122.3511 | -121.8796 | 122.4838 | -0.16022 | -0.36621 | 122.644 | 122.5388 | 122.4655 | 0.054932 | -0.01831 | -0.041199 | -0.036621 | -0.14648 | 1.268 | 0.72327 | 0.25177 | 0.76447 | 0.29297 | 0.16022 | 0 | 1.3092 | 122.7448 | 0.20599 | 122.8546 | 122.6898 | 122.8134 | -0.36621 | -122.8912 | 122.4838 | 122.7036 | 122.5159 | 56.4468
2509.8906 | 123.0331 | -122.5708 | 0.23346 | 0.0025177 | -0.016079 | -0.078583 | -0.010183 | -0.031298 | -0.050808 | -0.043383 | 0.00094606 | -0.022458 | 0.056414 | 0.040067 | -0.21851 | -0.015992 | -0.025603 | -0.064087 | 0.068665 | -0.10071 | -0.032043 | 0.17853 | 0.009155 | 0.064087 | -66.1377 | 0.20142 | -122.6303 | 0.21057 | -121.1563 | -122.1817 | -121.7651 | 122.4701 | -0.16479 | -0.2655 | 122.7493 | 122.6349 | 122.58 | 0.1648 | 0.10986 | -0.059509 | -0.032043 | -0.022888 | 1.4145 | 0.80566 | 0.3891 | 0.86517 | 0.44861 | 0.27924 | 0.068665 | 1.474 | 122.8409 | 0.16937 | 122.8317 | 122.6395 | 122.7722 | -0.33417 | -122.8638 | 122.5388 | 122.7814 | 122.5067 | 56.4331
2511.6875 | 122.9874 | -122.5937 | 0.2243 | -0.0051118 | -0.01437 | -0.080292 | -0.0078335 | -0.029802 | -0.049313 | -0.044023 | 0.00094606 | -0.019895 | 0.058763 | 0.043699 | -0.21894 | -0.016633 | -0.015349 | -0.09613 | 0.082397 | -0.10986 | -0.073242 | 0.07782 | -0.054932 | 0.022888 | -66.2842 | 0.19684 | -122.644 | 0.18768 | -121.2021 | -122.2092 | -121.788 | 122.4838 | -0.14191 | -0.29755 | 122.6715 | 122.6166 | 122.5388 | 0.13275 | 0.054931 | -0.050354 | -0.027466 | -0.036621 | 1.3916 | 0.80566 | 0.38452 | 0.85602 | 0.43488 | 0.18768 | 0.036621 | 1.442 | 122.8317 | 0.19226 | 122.8409 | 122.6761 | 122.7905 | -0.33417 | -122.8683 | 122.5204 | 122.7814 | 122.4976 | 56.3095
2513.4844 | 122.9782 | -122.5708 | 0.19684 | -0.0051118 | -0.010739 | -0.078583 | -0.0046291 | -0.034289 | -0.049099 | -0.040392 | -0.0051575 | -0.020963 | 0.057909 | 0.04968 | -0.22022 | -0.015778 | -0.024321 | -0.045776 | 0.068665 | -0.091553 | -0.013733 | 0.13733 | -0.059509 | 0.022888 | -66.3483 | 0.19684 | -122.6257 | 0.21057 | -121.1975 | -122.2321 | -121.7514 | 122.4792 | -0.12817 | -0.21057 | 122.7081 | 122.5937 | 122.5113 | 0.11444 | 0.032044 | -0.054931 | 0 | 0.013733 | 1.3733 | 0.8194 | 0.33875 | 0.87433 | 0.39368 | 0.22888 | 0.07782 | 1.4282 | 122.8363 | 0.16022 | 122.8226 | 122.6395 | 122.7676 | -0.28839 | -122.8226 | 122.5571 | 122.7814 | 122.525 | 56.2225
2515.2656 | 122.9141 | -122.6257 | 0.23346 | 0.010147 | -0.013089 | -0.079865 | -0.0035611 | -0.03258 | -0.051235 | -0.039537 | -0.0021057 | -0.017118 | 0.057695 | 0.049894 | -0.21894 | -0.015351 | -0.024321 | -0.086975 | 0.10986 | -0.1236 | -0.086975 | 0.059509 | -0.10071 | -0.036621 | -66.4627 | 0.21973 | -122.6624 | 0.13275 | -121.2753 | -122.3282 | -121.8567 | 122.5021 | -0.1236 | -0.32043 | 122.6852 | 122.5891 | 122.525 | 0.086975 | 0.022888 | -0.036622 | -0.013732 | -0.10071 | 1.3504 | 0.76904 | 0.29755 | 0.80566 | 0.33417 | 0.1831 | 0.036621 | 1.387 | 122.7951 | 0.23346 | 122.8821 | 122.7356 | 122.8455 | -0.35706 | -122.8958 | 122.5388 | 122.7585 | 122.5388 | 56.163
2516.9844 | 122.9141 | -122.6303 | 0.2655 | -0.0051118 | -0.014584 | -0.077942 | -0.0067653 | -0.031511 | -0.049099 | -0.042528 | -0.0021057 | -0.019467 | 0.059618 | 0.050107 | -0.21979 | -0.014924 | -0.022398 | -0.10071 | 0.11444 | -0.12817 | -0.10986 | 0.013733 | -0.13275 | -0.045776 | -66.5955 | 0.24261 | -122.6715 | 0.10986 | -121.2479 | -122.3145 | -121.8658 | 122.5021 | -0.15106 | -0.37537 | 122.644 | 122.5845 | 122.4976 | 0.082398 | -0.004577 | -0.041199 | -0.022888 | -0.15564 | 1.3824 | 0.76447 | 0.31586 | 0.80566 | 0.35706 | 0.14191 | 0.018311 | 1.4236 | 122.7814 | 0.24262 | 122.9141 | 122.7448 | 122.8729 | -0.39368 | -122.937 | 122.5204 | 122.7402 | 122.5296 | 56.0349
2518.7656 | 122.9599 | -122.5616 | 0.21515 | -0.0051118 | -0.012661 | -0.07837 | -0.0076199 | -0.030016 | -0.048031 | -0.039965 | -0.0051575 | -0.019254 | 0.058123 | 0.046476 | -0.21851 | -0.018128 | -0.01834 | -0.050354 | 0.054932 | -0.09613 | -0.036621 | 0.1236 | -0.064087 | 0.013733 | -66.6321 | 0.19226 | -122.644 | 0.17853 | -121.2021 | -122.2412 | -121.788 | 122.4655 | -0.16022 | -0.25177 | 122.6852 | 122.5754 | 122.4976 | 0.10986 | 0.032043 | -0.082397 | -0.022888 | -0.036621 | 1.3596 | 0.77362 | 0.32043 | 0.85602 | 0.40283 | 0.21973 | 0.059509 | 1.442 | 122.8226 | 0.15106 | 122.8363 | 122.6166 | 122.7539 | -0.31128 | -122.8592 | 122.525 | 122.7402 | 122.5113 | 55.9296
2520.5625 | 122.9919 | -122.612 | 0.21057 | -0.0051118 | -0.015438 | -0.080933 | -0.0086879 | -0.033648 | -0.04974 | -0.045092 | 0.0070497 | -0.024381 | 0.060472 | 0.040708 | -0.22172 | -0.015137 | -0.020049 | -0.10071 | 0.091553 | -0.091553 | -0.07782 | 0.082397 | -0.064087 | 0.018311 | -66.7648 | 0.19684 | -122.6761 | 0.16937 | -121.17 | -122.2275 | -121.7789 | 122.5204 | -0.11902 | -0.28839 | 122.6944 | 122.6303 | 122.5479 | 0.10986 | 0.027466 | -0.064086 | -0.013733 | -0.041198 | 1.442 | 0.83313 | 0.38452 | 0.89722 | 0.44861 | 0.17395 | 0.013733 | 1.506 | 122.8455 | 0.18311 | 122.8729 | 122.7036 | 122.8088 | -0.30212 | -122.8867 | 122.5342 | 122.7814 | 122.5113 | 55.8472
2522.2812 | 122.9782 | -122.6166 | 0.2243 | 0.0025177 | -0.011166 | -0.080079 | -0.0076199 | -0.03322 | -0.050167 | -0.040605 | -0.0021057 | -0.019467 | 0.060472 | 0.048398 | -0.21851 | -0.017273 | -0.020049 | -0.10071 | 0.091553 | -0.10986 | -0.082397 | 0.059509 | -0.086975 | 0 | -66.8518 | 0.19684 | -122.644 | 0.16479 | -121.1975 | -122.2458 | -121.8063 | 122.5067 | -0.13275 | -0.3067 | 122.6761 | 122.6166 | 122.5296 | 0.10986 | 0.022888 | -0.027466 | -0.027466 | -0.059509 | 1.4191 | 0.81024 | 0.37079 | 0.83771 | 0.39825 | 0.16937 | 0.027466 | 1.4465 | 122.8088 | 0.20142 | 122.8409 | 122.7081 | 122.8134 | -0.33417 | -122.8683 | 122.5342 | 122.7814 | 122.5159 | 55.7648
2524.0625 | 122.8638 | -122.6212 | 0.24719 | 0.0025177 | -0.010525 | -0.079224 | -0.0022793 | -0.026171 | -0.051235 | -0.041674 | -0.0021057 | -0.018186 | 0.058336 | 0.048185 | -0.22236 | -0.01471 | -0.023253 | -0.13733 | 0.10529 | -0.14191 | -0.14648 | -0.059509 | -0.19226 | -0.10529 | -67.1127 | 0.21973 | -122.6944 | 0.082397 | -121.3211 | -122.3923 | -121.8796 | 122.4792 | -0.14191 | -0.39368 | 122.5616 | 122.5159 | 122.4289 | 0.036621 | -0.050354 | -0.073242 | -0.027465 | -0.16479 | 1.3 | 0.74158 | 0.22888 | 0.81482 | 0.30212 | 0.082398 | -0.004577 | 1.3733 | 122.7768 | 0.24719 | 122.9141 | 122.7264 | 122.8409 | -0.3891 | -122.9416 | 122.4747 | 122.7036 | 122.4838 | 55.5084
2525.8438 | 122.9141 | -122.6303 | 0.22888 | 0.0025177 | -0.011807 | -0.078797 | -0.0056973 | -0.03023 | -0.048886 | -0.041674 | -0.0021057 | -0.019681 | 0.058977 | 0.050748 | -0.21958 | -0.014924 | -0.019621 | -0.09613 | 0.11444 | -0.1236 | -0.09613 | 0.032043 | -0.10986 | -0.041199 | -67.1036 | 0.21057 | -122.6578 | 0.11444 | -121.2112 | -122.319 | -121.843 | 122.5067 | -0.11444 | -0.32501 | 122.6624 | 122.5891 | 122.5204 | 0.082397 | 0.013733 | -0.027466 | -0.018311 | -0.11444 | 1.4191 | 0.78735 | 0.31128 | 0.81482 | 0.33875 | 0.15564 | 0.027466 | 1.4465 | 122.7722 | 0.23804 | 122.8683 | 122.7448 | 122.8409 | -0.35248 | -122.8867 | 122.5342 | 122.7448 | 122.5342 | 55.5267
2527.6406 | 122.9874 | -122.5754 | 0.21057 | -0.02037 | -0.010311 | -0.080719 | -0.0076199 | -0.027666 | -0.048886 | -0.041674 | -0.0021057 | -0.01904 | 0.058336 | 0.052671 | -0.22022 | -0.013856 | -0.020476 | -0.086975 | 0.09613 | -0.10986 | -0.082397 | 0.068665 | -0.10986 | -0.004578 | -67.1631 | 0.19684 | -122.6486 | 0.19684 | -121.1609 | -122.2549 | -121.7606 | 122.4655 | -0.11444 | -0.29297 | 122.644 | 122.5708 | 122.4655 | 0.10529 | 0 | -0.073243 | -0.013733 | -0.013733 | 1.4145 | 0.81482 | 0.32043 | 0.88806 | 0.39368 | 0.17853 | 0.027466 | 1.4877 | 122.8455 | 0.20599 | 122.8455 | 122.6715 | 122.7722 | -0.32043 | -122.8592 | 122.493 | 122.7722 | 122.4884 | 55.4123
2529.4219 | 122.9599 | -122.5937 | 0.19684 | 0.0025177 | -0.01138 | -0.079224 | -0.0063381 | -0.031084 | -0.04974 | -0.041674 | -0.0021057 | -0.020963 | 0.058763 | 0.049253 | -0.21979 | -0.016846 | -0.020903 | -0.082397 | 0.086975 | -0.082397 | -0.050354 | 0.13275 | -0.068665 | 0.009155 | -67.305 | 0.18768 | -122.6578 | 0.16479 | -121.1792 | -122.2458 | -121.7972 | 122.5113 | -0.10986 | -0.24719 | 122.7264 | 122.6028 | 122.525 | 0.091552 | 0.013732 | -0.064087 | -0.009155 | -0.032043 | 1.4145 | 0.79651 | 0.3479 | 0.8606 | 0.41199 | 0.21515 | 0.032043 | 1.4786 | 122.8226 | 0.16937 | 122.8455 | 122.6807 | 122.7814 | -0.27924 | -122.8546 | 122.5433 | 122.7585 | 122.5113 | 55.2887
2531.2031 | 123.0011 | -122.6212 | 0.20599 | -0.012741 | -0.015438 | -0.07837 | -0.0056973 | -0.03023 | -0.048886 | -0.042101 | -0.0021057 | -0.020963 | 0.057695 | 0.043912 | -0.21915 | -0.015351 | -0.023467 | -0.10529 | 0.082397 | -0.091553 | -0.073242 | 0.082397 | -0.073242 | 0.009155 | -67.392 | 0.18768 | -122.6486 | 0.16022 | -121.1288 | -122.2229 | -121.7789 | 122.5296 | -0.1236 | -0.27924 | 122.7036 | 122.6303 | 122.5479 | 0.10071 | 0.018311 | -0.027466 | -0.018311 | -0.045777 | 1.4923 | 0.84229 | 0.39826 | 0.86975 | 0.42572 | 0.17395 | 0.018311 | 1.5198 | 122.8088 | 0.17395 | 122.8363 | 122.7036 | 122.8088 | -0.29755 | -122.8546 | 122.5479 | 122.7814 | 122.5159 | 55.2292
2533 | 123.0103 | -122.5937 | 0.20599 | -0.0051118 | -0.01202 | -0.079011 | -0.0059109 | -0.026812 | -0.051876 | -0.04146 | -0.0021057 | -0.020749 | 0.058977 | 0.045835 | -0.21979 | -0.014069 | -0.022185 | -0.068665 | 0.07782 | -0.10986 | -0.041199 | 0.10071 | -0.07782 | 0.009155 | -67.4835 | 0.19226 | -122.6486 | 0.20599 | -121.1288 | -122.2412 | -121.7468 | 122.4838 | -0.12817 | -0.24719 | 122.6944 | 122.6028 | 122.5159 | 0.11902 | 0.032043 | -0.054932 | -0.013733 | 0 | 1.4648 | 0.84686 | 0.35248 | 0.9018 | 0.40741 | 0.21057 | 0.068664 | 1.5198 | 122.8546 | 0.18768 | 122.8409 | 122.6715 | 122.7859 | -0.31586 | -122.8546 | 122.5525 | 122.7997 | 122.525 | 55.1102
2534.7812 | 122.9279 | -122.6074 | 0.23804 | -0.0051118 | -0.0092435 | -0.080292 | -0.0048427 | -0.028307 | -0.050381 | -0.040605 | -0.0021057 | -0.018399 | 0.059404 | 0.049894 | -0.21958 | -0.014924 | -0.02133 | -0.07782 | 0.10071 | -0.1236 | -0.091553 | 0.045776 | -0.091553 | -0.045776 | -67.662 | 0.20599 | -122.6715 | 0.12817 | -121.1792 | -122.3099 | -121.843 | 122.4838 | -0.13733 | -0.32959 | 122.6532 | 122.5616 | 122.5159 | 0.07782 | 0.032043 | -0.064087 | -0.032043 | -0.10986 | 1.4282 | 0.76447 | 0.29755 | 0.82855 | 0.36163 | 0.16937 | 0.032043 | 1.4923 | 122.7997 | 0.2243 | 122.8775 | 122.7081 | 122.8134 | -0.36163 | -122.9095 | 122.5159 | 122.7356 | 122.5296 | 54.9454
2536.5 | 122.8958 | -122.6395 | 0.23346 | -0.012741 | -0.013943 | -0.082001 | -0.0063381 | -0.030016 | -0.053372 | -0.039751 | 0.00094606 | -0.017972 | 0.060045 | 0.051389 | -0.21637 | -0.015992 | -0.022826 | -0.14191 | 0.11902 | -0.13275 | -0.15564 | -0.022888 | -0.15106 | -0.073242 | -67.8543 | 0.2243 | -122.6852 | 0.073242 | -121.1929 | -122.3236 | -121.875 | 122.5067 | -0.11444 | -0.3891 | 122.6166 | 122.5662 | 122.4884 | 0.059509 | -0.018311 | -0.045777 | -0.009155 | -0.16022 | 1.4465 | 0.76447 | 0.31586 | 0.81024 | 0.36163 | 0.10986 | -0.022889 | 1.4923 | 122.7585 | 0.25177 | 122.9095 | 122.7585 | 122.8638 | -0.36621 | -122.9187 | 122.4838 | 122.7127 | 122.4976 | 54.7852
2538.2656 | 122.9507 | -122.6257 | 0.21973 | -0.012741 | -0.013089 | -0.080506 | -0.0048427 | -0.034716 | -0.050381 | -0.042528 | -0.0021057 | -0.020108 | 0.05855 | 0.046476 | -0.21979 | -0.014924 | -0.020689 | -0.09613 | 0.059509 | -0.091553 | -0.086975 | 0.064087 | -0.086975 | 0 | -67.8909 | 0.18768 | -122.6624 | 0.13733 | -121.1426 | -122.2733 | -121.8155 | 122.5342 | -0.16022 | -0.3067 | 122.6898 | 122.6257 | 122.5388 | 0.091553 | 0.004578 | -0.036622 | -0.032044 | -0.082398 | 1.4832 | 0.81024 | 0.35248 | 0.84686 | 0.3891 | 0.15564 | 0.004578 | 1.5198 | 122.7997 | 0.15106 | 122.85 | 122.6852 | 122.8134 | -0.31128 | -122.8821 | 122.5388 | 122.7631 | 122.5296 | 54.7348
2539.9844 | 122.9004 | -122.6166 | 0.22888 | 0.0025177 | -0.012448 | -0.080933 | -0.0048427 | -0.029162 | -0.04974 | -0.04381 | -0.0021057 | -0.016049 | 0.059191 | 0.052457 | -0.2215 | -0.015992 | -0.022826 | -0.11444 | 0.10986 | -0.12817 | -0.14648 | 0.009155 | -0.1236 | -0.059509 | -67.9916 | 0.20142 | -122.6807 | 0.10986 | -121.17 | -122.3099 | -121.843 | 122.4884 | -0.11902 | -0.37537 | 122.6257 | 122.5571 | 122.493 | 0.068665 | 0.004578 | -0.064087 | -0.027466 | -0.11902 | 1.4465 | 0.77362 | 0.3067 | 0.83771 | 0.37079 | 0.13733 | -0.01831 | 1.5106 | 122.7905 | 0.23804 | 122.8821 | 122.7264 | 122.818 | -0.35706 | -122.9095 | 122.4701 | 122.7264 | 122.5021 | 54.6249
2541.7656 | 122.9919 | -122.5891 | 0.21515 | 0.0025177 | -0.015866 | -0.079865 | -0.0078335 | -0.029589 | -0.053799 | -0.04146 | -0.0021057 | -0.017331 | 0.057482 | 0.044767 | -0.21851 | -0.015137 | -0.022612 | -0.068665 | 0.068665 | -0.091553 | -0.018311 | 0.15106 | -0.013733 | 0.050354 | -68.0008 | 0.18768 | -122.6486 | 0.1831 | -121.0602 | -122.2092 | -121.7606 | 122.4976 | -0.14648 | -0.23346 | 122.7402 | 122.6395 | 122.5754 | 0.14191 | 0.07782 | -0.05951 | -0.027466 | -0.032044 | 1.5289 | 0.82855 | 0.37994 | 0.88806 | 0.43945 | 0.24261 | 0.073242 | 1.5884 | 122.8317 | 0.16022 | 122.8363 | 122.6578 | 122.7768 | -0.3067 | -122.8638 | 122.5708 | 122.7722 | 122.5204 | 54.5883
2543.4844 | 122.9874 | -122.5891 | 0.21057 | 0.010147 | -0.010525 | -0.077942 | -0.0046291 | -0.024035 | -0.049313 | -0.041674 | 0.00094606 | -0.018827 | 0.058763 | 0.046689 | -0.21958 | -0.015565 | -0.024748 | -0.086975 | 0.10529 | -0.10986 | -0.091553 | 0.059509 | -0.10071 | -0.018311 | -68.1427 | 0.17853 | -122.6578 | 0.17853 | -121.0922 | -122.2549 | -121.7606 | 122.4792 | -0.10529 | -0.30212 | 122.6486 | 122.5708 | 122.4884 | 0.091552 | 0.009155 | -0.068665 | -0.032043 | -0.032043 | 1.4969 | 0.82855 | 0.33417 | 0.89722 | 0.40283 | 0.16937 | 0.01831 | 1.5656 | 122.8363 | 0.21515 | 122.8363 | 122.6944 | 122.7676 | -0.32043 | -122.8683 | 122.4976 | 122.7676 | 122.5021 | 54.4464
2545.2812 | 122.9599 | -122.6166 | 0.21515 | 0.0025177 | -0.011166 | -0.079438 | -0.0093289 | -0.030443 | -0.050595 | -0.041674 | -0.0021057 | -0.018186 | 0.058123 | 0.046689 | -0.21958 | -0.015778 | -0.025816 | -0.09613 | 0.086975 | -0.10529 | -0.07782 | 0.054932 | -0.086975 | -0.022888 | -68.2388 | 0.18768 | -122.6852 | 0.14191 | -121.1151 | -122.2458 | -121.7972 | 122.5113 | -0.12817 | -0.29297 | 122.6715 | 122.5937 | 122.5296 | 0.082398 | 0.018311 | -0.068665 | -0.027466 | -0.073242 | 1.5015 | 0.8194 | 0.37079 | 0.88806 | 0.43945 | 0.16022 | 0.027466 | 1.5701 | 122.8271 | 0.19226 | 122.8729 | 122.7036 | 122.8043 | -0.32044 | -122.9004 | 122.5388 | 122.7585 | 122.5204 | 54.3777
2547.0625 | 122.9324 | -122.6349 | 0.21515 | -0.0051118 | -0.0098843 | -0.079011 | -0.0046291 | -0.031084 | -0.050167 | -0.039965 | -0.0051575 | -0.017972 | 0.059618 | 0.046903 | -0.21979 | -0.015351 | -0.024107 | -0.073242 | 0.10071 | -0.1236 | -0.091553 | 0.059509 | -0.11444 | -0.032043 | -68.2983 | 0.21057 | -122.6624 | 0.10986 | -121.1334 | -122.3236 | -121.8338 | 122.5113 | -0.11444 | -0.3067 | 122.6944 | 122.6028 | 122.5204 | 0.091553 | 0.009155 | -0.027466 | -0.004578 | -0.10529 | 1.5015 | 0.80109 | 0.31128 | 0.82855 | 0.33875 | 0.1831 | 0.032043 | 1.5289 | 122.7722 | 0.2243 | 122.8729 | 122.7356 | 122.8455 | -0.33875 | -122.8775 | 122.5433 | 122.7448 | 122.5616 | 54.3365
2548.8594 | 122.9095 | -122.6303 | 0.22888 | -0.012741 | -0.011166 | -0.078583 | -0.0063381 | -0.02553 | -0.048458 | -0.040178 | 0.0070497 | -0.018399 | 0.060472 | 0.048398 | -0.21872 | -0.015992 | -0.029875 | -0.086975 | 0.11902 | -0.13275 | -0.10529 | 0.045776 | -0.12817 | -0.036621 | -68.4036 | 0.20142 | -122.6852 | 0.11444 | -121.1197 | -122.3007 | -121.8292 | 122.4976 | -0.10986 | -0.33417 | 122.6761 | 122.5937 | 122.5021 | 0.09613 | 0.004577 | -0.054932 | -0.027466 | -0.11444 | 1.5106 | 0.80109 | 0.32959 | 0.85602 | 0.38452 | 0.17853 | 0.027465 | 1.5656 | 122.7997 | 0.25177 | 122.8867 | 122.7493 | 122.8317 | -0.36163 | -122.9141 | 122.525 | 122.7448 | 122.5433 | 54.2267
2550.6562 | 122.9919 | -122.5983 | 0.1831 | 0.0025177 | -0.012661 | -0.078797 | -0.0052701 | -0.026812 | -0.047817 | -0.038256 | 0.00094606 | -0.020963 | 0.057909 | 0.046689 | -0.22001 | -0.015992 | -0.021117 | -0.036621 | 0.073242 | -0.086975 | -0.022888 | 0.11902 | -0.054932 | 0.013733 | -68.4402 | 0.17853 | -122.6898 | 0.20599 | -121.0419 | -122.2229 | -121.7331 | 122.5113 | -0.10986 | -0.20599 | 122.7173 | 122.612 | 122.5433 | 0.10071 | 0.032043 | -0.091552 | -0.004577 | 0.022889 | 1.5564 | 0.86517 | 0.37537 | 0.95673 | 0.46692 | 0.20599 | 0.064087 | 1.6479 | 122.8958 | 0.16022 | 122.8683 | 122.6715 | 122.7768 | -0.27008 | -122.8729 | 122.5754 | 122.8043 | 122.5616 | 54.158
2552.4375 | 122.9004 | -122.6395 | 0.21973 | -0.0051118 | -0.010311 | -0.079011 | -0.0059109 | -0.028948 | -0.050595 | -0.042101 | 0.00094606 | -0.019681 | 0.061968 | 0.047544 | -0.21958 | -0.015565 | -0.023253 | -0.091553 | 0.11902 | -0.1236 | -0.10986 | 0.041199 | -0.091553 | -0.041199 | -68.573 | 0.20142 | -122.6807 | 0.12817 | -121.0968 | -122.3007 | -121.8246 | 122.5159 | -0.10071 | -0.32959 | 122.6807 | 122.5983 | 122.5479 | 0.082397 | 0.032043 | -0.041199 | -0.018311 | -0.091553 | 1.5427 | 0.81482 | 0.33875 | 0.85602 | 0.37994 | 0.16479 | 0.013733 | 1.5839 | 122.8088 | 0.24261 | 122.8821 | 122.7585 | 122.8409 | -0.34332 | -122.9004 | 122.5296 | 122.7676 | 122.5479 | 54.0665
2554.1562 | 122.8409 | -122.6715 | 0.23346 | -0.0051118 | -0.0092435 | -0.079011 | -0.0061245 | -0.028948 | -0.051235 | -0.044237 | 0.00094606 | -0.017758 | 0.059404 | 0.046476 | -0.21915 | -0.015351 | -0.02368 | -0.1236 | 0.11444 | -0.13275 | -0.16937 | -0.045776 | -0.19684 | -0.11902 | -68.8705 | 0.19684 | -122.7173 | 0.041199 | -121.2158 | -122.4335 | -121.9116 | 122.5388 | -0.11902 | -0.40283 | 122.6257 | 122.5525 | 122.4747 | 0.013732 | -0.064087 | -0.045776 | -0.036621 | -0.19226 | 1.4557 | 0.75989 | 0.23804 | 0.80566 | 0.28381 | 0.086975 | -0.036622 | 1.5015 | 122.7585 | 0.24719 | 122.9141 | 122.7859 | 122.8683 | -0.36621 | -122.9507 | 122.5021 | 122.7127 | 122.5479 | 53.801
2555.9375 | 122.9553 | -122.6166 | 0.16022 | -0.0051118 | -0.01138 | -0.078583 | -0.0082607 | -0.024035 | -0.050381 | -0.042314 | 0.0039979 | -0.021176 | 0.060045 | 0.043058 | -0.21915 | -0.015137 | -0.02133 | -0.086975 | 0.07782 | -0.09613 | -0.068665 | 0.10529 | -0.086975 | 0.004578 | -68.8614 | 0.15564 | -122.6944 | 0.10529 | -121.0831 | -122.2778 | -121.8155 | 122.5204 | -0.082397 | -0.22888 | 122.7219 | 122.6212 | 122.5296 | 0.10071 | 0.009155 | -0.07782 | -0.004577 | -0.054931 | 1.5335 | 0.80109 | 0.33875 | 0.87891 | 0.41656 | 0.20142 | 0.027465 | 1.6113 | 122.7997 | 0.17395 | 122.85 | 122.6944 | 122.7722 | -0.25635 | -122.8546 | 122.5479 | 122.7219 | 122.5296 | 53.7552
2557.7188 | 122.8775 | -122.6257 | 0.21057 | -0.012741 | -0.0098843 | -0.078583 | -0.0063381 | -0.028307 | -0.04974 | -0.044237 | -0.0021057 | -0.019467 | 0.05855 | 0.047117 | -0.21915 | -0.013001 | -0.018126 | -0.07782 | 0.082397 | -0.10986 | -0.1236 | 0.009155 | -0.14191 | -0.064087 | -69.0262 | 0.19684 | -122.7127 | 0.045776 | -121.1563 | -122.3877 | -121.8979 | 122.5159 | -0.12817 | -0.33417 | 122.6349 | 122.5616 | 122.4838 | 0.045776 | -0.032044 | -0.086976 | -0.013733 | -0.1648 | 1.4694 | 0.72784 | 0.23804 | 0.81482 | 0.32501 | 0.11902 | -0.013733 | 1.5564 | 122.7585 | 0.19226 | 122.9095 | 122.7081 | 122.8226 | -0.32043 | -122.9233 | 122.5021 | 122.6715 | 122.5479 | 53.5995
2559.5156 | 122.8821 | -122.6944 | 0.20142 | -0.012741 | -0.014798 | -0.079438 | -0.0061245 | -0.030871 | -0.052517 | -0.038896 | 0.00094606 | -0.020536 | 0.057482 | 0.044553 | -0.21851 | -0.01706 | -0.019835 | -0.12817 | 0.10986 | -0.13275 | -0.14191 | 0.022888 | -0.13733 | -0.054932 | -69.1544 | 0.16937 | -122.7493 | 0.013733 | -121.138 | -122.3648 | -121.9162 | 122.5616 | -0.091553 | -0.34332 | 122.7173 | 122.6395 | 122.5571 | 0.077819 | -0.004578 | -0.054932 | -0.032043 | -0.18768 | 1.5564 | 0.7782 | 0.32959 | 0.83313 | 0.38452 | 0.15564 | -0.009156 | 1.6113 | 122.7631 | 0.24261 | 122.9187 | 122.8043 | 122.8638 | -0.33417 | -122.9507 | 122.5525 | 122.7081 | 122.5662 | 53.54
2561.2344 | 122.9782 | -122.6761 | 0.14648 | -0.0051118 | -0.011166 | -0.080506 | -0.0065517 | -0.02553 | -0.050595 | -0.041246 | -0.0021057 | -0.019467 | 0.059618 | 0.04498 | -0.22129 | -0.016846 | -0.020903 | -0.11444 | 0.11444 | -0.14648 | -0.11902 | 0.018311 | -0.13733 | -0.059509 | -69.2047 | 0.14191 | -122.699 | 0.10986 | -121.0648 | -122.3053 | -121.8109 | 122.5296 | -0.032043 | -0.2655 | 122.6944 | 122.6166 | 122.5388 | 0.086975 | 0.009155 | -0.022889 | -0.004577 | -0.036621 | 1.6113 | 0.86517 | 0.37079 | 0.88806 | 0.39368 | 0.16479 | 0.027465 | 1.6342 | 122.8088 | 0.26093 | 122.8409 | 122.7905 | 122.818 | -0.29297 | -122.8455 | 122.5571 | 122.7859 | 122.5616 | 53.4714
2563.0156 | 123.0103 | -122.6395 | 0.15106 | 0.0025177 | -0.01437 | -0.079865 | -0.0069791 | -0.029162 | -0.049099 | -0.038256 | 0.00094606 | -0.019681 | 0.057909 | 0.044126 | -0.21937 | -0.015565 | -0.021971 | -0.082397 | 0.073242 | -0.10071 | -0.059509 | 0.1236 | -0.027466 | 0.050354 | -69.2368 | 0.13275 | -122.7356 | 0.13275 | -121.0098 | -122.2229 | -121.7789 | 122.5388 | -0.07782 | -0.21057 | 122.7631 | 122.6898 | 122.612 | 0.15106 | 0.073242 | -0.096131 | -0.018311 | -0.018311 | 1.6296 | 0.8606 | 0.41657 | 0.95673 | 0.5127 | 0.2243 | 0.041199 | 1.7258 | 122.8683 | 0.17395 | 122.8683 | 122.7127 | 122.7722 | -0.25177 | -122.8867 | 122.58 | 122.7722 | 122.5571 | 53.4027
2564.7969 | 123.0194 | -122.6578 | 0.12817 | -0.012741 | -0.013729 | -0.078156 | -0.0074063 | -0.029375 | -0.050808 | -0.041674 | 0.00094606 | -0.020322 | 0.058977 | 0.044126 | -0.22214 | -0.018342 | -0.019408 | -0.068665 | 0.091553 | -0.12817 | -0.054932 | 0.10986 | -0.018311 | 0.036621 | -69.3008 | 0.13275 | -122.6898 | 0.14191 | -121.0007 | -122.2229 | -121.7972 | 122.5296 | -0.036621 | -0.18311 | 122.7676 | 122.6944 | 122.6395 | 0.1648 | 0.10986 | -0.032043 | 0.004577 | 0.013733 | 1.6571 | 0.8606 | 0.43488 | 0.89264 | 0.46692 | 0.23804 | 0.073242 | 1.6891 | 122.8317 | 0.21973 | 122.8226 | 122.7493 | 122.7905 | -0.25635 | -122.818 | 122.6028 | 122.7997 | 122.5891 | 53.3569
2566.5781 | 122.9507 | -122.6578 | 0.14191 | -0.0051118 | -0.013516 | -0.07837 | -0.0052701 | -0.032152 | -0.051449 | -0.041246 | -0.0021057 | -0.019681 | 0.060045 | 0.048612 | -0.22236 | -0.014496 | -0.020689 | -0.091553 | 0.068665 | -0.10071 | -0.086975 | 0.059509 | -0.10529 | -0.013733 | -69.5068 | 0.11444 | -122.731 | 0.068665 | -121.0739 | -122.3145 | -121.8475 | 122.5571 | -0.073242 | -0.22888 | 122.7173 | 122.644 | 122.5525 | 0.086975 | -0.004578 | -0.073242 | -0.027466 | -0.073242 | 1.5839 | 0.81024 | 0.34332 | 0.88348 | 0.41657 | 0.16022 | 0.013733 | 1.6571 | 122.7997 | 0.16937 | 122.8455 | 122.7264 | 122.7722 | -0.24262 | -122.8729 | 122.5708 | 122.7264 | 122.5662 | 53.1509
2568.2969 | 122.9782 | -122.6624 | 0.16022 | -0.0051118 | -0.013943 | -0.080933 | -0.0078335 | -0.031084 | -0.051022 | -0.039537 | -0.0021057 | -0.020322 | 0.057482 | 0.04733 | -0.22193 | -0.016846 | -0.020049 | -0.11444 | 0.09613 | -0.09613 | -0.086975 | 0.054932 | -0.091553 | -0.022888 | -69.6075 | 0.1236 | -122.7448 | 0.073242 | -121.0602 | -122.3099 | -121.843 | 122.5662 | -0.064087 | -0.24719 | 122.7173 | 122.6395 | 122.5708 | 0.073242 | 0.004577 | -0.082397 | -0.036621 | -0.086975 | 1.6022 | 0.8194 | 0.35248 | 0.90179 | 0.43488 | 0.15106 | 0.009155 | 1.6846 | 122.818 | 0.19226 | 122.8683 | 122.7585 | 122.7859 | -0.25635 | -122.905 | 122.5754 | 122.7356 | 122.5479 | 53.0548
2570.0938 | 122.9874 | -122.6761 | 0.14191 | 0.010147 | -0.013516 | -0.082642 | -0.0082607 | -0.030657 | -0.048672 | -0.042101 | -0.0051575 | -0.020322 | 0.057695 | 0.046476 | -0.21958 | -0.017273 | -0.023253 | -0.11444 | 0.10071 | -0.10986 | -0.082397 | 0.073242 | -0.086975 | 0.004578 | -69.7037 | 0.11444 | -122.7127 | 0.07782 | -121.0236 | -122.287 | -121.8292 | 122.5662 | -0.041199 | -0.2243 | 122.7493 | 122.6807 | 122.5891 | 0.11444 | 0.022888 | -0.036622 | -0.027466 | -0.064087 | 1.6525 | 0.84686 | 0.3891 | 0.88348 | 0.42572 | 0.18311 | 0.027466 | 1.6891 | 122.7905 | 0.21057 | 122.8271 | 122.7768 | 122.7905 | -0.25177 | -122.8546 | 122.5937 | 122.7539 | 122.5616 | 52.9724
2571.875 | 122.9279 | -122.7264 | 0.18768 | 0.0025177 | -0.014157 | -0.079224 | -0.0063381 | -0.029589 | -0.051876 | -0.040605 | -0.0021057 | -0.017758 | 0.059832 | 0.04968 | -0.223 | -0.015137 | -0.020476 | -0.11902 | 0.1236 | -0.13275 | -0.14191 | -0.018311 | -0.14648 | -0.073242 | -69.8685 | 0.16022 | -122.7448 | 0.032043 | -121.0876 | -122.4014 | -121.9025 | 122.5937 | -0.064087 | -0.32959 | 122.7081 | 122.6532 | 122.58 | 0.059509 | -0.013733 | -0.018311 | -0.027466 | -0.15564 | 1.6388 | 0.82397 | 0.32501 | 0.84228 | 0.34332 | 0.11444 | -0.009156 | 1.6571 | 122.7768 | 0.25635 | 122.905 | 122.85 | 122.8867 | -0.32043 | -122.9324 | 122.5845 | 122.7585 | 122.6074 | 52.858
2573.6562 | 122.9553 | -122.644 | 0.13733 | -0.0051118 | -0.011593 | -0.076661 | -0.0046291 | -0.032366 | -0.050808 | -0.04146 | -0.0021057 | -0.020322 | 0.057482 | 0.048398 | -0.22043 | -0.016846 | -0.024535 | -0.054932 | 0.068665 | -0.091553 | -0.027466 | 0.13733 | -0.064087 | 0.018311 | -69.8273 | 0.11902 | -122.7173 | 0.11902 | -120.9915 | -122.2778 | -121.8109 | 122.5525 | -0.068664 | -0.16479 | 122.7814 | 122.6624 | 122.58 | 0.10986 | 0.027466 | -0.073242 | -0.01831 | -0.01831 | 1.6525 | 0.83313 | 0.36621 | 0.90637 | 0.43945 | 0.22888 | 0.064087 | 1.7258 | 122.8363 | 0.16022 | 122.8363 | 122.7127 | 122.7631 | -0.22888 | -122.8546 | 122.6166 | 122.7631 | 122.5891 | 52.8168
2575.3906 | 122.8867 | -122.7219 | 0.17395 | 0.0025177 | -0.014584 | -0.080506 | -0.0050565 | -0.030657 | -0.05209 | -0.041033 | 0.00094606 | -0.016904 | 0.058123 | 0.045408 | -0.22001 | -0.015778 | -0.019621 | -0.15106 | 0.11902 | -0.14648 | -0.16022 | -0.018311 | -0.16937 | -0.086975 | -70.1019 | 0.15564 | -122.7722 | 0 | -121.0739 | -122.3831 | -121.9254 | 122.5754 | -0.054931 | -0.33417 | 122.7036 | 122.6349 | 122.5525 | 0.059509 | -0.022889 | -0.050354 | -0.01831 | -0.17395 | 1.6479 | 0.79651 | 0.33875 | 0.84686 | 0.3891 | 0.12817 | -0.013733 | 1.6983 | 122.7722 | 0.2655 | 122.9279 | 122.8409 | 122.8775 | -0.32043 | -122.9462 | 122.5616 | 122.7219 | 122.5708 | 52.6199
2577.1562 | 122.8867 | -122.699 | 0.1831 | -0.0051118 | -0.01202 | -0.080079 | -0.0029201 | -0.02553 | -0.050595 | -0.038896 | -0.0021057 | -0.017758 | 0.060686 | 0.048612 | -0.21937 | -0.013856 | -0.021758 | -0.09613 | 0.10529 | -0.14191 | -0.14191 | -0.027466 | -0.18768 | -0.09613 | -70.2255 | 0.15106 | -122.7448 | -0.004578 | -121.0693 | -122.4152 | -121.9345 | 122.5571 | -0.077819 | -0.32501 | 122.6715 | 122.6028 | 122.5113 | 0.045777 | -0.045776 | -0.045776 | -0.032043 | -0.18768 | 1.6296 | 0.76447 | 0.28381 | 0.81024 | 0.32959 | 0.11444 | 0 | 1.6754 | 122.7402 | 0.24719 | 122.8958 | 122.8043 | 122.85 | -0.32501 | -122.9279 | 122.5571 | 122.6944 | 122.6028 | 52.4734
2578.9375 | 122.9462 | -122.6669 | 0.16937 | -0.0051118 | -0.0077481 | -0.079865 | -0.0054837 | -0.030871 | -0.050595 | -0.041033 | -0.0051575 | -0.018827 | 0.059618 | 0.047758 | -0.22065 | -0.015565 | -0.025603 | -0.10986 | 0.10529 | -0.13733 | -0.14191 | 0 | -0.1831 | -0.082397 | -70.2621 | 0.16479 | -122.731 | 0.082397 | -120.9869 | -122.3419 | -121.8475 | 122.5296 | -0.064087 | -0.31128 | 122.6669 | 122.5845 | 122.4838 | 0.054932 | -0.045776 | -0.064087 | -0.004578 | -0.086976 | 1.68 | 0.8194 | 0.32501 | 0.88348 | 0.3891 | 0.13733 | -0.004578 | 1.7441 | 122.8134 | 0.24262 | 122.8958 | 122.7722 | 122.8317 | -0.3067 | -122.9004 | 122.525 | 122.7493 | 122.5571 | 52.4048
2580.75 | 123.0011 | -122.6349 | 0.14191 | 0.0025177 | -0.010525 | -0.078797 | -0.0091153 | -0.027239 | -0.048031 | -0.040819 | -0.0021057 | -0.020322 | 0.061113 | 0.041135 | -0.21958 | -0.014924 | -0.023467 | -0.036621 | 0.073242 | -0.09613 | -0.018311 | 0.1236 | -0.054932 | 0.027466 | -70.2484 | 0.1236 | -122.7081 | 0.16479 | -120.8679 | -122.2321 | -121.7789 | 122.5388 | -0.068665 | -0.16022 | 122.7585 | 122.6624 | 122.58 | 0.1236 | 0.041198 | -0.073242 | -0.018311 | 0.022888 | 1.767 | 0.85602 | 0.40283 | 0.92926 | 0.47607 | 0.21973 | 0.077819 | 1.8402 | 122.8729 | 0.16937 | 122.8317 | 122.7081 | 122.7585 | -0.23804 | -122.85 | 122.6166 | 122.7997 | 122.5983 | 52.3865
2582.4688 | 122.9462 | -122.6578 | 0.15564 | -0.0051118 | -0.01202 | -0.077942 | -0.0063381 | -0.031298 | -0.048031 | -0.040605 | 0.00094606 | -0.019681 | 0.058977 | 0.040494 | -0.22022 | -0.016846 | -0.022612 | -0.07782 | 0.073242 | -0.09613 | -0.041199 | 0.12817 | -0.068665 | 0.013733 | -70.4361 | 0.15106 | -122.7081 | 0.11902 | -120.8954 | -122.2641 | -121.8155 | 122.5616 | -0.082398 | -0.19684 | 122.7859 | 122.6715 | 122.5891 | 0.10986 | 0.027465 | -0.050354 | -0.004578 | -0.036621 | 1.7624 | 0.84229 | 0.39368 | 0.89264 | 0.44403 | 0.2243 | 0.054931 | 1.8127 | 122.8271 | 0.16937 | 122.8592 | 122.731 | 122.8088 | -0.25177 | -122.8638 | 122.6166 | 122.7768 | 122.58 | 52.2217
2584.2344 | 122.8867 | -122.6852 | 0.1831 | 0.0025177 | -0.011166 | -0.07837 | -0.0022793 | -0.027453 | -0.051449 | -0.039537 | -0.0021057 | -0.018186 | 0.057482 | 0.049039 | -0.21894 | -0.013428 | -0.023039 | -0.11444 | 0.12817 | -0.15106 | -0.16022 | -0.022888 | -0.19684 | -0.091553 | -70.6741 | 0.17853 | -122.731 | 0.027466 | -120.9869 | -122.3923 | -121.8979 | 122.5342 | -0.054931 | -0.34332 | 122.6624 | 122.5937 | 122.4884 | 0.059509 | -0.045776 | -0.045776 | -0.004577 | -0.15564 | 1.6983 | 0.78735 | 0.29297 | 0.83313 | 0.33875 | 0.12817 | -0.009155 | 1.7441 | 122.7585 | 0.27924 | 122.9095 | 122.8134 | 122.8638 | -0.33417 | -122.9141 | 122.525 | 122.7127 | 122.5708 | 52.0111
2586.0312 | 122.8729 | -122.6761 | 0.19226 | -0.0051118 | -0.010525 | -0.077729 | -0.0039883 | -0.028521 | -0.04739 | -0.040605 | 0.00094606 | -0.01904 | 0.059404 | 0.050535 | -0.21744 | -0.015137 | -0.021758 | -0.1236 | 0.11444 | -0.13733 | -0.17853 | -0.054932 | -0.19226 | -0.09613 | -70.8344 | 0.17853 | -122.7539 | 0.018311 | -120.9915 | -122.4014 | -121.8933 | 122.5388 | -0.07782 | -0.37079 | 122.6212 | 122.58 | 122.4838 | 0.041199 | -0.054932 | -0.07782 | -0.013733 | -0.17395 | 1.6846 | 0.78278 | 0.27466 | 0.8606 | 0.35248 | 0.082397 | -0.041199 | 1.7624 | 122.7722 | 0.25177 | 122.9324 | 122.7905 | 122.8546 | -0.32959 | -122.9462 | 122.4976 | 122.6944 | 122.5525 | 51.8417
2587.75 | 122.9462 | -122.6395 | 0.1831 | 0.0025177 | -0.012875 | -0.077942 | -0.0086879 | -0.029162 | -0.051876 | -0.042314 | -0.0051575 | -0.020536 | 0.059618 | 0.04498 | -0.21958 | -0.014924 | -0.02603 | -0.10071 | 0.068665 | -0.10071 | -0.086975 | 0.059509 | -0.10986 | -0.013733 | -70.8344 | 0.16937 | -122.7127 | 0.09613 | -120.8542 | -122.2733 | -121.7834 | 122.5388 | -0.11444 | -0.27008 | 122.699 | 122.6257 | 122.5296 | 0.086975 | -0.009155 | -0.073243 | -0.013732 | -0.086975 | 1.7853 | 0.85602 | 0.36621 | 0.92926 | 0.43945 | 0.16022 | 0.013733 | 1.8585 | 122.8088 | 0.16937 | 122.8821 | 122.7081 | 122.8088 | -0.28381 | -122.8958 | 122.5525 | 122.7356 | 122.5388 | 51.8051
2589.4688 | 122.8821 | -122.6624 | 0.21973 | -0.0051118 | -0.016293 | -0.081147 | -0.0050565 | -0.031298 | -0.050381 | -0.042742 | -0.0051575 | -0.01904 | 0.05855 | 0.053953 | -0.21872 | -0.014496 | -0.022826 | -0.14191 | 0.11902 | -0.13733 | -0.16022 | -0.018311 | -0.12817 | -0.082397 | -71.0083 | 0.20599 | -122.7219 | 0.036621 | -120.9 | -122.3465 | -121.8658 | 122.525 | -0.10071 | -0.37994 | 122.644 | 122.58 | 122.5342 | 0.054932 | 0.009155 | -0.059509 | -0.013733 | -0.18311 | 1.7624 | 0.79651 | 0.31586 | 0.85602 | 0.37537 | 0.11902 | -0.022888 | 1.8219 | 122.7585 | 0.25635 | 122.9279 | 122.7814 | 122.8683 | -0.35706 | -122.9416 | 122.5021 | 122.699 | 122.5204 | 51.6541
2591.25 | 122.905 | -122.6578 | 0.21515 | 0.0025177 | -0.013089 | -0.079011 | -0.0069791 | -0.031298 | -0.049954 | -0.043169 | 0.00094606 | -0.015836 | 0.060045 | 0.050962 | -0.22086 | -0.014283 | -0.021544 | -0.11444 | 0.11444 | -0.14648 | -0.15564 | 0 | -0.13275 | -0.07782 | -71.0587 | 0.20599 | -122.7219 | 0.059509 | -120.8405 | -122.3145 | -121.8292 | 122.5113 | -0.10071 | -0.37079 | 122.6578 | 122.58 | 122.525 | 0.068664 | 0.013733 | -0.064087 | -0.009155 | -0.15564 | 1.8173 | 0.82855 | 0.34332 | 0.89264 | 0.40741 | 0.14648 | -0.009156 | 1.8814 | 122.7814 | 0.26093 | 122.9279 | 122.7722 | 122.8638 | -0.36163 | -122.937 | 122.5021 | 122.7173 | 122.5433 | 51.5991
2592.9844 | 122.9279 | -122.6257 | 0.21057 | -0.0051118 | -0.011593 | -0.078797 | -0.0048427 | -0.029802 | -0.051022 | -0.039324 | 0.00094606 | -0.018613 | 0.061754 | 0.054594 | -0.21872 | -0.015992 | -0.024748 | -0.073242 | 0.10529 | -0.1236 | -0.10529 | 0.064087 | -0.10986 | -0.027466 | -71.0907 | 0.20142 | -122.7356 | 0.10986 | -120.8313 | -122.2824 | -121.8155 | 122.5021 | -0.10529 | -0.31586 | 122.6898 | 122.5983 | 122.5159 | 0.09613 | 0.013733 | -0.10986 | -0.009155 | -0.10071 | 1.7944 | 0.81024 | 0.34332 | 0.92011 | 0.45319 | 0.18768 | 0.01831 | 1.9043 | 122.8455 | 0.22888 | 122.937 | 122.731 | 122.8271 | -0.33417 | -122.9462 | 122.5204 | 122.7356 | 122.5525 | 51.535
2594.7812 | 122.9874 | -122.6303 | 0.1831 | -0.012741 | -0.01202 | -0.081147 | -0.010397 | -0.033007 | -0.051449 | -0.03911 | -0.0021057 | -0.020322 | 0.0609 | 0.041563 | -0.21915 | -0.015565 | -0.019835 | -0.082397 | 0.082397 | -0.07782 | -0.013733 | 0.14648 | -0.027466 | 0.041199 | -71.1411 | 0.16022 | -122.6852 | 0.15106 | -120.726 | -122.1863 | -121.7697 | 122.5525 | -0.10071 | -0.19684 | 122.7768 | 122.6715 | 122.6028 | 0.11902 | 0.050354 | -0.054932 | -0.022888 | -0.032043 | 1.9043 | 0.8606 | 0.44403 | 0.91553 | 0.49896 | 0.2243 | 0.064087 | 1.9592 | 122.8363 | 0.16022 | 122.8455 | 122.7127 | 122.7905 | -0.26092 | -122.8683 | 122.6166 | 122.7814 | 122.5479 | 51.4893
2596.5625 | 122.9279 | -122.6578 | 0.20142 | 0.0025177 | -0.011593 | -0.079651 | -0.0052701 | -0.031084 | -0.049099 | -0.039324 | 0.00094606 | -0.018827 | 0.058977 | 0.048826 | -0.22107 | -0.014283 | -0.022398 | -0.073242 | 0.10986 | -0.11902 | -0.10529 | 0.054932 | -0.10529 | -0.027466 | -71.2738 | 0.19226 | -122.7127 | 0.086975 | -120.8084 | -122.2961 | -121.8155 | 122.5388 | -0.091553 | -0.3067 | 122.7127 | 122.6303 | 122.5525 | 0.091553 | 0.013733 | -0.054932 | -0.009155 | -0.11444 | 1.8494 | 0.84229 | 0.36163 | 0.89722 | 0.41657 | 0.17395 | 0.013733 | 1.9043 | 122.7997 | 0.22888 | 122.905 | 122.7676 | 122.85 | -0.32044 | -122.9141 | 122.5525 | 122.7448 | 122.5845 | 51.384
2598.3594 | 122.9782 | -122.6166 | 0.16937 | 0.0025177 | -0.014584 | -0.080506 | -0.0067653 | -0.031939 | -0.050381 | -0.040819 | -0.0051575 | -0.020963 | 0.060472 | 0.046903 | -0.21872 | -0.015778 | -0.026457 | -0.10071 | 0.086975 | -0.1236 | -0.091553 | 0.07782 | -0.073242 | 0 | -71.3974 | 0.17395 | -122.6761 | 0.1236 | -120.7169 | -122.1909 | -121.7422 | 122.493 | -0.082398 | -0.26093 | 122.6944 | 122.6166 | 122.5433 | 0.1236 | 0.050354 | -0.059509 | 0.004577 | -0.045777 | 1.8997 | 0.87433 | 0.42572 | 0.93384 | 0.48523 | 0.20142 | 0.032043 | 1.9592 | 122.7997 | 0.21057 | 122.85 | 122.7036 | 122.7905 | -0.29297 | -122.8455 | 122.525 | 122.7402 | 122.5159 | 51.2192
2600.0781 | 122.9919 | -122.6303 | 0.16022 | 0.0025177 | -0.013516 | -0.079224 | -0.0069791 | -0.030443 | -0.047817 | -0.044451 | -0.0021057 | -0.021176 | 0.060045 | 0.04733 | -0.21958 | -0.015351 | -0.025389 | -0.09613 | 0.07782 | -0.10071 | -0.068665 | 0.086975 | -0.07782 | 0.009155 | -71.4661 | 0.14191 | -122.699 | 0.12817 | -120.7077 | -122.1863 | -121.7422 | 122.5296 | -0.082397 | -0.22888 | 122.7173 | 122.6395 | 122.5525 | 0.10986 | 0.022888 | -0.068665 | -0.01831 | -0.032043 | 1.9226 | 0.88806 | 0.44403 | 0.95673 | 0.5127 | 0.18768 | 0.032043 | 1.9913 | 122.8271 | 0.17853 | 122.8409 | 122.7081 | 122.7722 | -0.26093 | -122.8592 | 122.5616 | 122.7585 | 122.5342 | 51.1642
2601.8594 | 122.9965 | -122.6532 | 0.15564 | -0.0051118 | -0.014584 | -0.079438 | -0.0082607 | -0.034075 | -0.051022 | -0.044451 | -0.0021057 | -0.019467 | 0.058977 | 0.039426 | -0.22043 | -0.015992 | -0.025816 | -0.082397 | 0.086975 | -0.082397 | -0.073242 | 0.082397 | -0.054932 | 0.036621 | -71.5897 | 0.14648 | -122.699 | 0.14648 | -120.6848 | -122.1725 | -121.7377 | 122.5708 | -0.068665 | -0.22888 | 122.7356 | 122.6898 | 122.5983 | 0.11902 | 0.027465 | -0.045777 | -0.009156 | -0.009156 | 1.9684 | 0.91553 | 0.48065 | 0.9613 | 0.52643 | 0.16479 | 0.009155 | 2.0142 | 122.8455 | 0.16937 | 122.8455 | 122.7402 | 122.7997 | -0.23804 | -122.8546 | 122.58 | 122.7997 | 122.5708 | 51.0635
2603.6406 | 123.024 | -122.6212 | 0.1831 | 0.0025177 | -0.018002 | -0.079865 | -0.0078335 | -0.035143 | -0.052944 | -0.038896 | -0.0051575 | -0.019895 | 0.058763 | 0.042844 | -0.22129 | -0.017701 | -0.024321 | -0.054932 | 0.073242 | -0.086975 | 0.009155 | 0.1831 | 0.004578 | 0.068665 | -71.5668 | 0.16479 | -122.6715 | 0.15106 | -120.6436 | -122.1588 | -121.7148 | 122.5342 | -0.10986 | -0.17395 | 122.8043 | 122.6898 | 122.6257 | 0.15564 | 0.091553 | -0.050354 | -0.01831 | -0.032043 | 1.9775 | 0.90637 | 0.46234 | 0.95673 | 0.5127 | 0.27008 | 0.09613 | 2.0279 | 122.8226 | 0.16022 | 122.8363 | 122.6944 | 122.7859 | -0.27008 | -122.8546 | 122.6303 | 122.7722 | 122.5662 | 51.0544
2605.4375 | 122.9279 | -122.6624 | 0.19684 | 0.010147 | -0.011166 | -0.079865 | -0.0048427 | -0.026384 | -0.051235 | -0.040178 | -0.0082091 | -0.01669 | 0.059191 | 0.04968 | -0.22001 | -0.015778 | -0.021971 | -0.068665 | 0.10071 | -0.11902 | -0.082397 | 0.050354 | -0.10529 | -0.041199 | -71.7773 | 0.18768 | -122.7036 | 0.09613 | -120.7352 | -122.2778 | -121.7972 | 122.5433 | -0.09613 | -0.27924 | 122.7127 | 122.6212 | 122.5571 | 0.07782 | 0.013733 | -0.041198 | -0.009155 | -0.10071 | 1.9272 | 0.86517 | 0.38452 | 0.90637 | 0.42572 | 0.16937 | 0.036622 | 1.9684 | 122.7997 | 0.21973 | 122.8912 | 122.7631 | 122.85 | -0.31586 | -122.9004 | 122.58 | 122.7585 | 122.5937 | 50.885
2607.1562 | 122.9965 | -122.644 | 0.1831 | 0.0025177 | -0.016507 | -0.079438 | -0.0076199 | -0.027025 | -0.04974 | -0.039751 | -0.0021057 | -0.020749 | 0.05855 | 0.04199 | -0.21872 | -0.016419 | -0.024962 | -0.09613 | 0.10071 | -0.11902 | -0.091553 | 0.073242 | -0.086975 | 0 | -71.8689 | 0.16937 | -122.6761 | 0.11902 | -120.6207 | -122.1909 | -121.7468 | 122.525 | -0.082397 | -0.27466 | 122.7173 | 122.644 | 122.5571 | 0.11902 | 0.032044 | -0.032043 | -0.013732 | -0.064086 | 2.0233 | 0.89722 | 0.45319 | 0.92926 | 0.48523 | 0.19226 | 0.027466 | 2.0554 | 122.7951 | 0.21973 | 122.8455 | 122.7448 | 122.8134 | -0.30212 | -122.8592 | 122.5525 | 122.7631 | 122.5479 | 50.7751
2608.9375 | 122.9187 | -122.6578 | 0.19226 | -0.012741 | -0.012448 | -0.080506 | -0.0076199 | -0.028734 | -0.053372 | -0.040605 | -0.0051575 | -0.01669 | 0.059832 | 0.053525 | -0.22086 | -0.01471 | -0.024107 | -0.068665 | 0.10071 | -0.11902 | -0.082397 | 0.050354 | -0.11902 | -0.036621 | -71.965 | 0.19226 | -122.7081 | 0.09613 | -120.7031 | -122.3007 | -121.8018 | 122.5388 | -0.091553 | -0.27466 | 122.7081 | 122.6212 | 122.5388 | 0.082398 | 0 | -0.050354 | 0 | -0.096131 | 1.9547 | 0.85602 | 0.35706 | 0.90637 | 0.40741 | 0.16937 | 0.036622 | 2.005 | 122.8043 | 0.21973 | 122.9004 | 122.7585 | 122.85 | -0.31128 | -122.9004 | 122.5754 | 122.7539 | 122.5891 | 50.6927
2610.7344 | 122.8867 | -122.6624 | 0.21057 | -0.012741 | -0.010525 | -0.077942 | -0.0033475 | -0.029162 | -0.049313 | -0.039537 | -0.0051575 | -0.018186 | 0.060045 | 0.046903 | -0.21787 | -0.012787 | -0.017912 | -0.11444 | 0.11444 | -0.13733 | -0.16479 | -0.054932 | -0.19226 | -0.10986 | -72.1344 | 0.21057 | -122.7173 | 0.050354 | -120.7306 | -122.3648 | -121.8338 | 122.525 | -0.09613 | -0.37537 | 122.6074 | 122.5525 | 122.4701 | 0.027466 | -0.054932 | -0.054931 | 0 | -0.16022 | 1.9318 | 0.82855 | 0.29755 | 0.88348 | 0.35248 | 0.082397 | -0.027466 | 1.9867 | 122.7676 | 0.25177 | 122.9279 | 122.7768 | 122.8729 | -0.3479 | -122.9279 | 122.4976 | 122.7127 | 122.5479 | 50.528
2612.5312 | 122.9874 | -122.6303 | 0.1831 | -0.0051118 | -0.013943 | -0.078156 | -0.0091153 | -0.028734 | -0.051022 | -0.040605 | -0.0082091 | -0.018613 | 0.059404 | 0.048826 | -0.22001 | -0.015778 | -0.017699 | -0.10529 | 0.086975 | -0.082397 | -0.073242 | 0.068665 | -0.086975 | 0.004578 | -72.1207 | 0.15106 | -122.7081 | 0.11902 | -120.5933 | -122.1909 | -121.7331 | 122.5479 | -0.09613 | -0.25635 | 122.699 | 122.6349 | 122.5433 | 0.086975 | -0.004578 | -0.07782 | -0.032043 | -0.064086 | 2.037 | 0.89722 | 0.43945 | 0.97504 | 0.51727 | 0.15106 | 0.009155 | 2.1149 | 122.8271 | 0.16937 | 122.8592 | 122.7173 | 122.7814 | -0.2655 | -122.8912 | 122.5571 | 122.7493 | 122.525 | 50.5096
2614.2656 | 122.9874 | -122.6349 | 0.18768 | -0.0051118 | -0.011593 | -0.078583 | -0.0033475 | -0.028307 | -0.048886 | -0.041033 | -0.0051575 | -0.018186 | 0.058763 | 0.053739 | -0.22022 | -0.016419 | -0.020689 | -0.10529 | 0.11902 | -0.11902 | -0.09613 | 0.027466 | -0.13733 | -0.036621 | -72.1848 | 0.16937 | -122.6807 | 0.15106 | -120.5841 | -122.2321 | -121.7285 | 122.5159 | -0.068664 | -0.28381 | 122.6624 | 122.5983 | 122.4976 | 0.082398 | -0.01831 | -0.045776 | -0.01831 | -0.036621 | 2.0508 | 0.90637 | 0.40283 | 0.95215 | 0.44861 | 0.14649 | 0.022889 | 2.0966 | 122.8317 | 0.23804 | 122.85 | 122.7539 | 122.8043 | -0.3067 | -122.8683 | 122.5388 | 122.7859 | 122.5296 | 50.4501
2616.0312 | 122.9874 | -122.6624 | 0.16937 | -0.0051118 | -0.012234 | -0.078156 | -0.0039883 | -0.026812 | -0.05209 | -0.039324 | -0.0021057 | -0.016904 | 0.057482 | 0.046049 | -0.21851 | -0.01706 | -0.020689 | -0.11444 | 0.11444 | -0.12817 | -0.11902 | 0.009155 | -0.16022 | -0.054932 | -72.3038 | 0.16022 | -122.731 | 0.11902 | -120.5978 | -122.2641 | -121.7606 | 122.5342 | -0.054932 | -0.28839 | 122.6715 | 122.6074 | 122.5021 | 0.073242 | -0.032043 | -0.068664 | -0.009156 | -0.050354 | 2.0645 | 0.90179 | 0.39825 | 0.97046 | 0.46692 | 0.13733 | 0.009155 | 2.1332 | 122.85 | 0.24262 | 122.8912 | 122.7768 | 122.8226 | -0.29755 | -122.9004 | 122.5433 | 122.7814 | 122.5479 | 50.3586
2617.8125 | 123.0011 | -122.6578 | 0.15106 | -0.0051118 | -0.015225 | -0.082001 | -0.0082607 | -0.029375 | -0.053799 | -0.042528 | 0.00094606 | -0.019895 | 0.059404 | 0.04498 | -0.22043 | -0.013428 | -0.022185 | -0.082397 | 0.041199 | -0.07782 | -0.027466 | 0.16022 | -0.018311 | 0.041199 | -72.258 | 0.13275 | -122.7448 | 0.12817 | -120.5063 | -122.1771 | -121.7331 | 122.58 | -0.10986 | -0.17853 | 122.818 | 122.699 | 122.6395 | 0.11902 | 0.059509 | -0.086975 | -0.018311 | -0.022888 | 2.1515 | 0.92468 | 0.48065 | 1.0117 | 0.56763 | 0.23804 | 0.050354 | 2.2385 | 122.8729 | 0.11902 | 122.8775 | 122.699 | 122.7905 | -0.22888 | -122.8958 | 122.6303 | 122.7859 | 122.5754 | 50.3998
2619.6094 | 123.0148 | -122.6532 | 0.14648 | -0.02037 | -0.013089 | -0.077302 | -0.0063381 | -0.028093 | -0.048245 | -0.037615 | -0.0051575 | -0.019681 | 0.05855 | 0.047758 | -0.21937 | -0.016419 | -0.021758 | -0.032043 | 0.073242 | -0.091553 | -0.022888 | 0.13275 | -0.059509 | 0.027466 | -72.3633 | 0.11444 | -122.7173 | 0.13733 | -120.5292 | -122.2137 | -121.7331 | 122.5616 | -0.073242 | -0.16937 | 122.7859 | 122.6807 | 122.5937 | 0.11902 | 0.032044 | -0.064087 | -0.032043 | -0.009155 | 2.124 | 0.92011 | 0.43945 | 0.98419 | 0.50354 | 0.2243 | 0.068665 | 2.1881 | 122.8546 | 0.16479 | 122.8317 | 122.7264 | 122.7676 | -0.23804 | -122.8638 | 122.6303 | 122.7905 | 122.6212 | 50.2899
2621.3438 | 122.9279 | -122.6715 | 0.17395 | 0.0025177 | -0.013729 | -0.079438 | -0.0031337 | -0.029375 | -0.052304 | -0.041674 | 0.00094606 | -0.018186 | 0.058763 | 0.046262 | -0.22086 | -0.015992 | -0.023039 | -0.086975 | 0.10529 | -0.13275 | -0.10529 | 0.041199 | -0.11902 | -0.054932 | -72.3999 | 0.16022 | -122.731 | 0.064087 | -120.575 | -122.2961 | -121.8155 | 122.5388 | -0.068664 | -0.27924 | 122.7127 | 122.6166 | 122.5525 | 0.077819 | 0.013732 | -0.059509 | -0.013733 | -0.10986 | 2.0966 | 0.85602 | 0.37537 | 0.91553 | 0.43488 | 0.17395 | 0.027465 | 2.1561 | 122.7951 | 0.23804 | 122.8912 | 122.7768 | 122.8317 | -0.3067 | -122.905 | 122.5662 | 122.7356 | 122.5845 | 50.2716
2623.125 | 122.9141 | -122.6761 | 0.1831 | -0.0051118 | -0.013729 | -0.078797 | -0.0059109 | -0.032152 | -0.048031 | -0.038042 | 0.00094606 | -0.018399 | 0.059618 | 0.046476 | -0.21937 | -0.014283 | -0.021971 | -0.10071 | 0.11444 | -0.14191 | -0.13733 | -0.009155 | -0.13275 | -0.045776 | -72.4686 | 0.13733 | -122.7402 | 0.050354 | -120.5521 | -122.3145 | -121.8246 | 122.5342 | -0.068664 | -0.32043 | 122.6669 | 122.6303 | 122.5433 | 0.096131 | 0.009156 | -0.064087 | -0.045776 | -0.13275 | 2.124 | 0.85144 | 0.36163 | 0.91553 | 0.42572 | 0.13275 | 0.004578 | 2.1881 | 122.7905 | 0.25635 | 122.8775 | 122.7905 | 122.8134 | -0.32501 | -122.9233 | 122.5388 | 122.7264 | 122.5754 | 50.2075
2624.8438 | 123.0057 | -122.6257 | 0.15106 | -0.0051118 | -0.012875 | -0.079651 | -0.0056973 | -0.029162 | -0.050167 | -0.03911 | 0.0039979 | -0.020322 | 0.057482 | 0.050748 | -0.21915 | -0.016419 | -0.024107 | -0.045776 | 0.068665 | -0.082397 | -0.022888 | 0.13275 | -0.050354 | 0.022888 | -72.3953 | 0.11444 | -122.7173 | 0.15106 | -120.4422 | -122.2 | -121.7285 | 122.5433 | -0.082397 | -0.17395 | 122.7585 | 122.6486 | 122.5754 | 0.10528 | 0.032043 | -0.091553 | -0.036621 | 0 | 2.1835 | 0.89722 | 0.42572 | 0.98877 | 0.51727 | 0.21515 | 0.059509 | 2.2751 | 122.8683 | 0.15106 | 122.8317 | 122.6944 | 122.7402 | -0.23346 | -122.8683 | 122.6028 | 122.7768 | 122.58 | 50.2304
2626.6406 | 122.9645 | -122.6532 | 0.16022 | 0.0025177 | -0.014584 | -0.080933 | -0.0080471 | -0.030016 | -0.04974 | -0.04146 | -0.0051575 | -0.018399 | 0.058123 | 0.046476 | -0.22001 | -0.011719 | -0.020476 | -0.10071 | 0.073242 | -0.10071 | -0.082397 | 0.086975 | -0.10986 | -0.004578 | -72.496 | 0.11444 | -122.7219 | 0.073242 | -120.4697 | -122.2458 | -121.7834 | 122.5525 | -0.086975 | -0.24261 | 122.7402 | 122.6486 | 122.5433 | 0.09613 | -0.009155 | -0.068665 | -0.045776 | -0.086975 | 2.1835 | 0.86975 | 0.40741 | 0.93842 | 0.47607 | 0.18768 | 0.018311 | 2.2522 | 122.7951 | 0.17395 | 122.8363 | 122.7264 | 122.7676 | -0.26093 | -122.8821 | 122.5708 | 122.7264 | 122.5525 | 50.1572
2628.4219 | 122.85 | -122.7081 | 0.19226 | 0.0025177 | -0.011593 | -0.07837 | -0.0052701 | -0.028307 | -0.04974 | -0.038042 | -0.0051575 | -0.016049 | 0.060259 | 0.04733 | -0.22129 | -0.014924 | -0.021544 | -0.1236 | 0.1236 | -0.14191 | -0.15564 | -0.054932 | -0.18768 | -0.11444 | -72.6837 | 0.16022 | -122.731 | 0.022888 | -120.5612 | -122.3877 | -121.8613 | 122.5662 | -0.068665 | -0.3479 | 122.6532 | 122.5937 | 122.5204 | 0.027466 | -0.045776 | -0.022888 | -0.032044 | -0.16937 | 2.1469 | 0.84686 | 0.32044 | 0.86975 | 0.34332 | 0.086975 | -0.013733 | 2.1698 | 122.7539 | 0.2655 | 122.8912 | 122.8317 | 122.8683 | -0.33417 | -122.9233 | 122.5525 | 122.731 | 122.5845 | 50.0244
2630.1562 | 122.9599 | -122.6486 | 0.13275 | -0.012741 | -0.011593 | -0.078156 | -0.0056973 | -0.030443 | -0.051235 | -0.044451 | -0.0021057 | -0.019467 | 0.058763 | 0.046049 | -0.21915 | -0.015778 | -0.021758 | -0.073242 | 0.086975 | -0.086975 | -0.036621 | 0.12817 | -0.073242 | 0.018311 | -72.5327 | 0.11444 | -122.7081 | 0.10529 | -120.3873 | -122.2275 | -121.7697 | 122.5616 | -0.045776 | -0.16937 | 122.7768 | 122.6669 | 122.5754 | 0.10529 | 0.013733 | -0.059509 | -0.01831 | -0.027465 | 2.2614 | 0.87891 | 0.42114 | 0.93842 | 0.48065 | 0.21515 | 0.050354 | 2.3209 | 122.8134 | 0.17395 | 122.8226 | 122.7356 | 122.7631 | -0.21973 | -122.8409 | 122.612 | 122.7539 | 122.5754 | 50.116
2631.9375 | 122.9828 | -122.6852 | 0.16022 | -0.012741 | -0.012234 | -0.080292 | -0.0069791 | -0.028307 | -0.04974 | -0.039751 | 0.00094606 | -0.020322 | 0.057268 | 0.050107 | -0.22236 | -0.014924 | -0.02368 | -0.050354 | 0.07782 | -0.11444 | -0.022888 | 0.14648 | -0.054932 | 0.027466 | -72.5739 | 0.11444 | -122.7264 | 0.1236 | -120.3552 | -122.2092 | -121.7331 | 122.5708 | -0.082397 | -0.1831 | 122.8317 | 122.7127 | 122.6303 | 0.14191 | 0.059509 | -0.041198 | -0.045776 | -0.036621 | 2.33 | 0.95215 | 0.47608 | 0.99335 | 0.51727 | 0.26093 | 0.091553 | 2.3712 | 122.85 | 0.19226 | 122.8409 | 122.7631 | 122.7997 | -0.27466 | -122.8867 | 122.6624 | 122.8088 | 122.6349 | 50.1114
2633.7344 | 123.0011 | -122.6578 | 0.12817 | -0.012741 | -0.011166 | -0.077942 | -0.0044155 | -0.028307 | -0.050167 | -0.040178 | -0.0051575 | -0.01904 | 0.058123 | 0.050962 | -0.21979 | -0.016846 | -0.023253 | -0.045776 | 0.054932 | -0.091553 | -0.018311 | 0.13733 | -0.064087 | 0.013733 | -72.6837 | 0.12817 | -122.7127 | 0.13275 | -120.3049 | -122.1909 | -121.7102 | 122.5662 | -0.073242 | -0.14649 | 122.7951 | 122.6715 | 122.5937 | 0.10529 | 0.027466 | -0.054932 | 0 | 0.004577 | 2.3529 | 0.94757 | 0.46692 | 1.0025 | 0.52185 | 0.22888 | 0.073242 | 2.4078 | 122.8455 | 0.14649 | 122.8409 | 122.7127 | 122.7859 | -0.21973 | -122.8409 | 122.6395 | 122.7905 | 122.612 | 49.9741
2635.5312 | 122.9965 | -122.6807 | 0.14648 | -0.0051118 | -0.013729 | -0.080079 | -0.0080471 | -0.029802 | -0.051022 | -0.042955 | -0.0051575 | -0.020749 | 0.058123 | 0.049894 | -0.22107 | -0.017273 | -0.019621 | -0.050354 | 0.07782 | -0.10986 | -0.032043 | 0.14191 | -0.027466 | 0.027466 | -72.7661 | 0.11444 | -122.699 | 0.10529 | -120.2682 | -122.1771 | -121.7331 | 122.5708 | -0.068664 | -0.17853 | 122.8226 | 122.7081 | 122.6532 | 0.13733 | 0.082397 | -0.018311 | -0.032043 | -0.041198 | 2.4124 | 0.94757 | 0.50354 | 0.96588 | 0.52185 | 0.25177 | 0.07782 | 2.4307 | 122.8043 | 0.18768 | 122.8134 | 122.7585 | 122.7951 | -0.25635 | -122.8455 | 122.6486 | 122.7859 | 122.6303 | 49.9146
2637.25 | 122.9507 | -122.6486 | 0.13733 | -0.0051118 | -0.010739 | -0.080719 | -0.0084743 | -0.029802 | -0.04974 | -0.038683 | -0.0021057 | -0.018613 | 0.060259 | 0.054166 | -0.21894 | -0.01471 | -0.020476 | -0.068665 | 0.07782 | -0.10529 | -0.032043 | 0.1236 | -0.073242 | 0.004578 | -72.8989 | 0.1236 | -122.7219 | 0.091553 | -120.3049 | -122.2275 | -121.7514 | 122.5433 | -0.059509 | -0.16937 | 122.7722 | 122.6532 | 122.5754 | 0.10986 | 0.032044 | -0.073242 | -0.013733 | -0.045776 | 2.3438 | 0.89722 | 0.42114 | 0.97046 | 0.49438 | 0.22888 | 0.073243 | 2.417 | 122.8134 | 0.18311 | 122.8455 | 122.7264 | 122.7722 | -0.24262 | -122.8592 | 122.6166 | 122.7402 | 122.58 | 49.7498
2639.0156 | 123.024 | -122.6624 | 0.14648 | -0.0051118 | -0.012875 | -0.077942 | -0.0093289 | -0.03322 | -0.051663 | -0.042742 | -0.0021057 | -0.020536 | 0.059618 | 0.045408 | -0.22022 | -0.015137 | -0.021971 | -0.050354 | 0.07782 | -0.09613 | -0.004578 | 0.15106 | -0.004578 | 0.045776 | -72.9492 | 0.11444 | -122.7036 | 0.12817 | -120.1859 | -122.1497 | -121.6873 | 122.5662 | -0.068664 | -0.15106 | 122.8134 | 122.7081 | 122.6578 | 0.14191 | 0.091552 | -0.041198 | -0.032043 | -0.01831 | 2.4765 | 0.97504 | 0.5127 | 1.0162 | 0.55389 | 0.24719 | 0.091552 | 2.5177 | 122.8317 | 0.17395 | 122.818 | 122.7402 | 122.7768 | -0.24261 | -122.85 | 122.6578 | 122.7905 | 122.612 | 49.7131
2640.7656 | 123.0194 | -122.6669 | 0.12817 | -0.0051118 | -0.014584 | -0.080506 | -0.0056973 | -0.03258 | -0.053799 | -0.038896 | -0.0051575 | -0.018399 | 0.058763 | 0.044126 | -0.22022 | -0.015137 | -0.02133 | -0.059509 | 0.073242 | -0.10529 | -0.004578 | 0.16937 | 0 | 0.07782 | -73.1232 | 0.10986 | -122.7173 | 0.1236 | -120.1538 | -122.1359 | -121.7056 | 122.5616 | -0.054932 | -0.13275 | 122.8363 | 122.7448 | 122.6669 | 0.18311 | 0.10529 | -0.050354 | -0.018311 | -0.004578 | 2.5131 | 0.9613 | 0.53101 | 1.0117 | 0.58136 | 0.27466 | 0.10071 | 2.5635 | 122.8409 | 0.17853 | 122.8271 | 122.7402 | 122.7768 | -0.23346 | -122.8455 | 122.6624 | 122.7905 | 122.6074 | 49.5438
2642.5625 | 123.0103 | -122.6761 | 0.13733 | 0.010147 | -0.014157 | -0.080719 | -0.0061245 | -0.029802 | -0.051235 | -0.039751 | -0.0051575 | -0.018399 | 0.059191 | 0.045621 | -0.22065 | -0.018769 | -0.021117 | -0.054932 | 0.068665 | -0.086975 | -0.004578 | 0.15564 | -0.018311 | 0.054932 | -73.3017 | 0.11444 | -122.7173 | 0.1236 | -120.1218 | -122.1588 | -121.701 | 122.5891 | -0.068664 | -0.14191 | 122.8317 | 122.731 | 122.6578 | 0.14191 | 0.068664 | -0.041199 | -0.022888 | -0.013733 | 2.5543 | 0.97504 | 0.51727 | 1.0162 | 0.55847 | 0.24261 | 0.082397 | 2.5955 | 122.8409 | 0.15564 | 122.8317 | 122.7448 | 122.7905 | -0.2243 | -122.8546 | 122.6715 | 122.7997 | 122.6212 | 49.3744
2644.3438 | 122.8867 | -122.7127 | 0.16022 | -0.0051118 | -0.014584 | -0.080292 | -0.0078335 | -0.031725 | -0.051449 | -0.041674 | -0.0021057 | -0.017545 | 0.059404 | 0.04968 | -0.22043 | -0.014924 | -0.019835 | -0.068665 | 0.07782 | -0.10071 | -0.07782 | 0.073242 | -0.07782 | -0.004578 | -73.5168 | 0.13275 | -122.731 | 0.022888 | -120.1996 | -122.2595 | -121.8063 | 122.612 | -0.082397 | -0.23804 | 122.7859 | 122.7081 | 122.6349 | 0.09613 | 0.022888 | -0.01831 | -0.027466 | -0.13733 | 2.5131 | 0.90637 | 0.45319 | 0.92468 | 0.4715 | 0.17395 | 0.022888 | 2.5314 | 122.7539 | 0.17853 | 122.8638 | 122.7905 | 122.8455 | -0.26093 | -122.8912 | 122.6349 | 122.7356 | 122.644 | 49.1959
2646.1406 | 122.8775 | -122.6944 | 0.1831 | -0.0051118 | -0.011166 | -0.080079 | -0.0027065 | -0.030871 | -0.048672 | -0.041033 | 0.00094606 | -0.017545 | 0.063677 | 0.053739 | -0.22001 | -0.015351 | -0.02133 | -0.091553 | 0.10071 | -0.11902 | -0.11444 | 0.009155 | -0.16937 | -0.086975 | -73.6633 | 0.16937 | -122.7493 | 0.032043 | -120.2042 | -122.3145 | -121.8155 | 122.5754 | -0.082397 | -0.29755 | 122.7036 | 122.6074 | 122.525 | 0.032044 | -0.050354 | -0.054932 | -0.013732 | -0.15106 | 2.4902 | 0.87891 | 0.37994 | 0.93384 | 0.43488 | 0.12817 | 0.004578 | 2.5452 | 122.7814 | 0.21973 | 122.9187 | 122.7951 | 122.8638 | -0.30212 | -122.9324 | 122.58 | 122.7264 | 122.6028 | 49.0311
2647.9219 | 122.937 | -122.6761 | 0.16937 | 0.0025177 | -0.013943 | -0.080719 | -0.0052701 | -0.030443 | -0.050808 | -0.039324 | -0.0021057 | -0.016049 | 0.058336 | 0.047544 | -0.21787 | -0.01471 | -0.027525 | -0.10529 | 0.10986 | -0.14648 | -0.14648 | -0.009155 | -0.13275 | -0.064087 | -73.7366 | 0.16022 | -122.7631 | 0.036621 | -120.1172 | -122.2733 | -121.7834 | 122.5296 | -0.05951 | -0.31586 | 122.6669 | 122.612 | 122.5433 | 0.082397 | 0.013733 | -0.086976 | -0.009156 | -0.13275 | 2.5589 | 0.89264 | 0.40283 | 0.97962 | 0.48981 | 0.13733 | 0 | 2.6459 | 122.7997 | 0.25635 | 122.9233 | 122.7859 | 122.8363 | -0.31586 | -122.9324 | 122.5296 | 122.7127 | 122.5708 | 48.9395
2649.7031 | 123.0011 | -122.6669 | 0.11444 | 0.0025177 | -0.010952 | -0.078797 | -0.0054837 | -0.029162 | -0.051235 | -0.041887 | -0.0021057 | -0.019467 | 0.058763 | 0.042844 | -0.21915 | -0.013001 | -0.022398 | -0.068665 | 0.091553 | -0.10529 | -0.050354 | 0.10071 | -0.073242 | 0.004578 | -73.7366 | 0.10529 | -122.7356 | 0.13275 | -119.9936 | -122.1725 | -121.669 | 122.5616 | -0.022888 | -0.16479 | 122.7676 | 122.6715 | 122.5937 | 0.10986 | 0.032044 | -0.068665 | -0.009155 | 0.01831 | 2.6733 | 0.99793 | 0.49439 | 1.0666 | 0.56305 | 0.20599 | 0.054932 | 2.742 | 122.8683 | 0.19684 | 122.8409 | 122.7585 | 122.7722 | -0.21973 | -122.85 | 122.6166 | 122.7997 | 122.5983 | 48.9304
2651.4375 | 123.0148 | -122.6807 | 0.1236 | -0.0051118 | -0.014798 | -0.079011 | -0.0091153 | -0.032152 | -0.053372 | -0.039537 | -0.0051575 | -0.019895 | 0.059191 | 0.043699 | -0.21808 | -0.015565 | -0.021971 | -0.082397 | 0.086975 | -0.10071 | -0.045776 | 0.12817 | -0.022888 | 0.036621 | -73.9151 | 0.10071 | -122.7356 | 0.11444 | -119.9295 | -122.1313 | -121.6782 | 122.58 | -0.036621 | -0.16937 | 122.8088 | 122.7173 | 122.6578 | 0.13733 | 0.07782 | -0.054932 | -0.022888 | -0.009155 | 2.7512 | 1.0025 | 0.54932 | 1.0574 | 0.60425 | 0.22888 | 0.054932 | 2.8061 | 122.85 | 0.18768 | 122.8363 | 122.7676 | 122.7814 | -0.2243 | -122.8592 | 122.6349 | 122.7951 | 122.5983 | 48.7656
2653.2031 | 122.8821 | -122.731 | 0.16937 | -0.0051118 | -0.014584 | -0.080292 | -0.0078335 | -0.028734 | -0.049954 | -0.04146 | -0.0082091 | -0.017331 | 0.059191 | 0.046262 | -0.21744 | -0.011933 | -0.021971 | -0.14191 | 0.13275 | -0.13275 | -0.15564 | -0.004578 | -0.14191 | -0.064087 | -74.1577 | 0.16022 | -122.7631 | -0.013733 | -120.0531 | -122.2916 | -121.8109 | 122.5983 | -0.036622 | -0.32501 | 122.7264 | 122.6669 | 122.5891 | 0.068664 | -0.009156 | -0.032044 | -0.009156 | -0.18311 | 2.6779 | 0.92011 | 0.43945 | 0.95215 | 0.4715 | 0.12817 | -0.022889 | 2.71 | 122.7493 | 0.2655 | 122.9233 | 122.8638 | 122.8912 | -0.30212 | -122.9324 | 122.5754 | 122.7173 | 122.5891 | 48.5733
2654.9375 | 122.8043 | -122.7127 | 0.17853 | -0.012741 | -0.012875 | -0.077729 | -0.0086879 | -0.030657 | -0.052517 | -0.042742 | 0.00094606 | -0.017118 | 0.0609 | 0.047117 | -0.22001 | -0.015992 | -0.023253 | -0.1236 | 0.1236 | -0.12817 | -0.15106 | -0.009155 | -0.15106 | -0.064087 | -74.2035 | 0.14648 | -122.7493 | 0.009155 | -119.9844 | -122.2504 | -121.7743 | 122.5845 | -0.054932 | -0.32959 | 122.7036 | 122.6486 | 122.5616 | 0.064087 | -0.022888 | -0.036621 | -0.032044 | -0.16937 | 2.7283 | 0.93842 | 0.46234 | 0.97504 | 0.49896 | 0.11902 | -0.022888 | 2.7649 | 122.7585 | 0.25177 | 122.8958 | 122.8363 | 122.8592 | -0.3067 | -122.9279 | 122.5616 | 122.7219 | 122.5891 | 48.5092
2656.7188 | 123.0194 | -122.6761 | 0.13275 | -0.0051118 | -0.013516 | -0.078583 | -0.0067653 | -0.033648 | -0.051449 | -0.043596 | -0.0021057 | -0.019895 | 0.058977 | 0.04733 | -0.21915 | -0.018128 | -0.020903 | -0.073242 | 0.07782 | -0.091553 | -0.041199 | 0.14191 | -0.004578 | 0.050354 | -74.1623 | 0.10986 | -122.7402 | 0.12817 | -119.8242 | -122.1359 | -121.6644 | 122.5845 | -0.054931 | -0.17395 | 122.818 | 122.7264 | 122.6715 | 0.14191 | 0.086975 | -0.064087 | -0.022888 | -0.004577 | 2.8519 | 1.0117 | 0.54016 | 1.0757 | 0.60425 | 0.23346 | 0.050354 | 2.916 | 122.8683 | 0.16937 | 122.85 | 122.7539 | 122.7859 | -0.2243 | -122.8729 | 122.6349 | 122.8043 | 122.6028 | 48.5138
2658.4375 | 122.9141 | -122.7402 | 0.1831 | 0.0025177 | -0.011166 | -0.078797 | -0.0061245 | -0.026812 | -0.051235 | -0.041674 | 0.00094606 | -0.016904 | 0.060472 | 0.052244 | -0.22065 | -0.017273 | -0.01834 | -0.1236 | 0.11902 | -0.14648 | -0.16022 | -0.018311 | -0.13733 | -0.07782 | -74.3454 | 0.16937 | -122.7539 | 0.009155 | -119.8791 | -122.2641 | -121.7606 | 122.5937 | -0.064086 | -0.34332 | 122.7219 | 122.6624 | 122.6028 | 0.068664 | 0.009155 | -0.013733 | -0.013732 | -0.17395 | 2.861 | 0.97961 | 0.47607 | 0.99335 | 0.48981 | 0.12817 | -0.013733 | 2.8748 | 122.7631 | 0.2655 | 122.9233 | 122.8592 | 122.9095 | -0.32959 | -122.937 | 122.58 | 122.7493 | 122.6166 | 48.3948
2660.2188 | 123.0011 | -122.6669 | 0.13275 | -0.012741 | -0.0073209 | -0.077302 | -0.0065517 | -0.03023 | -0.04974 | -0.043169 | 0.00094606 | -0.017758 | 0.059618 | 0.050962 | -0.21915 | -0.014283 | -0.019194 | -0.036621 | 0.064087 | -0.086975 | -0.022888 | 0.13733 | -0.059509 | 0.022888 | -74.4461 | 0.10986 | -122.7402 | 0.13275 | -119.7739 | -122.1451 | -121.6507 | 122.58 | -0.068664 | -0.15564 | 122.8043 | 122.6898 | 122.6074 | 0.10986 | 0.027466 | -0.073242 | -0.022888 | 0 | 2.8931 | 1.0162 | 0.52185 | 1.0895 | 0.59509 | 0.2243 | 0.064087 | 2.9663 | 122.8729 | 0.15106 | 122.85 | 122.731 | 122.7768 | -0.21973 | -122.8729 | 122.644 | 122.7997 | 122.6303 | 48.2208
2662.0156 | 123.0331 | -122.6852 | 0.13733 | -0.0051118 | -0.015438 | -0.081147 | -0.0078335 | -0.030443 | -0.051663 | -0.040819 | 0.00094606 | -0.020108 | 0.058977 | 0.044553 | -0.22107 | -0.014496 | -0.019194 | -0.059509 | 0.073242 | -0.10986 | -0.013733 | 0.15564 | -0.013733 | 0.059509 | -74.6292 | 0.10529 | -122.7173 | 0.11444 | -119.696 | -122.0993 | -121.6553 | 122.5754 | -0.064087 | -0.15106 | 122.8409 | 122.7448 | 122.6715 | 0.16937 | 0.09613 | -0.032043 | -0.032043 | -0.022888 | 2.9892 | 1.03 | 0.58594 | 1.062 | 0.61798 | 0.2655 | 0.09613 | 3.0212 | 122.8317 | 0.18311 | 122.8226 | 122.7585 | 122.7905 | -0.24719 | -122.8546 | 122.6715 | 122.7997 | 122.6257 | 48.056
2663.75 | 123.0011 | -122.6669 | 0.13275 | -0.0051118 | -0.013943 | -0.081574 | -0.0080471 | -0.03023 | -0.052304 | -0.039751 | 0.0039979 | -0.020108 | 0.059404 | 0.043058 | -0.22001 | -0.015778 | -0.01834 | -0.059509 | 0.073242 | -0.086975 | -0.027466 | 0.15106 | -0.013733 | 0.050354 | -74.8581 | 0.10529 | -122.7264 | 0.11444 | -119.7144 | -122.1359 | -121.6873 | 122.58 | -0.059509 | -0.16022 | 122.818 | 122.7173 | 122.6532 | 0.13733 | 0.073242 | -0.059509 | -0.027465 | -0.01831 | 2.9526 | 0.97961 | 0.53101 | 1.0391 | 0.59051 | 0.23804 | 0.059509 | 3.0121 | 122.8409 | 0.16022 | 122.8317 | 122.7402 | 122.7722 | -0.21973 | -122.8592 | 122.6395 | 122.7814 | 122.6074 | 47.8088
2665.5469 | 122.9233 | -122.6898 | 0.16479 | -0.0051118 | -0.011166 | -0.078797 | -0.0016385 | -0.032793 | -0.048672 | -0.042955 | -0.0051575 | -0.016049 | 0.059618 | 0.052457 | -0.22236 | -0.013428 | -0.023039 | -0.082397 | 0.10986 | -0.13275 | -0.1236 | 0.027466 | -0.10986 | -0.059509 | -75.0229 | 0.14648 | -122.7539 | 0.045776 | -119.7464 | -122.2458 | -121.7148 | 122.5571 | -0.054932 | -0.28839 | 122.7173 | 122.6303 | 122.58 | 0.073242 | 0.022888 | -0.064087 | -0.018311 | -0.11902 | 2.9434 | 0.97504 | 0.44403 | 1.0391 | 0.50812 | 0.16022 | 0.009155 | 3.0075 | 122.7997 | 0.24261 | 122.9004 | 122.7997 | 122.8363 | -0.29755 | -122.9187 | 122.5662 | 122.7356 | 122.6074 | 47.6669
2667.3281 | 122.9095 | -122.6852 | 0.17395 | -0.0051118 | -0.012234 | -0.079224 | -0.0035611 | -0.032366 | -0.051022 | -0.040605 | -0.0021057 | -0.018399 | 0.0609 | 0.048185 | -0.22001 | -0.014496 | -0.021544 | -0.091553 | 0.10529 | -0.13733 | -0.091553 | 0.064087 | -0.11902 | -0.054932 | -75.1328 | 0.14191 | -122.7585 | 0.064087 | -119.7052 | -122.2321 | -121.7331 | 122.5479 | -0.068664 | -0.2655 | 122.7493 | 122.6303 | 122.5662 | 0.082397 | 0.01831 | -0.073242 | -0.032043 | -0.10986 | 2.98 | 0.95215 | 0.45319 | 1.0254 | 0.52643 | 0.20142 | 0.045776 | 3.0533 | 122.8226 | 0.24262 | 122.9004 | 122.7905 | 122.8271 | -0.31128 | -122.9324 | 122.5937 | 122.7493 | 122.5937 | 47.5525
2669.0938 | 122.8729 | -122.731 | 0.16937 | 0.0025177 | -0.0081753 | -0.080933 | -0.0033475 | -0.029802 | -0.049099 | -0.040819 | 0.0039979 | -0.014768 | 0.058977 | 0.047544 | -0.22065 | -0.01471 | -0.01834 | -0.11444 | 0.12817 | -0.11902 | -0.16937 | -0.064087 | -0.20142 | -0.11902 | -75.3616 | 0.14648 | -122.7676 | 0 | -119.7464 | -122.3145 | -121.7697 | 122.612 | -0.041199 | -0.33875 | 122.6669 | 122.612 | 122.5296 | 0 | -0.082397 | -0.036621 | -0.022889 | -0.16937 | 2.9846 | 0.9613 | 0.41657 | 0.99793 | 0.45319 | 0.054932 | -0.050354 | 3.0212 | 122.7676 | 0.24719 | 122.9141 | 122.8592 | 122.8775 | -0.28839 | -122.937 | 122.5616 | 122.731 | 122.6166 | 47.3694
2670.9219 | 122.9233 | -122.6898 | 0.16022 | 0.010147 | -0.0098843 | -0.078797 | -0.0037747 | -0.031939 | -0.04974 | -0.041033 | -0.0021057 | -0.01669 | 0.062609 | 0.046262 | -0.21915 | -0.013215 | -0.02133 | -0.1236 | 0.1236 | -0.13733 | -0.14648 | -0.013733 | -0.16937 | -0.086975 | -75.4257 | 0.14648 | -122.7356 | 0.032043 | -119.6594 | -122.2504 | -121.7285 | 122.5525 | -0.036621 | -0.3067 | 122.6761 | 122.6028 | 122.5204 | 0.050354 | -0.032044 | -0.045777 | -0.013733 | -0.12817 | 3.0304 | 0.9613 | 0.43945 | 1.0071 | 0.48523 | 0.1236 | -0.009155 | 3.0762 | 122.7676 | 0.26093 | 122.8821 | 122.8134 | 122.8363 | -0.29755 | -122.8958 | 122.5433 | 122.7219 | 122.5662 | 47.2641
2672.7188 | 123.0148 | -122.644 | 0.1236 | 0.0025177 | -0.01437 | -0.078156 | -0.0076199 | -0.03322 | -0.051663 | -0.04146 | -0.0021057 | -0.020536 | 0.061327 | 0.041776 | -0.21894 | -0.014924 | -0.019408 | -0.064087 | 0.064087 | -0.11444 | -0.045776 | 0.14191 | -0.004578 | 0.064087 | -75.3845 | 0.09613 | -122.7264 | 0.11902 | -119.4855 | -122.1176 | -121.6278 | 122.5296 | -0.059509 | -0.16937 | 122.7859 | 122.7081 | 122.6395 | 0.17853 | 0.10986 | -0.082397 | -0.027466 | -0.004577 | 3.1586 | 1.0162 | 0.52643 | 1.0986 | 0.60882 | 0.25635 | 0.068665 | 3.241 | 122.8455 | 0.17853 | 122.8226 | 122.7081 | 122.7402 | -0.23804 | -122.85 | 122.5983 | 122.7631 | 122.58 | 47.2595
2674.5 | 122.9187 | -122.7173 | 0.16022 | -0.0051118 | -0.010952 | -0.080506 | -0.0039883 | -0.031511 | -0.048672 | -0.042955 | -0.0051575 | -0.016263 | 0.06389 | 0.053525 | -0.22086 | -0.012787 | -0.016844 | -0.1236 | 0.11444 | -0.13275 | -0.16937 | -0.027466 | -0.17853 | -0.091553 | -75.6546 | 0.14191 | -122.7676 | 0.022888 | -119.5999 | -122.2549 | -121.7194 | 122.5845 | -0.045776 | -0.32959 | 122.6898 | 122.6257 | 122.5388 | 0.041198 | -0.045777 | -0.050354 | -0.01831 | -0.13733 | 3.1174 | 0.99793 | 0.46234 | 1.0483 | 0.5127 | 0.10529 | -0.036622 | 3.1677 | 122.7905 | 0.24719 | 122.9095 | 122.8317 | 122.8592 | -0.29297 | -122.9279 | 122.5479 | 122.7402 | 122.5937 | 47.0627
2676.2188 | 123.0011 | -122.6715 | 0.12817 | -0.0051118 | -0.012448 | -0.078583 | -0.0039883 | -0.031939 | -0.04739 | -0.042314 | -0.0051575 | -0.020536 | 0.061754 | 0.053953 | -0.21915 | -0.013001 | -0.02133 | -0.082397 | 0.09613 | -0.1236 | -0.045776 | 0.09613 | -0.082397 | 0.004578 | -75.65 | 0.09613 | -122.7264 | 0.11902 | -119.4443 | -122.1405 | -121.6095 | 122.5479 | -0.032044 | -0.17395 | 122.7676 | 122.6761 | 122.5891 | 0.12817 | 0.041199 | -0.054931 | -0.032044 | -0.009155 | 3.2272 | 1.062 | 0.53101 | 1.1169 | 0.58594 | 0.21973 | 0.07782 | 3.2822 | 122.8455 | 0.21973 | 122.8226 | 122.7676 | 122.7676 | -0.25177 | -122.8546 | 122.6257 | 122.7905 | 122.5891 | 47.0215
2678 | 122.9965 | -122.6761 | 0.13275 | 0.0025177 | -0.015652 | -0.079651 | -0.0093289 | -0.028948 | -0.05209 | -0.041887 | -0.0021057 | -0.019254 | 0.059832 | 0.047544 | -0.21937 | -0.015992 | -0.020903 | -0.059509 | 0.082397 | -0.10529 | -0.036621 | 0.15106 | -0.004578 | 0.050354 | -75.7782 | 0.11444 | -122.7127 | 0.11444 | -119.3436 | -122.081 | -121.6232 | 122.5708 | -0.050354 | -0.16937 | 122.8271 | 122.7264 | 122.6715 | 0.15564 | 0.10071 | -0.036622 | -0.01831 | -0.01831 | 3.3325 | 1.0529 | 0.59509 | 1.0895 | 0.63171 | 0.25635 | 0.068665 | 3.3691 | 122.8271 | 0.18768 | 122.8271 | 122.7585 | 122.7905 | -0.23804 | -122.8455 | 122.6395 | 122.7905 | 122.6166 | 46.8979
2679.7812 | 122.9645 | -122.6898 | 0.14191 | 0.017777 | -0.012875 | -0.082215 | -0.0065517 | -0.026598 | -0.048245 | -0.04146 | 0.0039979 | -0.01904 | 0.061327 | 0.042417 | -0.21894 | -0.01471 | -0.023467 | -0.10071 | 0.068665 | -0.10071 | -0.073242 | 0.082397 | -0.086975 | 0 | -75.9384 | 0.14191 | -122.7356 | 0.068665 | -119.3756 | -122.168 | -121.6599 | 122.5891 | -0.073242 | -0.21515 | 122.7722 | 122.6898 | 122.6028 | 0.10071 | 0.013733 | -0.045777 | 0 | -0.073242 | 3.3142 | 1.03 | 0.52185 | 1.0757 | 0.56763 | 0.18311 | 0.027466 | 3.36 | 122.8043 | 0.16937 | 122.8775 | 122.7585 | 122.8317 | -0.24262 | -122.8775 | 122.6166 | 122.7585 | 122.5891 | 46.7514
2681.5781 | 122.8912 | -122.699 | 0.17853 | 0.010147 | -0.012234 | -0.080079 | -0.0050565 | -0.031298 | -0.05209 | -0.04146 | 0.00094606 | -0.016263 | 0.063677 | 0.053098 | -0.22086 | -0.01471 | -0.019194 | -0.14191 | 0.11902 | -0.15106 | -0.16479 | -0.013733 | -0.15564 | -0.082397 | -76.1124 | 0.15564 | -122.7585 | -0.018311 | -119.3893 | -122.2504 | -121.7194 | 122.5479 | -0.059509 | -0.34332 | 122.6852 | 122.6166 | 122.5433 | 0.068665 | -0.004578 | -0.059509 | -0.022888 | -0.19684 | 3.3096 | 0.97962 | 0.44861 | 1.0391 | 0.50812 | 0.13733 | -0.013733 | 3.3691 | 122.7402 | 0.27008 | 122.9141 | 122.818 | 122.8546 | -0.32959 | -122.937 | 122.5342 | 122.6807 | 122.5571 | 46.5866
2683.2969 | 122.9416 | -122.6944 | 0.15106 | -0.0051118 | -0.013089 | -0.079865 | -0.0050565 | -0.029162 | -0.049954 | -0.040178 | 0.00094606 | -0.015836 | 0.061541 | 0.049253 | -0.22193 | -0.013642 | -0.021758 | -0.091553 | 0.11902 | -0.13275 | -0.09613 | 0.054932 | -0.10071 | -0.054932 | -76.0529 | 0.13733 | -122.7585 | 0.050354 | -119.2978 | -122.2137 | -121.6507 | 122.5616 | -0.032043 | -0.24719 | 122.7493 | 122.6395 | 122.5937 | 0.077819 | 0.032043 | -0.064087 | -0.013733 | -0.10071 | 3.3966 | 1.0437 | 0.48065 | 1.1078 | 0.54474 | 0.18768 | 0.036621 | 3.4607 | 122.8088 | 0.25177 | 122.8958 | 122.8134 | 122.8317 | -0.28381 | -122.9095 | 122.5983 | 122.7448 | 122.6028 | 46.6415
2685.0625 | 122.8638 | -122.699 | 0.16937 | -0.0051118 | -0.010739 | -0.079224 | -0.0050565 | -0.028521 | -0.050595 | -0.039965 | 0.00094606 | -0.017331 | 0.058123 | 0.051816 | -0.21958 | -0.016846 | -0.020903 | -0.10986 | 0.11444 | -0.13275 | -0.15106 | -0.009155 | -0.17853 | -0.10529 | -76.1536 | 0.13733 | -122.7356 | -0.009155 | -119.3298 | -122.2687 | -121.7148 | 122.5662 | -0.054932 | -0.32044 | 122.6898 | 122.5937 | 122.5204 | 0.027465 | -0.045777 | -0.036621 | -0.032044 | -0.17853 | 3.3691 | 0.98419 | 0.4303 | 1.0208 | 0.46692 | 0.1236 | -0.018311 | 3.4058 | 122.7264 | 0.24719 | 122.8729 | 122.8134 | 122.8363 | -0.30212 | -122.905 | 122.5479 | 122.6898 | 122.5891 | 46.5454
2686.8594 | 123.0057 | -122.644 | 0.13275 | 0.0025177 | -0.011593 | -0.080292 | -0.0039883 | -0.024462 | -0.04739 | -0.038896 | -0.0021057 | -0.017972 | 0.060472 | 0.038572 | -0.21937 | -0.01471 | -0.020903 | -0.027466 | 0.064087 | -0.082397 | -0.027466 | 0.13275 | -0.054932 | 0.013733 | -76.0803 | 0.11444 | -122.699 | 0.14648 | -119.1193 | -122.1039 | -121.5683 | 122.5616 | -0.068664 | -0.16022 | 122.7768 | 122.6578 | 122.5891 | 0.09613 | 0.027465 | -0.054932 | -0.01831 | 0.013733 | 3.5248 | 1.0757 | 0.54016 | 1.1307 | 0.59509 | 0.21515 | 0.054931 | 3.5797 | 122.8455 | 0.14648 | 122.8134 | 122.7081 | 122.7585 | -0.21515 | -122.8317 | 122.6166 | 122.7905 | 122.6166 | 46.5637
2688.5938 | 122.8867 | -122.7219 | 0.18768 | -0.012741 | -0.011593 | -0.079651 | -0.0059109 | -0.032366 | -0.051022 | -0.040178 | 0.00094606 | -0.016904 | 0.061327 | 0.041135 | -0.21808 | -0.014069 | -0.020903 | -0.1236 | 0.13733 | -0.1236 | -0.17853 | -0.013733 | -0.15106 | -0.068665 | -76.3229 | 0.14648 | -122.7539 | 0.004578 | -119.1925 | -122.2275 | -121.6873 | 122.5983 | -0.050354 | -0.36621 | 122.7081 | 122.6532 | 122.5708 | 0.054931 | -0.027466 | -0.032043 | -0.041199 | -0.1831 | 3.5294 | 1.0345 | 0.49438 | 1.0666 | 0.52643 | 0.10986 | -0.054932 | 3.5614 | 122.7585 | 0.26093 | 122.9004 | 122.8592 | 122.8683 | -0.31128 | -122.9416 | 122.5433 | 122.7264 | 122.5983 | 46.3989
2690.375 | 122.9919 | -122.6715 | 0.13733 | 0.0025177 | -0.012661 | -0.077942 | -0.0065517 | -0.03023 | -0.048672 | -0.039537 | -0.0021057 | -0.017972 | 0.0609 | 0.055662 | -0.21894 | -0.015992 | -0.019621 | -0.059509 | 0.054932 | -0.082397 | -0.022888 | 0.14648 | -0.059509 | 0.022888 | -76.1536 | 0.1236 | -122.7264 | 0.12817 | -119.0506 | -122.1222 | -121.582 | 122.5891 | -0.082397 | -0.16022 | 122.818 | 122.6944 | 122.612 | 0.10528 | 0.022888 | -0.054931 | -0.013733 | -0.009155 | 3.6209 | 1.0895 | 0.54932 | 1.1444 | 0.60425 | 0.22888 | 0.059509 | 3.6758 | 122.8546 | 0.13733 | 122.85 | 122.7264 | 122.7951 | -0.21973 | -122.8638 | 122.6486 | 122.7997 | 122.612 | 46.5179
2692.1562 | 122.8867 | -122.7081 | 0.16479 | -0.0051118 | -0.012234 | -0.080719 | -0.0054837 | -0.025103 | -0.050595 | -0.039537 | -0.0021057 | -0.016049 | 0.061754 | 0.052671 | -0.21851 | -0.015778 | -0.01898 | -0.13733 | 0.11444 | -0.14648 | -0.17395 | -0.050354 | -0.18768 | -0.10986 | -76.4877 | 0.15564 | -122.7539 | -0.013733 | -119.133 | -122.2641 | -121.6782 | 122.5616 | -0.050354 | -0.33874 | 122.6578 | 122.5983 | 122.5204 | 0.036621 | -0.041199 | -0.045776 | -0.009155 | -0.17853 | 3.5751 | 1.03 | 0.44403 | 1.0757 | 0.48981 | 0.09613 | -0.027466 | 3.6209 | 122.7402 | 0.26093 | 122.9095 | 122.8226 | 122.8638 | -0.31128 | -122.9187 | 122.5342 | 122.6944 | 122.5708 | 46.2204
2693.9531 | 122.8775 | -122.7081 | 0.16937 | 0.0025177 | -0.016293 | -0.079438 | -0.0063381 | -0.028307 | -0.051876 | -0.039324 | -0.0021057 | -0.016049 | 0.06389 | 0.044767 | -0.21937 | -0.016205 | -0.01898 | -0.14648 | 0.13275 | -0.14191 | -0.16479 | -0.004578 | -0.15106 | -0.073242 | -76.4511 | 0.15564 | -122.7859 | -0.022888 | -119.046 | -122.2229 | -121.6873 | 122.5662 | -0.036622 | -0.33417 | 122.7036 | 122.6349 | 122.5571 | 0.068665 | -0.009155 | -0.07782 | -0.013733 | -0.19226 | 3.6621 | 1.0208 | 0.48523 | 1.0986 | 0.56305 | 0.13733 | -0.022888 | 3.7399 | 122.7631 | 0.27466 | 122.9416 | 122.8409 | 122.8638 | -0.31128 | -122.9553 | 122.5433 | 122.6852 | 122.5616 | 46.257
2695.75 | 122.9279 | -122.699 | 0.17395 | 0.0025177 | -0.01202 | -0.079651 | -0.0048427 | -0.031084 | -0.049313 | -0.040819 | -0.0021057 | -0.017331 | 0.062609 | 0.049894 | -0.21894 | -0.015137 | -0.017912 | -0.07782 | 0.11902 | -0.13275 | -0.10529 | 0.036621 | -0.11444 | -0.050354 | -76.3962 | 0.14191 | -122.7539 | 0.054932 | -118.9362 | -122.1634 | -121.6141 | 122.5662 | -0.054931 | -0.27924 | 122.7356 | 122.6486 | 122.5845 | 0.082397 | 0.01831 | -0.054931 | -0.032043 | -0.11902 | 3.7628 | 1.0849 | 0.53558 | 1.1398 | 0.59051 | 0.16937 | 0.027465 | 3.8177 | 122.8088 | 0.25177 | 122.8958 | 122.818 | 122.8409 | -0.3067 | -122.9279 | 122.5937 | 122.7539 | 122.6212 | 46.3028
2697.4844 | 122.9965 | -122.6578 | 0.11902 | 0.010147 | -0.010098 | -0.080079 | -0.0061245 | -0.030016 | -0.049313 | -0.039537 | -0.0051575 | -0.019467 | 0.059618 | 0.053312 | -0.22022 | -0.013215 | -0.019621 | -0.045776 | 0.068665 | -0.10986 | -0.032043 | 0.11902 | -0.054932 | 0.013733 | -76.4557 | 0.10986 | -122.7036 | 0.13733 | -118.7943 | -122.081 | -121.5134 | 122.5479 | -0.050354 | -0.15106 | 122.7768 | 122.6715 | 122.6028 | 0.1236 | 0.054931 | -0.045776 | -0.009156 | 0.01831 | 3.8635 | 1.1444 | 0.57678 | 1.1902 | 0.62256 | 0.22888 | 0.07782 | 3.9093 | 122.8409 | 0.17853 | 122.8134 | 122.7264 | 122.7676 | -0.22888 | -122.8226 | 122.6257 | 122.7951 | 122.612 | 46.2021
2699.25 | 123.0194 | -122.6715 | 0.12817 | -0.012741 | -0.016079 | -0.080292 | -0.0071927 | -0.030443 | -0.052304 | -0.040819 | 0.00094606 | -0.020322 | 0.062181 | 0.052457 | -0.21958 | -0.013428 | -0.020689 | -0.091553 | 0.082397 | -0.091553 | -0.059509 | 0.13275 | -0.041199 | 0.045776 | -76.5289 | 0.1236 | -122.7173 | 0.13275 | -118.6935 | -122.0535 | -121.5134 | 122.58 | -0.045777 | -0.18768 | 122.8043 | 122.7173 | 122.6303 | 0.13733 | 0.050354 | -0.045776 | -0.004578 | 0.004577 | 3.978 | 1.1581 | 0.61798 | 1.2039 | 0.66376 | 0.2243 | 0.032044 | 4.0237 | 122.85 | 0.17395 | 122.8409 | 122.7539 | 122.7951 | -0.21973 | -122.8455 | 122.612 | 122.8043 | 122.58 | 46.1426
2701.0469 | 122.9782 | -122.6486 | 0.14191 | -0.0051118 | -0.014584 | -0.082428 | -0.0086879 | -0.031298 | -0.052304 | -0.041674 | -0.0021057 | -0.01904 | 0.062822 | 0.048185 | -0.21872 | -0.013856 | -0.02368 | -0.10986 | 0.086975 | -0.10986 | -0.073242 | 0.09613 | -0.07782 | 0.009155 | -76.7395 | 0.11902 | -122.7036 | 0.086975 | -118.6798 | -122.0764 | -121.55 | 122.5388 | -0.054932 | -0.21515 | 122.7448 | 122.6578 | 122.5708 | 0.11902 | 0.032043 | -0.054931 | -0.022888 | -0.054932 | 3.9688 | 1.0986 | 0.57221 | 1.1536 | 0.62714 | 0.20599 | 0.036621 | 4.0237 | 122.7905 | 0.19684 | 122.8226 | 122.7356 | 122.7676 | -0.25177 | -122.8455 | 122.5754 | 122.7356 | 122.5388 | 45.9091
2702.7812 | 122.8867 | -122.6578 | 0.16022 | 0.0025177 | -0.010952 | -0.078156 | -0.0033475 | -0.028521 | -0.051235 | -0.04146 | -0.0051575 | -0.016263 | 0.062609 | 0.046689 | -0.22257 | -0.014924 | -0.020476 | -0.07782 | 0.10986 | -0.12817 | -0.10986 | 0.013733 | -0.13733 | -0.091553 | -76.8173 | 0.14191 | -122.7631 | 0.027466 | -118.7256 | -122.2229 | -121.6141 | 122.5296 | -0.050354 | -0.27008 | 122.6715 | 122.5662 | 122.5204 | 0.036621 | -0.009155 | -0.10529 | -0.01831 | -0.13275 | 3.9322 | 1.0437 | 0.43488 | 1.149 | 0.54016 | 0.14191 | 0.018311 | 4.0375 | 122.7905 | 0.23804 | 122.905 | 122.7676 | 122.7997 | -0.28839 | -122.9233 | 122.5479 | 122.6852 | 122.58 | 45.8405
2704.5 | 122.8729 | -122.7081 | 0.20142 | 0.0025177 | -0.014798 | -0.081147 | -0.0050565 | -0.033434 | -0.052944 | -0.040605 | -0.0051575 | -0.01669 | 0.062181 | 0.058866 | -0.22129 | -0.013856 | -0.022826 | -0.14648 | 0.10529 | -0.16022 | -0.17395 | -0.009155 | -0.14191 | -0.082397 | -76.886 | 0.16022 | -122.7631 | -0.022888 | -118.6569 | -122.2046 | -121.6324 | 122.5479 | -0.09613 | -0.37537 | 122.699 | 122.6257 | 122.5662 | 0.07782 | 0.01831 | -0.054932 | -0.041199 | -0.2243 | 4.0512 | 1.0757 | 0.50354 | 1.1307 | 0.55847 | 0.15106 | -0.013733 | 4.1061 | 122.7402 | 0.2655 | 122.9233 | 122.8134 | 122.8683 | -0.36163 | -122.9645 | 122.5342 | 122.6852 | 122.5616 | 45.8221
2706.2969 | 122.9004 | -122.6944 | 0.19684 | 0.0025177 | -0.012234 | -0.079865 | -0.0052701 | -0.028307 | -0.050595 | -0.03911 | -0.0051575 | -0.01669 | 0.061968 | 0.046262 | -0.21915 | -0.012574 | -0.020049 | -0.11444 | 0.11444 | -0.13733 | -0.14191 | -0.027466 | -0.14648 | -0.073242 | -76.4786 | 0.13733 | -122.7585 | 0.004578 | -118.483 | -122.1725 | -121.5775 | 122.5571 | -0.082397 | -0.33875 | 122.6669 | 122.6212 | 122.5479 | 0.064087 | -0.009155 | -0.064087 | -0.059509 | -0.19226 | 4.2114 | 1.1169 | 0.52185 | 1.181 | 0.58594 | 0.10986 | -0.004578 | 4.2755 | 122.7631 | 0.25177 | 122.8958 | 122.8088 | 122.8317 | -0.33417 | -122.9553 | 122.5525 | 122.699 | 122.58 | 46.2158
2708.0156 | 122.9736 | -122.6852 | 0.15564 | -0.0051118 | -0.012661 | -0.079651 | -0.0063381 | -0.03322 | -0.049954 | -0.043169 | -0.0021057 | -0.01904 | 0.060259 | 0.047117 | -0.2183 | -0.015351 | -0.019621 | -0.068665 | 0.068665 | -0.064087 | -0.045776 | 0.12817 | -0.07782 | 0.022888 | -76.3824 | 0.11902 | -122.731 | 0.09613 | -118.3594 | -122.1085 | -121.5134 | 122.6212 | -0.086975 | -0.20142 | 122.8134 | 122.7081 | 122.6074 | 0.086975 | -0.013733 | -0.045776 | -0.036621 | -0.05951 | 4.3259 | 1.1719 | 0.57678 | 1.2177 | 0.62256 | 0.19226 | 0.018311 | 4.3716 | 122.8271 | 0.13275 | 122.85 | 122.7539 | 122.8043 | -0.21973 | -122.8867 | 122.6395 | 122.7814 | 122.6166 | 46.3028
2709.7969 | 122.8958 | -122.7081 | 0.19684 | 0.0025177 | -0.013729 | -0.080292 | -0.0050565 | -0.031939 | -0.053158 | -0.040819 | -0.0021057 | -0.017331 | 0.06325 | 0.050321 | -0.22129 | -0.015778 | -0.020049 | -0.11902 | 0.11902 | -0.1236 | -0.16022 | -0.027466 | -0.14648 | -0.07782 | -76.4145 | 0.17395 | -122.7448 | 0.013733 | -118.3044 | -122.1634 | -121.5454 | 122.5845 | -0.077819 | -0.35706 | 122.6807 | 122.6303 | 122.5616 | 0.045776 | -0.022888 | -0.036621 | -0.022888 | -0.18311 | 4.4037 | 1.1627 | 0.54474 | 1.1993 | 0.58136 | 0.09613 | -0.036621 | 4.4403 | 122.7585 | 0.24261 | 122.9187 | 122.8271 | 122.8821 | -0.32043 | -122.9416 | 122.5479 | 122.7219 | 122.5891 | 46.2936
2711.5781 | 122.8821 | -122.6898 | 0.18768 | -0.0051118 | -0.015652 | -0.082428 | -0.0048427 | -0.028093 | -0.050167 | -0.040178 | -0.0051575 | -0.016904 | 0.062395 | 0.045835 | -0.21723 | -0.015137 | -0.019194 | -0.16479 | 0.10986 | -0.13733 | -0.16479 | -0.004578 | -0.15106 | -0.07782 | -76.3275 | 0.16937 | -122.7356 | -0.004578 | -118.1992 | -122.1588 | -121.5729 | 122.5525 | -0.07782 | -0.35248 | 122.6852 | 122.612 | 122.5388 | 0.059509 | -0.013733 | -0.045777 | -0.01831 | -0.19226 | 4.4907 | 1.1169 | 0.53101 | 1.1627 | 0.57678 | 0.13275 | -0.027466 | 4.5364 | 122.731 | 0.24719 | 122.905 | 122.7997 | 122.8592 | -0.32501 | -122.9233 | 122.525 | 122.6852 | 122.525 | 46.3623
2713.3594 | 122.8821 | -122.699 | 0.17395 | 0.0025177 | -0.015011 | -0.080079 | -0.0074063 | -0.035143 | -0.052944 | -0.041246 | -0.0021057 | -0.017545 | 0.060259 | 0.050962 | -0.21744 | -0.013856 | -0.017058 | -0.086975 | 0.082397 | -0.11902 | -0.10529 | 0.064087 | -0.09613 | -0.032043 | -76.4465 | 0.17395 | -122.7676 | 0.004578 | -118.0939 | -122.1313 | -121.5637 | 122.58 | -0.091553 | -0.27924 | 122.7631 | 122.6669 | 122.6028 | 0.086976 | 0.022889 | -0.068664 | 0 | -0.16937 | 4.6051 | 1.1353 | 0.56763 | 1.2039 | 0.63629 | 0.18311 | 0.013733 | 4.6738 | 122.7722 | 0.20142 | 122.9416 | 122.7814 | 122.8729 | -0.29297 | -122.9416 | 122.5937 | 122.7036 | 122.612 | 46.2524
2715.125 | 123.0286 | -122.6349 | 0.16937 | 0.0025177 | -0.01672 | -0.079651 | -0.0065517 | -0.031298 | -0.049313 | -0.042314 | 0.00094606 | -0.017758 | 0.060686 | 0.045194 | -0.22001 | -0.014496 | -0.021971 | -0.050354 | 0.086975 | -0.086975 | -0.018311 | 0.17395 | 0.013733 | 0.073242 | -76.442 | 0.12817 | -122.6944 | 0.12817 | -117.9062 | -122.0123 | -121.4127 | 122.5479 | -0.082398 | -0.18768 | 122.8088 | 122.7081 | 122.6486 | 0.16022 | 0.10071 | -0.059509 | -0.041199 | -0.041199 | 4.7287 | 1.2222 | 0.62256 | 1.2817 | 0.68207 | 0.26092 | 0.068664 | 4.7882 | 122.8226 | 0.17395 | 122.8226 | 122.7219 | 122.7631 | -0.25635 | -122.8638 | 122.6166 | 122.7631 | 122.5845 | 46.1929
2716.8594 | 123.0103 | -122.6212 | 0.13733 | 0.010147 | -0.013089 | -0.080719 | -0.010397 | -0.030016 | -0.04974 | -0.039537 | -0.0051575 | -0.020322 | 0.060472 | 0.045835 | -0.21894 | -0.013642 | -0.018553 | -0.07782 | 0.082397 | -0.091553 | -0.050354 | 0.10986 | -0.045776 | 0.036621 | -76.7029 | 0.15106 | -122.7036 | 0.12817 | -117.8421 | -122.0306 | -121.3989 | 122.5296 | -0.054932 | -0.18768 | 122.731 | 122.6578 | 122.5754 | 0.12817 | 0.045777 | -0.082397 | 0.013733 | -0.009155 | 4.7791 | 1.2222 | 0.59051 | 1.3046 | 0.67291 | 0.20142 | 0.041199 | 4.8615 | 122.8317 | 0.17395 | 122.8546 | 122.7036 | 122.7722 | -0.22888 | -122.8409 | 122.5708 | 122.7493 | 122.5433 | 45.9183
2718.6406 | 123.0011 | -122.6486 | 0.16479 | 0.0025177 | -0.010952 | -0.076874 | -0.0054837 | -0.030443 | -0.049954 | -0.044451 | 0.00094606 | -0.016477 | 0.061754 | 0.04733 | -0.22193 | -0.014283 | -0.023467 | -0.004578 | 0.082397 | -0.09613 | -0.018311 | 0.11444 | -0.059509 | 0.027466 | -76.8631 | 0.11902 | -122.6761 | 0.16022 | -117.7826 | -122.0306 | -121.4081 | 122.5525 | -0.082398 | -0.18311 | 122.7631 | 122.6761 | 122.5891 | 0.1236 | 0.036621 | -0.027465 | -0.045776 | -0.004578 | 4.866 | 1.2405 | 0.61798 | 1.268 | 0.64545 | 0.21057 | 0.077819 | 4.8935 | 122.8363 | 0.17853 | 122.7951 | 122.731 | 122.7676 | -0.26092 | -122.8409 | 122.6303 | 122.8088 | 122.644 | 45.7855
2720.3594 | 122.8775 | -122.7081 | 0.17853 | -0.0051118 | -0.015011 | -0.079224 | -0.0063381 | -0.033434 | -0.05209 | -0.040605 | -0.0021057 | -0.016049 | 0.064959 | 0.051176 | -0.22129 | -0.015565 | -0.017485 | -0.11444 | 0.09613 | -0.14191 | -0.13275 | 0.004578 | -0.15106 | -0.073242 | -77.1698 | 0.16022 | -122.7081 | 0 | -117.8055 | -122.1634 | -121.5408 | 122.5662 | -0.082398 | -0.31128 | 122.7127 | 122.6349 | 122.5571 | 0.068665 | -0.009155 | 0 | -0.018311 | -0.17853 | 4.9026 | 1.1673 | 0.54474 | 1.1673 | 0.54474 | 0.14649 | 0.009156 | 4.9026 | 122.7081 | 0.23804 | 122.8683 | 122.8043 | 122.8683 | -0.32044 | -122.8867 | 122.5754 | 122.7081 | 122.5937 | 45.5383
2722.1562 | 122.9965 | -122.6395 | 0.16479 | -0.0051118 | -0.016079 | -0.080506 | -0.0084743 | -0.034716 | -0.051235 | -0.041033 | 0.00094606 | -0.021604 | 0.060259 | 0.048612 | -0.22129 | -0.017273 | -0.020262 | -0.054932 | 0.10071 | -0.10986 | -0.004578 | 0.17853 | 0.013733 | 0.068665 | -77.037 | 0.13733 | -122.6944 | 0.14648 | -117.5812 | -121.9986 | -121.3806 | 122.5296 | -0.064087 | -0.16937 | 122.818 | 122.7081 | 122.6532 | 0.17853 | 0.1236 | -0.054932 | -0.027466 | -0.018311 | 5.0583 | 1.2588 | 0.64087 | 1.3138 | 0.6958 | 0.28839 | 0.10529 | 5.1132 | 122.8409 | 0.21057 | 122.8317 | 122.7402 | 122.7768 | -0.27466 | -122.8592 | 122.6349 | 122.7859 | 122.5845 | 45.6024
2723.8906 | 122.9141 | -122.6944 | 0.16479 | -0.012741 | -0.01138 | -0.078797 | -0.0052701 | -0.031725 | -0.049313 | -0.044023 | -0.0021057 | -0.013486 | 0.061968 | 0.052885 | -0.21958 | -0.013856 | -0.01898 | -0.1236 | 0.11902 | -0.15106 | -0.14191 | -0.018311 | -0.17395 | -0.091553 | -77.3346 | 0.14191 | -122.7402 | 0.059509 | -117.6086 | -122.1542 | -121.4676 | 122.5433 | -0.045776 | -0.3067 | 122.6761 | 122.6028 | 122.5204 | 0.059509 | -0.022888 | -0.045776 | -0.022888 | -0.10529 | 5.0858 | 1.2268 | 0.54016 | 1.2726 | 0.58594 | 0.13275 | 0.009155 | 5.1315 | 122.7997 | 0.27008 | 122.8821 | 122.8134 | 122.8363 | -0.31586 | -122.905 | 122.5525 | 122.7539 | 122.5708 | 45.3598
2725.6719 | 123.0011 | -122.6486 | 0.14191 | -0.012741 | -0.010525 | -0.078583 | -0.0048427 | -0.033861 | -0.050381 | -0.040178 | -0.0021057 | -0.018186 | 0.062181 | 0.050321 | -0.21915 | -0.013001 | -0.023039 | -0.036621 | 0.068665 | -0.07782 | -0.018311 | 0.11902 | -0.059509 | 0.027466 | -77.3758 | 0.13275 | -122.6944 | 0.15564 | -117.4072 | -122.0215 | -121.376 | 122.5708 | -0.073242 | -0.16022 | 122.7676 | 122.6761 | 122.5891 | 0.10529 | 0.018311 | -0.045776 | -0.009156 | 0.013733 | 5.2414 | 1.2726 | 0.62714 | 1.3184 | 0.67291 | 0.19684 | 0.059509 | 5.2872 | 122.85 | 0.14649 | 122.8271 | 122.7173 | 122.7814 | -0.21973 | -122.8363 | 122.6303 | 122.8043 | 122.612 | 45.2728
2727.4688 | 122.9507 | -122.6486 | 0.16479 | -0.0051118 | -0.012875 | -0.077515 | -0.0054837 | -0.034075 | -0.048031 | -0.041246 | -0.0082091 | -0.016904 | 0.063463 | 0.053312 | -0.21937 | -0.015565 | -0.019408 | -0.091553 | 0.09613 | -0.09613 | -0.07782 | 0.050354 | -0.09613 | -0.027466 | -77.6138 | 0.15106 | -122.7127 | 0.068665 | -117.3431 | -122.0581 | -121.4127 | 122.5525 | -0.068665 | -0.24261 | 122.699 | 122.6212 | 122.5525 | 0.068664 | 0 | -0.064087 | -0.013733 | -0.09613 | 5.3055 | 1.236 | 0.59052 | 1.3 | 0.6546 | 0.14648 | 0.01831 | 5.3696 | 122.7814 | 0.19226 | 122.8638 | 122.7448 | 122.7997 | -0.26092 | -122.8775 | 122.5708 | 122.7173 | 122.5571 | 45.0348
2729.25 | 122.905 | -122.6715 | 0.1831 | -0.0051118 | -0.0096707 | -0.077088 | -0.0035611 | -0.030871 | -0.050381 | -0.041887 | 0.0039979 | -0.013913 | 0.063036 | 0.052671 | -0.22257 | -0.012787 | -0.021117 | -0.068665 | 0.10071 | -0.12817 | -0.086975 | 0.045776 | -0.1236 | -0.041199 | -77.7374 | 0.16022 | -122.7173 | 0.073242 | -117.2745 | -122.1085 | -121.4264 | 122.5433 | -0.082397 | -0.27008 | 122.7173 | 122.6303 | 122.5479 | 0.086975 | 0.004578 | -0.045776 | -0.022888 | -0.10986 | 5.397 | 1.2451 | 0.56305 | 1.2909 | 0.60883 | 0.17395 | 0.041199 | 5.4428 | 122.7905 | 0.22888 | 122.8775 | 122.7722 | 122.8317 | -0.31128 | -122.9004 | 122.5845 | 122.7448 | 122.6028 | 44.9341
2730.9688 | 123.0057 | -122.6257 | 0.15106 | 0.0025177 | -0.015011 | -0.079011 | -0.0093289 | -0.028307 | -0.050381 | -0.041674 | -0.0021057 | -0.016904 | 0.061968 | 0.049894 | -0.22129 | -0.016205 | -0.018126 | -0.064087 | 0.068665 | -0.091553 | -0.036621 | 0.16022 | -0.018311 | 0.064087 | -77.9068 | 0.11444 | -122.7036 | 0.15106 | -117.0868 | -121.9574 | -121.3348 | 122.5342 | -0.082397 | -0.18768 | 122.7859 | 122.6898 | 122.6074 | 0.15564 | 0.073242 | -0.07782 | -0.036621 | 0 | 5.5389 | 1.2909 | 0.66833 | 1.3687 | 0.74616 | 0.25177 | 0.054932 | 5.6168 | 122.8546 | 0.16022 | 122.818 | 122.6944 | 122.7402 | -0.24261 | -122.8546 | 122.5891 | 122.7768 | 122.5616 | 44.7189
2732.7656 | 122.9004 | -122.6807 | 0.16479 | -0.012741 | -0.014584 | -0.081147 | -0.0069791 | -0.030443 | -0.051449 | -0.039965 | -0.0021057 | -0.01434 | 0.063463 | 0.052885 | -0.21958 | -0.014496 | -0.019194 | -0.059509 | 0.082397 | -0.1236 | -0.064087 | 0.091553 | -0.064087 | 0.009155 | -77.9892 | 0.16022 | -122.7356 | 0.054932 | -117.0868 | -122.0673 | -121.3989 | 122.5571 | -0.082398 | -0.22888 | 122.7722 | 122.6898 | 122.6166 | 0.13275 | 0.059509 | -0.054932 | -0.004578 | -0.10986 | 5.5939 | 1.2817 | 0.6134 | 1.3367 | 0.66833 | 0.21515 | 0.059509 | 5.6488 | 122.7905 | 0.20599 | 122.8958 | 122.7631 | 122.8409 | -0.28839 | -122.9004 | 122.6166 | 122.7356 | 122.6212 | 44.6915
2734.5469 | 122.9691 | -122.6532 | 0.17395 | -0.012741 | -0.011593 | -0.080292 | -0.0020657 | -0.03258 | -0.050808 | -0.041674 | 0.00094606 | -0.01434 | 0.064531 | 0.055448 | -0.21958 | -0.014069 | -0.01834 | -0.1236 | 0.09613 | -0.13275 | -0.14191 | 0.009155 | -0.17395 | -0.068665 | -78.3051 | 0.15564 | -122.7264 | 0.09613 | -116.9952 | -122.0764 | -121.3623 | 122.5204 | -0.07782 | -0.31586 | 122.6624 | 122.5845 | 122.4792 | 0.064086 | -0.041199 | -0.073242 | -0.01831 | -0.07782 | 5.658 | 1.2909 | 0.57678 | 1.3641 | 0.65002 | 0.14191 | -0.009156 | 5.7312 | 122.8226 | 0.22888 | 122.8821 | 122.7493 | 122.8088 | -0.3067 | -122.9004 | 122.5113 | 122.7493 | 122.5296 | 44.3481
2736.2656 | 123.0057 | -122.6349 | 0.13733 | -0.0051118 | -0.011593 | -0.079651 | -0.0048427 | -0.029162 | -0.048886 | -0.041246 | -0.0051575 | -0.016477 | 0.061113 | 0.055448 | -0.22001 | -0.013215 | -0.01834 | -0.045776 | 0.091553 | -0.10071 | -0.041199 | 0.10529 | -0.064087 | 0.004578 | -78.1586 | 0.1236 | -122.7127 | 0.15106 | -116.7618 | -121.994 | -121.2845 | 122.5342 | -0.045776 | -0.17853 | 122.7402 | 122.6395 | 122.5708 | 0.10529 | 0.036621 | -0.07782 | -0.013733 | 0.013733 | 5.8731 | 1.3504 | 0.64087 | 1.4282 | 0.71869 | 0.20599 | 0.059509 | 5.9509 | 122.8638 | 0.19226 | 122.8363 | 122.7264 | 122.7585 | -0.23804 | -122.85 | 122.5937 | 122.7859 | 122.5891 | 44.4763
2738.0625 | 122.9416 | -122.6532 | 0.17853 | 0.0025177 | -0.013516 | -0.08136 | -0.0063381 | -0.033861 | -0.050595 | -0.042101 | -0.0051575 | -0.01669 | 0.064959 | 0.055021 | -0.21979 | -0.013642 | -0.017699 | -0.041199 | 0.059509 | -0.09613 | -0.036621 | 0.12817 | -0.036621 | 0.018311 | -78.4973 | 0.13275 | -122.7081 | 0.086975 | -116.7343 | -122.0078 | -121.3531 | 122.5571 | -0.11902 | -0.21515 | 122.7814 | 122.6715 | 122.6166 | 0.11444 | 0.059509 | -0.054932 | -0.045777 | -0.091553 | 5.9189 | 1.3 | 0.64545 | 1.355 | 0.70038 | 0.2243 | 0.059509 | 5.9738 | 122.7951 | 0.15564 | 122.8409 | 122.7127 | 122.7859 | -0.27466 | -122.8867 | 122.6166 | 122.7402 | 122.612 | 44.1559
2739.8438 | 122.8867 | -122.6944 | 0.19226 | -0.0051118 | -0.015011 | -0.079865 | -0.0052701 | -0.030016 | -0.04974 | -0.039537 | -0.0051575 | -0.016049 | 0.06325 | 0.053312 | -0.22043 | -0.01471 | -0.017699 | -0.12817 | 0.1236 | -0.13733 | -0.16937 | -0.018311 | -0.15106 | -0.07782 | -78.8086 | 0.17395 | -122.7402 | 0.027466 | -116.6885 | -122.0718 | -121.3852 | 122.5571 | -0.068665 | -0.36163 | 122.6761 | 122.6166 | 122.5433 | 0.059509 | -0.013733 | -0.045776 | -0.018311 | -0.16479 | 6.0059 | 1.3092 | 0.62256 | 1.355 | 0.66833 | 0.11902 | -0.032044 | 6.0516 | 122.7676 | 0.26093 | 122.9141 | 122.818 | 122.8683 | -0.32959 | -122.9324 | 122.525 | 122.7219 | 122.5662 | 43.8858
2741.5781 | 122.8683 | -122.6898 | 0.1831 | -0.0051118 | -0.016079 | -0.079224 | -0.0078335 | -0.027666 | -0.050595 | -0.042742 | -0.0021057 | -0.01669 | 0.063463 | 0.052671 | -0.21872 | -0.015992 | -0.017485 | -0.086975 | 0.091553 | -0.11444 | -0.10986 | 0.045776 | -0.10071 | -0.045776 | -79.01 | 0.17853 | -122.7127 | 0.013733 | -116.6016 | -122.0398 | -121.3898 | 122.5754 | -0.091552 | -0.29297 | 122.7356 | 122.644 | 122.5891 | 0.068665 | 0.013733 | -0.022889 | -0.004577 | -0.16937 | 6.0883 | 1.3 | 0.65002 | 1.3229 | 0.67291 | 0.16022 | 0.004578 | 6.1111 | 122.7264 | 0.20599 | 122.8912 | 122.7814 | 122.8683 | -0.29755 | -122.8958 | 122.58 | 122.7036 | 122.6028 | 43.6798
2743.375 | 122.9416 | -122.6303 | 0.16022 | 0.0025177 | -0.01202 | -0.079011 | -0.0059109 | -0.029802 | -0.048245 | -0.041887 | -0.0021057 | -0.01904 | 0.063036 | 0.043272 | -0.22001 | -0.015137 | -0.016844 | -0.09613 | 0.086975 | -0.11444 | -0.082397 | 0.068665 | -0.09613 | 0 | -79.1153 | 0.13733 | -122.7219 | 0.07782 | -116.4047 | -121.9803 | -121.312 | 122.5159 | -0.073242 | -0.24261 | 122.699 | 122.6303 | 122.5342 | 0.11444 | 0.018311 | -0.091553 | -0.022888 | -0.082397 | 6.2256 | 1.3184 | 0.65002 | 1.4099 | 0.74158 | 0.18311 | 0.032044 | 6.3171 | 122.7997 | 0.20142 | 122.8592 | 122.7173 | 122.7676 | -0.27466 | -122.8821 | 122.5479 | 122.7081 | 122.5342 | 43.515
2745.0938 | 122.905 | -122.6807 | 0.21515 | -0.0051118 | -0.013516 | -0.079011 | -0.0048427 | -0.030657 | -0.051449 | -0.040178 | 0.00094606 | -0.015622 | 0.063463 | 0.056303 | -0.21937 | -0.013428 | -0.019835 | -0.10529 | 0.11902 | -0.13275 | -0.14191 | -0.022888 | -0.13733 | -0.073242 | -79.303 | 0.17395 | -122.7081 | 0.027466 | -116.3361 | -122.0032 | -121.3074 | 122.5479 | -0.09613 | -0.35706 | 122.6578 | 122.6074 | 122.5433 | 0.059509 | -0.004578 | -0.027466 | -0.041199 | -0.18768 | 6.3446 | 1.3733 | 0.67749 | 1.4008 | 0.70496 | 0.10986 | -0.009156 | 6.3721 | 122.7356 | 0.25177 | 122.8821 | 122.7997 | 122.8546 | -0.3479 | -122.9233 | 122.5388 | 122.7081 | 122.5754 | 43.3777
2746.8906 | 122.8867 | -122.6669 | 0.19226 | 0.0025177 | -0.010739 | -0.079224 | -0.0033475 | -0.027666 | -0.050381 | -0.041246 | -0.0021057 | -0.015195 | 0.065813 | 0.052671 | -0.21937 | -0.014283 | -0.017271 | -0.1236 | 0.13275 | -0.12817 | -0.15564 | -0.036621 | -0.18768 | -0.10071 | -79.3854 | 0.17395 | -122.7264 | 0.027466 | -116.3132 | -122.0627 | -121.344 | 122.5388 | -0.05951 | -0.3479 | 122.6303 | 122.5662 | 122.4792 | 0.027466 | -0.059509 | -0.059509 | -0.018311 | -0.16479 | 6.3538 | 1.3229 | 0.60425 | 1.3824 | 0.66376 | 0.091553 | -0.027466 | 6.4133 | 122.7539 | 0.26093 | 122.9004 | 122.7997 | 122.8409 | -0.32044 | -122.9187 | 122.5113 | 122.6944 | 122.5433 | 43.2816
2748.6719 | 122.9233 | -122.6028 | 0.11902 | 0.0025177 | -0.011166 | -0.077729 | -0.0067653 | -0.030657 | -0.049313 | -0.041246 | 0.0039979 | -0.023954 | 0.0087756 | -0.02701 | -0.22172 | -0.017701 | -0.024962 | -0.059509 | 0.068665 | -0.07782 | -0.045776 | 0.13733 | -0.07782 | 0.022888 | -0.52185 | 0.12817 | -0.46234 | 0.10529 | -0.25635 | -0.21973 | -0.15564 | 122.525 | -0.050354 | -0.16479 | 122.7402 | 122.6257 | 122.525 | 0.10071 | 0 | 122.1405 | 0.009155 | -0.013733 | 122.3465 | 122.4472 | 122.3831 | 0.3067 | 0.24261 | 0.21515 | 0.032044 | 0.20599 | 0.56763 | 0.14649 | 0.59052 | 122.6715 | 122.731 | -0.19684 | -0.58136 | 122.5571 | 122.7081 | 122.5433 | 122.081
2750.4688 | 122.8546 | -122.7036 | 0.15564 | -0.02037 | -0.013302 | -0.080292 | -0.0050565 | -0.029589 | -0.049313 | -0.043169 | -0.0021057 | -0.018399 | 0.0064258 | -0.019961 | -0.21937 | -0.016419 | -0.022612 | -0.13275 | 0.11902 | -0.15106 | -0.15564 | -0.018311 | -0.15564 | -0.068665 | -0.64087 | 0.18768 | -0.41657 | -0.022888 | -0.25635 | -0.2243 | -0.1831 | 122.5525 | -0.036621 | -0.31128 | 122.6852 | 122.6349 | 122.5479 | 0.082397 | -0.004578 | 122.287 | 0.032043 | -0.17853 | 122.4472 | 122.5204 | 122.4792 | 0.23346 | 0.19226 | 0.13275 | -0.004578 | 0.16022 | 0.39368 | 0.27008 | 0.60425 | 122.8226 | 122.8912 | -0.3067 | -0.57221 | 122.5479 | 122.6807 | 122.5708 | 122.0627
2752.1875 | 123.0103 | -122.6486 | 0.10529 | -0.0051118 | -0.017361 | -0.083283 | -0.0067653 | -0.030016 | -0.050381 | -0.043169 | 0.00094606 | -0.019681 | 0.0081348 | -0.021456 | -0.22172 | -0.020051 | -0.02838 | -0.059509 | 0.068665 | -0.091553 | -0.009155 | 0.17853 | 0.004578 | 0.064087 | -0.5127 | 0.10529 | -0.43945 | 0.09613 | -0.15106 | -0.11902 | -0.10986 | 122.5571 | -0.036621 | -0.11444 | 122.8271 | 122.7127 | 122.6532 | 0.15564 | 0.096131 | 122.2092 | 0 | -0.009156 | 122.4976 | 122.5388 | 122.5296 | 0.32959 | 0.32043 | 0.27008 | 0.082398 | 0.28839 | 0.53558 | 0.16022 | 0.54474 | 122.7173 | 122.7539 | -0.19684 | -0.54474 | 122.6395 | 122.7448 | 122.5891 | 122.1359
2753.9844 | 122.9553 | -122.6669 | 0.11902 | -0.012741 | -0.011807 | -0.077942 | -0.0069791 | -0.028734 | -0.051449 | -0.043383 | 0.00094606 | -0.020963 | 0.0064258 | -0.019961 | -0.22172 | -0.01706 | -0.024535 | -0.050354 | 0.059509 | -0.082397 | -0.041199 | 0.12817 | -0.073242 | 0.018311 | -0.53101 | 0.11444 | -0.45319 | 0.10529 | -0.21515 | -0.20142 | -0.14648 | 122.5845 | -0.05951 | -0.16022 | 122.7951 | 122.6852 | 122.5937 | 0.10071 | 0.009155 | 122.2137 | -0.004578 | -0.013733 | 122.4518 | 122.5204 | 122.4655 | 0.3067 | 0.25177 | 0.21057 | 0.041198 | 0.23804 | 0.55847 | 0.14191 | 0.56763 | 122.7264 | 122.7814 | -0.20142 | -0.5722 | 122.6257 | 122.7722 | 122.6166 | 122.1359
2755.7656 | 122.8775 | -122.7036 | 0.14191 | -0.0051118 | -0.013943 | -0.081574 | -0.0046291 | -0.03023 | -0.05209 | -0.042101 | 0.00094606 | -0.018186 | 0.0092028 | -0.022952 | -0.22065 | -0.017701 | -0.020689 | -0.13733 | 0.11444 | -0.14191 | -0.15564 | -0.036621 | -0.14648 | -0.068665 | -0.65002 | 0.16022 | -0.42114 | -0.013733 | -0.2243 | -0.22888 | -0.1831 | 122.5616 | -0.027466 | -0.29755 | 122.6669 | 122.6349 | 122.5571 | 0.073242 | -0.004577 | 122.2824 | 0.01831 | -0.15564 | 122.4792 | 122.5204 | 122.4747 | 0.23804 | 0.19226 | 0.10529 | -0.013733 | 0.19684 | 0.40741 | 0.25635 | 0.58136 | 122.818 | 122.8638 | -0.28381 | -0.56305 | 122.5479 | 122.6898 | 122.5662 | 122.0535
2757.5 | 122.9599 | -122.6944 | 0.13733 | 0.0025177 | -0.013516 | -0.079865 | -0.0074063 | -0.032152 | -0.05209 | -0.040392 | 0.00094606 | -0.01904 | 0.0070666 | -0.021456 | -0.21958 | -0.017914 | -0.020262 | -0.10529 | 0.091553 | -0.10986 | -0.086975 | 0.059509 | -0.10529 | -0.032043 | -0.55389 | 0.1236 | -0.36163 | 0.050354 | -0.15106 | -0.11444 | -0.07782 | 122.5845 | -0.045776 | -0.2243 | 122.7539 | 122.6624 | 122.5891 | 0.07782 | 0.004577 | 122.3328 | -0.013733 | -0.086975 | 122.5433 | 122.6166 | 122.58 | 0.28381 | 0.24719 | 0.16937 | 0.022888 | 0.21057 | 0.41199 | 0.20142 | 0.48523 | 122.7859 | 122.818 | -0.24719 | -0.49896 | 122.6074 | 122.7448 | 122.5891 | 122.1405
2759.2812 | 122.8821 | -122.7402 | 0.13275 | -0.0051118 | -0.013089 | -0.079438 | -0.0056973 | -0.034289 | -0.050381 | -0.04146 | 0.00094606 | -0.019467 | 0.0072802 | -0.015048 | -0.21915 | -0.020051 | -0.022185 | -0.13733 | 0.1236 | -0.13275 | -0.15106 | -0.009155 | -0.13275 | -0.082397 | -0.64545 | 0.17853 | -0.44403 | -0.036621 | -0.27924 | -0.26093 | -0.21973 | 122.6074 | -0.009155 | -0.28381 | 122.731 | 122.6578 | 122.6074 | 0.050354 | 0 | 122.2961 | 0.045777 | -0.16937 | 122.4609 | 122.5204 | 122.4792 | 0.2243 | 0.18311 | 0.1236 | -0.018311 | 0.1648 | 0.40741 | 0.25635 | 0.62256 | 122.8638 | 122.9187 | -0.2655 | -0.57678 | 122.5891 | 122.7036 | 122.6028 | 122.0947
2761 | 122.9782 | -122.6807 | 0.10986 | 0.0025177 | -0.013943 | -0.080506 | -0.0076199 | -0.028948 | -0.049526 | -0.042101 | -0.0021057 | -0.020536 | 0.0098438 | -0.021029 | -0.21851 | -0.017701 | -0.02603 | -0.10529 | 0.073242 | -0.09613 | -0.09613 | 0.073242 | -0.091553 | -0.004578 | -0.50354 | 0.10986 | -0.32959 | 0.059509 | -0.10986 | -0.086975 | -0.050354 | 122.5845 | -0.036621 | -0.20599 | 122.7539 | 122.6761 | 122.5891 | 0.091552 | 0.004577 | 122.3511 | 0 | -0.050354 | 122.5708 | 122.6303 | 122.5937 | 0.27924 | 0.24261 | 0.16937 | 0 | 0.21973 | 0.3891 | 0.16937 | 0.43945 | 122.7539 | 122.7905 | -0.20599 | -0.43945 | 122.5845 | 122.7402 | 122.5754 | 122.1771
2762.7969 | 122.8867 | -122.7356 | 0.15564 | 0.0025177 | -0.014798 | -0.079224 | -0.0044155 | -0.032152 | -0.051663 | -0.041674 | -0.0021057 | -0.018827 | 0.010057 | -0.01697 | -0.22086 | -0.017487 | -0.020903 | -0.13733 | 0.11902 | -0.16479 | -0.16479 | -0.009155 | -0.15106 | -0.07782 | -0.58136 | 0.16022 | -0.35706 | -0.018311 | -0.21973 | -0.19684 | -0.14191 | 122.5708 | -0.036621 | -0.32044 | 122.7264 | 122.6578 | 122.5845 | 0.086975 | 0.013733 | 122.3785 | 0.004577 | -0.17395 | 122.5159 | 122.5937 | 122.5388 | 0.21515 | 0.16022 | 0.15564 | 0 | 0.13733 | 0.33874 | 0.28381 | 0.51727 | 122.8546 | 122.8958 | -0.32044 | -0.5127 | 122.5708 | 122.7173 | 122.5983 | 122.1542
2764.5156 | 122.8775 | -122.7631 | 0.15564 | 0.0025177 | -0.015866 | -0.079651 | -0.0069791 | -0.029802 | -0.053372 | -0.041246 | -0.0021057 | -0.020108 | 0.0083484 | -0.017184 | -0.2215 | -0.019196 | -0.025816 | -0.10529 | 0.086975 | -0.13275 | -0.13733 | 0.013733 | -0.14191 | -0.054932 | -0.63171 | 0.16479 | -0.43488 | -0.009155 | -0.25635 | -0.26093 | -0.21973 | 122.6303 | -0.068665 | -0.29297 | 122.7768 | 122.7081 | 122.6212 | 0.077819 | -0.009156 | 122.3282 | 0.009155 | -0.16479 | 122.5067 | 122.5433 | 122.5021 | 0.21515 | 0.17395 | 0.14648 | -0.004578 | 0.17853 | 0.42572 | 0.21973 | 0.59967 | 122.85 | 122.9279 | -0.28839 | -0.59052 | 122.6257 | 122.7539 | 122.6578 | 122.1313
2766.3125 | 122.9279 | -122.7493 | 0.13733 | 0.0025177 | -0.013729 | -0.080079 | -0.0059109 | -0.032793 | -0.053158 | -0.041246 | 0.00094606 | -0.020108 | 0.0094166 | -0.019106 | -0.21894 | -0.017914 | -0.021544 | -0.13733 | 0.11902 | -0.14648 | -0.16022 | -0.022888 | -0.15106 | -0.082397 | -0.63629 | 0.17853 | -0.43488 | -0.009155 | -0.26093 | -0.2655 | -0.20142 | 122.6028 | -0.01831 | -0.29755 | 122.7264 | 122.6669 | 122.5983 | 0.064087 | -0.004578 | 122.3145 | 0.041199 | -0.14648 | 122.4884 | 122.5479 | 122.4838 | 0.23346 | 0.16937 | 0.1236 | -0.013733 | 0.17395 | 0.42572 | 0.2655 | 0.6134 | 122.8683 | 122.9279 | -0.28381 | -0.5722 | 122.5891 | 122.7402 | 122.612 | 122.113
2768.1094 | 122.9462 | -122.7539 | 0.14191 | -0.0051118 | -0.013089 | -0.080933 | -0.0074063 | -0.031298 | -0.052731 | -0.037187 | 0.0039979 | -0.017758 | 0.0072802 | -0.019747 | -0.21723 | -0.016633 | -0.025603 | -0.11444 | 0.11902 | -0.14191 | -0.13733 | 0 | -0.1236 | -0.059509 | -0.61798 | 0.14648 | -0.4303 | 0.018311 | -0.23804 | -0.23804 | -0.19684 | 122.612 | -0.022888 | -0.27924 | 122.7539 | 122.6944 | 122.6303 | 0.082398 | 0.018311 | 122.3236 | 0.004577 | -0.1236 | 122.5159 | 122.5571 | 122.5159 | 0.23346 | 0.19226 | 0.14191 | 0.004578 | 0.19226 | 0.44861 | 0.26093 | 0.57678 | 122.8729 | 122.9004 | -0.28381 | -0.57221 | 122.6166 | 122.7722 | 122.6395 | 122.1359
2769.8281 | 122.9736 | -122.7219 | 0.15106 | -0.0051118 | -0.013302 | -0.080292 | -0.0080471 | -0.028093 | -0.052517 | -0.042742 | 0.00094606 | -0.022031 | 0.0092028 | -0.024447 | -0.22043 | -0.018128 | -0.022612 | -0.045776 | 0.064087 | -0.09613 | -0.036621 | 0.1236 | -0.036621 | 0.022888 | -0.50354 | 0.11902 | -0.40283 | 0.059509 | -0.17395 | -0.17395 | -0.12817 | 122.6257 | -0.086975 | -0.18768 | 122.8455 | 122.7448 | 122.6852 | 0.11902 | 0.059509 | 122.319 | -0.032043 | -0.091553 | 122.5479 | 122.5937 | 122.5479 | 0.27466 | 0.22888 | 0.21973 | 0.059509 | 0.22888 | 0.46234 | 0.16022 | 0.52185 | 122.7859 | 122.8409 | -0.24719 | -0.55389 | 122.6852 | 122.7814 | 122.6761 | 122.2183
2771.625 | 122.8867 | -122.7448 | 0.14648 | -0.0051118 | -0.013516 | -0.080933 | -0.0074063 | -0.028521 | -0.052944 | -0.040819 | -0.0021057 | -0.019467 | 0.007494 | -0.025942 | -0.21979 | -0.017487 | -0.02368 | -0.12817 | 0.1236 | -0.15106 | -0.15106 | -0.018311 | -0.15106 | -0.068665 | -0.6134 | 0.16022 | -0.43945 | -0.018311 | -0.27008 | -0.27924 | -0.22888 | 122.5937 | -0.022888 | -0.29755 | 122.7264 | 122.6761 | 122.5937 | 0.082397 | 0 | 122.3053 | 0.013733 | -0.16479 | 122.4747 | 122.5159 | 122.4655 | 0.21057 | 0.16022 | 0.13275 | 0 | 0.16937 | 0.42114 | 0.27466 | 0.59967 | 122.8683 | 122.905 | -0.29755 | -0.58594 | 122.5937 | 122.7264 | 122.6166 | 122.1313
2773.4219 | 122.8958 | -122.7493 | 0.13275 | 0.0025177 | -0.011166 | -0.079224 | -0.0052701 | -0.028948 | -0.051876 | -0.039324 | -0.0051575 | -0.019895 | 0.0072802 | -0.019534 | -0.21872 | -0.015992 | -0.02368 | -0.091553 | 0.11444 | -0.13733 | -0.10986 | 0.018311 | -0.16022 | -0.082397 | -0.5722 | 0.16022 | -0.41199 | 0.004578 | -0.28839 | -0.29297 | -0.21057 | 122.612 | -0.01831 | -0.24261 | 122.7676 | 122.6669 | 122.5891 | 0.054932 | -0.022888 | 122.3373 | 0.027466 | -0.12817 | 122.4609 | 122.5388 | 122.4564 | 0.20142 | 0.11902 | 0.15564 | 0.027466 | 0.1236 | 0.41657 | 0.25177 | 0.5722 | 122.8638 | 122.9095 | -0.27008 | -0.54474 | 122.6395 | 122.7539 | 122.6578 | 122.1771
2775.125 | 123.0103 | -122.731 | 0.11444 | 0.0025177 | -0.010739 | -0.080292 | -0.0074063 | -0.029589 | -0.051876 | -0.040178 | -0.0051575 | -0.021604 | 0.0066394 | -0.022097 | -0.2183 | -0.017273 | -0.021544 | -0.10529 | 0.07782 | -0.11902 | -0.09613 | 0.064087 | -0.068665 | -0.013733 | -0.50812 | 0.11444 | -0.40741 | 0.073242 | -0.16022 | -0.16479 | -0.11444 | 122.612 | -0.036621 | -0.21057 | 122.7951 | 122.7173 | 122.6624 | 0.10529 | 0.050354 | 122.3236 | 0 | -0.041199 | 122.5708 | 122.6166 | 122.5662 | 0.29297 | 0.24261 | 0.18311 | 0.022889 | 0.24719 | 0.48065 | 0.19684 | 0.52185 | 122.8088 | 122.8455 | -0.23346 | -0.52185 | 122.6349 | 122.8043 | 122.6257 | 122.2229
2776.9219 | 123.0194 | -122.699 | 0.10529 | -0.0051118 | -0.010311 | -0.076447 | -0.0071927 | -0.032366 | -0.049313 | -0.039751 | -0.0051575 | -0.020536 | 0.0092028 | -0.016757 | -0.21808 | -0.015992 | -0.02368 | -0.027466 | 0.064087 | -0.09613 | -0.018311 | 0.12817 | -0.059509 | 0.027466 | -0.41657 | 0.10071 | -0.40741 | 0.11444 | -0.15106 | -0.14191 | -0.059509 | 122.6028 | -0.041199 | -0.1236 | 122.8271 | 122.7264 | 122.6395 | 0.1236 | 0.036621 | 122.2916 | -0.004578 | 0.009155 | 122.5479 | 122.6395 | 122.5571 | 0.3479 | 0.2655 | 0.2243 | 0.077819 | 0.25635 | 0.52185 | 0.16022 | 0.50812 | 122.7631 | 122.7997 | -0.20142 | -0.5127 | 122.6807 | 122.8134 | 122.6715 | 122.2824
2778.7031 | 122.9416 | -122.7173 | 0.12817 | -0.012741 | -0.012448 | -0.080079 | -0.0039883 | -0.029802 | -0.050167 | -0.039965 | 0.00094606 | -0.018399 | 0.010057 | -0.023379 | -0.21808 | -0.015992 | -0.021971 | -0.11444 | 0.11902 | -0.15564 | -0.13275 | -0.004578 | -0.17853 | -0.073242 | -0.53101 | 0.13733 | -0.42572 | 0.050354 | -0.24719 | -0.24261 | -0.17395 | 122.5616 | -0.009155 | -0.26093 | 122.7127 | 122.644 | 122.5388 | 0.082398 | -0.022888 | 122.2916 | 0.009155 | -0.07782 | 122.4701 | 122.5433 | 122.4747 | 0.25177 | 0.1831 | 0.15106 | 0.022889 | 0.17853 | 0.47607 | 0.27466 | 0.56305 | 122.8363 | 122.8546 | -0.28381 | -0.55389 | 122.5845 | 122.7676 | 122.6028 | 122.1863
2780.4844 | 122.612 | -122.3831 | 0.1236 | 0.010147 | -0.010525 | -0.080933 | -0.0059109 | -0.029375 | -0.051449 | -0.041246 | -0.0021057 | -0.018827 | 0.0089892 | -0.016329 | -0.22001 | -0.01471 | -0.022398 | -0.068665 | 0.11444 | -0.11444 | -0.09613 | 0.064087 | -0.10071 | -0.045776 | -0.46692 | 0.16022 | -0.41199 | 0.050354 | -0.21057 | -0.21057 | -0.15564 | 122.2687 | -0.009155 | -0.21973 | 122.4472 | 122.3373 | 122.2824 | 0.068665 | 0.013733 | 121.9711 | 0.036621 | -0.073242 | 122.1725 | 122.2275 | 122.1725 | 0.25635 | 0.20142 | 0.17853 | 0.018311 | 0.20142 | 0.46234 | 0.22888 | 0.5722 | 122.4976 | 122.5433 | -0.23804 | -0.53558 | 122.287 | 122.4335 | 122.3145 | 121.9162
2782.25 | 122.8134 | -122.4655 | 0.10071 | 0.0025177 | -0.011166 | -0.077942 | -0.0033475 | -0.030871 | -0.051235 | -0.040819 | -0.0051575 | -0.021604 | 0.0092028 | -0.019747 | -0.21937 | -0.016633 | -0.024107 | -0.082397 | 0.086975 | -0.11902 | -0.050354 | 0.09613 | -0.07782 | 0 | -0.41657 | 0.10986 | -0.40283 | 0.10986 | -0.16479 | -0.16022 | -0.068665 | 122.3465 | -0.013733 | -0.15106 | 122.5616 | 122.4655 | 122.3877 | 0.11902 | 0.041199 | 122.0627 | 0.009155 | 0.009155 | 122.3007 | 122.3969 | 122.3053 | 0.33417 | 0.24262 | 0.21515 | 0.068665 | 0.23804 | 0.5127 | 0.20599 | 0.5127 | 122.5525 | 122.5754 | -0.21973 | -0.50354 | 122.4152 | 122.5754 | 122.3831 | 122.0489
2784.0469 | 122.7951 | -122.5204 | 0.11444 | -0.0051118 | -0.013943 | -0.077729 | -0.0074063 | -0.031511 | -0.049526 | -0.040392 | -0.0021057 | -0.02139 | 0.0081348 | -0.021884 | -0.21787 | -0.016205 | -0.021971 | -0.036621 | 0.091553 | -0.10071 | -0.027466 | 0.14648 | -0.018311 | 0.045776 | -0.39368 | 0.13733 | -0.38452 | 0.09613 | -0.13275 | -0.13275 | -0.10071 | 122.4197 | -0.022888 | -0.14191 | 122.6669 | 122.5662 | 122.5021 | 0.14648 | 0.082397 | 122.1359 | 0.022888 | -0.018311 | 122.3877 | 122.4197 | 122.3877 | 0.28381 | 0.25177 | 0.24719 | 0.073242 | 0.25177 | 0.48065 | 0.19226 | 0.52185 | 122.612 | 122.6578 | -0.21515 | -0.49896 | 122.493 | 122.6166 | 122.4838 | 122.1268
2785.8281 | 122.8134 | -122.5342 | 0.09613 | -0.0051118 | -0.012448 | -0.080506 | -0.0069791 | -0.029162 | -0.051022 | -0.042314 | -0.0051575 | -0.022885 | 0.0098438 | -0.018893 | -0.21851 | -0.018128 | -0.020476 | -0.059509 | 0.073242 | -0.082397 | -0.018311 | 0.13275 | -0.064087 | 0.022888 | -0.38452 | 0.10986 | -0.39825 | 0.09613 | -0.17853 | -0.16022 | -0.10986 | 122.4518 | -0.022888 | -0.11444 | 122.6669 | 122.5571 | 122.4701 | 0.10528 | 0.01831 | 122.1359 | 0.013733 | 0 | 122.3557 | 122.4243 | 122.374 | 0.28839 | 0.23804 | 0.21515 | 0.064086 | 0.21973 | 0.49438 | 0.15564 | 0.50812 | 122.6074 | 122.644 | -0.17853 | -0.49438 | 122.5159 | 122.6303 | 122.4747 | 122.1497
2787.5469 | 122.8912 | -122.5525 | 0.086975 | 0.0025177 | -0.014798 | -0.078797 | -0.0089017 | -0.034075 | -0.051022 | -0.043383 | -0.0021057 | -0.022458 | 0.007494 | -0.020175 | -0.22043 | -0.01941 | -0.025603 | -0.064087 | 0.07782 | -0.091553 | -0.022888 | 0.16022 | -0.009155 | 0.059509 | -0.35248 | 0.10529 | -0.39825 | 0.1236 | -0.10529 | -0.082397 | -0.073242 | 122.4609 | -0.009155 | -0.10986 | 122.7127 | 122.612 | 122.5433 | 0.15106 | 0.082398 | 122.1542 | 0.018311 | 0.036621 | 122.4472 | 122.4792 | 122.4701 | 0.32501 | 0.31586 | 0.25177 | 0.068665 | 0.29297 | 0.52185 | 0.16937 | 0.50354 | 122.6303 | 122.6578 | -0.17853 | -0.48523 | 122.5296 | 122.6761 | 122.4884 | 122.2
2789.3438 | 122.8638 | -122.5662 | 0.1236 | 0.0025177 | -0.015866 | -0.07837 | -0.0097561 | -0.028093 | -0.050808 | -0.039537 | -0.0021057 | -0.02139 | 0.005144 | -0.02402 | -0.22107 | -0.017701 | -0.023467 | -0.10529 | 0.091553 | -0.10071 | -0.07782 | 0.082397 | -0.054932 | 0.018311 | -0.40741 | 0.11444 | -0.3891 | 0.082397 | -0.15106 | -0.12817 | -0.10071 | 122.4655 | -0.032043 | -0.20142 | 122.6486 | 122.5845 | 122.5113 | 0.11902 | 0.045776 | 122.1771 | -0.009155 | -0.041199 | 122.4152 | 122.4655 | 122.438 | 0.28839 | 0.26092 | 0.18311 | 0.022888 | 0.23804 | 0.4715 | 0.19226 | 0.50354 | 122.6578 | 122.6807 | -0.2243 | -0.5127 | 122.4884 | 122.6486 | 122.4609 | 122.1588
2791.125 | 122.8729 | -122.58 | 0.10529 | -0.0051118 | -0.014798 | -0.077729 | -0.0069791 | -0.034716 | -0.050808 | -0.042742 | -0.0021057 | -0.020108 | 0.0053576 | -0.019961 | -0.22022 | -0.019196 | -0.025816 | -0.086975 | 0.07782 | -0.10529 | -0.064087 | 0.073242 | -0.059509 | 0.009155 | -0.41657 | 0.1236 | -0.40283 | 0.09613 | -0.15106 | -0.14648 | -0.10986 | 122.4747 | -0.027466 | -0.16937 | 122.6532 | 122.5891 | 122.5204 | 0.11444 | 0.045777 | 122.1771 | 0.01831 | -0.009156 | 122.4289 | 122.4701 | 122.4335 | 0.29297 | 0.25635 | 0.17853 | 0.041199 | 0.25177 | 0.49896 | 0.18311 | 0.52643 | 122.6578 | 122.7036 | -0.21057 | -0.50812 | 122.5159 | 122.6761 | 122.493 | 122.1634
2792.8594 | 122.8867 | -122.58 | 0.11444 | -0.0051118 | -0.010739 | -0.079651 | -0.0067653 | -0.031298 | -0.049313 | -0.041033 | -0.0021057 | -0.022885 | 0.0064258 | -0.024874 | -0.21958 | -0.018128 | -0.018126 | -0.050354 | 0.050354 | -0.091553 | -0.022888 | 0.12817 | -0.064087 | 0.009155 | -0.35706 | 0.1236 | -0.40283 | 0.12817 | -0.15564 | -0.16937 | -0.10986 | 122.4884 | -0.064087 | -0.13733 | 122.7081 | 122.5891 | 122.5159 | 0.10071 | 0.027466 | 122.1771 | 0.009155 | 0.013733 | 122.4243 | 122.4701 | 122.4106 | 0.29297 | 0.23346 | 0.21973 | 0.068665 | 0.24719 | 0.53101 | 0.14191 | 0.52643 | 122.6303 | 122.7036 | -0.20599 | -0.51727 | 122.5571 | 122.7081 | 122.5296 | 122.2229
2794.6406 | 122.7402 | -122.6212 | 0.14191 | -0.0051118 | -0.010952 | -0.078797 | -0.0035611 | -0.028307 | -0.050595 | -0.042528 | 0.00094606 | -0.018186 | 0.0081348 | -0.014193 | -0.21894 | -0.016846 | -0.026244 | -0.11444 | 0.10529 | -0.14648 | -0.16022 | -0.054932 | -0.19684 | -0.10071 | -0.54016 | 0.16022 | -0.4303 | -0.009155 | -0.30212 | -0.3067 | -0.20142 | 122.4747 | -0.036621 | -0.30212 | 122.5662 | 122.5204 | 122.4243 | 0.045776 | -0.050354 | 122.1909 | 0.01831 | -0.15106 | 122.319 | 122.4197 | 122.3145 | 0.22888 | 0.1236 | 0.091552 | -0.013733 | 0.12817 | 0.42114 | 0.25177 | 0.59052 | 122.7264 | 122.7814 | -0.28839 | -0.57221 | 122.4609 | 122.612 | 122.5067 | 122.081
2796.3594 | 122.0627 | -121.9254 | 0.14191 | 0.0025177 | -0.0096707 | -0.079438 | -0.0037747 | -0.029162 | -0.052944 | -0.040605 | -0.0021057 | -0.018399 | 0.0098438 | -0.019534 | -0.21872 | -0.015137 | -0.020476 | -0.12817 | 0.12817 | -0.12817 | -0.16479 | -0.036621 | -0.19684 | -0.10529 | -0.52643 | 0.15106 | -0.42572 | -0.013733 | -0.29297 | -0.32044 | -0.21515 | 121.7972 | -0.013733 | -0.3067 | 121.8887 | 121.8201 | 121.7285 | 0.022888 | -0.068664 | 121.4996 | 0.009155 | -0.15564 | 121.6324 | 121.7102 | 121.6049 | 0.21057 | 0.10528 | 0.091553 | -0.036621 | 0.13275 | 0.41199 | 0.25635 | 0.57678 | 122.0535 | 122.0764 | -0.27008 | -0.56763 | 121.7606 | 121.9116 | 121.7972 | 121.3989
2798.1406 | 122.3419 | -122.0764 | 0.11902 | 0.0025177 | -0.013943 | -0.079011 | -0.0080471 | -0.030657 | -0.04974 | -0.042314 | 0.00094606 | -0.020322 | 0.0083484 | -0.019747 | -0.21915 | -0.018555 | -0.023039 | -0.086975 | 0.082397 | -0.07782 | -0.068665 | 0.07782 | -0.09613 | 0 | -0.41657 | 0.11902 | -0.40283 | 0.059509 | -0.1831 | -0.17853 | -0.13733 | 121.9986 | -0.036622 | -0.18768 | 122.1542 | 122.0764 | 121.9803 | 0.07782 | -0.01831 | 121.6736 | 0 | -0.05951 | 121.8933 | 121.9391 | 121.8979 | 0.2655 | 0.2243 | 0.15564 | 0.009155 | 0.21973 | 0.46234 | 0.16022 | 0.52185 | 122.1588 | 122.1954 | -0.19684 | -0.52185 | 122.0078 | 122.1359 | 121.9894 | 121.6599
2799.9219 | 121.8933 | -121.6324 | 0.14191 | -0.0051118 | -0.012234 | -0.080079 | -0.0059109 | -0.030443 | -0.04974 | -0.041887 | 0.00094606 | -0.016477 | 0.0087756 | -0.017397 | -0.22107 | -0.015565 | -0.022826 | -0.11444 | 0.11444 | -0.15106 | -0.13275 | -0.004578 | -0.13733 | -0.064087 | -0.4715 | 0.16022 | -0.41199 | 0.022888 | -0.24261 | -0.23346 | -0.17395 | 121.4813 | -0.027466 | -0.27466 | 121.6278 | 121.5683 | 121.4951 | 0.086975 | 0.013733 | 121.2204 | 0.01831 | -0.11902 | 121.3898 | 121.4584 | 121.3989 | 0.23804 | 0.17853 | 0.14648 | 0.018311 | 0.16937 | 0.43488 | 0.2655 | 0.5722 | 121.7468 | 121.7926 | -0.29297 | -0.55389 | 121.4996 | 121.6553 | 121.5179 | 121.1609
2801.7188 | 122.1909 | -122.0215 | 0.15106 | 0.0025177 | -0.0092435 | -0.079438 | -0.0037747 | -0.028948 | -0.049099 | -0.040178 | -0.0021057 | -0.018186 | 0.0098438 | -0.016543 | -0.22043 | -0.01471 | -0.018553 | -0.09613 | 0.10986 | -0.13733 | -0.14191 | -0.013733 | -0.18768 | -0.10071 | -0.50354 | 0.16479 | -0.42114 | 0 | -0.30212 | -0.30212 | -0.21057 | 121.8842 | -0.041199 | -0.29297 | 122.0078 | 121.9208 | 121.8338 | 0.036621 | -0.050354 | 121.6003 | 0.013733 | -0.15106 | 121.7194 | 121.8109 | 121.7194 | 0.21057 | 0.11902 | 0.1236 | -0.004578 | 0.11902 | 0.42114 | 0.24719 | 0.58594 | 122.1313 | 122.1863 | -0.28839 | -0.5722 | 121.8796 | 122.0215 | 121.9254 | 121.5179
2803.4531 | 121.8475 | -121.6049 | 0.16022 | 0.010147 | -0.012448 | -0.080933 | -0.0061245 | -0.034502 | -0.051663 | -0.041674 | 0.00094606 | -0.020322 | 0.012407 | -0.019106 | -0.21979 | -0.01706 | -0.023039 | -0.12817 | 0.11444 | -0.15106 | -0.14648 | 0.032043 | -0.13733 | -0.059509 | -0.4715 | 0.16479 | -0.42572 | -0.022888 | -0.27008 | -0.24719 | -0.2243 | 121.4539 | -0.045776 | -0.3067 | 121.637 | 121.5454 | 121.4676 | 0.091553 | 0.013733 | 121.1792 | 0.004578 | -0.1831 | 121.3348 | 121.3806 | 121.3577 | 0.20142 | 0.17853 | 0.18311 | 0.004578 | 0.15564 | 0.40283 | 0.2655 | 0.59052 | 121.7194 | 121.7697 | -0.31128 | -0.58594 | 121.4584 | 121.582 | 121.4767 | 121.1334
2805.2344 | 122.0261 | -121.7697 | 0.15106 | 0.010147 | -0.012875 | -0.079651 | -0.0065517 | -0.030443 | -0.050381 | -0.040819 | -0.011261 | -0.019467 | 0.008562 | -0.021884 | -0.21937 | -0.018342 | -0.024535 | -0.10071 | 0.10986 | -0.15106 | -0.13733 | -0.004578 | -0.1236 | -0.073242 | -0.44861 | 0.16022 | -0.42572 | 0.045776 | -0.21973 | -0.23346 | -0.15564 | 121.6187 | -0.041199 | -0.28839 | 121.7651 | 121.6965 | 121.6461 | 0.07782 | 0.027466 | 121.344 | 0.009155 | -0.10529 | 121.55 | 121.6141 | 121.5363 | 0.27008 | 0.19226 | 0.14648 | 0.013733 | 0.20599 | 0.4715 | 0.26093 | 0.58594 | 121.8796 | 121.9299 | -0.30212 | -0.57678 | 121.6324 | 121.8155 | 121.669 | 121.3211
2806.9688 | 117.366 | -117.0273 | 0.086975 | 0.0025177 | -0.013089 | -0.079011 | -0.0082607 | -0.032793 | -0.049954 | -0.040392 | 0.00094606 | -0.021817 | 0.007494 | -0.02701 | -0.21915 | -0.018982 | -0.023894 | -0.068665 | 0.082397 | -0.10986 | -0.027466 | 0.16022 | 0 | 0.059509 | -0.25635 | 0.11444 | -0.36621 | 0.14191 | -0.086975 | -0.064087 | -0.050354 | 116.9174 | -0.004578 | -0.11444 | 117.1875 | 117.0868 | 117.0273 | 0.16937 | 0.10986 | 116.6611 | 0.027466 | 0.054932 | 116.9403 | 116.9769 | 116.9632 | 0.31586 | 0.30212 | 0.27008 | 0.082397 | 0.27924 | 0.50812 | 0.19226 | 0.48065 | 117.1097 | 117.1417 | -0.19684 | -0.45319 | 116.9998 | 117.1692 | 116.9586 | 116.7709
2808.75 | 121.8933 | -121.5088 | 0.13733 | 0.0025177 | -0.017147 | -0.079651 | -0.0082607 | -0.02788 | -0.052304 | -0.043383 | -0.0021057 | -0.020536 | 0.0081348 | -0.025088 | -0.22107 | -0.018342 | -0.024535 | -0.073242 | 0.068665 | -0.10986 | -0.013733 | 0.15106 | -0.018311 | 0.064087 | -0.2655 | 0.11902 | -0.37079 | 0.15106 | -0.086975 | -0.073242 | -0.054932 | 121.3989 | -0.068664 | -0.15106 | 121.6599 | 121.5729 | 121.4905 | 0.17395 | 0.091552 | 121.138 | -0.01831 | 0.013733 | 121.4218 | 121.4539 | 121.4355 | 0.31586 | 0.29755 | 0.26093 | 0.09613 | 0.28381 | 0.52185 | 0.17853 | 0.48981 | 121.5775 | 121.6278 | -0.24719 | -0.50812 | 121.4951 | 121.6599 | 121.4355 | 121.2433
2810.5469 | 121.8567 | -121.6873 | 0.14191 | -0.0051118 | -0.012661 | -0.07837 | -0.0039883 | -0.028734 | -0.051022 | -0.040605 | -0.0021057 | -0.020108 | 0.0098438 | -0.021243 | -0.22065 | -0.016846 | -0.020689 | -0.11902 | 0.1236 | -0.12817 | -0.14648 | -0.045776 | -0.20142 | -0.09613 | -0.45776 | 0.17395 | -0.40741 | 0.018311 | -0.27008 | -0.28839 | -0.18768 | 121.5591 | -0.018311 | -0.28839 | 121.6415 | 121.5912 | 121.4859 | 0.032044 | -0.073242 | 121.2799 | 0.032043 | -0.1236 | 121.4172 | 121.4996 | 121.3989 | 0.21973 | 0.11902 | 0.082398 | -0.01831 | 0.13733 | 0.42572 | 0.25177 | 0.58136 | 121.8109 | 121.8613 | -0.27008 | -0.54932 | 121.5408 | 121.7056 | 121.5683 | 121.2296
2812.2656 | 121.9437 | -121.7148 | 0.15106 | -0.0051118 | -0.011807 | -0.079224 | -0.0056973 | -0.032152 | -0.050595 | -0.041246 | -0.0021057 | -0.01904 | 0.010057 | -0.010134 | -0.2215 | -0.015137 | -0.021971 | -0.086975 | 0.10529 | -0.12817 | -0.091553 | 0.064087 | -0.10529 | -0.041199 | -0.34332 | 0.16937 | -0.38452 | 0.068665 | -0.1831 | -0.20142 | -0.13275 | 121.5866 | -0.045776 | -0.24261 | 121.7789 | 121.6736 | 121.6095 | 0.086975 | 0.022888 | 121.3303 | 0.018311 | -0.082397 | 121.5317 | 121.582 | 121.5134 | 0.25177 | 0.1831 | 0.19226 | 0.036621 | 0.20142 | 0.45319 | 0.23346 | 0.55389 | 121.8201 | 121.8842 | -0.27924 | -0.53558 | 121.6232 | 121.7834 | 121.6278 | 121.3715
2814.0312 | 122.049 | -121.7285 | 0.12817 | -0.0051118 | -0.010098 | -0.078156 | -0.0076199 | -0.029802 | -0.046108 | -0.041674 | 0.00094606 | -0.02139 | 0.0077076 | -0.027224 | -0.21979 | -0.018769 | -0.02133 | -0.045776 | 0.07782 | -0.068665 | -0.013733 | 0.13275 | -0.050354 | 0.018311 | -0.21515 | 0.13733 | -0.31128 | 0.15106 | -0.059509 | -0.041199 | 0.004578 | 121.6599 | -0.050354 | -0.14191 | 121.8613 | 121.7468 | 121.6782 | 0.086976 | 0.018311 | 121.4172 | 0.009155 | 0.022888 | 121.669 | 121.7331 | 121.6873 | 0.31586 | 0.27008 | 0.20142 | 0.054932 | 0.25177 | 0.46234 | 0.14649 | 0.44861 | 121.8063 | 121.8658 | -0.19684 | -0.43945 | 121.7148 | 121.8796 | 121.6827 | 121.5134
2815.8281 | 121.994 | -121.2753 | 0.41199 | 0.0025177 | -0.01138 | -0.07837 | -0.0056973 | -0.027239 | -0.051449 | -0.040178 | -0.0021057 | -0.012631 | 0.0072802 | -0.02167 | -0.22278 | -0.016846 | -0.022826 | -0.09613 | 0.10986 | -0.10071 | -0.10071 | 0.036621 | -0.14191 | -0.032043 | -0.19684 | 0.46692 | -0.16479 | 0.13275 | 0.045776 | 0.068665 | 0.45776 | 121.1746 | -0.30212 | -0.5127 | 121.312 | 121.2433 | 121.1334 | 0.068665 | -0.041199 | 121.1105 | 0.054932 | -0.27924 | 121.3211 | 121.7331 | 121.344 | 0.62256 | 0.23346 | 0.13733 | 0 | 0.21057 | 0.29755 | 0.21057 | 0.63171 | 121.3852 | 121.7422 | -0.5127 | -0.57678 | 121.1746 | 121.4081 | 121.1792 | 121.0785
2817.5625 | 120.7718 | -120.4605 | 0.10529 | -0.012741 | -0.018643 | -0.078156 | -0.0086879 | -0.028307 | -0.053799 | -0.039965 | 0.0039979 | -0.02139 | 0.0079212 | -0.024874 | -0.22022 | -0.018342 | -0.024107 | -0.086975 | 0.09613 | -0.1236 | -0.032043 | 0.15106 | -0.022888 | 0.054932 | -0.091553 | 0.11444 | -0.14648 | 0.11902 | 0.091553 | 0.13733 | 0.15106 | 120.3369 | -0.009156 | -0.13733 | 120.6116 | 120.5154 | 120.4376 | 0.17853 | 0.10071 | 120.314 | 0.009155 | 0.013733 | 120.5521 | 120.6116 | 120.5978 | 0.29755 | 0.28381 | 0.27466 | 0.091553 | 0.23804 | 0.2655 | 0.21973 | 0.26093 | 120.5566 | 120.575 | -0.22888 | -0.25177 | 120.4285 | 120.5795 | 120.3735 | 120.369
2819.3594 | 121.3852 | -121.0464 | 0.11444 | 0.010147 | -0.011593 | -0.078583 | -0.0059109 | -0.029162 | -0.050808 | -0.040819 | 0.0039979 | -0.020749 | 0.0053576 | -0.016757 | -0.22172 | -0.017273 | -0.024962 | -0.018311 | 0.07782 | -0.091553 | -0.009155 | 0.13275 | -0.073242 | 0.027466 | -0.10071 | 0.10986 | -0.12817 | 0.13275 | 0.082397 | 0.11444 | 0.16937 | 120.9549 | -0.036621 | -0.1236 | 121.1792 | 121.0739 | 120.9732 | 0.11902 | 0.018311 | 120.9183 | -0.004578 | 0.01831 | 121.1288 | 121.2158 | 121.1609 | 0.29755 | 0.24262 | 0.2243 | 0.082398 | 0.21057 | 0.26093 | 0.16937 | 0.23804 | 121.1243 | 121.1563 | -0.20599 | -0.24262 | 121.0373 | 121.1792 | 121.0281 | 120.9457
2821.1406 | 121.4447 | -121.1746 | 0.11902 | -0.0051118 | -0.013943 | -0.079651 | -0.0063381 | -0.031298 | -0.049954 | -0.038042 | 0.00094606 | -0.021817 | 0.0098438 | -0.021243 | -0.21894 | -0.017273 | -0.024535 | -0.091553 | 0.091553 | -0.10529 | -0.091553 | 0.068665 | -0.082397 | -0.009155 | -0.18768 | 0.1236 | -0.15564 | 0.082397 | 0.054932 | 0.09613 | 0.11444 | 121.0693 | -0.027466 | -0.21057 | 121.2433 | 121.1655 | 121.0922 | 0.096131 | 0.022889 | 121.019 | 0.004577 | -0.036622 | 121.2296 | 121.2891 | 121.2708 | 0.27008 | 0.25177 | 0.17395 | 0.013733 | 0.21057 | 0.23804 | 0.19684 | 0.27924 | 121.2662 | 121.2982 | -0.22431 | -0.27466 | 121.0831 | 121.257 | 121.0831 | 120.9869
2822.875 | 121.4676 | -121.2616 | 0.13733 | -0.012741 | -0.013089 | -0.078583 | -0.0035611 | -0.024675 | -0.050167 | -0.039751 | -0.0021057 | -0.019254 | 0.008562 | -0.014407 | -0.22107 | -0.01706 | -0.024107 | -0.082397 | 0.12817 | -0.13733 | -0.09613 | 0.022888 | -0.11444 | -0.041199 | -0.18768 | 0.14648 | -0.16022 | 0.045776 | 0.013733 | 0.018311 | 0.07782 | 121.1243 | -0.009155 | -0.23346 | 121.2845 | 121.2204 | 121.1472 | 0.09613 | 0.022888 | 121.1014 | 0.009155 | -0.091553 | 121.2753 | 121.3394 | 121.2799 | 0.23804 | 0.17853 | 0.16022 | 0.041199 | 0.17395 | 0.20599 | 0.2655 | 0.3067 | 121.3898 | 121.4081 | -0.27466 | -0.29755 | 121.1655 | 121.3074 | 121.1792 | 121.0739
2824.6719 | 121.5912 | -121.2845 | 0.10529 | -0.0051118 | -0.0098843 | -0.078583 | -0.0069791 | -0.026812 | -0.049954 | -0.040605 | -0.0051575 | -0.019254 | 0.0083484 | -0.023593 | -0.22172 | -0.015992 | -0.020049 | -0.045776 | 0.068665 | -0.073242 | -0.022888 | 0.11902 | -0.050354 | 0.032043 | -0.086975 | 0.10986 | -0.13733 | 0.11902 | 0.09613 | 0.10529 | 0.16022 | 121.2112 | -0.036621 | -0.12817 | 121.4035 | 121.3165 | 121.2341 | 0.10529 | 0.022888 | 121.1472 | 0.004577 | 0.013733 | 121.3806 | 121.4447 | 121.3898 | 0.29755 | 0.24262 | 0.19226 | 0.050354 | 0.23346 | 0.25635 | 0.14191 | 0.24719 | 121.3531 | 121.3943 | -0.17853 | -0.24262 | 121.2616 | 121.4035 | 121.2387 | 121.1975
2826.3906 | 121.5958 | -121.344 | 0.12817 | 0.0025177 | -0.0081753 | -0.078583 | -0.0063381 | -0.029589 | -0.048886 | -0.042528 | -0.0021057 | -0.019895 | 0.0077076 | -0.020175 | -0.21766 | -0.017914 | -0.022185 | -0.07782 | 0.064087 | -0.091553 | -0.027466 | 0.14648 | -0.068665 | 0.022888 | -0.086975 | 0.10986 | -0.13733 | 0.10529 | 0.059509 | 0.09613 | 0.13275 | 121.2524 | -0.064087 | -0.15564 | 121.4905 | 121.3669 | 121.2753 | 0.11444 | 0.022888 | 121.2067 | -0.018311 | -0.022888 | 121.4035 | 121.4767 | 121.4401 | 0.27008 | 0.23346 | 0.23804 | 0.064087 | 0.19684 | 0.24262 | 0.15564 | 0.24719 | 121.4081 | 121.4539 | -0.21973 | -0.2655 | 121.3165 | 121.4493 | 121.2662 | 121.257
2828.1719 | 121.6599 | -121.3577 | 0.11444 | 0.010147 | -0.012875 | -0.079224 | -0.0054837 | -0.031298 | -0.049954 | -0.037615 | -0.0021057 | -0.020963 | 0.0077076 | -0.019961 | -0.22107 | -0.01941 | -0.023894 | -0.059509 | 0.073242 | -0.10071 | -0.013733 | 0.16022 | -0.027466 | 0.045776 | -0.09613 | 0.12817 | -0.13275 | 0.09613 | 0.091553 | 0.12817 | 0.14648 | 121.257 | -0.041199 | -0.12817 | 121.5179 | 121.4035 | 121.3303 | 0.14648 | 0.073242 | 121.225 | 0.013733 | -0.018311 | 121.4493 | 121.5042 | 121.4859 | 0.27924 | 0.26093 | 0.26093 | 0.086975 | 0.2243 | 0.22888 | 0.17395 | 0.26093 | 121.431 | 121.4859 | -0.21515 | -0.24719 | 121.344 | 121.4539 | 121.2982 | 121.2616
2829.9062 | 121.6507 | -121.3669 | 0.12817 | -0.0051118 | -0.014798 | -0.082215 | -0.0059109 | -0.033648 | -0.048886 | -0.042528 | -0.0021057 | -0.018186 | 0.0066394 | -0.02637 | -0.21851 | -0.017914 | -0.026244 | -0.10529 | 0.073242 | -0.09613 | -0.07782 | 0.064087 | -0.082397 | -0.018311 | -0.15564 | 0.12817 | -0.16937 | 0.045776 | 0.032043 | 0.050354 | 0.1236 | 121.2708 | -0.054932 | -0.20599 | 121.431 | 121.3486 | 121.2845 | 0.077819 | 0.013733 | 121.1975 | 0 | -0.082398 | 121.3989 | 121.4905 | 121.4172 | 0.29297 | 0.21973 | 0.16022 | 0.01831 | 0.20142 | 0.21515 | 0.16937 | 0.29755 | 121.4401 | 121.4951 | -0.2243 | -0.29755 | 121.2891 | 121.4127 | 121.2616 | 121.2112
2831.6875 | 121.6049 | -121.4401 | 0.12817 | 0.0025177 | -0.010098 | -0.080079 | -0.0048427 | -0.028307 | -0.048886 | -0.041674 | -0.0021057 | -0.021176 | 0.0072802 | -0.013979 | -0.22086 | -0.01706 | -0.020689 | -0.10529 | 0.1236 | -0.14648 | -0.14648 | -0.054932 | -0.20142 | -0.10071 | -0.26093 | 0.14648 | -0.19226 | 0 | -0.068665 | -0.054932 | 0.027466 | 121.2936 | -0.004578 | -0.27466 | 121.3852 | 121.3394 | 121.2387 | 0.045776 | -0.054932 | 121.2479 | 0.01831 | -0.12817 | 121.3715 | 121.4676 | 121.3852 | 0.21973 | 0.13733 | 0.091552 | 0 | 0.1236 | 0.19226 | 0.27008 | 0.33874 | 121.5637 | 121.5866 | -0.27466 | -0.32044 | 121.2936 | 121.4401 | 121.3348 | 121.1792
2833.4844 | 121.6553 | -121.463 | 0.13275 | 0.0025177 | -0.010525 | -0.079438 | -0.0037747 | -0.02553 | -0.051022 | -0.042314 | 0.00094606 | -0.018399 | 0.0089892 | -0.013125 | -0.22107 | -0.016633 | -0.025389 | -0.07782 | 0.12817 | -0.13733 | -0.09613 | 0.054932 | -0.10986 | -0.050354 | -0.16479 | 0.16022 | -0.16479 | 0.050354 | 0.032043 | 0.036621 | 0.091553 | 121.3257 | -0.004577 | -0.22888 | 121.5179 | 121.4127 | 121.3531 | 0.086975 | 0.027466 | 121.2982 | 0.027466 | -0.082397 | 121.4951 | 121.5546 | 121.4996 | 0.25635 | 0.20142 | 0.19226 | 0.041199 | 0.19684 | 0.21515 | 0.2655 | 0.32501 | 121.5912 | 121.6232 | -0.27008 | -0.29755 | 121.3669 | 121.5134 | 121.3852 | 121.2982
2835.1875 | 121.7194 | -121.463 | 0.1236 | 0.0025177 | -0.013516 | -0.079865 | -0.0056973 | -0.03023 | -0.048031 | -0.04146 | 0.00094606 | -0.020536 | 0.007494 | -0.025942 | -0.21894 | -0.017273 | -0.025603 | -0.09613 | 0.07782 | -0.10986 | -0.091553 | 0.068665 | -0.10071 | -0.004578 | -0.17395 | 0.12817 | -0.16022 | 0.054932 | 0.050354 | 0.068665 | 0.09613 | 121.3531 | -0.045776 | -0.21515 | 121.5317 | 121.4584 | 121.3623 | 0.10529 | 0.009155 | 121.3028 | 0.004578 | -0.068664 | 121.5134 | 121.5591 | 121.5317 | 0.25635 | 0.22888 | 0.17853 | 0.01831 | 0.21057 | 0.21515 | 0.18768 | 0.28839 | 121.5408 | 121.5912 | -0.23346 | -0.28381 | 121.3715 | 121.5179 | 121.3669 | 121.2891
2836.9844 | 121.7606 | -121.4584 | 0.13275 | -0.0051118 | -0.013943 | -0.08136 | -0.0078335 | -0.032152 | -0.052517 | -0.041246 | 0.00094606 | -0.021176 | 0.008562 | -0.018466 | -0.21958 | -0.018342 | -0.02133 | -0.11444 | 0.09613 | -0.1236 | -0.091553 | 0.068665 | -0.09613 | -0.009155 | -0.16479 | 0.1236 | -0.14191 | 0.07782 | 0.059509 | 0.09613 | 0.11444 | 121.3348 | -0.036621 | -0.2243 | 121.5271 | 121.4493 | 121.3623 | 0.11444 | 0.027466 | 121.3165 | -0.009155 | -0.054931 | 121.5179 | 121.5729 | 121.5546 | 0.25635 | 0.23804 | 0.19226 | 0.032043 | 0.20142 | 0.21973 | 0.21973 | 0.2655 | 121.5546 | 121.582 | -0.25635 | -0.27466 | 121.3669 | 121.5363 | 121.344 | 121.2936
2838.7812 | 121.7422 | -121.4905 | 0.11902 | 0.0025177 | -0.013516 | -0.078797 | -0.0054837 | -0.031939 | -0.051876 | -0.042528 | -0.0021057 | -0.020108 | 0.0066394 | -0.024661 | -0.21915 | -0.018982 | -0.025389 | -0.082397 | 0.082397 | -0.10071 | -0.068665 | 0.091553 | -0.086975 | 0 | -0.13275 | 0.14191 | -0.15106 | 0.054932 | 0.050354 | 0.07782 | 0.10986 | 121.3898 | -0.036622 | -0.18768 | 121.582 | 121.4905 | 121.4035 | 0.10071 | 0.013733 | 121.3394 | 0.022888 | -0.064087 | 121.5408 | 121.6003 | 121.5683 | 0.26093 | 0.22888 | 0.19226 | 0.032043 | 0.20142 | 0.20599 | 0.18311 | 0.29297 | 121.5729 | 121.6324 | -0.21973 | -0.27008 | 121.4218 | 121.5454 | 121.4081 | 121.3577
2840.5781 | 121.7926 | -121.5088 | 0.11902 | 0.0025177 | -0.012234 | -0.078797 | -0.0050565 | -0.035357 | -0.052731 | -0.04146 | 0.00094606 | -0.020536 | 0.005785 | -0.018466 | -0.22129 | -0.019837 | -0.024107 | -0.064087 | 0.086975 | -0.10071 | -0.009155 | 0.13275 | -0.013733 | 0.045776 | -0.09613 | 0.12817 | -0.13733 | 0.10986 | 0.091553 | 0.12817 | 0.13733 | 121.4081 | -0.032044 | -0.12817 | 121.6415 | 121.5546 | 121.4951 | 0.14648 | 0.086975 | 121.3715 | 0.009155 | -0.009156 | 121.6003 | 121.6461 | 121.637 | 0.27466 | 0.2655 | 0.23346 | 0.091553 | 0.22888 | 0.24719 | 0.18768 | 0.2655 | 121.5958 | 121.637 | -0.21973 | -0.25635 | 121.4996 | 121.6187 | 121.4447 | 121.4127
2842.3125 | 121.8018 | -121.5363 | 0.11444 | -0.0051118 | -0.01138 | -0.078156 | -0.0074063 | -0.031725 | -0.04974 | -0.041674 | -0.0021057 | -0.01904 | 0.0079212 | -0.018038 | -0.22086 | -0.019196 | -0.026244 | -0.091553 | 0.086975 | -0.10986 | -0.086975 | 0.059509 | -0.10529 | -0.027466 | -0.17853 | 0.11902 | -0.14648 | 0.054932 | 0.032043 | 0.059509 | 0.09613 | 121.4264 | -0.027466 | -0.20142 | 121.5958 | 121.5088 | 121.431 | 0.082397 | 0.004577 | 121.3898 | 0.004578 | -0.059509 | 121.5683 | 121.6324 | 121.5958 | 0.24261 | 0.20599 | 0.16937 | 0.022888 | 0.17853 | 0.20142 | 0.19684 | 0.2655 | 121.6232 | 121.6553 | -0.2243 | -0.26093 | 121.4493 | 121.5912 | 121.4447 | 121.3577
2844.0938 | 121.8155 | -121.5546 | 0.11444 | -0.0051118 | -0.014798 | -0.079224 | -0.0071927 | -0.03322 | -0.051449 | -0.041246 | -0.0021057 | -0.021604 | 0.0059986 | -0.025301 | -0.22022 | -0.018555 | -0.026885 | -0.09613 | 0.086975 | -0.10071 | -0.082397 | 0.045776 | -0.09613 | -0.004578 | -0.16937 | 0.14191 | -0.15564 | 0.068665 | 0.041199 | 0.054932 | 0.10529 | 121.4539 | -0.027466 | -0.19684 | 121.6003 | 121.55 | 121.4584 | 0.09613 | 0.004578 | 121.3989 | 0.027466 | -0.045776 | 121.5958 | 121.6599 | 121.6095 | 0.26093 | 0.21057 | 0.14648 | 0.018311 | 0.19684 | 0.22431 | 0.18768 | 0.29755 | 121.6415 | 121.6965 | -0.21515 | -0.27008 | 121.4722 | 121.6232 | 121.4584 | 121.3852
2845.875 | 121.7285 | -121.6049 | 0.16022 | 0.010147 | -0.014798 | -0.080933 | -0.0052701 | -0.028948 | -0.050808 | -0.044664 | -0.0021057 | -0.019467 | 0.0092028 | -0.017611 | -0.22001 | -0.016419 | -0.023039 | -0.13275 | 0.10986 | -0.13733 | -0.14648 | -0.018311 | -0.13733 | -0.068665 | -0.25177 | 0.16937 | -0.17395 | -0.027466 | -0.050354 | -0.018311 | 0.013733 | 121.4676 | -0.050354 | -0.3067 | 121.5866 | 121.5363 | 121.4676 | 0.068664 | 0 | 121.431 | 0.009156 | -0.18768 | 121.5546 | 121.6187 | 121.5866 | 0.18768 | 0.15564 | 0.11902 | -0.009155 | 0.1236 | 0.14648 | 0.24719 | 0.34332 | 121.7148 | 121.7743 | -0.29755 | -0.33417 | 121.4584 | 121.5775 | 121.4722 | 121.3531
2847.6719 | 121.8842 | -121.5637 | 0.11902 | 0.0025177 | -0.015866 | -0.081147 | -0.0056973 | -0.031084 | -0.051235 | -0.042955 | -0.0021057 | -0.019681 | 0.0083484 | -0.021456 | -0.21958 | -0.018342 | -0.026244 | -0.054932 | 0.082397 | -0.10529 | -0.009155 | 0.15564 | -0.009155 | 0.054932 | -0.073242 | 0.13275 | -0.12817 | 0.10986 | 0.09613 | 0.15106 | 0.15564 | 121.4584 | -0.036622 | -0.12817 | 121.7194 | 121.6187 | 121.5546 | 0.16022 | 0.096131 | 121.4355 | 0.013732 | -0.009156 | 121.6599 | 121.7194 | 121.7148 | 0.28381 | 0.27924 | 0.26093 | 0.096131 | 0.2243 | 0.23804 | 0.18768 | 0.26093 | 121.6461 | 121.6965 | -0.22431 | -0.24719 | 121.5546 | 121.6736 | 121.5088 | 121.4905
2849.4062 | 121.7743 | -121.6187 | 0.16479 | 0.0025177 | -0.0088163 | -0.076661 | -0.0018521 | -0.029162 | -0.050595 | -0.043169 | -0.0021057 | -0.019254 | 0.0094166 | -0.023593 | -0.2215 | -0.015565 | -0.020903 | -0.12817 | 0.12817 | -0.14191 | -0.15564 | -0.036621 | -0.18768 | -0.10071 | -0.26093 | 0.16479 | -0.17853 | 0.004578 | -0.059509 | -0.059509 | 0.041199 | 121.4767 | -0.036621 | -0.32044 | 121.582 | 121.5179 | 121.431 | 0.041199 | -0.045776 | 121.4401 | 0 | -0.16022 | 121.5591 | 121.6599 | 121.5591 | 0.21973 | 0.11902 | 0.10529 | -0.013733 | 0.11902 | 0.18311 | 0.27008 | 0.34332 | 121.7468 | 121.7834 | -0.3067 | -0.34332 | 121.463 | 121.6232 | 121.4905 | 121.3577
2851.1719 | 121.8613 | -121.6003 | 0.1236 | 0.0025177 | -0.012448 | -0.080506 | -0.0071927 | -0.033434 | -0.04974 | -0.040392 | 0.00094606 | -0.020963 | 0.007494 | -0.022524 | -0.21808 | -0.018342 | -0.023039 | -0.091553 | 0.086975 | -0.10986 | -0.09613 | 0.045776 | -0.10986 | 0 | -0.16937 | 0.13275 | -0.14191 | 0.068665 | 0.054932 | 0.064087 | 0.10071 | 121.4905 | -0.036621 | -0.21973 | 121.6461 | 121.6003 | 121.4905 | 0.10986 | 0 | 121.4584 | 0.009155 | -0.054931 | 121.6553 | 121.701 | 121.6644 | 0.24262 | 0.20599 | 0.15564 | 0.013733 | 0.19684 | 0.21057 | 0.19684 | 0.27466 | 121.6873 | 121.7331 | -0.23346 | -0.2655 | 121.5042 | 121.669 | 121.5088 | 121.431
2852.9062 | 121.9208 | -121.5866 | 0.12817 | 0.0025177 | -0.014584 | -0.079865 | -0.0071927 | -0.02788 | -0.050381 | -0.039751 | -0.0021057 | -0.02139 | 0.0070666 | -0.016543 | -0.22043 | -0.017273 | -0.026885 | -0.059509 | 0.050354 | -0.091553 | -0.018311 | 0.13733 | -0.009155 | 0.041199 | -0.09613 | 0.14648 | -0.12817 | 0.10986 | 0.10529 | 0.12817 | 0.14648 | 121.4951 | -0.07782 | -0.14649 | 121.7239 | 121.6278 | 121.5775 | 0.13275 | 0.082398 | 121.4584 | 0.01831 | -0.018311 | 121.6919 | 121.7331 | 121.7148 | 0.27466 | 0.25635 | 0.22888 | 0.073242 | 0.23346 | 0.23804 | 0.14191 | 0.27466 | 121.637 | 121.7331 | -0.21973 | -0.25635 | 121.5683 | 121.6965 | 121.5271 | 121.4905
2854.7031 | 121.8796 | -121.6232 | 0.11902 | 0.0025177 | -0.01437 | -0.078797 | -0.0076199 | -0.034929 | -0.05209 | -0.040819 | 0.00094606 | -0.022672 | 0.0059986 | -0.019961 | -0.22065 | -0.016205 | -0.024107 | -0.091553 | 0.07782 | -0.10071 | -0.082397 | 0.054932 | -0.091553 | -0.018311 | -0.17853 | 0.13733 | -0.14191 | 0.064087 | 0.032043 | 0.064087 | 0.10529 | 121.5225 | -0.041199 | -0.20142 | 121.6782 | 121.6049 | 121.5317 | 0.082397 | 0.009155 | 121.4813 | 0.01831 | -0.054932 | 121.6553 | 121.7285 | 121.6873 | 0.24719 | 0.20599 | 0.15564 | 0.018311 | 0.17395 | 0.20599 | 0.17853 | 0.27924 | 121.7011 | 121.7606 | -0.21973 | -0.26093 | 121.5408 | 121.6873 | 121.5317 | 121.4447
2856.5 | 121.8658 | -121.6553 | 0.13733 | -0.0051118 | -0.01202 | -0.079011 | -0.0044155 | -0.034075 | -0.049954 | -0.038042 | -0.0021057 | -0.019895 | 0.0072802 | -0.0071436 | -0.21872 | -0.015778 | -0.025603 | -0.11902 | 0.11444 | -0.14191 | -0.13733 | -0.004578 | -0.17395 | -0.082397 | -0.21515 | 0.16479 | -0.17395 | 0.027466 | -0.027466 | -0.018311 | 0.064087 | 121.5134 | -0.022888 | -0.27466 | 121.6507 | 121.5729 | 121.4813 | 0.05951 | -0.032043 | 121.4813 | 0.027466 | -0.10986 | 121.6278 | 121.7194 | 121.637 | 0.23804 | 0.15564 | 0.13733 | 0.004578 | 0.14648 | 0.20142 | 0.25635 | 0.33874 | 121.7697 | 121.8201 | -0.27924 | -0.31128 | 121.5179 | 121.6827 | 121.5363 | 121.4401
2858.2188 | 121.9849 | -121.5912 | 0.16937 | -0.0051118 | -0.013729 | -0.079651 | -0.0074063 | -0.036852 | -0.053585 | -0.04146 | -0.0021057 | -0.020108 | 0.0081348 | -0.020815 | -0.21787 | -0.017914 | -0.022826 | -0.064087 | 0.059509 | -0.10529 | -0.013733 | 0.17853 | 0 | 0.054932 | 0.027466 | 0.17395 | -0.13275 | 0.16937 | 0.15564 | 0.14191 | 0.16479 | 121.4859 | -0.10986 | -0.18311 | 121.7697 | 121.6461 | 121.5912 | 0.16022 | 0.10529 | 121.4584 | 0.004577 | 0 | 121.7468 | 121.756 | 121.7331 | 0.29755 | 0.27466 | 0.28381 | 0.091553 | 0.28839 | 0.30212 | 0.16479 | 0.3067 | 121.6507 | 121.7651 | -0.27466 | -0.30212 | 121.5775 | 121.7606 | 121.5271 | 121.6187
2860.0156 | 121.9574 | -121.6003 | 0.1831 | -0.012741 | -0.015225 | -0.079865 | -0.0059109 | -0.031084 | -0.051449 | -0.04146 | 0.00094606 | -0.019681 | 0.0079212 | -0.025088 | -0.2183 | -0.019196 | -0.023253 | -0.041199 | 0.086975 | -0.10071 | -0.022888 | 0.14648 | -0.013733 | 0.032043 | -0.018311 | 0.18768 | -0.14648 | 0.15564 | 0.1236 | 0.13275 | 0.14191 | 121.4996 | -0.09613 | -0.20599 | 121.7468 | 121.6324 | 121.5866 | 0.13275 | 0.086975 | 121.4539 | 0.004578 | -0.027465 | 121.7239 | 121.7422 | 121.7331 | 0.28839 | 0.27924 | 0.24719 | 0.07782 | 0.27008 | 0.30212 | 0.18768 | 0.33417 | 121.6873 | 121.788 | -0.28381 | -0.32959 | 121.5775 | 121.756 | 121.5591 | 121.582
2861.7969 | 121.8475 | -121.6507 | 0.20599 | -0.0051118 | -0.0096707 | -0.079865 | -0.0031337 | -0.029802 | -0.050167 | -0.040178 | -0.0021057 | -0.019254 | 0.0077076 | -0.015261 | -0.21808 | -0.017487 | -0.024107 | -0.10986 | 0.13275 | -0.13275 | -0.16022 | -0.050354 | -0.21057 | -0.09613 | -0.17853 | 0.21515 | -0.17395 | 0.068665 | -0.032043 | -0.050354 | 0.036621 | 121.5179 | -0.073243 | -0.36621 | 121.6003 | 121.5546 | 121.4401 | 0.036621 | -0.07782 | 121.4767 | 0.009155 | -0.13733 | 121.6187 | 121.6873 | 121.6003 | 0.21057 | 0.1236 | 0.082397 | -0.027466 | 0.14191 | 0.24261 | 0.2655 | 0.3891 | 121.7834 | 121.8658 | -0.33875 | -0.37994 | 121.4905 | 121.7194 | 121.5408 | 121.4722
2863.5938 | 121.9711 | -121.6049 | 0.17853 | 0.0025177 | -0.0094571 | -0.078583 | -0.0050565 | -0.027453 | -0.050595 | -0.04146 | -0.0021057 | -0.020536 | 0.0079212 | -0.013766 | -0.21915 | -0.017273 | -0.024535 | -0.059509 | 0.091553 | -0.10529 | -0.032043 | 0.10529 | -0.068665 | -0.004578 | -0.004578 | 0.1831 | -0.13275 | 0.19226 | 0.11902 | 0.091553 | 0.17395 | 121.4996 | -0.086975 | -0.21057 | 121.7102 | 121.6003 | 121.5363 | 0.10071 | 0.036621 | 121.4722 | 0.004577 | 0.013733 | 121.7239 | 121.7789 | 121.6965 | 0.3067 | 0.2243 | 0.21057 | 0.073243 | 0.25177 | 0.32501 | 0.19684 | 0.31586 | 121.6965 | 121.788 | -0.28381 | -0.31128 | 121.5729 | 121.7972 | 121.5454 | 121.6003
2865.3125 | 121.9711 | -121.6324 | 0.19684 | -0.0051118 | -0.015011 | -0.080719 | -0.0086879 | -0.026598 | -0.049313 | -0.040392 | -0.0051575 | -0.023099 | 0.008562 | -0.022311 | -0.21958 | -0.018982 | -0.022185 | -0.10071 | 0.09613 | -0.11444 | -0.07782 | 0.073242 | -0.086975 | -0.013733 | -0.086975 | 0.18768 | -0.15564 | 0.15106 | 0.086975 | 0.10071 | 0.11902 | 121.5179 | -0.10071 | -0.27466 | 121.7056 | 121.6187 | 121.5454 | 0.10071 | 0.027466 | 121.4767 | -0.009155 | -0.045776 | 121.7194 | 121.7514 | 121.7331 | 0.27466 | 0.25635 | 0.18768 | 0.036621 | 0.24261 | 0.3067 | 0.21057 | 0.34332 | 121.7285 | 121.8201 | -0.31128 | -0.35248 | 121.5546 | 121.7834 | 121.5317 | 121.5454
2867.0938 | 121.9757 | -121.6324 | 0.1831 | 0.0025177 | -0.010525 | -0.080292 | -0.0033475 | -0.028521 | -0.052944 | -0.040819 | -0.0051575 | -0.017331 | 0.0077076 | -0.022738 | -0.21937 | -0.015778 | -0.023039 | -0.1236 | 0.11902 | -0.12817 | -0.10986 | 0.009155 | -0.16022 | -0.073242 | -0.09613 | 0.20599 | -0.15564 | 0.12817 | 0.059509 | 0.045776 | 0.11444 | 121.5042 | -0.064086 | -0.29297 | 121.6415 | 121.5591 | 121.4722 | 0.054932 | -0.032043 | 121.4767 | 0.022889 | -0.054931 | 121.6919 | 121.7468 | 121.6782 | 0.27008 | 0.20142 | 0.13733 | 0.018311 | 0.21515 | 0.28381 | 0.24719 | 0.36163 | 121.7514 | 121.8384 | -0.31128 | -0.33874 | 121.5225 | 121.7606 | 121.5088 | 121.5363
2868.8906 | 122.0398 | -121.6553 | 0.1831 | -0.0051118 | -0.013943 | -0.079224 | -0.0061245 | -0.034716 | -0.051022 | -0.04146 | -0.0021057 | -0.021817 | 0.0089892 | -0.028719 | -0.22086 | -0.016419 | -0.023039 | -0.086975 | 0.068665 | -0.10529 | -0.050354 | 0.10986 | -0.032043 | 0.032043 | -0.027466 | 0.20142 | -0.14648 | 0.16937 | 0.15564 | 0.13275 | 0.15106 | 121.55 | -0.11444 | -0.23346 | 121.7651 | 121.6873 | 121.6232 | 0.13733 | 0.073243 | 121.5088 | 0.018311 | -0.013732 | 121.8109 | 121.8063 | 121.788 | 0.29755 | 0.27924 | 0.21515 | 0.054932 | 0.30212 | 0.31586 | 0.17395 | 0.3479 | 121.7239 | 121.8567 | -0.28839 | -0.32959 | 121.6049 | 121.8246 | 121.5683 | 121.6278
2870.7031 | 121.994 | -121.6736 | 0.17853 | -0.0051118 | -0.012448 | -0.079224 | -0.0061245 | -0.029802 | -0.050595 | -0.04381 | 0.00094606 | -0.022885 | 0.0066394 | -0.021243 | -0.21894 | -0.016846 | -0.023253 | -0.086975 | 0.10529 | -0.082397 | -0.064087 | 0.082397 | -0.091553 | 0.009155 | -0.045776 | 0.1831 | -0.13733 | 0.11444 | 0.09613 | 0.068665 | 0.10529 | 121.5912 | -0.073242 | -0.24261 | 121.756 | 121.6827 | 121.582 | 0.091552 | -0.009156 | 121.5363 | 0.004577 | -0.064087 | 121.7697 | 121.7789 | 121.7422 | 0.24262 | 0.20599 | 0.16479 | 0.01831 | 0.23346 | 0.25177 | 0.18768 | 0.32043 | 121.7789 | 121.8567 | -0.26092 | -0.31586 | 121.6095 | 121.788 | 121.5866 | 121.6278
2872.5 | 121.9208 | -121.6644 | 0.21057 | -0.0051118 | -0.011166 | -0.07837 | -0.0052701 | -0.03023 | -0.048458 | -0.041674 | -0.0021057 | -0.019254 | 0.0055712 | -0.015688 | -0.21979 | -0.016205 | -0.023253 | -0.11444 | 0.1236 | -0.13733 | -0.16022 | -0.032043 | -0.1831 | -0.10071 | -0.12817 | 0.21973 | -0.17395 | 0.068665 | 0 | -0.050354 | 0.045776 | 121.5271 | -0.086975 | -0.37079 | 121.6324 | 121.5637 | 121.4813 | 0.036621 | -0.045776 | 121.4905 | 0.009156 | -0.14191 | 121.6644 | 121.7102 | 121.6141 | 0.21973 | 0.1236 | 0.10529 | -0.022888 | 0.17395 | 0.24261 | 0.26093 | 0.39368 | 121.788 | 121.8842 | -0.3479 | -0.38452 | 121.5042 | 121.7331 | 121.55 | 121.5363
2874.2188 | 121.9482 | -121.7331 | 0.20599 | -0.0051118 | -0.01202 | -0.080719 | -0.0054837 | -0.035784 | -0.049099 | -0.040178 | 0.00094606 | -0.018186 | 0.0094166 | -0.021456 | -0.22022 | -0.016419 | -0.026457 | -0.1236 | 0.12817 | -0.14191 | -0.15564 | -0.009155 | -0.15106 | -0.068665 | -0.14648 | 0.21515 | -0.1831 | 0.054932 | 0.018311 | 0 | 0.050354 | 121.5912 | -0.07782 | -0.36163 | 121.7239 | 121.6644 | 121.582 | 0.073242 | -0.009155 | 121.55 | 0.009155 | -0.15106 | 121.7514 | 121.7834 | 121.7331 | 0.23346 | 0.1831 | 0.13275 | -0.013733 | 0.20142 | 0.23804 | 0.27008 | 0.39825 | 121.8613 | 121.9482 | -0.3479 | -0.3891 | 121.5775 | 121.788 | 121.6095 | 121.5866
2876.0312 | 121.962 | -121.6965 | 0.20599 | 0.0025177 | -0.010098 | -0.077302 | -0.0042019 | -0.028948 | -0.049954 | -0.041246 | 0.00094606 | -0.01669 | 0.0089892 | -0.018038 | -0.21872 | -0.017487 | -0.024321 | -0.068665 | 0.12817 | -0.11902 | -0.086975 | 0.054932 | -0.1236 | -0.045776 | -0.073242 | 0.21057 | -0.15564 | 0.10986 | 0.032043 | -0.004578 | 0.064087 | 121.5775 | -0.07782 | -0.29297 | 121.7514 | 121.6507 | 121.5729 | 0.073243 | -0.004577 | 121.5408 | 0.004577 | -0.096131 | 121.7285 | 121.7606 | 121.6919 | 0.21973 | 0.15106 | 0.17395 | 0.032044 | 0.18768 | 0.2655 | 0.24719 | 0.36621 | 121.8246 | 121.907 | -0.32501 | -0.36163 | 121.6095 | 121.8063 | 121.6278 | 121.6232
2877.8281 | 121.9849 | -121.7331 | 0.19684 | -0.0051118 | -0.012448 | -0.080719 | -0.0054837 | -0.025316 | -0.048672 | -0.039324 | -0.0082091 | -0.019254 | 0.011125 | -0.020815 | -0.21979 | -0.016846 | -0.025816 | -0.086975 | 0.1236 | -0.14648 | -0.10529 | 0.041199 | -0.10071 | -0.050354 | -0.07782 | 0.22888 | -0.17853 | 0.10071 | 0.064087 | 0.013733 | 0.086975 | 121.5866 | -0.073242 | -0.30212 | 121.7743 | 121.6827 | 121.6324 | 0.09613 | 0.045776 | 121.5546 | 0.032044 | -0.09613 | 121.7972 | 121.8201 | 121.7468 | 0.2655 | 0.19226 | 0.18768 | 0.041198 | 0.24261 | 0.27924 | 0.27008 | 0.40741 | 121.8567 | 121.962 | -0.34332 | -0.37537 | 121.6278 | 121.8338 | 121.6461 | 121.6553
2879.6406 | 122.1085 | -121.6873 | 0.17395 | -0.0051118 | -0.014157 | -0.079011 | -0.0074063 | -0.033007 | -0.051022 | -0.04146 | 0.0039979 | -0.021176 | 0.0070666 | -0.024233 | -0.21744 | -0.019196 | -0.024748 | -0.064087 | 0.073242 | -0.10529 | -0.009155 | 0.1831 | -0.018311 | 0.059509 | 0.045776 | 0.18768 | -0.14648 | 0.19226 | 0.17395 | 0.15106 | 0.15564 | 121.582 | -0.10071 | -0.1831 | 121.8704 | 121.7468 | 121.669 | 0.16479 | 0.086975 | 121.5408 | 0.013733 | 0.018311 | 121.8613 | 121.843 | 121.8384 | 0.30212 | 0.29755 | 0.28839 | 0.096131 | 0.32043 | 0.33874 | 0.17853 | 0.33417 | 121.7606 | 121.875 | -0.27924 | -0.32043 | 121.6782 | 121.8796 | 121.6232 | 121.7331
2881.3594 | 122.0352 | -121.7056 | 0.20599 | -0.012741 | -0.012875 | -0.080506 | -0.0063381 | -0.030871 | -0.051663 | -0.040605 | -0.0051575 | -0.023099 | 0.0066394 | -0.021029 | -0.21915 | -0.017914 | -0.022185 | -0.10986 | 0.10529 | -0.11902 | -0.086975 | 0.073242 | -0.086975 | -0.004578 | -0.068665 | 0.19684 | -0.15106 | 0.11902 | 0.086975 | 0.054932 | 0.10071 | 121.5866 | -0.10071 | -0.29297 | 121.7789 | 121.701 | 121.6187 | 0.11444 | 0.032044 | 121.5546 | -0.009156 | -0.086975 | 121.7926 | 121.8063 | 121.7606 | 0.25177 | 0.20599 | 0.19226 | 0.032044 | 0.23804 | 0.27008 | 0.22431 | 0.3479 | 121.8109 | 121.9025 | -0.32501 | -0.35706 | 121.6187 | 121.8246 | 121.5958 | 121.637
2883.1406 | 122.0306 | -121.7285 | 0.17853 | -0.0051118 | -0.010311 | -0.080292 | -0.0052701 | -0.027239 | -0.049099 | -0.041674 | 0.00094606 | -0.019681 | 0.010271 | -0.019747 | -0.21915 | -0.01706 | -0.024535 | -0.1236 | 0.10529 | -0.13275 | -0.14648 | 0.009155 | -0.16022 | -0.064087 | -0.082397 | 0.2243 | -0.15106 | 0.1236 | 0.059509 | 0.036621 | 0.10071 | 121.5958 | -0.073242 | -0.32501 | 121.7377 | 121.6644 | 121.5683 | 0.068664 | -0.027466 | 121.5775 | 0.045776 | -0.054932 | 121.788 | 121.8292 | 121.7651 | 0.25177 | 0.18768 | 0.14191 | -0.013733 | 0.21057 | 0.27466 | 0.23804 | 0.37537 | 121.8338 | 121.9528 | -0.31128 | -0.32959 | 121.582 | 121.8521 | 121.6049 | 121.6461
2884.875 | 122.0306 | -121.7331 | 0.20142 | 0.0025177 | -0.01202 | -0.080079 | -0.0067653 | -0.033861 | -0.049313 | -0.038469 | -0.0021057 | -0.01904 | 0.011125 | -0.016757 | -0.22065 | -0.015778 | -0.020689 | -0.091553 | 0.1236 | -0.13733 | -0.1236 | 0.022888 | -0.11444 | -0.050354 | -0.086975 | 0.24261 | -0.16937 | 0.10529 | 0.068665 | 0.018311 | 0.068665 | 121.5958 | -0.07782 | -0.32501 | 121.756 | 121.6827 | 121.6187 | 0.086975 | 0.022888 | 121.5637 | 0.041199 | -0.09613 | 121.8018 | 121.8018 | 121.7514 | 0.23804 | 0.18768 | 0.16022 | 0.013733 | 0.23804 | 0.27466 | 0.26093 | 0.41199 | 121.8567 | 121.9757 | -0.33875 | -0.37079 | 121.6095 | 121.8384 | 121.6415 | 121.6461
2886.6719 | 121.9711 | -121.7789 | 0.21057 | 0.0025177 | -0.016507 | -0.080933 | -0.0061245 | -0.03258 | -0.052944 | -0.039324 | 0.00094606 | -0.021176 | 0.0083484 | -0.021456 | -0.21915 | -0.016846 | -0.022826 | -0.14191 | 0.1236 | -0.14648 | -0.15106 | 0 | -0.13733 | -0.064087 | -0.15564 | 0.24261 | -0.16479 | 0.045776 | 0.004578 | -0.009155 | 0.022888 | 121.6324 | -0.086975 | -0.36163 | 121.7789 | 121.7148 | 121.6415 | 0.082397 | 0.009155 | 121.6141 | 0.032044 | -0.1648 | 121.7834 | 121.8018 | 121.7697 | 0.18768 | 0.15564 | 0.14648 | -0.004578 | 0.16937 | 0.21057 | 0.27008 | 0.40741 | 121.9025 | 122.0215 | -0.35706 | -0.37537 | 121.6278 | 121.8246 | 121.637 | 121.6232
2888.4688 | 121.994 | -121.7468 | 0.20599 | -0.0051118 | -0.012234 | -0.079438 | -0.0044155 | -0.029589 | -0.051876 | -0.042101 | 0.00094606 | -0.020108 | 0.0081348 | -0.020602 | -0.21979 | -0.01706 | -0.021758 | -0.1236 | 0.11444 | -0.14191 | -0.14648 | -0.009155 | -0.14648 | -0.073242 | -0.14191 | 0.24261 | -0.17853 | 0.068665 | 0.032043 | 0 | 0.050354 | 121.6049 | -0.091553 | -0.35248 | 121.7377 | 121.6736 | 121.6003 | 0.068665 | -0.004577 | 121.5683 | 0.036621 | -0.13733 | 121.7789 | 121.7972 | 121.7468 | 0.22888 | 0.17853 | 0.13275 | -0.004577 | 0.21057 | 0.24719 | 0.25635 | 0.42114 | 121.8613 | 121.9894 | -0.3479 | -0.38452 | 121.6003 | 121.8155 | 121.6232 | 121.6049
2890.2656 | 122.0032 | -121.7834 | 0.21515 | 0.010147 | -0.015866 | -0.080292 | -0.0063381 | -0.030443 | -0.050595 | -0.042742 | 0.00094606 | -0.021604 | 0.0083484 | -0.01697 | -0.21937 | -0.017487 | -0.026671 | -0.064087 | 0.086975 | -0.11902 | -0.10071 | 0.050354 | -0.09613 | -0.032043 | -0.09613 | 0.24261 | -0.15564 | 0.050354 | 0.027466 | 0.004578 | 0.032043 | 121.6644 | -0.12817 | -0.31586 | 121.8338 | 121.7514 | 121.6873 | 0.086976 | 0.022889 | 121.6278 | 0.027466 | -0.16479 | 121.8109 | 121.8155 | 121.788 | 0.18768 | 0.16022 | 0.16937 | 0.018311 | 0.18311 | 0.20599 | 0.20599 | 0.39826 | 121.8704 | 122.0261 | -0.33417 | -0.37079 | 121.6827 | 121.8338 | 121.7194 | 121.6873
2891.9844 | 122.1268 | -121.7285 | 0.19226 | 0.0025177 | -0.014157 | -0.078797 | -0.0080471 | -0.029802 | -0.052304 | -0.039965 | 0.00094606 | -0.021176 | 0.0072802 | -0.027224 | -0.21872 | -0.01941 | -0.024748 | -0.054932 | 0.07782 | -0.1236 | -0.009155 | 0.16022 | 0 | 0.054932 | 0.027466 | 0.19226 | -0.14191 | 0.16479 | 0.17853 | 0.14191 | 0.16022 | 121.6049 | -0.11444 | -0.20142 | 121.8887 | 121.7834 | 121.7285 | 0.17853 | 0.1236 | 121.5866 | 0 | -0.027466 | 121.907 | 121.8887 | 121.8704 | 0.30212 | 0.28381 | 0.28381 | 0.11444 | 0.32044 | 0.3067 | 0.20142 | 0.33417 | 121.8063 | 121.9208 | -0.31586 | -0.33417 | 121.7194 | 121.8933 | 121.6736 | 121.756
2893.7812 | 122.0947 | -121.7606 | 0.19226 | -0.0051118 | -0.015011 | -0.082001 | -0.0076199 | -0.031725 | -0.049954 | -0.041246 | 0.00094606 | -0.021817 | 0.0094166 | -0.019747 | -0.22043 | -0.017487 | -0.02133 | -0.064087 | 0.082397 | -0.09613 | -0.032043 | 0.11902 | -0.018311 | 0.041199 | -0.009155 | 0.18768 | -0.13275 | 0.14191 | 0.1236 | 0.10071 | 0.12817 | 121.6644 | -0.10986 | -0.2243 | 121.8796 | 121.8018 | 121.7422 | 0.13733 | 0.077819 | 121.6278 | -0.004578 | -0.050354 | 121.8842 | 121.8887 | 121.8613 | 0.26093 | 0.23346 | 0.21515 | 0.064087 | 0.25635 | 0.27466 | 0.17853 | 0.32043 | 121.843 | 121.9482 | -0.28839 | -0.32501 | 121.7285 | 121.9025 | 121.6965 | 121.7514
2895.5781 | 122.0718 | -121.7514 | 0.19226 | 0.0025177 | -0.012661 | -0.076661 | -0.0031337 | -0.029589 | -0.051449 | -0.041033 | -0.0021057 | -0.020963 | 0.0092028 | -0.018679 | -0.22236 | -0.016846 | -0.025603 | -0.11444 | 0.12817 | -0.12817 | -0.12817 | 0 | -0.16022 | -0.073242 | -0.07782 | 0.23804 | -0.16022 | 0.11902 | 0.041199 | 0.018311 | 0.086975 | 121.6232 | -0.064087 | -0.32044 | 121.7514 | 121.6782 | 121.5912 | 0.054932 | -0.032043 | 121.5912 | 0.045776 | -0.073242 | 121.7926 | 121.8384 | 121.7697 | 0.24719 | 0.17853 | 0.12817 | 0 | 0.20142 | 0.27924 | 0.25635 | 0.39825 | 121.8796 | 121.9894 | -0.32044 | -0.35248 | 121.6232 | 121.8704 | 121.637 | 121.6736
2897.3594 | 122.0215 | -121.8018 | 0.21515 | 0.0025177 | -0.01138 | -0.07837 | -0.0046291 | -0.029589 | -0.049313 | -0.039324 | -0.0051575 | -0.019254 | 0.0066394 | -0.016116 | -0.22001 | -0.016419 | -0.024535 | -0.10071 | 0.11444 | -0.1236 | -0.10986 | 0.004578 | -0.16479 | -0.086975 | -0.11902 | 0.21973 | -0.16479 | 0.068665 | -0.013733 | -0.045776 | 0.032043 | 121.6782 | -0.10071 | -0.32501 | 121.8063 | 121.7148 | 121.637 | 0.036621 | -0.041199 | 121.637 | 0.004578 | -0.14648 | 121.788 | 121.8338 | 121.756 | 0.19684 | 0.11902 | 0.12817 | 0.013733 | 0.15106 | 0.23346 | 0.23804 | 0.38452 | 121.9162 | 122.0215 | -0.33875 | -0.37994 | 121.6919 | 121.8704 | 121.7011 | 121.6827
2899.0781 | 122.0169 | -121.8063 | 0.2243 | -0.012741 | -0.0096707 | -0.079651 | -0.0046291 | -0.030871 | -0.051235 | -0.039751 | -0.0051575 | -0.017758 | 0.007494 | -0.018679 | -0.21915 | -0.017487 | -0.024748 | -0.086975 | 0.12817 | -0.10529 | -0.15106 | 0 | -0.18768 | -0.091553 | -0.13733 | 0.23346 | -0.16937 | 0.064087 | 0 | -0.050354 | 0.032043 | 121.701 | -0.09613 | -0.37537 | 121.8063 | 121.7148 | 121.6187 | 0.013733 | -0.082397 | 121.637 | 0.009155 | -0.16022 | 121.8063 | 121.8384 | 121.756 | 0.20142 | 0.11902 | 0.10529 | -0.045776 | 0.16937 | 0.23346 | 0.23346 | 0.40283 | 121.9345 | 122.0398 | -0.32959 | -0.39368 | 121.6553 | 121.8704 | 121.7194 | 121.669
2900.8906 | 122.0993 | -121.8246 | 0.17853 | 0.0025177 | -0.01202 | -0.077942 | -0.0052701 | -0.02788 | -0.049526 | -0.042528 | -0.0021057 | -0.018186 | 0.0070666 | -0.018893 | -0.21979 | -0.016419 | -0.022398 | -0.11902 | 0.11444 | -0.14191 | -0.15106 | -0.009155 | -0.17395 | -0.07782 | -0.10986 | 0.20142 | -0.16937 | 0.073242 | 0.045776 | 0.004578 | 0.082397 | 121.6827 | -0.064087 | -0.32959 | 121.8155 | 121.7468 | 121.6507 | 0.064087 | -0.032043 | 121.6553 | 0.022888 | -0.10529 | 121.8704 | 121.907 | 121.8292 | 0.25177 | 0.17395 | 0.13275 | -0.009155 | 0.21515 | 0.24261 | 0.25635 | 0.37079 | 121.9391 | 122.0261 | -0.32044 | -0.3479 | 121.6736 | 121.8979 | 121.7056 | 121.7148
2902.6875 | 122.0673 | -121.8521 | 0.17395 | 0.010147 | -0.011807 | -0.078583 | -0.0076199 | -0.029375 | -0.050381 | -0.041887 | -0.0021057 | -0.01904 | 0.011553 | -0.020175 | -0.21808 | -0.01706 | -0.02603 | -0.073242 | 0.12817 | -0.13275 | -0.10529 | 0.059509 | -0.10986 | -0.036621 | -0.068665 | 0.16937 | -0.16022 | 0.045776 | 0.041199 | 0.013733 | 0.064087 | 121.7194 | -0.045776 | -0.27924 | 121.9116 | 121.8155 | 121.7422 | 0.09613 | 0.022888 | 121.6919 | -0.004577 | -0.12817 | 121.8933 | 121.9162 | 121.8658 | 0.2243 | 0.17395 | 0.19226 | 0.027465 | 0.20142 | 0.20599 | 0.26093 | 0.32959 | 121.9803 | 122.0215 | -0.3067 | -0.33417 | 121.7468 | 121.8979 | 121.7789 | 121.7834
2904.4844 | 122.0627 | -121.8842 | 0.16479 | 0.010147 | -0.013729 | -0.079438 | -0.0071927 | -0.03322 | -0.052944 | -0.044451 | -0.0021057 | -0.019681 | 0.0070666 | -0.022311 | -0.2183 | -0.017701 | -0.023894 | -0.11444 | 0.10071 | -0.13275 | -0.12817 | 0.027466 | -0.10986 | -0.050354 | -0.11902 | 0.1831 | -0.1831 | 0.009155 | 0.032043 | -0.009155 | 0.027466 | 121.7514 | -0.064087 | -0.29297 | 121.9116 | 121.8338 | 121.7743 | 0.082397 | 0.022888 | 121.7011 | 0.01831 | -0.15564 | 121.9162 | 121.9116 | 121.875 | 0.21057 | 0.17395 | 0.16022 | 0.004577 | 0.21515 | 0.19226 | 0.23346 | 0.36621 | 121.9849 | 122.0673 | -0.29755 | -0.3479 | 121.756 | 121.8933 | 121.7697 | 121.7651
2906.2188 | 122.1863 | -121.8567 | 0.14191 | -0.0051118 | -0.015652 | -0.08136 | -0.0078335 | -0.029802 | -0.051022 | -0.042528 | 0.00094606 | -0.021176 | 0.0077076 | -0.019961 | -0.21958 | -0.020051 | -0.022398 | -0.082397 | 0.091553 | -0.09613 | -0.073242 | 0.091553 | -0.050354 | 0.027466 | -0.022888 | 0.14191 | -0.12817 | 0.10986 | 0.16022 | 0.12817 | 0.16022 | 121.7606 | -0.050354 | -0.21515 | 121.9482 | 121.8842 | 121.8063 | 0.1236 | 0.045776 | 121.7285 | 0 | -0.032044 | 122.0169 | 122.0169 | 121.9849 | 0.28839 | 0.25635 | 0.18768 | 0.022888 | 0.28839 | 0.23804 | 0.18768 | 0.27008 | 121.9482 | 121.9986 | -0.23804 | -0.27008 | 121.7834 | 121.9666 | 121.7743 | 121.8338
2908.0156 | 122.0856 | -121.8887 | 0.15564 | -0.0051118 | -0.0090299 | -0.079224 | -0.0033475 | -0.028734 | -0.047604 | -0.042955 | -0.0051575 | -0.019254 | 0.0087756 | -0.005221 | -0.21958 | -0.015137 | -0.021758 | -0.11902 | 0.13733 | -0.15564 | -0.16022 | -0.018311 | -0.20142 | -0.07782 | -0.15106 | 0.16479 | -0.16022 | 0.032043 | 0.004578 | -0.027466 | 0.045776 | 121.7331 | -0.018311 | -0.31586 | 121.8704 | 121.8109 | 121.6873 | 0.07782 | -0.045776 | 121.7285 | 0.009155 | -0.1236 | 121.8933 | 121.9345 | 121.8613 | 0.20599 | 0.13275 | 0.13733 | -0.004577 | 0.16479 | 0.19226 | 0.29297 | 0.32501 | 122.0261 | 122.0535 | -0.31128 | -0.31586 | 121.7285 | 121.9208 | 121.7697 | 121.7377
2909.8125 | 122.2 | -121.8887 | 0.14191 | -0.0051118 | -0.01437 | -0.07837 | -0.0065517 | -0.031939 | -0.051876 | -0.040605 | -0.0051575 | -0.021604 | 0.007494 | -0.017184 | -0.21979 | -0.01941 | -0.028166 | -0.054932 | 0.07782 | -0.10986 | -0.004578 | 0.17395 | -0.004578 | 0.054932 | 0.022888 | 0.13275 | -0.12817 | 0.13275 | 0.16479 | 0.13733 | 0.16937 | 121.7789 | -0.064087 | -0.14649 | 122.0627 | 121.9437 | 121.8842 | 0.16479 | 0.10529 | 121.7606 | -0.009156 | -0.009156 | 122.0535 | 122.0581 | 122.0261 | 0.29755 | 0.2655 | 0.28381 | 0.10529 | 0.29297 | 0.26093 | 0.18768 | 0.26093 | 121.9666 | 122.0215 | -0.25177 | -0.27008 | 121.8842 | 122.0215 | 121.8338 | 121.9116
2911.5312 | 122.081 | -121.8979 | 0.17853 | 0.0025177 | -0.014584 | -0.079438 | -0.0054837 | -0.027666 | -0.054653 | -0.039324 | 0.00094606 | -0.022031 | 0.0081348 | -0.019534 | -0.21894 | -0.018982 | -0.022398 | -0.10986 | 0.091553 | -0.11902 | -0.14648 | 0.004578 | -0.15106 | -0.041199 | -0.086975 | 0.19226 | -0.16937 | -0.004578 | 0.041199 | -0.009155 | 0.032043 | 121.7789 | -0.086975 | -0.32501 | 121.9025 | 121.8567 | 121.7468 | 0.07782 | -0.032043 | 121.7285 | 0.013733 | -0.18311 | 121.9391 | 121.9299 | 121.8887 | 0.20142 | 0.16022 | 0.1236 | -0.027465 | 0.21057 | 0.16479 | 0.21057 | 0.36163 | 121.9894 | 122.0901 | -0.29755 | -0.3479 | 121.7514 | 121.8933 | 121.788 | 121.8109
2913.3281 | 122.1954 | -121.8567 | 0.13733 | -0.0051118 | -0.01437 | -0.082642 | -0.0091153 | -0.03322 | -0.048245 | -0.042101 | 0.0039979 | -0.022458 | 0.0081348 | -0.022952 | -0.22129 | -0.018769 | -0.025389 | -0.054932 | 0.073242 | -0.10529 | -0.022888 | 0.15106 | -0.013733 | 0.045776 | 0.086975 | 0.14191 | -0.13733 | 0.12817 | 0.19226 | 0.15564 | 0.15564 | 121.7514 | -0.064087 | -0.16022 | 122.0078 | 121.9025 | 121.843 | 0.15106 | 0.091553 | 121.7194 | 0.004578 | -0.009155 | 122.049 | 122.0123 | 122.0123 | 0.29297 | 0.29297 | 0.25635 | 0.082398 | 0.32959 | 0.2655 | 0.17853 | 0.27924 | 121.9299 | 121.9986 | -0.24262 | -0.27466 | 121.8338 | 121.9849 | 121.8018 | 121.9437
2915.125 | 122.0718 | -121.9025 | 0.18768 | 0.010147 | -0.014157 | -0.079438 | -0.0046291 | -0.026812 | -0.050381 | -0.042101 | -0.0051575 | -0.019895 | 0.0066394 | -0.023379 | -0.22043 | -0.016846 | -0.02133 | -0.11444 | 0.10529 | -0.12817 | -0.14648 | 0.004578 | -0.14648 | -0.054932 | -0.07782 | 0.18768 | -0.16022 | -0.009155 | 0.022888 | -0.009155 | 0.027466 | 121.7743 | -0.082397 | -0.33417 | 121.907 | 121.8475 | 121.756 | 0.073242 | -0.01831 | 121.7422 | 0 | -0.19684 | 121.9254 | 121.9299 | 121.8933 | 0.18768 | 0.15106 | 0.13275 | -0.01831 | 0.1831 | 0.15106 | 0.23346 | 0.3479 | 122.0078 | 122.0901 | -0.31586 | -0.3479 | 121.756 | 121.8933 | 121.788 | 121.8246
2916.9219 | 122.1313 | -121.9299 | 0.13733 | 0.0025177 | -0.0098843 | -0.080292 | -0.0031337 | -0.030871 | -0.051022 | -0.043596 | -0.0021057 | -0.019254 | 0.0062122 | -0.016543 | -0.22043 | -0.016419 | -0.02368 | -0.10986 | 0.1236 | -0.14648 | -0.16479 | -0.032043 | -0.19226 | -0.086975 | -0.045776 | 0.13733 | -0.16937 | 0.013733 | 0.059509 | -0.018311 | 0.050354 | 121.7834 | -0.013733 | -0.30212 | 121.8979 | 121.843 | 121.7377 | 0.059509 | -0.045777 | 121.7606 | 0 | -0.1236 | 121.9894 | 121.9803 | 121.9116 | 0.21973 | 0.15106 | 0.11444 | -0.018311 | 0.22888 | 0.18311 | 0.27008 | 0.3067 | 122.0535 | 122.0673 | -0.28381 | -0.3067 | 121.7651 | 121.9437 | 121.8201 | 121.8842
2918.7188 | 122.1909 | -121.9482 | 0.10071 | 0.0025177 | -0.012661 | -0.078583 | -0.0061245 | -0.030016 | -0.049954 | -0.042955 | 0.00094606 | -0.02139 | 0.0089892 | -0.023806 | -0.21937 | -0.01941 | -0.023894 | -0.07782 | 0.064087 | -0.091553 | -0.050354 | 0.10986 | -0.07782 | -0.004578 | 0.068665 | 0.1236 | -0.15106 | 0.059509 | 0.15564 | 0.082397 | 0.13733 | 121.8567 | -0.036621 | -0.15106 | 122.0581 | 121.9437 | 121.8704 | 0.086975 | 0.013733 | 121.7972 | 0.022888 | -0.041199 | 122.1039 | 122.0856 | 122.0306 | 0.28839 | 0.23346 | 0.20142 | 0.041199 | 0.3067 | 0.21057 | 0.15564 | 0.27466 | 122.0123 | 122.0718 | -0.19226 | -0.25177 | 121.8979 | 122.0078 | 121.8704 | 122.0169
2920.4531 | 122.168 | -121.9528 | 0.13275 | -0.012741 | -0.010739 | -0.078156 | -0.0037747 | -0.028948 | -0.050381 | -0.042742 | 0.00094606 | -0.016904 | 0.008562 | -0.015048 | -0.22129 | -0.017701 | -0.019194 | -0.09613 | 0.10071 | -0.14191 | -0.11444 | 0.022888 | -0.09613 | -0.050354 | 0.013733 | 0.13733 | -0.16022 | 0.027466 | 0.10529 | 0.018311 | 0.086975 | 121.8109 | -0.032043 | -0.24719 | 121.9757 | 121.9025 | 121.8567 | 0.091553 | 0.045777 | 121.7926 | 0.004578 | -0.10529 | 122.0581 | 122.0398 | 121.9711 | 0.24719 | 0.17853 | 0.16479 | 0.027466 | 0.2655 | 0.18768 | 0.24262 | 0.29755 | 122.0535 | 122.0901 | -0.27466 | -0.29297 | 121.8384 | 121.9803 | 121.8567 | 121.9666
2922.2344 | 122.2366 | -121.962 | 0.09613 | 0.0025177 | -0.011593 | -0.080719 | -0.0048427 | -0.025744 | -0.050595 | -0.039324 | 0.00094606 | -0.019254 | 0.0079212 | -0.017397 | -0.22172 | -0.013856 | -0.024107 | -0.10529 | 0.10071 | -0.13275 | -0.082397 | 0.059509 | -0.11902 | -0.013733 | 0.050354 | 0.12817 | -0.14648 | 0.09613 | 0.15564 | 0.082397 | 0.15106 | 121.8292 | 0.004578 | -0.17853 | 122.0215 | 121.9482 | 121.843 | 0.11902 | 0.013732 | 121.8155 | 0.032044 | 0 | 122.1176 | 122.113 | 122.0444 | 0.29755 | 0.22888 | 0.19226 | 0.050354 | 0.30212 | 0.24261 | 0.23346 | 0.27466 | 122.0627 | 122.0901 | -0.22888 | -0.24261 | 121.8796 | 122.0581 | 121.8567 | 122.0123
2924.0469 | 122.2 | -121.9803 | 0.14191 | -0.0051118 | -0.012234 | -0.079865 | -0.0059109 | -0.03258 | -0.048245 | -0.041033 | 0.00094606 | -0.020536 | 0.0083484 | -0.018252 | -0.21937 | -0.015565 | -0.024748 | -0.068665 | 0.086975 | -0.09613 | -0.036621 | 0.12817 | -0.027466 | 0.032043 | 0.050354 | 0.12817 | -0.14191 | 0.036621 | 0.13733 | 0.07782 | 0.11444 | 121.8842 | -0.054932 | -0.17853 | 122.1085 | 122.0123 | 121.9528 | 0.12817 | 0.068664 | 121.8384 | -0.013733 | -0.10529 | 122.1176 | 122.0947 | 122.0581 | 0.25635 | 0.21973 | 0.2243 | 0.059509 | 0.27924 | 0.17853 | 0.1831 | 0.27008 | 122.0673 | 122.1085 | -0.23804 | -0.28381 | 121.9437 | 122.0169 | 121.9116 | 122.0306
2925.8438 | 122.1451 | -122.0078 | 0.12817 | 0.0025177 | -0.0094571 | -0.079011 | -0.0031337 | -0.030657 | -0.050595 | -0.041246 | 0.00094606 | -0.017972 | 0.0089892 | -0.012698 | -0.22107 | -0.016419 | -0.026244 | -0.10529 | 0.10986 | -0.13275 | -0.16937 | -0.054932 | -0.20599 | -0.10986 | -0.064087 | 0.15564 | -0.15564 | -0.018311 | 0.032043 | -0.059509 | 0.036621 | 121.875 | -0.018311 | -0.29755 | 121.9528 | 121.8979 | 121.8018 | 0.022888 | -0.073243 | 121.8521 | 0.027466 | -0.14649 | 122.0398 | 122.0444 | 121.9482 | 0.19226 | 0.096131 | 0.077819 | -0.036622 | 0.18768 | 0.13733 | 0.24261 | 0.31128 | 122.1176 | 122.1634 | -0.26093 | -0.28381 | 121.8384 | 121.9894 | 121.9025 | 121.9437
2927.6406 | 122.2183 | -122.0078 | 0.12817 | -0.0051118 | -0.013302 | -0.07837 | -0.0052701 | -0.027666 | -0.050167 | -0.038042 | -0.0021057 | -0.01904 | 0.0089892 | -0.020175 | -0.2215 | -0.017701 | -0.020689 | -0.068665 | 0.10986 | -0.11444 | -0.091553 | 0.050354 | -0.10986 | -0.036621 | 0.041199 | 0.14191 | -0.13733 | 0.036621 | 0.10529 | 0.022888 | 0.091553 | 121.8933 | -0.018311 | -0.21973 | 122.0581 | 121.9711 | 121.8979 | 0.07782 | 0.004578 | 121.8704 | 0.013733 | -0.091553 | 122.113 | 122.0993 | 122.0306 | 0.22888 | 0.16022 | 0.16479 | 0.022888 | 0.24262 | 0.17395 | 0.2243 | 0.27924 | 122.1176 | 122.1497 | -0.24262 | -0.2655 | 121.9162 | 122.0444 | 121.9391 | 122.049
2929.3594 | 122.3007 | -121.9757 | 0.091553 | -0.0051118 | -0.016293 | -0.080719 | -0.0069791 | -0.030443 | -0.052944 | -0.038683 | 0.00094606 | -0.022885 | 0.0081348 | -0.021456 | -0.21915 | -0.018128 | -0.021758 | -0.064087 | 0.082397 | -0.10986 | -0.022888 | 0.17853 | 0.013733 | 0.07782 | 0.11444 | 0.11902 | -0.12817 | 0.091553 | 0.21973 | 0.14191 | 0.16937 | 121.8658 | -0.009156 | -0.11444 | 122.1542 | 122.0535 | 121.9894 | 0.18768 | 0.1236 | 121.8475 | 0.027466 | 0 | 122.1954 | 122.1451 | 122.1176 | 0.29755 | 0.27008 | 0.28839 | 0.086975 | 0.3479 | 0.21973 | 0.19226 | 0.24719 | 122.0581 | 122.0947 | -0.20142 | -0.21973 | 121.9528 | 122.0673 | 121.9116 | 122.0901
2931.1562 | 122.3145 | -121.9803 | 0.10986 | 0.0025177 | -0.015866 | -0.080079 | -0.0082607 | -0.035143 | -0.050167 | -0.042955 | 0.00094606 | -0.022885 | 0.0079212 | -0.025301 | -0.22065 | -0.018342 | -0.023894 | -0.068665 | 0.086975 | -0.073242 | -0.018311 | 0.14648 | -0.009155 | 0.059509 | 0.1236 | 0.11902 | -0.1236 | 0.10986 | 0.22888 | 0.16022 | 0.16937 | 121.907 | -0.022888 | -0.12817 | 122.1268 | 122.0398 | 121.9711 | 0.13275 | 0.064087 | 121.8567 | 0.009156 | 0 | 122.2092 | 122.1497 | 122.1405 | 0.29297 | 0.28381 | 0.21973 | 0.054931 | 0.35248 | 0.23346 | 0.16022 | 0.24261 | 122.0673 | 122.0993 | -0.18311 | -0.23346 | 121.962 | 122.0901 | 121.9116 | 122.1039
2932.9531 | 122.1725 | -122.0306 | 0.15106 | 0.0025177 | -0.013302 | -0.079865 | -0.0082607 | -0.029589 | -0.050381 | -0.040605 | -0.0021057 | -0.020108 | 0.0064258 | -0.022738 | -0.21872 | -0.015565 | -0.023894 | -0.13733 | 0.12817 | -0.13733 | -0.15564 | 0 | -0.13733 | -0.059509 | -0.064087 | 0.16022 | -0.17395 | -0.027466 | 0.064087 | -0.004578 | 0.018311 | 121.8933 | -0.022888 | -0.3067 | 122.0306 | 121.9711 | 121.8933 | 0.07782 | 0 | 121.8567 | 0.009155 | -0.17853 | 122.0947 | 122.049 | 122.0261 | 0.19226 | 0.16937 | 0.13733 | -0.018311 | 0.23804 | 0.14648 | 0.2655 | 0.33417 | 122.1588 | 122.1909 | -0.28839 | -0.32501 | 121.875 | 122.0032 | 121.8933 | 121.9666
2934.7344 | 122.2733 | -122.0032 | 0.13733 | 0.010147 | -0.013302 | -0.079865 | -0.0091153 | -0.029589 | -0.052517 | -0.041674 | 0.00094606 | -0.021604 | 0.0062122 | -0.024233 | -0.22129 | -0.017487 | -0.022185 | -0.054932 | 0.07782 | -0.091553 | -0.027466 | 0.12817 | -0.013733 | 0.027466 | 0.07782 | 0.1236 | -0.12817 | 0.073242 | 0.1831 | 0.10986 | 0.13275 | 121.9116 | -0.059509 | -0.16479 | 122.1313 | 122.0306 | 121.9894 | 0.11902 | 0.07782 | 121.875 | -0.013733 | -0.064087 | 122.1863 | 122.1359 | 122.113 | 0.26093 | 0.23804 | 0.21973 | 0.064087 | 0.31128 | 0.20142 | 0.16937 | 0.25177 | 122.081 | 122.1268 | -0.22888 | -0.2655 | 121.9757 | 122.0764 | 121.9482 | 122.081
2936.4688 | 122.2916 | -121.962 | 0.12817 | 0.010147 | -0.0098843 | -0.078583 | -0.0035611 | -0.03322 | -0.048031 | -0.041674 | -0.0051575 | -0.020963 | 0.0098438 | -0.019106 | -0.22001 | -0.016846 | -0.027312 | -0.082397 | 0.09613 | -0.09613 | -0.064087 | 0.082397 | -0.10986 | 0 | 0.064087 | 0.13275 | -0.14648 | 0.11902 | 0.17395 | 0.082397 | 0.16479 | 121.8658 | -0.032044 | -0.19226 | 122.0444 | 121.962 | 121.8521 | 0.09613 | -0.013733 | 121.8155 | 0.004577 | -0.009155 | 122.1359 | 122.1268 | 122.0444 | 0.31128 | 0.22888 | 0.17853 | 0.032043 | 0.32043 | 0.2655 | 0.19226 | 0.27924 | 122.0581 | 122.0947 | -0.2243 | -0.27466 | 121.8979 | 122.081 | 121.8796 | 122.0261
2938.25 | 122.2504 | -121.9711 | 0.16022 | -0.0051118 | -0.011593 | -0.079438 | -0.0048427 | -0.028521 | -0.050167 | -0.042101 | -0.0021057 | -0.019681 | 0.008562 | -0.018038 | -0.22022 | -0.016633 | -0.027098 | -0.11902 | 0.12817 | -0.12817 | -0.14191 | -0.004578 | -0.16937 | -0.073242 | 0 | 0.16022 | -0.16479 | 0.086975 | 0.11444 | 0.032043 | 0.09613 | 121.843 | -0.032043 | -0.30212 | 121.9666 | 121.8979 | 121.8018 | 0.054932 | -0.041199 | 121.8063 | 0 | -0.073242 | 122.0856 | 122.0673 | 122.0032 | 0.26092 | 0.19684 | 0.1236 | -0.013733 | 0.27924 | 0.25177 | 0.25635 | 0.32501 | 122.0993 | 122.1313 | -0.28839 | -0.32501 | 121.8292 | 122.0581 | 121.8521 | 121.9711
2940.0469 | 121.8887 | -120.5383 | 1.3229 | -0.012741 | -0.014584 | -0.082001 | -0.0042019 | -0.028948 | -0.050595 | -0.040605 | -0.0021057 | -0.020108 | 0.0059986 | -0.01697 | -0.21915 | -0.018128 | -0.022185 | -0.045776 | 0.18768 | -0.068665 | -0.064087 | 0.07782 | -0.054932 | 0.004578 | 0.23804 | 1.3687 | -0.16937 | 1.181 | 0.20142 | 0.041199 | 0.045776 | 120.4697 | -1.1353 | -1.387 | 120.6162 | 120.5429 | 120.4834 | 0.073243 | 0.013733 | 120.369 | 0.045776 | -0.14191 | 120.7397 | 120.5841 | 120.5795 | 0.21515 | 0.21057 | 0.14649 | 0.004578 | 0.37079 | 1.3504 | 0.25635 | 1.5381 | 120.726 | 121.907 | -1.3916 | -1.4923 | 120.4742 | 121.7194 | 120.4926 | 120.7764
2941.8438 | 122.0901 | -121.7834 | 0.09613 | -0.012741 | -0.0092435 | -0.079011 | -0.0078335 | -0.031511 | -0.049313 | -0.040178 | -0.0021057 | -0.020108 | 0.0083484 | -0.023379 | -0.21894 | -0.017487 | -0.029021 | -0.036621 | 0.073242 | -0.086975 | -0.018311 | 0.13733 | -0.050354 | 0.013733 | 0.10986 | 0.10529 | -0.1236 | 0.10071 | 0.1831 | 0.10986 | 0.16937 | 121.6965 | -0.022888 | -0.11444 | 121.9208 | 121.7972 | 121.7331 | 0.10071 | 0.036621 | 121.6599 | 0.009156 | 0.004578 | 121.9666 | 121.9528 | 121.8933 | 0.29297 | 0.23346 | 0.2243 | 0.068664 | 0.3067 | 0.2243 | 0.16022 | 0.22888 | 121.8567 | 121.8887 | -0.1831 | -0.21973 | 121.7651 | 121.8842 | 121.7468 | 121.8933
2943.6406 | 122.1954 | -121.8979 | 0.086975 | -0.0051118 | -0.012448 | -0.080933 | -0.0071927 | -0.033434 | -0.049954 | -0.040819 | 0.00094606 | -0.021604 | 0.0096302 | -0.024874 | -0.22043 | -0.017914 | -0.023467 | -0.091553 | 0.091553 | -0.11902 | -0.059509 | 0.11444 | -0.045776 | 0.032043 | 0.064087 | 0.10529 | -0.14191 | 0.073242 | 0.20142 | 0.15106 | 0.17395 | 121.7789 | 0.004578 | -0.14648 | 122.0123 | 121.9299 | 121.8521 | 0.15106 | 0.073243 | 121.756 | 0.018311 | -0.013733 | 122.0993 | 122.0718 | 122.0489 | 0.31586 | 0.29297 | 0.23346 | 0.05951 | 0.34332 | 0.21515 | 0.21057 | 0.24719 | 121.9894 | 122.0032 | -0.20599 | -0.22888 | 121.8384 | 121.9711 | 121.8063 | 121.962
2945.375 | 122.0993 | -121.9894 | 0.15106 | 0.0025177 | -0.01437 | -0.082856 | -0.0056973 | -0.029375 | -0.051235 | -0.039965 | -0.0021057 | -0.019467 | 0.0098438 | -0.021884 | -0.22022 | -0.017273 | -0.025176 | -0.14191 | 0.11444 | -0.15564 | -0.16479 | -0.022888 | -0.15106 | -0.073242 | -0.086975 | 0.13733 | -0.17395 | -0.041199 | 0.059509 | -0.018311 | 0.036621 | 121.8338 | -0.036621 | -0.31586 | 121.9666 | 121.9162 | 121.8384 | 0.082398 | 0.004578 | 121.8155 | -0.013733 | -0.19226 | 122.049 | 122.0261 | 121.9711 | 0.21057 | 0.15564 | 0.13275 | -0.009155 | 0.23346 | 0.13275 | 0.27008 | 0.31128 | 122.1039 | 122.1268 | -0.3067 | -0.32501 | 121.8246 | 121.9482 | 121.8475 | 121.9025
2947.1719 | 122.2366 | -121.9528 | 0.091553 | -0.0051118 | -0.011807 | -0.079011 | -0.0069791 | -0.024248 | -0.049313 | -0.040392 | -0.0021057 | -0.020536 | 0.008562 | -0.01697 | -0.22129 | -0.016205 | -0.023894 | -0.032043 | 0.064087 | -0.091553 | -0.027466 | 0.13275 | -0.059509 | 0.027466 | 0.10529 | 0.082397 | -0.10986 | 0.091553 | 0.17395 | 0.10986 | 0.16937 | 121.8613 | -0.027466 | -0.11902 | 122.0856 | 121.9803 | 121.8933 | 0.11902 | 0.032044 | 121.843 | -0.009156 | 0 | 122.1268 | 122.1222 | 122.0627 | 0.27924 | 0.21973 | 0.2243 | 0.064087 | 0.28381 | 0.20142 | 0.15564 | 0.19226 | 122.0169 | 122.0352 | -0.18311 | -0.20142 | 121.9254 | 122.0444 | 121.9208 | 122.0581
2948.9688 | 122.2824 | -121.9711 | 0.10529 | -0.012741 | -0.015652 | -0.079224 | -0.0086879 | -0.030871 | -0.051022 | -0.043596 | -0.0021057 | -0.022672 | 0.0087756 | -0.022097 | -0.21958 | -0.016846 | -0.022398 | -0.050354 | 0.073242 | -0.10071 | -0.013733 | 0.16479 | -0.013733 | 0.054932 | 0.11444 | 0.10986 | -0.14191 | 0.10529 | 0.2243 | 0.13733 | 0.16937 | 121.8704 | -0.032044 | -0.11902 | 122.1359 | 122.0261 | 121.9574 | 0.15564 | 0.086975 | 121.8292 | 0.004577 | 0 | 122.1954 | 122.1405 | 122.1085 | 0.31128 | 0.27924 | 0.2655 | 0.086975 | 0.36621 | 0.24719 | 0.17395 | 0.25177 | 122.0444 | 122.081 | -0.20599 | -0.24719 | 121.9574 | 122.0764 | 121.9208 | 122.0856
2950.6875 | 122.1542 | -122.0215 | 0.13733 | 0.010147 | -0.0096707 | -0.079011 | -0.0050565 | -0.033007 | -0.04974 | -0.040392 | 0.00094606 | -0.018827 | 0.0070666 | -0.015475 | -0.22065 | -0.018555 | -0.02603 | -0.10529 | 0.09613 | -0.14191 | -0.14648 | -0.032043 | -0.17395 | -0.10986 | -0.091553 | 0.14648 | -0.15564 | -0.041199 | 0.009155 | -0.059509 | 0.045776 | 121.8796 | -0.041199 | -0.28381 | 121.9894 | 121.9116 | 121.8475 | 0.032044 | -0.032043 | 121.8658 | 0.009155 | -0.17853 | 122.0306 | 122.0673 | 121.962 | 0.20142 | 0.096131 | 0.10986 | -0.004577 | 0.16479 | 0.11444 | 0.23804 | 0.30212 | 122.1176 | 122.168 | -0.27924 | -0.29297 | 121.875 | 121.9803 | 121.9162 | 121.9299
2952.4688 | 122.2 | -122.0169 | 0.11444 | -0.0051118 | -0.012234 | -0.079224 | -0.0037747 | -0.028948 | -0.050595 | -0.039537 | -0.0021057 | -0.01904 | 0.008562 | -0.017397 | -0.21979 | -0.01706 | -0.019408 | -0.073242 | 0.11444 | -0.12817 | -0.086975 | 0.073242 | -0.1236 | -0.036621 | 0.018311 | 0.1236 | -0.14648 | 0.032043 | 0.10071 | 0.013733 | 0.10529 | 121.8887 | 0 | -0.20142 | 122.0901 | 121.9803 | 121.8933 | 0.091553 | 0.004578 | 121.8704 | 0.009155 | -0.082398 | 122.1176 | 122.1222 | 122.0306 | 0.25177 | 0.16022 | 0.20142 | 0.041199 | 0.24719 | 0.17853 | 0.24262 | 0.27008 | 122.1313 | 122.1405 | -0.24262 | -0.26093 | 121.9299 | 122.049 | 121.9437 | 122.0352
2954.2344 | 122.2321 | -122.049 | 0.1236 | -0.0051118 | -0.011807 | -0.077729 | -0.0022793 | -0.025957 | -0.051022 | -0.041033 | 0.00094606 | -0.019467 | 0.007494 | -0.017611 | -0.21979 | -0.01471 | -0.023253 | -0.07782 | 0.1236 | -0.13275 | -0.10529 | 0.064087 | -0.10986 | -0.045776 | 0.009155 | 0.14191 | -0.16479 | 0.009155 | 0.10071 | 0.013733 | 0.073242 | 121.9162 | 0 | -0.22888 | 122.113 | 122.0032 | 121.9391 | 0.086975 | 0.022888 | 121.8842 | 0.018311 | -0.11444 | 122.1497 | 122.1222 | 122.0627 | 0.23804 | 0.17853 | 0.19684 | 0.027465 | 0.2655 | 0.17395 | 0.25635 | 0.3067 | 122.1725 | 122.1909 | -0.25635 | -0.28839 | 121.9437 | 122.0581 | 121.9711 | 122.0581
2956.0312 | 122.1954 | -122.0352 | 0.11902 | -0.012741 | -0.011166 | -0.079224 | -0.0044155 | -0.026598 | -0.051022 | -0.04146 | -0.0021057 | -0.018399 | 0.0096302 | -0.020175 | -0.21915 | -0.016633 | -0.02368 | -0.068665 | 0.10071 | -0.1236 | -0.10986 | 0.036621 | -0.14648 | -0.064087 | -0.022888 | 0.14191 | -0.16022 | 0.004578 | 0.086975 | -0.004578 | 0.059509 | 121.9116 | -0.018311 | -0.22888 | 122.0718 | 121.9711 | 121.8887 | 0.059509 | -0.022888 | 121.875 | 0.022888 | -0.11444 | 122.1222 | 122.0947 | 122.0306 | 0.21973 | 0.15564 | 0.16022 | 0.013733 | 0.24719 | 0.16479 | 0.2243 | 0.30212 | 122.1359 | 122.1771 | -0.24261 | -0.27924 | 121.9254 | 122.0398 | 121.9666 | 122.0123
2957.8281 | 122.2 | -122.0627 | 0.13733 | -0.0051118 | -0.014157 | -0.080079 | -0.0076199 | -0.032366 | -0.051449 | -0.040605 | -0.0021057 | -0.018827 | 0.010485 | -0.023806 | -0.21787 | -0.018555 | -0.022398 | -0.13733 | 0.12817 | -0.13733 | -0.15564 | -0.018311 | -0.14191 | -0.091553 | -0.09613 | 0.14191 | -0.16937 | -0.050354 | 0.050354 | -0.027466 | 0.041199 | 121.9254 | -0.009155 | -0.29297 | 122.0444 | 121.9711 | 121.9208 | 0.045776 | -0.004578 | 121.8933 | 0.004578 | -0.18768 | 122.113 | 122.1039 | 122.0352 | 0.21057 | 0.14191 | 0.11902 | -0.018311 | 0.21973 | 0.11902 | 0.2655 | 0.31128 | 122.1909 | 122.2046 | -0.27466 | -0.3067 | 121.907 | 122.0123 | 121.9254 | 121.9666
2959.625 | 122.3145 | -122.0169 | 0.10529 | 0.0025177 | -0.012448 | -0.079651 | -0.0084743 | -0.031939 | -0.04974 | -0.040819 | -0.0051575 | -0.022885 | 0.0070666 | -0.019747 | -0.22172 | -0.019623 | -0.024748 | -0.059509 | 0.059509 | -0.10529 | -0.036621 | 0.14191 | -0.009155 | 0.041199 | 0.082397 | 0.11444 | -0.12817 | 0.050354 | 0.18768 | 0.13733 | 0.14648 | 121.9116 | -0.045777 | -0.14191 | 122.1588 | 122.0581 | 122.0078 | 0.14649 | 0.096131 | 121.8887 | 0.009155 | -0.054932 | 122.2046 | 122.1634 | 122.1542 | 0.27466 | 0.2655 | 0.24719 | 0.068665 | 0.31586 | 0.17853 | 0.16479 | 0.24262 | 122.0764 | 122.1313 | -0.21057 | -0.23346 | 121.9803 | 122.0673 | 121.9574 | 122.0993
2961.3594 | 122.2092 | -122.0901 | 0.12817 | 0.0025177 | -0.013943 | -0.079865 | -0.0033475 | -0.028307 | -0.051022 | -0.042314 | -0.0021057 | -0.019681 | 0.008562 | -0.010561 | -0.22001 | -0.017701 | -0.02603 | -0.13275 | 0.12817 | -0.14191 | -0.16479 | -0.022888 | -0.14648 | -0.068665 | -0.086975 | 0.14191 | -0.17395 | -0.054932 | 0.050354 | -0.013733 | 0.041199 | 121.9482 | 0 | -0.29297 | 122.0673 | 122.0215 | 121.9437 | 0.073242 | -0.004577 | 121.9162 | 0.013733 | -0.18311 | 122.1405 | 122.1313 | 122.0764 | 0.21515 | 0.16022 | 0.11902 | -0.022888 | 0.2243 | 0.11902 | 0.27008 | 0.31586 | 122.2183 | 122.2321 | -0.27008 | -0.30212 | 121.9254 | 122.0352 | 121.9574 | 122.0032
2963.1406 | 122.3557 | -122.0261 | 0.082397 | 0.0025177 | -0.01138 | -0.07837 | -0.0067653 | -0.030871 | -0.04974 | -0.042528 | 0.0039979 | -0.021604 | 0.0089892 | -0.018038 | -0.22193 | -0.016846 | -0.025603 | -0.036621 | 0.068665 | -0.082397 | -0.036621 | 0.11902 | -0.059509 | 0.009155 | 0.086975 | 0.07782 | -0.10529 | 0.10986 | 0.20142 | 0.10986 | 0.17853 | 121.9437 | -0.013732 | -0.11902 | 122.1451 | 122.0352 | 121.9666 | 0.091552 | 0.022888 | 121.9208 | -0.004577 | 0.027466 | 122.2275 | 122.2046 | 122.1359 | 0.28381 | 0.21515 | 0.20142 | 0.045776 | 0.3067 | 0.21515 | 0.15106 | 0.18311 | 122.0947 | 122.1039 | -0.16479 | -0.18768 | 121.9894 | 122.1359 | 121.9894 | 122.113
2964.8594 | 122.2916 | -122.0627 | 0.10529 | -0.012741 | -0.01437 | -0.082215 | -0.0071927 | -0.031084 | -0.050595 | -0.041887 | 0.00094606 | -0.020108 | 0.0083484 | -0.025088 | -0.22022 | -0.019623 | -0.023894 | -0.11444 | 0.082397 | -0.13733 | -0.09613 | 0.050354 | -0.09613 | -0.018311 | -0.009155 | 0.086975 | -0.14191 | 0.022888 | 0.13733 | 0.050354 | 0.10986 | 121.9254 | -0.022889 | -0.20142 | 122.113 | 122.0444 | 121.9666 | 0.11902 | 0.041199 | 121.9208 | -0.018311 | -0.082398 | 122.2 | 122.1725 | 122.113 | 0.25177 | 0.19226 | 0.18768 | 0.041199 | 0.27924 | 0.16479 | 0.21973 | 0.22888 | 122.1451 | 122.1497 | -0.24262 | -0.24719 | 121.9666 | 122.0856 | 121.9482 | 122.0535
2966.5938 | 122.3373 | -122.0627 | 0.091553 | 0.0025177 | -0.011593 | -0.077302 | -0.0035611 | -0.030016 | -0.049526 | -0.039537 | 0.00094606 | -0.020322 | 0.0077076 | -0.020602 | -0.22172 | -0.01706 | -0.021971 | -0.10529 | 0.09613 | -0.1236 | -0.082397 | 0.059509 | -0.11902 | -0.032043 | 0.041199 | 0.10986 | -0.13733 | 0.07782 | 0.15564 | 0.082397 | 0.15106 | 121.9391 | 0.004577 | -0.17395 | 122.1222 | 122.0306 | 121.9437 | 0.091553 | 0.004577 | 121.9254 | 0.01831 | -0.013733 | 122.2183 | 122.2137 | 122.1451 | 0.28839 | 0.21973 | 0.1831 | 0.041199 | 0.29297 | 0.21515 | 0.21973 | 0.24719 | 122.1588 | 122.1725 | -0.21515 | -0.22888 | 121.9803 | 122.1405 | 121.9574 | 122.1039
2968.375 | 122.3328 | -122.0581 | 0.11902 | -0.0051118 | -0.011593 | -0.07837 | -0.0063381 | -0.032366 | -0.050595 | -0.042955 | 0.00094606 | -0.019895 | 0.0079212 | -0.018679 | -0.22236 | -0.018342 | -0.026457 | -0.068665 | 0.07782 | -0.091553 | -0.036621 | 0.12817 | -0.064087 | 0.013733 | 0.07782 | 0.10071 | -0.11444 | 0.082397 | 0.15564 | 0.082397 | 0.14191 | 121.9666 | -0.041199 | -0.15564 | 122.1863 | 122.0718 | 121.994 | 0.10529 | 0.027466 | 121.9437 | -0.018311 | -0.036622 | 122.2137 | 122.2 | 122.1405 | 0.25635 | 0.19684 | 0.21973 | 0.054932 | 0.27008 | 0.19684 | 0.16937 | 0.21515 | 122.1359 | 122.1588 | -0.21057 | -0.23346 | 122.0215 | 122.1405 | 121.9894 | 122.1359
2970.1562 | 122.2412 | -122.1313 | 0.12817 | 0.0025177 | -0.013943 | -0.080719 | -0.0042019 | -0.029375 | -0.050381 | -0.041674 | 0.0039979 | -0.02139 | 0.0083484 | -0.017397 | -0.22086 | -0.017701 | -0.020689 | -0.1236 | 0.11444 | -0.14191 | -0.15564 | -0.022888 | -0.14191 | -0.059509 | -0.086975 | 0.14648 | -0.16937 | -0.013733 | 0.050354 | -0.004578 | 0.027466 | 121.9894 | -0.013733 | -0.28381 | 122.1085 | 122.0718 | 121.9894 | 0.082398 | 0 | 121.962 | 0.01831 | -0.14191 | 122.1817 | 122.1588 | 122.1268 | 0.19684 | 0.16479 | 0.11902 | -0.013733 | 0.21973 | 0.15564 | 0.25635 | 0.31586 | 122.2458 | 122.2778 | -0.27008 | -0.29755 | 121.9757 | 122.1176 | 122.0078 | 122.0444
2971.9531 | 122.3877 | -122.0627 | 0.091553 | -0.0051118 | -0.015652 | -0.081574 | -0.0067653 | -0.031939 | -0.050167 | -0.040392 | 0.0039979 | -0.020108 | 0.0077076 | -0.025088 | -0.22107 | -0.017914 | -0.022398 | -0.054932 | 0.064087 | -0.10986 | -0.009155 | 0.16022 | -0.004578 | 0.054932 | 0.086975 | 0.11444 | -0.1236 | 0.10071 | 0.21515 | 0.14191 | 0.16479 | 121.9528 | -0.027466 | -0.10071 | 122.2229 | 122.1176 | 122.0581 | 0.16479 | 0.10529 | 121.9391 | 0.022888 | 0.009155 | 122.2778 | 122.2275 | 122.2046 | 0.28839 | 0.2655 | 0.27008 | 0.10071 | 0.33875 | 0.2243 | 0.17395 | 0.23804 | 122.1268 | 122.1771 | -0.20142 | -0.21515 | 122.0535 | 122.1634 | 122.0078 | 122.1497
2973.6719 | 122.3648 | -122.0718 | 0.1236 | -0.0051118 | -0.014798 | -0.080079 | -0.0091153 | -0.028948 | -0.051022 | -0.038896 | 0.00094606 | -0.020322 | 0.0049304 | -0.025515 | -0.22129 | -0.019196 | -0.025816 | -0.059509 | 0.082397 | -0.10986 | -0.027466 | 0.15564 | -0.022888 | 0.054932 | 0.068665 | 0.11444 | -0.1236 | 0.082397 | 0.19684 | 0.1236 | 0.14191 | 121.962 | -0.041199 | -0.15106 | 122.2275 | 122.1268 | 122.049 | 0.16479 | 0.086975 | 121.9482 | -0.009155 | -0.041199 | 122.2687 | 122.2137 | 122.1954 | 0.2655 | 0.24719 | 0.2655 | 0.082397 | 0.32043 | 0.20599 | 0.19226 | 0.23804 | 122.1542 | 122.1863 | -0.23346 | -0.24719 | 122.0444 | 122.1542 | 122.0123 | 122.1405
2975.4531 | 122.3465 | -122.0993 | 0.091553 | -0.012741 | -0.01138 | -0.080292 | -0.0071927 | -0.03322 | -0.04974 | -0.044023 | 0.00094606 | -0.019681 | 0.0070666 | -0.021243 | -0.21915 | -0.018128 | -0.027953 | -0.054932 | 0.082397 | -0.10529 | -0.027466 | 0.13733 | -0.022888 | 0.041199 | 0.059509 | 0.10529 | -0.14191 | 0.059509 | 0.17853 | 0.10986 | 0.13733 | 121.994 | -0.009156 | -0.11902 | 122.2366 | 122.1405 | 122.0764 | 0.14649 | 0.082398 | 121.9574 | 0.013733 | -0.032044 | 122.2778 | 122.2366 | 122.2092 | 0.27924 | 0.25177 | 0.24262 | 0.07782 | 0.32044 | 0.20142 | 0.18768 | 0.24719 | 122.1817 | 122.2046 | -0.19684 | -0.23346 | 122.0718 | 122.1588 | 122.0444 | 122.1588
2977.1719 | 122.3648 | -122.0535 | 0.10071 | -0.012741 | -0.011166 | -0.076447 | -0.0056973 | -0.03023 | -0.048886 | -0.043596 | -0.0021057 | -0.022458 | 0.005785 | -0.018038 | -0.22065 | -0.018769 | -0.019194 | -0.050354 | 0.064087 | -0.091553 | -0.018311 | 0.13275 | -0.054932 | 0.004578 | 0.10071 | 0.10529 | -0.12817 | 0.082397 | 0.1831 | 0.09613 | 0.17395 | 121.962 | -0.036621 | -0.11902 | 122.1863 | 122.0581 | 121.9986 | 0.096131 | 0.036621 | 121.9254 | 0.004578 | -0.018311 | 122.2366 | 122.2275 | 122.1497 | 0.30212 | 0.2243 | 0.2243 | 0.073242 | 0.31128 | 0.21057 | 0.15564 | 0.23346 | 122.1176 | 122.1588 | -0.19226 | -0.22888 | 122.0352 | 122.1359 | 122.0032 | 122.1542
2978.9688 | 122.3969 | -122.0901 | 0.10986 | 0.010147 | -0.012448 | -0.07837 | -0.0052701 | -0.032793 | -0.048886 | -0.040392 | -0.0021057 | -0.019895 | 0.0087756 | -0.019106 | -0.22065 | -0.015565 | -0.02368 | -0.082397 | 0.082397 | -0.10986 | -0.045776 | 0.086975 | -0.09613 | 0.009155 | 0.059509 | 0.09613 | -0.13275 | 0.09613 | 0.17853 | 0.091553 | 0.16022 | 121.9803 | -0.027466 | -0.15564 | 122.1771 | 122.0993 | 121.994 | 0.11902 | 0.013733 | 121.9574 | -0.013733 | -0.013733 | 122.2687 | 122.2504 | 122.1817 | 0.29297 | 0.2243 | 0.19684 | 0.064087 | 0.31128 | 0.22888 | 0.19226 | 0.22888 | 122.1725 | 122.1863 | -0.21973 | -0.24261 | 122.0444 | 122.1863 | 122.0078 | 122.1497
2980.7656 | 122.3145 | -122.1039 | 0.1236 | -0.012741 | -0.010739 | -0.078156 | -0.0044155 | -0.029162 | -0.050808 | -0.040819 | 0.0039979 | -0.020108 | 0.0079212 | -0.010989 | -0.22129 | -0.015565 | -0.023039 | -0.068665 | 0.11902 | -0.11902 | -0.10071 | 0.054932 | -0.10529 | -0.045776 | 0.018311 | 0.13275 | -0.14648 | 0.036621 | 0.10529 | 0.004578 | 0.091553 | 121.9849 | -0.004577 | -0.2243 | 122.1588 | 122.0581 | 121.9986 | 0.073243 | 0.013733 | 121.9574 | 0.009155 | -0.086975 | 122.2092 | 122.1954 | 122.1085 | 0.23804 | 0.15106 | 0.17395 | 0.018311 | 0.25177 | 0.18311 | 0.23804 | 0.27924 | 122.2229 | 122.2366 | -0.24261 | -0.27008 | 122.0032 | 122.1405 | 122.0352 | 122.1222
2982.5 | 122.4106 | -122.1085 | 0.10529 | -0.0051118 | -0.013516 | -0.080719 | -0.0084743 | -0.028521 | -0.052944 | -0.040605 | -0.0021057 | -0.023099 | 0.0079212 | -0.018893 | -0.21851 | -0.020478 | -0.025603 | -0.082397 | 0.091553 | -0.082397 | -0.045776 | 0.1236 | -0.045776 | 0.054932 | 0.07782 | 0.091553 | -0.13733 | 0.10529 | 0.21057 | 0.14191 | 0.16937 | 122.0261 | -0.013733 | -0.15106 | 122.2321 | 122.1634 | 122.0627 | 0.13733 | 0.036621 | 121.9711 | -0.013733 | 0 | 122.319 | 122.2778 | 122.2504 | 0.3067 | 0.27924 | 0.20599 | 0.036621 | 0.3479 | 0.24262 | 0.17395 | 0.22888 | 122.2 | 122.2 | -0.18768 | -0.24262 | 122.0627 | 122.2137 | 122.0261 | 122.1863
2984.2812 | 122.2824 | -122.1451 | 0.13733 | 0.0025177 | -0.013302 | -0.079651 | -0.0037747 | -0.029375 | -0.048031 | -0.039751 | 0.0039979 | -0.019254 | 0.0079212 | -0.01932 | -0.22065 | -0.017701 | -0.023253 | -0.12817 | 0.11444 | -0.14191 | -0.16022 | -0.036621 | -0.19226 | -0.091553 | -0.086975 | 0.14648 | -0.14191 | -0.018311 | 0.036621 | -0.050354 | 0.041199 | 122.0032 | -0.022888 | -0.29755 | 122.1085 | 122.0535 | 121.9528 | 0.050354 | -0.050354 | 122.0032 | 0.009155 | -0.15564 | 122.1817 | 122.1863 | 122.0947 | 0.18311 | 0.091553 | 0.10529 | -0.01831 | 0.17853 | 0.1236 | 0.25635 | 0.28839 | 122.2595 | 122.2916 | -0.27924 | -0.27924 | 121.9849 | 122.1268 | 122.0169 | 122.0581
2986.0625 | 122.4289 | -122.0947 | 0.11444 | -0.0051118 | -0.015225 | -0.08136 | -0.0074063 | -0.030016 | -0.051876 | -0.040819 | -0.0021057 | -0.023099 | 0.005785 | -0.019961 | -0.21872 | -0.017273 | -0.023894 | -0.059509 | 0.068665 | -0.10071 | -0.022888 | 0.14648 | -0.018311 | 0.054932 | 0.11444 | 0.10529 | -0.1236 | 0.086975 | 0.2243 | 0.14648 | 0.15564 | 121.994 | -0.045776 | -0.13733 | 122.2412 | 122.1497 | 122.0764 | 0.15564 | 0.082397 | 121.9711 | -0.009155 | -0.027466 | 122.319 | 122.2504 | 122.2412 | 0.27924 | 0.27008 | 0.24719 | 0.07782 | 0.3479 | 0.21057 | 0.16937 | 0.22888 | 122.1634 | 122.2 | -0.21515 | -0.23804 | 122.0718 | 122.1817 | 122.0352 | 122.2092
2987.8438 | 122.3877 | -122.1085 | 0.10986 | 0.0025177 | -0.0086027 | -0.079438 | -0.0052701 | -0.027453 | -0.051449 | -0.040392 | 0.00094606 | -0.018186 | 0.0062122 | -0.015475 | -0.22022 | -0.017701 | -0.027098 | -0.10529 | 0.10529 | -0.11902 | -0.10529 | 0.027466 | -0.14648 | -0.045776 | 0.045776 | 0.11444 | -0.13733 | 0.07782 | 0.15106 | 0.054932 | 0.13275 | 121.9894 | -0.004577 | -0.21515 | 122.1359 | 122.0627 | 121.962 | 0.073243 | -0.027465 | 121.9711 | 0.004578 | -0.032043 | 122.2595 | 122.2412 | 122.1634 | 0.27008 | 0.19226 | 0.14649 | 0.013733 | 0.28839 | 0.21515 | 0.22431 | 0.25177 | 122.2137 | 122.2229 | -0.22888 | -0.24719 | 122.0032 | 122.1863 | 122.0032 | 122.1542
2989.5625 | 122.4289 | -122.1176 | 0.11444 | -0.0051118 | -0.01138 | -0.077942 | -0.0071927 | -0.031725 | -0.047604 | -0.040819 | -0.0082091 | -0.019681 | 0.0072802 | -0.020388 | -0.21979 | -0.018982 | -0.023253 | -0.041199 | 0.07782 | -0.09613 | -0.027466 | 0.1236 | -0.073242 | 0 | 0.10986 | 0.10986 | -0.11444 | 0.12817 | 0.1831 | 0.10986 | 0.16937 | 122.0215 | -0.036621 | -0.14191 | 122.2412 | 122.1176 | 122.0444 | 0.09613 | 0.022888 | 122.0032 | -0.004578 | 0.013733 | 122.3007 | 122.287 | 122.2275 | 0.28381 | 0.2243 | 0.21973 | 0.068664 | 0.29755 | 0.24262 | 0.17395 | 0.2243 | 122.1954 | 122.2275 | -0.21057 | -0.22888 | 122.0901 | 122.2458 | 122.0764 | 122.2275
2991.3438 | 122.4243 | -122.0947 | 0.10529 | -0.012741 | -0.01138 | -0.078797 | -0.0065517 | -0.031298 | -0.049526 | -0.041033 | 0.00094606 | -0.02139 | 0.0070666 | -0.022524 | -0.21979 | -0.017487 | -0.019835 | -0.041199 | 0.073242 | -0.086975 | -0.032043 | 0.1236 | -0.059509 | 0.018311 | 0.11902 | 0.10071 | -0.1236 | 0.11902 | 0.17853 | 0.10529 | 0.1831 | 122.0078 | -0.032044 | -0.13733 | 122.2183 | 122.113 | 122.0352 | 0.10529 | 0.027466 | 121.9711 | -0.004578 | 0.013733 | 122.2733 | 122.2778 | 122.2 | 0.3067 | 0.22888 | 0.21057 | 0.054932 | 0.30212 | 0.24261 | 0.16022 | 0.2243 | 122.168 | 122.1954 | -0.19226 | -0.22888 | 122.0627 | 122.2137 | 122.0535 | 122.2137
2993.0625 | 122.3831 | -122.1451 | 0.10071 | -0.0051118 | -0.01138 | -0.079011 | -0.0050565 | -0.027666 | -0.048672 | -0.041246 | -0.0021057 | -0.021176 | 0.0077076 | -0.02167 | -0.21979 | -0.018982 | -0.024321 | -0.073242 | 0.07782 | -0.086975 | -0.059509 | 0.10071 | -0.091553 | 0.004578 | 0.059509 | 0.11902 | -0.14648 | 0.050354 | 0.13733 | 0.068665 | 0.13275 | 122.0581 | -0.022888 | -0.16022 | 122.2458 | 122.1497 | 122.0535 | 0.091553 | -0.004578 | 121.9986 | 0.018311 | -0.050354 | 122.2824 | 122.2778 | 122.2137 | 0.27924 | 0.21515 | 0.18768 | 0.027466 | 0.28381 | 0.19684 | 0.16479 | 0.2655 | 122.2229 | 122.2641 | -0.18768 | -0.24719 | 122.0856 | 122.1954 | 122.0718 | 122.2046
2994.8438 | 122.3465 | -122.1588 | 0.15106 | -0.0051118 | -0.016507 | -0.080506 | -0.0059109 | -0.02788 | -0.050808 | -0.040605 | 0.00094606 | -0.018399 | 0.0083484 | -0.022738 | -0.22107 | -0.01706 | -0.021971 | -0.12817 | 0.1236 | -0.14191 | -0.16022 | -0.022888 | -0.12817 | -0.068665 | -0.050354 | 0.15564 | -0.16479 | -0.018311 | 0.07782 | -0.009155 | 0.050354 | 122.0169 | -0.027466 | -0.31128 | 122.1359 | 122.0901 | 122.0306 | 0.073242 | 0.013733 | 121.994 | 0.004578 | -0.16937 | 122.2366 | 122.2092 | 122.1497 | 0.21515 | 0.15564 | 0.11902 | -0.01831 | 0.24261 | 0.14648 | 0.2655 | 0.32044 | 122.2824 | 122.3145 | -0.29297 | -0.31586 | 121.9986 | 122.1405 | 122.0306 | 122.1085
2996.6406 | 122.3145 | -122.1588 | 0.14191 | -0.0051118 | -0.012234 | -0.077942 | -0.0031337 | -0.031939 | -0.048031 | -0.041246 | 0.00094606 | -0.019895 | 0.0062122 | -0.020175 | -0.22022 | -0.015992 | -0.021971 | -0.1236 | 0.13275 | -0.15106 | -0.16479 | -0.050354 | -0.20599 | -0.10529 | -0.054932 | 0.14648 | -0.15564 | 0 | 0.004578 | -0.054932 | 0.036621 | 122.0078 | -0.009156 | -0.3067 | 122.1085 | 122.0535 | 121.9528 | 0.045776 | -0.054932 | 122.0032 | 0.004577 | -0.14191 | 122.1634 | 122.1954 | 122.1039 | 0.19226 | 0.10071 | 0.10071 | -0.013733 | 0.16022 | 0.15564 | 0.28381 | 0.30212 | 122.2916 | 122.3053 | -0.29297 | -0.29755 | 121.994 | 122.1588 | 122.0352 | 122.1039
2998.3594 | 122.319 | -122.1771 | 0.16022 | 0.0025177 | -0.013516 | -0.079438 | -0.0071927 | -0.03322 | -0.051449 | -0.041246 | 0.00094606 | -0.018399 | 0.0072802 | -0.026156 | -0.21894 | -0.017914 | -0.021544 | -0.15564 | 0.11902 | -0.14648 | -0.16937 | -0.018311 | -0.14648 | -0.059509 | -0.064087 | 0.16937 | -0.17395 | -0.027466 | 0.054932 | -0.018311 | 0.027466 | 122.0306 | -0.041198 | -0.32959 | 122.1588 | 122.1176 | 122.0306 | 0.086975 | 0 | 122.0032 | 0.009156 | -0.18768 | 122.2321 | 122.2046 | 122.1588 | 0.20142 | 0.15564 | 0.12817 | -0.022889 | 0.22888 | 0.14648 | 0.2655 | 0.34332 | 122.2961 | 122.3465 | -0.3067 | -0.33417 | 122.0078 | 122.1497 | 122.0215 | 122.113
3000.1406 | 122.4152 | -122.168 | 0.10529 | -0.0051118 | -0.015866 | -0.081147 | -0.0078335 | -0.028948 | -0.049099 | -0.041246 | -0.0021057 | -0.019254 | 0.0081348 | -0.020815 | -0.21872 | -0.019196 | -0.024321 | -0.064087 | 0.064087 | -0.09613 | -0.036621 | 0.13733 | -0.036621 | 0.041199 | 0.10071 | 0.12817 | -0.11902 | 0.073242 | 0.17853 | 0.10986 | 0.11902 | 122.0718 | -0.041199 | -0.14191 | 122.3053 | 122.2092 | 122.1313 | 0.13733 | 0.059509 | 122.049 | 0.022888 | -0.032044 | 122.3465 | 122.287 | 122.2778 | 0.23804 | 0.22888 | 0.23346 | 0.059509 | 0.29755 | 0.19226 | 0.16022 | 0.24719 | 122.2321 | 122.2961 | -0.20142 | -0.22431 | 122.1313 | 122.2412 | 122.1039 | 122.2687
3001.875 | 122.3465 | -122.1771 | 0.14648 | -0.0051118 | -0.0098843 | -0.078156 | -0.0031337 | -0.030871 | -0.051663 | -0.041246 | -0.0082091 | -0.020963 | 0.0098438 | -0.020175 | -0.22043 | -0.016419 | -0.026244 | -0.11902 | 0.11444 | -0.14191 | -0.16479 | -0.022888 | -0.19226 | -0.091553 | -0.027466 | 0.16479 | -0.16479 | 0.013733 | 0.041199 | -0.032043 | 0.045776 | 122.0352 | -0.032043 | -0.31128 | 122.1542 | 122.0856 | 121.9849 | 0.050354 | -0.050354 | 122.0123 | 0.018311 | -0.13275 | 122.2183 | 122.2229 | 122.1451 | 0.21057 | 0.13275 | 0.11902 | -0.022888 | 0.20599 | 0.17853 | 0.25635 | 0.32959 | 122.2916 | 122.3419 | -0.28839 | -0.31128 | 122.0123 | 122.1909 | 122.0581 | 122.1497
3003.6719 | 122.3236 | -122.1863 | 0.17395 | -0.0051118 | -0.0098843 | -0.077942 | -0.0042019 | -0.024675 | -0.050167 | -0.043596 | 0.00094606 | -0.018399 | 0.0089892 | -0.022738 | -0.22043 | -0.016419 | -0.021117 | -0.1236 | 0.10986 | -0.13733 | -0.17853 | -0.045776 | -0.20599 | -0.10529 | -0.059509 | 0.18768 | -0.15564 | 0.009155 | 0.032043 | -0.054932 | 0.045776 | 122.049 | -0.064087 | -0.35248 | 122.1405 | 122.081 | 121.9803 | 0.032043 | -0.068665 | 122.0306 | 0.013733 | -0.16479 | 122.2183 | 122.2321 | 122.1313 | 0.20142 | 0.10071 | 0.091553 | -0.041199 | 0.18768 | 0.16479 | 0.24719 | 0.34332 | 122.2961 | 122.374 | -0.31128 | -0.32959 | 122.0078 | 122.1954 | 122.0627 | 122.1268
3005.4688 | 122.4792 | -122.0947 | 0.15564 | 0.010147 | -0.01202 | -0.078797 | -0.0054837 | -0.027239 | -0.052731 | -0.040178 | -0.0051575 | -0.020536 | 0.0081348 | -0.02167 | -0.22043 | -0.018769 | -0.026885 | -0.032043 | 0.073242 | -0.09613 | -0.022888 | 0.13275 | -0.050354 | 0.022888 | 0.11902 | 0.14648 | -0.1236 | 0.15564 | 0.19226 | 0.11444 | 0.16022 | 121.9986 | -0.082398 | -0.17853 | 122.2275 | 122.1176 | 122.0444 | 0.11902 | 0.045776 | 121.9711 | -0.009156 | 0 | 122.287 | 122.2549 | 122.2092 | 0.28381 | 0.23804 | 0.22888 | 0.073242 | 0.31586 | 0.27924 | 0.16937 | 0.27008 | 122.168 | 122.2412 | -0.25177 | -0.27924 | 122.0718 | 122.2504 | 122.0627 | 122.2137
3007.2656 | 122.374 | -122.1405 | 0.17853 | -0.0051118 | -0.013516 | -0.080079 | -0.0052701 | -0.030871 | -0.049526 | -0.040819 | -0.0021057 | -0.01669 | 0.0092028 | -0.016543 | -0.21808 | -0.017487 | -0.021971 | -0.10986 | 0.11902 | -0.10986 | -0.13275 | 0.009155 | -0.10529 | -0.050354 | -0.013733 | 0.18768 | -0.16479 | 0.064087 | 0.09613 | 0.009155 | 0.07782 | 122.0306 | -0.059509 | -0.31128 | 122.1497 | 122.0901 | 122.0352 | 0.059509 | 0.004577 | 121.9757 | 0.009155 | -0.11444 | 122.2366 | 122.2183 | 122.1497 | 0.24261 | 0.17395 | 0.11902 | -0.022888 | 0.26092 | 0.22888 | 0.22888 | 0.35248 | 122.2595 | 122.3282 | -0.28839 | -0.34332 | 122.0078 | 122.2046 | 122.0306 | 122.1268
3008.9844 | 122.4472 | -122.0947 | 0.17853 | 0.0025177 | -0.010098 | -0.077942 | -0.0076199 | -0.028093 | -0.050167 | -0.040178 | -0.0021057 | -0.021817 | 0.0083484 | -0.023379 | -0.2183 | -0.017273 | -0.019408 | -0.054932 | 0.07782 | -0.073242 | -0.050354 | 0.14191 | -0.059509 | 0.032043 | 0.11444 | 0.17853 | -0.1236 | 0.16022 | 0.16022 | 0.09613 | 0.15564 | 122.0215 | -0.10071 | -0.22888 | 122.2366 | 122.1268 | 122.0352 | 0.10529 | 0.013733 | 121.9711 | 0 | -0.018311 | 122.2549 | 122.2504 | 122.1909 | 0.27924 | 0.21973 | 0.21515 | 0.022888 | 0.28381 | 0.28381 | 0.15106 | 0.30212 | 122.1725 | 122.2733 | -0.25177 | -0.30212 | 122.0444 | 122.2549 | 122.0398 | 122.2092
3010.7656 | 122.3602 | -121.7789 | 0.51727 | -0.0051118 | -0.012875 | -0.079224 | -0.0035611 | -0.029162 | -0.051663 | -0.039324 | -0.0021057 | -0.018827 | 0.0081348 | -0.015475 | -0.22086 | -0.017273 | -0.023253 | -0.086975 | 0.13733 | -0.1236 | -0.11444 | 0.027466 | -0.10529 | -0.041199 | -0.013733 | 0.50354 | -0.16022 | 0.39825 | 0.11902 | 0.032043 | 0.068665 | 121.6553 | -0.37994 | -0.63171 | 121.8063 | 121.7377 | 121.6736 | 0.082397 | 0.01831 | 121.6187 | -0.013733 | -0.11902 | 121.8979 | 121.8475 | 121.8109 | 0.22888 | 0.19226 | 0.15106 | 0.009155 | 0.27924 | 0.55847 | 0.26093 | 0.66376 | 121.9162 | 122.2824 | -0.64087 | -0.67749 | 121.6644 | 122.1771 | 121.6919 | 121.7651
3012.4844 | 122.4426 | -121.6507 | 0.58136 | -0.0051118 | -0.014798 | -0.079651 | -0.0074063 | -0.030871 | -0.048458 | -0.040605 | -0.0021057 | -0.022672 | 0.0079212 | -0.027224 | -0.21851 | -0.017914 | -0.022826 | -0.027466 | 0.11902 | -0.068665 | -0.004578 | 0.19684 | 0.004578 | 0.073242 | 0.14648 | 0.56763 | -0.11444 | 0.58136 | 0.24719 | 0.16022 | 0.16937 | 121.582 | -0.46234 | -0.58594 | 121.8475 | 121.7239 | 121.6553 | 0.14191 | 0.073243 | 121.5363 | -0.013733 | 0 | 121.8979 | 121.8201 | 121.8109 | 0.28381 | 0.27466 | 0.2655 | 0.064087 | 0.36163 | 0.6958 | 0.18768 | 0.68207 | 121.7697 | 122.2183 | -0.65002 | -0.6958 | 121.6461 | 122.2321 | 121.6232 | 121.7972
3014.2656 | 122.2595 | -120.5246 | 1.5793 | 0.0025177 | -0.018643 | -0.078156 | -0.0067653 | -0.03023 | -0.051449 | -0.040605 | 0.00094606 | -0.022458 | 0.0089892 | -0.015048 | -0.22278 | -0.018982 | -0.01898 | -0.004578 | 0.17853 | -0.018311 | 0 | 0.16479 | 0.013733 | 0.10529 | 0.064087 | 1.5976 | -0.13275 | 1.5289 | 0.28381 | 0.13733 | 0.17853 | 120.5063 | -1.4008 | -1.5793 | 120.6894 | 120.6299 | 120.5383 | 0.1236 | 0.032044 | 120.3918 | 0.01831 | -0.050354 | 120.8084 | 120.7031 | 120.6619 | 0.31128 | 0.27008 | 0.18311 | 0.018311 | 0.41656 | 1.6617 | 0.19684 | 1.7303 | 120.7031 | 122.1222 | -1.5976 | -1.712 | 120.5246 | 122.0535 | 120.52 | 120.5887
3015.9844 | 122.2549 | -121.4859 | 0.54474 | -0.012741 | -0.0098843 | -0.079011 | -0.0063381 | -0.03023 | -0.050595 | -0.039751 | 0.00094606 | -0.020108 | 0.0077076 | -0.017397 | -0.21851 | -0.017273 | -0.02603 | -0.013733 | 0.11444 | -0.054932 | -0.013733 | 0.12817 | -0.036621 | 0.032043 | 0.10071 | 0.52643 | -0.10986 | 0.57678 | 0.21973 | 0.12817 | 0.20142 | 121.431 | -0.4303 | -0.55847 | 121.6141 | 121.5179 | 121.4493 | 0.086975 | 0.018311 | 121.376 | -0.018311 | 0.032043 | 121.7056 | 121.6873 | 121.6141 | 0.31128 | 0.23804 | 0.18311 | 0.041199 | 0.32959 | 0.68665 | 0.16937 | 0.63629 | 121.6003 | 122.0123 | -0.59967 | -0.6546 | 121.4722 | 122.0627 | 121.4722 | 121.5866
3017.7812 | 121.9528 | -120.6665 | 1.2909 | -0.0051118 | -0.017575 | -0.081788 | -0.0065517 | -0.032366 | -0.051663 | -0.041887 | -0.0021057 | -0.020536 | 0.0079212 | -0.018679 | -0.21958 | -0.017701 | -0.025176 | -0.059509 | 0.19226 | -0.07782 | -0.059509 | 0.086975 | -0.068665 | 0.009155 | -0.027466 | 1.2817 | -0.14648 | 1.1124 | 0.1236 | 0.004578 | 0.054932 | 120.5887 | -1.0986 | -1.3504 | 120.7535 | 120.6757 | 120.5978 | 0.086975 | 0.009155 | 120.52 | -0.009156 | -0.17853 | 120.7901 | 120.7214 | 120.6711 | 0.20142 | 0.15106 | 0.16479 | 0.018311 | 0.27008 | 1.2589 | 0.27008 | 1.4282 | 120.8588 | 121.9482 | -1.3687 | -1.4374 | 120.607 | 121.7789 | 120.607 | 120.639
3019.5625 | 122.3099 | -122.0764 | 0.11902 | 0.0025177 | -0.014584 | -0.079011 | -0.0076199 | -0.033648 | -0.051449 | -0.041033 | 0.00094606 | -0.020749 | 0.0066394 | -0.026583 | -0.22193 | -0.01941 | -0.02368 | -0.059509 | 0.09613 | -0.10529 | -0.032043 | 0.11902 | -0.027466 | 0.041199 | 0.064087 | 0.11902 | -0.13275 | 0.018311 | 0.13275 | 0.086975 | 0.11902 | 121.9711 | -0.022889 | -0.15106 | 122.1954 | 122.1176 | 122.0489 | 0.14649 | 0.07782 | 121.9437 | 0 | -0.10071 | 122.2092 | 122.1954 | 122.1634 | 0.25177 | 0.21973 | 0.22431 | 0.073243 | 0.2655 | 0.15106 | 0.20142 | 0.25177 | 122.1725 | 122.1954 | -0.22431 | -0.25177 | 122.0444 | 122.0947 | 122.0169 | 122.1405
3021.2656 | 122.3831 | -122.049 | 0.13733 | -0.012741 | -0.011807 | -0.077942 | -0.0052701 | -0.031939 | -0.049313 | -0.044023 | -0.0051575 | -0.022031 | 0.0089892 | -0.021029 | -0.22043 | -0.016846 | -0.022398 | -0.027466 | 0.082397 | -0.086975 | -0.009155 | 0.13733 | -0.050354 | 0.032043 | 0.13275 | 0.13275 | -0.11902 | 0.13275 | 0.16937 | 0.10071 | 0.17395 | 121.962 | -0.054932 | -0.14648 | 122.1863 | 122.081 | 121.9986 | 0.11902 | 0.036621 | 121.9299 | -0.004578 | -0.004578 | 122.2183 | 122.2229 | 122.1497 | 0.29297 | 0.21973 | 0.2243 | 0.07782 | 0.28839 | 0.25177 | 0.16937 | 0.25177 | 122.1313 | 122.1817 | -0.2243 | -0.25635 | 122.0398 | 122.1817 | 122.0215 | 122.1817
3023.0625 | 122.4152 | -122.0901 | 0.1236 | -0.0051118 | -0.010098 | -0.079224 | -0.0050565 | -0.028521 | -0.051235 | -0.041033 | -0.0021057 | -0.020108 | 0.0066394 | -0.017825 | -0.22043 | -0.018342 | -0.026885 | -0.032043 | 0.091553 | -0.07782 | -0.036621 | 0.1236 | -0.07782 | 0.022888 | 0.10986 | 0.13275 | -0.12817 | 0.12817 | 0.17853 | 0.10529 | 0.16937 | 122.0123 | -0.032043 | -0.16022 | 122.2137 | 122.113 | 122.0123 | 0.10071 | 0 | 121.962 | 0.009155 | 0.004578 | 122.2687 | 122.2595 | 122.1954 | 0.29755 | 0.23346 | 0.20142 | 0.041199 | 0.3067 | 0.25635 | 0.16937 | 0.26093 | 122.1817 | 122.2229 | -0.20142 | -0.25177 | 122.0535 | 122.2183 | 122.0581 | 122.2
3024.8594 | 122.3465 | -122.0947 | 0.18768 | 0.0025177 | -0.012661 | -0.080933 | -0.0046291 | -0.032366 | -0.049313 | -0.039324 | -0.0021057 | -0.018613 | 0.0081348 | -0.01932 | -0.21958 | -0.018342 | -0.023467 | -0.10986 | 0.12817 | -0.10986 | -0.1236 | 0.004578 | -0.12817 | -0.068665 | 0.004578 | 0.16937 | -0.16022 | 0.050354 | 0.086975 | 0.022888 | 0.068665 | 121.9849 | -0.059509 | -0.31128 | 122.0993 | 122.0261 | 121.9666 | 0.041198 | -0.018311 | 121.9345 | -0.01831 | -0.13733 | 122.1817 | 122.1634 | 122.1176 | 0.22888 | 0.1831 | 0.11444 | -0.013733 | 0.24719 | 0.21057 | 0.23804 | 0.32959 | 122.2229 | 122.2641 | -0.29755 | -0.3479 | 121.9711 | 122.1451 | 121.9849 | 122.0993
3026.6406 | 122.438 | -122.1451 | 0.09613 | 0.0025177 | -0.012875 | -0.080079 | -0.0069791 | -0.028948 | -0.050167 | -0.04146 | -0.0021057 | -0.020963 | 0.0059986 | -0.022952 | -0.2183 | -0.018769 | -0.026457 | -0.064087 | 0.091553 | -0.10986 | -0.022888 | 0.16022 | -0.018311 | 0.050354 | 0.10529 | 0.091553 | -0.10529 | 0.091553 | 0.19684 | 0.12817 | 0.15106 | 122.0352 | -0.004577 | -0.11902 | 122.3053 | 122.1954 | 122.1268 | 0.16022 | 0.091552 | 122.0398 | -0.004577 | -0.004577 | 122.3419 | 122.2961 | 122.2733 | 0.25635 | 0.23346 | 0.27008 | 0.086975 | 0.30212 | 0.19684 | 0.20142 | 0.19684 | 122.2366 | 122.2366 | -0.20599 | -0.20142 | 122.1222 | 122.2366 | 122.081 | 122.2504
3028.3594 | 122.4518 | -122.1451 | 0.10986 | 0.0025177 | -0.013943 | -0.079438 | -0.0093289 | -0.032793 | -0.049526 | -0.040819 | 0.00094606 | -0.020108 | 0.0079212 | -0.029147 | -0.22001 | -0.015778 | -0.027739 | -0.045776 | 0.086975 | -0.10986 | -0.022888 | 0.15564 | 0 | 0.032043 | 0.11444 | 0.11444 | -0.11902 | 0.091553 | 0.20142 | 0.15564 | 0.14191 | 122.0352 | -0.022888 | -0.13275 | 122.3007 | 122.1771 | 122.1451 | 0.14191 | 0.10986 | 122.0261 | 0.004578 | -0.01831 | 122.3465 | 122.287 | 122.3007 | 0.26093 | 0.27466 | 0.2655 | 0.086975 | 0.32044 | 0.21057 | 0.19684 | 0.23346 | 122.2321 | 122.2595 | -0.21973 | -0.22888 | 122.1222 | 122.2366 | 122.0993 | 122.2595
3030.1406 | 122.4609 | -122.0718 | 0.16479 | -0.012741 | -0.010311 | -0.079651 | -0.0035611 | -0.03023 | -0.04974 | -0.042314 | 0.00094606 | -0.01904 | 0.0064258 | -0.017825 | -0.2215 | -0.017701 | -0.024962 | -0.11902 | 0.11444 | -0.11444 | -0.10529 | 0.036621 | -0.15106 | -0.032043 | 0.041199 | 0.20142 | -0.12817 | 0.15564 | 0.14648 | 0.07782 | 0.15106 | 121.9574 | -0.050354 | -0.27008 | 122.1085 | 122.0398 | 121.9208 | 0.082398 | -0.036621 | 121.9437 | 0.036621 | -0.009155 | 122.2183 | 122.2229 | 122.1497 | 0.27924 | 0.20599 | 0.15106 | 0.009155 | 0.27466 | 0.28381 | 0.22888 | 0.32959 | 122.1863 | 122.2733 | -0.27924 | -0.29297 | 121.9666 | 122.2275 | 121.9528 | 122.113
3031.875 | 122.2549 | -121.9299 | 0.37079 | -0.0051118 | -0.01437 | -0.079224 | -0.0033475 | -0.033648 | -0.05209 | -0.042528 | -0.0051575 | -0.019467 | 0.008562 | -0.017825 | -0.2168 | -0.018128 | -0.022185 | -0.1236 | 0.13275 | -0.1236 | -0.12817 | 0.022888 | -0.13275 | -0.050354 | -0.050354 | 0.37537 | -0.15564 | 0.15564 | 0.064087 | 0 | 0.032043 | 121.8063 | -0.23804 | -0.49896 | 121.9528 | 121.8796 | 121.7972 | 0.073242 | -0.009155 | 121.7743 | 0.004577 | -0.21515 | 121.994 | 121.962 | 121.9299 | 0.18768 | 0.15564 | 0.14648 | -0.004578 | 0.21973 | 0.31128 | 0.25635 | 0.53101 | 122.0627 | 122.3053 | -0.49438 | -0.52643 | 121.8018 | 122.0856 | 121.8063 | 121.8796
3033.6719 | 122.4564 | -122.1542 | 0.09613 | -0.0051118 | -0.016079 | -0.078583 | -0.0095425 | -0.030871 | -0.049954 | -0.039324 | -0.0051575 | -0.020963 | 0.0064258 | -0.014407 | -0.22043 | -0.01706 | -0.020903 | -0.059509 | 0.07782 | -0.091553 | -0.009155 | 0.17853 | -0.022888 | 0.054932 | 0.12817 | 0.10529 | -0.11902 | 0.091553 | 0.19684 | 0.12817 | 0.16022 | 122.0627 | -0.01831 | -0.10528 | 122.3328 | 122.2092 | 122.1313 | 0.14649 | 0.068665 | 122.0352 | 0.009156 | -0.004577 | 122.3511 | 122.3145 | 122.2824 | 0.27924 | 0.24719 | 0.27008 | 0.082398 | 0.31586 | 0.21057 | 0.16937 | 0.22431 | 122.2321 | 122.2595 | -0.18768 | -0.21515 | 122.1451 | 122.2458 | 122.0947 | 122.2824
3035.3906 | 122.4655 | -122.1359 | 0.086975 | -0.0051118 | -0.012234 | -0.078797 | -0.0067653 | -0.026171 | -0.051235 | -0.041887 | 0.00094606 | -0.020536 | 0.0036486 | -0.016329 | -0.22022 | -0.01706 | -0.024535 | -0.022888 | 0.07782 | -0.091553 | -0.018311 | 0.1236 | -0.07782 | 0.022888 | 0.1236 | 0.11444 | -0.11902 | 0.10986 | 0.16479 | 0.10986 | 0.15564 | 122.0444 | -0.009155 | -0.10529 | 122.2595 | 122.1588 | 122.0581 | 0.11444 | 0.013733 | 122.0169 | 0.027466 | 0.022888 | 122.3007 | 122.2916 | 122.2458 | 0.27466 | 0.22888 | 0.21515 | 0.073242 | 0.28381 | 0.22888 | 0.16937 | 0.23346 | 122.2137 | 122.2504 | -0.17853 | -0.20599 | 122.1176 | 122.2458 | 122.113 | 122.2595
3037.1875 | 122.3557 | -122.2366 | 0.14191 | 0.010147 | -0.01202 | -0.081147 | -0.0059109 | -0.028521 | -0.05209 | -0.038469 | 0.0039979 | -0.019895 | 0.0096302 | -0.01932 | -0.22022 | -0.017701 | -0.024107 | -0.10529 | 0.091553 | -0.11902 | -0.1236 | 0.027466 | -0.12817 | -0.054932 | -0.036621 | 0.16022 | -0.16479 | -0.045776 | 0.050354 | 0 | 0.036621 | 122.1176 | -0.050354 | -0.2655 | 122.2641 | 122.1817 | 122.1085 | 0.064087 | -0.009155 | 122.0718 | 0.01831 | -0.18768 | 122.287 | 122.2733 | 122.2366 | 0.20142 | 0.16479 | 0.14649 | -0.004577 | 0.21515 | 0.11902 | 0.21057 | 0.32501 | 122.3282 | 122.3969 | -0.26093 | -0.3067 | 122.113 | 122.1909 | 122.1313 | 122.2
3038.9219 | 122.4747 | -122.1817 | 0.07782 | -0.0051118 | -0.010739 | -0.07837 | -0.0059109 | -0.03023 | -0.050808 | -0.040392 | -0.0051575 | -0.019467 | 0.0094166 | -0.016757 | -0.22107 | -0.017273 | -0.020476 | -0.032043 | 0.086975 | -0.091553 | -0.022888 | 0.11902 | -0.082397 | 0.032043 | 0.11902 | 0.09613 | -0.12817 | 0.10529 | 0.16479 | 0.11444 | 0.17395 | 122.0901 | 0.009155 | -0.10071 | 122.3007 | 122.2137 | 122.0993 | 0.1236 | 0.009156 | 122.0535 | 0.01831 | 0.027466 | 122.3465 | 122.3557 | 122.2961 | 0.30212 | 0.24262 | 0.21057 | 0.068665 | 0.29297 | 0.23346 | 0.17853 | 0.2243 | 122.2687 | 122.2778 | -0.16937 | -0.20599 | 122.1588 | 122.287 | 122.1497 | 122.3007
3040.7031 | 122.406 | -122.2183 | 0.16937 | -0.0051118 | -0.0090299 | -0.080506 | -0.0039883 | -0.025957 | -0.048672 | -0.03911 | -0.0021057 | -0.018827 | 0.0094166 | -0.019747 | -0.21958 | -0.017701 | -0.022826 | -0.091553 | 0.10986 | -0.11444 | -0.13275 | 0.013733 | -0.17395 | -0.082397 | -0.036621 | 0.15106 | -0.14648 | -0.018311 | 0.022888 | -0.045776 | 0.036621 | 122.1039 | -0.05951 | -0.30212 | 122.2321 | 122.1359 | 122.0444 | 0.032044 | -0.059509 | 122.0718 | -0.018311 | -0.18768 | 122.2412 | 122.2549 | 122.1725 | 0.18311 | 0.10071 | 0.12817 | -0.01831 | 0.16937 | 0.12817 | 0.2243 | 0.29755 | 122.3282 | 122.3694 | -0.28381 | -0.31586 | 122.0856 | 122.2 | 122.1268 | 122.1817
3042.5 | 122.4426 | -122.2046 | 0.11444 | -0.012741 | -0.01138 | -0.079224 | -0.0061245 | -0.028948 | -0.048458 | -0.040819 | 0.00094606 | -0.020536 | 0.0066394 | -0.02701 | -0.21979 | -0.014069 | -0.019408 | -0.10529 | 0.10529 | -0.15564 | -0.13733 | 0.004578 | -0.17395 | -0.07782 | 0.004578 | 0.11444 | -0.14191 | 0.032043 | 0.10071 | 0.018311 | 0.082397 | 122.0489 | -0.009155 | -0.25177 | 122.2092 | 122.1268 | 122.0306 | 0.07782 | -0.01831 | 122.0627 | 0 | -0.082398 | 122.3053 | 122.287 | 122.2229 | 0.2243 | 0.16022 | 0.16022 | 0.018311 | 0.24262 | 0.17395 | 0.26093 | 0.25635 | 122.3099 | 122.319 | -0.27008 | -0.25635 | 122.0673 | 122.2366 | 122.0993 | 122.2092
3044.2344 | 122.3877 | -122.2458 | 0.13733 | -0.0051118 | -0.016293 | -0.079438 | -0.0076199 | -0.033434 | -0.049313 | -0.044237 | -0.0082091 | -0.021176 | 0.0083484 | -0.019961 | -0.21894 | -0.016633 | -0.021971 | -0.07782 | 0.10071 | -0.12817 | -0.09613 | 0.050354 | -0.091553 | -0.022888 | -0.013733 | 0.12817 | -0.13733 | -0.027466 | 0.064087 | -0.004578 | 0.041199 | 122.1176 | -0.036621 | -0.23346 | 122.2961 | 122.2229 | 122.1542 | 0.10529 | 0.036621 | 122.1085 | -0.009155 | -0.16479 | 122.3099 | 122.287 | 122.2412 | 0.17853 | 0.13275 | 0.17853 | 0.032044 | 0.20142 | 0.10986 | 0.22888 | 0.2655 | 122.3465 | 122.374 | -0.2655 | -0.27466 | 122.1497 | 122.2183 | 122.168 | 122.2321
3046.0156 | 122.4976 | -121.9299 | 0.32501 | -0.0051118 | -0.013089 | -0.079224 | -0.0039883 | -0.026171 | -0.049526 | -0.040605 | -0.0021057 | -0.020322 | 0.0079212 | -0.021456 | -0.21958 | -0.017273 | -0.023253 | -0.086975 | 0.10529 | -0.11444 | -0.091553 | 0.068665 | -0.091553 | -0.009155 | 0.07782 | 0.35248 | -0.14191 | 0.32959 | 0.16937 | 0.10071 | 0.16937 | 121.8155 | -0.21973 | -0.41657 | 121.9986 | 121.9208 | 121.8384 | 0.10529 | 0.022888 | 121.788 | 0.027466 | 0.004578 | 122.0993 | 122.0993 | 122.0306 | 0.31128 | 0.24262 | 0.18311 | 0.022888 | 0.31128 | 0.4715 | 0.21973 | 0.49439 | 122.0352 | 122.2824 | -0.43945 | -0.46692 | 121.8384 | 122.2595 | 121.843 | 122.0078
3047.8125 | 122.3923 | -121.7743 | 0.43488 | -0.012741 | -0.013729 | -0.079865 | -0.0061245 | -0.034716 | -0.051876 | -0.039965 | 0.0039979 | -0.021817 | 0.0066394 | -0.022311 | -0.21979 | -0.01706 | -0.020262 | -0.07782 | 0.10986 | -0.091553 | -0.07782 | 0.09613 | -0.068665 | 0.018311 | 0.041199 | 0.44861 | -0.12817 | 0.36163 | 0.14648 | 0.07782 | 0.13275 | 121.6827 | -0.32501 | -0.5127 | 121.8704 | 121.7926 | 121.7056 | 0.10986 | 0.022888 | 121.6461 | 0.013733 | -0.073242 | 121.9208 | 121.907 | 121.8521 | 0.26093 | 0.20599 | 0.18768 | 0.013733 | 0.27466 | 0.48981 | 0.20142 | 0.57678 | 121.8842 | 122.2229 | -0.52643 | -0.56305 | 121.6965 | 122.1359 | 121.6965 | 121.8155
3049.5938 | 122.3099 | -121.669 | 0.45776 | -0.0051118 | -0.010525 | -0.078797 | -0.0050565 | -0.028521 | -0.050595 | -0.039537 | 0.00094606 | -0.018613 | 0.0083484 | -0.022738 | -0.22022 | -0.018555 | -0.021971 | -0.013733 | 0.07782 | -0.073242 | -0.009155 | 0.14648 | -0.045776 | 0.036621 | 0.11902 | 0.47607 | -0.11444 | 0.48065 | 0.19684 | 0.10529 | 0.17853 | 121.5958 | -0.37994 | -0.46692 | 121.8155 | 121.7056 | 121.6232 | 0.10986 | 0.027466 | 121.5546 | 0.01831 | 0.022888 | 121.8658 | 121.8475 | 121.7743 | 0.29297 | 0.21973 | 0.21973 | 0.064087 | 0.31128 | 0.59509 | 0.15106 | 0.59052 | 121.7468 | 122.1451 | -0.53101 | -0.5722 | 121.6599 | 122.1497 | 121.6553 | 121.788
3051.375 | 122.3145 | -121.4493 | 0.6546 | 0.0025177 | -0.017147 | -0.078583 | -0.0048427 | -0.031084 | -0.051663 | -0.040819 | -0.0021057 | -0.021176 | 0.0079212 | -0.024874 | -0.22065 | -0.017701 | -0.027098 | -0.022888 | 0.1236 | -0.068665 | 0.004578 | 0.18768 | 0.022888 | 0.11444 | 0.14648 | 0.6546 | -0.11902 | 0.62714 | 0.23804 | 0.14648 | 0.16937 | 121.3806 | -0.53101 | -0.65002 | 121.637 | 121.5637 | 121.4722 | 0.18311 | 0.091553 | 121.3303 | 0 | -0.027466 | 121.6873 | 121.6187 | 121.5958 | 0.28839 | 0.2655 | 0.25635 | 0.073243 | 0.35706 | 0.74616 | 0.19226 | 0.77362 | 121.5729 | 122.1039 | -0.72327 | -0.77362 | 121.4539 | 122.0764 | 121.4264 | 121.5958
3053.1719 | 122.2 | -121.3531 | 0.71411 | 0.0025177 | -0.014584 | -0.079865 | -0.0048427 | -0.033007 | -0.048458 | -0.040819 | -0.0082091 | -0.022245 | 0.006853 | -0.019534 | -0.21787 | -0.017701 | -0.023894 | -0.050354 | 0.09613 | -0.059509 | -0.032043 | 0.13275 | -0.068665 | 0.018311 | 0.064087 | 0.73242 | -0.11902 | 0.67749 | 0.14648 | 0.073242 | 0.12817 | 121.2936 | -0.61798 | -0.74615 | 121.4859 | 121.3715 | 121.2845 | 0.07782 | -0.009156 | 121.2341 | 0.018311 | -0.036621 | 121.4996 | 121.4813 | 121.4264 | 0.24719 | 0.19226 | 0.19226 | 0.027466 | 0.2655 | 0.79651 | 0.15564 | 0.85144 | 121.4493 | 122.0856 | -0.77362 | -0.83313 | 121.3211 | 122.0306 | 121.3028 | 121.4172
3054.9688 | 122.0764 | -121.2524 | 0.76446 | 0.0025177 | -0.013089 | -0.079011 | -0.0024929 | -0.030871 | -0.051022 | -0.04146 | 0.00094606 | -0.018613 | 0.0089892 | -0.013125 | -0.22043 | -0.015351 | -0.024107 | -0.073242 | 0.15106 | -0.10071 | -0.12817 | 0.009155 | -0.17853 | -0.068665 | -0.032043 | 0.80109 | -0.15564 | 0.63629 | 0.059509 | -0.022888 | 0.041199 | 121.1517 | -0.6134 | -0.89264 | 121.2616 | 121.1838 | 121.0739 | 0.032043 | -0.07782 | 121.0968 | 0.036621 | -0.12817 | 121.312 | 121.2936 | 121.2296 | 0.19684 | 0.13275 | 0.10986 | -0.027466 | 0.21515 | 0.79193 | 0.25177 | 0.95673 | 121.4035 | 122.0535 | -0.86517 | -0.9201 | 121.1243 | 121.8887 | 121.1792 | 121.2204
3056.7656 | 122.0123 | -121.0602 | 0.90179 | 0.0025177 | -0.01202 | -0.078797 | -0.0018521 | -0.027666 | -0.050167 | -0.041246 | -0.0021057 | -0.018613 | 0.0072802 | -0.0099206 | -0.21723 | -0.015351 | -0.024962 | -0.032043 | 0.15106 | -0.091553 | -0.064087 | 0.07782 | -0.09613 | -0.018311 | 0.022888 | 0.91553 | -0.14648 | 0.7782 | 0.10986 | -0.004578 | 0.086975 | 120.9686 | -0.75073 | -0.96588 | 121.138 | 121.0419 | 120.9641 | 0.073242 | -0.004577 | 120.9137 | 0.013733 | -0.1236 | 121.17 | 121.1472 | 121.0556 | 0.23346 | 0.14191 | 0.16937 | 0.027466 | 0.25635 | 0.92468 | 0.24261 | 1.062 | 121.2112 | 121.9757 | -0.99335 | -1.0483 | 120.9961 | 121.8384 | 121.0281 | 121.0831
3058.5625 | 122.0856 | -120.9412 | 0.89264 | -0.0051118 | -0.013729 | -0.080719 | -0.0067653 | -0.031298 | -0.049526 | -0.045305 | 0.00094606 | -0.017331 | 0.0045032 | -0.01932 | -0.21808 | -0.017487 | -0.016844 | -0.032043 | 0.11444 | -0.054932 | 0.013733 | 0.18768 | 0.032043 | 0.10529 | 0.13733 | 0.90637 | -0.11444 | 0.90179 | 0.28839 | 0.16479 | 0.93384 | 120.8862 | -0.7782 | -0.87891 | 121.1288 | 121.0464 | 120.9732 | 0.16022 | 0.086975 | 120.8267 | 0.013733 | 0.009155 | 121.2296 | 121.875 | 121.106 | 1.0483 | 0.27924 | 0.24261 | 0.068665 | 0.40283 | 1.0162 | 0.16937 | 1.0208 | 121.0556 | 121.8475 | -0.94757 | -1.0071 | 120.9549 | 121.843 | 120.9091 | 121.0785
3060.2812 | 122.0306 | -121.17 | 0.60425 | -0.0051118 | -0.013516 | -0.080506 | -0.0076199 | -0.034289 | -0.050167 | -0.041246 | -0.0051575 | -0.020749 | 0.0045032 | -0.019747 | -0.21958 | -0.018555 | -0.019194 | -0.068665 | 0.14191 | -0.091553 | -0.027466 | 0.10071 | -0.041199 | 0.045776 | 0.059509 | 0.58594 | -0.13733 | 0.59967 | 0.23346 | 0.11444 | 0.6546 | 121.0785 | -0.46234 | -0.63171 | 121.2708 | 121.2158 | 121.1288 | 0.13733 | 0.050354 | 121.0327 | -0.018311 | -0.004578 | 121.4035 | 121.8246 | 121.2845 | 0.79193 | 0.25177 | 0.19226 | 0.064087 | 0.37079 | 0.737 | 0.23346 | 0.72327 | 121.312 | 121.756 | -0.6958 | -0.74158 | 121.1426 | 121.7697 | 121.1014 | 121.2296
3062.0625 | 122.0078 | -120.8176 | 0.94299 | -0.0051118 | -0.014157 | -0.076874 | -0.0037747 | -0.031298 | -0.050381 | -0.041674 | -0.0051575 | -0.016477 | 0.0019398 | -0.024233 | -0.22172 | -0.018982 | -0.016844 | 0.009155 | 0.12817 | -0.045776 | 0.022888 | 0.16937 | -0.009155 | 0.064087 | 0.12817 | 0.94299 | -0.1236 | 0.97961 | 0.27008 | 0.1236 | 0.99792 | 120.7718 | -0.81482 | -0.9201 | 120.9869 | 120.8817 | 120.8084 | 0.10986 | 0.036621 | 120.694 | 0 | 0.036621 | 121.0876 | 121.8155 | 120.9412 | 1.1215 | 0.24719 | 0.21515 | 0.068664 | 0.39368 | 1.1032 | 0.17395 | 1.0666 | 120.9457 | 121.7606 | -0.98877 | -1.0666 | 120.8405 | 121.7972 | 120.8267 | 120.9457
3063.8594 | 121.843 | -120.3186 | 1.3184 | -0.0051118 | -0.019711 | -0.080933 | -0.0050565 | -0.030871 | -0.050381 | -0.040819 | -0.0021057 | -0.014554 | 0.001726 | -0.021029 | -0.22043 | -0.018982 | -0.01599 | 0.018311 | 0.15564 | -0.013733 | 0.059509 | 0.21973 | 0.050354 | 0.11444 | 0.13275 | 1.3596 | -0.10986 | 1.3229 | 0.27924 | 0.16937 | 1.3916 | 120.3049 | -1.1627 | -1.2589 | 120.5383 | 120.433 | 120.369 | 0.12817 | 0.064087 | 120.2087 | 0.041199 | 0.004578 | 120.5978 | 121.7102 | 120.488 | 1.5015 | 0.27924 | 0.23346 | 0.073242 | 0.3891 | 1.4328 | 0.16937 | 1.4694 | 120.4742 | 121.6782 | -1.3321 | -1.4282 | 120.3781 | 121.6415 | 120.3369 | 120.4514
3065.6562 | 121.756 | -120.7764 | 0.86517 | 0.0025177 | -0.015652 | -0.079651 | -0.0059109 | -0.032152 | -0.051449 | -0.040605 | -0.0021057 | -0.018827 | 0.0019398 | -0.02167 | -0.22022 | -0.01706 | -0.017485 | -0.068665 | 0.12817 | -0.07782 | -0.041199 | 0.10071 | -0.064087 | 0.036621 | 0.018311 | 0.91095 | -0.13733 | 0.82398 | 0.17853 | 0.10986 | 0.89264 | 120.6985 | -0.737 | -0.90637 | 120.8771 | 120.813 | 120.7123 | 0.11444 | 0.013733 | 120.639 | 0.045777 | -0.041198 | 120.9549 | 121.669 | 120.8862 | 1.03 | 0.24719 | 0.17853 | 0.036621 | 0.31586 | 0.9613 | 0.20599 | 1.0483 | 120.9045 | 121.6873 | -0.94299 | -1.0025 | 120.7352 | 121.6003 | 120.7077 | 120.7947
3067.375 | 121.7285 | -120.7672 | 0.93384 | -0.012741 | -0.0092435 | -0.078797 | -0.0016385 | -0.031084 | -0.051235 | -0.039965 | -0.0051575 | -0.013913 | 0.001726 | -0.01697 | -0.22107 | -0.018555 | -0.018126 | -0.086975 | 0.1831 | -0.091553 | -0.13275 | -0.022888 | -0.17853 | -0.059509 | -0.068665 | 0.95673 | -0.14648 | 0.76904 | 0.059509 | -0.032043 | 0.87433 | 120.6757 | -0.75073 | -1.0666 | 120.7443 | 120.7077 | 120.5887 | 0.032044 | -0.086975 | 120.6207 | 0.022888 | -0.16479 | 120.8267 | 121.6415 | 120.7352 | 1.0208 | 0.11444 | 0.068665 | -0.041198 | 0.20599 | 0.91553 | 0.27466 | 1.1032 | 120.9503 | 121.7239 | -1.0254 | -1.0803 | 120.6345 | 121.5363 | 120.6802 | 120.6985
3069.1719 | 121.5134 | -118.602 | 2.7878 | -0.0051118 | -0.01672 | -0.079224 | 0.00092508 | -0.027453 | -0.050167 | -0.042314 | -0.0051575 | 0.18732 | -0.0087414 | 0.10693 | -0.21958 | -0.017487 | -0.0072311 | 0.041199 | 0.27008 | 0.022888 | 0.032043 | 0.17853 | 0.022888 | 0.11902 | 0.013733 | 2.8015 | -0.13733 | 2.6825 | 0.20599 | 0.1236 | 2.7145 | 118.6249 | -2.5177 | -2.7557 | 118.7805 | 118.721 | 118.6249 | 0.096131 | 0 | 118.4647 | 0.013733 | -0.10529 | 118.808 | 121.3165 | 118.7256 | 2.8519 | 0.26093 | 0.15564 | 0.009155 | 0.34332 | 2.8198 | 0.24719 | 2.9388 | 118.8721 | 121.4035 | -2.7649 | -2.9251 | 118.634 | 121.2845 | 118.6432 | 118.6157
3070.9531 | 121.3898 | -120.3232 | 0.99335 | -0.02037 | -0.013943 | -0.077942 | -0.0056973 | -0.028734 | -0.050595 | -0.042101 | 0.00094606 | 2.032 | 0.0047168 | 1.4237 | -0.21808 | -0.016846 | -0.021758 | -0.041199 | 0.14191 | -0.091553 | -0.059509 | 0.091553 | -0.073242 | 0.004578 | 0.050354 | 0.71869 | -0.11902 | 0.55847 | 0.21057 | 0.064087 | 0.24719 | 120.2316 | -0.85144 | -1.0529 | 120.4147 | 120.3278 | 120.2499 | 0.096131 | 0.018311 | 120.2042 | -0.27466 | -0.43488 | 120.5338 | 120.5704 | 120.3873 | 0.36621 | 0.18311 | 0.18311 | 0.032044 | 0.32959 | 0.67749 | 0.23346 | 0.83771 | 120.4651 | 121.0419 | -1.0849 | -1.1124 | 120.2637 | 120.8817 | 120.282 | 120.3735
3072.75 | 121.6507 | -120.6665 | 0.70953 | -0.0051118 | -0.011166 | -0.078797 | -0.0039883 | -0.031511 | -0.04974 | -0.040819 | -0.0051575 | 1.4342 | 0.0059986 | 0.99881 | -0.21915 | -0.017487 | -0.023039 | -0.013733 | 0.12817 | -0.073242 | -0.009155 | 0.14648 | -0.041199 | 0.045776 | 0.11902 | 0.50354 | -0.09613 | 0.49896 | 0.27466 | 0.12817 | 0.27466 | 120.5933 | -0.58136 | -0.71869 | 120.813 | 120.7123 | 120.6253 | 0.11902 | 0.032043 | 120.5704 | -0.20599 | -0.21057 | 120.9412 | 120.9412 | 120.7947 | 0.37079 | 0.2243 | 0.21973 | 0.064087 | 0.37079 | 0.59509 | 0.20142 | 0.59967 | 120.7947 | 121.17 | -0.78278 | -0.80566 | 120.6573 | 121.1655 | 120.6528 | 120.7855
3074.4844 | 121.5866 | -121.5408 | 0.10529 | 0.0025177 | -0.010952 | -0.077729 | -0.0044155 | -0.028093 | -0.04974 | -0.039751 | -0.0021057 | 0.016208 | 0.010057 | 0.0007606 | -0.22193 | -0.016205 | -0.024535 | -0.10071 | 0.11444 | -0.12817 | -0.086975 | 0.045776 | -0.11444 | -0.018311 | 0.082397 | 0.09613 | -0.14191 | 0.091553 | 0.1831 | 0.091553 | 0.15106 | 121.4127 | 0.009155 | -0.19226 | 121.5866 | 121.5225 | 121.4264 | 0.10986 | 0.013733 | 121.3989 | -0.009156 | -0.013733 | 121.7239 | 121.6919 | 121.6324 | 0.29297 | 0.23346 | 0.17395 | 0.041199 | 0.32501 | 0.23346 | 0.24262 | 0.23804 | 121.6553 | 121.637 | -0.23346 | -0.24719 | 121.4539 | 121.6324 | 121.4401 | 121.6232
3076.2656 | 121.8109 | -121.5317 | 0.091553 | -0.0051118 | -0.011807 | -0.078156 | -0.0069791 | -0.030443 | -0.049099 | -0.042955 | -0.0021057 | 0.084781 | 0.0094166 | 0.040281 | -0.21894 | -0.017914 | -0.021971 | -0.045776 | 0.082397 | -0.10071 | -0.027466 | 0.13275 | -0.064087 | 0.041199 | 0.12817 | 0.10986 | -0.10529 | 0.09613 | 0.17853 | 0.09613 | 0.16479 | 121.431 | -0.009156 | -0.11902 | 121.6644 | 121.5729 | 121.4676 | 0.14191 | 0.036621 | 121.4264 | 0.01831 | 0.004577 | 121.7102 | 121.6965 | 121.6278 | 0.27008 | 0.20142 | 0.23346 | 0.073242 | 0.28381 | 0.20142 | 0.18311 | 0.21515 | 121.6141 | 121.6415 | -0.19226 | -0.19684 | 121.5042 | 121.6278 | 121.4859 | 121.6599
3078 | 121.7651 | -121.4218 | 0.2243 | -0.0051118 | -0.01138 | -0.080719 | -0.0059109 | -0.031725 | -0.050167 | -0.037615 | 0.00094606 | 0.30823 | 0.005785 | 0.23596 | -0.22043 | -0.017701 | -0.02603 | -0.050354 | 0.073242 | -0.086975 | -0.041199 | 0.12817 | -0.073242 | 0.022888 | 0.10986 | 0.18768 | -0.11902 | 0.16022 | 0.17395 | 0.086975 | 0.16937 | 121.3348 | -0.15106 | -0.2655 | 121.55 | 121.4447 | 121.3486 | 0.10986 | 0.013733 | 121.3028 | -0.036621 | -0.064087 | 121.5958 | 121.5912 | 121.5088 | 0.28839 | 0.20599 | 0.21515 | 0.045776 | 0.29297 | 0.27924 | 0.16022 | 0.3067 | 121.4951 | 121.6095 | -0.31128 | -0.34332 | 121.3806 | 121.582 | 121.3715 | 121.5317
3079.7969 | 121.7285 | -121.6232 | 0.14191 | -0.012741 | -0.0096707 | -0.079011 | -0.0048427 | -0.027025 | -0.050167 | -0.039537 | 0.00094606 | 0.010653 | 0.008562 | 0.0090918 | -0.22107 | -0.014069 | -0.026244 | -0.073242 | 0.11444 | -0.13275 | -0.13733 | 0.009155 | -0.16479 | -0.091553 | -0.018311 | 0.12817 | -0.14191 | -0.032043 | 0.041199 | -0.050354 | 0.054932 | 121.4905 | -0.027466 | -0.27924 | 121.6324 | 121.5317 | 121.4584 | 0.041198 | -0.032044 | 121.4813 | -0.013733 | -0.17395 | 121.6644 | 121.6782 | 121.5729 | 0.19684 | 0.091553 | 0.14191 | -0.004578 | 0.18311 | 0.10986 | 0.24719 | 0.27008 | 121.7377 | 121.7514 | -0.27466 | -0.28381 | 121.4859 | 121.5912 | 121.55 | 121.6049
3081.5938 | 121.907 | -121.756 | 0.13733 | 0.0025177 | -0.010739 | -0.078583 | -0.0054837 | -0.031298 | -0.051876 | -0.042101 | 0.00094606 | 0.0065946 | 0.0087756 | -0.007998 | -0.2215 | -0.017701 | -0.023039 | -0.13275 | 0.1236 | -0.13733 | -0.16022 | -0.013733 | -0.15106 | -0.082397 | -0.045776 | 0.12817 | -0.15564 | -0.041199 | 0.082397 | 0.009155 | 0.064087 | 121.6187 | -0.013733 | -0.29755 | 121.7422 | 121.6736 | 121.6049 | 0.054932 | -0.013733 | 121.6003 | -0.009155 | -0.17853 | 121.8384 | 121.8201 | 121.7651 | 0.21973 | 0.16479 | 0.1236 | -0.022888 | 0.23804 | 0.11444 | 0.26093 | 0.28381 | 121.8796 | 121.8842 | -0.27466 | -0.29297 | 121.5958 | 121.7148 | 121.6232 | 121.7102
3083.375 | 121.907 | -121.5637 | 0.1236 | 0.0025177 | -0.010525 | -0.077729 | -0.0059109 | -0.030016 | -0.048458 | -0.039751 | 0.00094606 | 0.066836 | 0.010057 | 0.045408 | -0.21872 | -0.016846 | -0.02838 | -0.041199 | 0.086975 | -0.086975 | -0.022888 | 0.13733 | -0.045776 | 0.022888 | 0.14648 | 0.1236 | -0.10529 | 0.10529 | 0.16022 | 0.11902 | 0.15564 | 121.4767 | -0.036621 | -0.14648 | 121.701 | 121.5866 | 121.5179 | 0.10986 | 0.041199 | 121.4584 | 0 | -0.01831 | 121.7239 | 121.7194 | 121.6827 | 0.26093 | 0.22431 | 0.2243 | 0.064087 | 0.2655 | 0.21057 | 0.17395 | 0.22888 | 121.6507 | 121.6873 | -0.21057 | -0.22888 | 121.5408 | 121.669 | 121.5225 | 121.7102
3085.1562 | 121.6003 | -121.3028 | 0.13275 | 0.010147 | -0.010525 | -0.080079 | -0.0033475 | -0.031939 | -0.050595 | -0.037615 | -0.0051575 | 0.11682 | 0.0072802 | 0.07147 | -0.22236 | -0.01706 | -0.021971 | -0.082397 | 0.11444 | -0.11902 | -0.064087 | 0.086975 | -0.10071 | -0.004578 | 0.10529 | 0.13733 | -0.11902 | 0.10071 | 0.1831 | 0.1236 | 0.17395 | 121.1838 | -0.01831 | -0.19684 | 121.3898 | 121.2982 | 121.2021 | 0.11444 | 0.018311 | 121.1838 | 0.004578 | -0.032043 | 121.4859 | 121.4767 | 121.4264 | 0.29297 | 0.24261 | 0.20599 | 0.054932 | 0.30212 | 0.21973 | 0.23346 | 0.25635 | 121.4172 | 121.4401 | -0.25177 | -0.25177 | 121.2387 | 121.4035 | 121.2204 | 121.4081
3086.8906 | 118.3273 | -118.2953 | 0.21057 | -0.012741 | -0.012448 | -0.077729 | -0.0031337 | -0.033007 | -0.049526 | -0.039751 | 0.00094606 | 0.23816 | 0.006853 | 0.16076 | -0.21937 | -0.017914 | -0.02133 | -0.1236 | 0.11444 | -0.13275 | -0.15564 | -0.054932 | -0.19684 | -0.10986 | -0.082397 | 0.20599 | -0.15564 | 0.018311 | 0.041199 | -0.027466 | 0.054932 | 118.1625 | -0.09613 | -0.36621 | 118.2404 | 118.1854 | 118.0984 | 0.022888 | -0.064087 | 118.1396 | -0.004577 | -0.19226 | 118.3365 | 118.3502 | 118.2678 | 0.21057 | 0.12817 | 0.077819 | -0.022889 | 0.19684 | 0.17395 | 0.24719 | 0.36163 | 118.4097 | 118.5013 | -0.34332 | -0.36621 | 118.1396 | 118.3136 | 118.1717 | 118.2129
3088.6875 | 121.5134 | -120.726 | 0.55847 | 0.0025177 | -0.017361 | -0.080506 | -0.0071927 | -0.035143 | -0.050167 | -0.039965 | 0.0039979 | 1.0657 | 0.0066394 | 0.7525 | -0.21808 | -0.017273 | -0.021971 | -0.032043 | 0.09613 | -0.073242 | 0.009155 | 0.20599 | 0.041199 | 0.086975 | 0.13733 | 0.42572 | -0.091553 | 0.37994 | 0.29297 | 0.22888 | 0.23804 | 120.6528 | -0.46234 | -0.54932 | 120.932 | 120.813 | 120.7672 | 0.16022 | 0.11444 | 120.6345 | -0.13275 | -0.17853 | 121.019 | 120.9641 | 120.9549 | 0.32959 | 0.32044 | 0.27924 | 0.082397 | 0.38452 | 0.4715 | 0.16937 | 0.51727 | 120.8221 | 121.1517 | -0.63171 | -0.65002 | 120.7352 | 121.106 | 120.694 | 120.8633
3090.4062 | 121.3257 | -120.7031 | 0.39825 | 0.0025177 | -0.010952 | -0.077515 | -0.0065517 | -0.030657 | -0.04974 | -0.041246 | 0.00094606 | 0.70792 | 0.0079212 | 0.50128 | -0.22193 | -0.018555 | -0.022185 | -0.045776 | 0.10071 | -0.073242 | -0.036621 | 0.13275 | -0.050354 | 0.022888 | 0.09613 | 0.3067 | -0.10071 | 0.23346 | 0.19684 | 0.073242 | 0.17853 | 120.6299 | -0.29755 | -0.43488 | 120.8359 | 120.726 | 120.6528 | 0.09613 | 0.022888 | 120.6024 | -0.091552 | -0.16479 | 120.9 | 120.8817 | 120.7764 | 0.27924 | 0.17395 | 0.20599 | 0.036621 | 0.29755 | 0.33417 | 0.17395 | 0.40741 | 120.8038 | 121.0098 | -0.4715 | -0.49896 | 120.6665 | 120.9366 | 120.6573 | 120.7993
3092.1875 | 121.138 | -120.8679 | 0.2243 | -0.012741 | -0.012661 | -0.078583 | -0.0039883 | -0.031511 | -0.050808 | -0.041033 | -0.0051575 | 0.30823 | 0.0081348 | 0.17315 | -0.22022 | -0.017487 | -0.024107 | -0.064087 | 0.10071 | -0.11444 | -0.07782 | 0.050354 | -0.10529 | -0.013733 | 0.041199 | 0.21515 | -0.11902 | 0.10986 | 0.13275 | 0.027466 | 0.10529 | 120.7535 | -0.1236 | -0.30212 | 120.9183 | 120.8542 | 120.7626 | 0.10071 | 0.009155 | 120.7489 | -0.009155 | -0.11444 | 121.0007 | 120.9732 | 120.8954 | 0.22431 | 0.14649 | 0.16479 | 0.036621 | 0.25177 | 0.22888 | 0.21515 | 0.33417 | 120.9686 | 121.0831 | -0.33875 | -0.34332 | 120.7901 | 120.9778 | 120.8038 | 120.9091
3093.9844 | 121.4447 | -121.2799 | 0.11444 | -0.012741 | -0.010739 | -0.079438 | -0.0048427 | -0.028521 | -0.050595 | -0.043169 | -0.0051575 | 0.013431 | 0.0092028 | 0.0075964 | -0.22001 | -0.01706 | -0.021971 | -0.13275 | 0.12817 | -0.13733 | -0.17853 | -0.022888 | -0.1831 | -0.091553 | -0.018311 | 0.13275 | -0.14648 | 0.018311 | 0.068665 | -0.018311 | 0.068665 | 121.1426 | 0.013733 | -0.29297 | 121.257 | 121.1884 | 121.0968 | 0.045776 | -0.045776 | 121.1334 | 0.01831 | -0.09613 | 121.3486 | 121.3486 | 121.2616 | 0.21515 | 0.12817 | 0.11444 | -0.041199 | 0.21515 | 0.16479 | 0.2655 | 0.27924 | 121.4081 | 121.4127 | -0.25177 | -0.26093 | 121.1014 | 121.2982 | 121.1472 | 121.2616
3095.7188 | 121.2524 | -120.9641 | 0.09613 | 0.0025177 | -0.012448 | -0.079438 | -0.0078335 | -0.02788 | -0.050808 | -0.042742 | -0.0021057 | 0.030948 | 0.0066394 | 0.006742 | -0.22043 | -0.020905 | -0.025389 | -0.068665 | 0.082397 | -0.091553 | -0.050354 | 0.12817 | -0.07782 | 0.009155 | 0.10529 | 0.10529 | -0.09613 | 0.068665 | 0.13275 | 0.059509 | 0.1236 | 120.8725 | -0.013733 | -0.14648 | 121.0922 | 120.9732 | 120.8862 | 0.10071 | 0.013733 | 120.8679 | 0.009156 | -0.027465 | 121.0968 | 121.0876 | 121.0236 | 0.21973 | 0.15564 | 0.21973 | 0.041199 | 0.22888 | 0.16479 | 0.17395 | 0.20142 | 121.0464 | 121.0693 | -0.18768 | -0.19226 | 120.9137 | 121.0327 | 120.8954 | 121.0693
3097.5156 | 121.0007 | -120.845 | 0.14191 | 0.0025177 | -0.013089 | -0.078156 | -0.0056973 | -0.033861 | -0.050381 | -0.04146 | 0.00094606 | 0.015994 | 0.0096302 | 0.015073 | -0.22065 | -0.018982 | -0.026885 | -0.12817 | 0.1236 | -0.16022 | -0.16022 | -0.009155 | -0.14648 | -0.073242 | -0.059509 | 0.13733 | -0.16479 | -0.027466 | 0.082397 | 0 | 0.064087 | 120.6848 | -0.018311 | -0.30212 | 120.8359 | 120.7718 | 120.6985 | 0.086975 | 0.013733 | 120.6802 | -0.004578 | -0.16937 | 120.9274 | 120.9091 | 120.845 | 0.22888 | 0.16479 | 0.15106 | 0 | 0.24719 | 0.13733 | 0.28381 | 0.30212 | 120.9686 | 120.9824 | -0.30212 | -0.3067 | 120.6848 | 120.8176 | 120.7169 | 120.7855
3099.25 | 121.2708 | -121.0968 | 0.12817 | -0.0051118 | -0.012448 | -0.080506 | -0.0080471 | -0.030657 | -0.051022 | -0.042101 | 0.00094606 | -0.00066861 | 0.008562 | -0.0075708 | -0.22001 | -0.015351 | -0.023039 | -0.14191 | 0.10986 | -0.14648 | -0.17395 | -0.018311 | -0.13275 | -0.064087 | -0.064087 | 0.15106 | -0.15106 | -0.064087 | 0.041199 | -0.032043 | 0.050354 | 120.9503 | -0.018311 | -0.30212 | 121.0785 | 121.0327 | 120.9641 | 0.082397 | 0.013733 | 120.9457 | 0.022888 | -0.19226 | 121.138 | 121.1472 | 121.0648 | 0.20142 | 0.11902 | 0.12817 | -0.027466 | 0.19226 | 0.086975 | 0.25635 | 0.30212 | 121.2067 | 121.2479 | -0.27466 | -0.27924 | 120.9229 | 121.0327 | 120.9549 | 121.0327
3101.0312 | 121.4905 | -121.3303 | 0.09613 | 0.0025177 | -0.011807 | -0.081574 | -0.0056973 | -0.028948 | -0.050381 | -0.04146 | 0.00094606 | -0.00066861 | 0.0072802 | -0.0050072 | -0.21979 | -0.017487 | -0.022826 | -0.13275 | 0.12817 | -0.13733 | -0.17853 | -0.041199 | -0.19226 | -0.091553 | -0.041199 | 0.13733 | -0.14648 | -0.032043 | 0.036621 | -0.036621 | 0.045776 | 121.1929 | 0.032044 | -0.27466 | 121.2891 | 121.2387 | 121.138 | 0.045776 | -0.054932 | 121.1838 | 0.041199 | -0.12817 | 121.3669 | 121.376 | 121.2936 | 0.19226 | 0.10986 | 0.09613 | -0.041199 | 0.18311 | 0.11444 | 0.2655 | 0.28381 | 121.4584 | 121.4676 | -0.23346 | -0.24261 | 121.1517 | 121.2982 | 121.1975 | 121.2891
3102.8281 | 121.5134 | -121.3898 | 0.11902 | 0.0025177 | -0.0098843 | -0.078797 | -0.0052701 | -0.032366 | -0.049313 | -0.041674 | 0.00094606 | -0.003873 | 0.010698 | -0.0090662 | -0.22022 | -0.018128 | -0.021544 | -0.13733 | 0.11902 | -0.12817 | -0.17395 | -0.059509 | -0.21515 | -0.1236 | -0.086975 | 0.13733 | -0.16022 | -0.036621 | 0.018311 | -0.050354 | 0.054932 | 121.2616 | 0 | -0.29297 | 121.3303 | 121.2662 | 121.1746 | 0.004578 | -0.086975 | 121.2296 | 0.01831 | -0.15564 | 121.4081 | 121.4447 | 121.3394 | 0.21515 | 0.10986 | 0.068665 | -0.045776 | 0.17853 | 0.1236 | 0.24719 | 0.29755 | 121.5088 | 121.5271 | -0.24719 | -0.27924 | 121.2158 | 121.3531 | 121.2524 | 121.3028
3104.5469 | 121.7285 | -121.3852 | 0.091553 | -0.012741 | -0.013302 | -0.082001 | -0.0091153 | -0.030016 | -0.051663 | -0.038042 | -0.0021057 | -0.0057956 | 0.0083484 | -0.00693 | -0.21915 | -0.016419 | -0.026671 | -0.091553 | 0.091553 | -0.10529 | -0.054932 | 0.14648 | -0.013733 | 0.054932 | 0.10986 | 0.10986 | -0.1236 | 0.082397 | 0.20599 | 0.13275 | 0.16937 | 121.2799 | 0 | -0.14649 | 121.5317 | 121.4401 | 121.3715 | 0.16022 | 0.091553 | 121.2616 | 0.01831 | -0.009156 | 121.5912 | 121.5546 | 121.5179 | 0.29297 | 0.25635 | 0.25177 | 0.050354 | 0.32959 | 0.20599 | 0.19684 | 0.23346 | 121.4767 | 121.4951 | -0.19684 | -0.21515 | 121.3303 | 121.4676 | 121.2936 | 121.4951
3106.3281 | 121.7514 | -121.4172 | 0.086975 | -0.012741 | -0.011166 | -0.077942 | -0.0042019 | -0.027666 | -0.047817 | -0.044237 | -0.0021057 | -0.005582 | 0.0066394 | -0.011843 | -0.21979 | -0.016846 | -0.02368 | -0.059509 | 0.082397 | -0.091553 | -0.036621 | 0.10986 | -0.073242 | 0.013733 | 0.11444 | 0.10986 | -0.09613 | 0.10529 | 0.17853 | 0.10986 | 0.14648 | 121.3257 | -0.004578 | -0.1236 | 121.5271 | 121.431 | 121.344 | 0.10529 | 0.018311 | 121.3211 | 0.022888 | 0.018311 | 121.5958 | 121.5637 | 121.5271 | 0.24261 | 0.20599 | 0.20142 | 0.054932 | 0.27466 | 0.20142 | 0.17395 | 0.20599 | 121.4996 | 121.5271 | -0.17853 | -0.1831 | 121.3806 | 121.5225 | 121.3577 | 121.5317
3108.1094 | 121.7514 | -121.4447 | 0.07782 | 0.0025177 | -0.010311 | -0.078156 | -0.0061245 | -0.029802 | -0.04974 | -0.040178 | 0.0039979 | -0.0034458 | 0.0062122 | -0.012911 | -0.22107 | -0.016419 | -0.02603 | -0.050354 | 0.073242 | -0.091553 | -0.018311 | 0.13733 | -0.054932 | 0.018311 | 0.11902 | 0.09613 | -0.1236 | 0.09613 | 0.16937 | 0.10071 | 0.15564 | 121.3531 | -0.004578 | -0.096131 | 121.582 | 121.463 | 121.3898 | 0.10986 | 0.036621 | 121.3211 | 0.01831 | 0.01831 | 121.6141 | 121.6003 | 121.5454 | 0.27924 | 0.2243 | 0.22888 | 0.073242 | 0.29297 | 0.21973 | 0.16479 | 0.21973 | 121.5179 | 121.5408 | -0.16937 | -0.20142 | 121.4264 | 121.5408 | 121.3943 | 121.5637
3109.9062 | 121.7194 | -121.5271 | 0.1236 | 0.0025177 | -0.012661 | -0.080933 | -0.0048427 | -0.03258 | -0.050167 | -0.038042 | 0.00094606 | -0.00024141 | 0.008562 | -0.010348 | -0.22001 | -0.018128 | -0.024535 | -0.10529 | 0.10529 | -0.14648 | -0.13275 | -0.013733 | -0.13733 | -0.064087 | -0.027466 | 0.12817 | -0.15106 | -0.009155 | 0.091553 | 0.022888 | 0.082397 | 121.3806 | -0.01831 | -0.25635 | 121.5134 | 121.463 | 121.3898 | 0.082397 | 0.009155 | 121.376 | 0.004578 | -0.13275 | 121.6187 | 121.6095 | 121.55 | 0.23346 | 0.17395 | 0.13275 | 0.013733 | 0.24261 | 0.14191 | 0.25177 | 0.27924 | 121.6324 | 121.6553 | -0.27008 | -0.27466 | 121.3943 | 121.5179 | 121.4218 | 121.4996
3111.6875 | 121.6965 | -121.5546 | 0.12817 | -0.0051118 | -0.017147 | -0.079865 | -0.0078335 | -0.031939 | -0.051022 | -0.043169 | 0.00094606 | -0.001523 | 0.010271 | -0.010775 | -0.21894 | -0.017273 | -0.025603 | -0.13275 | 0.12817 | -0.14191 | -0.17395 | -0.018311 | -0.14648 | -0.073242 | -0.054932 | 0.15106 | -0.16479 | -0.045776 | 0.041199 | 0 | 0.054932 | 121.4127 | 0 | -0.30212 | 121.5363 | 121.4813 | 121.4081 | 0.068665 | -0.004577 | 121.3898 | 0.022888 | -0.17395 | 121.5958 | 121.6095 | 121.5546 | 0.21973 | 0.16479 | 0.1236 | -0.032043 | 0.20599 | 0.11902 | 0.27008 | 0.31586 | 121.6827 | 121.7056 | -0.27008 | -0.29297 | 121.3806 | 121.5088 | 121.4218 | 121.4996
3113.4062 | 121.7606 | -121.5546 | 0.13275 | -0.012741 | -0.013302 | -0.077942 | -0.0059109 | -0.030443 | -0.050381 | -0.043596 | -0.0051575 | 0.00018579 | 0.0081348 | -0.013552 | -0.22172 | -0.015351 | -0.020689 | -0.07782 | 0.10071 | -0.11902 | -0.10986 | 0.045776 | -0.10071 | -0.050354 | 0.041199 | 0.14648 | -0.12817 | 0.013733 | 0.11444 | 0.045776 | 0.10986 | 121.4355 | -0.032043 | -0.24261 | 121.6003 | 121.5042 | 121.4539 | 0.068665 | 0.018311 | 121.4264 | 0.013733 | -0.11902 | 121.669 | 121.6644 | 121.6003 | 0.23804 | 0.17395 | 0.16479 | 0.009156 | 0.24262 | 0.14191 | 0.21973 | 0.27466 | 121.6553 | 121.701 | -0.25177 | -0.26093 | 121.4447 | 121.5683 | 121.4767 | 121.5958
3115.1875 | 121.7789 | -121.582 | 0.09613 | -0.0051118 | -0.013729 | -0.080933 | -0.0061245 | -0.028093 | -0.051876 | -0.038469 | -0.0021057 | -0.00024141 | 0.010057 | -0.010989 | -0.21894 | -0.01706 | -0.025389 | -0.1236 | 0.11902 | -0.14191 | -0.14191 | 0.004578 | -0.12817 | -0.068665 | -0.013733 | 0.13733 | -0.15106 | -0.004578 | 0.09613 | 0.027466 | 0.07782 | 121.4401 | 0.022889 | -0.23804 | 121.5866 | 121.5134 | 121.4539 | 0.073242 | 0.013733 | 121.431 | 0.041199 | -0.10071 | 121.6782 | 121.6599 | 121.6095 | 0.22888 | 0.17853 | 0.14649 | 0 | 0.24719 | 0.14648 | 0.26093 | 0.28839 | 121.701 | 121.7194 | -0.23804 | -0.24719 | 121.4401 | 121.5775 | 121.4584 | 121.5683
3116.9531 | 121.7972 | -121.6187 | 0.12817 | 0.0025177 | -0.014157 | -0.078156 | -0.0059109 | -0.030443 | -0.051876 | -0.040392 | 0.00094606 | 0.00061319 | 0.011125 | -0.010134 | -0.21979 | -0.017701 | -0.023894 | -0.10986 | 0.11444 | -0.12817 | -0.14191 | 0.004578 | -0.13275 | -0.054932 | -0.013733 | 0.14191 | -0.14648 | 0.018311 | 0.10071 | 0.022888 | 0.073242 | 121.4905 | -0.013733 | -0.27008 | 121.6232 | 121.5637 | 121.4859 | 0.073242 | -0.004577 | 121.4722 | 0.013733 | -0.10986 | 121.7194 | 121.6919 | 121.6415 | 0.21973 | 0.16937 | 0.13275 | -0.013733 | 0.24719 | 0.16479 | 0.24262 | 0.28839 | 121.7331 | 121.7606 | -0.25635 | -0.27466 | 121.4767 | 121.637 | 121.5088 | 121.6049
3118.7344 | 121.7834 | -121.6278 | 0.11902 | -0.0051118 | -0.012661 | -0.078797 | -0.0080471 | -0.035357 | -0.053372 | -0.039537 | 0.00094606 | -0.0051546 | 0.008562 | -0.013125 | -0.2183 | -0.018555 | -0.020903 | -0.068665 | 0.091553 | -0.11902 | -0.09613 | 0.073242 | -0.068665 | -0.013733 | 0 | 0.12817 | -0.13733 | -0.032043 | 0.07782 | 0.018311 | 0.064087 | 121.5088 | -0.027466 | -0.21515 | 121.701 | 121.6141 | 121.5591 | 0.10529 | 0.050354 | 121.4905 | 0.009155 | -0.15106 | 121.7056 | 121.6919 | 121.6461 | 0.20142 | 0.15564 | 0.19226 | 0.022889 | 0.21515 | 0.10529 | 0.21057 | 0.2655 | 121.7194 | 121.756 | -0.23804 | -0.25635 | 121.5317 | 121.5958 | 121.5591 | 121.6278
3120.5312 | 121.788 | -121.6599 | 0.14648 | 0.0025177 | -0.013729 | -0.080719 | -0.0065517 | -0.030871 | -0.049313 | -0.03911 | 0.0039979 | -0.0023776 | 0.0081348 | -0.012698 | -0.21744 | -0.018128 | -0.020903 | -0.15106 | 0.11902 | -0.14191 | -0.16479 | -0.004578 | -0.13733 | -0.068665 | -0.050354 | 0.13733 | -0.15106 | -0.064087 | 0.045776 | 0 | 0.045776 | 121.5179 | -0.027465 | -0.31128 | 121.6553 | 121.5912 | 121.5225 | 0.073242 | 0.004578 | 121.5088 | -0.009155 | -0.21057 | 121.7056 | 121.7056 | 121.6599 | 0.19684 | 0.15106 | 0.13733 | -0.022888 | 0.19684 | 0.086975 | 0.26093 | 0.28839 | 121.7789 | 121.7972 | -0.28839 | -0.29755 | 121.4951 | 121.5958 | 121.5088 | 121.6095
3122.2656 | 121.9299 | -121.6049 | 0.086975 | -0.0051118 | -0.012661 | -0.079011 | -0.0054837 | -0.031084 | -0.048672 | -0.042955 | -0.0021057 | -0.003232 | 0.006853 | -0.0088526 | -0.21979 | -0.01706 | -0.024535 | -0.064087 | 0.082397 | -0.11902 | -0.059509 | 0.09613 | -0.068665 | 0.009155 | 0.10986 | 0.07782 | -0.10529 | 0.091553 | 0.16937 | 0.10529 | 0.17395 | 121.4859 | -0.004578 | -0.14648 | 121.701 | 121.6141 | 121.5363 | 0.12817 | 0.050354 | 121.4996 | -0.009155 | 0.004578 | 121.7743 | 121.7789 | 121.7102 | 0.27924 | 0.21057 | 0.21515 | 0.05951 | 0.27466 | 0.19684 | 0.20142 | 0.18311 | 121.6873 | 121.6827 | -0.20599 | -0.19226 | 121.5454 | 121.6965 | 121.5408 | 121.7148
3124.0469 | 121.8842 | -121.6507 | 0.10986 | -0.0051118 | -0.011807 | -0.077515 | -0.0069791 | -0.028307 | -0.049954 | -0.044664 | 0.0039979 | -0.0064364 | 0.007494 | -0.020175 | -0.22086 | -0.017914 | -0.022398 | -0.10071 | 0.07782 | -0.10986 | -0.10071 | 0.073242 | -0.086975 | -0.009155 | 0.027466 | 0.086975 | -0.1236 | 0.009155 | 0.13275 | 0.068665 | 0.10986 | 121.5408 | -0.032043 | -0.21057 | 121.7239 | 121.6415 | 121.5637 | 0.10071 | 0.022888 | 121.5271 | -0.022888 | -0.10071 | 121.7834 | 121.7606 | 121.7194 | 0.23346 | 0.19226 | 0.18311 | 0.009155 | 0.25635 | 0.13275 | 0.18768 | 0.21057 | 121.7285 | 121.7377 | -0.21973 | -0.23346 | 121.55 | 121.6599 | 121.55 | 121.6782
3125.8281 | 121.8246 | -121.7102 | 0.1236 | 0.0025177 | -0.014584 | -0.081147 | -0.0082607 | -0.030871 | -0.050808 | -0.042101 | -0.0051575 | -0.0060092 | 0.0089892 | -0.011416 | -0.21937 | -0.017701 | -0.023253 | -0.15106 | 0.10529 | -0.14648 | -0.16479 | 0.004578 | -0.13275 | -0.068665 | -0.045776 | 0.13275 | -0.14191 | -0.059509 | 0.041199 | 0 | 0.045776 | 121.5637 | -0.01831 | -0.28839 | 121.7148 | 121.6415 | 121.5775 | 0.077819 | 0.013733 | 121.5683 | 0.009155 | -0.1831 | 121.7514 | 121.756 | 121.7102 | 0.18768 | 0.14191 | 0.15106 | -0.018311 | 0.18311 | 0.082398 | 0.25177 | 0.27466 | 121.8155 | 121.843 | -0.27008 | -0.2655 | 121.5454 | 121.6507 | 121.5591 | 121.6644
3127.6094 | 121.9299 | -121.6736 | 0.10986 | -0.0051118 | -0.01138 | -0.081574 | -0.0082607 | -0.03258 | -0.051663 | -0.041674 | -0.0021057 | -0.0045138 | 0.0062122 | -0.022524 | -0.2215 | -0.018769 | -0.02603 | -0.09613 | 0.091553 | -0.10986 | -0.09613 | 0.064087 | -0.09613 | -0.027466 | 0.032043 | 0.11444 | -0.1236 | 0.027466 | 0.13275 | 0.059509 | 0.10529 | 121.5637 | -0.01831 | -0.20599 | 121.7377 | 121.6461 | 121.5775 | 0.082397 | 0.013733 | 121.55 | 0.004578 | -0.082397 | 121.8063 | 121.7789 | 121.7331 | 0.22888 | 0.1831 | 0.17395 | 0.013733 | 0.25635 | 0.15106 | 0.20142 | 0.23804 | 121.7651 | 121.788 | -0.21973 | -0.23346 | 121.5775 | 121.7011 | 121.5775 | 121.7056
3129.4062 | 121.9849 | -121.6782 | 0.09613 | 0.0025177 | -0.015866 | -0.082215 | -0.0086879 | -0.029589 | -0.053799 | -0.042528 | 0.00094606 | -0.004941 | 0.0059986 | -0.013339 | -0.22001 | -0.016846 | -0.021758 | -0.059509 | 0.082397 | -0.10986 | -0.018311 | 0.16479 | -0.013733 | 0.036621 | 0.11902 | 0.10529 | -0.10986 | 0.082397 | 0.19226 | 0.13733 | 0.14648 | 121.5683 | -0.013733 | -0.11444 | 121.843 | 121.7148 | 121.6644 | 0.14648 | 0.09613 | 121.5683 | 0.009156 | -0.013733 | 121.8704 | 121.8246 | 121.8155 | 0.25635 | 0.24719 | 0.27466 | 0.091552 | 0.30212 | 0.19226 | 0.19226 | 0.21515 | 121.7606 | 121.7834 | -0.20599 | -0.20599 | 121.6599 | 121.7606 | 121.6187 | 121.7972
3131.1875 | 121.8567 | -121.7148 | 0.11902 | 0.0025177 | -0.010098 | -0.079865 | -0.0054837 | -0.031725 | -0.05209 | -0.039965 | -0.0021057 | -0.0025912 | 0.0098438 | -0.0041528 | -0.22043 | -0.01471 | -0.020049 | -0.07782 | 0.10986 | -0.13275 | -0.10529 | 0.013733 | -0.15564 | -0.068665 | 0.013733 | 0.14191 | -0.13733 | -0.013733 | 0.064087 | -0.013733 | 0.059509 | 121.582 | -0.009156 | -0.22431 | 121.7285 | 121.6461 | 121.5591 | 0.064086 | -0.022889 | 121.5775 | 0.022888 | -0.13275 | 121.7789 | 121.7743 | 121.701 | 0.19684 | 0.1236 | 0.14648 | 0.027465 | 0.20142 | 0.1236 | 0.24261 | 0.27924 | 121.8246 | 121.8567 | -0.25177 | -0.25635 | 121.6095 | 121.701 | 121.637 | 121.7285
3132.9844 | 121.9711 | -121.7285 | 0.10071 | -0.0051118 | -0.010525 | -0.077942 | -0.0059109 | -0.03258 | -0.050167 | -0.04146 | -0.0051575 | -0.0057956 | 0.0070666 | -0.015688 | -0.21958 | -0.019623 | -0.022398 | -0.086975 | 0.068665 | -0.10986 | -0.086975 | 0.10071 | -0.091553 | 0.009155 | 0.050354 | 0.10986 | -0.12817 | 0.045776 | 0.13275 | 0.068665 | 0.11444 | 121.6187 | -0.032043 | -0.18768 | 121.8292 | 121.7377 | 121.637 | 0.11902 | 0.01831 | 121.6003 | 0.009155 | -0.054932 | 121.8613 | 121.843 | 121.7972 | 0.24262 | 0.19684 | 0.21057 | 0.022888 | 0.26093 | 0.17395 | 0.17853 | 0.23804 | 121.7972 | 121.8384 | -0.21057 | -0.22888 | 121.6415 | 121.7743 | 121.6415 | 121.7789
3134.7656 | 122.0444 | -121.7056 | 0.10529 | -0.0051118 | -0.015438 | -0.080506 | -0.0078335 | -0.028948 | -0.050808 | -0.042528 | -0.0021057 | -0.005582 | 0.0081348 | -0.016543 | -0.22086 | -0.019196 | -0.023467 | -0.073242 | 0.07782 | -0.086975 | -0.004578 | 0.15106 | -0.022888 | 0.064087 | 0.15564 | 0.09613 | -0.1236 | 0.07782 | 0.20599 | 0.13733 | 0.14648 | 121.6187 | -0.027466 | -0.10986 | 121.8567 | 121.7697 | 121.6827 | 0.15106 | 0.064087 | 121.582 | -0.009156 | -0.027466 | 121.9116 | 121.8521 | 121.843 | 0.27008 | 0.26093 | 0.23804 | 0.082397 | 0.32959 | 0.20142 | 0.16479 | 0.21973 | 121.7834 | 121.8018 | -0.19226 | -0.22888 | 121.701 | 121.7834 | 121.6324 | 121.8613
3136.4844 | 121.9345 | -121.7606 | 0.12817 | 0.0025177 | -0.013302 | -0.08136 | -0.0076199 | -0.03023 | -0.051663 | -0.039965 | 0.00094606 | -0.003232 | 0.0079212 | -0.011843 | -0.22193 | -0.018769 | -0.022185 | -0.059509 | 0.082397 | -0.10071 | -0.059509 | 0.10529 | -0.059509 | 0.018311 | 0.041199 | 0.12817 | -0.13275 | 0.004578 | 0.11444 | 0.050354 | 0.064087 | 121.6599 | -0.045777 | -0.18768 | 121.8658 | 121.7789 | 121.701 | 0.11902 | 0.041199 | 121.6278 | 0 | -0.1236 | 121.875 | 121.8246 | 121.8109 | 0.19684 | 0.18311 | 0.20599 | 0.041199 | 0.24719 | 0.13733 | 0.18311 | 0.26093 | 121.843 | 121.8887 | -0.22888 | -0.26093 | 121.701 | 121.7651 | 121.701 | 121.8018
3138.2656 | 121.9299 | -121.7743 | 0.1236 | -0.012741 | -0.013729 | -0.082001 | -0.0074063 | -0.028521 | -0.053372 | -0.03911 | -0.0051575 | -0.0040866 | 0.0081348 | -0.0026574 | -0.21894 | -0.017701 | -0.023894 | -0.068665 | 0.091553 | -0.10986 | -0.086975 | 0.068665 | -0.086975 | 0 | 0.018311 | 0.1236 | -0.14648 | -0.018311 | 0.073242 | 0.018311 | 0.059509 | 121.6644 | -0.032043 | -0.21057 | 121.843 | 121.7743 | 121.6873 | 0.10986 | 0.022888 | 121.6278 | 0 | -0.14191 | 121.8475 | 121.8338 | 121.7926 | 0.20599 | 0.16479 | 0.17853 | 0.022888 | 0.21973 | 0.12817 | 0.20142 | 0.27008 | 121.8658 | 121.8979 | -0.23346 | -0.27008 | 121.6873 | 121.756 | 121.7056 | 121.7926
3140 | 121.9391 | -121.8018 | 0.11444 | -0.0051118 | -0.013516 | -0.079438 | -0.0065517 | -0.032366 | -0.050381 | -0.042955 | 0.0039979 | -0.004941 | 0.0092028 | -0.01227 | -0.22001 | -0.018128 | -0.024748 | -0.082397 | 0.082397 | -0.10986 | -0.10529 | 0.036621 | -0.09613 | -0.036621 | -0.013733 | 0.13733 | -0.15564 | -0.018311 | 0.064087 | 0.013733 | 0.050354 | 121.6919 | -0.032044 | -0.21973 | 121.8384 | 121.7651 | 121.7056 | 0.073242 | 0.013733 | 121.6461 | 0.022888 | -0.13275 | 121.8658 | 121.8521 | 121.8155 | 0.20599 | 0.16937 | 0.14648 | 0.004577 | 0.21973 | 0.13733 | 0.19226 | 0.29297 | 121.8842 | 121.9391 | -0.2243 | -0.27008 | 121.6965 | 121.7834 | 121.7194 | 121.788
3141.7812 | 122.0398 | -121.7697 | 0.082397 | -0.012741 | -0.01138 | -0.079011 | -0.0071927 | -0.031298 | -0.050808 | -0.045092 | -0.0021057 | -0.007291 | 0.0081348 | -0.013766 | -0.22086 | -0.017914 | -0.022612 | -0.10986 | 0.086975 | -0.11444 | -0.086975 | 0.050354 | -0.09613 | 0.004578 | 0.045776 | 0.10529 | -0.13275 | 0.050354 | 0.16022 | 0.09613 | 0.13275 | 121.6553 | 0.004578 | -0.16937 | 121.8201 | 121.7743 | 121.6736 | 0.11902 | 0.018311 | 121.637 | 0.022889 | -0.032043 | 121.9299 | 121.9025 | 121.8658 | 0.2655 | 0.22888 | 0.16479 | 0.027466 | 0.29297 | 0.18311 | 0.20142 | 0.23804 | 121.8567 | 121.875 | -0.19684 | -0.21515 | 121.6827 | 121.8201 | 121.6599 | 121.8155
3143.5625 | 122.0627 | -121.7606 | 0.09613 | 0.0025177 | -0.0073209 | -0.07837 | -0.0061245 | -0.028307 | -0.048031 | -0.043383 | 0.00094606 | -0.0057956 | 0.0070666 | -0.010989 | -0.21958 | -0.016846 | -0.021971 | -0.036621 | 0.073242 | -0.091553 | -0.013733 | 0.13275 | -0.068665 | 0.027466 | 0.13275 | 0.11444 | -0.10529 | 0.09613 | 0.1831 | 0.11444 | 0.15106 | 121.669 | -0.022888 | -0.10986 | 121.8933 | 121.788 | 121.6919 | 0.11902 | 0.022888 | 121.6553 | 0.018311 | 0 | 121.9437 | 121.9116 | 121.875 | 0.25635 | 0.21973 | 0.2243 | 0.07782 | 0.28839 | 0.20142 | 0.16479 | 0.21973 | 121.8338 | 121.875 | -0.18768 | -0.20142 | 121.7468 | 121.8567 | 121.7239 | 121.8933
3145.2969 | 122.0306 | -121.7834 | 0.10529 | 0.0025177 | -0.013089 | -0.079651 | -0.0078335 | -0.034716 | -0.048672 | -0.042528 | -0.0021057 | -0.0057956 | 0.0070666 | -0.013766 | -0.21915 | -0.01941 | -0.019835 | -0.086975 | 0.082397 | -0.091553 | -0.064087 | 0.09613 | -0.10986 | 0.004578 | 0.073242 | 0.10071 | -0.11444 | 0.041199 | 0.12817 | 0.068665 | 0.1236 | 121.6919 | -0.022889 | -0.16937 | 121.8796 | 121.788 | 121.6736 | 0.096131 | -0.01831 | 121.669 | -0.004578 | -0.064087 | 121.9116 | 121.907 | 121.8521 | 0.23804 | 0.18311 | 0.18768 | 0.027466 | 0.24262 | 0.15564 | 0.17395 | 0.21515 | 121.8658 | 121.8842 | -0.19684 | -0.21973 | 121.7194 | 121.8246 | 121.6965 | 121.8567
3147.0938 | 122.081 | -121.7789 | 0.086975 | -0.0051118 | -0.012661 | -0.077729 | -0.0076199 | -0.029162 | -0.051449 | -0.042955 | 0.00094606 | -0.00665 | 0.0055712 | -0.021243 | -0.22043 | -0.017701 | -0.019194 | -0.086975 | 0.073242 | -0.082397 | -0.050354 | 0.091553 | -0.068665 | 0.032043 | 0.086975 | 0.11902 | -0.11444 | 0.082397 | 0.18768 | 0.1236 | 0.14648 | 121.6965 | -0.013733 | -0.13733 | 121.8704 | 121.8109 | 121.7102 | 0.11444 | 0.013732 | 121.6644 | 0.032044 | -0.004578 | 121.9666 | 121.9254 | 121.9025 | 0.26093 | 0.23804 | 0.17395 | 0.032043 | 0.30212 | 0.19684 | 0.15564 | 0.23346 | 121.8521 | 121.8979 | -0.16937 | -0.20142 | 121.7285 | 121.8613 | 121.6919 | 121.8658
3148.9062 | 122.0993 | -121.8063 | 0.10071 | -0.012741 | -0.011166 | -0.078583 | -0.0061245 | -0.030871 | -0.053158 | -0.043383 | 0.00094606 | -0.0057956 | 0.0059986 | -0.0092798 | -0.2215 | -0.015778 | -0.022398 | -0.041199 | 0.068665 | -0.09613 | -0.022888 | 0.1236 | -0.07782 | 0.009155 | 0.13733 | 0.10529 | -0.1236 | 0.10529 | 0.18768 | 0.10529 | 0.16479 | 121.7102 | -0.032043 | -0.1236 | 121.9299 | 121.8155 | 121.7285 | 0.10528 | 0.01831 | 121.6827 | 0.004578 | 0.004578 | 121.994 | 121.9711 | 121.9116 | 0.28839 | 0.22888 | 0.21973 | 0.073242 | 0.31128 | 0.22888 | 0.16479 | 0.22888 | 121.875 | 121.9116 | -0.19684 | -0.2243 | 121.7834 | 121.9116 | 121.7651 | 121.9437
3150.6406 | 121.9803 | -121.843 | 0.10529 | 0.010147 | -0.010098 | -0.077942 | -0.0033475 | -0.03023 | -0.050381 | -0.043169 | 0.00094606 | -0.0045138 | 0.0070666 | 0.0048194 | -0.22043 | -0.020051 | -0.026885 | -0.091553 | 0.10986 | -0.11902 | -0.10986 | 0.013733 | -0.16479 | -0.09613 | 0.004578 | 0.14648 | -0.12817 | -0.009155 | 0.041199 | -0.018311 | 0.054932 | 121.7239 | 0.004577 | -0.21515 | 121.8567 | 121.7468 | 121.6782 | 0.022889 | -0.045776 | 121.7148 | 0.041198 | -0.11444 | 121.8842 | 121.8979 | 121.8246 | 0.18311 | 0.10986 | 0.13275 | 0.009156 | 0.16937 | 0.11902 | 0.22888 | 0.27466 | 121.9528 | 121.9894 | -0.22431 | -0.23346 | 121.7331 | 121.8338 | 121.7514 | 121.8475
3152.4219 | 122.0078 | -121.8796 | 0.14191 | 0.0025177 | -0.015652 | -0.08136 | -0.0069791 | -0.029802 | -0.051663 | -0.040392 | -0.0021057 | -0.0062228 | 0.010057 | -0.0094934 | -0.22065 | -0.017701 | -0.027312 | -0.10071 | 0.09613 | -0.1236 | -0.14191 | 0.027466 | -0.13275 | -0.050354 | -0.018311 | 0.15564 | -0.14648 | -0.036621 | 0.068665 | 0.009155 | 0.032043 | 121.756 | -0.045777 | -0.28381 | 121.907 | 121.8292 | 121.7468 | 0.073242 | -0.009155 | 121.7331 | 0.013733 | -0.17853 | 121.9482 | 121.9116 | 121.8887 | 0.17853 | 0.15564 | 0.15106 | -0.018311 | 0.21515 | 0.10986 | 0.21973 | 0.30212 | 121.9757 | 122.0352 | -0.2655 | -0.28839 | 121.7377 | 121.843 | 121.7789 | 121.8613
3154.2031 | 122.0856 | -121.8475 | 0.10529 | -0.0051118 | -0.016079 | -0.079011 | -0.0082607 | -0.028734 | -0.053585 | -0.041674 | -0.0051575 | -0.0062228 | 0.008562 | -0.01697 | -0.22065 | -0.02176 | -0.023894 | -0.050354 | 0.064087 | -0.11444 | -0.032043 | 0.12817 | -0.036621 | 0.022888 | 0.082397 | 0.10529 | -0.12817 | 0.054932 | 0.17395 | 0.11444 | 0.13733 | 121.7331 | -0.041199 | -0.13733 | 121.9757 | 121.8704 | 121.8109 | 0.13733 | 0.07782 | 121.7194 | 0 | -0.050354 | 122.0215 | 121.9849 | 121.962 | 0.2655 | 0.24262 | 0.24262 | 0.082398 | 0.30212 | 0.18311 | 0.17853 | 0.23346 | 121.9116 | 121.9528 | -0.21973 | -0.23346 | 121.8155 | 121.9025 | 121.7972 | 121.9299
3155.9219 | 122.1588 | -121.843 | 0.09613 | -0.012741 | -0.014584 | -0.08136 | -0.0074063 | -0.030443 | -0.052517 | -0.042314 | -0.0051575 | -0.0087862 | 0.007494 | -0.017397 | -0.22236 | -0.019196 | -0.021544 | -0.041199 | 0.09613 | -0.091553 | -0.004578 | 0.17395 | -0.004578 | 0.064087 | 0.13275 | 0.10986 | -0.11444 | 0.091553 | 0.21057 | 0.14648 | 0.14191 | 121.7514 | 0 | -0.10071 | 122.0169 | 121.907 | 121.8384 | 0.15564 | 0.086975 | 121.7285 | 0.013733 | -0.004577 | 122.0535 | 121.9849 | 121.9894 | 0.25635 | 0.26093 | 0.2655 | 0.086975 | 0.32501 | 0.20599 | 0.18768 | 0.2243 | 121.9391 | 121.9528 | -0.18768 | -0.21057 | 121.8384 | 121.9345 | 121.8018 | 121.9757
3157.7031 | 122.1405 | -121.8521 | 0.091553 | -0.0051118 | -0.01138 | -0.078583 | -0.0033475 | -0.033434 | -0.050808 | -0.041246 | 0.00094606 | -0.0047274 | 0.0072802 | -0.019534 | -0.22236 | -0.016419 | -0.022612 | -0.073242 | 0.09613 | -0.10529 | -0.064087 | 0.082397 | -0.09613 | -0.004578 | 0.10071 | 0.10529 | -0.10986 | 0.11444 | 0.16937 | 0.10986 | 0.15106 | 121.7468 | 0.004577 | -0.15564 | 121.9345 | 121.8475 | 121.756 | 0.10071 | 0.009156 | 121.7422 | 0.013733 | 0.022888 | 122.0215 | 122.0032 | 121.962 | 0.26093 | 0.21973 | 0.18768 | 0.041199 | 0.27924 | 0.2243 | 0.20142 | 0.21515 | 121.9482 | 121.9574 | -0.19684 | -0.20142 | 121.788 | 121.9666 | 121.7789 | 121.9528
3159.4844 | 122.1542 | -121.8521 | 0.07782 | 0.0025177 | -0.010098 | -0.078583 | -0.0056973 | -0.027453 | -0.050167 | -0.039537 | -0.0051575 | -0.0068636 | 0.0081348 | -0.0065026 | -0.21979 | -0.016419 | -0.024107 | -0.036621 | 0.068665 | -0.086975 | -0.022888 | 0.13733 | -0.068665 | 0.022888 | 0.12817 | 0.10529 | -0.10071 | 0.10986 | 0.19684 | 0.10986 | 0.15106 | 121.7651 | -0.009155 | -0.10071 | 121.9894 | 121.875 | 121.7834 | 0.10986 | 0.01831 | 121.7514 | 0.027466 | 0.032043 | 122.049 | 122.0032 | 121.962 | 0.25177 | 0.21057 | 0.2243 | 0.064087 | 0.29755 | 0.21057 | 0.15564 | 0.20599 | 121.9208 | 121.9574 | -0.16479 | -0.17853 | 121.8292 | 121.962 | 121.8155 | 121.9803
3161.2031 | 122.1268 | -121.8613 | 0.09613 | 0.0025177 | -0.010098 | -0.079865 | -0.0069791 | -0.026812 | -0.048031 | -0.042528 | 0.00094606 | -0.007291 | 0.010057 | -0.00693 | -0.22022 | -0.016846 | -0.020049 | -0.054932 | 0.073242 | -0.086975 | -0.032043 | 0.13275 | -0.07782 | 0.009155 | 0.11902 | 0.10071 | -0.09613 | 0.086975 | 0.16022 | 0.086975 | 0.14648 | 121.7743 | -0.022888 | -0.12817 | 121.994 | 121.8704 | 121.7834 | 0.09613 | 0.009155 | 121.7651 | 0.004578 | -0.009155 | 122.0215 | 122.0078 | 121.9482 | 0.24261 | 0.1831 | 0.21973 | 0.054932 | 0.25635 | 0.1831 | 0.16022 | 0.19684 | 121.9345 | 121.962 | -0.1831 | -0.19226 | 121.8292 | 121.9482 | 121.8063 | 121.9803
3162.9844 | 122.1222 | -121.8933 | 0.068665 | -0.0051118 | -0.010525 | -0.079438 | -0.0050565 | -0.030657 | -0.050595 | -0.042101 | 0.0039979 | -0.00665 | 0.0077076 | -0.010561 | -0.22086 | -0.016846 | -0.023039 | -0.064087 | 0.073242 | -0.10071 | -0.036621 | 0.12817 | -0.082397 | 0.009155 | 0.091553 | 0.091553 | -0.11444 | 0.07782 | 0.15106 | 0.086975 | 0.12817 | 121.7926 | 0.004577 | -0.10529 | 122.0215 | 121.9025 | 121.8109 | 0.10986 | 0.018311 | 121.7789 | 0.022888 | 0.009155 | 122.0444 | 122.0215 | 121.9803 | 0.24262 | 0.20142 | 0.22888 | 0.064087 | 0.2655 | 0.19226 | 0.17395 | 0.20599 | 121.9666 | 121.9849 | -0.16937 | -0.18311 | 121.8567 | 121.9711 | 121.8292 | 121.9849
3164.7812 | 122.1725 | -121.8704 | 0.091553 | 0.0025177 | -0.013729 | -0.079651 | -0.0069791 | -0.031725 | -0.052304 | -0.040819 | 0.00094606 | -0.00665 | 0.0066394 | -0.01462 | -0.22257 | -0.017914 | -0.026457 | -0.068665 | 0.073242 | -0.1236 | -0.018311 | 0.16022 | -0.022888 | 0.050354 | 0.11902 | 0.10071 | -0.09613 | 0.091553 | 0.21973 | 0.13733 | 0.15106 | 121.7468 | -0.018311 | -0.10986 | 122.0306 | 121.9208 | 121.8475 | 0.17395 | 0.10071 | 121.7743 | 0.009155 | 0 | 122.0901 | 122.0215 | 122.0078 | 0.24719 | 0.23346 | 0.28381 | 0.10528 | 0.31586 | 0.18768 | 0.19684 | 0.19684 | 121.9437 | 121.9711 | -0.21515 | -0.18768 | 121.8521 | 121.962 | 121.8018 | 121.9894
3166.5156 | 122.2 | -121.8979 | 0.10071 | 0.0025177 | -0.015652 | -0.079438 | -0.0082607 | -0.031725 | -0.050381 | -0.042314 | -0.0021057 | -0.0075046 | 0.008562 | -0.014407 | -0.22022 | -0.020264 | -0.021544 | -0.064087 | 0.082397 | -0.10986 | -0.027466 | 0.15106 | -0.018311 | 0.041199 | 0.10986 | 0.11444 | -0.10529 | 0.086975 | 0.19684 | 0.12817 | 0.14191 | 121.788 | -0.018311 | -0.12817 | 122.0489 | 121.9391 | 121.8796 | 0.15106 | 0.091552 | 121.7926 | 0.013733 | -0.013733 | 122.0947 | 122.0398 | 122.0261 | 0.24719 | 0.23346 | 0.26093 | 0.082397 | 0.30212 | 0.19226 | 0.19226 | 0.21973 | 121.9803 | 122.0123 | -0.21057 | -0.20599 | 121.8704 | 121.9849 | 121.8338 | 122.0078
3168.3125 | 122.1222 | -121.9254 | 0.11444 | 0.010147 | -0.012448 | -0.079865 | -0.0050565 | -0.024675 | -0.051449 | -0.039751 | -0.0021057 | -0.0051546 | 0.0064258 | -0.00458 | -0.22043 | -0.015992 | -0.020689 | -0.073242 | 0.10529 | -0.13275 | -0.086975 | 0.050354 | -0.12817 | -0.036621 | 0.059509 | 0.13275 | -0.13275 | 0.045776 | 0.10986 | 0.054932 | 0.10071 | 121.7926 | -0.009155 | -0.20142 | 121.9757 | 121.8887 | 121.7972 | 0.09613 | 0.004577 | 121.7926 | 0.01831 | -0.068665 | 122.0352 | 122.0261 | 121.9803 | 0.23346 | 0.18768 | 0.18311 | 0.045776 | 0.24261 | 0.17853 | 0.23804 | 0.2655 | 122.0306 | 122.0581 | -0.24719 | -0.24719 | 121.8384 | 121.9711 | 121.8521 | 121.9849
3170.0312 | 122.1268 | -121.9345 | 0.10071 | 0.0025177 | -0.012661 | -0.077729 | -0.0046291 | -0.031084 | -0.050381 | -0.041887 | -0.0021057 | -0.0040866 | 0.010485 | -0.012057 | -0.22107 | -0.018769 | -0.021117 | -0.082397 | 0.11444 | -0.13275 | -0.10071 | 0.045776 | -0.11444 | -0.050354 | 0.032043 | 0.13733 | -0.11444 | 0.022888 | 0.10986 | 0.050354 | 0.091553 | 121.8018 | 0.013733 | -0.20142 | 121.9803 | 121.8842 | 121.8201 | 0.082397 | 0.01831 | 121.8201 | 0.036621 | -0.07782 | 122.0444 | 122.0261 | 121.9849 | 0.20599 | 0.16479 | 0.17853 | 0.032043 | 0.2243 | 0.13733 | 0.24719 | 0.25177 | 122.049 | 122.0718 | -0.23346 | -0.21515 | 121.8338 | 121.9574 | 121.8521 | 121.9666
3171.8281 | 122.1359 | -121.9116 | 0.1236 | -0.012741 | -0.011166 | -0.079438 | -0.0042019 | -0.029589 | -0.046963 | -0.039751 | 0.00094606 | -0.0028048 | 0.0070666 | -0.015261 | -0.22065 | -0.018342 | -0.021117 | -0.11444 | 0.12817 | -0.14191 | -0.14648 | 0.009155 | -0.1831 | -0.082397 | -0.009155 | 0.13733 | -0.13275 | 0.022888 | 0.10529 | 0.027466 | 0.10071 | 121.7697 | 0.004578 | -0.27008 | 121.9208 | 121.8292 | 121.7285 | 0.05951 | -0.041198 | 121.7789 | 0.013733 | -0.10071 | 122.0169 | 122.0123 | 121.9391 | 0.23346 | 0.16022 | 0.15106 | -0.004577 | 0.23804 | 0.15564 | 0.27008 | 0.27008 | 122.0398 | 122.0489 | -0.2655 | -0.25635 | 121.7651 | 121.9345 | 121.7972 | 121.9025
3173.5625 | 122.1497 | -121.9528 | 0.10986 | -0.0051118 | -0.0090299 | -0.080079 | -0.0042019 | -0.031084 | -0.047817 | -0.041033 | 0.00094606 | -0.0036594 | 0.0098438 | -0.0058618 | -0.21937 | -0.016846 | -0.024535 | -0.068665 | 0.091553 | -0.13275 | -0.091553 | 0.054932 | -0.11444 | -0.036621 | 0.054932 | 0.11444 | -0.1236 | 0.022888 | 0.11444 | 0.050354 | 0.10071 | 121.8201 | -0.01831 | -0.20142 | 122.0078 | 121.9162 | 121.8384 | 0.09613 | 0.01831 | 121.8292 | 0.004578 | -0.086975 | 122.0673 | 122.0535 | 122.0032 | 0.2243 | 0.17395 | 0.18768 | 0.041198 | 0.23804 | 0.14648 | 0.2243 | 0.23804 | 122.0444 | 122.0673 | -0.24261 | -0.23346 | 121.8613 | 121.9757 | 121.8842 | 122.0078
3175.3594 | 122.1359 | -121.9849 | 0.13275 | -0.012741 | -0.012875 | -0.079651 | -0.0082607 | -0.030443 | -0.051022 | -0.044237 | -0.0021057 | -0.004941 | 0.0066394 | -0.0092798 | -0.21958 | -0.018982 | -0.023894 | -0.082397 | 0.09613 | -0.10529 | -0.10986 | 0.07782 | -0.091553 | -0.009155 | 0 | 0.13733 | -0.13275 | -0.032043 | 0.064087 | 0.018311 | 0.054932 | 121.8796 | -0.036621 | -0.24261 | 122.0627 | 121.9757 | 121.8933 | 0.096131 | 0.013733 | 121.8521 | 0.004578 | -0.16479 | 122.049 | 122.0398 | 122.0032 | 0.18768 | 0.15106 | 0.18311 | -0.004577 | 0.19684 | 0.10071 | 0.20142 | 0.27008 | 122.081 | 122.1222 | -0.23804 | -0.2655 | 121.875 | 121.9528 | 121.9025 | 121.9849
3177.1406 | 122.2458 | -121.9666 | 0.086975 | 0.0025177 | -0.015225 | -0.082428 | -0.0080471 | -0.035143 | -0.051876 | -0.041033 | -0.0021057 | -0.0064364 | 0.005785 | -0.012057 | -0.22043 | -0.01706 | -0.02133 | -0.068665 | 0.082397 | -0.11444 | -0.027466 | 0.16937 | -0.013733 | 0.064087 | 0.15106 | 0.10071 | -0.11902 | 0.09613 | 0.20599 | 0.14648 | 0.15106 | 121.8521 | -0.004578 | -0.11444 | 122.1359 | 122.0306 | 121.9528 | 0.17853 | 0.10071 | 121.8475 | 0.013733 | 0.009155 | 122.1725 | 122.1176 | 122.113 | 0.27008 | 0.2655 | 0.28381 | 0.086975 | 0.32501 | 0.21515 | 0.19684 | 0.21973 | 122.049 | 122.0673 | -0.20142 | -0.20599 | 121.9391 | 122.0627 | 121.8979 | 122.1176
3178.9375 | 122.2137 | -121.9666 | 0.09613 | 0.010147 | -0.013943 | -0.079651 | -0.0056973 | -0.030657 | -0.051235 | -0.042314 | -0.0021057 | -0.0043002 | 0.0027942 | -0.012484 | -0.22236 | -0.017487 | -0.020262 | -0.11444 | 0.082397 | -0.11444 | -0.091553 | 0.054932 | -0.10529 | -0.013733 | 0.027466 | 0.09613 | -0.1236 | 0.013733 | 0.15106 | 0.086975 | 0.12817 | 121.8521 | -0.013733 | -0.18768 | 122.0215 | 121.9528 | 121.8613 | 0.10071 | 0.009155 | 121.843 | 0 | -0.082397 | 122.1176 | 122.0947 | 122.0535 | 0.25177 | 0.21057 | 0.16937 | 0.022888 | 0.27466 | 0.13733 | 0.19684 | 0.21973 | 122.049 | 122.0627 | -0.21057 | -0.21973 | 121.875 | 121.9803 | 121.8521 | 121.994
3180.6719 | 122.0993 | -121.9986 | 0.12817 | 0.010147 | -0.011807 | -0.079651 | -0.0044155 | -0.029162 | -0.049954 | -0.041887 | -0.0051575 | -0.0023776 | 0.007494 | -0.01163 | -0.22022 | -0.014924 | -0.026671 | -0.1236 | 0.11902 | -0.15564 | -0.16937 | -0.050354 | -0.20599 | -0.12817 | -0.07782 | 0.12817 | -0.17395 | -0.032043 | 0.032043 | -0.045776 | 0.050354 | 121.843 | -0.009155 | -0.29755 | 121.9482 | 121.8704 | 121.7926 | 0.027466 | -0.050354 | 121.8246 | 0 | -0.16022 | 122.0306 | 122.049 | 121.9528 | 0.2243 | 0.12817 | 0.10529 | -0.013733 | 0.20599 | 0.14191 | 0.27466 | 0.30212 | 122.1176 | 122.1268 | -0.28381 | -0.30212 | 121.8292 | 121.9666 | 121.875 | 121.9208
3182.4531 | 122.2183 | -121.9894 | 0.11444 | -0.0051118 | -0.014798 | -0.080719 | -0.0076199 | -0.031298 | -0.051235 | -0.040392 | 0.00094606 | -0.0060092 | 0.0059986 | -0.019747 | -0.21979 | -0.017487 | -0.022185 | -0.10529 | 0.073242 | -0.11444 | -0.086975 | 0.068665 | -0.10071 | -0.009155 | 0.022888 | 0.11902 | -0.10986 | 0.027466 | 0.12817 | 0.068665 | 0.10529 | 121.875 | -0.041199 | -0.20142 | 122.0581 | 121.9803 | 121.8887 | 0.10529 | 0.013733 | 121.8796 | 0.004578 | -0.086975 | 122.1176 | 122.0947 | 122.0581 | 0.21515 | 0.17853 | 0.18311 | 0.027466 | 0.23804 | 0.13733 | 0.18768 | 0.22888 | 122.0627 | 122.1085 | -0.22888 | -0.2243 | 121.9025 | 122.0169 | 121.8842 | 122.0123
3184.25 | 122.2183 | -121.9894 | 0.09613 | 0.010147 | -0.014157 | -0.079224 | -0.0076199 | -0.030016 | -0.051449 | -0.042955 | 0.00094606 | -0.0060092 | 0.006853 | -0.013766 | -0.22107 | -0.019623 | -0.022185 | -0.10071 | 0.091553 | -0.10986 | -0.091553 | 0.059509 | -0.09613 | -0.004578 | 0.022888 | 0.12817 | -0.1236 | 0.032043 | 0.12817 | 0.064087 | 0.10529 | 121.8796 | -0.004577 | -0.18768 | 122.049 | 121.9849 | 121.8933 | 0.10529 | 0.013733 | 121.8658 | 0.032044 | -0.064087 | 122.1176 | 122.0947 | 122.0535 | 0.22888 | 0.18768 | 0.16937 | 0.01831 | 0.25177 | 0.15564 | 0.20142 | 0.25177 | 122.081 | 122.1176 | -0.20599 | -0.21973 | 121.8979 | 122.0215 | 121.8887 | 122.0123
3186 | 122.2641 | -121.9849 | 0.082397 | 0.0025177 | -0.010739 | -0.078156 | -0.0061245 | -0.024889 | -0.051663 | -0.042528 | 0.0039979 | -0.0043002 | 0.010057 | -0.0082116 | -0.2215 | -0.015778 | -0.02603 | -0.036621 | 0.086975 | -0.09613 | -0.041199 | 0.11902 | -0.064087 | 0.018311 | 0.13275 | 0.086975 | -0.10529 | 0.11444 | 0.1831 | 0.10529 | 0.17853 | 121.8887 | 0.004578 | -0.1236 | 122.1039 | 122.0032 | 121.9208 | 0.11444 | 0.032043 | 121.8796 | 0.004578 | 0.032044 | 122.168 | 122.1634 | 122.0901 | 0.28381 | 0.21057 | 0.21515 | 0.054931 | 0.28839 | 0.21973 | 0.1831 | 0.19226 | 122.0718 | 122.0718 | -0.17853 | -0.18768 | 121.9437 | 122.0993 | 121.9482 | 122.1176
3187.7812 | 122.1954 | -122.0215 | 0.11902 | 0.0025177 | -0.013516 | -0.080079 | -0.0054837 | -0.03023 | -0.050808 | -0.045305 | -0.0021057 | -0.004941 | 0.0066394 | -0.012698 | -0.22065 | -0.016419 | -0.022826 | -0.11444 | 0.1236 | -0.14191 | -0.14191 | -0.013733 | -0.16022 | -0.068665 | -0.032043 | 0.13733 | -0.13733 | -0.022888 | 0.082397 | 0.009155 | 0.073242 | 121.8796 | 0.004577 | -0.26093 | 122.0078 | 121.9528 | 121.8613 | 0.073242 | -0.01831 | 121.8842 | 0.01831 | -0.14191 | 122.1039 | 122.0947 | 122.0306 | 0.21057 | 0.14648 | 0.12817 | 0 | 0.21973 | 0.11444 | 0.2655 | 0.27466 | 122.1451 | 122.1588 | -0.26093 | -0.25635 | 121.8796 | 121.9986 | 121.907 | 121.9894
3189.5781 | 122.2824 | -121.9849 | 0.10529 | -0.0051118 | -0.011593 | -0.078156 | -0.0052701 | -0.031298 | -0.050167 | -0.04146 | -0.0021057 | -0.0060092 | 0.0064258 | -0.012484 | -0.22043 | -0.017273 | -0.024107 | -0.11444 | 0.10986 | -0.14191 | -0.10529 | 0.041199 | -0.13733 | -0.045776 | 0.054932 | 0.11444 | -0.12817 | 0.082397 | 0.15564 | 0.07782 | 0.14648 | 121.843 | 0.004577 | -0.21057 | 122.0261 | 121.9391 | 121.8475 | 0.096131 | 0.004578 | 121.8567 | 0.009155 | -0.022889 | 122.1405 | 122.1313 | 122.0627 | 0.27466 | 0.20599 | 0.18311 | 0.036621 | 0.28381 | 0.21057 | 0.25177 | 0.24262 | 122.0947 | 122.0993 | -0.24719 | -0.23346 | 121.8796 | 122.0673 | 121.8704 | 122.0398
3191.2969 | 122.2321 | -122.0078 | 0.10986 | -0.0051118 | -0.01202 | -0.079224 | -0.0084743 | -0.031725 | -0.049099 | -0.04146 | -0.0021057 | -0.0077182 | 0.007494 | -0.016116 | -0.21851 | -0.01941 | -0.024748 | -0.10986 | 0.07782 | -0.11902 | -0.082397 | 0.064087 | -0.10071 | -0.022888 | 0.018311 | 0.11444 | -0.11444 | 0.027466 | 0.10529 | 0.045776 | 0.1236 | 121.8887 | -0.032043 | -0.19226 | 122.0718 | 121.9849 | 121.907 | 0.096131 | 0.018311 | 121.8933 | 0.004578 | -0.082397 | 122.113 | 122.1313 | 122.0535 | 0.23804 | 0.16022 | 0.18311 | 0.036622 | 0.21973 | 0.14191 | 0.19684 | 0.22888 | 122.0856 | 122.1222 | -0.22888 | -0.2243 | 121.9254 | 122.0352 | 121.8979 | 122.0261
3193.0625 | 122.2733 | -122.0261 | 0.091553 | -0.0051118 | -0.015866 | -0.080719 | -0.0078335 | -0.030443 | -0.051876 | -0.037615 | -0.0051575 | -0.0070772 | 0.0081348 | -0.017184 | -0.21958 | -0.018769 | -0.023467 | -0.054932 | 0.068665 | -0.10071 | -0.032043 | 0.14191 | -0.027466 | 0.036621 | 0.091553 | 0.10529 | -0.1236 | 0.064087 | 0.17395 | 0.11444 | 0.13733 | 121.9254 | -0.022888 | -0.1236 | 122.168 | 122.0627 | 121.9986 | 0.13733 | 0.073242 | 121.9025 | 0.013733 | -0.027466 | 122.2 | 122.1634 | 122.1405 | 0.26093 | 0.23804 | 0.24262 | 0.068665 | 0.29755 | 0.18768 | 0.16937 | 0.22888 | 122.0947 | 122.1313 | -0.19226 | -0.21515 | 121.994 | 122.0901 | 121.9711 | 122.1176
3194.8594 | 122.1863 | -122.0398 | 0.14648 | -0.0051118 | -0.010311 | -0.080506 | -0.0044155 | -0.03023 | -0.050381 | -0.042314 | -0.0082091 | -0.0019504 | 0.010057 | -0.012698 | -0.22043 | -0.016419 | -0.022398 | -0.10071 | 0.11444 | -0.12817 | -0.11902 | 0.004578 | -0.16022 | -0.082397 | -0.013733 | 0.13733 | -0.1236 | -0.018311 | 0.045776 | -0.022888 | 0.045776 | 121.9116 | -0.032043 | -0.2655 | 122.0444 | 121.9574 | 121.8796 | 0.045777 | -0.032043 | 121.9162 | -0.009155 | -0.16479 | 122.0856 | 122.0856 | 122.0169 | 0.16937 | 0.10071 | 0.13275 | 0.009155 | 0.16937 | 0.10528 | 0.24262 | 0.26093 | 122.1542 | 122.1771 | -0.27466 | -0.27008 | 121.9208 | 122.0215 | 121.9391 | 122.0261
3196.5781 | 122.1725 | -122.0673 | 0.12817 | 0.010147 | -0.0096707 | -0.079224 | -0.0046291 | -0.02553 | -0.052304 | -0.039324 | 0.00094606 | -0.003873 | 0.0081348 | -0.011416 | -0.22001 | -0.018128 | -0.025389 | -0.1236 | 0.12817 | -0.12817 | -0.16479 | -0.059509 | -0.18768 | -0.10986 | -0.068665 | 0.14191 | -0.14648 | -0.032043 | 0.032043 | -0.050354 | 0.050354 | 121.9391 | 0 | -0.29297 | 122.0078 | 121.9574 | 121.8796 | 0.018311 | -0.059509 | 121.9208 | 0.013733 | -0.16022 | 122.0993 | 122.1176 | 122.0169 | 0.19684 | 0.09613 | 0.068665 | -0.036621 | 0.17853 | 0.11444 | 0.25635 | 0.28839 | 122.1954 | 122.2092 | -0.25635 | -0.27466 | 121.9025 | 122.0352 | 121.9437 | 121.9986
3198.3594 | 122.2183 | -122.0444 | 0.11444 | 0.0025177 | -0.0096707 | -0.077942 | -0.0024929 | -0.029162 | -0.051449 | -0.044664 | -0.0082091 | -0.0057956 | 0.011125 | -0.013125 | -0.2183 | -0.016419 | -0.021971 | -0.1236 | 0.11902 | -0.16937 | -0.17395 | -0.013733 | -0.19684 | -0.086975 | -0.022888 | 0.13733 | -0.14648 | -0.009155 | 0.041199 | -0.018311 | 0.059509 | 121.875 | 0.004578 | -0.28839 | 122.0306 | 121.9574 | 121.8475 | 0.082398 | -0.027465 | 121.8979 | 0.022888 | -0.1236 | 122.0856 | 122.1039 | 122.0261 | 0.20599 | 0.12817 | 0.15564 | -0.004577 | 0.18768 | 0.13733 | 0.28839 | 0.28381 | 122.1634 | 122.1817 | -0.28381 | -0.26093 | 121.8704 | 122.0352 | 121.9208 | 122.0215
3200.1406 | 122.3099 | -122.0169 | 0.10071 | 0.0025177 | -0.015866 | -0.080079 | -0.0076199 | -0.033007 | -0.048886 | -0.038896 | -0.0021057 | -0.0075046 | 0.0062122 | -0.022311 | -0.21915 | -0.018342 | -0.021758 | -0.11444 | 0.073242 | -0.11902 | -0.082397 | 0.10071 | -0.064087 | 0.013733 | 0.059509 | 0.10529 | -0.10529 | 0.064087 | 0.18768 | 0.13275 | 0.16479 | 121.8979 | -0.027466 | -0.18311 | 122.1176 | 122.0306 | 121.9528 | 0.13275 | 0.054932 | 121.9116 | 0.004578 | -0.036621 | 122.2046 | 122.1817 | 122.1497 | 0.27008 | 0.23804 | 0.21973 | 0.036622 | 0.29297 | 0.16937 | 0.19226 | 0.21057 | 122.0901 | 122.1222 | -0.21973 | -0.20599 | 121.9345 | 122.081 | 121.9025 | 122.0764
3201.8906 | 122.3328 | -122.0398 | 0.086975 | -0.0051118 | -0.010525 | -0.077942 | -0.0061245 | -0.027025 | -0.051449 | -0.040178 | 0.00094606 | -0.005582 | 0.0083484 | -0.01697 | -0.22172 | -0.015565 | -0.021544 | -0.045776 | 0.091553 | -0.10529 | -0.054932 | 0.10529 | -0.073242 | 0.013733 | 0.10529 | 0.10529 | -0.10529 | 0.082397 | 0.16479 | 0.11444 | 0.17395 | 121.9345 | 0.004578 | -0.14191 | 122.1451 | 122.0535 | 121.9666 | 0.11902 | 0.032044 | 121.9345 | 0.018311 | -0.004578 | 122.2046 | 122.2137 | 122.1542 | 0.27924 | 0.21973 | 0.21057 | 0.050354 | 0.27008 | 0.18768 | 0.19684 | 0.21057 | 122.1313 | 122.1451 | -0.19226 | -0.19226 | 121.9849 | 122.1222 | 121.994 | 122.1451
3203.6719 | 122.2275 | -122.1085 | 0.13275 | -0.0051118 | -0.015225 | -0.079224 | -0.0061245 | -0.03258 | -0.052517 | -0.041033 | -0.0051575 | -0.0053684 | 0.0072802 | -0.006289 | -0.21808 | -0.018982 | -0.02368 | -0.07782 | 0.10529 | -0.11902 | -0.10071 | 0.073242 | -0.09613 | -0.036621 | -0.004578 | 0.11902 | -0.13275 | -0.032043 | 0.073242 | 0.009155 | 0.050354 | 121.9894 | -0.027465 | -0.23346 | 122.1817 | 122.0718 | 122.0123 | 0.082398 | 0.022889 | 121.9757 | -0.013732 | -0.16479 | 122.1817 | 122.1588 | 122.1176 | 0.18311 | 0.14191 | 0.19226 | 0.018311 | 0.20599 | 0.10071 | 0.22431 | 0.25177 | 122.2137 | 122.2275 | -0.25177 | -0.2655 | 122.0078 | 122.0764 | 122.0306 | 122.1039
3205.4062 | 122.2961 | -122.0718 | 0.10529 | 0.010147 | -0.01672 | -0.079438 | -0.0078335 | -0.030871 | -0.050595 | -0.04146 | -0.0051575 | -0.0075046 | 0.006853 | -0.015902 | -0.21958 | -0.018982 | -0.023467 | -0.10071 | 0.091553 | -0.11902 | -0.086975 | 0.050354 | -0.10071 | -0.013733 | 0.018311 | 0.10986 | -0.12817 | 0.027466 | 0.12817 | 0.09613 | 0.10529 | 121.9528 | -0.013733 | -0.19226 | 122.1222 | 122.0581 | 121.9711 | 0.10529 | 0.018311 | 121.9437 | 0.004577 | -0.07782 | 122.2 | 122.1771 | 122.168 | 0.23346 | 0.2243 | 0.16937 | 0.032044 | 0.25635 | 0.15564 | 0.21057 | 0.23804 | 122.1634 | 122.1817 | -0.22431 | -0.23346 | 121.9849 | 122.0993 | 121.9711 | 122.0901
3207.1875 | 122.2549 | -122.0856 | 0.14191 | 0.010147 | -0.011166 | -0.078797 | -0.0050565 | -0.030657 | -0.048245 | -0.039751 | -0.0021057 | -0.0025912 | 0.0089892 | -0.0086388 | -0.22001 | -0.016633 | -0.019835 | -0.064087 | 0.11444 | -0.12817 | -0.09613 | 0.054932 | -0.12817 | -0.045776 | 0.036621 | 0.11902 | -0.13275 | 0.013733 | 0.07782 | 0.022888 | 0.07782 | 121.9574 | -0.027466 | -0.23804 | 122.1405 | 122.0398 | 121.9574 | 0.082398 | 0 | 121.9528 | -0.022888 | -0.12817 | 122.1634 | 122.1634 | 122.1085 | 0.21057 | 0.15564 | 0.18311 | 0.032044 | 0.21057 | 0.14648 | 0.24262 | 0.25177 | 122.2 | 122.2046 | -0.27008 | -0.27466 | 121.9894 | 122.0993 | 122.0215 | 122.1222
3208.9844 | 122.2366 | -122.0993 | 0.11902 | 0.0025177 | -0.013089 | -0.080719 | -0.0095425 | -0.030016 | -0.051022 | -0.041033 | -0.0021057 | -0.00665 | 0.0087756 | -0.0073572 | -0.21958 | -0.018128 | -0.023039 | -0.10071 | 0.091553 | -0.11444 | -0.10986 | 0.050354 | -0.09613 | -0.027466 | -0.009155 | 0.1236 | -0.14191 | -0.022888 | 0.07782 | 0.013733 | 0.050354 | 121.9849 | -0.027466 | -0.22888 | 122.1497 | 122.0718 | 122.0032 | 0.086975 | 0.018311 | 121.9574 | 0.004577 | -0.14191 | 122.1771 | 122.1497 | 122.113 | 0.19226 | 0.15564 | 0.16479 | 0.004578 | 0.21973 | 0.11902 | 0.20599 | 0.2655 | 122.1909 | 122.2229 | -0.23346 | -0.26093 | 121.9894 | 122.0764 | 121.9986 | 122.0901
3210.7656 | 122.374 | -122.0856 | 0.10071 | 0.0025177 | -0.016293 | -0.078797 | -0.0076199 | -0.032793 | -0.051663 | -0.039751 | -0.0051575 | -0.0081454 | 0.0087756 | -0.015688 | -0.21937 | -0.018769 | -0.020903 | -0.050354 | 0.073242 | -0.10986 | -0.022888 | 0.15106 | -0.009155 | 0.050354 | 0.13733 | 0.091553 | -0.10986 | 0.073242 | 0.20142 | 0.15106 | 0.16479 | 121.9757 | -0.027466 | -0.1236 | 122.2366 | 122.1359 | 122.0764 | 0.16022 | 0.10071 | 121.9757 | -0.009155 | -0.027466 | 122.287 | 122.2504 | 122.2366 | 0.27466 | 0.26093 | 0.26093 | 0.086975 | 0.31128 | 0.18311 | 0.18311 | 0.20142 | 122.1588 | 122.1771 | -0.21057 | -0.21057 | 122.0627 | 122.1588 | 122.0352 | 122.2229
3212.5469 | 122.3557 | -122.081 | 0.086975 | -0.0051118 | -0.011166 | -0.080079 | -0.0054837 | -0.031298 | -0.04974 | -0.041887 | -0.0021057 | -0.0075046 | 0.0070666 | -0.011416 | -0.22107 | -0.018555 | -0.022826 | -0.059509 | 0.082397 | -0.073242 | -0.022888 | 0.13275 | -0.064087 | 0.009155 | 0.11444 | 0.11902 | -0.10529 | 0.086975 | 0.18768 | 0.10071 | 0.15564 | 122.0078 | -0.004578 | -0.10986 | 122.2137 | 122.0901 | 122.0169 | 0.082397 | 0.009155 | 121.9757 | 0.032044 | 0 | 122.2687 | 122.2366 | 122.1817 | 0.26093 | 0.20599 | 0.20599 | 0.050354 | 0.29297 | 0.19226 | 0.15564 | 0.22431 | 122.1634 | 122.2 | -0.16022 | -0.19226 | 122.0581 | 122.168 | 122.0215 | 122.1954
3214.2656 | 122.2916 | -122.1039 | 0.10986 | -0.012741 | -0.012661 | -0.079651 | -0.0056973 | -0.03258 | -0.050808 | -0.039324 | -0.0021057 | -0.0045138 | 0.0087756 | -0.0099206 | -0.22065 | -0.015565 | -0.023039 | -0.091553 | 0.10071 | -0.13733 | -0.10071 | 0.045776 | -0.10986 | -0.041199 | 0.032043 | 0.15106 | -0.1236 | 0.032043 | 0.09613 | 0.036621 | 0.10986 | 121.9666 | -0.009155 | -0.21057 | 122.1497 | 122.0627 | 121.994 | 0.09613 | 0.027466 | 121.9803 | 0.041199 | -0.07782 | 122.2 | 122.2137 | 122.1405 | 0.23346 | 0.16022 | 0.18311 | 0.036621 | 0.21973 | 0.15564 | 0.23804 | 0.27466 | 122.2046 | 122.2549 | -0.24719 | -0.23346 | 122.0032 | 122.1359 | 122.0123 | 122.1359
3216.0469 | 122.3877 | -122.0993 | 0.091553 | 0.0025177 | -0.012875 | -0.079651 | -0.0071927 | -0.030657 | -0.052731 | -0.039965 | -0.0021057 | -0.007291 | 0.010057 | -0.0084252 | -0.22043 | -0.018128 | -0.021971 | -0.068665 | 0.086975 | -0.09613 | -0.009155 | 0.14648 | -0.027466 | 0.054932 | 0.11444 | 0.11444 | -0.09613 | 0.07782 | 0.19684 | 0.14191 | 0.15564 | 122.0032 | -0.004578 | -0.10071 | 122.2458 | 122.1542 | 122.0718 | 0.15106 | 0.068664 | 122.0032 | 0.022888 | -0.013733 | 122.2961 | 122.2549 | 122.2412 | 0.25177 | 0.23804 | 0.24261 | 0.086975 | 0.29297 | 0.17395 | 0.1831 | 0.21057 | 122.1863 | 122.2137 | -0.18768 | -0.18768 | 122.0901 | 122.1771 | 122.0306 | 122.2137
3217.8281 | 122.3557 | -122.0856 | 0.082397 | -0.0051118 | -0.010739 | -0.079224 | -0.0065517 | -0.030443 | -0.048886 | -0.041033 | -0.0021057 | -0.0062228 | 0.0079212 | -0.011202 | -0.21894 | -0.01941 | -0.022185 | -0.050354 | 0.068665 | -0.091553 | -0.041199 | 0.1236 | -0.073242 | 0.027466 | 0.11444 | 0.09613 | -0.091553 | 0.086975 | 0.16937 | 0.10529 | 0.14648 | 121.994 | -0.013732 | -0.1236 | 122.2092 | 122.113 | 122.0123 | 0.11902 | 0.018311 | 121.994 | 0.013733 | 0.004578 | 122.2549 | 122.2321 | 122.1909 | 0.23804 | 0.19684 | 0.21515 | 0.050354 | 0.26093 | 0.17853 | 0.16022 | 0.18768 | 122.1542 | 122.1817 | -0.17395 | -0.17395 | 122.0444 | 122.1725 | 122.0352 | 122.2
3219.5469 | 122.2961 | -122.1085 | 0.11902 | -0.0051118 | -0.0094571 | -0.077729 | -0.0063381 | -0.027453 | -0.050595 | -0.040819 | -0.0021057 | -0.005582 | 0.0096302 | -0.0082116 | -0.22193 | -0.01706 | -0.026885 | -0.1236 | 0.11902 | -0.1236 | -0.16479 | -0.018311 | -0.19226 | -0.09613 | -0.027466 | 0.13275 | -0.14191 | -0.022888 | 0.041199 | -0.032043 | 0.059509 | 121.9849 | 0 | -0.28381 | 122.0901 | 122.0123 | 121.9162 | 0.027466 | -0.068665 | 121.9666 | 0.013732 | -0.14191 | 122.1497 | 122.168 | 122.0764 | 0.20142 | 0.10986 | 0.10528 | -0.041199 | 0.18311 | 0.11902 | 0.24261 | 0.27466 | 122.2275 | 122.2412 | -0.24261 | -0.26093 | 121.9437 | 122.0856 | 121.9849 | 122.081
3221.3281 | 122.2504 | -122.1268 | 0.12817 | -0.0051118 | -0.012875 | -0.077515 | -0.0039883 | -0.026384 | -0.04974 | -0.038896 | 0.00094606 | -0.0043002 | 0.010698 | -0.0060754 | -0.22001 | -0.016633 | -0.023253 | -0.11902 | 0.13275 | -0.11444 | -0.13275 | -0.013733 | -0.19684 | -0.11444 | -0.045776 | 0.13733 | -0.14648 | -0.032043 | 0.027466 | -0.050354 | 0.045776 | 122.0123 | 0.004577 | -0.26093 | 122.113 | 122.0123 | 121.9299 | 0 | -0.082397 | 121.9803 | 0.009155 | -0.16022 | 122.1542 | 122.1725 | 122.0764 | 0.19226 | 0.09613 | 0.10071 | -0.01831 | 0.17395 | 0.11444 | 0.24719 | 0.28381 | 122.2595 | 122.2641 | -0.24262 | -0.27466 | 121.994 | 122.0947 | 122.0078 | 122.081
3223.1094 | 122.2916 | -122.1359 | 0.13733 | -0.012741 | -0.013302 | -0.081574 | -0.0078335 | -0.029375 | -0.05209 | -0.041246 | 0.00094606 | -0.0062228 | 0.010485 | -0.0013758 | -0.21872 | -0.017914 | -0.023253 | -0.14191 | 0.14191 | -0.14191 | -0.17853 | -0.018311 | -0.15564 | -0.09613 | -0.059509 | 0.13275 | -0.14648 | -0.027466 | 0.068665 | -0.004578 | 0.07782 | 121.994 | 0.004578 | -0.31586 | 122.1176 | 122.0398 | 121.9803 | 0.045777 | -0.013733 | 121.9894 | -0.004578 | -0.16479 | 122.2046 | 122.2137 | 122.1313 | 0.2243 | 0.14191 | 0.1236 | -0.036621 | 0.21515 | 0.11902 | 0.28381 | 0.27924 | 122.2778 | 122.2687 | -0.27924 | -0.28381 | 121.9574 | 122.1085 | 121.994 | 122.0764
3224.8281 | 122.3328 | -122.1405 | 0.12817 | -0.0051118 | -0.010952 | -0.079651 | -0.0044155 | -0.029375 | -0.048886 | -0.04146 | 0.00094606 | -0.0075046 | 0.0087756 | -0.010348 | -0.22022 | -0.016846 | -0.022612 | -0.09613 | 0.11902 | -0.1236 | -0.082397 | 0.059509 | -0.1236 | -0.041199 | 0.032043 | 0.14191 | -0.14648 | 0.032043 | 0.11902 | 0.036621 | 0.10986 | 122.0169 | -0.009155 | -0.21057 | 122.2 | 122.0993 | 122.0169 | 0.082397 | 0 | 121.994 | 0.013733 | -0.096131 | 122.2595 | 122.2504 | 122.1771 | 0.25635 | 0.18311 | 0.1831 | 0.041199 | 0.2655 | 0.17853 | 0.24261 | 0.28839 | 122.2595 | 122.2824 | -0.25177 | -0.27466 | 122.0581 | 122.1725 | 122.0444 | 122.1725
3226.6094 | 122.4243 | -122.0947 | 0.082397 | 0.0025177 | -0.016293 | -0.080292 | -0.0082607 | -0.031725 | -0.051449 | -0.041246 | 0.00094606 | -0.0079318 | 0.0079212 | -0.013552 | -0.21808 | -0.018982 | -0.019835 | -0.082397 | 0.086975 | -0.10529 | -0.045776 | 0.1236 | -0.041199 | 0.050354 | 0.11444 | 0.09613 | -0.1236 | 0.091553 | 0.21057 | 0.14648 | 0.1831 | 121.9894 | 0.004578 | -0.12817 | 122.2183 | 122.1451 | 122.0535 | 0.15564 | 0.064087 | 121.9711 | 0.013733 | 0.009156 | 122.3053 | 122.2778 | 122.2412 | 0.3067 | 0.27008 | 0.22888 | 0.05951 | 0.33417 | 0.21515 | 0.19226 | 0.21973 | 122.1817 | 122.1909 | -0.18768 | -0.20599 | 122.049 | 122.1863 | 122.0123 | 122.2092
3228.4062 | 122.3969 | -122.0947 | 0.068665 | -0.0051118 | -0.011807 | -0.079438 | -0.0097561 | -0.029802 | -0.04974 | -0.041033 | -0.0051575 | -0.0062228 | 0.007494 | -0.015048 | -0.21937 | -0.015351 | -0.024962 | -0.059509 | 0.068665 | -0.082397 | -0.045776 | 0.13733 | -0.054932 | 0.022888 | 0.1236 | 0.09613 | -0.11444 | 0.07782 | 0.17853 | 0.091553 | 0.16022 | 122.0123 | 0 | -0.11444 | 122.2321 | 122.1176 | 122.0398 | 0.10528 | 0.027465 | 121.9803 | 0.027465 | 0.009155 | 122.2733 | 122.2549 | 122.1863 | 0.27466 | 0.20599 | 0.21973 | 0.036621 | 0.29297 | 0.19226 | 0.15106 | 0.21057 | 122.1634 | 122.1909 | -0.15106 | -0.18311 | 122.049 | 122.1725 | 122.0352 | 122.2183
3230.1875 | 122.2916 | -122.1954 | 0.14191 | -0.02037 | -0.014798 | -0.079011 | -0.0089017 | -0.029375 | -0.052731 | -0.040178 | -0.0051575 | -0.0051546 | 0.0066394 | -0.01163 | -0.2183 | -0.017273 | -0.02368 | -0.15564 | 0.12817 | -0.12817 | -0.16937 | -0.018311 | -0.15564 | -0.068665 | -0.059509 | 0.13733 | -0.13275 | -0.041199 | 0.054932 | -0.013733 | 0.027466 | 122.0673 | -0.013733 | -0.31128 | 122.1771 | 122.1268 | 122.0398 | 0.059509 | -0.027466 | 122.0627 | -0.004578 | -0.18311 | 122.2504 | 122.2229 | 122.1817 | 0.16022 | 0.11902 | 0.10986 | -0.041199 | 0.18768 | 0.091552 | 0.25635 | 0.27008 | 122.3236 | 122.3328 | -0.27008 | -0.27466 | 122.0261 | 122.1542 | 122.0398 | 122.1359
3231.9219 | 122.3145 | -122.1863 | 0.12817 | -0.0051118 | -0.014584 | -0.081574 | -0.0069791 | -0.031939 | -0.05209 | -0.040819 | -0.0051575 | -0.0045138 | 0.0096302 | -0.00458 | -0.22086 | -0.018128 | -0.025389 | -0.14648 | 0.11444 | -0.14648 | -0.16479 | -0.027466 | -0.16022 | -0.082397 | -0.059509 | 0.14191 | -0.14648 | -0.041199 | 0.059509 | 0.004578 | 0.050354 | 122.0398 | -0.013733 | -0.29297 | 122.1588 | 122.1039 | 122.0261 | 0.064087 | -0.013733 | 122.0398 | 0.013733 | -0.16937 | 122.2458 | 122.2366 | 122.1909 | 0.19684 | 0.15106 | 0.11902 | -0.018311 | 0.20599 | 0.10529 | 0.26093 | 0.28839 | 122.3007 | 122.3282 | -0.27466 | -0.27466 | 122.0215 | 122.1451 | 122.0398 | 122.1268
3233.7031 | 122.4243 | -122.1588 | 0.10071 | 0.010147 | -0.013943 | -0.080506 | -0.0082607 | -0.029375 | -0.052304 | -0.040392 | -0.0021057 | -0.007291 | 0.0087756 | -0.011202 | -0.22022 | -0.019623 | -0.01898 | -0.10071 | 0.09613 | -0.11902 | -0.086975 | 0.064087 | -0.086975 | 0.009155 | 0.036621 | 0.11444 | -0.1236 | 0.041199 | 0.16479 | 0.09613 | 0.12817 | 122.0398 | -0.004578 | -0.18768 | 122.2229 | 122.168 | 122.0718 | 0.12817 | 0.032044 | 122.0352 | 0.013733 | -0.059509 | 122.3236 | 122.287 | 122.2549 | 0.25177 | 0.21973 | 0.18311 | 0.032044 | 0.28839 | 0.16479 | 0.21515 | 0.23804 | 122.2549 | 122.2733 | -0.21973 | -0.2243 | 122.0718 | 122.2 | 122.0581 | 122.1954
3235.5 | 122.4472 | -122.1268 | 0.10529 | 0.0025177 | -0.013089 | -0.078797 | -0.0084743 | -0.03023 | -0.053799 | -0.042742 | 0.00094606 | -0.007291 | 0.0072802 | -0.016329 | -0.22129 | -0.018982 | -0.028807 | -0.054932 | 0.068665 | -0.09613 | -0.022888 | 0.15106 | -0.009155 | 0.050354 | 0.11444 | 0.09613 | -0.1236 | 0.082397 | 0.20142 | 0.13275 | 0.15564 | 122.0306 | -0.036621 | -0.12817 | 122.2778 | 122.1771 | 122.1176 | 0.14648 | 0.086975 | 122.0032 | -0.009156 | -0.022889 | 122.3282 | 122.2824 | 122.2595 | 0.27924 | 0.25635 | 0.24719 | 0.073242 | 0.32501 | 0.20599 | 0.16479 | 0.21973 | 122.1954 | 122.2229 | -0.20142 | -0.22888 | 122.1039 | 122.2092 | 122.0718 | 122.2412
3237.2969 | 122.4701 | -122.1451 | 0.086975 | -0.0051118 | -0.012661 | -0.080933 | -0.0080471 | -0.030443 | -0.053158 | -0.040605 | 0.00094606 | -0.0081454 | 0.0072802 | -0.017611 | -0.22065 | -0.019837 | -0.021758 | -0.09613 | 0.082397 | -0.11444 | -0.064087 | 0.10071 | -0.054932 | 0.032043 | 0.091553 | 0.10986 | -0.10986 | 0.086975 | 0.19226 | 0.14648 | 0.15564 | 122.0306 | -0.004578 | -0.15106 | 122.2458 | 122.1771 | 122.0901 | 0.14648 | 0.059509 | 122.0352 | 0.022888 | 0 | 122.3373 | 122.3007 | 122.2916 | 0.2655 | 0.25635 | 0.21515 | 0.050354 | 0.30212 | 0.19684 | 0.19684 | 0.21973 | 122.2275 | 122.2549 | -0.20142 | -0.19684 | 122.081 | 122.2321 | 122.049 | 122.2366
3239.0938 | 122.4472 | -122.1359 | 0.091553 | -0.0051118 | -0.016293 | -0.080719 | -0.0078335 | -0.029802 | -0.051876 | -0.041033 | -0.0021057 | -0.0087862 | 0.0083484 | -0.0084252 | -0.22129 | -0.017487 | -0.02368 | -0.10071 | 0.073242 | -0.10529 | -0.073242 | 0.064087 | -0.064087 | 0.009155 | 0.045776 | 0.09613 | -0.11444 | 0.054932 | 0.16479 | 0.10071 | 0.12817 | 122.0306 | -0.018311 | -0.16479 | 122.2 | 122.1451 | 122.0718 | 0.11444 | 0.041199 | 122.0215 | 0.004577 | -0.036621 | 122.3007 | 122.2641 | 122.2366 | 0.24262 | 0.21515 | 0.16937 | 0.032044 | 0.27924 | 0.16937 | 0.17853 | 0.21057 | 122.2092 | 122.2321 | -0.19684 | -0.20599 | 122.0627 | 122.1909 | 122.0352 | 122.1817
3240.8906 | 122.3557 | -122.1725 | 0.12817 | -0.0051118 | -0.011807 | -0.080719 | -0.0035611 | -0.029589 | -0.051449 | -0.038469 | 0.0039979 | -0.0047274 | 0.0089892 | -0.0030846 | -0.2215 | -0.01706 | -0.026244 | -0.10071 | 0.10529 | -0.13733 | -0.13733 | -0.022888 | -0.13275 | -0.073242 | -0.009155 | 0.14191 | -0.12817 | 0 | 0.07782 | 0.013733 | 0.086975 | 122.0352 | -0.022888 | -0.2655 | 122.1497 | 122.0993 | 122.0398 | 0.064087 | 0.004578 | 122.0444 | 0.013733 | -0.12817 | 122.2504 | 122.2595 | 122.1863 | 0.21515 | 0.14191 | 0.11444 | 0 | 0.20599 | 0.12817 | 0.24262 | 0.27008 | 122.2778 | 122.3145 | -0.2655 | -0.25635 | 122.0352 | 122.1725 | 122.0718 | 122.1634
3242.6719 | 122.406 | -122.1588 | 0.091553 | -0.0051118 | -0.013089 | -0.079011 | -0.0074063 | -0.032366 | -0.050167 | -0.043596 | -0.0051575 | -0.0053684 | 0.0087756 | -0.016757 | -0.22022 | -0.018342 | -0.025603 | -0.082397 | 0.09613 | -0.086975 | -0.07782 | 0.07782 | -0.09613 | 0 | 0.045776 | 0.10071 | -0.12817 | 0.027466 | 0.13733 | 0.068665 | 0.11902 | 122.0718 | 0.004577 | -0.16937 | 122.2366 | 122.1588 | 122.0627 | 0.086975 | -0.009155 | 122.0306 | 0.009155 | -0.064087 | 122.2961 | 122.2778 | 122.2275 | 0.24719 | 0.19684 | 0.16479 | 0.009155 | 0.2655 | 0.15564 | 0.1831 | 0.22888 | 122.2549 | 122.2595 | -0.17853 | -0.21973 | 122.081 | 122.1863 | 122.0764 | 122.2046
3244.4062 | 122.406 | -122.1725 | 0.11444 | -0.012741 | -0.011166 | -0.078583 | -0.0020657 | -0.026384 | -0.050808 | -0.040178 | -0.0021057 | -0.0043002 | 0.0081348 | -0.013339 | -0.22022 | -0.018555 | -0.026457 | -0.12817 | 0.13275 | -0.14648 | -0.12817 | -0.004578 | -0.17395 | -0.082397 | 0.022888 | 0.1236 | -0.1236 | 0.054932 | 0.11444 | 0.032043 | 0.10071 | 122.0261 | 0.01831 | -0.24262 | 122.168 | 122.0901 | 121.9986 | 0.064087 | -0.027466 | 122.0489 | 0.009155 | -0.059509 | 122.287 | 122.2733 | 122.2046 | 0.2243 | 0.15564 | 0.14191 | 0.01831 | 0.23804 | 0.17853 | 0.27924 | 0.24719 | 122.3053 | 122.2961 | -0.26093 | -0.23804 | 122.0444 | 122.2275 | 122.0444 | 122.1954
3246.2031 | 122.4564 | -122.1771 | 0.10071 | -0.0051118 | -0.0094571 | -0.079224 | -0.0048427 | -0.02788 | -0.049313 | -0.038896 | 0.00094606 | -0.005582 | 0.0077076 | -0.0099206 | -0.2183 | -0.017914 | -0.026671 | -0.10529 | 0.11444 | -0.14191 | -0.13275 | 0.004578 | -0.16022 | -0.050354 | 0.036621 | 0.14191 | -0.12817 | 0.064087 | 0.14648 | 0.059509 | 0.1236 | 122.0352 | 0.013733 | -0.23346 | 122.1817 | 122.1268 | 122.0169 | 0.091553 | -0.01831 | 122.049 | 0.041199 | -0.036621 | 122.3236 | 122.3007 | 122.2366 | 0.25177 | 0.18768 | 0.14649 | 0.009156 | 0.27466 | 0.19226 | 0.25635 | 0.27008 | 122.2916 | 122.319 | -0.24262 | -0.22888 | 122.0444 | 122.2412 | 122.0718 | 122.2137
3247.9219 | 122.4838 | -122.1954 | 0.09613 | 0.0025177 | -0.014157 | -0.08136 | -0.0091153 | -0.033648 | -0.050167 | -0.037828 | -0.0051575 | -0.0079318 | 0.0072802 | -0.022524 | -0.21958 | -0.018555 | -0.023039 | -0.073242 | 0.082397 | -0.10071 | -0.018311 | 0.15564 | -0.022888 | 0.045776 | 0.10986 | 0.091553 | -0.10071 | 0.09613 | 0.21057 | 0.16022 | 0.16479 | 122.0947 | -0.013733 | -0.11444 | 122.3511 | 122.2412 | 122.1725 | 0.14648 | 0.07782 | 122.0947 | -0.004577 | 0 | 122.406 | 122.3602 | 122.3557 | 0.2655 | 0.26093 | 0.25635 | 0.082397 | 0.31128 | 0.19684 | 0.18311 | 0.19226 | 122.2778 | 122.287 | -0.19684 | -0.19684 | 122.1771 | 122.2916 | 122.1222 | 122.3053
3249.7031 | 122.4335 | -122.1817 | 0.10529 | -0.012741 | -0.01202 | -0.080292 | -0.0076199 | -0.030871 | -0.052304 | -0.042742 | -0.0021057 | -0.00665 | 0.010485 | -0.016543 | -0.22107 | -0.018769 | -0.021971 | -0.10986 | 0.086975 | -0.11444 | -0.10071 | 0.059509 | -0.10529 | -0.013733 | 0.022888 | 0.10529 | -0.1236 | 0.032043 | 0.12817 | 0.07782 | 0.10986 | 122.0673 | -0.018311 | -0.20599 | 122.2412 | 122.168 | 122.0764 | 0.10071 | 0.009155 | 122.0581 | 0 | -0.073243 | 122.3099 | 122.2916 | 122.2595 | 0.23346 | 0.20142 | 0.17395 | 0.013733 | 0.25177 | 0.15564 | 0.20142 | 0.22888 | 122.2687 | 122.287 | -0.21973 | -0.22888 | 122.081 | 122.2137 | 122.0718 | 122.2046
3251.5156 | 122.4792 | -122.1588 | 0.07782 | -0.012741 | -0.011807 | -0.076874 | -0.0037747 | -0.028307 | -0.049099 | -0.040819 | -0.0051575 | -0.0040866 | 0.0062122 | -0.006289 | -0.22214 | -0.017487 | -0.02368 | -0.036621 | 0.082397 | -0.086975 | -0.036621 | 0.11444 | -0.07782 | 0.027466 | 0.12817 | 0.11902 | -0.10529 | 0.10986 | 0.18768 | 0.11444 | 0.16937 | 122.0718 | 0.004577 | -0.11444 | 122.2733 | 122.1863 | 122.081 | 0.11444 | 0.009155 | 122.0535 | 0.041199 | 0.032043 | 122.3465 | 122.3282 | 122.2733 | 0.27466 | 0.21973 | 0.20142 | 0.050354 | 0.29297 | 0.21515 | 0.16937 | 0.22431 | 122.2412 | 122.2778 | -0.16479 | -0.18311 | 122.1222 | 122.2687 | 122.1222 | 122.287
3253.2344 | 122.493 | -122.1634 | 0.082397 | 0.0025177 | -0.010098 | -0.078156 | -0.0065517 | -0.031298 | -0.051022 | -0.041887 | -0.0021057 | -0.0062228 | 0.0092028 | -0.0090662 | -0.22214 | -0.018769 | -0.022612 | -0.050354 | 0.073242 | -0.10071 | -0.027466 | 0.10529 | -0.07782 | 0.013733 | 0.11902 | 0.09613 | -0.082397 | 0.10529 | 0.1831 | 0.11444 | 0.16937 | 122.0627 | -0.009155 | -0.10986 | 122.2687 | 122.1771 | 122.0856 | 0.11444 | 0.022888 | 122.081 | 0.013733 | 0.022889 | 122.3465 | 122.3328 | 122.2778 | 0.25177 | 0.19684 | 0.20599 | 0.073242 | 0.2655 | 0.18768 | 0.17395 | 0.17853 | 122.2366 | 122.2595 | -0.18311 | -0.16479 | 122.1359 | 122.2687 | 122.113 | 122.2824
3255.0156 | 122.3648 | -122.2137 | 0.11444 | -0.0051118 | -0.0098843 | -0.079224 | -0.0046291 | -0.03023 | -0.051876 | -0.043596 | -0.0021057 | -0.0043002 | 0.0087756 | -0.0020166 | -0.22065 | -0.019623 | -0.023467 | -0.13275 | 0.1236 | -0.14648 | -0.15106 | -0.041199 | -0.21057 | -0.10529 | -0.045776 | 0.16022 | -0.15564 | -0.036621 | 0.027466 | -0.041199 | 0.041199 | 122.0673 | 0.009155 | -0.2655 | 122.1725 | 122.1085 | 122.0032 | 0.041198 | -0.064087 | 122.0581 | 0.045776 | -0.15106 | 122.2412 | 122.2549 | 122.1725 | 0.19684 | 0.11444 | 0.10529 | -0.004578 | 0.18311 | 0.11902 | 0.27008 | 0.31586 | 122.3373 | 122.374 | -0.26093 | -0.27008 | 122.0627 | 122.1771 | 122.081 | 122.168
3256.8125 | 122.406 | -122.2275 | 0.13733 | -0.0051118 | -0.01202 | -0.079438 | -0.0031337 | -0.031298 | -0.050808 | -0.04146 | -0.0051575 | -0.0057956 | 0.0072802 | -0.010348 | -0.21958 | -0.017701 | -0.02368 | -0.073242 | 0.10986 | -0.13275 | -0.091553 | 0.045776 | -0.10071 | -0.032043 | 0.064087 | 0.1236 | -0.11902 | 0.041199 | 0.10529 | 0.045776 | 0.091553 | 122.0947 | -0.027466 | -0.22888 | 122.2733 | 122.1954 | 122.1268 | 0.10071 | 0.032043 | 122.1085 | -0.013733 | -0.09613 | 122.3328 | 122.319 | 122.2733 | 0.21057 | 0.16479 | 0.17853 | 0.041198 | 0.22431 | 0.16022 | 0.24261 | 0.24261 | 122.3373 | 122.3511 | -0.27008 | -0.25635 | 122.1359 | 122.2687 | 122.1542 | 122.2916
3258.5312 | 122.493 | -122.1817 | 0.10071 | -0.0051118 | -0.017361 | -0.081788 | -0.0078335 | -0.034502 | -0.051876 | -0.043169 | -0.0021057 | -0.0064364 | 0.0083484 | -0.017184 | -0.21979 | -0.018555 | -0.019408 | -0.07782 | 0.068665 | -0.10529 | -0.054932 | 0.12817 | -0.018311 | 0.050354 | 0.13275 | 0.10529 | -0.11902 | 0.10986 | 0.21515 | 0.15106 | 0.16937 | 122.0764 | -0.032043 | -0.15564 | 122.3099 | 122.2321 | 122.1634 | 0.15564 | 0.086975 | 122.0627 | 0.004578 | 0.009155 | 122.3969 | 122.3511 | 122.3328 | 0.28839 | 0.27008 | 0.23346 | 0.050354 | 0.33417 | 0.22888 | 0.17395 | 0.22431 | 122.2504 | 122.287 | -0.20599 | -0.21973 | 122.1268 | 122.2916 | 122.1039 | 122.3145
3260.3281 | 122.374 | -122.2275 | 0.12817 | -0.0051118 | -0.010525 | -0.077729 | -0.0046291 | -0.028948 | -0.048672 | -0.041246 | 0.00094606 | -0.003232 | 0.0089892 | -0.0094934 | -0.22107 | -0.016419 | -0.024748 | -0.086975 | 0.10071 | -0.1236 | -0.13733 | -0.004578 | -0.18768 | -0.10071 | -0.022888 | 0.14648 | -0.14648 | -0.022888 | 0.050354 | -0.041199 | 0.050354 | 122.1039 | -0.027466 | -0.2655 | 122.2229 | 122.1268 | 122.0398 | 0.022888 | -0.064087 | 122.081 | 0.01831 | -0.15106 | 122.2778 | 122.2778 | 122.1863 | 0.19684 | 0.10529 | 0.11902 | -0.013733 | 0.19684 | 0.1236 | 0.2243 | 0.29297 | 122.3282 | 122.374 | -0.25177 | -0.27466 | 122.0901 | 122.2046 | 122.1405 | 122.2046
3262.125 | 122.3969 | -122.2549 | 0.13275 | 0.0025177 | -0.015652 | -0.081574 | -0.0074063 | -0.031939 | -0.051022 | -0.040605 | 0.00094606 | -0.0053684 | 0.006853 | -0.013979 | -0.21937 | -0.017701 | -0.020903 | -0.082397 | 0.091553 | -0.11444 | -0.091553 | 0.07782 | -0.068665 | 0 | 0.018311 | 0.11902 | -0.1236 | -0.022888 | 0.091553 | 0.022888 | 0.050354 | 122.1405 | -0.041198 | -0.2243 | 122.3328 | 122.2549 | 122.1863 | 0.11444 | 0.045776 | 122.1313 | -0.013732 | -0.15564 | 122.3465 | 122.3053 | 122.2778 | 0.17395 | 0.14648 | 0.19226 | 0.022888 | 0.21515 | 0.10071 | 0.20599 | 0.24261 | 122.3465 | 122.374 | -0.24719 | -0.25635 | 122.1634 | 122.2321 | 122.1725 | 122.2733
3263.8438 | 122.493 | -122.1909 | 0.086975 | -0.0051118 | -0.0090299 | -0.077515 | -0.0048427 | -0.028307 | -0.049313 | -0.039965 | -0.0051575 | -0.0047274 | 0.0083484 | -0.0054346 | -0.22043 | -0.018769 | -0.022398 | -0.068665 | 0.073242 | -0.10986 | -0.045776 | 0.09613 | -0.09613 | -0.009155 | 0.09613 | 0.09613 | -0.091553 | 0.10529 | 0.16937 | 0.10986 | 0.17395 | 122.081 | -0.013733 | -0.13275 | 122.287 | 122.1817 | 122.0947 | 0.10071 | 0.013733 | 122.0993 | 0.009155 | 0.018311 | 122.3602 | 122.3648 | 122.3007 | 0.2655 | 0.20142 | 0.20599 | 0.064087 | 0.26093 | 0.19684 | 0.18311 | 0.18768 | 122.2641 | 122.287 | -0.19684 | -0.17853 | 122.1451 | 122.2961 | 122.1222 | 122.287
3265.625 | 122.3831 | -122.2366 | 0.14648 | 0.0025177 | -0.017147 | -0.083069 | -0.0063381 | -0.032152 | -0.052731 | -0.040605 | -0.0021057 | -0.0060092 | 0.010698 | -0.012911 | -0.21979 | -0.019196 | -0.017912 | -0.13275 | 0.1236 | -0.13733 | -0.16479 | 0 | -0.14191 | -0.07782 | -0.041199 | 0.13733 | -0.12817 | -0.059509 | 0.059509 | 0 | 0.041199 | 122.0993 | -0.022888 | -0.31128 | 122.2366 | 122.1588 | 122.0947 | 0.059509 | -0.004578 | 122.1085 | -0.009155 | -0.20599 | 122.2961 | 122.2778 | 122.2366 | 0.16937 | 0.12817 | 0.13733 | -0.027466 | 0.18768 | 0.068665 | 0.26093 | 0.2655 | 122.3602 | 122.374 | -0.28381 | -0.27466 | 122.0718 | 122.1771 | 122.1039 | 122.1954
3267.4219 | 122.4564 | -122.2 | 0.091553 | -0.012741 | -0.01202 | -0.08136 | -0.0048427 | -0.025316 | -0.050381 | -0.041674 | -0.0021057 | -0.0043002 | 0.0092028 | -0.012911 | -0.22001 | -0.01706 | -0.020049 | -0.11902 | 0.11444 | -0.15564 | -0.15564 | 0.004578 | -0.17853 | -0.07782 | 0.004578 | 0.13733 | -0.11902 | 0.032043 | 0.11444 | 0.045776 | 0.09613 | 122.0444 | 0.022888 | -0.24719 | 122.2046 | 122.1222 | 122.0215 | 0.07782 | -0.022888 | 122.081 | 0.045776 | -0.05951 | 122.3145 | 122.2961 | 122.2458 | 0.21515 | 0.16479 | 0.16022 | 0 | 0.23346 | 0.15106 | 0.27008 | 0.25635 | 122.3145 | 122.3373 | -0.24719 | -0.21057 | 122.0444 | 122.2321 | 122.081 | 122.2046
3269.2031 | 122.525 | -122.2229 | 0.091553 | 0.0025177 | -0.015225 | -0.082215 | -0.0099697 | -0.02788 | -0.051876 | -0.040605 | -0.0021057 | -0.0068636 | 0.006853 | -0.01227 | -0.21979 | -0.018769 | -0.01898 | -0.068665 | 0.082397 | -0.10529 | -0.013733 | 0.16022 | -0.013733 | 0.050354 | 0.11902 | 0.10071 | -0.10986 | 0.086975 | 0.20142 | 0.16022 | 0.15106 | 122.1176 | -0.009156 | -0.10529 | 122.3831 | 122.2733 | 122.2092 | 0.15564 | 0.091553 | 122.113 | 0.009155 | -0.004578 | 122.4243 | 122.374 | 122.3831 | 0.26093 | 0.27008 | 0.2655 | 0.091553 | 0.31128 | 0.19684 | 0.18768 | 0.21057 | 122.3053 | 122.3236 | -0.19684 | -0.20142 | 122.2092 | 122.3099 | 122.1542 | 122.3419
3271 | 122.4838 | -122.2229 | 0.086975 | -0.0051118 | -0.013729 | -0.079438 | -0.0076199 | -0.03023 | -0.050595 | -0.042528 | -0.0021057 | -0.0081454 | 0.0092028 | -0.013339 | -0.21979 | -0.018982 | -0.02368 | -0.10529 | 0.09613 | -0.10529 | -0.10071 | 0.064087 | -0.10986 | -0.018311 | 0.027466 | 0.11902 | -0.10986 | 0.032043 | 0.14191 | 0.064087 | 0.1236 | 122.1176 | 0.009155 | -0.18768 | 122.287 | 122.2046 | 122.113 | 0.086975 | -0.004577 | 122.113 | 0.032044 | -0.054932 | 122.3648 | 122.3465 | 122.287 | 0.23346 | 0.17395 | 0.16937 | 0.004578 | 0.25177 | 0.14191 | 0.20142 | 0.22888 | 122.319 | 122.3419 | -0.19226 | -0.19684 | 122.1222 | 122.2549 | 122.1176 | 122.2504
3272.7344 | 122.525 | -122.2183 | 0.091553 | -0.0051118 | -0.015225 | -0.080292 | -0.0084743 | -0.034502 | -0.052517 | -0.043596 | -0.0051575 | -0.0079318 | 0.0059986 | -0.01227 | -0.22022 | -0.018555 | -0.024962 | -0.086975 | 0.068665 | -0.10071 | -0.07782 | 0.086975 | -0.050354 | 0.032043 | 0.073242 | 0.10986 | -0.10071 | 0.059509 | 0.19226 | 0.13275 | 0.14191 | 122.1176 | -0.022888 | -0.16937 | 122.3053 | 122.2504 | 122.168 | 0.13275 | 0.050354 | 122.1176 | 0.01831 | -0.032044 | 122.4106 | 122.3602 | 122.3511 | 0.24262 | 0.23346 | 0.18768 | 0.022888 | 0.29297 | 0.16022 | 0.16937 | 0.21057 | 122.287 | 122.3282 | -0.19226 | -0.19226 | 122.1405 | 122.2778 | 122.1313 | 122.2916
3274.4844 | 122.5113 | -122.2641 | 0.10071 | -0.0051118 | -0.014157 | -0.082215 | -0.0082607 | -0.031511 | -0.049954 | -0.040605 | 0.00094606 | -0.0062228 | 0.010057 | -0.010134 | -0.22043 | -0.020478 | -0.026457 | -0.059509 | 0.082397 | -0.09613 | -0.022888 | 0.1236 | -0.032043 | 0.036621 | 0.091553 | 0.10071 | -0.10986 | 0.041199 | 0.17853 | 0.10986 | 0.12817 | 122.168 | -0.018311 | -0.1236 | 122.3877 | 122.3007 | 122.2321 | 0.13275 | 0.064087 | 122.1542 | 0 | -0.059509 | 122.4426 | 122.3923 | 122.374 | 0.23804 | 0.21973 | 0.21973 | 0.073242 | 0.28839 | 0.15106 | 0.17853 | 0.21057 | 122.3465 | 122.3648 | -0.19684 | -0.21057 | 122.2412 | 122.3053 | 122.2046 | 122.3557
3276.2812 | 122.4838 | -122.2595 | 0.09613 | -0.012741 | -0.01437 | -0.08136 | -0.0054837 | -0.03023 | -0.04974 | -0.042528 | 0.00094606 | -0.0064364 | 0.0070666 | -0.018466 | -0.22022 | -0.018342 | -0.022826 | -0.10529 | 0.082397 | -0.09613 | -0.086975 | 0.050354 | -0.10529 | -0.009155 | 0.041199 | 0.10071 | -0.13275 | 0.018311 | 0.13275 | 0.068665 | 0.10071 | 122.1634 | -0.013733 | -0.1831 | 122.3099 | 122.2504 | 122.1542 | 0.086975 | -0.009156 | 122.1268 | 0.004578 | -0.077819 | 122.3923 | 122.3602 | 122.3282 | 0.23346 | 0.20142 | 0.14648 | 0.009155 | 0.2655 | 0.15106 | 0.17853 | 0.23346 | 122.3419 | 122.3602 | -0.19226 | -0.22888 | 122.1725 | 122.2778 | 122.1542 | 122.3007
3278.0156 | 122.525 | -122.2275 | 0.091553 | -0.0051118 | -0.01202 | -0.080079 | -0.0018521 | -0.028307 | -0.051876 | -0.04146 | -0.0021057 | -0.0053684 | 0.0089892 | -0.0088526 | -0.22193 | -0.016419 | -0.023253 | -0.10986 | 0.10071 | -0.13275 | -0.09613 | 0.027466 | -0.13733 | -0.045776 | 0.041199 | 0.13275 | -0.1236 | 0.082397 | 0.15106 | 0.082397 | 0.14648 | 122.0947 | 0.009155 | -0.18768 | 122.2549 | 122.1817 | 122.0901 | 0.086975 | -0.004578 | 122.1039 | 0.041198 | -0.009156 | 122.3785 | 122.374 | 122.3099 | 0.27008 | 0.20599 | 0.16022 | 0.036621 | 0.27466 | 0.20599 | 0.23346 | 0.25635 | 122.3282 | 122.3602 | -0.2243 | -0.21515 | 122.1313 | 122.3099 | 122.1176 | 122.2687
3279.75 | 122.438 | -122.287 | 0.11444 | -0.0051118 | -0.010525 | -0.080079 | -0.0020657 | -0.028734 | -0.051449 | -0.039965 | 0.00094606 | -0.0060092 | 0.0070666 | -0.0050072 | -0.21937 | -0.01706 | -0.022398 | -0.1236 | 0.11902 | -0.14648 | -0.16022 | -0.027466 | -0.19684 | -0.09613 | -0.027466 | 0.15106 | -0.13275 | -0.013733 | 0.050354 | -0.027466 | 0.059509 | 122.1405 | 0.004578 | -0.27466 | 122.2595 | 122.1909 | 122.0901 | 0.050354 | -0.050354 | 122.1542 | 0.036621 | -0.12817 | 122.3373 | 122.3465 | 122.2595 | 0.19226 | 0.10529 | 0.11902 | -0.013733 | 0.18311 | 0.11902 | 0.2655 | 0.28381 | 122.406 | 122.438 | -0.26093 | -0.24719 | 122.1268 | 122.2733 | 122.1634 | 122.2595
3281.5469 | 122.5937 | -122.2595 | 0.091553 | -0.0051118 | -0.015438 | -0.079865 | -0.0086879 | -0.035357 | -0.053372 | -0.041674 | -0.0021057 | -0.0075046 | 0.0059986 | -0.012484 | -0.21937 | -0.017914 | -0.026457 | -0.068665 | 0.07782 | -0.10986 | -0.018311 | 0.16022 | -0.004578 | 0.068665 | 0.15106 | 0.10529 | -0.10529 | 0.09613 | 0.20142 | 0.14191 | 0.16479 | 122.1497 | -0.013733 | -0.10986 | 122.4197 | 122.3282 | 122.2549 | 0.17853 | 0.10529 | 122.1542 | 0.013733 | 0.004577 | 122.4609 | 122.4243 | 122.4014 | 0.27008 | 0.24719 | 0.27008 | 0.091552 | 0.3067 | 0.20142 | 0.18768 | 0.21057 | 122.3373 | 122.3648 | -0.20142 | -0.19684 | 122.2412 | 122.3557 | 122.1909 | 122.4106
3283.3281 | 122.4152 | -122.2504 | 0.11902 | -0.012741 | -0.010525 | -0.079651 | -0.0039883 | -0.031298 | -0.049954 | -0.03911 | -0.0021057 | -0.003873 | 0.0062122 | -0.010134 | -0.22022 | -0.01706 | -0.020689 | -0.10529 | 0.12817 | -0.13733 | -0.15564 | -0.041199 | -0.19684 | -0.10986 | -0.068665 | 0.14648 | -0.14648 | -0.036621 | 0.009155 | -0.050354 | 0.032043 | 122.113 | 0.009155 | -0.27466 | 122.2092 | 122.1405 | 122.0535 | 0.027466 | -0.059509 | 122.1039 | 0.027465 | -0.15564 | 122.2595 | 122.2824 | 122.2 | 0.17853 | 0.09613 | 0.09613 | -0.018311 | 0.15564 | 0.10986 | 0.2655 | 0.29297 | 122.3785 | 122.3969 | -0.25635 | -0.2655 | 122.0947 | 122.2137 | 122.1451 | 122.1817
3285.0625 | 122.4976 | -122.2961 | 0.10986 | 0.0025177 | -0.0096707 | -0.078156 | -0.0037747 | -0.02553 | -0.050381 | -0.040819 | 0.00094606 | -0.004941 | 0.0081348 | -0.0056482 | -0.22043 | -0.017487 | -0.024535 | -0.07782 | 0.11444 | -0.10986 | -0.09613 | 0.050354 | -0.11444 | -0.041199 | 0.045776 | 0.13733 | -0.13733 | 0.036621 | 0.09613 | 0.050354 | 0.10986 | 122.1863 | 0.004578 | -0.20599 | 122.3465 | 122.2549 | 122.1817 | 0.068664 | -0.004578 | 122.1588 | 0.027466 | -0.073242 | 122.3923 | 122.406 | 122.3465 | 0.24719 | 0.18768 | 0.16022 | 0.013733 | 0.23346 | 0.17395 | 0.2243 | 0.27466 | 122.4106 | 122.4335 | -0.21973 | -0.24719 | 122.2 | 122.3328 | 122.2183 | 122.3419
3286.8594 | 122.5662 | -122.2687 | 0.082397 | -0.0051118 | -0.011593 | -0.079224 | -0.0095425 | -0.033648 | -0.050167 | -0.041674 | -0.0082091 | -0.0096408 | 0.0089892 | -0.009707 | -0.22043 | -0.020478 | -0.024321 | -0.086975 | 0.091553 | -0.091553 | -0.064087 | 0.11902 | -0.032043 | 0.045776 | 0.11444 | 0.09613 | -0.11444 | 0.09613 | 0.21515 | 0.14191 | 0.15564 | 122.1771 | 0.009156 | -0.14648 | 122.3877 | 122.3145 | 122.2366 | 0.13733 | 0.05951 | 122.1542 | 0.013733 | 0.013733 | 122.4838 | 122.4243 | 122.4106 | 0.27008 | 0.25635 | 0.21057 | 0.027466 | 0.32959 | 0.21057 | 0.18311 | 0.21057 | 122.3602 | 122.3648 | -0.17395 | -0.19684 | 122.2046 | 122.3648 | 122.1817 | 122.3831
3288.6406 | 122.4884 | -122.2733 | 0.11902 | -0.0051118 | -0.010098 | -0.079651 | -0.0046291 | -0.028521 | -0.049954 | -0.040819 | -0.0021057 | -0.0057956 | 0.006853 | -0.013339 | -0.22107 | -0.018769 | -0.02368 | -0.12817 | 0.1236 | -0.14191 | -0.16022 | -0.013733 | -0.1831 | -0.064087 | -0.004578 | 0.13275 | -0.12817 | 0.009155 | 0.086975 | 0.022888 | 0.10071 | 122.1313 | 0.004577 | -0.27924 | 122.2595 | 122.2092 | 122.0901 | 0.07782 | -0.041198 | 122.1451 | 0.013732 | -0.10986 | 122.3602 | 122.374 | 122.2961 | 0.22888 | 0.15106 | 0.12817 | -0.01831 | 0.21515 | 0.13733 | 0.2655 | 0.26093 | 122.3969 | 122.406 | -0.26093 | -0.24719 | 122.113 | 122.2824 | 122.1451 | 122.2687
3290.4219 | 122.4792 | -122.3099 | 0.11444 | -0.0051118 | -0.012448 | -0.079224 | -0.0046291 | -0.027453 | -0.051022 | -0.040819 | -0.0051575 | -0.007291 | 0.0079212 | -0.0015894 | -0.2183 | -0.017487 | -0.021758 | -0.12817 | 0.1236 | -0.13733 | -0.15106 | -0.022888 | -0.18768 | -0.091553 | -0.027466 | 0.13733 | -0.11902 | 0 | 0.07782 | 0.004578 | 0.073242 | 122.1725 | 0.009155 | -0.2655 | 122.287 | 122.2183 | 122.1222 | 0.045776 | -0.050354 | 122.1909 | 0.022888 | -0.11444 | 122.3877 | 122.3831 | 122.3145 | 0.19226 | 0.1236 | 0.11444 | -0.013733 | 0.19684 | 0.11902 | 0.26093 | 0.25635 | 122.4335 | 122.4472 | -0.25177 | -0.23346 | 122.1588 | 122.3099 | 122.1817 | 122.2824
3292.1562 | 122.58 | -122.2778 | 0.07782 | -0.0051118 | -0.015652 | -0.08136 | -0.0082607 | -0.031084 | -0.050808 | -0.039751 | 0.00094606 | -0.007291 | 0.005785 | -0.013339 | -0.21851 | -0.018769 | -0.026671 | -0.086975 | 0.091553 | -0.09613 | -0.064087 | 0.10071 | -0.050354 | 0.018311 | 0.068665 | 0.11444 | -0.10529 | 0.086975 | 0.20599 | 0.14191 | 0.14648 | 122.1817 | 0.013733 | -0.14191 | 122.3785 | 122.2961 | 122.2275 | 0.11444 | 0.045776 | 122.1725 | 0.036621 | 0.009155 | 122.4838 | 122.4243 | 122.4197 | 0.25177 | 0.24719 | 0.19684 | 0.032043 | 0.31128 | 0.19226 | 0.18768 | 0.21973 | 122.3694 | 122.3923 | -0.17395 | -0.18311 | 122.2137 | 122.3648 | 122.1909 | 122.3465
3293.9531 | 122.4289 | -122.3236 | 0.1236 | -0.0051118 | -0.0081753 | -0.079011 | -0.0012111 | -0.026598 | -0.047604 | -0.042955 | -0.0021057 | -0.0045138 | 0.0053576 | -0.015688 | -0.21744 | -0.018128 | -0.025816 | -0.10071 | 0.13733 | -0.11902 | -0.15564 | -0.045776 | -0.20142 | -0.10986 | -0.073242 | 0.14191 | -0.12817 | -0.045776 | 0.032043 | -0.050354 | 0.036621 | 122.2046 | 0.013733 | -0.27924 | 122.2778 | 122.2137 | 122.1222 | 0.009156 | -0.082397 | 122.1954 | 0.018311 | -0.16937 | 122.3557 | 122.3602 | 122.2733 | 0.1648 | 0.07782 | 0.073243 | -0.036621 | 0.16022 | 0.082398 | 0.25635 | 0.27008 | 122.4609 | 122.4655 | -0.24261 | -0.25177 | 122.168 | 122.2778 | 122.2229 | 122.2504
3295.6719 | 122.4564 | -122.3282 | 0.10986 | 0.0025177 | -0.016079 | -0.082215 | -0.0054837 | -0.030871 | -0.053585 | -0.041674 | 0.00094606 | -0.0064364 | 0.0098438 | -0.016116 | -0.21744 | -0.018555 | -0.022185 | -0.14191 | 0.10986 | -0.13275 | -0.16937 | -0.013733 | -0.15106 | -0.068665 | -0.032043 | 0.16022 | -0.13733 | -0.041199 | 0.064087 | -0.013733 | 0.045776 | 122.1954 | 0 | -0.27924 | 122.3145 | 122.2595 | 122.1771 | 0.064086 | -0.018311 | 122.1909 | 0.050354 | -0.15106 | 122.3923 | 122.374 | 122.3145 | 0.18311 | 0.1236 | 0.11902 | -0.036622 | 0.20142 | 0.09613 | 0.24261 | 0.29755 | 122.438 | 122.4884 | -0.24261 | -0.24719 | 122.1588 | 122.287 | 122.1863 | 122.2961
3297.4531 | 122.5342 | -122.2961 | 0.10986 | -0.0051118 | -0.012875 | -0.080292 | -0.0093289 | -0.029802 | -0.049954 | -0.041887 | 0.00094606 | -0.005582 | 0.0070666 | -0.0090662 | -0.22065 | -0.018769 | -0.019835 | -0.073242 | 0.07782 | -0.10986 | -0.050354 | 0.12817 | -0.036621 | 0.018311 | 0.068665 | 0.1236 | -0.086975 | 0.022888 | 0.14191 | 0.091553 | 0.11444 | 122.1863 | -0.032043 | -0.16022 | 122.4243 | 122.3145 | 122.2595 | 0.12817 | 0.073242 | 122.2092 | 0.013733 | -0.086975 | 122.4381 | 122.4106 | 122.3877 | 0.20142 | 0.17853 | 0.23804 | 0.059509 | 0.22888 | 0.10986 | 0.18768 | 0.21057 | 122.374 | 122.4197 | -0.21973 | -0.19684 | 122.2458 | 122.319 | 122.2229 | 122.3648
3299.1719 | 122.5021 | -122.3053 | 0.13275 | 0.0025177 | -0.011593 | -0.077942 | -0.0056973 | -0.026384 | -0.051449 | -0.042955 | -0.0051575 | -0.0047274 | 0.0094166 | -0.0030846 | -0.22129 | -0.017487 | -0.020689 | -0.082397 | 0.11444 | -0.12817 | -0.10529 | 0.059509 | -0.11444 | -0.041199 | 0.054932 | 0.12817 | -0.11902 | 0.013733 | 0.10071 | 0.041199 | 0.10071 | 122.1771 | -0.01831 | -0.23804 | 122.3648 | 122.2641 | 122.1909 | 0.086975 | 0.013733 | 122.1863 | -0.004577 | -0.11902 | 122.406 | 122.406 | 122.3465 | 0.21973 | 0.16022 | 0.18768 | 0.022888 | 0.21973 | 0.13275 | 0.24262 | 0.24719 | 122.4197 | 122.4335 | -0.26093 | -0.25177 | 122.2 | 122.319 | 122.2229 | 122.3602
3300.9688 | 122.4747 | -122.3419 | 0.11902 | -0.0051118 | -0.010098 | -0.079011 | -0.0039883 | -0.027239 | -0.050595 | -0.040819 | 0.00094606 | -0.004941 | 0.0094166 | -0.015688 | -0.21958 | -0.019837 | -0.019621 | -0.059509 | 0.1236 | -0.14191 | -0.10529 | 0.032043 | -0.1236 | -0.050354 | 0.041199 | 0.13275 | -0.11444 | 0.004578 | 0.091553 | 0.004578 | 0.086975 | 122.2 | 0.004577 | -0.22431 | 122.374 | 122.2916 | 122.2183 | 0.091553 | 0.018311 | 122.2275 | 0.013732 | -0.11444 | 122.4335 | 122.4289 | 122.3465 | 0.20142 | 0.11902 | 0.17395 | 0.036621 | 0.20599 | 0.11902 | 0.2655 | 0.24719 | 122.4655 | 122.4747 | -0.26093 | -0.23346 | 122.2366 | 122.3465 | 122.2824 | 122.3831
3302.7656 | 122.4884 | -122.3373 | 0.13733 | 0.0025177 | -0.01202 | -0.081147 | -0.0086879 | -0.031939 | -0.050381 | -0.042101 | -0.0051575 | -0.0045138 | 0.010057 | -0.010989 | -0.21894 | -0.018342 | -0.021117 | -0.11444 | 0.12817 | -0.14191 | -0.16937 | -0.018311 | -0.15106 | -0.068665 | -0.036621 | 0.14191 | -0.14191 | -0.032043 | 0.07782 | 0.013733 | 0.068665 | 122.1954 | -0.009155 | -0.3067 | 122.319 | 122.2687 | 122.1863 | 0.073242 | -0.009155 | 122.1954 | 0.004578 | -0.16937 | 122.4152 | 122.406 | 122.3511 | 0.21057 | 0.15564 | 0.1236 | -0.027466 | 0.21973 | 0.10986 | 0.27008 | 0.28381 | 122.4655 | 122.4792 | -0.27924 | -0.27924 | 122.168 | 122.3053 | 122.2229 | 122.3007
3304.5781 | 122.5525 | -122.287 | 0.10529 | -0.0051118 | -0.012875 | -0.079865 | -0.0074063 | -0.033861 | -0.053585 | -0.045519 | -0.0021057 | -0.008359 | 0.0089892 | -0.014834 | -0.21872 | -0.019196 | -0.023253 | -0.09613 | 0.09613 | -0.10986 | -0.086975 | 0.050354 | -0.10986 | -0.027466 | 0.022888 | 0.10071 | -0.11902 | 0.032043 | 0.14648 | 0.086975 | 0.1236 | 122.1771 | -0.009156 | -0.19226 | 122.3373 | 122.2595 | 122.1771 | 0.082397 | 0 | 122.168 | -0.004578 | -0.073243 | 122.4335 | 122.4106 | 122.374 | 0.24261 | 0.20599 | 0.16022 | 0.022888 | 0.2655 | 0.15106 | 0.20599 | 0.21973 | 122.3831 | 122.3877 | -0.21515 | -0.22431 | 122.2 | 122.319 | 122.1909 | 122.3099
3306.2969 | 122.5479 | -122.3145 | 0.12817 | 0.0025177 | -0.012661 | -0.079438 | -0.0056973 | -0.028307 | -0.050808 | -0.038042 | -0.0051575 | -0.0064364 | 0.0098438 | -0.010775 | -0.21958 | -0.017487 | -0.023039 | -0.10529 | 0.11902 | -0.12817 | -0.16022 | -0.009155 | -0.13275 | -0.059509 | -0.018311 | 0.12817 | -0.12817 | 0.004578 | 0.09613 | 0.027466 | 0.086975 | 122.1863 | -0.009155 | -0.28839 | 122.3053 | 122.2549 | 122.1817 | 0.068665 | -0.004577 | 122.1863 | 0 | -0.1236 | 122.4106 | 122.4014 | 122.3419 | 0.21515 | 0.15564 | 0.11902 | -0.032043 | 0.2243 | 0.13275 | 0.24719 | 0.25635 | 122.4335 | 122.4426 | -0.25635 | -0.25635 | 122.1542 | 122.319 | 122.2092 | 122.2961
3308.0938 | 122.6074 | -122.3145 | 0.086975 | 0.0025177 | -0.014584 | -0.081574 | -0.0089017 | -0.030443 | -0.05209 | -0.042314 | -0.0051575 | -0.0068636 | 0.0072802 | -0.012057 | -0.21937 | -0.018555 | -0.02603 | -0.073242 | 0.068665 | -0.10529 | -0.022888 | 0.18768 | 0.009155 | 0.045776 | 0.12817 | 0.091553 | -0.10071 | 0.082397 | 0.20599 | 0.14648 | 0.16022 | 122.2092 | -0.01831 | -0.10986 | 122.5021 | 122.3602 | 122.3236 | 0.15106 | 0.11444 | 122.2137 | 0.004578 | -0.004578 | 122.5204 | 122.4747 | 122.4609 | 0.26093 | 0.24719 | 0.29297 | 0.082398 | 0.3067 | 0.18311 | 0.17395 | 0.19226 | 122.3831 | 122.406 | -0.19226 | -0.18768 | 122.2916 | 122.3969 | 122.2412 | 122.4426
3309.8906 | 122.5067 | -122.3282 | 0.1236 | 0.0025177 | -0.010525 | -0.078583 | -0.0052701 | -0.029162 | -0.051449 | -0.042314 | -0.0021057 | -0.0075046 | 0.007494 | -0.011202 | -0.21958 | -0.01941 | -0.026885 | -0.064087 | 0.10071 | -0.12817 | -0.091553 | 0.050354 | -0.10986 | -0.050354 | 0.045776 | 0.13733 | -0.11444 | 0.013733 | 0.086975 | 0.013733 | 0.073242 | 122.2 | -0.022888 | -0.21515 | 122.3785 | 122.2778 | 122.2183 | 0.07782 | 0.018311 | 122.2137 | 0.013733 | -0.10986 | 122.4152 | 122.4014 | 122.3419 | 0.18768 | 0.12817 | 0.17853 | 0.036621 | 0.20142 | 0.12817 | 0.22888 | 0.25177 | 122.4289 | 122.4655 | -0.25177 | -0.23804 | 122.2366 | 122.3419 | 122.2641 | 122.374
3311.6094 | 122.5891 | -122.3053 | 0.10071 | 0.0025177 | -0.010311 | -0.080506 | -0.0065517 | -0.034716 | -0.051449 | -0.040605 | -0.0021057 | -0.0064364 | 0.0079212 | -0.014407 | -0.22001 | -0.019196 | -0.024535 | -0.10529 | 0.10986 | -0.12817 | -0.11444 | 0.032043 | -0.13733 | -0.054932 | 0.045776 | 0.11444 | -0.10986 | 0.064087 | 0.15564 | 0.082397 | 0.14191 | 122.1771 | 0.009155 | -0.21515 | 122.3373 | 122.2504 | 122.168 | 0.073242 | -0.009155 | 122.1954 | 0.013733 | -0.036621 | 122.4609 | 122.4472 | 122.3877 | 0.25177 | 0.19226 | 0.16022 | 0.013733 | 0.2655 | 0.17395 | 0.23804 | 0.2243 | 122.4152 | 122.4197 | -0.22888 | -0.21057 | 122.1909 | 122.3694 | 122.2 | 122.3511
3313.4062 | 122.5021 | -122.3877 | 0.11902 | 0.0025177 | -0.0094571 | -0.078797 | -0.0027065 | -0.027453 | -0.049526 | -0.044023 | 0.00094606 | -0.004941 | 0.010271 | -0.0039392 | -0.21937 | -0.019837 | -0.02133 | -0.1236 | 0.13275 | -0.13733 | -0.17395 | -0.045776 | -0.19226 | -0.10071 | -0.059509 | 0.13733 | -0.14191 | -0.032043 | 0.032043 | -0.041199 | 0.059509 | 122.2504 | 0.013732 | -0.29297 | 122.3419 | 122.287 | 122.1954 | 0.036621 | -0.054932 | 122.2458 | 0.01831 | -0.15106 | 122.4197 | 122.4472 | 122.3465 | 0.20142 | 0.10071 | 0.091553 | -0.036621 | 0.17395 | 0.10986 | 0.27008 | 0.27924 | 122.5204 | 122.525 | -0.25635 | -0.26093 | 122.2137 | 122.3557 | 122.2641 | 122.3282
3315.1875 | 122.5845 | -122.3373 | 0.09613 | -0.0051118 | -0.012234 | -0.08136 | -0.0044155 | -0.029802 | -0.049526 | -0.041674 | -0.0021057 | -0.007291 | 0.0079212 | -0.0084252 | -0.22236 | -0.015992 | -0.021117 | -0.11902 | 0.12817 | -0.13733 | -0.13275 | 0.027466 | -0.14648 | -0.050354 | 0.032043 | 0.10071 | -0.1236 | 0.068665 | 0.13733 | 0.059509 | 0.13733 | 122.2 | 0.032044 | -0.22888 | 122.3648 | 122.287 | 122.1909 | 0.086975 | -0.009155 | 122.2137 | 0.004578 | -0.027465 | 122.4747 | 122.4747 | 122.3969 | 0.26093 | 0.1831 | 0.16479 | 0.004578 | 0.26093 | 0.19226 | 0.2655 | 0.2243 | 122.4655 | 122.438 | -0.23346 | -0.21973 | 122.2046 | 122.406 | 122.2183 | 122.3694
3316.9375 | 122.6166 | -122.3282 | 0.10071 | -0.012741 | -0.013516 | -0.081574 | -0.0084743 | -0.035357 | -0.048672 | -0.04146 | -0.0021057 | -0.0075046 | 0.0072802 | -0.0065026 | -0.22043 | -0.017914 | -0.020049 | -0.10071 | 0.086975 | -0.11444 | -0.082397 | 0.091553 | -0.059509 | 0.022888 | 0.064087 | 0.10071 | -0.10071 | 0.068665 | 0.17853 | 0.12817 | 0.13275 | 122.2137 | -0.013733 | -0.18311 | 122.4197 | 122.3511 | 122.2687 | 0.13733 | 0.054932 | 122.2275 | 0 | -0.032043 | 122.5067 | 122.4609 | 122.4564 | 0.23346 | 0.22888 | 0.20599 | 0.032044 | 0.27924 | 0.16937 | 0.20142 | 0.20142 | 122.4152 | 122.4289 | -0.21515 | -0.20142 | 122.2458 | 122.3969 | 122.2275 | 122.3923
3318.7188 | 122.493 | -122.3877 | 0.10986 | -0.012741 | -0.0094571 | -0.078797 | -0.0029201 | -0.027666 | -0.048672 | -0.036119 | -0.0021057 | -0.002164 | 0.0089892 | -0.0084252 | -0.22022 | -0.016419 | -0.024748 | -0.1236 | 0.1236 | -0.1236 | -0.17395 | -0.050354 | -0.20142 | -0.09613 | -0.050354 | 0.13733 | -0.13275 | -0.041199 | 0.041199 | -0.036621 | 0.045776 | 122.2641 | 0.013733 | -0.28381 | 122.3373 | 122.2916 | 122.1863 | 0.027466 | -0.07782 | 122.2549 | 0.027466 | -0.15106 | 122.4289 | 122.4335 | 122.3511 | 0.17853 | 0.09613 | 0.073242 | -0.050354 | 0.17395 | 0.091552 | 0.24719 | 0.27008 | 122.5113 | 122.525 | -0.23346 | -0.24261 | 122.2137 | 122.3465 | 122.2641 | 122.3373
3320.4531 | 122.644 | -122.3145 | 0.091553 | 0.010147 | -0.011166 | -0.079651 | -0.0078335 | -0.033861 | -0.049526 | -0.039537 | -0.0051575 | -0.0064364 | 0.0066394 | -0.018038 | -0.22065 | -0.018555 | -0.024962 | -0.07782 | 0.09613 | -0.10986 | -0.050354 | 0.1236 | -0.041199 | 0.045776 | 0.10529 | 0.09613 | -0.11902 | 0.082397 | 0.21057 | 0.14648 | 0.15106 | 122.2046 | 0.004577 | -0.14191 | 122.438 | 122.3602 | 122.2733 | 0.15564 | 0.068664 | 122.1954 | 0.004577 | -0.009156 | 122.525 | 122.4655 | 122.4609 | 0.27008 | 0.2655 | 0.23346 | 0.059509 | 0.32959 | 0.20142 | 0.20599 | 0.21515 | 122.4106 | 122.4106 | -0.20142 | -0.21057 | 122.2641 | 122.3969 | 122.2366 | 122.4197
3322.2344 | 122.6166 | -122.3511 | 0.091553 | -0.0051118 | -0.013516 | -0.082001 | -0.0091153 | -0.033434 | -0.050808 | -0.04146 | -0.0051575 | -0.0064364 | 0.0083484 | -0.013125 | -0.22022 | -0.01941 | -0.022185 | -0.11444 | 0.086975 | -0.11902 | -0.091553 | 0.064087 | -0.09613 | 0 | 0.036621 | 0.10071 | -0.10986 | 0.045776 | 0.14648 | 0.10071 | 0.1236 | 122.2321 | -0.004578 | -0.18311 | 122.4152 | 122.3511 | 122.2549 | 0.11902 | 0.022889 | 122.2412 | 0.009155 | -0.045777 | 122.4976 | 122.4747 | 122.4518 | 0.23346 | 0.21057 | 0.18311 | 0.027466 | 0.25635 | 0.15564 | 0.20599 | 0.21057 | 122.438 | 122.4518 | -0.21057 | -0.20142 | 122.2595 | 122.3969 | 122.2366 | 122.3877
3323.9531 | 122.612 | -122.3328 | 0.09613 | -0.0051118 | -0.016079 | -0.080292 | -0.0071927 | -0.028093 | -0.053158 | -0.044451 | -0.0021057 | -0.0077182 | 0.0092028 | -0.013979 | -0.21958 | -0.020264 | -0.026885 | -0.050354 | 0.082397 | -0.10986 | -0.022888 | 0.13733 | -0.018311 | 0.027466 | 0.091553 | 0.10529 | -0.10529 | 0.054932 | 0.19226 | 0.11444 | 0.15106 | 122.2229 | -0.013733 | -0.11902 | 122.4701 | 122.3602 | 122.3145 | 0.13733 | 0.091552 | 122.2275 | 0.009156 | -0.041198 | 122.525 | 122.4838 | 122.4472 | 0.25635 | 0.21973 | 0.24719 | 0.086975 | 0.29755 | 0.16022 | 0.19226 | 0.21057 | 122.4152 | 122.4381 | -0.20599 | -0.20142 | 122.3099 | 122.3877 | 122.2824 | 122.4243
3325.7344 | 122.6074 | -122.3373 | 0.10071 | 0.0025177 | -0.013943 | -0.08136 | -0.0080471 | -0.031511 | -0.051663 | -0.042101 | 0.00094606 | -0.0075046 | 0.0070666 | -0.014407 | -0.2215 | -0.018555 | -0.024107 | -0.10986 | 0.086975 | -0.11902 | -0.082397 | 0.045776 | -0.091553 | -0.022888 | 0.032043 | 0.11902 | -0.1236 | 0.027466 | 0.1236 | 0.059509 | 0.11902 | 122.2183 | -0.013733 | -0.18311 | 122.3831 | 122.3145 | 122.2458 | 0.096131 | 0.027466 | 122.2137 | 0.018311 | -0.073242 | 122.4609 | 122.4564 | 122.3969 | 0.24261 | 0.1831 | 0.16479 | 0.036622 | 0.24719 | 0.15106 | 0.20599 | 0.24261 | 122.4243 | 122.4564 | -0.21973 | -0.2243 | 122.2549 | 122.3648 | 122.2275 | 122.3694
3327.5469 | 122.5388 | -122.3557 | 0.10986 | 0.010147 | -0.011593 | -0.079865 | -0.0039883 | -0.029375 | -0.051449 | -0.04146 | -0.0021057 | -0.0036594 | 0.0081348 | -0.0090662 | -0.22129 | -0.015778 | -0.024535 | -0.091553 | 0.10986 | -0.13733 | -0.10529 | 0.022888 | -0.13733 | -0.059509 | 0.013733 | 0.13275 | -0.1236 | 0.018311 | 0.068665 | -0.004578 | 0.064087 | 122.2183 | 0 | -0.21515 | 122.3785 | 122.2961 | 122.2183 | 0.07782 | 0 | 122.2321 | 0.022888 | -0.091552 | 122.4243 | 122.4197 | 122.3511 | 0.18768 | 0.11902 | 0.16022 | 0.032043 | 0.19226 | 0.14191 | 0.24719 | 0.25635 | 122.4655 | 122.4884 | -0.24719 | -0.23346 | 122.2504 | 122.374 | 122.2641 | 122.3694
3329.2656 | 122.6303 | -122.3465 | 0.091553 | 0.0025177 | -0.013302 | -0.080079 | -0.0050565 | -0.029375 | -0.051235 | -0.042101 | -0.0021057 | -0.0047274 | 0.0079212 | -0.016543 | -0.22129 | -0.017701 | -0.02133 | -0.086975 | 0.09613 | -0.10986 | -0.07782 | 0.059509 | -0.10071 | 0.004578 | 0.082397 | 0.10071 | -0.10071 | 0.09613 | 0.1831 | 0.11444 | 0.16479 | 122.2366 | 0.004577 | -0.16937 | 122.406 | 122.3511 | 122.2458 | 0.11444 | 0.009155 | 122.2458 | 0.009155 | 0.004577 | 122.5296 | 122.5113 | 122.4609 | 0.2655 | 0.21515 | 0.16937 | 0.032043 | 0.28381 | 0.19684 | 0.20599 | 0.20142 | 122.4426 | 122.4472 | -0.20142 | -0.19226 | 122.2687 | 122.4426 | 122.2595 | 122.4289
3331.0469 | 122.644 | -122.3373 | 0.091553 | -0.028 | -0.010952 | -0.079224 | -0.0052701 | -0.028521 | -0.051022 | -0.040178 | -0.0021057 | -0.0064364 | 0.010912 | -0.012698 | -0.22129 | -0.017701 | -0.021971 | -0.082397 | 0.091553 | -0.1236 | -0.064087 | 0.091553 | -0.07782 | 0 | 0.086975 | 0.10529 | -0.10071 | 0.09613 | 0.17395 | 0.10529 | 0.16022 | 122.2137 | 0 | -0.15564 | 122.4289 | 122.3373 | 122.2595 | 0.1236 | 0.045776 | 122.2366 | 0.013733 | 0.004577 | 122.5113 | 122.4976 | 122.4426 | 0.26093 | 0.20599 | 0.21515 | 0.059509 | 0.27466 | 0.19684 | 0.21515 | 0.20599 | 122.4289 | 122.4426 | -0.21515 | -0.19226 | 122.2733 | 122.4335 | 122.2549 | 122.4243
3332.7812 | 122.6669 | -122.3465 | 0.073242 | 0.010147 | -0.01437 | -0.080506 | -0.0089017 | -0.033434 | -0.052731 | -0.040392 | 0.0039979 | -0.0060092 | 0.0096302 | -0.011843 | -0.21915 | -0.01941 | -0.022826 | -0.082397 | 0.07782 | -0.11444 | -0.050354 | 0.12817 | -0.018311 | 0.027466 | 0.14191 | 0.09613 | -0.11444 | 0.10071 | 0.21973 | 0.15564 | 0.16479 | 122.2321 | 0.004578 | -0.1236 | 122.4747 | 122.374 | 122.3282 | 0.14191 | 0.09613 | 122.2321 | 0.022888 | 0.027466 | 122.5662 | 122.5113 | 122.5021 | 0.27924 | 0.27008 | 0.24262 | 0.064087 | 0.33417 | 0.21515 | 0.19226 | 0.21057 | 122.4243 | 122.4426 | -0.18768 | -0.18768 | 122.2961 | 122.4472 | 122.2641 | 122.4884
3334.5938 | 122.5204 | -122.4014 | 0.13275 | 0.0025177 | -0.010525 | -0.077942 | -0.0035611 | -0.028948 | -0.050381 | -0.042101 | 0.00094606 | -0.0043002 | 0.0098438 | -0.011843 | -0.21872 | -0.018982 | -0.024962 | -0.11902 | 0.13733 | -0.1236 | -0.16479 | -0.050354 | -0.20599 | -0.09613 | -0.050354 | 0.14191 | -0.14648 | -0.032043 | 0.022888 | -0.036621 | 0.050354 | 122.2778 | 0.004578 | -0.29755 | 122.3511 | 122.3053 | 122.1954 | 0.027466 | -0.082398 | 122.2549 | 0.009156 | -0.16479 | 122.4243 | 122.4518 | 122.3648 | 0.19684 | 0.10986 | 0.073242 | -0.041199 | 0.16937 | 0.11444 | 0.26093 | 0.28839 | 122.5388 | 122.5433 | -0.25635 | -0.27924 | 122.2366 | 122.3694 | 122.2824 | 122.3511
3336.3906 | 122.644 | -122.3877 | 0.082397 | -0.012741 | -0.014157 | -0.080506 | -0.0056973 | -0.03023 | -0.051235 | -0.039751 | -0.0021057 | -0.0077182 | 0.0077076 | -0.015688 | -0.21958 | -0.018982 | -0.022826 | -0.10071 | 0.091553 | -0.12817 | -0.082397 | 0.059509 | -0.086975 | 0.009155 | 0.050354 | 0.11902 | -0.10529 | 0.054932 | 0.16937 | 0.10986 | 0.13275 | 122.2595 | 0.009156 | -0.16479 | 122.4472 | 122.3969 | 122.3007 | 0.13733 | 0.041199 | 122.2824 | 0.036622 | -0.027465 | 122.5571 | 122.5204 | 122.4976 | 0.23804 | 0.21515 | 0.18768 | 0.045777 | 0.27466 | 0.16022 | 0.21973 | 0.22431 | 122.4792 | 122.5067 | -0.21057 | -0.18768 | 122.3053 | 122.4426 | 122.287 | 122.438
3338.125 | 122.6257 | -122.3648 | 0.07782 | -0.0051118 | -0.010739 | -0.079224 | -0.0067653 | -0.031939 | -0.051235 | -0.044451 | -0.0051575 | -0.0075046 | 0.0062122 | -0.014193 | -0.22065 | -0.017701 | -0.025603 | -0.068665 | 0.082397 | -0.091553 | -0.041199 | 0.11902 | -0.07782 | 0.013733 | 0.12817 | 0.10986 | -0.09613 | 0.073242 | 0.16479 | 0.09613 | 0.12817 | 122.2733 | 0.004577 | -0.11902 | 122.4838 | 122.3785 | 122.287 | 0.10529 | 0.013733 | 122.2687 | 0.032043 | -0.004578 | 122.5296 | 122.493 | 122.4609 | 0.2243 | 0.19226 | 0.21057 | 0.050354 | 0.26092 | 0.16937 | 0.17395 | 0.20599 | 122.4472 | 122.4747 | -0.16937 | -0.17395 | 122.3236 | 122.438 | 122.2961 | 122.493
3339.9219 | 122.6349 | -122.3373 | 0.11444 | 0.0025177 | -0.0098843 | -0.078797 | -0.0031337 | -0.030016 | -0.051663 | -0.042528 | 0.00094606 | -0.0053684 | 0.0089892 | -0.0065026 | -0.22129 | -0.017701 | -0.023467 | -0.1236 | 0.10986 | -0.13275 | -0.10986 | 0.022888 | -0.15564 | -0.041199 | 0.045776 | 0.11902 | -0.11444 | 0.07782 | 0.14648 | 0.082397 | 0.14648 | 122.2046 | -0.004578 | -0.2243 | 122.3602 | 122.2961 | 122.1817 | 0.091552 | -0.022889 | 122.2229 | 0.004578 | -0.036621 | 122.4838 | 122.4838 | 122.4197 | 0.26093 | 0.19684 | 0.15564 | 0.022888 | 0.26093 | 0.19226 | 0.24261 | 0.23346 | 122.4472 | 122.4564 | -0.24719 | -0.22888 | 122.2275 | 122.4152 | 122.2137 | 122.3831
3341.6562 | 122.6578 | -122.3969 | 0.086975 | -0.0051118 | -0.014584 | -0.079651 | -0.0069791 | -0.032366 | -0.051663 | -0.041033 | 0.00094606 | -0.0079318 | 0.005785 | -0.019961 | -0.21872 | -0.021332 | -0.023039 | -0.11902 | 0.091553 | -0.11444 | -0.07782 | 0.086975 | -0.07782 | 0.004578 | 0.041199 | 0.10529 | -0.11444 | 0.059509 | 0.17853 | 0.11444 | 0.13733 | 122.2824 | 0.004578 | -0.16479 | 122.4838 | 122.4014 | 122.319 | 0.11902 | 0.036621 | 122.2824 | 0.018311 | -0.027466 | 122.5754 | 122.5342 | 122.5113 | 0.25177 | 0.22888 | 0.20142 | 0.036621 | 0.29297 | 0.17395 | 0.20599 | 0.21973 | 122.4884 | 122.5021 | -0.20142 | -0.20142 | 122.319 | 122.4564 | 122.2778 | 122.4381
3343.4531 | 122.6578 | -122.3969 | 0.086975 | -0.0051118 | -0.014798 | -0.078797 | -0.0080471 | -0.034716 | -0.051449 | -0.043169 | 0.00094606 | -0.0075046 | 0.0055712 | -0.013552 | -0.21937 | -0.018555 | -0.024321 | -0.082397 | 0.07782 | -0.11902 | -0.045776 | 0.1236 | -0.032043 | 0.036621 | 0.086975 | 0.09613 | -0.09613 | 0.073242 | 0.20599 | 0.15106 | 0.16479 | 122.2778 | -0.009155 | -0.13275 | 122.5204 | 122.4335 | 122.3648 | 0.15564 | 0.086976 | 122.3007 | 0.009155 | -0.013733 | 122.6028 | 122.5616 | 122.5479 | 0.26092 | 0.24719 | 0.24261 | 0.073243 | 0.30212 | 0.16937 | 0.19684 | 0.19226 | 122.4747 | 122.493 | -0.20599 | -0.1831 | 122.3511 | 122.4701 | 122.3145 | 122.4838
3345.1719 | 122.6486 | -122.3923 | 0.082397 | 0.0025177 | -0.013089 | -0.080506 | -0.0074063 | -0.031298 | -0.051235 | -0.041246 | -0.0082091 | -0.0060092 | 0.0079212 | -0.018466 | -0.21958 | -0.018128 | -0.02368 | -0.11444 | 0.091553 | -0.11444 | -0.082397 | 0.054932 | -0.10071 | -0.018311 | 0.032043 | 0.1236 | -0.11444 | 0.041199 | 0.16022 | 0.091553 | 0.11902 | 122.2778 | 0.009156 | -0.16479 | 122.4472 | 122.374 | 122.2916 | 0.09613 | 0.013733 | 122.2778 | 0.041199 | -0.041198 | 122.5525 | 122.5113 | 122.4838 | 0.23346 | 0.20599 | 0.16937 | 0.032044 | 0.27466 | 0.15564 | 0.20599 | 0.23804 | 122.4838 | 122.5159 | -0.19684 | -0.19684 | 122.3099 | 122.4335 | 122.2778 | 122.4243
3346.9688 | 122.5296 | -122.4289 | 0.12817 | -0.012741 | -0.01437 | -0.080079 | -0.0065517 | -0.03322 | -0.052304 | -0.041246 | -0.0021057 | -0.007291 | 0.008562 | -0.0086388 | -0.22065 | -0.018342 | -0.020689 | -0.1236 | 0.10529 | -0.13275 | -0.14191 | 0.013733 | -0.14191 | -0.059509 | -0.027466 | 0.13733 | -0.13275 | -0.045776 | 0.050354 | 0.004578 | 0.032043 | 122.2961 | -0.022888 | -0.27008 | 122.4426 | 122.3694 | 122.287 | 0.073242 | -0.009156 | 122.2961 | 0.009155 | -0.17395 | 122.4792 | 122.4609 | 122.4335 | 0.16479 | 0.13733 | 0.14648 | -0.009156 | 0.18311 | 0.086975 | 0.23804 | 0.27008 | 122.5342 | 122.5662 | -0.26093 | -0.26093 | 122.287 | 122.3831 | 122.3053 | 122.4014
3348.7656 | 122.6852 | -122.4014 | 0.082397 | -0.0051118 | -0.015866 | -0.080933 | -0.0071927 | -0.029162 | -0.050167 | -0.041033 | -0.0051575 | -0.0070772 | 0.0064258 | -0.018893 | -0.22065 | -0.017487 | -0.026457 | -0.082397 | 0.086975 | -0.10986 | -0.064087 | 0.082397 | -0.054932 | 0.022888 | 0.09613 | 0.11902 | -0.11444 | 0.082397 | 0.19684 | 0.14648 | 0.16022 | 122.2916 | 0.004578 | -0.14648 | 122.4838 | 122.4243 | 122.3465 | 0.13275 | 0.054931 | 122.287 | 0.036622 | 0 | 122.5983 | 122.5616 | 122.5479 | 0.27466 | 0.26093 | 0.19226 | 0.045776 | 0.31128 | 0.19684 | 0.19684 | 0.23346 | 122.4884 | 122.5204 | -0.19226 | -0.19684 | 122.3373 | 122.4838 | 122.319 | 122.4976
3350.5 | 122.5204 | -121.9482 | 0.36163 | 0.0025177 | -0.015866 | -0.079865 | -0.0071927 | -0.033434 | -0.052304 | -0.042955 | 0.00094606 | 0.035006 | 0.0092028 | 0.008451 | -0.21915 | -0.018342 | -0.024107 | -0.068665 | 0.091553 | -0.082397 | -0.036621 | 0.10986 | -0.045776 | 0.036621 | 0.34332 | 0.3891 | 0.13733 | 0.35706 | 0.42572 | 0.39368 | 0.41199 | 121.8658 | -0.27008 | -0.39825 | 122.0581 | 121.9849 | 121.9025 | 0.11902 | 0.036621 | 122.0856 | 0.027466 | -0.004577 | 122.374 | 122.3602 | 122.3419 | 0.27466 | 0.25635 | 0.19226 | 0.045776 | 0.28839 | 0.21973 | 0.17395 | 0.25177 | 122.0398 | 122.3373 | -0.44403 | -0.2243 | 121.9116 | 122.3053 | 121.8796 | 122.2916
3352.2812 | 119.7144 | -91.1819 | 28.3218 | -0.012741 | -0.015866 | -0.079865 | 0.00049768 | -0.031725 | -0.051022 | -0.044664 | -0.0051575 | 0.0021084 | 0.0066394 | -0.0099206 | -0.22086 | -0.019837 | -0.022185 | 0.1236 | 0.21057 | 0.054932 | 0.10986 | 0.28381 | 0.10986 | 0.16479 | 0.07782 | 0.082397 | -0.13733 | 0.032043 | 0.16022 | 0.091553 | 0.10529 | 91.2369 | -28.1113 | -28.212 | 91.4658 | 91.3467 | 91.2918 | 0.10986 | 0.054931 | 91.0446 | -28.2394 | -28.2898 | 91.3422 | 91.2872 | 91.2735 | 0.24262 | 0.22888 | 0.22888 | 0.054931 | 0.29755 | 0.16937 | 0.15564 | 0.21973 | 91.3925 | 91.2643 | -28.2669 | -28.4592 | 91.2918 | 91.214 | 91.3055 | 91.2598
3354.0781 | 122.1451 | -121.6003 | 0.24261 | -0.012741 | -0.012448 | -0.076661 | -0.0059109 | -0.028734 | -0.048672 | -0.041887 | -0.0021057 | 0.0021084 | 0.0087756 | -0.012911 | -0.22001 | -0.014924 | -0.024321 | -0.036621 | 0.07782 | -0.07782 | -0.009155 | 0.13275 | -0.068665 | 0.013733 | 0.1236 | 0.10986 | -0.091553 | 0.10071 | 0.17853 | 0.10986 | 0.15564 | 121.5225 | -0.16479 | -0.25177 | 121.7331 | 121.6141 | 121.5317 | 0.091553 | 0.009155 | 121.5088 | -0.13275 | -0.14191 | 121.7789 | 121.756 | 121.7102 | 0.24719 | 0.20142 | 0.21057 | 0.068665 | 0.27008 | 0.19226 | 0.15564 | 0.20142 | 121.6782 | 121.7102 | -0.32044 | -0.33417 | 121.5912 | 121.701 | 121.5637 | 121.7239
3355.7969 | 122.0673 | -121.3898 | 0.50354 | -0.012741 | -0.01202 | -0.076233 | -0.0037747 | -0.029375 | -0.050167 | -0.041033 | 0.00094606 | 0.0044584 | 0.008562 | -0.009707 | -0.21979 | -0.016419 | -0.025389 | -0.073242 | 0.1236 | -0.13733 | -0.07782 | 0.054932 | -0.10529 | -0.054932 | 0.050354 | 0.13733 | -0.11902 | 0.032043 | 0.10986 | 0.041199 | 0.086975 | 121.2524 | -0.37994 | -0.58136 | 121.4447 | 121.3348 | 121.2845 | 0.082397 | 0.032043 | 121.2708 | -0.36621 | -0.4715 | 121.4996 | 121.4767 | 121.431 | 0.20599 | 0.16022 | 0.19226 | 0.059509 | 0.22888 | 0.15106 | 0.26093 | 0.25635 | 121.5134 | 121.5271 | -0.64087 | -0.62256 | 121.312 | 121.4218 | 121.3165 | 121.4401
3357.5938 | 122.2137 | -122.0123 | 0.1236 | -0.012741 | -0.011807 | -0.077302 | -0.0065517 | -0.026598 | -0.04974 | -0.04146 | 0.0039979 | 0.0031766 | 0.0079212 | -0.0032984 | -0.21894 | -0.018128 | -0.024321 | -0.12817 | 0.12817 | -0.13733 | -0.14191 | -0.018311 | -0.17853 | -0.086975 | -0.004578 | 0.13275 | -0.1236 | 0.027466 | 0.064087 | 0.013733 | 0.091553 | 121.875 | 0.004578 | -0.2655 | 121.994 | 121.9254 | 121.8338 | 0.050354 | -0.041199 | 121.8887 | 0.009155 | -0.09613 | 122.0764 | 122.1039 | 122.0261 | 0.21515 | 0.13733 | 0.11902 | -0.004578 | 0.18768 | 0.15106 | 0.2655 | 0.25635 | 122.1405 | 122.1451 | -0.26093 | -0.24719 | 121.8704 | 122.0398 | 121.8842 | 122.0078
3359.3906 | 122.1176 | -121.8933 | 0.21057 | 0.0025177 | -0.012661 | -0.081147 | -0.0061245 | -0.028734 | -0.051876 | -0.044878 | -0.0021057 | 0.0038174 | 0.0077076 | -0.01163 | -0.22086 | -0.01706 | -0.027739 | -0.13275 | 0.11444 | -0.14648 | -0.15564 | -0.018311 | -0.16479 | -0.073242 | -0.045776 | 0.13733 | -0.13275 | -0.036621 | 0.073242 | -0.004578 | 0.054932 | 121.7468 | -0.09613 | -0.36621 | 121.875 | 121.8201 | 121.7285 | 0.073242 | -0.018311 | 121.7606 | -0.073242 | -0.24719 | 121.9666 | 121.9482 | 121.8887 | 0.18768 | 0.12817 | 0.12817 | -0.009156 | 0.20599 | 0.09613 | 0.26093 | 0.27008 | 122.0078 | 122.0306 | -0.35706 | -0.34332 | 121.7377 | 121.8567 | 121.7606 | 121.8475
3361.1719 | 122.3145 | -121.9803 | 0.09613 | 0.0025177 | -0.010311 | -0.078797 | -0.0046291 | -0.029162 | -0.049526 | -0.041674 | -0.0021057 | 0.0040312 | 0.0077076 | -0.018466 | -0.21979 | -0.016419 | -0.022185 | -0.10986 | 0.1236 | -0.11902 | -0.064087 | 0.082397 | -0.09613 | -0.022888 | 0.07782 | 0.10529 | -0.10529 | 0.091553 | 0.17853 | 0.091553 | 0.15106 | 121.8613 | 0.027466 | -0.16022 | 122.0627 | 121.9574 | 121.8842 | 0.096131 | 0.022889 | 121.875 | 0.009156 | -0.004577 | 122.1588 | 122.1313 | 122.0718 | 0.25635 | 0.19684 | 0.20142 | 0.054932 | 0.28381 | 0.19684 | 0.24261 | 0.21057 | 122.1039 | 122.0856 | -0.21515 | -0.20142 | 121.9162 | 122.0718 | 121.8704 | 122.0581
3362.9062 | 122.2595 | -122.049 | 0.10986 | 0.0025177 | -0.010525 | -0.079865 | -0.0039883 | -0.029162 | -0.050808 | -0.042528 | 0.00094606 | 0.0038174 | 0.0083484 | -0.0047936 | -0.22107 | -0.016633 | -0.024321 | -0.1236 | 0.1236 | -0.13733 | -0.1236 | 0.013733 | -0.11902 | -0.036621 | 0.004578 | 0.14648 | -0.13733 | 0.018311 | 0.11444 | 0.027466 | 0.086975 | 121.9116 | 0.013733 | -0.23346 | 122.0627 | 122.0123 | 121.9299 | 0.10071 | 0.01831 | 121.9116 | 0.036621 | -0.091552 | 122.1634 | 122.1359 | 122.0764 | 0.2243 | 0.16479 | 0.15106 | 0.013733 | 0.25177 | 0.15564 | 0.26093 | 0.28381 | 122.1725 | 122.1954 | -0.24719 | -0.24719 | 121.9254 | 122.0673 | 121.9254 | 122.0535
3364.6875 | 122.3419 | -122.0261 | 0.07782 | -0.0051118 | -0.01138 | -0.079438 | -0.0061245 | -0.026812 | -0.048031 | -0.041033 | -0.0021057 | 0.004672 | 0.006853 | -0.01462 | -0.22001 | -0.016846 | -0.021971 | -0.041199 | 0.082397 | -0.091553 | -0.032043 | 0.1236 | -0.073242 | 0.004578 | 0.11444 | 0.091553 | -0.10529 | 0.10529 | 0.17853 | 0.10986 | 0.16937 | 121.9345 | 0.004577 | -0.10986 | 122.1497 | 122.0306 | 121.9528 | 0.096131 | 0.018311 | 121.9208 | 0.013733 | 0.027466 | 122.2046 | 122.1954 | 122.1359 | 0.27466 | 0.21515 | 0.21515 | 0.05951 | 0.28381 | 0.21057 | 0.17395 | 0.19684 | 122.1085 | 122.1176 | -0.16937 | -0.18311 | 121.994 | 122.1313 | 121.9849 | 122.1405
3366.4688 | 122.2183 | -122.0444 | 0.15564 | -0.0051118 | -0.011593 | -0.077302 | -0.0050565 | -0.031298 | -0.049526 | -0.041674 | 0.00094606 | 0.004672 | 0.0077076 | -0.010348 | -0.21702 | -0.015565 | -0.024107 | -0.13275 | 0.11444 | -0.12817 | -0.17395 | -0.032043 | -0.19226 | -0.10071 | -0.045776 | 0.14191 | -0.12817 | -0.018311 | 0.041199 | -0.018311 | 0.064087 | 121.9162 | -0.041199 | -0.32959 | 122.0123 | 121.9437 | 121.8521 | 0.027466 | -0.064087 | 121.9162 | -0.013733 | -0.17395 | 122.0856 | 122.1085 | 122.0261 | 0.19226 | 0.10986 | 0.096131 | -0.045776 | 0.16937 | 0.10986 | 0.24262 | 0.27008 | 122.1588 | 122.1863 | -0.28381 | -0.28381 | 121.8704 | 122.0261 | 121.9116 | 121.9986
3368.25 | 122.2549 | -122.1176 | 0.13733 | -0.0051118 | -0.013943 | -0.082001 | -0.0050565 | -0.02553 | -0.051663 | -0.041033 | -0.0021057 | 0.0036038 | 0.0072802 | -0.0077844 | -0.22001 | -0.018342 | -0.023894 | -0.14648 | 0.11444 | -0.13733 | -0.15106 | -0.022888 | -0.15564 | -0.091553 | -0.064087 | 0.1236 | -0.15564 | -0.041199 | 0.064087 | 0.013733 | 0.054932 | 121.9803 | -0.022888 | -0.28839 | 122.0947 | 122.0261 | 121.962 | 0.045776 | -0.018311 | 121.962 | -0.013733 | -0.17853 | 122.1817 | 122.1725 | 122.1313 | 0.21057 | 0.16937 | 0.11444 | -0.013733 | 0.21973 | 0.11444 | 0.25177 | 0.27924 | 122.2321 | 122.2412 | -0.27466 | -0.29297 | 121.9666 | 122.0764 | 121.9711 | 122.0535
3370.0469 | 122.1817 | -122.0901 | 0.10071 | 0.0025177 | -0.011166 | -0.078583 | -0.0065517 | -0.030657 | -0.050595 | -0.041674 | 0.0039979 | 0.0036038 | 0.0077076 | -0.007998 | -0.21937 | -0.01941 | -0.023039 | -0.12817 | 0.10986 | -0.15106 | -0.18768 | -0.027466 | -0.19684 | -0.10529 | -0.050354 | 0.13733 | -0.12817 | -0.022888 | 0.045776 | -0.027466 | 0.041199 | 121.9391 | 0.009155 | -0.28839 | 122.0627 | 121.9849 | 121.8933 | 0.045776 | -0.045776 | 121.962 | 0.036621 | -0.1236 | 122.1359 | 122.1313 | 122.0627 | 0.16937 | 0.10071 | 0.1236 | -0.036621 | 0.17395 | 0.10529 | 0.26093 | 0.2655 | 122.2 | 122.2275 | -0.25177 | -0.22888 | 121.9025 | 122.0673 | 121.962 | 122.0398
3371.7812 | 122.2687 | -122.1268 | 0.13733 | -0.012741 | -0.0096707 | -0.077515 | -0.0033475 | -0.030016 | -0.053158 | -0.042955 | -0.0021057 | 0.0031766 | 0.0092028 | -0.015048 | -0.21744 | -0.016846 | -0.019621 | -0.091553 | 0.11902 | -0.10986 | -0.10986 | 0.018311 | -0.14648 | -0.073242 | 0.004578 | 0.13733 | -0.1236 | -0.032043 | 0.045776 | -0.009155 | 0.054932 | 122.0169 | -0.01831 | -0.24719 | 122.1451 | 122.0535 | 121.9803 | 0.036621 | -0.036621 | 122.0032 | 0 | -0.16937 | 122.1725 | 122.1817 | 122.1176 | 0.17853 | 0.11444 | 0.12817 | 0 | 0.16937 | 0.091553 | 0.22888 | 0.26093 | 122.2458 | 122.2641 | -0.24719 | -0.26093 | 122.0169 | 122.0947 | 122.0352 | 122.1313
3373.5781 | 122.3602 | -122.1222 | 0.12817 | 0.0025177 | -0.016293 | -0.080933 | -0.0084743 | -0.029375 | -0.05209 | -0.043596 | 0.00094606 | 0.00018579 | 0.0070666 | -0.015688 | -0.22001 | -0.01941 | -0.024535 | -0.068665 | 0.086975 | -0.10986 | -0.032043 | 0.12817 | -0.018311 | 0.032043 | 0.082397 | 0.10529 | -0.1236 | 0.041199 | 0.16022 | 0.10529 | 0.11902 | 122.0123 | -0.041199 | -0.16022 | 122.2504 | 122.1542 | 122.1039 | 0.14191 | 0.091552 | 121.9986 | -0.022888 | -0.086975 | 122.2824 | 122.2412 | 122.2275 | 0.24261 | 0.22888 | 0.23804 | 0.07782 | 0.28381 | 0.16479 | 0.19684 | 0.22888 | 122.2092 | 122.2275 | -0.23804 | -0.25177 | 122.0901 | 122.1634 | 122.0535 | 122.2046
3375.3594 | 122.4152 | -122.1039 | 0.10986 | 0.010147 | -0.014798 | -0.081574 | -0.0076199 | -0.035143 | -0.051876 | -0.042955 | -0.0021057 | 0.0014676 | 0.0066394 | -0.0065026 | -0.21979 | -0.017487 | -0.019835 | -0.050354 | 0.091553 | -0.10986 | -0.036621 | 0.16479 | -0.018311 | 0.050354 | 0.11444 | 0.10071 | -0.10529 | 0.086975 | 0.20599 | 0.14648 | 0.15106 | 121.994 | -0.01831 | -0.14648 | 122.2687 | 122.1542 | 122.0856 | 0.16022 | 0.091552 | 121.9986 | -0.009155 | -0.022888 | 122.3099 | 122.2549 | 122.2504 | 0.25635 | 0.25177 | 0.27466 | 0.073242 | 0.31128 | 0.19226 | 0.20142 | 0.20599 | 122.1954 | 122.2046 | -0.21973 | -0.21515 | 122.0673 | 122.1909 | 122.0535 | 122.2183
3377.0781 | 122.438 | -122.1313 | 0.09613 | 0.0025177 | -0.012661 | -0.080292 | -0.0061245 | -0.027025 | -0.054013 | -0.042955 | -0.0051575 | 0.0010404 | 0.0096302 | -0.017397 | -0.21851 | -0.017487 | -0.024535 | -0.059509 | 0.064087 | -0.09613 | -0.022888 | 0.16022 | -0.013733 | 0.059509 | 0.16479 | 0.086975 | -0.11444 | 0.073242 | 0.20142 | 0.14648 | 0.15564 | 122.0352 | -0.032043 | -0.11902 | 122.2916 | 122.1909 | 122.1176 | 0.15564 | 0.082397 | 122.0169 | -0.009155 | -0.022888 | 122.3328 | 122.287 | 122.2778 | 0.27008 | 0.26093 | 0.25635 | 0.073242 | 0.31586 | 0.18768 | 0.16022 | 0.20142 | 122.1954 | 122.2183 | -0.19226 | -0.21057 | 122.1085 | 122.2046 | 122.0718 | 122.2961
3378.875 | 122.2778 | -122.1588 | 0.14191 | -0.012741 | -0.010739 | -0.080719 | -0.0033475 | -0.026598 | -0.050167 | -0.04146 | -0.0051575 | 0.0048856 | 0.0059986 | -0.0092798 | -0.2215 | -0.016419 | -0.024748 | -0.10529 | 0.11902 | -0.13275 | -0.14648 | -0.054932 | -0.20599 | -0.1236 | -0.068665 | 0.13733 | -0.14191 | -0.036621 | 0.032043 | -0.050354 | 0.041199 | 122.0261 | -0.022888 | -0.28839 | 122.1039 | 122.0352 | 121.9528 | 0.009155 | -0.073243 | 122.0169 | -0.004578 | -0.17853 | 122.1909 | 122.2 | 122.1085 | 0.18311 | 0.091553 | 0.077819 | -0.013733 | 0.17395 | 0.10529 | 0.25177 | 0.27924 | 122.2778 | 122.2961 | -0.27466 | -0.28381 | 122.0123 | 122.1222 | 122.0535 | 122.0901
3380.6562 | 122.4106 | -122.1268 | 0.086975 | -0.012741 | -0.010311 | -0.080292 | -0.0050565 | -0.027025 | -0.049526 | -0.042101 | -0.0021057 | 0.0018948 | 0.0070666 | -0.025729 | -0.22022 | -0.017914 | -0.020903 | -0.07782 | 0.07782 | -0.10071 | -0.045776 | 0.12817 | -0.073242 | 0.013733 | 0.09613 | 0.10986 | -0.09613 | 0.064087 | 0.13275 | 0.07782 | 0.12817 | 122.0261 | -0.009155 | -0.13275 | 122.2549 | 122.1405 | 122.0535 | 0.11444 | 0.027466 | 122.0306 | 0.022888 | -0.022888 | 122.2595 | 122.2549 | 122.2046 | 0.2243 | 0.17395 | 0.22888 | 0.054932 | 0.22888 | 0.16022 | 0.17853 | 0.20599 | 122.2046 | 122.2366 | -0.18768 | -0.1831 | 122.081 | 122.1909 | 122.0489 | 122.2229
3382.4531 | 122.3785 | -121.6187 | 0.54016 | -0.0051118 | -0.010525 | -0.077942 | -0.0048427 | -0.032366 | -0.049313 | -0.040819 | -0.0021057 | 0.0025358 | 0.0079212 | -0.012911 | -0.22236 | -0.018128 | -0.025603 | -0.045776 | 0.07782 | -0.07782 | -0.022888 | 0.13733 | -0.059509 | 0.018311 | 0.1236 | 0.11444 | -0.091553 | 0.086975 | 0.17395 | 0.09613 | 0.13275 | 121.5408 | -0.46234 | -0.56305 | 121.756 | 121.637 | 121.5591 | 0.096131 | 0.018311 | 121.5271 | -0.42572 | -0.45319 | 121.7926 | 121.7514 | 121.7148 | 0.2243 | 0.18768 | 0.21515 | 0.054932 | 0.2655 | 0.17853 | 0.15564 | 0.20599 | 121.6965 | 121.7331 | -0.61798 | -0.63171 | 121.5958 | 121.7056 | 121.5729 | 121.7422
3384.1875 | 122.4335 | -122.1497 | 0.09613 | -0.012741 | -0.014157 | -0.079224 | -0.0067653 | -0.033007 | -0.051235 | -0.041887 | -0.0021057 | 0.00039959 | 0.0070666 | -0.01932 | -0.21851 | -0.018128 | -0.022398 | -0.10986 | 0.082397 | -0.10529 | -0.091553 | 0.059509 | -0.07782 | -0.004578 | 0.041199 | 0.10529 | -0.10986 | 0.041199 | 0.16022 | 0.09613 | 0.13275 | 122.0444 | -0.013733 | -0.18768 | 122.2092 | 122.1451 | 122.0718 | 0.10071 | 0.027466 | 122.0398 | 0.009156 | -0.054931 | 122.3099 | 122.2824 | 122.2458 | 0.24261 | 0.20599 | 0.16479 | 0.013733 | 0.27008 | 0.15106 | 0.18768 | 0.21515 | 122.2321 | 122.2549 | -0.20142 | -0.20599 | 122.0581 | 122.1909 | 122.0398 | 122.1909
3385.9688 | 122.3419 | -122.2321 | 0.13733 | -0.012741 | -0.012234 | -0.080292 | -0.0063381 | -0.029802 | -0.051235 | -0.039965 | -0.0021057 | 0.0033902 | 0.0079212 | -0.014407 | -0.22022 | -0.018342 | -0.02368 | -0.13733 | 0.12817 | -0.14191 | -0.14648 | -0.013733 | -0.16022 | -0.054932 | -0.050354 | 0.13733 | -0.15106 | -0.068665 | 0.050354 | -0.013733 | 0.041199 | 122.0901 | -0.009155 | -0.28381 | 122.2183 | 122.1771 | 122.0718 | 0.086975 | -0.01831 | 122.081 | 0 | -0.20599 | 122.2824 | 122.2733 | 122.2183 | 0.19226 | 0.13733 | 0.12817 | -0.004577 | 0.20142 | 0.082397 | 0.27008 | 0.28839 | 122.3602 | 122.3694 | -0.27924 | -0.28839 | 122.0856 | 122.1634 | 122.0947 | 122.1817
3387.75 | 122.4747 | -122.1588 | 0.10529 | -0.0051118 | -0.010739 | -0.079865 | -0.0044155 | -0.028307 | -0.048458 | -0.041887 | -0.0021057 | 0.0040312 | 0.0083484 | -0.010989 | -0.22129 | -0.018342 | -0.023253 | -0.073242 | 0.068665 | -0.10986 | -0.050354 | 0.07782 | -0.082397 | 0.004578 | 0.10071 | 0.10986 | -0.11444 | 0.10071 | 0.17395 | 0.10986 | 0.15564 | 122.0489 | -0.036621 | -0.15564 | 122.2366 | 122.1634 | 122.0764 | 0.11444 | 0.027466 | 122.0444 | 0.004577 | -0.004578 | 122.3328 | 122.3145 | 122.2687 | 0.27008 | 0.2243 | 0.18768 | 0.059509 | 0.28839 | 0.21515 | 0.17853 | 0.2243 | 122.2275 | 122.2687 | -0.21515 | -0.21973 | 122.1085 | 122.2595 | 122.0856 | 122.2595
3389.4844 | 122.4197 | -122.1313 | 0.16937 | -0.0051118 | -0.011807 | -0.080933 | -0.0084743 | -0.029589 | -0.051876 | -0.038896 | -0.0021057 | 0.0042448 | 0.005785 | -0.010989 | -0.22001 | -0.017701 | -0.020689 | -0.059509 | 0.073242 | -0.10986 | -0.032043 | 0.10986 | -0.036621 | 0.018311 | 0.050354 | 0.1236 | -0.1236 | 0.018311 | 0.13275 | 0.073242 | 0.091553 | 122.0215 | -0.096131 | -0.20142 | 122.2412 | 122.1497 | 122.0947 | 0.12817 | 0.073242 | 122.0078 | -0.045777 | -0.15106 | 122.2641 | 122.2229 | 122.2046 | 0.21515 | 0.19684 | 0.21973 | 0.07782 | 0.25635 | 0.14191 | 0.18311 | 0.24719 | 122.2046 | 122.2549 | -0.27924 | -0.29297 | 122.0993 | 122.1497 | 122.0718 | 122.1817
3391.2656 | 122.3785 | -122.2046 | 0.12817 | -0.0051118 | -0.012234 | -0.079011 | -0.0050565 | -0.030016 | -0.050595 | -0.044664 | -0.0021057 | 0.00574 | 0.010485 | -0.011416 | -0.21937 | -0.016633 | -0.01834 | -0.14191 | 0.13733 | -0.13275 | -0.16937 | -0.022888 | -0.18768 | -0.10071 | -0.027466 | 0.13275 | -0.14191 | 0 | 0.064087 | 0.004578 | 0.07782 | 122.0718 | 0.009155 | -0.29755 | 122.1817 | 122.1039 | 122.0169 | 0.032043 | -0.054932 | 122.0627 | 0.004577 | -0.12817 | 122.2687 | 122.2824 | 122.2092 | 0.21973 | 0.14649 | 0.10986 | -0.036622 | 0.20599 | 0.14191 | 0.27008 | 0.27466 | 122.3419 | 122.3373 | -0.26093 | -0.27008 | 122.0352 | 122.2046 | 122.0627 | 122.1771
3393 | 122.374 | -122.2229 | 0.14191 | -0.0051118 | -0.0096707 | -0.079651 | -0.0039883 | -0.030016 | -0.052517 | -0.039537 | -0.0021057 | 0.004672 | 0.0079212 | -0.0082116 | -0.21958 | -0.01706 | -0.020689 | -0.13275 | 0.1236 | -0.15106 | -0.16022 | -0.045776 | -0.21057 | -0.11444 | -0.073242 | 0.15564 | -0.13733 | -0.050354 | 0.036621 | -0.041199 | 0.059509 | 122.0718 | -0.018311 | -0.30212 | 122.1771 | 122.1085 | 122.0123 | 0.036621 | -0.059509 | 122.0856 | 0.013733 | -0.19226 | 122.2595 | 122.2824 | 122.1817 | 0.19684 | 0.09613 | 0.10529 | -0.009155 | 0.17395 | 0.086975 | 0.27466 | 0.29297 | 122.3465 | 122.3785 | -0.29297 | -0.27924 | 122.0627 | 122.1725 | 122.0901 | 122.1497
3394.7969 | 122.4884 | -122.1909 | 0.09613 | -0.0051118 | -0.0088163 | -0.079438 | -0.0076199 | -0.029375 | -0.049526 | -0.042101 | -0.0021057 | 0.0053128 | 0.0079212 | -0.015048 | -0.21979 | -0.01941 | -0.022398 | -0.091553 | 0.10071 | -0.1236 | -0.086975 | 0.059509 | -0.10529 | -0.009155 | 0.07782 | 0.10986 | -0.10529 | 0.086975 | 0.17853 | 0.10071 | 0.16022 | 122.0673 | 0.004578 | -0.1831 | 122.2504 | 122.1817 | 122.0856 | 0.11444 | 0.01831 | 122.0856 | 0.013733 | -0.009155 | 122.3694 | 122.3511 | 122.2916 | 0.2655 | 0.20599 | 0.1831 | 0.036621 | 0.28381 | 0.19226 | 0.2243 | 0.21515 | 122.2916 | 122.3007 | -0.21973 | -0.20142 | 122.1039 | 122.2778 | 122.0993 | 122.2687
3396.5938 | 122.5159 | -122.2183 | 0.07782 | -0.0051118 | -0.013089 | -0.080719 | -0.0097561 | -0.029589 | -0.050595 | -0.040819 | 0.00094606 | 0.002963 | 0.0062122 | -0.014834 | -0.21915 | -0.019196 | -0.026244 | -0.086975 | 0.082397 | -0.09613 | -0.059509 | 0.12817 | -0.036621 | 0.032043 | 0.10986 | 0.091553 | -0.10986 | 0.073242 | 0.20142 | 0.14191 | 0.16937 | 122.1222 | 0.004577 | -0.13733 | 122.3465 | 122.2504 | 122.1817 | 0.12817 | 0.059509 | 122.1085 | 0.013733 | -0.004578 | 122.4197 | 122.3877 | 122.3602 | 0.27924 | 0.25177 | 0.2243 | 0.036621 | 0.31128 | 0.18311 | 0.17853 | 0.20142 | 122.3007 | 122.3099 | -0.17395 | -0.18768 | 122.1588 | 122.2916 | 122.1313 | 122.3282
3398.3906 | 122.3465 | -122.2229 | 0.17395 | -0.012741 | -0.01437 | -0.080933 | -0.0078335 | -0.030657 | -0.050381 | -0.04146 | -0.0021057 | 0.0040312 | 0.0083484 | -0.012911 | -0.22129 | -0.017701 | -0.024321 | -0.10071 | 0.10071 | -0.13275 | -0.10986 | 0.036621 | -0.11444 | -0.045776 | -0.027466 | 0.13733 | -0.10529 | -0.059509 | 0.07782 | 0.009155 | 0.036621 | 122.0901 | -0.073242 | -0.28381 | 122.2595 | 122.1771 | 122.1085 | 0.086975 | 0.01831 | 122.1176 | -0.036621 | -0.23346 | 122.3007 | 122.2595 | 122.2321 | 0.14191 | 0.11444 | 0.16937 | 0.022888 | 0.18311 | 0.045777 | 0.23346 | 0.24262 | 122.3236 | 122.3602 | -0.3067 | -0.27924 | 122.113 | 122.1634 | 122.1222 | 122.1954
3400.1094 | 122.4243 | -121.8887 | 0.32501 | 0.0025177 | -0.017147 | -0.080719 | -0.0095425 | -0.029162 | -0.049099 | -0.039965 | 0.00094606 | -2.7806e-05 | 0.0059986 | -0.0073572 | -0.22086 | -0.018128 | -0.023894 | -0.064087 | 0.07782 | -0.10071 | -0.018311 | 0.15564 | -0.022888 | 0.041199 | 0.12817 | 0.091553 | -0.10529 | 0.073242 | 0.21973 | 0.15106 | 0.15106 | 121.788 | -0.24719 | -0.34332 | 122.0444 | 121.9299 | 121.8658 | 0.14191 | 0.07782 | 121.7834 | -0.23346 | -0.25177 | 122.1085 | 122.0398 | 122.0398 | 0.25635 | 0.25635 | 0.25635 | 0.082397 | 0.32501 | 0.17853 | 0.17853 | 0.19684 | 121.9666 | 121.9803 | -0.42572 | -0.4303 | 121.8704 | 121.962 | 121.8246 | 122.0169
3401.9062 | 122.2641 | -121.6736 | 0.47607 | -0.0051118 | -0.013729 | -0.07837 | -0.0067653 | -0.032793 | -0.050167 | -0.044878 | 0.00094606 | 0.0021084 | 0.0081348 | -0.015688 | -0.21979 | -0.01706 | -0.022185 | -0.091553 | 0.091553 | -0.091553 | -0.082397 | 0.091553 | -0.10071 | 0.009155 | 0.064087 | 0.10071 | -0.10529 | 0.036621 | 0.13275 | 0.073242 | 0.11444 | 121.582 | -0.38452 | -0.55847 | 121.7651 | 121.6827 | 121.5729 | 0.10071 | -0.009155 | 121.5683 | -0.37537 | -0.43945 | 121.8063 | 121.788 | 121.7468 | 0.21973 | 0.17853 | 0.18311 | 0.009156 | 0.23804 | 0.14191 | 0.18311 | 0.20599 | 121.7651 | 121.7743 | -0.56763 | -0.58136 | 121.5912 | 121.7102 | 121.582 | 121.7377
3403.6562 | 122.2229 | -121.2936 | 0.72784 | 0.0025177 | -0.010952 | -0.07837 | -0.0052701 | -0.032793 | -0.051235 | -0.043169 | -0.0021057 | 0.0025358 | 0.0072802 | -0.01932 | -0.22086 | -0.017701 | -0.019621 | -0.064087 | 0.09613 | -0.09613 | -0.059509 | 0.1236 | -0.068665 | 0.013733 | 0.11902 | 0.11444 | -0.10986 | 0.050354 | 0.14191 | 0.07782 | 0.12817 | 121.1975 | -0.63171 | -0.78735 | 121.4172 | 121.3074 | 121.225 | 0.10986 | 0.027465 | 121.1838 | -0.6134 | -0.67749 | 121.4355 | 121.4218 | 121.3715 | 0.23804 | 0.18768 | 0.21973 | 0.036621 | 0.25177 | 0.16022 | 0.19226 | 0.2243 | 121.3898 | 121.4081 | -0.82397 | -0.83771 | 121.2341 | 121.344 | 121.2296 | 121.4127
3405.4531 | 121.8842 | -120.9137 | 1.0437 | -0.0051118 | -0.0094571 | -0.079651 | -0.0046291 | -0.028948 | -0.049099 | -0.041033 | -0.0021057 | 0.0053128 | 0.0070666 | -0.010348 | -0.21851 | -0.016846 | -0.025816 | -0.11444 | 0.12817 | -0.13275 | -0.16479 | -0.041199 | -0.19684 | -0.10071 | -0.045776 | 0.13275 | -0.14191 | -0.036621 | 0.032043 | -0.041199 | 0.041199 | 120.7809 | -0.91553 | -1.2085 | 120.8725 | 120.813 | 120.7169 | 0.032043 | -0.064087 | 120.7718 | -0.91095 | -1.0803 | 120.9457 | 120.9549 | 120.8725 | 0.18311 | 0.10071 | 0.091552 | -0.032044 | 0.17395 | 0.10529 | 0.26093 | 0.27466 | 121.0419 | 121.0464 | -1.1765 | -1.1856 | 120.7489 | 120.8771 | 120.7993 | 120.8679
3407.2344 | 121.788 | -121.3348 | 0.15564 | -0.012741 | -0.01437 | -0.079651 | -0.0074063 | -0.029589 | -0.051449 | -0.041246 | -0.0021057 | 0.0033902 | 0.0077076 | -0.012698 | -0.21851 | -0.015992 | -0.022185 | -0.10986 | 0.091553 | -0.10529 | -0.086975 | 0.059509 | -0.09613 | 0.004578 | 0.036621 | 0.10529 | -0.10986 | 0.041199 | 0.16022 | 0.082397 | 0.13275 | 121.2296 | -0.064087 | -0.24261 | 121.3943 | 121.3394 | 121.2387 | 0.10986 | 0.009156 | 121.225 | -0.050354 | -0.11444 | 121.4951 | 121.4676 | 121.4172 | 0.24261 | 0.19226 | 0.16479 | 0.018311 | 0.27008 | 0.15106 | 0.19684 | 0.21515 | 121.4264 | 121.4401 | -0.26093 | -0.2655 | 121.2479 | 121.376 | 121.225 | 121.3715
3409.0469 | 121.8796 | -121.7148 | 0.11902 | 0.0025177 | -0.010952 | -0.080719 | -0.0048427 | -0.028734 | -0.053372 | -0.042314 | 0.00094606 | 0.0036038 | 0.0072802 | -0.0090662 | -0.21937 | -0.018769 | -0.022398 | -0.09613 | 0.10986 | -0.12817 | -0.11444 | 0.036621 | -0.11902 | -0.073242 | 0.032043 | 0.14648 | -0.12817 | -0.004578 | 0.091553 | 0.009155 | 0.064087 | 121.5866 | -0.009156 | -0.23346 | 121.7514 | 121.6415 | 121.5958 | 0.054932 | 0.009155 | 121.5866 | 0.027465 | -0.1236 | 121.8063 | 121.7789 | 121.7239 | 0.19226 | 0.13733 | 0.1648 | 0.013733 | 0.21973 | 0.1236 | 0.23804 | 0.27466 | 121.8246 | 121.8613 | -0.24719 | -0.24719 | 121.6003 | 121.7102 | 121.6187 | 121.7468
3410.8281 | 122.1222 | -121.8155 | 0.091553 | -0.0051118 | -0.014584 | -0.080292 | -0.0080471 | -0.029802 | -0.050381 | -0.040392 | -0.0021057 | 0.0016812 | 0.0079212 | -0.015475 | -0.21915 | -0.018982 | -0.018553 | -0.082397 | 0.091553 | -0.11444 | -0.059509 | 0.10529 | -0.041199 | 0.027466 | 0.10986 | 0.091553 | -0.10529 | 0.068665 | 0.20142 | 0.14191 | 0.15106 | 121.701 | 0 | -0.15106 | 121.9208 | 121.843 | 121.7743 | 0.14191 | 0.073242 | 121.7102 | 0 | -0.022888 | 122.0169 | 121.9666 | 121.9574 | 0.25635 | 0.24719 | 0.21973 | 0.054932 | 0.3067 | 0.17395 | 0.20599 | 0.19684 | 121.907 | 121.907 | -0.20599 | -0.19684 | 121.756 | 121.8842 | 121.7331 | 121.9254
3412.5625 | 122.1634 | -121.8567 | 0.086975 | 0.0025177 | -0.015438 | -0.08136 | -0.0080471 | -0.032366 | -0.050167 | -0.039751 | -0.0021057 | 0.001254 | 0.007494 | -0.010775 | -0.21808 | -0.021332 | -0.01898 | -0.050354 | 0.073242 | -0.09613 | -0.018311 | 0.15564 | -0.013733 | 0.050354 | 0.12817 | 0.09613 | -0.10529 | 0.073242 | 0.20142 | 0.14648 | 0.15106 | 121.7606 | -0.013733 | -0.10529 | 122.0123 | 121.907 | 121.843 | 0.14648 | 0.082397 | 121.7514 | 0.009155 | -0.013733 | 122.0581 | 122.0078 | 122.0032 | 0.25635 | 0.25177 | 0.25177 | 0.077819 | 0.3067 | 0.17853 | 0.16937 | 0.20142 | 121.9299 | 121.9528 | -0.1831 | -0.19226 | 121.8384 | 121.9299 | 121.8063 | 121.9849
3414.3594 | 122.1909 | -121.9162 | 0.10071 | -0.012741 | -0.014157 | -0.080506 | -0.0069791 | -0.031511 | -0.053799 | -0.039537 | 0.00094606 | 0.0040312 | 0.0062122 | -0.0094934 | -0.22129 | -0.01941 | -0.021971 | -0.059509 | 0.064087 | -0.10529 | -0.022888 | 0.15106 | -0.022888 | 0.045776 | 0.11902 | 0.091553 | -0.10986 | 0.07782 | 0.20142 | 0.15564 | 0.15564 | 121.8109 | -0.036621 | -0.1236 | 122.0673 | 121.962 | 121.8933 | 0.15106 | 0.082398 | 121.8063 | -0.009155 | -0.022888 | 122.1176 | 122.0718 | 122.0718 | 0.2655 | 0.2655 | 0.25635 | 0.082398 | 0.31128 | 0.18768 | 0.16937 | 0.20142 | 121.9803 | 122.0078 | -0.20599 | -0.21057 | 121.8933 | 121.994 | 121.8567 | 122.0352
3416.0781 | 122.1313 | -121.9345 | 0.1236 | 0.010147 | -0.01437 | -0.079651 | -0.0065517 | -0.029375 | -0.050595 | -0.039965 | -0.0051575 | 0.0042448 | 0.0059986 | -0.0073572 | -0.22001 | -0.017273 | -0.023253 | -0.10071 | 0.12817 | -0.14648 | -0.13275 | -0.009155 | -0.13733 | -0.07782 | -0.045776 | 0.11902 | -0.13275 | -0.004578 | 0.086975 | 0.032043 | 0.07782 | 121.788 | 0.004578 | -0.25635 | 121.9254 | 121.8567 | 121.7972 | 0.068664 | 0.009155 | 121.8018 | -0.004577 | -0.12817 | 122.0215 | 122.0123 | 121.9666 | 0.21057 | 0.16479 | 0.13733 | 0.013733 | 0.21973 | 0.12817 | 0.27466 | 0.25177 | 122.0627 | 122.0535 | -0.27008 | -0.25635 | 121.8018 | 121.9299 | 121.8338 | 121.8887
3417.8438 | 122.1542 | -121.962 | 0.13275 | 0.0025177 | -0.011166 | -0.078797 | -0.0037747 | -0.029802 | -0.05209 | -0.041246 | 0.00094606 | 0.0059538 | 0.0081348 | -0.010989 | -0.22043 | -0.017273 | -0.02368 | -0.082397 | 0.11444 | -0.12817 | -0.10529 | 0.045776 | -0.12817 | -0.059509 | 0.018311 | 0.13733 | -0.13275 | 0.018311 | 0.086975 | 0.009155 | 0.086975 | 121.8338 | -0.01831 | -0.23804 | 122.0078 | 121.9025 | 121.8338 | 0.068665 | 0 | 121.8292 | 0.004578 | -0.11444 | 122.0489 | 122.0489 | 121.9711 | 0.21973 | 0.14191 | 0.17395 | 0.022888 | 0.21973 | 0.15106 | 0.24262 | 0.27008 | 122.0764 | 122.0993 | -0.26093 | -0.2655 | 121.8567 | 121.9803 | 121.8796 | 121.9803
3419.6562 | 122.1909 | -121.994 | 0.11902 | 0.0025177 | -0.010739 | -0.080292 | -0.0050565 | -0.032152 | -0.051663 | -0.043383 | -0.0051575 | 0.00574 | 0.0079212 | -0.012911 | -0.21872 | -0.018342 | -0.021971 | -0.073242 | 0.12817 | -0.13733 | -0.10986 | 0.045776 | -0.10529 | -0.059509 | 0.022888 | 0.12817 | -0.13275 | 0.013733 | 0.10986 | 0.050354 | 0.082397 | 121.8567 | 0.009155 | -0.22888 | 122.0398 | 121.9345 | 121.8887 | 0.07782 | 0.032043 | 121.8613 | 0.009155 | -0.10529 | 122.1039 | 122.0764 | 122.0444 | 0.21515 | 0.18311 | 0.18311 | 0.027466 | 0.24261 | 0.14648 | 0.2655 | 0.26093 | 122.1222 | 122.1222 | -0.25635 | -0.25177 | 121.8842 | 122.0078 | 121.9208 | 122.0169
3421.3906 | 122.1313 | -121.994 | 0.13275 | 0.010147 | -0.010311 | -0.079011 | -0.0044155 | -0.026812 | -0.050808 | -0.040819 | 0.00094606 | 0.0042448 | 0.0089892 | -0.017397 | -0.22065 | -0.017273 | -0.019408 | -0.09613 | 0.12817 | -0.14648 | -0.16022 | -0.036621 | -0.17853 | -0.10986 | -0.068665 | 0.14191 | -0.13275 | -0.050354 | 0.041199 | -0.054932 | 0.045776 | 121.8475 | -0.004577 | -0.29297 | 121.9574 | 121.8842 | 121.8155 | 0.036621 | -0.032044 | 121.8613 | 0.009156 | -0.18311 | 122.0352 | 122.0398 | 121.9391 | 0.17853 | 0.077819 | 0.10986 | -0.013733 | 0.17395 | 0.082397 | 0.27466 | 0.27466 | 122.1222 | 122.1359 | -0.27924 | -0.2655 | 121.8338 | 121.9437 | 121.8979 | 121.9254
3423.1875 | 122.2137 | -122.0032 | 0.10071 | 0.0025177 | -0.011166 | -0.080719 | -0.0050565 | -0.028307 | -0.050381 | -0.04381 | -0.0021057 | 0.0044584 | 0.0094166 | -0.013766 | -0.22086 | -0.017487 | -0.024107 | -0.073242 | 0.10529 | -0.13733 | -0.11444 | 0.036621 | -0.1236 | -0.045776 | 0.041199 | 0.13275 | -0.11902 | 0.009155 | 0.10986 | 0.050354 | 0.086975 | 121.8658 | 0.004578 | -0.21515 | 122.0398 | 121.9574 | 121.8796 | 0.091553 | 0.013733 | 121.8842 | 0.032043 | -0.091553 | 122.113 | 122.0901 | 122.0535 | 0.20599 | 0.16937 | 0.17395 | 0.022888 | 0.22888 | 0.12817 | 0.24262 | 0.25177 | 122.1085 | 122.1359 | -0.23804 | -0.21973 | 121.8887 | 122.0123 | 121.9299 | 122.0444
3424.9219 | 122.2961 | -122.0169 | 0.091553 | 0.010147 | -0.013729 | -0.079438 | -0.0061245 | -0.02788 | -0.050595 | -0.043383 | -0.0021057 | 0.0016812 | 0.0077076 | -0.019961 | -0.22214 | -0.020478 | -0.023253 | -0.068665 | 0.068665 | -0.10071 | -0.032043 | 0.16479 | -0.009155 | 0.045776 | 0.11444 | 0.07782 | -0.10529 | 0.07782 | 0.18768 | 0.14648 | 0.14648 | 121.9162 | -0.022888 | -0.1236 | 122.1817 | 122.0627 | 122.0078 | 0.14648 | 0.091553 | 121.9116 | -0.013733 | -0.013733 | 122.2046 | 122.1634 | 122.1634 | 0.25177 | 0.25177 | 0.2655 | 0.068665 | 0.29297 | 0.18311 | 0.16937 | 0.18311 | 122.0856 | 122.0947 | -0.19226 | -0.19684 | 121.9849 | 122.0947 | 121.9482 | 122.1313
3426.7188 | 122.2321 | -122.0169 | 0.11444 | 0.0025177 | -0.013302 | -0.078797 | -0.0059109 | -0.028307 | -0.050381 | -0.042101 | 0.00094606 | 0.0042448 | 0.0064258 | -0.009707 | -0.21958 | -0.018128 | -0.023253 | -0.07782 | 0.12817 | -0.12817 | -0.10986 | 0.059509 | -0.10529 | -0.059509 | 0.036621 | 0.11902 | -0.1236 | 0.027466 | 0.10529 | 0.036621 | 0.10071 | 121.8887 | 0.013733 | -0.2243 | 122.0764 | 121.9574 | 121.9116 | 0.068665 | 0.022888 | 121.8933 | 0.004578 | -0.086975 | 122.1222 | 122.1176 | 122.0535 | 0.2243 | 0.16022 | 0.18768 | 0.018311 | 0.22888 | 0.15106 | 0.25635 | 0.24261 | 122.1451 | 122.1359 | -0.24262 | -0.23804 | 121.907 | 122.0444 | 121.9391 | 122.0535
3428.5156 | 122.3419 | -122.0352 | 0.091553 | -0.02037 | -0.015011 | -0.08136 | -0.0067653 | -0.035357 | -0.05209 | -0.040392 | -0.0051575 | 0.0010404 | 0.008562 | -0.021029 | -0.21915 | -0.017273 | -0.018767 | -0.064087 | 0.064087 | -0.086975 | -0.032043 | 0.1831 | -0.004578 | 0.059509 | 0.11444 | 0.091553 | -0.10071 | 0.091553 | 0.20599 | 0.14648 | 0.14191 | 121.9482 | -0.027466 | -0.1236 | 122.2183 | 122.0947 | 122.0306 | 0.14648 | 0.082397 | 121.9345 | 0 | 0 | 122.2412 | 122.1771 | 122.1817 | 0.24262 | 0.24719 | 0.27008 | 0.054932 | 0.3067 | 0.19226 | 0.15106 | 0.19226 | 122.0993 | 122.1268 | -0.17853 | -0.19226 | 122.0032 | 122.1268 | 121.9711 | 122.1497
3430.3125 | 122.2137 | -122.081 | 0.11902 | -0.0051118 | -0.011807 | -0.080933 | -0.0054837 | -0.030871 | -0.052517 | -0.041674 | 0.0039979 | 0.0027494 | 0.0059986 | -0.011843 | -0.22043 | -0.017914 | -0.026244 | -0.14648 | 0.12817 | -0.13733 | -0.16937 | -0.013733 | -0.14648 | -0.073242 | -0.059509 | 0.14191 | -0.15106 | -0.036621 | 0.054932 | -0.013733 | 0.045776 | 121.9437 | 0.009155 | -0.28839 | 122.0673 | 122.0078 | 121.9345 | 0.064087 | -0.009155 | 121.9299 | 0.022888 | -0.15564 | 122.1359 | 122.1268 | 122.0673 | 0.19684 | 0.13733 | 0.1236 | -0.032044 | 0.20599 | 0.11444 | 0.2655 | 0.29297 | 122.2092 | 122.2229 | -0.25635 | -0.27008 | 121.9116 | 122.0444 | 121.9345 | 122.0215
3432.0938 | 122.3648 | -122.049 | 0.09613 | 0.017777 | -0.015011 | -0.080933 | -0.0076199 | -0.029589 | -0.04739 | -0.040178 | -0.0021057 | 0.0014676 | 0.0053576 | -0.015261 | -0.21979 | -0.017914 | -0.021117 | -0.050354 | 0.082397 | -0.11902 | -0.045776 | 0.15106 | -0.004578 | 0.041199 | 0.10529 | 0.10071 | -0.10071 | 0.064087 | 0.19684 | 0.1236 | 0.13275 | 121.9299 | -0.013733 | -0.14191 | 122.2 | 122.0901 | 122.0444 | 0.16022 | 0.11444 | 121.9482 | 0.004578 | -0.032043 | 122.2458 | 122.1817 | 122.1725 | 0.23346 | 0.2243 | 0.27008 | 0.073243 | 0.29755 | 0.1648 | 0.20142 | 0.20142 | 122.1313 | 122.1497 | -0.21515 | -0.19684 | 122.0032 | 122.113 | 121.9986 | 122.1542
3433.8125 | 122.2824 | -121.9666 | 0.14648 | -0.012741 | -0.012234 | -0.080506 | -0.0067653 | -0.031084 | -0.048458 | -0.041674 | 0.00094606 | 0.0021084 | 0.0072802 | -0.012484 | -0.22172 | -0.018555 | -0.026244 | -0.059509 | 0.064087 | -0.10071 | -0.045776 | 0.10986 | -0.073242 | 0 | 0.10529 | 0.10071 | -0.091553 | 0.091553 | 0.16479 | 0.091553 | 0.16479 | 121.8658 | -0.082397 | -0.19226 | 122.0764 | 121.9666 | 121.8933 | 0.10071 | 0.027466 | 121.875 | -0.045776 | -0.054931 | 122.1313 | 122.1313 | 122.0581 | 0.25635 | 0.18311 | 0.21057 | 0.054932 | 0.25635 | 0.18311 | 0.1648 | 0.19226 | 122.0306 | 122.0673 | -0.24719 | -0.23804 | 121.9208 | 122.0581 | 121.907 | 122.0718
3435.6094 | 122.3877 | -122.0627 | 0.07782 | -0.0051118 | -0.012448 | -0.077729 | -0.0048427 | -0.026598 | -0.04974 | -0.039324 | 0.0039979 | 0.0021084 | 0.008562 | -0.012698 | -0.22193 | -0.018555 | -0.024748 | -0.041199 | 0.07782 | -0.086975 | -0.041199 | 0.1236 | -0.064087 | 0.009155 | 0.11444 | 0.086975 | -0.11444 | 0.091553 | 0.17853 | 0.10529 | 0.15106 | 121.9757 | 0 | -0.11902 | 122.1863 | 122.0718 | 121.9986 | 0.09613 | 0.022888 | 121.9482 | 0.009155 | 0.013733 | 122.2412 | 122.2137 | 122.168 | 0.2655 | 0.21973 | 0.21057 | 0.045776 | 0.29297 | 0.20599 | 0.16479 | 0.20142 | 122.1405 | 122.1497 | -0.16479 | -0.19226 | 122.0215 | 122.1542 | 122.0215 | 122.1771
3437.4062 | 122.3465 | -122.0856 | 0.091553 | 0.010147 | -0.014584 | -0.079224 | -0.0076199 | -0.031084 | -0.047604 | -0.042314 | -0.0051575 | 0.00039959 | 0.0064258 | -0.011416 | -0.22129 | -0.01941 | -0.022826 | -0.086975 | 0.086975 | -0.10986 | -0.07782 | 0.068665 | -0.086975 | 0.004578 | 0.045776 | 0.10986 | -0.11902 | 0.032043 | 0.11902 | 0.068665 | 0.11902 | 121.9757 | -0.004578 | -0.16937 | 122.1542 | 122.0901 | 121.9986 | 0.11444 | 0.022888 | 121.9666 | 0.01831 | -0.05951 | 122.2046 | 122.2046 | 122.1542 | 0.23804 | 0.18768 | 0.17853 | 0.032043 | 0.23804 | 0.15106 | 0.19684 | 0.22888 | 122.1725 | 122.1954 | -0.20142 | -0.21057 | 122.0078 | 122.1176 | 121.9986 | 122.1313
3439.2031 | 122.406 | -122.081 | 0.11444 | -0.012741 | -0.0092435 | -0.078156 | -0.0054837 | -0.03258 | -0.04739 | -0.041887 | -0.0021057 | 0.0038174 | 0.0064258 | -0.011843 | -0.22065 | -0.015137 | -0.019408 | -0.050354 | 0.09613 | -0.10071 | -0.045776 | 0.09613 | -0.073242 | 0.013733 | 0.10071 | 0.10529 | -0.10071 | 0.10529 | 0.16937 | 0.10529 | 0.16479 | 121.9803 | -0.018311 | -0.16022 | 122.1771 | 122.0947 | 122.0078 | 0.11444 | 0.027466 | 121.9803 | -0.009155 | -0.009155 | 122.2504 | 122.2458 | 122.1863 | 0.2655 | 0.20599 | 0.19684 | 0.054932 | 0.27008 | 0.20599 | 0.19684 | 0.20599 | 122.1771 | 122.1863 | -0.21515 | -0.21515 | 122.0352 | 122.1863 | 122.0306 | 122.1817
3440.9219 | 122.374 | -122.0993 | 0.082397 | -0.012741 | -0.014157 | -0.079224 | -0.0069791 | -0.032152 | -0.049954 | -0.043383 | 0.00094606 | 0.0033902 | 0.0098438 | -0.013125 | -0.2215 | -0.019623 | -0.025603 | -0.068665 | 0.086975 | -0.091553 | -0.064087 | 0.11902 | -0.10071 | 0 | 0.068665 | 0.10986 | -0.10529 | 0.032043 | 0.13275 | 0.064087 | 0.10986 | 122.0078 | 0.004578 | -0.14648 | 122.2183 | 122.0993 | 121.9986 | 0.091553 | -0.009155 | 121.994 | 0.027466 | -0.050354 | 122.2321 | 122.2092 | 122.1634 | 0.21515 | 0.16937 | 0.21057 | 0.027466 | 0.23804 | 0.13733 | 0.17853 | 0.21515 | 122.1863 | 122.2092 | -0.17395 | -0.18768 | 122.0352 | 122.1313 | 122.0306 | 122.168
3442.7031 | 122.2824 | -122.1451 | 0.13733 | -0.0051118 | -0.010739 | -0.079224 | -0.0059109 | -0.031511 | -0.050167 | -0.041674 | 0.00094606 | 0.0076626 | 0.0079212 | -0.0092798 | -0.21979 | -0.017914 | -0.023467 | -0.10986 | 0.1236 | -0.15106 | -0.16022 | -0.036621 | -0.18768 | -0.11902 | -0.073242 | 0.13275 | -0.13275 | -0.050354 | 0.018311 | -0.059509 | 0.032043 | 121.994 | -0.013733 | -0.29755 | 122.1085 | 122.0261 | 121.9574 | 0.032043 | -0.036621 | 122.0123 | -0.004578 | -0.18768 | 122.1634 | 122.1771 | 122.0856 | 0.16479 | 0.073242 | 0.11444 | -0.009155 | 0.15106 | 0.082397 | 0.27466 | 0.2655 | 122.2687 | 122.2778 | -0.28839 | -0.27008 | 121.9849 | 122.0947 | 122.0352 | 122.0718
3444.5156 | 122.4197 | -122.113 | 0.11444 | 0.010147 | -0.013729 | -0.081574 | -0.0061245 | -0.030871 | -0.051022 | -0.042955 | -0.0021057 | 0.00039959 | 0.0055712 | -0.017184 | -0.21808 | -0.020478 | -0.02133 | -0.09613 | 0.082397 | -0.11902 | -0.064087 | 0.10529 | -0.036621 | 0.045776 | 0.10529 | 0.09613 | -0.11444 | 0.07782 | 0.19684 | 0.13733 | 0.15564 | 121.994 | -0.032044 | -0.17853 | 122.2183 | 122.1588 | 122.0764 | 0.16479 | 0.082398 | 121.9986 | -0.018311 | -0.036621 | 122.3099 | 122.2687 | 122.2504 | 0.27008 | 0.25177 | 0.22431 | 0.054932 | 0.31128 | 0.19226 | 0.20142 | 0.21057 | 122.1954 | 122.2092 | -0.23346 | -0.22888 | 122.049 | 122.1909 | 122.0169 | 122.2183
3446.2969 | 122.4106 | -122.1313 | 0.09613 | -0.0051118 | -0.010739 | -0.079651 | -0.0052701 | -0.029375 | -0.052304 | -0.041033 | -0.0021057 | 0.0027494 | 0.005144 | -0.0090662 | -0.22107 | -0.016846 | -0.024962 | -0.045776 | 0.07782 | -0.082397 | -0.027466 | 0.13275 | -0.054932 | 0.027466 | 0.11444 | 0.10071 | -0.086975 | 0.082397 | 0.16479 | 0.091553 | 0.14191 | 122.049 | -0.01831 | -0.1236 | 122.2641 | 122.1588 | 122.0764 | 0.10986 | 0.027465 | 122.0444 | 0.004578 | -0.013733 | 122.2961 | 122.2733 | 122.2229 | 0.22888 | 0.17853 | 0.21515 | 0.054931 | 0.25177 | 0.16937 | 0.16022 | 0.18768 | 122.2092 | 122.2321 | -0.17853 | -0.1831 | 122.1039 | 122.2137 | 122.0856 | 122.2458
3448.0781 | 122.3465 | -122.1588 | 0.10071 | -0.0051118 | -0.013089 | -0.077942 | -0.0050565 | -0.026598 | -0.049954 | -0.040605 | -0.0021057 | 0.0048856 | 0.0083484 | -0.013552 | -0.22107 | -0.017487 | -0.023467 | -0.13275 | 0.10071 | -0.15564 | -0.15106 | -0.013733 | -0.19684 | -0.07782 | -0.018311 | 0.12817 | -0.12817 | 0.036621 | 0.091553 | 0.018311 | 0.086975 | 122.0032 | 0 | -0.25177 | 122.1451 | 122.081 | 121.962 | 0.07782 | -0.041198 | 122.0306 | 0.027466 | -0.064087 | 122.2504 | 122.2458 | 122.1771 | 0.21515 | 0.14649 | 0.14191 | 0.004578 | 0.21973 | 0.1648 | 0.25635 | 0.25635 | 122.2595 | 122.287 | -0.25635 | -0.22888 | 122.0078 | 122.1954 | 122.0261 | 122.1405
3449.875 | 122.3419 | -122.1817 | 0.11902 | 0.010147 | -0.010739 | -0.079865 | -0.0033475 | -0.029589 | -0.050381 | -0.04146 | -0.0021057 | 0.0044584 | 0.007494 | -0.014193 | -0.22086 | -0.016633 | -0.025816 | -0.082397 | 0.10986 | -0.12817 | -0.11444 | 0.032043 | -0.14191 | -0.064087 | 0.022888 | 0.15106 | -0.10071 | 0.004578 | 0.07782 | -0.018311 | 0.073242 | 122.0535 | -0.009156 | -0.23346 | 122.2137 | 122.1176 | 122.0398 | 0.064087 | -0.013733 | 122.081 | 0.032043 | -0.11444 | 122.2595 | 122.2549 | 122.1634 | 0.17395 | 0.082397 | 0.16022 | 0.013733 | 0.17853 | 0.10529 | 0.23804 | 0.25177 | 122.2916 | 122.3328 | -0.24719 | -0.21973 | 122.0673 | 122.1863 | 122.0993 | 122.2046
3451.6719 | 122.4106 | -122.1771 | 0.086975 | -0.0051118 | -0.012448 | -0.080719 | -0.0078335 | -0.03557 | -0.050595 | -0.042314 | 0.00094606 | 0.001254 | 0.0083484 | -0.01462 | -0.21915 | -0.020264 | -0.021544 | -0.07782 | 0.086975 | -0.091553 | -0.073242 | 0.10529 | -0.10071 | 0 | 0.045776 | 0.12817 | -0.10529 | 0.054932 | 0.13275 | 0.073242 | 0.1236 | 122.0856 | 0 | -0.16022 | 122.2824 | 122.1771 | 122.0764 | 0.091553 | -0.009155 | 122.0718 | 0.041199 | -0.032043 | 122.3099 | 122.3007 | 122.2504 | 0.22888 | 0.17853 | 0.19684 | 0.018311 | 0.23804 | 0.16022 | 0.17853 | 0.23346 | 122.2641 | 122.3053 | -0.17853 | -0.19226 | 122.1039 | 122.2321 | 122.0993 | 122.2229
3453.3906 | 122.3282 | -122.2229 | 0.14648 | 0.0025177 | -0.015438 | -0.08136 | -0.0071927 | -0.029802 | -0.051449 | -0.043596 | 0.00094606 | 0.0027494 | 0.0055712 | -0.015688 | -0.22214 | -0.019196 | -0.023894 | -0.14648 | 0.11902 | -0.15106 | -0.16479 | -0.009155 | -0.14648 | -0.068665 | -0.045776 | 0.14648 | -0.16022 | -0.059509 | 0.059509 | -0.004578 | 0.027466 | 122.0718 | -0.027465 | -0.31128 | 122.2137 | 122.1542 | 122.0764 | 0.082397 | 0.004578 | 122.0627 | 0 | -0.20599 | 122.2824 | 122.2504 | 122.2183 | 0.18768 | 0.15564 | 0.14191 | -0.013733 | 0.21973 | 0.10071 | 0.27008 | 0.3067 | 122.3419 | 122.3694 | -0.29755 | -0.3067 | 122.0581 | 122.1634 | 122.0764 | 122.1771
3455.1719 | 122.4747 | -122.1542 | 0.086975 | -0.0051118 | -0.016934 | -0.080933 | -0.0080471 | -0.033007 | -0.051449 | -0.042742 | -0.0051575 | 0.00082679 | 0.0072802 | -0.017397 | -0.21979 | -0.021546 | -0.023467 | -0.050354 | 0.082397 | -0.086975 | -0.009155 | 0.18768 | -0.009155 | 0.068665 | 0.1236 | 0.11444 | -0.10986 | 0.091553 | 0.21057 | 0.14191 | 0.15106 | 122.0673 | -0.004578 | -0.09613 | 122.3419 | 122.2229 | 122.1451 | 0.15564 | 0.07782 | 122.0444 | 0.027466 | 0.004578 | 122.3648 | 122.3053 | 122.2961 | 0.26093 | 0.25177 | 0.27466 | 0.07782 | 0.32043 | 0.20142 | 0.16937 | 0.2243 | 122.2366 | 122.2687 | -0.17395 | -0.19684 | 122.1451 | 122.2458 | 122.1039 | 122.2778
3456.9688 | 122.4014 | -122.1909 | 0.11902 | -0.0051118 | -0.01138 | -0.07837 | -0.0029201 | -0.028948 | -0.051663 | -0.040819 | -0.0021057 | 0.0027494 | 0.007494 | -0.012698 | -0.22022 | -0.017701 | -0.027312 | -0.10529 | 0.12817 | -0.15106 | -0.14191 | 0.004578 | -0.1236 | -0.073242 | 0.004578 | 0.14191 | -0.1236 | 0.013733 | 0.10071 | 0.022888 | 0.07782 | 122.0398 | 0.009155 | -0.26093 | 122.1954 | 122.1176 | 122.0673 | 0.07782 | 0.027466 | 122.0673 | 0.022888 | -0.10529 | 122.2916 | 122.2687 | 122.2137 | 0.20142 | 0.14648 | 0.15564 | 0.009155 | 0.2243 | 0.13733 | 0.27924 | 0.2655 | 122.319 | 122.3328 | -0.27008 | -0.24261 | 122.0489 | 122.2046 | 122.0856 | 122.1954
3458.7031 | 122.3648 | -122.2275 | 0.13275 | 0.010147 | -0.012875 | -0.079011 | -0.0093289 | -0.03023 | -0.052731 | -0.042528 | -0.0021057 | 0.0038174 | 0.0077076 | -0.014193 | -0.21979 | -0.018769 | -0.024107 | -0.07782 | 0.091553 | -0.13275 | -0.11902 | 0.054932 | -0.10986 | -0.036621 | -0.009155 | 0.1236 | -0.13275 | -0.036621 | 0.064087 | 0 | 0.050354 | 122.0947 | -0.041198 | -0.25177 | 122.2824 | 122.1909 | 122.1176 | 0.09613 | 0.022888 | 122.0947 | -0.009155 | -0.16937 | 122.2916 | 122.2778 | 122.2275 | 0.18311 | 0.13275 | 0.18768 | 0.013732 | 0.19684 | 0.09613 | 0.2243 | 0.25635 | 122.319 | 122.3511 | -0.2655 | -0.2655 | 122.1085 | 122.1909 | 122.1497 | 122.2183
3460.5 | 122.4609 | -122.1909 | 0.082397 | -0.0051118 | -0.01202 | -0.079651 | -0.0074063 | -0.031939 | -0.050167 | -0.040819 | -0.0021057 | 0.0018948 | 0.0062122 | -0.013979 | -0.21787 | -0.018342 | -0.025389 | -0.054932 | 0.082397 | -0.091553 | -0.036621 | 0.1236 | -0.059509 | 0.009155 | 0.11444 | 0.10071 | -0.10529 | 0.086975 | 0.16479 | 0.091553 | 0.12817 | 122.0993 | 0 | -0.11902 | 122.3145 | 122.2 | 122.1313 | 0.10071 | 0.032044 | 122.0856 | 0.018311 | 0.004578 | 122.3557 | 122.319 | 122.2824 | 0.23346 | 0.19684 | 0.21515 | 0.054932 | 0.27008 | 0.19226 | 0.17395 | 0.20599 | 122.2733 | 122.2916 | -0.17395 | -0.18768 | 122.1542 | 122.2778 | 122.1359 | 122.3053
3462.2969 | 122.4701 | -122.1954 | 0.068665 | -0.012741 | -0.010952 | -0.07837 | -0.0065517 | -0.026171 | -0.048672 | -0.044023 | 0.00094606 | 0.00082679 | 0.0077076 | -0.0088526 | -0.22086 | -0.017914 | -0.025603 | -0.027466 | 0.082397 | -0.091553 | -0.032043 | 0.1236 | -0.050354 | 0.032043 | 0.13275 | 0.086975 | -0.10071 | 0.086975 | 0.16937 | 0.11444 | 0.13733 | 122.1039 | 0.013732 | -0.10071 | 122.319 | 122.2275 | 122.1451 | 0.1236 | 0.041199 | 122.0947 | 0.01831 | 0.01831 | 122.3648 | 122.3328 | 122.3099 | 0.23804 | 0.21515 | 0.21515 | 0.05951 | 0.27008 | 0.18768 | 0.17395 | 0.18768 | 122.2778 | 122.2824 | -0.16022 | -0.16937 | 122.1634 | 122.2824 | 122.168 | 122.3282
3464.0781 | 122.3785 | -122.2458 | 0.13275 | -0.0051118 | -0.013729 | -0.082642 | -0.0056973 | -0.032793 | -0.050595 | -0.042955 | 0.00094606 | 0.0044584 | 0.0087756 | -0.009707 | -0.21872 | -0.019196 | -0.023894 | -0.13733 | 0.11444 | -0.1236 | -0.16479 | -0.036621 | -0.14648 | -0.07782 | -0.050354 | 0.10986 | -0.1236 | -0.041199 | 0.045776 | 0 | 0.041199 | 122.1222 | -0.01831 | -0.29755 | 122.2092 | 122.168 | 122.0993 | 0.045776 | -0.022888 | 122.1222 | -0.022888 | -0.17395 | 122.2916 | 122.287 | 122.2458 | 0.16479 | 0.1236 | 0.086975 | -0.041199 | 0.16937 | 0.082397 | 0.23804 | 0.23346 | 122.3602 | 122.3557 | -0.25635 | -0.25635 | 122.081 | 122.2046 | 122.1085 | 122.1954
3465.8125 | 122.4426 | -122.2092 | 0.091553 | -0.0051118 | -0.012448 | -0.077302 | -0.0076199 | -0.030657 | -0.051235 | -0.042528 | -0.0021057 | 0.0018948 | 0.0059986 | -0.010348 | -0.22129 | -0.019837 | -0.024962 | -0.073242 | 0.07782 | -0.091553 | -0.050354 | 0.1236 | -0.073242 | 0.009155 | 0.082397 | 0.10986 | -0.10071 | 0.050354 | 0.14191 | 0.073242 | 0.1236 | 122.1176 | -0.013733 | -0.14191 | 122.3328 | 122.2183 | 122.1359 | 0.10071 | 0.018311 | 122.1085 | 0.01831 | -0.041199 | 122.3511 | 122.3328 | 122.2824 | 0.2243 | 0.17395 | 0.21515 | 0.041199 | 0.24262 | 0.15106 | 0.16937 | 0.21057 | 122.287 | 122.319 | -0.18311 | -0.19226 | 122.1588 | 122.2595 | 122.1359 | 122.2916
3467.6094 | 122.4243 | -122.2412 | 0.09613 | -0.0051118 | -0.012661 | -0.079224 | -0.0054837 | -0.028093 | -0.049313 | -0.040392 | 0.00094606 | 0.0031766 | 0.0072802 | -0.009707 | -0.22129 | -0.01706 | -0.023039 | -0.082397 | 0.14191 | -0.14191 | -0.10529 | 0.054932 | -0.11902 | -0.045776 | 0.041199 | 0.13733 | -0.12817 | 0.027466 | 0.10986 | 0.032043 | 0.091553 | 122.0993 | 0.045777 | -0.20142 | 122.2961 | 122.1954 | 122.1222 | 0.096131 | 0.022888 | 122.113 | 0.041199 | -0.068664 | 122.3511 | 122.3328 | 122.2733 | 0.21973 | 0.16022 | 0.19684 | 0.036621 | 0.23804 | 0.15564 | 0.28381 | 0.2655 | 122.3831 | 122.3785 | -0.23804 | -0.2243 | 122.1359 | 122.2687 | 122.1588 | 122.2824
3469.3438 | 122.4426 | -122.2275 | 0.086975 | 0.0025177 | -0.010311 | -0.078156 | -0.0037747 | -0.029375 | -0.050595 | -0.038256 | -0.0082091 | 0.0055264 | 0.0089892 | -0.014407 | -0.22043 | -0.01706 | -0.024321 | -0.1236 | 0.10529 | -0.12817 | -0.12817 | -0.009155 | -0.19226 | -0.082397 | 0.004578 | 0.11444 | -0.13275 | 0.022888 | 0.068665 | 0 | 0.086975 | 122.0993 | 0.018311 | -0.21515 | 122.2183 | 122.1451 | 122.0352 | 0.045777 | -0.064087 | 122.0947 | 0.027466 | -0.064087 | 122.2961 | 122.3145 | 122.2275 | 0.21973 | 0.13275 | 0.11902 | 0 | 0.20142 | 0.15564 | 0.23346 | 0.24719 | 122.3328 | 122.3419 | -0.21515 | -0.21973 | 122.0993 | 122.2504 | 122.1039 | 122.2321
3471.125 | 122.4335 | -122.2549 | 0.12817 | -0.012741 | -0.012448 | -0.079224 | -0.0046291 | -0.027239 | -0.051235 | -0.044451 | 0.0039979 | 0.0048856 | 0.0064258 | -0.013339 | -0.21872 | -0.017273 | -0.020903 | -0.10529 | 0.11902 | -0.14648 | -0.11902 | 0.022888 | -0.11902 | -0.054932 | 0.009155 | 0.11902 | -0.1236 | 0.018311 | 0.082397 | 0.036621 | 0.086975 | 122.1085 | -0.009155 | -0.24719 | 122.2778 | 122.2 | 122.1359 | 0.091552 | 0.027465 | 122.1313 | -0.009155 | -0.10986 | 122.3373 | 122.3419 | 122.2916 | 0.21057 | 0.16022 | 0.16937 | 0.027465 | 0.20599 | 0.14191 | 0.2655 | 0.24261 | 122.374 | 122.374 | -0.27466 | -0.25177 | 122.1359 | 122.2733 | 122.1497 | 122.2641
3472.9062 | 122.525 | -122.2092 | 0.086975 | 0.0025177 | -0.014798 | -0.081574 | -0.0063381 | -0.033434 | -0.051235 | -0.041033 | -0.0021057 | 0.0016812 | 0.008562 | -0.018252 | -0.22043 | -0.020051 | -0.021758 | -0.07782 | 0.10529 | -0.091553 | -0.064087 | 0.11902 | -0.050354 | 0.036621 | 0.09613 | 0.09613 | -0.10986 | 0.073242 | 0.20142 | 0.14191 | 0.14191 | 122.1176 | 0.018311 | -0.15106 | 122.3282 | 122.2458 | 122.1588 | 0.12817 | 0.041199 | 122.0993 | 0.009155 | -0.013733 | 122.4106 | 122.3511 | 122.3511 | 0.25177 | 0.25177 | 0.21057 | 0.027466 | 0.31128 | 0.18311 | 0.19684 | 0.20599 | 122.3145 | 122.3053 | -0.17853 | -0.19684 | 122.1451 | 122.2824 | 122.1313 | 122.3053
3474.7031 | 122.5296 | -122.2092 | 0.086975 | -0.012741 | -0.010525 | -0.079224 | -0.0059109 | -0.026598 | -0.049954 | -0.041033 | -0.0051575 | 0.0018948 | 0.0079212 | -0.0099206 | -0.22086 | -0.016633 | -0.021117 | -0.041199 | 0.082397 | -0.11444 | -0.041199 | 0.11444 | -0.073242 | 0.018311 | 0.1236 | 0.09613 | -0.10071 | 0.09613 | 0.1831 | 0.10071 | 0.16937 | 122.0947 | -0.004578 | -0.12817 | 122.3236 | 122.2275 | 122.1359 | 0.13275 | 0.041199 | 122.1085 | 0.009155 | 0.009155 | 122.3923 | 122.3785 | 122.3099 | 0.27008 | 0.20142 | 0.22888 | 0.073242 | 0.28381 | 0.19684 | 0.19684 | 0.19684 | 122.2916 | 122.3053 | -0.20142 | -0.18768 | 122.168 | 122.3053 | 122.168 | 122.3328
3476.4375 | 122.5296 | -122.2275 | 0.10529 | 0.0025177 | -0.015225 | -0.079224 | -0.0082607 | -0.034289 | -0.051449 | -0.039751 | -0.0051575 | 0.0016812 | 0.005144 | -0.014834 | -0.22065 | -0.018555 | -0.02368 | -0.068665 | 0.07782 | -0.10071 | -0.032043 | 0.15106 | -0.022888 | 0.050354 | 0.09613 | 0.1236 | -0.11444 | 0.07782 | 0.20599 | 0.14191 | 0.15106 | 122.1268 | -0.027466 | -0.13733 | 122.3785 | 122.2778 | 122.2046 | 0.15106 | 0.07782 | 122.113 | 0.01831 | -0.027466 | 122.4335 | 122.3785 | 122.3694 | 0.2655 | 0.25635 | 0.25177 | 0.068665 | 0.32044 | 0.19226 | 0.17853 | 0.23804 | 122.3053 | 122.3511 | -0.20599 | -0.21973 | 122.1954 | 122.3053 | 122.1588 | 122.3236
3478.2188 | 122.3648 | -122.0718 | 0.22888 | -0.012741 | -0.016507 | -0.080079 | -0.0078335 | -0.029802 | -0.051449 | -0.042742 | -0.0051575 | 0.0033902 | 0.0066394 | -0.0054346 | -0.22001 | -0.018555 | -0.021758 | -0.068665 | 0.086975 | -0.10529 | -0.064087 | 0.10986 | -0.059509 | 0.013733 | 0.059509 | 0.10529 | -0.1236 | 0.013733 | 0.1236 | 0.054932 | 0.082397 | 121.9666 | -0.14191 | -0.29297 | 122.1817 | 122.0856 | 122.0123 | 0.11902 | 0.045777 | 121.9482 | -0.1236 | -0.21515 | 122.1954 | 122.1542 | 122.1268 | 0.20599 | 0.17853 | 0.21515 | 0.041199 | 0.24719 | 0.13733 | 0.19226 | 0.22888 | 122.1588 | 122.1771 | -0.33417 | -0.35248 | 122.0078 | 122.0856 | 122.0032 | 122.1313
3480.0156 | 122.3099 | -122.1313 | 0.20599 | -0.0051118 | -0.010525 | -0.079651 | -0.0031337 | -0.029162 | -0.049954 | -0.042742 | -0.0082091 | 0.0023222 | 0.007494 | -0.007998 | -0.21958 | -0.018342 | -0.024107 | -0.09613 | 0.13275 | -0.14191 | -0.16937 | -0.032043 | -0.1831 | -0.10071 | -0.054932 | 0.13275 | -0.1236 | -0.064087 | 0.018311 | -0.050354 | 0.050354 | 121.9894 | -0.073243 | -0.37537 | 122.0993 | 122.0306 | 121.9482 | 0.041199 | -0.041198 | 122.0078 | -0.073243 | -0.27008 | 122.1497 | 122.1817 | 122.081 | 0.17395 | 0.073242 | 0.10986 | -0.027466 | 0.14191 | 0.059509 | 0.27466 | 0.25635 | 122.2641 | 122.2641 | -0.3479 | -0.32959 | 121.962 | 122.0673 | 122.0352 | 122.0764
3481.8125 | 122.4792 | -122.1313 | 0.10529 | -0.012741 | -0.0094571 | -0.077515 | -0.0063381 | -0.029162 | -0.049526 | -0.042314 | 0.00094606 | 0.002963 | 0.0087756 | -0.012057 | -0.22043 | -0.018128 | -0.025176 | -0.036621 | 0.07782 | -0.10529 | -0.041199 | 0.11444 | -0.064087 | 0.018311 | 0.11902 | 0.091553 | -0.10529 | 0.091553 | 0.17853 | 0.10071 | 0.16022 | 122.0261 | -0.027466 | -0.14649 | 122.2458 | 122.1497 | 122.0673 | 0.1236 | 0.041199 | 122.0261 | -0.013733 | -0.013733 | 122.3099 | 122.2916 | 122.2321 | 0.2655 | 0.20599 | 0.21973 | 0.064087 | 0.28381 | 0.19684 | 0.18311 | 0.19684 | 122.2092 | 122.2229 | -0.21057 | -0.21057 | 122.0901 | 122.2229 | 122.0947 | 122.2504
3483.6094 | 121.8201 | -121.5683 | 0.15564 | -0.012741 | -0.010952 | -0.079438 | -0.0052701 | -0.030657 | -0.04974 | -0.041674 | 0.0039979 | 0.0027494 | 0.008562 | -0.017397 | -0.21958 | -0.015778 | -0.026244 | -0.13275 | 0.11902 | -0.13733 | -0.15564 | -0.009155 | -0.19226 | -0.07782 | -0.018311 | 0.14191 | -0.12817 | 0 | 0.082397 | 0.013733 | 0.09613 | 121.431 | -0.036621 | -0.31128 | 121.5591 | 121.4905 | 121.376 | 0.059509 | -0.054932 | 121.4401 | -0.013733 | -0.15564 | 121.6507 | 121.6644 | 121.582 | 0.2243 | 0.14191 | 0.12817 | -0.018311 | 0.21057 | 0.12817 | 0.25635 | 0.27008 | 121.6873 | 121.7102 | -0.29297 | -0.28381 | 121.4127 | 121.5683 | 121.4355 | 121.55
3485.4062 | 122.1863 | -121.8796 | 0.073242 | -0.0051118 | -0.013089 | -0.079011 | -0.0048427 | -0.030016 | -0.04974 | -0.040819 | -0.0021057 | 0.0021084 | 0.0066394 | -0.01227 | -0.22086 | -0.01706 | -0.021758 | -0.07782 | 0.09613 | -0.11902 | -0.059509 | 0.09613 | -0.068665 | 0 | 0.10071 | 0.10071 | -0.091553 | 0.086975 | 0.17395 | 0.10071 | 0.16022 | 121.7606 | 0.022888 | -0.13275 | 121.9757 | 121.8796 | 121.8109 | 0.11902 | 0.050354 | 121.788 | 0.027466 | 0.013733 | 122.0535 | 122.0398 | 121.9803 | 0.25177 | 0.19226 | 0.21515 | 0.05951 | 0.2655 | 0.17853 | 0.21515 | 0.19226 | 121.9757 | 121.9803 | -0.19226 | -0.16479 | 121.8201 | 121.9666 | 121.8018 | 121.9803
3487.125 | 122.2321 | -121.9482 | 0.091553 | -0.0051118 | -0.0096707 | -0.080933 | -0.0069791 | -0.027025 | -0.050381 | -0.042528 | -0.0021057 | 0.0023222 | 0.007494 | -0.015048 | -0.21979 | -0.018342 | -0.026457 | -0.10529 | 0.086975 | -0.11902 | -0.10529 | 0.064087 | -0.09613 | 0 | 0.032043 | 0.11902 | -0.11902 | 0.032043 | 0.14648 | 0.068665 | 0.11444 | 121.8292 | -0.004578 | -0.19684 | 122.0123 | 121.9482 | 121.8521 | 0.11902 | 0.022889 | 121.8292 | 0.027466 | -0.05951 | 122.0947 | 122.0627 | 122.0169 | 0.23346 | 0.18768 | 0.18311 | 0.013733 | 0.2655 | 0.15106 | 0.20599 | 0.23804 | 122.0352 | 122.0673 | -0.21057 | -0.21057 | 121.843 | 121.9803 | 121.843 | 121.9803
3488.9062 | 122.1634 | -122.0261 | 0.13733 | -0.012741 | -0.014584 | -0.080933 | -0.0071927 | -0.02788 | -0.049099 | -0.039751 | -0.0051575 | 0.0048856 | 0.0066394 | -0.010775 | -0.21702 | -0.018128 | -0.020476 | -0.15564 | 0.11902 | -0.14191 | -0.16479 | -0.004578 | -0.15106 | -0.07782 | -0.073242 | 0.13733 | -0.14191 | -0.054932 | 0.041199 | -0.022888 | 0.032043 | 121.8842 | -0.01831 | -0.30212 | 122.0215 | 121.9482 | 121.875 | 0.064087 | -0.009155 | 121.8842 | 0 | -0.19226 | 122.0673 | 122.0581 | 122.0032 | 0.17395 | 0.11902 | 0.13733 | -0.022888 | 0.18311 | 0.086975 | 0.26093 | 0.27924 | 122.1451 | 122.1634 | -0.27924 | -0.27924 | 121.8613 | 121.9711 | 121.8704 | 121.9528
3490.6406 | 122.2824 | -122.0261 | 0.082397 | -0.0051118 | -0.012234 | -0.079865 | -0.0071927 | -0.031511 | -0.04974 | -0.042742 | -0.0051575 | 0.0016812 | 0.0053576 | -0.013339 | -0.22107 | -0.019196 | -0.022185 | -0.09613 | 0.082397 | -0.10529 | -0.09613 | 0.064087 | -0.10071 | -0.013733 | 0.018311 | 0.10986 | -0.10986 | 0.013733 | 0.1236 | 0.068665 | 0.10071 | 121.9208 | 0 | -0.17853 | 122.0901 | 122.0123 | 121.9254 | 0.091553 | 0.004578 | 121.9162 | 0.027466 | -0.068664 | 122.1497 | 122.1268 | 122.0947 | 0.21057 | 0.17853 | 0.16937 | 0.009156 | 0.23346 | 0.1236 | 0.18768 | 0.21973 | 122.1085 | 122.1359 | -0.18768 | -0.19226 | 121.9299 | 122.0398 | 121.9299 | 122.0444
3492.3594 | 122.2275 | -122.081 | 0.12817 | 0.010147 | -0.01437 | -0.081788 | -0.0082607 | -0.033434 | -0.050595 | -0.042314 | -0.0082091 | 0.0061674 | 0.006853 | -0.012911 | -0.22236 | -0.01941 | -0.022612 | -0.15564 | 0.1236 | -0.14191 | -0.16937 | -0.009155 | -0.15106 | -0.068665 | -0.068665 | 0.13733 | -0.13733 | -0.054932 | 0.027466 | 0 | 0.036621 | 121.9391 | -0.004578 | -0.29755 | 122.0718 | 122.0123 | 121.9299 | 0.073242 | -0.009155 | 121.9437 | 0.009155 | -0.18311 | 122.1085 | 122.1176 | 122.081 | 0.17395 | 0.13733 | 0.13275 | -0.027466 | 0.16479 | 0.082397 | 0.2655 | 0.27466 | 122.2046 | 122.2183 | -0.27008 | -0.2655 | 121.9116 | 122.0261 | 121.9254 | 122.0123
3494.1406 | 122.3282 | -122.0581 | 0.09613 | -0.012741 | -0.013516 | -0.080292 | -0.0067653 | -0.03258 | -0.051449 | -0.042101 | -0.0021057 | 0.0014676 | 0.0066394 | -0.01163 | -0.22065 | -0.020264 | -0.025603 | -0.073242 | 0.082397 | -0.09613 | -0.064087 | 0.11444 | -0.10071 | -0.013733 | 0.068665 | 0.10071 | -0.10986 | 0.032043 | 0.13733 | 0.07782 | 0.10529 | 121.962 | -0.013733 | -0.16022 | 122.1725 | 122.0444 | 121.9574 | 0.082397 | -0.004578 | 121.9482 | 0.004578 | -0.064087 | 122.1954 | 122.1634 | 122.1359 | 0.21515 | 0.18768 | 0.21057 | 0.032043 | 0.24719 | 0.14191 | 0.17853 | 0.21057 | 122.1405 | 122.1588 | -0.19226 | -0.20599 | 121.994 | 122.0901 | 121.9849 | 122.1268
3495.8594 | 122.2366 | -122.0535 | 0.15106 | -0.0051118 | -0.0090299 | -0.080933 | -0.0059109 | -0.027666 | -0.050595 | -0.041246 | -0.0021057 | 0.0033902 | 0.0081348 | -0.0084252 | -0.21915 | -0.016633 | -0.024748 | -0.13275 | 0.13733 | -0.15106 | -0.16479 | -0.050354 | -0.20599 | -0.1236 | -0.082397 | 0.13733 | -0.13275 | -0.041199 | 0.009155 | -0.041199 | 0.054932 | 121.9025 | -0.013733 | -0.31586 | 122.0032 | 121.9299 | 121.8475 | 0.027466 | -0.054932 | 121.9208 | -0.013733 | -0.19226 | 122.0627 | 122.1085 | 122.0123 | 0.18768 | 0.091552 | 0.10071 | -0.013733 | 0.14191 | 0.091552 | 0.28839 | 0.27008 | 122.1909 | 122.1909 | -0.30212 | -0.28381 | 121.8887 | 122.0123 | 121.9208 | 121.9711
3497.6562 | 122.3145 | -121.8109 | 0.28839 | 0.0025177 | -0.01672 | -0.080079 | -0.0080471 | -0.032152 | -0.05209 | -0.03911 | -0.0021057 | 0.0023222 | 0.005144 | -0.019534 | -0.22107 | -0.021546 | -0.026244 | -0.064087 | 0.082397 | -0.11444 | -0.022888 | 0.16022 | -0.022888 | 0.054932 | 0.11902 | 0.086975 | -0.09613 | 0.082397 | 0.19226 | 0.1236 | 0.14648 | 121.6965 | -0.20599 | -0.31128 | 121.9711 | 121.8658 | 121.788 | 0.16937 | 0.091553 | 121.7148 | -0.20142 | -0.20599 | 122.0032 | 121.9574 | 121.9345 | 0.24261 | 0.21973 | 0.27466 | 0.091553 | 0.28839 | 0.17853 | 0.19684 | 0.1831 | 121.8933 | 121.8979 | -0.40283 | -0.38452 | 121.788 | 121.8933 | 121.7468 | 121.9299
3499.4531 | 122.2046 | -122.0718 | 0.11444 | 0.010147 | -0.012661 | -0.079438 | -0.0052701 | -0.031084 | -0.051663 | -0.038469 | -0.0021057 | 0.0059538 | 0.0045032 | -0.0050072 | -0.22278 | -0.015565 | -0.024748 | -0.086975 | 0.11444 | -0.1236 | -0.10529 | 0.054932 | -0.10986 | -0.050354 | 0.036621 | 0.12817 | -0.10071 | 0.009155 | 0.10986 | 0.027466 | 0.09613 | 121.9482 | 0 | -0.21973 | 122.1268 | 122.0215 | 121.962 | 0.073242 | 0.013733 | 121.9711 | 0.013733 | -0.10529 | 122.1817 | 122.168 | 122.0993 | 0.19684 | 0.12817 | 0.17853 | 0.01831 | 0.21057 | 0.10986 | 0.23804 | 0.22888 | 122.1863 | 122.2 | -0.23804 | -0.21515 | 121.9666 | 122.081 | 121.9849 | 122.1085
3501.1719 | 122.3785 | -122.2137 | 0.086975 | -0.0051118 | -0.01437 | -0.082642 | -0.0084743 | -0.033648 | -0.05209 | -0.040819 | -0.0051575 | 0.00082679 | 0.0045032 | -0.01462 | -0.21851 | -0.020051 | -0.022185 | -0.10071 | 0.086975 | -0.11444 | -0.10986 | 0.050354 | -0.10071 | -0.009155 | 0.022888 | 0.1236 | -0.10986 | 0.032043 | 0.14648 | 0.068665 | 0.11902 | 122.0993 | 0 | -0.19684 | 122.2641 | 122.2046 | 122.113 | 0.10529 | 0.013733 | 122.1039 | 0.036621 | -0.054932 | 122.3602 | 122.3328 | 122.2824 | 0.22888 | 0.17853 | 0.16479 | 0.004578 | 0.25635 | 0.14191 | 0.20142 | 0.23346 | 122.3007 | 122.3373 | -0.20142 | -0.19684 | 122.1039 | 122.2458 | 122.113 | 122.2366
3502.9531 | 122.2916 | -122.0261 | 0.18768 | 0.0025177 | -0.0096707 | -0.080933 | -0.0037747 | -0.031298 | -0.04974 | -0.038469 | 0.00094606 | 0.0031766 | 0.0087756 | -0.015688 | -0.22043 | -0.017487 | -0.022398 | -0.1236 | 0.10071 | -0.1236 | -0.15564 | -0.032043 | -0.20599 | -0.091553 | -0.036621 | 0.14191 | -0.14648 | -0.022888 | 0.050354 | -0.022888 | 0.054932 | 121.9025 | -0.086975 | -0.34332 | 121.994 | 121.9345 | 121.8201 | 0.032043 | -0.082398 | 121.8796 | -0.045776 | -0.21057 | 122.0764 | 122.081 | 122.0032 | 0.20142 | 0.1236 | 0.091553 | -0.032044 | 0.19684 | 0.1236 | 0.2243 | 0.28839 | 122.1268 | 122.168 | -0.31128 | -0.33417 | 121.8704 | 122.0032 | 121.9025 | 121.9894
3504.6875 | 122.3511 | -122.0169 | 0.16479 | 0.0025177 | -0.015652 | -0.081574 | -0.0078335 | -0.029375 | -0.051876 | -0.041887 | -0.0051575 | 0.001254 | 0.0055712 | -0.015261 | -0.22065 | -0.019623 | -0.021758 | -0.068665 | 0.073242 | -0.09613 | -0.018311 | 0.16022 | -0.018311 | 0.050354 | 0.14191 | 0.091553 | -0.10071 | 0.09613 | 0.21057 | 0.15106 | 0.16022 | 121.9208 | -0.091553 | -0.18311 | 122.1771 | 122.0673 | 121.9986 | 0.14648 | 0.077819 | 121.9162 | -0.073242 | -0.068665 | 122.2275 | 122.1771 | 122.168 | 0.26093 | 0.25177 | 0.25635 | 0.077819 | 0.31128 | 0.19684 | 0.16937 | 0.19226 | 122.0901 | 122.1085 | -0.26092 | -0.2655 | 121.9986 | 122.113 | 121.9482 | 122.1588
3506.4844 | 122.1542 | -121.9482 | 0.21973 | -0.0051118 | -0.010311 | -0.080933 | -0.0050565 | -0.030016 | -0.050381 | -0.042314 | 0.00094606 | 0.0040312 | 0.0072802 | -0.0075708 | -0.22022 | -0.017701 | -0.021971 | -0.082397 | 0.11444 | -0.12817 | -0.14648 | -0.004578 | -0.19226 | -0.10529 | -0.045776 | 0.14191 | -0.10529 | -0.045776 | 0.013733 | -0.045776 | 0.032043 | 121.8201 | -0.10529 | -0.36621 | 121.9437 | 121.843 | 121.756 | 0.022888 | -0.064087 | 121.843 | -0.07782 | -0.2655 | 121.962 | 121.9803 | 121.9025 | 0.13733 | 0.05951 | 0.1236 | -0.01831 | 0.11902 | 0.05951 | 0.24262 | 0.24719 | 122.0627 | 122.0901 | -0.3479 | -0.32501 | 121.8018 | 121.9025 | 121.8658 | 121.9025
3508.2656 | 121.0236 | -120.5887 | 0.16022 | -0.012741 | -0.01202 | -0.081788 | -0.0082607 | -0.031084 | -0.048458 | -0.04146 | -0.0051575 | 0.0018948 | 0.0064258 | -0.020175 | -0.22086 | -0.019837 | -0.023253 | -0.054932 | 0.082397 | -0.073242 | -0.022888 | 0.13733 | -0.022888 | 0.045776 | 0.12817 | 0.12817 | -0.10986 | 0.086975 | 0.21515 | 0.15106 | 0.15564 | 120.5154 | -0.07782 | -0.1831 | 120.726 | 120.6345 | 120.5658 | 0.11902 | 0.050354 | 120.4788 | -0.032043 | -0.073242 | 120.8038 | 120.7443 | 120.7397 | 0.2655 | 0.26093 | 0.21057 | 0.050354 | 0.32501 | 0.19684 | 0.15564 | 0.23804 | 120.6711 | 120.7169 | -0.23346 | -0.27008 | 120.5658 | 120.6757 | 120.5338 | 120.7169
3510.0469 | 121.2158 | -116.8213 | 4.6097 | 0.0025177 | -0.015225 | -0.079651 | -0.0063381 | -0.029375 | -0.052944 | -0.041674 | -0.0021057 | 0.002963 | 0.007494 | -0.014407 | -0.22107 | -0.018982 | -0.01834 | -0.068665 | 0.14191 | -0.091553 | -0.10529 | 0.041199 | -0.086975 | -0.041199 | -0.027466 | 0.13733 | -0.14648 | -0.054932 | 0.054932 | 0.004578 | 0.036621 | 116.7297 | -4.4678 | -4.715 | 116.8625 | 116.7801 | 116.7343 | 0.050354 | 0.004578 | 116.6748 | -4.4724 | -4.6646 | 116.8762 | 116.8579 | 116.8259 | 0.18311 | 0.15106 | 0.13275 | -0.013733 | 0.20142 | 0.091552 | 0.23346 | 0.28381 | 116.9632 | 116.9586 | -4.7012 | -4.7562 | 116.716 | 116.7664 | 116.7526 | 116.7938
3511.8438 | 121.756 | -121.6599 | 0.12817 | -0.0051118 | -0.015011 | -0.080292 | -0.0044155 | -0.032152 | -0.051876 | -0.042742 | 0.00094606 | 0.0040312 | 0.0077076 | -0.017825 | -0.22107 | -0.017487 | -0.019835 | -0.14648 | 0.14191 | -0.13733 | -0.17395 | -0.013733 | -0.15564 | -0.07782 | -0.068665 | 0.15106 | -0.14191 | -0.050354 | 0.036621 | -0.009155 | 0.050354 | 121.5225 | 0.013733 | -0.30212 | 121.6461 | 121.582 | 121.5042 | 0.059509 | -0.018311 | 121.5179 | 0.022888 | -0.17853 | 121.6965 | 121.7102 | 121.6507 | 0.19226 | 0.13275 | 0.1236 | -0.036621 | 0.17853 | 0.091553 | 0.27924 | 0.29297 | 121.8018 | 121.8109 | -0.2655 | -0.27008 | 121.4859 | 121.6095 | 121.5134 | 121.5912
3513.5781 | 122.0535 | -121.6415 | 0.13275 | -0.0051118 | -0.0090299 | -0.078797 | -0.0059109 | -0.028521 | -0.050808 | -0.040819 | 0.00094606 | 0.0036038 | 0.0081348 | -0.015475 | -0.21958 | -0.018128 | -0.023894 | -0.032043 | 0.068665 | -0.10071 | -0.027466 | 0.13733 | -0.045776 | 0.032043 | 0.13733 | 0.10529 | -0.091553 | 0.091553 | 0.17853 | 0.10986 | 0.14191 | 121.5408 | -0.064086 | -0.16022 | 121.7789 | 121.6736 | 121.5958 | 0.13275 | 0.054932 | 121.55 | -0.027465 | -0.041198 | 121.8201 | 121.7834 | 121.7514 | 0.23346 | 0.20142 | 0.23804 | 0.073242 | 0.27008 | 0.18311 | 0.16937 | 0.19684 | 121.7102 | 121.7468 | -0.23346 | -0.2243 | 121.6141 | 121.7331 | 121.6095 | 121.7789
3515.375 | 122.0123 | -121.7926 | 0.086975 | -0.0051118 | -0.014157 | -0.079651 | -0.0061245 | -0.031725 | -0.052304 | -0.042955 | -0.0021057 | 0.0021084 | 0.0053576 | -0.016757 | -0.21937 | -0.020051 | -0.027953 | -0.10529 | 0.091553 | -0.11444 | -0.09613 | 0.068665 | -0.09613 | -0.004578 | 0.027466 | 0.11902 | -0.11444 | 0.032043 | 0.13733 | 0.09613 | 0.11902 | 121.6782 | 0.004578 | -0.1831 | 121.8613 | 121.788 | 121.6965 | 0.10986 | 0.018311 | 121.6782 | 0.032044 | -0.054932 | 121.9299 | 121.9116 | 121.8887 | 0.23346 | 0.21057 | 0.18311 | 0.018311 | 0.25177 | 0.14648 | 0.20599 | 0.23346 | 121.8842 | 121.9116 | -0.20142 | -0.20142 | 121.6965 | 121.8246 | 121.6873 | 121.8201
3517.1562 | 121.9894 | -121.8018 | 0.12817 | 0.0025177 | -0.011807 | -0.077942 | -0.0035611 | -0.026598 | -0.053585 | -0.041246 | -0.0021057 | 0.0044584 | 0.007494 | -0.0088526 | -0.22065 | -0.01941 | -0.025389 | -0.086975 | 0.10071 | -0.13275 | -0.10529 | 0.036621 | -0.14648 | -0.050354 | 0.032043 | 0.12817 | -0.11902 | 0.009155 | 0.082397 | 0.004578 | 0.07782 | 121.669 | -0.027466 | -0.23346 | 121.8384 | 121.7514 | 121.6553 | 0.082397 | -0.013733 | 121.6827 | 0 | -0.11902 | 121.8842 | 121.8796 | 121.8063 | 0.19684 | 0.1236 | 0.16937 | 0.027465 | 0.20142 | 0.12817 | 0.23346 | 0.24719 | 121.9025 | 121.9299 | -0.26093 | -0.24719 | 121.6965 | 121.8109 | 121.7148 | 121.8338
3518.9375 | 121.2296 | -118.0618 | 3.2501 | -0.012741 | -0.013516 | -0.080292 | -0.0054837 | -0.02788 | -0.052944 | -0.039965 | -0.0021057 | 0.002963 | 0.0081348 | -0.013766 | -0.22129 | -0.018128 | -0.024107 | -0.091553 | 0.16937 | -0.11444 | -0.10529 | 0.045776 | -0.10529 | -0.050354 | -0.050354 | 0.1236 | -0.15564 | -0.018311 | 0.086975 | 0.009155 | 0.064087 | 117.9474 | -3.0807 | -3.3554 | 118.1076 | 118.0115 | 117.9565 | 0.064087 | 0.009155 | 117.9062 | -3.1265 | -3.2684 | 118.1488 | 118.1259 | 118.071 | 0.21973 | 0.16479 | 0.16022 | 0.009155 | 0.24261 | 0.13733 | 0.28381 | 0.27924 | 118.2312 | 118.1854 | -3.3646 | -3.4058 | 117.9565 | 118.0435 | 117.9703 | 118.0115
3520.6719 | 121.6141 | -121.4355 | 0.11902 | -0.0051118 | -0.013302 | -0.079651 | -0.0065517 | -0.030657 | -0.050808 | -0.042955 | -0.0021057 | 0.0033902 | 0.0087756 | -0.01462 | -0.21808 | -0.020478 | -0.022398 | -0.1236 | 0.09613 | -0.12817 | -0.13733 | 0.013733 | -0.13733 | -0.064087 | -0.036621 | 0.12817 | -0.13275 | -0.064087 | 0.064087 | 0.018311 | 0.022888 | 121.3074 | -0.022889 | -0.25635 | 121.4493 | 121.3715 | 121.2982 | 0.064087 | -0.009155 | 121.3028 | 0.009155 | -0.18311 | 121.4996 | 121.4584 | 121.4539 | 0.15564 | 0.15106 | 0.14191 | -0.009155 | 0.19684 | 0.068664 | 0.2243 | 0.26093 | 121.5317 | 121.5637 | -0.24719 | -0.25177 | 121.2982 | 121.3715 | 121.312 | 121.3989
3522.4531 | 121.8887 | -121.6049 | 0.086975 | 0.0025177 | -0.011166 | -0.080079 | -0.0078335 | -0.030016 | -0.048886 | -0.042528 | -0.0021057 | 0.0018948 | 0.0066394 | -0.011202 | -0.22172 | -0.018769 | -0.019621 | -0.064087 | 0.07782 | -0.091553 | -0.059509 | 0.14191 | -0.059509 | 0.004578 | 0.09613 | 0.10529 | -0.09613 | 0.059509 | 0.15564 | 0.086975 | 0.11902 | 121.5134 | -0.009155 | -0.14648 | 121.7468 | 121.6095 | 121.5454 | 0.096131 | 0.032044 | 121.5088 | 0.018311 | -0.027466 | 121.7606 | 121.7239 | 121.6919 | 0.21515 | 0.1831 | 0.23346 | 0.032044 | 0.25177 | 0.15564 | 0.16937 | 0.20142 | 121.6827 | 121.7102 | -0.17853 | -0.1831 | 121.5454 | 121.6644 | 121.5408 | 121.701
3524.25 | 121.8933 | -121.637 | 0.09613 | -0.012741 | -0.012448 | -0.079865 | -0.0078335 | -0.033648 | -0.05209 | -0.042742 | -0.0082091 | 0.0038174 | 0.0059986 | -0.01163 | -0.21894 | -0.019623 | -0.024107 | -0.10986 | 0.091553 | -0.10986 | -0.091553 | 0.054932 | -0.086975 | -0.009155 | 0.036621 | 0.10986 | -0.10529 | 0.036621 | 0.13733 | 0.086975 | 0.12817 | 121.5271 | -0.004577 | -0.18768 | 121.6919 | 121.6278 | 121.55 | 0.10071 | 0.022888 | 121.5317 | 0.013733 | -0.059509 | 121.7743 | 121.7651 | 121.7239 | 0.23346 | 0.19226 | 0.16479 | 0.01831 | 0.24262 | 0.14191 | 0.20142 | 0.21515 | 121.7285 | 121.7468 | -0.20599 | -0.20142 | 121.5454 | 121.6736 | 121.5271 | 121.6736
3525.9688 | 121.8704 | -121.7377 | 0.12817 | 0.0025177 | -0.014798 | -0.081788 | -0.0069791 | -0.028093 | -0.052304 | -0.041887 | -0.0082091 | 0.0055264 | 0.0092028 | -0.014193 | -0.21787 | -0.018769 | -0.024535 | -0.13275 | 0.11444 | -0.15564 | -0.14648 | -0.009155 | -0.15106 | -0.068665 | -0.041199 | 0.13733 | -0.14648 | -0.064087 | 0.032043 | 0 | 0.032043 | 121.582 | -0.013733 | -0.27466 | 121.7285 | 121.669 | 121.5866 | 0.086975 | 0.004578 | 121.5912 | 0.009155 | -0.19226 | 121.7697 | 121.7697 | 121.7377 | 0.17853 | 0.14648 | 0.14649 | 0.009156 | 0.17853 | 0.082397 | 0.27008 | 0.28381 | 121.8521 | 121.875 | -0.28381 | -0.27466 | 121.5912 | 121.6736 | 121.6049 | 121.6965
3527.75 | 121.5317 | -121.3486 | 0.11902 | 0.0025177 | -0.013516 | -0.079438 | -0.0065517 | -0.031084 | -0.05209 | -0.043169 | -0.0051575 | 0.0036038 | 0.0096302 | -0.01462 | -0.22043 | -0.018128 | -0.021971 | -0.082397 | 0.064087 | -0.10986 | -0.09613 | 0.054932 | -0.082397 | -0.022888 | -0.013733 | 0.13733 | -0.12817 | -0.027466 | 0.068665 | 0.018311 | 0.041199 | 121.2387 | -0.054932 | -0.21515 | 121.4035 | 121.3257 | 121.2662 | 0.086975 | 0.027466 | 121.2204 | 0.01831 | -0.14649 | 121.4172 | 121.3898 | 121.3669 | 0.16937 | 0.14649 | 0.16479 | 0.013733 | 0.19684 | 0.10071 | 0.17395 | 0.2655 | 121.4127 | 121.4859 | -0.22888 | -0.24719 | 121.2524 | 121.3211 | 121.2662 | 121.3348
3529.5469 | 121.7743 | -121.5775 | 0.10529 | -0.012741 | -0.013089 | -0.079865 | -0.0078335 | -0.030443 | -0.050595 | -0.039751 | -0.0051575 | 0.0036038 | 0.0072802 | -0.0077844 | -0.22172 | -0.01941 | -0.02603 | -0.068665 | 0.073242 | -0.091553 | -0.050354 | 0.10986 | -0.041199 | 0.018311 | 0.041199 | 0.10986 | -0.10986 | 0 | 0.11902 | 0.068665 | 0.086975 | 121.4859 | -0.032044 | -0.15564 | 121.6873 | 121.5958 | 121.5363 | 0.10986 | 0.050354 | 121.4676 | 0.004577 | -0.10529 | 121.6965 | 121.6644 | 121.6461 | 0.19684 | 0.17853 | 0.20142 | 0.041199 | 0.22888 | 0.10986 | 0.16479 | 0.21973 | 121.6507 | 121.6873 | -0.19684 | -0.21515 | 121.5271 | 121.5775 | 121.5088 | 121.6187
3531.3438 | 121.5042 | -121.4767 | 0.12817 | 0.0025177 | -0.014584 | -0.079224 | -0.0067653 | -0.031725 | -0.051663 | -0.043169 | 0.0039979 | 0.0014676 | 0.0059986 | -0.014407 | -0.21979 | -0.019196 | -0.020903 | -0.09613 | 0.09613 | -0.11444 | -0.11444 | 0.036621 | -0.10529 | -0.036621 | -0.018311 | 0.13275 | -0.1236 | -0.059509 | 0.073242 | 0.018311 | 0.041199 | 121.3623 | -0.032044 | -0.24262 | 121.5134 | 121.4401 | 121.3715 | 0.07782 | 0.009155 | 121.3531 | 0.004577 | -0.18768 | 121.55 | 121.5179 | 121.4951 | 0.16479 | 0.14191 | 0.15106 | 0 | 0.19684 | 0.064087 | 0.21057 | 0.25635 | 121.5729 | 121.6095 | -0.24262 | -0.25177 | 121.3623 | 121.4172 | 121.3806 | 121.4584
3533.125 | 121.6553 | -121.5546 | 0.12817 | -0.0051118 | -0.010739 | -0.079651 | -0.0044155 | -0.029375 | -0.050808 | -0.039965 | -0.0051575 | 0.006381 | 0.0059986 | -0.0099206 | -0.22193 | -0.018128 | -0.026244 | -0.07782 | 0.10529 | -0.13733 | -0.12817 | 0.022888 | -0.15564 | -0.07782 | -0.018311 | 0.14191 | -0.13275 | -0.027466 | 0.041199 | -0.032043 | 0.050354 | 121.4172 | -0.022888 | -0.25635 | 121.5775 | 121.4767 | 121.3989 | 0.059509 | -0.018311 | 121.4218 | 0.013733 | -0.15564 | 121.5958 | 121.6049 | 121.5225 | 0.18311 | 0.10071 | 0.16022 | 0.009155 | 0.17395 | 0.10529 | 0.24262 | 0.27466 | 121.6599 | 121.6965 | -0.2655 | -0.26093 | 121.4264 | 121.5271 | 121.4767 | 121.5363
3534.8594 | 121.6827 | -121.6232 | 0.12817 | -0.0051118 | -0.010098 | -0.07837 | -0.0035611 | -0.026171 | -0.050808 | -0.040392 | -0.0021057 | 0.0031766 | 0.0070666 | -0.007998 | -0.21937 | -0.017701 | -0.020903 | -0.09613 | 0.10529 | -0.12817 | -0.13733 | 0 | -0.16479 | -0.09613 | -0.041199 | 0.13275 | -0.12817 | -0.041199 | 0.036621 | -0.050354 | 0.041199 | 121.4951 | -0.022888 | -0.2655 | 121.6232 | 121.5271 | 121.4584 | 0.032044 | -0.036621 | 121.4951 | 0.004577 | -0.16937 | 121.6599 | 121.6644 | 121.5729 | 0.16937 | 0.07782 | 0.12817 | -0.009155 | 0.1648 | 0.086975 | 0.23346 | 0.26093 | 121.7285 | 121.756 | -0.25635 | -0.25635 | 121.4859 | 121.582 | 121.5271 | 121.582
3536.6562 | 121.8384 | -121.6095 | 0.11444 | -0.012741 | -0.012661 | -0.079651 | -0.0078335 | -0.029162 | -0.050595 | -0.037828 | -0.0021057 | 0.001254 | 0.005785 | -0.0073572 | -0.21872 | -0.018128 | -0.020689 | -0.07782 | 0.09613 | -0.09613 | -0.059509 | 0.11444 | -0.091553 | 0 | 0.068665 | 0.09613 | -0.10529 | 0.032043 | 0.14191 | 0.07782 | 0.11902 | 121.5134 | -0.018311 | -0.17395 | 121.7239 | 121.6095 | 121.5179 | 0.09613 | 0.004577 | 121.5042 | -0.018311 | -0.082398 | 121.7514 | 121.7285 | 121.6873 | 0.22431 | 0.18311 | 0.21057 | 0.036621 | 0.24719 | 0.13733 | 0.19226 | 0.20142 | 121.7056 | 121.7056 | -0.21057 | -0.21973 | 121.55 | 121.6415 | 121.5317 | 121.6782
3538.4531 | 121.843 | -121.6599 | 0.1236 | -0.0051118 | -0.0098843 | -0.079224 | -0.0031337 | -0.029375 | -0.051876 | -0.041674 | -0.0051575 | 0.0055264 | 0.005144 | -0.0054346 | -0.21787 | -0.018555 | -0.022185 | -0.086975 | 0.10071 | -0.14191 | -0.10986 | 0.064087 | -0.10986 | -0.041199 | 0.036621 | 0.12817 | -0.1236 | 0 | 0.11902 | 0.041199 | 0.09613 | 121.5179 | -0.022888 | -0.23346 | 121.7239 | 121.6187 | 121.55 | 0.10071 | 0.032044 | 121.5363 | 0.004578 | -0.1236 | 121.7789 | 121.756 | 121.7011 | 0.21973 | 0.16479 | 0.20599 | 0.032044 | 0.24261 | 0.1236 | 0.24262 | 0.25177 | 121.7606 | 121.788 | -0.2655 | -0.24719 | 121.55 | 121.6599 | 121.5729 | 121.6965
3540.2344 | 121.9345 | -121.6415 | 0.09613 | -0.0051118 | -0.014157 | -0.080079 | -0.0056973 | -0.032366 | -0.051663 | -0.043169 | 0.00094606 | 0.0027494 | 0.0081348 | -0.019747 | -0.21915 | -0.017487 | -0.024748 | -0.091553 | 0.09613 | -0.12817 | -0.07782 | 0.10529 | -0.068665 | 0.036621 | 0.059509 | 0.10071 | -0.11902 | 0.068665 | 0.20142 | 0.13733 | 0.15564 | 121.5134 | 0 | -0.17395 | 121.7468 | 121.6782 | 121.5729 | 0.1648 | 0.059509 | 121.5225 | 0.004578 | -0.027465 | 121.843 | 121.7972 | 121.7789 | 0.27466 | 0.25635 | 0.23346 | 0.050354 | 0.32044 | 0.18768 | 0.2243 | 0.21973 | 121.7377 | 121.7422 | -0.2243 | -0.21515 | 121.5637 | 121.7102 | 121.55 | 121.7011
3542.0469 | 121.8384 | -121.7056 | 0.14191 | -0.012741 | -0.01437 | -0.081574 | -0.0080471 | -0.031511 | -0.052731 | -0.041674 | -0.0021057 | 0.0040312 | 0.005785 | -0.0086388 | -0.2215 | -0.018555 | -0.022612 | -0.12817 | 0.12817 | -0.14648 | -0.16479 | 0.004578 | -0.14191 | -0.073242 | -0.036621 | 0.14191 | -0.13733 | -0.073242 | 0.054932 | 0 | 0.036621 | 121.5591 | -0.013733 | -0.3067 | 121.7102 | 121.6324 | 121.5637 | 0.073242 | 0.004577 | 121.5683 | 0 | -0.21515 | 121.7606 | 121.7422 | 121.7056 | 0.17395 | 0.13733 | 0.15106 | -0.018311 | 0.19226 | 0.064087 | 0.27466 | 0.27924 | 121.8338 | 121.8475 | -0.28839 | -0.27924 | 121.5408 | 121.6324 | 121.5775 | 121.669
3543.8438 | 121.9803 | -121.669 | 0.07782 | 0.0025177 | -0.0098843 | -0.079438 | -0.0074063 | -0.02788 | -0.049313 | -0.043169 | 0.00094606 | 0.0027494 | 0.0083484 | -0.00693 | -0.21894 | -0.018982 | -0.020476 | -0.045776 | 0.086975 | -0.10071 | -0.032043 | 0.13733 | -0.073242 | 0.009155 | 0.11902 | 0.091553 | -0.091553 | 0.07782 | 0.16937 | 0.1236 | 0.13275 | 121.5683 | 0.009155 | -0.10986 | 121.8063 | 121.6782 | 121.5958 | 0.10986 | 0.027466 | 121.5775 | 0.013733 | 0 | 121.8384 | 121.8018 | 121.7926 | 0.2243 | 0.21515 | 0.23804 | 0.068665 | 0.26093 | 0.16937 | 0.18768 | 0.18311 | 121.756 | 121.7606 | -0.17853 | -0.16937 | 121.637 | 121.7468 | 121.6232 | 121.788
3545.5781 | 121.9711 | -121.7285 | 0.09613 | 0.0025177 | -0.013302 | -0.079011 | -0.0061245 | -0.034289 | -0.053158 | -0.040605 | -0.0021057 | 0.0033902 | 0.0062122 | -0.013339 | -0.21851 | -0.018769 | -0.024535 | -0.09613 | 0.091553 | -0.091553 | -0.082397 | 0.086975 | -0.10071 | 0 | 0.050354 | 0.10529 | -0.10986 | 0.036621 | 0.12817 | 0.073242 | 0.11444 | 121.637 | -0.004577 | -0.17853 | 121.8155 | 121.7285 | 121.6278 | 0.091553 | -0.009155 | 121.6187 | 0.009156 | -0.059509 | 121.8567 | 121.843 | 121.8018 | 0.2243 | 0.18311 | 0.17853 | 0.009156 | 0.23804 | 0.14648 | 0.18311 | 0.21515 | 121.8201 | 121.8338 | -0.18768 | -0.20599 | 121.6461 | 121.7651 | 121.6324 | 121.7789
3547.375 | 121.9757 | -121.7422 | 0.10529 | 0.010147 | -0.013516 | -0.078797 | -0.0067653 | -0.032366 | -0.048031 | -0.041033 | 0.00094606 | 0.0038174 | 0.0072802 | -0.0082116 | -0.22107 | -0.018342 | -0.021758 | -0.054932 | 0.086975 | -0.10986 | -0.045776 | 0.11902 | -0.082397 | 0.004578 | 0.10986 | 0.11444 | -0.07782 | 0.041199 | 0.14191 | 0.082397 | 0.11902 | 121.6324 | -0.018311 | -0.15106 | 121.8613 | 121.7468 | 121.6599 | 0.11444 | 0.027466 | 121.6644 | 0.009155 | -0.064087 | 121.8842 | 121.8613 | 121.8246 | 0.19684 | 0.16022 | 0.22888 | 0.064087 | 0.21973 | 0.11902 | 0.19684 | 0.19226 | 121.8292 | 121.8567 | -0.21515 | -0.18311 | 121.6965 | 121.7834 | 121.6873 | 121.8521
3549.0938 | 121.9208 | -121.7834 | 0.11902 | 0.010147 | -0.0090299 | -0.079011 | -0.0033475 | -0.030871 | -0.049099 | -0.042314 | 0.00094606 | 0.00574 | 0.0094166 | -0.014407 | -0.22257 | -0.017914 | -0.023253 | -0.11902 | 0.10071 | -0.13733 | -0.13275 | -0.045776 | -0.20142 | -0.09613 | -0.064087 | 0.14191 | -0.11902 | -0.041199 | 0.013733 | -0.041199 | 0.036621 | 121.6461 | -0.018311 | -0.25177 | 121.7377 | 121.6873 | 121.582 | 0.041199 | -0.064087 | 121.6644 | 0.022888 | -0.16022 | 121.7972 | 121.8201 | 121.7422 | 0.15564 | 0.07782 | 0.091553 | 0.004578 | 0.13275 | 0.07782 | 0.23804 | 0.26093 | 121.8842 | 121.9254 | -0.25635 | -0.23804 | 121.6507 | 121.7422 | 121.6644 | 121.7194
3550.8906 | 122.0123 | -121.7514 | 0.086975 | -0.0051118 | -0.010739 | -0.079011 | -0.0091153 | -0.032366 | -0.049526 | -0.040392 | -0.0021057 | 0.001254 | 0.0070666 | -0.019534 | -0.22129 | -0.017487 | -0.022612 | -0.086975 | 0.073242 | -0.10529 | -0.059509 | 0.11444 | -0.07782 | 0.004578 | 0.082397 | 0.10071 | -0.11444 | 0.054932 | 0.13733 | 0.082397 | 0.10986 | 121.6461 | -0.013733 | -0.14648 | 121.8658 | 121.756 | 121.6736 | 0.10986 | 0.027466 | 121.637 | 0.013733 | -0.032043 | 121.8887 | 121.8613 | 121.8338 | 0.2243 | 0.19684 | 0.21973 | 0.045777 | 0.25177 | 0.16937 | 0.17853 | 0.21515 | 121.8246 | 121.8521 | -0.19226 | -0.20142 | 121.6919 | 121.8063 | 121.6644 | 121.8338
3552.6406 | 121.9437 | -121.8018 | 0.11444 | -0.0051118 | -0.0094571 | -0.078583 | -0.0029201 | -0.033434 | -0.049313 | -0.039965 | -0.0021057 | 0.00574 | 0.0070666 | -0.006289 | -0.21937 | -0.018555 | -0.020689 | -0.12817 | 0.12817 | -0.14191 | -0.17395 | -0.059509 | -0.2243 | -0.13275 | -0.068665 | 0.11902 | -0.13733 | -0.036621 | 0.013733 | -0.050354 | 0.050354 | 121.6599 | 0.013733 | -0.28839 | 121.7422 | 121.669 | 121.5775 | 0.009156 | -0.082397 | 121.6644 | 0.004578 | -0.15106 | 121.8155 | 121.8521 | 121.7514 | 0.18768 | 0.086975 | 0.082398 | -0.032043 | 0.15106 | 0.10071 | 0.27008 | 0.25635 | 121.9299 | 121.9208 | -0.25635 | -0.25177 | 121.6278 | 121.7651 | 121.6736 | 121.7331
3554.4375 | 121.9849 | -121.7926 | 0.1236 | -0.0051118 | -0.0079617 | -0.077515 | -0.0042019 | -0.028093 | -0.048672 | -0.04146 | -0.0051575 | 0.0040312 | 0.007494 | -0.010989 | -0.21894 | -0.01706 | -0.023253 | -0.086975 | 0.12817 | -0.15106 | -0.11444 | 0.041199 | -0.13733 | -0.059509 | 0.022888 | 0.11902 | -0.10986 | -0.004578 | 0.068665 | -0.009155 | 0.068665 | 121.6415 | 0.004578 | -0.23804 | 121.8338 | 121.7331 | 121.6553 | 0.091553 | 0.013733 | 121.6827 | -0.004577 | -0.12817 | 121.8613 | 121.8613 | 121.7834 | 0.17853 | 0.10071 | 0.19226 | 0.036621 | 0.17853 | 0.10529 | 0.27924 | 0.22888 | 121.9208 | 121.9116 | -0.27466 | -0.23346 | 121.6782 | 121.788 | 121.7056 | 121.8155
3556.1719 | 122.0306 | -121.8201 | 0.10071 | 0.0025177 | -0.013302 | -0.079438 | -0.0082607 | -0.031084 | -0.047604 | -0.042955 | -0.0051575 | 0.0010404 | 0.008562 | -0.01932 | -0.21979 | -0.018555 | -0.020903 | -0.10986 | 0.09613 | -0.10529 | -0.082397 | 0.068665 | -0.10529 | -0.004578 | 0.036621 | 0.11902 | -0.11444 | 0.032043 | 0.12817 | 0.064087 | 0.11444 | 121.7148 | -0.004578 | -0.18311 | 121.8887 | 121.8155 | 121.7148 | 0.10071 | 0 | 121.7056 | 0.018311 | -0.068665 | 121.9482 | 121.9345 | 121.8842 | 0.22888 | 0.17853 | 0.17395 | 0.022889 | 0.24262 | 0.14648 | 0.20142 | 0.23346 | 121.9162 | 121.9391 | -0.20599 | -0.21515 | 121.7377 | 121.8521 | 121.7102 | 121.8567
3557.9531 | 121.9849 | -121.8475 | 0.10986 | -0.0051118 | -0.011166 | -0.080506 | -0.0027065 | -0.028734 | -0.048672 | -0.040178 | -0.0021057 | 0.0031766 | 0.010271 | -0.012911 | -0.21958 | -0.017273 | -0.024535 | -0.11902 | 0.11444 | -0.14191 | -0.16937 | -0.036621 | -0.20142 | -0.10529 | -0.050354 | 0.14191 | -0.12817 | -0.032043 | 0.032043 | -0.036621 | 0.054932 | 121.7056 | 0.004578 | -0.27924 | 121.8109 | 121.7422 | 121.6461 | 0.036621 | -0.059509 | 121.7194 | 0.032044 | -0.14191 | 121.8796 | 121.9025 | 121.8109 | 0.18311 | 0.091553 | 0.10529 | -0.027466 | 0.16022 | 0.096131 | 0.25635 | 0.27008 | 121.962 | 121.9894 | -0.25177 | -0.23804 | 121.6782 | 121.8155 | 121.7285 | 121.7972
3559.75 | 122.1085 | -121.8292 | 0.091553 | -0.0051118 | -0.0096707 | -0.076874 | -0.0065517 | -0.030443 | -0.047177 | -0.042528 | -0.0021057 | 0.0010404 | 0.0066394 | -0.013552 | -0.22086 | -0.017914 | -0.027098 | -0.054932 | 0.086975 | -0.091553 | -0.045776 | 0.13733 | -0.073242 | 0.032043 | 0.1236 | 0.10071 | -0.10071 | 0.091553 | 0.16937 | 0.11444 | 0.14191 | 121.7377 | -0.004578 | -0.13733 | 121.9666 | 121.8613 | 121.756 | 0.1236 | 0.018311 | 121.7285 | 0.009155 | 0 | 121.9986 | 121.9711 | 121.9437 | 0.24262 | 0.21515 | 0.22888 | 0.045777 | 0.27008 | 0.19226 | 0.17853 | 0.20142 | 121.9162 | 121.9299 | -0.18311 | -0.19226 | 121.7834 | 121.9208 | 121.7743 | 121.9528
3561.4844 | 122.1039 | -121.8338 | 0.091553 | -0.0051118 | -0.010311 | -0.080719 | -0.0031337 | -0.030657 | -0.049313 | -0.040819 | 0.00094606 | 0.0055264 | 0.0064258 | -0.012698 | -0.22065 | -0.018769 | -0.022185 | -0.13275 | 0.12817 | -0.15564 | -0.12817 | 0.013733 | -0.15564 | -0.064087 | 0.013733 | 0.11902 | -0.13733 | 0.045776 | 0.1236 | 0.064087 | 0.12817 | 121.6782 | 0.036621 | -0.21973 | 121.8475 | 121.7697 | 121.6782 | 0.091553 | 0 | 121.6965 | 0.027466 | -0.045777 | 121.9574 | 121.962 | 121.8979 | 0.2655 | 0.20142 | 0.16937 | 0.027466 | 0.26093 | 0.18311 | 0.28381 | 0.25635 | 121.962 | 121.9528 | -0.24719 | -0.22888 | 121.7056 | 121.8796 | 121.701 | 121.8475
3563.2656 | 122.0169 | -121.8796 | 0.14191 | -0.0051118 | -0.015438 | -0.079224 | -0.0063381 | -0.031298 | -0.05209 | -0.041887 | 0.00094606 | 0.0031766 | 0.007494 | -0.019961 | -0.22043 | -0.018769 | -0.022612 | -0.14648 | 0.11902 | -0.13733 | -0.19226 | -0.009155 | -0.14648 | -0.054932 | -0.054932 | 0.14648 | -0.15106 | -0.064087 | 0.050354 | -0.004578 | 0.045776 | 121.7422 | -0.022888 | -0.33417 | 121.8704 | 121.8246 | 121.7331 | 0.082397 | -0.009155 | 121.7285 | 0.004577 | -0.20599 | 121.9299 | 121.9254 | 121.875 | 0.19684 | 0.14648 | 0.12817 | -0.054932 | 0.20142 | 0.086975 | 0.25635 | 0.29755 | 121.9986 | 122.0261 | -0.27924 | -0.29297 | 121.6873 | 121.8155 | 121.7331 | 121.8246
3565.0625 | 122.1085 | -121.875 | 0.086975 | 0.0025177 | -0.012448 | -0.077729 | -0.0080471 | -0.034075 | -0.048245 | -0.040392 | -0.0051575 | 0.002963 | 0.0081348 | -0.016757 | -0.21808 | -0.020264 | -0.020476 | -0.09613 | 0.073242 | -0.086975 | -0.091553 | 0.082397 | -0.09613 | -0.013733 | 0.054932 | 0.091553 | -0.11444 | 0.036621 | 0.13275 | 0.07782 | 0.10529 | 121.788 | -0.013733 | -0.17853 | 121.9574 | 121.8613 | 121.7789 | 0.073242 | -0.009155 | 121.7606 | 0.004578 | -0.050354 | 122.0078 | 121.9803 | 121.9528 | 0.21973 | 0.19226 | 0.16937 | -0.004578 | 0.24719 | 0.15106 | 0.16022 | 0.20599 | 121.9482 | 121.9666 | -0.17395 | -0.20142 | 121.7834 | 121.9116 | 121.7789 | 121.9299
3566.875 | 122.168 | -121.843 | 0.07782 | -0.0051118 | -0.01138 | -0.076661 | -0.0080471 | -0.028948 | -0.050167 | -0.039965 | -0.0051575 | 0.0036038 | 0.0087756 | -0.012698 | -0.22065 | -0.01941 | -0.026244 | -0.059509 | 0.068665 | -0.09613 | -0.036621 | 0.12817 | -0.064087 | 0.027466 | 0.1236 | 0.10529 | -0.09613 | 0.086975 | 0.17395 | 0.10986 | 0.15106 | 121.7468 | -0.009155 | -0.11444 | 121.9711 | 121.8704 | 121.7789 | 0.1236 | 0.032043 | 121.7468 | 0.027466 | 0.009155 | 122.0169 | 121.994 | 121.9528 | 0.24719 | 0.20599 | 0.2243 | 0.059509 | 0.27008 | 0.1831 | 0.16479 | 0.20142 | 121.9116 | 121.9482 | -0.17395 | -0.17395 | 121.8063 | 121.9299 | 121.7834 | 121.9666
3568.6094 | 122.0398 | -121.9299 | 0.11902 | 0.0025177 | -0.013943 | -0.077942 | -0.0042019 | -0.031084 | -0.052517 | -0.042955 | -0.0051575 | 0.0044584 | 0.0083484 | -0.016116 | -0.22086 | -0.017487 | -0.025176 | -0.14191 | 0.11444 | -0.14191 | -0.15564 | -0.009155 | -0.15564 | -0.073242 | -0.054932 | 0.14191 | -0.14648 | -0.068665 | 0.045776 | 0 | 0.045776 | 121.788 | -0.004578 | -0.27466 | 121.9208 | 121.8567 | 121.7743 | 0.068665 | -0.013733 | 121.7834 | 0.022888 | -0.18768 | 121.9757 | 121.9757 | 121.9299 | 0.19226 | 0.14648 | 0.13275 | -0.013733 | 0.19226 | 0.077819 | 0.25635 | 0.28839 | 122.0444 | 122.0718 | -0.26093 | -0.2655 | 121.7743 | 121.8613 | 121.788 | 121.875
3570.3906 | 122.2046 | -121.8887 | 0.091553 | -0.0051118 | -0.015438 | -0.07837 | -0.0082607 | -0.03258 | -0.048886 | -0.041033 | -0.0021057 | 0.0018948 | 0.0049304 | -0.020175 | -0.22129 | -0.020691 | -0.019835 | -0.073242 | 0.073242 | -0.10529 | -0.032043 | 0.16479 | -0.004578 | 0.054932 | 0.12817 | 0.10071 | -0.11444 | 0.091553 | 0.21515 | 0.15106 | 0.16937 | 121.7834 | -0.018311 | -0.1236 | 122.0535 | 121.9437 | 121.8842 | 0.16022 | 0.10071 | 121.7743 | 0.009155 | 0 | 122.1039 | 122.0581 | 122.0398 | 0.28381 | 0.2655 | 0.27008 | 0.073243 | 0.32959 | 0.20599 | 0.17853 | 0.21515 | 121.962 | 121.9894 | -0.19684 | -0.20599 | 121.8567 | 121.9803 | 121.8155 | 122.0169
3572.1719 | 122.1909 | -121.8933 | 0.07782 | -0.0051118 | -0.011593 | -0.07837 | -0.0054837 | -0.027025 | -0.050595 | -0.041887 | -0.0021057 | 0.0018948 | 0.0053576 | -0.010561 | -0.21872 | -0.017701 | -0.027098 | -0.050354 | 0.07782 | -0.10529 | -0.045776 | 0.10071 | -0.073242 | 0.018311 | 0.10529 | 0.091553 | -0.09613 | 0.10986 | 0.17853 | 0.10529 | 0.1831 | 121.788 | 0 | -0.1236 | 121.994 | 121.9116 | 121.8201 | 0.1236 | 0.032044 | 121.7972 | 0.013733 | 0.032043 | 122.0718 | 122.0764 | 121.9986 | 0.27924 | 0.20142 | 0.20599 | 0.05951 | 0.27466 | 0.20599 | 0.18311 | 0.18768 | 121.9711 | 121.9849 | -0.18311 | -0.17395 | 121.8475 | 122.0032 | 121.843 | 121.9986
3573.8906 | 122.2275 | -121.8933 | 0.11444 | 0.0025177 | -0.015225 | -0.080933 | -0.0063381 | -0.031939 | -0.050595 | -0.040605 | -0.0021057 | 0.0018948 | 0.0066394 | -0.016543 | -0.22043 | -0.018769 | -0.027312 | -0.064087 | 0.073242 | -0.091553 | -0.009155 | 0.16022 | -0.032043 | 0.054932 | 0.13733 | 0.10071 | -0.10071 | 0.091553 | 0.19684 | 0.14648 | 0.15564 | 121.8018 | -0.041199 | -0.1236 | 122.0535 | 121.9482 | 121.8613 | 0.14649 | 0.05951 | 121.7926 | -0.013733 | -0.022888 | 122.0901 | 122.049 | 122.0398 | 0.25635 | 0.24719 | 0.25177 | 0.082398 | 0.29755 | 0.19226 | 0.16479 | 0.20142 | 121.9666 | 121.994 | -0.20599 | -0.21515 | 121.8842 | 121.9849 | 121.8292 | 122.0306
3575.6875 | 122.2046 | -121.9391 | 0.10071 | 0.010147 | -0.014584 | -0.082428 | -0.0074063 | -0.030657 | -0.051449 | -0.042528 | -0.0021057 | 0.0014676 | 0.0053576 | -0.0099206 | -0.22043 | -0.020478 | -0.02133 | -0.059509 | 0.086975 | -0.091553 | -0.018311 | 0.13275 | -0.022888 | 0.050354 | 0.10529 | 0.091553 | -0.10071 | 0.07782 | 0.19684 | 0.14191 | 0.14191 | 121.8475 | -0.013733 | -0.11902 | 122.0718 | 121.9894 | 121.9162 | 0.14191 | 0.068665 | 121.8384 | -0.009155 | -0.022888 | 122.1359 | 122.081 | 122.081 | 0.24262 | 0.24262 | 0.2243 | 0.073242 | 0.29755 | 0.17853 | 0.17853 | 0.19226 | 122.0261 | 122.0306 | -0.19226 | -0.20142 | 121.9208 | 122.0169 | 121.8796 | 122.0444
3577.4844 | 122.1451 | -121.9299 | 0.10986 | 0.0025177 | -0.010525 | -0.079438 | -0.0046291 | -0.029589 | -0.047604 | -0.040392 | 0.00094606 | 0.0038174 | 0.0077076 | -0.012484 | -0.21851 | -0.016633 | -0.023467 | -0.07782 | 0.10986 | -0.11902 | -0.10529 | 0.036621 | -0.1236 | -0.045776 | 0.036621 | 0.12817 | -0.1236 | 0.022888 | 0.091553 | 0.018311 | 0.054932 | 121.8109 | 0 | -0.21515 | 121.9666 | 121.8842 | 121.8063 | 0.073243 | -0.004577 | 121.8063 | 0.018311 | -0.086975 | 122.0215 | 121.9849 | 121.9482 | 0.17853 | 0.14191 | 0.15564 | 0.013733 | 0.21515 | 0.14648 | 0.22888 | 0.25177 | 122.0398 | 122.0581 | -0.22888 | -0.23346 | 121.8246 | 121.9528 | 121.8521 | 121.9666
3579.2656 | 122.1542 | -121.9528 | 0.12817 | 0.0025177 | -0.011593 | -0.080292 | -0.0052701 | -0.030657 | -0.054013 | -0.038683 | 0.00094606 | 0.0053128 | 0.0089892 | -0.014193 | -0.21937 | -0.018128 | -0.022398 | -0.068665 | 0.10071 | -0.14191 | -0.10529 | 0.054932 | -0.10986 | -0.041199 | 0.041199 | 0.13733 | -0.13275 | 0.018311 | 0.09613 | 0.036621 | 0.09613 | 121.8109 | -0.027466 | -0.23346 | 122.0078 | 121.9116 | 121.843 | 0.10071 | 0.032044 | 121.8201 | 0.009155 | -0.10986 | 122.049 | 122.049 | 121.9894 | 0.22888 | 0.16937 | 0.19684 | 0.036621 | 0.22888 | 0.15106 | 0.24262 | 0.27008 | 122.0535 | 122.0901 | -0.27008 | -0.26093 | 121.8475 | 121.9711 | 121.8842 | 121.994
3580.9844 | 122.1222 | -121.994 | 0.10529 | -0.012741 | -0.013729 | -0.080292 | -0.0069791 | -0.034502 | -0.052944 | -0.043169 | 0.00094606 | 0.0048856 | 0.0096302 | -0.018038 | -0.21787 | -0.017273 | -0.027525 | -0.15106 | 0.1236 | -0.16937 | -0.1831 | -0.022888 | -0.14648 | -0.068665 | -0.068665 | 0.15106 | -0.13733 | -0.045776 | 0.045776 | -0.004578 | 0.036621 | 121.8246 | 0.01831 | -0.28839 | 121.9711 | 121.9254 | 121.8475 | 0.10071 | 0.022889 | 121.8567 | 0.045776 | -0.15106 | 122.0398 | 122.0306 | 121.9894 | 0.17395 | 0.13275 | 0.14649 | -0.013732 | 0.18311 | 0.091553 | 0.29297 | 0.28839 | 122.1176 | 122.1451 | -0.27466 | -0.24262 | 121.8109 | 121.9482 | 121.843 | 121.9254
3582.7812 | 122.2366 | -121.9528 | 0.09613 | -0.0051118 | -0.0098843 | -0.079011 | -0.0048427 | -0.02788 | -0.049099 | -0.043169 | -0.0021057 | 0.002963 | 0.007494 | -0.0071436 | -0.22001 | -0.017701 | -0.023894 | -0.10071 | 0.091553 | -0.10986 | -0.11444 | 0.050354 | -0.12817 | -0.036621 | 0.07782 | 0.10529 | -0.10986 | 0.068665 | 0.15564 | 0.091553 | 0.13733 | 121.843 | -0.004577 | -0.21057 | 122.0032 | 121.9162 | 121.8246 | 0.073242 | -0.018311 | 121.843 | 0.009156 | -0.027465 | 122.1085 | 122.0901 | 122.0444 | 0.24719 | 0.20142 | 0.16022 | -0.004578 | 0.2655 | 0.17853 | 0.20142 | 0.21515 | 122.0444 | 122.0581 | -0.20599 | -0.20599 | 121.8384 | 122.0215 | 121.8521 | 122.0306
3584.5781 | 122.2366 | -121.9757 | 0.091553 | -0.0051118 | -0.010098 | -0.076661 | -0.0061245 | -0.031511 | -0.049313 | -0.040605 | -0.0051575 | 0.00082679 | 0.0070666 | -0.013979 | -0.21937 | -0.017273 | -0.024962 | -0.045776 | 0.068665 | -0.09613 | -0.022888 | 0.13275 | -0.07782 | 0.013733 | 0.11902 | 0.10529 | -0.10529 | 0.07782 | 0.16937 | 0.10071 | 0.14648 | 121.8796 | -0.022888 | -0.11444 | 122.1085 | 121.9894 | 121.8979 | 0.10986 | 0.01831 | 121.8704 | 0.013733 | -0.013733 | 122.1451 | 122.1222 | 122.0764 | 0.25177 | 0.20599 | 0.22888 | 0.073242 | 0.27466 | 0.18311 | 0.16479 | 0.21057 | 122.0444 | 122.081 | -0.18768 | -0.19684 | 121.9528 | 122.0535 | 121.9299 | 122.0947
3586.2969 | 122.2687 | -121.9574 | 0.086975 | -0.012741 | -0.013302 | -0.082856 | -0.0086879 | -0.029375 | -0.047604 | -0.040819 | 0.00094606 | 0.0031766 | 0.0087756 | -0.010134 | -0.22022 | -0.020478 | -0.022612 | -0.086975 | 0.09613 | -0.10986 | -0.059509 | 0.09613 | -0.054932 | 0.022888 | 0.091553 | 0.09613 | -0.091553 | 0.054932 | 0.16937 | 0.14191 | 0.13275 | 121.8475 | 0.009155 | -0.14648 | 122.0535 | 121.9803 | 121.9025 | 0.13275 | 0.054931 | 121.8658 | 0.009155 | -0.032043 | 122.1268 | 122.0901 | 122.0993 | 0.2243 | 0.23346 | 0.20599 | 0.050354 | 0.26093 | 0.14649 | 0.20599 | 0.18768 | 122.0535 | 122.0535 | -0.19684 | -0.17853 | 121.8979 | 122.0123 | 121.8704 | 122.049
3588.0781 | 122.2275 | -121.9666 | 0.082397 | 0.0025177 | -0.012875 | -0.079011 | -0.0056973 | -0.033007 | -0.051663 | -0.041246 | -0.0021057 | 0.0014676 | 0.0066394 | -0.016543 | -0.22065 | -0.018555 | -0.022826 | -0.082397 | 0.07782 | -0.09613 | -0.073242 | 0.064087 | -0.091553 | -0.004578 | 0.045776 | 0.10071 | -0.091553 | 0.022888 | 0.1236 | 0.068665 | 0.10986 | 121.8704 | -0.004577 | -0.15564 | 122.0306 | 121.962 | 121.875 | 0.091552 | 0.004577 | 121.875 | 0.018311 | -0.059509 | 122.0901 | 122.0764 | 122.0352 | 0.20142 | 0.16022 | 0.16022 | 0.022888 | 0.21515 | 0.11444 | 0.17395 | 0.19226 | 122.0444 | 122.0673 | -0.17853 | -0.17395 | 121.8933 | 121.9894 | 121.8842 | 122.0123
3589.875 | 122.2549 | -121.9894 | 0.09613 | 0.010147 | -0.016507 | -0.079224 | -0.0074063 | -0.036852 | -0.051449 | -0.040178 | -0.0021057 | 0.0021084 | 0.0062122 | -0.016116 | -0.21958 | -0.01941 | -0.02368 | -0.068665 | 0.09613 | -0.10986 | -0.032043 | 0.13275 | -0.022888 | 0.036621 | 0.07782 | 0.11444 | -0.10986 | 0.059509 | 0.16479 | 0.1236 | 0.13733 | 121.8796 | 0 | -0.12817 | 122.1222 | 122.0261 | 121.9666 | 0.14648 | 0.086975 | 121.8796 | 0.018311 | -0.036621 | 122.1542 | 122.1268 | 122.113 | 0.24719 | 0.23346 | 0.24261 | 0.07782 | 0.27466 | 0.16937 | 0.20599 | 0.2243 | 122.0856 | 122.1039 | -0.20599 | -0.20599 | 121.9574 | 122.049 | 121.9208 | 122.0673
3591.625 | 122.2229 | -121.994 | 0.091553 | -0.0051118 | -0.013943 | -0.079224 | -0.0076199 | -0.029162 | -0.051663 | -0.040819 | -0.0051575 | 0.0014676 | 0.0064258 | -0.014834 | -0.22214 | -0.017273 | -0.021544 | -0.10529 | 0.10071 | -0.11902 | -0.091553 | 0.054932 | -0.11902 | -0.004578 | 0.027466 | 0.10071 | -0.10986 | 0.018311 | 0.1236 | 0.054932 | 0.09613 | 121.875 | 0.009155 | -0.18311 | 122.049 | 121.9894 | 121.875 | 0.11444 | 0 | 121.8842 | 0.009155 | -0.073242 | 122.1176 | 122.0901 | 122.049 | 0.20599 | 0.16479 | 0.17395 | 0.027466 | 0.23346 | 0.12817 | 0.21973 | 0.21057 | 122.0947 | 122.0947 | -0.21057 | -0.20142 | 121.9025 | 122.0123 | 121.8887 | 122.0215
3593.4219 | 122.3007 | -121.9803 | 0.091553 | -0.012741 | -0.0088163 | -0.077729 | -0.0046291 | -0.029375 | -0.051235 | -0.040819 | 0.0039979 | 0.0038174 | 0.0059986 | -0.012911 | -0.22065 | -0.018769 | -0.027098 | -0.032043 | 0.082397 | -0.10071 | -0.032043 | 0.11902 | -0.054932 | 0.013733 | 0.13275 | 0.091553 | -0.091553 | 0.10071 | 0.16937 | 0.10986 | 0.15564 | 121.8796 | -0.009156 | -0.1236 | 122.0993 | 121.994 | 121.9254 | 0.11444 | 0.045776 | 121.8887 | 0 | 0.009155 | 122.1497 | 122.1359 | 122.0901 | 0.24719 | 0.20142 | 0.21973 | 0.068665 | 0.26093 | 0.19226 | 0.18311 | 0.18311 | 122.0627 | 122.0718 | -0.19226 | -0.18311 | 121.9482 | 122.081 | 121.9482 | 122.113
3595.2031 | 122.3099 | -121.9986 | 0.086975 | -0.0051118 | -0.014584 | -0.079651 | -0.0061245 | -0.025957 | -0.051022 | -0.039324 | -0.0021057 | 0.0036038 | 0.0072802 | -0.01163 | -0.21979 | -0.021332 | -0.021971 | -0.07782 | 0.07782 | -0.10071 | -0.036621 | 0.11902 | -0.036621 | 0.041199 | 0.11902 | 0.10529 | -0.10071 | 0.07782 | 0.19684 | 0.12817 | 0.14191 | 121.8979 | -0.009155 | -0.1236 | 122.1176 | 122.0398 | 121.962 | 0.14191 | 0.064087 | 121.8979 | 0.018311 | -0.009155 | 122.1954 | 122.1405 | 122.1268 | 0.24262 | 0.22888 | 0.21973 | 0.064087 | 0.29755 | 0.17853 | 0.17853 | 0.20599 | 122.0764 | 122.1039 | -0.18768 | -0.18768 | 121.962 | 122.0764 | 121.9208 | 122.1176
3597.0156 | 122.2 | -122.0398 | 0.10529 | -0.012741 | -0.015652 | -0.080933 | -0.0056973 | -0.03258 | -0.051235 | -0.041246 | -0.0051575 | 0.0036038 | 0.0059986 | -0.0084252 | -0.22172 | -0.019837 | -0.023467 | -0.11444 | 0.1236 | -0.14648 | -0.16479 | -0.032043 | -0.15564 | -0.082397 | -0.050354 | 0.12817 | -0.1236 | -0.032043 | 0.068665 | -0.004578 | 0.050354 | 121.8933 | 0.01831 | -0.27008 | 122.0078 | 121.9574 | 121.8842 | 0.064087 | -0.009156 | 121.9162 | 0.022888 | -0.13733 | 122.1085 | 122.0901 | 122.0352 | 0.17395 | 0.11902 | 0.11444 | -0.018311 | 0.19226 | 0.091553 | 0.27008 | 0.25177 | 122.1634 | 122.168 | -0.25177 | -0.22888 | 121.875 | 122.0078 | 121.9254 | 121.9894
3598.75 | 122.2275 | -122.0398 | 0.11902 | 0.0025177 | -0.010098 | -0.080079 | -0.0065517 | -0.030871 | -0.052304 | -0.040392 | 0.00094606 | 0.004672 | 0.006853 | -0.0088526 | -0.22214 | -0.016633 | -0.02603 | -0.086975 | 0.1236 | -0.15564 | -0.11902 | 0.022888 | -0.1236 | -0.050354 | 0.018311 | 0.11902 | -0.12817 | 0.018311 | 0.10529 | 0.036621 | 0.09613 | 121.8842 | 0.004577 | -0.23804 | 122.0627 | 121.9894 | 121.9162 | 0.10529 | 0.032044 | 121.9116 | 0 | -0.10071 | 122.1451 | 122.1359 | 122.0764 | 0.2243 | 0.1648 | 0.17853 | 0.036621 | 0.23346 | 0.14649 | 0.27924 | 0.24719 | 122.1634 | 122.1588 | -0.27466 | -0.24719 | 121.9208 | 122.0581 | 121.9528 | 122.0581
3600.5469 | 122.1909 | -122.0581 | 0.1236 | -0.0051118 | -0.015652 | -0.078583 | -0.0069791 | -0.031511 | -0.051022 | -0.042528 | -0.0021057 | 0.0042448 | 0.008562 | -0.01227 | -0.21766 | -0.020051 | -0.02133 | -0.11444 | 0.11444 | -0.14191 | -0.14648 | 0.009155 | -0.13275 | -0.054932 | -0.032043 | 0.12817 | -0.14648 | -0.050354 | 0.064087 | -0.009155 | 0.022888 | 121.9162 | -0.009155 | -0.27008 | 122.0673 | 122.0032 | 121.9254 | 0.086975 | 0.009156 | 121.9116 | 0.004578 | -0.17395 | 122.1222 | 122.081 | 122.0489 | 0.16937 | 0.13733 | 0.15106 | -0.004577 | 0.21057 | 0.09613 | 0.25635 | 0.27466 | 122.1725 | 122.1863 | -0.2655 | -0.27008 | 121.9116 | 122.0078 | 121.9437 | 122.0261
3602.3438 | 122.2458 | -122.0535 | 0.11902 | -0.0051118 | -0.014157 | -0.077729 | -0.0035611 | -0.033861 | -0.051663 | -0.043169 | -0.0021057 | 0.0053128 | 0.0081348 | -0.012057 | -0.22022 | -0.017701 | -0.024748 | -0.11444 | 0.11444 | -0.1236 | -0.16479 | -0.018311 | -0.17395 | -0.09613 | -0.013733 | 0.13275 | -0.1236 | 0.009155 | 0.086975 | 0.018311 | 0.082397 | 121.9299 | -0.004578 | -0.28381 | 122.0352 | 121.9574 | 121.8796 | 0.027466 | -0.050354 | 121.9299 | 0.013732 | -0.10986 | 122.1405 | 122.1359 | 122.0718 | 0.20599 | 0.14191 | 0.10528 | -0.041199 | 0.21057 | 0.13275 | 0.23804 | 0.25635 | 122.168 | 122.1863 | -0.24261 | -0.24261 | 121.8887 | 122.0627 | 121.9391 | 122.0398
3604.0625 | 122.2504 | -122.0627 | 0.11444 | -0.012741 | -0.015225 | -0.080079 | -0.0048427 | -0.028948 | -0.051022 | -0.041033 | -0.0051575 | 0.0027494 | 0.0081348 | -0.013979 | -0.22172 | -0.017273 | -0.022612 | -0.091553 | 0.10529 | -0.14648 | -0.10529 | 0.009155 | -0.11444 | -0.045776 | 0.018311 | 0.13275 | -0.12817 | 0.009155 | 0.11444 | 0.036621 | 0.086975 | 121.9162 | -0.009155 | -0.21973 | 122.0718 | 122.0169 | 121.9482 | 0.10071 | 0.032043 | 121.9345 | 0.01831 | -0.10529 | 122.1771 | 122.1497 | 122.0993 | 0.21515 | 0.1648 | 0.15564 | 0.041198 | 0.24262 | 0.13733 | 0.25177 | 0.26093 | 122.168 | 122.1954 | -0.26093 | -0.24262 | 121.9574 | 122.0718 | 121.9711 | 122.081
3605.8594 | 122.2595 | -122.0627 | 0.12817 | 0.010147 | -0.011807 | -0.080719 | -0.0067653 | -0.028948 | -0.050808 | -0.041887 | -0.0051575 | 0.0038174 | 0.006853 | -0.011843 | -0.21915 | -0.016846 | -0.021971 | -0.1236 | 0.11902 | -0.14191 | -0.16022 | -0.013733 | -0.14191 | -0.068665 | -0.045776 | 0.13733 | -0.13275 | -0.027466 | 0.086975 | 0.022888 | 0.07782 | 121.9208 | -0.009155 | -0.28839 | 122.049 | 121.994 | 121.9208 | 0.073242 | 0 | 121.9299 | 0.009155 | -0.15564 | 122.1497 | 122.1405 | 122.0856 | 0.21057 | 0.15564 | 0.12817 | -0.01831 | 0.21973 | 0.10529 | 0.26093 | 0.27008 | 122.1817 | 122.2 | -0.27008 | -0.26093 | 121.9025 | 122.0352 | 121.9391 | 122.0169
3607.5938 | 122.2366 | -122.0856 | 0.13733 | 0.0025177 | -0.013729 | -0.080079 | -0.0078335 | -0.03322 | -0.052731 | -0.041033 | -0.0021057 | 0.0040312 | 0.007494 | -0.014193 | -0.22065 | -0.01941 | -0.020476 | -0.07782 | 0.10071 | -0.11902 | -0.09613 | 0.07782 | -0.064087 | -0.004578 | 0.004578 | 0.11444 | -0.11444 | -0.018311 | 0.10071 | 0.036621 | 0.054932 | 121.9666 | -0.036621 | -0.23346 | 122.1634 | 122.081 | 122.0215 | 0.11444 | 0.054932 | 121.9711 | -0.022888 | -0.15564 | 122.1863 | 122.1405 | 122.1222 | 0.16937 | 0.15106 | 0.19684 | 0.022889 | 0.21515 | 0.09613 | 0.21973 | 0.22888 | 122.1863 | 122.2 | -0.25635 | -0.25177 | 121.9894 | 122.0673 | 122.0078 | 122.0901
3609.3906 | 122.3236 | -122.0398 | 0.091553 | 0.0025177 | -0.010525 | -0.078797 | -0.0052701 | -0.03023 | -0.050595 | -0.043169 | -0.0051575 | 0.0031766 | 0.006853 | -0.0060754 | -0.22107 | -0.016633 | -0.022185 | -0.11902 | 0.13275 | -0.14191 | -0.1236 | 0.022888 | -0.15106 | -0.041199 | 0.027466 | 0.11444 | -0.11444 | 0.068665 | 0.14648 | 0.091553 | 0.14191 | 121.8979 | 0.041198 | -0.21515 | 122.0627 | 121.9986 | 121.8887 | 0.10071 | -0.009155 | 121.9254 | 0.022888 | -0.022888 | 122.1863 | 122.1817 | 122.1313 | 0.25635 | 0.20599 | 0.16479 | 0.018311 | 0.26093 | 0.18311 | 0.27466 | 0.22888 | 122.1725 | 122.1542 | -0.23346 | -0.20599 | 121.9162 | 122.1085 | 121.9208 | 122.0673
3611.1719 | 122.3557 | -122.049 | 0.068665 | 0.017777 | -0.012448 | -0.079224 | -0.0061245 | -0.030443 | -0.048886 | -0.042955 | -0.0051575 | 0.0042448 | 0.011125 | -0.013552 | -0.21958 | -0.018128 | -0.021971 | -0.091553 | 0.082397 | -0.10529 | -0.054932 | 0.07782 | -0.082397 | -0.009155 | 0.086975 | 0.10529 | -0.086975 | 0.086975 | 0.15106 | 0.091553 | 0.15564 | 121.9437 | 0.013732 | -0.1236 | 122.1268 | 122.0398 | 121.9666 | 0.096131 | 0.022889 | 121.962 | 0.036621 | 0.01831 | 122.2 | 122.2046 | 122.1405 | 0.24261 | 0.17853 | 0.18311 | 0.050354 | 0.23804 | 0.17395 | 0.18768 | 0.19226 | 122.1313 | 122.1542 | -0.17395 | -0.15564 | 121.994 | 122.1359 | 121.9574 | 122.1359
3612.9688 | 122.2778 | -122.113 | 0.1236 | 0.0025177 | -0.01138 | -0.079651 | -0.0052701 | -0.025957 | -0.050167 | -0.040819 | -0.0051575 | 0.0040312 | 0.0096302 | -0.010348 | -0.22043 | -0.019623 | -0.02603 | -0.11902 | 0.11902 | -0.14648 | -0.16937 | -0.036621 | -0.19226 | -0.09613 | -0.041199 | 0.14191 | -0.13733 | -0.032043 | 0.041199 | -0.022888 | 0.050354 | 121.9666 | -0.004577 | -0.29297 | 122.0764 | 122.0169 | 121.9208 | 0.050354 | -0.045777 | 121.9757 | 0.018311 | -0.15564 | 122.1542 | 122.1634 | 122.0901 | 0.18768 | 0.11444 | 0.10986 | -0.022889 | 0.17853 | 0.10529 | 0.2655 | 0.27924 | 122.2321 | 122.2549 | -0.27008 | -0.26093 | 121.9437 | 122.081 | 121.994 | 122.0718
3614.7031 | 122.287 | -122.0947 | 0.10071 | -0.0051118 | -0.016293 | -0.080079 | -0.0074063 | -0.032152 | -0.05209 | -0.042101 | -0.0021057 | 0.001254 | 0.0077076 | -0.0071436 | -0.21937 | -0.019196 | -0.024321 | -0.07782 | 0.073242 | -0.10529 | -0.068665 | 0.09613 | -0.054932 | 0.009155 | 0.045776 | 0.11902 | -0.13733 | -0.004578 | 0.11902 | 0.050354 | 0.073242 | 121.9894 | -0.027466 | -0.16937 | 122.1909 | 122.1039 | 122.0398 | 0.11444 | 0.050354 | 121.9574 | 0.018311 | -0.10529 | 122.2137 | 122.168 | 122.1451 | 0.21057 | 0.18768 | 0.20142 | 0.036621 | 0.25635 | 0.13275 | 0.17853 | 0.25635 | 122.168 | 122.2137 | -0.20599 | -0.23804 | 122.0261 | 122.0901 | 122.0169 | 122.1405
3616.5 | 122.2458 | -122.1222 | 0.1236 | 0.0025177 | -0.014584 | -0.079011 | -0.0050565 | -0.03258 | -0.050381 | -0.040605 | -0.0021057 | 0.0033902 | 0.010698 | -0.011202 | -0.21958 | -0.018128 | -0.026885 | -0.15564 | 0.1236 | -0.14191 | -0.17395 | -0.018311 | -0.14648 | -0.07782 | -0.045776 | 0.13275 | -0.14191 | -0.045776 | 0.050354 | -0.004578 | 0.050354 | 121.9803 | 0 | -0.29755 | 122.1039 | 122.0444 | 121.9757 | 0.064087 | -0.004577 | 121.9803 | 0.009155 | -0.16937 | 122.1725 | 122.1725 | 122.1176 | 0.19226 | 0.13733 | 0.1236 | -0.032043 | 0.19226 | 0.096131 | 0.2655 | 0.27466 | 122.2458 | 122.2549 | -0.2655 | -0.2655 | 121.9482 | 122.0764 | 121.9666 | 122.0764
3618.2344 | 122.287 | -122.1176 | 0.1236 | -0.0051118 | -0.010098 | -0.079438 | -0.0063381 | -0.031725 | -0.051449 | -0.040392 | 0.00094606 | 0.0033902 | 0.010057 | -0.011843 | -0.21851 | -0.020478 | -0.022398 | -0.10529 | 0.11902 | -0.13275 | -0.12817 | 0.018311 | -0.11444 | -0.050354 | 0.004578 | 0.13733 | -0.1236 | 0 | 0.11902 | 0.027466 | 0.091553 | 121.9849 | -0.004577 | -0.25177 | 122.1359 | 122.0673 | 122.0032 | 0.082397 | 0.01831 | 121.994 | 0.013733 | -0.1236 | 122.2366 | 122.2092 | 122.1451 | 0.21515 | 0.15106 | 0.15106 | 0.004577 | 0.24261 | 0.1236 | 0.25177 | 0.26093 | 122.2366 | 122.2549 | -0.25635 | -0.24719 | 121.9894 | 122.1176 | 122.0123 | 122.1222
3620.0156 | 122.3923 | -122.0764 | 0.091553 | 0.0025177 | -0.0098843 | -0.079224 | -0.0063381 | -0.029375 | -0.049954 | -0.040392 | -0.0021057 | 0.0027494 | 0.0049304 | -0.013979 | -0.21894 | -0.016633 | -0.022826 | -0.054932 | 0.091553 | -0.09613 | -0.036621 | 0.14191 | -0.073242 | 0.022888 | 0.12817 | 0.10071 | -0.091553 | 0.10071 | 0.1831 | 0.10529 | 0.15106 | 121.9803 | 0 | -0.12817 | 122.2183 | 122.0993 | 122.0032 | 0.11902 | 0.022888 | 121.9849 | 0.009155 | 0.009155 | 122.2595 | 122.2275 | 122.1817 | 0.24261 | 0.19684 | 0.23804 | 0.059509 | 0.27466 | 0.19226 | 0.18768 | 0.19226 | 122.168 | 122.1771 | -0.18768 | -0.18311 | 122.0398 | 122.1771 | 122.0215 | 122.2046
3621.8125 | 122.4014 | -122.0856 | 0.07782 | 0.0025177 | -0.013302 | -0.079865 | -0.0091153 | -0.031725 | -0.050595 | -0.039324 | -0.0021057 | 0.0014676 | 0.0087756 | -0.01697 | -0.21979 | -0.017701 | -0.023253 | -0.10529 | 0.091553 | -0.10986 | -0.064087 | 0.10529 | -0.054932 | 0.027466 | 0.082397 | 0.10529 | -0.10071 | 0.073242 | 0.20142 | 0.14648 | 0.15106 | 121.9757 | 0.013733 | -0.14191 | 122.1909 | 122.113 | 122.0306 | 0.13733 | 0.054931 | 121.9849 | 0.027466 | -0.004578 | 122.287 | 122.2366 | 122.2321 | 0.25177 | 0.24719 | 0.21515 | 0.045776 | 0.30212 | 0.17395 | 0.20142 | 0.20599 | 122.1771 | 122.1909 | -0.18768 | -0.17853 | 122.0215 | 122.1588 | 121.9803 | 122.168
3623.5469 | 122.3328 | -122.168 | 0.11444 | -0.012741 | -0.0092435 | -0.077729 | -0.0044155 | -0.029375 | -0.04974 | -0.042101 | -0.0051575 | 0.0055264 | 0.006853 | -0.013552 | -0.22236 | -0.018769 | -0.022826 | -0.12817 | 0.11444 | -0.13275 | -0.15564 | -0.004578 | -0.18768 | -0.073242 | -0.009155 | 0.10986 | -0.11902 | 0.009155 | 0.07782 | 0.018311 | 0.07782 | 122.0352 | 0 | -0.27008 | 122.1634 | 122.0947 | 121.9803 | 0.059509 | -0.054932 | 122.049 | -0.004578 | -0.10529 | 122.2458 | 122.2458 | 122.1863 | 0.19684 | 0.13733 | 0.12817 | -0.022889 | 0.19684 | 0.12817 | 0.24719 | 0.22888 | 122.2824 | 122.2778 | -0.24719 | -0.23346 | 122.0123 | 122.1771 | 122.0398 | 122.1588
3625.3281 | 122.2687 | -122.1588 | 0.12817 | -0.0051118 | -0.01138 | -0.07837 | -0.0031337 | -0.028093 | -0.053585 | -0.041033 | -0.0021057 | 0.004672 | 0.0081348 | -0.011416 | -0.21851 | -0.015778 | -0.021544 | -0.12817 | 0.1236 | -0.13733 | -0.16479 | -0.041199 | -0.19226 | -0.11444 | -0.082397 | 0.15106 | -0.15564 | -0.054932 | 0.018311 | -0.041199 | 0.032043 | 122.0215 | -0.004578 | -0.29297 | 122.1176 | 122.0444 | 121.9666 | 0.022888 | -0.054932 | 122.0032 | 0.022888 | -0.18311 | 122.1771 | 122.1909 | 122.1176 | 0.18768 | 0.11444 | 0.09613 | -0.027466 | 0.17395 | 0.10071 | 0.26093 | 0.3067 | 122.2824 | 122.3099 | -0.2655 | -0.28381 | 121.994 | 122.1039 | 122.0306 | 122.0764
3627.1094 | 122.4243 | -122.1039 | 0.091553 | 0.0025177 | -0.015225 | -0.080719 | -0.0082607 | -0.029375 | -0.050381 | -0.040605 | -0.0021057 | 0.0038174 | 0.0077076 | -0.011843 | -0.21958 | -0.019837 | -0.022185 | -0.086975 | 0.082397 | -0.10529 | -0.045776 | 0.1236 | -0.018311 | 0.041199 | 0.1236 | 0.09613 | -0.091553 | 0.091553 | 0.20599 | 0.15564 | 0.15106 | 121.9986 | -0.009156 | -0.13733 | 122.2275 | 122.1451 | 122.0856 | 0.14649 | 0.086975 | 122.0123 | 0.004577 | 0 | 122.3099 | 122.2549 | 122.2595 | 0.24261 | 0.24719 | 0.22888 | 0.05951 | 0.29755 | 0.18311 | 0.18768 | 0.18768 | 122.1863 | 122.2 | -0.19684 | -0.18311 | 122.0581 | 122.1954 | 122.0169 | 122.2275
3628.8594 | 122.319 | -122.1725 | 0.10071 | -0.0051118 | -0.0096707 | -0.079651 | -0.0031337 | -0.025957 | -0.051022 | -0.038896 | 0.00094606 | 0.0027494 | 0.0083484 | -0.015475 | -0.21937 | -0.017487 | -0.020476 | -0.12817 | 0.11444 | -0.14648 | -0.16479 | -0.045776 | -0.18768 | -0.091553 | -0.022888 | 0.13275 | -0.13275 | -0.018311 | 0.064087 | -0.022888 | 0.050354 | 122.0261 | 0.013733 | -0.2655 | 122.1268 | 122.081 | 121.9849 | 0.054931 | -0.041199 | 122.0398 | 0.032043 | -0.11902 | 122.2366 | 122.2229 | 122.1497 | 0.18311 | 0.10986 | 0.10071 | -0.018311 | 0.19684 | 0.11444 | 0.26093 | 0.2655 | 122.287 | 122.3053 | -0.24719 | -0.23346 | 122.0078 | 122.1542 | 122.0444 | 122.1497
3630.6562 | 122.4106 | -122.168 | 0.082397 | -0.0051118 | -0.013729 | -0.079865 | -0.0071927 | -0.033648 | -0.048886 | -0.04146 | -0.0021057 | 0.0021084 | 0.0066394 | -0.02167 | -0.22172 | -0.020478 | -0.01898 | -0.10529 | 0.073242 | -0.10986 | -0.082397 | 0.082397 | -0.068665 | 0.018311 | 0.059509 | 0.10071 | -0.1236 | 0.07782 | 0.17853 | 0.13275 | 0.14648 | 122.0581 | -0.009155 | -0.16479 | 122.2504 | 122.1863 | 122.0993 | 0.12817 | 0.041198 | 122.0444 | 0.018311 | -0.004577 | 122.3465 | 122.3145 | 122.3007 | 0.27008 | 0.25635 | 0.19226 | 0.027466 | 0.30212 | 0.20142 | 0.18311 | 0.2243 | 122.2412 | 122.2687 | -0.19226 | -0.20599 | 122.0856 | 122.2458 | 122.0627 | 122.2275
3632.4375 | 122.3465 | -122.1588 | 0.11902 | 0.010147 | -0.013089 | -0.079651 | -0.0031337 | -0.027666 | -0.050167 | -0.040392 | -0.0051575 | 0.0042448 | 0.0083484 | -0.012911 | -0.22043 | -0.018555 | -0.024321 | -0.09613 | 0.1236 | -0.14191 | -0.13275 | 0.004578 | -0.11902 | -0.054932 | -0.009155 | 0.15106 | -0.12817 | 0.004578 | 0.09613 | 0.032043 | 0.086975 | 122.0169 | 0.004577 | -0.25177 | 122.1634 | 122.1039 | 122.0398 | 0.086975 | 0.022888 | 122.0306 | 0.032043 | -0.11444 | 122.2549 | 122.2458 | 122.1909 | 0.21515 | 0.16022 | 0.14649 | 0.009156 | 0.2243 | 0.13275 | 0.2655 | 0.27924 | 122.2824 | 122.3099 | -0.26093 | -0.24719 | 122.0261 | 122.1634 | 122.0627 | 122.1497
3634.2188 | 122.3145 | -122.1909 | 0.10529 | -0.012741 | -0.012234 | -0.080079 | -0.0031337 | -0.02788 | -0.050167 | -0.040819 | 0.00094606 | 0.0038174 | 0.0070666 | -0.009707 | -0.22107 | -0.017701 | -0.024962 | -0.082397 | 0.10986 | -0.13275 | -0.1236 | 0.045776 | -0.12817 | -0.050354 | 0.018311 | 0.11902 | -0.11902 | 0 | 0.082397 | -0.009155 | 0.068665 | 122.0581 | 0.004577 | -0.22888 | 122.2366 | 122.1405 | 122.0627 | 0.082397 | 0.004577 | 122.0718 | 0.013733 | -0.10529 | 122.2733 | 122.2595 | 122.1817 | 0.18768 | 0.10986 | 0.17853 | 0.009155 | 0.20142 | 0.11902 | 0.24261 | 0.23804 | 122.3007 | 122.3099 | -0.23804 | -0.22431 | 122.0673 | 122.1909 | 122.1085 | 122.2092
3635.9688 | 122.4518 | -122.1497 | 0.082397 | 0.0025177 | -0.010098 | -0.07837 | -0.0067653 | -0.02788 | -0.048886 | -0.039537 | 0.00094606 | 0.0023222 | 0.0072802 | -0.020175 | -0.21787 | -0.019196 | -0.021971 | -0.045776 | 0.07782 | -0.082397 | -0.045776 | 0.13275 | -0.073242 | 0 | 0.11444 | 0.11444 | -0.082397 | 0.09613 | 0.1831 | 0.10529 | 0.15564 | 122.0673 | -0.004577 | -0.12817 | 122.2824 | 122.1497 | 122.0764 | 0.082397 | 0.009155 | 122.0673 | 0.032044 | 0.013733 | 122.3328 | 122.3053 | 122.2549 | 0.23804 | 0.18768 | 0.21515 | 0.036621 | 0.2655 | 0.17853 | 0.16022 | 0.19684 | 122.2275 | 122.2641 | -0.16479 | -0.16479 | 122.1039 | 122.2458 | 122.1039 | 122.2641
3637.75 | 122.4106 | -122.1359 | 0.091553 | -0.0051118 | -0.011807 | -0.080719 | -0.0061245 | -0.028521 | -0.049526 | -0.039324 | -0.0021057 | 0.00039959 | 0.0081348 | -0.01462 | -0.21937 | -0.018342 | -0.024748 | -0.10986 | 0.091553 | -0.11444 | -0.073242 | 0.07782 | -0.09613 | 0 | 0.054932 | 0.10071 | -0.11902 | 0.027466 | 0.1236 | 0.059509 | 0.11444 | 122.0215 | 0 | -0.16479 | 122.2137 | 122.1359 | 122.0398 | 0.11444 | 0.018311 | 122.0169 | 0.009155 | -0.064087 | 122.2595 | 122.2504 | 122.1954 | 0.23346 | 0.17853 | 0.19226 | 0.041199 | 0.24261 | 0.14649 | 0.20599 | 0.21973 | 122.2275 | 122.2366 | -0.20599 | -0.21057 | 122.0627 | 122.1634 | 122.0261 | 122.1909
3639.5469 | 122.3328 | -122.1863 | 0.13275 | 0.010147 | -0.010098 | -0.080292 | -0.0046291 | -0.030443 | -0.04974 | -0.043169 | -0.0051575 | 0.0053128 | 0.008562 | -0.007998 | -0.21894 | -0.019837 | -0.020476 | -0.1236 | 0.12817 | -0.13733 | -0.17395 | -0.050354 | -0.19684 | -0.10529 | -0.054932 | 0.14648 | -0.13275 | -0.036621 | 0.027466 | -0.041199 | 0.050354 | 122.049 | -0.004577 | -0.3067 | 122.1359 | 122.081 | 121.9894 | 0.032043 | -0.059509 | 122.0535 | 0.013733 | -0.16937 | 122.2137 | 122.2366 | 122.1451 | 0.18311 | 0.091552 | 0.086975 | -0.036621 | 0.16022 | 0.09613 | 0.2655 | 0.27924 | 122.3145 | 122.3328 | -0.27008 | -0.2655 | 122.0123 | 122.1497 | 122.0627 | 122.1313
3641.2656 | 122.3557 | -122.1542 | 0.10529 | -0.0051118 | -0.013516 | -0.079438 | -0.0056973 | -0.028307 | -0.051022 | -0.041887 | 0.00094606 | 0.0040312 | 0.0053576 | -0.011843 | -0.22043 | -0.017273 | -0.024107 | -0.13733 | 0.11902 | -0.14191 | -0.1831 | -0.032043 | -0.17853 | -0.09613 | -0.032043 | 0.13733 | -0.13733 | -0.018311 | 0.041199 | -0.009155 | 0.073242 | 122.0123 | 0.013733 | -0.28839 | 122.1222 | 122.0581 | 121.9757 | 0.045777 | -0.036621 | 122.0169 | 0.032043 | -0.1236 | 122.1954 | 122.2275 | 122.1451 | 0.21057 | 0.12817 | 0.10986 | -0.041198 | 0.17853 | 0.11902 | 0.26093 | 0.27466 | 122.2733 | 122.2916 | -0.24719 | -0.24262 | 121.9711 | 122.1359 | 122.0169 | 122.1222
3643.0625 | 122.3511 | -122.2 | 0.1236 | -0.02037 | -0.0096707 | -0.077942 | -0.0052701 | -0.027025 | -0.050167 | -0.045092 | -0.0021057 | 0.0044584 | 0.0077076 | -0.012057 | -0.2183 | -0.018128 | -0.023467 | -0.11902 | 0.11902 | -0.14191 | -0.1831 | -0.041199 | -0.19684 | -0.10529 | -0.050354 | 0.13275 | -0.13275 | -0.045776 | 0.027466 | -0.036621 | 0.045776 | 122.0581 | -0.004577 | -0.3067 | 122.1588 | 122.0947 | 122.0032 | 0.036621 | -0.054931 | 122.0673 | 0.009155 | -0.16937 | 122.2275 | 122.2458 | 122.1634 | 0.17853 | 0.09613 | 0.10071 | -0.041198 | 0.16022 | 0.086975 | 0.26093 | 0.2655 | 122.319 | 122.3328 | -0.2655 | -0.25635 | 122.0169 | 122.1542 | 122.081 | 122.1497
3644.8438 | 122.4014 | -122.2046 | 0.11444 | 0.0025177 | -0.013089 | -0.079438 | -0.0044155 | -0.030871 | -0.04974 | -0.038896 | 0.00094606 | 0.0027494 | 0.0079212 | -0.017184 | -0.2183 | -0.019196 | -0.023894 | -0.086975 | 0.11902 | -0.13733 | -0.10529 | 0.050354 | -0.10986 | -0.045776 | 0.027466 | 0.14191 | -0.10986 | 0.018311 | 0.10071 | 0.045776 | 0.09613 | 122.0673 | 0.004578 | -0.21973 | 122.2549 | 122.1588 | 122.0947 | 0.091553 | 0.027466 | 122.0947 | 0.027466 | -0.09613 | 122.3053 | 122.3007 | 122.2504 | 0.20599 | 0.15564 | 0.18768 | 0.032043 | 0.21057 | 0.12817 | 0.25635 | 0.25177 | 122.3236 | 122.3465 | -0.25177 | -0.2243 | 122.0993 | 122.2229 | 122.1176 | 122.2321
3646.6406 | 122.3236 | -122.2 | 0.12817 | -0.0051118 | -0.010098 | -0.077729 | -0.0065517 | -0.02788 | -0.050808 | -0.040605 | 0.00094606 | 0.0040312 | 0.0089892 | -0.006289 | -0.21787 | -0.016846 | -0.021544 | -0.1236 | 0.11444 | -0.14191 | -0.18768 | -0.059509 | -0.20599 | -0.10529 | -0.07782 | 0.14191 | -0.12817 | -0.050354 | 0.022888 | -0.050354 | 0.045776 | 122.0581 | -0.013733 | -0.31586 | 122.1405 | 122.0947 | 121.994 | 0.036621 | -0.064087 | 122.0718 | 0.013733 | -0.17853 | 122.2229 | 122.2458 | 122.1497 | 0.17395 | 0.07782 | 0.082398 | -0.045776 | 0.15106 | 0.07782 | 0.25635 | 0.27008 | 122.3145 | 122.3419 | -0.27008 | -0.25635 | 122.0123 | 122.1497 | 122.0764 | 122.1222
3648.4531 | 122.3648 | -122.2366 | 0.12817 | -0.012741 | -0.014157 | -0.080292 | -0.0078335 | -0.028521 | -0.04974 | -0.04146 | 0.0039979 | 0.0027494 | 0.011339 | -0.016757 | -0.21851 | -0.018982 | -0.021544 | -0.14648 | 0.10986 | -0.13733 | -0.17853 | -0.009155 | -0.15106 | -0.073242 | -0.041199 | 0.13275 | -0.13275 | -0.068665 | 0.050354 | -0.018311 | 0.027466 | 122.0993 | -0.018311 | -0.3067 | 122.2275 | 122.1634 | 122.0856 | 0.064087 | -0.013733 | 122.1039 | 0.004577 | -0.19684 | 122.287 | 122.2641 | 122.2183 | 0.16022 | 0.11444 | 0.12817 | -0.041199 | 0.18311 | 0.064086 | 0.24719 | 0.2655 | 122.3465 | 122.3694 | -0.2655 | -0.26093 | 122.0581 | 122.168 | 122.0901 | 122.1954
3650.2344 | 122.3602 | -122.2137 | 0.11902 | 0.0025177 | -0.0098843 | -0.078797 | -0.0044155 | -0.026171 | -0.050167 | -0.040392 | -0.0021057 | 0.0040312 | 0.0066394 | -0.016543 | -0.21894 | -0.018982 | -0.020049 | -0.11444 | 0.11902 | -0.13733 | -0.16479 | -0.018311 | -0.19684 | -0.10529 | -0.073242 | 0.13733 | -0.13733 | -0.054932 | 0.022888 | -0.045776 | 0.036621 | 122.0764 | 0 | -0.28381 | 122.1954 | 122.1085 | 122.0169 | 0.032043 | -0.059509 | 122.0764 | 0.01831 | -0.17395 | 122.2366 | 122.2504 | 122.168 | 0.17395 | 0.091553 | 0.11902 | -0.027466 | 0.16022 | 0.082397 | 0.25635 | 0.27466 | 122.3328 | 122.3511 | -0.25635 | -0.25635 | 122.049 | 122.1588 | 122.0993 | 122.1405
3651.9844 | 122.4472 | -122.2092 | 0.10986 | -0.0051118 | -0.015225 | -0.079651 | -0.0086879 | -0.03023 | -0.052517 | -0.041246 | 0.00094606 | 0.0044584 | 0.0081348 | -0.020175 | -0.2215 | -0.018769 | -0.021544 | -0.10529 | 0.082397 | -0.11902 | -0.11444 | 0.064087 | -0.10071 | -0.022888 | 0.032043 | 0.11902 | -0.10529 | 0.022888 | 0.12817 | 0.073242 | 0.09613 | 122.0901 | -0.027466 | -0.2243 | 122.2733 | 122.1863 | 122.1085 | 0.096131 | 0.018311 | 122.1039 | 0.009156 | -0.086975 | 122.3373 | 122.3053 | 122.2824 | 0.20142 | 0.17853 | 0.18311 | 0.004578 | 0.23346 | 0.12817 | 0.20142 | 0.22431 | 122.2916 | 122.3282 | -0.22888 | -0.21515 | 122.0947 | 122.2321 | 122.1039 | 122.2412
3653.7812 | 122.374 | -122.2412 | 0.11444 | -0.0051118 | -0.014584 | -0.081574 | -0.0071927 | -0.026171 | -0.050381 | -0.041033 | 0.00094606 | 0.0036038 | 0.0070666 | -0.010348 | -0.22193 | -0.018982 | -0.025176 | -0.14648 | 0.12817 | -0.15564 | -0.1831 | -0.013733 | -0.14191 | -0.082397 | -0.073242 | 0.15106 | -0.14191 | -0.050354 | 0.032043 | -0.009155 | 0.059509 | 122.0856 | 0.013733 | -0.29755 | 122.2275 | 122.1588 | 122.0993 | 0.073243 | 0.013733 | 122.0993 | 0.036621 | -0.16479 | 122.2733 | 122.3007 | 122.2321 | 0.20142 | 0.13275 | 0.14191 | -0.027465 | 0.17395 | 0.091553 | 0.28381 | 0.29297 | 122.3694 | 122.3923 | -0.27008 | -0.25635 | 122.0581 | 122.1909 | 122.0947 | 122.168
3655.5781 | 122.3557 | -122.2458 | 0.14648 | -0.0051118 | -0.010311 | -0.077942 | -0.0042019 | -0.03322 | -0.051022 | -0.03911 | -0.0021057 | 0.0025358 | 0.007494 | -0.01163 | -0.22001 | -0.017273 | -0.025603 | -0.10986 | 0.13275 | -0.14648 | -0.17853 | -0.041199 | -0.19684 | -0.10986 | -0.054932 | 0.13275 | -0.1236 | -0.064087 | 0.004578 | -0.041199 | 0.032043 | 122.0993 | -0.013733 | -0.32501 | 122.2046 | 122.1359 | 122.049 | 0.036621 | -0.050354 | 122.1222 | -0.013733 | -0.21057 | 122.2504 | 122.2778 | 122.2046 | 0.15564 | 0.082397 | 0.10529 | -0.032044 | 0.12817 | 0.059509 | 0.27924 | 0.25635 | 122.3785 | 122.3785 | -0.29297 | -0.27008 | 122.0673 | 122.1817 | 122.1359 | 122.1909
3657.3281 | 122.5204 | -122.2092 | 0.091553 | -0.0051118 | -0.01437 | -0.080506 | -0.0091153 | -0.034929 | -0.051663 | -0.043596 | -0.0021057 | 0.0021084 | 0.0077076 | -0.010561 | -0.21851 | -0.020264 | -0.021971 | -0.091553 | 0.086975 | -0.091553 | -0.064087 | 0.14191 | -0.027466 | 0.050354 | 0.11902 | 0.09613 | -0.10071 | 0.10071 | 0.20142 | 0.16937 | 0.14648 | 122.1176 | -0.004578 | -0.15564 | 122.3511 | 122.2595 | 122.1817 | 0.14191 | 0.064087 | 122.1085 | 0.004577 | 0.009155 | 122.4106 | 122.3557 | 122.3785 | 0.24719 | 0.27008 | 0.23346 | 0.027466 | 0.30212 | 0.20142 | 0.17853 | 0.19684 | 122.2961 | 122.3053 | -0.18311 | -0.19226 | 122.1451 | 122.3099 | 122.1176 | 122.3282
3659.1094 | 122.3831 | -122.2687 | 0.10071 | 0.0025177 | -0.010525 | -0.078797 | -0.0022793 | -0.026384 | -0.048458 | -0.04146 | 0.00094606 | 0.0033902 | 0.008562 | -0.016329 | -0.22001 | -0.016205 | -0.027525 | -0.13275 | 0.13733 | -0.13733 | -0.17395 | -0.064087 | -0.2243 | -0.10986 | -0.073242 | 0.14191 | -0.13275 | -0.041199 | 0.022888 | -0.032043 | 0.041199 | 122.1313 | 0.036621 | -0.27466 | 122.2046 | 122.1588 | 122.0444 | 0.027466 | -0.086975 | 122.1359 | 0.041199 | -0.14191 | 122.2916 | 122.3099 | 122.2366 | 0.17395 | 0.10071 | 0.073242 | -0.036621 | 0.15564 | 0.091552 | 0.27466 | 0.27466 | 122.406 | 122.4106 | -0.23804 | -0.23346 | 122.0947 | 122.2275 | 122.1359 | 122.1954
3660.8594 | 122.4014 | -122.2687 | 0.12817 | -0.012741 | -0.014584 | -0.079438 | -0.0067653 | -0.031511 | -0.051235 | -0.04146 | -0.0021057 | 0.0040312 | 0.0072802 | -0.018893 | -0.2183 | -0.019196 | -0.024535 | -0.14191 | 0.12817 | -0.14648 | -0.16479 | -0.022888 | -0.14648 | -0.07782 | -0.059509 | 0.12817 | -0.12817 | -0.045776 | 0.054932 | 0 | 0.064087 | 122.1222 | 0 | -0.29297 | 122.2458 | 122.1909 | 122.1222 | 0.068664 | 0 | 122.1405 | 0 | -0.17395 | 122.3236 | 122.3328 | 122.2687 | 0.19226 | 0.12817 | 0.1236 | -0.018311 | 0.18311 | 0.082398 | 0.27466 | 0.25635 | 122.3969 | 122.3969 | -0.27466 | -0.25635 | 122.1039 | 122.2229 | 122.1268 | 122.2092
3662.6562 | 122.4197 | -122.2321 | 0.11444 | 0.0025177 | -0.010952 | -0.076874 | -0.0056973 | -0.030016 | -0.050381 | -0.040605 | -0.0021057 | 0.0027494 | 0.0066394 | -0.0099206 | -0.21937 | -0.017701 | -0.023253 | -0.13275 | 0.11444 | -0.13275 | -0.16937 | -0.009155 | -0.19226 | -0.091553 | -0.013733 | 0.13733 | -0.13275 | -0.009155 | 0.068665 | -0.004578 | 0.082397 | 122.0993 | 0 | -0.28381 | 122.2229 | 122.1405 | 122.0398 | 0.041198 | -0.05951 | 122.0993 | 0.022888 | -0.1236 | 122.3007 | 122.3145 | 122.2275 | 0.21515 | 0.12817 | 0.1236 | -0.036622 | 0.20142 | 0.1236 | 0.24719 | 0.27008 | 122.3465 | 122.3694 | -0.24719 | -0.24719 | 122.0627 | 122.2229 | 122.0993 | 122.2183
3664.4531 | 122.4518 | -122.2412 | 0.10071 | -0.0051118 | -0.010952 | -0.079865 | -0.0048427 | -0.03023 | -0.051449 | -0.040605 | -0.0082091 | 0.0025358 | 0.0083484 | -0.0075708 | -0.22193 | -0.018982 | -0.020476 | -0.11444 | 0.1236 | -0.12817 | -0.1236 | 0 | -0.1236 | -0.050354 | 0 | 0.1236 | -0.10529 | 0.004578 | 0.09613 | 0.027466 | 0.10071 | 122.113 | 0.022888 | -0.2243 | 122.2412 | 122.1909 | 122.1176 | 0.07782 | 0.004578 | 122.1359 | 0.022888 | -0.09613 | 122.3373 | 122.3419 | 122.2687 | 0.20599 | 0.13275 | 0.12817 | 0.004578 | 0.20142 | 0.10986 | 0.25177 | 0.22888 | 122.3648 | 122.3648 | -0.22888 | -0.20599 | 122.1176 | 122.2458 | 122.1268 | 122.2412
3666.2344 | 122.4152 | -122.2504 | 0.1236 | -0.012741 | -0.013516 | -0.080719 | -0.0054837 | -0.031939 | -0.050595 | -0.04146 | -0.0021057 | 0.0040312 | 0.0083484 | -0.015261 | -0.21787 | -0.018342 | -0.021971 | -0.13275 | 0.1236 | -0.14191 | -0.16937 | -0.032043 | -0.15106 | -0.064087 | -0.059509 | 0.13733 | -0.11902 | -0.027466 | 0.054932 | -0.009155 | 0.054932 | 122.1085 | 0 | -0.29297 | 122.2183 | 122.1863 | 122.0993 | 0.07782 | -0.009155 | 122.1313 | 0.013733 | -0.15106 | 122.3053 | 122.3053 | 122.2412 | 0.17395 | 0.10986 | 0.10986 | -0.027466 | 0.17395 | 0.091553 | 0.2655 | 0.25635 | 122.374 | 122.3877 | -0.2655 | -0.24261 | 122.081 | 122.2229 | 122.1176 | 122.1909
3667.9688 | 122.3923 | -122.2733 | 0.12817 | -0.012741 | -0.015011 | -0.080719 | -0.0093289 | -0.028948 | -0.051449 | -0.043169 | -0.0051575 | 0.002963 | 0.010698 | -0.0032984 | -0.21894 | -0.021119 | -0.020262 | -0.1236 | 0.10529 | -0.13733 | -0.16022 | -0.004578 | -0.15564 | -0.068665 | -0.027466 | 0.13733 | -0.13275 | -0.068665 | 0.050354 | -0.004578 | 0.036621 | 122.1359 | -0.022888 | -0.28839 | 122.2687 | 122.2046 | 122.1176 | 0.068664 | -0.018311 | 122.1405 | 0.009155 | -0.19684 | 122.3236 | 122.3099 | 122.2687 | 0.16937 | 0.12817 | 0.13275 | -0.022888 | 0.18311 | 0.064086 | 0.24262 | 0.27008 | 122.3785 | 122.4106 | -0.2655 | -0.26093 | 122.113 | 122.2046 | 122.1497 | 122.2458
3669.75 | 122.5342 | -122.2275 | 0.07782 | -0.0051118 | -0.016934 | -0.079651 | -0.0095425 | -0.03258 | -0.051663 | -0.039965 | 0.00094606 | 0.0021084 | 0.0045032 | -0.01227 | -0.22172 | -0.020264 | -0.026244 | -0.091553 | 0.09613 | -0.10529 | -0.022888 | 0.15564 | -0.009155 | 0.045776 | 0.1236 | 0.10071 | -0.10529 | 0.073242 | 0.21057 | 0.15106 | 0.15106 | 122.1222 | 0.01831 | -0.10071 | 122.3831 | 122.2733 | 122.2183 | 0.15106 | 0.096131 | 122.1222 | 0.022888 | -0.004578 | 122.438 | 122.3785 | 122.3785 | 0.25635 | 0.25635 | 0.26093 | 0.082398 | 0.31586 | 0.17853 | 0.20142 | 0.20599 | 122.3236 | 122.3282 | -0.18311 | -0.18311 | 122.2046 | 122.3007 | 122.1359 | 122.3511
3671.5469 | 122.4106 | -122.3007 | 0.12817 | -0.012741 | -0.0088163 | -0.07837 | -0.0035611 | -0.03023 | -0.049954 | -0.041887 | -0.0021057 | 0.004672 | 0.006853 | -0.013766 | -0.22065 | -0.017914 | -0.023253 | -0.10071 | 0.11444 | -0.14648 | -0.16479 | -0.036621 | -0.19684 | -0.11444 | -0.059509 | 0.14648 | -0.11444 | -0.064087 | 0.022888 | -0.050354 | 0.041199 | 122.1542 | -0.013733 | -0.29297 | 122.2641 | 122.1863 | 122.1039 | 0.032043 | -0.050354 | 122.1863 | 0.01831 | -0.19226 | 122.3236 | 122.3419 | 122.2504 | 0.15564 | 0.064087 | 0.10986 | -0.018311 | 0.13733 | 0.050354 | 0.26093 | 0.26093 | 122.4152 | 122.4472 | -0.27466 | -0.24262 | 122.1359 | 122.2366 | 122.2 | 122.2412
3673.3438 | 122.438 | -122.3053 | 0.12817 | 0.0025177 | -0.013729 | -0.080292 | -0.0042019 | -0.027025 | -0.050808 | -0.041887 | 0.00094606 | 0.0031766 | 0.0098438 | -0.0099206 | -0.21872 | -0.020051 | -0.022612 | -0.1236 | 0.13733 | -0.14191 | -0.15564 | -0.027466 | -0.15106 | -0.07782 | -0.054932 | 0.1236 | -0.13275 | -0.041199 | 0.068665 | 0.004578 | 0.068665 | 122.1634 | 0.009155 | -0.28381 | 122.2778 | 122.2275 | 122.1542 | 0.064087 | -0.009155 | 122.1725 | -0.004578 | -0.16937 | 122.374 | 122.374 | 122.3099 | 0.20142 | 0.13733 | 0.11444 | -0.013733 | 0.20142 | 0.091552 | 0.27924 | 0.25635 | 122.4426 | 122.4289 | -0.27008 | -0.26093 | 122.1497 | 122.2641 | 122.1817 | 122.2504
3675.1406 | 122.4197 | -122.3053 | 0.1236 | -0.0051118 | -0.010525 | -0.079011 | -0.0037747 | -0.028307 | -0.048886 | -0.04146 | -0.0021057 | 0.0036038 | 0.0064258 | -0.0094934 | -0.22043 | -0.017487 | -0.023039 | -0.12817 | 0.11444 | -0.13733 | -0.15106 | -0.027466 | -0.18768 | -0.10529 | -0.082397 | 0.14648 | -0.10986 | -0.050354 | 0.032043 | -0.036621 | 0.041199 | 122.168 | -0.009155 | -0.27466 | 122.2778 | 122.2 | 122.1176 | 0.032043 | -0.050354 | 122.1954 | 0.022888 | -0.17395 | 122.3373 | 122.3465 | 122.2687 | 0.15106 | 0.073242 | 0.10986 | -0.013733 | 0.14191 | 0.059509 | 0.25177 | 0.25635 | 122.4197 | 122.4518 | -0.26093 | -0.23346 | 122.1542 | 122.2549 | 122.1771 | 122.2229
3676.9375 | 122.4747 | -122.3007 | 0.11902 | 0.0025177 | -0.013302 | -0.078156 | -0.0044155 | -0.026598 | -0.050808 | -0.043383 | -0.0051575 | 0.002963 | 0.0092028 | -0.0032984 | -0.21766 | -0.016846 | -0.019408 | -0.11444 | 0.11444 | -0.14191 | -0.1236 | 0.013733 | -0.11444 | -0.045776 | 0.004578 | 0.11444 | -0.11444 | -0.009155 | 0.09613 | 0.036621 | 0.091553 | 122.1588 | -0.004578 | -0.24261 | 122.3145 | 122.2549 | 122.1863 | 0.096131 | 0.027466 | 122.1863 | -0.004578 | -0.12817 | 122.3969 | 122.3923 | 122.3373 | 0.20599 | 0.15106 | 0.15564 | 0.018311 | 0.21057 | 0.10529 | 0.25635 | 0.22888 | 122.4152 | 122.4152 | -0.26093 | -0.23346 | 122.1771 | 122.2916 | 122.1863 | 122.3053
3678.6719 | 122.4747 | -122.287 | 0.09613 | -0.012741 | -0.0094571 | -0.077729 | -0.0052701 | -0.029375 | -0.047817 | -0.041674 | -0.0021057 | 0.002963 | 0.0081348 | -0.014193 | -0.21915 | -0.019623 | -0.024962 | -0.11902 | 0.1236 | -0.14648 | -0.16479 | -0.009155 | -0.17853 | -0.086975 | -0.004578 | 0.13275 | -0.1236 | 0.009155 | 0.073242 | 0.018311 | 0.073242 | 122.1405 | 0.027466 | -0.26092 | 122.2778 | 122.2 | 122.1085 | 0.059509 | -0.032044 | 122.1634 | 0.036621 | -0.086975 | 122.3602 | 122.3602 | 122.3053 | 0.19684 | 0.14191 | 0.13733 | -0.018311 | 0.19684 | 0.13275 | 0.27008 | 0.25635 | 122.4106 | 122.4197 | -0.24261 | -0.21973 | 122.1222 | 122.2961 | 122.168 | 122.2824
3680.4688 | 122.5616 | -122.2412 | 0.07782 | 0.0025177 | -0.01138 | -0.077942 | -0.0061245 | -0.030657 | -0.052944 | -0.041033 | 0.00094606 | 0.0021084 | 0.006853 | -0.014193 | -0.2168 | -0.018769 | -0.026457 | -0.073242 | 0.10071 | -0.13733 | -0.068665 | 0.082397 | -0.09613 | -0.013733 | 0.091553 | 0.10071 | -0.10986 | 0.086975 | 0.17853 | 0.10986 | 0.14648 | 122.1039 | 0.022888 | -0.14649 | 122.3236 | 122.2275 | 122.1451 | 0.1236 | 0.041199 | 122.1313 | 0.022888 | 0.009155 | 122.4197 | 122.3877 | 122.3511 | 0.25635 | 0.21973 | 0.21973 | 0.068664 | 0.28839 | 0.19684 | 0.23804 | 0.21057 | 122.3419 | 122.3419 | -0.21515 | -0.18768 | 122.1725 | 122.3282 | 122.168 | 122.3328
3682.2031 | 122.5571 | -122.2778 | 0.07782 | 0.0025177 | -0.0086027 | -0.076233 | -0.0037747 | -0.029589 | -0.048031 | -0.041246 | 0.00094606 | 0.0027494 | 0.0083484 | -0.014193 | -0.22065 | -0.017273 | -0.023253 | -0.09613 | 0.11902 | -0.1236 | -0.09613 | 0.07782 | -0.10986 | 0 | 0.07782 | 0.10071 | -0.082397 | 0.07782 | 0.16022 | 0.09613 | 0.15106 | 122.1542 | 0.041199 | -0.17395 | 122.3557 | 122.2778 | 122.168 | 0.1236 | 0.013733 | 122.1954 | 0.022888 | 0 | 122.438 | 122.4289 | 122.374 | 0.23346 | 0.17853 | 0.20142 | 0.027466 | 0.24261 | 0.16022 | 0.24261 | 0.18311 | 122.3969 | 122.3785 | -0.20142 | -0.16022 | 122.1817 | 122.3557 | 122.1817 | 122.3557
3684.0156 | 122.4792 | -122.2687 | 0.11444 | -0.012741 | -0.010525 | -0.079865 | -0.0050565 | -0.029375 | -0.049526 | -0.042742 | -0.0051575 | 0.0044584 | 0.0070666 | -0.015261 | -0.21915 | -0.015778 | -0.021758 | -0.07782 | 0.1236 | -0.1236 | -0.09613 | 0.045776 | -0.10529 | -0.050354 | 0.059509 | 0.13275 | -0.11902 | 0.027466 | 0.09613 | 0.041199 | 0.086975 | 122.1451 | 0.009155 | -0.21057 | 122.3145 | 122.2183 | 122.1634 | 0.073242 | 0.01831 | 122.1497 | 0.01831 | -0.086975 | 122.3648 | 122.3557 | 122.3099 | 0.20599 | 0.16022 | 0.16937 | 0.027466 | 0.21515 | 0.14649 | 0.24719 | 0.25177 | 122.3923 | 122.4014 | -0.23804 | -0.23346 | 122.1725 | 122.2961 | 122.1909 | 122.3282
3685.75 | 122.4426 | -122.3099 | 0.12817 | 0.0025177 | -0.017575 | -0.080506 | -0.0095425 | -0.031511 | -0.048886 | -0.042314 | -0.0021057 | 0.0036038 | 0.0070666 | -0.016757 | -0.21894 | -0.019196 | -0.025603 | -0.15106 | 0.11444 | -0.15564 | -0.17395 | 0.009155 | -0.13733 | -0.073242 | -0.054932 | 0.15106 | -0.1236 | -0.064087 | 0.059509 | -0.004578 | 0.041199 | 122.1542 | -0.013733 | -0.30212 | 122.319 | 122.2366 | 122.1725 | 0.082398 | 0.018311 | 122.1863 | 0.022888 | -0.19226 | 122.3694 | 122.3511 | 122.3053 | 0.16479 | 0.11902 | 0.16479 | -0.01831 | 0.1831 | 0.059509 | 0.27008 | 0.27466 | 122.4243 | 122.4609 | -0.28381 | -0.25177 | 122.1359 | 122.2458 | 122.1588 | 122.2549
3687.5469 | 122.4426 | -122.3145 | 0.12817 | 0.0025177 | -0.0096707 | -0.076447 | -0.0029201 | -0.028734 | -0.050595 | -0.039751 | -0.0021057 | 0.0044584 | 0.0077076 | -0.013339 | -0.21958 | -0.018342 | -0.021971 | -0.09613 | 0.11902 | -0.15564 | -0.15564 | -0.013733 | -0.17853 | -0.082397 | -0.041199 | 0.11902 | -0.1236 | -0.045776 | 0.022888 | -0.032043 | 0.032043 | 122.1588 | -0.009155 | -0.28381 | 122.3007 | 122.2321 | 122.1359 | 0.073243 | -0.022888 | 122.1909 | -0.009155 | -0.17395 | 122.3373 | 122.3465 | 122.2824 | 0.15564 | 0.091553 | 0.14191 | 0 | 0.14648 | 0.07782 | 0.27466 | 0.24261 | 122.4335 | 122.4335 | -0.28381 | -0.25177 | 122.1588 | 122.2687 | 122.2183 | 122.2733
3689.2656 | 122.6028 | -122.2778 | 0.091553 | 0.0025177 | -0.015225 | -0.07837 | -0.0093289 | -0.032366 | -0.048245 | -0.044878 | 0.00094606 | 0.0031766 | 0.0079212 | -0.015902 | -0.22022 | -0.023041 | -0.024535 | -0.054932 | 0.068665 | -0.10071 | -0.036621 | 0.16479 | -0.018311 | 0.036621 | 0.13733 | 0.10071 | -0.082397 | 0.07782 | 0.20142 | 0.15564 | 0.13733 | 122.1771 | -0.022888 | -0.12817 | 122.4426 | 122.3145 | 122.2595 | 0.13733 | 0.082397 | 122.1954 | 0.009155 | -0.013733 | 122.4792 | 122.4152 | 122.4335 | 0.21973 | 0.23804 | 0.2655 | 0.064087 | 0.28381 | 0.16022 | 0.16937 | 0.18311 | 122.3465 | 122.3785 | -0.19226 | -0.17395 | 122.2412 | 122.3557 | 122.2229 | 122.4152
3691.0781 | 122.5983 | -122.2916 | 0.091553 | 0.0025177 | -0.017361 | -0.079224 | -0.0078335 | -0.03258 | -0.051235 | -0.039537 | 0.00094606 | 0.0036038 | 0.007494 | -0.016116 | -0.2215 | -0.019837 | -0.023039 | -0.091553 | 0.082397 | -0.10071 | -0.050354 | 0.14648 | -0.018311 | 0.059509 | 0.13733 | 0.10529 | -0.086975 | 0.064087 | 0.21057 | 0.13275 | 0.16022 | 122.1909 | -0.009156 | -0.14191 | 122.438 | 122.3511 | 122.2733 | 0.16022 | 0.082397 | 122.2046 | 0.013733 | -0.027466 | 122.5021 | 122.4518 | 122.4243 | 0.24719 | 0.21973 | 0.24719 | 0.050354 | 0.29755 | 0.15106 | 0.18311 | 0.19226 | 122.374 | 122.3969 | -0.19226 | -0.17853 | 122.2412 | 122.3557 | 122.2 | 122.4289
3692.875 | 122.4747 | -122.3236 | 0.1236 | -0.0051118 | -0.0098843 | -0.07837 | -0.0050565 | -0.027453 | -0.051876 | -0.039965 | 0.00094606 | 0.00574 | 0.0094166 | -0.0047936 | -0.22022 | -0.01706 | -0.020903 | -0.082397 | 0.10071 | -0.13733 | -0.11902 | 0.022888 | -0.14191 | -0.054932 | 0.022888 | 0.13733 | -0.11902 | -0.022888 | 0.054932 | -0.018311 | 0.045776 | 122.1863 | -0.022888 | -0.24261 | 122.3465 | 122.2687 | 122.1817 | 0.082397 | -0.004578 | 122.2046 | 0.013733 | -0.14648 | 122.3785 | 122.3694 | 122.3053 | 0.16479 | 0.10071 | 0.16022 | 0.01831 | 0.17395 | 0.096131 | 0.23804 | 0.25635 | 122.4243 | 122.4609 | -0.26093 | -0.24261 | 122.2046 | 122.3007 | 122.2412 | 122.3465
3694.6719 | 122.4747 | -122.3282 | 0.12817 | 0.0025177 | -0.015652 | -0.080719 | -0.0074063 | -0.024248 | -0.052304 | -0.043169 | -0.0021057 | 0.0010404 | 0.007494 | -0.012911 | -0.21958 | -0.018342 | -0.023467 | -0.14648 | 0.1236 | -0.15106 | -0.17853 | -0.013733 | -0.13733 | -0.068665 | -0.054932 | 0.14648 | -0.12817 | -0.050354 | 0.059509 | -0.004578 | 0.041199 | 122.1771 | -0.004578 | -0.3067 | 122.3145 | 122.2595 | 122.1909 | 0.082397 | 0.013733 | 122.2 | 0.01831 | -0.17853 | 122.3877 | 122.3694 | 122.3236 | 0.16937 | 0.1236 | 0.13733 | -0.027466 | 0.18768 | 0.07782 | 0.27466 | 0.27466 | 122.4518 | 122.4747 | -0.27924 | -0.25635 | 122.1497 | 122.2778 | 122.1817 | 122.2733
3696.4688 | 122.5708 | -122.3145 | 0.07782 | -0.0051118 | -0.013729 | -0.077729 | -0.0078335 | -0.035143 | -0.051235 | -0.042955 | -0.0021057 | 0.0010404 | 0.0066394 | -0.021029 | -0.21894 | -0.019623 | -0.025603 | -0.11444 | 0.082397 | -0.11902 | -0.10071 | 0.036621 | -0.10529 | -0.004578 | 0.022888 | 0.10986 | -0.10529 | 0.018311 | 0.14191 | 0.07782 | 0.10529 | 122.1954 | 0.004577 | -0.17853 | 122.3511 | 122.3099 | 122.2092 | 0.11444 | 0.013733 | 122.2092 | 0.032043 | -0.059509 | 122.4564 | 122.4197 | 122.3923 | 0.21057 | 0.18311 | 0.15564 | 0.018311 | 0.24719 | 0.1236 | 0.20142 | 0.21515 | 122.3969 | 122.4243 | -0.19684 | -0.18311 | 122.2137 | 122.3328 | 122.2 | 122.3373
3698.1875 | 122.5159 | -122.3282 | 0.11902 | 0.0025177 | -0.0094571 | -0.079865 | -0.0044155 | -0.031084 | -0.049313 | -0.039965 | -0.0021057 | 0.00574 | 0.0092028 | -0.0092798 | -0.22001 | -0.016419 | -0.024748 | -0.07782 | 0.11444 | -0.12817 | -0.11902 | 0.045776 | -0.11902 | -0.045776 | 0.041199 | 0.13733 | -0.10986 | 0.004578 | 0.091553 | 0.004578 | 0.09613 | 122.2 | -0.004578 | -0.23804 | 122.374 | 122.2824 | 122.2092 | 0.082398 | 0.009155 | 122.2183 | 0.01831 | -0.11444 | 122.4197 | 122.4243 | 122.3328 | 0.20599 | 0.11444 | 0.17395 | 0.009155 | 0.20142 | 0.11444 | 0.24262 | 0.24719 | 122.4426 | 122.4655 | -0.24719 | -0.22888 | 122.2092 | 122.3328 | 122.2504 | 122.3694
3700 | 122.4747 | -122.3419 | 0.11902 | -0.012741 | -0.012661 | -0.078797 | -0.0065517 | -0.029589 | -0.05209 | -0.045305 | -0.0021057 | 0.0055264 | 0.0079212 | -0.015688 | -0.22086 | -0.021119 | -0.026457 | -0.13275 | 0.11444 | -0.14191 | -0.16937 | 0 | -0.14648 | -0.073242 | -0.027466 | 0.14648 | -0.13733 | -0.064087 | 0.054932 | -0.009155 | 0.045776 | 122.2 | -0.004578 | -0.28839 | 122.3419 | 122.2687 | 122.1954 | 0.068665 | -0.004577 | 122.2046 | 0.027465 | -0.18311 | 122.3969 | 122.3877 | 122.3328 | 0.18311 | 0.12817 | 0.14191 | -0.027466 | 0.19226 | 0.073242 | 0.25635 | 0.28381 | 122.4564 | 122.4884 | -0.26093 | -0.25635 | 122.1725 | 122.2778 | 122.2092 | 122.3145
3701.7969 | 122.4701 | -122.3328 | 0.1236 | -0.012741 | -0.01138 | -0.076874 | -0.0056973 | -0.029589 | -0.048672 | -0.041033 | -0.0051575 | 0.0038174 | 0.006853 | -0.0094934 | -0.22236 | -0.019196 | -0.022826 | -0.11902 | 0.1236 | -0.13733 | -0.19226 | -0.064087 | -0.21057 | -0.09613 | -0.045776 | 0.13733 | -0.12817 | -0.045776 | 0.022888 | -0.050354 | 0.032043 | 122.1954 | 0 | -0.31586 | 122.2687 | 122.2366 | 122.1222 | 0.041199 | -0.073242 | 122.2046 | 0.013733 | -0.16937 | 122.3557 | 122.3648 | 122.2824 | 0.16022 | 0.07782 | 0.073242 | -0.054932 | 0.15106 | 0.082398 | 0.26093 | 0.2655 | 122.4564 | 122.4701 | -0.26093 | -0.25177 | 122.1405 | 122.287 | 122.2137 | 122.287
3703.6094 | 122.493 | -122.3328 | 0.12817 | 0.0025177 | -0.0096707 | -0.080506 | -0.0061245 | -0.030871 | -0.050381 | -0.042528 | -0.0021057 | 0.002963 | 0.0072802 | -0.01163 | -0.22043 | -0.018555 | -0.023894 | -0.086975 | 0.11444 | -0.11444 | -0.11902 | 0.045776 | -0.14648 | -0.059509 | 0.022888 | 0.14191 | -0.13275 | -0.013733 | 0.068665 | 0.004578 | 0.068665 | 122.2183 | -0.013733 | -0.24719 | 122.3785 | 122.2733 | 122.1863 | 0.054932 | -0.032043 | 122.2 | 0.013733 | -0.14191 | 122.4014 | 122.4014 | 122.3373 | 0.20142 | 0.13733 | 0.16022 | -0.004578 | 0.20142 | 0.11902 | 0.22888 | 0.27466 | 122.4472 | 122.4747 | -0.24262 | -0.26093 | 122.2137 | 122.319 | 122.2458 | 122.3557
3705.3906 | 122.5571 | -122.3694 | 0.10529 | 0.0025177 | -0.013943 | -0.079011 | -0.0078335 | -0.030871 | -0.050167 | -0.040392 | -0.0021057 | 0.002963 | 0.0079212 | -0.020175 | -0.21766 | -0.018769 | -0.023894 | -0.064087 | 0.09613 | -0.10986 | -0.068665 | 0.13275 | -0.045776 | 0.022888 | 0.068665 | 0.10529 | -0.10986 | 0.027466 | 0.14648 | 0.073242 | 0.10071 | 122.2595 | -0.009156 | -0.17395 | 122.5021 | 122.3923 | 122.3236 | 0.13275 | 0.064087 | 122.2595 | 0 | -0.07782 | 122.5159 | 122.4701 | 122.4426 | 0.21057 | 0.18311 | 0.24261 | 0.041198 | 0.25635 | 0.13733 | 0.20599 | 0.21515 | 122.4655 | 122.4747 | -0.21515 | -0.21515 | 122.3007 | 122.3969 | 122.3053 | 122.438
3707.125 | 122.5342 | -122.3602 | 0.10986 | 0.0025177 | -0.010311 | -0.080719 | -0.0048427 | -0.029162 | -0.051876 | -0.041033 | -0.0051575 | 0.0053128 | 0.0070666 | -0.01697 | -0.21915 | -0.018128 | -0.02133 | -0.086975 | 0.11444 | -0.1236 | -0.10986 | 0.032043 | -0.12817 | -0.036621 | 0.018311 | 0.14191 | -0.11444 | 0 | 0.10986 | 0.018311 | 0.091553 | 122.2366 | 0.004578 | -0.21973 | 122.3923 | 122.3236 | 122.2321 | 0.086975 | -0.004578 | 122.2458 | 0.032044 | -0.10986 | 122.4701 | 122.4518 | 122.3785 | 0.20599 | 0.13275 | 0.15564 | 0.013733 | 0.2243 | 0.11444 | 0.23804 | 0.25635 | 122.4747 | 122.5021 | -0.23346 | -0.2243 | 122.2504 | 122.3602 | 122.2733 | 122.3785
3708.9375 | 122.6074 | -122.3236 | 0.091553 | 0.0025177 | -0.014157 | -0.080292 | -0.0074063 | -0.034502 | -0.051876 | -0.041246 | -0.0021057 | 0.001254 | 0.0066394 | -0.017184 | -0.21723 | -0.020691 | -0.023253 | -0.10986 | 0.09613 | -0.12817 | -0.082397 | 0.082397 | -0.073242 | 0 | 0.050354 | 0.091553 | -0.10986 | 0.050354 | 0.16937 | 0.11444 | 0.12817 | 122.1954 | 0.004577 | -0.17395 | 122.406 | 122.3236 | 122.2504 | 0.12817 | 0.054932 | 122.2137 | 0 | -0.041199 | 122.493 | 122.4518 | 122.438 | 0.23804 | 0.2243 | 0.21057 | 0.045777 | 0.27924 | 0.16022 | 0.2243 | 0.20142 | 122.4197 | 122.4152 | -0.21973 | -0.20142 | 122.2412 | 122.374 | 122.2137 | 122.374
3710.6719 | 122.5021 | -122.374 | 0.1236 | -0.0051118 | -0.0094571 | -0.079011 | -0.0022793 | -0.029589 | -0.051022 | -0.041674 | -0.0021057 | 0.004672 | 0.0059986 | -0.01163 | -0.21915 | -0.017701 | -0.022398 | -0.10529 | 0.11902 | -0.13275 | -0.17853 | -0.045776 | -0.20142 | -0.10529 | -0.059509 | 0.14648 | -0.1236 | -0.032043 | 0.036621 | -0.036621 | 0.050354 | 122.2412 | -0.004577 | -0.30212 | 122.3282 | 122.2687 | 122.1725 | 0.027465 | -0.068665 | 122.2504 | 0.022888 | -0.15564 | 122.4106 | 122.4243 | 122.3373 | 0.17395 | 0.086975 | 0.086975 | -0.045777 | 0.16022 | 0.091553 | 0.25177 | 0.27008 | 122.493 | 122.5204 | -0.25635 | -0.24719 | 122.1954 | 122.3419 | 122.2687 | 122.3145
3712.4531 | 122.6303 | -122.3145 | 0.086975 | -0.02037 | -0.0088163 | -0.077515 | -0.0061245 | -0.031298 | -0.048672 | -0.044023 | 0.00094606 | 0.0038174 | 0.007494 | -0.017184 | -0.21894 | -0.018555 | -0.024748 | -0.082397 | 0.09613 | -0.10986 | -0.064087 | 0.082397 | -0.07782 | -0.009155 | 0.091553 | 0.10529 | -0.09613 | 0.07782 | 0.17395 | 0.10986 | 0.15564 | 122.2046 | 0.009155 | -0.15106 | 122.3969 | 122.3053 | 122.2366 | 0.10071 | 0.032043 | 122.2183 | 0.018311 | -0.009155 | 122.4884 | 122.4701 | 122.4243 | 0.25177 | 0.20599 | 0.19226 | 0.045776 | 0.27008 | 0.17395 | 0.20599 | 0.20142 | 122.4106 | 122.4197 | -0.19684 | -0.1831 | 122.2504 | 122.3923 | 122.2321 | 122.406
3714.1719 | 122.5204 | -122.3557 | 0.11902 | -0.012741 | -0.010952 | -0.079651 | -0.0063381 | -0.031298 | -0.051022 | -0.043383 | 0.0039979 | 0.0053128 | 0.007494 | -0.0094934 | -0.2183 | -0.017914 | -0.019621 | -0.10986 | 0.10986 | -0.14648 | -0.17853 | -0.032043 | -0.1831 | -0.091553 | -0.032043 | 0.13275 | -0.1236 | -0.032043 | 0.054932 | -0.032043 | 0.059509 | 122.2092 | -0.009156 | -0.29755 | 122.3236 | 122.2641 | 122.1725 | 0.054931 | -0.036621 | 122.2321 | 0.013732 | -0.15106 | 122.4106 | 122.4152 | 122.3236 | 0.1831 | 0.091553 | 0.11444 | -0.032044 | 0.17853 | 0.091553 | 0.25635 | 0.25635 | 122.4655 | 122.4884 | -0.2655 | -0.24261 | 122.1771 | 122.3236 | 122.2458 | 122.3236
3715.9688 | 122.6395 | -122.3053 | 0.086975 | -0.0051118 | -0.010525 | -0.077088 | -0.0063381 | -0.022326 | -0.048672 | -0.041887 | 0.00094606 | 0.0023222 | 0.005144 | -0.013552 | -0.22086 | -0.019196 | -0.022398 | -0.054932 | 0.07782 | -0.082397 | -0.036621 | 0.12817 | -0.068665 | 0.013733 | 0.1236 | 0.086975 | -0.082397 | 0.09613 | 0.18768 | 0.11444 | 0.15564 | 122.2229 | -0.009155 | -0.1236 | 122.4335 | 122.319 | 122.2366 | 0.09613 | 0.013732 | 122.2229 | 0 | 0.009155 | 122.493 | 122.4609 | 122.4197 | 0.23804 | 0.19684 | 0.21057 | 0.045776 | 0.27008 | 0.17853 | 0.16022 | 0.16937 | 122.3831 | 122.3923 | -0.16937 | -0.16937 | 122.2687 | 122.4014 | 122.2504 | 122.4289
3717.7656 | 122.4747 | -122.3831 | 0.13733 | -0.0051118 | -0.0086027 | -0.078156 | -0.0042019 | -0.025744 | -0.04974 | -0.044023 | 0.00094606 | 0.004672 | 0.0059986 | -0.014193 | -0.22001 | -0.018769 | -0.024321 | -0.10071 | 0.13275 | -0.14191 | -0.16022 | -0.041199 | -0.20142 | -0.11902 | -0.050354 | 0.14191 | -0.13275 | -0.045776 | 0 | -0.054932 | 0.036621 | 122.2412 | -0.004578 | -0.29755 | 122.3419 | 122.2641 | 122.1817 | 0.022888 | -0.059509 | 122.2504 | 0.004578 | -0.18311 | 122.3831 | 122.4197 | 122.3282 | 0.16937 | 0.077819 | 0.10071 | -0.01831 | 0.13275 | 0.086975 | 0.27466 | 0.27466 | 122.5159 | 122.525 | -0.27924 | -0.27008 | 122.2229 | 122.3373 | 122.2824 | 122.3328
3719.5 | 122.5525 | -122.3785 | 0.11444 | -0.0051118 | -0.016079 | -0.080079 | -0.0089017 | -0.032366 | -0.052944 | -0.041033 | 0.0039979 | 0.00039959 | 0.0081348 | -0.022311 | -0.21872 | -0.018555 | -0.021971 | -0.086975 | 0.09613 | -0.11444 | -0.068665 | 0.091553 | -0.059509 | 0.009155 | 0.036621 | 0.10071 | -0.10529 | -0.022888 | 0.10529 | 0.045776 | 0.073242 | 122.2641 | -0.018311 | -0.18311 | 122.4701 | 122.3877 | 122.319 | 0.1236 | 0.054932 | 122.2733 | -0.013733 | -0.13733 | 122.4838 | 122.4518 | 122.4243 | 0.17853 | 0.15106 | 0.20599 | 0.045776 | 0.21057 | 0.082398 | 0.21057 | 0.20599 | 122.4747 | 122.4792 | -0.22888 | -0.21973 | 122.3099 | 122.3557 | 122.2916 | 122.4152
3721.2969 | 122.5571 | -122.3831 | 0.13275 | 0.0025177 | -0.015011 | -0.079224 | -0.0035611 | -0.029589 | -0.050381 | -0.042314 | -0.0082091 | 0.0048856 | 0.0077076 | -0.0067162 | -0.21979 | -0.017273 | -0.021971 | -0.12817 | 0.11902 | -0.15106 | -0.17395 | -0.027466 | -0.15106 | -0.064087 | -0.064087 | 0.13733 | -0.14191 | -0.050354 | 0.059509 | 0.004578 | 0.050354 | 122.2321 | -0.013732 | -0.3067 | 122.3557 | 122.319 | 122.2321 | 0.086975 | 0 | 122.2412 | 0.004578 | -0.18311 | 122.4426 | 122.4335 | 122.3877 | 0.19226 | 0.14649 | 0.1236 | -0.022888 | 0.20142 | 0.091553 | 0.27008 | 0.27924 | 122.5021 | 122.5204 | -0.28381 | -0.27466 | 122.2092 | 122.3328 | 122.2549 | 122.319
3723.1094 | 122.5754 | -122.3694 | 0.11902 | -0.0051118 | -0.013729 | -0.079438 | -0.0059109 | -0.031511 | -0.051022 | -0.040605 | 0.00094606 | 0.0042448 | 0.0087756 | -0.0092798 | -0.21937 | -0.018769 | -0.023467 | -0.1236 | 0.1236 | -0.14191 | -0.15106 | -0.013733 | -0.14648 | -0.07782 | -0.032043 | 0.14648 | -0.13275 | -0.004578 | 0.073242 | 0.032043 | 0.086975 | 122.2275 | 0.004577 | -0.27008 | 122.3557 | 122.2916 | 122.2229 | 0.064087 | -0.004577 | 122.2366 | 0.027465 | -0.1236 | 122.4426 | 122.4564 | 122.4014 | 0.21973 | 0.16479 | 0.12817 | -0.009155 | 0.20599 | 0.12817 | 0.2655 | 0.27924 | 122.493 | 122.5159 | -0.26093 | -0.25177 | 122.2183 | 122.3648 | 122.2458 | 122.3373
3727.5781 | 122.6624 | -122.3602 | 0.064087 | 0.0025177 | -0.011593 | -0.080079 | -0.0097561 | -0.029802 | -0.051663 | -0.044023 | 0.00094606 | 0.0025358 | 0.0059986 | -0.018893 | -0.21851 | -0.018769 | -0.023039 | -0.086975 | 0.086975 | -0.11902 | -0.068665 | 0.11902 | -0.050354 | 0.032043 | 0.064087 | 0.10529 | -0.09613 | 0.073242 | 0.19226 | 0.15106 | 0.15564 | 122.2412 | 0.022888 | -0.13275 | 122.4792 | 122.3923 | 122.3099 | 0.15106 | 0.068665 | 122.2641 | 0.041199 | 0.009155 | 122.5525 | 122.5159 | 122.5113 | 0.25177 | 0.24719 | 0.23804 | 0.050354 | 0.28839 | 0.16937 | 0.20599 | 0.20142 | 122.4472 | 122.4655 | -0.18311 | -0.16022 | 122.2916 | 122.4335 | 122.2733 | 122.4243
3729.625 | 122.612 | -122.3694 | 0.11902 | 0.0025177 | -0.0098843 | -0.079011 | -0.0069791 | -0.026812 | -0.048245 | -0.038469 | -0.0021057 | 0.0038174 | 0.0094166 | -0.011843 | -0.22086 | -0.018769 | -0.023894 | -0.1236 | 0.10986 | -0.14191 | -0.13275 | 0.013733 | -0.17853 | -0.064087 | 0.009155 | 0.11902 | -0.10529 | 0.036621 | 0.10986 | 0.050354 | 0.11444 | 122.2275 | -0.009156 | -0.25177 | 122.3831 | 122.3053 | 122.1909 | 0.07782 | -0.036621 | 122.2641 | 0 | -0.082398 | 122.4792 | 122.4838 | 122.4197 | 0.21973 | 0.15564 | 0.15564 | 0.009156 | 0.21515 | 0.14191 | 0.25177 | 0.22431 | 122.4792 | 122.4884 | -0.26093 | -0.22431 | 122.2366 | 122.406 | 122.2458 | 122.3785
3732.25 | 122.6761 | -122.3877 | 0.09613 | -0.0051118 | -0.013516 | -0.07837 | -0.0084743 | -0.027666 | -0.051663 | -0.041674 | 0.00094606 | 0.0025358 | 0.0094166 | -0.014193 | -0.21958 | -0.019837 | -0.023039 | -0.10071 | 0.10071 | -0.11902 | -0.07782 | 0.086975 | -0.054932 | 0.032043 | 0.073242 | 0.10071 | -0.10986 | 0.059509 | 0.1831 | 0.13733 | 0.15564 | 122.2687 | 0.004578 | -0.17395 | 122.4747 | 122.4197 | 122.3328 | 0.15106 | 0.064087 | 122.2778 | 0.004578 | -0.036621 | 122.5708 | 122.5433 | 122.525 | 0.2655 | 0.24719 | 0.20599 | 0.041199 | 0.29297 | 0.16937 | 0.21973 | 0.21057 | 122.4884 | 122.4884 | -0.21515 | -0.20599 | 122.3099 | 122.4472 | 122.287 | 122.4609
3734.1406 | 122.5113 | -122.4197 | 0.1236 | -0.0051118 | -0.0096707 | -0.079011 | -0.0039883 | -0.027453 | -0.050808 | -0.040605 | -0.0021057 | 0.0048856 | 0.006853 | -0.015048 | -0.21894 | -0.019837 | -0.026885 | -0.1236 | 0.11444 | -0.14648 | -0.16937 | -0.032043 | -0.20142 | -0.10986 | -0.07782 | 0.14648 | -0.13733 | -0.041199 | 0.009155 | -0.068665 | 0.041199 | 122.2733 | -0.009155 | -0.29297 | 122.3877 | 122.3099 | 122.2183 | 0.036621 | -0.054932 | 122.2824 | 0.022888 | -0.16479 | 122.4289 | 122.4609 | 122.3511 | 0.17853 | 0.068664 | 0.11444 | -0.022889 | 0.14648 | 0.09613 | 0.26093 | 0.28381 | 122.5342 | 122.5662 | -0.27008 | -0.26093 | 122.2504 | 122.3785 | 122.2961 | 122.3419
3735.9375 | 122.5433 | -122.4289 | 0.1236 | -0.0051118 | -0.013089 | -0.078797 | -0.0074063 | -0.030016 | -0.051235 | -0.04146 | -0.0021057 | 0.0018948 | 0.0089892 | -0.009707 | -0.21915 | -0.018128 | -0.021971 | -0.091553 | 0.09613 | -0.1236 | -0.14191 | 0.013733 | -0.13733 | -0.064087 | -0.027466 | 0.13275 | -0.13275 | -0.045776 | 0.064087 | 0 | 0.032043 | 122.3053 | -0.027466 | -0.2655 | 122.4426 | 122.3648 | 122.2916 | 0.059509 | -0.013733 | 122.2961 | 0.009155 | -0.16937 | 122.493 | 122.4609 | 122.4289 | 0.16479 | 0.13275 | 0.13733 | -0.018311 | 0.19684 | 0.086975 | 0.21973 | 0.2655 | 122.525 | 122.5616 | -0.24719 | -0.25635 | 122.287 | 122.3831 | 122.3373 | 122.4014
3737.7656 | 122.6257 | -122.3923 | 0.10071 | 0.0025177 | -0.012234 | -0.079651 | -0.0059109 | -0.032793 | -0.049313 | -0.044451 | -0.0021057 | 0.0018948 | 0.0081348 | -0.0092798 | -0.22129 | -0.020905 | -0.027525 | -0.091553 | 0.091553 | -0.10986 | -0.10986 | 0.068665 | -0.11444 | -0.004578 | 0.027466 | 0.10071 | -0.10071 | 0.004578 | 0.13275 | 0.059509 | 0.086975 | 122.2824 | -0.009155 | -0.21057 | 122.4609 | 122.3877 | 122.2778 | 0.10529 | -0.004578 | 122.2916 | 0 | -0.09613 | 122.525 | 122.4792 | 122.4518 | 0.18768 | 0.16022 | 0.17853 | 0 | 0.23346 | 0.10529 | 0.20142 | 0.20142 | 122.4838 | 122.493 | -0.21057 | -0.20142 | 122.2824 | 122.3969 | 122.3007 | 122.4197
3739.6094 | 122.5479 | -122.4243 | 0.11902 | -0.0051118 | -0.011166 | -0.078583 | -0.0048427 | -0.029802 | -0.052304 | -0.040819 | 0.00094606 | 0.002963 | 0.0083484 | -0.0065026 | -0.22193 | -0.018128 | -0.023039 | -0.12817 | 0.12817 | -0.16479 | -0.19684 | -0.059509 | -0.20599 | -0.10986 | -0.068665 | 0.14191 | -0.09613 | -0.032043 | 0.018311 | -0.050354 | 0.050354 | 122.2595 | 0.009155 | -0.31586 | 122.3648 | 122.3145 | 122.2183 | 0.054932 | -0.041199 | 122.3282 | 0.022888 | -0.15106 | 122.4426 | 122.4747 | 122.374 | 0.14648 | 0.045776 | 0.10529 | -0.032043 | 0.11444 | 0.064087 | 0.29297 | 0.23804 | 122.5525 | 122.5662 | -0.28381 | -0.21515 | 122.2275 | 122.3923 | 122.2961 | 122.3557
3741.4062 | 122.6303 | -122.3877 | 0.091553 | -0.0051118 | -0.01202 | -0.077729 | -0.0074063 | -0.03023 | -0.051022 | -0.043383 | -0.0021057 | 0.0018948 | 0.0072802 | -0.016543 | -0.22001 | -0.018769 | -0.023039 | -0.10986 | 0.082397 | -0.10986 | -0.091553 | 0.064087 | -0.10071 | -0.009155 | 0.032043 | 0.10071 | -0.11444 | 0.018311 | 0.11902 | 0.064087 | 0.11444 | 122.2778 | -0.009156 | -0.18311 | 122.4518 | 122.3785 | 122.287 | 0.10071 | 0.009155 | 122.2733 | 0.009155 | -0.073242 | 122.5067 | 122.5021 | 122.4518 | 0.22888 | 0.17853 | 0.17395 | 0.01831 | 0.23346 | 0.13275 | 0.19226 | 0.21515 | 122.4701 | 122.4884 | -0.20142 | -0.20599 | 122.2961 | 122.406 | 122.2778 | 122.4197
3743.2812 | 122.6761 | -122.3648 | 0.10986 | 0.010147 | -0.01138 | -0.078156 | -0.0044155 | -0.028307 | -0.049099 | -0.04146 | -0.0051575 | 0.0038174 | 0.0055712 | -0.0099206 | -0.21851 | -0.017914 | -0.023894 | -0.1236 | 0.11444 | -0.13275 | -0.10071 | 0.041199 | -0.14648 | -0.032043 | 0.064087 | 0.10986 | -0.10071 | 0.07782 | 0.16022 | 0.086975 | 0.14648 | 122.2321 | 0.004578 | -0.21057 | 122.406 | 122.3328 | 122.2183 | 0.10071 | -0.013733 | 122.2641 | 0 | -0.032043 | 122.525 | 122.5113 | 122.4518 | 0.24719 | 0.18768 | 0.17395 | 0.032043 | 0.26093 | 0.17853 | 0.24719 | 0.21057 | 122.4792 | 122.4747 | -0.24261 | -0.21057 | 122.2641 | 122.4426 | 122.2412 | 122.4289
3745.0625 | 122.6807 | -122.3831 | 0.064087 | -0.012741 | -0.012234 | -0.077302 | -0.0056973 | -0.026598 | -0.05209 | -0.041033 | 0.0039979 | 0.0031766 | 0.0072802 | -0.011416 | -0.22065 | -0.019196 | -0.022185 | -0.09613 | 0.11902 | -0.13275 | -0.10529 | 0.032043 | -0.15106 | -0.027466 | 0.064087 | 0.11902 | -0.10071 | 0.082397 | 0.15564 | 0.091553 | 0.13733 | 122.2504 | 0.054932 | -0.16937 | 122.4152 | 122.3557 | 122.2321 | 0.10529 | -0.018311 | 122.2824 | 0.054932 | 0.01831 | 122.5388 | 122.5204 | 122.4747 | 0.23804 | 0.19226 | 0.16479 | 0.027465 | 0.25635 | 0.18311 | 0.25177 | 0.21973 | 122.5021 | 122.5021 | -0.19684 | -0.1648 | 122.2778 | 122.4655 | 122.287 | 122.4472
3746.8438 | 122.6028 | -122.4197 | 0.13275 | 0.0025177 | -0.013516 | -0.079651 | -0.0048427 | -0.030016 | -0.050808 | -0.042742 | -0.0021057 | 0.0027494 | 0.0081348 | -0.015048 | -0.22022 | -0.017914 | -0.024748 | -0.12817 | 0.10986 | -0.16022 | -0.15106 | -0.018311 | -0.14191 | -0.064087 | -0.045776 | 0.16022 | -0.13275 | -0.022888 | 0.07782 | 0.022888 | 0.068665 | 122.2595 | -0.022888 | -0.28381 | 122.4014 | 122.3557 | 122.2778 | 0.09613 | 0.01831 | 122.287 | 0.027466 | -0.15564 | 122.4976 | 122.4884 | 122.4426 | 0.20142 | 0.15564 | 0.14191 | 0.009155 | 0.21057 | 0.10986 | 0.27008 | 0.29297 | 122.5296 | 122.58 | -0.29297 | -0.2655 | 122.2687 | 122.3969 | 122.2916 | 122.374
3748.7188 | 122.6624 | -122.4197 | 0.073242 | -0.012741 | -0.012661 | -0.079865 | -0.0076199 | -0.033007 | -0.049526 | -0.040392 | -0.0051575 | 0.0023222 | 0.0045032 | -0.018252 | -0.21937 | -0.018982 | -0.02133 | -0.10071 | 0.10071 | -0.11902 | -0.09613 | 0.064087 | -0.086975 | 0.004578 | 0.036621 | 0.10529 | -0.10071 | 0.041199 | 0.16479 | 0.09613 | 0.11444 | 122.3007 | 0.027466 | -0.16937 | 122.4838 | 122.4243 | 122.3328 | 0.1236 | 0.032044 | 122.319 | 0.032044 | -0.032043 | 122.5845 | 122.5342 | 122.5159 | 0.21515 | 0.19684 | 0.18311 | 0.022889 | 0.2655 | 0.14191 | 0.21973 | 0.20599 | 122.5204 | 122.525 | -0.19226 | -0.17395 | 122.3236 | 122.4609 | 122.319 | 122.4564
3750.5469 | 122.7036 | -122.3969 | 0.064087 | 0.0025177 | -0.015866 | -0.081788 | -0.0067653 | -0.031939 | -0.052517 | -0.042101 | -0.0051575 | 0.0016812 | 0.0059986 | -0.01163 | -0.22065 | -0.017914 | -0.025603 | -0.068665 | 0.082397 | -0.09613 | -0.013733 | 0.16479 | -0.018311 | 0.054932 | 0.11902 | 0.11444 | -0.091553 | 0.068665 | 0.21057 | 0.14191 | 0.14648 | 122.3007 | 0.01831 | -0.07782 | 122.5616 | 122.4518 | 122.3785 | 0.15106 | 0.077819 | 122.3053 | 0.050354 | 0.004578 | 122.6074 | 122.5433 | 122.5388 | 0.23804 | 0.23346 | 0.26092 | 0.082397 | 0.30212 | 0.16022 | 0.17853 | 0.20599 | 122.4792 | 122.5113 | -0.16022 | -0.15564 | 122.3831 | 122.4655 | 122.3282 | 122.5159
3752.2969 | 122.6852 | -122.4014 | 0.082397 | 0.0025177 | -0.01202 | -0.079011 | -0.0069791 | -0.032366 | -0.051022 | -0.044237 | -0.0021057 | 0.0025358 | 0.0062122 | -0.014193 | -0.21851 | -0.01941 | -0.023467 | -0.041199 | 0.086975 | -0.091553 | -0.018311 | 0.13733 | -0.068665 | 0.022888 | 0.12817 | 0.091553 | -0.10071 | 0.082397 | 0.16937 | 0.10071 | 0.14648 | 122.3099 | 0.004578 | -0.10071 | 122.5388 | 122.4243 | 122.3328 | 0.11444 | 0.022888 | 122.3007 | 0.009156 | 0 | 122.5708 | 122.5479 | 122.5021 | 0.24719 | 0.20142 | 0.22888 | 0.073242 | 0.27008 | 0.18311 | 0.17853 | 0.19226 | 122.4884 | 122.493 | -0.17395 | -0.18311 | 122.3831 | 122.4838 | 122.3602 | 122.5296
3754.0938 | 122.5708 | -122.4564 | 0.11902 | -0.012741 | -0.0094571 | -0.078583 | -0.0033475 | -0.030657 | -0.049099 | -0.03911 | 0.00094606 | 0.006381 | 0.0087756 | -0.011416 | -0.22065 | -0.018555 | -0.024107 | -0.13733 | 0.11902 | -0.15106 | -0.1831 | -0.07782 | -0.23346 | -0.10529 | -0.059509 | 0.1236 | -0.13275 | -0.041199 | 0.027466 | -0.045776 | 0.059509 | 122.3053 | 0 | -0.30212 | 122.3785 | 122.3511 | 122.2229 | 0.045776 | -0.082397 | 122.3236 | 0.004577 | -0.16022 | 122.4838 | 122.5159 | 122.4106 | 0.19226 | 0.086975 | 0.073242 | -0.032043 | 0.16022 | 0.091552 | 0.27008 | 0.25635 | 122.5754 | 122.58 | -0.27008 | -0.25177 | 122.2733 | 122.4152 | 122.319 | 122.3969
3755.9219 | 122.6624 | -122.4197 | 0.091553 | 0.0025177 | -0.011593 | -0.076874 | -0.0063381 | -0.034289 | -0.049526 | -0.038896 | -0.0021057 | 0.0018948 | 0.0077076 | -0.014834 | -0.21937 | -0.018342 | -0.022826 | -0.064087 | 0.07782 | -0.10071 | -0.064087 | 0.10986 | -0.086975 | -0.004578 | 0.082397 | 0.10071 | -0.091553 | 0.045776 | 0.13733 | 0.064087 | 0.10986 | 122.319 | -0.013733 | -0.15564 | 122.5296 | 122.4152 | 122.3328 | 0.09613 | 0.013733 | 122.3282 | 0.009155 | -0.045777 | 122.5571 | 122.5296 | 122.4838 | 0.20142 | 0.15564 | 0.21057 | 0.036621 | 0.22888 | 0.13733 | 0.17853 | 0.19226 | 122.4976 | 122.5204 | -0.19226 | -0.18311 | 122.3557 | 122.4655 | 122.3557 | 122.5021
3758.6094 | 122.7402 | -122.406 | 0.091553 | -0.0051118 | -0.013729 | -0.07837 | -0.0086879 | -0.032793 | -0.050381 | -0.041033 | -0.0021057 | 0.0018948 | 0.0079212 | -0.019961 | -0.22086 | -0.020264 | -0.026457 | -0.059509 | 0.073242 | -0.10071 | -0.013733 | 0.16479 | -0.022888 | 0.050354 | 0.15564 | 0.10071 | -0.082397 | 0.082397 | 0.21057 | 0.14191 | 0.15564 | 122.3053 | -0.018311 | -0.10529 | 122.5708 | 122.4564 | 122.3831 | 0.15106 | 0.07782 | 122.3236 | 0.009155 | -0.009156 | 122.6166 | 122.5616 | 122.5479 | 0.23804 | 0.2243 | 0.2655 | 0.086975 | 0.29297 | 0.16479 | 0.17395 | 0.18311 | 122.4792 | 122.5067 | -0.19226 | -0.17395 | 122.3923 | 122.4884 | 122.3465 | 122.5616
3761 | 122.6898 | -122.406 | 0.086975 | -0.0051118 | -0.0094571 | -0.078583 | -0.0063381 | -0.030443 | -0.050167 | -0.040819 | 0.00094606 | 0.0036038 | 0.0066394 | -0.010134 | -0.21937 | -0.017914 | -0.022185 | -0.064087 | 0.082397 | -0.10071 | -0.036621 | 0.12817 | -0.059509 | 0.013733 | 0.12817 | 0.10071 | -0.086975 | 0.082397 | 0.15564 | 0.091553 | 0.14191 | 122.3053 | -0.004578 | -0.1236 | 122.5342 | 122.4197 | 122.3465 | 0.11444 | 0.041199 | 122.319 | 0.013733 | -0.004578 | 122.5616 | 122.5479 | 122.4976 | 0.22888 | 0.17853 | 0.22888 | 0.064087 | 0.24261 | 0.16937 | 0.18311 | 0.18768 | 122.4884 | 122.5067 | -0.18768 | -0.17395 | 122.3694 | 122.4884 | 122.3419 | 122.5342
3762.8125 | 122.612 | -122.4472 | 0.12817 | -0.0051118 | -0.013516 | -0.080506 | -0.0022793 | -0.028093 | -0.051663 | -0.041674 | 0.00094606 | 0.0055264 | 0.006853 | -0.0086388 | -0.21979 | -0.017487 | -0.023894 | -0.09613 | 0.10986 | -0.1236 | -0.10529 | 0.050354 | -0.12817 | -0.073242 | 0.013733 | 0.13733 | -0.12817 | -0.004578 | 0.068665 | 0 | 0.073242 | 122.3236 | -0.018311 | -0.23346 | 122.4976 | 122.374 | 122.319 | 0.050354 | -0.004578 | 122.319 | 0.009155 | -0.13275 | 122.5159 | 122.5204 | 122.4472 | 0.20142 | 0.12817 | 0.17395 | 0.01831 | 0.19684 | 0.1236 | 0.23346 | 0.2655 | 122.5571 | 122.5845 | -0.25177 | -0.25635 | 122.3419 | 122.4426 | 122.3511 | 122.4609
3764.75 | 122.6761 | -122.4335 | 0.09613 | -0.0051118 | -0.015225 | -0.081574 | -0.0074063 | -0.029162 | -0.050808 | -0.042528 | -0.0021057 | 0.0025358 | 0.0070666 | -0.01163 | -0.22043 | -0.018342 | -0.024321 | -0.091553 | 0.082397 | -0.10071 | -0.07782 | 0.10071 | -0.09613 | -0.013733 | 0.054932 | 0.10071 | -0.10071 | 0.041199 | 0.12817 | 0.073242 | 0.10986 | 122.3328 | -0.013733 | -0.17395 | 122.5342 | 122.4197 | 122.3373 | 0.086975 | 0.004578 | 122.3328 | 0.004578 | -0.054931 | 122.5616 | 122.5433 | 122.5067 | 0.21057 | 0.17395 | 0.20142 | 0.022888 | 0.22888 | 0.14191 | 0.18311 | 0.20142 | 122.5159 | 122.5342 | -0.19684 | -0.19684 | 122.3557 | 122.4747 | 122.3419 | 122.4884
3766.5469 | 122.6395 | -122.4335 | 0.10071 | -0.012741 | -0.011807 | -0.079224 | -0.0031337 | -0.031298 | -0.052731 | -0.042742 | -0.0051575 | 0.0038174 | 0.0070666 | -0.0065026 | -0.22129 | -0.017487 | -0.024107 | -0.07782 | 0.11444 | -0.1236 | -0.09613 | 0.059509 | -0.10986 | -0.050354 | 0.036621 | 0.11902 | -0.10986 | 0.018311 | 0.091553 | 0.018311 | 0.086975 | 122.3099 | 0.013733 | -0.19684 | 122.493 | 122.3831 | 122.3236 | 0.073242 | 0.013733 | 122.3236 | 0.018311 | -0.082397 | 122.525 | 122.5204 | 122.4518 | 0.19684 | 0.12817 | 0.1831 | 0.027466 | 0.20142 | 0.12817 | 0.23804 | 0.22888 | 122.5479 | 122.5525 | -0.2243 | -0.21057 | 122.3373 | 122.4518 | 122.3557 | 122.4701
3768.5 | 122.6486 | -122.4426 | 0.10986 | 0.0025177 | -0.012448 | -0.078797 | -0.0069791 | -0.028093 | -0.051022 | -0.042955 | -0.0021057 | 0.0027494 | 0.008562 | -0.009707 | -0.22022 | -0.018769 | -0.022185 | -0.068665 | 0.10529 | -0.11902 | -0.091553 | 0.054932 | -0.11444 | -0.032043 | 0.059509 | 0.11902 | -0.11902 | 0.018311 | 0.10071 | 0.027466 | 0.07782 | 122.3236 | -0.004577 | -0.20142 | 122.4976 | 122.4106 | 122.3282 | 0.086976 | 0.004578 | 122.3236 | 0.009156 | -0.091552 | 122.5433 | 122.5204 | 122.4701 | 0.19684 | 0.14649 | 0.17395 | 0.027466 | 0.21973 | 0.13733 | 0.22431 | 0.23804 | 122.5479 | 122.5616 | -0.22888 | -0.22888 | 122.3511 | 122.4609 | 122.374 | 122.5021
3771.0312 | 122.7356 | -122.4518 | 0.09613 | -0.012741 | -0.013516 | -0.080506 | -0.010397 | -0.031511 | -0.050595 | -0.04146 | -0.0021057 | 0.0023222 | 0.010057 | -0.012911 | -0.21979 | -0.021332 | -0.026671 | -0.091553 | 0.068665 | -0.11902 | -0.054932 | 0.10986 | -0.027466 | 0.045776 | 0.09613 | 0.11444 | -0.091553 | 0.082397 | 0.21515 | 0.16937 | 0.14648 | 122.3328 | -0.027465 | -0.15106 | 122.5616 | 122.4976 | 122.4243 | 0.16479 | 0.091553 | 122.3602 | 0.018311 | -0.013733 | 122.6669 | 122.5983 | 122.6212 | 0.23804 | 0.26093 | 0.22888 | 0.064087 | 0.3067 | 0.17395 | 0.18768 | 0.20599 | 122.5204 | 122.5662 | -0.21515 | -0.18768 | 122.3969 | 122.5342 | 122.3602 | 122.5479
3773.7031 | 122.6349 | -122.4701 | 0.11444 | -0.0051118 | -0.013302 | -0.080292 | -0.0044155 | -0.031084 | -0.053372 | -0.039751 | 0.00094606 | 0.0036038 | 0.0094166 | -0.0092798 | -0.22107 | -0.017701 | -0.021971 | -0.13733 | 0.11902 | -0.15564 | -0.16022 | -0.018311 | -0.15564 | -0.07782 | -0.050354 | 0.12817 | -0.12817 | -0.032043 | 0.064087 | 0.013733 | 0.054932 | 122.3145 | 0.004578 | -0.27466 | 122.4518 | 122.3923 | 122.3145 | 0.07782 | 0 | 122.3419 | 0.013733 | -0.14648 | 122.5342 | 122.525 | 122.4838 | 0.18311 | 0.14191 | 0.13733 | -0.004577 | 0.19226 | 0.096131 | 0.27466 | 0.25635 | 122.5891 | 122.5983 | -0.27008 | -0.24262 | 122.3099 | 122.4381 | 122.3328 | 122.4197
3776.3281 | 122.7493 | -122.4426 | 0.086975 | 0.0025177 | -0.012448 | -0.079438 | -0.0095425 | -0.028521 | -0.051022 | -0.040392 | -0.0021057 | 0.0010404 | 0.006853 | -0.012698 | -0.22043 | -0.020905 | -0.020903 | -0.045776 | 0.10986 | -0.09613 | -0.013733 | 0.16937 | -0.018311 | 0.045776 | 0.14648 | 0.07782 | -0.082397 | 0.068665 | 0.20599 | 0.16022 | 0.14648 | 122.3465 | 0.022888 | -0.10071 | 122.612 | 122.4884 | 122.4243 | 0.14191 | 0.077819 | 122.3602 | -0.009155 | -0.01831 | 122.6486 | 122.5891 | 122.6028 | 0.22888 | 0.24261 | 0.2655 | 0.082397 | 0.28839 | 0.15106 | 0.20599 | 0.16022 | 122.5525 | 122.5204 | -0.1831 | -0.16937 | 122.4289 | 122.5113 | 122.3969 | 122.5891
3778.7656 | 122.7036 | -122.4564 | 0.10071 | 0.0025177 | -0.01138 | -0.082001 | -0.0056973 | -0.028307 | -0.050167 | -0.044664 | 0.0039979 | 0.001254 | 0.0062122 | -0.013339 | -0.22043 | -0.020264 | -0.022612 | -0.10529 | 0.09613 | -0.10529 | -0.10071 | 0.054932 | -0.091553 | -0.018311 | 0.027466 | 0.10529 | -0.10071 | 0.022888 | 0.13275 | 0.064087 | 0.10986 | 122.3511 | -0.004578 | -0.20142 | 122.5113 | 122.438 | 122.3648 | 0.086975 | 0.013733 | 122.3557 | 0.004578 | -0.07782 | 122.5891 | 122.5662 | 122.5204 | 0.21057 | 0.1648 | 0.16022 | 0.004578 | 0.23346 | 0.1236 | 0.20142 | 0.20599 | 122.5525 | 122.5616 | -0.20599 | -0.20142 | 122.3557 | 122.4792 | 122.3511 | 122.4838
3781.2188 | 122.7585 | -122.4518 | 0.073242 | -0.012741 | -0.017361 | -0.080719 | -0.0050565 | -0.031298 | -0.052944 | -0.043169 | -0.0051575 | 0.0016812 | 0.0070666 | -0.0084252 | -0.21937 | -0.019837 | -0.025389 | -0.054932 | 0.07782 | -0.09613 | -0.032043 | 0.15564 | -0.013733 | 0.041199 | 0.14191 | 0.11902 | -0.086975 | 0.091553 | 0.19684 | 0.15106 | 0.14648 | 122.3557 | 0.004578 | -0.10529 | 122.6074 | 122.493 | 122.438 | 0.13733 | 0.082397 | 122.3648 | 0.045777 | 0.018311 | 122.6486 | 122.5983 | 122.6028 | 0.23346 | 0.23804 | 0.25177 | 0.064087 | 0.28381 | 0.17853 | 0.17395 | 0.20599 | 122.5296 | 122.5708 | -0.16937 | -0.16022 | 122.4197 | 122.5433 | 122.3969 | 122.5937
3783.125 | 122.644 | -122.4838 | 0.1236 | -0.0051118 | -0.013089 | -0.080506 | -0.0052701 | -0.03258 | -0.052517 | -0.039965 | -0.0082091 | 0.0050992 | 0.0064258 | -0.0058618 | -0.22022 | -0.018982 | -0.024321 | -0.1236 | 0.13275 | -0.15106 | -0.14191 | -0.027466 | -0.12817 | -0.07782 | -0.041199 | 0.1236 | -0.14648 | -0.027466 | 0.082397 | 0 | 0.073242 | 122.3328 | 0.009155 | -0.2655 | 122.4564 | 122.406 | 122.3557 | 0.073242 | 0.022888 | 122.3373 | 0 | -0.15106 | 122.5662 | 122.5571 | 122.4838 | 0.21973 | 0.14648 | 0.1236 | 0.009155 | 0.22888 | 0.11902 | 0.28381 | 0.27008 | 122.6166 | 122.6074 | -0.27466 | -0.27008 | 122.3419 | 122.4564 | 122.3602 | 122.4426
3784.9062 | 122.7356 | -122.4655 | 0.10071 | -0.0051118 | -0.015866 | -0.079224 | -0.0097561 | -0.033648 | -0.052517 | -0.040178 | 0.00094606 | 0.002963 | 0.005144 | -0.01227 | -0.21979 | -0.020905 | -0.025816 | -0.086975 | 0.091553 | -0.10071 | -0.086975 | 0.073242 | -0.09613 | -0.009155 | 0.041199 | 0.10071 | -0.10986 | 0.041199 | 0.15106 | 0.091553 | 0.11444 | 122.3648 | -0.009155 | -0.18768 | 122.5388 | 122.4564 | 122.3694 | 0.091553 | 0.004578 | 122.3557 | 0 | -0.059509 | 122.6166 | 122.58 | 122.5571 | 0.2243 | 0.20142 | 0.17395 | 0.013733 | 0.26093 | 0.15106 | 0.19226 | 0.21057 | 122.5571 | 122.5662 | -0.20142 | -0.21057 | 122.3785 | 122.5067 | 122.3785 | 122.5067
3787 | 122.6349 | -122.493 | 0.1236 | -0.0051118 | -0.013943 | -0.079224 | -0.0065517 | -0.028307 | -0.054653 | -0.042528 | -0.0021057 | 0.0050992 | 0.0062122 | -0.010561 | -0.22107 | -0.017914 | -0.024535 | -0.15106 | 0.11444 | -0.16479 | -0.16022 | -0.013733 | -0.15106 | -0.073242 | -0.041199 | 0.13275 | -0.13275 | -0.059509 | 0.036621 | 0 | 0.036621 | 122.3282 | -0.009155 | -0.28381 | 122.4792 | 122.4197 | 122.3419 | 0.091553 | 0.013733 | 122.3602 | 0.009155 | -0.1831 | 122.5296 | 122.5296 | 122.493 | 0.16937 | 0.13275 | 0.15106 | 0.004578 | 0.16937 | 0.073242 | 0.27924 | 0.2655 | 122.6074 | 122.6257 | -0.28839 | -0.25635 | 122.3328 | 122.4335 | 122.3419 | 122.4518
3788.8594 | 122.6807 | -122.4747 | 0.13275 | 0.0025177 | -0.013729 | -0.079438 | -0.0050565 | -0.029589 | -0.048886 | -0.040392 | -0.0021057 | 0.0042448 | 0.0066394 | -0.014193 | -0.22065 | -0.018128 | -0.02603 | -0.09613 | 0.1236 | -0.13733 | -0.12817 | 0.022888 | -0.11902 | -0.050354 | 0.013733 | 0.1236 | -0.1236 | 0 | 0.10071 | 0.027466 | 0.082397 | 122.3373 | -0.009155 | -0.26093 | 122.4976 | 122.4243 | 122.3557 | 0.086975 | 0.01831 | 122.3511 | -0.009155 | -0.13275 | 122.5754 | 122.5571 | 122.5021 | 0.20599 | 0.15106 | 0.16022 | 0.009155 | 0.2243 | 0.1236 | 0.26093 | 0.24719 | 122.5983 | 122.5983 | -0.27008 | -0.25635 | 122.3465 | 122.4747 | 122.3785 | 122.4884
3790.6406 | 122.6852 | -122.4838 | 0.09613 | 0.010147 | -0.01202 | -0.078797 | -0.0065517 | -0.030016 | -0.051235 | -0.042101 | -0.0021057 | 0.0055264 | 0.0083484 | -0.0071436 | -0.22086 | -0.017914 | -0.024748 | -0.07782 | 0.10071 | -0.12817 | -0.10986 | 0.036621 | -0.12817 | -0.050354 | 0.032043 | 0.12817 | -0.10986 | 0.027466 | 0.10071 | 0.032043 | 0.10071 | 122.3557 | 0.004578 | -0.20599 | 122.5204 | 122.4335 | 122.3557 | 0.07782 | 0 | 122.374 | 0.032044 | -0.068664 | 122.5845 | 122.5845 | 122.5159 | 0.21057 | 0.14191 | 0.1648 | 0.018311 | 0.21057 | 0.13733 | 0.22888 | 0.23804 | 122.5845 | 122.612 | -0.2243 | -0.20599 | 122.374 | 122.5113 | 122.406 | 122.5159
3792.5469 | 122.7585 | -122.4655 | 0.07782 | -0.0051118 | -0.013302 | -0.078797 | -0.0065517 | -0.029375 | -0.050381 | -0.040178 | -0.0021057 | 0.0023222 | 0.0055712 | -0.010775 | -0.22001 | -0.016846 | -0.023467 | -0.10986 | 0.10071 | -0.10986 | -0.064087 | 0.082397 | -0.10529 | -0.009155 | 0.059509 | 0.11444 | -0.091553 | 0.10071 | 0.15564 | 0.09613 | 0.16022 | 122.3557 | 0.022888 | -0.14191 | 122.5479 | 122.4564 | 122.3602 | 0.10071 | 0.004577 | 122.374 | 0.036621 | 0.022888 | 122.6212 | 122.6257 | 122.5616 | 0.25177 | 0.18768 | 0.19226 | 0.045776 | 0.24719 | 0.19226 | 0.21057 | 0.20599 | 122.5662 | 122.58 | -0.18768 | -0.16937 | 122.4014 | 122.5662 | 122.3557 | 122.525
3794.2656 | 122.6257 | -122.5159 | 0.11902 | 0.0025177 | -0.010739 | -0.077942 | -0.0046291 | -0.027666 | -0.049954 | -0.039751 | 0.00094606 | 0.0031766 | 0.0081348 | -0.013125 | -0.21937 | -0.017914 | -0.023467 | -0.11902 | 0.12817 | -0.14191 | -0.16479 | -0.041199 | -0.20142 | -0.11902 | -0.086975 | 0.13733 | -0.13733 | -0.036621 | 0.018311 | -0.041199 | 0.059509 | 122.374 | 0.009155 | -0.28381 | 122.4747 | 122.3969 | 122.3145 | 0.022888 | -0.059509 | 122.3785 | 0.01831 | -0.15564 | 122.5342 | 122.5754 | 122.4747 | 0.19684 | 0.09613 | 0.10071 | -0.022888 | 0.15564 | 0.10071 | 0.27008 | 0.27466 | 122.644 | 122.6532 | -0.26093 | -0.25635 | 122.3511 | 122.4792 | 122.3969 | 122.4289
3796.0469 | 122.7493 | -122.4655 | 0.10071 | -0.0051118 | -0.013943 | -0.080933 | -0.0071927 | -0.030871 | -0.049526 | -0.041887 | -0.0021057 | 0.00018579 | 0.007494 | -0.017825 | -0.21937 | -0.017914 | -0.022398 | -0.10529 | 0.082397 | -0.10986 | -0.09613 | 0.064087 | -0.091553 | 0 | 0.050354 | 0.091553 | -0.11444 | 0.045776 | 0.14191 | 0.091553 | 0.1236 | 122.3557 | -0.018311 | -0.19684 | 122.5296 | 122.4655 | 122.374 | 0.10986 | 0.01831 | 122.3511 | -0.009155 | -0.054932 | 122.6074 | 122.5891 | 122.5571 | 0.23804 | 0.20599 | 0.17395 | 0.013733 | 0.25635 | 0.16022 | 0.19226 | 0.20599 | 122.5479 | 122.5571 | -0.21057 | -0.21515 | 122.3694 | 122.5113 | 122.3602 | 122.5159
3797.7656 | 122.7448 | -122.4609 | 0.091553 | -0.012741 | -0.0094571 | -0.077302 | -0.0054837 | -0.025957 | -0.050595 | -0.039324 | 0.00094606 | 0.0025358 | 0.0045032 | -0.016543 | -0.22043 | -0.020051 | -0.019835 | -0.054932 | 0.082397 | -0.10071 | -0.045776 | 0.13733 | -0.064087 | 0.009155 | 0.11902 | 0.10071 | -0.091553 | 0.082397 | 0.15564 | 0.10071 | 0.13733 | 122.3602 | -0.009156 | -0.13733 | 122.5983 | 122.4701 | 122.3969 | 0.10986 | 0.036621 | 122.3694 | 0.009155 | -0.009156 | 122.6166 | 122.5983 | 122.5616 | 0.22888 | 0.19226 | 0.23804 | 0.054932 | 0.24719 | 0.17395 | 0.18311 | 0.19226 | 122.5433 | 122.5616 | -0.19226 | -0.18311 | 122.4152 | 122.5433 | 122.406 | 122.58
3799.4844 | 122.7859 | -122.493 | 0.07782 | -0.0051118 | -0.015438 | -0.08371 | -0.010183 | -0.03258 | -0.051876 | -0.040819 | -0.0021057 | 0.0010404 | 0.0053576 | -0.010775 | -0.22043 | -0.01941 | -0.023039 | -0.064087 | 0.082397 | -0.11444 | -0.045776 | 0.12817 | -0.004578 | 0.032043 | 0.14191 | 0.10071 | -0.09613 | 0.10529 | 0.20142 | 0.15564 | 0.16022 | 122.3785 | 0.004577 | -0.1236 | 122.6212 | 122.525 | 122.4884 | 0.14648 | 0.10986 | 122.3969 | 0.022888 | 0.027466 | 122.6944 | 122.6532 | 122.6486 | 0.25635 | 0.25177 | 0.24262 | 0.068665 | 0.29755 | 0.20142 | 0.19684 | 0.19684 | 122.5754 | 122.5937 | -0.19226 | -0.17395 | 122.4472 | 122.5983 | 122.4289 | 122.6349
3801.2344 | 122.6395 | -122.5067 | 0.12817 | 0.0025177 | -0.010952 | -0.078156 | -0.0044155 | -0.031084 | -0.050381 | -0.040819 | 0.0039979 | 0.0055264 | 0.005785 | -0.013339 | -0.22001 | -0.01706 | -0.02368 | -0.10071 | 0.10986 | -0.1236 | -0.14648 | -0.018311 | -0.16479 | -0.086975 | -0.022888 | 0.13275 | -0.12817 | -0.027466 | 0.027466 | -0.054932 | 0.054932 | 122.3831 | -0.018311 | -0.27466 | 122.4884 | 122.4197 | 122.3419 | 0.036621 | -0.041199 | 122.3785 | 0.004577 | -0.15564 | 122.5342 | 122.5616 | 122.4518 | 0.18311 | 0.073242 | 0.10528 | -0.022888 | 0.15564 | 0.10071 | 0.23346 | 0.26093 | 122.6166 | 122.6395 | -0.25177 | -0.25635 | 122.3602 | 122.4792 | 122.406 | 122.4838
3802.9375 | 122.7951 | -122.4792 | 0.10529 | -0.0051118 | -0.014584 | -0.078583 | -0.0071927 | -0.025316 | -0.049313 | -0.044664 | 0.0039979 | 0.0010404 | 0.0066394 | -0.014407 | -0.22257 | -0.018769 | -0.024321 | -0.07782 | 0.07782 | -0.091553 | -0.07782 | 0.10071 | -0.045776 | 0.036621 | 0.086975 | 0.09613 | -0.10071 | 0.073242 | 0.19226 | 0.12817 | 0.15106 | 122.3877 | -0.027466 | -0.18311 | 122.58 | 122.5159 | 122.4335 | 0.12817 | 0.045777 | 122.3785 | -0.009156 | -0.032044 | 122.6715 | 122.6303 | 122.6074 | 0.25177 | 0.22888 | 0.19226 | 0.013733 | 0.29297 | 0.17395 | 0.16937 | 0.19684 | 122.5571 | 122.5754 | -0.19684 | -0.20599 | 122.4014 | 122.5525 | 122.4014 | 122.5662
3804.7031 | 122.6807 | -122.5296 | 0.12817 | -0.0051118 | -0.010739 | -0.077942 | -0.0048427 | -0.029162 | -0.050167 | -0.039965 | -0.0051575 | 0.0038174 | 0.0096302 | -0.0065026 | -0.22001 | -0.019623 | -0.021971 | -0.11902 | 0.1236 | -0.1236 | -0.17395 | -0.022888 | -0.19226 | -0.09613 | -0.027466 | 0.14191 | -0.12817 | -0.018311 | 0.050354 | -0.018311 | 0.059509 | 122.406 | -0.004578 | -0.30212 | 122.5067 | 122.4335 | 122.3373 | 0.027466 | -0.068665 | 122.4014 | 0.013733 | -0.14649 | 122.58 | 122.5891 | 122.5113 | 0.18768 | 0.10986 | 0.10071 | -0.050354 | 0.17853 | 0.10986 | 0.24719 | 0.27008 | 122.6532 | 122.6715 | -0.25177 | -0.25635 | 122.3557 | 122.5113 | 122.4106 | 122.5021
3806.4062 | 122.8043 | -122.4976 | 0.07782 | -0.012741 | -0.014157 | -0.078797 | -0.0080471 | -0.030443 | -0.051876 | -0.039751 | -0.0021057 | 0.0023222 | 0.0072802 | -0.018466 | -0.22172 | -0.021119 | -0.020903 | -0.09613 | 0.082397 | -0.10071 | -0.059509 | 0.10529 | -0.041199 | 0.027466 | 0.10529 | 0.09613 | -0.10071 | 0.073242 | 0.19684 | 0.13733 | 0.16937 | 122.3969 | 0.004577 | -0.13733 | 122.6028 | 122.525 | 122.4564 | 0.12817 | 0.059509 | 122.3969 | 0.01831 | -0.004578 | 122.6944 | 122.6669 | 122.6349 | 0.27008 | 0.23804 | 0.20599 | 0.041199 | 0.29755 | 0.17395 | 0.18311 | 0.19684 | 122.58 | 122.5937 | -0.17853 | -0.17853 | 122.438 | 122.5708 | 122.4014 | 122.6028
3808.2031 | 122.7997 | -122.4564 | 0.082397 | -0.012741 | -0.013943 | -0.081574 | -0.0069791 | -0.031298 | -0.049099 | -0.040178 | -0.0051575 | 0.0014676 | 0.0077076 | -0.015688 | -0.22065 | -0.020905 | -0.022398 | -0.068665 | 0.091553 | -0.09613 | -0.032043 | 0.14191 | -0.032043 | 0.045776 | 0.13733 | 0.11902 | -0.086975 | 0.09613 | 0.20599 | 0.14648 | 0.16479 | 122.3602 | 0.009156 | -0.11444 | 122.5983 | 122.5021 | 122.4243 | 0.14191 | 0.064087 | 122.3694 | 0.036622 | 0.013733 | 122.6624 | 122.6212 | 122.6028 | 0.25177 | 0.23346 | 0.23804 | 0.064087 | 0.29297 | 0.1831 | 0.18768 | 0.20599 | 122.5479 | 122.5754 | -0.17853 | -0.16937 | 122.4243 | 122.5525 | 122.3877 | 122.5937
3810 | 122.7997 | -122.4564 | 0.073242 | -0.012741 | -0.010311 | -0.076874 | -0.0063381 | -0.031511 | -0.049099 | -0.041887 | -0.0021057 | 0.0023222 | 0.006853 | -0.010561 | -0.22214 | -0.018982 | -0.020476 | -0.027466 | 0.082397 | -0.09613 | -0.027466 | 0.12817 | -0.073242 | 0.018311 | 0.11902 | 0.091553 | -0.086975 | 0.10529 | 0.18768 | 0.11444 | 0.16022 | 122.3602 | 0.009155 | -0.10071 | 122.5845 | 122.4747 | 122.3831 | 0.11444 | 0.022888 | 122.3694 | 0.018311 | 0.032044 | 122.644 | 122.6166 | 122.5708 | 0.24719 | 0.20142 | 0.2243 | 0.068664 | 0.27466 | 0.19226 | 0.17853 | 0.17853 | 122.5388 | 122.5479 | -0.16937 | -0.16022 | 122.4289 | 122.5616 | 122.4289 | 122.5754
3811.9531 | 122.6578 | -122.525 | 0.1236 | 0.0025177 | -0.013729 | -0.080506 | -0.0050565 | -0.03023 | -0.053585 | -0.041674 | -0.0021057 | 0.0033902 | 0.0094166 | -0.020388 | -0.21851 | -0.020051 | -0.024962 | -0.13733 | 0.13275 | -0.15106 | -0.17395 | -0.022888 | -0.14648 | -0.054932 | -0.045776 | 0.14191 | -0.1236 | -0.054932 | 0.054932 | -0.018311 | 0.022888 | 122.374 | 0.009155 | -0.29755 | 122.5021 | 122.4701 | 122.3785 | 0.09613 | 0.004578 | 122.4014 | 0.018311 | -0.17853 | 122.58 | 122.5479 | 122.5067 | 0.14648 | 0.10528 | 0.12817 | -0.022888 | 0.17853 | 0.068664 | 0.28381 | 0.2655 | 122.6578 | 122.6669 | -0.27466 | -0.24719 | 122.3511 | 122.4701 | 122.3877 | 122.4792
3813.8594 | 122.6761 | -122.5571 | 0.12817 | 0.0025177 | -0.016293 | -0.08136 | -0.0061245 | -0.035143 | -0.051876 | -0.037615 | -0.0021057 | 0.0048856 | 0.0087756 | -0.011416 | -0.21979 | -0.017701 | -0.026244 | -0.14648 | 0.1236 | -0.13733 | -0.17395 | -0.018311 | -0.15106 | -0.086975 | -0.050354 | 0.15106 | -0.15106 | -0.050354 | 0.045776 | -0.018311 | 0.041199 | 122.4197 | -0.004578 | -0.30212 | 122.5388 | 122.4701 | 122.406 | 0.050354 | -0.013733 | 122.406 | 0.022888 | -0.17853 | 122.6028 | 122.5983 | 122.5388 | 0.19226 | 0.13275 | 0.11902 | -0.036621 | 0.19684 | 0.10071 | 0.26093 | 0.30212 | 122.6807 | 122.7081 | -0.2655 | -0.27924 | 122.3831 | 122.5067 | 122.4106 | 122.5067
3815.7188 | 122.6715 | -122.5525 | 0.13275 | 0.0025177 | -0.012661 | -0.077515 | -0.0037747 | -0.028093 | -0.051235 | -0.039537 | -0.0051575 | 0.0031766 | 0.0087756 | -0.0084252 | -0.21872 | -0.020478 | -0.022185 | -0.13733 | 0.1236 | -0.14191 | -0.17853 | -0.050354 | -0.19684 | -0.10529 | -0.068665 | 0.1236 | -0.13733 | -0.027466 | 0.032043 | -0.041199 | 0.045776 | 122.4106 | -0.009155 | -0.31128 | 122.5021 | 122.4472 | 122.3557 | 0.036621 | -0.054931 | 122.4152 | -0.009155 | -0.16022 | 122.5845 | 122.5983 | 122.5113 | 0.18311 | 0.09613 | 0.091553 | -0.036621 | 0.16937 | 0.10986 | 0.2655 | 0.26093 | 122.6761 | 122.6761 | -0.27466 | -0.27008 | 122.374 | 122.525 | 122.4152 | 122.4838
3817.5469 | 122.6669 | -122.58 | 0.11902 | 0.0025177 | -0.015011 | -0.080933 | -0.0061245 | -0.029375 | -0.048886 | -0.042955 | -0.0021057 | 0.0027494 | 0.007494 | -0.019961 | -0.22086 | -0.019837 | -0.024748 | -0.1236 | 0.10529 | -0.11902 | -0.16022 | 0.004578 | -0.14191 | -0.054932 | -0.041199 | 0.14191 | -0.1236 | -0.059509 | 0.064087 | -0.009155 | 0.036621 | 122.4609 | -0.013733 | -0.27924 | 122.5845 | 122.525 | 122.438 | 0.064087 | -0.022888 | 122.4564 | 0.022888 | -0.17853 | 122.644 | 122.6166 | 122.5708 | 0.16022 | 0.11444 | 0.1236 | -0.041198 | 0.18768 | 0.064087 | 0.22431 | 0.2655 | 122.6852 | 122.7219 | -0.23804 | -0.24261 | 122.4197 | 122.5204 | 122.4564 | 122.5388
3819.5156 | 122.6486 | -122.5479 | 0.13733 | 0.0025177 | -0.0098843 | -0.079224 | -0.0042019 | -0.027239 | -0.048245 | -0.041033 | -0.0021057 | 0.0053128 | 0.0066394 | -0.0065026 | -0.22107 | -0.017273 | -0.022185 | -0.13733 | 0.11902 | -0.15106 | -0.19226 | -0.064087 | -0.21057 | -0.11902 | -0.09613 | 0.13733 | -0.14648 | -0.036621 | 0.022888 | -0.032043 | 0.027466 | 122.3969 | -0.01831 | -0.32959 | 122.4838 | 122.4289 | 122.3373 | 0.032043 | -0.059509 | 122.4014 | 0 | -0.17395 | 122.5708 | 122.5754 | 122.5159 | 0.17395 | 0.11444 | 0.086975 | -0.041199 | 0.16937 | 0.10986 | 0.27008 | 0.28381 | 122.6669 | 122.6852 | -0.28839 | -0.28381 | 122.3557 | 122.5113 | 122.4106 | 122.4518
3821.7812 | 122.7905 | -122.5067 | 0.086975 | 0.0025177 | -0.015225 | -0.080933 | -0.0078335 | -0.032366 | -0.051022 | -0.043169 | -0.0051575 | 0.00082679 | 0.005785 | -0.018466 | -0.21851 | -0.020905 | -0.021758 | -0.064087 | 0.068665 | -0.10529 | -0.045776 | 0.15564 | 0 | 0.054932 | 0.1236 | 0.09613 | -0.09613 | 0.073242 | 0.20142 | 0.13733 | 0.15106 | 122.4014 | -0.01831 | -0.13275 | 122.6624 | 122.5616 | 122.5067 | 0.16022 | 0.10529 | 122.4106 | 0.009155 | -0.013733 | 122.7081 | 122.6578 | 122.644 | 0.24719 | 0.23346 | 0.26093 | 0.05951 | 0.29755 | 0.16937 | 0.17395 | 0.19226 | 122.5754 | 122.6028 | -0.19226 | -0.1831 | 122.4609 | 122.58 | 122.4426 | 122.6303
3823.5625 | 122.8317 | -122.493 | 0.073242 | -0.0051118 | -0.014798 | -0.081147 | -0.0091153 | -0.029802 | -0.051663 | -0.041033 | 0.00094606 | 0.0025358 | 0.006853 | -0.010134 | -0.22022 | -0.020478 | -0.020262 | -0.073242 | 0.086975 | -0.10529 | -0.041199 | 0.15106 | -0.013733 | 0.045776 | 0.15106 | 0.091553 | -0.10071 | 0.091553 | 0.20599 | 0.15106 | 0.15106 | 122.3877 | 0.013733 | -0.11444 | 122.644 | 122.5388 | 122.4792 | 0.15106 | 0.091553 | 122.3923 | 0.018311 | 0.018311 | 122.699 | 122.644 | 122.644 | 0.25177 | 0.25177 | 0.25635 | 0.064087 | 0.3067 | 0.19226 | 0.19226 | 0.19226 | 122.58 | 122.5845 | -0.17853 | -0.17395 | 122.4518 | 122.5845 | 122.4197 | 122.644
3825.5 | 122.7631 | -122.525 | 0.07782 | 0.0025177 | -0.012661 | -0.079224 | -0.0063381 | -0.030657 | -0.051235 | -0.039751 | 0.00094606 | 0.0038174 | 0.008562 | -0.012484 | -0.22001 | -0.020264 | -0.026885 | -0.091553 | 0.073242 | -0.10986 | -0.068665 | 0.082397 | -0.09613 | -0.004578 | 0.073242 | 0.10529 | -0.10529 | 0.041199 | 0.12817 | 0.068665 | 0.10529 | 122.4152 | -0.004578 | -0.14649 | 122.6074 | 122.5204 | 122.4289 | 0.10529 | 0.013733 | 122.4197 | 0.027466 | -0.036621 | 122.6532 | 122.6303 | 122.5937 | 0.21057 | 0.17395 | 0.19226 | 0.041198 | 0.23346 | 0.14649 | 0.18311 | 0.21057 | 122.5983 | 122.6303 | -0.18768 | -0.18311 | 122.4564 | 122.5662 | 122.4335 | 122.5983
3827.2969 | 122.7676 | -122.5433 | 0.11902 | -0.02037 | -0.013943 | -0.079651 | -0.0065517 | -0.029375 | -0.050381 | -0.043169 | -0.0021057 | 0.00082679 | 0.0094166 | -0.015261 | -0.22236 | -0.019837 | -0.02603 | -0.050354 | 0.082397 | -0.086975 | -0.036621 | 0.1236 | -0.032043 | 0.041199 | 0.082397 | 0.11444 | -0.091553 | 0.018311 | 0.14648 | 0.082397 | 0.10986 | 122.4564 | -0.036622 | -0.15564 | 122.6669 | 122.5845 | 122.5113 | 0.12817 | 0.054932 | 122.4518 | -0.004578 | -0.10071 | 122.6898 | 122.6532 | 122.6257 | 0.20142 | 0.17395 | 0.21057 | 0.050354 | 0.23804 | 0.10986 | 0.16937 | 0.20599 | 122.6257 | 122.6578 | -0.20599 | -0.21057 | 122.5067 | 122.5616 | 122.493 | 122.6257
3829.1094 | 122.8363 | -122.4884 | 0.082397 | 0.0025177 | -0.013729 | -0.080933 | -0.0091153 | -0.032366 | -0.05209 | -0.044237 | -0.0051575 | 0.0040312 | 0.0064258 | -0.016329 | -0.21979 | -0.01941 | -0.028807 | -0.050354 | 0.073242 | -0.09613 | -0.018311 | 0.17395 | -0.004578 | 0.082397 | 0.1236 | 0.11444 | -0.09613 | 0.086975 | 0.19226 | 0.14648 | 0.15106 | 122.3923 | -0.009155 | -0.10071 | 122.6624 | 122.5708 | 122.4838 | 0.17853 | 0.091552 | 122.3923 | 0.032044 | 0.004578 | 122.6807 | 122.6395 | 122.6349 | 0.24719 | 0.24261 | 0.27008 | 0.077819 | 0.28839 | 0.1831 | 0.16937 | 0.21057 | 122.5616 | 122.6028 | -0.17853 | -0.17853 | 122.4701 | 122.5754 | 122.438 | 122.612
3830.9062 | 122.6852 | -122.525 | 0.11902 | -0.0051118 | -0.011593 | -0.07837 | -0.0031337 | -0.030443 | -0.051022 | -0.03911 | -0.0021057 | 0.0040312 | 0.010271 | -0.0090662 | -0.22043 | -0.020051 | -0.022826 | -0.10986 | 0.10986 | -0.15564 | -0.17853 | -0.050354 | -0.21515 | -0.10071 | -0.036621 | 0.13733 | -0.1236 | -0.027466 | 0.018311 | -0.036621 | 0.054932 | 122.3694 | -0.009156 | -0.29755 | 122.4747 | 122.4243 | 122.3099 | 0.054932 | -0.059509 | 122.4014 | 0.01831 | -0.14649 | 122.5433 | 122.58 | 122.4884 | 0.17853 | 0.086975 | 0.10529 | -0.022888 | 0.14191 | 0.09613 | 0.2655 | 0.26093 | 122.6349 | 122.6624 | -0.27466 | -0.24261 | 122.3465 | 122.4976 | 122.4152 | 122.4884
3832.8438 | 122.7722 | -122.5204 | 0.082397 | 0.0025177 | -0.010952 | -0.079011 | -0.0061245 | -0.036425 | -0.050167 | -0.041246 | 0.00094606 | -2.7806e-05 | 0.0077076 | -0.012911 | -0.21915 | -0.019196 | -0.026457 | -0.068665 | 0.086975 | -0.10071 | -0.041199 | 0.11902 | -0.082397 | 0.022888 | 0.10986 | 0.10986 | -0.10529 | 0.064087 | 0.14191 | 0.07782 | 0.11902 | 122.4197 | 0.004578 | -0.1236 | 122.6395 | 122.5433 | 122.4381 | 0.1236 | 0.018311 | 122.4152 | 0.027466 | -0.01831 | 122.6624 | 122.6395 | 122.5983 | 0.22431 | 0.18311 | 0.21973 | 0.059509 | 0.24719 | 0.16937 | 0.18768 | 0.21515 | 122.6074 | 122.6303 | -0.18311 | -0.18768 | 122.4792 | 122.5845 | 122.4518 | 122.6303
3834.5938 | 122.8363 | -122.5113 | 0.10071 | 0.0025177 | -0.01138 | -0.080933 | -0.0080471 | -0.031084 | -0.051663 | -0.038683 | 0.0039979 | 0.0036038 | 0.0049304 | -0.017611 | -0.22043 | -0.020264 | -0.025816 | -0.050354 | 0.09613 | -0.11902 | -0.013733 | 0.16022 | 0 | 0.054932 | 0.12817 | 0.11444 | -0.09613 | 0.091553 | 0.20142 | 0.15106 | 0.16022 | 122.3923 | -0.004578 | -0.11444 | 122.6715 | 122.5662 | 122.5113 | 0.17395 | 0.11902 | 122.4152 | 0.013733 | -0.009155 | 122.7127 | 122.6715 | 122.6624 | 0.25635 | 0.24719 | 0.27924 | 0.10529 | 0.29755 | 0.18768 | 0.21515 | 0.21057 | 122.6074 | 122.6257 | -0.21973 | -0.19684 | 122.4976 | 122.6028 | 122.4609 | 122.6395
3836.4688 | 122.7676 | -122.5433 | 0.10529 | 0.0025177 | -0.013302 | -0.080079 | -0.0039883 | -0.031939 | -0.051449 | -0.040178 | -0.0021057 | 0.00574 | 0.0079212 | -0.013979 | -0.22129 | -0.01941 | -0.022612 | -0.091553 | 0.11444 | -0.12817 | -0.086975 | 0.050354 | -0.11902 | -0.032043 | 0.045776 | 0.13275 | -0.12817 | 0.022888 | 0.10986 | 0.050354 | 0.09613 | 122.4152 | 0.009155 | -0.19226 | 122.5937 | 122.5113 | 122.4243 | 0.096131 | 0.009155 | 122.4152 | 0.027465 | -0.082398 | 122.6532 | 122.6395 | 122.5937 | 0.2243 | 0.17853 | 0.17853 | 0.041199 | 0.23804 | 0.15106 | 0.24262 | 0.26093 | 122.6578 | 122.6761 | -0.23346 | -0.23346 | 122.4564 | 122.5662 | 122.4518 | 122.5891
3838.3125 | 122.7859 | -122.5159 | 0.09613 | -0.0051118 | -0.011807 | -0.079651 | -0.0074063 | -0.03258 | -0.051449 | -0.043596 | 0.00094606 | 0.0018948 | 0.0083484 | -0.010134 | -0.2183 | -0.019623 | -0.02133 | -0.07782 | 0.086975 | -0.09613 | -0.064087 | 0.11902 | -0.082397 | 0.013733 | 0.082397 | 0.10071 | -0.11444 | 0.064087 | 0.14191 | 0.068665 | 0.11902 | 122.4197 | -0.009155 | -0.16022 | 122.6349 | 122.5296 | 122.4335 | 0.10986 | 0.013733 | 122.4014 | 0.004578 | -0.032043 | 122.6578 | 122.6349 | 122.5845 | 0.23346 | 0.18311 | 0.21515 | 0.032043 | 0.25635 | 0.17853 | 0.1831 | 0.21515 | 122.6028 | 122.6166 | -0.19226 | -0.21057 | 122.4518 | 122.58 | 122.438 | 122.5983
3840.0781 | 122.8043 | -122.5479 | 0.09613 | -0.0051118 | -0.010739 | -0.080079 | -0.0069791 | -0.031725 | -0.047817 | -0.03911 | -0.0021057 | 0.0021084 | 0.0081348 | -0.010348 | -0.21915 | -0.020051 | -0.022398 | -0.045776 | 0.086975 | -0.086975 | -0.041199 | 0.11444 | -0.068665 | 0.009155 | 0.11444 | 0.091553 | -0.10071 | 0.059509 | 0.14648 | 0.07782 | 0.1236 | 122.4609 | -0.009155 | -0.13733 | 122.6624 | 122.5571 | 122.4792 | 0.09613 | 0.01831 | 122.4472 | -0.004577 | -0.036621 | 122.6944 | 122.6715 | 122.6257 | 0.2243 | 0.17853 | 0.20142 | 0.045776 | 0.24719 | 0.16022 | 0.17395 | 0.19226 | 122.6349 | 122.6395 | -0.1831 | -0.19684 | 122.5067 | 122.6074 | 122.5021 | 122.6624
3841.9219 | 122.7859 | -122.5159 | 0.10071 | 0.010147 | -0.014584 | -0.081574 | -0.0071927 | -0.032793 | -0.048458 | -0.040819 | -0.0051575 | 0.0027494 | 0.0081348 | -0.013766 | -0.22172 | -0.020264 | -0.024107 | -0.10986 | 0.09613 | -0.10071 | -0.091553 | 0.059509 | -0.10071 | -0.004578 | 0.032043 | 0.10986 | -0.09613 | 0.032043 | 0.14191 | 0.050354 | 0.10986 | 122.4152 | -0.004578 | -0.19226 | 122.5754 | 122.5113 | 122.4152 | 0.09613 | 0 | 122.4197 | 0.009155 | -0.068665 | 122.6578 | 122.6257 | 122.5662 | 0.20599 | 0.14648 | 0.16022 | 0.009155 | 0.23804 | 0.12817 | 0.19684 | 0.20599 | 122.612 | 122.6257 | -0.20142 | -0.19684 | 122.4243 | 122.5479 | 122.406 | 122.5479
3843.875 | 122.8638 | -122.525 | 0.091553 | 0.0025177 | -0.014584 | -0.080506 | -0.0074063 | -0.028948 | -0.050808 | -0.04381 | 0.00094606 | 0.002963 | 0.0070666 | -0.015475 | -0.22086 | -0.019623 | -0.021117 | -0.059509 | 0.086975 | -0.10986 | -0.027466 | 0.14648 | -0.004578 | 0.059509 | 0.14191 | 0.10986 | -0.10071 | 0.10529 | 0.21057 | 0.14191 | 0.15106 | 122.4152 | -0.004578 | -0.11902 | 122.6715 | 122.5845 | 122.5204 | 0.16937 | 0.10529 | 122.4243 | 0.01831 | 0.013733 | 122.7356 | 122.6761 | 122.6669 | 0.25177 | 0.24262 | 0.25635 | 0.082397 | 0.31128 | 0.20599 | 0.19684 | 0.21057 | 122.612 | 122.6349 | -0.20142 | -0.19226 | 122.4976 | 122.6303 | 122.4655 | 122.6669
3846 | 122.7585 | -122.5525 | 0.11444 | 0.010147 | -0.010311 | -0.079224 | -0.0059109 | -0.03258 | -0.050167 | -0.042742 | 0.00094606 | 0.0050992 | 0.008562 | -0.0084252 | -0.22193 | -0.017487 | -0.022612 | -0.082397 | 0.11902 | -0.13275 | -0.10986 | 0.036621 | -0.1236 | -0.050354 | 0.027466 | 0.13275 | -0.1236 | 0.009155 | 0.10986 | 0.041199 | 0.10529 | 122.4197 | 0.004578 | -0.2243 | 122.5891 | 122.5021 | 122.4289 | 0.082397 | 0.009155 | 122.4289 | 0.01831 | -0.10529 | 122.6624 | 122.6578 | 122.5937 | 0.22888 | 0.16479 | 0.16937 | 0.022888 | 0.23346 | 0.13275 | 0.25177 | 0.25635 | 122.6715 | 122.6852 | -0.24719 | -0.23804 | 122.4426 | 122.5616 | 122.4701 | 122.58
3848.0781 | 122.7036 | -122.5891 | 0.11902 | 0.0025177 | -0.010952 | -0.079224 | -0.0059109 | -0.033434 | -0.051663 | -0.044023 | -0.0021057 | 0.0018948 | 0.0094166 | -0.012484 | -0.21937 | -0.017914 | -0.025816 | -0.1236 | 0.1236 | -0.13733 | -0.15106 | -0.009155 | -0.14648 | -0.07782 | -0.036621 | 0.12817 | -0.11902 | -0.050354 | 0.050354 | -0.013733 | 0.032043 | 122.4518 | 0.004577 | -0.27008 | 122.58 | 122.5113 | 122.4426 | 0.059509 | -0.009155 | 122.4701 | 0.009155 | -0.16937 | 122.6395 | 122.6212 | 122.5754 | 0.15106 | 0.10529 | 0.12817 | -0.013733 | 0.16937 | 0.068665 | 0.26093 | 0.24719 | 122.7127 | 122.7173 | -0.25635 | -0.23804 | 122.438 | 122.5388 | 122.4655 | 122.5525
3849.875 | 122.8409 | -122.5433 | 0.086975 | 0.0025177 | -0.016934 | -0.078583 | -0.0074063 | -0.029589 | -0.05209 | -0.042528 | -0.0051575 | 0.0031766 | 0.0072802 | -0.015688 | -0.22022 | -0.020478 | -0.02368 | -0.082397 | 0.086975 | -0.1236 | -0.050354 | 0.11902 | -0.050354 | 0.045776 | 0.10071 | 0.09613 | -0.10071 | 0.07782 | 0.20142 | 0.15564 | 0.15564 | 122.4197 | 0 | -0.13733 | 122.6624 | 122.5891 | 122.493 | 0.16937 | 0.073242 | 122.4426 | 0.009155 | -0.009155 | 122.7448 | 122.699 | 122.699 | 0.25635 | 0.25635 | 0.24261 | 0.073242 | 0.30212 | 0.17853 | 0.21057 | 0.19684 | 122.6303 | 122.6395 | -0.21057 | -0.18768 | 122.493 | 122.6212 | 122.4609 | 122.644
3851.6875 | 122.7219 | -122.58 | 0.13733 | 0.0025177 | -0.013729 | -0.080506 | -0.0074063 | -0.029375 | -0.050167 | -0.041674 | -0.0021057 | 0.0038174 | 0.0079212 | -0.018679 | -0.21851 | -0.018982 | -0.020262 | -0.09613 | 0.10529 | -0.12817 | -0.13275 | 0.027466 | -0.12817 | -0.059509 | -0.018311 | 0.14648 | -0.10529 | -0.050354 | 0.068665 | 0.009155 | 0.032043 | 122.4518 | -0.032043 | -0.27008 | 122.6074 | 122.5204 | 122.4518 | 0.068665 | 0 | 122.4747 | 0.009155 | -0.18768 | 122.6486 | 122.612 | 122.5891 | 0.13733 | 0.11444 | 0.15564 | -0.004577 | 0.17395 | 0.054932 | 0.23346 | 0.25177 | 122.6852 | 122.7264 | -0.2655 | -0.24262 | 122.4472 | 122.5296 | 122.4838 | 122.5616
3853.5469 | 122.731 | -122.5708 | 0.13733 | -0.0051118 | -0.010739 | -0.079438 | -0.0039883 | -0.027025 | -0.051235 | -0.041246 | -0.0082091 | 0.0048856 | 0.0053576 | -0.0050072 | -0.22107 | -0.018342 | -0.022826 | -0.14191 | 0.10986 | -0.13733 | -0.15106 | -0.041199 | -0.20599 | -0.086975 | -0.073242 | 0.14191 | -0.12817 | -0.027466 | 0.022888 | -0.054932 | 0.059509 | 122.4335 | -0.027466 | -0.28839 | 122.5296 | 122.4838 | 122.3648 | 0.050354 | -0.068665 | 122.4426 | 0.004578 | -0.16479 | 122.5937 | 122.6303 | 122.5159 | 0.18768 | 0.073242 | 0.09613 | -0.013733 | 0.15106 | 0.10071 | 0.24719 | 0.27008 | 122.6807 | 122.7127 | -0.27466 | -0.2655 | 122.4197 | 122.5433 | 122.4289 | 122.4976
3855.2656 | 122.8134 | -122.5708 | 0.10986 | 0.0025177 | -0.011593 | -0.079438 | -0.0065517 | -0.031511 | -0.049954 | -0.037615 | -0.0051575 | 0.0027494 | 0.008562 | -0.021243 | -0.21872 | -0.019196 | -0.021544 | -0.10529 | 0.082397 | -0.10529 | -0.10071 | 0.050354 | -0.09613 | -0.018311 | 0.022888 | 0.10071 | -0.086975 | 0.032043 | 0.12817 | 0.073242 | 0.11902 | 122.4655 | -0.027466 | -0.21057 | 122.6212 | 122.5525 | 122.4747 | 0.086975 | 0.009156 | 122.4838 | -0.009155 | -0.07782 | 122.699 | 122.6898 | 122.644 | 0.20599 | 0.16022 | 0.15564 | 0.004578 | 0.21515 | 0.11902 | 0.18768 | 0.18768 | 122.6532 | 122.6715 | -0.21515 | -0.19684 | 122.4701 | 122.6028 | 122.4655 | 122.5937
3856.9844 | 122.7356 | -122.5754 | 0.12817 | -0.0051118 | -0.013943 | -0.080292 | -0.0050565 | -0.030657 | -0.050808 | -0.041246 | -0.0051575 | 0.0040312 | 0.007494 | -0.015475 | -0.21766 | -0.020905 | -0.027739 | -0.11902 | 0.10986 | -0.12817 | -0.14648 | 0.018311 | -0.14648 | -0.054932 | -0.032043 | 0.13275 | -0.13275 | -0.041199 | 0.059509 | 0.009155 | 0.045776 | 122.4472 | -0.018311 | -0.27466 | 122.5937 | 122.5204 | 122.4289 | 0.073242 | -0.01831 | 122.4426 | 0.004577 | -0.16937 | 122.6349 | 122.6212 | 122.5845 | 0.17853 | 0.14191 | 0.14649 | -0.01831 | 0.19226 | 0.091552 | 0.23804 | 0.2655 | 122.6852 | 122.7081 | -0.25635 | -0.26093 | 122.4289 | 122.5342 | 122.4564 | 122.5433
3858.7188 | 122.7402 | -122.5983 | 0.11902 | 0.010147 | -0.013943 | -0.078797 | -0.0059109 | -0.03322 | -0.052517 | -0.041887 | -0.0021057 | 0.0036038 | 0.007494 | -0.010989 | -0.2215 | -0.018342 | -0.025816 | -0.12817 | 0.12817 | -0.14648 | -0.17395 | -0.032043 | -0.15106 | -0.082397 | -0.059509 | 0.15106 | -0.11444 | -0.041199 | 0.064087 | 0 | 0.059509 | 122.4518 | 0.009155 | -0.29297 | 122.5662 | 122.5159 | 122.4472 | 0.064087 | -0.004578 | 122.4838 | 0.032043 | -0.16022 | 122.6624 | 122.6578 | 122.5983 | 0.17395 | 0.11444 | 0.11444 | -0.027466 | 0.17853 | 0.073242 | 0.27466 | 0.2655 | 122.7264 | 122.7493 | -0.2655 | -0.23346 | 122.4243 | 122.5571 | 122.4701 | 122.5388
3860.4688 | 122.8455 | -122.5342 | 0.073242 | 0.0025177 | -0.010311 | -0.079438 | -0.0065517 | -0.032152 | -0.048886 | -0.038683 | -0.0021057 | 0.0018948 | 0.0066394 | -0.013125 | -0.22321 | -0.01941 | -0.024748 | -0.068665 | 0.10529 | -0.1236 | -0.054932 | 0.10071 | -0.091553 | -0.004578 | 0.09613 | 0.09613 | -0.10986 | 0.086975 | 0.16479 | 0.10986 | 0.16479 | 122.4106 | 0.032044 | -0.12817 | 122.6349 | 122.5296 | 122.4426 | 0.11902 | 0.032043 | 122.4243 | 0.022888 | 0.013733 | 122.699 | 122.699 | 122.644 | 0.27466 | 0.21973 | 0.2243 | 0.068664 | 0.27466 | 0.19684 | 0.22888 | 0.20599 | 122.6395 | 122.6303 | -0.19684 | -0.18311 | 122.4792 | 122.6212 | 122.4655 | 122.6303
3862.1719 | 122.85 | -122.5662 | 0.086975 | 0.0025177 | -0.013516 | -0.079224 | -0.0082607 | -0.030657 | -0.050808 | -0.043169 | -0.0051575 | 0.0010404 | 0.0081348 | -0.014834 | -0.22065 | -0.016846 | -0.027312 | -0.10071 | 0.09613 | -0.12817 | -0.07782 | 0.073242 | -0.064087 | 0.013733 | 0.050354 | 0.10529 | -0.10986 | 0.054932 | 0.16937 | 0.11444 | 0.13275 | 122.438 | 0.009155 | -0.16479 | 122.6395 | 122.58 | 122.5021 | 0.14191 | 0.064087 | 122.4564 | 0.018311 | -0.032043 | 122.7356 | 122.699 | 122.6807 | 0.24261 | 0.2243 | 0.20142 | 0.050354 | 0.27924 | 0.16479 | 0.2243 | 0.21515 | 122.6624 | 122.6715 | -0.21515 | -0.19684 | 122.4884 | 122.6212 | 122.4655 | 122.6166
3863.8906 | 122.8592 | -122.5754 | 0.09613 | 0.010147 | -0.013943 | -0.080506 | -0.0067653 | -0.030871 | -0.048672 | -0.036974 | -0.0021057 | 0.0027494 | 0.0087756 | -0.019534 | -0.22001 | -0.020051 | -0.025176 | -0.07782 | 0.07782 | -0.09613 | -0.050354 | 0.13275 | -0.032043 | 0.050354 | 0.14191 | 0.09613 | -0.091553 | 0.091553 | 0.21515 | 0.14648 | 0.16479 | 122.4792 | -0.01831 | -0.14648 | 122.7081 | 122.6257 | 122.5433 | 0.14648 | 0.064087 | 122.4838 | 0 | -0.004577 | 122.7905 | 122.7402 | 122.7219 | 0.25635 | 0.23804 | 0.22888 | 0.045776 | 0.3067 | 0.18311 | 0.17395 | 0.18768 | 122.6532 | 122.6715 | -0.19226 | -0.18768 | 122.525 | 122.6669 | 122.4976 | 122.7173
3865.6562 | 122.8729 | -122.5616 | 0.082397 | -0.012741 | -0.010311 | -0.075806 | -0.0042019 | -0.028307 | -0.050381 | -0.042742 | -0.0051575 | 0.0044584 | 0.0081348 | -0.012484 | -0.22065 | -0.019196 | -0.027098 | -0.041199 | 0.086975 | -0.10071 | -0.032043 | 0.11444 | -0.073242 | 0.013733 | 0.11902 | 0.091553 | -0.09613 | 0.09613 | 0.17853 | 0.10529 | 0.16022 | 122.4609 | 0.004578 | -0.11444 | 122.6761 | 122.5754 | 122.4884 | 0.11444 | 0.027466 | 122.4655 | 0.009156 | 0.013733 | 122.7402 | 122.7219 | 122.6669 | 0.25635 | 0.20142 | 0.21515 | 0.068665 | 0.27466 | 0.19226 | 0.18768 | 0.18768 | 122.6486 | 122.6532 | -0.18311 | -0.17853 | 122.5296 | 122.6578 | 122.5204 | 122.6807
3867.4219 | 122.7631 | -122.5937 | 0.12817 | 0.0025177 | -0.012875 | -0.079865 | -0.0061245 | -0.029802 | -0.049313 | -0.042742 | 0.00094606 | 0.0038174 | 0.0083484 | -0.0086388 | -0.21851 | -0.018128 | -0.024321 | -0.13275 | 0.10071 | -0.14191 | -0.16022 | -0.018311 | -0.15564 | -0.082397 | -0.045776 | 0.13733 | -0.1236 | -0.032043 | 0.064087 | 0.009155 | 0.073242 | 122.4518 | -0.027466 | -0.28839 | 122.5754 | 122.5113 | 122.438 | 0.05951 | -0.013733 | 122.4701 | 0.009155 | -0.16022 | 122.6578 | 122.6669 | 122.6028 | 0.19684 | 0.13275 | 0.1236 | -0.01831 | 0.18768 | 0.091553 | 0.24262 | 0.26093 | 122.6944 | 122.731 | -0.27008 | -0.25177 | 122.4335 | 122.5616 | 122.4609 | 122.5479
3869.1406 | 122.7905 | -122.5662 | 0.10529 | 0.0025177 | -0.013516 | -0.079651 | -0.0078335 | -0.033648 | -0.051876 | -0.039537 | 0.00094606 | 0.00018579 | 0.005785 | -0.018038 | -0.21958 | -0.017701 | -0.024321 | -0.054932 | 0.07782 | -0.09613 | -0.073242 | 0.10071 | -0.022888 | 0.022888 | 0.068665 | 0.11444 | -0.091553 | 0.013733 | 0.13275 | 0.064087 | 0.091553 | 122.4701 | -0.027466 | -0.17853 | 122.6669 | 122.5891 | 122.5433 | 0.11902 | 0.073242 | 122.4747 | 0.009155 | -0.091553 | 122.699 | 122.6578 | 122.6303 | 0.18311 | 0.15564 | 0.19684 | 0.022888 | 0.2243 | 0.10529 | 0.17395 | 0.20599 | 122.644 | 122.6807 | -0.20142 | -0.19684 | 122.493 | 122.58 | 122.5113 | 122.6349
3870.8438 | 122.7768 | -122.58 | 0.1236 | -0.0051118 | -0.011807 | -0.080506 | -0.0037747 | -0.029589 | -0.048672 | -0.039324 | -0.0051575 | 0.004672 | 0.0081348 | -0.0099206 | -0.22214 | -0.018555 | -0.024107 | -0.082397 | 0.10986 | -0.13733 | -0.09613 | 0.054932 | -0.10529 | -0.036621 | 0.050354 | 0.11902 | -0.10529 | 0.032043 | 0.10529 | 0.036621 | 0.086975 | 122.4426 | -0.013733 | -0.21973 | 122.6349 | 122.5433 | 122.4747 | 0.10071 | 0.032043 | 122.4747 | -0.004577 | -0.091553 | 122.6852 | 122.6669 | 122.6166 | 0.19226 | 0.14191 | 0.19226 | 0.041199 | 0.21057 | 0.13733 | 0.24719 | 0.22431 | 122.6898 | 122.699 | -0.26093 | -0.22888 | 122.4838 | 122.612 | 122.4976 | 122.6303
3872.5625 | 122.8363 | -122.5754 | 0.091553 | -0.012741 | -0.013516 | -0.080079 | -0.0048427 | -0.029802 | -0.050167 | -0.03911 | -0.0051575 | 0.0014676 | 0.0059986 | -0.015048 | -0.21808 | -0.019837 | -0.022826 | -0.11902 | 0.082397 | -0.12817 | -0.10071 | 0.068665 | -0.10071 | -0.013733 | 0.018311 | 0.11444 | -0.10986 | 0.036621 | 0.15564 | 0.09613 | 0.11902 | 122.4472 | -0.009156 | -0.19226 | 122.644 | 122.5616 | 122.4747 | 0.11444 | 0.027466 | 122.4655 | 0.022888 | -0.054932 | 122.731 | 122.6944 | 122.6715 | 0.22888 | 0.20599 | 0.19684 | 0.027466 | 0.2655 | 0.14648 | 0.21057 | 0.2243 | 122.6578 | 122.6898 | -0.21973 | -0.20142 | 122.4747 | 122.612 | 122.4564 | 122.5937
3874.2812 | 122.7676 | -122.5891 | 0.10529 | -0.012741 | -0.012234 | -0.079011 | -0.0048427 | -0.026812 | -0.051022 | -0.043169 | 0.00094606 | 0.0048856 | 0.0072802 | -0.01163 | -0.2183 | -0.018982 | -0.024962 | -0.10529 | 0.10071 | -0.14191 | -0.16937 | -0.018311 | -0.19684 | -0.086975 | -0.027466 | 0.1236 | -0.12817 | 0.004578 | 0.050354 | -0.004578 | 0.073242 | 122.4472 | -0.004578 | -0.27466 | 122.5708 | 122.5021 | 122.3923 | 0.054932 | -0.054931 | 122.4609 | 0.01831 | -0.10071 | 122.6395 | 122.6624 | 122.5845 | 0.20142 | 0.1236 | 0.1236 | -0.027466 | 0.17853 | 0.13275 | 0.24262 | 0.25177 | 122.6898 | 122.7127 | -0.24719 | -0.23346 | 122.4197 | 122.5937 | 122.4838 | 122.5616
3876.0312 | 122.7905 | -122.5708 | 0.11902 | -0.012741 | -0.012448 | -0.077729 | -0.0029201 | -0.028734 | -0.051449 | -0.039965 | -0.0051575 | 0.0027494 | 0.0062122 | -0.014834 | -0.22022 | -0.017701 | -0.023039 | -0.07782 | 0.1236 | -0.12817 | -0.10529 | 0.045776 | -0.10986 | -0.050354 | 0.064087 | 0.13275 | -0.10071 | 0.027466 | 0.09613 | 0.036621 | 0.082397 | 122.4426 | 0.004577 | -0.22431 | 122.6166 | 122.5204 | 122.4609 | 0.07782 | 0.018311 | 122.4701 | 0.013732 | -0.091553 | 122.6669 | 122.6532 | 122.6074 | 0.18311 | 0.13733 | 0.17395 | 0.022888 | 0.19684 | 0.12817 | 0.25177 | 0.23346 | 122.6944 | 122.7036 | -0.24719 | -0.21973 | 122.4655 | 122.5983 | 122.493 | 122.6349
3877.75 | 122.7676 | -122.6028 | 0.1236 | -0.0051118 | -0.015225 | -0.080933 | -0.0076199 | -0.033648 | -0.051235 | -0.042955 | 0.00094606 | 0.0025358 | 0.0081348 | -0.013339 | -0.22001 | -0.018128 | -0.022826 | -0.082397 | 0.073242 | -0.10986 | -0.082397 | 0.082397 | -0.054932 | -0.018311 | 0.022888 | 0.1236 | -0.10071 | -0.027466 | 0.073242 | 0.018311 | 0.068665 | 122.493 | -0.050354 | -0.20599 | 122.6852 | 122.5845 | 122.5479 | 0.091552 | 0.054931 | 122.5021 | 0 | -0.15106 | 122.6761 | 122.6715 | 122.6212 | 0.16937 | 0.11902 | 0.19226 | 0.027466 | 0.17395 | 0.073242 | 0.18311 | 0.2243 | 122.6761 | 122.7264 | -0.23346 | -0.2243 | 122.5204 | 122.5754 | 122.5204 | 122.6257
3879.4844 | 122.8409 | -122.5708 | 0.10986 | -0.0051118 | -0.0094571 | -0.079224 | -0.0063381 | -0.030871 | -0.050381 | -0.040392 | 0.00094606 | 0.002963 | 0.0077076 | -0.017397 | -0.2183 | -0.019623 | -0.021117 | -0.073242 | 0.068665 | -0.086975 | -0.050354 | 0.1236 | -0.073242 | 0.004578 | 0.10071 | 0.10071 | -0.091553 | 0.064087 | 0.14191 | 0.086975 | 0.1236 | 122.4838 | -0.041198 | -0.16022 | 122.6944 | 122.5754 | 122.4976 | 0.091553 | 0.013733 | 122.4792 | -0.009155 | -0.045776 | 122.7127 | 122.6944 | 122.6578 | 0.21515 | 0.17853 | 0.21057 | 0.036621 | 0.23346 | 0.15564 | 0.15564 | 0.19226 | 122.6395 | 122.6715 | -0.19684 | -0.20142 | 122.5204 | 122.6349 | 122.4976 | 122.6715
3881.2031 | 122.7493 | -122.6257 | 0.13275 | -0.0051118 | -0.015225 | -0.080079 | -0.0056973 | -0.034075 | -0.053799 | -0.041246 | -0.0021057 | 0.0023222 | 0.0083484 | -0.014834 | -0.21744 | -0.018128 | -0.024107 | -0.14648 | 0.10529 | -0.13733 | -0.15106 | 0.004578 | -0.1236 | -0.073242 | -0.050354 | 0.1236 | -0.1236 | -0.050354 | 0.054932 | -0.004578 | 0.036621 | 122.4884 | -0.027465 | -0.28381 | 122.6303 | 122.5525 | 122.5021 | 0.064087 | 0.013733 | 122.5021 | -0.009155 | -0.18311 | 122.6807 | 122.6624 | 122.6212 | 0.16022 | 0.11902 | 0.14191 | -0.013733 | 0.17853 | 0.073242 | 0.24262 | 0.24719 | 122.731 | 122.7493 | -0.27008 | -0.25635 | 122.4747 | 122.5754 | 122.4792 | 122.5754
3882.9688 | 122.8363 | -122.6028 | 0.10071 | 0.0025177 | -0.015866 | -0.079438 | -0.0074063 | -0.032793 | -0.051449 | -0.042528 | 0.00094606 | 0.0031766 | 0.0087756 | -0.014834 | -0.21958 | -0.020478 | -0.024748 | -0.054932 | 0.068665 | -0.1236 | -0.036621 | 0.1236 | -0.036621 | 0.022888 | 0.07782 | 0.11444 | -0.086975 | 0.036621 | 0.15564 | 0.10986 | 0.1236 | 122.4792 | -0.032043 | -0.13733 | 122.7264 | 122.6257 | 122.5662 | 0.14648 | 0.086975 | 122.5159 | 0.013733 | -0.064087 | 122.7585 | 122.7264 | 122.7127 | 0.21057 | 0.19684 | 0.24719 | 0.086975 | 0.24261 | 0.1236 | 0.19226 | 0.20142 | 122.6715 | 122.7173 | -0.2243 | -0.18768 | 122.5662 | 122.6395 | 122.5479 | 122.6807
3884.7344 | 122.8592 | -122.5937 | 0.091553 | -0.02037 | -0.012448 | -0.080506 | -0.0071927 | -0.03023 | -0.049099 | -0.043596 | -0.0021057 | 0.00061319 | 0.0092028 | -0.007998 | -0.22001 | -0.018982 | -0.023894 | -0.059509 | 0.086975 | -0.10529 | -0.064087 | 0.11902 | -0.068665 | 0.013733 | 0.10986 | 0.11444 | -0.091553 | 0.064087 | 0.14191 | 0.09613 | 0.11902 | 122.4884 | -0.004578 | -0.15564 | 122.7127 | 122.6074 | 122.525 | 0.11902 | 0.036621 | 122.5021 | 0.022888 | -0.027466 | 122.7356 | 122.7127 | 122.6898 | 0.21057 | 0.18768 | 0.22431 | 0.041199 | 0.23346 | 0.15564 | 0.19226 | 0.20599 | 122.6807 | 122.7081 | -0.19684 | -0.18311 | 122.5296 | 122.6578 | 122.5342 | 122.7036
3886.4531 | 122.8867 | -122.58 | 0.082397 | 0.010147 | -0.015866 | -0.078797 | -0.0061245 | -0.033434 | -0.050808 | -0.042528 | -0.0021057 | 0.0021084 | 0.0083484 | -0.012484 | -0.22214 | -0.020905 | -0.022398 | -0.09613 | 0.07782 | -0.11902 | -0.073242 | 0.091553 | -0.064087 | 0.013733 | 0.073242 | 0.10986 | -0.10071 | 0.064087 | 0.17853 | 0.11444 | 0.13733 | 122.4609 | -0.004577 | -0.15564 | 122.6715 | 122.5937 | 122.5159 | 0.13275 | 0.054932 | 122.4792 | 0.027466 | -0.01831 | 122.7585 | 122.7173 | 122.6944 | 0.23804 | 0.21515 | 0.21057 | 0.045777 | 0.27924 | 0.1648 | 0.19684 | 0.21057 | 122.6578 | 122.6898 | -0.20142 | -0.18311 | 122.5067 | 122.644 | 122.4838 | 122.6532
3888.2188 | 122.7448 | -122.612 | 0.13733 | 0.010147 | -0.010952 | -0.079438 | -0.0044155 | -0.029589 | -0.049526 | -0.042314 | -0.0021057 | 0.0050992 | 0.0064258 | -0.015048 | -0.21915 | -0.020905 | -0.026457 | -0.10529 | 0.10986 | -0.13275 | -0.15564 | -0.050354 | -0.19226 | -0.11444 | -0.073242 | 0.15106 | -0.12817 | -0.041199 | 0.013733 | -0.045776 | 0.054932 | 122.4792 | -0.027466 | -0.29297 | 122.5616 | 122.4976 | 122.4197 | 0.01831 | -0.05951 | 122.4838 | 0.013733 | -0.17853 | 122.6257 | 122.6669 | 122.5662 | 0.18311 | 0.082398 | 0.082397 | -0.022889 | 0.14191 | 0.086975 | 0.24261 | 0.27924 | 122.7219 | 122.7631 | -0.27008 | -0.2655 | 122.4564 | 122.5708 | 122.5067 | 122.5388
3889.9219 | 122.85 | -122.5845 | 0.091553 | -0.0051118 | -0.012875 | -0.080292 | -0.0071927 | -0.030443 | -0.052944 | -0.040392 | -0.0021057 | 0.0025358 | 0.0066394 | -0.017825 | -0.21937 | -0.018342 | -0.022612 | -0.09613 | 0.09613 | -0.1236 | -0.10986 | 0.054932 | -0.10071 | -0.022888 | 0.027466 | 0.10071 | -0.10071 | 0.036621 | 0.15106 | 0.091553 | 0.11444 | 122.4609 | 0.004577 | -0.20142 | 122.6395 | 122.5616 | 122.4838 | 0.10071 | 0.022888 | 122.4838 | 0.009155 | -0.054932 | 122.7356 | 122.699 | 122.6761 | 0.21515 | 0.19226 | 0.17853 | 0.013733 | 0.25177 | 0.13733 | 0.21973 | 0.20142 | 122.6807 | 122.6852 | -0.21515 | -0.19226 | 122.4747 | 122.6212 | 122.4884 | 122.612
3891.6406 | 122.8226 | -122.612 | 0.10071 | -0.0051118 | -0.0098843 | -0.07837 | -0.0056973 | -0.027239 | -0.051022 | -0.036547 | -0.0051575 | 0.0061674 | 0.0066394 | -0.0050072 | -0.21894 | -0.017273 | -0.027739 | -0.07782 | 0.1236 | -0.14191 | -0.10529 | 0.054932 | -0.10986 | -0.041199 | 0.054932 | 0.14191 | -0.10529 | 0.022888 | 0.09613 | 0.050354 | 0.10071 | 122.4701 | 0.022888 | -0.20599 | 122.6669 | 122.5708 | 122.5021 | 0.10071 | 0.032044 | 122.5067 | 0.041199 | -0.07782 | 122.7081 | 122.7127 | 122.6624 | 0.20599 | 0.15564 | 0.19684 | 0.036621 | 0.20142 | 0.12817 | 0.2655 | 0.24719 | 122.7356 | 122.7539 | -0.24262 | -0.20599 | 122.5067 | 122.6349 | 122.5342 | 122.6669
3893.375 | 122.7814 | -122.6257 | 0.13275 | 0.0025177 | -0.01437 | -0.080506 | -0.0069791 | -0.029802 | -0.052517 | -0.042314 | -0.0021057 | 0.0018948 | 0.0087756 | -0.011202 | -0.21915 | -0.020264 | -0.019621 | -0.14648 | 0.14191 | -0.15564 | -0.16022 | -0.009155 | -0.14191 | -0.059509 | -0.050354 | 0.15564 | -0.1236 | -0.045776 | 0.050354 | -0.009155 | 0.036621 | 122.4701 | 0.009156 | -0.29297 | 122.6166 | 122.5662 | 122.4838 | 0.096131 | 0.013733 | 122.5021 | 0.022889 | -0.17853 | 122.6761 | 122.6624 | 122.6166 | 0.16022 | 0.11444 | 0.14649 | -0.004577 | 0.17395 | 0.07782 | 0.29755 | 0.27924 | 122.7676 | 122.7814 | -0.28839 | -0.25635 | 122.4655 | 122.58 | 122.4792 | 122.5754
3895.125 | 122.7676 | -122.6395 | 0.12817 | 0.0025177 | -0.014584 | -0.079865 | -0.0080471 | -0.030871 | -0.052304 | -0.043169 | -0.0021057 | 0.002963 | 0.0081348 | -0.017397 | -0.2183 | -0.020264 | -0.022826 | -0.11444 | 0.10986 | -0.12817 | -0.15106 | 0.013733 | -0.13733 | -0.068665 | -0.036621 | 0.14191 | -0.11902 | -0.041199 | 0.045776 | 0 | 0.041199 | 122.5113 | -0.018311 | -0.27924 | 122.6532 | 122.5708 | 122.5021 | 0.059509 | -0.009155 | 122.5204 | 0.013733 | -0.16937 | 122.6852 | 122.6807 | 122.6395 | 0.16022 | 0.11902 | 0.14191 | -0.022888 | 0.16479 | 0.07782 | 0.23804 | 0.26093 | 122.7493 | 122.7814 | -0.25635 | -0.24719 | 122.4884 | 122.5983 | 122.525 | 122.6028
3896.8438 | 122.9141 | -122.5754 | 0.091553 | 0.0025177 | -0.012875 | -0.080079 | -0.0056973 | -0.034716 | -0.049954 | -0.03911 | 0.00094606 | 0.0014676 | 0.0096302 | -0.015048 | -0.21808 | -0.020051 | -0.023467 | -0.07782 | 0.07782 | -0.09613 | -0.041199 | 0.12817 | -0.032043 | 0.050354 | 0.13275 | 0.091553 | -0.073242 | 0.09613 | 0.21973 | 0.15106 | 0.16022 | 122.4792 | -0.013733 | -0.13275 | 122.7036 | 122.6257 | 122.5433 | 0.14648 | 0.064087 | 122.5021 | 0 | 0.004577 | 122.7951 | 122.7356 | 122.7264 | 0.23346 | 0.2243 | 0.2243 | 0.054931 | 0.29297 | 0.16937 | 0.17395 | 0.16479 | 122.6532 | 122.6669 | -0.18768 | -0.16479 | 122.5342 | 122.6715 | 122.4976 | 122.7081
3898.6094 | 122.7722 | -122.6074 | 0.12817 | -0.02037 | -0.0094571 | -0.079011 | -0.0044155 | -0.031939 | -0.049954 | -0.038042 | -0.0051575 | 0.004672 | 0.006853 | -0.0065026 | -0.2215 | -0.017487 | -0.021758 | -0.082397 | 0.1236 | -0.14191 | -0.12817 | 0.018311 | -0.13733 | -0.091553 | 0.013733 | 0.13275 | -0.10986 | -0.018311 | 0.054932 | -0.022888 | 0.050354 | 122.4655 | -0.004578 | -0.25635 | 122.6257 | 122.5159 | 122.4701 | 0.050354 | 0.004578 | 122.4976 | 0.004577 | -0.14649 | 122.6624 | 122.6578 | 122.5845 | 0.16022 | 0.086975 | 0.16022 | 0.013733 | 0.16479 | 0.091552 | 0.2655 | 0.24261 | 122.731 | 122.7402 | -0.27008 | -0.23804 | 122.4792 | 122.5891 | 122.525 | 122.6212
3900.5 | 122.7768 | -122.6349 | 0.11444 | -0.0051118 | -0.010739 | -0.076661 | -0.0033475 | -0.025957 | -0.051449 | -0.044237 | -0.0021057 | 0.0025358 | 0.0077076 | -0.013979 | -0.22001 | -0.01941 | -0.02368 | -0.086975 | 0.10529 | -0.14191 | -0.12817 | 0.004578 | -0.15564 | -0.07782 | -0.004578 | 0.14648 | -0.1236 | -0.013733 | 0.041199 | -0.036621 | 0.041199 | 122.493 | -0.009155 | -0.24262 | 122.6395 | 122.5571 | 122.4792 | 0.064087 | -0.013733 | 122.5113 | 0.032043 | -0.12817 | 122.6761 | 122.6761 | 122.5983 | 0.16479 | 0.086975 | 0.14649 | 0.013733 | 0.16479 | 0.10986 | 0.24719 | 0.27008 | 122.7402 | 122.7814 | -0.25635 | -0.23804 | 122.5067 | 122.6212 | 122.5479 | 122.6303
3902.3125 | 122.8088 | -122.6578 | 0.13733 | -0.012741 | -0.014157 | -0.078583 | -0.0054837 | -0.029375 | -0.051663 | -0.039751 | -0.0021057 | 0.0042448 | 0.0066394 | -0.01163 | -0.21894 | -0.017273 | -0.021544 | -0.14648 | 0.12817 | -0.14191 | -0.16479 | -0.022888 | -0.14191 | -0.07782 | -0.041199 | 0.13275 | -0.12817 | -0.041199 | 0.07782 | 0.009155 | 0.059509 | 122.5159 | -0.009155 | -0.30212 | 122.6349 | 122.58 | 122.5159 | 0.064087 | 0 | 122.5296 | -0.004578 | -0.17853 | 122.7356 | 122.7173 | 122.6669 | 0.18768 | 0.13733 | 0.11902 | -0.022888 | 0.20599 | 0.086975 | 0.27008 | 0.26093 | 122.7859 | 122.7905 | -0.27924 | -0.2655 | 122.493 | 122.6166 | 122.5113 | 122.6166
3904.0469 | 122.8867 | -122.5891 | 0.07782 | -0.012741 | -0.011166 | -0.078583 | -0.0071927 | -0.03258 | -0.050381 | -0.039965 | 0.0039979 | 0.00039959 | 0.0083484 | -0.012484 | -0.21915 | -0.020051 | -0.023039 | -0.050354 | 0.086975 | -0.09613 | -0.032043 | 0.13275 | -0.059509 | 0.027466 | 0.11902 | 0.07782 | -0.086975 | 0.082397 | 0.17853 | 0.10529 | 0.15106 | 122.493 | 0.009155 | -0.10986 | 122.7219 | 122.6166 | 122.5296 | 0.1236 | 0.036621 | 122.5021 | 0 | 0.004577 | 122.7676 | 122.7402 | 122.6944 | 0.23804 | 0.19226 | 0.22888 | 0.064087 | 0.2655 | 0.16937 | 0.1831 | 0.16479 | 122.6761 | 122.6669 | -0.17395 | -0.16479 | 122.5571 | 122.6715 | 122.5388 | 122.7081
3905.8438 | 122.8317 | -122.644 | 0.11902 | 0.0025177 | -0.012448 | -0.080933 | -0.0074063 | -0.033007 | -0.051022 | -0.042528 | -0.0021057 | 0.0021084 | 0.0081348 | -0.0056482 | -0.21958 | -0.018128 | -0.022612 | -0.11444 | 0.10071 | -0.14191 | -0.13733 | 0.004578 | -0.11444 | -0.073242 | 0.004578 | 0.15564 | -0.11902 | 0.004578 | 0.09613 | 0.032043 | 0.091553 | 122.5021 | -0.018311 | -0.25635 | 122.6486 | 122.5708 | 122.5296 | 0.068665 | 0.027466 | 122.525 | 0.036621 | -0.11444 | 122.7402 | 122.7356 | 122.6761 | 0.21057 | 0.15106 | 0.14649 | 0.004578 | 0.21515 | 0.1236 | 0.24262 | 0.27466 | 122.7448 | 122.7997 | -0.26093 | -0.23804 | 122.5067 | 122.6486 | 122.5296 | 122.6486
3907.6562 | 122.9279 | -122.5937 | 0.091553 | -0.012741 | -0.015438 | -0.080719 | -0.0091153 | -0.031511 | -0.048458 | -0.042955 | -0.0051575 | 0.0014676 | 0.0081348 | -0.024233 | -0.21872 | -0.022187 | -0.02133 | -0.091553 | 0.086975 | -0.10071 | -0.045776 | 0.14648 | -0.009155 | 0.059509 | 0.13275 | 0.10986 | -0.073242 | 0.10071 | 0.21515 | 0.15564 | 0.16937 | 122.493 | -0.004578 | -0.13733 | 122.7402 | 122.6532 | 122.5845 | 0.16022 | 0.091553 | 122.5204 | 0.01831 | 0.009155 | 122.8088 | 122.7631 | 122.7493 | 0.24261 | 0.22888 | 0.24719 | 0.054932 | 0.28839 | 0.17395 | 0.18768 | 0.18311 | 122.6807 | 122.7036 | -0.19226 | -0.16479 | 122.5479 | 122.6944 | 122.5021 | 122.7264
3909.3906 | 122.7722 | -122.6166 | 0.13733 | 0.0025177 | -0.0096707 | -0.078583 | -0.0046291 | -0.026598 | -0.050808 | -0.04381 | 0.0039979 | 0.0036038 | 0.008562 | -0.016543 | -0.21979 | -0.021119 | -0.020049 | -0.13275 | 0.1236 | -0.13733 | -0.17853 | -0.054932 | -0.21515 | -0.11444 | -0.07782 | 0.14191 | -0.1236 | -0.032043 | 0.041199 | -0.050354 | 0.041199 | 122.4792 | -0.013733 | -0.31586 | 122.5616 | 122.5021 | 122.4014 | 0.022888 | -0.07782 | 122.493 | 0.004578 | -0.16937 | 122.6578 | 122.6578 | 122.5662 | 0.16479 | 0.073242 | 0.082397 | -0.041199 | 0.16479 | 0.091553 | 0.26093 | 0.2655 | 122.7402 | 122.7585 | -0.27466 | -0.26093 | 122.438 | 122.5845 | 122.4838 | 122.5388
3911.1875 | 122.9141 | -122.6212 | 0.07782 | -0.012741 | -0.012234 | -0.077302 | -0.0067653 | -0.030871 | -0.050167 | -0.042742 | -0.0051575 | 0.0021084 | 0.006853 | -0.01697 | -0.21958 | -0.018982 | -0.023253 | -0.054932 | 0.068665 | -0.10529 | -0.032043 | 0.13733 | -0.073242 | 0.018311 | 0.11902 | 0.09613 | -0.082397 | 0.10071 | 0.19684 | 0.13275 | 0.15564 | 122.5159 | -0.009155 | -0.10986 | 122.7585 | 122.6395 | 122.5479 | 0.1236 | 0.032044 | 122.5388 | 0.01831 | 0.022888 | 122.818 | 122.7768 | 122.7539 | 0.23804 | 0.21515 | 0.24262 | 0.073243 | 0.27924 | 0.18311 | 0.17395 | 0.17853 | 122.6898 | 122.7173 | -0.18311 | -0.16022 | 122.5891 | 122.7219 | 122.5662 | 122.7402
3912.9219 | 122.9187 | -122.58 | 0.073242 | 0.0025177 | -0.0094571 | -0.079438 | -0.0065517 | -0.029589 | -0.048458 | -0.042528 | 0.0039979 | 0.0038174 | 0.004076 | -0.016543 | -0.22129 | -0.018769 | -0.025389 | -0.045776 | 0.064087 | -0.09613 | -0.036621 | 0.12817 | -0.068665 | 0.022888 | 0.12817 | 0.10071 | -0.082397 | 0.082397 | 0.17853 | 0.11444 | 0.14648 | 122.4838 | -0.009155 | -0.10986 | 122.7081 | 122.6028 | 122.5113 | 0.11902 | 0.027465 | 122.4976 | 0.027466 | 0.009155 | 122.7585 | 122.7264 | 122.6944 | 0.22888 | 0.19684 | 0.2243 | 0.059509 | 0.26092 | 0.16479 | 0.16022 | 0.18311 | 122.644 | 122.6807 | -0.16937 | -0.15564 | 122.5433 | 122.6624 | 122.5342 | 122.7081
3914.7188 | 122.8363 | -122.6395 | 0.12817 | 0.0025177 | -0.011807 | -0.079438 | -0.0061245 | -0.028734 | -0.050595 | -0.043596 | -0.0021057 | 0.0016812 | 0.0087756 | -0.01163 | -0.22065 | -0.020051 | -0.022612 | -0.045776 | 0.086975 | -0.091553 | -0.054932 | 0.10986 | -0.036621 | 0.004578 | 0.068665 | 0.1236 | -0.086975 | 0 | 0.10529 | 0.050354 | 0.10071 | 122.5479 | -0.041199 | -0.18311 | 122.7493 | 122.644 | 122.6028 | 0.096131 | 0.054932 | 122.5525 | -0.004578 | -0.12817 | 122.7448 | 122.7402 | 122.6898 | 0.18768 | 0.13733 | 0.20142 | 0.036621 | 0.19226 | 0.086975 | 0.17853 | 0.21057 | 122.7264 | 122.7631 | -0.21973 | -0.21515 | 122.5845 | 122.6395 | 122.5937 | 122.7081
3916.5156 | 122.9187 | -122.6303 | 0.09613 | 0.0025177 | -0.013729 | -0.082001 | -0.0078335 | -0.030657 | -0.050595 | -0.04146 | -0.0021057 | 0.00082679 | 0.0081348 | -0.022311 | -0.2215 | -0.02176 | -0.024535 | -0.091553 | 0.09613 | -0.11444 | -0.064087 | 0.10071 | -0.054932 | 0.004578 | 0.082397 | 0.10071 | -0.091553 | 0.073242 | 0.20599 | 0.13275 | 0.16022 | 122.5159 | 0 | -0.16022 | 122.731 | 122.6349 | 122.5754 | 0.11902 | 0.059509 | 122.5388 | 0.004578 | -0.022888 | 122.8363 | 122.7905 | 122.7631 | 0.25177 | 0.2243 | 0.21515 | 0.050354 | 0.29755 | 0.16479 | 0.21057 | 0.19226 | 122.7264 | 122.731 | -0.21057 | -0.18768 | 122.5662 | 122.7036 | 122.5388 | 122.7127
3918.2344 | 122.7859 | -122.6486 | 0.13733 | 0.0025177 | -0.012234 | -0.080933 | -0.0067653 | -0.031298 | -0.051235 | -0.041887 | 0.00094606 | 0.004672 | 0.006853 | -0.0043664 | -0.22022 | -0.019196 | -0.022612 | -0.14648 | 0.11444 | -0.13733 | -0.16022 | -0.009155 | -0.14648 | -0.068665 | -0.036621 | 0.13733 | -0.12817 | -0.059509 | 0.059509 | -0.018311 | 0.041199 | 122.5113 | -0.022888 | -0.29755 | 122.6395 | 122.58 | 122.5021 | 0.068664 | -0.009155 | 122.5204 | 0 | -0.19684 | 122.7081 | 122.6898 | 122.6303 | 0.16937 | 0.10986 | 0.12817 | -0.022888 | 0.18768 | 0.068665 | 0.25177 | 0.2655 | 122.7631 | 122.7859 | -0.27466 | -0.2655 | 122.4884 | 122.5891 | 122.5021 | 122.612
3920.0156 | 122.8088 | -122.6486 | 0.12817 | -0.0051118 | -0.014157 | -0.079865 | -0.0074063 | -0.034289 | -0.051022 | -0.039751 | 0.0039979 | 0.0023222 | 0.0092028 | -0.018038 | -0.22086 | -0.018769 | -0.027098 | -0.086975 | 0.10071 | -0.1236 | -0.11902 | 0.041199 | -0.10071 | -0.036621 | -0.009155 | 0.11902 | -0.1236 | -0.027466 | 0.068665 | 0.009155 | 0.050354 | 122.525 | -0.027466 | -0.24719 | 122.6898 | 122.612 | 122.5479 | 0.086975 | 0.022888 | 122.525 | -0.009155 | -0.15564 | 122.7173 | 122.699 | 122.6578 | 0.17395 | 0.13275 | 0.16479 | 0.004577 | 0.19226 | 0.09613 | 0.2243 | 0.24261 | 122.7493 | 122.7676 | -0.25177 | -0.25177 | 122.5296 | 122.6212 | 122.5616 | 122.6395
3921.7969 | 122.9187 | -122.6257 | 0.086975 | 0.0025177 | -0.011807 | -0.079865 | -0.0065517 | -0.031939 | -0.051235 | -0.039324 | -0.0051575 | 0.0021084 | 0.005785 | -0.013766 | -0.22129 | -0.017701 | -0.023467 | -0.10071 | 0.082397 | -0.10529 | -0.091553 | 0.07782 | -0.068665 | 0.027466 | 0.054932 | 0.10071 | -0.10071 | 0.059509 | 0.16479 | 0.1236 | 0.13275 | 122.5204 | -0.004578 | -0.17853 | 122.7036 | 122.6532 | 122.5571 | 0.13275 | 0.036621 | 122.525 | 0.013733 | -0.027466 | 122.7905 | 122.7585 | 122.7493 | 0.23346 | 0.2243 | 0.18311 | 0.013733 | 0.2655 | 0.16022 | 0.18768 | 0.20142 | 122.7081 | 122.7264 | -0.19226 | -0.18768 | 122.5342 | 122.6852 | 122.525 | 122.6807
3923.5781 | 122.8775 | -122.6349 | 0.091553 | 0.0025177 | -0.011166 | -0.079865 | -0.0065517 | -0.032366 | -0.048031 | -0.043169 | -0.0021057 | 0.0023222 | 0.0089892 | -0.010134 | -0.22107 | -0.020264 | -0.02368 | -0.09613 | 0.07782 | -0.10071 | -0.07782 | 0.064087 | -0.10529 | -0.004578 | 0.045776 | 0.10071 | -0.086975 | 0.045776 | 0.1236 | 0.064087 | 0.10529 | 122.5342 | -0.013733 | -0.16937 | 122.699 | 122.6303 | 122.5296 | 0.09613 | -0.004578 | 122.5479 | 0.009155 | -0.045777 | 122.7585 | 122.7402 | 122.699 | 0.19226 | 0.15106 | 0.1648 | 0.022888 | 0.21057 | 0.13275 | 0.17853 | 0.18768 | 122.7127 | 122.7356 | -0.19226 | -0.17853 | 122.5571 | 122.6807 | 122.5388 | 122.6807
3925.3125 | 122.937 | -122.6212 | 0.086975 | -0.0051118 | -0.015652 | -0.08136 | -0.0078335 | -0.028307 | -0.050595 | -0.040392 | 0.00094606 | 0.0027494 | 0.0077076 | -0.016329 | -0.21851 | -0.020905 | -0.024535 | -0.059509 | 0.10071 | -0.10071 | -0.041199 | 0.11902 | -0.032043 | 0.050354 | 0.12817 | 0.091553 | -0.10071 | 0.091553 | 0.21057 | 0.14191 | 0.17395 | 122.5204 | 0.013733 | -0.12817 | 122.7402 | 122.6715 | 122.5891 | 0.15106 | 0.068665 | 122.5204 | 0.004578 | 0.004578 | 122.8317 | 122.7951 | 122.7631 | 0.27466 | 0.24262 | 0.21973 | 0.059509 | 0.31128 | 0.19226 | 0.20142 | 0.19226 | 122.7219 | 122.7127 | -0.18768 | -0.18768 | 122.58 | 122.7127 | 122.5616 | 122.7493
3927.1094 | 122.818 | -122.6532 | 0.11902 | -0.0051118 | -0.013729 | -0.079651 | -0.0076199 | -0.031939 | -0.052731 | -0.044664 | -0.0021057 | 0.0021084 | 0.0077076 | -0.010775 | -0.22065 | -0.019837 | -0.028166 | -0.073242 | 0.082397 | -0.11444 | -0.086975 | 0.064087 | -0.07782 | -0.009155 | 0.018311 | 0.12817 | -0.10071 | -0.018311 | 0.068665 | 0.032043 | 0.059509 | 122.5388 | -0.036622 | -0.20599 | 122.7173 | 122.644 | 122.5754 | 0.10529 | 0.036621 | 122.5525 | 0.009155 | -0.13733 | 122.7219 | 122.7127 | 122.6852 | 0.16022 | 0.13275 | 0.17853 | 0.027466 | 0.16937 | 0.082397 | 0.19684 | 0.22888 | 122.7356 | 122.7814 | -0.23346 | -0.21973 | 122.5662 | 122.6349 | 122.58 | 122.6715
3928.9062 | 122.8912 | -122.6578 | 0.10529 | 0.010147 | -0.014798 | -0.079224 | -0.0074063 | -0.028521 | -0.048672 | -0.043383 | -0.0021057 | 0.0016812 | 0.0059986 | -0.013552 | -0.21872 | -0.018555 | -0.023253 | -0.11902 | 0.082397 | -0.11444 | -0.10986 | 0.050354 | -0.10529 | -0.013733 | 0.022888 | 0.11444 | -0.10071 | 0.027466 | 0.11902 | 0.073242 | 0.11902 | 122.5433 | -0.022889 | -0.21515 | 122.7081 | 122.644 | 122.5525 | 0.10071 | 0.009155 | 122.5571 | 0.009155 | -0.07782 | 122.7768 | 122.7768 | 122.731 | 0.21973 | 0.17395 | 0.16479 | 0.004578 | 0.21973 | 0.12817 | 0.19684 | 0.21515 | 122.7402 | 122.7722 | -0.21973 | -0.20599 | 122.5479 | 122.6852 | 122.5388 | 122.6807
3930.7031 | 122.8271 | -122.6944 | 0.10986 | 0.0025177 | -0.01437 | -0.079651 | -0.0065517 | -0.029802 | -0.050167 | -0.041674 | 0.00094606 | 0.0016812 | 0.0066394 | -0.013125 | -0.21894 | -0.020264 | -0.027739 | -0.068665 | 0.086975 | -0.11902 | -0.086975 | 0.07782 | -0.07782 | -0.004578 | 0.041199 | 0.13733 | -0.10986 | -0.018311 | 0.091553 | 0.036621 | 0.068665 | 122.5754 | -0.022888 | -0.19684 | 122.7722 | 122.6898 | 122.6166 | 0.11444 | 0.041199 | 122.5845 | 0.027466 | -0.12817 | 122.7859 | 122.7631 | 122.731 | 0.17853 | 0.14648 | 0.19684 | 0.032044 | 0.20142 | 0.091552 | 0.20599 | 0.24719 | 122.7814 | 122.8317 | -0.22888 | -0.21973 | 122.6074 | 122.6761 | 122.6257 | 122.7356
3932.5 | 122.937 | -122.6074 | 0.068665 | -0.0051118 | -0.013516 | -0.08136 | -0.0067653 | -0.031298 | -0.051235 | -0.041033 | -0.0021057 | 0.0031766 | 0.0064258 | -0.011202 | -0.21872 | -0.020691 | -0.025603 | -0.068665 | 0.073242 | -0.10529 | -0.036621 | 0.13733 | -0.027466 | 0.045776 | 0.15106 | 0.10986 | -0.082397 | 0.10071 | 0.21057 | 0.14648 | 0.15564 | 122.5021 | 0.004577 | -0.10529 | 122.7448 | 122.6532 | 122.58 | 0.15106 | 0.07782 | 122.525 | 0.041198 | 0.032043 | 122.818 | 122.7631 | 122.7539 | 0.23804 | 0.22888 | 0.24262 | 0.068665 | 0.29297 | 0.18311 | 0.17853 | 0.19226 | 122.6807 | 122.7173 | -0.17395 | -0.15106 | 122.5708 | 122.7081 | 122.5388 | 122.7585
3934.2812 | 122.9507 | -122.6395 | 0.086975 | 0.0025177 | -0.013516 | -0.079011 | -0.0093289 | -0.034289 | -0.052731 | -0.042528 | -0.0021057 | 0.002963 | 0.007494 | -0.01163 | -0.22001 | -0.01941 | -0.019408 | -0.059509 | 0.091553 | -0.10071 | -0.027466 | 0.15564 | -0.036621 | 0.045776 | 0.14648 | 0.10529 | -0.082397 | 0.11444 | 0.21515 | 0.15564 | 0.15106 | 122.5388 | 0.004578 | -0.11444 | 122.7951 | 122.6852 | 122.6028 | 0.14648 | 0.064087 | 122.5571 | 0.018311 | 0.027466 | 122.8546 | 122.7905 | 122.7951 | 0.23346 | 0.23804 | 0.25635 | 0.073242 | 0.29755 | 0.19684 | 0.19226 | 0.18768 | 122.731 | 122.7448 | -0.18768 | -0.16937 | 122.612 | 122.7539 | 122.58 | 122.7859
3936.0156 | 122.9553 | -122.6028 | 0.10071 | 0.0025177 | -0.01437 | -0.080292 | -0.0076199 | -0.030871 | -0.051876 | -0.041246 | -0.0021057 | 0.0010404 | 0.007494 | -0.010989 | -0.22001 | -0.019837 | -0.024748 | -0.064087 | 0.073242 | -0.10071 | -0.009155 | 0.16022 | -0.018311 | 0.054932 | 0.15106 | 0.11902 | -0.07782 | 0.10071 | 0.20599 | 0.14191 | 0.16022 | 122.5021 | -0.027466 | -0.10986 | 122.7631 | 122.6578 | 122.5845 | 0.15564 | 0.082397 | 122.525 | 0.018311 | 0 | 122.8088 | 122.7631 | 122.7448 | 0.23804 | 0.21973 | 0.26093 | 0.091553 | 0.28381 | 0.17853 | 0.17395 | 0.19684 | 122.6761 | 122.7219 | -0.20142 | -0.17853 | 122.5937 | 122.7036 | 122.5388 | 122.7539
3937.7969 | 122.9553 | -122.6166 | 0.091553 | -0.012741 | -0.013729 | -0.077942 | -0.0056973 | -0.03258 | -0.050595 | -0.042955 | -0.0021057 | 0.0014676 | 0.005785 | -0.015902 | -0.21937 | -0.019837 | -0.023894 | -0.09613 | 0.091553 | -0.10529 | -0.050354 | 0.11444 | -0.059509 | 0.032043 | 0.10986 | 0.10071 | -0.086975 | 0.091553 | 0.19226 | 0.14648 | 0.15106 | 122.5113 | 0 | -0.14191 | 122.731 | 122.6486 | 122.5571 | 0.13733 | 0.045777 | 122.5296 | 0.009155 | 0 | 122.8088 | 122.7676 | 122.7631 | 0.23804 | 0.23346 | 0.21973 | 0.054932 | 0.27924 | 0.17853 | 0.19684 | 0.18768 | 122.7081 | 122.7173 | -0.19684 | -0.17853 | 122.5662 | 122.7081 | 122.5204 | 122.7264
3939.5938 | 122.9553 | -122.6578 | 0.082397 | -0.012741 | -0.01437 | -0.080079 | -0.0071927 | -0.032152 | -0.053585 | -0.042528 | 0.00094606 | 0.0027494 | 0.0064258 | -0.017397 | -0.22001 | -0.020051 | -0.021117 | -0.054932 | 0.073242 | -0.086975 | -0.022888 | 0.16022 | -0.018311 | 0.050354 | 0.15106 | 0.09613 | -0.073242 | 0.07782 | 0.20599 | 0.14648 | 0.14648 | 122.5708 | -0.009155 | -0.10528 | 122.818 | 122.7081 | 122.6395 | 0.13733 | 0.068664 | 122.5845 | 0.013733 | -0.004577 | 122.8638 | 122.8043 | 122.8043 | 0.21973 | 0.21973 | 0.24719 | 0.064087 | 0.27924 | 0.15106 | 0.16022 | 0.16937 | 122.731 | 122.7539 | -0.16937 | -0.15564 | 122.6349 | 122.7356 | 122.6028 | 122.8088
3941.4062 | 122.7951 | -122.6944 | 0.10986 | -0.0051118 | -0.01138 | -0.079651 | -0.0020657 | -0.028307 | -0.050595 | -0.040605 | 0.00094606 | 0.0055264 | 0.010057 | -0.0054346 | -0.22022 | -0.018769 | -0.024962 | -0.10071 | 0.11902 | -0.14648 | -0.12817 | -0.009155 | -0.17853 | -0.10529 | -0.041199 | 0.14648 | -0.11902 | -0.022888 | 0.018311 | -0.036621 | 0.050354 | 122.5479 | 0.009156 | -0.23804 | 122.6852 | 122.5891 | 122.5159 | 0.041198 | -0.032044 | 122.5754 | 0.036621 | -0.13275 | 122.7127 | 122.7448 | 122.6578 | 0.16937 | 0.082398 | 0.13733 | 0.01831 | 0.13733 | 0.096131 | 0.2655 | 0.2655 | 122.8134 | 122.8409 | -0.25635 | -0.22888 | 122.5662 | 122.6715 | 122.5937 | 122.6532
3943.125 | 122.8958 | -122.6578 | 0.086975 | -0.012741 | -0.012234 | -0.079224 | -0.0067653 | -0.033434 | -0.049313 | -0.043596 | -0.0051575 | 0.0023222 | 0.0083484 | -0.018252 | -0.22001 | -0.020264 | -0.020689 | -0.10529 | 0.07782 | -0.10071 | -0.086975 | 0.068665 | -0.09613 | -0.004578 | 0.032043 | 0.10529 | -0.10986 | 0.022888 | 0.13733 | 0.073242 | 0.10529 | 122.5571 | -0.009155 | -0.17395 | 122.7264 | 122.6532 | 122.5616 | 0.09613 | 0.004578 | 122.5479 | 0.018311 | -0.064087 | 122.7951 | 122.7631 | 122.731 | 0.21515 | 0.18311 | 0.16937 | 0.013733 | 0.24719 | 0.13275 | 0.17853 | 0.21515 | 122.7356 | 122.7631 | -0.18768 | -0.19684 | 122.5708 | 122.6807 | 122.5525 | 122.6898
3944.9375 | 122.9507 | -122.644 | 0.086975 | 0.0025177 | -0.011807 | -0.079865 | -0.0065517 | -0.028734 | -0.050595 | -0.041033 | 0.0039979 | 0.004672 | 0.0047168 | -0.007998 | -0.22043 | -0.017273 | -0.020476 | -0.059509 | 0.091553 | -0.10071 | -0.045776 | 0.10529 | -0.082397 | 0 | 0.11444 | 0.10071 | -0.07782 | 0.10986 | 0.16937 | 0.086975 | 0.16479 | 122.5433 | 0.004578 | -0.13275 | 122.7493 | 122.644 | 122.5616 | 0.10071 | 0.018311 | 122.5662 | 0.013733 | 0.022888 | 122.8134 | 122.8088 | 122.731 | 0.24261 | 0.16479 | 0.20599 | 0.054932 | 0.24719 | 0.18768 | 0.19226 | 0.17853 | 122.7356 | 122.7448 | -0.18768 | -0.16479 | 122.5983 | 122.7539 | 122.5845 | 122.7585
3946.7344 | 122.818 | -122.6898 | 0.1236 | 0.017777 | -0.010952 | -0.080933 | -0.0014249 | -0.028307 | -0.051235 | -0.041246 | -0.0021057 | 0.0044584 | 0.005785 | -0.015261 | -0.21979 | -0.018128 | -0.02603 | -0.13733 | 0.11902 | -0.14191 | -0.16937 | -0.041199 | -0.21515 | -0.10986 | -0.059509 | 0.15106 | -0.11902 | -0.027466 | 0.041199 | -0.036621 | 0.064087 | 122.5479 | -0.004577 | -0.29297 | 122.6486 | 122.58 | 122.4747 | 0.032044 | -0.073242 | 122.5708 | 0.027466 | -0.15106 | 122.731 | 122.7539 | 122.6532 | 0.18311 | 0.082398 | 0.10071 | -0.027466 | 0.16022 | 0.091553 | 0.26093 | 0.27008 | 122.8088 | 122.8409 | -0.2655 | -0.24261 | 122.5204 | 122.6624 | 122.5525 | 122.6303
3948.5312 | 122.8455 | -122.6898 | 0.10986 | -0.0051118 | -0.010525 | -0.079224 | -0.0014249 | -0.031725 | -0.050167 | -0.04146 | -0.0021057 | 0.0053128 | 0.008562 | -0.015048 | -0.21808 | -0.01941 | -0.021971 | -0.10986 | 0.11902 | -0.13733 | -0.16022 | -0.018311 | -0.18768 | -0.091553 | -0.027466 | 0.15106 | -0.12817 | 0 | 0.073242 | 0 | 0.07782 | 122.5525 | 0.009156 | -0.27008 | 122.6715 | 122.5983 | 122.5021 | 0.045776 | -0.050354 | 122.5616 | 0.041199 | -0.10986 | 122.7631 | 122.7676 | 122.6898 | 0.20599 | 0.12817 | 0.11902 | -0.022888 | 0.20142 | 0.12817 | 0.25635 | 0.27924 | 122.8088 | 122.8409 | -0.24719 | -0.23804 | 122.5296 | 122.6898 | 122.58 | 122.6624
3950.2656 | 122.8592 | -122.6852 | 0.10071 | -0.0051118 | -0.012661 | -0.079651 | -0.0046291 | -0.031511 | -0.053372 | -0.041033 | -0.0021057 | 0.0048856 | 0.0077076 | -0.015902 | -0.22107 | -0.020691 | -0.019835 | -0.13733 | 0.12817 | -0.12817 | -0.16479 | -0.009155 | -0.15106 | -0.086975 | -0.050354 | 0.13275 | -0.1236 | -0.027466 | 0.068665 | 0.004578 | 0.064087 | 122.5571 | 0.027466 | -0.2655 | 122.6761 | 122.5983 | 122.5342 | 0.041199 | -0.022888 | 122.5616 | 0.032043 | -0.12817 | 122.7539 | 122.7493 | 122.6898 | 0.18768 | 0.12817 | 0.11902 | -0.036621 | 0.19226 | 0.09613 | 0.25635 | 0.25635 | 122.8134 | 122.818 | -0.22888 | -0.2243 | 122.5204 | 122.6578 | 122.5479 | 122.6349
3952.0625 | 122.9187 | -122.6624 | 0.07782 | -0.0051118 | -0.0098843 | -0.079438 | -0.0089017 | -0.030016 | -0.052304 | -0.039751 | -0.0021057 | 0.00082679 | 0.0096302 | -0.0065026 | -0.21659 | -0.01941 | -0.027525 | -0.091553 | 0.10071 | -0.086975 | -0.091553 | 0.064087 | -0.091553 | -0.009155 | 0.045776 | 0.11444 | -0.086975 | 0.027466 | 0.13733 | 0.086975 | 0.12817 | 122.5754 | 0.022888 | -0.16937 | 122.7264 | 122.6532 | 122.5708 | 0.07782 | -0.004578 | 122.5754 | 0.036621 | -0.050354 | 122.7997 | 122.7905 | 122.7493 | 0.21515 | 0.17395 | 0.15106 | -0.004578 | 0.2243 | 0.11444 | 0.18768 | 0.20142 | 122.7631 | 122.7768 | -0.16479 | -0.16479 | 122.5708 | 122.6898 | 122.5708 | 122.7081
3953.7969 | 122.9187 | -122.6486 | 0.10071 | 0.0025177 | -0.011166 | -0.077942 | -0.0078335 | -0.030016 | -0.052731 | -0.042528 | 0.00094606 | 0.0018948 | 0.0066394 | -0.010775 | -0.21958 | -0.018342 | -0.023039 | -0.073242 | 0.073242 | -0.086975 | -0.036621 | 0.14191 | -0.068665 | 0.018311 | 0.10986 | 0.091553 | -0.07782 | 0.09613 | 0.16937 | 0.11444 | 0.14191 | 122.5616 | -0.027466 | -0.13733 | 122.7905 | 122.6669 | 122.58 | 0.10529 | 0.01831 | 122.5708 | -0.009155 | -0.004578 | 122.818 | 122.7905 | 122.7631 | 0.21973 | 0.19226 | 0.22888 | 0.050354 | 0.24719 | 0.17395 | 0.16022 | 0.16937 | 122.7219 | 122.7402 | -0.18768 | -0.17853 | 122.612 | 122.7448 | 122.5754 | 122.7585
3955.5781 | 122.9233 | -122.6532 | 0.07782 | 0.0025177 | -0.012234 | -0.079651 | -0.0074063 | -0.031084 | -0.04974 | -0.039751 | -0.0021057 | 0.0014676 | 0.0083484 | -0.014193 | -0.2215 | -0.019837 | -0.021117 | -0.068665 | 0.07782 | -0.10071 | -0.054932 | 0.12817 | -0.086975 | 0.013733 | 0.091553 | 0.10529 | -0.086975 | 0.064087 | 0.16022 | 0.091553 | 0.11902 | 122.5525 | 0 | -0.13275 | 122.7814 | 122.6669 | 122.5662 | 0.11444 | 0.013733 | 122.5662 | 0.027466 | -0.013733 | 122.8134 | 122.7722 | 122.7448 | 0.20599 | 0.17853 | 0.22888 | 0.045776 | 0.24719 | 0.15106 | 0.17853 | 0.19226 | 122.731 | 122.7585 | -0.17853 | -0.16479 | 122.5983 | 122.7173 | 122.5845 | 122.7448
3957.375 | 122.9187 | -122.6532 | 0.10986 | -0.0051118 | -0.01437 | -0.082215 | -0.0080471 | -0.027453 | -0.053158 | -0.040178 | -0.0051575 | 0.004672 | 0.007494 | -0.015048 | -0.22001 | -0.020264 | -0.02368 | -0.10986 | 0.07782 | -0.10071 | -0.10529 | 0.059509 | -0.09613 | 0.004578 | 0.036621 | 0.11444 | -0.10529 | 0.054932 | 0.15106 | 0.086975 | 0.11444 | 122.5525 | -0.032043 | -0.21515 | 122.7127 | 122.6578 | 122.5571 | 0.10529 | 0.004578 | 122.5479 | 0.004578 | -0.054931 | 122.8043 | 122.7676 | 122.7402 | 0.21973 | 0.19226 | 0.16022 | -0.004578 | 0.25635 | 0.16022 | 0.17853 | 0.21973 | 122.731 | 122.7676 | -0.21057 | -0.21515 | 122.5479 | 122.7081 | 122.5433 | 122.6898
3959.1094 | 122.9553 | -122.6532 | 0.10071 | 0.010147 | -0.015011 | -0.082428 | -0.0071927 | -0.031084 | -0.054653 | -0.039324 | -0.0021057 | 0.0021084 | 0.0072802 | -0.01932 | -0.22043 | -0.019837 | -0.024107 | -0.10529 | 0.082397 | -0.11902 | -0.068665 | 0.073242 | -0.073242 | 0.009155 | 0.054932 | 0.10986 | -0.086975 | 0.064087 | 0.16479 | 0.1236 | 0.13275 | 122.5342 | -0.018311 | -0.16937 | 122.7264 | 122.6624 | 122.58 | 0.12817 | 0.045777 | 122.5662 | 0.009155 | -0.036621 | 122.818 | 122.7859 | 122.7768 | 0.21973 | 0.21057 | 0.19226 | 0.050354 | 0.25177 | 0.15106 | 0.20142 | 0.19684 | 122.7356 | 122.7631 | -0.21973 | -0.18768 | 122.5845 | 122.7173 | 122.5479 | 122.7081
3960.9062 | 122.8271 | -122.6852 | 0.13275 | 0.0025177 | -0.011807 | -0.079011 | -0.0020657 | -0.028948 | -0.050808 | -0.040605 | -0.0021057 | 0.00574 | 0.0087756 | -0.0086388 | -0.22214 | -0.019196 | -0.025389 | -0.082397 | 0.10529 | -0.14191 | -0.1236 | 0.013733 | -0.15106 | -0.073242 | 0 | 0.14191 | -0.10986 | -0.022888 | 0.050354 | -0.022888 | 0.045776 | 122.5433 | -0.027465 | -0.25635 | 122.699 | 122.612 | 122.5342 | 0.068665 | -0.009155 | 122.5754 | 0.009156 | -0.15564 | 122.7356 | 122.731 | 122.6624 | 0.15564 | 0.086975 | 0.15564 | 0.018311 | 0.16022 | 0.086975 | 0.24719 | 0.25177 | 122.7905 | 122.8271 | -0.27466 | -0.24261 | 122.5616 | 122.6624 | 122.6028 | 122.6852
3962.7031 | 122.9782 | -122.6486 | 0.073242 | -0.0051118 | -0.010311 | -0.077302 | -0.0050565 | -0.026812 | -0.049526 | -0.039324 | -0.0021057 | 0.0027494 | 0.0083484 | -0.010561 | -0.21851 | -0.01706 | -0.022826 | -0.036621 | 0.07782 | -0.10529 | -0.027466 | 0.11902 | -0.07782 | 0.013733 | 0.11902 | 0.09613 | -0.07782 | 0.10986 | 0.19226 | 0.10529 | 0.16022 | 122.5433 | 0.004578 | -0.10071 | 122.7676 | 122.6624 | 122.5708 | 0.11902 | 0.027466 | 122.5708 | 0.022888 | 0.036621 | 122.8409 | 122.8088 | 122.7539 | 0.23804 | 0.18311 | 0.22431 | 0.07782 | 0.27008 | 0.18768 | 0.18311 | 0.17395 | 122.7264 | 122.7448 | -0.17853 | -0.15106 | 122.6212 | 122.7585 | 122.612 | 122.7676
3964.5 | 122.937 | -122.6761 | 0.09613 | -0.0051118 | -0.010952 | -0.078156 | -0.0061245 | -0.029589 | -0.052304 | -0.039965 | -0.0021057 | 0.0033902 | 0.0070666 | -0.013552 | -0.22086 | -0.017914 | -0.026671 | -0.045776 | 0.068665 | -0.082397 | -0.032043 | 0.13275 | -0.059509 | 0.027466 | 0.12817 | 0.091553 | -0.073242 | 0.09613 | 0.17395 | 0.10986 | 0.14648 | 122.5937 | -0.027465 | -0.12817 | 122.8088 | 122.7036 | 122.6166 | 0.10986 | 0.022888 | 122.6028 | -0.004577 | 0 | 122.85 | 122.8226 | 122.7859 | 0.21973 | 0.18311 | 0.21515 | 0.050354 | 0.24719 | 0.16937 | 0.15106 | 0.16479 | 122.7448 | 122.7676 | -0.17853 | -0.16937 | 122.644 | 122.7722 | 122.6303 | 122.8043
3966.3125 | 122.8409 | -122.6944 | 0.11444 | -0.012741 | -0.013729 | -0.079651 | -0.0074063 | -0.034075 | -0.054867 | -0.042528 | -0.0021057 | 0.0023222 | 0.0098438 | -0.017184 | -0.21851 | -0.020905 | -0.021971 | -0.10986 | 0.10529 | -0.12817 | -0.14191 | -0.004578 | -0.13733 | -0.064087 | -0.036621 | 0.15106 | -0.13275 | -0.045776 | 0.059509 | -0.004578 | 0.036621 | 122.5662 | -0.009155 | -0.25635 | 122.6898 | 122.6303 | 122.5571 | 0.064087 | -0.009155 | 122.5616 | 0.036621 | -0.16022 | 122.7539 | 122.731 | 122.6898 | 0.16937 | 0.12817 | 0.1236 | -0.013733 | 0.19226 | 0.086975 | 0.23346 | 0.28381 | 122.7997 | 122.8455 | -0.24262 | -0.24719 | 122.5525 | 122.6486 | 122.5845 | 122.6578
3968.0469 | 122.8409 | -122.7127 | 0.14191 | 0.0025177 | -0.014584 | -0.080719 | -0.0061245 | -0.030657 | -0.052731 | -0.040392 | -0.0021057 | 0.0033902 | 0.007494 | -0.0077844 | -0.21894 | -0.017914 | -0.02368 | -0.14191 | 0.11902 | -0.14648 | -0.16937 | -0.013733 | -0.15106 | -0.064087 | -0.054932 | 0.15106 | -0.1236 | -0.041199 | 0.054932 | -0.009155 | 0.045776 | 122.5662 | -0.022888 | -0.31128 | 122.699 | 122.6486 | 122.5616 | 0.082397 | -0.004578 | 122.5891 | 0.009155 | -0.18311 | 122.7676 | 122.7585 | 122.7036 | 0.16937 | 0.11444 | 0.13275 | -0.022889 | 0.17853 | 0.082397 | 0.2655 | 0.27466 | 122.8317 | 122.8638 | -0.28839 | -0.2655 | 122.5433 | 122.6715 | 122.5708 | 122.6578
3969.8438 | 122.8592 | -122.7264 | 0.13733 | 0.0025177 | -0.014157 | -0.082642 | -0.0078335 | -0.033648 | -0.051663 | -0.039324 | -0.0021057 | 0.0031766 | 0.006853 | -0.013339 | -0.21894 | -0.021119 | -0.024535 | -0.10071 | 0.09613 | -0.13275 | -0.12817 | 0.027466 | -0.11902 | -0.045776 | -0.032043 | 0.15564 | -0.11902 | -0.036621 | 0.059509 | -0.004578 | 0.036621 | 122.5937 | -0.041199 | -0.2655 | 122.7539 | 122.6807 | 122.6074 | 0.086975 | 0.013732 | 122.6074 | 0.018311 | -0.17395 | 122.7859 | 122.7631 | 122.7219 | 0.15564 | 0.11444 | 0.16022 | 0.004577 | 0.17853 | 0.082398 | 0.22888 | 0.27466 | 122.8226 | 122.8821 | -0.27008 | -0.25635 | 122.5983 | 122.6898 | 122.6257 | 122.6944
3971.6406 | 122.9691 | -122.6669 | 0.082397 | -0.012741 | -0.01138 | -0.077088 | -0.0067653 | -0.029375 | -0.050808 | -0.042742 | -0.0051575 | 0.001254 | 0.0079212 | -0.018893 | -0.21958 | -0.020478 | -0.023894 | -0.032043 | 0.07782 | -0.09613 | -0.018311 | 0.12817 | -0.068665 | 0.032043 | 0.12817 | 0.09613 | -0.082397 | 0.091553 | 0.1831 | 0.10071 | 0.15106 | 122.5708 | -0.004577 | -0.10071 | 122.7951 | 122.699 | 122.5983 | 0.12817 | 0.027465 | 122.5845 | 0.013733 | 0.009156 | 122.85 | 122.818 | 122.7676 | 0.23346 | 0.18311 | 0.2243 | 0.077819 | 0.2655 | 0.17395 | 0.17395 | 0.17853 | 122.7448 | 122.7631 | -0.17853 | -0.16479 | 122.6486 | 122.7585 | 122.6349 | 122.7951
3973.4375 | 122.9553 | -122.6944 | 0.09613 | -0.012741 | -0.015652 | -0.077729 | -0.0078335 | -0.031084 | -0.053158 | -0.038042 | -0.0021057 | 0.0014676 | 0.0089892 | -0.0073572 | -0.22065 | -0.018982 | -0.024107 | -0.068665 | 0.082397 | -0.12817 | -0.041199 | 0.14191 | -0.041199 | 0.032043 | 0.10071 | 0.10986 | -0.10986 | 0.068665 | 0.16479 | 0.11902 | 0.1236 | 122.5662 | -0.013733 | -0.13733 | 122.8363 | 122.7264 | 122.6532 | 0.16022 | 0.086975 | 122.5845 | 0.013733 | -0.027465 | 122.8592 | 122.818 | 122.8134 | 0.23346 | 0.22888 | 0.27008 | 0.086975 | 0.27466 | 0.17853 | 0.21057 | 0.21973 | 122.7768 | 122.8043 | -0.2243 | -0.20599 | 122.6532 | 122.7631 | 122.6257 | 122.7951
3975.2344 | 122.8592 | -122.699 | 0.10529 | -0.0051118 | -0.011593 | -0.078156 | -0.0033475 | -0.030871 | -0.048886 | -0.040819 | -0.0021057 | 0.0050992 | 0.0087756 | -0.012484 | -0.22001 | -0.016633 | -0.023467 | -0.082397 | 0.09613 | -0.13733 | -0.11444 | 0.022888 | -0.13733 | -0.068665 | 0.022888 | 0.12817 | -0.10986 | -0.004578 | 0.059509 | -0.009155 | 0.064087 | 122.5616 | -0.009156 | -0.21973 | 122.7219 | 122.6303 | 122.5616 | 0.068664 | 0 | 122.5891 | 0.022888 | -0.10986 | 122.7585 | 122.7631 | 122.6898 | 0.17395 | 0.10071 | 0.16022 | 0.022888 | 0.16937 | 0.10529 | 0.23346 | 0.23804 | 122.7951 | 122.8271 | -0.24262 | -0.21515 | 122.5845 | 122.6944 | 122.6166 | 122.7219
3976.9688 | 122.8958 | -122.6669 | 0.1236 | -0.0051118 | -0.011593 | -0.080292 | -0.0067653 | -0.030443 | -0.051663 | -0.038469 | -0.0021057 | 0.0059538 | 0.0089892 | -0.009707 | -0.22086 | -0.019837 | -0.021544 | -0.082397 | 0.10986 | -0.14191 | -0.10529 | 0.045776 | -0.11444 | -0.059509 | 0.054932 | 0.12817 | -0.11444 | 0.022888 | 0.10529 | 0.041199 | 0.09613 | 122.525 | -0.013733 | -0.22888 | 122.7127 | 122.6074 | 122.5525 | 0.082398 | 0.027466 | 122.5525 | 0.004578 | -0.10071 | 122.7722 | 122.7631 | 122.7081 | 0.21057 | 0.15564 | 0.18768 | 0.036621 | 0.21973 | 0.13733 | 0.25177 | 0.24262 | 122.7768 | 122.7951 | -0.2655 | -0.23804 | 122.5616 | 122.6898 | 122.5845 | 122.7219
3978.75 | 122.8592 | -122.7081 | 0.11444 | -0.0051118 | -0.012234 | -0.077302 | -0.0050565 | -0.030657 | -0.05209 | -0.038896 | 0.00094606 | 0.0048856 | 0.0092028 | -0.013339 | -0.21937 | -0.018555 | -0.021117 | -0.12817 | 0.10986 | -0.14648 | -0.17853 | -0.032043 | -0.18768 | -0.091553 | -0.050354 | 0.13275 | -0.11902 | -0.022888 | 0.041199 | -0.018311 | 0.059509 | 122.5616 | -0.004578 | -0.29297 | 122.6761 | 122.6166 | 122.5204 | 0.054931 | -0.041199 | 122.5891 | 0.01831 | -0.13733 | 122.7493 | 122.7676 | 122.6898 | 0.17853 | 0.10071 | 0.11444 | -0.032044 | 0.16022 | 0.096131 | 0.25635 | 0.25177 | 122.818 | 122.8409 | -0.26093 | -0.23346 | 122.5296 | 122.6852 | 122.58 | 122.6578
3980.5625 | 122.9965 | -122.6715 | 0.07782 | 0.010147 | -0.013729 | -0.080079 | -0.0086879 | -0.030657 | -0.050808 | -0.040392 | -0.0082091 | 0.00039959 | 0.005144 | -0.01462 | -0.21872 | -0.019837 | -0.022185 | -0.082397 | 0.091553 | -0.11902 | -0.041199 | 0.13275 | -0.018311 | 0.059509 | 0.13275 | 0.086975 | -0.086975 | 0.091553 | 0.20599 | 0.16022 | 0.15564 | 122.5525 | 0.013733 | -0.11902 | 122.8043 | 122.731 | 122.6532 | 0.17853 | 0.10071 | 122.5845 | 0.009155 | 0.013733 | 122.8775 | 122.8271 | 122.8317 | 0.24261 | 0.24719 | 0.25177 | 0.07782 | 0.29297 | 0.17853 | 0.21057 | 0.17395 | 122.7631 | 122.7585 | -0.19684 | -0.16479 | 122.6303 | 122.7631 | 122.5891 | 122.8043
3982.2812 | 122.8912 | -122.7127 | 0.10986 | 0.0025177 | -0.010739 | -0.081574 | -0.0076199 | -0.031298 | -0.051235 | -0.039537 | -0.0082091 | 0.0031766 | 0.007494 | -0.0071436 | -0.22193 | -0.019196 | -0.022612 | -0.10986 | 0.14648 | -0.1236 | -0.14191 | 0 | -0.1236 | -0.064087 | -0.009155 | 0.13275 | -0.11444 | 0.013733 | 0.10071 | 0.036621 | 0.09613 | 122.5891 | 0.036621 | -0.25177 | 122.7127 | 122.6486 | 122.5891 | 0.059509 | 0 | 122.5983 | 0.022888 | -0.09613 | 122.8134 | 122.8088 | 122.7493 | 0.21057 | 0.15106 | 0.1236 | -0.018311 | 0.21515 | 0.12817 | 0.27008 | 0.24719 | 122.8592 | 122.8455 | -0.23346 | -0.2243 | 122.5708 | 122.7264 | 122.6028 | 122.7036
3984.0781 | 122.9782 | -122.6349 | 0.086975 | -0.0051118 | -0.011593 | -0.080079 | -0.0052701 | -0.028521 | -0.050808 | -0.041246 | -0.0021057 | 0.001254 | 0.0070666 | -0.021884 | -0.22001 | -0.018342 | -0.024535 | -0.068665 | 0.086975 | -0.10986 | -0.073242 | 0.09613 | -0.073242 | 0.004578 | 0.09613 | 0.10071 | -0.10529 | 0.09613 | 0.16479 | 0.10986 | 0.16479 | 122.525 | 0 | -0.16022 | 122.731 | 122.6395 | 122.5616 | 0.11444 | 0.036621 | 122.5296 | 0.013733 | 0.009155 | 122.7997 | 122.7997 | 122.7448 | 0.27008 | 0.21515 | 0.20599 | 0.036621 | 0.27008 | 0.20142 | 0.19684 | 0.20599 | 122.7219 | 122.7356 | -0.19684 | -0.19226 | 122.5616 | 122.731 | 122.5662 | 122.731
3985.875 | 122.9874 | -122.6669 | 0.086975 | 0.0025177 | -0.015866 | -0.080079 | -0.0097561 | -0.031725 | -0.050595 | -0.04381 | -0.0021057 | 0.0027494 | 0.0059986 | -0.013766 | -0.21894 | -0.017914 | -0.02368 | -0.10071 | 0.082397 | -0.1236 | -0.086975 | 0.086975 | -0.073242 | 0.022888 | 0.07782 | 0.10071 | -0.10071 | 0.068665 | 0.17853 | 0.11902 | 0.15106 | 122.5433 | -0.004578 | -0.17395 | 122.7539 | 122.6898 | 122.5937 | 0.14648 | 0.050354 | 122.5662 | 0.013733 | -0.01831 | 122.8455 | 122.818 | 122.7859 | 0.25177 | 0.21973 | 0.21057 | 0.036621 | 0.27924 | 0.16937 | 0.20599 | 0.20142 | 122.7493 | 122.7676 | -0.21057 | -0.18768 | 122.58 | 122.7356 | 122.5662 | 122.7448
3987.6719 | 122.9782 | -122.6807 | 0.091553 | -0.0051118 | -0.016507 | -0.079438 | -0.0082607 | -0.03023 | -0.050167 | -0.039537 | -0.0021057 | 0.0016812 | 0.0081348 | -0.018252 | -0.22022 | -0.019837 | -0.021971 | -0.064087 | 0.07782 | -0.10529 | -0.032043 | 0.15564 | -0.013733 | 0.045776 | 0.13275 | 0.09613 | -0.07782 | 0.068665 | 0.20599 | 0.13733 | 0.14191 | 122.5754 | -0.013733 | -0.1236 | 122.8363 | 122.7264 | 122.6669 | 0.15106 | 0.091553 | 122.6028 | 0.004577 | -0.022888 | 122.8867 | 122.8226 | 122.818 | 0.21973 | 0.21515 | 0.26093 | 0.073243 | 0.28381 | 0.14649 | 0.18311 | 0.17395 | 122.7585 | 122.7768 | -0.19684 | -0.16937 | 122.6486 | 122.7493 | 122.6166 | 122.8134
3989.4688 | 122.8638 | -122.7219 | 0.10529 | 0.0025177 | -0.010739 | -0.077088 | -0.0018521 | -0.023821 | -0.051449 | -0.042314 | -0.0051575 | 0.0023222 | 0.0083484 | -0.012698 | -0.2215 | -0.01941 | -0.020262 | -0.11444 | 0.11902 | -0.14191 | -0.16022 | -0.045776 | -0.19684 | -0.10529 | -0.036621 | 0.15106 | -0.11444 | -0.041199 | 0.032043 | -0.036621 | 0.054932 | 122.58 | 0.013733 | -0.2655 | 122.6761 | 122.6166 | 122.525 | 0.036621 | -0.054931 | 122.6074 | 0.045776 | -0.14649 | 122.7539 | 122.7768 | 122.6852 | 0.16937 | 0.07782 | 0.096131 | -0.01831 | 0.14648 | 0.073242 | 0.26093 | 0.2655 | 122.8409 | 122.8729 | -0.24719 | -0.21973 | 122.5616 | 122.6807 | 122.6074 | 122.6852
3991.2656 | 122.9645 | -122.6852 | 0.091553 | -0.0051118 | -0.010952 | -0.077942 | -0.0095425 | -0.029162 | -0.051235 | -0.041033 | -0.0021057 | 0.00061319 | 0.005144 | -0.015688 | -0.22022 | -0.020264 | -0.023039 | -0.11444 | 0.09613 | -0.10071 | -0.10071 | 0.045776 | -0.10071 | -0.009155 | 0.027466 | 0.11902 | -0.09613 | 0.036621 | 0.15106 | 0.086975 | 0.11902 | 122.5845 | 0.004577 | -0.19226 | 122.731 | 122.6761 | 122.5845 | 0.091553 | 0 | 122.5891 | 0.027466 | -0.054932 | 122.8363 | 122.8043 | 122.7722 | 0.21515 | 0.1831 | 0.14648 | 0 | 0.24719 | 0.13275 | 0.19684 | 0.21515 | 122.7814 | 122.8043 | -0.19226 | -0.18768 | 122.5845 | 122.7219 | 122.5708 | 122.7127
3993.0156 | 122.9507 | -122.7173 | 0.10071 | -0.0051118 | -0.015225 | -0.079865 | -0.0078335 | -0.030443 | -0.051876 | -0.042528 | -0.0021057 | 0.0025358 | 0.0072802 | -0.010561 | -0.22043 | -0.019196 | -0.02368 | -0.09613 | 0.064087 | -0.11902 | -0.09613 | 0.054932 | -0.10986 | -0.009155 | 0.004578 | 0.11902 | -0.10071 | 0.022888 | 0.11902 | 0.050354 | 0.11444 | 122.5983 | -0.036621 | -0.19684 | 122.7722 | 122.7081 | 122.6074 | 0.10986 | 0.009156 | 122.6166 | 0.018311 | -0.07782 | 122.8363 | 122.8317 | 122.7676 | 0.21515 | 0.15106 | 0.17395 | 0.022889 | 0.21973 | 0.1236 | 0.18311 | 0.21973 | 122.7814 | 122.8363 | -0.21973 | -0.20142 | 122.6212 | 122.7402 | 122.6212 | 122.7219
3994.8125 | 122.8821 | -122.7127 | 0.11444 | 0.0025177 | -0.0098843 | -0.080933 | -0.0050565 | -0.03258 | -0.049954 | -0.042314 | 0.0039979 | 0.0050992 | 0.0070666 | -0.0077844 | -0.22107 | -0.018769 | -0.021758 | -0.082397 | 0.11444 | -0.14191 | -0.11444 | 0.045776 | -0.12817 | -0.064087 | 0.022888 | 0.15106 | -0.10529 | 0.004578 | 0.073242 | 0 | 0.073242 | 122.5708 | 0 | -0.22888 | 122.7585 | 122.6486 | 122.5845 | 0.07782 | 0.013733 | 122.6074 | 0.036621 | -0.10986 | 122.7859 | 122.7859 | 122.7127 | 0.17853 | 0.10529 | 0.18768 | 0.027466 | 0.17853 | 0.10986 | 0.25635 | 0.25635 | 122.8271 | 122.8638 | -0.25635 | -0.21973 | 122.5983 | 122.7173 | 122.6303 | 122.7356
3996.5625 | 122.8455 | -122.7493 | 0.10986 | -0.0051118 | -0.010098 | -0.076874 | -0.0044155 | -0.027239 | -0.052304 | -0.042528 | -0.0021057 | 0.004672 | 0.008562 | -0.013766 | -0.21894 | -0.019196 | -0.024535 | -0.11902 | 0.13275 | -0.12817 | -0.15564 | -0.041199 | -0.21515 | -0.11444 | -0.068665 | 0.13275 | -0.1236 | -0.032043 | 0.022888 | -0.045776 | 0.050354 | 122.6212 | 0.022888 | -0.2655 | 122.7081 | 122.6349 | 122.5342 | 0.013733 | -0.086975 | 122.6257 | 0.022888 | -0.14191 | 122.7722 | 122.7997 | 122.7036 | 0.17395 | 0.07782 | 0.086975 | -0.027466 | 0.14648 | 0.091553 | 0.26093 | 0.25635 | 122.8821 | 122.8821 | -0.23804 | -0.23346 | 122.5937 | 122.7173 | 122.6303 | 122.6807
3998.3438 | 122.8821 | -122.7448 | 0.11902 | 0.0025177 | -0.014157 | -0.079438 | -0.0078335 | -0.034289 | -0.052731 | -0.03911 | -0.0021057 | 0.0016812 | 0.008562 | -0.009707 | -0.21915 | -0.01941 | -0.024962 | -0.086975 | 0.10986 | -0.12817 | -0.10986 | 0.059509 | -0.09613 | -0.041199 | -0.004578 | 0.13275 | -0.10986 | -0.027466 | 0.068665 | 0 | 0.045776 | 122.6166 | -0.009156 | -0.22888 | 122.8043 | 122.7036 | 122.6486 | 0.086975 | 0.032044 | 122.6349 | 0.013732 | -0.14649 | 122.8134 | 122.7905 | 122.7448 | 0.15564 | 0.10986 | 0.18768 | 0.018311 | 0.17853 | 0.082397 | 0.23804 | 0.24261 | 122.8546 | 122.8775 | -0.24719 | -0.22888 | 122.6349 | 122.7173 | 122.6578 | 122.7402
4000.125 | 122.9691 | -122.7036 | 0.09613 | 0.0025177 | -0.014584 | -0.080506 | -0.0071927 | -0.033648 | -0.050808 | -0.042742 | -0.0082091 | 0.0023222 | 0.008562 | -0.021029 | -0.21851 | -0.019196 | -0.021971 | -0.10071 | 0.073242 | -0.11902 | -0.086975 | 0.068665 | -0.091553 | 0.004578 | 0.022888 | 0.10529 | -0.091553 | 0.022888 | 0.14648 | 0.10071 | 0.11444 | 122.5845 | -0.022888 | -0.1831 | 122.7722 | 122.7081 | 122.612 | 0.1236 | 0.027466 | 122.612 | 0.009156 | -0.073242 | 122.85 | 122.818 | 122.8043 | 0.20599 | 0.19226 | 0.18768 | 0.032044 | 0.23804 | 0.11444 | 0.19226 | 0.19684 | 122.7768 | 122.8088 | -0.21515 | -0.18768 | 122.6166 | 122.7264 | 122.6028 | 122.7264
4001.8594 | 122.905 | -122.7173 | 0.13275 | -0.0051118 | -0.013943 | -0.079651 | -0.0050565 | -0.028948 | -0.049313 | -0.04146 | 0.00094606 | 0.0055264 | 0.0070666 | -0.012484 | -0.21979 | -0.019837 | -0.026244 | -0.11444 | 0.1236 | -0.14648 | -0.15564 | -0.013733 | -0.15106 | -0.068665 | -0.041199 | 0.14191 | -0.13275 | -0.027466 | 0.07782 | 0.013733 | 0.073242 | 122.5708 | -0.009155 | -0.28839 | 122.7036 | 122.6486 | 122.5662 | 0.077819 | -0.004578 | 122.5845 | 0.009156 | -0.16022 | 122.7951 | 122.7905 | 122.731 | 0.20599 | 0.14648 | 0.13275 | -0.009156 | 0.21057 | 0.10529 | 0.27008 | 0.27466 | 122.8409 | 122.8592 | -0.27924 | -0.2655 | 122.5616 | 122.6898 | 122.6028 | 122.6761
4003.6406 | 122.9874 | -122.6852 | 0.086975 | -0.02037 | -0.0098843 | -0.075593 | -0.0080471 | -0.028307 | -0.046536 | -0.039537 | 0.00094606 | 0.00082679 | 0.0077076 | -0.015261 | -0.21894 | -0.020051 | -0.020476 | -0.050354 | 0.082397 | -0.10529 | -0.027466 | 0.12817 | -0.068665 | 0.022888 | 0.10986 | 0.10986 | -0.07782 | 0.082397 | 0.17853 | 0.10529 | 0.15106 | 122.58 | -0.004578 | -0.11444 | 122.8134 | 122.7081 | 122.6166 | 0.12817 | 0.036621 | 122.6074 | 0.022888 | -0.004578 | 122.8638 | 122.8363 | 122.7905 | 0.22888 | 0.18311 | 0.23346 | 0.07782 | 0.25635 | 0.16022 | 0.18768 | 0.18768 | 122.7676 | 122.7951 | -0.19226 | -0.16479 | 122.6578 | 122.7676 | 122.6349 | 122.7951
4005.4375 | 122.9462 | -122.7127 | 0.11444 | 0.017777 | -0.012661 | -0.077729 | -0.0076199 | -0.028734 | -0.053158 | -0.042742 | -0.0021057 | 0.0018948 | 0.0059986 | -0.018038 | -0.21851 | -0.020478 | -0.023039 | -0.11902 | 0.086975 | -0.10986 | -0.10529 | 0.054932 | -0.10071 | -0.013733 | 0.022888 | 0.11902 | -0.091553 | 0.022888 | 0.12817 | 0.082397 | 0.10986 | 122.6028 | -0.027466 | -0.21973 | 122.7676 | 122.699 | 122.612 | 0.09613 | 0.009155 | 122.6212 | 0.004578 | -0.091553 | 122.8409 | 122.8226 | 122.7951 | 0.20142 | 0.17395 | 0.16479 | 0.004577 | 0.21973 | 0.11444 | 0.19684 | 0.21057 | 122.7997 | 122.8317 | -0.2243 | -0.20599 | 122.6074 | 122.7356 | 122.5937 | 122.7356
4007.2344 | 122.9141 | -122.7219 | 0.13275 | 0.010147 | -0.01202 | -0.078797 | -0.0054837 | -0.026171 | -0.051022 | -0.040605 | -0.0021057 | 0.0038174 | 0.0064258 | -0.013125 | -0.22065 | -0.017914 | -0.02603 | -0.11444 | 0.11902 | -0.13733 | -0.1236 | 0 | -0.11902 | -0.064087 | -0.013733 | 0.14648 | -0.1236 | 0.004578 | 0.10071 | 0.045776 | 0.073242 | 122.5845 | -0.013732 | -0.25635 | 122.7219 | 122.6578 | 122.6028 | 0.073242 | 0.01831 | 122.5983 | 0.013733 | -0.12817 | 122.8226 | 122.7951 | 122.7676 | 0.19684 | 0.16937 | 0.13733 | 0.013733 | 0.2243 | 0.12817 | 0.25635 | 0.27008 | 122.8409 | 122.8683 | -0.27008 | -0.25635 | 122.5983 | 122.7264 | 122.6074 | 122.7081
4008.9688 | 122.9416 | -122.7081 | 0.11902 | -0.0051118 | -0.014798 | -0.078797 | -0.0086879 | -0.031725 | -0.054653 | -0.042742 | -0.0021057 | 0.001254 | 0.0081348 | -0.0092798 | -0.21958 | -0.020051 | -0.02133 | -0.059509 | 0.082397 | -0.11444 | -0.068665 | 0.10529 | -0.041199 | 0.018311 | 0.064087 | 0.11902 | -0.09613 | 0.018311 | 0.11902 | 0.07782 | 0.09613 | 122.5937 | -0.036622 | -0.18768 | 122.8134 | 122.7264 | 122.6669 | 0.13275 | 0.073242 | 122.612 | 0 | -0.10071 | 122.8271 | 122.8043 | 122.7859 | 0.19226 | 0.17395 | 0.21973 | 0.045776 | 0.21515 | 0.11444 | 0.19684 | 0.21515 | 122.7905 | 122.8271 | -0.23346 | -0.21515 | 122.6395 | 122.7264 | 122.6486 | 122.7722
4010.7656 | 122.8912 | -122.7219 | 0.11902 | 0.0025177 | -0.010525 | -0.080506 | -0.0039883 | -0.031298 | -0.04974 | -0.044023 | -0.0021057 | 0.0031766 | 0.0077076 | -0.01227 | -0.21979 | -0.018128 | -0.023894 | -0.082397 | 0.1236 | -0.12817 | -0.10529 | 0.041199 | -0.11902 | -0.059509 | 0.032043 | 0.11902 | -0.10529 | 0 | 0.082397 | 0.004578 | 0.07782 | 122.5937 | 0.004577 | -0.22431 | 122.7631 | 122.6624 | 122.6028 | 0.068665 | 0.009155 | 122.6166 | 0 | -0.11902 | 122.8043 | 122.7997 | 122.7264 | 0.18311 | 0.10986 | 0.16937 | 0.022888 | 0.18768 | 0.10529 | 0.25177 | 0.22431 | 122.8455 | 122.8409 | -0.24719 | -0.22431 | 122.6166 | 122.7219 | 122.6395 | 122.7539
4012.5781 | 122.9782 | -122.7402 | 0.10529 | -0.0051118 | -0.012448 | -0.079651 | -0.0086879 | -0.03322 | -0.050381 | -0.042314 | -0.0021057 | 0.00082679 | 0.0092028 | -0.015261 | -0.21808 | -0.018555 | -0.021544 | -0.11444 | 0.086975 | -0.12817 | -0.10071 | 0.059509 | -0.10529 | -0.004578 | 0.022888 | 0.10071 | -0.10529 | 0.041199 | 0.14648 | 0.09613 | 0.11902 | 122.612 | -0.018311 | -0.20599 | 122.7997 | 122.7356 | 122.6349 | 0.1236 | 0.022888 | 122.6349 | -0.004578 | -0.064087 | 122.8867 | 122.8592 | 122.8363 | 0.22431 | 0.20142 | 0.18768 | 0.027466 | 0.25177 | 0.14649 | 0.21515 | 0.20599 | 122.8271 | 122.8409 | -0.23346 | -0.21057 | 122.6395 | 122.7814 | 122.6257 | 122.7631
4014.3125 | 122.8867 | -122.7539 | 0.13275 | 0.0025177 | -0.013516 | -0.080719 | -0.0076199 | -0.030016 | -0.051449 | -0.039965 | -0.0051575 | 0.0036038 | 0.0070666 | -0.0075708 | -0.22043 | -0.021973 | -0.023253 | -0.13733 | 0.14648 | -0.15564 | -0.16937 | -0.013733 | -0.14648 | -0.091553 | -0.068665 | 0.14191 | -0.1236 | -0.036621 | 0.054932 | 0.004578 | 0.036621 | 122.5983 | 0.013733 | -0.30212 | 122.7402 | 122.6624 | 122.6074 | 0.064087 | 0.009156 | 122.6303 | 0.009156 | -0.16937 | 122.8088 | 122.7905 | 122.7585 | 0.16022 | 0.12817 | 0.14191 | -0.013733 | 0.17853 | 0.086975 | 0.30212 | 0.2655 | 122.9004 | 122.8958 | -0.28839 | -0.25635 | 122.5845 | 122.7173 | 122.6166 | 122.6852
4016.1094 | 122.9233 | -122.7402 | 0.11444 | 0.0025177 | -0.010739 | -0.079011 | -0.0052701 | -0.029162 | -0.05209 | -0.043169 | -0.0021057 | 0.002963 | 0.0089892 | -0.010561 | -0.21979 | -0.018769 | -0.022398 | -0.07782 | 0.11444 | -0.12817 | -0.10071 | 0.045776 | -0.10986 | -0.054932 | 0.027466 | 0.11902 | -0.10986 | 0.009155 | 0.091553 | 0.013733 | 0.073242 | 122.612 | 0 | -0.21515 | 122.7859 | 122.6852 | 122.6303 | 0.073242 | 0.018311 | 122.6303 | 0.004578 | -0.10529 | 122.8317 | 122.8134 | 122.7539 | 0.18311 | 0.1236 | 0.17395 | 0.027466 | 0.20142 | 0.11902 | 0.24262 | 0.22888 | 122.8546 | 122.8592 | -0.24262 | -0.2243 | 122.6395 | 122.7493 | 122.6624 | 122.7676
4017.9062 | 122.8775 | -122.7493 | 0.12817 | -0.0051118 | -0.01437 | -0.080506 | -0.0076199 | -0.028948 | -0.052944 | -0.039965 | -0.0021057 | 0.0018948 | 0.0072802 | -0.017184 | -0.21787 | -0.020478 | -0.024321 | -0.1236 | 0.11902 | -0.14191 | -0.16022 | 0.004578 | -0.14191 | -0.07782 | -0.032043 | 0.13733 | -0.11902 | -0.054932 | 0.054932 | 0 | 0.032043 | 122.6074 | -0.009155 | -0.28839 | 122.7539 | 122.6715 | 122.6074 | 0.064087 | 0 | 122.6303 | 0.009155 | -0.18311 | 122.8043 | 122.7814 | 122.7493 | 0.15106 | 0.11902 | 0.14649 | -0.01831 | 0.17395 | 0.064087 | 0.26093 | 0.25635 | 122.8683 | 122.8867 | -0.27008 | -0.24719 | 122.5891 | 122.6944 | 122.6257 | 122.7173
4019.6875 | 122.905 | -122.7539 | 0.13275 | 0.010147 | -0.013089 | -0.081147 | -0.0069791 | -0.034075 | -0.051663 | -0.042314 | -0.0021057 | 0.0025358 | 0.0077076 | -0.017397 | -0.21937 | -0.020691 | -0.025176 | -0.10986 | 0.086975 | -0.11444 | -0.16022 | 0 | -0.13733 | -0.059509 | -0.027466 | 0.15106 | -0.11444 | -0.054932 | 0.059509 | 0.009155 | 0.032043 | 122.6395 | -0.045776 | -0.29297 | 122.7539 | 122.6944 | 122.6166 | 0.054932 | -0.022888 | 122.6395 | 0.018311 | -0.18768 | 122.8134 | 122.7859 | 122.7631 | 0.14648 | 0.1236 | 0.11444 | -0.045776 | 0.17395 | 0.059509 | 0.20142 | 0.2655 | 122.8409 | 122.905 | -0.24719 | -0.24719 | 122.5937 | 122.699 | 122.644 | 122.7264
4021.4219 | 122.9828 | -122.7081 | 0.10986 | -0.0051118 | -0.01437 | -0.079865 | -0.0089017 | -0.028948 | -0.050595 | -0.040605 | 0.00094606 | 0.0010404 | 0.0079212 | -0.019534 | -0.22043 | -0.021332 | -0.021758 | -0.10071 | 0.082397 | -0.11444 | -0.10529 | 0.064087 | -0.10529 | -0.013733 | 0.022888 | 0.11444 | -0.10986 | 0.022888 | 0.13275 | 0.068665 | 0.10529 | 122.5937 | -0.027466 | -0.21515 | 122.7722 | 122.6944 | 122.6028 | 0.10071 | 0.009155 | 122.5983 | 0.004578 | -0.086975 | 122.8409 | 122.8134 | 122.7768 | 0.21515 | 0.17853 | 0.17853 | 0.009155 | 0.24261 | 0.13275 | 0.19684 | 0.2243 | 122.7905 | 122.8226 | -0.2243 | -0.21973 | 122.6028 | 122.731 | 122.6074 | 122.731
4023.2344 | 123.0331 | -122.7036 | 0.091553 | 0.010147 | -0.013089 | -0.079224 | -0.0078335 | -0.030443 | -0.050167 | -0.042314 | 0.00094606 | 0.0036038 | 0.0070666 | -0.018679 | -0.22065 | -0.020264 | -0.024107 | -0.059509 | 0.07782 | -0.091553 | -0.013733 | 0.19684 | -0.009155 | 0.068665 | 0.12817 | 0.091553 | -0.07782 | 0.086975 | 0.21057 | 0.12817 | 0.13733 | 122.612 | -0.013733 | -0.10529 | 122.9004 | 122.7722 | 122.6944 | 0.16022 | 0.082398 | 122.6257 | 0 | -0.004578 | 122.9141 | 122.8409 | 122.8317 | 0.21515 | 0.20599 | 0.28839 | 0.07782 | 0.28839 | 0.16479 | 0.16937 | 0.16937 | 122.7814 | 122.7951 | -0.18311 | -0.16937 | 122.6898 | 122.7905 | 122.644 | 122.8317
4025.0156 | 123.0011 | -122.731 | 0.09613 | -0.0051118 | -0.013516 | -0.078583 | -0.0097561 | -0.032152 | -0.050381 | -0.041033 | -0.0021057 | 0.0016812 | 0.006853 | -0.014193 | -0.2215 | -0.018769 | -0.022398 | -0.050354 | 0.073242 | -0.10986 | -0.032043 | 0.14191 | -0.027466 | 0.032043 | 0.10529 | 0.10529 | -0.07782 | 0.059509 | 0.19226 | 0.12817 | 0.13275 | 122.6212 | -0.022888 | -0.12817 | 122.8729 | 122.7631 | 122.7036 | 0.14191 | 0.082397 | 122.6532 | 0.009156 | -0.036621 | 122.9233 | 122.8638 | 122.8592 | 0.21057 | 0.20599 | 0.25177 | 0.07782 | 0.27008 | 0.13733 | 0.18311 | 0.18311 | 122.8043 | 122.8363 | -0.20599 | -0.17395 | 122.699 | 122.7905 | 122.6807 | 122.8363
4026.75 | 122.9828 | -122.7036 | 0.07782 | 0.0025177 | -0.01138 | -0.078797 | -0.0042019 | -0.028307 | -0.04974 | -0.042528 | 0.00094606 | 0.0010404 | 0.0096302 | -0.014407 | -0.22065 | -0.021332 | -0.023253 | -0.064087 | 0.07782 | -0.091553 | -0.050354 | 0.10986 | -0.07782 | 0.013733 | 0.09613 | 0.09613 | -0.091553 | 0.050354 | 0.14648 | 0.082397 | 0.11444 | 122.612 | 0 | -0.12817 | 122.8134 | 122.7173 | 122.6257 | 0.10529 | 0.013733 | 122.612 | 0.01831 | -0.027466 | 122.85 | 122.818 | 122.7859 | 0.20599 | 0.17395 | 0.20142 | 0.041199 | 0.23804 | 0.14191 | 0.16937 | 0.18768 | 122.7814 | 122.7997 | -0.16937 | -0.16937 | 122.6532 | 122.7539 | 122.6395 | 122.7997
4028.5469 | 122.9965 | -122.7127 | 0.091553 | 0.010147 | -0.0096707 | -0.078583 | -0.0042019 | -0.029375 | -0.050595 | -0.040819 | 0.0039979 | 0.0053128 | 0.008562 | -0.011416 | -0.22022 | -0.018342 | -0.024962 | -0.10071 | 0.11444 | -0.1236 | -0.10986 | 0.036621 | -0.15564 | -0.045776 | 0.045776 | 0.10529 | -0.10071 | 0.068665 | 0.14191 | 0.073242 | 0.14648 | 122.5891 | 0.022888 | -0.20142 | 122.7493 | 122.6669 | 122.5571 | 0.07782 | -0.032044 | 122.612 | 0.013733 | -0.022888 | 122.8546 | 122.8592 | 122.7859 | 0.24719 | 0.17395 | 0.16022 | 0.013733 | 0.24262 | 0.16937 | 0.23804 | 0.20599 | 122.8271 | 122.818 | -0.21515 | -0.19226 | 122.6028 | 122.7814 | 122.612 | 122.7585
4030.3438 | 123.0194 | -122.6715 | 0.086975 | -0.012741 | -0.0064663 | -0.019196 | -0.0084743 | -0.030443 | -0.051022 | -0.039965 | -0.0021057 | 0.0021084 | 0.0083484 | -0.016757 | -0.22086 | -0.020264 | -0.022398 | -0.050354 | 0.050354 | -0.12817 | -0.041199 | 0.11444 | -0.091553 | -0.004578 | 0.13733 | 0.09613 | -0.07782 | 0.10071 | 0.17853 | 0.09613 | 0.15106 | 122.5433 | -0.036621 | -0.12817 | 122.7859 | 122.6669 | 122.58 | 0.1236 | 0.036621 | 122.5937 | 0.009155 | 0.013733 | 122.85 | 122.8226 | 122.7676 | 0.22888 | 0.17395 | 0.24262 | 0.086975 | 0.25635 | 0.17853 | 0.17853 | 0.17395 | 122.7219 | 122.7676 | -0.21515 | -0.16479 | 122.6303 | 122.7722 | 122.6212 | 122.8088
4032.1406 | 122.8958 | -122.7448 | 0.10986 | -0.0051118 | -0.0094571 | -0.079011 | -0.0035611 | -0.030871 | -0.04974 | -0.04146 | 0.00094606 | 0.0042448 | 0.0062122 | -0.013339 | -0.22043 | -0.020051 | -0.024962 | -0.086975 | 0.11444 | -0.13275 | -0.12817 | 0.018311 | -0.15106 | -0.10071 | -0.022888 | 0.13275 | -0.11444 | -0.032043 | 0.027466 | -0.027466 | 0.041199 | 122.612 | 0.004578 | -0.23804 | 122.7631 | 122.644 | 122.5937 | 0.032043 | -0.018311 | 122.6303 | 0.022888 | -0.14191 | 122.7722 | 122.7859 | 122.7173 | 0.15564 | 0.086975 | 0.15106 | 0.004577 | 0.14191 | 0.082398 | 0.24719 | 0.24719 | 122.8592 | 122.8775 | -0.24261 | -0.2243 | 122.6166 | 122.7127 | 122.6578 | 122.7219
4033.8594 | 122.9691 | -122.7264 | 0.07782 | -0.0051118 | -0.015011 | -0.079011 | -0.0069791 | -0.030443 | -0.049954 | -0.041674 | -0.0021057 | 0.00082679 | 0.0059986 | -0.017611 | -0.21958 | -0.0224 | -0.023253 | -0.086975 | 0.082397 | -0.11444 | -0.082397 | 0.10071 | -0.091553 | -0.004578 | 0.059509 | 0.10071 | -0.10071 | 0.050354 | 0.12817 | 0.064087 | 0.11444 | 122.612 | 0.004577 | -0.16022 | 122.8271 | 122.7219 | 122.6349 | 0.10986 | 0.022888 | 122.6257 | 0.022888 | -0.027466 | 122.8546 | 122.8409 | 122.7905 | 0.21515 | 0.1648 | 0.21515 | 0.032044 | 0.22888 | 0.15106 | 0.19684 | 0.20142 | 122.8088 | 122.8271 | -0.19226 | -0.17853 | 122.644 | 122.7768 | 122.6395 | 122.7859
4035.6562 | 122.9416 | -122.7402 | 0.13733 | -0.012741 | -0.01138 | -0.079865 | -0.0061245 | -0.030871 | -0.051876 | -0.041887 | 0.00094606 | 0.011294 | 0.069017 | -0.013125 | -0.21851 | -0.018555 | -0.021971 | -0.064087 | 0.09613 | -0.13733 | -0.10986 | 0.054932 | -0.1236 | -0.050354 | 0.027466 | 0.10071 | -0.14648 | -0.004578 | 0.082397 | 0.018311 | 0.068665 | 122.6028 | -0.041199 | -0.24719 | 122.7951 | 122.6898 | 122.6166 | 0.086975 | 0.013733 | 122.5937 | -0.036621 | -0.14191 | 122.8226 | 122.8088 | 122.7585 | 0.21515 | 0.16479 | 0.19226 | 0.027466 | 0.22888 | 0.14191 | 0.23346 | 0.24719 | 122.8363 | 122.8409 | -0.27466 | -0.28381 | 122.6303 | 122.7356 | 122.6761 | 122.7676
4037.4531 | 122.9919 | -122.7081 | 0.091553 | 0.0025177 | -0.015866 | -0.08136 | -0.0097561 | -0.028948 | -0.051449 | -0.040178 | 0.00094606 | 0.0014676 | 0.0066394 | -0.0088526 | -0.21851 | -0.021119 | -0.019835 | -0.059509 | 0.07782 | -0.10986 | -0.027466 | 0.11444 | -0.027466 | 0.027466 | 0.086975 | 0.10529 | -0.086975 | 0.059509 | 0.16937 | 0.10529 | 0.11444 | 122.5983 | -0.013733 | -0.11902 | 122.8226 | 122.7356 | 122.6807 | 0.13733 | 0.082397 | 122.6212 | 0.013733 | -0.032044 | 122.8775 | 122.8226 | 122.8134 | 0.20142 | 0.19226 | 0.2243 | 0.082397 | 0.25635 | 0.14648 | 0.18768 | 0.19226 | 122.7859 | 122.8134 | -0.20142 | -0.17853 | 122.6807 | 122.7676 | 122.6486 | 122.7951
4039.25 | 123.0194 | -122.7173 | 0.09613 | -0.0051118 | -0.015011 | -0.07837 | -0.0089017 | -0.028948 | -0.050167 | -0.042528 | -0.0021057 | 0.0018948 | 0.0083484 | -0.01227 | -0.21979 | -0.021119 | -0.02603 | -0.054932 | 0.086975 | -0.10529 | -0.022888 | 0.13733 | -0.013733 | 0.027466 | 0.10986 | 0.091553 | -0.091553 | 0.07782 | 0.18768 | 0.13733 | 0.14191 | 122.612 | -0.009155 | -0.11902 | 122.8546 | 122.7448 | 122.7036 | 0.13275 | 0.091553 | 122.6257 | -0.004577 | -0.01831 | 122.905 | 122.8592 | 122.8546 | 0.23346 | 0.22888 | 0.24262 | 0.082398 | 0.27924 | 0.16937 | 0.19226 | 0.18311 | 122.8043 | 122.8088 | -0.20142 | -0.18768 | 122.6944 | 122.7951 | 122.6624 | 122.8271
4041.0312 | 122.9095 | -122.7402 | 0.14191 | -0.0051118 | -0.013943 | -0.079438 | -0.0056973 | -0.03792 | -0.051235 | -0.042314 | -0.0051575 | 0.001254 | 0.0087756 | -0.020388 | -0.22086 | -0.018769 | -0.022398 | -0.13733 | 0.13733 | -0.15106 | -0.17395 | -0.009155 | -0.14648 | -0.07782 | -0.054932 | 0.15564 | -0.13275 | -0.059509 | 0.050354 | -0.022888 | 0.036621 | 122.5891 | -0.004578 | -0.31586 | 122.731 | 122.6624 | 122.5937 | 0.073242 | 0.004578 | 122.6074 | 0.013733 | -0.20142 | 122.7905 | 122.7768 | 122.7173 | 0.16937 | 0.10986 | 0.14191 | -0.022888 | 0.18311 | 0.073242 | 0.28839 | 0.28839 | 122.8775 | 122.8958 | -0.29297 | -0.27466 | 122.5662 | 122.6807 | 122.6028 | 122.6852
4042.7656 | 122.9919 | -122.7356 | 0.082397 | -0.012741 | -0.013089 | -0.079224 | -0.0059109 | -0.028948 | -0.051022 | -0.043596 | -0.0051575 | 0.0023222 | 0.0072802 | -0.010775 | -0.21851 | -0.021546 | -0.022185 | -0.07782 | 0.082397 | -0.10986 | -0.073242 | 0.091553 | -0.10071 | 0 | 0.059509 | 0.086975 | -0.10071 | 0.041199 | 0.12817 | 0.068665 | 0.10986 | 122.6257 | 0 | -0.15564 | 122.8271 | 122.7356 | 122.6349 | 0.10986 | 0.009155 | 122.6349 | 0.004578 | -0.041198 | 122.8638 | 122.8455 | 122.8043 | 0.21057 | 0.16937 | 0.20142 | 0.036621 | 0.22888 | 0.14191 | 0.19226 | 0.18768 | 122.818 | 122.8226 | -0.19226 | -0.18311 | 122.6624 | 122.7768 | 122.6578 | 122.7951
4044.5625 | 123.0469 | -122.7173 | 0.068665 | -0.0051118 | -0.01672 | -0.080506 | -0.0069791 | -0.027453 | -0.051022 | -0.041674 | -0.0051575 | 0.0016812 | 0.005144 | -0.015261 | -0.22129 | -0.018982 | -0.026885 | -0.07782 | 0.073242 | -0.1236 | -0.059509 | 0.11444 | -0.027466 | 0.050354 | 0.12817 | 0.091553 | -0.10071 | 0.086975 | 0.20599 | 0.15564 | 0.16937 | 122.5937 | 0.004577 | -0.12817 | 122.8317 | 122.7676 | 122.6898 | 0.17395 | 0.09613 | 122.6166 | 0.022888 | 0.01831 | 122.9233 | 122.8867 | 122.8729 | 0.27008 | 0.25635 | 0.23804 | 0.064087 | 0.3067 | 0.18768 | 0.19684 | 0.19226 | 122.7905 | 122.8088 | -0.19226 | -0.16937 | 122.6578 | 122.8043 | 122.6395 | 122.8455
4046.2969 | 122.9095 | -122.7905 | 0.13275 | 0.0025177 | -0.014157 | -0.079651 | -0.0052701 | -0.030657 | -0.050167 | -0.040178 | 0.00094606 | 0.0050992 | 0.0079212 | -0.014407 | -0.22086 | -0.018769 | -0.02368 | -0.13275 | 0.10986 | -0.13733 | -0.15106 | -0.004578 | -0.15564 | -0.059509 | -0.059509 | 0.14648 | -0.13275 | -0.050354 | 0.050354 | -0.009155 | 0.032043 | 122.6532 | -0.022888 | -0.28381 | 122.7859 | 122.731 | 122.6349 | 0.07782 | -0.018311 | 122.6578 | 0.013733 | -0.18311 | 122.8409 | 122.8226 | 122.7814 | 0.16479 | 0.1236 | 0.13275 | -0.013733 | 0.18311 | 0.082397 | 0.24719 | 0.27924 | 122.9004 | 122.937 | -0.27008 | -0.2655 | 122.6395 | 122.7402 | 122.6578 | 122.731
4048.1094 | 122.905 | -122.7676 | 0.10986 | -0.012741 | -0.014157 | -0.080292 | -0.0074063 | -0.03258 | -0.051235 | -0.038896 | 0.00094606 | 0.0033902 | 0.0079212 | -0.018893 | -0.21851 | -0.019837 | -0.021544 | -0.11444 | 0.091553 | -0.13275 | -0.13733 | 0.032043 | -0.12817 | -0.050354 | -0.022888 | 0.14648 | -0.11902 | -0.041199 | 0.073242 | 0.009155 | 0.032043 | 122.6349 | -0.01831 | -0.24719 | 122.7997 | 122.7173 | 122.6395 | 0.082397 | 0.004577 | 122.6486 | 0.036621 | -0.15106 | 122.8409 | 122.7997 | 122.7768 | 0.15106 | 0.12817 | 0.16479 | -0.004578 | 0.19226 | 0.07782 | 0.2243 | 0.2655 | 122.8592 | 122.9141 | -0.24261 | -0.22888 | 122.6303 | 122.7264 | 122.6532 | 122.7448
4049.8906 | 122.9507 | -122.7539 | 0.11902 | -0.012741 | -0.012661 | -0.080079 | -0.0067653 | -0.03322 | -0.052731 | -0.041033 | 0.00094606 | 0.0048856 | 0.010057 | -0.013766 | -0.22086 | -0.01941 | -0.020476 | -0.10529 | 0.10071 | -0.13733 | -0.12817 | 0.018311 | -0.11444 | -0.050354 | 0.004578 | 0.13733 | -0.11902 | 0.009155 | 0.09613 | 0.036621 | 0.086975 | 122.6166 | -0.018311 | -0.24719 | 122.7722 | 122.7036 | 122.6395 | 0.086975 | 0.022888 | 122.6349 | 0.01831 | -0.10986 | 122.85 | 122.8409 | 122.7905 | 0.20599 | 0.15564 | 0.15564 | 0.009155 | 0.21515 | 0.12817 | 0.23804 | 0.25635 | 122.8546 | 122.8912 | -0.25635 | -0.23804 | 122.6257 | 122.7631 | 122.6486 | 122.7585
4051.6875 | 122.9462 | -122.7356 | 0.10986 | -0.0051118 | -0.010952 | -0.076661 | -0.0042019 | -0.032152 | -0.048031 | -0.04381 | 0.00094606 | 0.0042448 | 0.007494 | -0.017397 | -0.21872 | -0.018769 | -0.02133 | -0.073242 | 0.11444 | -0.1236 | -0.10529 | 0.036621 | -0.13275 | -0.059509 | 0.022888 | 0.12817 | -0.11902 | 0.009155 | 0.064087 | 0.013733 | 0.068665 | 122.612 | 0.004578 | -0.21515 | 122.7722 | 122.6761 | 122.6028 | 0.064087 | -0.009155 | 122.6166 | 0.018311 | -0.10071 | 122.7997 | 122.8043 | 122.7493 | 0.18768 | 0.13275 | 0.16022 | 0.01831 | 0.18311 | 0.12817 | 0.23804 | 0.24719 | 122.85 | 122.8638 | -0.23346 | -0.22888 | 122.6303 | 122.7448 | 122.6624 | 122.7585
4053.4219 | 123.0331 | -122.731 | 0.086975 | -0.0051118 | -0.011166 | -0.079865 | -0.0056973 | -0.032366 | -0.052731 | -0.041887 | 0.00094606 | 0.002963 | 0.0062122 | -0.0067162 | -0.22001 | -0.017914 | -0.026244 | -0.050354 | 0.07782 | -0.11444 | -0.041199 | 0.10986 | -0.068665 | 0.009155 | 0.091553 | 0.091553 | -0.09613 | 0.091553 | 0.18768 | 0.10529 | 0.17853 | 122.6166 | -0.009155 | -0.12817 | 122.8409 | 122.7402 | 122.6624 | 0.1236 | 0.045776 | 122.6349 | 0.004578 | 0.004578 | 122.9187 | 122.9095 | 122.8363 | 0.27466 | 0.20142 | 0.2243 | 0.073242 | 0.28381 | 0.18768 | 0.19226 | 0.18768 | 122.8088 | 122.8226 | -0.20142 | -0.1831 | 122.6898 | 122.8226 | 122.6807 | 122.8226
4055.2188 | 123.0377 | -122.7631 | 0.09613 | -0.0051118 | -0.015652 | -0.080079 | -0.0063381 | -0.030871 | -0.051235 | -0.043169 | -0.0051575 | 0.001254 | 0.005785 | -0.013339 | -0.21958 | -0.019196 | -0.025389 | -0.082397 | 0.082397 | -0.10529 | -0.027466 | 0.16479 | -0.009155 | 0.041199 | 0.10986 | 0.091553 | -0.086975 | 0.07782 | 0.19226 | 0.13275 | 0.14191 | 122.6578 | -0.013733 | -0.1236 | 122.9279 | 122.8043 | 122.7539 | 0.14649 | 0.096131 | 122.6761 | -0.004577 | -0.01831 | 122.9553 | 122.905 | 122.8958 | 0.22888 | 0.21973 | 0.27008 | 0.07782 | 0.27924 | 0.16479 | 0.18768 | 0.17853 | 122.8455 | 122.8546 | -0.20142 | -0.1831 | 122.7356 | 122.8409 | 122.6807 | 122.8729
4056.9531 | 122.9965 | -122.7402 | 0.10071 | -0.0051118 | -0.012661 | -0.079438 | -0.0082607 | -0.035784 | -0.051022 | -0.040392 | -0.0021057 | 0.0027494 | 0.0098438 | -0.023165 | -0.2215 | -0.018982 | -0.024321 | -0.10529 | 0.09613 | -0.10071 | -0.086975 | 0.064087 | -0.10529 | -0.004578 | 0.032043 | 0.10071 | -0.10529 | 0.027466 | 0.12817 | 0.073242 | 0.10986 | 122.6395 | -0.004578 | -0.18768 | 122.8043 | 122.7356 | 122.6349 | 0.09613 | -0.004578 | 122.6349 | 0 | -0.073242 | 122.8683 | 122.85 | 122.8134 | 0.21515 | 0.17853 | 0.1648 | 0.013733 | 0.23346 | 0.13275 | 0.19684 | 0.20599 | 122.8363 | 122.8409 | -0.20142 | -0.20599 | 122.6532 | 122.7676 | 122.6349 | 122.7722
4058.7344 | 122.9324 | -122.7859 | 0.13275 | -0.0051118 | -0.013729 | -0.080079 | -0.0080471 | -0.028734 | -0.051663 | -0.042101 | 0.00094606 | 0.0031766 | 0.0089892 | -0.009707 | -0.22086 | -0.020478 | -0.024962 | -0.068665 | 0.091553 | -0.13733 | -0.1236 | 0.027466 | -0.11444 | -0.050354 | -0.004578 | 0.13733 | -0.11902 | -0.036621 | 0.082397 | 0.022888 | 0.045776 | 122.6486 | -0.041198 | -0.25635 | 122.8134 | 122.7356 | 122.6715 | 0.086975 | 0.022888 | 122.6669 | 0.004578 | -0.16937 | 122.8683 | 122.8317 | 122.8088 | 0.16479 | 0.14191 | 0.16479 | 0.013733 | 0.20142 | 0.082398 | 0.22888 | 0.25635 | 122.8775 | 122.9233 | -0.27008 | -0.25177 | 122.6624 | 122.7493 | 122.7173 | 122.7814
4060.4688 | 123.0057 | -122.7585 | 0.10071 | 0.0025177 | -0.012448 | -0.079865 | -0.0067653 | -0.030871 | -0.049526 | -0.041674 | -0.0051575 | 0.001254 | 0.0070666 | -0.012484 | -0.21937 | -0.021332 | -0.025603 | -0.09613 | 0.09613 | -0.10529 | -0.09613 | 0.041199 | -0.09613 | -0.018311 | 0.009155 | 0.10986 | -0.09613 | 0.004578 | 0.12817 | 0.054932 | 0.10071 | 122.6532 | -0.004578 | -0.19684 | 122.7997 | 122.7402 | 122.6624 | 0.086975 | 0.009156 | 122.6624 | 0.009155 | -0.09613 | 122.8867 | 122.8592 | 122.8134 | 0.19684 | 0.15106 | 0.14649 | 0.009156 | 0.2243 | 0.10071 | 0.20142 | 0.20599 | 122.8546 | 122.8683 | -0.20599 | -0.19684 | 122.6624 | 122.7631 | 122.6624 | 122.7676
4062.2656 | 123.0377 | -122.7356 | 0.082397 | -0.0051118 | -0.0083889 | -0.07837 | -0.0042019 | -0.027666 | -0.048245 | -0.041246 | -0.0021057 | 0.0033902 | 0.0066394 | -0.014834 | -0.21958 | -0.018342 | -0.024962 | -0.091553 | 0.11902 | -0.10986 | -0.091553 | 0.068665 | -0.10529 | -0.027466 | 0.086975 | 0.10529 | -0.086975 | 0.07782 | 0.16479 | 0.09613 | 0.16022 | 122.6257 | 0.036622 | -0.17395 | 122.8043 | 122.7081 | 122.6303 | 0.082397 | 0.004577 | 122.6486 | 0.022889 | -0.004577 | 122.9004 | 122.8958 | 122.8317 | 0.24719 | 0.1831 | 0.17853 | 0.01831 | 0.25177 | 0.16479 | 0.22888 | 0.19226 | 122.8546 | 122.8409 | -0.19226 | -0.16937 | 122.644 | 122.8134 | 122.644 | 122.8226
4064.0469 | 123.0515 | -122.7539 | 0.10071 | -0.0051118 | -0.013302 | -0.079438 | -0.0071927 | -0.031084 | -0.049313 | -0.038896 | -0.0021057 | 0.0014676 | 0.0062122 | -0.016116 | -0.22065 | -0.01941 | -0.021971 | -0.086975 | 0.07782 | -0.1236 | -0.064087 | 0.09613 | -0.054932 | 0.013733 | 0.086975 | 0.10986 | -0.082397 | 0.059509 | 0.18768 | 0.13733 | 0.16022 | 122.6303 | -0.022888 | -0.1648 | 122.85 | 122.7676 | 122.699 | 0.13733 | 0.068664 | 122.6715 | 0.009155 | -0.041199 | 122.9416 | 122.9141 | 122.8912 | 0.24261 | 0.21973 | 0.21973 | 0.059509 | 0.27008 | 0.14191 | 0.20142 | 0.19226 | 122.8317 | 122.8638 | -0.2243 | -0.18311 | 122.6898 | 122.8134 | 122.6669 | 122.8409
4065.7812 | 123.0057 | -122.7448 | 0.068665 | -0.0051118 | -0.010311 | -0.07837 | -0.0067653 | -0.029589 | -0.048886 | -0.042955 | 0.00094606 | 0.0025358 | 0.0070666 | -0.01227 | -0.21979 | -0.019837 | -0.02603 | -0.068665 | 0.064087 | -0.10071 | -0.045776 | 0.1236 | -0.064087 | 0.004578 | 0.10071 | 0.10071 | -0.086975 | 0.073242 | 0.15106 | 0.091553 | 0.12817 | 122.644 | -0.004578 | -0.11444 | 122.8683 | 122.7493 | 122.6807 | 0.10529 | 0.036621 | 122.6578 | 0.032043 | 0.004577 | 122.8958 | 122.8729 | 122.8363 | 0.21515 | 0.17853 | 0.2243 | 0.054932 | 0.23804 | 0.16022 | 0.1648 | 0.18768 | 122.8088 | 122.8455 | -0.16937 | -0.15564 | 122.699 | 122.818 | 122.6761 | 122.8455
4067.5938 | 123.0011 | -122.7631 | 0.082397 | 0.0025177 | -0.011166 | -0.079651 | -0.0046291 | -0.027239 | -0.049954 | -0.040392 | 0.00094606 | 0.0048856 | 0.0089892 | -0.0060754 | -0.22022 | -0.018555 | -0.022398 | -0.1236 | 0.11444 | -0.13733 | -0.13733 | 0.013733 | -0.16479 | -0.068665 | 0.022888 | 0.1236 | -0.11444 | 0.050354 | 0.12817 | 0.050354 | 0.12817 | 122.6257 | 0.032044 | -0.21973 | 122.7768 | 122.6944 | 122.5983 | 0.068664 | -0.027466 | 122.6486 | 0.041199 | -0.032043 | 122.8912 | 122.8912 | 122.8134 | 0.24262 | 0.16479 | 0.15106 | 0 | 0.24262 | 0.16479 | 0.25177 | 0.23804 | 122.8775 | 122.8867 | -0.21973 | -0.19684 | 122.6257 | 122.8134 | 122.6395 | 122.7859
4069.3906 | 122.9004 | -122.7951 | 0.13733 | 0.0025177 | -0.0081753 | -0.077302 | -0.0074063 | -0.030871 | -0.04974 | -0.041246 | -0.0021057 | 0.006381 | 0.0070666 | -0.013125 | -0.21894 | -0.020478 | -0.023039 | -0.13275 | 0.1236 | -0.14648 | -0.16937 | -0.050354 | -0.21057 | -0.11444 | -0.073242 | 0.12817 | -0.10986 | -0.045776 | 0.027466 | -0.041199 | 0.045776 | 122.6486 | -0.013733 | -0.3067 | 122.7448 | 122.6807 | 122.5845 | 0.032043 | -0.064087 | 122.6852 | -0.009155 | -0.18311 | 122.8226 | 122.8409 | 122.7539 | 0.15564 | 0.068664 | 0.09613 | -0.022889 | 0.13733 | 0.064087 | 0.27008 | 0.23804 | 122.9187 | 122.9233 | -0.28381 | -0.24719 | 122.6257 | 122.7493 | 122.6624 | 122.7219
4071.125 | 122.9233 | -122.7585 | 0.11444 | -0.0051118 | -0.011807 | -0.078583 | -0.0056973 | -0.03023 | -0.050808 | -0.039537 | 0.00094606 | 0.0050992 | 0.0081348 | -0.0071436 | -0.21958 | -0.019196 | -0.025389 | -0.086975 | 0.11444 | -0.13275 | -0.13275 | 0.022888 | -0.14648 | -0.082397 | -0.009155 | 0.13275 | -0.10071 | -0.013733 | 0.045776 | -0.013733 | 0.050354 | 122.6257 | 0 | -0.24719 | 122.7814 | 122.6761 | 122.612 | 0.050354 | -0.013733 | 122.6578 | 0.01831 | -0.12817 | 122.8043 | 122.8088 | 122.7448 | 0.15106 | 0.086975 | 0.15564 | 0 | 0.14648 | 0.086975 | 0.24719 | 0.23346 | 122.8729 | 122.8912 | -0.24719 | -0.21515 | 122.6257 | 122.7448 | 122.6715 | 122.7493
4072.9375 | 122.937 | -122.7905 | 0.1236 | 0.0025177 | -0.010311 | -0.077515 | -0.0048427 | -0.031084 | -0.049099 | -0.04146 | -0.0051575 | 0.0038174 | 0.0083484 | -0.012484 | -0.21872 | -0.018982 | -0.023467 | -0.12817 | 0.1236 | -0.14191 | -0.17395 | -0.027466 | -0.18768 | -0.091553 | -0.027466 | 0.15106 | -0.11902 | -0.013733 | 0.054932 | -0.018311 | 0.050354 | 122.6486 | 0 | -0.29755 | 122.7631 | 122.699 | 122.6028 | 0.050354 | -0.045776 | 122.6715 | 0.027466 | -0.13733 | 122.8455 | 122.8409 | 122.7722 | 0.16937 | 0.10071 | 0.11444 | -0.032043 | 0.17395 | 0.10529 | 0.2655 | 0.27008 | 122.9141 | 122.9416 | -0.2655 | -0.24261 | 122.6166 | 122.7768 | 122.6624 | 122.7631
4074.7188 | 122.937 | -122.7722 | 0.13275 | -0.012741 | -0.012875 | -0.07602 | -0.0035611 | -0.030016 | -0.050381 | -0.041246 | 0.00094606 | 0.00574 | 0.010057 | -0.015688 | -0.22086 | -0.019623 | -0.024962 | -0.1236 | 0.1236 | -0.14648 | -0.1831 | -0.032043 | -0.19684 | -0.10071 | -0.050354 | 0.12817 | -0.11902 | -0.027466 | 0.036621 | -0.027466 | 0.050354 | 122.6257 | -0.009155 | -0.31586 | 122.7402 | 122.6715 | 122.5754 | 0.045776 | -0.050354 | 122.6532 | -0.004577 | -0.16022 | 122.8088 | 122.8226 | 122.7448 | 0.16937 | 0.091553 | 0.11444 | -0.036621 | 0.15564 | 0.091553 | 0.27008 | 0.24719 | 122.8958 | 122.9004 | -0.27924 | -0.25177 | 122.5891 | 122.7448 | 122.6486 | 122.7219
4076.4531 | 123.056 | -122.7539 | 0.091553 | -0.0051118 | -0.014798 | -0.079438 | -0.0095425 | -0.032152 | -0.051022 | -0.040178 | -0.0021057 | -0.00045501 | 0.0081348 | -0.015261 | -0.2215 | -0.021119 | -0.025389 | -0.082397 | 0.064087 | -0.10529 | -0.045776 | 0.16022 | -0.009155 | 0.045776 | 0.11902 | 0.091553 | -0.086975 | 0.07782 | 0.21057 | 0.13733 | 0.14191 | 122.6486 | -0.027466 | -0.13733 | 122.9141 | 122.7997 | 122.7448 | 0.15106 | 0.096131 | 122.6669 | 0 | -0.013733 | 122.9645 | 122.8958 | 122.8912 | 0.22888 | 0.2243 | 0.2655 | 0.05951 | 0.29755 | 0.16479 | 0.16937 | 0.17853 | 122.818 | 122.8455 | -0.19684 | -0.17853 | 122.7081 | 122.8317 | 122.6715 | 122.8729
4078.25 | 122.9233 | -122.7997 | 0.1236 | 0.0025177 | -0.0094571 | -0.077088 | -0.0046291 | -0.030657 | -0.048031 | -0.041887 | 0.00094606 | 0.0033902 | 0.0081348 | -0.010561 | -0.21872 | -0.01941 | -0.024107 | -0.10986 | 0.11444 | -0.12817 | -0.14648 | 0.004578 | -0.18768 | -0.10071 | -0.022888 | 0.15106 | -0.11444 | -0.036621 | 0.032043 | -0.027466 | 0.050354 | 122.6715 | -0.009155 | -0.27008 | 122.8043 | 122.699 | 122.612 | 0.027466 | -0.059509 | 122.6852 | 0.027466 | -0.16022 | 122.8317 | 122.85 | 122.7722 | 0.16479 | 0.086975 | 0.13275 | -0.01831 | 0.14648 | 0.07782 | 0.24262 | 0.2655 | 122.9141 | 122.9507 | -0.25177 | -0.23804 | 122.6532 | 122.7631 | 122.6898 | 122.7768
4080.0312 | 122.9324 | -122.8134 | 0.13275 | -0.0051118 | -0.015438 | -0.07837 | -0.0080471 | -0.034289 | -0.050808 | -0.040605 | -0.0021057 | 0.0018948 | 0.010698 | -0.014407 | -0.21744 | -0.018769 | -0.022185 | -0.1236 | 0.11444 | -0.1236 | -0.15564 | 0.032043 | -0.14648 | -0.054932 | -0.032043 | 0.12817 | -0.12817 | -0.045776 | 0.07782 | 0.009155 | 0.036621 | 122.6898 | -0.01831 | -0.28839 | 122.8455 | 122.7585 | 122.6669 | 0.068664 | -0.022888 | 122.6852 | -0.004577 | -0.17853 | 122.8912 | 122.85 | 122.8226 | 0.1648 | 0.13733 | 0.15564 | -0.032044 | 0.20599 | 0.082398 | 0.23804 | 0.25635 | 122.9279 | 122.9416 | -0.25635 | -0.26093 | 122.6578 | 122.7676 | 122.6898 | 122.7814
4081.8125 | 123.0469 | -122.7402 | 0.082397 | -0.0051118 | -0.011166 | -0.079651 | -0.0063381 | -0.030016 | -0.050808 | -0.040819 | -0.0021057 | 0.0014676 | 0.0059986 | -0.014834 | -0.21958 | -0.018555 | -0.023253 | -0.10529 | 0.11902 | -0.11902 | -0.10986 | 0.050354 | -0.11902 | -0.036621 | 0.059509 | 0.10529 | -0.10071 | 0.073242 | 0.16479 | 0.091553 | 0.15564 | 122.6212 | 0.036622 | -0.19226 | 122.7905 | 122.7036 | 122.6212 | 0.082398 | 0 | 122.6395 | 0.022889 | -0.009155 | 122.905 | 122.8958 | 122.8317 | 0.25635 | 0.19226 | 0.16937 | 0.009156 | 0.2655 | 0.17395 | 0.23804 | 0.20599 | 122.8592 | 122.8455 | -0.20142 | -0.18311 | 122.6303 | 122.8134 | 122.6349 | 122.7997
4083.6094 | 122.9782 | -122.7814 | 0.13733 | 0.010147 | -0.013729 | -0.079865 | -0.0080471 | -0.032152 | -0.050381 | -0.043169 | 0.00094606 | 0.0014676 | 0.005785 | -0.013552 | -0.21979 | -0.019196 | -0.023894 | -0.07782 | 0.073242 | -0.09613 | -0.068665 | 0.11902 | -0.041199 | 0.009155 | 0.054932 | 0.11902 | -0.09613 | 0.004578 | 0.12817 | 0.059509 | 0.086975 | 122.6852 | -0.064087 | -0.20599 | 122.9004 | 122.7905 | 122.7402 | 0.10528 | 0.054931 | 122.6852 | -0.01831 | -0.13275 | 122.9095 | 122.8683 | 122.8409 | 0.1831 | 0.15564 | 0.21515 | 0.027465 | 0.2243 | 0.10071 | 0.16937 | 0.21515 | 122.8546 | 122.9004 | -0.23346 | -0.23346 | 122.7127 | 122.7859 | 122.7036 | 122.8363
4085.3438 | 123.0515 | -122.7631 | 0.09613 | -0.0051118 | -0.013943 | -0.079865 | -0.0071927 | -0.032366 | -0.049099 | -0.044023 | 0.00094606 | 0.0023222 | 0.0079212 | -0.012698 | -0.2215 | -0.020264 | -0.021117 | -0.086975 | 0.086975 | -0.10071 | -0.091553 | 0.073242 | -0.068665 | 0.013733 | 0.068665 | 0.11902 | -0.091553 | 0.045776 | 0.16479 | 0.10071 | 0.13733 | 122.6624 | -0.009155 | -0.18768 | 122.8363 | 122.7768 | 122.6944 | 0.11444 | 0.032043 | 122.6715 | 0.022889 | -0.050354 | 122.9279 | 122.9004 | 122.8638 | 0.22888 | 0.19226 | 0.17395 | 0.009155 | 0.25635 | 0.13733 | 0.18768 | 0.21057 | 122.85 | 122.8821 | -0.19684 | -0.18768 | 122.6715 | 122.8088 | 122.6761 | 122.8317
4087.125 | 123.0743 | -122.7448 | 0.091553 | -0.0051118 | -0.015011 | -0.080506 | -0.0086879 | -0.030016 | -0.051663 | -0.042955 | -0.0021057 | 0.002963 | 0.0066394 | -0.018038 | -0.22107 | -0.020691 | -0.023894 | -0.068665 | 0.09613 | -0.086975 | -0.032043 | 0.14191 | -0.004578 | 0.054932 | 0.15564 | 0.091553 | -0.09613 | 0.09613 | 0.20599 | 0.17395 | 0.16479 | 122.6578 | 0.004577 | -0.1236 | 122.8867 | 122.7997 | 122.7402 | 0.14191 | 0.082397 | 122.6486 | 0 | 0.004577 | 122.9507 | 122.9095 | 122.9187 | 0.26092 | 0.27008 | 0.22888 | 0.054932 | 0.30212 | 0.19226 | 0.1831 | 0.18768 | 122.8409 | 122.8363 | -0.17853 | -0.18768 | 122.7127 | 122.8409 | 122.6761 | 122.9004
4088.875 | 123.0606 | -122.7585 | 0.10529 | 0.010147 | -0.01437 | -0.078797 | -0.0082607 | -0.029162 | -0.053372 | -0.040819 | -0.0021057 | 0.0021084 | 0.0072802 | -0.012057 | -0.22257 | -0.022614 | -0.024321 | -0.059509 | 0.086975 | -0.10529 | -0.022888 | 0.14191 | -0.018311 | 0.041199 | 0.11902 | 0.09613 | -0.082397 | 0.068665 | 0.18768 | 0.14191 | 0.13275 | 122.6532 | -0.018311 | -0.12817 | 122.9004 | 122.7997 | 122.7402 | 0.14649 | 0.086975 | 122.6761 | -0.009156 | -0.036621 | 122.9462 | 122.8912 | 122.9004 | 0.21515 | 0.2243 | 0.24719 | 0.082398 | 0.27008 | 0.15106 | 0.19226 | 0.17853 | 122.8455 | 122.8546 | -0.21057 | -0.18768 | 122.7356 | 122.8271 | 122.699 | 122.8775
4090.6875 | 123.0606 | -122.7493 | 0.086975 | -0.012741 | -0.012448 | -0.078797 | -0.0052701 | -0.028307 | -0.048886 | -0.040392 | 0.00094606 | 0.0023222 | 0.0053576 | -0.015902 | -0.22086 | -0.021119 | -0.020049 | -0.041199 | 0.086975 | -0.086975 | -0.036621 | 0.13275 | -0.073242 | 0.018311 | 0.12817 | 0.10529 | -0.07782 | 0.091553 | 0.16937 | 0.10071 | 0.14648 | 122.6624 | 0 | -0.1236 | 122.8821 | 122.7676 | 122.6761 | 0.10529 | 0.013733 | 122.6715 | 0.018311 | 0.004578 | 122.9187 | 122.8958 | 122.85 | 0.2243 | 0.17853 | 0.21973 | 0.050354 | 0.24719 | 0.16937 | 0.17395 | 0.18311 | 122.8363 | 122.8546 | -0.17395 | -0.16479 | 122.7127 | 122.8409 | 122.7081 | 122.8775
4092.5 | 122.9599 | -122.7997 | 0.11902 | -0.0051118 | -0.010311 | -0.077302 | -0.0033475 | -0.026171 | -0.05209 | -0.039965 | -0.0021057 | 0.0044584 | 0.006853 | -0.013125 | -0.22001 | -0.019837 | -0.022826 | -0.073242 | 0.11444 | -0.12817 | -0.091553 | 0.036621 | -0.11444 | -0.059509 | 0.041199 | 0.13275 | -0.1236 | 0 | 0.073242 | 0 | 0.064087 | 122.6715 | -0.004578 | -0.21057 | 122.8363 | 122.7402 | 122.6852 | 0.068665 | 0.013733 | 122.6761 | 0.013732 | -0.11902 | 122.8729 | 122.8638 | 122.7997 | 0.18768 | 0.1236 | 0.1648 | 0.036621 | 0.19684 | 0.1236 | 0.24262 | 0.25635 | 122.9141 | 122.9324 | -0.24719 | -0.24261 | 122.7081 | 122.7997 | 122.7264 | 122.8409
4094.2812 | 122.9691 | -122.7951 | 0.11902 | 0.0025177 | -0.01437 | -0.078797 | -0.0054837 | -0.030657 | -0.051235 | -0.040178 | -0.0021057 | 0.002963 | 0.0081348 | -0.01462 | -0.21723 | -0.018982 | -0.023039 | -0.13275 | 0.13733 | -0.14648 | -0.17395 | -0.022888 | -0.18768 | -0.086975 | -0.018311 | 0.12817 | -0.1236 | 0.004578 | 0.073242 | -0.009155 | 0.073242 | 122.6486 | 0.01831 | -0.29297 | 122.7722 | 122.7081 | 122.6074 | 0.059509 | -0.041199 | 122.6715 | 0.009155 | -0.11444 | 122.8683 | 122.8683 | 122.7859 | 0.19684 | 0.11444 | 0.1236 | -0.027466 | 0.19684 | 0.12817 | 0.28381 | 0.25177 | 122.9324 | 122.9233 | -0.2655 | -0.24261 | 122.6212 | 122.7997 | 122.6624 | 122.7768
4096.0625 | 122.937 | -122.8226 | 0.13733 | 0.0025177 | -0.014157 | -0.080719 | -0.0059109 | -0.032793 | -0.053372 | -0.041887 | 0.0039979 | 0.0038174 | 0.0092028 | -0.013766 | -0.22022 | -0.017701 | -0.021544 | -0.1236 | 0.1236 | -0.13275 | -0.15564 | 0.009155 | -0.15106 | -0.059509 | -0.036621 | 0.14648 | -0.11902 | -0.050354 | 0.064087 | -0.009155 | 0.032043 | 122.6898 | -0.013733 | -0.29297 | 122.8317 | 122.7631 | 122.6715 | 0.073242 | -0.018311 | 122.7036 | 0.009155 | -0.18768 | 122.8867 | 122.8546 | 122.8134 | 0.15106 | 0.10986 | 0.14191 | -0.022889 | 0.18311 | 0.068665 | 0.25635 | 0.2655 | 122.9462 | 122.9691 | -0.27008 | -0.25635 | 122.6669 | 122.7722 | 122.699 | 122.7859
4097.8594 | 123.056 | -122.7585 | 0.086975 | -0.012741 | -0.013089 | -0.080292 | -0.0080471 | -0.033007 | -0.051663 | -0.042101 | 0.00094606 | 0.001254 | 0.0087756 | -0.017611 | -0.22022 | -0.020051 | -0.027098 | -0.07782 | 0.086975 | -0.09613 | -0.050354 | 0.1236 | -0.027466 | 0.045776 | 0.091553 | 0.091553 | -0.086975 | 0.068665 | 0.16937 | 0.1236 | 0.13733 | 122.6624 | 0 | -0.13733 | 122.8821 | 122.8043 | 122.731 | 0.14191 | 0.068664 | 122.6715 | 0.004578 | -0.01831 | 122.9279 | 122.8958 | 122.8821 | 0.2243 | 0.21057 | 0.21973 | 0.045776 | 0.25635 | 0.15564 | 0.1831 | 0.17853 | 122.8455 | 122.85 | -0.1831 | -0.17395 | 122.7081 | 122.8271 | 122.6807 | 122.85
4099.5938 | 122.9874 | -122.7997 | 0.11444 | 0.0025177 | -0.011593 | -0.078156 | -0.0061245 | -0.028948 | -0.050167 | -0.040605 | -0.0021057 | 0.0036038 | 0.006853 | -0.0086388 | -0.21937 | -0.020691 | -0.023467 | -0.073242 | 0.09613 | -0.14191 | -0.09613 | 0.068665 | -0.1236 | -0.036621 | 0.059509 | 0.11444 | -0.10986 | 0.022888 | 0.10071 | 0.045776 | 0.09613 | 122.6578 | -0.018311 | -0.21057 | 122.8683 | 122.7631 | 122.6761 | 0.10529 | 0.018311 | 122.6898 | 0 | -0.091553 | 122.9004 | 122.8958 | 122.8455 | 0.20599 | 0.15564 | 0.21057 | 0.045777 | 0.21057 | 0.13275 | 0.23804 | 0.2243 | 122.8958 | 122.9141 | -0.25635 | -0.2243 | 122.7036 | 122.8226 | 122.7264 | 122.8592
4101.4062 | 123.024 | -122.7951 | 0.091553 | -0.0051118 | -0.014798 | -0.079011 | -0.0067653 | -0.029802 | -0.050808 | -0.038683 | -0.0021057 | 0.00082679 | 0.0079212 | -0.011843 | -0.21744 | -0.019837 | -0.022612 | -0.10071 | 0.082397 | -0.11902 | -0.09613 | 0.07782 | -0.10986 | 0 | 0.054932 | 0.10986 | -0.10071 | 0.041199 | 0.14191 | 0.068665 | 0.10071 | 122.6761 | -0.009156 | -0.18768 | 122.8729 | 122.7951 | 122.6852 | 0.11902 | 0.009156 | 122.6944 | 0.01831 | -0.050354 | 122.937 | 122.8958 | 122.8638 | 0.20142 | 0.16937 | 0.19684 | 0.022889 | 0.24262 | 0.14191 | 0.20142 | 0.21057 | 122.8775 | 122.905 | -0.21057 | -0.19226 | 122.699 | 122.8363 | 122.6944 | 122.85
4103.2031 | 122.9965 | -122.7859 | 0.11444 | 0.0025177 | -0.013302 | -0.079651 | -0.0078335 | -0.029162 | -0.051449 | -0.040819 | -0.0021057 | 0.004672 | 0.0094166 | -0.01227 | -0.21979 | -0.019623 | -0.019835 | -0.10986 | 0.11444 | -0.15106 | -0.14191 | -0.004578 | -0.11902 | -0.059509 | 0.013733 | 0.14191 | -0.10529 | -0.013733 | 0.10071 | 0.041199 | 0.07782 | 122.6349 | 0 | -0.25635 | 122.7814 | 122.7264 | 122.6669 | 0.091553 | 0.032043 | 122.6807 | 0.027466 | -0.12817 | 122.8867 | 122.8638 | 122.8271 | 0.18311 | 0.14649 | 0.14648 | 0.009155 | 0.20599 | 0.091553 | 0.2655 | 0.24719 | 122.9004 | 122.9279 | -0.2655 | -0.21973 | 122.644 | 122.7722 | 122.6761 | 122.7997
4104.9219 | 123.0606 | -122.7768 | 0.086975 | -0.012741 | -0.010311 | -0.078156 | -0.0048427 | -0.027239 | -0.050381 | -0.039965 | -0.0021057 | 0.0036038 | 0.0098438 | -0.015688 | -0.22086 | -0.018769 | -0.028594 | -0.10529 | 0.11902 | -0.11444 | -0.10986 | 0.041199 | -0.12817 | -0.059509 | 0.050354 | 0.11902 | -0.10986 | 0.082397 | 0.15564 | 0.073242 | 0.13733 | 122.6624 | 0.032044 | -0.19684 | 122.818 | 122.7173 | 122.6486 | 0.054932 | -0.013733 | 122.6669 | 0.032044 | -0.004578 | 122.9324 | 122.9141 | 122.85 | 0.24719 | 0.18311 | 0.15564 | 0.004578 | 0.2655 | 0.19226 | 0.23346 | 0.22888 | 122.8958 | 122.8958 | -0.20142 | -0.19684 | 122.6669 | 122.8592 | 122.6715 | 122.8271
4106.7188 | 122.9874 | -122.7768 | 0.10986 | -0.0051118 | -0.0079617 | -0.076447 | -0.0052701 | -0.028093 | -0.048458 | -0.040178 | -0.0021057 | 0.0044584 | 0.010057 | -0.013979 | -0.21979 | -0.018342 | -0.017485 | -0.082397 | 0.09613 | -0.13275 | -0.11444 | 0.041199 | -0.11902 | -0.064087 | 0.018311 | 0.13275 | -0.11444 | 0 | 0.082397 | -0.009155 | 0.082397 | 122.644 | -0.013733 | -0.2243 | 122.818 | 122.7127 | 122.6578 | 0.068664 | 0.013732 | 122.6624 | 0.022888 | -0.10986 | 122.8592 | 122.8592 | 122.7676 | 0.19684 | 0.10529 | 0.17395 | 0.01831 | 0.19684 | 0.11444 | 0.22888 | 0.24719 | 122.8729 | 122.9095 | -0.24261 | -0.2243 | 122.6624 | 122.7768 | 122.6944 | 122.7951
4108.5156 | 123.0881 | -122.7676 | 0.086975 | 0.0025177 | -0.015011 | -0.080506 | -0.010824 | -0.032366 | -0.051022 | -0.039751 | -0.0021057 | -0.002164 | 0.0064258 | -0.016116 | -0.22001 | -0.019837 | -0.025603 | -0.068665 | 0.073242 | -0.09613 | -0.022888 | 0.17395 | -0.004578 | 0.064087 | 0.14648 | 0.086975 | -0.091553 | 0.073242 | 0.20599 | 0.14191 | 0.15564 | 122.6715 | -0.013733 | -0.10986 | 122.9416 | 122.8317 | 122.7631 | 0.16022 | 0.091552 | 122.6761 | 0 | -0.013733 | 122.9736 | 122.9233 | 122.9095 | 0.24719 | 0.23346 | 0.27008 | 0.073242 | 0.29755 | 0.16479 | 0.16937 | 0.17853 | 122.8409 | 122.8546 | -0.1831 | -0.17853 | 122.7448 | 122.8409 | 122.699 | 122.9141
4110.2344 | 123.0057 | -122.8226 | 0.14191 | 0.0025177 | -0.012448 | -0.078156 | -0.0063381 | -0.029589 | -0.051663 | -0.042101 | -0.0051575 | 0.0031766 | 0.008562 | -0.0073572 | -0.22129 | -0.021546 | -0.01898 | -0.11444 | 0.11444 | -0.15106 | -0.14648 | -0.004578 | -0.11902 | -0.050354 | -0.027466 | 0.12817 | -0.13733 | -0.004578 | 0.086975 | 0.032043 | 0.07782 | 122.6715 | -0.027466 | -0.28839 | 122.818 | 122.7722 | 122.7036 | 0.10071 | 0.032043 | 122.6852 | -0.013733 | -0.14649 | 122.9095 | 122.9004 | 122.8546 | 0.21515 | 0.16937 | 0.14648 | 0.004578 | 0.2243 | 0.13275 | 0.2655 | 0.2655 | 122.937 | 122.9507 | -0.29297 | -0.27924 | 122.6761 | 122.818 | 122.7081 | 122.7951
4112.0312 | 123.0972 | -122.7859 | 0.086975 | -0.0051118 | -0.014584 | -0.079865 | -0.010824 | -0.034502 | -0.051663 | -0.040819 | -0.0021057 | 0.0014676 | 0.0066394 | -0.019747 | -0.21744 | -0.020905 | -0.023039 | -0.059509 | 0.073242 | -0.10529 | -0.027466 | 0.16479 | 0.004578 | 0.068665 | 0.15106 | 0.09613 | -0.068665 | 0.07782 | 0.21057 | 0.15106 | 0.15106 | 122.6807 | -0.013733 | -0.11444 | 122.9507 | 122.8546 | 122.7905 | 0.17395 | 0.10986 | 122.7173 | 0.009155 | -0.009155 | 122.9965 | 122.937 | 122.937 | 0.21973 | 0.21973 | 0.27008 | 0.07782 | 0.27924 | 0.14649 | 0.17853 | 0.16479 | 122.8592 | 122.8821 | -0.19226 | -0.15564 | 122.7585 | 122.8638 | 122.7264 | 122.937
4113.8281 | 123.0331 | -122.7905 | 0.10529 | -0.0051118 | -0.014157 | -0.079651 | -0.0078335 | -0.031939 | -0.053372 | -0.043383 | -0.0051575 | 0.0036038 | 0.006853 | -0.012484 | -0.21872 | -0.019623 | -0.027525 | -0.091553 | 0.073242 | -0.11444 | -0.09613 | 0.064087 | -0.10986 | -0.004578 | 0.036621 | 0.10529 | -0.10529 | 0.022888 | 0.1236 | 0.059509 | 0.10986 | 122.6761 | -0.032044 | -0.20142 | 122.8546 | 122.7859 | 122.6807 | 0.10986 | 0.004578 | 122.6852 | 0 | -0.082398 | 122.9141 | 122.9004 | 122.85 | 0.21515 | 0.16479 | 0.17853 | 0.018311 | 0.22888 | 0.12817 | 0.18768 | 0.21057 | 122.8638 | 122.8958 | -0.21973 | -0.21057 | 122.6944 | 122.8134 | 122.699 | 122.8271
4115.5781 | 123.0835 | -122.7951 | 0.082397 | 0.0025177 | -0.013729 | -0.081147 | -0.0089017 | -0.027239 | -0.052944 | -0.039537 | 0.0039979 | -2.7806e-05 | 0.005785 | -0.0077844 | -0.21979 | -0.020478 | -0.022185 | -0.050354 | 0.068665 | -0.10071 | -0.032043 | 0.14648 | -0.009155 | 0.045776 | 0.14648 | 0.09613 | -0.073242 | 0.073242 | 0.21515 | 0.13733 | 0.14648 | 122.6944 | -0.013732 | -0.11444 | 122.9416 | 122.8409 | 122.7859 | 0.14648 | 0.091553 | 122.7219 | 0.013733 | -0.009155 | 123.0103 | 122.9416 | 122.9324 | 0.21973 | 0.21057 | 0.24719 | 0.068665 | 0.28839 | 0.14648 | 0.16937 | 0.16937 | 122.8638 | 122.8912 | -0.18311 | -0.15564 | 122.7631 | 122.8683 | 122.7448 | 122.9416
4117.375 | 123.0835 | -122.7585 | 0.082397 | 0.0025177 | -0.012448 | -0.077729 | -0.0071927 | -0.031084 | -0.049954 | -0.040605 | -0.0021057 | 0.0014676 | 0.0077076 | -0.013552 | -0.2215 | -0.020264 | -0.025816 | -0.045776 | 0.064087 | -0.07782 | -0.027466 | 0.12817 | -0.054932 | 0.018311 | 0.11902 | 0.091553 | -0.07782 | 0.086975 | 0.15564 | 0.10529 | 0.14191 | 122.6807 | -0.01831 | -0.10986 | 122.8867 | 122.7768 | 122.7036 | 0.096131 | 0.022888 | 122.6807 | 0.009156 | 0.004578 | 122.9141 | 122.9004 | 122.8638 | 0.21973 | 0.18311 | 0.20599 | 0.050354 | 0.23346 | 0.16479 | 0.14191 | 0.16937 | 122.8226 | 122.85 | -0.16022 | -0.16022 | 122.731 | 122.8455 | 122.7127 | 122.8775
4119.1719 | 122.9553 | -122.7951 | 0.1236 | -0.012741 | -0.010952 | -0.079438 | -0.0020657 | -0.033007 | -0.047817 | -0.040819 | -0.0021057 | 0.0040312 | 0.0079212 | -0.0077844 | -0.22107 | -0.018555 | -0.020689 | -0.11902 | 0.1236 | -0.14648 | -0.17853 | -0.050354 | -0.19684 | -0.1236 | -0.086975 | 0.12817 | -0.12817 | -0.027466 | 0.022888 | -0.041199 | 0.045776 | 122.6486 | 0 | -0.30212 | 122.7448 | 122.6715 | 122.5983 | 0.022888 | -0.050354 | 122.6669 | 0.004578 | -0.15106 | 122.818 | 122.8409 | 122.7539 | 0.17395 | 0.086975 | 0.09613 | -0.032044 | 0.15106 | 0.10071 | 0.27008 | 0.25635 | 122.9187 | 122.9233 | -0.27008 | -0.25177 | 122.6166 | 122.7676 | 122.6761 | 122.7081
4120.9844 | 123.0835 | -122.7997 | 0.07782 | 0.0025177 | -0.012661 | -0.080506 | -0.0086879 | -0.03023 | -0.048672 | -0.040178 | 0.00094606 | 0.0025358 | 0.0079212 | -0.015902 | -0.21979 | -0.019837 | -0.022185 | -0.054932 | 0.073242 | -0.10529 | -0.022888 | 0.14648 | -0.013733 | 0.041199 | 0.10986 | 0.10071 | -0.091553 | 0.073242 | 0.18768 | 0.12817 | 0.14648 | 122.6944 | -0.004578 | -0.10071 | 122.9462 | 122.8409 | 122.7859 | 0.14649 | 0.091553 | 122.7081 | 0.022888 | -0.004578 | 122.9874 | 122.9462 | 122.9279 | 0.23804 | 0.21973 | 0.25177 | 0.082398 | 0.27924 | 0.16479 | 0.17853 | 0.19226 | 122.8729 | 122.9004 | -0.18311 | -0.16937 | 122.7768 | 122.8729 | 122.7448 | 122.9095
4122.7188 | 122.9828 | -122.8088 | 0.11444 | -0.0051118 | -0.011807 | -0.078797 | -0.0067653 | -0.029589 | -0.053372 | -0.042314 | -0.0021057 | 0.0040312 | 0.010057 | -0.0032984 | -0.22086 | -0.020264 | -0.023467 | -0.082397 | 0.1236 | -0.13733 | -0.10529 | 0.045776 | -0.13733 | -0.059509 | 0.032043 | 0.13275 | -0.10529 | 0.004578 | 0.064087 | -0.009155 | 0.054932 | 122.6715 | 0.009155 | -0.21973 | 122.8546 | 122.7493 | 122.6715 | 0.07782 | 0 | 122.7036 | 0.01831 | -0.10986 | 122.8729 | 122.8638 | 122.7997 | 0.16022 | 0.096131 | 0.18311 | 0.032043 | 0.16937 | 0.10986 | 0.26093 | 0.23804 | 122.9324 | 122.9416 | -0.25177 | -0.21973 | 122.7036 | 122.8134 | 122.7264 | 122.8409
4124.5156 | 122.9874 | -122.8088 | 0.09613 | -0.0051118 | -0.011166 | -0.079011 | -0.0052701 | -0.030443 | -0.049099 | -0.039965 | -0.0051575 | 0.0042448 | 0.006853 | -0.007998 | -0.21702 | -0.020691 | -0.02133 | -0.12817 | 0.11444 | -0.15106 | -0.16479 | -0.009155 | -0.19226 | -0.086975 | -0.027466 | 0.1236 | -0.11902 | 0.009155 | 0.068665 | 0.004578 | 0.073242 | 122.6578 | 0.018311 | -0.26092 | 122.7997 | 122.7219 | 122.6166 | 0.064087 | -0.041199 | 122.6898 | 0.027466 | -0.086975 | 122.8775 | 122.8821 | 122.8134 | 0.19226 | 0.1236 | 0.14191 | -0.013733 | 0.18768 | 0.12817 | 0.2655 | 0.24261 | 122.9233 | 122.9324 | -0.24719 | -0.21515 | 122.644 | 122.818 | 122.6807 | 122.7814
4126.2344 | 123.1155 | -122.7631 | 0.10071 | 0.0025177 | -0.015652 | -0.081147 | -0.0093289 | -0.030443 | -0.053372 | -0.039751 | -0.0021057 | 0.001254 | 0.0072802 | -0.016757 | -0.21787 | -0.01941 | -0.021758 | -0.07782 | 0.082397 | -0.10529 | -0.032043 | 0.15564 | -0.009155 | 0.064087 | 0.13733 | 0.086975 | -0.091553 | 0.10071 | 0.22888 | 0.16479 | 0.16937 | 122.6578 | -0.018311 | -0.13275 | 122.9187 | 122.8271 | 122.7539 | 0.16937 | 0.096131 | 122.6715 | -0.013733 | 0 | 122.9919 | 122.9324 | 122.9279 | 0.26093 | 0.25635 | 0.26093 | 0.073243 | 0.32044 | 0.19226 | 0.18768 | 0.17853 | 122.8455 | 122.85 | -0.20599 | -0.19226 | 122.731 | 122.8638 | 122.6852 | 122.9004
4128.0469 | 123.056 | -122.7951 | 0.09613 | -0.0051118 | -0.010952 | -0.078156 | -0.010183 | -0.030016 | -0.051876 | -0.041674 | 0.00094606 | 0.001254 | 0.006853 | -0.011202 | -0.22086 | -0.019837 | -0.024107 | -0.091553 | 0.068665 | -0.10529 | -0.064087 | 0.10986 | -0.086975 | 0.009155 | 0.068665 | 0.10529 | -0.091553 | 0.050354 | 0.14648 | 0.068665 | 0.11902 | 122.6898 | -0.027465 | -0.16022 | 122.905 | 122.8043 | 122.7081 | 0.11444 | 0.018311 | 122.7036 | 0.009156 | -0.045776 | 122.9416 | 122.9141 | 122.8638 | 0.21057 | 0.16022 | 0.21515 | 0.041199 | 0.23804 | 0.14191 | 0.17395 | 0.19684 | 122.8638 | 122.9004 | -0.20142 | -0.18768 | 122.731 | 122.8455 | 122.7036 | 122.8638
4129.8281 | 123.0057 | -122.8363 | 0.10986 | -0.0051118 | -0.010311 | -0.077942 | -0.0056973 | -0.028521 | -0.054013 | -0.040178 | 0.00094606 | 0.0038174 | 0.0079212 | -0.006289 | -0.22193 | -0.018128 | -0.024107 | -0.09613 | 0.09613 | -0.13733 | -0.09613 | 0.054932 | -0.11444 | -0.041199 | 0.054932 | 0.13275 | -0.10986 | 0.041199 | 0.091553 | 0.050354 | 0.086975 | 122.699 | -0.013733 | -0.20599 | 122.8912 | 122.7951 | 122.7219 | 0.09613 | 0.022888 | 122.7264 | 0.022888 | -0.068664 | 122.9279 | 122.9233 | 122.8867 | 0.19684 | 0.16022 | 0.19226 | 0.041199 | 0.20142 | 0.15106 | 0.23346 | 0.24261 | 122.9324 | 122.9691 | -0.24719 | -0.21973 | 122.7402 | 122.8775 | 122.7402 | 122.8912
4131.5625 | 123.0927 | -122.7768 | 0.086975 | -0.012741 | -0.011593 | -0.07837 | -0.0071927 | -0.025103 | -0.050381 | -0.040178 | -0.0021057 | 0.0036038 | 0.0089892 | -0.0082116 | -0.21808 | -0.018982 | -0.017912 | -0.050354 | 0.059509 | -0.10071 | -0.032043 | 0.14191 | -0.064087 | 0.018311 | 0.10529 | 0.10529 | -0.09613 | 0.082397 | 0.17853 | 0.10986 | 0.15564 | 122.6761 | -0.027466 | -0.11902 | 122.9187 | 122.7951 | 122.7127 | 0.11902 | 0.036621 | 122.6807 | 0.018311 | -0.004578 | 122.9553 | 122.9324 | 122.8867 | 0.25177 | 0.20599 | 0.24262 | 0.068665 | 0.27466 | 0.17853 | 0.16022 | 0.20142 | 122.8363 | 122.8821 | -0.18768 | -0.1831 | 122.7448 | 122.8592 | 122.7264 | 122.8821
4133.3594 | 122.9828 | -122.8271 | 0.10986 | -0.012741 | -0.010525 | -0.079651 | -0.0069791 | -0.02788 | -0.048672 | -0.03911 | -0.0021057 | 0.0038174 | 0.0070666 | -0.010348 | -0.22022 | -0.020264 | -0.02368 | -0.1236 | 0.10986 | -0.15106 | -0.15564 | -0.032043 | -0.17853 | -0.091553 | -0.027466 | 0.12817 | -0.11902 | 0 | 0.045776 | -0.018311 | 0.064087 | 122.6761 | 0 | -0.2655 | 122.7951 | 122.7356 | 122.6486 | 0.059509 | -0.027466 | 122.7081 | 0.018311 | -0.10986 | 122.8729 | 122.8912 | 122.8088 | 0.18311 | 0.10071 | 0.11902 | -0.004578 | 0.16479 | 0.11902 | 0.26093 | 0.24719 | 122.937 | 122.9553 | -0.26093 | -0.22888 | 122.6715 | 122.8271 | 122.7036 | 122.7997
4135.1562 | 122.9828 | -122.8271 | 0.11902 | -0.0051118 | -0.0098843 | -0.077515 | -0.0039883 | -0.03258 | -0.050595 | -0.039324 | 0.00094606 | 0.004672 | 0.0094166 | -0.015048 | -0.21808 | -0.019196 | -0.024962 | -0.13733 | 0.1236 | -0.14648 | -0.16479 | -0.045776 | -0.20142 | -0.10986 | -0.054932 | 0.12817 | -0.1236 | -0.032043 | 0.027466 | -0.041199 | 0.050354 | 122.6807 | 0.004577 | -0.28381 | 122.7814 | 122.7173 | 122.6257 | 0.036621 | -0.054932 | 122.7036 | 0.009155 | -0.15106 | 122.8546 | 122.8775 | 122.7859 | 0.17395 | 0.082397 | 0.10071 | -0.018311 | 0.15106 | 0.091553 | 0.27008 | 0.25177 | 122.9507 | 122.9553 | -0.2655 | -0.24261 | 122.6624 | 122.7951 | 122.6898 | 122.7722
4136.9688 | 123.1018 | -122.7722 | 0.10529 | -0.012741 | -0.012448 | -0.076874 | -0.0067653 | -0.031298 | -0.050167 | -0.038896 | 0.00094606 | 0.0025358 | 0.0087756 | -0.014834 | -0.21979 | -0.018982 | -0.02133 | -0.064087 | 0.07782 | -0.11902 | -0.045776 | 0.11444 | -0.07782 | 0.013733 | 0.10071 | 0.09613 | -0.09613 | 0.09613 | 0.1831 | 0.10529 | 0.17395 | 122.6532 | -0.027466 | -0.15106 | 122.8867 | 122.7859 | 122.6944 | 0.13275 | 0.041199 | 122.6761 | -0.009156 | -0.009156 | 122.9553 | 122.9462 | 122.8775 | 0.27008 | 0.20142 | 0.23346 | 0.073243 | 0.27924 | 0.19226 | 0.19684 | 0.19226 | 122.85 | 122.8683 | -0.22431 | -0.20142 | 122.7264 | 122.8683 | 122.7081 | 122.8729
4138.7031 | 123.0927 | -122.7859 | 0.10529 | -0.0051118 | -0.013943 | -0.080292 | -0.0084743 | -0.033434 | -0.052304 | -0.042101 | 0.0039979 | 0.0014676 | 0.0042896 | -0.019534 | -0.22129 | -0.020264 | -0.023253 | -0.082397 | 0.068665 | -0.10529 | -0.027466 | 0.15564 | -0.013733 | 0.045776 | 0.12817 | 0.10986 | -0.082397 | 0.086975 | 0.18768 | 0.13275 | 0.14648 | 122.6807 | -0.036621 | -0.13275 | 122.9416 | 122.8317 | 122.7722 | 0.15106 | 0.091553 | 122.7036 | 0.004577 | -0.018311 | 122.9736 | 122.9324 | 122.9187 | 0.22888 | 0.21515 | 0.26093 | 0.07782 | 0.27008 | 0.16937 | 0.17395 | 0.19226 | 122.8546 | 122.8958 | -0.21057 | -0.18768 | 122.7585 | 122.8729 | 122.7036 | 122.9141
4140.5 | 123.0927 | -122.7676 | 0.086975 | -0.0051118 | -0.011807 | -0.07837 | -0.0065517 | -0.027025 | -0.051235 | -0.041674 | 0.00094606 | 0.0021084 | 0.0064258 | -0.011416 | -0.22043 | -0.018982 | -0.024107 | -0.045776 | 0.07782 | -0.07782 | -0.022888 | 0.13275 | -0.059509 | 0.018311 | 0.11444 | 0.10986 | -0.068665 | 0.091553 | 0.1831 | 0.12817 | 0.14648 | 122.6898 | -0.009155 | -0.10986 | 122.9004 | 122.7859 | 122.7081 | 0.096131 | 0.018311 | 122.699 | 0.022888 | 0.004578 | 122.9507 | 122.9141 | 122.8958 | 0.21515 | 0.19684 | 0.21057 | 0.054932 | 0.25177 | 0.16022 | 0.15564 | 0.17853 | 122.8455 | 122.8775 | -0.16479 | -0.15564 | 122.7448 | 122.8592 | 122.7219 | 122.8821
4142.2969 | 122.9736 | -122.8455 | 0.12817 | -0.0051118 | -0.012448 | -0.080506 | -0.0071927 | -0.030443 | -0.051876 | -0.041674 | 0.00094606 | 0.0025358 | 0.0079212 | -0.016116 | -0.21958 | -0.020264 | -0.02368 | -0.15564 | 0.12817 | -0.15564 | -0.17853 | -0.032043 | -0.14191 | -0.07782 | -0.068665 | 0.15106 | -0.13275 | -0.054932 | 0.054932 | -0.022888 | 0.050354 | 122.6898 | 0 | -0.3067 | 122.8134 | 122.7676 | 122.7036 | 0.07782 | 0.013733 | 122.7127 | 0.022888 | -0.18311 | 122.9004 | 122.8958 | 122.8226 | 0.18311 | 0.10986 | 0.1236 | -0.022888 | 0.18768 | 0.077819 | 0.28381 | 0.28381 | 122.9736 | 122.9965 | -0.28381 | -0.26093 | 122.6669 | 122.7905 | 122.6898 | 122.7768
4144.0938 | 122.9736 | -122.8455 | 0.14191 | 0.0025177 | -0.015225 | -0.080719 | -0.0071927 | -0.031084 | -0.05209 | -0.043596 | -0.0021057 | 0.0048856 | 0.0098438 | -0.010561 | -0.22022 | -0.019196 | -0.021971 | -0.15106 | 0.10986 | -0.14191 | -0.16937 | -0.013733 | -0.13733 | -0.064087 | -0.045776 | 0.13733 | -0.15106 | -0.050354 | 0.054932 | -0.009155 | 0.045776 | 122.7036 | -0.032044 | -0.31128 | 122.8317 | 122.7814 | 122.7081 | 0.07782 | 0.004578 | 122.6944 | -0.004578 | -0.19226 | 122.9004 | 122.8912 | 122.8363 | 0.19684 | 0.14191 | 0.12817 | -0.027466 | 0.20599 | 0.10071 | 0.25177 | 0.28839 | 122.9553 | 122.9828 | -0.28381 | -0.29297 | 122.6761 | 122.7951 | 122.6944 | 122.7997
4145.8906 | 123.0057 | -122.818 | 0.10986 | -0.012741 | -0.0086027 | -0.077942 | -0.0037747 | -0.030443 | -0.050167 | -0.04146 | -0.0021057 | 0.0021084 | 0.0094166 | -0.012484 | -0.22001 | -0.020264 | -0.016631 | -0.11444 | 0.11902 | -0.13275 | -0.17853 | -0.013733 | -0.1831 | -0.086975 | -0.018311 | 0.13275 | -0.10071 | 0.004578 | 0.059509 | -0.009155 | 0.082397 | 122.6852 | 0.009156 | -0.28839 | 122.8043 | 122.731 | 122.6349 | 0.045776 | -0.050354 | 122.7173 | 0.022888 | -0.10529 | 122.8775 | 122.9004 | 122.8088 | 0.18311 | 0.091553 | 0.11902 | -0.045777 | 0.16022 | 0.10529 | 0.25177 | 0.23346 | 122.937 | 122.9507 | -0.24261 | -0.21057 | 122.6395 | 122.8226 | 122.7036 | 122.7997
4147.7031 | 123.0881 | -122.7768 | 0.086975 | -0.02037 | -0.0098843 | -0.076233 | -0.0059109 | -0.031939 | -0.051022 | -0.044451 | -0.0051575 | 0.00082679 | 0.008562 | -0.0067162 | -0.22086 | -0.020051 | -0.020689 | -0.059509 | 0.073242 | -0.082397 | -0.054932 | 0.13275 | -0.068665 | 0.027466 | 0.10986 | 0.086975 | -0.082397 | 0.068665 | 0.17395 | 0.10071 | 0.14648 | 122.6944 | -0.013733 | -0.14191 | 122.9095 | 122.8043 | 122.7081 | 0.10986 | 0.013732 | 122.6944 | 0 | -0.01831 | 122.9507 | 122.9233 | 122.8775 | 0.22888 | 0.18311 | 0.21515 | 0.027465 | 0.25635 | 0.15106 | 0.15564 | 0.16937 | 122.85 | 122.8638 | -0.16937 | -0.16937 | 122.7219 | 122.8455 | 122.7173 | 122.8867
4149.4531 | 123.024 | -122.8317 | 0.11902 | -0.0051118 | -0.010098 | -0.079011 | -0.0052701 | -0.026598 | -0.049954 | -0.039965 | -0.0021057 | 0.00574 | 0.0079212 | -0.0065026 | -0.21937 | -0.020051 | -0.021971 | -0.091553 | 0.11902 | -0.15564 | -0.11902 | 0.036621 | -0.11902 | -0.050354 | 0.022888 | 0.14191 | -0.13275 | 0.004578 | 0.10071 | 0.036621 | 0.086975 | 122.6761 | 0 | -0.23804 | 122.8683 | 122.7814 | 122.7127 | 0.10529 | 0.036621 | 122.699 | 0.022888 | -0.11444 | 122.9324 | 122.9187 | 122.8683 | 0.21973 | 0.16937 | 0.19226 | 0.036621 | 0.23346 | 0.13733 | 0.27466 | 0.27466 | 122.9507 | 122.9736 | -0.27466 | -0.25177 | 122.7127 | 122.8363 | 122.7402 | 122.8546
4151.25 | 123.1018 | -122.7905 | 0.082397 | -0.0051118 | -0.011593 | -0.077942 | -0.0084743 | -0.026598 | -0.050381 | -0.044451 | -0.0021057 | 0.001254 | 0.0079212 | -0.017825 | -0.22107 | -0.020905 | -0.024535 | -0.045776 | 0.064087 | -0.09613 | -0.036621 | 0.13275 | -0.073242 | 0.018311 | 0.10986 | 0.10071 | -0.073242 | 0.09613 | 0.17395 | 0.1236 | 0.14648 | 122.6944 | -0.01831 | -0.11902 | 122.9233 | 122.8088 | 122.7173 | 0.11444 | 0.022888 | 122.7173 | 0.018311 | 0.013733 | 122.9645 | 122.937 | 122.9141 | 0.21973 | 0.19684 | 0.22888 | 0.059509 | 0.24719 | 0.16937 | 0.16022 | 0.17395 | 122.8546 | 122.8912 | -0.17853 | -0.15564 | 122.7539 | 122.8867 | 122.7448 | 122.9004
4152.9844 | 122.9919 | -122.8363 | 0.10529 | -0.012741 | -0.0096707 | -0.079224 | -0.0056973 | -0.031725 | -0.049526 | -0.041033 | -0.0021057 | 0.0038174 | 0.0092028 | -0.013979 | -0.21766 | -0.020051 | -0.02133 | -0.11444 | 0.11902 | -0.12817 | -0.16937 | -0.045776 | -0.20142 | -0.10986 | -0.045776 | 0.1236 | -0.1236 | -0.036621 | 0.036621 | -0.045776 | 0.032043 | 122.7081 | 0.013733 | -0.27466 | 122.7905 | 122.7264 | 122.6349 | 0.018311 | -0.073242 | 122.7127 | 0.01831 | -0.14191 | 122.8729 | 122.8683 | 122.7905 | 0.15564 | 0.07782 | 0.082398 | -0.041199 | 0.16022 | 0.086975 | 0.24719 | 0.24719 | 122.9553 | 122.9599 | -0.23346 | -0.22888 | 122.6669 | 122.7997 | 122.7219 | 122.7905
4154.7656 | 123.0881 | -122.7905 | 0.086975 | -0.0051118 | -0.010311 | -0.078156 | -0.0059109 | -0.028521 | -0.050595 | -0.040819 | -0.0021057 | 0.0031766 | 0.0083484 | -0.013552 | -0.21937 | -0.019837 | -0.019194 | -0.10071 | 0.11444 | -0.14191 | -0.09613 | 0.059509 | -0.10071 | -0.022888 | 0.064087 | 0.11444 | -0.091553 | 0.068665 | 0.16479 | 0.09613 | 0.16022 | 122.6486 | 0.027466 | -0.1831 | 122.85 | 122.7676 | 122.6898 | 0.11902 | 0.041199 | 122.699 | 0.027466 | -0.01831 | 122.9553 | 122.9507 | 122.8867 | 0.25177 | 0.18768 | 0.20142 | 0.045777 | 0.25635 | 0.16022 | 0.25635 | 0.20599 | 122.905 | 122.905 | -0.22888 | -0.17853 | 122.6944 | 122.8592 | 122.6898 | 122.8546
4156.5 | 123.0606 | -122.818 | 0.10529 | -0.0051118 | -0.010952 | -0.079224 | -0.0084743 | -0.025744 | -0.050595 | -0.038683 | 0.00094606 | 0.0014676 | 0.0059986 | -0.017184 | -0.21702 | -0.01941 | -0.021117 | -0.082397 | 0.068665 | -0.091553 | -0.059509 | 0.11902 | -0.10071 | 0 | 0.086975 | 0.10986 | -0.091553 | 0.050354 | 0.12817 | 0.073242 | 0.11902 | 122.7264 | -0.036621 | -0.16479 | 122.937 | 122.818 | 122.7173 | 0.091553 | -0.009155 | 122.7264 | 0.004577 | -0.054932 | 122.9462 | 122.937 | 122.8912 | 0.21057 | 0.16479 | 0.21057 | 0.032044 | 0.21973 | 0.14191 | 0.16022 | 0.20142 | 122.8867 | 122.9279 | -0.19684 | -0.19684 | 122.7585 | 122.8683 | 122.7356 | 122.905
4158.3125 | 123.0652 | -122.8088 | 0.09613 | -0.0051118 | -0.0096707 | -0.079651 | -0.0048427 | -0.024462 | -0.048886 | -0.042742 | 0.00094606 | 0.0055264 | 0.0094166 | -0.014193 | -0.21937 | -0.018128 | -0.02133 | -0.10529 | 0.11444 | -0.14648 | -0.15106 | 0.004578 | -0.17395 | -0.059509 | 0.013733 | 0.11444 | -0.11444 | 0.041199 | 0.11444 | 0.041199 | 0.10986 | 122.6624 | 0.018311 | -0.24719 | 122.8134 | 122.7493 | 122.6349 | 0.086975 | -0.027466 | 122.6944 | 0.018311 | -0.054931 | 122.9233 | 122.9187 | 122.85 | 0.2243 | 0.15564 | 0.15106 | -0.004578 | 0.22888 | 0.15564 | 0.26093 | 0.22888 | 122.9233 | 122.9233 | -0.24261 | -0.21057 | 122.6578 | 122.85 | 122.7036 | 122.8226
4160.1094 | 123.1064 | -122.8043 | 0.09613 | 0.010147 | -0.012875 | -0.080506 | -0.0089017 | -0.035143 | -0.053372 | -0.041887 | -0.0021057 | 0.00018579 | 0.0062122 | -0.015902 | -0.22107 | -0.020051 | -0.023039 | -0.068665 | 0.068665 | -0.091553 | -0.032043 | 0.14191 | -0.004578 | 0.041199 | 0.11902 | 0.09613 | -0.086975 | 0.054932 | 0.20142 | 0.13275 | 0.14191 | 122.7127 | -0.027465 | -0.12817 | 122.9462 | 122.8455 | 122.7997 | 0.13275 | 0.086975 | 122.7173 | 0 | -0.041198 | 123.0057 | 122.9462 | 122.937 | 0.22888 | 0.21973 | 0.23346 | 0.05951 | 0.28839 | 0.14191 | 0.16022 | 0.1831 | 122.8729 | 122.9004 | -0.18768 | -0.1831 | 122.7722 | 122.8592 | 122.7356 | 122.9233
4161.8281 | 123.0743 | -122.8226 | 0.086975 | 0.0025177 | -0.012234 | -0.07837 | -0.0063381 | -0.029802 | -0.051449 | -0.039324 | 0.00094606 | 0.0031766 | 0.0070666 | -0.018679 | -0.21894 | -0.020051 | -0.024535 | -0.059509 | 0.064087 | -0.091553 | -0.064087 | 0.1236 | -0.073242 | 0.009155 | 0.086975 | 0.10071 | -0.086975 | 0.064087 | 0.13275 | 0.082397 | 0.11444 | 122.731 | -0.022888 | -0.15106 | 122.9462 | 122.8317 | 122.7493 | 0.10071 | 0.018311 | 122.7356 | 0.013733 | -0.022888 | 122.9553 | 122.937 | 122.905 | 0.20142 | 0.16937 | 0.21515 | 0.027466 | 0.21973 | 0.15106 | 0.15564 | 0.18768 | 122.8867 | 122.9233 | -0.17853 | -0.17395 | 122.7585 | 122.8867 | 122.7631 | 122.9095
4163.6406 | 122.9782 | -122.8683 | 0.11444 | -0.0051118 | -0.0092435 | -0.076874 | -0.0022793 | -0.030443 | -0.050167 | -0.044023 | -0.0021057 | 0.0048856 | 0.0092028 | -0.011843 | -0.22172 | -0.018982 | -0.019621 | -0.10529 | 0.11902 | -0.13275 | -0.16479 | -0.045776 | -0.19684 | -0.11902 | -0.064087 | 0.14648 | -0.1236 | -0.068665 | 0.009155 | -0.059509 | 0.022888 | 122.7356 | 0.004578 | -0.27924 | 122.8226 | 122.7493 | 122.6715 | 0.013732 | -0.064087 | 122.7448 | 0.032043 | -0.18311 | 122.8775 | 122.8912 | 122.8088 | 0.14648 | 0.064087 | 0.086975 | -0.032044 | 0.13275 | 0.054931 | 0.25177 | 0.27008 | 122.9874 | 123.0148 | -0.24719 | -0.23804 | 122.7036 | 122.7997 | 122.7631 | 122.8043
4165.3906 | 123.024 | -122.8226 | 0.09613 | -0.012741 | -0.012661 | -0.079224 | -0.0069791 | -0.030871 | -0.050808 | -0.043169 | 0.00094606 | 0.0033902 | 0.0081348 | -0.010989 | -0.22065 | -0.021332 | -0.024962 | -0.064087 | 0.10071 | -0.10986 | -0.07782 | 0.09613 | -0.064087 | -0.004578 | 0.032043 | 0.11444 | -0.086975 | -0.004578 | 0.086975 | 0.041199 | 0.064087 | 122.7127 | 0.004578 | -0.17395 | 122.9187 | 122.818 | 122.7585 | 0.10529 | 0.045776 | 122.7356 | 0.018311 | -0.10071 | 122.9095 | 122.8867 | 122.8638 | 0.15106 | 0.12817 | 0.20599 | 0.032043 | 0.17395 | 0.082397 | 0.21057 | 0.20142 | 122.9233 | 122.937 | -0.20599 | -0.1831 | 122.7448 | 122.818 | 122.7585 | 122.8546
4167.1875 | 123.1018 | -122.8088 | 0.086975 | -0.0051118 | -0.015652 | -0.080719 | -0.0099697 | -0.032152 | -0.051449 | -0.039324 | 0.00094606 | -0.00045501 | 0.0066394 | -0.007998 | -0.22001 | -0.021332 | -0.025816 | -0.054932 | 0.073242 | -0.10986 | -0.027466 | 0.16022 | -0.009155 | 0.050354 | 0.12817 | 0.11444 | -0.086975 | 0.073242 | 0.19684 | 0.12817 | 0.13733 | 122.699 | -0.013733 | -0.11444 | 122.9691 | 122.8592 | 122.7997 | 0.16022 | 0.10071 | 122.7219 | 0.027466 | -0.013733 | 123.0057 | 122.9462 | 122.937 | 0.2243 | 0.21515 | 0.27008 | 0.082397 | 0.28381 | 0.16022 | 0.18311 | 0.20142 | 122.8821 | 122.9233 | -0.19684 | -0.17395 | 122.7814 | 122.8821 | 122.7539 | 122.937
4168.9844 | 123.111 | -122.7997 | 0.09613 | 0.0025177 | -0.0096707 | -0.07837 | -0.0054837 | -0.032366 | -0.048672 | -0.04146 | -0.0021057 | 0.0025358 | 0.0049304 | -0.0092798 | -0.22278 | -0.020264 | -0.029662 | -0.064087 | 0.07782 | -0.10071 | -0.054932 | 0.091553 | -0.073242 | 0.009155 | 0.091553 | 0.09613 | -0.082397 | 0.091553 | 0.1831 | 0.10071 | 0.16022 | 122.699 | -0.01831 | -0.15106 | 122.8912 | 122.8088 | 122.7264 | 0.10986 | 0.027466 | 122.7173 | 0 | -0.004577 | 122.9828 | 122.9599 | 122.9004 | 0.24261 | 0.18311 | 0.19226 | 0.045776 | 0.2655 | 0.17395 | 0.17853 | 0.17853 | 122.8775 | 122.8958 | -0.19684 | -0.17853 | 122.7448 | 122.8912 | 122.7356 | 122.8912
4170.7188 | 123.056 | -122.8134 | 0.086975 | 0.0025177 | -0.010311 | -0.080933 | -0.0076199 | -0.029589 | -0.050381 | -0.043596 | 0.00094606 | 0.0023222 | 0.007494 | -0.01697 | -0.21766 | -0.019837 | -0.023467 | -0.068665 | 0.07782 | -0.10071 | -0.068665 | 0.10071 | -0.091553 | 0.004578 | 0.068665 | 0.086975 | -0.086975 | 0.041199 | 0.1236 | 0.082397 | 0.11444 | 122.7127 | -0.009155 | -0.15564 | 122.9141 | 122.818 | 122.7219 | 0.10529 | 0.009155 | 122.7264 | 0 | -0.045776 | 122.937 | 122.9279 | 122.8958 | 0.20142 | 0.16937 | 0.20142 | 0.032043 | 0.21057 | 0.12817 | 0.17853 | 0.17395 | 122.8912 | 122.9004 | -0.18768 | -0.17395 | 122.7448 | 122.8546 | 122.7448 | 122.8821
4172.5156 | 123.1247 | -122.7997 | 0.091553 | 0.0025177 | -0.014584 | -0.079011 | -0.0080471 | -0.031511 | -0.04974 | -0.042955 | -0.0021057 | 0.0027494 | 0.0077076 | -0.014407 | -0.21894 | -0.020051 | -0.023253 | -0.10071 | 0.09613 | -0.12817 | -0.059509 | 0.10529 | -0.036621 | 0.050354 | 0.082397 | 0.091553 | -0.086975 | 0.082397 | 0.19684 | 0.12817 | 0.15564 | 122.6715 | 0.004577 | -0.15106 | 122.905 | 122.85 | 122.7631 | 0.17853 | 0.091553 | 122.7127 | 0 | -0.009156 | 122.9965 | 122.9553 | 122.9279 | 0.24261 | 0.21515 | 0.23346 | 0.068665 | 0.28381 | 0.16937 | 0.2243 | 0.17853 | 122.8958 | 122.8912 | -0.21973 | -0.17853 | 122.7402 | 122.8821 | 122.699 | 122.8821
4174.25 | 122.9782 | -122.8592 | 0.13275 | 0.0025177 | -0.01138 | -0.079011 | -0.0027065 | -0.028307 | -0.050808 | -0.039965 | 0.00094606 | 0.006381 | 0.007494 | -0.011416 | -0.21894 | -0.018769 | -0.02603 | -0.10986 | 0.11902 | -0.13275 | -0.16022 | -0.045776 | -0.18768 | -0.11902 | -0.068665 | 0.14191 | -0.11902 | -0.045776 | 0.018311 | -0.050354 | 0.036621 | 122.7264 | -0.013732 | -0.29297 | 122.8134 | 122.7402 | 122.6715 | 0.013732 | -0.054932 | 122.7402 | 0.009156 | -0.17853 | 122.8775 | 122.8958 | 122.8088 | 0.15564 | 0.068665 | 0.086975 | -0.027466 | 0.13733 | 0.073243 | 0.25177 | 0.26093 | 122.9782 | 123.0011 | -0.2655 | -0.25177 | 122.699 | 122.8134 | 122.7493 | 122.7905
4176.0469 | 123.1201 | -122.7859 | 0.082397 | -0.0051118 | -0.010098 | -0.077942 | -0.0065517 | -0.028948 | -0.04974 | -0.039537 | 0.00094606 | 0.002963 | 0.0066394 | -0.012484 | -0.22001 | -0.019196 | -0.021971 | -0.045776 | 0.07782 | -0.091553 | -0.036621 | 0.11444 | -0.07782 | 0.009155 | 0.10986 | 0.082397 | -0.09613 | 0.10529 | 0.19226 | 0.10529 | 0.15564 | 122.6944 | -0.004577 | -0.11902 | 122.9004 | 122.7951 | 122.7081 | 0.10071 | 0.013733 | 122.6898 | 0 | 0.022889 | 122.9782 | 122.9416 | 122.8912 | 0.25177 | 0.20142 | 0.20599 | 0.054932 | 0.28839 | 0.20142 | 0.16937 | 0.17853 | 122.8638 | 122.8683 | -0.17395 | -0.17853 | 122.7493 | 122.8912 | 122.7402 | 122.8958
4177.8438 | 122.9965 | -122.8729 | 0.1236 | 0.0025177 | -0.0081753 | -0.080079 | -0.0035611 | -0.029802 | -0.052517 | -0.042101 | 0.0039979 | 0.0053128 | 0.0089892 | -0.0065026 | -0.22086 | -0.017914 | -0.022398 | -0.10529 | 0.1236 | -0.15106 | -0.16022 | -0.022888 | -0.18768 | -0.10986 | -0.045776 | 0.14191 | -0.11444 | -0.041199 | 0.032043 | -0.050354 | 0.036621 | 122.7219 | 0 | -0.28381 | 122.85 | 122.7631 | 122.6852 | 0.041199 | -0.036621 | 122.7585 | 0.018311 | -0.16479 | 122.905 | 122.9095 | 122.8226 | 0.15106 | 0.064087 | 0.12817 | -0.009155 | 0.14648 | 0.073242 | 0.27466 | 0.25635 | 122.9965 | 123.0148 | -0.27466 | -0.23804 | 122.7127 | 122.8317 | 122.7676 | 122.8271
4179.5938 | 123.0103 | -122.8683 | 0.11902 | -0.0051118 | -0.0098843 | -0.079224 | -0.0061245 | -0.032793 | -0.049313 | -0.041246 | -0.0021057 | 0.0050992 | 0.008562 | -0.016543 | -0.21894 | -0.018342 | -0.021117 | -0.1236 | 0.1236 | -0.14648 | -0.16937 | -0.036621 | -0.20599 | -0.091553 | -0.041199 | 0.13275 | -0.11902 | -0.022888 | 0.045776 | -0.032043 | 0.045776 | 122.7219 | 0.004577 | -0.28839 | 122.8317 | 122.7768 | 122.6624 | 0.054931 | -0.05951 | 122.7493 | 0.013732 | -0.14191 | 122.9141 | 122.9141 | 122.8363 | 0.16479 | 0.086976 | 0.10986 | -0.022889 | 0.16479 | 0.096131 | 0.27008 | 0.25177 | 122.9919 | 123.0011 | -0.2655 | -0.23804 | 122.699 | 122.8455 | 122.7448 | 122.8271
4181.4062 | 123.0469 | -122.85 | 0.12817 | 0.0025177 | -0.012448 | -0.080079 | -0.0080471 | -0.026384 | -0.050595 | -0.041033 | -0.0021057 | 0.004672 | 0.008562 | -0.013125 | -0.2183 | -0.019837 | -0.02603 | -0.12817 | 0.11902 | -0.14191 | -0.16022 | -0.004578 | -0.13733 | -0.059509 | -0.009155 | 0.13733 | -0.13275 | -0.004578 | 0.10071 | 0.022888 | 0.073242 | 122.7081 | -0.009155 | -0.28839 | 122.8455 | 122.7905 | 122.7127 | 0.082398 | 0.004578 | 122.7173 | 0.009155 | -0.13275 | 122.9507 | 122.9233 | 122.8729 | 0.20599 | 0.15564 | 0.13733 | -0.01831 | 0.23346 | 0.12817 | 0.26093 | 0.27008 | 122.9691 | 122.9874 | -0.27008 | -0.26093 | 122.6898 | 122.8455 | 122.7219 | 122.8409
4183.2031 | 123.1018 | -122.8271 | 0.09613 | 0.0025177 | -0.012661 | -0.080506 | -0.0097561 | -0.030657 | -0.053585 | -0.042101 | 0.0039979 | -0.00024141 | 0.0064258 | -0.015902 | -0.22022 | -0.021546 | -0.029448 | -0.050354 | 0.068665 | -0.10071 | -0.041199 | 0.14648 | -0.022888 | 0.027466 | 0.1236 | 0.10071 | -0.082397 | 0.059509 | 0.19226 | 0.1236 | 0.13733 | 122.7264 | -0.027465 | -0.13733 | 122.9736 | 122.8546 | 122.8043 | 0.12817 | 0.07782 | 122.7448 | 0.004578 | -0.036621 | 123.0194 | 122.9645 | 122.9507 | 0.21973 | 0.20599 | 0.24719 | 0.059509 | 0.27466 | 0.14191 | 0.16937 | 0.18311 | 122.8958 | 122.9279 | -0.19684 | -0.17853 | 122.7859 | 122.8867 | 122.7768 | 122.9507
4185.0156 | 122.9828 | -122.8775 | 0.12817 | -0.0051118 | -0.0092435 | -0.076874 | -0.0056973 | -0.029589 | -0.048245 | -0.039324 | 0.00094606 | 0.0042448 | 0.0092028 | -0.011202 | -0.21979 | -0.018128 | -0.025603 | -0.13733 | 0.1236 | -0.15106 | -0.16937 | -0.059509 | -0.21057 | -0.13275 | -0.086975 | 0.15564 | -0.11444 | -0.032043 | 0.022888 | -0.045776 | 0.059509 | 122.7264 | -0.004578 | -0.29755 | 122.818 | 122.7448 | 122.6669 | 0.018311 | -0.059509 | 122.7631 | 0.027466 | -0.16022 | 122.9004 | 122.937 | 122.8317 | 0.17395 | 0.068665 | 0.091553 | -0.018311 | 0.13733 | 0.082398 | 0.27466 | 0.27008 | 123.0011 | 123.0331 | -0.27924 | -0.24262 | 122.7081 | 122.8455 | 122.7402 | 122.7905
4186.7656 | 123.0011 | -122.8546 | 0.13733 | 0.0025177 | -0.0096707 | -0.079011 | -0.0054837 | -0.025744 | -0.04739 | -0.041887 | -0.0021057 | 0.0040312 | 0.0062122 | -0.0084252 | -0.21851 | -0.017701 | -0.022826 | -0.10071 | 0.1236 | -0.13733 | -0.16022 | 0 | -0.16937 | -0.10986 | -0.041199 | 0.13733 | -0.10986 | -0.050354 | 0.036621 | -0.027466 | 0.041199 | 122.7173 | -0.013733 | -0.29755 | 122.8546 | 122.7448 | 122.6852 | 0.027466 | -0.032044 | 122.7448 | 0 | -0.18768 | 122.8912 | 122.8958 | 122.8271 | 0.15106 | 0.082397 | 0.13733 | -0.022888 | 0.14648 | 0.059509 | 0.26093 | 0.24719 | 122.9782 | 122.9919 | -0.27466 | -0.24719 | 122.6944 | 122.8043 | 122.7539 | 122.8134
4188.5625 | 123.0148 | -122.8409 | 0.11902 | -0.012741 | -0.010311 | -0.078797 | -0.0037747 | -0.029162 | -0.049099 | -0.038683 | -0.0021057 | 0.0036038 | 0.007494 | -0.0082116 | -0.21894 | -0.021332 | -0.021544 | -0.091553 | 0.10529 | -0.12817 | -0.11902 | 0.027466 | -0.11902 | -0.050354 | 0.022888 | 0.1236 | -0.10529 | -0.004578 | 0.073242 | 0.004578 | 0.054932 | 122.7127 | -0.013733 | -0.23804 | 122.8683 | 122.7905 | 122.7219 | 0.07782 | 0.009155 | 122.7356 | 0.004577 | -0.1236 | 122.9141 | 122.8958 | 122.8455 | 0.16022 | 0.10986 | 0.15564 | 0.009155 | 0.17853 | 0.10071 | 0.23346 | 0.22888 | 122.9462 | 122.9645 | -0.24719 | -0.22431 | 122.7219 | 122.8363 | 122.7493 | 122.8638
4190.3125 | 123.0423 | -122.85 | 0.1236 | -0.0051118 | -0.015866 | -0.079438 | -0.0065517 | -0.035357 | -0.051876 | -0.041674 | 0.00094606 | 0.0021084 | 0.0055712 | -0.011843 | -0.21637 | -0.018982 | -0.026457 | -0.13733 | 0.13275 | -0.15106 | -0.17853 | -0.018311 | -0.13733 | -0.073242 | -0.068665 | 0.13733 | -0.1236 | -0.036621 | 0.068665 | 0.004578 | 0.068665 | 122.699 | 0.009155 | -0.30212 | 122.8317 | 122.7768 | 122.7127 | 0.07782 | 0.013733 | 122.7264 | 0.013733 | -0.16022 | 122.9187 | 122.9187 | 122.8546 | 0.19226 | 0.12817 | 0.13275 | -0.027466 | 0.19226 | 0.086975 | 0.28381 | 0.26093 | 122.9828 | 122.9874 | -0.27466 | -0.24719 | 122.6715 | 122.8134 | 122.7127 | 122.7814
4192.1094 | 123.1293 | -122.8546 | 0.086975 | 0.0025177 | -0.015225 | -0.080292 | -0.0067653 | -0.031298 | -0.05209 | -0.043169 | -0.0051575 | 0.0027494 | 0.0062122 | -0.014193 | -0.21915 | -0.020478 | -0.021544 | -0.073242 | 0.082397 | -0.10529 | -0.027466 | 0.17853 | 0.004578 | 0.064087 | 0.1236 | 0.10986 | -0.07782 | 0.07782 | 0.21973 | 0.15106 | 0.15106 | 122.7493 | -0.004578 | -0.11444 | 123.0331 | 122.9187 | 122.8592 | 0.16937 | 0.10986 | 122.7768 | 0.022888 | -0.009155 | 123.0743 | 123.0057 | 123.0057 | 0.22888 | 0.22888 | 0.28381 | 0.07782 | 0.29755 | 0.15564 | 0.18768 | 0.18768 | 122.937 | 122.9645 | -0.19226 | -0.16479 | 122.8271 | 122.9324 | 122.7814 | 122.9782
4193.9062 | 123.1338 | -122.8088 | 0.086975 | -0.012741 | -0.0071073 | -0.079224 | -0.0071927 | -0.027453 | -0.048031 | -0.042528 | -0.0021057 | 0.0016812 | 0.007494 | -0.018038 | -0.22129 | -0.019837 | -0.029662 | -0.050354 | 0.068665 | -0.07782 | -0.032043 | 0.12817 | -0.068665 | 0.018311 | 0.13275 | 0.10071 | -0.07782 | 0.086975 | 0.16479 | 0.1236 | 0.15106 | 122.731 | -0.01831 | -0.11902 | 122.937 | 122.8271 | 122.7402 | 0.096131 | 0.009155 | 122.731 | 0.013733 | 0 | 122.9736 | 122.9599 | 122.9324 | 0.22888 | 0.20142 | 0.20599 | 0.045777 | 0.24261 | 0.16479 | 0.14649 | 0.17853 | 122.8775 | 122.9095 | -0.16479 | -0.16479 | 122.7768 | 122.8958 | 122.7585 | 122.9416
4195.6562 | 122.9965 | -122.8592 | 0.13275 | -0.0051118 | -0.0092435 | -0.078797 | -0.0029201 | -0.030871 | -0.049526 | -0.038469 | -0.0021057 | 0.0036038 | 0.007494 | -0.0090662 | -0.22406 | -0.019837 | -0.023253 | -0.11902 | 0.11902 | -0.14648 | -0.16937 | -0.041199 | -0.19684 | -0.11902 | -0.059509 | 0.13733 | -0.11902 | -0.054932 | 0.009155 | -0.045776 | 0.036621 | 122.7127 | -0.013732 | -0.30212 | 122.818 | 122.7402 | 122.6624 | 0.027465 | -0.050354 | 122.7402 | 0.004578 | -0.18768 | 122.8683 | 122.8958 | 122.8134 | 0.15564 | 0.073243 | 0.10529 | -0.022889 | 0.12817 | 0.064087 | 0.2655 | 0.25635 | 122.9782 | 122.9965 | -0.27924 | -0.25177 | 122.6898 | 122.8043 | 122.7402 | 122.7997
4197.4375 | 123.0331 | -122.8134 | 0.11902 | -0.0051118 | -0.01202 | -0.078797 | -0.0059109 | -0.030871 | -0.048245 | -0.039751 | 0.00094606 | 0.0023222 | 0.0072802 | -0.015688 | -0.21787 | -0.020478 | -0.02603 | -0.086975 | 0.11902 | -0.13733 | -0.09613 | 0.045776 | -0.13275 | -0.054932 | 0.036621 | 0.11902 | -0.10986 | -0.004578 | 0.064087 | -0.004578 | 0.064087 | 122.6761 | 0 | -0.21515 | 122.8592 | 122.7585 | 122.6807 | 0.082397 | 0.004578 | 122.7036 | 0 | -0.1236 | 122.8775 | 122.8775 | 122.8088 | 0.17395 | 0.10529 | 0.18311 | 0.041199 | 0.17395 | 0.10529 | 0.25635 | 0.22888 | 122.9324 | 122.9324 | -0.25635 | -0.22888 | 122.7173 | 122.8088 | 122.7264 | 122.85
4199.1719 | 123.0927 | -122.8317 | 0.10986 | -0.0051118 | -0.013089 | -0.079438 | -0.0089017 | -0.030657 | -0.04974 | -0.041887 | -0.0021057 | 0.001254 | 0.006853 | -0.016543 | -0.22086 | -0.01941 | -0.024748 | -0.10529 | 0.09613 | -0.10529 | -0.091553 | 0.082397 | -0.10529 | 0 | 0.041199 | 0.09613 | -0.082397 | 0.013733 | 0.13275 | 0.07782 | 0.11902 | 122.7264 | -0.013733 | -0.20142 | 122.9141 | 122.8317 | 122.7264 | 0.10529 | 0 | 122.7493 | -0.013733 | -0.09613 | 122.9645 | 122.9507 | 122.9095 | 0.20142 | 0.16022 | 0.18768 | 0.013733 | 0.21515 | 0.09613 | 0.20142 | 0.17853 | 122.9279 | 122.9279 | -0.21515 | -0.19226 | 122.7402 | 122.8455 | 122.7264 | 122.8729
4200.9062 | 123.0515 | -122.8592 | 0.10529 | -0.012741 | -0.012234 | -0.076661 | -0.0065517 | -0.030016 | -0.050381 | -0.040819 | 0.00094606 | 0.0059538 | 0.0077076 | -0.009707 | -0.21915 | -0.016633 | -0.024748 | -0.082397 | 0.10071 | -0.13275 | -0.11902 | 0.045776 | -0.11902 | -0.054932 | 0.027466 | 0.13733 | -0.09613 | 0.013733 | 0.10529 | 0.032043 | 0.091553 | 122.7264 | -0.004578 | -0.22431 | 122.905 | 122.8043 | 122.7402 | 0.077819 | 0.013732 | 122.7631 | 0.032043 | -0.091553 | 122.9645 | 122.9507 | 122.8912 | 0.18768 | 0.12817 | 0.17853 | 0.013732 | 0.20142 | 0.10986 | 0.23346 | 0.23346 | 122.9599 | 122.9965 | -0.23804 | -0.20142 | 122.7402 | 122.8729 | 122.7768 | 122.8867
4202.7031 | 123.0286 | -122.8775 | 0.10529 | 0.0025177 | -0.013089 | -0.077515 | -0.0089017 | -0.031939 | -0.050381 | -0.041246 | -0.0051575 | 0.0021084 | 0.0083484 | -0.0088526 | -0.21894 | -0.020691 | -0.020049 | -0.1236 | 0.10986 | -0.13275 | -0.16479 | 0.022888 | -0.1236 | -0.059509 | -0.036621 | 0.15106 | -0.13275 | -0.059509 | 0.059509 | 0 | 0.036621 | 122.7448 | 0.004577 | -0.27008 | 122.9004 | 122.818 | 122.7539 | 0.073242 | 0.009155 | 122.7448 | 0.045776 | -0.16479 | 122.937 | 122.9141 | 122.8775 | 0.16937 | 0.13275 | 0.15564 | -0.032044 | 0.19226 | 0.073242 | 0.24261 | 0.28381 | 122.9874 | 123.0286 | -0.23804 | -0.23804 | 122.7127 | 122.818 | 122.7539 | 122.8409
4204.5 | 123.0927 | -122.8638 | 0.10529 | -0.0051118 | -0.013729 | -0.080079 | -0.0067653 | -0.029589 | -0.051449 | -0.042314 | -0.0021057 | -0.00066861 | 0.0081348 | -0.015688 | -0.22043 | -0.020051 | -0.024321 | -0.10986 | 0.091553 | -0.11902 | -0.11444 | 0.064087 | -0.10071 | -0.009155 | 0.022888 | 0.09613 | -0.10529 | 0.013733 | 0.13733 | 0.068665 | 0.11902 | 122.7448 | -0.013733 | -0.21973 | 122.9279 | 122.8546 | 122.7631 | 0.10986 | 0.018311 | 122.7585 | -0.009156 | -0.091553 | 123.0011 | 122.9828 | 122.9324 | 0.22431 | 0.17395 | 0.18311 | 0.004578 | 0.24262 | 0.11902 | 0.21057 | 0.20142 | 122.9553 | 122.9599 | -0.22431 | -0.21057 | 122.7493 | 122.8775 | 122.7539 | 122.8867
4206.2344 | 123.024 | -122.8867 | 0.1236 | 0.010147 | -0.011593 | -0.079224 | -0.0048427 | -0.031939 | -0.052944 | -0.040178 | 0.00094606 | 0.002963 | 0.0077076 | -0.013552 | -0.21851 | -0.019623 | -0.020049 | -0.13275 | 0.11444 | -0.15106 | -0.16937 | -0.013733 | -0.14191 | -0.073242 | -0.045776 | 0.14648 | -0.1236 | -0.059509 | 0.050354 | -0.009155 | 0.050354 | 122.7356 | -0.009155 | -0.29297 | 122.8729 | 122.8134 | 122.7448 | 0.07782 | 0.009155 | 122.7631 | 0.022888 | -0.1831 | 122.937 | 122.937 | 122.8775 | 0.17395 | 0.11444 | 0.13733 | -0.018311 | 0.17395 | 0.064087 | 0.2655 | 0.27008 | 123.0011 | 123.0331 | -0.27466 | -0.24719 | 122.7173 | 122.8271 | 122.7539 | 122.8409
4208.0312 | 123.0286 | -122.8683 | 0.14191 | -0.0051118 | -0.013302 | -0.079011 | -0.0069791 | -0.031939 | -0.052304 | -0.040392 | -0.0021057 | 0.0023222 | 0.0077076 | -0.012484 | -0.21894 | -0.02176 | -0.021971 | -0.13275 | 0.13275 | -0.15564 | -0.17395 | -0.022888 | -0.14191 | -0.073242 | -0.050354 | 0.14648 | -0.11902 | -0.050354 | 0.054932 | -0.013733 | 0.041199 | 122.7127 | -0.009156 | -0.31586 | 122.8455 | 122.7951 | 122.7264 | 0.082398 | 0.013733 | 122.7493 | 0.004577 | -0.19226 | 122.9233 | 122.9095 | 122.8546 | 0.16022 | 0.10529 | 0.13275 | -0.01831 | 0.17395 | 0.068665 | 0.28839 | 0.2655 | 123.0011 | 123.0148 | -0.29755 | -0.26093 | 122.6944 | 122.818 | 122.7356 | 122.818
4209.8438 | 123.056 | -122.8683 | 0.10529 | -0.0051118 | -0.010098 | -0.077088 | -0.0061245 | -0.028307 | -0.051235 | -0.042528 | 0.0039979 | 0.0027494 | 0.006853 | -0.013125 | -0.22001 | -0.019623 | -0.023467 | -0.11902 | 0.12817 | -0.13733 | -0.16022 | -0.013733 | -0.1831 | -0.09613 | -0.018311 | 0.12817 | -0.10986 | 0 | 0.07782 | 0.009155 | 0.082397 | 122.731 | 0.022888 | -0.2655 | 122.8546 | 122.7722 | 122.6852 | 0.041199 | -0.045776 | 122.7585 | 0.022888 | -0.10529 | 122.9462 | 122.9507 | 122.8775 | 0.19226 | 0.11902 | 0.1236 | -0.022888 | 0.18768 | 0.10986 | 0.2655 | 0.23804 | 122.9965 | 122.9965 | -0.24262 | -0.21515 | 122.7081 | 122.8683 | 122.7493 | 122.85
4211.5781 | 123.0698 | -122.8592 | 0.12817 | -0.0051118 | -0.016293 | -0.077088 | -0.0059109 | -0.026812 | -0.050595 | -0.039324 | -0.0051575 | 0.0038174 | 0.0092028 | -0.015475 | -0.22001 | -0.020478 | -0.025389 | -0.13275 | 0.12817 | -0.13733 | -0.14191 | 0 | -0.14648 | -0.068665 | -0.032043 | 0.14191 | -0.13733 | -0.013733 | 0.086975 | 0.018311 | 0.082397 | 122.7219 | 0 | -0.27008 | 122.8592 | 122.7905 | 122.7127 | 0.068664 | -0.009155 | 122.7219 | 0.013733 | -0.14191 | 122.9462 | 122.9416 | 122.8775 | 0.21973 | 0.15564 | 0.13733 | -0.004578 | 0.2243 | 0.1236 | 0.2655 | 0.27924 | 122.9874 | 123.0011 | -0.2655 | -0.2655 | 122.7173 | 122.8455 | 122.7264 | 122.8271
4213.3594 | 123.0469 | -122.8683 | 0.13733 | -0.012741 | -0.010525 | -0.080506 | -0.0074063 | -0.02553 | -0.051235 | -0.043169 | -0.0021057 | 0.0027494 | 0.0070666 | -0.0082116 | -0.21872 | -0.020264 | -0.020476 | -0.11902 | 0.1236 | -0.13733 | -0.16479 | -0.009155 | -0.13733 | -0.064087 | -0.041199 | 0.14191 | -0.11902 | -0.027466 | 0.07782 | 0.022888 | 0.068665 | 122.731 | -0.013733 | -0.30212 | 122.8592 | 122.8043 | 122.731 | 0.073242 | 0 | 122.7493 | 0.004578 | -0.16479 | 122.9462 | 122.937 | 122.8912 | 0.18768 | 0.14191 | 0.12817 | -0.027466 | 0.19684 | 0.091553 | 0.26093 | 0.26093 | 122.9919 | 123.0103 | -0.27466 | -0.25635 | 122.7036 | 122.8409 | 122.7493 | 122.8271
4215.1562 | 123.0469 | -122.8958 | 0.11444 | 0.010147 | -0.01202 | -0.080079 | -0.0063381 | -0.032793 | -0.051022 | -0.042528 | -0.0021057 | 0.0016812 | 0.0087756 | -0.010775 | -0.21894 | -0.01941 | -0.023039 | -0.10986 | 0.1236 | -0.13733 | -0.16937 | -0.022888 | -0.12817 | -0.086975 | -0.036621 | 0.14191 | -0.13733 | -0.027466 | 0.091553 | 0.018311 | 0.07782 | 122.7585 | 0.009155 | -0.28381 | 122.8729 | 122.8088 | 122.7676 | 0.050354 | 0.009155 | 122.7585 | 0.027466 | -0.14191 | 122.9874 | 122.9736 | 122.9141 | 0.21515 | 0.15564 | 0.11444 | -0.032044 | 0.22888 | 0.10986 | 0.26093 | 0.27924 | 123.0194 | 123.0377 | -0.25177 | -0.25177 | 122.7264 | 122.8683 | 122.7859 | 122.8592
4216.9531 | 123.024 | -122.8912 | 0.13275 | 0.0025177 | -0.012875 | -0.082215 | -0.0074063 | -0.02553 | -0.052731 | -0.040819 | -0.0021057 | 0.0023222 | 0.0092028 | -0.016116 | -0.21872 | -0.021119 | -0.022826 | -0.10986 | 0.10986 | -0.11902 | -0.13275 | 0.036621 | -0.1236 | -0.050354 | -0.032043 | 0.14648 | -0.10529 | -0.054932 | 0.064087 | 0.009155 | 0.032043 | 122.7722 | -0.022888 | -0.2655 | 122.9279 | 122.8409 | 122.7676 | 0.068665 | -0.004577 | 122.7859 | 0.013733 | -0.18768 | 122.9553 | 122.9233 | 122.9004 | 0.13733 | 0.11444 | 0.15564 | -0.013732 | 0.16937 | 0.050354 | 0.22888 | 0.25177 | 123.0011 | 123.0377 | -0.25177 | -0.23804 | 122.7585 | 122.8363 | 122.7814 | 122.8592
4218.75 | 123.1338 | -122.8317 | 0.082397 | 0.0025177 | -0.011807 | -0.077088 | -0.0076199 | -0.023607 | -0.048886 | -0.04146 | -0.0021057 | 0.001254 | 0.0064258 | -0.01697 | -0.21894 | -0.01941 | -0.024748 | -0.050354 | 0.064087 | -0.09613 | -0.032043 | 0.13275 | -0.068665 | 0.013733 | 0.14191 | 0.091553 | -0.091553 | 0.086975 | 0.1831 | 0.10529 | 0.13733 | 122.7356 | -0.01831 | -0.11444 | 122.9645 | 122.8455 | 122.7631 | 0.10986 | 0.027465 | 122.7402 | 0.009156 | 0.004578 | 123.0148 | 122.9691 | 122.937 | 0.22888 | 0.19684 | 0.22888 | 0.064087 | 0.27466 | 0.17853 | 0.16022 | 0.18311 | 122.8958 | 122.9233 | -0.17853 | -0.17395 | 122.7997 | 122.9187 | 122.7814 | 122.9736
4220.5625 | 123.143 | -122.8363 | 0.068665 | -0.0051118 | -0.010739 | -0.077729 | -0.0074063 | -0.026171 | -0.051235 | -0.039965 | -0.0051575 | 0.00082679 | 0.0089892 | -0.014193 | -0.2183 | -0.020264 | -0.023253 | -0.032043 | 0.082397 | -0.082397 | -0.041199 | 0.14191 | -0.07782 | 0.018311 | 0.12817 | 0.10071 | -0.068665 | 0.09613 | 0.17395 | 0.11902 | 0.16022 | 122.7539 | 0.013732 | -0.10986 | 122.9782 | 122.8546 | 122.7585 | 0.10071 | 0.004577 | 122.7676 | 0.032043 | 0.027465 | 123.0103 | 122.9965 | 122.9553 | 0.22888 | 0.18768 | 0.2243 | 0.041198 | 0.24261 | 0.16479 | 0.16479 | 0.16937 | 122.9187 | 122.937 | -0.15106 | -0.13733 | 122.7951 | 122.9324 | 122.8043 | 122.9645
4222.2969 | 123.0286 | -122.8912 | 0.1236 | 0.0025177 | -0.013729 | -0.08136 | -0.0074063 | -0.034716 | -0.052304 | -0.044237 | -0.0021057 | 0.00082679 | 0.0079212 | -0.013552 | -0.21937 | -0.018982 | -0.022185 | -0.11444 | 0.09613 | -0.1236 | -0.15564 | 0.027466 | -0.13275 | -0.064087 | -0.045776 | 0.16022 | -0.1236 | -0.054932 | 0.059509 | 0.009155 | 0.045776 | 122.7676 | -0.027466 | -0.27924 | 122.9187 | 122.8271 | 122.7585 | 0.059509 | -0.009155 | 122.7676 | 0.036621 | -0.17853 | 122.9507 | 122.937 | 122.9004 | 0.16937 | 0.13275 | 0.15106 | -0.032044 | 0.1831 | 0.068664 | 0.21973 | 0.28381 | 122.9874 | 123.0515 | -0.24719 | -0.24719 | 122.7356 | 122.8363 | 122.7768 | 122.8455
4224.0625 | 123.1155 | -122.8546 | 0.10529 | -0.0051118 | -0.015438 | -0.078797 | -0.0076199 | -0.033434 | -0.051663 | -0.041674 | -0.0021057 | -2.7806e-05 | 0.0092028 | -0.013766 | -0.21851 | -0.018982 | -0.025816 | -0.09613 | 0.082397 | -0.11444 | -0.091553 | 0.068665 | -0.086975 | 0 | 0.041199 | 0.10071 | -0.10071 | 0.036621 | 0.14191 | 0.086975 | 0.1236 | 122.7402 | -0.022889 | -0.19684 | 122.9233 | 122.8546 | 122.7676 | 0.11444 | 0.027466 | 122.7539 | -0.004578 | -0.068665 | 122.9965 | 122.9782 | 122.9416 | 0.2243 | 0.18768 | 0.18311 | 0.022888 | 0.24262 | 0.13733 | 0.19684 | 0.20142 | 122.937 | 122.9553 | -0.21973 | -0.20599 | 122.7631 | 122.8912 | 122.7585 | 122.8958
4225.8125 | 123.024 | -122.8821 | 0.11902 | -0.0051118 | -0.014157 | -0.079651 | -0.0069791 | -0.031725 | -0.053585 | -0.041887 | 0.0039979 | 0.0027494 | 0.0079212 | -0.01462 | -0.22001 | -0.020264 | -0.02133 | -0.14191 | 0.1236 | -0.14191 | -0.17395 | -0.022888 | -0.16022 | -0.07782 | -0.041199 | 0.14191 | -0.1236 | -0.045776 | 0.041199 | -0.018311 | 0.032043 | 122.7402 | 0.004577 | -0.29297 | 122.8592 | 122.8043 | 122.7219 | 0.064087 | -0.01831 | 122.7585 | 0.022888 | -0.16479 | 122.9233 | 122.9141 | 122.8638 | 0.15564 | 0.10528 | 0.11902 | -0.032043 | 0.16479 | 0.07782 | 0.2655 | 0.2655 | 123.0057 | 123.024 | -0.26093 | -0.24261 | 122.7081 | 122.8363 | 122.7402 | 122.8409
4227.6094 | 123.0057 | -122.9095 | 0.11444 | 0.0025177 | -0.010952 | -0.080933 | -0.0052701 | -0.027239 | -0.050167 | -0.044237 | -0.0051575 | 0.00574 | 0.010271 | -0.010775 | -0.21937 | -0.019623 | -0.024107 | -0.12817 | 0.11902 | -0.1236 | -0.16937 | -0.050354 | -0.19226 | -0.11444 | -0.073242 | 0.12817 | -0.11444 | -0.036621 | 0.018311 | -0.050354 | 0.045776 | 122.7859 | 0.004578 | -0.28381 | 122.8592 | 122.7951 | 122.7173 | 0.009155 | -0.068665 | 122.7951 | 0.013733 | -0.15106 | 122.9279 | 122.9553 | 122.8592 | 0.16022 | 0.064087 | 0.073242 | -0.045777 | 0.13275 | 0.07782 | 0.24261 | 0.24262 | 123.0286 | 123.0377 | -0.23804 | -0.22888 | 122.7402 | 122.8729 | 122.7814 | 122.8363
4229.3438 | 123.0148 | -122.8912 | 0.12817 | -0.0051118 | -0.016079 | -0.081788 | -0.0059109 | -0.031298 | -0.052517 | -0.043383 | -0.0021057 | 0.0036038 | 0.0081348 | -0.011843 | -0.21744 | -0.01941 | -0.021117 | -0.15106 | 0.1236 | -0.15564 | -0.16937 | -0.013733 | -0.12817 | -0.064087 | -0.064087 | 0.15564 | -0.12817 | -0.073242 | 0.036621 | -0.022888 | 0.032043 | 122.7356 | -0.004578 | -0.29755 | 122.8775 | 122.8271 | 122.7631 | 0.091553 | 0.027466 | 122.7631 | 0.027466 | -0.20142 | 122.9279 | 122.9233 | 122.8683 | 0.16022 | 0.10529 | 0.14191 | -0.013733 | 0.1648 | 0.054932 | 0.27924 | 0.28381 | 123.0148 | 123.0469 | -0.28381 | -0.25635 | 122.7219 | 122.818 | 122.7402 | 122.8271
4231.125 | 123.1476 | -122.8455 | 0.11444 | -0.02037 | -0.016079 | -0.080506 | -0.0078335 | -0.031939 | -0.051663 | -0.041674 | -0.0021057 | 0.00061319 | 0.0053576 | -0.015048 | -0.22043 | -0.020905 | -0.025389 | -0.064087 | 0.064087 | -0.10529 | -0.018311 | 0.14648 | -0.013733 | 0.036621 | 0.10071 | 0.10986 | -0.086975 | 0.086975 | 0.19226 | 0.12817 | 0.1236 | 122.7402 | -0.050354 | -0.13275 | 122.9919 | 122.8821 | 122.8317 | 0.14191 | 0.091553 | 122.7585 | -0.004578 | -0.027466 | 123.0377 | 122.9691 | 122.9736 | 0.21057 | 0.21515 | 0.25177 | 0.086975 | 0.27924 | 0.17395 | 0.16937 | 0.19684 | 122.9095 | 122.9553 | -0.21973 | -0.20142 | 122.8271 | 122.9324 | 122.7814 | 122.9462
4232.9219 | 123.143 | -122.8363 | 0.082397 | -0.0051118 | -0.011593 | -0.078156 | -0.0052701 | -0.028734 | -0.049099 | -0.042528 | 0.00094606 | 0.0016812 | 0.0098438 | -0.016543 | -0.22001 | -0.020051 | -0.025816 | -0.073242 | 0.068665 | -0.1236 | -0.064087 | 0.09613 | -0.091553 | 0.004578 | 0.10071 | 0.086975 | -0.073242 | 0.086975 | 0.16937 | 0.09613 | 0.16479 | 122.7127 | -0.013732 | -0.14648 | 122.9324 | 122.8409 | 122.7448 | 0.12817 | 0.032043 | 122.7631 | 0.004578 | 0.004578 | 123.0057 | 123.0011 | 122.9324 | 0.23804 | 0.16937 | 0.21973 | 0.059509 | 0.24261 | 0.16022 | 0.19226 | 0.16022 | 122.905 | 122.9233 | -0.20599 | -0.15564 | 122.7722 | 122.9233 | 122.7631 | 122.937
4234.7031 | 123.0972 | -122.8455 | 0.09613 | 0.0025177 | -0.010739 | -0.079438 | -0.0078335 | -0.024675 | -0.048245 | -0.042101 | -0.0021057 | 0.0025358 | 0.0079212 | -0.015261 | -0.21872 | -0.0224 | -0.021544 | -0.082397 | 0.064087 | -0.09613 | -0.054932 | 0.1236 | -0.073242 | 0.009155 | 0.10986 | 0.10529 | -0.068665 | 0.050354 | 0.14191 | 0.068665 | 0.1236 | 122.7493 | -0.032043 | -0.15106 | 122.9691 | 122.8546 | 122.7722 | 0.10528 | 0.022888 | 122.7768 | 0.009156 | -0.045776 | 122.9874 | 122.9691 | 122.9141 | 0.19226 | 0.13733 | 0.21973 | 0.041198 | 0.21057 | 0.11902 | 0.16022 | 0.17395 | 122.9095 | 122.9507 | -0.19226 | -0.16479 | 122.7905 | 122.8958 | 122.7631 | 122.9553
4236.5 | 123.0286 | -122.8958 | 0.13275 | 0.010147 | -0.013089 | -0.079865 | -0.0063381 | -0.03322 | -0.052731 | -0.041033 | -0.0021057 | 0.0040312 | 0.0072802 | -0.0086388 | -0.21851 | -0.023255 | -0.020689 | -0.15106 | 0.11902 | -0.15564 | -0.16479 | -0.018311 | -0.14191 | -0.073242 | -0.041199 | 0.12817 | -0.11444 | -0.059509 | 0.032043 | -0.013733 | 0.050354 | 122.7402 | -0.013732 | -0.29755 | 122.8775 | 122.8226 | 122.7539 | 0.082398 | 0.013733 | 122.7814 | -0.004577 | -0.19226 | 122.9279 | 122.9462 | 122.8821 | 0.16479 | 0.10071 | 0.13733 | -0.009155 | 0.14648 | 0.054932 | 0.27466 | 0.24262 | 123.0148 | 123.024 | -0.28839 | -0.24719 | 122.731 | 122.8363 | 122.7448 | 122.8546
4238.2969 | 123.0377 | -122.8729 | 0.10986 | -0.0051118 | -0.012661 | -0.077515 | -0.0037747 | -0.025744 | -0.049313 | -0.040605 | -0.0051575 | 0.0038174 | 0.0059986 | -0.017611 | -0.21894 | -0.019623 | -0.024962 | -0.12817 | 0.1236 | -0.14648 | -0.1831 | -0.032043 | -0.19684 | -0.086975 | -0.022888 | 0.14191 | -0.1236 | -0.018311 | 0.045776 | -0.027466 | 0.064087 | 122.7264 | 0.013733 | -0.29297 | 122.8409 | 122.7859 | 122.6761 | 0.059509 | -0.050354 | 122.7493 | 0.032044 | -0.12817 | 122.9187 | 122.937 | 122.8455 | 0.18768 | 0.09613 | 0.11444 | -0.036621 | 0.16937 | 0.10528 | 0.27008 | 0.2655 | 122.9965 | 123.0148 | -0.25635 | -0.23346 | 122.6898 | 122.8546 | 122.7448 | 122.85
4240.0312 | 123.0423 | -122.8775 | 0.12817 | 0.0025177 | -0.010739 | -0.079011 | -0.0037747 | -0.024248 | -0.048245 | -0.042955 | 0.0039979 | 0.002963 | 0.0089892 | -0.0099206 | -0.21872 | -0.018555 | -0.024535 | -0.1236 | 0.11902 | -0.14191 | -0.17395 | -0.032043 | -0.19226 | -0.10071 | -0.027466 | 0.11444 | -0.12817 | -0.027466 | 0.036621 | -0.027466 | 0.050354 | 122.7356 | -0.009155 | -0.30212 | 122.8455 | 122.7768 | 122.6852 | 0.041199 | -0.050354 | 122.7493 | -0.013733 | -0.15564 | 122.9141 | 122.9279 | 122.85 | 0.17853 | 0.10071 | 0.10986 | -0.032043 | 0.1648 | 0.10071 | 0.26093 | 0.24262 | 122.9965 | 122.9919 | -0.27008 | -0.25635 | 122.7036 | 122.85 | 122.7539 | 122.85
4241.8281 | 123.0835 | -122.8958 | 0.1236 | -0.0051118 | -0.012234 | -0.079224 | -0.0046291 | -0.02553 | -0.049526 | -0.041246 | -0.0021057 | 0.0038174 | 0.0081348 | -0.012057 | -0.21766 | -0.018769 | -0.025389 | -0.11902 | 0.11444 | -0.14191 | -0.15564 | -0.009155 | -0.13275 | -0.059509 | -0.027466 | 0.13275 | -0.12817 | -0.004578 | 0.086975 | 0.022888 | 0.073242 | 122.7539 | -0.009155 | -0.27924 | 122.8867 | 122.8363 | 122.7631 | 0.082398 | 0.009156 | 122.7676 | 0.009155 | -0.12817 | 122.9828 | 122.9691 | 122.9187 | 0.20142 | 0.15106 | 0.13275 | -0.013733 | 0.21515 | 0.1236 | 0.25635 | 0.26093 | 123.0103 | 123.0286 | -0.2655 | -0.25177 | 122.7402 | 122.8912 | 122.7768 | 122.8683
4243.625 | 123.1201 | -122.85 | 0.09613 | -0.0051118 | -0.0090299 | -0.078156 | -0.0084743 | -0.028734 | -0.049526 | -0.04381 | 0.00094606 | 0.00061319 | 0.008562 | -0.0075708 | -0.21872 | -0.019196 | -0.024962 | -0.064087 | 0.068665 | -0.082397 | -0.059509 | 0.13733 | -0.068665 | 0.013733 | 0.11902 | 0.082397 | -0.091553 | 0.082397 | 0.17395 | 0.09613 | 0.15106 | 122.7676 | -0.027465 | -0.15564 | 122.9874 | 122.8638 | 122.7814 | 0.09613 | 0.013732 | 122.7585 | -0.013733 | -0.013733 | 123.024 | 123.0011 | 122.9462 | 0.24261 | 0.18768 | 0.21973 | 0.022888 | 0.2655 | 0.17395 | 0.15106 | 0.17395 | 122.9187 | 122.9324 | -0.17853 | -0.18768 | 122.7905 | 122.9324 | 122.7859 | 122.9691
4245.4375 | 123.1064 | -122.8271 | 0.091553 | -0.0051118 | -0.013516 | -0.078156 | -0.0074063 | -0.033007 | -0.049526 | -0.040392 | 0.00094606 | 0.001254 | 0.0064258 | -0.017611 | -0.21872 | -0.021119 | -0.019621 | -0.091553 | 0.073242 | -0.091553 | -0.068665 | 0.11444 | -0.07782 | -0.009155 | 0.068665 | 0.091553 | -0.082397 | 0.032043 | 0.1236 | 0.082397 | 0.13275 | 122.7356 | -0.018311 | -0.16022 | 122.9416 | 122.818 | 122.7493 | 0.082398 | 0.013733 | 122.7448 | 0 | -0.05951 | 122.9507 | 122.9599 | 122.9095 | 0.21515 | 0.16479 | 0.20599 | 0.022888 | 0.20599 | 0.11444 | 0.16479 | 0.17395 | 122.9004 | 122.9187 | -0.18311 | -0.17395 | 122.7585 | 122.8592 | 122.7356 | 122.8958
4247.2344 | 123.1567 | -122.8271 | 0.091553 | -0.012741 | -0.011807 | -0.076874 | -0.0078335 | -0.02788 | -0.049954 | -0.039324 | 0.00094606 | 0.00082679 | 0.0072802 | -0.015048 | -0.2215 | -0.020051 | -0.02368 | -0.041199 | 0.073242 | -0.086975 | -0.027466 | 0.1236 | -0.073242 | 0.018311 | 0.1236 | 0.082397 | -0.059509 | 0.091553 | 0.17853 | 0.11902 | 0.15106 | 122.7402 | -0.018311 | -0.11902 | 122.9507 | 122.8455 | 122.7539 | 0.10529 | 0.013733 | 122.7676 | -0.009156 | 0 | 123.0057 | 122.9782 | 122.9462 | 0.21057 | 0.17853 | 0.21057 | 0.059509 | 0.23804 | 0.15106 | 0.16022 | 0.14191 | 122.9004 | 122.9095 | -0.17853 | -0.15106 | 122.7997 | 122.9187 | 122.7859 | 122.9507
4248.9688 | 123.0972 | -122.8683 | 0.10986 | -0.0051118 | -0.013729 | -0.080079 | -0.0095425 | -0.033007 | -0.051022 | -0.042742 | 0.00094606 | 0.0036038 | 0.008562 | -0.012698 | -0.21958 | -0.021332 | -0.022612 | -0.073242 | 0.073242 | -0.10071 | -0.068665 | 0.10986 | -0.032043 | 0.027466 | 0.064087 | 0.1236 | -0.091553 | 0.013733 | 0.11902 | 0.064087 | 0.10529 | 122.7676 | -0.036621 | -0.17853 | 122.9782 | 122.8958 | 122.8363 | 0.12817 | 0.068665 | 122.7768 | 0.013733 | -0.09613 | 122.9874 | 122.9736 | 122.9324 | 0.19684 | 0.15564 | 0.21057 | 0.032043 | 0.21057 | 0.10529 | 0.17395 | 0.21515 | 122.9416 | 122.9919 | -0.21057 | -0.20142 | 122.7997 | 122.8821 | 122.7951 | 122.9324
4250.7656 | 123.0423 | -122.905 | 0.12817 | 0.0025177 | -0.014584 | -0.079651 | -0.0080471 | -0.030016 | -0.04974 | -0.041033 | 0.00094606 | 0.004672 | 0.005785 | -0.012698 | -0.21915 | -0.020691 | -0.023039 | -0.15564 | 0.11902 | -0.16022 | -0.16479 | -0.004578 | -0.14648 | -0.073242 | -0.059509 | 0.13733 | -0.13275 | -0.045776 | 0.045776 | -0.009155 | 0.041199 | 122.7448 | -0.009155 | -0.29297 | 122.9004 | 122.8317 | 122.7585 | 0.086975 | 0.013733 | 122.7722 | 0.009155 | -0.17395 | 122.9507 | 122.9462 | 122.8958 | 0.17395 | 0.1236 | 0.15564 | -0.004578 | 0.17853 | 0.086975 | 0.27924 | 0.27008 | 123.024 | 123.0423 | -0.28839 | -0.26093 | 122.7402 | 122.8592 | 122.7493 | 122.8455
4252.5 | 123.1705 | -122.8546 | 0.07782 | -0.012741 | -0.015225 | -0.078583 | -0.0093289 | -0.031298 | -0.050167 | -0.042528 | -0.0051575 | 0.0010404 | 0.0062122 | -0.015475 | -0.22022 | -0.019623 | -0.026671 | -0.082397 | 0.073242 | -0.1236 | -0.045776 | 0.1236 | -0.022888 | 0.036621 | 0.12817 | 0.10529 | -0.09613 | 0.09613 | 0.21515 | 0.15106 | 0.15106 | 122.731 | -0.004578 | -0.1236 | 122.9782 | 122.8912 | 122.8317 | 0.16022 | 0.10071 | 122.7585 | 0.027466 | 0.01831 | 123.0698 | 123.0057 | 123.0057 | 0.24719 | 0.24719 | 0.24719 | 0.07782 | 0.31128 | 0.19226 | 0.19684 | 0.20142 | 122.9279 | 122.9599 | -0.20142 | -0.17395 | 122.8088 | 122.9507 | 122.7722 | 122.9828
4254.2812 | 123.0972 | -122.8683 | 0.10071 | -0.012741 | -0.012234 | -0.081788 | -0.0056973 | -0.030016 | -0.051235 | -0.043383 | 0.00094606 | 0.0036038 | 0.0083484 | -0.010134 | -0.2215 | -0.020051 | -0.021971 | -0.086975 | 0.10071 | -0.11902 | -0.10529 | 0.045776 | -0.11444 | -0.041199 | 0.041199 | 0.11444 | -0.10986 | 0.027466 | 0.10071 | 0.045776 | 0.091553 | 122.7493 | 0 | -0.20599 | 122.9141 | 122.8271 | 122.7539 | 0.07782 | 0.004578 | 122.7585 | 0.013733 | -0.073242 | 122.9691 | 122.9599 | 122.9141 | 0.20142 | 0.15564 | 0.16479 | 0.013733 | 0.21057 | 0.13733 | 0.21973 | 0.2243 | 122.9691 | 122.9828 | -0.21973 | -0.21057 | 122.7631 | 122.8958 | 122.7814 | 122.9095
4256.0156 | 123.0972 | -122.8775 | 0.11902 | -0.0051118 | -0.011807 | -0.077302 | -0.0063381 | -0.031084 | -0.05209 | -0.043169 | 0.00094606 | 0.0027494 | 0.008562 | -0.009707 | -0.22001 | -0.021332 | -0.023467 | -0.082397 | 0.10529 | -0.13275 | -0.10529 | 0.054932 | -0.1236 | -0.041199 | 0.032043 | 0.13275 | -0.10529 | 0.032043 | 0.10986 | 0.036621 | 0.091553 | 122.7448 | -0.013733 | -0.22431 | 122.9324 | 122.8363 | 122.7539 | 0.091552 | 0.009155 | 122.7722 | 0.013732 | -0.086976 | 122.9874 | 122.9691 | 122.9141 | 0.19684 | 0.14191 | 0.18768 | 0.027465 | 0.21515 | 0.13733 | 0.23804 | 0.23804 | 122.9828 | 123.0103 | -0.25177 | -0.22431 | 122.7722 | 122.9095 | 122.7951 | 122.9095
4257.8281 | 123.0789 | -122.905 | 0.10071 | -0.0051118 | -0.013302 | -0.079011 | -0.0082607 | -0.030443 | -0.051022 | -0.037401 | -0.0021057 | 0.0027494 | 0.0081348 | -0.015048 | -0.2183 | -0.020478 | -0.024962 | -0.073242 | 0.091553 | -0.10071 | -0.068665 | 0.10529 | -0.041199 | 0.013733 | 0.041199 | 0.11902 | -0.09613 | -0.004578 | 0.11902 | 0.041199 | 0.07782 | 122.8043 | -0.009155 | -0.16937 | 123.0103 | 122.9187 | 122.8638 | 0.11444 | 0.059509 | 122.8088 | 0.018311 | -0.10529 | 123.024 | 122.9828 | 122.9462 | 0.17395 | 0.13733 | 0.20599 | 0.032043 | 0.21515 | 0.091552 | 0.19226 | 0.21515 | 122.9965 | 123.024 | -0.20142 | -0.19684 | 122.8363 | 122.9004 | 122.8317 | 122.9462
4259.5625 | 123.1155 | -122.8683 | 0.10071 | 0.0025177 | -0.010525 | -0.079865 | -0.0084743 | -0.034075 | -0.050167 | -0.038256 | -0.0021057 | 0.0027494 | 0.0072802 | -0.015902 | -0.22043 | -0.018982 | -0.020689 | -0.086975 | 0.068665 | -0.10071 | -0.09613 | 0.064087 | -0.091553 | 0 | 0.041199 | 0.10986 | -0.10071 | 0.041199 | 0.10986 | 0.054932 | 0.09613 | 122.7676 | -0.032043 | -0.19684 | 122.9324 | 122.8683 | 122.7768 | 0.10071 | 0.009155 | 122.7676 | 0.009155 | -0.059509 | 122.9782 | 122.9645 | 122.9233 | 0.19684 | 0.15564 | 0.1648 | 0.004578 | 0.21057 | 0.14191 | 0.16937 | 0.21057 | 122.937 | 122.9782 | -0.20142 | -0.20142 | 122.7722 | 122.9095 | 122.7814 | 122.9095
4261.3438 | 123.1293 | -122.8683 | 0.091553 | -0.012741 | -0.01202 | -0.080719 | -0.0091153 | -0.030016 | -0.049954 | -0.042742 | 0.00094606 | 0.0018948 | 0.007494 | -0.01697 | -0.21787 | -0.020905 | -0.022826 | -0.10071 | 0.09613 | -0.11902 | -0.10071 | 0.068665 | -0.09613 | -0.004578 | 0.018311 | 0.11444 | -0.086975 | 0.045776 | 0.15106 | 0.07782 | 0.1236 | 122.7493 | 0.004577 | -0.19226 | 122.937 | 122.8638 | 122.7722 | 0.11444 | 0.022889 | 122.7814 | 0.022888 | -0.045777 | 123.0194 | 122.9919 | 122.9462 | 0.21057 | 0.16479 | 0.18768 | 0.018311 | 0.23804 | 0.13275 | 0.21515 | 0.20142 | 122.9645 | 122.9828 | -0.21057 | -0.17853 | 122.7676 | 122.9141 | 122.7676 | 122.8867
4263.125 | 123.1476 | -122.8546 | 0.086975 | -0.0051118 | -0.0094571 | -0.078797 | -0.0086879 | -0.030016 | -0.048458 | -0.04146 | -0.0021057 | 0.00061319 | 0.0081348 | -0.01227 | -0.22022 | -0.020905 | -0.022826 | -0.09613 | 0.086975 | -0.1236 | -0.07782 | 0.073242 | -0.082397 | 0 | 0.054932 | 0.10071 | -0.09613 | 0.041199 | 0.16022 | 0.10071 | 0.12817 | 122.731 | 0 | -0.16479 | 122.9279 | 122.8546 | 122.7722 | 0.1236 | 0.041199 | 122.7585 | 0.013733 | -0.045776 | 123.0148 | 122.9828 | 122.9553 | 0.2243 | 0.19684 | 0.19684 | 0.045776 | 0.25635 | 0.13733 | 0.21057 | 0.19684 | 122.9416 | 122.9553 | -0.21057 | -0.1831 | 122.7768 | 122.8958 | 122.7585 | 122.9095
4264.8594 | 123.1888 | -122.8729 | 0.082397 | -0.0051118 | -0.015438 | -0.079651 | -0.0067653 | -0.036211 | -0.051022 | -0.039965 | -0.0021057 | 0.0018948 | 0.0081348 | -0.011202 | -0.2215 | -0.019837 | -0.023253 | -0.068665 | 0.091553 | -0.086975 | -0.022888 | 0.14191 | -0.027466 | 0.064087 | 0.12817 | 0.10071 | -0.086975 | 0.086975 | 0.20142 | 0.14648 | 0.16479 | 122.7859 | 0.009156 | -0.10528 | 123.0148 | 122.937 | 122.8455 | 0.15106 | 0.059509 | 122.7859 | 0.018311 | 0.004578 | 123.0743 | 123.0377 | 123.0194 | 0.25177 | 0.23346 | 0.22888 | 0.064087 | 0.28839 | 0.17395 | 0.17853 | 0.18768 | 122.9645 | 122.9736 | -0.16937 | -0.16937 | 122.85 | 122.9599 | 122.8043 | 123.0011
4266.6562 | 123.0881 | -122.8592 | 0.10529 | -0.0051118 | -0.0092435 | -0.077942 | -0.0048427 | -0.029589 | -0.053799 | -0.040605 | -0.0021057 | 0.0053128 | 0.0094166 | -0.010134 | -0.22065 | -0.020691 | -0.025176 | -0.068665 | 0.10986 | -0.11902 | -0.10986 | 0.045776 | -0.11444 | -0.041199 | 0.041199 | 0.1236 | -0.09613 | 0.022888 | 0.10071 | 0.041199 | 0.09613 | 122.7402 | 0.004577 | -0.21515 | 122.905 | 122.818 | 122.7448 | 0.07782 | 0.004578 | 122.7631 | 0.01831 | -0.082398 | 122.9599 | 122.9553 | 122.9004 | 0.19226 | 0.13733 | 0.16479 | 0.009156 | 0.19684 | 0.11902 | 0.22888 | 0.21973 | 122.9691 | 122.9828 | -0.22431 | -0.20142 | 122.7493 | 122.8821 | 122.7905 | 122.9004
4268.4531 | 123.0698 | -122.9004 | 0.1236 | -0.0051118 | -0.015225 | -0.079011 | -0.0065517 | -0.033648 | -0.050595 | -0.039537 | -0.0021057 | 0.0010404 | 0.005144 | -0.010134 | -0.21915 | -0.01941 | -0.024748 | -0.073242 | 0.073242 | -0.12817 | -0.082397 | 0.073242 | -0.064087 | -0.009155 | 0.032043 | 0.11902 | -0.10529 | -0.004578 | 0.09613 | 0.041199 | 0.054932 | 122.7722 | -0.050354 | -0.20599 | 122.9736 | 122.8912 | 122.8363 | 0.11902 | 0.064087 | 122.7951 | -0.004577 | -0.12817 | 122.9965 | 122.9553 | 122.9416 | 0.16022 | 0.14649 | 0.20142 | 0.045777 | 0.20142 | 0.10071 | 0.20142 | 0.22431 | 122.9736 | 123.0194 | -0.25177 | -0.22888 | 122.818 | 122.8958 | 122.8271 | 122.9324
4270.1719 | 123.0743 | -122.8958 | 0.11444 | 0.010147 | -0.01138 | -0.077515 | -0.0056973 | -0.029162 | -0.053372 | -0.038896 | -0.0051575 | 0.0070218 | 0.0081348 | -0.00693 | -0.22043 | -0.018342 | -0.02368 | -0.068665 | 0.091553 | -0.12817 | -0.11444 | 0.059509 | -0.11902 | -0.064087 | 0.032043 | 0.14648 | -0.09613 | 0 | 0.082397 | 0.009155 | 0.07782 | 122.7676 | -0.022888 | -0.22888 | 122.9553 | 122.8317 | 122.7768 | 0.064087 | 0.009155 | 122.7997 | 0.032043 | -0.11444 | 122.9782 | 122.9736 | 122.905 | 0.17395 | 0.10528 | 0.18768 | 0.013733 | 0.17853 | 0.09613 | 0.21973 | 0.24261 | 122.9874 | 123.0423 | -0.24262 | -0.21057 | 122.7814 | 122.8958 | 122.8271 | 122.9279
4271.9688 | 123.0927 | -122.8775 | 0.10529 | 0.0025177 | -0.0092435 | -0.079438 | -0.0059109 | -0.027239 | -0.049099 | -0.040178 | -0.0051575 | 0.0018948 | 0.007494 | -0.013552 | -0.22001 | -0.019623 | -0.019835 | -0.12817 | 0.11902 | -0.13733 | -0.14191 | -0.022888 | -0.17853 | -0.082397 | -0.013733 | 0.1236 | -0.11902 | 0.022888 | 0.09613 | 0.018311 | 0.09613 | 122.7402 | 0.013733 | -0.24719 | 122.8546 | 122.7951 | 122.699 | 0.054932 | -0.041199 | 122.7585 | 0.01831 | -0.082398 | 122.9736 | 122.9736 | 122.8958 | 0.21515 | 0.13733 | 0.11444 | -0.004578 | 0.21515 | 0.14191 | 0.25635 | 0.24261 | 122.9965 | 123.0011 | -0.24262 | -0.22431 | 122.7356 | 122.9004 | 122.7493 | 122.8638
4273.7031 | 123.0423 | -122.905 | 0.11902 | -0.0051118 | -0.01437 | -0.080079 | -0.0065517 | -0.031298 | -0.05209 | -0.039537 | -0.0051575 | 0.0018948 | 0.011553 | -0.010134 | -0.21915 | -0.020051 | -0.020903 | -0.16479 | 0.10071 | -0.14648 | -0.16022 | 0 | -0.14648 | -0.07782 | -0.045776 | 0.15106 | -0.13733 | -0.054932 | 0.054932 | -0.004578 | 0.036621 | 122.7585 | -0.018311 | -0.27924 | 122.905 | 122.8271 | 122.7585 | 0.068664 | 0 | 122.7676 | 0.032043 | -0.17395 | 122.9599 | 122.9416 | 122.9004 | 0.17395 | 0.13275 | 0.14648 | -0.013733 | 0.19226 | 0.082397 | 0.24719 | 0.28839 | 123.0057 | 123.056 | -0.2655 | -0.25635 | 122.7448 | 122.85 | 122.7402 | 122.8592
4275.4844 | 123.1476 | -122.8821 | 0.082397 | 0.0025177 | -0.014584 | -0.081574 | -0.011038 | -0.031511 | -0.050808 | -0.039751 | 0.00094606 | 0.00061319 | 0.0070666 | -0.013339 | -0.22022 | -0.020051 | -0.023039 | -0.064087 | 0.082397 | -0.09613 | -0.022888 | 0.15106 | -0.027466 | 0.041199 | 0.11444 | 0.091553 | -0.091553 | 0.073242 | 0.1831 | 0.12817 | 0.14648 | 122.7859 | 0 | -0.10528 | 123.0331 | 122.9233 | 122.8546 | 0.13733 | 0.068664 | 122.7905 | 0.009156 | -0.009155 | 123.0652 | 123.0286 | 123.0103 | 0.23804 | 0.21973 | 0.24719 | 0.073242 | 0.27466 | 0.16479 | 0.17853 | 0.18311 | 122.9645 | 122.9736 | -0.17853 | -0.17395 | 122.8592 | 122.9553 | 122.818 | 122.9965
4277.2031 | 123.1293 | -122.8912 | 0.091553 | 0.0025177 | -0.013729 | -0.077515 | -0.0084743 | -0.028948 | -0.050808 | -0.042955 | -0.0021057 | 0.0016812 | 0.0066394 | -0.012698 | -0.21958 | -0.020691 | -0.024962 | -0.059509 | 0.068665 | -0.091553 | -0.059509 | 0.13733 | -0.036621 | 0.027466 | 0.091553 | 0.11902 | -0.086975 | 0.036621 | 0.15564 | 0.10529 | 0.11902 | 122.7997 | -0.022888 | -0.15106 | 123.0286 | 122.9187 | 122.8546 | 0.11902 | 0.054932 | 122.8043 | 0.027466 | -0.054932 | 123.0469 | 123.0103 | 122.9965 | 0.20599 | 0.19226 | 0.22888 | 0.032044 | 0.24261 | 0.1236 | 0.16022 | 0.20599 | 122.9599 | 123.0103 | -0.18311 | -0.17853 | 122.8317 | 122.9279 | 122.8317 | 122.9828
4279 | 123.0423 | -122.9095 | 0.1236 | -0.02037 | -0.01437 | -0.079865 | -0.0078335 | -0.031939 | -0.049954 | -0.042742 | -0.0021057 | 0.0042448 | 0.010057 | -0.015048 | -0.21958 | -0.021973 | -0.022185 | -0.13275 | 0.1236 | -0.15564 | -0.17853 | -0.013733 | -0.15564 | -0.082397 | -0.054932 | 0.13733 | -0.11444 | -0.036621 | 0.064087 | -0.004578 | 0.041199 | 122.7539 | 0 | -0.30212 | 122.8958 | 122.8271 | 122.7539 | 0.073243 | 0 | 122.7951 | 0.013733 | -0.16022 | 122.9736 | 122.9507 | 122.905 | 0.15564 | 0.10986 | 0.14191 | -0.022888 | 0.17853 | 0.07782 | 0.27924 | 0.25177 | 123.0331 | 123.0469 | -0.27924 | -0.23804 | 122.731 | 122.8729 | 122.7768 | 122.8546
4280.75 | 123.0789 | -122.905 | 0.13275 | 0.0025177 | -0.012875 | -0.081147 | -0.0061245 | -0.029802 | -0.053799 | -0.040178 | 0.00094606 | 0.0016812 | 0.0066394 | -0.017611 | -0.21894 | -0.018555 | -0.024535 | -0.059509 | 0.064087 | -0.11444 | -0.082397 | 0.09613 | -0.050354 | 0.009155 | 0.041199 | 0.11444 | -0.091553 | -0.013733 | 0.10986 | 0.045776 | 0.082397 | 122.7905 | -0.068664 | -0.21515 | 123.0011 | 122.9141 | 122.8546 | 0.1236 | 0.064087 | 122.8134 | -0.01831 | -0.14648 | 123.0148 | 122.9874 | 122.9507 | 0.17395 | 0.13733 | 0.21057 | 0.032044 | 0.20142 | 0.07782 | 0.17853 | 0.20599 | 122.9691 | 123.0194 | -0.24719 | -0.2243 | 122.8226 | 122.8912 | 122.8455 | 122.9462
4282.5469 | 123.0469 | -122.905 | 0.12817 | 0.0025177 | -0.01138 | -0.079011 | -0.0065517 | -0.031298 | -0.050381 | -0.043596 | -0.0051575 | 0.0033902 | 0.0079212 | -0.013979 | -0.22001 | -0.018128 | -0.027953 | -0.13275 | 0.11444 | -0.15564 | -0.15564 | 0.004578 | -0.14191 | -0.073242 | -0.054932 | 0.14191 | -0.10986 | -0.045776 | 0.054932 | 0 | 0.027466 | 122.7493 | -0.013733 | -0.28381 | 122.9095 | 122.8317 | 122.7631 | 0.082398 | 0.013733 | 122.7951 | 0.013733 | -0.17395 | 122.9599 | 122.9324 | 122.905 | 0.13733 | 0.10986 | 0.16022 | 0 | 0.16479 | 0.064087 | 0.27008 | 0.25177 | 123.0194 | 123.0469 | -0.28381 | -0.23804 | 122.7493 | 122.8592 | 122.7722 | 122.85
4284.3594 | 123.0469 | -122.905 | 0.10529 | -0.012741 | -0.010525 | -0.079011 | -0.0044155 | -0.029589 | -0.04974 | -0.040605 | 0.00094606 | 0.0031766 | 0.0070666 | -0.010989 | -0.22022 | -0.01941 | -0.019835 | -0.10529 | 0.10986 | -0.14648 | -0.17395 | -0.036621 | -0.20599 | -0.09613 | -0.050354 | 0.1236 | -0.12817 | -0.032043 | 0.032043 | -0.027466 | 0.050354 | 122.7585 | 0.004577 | -0.27924 | 122.8683 | 122.8088 | 122.699 | 0.050354 | -0.05951 | 122.7768 | 0.01831 | -0.13733 | 122.937 | 122.9553 | 122.8775 | 0.17853 | 0.10071 | 0.10986 | -0.027466 | 0.16022 | 0.096131 | 0.25635 | 0.25177 | 123.0148 | 123.0286 | -0.25177 | -0.23346 | 122.731 | 122.8729 | 122.7997 | 122.8546
4286.0938 | 123.1659 | -122.8775 | 0.09613 | 0.0025177 | -0.01672 | -0.080079 | -0.0097561 | -0.025744 | -0.052731 | -0.040605 | -0.0082091 | 0.0023222 | 0.0059986 | -0.013979 | -0.21872 | -0.01941 | -0.021971 | -0.064087 | 0.068665 | -0.11444 | -0.032043 | 0.16022 | -0.027466 | 0.041199 | 0.11902 | 0.091553 | -0.086975 | 0.07782 | 0.18768 | 0.13275 | 0.14191 | 122.7631 | -0.027465 | -0.12817 | 123.0377 | 122.9187 | 122.85 | 0.15564 | 0.086975 | 122.7905 | -0.004577 | -0.01831 | 123.0652 | 123.0194 | 123.0103 | 0.22888 | 0.21973 | 0.27466 | 0.082398 | 0.27466 | 0.16479 | 0.18311 | 0.17853 | 122.9462 | 122.9691 | -0.21057 | -0.1831 | 122.8455 | 122.9553 | 122.8134 | 122.9965
4287.875 | 123.0606 | -122.9187 | 0.12817 | 0.0025177 | -0.010098 | -0.078156 | -0.0063381 | -0.025316 | -0.048672 | -0.041674 | -0.0021057 | 0.0053128 | 0.007494 | -0.0050072 | -0.21937 | -0.018128 | -0.025603 | -0.10071 | 0.10529 | -0.13733 | -0.16022 | -0.018311 | -0.17395 | -0.10529 | -0.054932 | 0.14648 | -0.10986 | -0.041199 | 0.013733 | -0.027466 | 0.045776 | 122.7814 | -0.022888 | -0.28839 | 122.9004 | 122.8134 | 122.7448 | 0.032043 | -0.036621 | 122.8088 | 0.01831 | -0.16937 | 122.9324 | 122.9645 | 122.8912 | 0.15564 | 0.082397 | 0.11902 | -0.022888 | 0.1236 | 0.068664 | 0.24262 | 0.25635 | 123.024 | 123.0652 | -0.2655 | -0.23804 | 122.7585 | 122.8775 | 122.818 | 122.8638
4289.6719 | 123.0789 | -122.9095 | 0.10986 | 0.0025177 | -0.014157 | -0.080933 | -0.0082607 | -0.030016 | -0.051449 | -0.040605 | -0.0051575 | 0.001254 | 0.008562 | -0.013979 | -0.21808 | -0.019837 | -0.020262 | -0.086975 | 0.09613 | -0.10529 | -0.091553 | 0.082397 | -0.07782 | -0.013733 | 0.009155 | 0.10986 | -0.10071 | -0.018311 | 0.10986 | 0.032043 | 0.068665 | 122.8043 | -0.013733 | -0.20142 | 122.9919 | 122.8958 | 122.8317 | 0.091553 | 0.027466 | 122.8088 | 0 | -0.12817 | 123.0194 | 122.9782 | 122.9416 | 0.16937 | 0.13275 | 0.18768 | 0.013733 | 0.21057 | 0.082397 | 0.20142 | 0.21057 | 123.0057 | 123.0194 | -0.21515 | -0.21057 | 122.818 | 122.8912 | 122.8226 | 122.9187
4291.4062 | 123.1705 | -122.8912 | 0.082397 | 0.0025177 | -0.012234 | -0.078583 | -0.0093289 | -0.031084 | -0.050808 | -0.041887 | -0.0021057 | -0.00045501 | 0.0066394 | -0.018466 | -0.21915 | -0.020478 | -0.020903 | -0.082397 | 0.064087 | -0.11444 | -0.064087 | 0.10529 | -0.041199 | 0.027466 | 0.086975 | 0.10071 | -0.091553 | 0.086975 | 0.19226 | 0.13733 | 0.15106 | 122.7768 | -0.01831 | -0.14648 | 122.9965 | 122.9187 | 122.85 | 0.14191 | 0.073242 | 122.7997 | 0.018311 | 0.004578 | 123.0835 | 123.0423 | 123.0286 | 0.24261 | 0.22888 | 0.21973 | 0.050354 | 0.28381 | 0.17853 | 0.17853 | 0.19226 | 122.9553 | 122.9919 | -0.19684 | -0.17395 | 122.8271 | 122.9782 | 122.8088 | 122.9782
4293.2031 | 123.1888 | -122.8867 | 0.07782 | 0.0025177 | -0.014584 | -0.079438 | -0.0091153 | -0.034075 | -0.050808 | -0.041033 | -0.0021057 | 0.001254 | 0.008562 | -0.010134 | -0.21894 | -0.020691 | -0.027525 | -0.07782 | 0.082397 | -0.10529 | -0.045776 | 0.14191 | -0.032043 | 0.036621 | 0.15106 | 0.09613 | -0.07782 | 0.10071 | 0.21057 | 0.15106 | 0.15564 | 122.7814 | 0.004577 | -0.1236 | 123.0286 | 122.9233 | 122.8546 | 0.14191 | 0.073243 | 122.8088 | 0.01831 | 0.022888 | 123.0972 | 123.0423 | 123.0377 | 0.23346 | 0.22888 | 0.24719 | 0.05951 | 0.28839 | 0.17853 | 0.18768 | 0.17395 | 122.9691 | 122.9828 | -0.18311 | -0.15564 | 122.8409 | 122.9874 | 122.8088 | 123.0377
4294.9375 | 123.111 | -122.9324 | 0.12817 | -0.0051118 | -0.011807 | -0.081147 | -0.0061245 | -0.03023 | -0.051235 | -0.04146 | -0.0021057 | 0.0055264 | 0.0089892 | -0.0099206 | -0.22129 | -0.019623 | -0.024107 | -0.11902 | 0.11902 | -0.14191 | -0.14191 | -0.004578 | -0.1236 | -0.059509 | -0.009155 | 0.14648 | -0.11444 | 0.009155 | 0.082397 | 0.045776 | 0.073242 | 122.7905 | -0.009155 | -0.27008 | 122.9279 | 122.8729 | 122.8088 | 0.082398 | 0.018311 | 122.818 | 0.01831 | -0.11902 | 123.0148 | 123.0057 | 122.9782 | 0.18768 | 0.16022 | 0.13733 | 0 | 0.19684 | 0.1236 | 0.26093 | 0.26093 | 123.0515 | 123.0789 | -0.27008 | -0.24262 | 122.7905 | 122.9416 | 122.8134 | 122.9233
4296.7344 | 123.143 | -122.8775 | 0.07782 | -0.0051118 | -0.012234 | -0.079865 | -0.0063381 | -0.034289 | -0.050808 | -0.041674 | -0.0021057 | 0.0027494 | 0.010057 | -0.017825 | -0.21979 | -0.019623 | -0.023467 | -0.059509 | 0.059509 | -0.082397 | -0.036621 | 0.11444 | -0.086975 | 0.018311 | 0.09613 | 0.10071 | -0.073242 | 0.045776 | 0.12817 | 0.086975 | 0.11444 | 122.7951 | -0.018311 | -0.11444 | 122.9919 | 122.8958 | 122.7905 | 0.10071 | -0.004578 | 122.8043 | 0.022888 | -0.032044 | 123.0057 | 122.9919 | 122.9645 | 0.18768 | 0.16022 | 0.19684 | 0.045776 | 0.20142 | 0.11902 | 0.14191 | 0.17395 | 122.937 | 122.9782 | -0.16022 | -0.15106 | 122.8409 | 122.9233 | 122.818 | 122.9736
4298.5312 | 123.0972 | -122.9279 | 0.11444 | 0.010147 | -0.013089 | -0.080719 | -0.0065517 | -0.02788 | -0.052517 | -0.039537 | 0.00094606 | 0.0027494 | 0.010485 | -0.015048 | -0.22001 | -0.020051 | -0.027525 | -0.1236 | 0.10986 | -0.13275 | -0.16022 | -0.004578 | -0.14191 | -0.07782 | -0.032043 | 0.13275 | -0.11444 | -0.013733 | 0.091553 | 0.022888 | 0.073242 | 122.7951 | -0.004578 | -0.27466 | 122.9233 | 122.85 | 122.7859 | 0.054931 | -0.009156 | 122.8134 | 0.01831 | -0.12817 | 123.0194 | 123.0011 | 122.9507 | 0.18768 | 0.13733 | 0.12817 | -0.027466 | 0.20599 | 0.10071 | 0.24261 | 0.24719 | 123.0377 | 123.0606 | -0.24719 | -0.22888 | 122.7676 | 122.9141 | 122.8043 | 122.8958
4300.25 | 123.0789 | -122.9004 | 0.10986 | 0.0025177 | -0.010952 | -0.075806 | -0.0063381 | -0.02788 | -0.050595 | -0.041674 | 0.00094606 | 0.0042448 | 0.0081348 | -0.0088526 | -0.21851 | -0.021546 | -0.022826 | -0.1236 | 0.10071 | -0.13733 | -0.15106 | -0.022888 | -0.18768 | -0.10071 | -0.004578 | 0.14648 | -0.11902 | -0.009155 | 0.059509 | 0 | 0.064087 | 122.7631 | -0.009155 | -0.26093 | 122.8775 | 122.7997 | 122.7127 | 0.036621 | -0.050354 | 122.7814 | 0.036621 | -0.11902 | 122.9599 | 122.9645 | 122.9004 | 0.18311 | 0.11902 | 0.11444 | -0.013733 | 0.17853 | 0.10986 | 0.23804 | 0.2655 | 123.0011 | 123.0469 | -0.24719 | -0.22888 | 122.7493 | 122.8912 | 122.7768 | 122.8958
4302.0312 | 123.0423 | -122.8958 | 0.1236 | -0.012741 | -0.010311 | -0.079865 | -0.0044155 | -0.03023 | -0.051663 | -0.040392 | 0.00094606 | 0.0048856 | 0.0092028 | -0.015902 | -0.2183 | -0.021332 | -0.023253 | -0.1236 | 0.10529 | -0.13733 | -0.15564 | -0.032043 | -0.20142 | -0.11902 | -0.07782 | 0.13733 | -0.10529 | -0.045776 | 0.032043 | -0.050354 | 0.041199 | 122.7585 | -0.01831 | -0.27924 | 122.8638 | 122.7768 | 122.6944 | 0.01831 | -0.064087 | 122.7905 | 0.013733 | -0.16937 | 122.9279 | 122.937 | 122.8455 | 0.14649 | 0.054932 | 0.10529 | -0.018311 | 0.13733 | 0.05951 | 0.24262 | 0.24262 | 123.0011 | 123.0331 | -0.26093 | -0.22888 | 122.7402 | 122.85 | 122.7722 | 122.818
4303.8281 | 123.1522 | -122.8912 | 0.09613 | -0.0051118 | -0.01437 | -0.078156 | -0.0071927 | -0.033007 | -0.051663 | -0.042528 | 0.00094606 | -0.00024141 | 0.0087756 | -0.014834 | -0.21851 | -0.020905 | -0.017485 | -0.10529 | 0.091553 | -0.09613 | -0.086975 | 0.07782 | -0.10071 | -0.009155 | 0.032043 | 0.10071 | -0.091553 | 0.027466 | 0.13733 | 0.068665 | 0.10529 | 122.7951 | -0.004577 | -0.1831 | 122.9691 | 122.8821 | 122.7905 | 0.086975 | -0.004578 | 122.7997 | 0.004578 | -0.068664 | 123.0286 | 122.9965 | 122.9599 | 0.19684 | 0.16022 | 0.17395 | 0.009155 | 0.22888 | 0.11902 | 0.18768 | 0.19226 | 122.9828 | 122.9919 | -0.19226 | -0.18768 | 122.8043 | 122.9187 | 122.7859 | 122.9233
4305.5781 | 123.0606 | -122.8958 | 0.10986 | -0.0051118 | -0.0083889 | -0.077515 | -0.0046291 | -0.032793 | -0.04974 | -0.042314 | 0.00094606 | 0.0061674 | 0.008562 | -0.010348 | -0.22022 | -0.019196 | -0.021758 | -0.091553 | 0.11902 | -0.13733 | -0.15106 | 0.004578 | -0.18768 | -0.09613 | -0.032043 | 0.11902 | -0.11444 | -0.027466 | 0.045776 | -0.054932 | 0.050354 | 122.7585 | 0.009156 | -0.26093 | 122.9004 | 122.7997 | 122.7081 | 0.041199 | -0.050354 | 122.7814 | 0.009156 | -0.13733 | 122.9416 | 122.9462 | 122.8409 | 0.16479 | 0.059509 | 0.14191 | -0.013733 | 0.16022 | 0.086975 | 0.25635 | 0.23346 | 123.0148 | 123.0148 | -0.24719 | -0.2243 | 122.7448 | 122.8683 | 122.8043 | 122.8638
4307.375 | 123.0377 | -122.9416 | 0.10071 | -0.012741 | -0.0079617 | -0.075379 | -0.0031337 | -0.030871 | -0.048031 | -0.040605 | 0.0039979 | 0.0038174 | 0.0087756 | -0.016543 | -0.21702 | -0.020691 | -0.023253 | -0.11902 | 0.13275 | -0.14648 | -0.17395 | -0.045776 | -0.19684 | -0.10986 | -0.07782 | 0.13733 | -0.12817 | -0.032043 | 0.018311 | -0.036621 | 0.050354 | 122.7951 | 0.032043 | -0.27466 | 122.8958 | 122.8317 | 122.7448 | 0.036621 | -0.050354 | 122.8134 | 0.036621 | -0.13275 | 122.9599 | 122.9919 | 122.905 | 0.17853 | 0.091553 | 0.10071 | -0.027466 | 0.14649 | 0.096131 | 0.27924 | 0.2655 | 123.0743 | 123.0789 | -0.24719 | -0.22888 | 122.7676 | 122.9095 | 122.8226 | 122.8638
4309.1562 | 123.1842 | -122.9004 | 0.07782 | 0.0025177 | -0.013516 | -0.080079 | -0.0078335 | -0.031511 | -0.050595 | -0.040819 | 0.00094606 | 0.0027494 | 0.0066394 | -0.010989 | -0.22001 | -0.018342 | -0.021971 | -0.073242 | 0.07782 | -0.09613 | -0.027466 | 0.16022 | -0.004578 | 0.041199 | 0.10529 | 0.10071 | -0.07782 | 0.07782 | 0.20142 | 0.15564 | 0.14191 | 122.8043 | 0 | -0.10529 | 123.0606 | 122.9416 | 122.8958 | 0.13733 | 0.091552 | 122.8226 | 0.022888 | 0 | 123.1018 | 123.0423 | 123.056 | 0.21973 | 0.23346 | 0.25635 | 0.068664 | 0.27924 | 0.15564 | 0.17395 | 0.17853 | 122.9782 | 123.0011 | -0.17395 | -0.15564 | 122.8729 | 122.9782 | 122.8271 | 123.0057
4310.9062 | 123.1613 | -122.9095 | 0.10986 | 0.010147 | -0.015011 | -0.079438 | -0.0089017 | -0.031298 | -0.050381 | -0.04146 | -0.0021057 | 0.0021084 | 0.007494 | -0.010989 | -0.21915 | -0.018769 | -0.024748 | -0.054932 | 0.064087 | -0.10529 | -0.027466 | 0.11444 | -0.027466 | 0.045776 | 0.086975 | 0.10986 | -0.091553 | 0.054932 | 0.16479 | 0.10986 | 0.1236 | 122.8043 | -0.045776 | -0.13733 | 123.024 | 122.9553 | 122.8821 | 0.15106 | 0.07782 | 122.818 | 0 | -0.054931 | 123.0743 | 123.0331 | 123.0194 | 0.21515 | 0.20142 | 0.21973 | 0.07782 | 0.25635 | 0.14649 | 0.16937 | 0.20142 | 122.9736 | 123.0194 | -0.21515 | -0.20142 | 122.8821 | 122.9645 | 122.8546 | 122.9965
4312.7031 | 123.0789 | -122.9279 | 0.11444 | -0.0051118 | -0.01138 | -0.080079 | -0.0071927 | -0.028948 | -0.050808 | -0.041674 | -0.0021057 | 0.0031766 | 0.0098438 | -0.01163 | -0.22107 | -0.020691 | -0.021758 | -0.12817 | 0.11902 | -0.14648 | -0.16479 | -0.009155 | -0.15106 | -0.07782 | -0.050354 | 0.13275 | -0.13275 | -0.027466 | 0.064087 | 0.004578 | 0.050354 | 122.7814 | 0.004578 | -0.27924 | 122.9187 | 122.85 | 122.7768 | 0.068664 | -0.004578 | 122.7951 | 0.01831 | -0.14191 | 122.9919 | 122.9782 | 122.9324 | 0.18311 | 0.13733 | 0.13733 | -0.018311 | 0.19684 | 0.10529 | 0.2655 | 0.2655 | 123.0469 | 123.0606 | -0.26093 | -0.24719 | 122.7631 | 122.9004 | 122.7997 | 122.8775
4314.5 | 123.1567 | -122.8683 | 0.09613 | -0.0051118 | -0.010952 | -0.079865 | -0.0050565 | -0.033648 | -0.048886 | -0.03911 | -0.0021057 | 0.0025358 | 0.0072802 | -0.016329 | -0.21958 | -0.019196 | -0.020049 | -0.10986 | 0.11902 | -0.12817 | -0.12817 | 0.036621 | -0.16479 | -0.064087 | 0.027466 | 0.10529 | -0.10529 | 0.059509 | 0.14648 | 0.068665 | 0.14191 | 122.7402 | 0.022889 | -0.2243 | 122.905 | 122.8043 | 122.7036 | 0.064087 | -0.036621 | 122.7631 | 0.009156 | -0.036621 | 123.0148 | 123.0103 | 122.937 | 0.24719 | 0.17395 | 0.1648 | 0 | 0.25177 | 0.16479 | 0.24719 | 0.21057 | 122.9874 | 122.9736 | -0.2243 | -0.20142 | 122.7402 | 122.9279 | 122.7585 | 122.8958
4316.2344 | 123.1613 | -122.8958 | 0.09613 | -0.0051118 | -0.012448 | -0.078583 | -0.0091153 | -0.031725 | -0.051876 | -0.044237 | 0.00094606 | 0.0016812 | 0.0070666 | -0.017825 | -0.2183 | -0.02176 | -0.023467 | -0.10529 | 0.082397 | -0.10529 | -0.091553 | 0.086975 | -0.09613 | 0 | 0.032043 | 0.11902 | -0.091553 | 0.036621 | 0.13275 | 0.059509 | 0.10986 | 122.7905 | -0.013733 | -0.18768 | 122.9828 | 122.8958 | 122.7997 | 0.10529 | 0.009156 | 122.8043 | 0.022889 | -0.059509 | 123.0286 | 123.0057 | 122.9553 | 0.20142 | 0.15106 | 0.19226 | 0.013733 | 0.2243 | 0.12817 | 0.18768 | 0.21057 | 122.9782 | 123.0148 | -0.20142 | -0.18768 | 122.8043 | 122.9324 | 122.7905 | 122.9279
4318.0312 | 123.1842 | -122.8867 | 0.073242 | -0.012741 | -0.010739 | -0.077942 | -0.0042019 | -0.028307 | -0.050808 | -0.041887 | 0.00094606 | 0.0016812 | 0.010057 | -0.013552 | -0.21872 | -0.020051 | -0.023894 | -0.11444 | 0.10529 | -0.12817 | -0.11902 | 0.018311 | -0.16022 | -0.059509 | 0.041199 | 0.13275 | -0.07782 | 0.073242 | 0.14648 | 0.068665 | 0.14191 | 122.7585 | 0.032044 | -0.19226 | 122.905 | 122.8271 | 122.7264 | 0.068665 | -0.032043 | 122.8088 | 0.059509 | 0 | 123.0331 | 123.0286 | 122.9553 | 0.21973 | 0.14649 | 0.14649 | 0.009155 | 0.2243 | 0.15106 | 0.23346 | 0.21057 | 122.9919 | 123.0194 | -0.20142 | -0.15106 | 122.7676 | 122.9599 | 122.7722 | 122.9279
4319.8281 | 123.1888 | -122.8683 | 0.07782 | -0.0051118 | -0.010952 | -0.077942 | -0.0067653 | -0.027239 | -0.050808 | -0.042528 | 0.00094606 | 0.001254 | 0.0072802 | -0.011416 | -0.21958 | -0.01941 | -0.020903 | -0.045776 | 0.064087 | -0.09613 | -0.022888 | 0.12817 | -0.07782 | 0.018311 | 0.12817 | 0.10071 | -0.068665 | 0.091553 | 0.1831 | 0.10529 | 0.14191 | 122.7722 | -0.013733 | -0.10071 | 122.9965 | 122.8867 | 122.7905 | 0.11444 | 0.01831 | 122.7997 | 0.022888 | 0.013733 | 123.0515 | 123.0103 | 122.9736 | 0.21057 | 0.17395 | 0.2243 | 0.073242 | 0.25177 | 0.16022 | 0.16022 | 0.16937 | 122.9324 | 122.9691 | -0.17395 | -0.14649 | 122.8455 | 122.9599 | 122.8226 | 122.9965
4321.5781 | 123.2208 | -122.9004 | 0.07782 | 0.010147 | -0.013302 | -0.079865 | -0.0069791 | -0.027666 | -0.051876 | -0.040819 | 0.00094606 | 0.0018948 | 0.0066394 | -0.011843 | -0.21937 | -0.021332 | -0.024535 | -0.064087 | 0.073242 | -0.11444 | -0.022888 | 0.16937 | -0.013733 | 0.050354 | 0.15564 | 0.10071 | -0.082397 | 0.073242 | 0.18768 | 0.14648 | 0.13275 | 122.7859 | -0.004578 | -0.10071 | 123.0698 | 122.9507 | 122.8867 | 0.16479 | 0.10071 | 122.818 | 0.022888 | -0.004578 | 123.0881 | 123.0331 | 123.0469 | 0.21515 | 0.22888 | 0.28381 | 0.091553 | 0.27008 | 0.15564 | 0.18768 | 0.18311 | 122.9736 | 123.0011 | -0.19226 | -0.16022 | 122.8775 | 122.9736 | 122.8363 | 123.056
4323.3594 | 123.0652 | -122.9141 | 0.12817 | -0.0051118 | -0.012875 | -0.081147 | -0.0076199 | -0.033007 | -0.052731 | -0.040819 | -0.0082091 | 0.0033902 | 0.0081348 | -0.014407 | -0.22172 | -0.020691 | -0.023894 | -0.14648 | 0.10529 | -0.16022 | -0.17853 | -0.009155 | -0.13733 | -0.07782 | -0.050354 | 0.14191 | -0.12817 | -0.050354 | 0.054932 | -0.018311 | 0.045776 | 122.7539 | -0.022888 | -0.3067 | 122.905 | 122.8363 | 122.7768 | 0.082397 | 0.022888 | 122.7859 | 0.013733 | -0.17853 | 122.9691 | 122.9599 | 122.8958 | 0.17395 | 0.10986 | 0.15106 | -0.018311 | 0.18311 | 0.07782 | 0.2655 | 0.27008 | 123.0194 | 123.056 | -0.28839 | -0.25635 | 122.7356 | 122.8638 | 122.7676 | 122.8638
4325.1406 | 123.0881 | -122.9233 | 0.10529 | -0.012741 | -0.0081753 | -0.078797 | -0.0027065 | -0.029162 | -0.04974 | -0.040392 | -0.0021057 | 0.0038174 | 0.008562 | -0.012484 | -0.21979 | -0.018769 | -0.023467 | -0.10986 | 0.12817 | -0.15564 | -0.16479 | -0.059509 | -0.20599 | -0.10071 | -0.050354 | 0.14191 | -0.12817 | -0.036621 | 0.013733 | -0.036621 | 0.054932 | 122.7676 | 0.022888 | -0.27008 | 122.8638 | 122.8226 | 122.7173 | 0.054932 | -0.050354 | 122.7951 | 0.036621 | -0.14191 | 122.937 | 122.9782 | 122.8867 | 0.18311 | 0.091553 | 0.096131 | -0.009155 | 0.14191 | 0.091553 | 0.28381 | 0.27008 | 123.0515 | 123.0652 | -0.26093 | -0.23346 | 122.7585 | 122.8867 | 122.8134 | 122.8729
4326.9531 | 123.1705 | -122.8958 | 0.09613 | -0.0051118 | -0.012875 | -0.080506 | -0.0095425 | -0.028948 | -0.051449 | -0.042314 | -0.0051575 | 0.0023222 | 0.0087756 | -0.015261 | -0.21979 | -0.020905 | -0.022826 | -0.073242 | 0.07782 | -0.10529 | -0.036621 | 0.16022 | -0.009155 | 0.032043 | 0.10529 | 0.09613 | -0.09613 | 0.068665 | 0.19226 | 0.1236 | 0.14191 | 122.7905 | -0.01831 | -0.13275 | 123.056 | 122.9279 | 122.8867 | 0.13733 | 0.096131 | 122.7997 | 0 | -0.027465 | 123.0881 | 123.0377 | 123.0194 | 0.23804 | 0.21973 | 0.2655 | 0.068665 | 0.28839 | 0.16479 | 0.18311 | 0.19226 | 122.9736 | 122.9919 | -0.20142 | -0.19226 | 122.8592 | 122.9645 | 122.8226 | 123.0011
4328.7656 | 123.2025 | -122.8775 | 0.07782 | 0.0025177 | -0.010311 | -0.07837 | -0.0076199 | -0.03023 | -0.04739 | -0.041674 | 0.00094606 | 0.0023222 | 0.0066394 | -0.019747 | -0.21958 | -0.018555 | -0.024107 | -0.050354 | 0.086975 | -0.10071 | -0.054932 | 0.11902 | -0.082397 | 0.009155 | 0.10986 | 0.091553 | -0.07782 | 0.09613 | 0.16937 | 0.10529 | 0.16937 | 122.7768 | 0.009155 | -0.13275 | 122.9965 | 122.8867 | 122.7951 | 0.10986 | 0.018311 | 122.7997 | 0.013733 | 0.01831 | 123.0469 | 123.0469 | 122.9828 | 0.24719 | 0.18311 | 0.21973 | 0.045776 | 0.24719 | 0.17395 | 0.18768 | 0.16937 | 122.9645 | 122.9691 | -0.17853 | -0.15564 | 122.8226 | 122.9736 | 122.8271 | 122.9874
4330.5625 | 123.0881 | -122.9233 | 0.13733 | 0.0025177 | -0.015438 | -0.080292 | -0.0061245 | -0.030871 | -0.051663 | -0.041674 | 0.00094606 | 0.0040312 | 0.0079212 | -0.00458 | -0.21915 | -0.020478 | -0.02368 | -0.13275 | 0.09613 | -0.13733 | -0.16937 | -0.018311 | -0.15564 | -0.082397 | -0.064087 | 0.14191 | -0.11902 | -0.041199 | 0.068665 | 0.004578 | 0.050354 | 122.7859 | -0.041199 | -0.3067 | 122.905 | 122.8409 | 122.7676 | 0.054932 | -0.018311 | 122.8043 | 0.004578 | -0.17853 | 122.9919 | 122.9736 | 122.9279 | 0.16937 | 0.1236 | 0.11902 | -0.032044 | 0.18768 | 0.07782 | 0.23346 | 0.26093 | 123.0194 | 123.0652 | -0.27466 | -0.25635 | 122.7539 | 122.8821 | 122.7905 | 122.8592
4332.3594 | 123.1476 | -122.9141 | 0.07782 | -0.012741 | -0.010311 | -0.077729 | -0.0080471 | -0.028734 | -0.049099 | -0.041674 | -0.0021057 | -0.0013094 | 0.0072802 | -0.019534 | -0.21979 | -0.020905 | -0.026671 | -0.10986 | 0.086975 | -0.10986 | -0.091553 | 0.054932 | -0.10071 | -0.009155 | 0.018311 | 0.11902 | -0.091553 | 0.013733 | 0.10986 | 0.073242 | 0.11444 | 122.8043 | 0.009155 | -0.16937 | 122.9691 | 122.905 | 122.8134 | 0.10071 | 0.009155 | 122.8226 | 0.041199 | -0.064087 | 123.024 | 123.0286 | 122.9874 | 0.20599 | 0.16479 | 0.16479 | 0.01831 | 0.20142 | 0.10529 | 0.19684 | 0.21057 | 123.0011 | 123.0331 | -0.18768 | -0.16937 | 122.8226 | 122.9279 | 122.8043 | 122.9324
4334.0625 | 123.2071 | -122.8775 | 0.068665 | 0.010147 | -0.012448 | -0.075593 | -0.0061245 | -0.030871 | -0.051663 | -0.042742 | 0.00094606 | 0.001254 | 0.0079212 | -0.012698 | -0.22406 | -0.018769 | -0.023467 | -0.054932 | 0.07782 | -0.11902 | -0.050354 | 0.10529 | -0.073242 | 0.004578 | 0.11444 | 0.09613 | -0.073242 | 0.091553 | 0.1831 | 0.11902 | 0.16479 | 122.7585 | 0.009155 | -0.11902 | 122.9828 | 122.8821 | 122.8043 | 0.1236 | 0.045777 | 122.8043 | 0.027465 | 0.022888 | 123.0606 | 123.0423 | 122.9965 | 0.23804 | 0.19226 | 0.22431 | 0.068665 | 0.25635 | 0.16479 | 0.19684 | 0.16937 | 122.9553 | 122.9736 | -0.18768 | -0.14191 | 122.8271 | 122.9691 | 122.8226 | 122.9919
4335.8594 | 123.1934 | -122.9095 | 0.082397 | 0.0025177 | -0.014584 | -0.080719 | -0.0089017 | -0.030871 | -0.050595 | -0.039751 | 0.00094606 | -0.00066861 | 0.0072802 | -0.0094934 | -0.21894 | -0.020905 | -0.024535 | -0.064087 | 0.07782 | -0.086975 | -0.032043 | 0.13275 | -0.013733 | 0.050354 | 0.10986 | 0.09613 | -0.10529 | 0.068665 | 0.19684 | 0.14191 | 0.14648 | 122.8226 | -0.004577 | -0.11444 | 123.0423 | 122.9599 | 122.8958 | 0.13733 | 0.073242 | 122.8043 | 0.013733 | -0.013732 | 123.1064 | 123.056 | 123.0515 | 0.25177 | 0.24719 | 0.21973 | 0.054932 | 0.30212 | 0.17395 | 0.16479 | 0.20142 | 122.9874 | 123.0057 | -0.16937 | -0.18768 | 122.8775 | 122.9782 | 122.8455 | 123.0194
4337.6719 | 123.1934 | -122.8912 | 0.091553 | -0.0051118 | -0.01138 | -0.076661 | -0.0052701 | -0.033434 | -0.049526 | -0.041887 | -0.0021057 | 0.0033902 | 0.0064258 | -0.011416 | -0.22022 | -0.018128 | -0.020689 | -0.032043 | 0.082397 | -0.09613 | -0.032043 | 0.11444 | -0.064087 | 0.009155 | 0.10986 | 0.09613 | -0.068665 | 0.10986 | 0.17853 | 0.10529 | 0.16937 | 122.7951 | -0.009156 | -0.1236 | 123.0057 | 122.9004 | 122.8271 | 0.10528 | 0.032043 | 122.8226 | 0.004577 | 0.01831 | 123.0698 | 123.0606 | 122.9965 | 0.23804 | 0.17395 | 0.21057 | 0.064087 | 0.24719 | 0.17853 | 0.17853 | 0.16479 | 122.9736 | 122.9874 | -0.18768 | -0.16022 | 122.8592 | 123.0011 | 122.8592 | 123.0011
4339.4688 | 123.175 | -122.905 | 0.064087 | 0.0025177 | -0.014798 | -0.078156 | -0.0082607 | -0.037706 | -0.04974 | -0.041674 | -0.0051575 | 0.00039959 | 0.008562 | -0.019747 | -0.21958 | -0.02176 | -0.025389 | -0.10071 | 0.086975 | -0.12817 | -0.086975 | 0.073242 | -0.073242 | 0 | 0.045776 | 0.10071 | -0.10529 | 0.054932 | 0.16937 | 0.09613 | 0.13275 | 122.7768 | 0.022888 | -0.15106 | 122.9782 | 122.905 | 122.8317 | 0.12817 | 0.054932 | 122.7997 | 0.036621 | -0.009155 | 123.0743 | 123.0377 | 123.0011 | 0.23804 | 0.20142 | 0.20142 | 0.041199 | 0.27466 | 0.16022 | 0.21515 | 0.20599 | 122.9919 | 123.0057 | -0.19226 | -0.16937 | 122.818 | 122.9599 | 122.8043 | 122.9507
4341.1875 | 123.1384 | -122.905 | 0.09613 | -0.0051118 | -0.01202 | -0.079011 | -0.0039883 | -0.026171 | -0.046749 | -0.03911 | 0.00094606 | 0.0023222 | 0.0079212 | -0.01163 | -0.22065 | -0.018982 | -0.024748 | -0.11902 | 0.10071 | -0.14648 | -0.13733 | 0 | -0.16937 | -0.07782 | 0.004578 | 0.12817 | -0.086975 | 0.036621 | 0.10986 | 0.041199 | 0.10529 | 122.7585 | 0.004578 | -0.23346 | 122.905 | 122.8271 | 122.7356 | 0.068664 | -0.022889 | 122.818 | 0.032044 | -0.059509 | 123.0148 | 123.0103 | 122.9462 | 0.19226 | 0.12817 | 0.14648 | 0.009155 | 0.19684 | 0.1236 | 0.24719 | 0.21515 | 123.0057 | 123.0331 | -0.24261 | -0.1831 | 122.7676 | 122.9416 | 122.7859 | 122.9095
4343 | 123.1064 | -122.9324 | 0.10071 | -0.0051118 | -0.010311 | -0.077088 | -0.0048427 | -0.028948 | -0.050381 | -0.038896 | 0.00094606 | 0.0040312 | 0.0079212 | -0.0065026 | -0.22043 | -0.017914 | -0.020689 | -0.07782 | 0.11902 | -0.10529 | -0.1236 | 0.032043 | -0.14648 | -0.073242 | 0.022888 | 0.13275 | -0.10071 | 0.004578 | 0.059509 | 0 | 0.064087 | 122.8271 | 0.018311 | -0.2243 | 122.9645 | 122.8592 | 122.7859 | 0.032044 | -0.041198 | 122.8317 | 0.032043 | -0.09613 | 122.9919 | 122.9965 | 122.9324 | 0.1648 | 0.10071 | 0.13733 | -0.01831 | 0.16022 | 0.10529 | 0.22431 | 0.23346 | 123.0515 | 123.0652 | -0.20599 | -0.20142 | 122.8088 | 122.937 | 122.8546 | 122.9553
4344.7969 | 123.0652 | -122.9279 | 0.11444 | -0.0051118 | -0.0073209 | -0.075593 | -0.0046291 | -0.029375 | -0.046322 | -0.040178 | 0.00094606 | 0.0033902 | 0.0077076 | -0.013339 | -0.21872 | -0.018769 | -0.024321 | -0.12817 | 0.11902 | -0.12817 | -0.16937 | -0.068665 | -0.21973 | -0.11902 | -0.050354 | 0.12817 | -0.1236 | -0.045776 | 0.022888 | -0.041199 | 0.036621 | 122.7997 | 0.004578 | -0.28381 | 122.8592 | 122.8088 | 122.7081 | 0.009155 | -0.091553 | 122.8043 | 0.013733 | -0.16022 | 122.9507 | 122.9645 | 122.8867 | 0.16022 | 0.082397 | 0.059509 | -0.041199 | 0.14648 | 0.07782 | 0.24719 | 0.25177 | 123.0469 | 123.056 | -0.24262 | -0.23804 | 122.7585 | 122.8821 | 122.7997 | 122.8775
4346.5312 | 123.1567 | -122.9141 | 0.10529 | -0.02037 | -0.014157 | -0.080506 | -0.0078335 | -0.029162 | -0.053158 | -0.039965 | -0.0021057 | 0.00018579 | 0.0070666 | -0.020388 | -0.21744 | -0.020905 | -0.021971 | -0.10986 | 0.082397 | -0.10986 | -0.10986 | 0.054932 | -0.10529 | -0.022888 | 0.032043 | 0.13275 | -0.091553 | 0.022888 | 0.15106 | 0.054932 | 0.11902 | 122.8043 | -0.022889 | -0.21515 | 122.9691 | 122.8912 | 122.8088 | 0.086975 | 0.004577 | 122.8226 | 0.027465 | -0.082398 | 123.0652 | 123.0331 | 122.9691 | 0.21057 | 0.14649 | 0.16479 | 0 | 0.24261 | 0.11444 | 0.19226 | 0.2243 | 122.9965 | 123.0469 | -0.21515 | -0.19684 | 122.8043 | 122.937 | 122.8043 | 122.9462
4348.3281 | 123.1934 | -122.9004 | 0.10529 | 0.0025177 | -0.013516 | -0.079438 | -0.0065517 | -0.034716 | -0.050381 | -0.042101 | 0.00094606 | 0.0021084 | 0.008562 | -0.016116 | -0.21958 | -0.020051 | -0.026457 | -0.054932 | 0.07782 | -0.091553 | -0.036621 | 0.13275 | -0.027466 | 0.041199 | 0.10986 | 0.11444 | -0.091553 | 0.064087 | 0.1831 | 0.11444 | 0.14191 | 122.8088 | -0.027466 | -0.14191 | 123.0331 | 122.9416 | 122.8729 | 0.13275 | 0.064087 | 122.8088 | 0.009155 | -0.041199 | 123.0835 | 123.0423 | 123.0148 | 0.23346 | 0.20599 | 0.2243 | 0.054932 | 0.27466 | 0.15564 | 0.16937 | 0.20599 | 122.9782 | 123.0148 | -0.19684 | -0.19684 | 122.8638 | 122.9645 | 122.8455 | 123.0103
4350.1094 | 123.0789 | -122.9416 | 0.10986 | -0.0051118 | -0.0098843 | -0.077729 | -0.0052701 | -0.028093 | -0.051235 | -0.039324 | -0.0021057 | 0.0044584 | 0.008562 | -0.014834 | -0.21894 | -0.01941 | -0.022185 | -0.11444 | 0.11444 | -0.13733 | -0.16479 | -0.045776 | -0.19226 | -0.10529 | -0.036621 | 0.13733 | -0.1236 | -0.032043 | 0.041199 | -0.027466 | 0.059509 | 122.8043 | 0.004578 | -0.27466 | 122.8958 | 122.8363 | 122.7493 | 0.032043 | -0.054932 | 122.818 | 0.027466 | -0.14191 | 122.9828 | 123.0011 | 122.9141 | 0.1831 | 0.09613 | 0.091553 | -0.027466 | 0.16479 | 0.091553 | 0.25177 | 0.26093 | 123.056 | 123.0789 | -0.24719 | -0.23346 | 122.7768 | 122.9095 | 122.8271 | 122.905
4351.8438 | 123.1796 | -122.9141 | 0.07782 | -0.0051118 | -0.010952 | -0.07837 | -0.0084743 | -0.034289 | -0.048672 | -0.041887 | -0.0051575 | 0.0040312 | 0.0055712 | -0.01462 | -0.21744 | -0.020264 | -0.020476 | -0.068665 | 0.086975 | -0.10529 | -0.050354 | 0.12817 | -0.073242 | 0.013733 | 0.12817 | 0.10529 | -0.082397 | 0.059509 | 0.14191 | 0.09613 | 0.13275 | 122.8088 | 0.009155 | -0.12817 | 123.0423 | 122.9279 | 122.8409 | 0.11902 | 0.032044 | 122.8317 | 0.027466 | -0.018311 | 123.056 | 123.0469 | 123.0103 | 0.21515 | 0.17853 | 0.23346 | 0.054932 | 0.2243 | 0.14191 | 0.19226 | 0.18768 | 123.0011 | 123.0194 | -0.18311 | -0.16022 | 122.8638 | 122.9736 | 122.8455 | 123.0423
4353.6406 | 123.0927 | -122.9324 | 0.09613 | 0.0025177 | -0.0096707 | -0.076874 | -0.0035611 | -0.029589 | -0.050167 | -0.039965 | 0.0039979 | 0.0042448 | 0.008562 | -0.010561 | -0.22043 | -0.020051 | -0.023467 | -0.12817 | 0.11902 | -0.14191 | -0.1831 | -0.036621 | -0.20142 | -0.10529 | -0.045776 | 0.14191 | -0.11444 | -0.027466 | 0.045776 | -0.022888 | 0.050354 | 122.7905 | 0.022889 | -0.27924 | 122.8958 | 122.8271 | 122.731 | 0.036621 | -0.059509 | 122.818 | 0.045777 | -0.1236 | 122.9782 | 122.9828 | 122.9095 | 0.16479 | 0.091553 | 0.10529 | -0.041198 | 0.16022 | 0.086975 | 0.26093 | 0.25635 | 123.0515 | 123.0743 | -0.23804 | -0.21057 | 122.7493 | 122.905 | 122.8043 | 122.8867
4355.4219 | 123.1522 | -122.905 | 0.091553 | -0.0051118 | -0.011166 | -0.075379 | -0.0042019 | -0.034075 | -0.049954 | -0.04381 | -0.0021057 | 0.0027494 | 0.0081348 | -0.013766 | -0.22022 | -0.01941 | -0.024748 | -0.13275 | 0.11902 | -0.13275 | -0.14191 | 0.013733 | -0.16937 | -0.068665 | 0.009155 | 0.13733 | -0.11902 | 0.036621 | 0.11444 | 0.018311 | 0.10986 | 122.7722 | 0.027466 | -0.23346 | 122.9187 | 122.8363 | 122.7356 | 0.064086 | -0.036622 | 122.7859 | 0.045776 | -0.054932 | 123.0194 | 123.0148 | 122.9233 | 0.22888 | 0.13733 | 0.14648 | -0.009156 | 0.23346 | 0.15564 | 0.25177 | 0.25635 | 123.024 | 123.0423 | -0.2243 | -0.21057 | 122.7631 | 122.9416 | 122.7722 | 122.9141
4357.1562 | 123.2162 | -122.9004 | 0.091553 | 0.0025177 | -0.013943 | -0.078156 | -0.0097561 | -0.031298 | -0.05209 | -0.040178 | 0.00094606 | 0.0010404 | 0.0064258 | -0.015261 | -0.22001 | -0.020905 | -0.019408 | -0.086975 | 0.091553 | -0.11902 | -0.041199 | 0.14191 | -0.022888 | 0.045776 | 0.11444 | 0.10071 | -0.07782 | 0.086975 | 0.21973 | 0.15106 | 0.15564 | 122.7814 | 0 | -0.13275 | 123.0423 | 122.9462 | 122.8775 | 0.16479 | 0.096131 | 122.8226 | 0.009155 | -0.004578 | 123.1201 | 123.056 | 123.0515 | 0.23346 | 0.22888 | 0.26093 | 0.07782 | 0.29755 | 0.16479 | 0.21057 | 0.17853 | 122.9919 | 123.0011 | -0.21057 | -0.16937 | 122.8592 | 122.9874 | 122.8134 | 123.0148
4358.9531 | 123.1247 | -122.9645 | 0.09613 | 0.0025177 | -0.012448 | -0.079651 | -0.0061245 | -0.031511 | -0.051022 | -0.042101 | -0.0021057 | 0.0036038 | 0.0079212 | -0.010775 | -0.21937 | -0.020051 | -0.025389 | -0.11902 | 0.091553 | -0.15106 | -0.15564 | -0.013733 | -0.14648 | -0.073242 | -0.036621 | 0.1236 | -0.10529 | -0.027466 | 0.073242 | 0.032043 | 0.07782 | 122.8134 | -0.004577 | -0.25177 | 122.9507 | 122.8912 | 122.818 | 0.07782 | 0.004578 | 122.8592 | 0.027466 | -0.1236 | 123.0377 | 123.0423 | 122.9965 | 0.18311 | 0.13733 | 0.13733 | -0.004578 | 0.17853 | 0.07782 | 0.24261 | 0.22888 | 123.056 | 123.0881 | -0.24719 | -0.20142 | 122.8088 | 122.937 | 122.8455 | 122.9279
4360.6875 | 123.1613 | -122.9233 | 0.082397 | 0.010147 | -0.013729 | -0.078156 | -0.0082607 | -0.033648 | -0.050167 | -0.043383 | 0.00094606 | 0.002963 | 0.007494 | -0.017184 | -0.21851 | -0.021973 | -0.024535 | -0.11444 | 0.091553 | -0.1236 | -0.10529 | 0.036621 | -0.09613 | -0.009155 | 0.013733 | 0.10071 | -0.086975 | 0.013733 | 0.14191 | 0.068665 | 0.11444 | 122.7997 | 0.009156 | -0.18768 | 122.9599 | 122.9141 | 122.8271 | 0.11444 | 0.027466 | 122.8363 | 0.018311 | -0.068664 | 123.0652 | 123.0377 | 122.9919 | 0.20142 | 0.15564 | 0.16022 | 0.01831 | 0.22888 | 0.10071 | 0.21515 | 0.18768 | 123.0148 | 123.024 | -0.20599 | -0.16937 | 122.818 | 122.937 | 122.8088 | 122.937
4362.4844 | 123.1201 | -122.9141 | 0.10529 | -0.0051118 | -0.010525 | -0.078797 | -0.0061245 | -0.026598 | -0.050595 | -0.040819 | -0.0021057 | 0.0053128 | 0.0087756 | -0.016329 | -0.21979 | -0.018769 | -0.025816 | -0.073242 | 0.10529 | -0.13733 | -0.10529 | 0.045776 | -0.13275 | -0.050354 | 0.032043 | 0.13275 | -0.086975 | 0 | 0.068665 | 0 | 0.073242 | 122.7768 | 0 | -0.21057 | 122.9599 | 122.8638 | 122.7814 | 0.086975 | 0.004578 | 122.8271 | 0.027465 | -0.10529 | 122.9828 | 122.9874 | 122.9141 | 0.16022 | 0.086975 | 0.18311 | 0.032043 | 0.15564 | 0.086975 | 0.24262 | 0.21973 | 123.0194 | 123.0469 | -0.24262 | -0.19226 | 122.8088 | 122.9141 | 122.8409 | 122.9462
4364.2812 | 123.1384 | -122.9462 | 0.11444 | -0.0051118 | -0.010311 | -0.082215 | -0.0074063 | -0.029375 | -0.053158 | -0.042742 | 0.00094606 | 0.0025358 | 0.0079212 | -0.0092798 | -0.21872 | -0.018555 | -0.021117 | -0.09613 | 0.1236 | -0.15106 | -0.1236 | 0.027466 | -0.1236 | -0.064087 | 0.022888 | 0.12817 | -0.11444 | 0.013733 | 0.10071 | 0.036621 | 0.07782 | 122.7951 | 0.009155 | -0.23804 | 122.9736 | 122.8821 | 122.8226 | 0.086975 | 0.027466 | 122.8317 | 0.013733 | -0.10071 | 123.0469 | 123.024 | 122.9828 | 0.19226 | 0.15106 | 0.17853 | 0.027466 | 0.21515 | 0.12817 | 0.27466 | 0.24262 | 123.0698 | 123.0743 | -0.2655 | -0.22888 | 122.8226 | 122.9599 | 122.85 | 122.9691
4366.0156 | 123.0469 | -122.9507 | 0.1236 | -0.0051118 | -0.0094571 | -0.081147 | -0.0044155 | -0.028948 | -0.05209 | -0.038896 | 0.0039979 | 0.0053128 | 0.0087756 | -0.007998 | -0.22107 | -0.020478 | -0.025176 | -0.10529 | 0.10071 | -0.1236 | -0.16937 | -0.032043 | -0.19684 | -0.1236 | -0.068665 | 0.15564 | -0.14648 | -0.050354 | 0.027466 | -0.050354 | 0.027466 | 122.8271 | -0.022888 | -0.29297 | 122.9187 | 122.8271 | 122.7539 | 0 | -0.073242 | 122.8043 | 0.032044 | -0.17395 | 122.9782 | 122.9782 | 122.9004 | 0.17395 | 0.09613 | 0.091553 | -0.045777 | 0.17395 | 0.09613 | 0.2243 | 0.30212 | 123.0515 | 123.1064 | -0.24719 | -0.27008 | 122.7814 | 122.9004 | 122.8455 | 122.8821
4367.8281 | 123.0927 | -122.9279 | 0.1236 | -0.0051118 | -0.012875 | -0.078797 | -0.0063381 | -0.028734 | -0.051876 | -0.042528 | 0.00094606 | 0.0027494 | 0.0092028 | -0.01462 | -0.21872 | -0.02176 | -0.022826 | -0.13275 | 0.12817 | -0.14191 | -0.18768 | -0.036621 | -0.15564 | -0.082397 | -0.050354 | 0.13733 | -0.12817 | -0.050354 | 0.059509 | -0.004578 | 0.054932 | 122.7859 | 0.004578 | -0.31128 | 122.8912 | 122.8455 | 122.7722 | 0.05951 | -0.013733 | 122.7997 | 0.013733 | -0.17395 | 122.9874 | 122.9828 | 122.9233 | 0.18311 | 0.1236 | 0.10529 | -0.045776 | 0.18768 | 0.07782 | 0.27008 | 0.2655 | 123.056 | 123.0652 | -0.2655 | -0.25177 | 122.7402 | 122.8775 | 122.7951 | 122.8775
4369.5781 | 123.1064 | -122.9462 | 0.1236 | -0.0051118 | -0.013729 | -0.079651 | -0.0093289 | -0.030443 | -0.05209 | -0.038256 | -0.0021057 | 0.0031766 | 0.0096302 | -0.015902 | -0.21851 | -0.020264 | -0.024535 | -0.16022 | 0.11902 | -0.14648 | -0.17853 | -0.004578 | -0.14191 | -0.068665 | -0.045776 | 0.13275 | -0.13275 | -0.064087 | 0.054932 | -0.004578 | 0.041199 | 122.7997 | -0.004577 | -0.30212 | 122.9416 | 122.8775 | 122.8043 | 0.077819 | 0.004577 | 122.8134 | 0.009155 | -0.18768 | 123.0011 | 122.9874 | 122.9416 | 0.17395 | 0.12817 | 0.14191 | -0.032044 | 0.18768 | 0.068664 | 0.2655 | 0.2655 | 123.0652 | 123.0789 | -0.27008 | -0.25635 | 122.7676 | 122.8821 | 122.7859 | 122.9004
4371.3594 | 123.1934 | -122.9233 | 0.1236 | -0.0051118 | -0.01202 | -0.079438 | -0.0076199 | -0.029802 | -0.051022 | -0.041246 | 0.0039979 | 0.002963 | 0.007494 | -0.018466 | -0.21958 | -0.018769 | -0.018553 | -0.11902 | 0.086975 | -0.10986 | -0.10986 | 0.068665 | -0.10071 | 0 | 0.027466 | 0.09613 | -0.09613 | 0.041199 | 0.15564 | 0.091553 | 0.11902 | 122.8134 | -0.036621 | -0.23346 | 122.9919 | 122.9233 | 122.8226 | 0.10986 | 0.009155 | 122.8271 | -0.027466 | -0.082397 | 123.0789 | 123.0423 | 123.0148 | 0.21515 | 0.18768 | 0.17853 | 0 | 0.25177 | 0.13733 | 0.19684 | 0.19226 | 123.0103 | 123.0194 | -0.23346 | -0.21973 | 122.8134 | 122.9645 | 122.8043 | 122.9507
4373.1562 | 123.23 | -122.8958 | 0.086975 | -0.0051118 | -0.01138 | -0.07837 | -0.0056973 | -0.023607 | -0.049526 | -0.042528 | -0.0021057 | 0.0023222 | 0.0092028 | -0.016757 | -0.22172 | -0.019623 | -0.024107 | -0.045776 | 0.086975 | -0.091553 | -0.050354 | 0.11444 | -0.059509 | 0 | 0.11902 | 0.09613 | -0.07782 | 0.10529 | 0.16937 | 0.10986 | 0.16022 | 122.8043 | 0 | -0.13733 | 123.0103 | 122.8958 | 122.8363 | 0.091553 | 0.032044 | 122.818 | 0.009155 | 0.018311 | 123.0652 | 123.056 | 123.0057 | 0.23804 | 0.18768 | 0.20599 | 0.041199 | 0.24719 | 0.18311 | 0.17853 | 0.17395 | 122.9828 | 122.9919 | -0.17853 | -0.16479 | 122.8455 | 123.0011 | 122.85 | 123.0148
4374.9531 | 123.0743 | -122.9691 | 0.12817 | 0.0025177 | -0.01138 | -0.077729 | -0.0031337 | -0.026598 | -0.048672 | -0.041887 | -0.0021057 | 0.0053128 | 0.0064258 | -0.017397 | -0.21937 | -0.018342 | -0.021971 | -0.11444 | 0.10529 | -0.13275 | -0.15564 | -0.013733 | -0.19226 | -0.10071 | -0.050354 | 0.14648 | -0.11444 | -0.045776 | 0.027466 | -0.036621 | 0.036621 | 122.8363 | -0.022888 | -0.28381 | 122.9553 | 122.8683 | 122.7768 | 0.032043 | -0.05951 | 122.8546 | 0.01831 | -0.17395 | 122.9965 | 123.0057 | 122.9324 | 0.15106 | 0.07782 | 0.11902 | -0.022889 | 0.14191 | 0.068665 | 0.23804 | 0.26093 | 123.0743 | 123.1155 | -0.26093 | -0.24262 | 122.8134 | 122.9233 | 122.8546 | 122.9187
4376.75 | 123.0881 | -122.9462 | 0.12817 | 0.0025177 | -0.0073209 | -0.079011 | -0.0048427 | -0.031511 | -0.048672 | -0.041246 | -0.0021057 | 0.0036038 | 0.0092028 | -0.013979 | -0.2215 | -0.019196 | -0.023467 | -0.11902 | 0.11444 | -0.11444 | -0.17853 | -0.050354 | -0.20142 | -0.13275 | -0.082397 | 0.1236 | -0.12817 | -0.041199 | 0.018311 | -0.032043 | 0.050354 | 122.8317 | -0.013733 | -0.3067 | 122.8958 | 122.8134 | 122.7448 | -0.01831 | -0.086975 | 122.818 | -0.004578 | -0.16937 | 122.9645 | 122.9965 | 122.9141 | 0.17853 | 0.096131 | 0.064087 | -0.064087 | 0.14649 | 0.086975 | 0.22888 | 0.25177 | 123.0606 | 123.0698 | -0.24262 | -0.25635 | 122.7676 | 122.905 | 122.8271 | 122.8638
4378.5 | 123.0698 | -122.9782 | 0.11444 | -0.012741 | -0.0088163 | -0.078156 | -0.0044155 | -0.025957 | -0.048458 | -0.041033 | 0.00094606 | 0.0038174 | 0.0096302 | -0.013339 | -0.22107 | -0.018128 | -0.024107 | -0.11902 | 0.11444 | -0.13733 | -0.16022 | -0.027466 | -0.19226 | -0.10071 | -0.07782 | 0.15106 | -0.11444 | -0.045776 | 0.022888 | -0.054932 | 0.032043 | 122.8409 | 0 | -0.27466 | 122.9507 | 122.8775 | 122.7859 | 0.036621 | -0.054932 | 122.8638 | 0.036621 | -0.16022 | 123.0011 | 123.0103 | 122.9233 | 0.14648 | 0.059509 | 0.10986 | -0.022888 | 0.13733 | 0.068665 | 0.25177 | 0.2655 | 123.0927 | 123.1293 | -0.25177 | -0.22888 | 122.818 | 122.9324 | 122.8592 | 122.9004
4380.2969 | 123.1338 | -122.9599 | 0.11444 | 0.010147 | -0.012875 | -0.077302 | -0.0054837 | -0.031298 | -0.050167 | -0.040605 | -0.0021057 | 0.0053128 | 0.0072802 | -0.010134 | -0.21744 | -0.018342 | -0.025176 | -0.10071 | 0.10986 | -0.14648 | -0.10986 | 0.050354 | -0.1236 | -0.054932 | 0.041199 | 0.13733 | -0.10529 | 0.004578 | 0.07782 | 0.013733 | 0.068665 | 122.8134 | -0.004578 | -0.2243 | 123.0103 | 122.905 | 122.8363 | 0.091552 | 0.022888 | 122.8546 | 0.022888 | -0.10986 | 123.0377 | 123.0286 | 122.9736 | 0.17395 | 0.11902 | 0.19684 | 0.036621 | 0.18311 | 0.10986 | 0.25635 | 0.24262 | 123.0698 | 123.0972 | -0.26093 | -0.21973 | 122.85 | 122.9645 | 122.8592 | 123.0011
4382.0156 | 123.1705 | -122.9462 | 0.10071 | 0.0025177 | -0.01437 | -0.079865 | -0.011892 | -0.028093 | -0.049099 | -0.041246 | 0.00094606 | 0.00039959 | 0.0079212 | -0.015902 | -0.21915 | -0.021546 | -0.022826 | -0.073242 | 0.068665 | -0.11902 | -0.054932 | 0.1236 | -0.036621 | 0.022888 | 0.082397 | 0.10071 | -0.09613 | 0.036621 | 0.15106 | 0.091553 | 0.11444 | 122.8271 | -0.032043 | -0.15564 | 123.0698 | 122.9691 | 122.9095 | 0.14191 | 0.082398 | 122.85 | 0 | -0.064087 | 123.0972 | 123.0606 | 123.0377 | 0.21057 | 0.18768 | 0.24261 | 0.064087 | 0.24719 | 0.13275 | 0.18768 | 0.19684 | 123.0148 | 123.0469 | -0.21973 | -0.19684 | 122.8912 | 122.9828 | 122.8729 | 123.0286
4383.8125 | 123.175 | -122.937 | 0.10529 | -0.0051118 | -0.01437 | -0.079438 | -0.0074063 | -0.032793 | -0.049954 | -0.040178 | -0.0021057 | -2.7806e-05 | 0.0064258 | -0.018466 | -0.21958 | -0.020905 | -0.02133 | -0.10529 | 0.09613 | -0.10529 | -0.09613 | 0.082397 | -0.10071 | 0 | 0.041199 | 0.11444 | -0.10071 | 0.022888 | 0.13275 | 0.068665 | 0.10529 | 122.8317 | -0.009156 | -0.20142 | 123.0194 | 122.937 | 122.8363 | 0.10529 | 0.004578 | 122.8363 | 0.009155 | -0.082398 | 123.0698 | 123.0423 | 123.0057 | 0.20599 | 0.16937 | 0.18768 | 0.009156 | 0.23346 | 0.1236 | 0.20142 | 0.21515 | 123.0331 | 123.0515 | -0.21057 | -0.20599 | 122.8409 | 122.9599 | 122.8317 | 122.9782
4385.5469 | 123.0972 | -122.9507 | 0.13275 | -0.0051118 | -0.0088163 | -0.079011 | -0.0050565 | -0.03023 | -0.051449 | -0.042314 | 0.00094606 | 0.0044584 | 0.0083484 | -0.0090662 | -0.21937 | -0.017487 | -0.022398 | -0.082397 | 0.09613 | -0.12817 | -0.13275 | 0.004578 | -0.16479 | -0.091553 | -0.009155 | 0.14191 | -0.10529 | -0.032043 | 0.036621 | -0.027466 | 0.054932 | 122.8226 | -0.036621 | -0.2655 | 122.9553 | 122.8592 | 122.7859 | 0.036621 | -0.036621 | 122.8455 | 0.009156 | -0.16479 | 122.9874 | 123.0057 | 122.9233 | 0.16022 | 0.07782 | 0.13275 | -0.004577 | 0.14191 | 0.073243 | 0.2243 | 0.24719 | 123.0469 | 123.0927 | -0.26093 | -0.23804 | 122.818 | 122.9187 | 122.8683 | 122.9416
4387.3438 | 123.23 | -122.9279 | 0.086975 | -0.0051118 | -0.010739 | -0.078583 | -0.0052701 | -0.028093 | -0.048245 | -0.042742 | 0.00094606 | 0.0025358 | 0.0077076 | -0.011416 | -0.22043 | -0.017701 | -0.020049 | -0.09613 | 0.09613 | -0.11444 | -0.086975 | 0.050354 | -0.13275 | -0.032043 | 0.091553 | 0.11902 | -0.091553 | 0.07782 | 0.16479 | 0.09613 | 0.16479 | 122.8134 | 0.009155 | -0.17395 | 122.9782 | 122.8958 | 122.7951 | 0.082398 | -0.01831 | 122.8363 | 0.032044 | -0.009155 | 123.0927 | 123.0927 | 123.024 | 0.25635 | 0.18768 | 0.16479 | 0.027466 | 0.25635 | 0.16937 | 0.21057 | 0.21057 | 123.024 | 123.0469 | -0.20142 | -0.17853 | 122.8409 | 123.0057 | 122.8317 | 123.0194
4389.0781 | 123.2071 | -122.9141 | 0.10071 | -0.0051118 | -0.015225 | -0.078583 | -0.0078335 | -0.033648 | -0.051022 | -0.040819 | 0.0039979 | 0.0023222 | 0.007494 | -0.016757 | -0.21937 | -0.01941 | -0.024962 | -0.064087 | 0.07782 | -0.10986 | -0.022888 | 0.14191 | -0.027466 | 0.041199 | 0.11444 | 0.091553 | -0.091553 | 0.059509 | 0.1831 | 0.12817 | 0.13733 | 122.8043 | -0.022888 | -0.1236 | 123.056 | 122.9553 | 122.8867 | 0.15106 | 0.082397 | 122.8226 | -0.009155 | -0.041199 | 123.0972 | 123.0515 | 123.0423 | 0.22888 | 0.21973 | 0.25177 | 0.086975 | 0.27466 | 0.15106 | 0.18768 | 0.18311 | 122.9919 | 123.0057 | -0.21057 | -0.19226 | 122.8912 | 122.9736 | 122.85 | 123.0286
4390.875 | 123.0789 | -122.9233 | 0.12817 | -0.0051118 | -0.010098 | -0.076661 | -0.0039883 | -0.028307 | -0.048886 | -0.042101 | -0.0021057 | 0.0018948 | 0.0081348 | -0.0088526 | -0.22065 | -0.019196 | -0.022612 | -0.1236 | 0.11902 | -0.13275 | -0.16937 | -0.045776 | -0.19226 | -0.10986 | -0.073242 | 0.14191 | -0.13733 | -0.059509 | 0.013733 | -0.059509 | 0.045776 | 122.7905 | -0.009155 | -0.29755 | 122.8775 | 122.8134 | 122.731 | 0.022888 | -0.05951 | 122.7859 | 0.013733 | -0.18768 | 122.937 | 122.9691 | 122.8638 | 0.18311 | 0.07782 | 0.086975 | -0.036622 | 0.15106 | 0.07782 | 0.25177 | 0.27924 | 123.0423 | 123.0652 | -0.26093 | -0.2655 | 122.7539 | 122.8638 | 122.7997 | 122.85
4392.6094 | 123.1842 | -122.9416 | 0.11444 | 0.0025177 | -0.012875 | -0.08136 | -0.0084743 | -0.030657 | -0.051663 | -0.039324 | 0.00094606 | 0.0014676 | 0.0072802 | -0.01462 | -0.22022 | -0.02176 | -0.022398 | -0.068665 | 0.064087 | -0.10071 | -0.045776 | 0.11902 | -0.036621 | 0.018311 | 0.086975 | 0.11444 | -0.086975 | 0.018311 | 0.14191 | 0.082397 | 0.11902 | 122.8409 | -0.050354 | -0.16022 | 123.0606 | 122.9599 | 122.905 | 0.11902 | 0.064087 | 122.8546 | 0 | -0.09613 | 123.0835 | 123.0606 | 123.024 | 0.20599 | 0.16937 | 0.21973 | 0.054932 | 0.22888 | 0.10529 | 0.1648 | 0.20142 | 123.0057 | 123.056 | -0.21515 | -0.20142 | 122.8958 | 122.9599 | 122.8729 | 123.0286
4394.4219 | 123.2391 | -122.9187 | 0.091553 | -0.0051118 | -0.01138 | -0.077302 | -0.0042019 | -0.027239 | -0.049099 | -0.041246 | 0.00094606 | 0.0018948 | 0.0077076 | -0.0060754 | -0.21872 | -0.018128 | -0.025389 | -0.064087 | 0.091553 | -0.11902 | -0.054932 | 0.11444 | -0.073242 | 0 | 0.10529 | 0.09613 | -0.068665 | 0.09613 | 0.16937 | 0.10071 | 0.16937 | 122.7997 | 0 | -0.14649 | 123.0331 | 122.9187 | 122.8455 | 0.11902 | 0.045777 | 122.85 | 0.004577 | 0.004577 | 123.0881 | 123.0881 | 123.0194 | 0.23804 | 0.16937 | 0.23346 | 0.064087 | 0.23804 | 0.16479 | 0.21057 | 0.16479 | 123.0103 | 123.0148 | -0.21057 | -0.16022 | 122.8638 | 123.0148 | 122.8546 | 123.024
4396.2031 | 123.111 | -122.9553 | 0.1236 | -0.0051118 | -0.015652 | -0.077942 | -0.0044155 | -0.028734 | -0.050595 | -0.04146 | 0.00094606 | 0.0031766 | 0.0077076 | -0.014193 | -0.21979 | -0.018555 | -0.02368 | -0.14648 | 0.1236 | -0.13275 | -0.17853 | -0.032043 | -0.15106 | -0.086975 | -0.054932 | 0.13275 | -0.12817 | -0.041199 | 0.059509 | -0.004578 | 0.064087 | 122.8226 | 0 | -0.30212 | 122.9233 | 122.8683 | 122.8043 | 0.045776 | -0.018311 | 122.8271 | 0.009155 | -0.16479 | 123.0148 | 123.0194 | 122.9507 | 0.19226 | 0.1236 | 0.10071 | -0.045777 | 0.18768 | 0.086975 | 0.25635 | 0.26093 | 123.0789 | 123.0881 | -0.25635 | -0.25177 | 122.7768 | 122.9141 | 122.8088 | 122.9004
4398 | 123.2346 | -122.9187 | 0.086975 | 0.010147 | -0.014584 | -0.079865 | -0.0065517 | -0.03258 | -0.049526 | -0.039751 | -0.0021057 | -0.001523 | 0.0072802 | -0.018679 | -0.22001 | -0.021119 | -0.023894 | -0.054932 | 0.073242 | -0.086975 | -0.036621 | 0.16479 | -0.027466 | 0.041199 | 0.13275 | 0.091553 | -0.073242 | 0.068665 | 0.20599 | 0.13733 | 0.15564 | 122.8317 | -0.013733 | -0.1236 | 123.0835 | 122.9599 | 122.8912 | 0.12817 | 0.059509 | 122.8455 | 0.004578 | -0.01831 | 123.1247 | 123.0743 | 123.056 | 0.22888 | 0.21057 | 0.25177 | 0.050354 | 0.27924 | 0.14191 | 0.16022 | 0.16479 | 122.9919 | 123.0103 | -0.17395 | -0.16022 | 122.8821 | 122.9874 | 122.8638 | 123.0515
4399.7969 | 123.2025 | -122.9324 | 0.07782 | -0.012741 | -0.010739 | -0.076874 | -0.0039883 | -0.028307 | -0.049099 | -0.039324 | -0.0021057 | 0.0031766 | 0.0064258 | -0.0067162 | -0.22065 | -0.020264 | -0.023039 | -0.11902 | 0.10529 | -0.1236 | -0.1236 | 0.018311 | -0.16479 | -0.045776 | 0.054932 | 0.10986 | -0.10529 | 0.059509 | 0.14191 | 0.073242 | 0.1236 | 122.8088 | 0.027466 | -0.20142 | 122.9507 | 122.8867 | 122.7676 | 0.07782 | -0.041199 | 122.8271 | 0.032043 | -0.018311 | 123.0743 | 123.056 | 123.0057 | 0.22888 | 0.17853 | 0.14191 | 0 | 0.24719 | 0.16479 | 0.22888 | 0.21515 | 123.0377 | 123.0423 | -0.20142 | -0.18311 | 122.8088 | 122.9919 | 122.8134 | 122.9874
4401.5938 | 123.2208 | -122.9233 | 0.07782 | 0.0025177 | -0.015225 | -0.079651 | -0.0071927 | -0.031725 | -0.051663 | -0.038042 | 0.00094606 | 0.0027494 | 0.008562 | -0.018893 | -0.22022 | -0.020691 | -0.025389 | -0.073242 | 0.082397 | -0.082397 | -0.018311 | 0.13733 | -0.009155 | 0.027466 | 0.10529 | 0.10986 | -0.082397 | 0.082397 | 0.19226 | 0.12817 | 0.14191 | 122.8409 | 0.004577 | -0.096131 | 123.0606 | 122.9507 | 122.9141 | 0.10986 | 0.073242 | 122.8409 | 0.032043 | 0.004577 | 123.1155 | 123.0652 | 123.0515 | 0.2243 | 0.21057 | 0.21973 | 0.064086 | 0.27466 | 0.16479 | 0.16479 | 0.19226 | 123.0057 | 123.0331 | -0.16022 | -0.16022 | 122.905 | 123.0057 | 122.85 | 123.0286
4403.3438 | 123.1888 | -122.9279 | 0.09613 | 0.0025177 | -0.01437 | -0.078156 | -0.010611 | -0.035998 | -0.048886 | -0.041887 | -0.0051575 | 0.0018948 | 0.0062122 | -0.015048 | -0.21937 | -0.0224 | -0.022185 | -0.10529 | 0.073242 | -0.10986 | -0.086975 | 0.059509 | -0.10071 | -0.009155 | 0.032043 | 0.10986 | -0.10986 | 0.022888 | 0.13733 | 0.068665 | 0.10071 | 122.818 | -0.022888 | -0.1831 | 122.9874 | 122.9187 | 122.8271 | 0.10071 | 0.009155 | 122.818 | 0.013733 | -0.073242 | 123.0652 | 123.0286 | 122.9965 | 0.21057 | 0.17853 | 0.16937 | 0.022888 | 0.24719 | 0.13275 | 0.18311 | 0.21973 | 123.0011 | 123.0377 | -0.20599 | -0.20599 | 122.8409 | 122.9507 | 122.8226 | 122.9599
4405.1406 | 123.1155 | -122.9691 | 0.1236 | 0.010147 | -0.014157 | -0.08136 | -0.0091153 | -0.032793 | -0.051235 | -0.04146 | -0.0051575 | 0.0014676 | 0.0053576 | -0.014193 | -0.22086 | -0.020905 | -0.024107 | -0.10071 | 0.11444 | -0.12817 | -0.12817 | 0.032043 | -0.11444 | -0.041199 | 0 | 0.13733 | -0.13275 | -0.032043 | 0.068665 | 0.004578 | 0.041199 | 122.8409 | -0.009155 | -0.25177 | 123.0011 | 122.9279 | 122.8546 | 0.086975 | 0.013733 | 122.8363 | 0.013733 | -0.15564 | 123.0377 | 123.0103 | 122.9736 | 0.17395 | 0.13733 | 0.16022 | 0 | 0.20142 | 0.10071 | 0.24262 | 0.27008 | 123.0835 | 123.1064 | -0.25177 | -0.25635 | 122.8409 | 122.937 | 122.8683 | 122.9691
4406.875 | 123.2346 | -122.937 | 0.086975 | -0.0051118 | -0.0090299 | -0.079438 | -0.0069791 | -0.030871 | -0.049526 | -0.040392 | -0.0021057 | 0.0048856 | 0.007494 | -0.012698 | -0.22043 | -0.020051 | -0.022398 | -0.041199 | 0.064087 | -0.10986 | -0.036621 | 0.10986 | -0.064087 | 0.018311 | 0.11902 | 0.10071 | -0.082397 | 0.11902 | 0.18768 | 0.10986 | 0.16022 | 122.8271 | -0.022888 | -0.1236 | 123.0469 | 122.9553 | 122.8729 | 0.12817 | 0.045776 | 122.8546 | 0.013733 | 0.032044 | 123.1247 | 123.0972 | 123.0469 | 0.24261 | 0.19226 | 0.21973 | 0.073242 | 0.27008 | 0.20142 | 0.17395 | 0.18311 | 123.0011 | 123.0377 | -0.19684 | -0.16937 | 122.9004 | 123.056 | 122.8958 | 123.056
4408.6719 | 123.1384 | -122.9736 | 0.11444 | 0.0025177 | -0.014798 | -0.080292 | -0.0059109 | -0.029375 | -0.052944 | -0.041246 | 0.00094606 | 0.0055264 | 0.0059986 | -0.0050072 | -0.21958 | -0.017701 | -0.022826 | -0.12817 | 0.12817 | -0.14191 | -0.16937 | -0.022888 | -0.16022 | -0.086975 | -0.054932 | 0.1236 | -0.1236 | -0.036621 | 0.064087 | 0 | 0.059509 | 122.8317 | 0.013733 | -0.28381 | 122.9507 | 122.8867 | 122.8134 | 0.054932 | -0.01831 | 122.85 | 0.009155 | -0.15106 | 123.0377 | 123.0331 | 122.9736 | 0.1831 | 0.1236 | 0.11902 | -0.027466 | 0.18768 | 0.086975 | 0.27008 | 0.24719 | 123.1018 | 123.0972 | -0.25635 | -0.23804 | 122.8043 | 122.937 | 122.8455 | 122.9187
4410.4688 | 123.2346 | -122.9233 | 0.082397 | -0.0051118 | -0.010098 | -0.077729 | -0.0076199 | -0.026812 | -0.049526 | -0.041674 | -0.0021057 | 0.0025358 | 0.0083484 | -0.016757 | -0.21958 | -0.022187 | -0.02133 | -0.045776 | 0.086975 | -0.091553 | -0.027466 | 0.12817 | -0.064087 | 0.022888 | 0.12817 | 0.09613 | -0.068665 | 0.082397 | 0.16937 | 0.11444 | 0.14191 | 122.8317 | 0.004578 | -0.10986 | 123.0515 | 122.9462 | 122.8592 | 0.11444 | 0.027466 | 122.8546 | 0.013733 | 0 | 123.0927 | 123.0652 | 123.0377 | 0.21057 | 0.18311 | 0.21973 | 0.064087 | 0.23804 | 0.15106 | 0.17853 | 0.16479 | 123.0103 | 123.0194 | -0.17395 | -0.15106 | 122.8958 | 123.0057 | 122.8775 | 123.0515
4412.25 | 123.1338 | -122.9645 | 0.11902 | -0.0051118 | -0.012661 | -0.078156 | -0.0063381 | -0.029375 | -0.051663 | -0.041887 | -0.0051575 | 0.0025358 | 0.0077076 | -0.013125 | -0.22065 | -0.020905 | -0.022612 | -0.10529 | 0.1236 | -0.13275 | -0.12817 | 0.009155 | -0.11902 | -0.050354 | -0.004578 | 0.13275 | -0.10071 | 0 | 0.11444 | 0.027466 | 0.07782 | 122.8317 | 0.004577 | -0.24719 | 122.9736 | 122.9141 | 122.8455 | 0.082397 | 0.013732 | 122.8638 | 0.013732 | -0.11902 | 123.0789 | 123.0423 | 122.9919 | 0.17853 | 0.12817 | 0.14191 | 0.004577 | 0.21515 | 0.10071 | 0.25635 | 0.23346 | 123.0881 | 123.0972 | -0.25177 | -0.21973 | 122.8363 | 122.9645 | 122.8592 | 122.9599
4414 | 123.111 | -122.9874 | 0.13275 | -0.02037 | -0.013089 | -0.079011 | -0.0069791 | -0.034502 | -0.048672 | -0.043596 | -0.0021057 | 0.0040312 | 0.007494 | -0.013552 | -0.22022 | -0.020478 | -0.023467 | -0.11902 | 0.10986 | -0.1236 | -0.13733 | 0.018311 | -0.13275 | -0.073242 | -0.032043 | 0.1236 | -0.11902 | -0.050354 | 0.068665 | 0.009155 | 0.032043 | 122.8638 | -0.022888 | -0.27008 | 123.0057 | 122.9141 | 122.8546 | 0.050354 | -0.009155 | 122.8683 | -0.009155 | -0.18311 | 123.056 | 123.0194 | 122.9965 | 0.15106 | 0.12817 | 0.14191 | -0.013733 | 0.18768 | 0.068665 | 0.23346 | 0.24261 | 123.0972 | 123.111 | -0.25635 | -0.25177 | 122.85 | 122.937 | 122.8683 | 122.9553
4415.7969 | 123.1064 | -122.9553 | 0.11444 | -0.0051118 | -0.016293 | -0.079865 | -0.0050565 | -0.027453 | -0.050595 | -0.041887 | -0.0021057 | -0.00066861 | 0.0089892 | -0.01227 | -0.21851 | -0.021973 | -0.022612 | -0.091553 | 0.086975 | -0.10529 | -0.11444 | 0.054932 | -0.091553 | -0.032043 | 0 | 0.1236 | -0.10986 | -0.032043 | 0.068665 | 0.018311 | 0.064087 | 122.85 | -0.027466 | -0.22888 | 123.0103 | 122.9233 | 122.8638 | 0.073243 | 0.013733 | 122.8455 | 0.009155 | -0.14648 | 123.024 | 123.0194 | 122.9736 | 0.17395 | 0.12817 | 0.16022 | -0.009155 | 0.17853 | 0.07782 | 0.19226 | 0.23346 | 123.0423 | 123.0789 | -0.21973 | -0.2243 | 122.8409 | 122.9233 | 122.8638 | 122.9553
4417.6094 | 123.2346 | -122.9279 | 0.091553 | -0.012741 | -0.010525 | -0.077302 | -0.0048427 | -0.031084 | -0.04974 | -0.038896 | 0.00094606 | 0.0010404 | 0.0089892 | -0.01462 | -0.21915 | -0.020478 | -0.020903 | -0.064087 | 0.09613 | -0.09613 | -0.050354 | 0.10071 | -0.082397 | 0 | 0.10986 | 0.10071 | -0.091553 | 0.086975 | 0.17853 | 0.09613 | 0.16937 | 122.8317 | 0.004577 | -0.14191 | 123.0286 | 122.9279 | 122.8455 | 0.09613 | 0.013733 | 122.8363 | 0.009155 | -0.004578 | 123.1064 | 123.0972 | 123.024 | 0.26093 | 0.18768 | 0.19684 | 0.045776 | 0.27008 | 0.17853 | 0.19226 | 0.19226 | 123.024 | 123.0286 | -0.18768 | -0.18311 | 122.8775 | 123.0148 | 122.8638 | 123.0377
4419.3438 | 123.1155 | -122.9599 | 0.10071 | -0.0051118 | -0.012448 | -0.077729 | -0.0046291 | -0.031084 | -0.050167 | -0.041246 | -0.0021057 | 0.0040312 | 0.0072802 | -0.0086388 | -0.21937 | -0.018342 | -0.023894 | -0.1236 | 0.1236 | -0.14648 | -0.16937 | -0.032043 | -0.20142 | -0.10529 | -0.050354 | 0.10986 | -0.13275 | -0.013733 | 0.036621 | -0.032043 | 0.059509 | 122.8134 | 0.022888 | -0.27008 | 122.9279 | 122.8546 | 122.7585 | 0.041198 | -0.054932 | 122.8271 | 0.009155 | -0.11444 | 122.9965 | 123.0194 | 122.9279 | 0.19226 | 0.10071 | 0.11444 | -0.022889 | 0.16937 | 0.11902 | 0.27008 | 0.24261 | 123.0835 | 123.0698 | -0.24719 | -0.23346 | 122.7905 | 122.9462 | 122.8363 | 122.9095
4421.125 | 123.1522 | -122.9691 | 0.11902 | 0.010147 | -0.013729 | -0.082001 | -0.0039883 | -0.028307 | -0.049526 | -0.038256 | 0.0039979 | 0.0027494 | 0.0047168 | -0.01697 | -0.21937 | -0.020051 | -0.022398 | -0.12817 | 0.11444 | -0.13275 | -0.16022 | -0.013733 | -0.13733 | -0.07782 | -0.036621 | 0.15106 | -0.1236 | -0.009155 | 0.091553 | 0.018311 | 0.073242 | 122.8363 | -0.004578 | -0.27924 | 122.9553 | 122.8912 | 122.8317 | 0.054931 | -0.004578 | 122.8455 | 0.032043 | -0.12817 | 123.0606 | 123.0423 | 122.9874 | 0.19684 | 0.14191 | 0.11902 | -0.027466 | 0.21515 | 0.11444 | 0.24719 | 0.27466 | 123.0835 | 123.1201 | -0.25177 | -0.24261 | 122.8088 | 122.9599 | 122.8409 | 122.9324
4422.9219 | 123.23 | -122.9141 | 0.086975 | -0.0051118 | -0.01437 | -0.080506 | -0.0095425 | -0.031511 | -0.051663 | -0.043383 | -0.0051575 | 0.0010404 | 0.0047168 | -0.018038 | -0.21872 | -0.020264 | -0.025603 | -0.068665 | 0.082397 | -0.10071 | -0.036621 | 0.14648 | -0.013733 | 0.036621 | 0.09613 | 0.10071 | -0.082397 | 0.073242 | 0.19684 | 0.13733 | 0.13733 | 122.8134 | -0.004578 | -0.1236 | 123.0606 | 122.9507 | 122.9004 | 0.13733 | 0.086975 | 122.8317 | 0.013733 | -0.013733 | 123.111 | 123.0515 | 123.0515 | 0.21973 | 0.21973 | 0.24719 | 0.064087 | 0.27924 | 0.15564 | 0.18311 | 0.18311 | 122.9965 | 123.0148 | -0.18768 | -0.16937 | 122.8775 | 122.9874 | 122.8455 | 123.0103
4424.6562 | 123.2254 | -122.937 | 0.091553 | -0.0051118 | -0.015011 | -0.079438 | -0.0091153 | -0.034075 | -0.051022 | -0.039965 | -0.0051575 | 0.001254 | 0.0066394 | -0.016116 | -0.2215 | -0.01941 | -0.023894 | -0.059509 | 0.086975 | -0.10986 | -0.032043 | 0.14648 | -0.027466 | 0.064087 | 0.10529 | 0.09613 | -0.07782 | 0.082397 | 0.19684 | 0.13733 | 0.14191 | 122.8271 | -0.004578 | -0.1236 | 123.0835 | 123.0011 | 122.9095 | 0.17395 | 0.082397 | 122.8592 | 0.004577 | -0.009156 | 123.1338 | 123.0789 | 123.0743 | 0.21973 | 0.21515 | 0.25635 | 0.07782 | 0.27466 | 0.16022 | 0.19684 | 0.17395 | 123.024 | 123.0331 | -0.20142 | -0.16937 | 122.905 | 123.0194 | 122.8775 | 123.0423
4426.4531 | 123.1155 | -122.9691 | 0.1236 | 0.0025177 | -0.013943 | -0.08136 | -0.0071927 | -0.030657 | -0.050808 | -0.037401 | -0.0021057 | 0.0044584 | 0.0072802 | -0.012911 | -0.22193 | -0.021119 | -0.023039 | -0.15564 | 0.10071 | -0.13733 | -0.16937 | -0.009155 | -0.13733 | -0.07782 | -0.064087 | 0.15564 | -0.11902 | -0.059509 | 0.050354 | -0.009155 | 0.041199 | 122.8317 | -0.022888 | -0.29297 | 122.9599 | 122.8912 | 122.8317 | 0.059509 | 0 | 122.85 | 0.032044 | -0.1831 | 123.0194 | 123.0103 | 122.9599 | 0.16022 | 0.10986 | 0.12817 | -0.032044 | 0.16937 | 0.05951 | 0.23804 | 0.27466 | 123.0698 | 123.1247 | -0.26093 | -0.24261 | 122.7997 | 122.9095 | 122.8134 | 122.905
4428.25 | 123.111 | -123.0011 | 0.13733 | -0.0051118 | -0.012875 | -0.082001 | -0.0089017 | -0.031298 | -0.050167 | -0.039324 | -0.0021057 | 0.002963 | 0.010698 | -0.018893 | -0.21915 | -0.020051 | -0.022826 | -0.10071 | 0.082397 | -0.11902 | -0.14191 | 0.013733 | -0.1236 | -0.068665 | -0.027466 | 0.15106 | -0.10071 | -0.041199 | 0.041199 | 0.004578 | 0.036621 | 122.8821 | -0.054932 | -0.27924 | 123.0148 | 122.9324 | 122.8775 | 0.050354 | -0.004577 | 122.9004 | 0.013733 | -0.17853 | 123.0423 | 123.0377 | 123.0057 | 0.13733 | 0.10529 | 0.13275 | -0.022888 | 0.14191 | 0.059509 | 0.20142 | 0.25177 | 123.0835 | 123.1522 | -0.25635 | -0.23804 | 122.8592 | 122.9599 | 122.9004 | 122.9736
4430.0625 | 123.1064 | -122.9874 | 0.11902 | -0.0051118 | -0.011807 | -0.080506 | -0.0091153 | -0.029589 | -0.050381 | -0.042742 | -0.0021057 | 0.0027494 | 0.0081348 | -0.015902 | -0.2183 | -0.022614 | -0.027098 | -0.12817 | 0.10071 | -0.14648 | -0.16022 | 0.004578 | -0.15564 | -0.073242 | -0.041199 | 0.14191 | -0.11902 | -0.059509 | 0.059509 | -0.004578 | 0.041199 | 122.8409 | -0.018311 | -0.27924 | 122.9919 | 122.9141 | 122.8317 | 0.073242 | -0.009156 | 122.8683 | 0.022888 | -0.17853 | 123.0469 | 123.0286 | 122.9828 | 0.16022 | 0.11444 | 0.15106 | -0.013733 | 0.17853 | 0.05951 | 0.24719 | 0.26093 | 123.0881 | 123.1293 | -0.2655 | -0.23804 | 122.8271 | 122.9279 | 122.8592 | 122.9462
4431.7969 | 123.1659 | -122.937 | 0.10071 | -0.0051118 | -0.0081753 | -0.077515 | -0.0046291 | -0.025744 | -0.050595 | -0.042742 | -0.0021057 | 0.004672 | 0.0072802 | -0.013766 | -0.21958 | -0.020051 | -0.023894 | -0.11444 | 0.10986 | -0.14191 | -0.15564 | -0.004578 | -0.16937 | -0.082397 | 0.009155 | 0.1236 | -0.10071 | 0.022888 | 0.086975 | 0.022888 | 0.09613 | 122.7951 | 0.009155 | -0.25635 | 122.9324 | 122.8546 | 122.7676 | 0.05951 | -0.027466 | 122.8363 | 0.022888 | -0.07782 | 123.024 | 123.0331 | 122.9599 | 0.19684 | 0.1236 | 0.13733 | -0.013733 | 0.18768 | 0.1236 | 0.25177 | 0.2243 | 123.0469 | 123.0606 | -0.24262 | -0.20142 | 122.7814 | 122.9599 | 122.8226 | 122.9462
4433.5938 | 123.1613 | -122.9462 | 0.10986 | 0.0025177 | -0.012234 | -0.07837 | -0.0014249 | -0.032366 | -0.051235 | -0.039537 | -0.0021057 | 0.0033902 | 0.0079212 | -0.011202 | -0.21872 | -0.01941 | -0.025176 | -0.082397 | 0.10071 | -0.12817 | -0.10071 | 0.054932 | -0.11444 | -0.041199 | 0.045776 | 0.11902 | -0.10529 | 0.022888 | 0.082397 | 0.032043 | 0.086975 | 122.818 | -0.009155 | -0.21057 | 123.0011 | 122.905 | 122.8317 | 0.086975 | 0.013733 | 122.8409 | 0.009156 | -0.086975 | 123.0286 | 123.0331 | 122.9782 | 0.19226 | 0.13733 | 0.18311 | 0.027466 | 0.18768 | 0.12817 | 0.22888 | 0.22431 | 123.0469 | 123.0652 | -0.23804 | -0.21515 | 122.8455 | 122.9691 | 122.8638 | 122.9919
4435.3906 | 123.1247 | -122.9828 | 0.11902 | -0.0051118 | -0.013089 | -0.079224 | -0.0082607 | -0.025316 | -0.050595 | -0.041887 | -0.0021057 | 0.0031766 | 0.010485 | -0.012911 | -0.2168 | -0.019837 | -0.021971 | -0.14648 | 0.1236 | -0.15106 | -0.17853 | -0.013733 | -0.16022 | -0.073242 | -0.045776 | 0.13733 | -0.1236 | -0.045776 | 0.068665 | 0.004578 | 0.050354 | 122.8317 | 0.004577 | -0.29755 | 122.9691 | 122.9095 | 122.8226 | 0.07782 | -0.009155 | 122.8592 | 0.01831 | -0.16479 | 123.0515 | 123.0331 | 122.9874 | 0.17395 | 0.12817 | 0.13733 | -0.027466 | 0.19226 | 0.07782 | 0.27466 | 0.26093 | 123.1064 | 123.1201 | -0.27008 | -0.24261 | 122.8043 | 122.937 | 122.8363 | 122.937
4437.1094 | 123.1659 | -122.9599 | 0.12817 | 0.010147 | -0.013302 | -0.079224 | -0.0061245 | -0.032366 | -0.050381 | -0.041033 | -0.0051575 | 0.0031766 | 0.0087756 | -0.014193 | -0.22001 | -0.020264 | -0.023253 | -0.12817 | 0.12817 | -0.15106 | -0.14648 | 0 | -0.1236 | -0.064087 | -0.022888 | 0.1236 | -0.11902 | -0.004578 | 0.09613 | 0.013733 | 0.07782 | 122.8088 | 0 | -0.27466 | 122.9599 | 122.8958 | 122.8363 | 0.086975 | 0.027466 | 122.8409 | -0.004578 | -0.13275 | 123.056 | 123.0377 | 122.9736 | 0.19684 | 0.13275 | 0.15106 | 0.004578 | 0.21515 | 0.11444 | 0.27924 | 0.24261 | 123.0881 | 123.0835 | -0.27924 | -0.24719 | 122.8134 | 122.9553 | 122.8317 | 122.937
4438.9062 | 123.1888 | -122.9507 | 0.073242 | 0.0025177 | -0.013089 | -0.077729 | -0.0071927 | -0.031939 | -0.049099 | -0.041246 | 0.00094606 | 0.0010404 | 0.0077076 | -0.015902 | -0.21851 | -0.022187 | -0.027098 | -0.068665 | 0.068665 | -0.09613 | -0.073242 | 0.1236 | -0.086975 | 0.004578 | 0.10071 | 0.12817 | -0.091553 | 0.059509 | 0.14648 | 0.086975 | 0.11444 | 122.8546 | -0.004577 | -0.14648 | 123.0743 | 122.9553 | 122.8638 | 0.10071 | 0.009155 | 122.8592 | 0.054932 | -0.013733 | 123.0972 | 123.0652 | 123.0377 | 0.20599 | 0.17853 | 0.21973 | 0.022888 | 0.23804 | 0.15106 | 0.16479 | 0.21973 | 123.0194 | 123.0789 | -0.16937 | -0.16479 | 122.8775 | 123.0103 | 122.8821 | 123.0515
4440.6406 | 123.2208 | -122.9416 | 0.07782 | -0.012741 | -0.010311 | -0.07602 | -0.0050565 | -0.028521 | -0.051449 | -0.043596 | -0.0051575 | 0.001254 | 0.0070666 | -0.01163 | -0.22107 | -0.020478 | -0.021971 | -0.050354 | 0.086975 | -0.09613 | -0.022888 | 0.13275 | -0.064087 | 0.018311 | 0.11902 | 0.11902 | -0.082397 | 0.086975 | 0.15106 | 0.10071 | 0.14648 | 122.8455 | 0.009155 | -0.10071 | 123.0743 | 122.9599 | 122.8775 | 0.11444 | 0.032043 | 122.8592 | 0.041199 | 0.009155 | 123.0927 | 123.0881 | 123.0423 | 0.22888 | 0.18311 | 0.22888 | 0.073242 | 0.23346 | 0.16937 | 0.1831 | 0.20142 | 123.0286 | 123.0606 | -0.17395 | -0.16022 | 122.9187 | 123.0286 | 122.8912 | 123.0606
4442.4219 | 123.1842 | -122.9645 | 0.091553 | 0.010147 | -0.012661 | -0.079011 | -0.0076199 | -0.028521 | -0.051876 | -0.040605 | -0.0021057 | 0.0018948 | 0.0062122 | -0.016329 | -0.22043 | -0.020905 | -0.020689 | -0.10529 | 0.07782 | -0.10529 | -0.091553 | 0.054932 | -0.09613 | -0.018311 | 0.041199 | 0.10529 | -0.10529 | 0.027466 | 0.11444 | 0.064087 | 0.10986 | 122.8592 | -0.013733 | -0.18311 | 123.0194 | 122.9462 | 122.8683 | 0.086975 | 0.009156 | 122.8592 | 0.013733 | -0.064087 | 123.0789 | 123.0743 | 123.0286 | 0.21515 | 0.16937 | 0.16022 | 0.013733 | 0.21973 | 0.13275 | 0.18311 | 0.21057 | 123.0423 | 123.0698 | -0.19684 | -0.19684 | 122.8729 | 122.9919 | 122.8592 | 123.0057
4444.2188 | 123.1247 | -122.9874 | 0.12817 | 0.010147 | -0.013729 | -0.080933 | -0.0056973 | -0.033434 | -0.050595 | -0.041887 | -0.0021057 | 0.0048856 | 0.006853 | -0.015261 | -0.22065 | -0.019837 | -0.027098 | -0.12817 | 0.11444 | -0.14648 | -0.16022 | -0.018311 | -0.14648 | -0.07782 | -0.045776 | 0.14191 | -0.11902 | -0.036621 | 0.082397 | -0.004578 | 0.054932 | 122.8409 | -0.013733 | -0.28839 | 122.9691 | 122.9095 | 122.8409 | 0.068664 | 0 | 122.8683 | 0.013733 | -0.1648 | 123.0698 | 123.0423 | 122.9828 | 0.17395 | 0.11444 | 0.12817 | -0.013733 | 0.20142 | 0.082398 | 0.26093 | 0.26093 | 123.1018 | 123.1293 | -0.27466 | -0.24719 | 122.8271 | 122.9507 | 122.8592 | 122.9416
4445.9531 | 123.1842 | -122.9645 | 0.082397 | 0.0025177 | -0.0092435 | -0.079011 | -0.0065517 | -0.034075 | -0.053372 | -0.041033 | 0.00094606 | 0.00018579 | 0.008562 | -0.016757 | -0.22043 | -0.021332 | -0.020476 | -0.064087 | 0.07782 | -0.091553 | -0.059509 | 0.10986 | -0.07782 | 0.018311 | 0.091553 | 0.10071 | -0.086975 | 0.054932 | 0.13275 | 0.086975 | 0.11902 | 122.8729 | -0.004577 | -0.14191 | 123.0743 | 122.9828 | 122.8867 | 0.10986 | 0.013733 | 122.8775 | 0.018311 | -0.027465 | 123.0972 | 123.0835 | 123.0515 | 0.20599 | 0.17395 | 0.20142 | 0.032044 | 0.21973 | 0.14191 | 0.16937 | 0.18768 | 123.0423 | 123.0652 | -0.17395 | -0.16937 | 122.905 | 123.0194 | 122.9004 | 123.056
4447.75 | 123.1659 | -122.9691 | 0.1236 | -0.0051118 | -0.01202 | -0.078797 | -0.0048427 | -0.026171 | -0.049313 | -0.041674 | -0.0021057 | 0.0038174 | 0.0087756 | -0.014834 | -0.21979 | -0.020478 | -0.022398 | -0.07782 | 0.10529 | -0.14648 | -0.10529 | 0.045776 | -0.09613 | -0.050354 | 0.059509 | 0.13733 | -0.11444 | 0.022888 | 0.11444 | 0.050354 | 0.091553 | 122.8226 | -0.01831 | -0.22888 | 123.0148 | 122.9187 | 122.8729 | 0.09613 | 0.050354 | 122.8546 | 0.013733 | -0.10071 | 123.0835 | 123.0606 | 123.0194 | 0.20599 | 0.16479 | 0.19226 | 0.041198 | 0.22888 | 0.13733 | 0.25177 | 0.25177 | 123.0743 | 123.1064 | -0.27008 | -0.23804 | 122.8638 | 122.9919 | 122.8912 | 123.0286
4449.4844 | 123.2117 | -122.9324 | 0.10071 | 0.0025177 | -0.011593 | -0.079224 | -0.0052701 | -0.028948 | -0.049313 | -0.041246 | 0.00094606 | 0.0018948 | 0.0042896 | -0.010134 | -0.22129 | -0.018982 | -0.021117 | -0.10986 | 0.10529 | -0.15106 | -0.14191 | 0.027466 | -0.14191 | -0.059509 | 0.022888 | 0.13733 | -0.091553 | 0.050354 | 0.13733 | 0.07782 | 0.14648 | 122.7814 | 0.004578 | -0.24262 | 122.9599 | 122.8729 | 122.7905 | 0.091553 | 0.009155 | 122.8409 | 0.036621 | -0.050354 | 123.0698 | 123.0789 | 123.0103 | 0.23804 | 0.16937 | 0.17853 | 0.009155 | 0.22888 | 0.14191 | 0.25635 | 0.22888 | 123.0377 | 123.0698 | -0.25177 | -0.19226 | 122.7905 | 122.9828 | 122.8226 | 122.9553
4451.2656 | 123.1979 | -122.9645 | 0.082397 | 0.0025177 | -0.015011 | -0.080079 | -0.0095425 | -0.030657 | -0.049099 | -0.040178 | -0.0082091 | 0.0027494 | 0.0092028 | -0.012057 | -0.21744 | -0.019623 | -0.022612 | -0.091553 | 0.082397 | -0.10986 | -0.082397 | 0.064087 | -0.10071 | 0 | 0.050354 | 0.1236 | -0.082397 | 0.036621 | 0.12817 | 0.073242 | 0.10071 | 122.8546 | 0 | -0.16479 | 123.0286 | 122.9645 | 122.8638 | 0.10986 | 0.009155 | 122.8821 | 0.041199 | -0.045776 | 123.0927 | 123.0652 | 123.0377 | 0.18311 | 0.15564 | 0.17395 | 0.027466 | 0.21057 | 0.11902 | 0.19226 | 0.20599 | 123.0469 | 123.0881 | -0.19226 | -0.16479 | 122.8821 | 123.0011 | 122.8729 | 123.0148
4453.0625 | 123.111 | -122.9828 | 0.10986 | 0.0025177 | -0.010098 | -0.07837 | -0.0020657 | -0.031511 | -0.050167 | -0.040819 | -0.0051575 | 0.002963 | 0.008562 | -0.0086388 | -0.21894 | -0.01941 | -0.022826 | -0.10529 | 0.11902 | -0.13733 | -0.12817 | 0 | -0.16479 | -0.09613 | -0.018311 | 0.14648 | -0.10986 | -0.036621 | 0.045776 | -0.041199 | 0.050354 | 122.8455 | 0.009156 | -0.23804 | 122.9828 | 122.8867 | 122.818 | 0.041199 | -0.027466 | 122.8729 | 0.036621 | -0.14648 | 123.0286 | 123.0331 | 122.9416 | 0.16022 | 0.068664 | 0.13733 | 0.009155 | 0.15564 | 0.073242 | 0.25635 | 0.25635 | 123.1018 | 123.1293 | -0.24719 | -0.21973 | 122.8546 | 122.9462 | 122.8775 | 122.9645
4454.8125 | 123.1018 | -122.9919 | 0.10986 | -0.0051118 | -0.0088163 | -0.076874 | -0.0061245 | -0.026384 | -0.049526 | -0.039537 | -0.0051575 | 0.0036038 | 0.0098438 | -0.014193 | -0.21915 | -0.018342 | -0.020903 | -0.11444 | 0.11444 | -0.13275 | -0.16022 | -0.050354 | -0.18768 | -0.1236 | -0.073242 | 0.13275 | -0.11444 | -0.032043 | 0.022888 | -0.041199 | 0.054932 | 122.8592 | 0.004578 | -0.27008 | 122.9416 | 122.8683 | 122.8043 | 0.009155 | -0.054932 | 122.8775 | 0.022888 | -0.14191 | 123.0148 | 123.0469 | 122.9507 | 0.16937 | 0.073242 | 0.082397 | -0.027466 | 0.13733 | 0.082398 | 0.24719 | 0.24719 | 123.1064 | 123.1247 | -0.24261 | -0.2243 | 122.8317 | 122.9599 | 122.8775 | 122.9187
4456.6094 | 123.23 | -122.9553 | 0.09613 | 0.0025177 | -0.014157 | -0.080292 | -0.0086879 | -0.027453 | -0.050808 | -0.043596 | -0.0021057 | 0.0027494 | 0.007494 | -0.0092798 | -0.21894 | -0.022614 | -0.025389 | -0.073242 | 0.091553 | -0.09613 | -0.045776 | 0.15106 | -0.013733 | 0.032043 | 0.11444 | 0.10071 | -0.073242 | 0.064087 | 0.18768 | 0.12817 | 0.14191 | 122.8592 | -0.004577 | -0.14191 | 123.1064 | 122.9874 | 122.9416 | 0.12817 | 0.082397 | 122.8821 | 0.004578 | -0.032043 | 123.143 | 123.0972 | 123.0835 | 0.21515 | 0.20142 | 0.24719 | 0.050354 | 0.26092 | 0.13733 | 0.18768 | 0.17395 | 123.0469 | 123.056 | -0.19226 | -0.16937 | 122.9095 | 123.0194 | 122.8821 | 123.0698
4458.3906 | 123.262 | -122.9462 | 0.086975 | -0.0051118 | -0.016293 | -0.080079 | -0.0084743 | -0.03322 | -0.051449 | -0.04146 | 0.00094606 | 0.0014676 | 0.0087756 | -0.022311 | -0.21872 | -0.022614 | -0.021971 | -0.07782 | 0.073242 | -0.10986 | -0.041199 | 0.13275 | -0.032043 | 0.041199 | 0.12817 | 0.091553 | -0.086975 | 0.10071 | 0.19684 | 0.15564 | 0.16022 | 122.8363 | -0.013733 | -0.12817 | 123.0789 | 122.9874 | 122.9141 | 0.15106 | 0.07782 | 122.8592 | 0.004578 | 0.013733 | 123.143 | 123.1064 | 123.1018 | 0.24719 | 0.24261 | 0.24261 | 0.068664 | 0.28381 | 0.18768 | 0.18311 | 0.17853 | 123.0194 | 123.0377 | -0.19684 | -0.17395 | 122.905 | 123.0469 | 122.8683 | 123.0743
4460.1875 | 123.1522 | -122.9507 | 0.11902 | 0.0025177 | -0.011593 | -0.078797 | -0.0067653 | -0.032152 | -0.051876 | -0.041246 | -0.0021057 | 0.0033902 | 0.0087756 | -0.0067162 | -0.22065 | -0.01941 | -0.024321 | -0.1236 | 0.11902 | -0.12817 | -0.16022 | -0.013733 | -0.15564 | -0.073242 | -0.045776 | 0.1236 | -0.1236 | -0.027466 | 0.068665 | 0 | 0.064087 | 122.8226 | 0 | -0.27924 | 122.937 | 122.8775 | 122.7951 | 0.054932 | -0.027466 | 122.8271 | 0.004577 | -0.14649 | 123.0194 | 123.0148 | 122.9507 | 0.18768 | 0.1236 | 0.11444 | -0.032043 | 0.19226 | 0.09613 | 0.24719 | 0.24719 | 123.0698 | 123.0743 | -0.24719 | -0.24261 | 122.7905 | 122.9233 | 122.8271 | 122.905
4461.9375 | 123.1567 | -122.9782 | 0.10986 | -0.012741 | -0.012448 | -0.080933 | -0.0086879 | -0.031939 | -0.052944 | -0.041674 | -0.0021057 | 0.0036038 | 0.0079212 | -0.015048 | -0.21851 | -0.021332 | -0.019835 | -0.073242 | 0.073242 | -0.11444 | -0.082397 | 0.082397 | -0.059509 | 0.004578 | 0.032043 | 0.1236 | -0.10071 | -0.032043 | 0.086975 | 0.022888 | 0.054932 | 122.8638 | -0.036621 | -0.19226 | 123.0606 | 122.9828 | 122.9187 | 0.11902 | 0.054932 | 122.8775 | 0.013733 | -0.14191 | 123.0652 | 123.0331 | 123.0011 | 0.15564 | 0.1236 | 0.19684 | 0.032044 | 0.18768 | 0.068665 | 0.18768 | 0.2243 | 123.0515 | 123.1018 | -0.2243 | -0.21057 | 122.8958 | 122.9462 | 122.905 | 123.0103
4463.7344 | 123.1247 | -123.0011 | 0.11902 | -0.0051118 | -0.011166 | -0.078583 | -0.0035611 | -0.027453 | -0.051876 | -0.040605 | -0.0021057 | 0.004672 | 0.0070666 | -0.0073572 | -0.22065 | -0.021332 | -0.020049 | -0.10071 | 0.09613 | -0.12817 | -0.13275 | 0.013733 | -0.17853 | -0.09613 | -0.027466 | 0.14191 | -0.10529 | -0.036621 | 0.022888 | -0.027466 | 0.045776 | 122.8729 | -0.022889 | -0.25177 | 123.0148 | 122.905 | 122.8226 | 0.032044 | -0.050354 | 122.8958 | 0.022888 | -0.15564 | 123.024 | 123.0469 | 122.9736 | 0.15106 | 0.07782 | 0.14191 | -0.004577 | 0.12817 | 0.068665 | 0.2243 | 0.24719 | 123.0972 | 123.143 | -0.24719 | -0.22431 | 122.8683 | 122.9645 | 122.9004 | 122.9736
4465.5312 | 123.2758 | -122.9507 | 0.082397 | 0.010147 | -0.017788 | -0.078797 | -0.0078335 | -0.032366 | -0.04974 | -0.042101 | -0.0051575 | 0.0010404 | 0.0079212 | -0.015048 | -0.21744 | -0.021973 | -0.021117 | -0.086975 | 0.086975 | -0.10071 | -0.036621 | 0.15564 | -0.022888 | 0.064087 | 0.13275 | 0.086975 | -0.086975 | 0.091553 | 0.21515 | 0.15106 | 0.16479 | 122.85 | 0.004578 | -0.11902 | 123.1064 | 123.0148 | 122.9279 | 0.1648 | 0.07782 | 122.8638 | 0.004578 | 0.009156 | 123.1659 | 123.1155 | 123.1018 | 0.25177 | 0.23804 | 0.25635 | 0.064087 | 0.30212 | 0.17853 | 0.18768 | 0.17395 | 123.0377 | 123.0377 | -0.18311 | -0.16937 | 122.9141 | 123.0423 | 122.8638 | 123.0835
4467.2656 | 123.2529 | -122.9324 | 0.091553 | -0.0051118 | -0.011166 | -0.076874 | -0.0078335 | -0.029162 | -0.049313 | -0.043596 | -0.0021057 | 0.001254 | 0.0079212 | -0.0094934 | -0.21766 | -0.020691 | -0.023253 | -0.041199 | 0.064087 | -0.10071 | -0.032043 | 0.13733 | -0.068665 | 0.009155 | 0.12817 | 0.09613 | -0.082397 | 0.09613 | 0.1831 | 0.11444 | 0.15564 | 122.8317 | -0.027466 | -0.1236 | 123.0698 | 122.9416 | 122.8638 | 0.10986 | 0.032043 | 122.85 | 0.004577 | 0.004577 | 123.1155 | 123.0881 | 123.0469 | 0.23804 | 0.19684 | 0.23804 | 0.068665 | 0.2655 | 0.17853 | 0.1648 | 0.17853 | 122.9965 | 123.0286 | -0.19226 | -0.17395 | 122.9004 | 123.0286 | 122.8912 | 123.0606
4469.0781 | 123.2666 | -122.9691 | 0.082397 | 0.0025177 | -0.014798 | -0.07837 | -0.0084743 | -0.031939 | -0.051663 | -0.042314 | 0.00094606 | 0.0018948 | 0.0081348 | -0.018252 | -0.21894 | -0.021546 | -0.02368 | -0.073242 | 0.086975 | -0.09613 | -0.009155 | 0.16479 | 0.004578 | 0.064087 | 0.1236 | 0.10986 | -0.073242 | 0.082397 | 0.19226 | 0.14191 | 0.14191 | 122.8729 | 0.004578 | -0.091552 | 123.1338 | 123.0331 | 122.9736 | 0.16022 | 0.10071 | 122.8958 | 0.027466 | 0 | 123.1613 | 123.111 | 123.111 | 0.21515 | 0.21515 | 0.26092 | 0.086975 | 0.2655 | 0.15564 | 0.1831 | 0.18311 | 123.056 | 123.0789 | -0.17853 | -0.15564 | 122.9599 | 123.0515 | 122.8958 | 123.0927
4470.8125 | 123.2208 | -122.9553 | 0.10529 | -0.0051118 | -0.014157 | -0.079438 | -0.0069791 | -0.034289 | -0.049313 | -0.038256 | 0.00094606 | 0.00039959 | 0.0059986 | -0.015048 | -0.2215 | -0.021119 | -0.025816 | -0.10529 | 0.068665 | -0.10529 | -0.10071 | 0.050354 | -0.09613 | -0.004578 | 0.022888 | 0.10986 | -0.09613 | 0.041199 | 0.14648 | 0.068665 | 0.10529 | 122.85 | -0.036621 | -0.20599 | 123.0057 | 122.9507 | 122.8592 | 0.10071 | 0.009156 | 122.8592 | 0.004577 | -0.064087 | 123.1018 | 123.0606 | 123.024 | 0.20142 | 0.16479 | 0.15564 | 0.004578 | 0.24261 | 0.13733 | 0.17395 | 0.20599 | 123.024 | 123.0652 | -0.21057 | -0.20142 | 122.8546 | 122.9965 | 122.85 | 122.9782
4472.6094 | 123.1979 | -122.9691 | 0.082397 | 0.0025177 | -0.014798 | -0.079011 | -0.0061245 | -0.030871 | -0.051663 | -0.039324 | 0.00094606 | 0.001254 | 0.0055712 | -0.012057 | -0.22001 | -0.022187 | -0.026885 | -0.059509 | 0.082397 | -0.11444 | -0.045776 | 0.12817 | -0.032043 | 0.032043 | 0.07782 | 0.10529 | -0.091553 | 0.027466 | 0.16479 | 0.086975 | 0.11444 | 122.8546 | 0 | -0.12817 | 123.0972 | 123.0011 | 122.937 | 0.14648 | 0.082398 | 122.8775 | 0.022889 | -0.054931 | 123.1338 | 123.0835 | 123.056 | 0.20599 | 0.17853 | 0.24262 | 0.068665 | 0.25635 | 0.11902 | 0.19684 | 0.19684 | 123.0515 | 123.0743 | -0.19684 | -0.17395 | 122.9233 | 122.9965 | 122.9095 | 123.0469
4474.4062 | 123.2483 | -122.937 | 0.091553 | -0.0051118 | -0.010952 | -0.077515 | -0.0054837 | -0.029589 | -0.051663 | -0.039324 | -0.0021057 | 0.0023222 | 0.006853 | -0.0043664 | -0.22043 | -0.021332 | -0.02368 | -0.054932 | 0.068665 | -0.082397 | -0.032043 | 0.1236 | -0.086975 | 0.013733 | 0.12817 | 0.10071 | -0.086975 | 0.086975 | 0.17395 | 0.10071 | 0.14648 | 122.8546 | -0.022888 | -0.1236 | 123.0606 | 122.9507 | 122.85 | 0.09613 | -0.004578 | 122.85 | 0.009155 | -0.004578 | 123.111 | 123.0835 | 123.0377 | 0.23346 | 0.18768 | 0.20599 | 0.050354 | 0.26092 | 0.17395 | 0.15106 | 0.18768 | 123.0057 | 123.0377 | -0.17395 | -0.17853 | 122.905 | 123.024 | 122.8821 | 123.0652
4476.125 | 123.1979 | -122.9691 | 0.086975 | -0.0051118 | -0.01138 | -0.079011 | -0.0091153 | -0.026171 | -0.049954 | -0.042314 | 0.00094606 | -0.00088221 | 0.0072802 | -0.0075708 | -0.22086 | -0.019196 | -0.021971 | -0.10529 | 0.073242 | -0.10071 | -0.086975 | 0.050354 | -0.10986 | -0.018311 | 0.036621 | 0.11902 | -0.091553 | 0.027466 | 0.12817 | 0.064087 | 0.10071 | 122.8683 | -0.013733 | -0.17395 | 123.0194 | 122.9507 | 122.8592 | 0.082397 | -0.009155 | 122.8775 | 0.032044 | -0.059509 | 123.0972 | 123.0698 | 123.0331 | 0.19226 | 0.15564 | 0.15106 | 0.013733 | 0.21973 | 0.11902 | 0.17395 | 0.21057 | 123.0423 | 123.0881 | -0.18768 | -0.17853 | 122.8821 | 122.9965 | 122.8638 | 123.0057
4477.9219 | 123.111 | -123.0148 | 0.10529 | -0.0051118 | -0.012448 | -0.080292 | -0.0056973 | -0.033648 | -0.051022 | -0.039751 | -0.0021057 | 0.0048856 | 0.0066394 | -0.010775 | -0.2183 | -0.020691 | -0.02368 | -0.14648 | 0.11444 | -0.13733 | -0.16479 | -0.022888 | -0.15106 | -0.07782 | -0.050354 | 0.13733 | -0.12817 | -0.045776 | 0.045776 | -0.013733 | 0.045776 | 122.8775 | 0.009155 | -0.27008 | 122.9919 | 122.937 | 122.8638 | 0.059509 | -0.013733 | 122.8867 | 0.032043 | -0.15106 | 123.0606 | 123.0606 | 123.0011 | 0.17395 | 0.11444 | 0.11444 | -0.027466 | 0.17395 | 0.082398 | 0.25177 | 0.2655 | 123.1293 | 123.1522 | -0.24262 | -0.23346 | 122.85 | 122.9691 | 122.8683 | 122.9645
4479.7344 | 123.2391 | -122.9645 | 0.082397 | -0.0051118 | -0.017147 | -0.079438 | -0.0065517 | -0.032152 | -0.051663 | -0.038896 | 0.00094606 | 0.0016812 | 0.0079212 | -0.012911 | -0.21958 | -0.0224 | -0.020903 | -0.09613 | 0.07782 | -0.11444 | -0.086975 | 0.073242 | -0.082397 | 0.013733 | 0.064087 | 0.11444 | -0.09613 | 0.068665 | 0.17853 | 0.10529 | 0.13733 | 122.85 | -0.004577 | -0.16937 | 123.0377 | 122.9782 | 122.8821 | 0.12817 | 0.032044 | 122.8683 | 0.032044 | -0.013732 | 123.143 | 123.1018 | 123.0698 | 0.23346 | 0.20142 | 0.18768 | 0.027466 | 0.27466 | 0.16479 | 0.19226 | 0.21057 | 123.0423 | 123.0789 | -0.19684 | -0.17853 | 122.8775 | 123.0331 | 122.8683 | 123.0286
4481.4688 | 123.2071 | -122.9645 | 0.07782 | 0.0025177 | -0.012234 | -0.080506 | -0.0095425 | -0.029162 | -0.051876 | -0.042955 | -0.0051575 | 0.0010404 | 0.007494 | -0.013766 | -0.22022 | -0.020478 | -0.021544 | -0.09613 | 0.073242 | -0.10071 | -0.082397 | 0.050354 | -0.10071 | -0.022888 | 0.045776 | 0.10986 | -0.091553 | 0.032043 | 0.13275 | 0.073242 | 0.09613 | 122.8638 | -0.004578 | -0.16022 | 123.0148 | 122.9416 | 122.8638 | 0.07782 | 0 | 122.8729 | 0.032043 | -0.045777 | 123.0972 | 123.0606 | 123.0377 | 0.18768 | 0.16479 | 0.15106 | 0.018311 | 0.2243 | 0.1236 | 0.17395 | 0.20142 | 123.0377 | 123.0743 | -0.17853 | -0.16937 | 122.8821 | 122.9965 | 122.8683 | 123.0103
4483.25 | 123.1888 | -122.9553 | 0.082397 | -0.012741 | -0.012448 | -0.077515 | -0.0050565 | -0.033007 | -0.048886 | -0.04146 | -0.0021057 | 0.0031766 | 0.0079212 | -0.0099206 | -0.21979 | -0.022614 | -0.023894 | -0.086975 | 0.064087 | -0.091553 | -0.068665 | 0.073242 | -0.086975 | -0.009155 | 0.054932 | 0.09613 | -0.10071 | 0.041199 | 0.14648 | 0.059509 | 0.10071 | 122.8638 | -0.01831 | -0.15106 | 123.0286 | 122.9462 | 122.8683 | 0.082398 | 0.004578 | 122.8546 | 0.013733 | -0.041198 | 123.1018 | 123.056 | 123.0148 | 0.20142 | 0.16022 | 0.16479 | 0.022888 | 0.24719 | 0.14191 | 0.15564 | 0.19684 | 123.0194 | 123.0515 | -0.17395 | -0.18311 | 122.8867 | 122.9965 | 122.8683 | 123.0103
4485.0469 | 123.23 | -122.9279 | 0.091553 | 0.0025177 | -0.0098843 | -0.076447 | -0.0027065 | -0.026812 | -0.049954 | -0.041887 | 0.00094606 | 0.0036038 | 0.0072802 | -0.015261 | -0.21937 | -0.020905 | -0.024535 | -0.10071 | 0.091553 | -0.12817 | -0.091553 | 0.045776 | -0.13733 | -0.036621 | 0.07782 | 0.10529 | -0.082397 | 0.07782 | 0.16479 | 0.091553 | 0.14191 | 122.7997 | 0 | -0.18311 | 122.9736 | 122.8912 | 122.7905 | 0.091553 | -0.009155 | 122.8455 | 0.013733 | -0.013733 | 123.0927 | 123.0698 | 123.0194 | 0.2243 | 0.17395 | 0.17395 | 0.036621 | 0.24719 | 0.16022 | 0.21973 | 0.18768 | 123.0194 | 123.0331 | -0.21973 | -0.17395 | 122.8363 | 123.0057 | 122.8271 | 123.0057
4486.7812 | 123.2483 | -122.9553 | 0.082397 | -0.0051118 | -0.010098 | -0.076874 | -0.0067653 | -0.032152 | -0.049313 | -0.041674 | 0.0039979 | 0.0018948 | 0.0083484 | -0.015048 | -0.21958 | -0.022187 | -0.023253 | -0.045776 | 0.073242 | -0.091553 | -0.036621 | 0.13275 | -0.082397 | 0.022888 | 0.1236 | 0.091553 | -0.073242 | 0.086975 | 0.16937 | 0.10529 | 0.15106 | 122.8638 | -0.009155 | -0.11902 | 123.0881 | 122.9782 | 122.8729 | 0.11444 | 0.009156 | 122.8821 | 0.009156 | 0.004578 | 123.1247 | 123.1064 | 123.0606 | 0.2243 | 0.17853 | 0.2243 | 0.054932 | 0.24261 | 0.16022 | 0.16479 | 0.16479 | 123.0286 | 123.0469 | -0.17395 | -0.15564 | 122.9187 | 123.0423 | 122.9095 | 123.0789
4488.5781 | 123.175 | -123.0011 | 0.10986 | 0.010147 | -0.013516 | -0.07837 | -0.0061245 | -0.02788 | -0.050595 | -0.041887 | -0.0021057 | 0.0031766 | 0.008562 | -0.0060754 | -0.21787 | -0.021119 | -0.023039 | -0.1236 | 0.09613 | -0.14648 | -0.16937 | -0.027466 | -0.14191 | -0.082397 | -0.054932 | 0.15564 | -0.10529 | -0.022888 | 0.082397 | 0.009155 | 0.050354 | 122.8546 | -0.013733 | -0.27924 | 122.9736 | 122.9187 | 122.8592 | 0.064087 | 0.004577 | 122.8958 | 0.045777 | -0.13275 | 123.0835 | 123.0515 | 123.0103 | 0.15564 | 0.11444 | 0.11902 | -0.022889 | 0.18768 | 0.082398 | 0.24261 | 0.26093 | 123.0972 | 123.1567 | -0.25635 | -0.21515 | 122.8317 | 122.9782 | 122.8775 | 122.9462
4490.3594 | 123.2529 | -122.9279 | 0.064087 | 0.017777 | -0.010952 | -0.078156 | -0.0054837 | -0.029162 | -0.051449 | -0.041246 | -0.0051575 | 0.0042448 | 0.0092028 | -0.0058618 | -0.21958 | -0.018128 | -0.024107 | -0.10986 | 0.086975 | -0.10071 | -0.082397 | 0.064087 | -0.1236 | -0.009155 | 0.091553 | 0.11444 | -0.082397 | 0.091553 | 0.16937 | 0.082397 | 0.16022 | 122.8271 | 0.022888 | -0.14648 | 122.9919 | 122.9187 | 122.8043 | 0.091553 | -0.022888 | 122.8455 | 0.050354 | 0.027466 | 123.0972 | 123.0881 | 123.0103 | 0.24261 | 0.16479 | 0.1648 | 0.018311 | 0.25177 | 0.17395 | 0.18768 | 0.19684 | 123.0148 | 123.0423 | -0.1648 | -0.14648 | 122.8455 | 123.0194 | 122.818 | 123.0194
4492.1562 | 123.2391 | -122.9507 | 0.091553 | -0.0051118 | -0.010098 | -0.076233 | -0.0042019 | -0.03258 | -0.048886 | -0.040178 | -0.0021057 | 0.0036038 | 0.0081348 | -0.01227 | -0.21872 | -0.01941 | -0.02133 | -0.10986 | 0.10071 | -0.12817 | -0.09613 | 0.027466 | -0.14648 | -0.032043 | 0.064087 | 0.1236 | -0.09613 | 0.073242 | 0.14191 | 0.091553 | 0.13733 | 122.8226 | 0.009155 | -0.18768 | 122.9782 | 122.9187 | 122.8043 | 0.096131 | -0.01831 | 122.8546 | 0.032043 | -0.018311 | 123.0927 | 123.0881 | 123.0423 | 0.23346 | 0.18768 | 0.15564 | 0.032044 | 0.23804 | 0.16937 | 0.22888 | 0.21973 | 123.0515 | 123.0743 | -0.21973 | -0.18768 | 122.8546 | 123.024 | 122.8409 | 123.0148
4493.8906 | 123.1796 | -122.9919 | 0.10986 | -0.0051118 | -0.013302 | -0.07602 | -0.0052701 | -0.030871 | -0.048672 | -0.039537 | 0.00094606 | 0.0036038 | 0.0087756 | -0.0058618 | -0.22022 | -0.020691 | -0.021117 | -0.086975 | 0.10986 | -0.13275 | -0.10986 | 0.059509 | -0.11902 | -0.045776 | 0.041199 | 0.13275 | -0.11444 | 0.036621 | 0.11902 | 0.036621 | 0.10071 | 122.8592 | 0 | -0.21973 | 123.0515 | 122.9462 | 122.8729 | 0.086975 | 0.013732 | 122.8775 | 0.022888 | -0.073242 | 123.111 | 123.0927 | 123.0286 | 0.21515 | 0.15106 | 0.19226 | 0.022888 | 0.23346 | 0.15106 | 0.24261 | 0.24719 | 123.1018 | 123.1247 | -0.24261 | -0.2243 | 122.8821 | 123.0286 | 122.905 | 123.0331
4495.6875 | 123.2071 | -122.9645 | 0.10986 | -0.0051118 | -0.011807 | -0.079224 | -0.0099697 | -0.03258 | -0.051449 | -0.041246 | 0.00094606 | 0.00018579 | 0.007494 | -0.013979 | -0.21531 | -0.019623 | -0.024321 | -0.10529 | 0.086975 | -0.10071 | -0.10071 | 0.064087 | -0.091553 | -0.013733 | 0.032043 | 0.12817 | -0.091553 | 0.027466 | 0.13733 | 0.064087 | 0.11902 | 122.8638 | -0.022888 | -0.21057 | 123.0286 | 122.9507 | 122.8729 | 0.086975 | 0.009155 | 122.8729 | 0.018311 | -0.082397 | 123.1018 | 123.0835 | 123.0286 | 0.21057 | 0.15564 | 0.1648 | 0 | 0.22888 | 0.11902 | 0.18768 | 0.21973 | 123.0515 | 123.0927 | -0.21057 | -0.20142 | 122.8638 | 122.9919 | 122.8592 | 122.9965
4497.4844 | 123.2712 | -122.9507 | 0.064087 | -0.0051118 | -0.015225 | -0.081147 | -0.0082607 | -0.031725 | -0.052944 | -0.04146 | -0.0021057 | 0.0010404 | 0.0066394 | -0.012057 | -0.21872 | -0.021119 | -0.02838 | -0.09613 | 0.091553 | -0.10986 | -0.036621 | 0.11902 | -0.032043 | 0.045776 | 0.12817 | 0.10986 | -0.09613 | 0.086975 | 0.20599 | 0.15106 | 0.16022 | 122.8409 | 0.027466 | -0.10071 | 123.0698 | 122.9965 | 122.9187 | 0.15564 | 0.07782 | 122.8546 | 0.045776 | 0.022888 | 123.1567 | 123.111 | 123.1018 | 0.25635 | 0.24719 | 0.22888 | 0.073242 | 0.30212 | 0.1831 | 0.20142 | 0.20599 | 123.0423 | 123.0606 | -0.17395 | -0.16022 | 122.9141 | 123.0377 | 122.8546 | 123.0789
4499.2656 | 123.1338 | -122.9874 | 0.11902 | 0.0025177 | -0.0092435 | -0.079011 | -0.0059109 | -0.02788 | -0.049954 | -0.042742 | 0.0039979 | 0.00574 | 0.0089892 | -0.010775 | -0.22001 | -0.018982 | -0.023253 | -0.1236 | 0.10986 | -0.14648 | -0.1831 | -0.07782 | -0.20142 | -0.10529 | -0.054932 | 0.1236 | -0.11902 | -0.032043 | 0.032043 | -0.041199 | 0.050354 | 122.8409 | -0.009156 | -0.30212 | 122.9095 | 122.8821 | 122.7859 | 0.041198 | -0.054932 | 122.8683 | 0.004577 | -0.15106 | 123.0194 | 123.0377 | 122.9462 | 0.16937 | 0.07782 | 0.068664 | -0.036621 | 0.15106 | 0.086976 | 0.25635 | 0.24261 | 123.0972 | 123.111 | -0.2655 | -0.23804 | 122.8043 | 122.9553 | 122.8638 | 122.9324
4501 | 123.143 | -123.0148 | 0.1236 | 0.0025177 | -0.010952 | -0.076874 | -0.0067653 | -0.027666 | -0.049099 | -0.039537 | -0.0021057 | 0.0031766 | 0.0089892 | -0.012698 | -0.21851 | -0.020051 | -0.024321 | -0.1236 | 0.12817 | -0.13733 | -0.1831 | -0.041199 | -0.20142 | -0.10529 | -0.059509 | 0.14191 | -0.11444 | -0.027466 | 0.022888 | -0.036621 | 0.050354 | 122.8775 | 0.004578 | -0.3067 | 122.9736 | 122.9095 | 122.8134 | 0.032043 | -0.064087 | 122.9004 | 0.018311 | -0.15106 | 123.0377 | 123.0652 | 122.9782 | 0.16479 | 0.07782 | 0.09613 | -0.045776 | 0.13733 | 0.086975 | 0.2655 | 0.25635 | 123.143 | 123.1567 | -0.26093 | -0.23804 | 122.8317 | 122.9874 | 122.8912 | 122.9553

## Thermal Data
Fire Time | B Position - Middle | D Position - 3' | D Position - Middle | D Position - 7'
-0.8708 | 13.7945 | 13.8555 | 13.6501 | 13.3753
0.1292 | 13.7801 | 13.853 | 13.6607 | 13.379
1.1292 | 13.833 | 13.869 | 13.6622 | 13.3787
2.1292 | 13.7828 | 13.8669 | 13.6608 | 13.3738
3.1292 | 13.7546 | 13.8647 | 13.6803 | 13.3697
4.1292 | 13.7563 | 13.8657 | 13.6792 | 13.3712
5.1292 | 13.7724 | 13.8627 | 13.6914 | 13.3694
6.1292 | 13.7966 | 13.8927 | 13.7164 | 13.3735
7.1292 | 13.8906 | 13.8632 | 13.9248 | 13.4571
8.1292 | 14.2047 | 14.0485 | 14.6782 | 13.8355
9.1292 | 15.0359 | 14.9506 | 16.0409 | 14.8593
10.1292 | 16.3714 | 16.667 | 19.3255 | 17.7258
11.1292 | 18.1006 | 17.863 | 23.0924 | 20.4005
12.1292 | 20.8924 | 19.8433 | 28.4009 | 24.4665
13.1292 | 23.3311 | 21.0134 | 35.0865 | 29.9164
14.1292 | 26.4924 | 23.1818 | 40.4745 | 34.1206
15.1292 | 29.8732 | 25.7888 | 46.1515 | 38.1307
16.1292 | 33.2908 | 29.0381 | 51.9939 | 43.8155
17.1292 | 35.6068 | 30.5266 | 55.0672 | 46.8591
18.1292 | 37.5578 | 32.1277 | 57.9959 | 48.3883
19.1448 | 39.5921 | 33.4671 | 62.4385 | 51.2609
20.1292 | 41.4415 | 34.6939 | 64.3751 | 53.6767
21.1292 | 43.0797 | 37.0047 | 66.9537 | 56.3411
22.1292 | 44.4431 | 38.6482 | 69.7505 | 57.5981
23.1292 | 46.1314 | 39.9561 | 73.6011 | 60.9881
24.1292 | 47.3893 | 42.3501 | 76.7189 | 63.8434
25.1292 | 49.1759 | 43.8935 | 79.7633 | 66.5986
26.1292 | 50.8247 | 45.1137 | 83.106 | 69.6039
27.1292 | 53.0537 | 47.1881 | 86.542 | 72.9646
28.1292 | 54.961 | 49.0493 | 89.1495 | 75.7717
29.1292 | 56.4574 | 50.3455 | 91.5288 | 77.8041
30.1292 | 57.585 | 51.8382 | 93.7208 | 80.0172
31.1292 | 58.6379 | 53.7533 | 95.1221 | 81.3054
32.1292 | 60.2297 | 55.6936 | 96.9875 | 82.3802
33.1292 | 61.6156 | 57.5003 | 99.705 | 83.9898
34.1292 | 62.954 | 59.3262 | 102.1444 | 85.4682
35.1292 | 63.8523 | 61.5475 | 103.4823 | 87.492
36.1292 | 64.7835 | 63.2037 | 105.2495 | 88.5329
37.1292 | 65.775 | 65.6195 | 106.6556 | 90.2873
38.1292 | 66.4592 | 67.8906 | 108.1867 | 91.686
39.1292 | 67.4337 | 70.1432 | 108.8826 | 93.1486
40.1292 | 68.0382 | 71.2965 | 110.9026 | 94.4373
41.1292 | 68.9545 | 73.4003 | 112.0524 | 97.0642
42.1292 | 69.9164 | 74.5293 | 113.1769 | 98.019
43.1292 | 71.1869 | 79.3794 | 115.8054 | 98.5555
44.1448 | 72.1189 | 81.3678 | 116.8706 | 99.6278
45.1292 | 73.3237 | 83.0368 | 119.7829 | 101.8065
46.1292 | 74.0965 | 85.3966 | 121.6094 | 103.3135
47.1292 | 75.5821 | 87.1247 | 124.3148 | 106.7412
48.1448 | 76.9872 | 90.7235 | 127.9274 | 108.0103
49.1448 | 77.993 | 92.9654 | 130.8353 | 109.7173
50.1448 | 79.2296 | 97.131 | 132.8194 | 110.0606
51.1292 | 80.6962 | 100.5195 | 134.2327 | 110.4011
52.1292 | 82.0365 | 102.451 | 135.4517 | 110.5442
53.1292 | 83.801 | 104.7376 | 136.3556 | 111.3771
54.1292 | 84.659 | 106.4011 | 137.8119 | 113.0703
55.1292 | 85.3419 | 111.4876 | 139.2336 | 113.9978
56.1292 | 86.178 | 115.0705 | 141.907 | 117.3639
57.1292 | 87.5743 | 117.9628 | 143.6742 | 118.4061
58.1292 | 88.3365 | 119.5452 | 145.072 | 119.4222
59.1292 | 88.7796 | 120.5941 | 145.4631 | 120.1231
60.1292 | 89.1557 | 121.401 | 145.3593 | 121.7216
61.1292 | 89.8128 | 122.5174 | 146.5865 | 123.5707
62.1292 | 91.5214 | 122.9088 | 147.4614 | 124.6351
63.1292 | 92.3539 | 125.9878 | 150.8364 | 126.9917
64.1292 | 93.182 | 127.4463 | 151.5929 | 128.0802
65.1292 | 94.2908 | 129.4713 | 153.3059 | 128.7739
66.1292 | 94.8365 | 132.3337 | 154.8178 | 130.5611
67.1292 | 96.1212 | 132.4041 | 155.6808 | 134.1249
68.1292 | 97.3474 | 132.8679 | 156.6246 | 135.8726
69.1292 | 98.5962 | 133.9631 | 158.7264 | 136.8925
70.1292 | 99.6286 | 133.9807 | 160.0051 | 136.6802
71.1292 | 100.6856 | 134.5635 | 160.9996 | 137.6614
72.1292 | 101.5456 | 136.6729 | 162.5201 | 140.6902
73.1292 | 101.861 | 136.6771 | 163.5035 | 142.1184
74.1292 | 103.0578 | 136.6447 | 165.2586 | 143.2883
75.1292 | 103.7934 | 137.6821 | 166.0604 | 147.1035
76.1292 | 105.2822 | 138.9539 | 167.9867 | 151.0719
77.1292 | 106.368 | 138.9083 | 169.6869 | 152.9394
78.1292 | 107.7405 | 138.8087 | 169.8596 | 153.212
79.1292 | 108.406 | 139.1847 | 170.5579 | 155.1969
80.1292 | 109.3903 | 139.3225 | 170.4005 | 156.4763
81.1292 | 110.2467 | 139.7529 | 171.0925 | 156.7751
82.1292 | 110.9988 | 139.8461 | 172.5311 | 157.8255
83.1292 | 111.2907 | 142.701 | 173.8458 | 160.5741
84.1292 | 111.5094 | 141.9201 | 173.5223 | 163.4426
85.1292 | 112.212 | 142.2485 | 174.3379 | 163.7407
86.1292 | 112.6778 | 143.8958 | 173.6944 | 163.1548
87.1292 | 113.5584 | 145.8279 | 174.5415 | 163.4184
88.1292 | 114.4802 | 145.5298 | 175.7794 | 163.6273
89.1292 | 115.0693 | 145.7819 | 175.2479 | 164.4574
90.1292 | 116.1392 | 145.5679 | 175.802 | 166.5513
91.1292 | 116.1047 | 145.5632 | 176.8101 | 167.4002
92.1292 | 116.6315 | 146.8394 | 177.2952 | 170.1505
93.1292 | 116.9591 | 147.4351 | 178.2126 | 172.321
94.1292 | 117.5515 | 147.5804 | 178.5876 | 171.8911
95.1292 | 118.7735 | 147.1129 | 178.9402 | 173.0359
96.1292 | 119.4279 | 147.601 | 179.0723 | 173.9314
97.1292 | 120.3523 | 146.6612 | 179.2088 | 173.7459
98.1292 | 120.6767 | 146.9132 | 179.423 | 175.2755
99.1292 | 121.7584 | 146.3232 | 181.5555 | 175.3851
100.1292 | 122.3117 | 147.4527 | 181.7047 | 175.8848
101.1292 | 123.895 | 148.533 | 182.9443 | 176.581
102.1292 | 124.1472 | 149.1775 | 182.4292 | 177.2235
103.1292 | 124.7034 | 148.5561 | 183.4724 | 177.058
104.1292 | 124.5054 | 148.6416 | 184.3039 | 177.8885
105.1292 | 125.2389 | 148.5832 | 183.9904 | 177.76
106.1292 | 125.1245 | 148.6002 | 183.1807 | 175.8918
107.1292 | 125.3826 | 147.9094 | 183.183 | 174.7547
108.1292 | 125.5057 | 147.5103 | 182.6422 | 173.6859
109.1292 | 125.2789 | 146.9908 | 181.9682 | 171.4019
110.1292 | 125.542 | 146.8585 | 181.2112 | 171.3226
111.1292 | 126.2802 | 147.0228 | 180.5239 | 170.6776
112.1292 | 126.8319 | 147.1424 | 179.9167 | 170.2454
113.1292 | 127.3929 | 148.234 | 180.0828 | 170.1589
114.1292 | 127.3641 | 148.3764 | 179.8399 | 170.6301
115.1448 | 127.3337 | 149.456 | 179.5574 | 172.0881
116.1292 | 128.0319 | 148.7698 | 179.3377 | 172.6844
117.1292 | 128.958 | 149.4248 | 179.3579 | 172.2785
118.1292 | 129.1652 | 150.1844 | 179.9192 | 173.0446
119.1292 | 128.9896 | 150.2034 | 180.4678 | 174.6356
120.1292 | 128.8527 | 150.3834 | 180.2589 | 176.6699
121.1292 | 128.7459 | 150.8594 | 180.1578 | 177.1268
122.1292 | 128.8999 | 152.2395 | 179.9979 | 177.2148
123.1292 | 128.8716 | 152.0787 | 180.0345 | 175.1165
124.1292 | 128.5817 | 154.0389 | 180.3354 | 175.0077
125.1292 | 128.0683 | 154.4739 | 180.6704 | 176.0762
126.1292 | 127.6089 | 154.4806 | 179.8801 | 175.1343
127.1292 | 127.3938 | 153.6312 | 179.2072 | 176.6219
128.1292 | 127.1383 | 153.9867 | 178.6784 | 175.9418
129.1292 | 127.0737 | 155.2192 | 179.651 | 176.3043
130.1292 | 127.0393 | 154.9056 | 179.6992 | 177.6214
131.1292 | 127.1782 | 154.9252 | 179.5731 | 177.3918
132.1292 | 127.7086 | 154.6562 | 181.4692 | 177.9753
133.1292 | 127.8393 | 155.3851 | 181.5262 | 176.9607
134.1292 | 128.1924 | 155.2221 | 182.3469 | 176.5376
135.1292 | 128.4024 | 155.4212 | 182.2809 | 177.4288
136.1292 | 128.5703 | 155.3105 | 182.1023 | 177.0339
137.1292 | 128.3921 | 154.523 | 182.0024 | 178.5463
138.1292 | 128.9038 | 154.4211 | 183.0338 | 180.5618
139.1292 | 128.4445 | 155.3143 | 183.8365 | 181.5895
140.1292 | 128.6475 | 155.9995 | 185.0257 | 181.0797
141.1292 | 128.4232 | 156.4258 | 184.1958 | 180.1112
142.1292 | 128.4077 | 156.4081 | 184.6883 | 179.8561
143.1292 | 129.1877 | 156.7805 | 185.0503 | 179.8727
144.1292 | 129.1843 | 156.5267 | 184.9302 | 180.7782
145.1448 | 129.8991 | 157.1021 | 184.7053 | 181.0679
146.1292 | 130.3599 | 156.605 | 183.9947 | 180.9179
147.1292 | 130.6583 | 155.7004 | 185.1619 | 181.715
148.1292 | 130.9209 | 155.8524 | 184.7488 | 181.5299
149.1292 | 131.285 | 154.5139 | 183.8632 | 180.6077
150.1292 | 131.6555 | 153.8134 | 183.0149 | 180.1641
151.1292 | 131.7339 | 153.6694 | 182.2843 | 180.9745
152.1292 | 132.2375 | 153.9743 | 182.8208 | 182.5684
153.1292 | 132.3824 | 154.0895 | 182.7626 | 184.0875
154.1292 | 132.9893 | 154.4022 | 182.9859 | 184.5902
155.1292 | 133.2288 | 154.6373 | 184.2985 | 185.5948
156.1292 | 133.898 | 153.8531 | 184.7972 | 187.2704
157.1292 | 133.9663 | 152.6581 | 184.655 | 188.6635
158.1292 | 134.816 | 152.5783 | 185.3576 | 188.9162
159.1292 | 134.94 | 153.5236 | 186.3484 | 192.8039
160.1292 | 135.1707 | 153.7807 | 186.3157 | 193.1237
161.1292 | 135.7998 | 155.3951 | 188.0926 | 192.8556
162.1292 | 136.6739 | 155.4375 | 188.8387 | 193.1378
163.1292 | 137.6291 | 157.104 | 189.2038 | 194.7475
164.1292 | 138.0949 | 157.6844 | 189.4668 | 193.0167
165.1292 | 138.7047 | 158.6151 | 189.7832 | 193.6461
166.1292 | 139.4018 | 157.6077 | 190.0367 | 192.2217
167.1292 | 140.009 | 157.7143 | 190.5939 | 191.1698
168.1292 | 140.6256 | 157.614 | 190.3533 | 190.7674
169.1292 | 140.9513 | 158.1493 | 190.9453 | 190.9727
170.1292 | 140.8603 | 159.3077 | 191.32 | 191.7282
171.1292 | 141.2379 | 158.6582 | 192.3115 | 190.94
172.1292 | 141.8764 | 158.5075 | 192.2235 | 190.3355
173.1292 | 142.485 | 158.5317 | 193.7488 | 189.999
174.1292 | 142.6339 | 158.3115 | 195.2616 | 189.899
175.1292 | 142.7455 | 158.9124 | 194.8304 | 189.8674
176.1292 | 143.0743 | 159.2901 | 194.5655 | 189.9792
177.1292 | 143.3668 | 159.1156 | 194.8578 | 192.5238
178.1292 | 143.3093 | 159.9948 | 194.6386 | 194.5524
179.1292 | 143.4453 | 162.0791 | 196.0535 | 195.9085
180.1292 | 143.4277 | 161.3208 | 195.7204 | 195.5458
181.1292 | 143.5775 | 160.2606 | 195.2963 | 195.089
182.1292 | 144.0453 | 160.4767 | 195.0674 | 194.6063
183.1292 | 143.8834 | 160.83 | 194.4097 | 194.0796
184.1292 | 144.1474 | 163.5573 | 196.1612 | 194.9656
185.1292 | 144.5398 | 162.7978 | 197.3852 | 194.9933
186.1292 | 144.9413 | 163.1434 | 198.495 | 195.0289
187.1292 | 144.7613 | 162.9523 | 198.3326 | 195.2606
188.1292 | 144.8457 | 163.8156 | 198.6491 | 196.1339
189.1292 | 144.4958 | 164.0965 | 198.3176 | 198.6832
190.1292 | 144.7675 | 163.2959 | 198.1338 | 199.5214
191.1292 | 145.1295 | 165.033 | 197.7512 | 200.2754
192.1292 | 146.4768 | 164.4746 | 198.1874 | 201.4104
193.1292 | 146.5086 | 166.2379 | 198.9924 | 204.0649
194.1292 | 147.2562 | 168.4732 | 200.4581 | 205.7512
195.1292 | 147.4818 | 167.749 | 201.2182 | 203.9768
196.1292 | 147.653 | 167.9965 | 201.2129 | 203.3951
197.1292 | 147.7218 | 168.4786 | 201.6889 | 203.9221
198.1292 | 147.4397 | 168.6632 | 200.3912 | 203.014
199.1448 | 147.7963 | 169.652 | 200.134 | 203.5049
200.1292 | 147.6912 | 168.4728 | 200.1406 | 204.06
201.1292 | 147.6199 | 168.5144 | 200.4374 | 204.6482
202.1292 | 147.5196 | 170.0084 | 201.7743 | 204.167
203.1292 | 148.0698 | 169.3509 | 202.1729 | 204.9896
204.1292 | 149.129 | 168.5114 | 203.7777 | 206.2
205.1292 | 149.6197 | 168.3509 | 204.7537 | 207.3819
206.1292 | 149.7265 | 170.5418 | 204.7144 | 207.2376
207.1292 | 150.9003 | 171.8175 | 205.0697 | 210.4115
208.1292 | 151.824 | 170.8555 | 204.6068 | 210.73
209.1292 | 152.2727 | 171.0274 | 204.5022 | 209.9582
210.1292 | 152.5 | 170.3225 | 203.8832 | 210.4554
211.1292 | 152.3363 | 171.3457 | 203.7972 | 211.1832
212.1292 | 151.9537 | 171.3243 | 204.0379 | 211.0715
213.1292 | 152.0161 | 172.3937 | 205.7227 | 211.7977
214.1292 | 152.2195 | 172.9899 | 206.222 | 212.5497
215.1292 | 152.4363 | 172.2333 | 206.1301 | 211.5661
216.1292 | 152.9387 | 172.5778 | 206.4231 | 210.7237
217.1292 | 153.1145 | 172.6435 | 205.8354 | 211.3099
218.1292 | 153.5302 | 172.4368 | 205.3715 | 211.1385
219.1292 | 153.8979 | 171.6394 | 205.7425 | 210.767
220.1292 | 154.9647 | 171.1032 | 204.796 | 209.9147
221.1292 | 155.0785 | 170.9594 | 205.7619 | 210.2848
222.1292 | 155.595 | 170.2458 | 204.7902 | 210.4464
223.1292 | 156.3211 | 171.5038 | 206.5114 | 211.0112
224.1292 | 156.9833 | 172.2438 | 206.5583 | 210.9298
225.1292 | 157.1218 | 172.6505 | 206.3612 | 211.4565
226.1292 | 156.6708 | 172.2681 | 206.7688 | 211.5235
227.1292 | 155.6927 | 172.416 | 206.6007 | 210.1152
228.1292 | 154.8338 | 172.9348 | 206.4678 | 208.6359
229.1292 | 153.9547 | 173.4637 | 205.7898 | 206.6038
230.1292 | 153.8017 | 172.9601 | 205.8803 | 205.3487
231.1292 | 154.0224 | 173.7549 | 206.7447 | 206.0712
232.1292 | 154.0211 | 173.488 | 207.3416 | 206.2504
233.1292 | 154.669 | 174.6343 | 208.237 | 206.3308
234.1292 | 154.9921 | 174.0075 | 208.0912 | 207.2616
235.1292 | 155.0354 | 175.1084 | 207.9283 | 207.1491
236.1292 | 155.4491 | 176.7676 | 208.2413 | 207.2434
237.1292 | 155.1916 | 176.4703 | 208.3126 | 206.6701
238.1292 | 154.8356 | 176.5528 | 208.4239 | 206.2659
239.1292 | 154.7408 | 175.425 | 208.0863 | 205.2517
240.1292 | 155.7069 | 174.8594 | 208.0867 | 205.1116
241.1292 | 155.5635 | 174.5022 | 207.5907 | 204.0152
242.1292 | 155.8619 | 173.7396 | 207.9541 | 202.9769
243.1292 | 155.596 | 173.6297 | 207.4959 | 202.6012
244.1292 | 155.3002 | 173.4477 | 208.0313 | 202.9064
245.1292 | 154.8705 | 173.5443 | 208.4289 | 203.3876
246.1292 | 154.2125 | 173.7804 | 208.4539 | 204.4232
247.1292 | 154.4175 | 174.1088 | 209.1197 | 204.5905
248.1292 | 154.912 | 173.6168 | 209.7277 | 206.3787
249.1292 | 155.1845 | 173.183 | 208.9529 | 207.2356
250.1292 | 155.7868 | 172.9713 | 209.49 | 207.9061
251.1292 | 155.8268 | 172.9364 | 210.8355 | 208.8779
252.1292 | 156.559 | 173.5994 | 213.0114 | 209.4363
253.1292 | 156.8286 | 173.5773 | 212.1152 | 208.5511
254.1292 | 157.5327 | 175.0383 | 211.0617 | 208.2804
255.1292 | 157.6207 | 175.0179 | 210.2397 | 207.9756
256.1292 | 157.6521 | 174.4682 | 210.4863 | 208.4939
257.1292 | 158.7474 | 174.549 | 212.5179 | 207.6675
258.1292 | 159.3654 | 175.3127 | 213.426 | 208.4033
259.1292 | 159.2171 | 176.1052 | 214.0767 | 208.8405
260.1292 | 159.712 | 176.9876 | 215.9359 | 208.9882
261.1292 | 160.2501 | 177.4044 | 216.5626 | 209.4258
262.1292 | 160.9132 | 177.7045 | 216.9139 | 208.595
263.1292 | 162.2036 | 177.0879 | 217.8213 | 209.6637
264.1292 | 162.1491 | 178.1353 | 216.6876 | 209.394
265.1448 | 162.2221 | 178.6754 | 216.5643 | 208.2417
266.1292 | 162.9319 | 178.7397 | 216.4144 | 208.4086
267.1292 | 163.8778 | 180.956 | 217.5086 | 208.6321
268.1292 | 164.5996 | 182.3373 | 218.6096 | 209.8379
269.1292 | 165.1798 | 182.6524 | 219.4731 | 209.598
270.1292 | 165.3363 | 182.7776 | 220.0614 | 209.2587
271.1292 | 165.3651 | 183.4807 | 219.1798 | 209.1835
272.1292 | 164.8112 | 183.3053 | 219.0968 | 208.9608
273.1292 | 164.8076 | 186.1503 | 219.8068 | 207.7727
274.1292 | 165.5895 | 186.0426 | 219.4852 | 207.6699
275.1292 | 166.3936 | 184.9761 | 220.0356 | 207.2625
276.1292 | 166.8517 | 183.2635 | 220.663 | 209.0167
277.1292 | 167.0291 | 183.2618 | 221.9972 | 209.3701
278.1292 | 167.0732 | 182.9143 | 221.6769 | 208.8745
279.1292 | 167.5954 | 183.7935 | 223.4888 | 209.7746
280.1292 | 168.1317 | 185.0789 | 223.6054 | 209.5575
281.1292 | 168.3387 | 184.876 | 222.9464 | 208.6339
282.1292 | 168.4313 | 185.5258 | 223.8201 | 209.0301
283.1292 | 168.232 | 185.4674 | 223.4672 | 208.5903
284.1292 | 168.4456 | 185.322 | 223.946 | 209.3698
285.1292 | 168.5464 | 188.7384 | 224.3732 | 213.3807
286.1292 | 169.3137 | 188.1546 | 225.1555 | 213.7863
287.1292 | 169.6311 | 187.4997 | 224.8149 | 213.1734
288.1292 | 169.9582 | 189.3338 | 225.3981 | 215.4423
289.1292 | 170.3376 | 189.5846 | 225.8477 | 215.003
290.1448 | 170.7177 | 189.2458 | 226.9828 | 214.0286
291.1292 | 171.5769 | 189.3855 | 228.6726 | 213.9231
292.1292 | 171.9188 | 189.7024 | 228.2201 | 212.5573
293.1292 | 172.0003 | 189.3113 | 227.9553 | 212.6745
294.1292 | 171.8807 | 189.0248 | 227.2282 | 213.9904
295.1448 | 171.9318 | 189.8777 | 227.0498 | 214.69
296.1292 | 172.0989 | 188.9168 | 229.1628 | 214.4409
297.1292 | 172.4045 | 188.7516 | 228.8966 | 215.4756
298.1292 | 172.5008 | 189.3637 | 229.6973 | 215.5711
299.1292 | 172.7584 | 191.9978 | 230.7057 | 215.6233
300.1292 | 173.3155 | 192.628 | 230.8761 | 216.0203
301.1292 | 173.6532 | 192.2099 | 230.4762 | 217.3516
302.1292 | 173.4327 | 191.5906 | 229.3621 | 217.6515
303.1292 | 173.4766 | 191.5427 | 230.0785 | 218.072
304.1292 | 173.8403 | 190.8249 | 229.9098 | 218.6405
305.1292 | 174.1225 | 190.2836 | 229.8172 | 218.3517
306.1292 | 174.8945 | 190.125 | 228.9884 | 218.9014
307.1292 | 176.0958 | 189.0153 | 228.4745 | 221.4064
308.1292 | 176.4807 | 189.8275 | 229.4597 | 222.3371
309.1292 | 176.8797 | 190.7602 | 230.5995 | 223.9183
310.1292 | 177.0166 | 191.6946 | 231.4382 | 224.6405
311.1292 | 177.3601 | 191.0359 | 231.7624 | 222.8389
312.1292 | 177.4965 | 192.104 | 233.3457 | 222.7463
313.1292 | 177.7375 | 191.8787 | 232.6407 | 223.0725
314.1292 | 177.9656 | 191.4075 | 232.6072 | 223.3347
315.1292 | 178.1509 | 192.7087 | 231.7849 | 224.3662
316.1292 | 178.1287 | 193.0985 | 231.8428 | 224.6197
317.1292 | 177.9517 | 194.7349 | 230.7579 | 224.7303
318.1292 | 178.3886 | 195.9437 | 232.1845 | 225.5412
319.1292 | 178.4359 | 196.0697 | 232.9257 | 224.8726
320.1292 | 178.6606 | 195.4956 | 232.6281 | 223.4711
321.1292 | 178.7859 | 196.0219 | 233.2362 | 223.2988
322.1292 | 179.0813 | 195.2179 | 233.0246 | 223.5634
323.1292 | 179.6607 | 194.5813 | 232.8369 | 223.5917
324.1292 | 180.1116 | 193.6652 | 233.5523 | 224.4805
325.1292 | 180.2012 | 194.0764 | 233.8195 | 225.1065
326.1292 | 180.092 | 195.1134 | 233.7296 | 225.4362
327.1292 | 180.2177 | 194.0358 | 233.8353 | 225.2432
328.1292 | 180.303 | 193.2853 | 234.0877 | 226.1757
329.1292 | 179.957 | 192.7155 | 233.8636 | 225.6173
330.1292 | 179.7468 | 192.9005 | 233.1416 | 225.9754
331.1292 | 179.8227 | 193.3609 | 233.3613 | 227.5832
332.1292 | 180.7457 | 192.56 | 232.832 | 229.1588
333.1292 | 180.6867 | 192.3511 | 232.7139 | 229.0192
334.1292 | 181.1548 | 192.4372 | 233.5615 | 229.6105
335.1292 | 180.7637 | 192.4228 | 234.4571 | 230.4742
336.1292 | 180.0258 | 191.8627 | 234.1876 | 230.527
337.1292 | 180.8153 | 192.0216 | 234.8053 | 230.7544
338.1292 | 181.1537 | 191.3241 | 234.6406 | 230.8573
339.1292 | 180.7359 | 191.1673 | 234.7976 | 230.5074
340.1292 | 181.1421 | 193.3019 | 235.9771 | 231.301
341.1292 | 181.0058 | 194.092 | 236.1741 | 230.5198
342.1292 | 181.009 | 195.6244 | 235.4078 | 230.924
343.1292 | 181.1587 | 194.8659 | 236.6064 | 229.7429
344.1292 | 181.063 | 194.7931 | 235.3544 | 230.0783
345.1292 | 181.0371 | 194.5694 | 235.7084 | 229.702
346.1292 | 181.4328 | 196.915 | 235.3243 | 231.3686
347.1292 | 181.6911 | 197.963 | 235.4936 | 232.5126
348.1292 | 181.9766 | 198.726 | 235.8378 | 231.8375
349.1292 | 182.5867 | 199.1297 | 238.1253 | 233.8444
350.1292 | 183.2258 | 198.8738 | 238.3908 | 236.687
351.1292 | 183.6727 | 198.5367 | 238.9734 | 238.5256
352.1292 | 183.4405 | 198.8751 | 238.0772 | 240.4111
353.1292 | 183.8092 | 199.0223 | 237.688 | 240.2505
354.1292 | 184.0265 | 198.1727 | 237.9011 | 239.5563
355.1292 | 184.2164 | 197.0038 | 237.3517 | 239.4434
356.1292 | 183.9893 | 196.5821 | 239.0965 | 240.3461
357.1292 | 183.9421 | 197.809 | 240.6579 | 239.6599
358.1292 | 184.0945 | 198.9726 | 241.3813 | 239.1059
359.1292 | 185.6214 | 201.1653 | 240.9793 | 239.3894
360.1292 | 185.3477 | 200.9445 | 241.9861 | 239.4043
361.1292 | 185.3007 | 200.9905 | 243.0397 | 239.7267
362.1292 | 185.8357 | 202.1496 | 243.4474 | 240.1705
363.1292 | 185.6935 | 202.9259 | 243.9448 | 240.2934
364.1292 | 185.5815 | 203.4348 | 245.0704 | 240.5251
365.1292 | 186.018 | 202.7625 | 245.7049 | 239.6155
366.1292 | 186.459 | 203.4958 | 246.5111 | 240.6033
367.1292 | 186.7754 | 204.2873 | 245.9603 | 240.1367
368.1292 | 186.5353 | 205.0757 | 247.1308 | 239.7528
369.1292 | 186.9145 | 204.7506 | 247.406 | 241.2356
370.1292 | 187.3618 | 205.04 | 247.9276 | 241.1243
371.1292 | 187.466 | 205.1174 | 247.8097 | 240.0566
372.1292 | 187.7343 | 207.0294 | 248.3586 | 239.253
373.1292 | 187.3217 | 207.4874 | 248.2187 | 238.1759
374.1292 | 187.332 | 206.8253 | 248.6853 | 237.439
375.1292 | 187.4313 | 206.6557 | 249.542 | 238.4479
376.1292 | 186.8773 | 205.5187 | 250.6025 | 237.3288
377.1292 | 187.0512 | 206.1752 | 250.2741 | 237.4511
378.1292 | 187.1771 | 206.5916 | 250.688 | 237.4487
379.1448 | 187.6068 | 206.7761 | 249.9728 | 239.2605
380.1292 | 188.3638 | 208.1491 | 250.5015 | 241.315
381.1292 | 189.1838 | 207.8791 | 251.8151 | 241.727
382.1292 | 189.2857 | 208.2182 | 251.1288 | 240.366
383.1292 | 188.9087 | 207.247 | 251.4019 | 239.4291
384.1292 | 189.1905 | 206.5687 | 251.9105 | 242.3979
385.1292 | 189.3968 | 207.209 | 251.6404 | 242.8107
386.1292 | 190.0922 | 208.0943 | 252.3391 | 242.375
387.1292 | 190.482 | 208.3702 | 252.1452 | 243.0511
388.1292 | 190.8714 | 207.7639 | 252.8333 | 243.4285
389.1292 | 191.0257 | 207.5549 | 251.7197 | 245.1992
390.1292 | 191.5854 | 210.2378 | 252.0077 | 245.9938
391.1292 | 191.6082 | 211.4076 | 252.5278 | 246.2145
392.1292 | 192.1273 | 209.9741 | 253.2028 | 245.8816
393.1292 | 192.6759 | 210.2179 | 252.5433 | 246.7269
394.1292 | 192.7203 | 209.8269 | 253.4901 | 248.5102
395.1292 | 193.6219 | 209.5662 | 253.4911 | 248.1753
396.1292 | 194.2287 | 208.895 | 253.8809 | 246.8137
397.1292 | 195.0033 | 209.2908 | 255.1477 | 247.0214
398.1292 | 195.4699 | 209.2951 | 254.8891 | 246.6567
399.1292 | 195.6758 | 208.9794 | 255.1513 | 246.9994
400.1292 | 196.4578 | 209.8436 | 255.7058 | 245.5996
401.1292 | 197.0923 | 210.0565 | 257.4592 | 244.8966
402.1292 | 197.1308 | 209.8017 | 257.3311 | 244.6849
403.1292 | 196.9163 | 209.7547 | 257.0231 | 245.1544
404.1292 | 197.4549 | 208.3272 | 255.6579 | 244.2769
405.1292 | 197.2288 | 207.4248 | 255.6953 | 245.4325
406.1292 | 197.2001 | 207.5186 | 256.1858 | 245.8481
407.1292 | 197.2847 | 207.4909 | 257.3282 | 245.3924
408.1292 | 197.636 | 208.4466 | 259.2036 | 245.9811
409.1292 | 198.5665 | 210.5027 | 260.2582 | 246.5874
410.1292 | 199.3165 | 211.2509 | 259.8691 | 246.7609
411.1292 | 199.9984 | 210.9306 | 261.0063 | 247.5662
412.1292 | 200.0922 | 211.4328 | 261.9479 | 247.6194
413.1292 | 200.964 | 210.8968 | 262.4445 | 246.7124
414.1292 | 200.5202 | 210.5308 | 261.904 | 246.9583
415.1292 | 200.5362 | 211.5817 | 262.5885 | 246.471
416.1292 | 201.9724 | 212.1076 | 262.4887 | 248.8076
417.1292 | 202.2332 | 211.9535 | 263.0503 | 249.5381
418.1292 | 202.8229 | 213.0515 | 263.7261 | 251.0578
419.1292 | 202.985 | 212.972 | 263.6956 | 250.774
420.1292 | 203.2729 | 213.0631 | 264.9538 | 251.0184
421.1292 | 203.9427 | 212.7122 | 264.1556 | 250.7721
422.1292 | 203.821 | 211.8374 | 263.0736 | 251.2319
423.1292 | 204.2953 | 211.6696 | 264.4185 | 250.8316
424.1292 | 204.2266 | 210.9721 | 263.6614 | 250.6104
425.1292 | 204.4866 | 210.8865 | 264.3626 | 249.5512
426.1292 | 205.7509 | 211.0909 | 264.9459 | 249.3665
427.1292 | 207.0529 | 211.3481 | 265.3369 | 248.5486
428.1292 | 207.9497 | 213.4084 | 265.0854 | 249.2813
429.1292 | 207.4584 | 214.5389 | 265.1411 | 249.2381
430.1292 | 207.6702 | 217.8461 | 266.3566 | 250.6694
431.1292 | 208.1792 | 217.2718 | 267.155 | 251.6374
432.1292 | 209.0191 | 216.5999 | 267.1962 | 253.3867
433.1292 | 210.9293 | 217.0918 | 267.579 | 255.4242
434.1292 | 211.3654 | 216.8448 | 267.2073 | 257.032
435.1292 | 211.3964 | 216.6082 | 267.4134 | 256.1358
436.1292 | 212.223 | 216.2707 | 269.2451 | 257.0221
437.1292 | 212.8677 | 216.3845 | 270.2261 | 256.4767
438.1292 | 213.5695 | 216.1269 | 270.5326 | 257.402
439.1292 | 214.3887 | 216.816 | 271.5519 | 258.7234
440.1292 | 214.7613 | 217.1997 | 271.9532 | 258.5578
441.1292 | 214.7742 | 217.1494 | 273.7077 | 259.7576
442.1292 | 214.7741 | 216.7235 | 273.4062 | 260.1024
443.1292 | 215.5592 | 218.9139 | 272.7917 | 261.9143
444.1292 | 215.907 | 221.3626 | 272.4631 | 261.9072
445.1292 | 216.2839 | 223.6439 | 274.4021 | 261.9304
446.1292 | 216.6367 | 225.5816 | 275.7736 | 261.4802
447.1292 | 217.2687 | 225.6118 | 276.8963 | 263.3421
448.1292 | 217.1546 | 227.7664 | 277.1576 | 262.3134
449.1292 | 217.6257 | 227.6128 | 277.3352 | 262.0153
450.1292 | 218.0909 | 227.9398 | 277.2333 | 262.7808
451.1292 | 218.973 | 226.9943 | 276.5124 | 262.1387
452.1292 | 219.5482 | 226.3922 | 276.6494 | 262.5839
453.1292 | 220.0471 | 226.0285 | 277.5451 | 263.1464
454.1292 | 220.1376 | 225.3167 | 277.0924 | 262.9901
455.1292 | 221.1536 | 224.5919 | 277.3017 | 264.0355
456.1292 | 222.2153 | 223.5812 | 277.6501 | 263.9149
457.1292 | 222.9409 | 223.1248 | 278.8287 | 263.5819
458.1292 | 222.8637 | 222.9434 | 279.0475 | 262.7996
459.1292 | 222.9266 | 223.5581 | 278.4976 | 262.1747
460.1292 | 223.4682 | 223.8641 | 280.3454 | 261.4781
461.1292 | 223.9022 | 224.4234 | 280.4578 | 262.4346
462.1292 | 223.9727 | 224.1372 | 282.0813 | 261.6981
463.1292 | 224.6354 | 224.5326 | 282.2411 | 260.4446
464.1292 | 224.7522 | 224.1458 | 282.3846 | 262.3702
465.1292 | 225.6406 | 223.9765 | 283.4501 | 261.3036
466.1292 | 226.7995 | 222.3797 | 282.5508 | 260.2489
467.1292 | 226.9268 | 221.8233 | 282.9915 | 260.0322
468.1292 | 226.781 | 223.1679 | 283.4894 | 259.6313
469.1292 | 227.3724 | 222.7772 | 283.3845 | 260.5435
470.1292 | 228.3261 | 222.9598 | 284.1852 | 260.6348
471.1292 | 229.2619 | 223.7001 | 284.9402 | 260.8174
472.1292 | 230.1765 | 223.4238 | 286.0052 | 261.0786
473.1292 | 230.7152 | 223.2057 | 287.1777 | 261.4949
474.1292 | 231.4397 | 222.8955 | 287.676 | 261.1999
475.1292 | 231.8302 | 223.769 | 289.0582 | 261.8229
476.1292 | 232.6258 | 223.6923 | 288.7933 | 261.6852
477.1292 | 233.1495 | 224.1217 | 288.6703 | 262.967
478.1292 | 233.1217 | 224.2302 | 289.2494 | 262.3837
479.1292 | 233.4511 | 224.4156 | 290.003 | 263.3323
480.1292 | 234.0233 | 224.696 | 290.6135 | 263.982
481.1292 | 234.5355 | 224.3209 | 291.1262 | 264.534
482.1292 | 234.9186 | 224.6348 | 290.6513 | 265.3786
483.1292 | 235.3552 | 225.288 | 289.9826 | 265.8052
484.1292 | 235.3073 | 226.4581 | 290.263 | 265.572
485.1292 | 234.965 | 227.0973 | 289.5848 | 267.6695
486.1292 | 234.3728 | 228.1366 | 288.8783 | 268.4795
487.1292 | 234.1432 | 228.7604 | 289.3454 | 268.6297
488.1292 | 234.3744 | 230.2728 | 290.2599 | 269.1649
489.1292 | 234.3742 | 231.5391 | 290.4127 | 268.9997
490.1292 | 234.6167 | 231.7999 | 290.8666 | 270.4182
491.1448 | 234.6044 | 231.7347 | 291.0311 | 269.8306
492.1292 | 235.3474 | 233.2402 | 291.9127 | 271.789
493.1292 | 235.7126 | 235.2335 | 292.0282 | 274.8478
494.1292 | 235.9286 | 234.4604 | 291.8649 | 275.1218
495.1292 | 236.627 | 234.1793 | 291.9033 | 274.6263
496.1292 | 236.8551 | 232.9164 | 291.417 | 274.8778
497.1292 | 237.1434 | 233.44 | 293.7766 | 274.8846
498.1292 | 237.7825 | 232.6037 | 293.9641 | 274.6417
499.1292 | 236.9861 | 231.7145 | 294.3214 | 274.7024
500.1292 | 236.9764 | 231.1631 | 294.6527 | 275.696
501.1292 | 236.8598 | 230.8227 | 293.9081 | 276.6921
502.1292 | 236.4881 | 231.771 | 295.32 | 277.5282
503.1292 | 236.5188 | 232.2442 | 295.6199 | 279.4194
504.1292 | 236.0495 | 234.9382 | 296.687 | 280.1468
505.1292 | 236.1044 | 237.1189 | 297.3533 | 281.7278
506.1292 | 236.4348 | 236.9826 | 299.1333 | 283.8878
507.1292 | 237.0509 | 236.4066 | 298.8354 | 284.6334
508.1292 | 237.2614 | 238.2766 | 300.1181 | 284.801
509.1292 | 238.1423 | 238.415 | 300.0175 | 285.3583
510.1292 | 239.4688 | 236.5328 | 298.7708 | 285.2411
511.1292 | 239.5788 | 235.541 | 297.714 | 284.4466
512.1292 | 239.8589 | 234.8021 | 297.9177 | 283.9
513.1292 | 239.9033 | 234.4454 | 298.1277 | 283.9956
514.1292 | 240.3436 | 234.6856 | 298.5648 | 283.3283
515.1292 | 240.656 | 234.966 | 299.8102 | 284.0651
516.1292 | 241.2568 | 235.9006 | 301.5611 | 283.8251
517.1292 | 241.4102 | 235.6292 | 301.7246 | 283.6624
518.1292 | 242.1 | 235.5166 | 301.5 | 283.2148
519.1292 | 242.2893 | 236.0865 | 302.0563 | 282.7021
520.1292 | 242.5543 | 237.2372 | 302.3076 | 282.0396
521.1292 | 243.2555 | 237.4977 | 302.3708 | 281.3021
522.1292 | 243.1495 | 236.4154 | 302.9439 | 281.7102
523.1292 | 244.6327 | 235.535 | 302.7609 | 281.208
524.1292 | 244.8509 | 235.2697 | 304.6896 | 282.0529
525.1448 | 245.1337 | 234.406 | 303.4324 | 282.1947
526.1292 | 244.7779 | 234.0801 | 303.2784 | 282.1993
527.1292 | 245.0951 | 234.6588 | 302.3279 | 282.1339
528.1292 | 244.8553 | 233.7561 | 301.3712 | 282.9095
529.1292 | 244.6899 | 233.3366 | 300.7005 | 281.9423
530.1292 | 244.2772 | 233.7926 | 301.1658 | 282.2904
531.1292 | 244.9772 | 234.3993 | 301.2571 | 280.2994
532.1292 | 244.3147 | 234.5253 | 301.9757 | 278.9071
533.1292 | 244.4079 | 235.4272 | 302.5647 | 278.2567
534.1292 | 244.5238 | 235.876 | 303.5226 | 278.7372
535.1292 | 244.4331 | 236.6932 | 302.3807 | 277.2997
536.1292 | 244.7849 | 238.4505 | 302.8702 | 277.2117
537.1292 | 244.6253 | 238.4125 | 303.634 | 277.0234
538.1292 | 244.3459 | 238.4623 | 302.5459 | 276.4897
539.1292 | 244.8727 | 238.3762 | 302.9358 | 276.4819
540.1292 | 246.0695 | 237.8644 | 303.9377 | 278.5349
541.1292 | 245.9384 | 238.2346 | 304.7031 | 278.6141
542.1292 | 246.6348 | 239.1115 | 306.5293 | 279.833
543.1292 | 247.0745 | 239.1501 | 306.925 | 280.8956
544.1292 | 247.149 | 238.7205 | 307.1643 | 280.2309
545.1292 | 247.1291 | 240.181 | 307.9796 | 282.026
546.1292 | 247.6129 | 240.4408 | 309.7459 | 284.8192
547.1292 | 247.7961 | 242.2767 | 310.8304 | 285.4441
548.1292 | 248.0477 | 243.7035 | 311.5105 | 287.3339
549.1292 | 248.1457 | 246.872 | 311.824 | 289.9809
550.1292 | 248.5736 | 248.3651 | 312.9431 | 289.7244
551.1292 | 249.6663 | 251.2505 | 313.4883 | 291.7044
552.1292 | 249.8834 | 251.3964 | 313.7179 | 291.3354
553.1292 | 250.1573 | 251.5253 | 313.3727 | 291.6239
554.1292 | 251.2476 | 251.5337 | 313.8765 | 293.2005
555.1292 | 251.5596 | 251.6001 | 314.1556 | 294.4356
556.1292 | 251.2891 | 252.4757 | 313.4172 | 294.7717
557.1292 | 251.5282 | 252.6353 | 313.4899 | 295.325
558.1292 | 252.3179 | 254.1894 | 313.1623 | 297.721
559.1292 | 252.6188 | 253.3431 | 313.7855 | 298.4265
560.1292 | 252.7187 | 253.6153 | 314.0897 | 299.9287
561.1292 | 253.2946 | 255.6258 | 315.3615 | 301.8342
562.1292 | 253.537 | 256.8409 | 316.7958 | 300.8861
563.1292 | 254.7671 | 261.1324 | 318.2863 | 299.8277
564.1292 | 255.8195 | 260.7161 | 318.7384 | 299.5934
565.1292 | 256.9625 | 259.9969 | 319.4834 | 299.9908
566.1292 | 257.7373 | 259.2434 | 321.2364 | 300.0583
567.1292 | 258.2686 | 262.203 | 321.67 | 301.0489
568.1292 | 258.4418 | 262.1139 | 322.6863 | 303.7967
569.1292 | 257.8754 | 263.0091 | 321.7378 | 304.6024
570.1292 | 258.7108 | 262.1808 | 321.9785 | 307.195
571.1292 | 258.3689 | 261.6595 | 322.9349 | 307.8197
572.1292 | 258.6186 | 262.375 | 322.3459 | 307.918
573.1292 | 258.7824 | 262.6492 | 322.4241 | 309.116
574.1292 | 258.5034 | 261.8071 | 323.6869 | 308.1942
575.1292 | 258.1345 | 262.8886 | 323.0523 | 309.1749
576.1292 | 257.4093 | 262.0394 | 322.842 | 310.5342
577.1292 | 257.4765 | 262.5614 | 323.0034 | 311.0805
578.1292 | 257.8867 | 263.4788 | 324.1551 | 313.6485
579.1292 | 258.3584 | 265.9862 | 324.8425 | 314.6524
580.1292 | 258.9873 | 267.6216 | 325.7353 | 314.4854
581.1292 | 259.4521 | 266.802 | 326.1323 | 314.0952
582.1292 | 259.9327 | 269.6124 | 325.8642 | 313.4948
583.1292 | 260.3525 | 270.6862 | 325.9741 | 314.2437
584.1292 | 260.9153 | 268.6246 | 326.8261 | 312.7812
585.1292 | 261.3902 | 268.6001 | 326.2342 | 312.7929
586.1292 | 261.3733 | 268.4196 | 325.6476 | 313.8492
587.1292 | 261.7093 | 267.5556 | 325.5976 | 312.6848
588.1292 | 262.8753 | 266.7385 | 327.0521 | 312.5603
589.1292 | 264.1227 | 267.2997 | 327.9784 | 311.3646
590.1292 | 264.3579 | 268.6268 | 329.0144 | 309.7945
591.1292 | 264.7738 | 268.0174 | 329.3938 | 310.2009
592.1292 | 265.4062 | 268.6317 | 330.835 | 309.6435
593.1292 | 265.7785 | 268.7021 | 333.1362 | 311.0889
594.1292 | 265.8063 | 268.9091 | 333.7325 | 312.3676
595.1292 | 266.4828 | 269.4581 | 334.0132 | 314.0829
596.1292 | 266.8683 | 271.3624 | 332.9425 | 314.8302
597.1292 | 267.9254 | 273.3101 | 333.7332 | 317.0379
598.1292 | 269.0162 | 274.228 | 335.0674 | 317.2427
599.1292 | 270.5633 | 274.2765 | 337.0692 | 317.2691
600.1292 | 271.9728 | 273.4478 | 338.7166 | 315.994
601.1292 | 272.4267 | 274.0245 | 338.4181 | 317.422
602.1292 | 273.2667 | 276.1574 | 339.1322 | 317.6726
603.1292 | 273.7178 | 278.309 | 339.7323 | 320.2466
604.1292 | 274.3824 | 276.6294 | 339.7007 | 320.6684
605.1292 | 274.2085 | 277.1191 | 339.0741 | 320.6562
606.1292 | 274.4631 | 278.7159 | 339.9984 | 321.5238
607.1292 | 275.4834 | 279.8031 | 340.246 | 321.1197
608.1292 | 276.5535 | 281.1742 | 340.6961 | 319.6661
609.1292 | 278.5829 | 283.4119 | 341.0331 | 319.4799
610.1292 | 280.6343 | 283.2047 | 340.2879 | 317.2374
611.1292 | 280.3299 | 282.2073 | 340.2595 | 316.9653
612.1292 | 280.8245 | 280.9701 | 339.5227 | 316.2946
613.1292 | 280.8587 | 279.9535 | 338.7757 | 315.3592
614.1292 | 280.505 | 278.5853 | 339.5683 | 314.0074
615.1292 | 280.9649 | 277.6401 | 338.4697 | 313.6508
616.1292 | 281.9879 | 277.1105 | 339.6047 | 312.1177
617.1292 | 282.0516 | 278.9419 | 340.738 | 313.8538
618.1292 | 281.8379 | 278.968 | 342.4484 | 311.6183
619.1292 | 281.2584 | 277.967 | 341.5464 | 311.4766
620.1292 | 281.1979 | 278.3323 | 341.1752 | 314.5896
621.1292 | 281.8717 | 277.7924 | 341.6754 | 315.6434
622.1292 | 281.3358 | 278.5863 | 341.1186 | 316.6055
623.1292 | 281.4445 | 280.2794 | 341.2033 | 317.7642
624.1292 | 281.4614 | 283.072 | 342.1335 | 320.1391
625.1292 | 280.5775 | 282.152 | 341.7966 | 319.3764
626.1292 | 280.4186 | 280.6743 | 341.3505 | 319.015
627.1292 | 280.633 | 280.3416 | 341.2109 | 317.5294
628.1292 | 280.0851 | 283.5503 | 341.5895 | 317.1683
629.1292 | 280.1278 | 285.7475 | 341.0032 | 315.1893
630.1292 | 280.5902 | 284.6352 | 340.9824 | 314.0127
631.1292 | 280.6745 | 284.9698 | 340.9664 | 313.8177
632.1292 | 280.014 | 283.9899 | 342.7074 | 314.1097
633.1292 | 279.8351 | 283.2292 | 342.5705 | 314.1786
634.1292 | 280.2481 | 282.4297 | 343.0228 | 313.871
635.1292 | 280.3822 | 281.4452 | 342.0912 | 312.2867
636.1292 | 281.3355 | 281.5992 | 342.165 | 312.9429
637.1292 | 282.3759 | 281.1911 | 342.819 | 311.7736
638.1292 | 282.8777 | 280.5248 | 342.5791 | 311.0521
639.1292 | 283.2865 | 280.6066 | 343.6961 | 309.3627
640.1292 | 283.6727 | 278.7326 | 342.7142 | 308.0504
641.1292 | 284.9608 | 278.1928 | 343.0782 | 307.2242
642.1292 | 285.0926 | 278.1667 | 342.2504 | 305.6667
643.1292 | 286.9069 | 277.6885 | 341.6966 | 304.3373
644.1292 | 286.9012 | 277.1911 | 341.7439 | 304.6094
645.1292 | 286.2372 | 277.9438 | 341.5706 | 303.6826
646.1292 | 285.5879 | 278.6048 | 341.5584 | 303.2618
647.1292 | 285.6354 | 278.6101 | 341.4668 | 303.2595
648.1292 | 285.8406 | 279.2033 | 342.1875 | 303.1051
649.1292 | 287.4489 | 278.6073 | 343.4508 | 302.9707
650.1292 | 286.583 | 277.5435 | 343.0548 | 301.772
651.1292 | 285.9176 | 277.168 | 343.0003 | 300.8797
652.1292 | 286.8647 | 276.3576 | 342.6177 | 299.8645
653.1292 | 285.8486 | 277.0458 | 342.4795 | 299.6929
654.1292 | 286.2687 | 275.8445 | 342.7824 | 300.2374
655.1292 | 286.6854 | 275.9669 | 342.5444 | 299.6038
656.1292 | 286.3854 | 276.7413 | 341.6192 | 297.9512
657.1292 | 285.9546 | 275.3449 | 342.1777 | 299.1453
658.1292 | 285.5668 | 275.1724 | 342.1025 | 298.8837
659.1292 | 285.0583 | 274.8415 | 340.8639 | 297.4863
660.1292 | 285.5566 | 274.7491 | 341.4825 | 297.9556
661.1292 | 286.3267 | 275.634 | 341.0877 | 297.1002
662.1292 | 286.5701 | 274.3831 | 341.533 | 295.7097
663.1292 | 287.2315 | 274.4196 | 341.4392 | 294.5877
664.1292 | 287.3301 | 273.635 | 340.2203 | 293.6116
665.1292 | 286.7026 | 273.9925 | 340.0279 | 293.5796
666.1292 | 285.9659 | 277.1981 | 340.3508 | 296.6204
667.1292 | 285.6981 | 276.2068 | 339.8484 | 300.0125
668.1292 | 285.0731 | 275.8313 | 339.787 | 299.7877
669.1292 | 283.9594 | 276.4464 | 338.853 | 300.1113
670.1292 | 284.7893 | 277.3141 | 338.0199 | 301.3886
671.1292 | 283.7926 | 277.3093 | 337.26 | 302.7101
672.1292 | 283.4485 | 279.5723 | 337.0486 | 303.8921
673.1292 | 283.5702 | 279.4925 | 336.9799 | 302.7117
674.1292 | 283.5328 | 280.4514 | 335.5323 | 301.7514
675.1292 | 283.5421 | 279.8727 | 334.8644 | 301.7485
676.1292 | 283.752 | 278.7586 | 334.6959 | 299.8757
677.1292 | 283.9107 | 278.69 | 335.4322 | 300.296
678.1292 | 283.844 | 277.5684 | 335.7748 | 301.4645
679.1292 | 283.8833 | 277.7592 | 335.9628 | 302.1727
680.1292 | 284.588 | 280.2778 | 335.321 | 302.8121
681.1292 | 284.8436 | 281.092 | 335.7419 | 302.2134
682.1292 | 285.3568 | 281.9449 | 336.9323 | 301.959
683.1292 | 285.059 | 281.4768 | 336.6642 | 303.8378
684.1292 | 284.1333 | 281.3376 | 336.4166 | 304.6077
685.1292 | 283.6985 | 279.5166 | 335.9614 | 303.972
686.1292 | 283.7094 | 279.3145 | 336.3649 | 304.037
687.1292 | 283.347 | 278.9787 | 337.1996 | 302.5414
688.1292 | 282.7334 | 278.3927 | 338.0496 | 301.1484
689.1292 | 283.0906 | 278.5509 | 337.2132 | 300.3676
690.1292 | 282.8433 | 279.4636 | 338.1185 | 301.556
691.1292 | 282.6305 | 280.4327 | 338.7684 | 302.8148
692.1292 | 282.7282 | 281.8123 | 338.8446 | 303.2795
693.1292 | 282.0407 | 282.692 | 339.1391 | 304.6842
694.1292 | 281.7831 | 282.5602 | 338.7148 | 304.7177
695.1292 | 281.5413 | 282.6073 | 337.9714 | 305.2194
696.1292 | 281.9867 | 281.2323 | 335.8667 | 304.8022
697.1292 | 283.0616 | 280.426 | 336.0221 | 303.0364
698.1292 | 282.4138 | 282.8455 | 335.7204 | 301.8417
699.1292 | 282.3978 | 281.1996 | 336.1657 | 301.858
700.1292 | 283.1218 | 280.3551 | 336.959 | 301.2181
701.1292 | 284.967 | 279.4484 | 339.6369 | 302.0508
702.1292 | 285.6025 | 278.6564 | 339.2523 | 300.313
703.1292 | 287.0935 | 278.2601 | 339.4123 | 299.2785
704.1292 | 288.9679 | 278.0143 | 338.8541 | 297.998
705.1292 | 292.1887 | 278.719 | 338.7046 | 297.1029
706.1292 | 294.2375 | 280.0387 | 338.7631 | 295.6095
707.1292 | 294.4886 | 282.0782 | 340.915 | 296.1523
708.1292 | 296.1649 | 280.9959 | 341.2606 | 296.3197
709.1292 | 297.3631 | 281.6032 | 341.0987 | 296.8909
710.1292 | 298.1179 | 282.1223 | 341.1151 | 296.3019
711.1292 | 300.1492 | 282.5412 | 342.1553 | 296.4712
712.1292 | 301.6685 | 282.9425 | 341.6742 | 295.8609
713.1292 | 303.2286 | 283.5191 | 341.5522 | 294.9948
714.1292 | 303.3555 | 282.7953 | 341.0422 | 294.3945
715.1292 | 304.092 | 282.8738 | 341.886 | 292.3001
716.1292 | 303.4442 | 282.8011 | 340.7947 | 290.4399
717.1292 | 305.304 | 281.5064 | 339.4764 | 290.0844
718.1292 | 306.8812 | 281.1824 | 338.165 | 289.4608
719.1292 | 306.5687 | 280.1265 | 336.4479 | 289.3543
720.1292 | 308.9514 | 280.3583 | 336.4967 | 287.9004
721.1448 | 314.3262 | 279.2822 | 335.8095 | 287.1768
722.1292 | 319.7356 | 279.9624 | 336.5264 | 285.9007
723.1448 | 326.0269 | 280.0437 | 336.494 | 284.8968
724.1448 | 329.6567 | 280.0491 | 336.3658 | 285.2374
725.1448 | 332.0326 | 279.9274 | 336.1569 | 284.8041
726.1292 | 334.0207 | 280.158 | 336.8846 | 285.781
727.1292 | 334.8745 | 279.5135 | 337.365 | 285.1652
728.1292 | 335.2686 | 280.4492 | 336.9838 | 284.5071
729.1292 | 333.6979 | 280.8896 | 336.8629 | 285.1544
730.1292 | 332.7612 | 280.3594 | 336.1488 | 285.5236
731.1292 | 334.0358 | 282.2942 | 337.7369 | 287.2537
732.1292 | 334.6182 | 283.8762 | 339.1833 | 287.7437
733.1292 | 333.8324 | 286.1654 | 340.2434 | 291.538
734.1292 | 334.9111 | 285.5538 | 340.5535 | 292.5815
735.1292 | 336.653 | 286.704 | 340.9761 | 291.8455
736.1292 | 337.1514 | 287.8982 | 341.7895 | 294.203
737.1292 | 337.5894 | 289.2621 | 343.1458 | 293.5816
738.1292 | 338.7197 | 289.0563 | 343.5255 | 292.2218
739.1292 | 339.5444 | 290.17 | 344.2104 | 293.9283
740.1292 | 340.0914 | 289.7933 | 345.9722 | 295.0029
741.1292 | 339.1544 | 289.28 | 346.9782 | 295.3927
742.1292 | 340.0658 | 289.9451 | 347.7623 | 296.9723
743.1292 | 340.5261 | 292.8896 | 347.2846 | 298.1194
744.1292 | 340.1709 | 293.7683 | 347.2085 | 297.0821
745.1292 | 339.7 | 293.5838 | 346.1768 | 296.4821
746.1292 | 336.9822 | 292.4256 | 346.7691 | 295.9169
747.1292 | 336.3945 | 291.9593 | 345.5981 | 295.0077
748.1292 | 336.6569 | 291.8916 | 344.875 | 294.3162
749.1292 | 338.813 | 292.5336 | 345.494 | 293.9881
750.1292 | 338.1895 | 291.8994 | 345.4548 | 293.9665
751.1292 | 338.9404 | 291.4014 | 345.4828 | 293.7823
752.1292 | 339.3181 | 290.965 | 344.6779 | 294.3844
753.1292 | 340.5141 | 290.9629 | 344.7775 | 294.001
754.1292 | 340.9528 | 291.4498 | 345.0363 | 294.1443
755.1292 | 340.8753 | 291.2968 | 345.3296 | 295.0451
756.1292 | 338.6492 | 290.7914 | 347.2524 | 294.5396
757.1292 | 336.3715 | 290.4153 | 347.5014 | 294.528
758.1292 | 335.3946 | 291.0228 | 346.5003 | 296.2526
759.1292 | 335.4388 | 292.1183 | 348.4755 | 299.2705
760.1292 | 337.5483 | 294.5011 | 349.295 | 300.8462
761.1292 | 340.5873 | 295.4811 | 350.3543 | 300.2143
762.1292 | 340.481 | 295.5591 | 350.3239 | 300.7268
763.1292 | 339.216 | 296.2137 | 349.0756 | 301.9601
764.1292 | 337.6647 | 295.933 | 348.09 | 301.6096
765.1292 | 337.5477 | 296.7143 | 348.2569 | 303.5689
766.1292 | 337.2636 | 297.4822 | 347.4308 | 304.9661
767.1292 | 339.2511 | 297.3564 | 347.8094 | 305.8333
768.1292 | 339.9186 | 298.1469 | 349.4164 | 305.5454
769.1292 | 341.1506 | 297.7716 | 349.87 | 305.0528
770.1292 | 342.3067 | 297.1721 | 348.9714 | 304.085
771.1292 | 342.8453 | 298.4223 | 350.2407 | 304.8487
772.1292 | 345.4006 | 300.1858 | 350.4823 | 306.536
773.1292 | 345.3091 | 300.2857 | 350.8281 | 309.0796
774.1292 | 344.4316 | 299.7559 | 349.9931 | 308.9629
775.1292 | 342.9785 | 299.5266 | 350.5441 | 309.643
776.1292 | 344.756 | 298.4757 | 349.4084 | 308.021
777.1292 | 344.8605 | 298.0364 | 349.0014 | 306.4985
778.1292 | 343.27 | 298.9026 | 350.315 | 306.0142
779.1292 | 343.9005 | 297.8721 | 350.9316 | 305.7274
780.1292 | 343.4436 | 297.9046 | 350.6862 | 305.7205
781.1292 | 343.2875 | 297.6833 | 351.6335 | 304.9261
782.1292 | 342.3123 | 298.3207 | 351.5601 | 306.4854
783.1292 | 345.3667 | 297.6509 | 351.0396 | 307.5762
784.1292 | 343.3267 | 297.4792 | 350.4788 | 307.112
785.1292 | 342.108 | 296.9125 | 349.533 | 306.6708
786.1292 | 341.7244 | 298.5184 | 349.173 | 306.1864
787.1292 | 342.5273 | 298.2281 | 348.2284 | 305.8377
788.1292 | 344.1648 | 298.3563 | 347.7672 | 305.0013
789.1292 | 343.9375 | 297.6373 | 347.185 | 304.2208
790.1292 | 346.9796 | 298.2781 | 347.533 | 305.7217
791.1292 | 347.3563 | 299.0219 | 347.7293 | 306.1186
792.1292 | 349.2892 | 298.5676 | 346.8613 | 306.5278
793.1292 | 350.1446 | 298.9485 | 347.2711 | 307.287
794.1292 | 351.2377 | 301.0441 | 347.0463 | 306.2296
795.1292 | 351.389 | 299.9451 | 346.9796 | 305.806
796.1292 | 348.4574 | 300.4845 | 346.4239 | 307.1312
797.1292 | 346.3943 | 300.312 | 347.1314 | 306.097
798.1292 | 344.5825 | 299.7819 | 347.4163 | 307.0677
799.1292 | 343.8186 | 297.7421 | 347.2098 | 305.1839
800.1292 | 346.8518 | 297.1991 | 346.8083 | 304.3051
801.1292 | 347.2621 | 295.8651 | 346.3291 | 302.841
802.1292 | 344.9333 | 295.4476 | 346.0815 | 301.9858
803.1292 | 343.6154 | 295.9716 | 345.3532 | 302.3778
804.1292 | 343.2756 | 295.6944 | 346.0643 | 301.5027
805.1292 | 344.669 | 294.7009 | 346.1601 | 300.8022
806.1292 | 341.7134 | 294.699 | 346.6174 | 299.5034
807.1292 | 343.2532 | 293.5861 | 347.055 | 299.6974
808.1292 | 341.4732 | 293.6314 | 348.2084 | 299.9701
809.1292 | 341.1473 | 292.4728 | 348.6663 | 300.3056
810.1292 | 340.6791 | 292.6861 | 348.7432 | 299.2456
811.1292 | 341.5142 | 294.6197 | 348.5784 | 297.8195
812.1292 | 341.6676 | 293.126 | 347.9696 | 296.8152
813.1292 | 342.7451 | 292.2413 | 347.2343 | 296.2538
814.1292 | 342.417 | 292.5631 | 346.7506 | 295.2552
815.1292 | 341.8671 | 292.8842 | 346.0826 | 296.3778
816.1292 | 341.5731 | 292.0518 | 346.5219 | 296.516
817.1292 | 341.8423 | 291.3678 | 346.1594 | 297.1844
818.1292 | 341.2576 | 291.0877 | 345.5581 | 296.5966
819.1292 | 339.7475 | 290.3891 | 345.5242 | 297.6835
820.1292 | 341.8448 | 290.3168 | 345.4635 | 299.6135
821.1292 | 339.372 | 290.1438 | 344.9589 | 301.4318
822.1292 | 340.8508 | 290.4532 | 344.6181 | 304.175
823.1292 | 342.3682 | 289.9401 | 344.65 | 303.574
824.1292 | 343.2951 | 290.3974 | 344.541 | 304.0584
825.1292 | 342.1562 | 290.4742 | 344.2709 | 303.3127
826.1292 | 340.4424 | 290.6743 | 342.8296 | 304.5864
827.1292 | 344.1644 | 291.037 | 343.1291 | 305.7984
828.1292 | 344.8947 | 294.8645 | 344.1659 | 309.9977
829.1292 | 343.1346 | 293.9943 | 343.8433 | 309.8642
830.1292 | 342.4116 | 294.1796 | 344.3697 | 310.8177
831.1292 | 343.7067 | 293.3668 | 344.4642 | 312.2425
832.1292 | 341.1139 | 291.9417 | 343.2123 | 312.5385
833.1292 | 340.258 | 291.1079 | 342.997 | 313.569
834.1292 | 342.6535 | 292.6521 | 342.5958 | 313.822
835.1292 | 341.7804 | 292.5914 | 343.5765 | 315.5372
836.1292 | 343.4157 | 291.529 | 343.7542 | 315.8638
837.1292 | 344.6887 | 291.5684 | 344.2772 | 313.9992
838.1292 | 346.6883 | 291.0187 | 343.6887 | 313.7192
839.1292 | 343.8117 | 290.0528 | 344.2205 | 315.7489
840.1292 | 344.9034 | 289.6414 | 345.1435 | 314.7231
841.1292 | 347.2523 | 289.7689 | 345.6426 | 312.6888
842.1292 | 347.8915 | 290.2154 | 345.6778 | 311.9403
843.1292 | 347.93 | 290.5215 | 345.8853 | 310.5061
844.1292 | 350.591 | 290.207 | 346.0355 | 309.4202
845.1292 | 352.4716 | 291.1 | 345.903 | 307.8224
846.1292 | 353.6884 | 291.0243 | 346.182 | 307.2539
847.1292 | 354.3183 | 292.9982 | 346.7371 | 306.9549
848.1292 | 355.3808 | 294.4608 | 347.1882 | 309.2028
849.1292 | 355.7814 | 296.4735 | 347.8387 | 310.7007
850.1292 | 356.6887 | 296.2656 | 346.7931 | 311.6714
851.1292 | 356.3211 | 295.6339 | 348.2478 | 311.0159
852.1292 | 358.2349 | 295.5655 | 349.1157 | 311.1599
853.1292 | 357.6603 | 296.4318 | 349.6692 | 312.4025
854.1292 | 359.1608 | 295.6013 | 349.898 | 312.4878
855.1292 | 361.9523 | 295.4047 | 349.5884 | 311.3838
856.1292 | 364.0635 | 296.0133 | 350.5441 | 311.0837
857.1292 | 363.8093 | 296.6648 | 351.8887 | 310.2458
858.1292 | 363.1133 | 295.8228 | 352.4412 | 310.2795
859.1292 | 364.6475 | 295.4022 | 351.4066 | 309.4725
860.1292 | 367.6598 | 294.9335 | 350.8422 | 308.3236
861.1292 | 367.2203 | 295.7538 | 351.2833 | 309.027
862.1292 | 368.9512 | 294.9862 | 351.9464 | 309.3112
863.1292 | 370.621 | 294.2202 | 352.0244 | 309.0921
864.1292 | 368.7572 | 294.0731 | 352.8274 | 310.5412
865.1292 | 370.2406 | 292.8169 | 352.5853 | 309.8607
866.1292 | 369.4526 | 293.0652 | 351.8822 | 311.1939
867.1292 | 368.8644 | 293.5108 | 351.2743 | 312.0061
868.1292 | 369.4135 | 293.0863 | 351.2322 | 310.9712
869.1292 | 371.5056 | 294.4962 | 351.3296 | 310.4729
870.1292 | 371.7662 | 296.9308 | 352.8016 | 309.935
871.1292 | 372.7174 | 296.9326 | 353.3227 | 309.7051
872.1292 | 374.718 | 297.9957 | 354.0463 | 310.283
873.1292 | 375.9244 | 298.1946 | 355.6905 | 309.9766
874.1292 | 376.8923 | 296.7397 | 354.8152 | 309.1437
875.1292 | 378.1082 | 296.7891 | 355.5957 | 309.8019
876.1292 | 378.5874 | 296.9899 | 355.8325 | 309.9021
877.1292 | 378.6588 | 298.0205 | 355.8978 | 310.385
878.1292 | 379.6283 | 296.9012 | 356.6577 | 310.011
879.1292 | 379.4895 | 297.3877 | 356.4461 | 310.1111
880.1292 | 380.2877 | 296.9543 | 357.4654 | 310.5412
881.1292 | 379.9596 | 296.2873 | 357.0106 | 311.5996
882.1292 | 377.0997 | 296.7253 | 357.102 | 312.6967
883.1292 | 376.2673 | 295.8681 | 356.6174 | 313.01
884.1292 | 376.5152 | 290.8234 | 356.8283 | 310.5547
885.1292 | 376.9535 | 289.0615 | 358.1424 | 309.5199
886.1292 | 377.9046 | 290.8304 | 358.9641 | 309.948
887.1292 | 378.8321 | 290.9561 | 357.9311 | 310.1018
888.1292 | 379.7764 | 290.3995 | 358.9792 | 310.0253
889.1292 | 380.2211 | 292.8382 | 359.6692 | 311.0485
890.1292 | 378.2872 | 294.2908 | 360.0725 | 312.8928
891.1292 | 377.4666 | 292.9805 | 360.4828 | 312.587
892.1292 | 375.5411 | 294.7303 | 360.9521 | 314.302
893.1292 | 374.6247 | 298.0793 | 360.8419 | 316.0287
894.1292 | 374.4356 | 295.1472 | 361.2396 | 317.368
895.1292 | 373.3805 | 295.0229 | 360.4188 | 317.8688
896.1292 | 373.8565 | 298.0922 | 360.5983 | 317.9992
897.1292 | 377.2124 | 299.6818 | 362.185 | 301.7119
898.1292 | 376.7218 | 298.8871 | 362.806 | 317.2338
899.1292 | 376.1083 | 299.1845 | 363.746 | 317.6196
900.1292 | 376.5773 | 299.3696 | 361.9245 | 316.8044
901.1292 | 376.643 | 303.5953 | 361.1277 | 316.8893
902.1292 | 377.2151 | 308.9358 | 361.0298 | 319.3003
903.1448 | 377.8927 | 310.1933 | 360.9389 | 318.8254
904.1292 | 378.039 | 309.8501 | 360.8374 | 317.7535
905.1292 | 378.6636 | 310.0299 | 361.9106 | 321.5689
906.1292 | 379.6409 | 309.6718 | 362.3958 | 321.3667
907.1448 | 379.3241 | 312.3135 | 364.0431 | 324.6911
908.1448 | 378.6098 | 311.9501 | 364.8011 | 324.6061
909.1292 | 378.7161 | 311.0623 | 365.8764 | 322.9194
910.1292 | 380.6097 | 312.06 | 366.6568 | 321.5303
911.1292 | 380.6798 | 312.4273 | 366.2148 | 320.4029
912.1448 | 380.1226 | 314.1784 | 365.8715 | 322.2462
913.1292 | 380.9395 | 313.9244 | 365.2892 | 321.7298
914.1292 | 382.1689 | 313.5194 | 364.0499 | 320.1659
915.1292 | 382.9499 | 312.2856 | 362.6281 | 318.5833
916.1292 | 382.7942 | 312.3098 | 361.3714 | 317.7187
917.1292 | 383.4526 | 311.9386 | 361.4447 | 316.6564
918.1292 | 384.8675 | 311.68 | 362.6165 | 315.2859
919.1292 | 386.2497 | 311.4519 | 363.6585 | 315.4126
920.1292 | 387.4008 | 311.613 | 365.2777 | 315.7918
921.1292 | 387.297 | 312.3769 | 365.0441 | 316.7538
922.1292 | 388.5359 | 314.6937 | 366.39 | 319.4641
923.1292 | 389.0176 | 314.2598 | 366.7224 | 319.0915
924.1292 | 389.1736 | 314.0911 | 367.8742 | 318.3953
925.1292 | 388.2084 | 312.8909 | 366.9339 | 317.4545
926.1292 | 387.7642 | 312.2856 | 368.4495 | 319.1233
927.1292 | 387.6397 | 311.9384 | 369.4829 | 319.0106
928.1292 | 387.7506 | 311.6242 | 368.6675 | 319.7405
929.1292 | 388.7276 | 311.8764 | 369.5959 | 321.0321
930.1292 | 390.1265 | 313.5234 | 368.7463 | 321.7478
931.1292 | 390.0792 | 313.3867 | 370.0827 | 321.2026
932.1292 | 389.1894 | 313.7337 | 369.4377 | 321.3758
933.1292 | 388.4217 | 313.9979 | 368.1794 | 321.173
934.1292 | 388.0986 | 314.0809 | 368.591 | 322.9615
935.1292 | 388.9511 | 313.7848 | 367.0614 | 321.7582
936.1292 | 389.5574 | 314.3536 | 366.087 | 320.7139
937.1292 | 390.6353 | 314.5508 | 364.3444 | 318.6905
938.1292 | 390.8871 | 315.1265 | 362.4877 | 317.001
939.1292 | 390.1243 | 313.9205 | 361.3237 | 315.1663
940.1292 | 389.3209 | 312.7821 | 361.197 | 313.9486
941.1292 | 388.5963 | 312.8142 | 360.9913 | 312.5699
942.1292 | 387.918 | 312.3759 | 361.1441 | 311.2156
943.1292 | 388.7221 | 313.1137 | 361.7818 | 309.9221
944.1292 | 388.8696 | 312.9067 | 360.688 | 308.8611
945.1292 | 389.3291 | 313.8033 | 361.1777 | 308.2851
946.1292 | 388.7049 | 312.5526 | 360.0524 | 308.1056
947.1292 | 386.2501 | 311.5358 | 359.3014 | 308.1417
948.1292 | 385.8798 | 309.7545 | 357.9581 | 307.5417
949.1292 | 385.1964 | 307.877 | 356.3053 | 307.5006
950.1292 | 384.3655 | 306.6807 | 355.8559 | 306.8868
951.1292 | 382.2278 | 306.6637 | 355.1537 | 307.4744
952.1292 | 382.3547 | 305.765 | 354.7157 | 308.0813
953.1292 | 381.9785 | 305.4532 | 355.3887 | 307.3108
954.1292 | 382.187 | 305.4666 | 357.0904 | 308.8004
955.1292 | 382.6856 | 305.954 | 357.4832 | 309.1417
956.1292 | 383.2973 | 307.2051 | 359.2657 | 309.3187
957.1292 | 383.7669 | 308.9523 | 359.4621 | 309.3022
958.1292 | 384.6152 | 310.0285 | 360.0151 | 310.229
959.1292 | 385.3285 | 311.4752 | 360.8543 | 311.2002
960.1292 | 385.8143 | 311.1205 | 361.2953 | 310.78
961.1292 | 386.2246 | 311.0893 | 362.6009 | 311.4365
962.1292 | 386.3208 | 311.7216 | 364.2013 | 310.926
963.1292 | 386.6843 | 311.9828 | 363.359 | 310.4013
964.1292 | 386.5952 | 312.5092 | 362.8763 | 309.7051
965.1292 | 386.9553 | 312.7104 | 363.6994 | 309.452
966.1292 | 387.1749 | 312.4924 | 363.9573 | 311.2771
967.1292 | 387.1288 | 312.5555 | 365.6915 | 310.8625
968.1292 | 387.6407 | 313.8793 | 367.3281 | 310.8163
969.1292 | 388.6952 | 315.0856 | 368.5881 | 311.1023
970.1292 | 388.8905 | 314.9909 | 370.0532 | 311.0676
971.1292 | 388.9644 | 314.6649 | 369.5439 | 310.6139
972.1292 | 389.5491 | 315.0131 | 371.4297 | 310.3369
973.1292 | 390.4779 | 316.1378 | 373.3244 | 310.5845
974.1292 | 390.8167 | 315.7207 | 373.0501 | 310.9318
975.1292 | 390.7061 | 315.9473 | 372.5151 | 309.8101
976.1292 | 390.9052 | 315.7033 | 372.3032 | 309.9528
977.1292 | 391.4062 | 316.508 | 373.235 | 310.0772
978.1292 | 392.8738 | 317.1829 | 375.1833 | 310.3121
979.1292 | 392.7384 | 317.388 | 374.3892 | 312.3001
980.1292 | 392.3875 | 316.0822 | 371.829 | 311.8059
981.1292 | 392.6903 | 314.6976 | 370.9827 | 310.8548
982.1292 | 392.7135 | 314.7257 | 371.9494 | 309.6323
983.1292 | 394.2577 | 314.6068 | 371.7575 | 308.8561
984.1292 | 393.7949 | 313.8104 | 371.7353 | 308.4099
985.1292 | 394.1431 | 314.6589 | 372.1531 | 309.1982
986.1292 | 394.4103 | 315.283 | 372.8725 | 310.9377
987.1292 | 394.911 | 315.6992 | 373.4512 | 311.7231
988.1292 | 395.5292 | 316.5612 | 374.3594 | 312.4226
989.1292 | 395.5743 | 316.7577 | 376.8724 | 314.9358
990.1292 | 395.6076 | 316.1312 | 376.8498 | 315.6718
991.1292 | 395.7464 | 316.7602 | 378.0298 | 316.8711
992.1292 | 396.0812 | 318.6286 | 378.281 | 318.8982
993.1292 | 395.6672 | 318.0174 | 377.2447 | 318.0842
994.1292 | 395.9375 | 317.8016 | 377.8211 | 318.6147
995.1292 | 396.8844 | 320.6172 | 378.159 | 318.8004
996.1292 | 397.361 | 322.6175 | 377.6882 | 318.2995
997.1292 | 398.5004 | 323.6621 | 379.4635 | 319.0796
998.1292 | 398.2279 | 323.664 | 379.6846 | 318.489
999.1292 | 398.1877 | 324.8186 | 380.1272 | 317.9771
1000.1292 | 398.6979 | 325.4785 | 379.884 | 317.9224
1001.1292 | 399.123 | 325.7957 | 380.4569 | 317.9827
1002.1292 | 400.2967 | 326.5108 | 379.7817 | 316.8554
1003.1292 | 401.1839 | 328.1466 | 379.2555 | 315.4623
1004.1292 | 402.8585 | 330.1026 | 379.6908 | 314.547
1005.1292 | 403.7738 | 331.3193 | 380.851 | 314.2878
1006.1292 | 404.3481 | 332.092 | 382.2572 | 316.811
1007.1292 | 404.7616 | 332.0257 | 385.0423 | 319.6743
1008.1292 | 406.1117 | 333.0639 | 386.6264 | 320.2369
1009.1292 | 405.7452 | 334.5311 | 387.0827 | 321.3412
1010.1292 | 406.3266 | 335.4312 | 387.1252 | 321.5827
1011.1292 | 406.5797 | 336.2078 | 388.8833 | 322.3246
1012.1292 | 407.8284 | 337.1437 | 389.3453 | 322.1674
1013.1292 | 408.8512 | 337.6328 | 391.549 | 322.8299
1014.1292 | 408.8521 | 338.803 | 392.3232 | 324.3409
1015.1292 | 409.4012 | 338.5461 | 393.1874 | 325.1142
1016.1292 | 409.6625 | 340.2776 | 395.4708 | 328.7372
1017.1292 | 410.7876 | 340.4647 | 398.3747 | 330.7174
1018.1292 | 411.1606 | 341.0147 | 399.1102 | 332.1784
1019.1292 | 412.426 | 341.4312 | 400.8598 | 332.8544
1020.1292 | 412.9583 | 341.3922 | 402.03 | 335.75
1021.1292 | 412.5264 | 341.1921 | 400.4389 | 338.1441
1022.1292 | 411.2295 | 338.8387 | 398.9268 | 340.7593
1023.1292 | 410.0121 | 337.0338 | 398.1054 | 343.0142
1024.1292 | 410.7246 | 336.266 | 397.8859 | 344.6928
1025.1292 | 411.0947 | 335.8608 | 399.1332 | 344.1735
1026.1292 | 410.438 | 335.1465 | 398.5474 | 343.172
1027.1292 | 410.2025 | 335.4228 | 397.6375 | 344.0162
1028.1292 | 410.2803 | 334.7611 | 397.0826 | 344.6288
1029.1292 | 410.383 | 333.5382 | 396.2139 | 344.7351
1030.1292 | 411.1523 | 333.7146 | 396.6642 | 343.2773
1031.1292 | 412.6997 | 334.8272 | 397.3119 | 342.5115
1032.1292 | 413.8715 | 336.7389 | 398.5877 | 341.8429
1033.1292 | 414.7059 | 336.9922 | 398.6516 | 342.7614
1034.1292 | 414.2984 | 336.5958 | 398.1709 | 343.3422
1035.1292 | 414.6125 | 335.9244 | 397.7766 | 343.2649
1036.1292 | 415.6456 | 335.9395 | 399.365 | 342.9929
1037.1292 | 417.1494 | 338.1214 | 399.8085 | 341.9853
1038.1292 | 419.2832 | 340.0393 | 399.4803 | 341.1847
1039.1292 | 420.7787 | 341.4583 | 401.0949 | 340.6789
1040.1292 | 422.0848 | 341.3842 | 400.6001 | 341.349
1041.1292 | 422.877 | 341.6325 | 401.6389 | 341.9515
1042.1292 | 423.3217 | 342.5668 | 402.0102 | 342.0013
1043.1292 | 423.5601 | 343.5092 | 404.1741 | 341.6092
1044.1292 | 424.543 | 344.064 | 404.4648 | 340.7284
1045.1292 | 424.6681 | 344.074 | 403.8815 | 339.2396
1046.1292 | 425.3653 | 346.003 | 403.7632 | 339.6032
1047.1292 | 425.3312 | 349.3317 | 403.4433 | 341.0232
1048.1292 | 425.3427 | 350.8129 | 404.2552 | 340.7785
1049.1292 | 425.1138 | 351.5332 | 404.8295 | 341.2752
1050.1292 | 424.5571 | 353.1978 | 405.4152 | 341.583
1051.1292 | 424.3737 | 352.1961 | 405.59 | 342.389
1052.1292 | 424.3998 | 352.0014 | 406.0279 | 342.9098
1053.1292 | 425.0904 | 353.1461 | 406.6579 | 344.3223
1054.1292 | 424.9951 | 352.7823 | 407.3561 | 346.0253
1055.1292 | 425.3079 | 351.5435 | 409.0627 | 346.4969
1056.1292 | 424.2955 | 351.6428 | 409.972 | 347.4971
1057.1292 | 424.4347 | 350.9183 | 409.877 | 348.4075
1058.1292 | 423.9759 | 351.8948 | 410.6934 | 350.4075
1059.1292 | 423.5414 | 351.8717 | 410.4749 | 348.9431
1060.1292 | 423.0754 | 352.2118 | 408.7236 | 347.4997
1061.1292 | 423.9757 | 351.9875 | 407.7229 | 345.9639
1062.1292 | 424.3858 | 352.6709 | 406.9089 | 344.4771
1063.1292 | 425.4533 | 352.2943 | 405.3444 | 342.8851
1064.1292 | 426.5589 | 352.708 | 403.9209 | 342.4437
1065.1292 | 427.6974 | 352.9747 | 404.7719 | 341.8402
1066.1292 | 427.6847 | 351.6162 | 403.8136 | 340.7291
1067.1292 | 428.303 | 351.9391 | 406.7597 | 340.2095
1068.1292 | 428.6487 | 352.1397 | 407.1829 | 340.3075
1069.1292 | 429.635 | 352.9084 | 407.8948 | 341.0005
1070.1292 | 430.1799 | 352.8523 | 408.8483 | 340.8283
1071.1292 | 429.4902 | 353.0431 | 410.4532 | 343.4449
1072.1292 | 430.9604 | 353.6255 | 409.638 | 344.2372
1073.1292 | 431.6536 | 353.6173 | 408.9354 | 344.0509
1074.1292 | 432.2057 | 352.5563 | 408.8784 | 344.6191
1075.1292 | 431.4654 | 351.9532 | 408.7192 | 343.8146
1076.1292 | 431.4538 | 350.6402 | 409.0308 | 343.8159
1077.1292 | 431.8742 | 350.7095 | 409.6965 | 343.0516
1078.1292 | 432.7719 | 351.4359 | 409.6921 | 343.7886
1079.1292 | 434.1823 | 351.4048 | 411.3107 | 344.5322
1080.1292 | 435.8052 | 351.3599 | 411.5228 | 343.4049
1081.1292 | 436.3297 | 351.0657 | 410.8784 | 343.3388
1082.1292 | 436.8729 | 352.1577 | 411.6545 | 342.6001
1083.1292 | 437.1138 | 353.1743 | 412.0979 | 342.8792
1084.1292 | 436.6837 | 354.2164 | 413.1248 | 341.7494
1085.1292 | 436.8852 | 353.2065 | 412.4999 | 341.8993
1086.1292 | 437.6636 | 352.9387 | 414.3928 | 342.9569
1087.1292 | 437.3742 | 354.1484 | 417.3988 | 345.423
1088.1292 | 436.1933 | 353.5914 | 419.0615 | 346.6595
1089.1292 | 435.4423 | 352.2616 | 418.6311 | 348.5961
1090.1292 | 436.3595 | 350.6988 | 417.6918 | 348.3588
1091.1292 | 436.897 | 351.326 | 418.5335 | 347.8697
1092.1292 | 437.8372 | 352.9643 | 418.0275 | 347.5896
1093.1292 | 437.9682 | 352.1747 | 417.3966 | 347.4043
1094.1292 | 437.948 | 352.7408 | 418.8798 | 347.0413
1095.1292 | 438.5083 | 352.3431 | 420.0487 | 347.0106
1096.1292 | 439.3185 | 353.0148 | 421.3108 | 346.7439
1097.1292 | 439.0264 | 353.6509 | 421.6705 | 347.2882
1098.1292 | 438.4871 | 353.7016 | 423.8305 | 349.8781
1099.1292 | 439.5289 | 353.4665 | 428.4486 | 351.925
1100.1292 | 439.7665 | 352.7603 | 429.6826 | 352.9499
1101.1292 | 441.0002 | 352.909 | 429.6466 | 352.9535
1102.1292 | 442.1626 | 353.1456 | 429.44 | 352.6212
1103.1292 | 443.3179 | 354.1821 | 430.5486 | 352.8289
1104.1292 | 444.4374 | 355.4002 | 429.2037 | 351.3048
1105.1292 | 446.2182 | 355.2807 | 428.0567 | 350.3726
1106.1448 | 447.0215 | 356.8793 | 428.246 | 350.3872
1107.1292 | 447.9844 | 357.0855 | 428.2691 | 352.0291
1108.1292 | 447.9982 | 356.6871 | 426.9574 | 352.1036
1109.1292 | 447.7941 | 355.9468 | 425.8867 | 351.7604
1110.1292 | 448.6686 | 356.2996 | 428.9293 | 351.8588
1111.1292 | 449.3197 | 357.0032 | 428.4028 | 352.377
1112.1292 | 449.3444 | 357.7766 | 429.5704 | 351.6225
1113.1292 | 450.0052 | 359.4941 | 427.6725 | 351.2304
1114.1292 | 449.5457 | 361.2214 | 428.8037 | 350.6248
1115.1292 | 449.8278 | 361.4638 | 427.4538 | 350.6888
1116.1292 | 450.1241 | 361.7571 | 426.5359 | 349.8956
1117.1292 | 450.2441 | 361.1922 | 424.0003 | 348.4344
1118.1292 | 450.1645 | 361.2935 | 423.5858 | 347.765
1119.1292 | 451.3749 | 362.4995 | 431.1911 | 348.1175
1120.1292 | 451.494 | 362.8395 | 434.4452 | 350.1486
1121.1292 | 452.8547 | 363.0209 | 437.1423 | 352.0965
1122.1292 | 454.385 | 363.0089 | 438.6138 | 352.2431
1123.1292 | 454.707 | 364.9464 | 439.4019 | 352.7922
1124.1292 | 454.2969 | 364.4044 | 437.3261 | 354.6192
1125.1292 | 453.6986 | 362.861 | 434.6728 | 352.9908
1126.1292 | 454.6551 | 361.6561 | 433.0143 | 352.2812
1127.1292 | 454.6729 | 360.5234 | 435.2233 | 352.0905
1128.1292 | 453.9246 | 360.5618 | 434.5418 | 351.2972
1129.1292 | 453.2418 | 360.9003 | 435.3498 | 351.7473
1130.1292 | 452.8775 | 360.3736 | 433.2214 | 352.3906
1131.1292 | 453.6003 | 359.2225 | 431.6454 | 354.1328
1132.1292 | 451.5825 | 357.136 | 428.4145 | 355.6912
1133.1292 | 450.0451 | 355.1506 | 424.7234 | 359.2966
1134.1292 | 449.8103 | 353.9264 | 422.6284 | 361.5257
1135.1292 | 448.9337 | 352.3818 | 420.6922 | 361.7681
1136.1448 | 449.1827 | 351.5414 | 422.5001 | 363.278
1137.1292 | 451.0191 | 352.901 | 426.2201 | 364.7349
1138.1292 | 452.0873 | 352.9595 | 424.9438 | 363.6628
1139.1292 | 453.1735 | 353.395 | 423.4937 | 362.6146
1140.1292 | 453.4804 | 354.4392 | 422.9866 | 362.2989
1141.1292 | 452.6417 | 355.0028 | 424.1995 | 362.1379
1142.1292 | 452.8445 | 354.3846 | 425.3651 | 363.5467
1143.1292 | 453.6147 | 353.5617 | 424.3909 | 363.4181
1144.1292 | 454.1935 | 354.722 | 426.2114 | 364.4243
1145.1292 | 454.0606 | 353.722 | 426.4437 | 364.5899
1146.1292 | 454.2624 | 352.7078 | 426.4774 | 364.6544
1147.1448 | 454.9226 | 352.8053 | 426.6168 | 364.6293
1148.1448 | 455.1392 | 351.4461 | 426.9849 | 363.6075
1149.1292 | 455.4731 | 351.2684 | 425.6114 | 361.9872
1150.1292 | 457.3699 | 352.0959 | 423.6384 | 360.2896
1151.1448 | 458.9629 | 355.9825 | 430.0104 | 360.4463
1152.1448 | 459.0775 | 356.1484 | 432.4143 | 361.0591
1153.1448 | 458.9062 | 355.2605 | 431.0816 | 363.9808
1154.1448 | 459.7581 | 354.6689 | 435.3723 | 366.39
1155.1292 | 458.7254 | 353.2609 | 431.6549 | 365.5506
1156.1292 | 458.6719 | 352.5109 | 431.5548 | 364.9639
1157.1292 | 457.4966 | 352.3283 | 431.1239 | 365.6982
1158.1292 | 456.971 | 351.7624 | 430.0126 | 365.1397
1159.1292 | 456.3485 | 351.2474 | 427.8879 | 363.3429
1160.1292 | 456.2564 | 351.378 | 428.1975 | 364.1025
1161.1292 | 455.3489 | 351.1038 | 426.7478 | 364.3808
1162.1292 | 454.6345 | 349.3551 | 424.9896 | 363.78
1163.1292 | 456.3996 | 348.8684 | 424.5358 | 366.3429
1164.1292 | 457.1743 | 349.7385 | 425.1301 | 367.3593
1165.1292 | 458.0372 | 349.845 | 427.0852 | 365.8343
1166.1448 | 459.6439 | 350.7246 | 432.8799 | 365.6267
1167.1448 | 460.0478 | 353.1056 | 434.7359 | 366.3098
1168.1292 | 461.1883 | 354.3637 | 436.7217 | 366.6734
1169.1292 | 461.8374 | 357.0396 | 437.8061 | 366.7638
1170.1292 | 461.3053 | 359.3313 | 437.4315 | 366.0921
1171.1292 | 461.837 | 361.223 | 436.78 | 366.7102
1172.1292 | 461.8315 | 361.3417 | 437.6437 | 365.8206
1173.1292 | 462.0007 | 362.0877 | 435.7878 | 364.2663
1174.1292 | 462.931 | 363.2232 | 436.8877 | 363.6361
1175.1292 | 462.8403 | 364.617 | 435.8692 | 363.6177
1176.1292 | 461.403 | 363.311 | 434.0771 | 364.6727
1177.1292 | 460.741 | 361.7343 | 435.1761 | 365.8082
1178.1292 | 461.4145 | 361.7895 | 439.2191 | 368.2462
1179.1292 | 460.915 | 360.3083 | 437.1257 | 368.5256
1180.1292 | 461.4181 | 359.5148 | 435.5079 | 367.7956
1181.1292 | 462.2231 | 360.2855 | 435.247 | 366.2702
1182.1292 | 462.3149 | 360.6761 | 432.811 | 363.8515
1183.1292 | 463.1855 | 360.1597 | 432.9174 | 361.688
1184.1292 | 463.3508 | 362.045 | 432.1836 | 362.2428
1185.1292 | 463.396 | 362.8004 | 432.4386 | 361.8824
1186.1292 | 463.4945 | 362.3159 | 429.9149 | 360.9409
1187.1292 | 463.3993 | 361.4207 | 429.6657 | 360.2029
1188.1292 | 464.1976 | 361.4271 | 428.2776 | 359.3065
1189.1292 | 464.2342 | 361.716 | 428.6277 | 357.8129
1190.1292 | 465.3703 | 361.7375 | 428.6384 | 356.4513
1191.1292 | 465.9047 | 364.32 | 431.646 | 355.1372
1192.1292 | 465.5 | 364.5731 | 435.6779 | 356.3032
1193.1292 | 466.2409 | 363.8511 | 436.0451 | 355.7346
1194.1292 | 466.9808 | 363.8964 | 436.1934 | 356.026
1195.1292 | 466.853 | 364.1207 | 436.9531 | 356.4492
1196.1292 | 467.3917 | 363.4189 | 437.3909 | 356.5467
1197.1292 | 468.2366 | 365.6766 | 437.6164 | 356.095
1198.1292 | 470.6291 | 368.7426 | 441.2322 | 354.8877
1199.1292 | 472.6313 | 371.7749 | 441.7221 | 356.908
1200.1292 | 472.4723 | 373.1694 | 440.6269 | 356.5049
1201.1292 | 472.8774 | 373.4313 | 440.9111 | 356.3787
1202.1292 | 473.5408 | 373.4916 | 440.0772 | 355.2243
1203.1292 | 474.0092 | 374.058 | 438.7395 | 353.6806
1204.1292 | 475.4697 | 377.2953 | 440.8096 | 353.7172
1205.1292 | 476.6359 | 382.9429 | 444.8462 | 354.0561
1206.1292 | 476.8997 | 382.6628 | 442.7039 | 353.8933
1207.1292 | 476.9943 | 382.9291 | 444.5984 | 354.5552
1208.1292 | 478.1618 | 383.427 | 443.4398 | 355.2101
1209.1292 | 478.9661 | 383.807 | 442.1314 | 357.0562
1210.1292 | 478.6823 | 383.297 | 441.8487 | 357.6211
1211.1292 | 479.2756 | 384.9702 | 445.9674 | 360.7785
1212.1292 | 480.6541 | 383.3884 | 447.7543 | 362.3745
1213.1292 | 481.425 | 382.5631 | 450.5767 | 363.4733
1214.1292 | 481.5426 | 383.1748 | 451.3056 | 362.9655
1215.1292 | 480.5095 | 383.8562 | 450.4427 | 364.0079
1216.1292 | 479.3199 | 382.4646 | 449.3815 | 362.774
1217.1292 | 478.3723 | 382.0549 | 448.9462 | 364.7981
1218.1292 | 478.5993 | 382.026 | 448.2176 | 365.8405
1219.1292 | 477.664 | 381.2454 | 446.5573 | 367.2283
1220.1292 | 477.3562 | 378.9729 | 444.2987 | 366.792
1221.1292 | 478.8794 | 379.8622 | 452.1615 | 369.2693
1222.1292 | 480.565 | 379.3559 | 457.5694 | 370.33
1223.1292 | 481.914 | 378.2365 | 459.0294 | 370.3494
1224.1292 | 482.0835 | 377.4977 | 458.6979 | 372.874
1225.1292 | 483.1055 | 374.6919 | 457.5452 | 372.889
1226.1292 | 484.2186 | 373.404 | 458.9036 | 373.5138
1227.1292 | 484.0776 | 373.0397 | 460.8564 | 372.9936
1228.1292 | 485.5275 | 373.0951 | 462.6995 | 373.0601
1229.1292 | 486.302 | 375.2014 | 469.9808 | 374.2336
1230.1292 | 487.2914 | 376.3998 | 472.9565 | 375.1293
1231.1292 | 488.0797 | 376.2385 | 470.9058 | 376.8374
1232.1292 | 488.4811 | 375.9911 | 470.0676 | 376.1425
1233.1292 | 489.1278 | 377.4952 | 471.7979 | 377.5517
1234.1292 | 489.53 | 377.2903 | 471.8175 | 377.0024
1235.1292 | 489.1764 | 376.8787 | 470.0482 | 376.9957
1236.1292 | 488.6882 | 376.6532 | 467.0339 | 375.2479
1237.1292 | 488.4558 | 378.7271 | 469.7746 | 376.945
1238.1292 | 488.0306 | 377.4955 | 466.6333 | 376.0623
1239.1292 | 488.2147 | 375.8503 | 466.0784 | 376.039
1240.1292 | 487.4532 | 374.2753 | 462.5627 | 376.8795
1241.1292 | 488.8445 | 373.1712 | 462.9407 | 376.9069
1242.1292 | 489.83 | 374.4332 | 464.5967 | 376.2724
1243.1292 | 490.9093 | 375.2966 | 465.8383 | 375.1367
1244.1292 | 490.8863 | 376.5706 | 469.8982 | 376.6605
1245.1292 | 491.2724 | 376.9272 | 472.7185 | 378.6541
1246.1292 | 491.9895 | 378.1221 | 471.3666 | 379.5293
1247.1292 | 492.6433 | 377.385 | 468.4987 | 377.6602
1248.1292 | 494.5552 | 379.2495 | 474.332 | 377.232
1249.1292 | 494.5367 | 381.4405 | 472.7559 | 378.4106
1250.1448 | 494.4638 | 381.2898 | 470.8316 | 377.2049
1251.1292 | 493.6015 | 381.7402 | 468.1247 | 375.9292
1252.1292 | 492.9383 | 380.2846 | 465.5553 | 375.7927
1253.1292 | 493.0152 | 379.3253 | 464.12 | 374.5873
1254.1292 | 493.614 | 378.9786 | 470.1145 | 375.3724
1255.1292 | 495.6449 | 378.6686 | 472.784 | 375.6277
1256.1292 | 496.5664 | 384.8887 | 475.0978 | 375.8212
1257.1292 | 497.3956 | 386.9516 | 474.0217 | 376.0208
1258.1292 | 498.4387 | 387.3631 | 472.4419 | 375.3195
1259.1292 | 497.959 | 387.1129 | 472.0253 | 375.1037
1260.1292 | 498.6316 | 386.7218 | 471.2967 | 375.2077
1261.1292 | 499.4731 | 385.9165 | 470.5983 | 374.9981
1262.1292 | 500.2148 | 386.4983 | 471.046 | 374.914
1263.1292 | 500.8486 | 385.5285 | 468.3406 | 373.3338
1264.1292 | 501.1393 | 385.9005 | 465.9083 | 372.3158
1265.1292 | 501.11 | 385.1947 | 466.0178 | 371.089
1266.1292 | 501.842 | 384.789 | 466.8777 | 369.9073
1267.1292 | 503.7861 | 386.7435 | 478.6761 | 372.288
1268.1292 | 505.6494 | 390.8309 | 488.8118 | 371.8879
1269.1292 | 506.0324 | 392.9724 | 490.3591 | 371.3515
1270.1292 | 505.8623 | 392.3199 | 486.9139 | 370.5642
1271.1292 | 506.5168 | 393.4532 | 483.8077 | 368.3371
1272.1292 | 507.7521 | 396.6299 | 479.6347 | 367.0069
1273.1292 | 508.2033 | 402.3628 | 479.6767 | 366.2578
1274.1292 | 508.8598 | 407.2586 | 484.2459 | 366.4571
1275.1292 | 509.7147 | 411.9793 | 490.6992 | 367.4718
1276.1292 | 510.9176 | 415.5155 | 495.1983 | 367.3325
1277.1292 | 509.8196 | 416.1065 | 495.9002 | 367.6925
1278.1292 | 510.2829 | 414.6246 | 491.6062 | 366.488
1279.1292 | 509.8521 | 413.3832 | 488.3452 | 365.3096
1280.1292 | 509.2191 | 413.2708 | 484.6296 | 364.3397
1281.1292 | 509.3728 | 413.4219 | 482.3725 | 364.6951
1282.1292 | 510.6997 | 422.8863 | 490.3598 | 364.6998
1283.1292 | 509.82 | 423.1318 | 486.4311 | 365.832
1284.1292 | 509.0499 | 421.391 | 482.3948 | 366.3001
1285.1292 | 509.0908 | 420.1876 | 480.1626 | 366.5903
1286.1292 | 510.5067 | 422.8974 | 489.9725 | 369.8931
1287.1292 | 512.6866 | 422.7775 | 491.3148 | 372.0792
1288.1292 | 512.5506 | 421.658 | 490.197 | 373.228
1289.1292 | 513.9526 | 421.1137 | 488.2767 | 373.7324
1290.1292 | 514.1568 | 422.5229 | 491.4025 | 374.3817
1291.1292 | 514.3526 | 420.9859 | 492.8007 | 376.8217
1292.1292 | 514.2066 | 419.9456 | 494.8519 | 380.324
1293.1292 | 513.9375 | 418.6378 | 495.6431 | 381.9072
1294.1292 | 513.9753 | 417.1206 | 495.0942 | 383.1037
1295.1292 | 514.5949 | 416.1939 | 498.2148 | 383.2465
1296.1292 | 513.7113 | 415.6541 | 494.9675 | 381.6596
1297.1292 | 511.7755 | 412.7417 | 490.9418 | 382.2021
1298.1292 | 510.7414 | 409.2861 | 486.3415 | 382.0151
1299.1292 | 509.6074 | 406.2523 | 482.6961 | 380.7971
1300.1292 | 508.8034 | 403.4618 | 479.6148 | 381.333
1301.1292 | 507.903 | 400.4426 | 475.4743 | 380.7819
1302.1292 | 506.3181 | 397.1991 | 471.3047 | 380.2979
1303.1292 | 506.6654 | 394.523 | 467.8688 | 381.9473
1304.1292 | 508.4684 | 392.8344 | 468.369 | 386.5276
1305.1292 | 511.7799 | 393.7177 | 477.241 | 391.8861
1306.1292 | 511.5093 | 396.0561 | 480.1118 | 392.1401
1307.1292 | 512.1815 | 399.8116 | 482.6277 | 390.1328
1308.1292 | 512.4269 | 403.8555 | 485.6421 | 391.807
1309.1292 | 512.3809 | 403.927 | 489.7025 | 391.7931
1310.1292 | 511.9109 | 404.4949 | 490.7879 | 392.5691
1311.1292 | 512.0442 | 404.795 | 490.6307 | 392.1446
1312.1292 | 511.4445 | 406.4394 | 493.2572 | 393.272
1313.1292 | 512.0511 | 405.5278 | 492.768 | 392.5169
1314.1292 | 512.4532 | 406.0737 | 495.3084 | 392.9307
1315.1292 | 511.9767 | 405.3399 | 492.3236 | 390.8858
1316.1292 | 512.5495 | 407.338 | 491.8423 | 390.1987
1317.1292 | 512.6304 | 407.4199 | 489.1024 | 388.9967
1318.1292 | 513.6972 | 407.9296 | 488.8183 | 388.7412
1319.1292 | 513.7543 | 409.6195 | 484.9975 | 386.4193
1320.1292 | 513.9446 | 415.4686 | 481.6596 | 384.6977
1321.1292 | 513.5444 | 416.534 | 482.0158 | 383.5472
1322.1292 | 512.8412 | 415.8762 | 478.8147 | 382.8713
1323.1292 | 513.2922 | 414.7139 | 475.4723 | 382.0817
1324.1292 | 513.3989 | 415.1406 | 474.3897 | 380.1513
1325.1292 | 512.5172 | 415.3784 | 472.9639 | 379.6889
1326.1292 | 512.9456 | 414.3724 | 470.1691 | 379.5331
1327.1292 | 513.0468 | 414.5542 | 468.5691 | 378.2834
1328.1292 | 512.9363 | 412.8136 | 466.6699 | 378.0065
1329.1292 | 512.422 | 411.7484 | 462.9215 | 377.3882
1330.1292 | 511.4378 | 409.7307 | 462.3025 | 378.4541
1331.1292 | 511.0022 | 408.827 | 461.0062 | 379.0548
1332.1292 | 509.6332 | 407.9754 | 460.1929 | 379.3709
1333.1292 | 510.3839 | 407.4714 | 463.9437 | 379.0491
1334.1292 | 510.9894 | 408.508 | 465.867 | 378.3414
1335.1292 | 511.3622 | 409.1235 | 469.8469 | 378.6776
1336.1292 | 510.972 | 406.9985 | 469.3515 | 378.6231
1337.1292 | 510.2891 | 405.1997 | 468.8459 | 379.1829
1338.1292 | 509.4468 | 403.6769 | 468.7217 | 378.7195
1339.1292 | 508.4176 | 401.2611 | 466.2785 | 378.7459
1340.1292 | 509.5627 | 399.7974 | 463.1905 | 379.3155
1341.1292 | 509.6066 | 399.0745 | 463.2189 | 381.1082
1342.1292 | 510.0173 | 398.5147 | 464.5805 | 382.582
1343.1292 | 510.7181 | 397.684 | 464.0203 | 382.9666
1344.1292 | 511.8626 | 399.1008 | 468.4654 | 382.2407
1345.1292 | 511.5088 | 397.9655 | 468.4236 | 381.652
1346.1292 | 512.5369 | 398.3331 | 470.3094 | 381.6691
1347.1292 | 512.2899 | 399.038 | 472.8867 | 383.0238
1348.1292 | 512.0349 | 399.2875 | 471.5609 | 382.67
1349.1292 | 511.5346 | 399.0894 | 470.4077 | 381.2917
1350.1292 | 511.198 | 398.8574 | 469.0725 | 380.7391
1351.1292 | 511.2071 | 398.2005 | 467.8253 | 379.8468
1352.1292 | 511.0459 | 398.2697 | 468.7426 | 379.9071
1353.1292 | 511.0283 | 398.3753 | 468.5658 | 380.815
1354.1292 | 510.7747 | 397.883 | 467.639 | 381.7454
1355.1292 | 510.6503 | 397.97 | 467.2877 | 382.3033
1356.1292 | 511.0119 | 397.2124 | 465.1318 | 380.335
1357.1292 | 511.4083 | 396.4461 | 464.7615 | 381.2443
1358.1292 | 511.3218 | 396.5048 | 464.1214 | 382.5088
1359.1292 | 510.9018 | 396.0135 | 465.315 | 383.9212
1360.1292 | 511.8382 | 394.5776 | 468.9577 | 385.422
1361.1292 | 513.7079 | 394.4106 | 474.5997 | 389.1946
1362.1292 | 513.8068 | 395.0006 | 476.8063 | 391.5713
1363.1292 | 513.6204 | 393.9909 | 475.5733 | 389.8176
1364.1292 | 513.4466 | 394.5736 | 475.0434 | 390.4763
1365.1292 | 514.0239 | 395.097 | 475.8775 | 390.507
1366.1292 | 514.331 | 396.2586 | 478.0709 | 389.5428
1367.1292 | 513.4134 | 398.1327 | 477.1775 | 389.5955
1368.1292 | 512.466 | 397.805 | 476.4472 | 388.3945
1369.1292 | 511.6154 | 398.2847 | 475.4371 | 386.2515
1370.1292 | 512.7305 | 400.2274 | 477.0356 | 385.6038
1371.1292 | 512.9381 | 401.6068 | 476.9744 | 384.7984
1372.1292 | 512.9621 | 401.8786 | 475.6095 | 385.3625
1373.1292 | 512.3479 | 402.4588 | 473.1832 | 383.945
1374.1292 | 512.7739 | 403.5273 | 474.9007 | 384.7436
1375.1292 | 512.9409 | 404.1548 | 474.0212 | 385.5172
1376.1448 | 514.9231 | 405.5145 | 478.1139 | 387.7692
1377.1292 | 514.65 | 405.615 | 475.3778 | 387.4252
1378.1292 | 514.8083 | 404.8075 | 473.9609 | 386.7021
1379.1292 | 514.4712 | 404.1012 | 472.8844 | 386.17
1380.1292 | 513.9348 | 406.8986 | 472.4926 | 385.9319
1381.1292 | 513.809 | 408.5068 | 470.752 | 386.2078
1382.1292 | 512.976 | 408.11 | 467.6342 | 385.0339
1383.1292 | 512.8823 | 407.558 | 466.5945 | 383.8977
1384.1292 | 513.0987 | 406.5519 | 466.5421 | 384.1013
1385.1292 | 513.7876 | 407.5091 | 466.5373 | 384.5411
1386.1292 | 515.2005 | 408.2177 | 467.4059 | 385.0312
1387.1292 | 515.2845 | 408.4766 | 467.9909 | 385.8614
1388.1292 | 515.1162 | 406.974 | 468.659 | 386.4673
1389.1292 | 515.055 | 406.2856 | 467.319 | 386.4911
1390.1292 | 514.7846 | 404.237 | 466.2549 | 388.8526
1391.1448 | 515.3221 | 401.7922 | 465.668 | 390.8802
1392.1448 | 517.536 | 401.0798 | 471.3524 | 392.8671
1393.1292 | 517.0844 | 401.5806 | 475.7921 | 394.2083
1394.1292 | 516.6439 | 405.4101 | 477.8867 | 394.0785
1395.1448 | 516.09 | 407.3461 | 476.927 | 394.3752
1396.1448 | 516.0958 | 405.9525 | 476.7638 | 394.0633
1397.1448 | 515.9844 | 406.599 | 475.8726 | 393.6824
1398.1448 | 516.2977 | 405.0269 | 473.1883 | 393.6895
1399.1292 | 516.8839 | 406.0852 | 474.4464 | 393.8714
1400.1292 | 517.1639 | 405.547 | 475.2639 | 393.5501
1401.1292 | 517.3822 | 404.9824 | 474.4502 | 395.1723
1402.1292 | 517.8159 | 405.6704 | 476.417 | 394.7597
1403.1292 | 517.8171 | 405.782 | 475.3786 | 396.2781
1404.1292 | 517.4543 | 404.4065 | 473.0246 | 396.0111
1405.1292 | 517.2933 | 404.6146 | 472.4956 | 395.8378
1406.1292 | 517.5744 | 403.6555 | 470.9594 | 396.5149
1407.1292 | 517.0391 | 401.8538 | 468.4608 | 394.8801
1408.1292 | 516.5129 | 402.1915 | 467.2415 | 393.0581
1409.1292 | 516.4772 | 402.7964 | 466.1624 | 392.2009
1410.1292 | 518.0182 | 401.5834 | 463.5397 | 390.565
1411.1292 | 517.1208 | 401.1812 | 462.4341 | 389.4117
1412.1292 | 516.6714 | 402.9427 | 462.741 | 388.3803
1413.1292 | 516.535 | 402.8999 | 461.6958 | 388.813
1414.1292 | 517.2476 | 400.1988 | 459.0767 | 388.6662
1415.1292 | 517.262 | 398.2439 | 458.5478 | 388.1744
1416.1292 | 518.7739 | 396.9815 | 461.2709 | 386.9311
1417.1292 | 517.8146 | 399.6402 | 461.4578 | 386.2151
1418.1292 | 518.77 | 400.4738 | 459.6646 | 385.7069
1419.1292 | 518.3246 | 398.9644 | 457.82 | 384.66
1420.1292 | 519.4667 | 399.2813 | 459.8739 | 384.3811
1421.1292 | 520.2342 | 399.6739 | 460.5024 | 384.9548
1422.1292 | 521.1525 | 398.8971 | 461.1118 | 384.9215
1423.1292 | 521.4959 | 399.0869 | 463.3881 | 385.5152
1424.1292 | 522.4153 | 399.4772 | 464.642 | 386.6137
1425.1292 | 522.0007 | 398.1672 | 465.5044 | 386.9356
1426.1292 | 521.8862 | 397.4062 | 463.9943 | 386.2322
1427.1292 | 521.5416 | 396.2487 | 463.1488 | 385.5037
1428.1292 | 522.2978 | 396.7215 | 463.0694 | 386.4664
1429.1292 | 522.4603 | 398.5962 | 461.8394 | 385.1163
1430.1292 | 522.2875 | 399.2173 | 460.1898 | 384.3363
1431.1292 | 522.2106 | 400.2841 | 458.758 | 384.5943
1432.1292 | 522.9594 | 401.0233 | 458.0263 | 384.9676
1433.1292 | 524.4099 | 401.6036 | 456.7122 | 384.6156
1434.1292 | 524.58 | 401.8781 | 457.1845 | 385.7445
1435.1292 | 524.8606 | 401.6752 | 459.3035 | 385.5901
1436.1292 | 525.4383 | 400.6547 | 458.1931 | 385.4746
1437.1292 | 525.6448 | 400.606 | 458.9386 | 386.1718
1438.1292 | 525.0403 | 399.413 | 458.1888 | 385.5955
1439.1292 | 525.3657 | 399.5343 | 458.1832 | 385.2076
1440.1292 | 526.1786 | 399.5347 | 460.6801 | 386.122
1441.1292 | 525.9767 | 397.4373 | 459.9051 | 386.6611
1442.1292 | 525.5872 | 396.3412 | 457.6429 | 387.3902
1443.1292 | 525.8297 | 395.1266 | 457.5185 | 387.7882
1444.1292 | 526.0154 | 393.6038 | 457.2926 | 387.3094
1445.1292 | 526.841 | 393.6806 | 459.7805 | 388.355
1446.1292 | 526.9698 | 394.1326 | 460.2983 | 387.7722
1447.1292 | 526.7687 | 395.7447 | 460.494 | 387.9152
1448.1292 | 526.9059 | 396.7403 | 461.7577 | 388.8647
1449.1292 | 526.7711 | 398.4124 | 461.7128 | 389.0147
1450.1292 | 528.0807 | 399.6881 | 460.6529 | 387.6776
1451.1292 | 528.4834 | 399.6727 | 458.8512 | 386.5146
1452.1292 | 528.3816 | 398.064 | 456.3859 | 386.5293
1453.1292 | 528.5117 | 397.5219 | 455.2329 | 385.2955
1454.1292 | 530.6341 | 397.1015 | 454.7486 | 384.9238
1455.1292 | 530.5622 | 396.5458 | 455.3168 | 384.3696
1456.1292 | 530.3612 | 396.3766 | 454.399 | 383.4982
1457.1292 | 529.9117 | 397.1552 | 452.9157 | 381.8321
1458.1292 | 529.7069 | 397.6992 | 450.357 | 379.9032
1459.1292 | 531.8226 | 397.9579 | 447.8102 | 378.7849
1460.1292 | 531.8969 | 398.3766 | 448.7057 | 378.9761
1461.1292 | 531.954 | 398.3482 | 450.274 | 378.7618
1462.1292 | 531.4958 | 397.8406 | 449.0197 | 378.093
1463.1292 | 530.527 | 396.7213 | 448.8466 | 377.0607
1464.1292 | 530.0223 | 397.844 | 448.5008 | 376.6379
1465.1292 | 530.2147 | 397.9373 | 448.684 | 376.7464
1466.1448 | 530.6521 | 396.8045 | 449.113 | 377.2651
1467.1292 | 530.7571 | 396.3933 | 450.3579 | 378.5444
1468.1292 | 531.5282 | 395.9279 | 451.5324 | 379.613
1469.1292 | 531.5835 | 395.219 | 451.3146 | 379.817
1470.1292 | 530.8847 | 395.164 | 448.9985 | 378.7668
1471.1292 | 530.6772 | 395.4785 | 447.9585 | 377.8947
1472.1292 | 530.8017 | 395.8904 | 448.2163 | 378.942
1473.1292 | 530.5551 | 394.4694 | 446.2236 | 378.111
1474.1292 | 531.8842 | 395.1065 | 447.6665 | 378.349
1475.1292 | 531.3537 | 394.8158 | 448.6348 | 379.0893
1476.1292 | 531.0554 | 394.1065 | 447.6291 | 380.2688
1477.1292 | 532.4464 | 392.2066 | 446.721 | 379.6418
1478.1292 | 532.546 | 392.313 | 449.1588 | 380.9073
1479.1292 | 531.8069 | 392.0659 | 451.0423 | 380.8106
1480.1292 | 531.7743 | 391.4956 | 452.1197 | 381.9245
1481.1292 | 533.1481 | 392.3703 | 454.5441 | 383.2035
1482.1292 | 533.3806 | 391.5843 | 453.8115 | 383.8965
1483.1292 | 533.9551 | 391.9844 | 454.0425 | 383.9405
1484.1292 | 532.7176 | 393.8166 | 454.6655 | 384.2896
1485.1292 | 533.561 | 393.8563 | 454.4335 | 385.9455
1486.1292 | 535.3515 | 392.8481 | 454.3051 | 387.5742
1487.1292 | 540.4344 | 392.4086 | 455.9759 | 389.619
1488.1292 | 541.0413 | 394.2595 | 458.3632 | 390.0791
1489.1292 | 542.9431 | 395.0191 | 460.7776 | 392.3482
1490.1292 | 542.1672 | 395.1347 | 462.1048 | 394.4625
1491.1292 | 541.1567 | 396.0753 | 462.8435 | 393.3199
1492.1292 | 541.1095 | 396.5171 | 463.6471 | 393.1147
1493.1292 | 540.0841 | 397.0454 | 463.9394 | 392.4135
1494.1292 | 540.1111 | 397.8462 | 463.8767 | 392.7656
1495.1292 | 539.9229 | 398.1289 | 462.9111 | 393.3702
1496.1292 | 540.5007 | 396.3403 | 463.5566 | 393.4599
1497.1292 | 540.7769 | 395.8876 | 463.205 | 394.0956
1498.1292 | 542.2997 | 396.4426 | 461.8754 | 395.6476
1499.1292 | 543.5667 | 395.7005 | 460.2122 | 397.5543
1500.1292 | 544.1923 | 394.0144 | 458.8657 | 397.6676
1501.1292 | 545.7214 | 393.0782 | 458.6725 | 397.3877
1502.1292 | 545.9931 | 392.251 | 458.0193 | 397.2689
1503.1292 | 544.9493 | 393.2882 | 459.6073 | 397.0432
1504.1292 | 543.5917 | 393.4585 | 458.5735 | 397.2586
1505.1292 | 543.0725 | 393.7025 | 459.0394 | 397.3188
1506.1292 | 543.6385 | 393.079 | 460.615 | 397.3464
1507.1292 | 543.6953 | 393.7975 | 461.8968 | 398.0068
1508.1292 | 542.7163 | 394.0417 | 460.6971 | 396.8508
1509.1292 | 542.4268 | 395.1749 | 461.6815 | 397.3635
1510.1292 | 544.5641 | 394.0812 | 462.2908 | 397.2769
1511.1292 | 545.4003 | 394.1972 | 463.0502 | 398.3034
1512.1292 | 543.5561 | 394.4247 | 461.7531 | 397.7722
1513.1292 | 543.8744 | 395.4073 | 462.453 | 396.9798
1514.1292 | 542.2032 | 394.6435 | 461.5994 | 396.463
1515.1292 | 541.8677 | 392.8577 | 459.0267 | 394.4419
1516.1292 | 540.3837 | 393.4764 | 460.2334 | 393.1724
1517.1292 | 540.5834 | 393.9566 | 461.0121 | 392.1189
1518.1292 | 542.5755 | 393.203 | 460.376 | 391.645
1519.1292 | 541.3079 | 393.4729 | 460.0858 | 393.0466
1520.1292 | 541.8564 | 393.3593 | 460.5811 | 391.8802
1521.1292 | 541.7129 | 393.061 | 460.3904 | 390.6988
1522.1292 | 541.2792 | 394.2845 | 460.2201 | 390.3858
1523.1292 | 541.7526 | 397.0388 | 461.3442 | 390.3727
1524.1292 | 540.1125 | 396.5949 | 460.1613 | 390.3172
1525.1292 | 540.4913 | 395.3822 | 459.6517 | 389.6282
1526.1292 | 541.9971 | 395.5712 | 460.5862 | 390.2497
1527.1292 | 541.831 | 394.176 | 460.5159 | 389.4444
1528.1292 | 540.2339 | 393.7595 | 460.6241 | 389.7125
1529.1292 | 539.9262 | 393.2089 | 460.0655 | 389.1493
1530.1292 | 539.3825 | 394.2017 | 460.166 | 389.0302
1531.1292 | 539.2136 | 395.222 | 460.1665 | 388.7858
1532.1292 | 539.1357 | 395.2035 | 459.5184 | 388.0323
1533.1292 | 539.7244 | 395.3225 | 459.1246 | 387.6153
1534.1292 | 539.3553 | 396.4214 | 459.2971 | 389.1485
1535.1292 | 538.8532 | 395.8383 | 459.5169 | 389.4126
1536.1292 | 540.3464 | 395.3336 | 460.4396 | 389.1559
1537.1292 | 540.3911 | 394.6169 | 459.8298 | 389.5615
1538.1292 | 540.3295 | 393.8616 | 456.9785 | 388.5997
1539.1292 | 541.0718 | 394.0838 | 456.4583 | 388.091
1540.1292 | 540.8271 | 393.1629 | 454.8707 | 386.5022
1541.1292 | 539.9786 | 393.4989 | 453.1126 | 385.6758
1542.1292 | 541.1345 | 392.3148 | 452.8783 | 386.5667
1543.1292 | 542.5673 | 391.4607 | 451.9818 | 387.1125
1544.1292 | 543.2285 | 390.3726 | 451.7197 | 385.6119
1545.1292 | 541.3361 | 390.9036 | 451.6728 | 385.9722
1546.1292 | 539.9334 | 390.6461 | 451.9259 | 386.2575
1547.1292 | 539.2251 | 390.0387 | 452.5656 | 386.7883
1548.1292 | 538.7368 | 390.2446 | 454.7513 | 388.3349
1549.1292 | 540.3446 | 390.8903 | 455.3841 | 390.4828
1550.1292 | 541.9483 | 390.1335 | 456.0201 | 393.0578
1551.1292 | 542.4869 | 390.3211 | 457.3693 | 395.6789
1552.1292 | 542.4333 | 390.4487 | 458.0289 | 395.5911
1553.1292 | 542.614 | 392.1433 | 459.0159 | 396.119
1554.1292 | 541.3023 | 392.4796 | 458.1064 | 396.4816
1555.1292 | 541.2304 | 392.2853 | 458.8416 | 395.7343
1556.1292 | 541.8993 | 392.8413 | 458.7612 | 394.9714
1557.1292 | 545.392 | 392.3216 | 458.0829 | 394.9977
1558.1292 | 547.945 | 392.1909 | 460.5638 | 396.3461
1559.1292 | 549.3711 | 391.9305 | 460.8876 | 396.1327
1560.1292 | 548.3887 | 392.0908 | 460.9004 | 397.1597
1561.1292 | 548.4411 | 391.7038 | 459.3575 | 397.3617
1562.1292 | 548.0295 | 392.9734 | 460.6602 | 396.4619
1563.1292 | 545.1167 | 394.8269 | 460.5291 | 395.7754
1564.1292 | 544.3856 | 394.7812 | 461.0944 | 394.65
1565.1292 | 543.3678 | 397.0022 | 459.9253 | 394.7975
1566.1292 | 542.553 | 397.467 | 459.0892 | 394.2156
1567.1292 | 541.7744 | 397.1189 | 460.6391 | 393.9147
1568.1292 | 542.1318 | 395.2993 | 458.1457 | 393.7932
1569.1292 | 541.5313 | 393.2715 | 455.8449 | 393.1766
1570.1292 | 542.2796 | 393.0445 | 456.2601 | 394.5351
1571.1292 | 540.6278 | 393.4925 | 456.1939 | 393.5106
1572.1292 | 540.8723 | 395.9313 | 456.4028 | 393.1093
1573.1292 | 530.8901 | 398.1792 | 452.1357 | 392.1979
1574.1292 | 531.3136 | 398.7972 | 451.2347 | 391.0758
1575.1292 | 543.0525 | 399.9864 | 459.2797 | 392.8374
1576.1292 | 543.2846 | 400.3712 | 460.9452 | 393.3533
1577.1292 | 543.4074 | 398.9733 | 461.6458 | 393.6866
1578.1292 | 547.0123 | 397.3892 | 463.3073 | 395.0143
1579.1292 | 548.5754 | 396.8776 | 464.3273 | 396.9531
1580.1292 | 550.0225 | 396.3898 | 465.4253 | 397.1782
1581.1292 | 549.3863 | 396.3439 | 464.1226 | 395.8634
1582.1292 | 549.37 | 397.6349 | 462.8472 | 395.2358
1583.1292 | 548.0226 | 398.4502 | 463.6389 | 395.108
1584.1292 | 549.2089 | 399.5652 | 462.6804 | 394.4911
1585.1292 | 547.7818 | 401.1191 | 464.1118 | 395.7235
1586.1292 | 549.1162 | 401.744 | 463.9087 | 397.2301
1587.1292 | 548.7549 | 402.3042 | 464.6193 | 397.0985
1588.1292 | 548.7171 | 403.7437 | 465.0954 | 397.919
1589.1292 | 548.7693 | 402.7747 | 464.1187 | 396.9214
1590.1292 | 548.329 | 402.5522 | 464.7676 | 396.9737
1591.1292 | 549.0986 | 401.6919 | 464.4777 | 397.8484
1592.1292 | 550.1378 | 401.3743 | 466.6927 | 398.9928
1593.1292 | 551.0926 | 401.0971 | 466.4919 | 398.8516
1594.1292 | 549.7966 | 401.6716 | 467.3935 | 399.603
1595.1292 | 550.874 | 400.984 | 467.52 | 401.3565
1596.1292 | 552.455 | 399.8277 | 468.4231 | 403.1484
1597.1292 | 554.6979 | 399.9552 | 467.7177 | 406.9778
1598.1292 | 557.4202 | 399.0163 | 468.1559 | 407.0398
1599.1292 | 560.5096 | 400.1115 | 469.6133 | 409.6838
1600.1292 | 560.1702 | 401.7055 | 472.2063 | 411.6545
1601.1292 | 558.912 | 401.6911 | 473.8546 | 411.503
1602.1292 | 561.3246 | 400.8364 | 474.8217 | 413.5015
1603.1292 | 563.7729 | 400.203 | 476.2728 | 415.0193
1604.1292 | 568.515 | 399.3033 | 475.2934 | 415.4137
1605.1292 | 570.481 | 397.9643 | 474.0172 | 416.659
1606.1292 | 575.5233 | 397.1411 | 474.1404 | 420.3188
1607.1292 | 580.8805 | 396.8196 | 473.8719 | 423.0477
1608.1292 | 584.2009 | 396.6987 | 472.2128 | 425.8095
1609.1292 | 584.623 | 395.7947 | 469.8477 | 425.3949
1610.1292 | 587.0845 | 395.3056 | 469.4473 | 425.0091
1611.1292 | 586.894 | 394.5863 | 469.9844 | 425.0506
1612.1292 | 586.0609 | 393.8255 | 469.1581 | 424.8362
1613.1292 | 584.877 | 393.6675 | 469.3758 | 426.5377
1614.1292 | 580.337 | 394.406 | 471.5272 | 427.5734
1615.1292 | 576.9057 | 395.033 | 475.0109 | 428.4868
1616.1292 | 578.1906 | 396.0113 | 478.267 | 430.292
1617.1292 | 577.3207 | 395.7466 | 478.355 | 429.3641
1618.1292 | 578.2655 | 396.325 | 479.8831 | 429.8906
1619.1292 | 581.029 | 396.4547 | 479.7151 | 430.5469
1620.1292 | 579.0846 | 397.8535 | 482.4318 | 430.2495
1621.1292 | 575.8657 | 398.4801 | 483.467 | 430.0958
1622.1292 | 571.8181 | 400.7334 | 482.6848 | 428.1307
1623.1292 | 569.8296 | 402.9314 | 481.6005 | 425.2515
1624.1292 | 569.1892 | 405.2476 | 480.9222 | 423.7025
1625.1292 | 566.5094 | 407.9267 | 481.0781 | 422.7227
1626.1292 | 565.0129 | 409.426 | 481.2658 | 420.2699
1627.1292 | 562.3004 | 409.59 | 480.5271 | 418.3735
1628.1292 | 560.0654 | 413.0221 | 480.3095 | 417.4532
1629.1292 | 558.8408 | 414.8741 | 481.7072 | 416.8171
1630.1292 | 557.603 | 415.3273 | 481.0299 | 415.4911
1631.1292 | 557.2566 | 415.1691 | 482.4925 | 414.657
1632.1292 | 555.839 | 415.7154 | 484.2833 | 414.0601
1633.1292 | 557.3027 | 415.9294 | 483.7433 | 414.9943
1634.1292 | 557.3497 | 415.8776 | 482.51 | 419.2909
1635.1448 | 559.1182 | 414.8329 | 481.8123 | 420.9633
1636.1448 | 560.5022 | 413.6344 | 481.3395 | 421.4442
1637.1292 | 560.9863 | 413.7952 | 481.5254 | 422.4944
1638.1292 | 564.6816 | 411.6633 | 481.0598 | 424.6589
1639.1448 | 564.8923 | 410.9343 | 481.0549 | 425.9532
1640.1448 | 566.3501 | 409.7922 | 483.1654 | 430.5874
1641.1448 | 568.0749 | 408.0428 | 480.5627 | 430.3059
1642.1448 | 567.7611 | 407.5403 | 480.6957 | 430.887
1643.1292 | 566.2985 | 407.5098 | 480.6262 | 431.1434
1644.1292 | 566.3841 | 408.2116 | 483.0729 | 430.8096
1645.1292 | 565.7634 | 408.7932 | 485.9539 | 429.8195
1646.1292 | 564.0152 | 410.5505 | 487.0281 | 428.6012
1647.1292 | 563.2108 | 411.3196 | 486.4847 | 427.2906
1648.1292 | 560.7934 | 414.0049 | 486.5707 | 427.056
1649.1292 | 560.3546 | 414.707 | 486.887 | 425.8644
1650.1292 | 558.8724 | 415.4825 | 485.8197 | 424.2612
1651.1292 | 558.6262 | 416.4316 | 485.6773 | 423.2423
1652.1448 | 557.9999 | 418.0978 | 484.7721 | 422.041
1653.1292 | 556.242 | 418.0786 | 484.4418 | 421.3345
1654.1292 | 555.4115 | 418.233 | 485.9532 | 421.9047
1655.1292 | 554.7677 | 418.8062 | 488.4587 | 422.5275
1656.1292 | 554.1811 | 418.2386 | 486.7782 | 420.6121
1657.1292 | 553.2484 | 419.0493 | 485.9223 | 419.1431
1658.1292 | 552.564 | 421.2831 | 485.2279 | 417.8798
1659.1292 | 551.2622 | 423.3507 | 486.4252 | 417.1783
1660.1292 | 551.6821 | 423.3505 | 488.7435 | 417.8677
1661.1448 | 551.8975 | 423.857 | 491.862 | 419.0045
1662.1292 | 554.3101 | 424.5378 | 492.4222 | 421.8307
1663.1292 | 554.9673 | 425.5858 | 494.1568 | 423.7324
1664.1292 | 554.8096 | 424.3745 | 492.4849 | 423.5089
1665.1292 | 554.9175 | 425.1728 | 493.4524 | 424.0778
1666.1292 | 555.0433 | 426.3244 | 495.2964 | 426.0483
1667.1292 | 554.2217 | 426.3582 | 493.8766 | 425.2244
1668.1292 | 554.4332 | 426.9242 | 493.7644 | 423.1357
1669.1292 | 554.024 | 430.6844 | 496.4263 | 422.1629
1670.1292 | 554.6342 | 434.0639 | 499.7635 | 422.1419
1671.1292 | 554.3424 | 434.3274 | 503.0318 | 421.7993
1672.1292 | 554.6057 | 433.48 | 504.1205 | 420.4072
1673.1292 | 553.7351 | 432.9437 | 502.4635 | 420.4637
1674.1292 | 553.0675 | 433.505 | 501.7478 | 419.5764
1675.1292 | 552.0126 | 433.3985 | 500.133 | 418.2026
1676.1292 | 551.2403 | 432.7643 | 498.3063 | 416.7292
1677.1292 | 551.8281 | 431.8148 | 497.0355 | 416.9635
1678.1292 | 552.5818 | 432.5399 | 497.3371 | 417.1229
1679.1292 | 552.0802 | 433.8149 | 496.7971 | 419.3975
1680.1292 | 553.946 | 432.8414 | 496.498 | 419.8149
1681.1292 | 555.9714 | 432.5552 | 497.5536 | 420.0039
1682.1292 | 555.7942 | 434.3639 | 498.8577 | 421.9322
1683.1292 | 555.5361 | 436.7994 | 501.1782 | 422.8776
1684.1292 | 556.6169 | 435.8774 | 503.8567 | 425.603
1685.1292 | 557.3069 | 436.1942 | 504.5191 | 425.519
1686.1292 | 556.5163 | 436.5071 | 506.8094 | 424.9505
1687.1292 | 556.5998 | 438.1551 | 507.813 | 424.1038
1688.1292 | 556.2486 | 438.3161 | 506.8417 | 422.6516
1689.1292 | 556.8727 | 436.5921 | 504.9984 | 423.6587
1690.1292 | 556.4109 | 436.2962 | 503.8321 | 424.1825
1691.1292 | 558.0538 | 435.8953 | 503.2258 | 425.8843
1692.1292 | 561.8677 | 433.845 | 502.6605 | 429.8883
1693.1292 | 562.181 | 434.5389 | 503.5613 | 432.225
1694.1292 | 563.6794 | 435.1258 | 503.8194 | 431.4674
1695.1292 | 562.9768 | 436.0881 | 502.1018 | 430.2488
1696.1292 | 561.1837 | 436.8204 | 500.5247 | 429.1169
1697.1292 | 559.9548 | 437.1509 | 499.9618 | 428.1716
1698.1292 | 561.4724 | 437.7037 | 497.6409 | 426.539
1699.1292 | 561.9661 | 439.6533 | 500.0016 | 425.414
1700.1292 | 564.0764 | 438.195 | 500.3736 | 424.062
1701.1292 | 563.6933 | 438.8828 | 502.6146 | 424.4767
1702.1292 | 565.9116 | 437.2886 | 503.6809 | 426.2969
1703.1292 | 571.0815 | 437.4978 | 506.0437 | 429.5238
1704.1292 | 573.571 | 436.7677 | 510.2394 | 431.457
1705.1292 | 574.109 | 437.8447 | 516.5903 | 432.272
1706.1292 | 574.8294 | 438.4107 | 516.7843 | 430.7106
1707.1292 | 575.839 | 437.858 | 513.494 | 428.2745
1708.1292 | 573.6396 | 439.4951 | 511.5019 | 425.9933
1709.1292 | 573.1332 | 445.3956 | 517.0967 | 426.7926
1710.1292 | 572.6148 | 446.5234 | 520.0392 | 425.6625
1711.1292 | 571.5035 | 445.9761 | 518.7951 | 425.175
1712.1292 | 569.2711 | 447.8658 | 520.191 | 426.284
1713.1292 | 567.7104 | 449.4538 | 519.8889 | 428.3335
1714.1292 | 566.1112 | 450.1906 | 519.8831 | 428.0235
1715.1292 | 564.875 | 449.8827 | 518.9594 | 429.0959
1716.1292 | 563.0549 | 451.7489 | 516.8308 | 428.2914
1717.1292 | 562.1038 | 452.2636 | 516.6337 | 428.7421
1718.1292 | 561.223 | 452.0988 | 516.456 | 429.6167
1719.1292 | 561.8928 | 453.4124 | 516.4403 | 430.5451
1720.1292 | 560.9023 | 453.0821 | 514.7389 | 429.4341
1721.1292 | 560.1157 | 453.7454 | 513.3781 | 428.9781
1722.1292 | 560.0334 | 451.8834 | 513.2184 | 429.421
1723.1292 | 561.6206 | 451.758 | 515.6311 | 429.0667
1724.1292 | 561.6083 | 452.0473 | 515.1885 | 429.5454
1725.1292 | 561.5696 | 453.2371 | 514.9083 | 428.9253
1726.1292 | 560.4757 | 452.3154 | 515.0922 | 428.1978
1727.1292 | 560.2518 | 453.0229 | 519.2373 | 428.4941
1728.1292 | 560.9284 | 452.5088 | 520.334 | 428.5153
1729.1292 | 560.628 | 451.0445 | 520.4311 | 427.8709
1730.1292 | 560.4979 | 450.2299 | 518.9652 | 429.9401
1731.1292 | 562.4527 | 452.4991 | 522.0235 | 430.5336
1732.1292 | 564.2077 | 451.6206 | 521.2255 | 429.9163
1733.1292 | 563.4878 | 450.3207 | 521.9132 | 429.0434
1734.1292 | 564.7551 | 449.2971 | 524.4687 | 429.8369
1735.1292 | 566.2464 | 449.5669 | 525.5918 | 428.9934
1736.1292 | 567.1959 | 447.8077 | 530.4931 | 429.2064
1737.1292 | 565.9951 | 448.9581 | 530.3674 | 431.0057
1738.1292 | 566.7021 | 450.2702 | 531.1612 | 430.8389
1739.1292 | 565.3773 | 450.4249 | 530.3207 | 431.3837
1740.1292 | 565.7281 | 449.2858 | 528.3304 | 431.6362
1741.1292 | 565.3356 | 449.4039 | 529.6994 | 431.1086
1742.1292 | 566.7632 | 449.2207 | 529.0288 | 431.7182
1743.1292 | 565.7303 | 448.7288 | 530.53 | 432.3886
1744.1292 | 563.9687 | 447.998 | 528.7751 | 431.086
1745.1292 | 565.088 | 447.1218 | 527.633 | 429.7631
1746.1292 | 565.4467 | 448.9484 | 530.1448 | 432.0797
1747.1292 | 566.1223 | 448.8857 | 530.7805 | 431.718
1748.1292 | 568.6543 | 447.6677 | 530.7125 | 434.1778
1749.1292 | 568.4107 | 447.6179 | 532.8685 | 434.9681
1750.1292 | 568.1777 | 446.9989 | 533.7386 | 431.78
1751.1292 | 566.8436 | 447.1743 | 529.3459 | 429.7075
1752.1292 | 565.7738 | 448.4293 | 525.5886 | 427.591
1753.1292 | 565.6039 | 446.4241 | 524.1387 | 426.8389
1754.1292 | 564.2168 | 447.3657 | 524.1593 | 427.2599
1755.1292 | 563.5204 | 448.6532 | 528.057 | 428.0852
1756.1292 | 564.2479 | 452.8606 | 527.5718 | 428.9787
1757.1292 | 563.9291 | 454.099 | 525.6065 | 428.7884
1758.1292 | 565.8734 | 456.8636 | 525.0669 | 429.7107
1759.1292 | 566.0984 | 456.9117 | 522.4517 | 429.3903
1760.1292 | 566.9054 | 457.2455 | 521.959 | 427.9259
1761.1292 | 568.008 | 457.9135 | 521.131 | 429.6345
1762.1292 | 571.1504 | 460.0582 | 526.0847 | 431.6492
1763.1292 | 569.9825 | 463.4149 | 528.0075 | 431.9793
1764.1292 | 571.5032 | 465.3985 | 527.6512 | 433.7845
1765.1292 | 575.3795 | 464.1759 | 527.2748 | 434.615
1766.1292 | 577.8642 | 462.727 | 532.7546 | 434.6882
1767.1292 | 579.2645 | 464.0461 | 536.0719 | 434.8717
1768.1292 | 579.3837 | 465.5722 | 535.7758 | 437.7838
1769.1292 | 581.6159 | 468.0918 | 538.0684 | 439.9127
1770.1292 | 582.7987 | 471.4075 | 540.0318 | 443.4286
1771.1292 | 585.1043 | 472.4861 | 542.801 | 443.1018
1772.1292 | 586.1023 | 471.8332 | 545.4497 | 441.5817
1773.1292 | 584.6352 | 470.7285 | 548.3019 | 441.9992
1774.1292 | 583.4546 | 471.461 | 549.1787 | 439.9003
1775.1292 | 581.6691 | 475.9039 | 550.3455 | 440.8767
1776.1292 | 579.2155 | 477.3178 | 550.0353 | 441.2341
1777.1292 | 577.9514 | 477.8206 | 549.205 | 441.2851
1778.1292 | 578.3822 | 478.7913 | 557.3692 | 443.9304
1779.1292 | 577.9196 | 481.9995 | 557.9229 | 444.7472
1780.1292 | 577.7908 | 484.1855 | 559.0221 | 447.4244
1781.1292 | 577.9908 | 484.8801 | 558.6339 | 447.5882
1782.1292 | 578.1255 | 487.0639 | 561.5058 | 449.4771
1783.1292 | 577.5992 | 488.1221 | 562.7945 | 451.0872
1784.1292 | 577.1464 | 489.0038 | 565.3089 | 451.0617
1785.1292 | 575.9557 | 489.247 | 571.6722 | 451.1859
1786.1292 | 574.3523 | 488.8364 | 576.8761 | 450.9376
1787.1292 | 575.6856 | 487.9428 | 575.6259 | 451.0757
1788.1292 | 577.4507 | 489.6245 | 584.9988 | 452.5827
1789.1292 | 580.2325 | 487.2254 | 586.2233 | 452.1847
1790.1292 | 582.0599 | 485.516 | 586.7761 | 451.3173
1791.1292 | 581.1965 | 481.4552 | 584.9092 | 449.5128
1792.1292 | 582.128 | 480.6222 | 584.0664 | 448.3353
1793.1292 | 584.3666 | 482.675 | 587.0444 | 448.0533
1794.1292 | 586.7768 | 480.1027 | 591.2984 | 447.837
1795.1292 | 587.5672 | 479.2962 | 591.3009 | 449.1879
1796.1292 | 587.4734 | 478.5683 | 588.0629 | 448.5936
1797.1292 | 585.8593 | 478.3252 | 586.341 | 447.4569
1798.1292 | 584.5544 | 479.4124 | 581.9698 | 447.0078
1799.1292 | 583.651 | 477.9222 | 593.5034 | 445.6572
1800.1292 | 582.3842 | 478.5714 | 600.8948 | 445.6128
1801.1292 | 580.9488 | 477.3599 | 601.3825 | 445.7304
1802.1292 | 580.5827 | 475.7588 | 596.5282 | 445.3921
1803.1292 | 580.4147 | 475.0109 | 592.8175 | 446.2559
1804.1292 | 579.0164 | 475.5739 | 585.8115 | 446.98
1805.1292 | 578.8869 | 474.9001 | 580.42 | 446.8507
1806.1292 | 577.0746 | 474.4604 | 577.3132 | 444.3025
1807.1292 | 575.7866 | 471.6599 | 569.6682 | 443.3342
1808.1292 | 575.5662 | 470.763 | 566.3464 | 443.0847
1809.1292 | 576.5108 | 470.6638 | 567.3767 | 443.4257
1810.1292 | 575.7192 | 468.6493 | 569.0818 | 442.7526
1811.1292 | 576.9275 | 467.8032 | 572.1359 | 442.4816
1812.1292 | 577.051 | 465.8231 | 573.046 | 441.8877
1813.1292 | 576.2415 | 464.9811 | 570.0557 | 441.5365
1814.1292 | 574.9388 | 465.3626 | 570.5248 | 441.6838
1815.1292 | 574.2335 | 463.947 | 568.317 | 440.0623
1816.1292 | 574.1189 | 462.9055 | 563.763 | 439.4732
1817.1292 | 577.6747 | 465.9572 | 562.2252 | 442.289
1818.1292 | 579.5219 | 465.2345 | 562.6622 | 442.9112
1819.1292 | 579.5427 | 462.398 | 563.728 | 441.2214
1820.1292 | 577.7767 | 460.8098 | 562.2561 | 439.8824
1821.1292 | 576.8664 | 460.6242 | 561.5502 | 439.0531
1822.1292 | 575.8089 | 459.6368 | 558.2413 | 437.5599
1823.1292 | 577.5469 | 457.236 | 555.7743 | 437.6071
1824.1292 | 578.285 | 456.2951 | 556.8989 | 438.6555
1825.1292 | 577.5519 | 455.6802 | 556.8009 | 438.6013
1826.1292 | 576.1148 | 455.8167 | 552.7883 | 439.0783
1827.1292 | 577.1011 | 456.1413 | 550.5543 | 439.4732
1828.1292 | 577.1103 | 455.9564 | 548.4676 | 439.308
1829.1292 | 575.7934 | 455.2752 | 542.5124 | 435.8811
1830.1292 | 574.4739 | 457.0945 | 539.8405 | 434.9358
1831.1292 | 574.9798 | 458.9813 | 540.5636 | 435.4189
1832.1292 | 575.7497 | 458.1395 | 542.9858 | 435.6126
1833.1292 | 576.4582 | 458.4463 | 546.8689 | 437.0637
1834.1292 | 576.4385 | 458.703 | 548.4586 | 437.555
1835.1292 | 578.5431 | 460.2995 | 548.5509 | 437.1202
1836.1292 | 578.7915 | 462.2049 | 553.0499 | 440.1628
1837.1292 | 577.5657 | 464.2209 | 551.0027 | 441.2711
1838.1292 | 576.498 | 464.0226 | 548.3145 | 440.6547
1839.1292 | 574.8841 | 466.6731 | 544.0455 | 438.3857
1840.1292 | 573.4825 | 465.0147 | 540.3724 | 437.5383
1841.1292 | 572.6224 | 465.1124 | 540.1312 | 436.1498
1842.1292 | 571.1632 | 466.4155 | 540.9123 | 435.5945
1843.1292 | 570.1603 | 466.5518 | 540.1718 | 435.8018
1844.1292 | 571.4044 | 467.8486 | 536.7041 | 437.3664
1845.1292 | 570.5488 | 467.9129 | 538.9209 | 438.0153
1846.1292 | 569.3105 | 466.443 | 536.7522 | 437.2017
1847.1292 | 568.9806 | 468.0387 | 539.2257 | 435.8873
1848.1292 | 568.3541 | 466.5959 | 535.8439 | 434.4291
1849.1292 | 568.571 | 467.8394 | 533.7105 | 431.685
1850.1292 | 568.1487 | 467.5568 | 533.3346 | 433.1397
1851.1292 | 569.1826 | 468.2102 | 537.4713 | 435.5985
1852.1292 | 569.7071 | 468.5354 | 539.1247 | 436.8141
1853.1292 | 569.9079 | 467.4829 | 537.9913 | 436.5541
1854.1292 | 571.6418 | 467.3303 | 534.7471 | 433.6763
1855.1292 | 570.873 | 465.8222 | 535.4359 | 432.7377
1856.1292 | 572.6435 | 466.3148 | 534.5995 | 433.4269
1857.1292 | 573.1689 | 464.7082 | 531.4718 | 432.7436
1858.1292 | 572.5682 | 463.2897 | 531.5012 | 433.0138
1859.1292 | 574.0454 | 463.3889 | 542.1168 | 434.1963
1860.1292 | 575.3966 | 462.596 | 543.9714 | 434.0502
1861.1292 | 577.7243 | 461.5999 | 543.6177 | 432.8501
1862.1292 | 577.7056 | 462.0823 | 541.2904 | 432.3767
1863.1292 | 579.7575 | 460.9648 | 540.9844 | 431.911
1864.1292 | 581.0629 | 461.7638 | 542.9871 | 432.2869
1865.1292 | 581.7706 | 460.6993 | 542.5319 | 432.7089
1866.1292 | 580.521 | 462.0871 | 540.8715 | 433.2556
1867.1292 | 579.9337 | 460.0526 | 537.5214 | 434.6458
1868.1292 | 581.6963 | 457.5389 | 546.0479 | 436.5285
1869.1292 | 582.6388 | 455.1487 | 555.0788 | 437.483
1870.1292 | 582.1928 | 453.1238 | 556.1305 | 436.4076
1871.1292 | 582.4045 | 450.5467 | 550.4427 | 435.6701
1872.1292 | 580.6701 | 449.8197 | 546.7796 | 433.8017
1873.1448 | 579.8164 | 449.0566 | 544.8126 | 433.4795
1874.1448 | 579.3479 | 447.2802 | 542.8393 | 433.4566
1875.1292 | 580.2364 | 446.3567 | 544.1787 | 433.1485
1876.1292 | 580.8097 | 448.6187 | 548.5122 | 432.5691
1877.1448 | 580.4305 | 448.4523 | 546.9615 | 432.0068
1878.1292 | 581.7388 | 451.3042 | 543.3921 | 431.3697
1879.1448 | 581.2982 | 452.4034 | 542.8947 | 433.9158
1880.1292 | 580.0612 | 453.5999 | 542.9126 | 432.3559
1881.1292 | 579.6804 | 452.431 | 543.566 | 431.9505
1882.1292 | 580.2269 | 450.8828 | 544.7454 | 431.5615
1883.1292 | 582.067 | 453.1762 | 547.4889 | 430.9209
1884.1292 | 582.613 | 453.1273 | 547.6857 | 432.21
1885.1292 | 581.7996 | 453.43 | 543.6162 | 432.957
1886.1292 | 580.9318 | 453.8023 | 544.0814 | 432.7632
1887.1292 | 580.8491 | 453.4182 | 541.6503 | 431.4594
1888.1292 | 580.1727 | 452.9431 | 537.6479 | 430.7231
1889.1292 | 579.416 | 452.7928 | 534.855 | 429.4617
1890.1292 | 579.4768 | 452.9499 | 532.919 | 428.6777
1891.1292 | 579.3942 | 454.5605 | 531.7753 | 429.2295
1892.1292 | 578.3859 | 455.206 | 531.5886 | 429.1903
1893.1292 | 578.2349 | 456.4876 | 530.7867 | 429.2381
1894.1292 | 577.817 | 457.9975 | 531.2754 | 430.6236
1895.1292 | 579.61 | 455.5891 | 530.3807 | 432.188
1896.1292 | 582.0942 | 455.0384 | 532.3674 | 433.5256
1897.1292 | 583.1853 | 455.5655 | 532.2543 | 433.447
1898.1292 | 583.0933 | 456.1421 | 534.2902 | 433.9637
1899.1292 | 584.4458 | 459.4258 | 535.5981 | 433.2463
1900.1292 | 584.7901 | 460.5897 | 538.992 | 432.8953
1901.1292 | 583.825 | 461.2358 | 536.9385 | 433.0131
1902.1292 | 583.329 | 458.9262 | 533.989 | 433.2788
1903.1292 | 587.6127 | 456.5809 | 534.8862 | 434.9291
1904.1292 | 589.0214 | 457.1832 | 536.7928 | 435.9677
1905.1292 | 587.7181 | 457.7262 | 533.35 | 435.3338
1906.1292 | 586.8289 | 456.0504 | 530.0918 | 436.6545
1907.1292 | 585.8907 | 455.886 | 530.4352 | 435.9218
1908.1292 | 584.2482 | 457.0533 | 531.9344 | 435.6644
1909.1292 | 583.8979 | 457.1154 | 530.5584 | 435.03
1910.1292 | 584.7039 | 458.6682 | 527.6169 | 433.1565
1911.1292 | 584.062 | 458.59 | 524.8609 | 430.4528
1912.1292 | 582.6624 | 458.653 | 524.6521 | 430.2445
1913.1292 | 582.7707 | 459.6316 | 524.97 | 430.9229
1914.1292 | 582.3169 | 461.3488 | 526.3119 | 431.2513
1915.1292 | 581.3059 | 462.0648 | 527.7467 | 431.4774
1916.1292 | 580.1134 | 460.9116 | 525.1504 | 430.9428
1917.1292 | 579.4601 | 459.1964 | 522.9439 | 429.6171
1918.1292 | 579.8699 | 458.2776 | 520.6331 | 427.3161
1919.1292 | 578.9664 | 457.3659 | 519.2289 | 427.3272
1920.1292 | 581.1241 | 456.8623 | 517.316 | 429.7187
1921.1292 | 588.7411 | 456.4644 | 523.3179 | 432.3167
1922.1292 | 590.5256 | 456.7854 | 524.9775 | 432.8831
1923.1292 | 592.3508 | 457.8971 | 525.1199 | 435.1537
1924.1292 | 593.537 | 458.2467 | 527.7087 | 435.4394
1925.1292 | 593.7312 | 460.9688 | 527.589 | 434.1206
1926.1292 | 591.7904 | 463.109 | 526.6743 | 432.2588
1927.1292 | 590.9585 | 463.6363 | 529.6989 | 430.8643
1928.1292 | 591.1605 | 465.2292 | 529.6191 | 430.7716
1929.1292 | 589.7975 | 465.2875 | 529.5921 | 430.6637
1930.1292 | 589.0866 | 464.3233 | 529.4218 | 430.8693
1931.1292 | 590.6062 | 464.0339 | 529.5309 | 431.3783
1932.1292 | 591.4339 | 465.2578 | 527.2615 | 432.7374
1933.1292 | 590.4014 | 466.494 | 527.0946 | 433.0541
1934.1292 | 588.8415 | 467.4735 | 526.7699 | 431.5561
1935.1292 | 592.9258 | 466.8375 | 523.0582 | 433.0678
1936.1292 | 598.8172 | 467.5582 | 525.7981 | 437.1291
1937.1292 | 599.1601 | 468.4368 | 530.4865 | 440.6319
1938.1292 | 598.0723 | 469.5717 | 532.4165 | 439.6444
1939.1292 | 596.4837 | 470.2516 | 530.5818 | 440.0769
1940.1292 | 599.9725 | 469.8589 | 532.3177 | 438.3841
1941.1292 | 598.2481 | 471.5387 | 533.5075 | 437.5069
1942.1292 | 596.3798 | 470.1189 | 532.6212 | 436.9263
1943.1292 | 595.5063 | 470.8611 | 530.5658 | 435.4786
1944.1292 | 592.9636 | 471.7413 | 529.0362 | 436.042
1945.1292 | 591.689 | 470.1441 | 530.607 | 435.5931
1946.1292 | 590.4193 | 468.6348 | 531.7933 | 435.046
1947.1292 | 590.2062 | 471.5435 | 529.572 | 435.3244
1948.1292 | 589.5385 | 472.9072 | 537.7787 | 437.196
1949.1292 | 590.996 | 471.5182 | 536.7154 | 438.7998
1950.1292 | 590.4857 | 468.7069 | 542.4887 | 438.8062
1951.1292 | 590.1487 | 466.7273 | 544.3682 | 438.1599
1952.1292 | 590.3202 | 465.8157 | 541.137 | 436.4066
1953.1292 | 590.6789 | 467.2004 | 538.3218 | 435.6915
1954.1292 | 589.8207 | 468.5112 | 541.4626 | 435.8261
1955.1292 | 590.5599 | 469.8996 | 538.4377 | 434.7851
1956.1292 | 589.2672 | 471.5591 | 533.5615 | 433.3755
1957.1292 | 589.9341 | 470.046 | 530.2572 | 431.1087
1958.1292 | 590.0905 | 472.3047 | 531.4926 | 429.9493
1959.1292 | 589.227 | 470.4512 | 527.7414 | 430.2091
1960.1292 | 588.0804 | 468.2825 | 523.779 | 429.4378
1961.1292 | 594.8795 | 467.0069 | 520.8495 | 430.3242
1962.1292 | 596.4785 | 464.3914 | 521.2099 | 430.5131
1963.1292 | 600.4251 | 464.4168 | 523.3325 | 432.5627
1964.1292 | 600.1862 | 461.7053 | 526.6687 | 436.654
1965.1292 | 600.9984 | 463.2299 | 525.7785 | 437.6642
1966.1292 | 599.4908 | 465.8491 | 528.7601 | 438.2166
1967.1292 | 598.8769 | 467.1615 | 526.6614 | 437.7218
1968.1292 | 598.003 | 468.1241 | 525.471 | 438.9167
1969.1292 | 601.6966 | 465.6657 | 525.5327 | 438.2266
1970.1292 | 603.3993 | 464.5216 | 530.3912 | 440.0602
1971.1292 | 602.5061 | 466.0815 | 531.6201 | 439.1197
1972.1292 | 600.7146 | 466.5041 | 529.5016 | 440.3335
1973.1292 | 599.9759 | 465.88 | 527.8228 | 438.435
1974.1292 | 599.1982 | 464.6861 | 526.9154 | 436.6231
1975.1292 | 599.2978 | 466.3778 | 529.1589 | 440.3497
1976.1292 | 598.8765 | 464.2132 | 525.1271 | 439.0101
1977.1292 | 602.5638 | 462.9765 | 522.1542 | 436.562
1978.1292 | 601.1073 | 463.5267 | 520.253 | 435.2954
1979.1292 | 601.0717 | 462.7634 | 519.767 | 435.0152
1980.1292 | 599.4504 | 463.3616 | 523.1157 | 433.4958
1981.1292 | 601.7705 | 465.0195 | 523.2187 | 435.6158
1982.1292 | 601.8393 | 463.6527 | 519.2642 | 435.3535
1983.1292 | 598.8878 | 462.4413 | 516.7586 | 434.1409
1984.1292 | 598.478 | 461.3188 | 516.2099 | 434.0222
1985.1292 | 599.0267 | 460.8567 | 516.2615 | 434.5166
1986.1292 | 599.1952 | 463.0078 | 519.8057 | 435.9386
1987.1292 | 597.5265 | 463.7881 | 520.118 | 436.9559
1988.1292 | 595.3153 | 463.285 | 520.2109 | 435.5152
1989.1292 | 595.4854 | 462.7979 | 518.4149 | 434.9786
1990.1292 | 593.4407 | 462.0587 | 515.3472 | 434.3351
1991.1292 | 593.0612 | 461.2744 | 515.0203 | 433.2408
1992.1292 | 594.4234 | 460.5568 | 516.6417 | 433.8897
1993.1292 | 593.5708 | 461.0893 | 521.2411 | 433.7757
1994.1292 | 592.7566 | 460.7436 | 522.7146 | 433.3003
1995.1292 | 592.3994 | 461.0957 | 522.4906 | 432.9726
1996.1292 | 591.0003 | 460.5684 | 520.4539 | 432.6805
1997.1292 | 591.5227 | 459.5244 | 523.3913 | 431.6294
1998.1292 | 593.9843 | 459.1934 | 525.2003 | 431.6887
1999.1292 | 595.6329 | 458.5446 | 527.9886 | 432.8604
2000.1292 | 595.5744 | 459.1897 | 526.9479 | 431.7771
2001.1292 | 595.4818 | 459.5086 | 527.9814 | 431.5112
2002.1292 | 595.2062 | 458.1821 | 530.859 | 430.3358
2003.1292 | 595.5114 | 458.5899 | 534.6008 | 429.4982
2004.1292 | 594.7606 | 458.7453 | 533.7728 | 429.8722
2005.1292 | 594.7898 | 459.4301 | 533.3342 | 429.9657
2006.1292 | 594.4669 | 458.5002 | 535.0207 | 429.4814
2007.1292 | 593.2433 | 459.415 | 535.3101 | 430.4204
2008.1292 | 593.8096 | 459.5327 | 532.8764 | 429.6136
2009.1292 | 595.0631 | 461.8625 | 532.6063 | 430.0251
2010.1292 | 595.0293 | 462.7783 | 530.5343 | 429.4531
2011.1292 | 595.3095 | 465.6064 | 532.9283 | 429.6629
2012.1292 | 594.7218 | 466.5634 | 531.2695 | 429.4403
2013.1292 | 594.8506 | 468.2669 | 533.3682 | 430.2137
2014.1292 | 594.2978 | 467.9722 | 532.1408 | 430.3061
2015.1292 | 594.3675 | 471.0671 | 534.0962 | 430.638
2016.1292 | 593.5525 | 470.3234 | 534.3514 | 430.7593
2017.1292 | 592.4752 | 471.2343 | 532.73 | 431.0157
2018.1292 | 596.8018 | 471.7404 | 537.5837 | 431.1175
2019.1292 | 598.3672 | 470.2974 | 539.2971 | 431.5765
2020.1292 | 599.6412 | 470.5645 | 540.2447 | 430.9067
2021.1292 | 603.0578 | 470.6898 | 540.566 | 430.868
2022.1292 | 604.2225 | 471.3718 | 541.1872 | 431.8591
2023.1292 | 605.9971 | 470.9754 | 540.2258 | 433.1123
2024.1292 | 608.0951 | 470.2349 | 540.225 | 433.6012
2025.1292 | 609.0613 | 470.3026 | 542.0227 | 435.0302
2026.1292 | 612.4063 | 472.1401 | 541.3878 | 438.0373
2027.1292 | 613.8207 | 471.531 | 538.0934 | 438.9779
2028.1292 | 613.0983 | 470.4083 | 537.2711 | 439.4921
2029.1292 | 613.8507 | 468.6595 | 538.1173 | 439.0162
2030.1292 | 611.9151 | 468.0662 | 540.7777 | 440.1393
2031.1292 | 609.6367 | 470.4857 | 540.7291 | 441.4455
2032.1292 | 608.9451 | 469.3154 | 539.2428 | 440.4635
2033.1292 | 607.9493 | 469.1606 | 539.4676 | 440.7321
2034.1292 | 607.3486 | 469.8529 | 536.9937 | 439.9082
2035.1292 | 608.2588 | 471.3464 | 534.5789 | 440.1815
2036.1292 | 607.1523 | 472.5889 | 535.5353 | 439.5393
2037.1292 | 606.6241 | 470.0524 | 533.7489 | 439.508
2038.1292 | 606.5674 | 468.8818 | 535.7228 | 440.1154
2039.1292 | 610.0397 | 467.4869 | 534.6601 | 439.3899
2040.1292 | 609.2648 | 466.31 | 537.2527 | 441.0219
2041.1292 | 608.5638 | 466.7172 | 533.5099 | 441.359
2042.1292 | 606.8279 | 466.6154 | 530.47 | 439.6052
2043.1292 | 605.1263 | 468.9548 | 528.9403 | 438.9149
2044.1292 | 604.401 | 468.2806 | 530.0299 | 438.1147
2045.1292 | 605.6899 | 467.3241 | 532.6119 | 437.0444
2046.1292 | 606.6162 | 468.7585 | 534.3952 | 438.3721
2047.1292 | 605.69 | 470.4461 | 532.7551 | 438.45
2048.1292 | 604.1011 | 469.734 | 531.0531 | 436.8955
2049.1292 | 602.8604 | 469.4886 | 529.3985 | 435.5234
2050.1292 | 601.4206 | 467.8717 | 528.0326 | 433.9309
2051.1292 | 600.5973 | 467.8815 | 528.2494 | 434.275
2052.1292 | 599.8621 | 468.1853 | 527.4872 | 433.8892
2053.1292 | 599.3925 | 467.9845 | 525.3772 | 432.2616
2054.1292 | 600.4792 | 467.2541 | 524.7857 | 431.0159
2055.1292 | 600.0922 | 467.41 | 522.3189 | 430.0846
2056.1292 | 600.2886 | 467.0192 | 519.7656 | 428.9941
2057.1292 | 599.6193 | 465.3174 | 517.4452 | 428.6151
2058.1292 | 600.1937 | 466.7926 | 518.2761 | 429.2584
2059.1292 | 601.1399 | 465.2654 | 527.2277 | 430.0946
2060.1292 | 600.7369 | 465.6932 | 529.6661 | 432.4889
2061.1292 | 599.3744 | 466.2574 | 529.6135 | 432.2355
2062.1292 | 599.0152 | 465.8692 | 530.7772 | 431.9926
2063.1292 | 599.0733 | 465.574 | 533.0809 | 431.6932
2064.1292 | 599.6263 | 465.4299 | 530.2114 | 430.3188
2065.1292 | 600.8768 | 466.798 | 531.5922 | 429.9191
2066.1292 | 602.3171 | 468.9217 | 528.4438 | 428.9861
2067.1292 | 602.4915 | 468.7952 | 527.0768 | 429.2091
2068.1292 | 605.1628 | 468.5283 | 526.8776 | 429.2315
2069.1292 | 605.3807 | 469.9314 | 527.4198 | 429.2466
2070.1292 | 605.6165 | 470.6943 | 526.9373 | 429.2633
2071.1292 | 605.0549 | 470.9119 | 528.0373 | 428.8032
2072.1292 | 605.3164 | 470.8154 | 526.7349 | 427.4413
2073.1292 | 604.9213 | 470.276 | 526.0839 | 427.7615
2074.1292 | 606.9757 | 469.3793 | 524.6319 | 429.7278
2075.1292 | 607.4397 | 469.7458 | 525.7089 | 431.2054
2076.1292 | 606.7086 | 468.6003 | 529.8495 | 431.797
2077.1292 | 604.4516 | 467.314 | 534.218 | 431.9232
2078.1292 | 603.6349 | 466.185 | 531.1513 | 433.6679
2079.1292 | 602.0214 | 465.008 | 530.2634 | 434.0618
2080.1292 | 600.5482 | 465.6636 | 528.5584 | 433.6723
2081.1292 | 600.2908 | 465.8932 | 525.0817 | 433.1894
2082.1292 | 599.3045 | 463.9675 | 520.7058 | 431.9347
2083.1292 | 599.2582 | 462.8751 | 517.971 | 430.2576
2084.1292 | 599.0051 | 462.4585 | 515.7991 | 429.5354
2085.1292 | 597.7855 | 461.4715 | 514.9539 | 429.4364
2086.1292 | 597.4269 | 460.7978 | 521.1783 | 431.0765
2087.1292 | 598.3423 | 462.3742 | 520.7546 | 429.6154
2088.1292 | 602.4582 | 462.4883 | 518.534 | 428.7172
2089.1292 | 604.1185 | 461.1355 | 515.8626 | 428.3602
2090.1292 | 602.7403 | 461.5545 | 512.9822 | 426.7974
2091.1292 | 603.8383 | 462.7945 | 513.3002 | 426.805
2092.1292 | 603.8339 | 461.6116 | 514.582 | 426.6206
2093.1292 | 604.6808 | 461.4431 | 514.2966 | 426.7926
2094.1292 | 603.6841 | 462.7358 | 514.7938 | 427.8113
2095.1292 | 602.0745 | 460.7681 | 513.8901 | 426.9109
2096.1292 | 601.7284 | 461.0941 | 513.355 | 427.6238
2097.1292 | 600.9855 | 460.0472 | 516.3667 | 427.5154
2098.1292 | 601.7697 | 459.9087 | 516.6639 | 427.4005
2099.1292 | 602.1935 | 459.7835 | 517.708 | 427.0548
2100.1292 | 602.9443 | 461.4724 | 518.5484 | 427.7994
2101.1292 | 603.4871 | 461.8403 | 516.644 | 427.4361
2102.1292 | 603.3092 | 461.4026 | 518.6244 | 427.8975
2103.1292 | 602.5422 | 462.197 | 518.9413 | 429.2638
2104.1292 | 602.4134 | 460.8423 | 520.3311 | 429.2547
2105.1292 | 603.59 | 460.492 | 519.1597 | 429.053
2106.1292 | 602.1168 | 460.5118 | 517.1582 | 427.9579
2107.1292 | 600.0168 | 460.775 | 516.2526 | 427.5192
2108.1292 | 599.1764 | 461.3433 | 516.443 | 427.1519
2109.1292 | 597.4831 | 462.0311 | 517.6812 | 427.5976
2110.1292 | 596.2174 | 461.2147 | 515.1809 | 427.3104
2111.1292 | 596.4014 | 461.1771 | 520.6723 | 427.0347
2112.1292 | 594.9762 | 461.4449 | 518.3025 | 429.3148
2113.1292 | 594.9001 | 461.3343 | 516.2883 | 428.7249
2114.1292 | 595.2305 | 461.7915 | 516.8226 | 427.3517
2115.1292 | 597.1009 | 462.8592 | 514.4292 | 426.656
2116.1292 | 595.9656 | 462.9254 | 512.9536 | 427.3319
2117.1292 | 595.0336 | 463.135 | 512.788 | 427.4614
2118.1292 | 594.5012 | 465.1472 | 511.0465 | 428.3346
2119.1448 | 595.9143 | 463.1207 | 511.0893 | 428.1449
2120.1292 | 598.3751 | 462.3806 | 510.4559 | 427.4219
2121.1448 | 601.7219 | 461.0187 | 510.7931 | 428.5539
2122.1292 | 605.3868 | 459.3881 | 510.4096 | 428.6801
2123.1448 | 606.0502 | 462.654 | 509.9672 | 429.3652
2124.1292 | 607.6906 | 462.7686 | 509.614 | 427.9912
2125.1448 | 609.2531 | 466.7582 | 508.6866 | 428.4018
2126.1292 | 609.0144 | 484.4103 | 507.3172 | 428.7953
2127.1292 | 607.7938 | 483.1475 | 505.7189 | 427.7852
2128.1292 | 609.1512 | 480.7306 | 505.1665 | 428.1137
2129.1292 | 609.3374 | 477.2704 | 506.8715 | 428.3741
2130.1292 | 610.0861 | 473.0101 | 508.423 | 428.0804
2131.1292 | 616.4096 | 469.2962 | 508.2641 | 428.5174
2132.1292 | 617.2478 | 466.7764 | 509.0721 | 429.8551
2133.1292 | 616.6413 | 465.4112 | 509.3464 | 430.4841
2134.1292 | 616.178 | 463.3582 | 509.988 | 430.6691
2135.1292 | 615.0976 | 462.3623 | 508.5183 | 431.1844
2136.1292 | 615.0018 | 464.1414 | 508.5874 | 432.7177
2137.1292 | 614.688 | 464.9729 | 507.4777 | 432.151
2138.1292 | 614.0015 | 463.9949 | 505.1721 | 432.4199
2139.1292 | 612.8019 | 463.5439 | 504.851 | 433.2626
2140.1292 | 613.6572 | 463.1578 | 503.2244 | 434.9524
2141.1292 | 612.2681 | 463.7994 | 511.2519 | 435.6938
2142.1292 | 610.0816 | 466.442 | 512.9059 | 436.6736
2143.1292 | 608.8536 | 467.0848 | 512.5309 | 436.7505
2144.1292 | 607.65 | 467.1691 | 512.1015 | 436.2006
2145.1292 | 608.0401 | 468.967 | 511.9701 | 436.2622
2146.1292 | 611.9681 | 468.0908 | 512.3596 | 437.2254
2147.1292 | 614.7691 | 466.3443 | 511.1193 | 437.6713
2148.1292 | 615 | 465.0417 | 509.3169 | 437.0645
2149.1292 | 615.9682 | 464.7902 | 509.012 | 437.1779
2150.1292 | 615.4793 | 464.709 | 508.1407 | 436.821
2151.1292 | 615.0506 | 464.7184 | 507.551 | 435.4782
2152.1292 | 614.0536 | 464.1083 | 507.6966 | 435.6422
2153.1292 | 613.3501 | 464.5525 | 506.8625 | 435.389
2154.1292 | 613.6477 | 464.0333 | 507.6681 | 436.0133
2155.1292 | 614.1257 | 465.2624 | 509.3736 | 436.7561
2156.1292 | 615.367 | 465.0205 | 512.2975 | 437.03
2157.1292 | 614.3119 | 463.0771 | 513.2176 | 436.2239
2158.1292 | 612.5062 | 463.4754 | 511.9802 | 436.2079
2159.1292 | 611.305 | 462.6295 | 511.539 | 434.7534
2160.1292 | 611.1499 | 462.5671 | 511.4527 | 433.349
2161.1292 | 612.1632 | 462.7584 | 509.4949 | 433.6979
2162.1292 | 610.4369 | 462.2659 | 521.821 | 433.5967
2163.1292 | 612.8087 | 459.8034 | 518.884 | 433.7055
2164.1292 | 611.1635 | 461.4505 | 519.3971 | 433.5908
2165.1292 | 609.1372 | 462.3815 | 519.9337 | 434.9502
2166.1292 | 609.8206 | 460.7851 | 517.8965 | 435.7143
2167.1292 | 612.3289 | 460.12 | 518.4347 | 436.6006
2168.1292 | 614.2157 | 461.263 | 519.5276 | 437.8047
2169.1292 | 614.2396 | 461.2047 | 520.6595 | 439.5883
2170.1292 | 614.9165 | 460.0247 | 519.3382 | 440.6289
2171.1292 | 612.7085 | 460.8628 | 521.0474 | 440.6934
2172.1292 | 609.9622 | 460.9469 | 522.2866 | 439.6146
2173.1292 | 608.7335 | 461.2719 | 520.4658 | 439.6023
2174.1292 | 609.2602 | 461.0323 | 519.7285 | 438.9905
2175.1292 | 608.641 | 460.0119 | 517.6759 | 438.6703
2176.1292 | 607.1166 | 458.7018 | 517.4253 | 438.5805
2177.1292 | 607.6338 | 460.5997 | 516.7268 | 440.3922
2178.1292 | 609.9561 | 459.1109 | 515.1071 | 442.5038
2179.1292 | 610.0256 | 458.5552 | 514.9548 | 442.5136
2180.1292 | 611.0053 | 457.744 | 515.3689 | 442.4531
2181.1292 | 611.4103 | 458.3461 | 516.9352 | 440.565
2182.1292 | 610.4349 | 461.2399 | 516.915 | 440.4941
2183.1292 | 609.9139 | 460.7652 | 518.4437 | 441.5441
2184.1292 | 608.3237 | 461.1861 | 516.3818 | 441.9936
2185.1292 | 607.5912 | 462.0388 | 515.4011 | 442.3108
2186.1292 | 606.6583 | 462.8448 | 515.1425 | 443.5578
2187.1292 | 605.5167 | 462.2949 | 513.8374 | 442.2889
2188.1292 | 605.2376 | 462.3428 | 513.7912 | 442.8595
2189.1292 | 604.6736 | 462.4458 | 514.0633 | 441.7758
2190.1292 | 604.6403 | 462.8535 | 514.5576 | 442.4549
2191.1292 | 604.7729 | 461.4356 | 513.3356 | 441.2669
2192.1292 | 605.3126 | 460.1429 | 526.112 | 440.5193
2193.1292 | 604.8642 | 461.4263 | 528.8894 | 441.1394
2194.1292 | 602.7115 | 460.3818 | 526.575 | 441.2303
2195.1292 | 602.1275 | 460.3279 | 526.3179 | 441.9085
2196.1292 | 602.0488 | 458.8614 | 525.5133 | 443.1979
2197.1292 | 602.507 | 460.0504 | 526.4351 | 443.8566
2198.1292 | 602.6894 | 459.7692 | 524.4419 | 444.0741
2199.1292 | 601.5926 | 460.4303 | 523.3618 | 445.6684
2200.1292 | 600.955 | 460.4223 | 521.3144 | 447.4547
2201.1292 | 602.8941 | 459.8386 | 521.0171 | 447.3804
2202.1292 | 603.1522 | 458.4509 | 519.289 | 449.5733
2203.1292 | 603.4872 | 458.3594 | 519.5774 | 449.95
2204.1292 | 604.9512 | 456.5557 | 517.484 | 448.6352
2205.1292 | 605.3028 | 457.9435 | 519.6751 | 448.8486
2206.1292 | 606.3229 | 457.3745 | 518.582 | 450.1982
2207.1292 | 607.4324 | 455.4413 | 515.4751 | 450.5444
2208.1292 | 608.6255 | 453.5313 | 512.9485 | 450.3019
2209.1292 | 608.5474 | 453.2627 | 513.0032 | 451.4908
2210.1292 | 608.1952 | 453.0444 | 512.9882 | 453.4138
2211.1292 | 607.6481 | 452.1175 | 513.4005 | 453.2277
2212.1292 | 606.1279 | 452.2511 | 512.731 | 453.0536
2213.1292 | 604.4244 | 451.2377 | 512.3473 | 451.7459
2214.1292 | 604.5458 | 449.6943 | 512.1822 | 452.6814
2215.1292 | 605.3593 | 448.5533 | 512.1546 | 453.9795
2216.1292 | 607.003 | 449.1502 | 511.3646 | 456.5325
2217.1292 | 607.6624 | 447.9989 | 508.5545 | 456.2476
2218.1292 | 608.2498 | 448.7175 | 507.8732 | 458.347
2219.1292 | 610.1374 | 449.2269 | 507.2597 | 458.4379
2220.1292 | 609.5169 | 449.9759 | 509.225 | 458.2927
2221.1292 | 609.7715 | 450.6811 | 509.9389 | 457.3064
2222.1292 | 608.3548 | 455.3269 | 512.498 | 460.0775
2223.1292 | 606.2326 | 457.5329 | 514.1297 | 463.2699
2224.1292 | 604.9421 | 458.7121 | 514.4212 | 463.0066
2225.1292 | 604.3686 | 460.6335 | 516.4083 | 463.4778
2226.1292 | 604.1437 | 459.3981 | 517.7041 | 462.1273
2227.1292 | 603.9566 | 459.3161 | 519.7027 | 461.8576
2228.1292 | 603.5763 | 459.9458 | 521.6126 | 462.6512
2229.1292 | 603.3094 | 462.1017 | 522.4983 | 464.2205
2230.1292 | 603.7676 | 462.8371 | 521.1404 | 464.3565
2231.1292 | 602.6683 | 463.092 | 522.6799 | 467.2464
2232.1292 | 603.2941 | 461.529 | 523.7588 | 467.3434
2233.1292 | 603.4535 | 461.8609 | 526.0173 | 467.824
2234.1292 | 604.1468 | 463.0336 | 527.0995 | 467.113
2235.1292 | 605.3746 | 463.2767 | 528.1553 | 469.3467
2236.1292 | 606.0532 | 464.3523 | 530.8896 | 470.1391
2237.1292 | 605.2533 | 465.8033 | 531.7824 | 468.9265
2238.1292 | 604.7392 | 465.1438 | 530.9707 | 468.3261
2239.1292 | 604.1372 | 466.3296 | 532.9028 | 468.9513
2240.1292 | 603.4902 | 466.3818 | 535.38 | 469.4077
2241.1292 | 603.7508 | 467.5554 | 537.6985 | 469.8246
2242.1292 | 604.5653 | 468.8024 | 539.3035 | 470.1786
2243.1292 | 603.9106 | 468.5568 | 538.9123 | 469.5611
2244.1292 | 603.7901 | 469.5366 | 539.0614 | 470.0139
2245.1292 | 603.1975 | 470.1757 | 539.982 | 471.3421
2246.1292 | 603.4083 | 470.7069 | 542.1751 | 470.9382
2247.1292 | 602.9926 | 472.2514 | 542.1055 | 470.6034
2248.1292 | 602.6716 | 471.9089 | 542.3699 | 470.2168
2249.1292 | 602.3554 | 471.6028 | 541.6012 | 471.1591
2250.1292 | 602.2712 | 471.1138 | 541.2429 | 472.1939
2251.1292 | 603.6433 | 471.5675 | 540.0307 | 470.8731
2252.1292 | 604.027 | 470.3357 | 546.2842 | 471.0501
2253.1292 | 604.6448 | 471.5867 | 545.1979 | 470.4867
2254.1292 | 605.0215 | 473.2284 | 546.7385 | 472.7266
2255.1292 | 605.9166 | 474.4504 | 546.9492 | 472.1526
2256.1292 | 606.94 | 476.1908 | 544.5294 | 471.2357
2257.1292 | 608.8991 | 477.8775 | 541.9449 | 470.3694
2258.1292 | 610.6141 | 480.0407 | 540.0371 | 468.857
2259.1292 | 611.3208 | 480.1305 | 537.4344 | 467.9619
2260.1292 | 612.2595 | 481.8419 | 536.3358 | 468.5225
2261.1292 | 613.6505 | 482.9112 | 540.035 | 470.2242
2262.1292 | 613.5396 | 485.468 | 542.2895 | 471.1881
2263.1292 | 613.1829 | 485.4291 | 543.1979 | 471.4934
2264.1292 | 612.2311 | 486.8449 | 544.891 | 470.3813
2265.1292 | 611.1264 | 489.0033 | 544.4627 | 471.3364
2266.1292 | 610.2902 | 490.278 | 545.469 | 472.9702
2267.1292 | 609.8305 | 491.2919 | 547.094 | 472.8676
2268.1292 | 609.2919 | 490.0722 | 549.8911 | 471.741
2269.1292 | 608.639 | 491.1207 | 550.2989 | 471.1205
2270.1292 | 608.2473 | 491.6888 | 548.044 | 470.4982
2271.1292 | 608.7392 | 491.0334 | 547.1807 | 469.989
2272.1292 | 609.308 | 491.0855 | 548.6482 | 471.3706
2273.1292 | 608.5528 | 491.6308 | 548.8285 | 471.7427
2274.1292 | 607.5136 | 490.0106 | 548.2731 | 470.9454
2275.1292 | 606.3648 | 489.7217 | 550.1874 | 471.7478
2276.1292 | 606.2092 | 489.7688 | 551.1582 | 473.2138
2277.1292 | 607.3903 | 494.0385 | 556.9913 | 474.8394
2278.1292 | 608.1135 | 492.4732 | 556.1785 | 474.0432
2279.1292 | 608.6337 | 492.8403 | 556.4859 | 474.5658
2280.1292 | 608.5296 | 495.1279 | 558.0126 | 475.3858
2281.1292 | 607.5552 | 494.4231 | 556.5803 | 473.9608
2282.1292 | 606.7345 | 492.9243 | 556.3794 | 472.5045
2283.1292 | 606.3287 | 493.156 | 565.7181 | 472.2111
2284.1292 | 606.1587 | 494.9797 | 568.0672 | 472.8054
2285.1292 | 606.3515 | 495.3558 | 567.2558 | 474.3618
2286.1292 | 606.6366 | 496.9318 | 569.7377 | 476.323
2287.1292 | 605.4599 | 497.7579 | 568.7764 | 477.4844
2288.1292 | 607.0575 | 496.0698 | 566.4619 | 477.8136
2289.1292 | 608.381 | 494.5387 | 562.6584 | 477.6869
2290.1292 | 609.5213 | 501.5197 | 566.219 | 478.4981
2291.1292 | 608.9637 | 498.8572 | 563.8244 | 476.5223
2292.1292 | 609.1099 | 499.0361 | 564.6605 | 477.6175
2293.1292 | 606.9368 | 498.1965 | 562.6167 | 478.0942
2294.1292 | 606.7053 | 496.4109 | 566.2603 | 478.711
2295.1292 | 607.3453 | 501.7447 | 574.536 | 478.0568
2296.1292 | 608.8098 | 505.0614 | 582.1167 | 480.2863
2297.1292 | 610.165 | 507.6978 | 587.7657 | 479.9827
2298.1292 | 610.9203 | 507.5143 | 587.8153 | 480.5211
2299.1292 | 610.086 | 507.5069 | 589.1589 | 498.0277
2300.1292 | 611.472 | 508.4546 | 593.9038 | 499.0294
2301.1292 | 609.457 | 508.527 | 598.3339 | 501.1472
2302.1292 | 608.2658 | 513.4415 | 599.2656 | 507.0512
2303.1292 | 607.2082 | 513.186 | 611.3321 | 505.9985
2304.1292 | 609.1516 | 511.8457 | 610.6609 | 507.501
2305.1292 | 609.6738 | 513.1455 | 612.6296 | 517.7216
2306.1292 | 610.2474 | 512.747 | 607.3596 | 516.1755
2307.1292 | 611.6102 | 514.0618 | 602.3998 | 517.1474
2308.1292 | 611.7058 | 514.3421 | 598.1141 | 523.0054
2309.1292 | 611.7044 | 513.5294 | 595.6519 | 520.3067
2310.1292 | 611.4094 | 517.0581 | 600.0311 | 522.3587
2311.1292 | 610.7847 | 515.3593 | 595.9238 | 520.4112
2312.1292 | 609.8652 | 514.8906 | 607.4137 | 519.3853
2313.1292 | 609.9367 | 514.0217 | 607.0599 | 527.0386
2314.1292 | 609.3623 | 513.3435 | 599.384 | 525.5762
2315.1292 | 610.0334 | 515.4653 | 600.1609 | 522.8234
2316.1292 | 609.4786 | 516.2127 | 595.6607 | 518.9291
2317.1292 | 609.0086 | 515.5307 | 591.9009 | 516.4814
2318.1292 | 608.1479 | 516.0225 | 588.8201 | 514.445
2319.1292 | 608.6278 | 515.7159 | 593.2302 | 515.1609
2320.1292 | 608.2957 | 517.5928 | 593.8315 | 514.0165
2321.1292 | 607.708 | 517.3102 | 610.7907 | 512.107
2322.1292 | 607.3077 | 518.1324 | 621.8541 | 507.6051
2323.1292 | 607.8056 | 519.2678 | 622.3042 | 510.9625
2324.1292 | 607.8203 | 521.109 | 625.4622 | 518.85
2325.1292 | 608.2664 | 521.6814 | 619.614 | 522.1948
2326.1292 | 607.8229 | 521.1467 | 612.0367 | 519.3715
2327.1292 | 607.1331 | 519.941 | 607.1775 | 518.6152
2328.1292 | 607.1111 | 521.4138 | 602.9798 | 515.7919
2329.1292 | 606.9227 | 520.9734 | 598.3068 | 512.4327
2330.1292 | 608.0442 | 519.6861 | 606.8236 | 511.7762
2331.1292 | 609.1935 | 520.0458 | 604.3227 | 510.4284
2332.1292 | 609.729 | 520.0014 | 600.0675 | 506.7006
2333.1292 | 609.3499 | 519.3871 | 593.98 | 505.2624
2334.1448 | 608.8281 | 516.9181 | 588.7009 | 505.5341
2335.1292 | 609.326 | 516.2105 | 586.9563 | 505.0701
2336.1292 | 609.0988 | 517.0784 | 585.2875 | 503.5806
2337.1448 | 608.6972 | 517.1267 | 582.4413 | 502.7952
2338.1292 | 608.1344 | 516.7104 | 579.6449 | 502.3268
2339.1292 | 608.4986 | 515.325 | 576.3986 | 500.0672
2340.1292 | 608.5505 | 514.5033 | 576.0982 | 499.4145
2341.1292 | 608.2833 | 514.3525 | 574.6814 | 501.9462
2342.1292 | 607.9322 | 513.7405 | 575.2832 | 501.4858
2343.1292 | 609.0979 | 511.6445 | 573.2003 | 500.4604
2344.1292 | 610.4181 | 514.4611 | 575.6994 | 498.8734
2345.1292 | 610.2541 | 514.3343 | 574.4539 | 501.1413
2346.1292 | 611.4623 | 515.8154 | 573.6344 | 502.9497
2347.1292 | 611.2798 | 517.9262 | 576.815 | 502.1189
2348.1292 | 610.7457 | 516.8479 | 575.7911 | 499.1965
2349.1292 | 610.8091 | 517.7016 | 580.3709 | 500.5936
2350.1292 | 610.1416 | 517.6331 | 581.7273 | 500.7289
2351.1292 | 610.1835 | 524.1465 | 589.9959 | 502.4253
2352.1292 | 610.7913 | 528.0272 | 590.8597 | 502.5224
2353.1292 | 613.6644 | 530.7704 | 592.1833 | 503.2538
2354.1292 | 614.3717 | 529.4619 | 590.107 | 503.0056
2355.1292 | 613.302 | 529.8025 | 588.7115 | 503.6672
2356.1292 | 613.5522 | 529.1155 | 587.8745 | 505.8815
2357.1292 | 613.4281 | 537.1146 | 595.4732 | 515.5559
2358.1292 | 615.0315 | 542.9216 | 597.9303 | 515.9925
2359.1292 | 614.9456 | 541.2543 | 594.6254 | 514.3264
2360.1292 | 615.6489 | 538.664 | 593.6733 | 514.3588
2361.1292 | 615.8333 | 540.1136 | 592.3566 | 513.5641
2362.1448 | 616.3273 | 538.5843 | 593.0438 | 514.7428
2363.1292 | 617.7496 | 551.943 | 592.6546 | 531.2429
2364.1448 | 616.2006 | 550.1209 | 590.8436 | 532.7645
2365.1292 | 617.2489 | 555.8017 | 590.7217 | 530.6918
2366.1448 | 616.9626 | 555.0344 | 586.5293 | 529.6208
2367.1292 | 616.9227 | 552.6522 | 583.2786 | 533.4391
2368.1292 | 616.9616 | 551.3011 | 579.8708 | 531.3266
2369.1292 | 616.0293 | 548.8076 | 576.2951 | 529.9256
2370.1292 | 615.9756 | 547.8573 | 580.5139 | 529.5607
2371.1292 | 616.5434 | 547.1422 | 585.072 | 532.112
2372.1292 | 616.0268 | 545.6634 | 581.2475 | 531.4307
2373.1292 | 616.2954 | 542.7823 | 576.456 | 528.7999
2374.1448 | 616.5276 | 539.0987 | 572.5529 | 526.0029
2375.1292 | 615.658 | 536.1756 | 569.7242 | 524.3866
2376.1292 | 615.0377 | 534.5319 | 569.2182 | 524.3009
2377.1292 | 615.1788 | 532.6832 | 572.885 | 521.8551
2378.1292 | 614.5591 | 531.5623 | 571.0843 | 522.6124
2379.1292 | 614.3348 | 535.9934 | 572.5702 | 523.5616
2380.1292 | 614.8483 | 534.8502 | 570.7754 | 522.9267
2381.1292 | 614.2714 | 534.1257 | 567.3856 | 520.8872
2382.1292 | 613.9292 | 532.7175 | 566.4098 | 520.2299
2383.1292 | 612.9948 | 531.3969 | 567.2019 | 520.7573
2384.1292 | 612.6884 | 534.9013 | 572.2956 | 521.1601
2385.1292 | 612.1718 | 536.1059 | 579.5638 | 525.2725
2386.1292 | 613.0071 | 537.6749 | 581.0692 | 526.6667
2387.1292 | 615.4087 | 540.8944 | 583.3531 | 531.0143
2388.1292 | 616.1652 | 541.5097 | 581.0371 | 529.4128
2389.1292 | 616.5832 | 542.5458 | 582.0809 | 530.7253
2390.1292 | 616.6013 | 541.4912 | 580.4249 | 530.5729
2391.1292 | 616.9146 | 539.575 | 580.0297 | 531.3603
2392.1292 | 617.6757 | 538.0464 | 579.47 | 531.1821
2393.1292 | 618.1041 | 538.3898 | 579.4704 | 532.6242
2394.1292 | 618.3644 | 537.7577 | 578.6853 | 532.1945
2395.1292 | 618.7499 | 536.2376 | 577.3974 | 531.098
2396.1292 | 618.7355 | 534.1092 | 575.9957 | 531.5551
2397.1448 | 619.1461 | 535.2119 | 578.0585 | 532.1307
2398.1292 | 619.3286 | 536.5355 | 577.593 | 529.4419
2399.1292 | 619.1181 | 535.0956 | 582.9325 | 527.3986
2400.1292 | 619.3576 | 540.4267 | 598.9954 | 525.1114
2401.1292 | 618.9472 | 546.941 | 600.2882 | 524.9915
2402.1292 | 618.0861 | 552.3347 | 603.7239 | 527.8745
2403.1292 | 618.1188 | 562.1237 | 602.4723 | 534.6428
2404.1292 | 616.6068 | 565.3177 | 599.9277 | 533.9215
2405.1292 | 615.1288 | 566.0508 | 597.6146 | 534.9384
2406.1292 | 614.6426 | 566.5184 | 598.9288 | 535.2562
2407.1292 | 614.8544 | 568.1758 | 608.1496 | 537.0672
2408.1292 | 615.0618 | 571.3952 | 606.2374 | 539.6584
2409.1292 | 616.1258 | 574.7575 | 607.5138 | 539.3831
2410.1292 | 616.4936 | 573.129 | 607.902 | 542.0302
2411.1292 | 617.299 | 571.2792 | 604.233 | 556.7864
2412.1292 | 618.5495 | 575.9067 | 607.8709 | 569.8641
2413.1292 | 619.0695 | 576.6024 | 605.7422 | 565.3663
2414.1292 | 619.1718 | 573.9046 | 600.0365 | 561.7865
2415.1292 | 619.3489 | 571.2785 | 595.8243 | 558.4957
2416.1292 | 619.642 | 568.9492 | 599.2724 | 553.2394
2417.1292 | 618.8238 | 567.2504 | 595.9348 | 551.9189
2418.1292 | 619.4 | 565.4383 | 593.1486 | 548.6323
2419.1292 | 619.3701 | 569.3137 | 595.5813 | 548.02
2420.1292 | 619.6569 | 566.7809 | 595.1874 | 547.64
2421.1292 | 620.5589 | 568.9347 | 594.3716 | 547.2724
2422.1292 | 620.9851 | 568.5011 | 592.6161 | 545.2201
2423.1292 | 620.4154 | 564.2213 | 589.2206 | 545.5995
2424.1292 | 620.5498 | 562.1226 | 587.5724 | 542.3359
2425.1292 | 620.7054 | 558.3384 | 586.0446 | 542.4489
2426.1292 | 620.9697 | 557.1858 | 584.3877 | 542.1838
2427.1292 | 619.873 | 554.054 | 582.0592 | 539.5346
2428.1292 | 619.7683 | 552.9659 | 580.5263 | 537.7158
2429.1292 | 620.4083 | 551.9197 | 580.7284 | 539.6182
2430.1292 | 620.6203 | 552.9991 | 583.4922 | 538.4441
2431.1292 | 621.7573 | 555.1183 | 584.3607 | 551.3647
2432.1292 | 621.3869 | 554.599 | 583.9138 | 550.3702
2433.1292 | 621.5347 | 552.6899 | 581.0659 | 547.0539
2434.1292 | 622.1213 | 551.8533 | 580.771 | 545.9945
2435.1292 | 622.3638 | 550.622 | 577.3329 | 544.384
2436.1292 | 622.8398 | 551.0623 | 584.8059 | 553.1113
2437.1292 | 622.8598 | 550.0702 | 588.7849 | 550.9868
2438.1292 | 623.5789 | 556.9381 | 588.9464 | 549.6165
2439.1292 | 624.1462 | 560.0199 | 590.466 | 550.3243
2440.1292 | 623.8535 | 563.5645 | 591.6842 | 548.3656
2441.1292 | 624.8016 | 567.7152 | 593.9974 | 555.5888
2442.1292 | 625.4628 | 564.8497 | 590.4283 | 554.0646
2443.1292 | 624.9972 | 563.5785 | 587.6148 | 549.9245
2444.1292 | 624.4554 | 563.604 | 585.5376 | 563.6546
2445.1292 | 624.4011 | 561.4313 | 585.7313 | 581.5958
2446.1292 | 624.6531 | 562.7959 | 585.7618 | 589.3354
2447.1292 | 625.9427 | 561.665 | 585.6242 | 586.6307
2448.1292 | 626.3461 | 562.5975 | 585.3926 | 582.9703
2449.1292 | 626.4595 | 565.8115 | 588.0551 | 578.7341
2450.1292 | 626.8968 | 566.2171 | 587.7705 | 575.0988
2451.1292 | 629.081 | 567.3177 | 588.0241 | 575.0574
2452.1292 | 629.1111 | 565.6835 | 588.7501 | 572.9443
2453.1292 | 629.2135 | 567.2566 | 586.8822 | 568.7876
2454.1292 | 626.8036 | 579.1438 | 589.8683 | 567.8544
2455.1292 | 627.0867 | 579.7526 | 595.3825 | 576.0001
2456.1292 | 627.7029 | 584.5944 | 600.806 | 575.2336
2457.1448 | 628.2751 | 586.6505 | 598.7653 | 569.6245
2458.1292 | 627.8949 | 583.8639 | 598.278 | 567.1966
2459.1292 | 627.5801 | 580.8721 | 594.1532 | 574.8554
2460.1292 | 628.1089 | 578.4012 | 595.6268 | 592.2439
2461.1292 | 628.7542 | 578.7795 | 598.4473 | 600.4721
2462.1292 | 627.1004 | 575.4114 | 595.9705 | 595.2976
2463.1292 | 626.4863 | 577.3877 | 603.8466 | 601.0302
2464.1292 | 626.0752 | 580.2623 | 598.0351 | 597.2016
2465.1292 | 626.8945 | 581.0075 | 602.9409 | 599.0338
2466.1292 | 626.7571 | 583.7113 | 604.4763 | 593.9975
2467.1292 | 627.6925 | 583.8178 | 603.8026 | 601.7432
2468.1292 | 628.6804 | 581.277 | 599.6918 | 598.8089
2469.1292 | 628.9829 | 578.5731 | 596.5779 | 595.4642
2470.1292 | 630.5509 | 578.5677 | 597.185 | 593.0969
2471.1448 | 630.7493 | 577.5095 | 593.4396 | 588.5714
2472.1292 | 631.7923 | 578.1513 | 591.4565 | 582.6294
2473.1292 | 631.7795 | 579.6519 | 590.7772 | 578.5199
2474.1292 | 631.8353 | 578.2905 | 588.6516 | 577.1896
2475.1292 | 632.0413 | 577.8778 | 587.3623 | 576.8259
2476.1292 | 630.8075 | 577.4976 | 591.4732 | 578.1986
2477.1292 | 630.2694 | 579.3151 | 592.0781 | 579.2299
2478.1292 | 631.3244 | 587.6008 | 591.4774 | 579.4927
2479.1292 | 632.2187 | 593.3154 | 593.9181 | 576.1235
2480.1292 | 632.2825 | 592.9996 | 595.011 | 576.4594
2481.1292 | 632.6367 | 592.2913 | 595.3811 | 585.1769
2482.1292 | 632.6415 | 588.2501 | 593.5448 | 583.1205
2483.1292 | 631.4348 | 585.4199 | 592.5363 | 583.0259
2484.1292 | 631.3578 | 584.0053 | 592.4867 | 582.0033
2485.1292 | 628.5397 | 588.1003 | 591.0063 | 580.6981
2486.1292 | 628.2026 | 586.3575 | 589.1822 | 577.0776
2487.1448 | 628.7724 | 590.1193 | 588.3288 | 572.8259
2488.1292 | 629.2629 | 587.6106 | 586.8085 | 571.4372
2489.1292 | 629.8195 | 583.812 | 586.7631 | 569.9436
2490.1292 | 629.8546 | 582.6065 | 585.8417 | 571.0315
2491.1292 | 629.8809 | 578.5209 | 584.4782 | 572.2965
2492.1292 | 630.244 | 578.2256 | 586.876 | 570.6767
2493.1292 | 630.7766 | 579.2089 | 589.8525 | 572.4538
2494.1292 | 631.4891 | 577.4564 | 589.6242 | 571.2887
2495.1292 | 631.2324 | 577.075 | 589.57 | 569.7494
2496.1292 | 633.8875 | 575.2574 | 588.7289 | 569.5212
2497.1292 | 633.882 | 575.6734 | 587.8227 | 568.7403
2498.1292 | 633.1806 | 574.1415 | 589.3403 | 567.3457
2499.1292 | 634.1482 | 577.6392 | 594.0701 | 573.8097
2500.1292 | 635.3721 | 581.7719 | 595.7853 | 573.0299
2501.1292 | 635.091 | 583.9804 | 594.4052 | 571.1909
2502.1292 | 635.0913 | 584.7191 | 598.6376 | 575.3143
2503.1292 | 635.8241 | 587.4676 | 597.8428 | 577.162
2504.1292 | 635.8034 | 586.758 | 597.4478 | 575.5943
2505.1292 | 635.7733 | 588.6827 | 597.035 | 575.1293
2506.1292 | 636.5209 | 588.5431 | 597.141 | 574.5453
2507.1292 | 636.7058 | 589.1509 | 598.6121 | 575.2396
2508.1292 | 637.2239 | 589.5946 | 599.6036 | 578.0309
2509.1292 | 637.0666 | 589.4456 | 599.4337 | 578.9706
2510.1292 | 637.2528 | 587.7981 | 598.7024 | 579.2659
2511.1292 | 637.2849 | 593.1114 | 597.359 | 584.7692
2512.1292 | 637.3588 | 590.9974 | 598.3178 | 584.2447
2513.1292 | 636.4295 | 591.4792 | 599.3315 | 581.0402
2514.1292 | 636.4191 | 593.5402 | 600.4645 | 593.5672
2515.1292 | 635.9751 | 591.7181 | 600.2247 | 608.1795
2516.1292 | 636.2979 | 595.4442 | 600.6097 | 607.0896
2517.1292 | 635.9591 | 599.0357 | 601.9569 | 599.7092
2518.1292 | 636.1004 | 596.5361 | 613.9131 | 596.5144
2519.1292 | 636.2279 | 594.2952 | 610.6098 | 605.9386
2520.1292 | 635.3342 | 591.2818 | 606.4744 | 606.2967
2521.1292 | 634.7287 | 594.542 | 606.3123 | 610.7985
2522.1292 | 635.2547 | 598.4232 | 617.4776 | 610.4259
2523.1292 | 636.691 | 597.0281 | 618.8246 | 608.2608
2524.1292 | 636.4702 | 596.8654 | 616.6028 | 603.8625
2525.1292 | 637.6054 | 596.3966 | 613.7826 | 605.9504
2526.1292 | 637.2694 | 599.2429 | 612.536 | 604.3782
2527.1292 | 635.8388 | 598.6155 | 608.6647 | 599.6881
2528.1292 | 636.4839 | 604.2149 | 614.7486 | 597.6208
2529.1292 | 635.3816 | 605.8055 | 622.294 | 609.6427
2530.1292 | 635.4697 | 612.6508 | 631.5748 | 605.9404
2531.1292 | 635.0437 | 611.0127 | 627.6685 | 605.409
2532.1292 | 635.0657 | 608.2109 | 623.0517 | 604.1636
2533.1292 | 634.5751 | 605.8046 | 618.4671 | 599.7526
2534.1292 | 634.5112 | 601.1999 | 614.0792 | 594.7038
2535.1292 | 635.4927 | 599.8277 | 612.4939 | 589.8247
2536.1292 | 636.0894 | 598.9589 | 611.485 | 588.9411
2537.1292 | 636.0834 | 597.4827 | 614.3024 | 595.3334
2538.1292 | 637.0476 | 596.1392 | 611.5196 | 595.0171
2539.1292 | 638.2679 | 600.9169 | 609.2017 | 596.2168
2540.1292 | 638.6593 | 605.1497 | 612.0492 | 594.9902
2541.1292 | 638.7827 | 606.7464 | 609.6327 | 594.2064
2542.1292 | 639.6551 | 607.1561 | 605.8154 | 588.8929
2543.1292 | 638.7596 | 606.7106 | 604.4206 | 590.1749
2544.1292 | 638.7149 | 602.8765 | 602.249 | 593.0159
2545.1292 | 639.0145 | 608.8636 | 604.1654 | 592.1325
2546.1292 | 639.6331 | 605.1085 | 602.5692 | 588.4225
2547.1292 | 639.2558 | 603.9794 | 602.2286 | 597.7711
2548.1292 | 640.1384 | 604.4361 | 603.061 | 598.4529
2549.1292 | 640.06 | 604.1196 | 604.7777 | 600.7903
2550.1292 | 640.1088 | 603.1001 | 603.5239 | 615.4858
2551.1292 | 639.8984 | 602.5525 | 603.1019 | 619.8649
2552.1292 | 639.8165 | 601.0251 | 600.9473 | 614.7339
2553.1292 | 640.0654 | 604.2281 | 600.508 | 612.4836
2554.1292 | 639.6603 | 614.526 | 612.4582 | 622.9927
2555.1292 | 640.2692 | 627.5392 | 619.5242 | 623.7664
2556.1292 | 641.1733 | 624.1111 | 614.4127 | 621.6345
2557.1292 | 640.5155 | 620.5562 | 611.253 | 628.1235
2558.1292 | 640.467 | 617.1954 | 606.388 | 627.2766
2559.1292 | 640.2752 | 619.2144 | 602.257 | 618.0065
2560.1292 | 640.2983 | 613.6787 | 600.3038 | 611.358
2561.1292 | 639.7192 | 618.1288 | 600.4183 | 605.1877
2562.1292 | 640.8636 | 618.2681 | 601.1344 | 605.0762
2563.1292 | 641.2541 | 619.7743 | 602.5996 | 603.9624
2564.1292 | 641.7152 | 627.9867 | 603.2354 | 600.642
2565.1292 | 641.9189 | 633.0004 | 602.5198 | 597.3405
2566.1292 | 640.9595 | 635.4842 | 602.0885 | 598.8423
2567.1292 | 640.519 | 637.9956 | 606.9683 | 601.0099
2568.1292 | 641.7628 | 634.9025 | 608.7762 | 607.1188
2569.1292 | 641.5255 | 631.5282 | 609.8948 | 603.2628
2570.1292 | 641.2067 | 628.079 | 608.4641 | 601.3164
2571.1292 | 641.1439 | 624.2016 | 604.7276 | 598.6959
2572.1292 | 640.8295 | 625.0266 | 608.4071 | 603.9461
2573.1292 | 639.9541 | 622.6772 | 608.0798 | 607.7905
2574.1292 | 640.4868 | 627.4321 | 607.7634 | 604.3792
2575.1292 | 640.6979 | 635.5266 | 611.5262 | 606.8423
2576.1292 | 642.2497 | 633.325 | 613.2168 | 605.0959
2577.1292 | 642.4159 | 637.8049 | 613.9219 | 608.2874
2578.1292 | 642.9532 | 640.6099 | 622.4751 | 625.4551
2579.1292 | 641.6105 | 631.7188 | 617.7554 | 628.4114
2580.1292 | 640.8093 | 635.6578 | 616.9092 | 622.6594
2581.1292 | 640.625 | 638.7701 | 618.8979 | 621.5581
2582.1292 | 641.3267 | 638.5412 | 616.3747 | 613.4314
2583.1292 | 640.6888 | 638.6726 | 616.0623 | 614.2131
2584.1292 | 640.2207 | 633.0956 | 621.9822 | 613.9556
2585.1292 | 640.0355 | 631.7458 | 630.5344 | 627.6194
2586.1292 | 640.9542 | 631.6513 | 629.1498 | 634.3271
2587.1292 | 640.5566 | 639.031 | 626.5014 | 634.9143
2588.1292 | 639.5992 | 646.5537 | 628.1682 | 630.845
2589.1292 | 639.0226 | 649.7832 | 639.1573 | 631.9958
2590.1292 | 639.1271 | 648.2442 | 633.3564 | 629.6133
2591.1292 | 639.6197 | 647.7332 | 628.0105 | 622.1925
2592.1292 | 639.4108 | 649.6073 | 623.6624 | 619.9941
2593.1292 | 639.9626 | 655.8889 | 630.9553 | 619.2411
2594.1292 | 639.6027 | 653.8859 | 624.4816 | 631.7904
2595.1292 | 640.0962 | 651.4527 | 620.9103 | 621.4089
2596.1292 | 639.8923 | 643.0837 | 616.8184 | 616.3533
2597.1292 | 639.1708 | 636.0497 | 613.6513 | 610.9123
2598.1292 | 639.3099 | 639.6262 | 614.0483 | 609.0053
2599.1448 | 639.2794 | 637.7702 | 616.0987 | 605.469
2600.1448 | 640.3253 | 639.0951 | 620.4949 | 614.9584
2601.1292 | 639.8099 | 635.9367 | 619.4128 | 624.2955
2602.1292 | 638.576 | 628.8212 | 613.8963 | 624.1772
2603.1448 | 638.3685 | 628.8538 | 611.8785 | 624.9657
2604.1448 | 638.148 | 630.3971 | 617.8591 | 630.2292
2605.1448 | 638.7794 | 628.711 | 626.2903 | 627.9369
2606.1292 | 638.4715 | 629.8427 | 619.9313 | 621.8003
2607.1292 | 638.942 | 627.0497 | 615.6157 | 624.7913
2608.1292 | 638.7351 | 624.7924 | 615.6381 | 622.4061
2609.1292 | 639.0157 | 623.3933 | 613.8367 | 628.5838
2610.1292 | 639.1964 | 621.5778 | 610.3638 | 630.8341
2611.1292 | 640.1447 | 619.9761 | 613.2242 | 647.3347
2612.1292 | 640.6965 | 620.2785 | 614.9437 | 644.1169
2613.1292 | 640.4534 | 622.0164 | 617.9451 | 639.0203
2614.1292 | 640.7338 | 628.1194 | 619.304 | 630.6649
2615.1292 | 640.3342 | 627.1875 | 631.6118 | 632.6109
2616.1292 | 640.5875 | 631.0577 | 634.2077 | 641.2053
2617.1292 | 640.8959 | 636.5084 | 636.6412 | 653.0731
2618.1292 | 642.3915 | 641.45 | 637.6751 | 646.3313
2619.1292 | 642.4489 | 644.8206 | 633.3791 | 636.3467
2620.1292 | 642.9415 | 642.2058 | 630.8826 | 631.421
2621.1292 | 643.2977 | 636.9939 | 627.067 | 636.5845
2622.1292 | 643.5468 | 638.3397 | 624.6053 | 635.1288
2623.1292 | 642.8419 | 640.4469 | 626.8299 | 630.0843
2624.1292 | 642.7943 | 645.7748 | 626.9981 | 628.1786
2625.1292 | 642.2927 | 645.0216 | 639.5353 | 623.7258
2626.1292 | 642.6724 | 649.5315 | 635.3139 | 623.3912
2627.1292 | 643.0405 | 655.4533 | 633.3869 | 625.4821
2628.1292 | 644.1925 | 658.3968 | 630.42 | 622.8173
2629.1292 | 644.0269 | 657.4445 | 632.4411 | 633.3806
2630.1292 | 643.6196 | 654.9522 | 648.8774 | 636.3521
2631.1292 | 644.588 | 656.4112 | 648.4316 | 636.917
2632.1292 | 644.8285 | 662.1469 | 643.0477 | 633.788
2633.1292 | 645.1068 | 657.0236 | 640.1218 | 630.4362
2634.1292 | 645.3519 | 654.9008 | 637.7377 | 628.6661
2635.1292 | 645.3861 | 660.9157 | 635.7063 | 628.7736
2636.1292 | 645.1754 | 667.5042 | 634.6127 | 626.5362
2637.1292 | 645.5116 | 670.3834 | 638.3999 | 623.7689
2638.1292 | 645.6937 | 672.5278 | 636.7742 | 625.0343
2639.1292 | 645.7693 | 669.7996 | 633.0964 | 621.0547
2640.1292 | 646.7684 | 666.949 | 633.601 | 620.1546
2641.1292 | 646.1749 | 670.1332 | 635.3348 | 619.188
2642.1292 | 645.0473 | 669.978 | 637.3597 | 618.5396
2643.1292 | 644.4515 | 676.4052 | 637.6216 | 615.3089
2644.1292 | 644.2754 | 674.8717 | 640.686 | 610.6491
2645.1292 | 644.957 | 678.8098 | 639.0414 | 609.0083
2646.1292 | 645.7688 | 677.5223 | 638.2148 | 620.4033
2647.1292 | 646.3197 | 671.8045 | 635.7359 | 617.8361
2648.1292 | 646.0684 | 667.9043 | 638.1852 | 621.8574
2649.1292 | 646.6016 | 671.2949 | 640.7816 | 618.0789
2650.1292 | 647.4609 | 670.4691 | 642.2206 | 616.3709
2651.1292 | 646.6577 | 669.9467 | 647.6094 | 617.4853
2652.1292 | 648.0494 | 675.5758 | 652.0963 | 619.1148
2653.1292 | 648.3043 | 674.2537 | 649.0904 | 627.4346
2654.1292 | 648.1702 | 674.1167 | 653.0971 | 635.5723
2655.1292 | 649.0412 | 678.054 | 660.4372 | 629.2284
2656.1292 | 649.189 | 676.4976 | 660.7827 | 633.6486
2657.1292 | 649.8963 | 673.0581 | 655.0478 | 643.1675
2658.1292 | 650.3165 | 668.7068 | 657.5177 | 643.5013
2659.1292 | 649.8417 | 665.2974 | 651.0362 | 649.0812
2660.1292 | 650.1431 | 666.5296 | 659.8403 | 650.7148
2661.1292 | 651.4502 | 666.2245 | 653.2119 | 642.4678
2662.1292 | 652.0821 | 660.5852 | 647.741 | 638.8291
2663.1292 | 651.8978 | 657.7093 | 643.2682 | 632.1054
2664.1292 | 651.1678 | 664.1763 | 639.428 | 628.6729
2665.1292 | 650.0938 | 664.0631 | 635.1416 | 622.2561
2666.1292 | 648.8048 | 669.4644 | 640.8745 | 620.6252
2667.1292 | 648.0544 | 665.7871 | 640.8844 | 618.3198
2668.1292 | 648.5444 | 665.4029 | 644.7996 | 616.2795
2669.1292 | 649.1441 | 672.6766 | 641.9117 | 617.3821
2670.1292 | 650.8448 | 668.137 | 639.7997 | 617.281
2671.1292 | 651.8608 | 675.4202 | 638.4921 | 622.3727
2672.1292 | 653.036 | 680.122 | 636.6703 | 618.1113
2673.1292 | 653.7685 | 677.0651 | 635.6333 | 615.6716
2674.1292 | 655.538 | 670.5588 | 635.8279 | 614.8855
2675.1292 | 655.3289 | 672.4184 | 638.6158 | 613.3618
2676.1292 | 654.3798 | 670.4564 | 634.1663 | 610.1513
2677.1292 | 654.1291 | 672.8509 | 633.1363 | 613.2519
2678.1292 | 654.405 | 675.9807 | 634.7848 | 610.1899
2679.1292 | 654.5305 | 675.5768 | 633.3032 | 614.9964
2680.1292 | 653.2805 | 666.869 | 627.9893 | 612.6557
2681.1292 | 652.2311 | 663.872 | 625.5177 | 608.2515
2682.1292 | 652.1505 | 662.997 | 624.1034 | 608.4247
2683.1292 | 653.0127 | 661.7192 | 623.8746 | 608.8158
2684.1292 | 654.3722 | 661.8694 | 624.1874 | 609.0232
2685.1292 | 652.3391 | 658.045 | 623.1272 | 608.8258
2686.1292 | 651.5673 | 664.6767 | 622.7785 | 608.2284
2687.1292 | 651.5393 | 666.6745 | 623.6369 | 610.5883
2688.1292 | 651.9353 | 677.7836 | 624.8162 | 609.1247
2689.1292 | 652.6537 | 676.6832 | 624.1547 | 605.6736
2690.1292 | 652.2034 | 676.9286 | 621.3581 | 601.1982
2691.1292 | 650.742 | 680.7295 | 623.0033 | 602.7911
2692.1292 | 649.9511 | 679.702 | 622.4738 | 605.4437
2693.1292 | 650.1598 | 674.1196 | 619.6862 | 599.9304
2694.1292 | 649.7244 | 670.8627 | 620.3463 | 599.6744
2695.1292 | 648.971 | 666.2559 | 618.8003 | 598.4556
2696.1292 | 649.153 | 669.9311 | 625.1321 | 599.585
2697.1292 | 648.4708 | 670.6581 | 630.7335 | 602.1156
2698.1292 | 648.2798 | 672.6213 | 632.2653 | 606.7784
2699.1292 | 647.9804 | 668.2198 | 639.2195 | 620.6955
2700.1292 | 648.5219 | 674.5828 | 638.8104 | 621.426
2701.1292 | 648.8731 | 671.6608 | 638.4789 | 621.962
2702.1292 | 649.007 | 675.4893 | 638.3551 | 626.2771
2703.1292 | 649.891 | 677.2793 | 636.8859 | 622.3329
2704.1292 | 650.94 | 676.7305 | 637.0786 | 632.7276
2705.1292 | 651.804 | 681.3131 | 644.0922 | 634.2384
2706.1292 | 652.5746 | 679.6943 | 642.9731 | 630.8728
2707.1292 | 652.9901 | 675.0449 | 639.4995 | 625.0569
2708.1292 | 652.4393 | 670.2684 | 636.6331 | 618.471
2709.1292 | 652.2672 | 669.8302 | 632.2908 | 615.9882
2710.1292 | 652.1763 | 671.0171 | 630.26 | 615.5503
2711.1292 | 651.3209 | 666.7773 | 629.4573 | 613.2475
2712.1292 | 651.5696 | 665.8928 | 629.0772 | 611.2034
2713.1292 | 651.3035 | 671.9404 | 631.9516 | 611.4441
2714.1292 | 651.2299 | 669.3956 | 631.4039 | 611.1014
2715.1292 | 651.1823 | 672.4027 | 634.6402 | 610.4566
2716.1292 | 650.6892 | 677.3348 | 644.4986 | 611.4268
2717.1292 | 650.3781 | 678.4367 | 650.154 | 613.2627
2718.1292 | 649.5563 | 678.8303 | 656.0705 | 617.5263
2719.1292 | 649.1052 | 677.8169 | 669.8117 | 626.5151
2720.1292 | 648.6664 | 677.207 | 664.6283 | 633.6636
2721.1292 | 648.4771 | 684.9804 | 658.4473 | 637.7305
2722.1292 | 648.3037 | 684.6164 | 657 | 638.269
2723.1292 | 647.8836 | 684.8428 | 661.3822 | 633.1118
2724.1292 | 648.5247 | 685.5015 | 658.4841 | 630.7853
2725.1292 | 648.8939 | 682.341 | 660.293 | 631.8655
2726.1292 | 649.2573 | 679.6929 | 662.8218 | 631.4497
2727.1292 | 649.0251 | 680.6131 | 662.7339 | 631.2256
2728.1292 | 649.7751 | 684.104 | 660.2572 | 628.4829
2729.1292 | 649.1326 | 680.3386 | 656.6083 | 627.6098
2730.1292 | 649.1075 | 682.7569 | 666.5091 | 634.8469
2731.1292 | 648.78 | 681.7703 | 670.1707 | 640.8773
2732.1292 | 648.749 | 682.8295 | 661.9367 | 637.0949
2733.1292 | 648.2407 | 683.3178 | 661.7472 | 637.403
2734.1292 | 648.3348 | 683.641 | 667.7951 | 642.079
2735.1292 | 648.1306 | 686.9569 | 669.967 | 644.3607
2736.1292 | 648.7756 | 697.2383 | 666.3294 | 654.2015
2737.1292 | 649.0248 | 693.3205 | 659.4815 | 643.2784
2738.1292 | 648.7315 | 690.2398 | 660.6225 | 645.943
2739.1292 | 646.8256 | 691.6208 | 658.4175 | 646.0429
2740.1292 | 646.204 | 694.3405 | 655.0155 | 640.1766
2741.1292 | 646.4248 | 695.6736 | 654.7141 | 633.8701
2742.1292 | 646.8288 | 698.6902 | 651.1584 | 631.678
2743.1292 | 647.2944 | 697.225 | 646.0552 | 627.5805
2744.1292 | 648.2529 | 693.9041 | 647.1557 | 631.0472
2745.1292 | 647.7673 | 697.3037 | 644.405 | 630.4802
2746.1292 | 647.596 | 699.4594 | 643.6844 | 634.4715
2747.1292 | 647.7191 | 697.5784 | 644.7961 | 641.1659
2748.1292 | 648.4156 | 693.4796 | 644.3199 | 650.0777
2749.1292 | 648.5343 | 693.1798 | 640.6077 | 640.9733
2750.1292 | 647.4047 | 691.9589 | 637.6855 | 646.0548
2751.1292 | 646.6113 | 694.3251 | 642.1471 | 645.6179
2752.1292 | 647.3175 | 689.6952 | 644.0879 | 646.0355
2753.1292 | 647.8527 | 696.3065 | 642.8056 | 642.6788
2754.1448 | 647.6568 | 694.8813 | 638.5288 | 635.9917
2755.1292 | 647.8784 | 697.1463 | 635.8549 | 629.8646
2756.1292 | 647.2621 | 690.5358 | 632.4445 | 626.3205
2757.1292 | 647.4015 | 686.6944 | 627.8951 | 622.8319
2758.1292 | 647.1008 | 678.2974 | 625.6708 | 628.2902
2759.1292 | 647.9738 | 682.3747 | 623.7212 | 623.4483
2760.1292 | 649.3506 | 683.5079 | 627.1114 | 619.2023
2761.1292 | 650.8628 | 682.2105 | 633.9608 | 617.7851
2762.1292 | 651.3672 | 685.4411 | 632.9948 | 614.733
2763.1292 | 651.2776 | 686.73 | 640.1411 | 616.1355
2764.1292 | 650.0225 | 685.881 | 635.0459 | 631.6058
2765.1448 | 649.9841 | 691.0812 | 631.5551 | 639.8423
2766.1292 | 650.2687 | 683.7904 | 628.7381 | 631.104
2767.1292 | 650.2189 | 688.8341 | 627.1301 | 642.3711
2768.1292 | 650.3832 | 694.6738 | 625.8979 | 637.7031
2769.1292 | 649.5122 | 692.2523 | 627.8297 | 630.8745
2770.1292 | 649.0854 | 691.1387 | 629.8359 | 630.8345
2771.1292 | 649.1126 | 689.2104 | 640.0502 | 647.4894
2772.1292 | 648.1482 | 693.4067 | 639.8179 | 649.5681
2773.1292 | 648.1647 | 693.6661 | 639.9111 | 656.7857
2774.1292 | 647.8603 | 686.001 | 636.0896 | 648.7528
2775.1292 | 647.1076 | 681.155 | 632.3926 | 640.7627
2776.1292 | 646.7703 | 674.6812 | 629.1887 | 635.2933
2777.1292 | 646.3068 | 677.1246 | 629.3637 | 632.511
2778.1292 | 646.3016 | 682.6914 | 629.0086 | 632.9492
2779.1292 | 646.7523 | 692.2533 | 630.9184 | 650.9387
2780.1448 | 645.9335 | 693.6292 | 630.6243 | 651.869
2781.1292 | 646.2623 | 695.1009 | 631.1663 | 648.0459
2782.1292 | 646.3062 | 688.4802 | 628.6238 | 640.489
2783.1292 | 646.0495 | 684.9571 | 626.3338 | 635.8359
2784.1292 | 645.6565 | 683.914 | 628.875 | 632.0799
2785.1292 | 645.6373 | 689.5576 | 627.25 | 629.1327
2786.1292 | 646.359 | 687.5303 | 631.3165 | 626.4032
2787.1292 | 645.4439 | 684.0466 | 627.7024 | 639.3824
2788.1292 | 643.685 | 680.8748 | 628.5445 | 654.147
2789.1292 | 644.2609 | 684.0758 | 628.7966 | 660.4088
2790.1292 | 644.8777 | 678.8501 | 626.1586 | 654.3178
2791.1292 | 645.318 | 676.3406 | 623.0074 | 647.9235
2792.1292 | 645.8272 | 675.7241 | 626.0534 | 643.7551
2793.1292 | 644.6844 | 668.567 | 623.3242 | 641.0097
2794.1292 | 645.8892 | 666.1496 | 623.5393 | 637.2154
2795.1292 | 644.4322 | 670.6789 | 634.7993 | 648.0413
2796.1292 | 644.3261 | 670.6981 | 639.0887 | 651.3406
2797.1292 | 644.0426 | 669.0014 | 632.4903 | 642.5857
2798.1292 | 644.6077 | 667.0623 | 629.3522 | 636.1629
2799.1292 | 645.1054 | 664.7099 | 626.8516 | 631.0058
2800.1292 | 645.7471 | 657.8924 | 622.0507 | 624.4696
2801.1292 | 644.8938 | 660.1417 | 621.941 | 640.3476
2802.1292 | 644.3521 | 655.6597 | 620.3121 | 645.8537
2803.1292 | 643.9346 | 665.8499 | 617.8788 | 641.2746
2804.1292 | 644.083 | 663.5722 | 618.5465 | 649.2469
2805.1292 | 644.3724 | 663.4096 | 616.2454 | 654.8272
2806.1292 | 644.6995 | 662.5492 | 621.4413 | 657.9576
2807.1292 | 645.0017 | 661.0509 | 623.2806 | 667.4752
2808.1292 | 644.7953 | 663.7659 | 628.5651 | 662.3309
2809.1292 | 644.3149 | 670.4997 | 630.1331 | 657.5337
2810.1292 | 644.1921 | 669.051 | 634.9278 | 664.8322
2811.1292 | 644.084 | 674.0132 | 633.9496 | 658.6967
2812.1292 | 644.1836 | 676.6458 | 638.1273 | 671.0564
2813.1292 | 644.2351 | 679.1531 | 642.7274 | 663.8987
2814.1292 | 644.4538 | 681.5103 | 643.6592 | 662.9019
2815.1292 | 644.8425 | 681.2611 | 644.0765 | 653.5287
2816.1292 | 644.8672 | 676.7776 | 641.9441 | 659.6636
2817.1292 | 644.7556 | 678.2521 | 649.6557 | 652.5003
2818.1292 | 644.6364 | 678.1125 | 645.6258 | 651.3163
2819.1292 | 644.4111 | 674.9518 | 640.6943 | 645.7776
2820.1292 | 644.4179 | 679.6723 | 645.0108 | 652.9112
2821.1292 | 644.6116 | 679.2008 | 642.2668 | 646.6625
2822.1292 | 643.9534 | 677.3824 | 637.5075 | 639.4104
2823.1292 | 644.3601 | 673.767 | 635.1752 | 636.813
2824.1292 | 644.1566 | 676.8524 | 631.3553 | 636.6423
2825.1292 | 644.9298 | 678.0515 | 638.216 | 646.8604
2826.1292 | 643.9 | 678.413 | 637.5591 | 645.9276
2827.1292 | 644.2852 | 680.9164 | 634.0992 | 642.8689
2828.1448 | 644.5682 | 681.9133 | 639.0341 | 642.3919
2829.1292 | 644.0286 | 675.4817 | 639.1315 | 641.7341
2830.1292 | 644.751 | 679.1818 | 644.8975 | 637.2292
2831.1292 | 644.5128 | 674.1372 | 642.01 | 632.899
2832.1292 | 645.4476 | 671.712 | 637.7459 | 630.6834
2833.1292 | 646.0227 | 669.0035 | 638.2283 | 632.4759
2834.1292 | 645.9332 | 666.2728 | 637.698 | 628.2603
2835.1292 | 646.2376 | 664.7832 | 636.9386 | 627.95
2836.1292 | 646.7271 | 663.5726 | 640.5352 | 643.8
2837.1292 | 646.1126 | 669.9649 | 645.8356 | 642.0048
2838.1292 | 646.3844 | 675.2899 | 650.8308 | 640.4387
2839.1292 | 646.234 | 676.7911 | 652.9458 | 659.4483
2840.1448 | 645.9823 | 680.2033 | 649.5958 | 651.5572
2841.1292 | 645.8241 | 684.9331 | 656.6327 | 647.987
2842.1292 | 645.9768 | 695.5986 | 668.6313 | 646.2435
2843.1292 | 645.5609 | 695.3177 | 669.1456 | 649.6781
2844.1292 | 645.2085 | 698.4192 | 680.0989 | 645.9718
2845.1292 | 644.4219 | 694.4569 | 682.421 | 640.8776
2846.1292 | 643.9643 | 693.5876 | 684.0059 | 638.054
2847.1292 | 643.755 | 696.5309 | 677.8736 | 637.4946
2848.1292 | 643.5214 | 695.53 | 679.1064 | 637.7937
2849.1292 | 642.7991 | 693.2669 | 679.6146 | 641.9845
2850.1292 | 643.1177 | 696.1427 | 681.1617 | 658.2487
2851.1292 | 643.4792 | 692.0267 | 674.4608 | 658.3632
2852.1292 | 644.6286 | 687.7798 | 668.6446 | 651.5044
2853.1292 | 644.7225 | 685.0334 | 662.4975 | 643.9304
2854.1292 | 645.1296 | 687.3835 | 662.2269 | 639.0636
2855.1292 | 645.4726 | 692.0685 | 659.1516 | 635.2281
2856.1292 | 645.2426 | 691.8374 | 655.4957 | 633.91
2857.1292 | 645.3884 | 693.2039 | 657.4379 | 633.3959
2858.1292 | 645.2866 | 695.0605 | 659.9681 | 634.7596
2859.1292 | 644.7358 | 695.2823 | 661.0195 | 633.1383
2860.1292 | 644.5106 | 700.9693 | 669.9062 | 647.2226
2861.1292 | 644.4478 | 703.6418 | 673.5381 | 653.9249
2862.1292 | 644.2011 | 709.1671 | 675.826 | 658.1027
2863.1292 | 643.89 | 709.1598 | 668.7111 | 653.3066
2864.1292 | 643.7339 | 700.9484 | 662.0393 | 645.5575
2865.1292 | 643.5574 | 701.4301 | 659.7831 | 644.428
2866.1292 | 644.0735 | 712.9704 | 656.9125 | 643.6139
2867.1292 | 643.675 | 705.9335 | 654.4047 | 657.0946
2868.1292 | 643.4671 | 707.9158 | 652.1867 | 650.7078
2869.1292 | 643.5936 | 700.3372 | 651.4079 | 661.7585
2870.1292 | 643.7087 | 698.4979 | 649.0397 | 653.8097
2871.1292 | 644.5329 | 687.5082 | 645.936 | 649.718
2872.1292 | 645.4489 | 679.654 | 643.3998 | 644.3736
2873.1292 | 645.5294 | 675.5236 | 640.3229 | 640.4296
2874.1292 | 645.1616 | 674.7953 | 638.232 | 637.0646
2875.1292 | 645.1017 | 681.4009 | 653.2374 | 632.5307
2876.1292 | 644.7523 | 683.5 | 664.1772 | 653.7781
2877.1292 | 645.005 | 682.0889 | 660.5519 | 661.3921
2878.1292 | 646.005 | 675.0227 | 656.454 | 660.9862
2879.1292 | 647.4203 | 670.3384 | 652.9617 | 655.9963
2880.1292 | 647.3261 | 674.1553 | 648.6587 | 648.4635
2881.1292 | 647.3115 | 676.5123 | 652.8524 | 643.6332
2882.1292 | 647.098 | 675.8974 | 660.8783 | 640.4858
2883.1292 | 647.5833 | 684.7731 | 657.8498 | 640.6577
2884.1292 | 647.7751 | 689.9164 | 660.2337 | 645.6773
2885.1292 | 647.3819 | 695.7503 | 660.9689 | 644.003
2886.1292 | 647.1506 | 701.6651 | 659.1684 | 653.9931
2887.1292 | 645.8395 | 698.4106 | 668.2491 | 645.2682
2888.1292 | 645.7964 | 695.9147 | 667.652 | 660.1701
2889.1292 | 645.7528 | 694.5406 | 662.4621 | 658.6051
2890.1292 | 646.9029 | 694.6413 | 663.4864 | 651.1504
2891.1292 | 646.2865 | 689.093 | 658.7886 | 642.4617
2892.1292 | 645.3406 | 690.6333 | 658.5602 | 636.2017
2893.1292 | 645.1043 | 693.7558 | 673.4414 | 644.8112
2894.1292 | 645.2275 | 696.983 | 675.3426 | 648.0567
2895.1292 | 644.702 | 692.514 | 669.9664 | 649.2297
2896.1292 | 644.7761 | 690.453 | 665.7143 | 652.2761
2897.1292 | 644.4571 | 690.4476 | 670.8008 | 663.0763
2898.1292 | 644.4852 | 693.76 | 672.9726 | 657.6556
2899.1292 | 644.6681 | 693.032 | 680.986 | 658.6762
2900.1448 | 644.7015 | 700.298 | 685.4088 | 670.1483
2901.1292 | 644.7399 | 698.069 | 687.8234 | 661.6748
2902.1292 | 644.7156 | 702.0977 | 686.7616 | 668.6053
2903.1292 | 644.8836 | 702.7053 | 689.2692 | 678.3756
2904.1292 | 644.8204 | 707.6428 | 684.7434 | 679.6563
2905.1292 | 644.5202 | 704.8566 | 684.502 | 683.0947
2906.1292 | 644.2209 | 705.3006 | 680.6332 | 674.3519
2907.1292 | 643.6773 | 702.1502 | 683.0014 | 674.6564
2908.1292 | 643.1475 | 704.8932 | 690.1503 | 672.5957
2909.1292 | 642.78 | 702.3244 | 687.3161 | 676.9618
2910.1292 | 642.3606 | 702.1939 | 687.2777 | 679.7153
2911.1292 | 642.1029 | 699.8229 | 687.4203 | 680.5418
2912.1292 | 641.686 | 698.78 | 685.7847 | 682.6857
2913.1292 | 642.4696 | 697.2052 | 679.2687 | 681.4192
2914.1292 | 642.2481 | 699.5251 | 674.4808 | 675.1367
2915.1292 | 642.2096 | 701.6281 | 670.3322 | 682.1957
2916.1292 | 642.1346 | 695.3665 | 678.7765 | 685.7834
2917.1292 | 642.1446 | 691.6779 | 672.9446 | 681.9375
2918.1292 | 642.3297 | 687.9657 | 681.0628 | 695.2693
2919.1292 | 641.8884 | 688.1456 | 678.2134 | 693.7951
2920.1292 | 640.8961 | 690.9012 | 681.2149 | 688.1146
2921.1292 | 641.3563 | 688.8343 | 678.7391 | 689.1321
2922.1292 | 641.1233 | 691.7404 | 680.3742 | 694.8484
2923.1292 | 640.9578 | 692.9394 | 673.3159 | 692.4986
2924.1292 | 641.0258 | 695.4844 | 672.8462 | 689.3787
2925.1292 | 642.5893 | 694.5628 | 670.9621 | 688.6059
2926.1292 | 642.7631 | 697.7053 | 671.754 | 685.855
2927.1292 | 641.7847 | 697.82 | 681.6947 | 676.1752
2928.1292 | 640.7176 | 696.7513 | 686.136 | 675.7011
2929.1292 | 638.9034 | 693.1791 | 685.1195 | 678.8176
2930.1292 | 638.8292 | 693.753 | 684.9467 | 674.4552
2931.1292 | 639.5412 | 700.6472 | 683.5724 | 679.4328
2932.1292 | 640.1949 | 701.8692 | 675.1375 | 675.8113
2933.1292 | 640.7449 | 698.3494 | 678.3689 | 671.8013
2934.1292 | 640.4673 | 695.8984 | 675.7221 | 676.181
2935.1292 | 640.9858 | 698.5175 | 677.8621 | 685.8591
2936.1292 | 641.6166 | 708.9018 | 680.9596 | 689.4578
2937.1292 | 641.8114 | 715.744 | 672.3922 | 679.6231
2938.1292 | 642.1097 | 714.4387 | 668.77 | 670.0183
2939.1292 | 642.3558 | 711.4351 | 663.2666 | 664.0808
2940.1292 | 642.6187 | 723.9427 | 662.3748 | 658.7667
2941.1292 | 641.6797 | 713.6168 | 661.3551 | 669.9308
2942.1292 | 641.3317 | 712.8217 | 670.1545 | 677.0713
2943.1292 | 640.9511 | 718.1936 | 673.2514 | 668.5944
2944.1292 | 641.2291 | 712.9616 | 674.7274 | 659.619
2945.1292 | 641.2687 | 713.2352 | 669.2819 | 663.8266
2946.1292 | 641.7087 | 711.4824 | 671.7512 | 659.3759
2947.1292 | 642.3173 | 706.0612 | 666.9326 | 655.3005
2948.1292 | 642.7172 | 702.2552 | 661.5139 | 653.0526
2949.1292 | 644.9792 | 704.1758 | 656.6033 | 645.9001
2950.1292 | 645.3814 | 701.9582 | 652.2275 | 640.8545
2951.1292 | 645.3237 | 704.4746 | 649.0238 | 638.0598
2952.1292 | 645.1876 | 710.4132 | 649.0943 | 633.0825
2953.1292 | 645.2088 | 707.3356 | 651.0201 | 630.9642
2954.1292 | 643.7823 | 707.3814 | 662.3278 | 628.1978
2955.1292 | 643.9431 | 707.9562 | 664.0222 | 633.1858
2956.1292 | 643.6417 | 714.6173 | 673.8104 | 640.2302
2957.1292 | 643.9746 | 716.4673 | 675.8873 | 651.3189
2958.1292 | 643.9406 | 723.3996 | 683.2044 | 654.8762
2959.1292 | 644.9549 | 720.0639 | 682.5053 | 654.2127
2960.1448 | 644.5704 | 715.6371 | 678.1498 | 653.4636
2961.1292 | 644.6266 | 710.4698 | 671.6592 | 648.2027
2962.1292 | 643.8453 | 712.5662 | 664.2265 | 650.6013
2963.1292 | 643.1791 | 704.3417 | 665.8695 | 656.6737
2964.1292 | 642.7185 | 707.0898 | 663.7499 | 655.9031
2965.1292 | 642.0542 | 704.7287 | 661.585 | 650.9903
2966.1292 | 642.4909 | 712.5067 | 668.2131 | 647.57
2967.1292 | 642.3283 | 714.5741 | 673.2537 | 646.648
2968.1292 | 642.4 | 713.2943 | 682.3068 | 653.5785
2969.1292 | 642.3162 | 713.1966 | 682.6655 | 660.4927
2970.1292 | 642.7522 | 708.8368 | 681.0307 | 665.2606
2971.1292 | 643.0727 | 705.5034 | 675.2329 | 665.4452
2972.1292 | 643.8312 | 704.4732 | 670.0224 | 662.3127
2973.1292 | 643.2482 | 701.0531 | 663.3292 | 664.1269
2974.1292 | 642.6108 | 700.2511 | 674.9024 | 677.5103
2975.1292 | 642.656 | 711.1565 | 668.6918 | 673.6707
2976.1292 | 642.3006 | 708.3776 | 667.6034 | 677.8522
2977.1292 | 641.3711 | 704.3179 | 662.3437 | 670.6506
2978.1292 | 640.3314 | 696.5422 | 660.6363 | 663.5394
2979.1292 | 640.6531 | 695.8546 | 655.5702 | 665.6097
2980.1292 | 642.1282 | 690.9489 | 652.4531 | 669.0177
2981.1292 | 642.5147 | 684.4096 | 647.4501 | 664.6067
2982.1292 | 642.8505 | 679.4522 | 643.4308 | 662.5559
2983.1292 | 642.849 | 674.8688 | 642.5264 | 665.4911
2984.1292 | 643.099 | 687.1786 | 646.8828 | 667.5784
2985.1292 | 643.3038 | 688.7971 | 646.3456 | 665.7345
2986.1292 | 643.1266 | 687.944 | 644.0898 | 665.1652
2987.1292 | 643.3092 | 687.7307 | 649.2256 | 664.1246
2988.1292 | 643.0587 | 686.6274 | 648.0535 | 663.2791
2989.1292 | 643.5371 | 697.1591 | 650.928 | 667.3741
2990.1292 | 643.3541 | 700.4466 | 654.4036 | 682.3256
2991.1292 | 643.2942 | 700.0089 | 665.6309 | 675.0794
2992.1292 | 643.1816 | 701.8561 | 665.9354 | 676.5478
2993.1292 | 642.6782 | 698.2853 | 660.4479 | 667.3399
2994.1292 | 642.6105 | 690.5269 | 661.406 | 657.529
2995.1292 | 642.1208 | 695.1865 | 665.6629 | 659.9025
2996.1292 | 641.578 | 693.3849 | 664.2486 | 664.1861
2997.1292 | 641.8521 | 690.4213 | 660.0348 | 666.7706
2998.1292 | 643.0953 | 684.5667 | 663.8101 | 672.9889
2999.1292 | 643.7306 | 677.6315 | 658.1364 | 671.2534
3000.1292 | 643.6826 | 671.4505 | 653.628 | 675.0771
3001.1292 | 644.6307 | 674.6655 | 651.692 | 676.4433
3002.1292 | 645.1537 | 677.0168 | 650.4555 | 674.2319
3003.1292 | 645.6111 | 681.8472 | 648.6418 | 667.5355
3004.1292 | 645.4192 | 687.6532 | 649.3694 | 666.9068
3005.1292 | 645.3738 | 687.631 | 652.005 | 659.7526
3006.1292 | 645.7357 | 696.6907 | 660.0672 | 655.0952
3007.1292 | 646.021 | 699.1847 | 659.9212 | 650.4141
3008.1292 | 645.7889 | 704.1643 | 666.2055 | 648.2453
3009.1292 | 645.2685 | 710.1981 | 677.8398 | 654.5945
3010.1292 | 644.4492 | 704.9033 | 678.955 | 650.4134
3011.1292 | 643.5635 | 701.6551 | 686.7511 | 657.6117
3012.1292 | 643.5202 | 700.3936 | 683.0153 | 657.8539
3013.1292 | 642.9346 | 700.02 | 685.4702 | 660.2532
3014.1292 | 642.656 | 696.8029 | 682.1043 | 652.4893
3015.1292 | 642.2767 | 694.9652 | 675.804 | 653.4683
3016.1292 | 641.961 | 691.6103 | 685.7274 | 658.5516
3017.1292 | 640.592 | 692.7076 | 677.6647 | 662.7565
3018.1292 | 640.6795 | 695.9592 | 684.8489 | 659.5427
3019.1292 | 640.6349 | 695.8174 | 687.1624 | 651.1034
3020.1448 | 641.0368 | 698.5966 | 681.2071 | 646.1878
3021.1292 | 641.5726 | 704.0878 | 675.9528 | 645.901
3022.1292 | 641.6519 | 715.4499 | 670.9549 | 653.8029
3023.1292 | 641.6393 | 709.3934 | 678.8019 | 657.4797
3024.1292 | 642.0457 | 710.4882 | 678.8115 | 657.3743
3025.1292 | 642.655 | 707.9803 | 681.666 | 659.3349
3026.1292 | 643.2294 | 707.6395 | 685.6507 | 667.4588
3027.1292 | 642.8755 | 711.9182 | 680.5886 | 672.7303
3028.1292 | 642.7809 | 711.5429 | 681.1565 | 668.8505
3029.1292 | 642.3562 | 714.4039 | 685.0042 | 668.2605
3030.1292 | 642.159 | 715.3009 | 681.7469 | 670.0902
3031.1292 | 642.4616 | 714.6101 | 681.3651 | 677.5223
3032.1292 | 643.3875 | 706.112 | 675.3282 | 674.8156
3033.1292 | 644.1832 | 697.7495 | 672.7752 | 675.0297
3034.1292 | 644.6843 | 688.9131 | 664.8531 | 663.9047
3035.1292 | 644.0712 | 690.2227 | 665.4917 | 668.0829
3036.1292 | 643.3538 | 684.1762 | 665.2416 | 672.9661
3037.1292 | 642.8593 | 682.1435 | 658.2376 | 675.5179
3038.1292 | 642.8442 | 676.1947 | 654.5887 | 673.5566
3039.1292 | 642.829 | 671.2496 | 659.6406 | 672.9429
3040.1292 | 642.6202 | 671.2472 | 655.4631 | 669.4149
3041.1292 | 642.5236 | 677.0225 | 663.479 | 672.7039
3042.1292 | 642.2985 | 681.1824 | 668.784 | 675.1634
3043.1292 | 641.9783 | 681.7367 | 670.3037 | 676.0333
3044.1292 | 642.5969 | 679.5373 | 673.4036 | 674.3761
3045.1292 | 645.0456 | 677.9563 | 668.5925 | 667.488
3046.1292 | 645.944 | 685.4056 | 663.8606 | 658.3899
3047.1292 | 645.8016 | 688.0286 | 669.3642 | 662.7832
3048.1292 | 645.1097 | 683.3682 | 667.5134 | 658.1484
3049.1292 | 644.8435 | 684.1386 | 672.2004 | 665.8996
3050.1292 | 644.7049 | 691.0278 | 676.5052 | 660.0981
3051.1292 | 644.209 | 700.4898 | 675.1418 | 666.6107
3052.1292 | 644.2349 | 695.6279 | 669.4984 | 673.2515
3053.1292 | 643.6557 | 694.0375 | 664.8887 | 669.0431
3054.1292 | 643.6938 | 691.071 | 669.3423 | 671.9491
3055.1292 | 643.2562 | 693.5612 | 666.5851 | 666.3327
3056.1292 | 643.3978 | 702.4618 | 679.7768 | 660.7595
3057.1292 | 642.3821 | 698.5147 | 672.5413 | 651.3625
3058.1292 | 642.3048 | 692.758 | 678.693 | 645.132
3059.1292 | 642.0107 | 692.0668 | 676.9688 | 656.8067
3060.1292 | 642.5072 | 703.0726 | 671.1829 | 659.3144
3061.1292 | 643.2872 | 702.2987 | 673.3018 | 659.0376
3062.1292 | 644.0177 | 703.1093 | 675.6511 | 656.6573
3063.1292 | 644.2706 | 711.6722 | 682.2863 | 651.6386
3064.1292 | 643.9948 | 708.3122 | 686.8673 | 658.0501
3065.1292 | 643.4947 | 708.044 | 685.7803 | 649.311
3066.1292 | 643.4859 | 710.0793 | 687.7903 | 656.1262
3067.1292 | 644.1371 | 711.3788 | 682.78 | 663.4887
3068.1292 | 645.2955 | 709.762 | 693.6543 | 665.7269
3069.1292 | 645.7365 | 708.014 | 698.5011 | 669.517
3070.1292 | 645.848 | 708.9126 | 693.175 | 668.0549
3071.1292 | 646.4342 | 705.9451 | 691.128 | 675.7955
3072.1292 | 646.9964 | 704.4132 | 703.764 | 677.4986
3073.1292 | 646.9185 | 714.4198 | 698.8327 | 675.479
3074.1292 | 646.3466 | 714.6353 | 694.493 | 677.1145
3075.1292 | 645.4166 | 710.0096 | 698.2126 | 678.052
3076.1292 | 645.2089 | 708.3432 | 697.5993 | 687.4467
3077.1292 | 644.2439 | 699.6089 | 686.4668 | 686.1214
3078.1292 | 645.5565 | 697.831 | 681.7108 | 690.1465
3079.1292 | 646.7562 | 695.5448 | 676.5058 | 687.5354
3080.1292 | 648.2776 | 697.7349 | 671.2058 | 676.4179
3081.1292 | 650.1954 | 701.0189 | 664.9412 | 675.4741
3082.1292 | 649.0638 | 698.5667 | 663.5565 | 681.6101
3083.1292 | 648.085 | 693.9988 | 657.8667 | 682.3998
3084.1292 | 646.9766 | 695.0467 | 668.8308 | 675.8621
3085.1292 | 647.3098 | 699.7684 | 672.7596 | 671.1347
3086.1292 | 648.2656 | 708.535 | 677.2199 | 671.4894
3087.1292 | 648.4613 | 704.5747 | 678.4355 | 673.7943
3088.1292 | 648.4615 | 706.3697 | 674.8808 | 674.6424
3089.1292 | 648.3581 | 704.3176 | 675.2395 | 678.4546
3090.1292 | 647.6186 | 697.6307 | 678.3019 | 679.2144
3091.1292 | 647.6769 | 699.5883 | 676.382 | 678.311
3092.1292 | 647.704 | 707.2071 | 676.2807 | 678.5145
3093.1292 | 648.9826 | 703.1038 | 666.8508 | 673.3327
3094.1292 | 649.0322 | 697.2433 | 661.7175 | 672.0774
3095.1292 | 650.2157 | 690.6971 | 659.2553 | 676.2726
3096.1292 | 650.2557 | 684.8468 | 663.5627 | 682.1718
3097.1292 | 651.0059 | 677.2509 | 657.1494 | 678.2187
3098.1292 | 651.0349 | 670.4495 | 653.1442 | 672.6529
3099.1292 | 651.7387 | 674.8513 | 651.6403 | 665.5755
3100.1292 | 653.4481 | 683.1418 | 652.3241 | 662.6274
3101.1292 | 654.3201 | 683.493 | 654.4357 | 660.4771
3102.1292 | 653.273 | 688.3726 | 668.2907 | 663.8354
3103.1292 | 652.233 | 686.267 | 680.621 | 664.0426
3104.1292 | 651.4013 | 682.1611 | 674.5706 | 661.9089
3105.1292 | 651.2187 | 686.6919 | 676.8462 | 667.4186
3106.1292 | 651.2854 | 683.1715 | 669.3812 | 676.7224
3107.1292 | 650.4358 | 677.7764 | 666.4379 | 680.1847
3108.1292 | 650.128 | 675.1573 | 663.8151 | 682.1288
3109.1292 | 650.1374 | 667.648 | 656.1435 | 686.5622
3110.1292 | 650.5181 | 665.4865 | 651.2132 | 681.6678
3111.1292 | 650.9093 | 665.8716 | 644.985 | 678.2103
3112.1292 | 651.8918 | 662.8917 | 642.6966 | 672.3721
3113.1292 | 652.3295 | 660.5298 | 644.1487 | 673.2905
3114.1292 | 652.8219 | 662.5144 | 640.4778 | 671.4218
3115.1292 | 652.2117 | 665.5822 | 648.0441 | 667.2886
3116.1292 | 651.3506 | 669.275 | 660.3302 | 676.3889
3117.1292 | 651.7664 | 673.5018 | 662.4505 | 677.8063
3118.1292 | 652.81 | 684.0199 | 659.5364 | 685.062
3119.1292 | 652.1862 | 680.5364 | 661.8254 | 686.8485
3120.1292 | 651.3986 | 683.1792 | 670.4337 | 684.2497
3121.1292 | 651.3284 | 687.5052 | 672.7207 | 683.3025
3122.1292 | 650.3829 | 685.8205 | 680.6622 | 683.7145
3123.1292 | 649.6323 | 679.9765 | 675.1322 | 672.6262
3124.1292 | 649.5073 | 675.9538 | 666.0474 | 660.6805
3125.1292 | 648.2795 | 686.5351 | 660.6495 | 662.2954
3126.1292 | 648.7857 | 677.1352 | 659.58 | 672.3926
3127.1292 | 648.5399 | 670.8195 | 653.9003 | 663.3202
3128.1292 | 649.3332 | 673.482 | 648.3967 | 656.8147
3129.1292 | 649.6568 | 672.7559 | 646.3047 | 669.564
3130.1292 | 649.2949 | 680.3738 | 648.5284 | 675.6256
3131.1292 | 648.9493 | 675.1703 | 656.033 | 674.6798
3132.1292 | 649.2909 | 670.5506 | 651.3839 | 672.1935
3133.1292 | 649.3428 | 665.204 | 647.3044 | 670.9904
3134.1292 | 649.6107 | 661.9161 | 643.7047 | 660.5719
3135.1292 | 649.338 | 658.6425 | 638.2148 | 651.9558
3136.1292 | 648.8428 | 656.1281 | 645.6139 | 653.7392
3137.1292 | 648.7838 | 661.0307 | 649.5022 | 659.3047
3138.1292 | 648.654 | 663.5598 | 652.035 | 667.15
3139.1292 | 648.507 | 659.3143 | 654.03 | 672.4034
3140.1292 | 648.2006 | 654.7753 | 647.1901 | 677.0254
3141.1292 | 647.3119 | 653.4311 | 652.1371 | 673.9131
3142.1292 | 648.3614 | 652.704 | 650.2984 | 668.0129
3143.1292 | 648.6553 | 659.1 | 661.06 | 671.8385
3144.1292 | 648.9725 | 670.2851 | 669.4727 | 671.2066
3145.1292 | 649.3128 | 671.1857 | 667.1108 | 673.389
3146.1292 | 648.5735 | 676.1941 | 671.3258 | 665.2988
3147.1292 | 648.3391 | 679.3316 | 671.8397 | 664.8172
3148.1292 | 647.7793 | 681.7333 | 676.336 | 672.4598
3149.1292 | 648.3328 | 687.8995 | 687.256 | 676.7164
3150.1292 | 647.5625 | 690.4493 | 687.9709 | 674.8698
3151.1292 | 647.4407 | 691.1653 | 690.9609 | 675.7465
3152.1292 | 647.0181 | 692.8848 | 686.4059 | 676.4622
3153.1292 | 647.2705 | 698.3215 | 684.955 | 673.6871
3154.1292 | 646.9838 | 699.7891 | 683.3415 | 676.9894
3155.1292 | 646.4531 | 695.1374 | 683.6213 | 673.3397
3156.1292 | 646.3979 | 698.061 | 688.0683 | 668.1277
3157.1292 | 646.2295 | 697.488 | 683.9296 | 665.152
3158.1292 | 645.6169 | 698.5063 | 684.6071 | 670.8825
3159.1292 | 645.387 | 698.2416 | 684.9491 | 675.5059
3160.1292 | 644.3892 | 699.92 | 695.7318 | 678.4435
3161.1292 | 644.9524 | 695.802 | 691.0235 | 671.9309
3162.1292 | 645.6778 | 691.4834 | 687.7528 | 665.5747
3163.1292 | 646.0837 | 687.6125 | 684.4284 | 665.7433
3164.1292 | 645.6712 | 683.7728 | 675.7384 | 665.6885
3165.1292 | 645.5498 | 685.9292 | 670.2714 | 670.8518
3166.1292 | 645.0486 | 696.6208 | 669.4787 | 674.054
3167.1292 | 644.9993 | 691.8748 | 672.1891 | 672.3882
3168.1292 | 643.9888 | 681.0743 | 664.3176 | 661.5725
3169.1292 | 643.8556 | 682.225 | 668.8537 | 654.5761
3170.1292 | 643.5335 | 675.6884 | 670.7651 | 661.0725
3171.1292 | 643.1326 | 672.015 | 674.2923 | 668.1216
3172.1292 | 642.4804 | 670.4104 | 670.0103 | 671.2916
3173.1292 | 642.2957 | 664.3547 | 677.8811 | 674.4442
3174.1292 | 642.4315 | 662.9504 | 678.3817 | 672.2326
3175.1292 | 643.1858 | 657.8331 | 679.9124 | 679.9482
3176.1292 | 643.8539 | 652.7239 | 676.0244 | 676.4701
3177.1292 | 644.1678 | 650.6231 | 667.7086 | 667.8724
3178.1292 | 645.0298 | 657.1182 | 663.4893 | 662.9754
3179.1292 | 644.9814 | 663.1401 | 659.7808 | 654.8902
3180.1292 | 644.4277 | 659.2126 | 663.0195 | 657.7696
3181.1292 | 644.4291 | 660.7501 | 665.3873 | 666.1283
3182.1292 | 644.1822 | 666.3929 | 666.944 | 661.3135
3183.1448 | 645.2813 | 668.8392 | 663.5453 | 658.5554
3184.1292 | 645.596 | 662.8029 | 660.8884 | 658.0704
3185.1292 | 645.3433 | 656.1496 | 657.0717 | 655.1774
3186.1292 | 645.044 | 654.0139 | 657.6838 | 655.6618
3187.1292 | 645.4153 | 651.2172 | 660.432 | 656.9458
3188.1292 | 645.974 | 659.5142 | 663.8742 | 655.4993
3189.1448 | 645.6281 | 657.848 | 664.0536 | 658.1109
3190.1292 | 645.3024 | 664.2467 | 662.7208 | 661.2997
3191.1292 | 644.7494 | 672.0592 | 666.0195 | 665.6665
3192.1292 | 644.2353 | 675.0696 | 672.4549 | 673.6402
3193.1292 | 644.0321 | 673.75 | 679.0891 | 672.0315
3194.1292 | 643.7166 | 677.5118 | 679.7102 | 674.9393
3195.1292 | 643.8048 | 675.7078 | 680.3959 | 681.4548
3196.1292 | 644.0543 | 671.6493 | 689.0803 | 682.5669
3197.1292 | 644.4736 | 676.8864 | 691.5844 | 690.8988
3198.1292 | 645.0591 | 671.6028 | 685.1894 | 683.5739
3199.1292 | 644.7989 | 674.569 | 682.2287 | 672.0591
3200.1448 | 645.454 | 681.16 | 680.685 | 666.1642
3201.1292 | 645.267 | 678.6348 | 676.1562 | 673.6327
3202.1292 | 644.5306 | 673.8035 | 682.1062 | 669.6825
3203.1292 | 644.5797 | 677.0174 | 677.5013 | 666.4897
3204.1292 | 644.5218 | 671.208 | 672.8187 | 671.6806
3205.1292 | 645.0286 | 672.2578 | 672.4007 | 668.5009
3206.1292 | 645.521 | 673.1465 | 673.1752 | 660.766
3207.1292 | 644.7851 | 675.1282 | 675.9034 | 660.736
3208.1292 | 643.8803 | 669.5019 | 666.655 | 673.4282
3209.1292 | 643.282 | 664.359 | 662.2751 | 683.1166
3210.1292 | 643.2036 | 658.9505 | 654.5953 | 677.2979
3211.1292 | 643.643 | 654.5664 | 653.7329 | 680.0867
3212.1292 | 644.3186 | 665.1297 | 652.7666 | 676.2726
3213.1292 | 645.0752 | 664.9352 | 653.5503 | 674.2051
3214.1292 | 645.1806 | 658.1602 | 653.2216 | 680.5805
3215.1292 | 645.0237 | 657.203 | 657.1485 | 677.4427
3216.1292 | 644.3032 | 653.1334 | 657.4347 | 676.0938
3217.1292 | 644.1982 | 651.2605 | 662.8218 | 681.2781
3218.1292 | 643.5229 | 647.5633 | 654.8326 | 688.8112
3219.1292 | 643.3222 | 646.2423 | 653.9133 | 694.7328
3220.1292 | 642.8446 | 643.455 | 650.1234 | 684.4793
3221.1292 | 642.236 | 651.4437 | 651.207 | 683.638
3222.1292 | 642.6419 | 661.628 | 655.1765 | 678.5119
3223.1292 | 642.4525 | 655.824 | 650.3788 | 676.3183
3224.1292 | 642.6276 | 649.4553 | 646.2157 | 666.5447
3225.1292 | 642.9668 | 648.4809 | 647.6855 | 667.0325
3226.1292 | 642.9919 | 645.4719 | 653.264 | 674.9976
3227.1292 | 643.0194 | 659.2973 | 657.4163 | 678.2733
3228.1292 | 642.2795 | 661.5525 | 669.9599 | 681.6012
3229.1292 | 641.386 | 660.9133 | 679.3235 | 682.5821
3230.1292 | 641.4135 | 663.6606 | 677.3372 | 674.8751
3231.1292 | 641.5585 | 670.6111 | 673.7924 | 670.1247
3232.1292 | 641.8227 | 668.0446 | 680.1858 | 670.5996
3233.1292 | 641.5484 | 677.7318 | 688.9286 | 666.6797
3234.1292 | 641.1543 | 681.5477 | 691.4472 | 658.9863
3235.1292 | 640.4387 | 674.0068 | 697.1602 | 656.5814
3236.1292 | 639.7328 | 668.4817 | 692.1229 | 649.9925
3237.1292 | 639.6858 | 662.8862 | 684.8306 | 651.4978
3238.1292 | 639.3317 | 658.6087 | 681.5099 | 655.3436
3239.1292 | 639.1572 | 655.8322 | 689.0688 | 658.0093
3240.1292 | 638.718 | 651.1706 | 695.8446 | 652.12
3241.1292 | 638.0962 | 652.5246 | 686.8268 | 653.7557
3242.1292 | 638.5304 | 650.4659 | 683.2313 | 668.6866
3243.1292 | 638.4952 | 648.8856 | 676.865 | 662.5418
3244.1292 | 638.0305 | 644.5429 | 667.9568 | 655.9489
3245.1292 | 638.0252 | 640.2212 | 660.6758 | 654.8391
3246.1292 | 638.4597 | 641.7142 | 661.0521 | 654.2217
3247.1292 | 638.2949 | 644.2483 | 656.7639 | 646.3646
3248.1292 | 637.8029 | 648.1693 | 652.3688 | 643.6574
3249.1292 | 637.4616 | 644.6761 | 647.2487 | 641.1414
3250.1292 | 637.2835 | 642.0567 | 647.2239 | 655.3647
3251.1292 | 637.5946 | 645.743 | 644.6956 | 656.6734
3252.1292 | 637.5808 | 649.0046 | 648.5235 | 660.6735
3253.1292 | 637.4739 | 644.9877 | 646.3028 | 669.478
3254.1292 | 637.547 | 643.1103 | 646.6026 | 669.735
3255.1292 | 637.4195 | 650.1539 | 654.8234 | 672.966
3256.1292 | 637.5389 | 649.3424 | 661.3092 | 669.5198
3257.1292 | 637.6072 | 652.5815 | 659.0467 | 663.1419
3258.1292 | 638.017 | 649.1023 | 672.0068 | 666.5025
3259.1292 | 637.8018 | 653.4742 | 675.2699 | 665.0082
3260.1292 | 637.8871 | 652.3366 | 677.0589 | 661.0343
3261.1292 | 637.537 | 648.7131 | 679.6805 | 668.6589
3262.1292 | 637.6062 | 647.7474 | 680.2352 | 666.7851
3263.1292 | 637.8432 | 652.1076 | 674.7877 | 669.7706
3264.1292 | 637.7967 | 651.4738 | 671.9807 | 667.8977
3265.1292 | 638.2696 | 654.8407 | 673.2532 | 665.1416
3266.1292 | 639.4853 | 655.7393 | 666.7246 | 666.6003
3267.1292 | 640.1707 | 650.0853 | 659.5938 | 660.5105
3268.1292 | 640.2888 | 645.0286 | 654.9982 | 658.1619
3269.1292 | 640.3559 | 642.1311 | 652.1863 | 650.3982
3270.1292 | 640.2285 | 642.1071 | 650.2426 | 645.37
3271.1292 | 640.0785 | 654.6748 | 653.3164 | 639.3946
3272.1292 | 640.2615 | 654.5228 | 654.2968 | 645.8482
3273.1292 | 640.2728 | 648.8266 | 650.2863 | 649.0858
3274.1292 | 640.0317 | 653.0534 | 650.5757 | 651.3063
3275.1292 | 640.4171 | 662.9362 | 659.1672 | 659.4485
3276.1292 | 640.8159 | 662.5138 | 659.1037 | 661.1097
3277.1292 | 640.9585 | 657.0484 | 661.1191 | 666.2621
3278.1292 | 641.0441 | 651.9602 | 662.0366 | 662.4722
3279.1292 | 640.8653 | 647.6573 | 658.0741 | 668.0528
3280.1292 | 641.1713 | 652.634 | 655.5819 | 666.9268
3281.1292 | 640.7604 | 649.7592 | 649.4168 | 669.7139
3282.1292 | 640.6031 | 657.3858 | 644.8967 | 672.5663
3283.1292 | 640.1828 | 649.1818 | 641.5363 | 675.0139
3284.1292 | 639.941 | 643.3664 | 639.9099 | 675.8331
3285.1292 | 639.5766 | 652.6917 | 645.1641 | 673.832
3286.1292 | 639.1774 | 651.1709 | 653.1369 | 671.8346
3287.1292 | 638.2489 | 645.1903 | 652.4347 | 674.0357
3288.1292 | 637.7162 | 652.0833 | 652.6939 | 669.3989
3289.1292 | 636.943 | 654.456 | 654.8831 | 657.3421
3290.1292 | 636.6516 | 650.2835 | 657.7442 | 662.1013
3291.1292 | 635.8659 | 645.3756 | 672.4715 | 661.5039
3292.1292 | 636.8099 | 647.6317 | 672.0635 | 662.6506
3293.1292 | 637.0979 | 656.1869 | 678.4287 | 657.8501
3294.1292 | 637.4069 | 652.1756 | 674.1707 | 664.7957
3295.1292 | 637.5959 | 648.7665 | 671.6148 | 671.5141
3296.1292 | 637.7999 | 645.9593 | 671.095 | 671.6285
3297.1292 | 637.8192 | 643.7381 | 668.2001 | 672.9901
3298.1292 | 638.4355 | 650.9461 | 665.6275 | 674.0745
3299.1292 | 638.8607 | 657.1451 | 661.4614 | 676.8384
3300.1292 | 638.5233 | 655.3698 | 654.4044 | 666.7754
3301.1292 | 637.8092 | 650.303 | 655.1262 | 661.281
3302.1292 | 637.3298 | 647.7475 | 657.3464 | 667.8857
3303.1292 | 637.5976 | 644.7105 | 661.5899 | 666.459
3304.1292 | 637.4808 | 649.6598 | 667.3498 | 660.3883
3305.1292 | 636.7377 | 649.5048 | 673.6852 | 658.5418
3306.1292 | 636.5144 | 647.3324 | 672.8756 | 658.7373
3307.1292 | 635.9879 | 643.1001 | 677.4178 | 662.1157
3308.1292 | 635.9676 | 643.4699 | 682.5119 | 655.0036
3309.1292 | 635.9857 | 644.9944 | 674.4755 | 666.4254
3310.1292 | 636.7859 | 640.2985 | 665.8981 | 657.3711
3311.1292 | 636.7972 | 637.1305 | 657.6625 | 650.3449
3312.1292 | 637.9924 | 635.5031 | 657.1636 | 640.8867
3313.1292 | 638.5536 | 631.9796 | 652.4439 | 641.8411
3314.1292 | 638.1916 | 628.7018 | 646.0741 | 645.9029
3315.1292 | 638.7115 | 628.2457 | 645.3558 | 653.8651
3316.1292 | 638.911 | 625.3866 | 642.2394 | 657.2681
3317.1292 | 639.3514 | 623.8929 | 641.1936 | 647.9057
3318.1292 | 639.1334 | 626.4738 | 637.6033 | 642.863
3319.1292 | 639.5584 | 623.9084 | 634.4914 | 634.6435
3320.1292 | 638.9389 | 626.9131 | 637.3468 | 634.0971
3321.1292 | 638.9136 | 633.8179 | 635.1275 | 630.1105
3322.1292 | 639.4772 | 637.595 | 635.4266 | 627.3171
3323.1292 | 640.4359 | 633.7265 | 634.2937 | 621.8194
3324.1292 | 640.8898 | 633.188 | 635.7311 | 626.1166
3325.1292 | 640.8586 | 631.3816 | 634.1647 | 622.5605
3326.1292 | 640.4847 | 627.6614 | 633.7271 | 634.484
3327.1292 | 639.9009 | 628.1937 | 637.2423 | 644.9582
3328.1292 | 639.4778 | 627.0135 | 640.9568 | 653.4324
3329.1292 | 638.5208 | 629.8749 | 635.1636 | 643.8229
3330.1292 | 637.9297 | 630.0165 | 643.263 | 637.068
3331.1292 | 638.1853 | 627.4772 | 643.389 | 637.8302
3332.1292 | 638.4375 | 624.5344 | 640.2626 | 633.266
3333.1292 | 639.0854 | 623.1185 | 638.1547 | 631.7027
3334.1292 | 639.3268 | 623.0178 | 638.7801 | 628.8917
3335.1292 | 639.7335 | 633.2317 | 638.2396 | 625.4848
3336.1292 | 639.4096 | 642.1518 | 641.5904 | 624.5506
3337.1292 | 639.2807 | 637.8412 | 639.9665 | 628.1903
3338.1292 | 638.76 | 634.4284 | 635.7845 | 632.0239
3339.1292 | 638.6606 | 631.5191 | 632.9695 | 632.2358
3340.1292 | 638.6928 | 627.3658 | 630.3056 | 626.6126
3341.1292 | 638.9313 | 626.9974 | 631.1451 | 624.8735
3342.1292 | 638.7641 | 645.6939 | 632.6317 | 624.5226
3343.1292 | 638.3585 | 649.9607 | 634.0131 | 633.543
3344.1292 | 637.756 | 647.1428 | 635.061 | 636.8618
3345.1292 | 636.9835 | 647.1501 | 639.4472 | 635.3593
3346.1292 | 636.3418 | 646.589 | 637.6996 | 649.6067
3347.1292 | 635.1426 | 650.5196 | 639.4029 | 651.4337
3348.1292 | 634.3938 | 644.5179 | 634.8561 | 639.3366
3349.1292 | 634.4022 | 636.2314 | 631.0125 | 631.5277
3350.1292 | 633.4947 | 629.5636 | 627.8657 | 625.6594
3351.1292 | 634.1989 | 627.2753 | 625.6924 | 620.8468
3352.1292 | 634.7887 | 631.7931 | 624.5492 | 623.5345
3353.1292 | 635.2036 | 631.4227 | 625.0906 | 635.0298
3354.1292 | 634.718 | 630.4094 | 626.1342 | 636.656
3355.1292 | 634.4739 | 630.6961 | 631.4396 | 634.368
3356.1292 | 634.3394 | 628.8547 | 632.9409 | 637.4813
3357.1292 | 633.9186 | 625.7786 | 632.3284 | 641.6826
3358.1448 | 633.3139 | 622.8462 | 630.9206 | 646.6977
3359.1292 | 634.4048 | 621.7623 | 632.8067 | 654.1907
3360.1292 | 634.3762 | 618.8478 | 632.2079 | 659.159
3361.1292 | 634.2853 | 616.6353 | 632.0143 | 647.2689
3362.1292 | 634.0078 | 615.5876 | 637.8543 | 642.2955
3363.1292 | 633.9456 | 623.426 | 637.8474 | 647.3338
3364.1292 | 634.7877 | 629.5046 | 639.1728 | 648.7465
3365.1292 | 634.684 | 639.0612 | 638.1074 | 643.2393
3366.1292 | 634.5183 | 640.6903 | 636.8535 | 641.8403
3367.1292 | 635.2685 | 641.9972 | 643.9569 | 660.6364
3368.1292 | 635.6796 | 647.4158 | 644.2611 | 657.2439
3369.1292 | 635.9264 | 648.1385 | 646.5164 | 656.6235
3370.1292 | 636.2492 | 648.655 | 646.1554 | 652.2736
3371.1292 | 636.9871 | 641.6544 | 641.8598 | 655.4337
3372.1292 | 637.0726 | 636.7625 | 638.0348 | 653.7435
3373.1292 | 637.3536 | 632.7313 | 633.0844 | 657.437
3374.1292 | 637.3381 | 629.4183 | 634.4501 | 656.8381
3375.1292 | 638.585 | 627.3986 | 641.5543 | 657.571
3376.1292 | 639.4762 | 625.816 | 642.4108 | 663.805
3377.1292 | 641.3529 | 626.2596 | 651.1977 | 661.706
3378.1292 | 642.8828 | 629.4928 | 656.4361 | 658.8422
3379.1292 | 643.535 | 630.0266 | 652.041 | 659.0696
3380.1448 | 644.5064 | 630.761 | 649.9013 | 651.6891
3381.1292 | 643.6349 | 628.212 | 645.2984 | 645.3843
3382.1292 | 643.4794 | 626.6333 | 640.6618 | 642.7329
3383.1292 | 642.9042 | 623.7767 | 635.9682 | 635.1983
3384.1292 | 641.8927 | 624.8225 | 634.1279 | 628.6103
3385.1292 | 642.4362 | 621.8133 | 632.6302 | 636.5586
3386.1292 | 641.9468 | 619.4904 | 630.0675 | 632.9763
3387.1292 | 641.1384 | 616.4495 | 627.287 | 625.8486
3388.1448 | 641.246 | 614.3365 | 626.2442 | 627.5792
3389.1292 | 639.5721 | 613.2697 | 624.108 | 625.512
3390.1292 | 639.4427 | 609.7724 | 620.9887 | 617.4007
3391.1292 | 639.1635 | 607.9424 | 619.7736 | 611.8118
3392.1292 | 639.2823 | 620.8418 | 623.7404 | 613.5074
3393.1292 | 638.8771 | 616.6431 | 622.6251 | 607.5901
3394.1292 | 638.5416 | 618.7508 | 624.3269 | 605.7058
3395.1292 | 637.744 | 616.9007 | 622.4283 | 613.2385
3396.1292 | 636.8898 | 614.4189 | 623.9932 | 609.4048
3397.1292 | 637.1139 | 618.9115 | 624.6485 | 615.8773
3398.1292 | 636.3621 | 624.5306 | 622.7855 | 617.484
3399.1292 | 636.2034 | 622.846 | 624.5466 | 630.5978
3400.1292 | 636.1497 | 626.7396 | 623.591 | 635.623
3401.1292 | 635.6619 | 623.6958 | 623.6861 | 633.9619
3402.1292 | 634.8287 | 623.7935 | 629.2114 | 633.3049
3403.1292 | 634.4463 | 619.6735 | 635.39 | 625.2962
3404.1292 | 634.1402 | 615.9741 | 636.6275 | 624.6364
3405.1292 | 634.5548 | 614.1033 | 631.8235 | 631.7287
3406.1292 | 633.9836 | 613.4962 | 629.9274 | 637.1372
3407.1292 | 633.6314 | 614.8834 | 626.9075 | 633.4158
3408.1292 | 632.8587 | 615.8512 | 624.3859 | 637.4653
3409.1292 | 632.9461 | 618.0444 | 622.4287 | 630.7109
3410.1292 | 633.1367 | 616.7276 | 621.3651 | 634.4881
3411.1292 | 632.6565 | 619.3912 | 618.97 | 638.8804
3412.1292 | 632.296 | 617.4714 | 629.8812 | 640.626
3413.1292 | 632.0115 | 616.6223 | 637.1874 | 637.7218
3414.1292 | 632.357 | 615.1292 | 639.1853 | 640.3678
3415.1292 | 632.6653 | 612.3133 | 635.1434 | 639.4076
3416.1292 | 634.3236 | 613.2274 | 634.996 | 646.4062
3417.1292 | 635.296 | 611.908 | 634.361 | 653.2753
3418.1292 | 635.1102 | 611.1514 | 635.7415 | 649.3075
3419.1292 | 635.6131 | 618.4256 | 634.6513 | 651.8864
3420.1292 | 635.7043 | 624.6349 | 632.7523 | 662.543
3421.1292 | 635.8729 | 622.0336 | 628.4772 | 667.4805
3422.1292 | 635.8964 | 620.9417 | 629.4148 | 660.7195
3423.1292 | 637.4627 | 617.6597 | 627.1333 | 667.7918
3424.1292 | 638.3352 | 616.0404 | 628.414 | 664.4207
3425.1292 | 638.5959 | 615.4918 | 627.5477 | 655.2827
3426.1292 | 638.3947 | 612.3465 | 624.4213 | 643.5715
3427.1292 | 638.2184 | 609.4037 | 622.0536 | 637.9832
3428.1292 | 638.7202 | 609.2406 | 619.9889 | 630.6778
3429.1292 | 638.4208 | 608.0903 | 619.5617 | 625.5737
3430.1292 | 637.4918 | 607.7638 | 619.9902 | 636.8529
3431.1292 | 636.4434 | 604.9501 | 618.5431 | 639.466
3432.1292 | 637.1523 | 603.88 | 618.6482 | 636.7665
3433.1292 | 637.8889 | 605.3264 | 621.941 | 635.5471
3434.1292 | 638.7233 | 612.9829 | 625.3125 | 629.843
3435.1292 | 638.0053 | 618.2413 | 625.5604 | 622.3757
3436.1292 | 637.7998 | 620.8606 | 627.378 | 616.8478
3437.1292 | 637.4928 | 623.142 | 630.6733 | 619.6415
3438.1292 | 637.2188 | 621.291 | 632.0654 | 627.2127
3439.1292 | 636.6042 | 619.6511 | 629.4536 | 625.2916
3440.1448 | 635.9305 | 625.2726 | 630.7251 | 628.3984
3441.1292 | 636.1258 | 626.4373 | 637.6187 | 627.6458
3442.1292 | 635.5075 | 624.006 | 634.5867 | 627.3869
3443.1292 | 634.6713 | 620.5584 | 631.2406 | 632.8895
3444.1292 | 634.7301 | 617.0014 | 628.0682 | 637.8242
3445.1292 | 634.4854 | 619.9018 | 627.1493 | 635.3158
3446.1292 | 635.0522 | 616.5409 | 625.6264 | 630.155
3447.1292 | 635.1959 | 613.7822 | 622.7852 | 626.8909
3448.1292 | 634.9051 | 612.3278 | 621.6629 | 645.7025
3449.1292 | 634.9958 | 611.4382 | 618.2987 | 643.4752
3450.1292 | 635.9882 | 610.2748 | 616.8897 | 641.0376
3451.1292 | 637.4884 | 608.7646 | 618.2934 | 641.662
3452.1292 | 638.3773 | 607.0406 | 619.3403 | 635.2684
3453.1292 | 638.714 | 609.8338 | 618.4481 | 626.8396
3454.1292 | 638.6888 | 608.2394 | 617.3775 | 619.5063
3455.1292 | 638.3741 | 608.2265 | 614.6865 | 623.1455
3456.1292 | 637.7117 | 609.1919 | 616.1421 | 619.6066
3457.1292 | 636.9425 | 607.8327 | 616.0517 | 625.9267
3458.1292 | 636.9807 | 616.5693 | 623.5176 | 626.3276
3459.1292 | 637.6563 | 624.446 | 629.8216 | 630.9485
3460.1292 | 637.2951 | 633.0258 | 636.1377 | 631.619
3461.1292 | 637.3201 | 633.1341 | 632.9109 | 622.6645
3462.1292 | 636.6874 | 632.9838 | 632.3782 | 618.7861
3463.1292 | 636.206 | 628.8603 | 627.3182 | 625.8002
3464.1292 | 635.323 | 629.2862 | 627.8701 | 629.1073
3465.1292 | 636.1798 | 630.4736 | 625.3058 | 630.5823
3466.1292 | 636.6159 | 626.5966 | 622.7956 | 625.6099
3467.1292 | 637.9196 | 628.6924 | 622.8042 | 618.3449
3468.1292 | 638.0365 | 624.6967 | 622.0196 | 616.292
3469.1292 | 638.896 | 622.665 | 624.6289 | 612.605
3470.1292 | 638.8665 | 619.4959 | 623.3324 | 607.1419
3471.1292 | 640.0989 | 618.5322 | 623.0512 | 602.5718
3472.1292 | 641.1024 | 616.5957 | 621.1747 | 599.4196
3473.1292 | 641.2259 | 615.8608 | 622.42 | 596.6747
3474.1292 | 642.027 | 615.2516 | 620.3803 | 593.6238
3475.1292 | 641.7766 | 613.7021 | 620.1164 | 596.7854
3476.1292 | 642.4623 | 611.7026 | 619.4097 | 594.9122
3477.1292 | 641.1787 | 609.6258 | 618.213 | 598.0079
3478.1448 | 640.5301 | 606.4362 | 616.9834 | 595.2244
3479.1292 | 640.2509 | 603.1165 | 614.1506 | 592.4237
3480.1292 | 641.1959 | 603.2653 | 614.6303 | 589.4355
3481.1292 | 640.8801 | 601.9268 | 614.1558 | 588.8748
3482.1292 | 639.832 | 606.5661 | 614.5948 | 587.5187
3483.1292 | 639.2956 | 609.3871 | 613.261 | 584.01
3484.1292 | 638.2438 | 606.2635 | 611.7749 | 588.8537
3485.1292 | 637.4849 | 604.2286 | 613.0435 | 590.8709
3486.1292 | 637.6038 | 610.9346 | 616.4819 | 597.96
3487.1292 | 637.4287 | 611.8704 | 617.1197 | 595.3747
3488.1292 | 636.4319 | 610.0531 | 615.5359 | 597.0336
3489.1292 | 635.8502 | 610.5239 | 617.0857 | 597.2864
3490.1292 | 635.9917 | 617.5314 | 615.889 | 592.8839
3491.1292 | 635.722 | 615.9062 | 619.086 | 610.9889
3492.1292 | 635.2108 | 614.8112 | 618.4309 | 615.7247
3493.1292 | 635.7894 | 617.2106 | 623.0051 | 614.7824
3494.1292 | 635.2435 | 614.6931 | 620.138 | 614.235
3495.1292 | 635.1012 | 612.4971 | 617.9885 | 615.1946
3496.1292 | 634.6636 | 615.4915 | 615.1074 | 610.2697
3497.1292 | 634.7945 | 613.1811 | 612.3732 | 616.1793
3498.1292 | 634.5154 | 609.9532 | 610.9771 | 618.4546
3499.1292 | 634.66 | 608.6179 | 610.9621 | 611.215
3500.1448 | 634.6531 | 614.6928 | 609.5793 | 616.9201
3501.1292 | 634.9844 | 618.7462 | 611.7325 | 624.5291
3502.1292 | 634.9928 | 617.3217 | 613.343 | 627.5558
3503.1292 | 634.3013 | 614.5646 | 615.2614 | 631.2097
3504.1292 | 633.4551 | 611.5304 | 611.7353 | 628.8652
3505.1292 | 633.3191 | 633.4188 | 613.129 | 623.1656
3506.1292 | 633.159 | 631.3729 | 611.7152 | 614.8652
3507.1292 | 633.6376 | 626.5077 | 613.1997 | 618.002
3508.1448 | 633.5067 | 624.2959 | 611.8343 | 622.961
3509.1292 | 633.386 | 622.2962 | 612.1936 | 622.4858
3510.1292 | 633.4565 | 621.8465 | 612.0751 | 617.7398
3511.1292 | 633.9958 | 620.1119 | 611.1017 | 615.9924
3512.1292 | 633.7959 | 619.331 | 610.2912 | 615.4313
3513.1292 | 633.9868 | 616.8668 | 609.4242 | 614.8855
3514.1292 | 634.4593 | 624.2171 | 612.8517 | 613.5989
3515.1292 | 635.511 | 621.5263 | 613.6185 | 612.1748
3516.1292 | 636.1147 | 621.6162 | 615.6065 | 613.6008
3517.1292 | 635.8811 | 622.2629 | 615.1241 | 605.6068
3518.1292 | 635.8655 | 620.7884 | 613.2364 | 601.3494
3519.1292 | 635.8591 | 629.1627 | 614.2584 | 603.5371
3520.1292 | 635.3717 | 625.8768 | 611.1306 | 598.9024
3521.1292 | 635.0994 | 621.9877 | 608.1884 | 607.7471
3522.1292 | 635.4762 | 619.5339 | 607.2834 | 607.0897
3523.1292 | 636.1219 | 617.7427 | 608.1251 | 610.2326
3524.1292 | 637.5627 | 620.3881 | 610.7402 | 607.1427
3525.1292 | 636.9579 | 623.173 | 614.3081 | 605.4623
3526.1292 | 637.2625 | 631.7148 | 616.2979 | 606.1518
3527.1292 | 635.8949 | 627.8787 | 615.4243 | 609.1763
3528.1292 | 636.1686 | 628.2375 | 614.7343 | 609.2888
3529.1292 | 636.9505 | 629.2216 | 618.0152 | 613.3151
3530.1292 | 636.9222 | 629.6196 | 622.7775 | 613.4726
3531.1292 | 636.8978 | 632.2856 | 623.2312 | 616.0075
3532.1292 | 637.497 | 635.5604 | 628.1861 | 610.6574
3533.1292 | 637.609 | 634.8327 | 628.6885 | 606.7136
3534.1292 | 637.2417 | 632.9587 | 625.1645 | 608.0166
3535.1292 | 636.908 | 630.346 | 623.2355 | 606.0033
3536.1292 | 636.767 | 626.8917 | 622.5108 | 605.0713
3537.1292 | 636.4032 | 629.4175 | 620.4141 | 608.0793
3538.1292 | 636.8233 | 634.5328 | 620.092 | 611.1344
3539.1292 | 636.6487 | 630.0139 | 619.9467 | 623.0826
3540.1292 | 636.8228 | 626.3327 | 617.069 | 614.6506
3541.1292 | 636.7288 | 624.0915 | 616.9614 | 608.5158
3542.1292 | 636.8982 | 621.3222 | 616.8513 | 611.5289
3543.1292 | 636.6833 | 625.5658 | 617.1698 | 613.5218
3544.1292 | 637.1071 | 631.09 | 616.7222 | 609.5697
3545.1292 | 637.1823 | 626.0263 | 614.7673 | 602.66
3546.1292 | 636.9748 | 624.5626 | 614.7065 | 598.8682
3547.1292 | 637.2434 | 623.2442 | 615.6462 | 603.0369
3548.1292 | 637.5012 | 621.1948 | 617.7687 | 602.6346
3549.1292 | 637.521 | 618.2792 | 616.5423 | 603.2548
3550.1292 | 637.6306 | 617.1457 | 614.9918 | 597.6836
3551.1292 | 638.7897 | 616.4494 | 614.1483 | 593.2995
3552.1292 | 638.8614 | 621.7666 | 615.1603 | 604.0034
3553.1292 | 638.5435 | 620.7661 | 613.4876 | 597.4966
3554.1292 | 638.5568 | 624.0749 | 612.3918 | 593.225
3555.1292 | 638.6923 | 622.9621 | 610.1911 | 590.0771
3556.1292 | 639.221 | 620.3706 | 612.2008 | 596.6299
3557.1292 | 640.5581 | 622.6031 | 617.3483 | 602.465
3558.1292 | 640.1815 | 620.9145 | 618.0234 | 601.1906
3559.1292 | 639.5972 | 615.8465 | 616.3934 | 601.9176
3560.1448 | 637.9606 | 626.3127 | 619.1102 | 606.2891
3561.1292 | 639.3376 | 632.1615 | 622.076 | 610.1272
3562.1292 | 638.2325 | 632.4898 | 621.7633 | 607.984
3563.1292 | 638.3129 | 637.1027 | 620.979 | 604.0611
3564.1292 | 638.5809 | 642.8225 | 622.1859 | 602.8358
3565.1292 | 637.6943 | 648.3134 | 621.8332 | 595.8754
3566.1292 | 636.0915 | 647.6774 | 616.355 | 590.4113
3567.1292 | 635.4495 | 646.1846 | 613.5221 | 587.581
3568.1292 | 635.7658 | 639.3957 | 612.8133 | 584.4544
3569.1292 | 635.0916 | 634.1541 | 610.653 | 581.9311
3570.1292 | 635.4411 | 643.5846 | 610.4057 | 579.0987
3571.1292 | 636.0799 | 636.7644 | 610.3426 | 575.6636
3572.1292 | 636.7297 | 631.9399 | 610.395 | 574.1711
3573.1292 | 636.9075 | 633.2454 | 610.956 | 586.4165
3574.1292 | 637.6378 | 631.137 | 611.1959 | 588.0985
3575.1292 | 637.4214 | 627.0786 | 609.2417 | 590.3692
3576.1292 | 636.8915 | 624.6812 | 607.0866 | 590.6836
3577.1448 | 636.7951 | 620.9254 | 606.3763 | 592.3956
3578.1292 | 637.2287 | 627.3589 | 609.7619 | 591.118
3579.1292 | 636.9154 | 632.9938 | 610.0097 | 593.3501
3580.1292 | 636.5522 | 632.5555 | 613.3991 | 589.412
3581.1292 | 636.3625 | 633.3676 | 611.2978 | 592.0706
3582.1292 | 636.5351 | 633.9824 | 609.8086 | 594.4535
3583.1292 | 636.0746 | 629.194 | 608.273 | 602.2107
3584.1292 | 636.1568 | 632.8219 | 607.5766 | 606.6408
3585.1292 | 636.4017 | 631.3118 | 606.9991 | 603.9251
3586.1292 | 636.9059 | 638.3015 | 607.3745 | 601.1617
3587.1292 | 637.1545 | 640.0861 | 606.0152 | 596.2874
3588.1292 | 637.1844 | 636.822 | 608.516 | 597.4623
3589.1292 | 636.8033 | 639.2189 | 609.5936 | 600.4052
3590.1292 | 636.8985 | 646.4061 | 611.096 | 603.2012
3591.1292 | 637.1505 | 641.0574 | 611.8861 | 599.1399
3592.1292 | 636.9387 | 636.069 | 614.9946 | 597.3555
3593.1292 | 637.9638 | 638.6385 | 617.0891 | 594.4658
3594.1292 | 638.3223 | 638.6833 | 614.0105 | 591.9812
3595.1292 | 637.3682 | 633.2902 | 611.4826 | 597.3574
3596.1292 | 636.7404 | 627.1113 | 608.8472 | 598.5906
3597.1292 | 636.5004 | 622.2949 | 607.9951 | 606.8591
3598.1292 | 636.9979 | 619.9965 | 607.2319 | 606.6054
3599.1292 | 637.2754 | 623.0687 | 607.317 | 601.7354
3600.1292 | 639.4518 | 620.9544 | 610.8489 | 598.7527
3601.1292 | 639.8842 | 617.1206 | 609.5984 | 594.8405
3602.1292 | 640.4486 | 617.6006 | 609.7176 | 589.7397
3603.1292 | 640.4681 | 618.1606 | 607.7885 | 591.0779
3604.1292 | 639.9164 | 618.5586 | 607.3505 | 587.6458
3605.1292 | 640.41 | 616.9451 | 607.6052 | 589.258
3606.1292 | 639.7802 | 615.6971 | 605.9041 | 586.0562
3607.1292 | 638.9881 | 612.2364 | 603.7645 | 583.7114
3608.1292 | 639.0657 | 610.9821 | 603.5479 | 588.0267
3609.1292 | 638.8654 | 609.6162 | 603.535 | 585.8587
3610.1292 | 638.0954 | 610.4932 | 603.9303 | 588.2618
3611.1292 | 638.3224 | 611.2092 | 604.8929 | 588.548
3612.1292 | 637.6302 | 609.9545 | 604.1797 | 589.0102
3613.1292 | 636.6568 | 616.91 | 602.7008 | 586.0115
3614.1292 | 636.3464 | 614.2335 | 601.382 | 584.6926
3615.1292 | 636.7055 | 615.9136 | 601.5732 | 582.4207
3616.1292 | 637.2106 | 619.942 | 603.3971 | 584.8658
3617.1292 | 637.6717 | 619.7833 | 605.1251 | 584.8457
3618.1292 | 637.9791 | 626.3589 | 606.2462 | 583.8554
3619.1292 | 637.1772 | 637.137 | 606.889 | 583.7903
3620.1292 | 637.9045 | 640.0372 | 610.3421 | 583.8035
3621.1292 | 638.4181 | 645.2379 | 612.378 | 583.8386
3622.1292 | 638.1854 | 639.9985 | 613.0696 | 584.0069
3623.1292 | 636.8205 | 638.7013 | 611.5774 | 582.7295
3624.1292 | 636.4374 | 649.4888 | 612.7924 | 581.2622
3625.1292 | 637.3501 | 657.4329 | 616.4678 | 582.3321
3626.1292 | 638.2769 | 662.5719 | 618.6998 | 582.8893
3627.1292 | 638.2593 | 665.8221 | 616.5577 | 579.8436
3628.1292 | 637.4976 | 663.9828 | 618.0521 | 578.6534
3629.1292 | 636.8851 | 657.0837 | 617.3355 | 582.8645
3630.1292 | 637.6153 | 647.7096 | 614.802 | 585.284
3631.1292 | 637.4 | 643.2731 | 614.0287 | 582.9321
3632.1292 | 637.2918 | 637.5318 | 612.285 | 588.6758
3633.1292 | 637.5222 | 634.7376 | 611.4383 | 590.1746
3634.1292 | 637.497 | 644.9499 | 611.5005 | 587.9529
3635.1292 | 637.3484 | 648.6652 | 610.4578 | 584.5839
3636.1292 | 637.0327 | 650.3382 | 610.7059 | 581.5353
3637.1292 | 636.7564 | 646.6009 | 610.2764 | 582.0125
3638.1292 | 637.534 | 647.3611 | 614.9002 | 579.4825
3639.1292 | 638.1571 | 645.1233 | 614.6089 | 584.3743
3640.1292 | 638.1074 | 640.487 | 613.8173 | 582.6717
3641.1292 | 637.7899 | 637.7368 | 616.3147 | 588.7105
3642.1292 | 638.3115 | 640.2575 | 614.7534 | 585.9734
3643.1292 | 639.1331 | 641.3222 | 616.27 | 584.018
3644.1292 | 639.0131 | 643.469 | 617.6043 | 583.3376
3645.1292 | 639.0774 | 650.8895 | 617.1964 | 581.681
3646.1292 | 638.0351 | 655.6699 | 614.9506 | 581.5094
3647.1292 | 638.0594 | 652.2325 | 620.358 | 584.6405
3648.1292 | 637.9146 | 656.9667 | 620.7666 | 597.2821
3649.1292 | 637.9357 | 663.9546 | 618.1506 | 593.5801
3650.1292 | 637.2729 | 660.0611 | 617.0225 | 589.1776
3651.1292 | 637.1491 | 656.1931 | 616.1165 | 590.8416
3652.1292 | 637.4699 | 652.0442 | 616.0333 | 589.4953
3653.1292 | 638.3222 | 649.8732 | 617.7353 | 588.2476
3654.1292 | 638.1554 | 648.9848 | 616.6883 | 587.7639
3655.1292 | 638.1189 | 649.0055 | 616.6875 | 583.6192
3656.1292 | 637.9091 | 645.1366 | 615.5476 | 585.6798
3657.1292 | 636.9682 | 640.9647 | 615.0703 | 588.3548
3658.1448 | 636.7749 | 640.415 | 611.6038 | 587.5079
3659.1292 | 636.5994 | 640.0136 | 611.8307 | 586.8676
3660.1292 | 636.6073 | 635.3857 | 610.6102 | 590.6442
3661.1292 | 635.8857 | 630.5416 | 608.2175 | 593.3874
3662.1292 | 635.8787 | 626.1682 | 607.3241 | 593.3833
3663.1292 | 635.884 | 622.2843 | 607.6791 | 592.6697
3664.1292 | 636.1657 | 624.3099 | 609.9251 | 589.0776
3665.1292 | 636.3351 | 624.5142 | 609.2802 | 585.7918
3666.1292 | 636.0674 | 626.1787 | 609.3242 | 582.4689
3667.1292 | 635.5867 | 634.8948 | 607.8871 | 579.3273
3668.1292 | 635.3333 | 645.3594 | 605.3765 | 577.2325
3669.1292 | 635.6435 | 642.0597 | 606.142 | 577.0262
3670.1292 | 636.3992 | 645.0127 | 610.2654 | 586.5283
3671.1292 | 636.2797 | 645.8757 | 610.8294 | 582.9936
3672.1292 | 635.9595 | 651.4727 | 608.9325 | 578.2992
3673.1292 | 635.3308 | 644.8526 | 610.2036 | 574.8322
3674.1292 | 635.1906 | 638.3846 | 608.7159 | 578.7777
3675.1292 | 635.7885 | 637.9744 | 610.2569 | 588.4342
3676.1292 | 636.0267 | 640.4399 | 610.048 | 586.2489
3677.1292 | 636.6771 | 650.8397 | 611.8224 | 586.2158
3678.1292 | 636.8381 | 654.8574 | 612.0433 | 583.3265
3679.1292 | 637.2591 | 659.8716 | 614.2194 | 584.9174
3680.1292 | 637.0236 | 659.6036 | 617.988 | 585.0658
3681.1292 | 636.9067 | 659.0059 | 616.9066 | 582.606
3682.1292 | 637.8737 | 664.4083 | 616.5556 | 583.2716
3683.1292 | 637.6481 | 662.3833 | 617.8419 | 581.4693
3684.1292 | 636.1823 | 658.8307 | 615.8624 | 579.6136
3685.1292 | 635.9259 | 656.9367 | 615.2605 | 579.8096
3686.1292 | 635.9764 | 658.1081 | 613.4483 | 583.0526
3687.1292 | 636.1385 | 651.8485 | 612.6636 | 583.5994
3688.1292 | 635.9592 | 648.327 | 613.1894 | 581.767
3689.1292 | 636.0441 | 644.3608 | 611.5624 | 580.7567
3690.1292 | 636.5795 | 642.5179 | 610.9377 | 578.8996
3691.1292 | 636.8566 | 638.9304 | 609.4423 | 575.2075
3692.1292 | 636.6943 | 633.9635 | 608.2495 | 572.6166
3693.1292 | 636.3522 | 630.0679 | 604.9215 | 569.3345
3694.1292 | 635.1793 | 626.8756 | 604.726 | 576.6974
3695.1292 | 634.8033 | 630.4778 | 605.3166 | 578.6814
3696.1292 | 634.7453 | 627.3376 | 602.7298 | 577.1582
3697.1292 | 634.4096 | 625.5513 | 602.1026 | 575.1269
3698.1292 | 635.3026 | 625.8978 | 599.9787 | 578.1144
3699.1292 | 636.3722 | 624.2498 | 601.9487 | 576.5984
3700.1292 | 636.3569 | 621.9196 | 602.5486 | 575.6191
3701.1292 | 636.0117 | 618.4992 | 603.6913 | 574.2114
3702.1292 | 635.8577 | 631.0095 | 603.0788 | 574.4036
3703.1292 | 636.2922 | 643.0973 | 606.3202 | 575.3864
3704.1292 | 635.7232 | 646.6017 | 609.4825 | 578.5042
3705.1292 | 635.6827 | 649.2145 | 609.4429 | 577.0068
3706.1292 | 635.796 | 647.4812 | 607.5889 | 577.4098
3707.1292 | 635.2596 | 643.6575 | 606.6651 | 576.3528
3708.1292 | 635.0762 | 636.9669 | 604.536 | 572.9577
3709.1292 | 634.714 | 636.3569 | 604.3492 | 571.9714
3710.1292 | 633.7965 | 631.8619 | 603.3648 | 570.6293
3711.1292 | 633.8778 | 625.6982 | 600.9347 | 568.7575
3712.1292 | 634.0544 | 620.9119 | 600.4194 | 569.3298
3713.1292 | 633.9776 | 617.8721 | 599.9877 | 573.2485
3714.1292 | 634.4645 | 619.4617 | 600.3817 | 571.1676
3715.1292 | 634.1721 | 624.1228 | 600.8407 | 571.3048
3716.1292 | 633.996 | 621.277 | 600.4 | 576.1517
3717.1292 | 634.484 | 616.4624 | 599.4702 | 574.0849
3718.1292 | 634.4126 | 615.4826 | 597.9024 | 572.9911
3719.1292 | 634.5661 | 614.0472 | 597.5778 | 576.8498
3720.1292 | 635.2361 | 611.5937 | 596.7266 | 586.8608
3721.1292 | 635.9168 | 610.6149 | 597.1827 | 586.0318
3722.1292 | 637.9854 | 612.2524 | 599.1646 | 582.0956
3723.1292 | 638.6647 | 615.8577 | 600.0694 | 587.7601
3724.1292 | 637.964 | 616.9687 | 600.3544 | 583.9514
3725.1292 | 637.3486 | 620.5248 | 599.6266 | 585.2197
3726.1292 | 637.0157 | 621.0743 | 598.8635 | 580.247
3727.1292 | 636.749 | 620.9258 | 597.3181 | 578.2364
3728.1292 | 635.8883 | 619.6299 | 596.9232 | 575.1672
3729.1292 | 635.2106 | 616.0722 | 595.6967 | 575.2999
3730.1292 | 635.4836 | 612.8433 | 595.1528 | 575.3587
3731.1292 | 635.9253 | 612.5276 | 594.9145 | 576.0572
3732.1292 | 635.7035 | 610.6192 | 596.2641 | 575.5545
3733.1292 | 635.3844 | 608.3826 | 595.873 | 572.9502
3734.1292 | 636.0134 | 618.3462 | 599.8603 | 571.799
3735.1292 | 635.5445 | 616.6658 | 599.1695 | 569.0204
3736.1292 | 636.0681 | 615.7212 | 600.4514 | 567.5984
3737.1292 | 636.5754 | 616.198 | 600.8166 | 567.2692
3738.1292 | 636.6905 | 616.3897 | 600.7296 | 565.9434
3739.1292 | 636.4138 | 614.9513 | 600.8335 | 567.0357
3740.1292 | 636.2464 | 616.3697 | 600.9821 | 568.5313
3741.1292 | 636.5005 | 617.2647 | 602.0651 | 570.8763
3742.1292 | 636.1802 | 623.2106 | 601.4184 | 573.8847
3743.1292 | 635.3359 | 622.7548 | 599.907 | 572.8799
3744.1292 | 635.4386 | 620.9959 | 599.9849 | 570.8923
3745.1448 | 635.203 | 627.4225 | 598.8186 | 579.7468
3746.1292 | 635.3119 | 631.1399 | 597.5436 | 580.5324
3747.1292 | 634.0474 | 625.2339 | 597.0735 | 576.982
3748.1292 | 633.8398 | 625.9986 | 597.2069 | 584.2348
3749.1292 | 634.2651 | 622.1149 | 596.1989 | 581.2808
3750.1292 | 634.3316 | 618.4484 | 595.2528 | 577.018
3751.1292 | 635.2859 | 616.6491 | 593.955 | 571.7659
3752.1292 | 636.1016 | 613.6063 | 594.8124 | 579.2231
3753.1292 | 636.2974 | 611.7656 | 595.8215 | 578.2871
3754.1292 | 635.923 | 609.9335 | 594.7984 | 575.4828
3755.1292 | 635.8858 | 610.883 | 595.192 | 571.4167
3756.1292 | 635.468 | 610.3116 | 594.3209 | 571.6451
3757.1292 | 635.4948 | 609.9691 | 592.9531 | 576.1992
3758.1292 | 635.8511 | 614.9924 | 593.4718 | 572.3336
3759.1292 | 634.7016 | 616.3398 | 592.8522 | 569.5021
3760.1292 | 634.2503 | 613.3703 | 591.7445 | 570.7091
3761.1292 | 634.7029 | 609.9915 | 591.6924 | 571.6954
3762.1292 | 636.0381 | 608.8569 | 594.4703 | 576.2175
3763.1292 | 637.0087 | 608.9836 | 597.9818 | 576.8197
3764.1292 | 637.2282 | 608.0172 | 598.0053 | 574.5995
3765.1292 | 638.3912 | 609.1147 | 598.7537 | 572.0256
3766.1292 | 639.0227 | 611.0387 | 598.4425 | 571.0127
3767.1292 | 637.6674 | 610.9392 | 597.4082 | 572.9284
3768.1292 | 638.222 | 611.1568 | 596.7228 | 573.3675
3769.1448 | 638.0396 | 608.767 | 596.0217 | 569.7446
3770.1292 | 638.028 | 608.4253 | 594.833 | 570.6338
3771.1448 | 637.8074 | 608.8693 | 594.4619 | 567.4953
3772.1292 | 637.5993 | 607.604 | 593.8164 | 564.9869
3773.1292 | 637.4186 | 605.6139 | 593.92 | 564.2685
3774.1292 | 637.043 | 605.8539 | 593.8822 | 562.5715
3775.1292 | 635.8082 | 605.3658 | 592.4555 | 559.2455
3776.1292 | 635.4052 | 604.1406 | 591.9719 | 558.8032
3777.1292 | 635.4566 | 603.2915 | 592.4352 | 562.5612
3778.1292 | 635.4933 | 603.4686 | 592.0701 | 569.6251
3779.1292 | 635.1383 | 603.249 | 591.4434 | 574.1509
3780.1292 | 635.7889 | 604.9715 | 593.1584 | 575.3725
3781.1292 | 634.5983 | 604.7437 | 591.5775 | 573.1576
3782.1292 | 634.02 | 607.9257 | 591.9901 | 569.1911
3783.1292 | 633.5846 | 610.2164 | 589.1633 | 566.0222
3784.1292 | 633.9569 | 612.1954 | 589.8822 | 566.9425
3785.1292 | 634.7155 | 614.166 | 592.9701 | 567.3187
3786.1292 | 634.2956 | 612.7849 | 591.6175 | 563.253
3787.1292 | 633.7527 | 612.5326 | 590.9764 | 560.1438
3788.1292 | 633.506 | 611.6345 | 591.4436 | 559.8285
3789.1292 | 633.7473 | 608.7083 | 590.5932 | 567.3048
3790.1292 | 634.8103 | 607.1832 | 591.4331 | 564.9541
3791.1292 | 636.0596 | 609.7399 | 592.5793 | 563.5747
3792.1292 | 636.9502 | 611.6713 | 592.6069 | 566.7716
3793.1292 | 638.8105 | 610.8222 | 594.4624 | 564.6059
3794.1292 | 639.8966 | 612.1822 | 595.5673 | 565.2828
3795.1292 | 638.9759 | 611.3396 | 594.8119 | 567.1682
3796.1292 | 640.2849 | 610.2732 | 595.2143 | 565.8544
3797.1292 | 639.7118 | 611.1101 | 595.7227 | 565.031
3798.1292 | 638.7868 | 611.8795 | 594.6697 | 563.8722
3799.1292 | 638.1204 | 611.4435 | 593.2216 | 568.7798
3800.1292 | 638.1621 | 609.9862 | 591.7249 | 565.0707
3801.1292 | 638.0355 | 608.7474 | 591.1273 | 564.768
3802.1292 | 637.4687 | 610.0209 | 591.3414 | 564.7636
3803.1292 | 637.4657 | 613.8389 | 591.1257 | 567.276
3804.1292 | 637.1302 | 612.3829 | 592.8535 | 566.1678
3805.1292 | 637.7388 | 609.9057 | 593.3135 | 564.7657
3806.1292 | 639.6832 | 607.6456 | 594.6812 | 567.3862
3807.1292 | 640.8249 | 612.6895 | 596.4562 | 565.1861
3808.1292 | 640.2697 | 612.38 | 594.8123 | 562.8241
3809.1292 | 641.1415 | 609.9068 | 595.3835 | 561.6748
3810.1292 | 642.7421 | 609.9417 | 595.9705 | 561.1021
3811.1292 | 642.3379 | 611.2277 | 595.3944 | 558.8458
3812.1292 | 642.2627 | 610.9837 | 595.6696 | 563.8832
3813.1292 | 643.9479 | 609.2001 | 598.2245 | 565.4487
3814.1292 | 645.3012 | 609.7608 | 599.986 | 563.5806
3815.1292 | 645.1404 | 611.7935 | 600.8782 | 563.0078
3816.1292 | 644.9937 | 611.6105 | 600.0473 | 561.8111
3817.1292 | 644.0849 | 612.2707 | 601.9851 | 562.5224
3818.1292 | 643.2792 | 617.3986 | 602.8898 | 562.8184
3819.1292 | 643.0411 | 614.2505 | 601.2255 | 560.9354
3820.1292 | 642.0312 | 612.8632 | 600.9594 | 558.8333
3821.1292 | 641.9058 | 612.4952 | 600.7647 | 558.0885
3822.1292 | 641.5151 | 616.1654 | 602.1147 | 557.2193
3823.1292 | 640.1788 | 614.0971 | 599.0196 | 555.3243
3824.1292 | 639.2133 | 614.3117 | 598.1158 | 552.6673
3825.1292 | 638.2531 | 615.8741 | 596.1414 | 550.1007
3826.1292 | 637.3175 | 613.4521 | 594.405 | 548.2608
3827.1292 | 636.2108 | 609.8901 | 593.0475 | 547.0247
3828.1292 | 636.7068 | 608.353 | 593.8444 | 545.6726
3829.1292 | 637.4097 | 611.9301 | 596.2735 | 547.0215
3830.1292 | 637.5664 | 615.4372 | 598.0855 | 549.3967
3831.1292 | 637.8269 | 614.6387 | 598.9899 | 549.3594
3832.1292 | 637.5934 | 613.6065 | 598.5451 | 549.5052
3833.1292 | 637.0902 | 615.9905 | 598.8987 | 556.1489
3834.1292 | 637.3482 | 616.0229 | 599.2926 | 556.5052
3835.1292 | 637.259 | 616.6472 | 599.5018 | 558.5726
3836.1292 | 637.1925 | 617.4773 | 599.0732 | 559.3802
3837.1292 | 636.5871 | 621.2834 | 597.4838 | 558.8632
3838.1292 | 635.4913 | 620.4374 | 595.7872 | 558.4972
3839.1292 | 634.3953 | 618.4596 | 593.4625 | 556.0097
3840.1292 | 634.2979 | 619.6726 | 593.2267 | 555.8891
3841.1292 | 634.1867 | 617.6887 | 593.0055 | 555.7269
3842.1292 | 634.4285 | 615.5925 | 592.171 | 555.7404
3843.1292 | 634.6376 | 615.0109 | 592.5781 | 554.9289
3844.1292 | 634.9905 | 615.1412 | 594.3985 | 555.9785
3845.1292 | 634.9902 | 614.938 | 595.9077 | 558.4837
3846.1292 | 634.4046 | 616.8556 | 594.4938 | 558.5602
3847.1292 | 634.8039 | 615.2046 | 594.6397 | 557.0305
3848.1292 | 634.5286 | 612.7001 | 595.6144 | 558.6885
3849.1292 | 635.5825 | 611.6815 | 598.4051 | 560.9805
3850.1292 | 635.2144 | 609.7351 | 598.6383 | 560.7347
3851.1292 | 635.2937 | 607.9129 | 599.1846 | 559.876
3852.1292 | 634.0382 | 611.4392 | 598.2487 | 558.6466
3853.1292 | 633.7438 | 610.196 | 600.733 | 561.5073
3854.1292 | 634.1603 | 609.7877 | 604.1551 | 564.5627
3855.1292 | 634.3367 | 610.7633 | 604.896 | 562.7789
3856.1292 | 633.8499 | 609.952 | 604.5632 | 565.9675
3857.1292 | 633.7076 | 611.8034 | 604.8447 | 562.9055
3858.1292 | 634.6901 | 611.664 | 605.8399 | 561.2578
3859.1292 | 634.1429 | 614.923 | 606.5256 | 559.2818
3860.1292 | 635.3967 | 612.0226 | 604.9169 | 558.1229
3861.1292 | 635.9951 | 611.4179 | 606.05 | 556.6447
3862.1292 | 635.5343 | 610.5615 | 606.6432 | 557.5599
3863.1292 | 634.8122 | 610.9771 | 605.607 | 556.1659
3864.1292 | 635.5509 | 608.4462 | 604.1438 | 554.3062
3865.1292 | 634.9329 | 607.0917 | 603.761 | 553.4878
3866.1292 | 634.3612 | 605.6491 | 601.7153 | 552.2033
3867.1292 | 634.1734 | 602.8563 | 600.4126 | 550.0281
3868.1292 | 633.5269 | 602.8425 | 599.8814 | 549.987
3869.1292 | 633.5309 | 600.9623 | 598.3943 | 549.5213
3870.1292 | 634.8769 | 600.5689 | 600.2328 | 550.046
3871.1292 | 635.5795 | 601.6841 | 600.8308 | 550.0902
3872.1292 | 634.7817 | 600.4935 | 600.3413 | 548.6059
3873.1292 | 634.6667 | 599.0195 | 599.2768 | 547.392
3874.1292 | 634.2272 | 597.5409 | 598.5715 | 547.7113
3875.1292 | 633.2937 | 596.0089 | 596.7426 | 545.5572
3876.1292 | 632.4887 | 596.997 | 595.7813 | 543.7128
3877.1292 | 632.1567 | 597.5247 | 594.5037 | 542.6761
3878.1292 | 631.9487 | 597.8277 | 594.117 | 542.381
3879.1292 | 632.4387 | 596.7288 | 594.9938 | 542.3475
3880.1292 | 632.2587 | 595.5002 | 595.6773 | 543.7216
3881.1292 | 632.0239 | 594.402 | 596.8316 | 544.5585
3882.1292 | 631.5977 | 596.7452 | 599.0661 | 546.3408
3883.1292 | 631.7894 | 596.701 | 600.0121 | 547.8706
3884.1292 | 632.4915 | 596.1647 | 598.6583 | 548.7795
3885.1292 | 632.1782 | 596.2044 | 599.0866 | 555.8965
3886.1292 | 632.1624 | 600.7121 | 596.8054 | 559.4599
3887.1292 | 632.3392 | 600.6372 | 596.2292 | 556.4264
3888.1292 | 632.2323 | 599.0163 | 595.3827 | 555.0851
3889.1292 | 632.1677 | 598.618 | 596.2754 | 561.5585
3890.1292 | 633.0667 | 597.5753 | 598.0763 | 560.2746
3891.1292 | 632.335 | 595.7748 | 597.3836 | 559.2491
3892.1292 | 632.9819 | 596.6924 | 597.0522 | 557.2324
3893.1292 | 632.7617 | 597.087 | 597.85 | 556.283
3894.1292 | 631.9556 | 596.7325 | 596.3185 | 556.751
3895.1292 | 632.2334 | 596.6153 | 597.7365 | 556.3865
3896.1292 | 632.8704 | 595.9641 | 596.6269 | 554.7379
3897.1292 | 633.4068 | 594.1732 | 595.7381 | 553.5257
3898.1292 | 632.7217 | 594.675 | 595.3122 | 555.858
3899.1292 | 632.2101 | 593.0427 | 593.7335 | 554.6687
3900.1292 | 632.5754 | 592.4168 | 592.552 | 554.4338
3901.1292 | 632.2206 | 596.9334 | 593.4061 | 556.9107
3902.1292 | 632.9294 | 598.185 | 593.6398 | 557.0574
3903.1292 | 633.3364 | 600.8493 | 594.2774 | 557.0728
3904.1292 | 633.9355 | 601.2093 | 598.2238 | 557.5983
3905.1292 | 634.4886 | 599.0816 | 597.9157 | 557.9812
3906.1292 | 634.4621 | 597.5937 | 597.2243 | 558.1699
3907.1292 | 634.2149 | 599.0698 | 597.0738 | 556.1454
3908.1292 | 633.9855 | 598.4953 | 595.6771 | 555.2766
3909.1292 | 634.835 | 597.3094 | 595.2542 | 553.8722
3910.1292 | 635.8301 | 597.3719 | 595.7071 | 554.37
3911.1292 | 636.1056 | 597.7584 | 596.0489 | 555.0318
3912.1292 | 636.5263 | 596.9381 | 596.6619 | 554.9719
3913.1292 | 636.4902 | 595.7512 | 596.6558 | 556.7299
3914.1292 | 636.2732 | 594.5996 | 596.2647 | 558.8661
3915.1292 | 635.4951 | 592.788 | 594.2395 | 556.4262
3916.1292 | 635.7159 | 593.4574 | 595.9358 | 555.3187
3917.1292 | 636.3214 | 595.4615 | 596.6206 | 556.8476
3918.1292 | 635.9441 | 596.0479 | 597.0746 | 563.9543
3919.1292 | 636.5868 | 596.3235 | 597.5775 | 562.0263
3920.1292 | 636.7341 | 597.9838 | 599.6077 | 561.8063
3921.1292 | 636.8815 | 599.3964 | 601.9494 | 562.0076
3922.1292 | 635.996 | 604.4922 | 601.0409 | 561.024
3923.1292 | 635.9226 | 601.9374 | 599.498 | 559.1489
3924.1292 | 635.9693 | 601.4544 | 598.9762 | 563.4876
3925.1292 | 635.7383 | 601.8259 | 597.6326 | 561.1919
3926.1292 | 636.4127 | 603.6117 | 598.367 | 559.7931
3927.1292 | 636.6765 | 602.6884 | 598.6938 | 562.045
3928.1292 | 635.7217 | 601.3975 | 598.7756 | 559.3804
3929.1292 | 635.2922 | 600.2938 | 597.4747 | 562.1128
3930.1292 | 635.4227 | 599.4354 | 596.5014 | 559.2252
3931.1292 | 635.7036 | 597.9726 | 596.191 | 557.1592
3932.1292 | 635.8785 | 597.1965 | 596.4904 | 557.7775
3933.1292 | 635.5276 | 596.4639 | 596.3594 | 556.863
3934.1292 | 634.8982 | 595.3557 | 594.7663 | 557.0134
3935.1292 | 634.9652 | 593.5081 | 593.7688 | 555.2903
3936.1292 | 634.49 | 594.5382 | 594.1857 | 554.3621
3937.1292 | 634.3387 | 595.068 | 593.8981 | 556.112
3938.1292 | 634.1274 | 595.7094 | 593.4253 | 554.728
3939.1292 | 634.3193 | 596.4072 | 594.8169 | 556.0777
3940.1292 | 634.6342 | 599.2525 | 600.3112 | 559.3998
3941.1292 | 634.0104 | 599.8394 | 598.4639 | 557.3829
3942.1292 | 634.2234 | 597.5115 | 597.5125 | 556.0715
3943.1292 | 634.4775 | 597.993 | 598.486 | 555.4884
3944.1292 | 634.3094 | 597.521 | 597.9812 | 553.9021
3945.1292 | 634.9422 | 595.8073 | 597.7984 | 553.1508
3946.1292 | 635.466 | 598.2919 | 597.3143 | 552.466
3947.1292 | 634.4767 | 597.4898 | 594.6087 | 559.1073
3948.1292 | 634.1273 | 597.403 | 594.5172 | 558.7137
3949.1292 | 634.3675 | 595.8684 | 595.0368 | 556.4273
3950.1292 | 634.553 | 594.1025 | 595.2422 | 556.025
3951.1292 | 635.5926 | 594.4003 | 596.2779 | 555.3132
3952.1292 | 635.263 | 595.3812 | 595.228 | 557.3541
3953.1292 | 635.3633 | 595.9038 | 594.5553 | 554.041
3954.1292 | 635.2233 | 595.2795 | 595.4437 | 553.3594
3955.1292 | 635.0496 | 593.913 | 596.2491 | 553.0797
3956.1292 | 634.9802 | 591.1142 | 595.6147 | 553.8799
3957.1292 | 634.2279 | 589.6028 | 595.4224 | 557.226
3958.1292 | 634.2278 | 589.5984 | 595.763 | 556.9387
3959.1292 | 633.8022 | 591.203 | 597.8303 | 556.887
3960.1292 | 634.476 | 591.9126 | 597.661 | 556.225
3961.1292 | 633.3604 | 590.954 | 597.7671 | 557.5649
3962.1292 | 632.8433 | 589.0491 | 596.6773 | 556.3661
3963.1292 | 632.3214 | 588.2824 | 595.8962 | 556.448
3964.1292 | 631.5573 | 587.9692 | 595.1152 | 555.2723
3965.1292 | 629.6425 | 587.0829 | 592.0155 | 553.1481
3966.1292 | 629.5547 | 585.0346 | 589.6451 | 550.4294
3967.1292 | 629.5835 | 582.9112 | 588.7614 | 549.0271
3968.1292 | 629.3555 | 584.4223 | 589.2761 | 548.3055
3969.1292 | 628.9555 | 584.7317 | 589.6109 | 549.3785
3970.1292 | 630.137 | 585.5448 | 590.1813 | 549.1907
3971.1292 | 629.8404 | 584.8333 | 590.6809 | 550.5193
3972.1292 | 629.5136 | 584.8247 | 590.1218 | 555.0815
3973.1292 | 630.1066 | 583.8578 | 590.4925 | 555.0044
3974.1292 | 630.3395 | 584.6404 | 590.4428 | 555.087
3975.1292 | 630.87 | 584.629 | 591.6428 | 555.2217
3976.1292 | 631.6442 | 586.3605 | 594.0428 | 559.2737
3977.1292 | 631.8449 | 587.6385 | 595.1604 | 560.1674
3978.1292 | 632.2534 | 586.5915 | 595.3151 | 557.7201
3979.1292 | 632.3303 | 586.4012 | 595.8119 | 556.5103
3980.1292 | 631.3942 | 589.5288 | 594.4551 | 554.8555
3981.1292 | 630.8529 | 588.4461 | 593.65 | 555.8125
3982.1292 | 630.4362 | 586.2638 | 591.3656 | 554.3058
3983.1292 | 630.5196 | 586.752 | 589.7192 | 552.0139
3984.1448 | 629.9876 | 586.7549 | 588.5432 | 552.1268
3985.1292 | 629.8453 | 586.3456 | 588.0224 | 555.9512
3986.1292 | 629.6131 | 585.3887 | 588.4725 | 555.2176
3987.1292 | 629.8148 | 587.0551 | 589.6077 | 554.3011
3988.1292 | 629.9766 | 588.7439 | 589.7084 | 553.8564
3989.1292 | 629.4764 | 588.0818 | 588.5342 | 552.676
3990.1292 | 628.8583 | 585.87 | 586.3623 | 552.6944
3991.1292 | 627.4836 | 584.691 | 584.7542 | 553.1144
3992.1292 | 626.6982 | 587.2878 | 584.0676 | 553.2199
3993.1292 | 626.9057 | 587.6373 | 584.0411 | 556.3864
3994.1292 | 627.2434 | 585.8461 | 582.6506 | 553.8652
3995.1292 | 628.7188 | 586.7056 | 582.8306 | 552.2915
3996.1292 | 629.7155 | 587.6503 | 582.187 | 551.9074
3997.1292 | 630.7013 | 587.2147 | 583.715 | 551.2871
3998.1292 | 630.8511 | 586.5854 | 583.568 | 550.6689
3999.1292 | 631.2304 | 587.6204 | 584.286 | 550.1731
4000.1292 | 631.2723 | 587.7195 | 584.6263 | 551.3663
4001.1292 | 631.8373 | 589.2094 | 584.5738 | 550.0194
4002.1292 | 630.65 | 590.6436 | 583.4514 | 549.7661
4003.1292 | 630.0352 | 592.2735 | 583.9073 | 551.7084
4004.1292 | 630.3733 | 594.3525 | 584.422 | 549.3733
4005.1292 | 630.0612 | 595.2705 | 583.6871 | 548.5155
4006.1292 | 630.5384 | 593.2307 | 583.4733 | 547.5217
4007.1292 | 631.4154 | 592.4555 | 583.9333 | 547.1663
4008.1292 | 632.0631 | 592.6836 | 583.411 | 546.4668
4009.1292 | 633.269 | 592.0275 | 584.3179 | 546.9511
4010.1292 | 633.3059 | 591.8498 | 584.0654 | 547.4701
4011.1292 | 633.4382 | 591.9862 | 583.9431 | 546.2691
4012.1292 | 633.4593 | 592.4442 | 585.8613 | 550.6193
4013.1292 | 633.3818 | 592.5847 | 586.5301 | 549.4593
4014.1292 | 633.4287 | 592.8762 | 587.7281 | 549.2873
4015.1292 | 633.3209 | 594.4617 | 586.6233 | 547.9717
4016.1292 | 632.2602 | 592.1 | 585.4623 | 547.5104
4017.1292 | 632.3375 | 591.6827 | 585.569 | 546.2872
4018.1292 | 632.82 | 592.5098 | 587.409 | 547.8274
4019.1292 | 633.3477 | 592.6767 | 589.6875 | 549.1822
4020.1292 | 633.7445 | 592.5108 | 590.3706 | 547.9409
4021.1292 | 633.1924 | 591.8605 | 589.5423 | 546.6071
4022.1292 | 632.6104 | 591.6742 | 589.6136 | 546.1772
4023.1292 | 632.4446 | 592.278 | 588.1815 | 557.1095
4024.1292 | 632.1069 | 592.7811 | 587.2275 | 555.902
4025.1292 | 632.0427 | 590.5612 | 586.7072 | 557.6478
4026.1292 | 631.9339 | 588.8941 | 588.8113 | 556.753
4027.1292 | 631.9799 | 590.7828 | 588.0895 | 554.7931
4028.1292 | 631.838 | 591.3435 | 589.5836 | 553.2477
4029.1292 | 631.5385 | 590.0193 | 588.943 | 552.3296
4030.1292 | 632.3109 | 594.6235 | 595.0914 | 553.1619
4031.1292 | 631.8154 | 594.52 | 595.1134 | 556.0818
4032.1292 | 631.3358 | 593.0282 | 592.5928 | 556.0472
4033.1292 | 630.5221 | 593.6575 | 592.5379 | 556.4494
4034.1292 | 630.2785 | 592.1612 | 590.724 | 557.2799
4035.1292 | 629.9916 | 589.8051 | 589.5806 | 555.0188
4036.1292 | 630.0864 | 588.5538 | 589.2618 | 553.8754
4037.1292 | 630.6385 | 589.1445 | 588.5131 | 551.9357
4038.1292 | 630.7905 | 589.0714 | 589.3194 | 551.2358
4039.1292 | 631.1779 | 589.5205 | 589.6396 | 550.8019
4040.1292 | 630.8344 | 590.5211 | 589.6022 | 550.2436
4041.1292 | 630.9764 | 589.2149 | 589.3078 | 552.5345
4042.1292 | 631.6193 | 587.2454 | 589.1427 | 551.448
4043.1292 | 631.9521 | 587.4638 | 590.6639 | 550.8978
4044.1292 | 631.9989 | 586.5686 | 589.9166 | 550.7175
4045.1292 | 631.8382 | 588.4257 | 591.4097 | 551.4038
4046.1292 | 632.1189 | 588.6938 | 589.2292 | 549.2072
4047.1292 | 630.7135 | 589.633 | 588.0976 | 549.0127
4048.1292 | 630.2832 | 587.3195 | 585.9578 | 548.0214
4049.1292 | 629.7409 | 587.2892 | 585.563 | 546.9701
4050.1292 | 629.4187 | 588.5317 | 585.486 | 548.5024
4051.1292 | 629.9141 | 589.5439 | 586.0543 | 549.8747
4052.1292 | 629.4257 | 588.9325 | 585.8422 | 549.1808
4053.1292 | 629.1832 | 587.7309 | 585.0057 | 547.8323
4054.1292 | 628.6258 | 589.5336 | 584.1849 | 546.6149
4055.1292 | 629.142 | 589.4203 | 584.1335 | 545.6975
4056.1292 | 628.7154 | 588.9908 | 583.808 | 545.2683
4057.1292 | 628.7225 | 588.0203 | 583.6206 | 545.2454
4058.1292 | 628.8959 | 587.1014 | 583.9252 | 544.7357
4059.1292 | 628.3381 | 586.8256 | 583.482 | 544.6686
4060.1292 | 628.5961 | 585.3281 | 583.4563 | 544.1255
4061.1292 | 629.0151 | 584.7665 | 582.9005 | 544.7815
4062.1292 | 628.9177 | 584.728 | 583.7944 | 545.1364
4063.1292 | 628.8346 | 583.6114 | 583.6362 | 543.9378
4064.1292 | 629.1634 | 584.5126 | 583.522 | 543.8497
4065.1292 | 628.4864 | 586.4494 | 583.7892 | 543.2052
4066.1292 | 628.4894 | 585.8537 | 583.8227 | 543.0689
4067.1292 | 628.7174 | 587.3075 | 585.2951 | 543.1831
4068.1292 | 628.8598 | 589.1159 | 586.1503 | 544.7271
4069.1292 | 629.6033 | 591.643 | 591.2007 | 545.9571
4070.1292 | 630.1186 | 594.795 | 593.5657 | 548.8841
4071.1292 | 629.9958 | 595.7292 | 594.3603 | 548.4349
4072.1292 | 630.0954 | 594.9512 | 593.4451 | 547.2618
4073.1292 | 629.3067 | 594.3019 | 591.849 | 546.4245
4074.1292 | 628.6275 | 592.7089 | 589.8787 | 547.3482
4075.1292 | 628.2402 | 592.4699 | 588.6154 | 545.1637
4076.1292 | 627.9648 | 592.5987 | 589.9568 | 544.7696
4077.1292 | 627.7035 | 592.5042 | 588.4741 | 545.4
4078.1292 | 627.6237 | 592.3365 | 586.9166 | 544.1209
4079.1292 | 628.1679 | 592.084 | 586.2637 | 543.0702
4080.1292 | 628.5888 | 593.5729 | 583.9077 | 542.1734
4081.1292 | 628.3113 | 593.4003 | 583.2773 | 541.1775
4082.1292 | 627.6987 | 593.0995 | 582.3163 | 540.9584
4083.1292 | 628.3336 | 592.9721 | 581.3609 | 540.993
4084.1292 | 629.5737 | 592.8078 | 581.1199 | 541.651
4085.1292 | 630.2559 | 593.1445 | 582.6179 | 541.7736
4086.1292 | 629.7634 | 591.5456 | 582.7966 | 541.9425
4087.1292 | 629.6864 | 591.5416 | 582.3595 | 542.3985
4088.1292 | 628.9475 | 592.1835 | 581.8776 | 541.5945
4089.1292 | 628.9505 | 591.1405 | 582.2651 | 539.6732
4090.1292 | 629.3853 | 592.7 | 581.4114 | 538.2477
4091.1292 | 628.6559 | 594.1589 | 579.1646 | 542.8599
4092.1292 | 628.3138 | 593.6905 | 578.9645 | 541.7652
4093.1292 | 628.6048 | 595.076 | 584.5547 | 542.7315
4094.1292 | 628.428 | 595.0277 | 585.5599 | 542.7968
4095.1292 | 628.8119 | 593.7865 | 585.0995 | 541.7368
4096.1292 | 628.9707 | 593.4675 | 586.2014 | 543.7425
4097.1292 | 629.0729 | 594.3258 | 585.8092 | 542.8752
4098.1292 | 629.8701 | 595.1588 | 585.8979 | 542.3877
4099.1292 | 628.7582 | 595.9414 | 586.6138 | 542.8712
4100.1292 | 628.8292 | 595.5285 | 586.2865 | 542.5315
4101.1292 | 628.5284 | 594.0824 | 584.9941 | 542.6536
4102.1292 | 629.5972 | 592.0113 | 584.8855 | 541.2801
4103.1292 | 631.6562 | 593.96 | 588.1644 | 541.5769
4104.1292 | 632.5384 | 594.5965 | 589.9921 | 544.8925
4105.1292 | 632.3612 | 594.3054 | 590.1066 | 549.2046
4106.1292 | 632.1968 | 593.4468 | 592.9958 | 552.0601
4107.1292 | 632.9319 | 591.4243 | 592.8621 | 551.8018
4108.1292 | 632.9432 | 591.726 | 592.8554 | 552.151
4109.1292 | 633.3605 | 593.3794 | 592.456 | 550.852
4110.1292 | 634.0429 | 594.5503 | 591.9623 | 549.6798
4111.1292 | 633.7918 | 596.5451 | 593.9036 | 552.0514
4112.1292 | 633.8108 | 596.6157 | 594.3279 | 551.7889
4113.1292 | 633.9933 | 595.1623 | 593.4214 | 550.7904
4114.1292 | 634.0283 | 595.5359 | 593.6985 | 549.9904
4115.1292 | 633.8139 | 599.2316 | 594.9606 | 551.3365
4116.1292 | 633.5997 | 599.4962 | 597.0878 | 552.5205
4117.1292 | 633.5651 | 599.3565 | 598.1203 | 556.2211
4118.1292 | 634.6948 | 596.9333 | 598.6086 | 554.3272
4119.1292 | 635.7475 | 597.3449 | 600.4337 | 555.2271
4120.1292 | 636.1047 | 599.3352 | 600.981 | 556.072
4121.1292 | 635.4312 | 599.7002 | 601.5832 | 556.3596
4122.1292 | 635.4167 | 598.8959 | 601.3113 | 554.474
4123.1292 | 635.015 | 598.0215 | 599.8407 | 554.0726
4124.1292 | 636.9822 | 599.7816 | 602.0096 | 553.809
4125.1292 | 637.4391 | 597.74 | 601.996 | 555.2418
4126.1292 | 636.7903 | 596.7914 | 600.2188 | 554.7143
4127.1292 | 636.3044 | 597.066 | 600.9231 | 553.2289
4128.1292 | 636.2801 | 596.013 | 601.764 | 552.7888
4129.1292 | 636.5732 | 593.9672 | 601.4833 | 552.7997
4130.1292 | 636.518 | 598.0825 | 604.251 | 553.5417
4131.1292 | 635.9367 | 597.0886 | 603.3327 | 552.0434
4132.1292 | 636.3484 | 595.3043 | 603.0295 | 551.5869
4133.1292 | 638.2068 | 594.1039 | 602.275 | 552.7891
4134.1292 | 640.1183 | 595.9045 | 604.0381 | 553.6663
4135.1292 | 638.3004 | 595.6054 | 601.9469 | 555.1847
4136.1292 | 638.4507 | 596.0096 | 600.7504 | 552.5174
4137.1292 | 637.6634 | 597.5234 | 600.0916 | 552.0833
4138.1292 | 637.175 | 597.7338 | 598.5152 | 550.0641
4139.1292 | 637.5238 | 600.8864 | 599.5117 | 550.2132
4140.1292 | 637.9358 | 600.6432 | 599.9401 | 549.9936
4141.1292 | 637.8701 | 602.7205 | 600.1945 | 550.6038
4142.1292 | 637.3814 | 602.6155 | 599.5713 | 549.738
4143.1292 | 636.5588 | 602.2036 | 598.3551 | 548.7938
4144.1292 | 636.7173 | 604.3828 | 600.3618 | 549.4519
4145.1292 | 636.6856 | 606.011 | 601.1305 | 549.6386
4146.1292 | 636.4281 | 603.3992 | 599.6135 | 548.7951
4147.1292 | 636.9467 | 604.4727 | 598.7592 | 547.2761
4148.1292 | 637.6125 | 604.4861 | 598.8147 | 546.7122
4149.1292 | 637.7677 | 604.0269 | 598.3929 | 546.6207
4150.1292 | 637.7947 | 604.5614 | 599.4988 | 547.6285
4151.1292 | 638.1547 | 604.8852 | 598.7208 | 548.273
4152.1292 | 638.6137 | 606.2875 | 597.7343 | 547.7458
4153.1292 | 638.7399 | 607.0463 | 596.6071 | 546.5621
4154.1292 | 638.2579 | 605.5174 | 594.8565 | 545.1607
4155.1292 | 637.326 | 603.8747 | 594.8044 | 545.1989
4156.1292 | 637.9628 | 604.0104 | 596.0597 | 546.1793
4157.1292 | 638.4431 | 605.5321 | 596.5067 | 545.5673
4158.1292 | 637.7024 | 605.5959 | 596.39 | 546.0625
4159.1292 | 637.3235 | 605.3124 | 596.3598 | 546.1837
4160.1292 | 637.2496 | 605.3826 | 595.3381 | 544.5777
4161.1292 | 636.9873 | 604.7617 | 593.7976 | 544.312
4162.1292 | 638.3008 | 603.3229 | 593.1354 | 543.5257
4163.1292 | 638.9529 | 602.7306 | 593.4532 | 543.7425
4164.1448 | 638.5283 | 601.8339 | 593.7025 | 543.0535
4165.1292 | 637.8552 | 600.806 | 594.1379 | 543.6181
4166.1292 | 636.9082 | 598.7642 | 593.1733 | 543.9786
4167.1292 | 636.6952 | 597.7715 | 592.7031 | 544.7566
4168.1292 | 636.5707 | 597.8452 | 592.9227 | 544.7431
4169.1292 | 636.4379 | 598.2784 | 592.5826 | 548.2752
4170.1292 | 635.4751 | 599.3599 | 592.1382 | 546.7244
4171.1292 | 635.5175 | 601.0981 | 591.7911 | 546.9126
4172.1292 | 636.5874 | 599.5886 | 592.2852 | 546.0292
4173.1292 | 636.8792 | 598.0435 | 592.0366 | 545.8408
4174.1292 | 636.4858 | 597.5963 | 592.4223 | 544.8307
4175.1292 | 636.1602 | 595.3021 | 593.731 | 544.685
4176.1292 | 636.3265 | 594.1403 | 594.2864 | 544.9176
4177.1292 | 635.9539 | 591.9542 | 594.6101 | 547.3753
4178.1292 | 635.2684 | 590.4945 | 594.5266 | 548.6817
4179.1292 | 634.9401 | 588.3723 | 595.8984 | 549.5985
4180.1292 | 635.3444 | 585.3619 | 595.6428 | 549.2926
4181.1292 | 635.4435 | 585.9516 | 596.5708 | 549.0607
4182.1292 | 635.3862 | 588.783 | 598.5289 | 548.9941
4183.1292 | 634.9564 | 588.2312 | 600.4502 | 549.1742
4184.1292 | 634.3945 | 586.1725 | 598.8849 | 547.086
4185.1292 | 633.5747 | 584.493 | 597.3779 | 546.8757
4186.1292 | 632.7248 | 586.1732 | 597.5192 | 547.6776
4187.1292 | 632.3457 | 584.9579 | 595.9311 | 547.4972
4188.1292 | 632.1751 | 584.5878 | 594.3572 | 546.7726
4189.1292 | 632.0074 | 584.0433 | 594.5995 | 547.2661
4190.1292 | 632.8162 | 585.4497 | 596.0032 | 547.445
4191.1292 | 632.9197 | 587.2438 | 598.0075 | 548.4572
4192.1292 | 633.1602 | 587.9006 | 598.0157 | 549.7624
4193.1292 | 634.1667 | 587.7803 | 599.2501 | 550.9913
4194.1292 | 634.4309 | 590.7032 | 600.2642 | 551.3581
4195.1292 | 634.4705 | 592.0587 | 599.5726 | 549.7601
4196.1292 | 634.3723 | 590.6865 | 597.2396 | 546.8608
4197.1292 | 633.7265 | 592.3042 | 596.3626 | 545.1375
4198.1292 | 636.4725 | 594.2764 | 599.0511 | 544.7698
4199.1292 | 635.9717 | 592.1705 | 596.84 | 543.8493
4200.1292 | 635.2002 | 591.8707 | 597.3085 | 548.2314
4201.1292 | 634.8593 | 591.1674 | 597.909 | 547.7034
4202.1292 | 634.9159 | 590.4455 | 598.6021 | 549.6373
4203.1292 | 635.2304 | 589.4305 | 599.0144 | 551.7886
4204.1292 | 636.3341 | 587.6556 | 599.3278 | 553.4257
4205.1292 | 637.4041 | 588.9748 | 600.3225 | 553.2766
4206.1292 | 637.8018 | 590.1825 | 599.9655 | 552.5687
4207.1292 | 636.246 | 590.2285 | 597.6613 | 550.4472
4208.1292 | 635.7725 | 590.6554 | 596.4017 | 549.0287
4209.1292 | 636.4946 | 591.3556 | 596.269 | 549.9092
4210.1292 | 636.5614 | 590.2278 | 596.9697 | 553.1642
4211.1292 | 636.4313 | 592.8092 | 595.8197 | 552.2021
4212.1292 | 635.7408 | 593.6214 | 594.9124 | 550.9107
4213.1292 | 635.577 | 593.3247 | 594.5974 | 549.5285
4214.1292 | 635.5828 | 591.9194 | 593.4564 | 548.4447
4215.1292 | 636.9277 | 594.4507 | 593.6638 | 548.2969
4216.1292 | 636.7328 | 595.7606 | 592.8893 | 546.9985
4217.1292 | 637.5994 | 599.2796 | 593.6002 | 546.8871
4218.1292 | 640.1302 | 600.0842 | 593.5081 | 546.3725
4219.1292 | 641.2208 | 599.2518 | 593.9981 | 546.1564
4220.1292 | 639.6083 | 598.8015 | 592.6903 | 545.0571
4221.1292 | 639.5117 | 598.7522 | 591.9585 | 543.8469
4222.1292 | 638.7694 | 599.2882 | 590.1204 | 543.2307
4223.1292 | 638.0422 | 599.4523 | 589.8821 | 543.095
4224.1292 | 638.3818 | 601.554 | 591.2418 | 543.2248
4225.1292 | 639.912 | 603.326 | 592.186 | 543.4027
4226.1292 | 638.1503 | 600.8354 | 589.4584 | 542.0596
4227.1292 | 637.9044 | 600.647 | 590.5483 | 541.9213
4228.1292 | 638.3523 | 601.9879 | 595.006 | 543.2167
4229.1292 | 638.0442 | 601.2292 | 595.5623 | 542.9355
4230.1292 | 637.9897 | 599.9008 | 594.3944 | 541.9152
4231.1292 | 638.2296 | 599.941 | 594.1008 | 540.7305
4232.1292 | 639.2472 | 602.6998 | 593.5163 | 538.5216
4233.1292 | 640.5678 | 603.3291 | 593.5108 | 538.0414
4234.1292 | 641.7546 | 602.7261 | 595.6156 | 538.5136
4235.1292 | 640.8903 | 603.8047 | 598.0157 | 540.8947
4236.1292 | 640.3095 | 601.9544 | 597.4477 | 541.5746
4237.1292 | 640.6293 | 600.1572 | 598.2586 | 543.3474
4238.1292 | 639.7351 | 600.8451 | 596.9079 | 542.9228
4239.1292 | 638.8421 | 602.7173 | 597.2312 | 543.494
4240.1292 | 638.1881 | 601.5908 | 595.7508 | 542.341
4241.1292 | 638.0234 | 600.7337 | 594.9285 | 541.3842
4242.1292 | 637.2732 | 602.2428 | 593.0613 | 542.036
4243.1292 | 635.7886 | 600.6136 | 590.2227 | 540.146
4244.1292 | 634.6114 | 599.456 | 589.2855 | 539.5943
4245.1292 | 634.638 | 599.8656 | 589.9213 | 541.751
4246.1292 | 634.7758 | 598.7585 | 590.2265 | 540.8338
4247.1292 | 635.9645 | 599.3885 | 590.3265 | 540.6898
4248.1292 | 635.9383 | 600.5225 | 589.3141 | 540.6723
4249.1292 | 637.9212 | 600.4924 | 590.2162 | 540.1364
4250.1292 | 638.5493 | 600.2726 | 590.0068 | 540.4976
4251.1292 | 639.6172 | 601.6092 | 590.6376 | 541.5326
4252.1292 | 639.5503 | 600.6126 | 590.8492 | 541.7189
4253.1292 | 641.3802 | 599.8909 | 592.8223 | 544.1824
4254.1292 | 644.0682 | 602.7673 | 595.7445 | 546.2096
4255.1292 | 644.2358 | 603.583 | 596.1445 | 545.0937
4256.1292 | 644.8388 | 601.9743 | 596.6599 | 544.9473
4257.1292 | 644.8785 | 600.9433 | 597.7121 | 545.7521
4258.1292 | 643.8819 | 601.3636 | 597.8591 | 545.7582
4259.1292 | 643.9727 | 602.1213 | 599.8088 | 546.7849
4260.1292 | 643.5181 | 600.6789 | 599.342 | 546.7541
4261.1292 | 643.0465 | 598.4962 | 599.1459 | 546.5091
4262.1292 | 641.6915 | 596.4021 | 599.2516 | 546.1001
4263.1292 | 641.3557 | 594.8159 | 598.2665 | 544.6948
4264.1292 | 639.7155 | 593.0722 | 597.4084 | 543.8216
4265.1292 | 638.7606 | 592.7259 | 596.0868 | 542.5302
4266.1292 | 638.19 | 591.4473 | 594.2913 | 541.6275
4267.1292 | 636.6592 | 591.1691 | 593.1081 | 541.404
4268.1292 | 635.7773 | 590.6338 | 592.3776 | 540.7211
4269.1292 | 635.5147 | 591.1627 | 593.7427 | 541.1083
4270.1292 | 635.4395 | 590.8016 | 592.117 | 540.8929
4271.1292 | 635.1138 | 590.9211 | 592.9202 | 540.8694
4272.1292 | 635.8362 | 590.5485 | 591.9607 | 540.3178
4273.1292 | 636.4016 | 592.8016 | 592.8837 | 540.7909
4274.1292 | 635.9051 | 593.5074 | 593.027 | 540.268
4275.1292 | 635.2949 | 594.074 | 592.1849 | 539.7182
4276.1292 | 634.206 | 593.3835 | 590.6549 | 538.6288
4277.1292 | 633.8162 | 595.1496 | 591.6821 | 538.2101
4278.1292 | 633.7115 | 596.6704 | 591.7819 | 538.2031
4279.1292 | 633.1211 | 595.6301 | 590.5588 | 537.3185
4280.1292 | 632.3264 | 597.2857 | 591.0416 | 536.4391
4281.1292 | 631.8383 | 596.1464 | 590.3254 | 535.9586
4282.1292 | 632.5621 | 595.3539 | 589.6722 | 535.7829
4283.1292 | 632.3341 | 595.2708 | 588.9622 | 538.1034
4284.1292 | 633.3257 | 595.0902 | 589.618 | 538.7838
4285.1292 | 634.0938 | 594.9532 | 590.4325 | 539.0356
4286.1292 | 634.2166 | 595.389 | 592.2864 | 542.9852
4287.1292 | 635.4844 | 595.1382 | 594.5623 | 543.9771
4288.1292 | 635.5643 | 595.6426 | 595.8849 | 544.1314
4289.1292 | 634.8266 | 597.6204 | 594.5588 | 542.2527
4290.1292 | 632.5512 | 601.371 | 592.3618 | 540.5587
4291.1292 | 631.3444 | 601.1472 | 590.2809 | 538.6418
4292.1292 | 631.7004 | 600.8986 | 591.9167 | 537.2588
4293.1292 | 631.9926 | 600.3758 | 593.1796 | 536.9303
4294.1292 | 632.1257 | 600.2233 | 591.281 | 536.568
4295.1292 | 632.3506 | 599.7375 | 590.0959 | 536.1199
4296.1292 | 631.814 | 598.8717 | 588.3904 | 535.9474
4297.1292 | 631.9462 | 600.1391 | 589.0645 | 536.4014
4298.1292 | 631.8975 | 601.803 | 592.6066 | 536.6381
4299.1292 | 632.0927 | 600.4556 | 592.2557 | 537.2146
4300.1292 | 632.795 | 601.4261 | 592.2175 | 536.1486
4301.1292 | 632.7262 | 600.3339 | 591.3596 | 536.0354
4302.1292 | 633.1058 | 599.0828 | 591.1769 | 536.0929
4303.1292 | 633.7231 | 604.754 | 595.3804 | 538.2121
4304.1292 | 633.9799 | 603.8486 | 594.9978 | 541.5426
4305.1292 | 634.0948 | 601.8758 | 595.491 | 541.9214
4306.1292 | 634.4091 | 601.7616 | 599.2086 | 543.0518
4307.1292 | 633.8138 | 600.4815 | 602.3584 | 546.2865
4308.1292 | 634.2623 | 601.854 | 605.5348 | 552.1495
4309.1292 | 633.6032 | 602.6186 | 604.3235 | 549.0642
4310.1292 | 632.5022 | 603.0806 | 601.469 | 546.5151
4311.1292 | 632.3407 | 603.0982 | 599.6591 | 544.5043
4312.1292 | 632.054 | 601.0983 | 597.0327 | 542.2517
4313.1292 | 632.5222 | 599.8742 | 597.1568 | 541.6224
4314.1292 | 632.7679 | 599.8324 | 596.7799 | 541.2574
4315.1292 | 632.6866 | 599.9113 | 597.9892 | 541.928
4316.1292 | 632.3975 | 597.9704 | 596.2513 | 541.3456
4317.1292 | 634.6417 | 598.3323 | 598.5017 | 542.5042
4318.1292 | 636.1066 | 599.4252 | 602.3808 | 543.5814
4319.1292 | 636.2872 | 600.3225 | 603.7898 | 544.6164
4320.1292 | 636.0991 | 599.277 | 602.9583 | 544.0168
4321.1292 | 635.7051 | 597.3904 | 601.4617 | 543.605
4322.1292 | 635.2065 | 599.726 | 600.8056 | 543.2382
4323.1292 | 635.9085 | 600.0103 | 601.0348 | 543.7376
4324.1292 | 635.8686 | 597.7435 | 600.1233 | 543.8615
4325.1292 | 635.7462 | 597.6366 | 599.6717 | 543.8991
4326.1292 | 634.8047 | 596.4238 | 597.6911 | 542.4205
4327.1292 | 633.6315 | 599.3462 | 598.4114 | 542.0816
4328.1292 | 632.0333 | 600.8859 | 597.892 | 541.9244
4329.1292 | 630.9825 | 601.3385 | 595.7011 | 540.6558
4330.1292 | 630.459 | 600.6113 | 592.4931 | 539.9117
4331.1292 | 630.5167 | 599.0682 | 591.5333 | 538.4959
4332.1292 | 630.4418 | 596.896 | 590.2298 | 538.5783
4333.1292 | 631.1732 | 596.2172 | 591.0697 | 538.8781
4334.1292 | 633.3184 | 597.9744 | 591.48 | 540.0139
4335.1292 | 633.6911 | 597.5336 | 590.5271 | 537.5361
4336.1292 | 633.556 | 599.1041 | 590.4762 | 536.3017
4337.1292 | 632.6646 | 601.3722 | 592.7753 | 537.3422
4338.1292 | 633.3478 | 601.7547 | 594.8872 | 542.8609
4339.1292 | 633.9904 | 601.2324 | 596.5172 | 542.348
4340.1292 | 633.9917 | 601.7488 | 594.8835 | 541.8723
4341.1292 | 633.2527 | 601.8898 | 595.8078 | 541.6834
4342.1292 | 633.031 | 600.5615 | 594.6622 | 542.0488
4343.1292 | 632.782 | 597.4416 | 593.1985 | 540.6874
4344.1292 | 633.2954 | 596.9729 | 592.9549 | 539.3804
4345.1292 | 633.0586 | 598.0625 | 593.82 | 540.1689
4346.1292 | 633.2738 | 599.5006 | 594.5624 | 540.8485
4347.1292 | 633.5035 | 599.4883 | 594.2965 | 539.5356
4348.1292 | 634.4051 | 599.0981 | 594.0973 | 539.1477
4349.1448 | 633.9845 | 599.6249 | 594.7894 | 539.0592
4350.1292 | 634.0979 | 598.702 | 594.9144 | 539.7763
4351.1292 | 634.8628 | 597.2278 | 595.0037 | 540.7706
4352.1292 | 636.3174 | 597.7897 | 598.2466 | 543.4798
4353.1292 | 636.6395 | 597.3702 | 598.9119 | 543.5154
4354.1292 | 636.4932 | 598.9419 | 599.1184 | 543.3929
4355.1292 | 636.503 | 598.6304 | 598.9853 | 542.415
4356.1292 | 636.997 | 600.5957 | 599.912 | 542.1419
4357.1292 | 637.3583 | 601.1066 | 599.6504 | 541.6115
4358.1292 | 637.2838 | 601.6458 | 598.8099 | 541.0963
4359.1292 | 638.1034 | 601.0753 | 601.5003 | 542.7878
4360.1292 | 637.7429 | 600.6139 | 603.2801 | 546.1876
4361.1292 | 638.5664 | 600.0907 | 603.1621 | 545.5072
4362.1292 | 639.0405 | 599.364 | 603.1882 | 546.5792
4363.1292 | 639.6862 | 601.794 | 605.2528 | 547.625
4364.1292 | 640.3239 | 602.3391 | 605.281 | 549.9462
4365.1292 | 640.1473 | 603.1621 | 604.8172 | 550.309
4366.1292 | 639.1886 | 602.4572 | 601.6672 | 548.5362
4367.1292 | 641.7223 | 604.6677 | 605.0415 | 547.6221
4368.1292 | 642.3316 | 604.9069 | 605.6351 | 547.2775
4369.1292 | 640.8154 | 604.6236 | 603.0655 | 545.9735
4370.1292 | 639.7663 | 604.8941 | 602.0274 | 545.1531
4371.1292 | 639.1719 | 606.1688 | 602.4483 | 546.1247
4372.1292 | 638.732 | 604.5647 | 601.1601 | 545.5616
4373.1292 | 638.4799 | 603.1307 | 600.3309 | 544.9568
4374.1292 | 638.851 | 604.089 | 601.5886 | 544.8115
4375.1292 | 638.7819 | 606.3088 | 606.8155 | 547.0634
4376.1292 | 638.0755 | 605.1092 | 604.2156 | 545.8108
4377.1292 | 636.9977 | 605.2841 | 603.8211 | 544.4083
4378.1292 | 636.7919 | 604.3283 | 605.7024 | 545.5422
4379.1448 | 636.6633 | 601.8569 | 605.2054 | 544.5889
4380.1292 | 636.4798 | 599.5116 | 603.8399 | 542.8873
4381.1292 | 637.2747 | 599.5878 | 603.3558 | 541.7959
4382.1292 | 637.1581 | 598.7724 | 601.7844 | 541.4603
4383.1292 | 636.3753 | 598.4712 | 600.0525 | 540.6698
4384.1292 | 635.767 | 599.1485 | 597.9678 | 539.7657
4385.1292 | 634.5008 | 599.4303 | 595.5642 | 538.7462
4386.1292 | 634.3172 | 599.2707 | 594.5779 | 537.335
4387.1292 | 633.3137 | 599.0276 | 593.0534 | 536.1976
4388.1292 | 632.7218 | 598.3479 | 591.8147 | 535.182
4389.1292 | 632.7423 | 602.305 | 595.1481 | 536.7811
4390.1292 | 632.6454 | 599.8442 | 593.5296 | 536.353
4391.1292 | 632.5352 | 598.1463 | 591.6511 | 535.0605
4392.1292 | 632.6708 | 598.4703 | 590.9 | 533.3805
4393.1292 | 632.9784 | 598.3911 | 590.978 | 532.4399
4394.1292 | 633.0258 | 598.3976 | 594.1301 | 533.7862
4395.1292 | 633.0369 | 597.3931 | 592.6701 | 533.5994
4396.1292 | 633.832 | 597.0137 | 591.5151 | 532.9148
4397.1292 | 634.3407 | 598.5469 | 592.5809 | 533.526
4398.1292 | 633.2792 | 597.6624 | 591.6683 | 533.0027
4399.1292 | 634.6197 | 599.3404 | 592.919 | 532.5741
4400.1292 | 635.0015 | 599.4866 | 593.8538 | 532.5301
4401.1292 | 634.3858 | 599.0683 | 592.0551 | 531.1158
4402.1292 | 632.6021 | 597.9557 | 589.6024 | 529.5896
4403.1292 | 632.0399 | 597.9892 | 588.6884 | 528.9191
4404.1292 | 634.1748 | 600.0205 | 590.6615 | 529.5685
4405.1292 | 634.1782 | 599.2002 | 591.8988 | 529.9376
4406.1292 | 634.6482 | 599.0614 | 592.788 | 531.6544
4407.1292 | 636.2315 | 599.3923 | 594.3074 | 532.5153
4408.1292 | 635.8883 | 598.2804 | 594.5141 | 532.4349
4409.1292 | 636.7012 | 599.1209 | 595.4426 | 533.5305
4410.1292 | 635.9437 | 600.4519 | 595.897 | 533.9354
4411.1292 | 635.3866 | 599.5919 | 593.5328 | 532.4649
4412.1292 | 636.4945 | 599.8547 | 594.0517 | 532.4726
4413.1292 | 638.5502 | 600.4544 | 596.0991 | 533.1917
4414.1292 | 638.489 | 601.517 | 596.518 | 534.722
4415.1292 | 637.8287 | 601.0099 | 594.8249 | 533.2197
4416.1292 | 637.5466 | 601.8157 | 595.4786 | 533.0533
4417.1292 | 637.7851 | 602.3302 | 596.414 | 532.5271
4418.1292 | 637.9045 | 603.2583 | 596.8592 | 534.0007
4419.1292 | 637.8779 | 605.2469 | 598.8285 | 534.5333
4420.1292 | 638.5426 | 604.0729 | 599.8174 | 534.7267
4421.1292 | 638.3337 | 606.0858 | 601.0538 | 534.9123
4422.1292 | 637.9064 | 605.6584 | 601.2258 | 533.8439
4423.1292 | 637.0029 | 604.1142 | 599.4327 | 532.8765
4424.1292 | 636.5148 | 602.2914 | 597.5613 | 531.9803
4425.1292 | 636.6302 | 600.769 | 595.391 | 530.3529
4426.1292 | 636.8062 | 601.608 | 595.403 | 530.3078
4427.1292 | 635.4326 | 600.9872 | 594.6516 | 529.8989
4428.1292 | 635.6309 | 600.7217 | 594.2845 | 531.8379
4429.1292 | 635.9265 | 600.2095 | 594.6111 | 531.5473
4430.1292 | 636.3682 | 600.2744 | 596.3551 | 532.4273
4431.1292 | 636.6679 | 599.8757 | 598.0536 | 533.0459
4432.1292 | 636.9006 | 600.5098 | 598.8417 | 533.313
4433.1292 | 636.8887 | 599.2819 | 599.7349 | 533.7301
4434.1292 | 637.2804 | 598.317 | 598.3241 | 533.2942
4435.1292 | 637.2386 | 599.1851 | 598.2503 | 533.2421
4436.1292 | 636.7696 | 598.9626 | 597.9963 | 532.8227
4437.1292 | 636.5964 | 598.5026 | 598.3486 | 533.0984
4438.1292 | 636.81 | 598.589 | 598.448 | 534.0094
4439.1448 | 636.3802 | 598.6444 | 596.3159 | 533.2195
4440.1292 | 636.8755 | 597.4384 | 596.0457 | 533.5247
4441.1292 | 637.0592 | 597.0586 | 597.0347 | 535.2924
4442.1292 | 636.2086 | 600.2449 | 599.1439 | 537.786
4443.1292 | 635.201 | 598.2715 | 596.4022 | 536.7544
4444.1292 | 635.2143 | 597.6904 | 596.4038 | 536.2023
4445.1292 | 636.2841 | 597.2363 | 596.7699 | 537.6628
4446.1292 | 636.8611 | 597.1294 | 599.1517 | 539.398
4447.1292 | 637.657 | 596.1762 | 598.8111 | 538.6954
4448.1292 | 638.5489 | 597.435 | 602.5879 | 539.6485
4449.1292 | 638.8656 | 596.7644 | 604.1073 | 539.3359
4450.1292 | 639.5631 | 597.9694 | 603.7854 | 540.2271
4451.1292 | 640.1343 | 598.2212 | 603.1715 | 539.6835
4452.1292 | 639.7913 | 596.8404 | 603.2317 | 539.7781
4453.1292 | 639.3111 | 595.2425 | 602.501 | 540.4993
4454.1292 | 639.2325 | 595.7637 | 601.1433 | 539.6735
4455.1292 | 639.0452 | 597.616 | 602.9101 | 540.3805
4456.1292 | 638.3359 | 597.5378 | 603.4517 | 540.9891
4457.1292 | 637.267 | 596.7248 | 602.7542 | 540.8048
4458.1292 | 636.838 | 595.7148 | 602.3844 | 541.4345
4459.1292 | 636.6716 | 594.1539 | 602.8931 | 542.203
4460.1292 | 635.7584 | 592.4721 | 602.1306 | 543.9144
4461.1292 | 635.11 | 590.1134 | 599.766 | 542.2959
4462.1292 | 634.4094 | 589.8375 | 598.923 | 541.4409
4463.1292 | 633.4043 | 588.7397 | 597.9383 | 540.5451
4464.1292 | 632.9497 | 587.6378 | 597.628 | 540.3068
4465.1292 | 632.5934 | 589.4729 | 596.8794 | 539.0943
4466.1292 | 632.3078 | 588.7481 | 596.027 | 538.1084
4467.1292 | 631.7609 | 586.8075 | 593.9778 | 538.2582
4468.1292 | 631.5718 | 585.6503 | 593.5145 | 537.6446
4469.1448 | 631.8499 | 586.9176 | 595.3982 | 538.0471
4470.1292 | 631.741 | 588.6368 | 598.1984 | 538.5303
4471.1292 | 630.9203 | 588.2944 | 596.8033 | 538.221
4472.1292 | 631.04 | 587.983 | 595.6639 | 536.4531
4473.1292 | 632.0284 | 589.097 | 596.8723 | 538.8176
4474.1292 | 633.4413 | 589.661 | 597.7662 | 539.6884
4475.1292 | 632.6155 | 589.2807 | 595.1027 | 537.8835
4476.1292 | 632.2629 | 588.4094 | 592.64 | 537.2919
4477.1292 | 631.7444 | 588.2206 | 591.5659 | 536.0065
4478.1292 | 630.689 | 589.9567 | 591.2688 | 535.3812
4479.1292 | 631.4352 | 591.4458 | 591.038 | 535.1738
4480.1292 | 631.2456 | 592.8094 | 589.4286 | 534.6759
4481.1292 | 629.9054 | 591.9168 | 588.7802 | 533.2063
4482.1292 | 629.8764 | 592.2296 | 590.4615 | 534.5046
4483.1292 | 630.9205 | 594.942 | 593.3324 | 533.8949
4484.1292 | 631.5167 | 596.894 | 594.9085 | 536.3682
4485.1292 | 632.9111 | 596.6369 | 595.3824 | 536.4574
4486.1292 | 633.5666 | 597.7212 | 594.4244 | 535.6261
4487.1292 | 632.8154 | 597.4645 | 593.3871 | 534.9763
4488.1292 | 633.5202 | 598.8137 | 593.1258 | 535.4904
4489.1292 | 635.2521 | 598.8626 | 593.7207 | 536.2538
4490.1292 | 635.3632 | 598.2023 | 593.3346 | 535.2025
4491.1292 | 635.6105 | 599.6267 | 594.0249 | 535.5965
4492.1292 | 635.4428 | 600.9163 | 593.4833 | 536.0517
4493.1292 | 635.4431 | 600.2434 | 594.7028 | 535.1371
4494.1292 | 635.363 | 600.9266 | 594.5293 | 534.5439
4495.1292 | 634.8681 | 601.3883 | 594.6578 | 534.2111
4496.1292 | 634.6504 | 602.1254 | 595.1682 | 534.6032
4497.1292 | 634.1875 | 602.9817 | 595.059 | 534.597
4498.1292 | 634.3856 | 601.0913 | 594.7649 | 533.6809
4499.1448 | 635.6663 | 600.4582 | 597.4075 | 535.2268
4500.1292 | 637.7428 | 600.7835 | 598.7181 | 535.906
4501.1292 | 638.7549 | 602.6844 | 598.5495 | 536.2238