## Test Conditions
DESIREE-FIRE Intermediate Scale Test 11 - Circuit Simulator Data Only
Test Date: | 2009-11-25
DCSim DAQ Start Time | 13:25
DCSim Time for Synchronization | 13:28
Heat Source Synchronization | 0:02 | hour:minutes:seconds
Heat Source DAQ Start Time | 13:26
Fire Time | 15:38
Offset | 2:13 | hour:minutes:seconds | This is the time after the DCSim DAQ was started and the heat source was initiated.
| 7980 | seconds
Heat Source Offset | 2:12 | hour:minutes:seconds | This is the time after the Heat Source DAQ was started and the heat source was initiated.
| 7945 | seconds
Heat Source Stop Time | 16:53
Test Duration | 1:15 | hour:minutes:seconds
| 4500 | seconds
CT500 turns | 2 | 1 or 2 | This is the number of times the lead conductor within the DCSim Panels were wrapped around the Hall Effect Device of the current transducer.
CT35 turns | 5 | 1 or 5
Pre-Test Baseline: | Gathered | Gathered or Not Gathered
Cable Information: | Record info about cable type on each circuit and which of the cable thermocouples corresponds to cable and air temperature
Unit Number | Cable Type |  | Cable TC Channel | Air TC Channel
SOV 1 | EPR/CPE, 7c, 12AWG |  | Cable thermocouples were not used for this test. | Channel 1 which is defined as "B Position - Middle" in the Temperature Data File respresents the temperature in the center of the cable tray.
SOV 2 | EPR/CPE, 7c, 12AWG |  | Cable thermocouples were not used for this test. | Channel 5, 6, and 7 represents the air temperature 3', 5', and 7' down the cable tray located in D-Position. These are labeled as "D-Position - 3'", "D-Position - Middle", " D-Position - 7'", respectively.
A Note on Data Conversion and Accuracy:
Two different types of voltage transducers were used for each circuit. A bidirectional transducer (Ohio Semitronics, model number VT7-005X5-11) produces a 0 - 5V output signal which is directly proportional to the DC input ranging from 0 - 150VDC. The accuracy of this device is +/-0.25% full scale at DC and the response time is 50 mircoseconds. The unidirectional DC voltage isolator (Ohio Semitronics, model number VTU-005X5) used throughout tests also produces a 0 - 5V output over a 0 - 150VDC range. The accuracy of this device is +/-0.25% Rdg., +/-1% full scale at DC and the response time is 500 microseconds. Two different current transducers were for each circuit. One current transducer (Ohio Semitronics, model number CTL-51/35) was used to detect lower (0 - 35A) amperage transient behavior through a paired and calibrated signal conditioner (CTA201RX5). The other transducer (Ohio Semitronics, model number CTL-601/500) was set to detect transient current increases from 0 - 500A. These were also paired and calibrated with a signal conditioner (CTA2-1X5).
The readings were monitored using a National Instruments SCXI-1100 modules attached to SCXI-1300 multiplexers and housed within a SCXI-1001, 12-slot chassis. The "Raw Data" worksheet has been previously converted by LabView program created for this test series. The nominal zero point readings for each current transducer was taken before each test due to an electromagnetic effect created by direct current power. Zero Point values are provided, and the full run is documented in a separate data sheet (see "Current Offsets" worksheet). The converted data are presented as nominal indications of circuit path voltage and current. The data gathering equipment (transducers and DAQ card) have not been subject to specific calibration beyond that provided by the manufacturers. The accuracy of the converted data is estimated at +/-2%.

## Electrical Data
Fire Time (s) | Ground_VT7_1 | Ground_VTU_1 | Ground_VTU_2 | SOV-1_CT500 | SOV-1_CT35_1_P | SOV-1_CT35_2_S1 | SOV-1_CT35_3_G | SOV-1_CT35_4_S2 | SOV-1_CT35_5_N | SOV-2_CT500 | SOV-2_CT35_1_P | SOV-2_CT35_2_S1 | SOV-2_CT35_3_G | SOV-2_CT35_4_S2 | SOV-2_CT35_5_N | SOV-1_VT7_1_R | SOV-1_VT7_2_SP | SOV-1_VT7_3_S | SOV-1_VTU_1_P | SOV-1_VTU_2_S1 | SOV-1_VTU_3_G | SOV-1_VTU_4_N | SOV-2_VT7_1_R | SOV-2_VT7_2_SP | SOV-2_VT7_3_S | SOV-2_VTU_1_P | SOV-2_VTU_2_S1 | SOV-2_VTU_3_G | SOV-2_VTU_4_N | {SOV1} V(N) - V(Batt -) | {SOV1} V(P) - V(Batt +) | {SOV1} V(R) - V(Batt -) | {SOV1} V(S) - V(Batt -) | {SOV1} V(S) - V(N) | {SOV1} V(S1) - V(Batt +) | {SOV1} V(G) - V(Batt +) | {SOV2} V(N) - V(Batt -) | {SOV2} V(P) - V(Batt +) | {SOV2} V(R) - V(Batt -) | {SOV2} V(S) - V(Batt -) | {SOV2} V(S) - V(N) | {SOV2} V(S1) - V(Batt +) | {SOV2} V(G) - V(Batt +) | {SOV1} V(P) - V(Batt -) | {SOV1} V(S1) - V(Batt -) | {SOV1} V(G) - V(Batt -) | {SOV1} V(SP) - V(Batt -) | {SOV1} V(N) - V(Batt +) | {SOV2} V(P) - V(Batt -) | {SOV2} V(S1) - V(Batt -) | {SOV1} V(G) - V(Batt -) | {SOV2} V(SP) - V(Batt -) | {SOV2} V(N) - V(Batt +)
-0.42188 | 122.9324 | -62.3428 | 60.2417 | 1.4211e-13 | -0.0093547 | -0.013077 | 0.017225 | -0.035301 | 0.033158 | -0.00083919 | -0.012803 | 0.01173 | 0.035777 | -0.010355 | 0.041188 | -62.3474 | 0.015142 | -62.3325 | 60.2488 | 60.0438 | 60.1491 | -62.3181 | -62.3244 | 0.082776 | -62.4275 | 60.0765 | 60.2178 | 60.0195 | -62.4544 | 0.024719 | 0.007072 | -0.004604 | 0.010292 | -0.014427 | -0.1979 | -0.092568 | -0.11154 | -0.16517 | 0.018483 | -0.084703 | 0.026841 | -0.023948 | -0.2222 | 122.5916 | 122.3866 | 122.492 | 62.358 | -122.5598 | 122.4194 | 122.5606 | 122.3623 | 62.4256 | -122.6961
1.3125 | 122.8409 | -62.3932 | 60.2921 | 1.4211e-13 | -0.0093547 | -0.012863 | 0.017011 | -0.035515 | 0.032945 | 0.0067908 | -0.012803 | 0.01173 | 0.035991 | -0.0099273 | 0.040974 | -62.3337 | 0.010564 | -62.3325 | 60.2488 | 60.0438 | 60.1446 | -62.3181 | -62.3152 | 0.078197 | -62.4275 | 60.0674 | 60.2223 | 60.0241 | -62.4635 | 0.075073 | -0.043282 | 0.059485 | 0.060646 | -0.014427 | -0.24826 | -0.1475 | -0.070348 | -0.22468 | 0.077994 | -0.034349 | 0.035999 | -0.069723 | -0.26798 | 122.642 | 122.437 | 122.5377 | 62.4038 | -122.6102 | 122.4606 | 122.6155 | 122.4173 | 62.4714 | -122.7556
3.0781 | 122.8317 | -62.3611 | 60.3195 | 1.4211e-13 | -0.0093547 | -0.013291 | 0.017225 | -0.035301 | 0.033158 | 0.014421 | -0.01259 | 0.011516 | 0.03535 | -0.010355 | 0.041188 | -62.3429 | 0.015142 | -62.328 | 60.2396 | 60.0346 | 60.1446 | -62.3227 | -62.3106 | 0.082776 | -62.423 | 60.0674 | 60.2132 | 60.0103 | -62.4544 | 0.038451 | -0.079904 | 0.018285 | 0.033181 | -0.00527 | -0.28488 | -0.17497 | -0.093233 | -0.25215 | 0.05053 | -0.061813 | 0.03142 | -0.10635 | -0.30918 | 122.6008 | 122.3958 | 122.5057 | 62.3763 | -122.6422 | 122.4285 | 122.5743 | 122.3715 | 62.4439 | -122.7739
4.7969 | 122.8363 | -62.3657 | 60.3699 | 1.4211e-13 | -0.0095683 | -0.013077 | 0.017225 | -0.035515 | 0.033372 | 0.0067908 | -0.012803 | 0.011089 | 0.035777 | -0.010141 | 0.040974 | -62.3383 | 0.010564 | -62.328 | 60.2396 | 60.0438 | 60.14 | -62.3181 | -62.3198 | 0.082776 | -62.423 | 60.0628 | 60.2223 | 60.0195 | -62.4498 | 0.047608 | -0.13026 | 0.027441 | 0.037759 | -0.009849 | -0.32608 | -0.2299 | -0.084076 | -0.30708 | 0.045951 | -0.057235 | 0.026841 | -0.14754 | -0.35038 | 122.6053 | 122.4095 | 122.5057 | 62.3763 | -122.688 | 122.4285 | 122.5881 | 122.3852 | 62.4485 | -122.8197
6.5625 | 122.8546 | -62.3566 | 60.3149 | 1.4211e-13 | -0.0093547 | -0.013291 | 0.017225 | -0.035515 | 0.032945 | 0.0067908 | -0.012376 | 0.011303 | 0.035777 | -0.010141 | 0.041188 | -62.3337 | 0.010564 | -62.328 | 60.2396 | 60.0346 | 60.1491 | -62.3135 | -62.3106 | 0.082776 | -62.4275 | 60.0765 | 60.2132 | 60.0241 | -62.4498 | 0.043031 | -0.075326 | 0.022864 | 0.028603 | -0.014428 | -0.2803 | -0.16581 | -0.093232 | -0.23841 | 0.045952 | -0.07097 | 0.022262 | -0.10177 | -0.29087 | 122.5962 | 122.3912 | 122.5057 | 62.3671 | -122.6285 | 122.4331 | 122.5697 | 122.3806 | 62.4393 | -122.7647
8.2812 | 122.9416 | -62.3474 | 60.2463 | 1.4211e-13 | -0.0091411 | -0.013077 | 0.017011 | -0.035515 | 0.033158 | -0.00083919 | -0.012803 | 0.011516 | 0.035777 | -0.010141 | 0.041188 | -62.3429 | 0.001407 | -62.3371 | 60.2396 | 60.0484 | 60.1446 | -62.3135 | -62.3244 | 0.082776 | -62.423 | 60.072 | 60.2223 | 60.0241 | -62.4498 | 0.033876 | -0.006662 | 0.004552 | 0.010291 | -0.023585 | -0.1979 | -0.10173 | -0.10239 | -0.17432 | 0.023061 | -0.075546 | 0.026841 | -0.023947 | -0.22221 | 122.587 | 122.3958 | 122.492 | 62.3488 | -122.5598 | 122.4194 | 122.5697 | 122.3715 | 62.4302 | -122.6961
10.0469 | 122.9004 | -62.3657 | 60.2737 | 1.4211e-13 | -0.0093547 | -0.013291 | 0.016798 | -0.035729 | 0.033158 | -0.00083919 | -0.01259 | 0.011303 | 0.035564 | -0.0099273 | 0.040761 | -62.3291 | 0.010564 | -62.3325 | 60.2442 | 60.0392 | 60.1491 | -62.3181 | -62.3152 | 0.078197 | -62.4184 | 60.0765 | 60.2178 | 60.0103 | -62.4544 | 0.047608 | -0.02955 | 0.036598 | 0.033181 | -0.014427 | -0.23453 | -0.12461 | -0.088655 | -0.19721 | 0.050529 | -0.052656 | 0.035999 | -0.055992 | -0.26341 | 122.6099 | 122.4049 | 122.5149 | 62.3763 | -122.5919 | 122.4423 | 122.5835 | 122.3761 | 62.4439 | -122.7281
11.8281 | 122.7997 | -62.3474 | 60.2875 | 1.4211e-13 | -0.0095683 | -0.013077 | 0.017011 | -0.035088 | 0.032731 | -0.00083919 | -0.012803 | 0.011303 | 0.035777 | -0.0097135 | 0.040547 | -62.3337 | 0.010564 | -62.3325 | 60.2442 | 60.0392 | 60.14 | -62.3181 | -62.3152 | 0.087354 | -62.4184 | 60.072 | 60.2269 | 60.0103 | -62.4498 | 0.029297 | -0.043283 | 0.013709 | 0.01487 | -0.014427 | -0.24826 | -0.1475 | -0.10239 | -0.21552 | 0.032218 | -0.070967 | 0.03142 | -0.060568 | -0.27714 | 122.5916 | 122.3866 | 122.4874 | 62.358 | -122.6056 | 122.4194 | 122.5743 | 122.3577 | 62.4348 | -122.7373
13.6094 | 122.8271 | -62.3703 | 60.2692 | 1.4211e-13 | -0.0091411 | -0.013077 | 0.017225 | -0.035301 | 0.032731 | -0.00083919 | -0.01259 | 0.011516 | 0.036205 | -0.0099273 | 0.040974 | -62.3383 | 0.010564 | -62.3371 | 60.2442 | 60.0392 | 60.14 | -62.3135 | -62.3106 | 0.082776 | -62.4138 | 60.0628 | 60.2132 | 60.0195 | -62.4498 | 0.056764 | -0.024972 | 0.032018 | 0.033179 | -0.023585 | -0.22995 | -0.12919 | -0.079499 | -0.20637 | 0.059685 | -0.043501 | 0.035998 | -0.055993 | -0.24967 | 122.6145 | 122.4095 | 122.5103 | 62.3809 | -122.5827 | 122.4331 | 122.5835 | 122.3898 | 62.4531 | -122.719
15.3281 | 122.9599 | -62.3291 | 60.2737 | 1.4211e-13 | -0.0093547 | -0.013077 | 0.017011 | -0.035301 | 0.032945 | 0.014421 | -0.01259 | 0.011516 | 0.035991 | -0.0099273 | 0.040974 | -62.3337 | 0.010564 | -62.328 | 60.2442 | 60.0346 | 60.1491 | -62.3135 | -62.3198 | 0.078197 | -62.4184 | 60.072 | 60.2178 | 60.0058 | -62.4498 | 0.015566 | -0.02955 | -0.004601 | 0.001138 | -0.014428 | -0.2391 | -0.12461 | -0.1207 | -0.20179 | 0.00933 | -0.089277 | 0.03142 | -0.055992 | -0.26799 | 122.5733 | 122.3637 | 122.4782 | 62.3397 | -122.5873 | 122.4011 | 122.5469 | 122.3349 | 62.4073 | -122.7235
17.0312 | 122.7997 | -62.3245 | 60.3424 | 1.4211e-13 | -0.0091411 | -0.013291 | 0.017225 | -0.035301 | 0.032945 | -0.0084697 | -0.012803 | 0.011516 | 0.035777 | -0.0099273 | 0.040974 | -62.3383 | 0.015142 | -62.3325 | 60.2442 | 60.0346 | 60.14 | -62.309 | -62.3106 | 0.078197 | -62.4138 | 60.072 | 60.2132 | 60.0058 | -62.4452 | 0.015567 | -0.098214 | -0.013758 | -0.008018 | -0.023585 | -0.30777 | -0.20243 | -0.1207 | -0.27045 | 0.013909 | -0.089277 | 0.031419 | -0.12924 | -0.33665 | 122.5687 | 122.3592 | 122.4645 | 62.3397 | -122.6514 | 122.3965 | 122.5377 | 122.3303 | 62.4027 | -122.7876
18.8125 | 122.8043 | -62.3337 | 60.3378 | 1.4211e-13 | -0.0093547 | -0.012863 | 0.017225 | -0.035515 | 0.032945 | -0.00083919 | -0.01259 | 0.011303 | 0.035777 | -0.010141 | 0.040974 | -62.3383 | 0.015142 | -62.3234 | 60.2396 | 60.0346 | 60.1446 | -62.3044 | -62.306 | 0.087354 | -62.423 | 60.0674 | 60.2178 | 60.0103 | -62.4544 | 0.0293 | -0.098215 | -0.004603 | 0.010293 | -0.019007 | -0.30319 | -0.19328 | -0.1207 | -0.27046 | 0.027643 | -0.089279 | 0.03142 | -0.12008 | -0.32749 | 122.5733 | 122.3683 | 122.4782 | 62.3488 | -122.6422 | 122.4011 | 122.5514 | 122.344 | 62.421 | -122.7922
20.5938 | 122.9004 | -62.3245 | 60.2829 | 1.4211e-13 | -0.0095683 | -0.013077 | 0.016798 | -0.035729 | 0.033158 | 0.0067908 | -0.012803 | 0.011303 | 0.035777 | -0.010141 | 0.040761 | -62.3291 | 0.005985 | -62.3234 | 60.2396 | 60.0346 | 60.1491 | -62.3135 | -62.306 | 0.082776 | -62.4092 | 60.0674 | 60.2132 | 60.0103 | -62.4498 | 0.010988 | -0.043283 | -0.004601 | 0.001138 | -0.00985 | -0.24826 | -0.13377 | -0.12528 | -0.21552 | 0.018488 | -0.084698 | 0.040577 | -0.069726 | -0.27256 | 122.5641 | 122.3592 | 122.4737 | 62.3305 | -122.5964 | 122.3919 | 122.5377 | 122.3349 | 62.4073 | -122.7327
22.3594 | 122.9599 | -62.3108 | 60.2692 | 1.4211e-13 | -0.0093547 | -0.013077 | 0.016798 | -0.035515 | 0.032731 | -0.00083919 | -0.012376 | 0.011303 | 0.03535 | -0.0099273 | 0.040974 | -62.3337 | 0.005985 | -62.328 | 60.2488 | 60.0392 | 60.1354 | -62.309 | -62.3106 | 0.078197 | -62.423 | 60.072 | 60.2223 | 60.0058 | -62.4498 | 0.001834 | -0.020394 | -0.022912 | -0.017173 | -0.019007 | -0.22995 | -0.13377 | -0.13901 | -0.19721 | 0.000176 | -0.11217 | 0.026841 | -0.046835 | -0.26341 | 122.5596 | 122.35 | 122.4462 | 62.3168 | -122.5781 | 122.3827 | 122.5331 | 122.3165 | 62.389 | -122.719
24.125 | 122.8683 | -62.3337 | 60.2646 | 1.4211e-13 | -0.0093547 | -0.012863 | 0.017011 | -0.035301 | 0.033158 | 0.0067908 | -0.013017 | 0.011303 | 0.035564 | -0.0097135 | 0.040974 | -62.3383 | 0.015142 | -62.328 | 60.2396 | 60.0392 | 60.1491 | -62.3044 | -62.3106 | 0.082776 | -62.4184 | 60.072 | 60.2178 | 60.0103 | -62.4406 | 0.0293 | -0.024972 | -0.004603 | 0.005715 | -0.023585 | -0.22537 | -0.11546 | -0.10696 | -0.19263 | 0.023064 | -0.0847 | 0.022262 | -0.046836 | -0.25425 | 122.5733 | 122.3729 | 122.4828 | 62.3488 | -122.569 | 122.4056 | 122.5514 | 122.344 | 62.4165 | -122.7052
25.8438 | 122.7722 | -62.3611 | 60.3058 | 1.4211e-13 | -0.0091411 | -0.013077 | 0.017011 | -0.035088 | 0.033372 | 0.014421 | -0.01259 | 0.011303 | 0.035777 | -0.0099273 | 0.040761 | -62.3337 | 0.005985 | -62.328 | 60.235 | 60.0346 | 60.14 | -62.3044 | -62.3152 | 0.082776 | -62.4138 | 60.0582 | 60.2178 | 60.0103 | -62.4452 | 0.056766 | -0.07075 | 0.027442 | 0.033181 | -0.023585 | -0.27115 | -0.16581 | -0.084075 | -0.24757 | 0.045951 | -0.052656 | 0.031419 | -0.088035 | -0.29545 | 122.5962 | 122.3958 | 122.5011 | 62.3671 | -122.6102 | 122.4194 | 122.5789 | 122.3715 | 62.4439 | -122.751
27.6406 | 122.7905 | -62.3566 | 60.3378 | 1.4211e-13 | -0.0093547 | -0.013077 | 0.016584 | -0.035729 | 0.032731 | 0.0067908 | -0.01259 | 0.011516 | 0.035777 | -0.010141 | 0.040974 | -62.3337 | 0.010564 | -62.328 | 60.235 | 60.0346 | 60.1354 | -62.3044 | -62.306 | 0.087354 | -62.4184 | 60.0674 | 60.2132 | 60.0103 | -62.4452 | 0.052188 | -0.10279 | 0.022864 | 0.028603 | -0.023585 | -0.30319 | -0.20243 | -0.088653 | -0.27046 | 0.050531 | -0.061812 | 0.026841 | -0.12466 | -0.32749 | 122.5916 | 122.3912 | 122.492 | 62.3671 | -122.6422 | 122.4239 | 122.5697 | 122.3669 | 62.4439 | -122.7831
29.3594 | 122.9141 | -62.3291 | 60.2829 | 1.4211e-13 | -0.0091411 | -0.012863 | 0.017011 | -0.035942 | 0.032945 | 0.014421 | -0.012376 | 0.011516 | 0.035564 | -0.0099273 | 0.040974 | -62.3383 | 0.010564 | -62.3234 | 60.235 | 60.0301 | 60.14 | -62.309 | -62.3152 | 0.082776 | -62.4092 | 60.0628 | 60.2178 | 60.0012 | -62.4406 | 0.020145 | -0.047862 | -0.00918 | 0.005716 | -0.014429 | -0.25284 | -0.14293 | -0.11154 | -0.2201 | 0.013908 | -0.08012 | 0.031419 | -0.065147 | -0.28172 | 122.5641 | 122.3592 | 122.4691 | 62.3397 | -122.5919 | 122.3919 | 122.5469 | 122.3303 | 62.4119 | -122.7235
31.1094 | 122.7997 | -62.3566 | 60.3241 | 1.4211e-13 | -0.0089273 | -0.013077 | 0.017011 | -0.035515 | 0.032731 | 0.0067908 | -0.012376 | 0.011303 | 0.03535 | -0.010141 | 0.040974 | -62.3337 | 0.010564 | -62.3234 | 60.2396 | 60.0346 | 60.1446 | -62.2998 | -62.3106 | 0.082776 | -62.4092 | 60.0674 | 60.2178 | 60.0058 | -62.4406 | 0.056767 | -0.084482 | 0.022864 | 0.033181 | -0.023586 | -0.28946 | -0.17955 | -0.084074 | -0.25672 | 0.045952 | -0.052655 | 0.031419 | -0.10635 | -0.31834 | 122.5962 | 122.3912 | 122.5011 | 62.3671 | -122.6239 | 122.4239 | 122.5743 | 122.3623 | 62.4393 | -122.7647
32.8906 | 122.8226 | -62.3291 | 60.3241 | 1.4211e-13 | -0.0091411 | -0.012863 | 0.017011 | -0.035301 | 0.032731 | -0.00083919 | -0.01259 | 0.01173 | 0.035777 | -0.0099273 | 0.040974 | -62.3383 | 0.010564 | -62.3234 | 60.235 | 60.0346 | 60.1354 | -62.309 | -62.306 | 0.078197 | -62.4138 | 60.0674 | 60.2178 | 60.0058 | -62.4406 | 0.020145 | -0.089061 | -0.00918 | 0.005716 | -0.014429 | -0.28946 | -0.1887 | -0.11154 | -0.25672 | 0.023066 | -0.084699 | 0.02684 | -0.10635 | -0.31834 | 122.5641 | 122.3637 | 122.4645 | 62.3397 | -122.6331 | 122.3965 | 122.5469 | 122.3349 | 62.4073 | -122.7647
34.6719 | 122.7859 | -62.3428 | 60.3378 | 1.4211e-13 | -0.0091411 | -0.013077 | 0.017225 | -0.035088 | 0.032731 | -0.00083919 | -0.01259 | 0.011303 | 0.035564 | -0.0097135 | 0.040761 | -62.32 | 0.010564 | -62.3234 | 60.2259 | 60.0301 | 60.1446 | -62.3044 | -62.306 | 0.082776 | -62.4184 | 60.0628 | 60.2178 | 60.0058 | -62.4498 | 0.038455 | -0.11195 | 0.022866 | 0.019448 | -0.019007 | -0.30777 | -0.19328 | -0.10696 | -0.27503 | 0.036798 | -0.075545 | 0.03142 | -0.12008 | -0.33207 | 122.5687 | 122.3729 | 122.4874 | 62.3534 | -122.6422 | 122.4056 | 122.5606 | 122.3486 | 62.4256 | -122.7876
36.4531 | 122.7722 | -62.3611 | 60.3149 | 1.4211e-13 | -0.0093547 | -0.013077 | 0.016798 | -0.035301 | 0.032517 | -0.00083919 | -0.01259 | 0.011303 | 0.035777 | -0.0099273 | 0.040761 | -62.3245 | 0.005985 | -62.3234 | 60.2305 | 60.0301 | 60.14 | -62.3044 | -62.306 | 0.082776 | -62.4092 | 60.0582 | 60.2132 | 60.0149 | -62.4406 | 0.056766 | -0.084483 | 0.036599 | 0.037759 | -0.019007 | -0.28488 | -0.17497 | -0.079496 | -0.25672 | 0.055109 | -0.048077 | 0.031419 | -0.10177 | -0.30003 | 122.5916 | 122.3912 | 122.5011 | 62.3671 | -122.6193 | 122.4194 | 122.5743 | 122.3761 | 62.4439 | -122.7556
38.2344 | 122.8683 | -62.3291 | 60.2966 | 1.4211e-13 | -0.0093547 | -0.012863 | 0.017011 | -0.035515 | 0.03209 | 0.0067908 | -0.012803 | 0.011303 | 0.03535 | -0.0099273 | 0.040761 | -62.3245 | 0.010564 | -62.3234 | 60.235 | 60.0346 | 60.14 | -62.309 | -62.3015 | 0.078197 | -62.4138 | 60.0628 | 60.2086 | 60.0058 | -62.4452 | 0.020145 | -0.061595 | 0.004556 | 0.005716 | -0.014429 | -0.26199 | -0.15666 | -0.11612 | -0.23384 | 0.027645 | -0.084699 | 0.031419 | -0.088037 | -0.29087 | 122.5641 | 122.3637 | 122.4691 | 62.3397 | -122.6056 | 122.3919 | 122.5377 | 122.3349 | 62.4073 | -122.7419
40 | 122.7768 | -62.3474 | 60.3149 | 1.4211e-13 | -0.0093547 | -0.012863 | 0.017011 | -0.035301 | 0.032731 | 0.014421 | -0.01259 | 0.011303 | 0.035777 | -0.0097135 | 0.040974 | -62.3245 | 0.005985 | -62.3234 | 60.235 | 60.0346 | 60.1446 | -62.309 | -62.306 | 0.078197 | -62.4092 | 60.0582 | 60.2132 | 60.0058 | -62.4406 | 0.038455 | -0.079905 | 0.022866 | 0.024026 | -0.014429 | -0.2803 | -0.17039 | -0.093229 | -0.25672 | 0.041376 | -0.06181 | 0.031419 | -0.10177 | -0.30918 | 122.5824 | 122.3821 | 122.492 | 62.3534 | -122.6239 | 122.4056 | 122.5606 | 122.3532 | 62.4256 | -122.7556
41.7188 | 122.7997 | -62.3199 | 60.3333 | 1.4211e-13 | -0.0087137 | -0.013291 | 0.017225 | -0.035729 | 0.032945 | -0.00083919 | -0.01259 | 0.011516 | 0.035564 | -0.0094999 | 0.040974 | -62.3245 | 0.015142 | -62.3188 | 60.235 | 60.0301 | 60.14 | -62.3044 | -62.3015 | 0.073618 | -62.4184 | 60.0628 | 60.2132 | 60.0012 | -62.4361 | 0.015567 | -0.098216 | -0.0046 | 0.001138 | -0.014429 | -0.30319 | -0.19328 | -0.11612 | -0.27046 | 0.018489 | -0.098433 | 0.017684 | -0.12008 | -0.33207 | 122.555 | 122.35 | 122.4599 | 62.3351 | -122.6376 | 122.3827 | 122.5331 | 122.3211 | 62.3936 | -122.7693
43.4844 | 122.7631 | -62.352 | 60.3378 | 1.4211e-13 | -0.0093547 | -0.01265 | 0.017011 | -0.034874 | 0.032945 | 0.0067908 | -0.012803 | 0.011516 | 0.035564 | -0.0097135 | 0.040761 | -62.3154 | 0.010564 | -62.3234 | 60.2305 | 60.0255 | 60.1354 | -62.2998 | -62.306 | 0.082776 | -62.4138 | 60.0582 | 60.2086 | 60.0012 | -62.4406 | 0.05219 | -0.10737 | 0.0366 | 0.028604 | -0.023586 | -0.31235 | -0.20243 | -0.088651 | -0.27961 | 0.045954 | -0.061811 | 0.02684 | -0.12924 | -0.33665 | 122.5824 | 122.3775 | 122.4874 | 62.3626 | -122.6376 | 122.4102 | 122.5606 | 122.3532 | 62.4348 | -122.7785
45.1875 | 122.8867 | -62.2925 | 60.2783 | 1.4211e-13 | -0.0093547 | -0.013291 | 0.017011 | -0.035301 | 0.032945 | 0.022052 | -0.01259 | 0.011303 | 0.035777 | -0.010141 | 0.040761 | -62.3245 | 0.010564 | -62.3188 | 60.235 | 60.0301 | 60.1491 | -62.3135 | -62.306 | 0.078197 | -62.4001 | 60.0582 | 60.204 | 60.0149 | -62.4498 | -0.021056 | -0.043284 | -0.032066 | -0.026328 | -0.005272 | -0.24826 | -0.12919 | -0.15732 | -0.2201 | -0.013556 | -0.10758 | 0.049735 | -0.074305 | -0.2634 | 122.5275 | 122.3225 | 122.4416 | 62.303 | -122.5919 | 122.3507 | 122.4965 | 122.3074 | 62.3707 | -122.7281
46.9688 | 122.8363 | -62.3383 | 60.3149 | 1.4211e-13 | -0.0091411 | -0.012863 | 0.017439 | -0.035729 | 0.032517 | -0.00083919 | -0.012376 | 0.011089 | 0.035777 | -0.0092861 | 0.040761 | -62.32 | 0.015142 | -62.3234 | 60.235 | 60.0255 | 60.1354 | -62.3044 | -62.2969 | 0.073618 | -62.4092 | 60.0536 | 60.204 | 60.0103 | -62.4452 | 0.033878 | -0.079905 | 0.018289 | 0.014871 | -0.019007 | -0.28946 | -0.17955 | -0.10696 | -0.2613 | 0.041378 | -0.070965 | 0.035998 | -0.11093 | -0.3046 | 122.5733 | 122.3637 | 122.4737 | 62.3534 | -122.6193 | 122.3919 | 122.5423 | 122.3486 | 62.4119 | -122.7602
48.7344 | 122.8088 | -62.3245 | 60.3195 | 1.4211e-13 | -0.0091411 | -0.013291 | 0.016798 | -0.035515 | 0.032945 | -0.00083919 | -0.012803 | 0.011516 | 0.035564 | -0.0097135 | 0.040761 | -62.3154 | 0.010564 | -62.3188 | 60.2305 | 60.0255 | 60.1354 | -62.3044 | -62.2923 | 0.078197 | -62.4092 | 60.0536 | 60.2132 | 60.0103 | -62.4406 | 0.020145 | -0.089061 | 0.009134 | 0.005716 | -0.014429 | -0.29404 | -0.18412 | -0.11612 | -0.26588 | 0.032224 | -0.084698 | 0.031419 | -0.10635 | -0.30918 | 122.555 | 122.35 | 122.4599 | 62.3351 | -122.6239 | 122.3782 | 122.5377 | 122.3349 | 62.4027 | -122.7602
50.4531 | 122.8134 | -62.3245 | 60.3241 | 1.4211e-13 | -0.0089273 | -0.012863 | 0.017011 | -0.035515 | 0.032731 | -0.00083919 | -0.01259 | 0.010875 | 0.035991 | -0.0097135 | 0.040974 | -62.3245 | 0.010564 | -62.3234 | 60.2305 | 60.0255 | 60.1354 | -62.3044 | -62.2969 | 0.078197 | -62.4046 | 60.0536 | 60.2132 | 60.0103 | -62.4406 | 0.020145 | -0.093639 | -2.2e-05 | 0.001138 | -0.019007 | -0.29862 | -0.1887 | -0.11612 | -0.27046 | 0.027645 | -0.080119 | 0.035998 | -0.11093 | -0.31376 | 122.555 | 122.35 | 122.4599 | 62.3351 | -122.6285 | 122.3782 | 122.5377 | 122.3349 | 62.4027 | -122.7647
52.2188 | 122.8592 | -62.3199 | 60.26 | 1.4211e-13 | -0.0091411 | -0.012863 | 0.016798 | -0.035729 | 0.032517 | 0.014421 | -0.01259 | 0.011516 | 0.035777 | -0.0094999 | 0.040547 | -62.32 | 0.015142 | -62.3234 | 60.235 | 60.0301 | 60.1446 | -62.309 | -62.3015 | 0.091933 | -62.4092 | 60.0582 | 60.204 | 60.0012 | -62.4406 | 0.010989 | -0.024974 | -2.2e-05 | -0.00344 | -0.014429 | -0.22995 | -0.11546 | -0.12069 | -0.20179 | 0.018489 | -0.089276 | 0.031419 | -0.055995 | -0.25883 | 122.555 | 122.35 | 122.4645 | 62.3351 | -122.569 | 122.3782 | 122.524 | 122.3211 | 62.4119 | -122.7007
53.9844 | 122.9004 | -62.2925 | 60.2783 | 1.4211e-13 | -0.0093547 | -0.013077 | 0.017011 | -0.035515 | 0.032731 | 0.0067908 | -0.01259 | 0.011516 | 0.03535 | -0.0094999 | 0.040761 | -62.3245 | 0.010564 | -62.3188 | 60.2259 | 60.0255 | 60.1354 | -62.309 | -62.3015 | 0.082776 | -62.4046 | 60.0582 | 60.2132 | 59.992 | -62.4406 | -0.016477 | -0.052441 | -0.032066 | -0.026328 | -0.009851 | -0.25284 | -0.14292 | -0.14816 | -0.2201 | -0.008977 | -0.11216 | 0.035998 | -0.065148 | -0.2863 | 122.5184 | 122.318 | 122.4279 | 62.303 | -122.5873 | 122.3507 | 122.5057 | 122.2845 | 62.3753 | -122.719
55.75 | 122.8134 | -62.3108 | 60.3149 | 1.4211e-13 | -0.0089273 | -0.012863 | 0.016798 | -0.035729 | 0.032731 | 0.014421 | -0.012803 | 0.011303 | 0.035564 | -0.0097135 | 0.040547 | -62.3245 | 0.010564 | -62.3097 | 60.2213 | 60.0209 | 60.1354 | -62.309 | -62.2969 | 0.082776 | -62.4046 | 60.0582 | 60.2132 | 60.0058 | -62.4406 | 0.001834 | -0.09364 | -0.013755 | 0.00114 | -0.000694 | -0.29404 | -0.17955 | -0.12985 | -0.25672 | 0.013912 | -0.093852 | 0.035998 | -0.10177 | -0.30918 | 122.5321 | 122.3317 | 122.4462 | 62.3214 | -122.6239 | 122.369 | 122.524 | 122.3165 | 62.3936 | -122.7556
57.5312 | 122.8043 | -62.3062 | 60.2692 | 1.4211e-13 | -0.0093547 | -0.012863 | 0.016798 | -0.035515 | 0.032731 | 0.0067908 | -0.012803 | 0.011303 | 0.03535 | -0.0097135 | 0.040761 | -62.3245 | 0.015142 | -62.3234 | 60.2259 | 60.0255 | 60.14 | -62.2998 | -62.2923 | 0.082776 | -62.4046 | 60.0628 | 60.2132 | 60.0058 | -62.4406 | 0.006413 | -0.043286 | -0.018333 | -0.017173 | -0.023586 | -0.24368 | -0.12919 | -0.13443 | -0.20637 | 0.013913 | -0.09843 | 0.035998 | -0.055993 | -0.26341 | 122.5321 | 122.3317 | 122.4462 | 62.3214 | -122.569 | 122.369 | 122.5194 | 122.312 | 62.389 | -122.7098
59.2344 | 122.818 | -62.3199 | 60.2509 | 1.4211e-13 | -0.0089273 | -0.012863 | 0.016798 | -0.035942 | 0.032731 | 0.0067908 | -0.012803 | 0.011303 | 0.035777 | -0.0097135 | 0.040547 | -62.3245 | 0.010564 | -62.3188 | 60.235 | 60.0209 | 60.1308 | -62.3044 | -62.2969 | 0.087354 | -62.4046 | 60.0536 | 60.2178 | 60.0058 | -62.4406 | 0.015567 | -0.015818 | -0.0046 | 0.001138 | -0.014429 | -0.22995 | -0.12004 | -0.12069 | -0.19722 | 0.023067 | -0.084697 | 0.035998 | -0.033103 | -0.2451 | 122.555 | 122.3408 | 122.4508 | 62.3305 | -122.5552 | 122.3736 | 122.5377 | 122.3257 | 62.4073 | -122.6915
61.0312 | 122.7585 | -62.3611 | 60.3149 | 1.4211e-13 | -0.0091411 | -0.013077 | 0.016798 | -0.035942 | 0.032517 | 0.0067908 | -0.012803 | 0.011303 | 0.03535 | -0.0094999 | 0.040334 | -62.32 | 0.015142 | -62.3097 | 60.2305 | 60.0255 | 60.1308 | -62.2952 | -62.2969 | 0.078197 | -62.3955 | 60.0674 | 60.2086 | 60.0103 | -62.4452 | 0.065924 | -0.084483 | 0.041177 | 0.051494 | -0.01443 | -0.28946 | -0.18412 | -0.084075 | -0.24757 | 0.064266 | -0.034341 | 0.049734 | -0.10635 | -0.3046 | 122.5916 | 122.3866 | 122.492 | 62.3763 | -122.6102 | 122.4285 | 122.5697 | 122.3715 | 62.4393 | -122.7602
62.8281 | 122.8226 | -62.3154 | 60.3058 | 1.4211e-13 | -0.0093547 | -0.013077 | 0.016798 | -0.035729 | 0.032517 | 0.014421 | -0.01259 | 0.011089 | 0.035777 | -0.0099273 | 0.040547 | -62.32 | 0.010564 | -62.3097 | 60.2259 | 60.0301 | 60.1354 | -62.2906 | -62.2877 | 0.082776 | -62.4092 | 60.0536 | 60.204 | 59.9966 | -62.4406 | 0.024727 | -0.079907 | -0.004599 | 0.005718 | -0.019009 | -0.27573 | -0.17039 | -0.12527 | -0.25215 | 0.027648 | -0.093853 | 0.031419 | -0.10177 | -0.30918 | 122.5412 | 122.3454 | 122.4508 | 62.3259 | -122.5964 | 122.369 | 122.5194 | 122.312 | 62.3981 | -122.7464
64.5469 | 122.7631 | -62.3291 | 60.3058 | 1.4211e-13 | -0.0087137 | -0.012863 | 0.017011 | -0.035942 | 0.032731 | -0.0084697 | -0.01259 | 0.011089 | 0.035777 | -0.0094999 | 0.040547 | -62.3154 | 0.005985 | -62.3051 | 60.2259 | 60.0301 | 60.1354 | -62.2998 | -62.2877 | 0.082776 | -62.4046 | 60.0536 | 60.2178 | 60.0149 | -62.4361 | 0.029302 | -0.079907 | 0.013712 | 0.024029 | -0.005273 | -0.27573 | -0.17039 | -0.10696 | -0.25215 | 0.041381 | -0.075541 | 0.03142 | -0.088035 | -0.29087 | 122.555 | 122.3592 | 122.4645 | 62.3351 | -122.6056 | 122.3827 | 122.5469 | 122.344 | 62.4119 | -122.7418
66.3281 | 122.8363 | -62.3016 | 60.3012 | 1.4211e-13 | -0.0089273 | -0.013077 | 0.017225 | -0.035515 | 0.032517 | -0.00083919 | -0.013017 | 0.011303 | 0.035777 | -0.0092861 | 0.040761 | -62.3154 | 0.015142 | -62.3142 | 60.2213 | 60.0163 | 60.1308 | -62.2952 | -62.2877 | 0.078197 | -62.4001 | 60.0536 | 60.204 | 59.992 | -62.4406 | 0.006415 | -0.079907 | -0.013754 | -0.012593 | -0.019008 | -0.28489 | -0.17039 | -0.139 | -0.24757 | 0.013915 | -0.098428 | 0.040577 | -0.097193 | -0.30919 | 122.5229 | 122.318 | 122.4325 | 62.3168 | -122.5964 | 122.3553 | 122.5057 | 122.2937 | 62.3798 | -122.7418
68.1094 | 122.8226 | -62.3108 | 60.2966 | 1.4211e-13 | -0.0091411 | -0.012863 | 0.01637 | -0.035942 | 0.032517 | -0.00083919 | -0.013017 | 0.011303 | 0.03535 | -0.0094999 | 0.040974 | -62.3154 | 0.010564 | -62.3051 | 60.2259 | 60.0346 | 60.1262 | -62.3135 | -62.2877 | 0.082776 | -62.4046 | 60.0536 | 60.2086 | 60.166 | -62.4315 | -0.002745 | -0.070752 | -0.004599 | 0.005718 | 0.008463 | -0.26199 | -0.17039 | -0.12069 | -0.24299 | 0.02307 | -0.093852 | 0.026841 | -0.088037 | -0.13062 | 122.5367 | 122.3454 | 122.437 | 62.3214 | -122.6102 | 122.3644 | 122.5194 | 122.4768 | 62.3936 | -122.7281
69.8125 | 122.85 | -62.3199 | 60.2325 | 1.4211e-13 | -0.0093547 | -0.013077 | 0.017225 | -0.035942 | 0.032517 | -0.0084697 | -0.012803 | 0.011303 | 0.035564 | -0.0097135 | 0.040761 | -62.3154 | 0.010564 | -62.3142 | 60.2167 | 60.0346 | 60.14 | -62.3044 | -62.2877 | 0.082776 | -62.3909 | 60.0491 | 60.204 | 60.0103 | -62.4361 | 0.015567 | -0.015821 | 0.004556 | 0.005717 | -0.00985 | -0.1979 | -0.092571 | -0.11612 | -0.18348 | 0.032225 | -0.070961 | 0.045156 | -0.028529 | -0.22221 | 122.5367 | 122.3546 | 122.4599 | 62.3305 | -122.5369 | 122.369 | 122.524 | 122.3303 | 62.4027 | -122.6686
71.5938 | 122.8409 | -62.3428 | 60.2646 | 1.4211e-13 | -0.0091411 | -0.012863 | 0.016798 | -0.035515 | 0.032731 | 0.0067908 | -0.012803 | 0.011303 | 0.035777 | -0.0097135 | 0.040547 | -62.3154 | 0.005985 | -62.3097 | 60.2305 | 60.0301 | 60.1354 | -62.309 | -62.2923 | 0.078197 | -62.4138 | 60.0491 | 60.2086 | 60.0012 | -62.4406 | 0.033877 | -0.034129 | 0.027444 | 0.033183 | -0.000694 | -0.23453 | -0.12919 | -0.097807 | -0.21553 | 0.050534 | -0.070967 | 0.02684 | -0.055993 | -0.26341 | 122.5733 | 122.3729 | 122.4782 | 62.3488 | -122.5735 | 122.3919 | 122.5514 | 122.344 | 62.421 | -122.7052
73.375 | 122.8912 | -62.2833 | 60.2737 | 1.4211e-13 | -0.0089273 | -0.012863 | 0.016798 | -0.035942 | 0.032731 | 0.0067908 | -0.012803 | 0.011516 | 0.035564 | -0.0097135 | 0.040547 | -62.3154 | 0.015142 | -62.3051 | 60.2259 | 60.0209 | 60.1308 | -62.3044 | -62.2923 | 0.078197 | -62.3955 | 60.0536 | 60.1994 | 60.0058 | -62.4452 | -0.021054 | -0.047864 | -0.032065 | -0.021748 | -0.000694 | -0.25284 | -0.14293 | -0.1619 | -0.22011 | -0.008975 | -0.11216 | 0.049734 | -0.074306 | -0.26799 | 122.5092 | 122.3042 | 122.4141 | 62.2985 | -122.5781 | 122.337 | 122.4828 | 122.2891 | 62.3615 | -122.719
75.1562 | 122.8638 | -62.3108 | 60.2463 | 1.4211e-13 | -0.0089273 | -0.012863 | 0.016798 | -0.035515 | 0.032517 | -0.00083919 | -0.01259 | 0.011303 | 0.035564 | -0.0092861 | 0.040761 | -62.32 | 0.015142 | -62.3097 | 60.2213 | 60.0255 | 60.1262 | -62.2998 | -62.2923 | 0.082776 | -62.3955 | 60.0536 | 60.204 | 60.0012 | -62.4406 | 0.010991 | -0.024976 | -0.009177 | 0.00114 | -0.009851 | -0.2208 | -0.12004 | -0.12985 | -0.19264 | 0.018491 | -0.084695 | 0.045155 | -0.042262 | -0.2451 | 122.5321 | 122.3363 | 122.437 | 62.3259 | -122.5461 | 122.3644 | 122.5148 | 122.312 | 62.3936 | -122.6869
76.875 | 122.7997 | -62.3154 | 60.3149 | 1.4211e-13 | -0.0091411 | -0.012863 | 0.017011 | -0.035729 | 0.032731 | 0.014421 | -0.01259 | 0.011303 | 0.035777 | -0.0092861 | 0.041188 | -62.3154 | 0.005985 | -62.3097 | 60.2213 | 60.0301 | 60.1354 | -62.2906 | -62.2877 | 0.082776 | -62.3955 | 60.0536 | 60.204 | 59.9966 | -62.4315 | 0.024727 | -0.09364 | -2.1e-05 | 0.005718 | -0.019009 | -0.28488 | -0.17955 | -0.11612 | -0.2613 | 0.027648 | -0.080117 | 0.035998 | -0.11093 | -0.31834 | 122.5367 | 122.3454 | 122.4508 | 62.3214 | -122.6056 | 122.369 | 122.5194 | 122.312 | 62.3981 | -122.7464
78.6562 | 122.8546 | -62.3016 | 60.2875 | 1.4211e-13 | -0.0089273 | -0.013077 | 0.016798 | -0.035729 | 0.032517 | -0.00083919 | -0.01259 | 0.011303 | 0.035564 | -0.0094999 | 0.040761 | -62.3108 | 0.019721 | -62.3051 | 60.2259 | 60.0301 | 60.14 | -62.2998 | -62.2923 | 0.087354 | -62.3909 | 60.0491 | 60.1994 | 60.0103 | -62.4406 | 0.001836 | -0.061597 | -0.009175 | -0.003437 | -0.005273 | -0.25742 | -0.1475 | -0.139 | -0.23842 | 0.009336 | -0.089271 | 0.049734 | -0.088039 | -0.27714 | 122.5275 | 122.3317 | 122.4416 | 62.3214 | -122.5873 | 122.3507 | 122.5011 | 122.312 | 62.389 | -122.7281
80.4375 | 122.8958 | -62.2787 | 60.2463 | 1.4211e-13 | -0.0089273 | -0.013077 | 0.017011 | -0.035515 | 0.032945 | 0.014421 | -0.01259 | 0.011516 | 0.035991 | -0.0097135 | 0.040334 | -62.3062 | 0.015142 | -62.3051 | 60.2213 | 60.0163 | 60.1354 | -62.3044 | -62.2877 | 0.073618 | -62.3955 | 60.0491 | 60.204 | 60.0149 | -62.4315 | -0.025631 | -0.024976 | -0.027485 | -0.026325 | -0.000694 | -0.22995 | -0.11088 | -0.15274 | -0.19722 | -0.008973 | -0.11674 | 0.035998 | -0.042262 | -0.23136 | 122.5 | 122.2951 | 122.4141 | 62.2939 | -122.5507 | 122.3278 | 122.4828 | 122.2937 | 62.3524 | -122.6778
82.1875 | 122.7905 | -62.3245 | 60.2783 | 1.4211e-13 | -0.0091411 | -0.013077 | 0.016584 | -0.035301 | 0.032517 | -0.00083919 | -0.012803 | 0.011303 | 0.035777 | -0.0090725 | 0.040974 | -62.3062 | 0.015142 | -62.3051 | 60.2213 | 60.0209 | 60.1354 | -62.2952 | -62.2877 | 0.087354 | -62.4001 | 60.0582 | 60.204 | 59.992 | -62.4452 | 0.029303 | -0.057019 | 0.018291 | 0.019451 | -0.009852 | -0.25742 | -0.14292 | -0.1207 | -0.2201 | 0.036803 | -0.07554 | 0.045156 | -0.074305 | -0.2863 | 122.5458 | 122.3454 | 122.4599 | 62.3397 | -122.5735 | 122.3827 | 122.5285 | 122.3165 | 62.4119 | -122.7235
83.9219 | 122.7448 | -62.352 | 60.2829 | 1.4211e-13 | -0.0089273 | -0.012863 | 0.017225 | -0.035515 | 0.032517 | -0.0084697 | -0.01259 | 0.011303 | 0.035564 | -0.0090725 | 0.040761 | -62.3154 | 0.005985 | -62.3051 | 60.2213 | 60.0255 | 60.1354 | -62.2906 | -62.2831 | 0.082776 | -62.3955 | 60.0491 | 60.204 | 60.0012 | -62.4406 | 0.061348 | -0.061597 | 0.0366 | 0.046917 | -0.014431 | -0.25742 | -0.1475 | -0.088651 | -0.23384 | 0.068847 | -0.043496 | 0.045155 | -0.078883 | -0.28172 | 122.5733 | 122.3775 | 122.4874 | 62.358 | -122.5735 | 122.401 | 122.556 | 122.3532 | 62.4348 | -122.7235
85.7031 | 122.7997 | -62.3062 | 60.2966 | 1.4211e-13 | -0.0084999 | -0.012863 | 0.016798 | -0.035515 | 0.032517 | -0.00083919 | -0.012803 | 0.011089 | 0.035777 | -0.0092861 | 0.040761 | -62.3062 | 0.015142 | -62.3142 | 60.2167 | 60.0255 | 60.1308 | -62.2906 | -62.2923 | 0.087354 | -62.3909 | 60.0445 | 60.204 | 59.9966 | -62.4361 | 0.015571 | -0.079908 | -2e-05 | -0.008016 | -0.023587 | -0.27115 | -0.16581 | -0.12985 | -0.25215 | 0.013913 | -0.084694 | 0.045156 | -0.092616 | -0.30003 | 122.5229 | 122.3317 | 122.437 | 62.3214 | -122.5873 | 122.3507 | 122.5102 | 122.3028 | 62.3936 | -122.7327
87.4844 | 122.8317 | -62.2787 | 60.2966 | 1.4211e-13 | -0.0084999 | -0.01265 | 0.016798 | -0.035729 | 0.032517 | -0.00083919 | -0.013017 | 0.011089 | 0.03535 | -0.0092861 | 0.040334 | -62.3062 | 0.015142 | -62.3051 | 60.2121 | 60.0163 | 60.1308 | -62.2906 | -62.2786 | 0.073618 | -62.3863 | 60.0491 | 60.2086 | 59.9829 | -62.4361 | -0.011894 | -0.084487 | -0.027485 | -0.026325 | -0.014431 | -0.28031 | -0.16581 | -0.15731 | -0.24757 | 0.000184 | -0.10758 | 0.049735 | -0.088037 | -0.31377 | 122.4909 | 122.2951 | 122.4096 | 62.2939 | -122.5873 | 122.3278 | 122.4873 | 122.2616 | 62.3524 | -122.7327
89.25 | 122.8775 | -62.2879 | 60.2783 | 1.4211e-13 | -0.0089273 | -0.012863 | 0.017011 | -0.035515 | 0.032731 | -0.00083919 | -0.01259 | 0.011089 | 0.035777 | -0.0094999 | 0.040761 | -62.3062 | 0.010564 | -62.3097 | 60.2213 | 60.0117 | 60.1217 | -62.2952 | -62.2877 | 0.082776 | -62.3909 | 60.0399 | 60.204 | 59.9874 | -62.4315 | -0.007318 | -0.057019 | -0.01833 | -0.021748 | -0.01443 | -0.26658 | -0.15666 | -0.14358 | -0.23842 | 0.000182 | -0.103 | 0.040577 | -0.074305 | -0.29088 | 122.5092 | 122.2996 | 122.4096 | 62.2985 | -122.5735 | 122.3278 | 122.4919 | 122.2753 | 62.3707 | -122.7098
90.9531 | 122.8043 | -62.2925 | 60.3058 | 1.4211e-13 | -0.0089273 | -0.013077 | 0.016584 | -0.035729 | 0.032304 | -0.00083919 | -0.013017 | 0.011303 | 0.03535 | -0.0092861 | 0.040761 | -62.3017 | 0.010564 | -62.3051 | 60.2213 | 60.0117 | 60.1354 | -62.2952 | -62.2831 | 0.078197 | -62.3909 | 60.0445 | 60.204 | 59.992 | -62.4361 | -0.002741 | -0.084485 | -0.009174 | -0.012593 | -0.009852 | -0.29404 | -0.17039 | -0.14358 | -0.26131 | 0.009337 | -0.098427 | 0.045156 | -0.10177 | -0.31376 | 122.5138 | 122.3042 | 122.4279 | 62.303 | -122.601 | 122.337 | 122.4965 | 122.2845 | 62.3707 | -122.7418
92.7188 | 122.7493 | -62.3108 | 60.3149 | 1.4211e-13 | -0.0089273 | -0.012863 | 0.016798 | -0.035729 | 0.032517 | -0.0084697 | -0.012803 | 0.011089 | 0.035564 | -0.0092861 | 0.040547 | -62.3062 | 0.015142 | -62.3097 | 60.2213 | 60.0163 | 60.1354 | -62.2906 | -62.2831 | 0.082776 | -62.3955 | 60.0445 | 60.2086 | 59.9874 | -62.4269 | 0.020149 | -0.09364 | 0.004558 | 0.00114 | -0.019009 | -0.29862 | -0.17955 | -0.11611 | -0.27046 | 0.027648 | -0.084695 | 0.031419 | -0.10635 | -0.3275 | 122.5321 | 122.3271 | 122.4462 | 62.3259 | -122.6056 | 122.3553 | 122.5194 | 122.2982 | 62.3936 | -122.7418
94.5 | 122.7448 | -62.3383 | 60.2646 | 1.4211e-13 | -0.0091411 | -0.012863 | 0.017225 | -0.035729 | 0.032304 | 0.0067908 | -0.013017 | 0.011516 | 0.035564 | -0.0094999 | 0.040334 | -62.2925 | 0.010564 | -62.2959 | 60.2167 | 60.0163 | 60.1354 | -62.2952 | -62.2831 | 0.087354 | -62.3909 | 60.0491 | 60.204 | 59.9966 | -62.4315 | 0.043036 | -0.047864 | 0.045759 | 0.042341 | -0.000695 | -0.24826 | -0.12919 | -0.093227 | -0.21553 | 0.055114 | -0.05265 | 0.040577 | -0.060572 | -0.26799 | 122.555 | 122.3546 | 122.4737 | 62.3488 | -122.5598 | 122.3873 | 122.5423 | 122.3349 | 62.4256 | -122.6961
96.2188 | 122.7356 | -62.3062 | 60.2966 | 1.4211e-13 | -0.0084999 | -0.013077 | 0.016584 | -0.035515 | 0.032517 | 0.0067908 | -0.013017 | 0.011089 | 0.035777 | -0.0090725 | 0.040547 | -62.3108 | 0.010564 | -62.3051 | 60.2213 | 60.0117 | 60.1354 | -62.2861 | -62.2786 | 0.078197 | -62.3955 | 60.0445 | 60.1857 | 59.992 | -62.4269 | 0.02015 | -0.07533 | -0.004598 | 0.00114 | -0.01901 | -0.28489 | -0.16124 | -0.12069 | -0.25215 | 0.027649 | -0.089273 | 0.031419 | -0.11093 | -0.30461 | 122.5275 | 122.318 | 122.4416 | 62.3168 | -122.5827 | 122.3507 | 122.4919 | 122.2982 | 62.3844 | -122.7235
98.0156 | 122.7676 | -62.2879 | 60.3149 | 1.4211e-13 | -0.0091411 | -0.012863 | 0.016798 | -0.035515 | 0.032731 | -0.00083919 | -0.012803 | 0.011089 | 0.035777 | -0.0092861 | 0.040761 | -62.3062 | 0.005985 | -62.3051 | 60.2167 | 60.0117 | 60.1308 | -62.2906 | -62.2831 | 0.087354 | -62.3955 | 60.0491 | 60.204 | 59.9874 | -62.4361 | -0.002739 | -0.098218 | -0.01833 | -0.01717 | -0.014431 | -0.3032 | -0.18412 | -0.14816 | -0.26588 | 0.00476 | -0.10758 | 0.040577 | -0.11093 | -0.3275 | 122.5046 | 122.2996 | 122.4187 | 62.2939 | -122.6056 | 122.337 | 122.4919 | 122.2753 | 62.3753 | -122.751
99.7344 | 122.7493 | -62.3245 | 60.2829 | 1.4211e-13 | -0.0084999 | -0.012863 | 0.016584 | -0.036156 | 0.032517 | -0.00083919 | -0.012803 | 0.011089 | 0.03535 | -0.0092861 | 0.040761 | -62.3017 | 0.010564 | -62.3005 | 60.2121 | 60.0209 | 60.1308 | -62.2815 | -62.2786 | 0.073618 | -62.3909 | 60.0445 | 60.1994 | 59.9874 | -62.4315 | 0.04304 | -0.070754 | 0.02287 | 0.02403 | -0.01901 | -0.262 | -0.15208 | -0.10696 | -0.23842 | 0.04596 | -0.066383 | 0.040577 | -0.083461 | -0.29545 | 122.5367 | 122.3454 | 122.4553 | 62.3351 | -122.5644 | 122.369 | 122.524 | 122.312 | 62.3981 | -122.7144
101.5156 | 122.8271 | -62.3062 | 60.2554 | 1.4211e-13 | -0.0089273 | -0.013077 | 0.016798 | -0.035729 | 0.032517 | -0.00083919 | -0.012803 | 0.011089 | 0.035777 | -0.0088589 | 0.040334 | -62.3017 | 0.019721 | -62.3005 | 60.2213 | 60.0209 | 60.1308 | -62.2906 | -62.2831 | 0.078197 | -62.3817 | 60.0491 | 60.1949 | 59.9874 | -62.4361 | 0.015571 | -0.034131 | 0.004559 | 0.005719 | -0.009852 | -0.23453 | -0.12462 | -0.12985 | -0.20637 | 0.02307 | -0.075537 | 0.054313 | -0.060574 | -0.26799 | 122.5275 | 122.3271 | 122.437 | 62.3259 | -122.5461 | 122.3553 | 122.5011 | 122.2937 | 62.3844 | -122.6915
103.2812 | 122.7539 | -62.2925 | 60.3287 | 1.4211e-13 | -0.0089273 | -0.012863 | 0.01637 | -0.035729 | 0.032517 | -0.00083919 | -0.012803 | 0.011303 | 0.035564 | -0.0090725 | 0.040334 | -62.3017 | 0.010564 | -62.2959 | 60.2167 | 60.0117 | 60.1354 | -62.2906 | -62.2877 | 0.078197 | -62.3863 | 60.0445 | 60.1949 | 59.9829 | -62.4406 | 0.001838 | -0.11195 | -0.009174 | -0.003436 | -0.005274 | -0.31693 | -0.19328 | -0.14816 | -0.28419 | 0.004759 | -0.093848 | 0.054313 | -0.13382 | -0.34581 | 122.5092 | 122.3042 | 122.4279 | 62.303 | -122.6193 | 122.337 | 122.4873 | 122.2753 | 62.3707 | -122.7693
104.9844 | 122.7676 | -62.3062 | 60.2921 | 1.4211e-13 | -0.0087137 | -0.01265 | 0.016584 | -0.035729 | 0.032517 | -0.00083919 | -0.012376 | 0.011089 | 0.035564 | -0.0088589 | 0.040334 | -62.3017 | 0.010564 | -62.3051 | 60.2121 | 60.0117 | 60.1308 | -62.2861 | -62.2786 | 0.078197 | -62.3817 | 60.0307 | 60.204 | 59.9874 | -62.4315 | 0.02015 | -0.079909 | 0.004559 | 0.00114 | -0.01901 | -0.28031 | -0.16124 | -0.12527 | -0.26131 | 0.027649 | -0.075537 | 0.049734 | -0.088038 | -0.30461 | 122.5184 | 122.318 | 122.437 | 62.3168 | -122.5781 | 122.337 | 122.5102 | 122.2937 | 62.3844 | -122.7235
106.7812 | 122.7859 | -62.2971 | 60.3012 | 1.4211e-13 | -0.0084999 | -0.013077 | 0.017011 | -0.035515 | 0.032304 | 0.0067908 | -0.013017 | 0.011089 | 0.035564 | -0.0090725 | 0.040547 | -62.3017 | 0.010564 | -62.3005 | 60.2076 | 60.0163 | 60.1308 | -62.2815 | -62.2786 | 0.073618 | -62.3909 | 60.0399 | 60.204 | 59.9874 | -62.4315 | 0.015574 | -0.093642 | -0.004596 | -0.003436 | -0.01901 | -0.28489 | -0.17039 | -0.13443 | -0.26131 | 0.018494 | -0.093849 | 0.040577 | -0.097193 | -0.31376 | 122.5046 | 122.3134 | 122.4279 | 62.3076 | -122.5827 | 122.337 | 122.5011 | 122.2845 | 62.3707 | -122.7327
108.5781 | 122.8729 | -62.2879 | 60.2509 | 1.4211e-13 | -0.0084999 | -0.013077 | 0.016798 | -0.035729 | 0.032517 | -0.0084697 | -0.012803 | 0.010662 | 0.035136 | -0.0090725 | 0.040547 | -62.3017 | 0.015142 | -62.3005 | 60.2121 | 60.0117 | 60.1262 | -62.2815 | -62.2786 | 0.078197 | -62.3909 | 60.0399 | 60.204 | 59.9829 | -62.4269 | 0.006419 | -0.03871 | -0.013751 | -0.012591 | -0.01901 | -0.23911 | -0.12462 | -0.139 | -0.21095 | 0.009339 | -0.103 | 0.035998 | -0.046839 | -0.26799 | 122.5 | 122.2996 | 122.4141 | 62.303 | -122.5323 | 122.3278 | 122.4919 | 122.2708 | 62.3661 | -122.6778
110.2969 | 122.8363 | -62.3154 | 60.2371 | 1.4211e-13 | -0.0087137 | -0.01265 | 0.016798 | -0.035301 | 0.032304 | 0.0067908 | -0.013017 | 0.011089 | 0.035777 | -0.0088589 | 0.04012 | -62.2971 | 0.010564 | -62.3005 | 60.2167 | 60.0209 | 60.1308 | -62.2861 | -62.274 | 0.073618 | -62.3863 | 60.0399 | 60.1994 | 59.9966 | -62.4315 | 0.029306 | -0.020399 | 0.018293 | 0.014875 | -0.014431 | -0.21622 | -0.10631 | -0.11612 | -0.19722 | 0.041384 | -0.070959 | 0.045156 | -0.037685 | -0.24052 | 122.5321 | 122.3363 | 122.4462 | 62.3259 | -122.5232 | 122.3553 | 122.5148 | 122.312 | 62.389 | -122.6686
112.0469 | 122.85 | -62.3199 | 60.2371 | 1.4211e-13 | -0.0084999 | -0.013077 | 0.016798 | -0.035942 | 0.032304 | 0.0067908 | -0.01259 | 0.011089 | 0.035777 | -0.0090725 | 0.040761 | -62.3017 | 0.015142 | -62.3005 | 60.2076 | 60.0117 | 60.1354 | -62.2906 | -62.2786 | 0.082776 | -62.3909 | 60.0445 | 60.2086 | 59.9874 | -62.4315 | 0.029304 | -0.029556 | 0.018292 | 0.019452 | -0.009852 | -0.22538 | -0.10173 | -0.11154 | -0.19264 | 0.041382 | -0.070961 | 0.040577 | -0.028528 | -0.24968 | 122.5275 | 122.3317 | 122.4553 | 62.3351 | -122.5278 | 122.3644 | 122.5285 | 122.3074 | 62.4027 | -122.6686
113.7656 | 122.7585 | -62.3108 | 60.2829 | 1.4211e-13 | -0.0087137 | -0.012863 | 0.016798 | -0.035515 | 0.032517 | -0.00083919 | -0.012803 | 0.011089 | 0.035564 | -0.0092861 | 0.040547 | -62.2925 | 0.015142 | -62.3051 | 60.2167 | 60.0163 | 60.1262 | -62.2906 | -62.274 | 0.082776 | -62.3863 | 60.0445 | 60.1994 | 59.9874 | -62.4361 | 0.020149 | -0.066175 | 0.018293 | 0.005718 | -0.014431 | -0.26658 | -0.15666 | -0.12527 | -0.23842 | 0.036806 | -0.075537 | 0.049735 | -0.083461 | -0.29545 | 122.5275 | 122.3271 | 122.437 | 62.3259 | -122.5735 | 122.3553 | 122.5102 | 122.2982 | 62.3936 | -122.719
115.5469 | 122.7859 | -62.2925 | 60.2737 | 1.4211e-13 | -0.0084999 | -0.012863 | 0.016798 | -0.035729 | 0.032304 | -0.00083919 | -0.013231 | 0.011089 | 0.03535 | -0.0092861 | 0.040334 | -62.3017 | 0.010564 | -62.3051 | 60.2076 | 60.0117 | 60.1308 | -62.2861 | -62.2786 | 0.078197 | -62.3863 | 60.0399 | 60.1949 | 59.9874 | -62.4361 | 0.006417 | -0.066177 | -0.009174 | -0.012593 | -0.01901 | -0.262 | -0.14293 | -0.14358 | -0.23384 | 0.013916 | -0.093848 | 0.049735 | -0.078885 | -0.2863 | 122.5 | 122.3042 | 122.4233 | 62.303 | -122.5598 | 122.3324 | 122.4873 | 122.2799 | 62.3707 | -122.7098
117.3281 | 122.7448 | -62.3199 | 60.3149 | 1.4211e-13 | -0.0082863 | -0.012863 | 0.01637 | -0.035729 | 0.032304 | -0.00083919 | -0.012803 | 0.011089 | 0.035564 | -0.0088589 | 0.040334 | -62.2971 | 0.010564 | -62.3005 | 60.2121 | 60.0163 | 60.1308 | -62.2815 | -62.274 | 0.078197 | -62.3909 | 60.0445 | 60.1994 | 59.9966 | -62.4269 | 0.038462 | -0.1028 | 0.02287 | 0.019452 | -0.01901 | -0.29862 | -0.18412 | -0.10696 | -0.27046 | 0.045961 | -0.070961 | 0.035998 | -0.1155 | -0.31834 | 122.5321 | 122.3363 | 122.4508 | 62.3305 | -122.5964 | 122.3644 | 122.5194 | 122.3165 | 62.3981 | -122.7418
119.0312 | 122.8638 | -62.265 | 60.2463 | 1.4211e-13 | -0.0084999 | -0.013077 | 0.016584 | -0.035729 | 0.032517 | -0.00083919 | -0.012803 | 0.011089 | 0.035564 | -0.0086451 | 0.040334 | -62.2971 | 0.010564 | -62.3005 | 60.2121 | 60.0163 | 60.1308 | -62.2815 | -62.2786 | 0.078197 | -62.3772 | 60.0399 | 60.1949 | 59.9783 | -62.4315 | -0.016469 | -0.034133 | -0.032061 | -0.035479 | -0.01901 | -0.22995 | -0.11546 | -0.16647 | -0.20637 | -0.013549 | -0.11216 | 0.054313 | -0.051419 | -0.26799 | 122.4772 | 122.2813 | 122.3958 | 62.2756 | -122.5278 | 122.3049 | 122.4599 | 122.2433 | 62.3432 | -122.6778
120.8125 | 122.7951 | -62.3062 | 60.228 | 1.4211e-13 | -0.0084999 | -0.01265 | 0.017011 | -0.035729 | 0.032304 | -0.00083919 | -0.013017 | 0.011089 | 0.035564 | -0.0094999 | 0.040334 | -62.2971 | 0.015142 | -62.3005 | 60.2121 | 60.0255 | 60.1262 | -62.2815 | -62.2786 | 0.087354 | -62.3817 | 60.0445 | 60.1949 | 59.992 | -62.4223 | 0.024729 | -0.015822 | 0.009137 | 0.005719 | -0.01901 | -0.20249 | -0.10173 | -0.11611 | -0.18349 | 0.027649 | -0.075537 | 0.040576 | -0.033108 | -0.23594 | 122.5184 | 122.3317 | 122.4325 | 62.3214 | -122.5095 | 122.3507 | 122.5011 | 122.2982 | 62.3936 | -122.6503
122.5781 | 122.8317 | -62.2971 | 60.2142 | 1.4211e-13 | -0.0084999 | -0.013077 | 0.016798 | -0.035729 | 0.032517 | -0.00083919 | -0.01259 | 0.011089 | 0.03535 | -0.0090725 | 0.040334 | -62.2971 | 0.015142 | -62.3005 | 60.2121 | 60.0117 | 60.1354 | -62.2861 | -62.2786 | 0.087354 | -62.3817 | 60.0491 | 60.1903 | 59.9874 | -62.4269 | 0.010995 | -0.002089 | -1.8e-05 | -0.003436 | -0.014431 | -0.20249 | -0.078838 | -0.12985 | -0.16517 | 0.018494 | -0.084692 | 0.045155 | -0.023954 | -0.22679 | 122.5092 | 122.3088 | 122.4325 | 62.3122 | -122.5003 | 122.3461 | 122.4873 | 122.2845 | 62.3844 | -122.6411
124.3594 | 122.8363 | -62.3291 | 60.2051 | 1.4211e-13 | -0.0087137 | -0.012436 | 0.016798 | -0.035515 | 0.032517 | -0.0084697 | -0.013017 | 0.011303 | 0.035564 | -0.0090725 | 0.040334 | -62.2971 | 0.010564 | -62.2959 | 60.2167 | 60.0117 | 60.1308 | -62.2906 | -62.274 | 0.082776 | -62.3817 | 60.0399 | 60.1994 | 59.992 | -62.4269 | 0.03846 | 0.011645 | 0.032026 | 0.033186 | -0.005274 | -0.19333 | -0.074262 | -0.097803 | -0.16517 | 0.055117 | -0.052648 | 0.045155 | -0.005641 | -0.21306 | 122.5458 | 122.3408 | 122.4599 | 62.3397 | -122.4957 | 122.369 | 122.5285 | 122.3211 | 62.4119 | -122.632
126.125 | 122.7264 | -62.3108 | 60.2737 | 1.4211e-13 | -0.0082863 | -0.01265 | 0.017011 | -0.035942 | 0.032304 | -0.00083919 | -0.013017 | 0.011303 | 0.035564 | -0.0090725 | 0.040547 | -62.2971 | 0.019721 | -62.2959 | 60.2121 | 60.0209 | 60.1217 | -62.2861 | -62.2786 | 0.087354 | -62.3817 | 60.0445 | 60.1903 | 59.992 | -62.4315 | 0.024728 | -0.061599 | 0.013715 | 0.014875 | -0.009853 | -0.25284 | -0.15208 | -0.12069 | -0.22926 | 0.032227 | -0.070959 | 0.049734 | -0.083464 | -0.28172 | 122.5229 | 122.3317 | 122.4325 | 62.3305 | -122.5598 | 122.3553 | 122.5011 | 122.3028 | 62.3981 | -122.7052
127.8281 | 122.8455 | -62.3016 | 60.2188 | 1.4211e-13 | -0.0089273 | -0.012863 | 0.016798 | -0.035515 | 0.032517 | -0.00083919 | -0.012803 | 0.010875 | 0.035564 | -0.0094999 | 0.040334 | -62.2879 | 0.015142 | -62.2959 | 60.2121 | 60.0163 | 60.1308 | -62.2861 | -62.2694 | 0.078197 | -62.3863 | 60.0445 | 60.1949 | 59.9829 | -62.4269 | 0.015573 | -0.006667 | 0.013717 | 0.00572 | -0.009853 | -0.20249 | -0.087995 | -0.12527 | -0.17433 | 0.03223 | -0.084692 | 0.040577 | -0.023953 | -0.23595 | 122.5138 | 122.318 | 122.4325 | 62.3168 | -122.5049 | 122.3461 | 122.4965 | 122.2845 | 62.3798 | -122.6457
129.6094 | 122.8409 | -62.2833 | 60.2005 | 1.4211e-13 | -0.0089273 | -0.01265 | 0.016584 | -0.035729 | 0.032517 | -0.00083919 | -0.013231 | 0.011089 | 0.035777 | -0.0092861 | 0.040334 | -62.2879 | 0.005985 | -62.2959 | 60.2121 | 60.0163 | 60.1354 | -62.2906 | -62.2694 | 0.078197 | -62.3817 | 60.0307 | 60.1949 | 59.9829 | -62.4086 | -0.007317 | 0.011644 | -0.004594 | -0.012591 | -0.005274 | -0.18418 | -0.065105 | -0.12526 | -0.16975 | 0.013919 | -0.098425 | 0.02684 | -0.005642 | -0.21764 | 122.4955 | 122.2996 | 122.4187 | 62.2893 | -122.4911 | 122.3141 | 122.4782 | 122.2662 | 62.3615 | -122.6091
131.3906 | 122.7997 | -62.3154 | 60.228 | 1.4211e-13 | -0.0087137 | -0.01265 | 0.016584 | -0.035729 | 0.032731 | -0.00083919 | -0.013017 | 0.011089 | 0.035564 | -0.0088589 | 0.040761 | -62.2879 | 0.019721 | -62.2959 | 60.203 | 60.0163 | 60.1308 | -62.2952 | -62.2694 | 0.078197 | -62.3772 | 60.0399 | 60.1857 | 59.9874 | -62.4269 | 0.020148 | -0.024979 | 0.02745 | 0.019453 | -0.000695 | -0.21164 | -0.09715 | -0.11154 | -0.18806 | 0.045963 | -0.061802 | 0.049734 | -0.042265 | -0.24052 | 122.5184 | 122.3317 | 122.4462 | 62.3351 | -122.5232 | 122.3553 | 122.5011 | 122.3028 | 62.3936 | -122.6549
133.1562 | 122.7127 | -62.3245 | 60.2783 | 1.4211e-13 | -0.0084999 | -0.012436 | 0.016798 | -0.035729 | 0.032304 | 0.014421 | -0.013444 | 0.011303 | 0.035564 | -0.0090725 | 0.04012 | -62.2971 | 0.015142 | -62.2959 | 60.203 | 60.0209 | 60.1262 | -62.2815 | -62.2694 | 0.078197 | -62.3817 | 60.0399 | 60.1903 | 59.9829 | -62.4132 | 0.04304 | -0.075333 | 0.027448 | 0.028608 | -0.014432 | -0.25742 | -0.15208 | -0.088645 | -0.23842 | 0.055118 | -0.057226 | 0.031419 | -0.088041 | -0.29546 | 122.5275 | 122.3454 | 122.4508 | 62.3397 | -122.5598 | 122.3644 | 122.5148 | 122.3074 | 62.4027 | -122.6915
134.8906 | 122.7173 | -62.3383 | 60.26 | 1.4211e-13 | -0.0084999 | -0.012863 | 0.016798 | -0.035729 | 0.03209 | -0.00083919 | -0.01259 | 0.011089 | 0.035564 | -0.0088589 | 0.040334 | -62.2925 | 0.010564 | -62.2959 | 60.2076 | 60.0117 | 60.1217 | -62.2815 | -62.2694 | 0.082776 | -62.3772 | 60.0307 | 60.1903 | 59.9783 | -62.4269 | 0.056773 | -0.052444 | 0.045759 | 0.042341 | -0.014432 | -0.24827 | -0.13835 | -0.088648 | -0.22926 | 0.068851 | -0.038914 | 0.049734 | -0.069731 | -0.28172 | 122.5458 | 122.35 | 122.4599 | 62.3488 | -122.5415 | 122.369 | 122.5285 | 122.3165 | 62.421 | -122.6869
136.6875 | 122.7585 | -62.3062 | 60.2554 | 1.4211e-13 | -0.0084999 | -0.01265 | 0.016584 | -0.035729 | 0.032517 | -0.0084697 | -0.013017 | 0.011089 | 0.03535 | -0.0088589 | 0.040334 | -62.2971 | 0.010564 | -62.2959 | 60.1984 | 60.0117 | 60.1171 | -62.2815 | -62.2694 | 0.073618 | -62.3772 | 60.0399 | 60.1903 | 59.9783 | -62.4223 | 0.024729 | -0.057023 | 0.009137 | 0.010297 | -0.014432 | -0.24369 | -0.13835 | -0.11611 | -0.21553 | 0.036807 | -0.070958 | 0.045155 | -0.065153 | -0.27715 | 122.5046 | 122.318 | 122.4233 | 62.3168 | -122.5369 | 122.3461 | 122.4965 | 122.2845 | 62.3798 | -122.6778
138.4062 | 122.7173 | -62.2833 | 60.3104 | 1.4211e-13 | -0.0084999 | -0.012436 | 0.016584 | -0.035729 | 0.032517 | 0.0067908 | -0.012803 | 0.011089 | 0.035564 | -0.0090725 | 0.040547 | -62.2925 | 0.005985 | -62.2959 | 60.2076 | 60.0026 | 60.1308 | -62.2861 | -62.2648 | 0.082776 | -62.3726 | 60.0399 | 60.1994 | 59.9737 | -62.4223 | -0.002738 | -0.1028 | -0.009173 | -0.012591 | -0.009853 | -0.30778 | -0.17955 | -0.139 | -0.27046 | 0.018497 | -0.089267 | 0.049734 | -0.11093 | -0.33666 | 122.4909 | 122.2859 | 122.4141 | 62.2893 | -122.5964 | 122.3232 | 122.4828 | 122.257 | 62.3661 | -122.7327
140.1719 | 122.7127 | -62.3016 | 60.2554 | 1.4211e-13 | -0.0082863 | -0.012436 | 0.016798 | -0.036156 | 0.031876 | 0.0067908 | -0.012803 | 0.010875 | 0.035777 | -0.0088589 | 0.04012 | -62.2925 | 0.010564 | -62.2913 | 60.203 | 60.0117 | 60.1308 | -62.2769 | -62.274 | 0.082776 | -62.3817 | 60.0353 | 60.1949 | 59.9783 | -62.4177 | 0.024731 | -0.052445 | 0.009138 | 0.010298 | -0.014433 | -0.24369 | -0.12462 | -0.11611 | -0.22011 | 0.027651 | -0.080114 | 0.035997 | -0.060574 | -0.27715 | 122.5046 | 122.3134 | 122.4325 | 62.3122 | -122.5323 | 122.337 | 122.4965 | 122.2799 | 62.3844 | -122.6732
141.9531 | 122.8226 | -62.3016 | 60.2051 | 1.4211e-13 | -0.0087137 | -0.012436 | 0.016798 | -0.035942 | 0.032731 | -0.00083919 | -0.012803 | 0.011089 | 0.03535 | -0.0090725 | 0.04012 | -62.2879 | 0.001407 | -62.2913 | 60.2076 | 60.0072 | 60.1308 | -62.2815 | -62.2694 | 0.082776 | -62.3726 | 60.0353 | 60.1903 | 59.9874 | -62.4177 | 0.020152 | 0.002488 | 0.013717 | 0.010298 | -0.009854 | -0.19791 | -0.074262 | -0.11611 | -0.16975 | 0.03223 | -0.070956 | 0.045155 | -0.014799 | -0.21763 | 122.5092 | 122.3088 | 122.4325 | 62.303 | -122.4866 | 122.337 | 122.4919 | 122.2891 | 62.3844 | -122.6228
143.7188 | 122.8363 | -62.2787 | 60.2371 | 1.4211e-13 | -0.0087137 | -0.012436 | 0.016798 | -0.035729 | 0.03209 | 0.014421 | -0.012803 | 0.011089 | 0.03535 | -0.0084315 | 0.04012 | -62.2879 | 0.015142 | -62.2868 | 60.1984 | 60.0026 | 60.1217 | -62.2815 | -62.2694 | 0.078197 | -62.3817 | 60.0399 | 60.1857 | 59.9783 | -62.4223 | -0.002736 | -0.038713 | -0.009171 | -0.008012 | -0.005276 | -0.23454 | -0.11546 | -0.14358 | -0.19722 | 0.009342 | -0.103 | 0.040576 | -0.051421 | -0.25884 | 122.4772 | 122.2813 | 122.4004 | 62.2939 | -122.5186 | 122.3187 | 122.4644 | 122.257 | 62.3569 | -122.6594
145.4375 | 122.7905 | -62.2971 | 60.2554 | 1.4211e-13 | -0.0084999 | -0.012863 | 0.016584 | -0.035942 | 0.032517 | 0.0067908 | -0.012803 | 0.010875 | 0.035777 | -0.0086451 | 0.04012 | -62.2833 | 0.019721 | -62.2959 | 60.2076 | 60.0117 | 60.1262 | -62.2769 | -62.2694 | 0.087354 | -62.368 | 60.0307 | 60.1857 | 59.9737 | -62.4177 | 0.020153 | -0.047866 | 0.013717 | 0.001142 | -0.019011 | -0.24369 | -0.12919 | -0.12069 | -0.22469 | 0.027652 | -0.070955 | 0.049734 | -0.069731 | -0.28172 | 122.5046 | 122.3088 | 122.4233 | 62.3168 | -122.5323 | 122.3278 | 122.4828 | 122.2708 | 62.3844 | -122.6732
147.1875 | 122.7127 | -62.2971 | 60.2966 | 1.4211e-13 | -0.0087137 | -0.012863 | 0.017011 | -0.035515 | 0.032304 | 0.0067908 | -0.01259 | 0.011303 | 0.035777 | -0.0086451 | 0.04012 | -62.2879 | 0.010564 | -62.2959 | 60.203 | 60.0117 | 60.1262 | -62.2723 | -62.2694 | 0.082776 | -62.3863 | 60.0353 | 60.1903 | 59.9691 | -62.4269 | 0.024732 | -0.093644 | 0.009139 | 0.001142 | -0.02359 | -0.28489 | -0.17039 | -0.12985 | -0.26131 | 0.027652 | -0.08927 | 0.040577 | -0.10635 | -0.3275 | 122.5 | 122.3088 | 122.4233 | 62.3076 | -122.569 | 122.3324 | 122.4873 | 122.2662 | 62.3798 | -122.7235
148.9844 | 122.7219 | -62.3016 | 60.3287 | 1.4211e-13 | -0.0084999 | -0.01265 | 0.016798 | -0.035942 | 0.032304 | 0.0067908 | -0.013231 | 0.011089 | 0.035777 | -0.0086451 | 0.040334 | -62.2833 | 0.015142 | -62.2959 | 60.1984 | 60.0117 | 60.1308 | -62.2815 | -62.2648 | 0.082776 | -62.3726 | 60.0353 | 60.1903 | 59.9646 | -62.4223 | 0.020152 | -0.13027 | 0.018295 | 0.00572 | -0.014432 | -0.31693 | -0.19786 | -0.12069 | -0.29335 | 0.036808 | -0.070956 | 0.049734 | -0.1384 | -0.36412 | 122.5 | 122.3134 | 122.4325 | 62.3168 | -122.6102 | 122.337 | 122.4919 | 122.2662 | 62.3844 | -122.751
150.7031 | 122.7402 | -62.2833 | 60.3058 | 1.4211e-13 | -0.0084999 | -0.01265 | 0.017011 | -0.035942 | 0.03209 | -0.00083919 | -0.01259 | 0.011089 | 0.03535 | -0.0088589 | 0.040761 | -62.2742 | 0.015142 | -62.2913 | 60.203 | 60.0072 | 60.1262 | -62.2723 | -62.2557 | 0.082776 | -62.3726 | 60.0307 | 60.1857 | 59.9646 | -62.4223 | 0.010999 | -0.1028 | 0.009141 | -0.008013 | -0.019012 | -0.29862 | -0.17955 | -0.139 | -0.27504 | 0.027655 | -0.089267 | 0.049734 | -0.12008 | -0.34123 | 122.4863 | 122.2905 | 122.4096 | 62.2985 | -122.5781 | 122.3141 | 122.469 | 122.2479 | 62.3661 | -122.7281
152.4844 | 122.8409 | -62.2742 | 60.2646 | 1.4211e-13 | -0.0080727 | -0.012436 | 0.016584 | -0.035729 | 0.032517 | 0.0067908 | -0.012803 | 0.010662 | 0.035564 | -0.0086451 | 0.04012 | -62.2833 | 0.010564 | -62.2959 | 60.2076 | 60.0026 | 60.1262 | -62.2723 | -62.2648 | 0.078197 | -62.368 | 60.0307 | 60.1949 | 59.9737 | -62.4223 | 0.001844 | -0.057021 | -0.009171 | -0.021746 | -0.02359 | -0.262 | -0.13835 | -0.14816 | -0.23384 | 0.009342 | -0.093843 | 0.054313 | -0.069729 | -0.29088 | 122.4817 | 122.2768 | 122.4004 | 62.2847 | -122.5369 | 122.3049 | 122.469 | 122.2479 | 62.3524 | -122.6869
154.2656 | 122.7493 | -62.2833 | 60.2783 | 1.4211e-13 | -0.0082863 | -0.01265 | 0.016798 | -0.035942 | 0.032304 | -0.0084697 | -0.012803 | 0.011089 | 0.035564 | -0.0086451 | 0.040334 | -62.2879 | 0.010564 | -62.2913 | 60.203 | 60.0117 | 60.1171 | -62.2677 | -62.2602 | 0.082776 | -62.368 | 60.0307 | 60.1857 | 59.9829 | -62.4177 | 0.015578 | -0.075333 | -0.004594 | -0.008013 | -0.023591 | -0.26658 | -0.16124 | -0.13442 | -0.24757 | 0.023076 | -0.084688 | 0.049734 | -0.092619 | -0.29546 | 122.4863 | 122.2951 | 122.4004 | 62.2939 | -122.5461 | 122.3141 | 122.469 | 122.2662 | 62.3661 | -122.6961
155.9688 | 122.7173 | -62.3062 | 60.2921 | 1.4211e-13 | -0.0089273 | -0.01265 | 0.016584 | -0.035729 | 0.032517 | 0.0067908 | -0.012803 | 0.011089 | 0.03535 | -0.0090725 | 0.04012 | -62.2879 | 0.019721 | -62.2868 | 60.1984 | 60.0117 | 60.1217 | -62.2632 | -62.2602 | 0.087354 | -62.3726 | 60.0353 | 60.1765 | 59.9829 | -62.4223 | 0.043045 | -0.093644 | 0.018294 | 0.019453 | -0.023592 | -0.28031 | -0.17039 | -0.11611 | -0.25673 | 0.045964 | -0.066379 | 0.049734 | -0.11551 | -0.30919 | 122.5046 | 122.318 | 122.4279 | 62.3259 | -122.5552 | 122.3415 | 122.4828 | 122.2891 | 62.3936 | -122.7144
157.7344 | 122.8088 | -62.3154 | 60.1822 | 1.4211e-13 | -0.0084999 | -0.01265 | 0.016798 | -0.035942 | 0.032304 | 0.014421 | -0.012803 | 0.010875 | 0.03535 | -0.0088589 | 0.040547 | -62.2879 | 0.015142 | -62.2959 | 60.1984 | 60.0117 | 60.1308 | -62.2815 | -62.2557 | 0.082776 | -62.368 | 60.0353 | 60.1857 | 59.9783 | -62.4223 | 0.033885 | 0.016219 | 0.02745 | 0.019453 | -0.014432 | -0.17045 | -0.051374 | -0.10696 | -0.14687 | 0.059699 | -0.052644 | 0.054313 | 0.003511 | -0.2039 | 122.5138 | 122.3271 | 122.4462 | 62.3305 | -122.4637 | 122.3507 | 122.5011 | 122.2937 | 62.3981 | -122.6045
159.5156 | 122.7539 | -62.2559 | 60.2646 | 1.4211e-13 | -0.0087137 | -0.01265 | 0.016584 | -0.035942 | 0.032304 | -0.00083919 | -0.012803 | 0.010875 | 0.034923 | -0.0084315 | 0.040334 | -62.2833 | 0.015142 | -62.2959 | 60.1938 | 60.0026 | 60.1262 | -62.2815 | -62.2648 | 0.078197 | -62.368 | 60.0307 | 60.1857 | 59.9691 | -62.4269 | -0.025625 | -0.070756 | -0.027482 | -0.040057 | -0.014432 | -0.262 | -0.13835 | -0.17105 | -0.23384 | -0.008969 | -0.11215 | 0.058892 | -0.078886 | -0.29546 | 122.4497 | 122.2584 | 122.3821 | 62.271 | -122.5461 | 122.2866 | 122.4416 | 122.225 | 62.3341 | -122.6915
161.2344 | 122.8226 | -62.2787 | 60.2325 | 1.4211e-13 | -0.0087137 | -0.012436 | 0.016798 | -0.035729 | 0.03209 | 0.0067908 | -0.013017 | 0.010875 | 0.035564 | -0.0088589 | 0.040334 | -62.2833 | 0.015142 | -62.2822 | 60.203 | 60.0072 | 60.1262 | -62.2723 | -62.2602 | 0.082776 | -62.368 | 60.0307 | 60.1903 | 59.9737 | -62.4132 | 0.006422 | -0.029557 | -0.004593 | -0.003433 | -0.009855 | -0.22538 | -0.10631 | -0.13442 | -0.2018 | 0.018499 | -0.089265 | 0.045156 | -0.042265 | -0.25884 | 122.4817 | 122.2859 | 122.405 | 62.2939 | -122.5049 | 122.3095 | 122.469 | 122.2525 | 62.3615 | -122.6457
163.0156 | 122.6898 | -62.3199 | 60.2783 | 1.4211e-13 | -0.0082863 | -0.012436 | 0.016798 | -0.035942 | 0.031876 | 0.0067908 | -0.012803 | 0.011089 | 0.035777 | -0.0084315 | 0.04012 | -62.2879 | 0.019721 | -62.2868 | 60.1984 | 60.0117 | 60.1308 | -62.2815 | -62.2648 | 0.078197 | -62.3726 | 60.0353 | 60.1903 | 59.9783 | -62.4132 | 0.038462 | -0.079911 | 0.032027 | 0.033186 | -0.005276 | -0.26658 | -0.1475 | -0.093223 | -0.243 | 0.055118 | -0.052646 | 0.040577 | -0.088041 | -0.30003 | 122.5184 | 122.3317 | 122.4508 | 62.3397 | -122.5598 | 122.3553 | 122.5102 | 122.2982 | 62.3981 | -122.6915
164.7969 | 122.7631 | -62.2925 | 60.228 | 1.4211e-13 | -0.0084999 | -0.012863 | 0.016798 | -0.035729 | 0.032517 | -0.0084697 | -0.013017 | 0.010875 | 0.03535 | -0.0086451 | 0.040334 | -62.2833 | 0.015142 | -62.2913 | 60.1984 | 60.0072 | 60.1308 | -62.2769 | -62.2602 | 0.082776 | -62.3634 | 60.0262 | 60.1857 | 59.9783 | -62.4223 | 0.015575 | -0.029557 | 0.009139 | 0.001142 | -0.014433 | -0.2208 | -0.09715 | -0.12985 | -0.2018 | 0.032231 | -0.070955 | 0.058891 | -0.042265 | -0.24968 | 122.4909 | 122.2996 | 122.4233 | 62.3076 | -122.5049 | 122.3186 | 122.4782 | 122.2708 | 62.3753 | -122.6503
166.5938 | 122.7631 | -62.2879 | 60.2783 | 1.4211e-13 | -0.0084999 | -0.01265 | 0.016584 | -0.035942 | 0.032304 | 0.0067908 | -0.013017 | 0.010875 | 0.03535 | -0.0088589 | 0.040334 | -62.2788 | 0.015142 | -62.2822 | 60.2076 | 59.998 | 60.1171 | -62.2769 | -62.2602 | 0.087354 | -62.3726 | 60.0307 | 60.1857 | 59.9691 | -62.4223 | 0.010998 | -0.070754 | 0.00914 | 0.005722 | -0.005276 | -0.28031 | -0.16124 | -0.13442 | -0.24757 | 0.027654 | -0.084689 | 0.049734 | -0.092619 | -0.30919 | 122.4955 | 122.2859 | 122.405 | 62.303 | -122.5552 | 122.3186 | 122.4736 | 122.257 | 62.3753 | -122.7006
168.375 | 122.7631 | -62.2833 | 60.2692 | 1.4211e-13 | -0.0087137 | -0.012436 | 0.016157 | -0.035729 | 0.032304 | -0.00083919 | -0.012803 | 0.010662 | 0.03535 | -0.0084315 | 0.040334 | -62.2788 | 0.010564 | -62.2822 | 60.203 | 60.0072 | 60.1217 | -62.2769 | -62.2557 | 0.082776 | -62.3726 | 60.0307 | 60.1857 | 59.9691 | -62.4177 | 0.00642 | -0.066178 | 0.004562 | 0.001144 | -0.005276 | -0.262 | -0.14751 | -0.13442 | -0.23842 | 0.027655 | -0.089267 | 0.045155 | -0.083464 | -0.30004 | 122.4863 | 122.2905 | 122.405 | 62.2939 | -122.5461 | 122.3141 | 122.469 | 122.2525 | 62.3661 | -122.6869
170.0781 | 122.7356 | -62.2971 | 60.2692 | 1.4211e-13 | -0.0082863 | -0.01265 | 0.01637 | -0.036156 | 0.03209 | -0.0084697 | -0.013017 | 0.010875 | 0.035564 | -0.0088589 | 0.04012 | -62.2833 | 0.010564 | -62.2868 | 60.1984 | 59.998 | 60.1262 | -62.2769 | -62.2602 | 0.082776 | -62.3726 | 60.0353 | 60.1811 | 59.9737 | -62.4086 | 0.020153 | -0.070756 | 0.013717 | 0.010298 | -0.009855 | -0.27116 | -0.14293 | -0.11153 | -0.23384 | 0.036809 | -0.075534 | 0.035998 | -0.088043 | -0.29546 | 122.4955 | 122.2951 | 122.4233 | 62.3076 | -122.5461 | 122.3324 | 122.4782 | 122.2708 | 62.3798 | -122.6778
171.8438 | 122.7264 | -62.2879 | 60.2875 | 1.4211e-13 | -0.0084999 | -0.01265 | 0.016584 | -0.036156 | 0.031876 | -0.0084697 | -0.012803 | 0.010875 | 0.03535 | -0.0088589 | 0.040334 | -62.2742 | 0.015142 | -62.2959 | 60.2076 | 60.0026 | 60.1308 | -62.2769 | -62.2602 | 0.082776 | -62.3726 | 60.0262 | 60.1857 | 59.9691 | -62.4177 | 0.010998 | -0.07991 | 0.013719 | -0.008013 | -0.019011 | -0.28489 | -0.15666 | -0.12984 | -0.26131 | 0.027654 | -0.084689 | 0.045155 | -0.10177 | -0.31835 | 122.4955 | 122.2905 | 122.4187 | 62.303 | -122.5644 | 122.3141 | 122.4736 | 122.257 | 62.3707 | -122.7052
173.625 | 122.8134 | -62.265 | 60.2234 | 1.4211e-13 | -0.0087137 | -0.012436 | 0.016798 | -0.035942 | 0.032304 | -0.0084697 | -0.013017 | 0.011089 | 0.035564 | -0.0088589 | 0.040334 | -62.2788 | 0.010564 | -62.2822 | 60.1984 | 60.0117 | 60.1262 | -62.2861 | -62.2557 | 0.082776 | -62.3726 | 60.0216 | 60.1949 | 59.9783 | -62.4132 | -0.021048 | -0.02498 | -0.013748 | -0.017166 | 0.003882 | -0.21164 | -0.097151 | -0.14815 | -0.2018 | 0.009345 | -0.10758 | 0.040577 | -0.028531 | -0.2451 | 122.4634 | 122.2768 | 122.3913 | 62.2756 | -122.5095 | 122.2866 | 122.4599 | 122.2433 | 62.3478 | -122.6366
175.3281 | 122.7859 | -62.2833 | 60.2692 | 1.4211e-13 | -0.0080727 | -0.012436 | 0.016584 | -0.035729 | 0.032304 | 0.0067908 | -0.012803 | 0.010662 | 0.03535 | -0.0086451 | 0.039906 | -62.2788 | 0.010564 | -62.2868 | 60.1984 | 60.0117 | 60.1262 | -62.2723 | -62.2557 | 0.082776 | -62.368 | 60.0262 | 60.1811 | 59.9691 | -62.4177 | 0.010999 | -0.070756 | 0.004562 | -0.003435 | -0.014434 | -0.25742 | -0.14293 | -0.13442 | -0.243 | 0.027655 | -0.084688 | 0.049734 | -0.088043 | -0.30004 | 122.4817 | 122.2951 | 122.4096 | 62.2939 | -122.5415 | 122.3095 | 122.4644 | 122.2525 | 62.3661 | -122.6869
177.0938 | 122.7219 | -62.2925 | 60.2783 | 1.4211e-13 | -0.0082863 | -0.012863 | 0.016798 | -0.035729 | 0.03209 | 0.014421 | -0.012803 | 0.010875 | 0.035136 | -0.0084315 | 0.04012 | -62.2742 | 0.005985 | -62.2822 | 60.203 | 60.0026 | 60.1217 | -62.2677 | -62.2557 | 0.082776 | -62.3634 | 60.0262 | 60.1857 | 59.9646 | -62.4223 | 0.024733 | -0.075333 | 0.018296 | 0.010299 | -0.014434 | -0.27573 | -0.15666 | -0.12985 | -0.25215 | 0.03681 | -0.070955 | 0.058891 | -0.092619 | -0.31377 | 122.4955 | 122.2951 | 122.4141 | 62.2985 | -122.5461 | 122.3186 | 122.4782 | 122.257 | 62.3753 | -122.7006
178.8906 | 122.6807 | -62.3245 | 60.2692 | 1.4211e-13 | -0.0084999 | -0.01265 | 0.016798 | -0.035729 | 0.032517 | -0.00083919 | -0.012803 | 0.010662 | 0.03535 | -0.0088589 | 0.039906 | -62.2742 | 0.010564 | -62.2868 | 60.1984 | 60.0117 | 60.1262 | -62.2632 | -62.2602 | 0.087354 | -62.368 | 60.0307 | 60.1811 | 59.9783 | -62.4177 | 0.061356 | -0.070756 | 0.05034 | 0.037764 | -0.023592 | -0.25742 | -0.14293 | -0.093223 | -0.23842 | 0.064275 | -0.043489 | 0.049734 | -0.088043 | -0.29088 | 122.5229 | 122.3363 | 122.4508 | 62.3351 | -122.5323 | 122.3553 | 122.5056 | 122.3028 | 62.4119 | -122.6869
180.5938 | 122.818 | -62.2559 | 60.2051 | 1.4211e-13 | -0.0084999 | -0.012436 | 0.016798 | -0.03637 | 0.032304 | -0.00083919 | -0.013017 | 0.010662 | 0.03535 | -0.0088589 | 0.04012 | -62.2742 | 0.010564 | -62.2776 | 60.1938 | 60.0026 | 60.1262 | -62.2677 | -62.2557 | 0.082776 | -62.3589 | 60.0262 | 60.1857 | 59.9691 | -62.4223 | -0.011888 | -0.011247 | -0.018325 | -0.021744 | -0.009856 | -0.20249 | -0.07884 | -0.16647 | -0.17891 | 0.000189 | -0.103 | 0.06347 | -0.019377 | -0.23595 | 122.4497 | 122.2584 | 122.3821 | 62.2664 | -122.4728 | 122.282 | 122.4416 | 122.225 | 62.3386 | -122.6274
182.3594 | 122.7814 | -62.2879 | 60.2097 | 1.4211e-13 | -0.0084999 | -0.012436 | 0.016798 | -0.035942 | 0.032304 | 0.0067908 | -0.012803 | 0.010662 | 0.03535 | -0.0086451 | 0.04012 | -62.2742 | 0.010564 | -62.2822 | 60.2076 | 60.0072 | 60.1217 | -62.2586 | -62.2557 | 0.087354 | -62.3634 | 60.0262 | 60.1949 | 59.9691 | -62.4177 | 0.029314 | -0.00209 | 0.013719 | 0.005722 | -0.023592 | -0.20249 | -0.087997 | -0.12984 | -0.18349 | 0.032233 | -0.075532 | 0.054312 | -0.014798 | -0.24053 | 122.4955 | 122.2951 | 122.4096 | 62.2985 | -122.4682 | 122.3141 | 122.4828 | 122.257 | 62.3753 | -122.6274
184.1562 | 122.8134 | -62.2742 | 60.2005 | 1.4211e-13 | -0.0082863 | -0.01265 | 0.016798 | -0.035729 | 0.032304 | -0.00083919 | -0.013231 | 0.010875 | 0.035777 | -0.0082179 | 0.04012 | -62.2696 | 0.015142 | -62.2822 | 60.1938 | 60.0072 | 60.1217 | -62.2632 | -62.2557 | 0.082776 | -62.368 | 60.0262 | 60.1903 | 59.9737 | -62.4086 | 0.011002 | -0.006669 | 0.004564 | -0.008011 | -0.019013 | -0.19333 | -0.078841 | -0.13442 | -0.17433 | 0.0185 | -0.093843 | 0.040577 | -0.010221 | -0.22679 | 122.468 | 122.2813 | 122.3958 | 62.2893 | -122.4637 | 122.3003 | 122.4644 | 122.2479 | 62.3569 | -122.6091
185.875 | 122.7676 | -62.2513 | 60.2737 | 1.4211e-13 | -0.0084999 | -0.01265 | 0.016584 | -0.035942 | 0.032304 | -0.00083919 | -0.013444 | 0.010875 | 0.03535 | -0.0088589 | 0.040334 | -62.2742 | 0.015142 | -62.2822 | 60.1938 | 60.0026 | 60.1217 | -62.2677 | -62.2557 | 0.082776 | -62.368 | 60.0307 | 60.1811 | 59.9646 | -62.4177 | -0.016465 | -0.079912 | -0.022902 | -0.030899 | -0.014434 | -0.27116 | -0.15208 | -0.16646 | -0.243 | -0.004388 | -0.11673 | 0.049734 | -0.092621 | -0.30919 | 122.4451 | 122.2539 | 122.3729 | 62.2664 | -122.5415 | 122.282 | 122.4324 | 122.2158 | 62.3341 | -122.6915
187.6562 | 122.7631 | -62.2971 | 60.2051 | 1.4211e-13 | -0.0087137 | -0.012863 | 0.016584 | -0.036156 | 0.03209 | -0.00083919 | -0.013017 | 0.010875 | 0.03535 | -0.0086451 | 0.039693 | -62.2788 | 0.005985 | -62.2822 | 60.1938 | 60.0072 | 60.1262 | -62.2723 | -62.2511 | 0.087354 | -62.3634 | 60.0216 | 60.1903 | 59.9737 | -62.4177 | 0.024732 | -0.011247 | 0.018295 | 0.014877 | -0.009855 | -0.19791 | -0.07884 | -0.12069 | -0.18349 | 0.045966 | -0.066377 | 0.054312 | -0.014799 | -0.23137 | 122.4909 | 122.3042 | 122.4233 | 62.303 | -122.4774 | 122.3186 | 122.4873 | 122.2708 | 62.3844 | -122.6228
189.375 | 122.6898 | -62.2787 | 60.2829 | 1.4211e-13 | -0.0082863 | -0.012436 | 0.016798 | -0.035942 | 0.031876 | -0.00083919 | -0.012803 | 0.011089 | 0.035564 | -0.0084315 | 0.039906 | -62.2742 | 0.015142 | -62.2776 | 60.203 | 60.0026 | 60.1125 | -62.2677 | -62.2557 | 0.082776 | -62.3634 | 60.0216 | 60.1811 | 59.9691 | -62.4177 | 0.011001 | -0.079911 | 0.004564 | 0.001145 | -0.009856 | -0.28031 | -0.1704 | -0.139 | -0.26131 | 0.023078 | -0.084687 | 0.054312 | -0.10178 | -0.31377 | 122.4817 | 122.2813 | 122.3912 | 62.2939 | -122.5506 | 122.3003 | 122.4599 | 122.2479 | 62.3615 | -122.7006
191.1406 | 122.7493 | -62.3108 | 60.2097 | 1.4211e-13 | -0.0084999 | -0.012436 | 0.016584 | -0.035942 | 0.032304 | -0.00083919 | -0.012803 | 0.011089 | 0.03535 | -0.0084315 | 0.039906 | -62.2696 | 0.019721 | -62.273 | 60.1938 | 60.0072 | 60.1171 | -62.2677 | -62.2557 | 0.082776 | -62.3589 | 60.0262 | 60.1765 | 59.9737 | -62.4086 | 0.043044 | -0.015825 | 0.041185 | 0.037766 | -0.005278 | -0.20249 | -0.092576 | -0.097799 | -0.18349 | 0.055121 | -0.048065 | 0.049734 | -0.033112 | -0.23595 | 122.5046 | 122.318 | 122.4279 | 62.3305 | -122.4774 | 122.337 | 122.4873 | 122.2845 | 62.3936 | -122.6182
192.9219 | 122.7905 | -62.2833 | 60.2097 | 1.4211e-13 | -0.0082863 | -0.012863 | 0.016584 | -0.036156 | 0.03209 | -0.00083919 | -0.013017 | 0.011089 | 0.035136 | -0.0082179 | 0.04012 | -62.2696 | 0.010564 | -62.273 | 60.203 | 59.998 | 60.1217 | -62.2677 | -62.2557 | 0.087354 | -62.3634 | 60.0216 | 60.1811 | 59.9691 | -62.4177 | 0.015578 | -0.006669 | 0.013719 | 0.0103 | -0.005278 | -0.21165 | -0.087997 | -0.13442 | -0.18807 | 0.027655 | -0.08011 | 0.054312 | -0.028534 | -0.24053 | 122.4863 | 122.2813 | 122.405 | 62.2939 | -122.4774 | 122.3049 | 122.4644 | 122.2525 | 62.3707 | -122.6274
194.7031 | 122.6807 | -62.2925 | 60.2692 | 1.4211e-13 | -0.0082863 | -0.01265 | 0.016584 | -0.035942 | 0.032304 | -0.00083919 | -0.012803 | 0.010875 | 0.03535 | -0.0084315 | 0.039906 | -62.2788 | 0.010564 | -62.2776 | 60.1893 | 60.0026 | 60.1125 | -62.2632 | -62.2511 | 0.082776 | -62.3634 | 60.0216 | 60.1857 | 59.9691 | -62.4132 | 0.029312 | -0.079913 | 0.013717 | 0.014877 | -0.014435 | -0.26658 | -0.15666 | -0.12069 | -0.24758 | 0.041388 | -0.070955 | 0.049734 | -0.083464 | -0.30004 | 122.4817 | 122.2951 | 122.405 | 62.303 | -122.5323 | 122.3141 | 122.4782 | 122.2616 | 62.3753 | -122.6823
196.4219 | 122.7997 | -62.265 | 60.2188 | 1.4211e-13 | -0.0082863 | -0.01265 | 0.016798 | -0.036156 | 0.03209 | 0.0067908 | -0.013017 | 0.010875 | 0.03535 | -0.0082179 | 0.04012 | -62.265 | 0.015142 | -62.2776 | 60.1847 | 59.998 | 60.1262 | -62.2632 | -62.2511 | 0.087354 | -62.3634 | 60.0262 | 60.1811 | 59.9691 | -62.4132 | 0.001847 | -0.034137 | -1.2e-05 | -0.012588 | -0.014435 | -0.2208 | -0.092573 | -0.14815 | -0.19264 | 0.013923 | -0.09842 | 0.049734 | -0.037689 | -0.24968 | 122.4497 | 122.263 | 122.3913 | 62.2802 | -122.482 | 122.2912 | 122.4461 | 122.2341 | 62.3524 | -122.632
198.1875 | 122.7081 | -62.2696 | 60.2875 | 1.4211e-13 | -0.0082863 | -0.01265 | 0.016798 | -0.035942 | 0.032304 | 0.0067908 | -0.012803 | 0.010662 | 0.03535 | -0.0086451 | 0.04012 | -62.2696 | 0.019721 | -62.273 | 60.1938 | 59.998 | 60.1262 | -62.2632 | -62.2465 | 0.082776 | -62.3589 | 60.0216 | 60.1811 | 59.9508 | -62.4177 | 0.006424 | -0.093645 | -1.4e-05 | -0.003433 | -0.009857 | -0.28947 | -0.16124 | -0.14815 | -0.26589 | 0.023079 | -0.089264 | 0.058891 | -0.10635 | -0.33666 | 122.4634 | 122.2676 | 122.3958 | 62.2893 | -122.5506 | 122.2912 | 122.4507 | 122.2204 | 62.3524 | -122.7052
199.9688 | 122.7814 | -62.2925 | 60.1959 | 1.4211e-13 | -0.0080727 | -0.012863 | 0.016584 | -0.035942 | 0.03209 | -0.00083919 | -0.013017 | 0.010875 | 0.03535 | -0.0084315 | 0.04012 | -62.2696 | 0.015142 | -62.2776 | 60.1893 | 60.0072 | 60.1171 | -62.2723 | -62.2465 | 0.087354 | -62.3543 | 60.0262 | 60.1765 | 59.9646 | -62.404 | 0.020154 | -0.006671 | 0.022874 | 0.014877 | -0.005277 | -0.18876 | -0.078843 | -0.11153 | -0.16976 | 0.045967 | -0.061797 | 0.049734 | -0.019379 | -0.23137 | 122.4817 | 122.2996 | 122.4096 | 62.3076 | -122.4682 | 122.3186 | 122.469 | 122.257 | 62.3798 | -122.5999
201.6875 | 122.7264 | -62.265 | 60.2692 | 1.4211e-13 | -0.0084999 | -0.012863 | 0.016798 | -0.035942 | 0.031876 | -0.00083919 | -0.01259 | 0.011089 | 0.03535 | -0.0082179 | 0.04012 | -62.2742 | 0.010564 | -62.2776 | 60.1938 | 59.9934 | 60.1171 | -62.2586 | -62.2465 | 0.078197 | -62.3589 | 60.0216 | 60.1765 | 59.96 | -62.4132 | 0.006426 | -0.075334 | -0.009169 | -0.012588 | -0.019014 | -0.27574 | -0.15208 | -0.14815 | -0.24758 | 0.018502 | -0.093841 | 0.054313 | -0.092621 | -0.30919 | 122.4588 | 122.2584 | 122.3821 | 62.2756 | -122.5278 | 122.2866 | 122.4416 | 122.225 | 62.3432 | -122.6823
203.4531 | 122.6761 | -62.2833 | 60.2829 | 1.4211e-13 | -0.0082863 | -0.01265 | 0.017011 | -0.035942 | 0.03209 | -0.00083919 | -0.012803 | 0.010875 | 0.035564 | -0.0086451 | 0.04012 | -62.2696 | 0.010564 | -62.273 | 60.1893 | 59.9934 | 60.1217 | -62.2632 | -62.2511 | 0.082776 | -62.3497 | 60.0262 | 60.1811 | 59.9783 | -62.4086 | 0.020157 | -0.093646 | 0.013719 | 0.0103 | -0.009857 | -0.28947 | -0.16124 | -0.12526 | -0.25673 | 0.032233 | -0.066374 | 0.058891 | -0.10178 | -0.30461 | 122.4726 | 122.2768 | 122.405 | 62.2939 | -122.5461 | 122.3095 | 122.4644 | 122.2616 | 62.3661 | -122.6915
205.2188 | 122.7951 | -62.2559 | 60.2325 | 1.4211e-13 | -0.0082863 | -0.012436 | 0.016798 | -0.035729 | 0.031876 | -0.00083919 | -0.012803 | 0.010662 | 0.03535 | -0.0082179 | 0.039906 | -62.2696 | 0.010564 | -62.2776 | 60.1893 | 59.9934 | 60.1171 | -62.2586 | -62.2511 | 0.082776 | -62.3589 | 60.0216 | 60.1765 | 59.9646 | -62.4086 | -0.00273 | -0.043292 | -0.013747 | -0.021744 | -0.019014 | -0.23912 | -0.11546 | -0.15273 | -0.21095 | 0.004767 | -0.103 | 0.049734 | -0.056 | -0.26799 | 122.4451 | 122.2493 | 122.3729 | 62.2664 | -122.4911 | 122.2774 | 122.4324 | 122.2204 | 62.3386 | -122.6411
207 | 122.6715 | -62.2879 | 60.2692 | 1.4211e-13 | -0.0082863 | -0.012222 | 0.016584 | -0.035729 | 0.03209 | -0.00083919 | -0.013017 | 0.010875 | 0.03535 | -0.0086451 | 0.04012 | -62.265 | 0.010564 | -62.2822 | 60.1938 | 59.9934 | 60.1217 | -62.2586 | -62.2511 | 0.082776 | -62.3589 | 60.0262 | 60.1765 | 59.9554 | -62.4177 | 0.029314 | -0.075334 | 0.022876 | 0.005722 | -0.023592 | -0.27574 | -0.14751 | -0.12984 | -0.243 | 0.036811 | -0.070953 | 0.058891 | -0.092621 | -0.31377 | 122.4817 | 122.2813 | 122.4096 | 62.2985 | -122.5278 | 122.3141 | 122.4644 | 122.2433 | 62.3707 | -122.6869
208.7812 | 122.7676 | -62.2833 | 60.1959 | 1.4211e-13 | -0.0080727 | -0.01265 | 0.017011 | -0.035942 | 0.032304 | 0.0067908 | -0.013017 | 0.011303 | 0.035564 | -0.0084315 | 0.039693 | -62.2696 | 0.010564 | -62.2776 | 60.1938 | 59.998 | 60.1217 | -62.2677 | -62.2511 | 0.082776 | -62.3451 | 60.0262 | 60.1811 | 59.9646 | -62.4086 | 0.015578 | -0.002092 | 0.013719 | 0.005722 | -0.009856 | -0.19792 | -0.074264 | -0.12526 | -0.16976 | 0.032233 | -0.061795 | 0.06347 | -0.014801 | -0.23137 | 122.4772 | 122.2813 | 122.405 | 62.2939 | -122.4637 | 122.3095 | 122.4644 | 122.2479 | 62.3661 | -122.6045
210.5625 | 122.818 | -62.2559 | 60.2234 | 1.4211e-13 | -0.0080727 | -0.012436 | 0.016584 | -0.035729 | 0.03209 | -0.0084697 | -0.013231 | 0.010875 | 0.035564 | -0.0082179 | 0.040334 | -62.2604 | 0.010564 | -62.2639 | 60.1938 | 60.0026 | 60.1125 | -62.2677 | -62.2465 | 0.082776 | -62.3589 | 60.017 | 60.1811 | 59.96 | -62.4132 | -0.011888 | -0.029558 | -0.00459 | -0.008009 | 0.003879 | -0.2208 | -0.11089 | -0.15731 | -0.20638 | 0.009346 | -0.103 | 0.054313 | -0.042267 | -0.26342 | 122.4497 | 122.2584 | 122.3684 | 62.2664 | -122.4911 | 122.2729 | 122.437 | 122.2158 | 62.3386 | -122.6366
212.2812 | 122.8363 | -62.2559 | 60.2371 | 1.4211e-13 | -0.0082863 | -0.012436 | 0.016584 | -0.035942 | 0.032517 | 0.0067908 | -0.013231 | 0.010662 | 0.03535 | -0.0084315 | 0.04012 | -62.265 | 0.010564 | -62.273 | 60.1938 | 60.0072 | 60.1262 | -62.2723 | -62.2511 | 0.082776 | -62.3497 | 60.017 | 60.1765 | 59.9691 | -62.4132 | -0.016467 | -0.043291 | -0.009168 | -0.017166 | -0.000699 | -0.22996 | -0.11088 | -0.15731 | -0.22011 | 0.004767 | -0.09384 | 0.06347 | -0.060578 | -0.26799 | 122.4497 | 122.263 | 122.3821 | 62.2664 | -122.5094 | 122.2729 | 122.4324 | 122.225 | 62.3386 | -122.6503
214.0781 | 122.7951 | -62.2696 | 60.1822 | 1.4211e-13 | -0.0078589 | -0.012436 | 0.016798 | -0.035942 | 0.03209 | -0.0084697 | -0.013017 | 0.010875 | 0.03535 | -0.0082179 | 0.040334 | -62.2696 | 0.015142 | -62.273 | 60.1893 | 60.0072 | 60.1171 | -62.2632 | -62.2511 | 0.073618 | -62.3497 | 60.0216 | 60.1765 | 59.96 | -62.4086 | 0.006424 | 0.007062 | -1.4e-05 | -0.003433 | -0.009857 | -0.17502 | -0.06511 | -0.139 | -0.1606 | 0.0185 | -0.080107 | 0.058891 | -0.005646 | -0.22222 | 122.4588 | 122.2768 | 122.3867 | 62.2847 | -122.4454 | 122.2912 | 122.4461 | 122.2296 | 62.3432 | -122.5908
215.7969 | 122.7219 | -62.2696 | 60.2554 | 1.4211e-13 | -0.0082863 | -0.01265 | 0.016798 | -0.03637 | 0.032304 | -0.0084697 | -0.013017 | 0.010662 | 0.035564 | -0.0086451 | 0.039479 | -62.2604 | 0.015142 | -62.273 | 60.1938 | 60.0026 | 60.1171 | -62.2677 | -62.2465 | 0.078197 | -62.3543 | 60.0216 | 60.1765 | 59.96 | -62.3994 | 0.001845 | -0.061601 | 0.009143 | -0.003433 | -0.005278 | -0.25285 | -0.13835 | -0.12984 | -0.23384 | 0.023079 | -0.084685 | 0.045155 | -0.078888 | -0.29546 | 122.4634 | 122.2722 | 122.3867 | 62.2847 | -122.5232 | 122.2912 | 122.4461 | 122.2296 | 62.3478 | -122.6549
217.5781 | 122.6578 | -62.2971 | 60.2783 | 1.4211e-13 | -0.0082863 | -0.012436 | 0.016584 | -0.036156 | 0.03209 | 0.0067908 | -0.013017 | 0.010662 | 0.03535 | -0.0084315 | 0.04012 | -62.265 | 0.010564 | -62.273 | 60.1893 | 60.0026 | 60.1217 | -62.2586 | -62.2419 | 0.091933 | -62.3634 | 60.0262 | 60.1857 | 59.9691 | -62.4132 | 0.038469 | -0.089068 | 0.032031 | 0.024033 | -0.014436 | -0.27573 | -0.15666 | -0.11611 | -0.25215 | 0.055124 | -0.066377 | 0.049734 | -0.092619 | -0.30919 | 122.4863 | 122.2996 | 122.4187 | 62.3076 | -122.5369 | 122.3232 | 122.4828 | 122.2662 | 62.389 | -122.6915
219.2812 | 122.731 | -62.265 | 60.2417 | 1.4211e-13 | -0.0082863 | -0.01265 | 0.016798 | -0.035942 | 0.031876 | -0.00083919 | -0.013017 | 0.010875 | 0.035136 | -0.0080041 | 0.039693 | -62.265 | 0.010564 | -62.273 | 60.1938 | 59.9934 | 60.1171 | -62.2677 | -62.2419 | 0.087354 | -62.3543 | 60.0216 | 60.1811 | 59.96 | -62.404 | -0.002732 | -0.047868 | -1.2e-05 | -0.00801 | -0.005278 | -0.24827 | -0.12462 | -0.139 | -0.22011 | 0.023081 | -0.089262 | 0.049734 | -0.060577 | -0.28173 | 122.4588 | 122.2584 | 122.3821 | 62.2756 | -122.5094 | 122.2866 | 122.4461 | 122.225 | 62.3524 | -122.6457
221.0625 | 122.8088 | -62.2787 | 60.1959 | 1.4211e-13 | -0.0080727 | -0.012436 | 0.016584 | -0.035942 | 0.032517 | 0.0067908 | -0.013444 | 0.010875 | 0.03535 | -0.0084315 | 0.040334 | -62.2559 | 0.010564 | -62.273 | 60.1984 | 60.0072 | 60.1262 | -62.2586 | -62.2419 | 0.087354 | -62.3497 | 60.017 | 60.172 | 59.9646 | -62.4086 | 0.020159 | 0.002486 | 0.022877 | 0.005723 | -0.014436 | -0.18876 | -0.069685 | -0.12984 | -0.17891 | 0.036814 | -0.070951 | 0.058891 | -0.023958 | -0.23137 | 122.4772 | 122.2859 | 122.405 | 62.2893 | -122.4545 | 122.2958 | 122.4507 | 122.2433 | 62.3661 | -122.6045
222.8281 | 122.6669 | -62.2879 | 60.2646 | 1.4211e-13 | -0.0082863 | -0.012436 | 0.016584 | -0.036156 | 0.03209 | -0.0084697 | -0.012803 | 0.010875 | 0.035564 | -0.0084315 | 0.04012 | -62.265 | 0.010564 | -62.273 | 60.1938 | 59.9934 | 60.1262 | -62.2586 | -62.2419 | 0.082776 | -62.3589 | 60.0262 | 60.172 | 59.9554 | -62.3994 | 0.029314 | -0.070756 | 0.022876 | 0.014878 | -0.014436 | -0.27116 | -0.13835 | -0.11153 | -0.23842 | 0.045969 | -0.070953 | 0.040576 | -0.092622 | -0.30919 | 122.4817 | 122.2813 | 122.4141 | 62.2985 | -122.5232 | 122.3141 | 122.4599 | 122.2433 | 62.3707 | -122.664
224.6094 | 122.8043 | -62.265 | 60.1913 | 1.4211e-13 | -0.0084999 | -0.01265 | 0.01637 | -0.035942 | 0.03209 | -0.00083919 | -0.013017 | 0.010875 | 0.035136 | -0.0084315 | 0.039906 | -62.2604 | 0.019721 | -62.2639 | 60.1847 | 59.998 | 60.1171 | -62.2632 | -62.2511 | 0.087354 | -62.3497 | 60.0216 | 60.1628 | 59.9554 | -62.4132 | 0.001847 | -0.006671 | 0.004566 | 0.001147 | -0.0007 | -0.19334 | -0.074265 | -0.14815 | -0.16976 | 0.013923 | -0.084684 | 0.06347 | -0.028537 | -0.23595 | 122.4497 | 122.263 | 122.3821 | 62.2847 | -122.4545 | 122.2866 | 122.4278 | 122.2204 | 62.3524 | -122.6045
226.3125 | 122.7951 | -62.2604 | 60.1776 | 1.4211e-13 | -0.0080727 | -0.012436 | 0.017011 | -0.03637 | 0.032304 | -0.00083919 | -0.013231 | 0.010875 | 0.035564 | -0.0082179 | 0.04012 | -62.265 | 0.019721 | -62.273 | 60.1893 | 59.998 | 60.1217 | -62.2586 | -62.2419 | 0.082776 | -62.3497 | 60.0262 | 60.172 | 59.9646 | -62.4086 | 0.001848 | 0.01164 | -0.00459 | -0.012588 | -0.014436 | -0.17961 | -0.055953 | -0.14815 | -0.15145 | 0.018503 | -0.089262 | 0.058891 | -0.005647 | -0.21306 | 122.4497 | 122.2584 | 122.3821 | 62.2802 | -122.4362 | 122.2866 | 122.4324 | 122.225 | 62.3432 | -122.5862
228.0781 | 122.7859 | -62.2879 | 60.2005 | 1.4211e-13 | -0.0082863 | -0.01265 | 0.01637 | -0.035942 | 0.032304 | 0.0067908 | -0.013017 | 0.010662 | 0.035564 | -0.0082179 | 0.039693 | -62.2696 | 0.015142 | -62.273 | 60.1801 | 60.0026 | 60.1217 | -62.2586 | -62.2374 | 0.087354 | -62.3497 | 60.017 | 60.1765 | 59.9508 | -62.404 | 0.029314 | -0.020405 | 0.018297 | 0.014878 | -0.014436 | -0.19791 | -0.078841 | -0.11611 | -0.18349 | 0.050548 | -0.061796 | 0.054312 | -0.023956 | -0.24968 | 122.468 | 122.2905 | 122.4096 | 62.303 | -122.4591 | 122.3049 | 122.4644 | 122.2387 | 62.3753 | -122.6045
229.8594 | 122.7127 | -62.2742 | 60.2509 | 1.4211e-13 | -0.0080727 | -0.012009 | 0.016584 | -0.035729 | 0.03209 | -0.00083919 | -0.012803 | 0.011089 | 0.03535 | -0.0086451 | 0.039693 | -62.265 | 0.010564 | -62.2684 | 60.1847 | 59.998 | 60.1262 | -62.254 | -62.2374 | 0.087354 | -62.3497 | 60.0079 | 60.172 | 59.9508 | -62.4086 | 0.02016 | -0.06618 | 0.009143 | 0.005724 | -0.014436 | -0.25285 | -0.12462 | -0.13442 | -0.243 | 0.036815 | -0.075529 | 0.058891 | -0.078889 | -0.30004 | 122.4588 | 122.2722 | 122.4004 | 62.2847 | -122.5049 | 122.282 | 122.4461 | 122.225 | 62.3615 | -122.6594
231.625 | 122.6715 | -62.3016 | 60.2554 | 1.4211e-13 | -0.0080727 | -0.012222 | 0.016584 | -0.036156 | 0.031663 | -0.00083919 | -0.013017 | 0.010875 | 0.035136 | -0.0082179 | 0.040334 | -62.2513 | 0.015142 | -62.2684 | 60.1893 | 59.9934 | 60.1125 | -62.254 | -62.2419 | 0.087354 | -62.3405 | 60.017 | 60.172 | 59.9691 | -62.4086 | 0.047626 | -0.06618 | 0.050344 | 0.03319 | -0.014436 | -0.262 | -0.14293 | -0.10695 | -0.23842 | 0.059702 | -0.038905 | 0.068049 | -0.083467 | -0.2863 | 122.4909 | 122.2951 | 122.4141 | 62.3168 | -122.5094 | 122.3186 | 122.4736 | 122.2708 | 62.389 | -122.664
233.3281 | 122.7905 | -62.2696 | 60.1639 | 1.4211e-13 | -0.0082863 | -0.01265 | 0.017011 | -0.035942 | 0.031663 | -0.00083919 | -0.013231 | 0.011089 | 0.03535 | -0.0080041 | 0.039693 | -62.2559 | 0.010564 | -62.273 | 60.1801 | 59.998 | 60.1171 | -62.2632 | -62.2419 | 0.082776 | -62.3497 | 60.017 | 60.172 | 59.9646 | -62.4086 | 0.006424 | 0.016216 | 0.013721 | -0.003433 | -0.009857 | -0.16587 | -0.046799 | -0.139 | -0.14687 | 0.027658 | -0.080107 | 0.058891 | 0.008086 | -0.19933 | 122.4497 | 122.2676 | 122.3867 | 62.2802 | -122.427 | 122.2866 | 122.4416 | 122.2341 | 62.3524 | -122.5725
235.1094 | 122.7127 | -62.2787 | 60.2188 | 1.4211e-13 | -0.0082863 | -0.012863 | 0.016584 | -0.036156 | 0.032304 | -0.00083919 | -0.013017 | 0.010662 | 0.035564 | -0.0084315 | 0.039906 | -62.2513 | 0.015142 | -62.2776 | 60.1893 | 60.0026 | 60.1079 | -62.2586 | -62.2465 | 0.087354 | -62.3451 | 60.0216 | 60.1765 | 59.9646 | -62.404 | 0.020159 | -0.029559 | 0.027456 | 0.001145 | -0.019014 | -0.21623 | -0.11089 | -0.12526 | -0.19722 | 0.032235 | -0.066372 | 0.058891 | -0.042267 | -0.25426 | 122.468 | 122.2813 | 122.3867 | 62.2939 | -122.4774 | 122.3003 | 122.4553 | 122.2433 | 62.3661 | -122.6228
236.9062 | 122.6532 | -62.2833 | 60.2692 | 1.4211e-13 | -0.0084999 | -0.012222 | 0.016584 | -0.036156 | 0.03209 | 0.0067908 | -0.01259 | 0.010662 | 0.03535 | -0.0077905 | 0.04012 | -62.265 | 0.015142 | -62.273 | 60.1847 | 59.9934 | 60.1171 | -62.2586 | -62.2374 | 0.087354 | -62.3497 | 60.0216 | 60.172 | 59.9646 | -62.404 | 0.024736 | -0.084491 | 0.018298 | 0.0103 | -0.014436 | -0.27574 | -0.15208 | -0.12069 | -0.24758 | 0.04597 | -0.066374 | 0.054312 | -0.0972 | -0.30461 | 122.468 | 122.2768 | 122.4004 | 62.2985 | -122.5278 | 122.3049 | 122.4553 | 122.2479 | 62.3707 | -122.6732
238.6875 | 122.7905 | -62.2513 | 60.2325 | 1.4211e-13 | -0.0082863 | -0.012863 | 0.016584 | -0.035942 | 0.031876 | 0.0067908 | -0.013017 | 0.011089 | 0.035564 | -0.0080041 | 0.04012 | -62.2559 | 0.015142 | -62.2639 | 60.1893 | 59.9934 | 60.1171 | -62.2586 | -62.2419 | 0.078197 | -62.3497 | 60.0216 | 60.1765 | 59.9508 | -62.4086 | -0.007307 | -0.043292 | -0.004589 | -0.012586 | -0.005279 | -0.23912 | -0.11546 | -0.15731 | -0.21095 | 0.009348 | -0.098417 | 0.058891 | -0.056 | -0.28173 | 122.4405 | 122.2447 | 122.3684 | 62.2664 | -122.4911 | 122.2729 | 122.4278 | 122.2021 | 62.3295 | -122.6411
240.4688 | 122.7905 | -62.2559 | 60.2188 | 1.4211e-13 | -0.0080727 | -0.012436 | 0.016798 | -0.035942 | 0.03209 | 0.0067908 | -0.013231 | 0.010662 | 0.03535 | -0.0084315 | 0.039693 | -62.2604 | 0.010564 | -62.273 | 60.1893 | 59.9888 | 60.1262 | -62.2586 | -62.2419 | 0.078197 | -62.3543 | 60.017 | 60.172 | 59.9508 | -62.4132 | -0.00273 | -0.029559 | -0.00459 | -0.017166 | -0.014436 | -0.22996 | -0.092573 | -0.15731 | -0.2018 | 0.013925 | -0.098418 | 0.058892 | -0.046846 | -0.268 | 122.4451 | 122.2447 | 122.3821 | 62.2664 | -122.4774 | 122.2729 | 122.4278 | 122.2067 | 62.3341 | -122.632
242.25 | 122.7814 | -62.2284 | 60.228 | 1.4211e-13 | -0.0082863 | -0.012436 | 0.016584 | -0.035942 | 0.031876 | -0.00083919 | -0.013231 | 0.010875 | 0.03535 | -0.0080041 | 0.039906 | -62.2604 | 0.015142 | -62.2684 | 60.1755 | 59.9843 | 60.1171 | -62.2494 | -62.2374 | 0.082776 | -62.3543 | 60.0262 | 60.172 | 59.9462 | -62.4132 | -0.021037 | -0.052449 | -0.032055 | -0.040052 | -0.019015 | -0.2437 | -0.11089 | -0.18478 | -0.2018 | -0.008961 | -0.12588 | 0.058892 | -0.056001 | -0.28173 | 122.4039 | 122.2127 | 122.3455 | 62.2435 | -122.4774 | 122.2546 | 122.4004 | 122.1746 | 62.3112 | -122.6411
243.9688 | 122.7173 | -62.265 | 60.2554 | 1.4211e-13 | -0.0078589 | -0.01265 | 0.01637 | -0.035942 | 0.031663 | -0.00083919 | -0.013231 | 0.010875 | 0.03535 | -0.0077905 | 0.04012 | -62.2513 | 0.010564 | -62.273 | 60.1847 | 60.0026 | 60.1171 | -62.2586 | -62.2419 | 0.082776 | -62.3497 | 60.017 | 60.172 | 59.9554 | -62.4086 | 0.006426 | -0.070758 | 0.013723 | -0.00801 | -0.014436 | -0.25285 | -0.13835 | -0.14357 | -0.23842 | 0.023081 | -0.084684 | 0.058891 | -0.083467 | -0.30004 | 122.4497 | 122.2676 | 122.3821 | 62.2756 | -122.514 | 122.282 | 122.437 | 122.2204 | 62.3478 | -122.664
245.75 | 122.7814 | -62.2513 | 60.228 | 1.4211e-13 | -0.0078589 | -0.012436 | 0.016584 | -0.036156 | 0.03209 | -0.00083919 | -0.013231 | 0.010875 | 0.03535 | -0.0082179 | 0.04012 | -62.2604 | 0.010564 | -62.2684 | 60.1755 | 59.9934 | 60.1079 | -62.2677 | -62.2419 | 0.082776 | -62.3451 | 60.0124 | 60.172 | 59.96 | -62.4086 | -0.016465 | -0.052449 | -0.009167 | -0.017164 | -0.000699 | -0.23454 | -0.12004 | -0.15731 | -0.21553 | 0.009348 | -0.093838 | 0.06347 | -0.056001 | -0.26799 | 122.4268 | 122.2447 | 122.3592 | 62.2618 | -122.4957 | 122.2637 | 122.4232 | 122.2113 | 62.3341 | -122.6366
247.5312 | 122.6532 | -62.2604 | 60.26 | 1.4211e-13 | -0.0080727 | -0.01265 | 0.01637 | -0.035942 | 0.031663 | -0.00083919 | -0.012803 | 0.010875 | 0.034923 | -0.0082179 | 0.039479 | -62.2559 | 0.010564 | -62.2684 | 60.1801 | 59.998 | 60.1171 | -62.2586 | -62.2374 | 0.082776 | -62.3497 | 60.017 | 60.1674 | 59.9508 | -62.404 | 0.001848 | -0.079915 | 0.004566 | -0.008009 | -0.009857 | -0.262 | -0.14293 | -0.14357 | -0.243 | 0.023082 | -0.089262 | 0.054312 | -0.092624 | -0.3092 | 122.4405 | 122.2584 | 122.3775 | 62.271 | -122.5186 | 122.2774 | 122.4278 | 122.2113 | 62.3432 | -122.664
249.2344 | 122.7585 | -62.233 | 60.228 | 1.4211e-13 | -0.0078589 | -0.012436 | 0.016584 | -0.035942 | 0.031876 | -0.0084697 | -0.013017 | 0.010662 | 0.035777 | -0.0080041 | 0.039693 | -62.2513 | 0.015142 | -62.2639 | 60.1801 | 59.9888 | 60.1125 | -62.2586 | -62.2374 | 0.082776 | -62.3451 | 60.0124 | 60.172 | 59.9554 | -62.3994 | -0.025618 | -0.047871 | -0.018321 | -0.030897 | -0.005279 | -0.23912 | -0.11546 | -0.16646 | -0.21553 | -0.004384 | -0.11215 | 0.054312 | -0.056001 | -0.27257 | 122.4131 | 122.2218 | 122.3455 | 62.2481 | -122.4866 | 122.2454 | 122.4049 | 122.1884 | 62.3157 | -122.6274
251.0156 | 122.7676 | -62.2513 | 60.1822 | 1.4211e-13 | -0.0080727 | -0.012863 | 0.016584 | -0.036156 | 0.03209 | -0.00083919 | -0.013444 | 0.010875 | 0.03535 | -0.0082179 | 0.04012 | -62.2467 | 0.015142 | -62.2593 | 60.1847 | 59.9934 | 60.1171 | -62.2586 | -62.2374 | 0.082776 | -62.3497 | 60.0124 | 60.172 | 59.96 | -62.404 | -0.007307 | 0.002484 | 0.004568 | -0.008008 | -0.000701 | -0.18876 | -0.06511 | -0.15273 | -0.16976 | 0.013927 | -0.098417 | 0.054312 | -0.010225 | -0.22222 | 122.436 | 122.2447 | 122.3684 | 62.2664 | -122.4408 | 122.2637 | 122.4232 | 122.2113 | 62.3341 | -122.5862
252.7969 | 122.7356 | -62.2742 | 60.1913 | 1.4211e-13 | -0.0080727 | -0.012436 | 0.016584 | -0.035942 | 0.031876 | -0.00083919 | -0.013231 | 0.010662 | 0.03535 | -0.0084315 | 0.039693 | -62.2559 | 0.019721 | -62.2684 | 60.1893 | 59.9934 | 60.1171 | -62.254 | -62.2328 | 0.078197 | -62.3405 | 60.017 | 60.1674 | 59.9554 | -62.404 | 0.02016 | -0.002093 | 0.018299 | 0.005724 | -0.014436 | -0.19792 | -0.074265 | -0.12984 | -0.17433 | 0.041393 | -0.066371 | 0.06347 | -0.023959 | -0.23595 | 122.4634 | 122.2676 | 122.3912 | 62.2939 | -122.4454 | 122.2912 | 122.4416 | 122.2296 | 62.3524 | -122.5954
254.5781 | 122.6395 | -62.2787 | 60.26 | 1.4211e-13 | -0.0080727 | -0.012863 | 0.01637 | -0.03637 | 0.03209 | -0.00083919 | -0.013444 | 0.010662 | 0.03535 | -0.0075769 | 0.039906 | -62.2604 | 0.015142 | -62.2684 | 60.1801 | 59.9888 | 60.1125 | -62.254 | -62.2328 | 0.073618 | -62.3451 | 60.017 | 60.172 | 59.9462 | -62.3994 | 0.024738 | -0.079915 | 0.018299 | 0.010302 | -0.014436 | -0.27116 | -0.14751 | -0.12068 | -0.243 | 0.045971 | -0.066372 | 0.054312 | -0.088045 | -0.31377 | 122.4588 | 122.2676 | 122.3912 | 62.2939 | -122.514 | 122.2958 | 122.4507 | 122.225 | 62.3524 | -122.6594
256.3594 | 122.644 | -62.2696 | 60.2325 | 1.4211e-13 | -0.0078589 | -0.01265 | 0.01637 | -0.036156 | 0.031876 | 0.0067908 | -0.013231 | 0.010662 | 0.03535 | -0.0082179 | 0.039265 | -62.2559 | 0.010564 | -62.273 | 60.1847 | 59.9934 | 60.1125 | -62.2494 | -62.2328 | 0.078197 | -62.3405 | 60.0216 | 60.1628 | 59.9508 | -62.3994 | 0.020161 | -0.04787 | 0.013721 | -0.003433 | -0.023594 | -0.23912 | -0.12004 | -0.12984 | -0.21095 | 0.036815 | -0.070949 | 0.058891 | -0.069736 | -0.28173 | 122.4543 | 122.263 | 122.3821 | 62.2802 | -122.482 | 122.2912 | 122.4324 | 122.2204 | 62.3478 | -122.632
258.0625 | 122.7402 | -62.2742 | 60.228 | 1.4211e-13 | -0.0078589 | -0.012436 | 0.016584 | -0.035729 | 0.031876 | -0.0084697 | -0.013444 | 0.010875 | 0.03535 | -0.0080041 | 0.039906 | -62.2559 | 0.005985 | -62.2684 | 60.1893 | 59.998 | 60.1125 | -62.254 | -62.2419 | 0.073618 | -62.3405 | 60.0124 | 60.1674 | 59.9554 | -62.404 | 0.02016 | -0.038714 | 0.018299 | 0.005724 | -0.014436 | -0.22996 | -0.11546 | -0.12984 | -0.21553 | 0.032236 | -0.066371 | 0.06347 | -0.06058 | -0.27257 | 122.4634 | 122.2722 | 122.3867 | 62.2802 | -122.482 | 122.2866 | 122.4416 | 122.2296 | 62.3478 | -122.632
259.8438 | 122.7631 | -62.2742 | 60.1639 | 1.4211e-13 | -0.0078589 | -0.012436 | 0.01637 | -0.035942 | 0.031876 | -0.00083919 | -0.013444 | 0.010662 | 0.035564 | -0.0082179 | 0.04012 | -62.2513 | 0.010564 | -62.2684 | 60.1801 | 59.9934 | 60.1171 | -62.2494 | -62.2282 | 0.082776 | -62.3405 | 60.0079 | 60.1674 | 59.96 | -62.404 | 0.024739 | 0.016216 | 0.022878 | 0.005724 | -0.019015 | -0.17045 | -0.046799 | -0.12984 | -0.15603 | 0.045972 | -0.066371 | 0.06347 | 0.003507 | -0.20391 | 122.4543 | 122.2676 | 122.3912 | 62.2847 | -122.4133 | 122.282 | 122.4416 | 122.2341 | 62.3569 | -122.5679
261.6406 | 122.7036 | -62.2421 | 60.2646 | 1.4211e-13 | -0.0076453 | -0.012436 | 0.016584 | -0.035942 | 0.031876 | -0.00083919 | -0.013017 | 0.010875 | 0.03535 | -0.0082179 | 0.039906 | -62.2559 | 0.015142 | -62.2593 | 60.1755 | 59.9888 | 60.1125 | -62.2586 | -62.2328 | 0.082776 | -62.3405 | 60.017 | 60.1674 | 59.9554 | -62.404 | -0.016463 | -0.08907 | -0.013745 | -0.017164 | -0.000701 | -0.27574 | -0.15208 | -0.16188 | -0.24758 | 0.009349 | -0.098415 | 0.06347 | -0.097201 | -0.30919 | 122.4176 | 122.231 | 122.3546 | 62.2573 | -122.5232 | 122.2591 | 122.4095 | 122.1975 | 62.3249 | -122.6686
263.3438 | 122.7081 | -62.2375 | 60.26 | 1.4211e-13 | -0.0080727 | -0.012436 | 0.01637 | -0.035729 | 0.031876 | 0.0067908 | -0.012803 | 0.010875 | 0.035136 | -0.0082179 | 0.039906 | -62.2559 | 0.010564 | -62.2684 | 60.1755 | 59.9934 | 60.1171 | -62.254 | -62.2328 | 0.078197 | -62.3405 | 60.0124 | 60.1628 | 59.9462 | -62.3994 | -0.016461 | -0.084493 | -0.018322 | -0.030897 | -0.014436 | -0.26658 | -0.14293 | -0.16188 | -0.24758 | 0.004772 | -0.10299 | 0.058891 | -0.097202 | -0.31377 | 122.4131 | 122.231 | 122.3546 | 62.2481 | -122.514 | 122.25 | 122.4004 | 122.1838 | 62.3157 | -122.6594
265.1094 | 122.6852 | -62.2421 | 60.2509 | 1.4211e-13 | -0.0080727 | -0.01265 | 0.016584 | -0.036156 | 0.031876 | -0.00083919 | -0.013017 | 0.010875 | 0.03535 | -0.0075769 | 0.039906 | -62.2513 | 0.005985 | -62.2639 | 60.1801 | 59.9888 | 60.1125 | -62.254 | -62.2282 | 0.082776 | -62.3451 | 60.0124 | 60.172 | 59.9417 | -62.404 | -0.011884 | -0.070759 | -0.009166 | -0.021742 | -0.009858 | -0.262 | -0.13835 | -0.16188 | -0.23842 | 0.013928 | -0.10299 | 0.058891 | -0.078889 | -0.3092 | 122.4222 | 122.231 | 122.3546 | 62.2481 | -122.5049 | 122.2546 | 122.4141 | 122.1838 | 62.3249 | -122.6549
266.8906 | 122.7585 | -62.2467 | 60.2234 | 1.4211e-13 | -0.0080727 | -0.01265 | 0.016584 | -0.036156 | 0.03209 | -0.00083919 | -0.013017 | 0.010875 | 0.03535 | -0.0077905 | 0.039693 | -62.2467 | 0.010564 | -62.2684 | 60.1755 | 59.9934 | 60.1171 | -62.254 | -62.2282 | 0.078197 | -62.3451 | 60.017 | 60.172 | 59.9554 | -62.3994 | -0.007306 | -0.047872 | -1e-05 | -0.021742 | -0.014436 | -0.22996 | -0.10631 | -0.15273 | -0.20638 | 0.018506 | -0.098416 | 0.054312 | -0.051424 | -0.268 | 122.4222 | 122.2401 | 122.3638 | 62.2573 | -122.4774 | 122.2637 | 122.4187 | 122.2021 | 62.3249 | -122.6228
268.6719 | 122.6212 | -62.2604 | 60.2692 | 1.4211e-13 | -0.0080727 | -0.012436 | 0.016798 | -0.036156 | 0.031235 | 0.014421 | -0.013231 | 0.010875 | 0.035136 | -0.0082179 | 0.039693 | -62.2513 | 0.010564 | -62.2639 | 60.1755 | 59.9888 | 60.1171 | -62.2494 | -62.2328 | 0.087354 | -62.3405 | 60.0124 | 60.172 | 59.9462 | -62.4086 | 0.011006 | -0.093648 | 0.009145 | -0.003431 | -0.014437 | -0.28032 | -0.15208 | -0.14815 | -0.25673 | 0.02766 | -0.080104 | 0.068049 | -0.0972 | -0.32293 | 122.436 | 122.2493 | 122.3775 | 62.271 | -122.5186 | 122.2729 | 122.4324 | 122.2067 | 62.3478 | -122.6778
270.4531 | 122.7905 | -62.2467 | 60.1959 | 1.4211e-13 | -0.0080727 | -0.01265 | 0.016157 | -0.035942 | 0.031876 | -0.00083919 | -0.013231 | 0.010448 | 0.035136 | -0.0077905 | 0.039906 | -62.2467 | 0.015142 | -62.2593 | 60.1847 | 59.9934 | 60.1217 | -62.254 | -62.2374 | 0.082776 | -62.3405 | 60.0079 | 60.1628 | 59.9508 | -62.3994 | -0.007306 | -0.011249 | -1e-05 | -0.012586 | -0.00528 | -0.20249 | -0.074264 | -0.15273 | -0.18807 | 0.009349 | -0.093837 | 0.058891 | -0.033115 | -0.24511 | 122.4314 | 122.2401 | 122.3684 | 62.2618 | -122.4499 | 122.2546 | 122.4095 | 122.1975 | 62.3295 | -122.5954
272.1562 | 122.7722 | -62.2559 | 60.2097 | 1.4211e-13 | -0.0080727 | -0.012009 | 0.016584 | -0.03637 | 0.03209 | -0.00083919 | -0.013444 | 0.011089 | 0.03535 | -0.0080041 | 0.04012 | -62.2513 | 0.005985 | -62.2684 | 60.1801 | 59.9797 | 60.1125 | -62.2403 | -62.2236 | 0.078197 | -62.3314 | 60.0079 | 60.1674 | 59.9462 | -62.404 | 0.015585 | -0.029561 | 0.004567 | -0.012587 | -0.028172 | -0.22996 | -0.097154 | -0.14815 | -0.2018 | 0.03224 | -0.075525 | 0.072627 | -0.04227 | -0.26342 | 122.436 | 122.2356 | 122.3684 | 62.2618 | -122.4499 | 122.2637 | 122.4232 | 122.2021 | 62.3341 | -122.6137
273.9219 | 122.7722 | -62.2421 | 60.2325 | 1.4211e-13 | -0.0076453 | -0.012436 | 0.01637 | -0.03637 | 0.031876 | 0.0067908 | -0.012803 | 0.010448 | 0.035564 | -0.0080041 | 0.039906 | -62.2467 | 0.010564 | -62.2684 | 60.1755 | 59.9934 | 60.1217 | -62.2586 | -62.2236 | 0.087354 | -62.336 | 60.0124 | 60.1582 | 59.9508 | -62.3994 | -0.016463 | -0.057027 | -0.004588 | -0.02632 | -0.009857 | -0.23912 | -0.11088 | -0.15731 | -0.22011 | 0.018507 | -0.093837 | 0.063469 | -0.074315 | -0.28173 | 122.4176 | 122.2356 | 122.3638 | 62.2527 | -122.4911 | 122.2546 | 122.4004 | 122.1929 | 62.3295 | -122.632
275.7031 | 122.6669 | -62.2467 | 60.2737 | 1.4211e-13 | -0.0080727 | -0.01265 | 0.016584 | -0.036156 | 0.031876 | -0.00083919 | -0.013231 | 0.010662 | 0.035136 | -0.0080041 | 0.039906 | -62.2513 | 0.010564 | -62.2593 | 60.1709 | 59.9888 | 60.1217 | -62.2449 | -62.2328 | 0.082776 | -62.336 | 60.0033 | 60.1674 | 59.9462 | -62.3994 | 0.001851 | -0.1028 | -0.004588 | -0.012586 | -0.014437 | -0.28489 | -0.15208 | -0.15273 | -0.27047 | 0.013927 | -0.089259 | 0.063469 | -0.10636 | -0.32751 | 122.4176 | 122.2356 | 122.3684 | 62.2573 | -122.5186 | 122.25 | 122.4141 | 122.1929 | 62.3295 | -122.6732
277.4219 | 122.6166 | -62.2833 | 60.2509 | 1.4211e-13 | -0.0078589 | -0.01265 | 0.016584 | -0.035729 | 0.031876 | 0.0067908 | -0.013017 | 0.010875 | 0.034923 | -0.0080041 | 0.04012 | -62.2467 | 0.010564 | -62.2593 | 60.1755 | 59.9888 | 60.1079 | -62.2586 | -62.2282 | 0.082776 | -62.336 | 60.0079 | 60.1674 | 59.9554 | -62.3994 | 0.024736 | -0.075337 | 0.036611 | 0.024035 | -0.000701 | -0.262 | -0.14293 | -0.11611 | -0.243 | 0.055127 | -0.052638 | 0.063469 | -0.083468 | -0.29546 | 122.4588 | 122.2722 | 122.3912 | 62.2939 | -122.5094 | 122.2912 | 122.4507 | 122.2387 | 62.3661 | -122.6503
279.2031 | 122.7814 | -62.2513 | 60.2005 | 1.4211e-13 | -0.0078589 | -0.012436 | 0.01637 | -0.036156 | 0.031876 | 0.0067908 | -0.013017 | 0.010875 | 0.035136 | -0.0080041 | 0.039693 | -62.2513 | 0.010564 | -62.2593 | 60.1755 | 59.9934 | 60.1171 | -62.2494 | -62.2328 | 0.087354 | -62.3405 | 60.0079 | 60.1811 | 59.9508 | -62.404 | 0.001851 | -0.024983 | -1e-05 | -0.008008 | -0.009859 | -0.20707 | -0.08342 | -0.15273 | -0.19265 | 0.018505 | -0.089259 | 0.06347 | -0.019378 | -0.24968 | 122.4268 | 122.2447 | 122.3684 | 62.2618 | -122.4499 | 122.2591 | 122.4324 | 122.2021 | 62.3386 | -122.6045
280.9844 | 122.7585 | -62.2513 | 60.1959 | 1.4211e-13 | -0.0078589 | -0.012222 | 0.01637 | -0.035942 | 0.031876 | -0.00083919 | -0.013444 | 0.010448 | 0.03535 | -0.0075769 | 0.04012 | -62.2513 | 0.010564 | -62.2593 | 60.1801 | 60.0026 | 60.1171 | -62.2449 | -62.2282 | 0.082776 | -62.3314 | 60.0033 | 60.172 | 59.96 | -62.404 | 0.006429 | -0.015828 | -1e-05 | -0.008008 | -0.014437 | -0.19334 | -0.078843 | -0.15273 | -0.19265 | 0.023084 | -0.080102 | 0.072627 | -0.023958 | -0.23595 | 122.4314 | 122.2539 | 122.3684 | 62.2618 | -122.4408 | 122.2546 | 122.4232 | 122.2113 | 62.3341 | -122.5999
282.7031 | 122.7493 | -62.2467 | 60.1959 | 1.4211e-13 | -0.0080727 | -0.01265 | 0.01637 | -0.035942 | 0.031663 | 0.0067908 | -0.013017 | 0.010875 | 0.035136 | -0.0077905 | 0.039906 | -62.2467 | 0.010564 | -62.2639 | 60.1755 | 59.9888 | 60.1171 | -62.2494 | -62.2282 | 0.091933 | -62.3405 | 60.0124 | 60.1674 | 59.9508 | -62.3949 | -0.002727 | -0.020406 | -1e-05 | -0.017164 | -0.014437 | -0.20707 | -0.078843 | -0.14815 | -0.18349 | 0.018506 | -0.093837 | 0.054312 | -0.028537 | -0.24511 | 122.4222 | 122.2356 | 122.3638 | 62.2573 | -122.4454 | 122.2591 | 122.4141 | 122.1975 | 62.3386 | -122.5908
284.5 | 122.7493 | -62.2513 | 60.1868 | 1.4211e-13 | -0.0076453 | -0.01265 | 0.016584 | -0.035942 | 0.031663 | -0.00083919 | -0.013017 | 0.010662 | 0.035136 | -0.0075769 | 0.039693 | -62.2513 | 0.015142 | -62.2593 | 60.1801 | 59.998 | 60.1171 | -62.254 | -62.2328 | 0.091933 | -62.336 | 60.0079 | 60.1628 | 59.9554 | -62.3994 | -0.002728 | -0.006673 | -1e-05 | -0.008008 | -0.00528 | -0.18876 | -0.069688 | -0.14815 | -0.17892 | 0.018505 | -0.084681 | 0.063469 | -0.02396 | -0.23137 | 122.4314 | 122.2493 | 122.3684 | 62.2664 | -122.4408 | 122.2591 | 122.4141 | 122.2067 | 62.3432 | -122.5862
286.2812 | 122.6486 | -62.2742 | 60.2692 | 1.4211e-13 | -0.0078589 | -0.01265 | 0.016584 | -0.035729 | 0.031663 | -0.00083919 | -0.013231 | 0.010662 | 0.035564 | -0.0077905 | 0.04012 | -62.2513 | 0.010564 | -62.2593 | 60.1709 | 59.9888 | 60.1217 | -62.2449 | -62.2328 | 0.087354 | -62.3405 | 60.0079 | 60.1674 | 59.9462 | -62.3994 | 0.029317 | -0.098226 | 0.022878 | 0.01488 | -0.014437 | -0.28032 | -0.14751 | -0.12526 | -0.26131 | 0.041393 | -0.066371 | 0.058891 | -0.10178 | -0.32293 | 122.4451 | 122.263 | 122.3958 | 62.2847 | -122.514 | 122.282 | 122.4416 | 122.2204 | 62.3615 | -122.6686
288.0469 | 122.7173 | -62.265 | 60.2188 | 1.4211e-13 | -0.0082863 | -0.012863 | 0.01637 | -0.035942 | 0.031663 | -0.00083919 | -0.013231 | 0.010662 | 0.03535 | -0.0080041 | 0.039906 | -62.2467 | 0.010564 | -62.2593 | 60.1755 | 60.0026 | 60.1125 | -62.2494 | -62.2282 | 0.078197 | -62.336 | 60.0124 | 60.1674 | 59.9508 | -62.3994 | 0.015584 | -0.043294 | 0.018301 | 0.005725 | -0.009859 | -0.21623 | -0.10631 | -0.13442 | -0.20638 | 0.036817 | -0.070948 | 0.063469 | -0.051425 | -0.268 | 122.4405 | 122.2676 | 122.3775 | 62.2756 | -122.4682 | 122.2774 | 122.4324 | 122.2158 | 62.3432 | -122.6182
289.8281 | 122.7722 | -62.2238 | 60.1959 | 1.4211e-13 | -0.0082863 | -0.01265 | 0.016584 | -0.035942 | 0.031663 | -0.0084697 | -0.013444 | 0.010448 | 0.035136 | -0.0075769 | 0.039906 | -62.2376 | 0.019721 | -62.2639 | 60.1755 | 59.9888 | 60.1125 | -62.2449 | -62.2282 | 0.087354 | -62.336 | 60.0124 | 60.1628 | 59.9508 | -62.404 | -0.021037 | -0.020406 | -0.013741 | -0.040052 | -0.019015 | -0.20707 | -0.083421 | -0.18019 | -0.18349 | -0.004382 | -0.11215 | 0.068048 | -0.033115 | -0.24511 | 122.3993 | 122.2127 | 122.3363 | 62.2435 | -122.4408 | 122.2362 | 122.3866 | 122.1746 | 62.3112 | -122.5999
291.5469 | 122.6349 | -62.2559 | 60.2463 | 1.4211e-13 | -0.0080727 | -0.01265 | 0.01637 | -0.035942 | 0.031876 | -0.0084697 | -0.013017 | 0.010875 | 0.035564 | -0.0075769 | 0.040334 | -62.2467 | 0.015142 | -62.2593 | 60.1801 | 59.9888 | 60.1171 | -62.2403 | -62.2236 | 0.082776 | -62.3314 | 60.0079 | 60.1674 | 59.9508 | -62.3994 | 0.015585 | -0.066182 | 0.009145 | -0.003431 | -0.019016 | -0.25743 | -0.1292 | -0.14357 | -0.23842 | 0.03224 | -0.075525 | 0.068048 | -0.078891 | -0.29546 | 122.436 | 122.2447 | 122.3729 | 62.271 | -122.4866 | 122.2637 | 122.4232 | 122.2067 | 62.3386 | -122.6457
293.3125 | 122.7905 | -62.2421 | 60.1959 | 1.4211e-13 | -0.0082863 | -0.012222 | 0.01637 | -0.035942 | 0.031663 | -0.0161 | -0.013017 | 0.010662 | 0.035136 | -0.0077905 | 0.040334 | -62.2376 | 0.015142 | -62.2547 | 60.1755 | 59.9888 | 60.1171 | -62.2494 | -62.2282 | 0.082776 | -62.3314 | 60.0124 | 60.172 | 59.9417 | -62.404 | -0.007305 | -0.020406 | 0.004569 | -0.012586 | -0.005281 | -0.20707 | -0.078843 | -0.16188 | -0.18349 | 0.013928 | -0.089258 | 0.072627 | -0.023958 | -0.25427 | 122.4176 | 122.231 | 122.3592 | 62.2573 | -122.4454 | 122.2546 | 122.4141 | 122.1838 | 62.3249 | -122.5999
295.0156 | 122.6669 | -62.2559 | 60.26 | 1.4211e-13 | -0.0078589 | -0.012436 | 0.016584 | -0.03637 | 0.03209 | 0.0067908 | -0.013231 | 0.010448 | 0.035136 | -0.0073631 | 0.04012 | -62.2513 | 0.015142 | -62.2593 | 60.1709 | 59.998 | 60.1125 | -62.2494 | -62.2282 | 0.082776 | -62.336 | 60.0079 | 60.1628 | 59.9417 | -62.3994 | 0.006428 | -0.089071 | 0.004567 | -0.003431 | -0.009859 | -0.262 | -0.14751 | -0.14357 | -0.25216 | 0.027661 | -0.080104 | 0.063469 | -0.097202 | -0.31835 | 122.4268 | 122.2539 | 122.3684 | 62.271 | -122.5094 | 122.2637 | 122.4187 | 122.1975 | 62.3386 | -122.6594
296.8125 | 122.6212 | -62.2787 | 60.2463 | 1.4211e-13 | -0.0080727 | -0.012222 | 0.016584 | -0.036156 | 0.031663 | -0.00083919 | -0.013231 | 0.010662 | 0.035136 | -0.0075769 | 0.039693 | -62.2376 | 0.005985 | -62.2547 | 60.1709 | 59.9888 | 60.1079 | -62.2449 | -62.2282 | 0.082776 | -62.336 | 60.0079 | 60.1582 | 59.9462 | -62.3949 | 0.033895 | -0.075338 | 0.041191 | 0.024036 | -0.009859 | -0.25743 | -0.13835 | -0.1161 | -0.23842 | 0.05055 | -0.057215 | 0.05889 | -0.088048 | -0.30004 | 122.4497 | 122.2676 | 122.3867 | 62.2847 | -122.4911 | 122.2866 | 122.437 | 122.225 | 62.3615 | -122.6411
298.5938 | 122.6852 | -62.2787 | 60.2051 | 1.4211e-13 | -0.0076453 | -0.012222 | 0.01637 | -0.035942 | 0.031663 | 0.014421 | -0.013017 | 0.011089 | 0.035564 | -0.0077905 | 0.039479 | -62.2467 | 0.019721 | -62.2639 | 60.1709 | 59.9888 | 60.1033 | -62.254 | -62.2282 | 0.078197 | -62.3314 | 60.0079 | 60.1628 | 59.9462 | -62.3949 | 0.024738 | -0.034139 | 0.032034 | 0.01488 | -0.009858 | -0.21623 | -0.10173 | -0.1161 | -0.19723 | 0.05055 | -0.052636 | 0.063469 | -0.04227 | -0.25884 | 122.4497 | 122.2676 | 122.3821 | 62.2985 | -122.4591 | 122.2866 | 122.4416 | 122.225 | 62.3569 | -122.5999
300.375 | 122.7585 | -62.233 | 60.1685 | 1.4211e-13 | -0.0078589 | -0.012222 | 0.01637 | -0.036156 | 0.031876 | 0.0067908 | -0.013017 | 0.010662 | 0.035136 | -0.0075769 | 0.04012 | -62.2467 | 0.010564 | -62.2547 | 60.1755 | 59.9888 | 60.1079 | -62.2494 | -62.2236 | 0.082776 | -62.3314 | 60.0079 | 60.1582 | 59.9462 | -62.3994 | -0.01646 | 0.00706 | -0.013743 | -0.021741 | -0.005281 | -0.17961 | -0.060534 | -0.16646 | -0.1606 | 0.009352 | -0.098413 | 0.068048 | -0.010228 | -0.22222 | 122.4085 | 122.2218 | 122.3409 | 62.2435 | -122.4179 | 122.2408 | 122.3912 | 122.1792 | 62.3157 | -122.5679
302.0938 | 122.6486 | -62.2696 | 60.2692 | 1.4211e-13 | -0.0080727 | -0.01265 | 0.016798 | -0.036156 | 0.031876 | 0.0067908 | -0.013658 | 0.010448 | 0.034923 | -0.0075769 | 0.04012 | -62.2421 | 0.010564 | -62.2547 | 60.1755 | 59.9934 | 60.1125 | -62.2449 | -62.2328 | 0.082776 | -62.3314 | 60.0079 | 60.1582 | 59.9462 | -62.3949 | 0.024739 | -0.093648 | 0.027457 | 0.01488 | -0.009859 | -0.27574 | -0.15666 | -0.12526 | -0.26131 | 0.036815 | -0.061792 | 0.063469 | -0.11094 | -0.32293 | 122.4451 | 122.263 | 122.3821 | 62.2802 | -122.514 | 122.2774 | 122.4278 | 122.2158 | 62.3524 | -122.664
303.875 | 122.7493 | -62.2192 | 60.2142 | 1.4211e-13 | -0.0078589 | -0.01265 | 0.016157 | -0.036156 | 0.03209 | 0.014421 | -0.013231 | 0.010662 | 0.03535 | -0.0077905 | 0.039693 | -62.2376 | 0.015142 | -62.2547 | 60.1709 | 59.9888 | 60.1125 | -62.2449 | -62.2282 | 0.082776 | -62.336 | 60.0033 | 60.1674 | 59.9417 | -62.3994 | -0.025615 | -0.043294 | -0.018319 | -0.035474 | -0.009859 | -0.22538 | -0.10173 | -0.18019 | -0.21096 | -0.00896 | -0.11673 | 0.063469 | -0.046847 | -0.27258 | 122.3902 | 122.2081 | 122.3317 | 62.2344 | -122.4591 | 122.2225 | 122.3866 | 122.1609 | 62.302 | -122.6137
305.5938 | 122.6532 | -62.2375 | 60.2509 | 1.4211e-13 | -0.0076453 | -0.012222 | 0.016584 | -0.035729 | 0.031235 | -0.0084697 | -0.013017 | 0.010875 | 0.035136 | -0.0071495 | 0.04012 | -62.2421 | 0.010564 | -62.2593 | 60.1801 | 59.9934 | 60.1125 | -62.2449 | -62.2282 | 0.082776 | -62.3314 | 60.0079 | 60.1628 | 59.9508 | -62.3994 | -0.007304 | -0.070759 | -0.004586 | -0.021741 | -0.014437 | -0.25743 | -0.13835 | -0.16188 | -0.243 | 0.009351 | -0.093835 | 0.068048 | -0.088046 | -0.30004 | 122.4176 | 122.231 | 122.3501 | 62.2481 | -122.4957 | 122.2454 | 122.4004 | 122.1884 | 62.3203 | -122.6503
307.375 | 122.6395 | -62.2467 | 60.2371 | 1.4211e-13 | -0.0080727 | -0.012009 | 0.01637 | -0.036156 | 0.031876 | -0.0084697 | -0.013658 | 0.010662 | 0.034923 | -0.0077905 | 0.039906 | -62.2421 | 0.010564 | -62.2593 | 60.1709 | 59.9888 | 60.1125 | -62.2449 | -62.2282 | 0.087354 | -62.3314 | 59.9987 | 60.1582 | 59.9462 | -62.3949 | 0.001851 | -0.066183 | 0.004569 | -0.012586 | -0.014437 | -0.24827 | -0.12462 | -0.14815 | -0.23843 | 0.018506 | -0.08468 | 0.063469 | -0.078893 | -0.29089 | 122.4176 | 122.2356 | 122.3592 | 62.2573 | -122.482 | 122.2454 | 122.4049 | 122.1929 | 62.3341 | -122.632
309.1719 | 122.731 | -62.2467 | 60.1868 | 1.4211e-13 | -0.0080727 | -0.012436 | 0.016157 | -0.036156 | 0.031663 | 0.0067908 | -0.013658 | 0.010662 | 0.03535 | -0.0073631 | 0.04012 | -62.2467 | 0.010564 | -62.2547 | 60.1755 | 60.0026 | 60.1079 | -62.2403 | -62.219 | 0.082776 | -62.3268 | 60.017 | 60.1628 | 59.9462 | -62.3994 | 0.00643 | -0.011251 | -1e-05 | -0.008008 | -0.014438 | -0.18418 | -0.078845 | -0.15273 | -0.16976 | 0.027663 | -0.080101 | 0.072627 | -0.02396 | -0.24053 | 122.4222 | 122.2493 | 122.3546 | 62.2573 | -122.427 | 122.2637 | 122.4095 | 122.1929 | 62.3295 | -122.5862
310.8906 | 122.6578 | -62.2604 | 60.2509 | 1.4211e-13 | -0.0078589 | -0.01265 | 0.01637 | -0.036156 | 0.031663 | -0.00083919 | -0.013231 | 0.011089 | 0.035136 | -0.0077905 | 0.039479 | -62.2376 | 0.010564 | -62.2593 | 60.1755 | 59.9888 | 60.1125 | -62.2449 | -62.2236 | 0.082776 | -62.336 | 60.0124 | 60.1628 | 59.9417 | -62.3994 | 0.015584 | -0.075337 | 0.02288 | 0.001147 | -0.014437 | -0.262 | -0.13835 | -0.13899 | -0.23842 | 0.036818 | -0.075526 | 0.063469 | -0.088046 | -0.3092 | 122.436 | 122.2493 | 122.3729 | 62.271 | -122.4957 | 122.2729 | 122.4232 | 122.2021 | 62.3432 | -122.6503
312.6875 | 122.7631 | -62.2467 | 60.2005 | 1.4211e-13 | -0.0076453 | -0.01265 | 0.01637 | -0.036583 | 0.031449 | -0.0084697 | -0.013231 | 0.010662 | 0.035136 | -0.0075769 | 0.039906 | -62.233 | 0.015142 | -62.2593 | 60.1709 | 59.9797 | 60.1171 | -62.2494 | -62.2236 | 0.082776 | -62.3268 | 60.0033 | 60.1628 | 59.9371 | -62.3949 | -0.002727 | -0.029561 | 0.013725 | -0.012586 | -0.009859 | -0.22081 | -0.08342 | -0.14815 | -0.19722 | 0.023085 | -0.080101 | 0.068048 | -0.037692 | -0.26342 | 122.4176 | 122.2264 | 122.3638 | 62.2618 | -122.4499 | 122.25 | 122.4095 | 122.1838 | 62.3295 | -122.5954
314.4062 | 122.6715 | -62.2375 | 60.26 | 1.4211e-13 | -0.0076453 | -0.012436 | 0.016798 | -0.036156 | 0.031876 | 0.0067908 | -0.013444 | 0.010662 | 0.035136 | -0.0075769 | 0.039906 | -62.2421 | 0.010564 | -62.2501 | 60.1709 | 59.9888 | 60.1079 | -62.2403 | -62.2236 | 0.082776 | -62.3314 | 60.0124 | 60.1628 | 59.9462 | -62.3949 | -0.002725 | -0.089071 | -0.004586 | -0.012584 | -0.009859 | -0.27116 | -0.15209 | -0.1573 | -0.24758 | 0.01393 | -0.093835 | 0.063469 | -0.097202 | -0.31377 | 122.4085 | 122.2264 | 122.3455 | 62.2481 | -122.5003 | 122.25 | 122.4004 | 122.1838 | 62.3203 | -122.6549
316.1875 | 122.6486 | -62.2421 | 60.2188 | 1.4211e-13 | -0.0076453 | -0.01265 | 0.01637 | -0.036156 | 0.031449 | -0.00083919 | -0.013444 | 0.011089 | 0.03535 | -0.0077905 | 0.039906 | -62.2467 | 0.010564 | -62.2501 | 60.1755 | 59.9934 | 60.1079 | -62.2449 | -62.2282 | 0.087354 | -62.3314 | 59.9987 | 60.1628 | 59.9417 | -62.3949 | -0.002727 | -0.043294 | -0.004588 | -0.008007 | -0.00528 | -0.22538 | -0.11089 | -0.15273 | -0.22011 | 0.013928 | -0.089258 | 0.063469 | -0.056003 | -0.27715 | 122.4176 | 122.2356 | 122.35 | 62.2527 | -122.4637 | 122.2408 | 122.4049 | 122.1838 | 62.3295 | -122.6137
317.9531 | 122.7768 | -62.233 | 60.1593 | 1.4211e-13 | -0.0078589 | -0.01265 | 0.01637 | -0.035942 | 0.031663 | -0.00083919 | -0.013231 | 0.010448 | 0.03535 | -0.0073631 | 0.04012 | -62.2376 | 0.015142 | -62.2501 | 60.1755 | 59.9888 | 60.1125 | -62.2449 | -62.219 | 0.082776 | -62.3268 | 59.9987 | 60.1674 | 59.9462 | -62.3949 | -0.011882 | 0.016215 | -0.004586 | -0.017162 | -0.00528 | -0.17045 | -0.0468 | -0.16188 | -0.16061 | 0.01393 | -0.093834 | 0.068048 | 0.008084 | -0.21307 | 122.4085 | 122.2218 | 122.3455 | 62.2481 | -122.4042 | 122.2317 | 122.4004 | 122.1792 | 62.3157 | -122.5542
319.6719 | 122.6257 | -62.2284 | 60.2554 | 1.4211e-13 | -0.0080727 | -0.013291 | 0.016157 | -0.03637 | 0.031449 | -0.00083919 | -0.013444 | 0.010875 | 0.035136 | -0.0073631 | 0.039693 | -62.2376 | 0.010564 | -62.2547 | 60.1664 | 59.9797 | 60.1079 | -62.2403 | -62.219 | 0.087354 | -62.336 | 60.0033 | 60.172 | 59.9325 | -62.3903 | -0.01188 | -0.089072 | -0.009163 | -0.026318 | -0.014438 | -0.27574 | -0.14751 | -0.16188 | -0.25216 | 0.009353 | -0.10757 | 0.054311 | -0.083467 | -0.32293 | 122.3948 | 122.2081 | 122.3363 | 62.239 | -122.4957 | 122.2317 | 122.4004 | 122.1609 | 62.3157 | -122.6457
321.4531 | 122.6532 | -62.2513 | 60.2646 | 1.4211e-13 | -0.0080727 | -0.01265 | 0.015943 | -0.036156 | 0.031235 | -0.0084697 | -0.013658 | 0.010662 | 0.03535 | -0.0073631 | 0.039479 | -62.2376 | 0.005985 | -62.2501 | 60.1709 | 59.9797 | 60.1125 | -62.2403 | -62.2145 | 0.082776 | -62.3268 | 60.0033 | 60.1628 | 59.9371 | -62.3994 | 0.011008 | -0.093648 | 0.013725 | 0.001149 | -0.009859 | -0.28489 | -0.15208 | -0.14815 | -0.26131 | 0.03682 | -0.075523 | 0.072627 | -0.10178 | -0.32751 | 122.4222 | 122.231 | 122.3638 | 62.2573 | -122.5049 | 122.2546 | 122.4141 | 122.1884 | 62.3341 | -122.664
323.2344 | 122.7631 | -62.233 | 60.2234 | 1.4211e-13 | -0.0078589 | -0.012436 | 0.01637 | -0.035942 | 0.031663 | -0.00083919 | -0.013231 | 0.010662 | 0.035136 | -0.0073631 | 0.039906 | -62.2376 | 0.010564 | -62.2456 | 60.1755 | 59.9934 | 60.1171 | -62.2449 | -62.219 | 0.078197 | -62.3222 | 60.0079 | 60.1674 | 59.9371 | -62.3949 | -0.011882 | -0.047872 | -0.004586 | -0.012584 | -0.000702 | -0.22996 | -0.10631 | -0.16188 | -0.21554 | 0.01393 | -0.089255 | 0.072627 | -0.056003 | -0.28631 | 122.4085 | 122.2264 | 122.3501 | 62.2435 | -122.4682 | 122.2408 | 122.4004 | 122.1701 | 62.3112 | -122.6182
325.0156 | 122.7493 | -62.2421 | 60.1685 | 1.4211e-13 | -0.0080727 | -0.012436 | 0.016798 | -0.036156 | 0.031449 | -0.00083919 | -0.013444 | 0.010875 | 0.035136 | -0.0077905 | 0.04012 | -62.2421 | 0.010564 | -62.2501 | 60.1709 | 59.9934 | 60.1125 | -62.2403 | -62.2236 | 0.087354 | -62.336 | 59.9941 | 60.1628 | 59.9417 | -62.3994 | 0.001852 | 0.002482 | -9e-06 | -0.008007 | -0.009859 | -0.17503 | -0.055955 | -0.15731 | -0.17434 | 0.018507 | -0.093837 | 0.063469 | -0.005649 | -0.2268 | 122.4131 | 122.2356 | 122.3546 | 62.2527 | -122.4087 | 122.2362 | 122.4049 | 122.1838 | 62.3295 | -122.5679
326.7969 | 122.6578 | -62.2421 | 60.2966 | 1.4211e-13 | -0.0078589 | -0.012436 | 0.015943 | -0.035942 | 0.031663 | -0.00083919 | -0.013231 | 0.010662 | 0.03535 | -0.0075769 | 0.039693 | -62.2376 | 0.015142 | -62.2501 | 60.1618 | 59.9797 | 60.1079 | -62.2311 | -62.219 | 0.087354 | -62.3268 | 59.9987 | 60.1765 | 59.9371 | -62.3994 | 0.01101 | -0.13485 | 0.004569 | -0.008007 | -0.019017 | -0.31694 | -0.18871 | -0.15731 | -0.29793 | 0.023085 | -0.084679 | 0.072627 | -0.12009 | -0.35955 | 122.4039 | 122.2218 | 122.35 | 62.2573 | -122.5277 | 122.2408 | 122.4187 | 122.1792 | 62.3295 | -122.6961
328.5 | 122.7448 | -62.2467 | 60.1868 | 1.4211e-13 | -0.0078589 | -0.012436 | 0.016584 | -0.036156 | 0.031449 | 0.0067908 | -0.013231 | 0.011089 | 0.035136 | -0.0075769 | 0.039906 | -62.233 | 0.019721 | -62.2456 | 60.1755 | 59.9843 | 60.1125 | -62.2357 | -62.219 | 0.087354 | -62.3314 | 59.9987 | 60.1628 | 59.9371 | -62.3949 | 0.011009 | -0.011251 | 0.013725 | 0.001149 | -0.00986 | -0.2025 | -0.074266 | -0.14815 | -0.18807 | 0.027663 | -0.08468 | 0.063469 | -0.02396 | -0.24969 | 122.4222 | 122.231 | 122.3592 | 62.2664 | -122.4225 | 122.2454 | 122.4095 | 122.1838 | 62.3341 | -122.5816
330.2812 | 122.6212 | -62.2696 | 60.2371 | 1.4211e-13 | -0.0078589 | -0.012009 | 0.016584 | -0.036156 | 0.031876 | 0.0067908 | -0.013231 | 0.010662 | 0.035136 | -0.0071495 | 0.039906 | -62.2467 | 0.010564 | -62.2593 | 60.1664 | 59.9843 | 60.1125 | -62.2494 | -62.219 | 0.082776 | -62.3268 | 60.0033 | 60.1628 | 59.9462 | -62.3949 | 0.020161 | -0.070762 | 0.022878 | 0.010302 | -0.009859 | -0.25285 | -0.12462 | -0.12526 | -0.23385 | 0.050551 | -0.057213 | 0.068048 | -0.074314 | -0.29089 | 122.436 | 122.2539 | 122.3821 | 62.2802 | -122.4866 | 122.2729 | 122.4324 | 122.2158 | 62.3524 | -122.632
332.0625 | 122.7493 | -62.2559 | 60.1822 | 1.4211e-13 | -0.0080727 | -0.012436 | 0.016157 | -0.036156 | 0.031663 | -0.00083919 | -0.013658 | 0.010662 | 0.035136 | -0.0075769 | 0.040334 | -62.2376 | 0.010564 | -62.2501 | 60.1618 | 59.9934 | 60.1125 | -62.254 | -62.2145 | 0.082776 | -62.3222 | 60.0033 | 60.1582 | 59.96 | -62.3903 | 0.001849 | -0.020408 | 0.018302 | 0.005726 | 0.003877 | -0.18876 | -0.069688 | -0.13441 | -0.17891 | 0.041397 | -0.066367 | 0.068048 | -0.023961 | -0.22222 | 122.4176 | 122.2493 | 122.3684 | 62.2664 | -122.4362 | 122.2591 | 122.4141 | 122.2158 | 62.3386 | -122.5725
333.8438 | 122.7173 | -62.2284 | 60.1959 | 1.4211e-13 | -0.0078589 | -0.01265 | 0.016798 | -0.035729 | 0.031449 | -0.0084697 | -0.013658 | 0.010448 | 0.034709 | -0.0077905 | 0.039693 | -62.2376 | 0.019721 | -62.2456 | 60.1664 | 59.9843 | 60.1125 | -62.2403 | -62.219 | 0.082776 | -62.3222 | 59.9987 | 60.1628 | 59.9417 | -62.3949 | -0.01188 | -0.029563 | -0.009163 | -0.017161 | -0.005281 | -0.21165 | -0.083421 | -0.16646 | -0.19723 | 0.009353 | -0.093832 | 0.072627 | -0.033115 | -0.25427 | 122.3948 | 122.2127 | 122.3409 | 62.2481 | -122.4362 | 122.2271 | 122.3912 | 122.1701 | 62.3112 | -122.5908
335.6094 | 122.7127 | -62.233 | 60.2371 | 1.4211e-13 | -0.0078589 | -0.01265 | 0.016584 | -0.035942 | 0.031876 | -0.00083919 | -0.013231 | 0.010448 | 0.035136 | -0.0075769 | 0.039479 | -62.233 | 0.015142 | -62.2456 | 60.1755 | 59.9843 | 60.1079 | -62.2449 | -62.2145 | 0.082776 | -62.3268 | 60.0033 | 60.1582 | 59.9325 | -62.3949 | -0.011882 | -0.061605 | -8e-06 | -0.012584 | -0.000702 | -0.25285 | -0.1292 | -0.16188 | -0.23385 | 0.018509 | -0.093834 | 0.068048 | -0.078893 | -0.30462 | 122.4085 | 122.2172 | 122.3409 | 62.2481 | -122.482 | 122.2362 | 122.3912 | 122.1655 | 62.3157 | -122.632
337.3281 | 122.7036 | -62.265 | 60.1868 | 1.4211e-13 | -0.0078589 | -0.012436 | 0.01637 | -0.03637 | 0.031663 | 0.0067908 | -0.013231 | 0.010875 | 0.03535 | -0.0073631 | 0.039906 | -62.2376 | 0.015142 | -62.2501 | 60.1664 | 59.9934 | 60.1171 | -62.2494 | -62.219 | 0.091933 | -62.3222 | 59.9987 | 60.1582 | 59.9417 | -62.3857 | 0.015584 | -0.020408 | 0.027458 | 0.014882 | -0.000702 | -0.19334 | -0.069688 | -0.12068 | -0.18807 | 0.045974 | -0.057211 | 0.06347 | -0.028539 | -0.24511 | 122.4314 | 122.2584 | 122.3821 | 62.2802 | -122.4362 | 122.2637 | 122.4232 | 122.2067 | 62.3569 | -122.5725
339.1094 | 122.644 | -62.2559 | 60.2371 | 1.4211e-13 | -0.0078589 | -0.01265 | 0.016584 | -0.036156 | 0.031235 | -0.00083919 | -0.013017 | 0.010662 | 0.034923 | -0.0073631 | 0.039693 | -62.233 | 0.019721 | -62.2456 | 60.1709 | 59.9843 | 60.1171 | -62.2357 | -62.219 | 0.082776 | -62.3268 | 60.0033 | 60.1628 | 59.9417 | -62.3949 | 0.020164 | -0.066183 | 0.02288 | 0.010304 | -0.00986 | -0.25285 | -0.12004 | -0.13899 | -0.23385 | 0.036818 | -0.070946 | 0.068048 | -0.074314 | -0.29546 | 122.4268 | 122.2401 | 122.3729 | 62.2756 | -122.4728 | 122.2591 | 122.4187 | 122.1975 | 62.3386 | -122.632
340.8281 | 122.612 | -62.233 | 60.26 | 1.4211e-13 | -0.0080727 | -0.012222 | 0.016798 | -0.036156 | 0.031663 | -0.0084697 | -0.013444 | 0.010662 | 0.03535 | -0.0073631 | 0.039479 | -62.233 | 0.019721 | -62.2547 | 60.1664 | 59.9888 | 60.1125 | -62.2403 | -62.219 | 0.082776 | -62.3268 | 59.9987 | 60.1537 | 59.9325 | -62.3903 | -0.007303 | -0.09365 | -8e-06 | -0.021741 | -0.014438 | -0.27116 | -0.14751 | -0.1573 | -0.26131 | 0.01393 | -0.093834 | 0.063469 | -0.10636 | -0.32751 | 122.3993 | 122.2218 | 122.3455 | 62.2527 | -122.5003 | 122.2317 | 122.3866 | 122.1655 | 62.3157 | -122.6503
342.6094 | 122.7493 | -62.2421 | 60.173 | 1.4211e-13 | -0.0078589 | -0.012436 | 0.01637 | -0.03637 | 0.031663 | -0.00083919 | -0.013017 | 0.010448 | 0.034923 | -0.0073631 | 0.039693 | -62.2238 | 0.010564 | -62.241 | 60.1664 | 59.9843 | 60.1079 | -62.2449 | -62.2099 | 0.087354 | -62.3268 | 59.9987 | 60.1628 | 59.9417 | -62.3994 | -0.002727 | -0.006675 | 0.018304 | 0.001149 | 0.003876 | -0.18876 | -0.065112 | -0.15731 | -0.17434 | 0.032243 | -0.084679 | 0.072627 | -0.010227 | -0.23138 | 122.4085 | 122.2264 | 122.35 | 62.2527 | -122.4179 | 122.2408 | 122.4049 | 122.1838 | 62.3295 | -122.5725
344.375 | 122.644 | -62.2375 | 60.26 | 1.4211e-13 | -0.0078589 | -0.012222 | 0.016584 | -0.036156 | 0.031449 | 0.0067908 | -0.013231 | 0.010662 | 0.035136 | -0.0075769 | 0.039693 | -62.2284 | 0.015142 | -62.2501 | 60.1664 | 59.9843 | 60.1079 | -62.2403 | -62.219 | 0.082776 | -62.336 | 60.0033 | 60.1628 | 59.9417 | -62.3994 | -0.002725 | -0.09365 | 0.009149 | -0.012584 | -0.009859 | -0.27574 | -0.15209 | -0.16188 | -0.25673 | 0.018508 | -0.098414 | 0.063469 | -0.097202 | -0.31835 | 122.4039 | 122.2218 | 122.3455 | 62.2527 | -122.5003 | 122.2408 | 122.4004 | 122.1792 | 62.3203 | -122.6594
346.0938 | 122.7081 | -62.2238 | 60.1959 | 1.4211e-13 | -0.0080727 | -0.012222 | 0.016798 | -0.036156 | 0.031449 | -0.0161 | -0.013231 | 0.010662 | 0.034923 | -0.0075769 | 0.039693 | -62.233 | 0.015142 | -62.2456 | 60.1618 | 59.9797 | 60.1171 | -62.2311 | -62.2145 | 0.082776 | -62.3222 | 59.9987 | 60.1582 | 59.9325 | -62.3903 | -0.0073 | -0.034141 | -0.009163 | -0.021739 | -0.014439 | -0.21623 | -0.078843 | -0.16646 | -0.19723 | 0.009354 | -0.09841 | 0.068048 | -0.037694 | -0.26342 | 122.3856 | 122.2035 | 122.3409 | 62.239 | -122.427 | 122.2225 | 122.382 | 122.1563 | 62.3066 | -122.5862
347.875 | 122.6761 | -62.2238 | 60.2325 | 1.4211e-13 | -0.0078589 | -0.012436 | 0.016157 | -0.035729 | 0.031449 | 0.0067908 | -0.013231 | 0.010448 | 0.034923 | -0.0071495 | 0.039693 | -62.2284 | 0.015142 | -62.241 | 60.1618 | 59.9888 | 60.1125 | -62.2311 | -62.2145 | 0.082776 | -62.3268 | 60.0033 | 60.1582 | 59.9508 | -62.404 | -0.0073 | -0.070762 | -0.004584 | -0.017161 | -0.009861 | -0.24369 | -0.12004 | -0.18019 | -0.22927 | 0.009354 | -0.10299 | 0.077206 | -0.074315 | -0.28173 | 122.3856 | 122.2127 | 122.3363 | 62.239 | -122.4637 | 122.2271 | 122.382 | 122.1746 | 62.3066 | -122.6366
349.6719 | 122.6852 | -62.2284 | 60.2005 | 1.4211e-13 | -0.0076453 | -0.012436 | 0.01637 | -0.036156 | 0.031663 | -0.00083919 | -0.013231 | 0.010448 | 0.03535 | -0.0075769 | 0.039693 | -62.233 | 0.010564 | -62.2456 | 60.1709 | 59.9888 | 60.1171 | -62.2449 | -62.2099 | 0.078197 | -62.3222 | 60.0033 | 60.1628 | 59.9417 | -62.3949 | -0.016459 | -0.029561 | -0.004585 | -0.017161 | -0.000702 | -0.21165 | -0.08342 | -0.16646 | -0.19722 | 0.018511 | -0.093832 | 0.072627 | -0.037692 | -0.25884 | 122.3993 | 122.2172 | 122.3455 | 62.239 | -122.4454 | 122.2317 | 122.3912 | 122.1701 | 62.3066 | -122.5954
351.4531 | 122.6944 | -62.2604 | 60.1822 | 1.4211e-13 | -0.0078589 | -0.012436 | 0.01637 | -0.03637 | 0.031449 | -0.0084697 | -0.013444 | 0.010662 | 0.035136 | -0.0073631 | 0.039693 | -62.178 | 0.019721 | -62.2547 | 60.1709 | 59.9934 | 60.1217 | -62.2403 | -62.2099 | 0.087354 | -62.3268 | 60.0079 | 60.1582 | 59.9417 | -62.3949 | 0.020163 | -0.011251 | 0.082399 | 0.005725 | -0.014438 | -0.18876 | -0.060531 | -0.13442 | -0.17434 | 0.050554 | -0.066368 | 0.068048 | -0.023961 | -0.24053 | 122.4314 | 122.2539 | 122.3821 | 62.2802 | -122.4225 | 122.2683 | 122.4187 | 122.2021 | 62.3478 | -122.577
353.1719 | 122.7539 | -62.2147 | 60.173 | 1.4211e-13 | -0.0078589 | -0.012436 | 0.01637 | -0.03637 | 0.031449 | 0.0067908 | -0.013444 | 0.010662 | 0.035136 | -0.0071495 | 0.039693 | -62.1826 | 0.015142 | -62.2501 | 60.1618 | 59.9843 | 60.1079 | -62.2403 | -62.2145 | 0.078197 | -62.3176 | 59.9987 | 60.1537 | 59.9462 | -62.3949 | -0.025613 | -0.011253 | 0.032045 | -0.035472 | -0.009859 | -0.18876 | -0.065112 | -0.18019 | -0.17434 | 0.000199 | -0.10299 | 0.077205 | -0.019384 | -0.2268 | 122.3764 | 122.1989 | 122.3226 | 62.2298 | -122.4133 | 122.2134 | 122.3683 | 122.1609 | 62.2929 | -122.5679
354.9531 | 122.6669 | -62.2375 | 60.2188 | 1.4211e-13 | -0.0076453 | -0.012436 | 0.016584 | -0.036156 | 0.031876 | -0.0084697 | -0.013231 | 0.010662 | 0.034923 | -0.0071495 | 0.039693 | -62.1872 | 0.010564 | -62.2501 | 60.1618 | 59.9751 | 60.1079 | -62.2403 | -62.2145 | 0.082776 | -62.3268 | 60.0033 | 60.1491 | 59.9325 | -62.3949 | -0.002725 | -0.057029 | 0.050354 | -0.012584 | -0.009859 | -0.2437 | -0.11089 | -0.1573 | -0.21554 | 0.023087 | -0.089256 | 0.068048 | -0.069739 | -0.28631 | 122.3993 | 122.2127 | 122.3455 | 62.2481 | -122.4591 | 122.2408 | 122.3866 | 122.17 | 62.3203 | -122.6137
356.6719 | 122.6349 | -62.2513 | 60.2417 | 1.4211e-13 | -0.0080727 | -0.012436 | 0.01637 | -0.036156 | 0.031449 | 0.0067908 | -0.013231 | 0.010448 | 0.034923 | -0.0071495 | 0.039693 | -62.178 | 0.015142 | -62.2318 | 60.1709 | 59.9843 | 60.1079 | -62.2357 | -62.2053 | 0.082776 | -62.3222 | 59.9941 | 60.1537 | 59.9279 | -62.3949 | 0.015587 | -0.07076 | 0.073244 | 0.019462 | 0.003875 | -0.25743 | -0.13378 | -0.14357 | -0.24758 | 0.045978 | -0.070944 | 0.072627 | -0.088048 | -0.31378 | 122.4222 | 122.2356 | 122.3592 | 62.2664 | -122.4774 | 122.2454 | 122.4049 | 122.1792 | 62.3341 | -122.6366
358.4375 | 122.7493 | -62.2101 | 60.1868 | 1.4211e-13 | -0.0078589 | -0.012222 | 0.016157 | -0.036583 | 0.031663 | -0.00083919 | -0.013444 | 0.010234 | 0.035136 | -0.0075769 | 0.039906 | -62.178 | 0.019721 | -62.2364 | 60.1664 | 59.9843 | 60.1125 | -62.2357 | -62.2099 | 0.078197 | -62.3222 | 59.9987 | 60.1537 | 59.9279 | -62.3903 | -0.025612 | -0.020408 | 0.032045 | -0.026315 | -0.000703 | -0.2025 | -0.074266 | -0.18019 | -0.18807 | 0.0002 | -0.11214 | 0.068048 | -0.033117 | -0.25885 | 122.3764 | 122.1944 | 122.3226 | 62.2298 | -122.4225 | 122.2088 | 122.3637 | 122.138 | 62.2883 | -122.577
360.2188 | 122.699 | -62.2147 | 60.1959 | 1.4211e-13 | -0.0080727 | -0.012436 | 0.016584 | -0.03637 | 0.031876 | 0.0067908 | -0.013231 | 0.011089 | 0.034923 | -0.0071495 | 0.039693 | -62.1872 | 0.015142 | -62.2501 | 60.1572 | 59.9843 | 60.1171 | -62.2357 | -62.2145 | 0.091933 | -62.3222 | 59.9987 | 60.1582 | 59.9371 | -62.3903 | -0.021034 | -0.038719 | 0.027466 | -0.035472 | -0.014438 | -0.21165 | -0.078843 | -0.17561 | -0.19723 | 0.000199 | -0.10757 | 0.068048 | -0.037694 | -0.25884 | 122.3719 | 122.1989 | 122.3317 | 62.2298 | -122.4316 | 122.2134 | 122.3729 | 122.1517 | 62.3066 | -122.5862
362.0156 | 122.6715 | -62.2513 | 60.173 | 1.4211e-13 | -0.0078589 | -0.012436 | 0.01637 | -0.03637 | 0.031235 | 0.0067908 | -0.013444 | 0.010875 | 0.03535 | -0.0073631 | 0.039693 | -62.1826 | 0.005985 | -62.2547 | 60.1664 | 59.9888 | 60.1033 | -62.2357 | -62.2099 | 0.087354 | -62.3176 | 60.0033 | 60.1582 | 59.9371 | -62.3949 | 0.015587 | -0.006675 | 0.068666 | -0.00343 | -0.019017 | -0.18419 | -0.06969 | -0.14357 | -0.16976 | 0.041399 | -0.066366 | 0.077205 | -0.014806 | -0.23596 | 122.4176 | 122.2401 | 122.3546 | 62.2573 | -122.4087 | 122.2546 | 122.4095 | 122.1884 | 62.3386 | -122.5679
363.75 | 122.7356 | -62.2147 | 60.2051 | 1.4211e-13 | -0.0078589 | -0.012436 | 0.016157 | -0.036156 | 0.031663 | -0.0084697 | -0.013658 | 0.010875 | 0.035136 | -0.0069357 | 0.039479 | -62.1872 | 0.019721 | -62.2364 | 60.1664 | 59.9843 | 60.1079 | -62.2449 | -62.2145 | 0.082776 | -62.3131 | 59.9941 | 60.1445 | 59.9279 | -62.3903 | -0.030192 | -0.038718 | 0.027466 | -0.021737 | 0.008455 | -0.22081 | -0.097155 | -0.17561 | -0.21096 | 0.000199 | -0.098408 | 0.077205 | -0.060585 | -0.27716 | 122.381 | 122.1989 | 122.3226 | 62.2344 | -122.4499 | 122.2088 | 122.3592 | 122.1426 | 62.2974 | -122.5954
365.5156 | 122.6715 | -62.2559 | 60.1868 | 1.4211e-13 | -0.0078589 | -0.012436 | 0.016584 | -0.03637 | 0.031449 | 0.022052 | -0.013444 | 0.010448 | 0.035136 | -0.0075769 | 0.039693 | -62.1826 | 0.015142 | -62.2456 | 60.1664 | 59.9843 | 60.1171 | -62.2449 | -62.2099 | 0.082776 | -62.3222 | 60.0033 | 60.1628 | 59.9417 | -62.3903 | 0.011006 | -0.020408 | 0.073243 | 0.010304 | -0.000702 | -0.2025 | -0.069688 | -0.13441 | -0.18349 | 0.045976 | -0.066367 | 0.068048 | -0.02396 | -0.24511 | 122.4222 | 122.2401 | 122.3729 | 62.271 | -122.4316 | 122.2591 | 122.4187 | 122.1975 | 62.3386 | -122.577
367.2969 | 122.6028 | -62.2375 | 60.2646 | 1.4211e-13 | -0.0078589 | -0.012436 | 0.01637 | -0.036583 | 0.031663 | 0.014421 | -0.013231 | 0.010234 | 0.034923 | -0.0073631 | 0.039906 | -62.1826 | 0.019721 | -62.2501 | 60.1664 | 59.9843 | 60.1079 | -62.2449 | -62.2145 | 0.082776 | -62.3176 | 59.9941 | 60.1537 | 59.9325 | -62.3903 | -0.007304 | -0.098227 | 0.054933 | -0.012584 | -0.00528 | -0.28032 | -0.15666 | -0.15272 | -0.27047 | 0.023087 | -0.080099 | 0.072626 | -0.11094 | -0.33209 | 122.4039 | 122.2218 | 122.3455 | 62.2573 | -122.5094 | 122.2317 | 122.3912 | 122.17 | 62.3203 | -122.6549
369.0781 | 122.5937 | -62.2513 | 60.2646 | 1.4211e-13 | -0.0076453 | -0.01265 | 0.01637 | -0.036156 | 0.031663 | -0.0084697 | -0.013444 | 0.010662 | 0.034923 | -0.0073631 | 0.039906 | -62.1918 | 0.015142 | -62.2456 | 60.1618 | 59.9843 | 60.1079 | -62.2357 | -62.2053 | 0.082776 | -62.3176 | 60.0033 | 60.1582 | 59.9371 | -62.3949 | 0.015587 | -0.1028 | 0.059509 | 0.005727 | -0.00986 | -0.28032 | -0.15666 | -0.14357 | -0.26131 | 0.045978 | -0.066366 | 0.077205 | -0.10636 | -0.32751 | 122.4131 | 122.2356 | 122.3592 | 62.2664 | -122.5003 | 122.2546 | 122.4095 | 122.1884 | 62.3341 | -122.6594
370.7969 | 122.7173 | -62.2238 | 60.1639 | 1.4211e-13 | -0.0078589 | -0.012863 | 0.016798 | -0.036156 | 0.031235 | -0.00083919 | -0.013658 | 0.010662 | 0.03535 | -0.0071495 | 0.039693 | -62.1872 | 0.019721 | -62.2501 | 60.1618 | 59.9888 | 60.1171 | -62.2311 | -62.2145 | 0.073618 | -62.3222 | 59.9895 | 60.1674 | 59.9279 | -62.3949 | -0.0073 | -0.002097 | 0.036621 | -0.026317 | -0.019017 | -0.17503 | -0.046799 | -0.17104 | -0.17434 | 0.009354 | -0.09841 | 0.072627 | 0.003507 | -0.23596 | 122.3856 | 122.2127 | 122.3409 | 62.2435 | -122.395 | 122.2134 | 122.3912 | 122.1517 | 62.2974 | -122.5587
372.5781 | 122.6028 | -62.233 | 60.26 | 1.4211e-13 | -0.0080727 | -0.012222 | 0.016584 | -0.036156 | 0.031663 | 0.0067908 | -0.013231 | 0.010662 | 0.034923 | -0.0069357 | 0.039693 | -62.178 | 0.015142 | -62.2456 | 60.1572 | 59.9888 | 60.0988 | -62.2403 | -62.2053 | 0.082776 | -62.3268 | 59.9941 | 60.1582 | 59.9371 | -62.3903 | -0.007303 | -0.10281 | 0.054933 | -0.012584 | -0.005281 | -0.27116 | -0.16124 | -0.1573 | -0.26589 | 0.027667 | -0.093834 | 0.063469 | -0.10178 | -0.32293 | 122.3902 | 122.2218 | 122.3317 | 62.2481 | -122.5003 | 122.2271 | 122.3912 | 122.1701 | 62.3157 | -122.6503
374.3594 | 122.7448 | -62.2147 | 60.2142 | 1.4211e-13 | -0.0080727 | -0.012222 | 0.016584 | -0.036156 | 0.031449 | 0.0067908 | -0.013444 | 0.010662 | 0.03535 | -0.0071495 | 0.039693 | -62.1826 | 0.019721 | -62.2501 | 60.1709 | 60.0072 | 60.1033 | -62.2357 | -62.2053 | 0.082776 | -62.3222 | 59.9941 | 60.1537 | 59.9325 | -62.3903 | -0.021034 | -0.043294 | 0.032045 | -0.035472 | -0.014438 | -0.20707 | -0.11089 | -0.17561 | -0.22011 | 0.009357 | -0.10757 | 0.068048 | -0.060582 | -0.28173 | 122.3856 | 122.2218 | 122.318 | 62.2344 | -122.4499 | 122.2088 | 122.3683 | 122.1472 | 62.2974 | -122.6045
376.0625 | 122.6715 | -62.2284 | 60.2554 | 1.4211e-13 | -0.0080727 | -0.01265 | 0.01637 | -0.03637 | 0.031663 | -0.00083919 | -0.013658 | 0.010662 | 0.035136 | -0.0071495 | 0.039906 | -62.1735 | 0.010564 | -62.2501 | 60.1572 | 59.9888 | 60.1079 | -62.2357 | -62.2145 | 0.091933 | -62.3131 | 59.9941 | 60.1582 | 59.9325 | -62.3857 | -0.007301 | -0.098228 | 0.054934 | -0.021739 | -0.014438 | -0.26658 | -0.14751 | -0.1573 | -0.26131 | 0.013932 | -0.084675 | 0.072627 | -0.097203 | -0.32293 | 122.3856 | 122.2172 | 122.3363 | 62.239 | -122.4911 | 122.2225 | 122.3866 | 122.1609 | 62.3203 | -122.6411
377.8438 | 122.6578 | -62.2559 | 60.2005 | 1.4211e-13 | -0.0076453 | -0.012222 | 0.016157 | -0.036156 | 0.031663 | -0.00083919 | -0.013444 | 0.010875 | 0.03535 | -0.0067221 | 0.039693 | -62.178 | 0.010564 | -62.2456 | 60.1664 | 59.9843 | 60.1079 | -62.2311 | -62.2099 | 0.078197 | -62.3176 | 59.9895 | 60.1537 | 59.9371 | -62.3903 | 0.024743 | -0.03414 | 0.077821 | 0.010304 | -0.014439 | -0.21623 | -0.092577 | -0.13441 | -0.21096 | 0.045976 | -0.061789 | 0.072626 | -0.046849 | -0.26342 | 122.4222 | 122.2401 | 122.3638 | 62.2664 | -122.4316 | 122.2454 | 122.4095 | 122.1929 | 62.3341 | -122.5908
379.5469 | 122.6257 | -62.2284 | 60.2554 | 1.4211e-13 | -0.0074317 | -0.012436 | 0.01637 | -0.036583 | 0.031022 | -0.00083919 | -0.013444 | 0.010234 | 0.035136 | -0.0069357 | 0.04012 | -62.1826 | 0.019721 | -62.241 | 60.1664 | 59.9843 | 60.1079 | -62.2311 | -62.2099 | 0.082776 | -62.3222 | 59.9941 | 60.1491 | 59.9279 | -62.3903 | -0.002722 | -0.089072 | 0.045778 | -0.012583 | -0.009861 | -0.27116 | -0.14751 | -0.16188 | -0.26131 | 0.018511 | -0.093832 | 0.068048 | -0.10636 | -0.32751 | 122.3948 | 122.2127 | 122.3363 | 62.2481 | -122.4865 | 122.2225 | 122.3775 | 122.1563 | 62.3112 | -122.6457
381.3125 | 122.7448 | -62.2375 | 60.1913 | 1.4211e-13 | -0.0076453 | -0.012222 | 0.01637 | -0.035942 | 0.031449 | -0.0161 | -0.013658 | 0.010448 | 0.03535 | -0.0071495 | 0.039693 | -62.1826 | 0.019721 | -62.2456 | 60.1664 | 59.9888 | 60.1079 | -62.2403 | -62.2053 | 0.082776 | -62.3176 | 59.9987 | 60.1628 | 59.9325 | -62.3949 | -0.002725 | -0.024985 | 0.054933 | -0.008006 | -0.005281 | -0.2025 | -0.083422 | -0.1573 | -0.19265 | 0.032245 | -0.080099 | 0.077205 | -0.028537 | -0.25885 | 122.4039 | 122.2264 | 122.3455 | 62.2573 | -122.4316 | 122.2362 | 122.4004 | 122.17 | 62.3203 | -122.5862
383.0312 | 122.7356 | -62.2238 | 60.1776 | 1.4211e-13 | -0.0074317 | -0.01265 | 0.01637 | -0.036156 | 0.031449 | 0.014421 | -0.013444 | 0.010448 | 0.035564 | -0.0073631 | 0.039693 | -62.1735 | 0.010564 | -62.2456 | 60.1664 | 59.9934 | 60.1079 | -62.2403 | -62.2099 | 0.091933 | -62.3131 | 59.9987 | 60.1445 | 59.9325 | -62.3903 | -0.016458 | -0.011252 | 0.050356 | -0.021739 | -0.005281 | -0.18418 | -0.069689 | -0.16646 | -0.17892 | 0.013933 | -0.089253 | 0.077205 | -0.033119 | -0.24511 | 122.3902 | 122.2172 | 122.3317 | 62.2344 | -122.4179 | 122.2225 | 122.3683 | 122.1563 | 62.3157 | -122.5679
384.8125 | 122.6074 | -62.2238 | 60.2234 | 1.4211e-13 | -0.0076453 | -0.01265 | 0.016584 | -0.03637 | 0.031235 | 0.0067908 | -0.013231 | 0.010662 | 0.034923 | -0.0071495 | 0.039693 | -62.1735 | 0.015142 | -62.241 | 60.1572 | 59.9797 | 60.1079 | -62.2265 | -62.2099 | 0.087354 | -62.3176 | 59.9987 | 60.1491 | 59.9325 | -62.3903 | -0.002721 | -0.066185 | 0.050356 | -0.017161 | -0.01444 | -0.2437 | -0.11547 | -0.16646 | -0.22469 | 0.013933 | -0.093832 | 0.072626 | -0.074317 | -0.29089 | 122.381 | 122.2035 | 122.3317 | 62.239 | -122.4499 | 122.2225 | 122.3729 | 122.1563 | 62.3112 | -122.6137
386.5156 | 122.6532 | -62.2421 | 60.2371 | 1.4211e-13 | -0.0076453 | -0.012222 | 0.016157 | -0.036156 | 0.031449 | -0.00083919 | -0.013444 | 0.010448 | 0.034923 | -0.0069357 | 0.039693 | -62.178 | 0.015142 | -62.2501 | 60.1618 | 59.9888 | 60.1079 | -62.2265 | -62.2099 | 0.082776 | -62.3176 | 59.9987 | 60.1491 | 59.9325 | -62.3903 | 0.015589 | -0.07534 | 0.064088 | -0.008007 | -0.023596 | -0.24827 | -0.1292 | -0.14815 | -0.23843 | 0.032243 | -0.075522 | 0.072626 | -0.08805 | -0.30462 | 122.4039 | 122.231 | 122.35 | 62.2573 | -122.4637 | 122.2408 | 122.3912 | 122.1746 | 62.3249 | -122.6274
388.2969 | 122.5754 | -62.2604 | 60.2417 | 1.4211e-13 | -0.0076453 | -0.012222 | 0.016584 | -0.03637 | 0.031449 | -0.00083919 | -0.013658 | 0.010662 | 0.035136 | -0.0071495 | 0.039906 | -62.178 | 0.015142 | -62.2456 | 60.1618 | 59.9843 | 60.1171 | -62.2311 | -62.2007 | 0.082776 | -62.3131 | 59.9987 | 60.1491 | 59.9371 | -62.3949 | 0.029321 | -0.079917 | 0.082399 | 0.014882 | -0.014439 | -0.25743 | -0.12462 | -0.13442 | -0.243 | 0.059711 | -0.052632 | 0.081784 | -0.092627 | -0.30462 | 122.4222 | 122.2447 | 122.3775 | 62.2756 | -122.4728 | 122.2591 | 122.4095 | 122.1975 | 62.3432 | -122.6366
390.0625 | 122.5983 | -62.2513 | 60.2463 | 1.4211e-13 | -0.0076453 | -0.012436 | 0.01637 | -0.036156 | 0.031235 | -0.0084697 | -0.013444 | 0.010662 | 0.03535 | -0.0067221 | 0.039693 | -62.178 | 0.019721 | -62.2364 | 60.1664 | 60.0163 | 60.1125 | -62.2357 | -62.2053 | 0.087354 | -62.3176 | 60.0033 | 60.1582 | 59.9325 | -62.3903 | 0.015587 | -0.079917 | 0.073244 | 0.014884 | -0.000703 | -0.22995 | -0.13377 | -0.13899 | -0.243 | 0.045978 | -0.066366 | 0.072626 | -0.088048 | -0.31378 | 122.4176 | 122.2676 | 122.3638 | 62.271 | -122.482 | 122.2546 | 122.4095 | 122.1838 | 62.3386 | -122.6366
391.8438 | 122.6486 | -62.2238 | 60.2371 | 1.4211e-13 | -0.0076453 | -0.012222 | 0.01637 | -0.036156 | 0.031449 | 0.0067908 | -0.013444 | 0.010662 | 0.034923 | -0.0071495 | 0.039693 | -62.1826 | 0.010564 | -62.241 | 60.1664 | 60.0072 | 60.1171 | -62.2311 | -62.2053 | 0.082776 | -62.3085 | 59.9941 | 60.1445 | 59.9371 | -62.3857 | -0.0073 | -0.070762 | 0.0412 | -0.017161 | -0.009861 | -0.22996 | -0.12004 | -0.16188 | -0.243 | 0.018512 | -0.084674 | 0.077206 | -0.092629 | -0.30004 | 122.3902 | 122.231 | 122.3409 | 62.2344 | -122.4682 | 122.2179 | 122.3683 | 122.1609 | 62.3066 | -122.6228
393.6406 | 122.7219 | -62.2101 | 60.1547 | 1.4211e-13 | -0.0078589 | -0.012222 | 0.01637 | -0.036156 | 0.031449 | -0.00083919 | -0.013444 | 0.010448 | 0.035564 | -0.0069357 | 0.039479 | -62.178 | 0.019721 | -62.2364 | 60.1664 | 59.9888 | 60.1033 | -62.2311 | -62.1961 | 0.087354 | -62.3176 | 59.9941 | 60.1537 | 59.9279 | -62.3949 | -0.021033 | 0.011636 | 0.032045 | -0.026315 | -0.005282 | -0.16587 | -0.051379 | -0.18477 | -0.16061 | 0.013936 | -0.10757 | 0.077205 | -0.001073 | -0.2268 | 122.3764 | 122.1989 | 122.3134 | 62.2298 | -122.3858 | 122.2042 | 122.3637 | 122.138 | 62.2974 | -122.5496
395.3594 | 122.7127 | -62.233 | 60.2097 | 1.4211e-13 | -0.0078589 | -0.012009 | 0.016157 | -0.036156 | 0.031235 | -0.00083919 | -0.013444 | 0.010875 | 0.034709 | -0.0073631 | 0.039906 | -62.1735 | 0.015142 | -62.2364 | 60.1618 | 59.9934 | 60.1079 | -62.2357 | -62.2099 | 0.078197 | -62.3131 | 59.9895 | 60.1491 | 59.9279 | -62.3903 | -0.002724 | -0.047874 | 0.059511 | -0.003427 | -0.000703 | -0.21623 | -0.10173 | -0.1573 | -0.22012 | 0.023088 | -0.080098 | 0.077205 | -0.060584 | -0.28173 | 122.3948 | 122.2264 | 122.3409 | 62.2481 | -122.4454 | 122.2225 | 122.382 | 122.1609 | 62.3112 | -122.5999
397.1406 | 122.7539 | -62.2192 | 60.173 | 1.4211e-13 | -0.0076453 | -0.012009 | 0.016584 | -0.036156 | 0.031663 | 0.0067908 | -0.013231 | 0.010234 | 0.035136 | -0.0069357 | 0.039693 | -62.1689 | 0.015142 | -62.2364 | 60.1664 | 59.9797 | 60.1079 | -62.2357 | -62.2007 | 0.087354 | -62.3176 | 59.9895 | 60.1537 | 59.9233 | -62.3903 | -0.016457 | -0.006675 | 0.050357 | -0.01716 | -0.000703 | -0.19334 | -0.065112 | -0.17104 | -0.1835 | 0.018512 | -0.09841 | 0.072626 | -0.019384 | -0.24969 | 122.3856 | 122.1989 | 122.3272 | 62.2344 | -122.4087 | 122.2088 | 122.3729 | 122.1426 | 62.3066 | -122.5633
398.875 | 122.6349 | -62.2055 | 60.228 | 1.4211e-13 | -0.0080727 | -0.012436 | 0.016584 | -0.036156 | 0.031876 | 0.0067908 | -0.013658 | 0.010662 | 0.03535 | -0.0071495 | 0.039265 | -62.1689 | 0.015142 | -62.241 | 60.1572 | 60.0163 | 60.1171 | -62.2311 | -62.2007 | 0.087354 | -62.3131 | 59.9895 | 60.1582 | 59.9325 | -62.3903 | -0.025611 | -0.070762 | 0.036624 | -0.035472 | -0.009861 | -0.21164 | -0.11089 | -0.18477 | -0.23843 | 0.004779 | -0.10756 | 0.077205 | -0.069737 | -0.29547 | 122.3627 | 122.2218 | 122.3226 | 62.2206 | -122.4591 | 122.195 | 122.3637 | 122.138 | 62.2929 | -122.6182
400.6406 | 122.6532 | -62.2467 | 60.2234 | 1.4211e-13 | -0.0074317 | -0.012222 | 0.016584 | -0.03637 | 0.031449 | 0.0067908 | -0.013658 | 0.010875 | 0.034923 | -0.0071495 | 0.039906 | -62.1735 | 0.005985 | -62.2364 | 60.1618 | 59.9934 | 60.1125 | -62.2311 | -62.2053 | 0.078197 | -62.3131 | 59.9941 | 60.1537 | 59.9279 | -62.3857 | 0.015588 | -0.061607 | 0.073244 | 0.010306 | -0.005282 | -0.22996 | -0.11089 | -0.13899 | -0.22927 | 0.0414 | -0.066365 | 0.072627 | -0.069738 | -0.29547 | 122.4085 | 122.2401 | 122.3592 | 62.2527 | -122.4545 | 122.2408 | 122.4004 | 122.1746 | 62.3249 | -122.6091
402.4219 | 122.6303 | -62.2742 | 60.173 | 1.4211e-13 | -0.0074317 | -0.01265 | 0.01637 | -0.03637 | 0.031449 | -0.00083919 | -0.013231 | 0.010448 | 0.035136 | -0.0067221 | 0.039693 | -62.1735 | 0.005985 | -62.2364 | 60.1664 | 60.0621 | 60.1125 | -62.2403 | -62.2053 | 0.082776 | -62.3176 | 59.9895 | 60.1445 | 59.9646 | -62.3857 | 0.033896 | -0.006675 | 0.10071 | 0.037772 | 0.003876 | -0.11092 | -0.060533 | -0.11153 | -0.1835 | 0.068866 | -0.043478 | 0.068048 | -0.028542 | -0.20848 | 122.4405 | 122.3363 | 122.3867 | 62.2802 | -122.4133 | 122.2637 | 122.4187 | 122.2387 | 62.3569 | -122.5587
404.2031 | 122.6303 | -62.2421 | 60.2188 | 1.4211e-13 | -0.0076453 | -0.012222 | 0.016584 | -0.03637 | 0.031235 | -0.00083919 | -0.013231 | 0.010875 | 0.034923 | -0.0067221 | 0.04012 | -62.1689 | 0.015142 | -62.241 | 60.1664 | 60.0301 | 60.1079 | -62.2357 | -62.1961 | 0.096512 | -62.3085 | 59.9895 | 60.1537 | 59.9371 | -62.3994 | 0.006431 | -0.052451 | 0.073245 | 0.001149 | -0.005282 | -0.18875 | -0.11089 | -0.15731 | -0.22927 | 0.045979 | -0.066364 | 0.090942 | -0.06516 | -0.28173 | 122.4085 | 122.2722 | 122.35 | 62.2573 | -122.4545 | 122.2317 | 122.3958 | 122.1792 | 62.3386 | -122.6182
405.9688 | 122.6257 | -62.2421 | 60.2463 | 1.4211e-13 | -0.0078589 | -0.01265 | 0.016584 | -0.03637 | 0.031235 | -0.00083919 | -0.013231 | 0.010662 | 0.034923 | -0.0067221 | 0.039906 | -62.178 | 0.010564 | -62.241 | 60.1572 | 59.9843 | 60.1079 | -62.2403 | -62.2053 | 0.078197 | -62.3085 | 59.9895 | 60.1491 | 59.9233 | -62.3811 | 0.001852 | -0.089073 | 0.064088 | 0.001149 | -0.000703 | -0.26201 | -0.13835 | -0.13899 | -0.25674 | 0.036822 | -0.066364 | 0.072627 | -0.097205 | -0.32293 | 122.3993 | 122.2264 | 122.35 | 62.2527 | -122.4866 | 122.2317 | 122.3912 | 122.1655 | 62.3203 | -122.6274
407.7031 | 122.5983 | -62.2421 | 60.2417 | 1.4211e-13 | -0.0074317 | -0.012222 | 0.016584 | -0.03637 | 0.031449 | -0.00083919 | -0.013444 | 0.010448 | 0.03535 | -0.0071495 | 0.039906 | -62.1735 | 0.015142 | -62.2456 | 60.1572 | 60.085 | 60.1079 | -62.2403 | -62.1961 | 0.087354 | -62.3131 | 59.9941 | 60.1537 | 59.9783 | -62.3903 | 0.001852 | -0.084495 | 0.068666 | -0.003429 | -0.005281 | -0.15669 | -0.13378 | -0.14815 | -0.24758 | 0.045979 | -0.070943 | 0.077205 | -0.088048 | -0.26341 | 122.3993 | 122.3271 | 122.35 | 62.2573 | -122.482 | 122.2362 | 122.3958 | 122.2204 | 62.3295 | -122.632
409.4688 | 122.6395 | -62.2238 | 60.2463 | 1.4211e-13 | -0.0078589 | -0.01265 | 0.016157 | -0.03637 | 0.031663 | -0.00083919 | -0.013444 | 0.010662 | 0.03535 | -0.0071495 | 0.040334 | -62.1689 | 0.015142 | -62.2364 | 60.1664 | 60.0255 | 60.1079 | -62.2357 | -62.2007 | 0.078197 | -62.3131 | 59.9941 | 60.1537 | 59.9279 | -62.3903 | -0.011879 | -0.079917 | 0.054935 | -0.012582 | -0.000703 | -0.2208 | -0.13835 | -0.16646 | -0.25216 | 0.02309 | -0.089253 | 0.077205 | -0.092626 | -0.31835 | 122.3902 | 122.2493 | 122.3317 | 62.239 | -122.482 | 122.2179 | 122.3775 | 122.1517 | 62.302 | -122.6366
411.2344 | 122.6578 | -62.2101 | 60.2325 | 1.4211e-13 | -0.0078589 | -0.012436 | 0.016584 | -0.036156 | 0.031235 | 0.0067908 | -0.013231 | 0.010448 | 0.034923 | -0.0067221 | 0.039479 | -62.178 | 0.019721 | -62.2364 | 60.1572 | 59.998 | 60.1125 | -62.2311 | -62.1961 | 0.078197 | -62.3085 | 59.9895 | 60.1491 | 59.9279 | -62.3857 | -0.021033 | -0.07534 | 0.032045 | -0.026315 | -0.005282 | -0.23454 | -0.12004 | -0.17561 | -0.243 | 0.013936 | -0.098407 | 0.077206 | -0.083472 | -0.30462 | 122.3673 | 122.2081 | 122.3226 | 62.2298 | -122.4637 | 122.1996 | 122.3592 | 122.138 | 62.2883 | -122.6182
413.0312 | 122.5754 | -62.2696 | 60.228 | 1.4211e-13 | -0.0076453 | -0.012222 | 0.016584 | -0.036156 | 0.031449 | -0.00083919 | -0.013444 | 0.010662 | 0.03535 | -0.0069357 | 0.039693 | -62.1735 | 0.015142 | -62.2364 | 60.1618 | 60.0255 | 60.1079 | -62.2403 | -62.1961 | 0.082776 | -62.3085 | 59.9941 | 60.1491 | 59.9371 | -62.3949 | 0.029318 | -0.066184 | 0.096132 | 0.033194 | 0.003876 | -0.20249 | -0.12004 | -0.12526 | -0.23385 | 0.073445 | -0.038898 | 0.086363 | -0.078894 | -0.29089 | 122.4314 | 122.2951 | 122.3775 | 62.2847 | -122.4682 | 122.2637 | 122.4187 | 122.2067 | 62.3524 | -122.6228
414.75 | 122.6669 | -62.2375 | 60.228 | 1.4211e-13 | -0.0078589 | -0.012436 | 0.01637 | -0.036156 | 0.031235 | -0.00083919 | -0.013231 | 0.010662 | 0.034923 | -0.0067221 | 0.039479 | -62.1735 | 0.019721 | -62.241 | 60.1572 | 60.0026 | 60.1171 | -62.2357 | -62.2007 | 0.091933 | -62.3131 | 59.9987 | 60.1491 | 59.9233 | -62.3857 | 0.001854 | -0.070762 | 0.064089 | -0.003428 | -0.005282 | -0.22538 | -0.11089 | -0.14815 | -0.22927 | 0.036823 | -0.07552 | 0.072627 | -0.078894 | -0.30462 | 122.3948 | 122.2401 | 122.3546 | 62.2573 | -122.4637 | 122.2362 | 122.3866 | 122.1609 | 62.3295 | -122.6137
416.5156 | 122.7081 | -62.2009 | 60.2097 | 1.4211e-13 | -0.0076453 | -0.012009 | 0.016584 | -0.036156 | 0.031235 | -0.0084697 | -0.013658 | 0.010448 | 0.034923 | -0.0069357 | 0.039693 | -62.1689 | 0.019721 | -62.2364 | 60.1572 | 59.998 | 60.1033 | -62.2265 | -62.2053 | 0.082776 | -62.3131 | 59.9895 | 60.1582 | 59.9279 | -62.3903 | -0.025609 | -0.052452 | 0.032047 | -0.03547 | -0.009861 | -0.21165 | -0.10631 | -0.18935 | -0.22012 | -0.004376 | -0.11214 | 0.077205 | -0.051427 | -0.28173 | 122.3581 | 122.1989 | 122.3043 | 62.2206 | -122.4362 | 122.1905 | 122.3592 | 122.1288 | 62.2837 | -122.5999
418.3125 | 122.5891 | -62.2238 | 60.2737 | 1.4211e-13 | -0.0078589 | -0.012222 | 0.01637 | -0.03637 | 0.031022 | -0.00083919 | -0.013231 | 0.010662 | 0.035136 | -0.0067221 | 0.039479 | -62.1643 | 0.015142 | -62.2364 | 60.1572 | 60.0072 | 60.1079 | -62.222 | -62.2007 | 0.091933 | -62.3131 | 59.985 | 60.1537 | 59.9233 | -62.3857 | 0.001858 | -0.11654 | 0.059513 | -0.012582 | -0.01444 | -0.26658 | -0.16582 | -0.16188 | -0.28878 | 0.02309 | -0.089253 | 0.072627 | -0.12009 | -0.3504 | 122.381 | 122.231 | 122.3317 | 62.239 | -122.4957 | 122.2088 | 122.3775 | 122.1472 | 62.3157 | -122.6594
420.0312 | 122.6074 | -62.2192 | 60.26 | 1.4211e-13 | -0.0076453 | -0.012222 | 0.01637 | -0.036156 | 0.031235 | -0.0084697 | -0.013658 | 0.010448 | 0.035136 | -0.0069357 | 0.039479 | -62.1735 | 0.015142 | -62.2364 | 60.1526 | 60.0209 | 60.1079 | -62.2357 | -62.1961 | 0.078197 | -62.3131 | 59.9895 | 60.1537 | 59.9233 | -62.3811 | -0.016457 | -0.10739 | 0.045778 | -0.01716 | -0.000703 | -0.23911 | -0.15209 | -0.16188 | -0.27047 | 0.023091 | -0.093831 | 0.068048 | -0.10636 | -0.33667 | 122.3719 | 122.2401 | 122.3272 | 62.2344 | -122.4957 | 122.2088 | 122.3729 | 122.1426 | 62.2974 | -122.6411
421.8281 | 122.7036 | -62.2238 | 60.1456 | 1.4211e-13 | -0.0076453 | -0.012222 | 0.01637 | -0.03637 | 0.031449 | -0.0084697 | -0.013872 | 0.010448 | 0.035136 | -0.0067221 | 0.039906 | -62.1735 | 0.005985 | -62.2364 | 60.1526 | 59.9934 | 60.1079 | -62.2311 | -62.2053 | 0.082776 | -62.3085 | 59.9941 | 60.1445 | 59.9371 | -62.3811 | -0.0073 | 0.007056 | 0.050356 | -0.012582 | -0.005282 | -0.15214 | -0.037646 | -0.1573 | -0.15145 | 0.018512 | -0.084674 | 0.072627 | -0.001076 | -0.20849 | 122.3764 | 122.2172 | 122.3317 | 62.2298 | -122.3767 | 122.2179 | 122.3683 | 122.1609 | 62.3066 | -122.5267
423.5938 | 122.6669 | -62.233 | 60.2325 | 1.4211e-13 | -0.0080727 | -0.012009 | 0.01637 | -0.036156 | 0.031235 | -0.00083919 | -0.013444 | 0.010662 | 0.035136 | -0.0067221 | 0.039265 | -62.1735 | 0.015142 | -62.2318 | 60.1526 | 59.998 | 60.1033 | -62.2311 | -62.2007 | 0.078197 | -62.3085 | 59.9941 | 60.1399 | 59.9325 | -62.3903 | 0.001855 | -0.079919 | 0.059511 | 0.001151 | -0.000704 | -0.23454 | -0.1292 | -0.1573 | -0.23843 | 0.032245 | -0.075519 | 0.081784 | -0.092629 | -0.30004 | 122.3856 | 122.231 | 122.3363 | 62.2481 | -122.4637 | 122.2271 | 122.3729 | 122.1655 | 62.3112 | -122.6228
425.375 | 122.612 | -62.2284 | 60.2509 | 1.4211e-13 | -0.0076453 | -0.012009 | 0.01637 | -0.036156 | 0.031235 | 0.014421 | -0.013872 | 0.010448 | 0.03535 | -0.0069357 | 0.039693 | -62.178 | 0.010564 | -62.2364 | 60.1618 | 60.0117 | 60.1033 | -62.2311 | -62.1961 | 0.082776 | -62.3131 | 59.9941 | 60.1445 | 59.9233 | -62.3903 | -0.002722 | -0.089072 | 0.050356 | -0.008004 | -0.005282 | -0.23911 | -0.14751 | -0.16188 | -0.25674 | 0.032247 | -0.084675 | 0.077205 | -0.10636 | -0.32751 | 122.3902 | 122.2401 | 122.3317 | 62.239 | -122.482 | 122.2225 | 122.3729 | 122.1517 | 62.3112 | -122.6411
427.0938 | 122.7264 | -62.2101 | 60.1822 | 1.4211e-13 | -0.0076453 | -0.012222 | 0.016584 | -0.03637 | 0.031449 | -0.00083919 | -0.013444 | 0.010662 | 0.035564 | -0.0067221 | 0.039906 | -62.1689 | 0.019721 | -62.2318 | 60.1572 | 60.0667 | 60.1171 | -62.2311 | -62.1961 | 0.082776 | -62.3085 | 59.9941 | 60.1445 | 59.9233 | -62.3903 | -0.021033 | -0.024986 | 0.041202 | -0.021737 | -0.000704 | -0.1155 | -0.06511 | -0.18019 | -0.18807 | 0.013936 | -0.098407 | 0.081784 | -0.037697 | -0.25885 | 122.3673 | 122.2768 | 122.3272 | 62.2298 | -122.4133 | 122.2042 | 122.3546 | 122.1334 | 62.2929 | -122.5725
428.875 | 122.5845 | -62.2513 | 60.2417 | 1.4211e-13 | -0.0076453 | -0.012222 | 0.016798 | -0.03637 | 0.031235 | 0.0067908 | -0.013872 | 0.010875 | 0.03535 | -0.0065085 | 0.039693 | -62.1735 | 0.015142 | -62.2318 | 60.1572 | 60.0255 | 60.1125 | -62.222 | -62.1961 | 0.078197 | -62.3039 | 59.9895 | 60.1491 | 59.9371 | -62.3857 | 0.029324 | -0.084495 | 0.077822 | 0.019462 | -0.009862 | -0.21622 | -0.1292 | -0.13441 | -0.25216 | 0.055135 | -0.05263 | 0.081784 | -0.092627 | -0.30462 | 122.4085 | 122.2768 | 122.3638 | 62.2664 | -122.4637 | 122.2408 | 122.4004 | 122.1884 | 62.3295 | -122.6274
430.6406 | 122.731 | -62.233 | 60.1593 | 1.4211e-13 | -0.0076453 | -0.012222 | 0.01637 | -0.036583 | 0.031449 | -0.00083919 | -0.013872 | 0.010234 | 0.03535 | -0.0067221 | 0.039693 | -62.1689 | 0.015142 | -62.2364 | 60.1526 | 60.0209 | 60.1125 | -62.2265 | -62.2007 | 0.082776 | -62.3039 | 59.9895 | 60.1537 | 59.9371 | -62.3903 | 0.006434 | -0.006677 | 0.06409 | -0.003427 | -0.009861 | -0.1384 | -0.0468 | -0.1573 | -0.16976 | 0.032245 | -0.070941 | 0.086362 | -0.005651 | -0.22222 | 122.3856 | 122.2539 | 122.3455 | 62.2481 | -122.3858 | 122.2225 | 122.3866 | 122.1701 | 62.3157 | -122.5496
432.3438 | 122.731 | -62.1964 | 60.1776 | 1.4211e-13 | -0.0074317 | -0.012436 | 0.016157 | -0.03637 | 0.031663 | 0.0067908 | -0.013231 | 0.010662 | 0.03535 | -0.0069357 | 0.039265 | -62.1689 | 0.015142 | -62.2318 | 60.1572 | 60.0484 | 60.1125 | -62.2311 | -62.1961 | 0.087354 | -62.3131 | 59.9895 | 60.1582 | 59.9508 | -62.3857 | -0.034766 | -0.020408 | 0.027469 | -0.03547 | -0.000704 | -0.12924 | -0.06511 | -0.18935 | -0.18807 | 0.000203 | -0.11672 | 0.072627 | -0.019383 | -0.2268 | 122.3536 | 122.2447 | 122.3089 | 62.2115 | -122.4087 | 122.1859 | 122.3546 | 122.1472 | 62.2837 | -122.5633
434.1406 | 122.644 | -62.2101 | 60.2234 | 1.4211e-13 | -0.0076453 | -0.012009 | 0.016584 | -0.03637 | 0.031235 | 0.0067908 | -0.013658 | 0.010875 | 0.035136 | -0.0067221 | 0.039479 | -62.1735 | 0.0243 | -62.2318 | 60.1572 | 60.0667 | 60.1125 | -62.2403 | -62.2007 | 0.078197 | -62.3039 | 59.9895 | 60.1537 | 59.96 | -62.3857 | -0.030191 | -0.066185 | 0.036623 | -0.021737 | 0.008454 | -0.1567 | -0.11089 | -0.17561 | -0.23385 | 0.009357 | -0.093829 | 0.081784 | -0.069738 | -0.26342 | 122.3673 | 122.2768 | 122.3226 | 62.2344 | -122.4637 | 122.1996 | 122.3637 | 122.1701 | 62.2883 | -122.6091
435.8594 | 122.58 | -62.2559 | 60.26 | 1.4211e-13 | -0.0076453 | -0.012009 | 0.016157 | -0.036583 | 0.031663 | -0.00083919 | -0.013872 | 0.010662 | 0.034923 | -0.0067221 | 0.039693 | -62.1643 | 0.015142 | -62.2364 | 60.1572 | 60.0392 | 60.1079 | -62.2265 | -62.1916 | 0.087354 | -62.3085 | 59.9895 | 60.1537 | 59.9279 | -62.3857 | 0.029322 | -0.10281 | 0.091556 | 0.019461 | -0.009861 | -0.22079 | -0.15209 | -0.12984 | -0.27047 | 0.064291 | -0.052631 | 0.077206 | -0.10636 | -0.33209 | 122.4131 | 122.2951 | 122.3638 | 62.271 | -122.4865 | 122.2454 | 122.4095 | 122.1838 | 62.3432 | -122.6457
437.6406 | 122.7081 | -62.2055 | 60.1547 | 1.4211e-13 | -0.0076453 | -0.012222 | 0.016584 | -0.03637 | 0.031235 | -0.00083919 | -0.013444 | 0.010662 | 0.035136 | -0.0067221 | 0.039479 | -62.1643 | 0.015142 | -62.2364 | 60.1572 | 60.0209 | 60.1079 | -62.2265 | -62.2053 | 0.082776 | -62.3039 | 59.985 | 60.1491 | 59.9554 | -62.3903 | -0.021032 | 0.00248 | 0.041202 | -0.030893 | -0.009861 | -0.13382 | -0.046801 | -0.18477 | -0.16976 | 0.000201 | -0.098407 | 0.086362 | -0.005652 | -0.19933 | 122.3627 | 122.2264 | 122.3134 | 62.2206 | -122.3813 | 122.1905 | 122.3546 | 122.1609 | 62.2883 | -122.545
439.3594 | 122.6395 | -62.2192 | 60.2371 | 1.4211e-13 | -0.0078589 | -0.012436 | 0.016584 | -0.036583 | 0.031235 | 0.0067908 | -0.013872 | 0.010662 | 0.034923 | -0.0067221 | 0.039479 | -62.1643 | 0.010564 | -62.2364 | 60.148 | 60.0026 | 60.1079 | -62.2265 | -62.2007 | 0.078197 | -62.3039 | 59.9987 | 60.1537 | 59.9325 | -62.3903 | -0.007299 | -0.089075 | 0.054935 | -0.01716 | -0.009861 | -0.23454 | -0.1292 | -0.17104 | -0.23843 | 0.018512 | -0.084674 | 0.086362 | -0.083471 | -0.30462 | 122.3673 | 122.2218 | 122.3272 | 62.2298 | -122.4637 | 122.2179 | 122.3729 | 122.1517 | 62.2974 | -122.6274
441.1406 | 122.6852 | -62.2192 | 60.173 | 1.4211e-13 | -0.0076453 | -0.012222 | 0.01637 | -0.036156 | 0.031022 | -0.00083919 | -0.013658 | 0.010662 | 0.03535 | -0.0067221 | 0.039693 | -62.1689 | 0.0243 | -62.2318 | 60.1526 | 60.0484 | 60.1079 | -62.2311 | -62.2053 | 0.082776 | -62.2993 | 59.985 | 60.1537 | 59.9188 | -62.3857 | -0.011878 | -0.02041 | 0.050357 | -0.012582 | -0.000704 | -0.12466 | -0.065112 | -0.16646 | -0.18807 | 0.013934 | -0.080095 | 0.086363 | -0.019384 | -0.25427 | 122.3719 | 122.2676 | 122.3272 | 62.2435 | -122.4042 | 122.2042 | 122.3729 | 122.138 | 62.302 | -122.5587
442.9219 | 122.5754 | -62.2696 | 60.2188 | 1.4211e-13 | -0.0074317 | -0.012222 | 0.01637 | -0.03637 | 0.031449 | -0.00083919 | -0.013658 | 0.010234 | 0.035136 | -0.0067221 | 0.039479 | -62.1689 | 0.015142 | -62.2364 | 60.1526 | 60.0484 | 60.1033 | -62.2311 | -62.1961 | 0.082776 | -62.3131 | 59.9895 | 60.1491 | 59.9188 | -62.3857 | 0.038476 | -0.066186 | 0.10071 | 0.033194 | -0.005282 | -0.17044 | -0.11547 | -0.1161 | -0.22927 | 0.073445 | -0.043477 | 0.072627 | -0.069739 | -0.30005 | 122.4222 | 122.318 | 122.3729 | 62.2847 | -122.4499 | 122.2591 | 122.4187 | 122.1884 | 62.3524 | -122.6045
444.7031 | 122.5983 | -62.2467 | 60.2097 | 1.4211e-13 | -0.0078589 | -0.012222 | 0.01637 | -0.03637 | 0.031022 | -0.0084697 | -0.013444 | 0.010448 | 0.035136 | -0.0069357 | 0.039479 | -62.1597 | 0.015142 | -62.2364 | 60.1572 | 60.053 | 60.1033 | -62.2265 | -62.2007 | 0.087354 | -62.3131 | 59.985 | 60.1491 | 59.9142 | -62.3811 | 0.020167 | -0.052452 | 0.08698 | 0.010306 | -0.009861 | -0.1567 | -0.10631 | -0.13441 | -0.2247 | 0.045978 | -0.066365 | 0.068048 | -0.060584 | -0.29547 | 122.4039 | 122.2997 | 122.35 | 62.2618 | -122.4362 | 122.2317 | 122.3958 | 122.1609 | 62.3341 | -122.5908
446.4062 | 122.6303 | -62.2009 | 60.2234 | 1.4211e-13 | -0.0074317 | -0.012009 | 0.016157 | -0.036797 | 0.031235 | -0.00083919 | -0.013444 | 0.010662 | 0.035136 | -0.0067221 | 0.039693 | -62.1689 | 0.019721 | -62.2318 | 60.1572 | 60.0896 | 60.1033 | -62.2357 | -62.2007 | 0.082776 | -62.3131 | 59.985 | 60.1582 | 59.9233 | -62.3857 | -0.034767 | -0.066185 | 0.032047 | -0.030892 | 0.003875 | -0.1338 | -0.12004 | -0.18477 | -0.23843 | 0.000202 | -0.11214 | 0.072627 | -0.06516 | -0.30005 | 122.3581 | 122.2905 | 122.3043 | 62.2206 | -122.4591 | 122.1859 | 122.3592 | 122.1243 | 62.2837 | -122.6091
448.1719 | 122.5983 | -62.2375 | 60.1959 | 1.4211e-13 | -0.0076453 | -0.012863 | 0.015943 | -0.03637 | 0.031235 | 0.0067908 | -0.013658 | 0.010875 | 0.034923 | -0.0065085 | 0.039693 | -62.1689 | 0.010564 | -62.2272 | 60.148 | 60.053 | 60.1079 | -62.2311 | -62.1961 | 0.087354 | -62.3085 | 59.985 | 60.1537 | 59.9325 | -62.3811 | 0.006433 | -0.047876 | 0.068668 | 0.010307 | 0.003874 | -0.14297 | -0.088 | -0.14357 | -0.21096 | 0.041402 | -0.070941 | 0.072627 | -0.042272 | -0.26342 | 122.3856 | 122.2905 | 122.3455 | 62.2481 | -122.427 | 122.2225 | 122.3912 | 122.17 | 62.3249 | -122.577
449.9375 | 122.6303 | -62.2101 | 60.2188 | 1.4211e-13 | -0.0078589 | -0.012009 | 0.01637 | -0.03637 | 0.031235 | 0.014421 | -0.013658 | 0.010662 | 0.035136 | -0.0067221 | 0.039906 | -62.1689 | 0.015142 | -62.241 | 60.1572 | 60.053 | 60.1125 | -62.2357 | -62.2007 | 0.078197 | -62.3039 | 59.9941 | 60.1537 | 59.9508 | -62.3857 | -0.025612 | -0.061607 | 0.041202 | -0.030894 | -0.005282 | -0.16586 | -0.10631 | -0.17561 | -0.22469 | 0.009357 | -0.093829 | 0.081784 | -0.06516 | -0.268 | 122.3673 | 122.263 | 122.3226 | 62.2252 | -122.4545 | 122.2042 | 122.3637 | 122.1609 | 62.2883 | -122.6045
451.6562 | 122.6257 | -62.2147 | 60.228 | 1.4211e-13 | -0.0076453 | -0.012222 | 0.015943 | -0.036583 | 0.031449 | -0.00083919 | -0.013658 | 0.010448 | 0.034709 | -0.0062947 | 0.039479 | -62.1689 | 0.0243 | -62.2364 | 60.1572 | 60.0758 | 60.1079 | -62.2265 | -62.1961 | 0.082776 | -62.3039 | 59.9804 | 60.1491 | 59.9325 | -62.3811 | -0.011876 | -0.070762 | 0.04578 | -0.021737 | -0.009861 | -0.15212 | -0.12004 | -0.16646 | -0.24758 | 0.018514 | -0.089251 | 0.077205 | -0.078894 | -0.29547 | 122.3719 | 122.2905 | 122.3226 | 62.239 | -122.4545 | 122.195 | 122.3637 | 122.1472 | 62.2974 | -122.6091
453.4219 | 122.5708 | -62.2604 | 60.2142 | 1.4211e-13 | -0.0078589 | -0.012222 | 0.01637 | -0.03637 | 0.031235 | 0.022052 | -0.013658 | 0.010234 | 0.035136 | -0.0065085 | 0.039479 | -62.178 | 0.015142 | -62.2318 | 60.1526 | 60.0621 | 60.1033 | -62.2311 | -62.1961 | 0.082776 | -62.2993 | 59.9895 | 60.1491 | 59.9233 | -62.3811 | 0.029321 | -0.061608 | 0.082399 | 0.028617 | -0.000704 | -0.15212 | -0.11089 | -0.12068 | -0.22469 | 0.06429 | -0.038896 | 0.081784 | -0.065161 | -0.29089 | 122.4131 | 122.3225 | 122.3638 | 62.2756 | -122.4453 | 122.25 | 122.4095 | 122.1838 | 62.3432 | -122.5953
455.1406 | 122.699 | -62.2192 | 60.1639 | 1.4211e-13 | -0.0074317 | -0.012222 | 0.016584 | -0.036797 | 0.031022 | -0.00083919 | -0.013658 | 0.010448 | 0.035136 | -0.0065085 | 0.039693 | -62.1689 | 0.010564 | -62.2364 | 60.1572 | 60.0484 | 60.1079 | -62.2265 | -62.1916 | 0.087354 | -62.2993 | 59.9895 | 60.1491 | 59.9279 | -62.3811 | -0.007299 | -0.006675 | 0.050357 | -0.01716 | -0.009861 | -0.1155 | -0.055956 | -0.16188 | -0.17434 | 0.02767 | -0.080095 | 0.081784 | -0.014807 | -0.23596 | 122.3764 | 122.2676 | 122.3272 | 62.2298 | -122.3904 | 122.2088 | 122.3683 | 122.1472 | 62.3066 | -122.545
456.9219 | 122.5891 | -62.233 | 60.2554 | 1.4211e-13 | -0.0080727 | -0.01265 | 0.016584 | -0.036156 | 0.031235 | -0.00083919 | -0.013872 | 0.010662 | 0.034923 | -0.0069357 | 0.039693 | -62.1643 | 0.015142 | -62.241 | 60.148 | 60.0301 | 60.1125 | -62.2265 | -62.2007 | 0.082776 | -62.3085 | 59.985 | 60.1537 | 59.9325 | -62.3857 | 0.006434 | -0.10739 | 0.068668 | -0.008006 | -0.01444 | -0.22537 | -0.14293 | -0.15273 | -0.27047 | 0.032245 | -0.075519 | 0.077206 | -0.10178 | -0.32293 | 122.381 | 122.263 | 122.3455 | 62.2481 | -122.482 | 122.2179 | 122.3866 | 122.1655 | 62.3157 | -122.6411
458.7031 | 122.5662 | -62.2513 | 60.2234 | 1.4211e-13 | -0.0076453 | -0.012222 | 0.01637 | -0.03637 | 0.031235 | -0.00083919 | -0.013444 | 0.010662 | 0.034923 | -0.0065085 | 0.039693 | -62.1551 | 0.015142 | -62.2364 | 60.1526 | 60.0209 | 60.1079 | -62.222 | -62.1961 | 0.087354 | -62.2993 | 59.9895 | 60.1445 | 59.9233 | -62.3811 | 0.029324 | -0.070764 | 0.096136 | 0.014884 | -0.01444 | -0.20249 | -0.11547 | -0.12983 | -0.23385 | 0.055135 | -0.048051 | 0.081784 | -0.078896 | -0.30005 | 122.4039 | 122.2722 | 122.3592 | 62.2664 | -122.4453 | 122.2408 | 122.3958 | 122.1746 | 62.3386 | -122.6045
460.4219 | 122.6578 | -62.2101 | 60.173 | 1.4211e-13 | -0.0072179 | -0.012009 | 0.01637 | -0.036156 | 0.031235 | -0.0084697 | -0.013658 | 0.010448 | 0.035136 | -0.0067221 | 0.039479 | -62.1689 | 0.019721 | -62.2272 | 60.148 | 60.0484 | 60.1079 | -62.2265 | -62.2007 | 0.087354 | -62.3039 | 59.9895 | 60.1537 | 59.9233 | -62.3811 | -0.016454 | -0.024988 | 0.041202 | -0.017159 | -0.000705 | -0.12466 | -0.065112 | -0.17103 | -0.1835 | 0.009357 | -0.093829 | 0.077205 | -0.019384 | -0.24969 | 122.3581 | 122.2585 | 122.318 | 62.2298 | -122.3996 | 122.1996 | 122.3637 | 122.1334 | 62.2974 | -122.5542
462.2031 | 122.5845 | -62.2009 | 60.2509 | 1.4211e-13 | -0.0076453 | -0.012009 | 0.016157 | -0.036156 | 0.031235 | -0.00083919 | -0.013444 | 0.010662 | 0.034709 | -0.0062947 | 0.039479 | -62.1643 | 0.019721 | -62.2318 | 60.148 | 60.0209 | 60.1079 | -62.222 | -62.187 | 0.087354 | -62.2993 | 59.9895 | 60.1537 | 59.9233 | -62.3857 | -0.02103 | -0.10281 | 0.036625 | -0.030892 | -0.009862 | -0.22995 | -0.14293 | -0.18477 | -0.26131 | 0.013938 | -0.098405 | 0.086363 | -0.097203 | -0.32751 | 122.349 | 122.2218 | 122.3089 | 62.2206 | -122.4728 | 122.1905 | 122.3546 | 122.1243 | 62.2883 | -122.6365
463.9844 | 122.5937 | -62.2284 | 60.2646 | 1.4211e-13 | -0.0074317 | -0.012436 | 0.016157 | -0.03637 | 0.031235 | -0.0084697 | -0.013444 | 0.010662 | 0.034709 | -0.0067221 | 0.039479 | -62.1597 | 0.015142 | -62.2318 | 60.1572 | 60.0346 | 60.1079 | -62.222 | -62.1961 | 0.087354 | -62.3039 | 59.985 | 60.1445 | 59.9233 | -62.3811 | 0.006436 | -0.10738 | 0.06867 | -0.003426 | -0.009862 | -0.22995 | -0.15666 | -0.15272 | -0.27963 | 0.032247 | -0.075518 | 0.077205 | -0.12009 | -0.34124 | 122.3856 | 122.263 | 122.3363 | 62.2435 | -122.4865 | 122.2134 | 122.3729 | 122.1517 | 62.3157 | -122.6457
465.7656 | 122.7264 | -62.2147 | 60.1959 | 1.4211e-13 | -0.0074317 | -0.012222 | 0.016157 | -0.037011 | 0.031235 | 0.0067908 | -0.013658 | 0.010448 | 0.034923 | -0.0067221 | 0.039265 | -62.1689 | 0.0243 | -62.2318 | 60.1526 | 60.0758 | 60.1125 | -62.2311 | -62.1961 | 0.082776 | -62.3039 | 59.985 | 60.1491 | 59.9462 | -62.3811 | -0.016455 | -0.043298 | 0.04578 | -0.017159 | -0.000704 | -0.12007 | -0.083421 | -0.16646 | -0.21096 | 0.018514 | -0.089251 | 0.077205 | -0.046851 | -0.24969 | 122.3673 | 122.2905 | 122.3272 | 62.239 | -122.427 | 122.1996 | 122.3637 | 122.1609 | 62.2974 | -122.577
467.5312 | 122.6807 | -62.2421 | 60.1593 | 1.4211e-13 | -0.0078589 | -0.012222 | 0.016584 | -0.036797 | 0.031235 | 0.0067908 | -0.013231 | 0.010875 | 0.034923 | -0.0065085 | 0.039479 | -62.1643 | 0.0243 | -62.2318 | 60.1526 | 60.0942 | 60.1125 | -62.2311 | -62.1824 | 0.087354 | -62.3039 | 59.985 | 60.1399 | 59.9371 | -62.3857 | 0.01101 | -0.006677 | 0.077823 | 0.010306 | -0.000704 | -0.065137 | -0.0468 | -0.14357 | -0.17434 | 0.059715 | -0.061786 | 0.081784 | -0.019387 | -0.22222 | 122.3948 | 122.3363 | 122.3546 | 62.2664 | -122.3904 | 122.2271 | 122.382 | 122.1792 | 62.3295 | -122.545
469.3438 | 122.5525 | -62.2467 | 60.2142 | 1.4211e-13 | -0.0076453 | -0.012222 | 0.01637 | -0.036797 | 0.031449 | 0.0067908 | -0.013444 | 0.010448 | 0.03535 | -0.0065085 | 0.039906 | -62.1643 | 0.015142 | -62.2272 | 60.148 | 60.0346 | 60.1033 | -62.2311 | -62.1961 | 0.082776 | -62.3039 | 59.9758 | 60.1445 | 59.9233 | -62.3765 | 0.015588 | -0.066186 | 0.082401 | 0.019462 | 0.003874 | -0.17959 | -0.11089 | -0.12983 | -0.23843 | 0.050557 | -0.057208 | 0.072626 | -0.06974 | -0.29089 | 122.3948 | 122.2813 | 122.35 | 62.2618 | -122.4453 | 122.2225 | 122.3912 | 122.17 | 62.3295 | -122.5908
471.0469 | 122.6166 | -62.233 | 60.1868 | 1.4211e-13 | -0.0074317 | -0.012436 | 0.016157 | -0.03637 | 0.031449 | -0.0084697 | -0.013872 | 0.010448 | 0.034923 | -0.0062947 | 0.039479 | -62.1689 | 0.010564 | -62.2364 | 60.148 | 60.0758 | 60.1033 | -62.2265 | -62.1961 | 0.082776 | -62.3039 | 59.9987 | 60.1445 | 59.9233 | -62.3765 | 0.006434 | -0.038721 | 0.06409 | -0.003427 | -0.009861 | -0.11092 | -0.083423 | -0.14357 | -0.18807 | 0.036824 | -0.070941 | 0.072626 | -0.042275 | -0.26342 | 122.381 | 122.3088 | 122.3363 | 62.2435 | -122.4133 | 122.2317 | 122.3775 | 122.1563 | 62.3157 | -122.5633
472.8281 | 122.5754 | -62.2192 | 60.2371 | 1.4211e-13 | -0.0076453 | -0.012222 | 0.016157 | -0.036583 | 0.031022 | -0.00083919 | -0.013658 | 0.010875 | 0.034709 | -0.0067221 | 0.039479 | -62.1689 | 0.010564 | -62.2272 | 60.1526 | 60.0804 | 60.1033 | -62.222 | -62.1961 | 0.082776 | -62.3039 | 59.9895 | 60.1491 | 59.9233 | -62.3765 | -0.00272 | -0.084497 | 0.050357 | -0.008004 | -0.005284 | -0.15669 | -0.13378 | -0.1573 | -0.24758 | 0.023091 | -0.084674 | 0.072626 | -0.08805 | -0.31378 | 122.3719 | 122.2997 | 122.3226 | 62.2298 | -122.4591 | 122.2088 | 122.3683 | 122.1426 | 62.302 | -122.6137
474.5312 | 122.5525 | -62.2192 | 60.2371 | 1.4211e-13 | -0.0074317 | -0.012222 | 0.016584 | -0.03637 | 0.031235 | 0.0067908 | -0.014085 | 0.010662 | 0.034923 | -0.0062947 | 0.039479 | -62.1597 | 0.015142 | -62.2272 | 60.1572 | 60.0758 | 60.1079 | -62.2265 | -62.1916 | 0.082776 | -62.2993 | 59.9804 | 60.1445 | 59.9325 | -62.3857 | -0.007299 | -0.079918 | 0.059514 | -0.008004 | -0.000705 | -0.16127 | -0.1292 | -0.16646 | -0.25674 | 0.02767 | -0.080095 | 0.086363 | -0.092629 | -0.30462 | 122.3764 | 122.2951 | 122.3272 | 62.2344 | -122.4637 | 122.1996 | 122.3637 | 122.1517 | 62.302 | -122.6228
476.2969 | 122.6395 | -62.2421 | 60.1685 | 1.4211e-13 | -0.0076453 | -0.012222 | 0.01637 | -0.036797 | 0.031449 | -0.00083919 | -0.013658 | 0.010662 | 0.034709 | -0.0065085 | 0.039479 | -62.1643 | 0.019721 | -62.2227 | 60.1526 | 60.0667 | 60.1125 | -62.2311 | -62.187 | 0.078197 | -62.3039 | 59.985 | 60.1445 | 59.9279 | -62.3857 | 0.01101 | -0.015832 | 0.077823 | 0.019462 | 0.008452 | -0.10177 | -0.055955 | -0.14357 | -0.1835 | 0.055136 | -0.061786 | 0.081784 | -0.023964 | -0.24053 | 122.3948 | 122.3088 | 122.3546 | 62.2618 | -122.3996 | 122.2271 | 122.3866 | 122.17 | 62.3203 | -122.5542
478.0625 | 122.6303 | -62.2192 | 60.228 | 1.4211e-13 | -0.0078589 | -0.012222 | 0.016157 | -0.036583 | 0.031022 | 0.0067908 | -0.013658 | 0.010234 | 0.034923 | -0.0062947 | 0.039265 | -62.1643 | 0.015142 | -62.2272 | 60.148 | 60.0255 | 60.0988 | -62.2265 | -62.187 | 0.082776 | -62.2993 | 59.985 | 60.1445 | 59.9142 | -62.3765 | -0.007299 | -0.079919 | 0.054935 | -0.008004 | -0.000705 | -0.20249 | -0.1292 | -0.1573 | -0.24301 | 0.032248 | -0.080095 | 0.077205 | -0.083473 | -0.31378 | 122.3673 | 122.2447 | 122.318 | 62.2344 | -122.4545 | 122.2042 | 122.3637 | 122.1334 | 62.302 | -122.6045
479.8438 | 122.6166 | -62.233 | 60.2188 | 1.4211e-13 | -0.0076453 | -0.012436 | 0.016584 | -0.03637 | 0.031022 | -0.00083919 | -0.013658 | 0.010662 | 0.034923 | -0.0067221 | 0.039052 | -62.1643 | 0.010564 | -62.2272 | 60.1526 | 60.0346 | 60.0988 | -62.222 | -62.1824 | 0.091933 | -62.2993 | 59.985 | 60.1491 | 59.9096 | -62.3765 | 0.011013 | -0.066186 | 0.068668 | 0.005729 | -0.005284 | -0.18417 | -0.12005 | -0.14357 | -0.23385 | 0.05056 | -0.066362 | 0.077205 | -0.069739 | -0.3092 | 122.3856 | 122.2676 | 122.3317 | 62.2435 | -122.4408 | 122.2179 | 122.382 | 122.1426 | 62.3249 | -122.5953
481.625 | 122.58 | -62.2238 | 60.2371 | 1.4211e-13 | -0.0076453 | -0.012436 | 0.016157 | -0.036797 | 0.030594 | -0.0084697 | -0.013872 | 0.010448 | 0.034923 | -0.0065085 | 0.039693 | -62.1643 | 0.015142 | -62.2272 | 60.148 | 60.0575 | 60.1079 | -62.222 | -62.1961 | 0.091933 | -62.2993 | 59.9895 | 60.1491 | 59.9096 | -62.3857 | 0.001858 | -0.089075 | 0.059513 | -0.003426 | -0.005284 | -0.17959 | -0.1292 | -0.16188 | -0.24758 | 0.027669 | -0.075517 | 0.086363 | -0.08805 | -0.32751 | 122.3719 | 122.2813 | 122.3317 | 62.239 | -122.4591 | 122.2134 | 122.3729 | 122.1334 | 62.3157 | -122.6228
483.4062 | 122.58 | -62.2559 | 60.2371 | 1.4211e-13 | -0.0078589 | -0.011795 | 0.01637 | -0.036156 | 0.031022 | -0.00083919 | -0.013658 | 0.010448 | 0.034709 | -0.0062947 | 0.039479 | -62.1597 | 0.010564 | -62.2318 | 60.148 | 60.0804 | 60.1079 | -62.2128 | -62.187 | 0.087354 | -62.2948 | 59.9804 | 60.1399 | 59.9096 | -62.3811 | 0.043059 | -0.089075 | 0.096135 | 0.024039 | -0.01902 | -0.15669 | -0.1292 | -0.12526 | -0.25674 | 0.068869 | -0.038895 | 0.086363 | -0.097207 | -0.32751 | 122.4039 | 122.3363 | 122.3638 | 62.2664 | -122.4499 | 122.2362 | 122.3958 | 122.1655 | 62.3432 | -122.6182
485.125 | 122.6578 | -62.2192 | 60.1776 | 1.4211e-13 | -0.0078589 | -0.012436 | 0.016157 | -0.036583 | 0.031235 | -0.00083919 | -0.013872 | 0.010875 | 0.034709 | -0.0062947 | 0.039265 | -62.1597 | 0.019721 | -62.2272 | 60.1526 | 60.0438 | 60.1079 | -62.222 | -62.1961 | 0.091933 | -62.2993 | 59.985 | 60.1445 | 59.9188 | -62.3811 | -0.00272 | -0.024987 | 0.059514 | -0.008004 | -0.005284 | -0.13382 | -0.069689 | -0.16188 | -0.19265 | 0.023091 | -0.080095 | 0.081784 | -0.033119 | -0.25885 | 122.3719 | 122.263 | 122.3272 | 62.239 | -122.3996 | 122.2042 | 122.3637 | 122.138 | 62.3112 | -122.5587
486.9062 | 122.5616 | -62.2467 | 60.2417 | 1.4211e-13 | -0.0076453 | -0.012222 | 0.016157 | -0.03637 | 0.030808 | -0.0084697 | -0.013872 | 0.010875 | 0.03535 | -0.0062947 | 0.039479 | -62.1597 | 0.019721 | -62.2272 | 60.1572 | 60.0621 | 60.1079 | -62.222 | -62.1824 | 0.091933 | -62.2856 | 59.985 | 60.1537 | 59.9188 | -62.3811 | 0.024746 | -0.084495 | 0.08698 | 0.019462 | -0.005284 | -0.17959 | -0.13378 | -0.13441 | -0.25674 | 0.064293 | -0.038893 | 0.09552 | -0.088048 | -0.32293 | 122.4039 | 122.3088 | 122.3546 | 62.2664 | -122.4637 | 122.2317 | 122.4004 | 122.1655 | 62.3386 | -122.6228
488.6719 | 122.5845 | -62.2467 | 60.1868 | 1.4211e-13 | -0.0076453 | -0.011795 | 0.01637 | -0.036797 | 0.031022 | -0.00083919 | -0.013872 | 0.010662 | 0.035136 | -0.0067221 | 0.039693 | -62.1597 | 0.015142 | -62.2318 | 60.148 | 60.0758 | 60.1079 | -62.2311 | -62.187 | 0.091933 | -62.2993 | 59.985 | 60.1445 | 59.9371 | -62.3811 | 0.015588 | -0.038721 | 0.08698 | 0.014884 | -0.000704 | -0.11092 | -0.078845 | -0.13441 | -0.20181 | 0.059714 | -0.052629 | 0.081784 | -0.042275 | -0.24969 | 122.3948 | 122.3226 | 122.3546 | 62.2618 | -122.4179 | 122.2317 | 122.3912 | 122.1838 | 62.3386 | -122.5679
490.3906 | 122.6257 | -62.1872 | 60.2234 | 1.4211e-13 | -0.0076453 | -0.012222 | 0.016157 | -0.03637 | 0.031235 | 0.014421 | -0.013658 | 0.010234 | 0.034923 | -0.0060811 | 0.039265 | -62.1551 | 0.010564 | -62.2272 | 60.1526 | 60.085 | 60.1079 | -62.222 | -62.1824 | 0.087354 | -62.2993 | 59.9804 | 60.1445 | 59.9188 | -62.3903 | -0.034763 | -0.070764 | 0.032049 | -0.040047 | -0.005284 | -0.13838 | -0.11547 | -0.20308 | -0.24301 | 0.004784 | -0.11214 | 0.090941 | -0.078896 | -0.30462 | 122.3398 | 122.2722 | 122.2951 | 62.1978 | -122.4453 | 122.1676 | 122.3317 | 122.106 | 62.2745 | -122.6137
492.1719 | 122.5891 | -62.2284 | 60.228 | 1.4211e-13 | -0.0076453 | -0.012009 | 0.01637 | -0.036583 | 0.031449 | -0.00083919 | -0.013872 | 0.010662 | 0.035136 | -0.0062947 | 0.039479 | -62.1551 | 0.010564 | -62.2227 | 60.148 | 60.085 | 60.0988 | -62.222 | -62.1916 | 0.087354 | -62.2993 | 59.9804 | 60.1399 | 59.9188 | -62.3811 | 0.006436 | -0.079919 | 0.073248 | 0.00573 | -0.000706 | -0.14296 | -0.1292 | -0.15272 | -0.24758 | 0.036826 | -0.070939 | 0.081784 | -0.088051 | -0.3092 | 122.3764 | 122.3134 | 122.3272 | 62.239 | -122.4499 | 122.2088 | 122.3683 | 122.1472 | 62.3157 | -122.6091
493.9531 | 122.5708 | -62.233 | 60.2463 | 1.4211e-13 | -0.0074317 | -0.012222 | 0.016157 | -0.036583 | 0.031235 | -0.00083919 | -0.013444 | 0.010448 | 0.035136 | -0.0062947 | 0.039479 | -62.1597 | 0.0243 | -62.2272 | 60.148 | 60.0621 | 60.1033 | -62.2174 | -62.2007 | 0.073618 | -62.2993 | 59.985 | 60.1353 | 59.9142 | -62.3811 | 0.015592 | -0.09823 | 0.073247 | 0.005729 | -0.009863 | -0.18417 | -0.14293 | -0.14815 | -0.26132 | 0.032245 | -0.066362 | 0.081784 | -0.11094 | -0.33209 | 122.381 | 122.2951 | 122.3363 | 62.2573 | -122.4637 | 122.2179 | 122.3683 | 122.1472 | 62.3066 | -122.6274
495.6562 | 122.6257 | -62.2375 | 60.1776 | 1.4211e-13 | -0.0074317 | -0.011795 | 0.01637 | -0.036583 | 0.031449 | -0.00083919 | -0.013444 | 0.010662 | 0.035136 | -0.0062947 | 0.039265 | -62.1597 | 0.010564 | -62.2272 | 60.148 | 60.053 | 60.1033 | -62.2265 | -62.187 | 0.087354 | -62.2856 | 59.985 | 60.1399 | 59.9279 | -62.3857 | 0.011012 | -0.029565 | 0.077825 | 0.010307 | -0.000705 | -0.12466 | -0.074267 | -0.14815 | -0.19265 | 0.050559 | -0.048048 | 0.1001 | -0.037697 | -0.24969 | 122.3856 | 122.2905 | 122.3409 | 62.2481 | -122.4041 | 122.2225 | 122.3775 | 122.1655 | 62.3249 | -122.5633
497.4375 | 122.6212 | -62.2009 | 60.2325 | 1.4211e-13 | -0.0080727 | -0.012222 | 0.015943 | -0.036583 | 0.031022 | 0.0067908 | -0.014085 | 0.010448 | 0.035136 | -0.0065085 | 0.039479 | -62.1506 | 0.015142 | -62.2318 | 60.148 | 60.0392 | 60.1079 | -62.222 | -62.187 | 0.082776 | -62.2948 | 59.985 | 60.1491 | 59.9188 | -62.3811 | -0.02103 | -0.084497 | 0.05036 | -0.030892 | -0.009862 | -0.19333 | -0.12462 | -0.18019 | -0.24758 | 0.013938 | -0.093826 | 0.086363 | -0.083472 | -0.31378 | 122.349 | 122.2401 | 122.3089 | 62.2161 | -122.4545 | 122.1859 | 122.35 | 122.1197 | 62.2837 | -122.6137
499.1562 | 122.7219 | -62.1826 | 60.1822 | 1.4211e-13 | -0.0078589 | -0.012009 | 0.016798 | -0.03637 | 0.031235 | 0.0067908 | -0.013658 | 0.010448 | 0.034923 | -0.0060811 | 0.039265 | -62.1597 | 0.019721 | -62.2227 | 60.1435 | 60.0621 | 60.1033 | -62.222 | -62.1961 | 0.087354 | -62.2856 | 59.985 | 60.1491 | 59.9188 | -62.3857 | -0.039341 | -0.038722 | 0.022893 | -0.040047 | -0.000706 | -0.12008 | -0.078845 | -0.20308 | -0.19723 | -0.01353 | -0.10298 | 0.1001 | -0.033118 | -0.26342 | 122.3261 | 122.2447 | 122.286 | 62.2023 | -122.4041 | 122.1676 | 122.3317 | 122.1014 | 62.27 | -122.5679
500.9219 | 122.5891 | -62.1918 | 60.2234 | 1.4211e-13 | -0.0072179 | -0.012009 | 0.016157 | -0.03637 | 0.031235 | -0.00083919 | -0.013658 | 0.010662 | 0.034709 | -0.0058675 | 0.039693 | -62.1597 | 0.015142 | -62.2272 | 60.148 | 60.085 | 60.1079 | -62.2265 | -62.1916 | 0.087354 | -62.2993 | 59.9758 | 60.1445 | 59.9233 | -62.3903 | -0.034765 | -0.075342 | 0.032048 | -0.03547 | -0.000705 | -0.13838 | -0.11547 | -0.1985 | -0.24759 | 0.000204 | -0.10756 | 0.090941 | -0.078896 | -0.30005 | 122.3398 | 122.2768 | 122.2997 | 62.2069 | -122.4499 | 122.1676 | 122.3363 | 122.1151 | 62.2791 | -122.6137
502.7031 | 122.6028 | -62.1964 | 60.228 | 1.4211e-13 | -0.0076453 | -0.012222 | 0.01637 | -0.036583 | 0.031235 | 0.0067908 | -0.013872 | 0.010448 | 0.03535 | -0.0062947 | 0.039479 | -62.1643 | 0.019721 | -62.2227 | 60.1435 | 60.0713 | 60.1033 | -62.2265 | -62.1824 | 0.082776 | -62.2948 | 59.985 | 60.1491 | 59.9142 | -62.3857 | -0.030187 | -0.084498 | 0.032047 | -0.026314 | 0.003873 | -0.1567 | -0.12462 | -0.18935 | -0.24301 | 0.013939 | -0.098404 | 0.090942 | -0.078894 | -0.31378 | 122.3398 | 122.2676 | 122.2997 | 62.2161 | -122.4545 | 122.1813 | 122.3454 | 122.1105 | 62.2791 | -122.6137
504.4844 | 122.6761 | -62.2192 | 60.1501 | 1.4211e-13 | -0.0074317 | -0.012436 | 0.016584 | -0.036583 | 0.031022 | 0.0067908 | -0.013658 | 0.010448 | 0.035136 | -0.0060811 | 0.039479 | -62.1597 | 0.019721 | -62.2227 | 60.1526 | 60.0438 | 60.1033 | -62.2174 | -62.1824 | 0.082776 | -62.2902 | 59.985 | 60.1399 | 59.9233 | -62.3857 | 0.001859 | 0.002479 | 0.059514 | -0.003426 | -0.005285 | -0.10635 | -0.046801 | -0.16646 | -0.16519 | 0.036827 | -0.070937 | 0.095521 | -0.010231 | -0.2268 | 122.3719 | 122.263 | 122.3226 | 62.239 | -122.3675 | 122.2042 | 122.3592 | 122.1426 | 62.302 | -122.5358
506.25 | 122.612 | -62.2055 | 60.1776 | 1.4211e-13 | -0.0074317 | -0.012009 | 0.016157 | -0.036797 | 0.031235 | -0.00083919 | -0.014085 | 0.010448 | 0.035136 | -0.0062947 | 0.039693 | -62.1506 | 0.015142 | -62.2227 | 60.148 | 60.085 | 60.1033 | -62.2265 | -62.1824 | 0.087354 | -62.2948 | 59.9804 | 60.1537 | 59.9233 | -62.3857 | -0.021032 | -0.029565 | 0.054937 | -0.017159 | 0.003873 | -0.092605 | -0.074267 | -0.18019 | -0.19723 | 0.023094 | -0.089249 | 0.090942 | -0.023961 | -0.25427 | 122.3536 | 122.2905 | 122.3089 | 62.2206 | -122.4041 | 122.1859 | 122.3592 | 122.1288 | 62.2929 | -122.5633
508.0156 | 122.5754 | -62.2467 | 60.1822 | 1.4211e-13 | -0.0078589 | -0.012436 | 0.015943 | -0.036583 | 0.030808 | -0.00083919 | -0.014085 | 0.010448 | 0.034709 | -0.0060811 | 0.039479 | -62.1597 | 0.010564 | -62.2318 | 60.1435 | 60.0667 | 60.1033 | -62.222 | -62.187 | 0.091933 | -62.2902 | 59.9804 | 60.1491 | 59.9279 | -62.3903 | 0.024746 | -0.038722 | 0.08698 | 0.014884 | -0.009862 | -0.1155 | -0.078845 | -0.14357 | -0.20181 | 0.059714 | -0.043471 | 0.1001 | -0.033118 | -0.25427 | 122.3902 | 122.3134 | 122.35 | 62.2573 | -122.4041 | 122.2271 | 122.3958 | 122.1746 | 62.3386 | -122.5725
509.7656 | 122.5616 | -62.2467 | 60.1959 | 1.4211e-13 | -0.0078589 | -0.012222 | 0.01637 | -0.03637 | 0.031235 | -0.00083919 | -0.013872 | 0.010662 | 0.035136 | -0.0058675 | 0.039265 | -62.1643 | 0.010564 | -62.2272 | 60.1389 | 60.0896 | 60.1079 | -62.2265 | -62.1916 | 0.078197 | -62.2948 | 59.9758 | 60.1491 | 59.9508 | -62.3811 | 0.020167 | -0.057033 | 0.082401 | 0.019462 | -0.000705 | -0.10634 | -0.088 | -0.13441 | -0.22012 | 0.055136 | -0.04805 | 0.086363 | -0.046851 | -0.24511 | 122.3856 | 122.3363 | 122.3546 | 62.2573 | -122.4225 | 122.2225 | 122.3958 | 122.1975 | 62.3249 | -122.577
511.5469 | 122.612 | -62.2055 | 60.2097 | 1.4211e-13 | -0.0076453 | -0.012222 | 0.016584 | -0.036583 | 0.031022 | 0.0067908 | -0.013658 | 0.010234 | 0.034923 | -0.0060811 | 0.039052 | -62.1597 | 0.019721 | -62.2227 | 60.1435 | 60.0758 | 60.1033 | -62.222 | -62.187 | 0.087354 | -62.2948 | 59.9804 | 60.1399 | 59.9142 | -62.3857 | -0.016453 | -0.066188 | 0.045781 | -0.017159 | -0.000706 | -0.13381 | -0.10631 | -0.18019 | -0.22927 | 0.018515 | -0.089249 | 0.090942 | -0.069741 | -0.29547 | 122.349 | 122.2814 | 122.3089 | 62.2252 | -122.4316 | 122.1859 | 122.3454 | 122.1197 | 62.2929 | -122.5954
513.3125 | 122.6028 | -62.2055 | 60.2234 | 1.4211e-13 | -0.0074317 | -0.012222 | 0.01637 | -0.036797 | 0.031022 | -0.00083919 | -0.013872 | 0.010662 | 0.035564 | -0.0060811 | 0.039265 | -62.1597 | 0.019721 | -62.2272 | 60.1435 | 60.0575 | 60.1079 | -62.222 | -62.1778 | 0.082776 | -62.2993 | 59.985 | 60.1445 | 59.9188 | -62.3857 | -0.016453 | -0.079921 | 0.045781 | -0.021737 | -0.005284 | -0.16586 | -0.11547 | -0.18019 | -0.23843 | 0.027673 | -0.093828 | 0.086363 | -0.078896 | -0.30462 | 122.349 | 122.263 | 122.3134 | 62.2252 | -122.4453 | 122.1905 | 122.35 | 122.1243 | 62.2883 | -122.6091
515.0156 | 122.6807 | -62.2101 | 60.1593 | 1.4211e-13 | -0.0078589 | -0.012009 | 0.016157 | -0.03637 | 0.031022 | 0.0067908 | -0.013872 | 0.010662 | 0.034709 | -0.0060811 | 0.039052 | -62.1597 | 0.0243 | -62.2227 | 60.148 | 60.0942 | 60.1079 | -62.222 | -62.1824 | 0.087354 | -62.2902 | 59.985 | 60.1445 | 59.9233 | -62.3765 | -0.011875 | -0.011255 | 0.050359 | -0.012581 | -0.000706 | -0.065137 | -0.051379 | -0.16645 | -0.17434 | 0.027672 | -0.080092 | 0.086363 | -0.014809 | -0.23596 | 122.3581 | 122.3042 | 122.318 | 62.2344 | -122.3813 | 122.195 | 122.3546 | 122.1334 | 62.2974 | -122.5358
516.8281 | 122.7036 | -62.2147 | 60.1959 | 1.4211e-13 | -0.0076453 | -0.012436 | 0.01637 | -0.037011 | 0.031022 | 0.0067908 | -0.013872 | 0.010234 | 0.034923 | -0.0060811 | 0.039479 | -62.1551 | 0.010564 | -62.2227 | 60.1435 | 60.0942 | 60.1079 | -62.222 | -62.187 | 0.091933 | -62.2948 | 59.9804 | 60.1537 | 59.9325 | -62.3765 | -0.007297 | -0.052455 | 0.059515 | -0.008003 | -0.000706 | -0.10176 | -0.088 | -0.16188 | -0.21554 | 0.027671 | -0.080093 | 0.081784 | -0.042272 | -0.26342 | 122.3581 | 122.3088 | 122.3226 | 62.2252 | -122.4179 | 122.195 | 122.3683 | 122.1472 | 62.3066 | -122.5725
518.625 | 122.5662 | -62.2147 | 60.2417 | 1.4211e-13 | -0.0074317 | -0.012009 | 0.016157 | -0.036583 | 0.030808 | 0.0067908 | -0.014085 | 0.010234 | 0.035564 | -0.0056537 | 0.039693 | -62.1597 | 0.015142 | -62.2272 | 60.1526 | 60.0896 | 60.1033 | -62.222 | -62.1824 | 0.087354 | -62.2902 | 59.9758 | 60.1491 | 59.9142 | -62.3857 | -0.007297 | -0.089074 | 0.054937 | -0.012581 | -0.005284 | -0.15211 | -0.13835 | -0.17104 | -0.2659 | 0.03225 | -0.075514 | 0.095521 | -0.092627 | -0.32751 | 122.3673 | 122.3042 | 122.318 | 62.2298 | -122.4637 | 122.1905 | 122.3637 | 122.1288 | 62.302 | -122.6274
520.75 | 122.5708 | -62.2467 | 60.2142 | 1.4211e-13 | -0.0074317 | -0.012222 | 0.015943 | -0.036583 | 0.031022 | 0.014421 | -0.014085 | 0.010448 | 0.035136 | -0.0065085 | 0.039265 | -62.1506 | 0.015142 | -62.2272 | 60.148 | 60.0621 | 60.1079 | -62.2174 | -62.187 | 0.082776 | -62.2856 | 59.9804 | 60.1445 | 59.9279 | -62.3903 | 0.029325 | -0.066186 | 0.096136 | 0.019462 | -0.009863 | -0.15212 | -0.10631 | -0.14357 | -0.23385 | 0.059714 | -0.038893 | 0.10468 | -0.06974 | -0.28631 | 122.3948 | 122.3088 | 122.3546 | 62.2618 | -122.4316 | 122.2271 | 122.3912 | 122.1746 | 62.3295 | -122.6045
522.5469 | 122.699 | -62.1689 | 60.141 | 1.4211e-13 | -0.0078589 | -0.012222 | 0.016157 | -0.036583 | 0.031022 | -0.00083919 | -0.014085 | 0.010234 | 0.034923 | -0.0060811 | 0.039479 | -62.1597 | 0.019721 | -62.2227 | 60.1526 | 60.085 | 60.1033 | -62.2174 | -62.1778 | 0.087354 | -62.2948 | 59.9804 | 60.1399 | 59.9188 | -62.3857 | -0.048495 | 0.011634 | 0.00916 | -0.05378 | -0.005285 | -0.055984 | -0.037646 | -0.21681 | -0.16061 | -0.008948 | -0.12587 | 0.090942 | -0.001076 | -0.22223 | 122.3215 | 122.2539 | 122.2722 | 62.1886 | -122.3584 | 122.1493 | 122.3088 | 122.0876 | 62.2562 | -122.5267
524.4688 | 122.5571 | -62.2559 | 60.1913 | 1.4211e-13 | -0.0074317 | -0.011581 | 0.015943 | -0.036797 | 0.031235 | -0.00083919 | -0.013658 | 0.010448 | 0.035136 | -0.0060811 | 0.039479 | -62.1551 | 0.015142 | -62.2181 | 60.1389 | 60.0758 | 60.1079 | -62.2311 | -62.1824 | 0.082776 | -62.2856 | 59.985 | 60.1399 | 59.9233 | -62.3765 | 0.024743 | -0.052455 | 0.10071 | 0.037774 | 0.013031 | -0.1155 | -0.083422 | -0.12068 | -0.20638 | 0.073448 | -0.029738 | 0.090941 | -0.05143 | -0.268 | 122.3947 | 122.3317 | 122.3638 | 62.271 | -122.4225 | 122.2408 | 122.3958 | 122.1792 | 62.3386 | -122.5679
528.8594 | 122.5708 | -62.2009 | 60.1913 | 1.4211e-13 | -0.0078589 | -0.012009 | 0.015943 | -0.036797 | 0.031022 | -0.00083919 | -0.014085 | 0.010234 | 0.034923 | -0.0062947 | 0.039693 | -62.1506 | 0.019721 | -62.2227 | 60.1435 | 60.0621 | 60.1033 | -62.222 | -62.187 | 0.087354 | -62.2902 | 59.9804 | 60.1445 | 59.9233 | -62.3811 | -0.02103 | -0.047877 | 0.05036 | -0.021736 | -0.000706 | -0.12923 | -0.088 | -0.18019 | -0.21096 | 0.013938 | -0.089247 | 0.090942 | -0.046852 | -0.268 | 122.3444 | 122.263 | 122.3043 | 62.2206 | -122.4133 | 122.1813 | 122.3454 | 122.1243 | 62.2883 | -122.5725
530.9062 | 122.5983 | -62.1964 | 60.2188 | 1.4211e-13 | -0.0078589 | -0.012009 | 0.01637 | -0.036797 | 0.031022 | 0.0067908 | -0.014085 | 0.010448 | 0.034923 | -0.0058675 | 0.039479 | -62.1597 | 0.015142 | -62.2227 | 60.1435 | 60.0942 | 60.1033 | -62.2174 | -62.187 | 0.087354 | -62.2948 | 59.9804 | 60.1353 | 59.9142 | -62.3811 | -0.021029 | -0.075343 | 0.036626 | -0.026314 | -0.005285 | -0.12465 | -0.11547 | -0.18477 | -0.23843 | 0.00936 | -0.098404 | 0.086363 | -0.083475 | -0.30463 | 122.3398 | 122.2905 | 122.2997 | 62.2115 | -122.4362 | 122.1767 | 122.3317 | 122.1105 | 62.2837 | -122.5999
532.6875 | 122.7081 | -62.1826 | 60.173 | 1.4211e-13 | -0.0074317 | -0.012009 | 0.016157 | -0.036583 | 0.031235 | 0.014421 | -0.013872 | 0.010234 | 0.034923 | -0.0060811 | 0.039265 | -62.146 | 0.010564 | -62.2318 | 60.1435 | 60.0896 | 60.1033 | -62.2128 | -62.187 | 0.078197 | -62.2856 | 59.9895 | 60.1445 | 59.9142 | -62.3811 | -0.030183 | -0.029567 | 0.036628 | -0.049203 | -0.01902 | -0.083449 | -0.06969 | -0.1985 | -0.1835 | -0.004373 | -0.10298 | 0.09552 | -0.028542 | -0.25885 | 122.3261 | 122.2722 | 122.286 | 62.1932 | -122.3858 | 122.1722 | 122.3271 | 122.0968 | 62.2608 | -122.5542
534.4375 | 122.58 | -62.2238 | 60.2097 | 1.4211e-13 | -0.0080727 | -0.012222 | 0.015943 | -0.036797 | 0.031022 | -0.0084697 | -0.014299 | 0.010234 | 0.034923 | -0.0058675 | 0.039265 | -62.1506 | 0.015142 | -62.2227 | 60.1526 | 60.0896 | 60.1033 | -62.222 | -62.1824 | 0.087354 | -62.2856 | 59.985 | 60.1491 | 59.9188 | -62.3811 | 0.001858 | -0.057031 | 0.073248 | 0.001152 | -0.000706 | -0.12007 | -0.10631 | -0.1573 | -0.2247 | 0.041405 | -0.061781 | 0.09552 | -0.060584 | -0.29089 | 122.3764 | 122.3134 | 122.3272 | 62.239 | -122.4316 | 122.2088 | 122.3729 | 122.1426 | 62.3112 | -122.5908
536.375 | 122.644 | -62.2192 | 60.1868 | 1.4211e-13 | -0.0080727 | -0.012009 | 0.016157 | -0.037011 | 0.031022 | -0.00083919 | -0.014085 | 0.010662 | 0.034709 | -0.0062947 | 0.039265 | -62.1551 | 0.019721 | -62.2227 | 60.1435 | 60.0804 | 60.1033 | -62.2311 | -62.187 | 0.087354 | -62.2948 | 59.9758 | 60.1445 | 59.9279 | -62.3811 | -0.011878 | -0.0433 | 0.064092 | -0.003426 | 0.008452 | -0.10634 | -0.083423 | -0.16188 | -0.21096 | 0.032248 | -0.075516 | 0.086363 | -0.042275 | -0.25885 | 122.3627 | 122.2997 | 122.3226 | 62.239 | -122.4179 | 122.195 | 122.3637 | 122.1472 | 62.3066 | -122.5679
538.875 | 122.6669 | -62.2238 | 60.1685 | 1.4211e-13 | -0.0076453 | -0.012222 | 0.016157 | -0.03637 | 0.031022 | 0.0067908 | -0.013872 | 0.010448 | 0.034923 | -0.0058675 | 0.039052 | -62.1551 | 0.0243 | -62.2227 | 60.1435 | 60.085 | 60.1079 | -62.2265 | -62.187 | 0.087354 | -62.2902 | 59.9895 | 60.1399 | 59.9096 | -62.3811 | -0.002721 | -0.024989 | 0.06867 | 0.001152 | 0.003873 | -0.08345 | -0.060534 | -0.1573 | -0.17892 | 0.036826 | -0.066359 | 0.090942 | -0.028542 | -0.25885 | 122.3673 | 122.3088 | 122.3317 | 62.2481 | -122.395 | 122.2134 | 122.3637 | 122.1334 | 62.3112 | -122.5496
540.6562 | 122.5525 | -62.2192 | 60.228 | 1.4211e-13 | -0.0076453 | -0.012009 | 0.016157 | -0.036583 | 0.031235 | 0.0067908 | -0.014085 | 0.010662 | 0.034923 | -0.0062947 | 0.039479 | -62.1597 | 0.015142 | -62.2227 | 60.1389 | 60.0942 | 60.1033 | -62.2128 | -62.1778 | 0.091933 | -62.2902 | 59.9895 | 60.1445 | 59.9096 | -62.3765 | 0.006438 | -0.089076 | 0.059514 | -0.003426 | -0.009864 | -0.1338 | -0.12462 | -0.1573 | -0.23843 | 0.041406 | -0.070937 | 0.086363 | -0.083473 | -0.31836 | 122.3581 | 122.3134 | 122.3226 | 62.2344 | -122.4408 | 122.2088 | 122.3637 | 122.1288 | 62.3112 | -122.6045
542.5781 | 122.644 | -62.2101 | 60.1776 | 1.4211e-13 | -0.0078589 | -0.012009 | 0.015729 | -0.036583 | 0.030808 | 0.0067908 | -0.013872 | 0.010234 | 0.034923 | -0.0056537 | 0.039479 | -62.1551 | 0.019721 | -62.2227 | 60.1435 | 60.0942 | 60.1079 | -62.2128 | -62.1778 | 0.087354 | -62.2902 | 59.9804 | 60.1445 | 59.9142 | -62.3765 | -0.002717 | -0.034144 | 0.054937 | -0.012581 | -0.009864 | -0.083447 | -0.069689 | -0.16645 | -0.19723 | 0.032251 | -0.080092 | 0.086363 | -0.033119 | -0.26343 | 122.3536 | 122.3042 | 122.318 | 62.2298 | -122.3904 | 122.1905 | 122.3546 | 122.1243 | 62.2974 | -122.5541
544.4062 | 122.6624 | -62.2009 | 60.1685 | 1.4211e-13 | -0.0078589 | -0.012222 | 0.016157 | -0.036797 | 0.031022 | -0.00083919 | -0.014299 | 0.010448 | 0.034709 | -0.0058675 | 0.039479 | -62.1551 | 0.0243 | -62.2181 | 60.148 | 60.0713 | 60.1079 | -62.2082 | -62.1778 | 0.087354 | -62.2902 | 59.985 | 60.1445 | 59.9325 | -62.3857 | -0.007293 | -0.02041 | 0.045782 | -0.017157 | -0.009864 | -0.097187 | -0.060534 | -0.18477 | -0.1835 | 0.023096 | -0.089247 | 0.095521 | -0.023964 | -0.23596 | 122.349 | 122.2722 | 122.3089 | 62.2252 | -122.3767 | 122.1859 | 122.3454 | 122.1334 | 62.2883 | -122.5542
546.2812 | 122.525 | -62.2238 | 60.2005 | 1.4211e-13 | -0.0076453 | -0.012009 | 0.016157 | -0.036583 | 0.031235 | -0.00083919 | -0.014299 | 0.010448 | 0.035136 | -0.0060811 | 0.039479 | -62.1551 | 0.015142 | -62.2227 | 60.1526 | 60.0896 | 60.1033 | -62.222 | -62.1824 | 0.091933 | -62.2902 | 59.9804 | 60.1491 | 59.9142 | -62.3857 | 0.001858 | -0.047875 | 0.06867 | 0.001152 | -0.000706 | -0.11091 | -0.097155 | -0.16188 | -0.22012 | 0.041405 | -0.066359 | 0.095521 | -0.051428 | -0.28631 | 122.3764 | 122.3134 | 122.3272 | 62.239 | -122.4225 | 122.2042 | 122.3729 | 122.138 | 62.3157 | -122.5862
548.0938 | 122.6257 | -62.2238 | 60.1547 | 1.4211e-13 | -0.0078589 | -0.012009 | 0.01637 | -0.036797 | 0.031022 | 0.014421 | -0.013872 | 0.011089 | 0.034709 | -0.0054401 | 0.039052 | -62.1551 | 0.0243 | -62.2181 | 60.148 | 60.0987 | 60.1079 | -62.222 | -62.1824 | 0.096512 | -62.2856 | 59.9804 | 60.1445 | 59.9142 | -62.3811 | 0.001858 | -0.006677 | 0.06867 | 0.005731 | 0.003873 | -0.05598 | -0.046801 | -0.1573 | -0.17434 | 0.041405 | -0.061781 | 0.09552 | -0.010231 | -0.24054 | 122.3719 | 122.3226 | 122.3317 | 62.2481 | -122.3767 | 122.2042 | 122.3683 | 122.138 | 62.3203 | -122.5358
549.9062 | 122.5342 | -62.2101 | 60.2234 | 1.4211e-13 | -0.0076453 | -0.012009 | 0.015943 | -0.037011 | 0.030808 | -0.00083919 | -0.014085 | 0.010234 | 0.034923 | -0.0058675 | 0.039479 | -62.146 | 0.015142 | -62.2227 | 60.1435 | 60.0804 | 60.1079 | -62.2128 | -62.1824 | 0.082776 | -62.2948 | 59.9804 | 60.1445 | 59.9233 | -62.3857 | -0.002717 | -0.079921 | 0.064094 | -0.012581 | -0.009864 | -0.14296 | -0.11547 | -0.17561 | -0.24301 | 0.027672 | -0.084671 | 0.090942 | -0.078896 | -0.30005 | 122.3536 | 122.2905 | 122.318 | 62.2252 | -122.4362 | 122.1905 | 122.3546 | 122.1334 | 62.2929 | -122.6091
551.625 | 122.5433 | -62.2375 | 60.2005 | 1.4211e-13 | -0.0080727 | -0.012222 | 0.016157 | -0.036583 | 0.031022 | -0.0084697 | -0.014299 | 0.010448 | 0.034709 | -0.0060811 | 0.039479 | -62.146 | 0.015142 | -62.2272 | 60.148 | 60.0713 | 60.1079 | -62.2174 | -62.1778 | 0.082776 | -62.2902 | 59.9895 | 60.1399 | 59.9096 | -62.3765 | 0.02017 | -0.052453 | 0.09156 | 0.010307 | -0.009863 | -0.12923 | -0.092577 | -0.13899 | -0.21096 | 0.059717 | -0.052626 | 0.086363 | -0.060585 | -0.29089 | 122.3856 | 122.3088 | 122.3455 | 62.2527 | -122.4179 | 122.2271 | 122.3775 | 122.1472 | 62.3203 | -122.577
553.3438 | 122.5845 | -62.2147 | 60.2005 | 1.4211e-13 | -0.0076453 | -0.011795 | 0.01637 | -0.036797 | 0.031022 | 0.0067908 | -0.014085 | 0.010662 | 0.034709 | -0.0062947 | 0.038838 | -62.1506 | 0.019721 | -62.2181 | 60.1389 | 60.0804 | 60.0988 | -62.2128 | -62.1778 | 0.078197 | -62.2856 | 59.9758 | 60.1445 | 59.9142 | -62.372 | 0.001861 | -0.06161 | 0.064093 | -0.003424 | -0.005285 | -0.12007 | -0.10173 | -0.1573 | -0.2247 | 0.036829 | -0.070936 | 0.086362 | -0.056007 | -0.28631 | 122.3536 | 122.2951 | 122.3134 | 62.2344 | -122.4133 | 122.1905 | 122.3592 | 122.1288 | 62.2929 | -122.5725
555.0625 | 122.6852 | -62.2147 | 60.141 | 1.4211e-13 | -0.0076453 | -0.012436 | 0.016157 | -0.036797 | 0.031022 | -0.00083919 | -0.014299 | 0.010662 | 0.034496 | -0.0058675 | 0.039479 | -62.146 | 0.015142 | -62.2181 | 60.148 | 60.0942 | 60.1079 | -62.2265 | -62.187 | 0.091933 | -62.2856 | 59.9758 | 60.1399 | 59.9142 | -62.3765 | -0.011876 | 0.007056 | 0.068672 | -0.003424 | 0.008452 | -0.046826 | -0.033068 | -0.16188 | -0.16519 | 0.027671 | -0.070936 | 0.090941 | -0.001076 | -0.2268 | 122.3627 | 122.3088 | 122.3226 | 62.2298 | -122.3675 | 122.1905 | 122.3546 | 122.1288 | 62.3066 | -122.5175
556.8906 | 122.5845 | -62.2101 | 60.1776 | 1.4211e-13 | -0.0078589 | -0.012009 | 0.015943 | -0.036583 | 0.031022 | -0.00083919 | -0.014299 | 0.010234 | 0.034923 | -0.0058675 | 0.039479 | -62.1414 | 0.0243 | -62.2135 | 60.1389 | 60.0942 | 60.1033 | -62.222 | -62.1824 | 0.078197 | -62.2856 | 59.9712 | 60.1353 | 59.9142 | -62.3765 | -0.011875 | -0.038722 | 0.068672 | -0.003424 | 0.008451 | -0.083447 | -0.074267 | -0.16645 | -0.20639 | 0.027672 | -0.075514 | 0.090941 | -0.042276 | -0.26343 | 122.349 | 122.3042 | 122.3134 | 62.2344 | -122.3996 | 122.1813 | 122.3454 | 122.1243 | 62.2883 | -122.5541
558.6562 | 122.612 | -62.178 | 60.2051 | 1.4211e-13 | -0.0078589 | -0.011795 | 0.016157 | -0.036583 | 0.030808 | 0.0067908 | -0.013872 | 0.010234 | 0.034709 | -0.0056537 | 0.039265 | -62.1551 | 0.015142 | -62.2227 | 60.1435 | 60.0942 | 60.1171 | -62.222 | -62.1824 | 0.091933 | -62.2948 | 59.9804 | 60.1445 | 59.9188 | -62.3765 | -0.043918 | -0.06161 | 0.022894 | -0.044624 | -0.000706 | -0.11091 | -0.087998 | -0.1985 | -0.2247 | -0.004371 | -0.11671 | 0.081784 | -0.060585 | -0.28631 | 122.3215 | 122.2722 | 122.2951 | 62.1932 | -122.427 | 122.1584 | 122.3225 | 122.0968 | 62.27 | -122.5816
560.375 | 122.6349 | -62.1964 | 60.2005 | 1.4211e-13 | -0.0076453 | -0.012009 | 0.016157 | -0.03637 | 0.030808 | -0.00083919 | -0.013658 | 0.010234 | 0.034923 | -0.0056537 | 0.039052 | -62.1368 | 0.015142 | -62.2181 | 60.1389 | 60.0942 | 60.1079 | -62.2174 | -62.1824 | 0.087354 | -62.2856 | 59.9804 | 60.1399 | 59.9188 | -62.372 | -0.021029 | -0.06161 | 0.059517 | -0.021735 | -0.000706 | -0.10634 | -0.092577 | -0.17561 | -0.22012 | 0.013939 | -0.089247 | 0.086362 | -0.060585 | -0.28173 | 122.3352 | 122.2905 | 122.3043 | 62.2115 | -122.4179 | 122.1767 | 122.3363 | 122.1151 | 62.2837 | -122.5725
562.1562 | 122.7036 | -62.2009 | 60.1868 | 1.4211e-13 | -0.0076453 | -0.012222 | 0.016584 | -0.036797 | 0.031235 | -0.0084697 | -0.014085 | 0.010448 | 0.035136 | -0.0060811 | 0.039265 | -62.1506 | 0.019721 | -62.2227 | 60.148 | 60.0896 | 60.1079 | -62.2128 | -62.1778 | 0.091933 | -62.2902 | 59.985 | 60.1399 | 59.9188 | -62.3765 | -0.011872 | -0.038721 | 0.05036 | -0.021736 | -0.009864 | -0.097182 | -0.078845 | -0.17561 | -0.20181 | 0.023096 | -0.089247 | 0.086363 | -0.046853 | -0.268 | 122.349 | 122.2905 | 122.3089 | 62.2206 | -122.3996 | 122.1859 | 122.3408 | 122.1197 | 62.2929 | -122.5633
563.875 | 122.7036 | -62.178 | 60.1639 | 1.4211e-13 | -0.0078589 | -0.011795 | 0.015943 | -0.036797 | 0.031022 | 0.0067908 | -0.013444 | 0.010234 | 0.034923 | -0.0058675 | 0.039265 | -62.146 | 0.015142 | -62.2181 | 60.1526 | 60.0758 | 60.1079 | -62.2265 | -62.1733 | 0.091933 | -62.281 | 59.985 | 60.1399 | 59.9096 | -62.3765 | -0.048497 | -0.011254 | 0.032051 | -0.040045 | 0.008452 | -0.08803 | -0.055956 | -0.1985 | -0.17892 | 0.004787 | -0.10298 | 0.09552 | -0.023964 | -0.25427 | 122.3307 | 122.2539 | 122.286 | 62.1932 | -122.3904 | 122.163 | 122.318 | 122.0876 | 62.27 | -122.5404
565.6562 | 122.6944 | -62.1918 | 60.1639 | 1.4211e-13 | -0.0080727 | -0.012009 | 0.016157 | -0.036797 | 0.030808 | 0.0067908 | -0.013872 | 0.010448 | 0.034923 | -0.0056537 | 0.039479 | -62.1506 | 0.028878 | -62.2181 | 60.1435 | 60.085 | 60.1125 | -62.2128 | -62.1733 | 0.087354 | -62.281 | 59.985 | 60.1399 | 59.9188 | -62.3811 | -0.021028 | -0.020411 | 0.041204 | -0.026313 | -0.005285 | -0.078872 | -0.051377 | -0.18935 | -0.17892 | 0.018519 | -0.089246 | 0.1001 | -0.023964 | -0.24511 | 122.3352 | 122.2768 | 122.3043 | 62.2206 | -122.3767 | 122.1767 | 122.3317 | 122.1105 | 62.2791 | -122.545
567.3906 | 122.5571 | -62.2009 | 60.2188 | 1.4211e-13 | -0.0076453 | -0.012009 | 0.01637 | -0.037011 | 0.031022 | 0.0067908 | -0.013872 | 0.010662 | 0.034923 | -0.0060811 | 0.039479 | -62.1506 | 0.019721 | -62.2181 | 60.1343 | 60.085 | 60.1033 | -62.2082 | -62.1778 | 0.082776 | -62.281 | 59.9895 | 60.1399 | 59.9096 | -62.3811 | -0.007293 | -0.084499 | 0.05036 | -0.017157 | -0.009864 | -0.1338 | -0.11547 | -0.18019 | -0.22927 | 0.023096 | -0.08009 | 0.1001 | -0.078896 | -0.3092 | 122.3352 | 122.2859 | 122.3043 | 62.2206 | -122.427 | 122.1905 | 122.3408 | 122.1105 | 62.2837 | -122.5999
569.1562 | 122.5433 | -62.1918 | 60.2325 | 1.4211e-13 | -0.0076453 | -0.012222 | 0.01637 | -0.036583 | 0.031022 | -0.00083919 | -0.014085 | 0.010448 | 0.035136 | -0.0054401 | 0.039479 | -62.146 | 0.015142 | -62.2135 | 60.1435 | 60.0804 | 60.1125 | -62.2082 | -62.1778 | 0.087354 | -62.2948 | 59.9758 | 60.1399 | 59.9142 | -62.3765 | -0.016449 | -0.089076 | 0.045783 | -0.021735 | -0.005286 | -0.15212 | -0.12004 | -0.18477 | -0.25674 | 0.01394 | -0.10298 | 0.081784 | -0.092629 | -0.31836 | 122.3352 | 122.2722 | 122.3043 | 62.2069 | -122.4408 | 122.1676 | 122.3317 | 122.106 | 62.2791 | -122.6091
570.9375 | 122.5342 | -62.2147 | 60.2325 | 1.4211e-13 | -0.0082863 | -0.012436 | 0.016157 | -0.036797 | 0.031022 | 0.0067908 | -0.013872 | 0.010448 | 0.034923 | -0.0062947 | 0.039265 | -62.146 | 0.019721 | -62.2135 | 60.1435 | 60.0346 | 60.0988 | -62.2128 | -62.1824 | 0.087354 | -62.2856 | 59.9804 | 60.1399 | 59.9188 | -62.3765 | 0.001861 | -0.089076 | 0.068672 | 0.001154 | -0.000707 | -0.1979 | -0.13378 | -0.16188 | -0.25216 | 0.03225 | -0.070936 | 0.090941 | -0.092629 | -0.31378 | 122.3581 | 122.2493 | 122.3134 | 62.2344 | -122.4453 | 122.195 | 122.3546 | 122.1334 | 62.302 | -122.6091
572.6562 | 122.6807 | -62.1735 | 60.1501 | 1.4211e-13 | -0.0076453 | -0.012222 | 0.01637 | -0.036583 | 0.030808 | -0.00083919 | -0.014299 | 0.010448 | 0.034923 | -0.0060811 | 0.039265 | -62.1506 | 0.019721 | -62.2227 | 60.148 | 60.0804 | 60.1079 | -62.2128 | -62.1778 | 0.087354 | -62.2856 | 59.9758 | 60.1399 | 59.9096 | -62.3765 | -0.039338 | -0.002099 | 0.022894 | -0.049202 | -0.009864 | -0.069718 | -0.042223 | -0.20308 | -0.17434 | -0.00437 | -0.11214 | 0.090941 | -0.010231 | -0.24054 | 122.3215 | 122.2539 | 122.2814 | 62.1932 | -122.3629 | 122.1493 | 122.3134 | 122.0831 | 62.2608 | -122.5267
574.3906 | 122.5067 | -62.2284 | 60.228 | 1.4211e-13 | -0.0078589 | -0.012436 | 0.016584 | -0.036797 | 0.030808 | 0.014421 | -0.013872 | 0.010234 | 0.034709 | -0.0058675 | 0.039052 | -62.146 | 0.015142 | -62.2135 | 60.148 | 60.0575 | 60.1079 | -62.2082 | -62.1778 | 0.087354 | -62.2902 | 59.9758 | 60.1353 | 59.9096 | -62.3765 | 0.020173 | -0.079919 | 0.082405 | 0.014887 | -0.005286 | -0.17043 | -0.12004 | -0.14814 | -0.25216 | 0.050562 | -0.061781 | 0.086363 | -0.09263 | -0.31836 | 122.3764 | 122.2859 | 122.3363 | 62.2435 | -122.4362 | 122.2042 | 122.3637 | 122.138 | 62.3157 | -122.6045
576.1562 | 122.5616 | -62.1964 | 60.2371 | 1.4211e-13 | -0.0080727 | -0.012222 | 0.015943 | -0.036797 | 0.031022 | -0.00083919 | -0.014085 | 0.010662 | 0.034923 | -0.0060811 | 0.039052 | -62.1506 | 0.015142 | -62.2181 | 60.1435 | 60.0621 | 60.1079 | -62.2082 | -62.1778 | 0.082776 | -62.281 | 59.985 | 60.1445 | 59.9096 | -62.3811 | -0.011871 | -0.093654 | 0.045782 | -0.021735 | -0.009864 | -0.17501 | -0.1292 | -0.18477 | -0.25216 | 0.018518 | -0.084668 | 0.1001 | -0.092629 | -0.32751 | 122.3398 | 122.2585 | 122.3043 | 62.2115 | -122.4453 | 122.1813 | 122.3408 | 122.106 | 62.2791 | -122.6182
577.8594 | 122.6669 | -62.1872 | 60.1547 | 1.4211e-13 | -0.0078589 | -0.011581 | 0.015943 | -0.036797 | 0.030808 | -0.0161 | -0.013872 | 0.010448 | 0.034923 | -0.0056537 | 0.039052 | -62.1506 | 0.0243 | -62.2181 | 60.1389 | 60.0621 | 60.0988 | -62.2082 | -62.1733 | 0.082776 | -62.2856 | 59.9758 | 60.1399 | 59.9188 | -62.3765 | -0.021026 | -0.015834 | 0.036627 | -0.03089 | -0.009864 | -0.092612 | -0.055958 | -0.18934 | -0.17892 | 0.013942 | -0.098402 | 0.090941 | -0.014809 | -0.23596 | 122.3261 | 122.2493 | 122.286 | 62.2115 | -122.3629 | 122.163 | 122.3271 | 122.106 | 62.27 | -122.5313
579.625 | 122.6669 | -62.2147 | 60.2005 | 1.4211e-13 | -0.0076453 | -0.012009 | 0.015943 | -0.037011 | 0.031022 | -0.00083919 | -0.013872 | 0.010448 | 0.034923 | -0.0060811 | 0.039265 | -62.1506 | 0.015142 | -62.2272 | 60.1435 | 60.0942 | 60.1079 | -62.2128 | -62.1778 | 0.087354 | -62.2902 | 59.9804 | 60.1491 | 59.9142 | -62.372 | 0.001861 | -0.057032 | 0.064093 | -0.012581 | -0.014442 | -0.10634 | -0.092577 | -0.1573 | -0.22012 | 0.036829 | -0.075514 | 0.081784 | -0.051428 | -0.28631 | 122.3581 | 122.3088 | 122.3226 | 62.2298 | -122.4133 | 122.195 | 122.3637 | 122.1288 | 62.302 | -122.5725
581.4219 | 122.525 | -62.2284 | 60.2097 | 1.4211e-13 | -0.0080727 | -0.012222 | 0.015943 | -0.036797 | 0.031022 | -0.0084697 | -0.013872 | 0.010448 | 0.035136 | -0.0058675 | 0.039693 | -62.1368 | 0.019721 | -62.2135 | 60.1389 | 60.0575 | 60.1033 | -62.2265 | -62.1733 | 0.087354 | -62.2948 | 59.9758 | 60.1445 | 59.9325 | -62.3765 | 0.001857 | -0.070766 | 0.091561 | 0.014887 | 0.01303 | -0.15212 | -0.10631 | -0.14814 | -0.23385 | 0.055141 | -0.06636 | 0.081784 | -0.065163 | -0.27716 | 122.3673 | 122.2859 | 122.3317 | 62.2481 | -122.4362 | 122.2042 | 122.3729 | 122.1609 | 62.3157 | -122.5862
583.2031 | 122.6669 | -62.1964 | 60.1318 | 1.4211e-13 | -0.0080727 | -0.011795 | 0.016157 | -0.037011 | 0.030594 | 0.0067908 | -0.014299 | 0.010448 | 0.035136 | -0.0056537 | 0.039265 | -62.1506 | 0.010564 | -62.2227 | 60.1435 | 60.0942 | 60.1125 | -62.2128 | -62.1687 | 0.087354 | -62.2856 | 59.9804 | 60.1399 | 59.9233 | -62.3765 | -0.01645 | 0.011632 | 0.045782 | -0.026314 | -0.009864 | -0.037671 | -0.019334 | -0.18019 | -0.15145 | 0.027675 | -0.089247 | 0.090941 | 0.008079 | -0.20849 | 122.3398 | 122.2905 | 122.3089 | 62.2069 | -122.3446 | 122.1767 | 122.3363 | 122.1197 | 62.2837 | -122.5084
584.9844 | 122.6624 | -62.1826 | 60.1639 | 1.4211e-13 | -0.0082863 | -0.012009 | 0.015943 | -0.036583 | 0.031022 | -0.00083919 | -0.014085 | 0.010448 | 0.034496 | -0.0054401 | 0.039265 | -62.1414 | 0.0243 | -62.2181 | 60.148 | 60.0804 | 60.1125 | -62.2174 | -62.1733 | 0.082776 | -62.2856 | 59.9804 | 60.1445 | 59.905 | -62.3765 | -0.034762 | -0.015832 | 0.041206 | -0.035468 | -0.000706 | -0.083451 | -0.051377 | -0.19392 | -0.1835 | 0.009364 | -0.10298 | 0.090941 | -0.019386 | -0.25885 | 122.3307 | 122.263 | 122.2951 | 62.2069 | -122.3813 | 122.163 | 122.3271 | 122.0876 | 62.2654 | -122.5404
586.7031 | 122.5296 | -62.2101 | 60.2234 | 1.4211e-13 | -0.0080727 | -0.012222 | 0.015943 | -0.036797 | 0.031235 | 0.014421 | -0.013872 | 0.010234 | 0.034923 | -0.0056537 | 0.039265 | -62.1414 | 0.010564 | -62.2181 | 60.1389 | 60.0942 | 60.1033 | -62.2036 | -62.1733 | 0.087354 | -62.281 | 59.9804 | 60.1445 | 59.9096 | -62.372 | 0.006441 | -0.084499 | 0.068672 | -0.008002 | -0.014443 | -0.12922 | -0.12004 | -0.16188 | -0.24301 | 0.03683 | -0.070935 | 0.090941 | -0.078896 | -0.31378 | 122.349 | 122.3042 | 122.3134 | 62.2206 | -122.427 | 122.1905 | 122.3546 | 122.1197 | 62.2974 | -122.5953
588.4375 | 122.5983 | -62.2238 | 60.2188 | 1.4211e-13 | -0.0078589 | -0.011795 | 0.015729 | -0.036583 | 0.031449 | -0.00083919 | -0.013872 | 0.010448 | 0.035136 | -0.0058675 | 0.039265 | -62.146 | 0.019721 | -62.2089 | 60.1435 | 60.0942 | 60.1033 | -62.2174 | -62.1733 | 0.087354 | -62.281 | 59.9666 | 60.1491 | 59.9096 | -62.3765 | 0.006437 | -0.075343 | 0.077827 | 0.014887 | 0.00845 | -0.12465 | -0.11547 | -0.15272 | -0.25216 | 0.050563 | -0.057202 | 0.09552 | -0.069739 | -0.3092 | 122.3673 | 122.318 | 122.3272 | 62.2435 | -122.4362 | 122.1905 | 122.3729 | 122.1334 | 62.3112 | -122.5953
590.2031 | 122.5479 | -62.1964 | 60.2463 | 1.4211e-13 | -0.0078589 | -0.012222 | 0.015943 | -0.036583 | 0.030808 | 0.014421 | -0.014085 | 0.010234 | 0.034923 | -0.0054401 | 0.039052 | -62.1368 | 0.015142 | -62.2135 | 60.1389 | 60.0804 | 60.1079 | -62.2128 | -62.1733 | 0.087354 | -62.281 | 59.9804 | 60.1445 | 59.9096 | -62.3811 | -0.01645 | -0.10739 | 0.059517 | -0.017157 | -0.000707 | -0.16585 | -0.13835 | -0.18477 | -0.2659 | 0.023097 | -0.084668 | 0.1001 | -0.10178 | -0.33667 | 122.3352 | 122.2768 | 122.3043 | 62.2115 | -122.4591 | 122.1767 | 122.3408 | 122.106 | 62.2837 | -122.6274
592 | 122.644 | -62.2055 | 60.1685 | 1.4211e-13 | -0.0078589 | -0.012222 | 0.016157 | -0.036797 | 0.031449 | -0.00083919 | -0.014085 | 0.010662 | 0.035136 | -0.0056537 | 0.039265 | -62.1506 | 0.015142 | -62.2227 | 60.148 | 60.1033 | 60.1125 | -62.222 | -62.1778 | 0.082776 | -62.2764 | 59.9758 | 60.1445 | 59.9188 | -62.3811 | -0.016453 | -0.02041 | 0.054937 | -0.017159 | -0.000706 | -0.065134 | -0.055955 | -0.17561 | -0.19265 | 0.027673 | -0.070934 | 0.10468 | -0.023964 | -0.24969 | 122.3536 | 122.3088 | 122.318 | 62.2206 | -122.3904 | 122.1813 | 122.35 | 122.1243 | 62.2883 | -122.5496
593.7031 | 122.644 | -62.2055 | 60.1456 | 1.4211e-13 | -0.0076453 | -0.012222 | 0.015943 | -0.036583 | 0.031235 | 0.0067908 | -0.014513 | 0.010234 | 0.034923 | -0.0056537 | 0.039052 | -62.1506 | 0.019721 | -62.2227 | 60.148 | 60.0942 | 60.1125 | -62.2128 | -62.1687 | 0.091933 | -62.2856 | 59.9758 | 60.1491 | 59.9142 | -62.3811 | -0.007295 | 0.002478 | 0.054937 | -0.017159 | -0.009864 | -0.051404 | -0.033067 | -0.17561 | -0.16977 | 0.03683 | -0.080092 | 0.09552 | 0.003503 | -0.23138 | 122.3536 | 122.2997 | 122.318 | 62.2252 | -122.3584 | 122.1813 | 122.3546 | 122.1197 | 62.2974 | -122.5267
595.4844 | 122.6349 | -62.178 | 60.1547 | 1.4211e-13 | -0.0078589 | -0.011795 | 0.015943 | -0.036797 | 0.030808 | -0.00083919 | -0.014085 | 0.010448 | 0.035136 | -0.0052265 | 0.038838 | -62.146 | 0.0243 | -62.2135 | 60.1435 | 60.0896 | 60.1079 | -62.2128 | -62.1824 | 0.087354 | -62.281 | 59.9712 | 60.1445 | 59.9188 | -62.3811 | -0.03476 | -0.011256 | 0.032051 | -0.035467 | -0.000707 | -0.065138 | -0.046801 | -0.20308 | -0.1835 | -0.004371 | -0.10298 | 0.1001 | -0.010231 | -0.23596 | 122.3215 | 122.2676 | 122.286 | 62.2023 | -122.3675 | 122.1493 | 122.3225 | 122.0968 | 62.2654 | -122.5358
597.25 | 122.5204 | -62.2009 | 60.2325 | 1.4211e-13 | -0.0076453 | -0.012009 | 0.016157 | -0.037011 | 0.031022 | 0.0067908 | -0.014085 | 0.010234 | 0.034709 | -0.0056537 | 0.039265 | -62.1368 | 0.015142 | -62.2227 | 60.148 | 60.0896 | 60.1079 | -62.222 | -62.1778 | 0.082776 | -62.2902 | 59.985 | 60.1445 | 59.9096 | -62.3811 | -0.02103 | -0.084497 | 0.064095 | -0.021736 | -0.000706 | -0.14296 | -0.12462 | -0.18019 | -0.24758 | 0.023096 | -0.089247 | 0.090942 | -0.088051 | -0.32294 | 122.349 | 122.2905 | 122.3089 | 62.2161 | -122.4545 | 122.1859 | 122.3454 | 122.1105 | 62.2837 | -122.6137
599.8906 | 122.5342 | -62.178 | 60.2188 | 1.4211e-13 | -0.0078589 | -0.011795 | 0.015729 | -0.036583 | 0.030808 | -0.0084697 | -0.013658 | 0.010448 | 0.034923 | -0.0058675 | 0.039479 | -62.146 | 0.019721 | -62.2181 | 60.1389 | 60.0942 | 60.1079 | -62.2174 | -62.1778 | 0.087354 | -62.2856 | 59.9758 | 60.1445 | 59.9142 | -62.3765 | -0.039339 | -0.079921 | 0.032051 | -0.040045 | -0.000706 | -0.12465 | -0.11089 | -0.1985 | -0.24301 | 0.000208 | -0.10756 | 0.090941 | -0.074318 | -0.30463 | 122.3169 | 122.2722 | 122.286 | 62.1978 | -122.4362 | 122.1538 | 122.3225 | 122.0922 | 62.2654 | -122.5953
602.0938 | 122.5296 | -62.2101 | 60.2051 | 1.4211e-13 | -0.0078589 | -0.012009 | 0.015729 | -0.036797 | 0.031235 | -0.0084697 | -0.013872 | 0.010662 | 0.034923 | -0.0056537 | 0.039265 | -62.1368 | 0.019721 | -62.2227 | 60.1435 | 60.0987 | 60.1079 | -62.2174 | -62.1733 | 0.082776 | -62.2856 | 59.9666 | 60.1353 | 59.9554 | -62.3765 | -0.007296 | -0.06161 | 0.07325 | -0.012581 | -0.005285 | -0.10633 | -0.097155 | -0.16645 | -0.23843 | 0.03683 | -0.075514 | 0.090941 | -0.069742 | -0.24968 | 122.3536 | 122.3088 | 122.318 | 62.2298 | -122.4225 | 122.1767 | 122.3454 | 122.1655 | 62.2929 | -122.5816
604.4688 | 122.6624 | -62.1872 | 60.1364 | 1.4211e-13 | -0.0080727 | -0.012009 | 0.015943 | -0.036797 | 0.031022 | -0.00083919 | -0.014085 | 0.010448 | 0.034923 | -0.0054401 | 0.039265 | -62.146 | 0.010564 | -62.2135 | 60.1389 | 60.0942 | 60.1079 | -62.222 | -62.1733 | 0.087354 | -62.2764 | 59.9712 | 60.1399 | 59.9554 | -62.372 | -0.034763 | 0.002476 | 0.041206 | -0.026312 | 0.008451 | -0.042249 | -0.028491 | -0.18476 | -0.16519 | 0.013942 | -0.089244 | 0.09552 | 0.003501 | -0.18102 | 122.3261 | 122.2814 | 122.2951 | 62.1978 | -122.3584 | 122.1584 | 122.3271 | 122.1426 | 62.2745 | -122.5084
606.7656 | 122.612 | -62.1872 | 60.2097 | 1.4211e-13 | -0.0078589 | -0.012222 | 0.016157 | -0.036797 | 0.031022 | -0.00083919 | -0.014085 | 0.010662 | 0.034923 | -0.0054401 | 0.039265 | -62.146 | 0.010564 | -62.2089 | 60.1343 | 60.1033 | 60.1079 | -62.2128 | -62.1778 | 0.091933 | -62.2856 | 59.9758 | 60.1308 | 59.9142 | -62.3765 | -0.025605 | -0.075344 | 0.041206 | -0.021734 | 0.003871 | -0.10633 | -0.10173 | -0.18934 | -0.23385 | 0.009363 | -0.098402 | 0.090941 | -0.078898 | -0.29547 | 122.3215 | 122.2905 | 122.2951 | 62.1978 | -122.4225 | 122.163 | 122.318 | 122.1014 | 62.2791 | -122.5862
608.8281 | 122.525 | -62.2055 | 60.2097 | 1.4211e-13 | -0.0078589 | -0.012009 | 0.015943 | -0.03637 | 0.031022 | 0.0067908 | -0.014299 | 0.010234 | 0.034923 | -0.0052265 | 0.039265 | -62.1506 | 0.019721 | -62.2181 | 60.148 | 60.0942 | 60.1079 | -62.2082 | -62.1733 | 0.091933 | -62.281 | 59.9758 | 60.1399 | 59.9142 | -62.372 | -0.002716 | -0.061609 | 0.054937 | -0.01258 | -0.009864 | -0.11549 | -0.10173 | -0.16645 | -0.23385 | 0.032252 | -0.075513 | 0.090941 | -0.069741 | -0.29547 | 122.3536 | 122.2997 | 122.3134 | 62.2252 | -122.4179 | 122.1813 | 122.3454 | 122.1197 | 62.2974 | -122.5816
611.1406 | 122.6257 | -62.2101 | 60.1501 | 1.4211e-13 | -0.0080727 | -0.012009 | 0.015729 | -0.037224 | 0.030808 | -0.00083919 | -0.014085 | 0.010448 | 0.034923 | -0.0054401 | 0.038838 | -62.1368 | 0.019721 | -62.2089 | 60.1435 | 60.0987 | 60.1079 | -62.2128 | -62.1778 | 0.082776 | -62.281 | 59.9804 | 60.1491 | 59.9142 | -62.3811 | -0.002717 | -0.006678 | 0.07325 | 0.001154 | 0.003871 | -0.051402 | -0.042223 | -0.17103 | -0.16976 | 0.032251 | -0.070935 | 0.1001 | -0.001074 | -0.23596 | 122.3536 | 122.3088 | 122.318 | 62.2298 | -122.3629 | 122.1905 | 122.3592 | 122.1243 | 62.2929 | -122.5313
612.9375 | 122.6761 | -62.1643 | 60.1776 | 1.4211e-13 | -0.0080727 | -0.012009 | 0.016157 | -0.036797 | 0.031022 | -0.0084697 | -0.013872 | 0.010448 | 0.034923 | -0.0054401 | 0.039265 | -62.1414 | 0.028878 | -62.2089 | 60.1389 | 60.0942 | 60.1079 | -62.2128 | -62.1687 | 0.087354 | -62.281 | 59.9804 | 60.1445 | 59.905 | -62.3765 | -0.048493 | -0.038722 | 0.022896 | -0.044622 | 0.003871 | -0.083447 | -0.069689 | -0.21223 | -0.19723 | -0.004368 | -0.11671 | 0.09552 | -0.033119 | -0.27258 | 122.3032 | 122.2585 | 122.2722 | 62.1932 | -122.3904 | 122.1447 | 122.3088 | 122.0693 | 62.2517 | -122.5541
615.0625 | 122.5525 | -62.1826 | 60.2509 | 1.4211e-13 | -0.0082863 | -0.012009 | 0.015943 | -0.036797 | 0.030808 | 0.014421 | -0.014299 | 0.010448 | 0.035136 | -0.0050127 | 0.039052 | -62.1323 | 0.019721 | -62.2135 | 60.1389 | 60.0896 | 60.1079 | -62.2128 | -62.1687 | 0.091933 | -62.281 | 59.9804 | 60.1308 | 59.905 | -62.3765 | -0.030183 | -0.11196 | 0.050363 | -0.03089 | -0.000707 | -0.16127 | -0.14293 | -0.19392 | -0.27047 | 0.013942 | -0.098401 | 0.09552 | -0.1201 | -0.34582 | 122.3215 | 122.2722 | 122.2905 | 62.2023 | -122.4637 | 122.163 | 122.3134 | 122.0876 | 62.2745 | -122.6274
618.0625 | 122.5754 | -62.1964 | 60.2234 | 1.4211e-13 | -0.0078589 | -0.012009 | 0.015729 | -0.036797 | 0.030808 | 0.0067908 | -0.013872 | 0.010234 | 0.034709 | -0.0052265 | 0.039479 | -62.1323 | 0.019721 | -62.2135 | 60.1435 | 60.0942 | 60.1033 | -62.2036 | -62.1687 | 0.078197 | -62.2764 | 59.9804 | 60.1399 | 59.905 | -62.3811 | -0.007292 | -0.079921 | 0.064096 | -0.017157 | -0.009865 | -0.12922 | -0.12004 | -0.18477 | -0.24301 | 0.027675 | -0.080089 | 0.10468 | -0.083474 | -0.31836 | 122.3398 | 122.2905 | 122.2997 | 62.2161 | -122.427 | 122.1767 | 122.3363 | 122.1014 | 62.2745 | -122.6045
620.125 | 122.5021 | -62.2147 | 60.1868 | 1.4211e-13 | -0.0082863 | -0.012222 | 0.015943 | -0.037011 | 0.030381 | -0.0084697 | -0.014299 | 0.010234 | 0.034923 | -0.0054401 | 0.039265 | -62.1368 | 0.019721 | -62.2135 | 60.1389 | 60.0896 | 60.1079 | -62.2082 | -62.1687 | 0.082776 | -62.281 | 59.9758 | 60.1353 | 59.9142 | -62.3765 | 0.00644 | -0.047878 | 0.077828 | 0.001154 | -0.005286 | -0.097182 | -0.078845 | -0.16188 | -0.21096 | 0.045986 | -0.066357 | 0.09552 | -0.051432 | -0.27258 | 122.3536 | 122.3042 | 122.3226 | 62.2344 | -122.395 | 122.1905 | 122.35 | 122.1288 | 62.2974 | -122.5633
622.1094 | 122.6028 | -62.1964 | 60.1913 | 1.4211e-13 | -0.0080727 | -0.012009 | 0.016157 | -0.036583 | 0.030808 | 0.0067908 | -0.014085 | 0.010448 | 0.034923 | -0.0052265 | 0.039265 | -62.1323 | 0.028878 | -62.2089 | 60.148 | 60.0987 | 60.1079 | -62.2082 | -62.1687 | 0.091933 | -62.2764 | 59.9804 | 60.1445 | 59.9096 | -62.3765 | -0.011871 | -0.043298 | 0.064096 | -0.012579 | -0.000708 | -0.092601 | -0.083422 | -0.18019 | -0.21096 | 0.027675 | -0.080089 | 0.1001 | -0.046852 | -0.28174 | 122.3444 | 122.2951 | 122.3043 | 62.2252 | -122.3996 | 122.1767 | 122.3408 | 122.106 | 62.2883 | -122.5679
624.1406 | 122.6028 | -62.2147 | 60.1547 | 1.4211e-13 | -0.0082863 | -0.012436 | 0.015943 | -0.037224 | 0.030808 | -0.00083919 | -0.014085 | 0.010662 | 0.035136 | -0.0050127 | 0.039265 | -62.1368 | 0.015142 | -62.2135 | 60.1389 | 60.1033 | 60.1033 | -62.2128 | -62.1733 | 0.087354 | -62.2719 | 59.9804 | 60.1491 | 59.9096 | -62.3765 | 0.001861 | -0.015834 | 0.077828 | 0.001154 | -0.000707 | -0.051401 | -0.051379 | -0.16188 | -0.17434 | 0.041408 | -0.0572 | 0.10468 | -0.005652 | -0.24512 | 122.3536 | 122.318 | 122.318 | 62.2298 | -122.3675 | 122.195 | 122.3637 | 122.1243 | 62.302 | -122.5313
626.3594 | 122.5342 | -62.2055 | 60.2325 | 1.4211e-13 | -0.0080727 | -0.012222 | 0.015729 | -0.037011 | 0.030808 | 0.014421 | -0.013872 | 0.010448 | 0.034923 | -0.0052265 | 0.039265 | -62.1368 | 0.015142 | -62.2135 | 60.148 | 60.0942 | 60.1033 | -62.2036 | -62.1641 | 0.087354 | -62.281 | 59.9758 | 60.1353 | 59.9142 | -62.3765 | 0.001863 | -0.084497 | 0.068672 | -0.008002 | -0.009865 | -0.13838 | -0.1292 | -0.17103 | -0.25674 | 0.041409 | -0.075513 | 0.09552 | -0.097208 | -0.31836 | 122.3536 | 122.2997 | 122.3089 | 62.2206 | -122.4362 | 122.1813 | 122.3408 | 122.1197 | 62.2929 | -122.6091
628.2812 | 122.644 | -62.2009 | 60.1547 | 1.4211e-13 | -0.0078589 | -0.012009 | 0.016157 | -0.037011 | 0.030594 | -0.00083919 | -0.014299 | 0.010448 | 0.034923 | -0.0052265 | 0.039479 | -62.1414 | 0.015142 | -62.2089 | 60.1389 | 60.0942 | 60.1079 | -62.2082 | -62.1641 | 0.082776 | -62.281 | 59.9758 | 60.1399 | 59.9142 | -62.372 | -0.007293 | -0.015834 | 0.059517 | -0.008001 | -0.000708 | -0.060559 | -0.046801 | -0.17103 | -0.17892 | 0.036832 | -0.08009 | 0.090941 | -0.014809 | -0.24054 | 122.3398 | 122.2951 | 122.3089 | 62.2161 | -122.3629 | 122.1767 | 122.3408 | 122.1151 | 62.2837 | -122.5267
630 | 122.644 | -62.1872 | 60.1273 | 1.4211e-13 | -0.0082863 | -0.012222 | 0.016157 | -0.036797 | 0.030594 | -0.00083919 | -0.014085 | 0.010662 | 0.034923 | -0.0052265 | 0.039265 | -62.1414 | 0.0243 | -62.2044 | 60.1435 | 60.0987 | 60.1079 | -62.2082 | -62.1687 | 0.091933 | -62.2719 | 59.9758 | 60.1399 | 59.9233 | -62.3765 | -0.021026 | 0.01621 | 0.045784 | -0.017156 | 0.00387 | -0.028514 | -0.019335 | -0.18934 | -0.15145 | 0.01852 | -0.084666 | 0.10468 | 0.012657 | -0.20391 | 122.3307 | 122.2859 | 122.2951 | 62.2115 | -122.3355 | 122.163 | 122.3271 | 122.1105 | 62.2791 | -122.5038
631.7812 | 122.6395 | -62.178 | 60.1822 | 1.4211e-13 | -0.0080727 | -0.012009 | 0.015729 | -0.036797 | 0.030808 | -0.00083919 | -0.014299 | 0.010662 | 0.035136 | -0.0054401 | 0.039265 | -62.1368 | 0.015142 | -62.2044 | 60.148 | 60.0987 | 60.1125 | -62.2128 | -62.1778 | 0.082776 | -62.2719 | 59.9804 | 60.1399 | 59.9096 | -62.3765 | -0.03476 | -0.034143 | 0.041207 | -0.026311 | 0.008449 | -0.083446 | -0.069688 | -0.1985 | -0.20181 | 0.000208 | -0.093821 | 0.10468 | -0.042275 | -0.27258 | 122.3261 | 122.2768 | 122.2905 | 62.1932 | -122.395 | 122.1584 | 122.318 | 122.0876 | 62.2608 | -122.5587
633.5156 | 122.5891 | -62.1918 | 60.2097 | 1.4211e-13 | -0.0080727 | -0.012222 | 0.015943 | -0.037011 | 0.030594 | 0.014421 | -0.014513 | 0.010234 | 0.034923 | -0.0050127 | 0.039265 | -62.1414 | 0.019721 | -62.2181 | 60.1435 | 60.0942 | 60.1079 | -62.2082 | -62.1641 | 0.091933 | -62.281 | 59.9804 | 60.1399 | 59.9096 | -62.3765 | -0.016449 | -0.066188 | 0.050361 | -0.026313 | -0.009864 | -0.11549 | -0.10173 | -0.18477 | -0.22927 | 0.027676 | -0.089246 | 0.09552 | -0.069741 | -0.30005 | 122.3352 | 122.2859 | 122.2997 | 62.2115 | -122.4179 | 122.1722 | 122.3317 | 122.1014 | 62.2837 | -122.5862
635.2812 | 122.5342 | -62.2101 | 60.2371 | 1.4211e-13 | -0.0080727 | -0.011795 | 0.01637 | -0.03637 | 0.030594 | -0.0084697 | -0.014299 | 0.010448 | 0.035136 | -0.0054401 | 0.039265 | -62.1368 | 0.010564 | -62.2089 | 60.1343 | 60.0942 | 60.1033 | -62.2174 | -62.1733 | 0.082776 | -62.281 | 59.9804 | 60.1491 | 59.9096 | -62.372 | -0.007296 | -0.10281 | 0.07325 | 0.001154 | 0.00845 | -0.14296 | -0.13378 | -0.16188 | -0.25674 | 0.03683 | -0.070935 | 0.090941 | -0.08805 | -0.32751 | 122.3444 | 122.3042 | 122.3134 | 62.2206 | -122.4545 | 122.1905 | 122.3592 | 122.1197 | 62.2929 | -122.6091
637.0469 | 122.5891 | -62.2009 | 60.2051 | 1.4211e-13 | -0.0082863 | -0.012009 | 0.015943 | -0.036797 | 0.030381 | 0.0067908 | -0.014513 | 0.010448 | 0.034923 | -0.0054401 | 0.039052 | -62.1414 | 0.019721 | -62.2044 | 60.148 | 60.0987 | 60.1125 | -62.2082 | -62.1595 | 0.082776 | -62.2719 | 59.9758 | 60.1491 | 59.9142 | -62.3765 | -0.007293 | -0.057031 | 0.059517 | -0.003423 | 0.00387 | -0.10633 | -0.092576 | -0.17561 | -0.22927 | 0.041411 | -0.070933 | 0.10468 | -0.056006 | -0.29089 | 122.349 | 122.2997 | 122.3134 | 62.2206 | -122.4133 | 122.1767 | 122.35 | 122.1151 | 62.2837 | -122.5816
638.7656 | 122.6761 | -62.2055 | 60.1547 | 1.4211e-13 | -0.0084999 | -0.011795 | 0.015943 | -0.037011 | 0.030594 | 0.0067908 | -0.013872 | 0.010234 | 0.034709 | -0.0047991 | 0.039265 | -62.1414 | 0.015142 | -62.2089 | 60.1389 | 60.0942 | 60.1079 | -62.2036 | -62.1687 | 0.082776 | -62.281 | 59.9804 | 60.1445 | 59.9233 | -62.372 | 0.001863 | -0.015834 | 0.064094 | -0.003424 | -0.005287 | -0.060559 | -0.046801 | -0.16645 | -0.17434 | 0.03683 | -0.075513 | 0.090941 | -0.010231 | -0.23138 | 122.3444 | 122.2997 | 122.3134 | 62.2206 | -122.3584 | 122.1859 | 122.35 | 122.1288 | 62.2883 | -122.5267
640.5625 | 122.5342 | -62.1964 | 60.2051 | 1.4211e-13 | -0.0080727 | -0.011795 | 0.015943 | -0.036583 | 0.030167 | -0.00083919 | -0.014085 | 0.010234 | 0.034923 | -0.0054401 | 0.039052 | -62.1368 | 0.010564 | -62.2089 | 60.1389 | 60.0942 | 60.1033 | -62.2128 | -62.1641 | 0.087354 | -62.2764 | 59.9758 | 60.1399 | 59.905 | -62.3857 | -0.01645 | -0.066188 | 0.059517 | -0.012579 | 0.003871 | -0.11091 | -0.10173 | -0.18935 | -0.22927 | 0.032254 | -0.080089 | 0.10926 | -0.065163 | -0.30005 | 122.3352 | 122.2905 | 122.2997 | 62.2069 | -122.4179 | 122.1722 | 122.3363 | 122.1014 | 62.2837 | -122.5908
642.2812 | 122.612 | -62.2055 | 60.1593 | 1.4211e-13 | -0.0080727 | -0.012009 | 0.015516 | -0.037011 | 0.030594 | -0.00083919 | -0.014085 | 0.010234 | 0.034709 | -0.0054401 | 0.039265 | -62.1323 | 0.015142 | -62.2089 | 60.148 | 60.1079 | 60.1079 | -62.2128 | -62.1687 | 0.082776 | -62.2719 | 59.9804 | 60.1445 | 59.9233 | -62.3765 | -0.007295 | -0.011255 | 0.073251 | -0.003424 | 0.003871 | -0.051401 | -0.051379 | -0.17103 | -0.17892 | 0.03683 | -0.066356 | 0.10468 | -0.014809 | -0.23596 | 122.3536 | 122.3134 | 122.3134 | 62.2206 | -122.3721 | 122.1859 | 122.35 | 122.1288 | 62.2883 | -122.5358
644.2812 | 122.5662 | -62.178 | 60.2142 | 1.4211e-13 | -0.0084999 | -0.011795 | 0.016157 | -0.037011 | 0.030594 | -0.00083919 | -0.014513 | 0.010448 | 0.034923 | -0.0050127 | 0.039052 | -62.1277 | 0.015142 | -62.2044 | 60.1435 | 60.0942 | 60.1079 | -62.2082 | -62.1641 | 0.087354 | -62.2764 | 59.9758 | 60.1399 | 59.905 | -62.3765 | -0.030181 | -0.070765 | 0.050364 | -0.026311 | 0.00387 | -0.12007 | -0.10631 | -0.1985 | -0.23843 | 0.013944 | -0.098399 | 0.1001 | -0.074318 | -0.3092 | 122.3215 | 122.2722 | 122.286 | 62.1932 | -122.4225 | 122.1538 | 122.318 | 122.0831 | 62.2654 | -122.5908
646.25 | 122.6212 | -62.1826 | 60.1318 | 1.4211e-13 | -0.0082863 | -0.012009 | 0.015943 | -0.036797 | 0.030594 | -0.00083919 | -0.014085 | 0.010448 | 0.034923 | -0.0047991 | 0.039052 | -62.1323 | 0.019721 | -62.2044 | 60.1435 | 60.1033 | 60.1125 | -62.2174 | -62.1687 | 0.087354 | -62.2764 | 59.9804 | 60.1445 | 59.9142 | -62.372 | -0.034762 | 0.011632 | 0.050363 | -0.021734 | 0.013028 | -0.028513 | -0.019334 | -0.18934 | -0.15145 | 0.013942 | -0.093822 | 0.09552 | 0.012657 | -0.21765 | 122.3261 | 122.2859 | 122.2951 | 62.2023 | -122.3492 | 122.163 | 122.3271 | 122.0968 | 62.27 | -122.5038
648.4844 | 122.6257 | -62.2055 | 60.1273 | 1.4211e-13 | -0.0080727 | -0.012009 | 0.015729 | -0.037224 | 0.030808 | 0.0067908 | -0.014299 | 0.010021 | 0.034923 | -0.0050127 | 0.039265 | -62.1277 | 0.010564 | -62.2044 | 60.148 | 60.1033 | 60.1079 | -62.2082 | -62.1595 | 0.078197 | -62.2764 | 59.9712 | 60.1445 | 59.9325 | -62.3765 | -0.002716 | 0.020789 | 0.077829 | 0.001154 | 0.00387 | -0.023935 | -0.019335 | -0.17103 | -0.15603 | 0.045988 | -0.070934 | 0.1001 | 0.017235 | -0.19476 | 122.3536 | 122.3088 | 122.3134 | 62.2161 | -122.3355 | 122.1767 | 122.35 | 122.138 | 62.2837 | -122.5038
650.6875 | 122.5891 | -62.2101 | 60.1639 | 1.4211e-13 | -0.0080727 | -0.012222 | 0.015729 | -0.036797 | 0.030594 | -0.00083919 | -0.014513 | 0.010875 | 0.034709 | -0.0052265 | 0.039265 | -62.1368 | 0.0243 | -62.2089 | 60.148 | 60.1033 | 60.1079 | -62.2036 | -62.1641 | 0.082776 | -62.2719 | 59.9804 | 60.1399 | 59.9325 | -62.372 | 0.006441 | -0.015832 | 0.07325 | 0.001154 | -0.005287 | -0.060556 | -0.055956 | -0.16188 | -0.1835 | 0.045987 | -0.061778 | 0.1001 | -0.023964 | -0.23138 | 122.3581 | 122.3134 | 122.318 | 62.2344 | -122.3675 | 122.1905 | 122.35 | 122.1426 | 62.2929 | -122.5358
652.9531 | 122.6532 | -62.146 | 60.173 | 1.4211e-13 | -0.0082863 | -0.012009 | 0.015729 | -0.036797 | 0.030594 | -0.0084697 | -0.014085 | 0.010662 | 0.034709 | -0.0045853 | 0.039265 | -62.1414 | 0.015142 | -62.2089 | 60.1435 | 60.0896 | 60.1079 | -62.2036 | -62.1687 | 0.091933 | -62.2764 | 59.9758 | 60.1491 | 59.9096 | -62.3765 | -0.057646 | -0.029567 | 0.004585 | -0.062933 | -0.005287 | -0.083449 | -0.065112 | -0.23054 | -0.19723 | -0.022679 | -0.13044 | 0.1001 | -0.023963 | -0.26343 | 122.2895 | 122.2356 | 122.2539 | 62.1611 | -122.3767 | 122.1218 | 122.2951 | 122.0556 | 62.2379 | -122.5496
655.4688 | 122.5388 | -62.2055 | 60.2371 | 1.4211e-13 | -0.0080727 | -0.012222 | 0.015729 | -0.036797 | 0.030381 | -0.00083919 | -0.013872 | 0.010448 | 0.035136 | -0.0047991 | 0.038838 | -62.1277 | 0.010564 | -62.2089 | 60.1435 | 60.0987 | 60.1079 | -62.2082 | -62.1641 | 0.096512 | -62.2719 | 59.9758 | 60.1445 | 59.9096 | -62.3674 | -0.002716 | -0.093654 | 0.077829 | -0.003424 | -0.000708 | -0.13838 | -0.1292 | -0.16187 | -0.26132 | 0.041409 | -0.066356 | 0.095519 | -0.092629 | -0.32751 | 122.349 | 122.3042 | 122.3134 | 62.2161 | -122.4453 | 122.1813 | 122.35 | 122.1151 | 62.302 | -122.6045
657.3906 | 122.5525 | -62.2055 | 60.2554 | 1.4211e-13 | -0.0082863 | -0.012009 | 0.016157 | -0.037011 | 0.030381 | -0.00083919 | -0.013872 | 0.010448 | 0.034709 | -0.0050127 | 0.039052 | -62.1368 | 0.019721 | -62.2089 | 60.148 | 60.1033 | 60.1125 | -62.2082 | -62.1595 | 0.082776 | -62.2673 | 59.9804 | 60.1399 | 59.9233 | -62.3674 | -0.002716 | -0.10739 | 0.068672 | -0.003424 | -0.000708 | -0.15211 | -0.14293 | -0.16187 | -0.27505 | 0.045988 | -0.061777 | 0.1001 | -0.11552 | -0.33209 | 122.3536 | 122.3088 | 122.318 | 62.2252 | -122.4637 | 122.1859 | 122.3454 | 122.1288 | 62.2883 | -122.6228
659.4062 | 122.5525 | -62.2101 | 60.2142 | 1.4211e-13 | -0.0080727 | -0.012222 | 0.015943 | -0.037011 | 0.030381 | -0.0084697 | -0.014085 | 0.010021 | 0.034923 | -0.0050127 | 0.039052 | -62.1368 | 0.015142 | -62.2089 | 60.1435 | 60.0987 | 60.1079 | -62.2036 | -62.1733 | 0.087354 | -62.2764 | 59.9712 | 60.1445 | 59.905 | -62.3903 | 0.006441 | -0.070765 | 0.07325 | 0.001154 | -0.005287 | -0.11549 | -0.10631 | -0.18019 | -0.24301 | 0.03683 | -0.066356 | 0.11383 | -0.06974 | -0.3092 | 122.3536 | 122.3088 | 122.318 | 62.2252 | -122.4179 | 122.1813 | 122.3546 | 122.1151 | 62.2974 | -122.6045
661.3438 | 122.6624 | -62.1918 | 60.1456 | 1.4211e-13 | -0.0082863 | -0.011795 | 0.015943 | -0.037011 | 0.030381 | 0.014421 | -0.014299 | 0.010662 | 0.034709 | -0.0052265 | 0.039052 | -62.1323 | 0.0243 | -62.2089 | 60.1435 | 60.0987 | 60.1033 | -62.2036 | -62.1641 | 0.078197 | -62.2764 | 59.9758 | 60.1353 | 59.9142 | -62.372 | -0.01187 | -0.002101 | 0.059518 | -0.017157 | -0.005287 | -0.046825 | -0.042224 | -0.18019 | -0.16977 | 0.027676 | -0.084667 | 0.09552 | -0.010233 | -0.23138 | 122.3352 | 122.2905 | 122.2951 | 62.2161 | -122.3492 | 122.1676 | 122.3271 | 122.106 | 62.27 | -122.5175
663.2188 | 122.6807 | -62.1872 | 60.1593 | 1.4211e-13 | -0.0080727 | -0.012009 | 0.015729 | -0.037011 | 0.030808 | 0.0067908 | -0.014085 | 0.010448 | 0.034709 | -0.0050127 | 0.039052 | -62.1323 | 0.019721 | -62.2044 | 60.1435 | 60.0942 | 60.1171 | -62.1991 | -62.1595 | 0.087354 | -62.2673 | 59.9712 | 60.1445 | 59.9096 | -62.3765 | -0.011868 | -0.015834 | 0.054941 | -0.017156 | -0.005288 | -0.065137 | -0.042222 | -0.18934 | -0.18808 | 0.027678 | -0.080087 | 0.10926 | -0.014809 | -0.24969 | 122.3307 | 122.2814 | 122.3043 | 62.2069 | -122.3584 | 122.1584 | 122.3317 | 122.0968 | 62.2745 | -122.5358
664.9375 | 122.612 | -62.1689 | 60.1959 | 1.4211e-13 | -0.0080727 | -0.012009 | 0.015729 | -0.037011 | 0.030594 | -0.00083919 | -0.014299 | 0.010234 | 0.035136 | -0.0047991 | 0.039265 | -62.1323 | 0.015142 | -62.2044 | 60.1435 | 60.0896 | 60.1079 | -62.2128 | -62.1687 | 0.082776 | -62.2764 | 59.9804 | 60.1308 | 59.905 | -62.3765 | -0.043916 | -0.052455 | 0.03663 | -0.035467 | 0.008449 | -0.10634 | -0.088 | -0.20765 | -0.21554 | 0.000209 | -0.10756 | 0.1001 | -0.065165 | -0.29089 | 122.3124 | 122.2585 | 122.2768 | 62.184 | -122.4087 | 122.1493 | 122.2996 | 122.0739 | 62.2517 | -122.5725
666.7188 | 122.58 | -62.1689 | 60.2325 | 1.4211e-13 | -0.0082863 | -0.011795 | 0.015729 | -0.036797 | 0.030381 | -0.00083919 | -0.013872 | 0.010662 | 0.034923 | -0.0050127 | 0.039052 | -62.1323 | 0.015142 | -62.2089 | 60.1435 | 60.1033 | 60.1079 | -62.2036 | -62.1641 | 0.078197 | -62.2764 | 59.9712 | 60.1399 | 59.9142 | -62.372 | -0.034758 | -0.089076 | 0.03663 | -0.040045 | -0.005287 | -0.12922 | -0.12462 | -0.20307 | -0.26132 | 0.004788 | -0.10756 | 0.09552 | -0.092629 | -0.31836 | 122.3124 | 122.2722 | 122.2768 | 62.184 | -122.4362 | 122.1401 | 122.3088 | 122.0831 | 62.2471 | -122.6045
668.5625 | 122.5342 | -62.1918 | 60.2463 | 1.4211e-13 | -0.0080727 | -0.011795 | 0.015943 | -0.037011 | 0.030381 | -0.0084697 | -0.014726 | 0.010448 | 0.034709 | -0.0050127 | 0.039052 | -62.1323 | 0.019721 | -62.1998 | 60.1343 | 60.1079 | 60.1079 | -62.1991 | -62.1595 | 0.082776 | -62.281 | 59.9758 | 60.1399 | 59.9096 | -62.372 | -0.007291 | -0.11196 | 0.059518 | -0.008 | -0.000709 | -0.13838 | -0.13835 | -0.18019 | -0.27047 | 0.032255 | -0.089246 | 0.090941 | -0.10636 | -0.33667 | 122.3261 | 122.2997 | 122.2997 | 62.2115 | -122.4453 | 122.1676 | 122.3317 | 122.1014 | 62.2745 | -122.6182
671.3906 | 122.5204 | -62.178 | 60.228 | 1.4211e-13 | -0.0080727 | -0.012009 | 0.015516 | -0.037224 | 0.030594 | -0.0084697 | -0.014085 | 0.010234 | 0.034923 | -0.0050127 | 0.039052 | -62.1277 | 0.015142 | -62.2089 | 60.1435 | 60.0942 | 60.1079 | -62.2174 | -62.1595 | 0.087354 | -62.2719 | 59.9758 | 60.1445 | 59.9233 | -62.372 | -0.039339 | -0.084498 | 0.050364 | -0.030889 | 0.00845 | -0.1338 | -0.12004 | -0.19392 | -0.25216 | 0.018523 | -0.093821 | 0.1001 | -0.083473 | -0.30462 | 122.3215 | 122.2722 | 122.286 | 62.1932 | -122.4453 | 122.1538 | 122.3225 | 122.1014 | 62.2654 | -122.5999
673.75 | 122.6578 | -62.1552 | 60.1776 | 1.4211e-13 | -0.0084999 | -0.011795 | 0.015943 | -0.037224 | 0.030594 | -0.00083919 | -0.014513 | 0.010234 | 0.034709 | -0.0050127 | 0.039265 | -62.1231 | 0.015142 | -62.2135 | 60.1435 | 60.0987 | 60.1217 | -62.2036 | -62.1549 | 0.082776 | -62.2673 | 59.9758 | 60.1353 | 59.9142 | -62.3765 | -0.048491 | -0.034144 | 0.032054 | -0.058356 | -0.009865 | -0.078868 | -0.055953 | -0.22139 | -0.20181 | 0.000212 | -0.11213 | 0.10926 | -0.042276 | -0.26343 | 122.2986 | 122.2539 | 122.2768 | 62.1703 | -122.3813 | 122.131 | 122.2905 | 122.0693 | 62.2379 | -122.5541
675.6719 | 122.6669 | -62.1735 | 60.173 | 1.4211e-13 | -0.0087137 | -0.012222 | 0.016157 | -0.037224 | 0.030594 | -0.00083919 | -0.014085 | 0.010662 | 0.034923 | -0.0047991 | 0.039265 | -62.1414 | 0.015142 | -62.2044 | 60.1389 | 60.1033 | 60.1079 | -62.2082 | -62.1641 | 0.091933 | -62.2673 | 59.9804 | 60.1399 | 59.9096 | -62.3811 | -0.034759 | -0.034145 | 0.032051 | -0.030889 | 0.00387 | -0.069712 | -0.065112 | -0.20766 | -0.19265 | 0.009366 | -0.09382 | 0.11384 | -0.03312 | -0.26343 | 122.3124 | 122.2768 | 122.2814 | 62.1886 | -122.3813 | 122.1538 | 122.3134 | 122.0831 | 62.2654 | -122.5542
677.3906 | 122.5708 | -62.2147 | 60.1959 | 1.4211e-13 | -0.0080727 | -0.012009 | 0.015729 | -0.036797 | 0.030381 | -0.0084697 | -0.014085 | 0.010234 | 0.034709 | -0.0047991 | 0.039052 | -62.1277 | 0.010564 | -62.2135 | 60.1389 | 60.0987 | 60.1217 | -62.1991 | -62.1641 | 0.078197 | -62.2673 | 59.9758 | 60.1353 | 59.9142 | -62.372 | 0.015598 | -0.057033 | 0.086985 | 0.001154 | -0.014444 | -0.097179 | -0.074264 | -0.1573 | -0.22012 | 0.050565 | -0.052621 | 0.10468 | -0.060587 | -0.28174 | 122.3536 | 122.3134 | 122.3363 | 62.2252 | -122.395 | 122.1905 | 122.35 | 122.1288 | 62.2929 | -122.5679
679.2812 | 122.5433 | -62.1964 | 60.2417 | 1.4211e-13 | -0.0084999 | -0.012009 | 0.015729 | -0.036583 | 0.030381 | 0.0067908 | -0.014085 | 0.010448 | 0.034923 | -0.0050127 | 0.039265 | -62.1231 | 0.010564 | -62.2044 | 60.1389 | 60.1079 | 60.1125 | -62.2036 | -62.1595 | 0.087354 | -62.2627 | 59.9758 | 60.1399 | 59.9188 | -62.372 | -0.007292 | -0.10281 | 0.073253 | -0.008001 | -0.000709 | -0.1338 | -0.1292 | -0.17561 | -0.2659 | 0.036833 | -0.066353 | 0.10926 | -0.10178 | -0.32293 | 122.3352 | 122.3043 | 122.3089 | 62.2069 | -122.4453 | 122.1722 | 122.3363 | 122.1151 | 62.2837 | -122.6137
681.0469 | 122.5479 | -62.2055 | 60.1868 | 1.4211e-13 | -0.0082863 | -0.012222 | 0.016157 | -0.037224 | 0.030381 | -0.00083919 | -0.014513 | 0.010448 | 0.034923 | -0.0052265 | 0.039052 | -62.1231 | 0.019721 | -62.1998 | 60.1435 | 60.1033 | 60.1125 | -62.2036 | -62.1641 | 0.078197 | -62.2719 | 59.985 | 60.1399 | 59.9142 | -62.3903 | 0.001863 | -0.0433 | 0.082408 | 0.005733 | 0.00387 | -0.083445 | -0.074266 | -0.18477 | -0.20181 | 0.041409 | -0.066356 | 0.11841 | -0.046853 | -0.27258 | 122.349 | 122.3088 | 122.318 | 62.2252 | -122.3904 | 122.1905 | 122.3454 | 122.1197 | 62.2837 | -122.577
682.8438 | 122.644 | -62.1918 | 60.1273 | 1.4211e-13 | -0.0080727 | -0.012009 | 0.015943 | -0.037011 | 0.030594 | -0.00083919 | -0.013872 | 0.010448 | 0.035136 | -0.0045853 | 0.039265 | -62.1323 | 0.010564 | -62.1998 | 60.1435 | 60.0987 | 60.1171 | -62.1991 | -62.1595 | 0.087354 | -62.2719 | 59.9758 | 60.1353 | 59.9096 | -62.3628 | -0.007291 | 0.01621 | 0.059518 | -0.008 | -0.000709 | -0.028514 | -0.010178 | -0.17103 | -0.15145 | 0.032255 | -0.080089 | 0.090941 | 0.008078 | -0.21765 | 122.3352 | 122.2905 | 122.3089 | 62.2023 | -122.3263 | 122.1676 | 122.3271 | 122.1014 | 62.2791 | -122.4901
684.7188 | 122.5113 | -62.2284 | 60.2142 | 1.4211e-13 | -0.0082863 | -0.012222 | 0.015516 | -0.037224 | 0.030381 | 0.014421 | -0.014299 | 0.010234 | 0.034923 | -0.0050127 | 0.038838 | -62.1323 | 0.019721 | -62.2044 | 60.148 | 60.1033 | 60.1079 | -62.1991 | -62.1595 | 0.087354 | -62.2673 | 59.9804 | 60.1445 | 59.905 | -62.372 | 0.029331 | -0.066186 | 0.09614 | 0.024043 | -0.005288 | -0.11091 | -0.10631 | -0.14356 | -0.23385 | 0.068877 | -0.038888 | 0.10468 | -0.06974 | -0.3092 | 122.3764 | 122.3317 | 122.3363 | 62.2481 | -122.4133 | 122.2088 | 122.3729 | 122.1334 | 62.3157 | -122.5862
687.2969 | 122.5754 | -62.1872 | 60.2097 | 1.4211e-13 | -0.0084999 | -0.012009 | 0.015516 | -0.037224 | 0.030594 | -0.0084697 | -0.014085 | 0.010448 | 0.034709 | -0.0050127 | 0.039052 | -62.1323 | 0.010564 | -62.1998 | 60.1389 | 60.1033 | 60.1125 | -62.1991 | -62.1641 | 0.073618 | -62.2719 | 59.9758 | 60.1491 | 59.9142 | -62.3765 | -0.011868 | -0.070766 | 0.054941 | -0.012577 | -0.000709 | -0.10633 | -0.097154 | -0.18934 | -0.23385 | 0.023099 | -0.084666 | 0.10468 | -0.060584 | -0.29547 | 122.3261 | 122.2905 | 122.2997 | 62.1978 | -122.4087 | 122.163 | 122.3363 | 122.1014 | 62.2608 | -122.5862
689.0781 | 122.525 | -62.1918 | 60.2371 | 1.4211e-13 | -0.0084999 | -0.012222 | 0.015943 | -0.037224 | 0.030594 | -0.00083919 | -0.014299 | 0.010448 | 0.035136 | -0.0050127 | 0.039265 | -62.1323 | 0.019721 | -62.2089 | 60.148 | 60.1079 | 60.1171 | -62.2128 | -62.1595 | 0.087354 | -62.2673 | 59.985 | 60.1445 | 59.9142 | -62.3765 | -0.021028 | -0.089075 | 0.059518 | -0.017157 | 0.003871 | -0.12922 | -0.12004 | -0.18477 | -0.25216 | 0.032255 | -0.07551 | 0.10926 | -0.092629 | -0.32294 | 122.3398 | 122.2997 | 122.3089 | 62.2115 | -122.4499 | 122.1767 | 122.3363 | 122.106 | 62.2791 | -122.6137
690.9688 | 122.5525 | -62.178 | 60.2371 | 1.4211e-13 | -0.0082863 | -0.011795 | 0.015729 | -0.037011 | 0.030594 | -0.00083919 | -0.014299 | 0.010234 | 0.034709 | -0.0050127 | 0.039052 | -62.1277 | 0.019721 | -62.2089 | 60.1435 | 60.1033 | 60.1125 | -62.1991 | -62.1595 | 0.078197 | -62.2673 | 59.9804 | 60.1399 | 59.905 | -62.3674 | -0.021023 | -0.093654 | 0.050364 | -0.030889 | -0.009866 | -0.1338 | -0.12462 | -0.18934 | -0.25674 | 0.018523 | -0.089242 | 0.1001 | -0.097207 | -0.33209 | 122.3215 | 122.2814 | 122.2905 | 62.1978 | -122.4362 | 122.1584 | 122.318 | 122.0831 | 62.2562 | -122.6045
692.8125 | 122.5525 | -62.2055 | 60.1959 | 1.4211e-13 | -0.0082863 | -0.011795 | 0.015516 | -0.036797 | 0.030594 | -0.00083919 | -0.013872 | 0.010234 | 0.034709 | -0.0045853 | 0.039052 | -62.1323 | 0.019721 | -62.2044 | 60.148 | 60.0987 | 60.1079 | -62.1991 | -62.1549 | 0.078197 | -62.2719 | 59.9758 | 60.1491 | 59.9279 | -62.3674 | 0.006442 | -0.047876 | 0.073251 | 0.001154 | -0.005288 | -0.097179 | -0.088 | -0.16187 | -0.22012 | 0.050566 | -0.066356 | 0.095519 | -0.046851 | -0.268 | 122.3536 | 122.3042 | 122.3134 | 62.2252 | -122.395 | 122.1813 | 122.3546 | 122.1334 | 62.2837 | -122.5633
694.5312 | 122.5388 | -62.2192 | 60.2005 | 1.4211e-13 | -0.0087137 | -0.012009 | 0.015729 | -0.037011 | 0.030594 | -0.00083919 | -0.014299 | 0.010234 | 0.034923 | -0.0047991 | 0.038838 | -62.1277 | 0.005985 | -62.1998 | 60.148 | 60.1033 | 60.1171 | -62.2082 | -62.1595 | 0.082776 | -62.2673 | 59.9804 | 60.1399 | 59.9188 | -62.372 | 0.011017 | -0.052453 | 0.091562 | 0.019466 | 0.008449 | -0.097177 | -0.08342 | -0.15272 | -0.22012 | 0.059721 | -0.048044 | 0.10468 | -0.060585 | -0.28173 | 122.3673 | 122.3226 | 122.3363 | 62.2252 | -122.4087 | 122.1996 | 122.3592 | 122.138 | 62.302 | -122.5725
696.25 | 122.5433 | -62.2009 | 60.1822 | 1.4211e-13 | -0.0082863 | -0.012009 | 0.015729 | -0.037011 | 0.030594 | -0.00083919 | -0.014299 | 0.010448 | 0.035136 | -0.0047991 | 0.039265 | -62.1277 | 0.015142 | -62.2044 | 60.1389 | 60.0987 | 60.1171 | -62.1991 | -62.1549 | 0.078197 | -62.2627 | 59.9758 | 60.1445 | 59.9142 | -62.3765 | 0.001865 | -0.0433 | 0.073252 | -0.003423 | -0.005288 | -0.083446 | -0.06511 | -0.17561 | -0.20639 | 0.045989 | -0.061775 | 0.11383 | -0.037697 | -0.268 | 122.3398 | 122.2997 | 122.318 | 62.2161 | -122.3813 | 122.1767 | 122.3454 | 122.1151 | 62.2791 | -122.5587
697.9844 | 122.6532 | -62.1918 | 60.1273 | 1.4211e-13 | -0.0078589 | -0.011795 | 0.015943 | -0.037011 | 0.030167 | 0.0067908 | -0.014085 | 0.010448 | 0.034709 | -0.0050127 | 0.039052 | -62.1277 | 0.015142 | -62.2044 | 60.1435 | 60.1033 | 60.1171 | -62.1945 | -62.1641 | 0.082776 | -62.2627 | 59.9712 | 60.1445 | 59.9188 | -62.3674 | -0.002712 | 0.01621 | 0.064096 | -0.012579 | -0.009867 | -0.023935 | -0.010178 | -0.17561 | -0.15603 | 0.027676 | -0.070931 | 0.10468 | 0.017235 | -0.20849 | 122.3352 | 122.2951 | 122.3089 | 62.2069 | -122.3217 | 122.163 | 122.3363 | 122.1105 | 62.2745 | -122.4946
699.8438 | 122.6166 | -62.1918 | 60.173 | 1.4211e-13 | -0.0087137 | -0.012222 | 0.015516 | -0.037224 | 0.030594 | 0.014421 | -0.014299 | 0.010448 | 0.034923 | -0.0047991 | 0.039265 | -62.1277 | 0.019721 | -62.1906 | 60.1435 | 60.1033 | 60.1125 | -62.2036 | -62.1549 | 0.087354 | -62.2535 | 59.9804 | 60.1537 | 59.9188 | -62.3674 | -0.01187 | -0.029567 | 0.064096 | 0.001156 | 0.013026 | -0.069712 | -0.060533 | -0.17561 | -0.19265 | 0.036833 | -0.061774 | 0.11383 | -0.019384 | -0.25427 | 122.3352 | 122.2951 | 122.3043 | 62.2115 | -122.3767 | 122.1722 | 122.3454 | 122.1105 | 62.2791 | -122.5404
701.6406 | 122.6349 | -62.1643 | 60.1501 | 1.4211e-13 | -0.0082863 | -0.011581 | 0.016157 | -0.037224 | 0.030594 | 0.0067908 | -0.014085 | 0.010448 | 0.034496 | -0.0045853 | 0.038838 | -62.1277 | 0.019721 | -62.2044 | 60.148 | 60.0942 | 60.1125 | -62.1991 | -62.1595 | 0.087354 | -62.2627 | 59.9804 | 60.1445 | 59.9188 | -62.3765 | -0.034756 | -0.002099 | 0.036631 | -0.040044 | -0.005288 | -0.055981 | -0.037644 | -0.21223 | -0.16976 | 0.00479 | -0.098396 | 0.11383 | -0.005653 | -0.23138 | 122.3124 | 122.2585 | 122.2768 | 62.184 | -122.3492 | 122.1447 | 122.3088 | 122.0831 | 62.2517 | -122.5267
703.375 | 122.5891 | -62.1735 | 60.2051 | 1.4211e-13 | -0.0084999 | -0.011795 | 0.015943 | -0.036797 | 0.030381 | -0.00083919 | -0.014299 | 0.010234 | 0.034923 | -0.0050127 | 0.039052 | -62.1231 | 0.015142 | -62.1998 | 60.1389 | 60.1033 | 60.1125 | -62.1991 | -62.1504 | 0.087354 | -62.2581 | 59.985 | 60.1445 | 59.9188 | -62.3674 | -0.025601 | -0.066188 | 0.050365 | -0.02631 | -0.000709 | -0.10175 | -0.092576 | -0.19392 | -0.22012 | 0.023102 | -0.084662 | 0.10926 | -0.060585 | -0.28631 | 122.3124 | 122.2768 | 122.286 | 62.1886 | -122.4041 | 122.1584 | 122.318 | 122.0922 | 62.2608 | -122.5725
705.1562 | 122.5159 | -62.1826 | 60.2188 | 1.4211e-13 | -0.0082863 | -0.011581 | 0.015943 | -0.037224 | 0.029953 | 0.0067908 | -0.013872 | 0.010234 | 0.034923 | -0.0047991 | 0.039265 | -62.1277 | 0.015142 | -62.2044 | 60.148 | 60.1033 | 60.1171 | -62.1899 | -62.1549 | 0.087354 | -62.2673 | 59.9804 | 60.1537 | 59.9142 | -62.3765 | -0.007288 | -0.070764 | 0.054941 | -0.021734 | -0.014446 | -0.11549 | -0.10173 | -0.19392 | -0.23843 | 0.027678 | -0.084665 | 0.10926 | -0.06516 | -0.30463 | 122.3307 | 122.2859 | 122.2997 | 62.1978 | -122.4087 | 122.163 | 122.3363 | 122.0968 | 62.27 | -122.5953
706.9375 | 122.5342 | -62.2192 | 60.1868 | 1.4211e-13 | -0.0082863 | -0.012009 | 0.015729 | -0.037011 | 0.030381 | 0.0067908 | -0.014085 | 0.009807 | 0.034923 | -0.0045853 | 0.039052 | -62.1323 | 0.015142 | -62.1998 | 60.1435 | 60.1033 | 60.1217 | -62.1945 | -62.1595 | 0.082776 | -62.2627 | 59.9804 | 60.1491 | 59.9188 | -62.3628 | 0.024754 | -0.0433 | 0.086984 | 0.019466 | -0.005288 | -0.083445 | -0.065109 | -0.14356 | -0.20639 | 0.059721 | -0.043465 | 0.1001 | -0.037696 | -0.268 | 122.3627 | 122.3226 | 122.3409 | 62.2344 | -122.3813 | 122.1996 | 122.3683 | 122.138 | 62.302 | -122.5496
708.6562 | 122.525 | -62.1689 | 60.2463 | 1.4211e-13 | -0.0087137 | -0.012009 | 0.016157 | -0.037011 | 0.030381 | -0.0084697 | -0.014085 | 0.010448 | 0.034709 | -0.0047991 | 0.039265 | -62.1231 | 0.010564 | -62.1952 | 60.1435 | 60.1079 | 60.1125 | -62.1899 | -62.1549 | 0.073618 | -62.2627 | 59.985 | 60.1445 | 59.9142 | -62.3674 | -0.021021 | -0.10281 | 0.045787 | -0.02631 | -0.005289 | -0.13838 | -0.13377 | -0.1985 | -0.26132 | 0.013945 | -0.093819 | 0.10468 | -0.10178 | -0.33209 | 122.3124 | 122.2768 | 122.2814 | 62.1794 | -122.4362 | 122.1538 | 122.3134 | 122.0831 | 62.2425 | -122.6137
710.4531 | 122.5342 | -62.178 | 60.2142 | 1.4211e-13 | -0.0084999 | -0.012009 | 0.016157 | -0.037011 | 0.030167 | -0.0084697 | -0.014085 | 0.010448 | 0.034709 | -0.0047991 | 0.039265 | -62.1231 | 0.010564 | -62.1998 | 60.148 | 60.1079 | 60.1217 | -62.1899 | -62.1595 | 0.073618 | -62.2535 | 59.9712 | 60.1399 | 59.9096 | -62.3674 | -0.011865 | -0.066186 | 0.054943 | -0.021732 | -0.009867 | -0.10633 | -0.092574 | -0.18934 | -0.24301 | 0.018523 | -0.075506 | 0.11383 | -0.074318 | -0.30463 | 122.3261 | 122.2859 | 122.2997 | 62.1886 | -122.4041 | 122.1493 | 122.318 | 122.0876 | 62.2517 | -122.5816
712.2188 | 122.5983 | -62.2009 | 60.1776 | 1.4211e-13 | -0.0082863 | -0.012009 | 0.015943 | -0.037224 | 0.030381 | -0.00083919 | -0.014299 | 0.010021 | 0.035136 | -0.0047991 | 0.039052 | -62.1231 | 0.015142 | -62.1998 | 60.1526 | 60.1079 | 60.1217 | -62.1991 | -62.1504 | 0.082776 | -62.2627 | 59.985 | 60.1491 | 59.9279 | -62.3674 | 0.001865 | -0.024987 | 0.077831 | 0.001156 | -0.000709 | -0.069711 | -0.055953 | -0.16645 | -0.19265 | 0.050568 | -0.061775 | 0.10468 | -0.02854 | -0.24969 | 122.3536 | 122.3088 | 122.3226 | 62.2161 | -122.3767 | 122.1859 | 122.35 | 122.1288 | 62.2837 | -122.545
714 | 122.6074 | -62.1918 | 60.1776 | 1.4211e-13 | -0.0082863 | -0.011795 | 0.015943 | -0.037224 | 0.030594 | 0.0067908 | -0.014299 | 0.010448 | 0.035136 | -0.0047991 | 0.039052 | -62.1231 | 0.010564 | -62.1998 | 60.1526 | 60.1171 | 60.1171 | -62.1991 | -62.1549 | 0.091933 | -62.2581 | 59.985 | 60.1491 | 59.9233 | -62.3628 | -0.007291 | -0.024987 | 0.068675 | -0.008 | -0.000709 | -0.060553 | -0.060532 | -0.17103 | -0.19265 | 0.036833 | -0.066352 | 0.10468 | -0.02854 | -0.25427 | 122.3444 | 122.3088 | 122.3089 | 62.2023 | -122.3767 | 122.1767 | 122.3408 | 122.1151 | 62.2837 | -122.5404
715.7969 | 122.5937 | -62.1597 | 60.2142 | 1.4211e-13 | -0.0082863 | -0.012009 | 0.015943 | -0.036797 | 0.030381 | -0.00083919 | -0.013872 | 0.010234 | 0.034923 | -0.0043717 | 0.039265 | -62.1231 | 0.010564 | -62.1952 | 60.1572 | 60.1079 | 60.1217 | -62.1991 | -62.1504 | 0.082776 | -62.2581 | 59.985 | 60.1491 | 59.9142 | -62.3628 | -0.039334 | -0.057029 | 0.036632 | -0.035465 | 0.003869 | -0.10633 | -0.092574 | -0.20307 | -0.22927 | 0.009369 | -0.098395 | 0.10468 | -0.065161 | -0.30005 | 122.3169 | 122.2676 | 122.2814 | 62.1703 | -122.4133 | 122.1447 | 122.3088 | 122.0739 | 62.2425 | -122.577
717.5781 | 122.6349 | -62.1689 | 60.1776 | 1.4211e-13 | -0.0087137 | -0.011795 | 0.016157 | -0.037224 | 0.030381 | 0.0067908 | -0.014085 | 0.010448 | 0.034709 | -0.0041581 | 0.039265 | -62.1094 | 0.010564 | -62.1952 | 60.1435 | 60.1079 | 60.1217 | -62.1899 | -62.1549 | 0.082776 | -62.2627 | 59.985 | 60.1491 | 59.9188 | -62.3628 | -0.021021 | -0.034144 | 0.059522 | -0.02631 | -0.005289 | -0.069711 | -0.055953 | -0.19392 | -0.19265 | 0.013945 | -0.093819 | 0.1001 | -0.02854 | -0.25885 | 122.3124 | 122.2768 | 122.2905 | 62.1794 | -122.3675 | 122.1538 | 122.318 | 122.0876 | 62.2517 | -122.5404
719.2812 | 122.5571 | -62.178 | 60.2097 | 1.4211e-13 | -0.0082863 | -0.011795 | 0.015516 | -0.037224 | 0.030594 | 0.0067908 | -0.014085 | 0.010448 | 0.035136 | -0.0045853 | 0.039052 | -62.1185 | 0.005985 | -62.1952 | 60.1435 | 60.1125 | 60.1262 | -62.1853 | -62.1504 | 0.091933 | -62.2627 | 59.985 | 60.1445 | 59.9142 | -62.3582 | -0.007287 | -0.066188 | 0.059521 | -0.017154 | -0.009867 | -0.097176 | -0.083418 | -0.18018 | -0.2247 | 0.02768 | -0.084663 | 0.09552 | -0.065163 | -0.29547 | 122.3215 | 122.2905 | 122.3043 | 62.184 | -122.395 | 122.163 | 122.3225 | 122.0922 | 62.27 | -122.5679
721.0781 | 122.612 | -62.1735 | 60.141 | 1.4211e-13 | -0.0082863 | -0.012222 | 0.015943 | -0.037438 | 0.030167 | -0.0084697 | -0.014299 | 0.010448 | 0.035136 | -0.0045853 | 0.039052 | -62.1139 | 0.010564 | -62.1952 | 60.148 | 60.1125 | 60.1217 | -62.1991 | -62.1504 | 0.087354 | -62.2581 | 59.9895 | 60.1537 | 59.9233 | -62.3674 | -0.025601 | 0.007056 | 0.059521 | -0.021732 | 0.003869 | -0.028511 | -0.019332 | -0.19392 | -0.15145 | 0.023102 | -0.084662 | 0.10926 | 0.01266 | -0.21765 | 122.3215 | 122.2859 | 122.2951 | 62.184 | -122.3401 | 122.163 | 122.3271 | 122.0968 | 62.2608 | -122.5084
722.875 | 122.5388 | -62.1826 | 60.228 | 1.4211e-13 | -0.0087137 | -0.011795 | 0.016157 | -0.037011 | 0.030381 | -0.0084697 | -0.014513 | 0.010448 | 0.034709 | -0.0043717 | 0.039052 | -62.1185 | 0.010564 | -62.1906 | 60.1526 | 60.1079 | 60.1171 | -62.1945 | -62.1504 | 0.082776 | -62.2581 | 59.9895 | 60.1537 | 59.9279 | -62.3765 | -0.011867 | -0.075341 | 0.064098 | -0.007999 | 0.003868 | -0.12007 | -0.11089 | -0.19392 | -0.23843 | 0.032257 | -0.075507 | 0.11841 | -0.074315 | -0.30004 | 122.3352 | 122.2905 | 122.2997 | 62.1932 | -122.4224 | 122.1722 | 122.3363 | 122.1105 | 62.2654 | -122.6045
724.5938 | 122.6486 | -62.1643 | 60.1959 | 1.4211e-13 | -0.0084999 | -0.011795 | 0.015943 | -0.037224 | 0.030594 | -0.023731 | -0.014299 | 0.010448 | 0.035136 | -0.0050127 | 0.038838 | -62.1139 | 0.019721 | -62.1952 | 60.1572 | 60.1171 | 60.1262 | -62.1945 | -62.1458 | 0.091933 | -62.2581 | 59.9895 | 60.1445 | 59.9188 | -62.3628 | -0.030177 | -0.038719 | 0.050366 | -0.030887 | -0.00071 | -0.078864 | -0.069685 | -0.1985 | -0.20638 | 0.018526 | -0.093817 | 0.10468 | -0.05143 | -0.27716 | 122.3215 | 122.2814 | 122.2905 | 62.184 | -122.3904 | 122.1538 | 122.3088 | 122.0831 | 62.2562 | -122.5587
726.3125 | 122.5388 | -62.1872 | 60.2417 | 1.4211e-13 | -0.0084999 | -0.012222 | 0.015729 | -0.037224 | 0.030594 | -0.00083919 | -0.014085 | 0.010448 | 0.034923 | -0.0045853 | 0.039265 | -62.1185 | 0.015142 | -62.186 | 60.1526 | 60.1125 | 60.1217 | -62.1899 | -62.1504 | 0.087354 | -62.2581 | 59.985 | 60.1537 | 59.9233 | -62.3628 | -0.00271 | -0.089074 | 0.068676 | 0.001158 | 0.003868 | -0.12922 | -0.12004 | -0.17561 | -0.25674 | 0.036835 | -0.070929 | 0.10468 | -0.088048 | -0.31836 | 122.3398 | 122.2997 | 122.3089 | 62.2023 | -122.4316 | 122.1722 | 122.3408 | 122.1105 | 62.2745 | -122.6045
728.0156 | 122.6532 | -62.1643 | 60.1501 | 1.4211e-13 | -0.0087137 | -0.012009 | 0.015943 | -0.037011 | 0.030381 | -0.00083919 | -0.014513 | 0.010448 | 0.034923 | -0.0043717 | 0.038838 | -62.1185 | 0.005985 | -62.186 | 60.1572 | 60.1079 | 60.1262 | -62.1853 | -62.1504 | 0.078197 | -62.2535 | 59.985 | 60.1491 | 59.9233 | -62.3628 | -0.02102 | 0.007058 | 0.045788 | -0.02173 | -0.00071 | -0.042245 | -0.023908 | -0.1985 | -0.16519 | 0.013947 | -0.089239 | 0.10926 | -0.001074 | -0.2268 | 122.3215 | 122.2722 | 122.2905 | 62.1703 | -122.3355 | 122.1493 | 122.3134 | 122.0876 | 62.2425 | -122.5129
729.8125 | 122.6532 | -62.1506 | 60.1639 | 1.4211e-13 | -0.0084999 | -0.011795 | 0.015516 | -0.036797 | 0.030594 | -0.00083919 | -0.013872 | 0.010448 | 0.034496 | -0.0041581 | 0.039052 | -62.1185 | 0.010564 | -62.186 | 60.1572 | 60.1125 | 60.1262 | -62.1945 | -62.1412 | 0.087354 | -62.249 | 59.9895 | 60.1537 | 59.9325 | -62.3582 | -0.04391 | -0.006675 | 0.032055 | -0.035463 | 0.008447 | -0.051399 | -0.037641 | -0.20765 | -0.17434 | 0.009371 | -0.098393 | 0.10926 | -0.010228 | -0.23138 | 122.3078 | 122.2631 | 122.2768 | 62.1611 | -122.3584 | 122.1401 | 122.3042 | 122.0831 | 62.2379 | -122.5221
731.6094 | 122.6166 | -62.1643 | 60.1685 | 1.4211e-13 | -0.0087137 | -0.011795 | 0.015943 | -0.037011 | 0.030594 | -0.0084697 | -0.014513 | 0.010021 | 0.034923 | -0.0045853 | 0.038838 | -62.1139 | 0.019721 | -62.186 | 60.1572 | 60.1216 | 60.1217 | -62.1899 | -62.1412 | 0.082776 | -62.249 | 59.9941 | 60.1628 | 59.9462 | -62.3582 | -0.025598 | -0.011253 | 0.050366 | -0.02173 | 0.003868 | -0.046819 | -0.046798 | -0.19392 | -0.17434 | 0.023104 | -0.08466 | 0.10926 | -0.005649 | -0.22222 | 122.3215 | 122.2859 | 122.286 | 62.184 | -122.3584 | 122.1584 | 122.3271 | 122.1105 | 62.2471 | -122.5267
733.4062 | 122.5159 | -62.146 | 60.2371 | 1.4211e-13 | -0.0080727 | -0.012009 | 0.016157 | -0.037438 | 0.030381 | 0.0067908 | -0.014085 | 0.010448 | 0.034709 | -0.0043717 | 0.038838 | -62.1139 | 0.010564 | -62.186 | 60.1526 | 60.1171 | 60.1217 | -62.1853 | -62.1412 | 0.087354 | -62.2444 | 59.985 | 60.1537 | 59.9188 | -62.3536 | -0.039331 | -0.084497 | 0.032055 | -0.040041 | -0.00071 | -0.12006 | -0.11546 | -0.20765 | -0.25216 | 0.004793 | -0.098392 | 0.10926 | -0.083471 | -0.31836 | 122.2986 | 122.2631 | 122.2677 | 62.1566 | -122.4224 | 122.131 | 122.2996 | 122.0648 | 62.2333 | -122.5908
735.1875 | 122.5021 | -62.1918 | 60.2234 | 1.4211e-13 | -0.0080727 | -0.011795 | 0.015943 | -0.037224 | 0.030594 | -0.00083919 | -0.014513 | 0.010234 | 0.034923 | -0.0045853 | 0.038838 | -62.1094 | 0.010564 | -62.186 | 60.1572 | 60.1171 | 60.1217 | -62.1762 | -62.1412 | 0.087354 | -62.2398 | 59.9895 | 60.1582 | 59.9233 | -62.3628 | 0.015603 | -0.066185 | 0.08241 | 0.005735 | -0.009868 | -0.10633 | -0.10173 | -0.17103 | -0.23385 | 0.050569 | -0.048038 | 0.12299 | -0.06516 | -0.30005 | 122.349 | 122.3088 | 122.3134 | 62.2023 | -122.3996 | 122.1813 | 122.35 | 122.1151 | 62.2791 | -122.5862
736.9688 | 122.5479 | -62.1597 | 60.2554 | 1.4211e-13 | -0.0087137 | -0.011795 | 0.015943 | -0.037438 | 0.029953 | 0.014421 | -0.014299 | 0.010234 | 0.035136 | -0.0043717 | 0.038838 | -62.1002 | 0.005985 | -62.1815 | 60.1618 | 60.1171 | 60.1308 | -62.1899 | -62.1458 | 0.087354 | -62.2535 | 59.9895 | 60.1582 | 59.9279 | -62.3536 | -0.030176 | -0.09365 | 0.059524 | -0.02173 | 0.008446 | -0.13837 | -0.12462 | -0.19392 | -0.26589 | 0.013948 | -0.093817 | 0.1001 | -0.097203 | -0.32751 | 122.3215 | 122.2768 | 122.2905 | 62.1657 | -122.4453 | 122.1493 | 122.318 | 122.0877 | 62.2471 | -122.6091
738.7031 | 122.6532 | -62.1277 | 60.1776 | 1.4211e-13 | -0.0087137 | -0.011795 | 0.015516 | -0.037224 | 0.030167 | 0.0067908 | -0.014726 | 0.010021 | 0.034496 | -0.0043717 | 0.039052 | -62.1094 | 0.005985 | -62.1815 | 60.1618 | 60.1125 | 60.1308 | -62.1807 | -62.1366 | 0.087354 | -62.249 | 59.9987 | 60.1537 | 59.9325 | -62.3536 | -0.053062 | -0.01583 | 0.018324 | -0.053773 | -0.000711 | -0.065132 | -0.046796 | -0.22596 | -0.17892 | -0.008938 | -0.12128 | 0.10468 | -0.023961 | -0.24511 | 122.2895 | 122.2402 | 122.2585 | 62.1337 | -122.3584 | 122.1264 | 122.2813 | 122.0602 | 62.215 | -122.5313
740.5 | 122.644 | -62.178 | 60.1501 | 1.4211e-13 | -0.0082863 | -0.011795 | 0.015729 | -0.037224 | 0.030594 | 0.014421 | -0.014299 | 0.010021 | 0.034923 | -0.0047991 | 0.039052 | -62.1048 | 0.005985 | -62.1769 | 60.1664 | 60.1262 | 60.1354 | -62.1807 | -62.1366 | 0.091933 | -62.2444 | 60.0079 | 60.1674 | 59.9325 | -62.3491 | -0.002708 | 0.016214 | 0.073256 | 0.001159 | 0.003867 | -0.023929 | -0.014751 | -0.17103 | -0.14229 | 0.041416 | -0.066348 | 0.10468 | 0.01724 | -0.21765 | 122.3444 | 122.3043 | 122.3134 | 62.184 | -122.3309 | 122.1859 | 122.3454 | 122.1105 | 62.27 | -122.4992
742.2969 | 122.6532 | -62.1552 | 60.1685 | 1.4211e-13 | -0.0084999 | -0.012222 | 0.015729 | -0.037224 | 0.030594 | -0.00083919 | -0.014513 | 0.010021 | 0.034923 | -0.0043717 | 0.039052 | -62.1094 | 0.010564 | -62.1815 | 60.1618 | 60.1308 | 60.1537 | -62.1762 | -62.1366 | 0.082776 | -62.249 | 59.9941 | 60.1628 | 59.9371 | -62.3582 | -0.021018 | -0.006675 | 0.045789 | -0.026308 | -0.00529 | -0.037661 | -0.014748 | -0.20307 | -0.17434 | 0.018527 | -0.093816 | 0.10926 | -0.005649 | -0.23138 | 122.3169 | 122.2859 | 122.3089 | 62.1657 | -122.3446 | 122.1493 | 122.318 | 122.0922 | 62.2379 | -122.5267
744.0781 | 122.5204 | -62.1414 | 60.2554 | 1.4211e-13 | -0.0084999 | -0.012222 | 0.015943 | -0.037224 | 0.030167 | 0.0067908 | -0.014085 | 0.010448 | 0.034923 | -0.0043717 | 0.039052 | -62.1002 | 0.010564 | -62.1723 | 60.1664 | 60.1216 | 60.1308 | -62.1716 | -62.1366 | 0.087354 | -62.249 | 60.0033 | 60.1628 | 59.9279 | -62.3445 | -0.030172 | -0.089072 | 0.041213 | -0.030885 | -0.000713 | -0.13379 | -0.12462 | -0.20307 | -0.25216 | 0.004794 | -0.10755 | 0.095519 | -0.092624 | -0.32751 | 122.3078 | 122.2631 | 122.2722 | 62.152 | -122.427 | 122.1447 | 122.3042 | 122.0693 | 62.2288 | -122.5999
745.875 | 122.5204 | -62.146 | 60.2417 | 1.4211e-13 | -0.0084999 | -0.012009 | 0.015729 | -0.037438 | 0.030167 | 0.0067908 | -0.014299 | 0.010448 | 0.035136 | -0.0041581 | 0.039265 | -62.0956 | 0.015142 | -62.1723 | 60.1618 | 60.1262 | 60.14 | -62.1762 | -62.132 | 0.078197 | -62.2352 | 60.0033 | 60.1674 | 59.9279 | -62.3491 | -0.030173 | -0.079917 | 0.050369 | -0.026307 | 0.003866 | -0.11548 | -0.10173 | -0.20307 | -0.23842 | 0.013951 | -0.089235 | 0.11383 | -0.074313 | -0.31378 | 122.3078 | 122.2722 | 122.286 | 62.1611 | -122.4179 | 122.1493 | 122.3134 | 122.0739 | 62.2242 | -122.5908
747.6094 | 122.5388 | -62.178 | 60.2417 | 1.4211e-13 | -0.0082863 | -0.012009 | 0.015516 | -0.037011 | 0.029953 | 0.0067908 | -0.014513 | 0.010021 | 0.034709 | -0.0045853 | 0.038838 | -62.1002 | 0.001407 | -62.1723 | 60.1618 | 60.1308 | 60.1446 | -62.1624 | -62.1229 | 0.078197 | -62.2352 | 60.0079 | 60.172 | 59.9325 | -62.3491 | 0.015608 | -0.079917 | 0.077835 | 0.005737 | -0.009871 | -0.1109 | -0.097147 | -0.17103 | -0.23385 | 0.055152 | -0.057191 | 0.11383 | -0.069734 | -0.3092 | 122.3398 | 122.3088 | 122.3226 | 62.1794 | -122.4041 | 122.1859 | 122.35 | 122.1105 | 62.2562 | -122.5908
749.3906 | 122.5479 | -62.1597 | 60.2371 | 1.4211e-13 | -0.0082863 | -0.012009 | 0.015729 | -0.037011 | 0.030167 | -0.00083919 | -0.014085 | 0.010234 | 0.035136 | -0.0043717 | 0.039052 | -62.0956 | 0.005985 | -62.1677 | 60.1709 | 60.1262 | 60.1354 | -62.1716 | -62.1183 | 0.078197 | -62.2398 | 60.0079 | 60.172 | 59.9371 | -62.3491 | -0.011861 | -0.066183 | 0.064102 | -0.007995 | 0.003866 | -0.11091 | -0.10173 | -0.18934 | -0.22927 | 0.04142 | -0.080081 | 0.10926 | -0.065157 | -0.30004 | 122.3307 | 122.2859 | 122.2951 | 62.1657 | -122.4087 | 122.1676 | 122.3317 | 122.0968 | 62.2379 | -122.5862
751.0938 | 122.6624 | -62.1231 | 60.1776 | 1.4211e-13 | -0.0089273 | -0.011581 | 0.015729 | -0.037438 | 0.030381 | 0.0067908 | -0.014726 | 0.010234 | 0.035136 | -0.0043717 | 0.038838 | -62.0956 | 0.010564 | -62.1723 | 60.1709 | 60.1308 | 60.1491 | -62.1716 | -62.1275 | 0.091933 | -62.2261 | 60.0033 | 60.1765 | 59.9371 | -62.3445 | -0.048482 | -0.006673 | 0.027481 | -0.049195 | -0.000713 | -0.046816 | -0.028481 | -0.22138 | -0.17434 | -0.004358 | -0.10296 | 0.11841 | -0.001068 | -0.24053 | 122.294 | 122.2539 | 122.2722 | 62.1337 | -122.3492 | 122.1264 | 122.2997 | 122.0602 | 62.215 | -122.5221
752.8906 | 122.644 | -62.1368 | 60.1593 | 1.4211e-13 | -0.0082863 | -0.011795 | 0.015729 | -0.037438 | 0.030167 | 0.014421 | -0.014085 | 0.010234 | 0.035136 | -0.0041581 | 0.039265 | -62.091 | 0.010564 | -62.1631 | 60.1755 | 60.1308 | 60.1446 | -62.1762 | -62.1275 | 0.082776 | -62.2307 | 60.0033 | 60.1674 | 59.9417 | -62.3399 | -0.039328 | 0.016215 | 0.045792 | -0.026305 | 0.013023 | -0.028506 | -0.01475 | -0.20307 | -0.15603 | 0.009375 | -0.093811 | 0.10925 | 0.008084 | -0.21764 | 122.3124 | 122.2676 | 122.2814 | 62.1474 | -122.3355 | 122.1401 | 122.3042 | 122.0785 | 62.2196 | -122.4992
754.5938 | 122.5113 | -62.146 | 60.2554 | 1.4211e-13 | -0.0089273 | -0.012222 | 0.015729 | -0.036797 | 0.030381 | -0.00083919 | -0.014085 | 0.010448 | 0.035136 | -0.0043717 | 0.039265 | -62.091 | 0.005985 | -62.1769 | 60.1801 | 60.1308 | 60.14 | -62.167 | -62.1183 | 0.087354 | -62.2307 | 60.0124 | 60.172 | 59.9371 | -62.3353 | -0.021015 | -0.075337 | 0.054947 | -0.030885 | -0.00987 | -0.12464 | -0.11546 | -0.18933 | -0.243 | 0.027687 | -0.084656 | 0.10468 | -0.083467 | -0.31835 | 122.3261 | 122.2768 | 122.286 | 62.152 | -122.4224 | 122.1584 | 122.318 | 122.0831 | 62.2333 | -122.5908
756.375 | 122.6624 | -62.114 | 60.2005 | 1.4211e-13 | -0.0084999 | -0.012222 | 0.015729 | -0.037224 | 0.030594 | -0.00083919 | -0.014513 | 0.010662 | 0.034496 | -0.0045853 | 0.039052 | -62.091 | 0.010564 | -62.1677 | 60.1801 | 60.1445 | 60.1491 | -62.167 | -62.1183 | 0.078197 | -62.2352 | 60.0079 | 60.1765 | 59.9417 | -62.3353 | -0.053058 | -0.020405 | 0.022904 | -0.053771 | -0.000713 | -0.055967 | -0.051369 | -0.22138 | -0.19265 | -0.004356 | -0.12128 | 0.1001 | -0.023956 | -0.25884 | 122.294 | 122.2585 | 122.2631 | 62.1245 | -122.3675 | 122.1218 | 122.2905 | 122.0556 | 62.1922 | -122.5358
758.1406 | 122.5662 | -62.1323 | 60.2417 | 1.4211e-13 | -0.0089273 | -0.012222 | 0.015729 | -0.037224 | 0.030381 | -0.0084697 | -0.014085 | 0.010234 | 0.034709 | -0.0043717 | 0.039052 | -62.0865 | 0.005985 | -62.1631 | 60.1755 | 60.14 | 60.1537 | -62.1579 | -62.1183 | 0.087354 | -62.2261 | 60.0124 | 60.1811 | 59.9462 | -62.3399 | -0.02559 | -0.066182 | 0.045793 | -0.030883 | -0.005293 | -0.10174 | -0.08799 | -0.20764 | -0.22927 | 0.013954 | -0.09381 | 0.11383 | -0.060577 | -0.29546 | 122.3078 | 122.2722 | 122.286 | 62.1382 | -122.3996 | 122.1447 | 122.3134 | 122.0785 | 62.2196 | -122.5816
759.9219 | 122.6349 | -62.1368 | 60.2097 | 1.4211e-13 | -0.0084999 | -0.011795 | 0.015729 | -0.037224 | 0.030381 | -0.00083919 | -0.014299 | 0.010021 | 0.034923 | -0.0043717 | 0.039052 | -62.091 | 0.005985 | -62.1631 | 60.1709 | 60.14 | 60.1491 | -62.1716 | -62.1183 | 0.078197 | -62.2215 | 60.0079 | 60.1811 | 59.9462 | -62.3399 | -0.034749 | -0.038717 | 0.045792 | -0.026305 | 0.008444 | -0.069702 | -0.060525 | -0.20307 | -0.2018 | 0.018532 | -0.084654 | 0.11841 | -0.028534 | -0.26342 | 122.3078 | 122.2768 | 122.286 | 62.1428 | -122.3812 | 122.1447 | 122.318 | 122.0831 | 62.215 | -122.5496
761.6406 | 122.6532 | -62.1231 | 60.1593 | 1.4211e-13 | -0.0089273 | -0.011795 | 0.015943 | -0.037011 | 0.030594 | 0.0067908 | -0.014299 | 0.010448 | 0.034923 | -0.0043717 | 0.038838 | -62.0865 | 0.001407 | -62.1677 | 60.1847 | 60.14 | 60.1491 | -62.1579 | -62.1183 | 0.087354 | -62.2215 | 60.0079 | 60.1765 | 59.9508 | -62.3262 | -0.034745 | 0.025372 | 0.036638 | -0.044616 | -0.009871 | -0.019348 | -0.010171 | -0.20306 | -0.15145 | 0.004799 | -0.098387 | 0.10468 | 0.017242 | -0.20849 | 122.3078 | 122.2631 | 122.2722 | 62.1245 | -122.3172 | 122.131 | 122.2997 | 122.0739 | 62.2105 | -122.4855
763.4219 | 122.644 | -62.1231 | 60.2097 | 1.4211e-13 | -0.0087137 | -0.012009 | 0.015729 | -0.037224 | 0.030381 | 0.0067908 | -0.014085 | 0.010448 | 0.034923 | -0.0039443 | 0.039265 | -62.0865 | 0.010564 | -62.1631 | 60.1847 | 60.1354 | 60.1537 | -62.1579 | -62.1137 | 0.087354 | -62.2215 | 60.017 | 60.1903 | 59.9508 | -62.3308 | -0.034745 | -0.024982 | 0.036638 | -0.040038 | -0.005293 | -0.074281 | -0.055947 | -0.20764 | -0.19265 | 0.009378 | -0.098387 | 0.10926 | -0.019377 | -0.25884 | 122.3078 | 122.2585 | 122.2768 | 62.1337 | -122.3675 | 122.1401 | 122.3134 | 122.0739 | 62.2105 | -122.5404
765.125 | 122.6349 | -62.1185 | 60.2325 | 1.4211e-13 | -0.0087137 | -0.011795 | 0.015943 | -0.037011 | 0.030594 | -0.00083919 | -0.014299 | 0.010448 | 0.034709 | -0.0043717 | 0.039052 | -62.0819 | 0.005985 | -62.1631 | 60.1893 | 60.1445 | 60.1446 | -62.1533 | -62.1137 | 0.082776 | -62.2261 | 60.017 | 60.1857 | 59.9462 | -62.3353 | -0.034744 | -0.043292 | 0.036638 | -0.044616 | -0.009872 | -0.088011 | -0.087992 | -0.2168 | -0.21553 | 0.0048 | -0.10754 | 0.10926 | -0.046843 | -0.28631 | 122.3078 | 122.2631 | 122.2631 | 62.1245 | -122.3858 | 122.1355 | 122.3042 | 122.0648 | 62.2013 | -122.5679
766.9219 | 122.6303 | -62.1368 | 60.2097 | 1.4211e-13 | -0.0084999 | -0.012009 | 0.015943 | -0.037224 | 0.030381 | -0.00083919 | -0.014299 | 0.010448 | 0.035136 | -0.0039443 | 0.038838 | -62.0819 | 0.005985 | -62.1586 | 60.1893 | 60.1491 | 60.1629 | -62.1624 | -62.1046 | 0.087354 | -62.2215 | 60.0307 | 60.1857 | 59.9508 | -62.3308 | -0.025591 | -0.020404 | 0.054949 | -0.021727 | 0.003864 | -0.060544 | -0.04679 | -0.19391 | -0.17891 | 0.032268 | -0.084654 | 0.10926 | -0.023955 | -0.25884 | 122.3261 | 122.286 | 122.2997 | 62.1428 | -122.3721 | 122.1676 | 122.3225 | 122.0877 | 62.2242 | -122.5404
768.7031 | 122.5662 | -62.1368 | 60.2646 | 1.4211e-13 | -0.0087137 | -0.011795 | 0.015943 | -0.037224 | 0.030167 | 0.0067908 | -0.014513 | 0.010234 | 0.034709 | -0.0043717 | 0.038838 | -62.0773 | 0.005985 | -62.154 | 60.1847 | 60.1537 | 60.1629 | -62.1487 | -62.1137 | 0.082776 | -62.2169 | 60.0262 | 60.1903 | 59.9508 | -62.3216 | -0.011854 | -0.079913 | 0.059528 | -0.017148 | -0.005294 | -0.1109 | -0.10172 | -0.18475 | -0.23842 | 0.023111 | -0.080075 | 0.10468 | -0.074308 | -0.31377 | 122.3215 | 122.2905 | 122.2997 | 62.1428 | -122.4133 | 122.163 | 122.3271 | 122.0877 | 62.2196 | -122.5862
770.4844 | 122.4884 | -62.1689 | 60.2646 | 1.4211e-13 | -0.0087137 | -0.011795 | 0.015943 | -0.036797 | 0.030594 | -0.00083919 | -0.014299 | 0.010234 | 0.035136 | -0.0043717 | 0.038624 | -62.0682 | 0.010564 | -62.1586 | 60.1847 | 60.14 | 60.1629 | -62.1395 | -62.1137 | 0.082776 | -62.2123 | 60.0307 | 60.1903 | 59.9554 | -62.3308 | 0.029347 | -0.079913 | 0.10073 | 0.010316 | -0.019031 | -0.12463 | -0.10172 | -0.16187 | -0.23384 | 0.055154 | -0.043453 | 0.11841 | -0.074308 | -0.30919 | 122.3536 | 122.3088 | 122.3317 | 62.1794 | -122.4041 | 122.1996 | 122.3592 | 122.1243 | 62.2517 | -122.5953
772.2656 | 122.5113 | -62.1506 | 60.2966 | 1.4211e-13 | -0.0089273 | -0.012009 | 0.015943 | -0.037438 | 0.030167 | -0.0084697 | -0.014299 | 0.010021 | 0.034709 | -0.0041581 | 0.039052 | -62.0727 | 0.005985 | -62.1448 | 60.1984 | 60.1583 | 60.1629 | -62.1441 | -62.1092 | 0.082776 | -62.2169 | 60.0216 | 60.1857 | 59.9554 | -62.3216 | 0.006458 | -0.098222 | 0.077839 | 0.005741 | -0.000717 | -0.13836 | -0.13376 | -0.17102 | -0.27504 | 0.041422 | -0.066342 | 0.10468 | -0.11093 | -0.34124 | 122.349 | 122.3088 | 122.3134 | 62.1566 | -122.4407 | 122.1722 | 122.3363 | 122.106 | 62.2334 | -122.6182
773.9688 | 122.6669 | -62.1094 | 60.2188 | 1.4211e-13 | -0.0089273 | -0.012009 | 0.015729 | -0.037224 | 0.030381 | 0.0067908 | -0.014513 | 0.010234 | 0.034923 | -0.0043717 | 0.039052 | -62.0773 | 0.005985 | -62.154 | 60.1938 | 60.1583 | 60.1629 | -62.1533 | -62.1046 | 0.082776 | -62.2078 | 60.0307 | 60.1903 | 59.96 | -62.3216 | -0.043899 | -0.02498 | 0.032062 | -0.044614 | -0.000715 | -0.060541 | -0.055945 | -0.21222 | -0.18807 | 0.004802 | -0.098384 | 0.11383 | -0.028532 | -0.25884 | 122.3032 | 122.2676 | 122.2722 | 62.1154 | -122.3721 | 122.1401 | 122.2997 | 122.0693 | 62.1922 | -122.5404
775.7656 | 122.6303 | -62.1231 | 60.1959 | 1.4211e-13 | -0.0087137 | -0.012009 | 0.015729 | -0.037011 | 0.030167 | -0.0084697 | -0.014299 | 0.010234 | 0.034923 | -0.0039443 | 0.039052 | -62.0636 | 0.001407 | -62.1403 | 60.1984 | 60.1583 | 60.172 | -62.1441 | -62.0954 | 0.087354 | -62.2123 | 60.0353 | 60.1994 | 59.9737 | -62.317 | -0.021008 | 0.002486 | 0.05953 | -0.017147 | 0.003861 | -0.037653 | -0.023899 | -0.19391 | -0.1606 | 0.027693 | -0.089229 | 0.10468 | 0.003514 | -0.22221 | 122.3215 | 122.2814 | 122.2951 | 62.1245 | -122.34 | 122.1584 | 122.3225 | 122.0968 | 62.2105 | -122.5129
777.5781 | 122.5342 | -62.1277 | 60.2646 | 1.4211e-13 | -0.0087137 | -0.011795 | 0.015943 | -0.037224 | 0.030167 | 0.0067908 | -0.014299 | 0.010234 | 0.034923 | -0.0041581 | 0.037983 | -62.0636 | -0.003172 | -62.1403 | 60.1938 | 60.1583 | 60.1812 | -62.1395 | -62.0954 | 0.087354 | -62.2078 | 60.0307 | 60.1994 | 59.9691 | -62.3079 | -0.011851 | -0.070756 | 0.064108 | -0.012569 | -0.000718 | -0.10632 | -0.083406 | -0.18017 | -0.23384 | 0.032271 | -0.080073 | 0.1001 | -0.06515 | -0.29546 | 122.3215 | 122.286 | 122.3089 | 62.1245 | -122.4041 | 122.1584 | 122.3271 | 122.0968 | 62.215 | -122.5724
779.2969 | 122.6532 | -62.0911 | 60.2234 | 1.4211e-13 | -0.0089273 | -0.011795 | 0.015729 | -0.037224 | 0.030381 | 0.0067908 | -0.014513 | 0.010234 | 0.034923 | -0.0037307 | 0.038197 | -62.0544 | 0.005985 | -62.1357 | 60.1984 | 60.1674 | 60.1812 | -62.1395 | -62.0954 | 0.073618 | -62.2078 | 60.0353 | 60.204 | 59.9691 | -62.3124 | -0.048473 | -0.02498 | 0.036642 | -0.044612 | 0.003861 | -0.055962 | -0.042208 | -0.22137 | -0.18806 | -0.004351 | -0.11669 | 0.10468 | -0.019374 | -0.25426 | 122.2895 | 122.2585 | 122.2722 | 62.097 | -122.3629 | 122.1264 | 122.2951 | 122.0602 | 62.1647 | -122.5358
781.0625 | 122.5021 | -62.114 | 60.3149 | 1.4211e-13 | -0.0089273 | -0.012222 | 0.015729 | -0.037011 | 0.030808 | 0.0067908 | -0.014726 | 0.010662 | 0.034709 | -0.0041581 | 0.037983 | -62.0544 | -0.003172 | -62.1403 | 60.203 | 60.1674 | 60.172 | -62.1304 | -62.0954 | 0.078197 | -62.2032 | 60.0445 | 60.2132 | 59.9737 | -62.3033 | -0.016426 | -0.11195 | 0.059531 | -0.026302 | -0.009876 | -0.14751 | -0.14292 | -0.18932 | -0.27046 | 0.018538 | -0.089227 | 0.1001 | -0.10177 | -0.34123 | 122.3169 | 122.2814 | 122.286 | 62.1108 | -122.4453 | 122.1584 | 122.3271 | 122.0877 | 62.1922 | -122.6182
782.875 | 122.5525 | -62.0911 | 60.2417 | 1.4211e-13 | -0.0087137 | -0.012009 | 0.015943 | -0.037224 | 0.030167 | -0.00083919 | -0.014085 | 0.010021 | 0.034496 | -0.0039443 | 0.037983 | -62.059 | -0.003172 | -62.1311 | 60.2076 | 60.1674 | 60.1812 | -62.1212 | -62.0908 | 0.087354 | -62.1849 | 60.0445 | 60.2178 | 59.9737 | -62.3079 | -0.030158 | -0.034133 | 0.032064 | -0.040034 | -0.009876 | -0.074272 | -0.060518 | -0.21679 | -0.19722 | 0.000227 | -0.093801 | 0.12299 | -0.023948 | -0.26799 | 122.2986 | 122.2585 | 122.2722 | 62.0879 | -122.3629 | 122.1355 | 122.3088 | 122.0648 | 62.1784 | -122.5496
784.5938 | 122.6303 | -62.1185 | 60.2005 | 1.4211e-13 | -0.0087137 | -0.011581 | 0.015729 | -0.037652 | 0.030381 | -0.0084697 | -0.014513 | 0.010662 | 0.034923 | -0.0041581 | 0.037983 | -62.0544 | 0.001407 | -62.1311 | 60.2167 | 60.1674 | 60.1858 | -62.1212 | -62.0863 | 0.078197 | -62.194 | 60.0445 | 60.2132 | 59.992 | -62.3033 | -0.002692 | 0.016223 | 0.064108 | -0.012568 | -0.009876 | -0.033073 | -0.014741 | -0.18475 | -0.15602 | 0.032272 | -0.075493 | 0.10925 | 0.012672 | -0.20848 | 122.3353 | 122.286 | 122.3043 | 62.1199 | -122.3217 | 122.163 | 122.3317 | 122.1106 | 62.1967 | -122.5038
786.375 | 122.6578 | -62.0911 | 60.2417 | 1.4211e-13 | -0.0089273 | -0.011795 | 0.015729 | -0.037011 | 0.030594 | 0.0067908 | -0.014513 | 0.010448 | 0.034923 | -0.0039443 | 0.038197 | -62.0453 | 0.005985 | -62.1174 | 60.2167 | 60.1812 | 60.1949 | -62.1258 | -62.0863 | 0.082776 | -62.1894 | 60.0445 | 60.2315 | 59.9829 | -62.3033 | -0.034737 | -0.024976 | 0.045799 | -0.026299 | 0.008438 | -0.060535 | -0.046782 | -0.21221 | -0.19722 | 0.004806 | -0.09838 | 0.11383 | -0.010212 | -0.25883 | 122.3078 | 122.2722 | 122.286 | 62.097 | -122.3675 | 122.1355 | 122.3226 | 122.0739 | 62.1738 | -122.545
788.1562 | 122.5433 | -62.1048 | 60.2829 | 1.4211e-13 | -0.0084999 | -0.011795 | 0.015943 | -0.037011 | 0.030381 | -0.00083919 | -0.014299 | 0.010234 | 0.034709 | -0.0043717 | 0.03777 | -62.0407 | 0.001407 | -62.1219 | 60.2167 | 60.1812 | 60.1949 | -62.1212 | -62.0771 | 0.082776 | -62.1849 | 60.0445 | 60.2178 | 59.9829 | -62.2941 | -0.016425 | -0.066175 | 0.064111 | -0.017144 | -0.000719 | -0.10173 | -0.087981 | -0.18932 | -0.23842 | 0.027696 | -0.080068 | 0.10925 | -0.065147 | -0.30003 | 122.3215 | 122.286 | 122.2997 | 62.1062 | -122.4041 | 122.1493 | 122.3225 | 122.0877 | 62.1876 | -122.577
789.875 | 122.6532 | -62.0636 | 60.2371 | 1.4211e-13 | -0.0089273 | -0.011795 | 0.015729 | -0.037438 | 0.030381 | -0.00083919 | -0.014513 | 0.010662 | 0.034923 | -0.0043717 | 0.038197 | -62.0453 | -0.003172 | -62.1174 | 60.2305 | 60.1812 | 60.2132 | -62.1166 | -62.0817 | 0.087354 | -62.1803 | 60.0536 | 60.2269 | 59.992 | -62.2895 | -0.053044 | -0.006664 | 0.018334 | -0.053764 | -0.00072 | -0.055958 | -0.023891 | -0.22594 | -0.18348 | -0.01808 | -0.11669 | 0.10925 | -0.010214 | -0.2451 | 122.2941 | 122.2448 | 122.2768 | 62.0604 | -122.3538 | 122.1172 | 122.2905 | 122.0556 | 62.151 | -122.5267
791.6562 | 122.6028 | -62.0773 | 60.2554 | 1.4211e-13 | -0.0087137 | -0.011581 | 0.015729 | -0.037652 | 0.030594 | -0.0084697 | -0.014513 | 0.010021 | 0.035136 | -0.0037307 | 0.037983 | -62.0361 | 0.001407 | -62.1128 | 60.2305 | 60.1903 | 60.2087 | -62.1121 | -62.0634 | 0.078197 | -62.1757 | 60.0628 | 60.2361 | 60.0058 | -62.285 | -0.034732 | -0.024974 | 0.041224 | -0.035453 | -0.000721 | -0.06511 | -0.04678 | -0.20763 | -0.19264 | 0.013968 | -0.098376 | 0.10925 | -0.019367 | -0.24967 | 122.3078 | 122.2677 | 122.286 | 62.0787 | -122.3675 | 122.1401 | 122.3134 | 122.0831 | 62.1555 | -122.5404
793.4375 | 122.6486 | -62.0865 | 60.2142 | 1.4211e-13 | -0.0089273 | -0.012009 | 0.015516 | -0.037224 | 0.030381 | -0.0084697 | -0.014299 | 0.010448 | 0.03535 | -0.0043717 | 0.038197 | -62.0361 | -0.003172 | -62.099 | 60.235 | 60.1995 | 60.2087 | -62.1166 | -62.0588 | 0.082776 | -62.1711 | 60.072 | 60.2406 | 60.0195 | -62.2804 | -0.030156 | 0.020803 | 0.050379 | -0.012563 | 0.017593 | -0.014753 | -0.005581 | -0.1939 | -0.14228 | 0.027701 | -0.084642 | 0.10925 | 0.026411 | -0.19474 | 122.3215 | 122.286 | 122.2951 | 62.0833 | -122.3309 | 122.1584 | 122.3271 | 122.106 | 62.1693 | -122.4946
795.1562 | 122.6349 | -62.0728 | 60.228 | 1.4211e-13 | -0.0091411 | -0.012009 | 0.016157 | -0.037652 | 0.030808 | -0.0084697 | -0.014513 | 0.010234 | 0.034923 | -0.0039443 | 0.037983 | -62.0315 | -0.007751 | -62.1128 | 60.235 | 60.2086 | 60.2224 | -62.1029 | -62.0588 | 0.078197 | -62.1666 | 60.0765 | 60.2315 | 60.0149 | -62.2758 | -0.030152 | 0.00707 | 0.041224 | -0.040031 | -0.009879 | -0.019328 | -0.005578 | -0.20305 | -0.15144 | 0.013968 | -0.093796 | 0.10925 | 0.003521 | -0.21305 | 122.3078 | 122.2814 | 122.2951 | 62.065 | -122.3309 | 122.1493 | 122.3042 | 122.0877 | 62.151 | -122.5038
796.9375 | 122.5616 | -62.0453 | 60.3241 | 1.4211e-13 | -0.0087137 | -0.012009 | 0.015729 | -0.037652 | 0.030808 | 0.0067908 | -0.014513 | 0.010021 | 0.034496 | -0.0037307 | 0.038197 | -62.027 | -0.003172 | -62.1036 | 60.235 | 60.1949 | 60.2178 | -62.0937 | -62.0588 | 0.078197 | -62.162 | 60.0765 | 60.2452 | 60.0103 | -62.2758 | -0.04846 | -0.089061 | 0.018337 | -0.05834 | -0.00988 | -0.1292 | -0.10629 | -0.23052 | -0.24757 | -0.013498 | -0.11668 | 0.11383 | -0.078874 | -0.31376 | 122.2803 | 122.2402 | 122.2631 | 62.0421 | -122.4178 | 122.1218 | 122.2905 | 122.0556 | 62.1235 | -122.5999
798.6719 | 122.5525 | -62.0911 | 60.2829 | 1.4211e-13 | -0.0087137 | -0.012009 | 0.015729 | -0.037438 | 0.030167 | -0.00083919 | -0.014726 | 0.010234 | 0.034923 | -0.0039443 | 0.038197 | -62.0132 | -0.003172 | -62.0945 | 60.2396 | 60.2041 | 60.2178 | -62.0937 | -62.0496 | 0.078197 | -62.162 | 60.0765 | 60.2406 | 60.0149 | -62.2804 | -0.002684 | -0.043283 | 0.077848 | -0.003408 | -0.000724 | -0.078839 | -0.065088 | -0.18932 | -0.20637 | 0.041436 | -0.070908 | 0.11841 | -0.042254 | -0.26798 | 122.3307 | 122.2951 | 122.3089 | 62.0879 | -122.3766 | 122.1676 | 122.3317 | 122.106 | 62.1693 | -122.5633
800.4688 | 122.6074 | -62.1002 | 60.2875 | 1.4211e-13 | -0.0087137 | -0.011795 | 0.015729 | -0.037438 | 0.030167 | 0.0067908 | -0.014726 | 0.010234 | 0.035136 | -0.0039443 | 0.038197 | -62.0132 | -0.003172 | -62.0899 | 60.2396 | 60.2086 | 60.2315 | -62.08 | -62.0496 | 0.073618 | -62.1574 | 60.0857 | 60.2498 | 60.0149 | -62.2621 | 0.020209 | -0.047861 | 0.087004 | 0.010326 | -0.009883 | -0.078838 | -0.055931 | -0.16185 | -0.20179 | 0.050592 | -0.057173 | 0.10468 | -0.037675 | -0.27256 | 122.3398 | 122.3089 | 122.3318 | 62.097 | -122.3675 | 122.1859 | 122.35 | 122.1151 | 62.1738 | -122.5495
802.1875 | 122.6028 | -62.0773 | 60.2554 | 1.4211e-13 | -0.0089273 | -0.012222 | 0.015516 | -0.037438 | 0.030594 | 0.0067908 | -0.014726 | 0.010234 | 0.034496 | -0.0037307 | 0.037983 | -62.0132 | -0.012329 | -62.0853 | 60.2442 | 60.2132 | 60.2361 | -62.0937 | -62.0496 | 0.082776 | -62.1482 | 60.0811 | 60.2544 | 60.0332 | -62.2621 | -0.016416 | -0.011239 | 0.064116 | -0.007983 | 0.008433 | -0.042215 | -0.019308 | -0.18474 | -0.17432 | 0.027704 | -0.070903 | 0.11383 | -0.001052 | -0.2222 | 122.3215 | 122.2905 | 122.3135 | 62.065 | -122.3492 | 122.1584 | 122.3317 | 122.1106 | 62.1601 | -122.5175
803.9688 | 122.5204 | -62.0911 | 60.3333 | 1.4211e-13 | -0.0093547 | -0.011795 | 0.015729 | -0.037224 | 0.030594 | -0.00083919 | -0.014513 | 0.010234 | 0.034923 | -0.0039443 | 0.03777 | -62.0086 | -0.007751 | -62.0762 | 60.2579 | 60.2178 | 60.2361 | -62.0846 | -62.0405 | 0.082776 | -62.1437 | 60.0903 | 60.2544 | 60.0195 | -62.2575 | 0.006474 | -0.075324 | 0.082426 | 0.014905 | 0.008431 | -0.11546 | -0.097128 | -0.16642 | -0.24299 | 0.050593 | -0.052593 | 0.11383 | -0.078872 | -0.31376 | 122.349 | 122.3089 | 122.3272 | 62.0833 | -122.4178 | 122.1813 | 122.3454 | 122.1106 | 62.1738 | -122.5907
805.7656 | 122.5983 | -62.0499 | 60.2783 | 1.4211e-13 | -0.0087137 | -0.011795 | 0.015516 | -0.037652 | 0.030808 | -0.00083919 | -0.014299 | 0.010234 | 0.034709 | -0.0037307 | 0.038411 | -62.0041 | -0.007751 | -62.0899 | 60.2671 | 60.2315 | 60.2407 | -62.08 | -62.0313 | 0.073618 | -62.1391 | 60.0903 | 60.2635 | 60.0332 | -62.2483 | -0.030145 | -0.011235 | 0.045807 | -0.040028 | -0.009883 | -0.046788 | -0.037617 | -0.19846 | -0.18805 | 0.018553 | -0.089212 | 0.10925 | -0.014783 | -0.24509 | 122.317 | 122.2814 | 122.2906 | 62.0421 | -122.3583 | 122.1401 | 122.3134 | 122.0831 | 62.1235 | -122.5267
807.5781 | 122.6669 | -62.0224 | 60.2921 | 1.4211e-13 | -0.0091411 | -0.011795 | 0.015516 | -0.037011 | 0.030381 | 0.0067908 | -0.014085 | 0.010234 | 0.034923 | -0.0039443 | 0.03777 | -61.9995 | -0.012329 | -62.0762 | 60.2671 | 60.2315 | 60.2453 | -62.0709 | -62.0267 | 0.078197 | -62.1299 | 60.0994 | 60.2635 | 60.0241 | -62.2575 | -0.048453 | -0.024968 | 0.022919 | -0.053759 | -0.005306 | -0.060521 | -0.046772 | -0.23509 | -0.19263 | -0.004335 | -0.10752 | 0.12757 | -0.028516 | -0.26798 | 122.2895 | 122.2539 | 122.2677 | 62.0101 | -122.3629 | 122.1218 | 122.2859 | 122.0465 | 62.1006 | -122.5495
809.2812 | 122.5571 | -62.0224 | 60.347 | 1.4211e-13 | -0.0082863 | -0.011581 | 0.015729 | -0.037224 | 0.030381 | 0.0067908 | -0.014513 | 0.010234 | 0.035136 | -0.0039443 | 0.038197 | -61.9812 | -0.003172 | -62.067 | 60.2762 | 60.2407 | 60.2499 | -62.0617 | -62.0176 | 0.082776 | -62.1299 | 60.1086 | 60.2864 | 60.0424 | -62.2392 | -0.039296 | -0.070743 | 0.041233 | -0.044602 | -0.005306 | -0.10629 | -0.097125 | -0.21677 | -0.2384 | 0.004823 | -0.10752 | 0.10925 | -0.060555 | -0.3046 | 122.2986 | 122.2631 | 122.2723 | 62.0192 | -122.4087 | 122.131 | 122.3088 | 122.0648 | 62.1052 | -122.5862
811.0625 | 122.4884 | -62.0361 | 60.3424 | 1.4211e-13 | -0.0089273 | -0.012009 | 0.015516 | -0.037224 | 0.030381 | -0.00083919 | -0.014513 | 0.010234 | 0.035136 | -0.0039443 | 0.03777 | -61.9766 | -0.007751 | -62.0578 | 60.2808 | 60.2544 | 60.2636 | -62.048 | -62.0084 | 0.078197 | -62.1116 | 60.1223 | 60.2956 | 60.0515 | -62.23 | -0.011826 | -0.061587 | 0.059544 | -0.021713 | -0.009887 | -0.08798 | -0.078811 | -0.19388 | -0.22009 | 0.027713 | -0.075473 | 0.11841 | -0.04682 | -0.29086 | 122.317 | 122.2906 | 122.2997 | 62.0284 | -122.3904 | 122.1584 | 122.3317 | 122.0877 | 62.1143 | -122.5724
812.875 | 122.5937 | -62.0316 | 60.2692 | 1.4211e-13 | -0.0084999 | -0.012009 | 0.015729 | -0.037652 | 0.030381 | 0.0067908 | -0.014513 | 0.010234 | 0.03535 | -0.0039443 | 0.037983 | -61.972 | -0.016908 | -62.0533 | 60.2854 | 60.259 | 60.2728 | -62.0434 | -62.0038 | 0.078197 | -62.107 | 60.1223 | 60.2956 | 60.0699 | -62.2209 | -0.011825 | 0.016233 | 0.059544 | -0.021712 | -0.009887 | -0.010159 | 0.003588 | -0.1893 | -0.14685 | 0.027714 | -0.075472 | 0.11383 | 0.026422 | -0.19931 | 122.317 | 122.2906 | 122.3043 | 62.0146 | -122.3125 | 122.1539 | 122.3271 | 122.1014 | 62.1098 | -122.49
814.6562 | 122.5388 | -62.0224 | 60.3882 | 1.4211e-13 | -0.0089273 | -0.012222 | 0.015516 | -0.037438 | 0.030381 | 0.0067908 | -0.014085 | 0.010234 | 0.034923 | -0.0037307 | 0.038197 | -61.9629 | -0.007751 | -62.0533 | 60.2946 | 60.2544 | 60.2773 | -62.0388 | -61.9901 | 0.078197 | -62.107 | 60.1361 | 60.2956 | 60.0653 | -62.2163 | -0.016401 | -0.093629 | 0.059546 | -0.030867 | -0.014466 | -0.13376 | -0.11085 | -0.19388 | -0.25213 | 0.032295 | -0.084627 | 0.10925 | -0.092597 | -0.3229 | 122.317 | 122.2768 | 122.2997 | 62.0146 | -122.427 | 122.1585 | 122.318 | 122.0877 | 62.1006 | -122.6045
816.4531 | 122.6212 | -62.027 | 60.3058 | 1.4211e-13 | -0.0093547 | -0.011795 | 0.015943 | -0.037438 | 0.030808 | 0.0067908 | -0.014513 | 0.010021 | 0.034709 | -0.0041581 | 0.03777 | -61.9629 | -0.016908 | -62.0441 | 60.2946 | 60.2636 | 60.2819 | -62.0388 | -61.9901 | 0.087354 | -62.107 | 60.1361 | 60.3002 | 60.0699 | -62.2117 | -0.011823 | -0.011231 | 0.064124 | -0.017133 | -0.00531 | -0.042201 | -0.023876 | -0.18472 | -0.16973 | 0.036873 | -0.080049 | 0.10467 | -0.00562 | -0.23593 | 122.3215 | 122.2906 | 122.3089 | 62.0101 | -122.3446 | 122.163 | 122.3271 | 122.0968 | 62.1143 | -122.5175
818.2344 | 122.5433 | -62.0178 | 60.3516 | 1.4211e-13 | -0.0089273 | -0.011795 | 0.015943 | -0.037652 | 0.030381 | -0.00083919 | -0.014513 | 0.010021 | 0.034923 | -0.0039443 | 0.03777 | -61.9354 | -0.021486 | -62.0121 | 60.322 | 60.2865 | 60.3002 | -62.0205 | -61.9626 | 0.082776 | -62.0796 | 60.1589 | 60.3322 | 60.0928 | -62.1934 | -0.002663 | -0.029537 | 0.082439 | 0.005759 | 0.008422 | -0.065083 | -0.051338 | -0.17556 | -0.19262 | 0.055189 | -0.061733 | 0.11383 | -0.019346 | -0.25881 | 122.3398 | 122.3043 | 122.318 | 61.9963 | -122.372 | 122.1768 | 122.35 | 122.1106 | 62.1006 | -122.5449
819.9375 | 122.5891 | -61.9949 | 60.3653 | 1.4211e-13 | -0.0091411 | -0.012436 | 0.015729 | -0.037438 | 0.030381 | -0.0084697 | -0.014513 | 0.010021 | 0.035136 | -0.0039443 | 0.03777 | -61.9171 | -0.021486 | -61.9983 | 60.3403 | 60.3094 | 60.3231 | -61.993 | -61.9535 | 0.082776 | -62.0658 | 60.1727 | 60.3414 | 60.1111 | -62.1751 | 0.001922 | -0.024956 | 0.077864 | -0.003394 | -0.005316 | -0.055921 | -0.042178 | -0.18014 | -0.19262 | 0.041459 | -0.070885 | 0.10925 | -0.023922 | -0.25423 | 122.3353 | 122.3043 | 122.3181 | 61.9734 | -122.3583 | 122.1676 | 122.3363 | 122.106 | 62.0777 | -122.5404
821.7344 | 122.6349 | -61.9492 | 60.3561 | 1.4211e-13 | -0.0087137 | -0.012009 | 0.015943 | -0.037438 | 0.030381 | -0.00083919 | -0.014726 | 0.010662 | 0.034923 | -0.0037307 | 0.038197 | -61.9033 | -0.021486 | -61.98 | 60.3449 | 60.3185 | 60.3277 | -61.9884 | -61.9397 | 0.082776 | -62.0475 | 60.1864 | 60.3505 | 60.1294 | -62.1613 | -0.039275 | -0.011223 | 0.045823 | -0.030857 | 0.008418 | -0.037608 | -0.028444 | -0.21218 | -0.16973 | 0.009419 | -0.098346 | 0.11383 | -0.00561 | -0.22676 | 122.2941 | 122.2677 | 122.2769 | 61.9277 | -122.3446 | 122.1356 | 122.2997 | 122.0785 | 62.0319 | -122.5175
823.4688 | 122.5525 | -61.9446 | 60.4431 | 1.4211e-13 | -0.0089273 | -0.012009 | 0.015729 | -0.037438 | 0.030594 | -0.00083919 | -0.014299 | 0.010021 | 0.034923 | -0.0037307 | 0.038197 | -61.9033 | -0.021486 | -61.98 | 60.3541 | 60.314 | 60.3277 | -61.9839 | -61.9306 | 0.078197 | -62.0429 | 60.1956 | 60.3551 | 60.1202 | -62.1613 | -0.039274 | -0.089041 | 0.041245 | -0.035435 | 0.003839 | -0.12916 | -0.11542 | -0.21675 | -0.24754 | 0.013998 | -0.098345 | 0.11841 | -0.088006 | -0.32289 | 122.2987 | 122.2585 | 122.2723 | 61.9231 | -122.427 | 122.1402 | 122.2997 | 122.0648 | 62.0228 | -122.6044
825.2344 | 122.6349 | -61.9308 | 60.3928 | 1.4211e-13 | -0.0089273 | -0.011795 | 0.015516 | -0.037224 | 0.030594 | -0.00083919 | -0.014726 | 0.010448 | 0.034709 | -0.0039443 | 0.037983 | -61.8988 | -0.026065 | -61.9709 | 60.3678 | 60.3323 | 60.346 | -61.9701 | -61.926 | 0.082776 | -62.0429 | 60.1956 | 60.3643 | 60.1385 | -62.1522 | -0.03927 | -0.024952 | 0.032091 | -0.040011 | -0.000741 | -0.060492 | -0.046751 | -0.22133 | -0.19719 | 0.004844 | -0.11208 | 0.10925 | -0.028495 | -0.25422 | 122.2987 | 122.2631 | 122.2769 | 61.9048 | -122.3629 | 122.1264 | 122.2951 | 122.0694 | 62.0136 | -122.5449
827.0312 | 122.5159 | -61.94 | 60.4614 | 1.4211e-13 | -0.0093547 | -0.011795 | 0.015729 | -0.037438 | 0.030381 | 0.014421 | -0.014726 | 0.010448 | 0.034923 | -0.0037307 | 0.037556 | -61.8896 | -0.021486 | -61.9709 | 60.3724 | 60.3414 | 60.3414 | -61.9564 | -61.926 | 0.073618 | -62.0246 | 60.2093 | 60.378 | 60.1385 | -62.1522 | -0.016378 | -0.089038 | 0.050402 | -0.030856 | -0.014478 | -0.12 | -0.11999 | -0.21217 | -0.25212 | 0.013999 | -0.084608 | 0.12757 | -0.083424 | -0.32289 | 122.3124 | 122.2814 | 122.2814 | 61.9185 | -122.4178 | 122.1493 | 122.318 | 122.0785 | 62.0136 | -122.6136
828.75 | 122.5571 | -61.908 | 60.4294 | 1.4211e-13 | -0.0089273 | -0.011795 | 0.015516 | -0.037438 | 0.030381 | -0.00083919 | -0.014299 | 0.010448 | 0.034923 | -0.0037307 | 0.038197 | -61.8896 | -0.021486 | -61.9663 | 60.3678 | 60.3323 | 60.346 | -61.961 | -61.9168 | 0.082776 | -62.0292 | 60.2139 | 60.3734 | 60.1385 | -62.1384 | -0.053 | -0.061573 | 0.018359 | -0.058321 | -0.005321 | -0.097113 | -0.083372 | -0.23048 | -0.2155 | -0.008887 | -0.12123 | 0.10925 | -0.055959 | -0.29084 | 122.2758 | 122.2402 | 122.254 | 61.8865 | -122.3903 | 122.1218 | 122.2814 | 122.0465 | 61.9907 | -122.5678
830.5469 | 122.5708 | -61.9125 | 60.434 | 1.4211e-13 | -0.0091411 | -0.011795 | 0.015943 | -0.037865 | 0.030167 | -0.00083919 | -0.014299 | 0.010021 | 0.03535 | -0.0037307 | 0.037983 | -61.8804 | -0.026065 | -61.948 | 60.377 | 60.3414 | 60.3597 | -61.9564 | -61.9168 | 0.078197 | -62.02 | 60.2139 | 60.3872 | 60.1523 | -62.1293 | -0.043843 | -0.056994 | 0.032094 | -0.03543 | 0.008413 | -0.092533 | -0.074214 | -0.21675 | -0.22008 | -0.004309 | -0.1075 | 0.10925 | -0.046801 | -0.28169 | 122.2895 | 122.254 | 122.2723 | 61.8865 | -122.3903 | 122.1264 | 122.2997 | 122.0648 | 61.9907 | -122.5632
832.2656 | 122.5891 | -61.9217 | 60.3928 | 1.4211e-13 | -0.0091411 | -0.011581 | 0.015729 | -0.037652 | 0.030594 | -0.0084697 | -0.014513 | 0.010448 | 0.035136 | -0.0039443 | 0.038197 | -61.8804 | -0.026065 | -61.9434 | 60.3861 | 60.3552 | 60.3735 | -61.9426 | -61.9031 | 0.078197 | -62.0063 | 60.2322 | 60.4009 | 60.1706 | -62.1247 | -0.020952 | -0.006638 | 0.041249 | -0.021697 | -0.000745 | -0.037598 | -0.019279 | -0.20301 | -0.16056 | 0.018582 | -0.084603 | 0.11841 | 0.008134 | -0.22217 | 122.3078 | 122.2769 | 122.2952 | 61.8956 | -122.3354 | 122.1539 | 122.3226 | 122.0923 | 61.9999 | -122.5175
834.0625 | 122.58 | -61.9263 | 60.434 | 1.4211e-13 | -0.0093547 | -0.012009 | 0.015943 | -0.037652 | 0.029953 | -0.0161 | -0.014513 | 0.010448 | 0.034709 | -0.0037307 | 0.03777 | -61.8576 | -0.021486 | -61.9388 | 60.4044 | 60.3735 | 60.3872 | -61.9335 | -61.8894 | 0.082776 | -62.0063 | 60.2414 | 60.4146 | 60.1889 | -62.111 | -0.007216 | -0.029524 | 0.068719 | -0.01254 | -0.005324 | -0.060481 | -0.046742 | -0.1847 | -0.1926 | 0.036897 | -0.080025 | 0.10467 | -0.019329 | -0.24506 | 122.3307 | 122.2997 | 122.3135 | 61.9048 | -122.3674 | 122.1676 | 122.3409 | 122.1152 | 62.009 | -122.5449
835.7812 | 122.5616 | -61.8851 | 60.4752 | 1.4211e-13 | -0.0091411 | -0.012009 | 0.015729 | -0.037865 | 0.030381 | -0.00083919 | -0.014726 | 0.010234 | 0.034923 | -0.0035171 | 0.03777 | -61.8484 | -0.030644 | -61.9297 | 60.409 | 60.3781 | 60.3918 | -61.9197 | -61.8802 | 0.082776 | -61.988 | 60.2459 | 60.4238 | 60.1797 | -62.111 | -0.034678 | -0.066144 | 0.036677 | -0.044583 | -0.009905 | -0.097101 | -0.083362 | -0.2259 | -0.22922 | 0.004855 | -0.10291 | 0.12299 | -0.051371 | -0.29541 | 122.2941 | 122.2631 | 122.2769 | 61.8544 | -122.3949 | 122.131 | 122.3089 | 122.0648 | 61.9678 | -122.5861
837.5781 | 122.5891 | -61.9034 | 60.4111 | 1.4211e-13 | -0.0091411 | -0.011795 | 0.015516 | -0.037438 | 0.030381 | 0.0067908 | -0.014513 | 0.010021 | 0.034923 | -0.0035171 | 0.03777 | -61.8484 | -0.021486 | -61.9159 | 60.4228 | 60.3872 | 60.401 | -61.9243 | -61.8711 | 0.082776 | -61.9788 | 60.2597 | 60.4329 | 60.1889 | -62.0972 | -0.020947 | 0.011678 | 0.054987 | -0.012538 | 0.008409 | -0.023856 | -0.010118 | -0.19385 | -0.1514 | 0.032322 | -0.075442 | 0.11841 | 0.021873 | -0.22217 | 122.3261 | 122.2906 | 122.3043 | 61.8819 | -122.3354 | 122.1631 | 122.3363 | 122.0923 | 61.9862 | -122.5083
839.2969 | 122.5983 | -61.908 | 60.4523 | 1.4211e-13 | -0.0091411 | -0.012009 | 0.016157 | -0.037652 | 0.030167 | 0.014421 | -0.014513 | 0.010234 | 0.034923 | -0.0039443 | 0.038197 | -61.8301 | -0.030644 | -61.9113 | 60.4319 | 60.3918 | 60.4101 | -61.906 | -61.8711 | 0.082776 | -61.9697 | 60.2734 | 60.4329 | 60.2072 | -62.0881 | 0.001947 | -0.020364 | 0.077878 | -0.003382 | -0.005329 | -0.060476 | -0.04216 | -0.18011 | -0.17887 | 0.0369 | -0.061707 | 0.11841 | -0.019326 | -0.24505 | 122.3399 | 122.2998 | 122.3181 | 61.8773 | -122.3583 | 122.1814 | 122.3409 | 122.1152 | 61.9907 | -122.5403
841.0781 | 122.5937 | -61.8896 | 60.4431 | 1.4211e-13 | -0.0091411 | -0.012009 | 0.015516 | -0.037652 | 0.030381 | -0.00083919 | -0.014085 | 0.010448 | 0.034923 | -0.0037307 | 0.037983 | -61.8118 | -0.030644 | -61.8839 | 60.4548 | 60.4193 | 60.4238 | -61.8877 | -61.839 | 0.082776 | -61.9514 | 60.2871 | 60.4513 | 60.221 | -62.0606 | 0.001952 | 0.011684 | 0.077881 | 0.005777 | 0.003825 | -0.023847 | -0.019268 | -0.17095 | -0.15597 | 0.05064 | -0.061703 | 0.10925 | 0.008145 | -0.22216 | 122.3444 | 122.3089 | 122.3135 | 61.859 | -122.3308 | 122.1768 | 122.3409 | 122.1106 | 61.9724 | -122.5037
842.875 | 122.6303 | -61.8301 | 60.4797 | 1.4211e-13 | -0.0093547 | -0.012009 | 0.015729 | -0.037438 | 0.030167 | -0.00083919 | -0.014726 | 0.010234 | 0.034709 | -0.0037307 | 0.037983 | -61.7935 | -0.039801 | -61.8793 | 60.4777 | 60.4376 | 60.4559 | -61.8694 | -61.8207 | 0.082776 | -61.9376 | 60.31 | 60.4833 | 60.2438 | -62.0469 | -0.039242 | -0.002045 | 0.036686 | -0.049154 | -0.009912 | -0.042152 | -0.023839 | -0.21672 | -0.1697 | 0.009446 | -0.10748 | 0.10925 | 0.003574 | -0.23589 | 122.3078 | 122.2677 | 122.286 | 61.7903 | -122.3491 | 122.1402 | 122.3134 | 122.074 | 61.9129 | -122.5266
844.6719 | 122.58 | -61.8484 | 60.5118 | 1.4211e-13 | -0.0093547 | -0.012009 | 0.015516 | -0.037011 | 0.030594 | -0.0084697 | -0.014299 | 0.010234 | 0.035136 | -0.0037307 | 0.037556 | -61.7797 | -0.035222 | -61.8564 | 60.4823 | 60.4467 | 60.4651 | -61.8556 | -61.8115 | 0.078197 | -61.9101 | 60.3146 | 60.4879 | 60.253 | -62.0331 | -0.007194 | -0.029511 | 0.068732 | -0.007951 | -0.000757 | -0.065038 | -0.046726 | -0.18468 | -0.19717 | 0.036915 | -0.061693 | 0.12298 | -0.023891 | -0.25878 | 122.3307 | 122.2952 | 122.3135 | 61.8132 | -122.3674 | 122.1631 | 122.3363 | 122.1015 | 61.9266 | -122.5449
846.4688 | 122.6028 | -61.8118 | 60.5301 | 1.4211e-13 | -0.0091411 | -0.011581 | 0.015516 | -0.037438 | 0.030167 | -0.00083919 | -0.014726 | 0.010021 | 0.034923 | -0.0035171 | 0.03777 | -61.766 | -0.030644 | -61.8381 | 60.5097 | 60.4696 | 60.4879 | -61.8282 | -61.7841 | 0.073618 | -61.901 | 60.3329 | 60.5062 | 60.2759 | -62.0148 | -0.016341 | -0.020351 | 0.045846 | -0.026259 | -0.009918 | -0.060454 | -0.042143 | -0.20298 | -0.19716 | 0.027766 | -0.089156 | 0.11383 | -0.023887 | -0.25419 | 122.3216 | 122.2815 | 122.2998 | 61.7812 | -122.3583 | 122.1448 | 122.318 | 122.0877 | 61.8854 | -122.5449
848.1875 | 122.5983 | -61.7844 | 60.5209 | 1.4211e-13 | -0.0089273 | -0.011795 | 0.015729 | -0.037438 | 0.030381 | -0.0084697 | -0.014299 | 0.010234 | 0.034923 | -0.0039443 | 0.037983 | -61.7385 | -0.030644 | -61.8198 | 60.5281 | 60.4925 | 60.5154 | -61.819 | -61.7657 | 0.078197 | -61.8735 | 60.3558 | 60.5291 | 60.3079 | -61.9828 | -0.03465 | 0.007118 | 0.04585 | -0.035412 | -0.000762 | -0.028404 | -0.005516 | -0.1984 | -0.16512 | 0.018615 | -0.08915 | 0.10925 | 0.008161 | -0.21299 | 122.3124 | 122.2769 | 122.2998 | 61.7537 | -122.3399 | 122.1402 | 122.3135 | 122.0923 | 61.8626 | -122.5037
849.9688 | 122.4884 | -61.7889 | 60.5988 | 1.4211e-13 | -0.0093547 | -0.011795 | 0.015729 | -0.037224 | 0.030594 | 0.0067908 | -0.014726 | 0.010234 | 0.034923 | -0.0035171 | 0.037983 | -61.7202 | -0.039801 | -61.806 | 60.5464 | 60.5017 | 60.5246 | -61.7961 | -61.752 | 0.073618 | -61.8644 | 60.3741 | 60.5383 | 60.3171 | -61.9736 | -0.007178 | -0.052389 | 0.068741 | -0.0171 | -0.009922 | -0.097066 | -0.074179 | -0.18466 | -0.22462 | 0.036928 | -0.075415 | 0.10925 | -0.060502 | -0.28165 | 122.3353 | 122.2906 | 122.3135 | 61.7491 | -122.3949 | 122.1631 | 122.3272 | 122.106 | 61.8626 | -122.5724
851.75 | 122.5479 | -61.7477 | 60.6171 | 1.4211e-13 | -0.0091411 | -0.011795 | 0.015516 | -0.037438 | 0.030381 | 0.0067908 | -0.014513 | 0.010448 | 0.034709 | -0.0037307 | 0.03777 | -61.7065 | -0.044379 | -61.7877 | 60.5555 | 60.5246 | 60.5429 | -61.787 | -61.7429 | 0.078197 | -61.846 | 60.3879 | 60.5611 | 60.3308 | -61.9553 | -0.039218 | -0.061542 | 0.041278 | -0.039985 | -0.000767 | -0.092481 | -0.074175 | -0.20754 | -0.2292 | 0.004887 | -0.098299 | 0.10925 | -0.055919 | -0.28623 | 122.3033 | 122.2723 | 122.2906 | 61.7034 | -122.404 | 122.1356 | 122.3089 | 122.0786 | 61.8259 | -122.5724
853.5312 | 122.5616 | -61.7523 | 60.6445 | 1.4211e-13 | -0.0095683 | -0.012009 | 0.015943 | -0.037438 | 0.030381 | -0.00083919 | -0.014513 | 0.010448 | 0.034923 | -0.0035171 | 0.03777 | -61.6927 | -0.048958 | -61.7786 | 60.5555 | 60.5246 | 60.5429 | -61.7686 | -61.7245 | 0.078197 | -61.8369 | 60.397 | 60.5749 | 60.3308 | -61.9507 | -0.016325 | -0.089008 | 0.05959 | -0.026251 | -0.009926 | -0.11995 | -0.10164 | -0.19839 | -0.24751 | 0.027779 | -0.084564 | 0.11382 | -0.069649 | -0.31369 | 122.3078 | 122.2769 | 122.2952 | 61.7034 | -122.4132 | 122.1493 | 122.3272 | 122.0832 | 61.8305 | -122.5952
855.3125 | 122.5342 | -61.7294 | 60.6445 | 1.4211e-13 | -0.0091411 | -0.011795 | 0.015516 | -0.037224 | 0.030381 | -0.0084697 | -0.014513 | 0.010234 | 0.034923 | -0.0035171 | 0.037556 | -61.6744 | -0.044379 | -61.7511 | 60.5784 | 60.5475 | 60.5749 | -61.7503 | -61.7062 | 0.078197 | -61.814 | 60.4245 | 60.5886 | 60.3492 | -61.9324 | -0.020898 | -0.066116 | 0.055016 | -0.02167 | -0.000772 | -0.097053 | -0.06959 | -0.20296 | -0.22004 | 0.023206 | -0.084559 | 0.1184 | -0.055913 | -0.29538 | 122.3078 | 122.2769 | 122.3044 | 61.6851 | -122.3949 | 122.1539 | 122.318 | 122.0786 | 61.8076 | -122.5769
857.0938 | 122.6257 | -61.7249 | 60.5804 | 1.4211e-13 | -0.0093547 | -0.011795 | 0.015729 | -0.037652 | 0.030381 | -0.00083919 | -0.014513 | 0.010448 | 0.035136 | -0.0035171 | 0.037983 | -61.6698 | -0.048958 | -61.7465 | 60.5967 | 60.5612 | 60.5795 | -61.7366 | -61.7016 | 0.082776 | -61.8048 | 60.4337 | 60.5978 | 60.3675 | -61.9278 | -0.011738 | 0.016285 | 0.055017 | -0.021668 | -0.00993 | -0.019229 | -0.000925 | -0.20296 | -0.14679 | 0.023208 | -0.079978 | 0.12298 | 0.017331 | -0.21298 | 122.3216 | 122.2861 | 122.3044 | 61.6759 | -122.317 | 122.1585 | 122.3226 | 122.0923 | 61.8076 | -122.5083
858.875 | 122.5113 | -61.7157 | 60.6995 | 1.4211e-13 | -0.0091411 | -0.012436 | 0.015729 | -0.037865 | 0.030381 | -0.00083919 | -0.014299 | 0.010234 | 0.034709 | -0.0035171 | 0.037556 | -61.6515 | -0.044379 | -61.7328 | 60.615 | 60.5704 | 60.5887 | -61.7183 | -61.6833 | 0.078197 | -61.7957 | 60.4474 | 60.6252 | 60.3766 | -61.9003 | -0.002578 | -0.084421 | 0.064175 | -0.01709 | -0.014512 | -0.12909 | -0.11079 | -0.18464 | -0.25207 | 0.032366 | -0.079977 | 0.10467 | -0.074216 | -0.32284 | 122.3307 | 122.2861 | 122.3044 | 61.6713 | -122.4177 | 122.1631 | 122.3409 | 122.0923 | 61.7939 | -122.5998
860.6719 | 122.6028 | -61.6837 | 60.6354 | 1.4211e-13 | -0.0093547 | -0.012222 | 0.015943 | -0.037224 | 0.030594 | -0.00083919 | -0.014726 | 0.009807 | 0.035136 | -0.0035171 | 0.037556 | -61.6424 | -0.048958 | -61.7236 | 60.6288 | 60.5887 | 60.6024 | -61.7137 | -61.6696 | 0.082776 | -61.7774 | 60.452 | 60.6344 | 60.3995 | -61.9003 | -0.030042 | -0.006599 | 0.041288 | -0.039976 | -0.009934 | -0.046687 | -0.032964 | -0.21669 | -0.18341 | 0.01406 | -0.093705 | 0.12298 | -0.000972 | -0.23586 | 122.3124 | 122.2723 | 122.2861 | 61.6347 | -122.3491 | 122.1356 | 122.3181 | 122.0832 | 61.7664 | -122.5357
862.4531 | 122.5616 | -61.6699 | 60.704 | 1.4211e-13 | -0.0093547 | -0.011795 | 0.015943 | -0.037865 | 0.030167 | 0.0067908 | -0.014513 | 0.010021 | 0.034709 | -0.0037307 | 0.03777 | -61.6378 | -0.058115 | -61.7145 | 60.6196 | 60.5887 | 60.6024 | -61.7045 | -61.6696 | 0.06904 | -61.7819 | 60.4565 | 60.6298 | 60.3949 | -61.9003 | -0.034617 | -0.08442 | 0.032134 | -0.044552 | -0.009935 | -0.11535 | -0.10163 | -0.23042 | -0.24749 | 0.000327 | -0.11202 | 0.1184 | -0.074216 | -0.3091 | 122.2895 | 122.2586 | 122.2723 | 61.6118 | -122.4086 | 122.1265 | 122.2997 | 122.0649 | 61.739 | -122.6044
864.1562 | 122.6349 | -61.6791 | 60.6491 | 1.4211e-13 | -0.0093547 | -0.011795 | 0.015943 | -0.037224 | 0.029953 | 0.0067908 | -0.014299 | 0.010021 | 0.034709 | -0.0037307 | 0.03777 | -61.6103 | -0.048958 | -61.687 | 60.6425 | 60.6162 | 60.6299 | -61.6908 | -61.6421 | 0.078197 | -61.7499 | 60.4749 | 60.6527 | 60.4224 | -61.8683 | -0.011726 | -0.006596 | 0.068759 | -0.007928 | 0.003798 | -0.032947 | -0.019225 | -0.18921 | -0.17425 | 0.036954 | -0.070811 | 0.1184 | 0.003609 | -0.2267 | 122.3216 | 122.2952 | 122.309 | 61.6301 | -122.3399 | 122.1539 | 122.3318 | 122.1015 | 61.7573 | -122.5174
865.9375 | 122.5479 | -61.6562 | 60.7132 | 1.4211e-13 | -0.0093547 | -0.011795 | 0.015516 | -0.037224 | 0.030167 | -0.0084697 | -0.014726 | 0.010234 | 0.034923 | -0.0035171 | 0.03777 | -61.6057 | -0.053537 | -61.687 | 60.6517 | 60.6207 | 60.6345 | -61.6816 | -61.6467 | 0.078197 | -61.7499 | 60.484 | 60.6573 | 60.427 | -61.8591 | -0.025456 | -0.061527 | 0.050449 | -0.030816 | -0.00536 | -0.092455 | -0.078734 | -0.20294 | -0.22918 | 0.009487 | -0.093699 | 0.10924 | -0.055899 | -0.28621 | 122.3079 | 122.2769 | 122.2907 | 61.6027 | -122.3948 | 122.1402 | 122.3135 | 122.0832 | 61.7344 | -122.5723
867.7188 | 122.6532 | -61.6104 | 60.6766 | 1.4211e-13 | -0.0093547 | -0.012009 | 0.015729 | -0.037652 | 0.030594 | -0.00083919 | -0.014513 | 0.010234 | 0.035136 | -0.0037307 | 0.03777 | -61.5783 | -0.058115 | -61.6641 | 60.6837 | 60.6436 | 60.6619 | -61.6542 | -61.6101 | 0.082776 | -61.7178 | 60.5161 | 60.6848 | 60.4499 | -61.8362 | -0.043758 | 0.007143 | 0.032144 | -0.0537 | -0.009942 | -0.032939 | -0.014641 | -0.22583 | -0.16051 | 0.000341 | -0.10742 | 0.1184 | 0.008193 | -0.22669 | 122.2941 | 122.254 | 122.2723 | 61.5523 | -122.3307 | 122.1265 | 122.2952 | 122.0603 | 61.6932 | -122.5128
869.5156 | 122.5891 | -61.6013 | 60.7498 | 1.4211e-13 | -0.0091411 | -0.011795 | 0.015729 | -0.037652 | 0.030381 | -0.0084697 | -0.014513 | 0.010021 | 0.034923 | -0.0030897 | 0.037983 | -61.5462 | -0.058115 | -61.6321 | 60.702 | 60.6711 | 60.6802 | -61.6359 | -61.5918 | 0.073618 | -61.7041 | 60.5344 | 60.7168 | 60.4682 | -61.8225 | -0.034599 | -0.047785 | 0.055037 | -0.030808 | 0.003791 | -0.078708 | -0.069569 | -0.22124 | -0.21544 | 0.0095 | -0.10284 | 0.1184 | -0.032998 | -0.28162 | 122.3033 | 122.2724 | 122.2815 | 61.5431 | -122.3857 | 122.1356 | 122.3181 | 122.0695 | 61.6749 | -122.5723
871.2969 | 122.6074 | -61.5967 | 60.7361 | 1.4211e-13 | -0.0091411 | -0.011795 | 0.015516 | -0.037224 | 0.029953 | -0.00083919 | -0.014299 | 0.010021 | 0.034709 | -0.0035171 | 0.037983 | -61.5554 | -0.058115 | -61.6366 | 60.6975 | 60.662 | 60.6848 | -61.6359 | -61.5963 | 0.082776 | -61.6949 | 60.5298 | 60.7077 | 60.4911 | -61.8133 | -0.039176 | -0.038631 | 0.041303 | -0.039964 | -0.000788 | -0.074133 | -0.051257 | -0.21666 | -0.20628 | 0.000344 | -0.098263 | 0.1184 | -0.028423 | -0.24499 | 122.2941 | 122.2586 | 122.2815 | 61.5386 | -122.3719 | 122.1265 | 122.3043 | 122.0878 | 61.6795 | -122.5494
873.0781 | 122.5067 | -61.6058 | 60.7773 | 1.4211e-13 | -0.0093547 | -0.012009 | 0.015729 | -0.037438 | 0.030381 | 0.0067908 | -0.014299 | 0.010021 | 0.034923 | -0.0035171 | 0.03777 | -61.5508 | -0.062694 | -61.6275 | 60.7112 | 60.6711 | 60.6894 | -61.6313 | -61.578 | 0.06904 | -61.6949 | 60.539 | 60.7168 | 60.4865 | -61.8088 | -0.025442 | -0.066095 | 0.055036 | -0.021652 | 0.00379 | -0.10617 | -0.087877 | -0.20293 | -0.23832 | 0.027814 | -0.089108 | 0.11382 | -0.060464 | -0.29077 | 122.317 | 122.2769 | 122.2952 | 61.5431 | -122.4086 | 122.1448 | 122.3227 | 122.0923 | 61.6749 | -122.586
874.875 | 122.6532 | -61.6058 | 60.6995 | 1.4211e-13 | -0.0093547 | -0.012436 | 0.015729 | -0.037652 | 0.029953 | -0.0084697 | -0.014299 | 0.010234 | 0.034709 | -0.0037307 | 0.03777 | -61.5416 | -0.062694 | -61.6229 | 60.7203 | 60.6803 | 60.6986 | -61.613 | -61.5734 | 0.082776 | -61.6812 | 60.5481 | 60.726 | 60.4957 | -61.8042 | -0.007126 | 0.020882 | 0.064193 | -0.017074 | -0.009948 | -0.019196 | -0.0009 | -0.19835 | -0.15135 | 0.032392 | -0.075372 | 0.12298 | 0.026513 | -0.20379 | 122.3262 | 122.2861 | 122.3044 | 61.5431 | -122.3124 | 122.154 | 122.3318 | 122.1015 | 61.6886 | -122.5036
876.6719 | 122.6028 | -61.5829 | 60.7452 | 1.4211e-13 | -0.0091411 | -0.011795 | 0.016157 | -0.037652 | 0.030381 | 0.0067908 | -0.014513 | 0.010448 | 0.034709 | -0.0037307 | 0.037983 | -61.5233 | -0.067272 | -61.6092 | 60.7387 | 60.7077 | 60.7169 | -61.6038 | -61.5597 | 0.078197 | -61.6629 | 60.571 | 60.7397 | 60.5186 | -61.7767 | -0.020856 | -0.00658 | 0.059618 | -0.026227 | -0.005371 | -0.037498 | -0.028362 | -0.19377 | -0.17423 | 0.023241 | -0.079945 | 0.11382 | -0.005527 | -0.22668 | 122.3216 | 122.2907 | 122.2998 | 61.5157 | -122.349 | 122.154 | 122.3227 | 122.1015 | 61.6611 | -122.522
878.4531 | 122.5021 | -61.615 | 60.7864 | 1.4211e-13 | -0.0095683 | -0.012222 | 0.015943 | -0.037865 | 0.030381 | -0.0084697 | -0.014513 | 0.010021 | 0.035136 | -0.0033033 | 0.03777 | -61.5096 | -0.067272 | -61.5909 | 60.7387 | 60.7077 | 60.7306 | -61.5901 | -61.5505 | 0.078197 | -61.6537 | 60.571 | 60.7534 | 60.5598 | -61.7767 | 0.024924 | -0.047779 | 0.1054 | 0.024129 | -0.000795 | -0.078697 | -0.055825 | -0.16172 | -0.21543 | 0.064441 | -0.038745 | 0.12298 | -0.03299 | -0.22667 | 122.3536 | 122.3227 | 122.3456 | 61.5477 | -122.3765 | 122.186 | 122.3684 | 122.1748 | 61.6932 | -122.5632
880.1562 | 122.644 | -61.5692 | 60.7727 | 1.4211e-13 | -0.0095683 | -0.012222 | 0.015729 | -0.037438 | 0.030167 | -0.00083919 | -0.014726 | 0.010021 | 0.034923 | -0.0035171 | 0.037556 | -61.5096 | -0.071851 | -61.5954 | 60.7478 | 60.7077 | 60.7306 | -61.5901 | -61.5505 | 0.078197 | -61.6583 | 60.5756 | 60.7534 | 60.5186 | -61.7721 | -0.020852 | -0.024889 | 0.059621 | -0.026225 | -0.005373 | -0.064964 | -0.042092 | -0.20292 | -0.19712 | 0.018665 | -0.089099 | 0.11382 | -0.019257 | -0.25414 | 122.317 | 122.277 | 122.2998 | 61.4974 | -122.3628 | 122.1448 | 122.3227 | 122.0878 | 61.6474 | -122.5448
881.9531 | 122.5708 | -61.5967 | 60.7819 | 1.4211e-13 | -0.0093547 | -0.012009 | 0.015943 | -0.037652 | 0.029953 | -0.00083919 | -0.014299 | 0.010234 | 0.034923 | -0.0037307 | 0.03777 | -61.5004 | -0.067272 | -61.5863 | 60.7524 | 60.7215 | 60.7306 | -61.5809 | -61.5414 | 0.078197 | -61.6446 | 60.5847 | 60.7626 | 60.5323 | -61.7584 | 0.015772 | -0.029466 | 0.096243 | 0.010397 | -0.005375 | -0.060383 | -0.051247 | -0.16172 | -0.19712 | 0.055288 | -0.047897 | 0.11382 | -0.019255 | -0.24956 | 122.3491 | 122.3182 | 122.3273 | 61.5294 | -122.3628 | 122.1814 | 122.3593 | 122.129 | 61.6749 | -122.5403
883.7344 | 122.5067 | -61.528 | 60.8551 | 1.4211e-13 | -0.0091411 | -0.011581 | 0.015729 | -0.037652 | 0.030167 | 0.0067908 | -0.014513 | 0.010021 | 0.034496 | -0.0033033 | 0.03777 | -61.5004 | -0.081008 | -61.5725 | 60.7661 | 60.7352 | 60.7443 | -61.5763 | -61.5277 | 0.078197 | -61.64 | 60.5939 | 60.7718 | 60.5415 | -61.7538 | -0.048315 | -0.088974 | 0.027578 | -0.044533 | 0.003782 | -0.11989 | -0.11075 | -0.2258 | -0.2612 | 0.00036 | -0.11198 | 0.11382 | -0.083341 | -0.31365 | 122.2941 | 122.2632 | 122.2724 | 61.447 | -122.4314 | 122.1219 | 122.2998 | 122.0695 | 61.6062 | -122.6089
885.4531 | 122.5342 | -61.5738 | 60.791 | 1.4211e-13 | -0.0091411 | -0.011795 | 0.015729 | -0.037652 | 0.029953 | -0.00083919 | -0.014513 | 0.010234 | 0.034923 | -0.0033033 | 0.037983 | -61.4821 | -0.071851 | -61.5634 | 60.7753 | 60.7398 | 60.7672 | -61.558 | -61.5139 | 0.073618 | -61.6217 | 60.6122 | 60.7901 | 60.5598 | -61.7401 | 0.015778 | -0.01573 | 0.091669 | 0.010401 | -0.005377 | -0.051223 | -0.023774 | -0.16629 | -0.1788 | 0.059873 | -0.047892 | 0.1184 | -0.00094 | -0.23125 | 122.3491 | 122.3136 | 122.341 | 61.5019 | -122.349 | 122.186 | 122.3639 | 122.1336 | 61.6474 | -122.5311
887.2344 | 122.5983 | -61.528 | 60.7819 | 1.4211e-13 | -0.0091411 | -0.011795 | 0.015943 | -0.037652 | 0.029953 | -0.0161 | -0.014513 | 0.010234 | 0.034923 | -0.0035171 | 0.037983 | -61.4775 | -0.071851 | -61.5588 | 60.7844 | 60.749 | 60.7764 | -61.5534 | -61.5093 | 0.082776 | -61.6217 | 60.6122 | 60.7855 | 60.5598 | -61.7355 | -0.02542 | 0.002583 | 0.05047 | -0.030798 | -0.005378 | -0.032909 | -0.005461 | -0.20749 | -0.16965 | 0.018674 | -0.093669 | 0.11382 | 0.003638 | -0.22209 | 122.3125 | 122.277 | 122.3044 | 61.4562 | -122.3353 | 122.1402 | 122.3135 | 122.0878 | 61.6108 | -122.5174
889.0312 | 122.5204 | -61.528 | 60.7864 | 1.4211e-13 | -0.0095683 | -0.012009 | 0.015943 | -0.037652 | 0.02974 | -0.00083919 | -0.014513 | 0.010875 | 0.03535 | -0.0030897 | 0.03777 | -61.4592 | -0.081008 | -61.5313 | 60.8073 | 60.7627 | 60.7947 | -61.5443 | -61.4864 | 0.073618 | -61.5988 | 60.6305 | 60.8038 | 60.5918 | -61.7218 | -0.016262 | 0.020897 | 0.068784 | -0.003328 | 0.012934 | -0.02375 | 0.008276 | -0.19375 | -0.15591 | 0.041568 | -0.070775 | 0.12298 | 0.017374 | -0.19462 | 122.3354 | 122.2907 | 122.3227 | 61.447 | -122.3307 | 122.1585 | 122.3318 | 122.1198 | 61.6016 | -122.5082
890.7656 | 122.6578 | -61.4456 | 60.8688 | 1.4211e-13 | -0.0093547 | -0.011795 | 0.016157 | -0.037438 | 0.030167 | -0.0084697 | -0.014513 | 0.010021 | 0.034709 | -0.0033033 | 0.037556 | -61.4363 | -0.085587 | -61.513 | 60.8211 | 60.7856 | 60.8084 | -61.5122 | -61.4681 | 0.078197 | -61.5851 | 60.6488 | 60.8359 | 60.5872 | -61.7035 | -0.066607 | -0.047765 | 0.009279 | -0.067412 | -0.000805 | -0.083253 | -0.060386 | -0.25783 | -0.21999 | -0.022514 | -0.13944 | 0.1184 | -0.032973 | -0.28159 | 122.2667 | 122.2312 | 122.2541 | 61.36 | -122.3811 | 122.0945 | 122.2815 | 122.0329 | 61.5238 | -122.5723
892.5 | 122.5296 | -61.4685 | 60.8826 | 1.4211e-13 | -0.0095683 | -0.011581 | 0.015943 | -0.037652 | 0.030167 | -0.0084697 | -0.014726 | 0.010234 | 0.034923 | -0.0033033 | 0.03777 | -61.4134 | -0.085587 | -61.5039 | 60.8394 | 60.8039 | 60.8268 | -61.4939 | -61.4544 | 0.078197 | -61.5622 | 60.6672 | 60.8496 | 60.6101 | -61.6806 | -0.025403 | -0.043185 | 0.055059 | -0.035368 | -0.009965 | -0.07867 | -0.055804 | -0.21205 | -0.21541 | 0.01411 | -0.093655 | 0.1184 | -0.03297 | -0.27243 | 122.3079 | 122.2724 | 122.2953 | 61.3829 | -122.3765 | 122.1357 | 122.3181 | 122.0786 | 61.5467 | -122.5631
894.2812 | 122.5433 | -61.4273 | 60.9512 | 1.4211e-13 | -0.0093547 | -0.012222 | 0.015943 | -0.037652 | 0.030594 | 0.014421 | -0.014726 | 0.010234 | 0.034709 | -0.0030897 | 0.037983 | -61.3997 | -0.090166 | -61.481 | 60.8577 | 60.8176 | 60.8405 | -61.471 | -61.4315 | 0.073618 | -61.5484 | 60.6855 | 60.8679 | 60.6239 | -61.6622 | -0.043707 | -0.093536 | 0.027595 | -0.053675 | -0.009968 | -0.1336 | -0.11073 | -0.23494 | -0.26576 | -0.004196 | -0.12112 | 0.11382 | -0.08332 | -0.32736 | 122.285 | 122.2449 | 122.2678 | 61.3371 | -122.4222 | 122.1128 | 122.2952 | 122.0512 | 61.5009 | -122.6135
896 | 122.58 | -61.4594 | 60.8826 | 1.4211e-13 | -0.0097821 | -0.011795 | 0.016157 | -0.037652 | 0.029953 | 0.0067908 | -0.014513 | 0.010234 | 0.035136 | -0.0030897 | 0.037983 | -61.3768 | -0.099323 | -61.4535 | 60.8852 | 60.8497 | 60.868 | -61.5031 | -61.4086 | 0.078197 | -61.5072 | 60.7175 | 60.8908 | 60.6559 | -61.6393 | -0.043716 | 0.002599 | 0.082531 | 0.005838 | 0.049554 | -0.032881 | -0.014597 | -0.18 | -0.16505 | 0.050742 | -0.047865 | 0.13213 | 0.008238 | -0.22665 | 122.3445 | 122.309 | 122.3273 | 61.36 | -122.3856 | 122.1769 | 122.3502 | 122.1153 | 61.5375 | -122.5219
897.7969 | 122.5754 | -61.4182 | 60.9238 | 1.4211e-13 | -0.0095683 | -0.011795 | 0.015516 | -0.037438 | 0.029953 | -0.0084697 | -0.014726 | 0.010234 | 0.034923 | -0.0033033 | 0.03777 | -61.331 | -0.1039 | -61.4169 | 60.9264 | 60.8863 | 60.9138 | -61.4115 | -61.3628 | 0.078197 | -61.4706 | 60.7541 | 60.9366 | 60.7017 | -61.5981 | 0.006664 | 0.002606 | 0.087116 | 0.001266 | -0.005398 | -0.037448 | -0.01001 | -0.17999 | -0.16962 | 0.05533 | -0.052434 | 0.12755 | 0.012825 | -0.22206 | 122.3445 | 122.3045 | 122.3319 | 61.3143 | -122.3353 | 122.1723 | 122.3547 | 122.1199 | 61.4963 | -122.5219
899.5312 | 122.6074 | -61.3541 | 60.9924 | 1.4211e-13 | -0.0093547 | -0.011581 | 0.016157 | -0.037652 | 0.030381 | -0.00083919 | -0.01494 | 0.010448 | 0.034496 | -0.0030897 | 0.03777 | -61.2807 | -0.099323 | -61.3619 | 60.9813 | 60.9458 | 60.9641 | -61.3474 | -61.3033 | 0.073618 | -61.4248 | 60.8091 | 60.9915 | 60.7521 | -61.5295 | 0.006682 | -0.011119 | 0.073391 | -0.007882 | -0.014564 | -0.046587 | -0.02831 | -0.17539 | -0.18334 | 0.050766 | -0.070734 | 0.10466 | -0.000897 | -0.24036 | 122.3354 | 122.2999 | 122.3182 | 61.2547 | -122.3398 | 122.1632 | 122.3456 | 122.1061 | 61.4277 | -122.5219
901.3125 | 122.5296 | -61.3495 | 61.0703 | 1.4211e-13 | -0.0097821 | -0.011581 | 0.015943 | -0.037865 | 0.030167 | -0.00083919 | -0.014726 | 0.010234 | 0.034923 | -0.0033033 | 0.03777 | -61.2624 | -0.099323 | -61.3482 | 60.995 | 60.955 | 60.9779 | -61.3382 | -61.3033 | 0.078197 | -61.4111 | 60.8274 | 61.0098 | 60.7612 | -61.5295 | 0.011262 | -0.075202 | 0.087127 | 0.001275 | -0.009987 | -0.11525 | -0.092393 | -0.17997 | -0.24285 | 0.046188 | -0.061576 | 0.11839 | -0.060402 | -0.30902 | 122.3445 | 122.3045 | 122.3273 | 61.2502 | -122.4085 | 122.1769 | 122.3593 | 122.1107 | 61.4277 | -122.5997
903.0312 | 122.5296 | -61.3724 | 61.0062 | 1.4211e-13 | -0.0095683 | -0.011581 | 0.016157 | -0.038079 | 0.030167 | 0.0067908 | -0.014513 | 0.010021 | 0.034923 | -0.0028759 | 0.037556 | -61.331 | -0.1039 | -61.4169 | 60.9264 | 60.8863 | 60.9183 | -61.4115 | -61.372 | 0.073618 | -61.4752 | 60.7587 | 60.9366 | 60.6925 | -61.589 | -0.039113 | -0.079792 | 0.041339 | -0.044511 | -0.005398 | -0.11985 | -0.087829 | -0.21661 | -0.24744 | 0.000396 | -0.10279 | 0.11382 | -0.069573 | -0.31362 | 122.2987 | 122.2587 | 122.2907 | 61.2685 | -122.4177 | 122.1311 | 122.309 | 122.0649 | 61.446 | -122.5951
904.8281 | 122.4792 | -61.4044 | 60.997 | 1.4211e-13 | -0.0097821 | -0.011795 | 0.016157 | -0.037652 | 0.029953 | -0.0084697 | -0.014513 | 0.010021 | 0.034923 | -0.0033033 | 0.037556 | -61.331 | -0.10848 | -61.4077 | 60.9401 | 60.9046 | 60.9183 | -61.4023 | -61.3628 | 0.078197 | -61.466 | 60.7633 | 60.9503 | 60.7017 | -61.589 | 0.002089 | -0.056901 | 0.073383 | -0.003311 | -0.0054 | -0.092375 | -0.078673 | -0.18456 | -0.2337 | 0.041597 | -0.061589 | 0.12297 | -0.046682 | -0.2953 | 122.3445 | 122.3091 | 122.3228 | 61.2959 | -122.3993 | 122.1677 | 122.3547 | 122.1061 | 61.4826 | -122.586
906.5469 | 122.5067 | -61.3586 | 61.0336 | 1.4211e-13 | -0.0095683 | -0.011795 | 0.015943 | -0.037652 | 0.030381 | 0.0067908 | -0.014299 | 0.010234 | 0.034709 | -0.0035171 | 0.037556 | -61.299 | -0.11306 | -61.3803 | 60.9584 | 60.9275 | 60.9458 | -61.3749 | -61.3353 | 0.06904 | -61.4431 | 60.7908 | 60.9641 | 60.7292 | -61.5569 | -0.016214 | -0.075209 | 0.059655 | -0.021617 | -0.005403 | -0.1061 | -0.087823 | -0.19829 | -0.24285 | 0.023293 | -0.084471 | 0.11382 | -0.069567 | -0.30445 | 122.3171 | 122.2862 | 122.3045 | 61.2456 | -122.4085 | 122.1494 | 122.3227 | 122.0878 | 61.4277 | -122.5906
908.3281 | 122.6166 | -61.3495 | 60.965 | 1.4211e-13 | -0.0095683 | -0.011795 | 0.01637 | -0.037652 | 0.030167 | -0.00083919 | -0.014726 | 0.010448 | 0.034709 | -0.0026623 | 0.037983 | -61.299 | -0.11306 | -61.3803 | 60.9676 | 60.9275 | 60.9504 | -61.3703 | -61.3308 | 0.073618 | -61.434 | 60.7954 | 60.9686 | 60.7429 | -61.5569 | -0.020791 | 0.002612 | 0.050499 | -0.030773 | -0.009982 | -0.037437 | -0.01458 | -0.20744 | -0.16961 | 0.018716 | -0.08447 | 0.12297 | 0.003676 | -0.22205 | 122.3171 | 122.277 | 122.2999 | 61.2364 | -122.3352 | 122.1448 | 122.3181 | 122.0924 | 61.4231 | -122.5219
910.125 | 122.6028 | -61.3358 | 60.9833 | 1.4211e-13 | -0.0097821 | -0.011795 | 0.015729 | -0.037652 | 0.030381 | 0.0067908 | -0.014513 | 0.010234 | 0.034709 | -0.0028759 | 0.03777 | -61.2853 | -0.12222 | -61.3711 | 60.9722 | 60.9367 | 60.955 | -61.3657 | -61.3216 | 0.082776 | -61.4294 | 60.7999 | 60.987 | 60.7475 | -61.5432 | -0.029945 | -0.011119 | 0.050502 | -0.035349 | -0.005404 | -0.046589 | -0.028311 | -0.20744 | -0.18334 | 0.014141 | -0.093624 | 0.11382 | 0.00368 | -0.23578 | 122.3079 | 122.2724 | 122.2907 | 61.2135 | -122.349 | 122.1357 | 122.3227 | 122.0832 | 61.4185 | -122.5265
911.9062 | 122.493 | -61.3266 | 61.0611 | 1.4211e-13 | -0.0093547 | -0.011795 | 0.016157 | -0.037652 | 0.030167 | 0.014421 | -0.01494 | 0.010234 | 0.034923 | -0.0030897 | 0.037983 | -61.2669 | -0.11764 | -61.3528 | 60.9905 | 60.9504 | 60.9779 | -61.3382 | -61.2987 | 0.078197 | -61.4156 | 60.8137 | 61.0053 | 60.7566 | -61.5249 | -0.011626 | -0.070626 | 0.05966 | -0.026191 | -0.014565 | -0.11067 | -0.083238 | -0.19828 | -0.24743 | 0.027879 | -0.089043 | 0.10924 | -0.055825 | -0.30445 | 122.3171 | 122.277 | 122.3045 | 61.209 | -122.3993 | 122.1403 | 122.3319 | 122.0832 | 61.4048 | -122.586
913.7031 | 122.5845 | -61.322 | 61.0107 | 1.4211e-13 | -0.0095683 | -0.012009 | 0.015943 | -0.037865 | 0.030381 | -0.0084697 | -0.014513 | 0.010234 | 0.034923 | -0.0033033 | 0.037556 | -61.2578 | -0.13137 | -61.3345 | 60.9996 | 60.9779 | 60.987 | -61.3245 | -61.285 | 0.078197 | -61.3927 | 60.8366 | 61.0236 | 60.8116 | -61.5111 | -0.002468 | -0.011115 | 0.064239 | -0.012456 | -0.009988 | -0.032845 | -0.023727 | -0.18912 | -0.17418 | 0.037037 | -0.070727 | 0.11839 | 0.012843 | -0.19915 | 122.3216 | 122.2999 | 122.309 | 61.1906 | -122.3352 | 122.1586 | 122.3456 | 122.1336 | 61.4002 | -122.5219
915.5 | 122.5983 | -61.3129 | 61.0565 | 1.4211e-13 | -0.0097821 | -0.011581 | 0.016157 | -0.037652 | 0.030167 | -0.0084697 | -0.014513 | 0.010662 | 0.034923 | -0.0033033 | 0.03777 | -61.2578 | -0.14053 | -61.3253 | 61.0088 | 60.9779 | 60.9962 | -61.3245 | -61.2804 | 0.073618 | -61.3882 | 60.8366 | 61.0236 | 60.7887 | -61.5066 | -0.011623 | -0.047735 | 0.055084 | -0.012455 | -0.000832 | -0.078622 | -0.060347 | -0.1937 | -0.21996 | 0.032461 | -0.075304 | 0.11839 | -0.032934 | -0.26782 | 122.3217 | 122.2908 | 122.309 | 61.1723 | -122.381 | 122.1494 | 122.3365 | 122.1016 | 61.3865 | -122.5631
917.2031 | 122.493 | -61.2717 | 61.1298 | 1.4211e-13 | -0.0095683 | -0.011795 | 0.015943 | -0.037438 | 0.030167 | 0.0067908 | -0.01494 | 0.010021 | 0.035136 | -0.0026623 | 0.037556 | -61.2166 | -0.13595 | -61.3162 | 61.0225 | 61.0008 | 61.0099 | -61.3016 | -61.2621 | 0.06904 | -61.379 | 60.8595 | 61.0465 | 60.8024 | -61.4882 | -0.029927 | -0.10724 | 0.05509 | -0.044497 | -0.01457 | -0.12897 | -0.11985 | -0.21658 | -0.27031 | 0.009577 | -0.10735 | 0.10923 | -0.083283 | -0.32733 | 122.2942 | 122.2725 | 122.2816 | 61.1357 | -122.4314 | 122.1311 | 122.3181 | 122.0741 | 61.3407 | -122.618
919 | 122.6303 | -61.2259 | 61.0886 | 1.4211e-13 | -0.0093547 | -0.012222 | 0.015729 | -0.037652 | 0.029953 | 0.0067908 | -0.014513 | 0.010448 | 0.034496 | -0.0028759 | 0.037556 | -61.2028 | -0.13595 | -61.2795 | 61.0546 | 61.0283 | 61.0511 | -61.2741 | -61.2346 | 0.078197 | -61.3378 | 60.8915 | 61.074 | 60.8299 | -61.4562 | -0.04823 | -0.033994 | 0.02305 | -0.053647 | -0.005417 | -0.060297 | -0.037447 | -0.23031 | -0.19706 | -0.008727 | -0.11191 | 0.11839 | -0.014612 | -0.25866 | 122.2805 | 122.2542 | 122.277 | 61.0899 | -122.3627 | 122.1174 | 122.2998 | 122.0558 | 61.3041 | -122.5448
920.7812 | 122.6532 | -61.1847 | 61.116 | 1.4211e-13 | -0.0095683 | -0.012009 | 0.015943 | -0.037865 | 0.030594 | 0.014421 | -0.014513 | 0.010234 | 0.034923 | -0.0030897 | 0.03777 | -61.1708 | -0.13595 | -61.2429 | 61.1004 | 61.0649 | 61.0786 | -61.2421 | -61.1934 | 0.087354 | -61.3012 | 60.9236 | 61.1014 | 60.862 | -61.4287 | -0.057376 | -0.015677 | 0.013899 | -0.05822 | -0.000844 | -0.051131 | -0.037441 | -0.24403 | -0.19248 | -0.008718 | -0.11648 | 0.12755 | -0.014607 | -0.25407 | 122.285 | 122.2496 | 122.2633 | 61.0487 | -122.3581 | 122.1082 | 122.2861 | 122.0466 | 61.272 | -122.5448
922.5 | 122.5891 | -61.2076 | 61.1343 | 1.4211e-13 | -0.0095683 | -0.012222 | 0.015729 | -0.037438 | 0.030381 | -0.00083919 | -0.014513 | 0.010234 | 0.034282 | -0.0030897 | 0.037983 | -61.1571 | -0.14511 | -61.2338 | 61.0866 | 61.0649 | 61.0877 | -61.2375 | -61.1888 | 0.078197 | -61.3012 | 60.9281 | 61.106 | 60.8665 | -61.4241 | -0.029908 | -0.047722 | 0.050523 | -0.026174 | 0.003734 | -0.069441 | -0.046594 | -0.21656 | -0.20621 | 0.01875 | -0.093593 | 0.12297 | -0.028338 | -0.2678 | 122.2942 | 122.2725 | 122.2953 | 61.0625 | -122.3718 | 122.1357 | 122.3136 | 122.0741 | 61.2858 | -122.5585
924.2812 | 122.5342 | -61.171 | 61.2305 | 1.4211e-13 | -0.0093547 | -0.011795 | 0.015943 | -0.037865 | 0.030381 | -0.0084697 | -0.014085 | 0.010234 | 0.034923 | -0.0028759 | 0.03777 | -61.1021 | -0.14969 | -61.1788 | 61.1461 | 61.1244 | 61.1381 | -61.178 | -61.1339 | 0.06904 | -61.2462 | 60.9831 | 61.1609 | 60.9215 | -61.3692 | -0.007004 | -0.084334 | 0.068842 | -0.007857 | -0.000853 | -0.10605 | -0.09236 | -0.19824 | -0.2474 | 0.037073 | -0.075271 | 0.12297 | -0.069526 | -0.30899 | 122.3171 | 122.2954 | 122.3091 | 61.0213 | -122.4084 | 122.154 | 122.3319 | 122.0924 | 61.24 | -122.5997
926 | 122.6212 | -61.1343 | 61.1847 | 1.4211e-13 | -0.0097821 | -0.012009 | 0.016157 | -0.037865 | 0.030381 | -0.00083919 | -0.01494 | 0.010021 | 0.034923 | -0.0026623 | 0.038197 | -61.1067 | -0.14969 | -61.188 | 61.1599 | 61.1153 | 61.1427 | -61.1734 | -61.1385 | 0.073618 | -61.2508 | 60.9785 | 61.1609 | 60.9169 | -61.3646 | -0.039046 | -0.024822 | 0.027643 | -0.053634 | -0.014588 | -0.069427 | -0.042005 | -0.23028 | -0.2062 | -0.004127 | -0.11647 | 0.11381 | -0.023749 | -0.26779 | 122.2942 | 122.2496 | 122.277 | 60.9847 | -122.3581 | 122.1128 | 122.2953 | 122.0512 | 61.208 | -122.5493
927.7812 | 122.5983 | -61.0931 | 61.2442 | 1.4211e-13 | -0.0097821 | -0.012009 | 0.015943 | -0.037224 | 0.030381 | -0.00083919 | -0.014726 | 0.010234 | 0.034709 | -0.0028759 | 0.03777 | -61.0701 | -0.15884 | -61.1559 | 61.1873 | 61.1473 | 61.1702 | -61.1459 | -61.1064 | 0.082776 | -61.2096 | 61.0151 | 61.1976 | 60.9581 | -61.3326 | -0.052771 | -0.056861 | 0.023072 | -0.062784 | -0.010013 | -0.096885 | -0.074043 | -0.23943 | -0.22908 | -0.013274 | -0.11646 | 0.12297 | -0.04663 | -0.2861 | 122.2805 | 122.2405 | 122.2633 | 60.9343 | -122.3901 | 122.1083 | 122.2907 | 122.0512 | 61.1759 | -122.5768
929.5 | 122.6257 | -61.0565 | 61.2579 | 1.4211e-13 | -0.0095683 | -0.012009 | 0.016157 | -0.037438 | 0.030594 | 0.0067908 | -0.014726 | 0.010448 | 0.034496 | -0.0030897 | 0.037556 | -61.0243 | -0.15427 | -61.0964 | 61.2423 | 61.2114 | 61.2251 | -61.091 | -61.0606 | 0.06904 | -61.1638 | 61.0655 | 61.2434 | 61.0131 | -61.2822 | -0.034445 | -0.015654 | 0.032235 | -0.039888 | -0.005443 | -0.046513 | -0.032833 | -0.22568 | -0.19245 | -0.004108 | -0.10729 | 0.11839 | -0.014577 | -0.24488 | 122.2988 | 122.2679 | 122.2816 | 60.9023 | -122.3489 | 122.122 | 122.2999 | 122.0696 | 61.1256 | -122.5401
931.2969 | 122.4838 | -61.0703 | 61.3174 | 1.4211e-13 | -0.0097821 | -0.012009 | 0.015516 | -0.037865 | 0.030167 | -0.00083919 | -0.014513 | 0.010021 | 0.034709 | -0.0030897 | 0.03777 | -60.9968 | -0.168 | -61.0735 | 61.2606 | 61.2297 | 61.2526 | -61.0726 | -61.024 | 0.073618 | -61.1455 | 61.093 | 61.2708 | 61.0359 | -61.2593 | -0.002397 | -0.056849 | 0.073437 | -0.003264 | -0.000867 | -0.087706 | -0.06487 | -0.18906 | -0.22449 | 0.046254 | -0.075247 | 0.11381 | -0.046614 | -0.2815 | 122.3308 | 122.3 | 122.3228 | 60.9022 | -122.3901 | 122.1632 | 122.3411 | 122.1062 | 61.1439 | -122.5768
933.0312 | 122.6074 | -61.0565 | 61.29 | 1.4211e-13 | -0.0095683 | -0.011581 | 0.015943 | -0.037652 | 0.030381 | -0.00083919 | -0.014726 | 0.010234 | 0.034709 | -0.0028759 | 0.03777 | -60.9648 | -0.17258 | -61.0369 | 61.3018 | 61.2572 | 61.2846 | -61.0406 | -60.9919 | 0.06904 | -61.1043 | 61.125 | 61.3029 | 61.0772 | -61.2135 | 0.015924 | 0.011822 | 0.091754 | 0.01963 | 0.003706 | -0.032766 | -0.005354 | -0.157 | -0.16497 | 0.064573 | -0.047771 | 0.10923 | 0.012902 | -0.21283 | 122.3583 | 122.3137 | 122.3411 | 60.8839 | -122.3306 | 122.1815 | 122.3594 | 122.1337 | 61.1256 | -122.5035
934.8125 | 122.5754 | -61.0336 | 61.322 | 1.4211e-13 | -0.0097821 | -0.011795 | 0.016157 | -0.037438 | 0.030167 | -0.00083919 | -0.014513 | 0.010234 | 0.035136 | -0.0026623 | 0.037342 | -60.9602 | -0.17258 | -61.0415 | 61.3064 | 61.2572 | 61.2892 | -61.036 | -60.9919 | 0.06904 | -61.0951 | 61.125 | 61.312 | 61.0726 | -61.2181 | -0.002386 | -0.015642 | 0.073443 | -0.007837 | -0.005451 | -0.064809 | -0.032818 | -0.18447 | -0.19702 | 0.041684 | -0.061502 | 0.12297 | -0.009984 | -0.24945 | 122.34 | 122.2908 | 122.3228 | 60.861 | -122.358 | 122.1586 | 122.3457 | 122.1062 | 61.1027 | -122.5401
936.5938 | 122.6532 | -61.0016 | 61.2991 | 1.4211e-13 | -0.0099957 | -0.012009 | 0.015516 | -0.038079 | 0.030167 | -0.0084697 | -0.014085 | 0.010021 | 0.034923 | -0.0028759 | 0.03777 | -60.951 | -0.18174 | -61.0323 | 61.3064 | 61.2709 | 61.3029 | -61.036 | -60.9828 | 0.073618 | -61.0906 | 61.1296 | 61.3166 | 61.0772 | -61.2089 | -0.034429 | 0.007246 | 0.050557 | -0.030724 | 0.003705 | -0.028185 | 0.003805 | -0.20735 | -0.16955 | 0.018798 | -0.088966 | 0.11839 | 0.017483 | -0.22198 | 122.308 | 122.2725 | 122.3045 | 60.8198 | -122.3351 | 122.1312 | 122.3182 | 122.0787 | 61.0752 | -122.5081
938.3125 | 122.5342 | -60.9467 | 61.409 | 1.4211e-13 | -0.0099957 | -0.011581 | 0.016157 | -0.037652 | 0.030381 | 0.0067908 | -0.01494 | 0.010448 | 0.034709 | -0.0028759 | 0.037983 | -60.9144 | -0.18632 | -60.9911 | 61.3522 | 61.3167 | 61.335 | -60.9811 | -60.9462 | 0.073618 | -61.0585 | 61.1799 | 61.3578 | 61.1184 | -61.1723 | -0.034414 | -0.056834 | 0.032252 | -0.044451 | -0.010037 | -0.092259 | -0.074008 | -0.22565 | -0.22905 | 0.000496 | -0.11185 | 0.11381 | -0.051174 | -0.29064 | 122.2988 | 122.2634 | 122.2816 | 60.7603 | -122.3901 | 122.1266 | 122.3045 | 122.065 | 61.0203 | -122.5813
940.0938 | 122.5433 | -60.9146 | 61.4548 | 1.4211e-13 | -0.0095683 | -0.011795 | 0.015943 | -0.038079 | 0.030381 | -0.00083919 | -0.014299 | 0.010234 | 0.034923 | -0.0024487 | 0.038197 | -60.8824 | -0.20005 | -60.9636 | 61.3796 | 61.3488 | 61.367 | -60.9582 | -60.9141 | 0.073618 | -61.0265 | 61.212 | 61.3899 | 61.1458 | -61.1311 | -0.043563 | -0.07514 | 0.032258 | -0.049024 | -0.005461 | -0.10598 | -0.087734 | -0.21649 | -0.24278 | 0.000504 | -0.11184 | 0.10465 | -0.0649 | -0.30894 | 122.2942 | 122.2634 | 122.2817 | 60.7146 | -122.4129 | 122.1266 | 122.3045 | 122.0604 | 60.9882 | -122.5859
941.8281 | 122.5845 | -60.878 | 61.4822 | 1.4211e-13 | -0.0097821 | -0.011581 | 0.015729 | -0.037865 | 0.030381 | 0.0067908 | -0.014299 | 0.010448 | 0.034709 | -0.0030897 | 0.037983 | -60.832 | -0.20005 | -60.9179 | 61.4208 | 61.4037 | 61.4128 | -60.9032 | -60.8729 | 0.078197 | -60.9715 | 61.2624 | 61.4402 | 61.2008 | -61.0853 | -0.025237 | -0.0614 | 0.045999 | -0.039863 | -0.014626 | -0.078502 | -0.069414 | -0.20732 | -0.21988 | 0.005091 | -0.093516 | 0.1138 | -0.042001 | -0.28147 | 122.2988 | 122.2817 | 122.2908 | 60.6779 | -122.3855 | 122.1404 | 122.3182 | 122.0788 | 60.9562 | -122.5676
943.6094 | 122.5983 | -60.8002 | 61.5189 | 1.4211e-13 | -0.0099957 | -0.011581 | 0.015729 | -0.037865 | 0.030381 | -0.00083919 | -0.014513 | 0.010448 | 0.034709 | -0.0028759 | 0.037983 | -60.7725 | -0.20921 | -60.8629 | 61.4849 | 61.4541 | 61.4723 | -60.8529 | -60.8134 | 0.078197 | -60.9166 | 61.3127 | 61.4952 | 61.2557 | -61.0304 | -0.052688 | -0.033924 | 0.027698 | -0.062743 | -0.010055 | -0.064755 | -0.046513 | -0.2302 | -0.20614 | -0.013206 | -0.11639 | 0.1138 | -0.023679 | -0.26314 | 122.2851 | 122.2543 | 122.2725 | 60.591 | -122.3717 | 122.1129 | 122.2954 | 122.0559 | 60.8784 | -122.5492
945.3906 | 122.4884 | -60.8047 | 61.5738 | 1.4211e-13 | -0.0099957 | -0.011368 | 0.016157 | -0.037652 | 0.029953 | -0.00083919 | -0.014299 | 0.010234 | 0.034709 | -0.0028759 | 0.037983 | -60.7725 | -0.21379 | -60.8538 | 61.4849 | 61.4587 | 61.4632 | -60.8483 | -60.7996 | 0.073618 | -60.912 | 61.3127 | 61.4998 | 61.2649 | -61.0304 | -0.043532 | -0.088856 | 0.032276 | -0.049009 | -0.005477 | -0.11511 | -0.1106 | -0.22562 | -0.26107 | 0.005108 | -0.10723 | 0.11838 | -0.074032 | -0.30892 | 122.2897 | 122.2634 | 122.2679 | 60.591 | -122.4221 | 122.1175 | 122.3045 | 122.0696 | 60.8784 | -122.6042
947.1562 | 122.5021 | -60.8002 | 61.5738 | 1.4211e-13 | -0.0095683 | -0.011795 | 0.015729 | -0.037865 | 0.030167 | -0.0084697 | -0.014299 | 0.009807 | 0.035136 | -0.0024487 | 0.037556 | -60.7679 | -0.22295 | -60.8492 | 61.4987 | 61.4678 | 61.4815 | -60.8391 | -60.7996 | 0.082776 | -60.9074 | 61.3265 | 61.5043 | 61.274 | -61.0212 | -0.038952 | -0.075121 | 0.032276 | -0.049008 | -0.010056 | -0.10595 | -0.092288 | -0.22104 | -0.24733 | 0.00053 | -0.10723 | 0.1138 | -0.069454 | -0.29976 | 122.2988 | 122.268 | 122.2817 | 60.5772 | -122.4129 | 122.1266 | 122.3045 | 122.0742 | 60.8829 | -122.595
948.875 | 122.5937 | -60.7636 | 61.5875 | 1.4211e-13 | -0.010209 | -0.011795 | 0.015943 | -0.037865 | 0.029953 | -0.0084697 | -0.014726 | 0.010234 | 0.034923 | -0.0026623 | 0.037556 | -60.6809 | -0.22295 | -60.7668 | 61.5765 | 61.5457 | 61.5548 | -60.7613 | -60.7218 | 0.078197 | -60.825 | 61.3997 | 61.5868 | 61.3702 | -60.9434 | 0.002269 | -0.01102 | 0.082645 | -0.00322 | -0.005489 | -0.04184 | -0.032762 | -0.17982 | -0.18781 | 0.041748 | -0.061438 | 0.11838 | -0.000771 | -0.21734 | 122.3401 | 122.3092 | 122.3183 | 60.5406 | -122.3488 | 122.1633 | 122.3503 | 122.1337 | 60.8417 | -122.5309
950.6562 | 122.5662 | -60.6628 | 61.6699 | 1.4211e-13 | -0.0099957 | -0.011795 | 0.015516 | -0.037865 | 0.030167 | -0.00083919 | -0.014513 | 0.010021 | 0.03535 | -0.0026623 | 0.03777 | -60.5985 | -0.2321 | -60.6844 | 61.6589 | 61.6281 | 61.6555 | -60.6789 | -60.6302 | 0.078197 | -60.738 | 61.4913 | 61.6692 | 61.4389 | -60.8564 | -0.016018 | -0.011007 | 0.064348 | -0.021519 | -0.005501 | -0.041818 | -0.014431 | -0.19353 | -0.17864 | 0.032614 | -0.075151 | 0.11838 | -0.000754 | -0.23106 | 122.3218 | 122.2909 | 122.3183 | 60.4307 | -122.3488 | 122.1541 | 122.332 | 122.1017 | 60.741 | -122.5263
952.4375 | 122.5937 | -60.5621 | 61.7432 | 1.4211e-13 | -0.0097821 | -0.012436 | 0.016157 | -0.037865 | 0.029953 | 0.0067908 | -0.014726 | 0.010234 | 0.034709 | -0.0028759 | 0.03777 | -60.5252 | -0.23668 | -60.6157 | 61.7322 | 61.6968 | 61.7287 | -60.601 | -60.5615 | 0.078197 | -60.6647 | 61.56 | 61.7424 | 61.5121 | -60.7831 | -0.038885 | -0.010995 | 0.036894 | -0.053553 | -0.014668 | -0.046376 | -0.014416 | -0.22098 | -0.1832 | 0.000586 | -0.1026 | 0.11838 | -0.000738 | -0.23105 | 122.2943 | 122.2589 | 122.2909 | 60.3255 | -122.3442 | 122.1221 | 122.3046 | 122.0743 | 60.6403 | -122.5263
954.2188 | 122.6257 | -60.585 | 61.7569 | 1.4211e-13 | -0.0099957 | -0.011795 | 0.015729 | -0.037438 | 0.02974 | -0.0084697 | -0.014726 | 0.010662 | 0.034709 | -0.0030897 | 0.038197 | -60.5207 | -0.24126 | -60.5928 | 61.7551 | 61.7243 | 61.7333 | -60.5964 | -60.5478 | 0.078197 | -60.651 | 61.5783 | 61.7607 | 61.5304 | -60.774 | -0.011418 | -0.001836 | 0.06436 | -0.007774 | 0.003644 | -0.032635 | -0.02357 | -0.18893 | -0.17862 | 0.037211 | -0.065975 | 0.12296 | 0.003843 | -0.22646 | 122.3401 | 122.3093 | 122.3183 | 60.3438 | -122.3533 | 122.1633 | 122.3458 | 122.1155 | 60.6632 | -122.5308
955.9688 | 122.5479 | -60.5255 | 61.8256 | 1.4211e-13 | -0.0099957 | -0.011795 | 0.015943 | -0.037438 | 0.030381 | -0.00083919 | -0.014513 | 0.010234 | 0.034923 | -0.0026623 | 0.03777 | -60.4566 | -0.255 | -60.5333 | 61.81 | 61.7838 | 61.7928 | -60.5278 | -60.4883 | 0.082776 | -60.5961 | 61.6378 | 61.8203 | 61.6083 | -60.7144 | -0.002243 | -0.01556 | 0.068949 | -0.007765 | -0.005522 | -0.041774 | -0.032713 | -0.18891 | -0.18776 | 0.037225 | -0.07054 | 0.11837 | -0.0053 | -0.21729 | 122.3355 | 122.3093 | 122.3184 | 60.2705 | -122.3533 | 122.1633 | 122.3458 | 122.1338 | 60.6083 | -122.54
957.7656 | 122.4976 | -60.5026 | 61.8851 | 1.4211e-13 | -0.0097821 | -0.012009 | 0.015943 | -0.037438 | 0.029953 | -0.00083919 | -0.014513 | 0.010021 | 0.035136 | -0.0028759 | 0.03777 | -60.4154 | -0.255 | -60.4967 | 61.8421 | 61.8113 | 61.8341 | -60.4911 | -60.4471 | 0.073618 | -60.564 | 61.6698 | 61.8615 | 61.6312 | -60.6732 | 0.011501 | -0.043021 | 0.087266 | 0.005973 | -0.005528 | -0.07381 | -0.051015 | -0.17059 | -0.21522 | 0.055545 | -0.061377 | 0.10922 | -0.023602 | -0.25391 | 122.3447 | 122.3139 | 122.3367 | 60.2476 | -122.3762 | 122.1725 | 122.3641 | 122.1338 | 60.5762 | -122.5583
959.5625 | 122.5159 | -60.4431 | 61.9217 | 1.4211e-13 | -0.0099957 | -0.011795 | 0.016157 | -0.037438 | 0.030167 | -0.00083919 | -0.014513 | 0.010662 | 0.034709 | -0.0026623 | 0.03777 | -60.4062 | -0.26415 | -60.4829 | 61.8558 | 61.825 | 61.8432 | -60.4728 | -60.4379 | 0.078197 | -60.5457 | 61.6882 | 61.8706 | 61.6403 | -60.6732 | -0.029694 | -0.065907 | 0.036913 | -0.039802 | -0.010108 | -0.096694 | -0.078478 | -0.2301 | -0.23353 | 0.005193 | -0.10257 | 0.12753 | -0.051065 | -0.28137 | 122.2989 | 122.2681 | 122.2863 | 60.179 | -122.3945 | 122.1313 | 122.3137 | 122.0834 | 60.5213 | -122.5949
961.2812 | 122.5113 | -60.466 | 61.972 | 1.4211e-13 | -0.0099957 | -0.011581 | 0.015943 | -0.037652 | 0.029953 | -0.0084697 | -0.014299 | 0.010021 | 0.034709 | -0.0026623 | 0.03777 | -60.3833 | -0.27331 | -60.46 | 61.8833 | 61.8479 | 61.8661 | -60.4545 | -60.4196 | 0.073618 | -60.5274 | 61.7065 | 61.8844 | 61.6541 | -60.6412 | 0.01151 | -0.08879 | 0.082693 | 0.005977 | -0.005533 | -0.12415 | -0.10594 | -0.17516 | -0.26557 | 0.046395 | -0.061369 | 0.11379 | -0.087684 | -0.31799 | 122.3493 | 122.3139 | 122.3321 | 60.1927 | -122.4265 | 122.1725 | 122.3504 | 122.1201 | 60.5396 | -122.6132
963.0781 | 122.5388 | -60.3745 | 62.0087 | 1.4211e-13 | -0.010209 | -0.011795 | 0.016157 | -0.038293 | 0.030167 | -0.00083919 | -0.014513 | 0.010234 | 0.034709 | -0.0024487 | 0.03777 | -60.3238 | -0.28247 | -60.4097 | 61.9245 | 61.9028 | 61.9165 | -60.4133 | -60.3692 | 0.073618 | -60.4724 | 61.7568 | 61.9393 | 61.709 | -60.5954 | -0.038832 | -0.084206 | 0.05066 | -0.035214 | 0.003618 | -0.10583 | -0.092196 | -0.22093 | -0.25183 | 0.005209 | -0.097977 | 0.12295 | -0.069361 | -0.29967 | 122.2989 | 122.2773 | 122.2909 | 60.092 | -122.422 | 122.1313 | 122.3138 | 122.0834 | 60.4481 | -122.604
964.8594 | 122.644 | -60.3195 | 61.9858 | 1.4211e-13 | -0.0099957 | -0.011581 | 0.015729 | -0.037865 | 0.030167 | -0.00083919 | -0.014299 | 0.010448 | 0.034496 | -0.0026623 | 0.037556 | -60.2734 | -0.29162 | -60.3593 | 61.984 | 61.9486 | 61.9714 | -60.3538 | -60.3189 | 0.073618 | -60.4221 | 61.8072 | 61.9897 | 61.7456 | -60.5404 | -0.034238 | -0.001799 | 0.04609 | -0.039784 | -0.005546 | -0.03715 | -0.014365 | -0.22091 | -0.17858 | 0.000643 | -0.10254 | 0.11837 | 0.003891 | -0.24015 | 122.3035 | 122.2681 | 122.2909 | 60.0279 | -122.3395 | 122.1267 | 122.3092 | 122.0651 | 60.3931 | -122.5262
966.6562 | 122.5891 | -60.3195 | 62.0087 | 1.4211e-13 | -0.0099957 | -0.012222 | 0.015943 | -0.037865 | 0.029953 | 0.0067908 | -0.014299 | 0.010021 | 0.034923 | -0.0026623 | 0.037342 | -60.2414 | -0.30078 | -60.3273 | 62.0115 | 61.9898 | 62.008 | -60.308 | -60.2822 | 0.073618 | -60.3763 | 61.8438 | 62.0355 | 61.796 | -60.4992 | 0.011552 | 0.002784 | 0.078139 | -0.007736 | -0.019288 | -0.018828 | -0.000624 | -0.1797 | -0.16484 | 0.037273 | -0.056756 | 0.12295 | 0.026789 | -0.21268 | 122.331 | 122.3094 | 122.3276 | 60.0187 | -122.3166 | 122.1633 | 122.355 | 122.1155 | 60.3931 | -122.5079
968.4375 | 122.6303 | -60.2921 | 62.0132 | 1.4211e-13 | -0.010423 | -0.011795 | 0.016157 | -0.037865 | 0.030167 | 0.0067908 | -0.014726 | 0.010448 | 0.034923 | -0.0024487 | 0.03777 | -60.2368 | -0.30994 | -60.3181 | 62.0206 | 61.9898 | 62.008 | -60.3125 | -60.2685 | 0.078197 | -60.3854 | 61.853 | 62.0263 | 61.796 | -60.5038 | -0.020493 | 0.007362 | 0.055251 | -0.026046 | -0.005553 | -0.023406 | -0.005202 | -0.21175 | -0.16026 | 0.023543 | -0.093379 | 0.11837 | 0.013054 | -0.21725 | 122.3127 | 122.2819 | 122.3001 | 59.9821 | -122.3258 | 122.145 | 122.3184 | 122.088 | 60.3703 | -122.517
970.1406 | 122.58 | -60.2646 | 62.0453 | 1.4211e-13 | -0.010209 | -0.012222 | 0.015943 | -0.037652 | 0.030381 | -0.00083919 | -0.01494 | 0.010234 | 0.034923 | -0.0026623 | 0.037556 | -60.2139 | -0.31452 | -60.2998 | 62.0481 | 62.0265 | 62.0447 | -60.2942 | -60.2548 | 0.078197 | -60.3625 | 61.8759 | 62.0629 | 61.8235 | -60.4718 | -0.029644 | 0.00279 | 0.050677 | -0.035199 | -0.005555 | -0.018817 | -0.000616 | -0.20716 | -0.16941 | 0.009813 | -0.097952 | 0.10921 | 0.01764 | -0.22183 | 122.3127 | 122.2911 | 122.3093 | 59.9501 | -122.3395 | 122.1405 | 122.3275 | 122.088 | 60.3428 | -122.517
971.9375 | 122.58 | -60.2646 | 62.0636 | 1.4211e-13 | -0.0099957 | -0.011795 | 0.015943 | -0.037652 | 0.030167 | -0.00083919 | -0.01494 | 0.010448 | 0.034709 | -0.0028759 | 0.037556 | -60.1635 | -0.33741 | -60.2494 | 62.0984 | 62.0585 | 62.0859 | -60.2439 | -60.209 | 0.06904 | -60.3122 | 61.9171 | 62.1087 | 61.8647 | -60.4305 | 0.020724 | 0.034841 | 0.10104 | 0.015162 | -0.005562 | -0.005076 | 0.02228 | -0.16595 | -0.14651 | 0.0556 | -0.047586 | 0.11837 | 0.045115 | -0.19893 | 122.363 | 122.3231 | 122.3505 | 59.9272 | -122.3075 | 122.1817 | 122.3733 | 122.1293 | 60.3336 | -122.4941
973.7344 | 122.5754 | -60.1364 | 62.1872 | 1.4211e-13 | -0.010209 | -0.012009 | 0.015943 | -0.037865 | 0.029953 | -0.00083919 | -0.014513 | 0.010021 | 0.034709 | -0.0024487 | 0.037342 | -60.0949 | -0.34657 | -60.1762 | 62.1763 | 62.1455 | 62.1637 | -60.1706 | -60.1266 | 0.082776 | -60.2389 | 61.9949 | 62.1865 | 61.9471 | -60.3481 | -0.034186 | -0.010922 | 0.041542 | -0.039758 | -0.005572 | -0.041672 | -0.023479 | -0.21171 | -0.19228 | 0.009844 | -0.1025 | 0.10921 | -0.000645 | -0.24011 | 122.3127 | 122.2819 | 122.3001 | 59.7898 | -122.3578 | 122.1313 | 122.323 | 122.0835 | 60.2192 | -122.5353
975.4531 | 122.5754 | -60.0403 | 62.2925 | 1.4211e-13 | -0.0099957 | -0.012009 | 0.015729 | -0.037652 | 0.030167 | -0.00083919 | -0.014513 | 0.010021 | 0.035136 | -0.0026623 | 0.037983 | -59.9941 | -0.35572 | -60.0754 | 62.2816 | 62.2463 | 62.2644 | -60.0699 | -60.0304 | 0.082776 | -60.1336 | 62.1002 | 62.2735 | 62.0524 | -60.252 | -0.02958 | -0.010905 | 0.046136 | -0.035167 | -0.005587 | -0.046221 | -0.028035 | -0.21168 | -0.19225 | 0.009866 | -0.09332 | 0.11836 | -0.018936 | -0.24009 | 122.3219 | 122.2865 | 122.3047 | 59.6846 | -122.3623 | 122.1405 | 122.3138 | 122.0927 | 60.1231 | -122.5444
977.2344 | 122.6349 | -60.022 | 62.3199 | 1.4211e-13 | -0.0097821 | -0.011795 | 0.016157 | -0.037652 | 0.030381 | 0.014421 | -0.014299 | 0.010234 | 0.034709 | -0.0026623 | 0.03777 | -59.9758 | -0.36488 | -60.0526 | 62.2816 | 62.2554 | 62.269 | -60.0561 | -60.0167 | 0.078197 | -60.1153 | 62.1094 | 62.3056 | 62.0799 | -60.2428 | -0.034154 | -0.038371 | 0.04614 | -0.030586 | 0.003568 | -0.064529 | -0.050922 | -0.22084 | -0.21056 | 0.005292 | -0.093315 | 0.12752 | -0.014352 | -0.24008 | 122.3035 | 122.2774 | 122.291 | 59.6571 | -122.3761 | 122.1314 | 122.3276 | 122.1018 | 60.1002 | -122.5628
978.9688 | 122.644 | -59.9945 | 62.3337 | 1.4211e-13 | -0.010209 | -0.011581 | 0.015943 | -0.037865 | 0.030167 | 0.0067908 | -0.014726 | 0.010234 | 0.034923 | -0.0022349 | 0.03777 | -59.9713 | -0.37862 | -60.0571 | 62.2907 | 62.26 | 62.2736 | -60.0378 | -60.0029 | 0.073618 | -60.1107 | 62.1185 | 62.3102 | 62.0661 | -60.2337 | -0.043304 | -0.042947 | 0.023252 | -0.06263 | -0.019326 | -0.073683 | -0.060077 | -0.23915 | -0.21514 | -0.008438 | -0.1162 | 0.12294 | -0.023507 | -0.26755 | 122.2852 | 122.2545 | 122.2681 | 59.6159 | -122.3715 | 122.113 | 122.3047 | 122.0606 | 60.0681 | -122.5673
980.7656 | 122.5754 | -59.9579 | 62.3932 | 1.4211e-13 | -0.010209 | -0.011795 | 0.015943 | -0.037652 | 0.029953 | 0.0067908 | -0.014726 | 0.010234 | 0.034923 | -0.0026623 | 0.037983 | -59.9163 | -0.3832 | -59.993 | 62.3503 | 62.3241 | 62.3331 | -59.992 | -59.9434 | 0.078197 | -60.0603 | 62.1689 | 62.3605 | 62.1211 | -60.1741 | -0.034136 | -0.042937 | 0.041572 | -0.035155 | -0.001019 | -0.069087 | -0.060064 | -0.21624 | -0.22429 | 0.014464 | -0.10246 | 0.11378 | -0.032651 | -0.27212 | 122.3081 | 122.282 | 122.291 | 59.5747 | -122.3852 | 122.1268 | 122.3184 | 122.079 | 60.0361 | -122.5673
982.5625 | 122.5433 | -60.022 | 62.3703 | 1.4211e-13 | -0.010209 | -0.012009 | 0.016157 | -0.037865 | 0.030167 | -0.00083919 | -0.014513 | 0.010234 | 0.035136 | -0.0022349 | 0.03777 | -59.9575 | -0.40609 | -60.0388 | 62.2999 | 62.2646 | 62.2919 | -60.0241 | -59.9938 | 0.073618 | -60.1061 | 62.1323 | 62.3193 | 62.0753 | -60.2245 | -0.002101 | -0.070411 | 0.064453 | -0.016851 | -0.01475 | -0.10572 | -0.078383 | -0.20252 | -0.23803 | 0.028185 | -0.084158 | 0.11836 | -0.05097 | -0.29501 | 122.3219 | 122.2865 | 122.3139 | 59.6159 | -122.3944 | 122.1542 | 122.3413 | 122.0973 | 60.0956 | -122.5948
984.3594 | 122.6257 | -59.8663 | 62.4252 | 1.4211e-13 | -0.0097821 | -0.012436 | 0.015729 | -0.037865 | 0.029953 | -0.00083919 | -0.014513 | 0.010234 | 0.034709 | -0.0024487 | 0.03777 | -59.8476 | -0.41525 | -59.9289 | 62.4143 | 62.3928 | 62.4064 | -59.9188 | -59.8885 | 0.073618 | -59.9917 | 62.2422 | 62.4246 | 62.1989 | -60.11 | -0.052426 | -0.010883 | 0.018694 | -0.062612 | -0.010186 | -0.032447 | -0.01885 | -0.24369 | -0.18307 | -0.022144 | -0.12533 | 0.11836 | -0.000595 | -0.22632 | 122.2807 | 122.2591 | 122.2727 | 59.4511 | -122.344 | 122.1085 | 122.291 | 122.0652 | 59.94 | -122.5353
986.0625 | 122.612 | -59.9213 | 62.384 | 1.4211e-13 | -0.0099957 | -0.012222 | 0.015516 | -0.037865 | 0.030167 | 0.014421 | -0.014299 | 0.010234 | 0.034923 | -0.0024487 | 0.03777 | -59.866 | -0.42898 | -59.9564 | 62.3869 | 62.3607 | 62.3743 | -59.9554 | -59.9068 | 0.078197 | -60.0237 | 62.2147 | 62.4017 | 62.1623 | -60.1329 | -0.034125 | 0.002845 | 0.055313 | -0.03515 | -0.001025 | -0.023301 | -0.009702 | -0.21165 | -0.16934 | 0.014473 | -0.10245 | 0.1092 | 0.017711 | -0.22175 | 122.3081 | 122.282 | 122.2956 | 59.4923 | -122.3394 | 122.136 | 122.323 | 122.0835 | 59.9995 | -122.517
987.8438 | 122.5021 | -59.8251 | 62.5351 | 1.4211e-13 | -0.0099957 | -0.012009 | 0.015729 | -0.037865 | 0.029953 | -0.00083919 | -0.014726 | 0.010448 | 0.034923 | -0.0024487 | 0.037342 | -59.7927 | -0.43814 | -59.8786 | 62.4647 | 62.4386 | 62.4613 | -59.8684 | -59.829 | 0.078197 | -59.9413 | 62.2971 | 62.475 | 62.2401 | -60.0551 | -0.043257 | -0.070384 | 0.032436 | -0.05345 | -0.010193 | -0.096521 | -0.07377 | -0.22994 | -0.23799 | -0.00382 | -0.11616 | 0.11378 | -0.060093 | -0.29498 | 122.2898 | 122.2637 | 122.2865 | 59.387 | -122.4035 | 122.1222 | 122.3001 | 122.0652 | 59.9033 | -122.5902
989.6406 | 122.5388 | -59.8114 | 62.5809 | 1.4211e-13 | -0.0097821 | -0.012222 | 0.016157 | -0.037652 | 0.030167 | -0.0084697 | -0.014085 | 0.010021 | 0.034709 | -0.0024487 | 0.037342 | -59.7378 | -0.45645 | -59.8145 | 62.5288 | 62.5118 | 62.5163 | -59.7997 | -59.7832 | 0.073618 | -59.8772 | 62.3658 | 62.5483 | 62.3042 | -59.9956 | 0.011694 | -0.052064 | 0.073644 | -0.003087 | -0.014781 | -0.069035 | -0.064604 | -0.18415 | -0.21509 | 0.028234 | -0.065794 | 0.11836 | -0.032612 | -0.27665 | 122.3402 | 122.3232 | 122.3277 | 59.3549 | -122.3806 | 122.1772 | 122.3597 | 122.1156 | 59.885 | -122.5764
991.3594 | 122.612 | -59.7565 | 62.5763 | 1.4211e-13 | -0.010209 | -0.012009 | 0.015729 | -0.038079 | 0.030167 | -0.00083919 | -0.014513 | 0.010021 | 0.034496 | -0.0024487 | 0.03777 | -59.724 | -0.46103 | -59.8053 | 62.5334 | 62.5027 | 62.5254 | -59.7997 | -59.7694 | 0.078197 | -59.868 | 62.3566 | 62.5574 | 62.3042 | -59.991 | -0.043237 | -0.042907 | 0.032448 | -0.048862 | -0.005625 | -0.073615 | -0.050869 | -0.2345 | -0.21967 | -0.012961 | -0.11157 | 0.12294 | -0.018877 | -0.27208 | 122.2899 | 122.2591 | 122.2819 | 59.2954 | -122.376 | 122.1131 | 122.3139 | 122.0607 | 59.8347 | -122.5673
993.1562 | 122.5204 | -59.729 | 62.6129 | 1.4211e-13 | -0.0099957 | -0.011368 | 0.015943 | -0.037652 | 0.030167 | -0.0084697 | -0.014513 | 0.010234 | 0.035136 | -0.0022349 | 0.037556 | -59.6828 | -0.47935 | -59.7733 | 62.57 | 62.5347 | 62.5621 | -59.7631 | -59.7282 | 0.073618 | -59.8406 | 62.3978 | 62.594 | 62.3592 | -59.9543 | -0.034071 | -0.042901 | 0.046187 | -0.04428 | -0.010209 | -0.078184 | -0.050861 | -0.22534 | -0.21509 | 0.000782 | -0.11156 | 0.11378 | -0.018869 | -0.25375 | 122.299 | 122.2637 | 122.2911 | 59.2497 | -122.376 | 122.1268 | 122.323 | 122.0882 | 59.8026 | -122.5673
994.9531 | 122.5021 | -59.6695 | 62.7365 | 1.4211e-13 | -0.0097821 | -0.012009 | 0.015943 | -0.038079 | 0.030167 | -0.00083919 | -0.014726 | 0.010021 | 0.035136 | -0.0020213 | 0.037556 | -59.6325 | -0.49766 | -59.7229 | 62.6295 | 62.5851 | 62.6124 | -59.7081 | -59.6779 | 0.078197 | -59.7856 | 62.4573 | 62.6444 | 62.3866 | -59.8948 | -0.038633 | -0.10698 | 0.037041 | -0.053427 | -0.014794 | -0.15141 | -0.12409 | -0.22532 | -0.27916 | -0.008362 | -0.11613 | 0.1092 | -0.092101 | -0.34988 | 122.299 | 122.2546 | 122.2819 | 59.1718 | -122.4446 | 122.1268 | 122.3139 | 122.0561 | 59.7477 | -122.6313
996.6875 | 122.5891 | -59.6832 | 62.6404 | 1.4211e-13 | -0.010423 | -0.011795 | 0.015943 | -0.037652 | 0.029953 | -0.0084697 | -0.014513 | 0.010448 | 0.034923 | -0.0022349 | 0.03777 | -59.605 | -0.48392 | -59.6863 | 62.6524 | 62.6263 | 62.6399 | -59.6761 | -59.6412 | 0.073618 | -59.749 | 62.4802 | 62.6765 | 62.4233 | -59.8673 | 0.007152 | 0.012044 | 0.078244 | -0.003068 | -0.01022 | -0.014071 | -0.000491 | -0.18412 | -0.16014 | 0.042001 | -0.065763 | 0.11836 | 0.03608 | -0.21712 | 122.3357 | 122.3095 | 122.3231 | 59.1993 | -122.3165 | 122.1635 | 122.3597 | 122.1065 | 59.7568 | -122.5077
998.4844 | 122.58 | -59.523 | 62.7914 | 1.4211e-13 | -0.010423 | -0.012009 | 0.015729 | -0.037865 | 0.030167 | -0.00083919 | -0.014513 | 0.010448 | 0.035136 | -0.0022349 | 0.03777 | -59.4997 | -0.48392 | -59.5764 | 62.7623 | 62.7362 | 62.7498 | -59.5799 | -59.5405 | 0.078197 | -59.6483 | 62.5947 | 62.7726 | 62.5606 | -59.7529 | -0.056908 | -0.029137 | 0.023329 | -0.053407 | 0.003501 | -0.055239 | -0.041666 | -0.22987 | -0.19674 | -0.017485 | -0.12525 | 0.10462 | -0.018832 | -0.23083 | 122.2853 | 122.2592 | 122.2728 | 59.0391 | -122.3714 | 122.1177 | 122.2956 | 122.0836 | 59.6012 | -122.5443
1000.2656 | 122.525 | -59.436 | 62.9425 | 1.4211e-13 | -0.010637 | -0.012009 | 0.015943 | -0.038079 | 0.029953 | -0.0084697 | -0.014513 | 0.010021 | 0.034496 | -0.0026623 | 0.03777 | -59.3898 | -0.49766 | -59.4711 | 62.8676 | 62.8415 | 62.8551 | -59.47 | -59.4306 | 0.078197 | -59.5384 | 62.6954 | 62.8871 | 62.6568 | -59.6567 | -0.033989 | -0.074896 | 0.046235 | -0.035082 | -0.001093 | -0.10099 | -0.08742 | -0.22069 | -0.24707 | 0.005429 | -0.10234 | 0.11835 | -0.055429 | -0.28574 | 122.3036 | 122.2776 | 122.2911 | 58.9384 | -122.4125 | 122.1315 | 122.3231 | 122.0928 | 59.5142 | -122.5992
1002.0625 | 122.5983 | -59.5139 | 62.8189 | 1.4211e-13 | -0.010209 | -0.012009 | 0.015729 | -0.037652 | 0.030167 | 0.0067908 | -0.014726 | 0.010021 | 0.034709 | -0.0020213 | 0.037556 | -59.4676 | -0.5114 | -59.5535 | 62.8081 | 62.7728 | 62.7864 | -59.5433 | -59.4993 | 0.073618 | -59.6071 | 62.6222 | 62.8184 | 62.6018 | -59.7254 | -0.029432 | -0.010819 | 0.046223 | -0.039671 | -0.010239 | -0.046073 | -0.032503 | -0.21155 | -0.19673 | 0.014568 | -0.093196 | 0.11835 | -0.000512 | -0.21708 | 122.3219 | 122.2867 | 122.3003 | 59.0025 | -122.3622 | 122.136 | 122.3323 | 122.1157 | 59.5875 | -122.5443
1003.7812 | 122.4609 | -59.4406 | 62.9562 | 1.4211e-13 | -0.010209 | -0.012009 | 0.016157 | -0.038079 | 0.030594 | 0.0067908 | -0.014726 | 0.010234 | 0.034709 | -0.0022349 | 0.037342 | -59.3761 | -0.5526 | -59.462 | 62.8905 | 62.8598 | 62.878 | -59.4426 | -59.4077 | 0.082776 | -59.5201 | 62.7137 | 62.9008 | 62.6613 | -59.6338 | -0.001938 | -0.065737 | 0.064548 | -0.021347 | -0.019409 | -0.096403 | -0.07826 | -0.19321 | -0.24249 | 0.0329 | -0.079443 | 0.11377 | -0.055426 | -0.29489 | 122.3311 | 122.3004 | 122.3186 | 58.888 | -122.3988 | 122.1544 | 122.3414 | 122.102 | 59.5234 | -122.5901
1005.5781 | 122.5021 | -59.2804 | 63.121 | 1.4211e-13 | -0.010209 | -0.011795 | 0.015943 | -0.038079 | 0.029526 | -0.00083919 | -0.014726 | 0.010021 | 0.034709 | -0.0022349 | 0.037342 | -59.2204 | -0.58008 | -59.3063 | 63.0416 | 63.0109 | 63.0245 | -59.3006 | -59.2566 | 0.082776 | -59.3735 | 62.8557 | 63.0565 | 62.8124 | -59.4827 | -0.020208 | -0.079445 | 0.059997 | -0.025903 | -0.005695 | -0.11009 | -0.09654 | -0.20233 | -0.26536 | 0.023781 | -0.093141 | 0.10919 | -0.064548 | -0.30859 | 122.322 | 122.2913 | 122.3049 | 58.7003 | -122.4216 | 122.1361 | 122.3369 | 122.0928 | 59.3632 | -122.6038
1007.375 | 122.5342 | -59.3262 | 63.1027 | 1.4211e-13 | -0.010209 | -0.011795 | 0.015729 | -0.037865 | 0.029953 | -0.00083919 | -0.014513 | 0.010021 | 0.034496 | -0.0024487 | 0.03777 | -59.2387 | -0.61213 | -59.3246 | 63.0233 | 62.9972 | 63.0062 | -59.3143 | -59.2749 | 0.073618 | -59.3919 | 62.8511 | 63.0382 | 62.8216 | -59.5056 | 0.011831 | -0.079448 | 0.087459 | 0.00156 | -0.010271 | -0.10552 | -0.096543 | -0.17945 | -0.25162 | 0.051242 | -0.06568 | 0.11377 | -0.064552 | -0.28112 | 122.3494 | 122.3234 | 122.3324 | 58.714 | -122.4171 | 122.1773 | 122.3643 | 122.1478 | 59.3998 | -122.6083
1009.1719 | 122.5662 | -59.2117 | 63.1119 | 1.4211e-13 | -0.010209 | -0.011581 | 0.015943 | -0.038293 | 0.030381 | -0.00083919 | -0.014726 | 0.010234 | 0.034709 | -0.0024487 | 0.037983 | -59.1471 | -0.63502 | -59.2285 | 63.1286 | 63.0888 | 63.1069 | -59.2319 | -59.1879 | 0.082776 | -59.2865 | 62.9472 | 63.1297 | 62.9406 | -59.4049 | -0.020189 | 0.0167 | 0.064586 | -0.016737 | 0.003452 | -0.023096 | -0.004969 | -0.19315 | -0.16463 | 0.023796 | -0.074811 | 0.11834 | 0.017865 | -0.17124 | 122.3403 | 122.3005 | 122.3186 | 58.5767 | -122.3438 | 122.159 | 122.3415 | 122.1524 | 59.2945 | -122.5168
1010.9062 | 122.5342 | -59.166 | 63.2217 | 1.4211e-13 | -0.010209 | -0.011581 | 0.015729 | -0.038079 | 0.02974 | -0.00083919 | -0.014726 | 0.010021 | 0.034709 | -0.0024487 | 0.03777 | -59.1243 | -0.66707 | -59.2102 | 63.1332 | 63.1071 | 63.1252 | -59.1953 | -59.165 | 0.06904 | -59.2728 | 62.961 | 63.1526 | 62.904 | -59.3911 | -0.029334 | -0.088585 | 0.041702 | -0.0442 | -0.014866 | -0.11464 | -0.096519 | -0.22519 | -0.26076 | 0.000914 | -0.10685 | 0.11834 | -0.069106 | -0.31773 | 122.2991 | 122.2731 | 122.2912 | 58.4989 | -122.417 | 122.1269 | 122.3186 | 122.07 | 59.235 | -122.6129
1012.6875 | 122.6166 | -59.079 | 63.2263 | 1.4211e-13 | -0.0097821 | -0.011795 | 0.015943 | -0.038079 | 0.030167 | -0.00083919 | -0.01494 | 0.010021 | 0.034709 | -0.0024487 | 0.037983 | -59.0418 | -0.69454 | -59.1277 | 63.2293 | 63.1987 | 63.2076 | -59.1129 | -59.0826 | 0.073618 | -59.195 | 63.0526 | 63.2396 | 62.991 | -59.3042 | -0.033889 | 0.002984 | 0.037137 | -0.048767 | -0.014878 | -0.027642 | -0.018681 | -0.22517 | -0.17377 | -0.003645 | -0.11599 | 0.10918 | 0.013311 | -0.23531 | 122.3083 | 122.2777 | 122.2866 | 58.3844 | -122.3392 | 122.1315 | 122.3186 | 122.07 | 59.1526 | -122.5305
1014.4688 | 122.4838 | -59.0836 | 63.2904 | 1.4211e-13 | -0.010423 | -0.012009 | 0.015516 | -0.037652 | 0.030167 | 0.0067908 | -0.014299 | 0.010234 | 0.034709 | -0.0022349 | 0.037556 | -59.0647 | -0.72201 | -59.1461 | 63.2064 | 63.1712 | 63.1847 | -59.1403 | -59.1055 | 0.073618 | -59.1995 | 63.0251 | 63.2122 | 62.9727 | -59.3179 | -0.056785 | -0.083995 | 0.018823 | -0.062502 | -0.005717 | -0.1192 | -0.10566 | -0.23433 | -0.26532 | -0.021961 | -0.11599 | 0.11834 | -0.078248 | -0.31771 | 122.29 | 122.2548 | 122.2683 | 58.3615 | -122.4307 | 122.1086 | 122.2957 | 122.0562 | 59.1572 | -122.6083
1016.1719 | 122.4747 | -59.1614 | 63.2492 | 1.4211e-13 | -0.010209 | -0.012009 | 0.015729 | -0.037865 | 0.029953 | -0.00083919 | -0.014085 | 0.010021 | 0.034923 | -0.0024487 | 0.037556 | -59.0647 | -0.77696 | -59.1506 | 63.2018 | 63.1666 | 63.1802 | -59.1449 | -59.1101 | 0.06904 | -59.2133 | 63.0251 | 63.2076 | 62.9681 | -59.327 | 0.016456 | -0.047376 | 0.096643 | 0.01074 | -0.005716 | -0.082584 | -0.069042 | -0.16567 | -0.22413 | 0.05128 | -0.051905 | 0.11376 | -0.041629 | -0.28109 | 122.3632 | 122.328 | 122.3415 | 58.3844 | -122.3941 | 122.1865 | 122.369 | 122.1295 | 59.2304 | -122.5763
1017.9531 | 122.4655 | -59.0515 | 63.3453 | 1.4211e-13 | -0.010423 | -0.012009 | 0.015729 | -0.038079 | 0.02974 | 0.0067908 | -0.014726 | 0.010234 | 0.034709 | -0.0020213 | 0.037556 | -59.0006 | -0.78611 | -59.082 | 63.2568 | 63.2261 | 63.2534 | -59.0717 | -59.0414 | 0.073618 | -59.1538 | 63.08 | 63.2854 | 63.0322 | -59.2629 | -0.020144 | -0.088565 | 0.050877 | -0.030449 | -0.010305 | -0.11919 | -0.091914 | -0.21143 | -0.26531 | 0.010098 | -0.10225 | 0.10918 | -0.059922 | -0.31312 | 122.3083 | 122.2777 | 122.3049 | 58.2654 | -122.417 | 122.1315 | 122.3369 | 122.0837 | 59.1251 | -122.6083
1019.75 | 122.6028 | -59.0378 | 63.2492 | 1.4211e-13 | -0.010637 | -0.012009 | 0.015729 | -0.038293 | 0.029953 | -0.00083919 | -0.014726 | 0.010021 | 0.034923 | -0.0022349 | 0.038197 | -58.9869 | -0.88226 | -59.0774 | 63.2842 | 63.2536 | 63.2626 | -59.0671 | -59.0277 | 0.073618 | -59.1354 | 63.1075 | 63.2946 | 63.0551 | -59.2492 | -0.029298 | 0.035035 | 0.050879 | -0.039604 | -0.010306 | 0.004416 | 0.013373 | -0.21142 | -0.14171 | 0.010101 | -0.097663 | 0.11376 | 0.045365 | -0.1941 | 122.322 | 122.2914 | 122.3004 | 58.1555 | -122.3163 | 122.1453 | 122.3324 | 122.0929 | 59.1114 | -122.4984
1021.4844 | 122.4792 | -58.9966 | 63.4094 | 1.4211e-13 | -0.01085 | -0.011795 | 0.015943 | -0.037865 | 0.029953 | -0.0084697 | -0.014726 | 0.010448 | 0.034923 | -0.0020213 | 0.03777 | -58.9182 | -0.90973 | -59.0041 | 63.3438 | 63.3131 | 63.3358 | -58.9892 | -58.9544 | 0.06904 | -59.0622 | 63.167 | 63.3633 | 63.1604 | -59.1759 | 0.007345 | -0.065663 | 0.078356 | -0.00755 | -0.014895 | -0.096275 | -0.073586 | -0.17936 | -0.24241 | 0.042162 | -0.065603 | 0.11376 | -0.046173 | -0.24901 | 122.3403 | 122.3097 | 122.3324 | 58.0868 | -122.3987 | 122.1636 | 122.3598 | 122.157 | 59.0656 | -122.5854
1023.2969 | 122.4976 | -58.9645 | 63.414 | 1.4211e-13 | -0.010209 | -0.012222 | 0.015729 | -0.038293 | 0.029953 | -0.00083919 | -0.014726 | 0.010234 | 0.034923 | -0.0022349 | 0.037129 | -58.9091 | -0.90973 | -59.0087 | 63.3529 | 63.3131 | 63.3358 | -58.9847 | -58.959 | 0.06904 | -59.0622 | 63.167 | 63.3678 | 63.1284 | -59.1759 | -0.020119 | -0.061083 | 0.05547 | -0.044172 | -0.024053 | -0.10085 | -0.078163 | -0.21141 | -0.24699 | 0.00554 | -0.097646 | 0.11376 | -0.046171 | -0.28564 | 122.3175 | 122.2777 | 122.3004 | 58.0548 | -122.3987 | 122.1316 | 122.3324 | 122.0929 | 59.0336 | -122.5899
1025.0156 | 122.525 | -58.9279 | 63.4277 | 1.4211e-13 | -0.010637 | -0.012009 | 0.015516 | -0.037865 | 0.029953 | 0.0067908 | -0.014299 | 0.010234 | 0.034923 | -0.0024487 | 0.037556 | -58.8587 | -0.92805 | -58.94 | 63.4079 | 63.3773 | 63.3954 | -58.9297 | -58.8995 | 0.073618 | -59.0164 | 63.2357 | 63.4182 | 63.1879 | -59.121 | -0.001794 | -0.019875 | 0.06921 | -0.012119 | -0.010325 | -0.05048 | -0.032374 | -0.19308 | -0.19204 | 0.028441 | -0.088481 | 0.1046 | -0.00954 | -0.23985 | 122.3358 | 122.3052 | 122.3233 | 57.9999 | -122.3574 | 122.1636 | 122.3461 | 122.1158 | 59.0015 | -122.5487
1026.7969 | 122.5983 | -58.7952 | 63.5147 | 1.4211e-13 | -0.010209 | -0.011795 | 0.015943 | -0.038079 | 0.029953 | 0.014421 | -0.014726 | 0.010234 | 0.034709 | -0.0020213 | 0.037342 | -58.7763 | -0.9601 | -58.8576 | 63.4811 | 63.4597 | 63.4686 | -58.8519 | -58.8125 | 0.073618 | -58.9294 | 63.3135 | 63.496 | 63.2566 | -59.0386 | -0.056703 | -0.033596 | 0.01887 | -0.062461 | -0.005758 | -0.055035 | -0.046092 | -0.24341 | -0.20118 | -0.017314 | -0.13424 | 0.10918 | -0.018679 | -0.25814 | 122.2763 | 122.2548 | 122.2638 | 57.8351 | -122.3666 | 122.1087 | 122.2912 | 122.0517 | 58.8688 | -122.5533
1028.5938 | 122.5937 | -58.7357 | 63.6063 | 1.4211e-13 | -0.010423 | -0.012009 | 0.015729 | -0.038079 | 0.02974 | -0.00083919 | -0.014726 | 0.010234 | 0.035136 | -0.0020213 | 0.037556 | -58.7122 | -1.0013 | -58.7981 | 63.5498 | 63.51 | 63.5373 | -58.7878 | -58.753 | 0.073618 | -58.8653 | 63.373 | 63.5647 | 63.3298 | -58.9745 | -0.052108 | -0.056473 | 0.023459 | -0.062453 | -0.010345 | -0.09622 | -0.068966 | -0.23882 | -0.23322 | -0.0173 | -0.12964 | 0.10918 | -0.041553 | -0.27644 | 122.2854 | 122.2457 | 122.273 | 57.7344 | -122.394 | 122.1087 | 122.3004 | 122.0655 | 58.8093 | -122.5807
1030.375 | 122.4884 | -58.8455 | 63.5925 | 1.4211e-13 | -0.010637 | -0.011581 | 0.015943 | -0.038293 | 0.029953 | -0.00083919 | -0.014299 | 0.010234 | 0.034923 | -0.0020213 | 0.037556 | -58.7488 | -1.0608 | -58.8302 | 63.5177 | 63.4871 | 63.5098 | -58.8152 | -58.785 | 0.06904 | -58.8928 | 63.3456 | 63.5327 | 63.3069 | -59.0111 | 0.030282 | -0.074789 | 0.096695 | 0.015362 | -0.01492 | -0.10538 | -0.082704 | -0.16559 | -0.24695 | 0.060512 | -0.047253 | 0.11833 | -0.05987 | -0.2856 | 122.3633 | 122.3327 | 122.3553 | 57.7847 | -122.4078 | 122.1911 | 122.3782 | 122.1525 | 58.9146 | -122.6036
1032.1562 | 122.493 | -58.7219 | 63.6566 | 1.4211e-13 | -0.010637 | -0.011581 | 0.015943 | -0.038079 | 0.029953 | -0.00083919 | -0.01494 | 0.010234 | 0.035136 | -0.0020213 | 0.037556 | -58.6481 | -1.07 | -58.7294 | 63.6139 | 63.5879 | 63.606 | -58.7145 | -58.6934 | 0.06904 | -58.8012 | 63.4371 | 63.638 | 63.4397 | -58.9058 | 0.007422 | -0.04273 | 0.073823 | -0.007512 | -0.014934 | -0.068732 | -0.050641 | -0.18387 | -0.21947 | 0.02849 | -0.079275 | 0.1046 | -0.018649 | -0.21691 | 122.3358 | 122.3098 | 122.3279 | 57.6519 | -122.3711 | 122.1591 | 122.3599 | 122.1616 | 58.791 | -122.5624
1033.875 | 122.5342 | -58.6395 | 63.7115 | 1.4211e-13 | -0.010209 | -0.011795 | 0.015729 | -0.038079 | 0.02974 | 0.0067908 | -0.014726 | 0.009807 | 0.034709 | -0.0018077 | 0.037342 | -58.6252 | -1.0883 | -58.7065 | 63.6414 | 63.6062 | 63.6289 | -58.6916 | -58.6705 | 0.078197 | -58.7737 | 63.4646 | 63.6609 | 63.4351 | -58.8875 | -0.052081 | -0.070191 | 0.014317 | -0.067018 | -0.014937 | -0.10535 | -0.08268 | -0.24795 | -0.24693 | -0.031014 | -0.1342 | 0.11375 | -0.050688 | -0.27642 | 122.2809 | 122.2457 | 122.2684 | 57.5512 | -122.4032 | 122.1041 | 122.3004 | 122.0747 | 58.7177 | -122.599
1035.6719 | 122.5616 | -58.5846 | 63.7344 | 1.4211e-13 | -0.010637 | -0.011795 | 0.015729 | -0.038293 | 0.030167 | -0.00083919 | -0.014726 | 0.010021 | 0.034709 | -0.0018077 | 0.037342 | -58.5748 | -1.1387 | -58.6516 | 63.6917 | 63.6657 | 63.6884 | -58.6458 | -58.6202 | 0.078197 | -58.7188 | 63.515 | 63.7158 | 63.5359 | -58.8371 | -0.061223 | -0.042717 | 0.009748 | -0.06701 | -0.005787 | -0.06871 | -0.046046 | -0.25252 | -0.21946 | -0.03558 | -0.13419 | 0.11833 | -0.018633 | -0.19858 | 122.2763 | 122.2503 | 122.273 | 57.4459 | -122.3803 | 122.0996 | 122.3004 | 122.1205 | 58.6628 | -122.5715
1037.4688 | 122.612 | -58.4702 | 63.8214 | 1.4211e-13 | -0.010637 | -0.011795 | 0.016157 | -0.038079 | 0.030167 | 0.0067908 | -0.014299 | 0.010234 | 0.034923 | -0.0020213 | 0.037556 | -58.465 | -1.1799 | -58.5417 | 63.8108 | 63.7848 | 63.7983 | -58.5268 | -58.4965 | 0.073618 | -58.6043 | 63.6249 | 63.8257 | 63.6183 | -58.7181 | -0.056612 | -0.010654 | 0.005189 | -0.071572 | -0.01496 | -0.036633 | -0.023134 | -0.24791 | -0.19655 | -0.026395 | -0.13416 | 0.11375 | 0.004279 | -0.20314 | 122.2809 | 122.2549 | 122.2684 | 57.2903 | -122.3482 | 122.095 | 122.2958 | 122.0884 | 58.5438 | -122.5395
1039.25 | 122.525 | -58.4106 | 63.945 | 1.4211e-13 | -0.010423 | -0.011795 | 0.015729 | -0.038079 | 0.030167 | -0.00083919 | -0.014513 | 0.010234 | 0.034709 | -0.0022349 | 0.037556 | -58.3688 | -1.2073 | -58.4547 | 63.8932 | 63.8718 | 63.8853 | -58.4398 | -58.4141 | 0.06904 | -58.5173 | 63.7119 | 63.9127 | 63.6641 | -58.6311 | -0.029121 | -0.051839 | 0.041826 | -0.044094 | -0.014973 | -0.07323 | -0.059737 | -0.22042 | -0.23315 | -0.003488 | -0.10667 | 0.11375 | -0.032324 | -0.28095 | 122.3038 | 122.2824 | 122.2959 | 57.2033 | -122.3848 | 122.1225 | 122.3233 | 122.0747 | 58.4797 | -122.5761
1040.9688 | 122.4884 | -58.4106 | 63.9999 | 1.4211e-13 | -0.010637 | -0.012009 | 0.015943 | -0.038079 | 0.029953 | -0.00083919 | -0.014513 | 0.010234 | 0.034923 | -0.0024487 | 0.037556 | -58.3276 | -1.244 | -58.4135 | 63.939 | 63.9084 | 63.9173 | -58.3986 | -58.3729 | 0.078197 | -58.4715 | 63.7622 | 63.9493 | 63.7556 | -58.5853 | 0.012089 | -0.060987 | 0.083031 | -0.002889 | -0.014978 | -0.09153 | -0.082619 | -0.17463 | -0.23772 | 0.037721 | -0.060886 | 0.11375 | -0.050627 | -0.2443 | 122.3496 | 122.3191 | 122.328 | 57.1667 | -122.3985 | 122.1729 | 122.36 | 122.1663 | 58.4888 | -122.5852
1042.7812 | 122.6212 | -58.2733 | 64.0549 | 1.4211e-13 | -0.010637 | -0.011795 | 0.015943 | -0.038079 | 0.030381 | 0.0067908 | -0.014513 | 0.010234 | 0.034923 | -0.0022349 | 0.037342 | -58.2315 | -1.2577 | -58.3128 | 64.0351 | 64.0046 | 64.0226 | -58.3024 | -58.2676 | 0.078197 | -58.3754 | 63.8584 | 64.05 | 63.8564 | -58.4845 | -0.029084 | -0.019773 | 0.041847 | -0.039497 | -0.010413 | -0.050305 | -0.032243 | -0.21123 | -0.1965 | 0.005701 | -0.10206 | 0.10916 | -0.00483 | -0.19851 | 122.3084 | 122.2779 | 122.2959 | 57.0156 | -122.3573 | 122.1317 | 122.3234 | 122.1297 | 58.3515 | -122.5394
1044.5 | 122.4792 | -58.0811 | 64.2929 | 1.4211e-13 | -0.010423 | -0.011581 | 0.015729 | -0.037865 | 0.029953 | -0.0084697 | -0.014513 | 0.010234 | 0.034923 | -0.0020213 | 0.037556 | -58.0438 | -1.2989 | -58.1297 | 64.2182 | 64.1969 | 64.2149 | -58.1192 | -58.089 | 0.078197 | -58.1968 | 64.0461 | 64.2423 | 64.012 | -58.3014 | -0.038187 | -0.074674 | 0.037301 | -0.048626 | -0.010439 | -0.096027 | -0.077978 | -0.22034 | -0.24682 | -0.007989 | -0.11575 | 0.10458 | -0.050565 | -0.28087 | 122.2993 | 122.2779 | 122.296 | 56.7821 | -122.4121 | 122.1271 | 122.3234 | 122.0931 | 58.1593 | -122.5943
1046.2812 | 122.58 | -57.8934 | 64.4394 | 1.4211e-13 | -0.010423 | -0.011795 | 0.015729 | -0.038079 | 0.030167 | 0.0067908 | -0.01494 | 0.010448 | 0.034923 | -0.0020213 | 0.03777 | -57.8606 | -1.3493 | -57.9374 | 64.4059 | 64.38 | 64.4027 | -57.9269 | -57.8967 | 0.078197 | -58.0137 | 64.243 | 64.4255 | 64.241 | -58.1137 | -0.033555 | -0.033445 | 0.032754 | -0.044021 | -0.010466 | -0.059354 | -0.03674 | -0.22029 | -0.19643 | -0.003366 | -0.12029 | 0.099999 | -0.013905 | -0.19843 | 122.2993 | 122.2734 | 122.296 | 56.5441 | -122.3663 | 122.1363 | 122.3189 | 122.1343 | 57.9716 | -122.5531
1048.0938 | 122.5571 | -57.7515 | 64.6042 | 1.4211e-13 | -0.010637 | -0.011795 | 0.015943 | -0.038293 | 0.030381 | 0.0067908 | -0.014513 | 0.010021 | 0.034709 | -0.0015939 | 0.037556 | -57.7095 | -1.3905 | -57.7909 | 64.557 | 64.5357 | 64.5446 | -57.7804 | -57.7411 | 0.073618 | -57.8626 | 64.3803 | 64.572 | 64.4012 | -57.9671 | -0.028936 | -0.047153 | 0.041934 | -0.039423 | -0.010487 | -0.068466 | -0.059598 | -0.21567 | -0.22387 | 0.010403 | -0.1111 | 0.10457 | -0.032185 | -0.20297 | 122.3085 | 122.2872 | 122.2961 | 56.361 | -122.3846 | 122.1318 | 122.3235 | 122.1527 | 57.8251 | -122.5713
1049.8125 | 122.5616 | -57.6279 | 64.7278 | 1.4211e-13 | -0.010637 | -0.012009 | 0.015943 | -0.038506 | 0.030381 | -0.023731 | -0.014726 | 0.010021 | 0.034923 | -0.0018077 | 0.03777 | -57.6134 | -1.4454 | -57.6902 | 64.6669 | 64.6273 | 64.6545 | -57.6705 | -57.6449 | 0.073618 | -57.7481 | 64.4856 | 64.6773 | 64.4653 | -57.8664 | -0.042638 | -0.060867 | 0.014484 | -0.062297 | -0.019659 | -0.10048 | -0.073308 | -0.23853 | -0.24216 | -0.01704 | -0.12023 | 0.11831 | -0.050473 | -0.26247 | 122.2948 | 122.2552 | 122.2823 | 56.1824 | -122.3983 | 122.1135 | 122.3052 | 122.0932 | 57.7015 | -122.5942
1051.5938 | 122.4884 | -57.5729 | 64.8376 | 1.4211e-13 | -0.010209 | -0.011581 | 0.015943 | -0.038079 | 0.02974 | 0.014421 | -0.01494 | 0.010234 | 0.034709 | -0.0020213 | 0.037556 | -57.5218 | -1.4775 | -57.6032 | 64.7447 | 64.7235 | 64.7323 | -57.5881 | -57.5716 | 0.078197 | -57.6748 | 64.5726 | 64.7597 | 64.5889 | -57.784 | -0.015149 | -0.092898 | 0.051119 | -0.030242 | -0.015093 | -0.11419 | -0.10533 | -0.21105 | -0.26503 | 0.001287 | -0.1019 | 0.10915 | -0.077921 | -0.24871 | 122.3177 | 122.2964 | 122.3052 | 56.0955 | -122.4257 | 122.1456 | 122.3327 | 122.1619 | 57.6511 | -122.6216
1053.375 | 122.6212 | -57.4448 | 64.856 | 1.4211e-13 | -0.01085 | -0.012009 | 0.015729 | -0.037865 | 0.029953 | -0.0084697 | -0.01494 | 0.010021 | 0.03535 | -0.0022349 | 0.03777 | -57.4303 | -1.5507 | -57.5162 | 64.8409 | 64.8059 | 64.8193 | -57.5011 | -57.4709 | 0.06904 | -57.5833 | 64.655 | 64.8467 | 64.6714 | -57.6833 | -0.056324 | -0.015063 | 0.014513 | -0.071428 | -0.015104 | -0.050079 | -0.036652 | -0.23849 | -0.20093 | -0.026155 | -0.1385 | 0.099988 | -0.009239 | -0.1846 | 122.2857 | 122.2506 | 122.2641 | 55.894 | -122.357 | 122.0998 | 122.2915 | 122.1161 | 57.5138 | -122.5392
1055.0938 | 122.4976 | -57.4036 | 65.0391 | 1.4211e-13 | -0.01085 | -0.011795 | 0.015729 | -0.038293 | 0.029953 | 0.0067908 | -0.014513 | 0.010448 | 0.035136 | -0.0020213 | 0.037556 | -57.3066 | -1.6011 | -57.3788 | 64.9645 | 64.9387 | 64.9567 | -57.3729 | -57.3427 | 0.06904 | -57.4551 | 64.7924 | 64.9795 | 64.7996 | -57.555 | 0.030687 | -0.074551 | 0.096931 | 0.024721 | -0.005966 | -0.1004 | -0.082399 | -0.15148 | -0.24668 | 0.060849 | -0.051494 | 0.099985 | -0.059564 | -0.23951 | 122.3681 | 122.3422 | 122.3602 | 55.8025 | -122.4119 | 122.1959 | 122.3831 | 122.2031 | 57.4726 | -122.5941
1056.8906 | 122.4976 | -57.106 | 65.2679 | 1.4211e-13 | -0.011064 | -0.012009 | 0.015729 | -0.037865 | 0.030167 | -0.00083919 | -0.014513 | 0.010448 | 0.035136 | -0.0015939 | 0.03777 | -57.1143 | -1.6332 | -57.2049 | 65.1568 | 65.131 | 65.1444 | -57.1851 | -57.1596 | 0.073618 | -57.2628 | 64.9755 | 65.1672 | 64.9827 | -57.3765 | -0.079123 | -0.11114 | -0.008323 | -0.09885 | -0.019727 | -0.13696 | -0.12356 | -0.27045 | -0.29242 | -0.053548 | -0.15673 | 0.11372 | -0.10072 | -0.28525 | 122.2628 | 122.237 | 122.2504 | 55.4729 | -122.4531 | 122.0815 | 122.2732 | 122.0887 | 57.1796 | -122.6444
1058.625 | 122.4884 | -57.0831 | 65.3229 | 1.4211e-13 | -0.01085 | -0.012009 | 0.015943 | -0.038293 | 0.029526 | 0.0067908 | -0.01494 | 0.010021 | 0.035136 | -0.0020213 | 0.03777 | -57.0365 | -1.6789 | -57.127 | 65.2301 | 65.1951 | 65.2176 | -57.1119 | -57.0863 | 0.073618 | -57.1987 | 65.0625 | 65.2405 | 65.0926 | -57.2941 | -0.028748 | -0.092819 | 0.046622 | -0.043907 | -0.015159 | -0.12779 | -0.10523 | -0.21092 | -0.26036 | -0.003177 | -0.11552 | 0.095401 | -0.082398 | -0.23029 | 122.3132 | 122.2782 | 122.3008 | 55.4042 | -122.4348 | 122.1456 | 122.3236 | 122.1757 | 57.1567 | -122.6169
1060.4062 | 122.612 | -56.9183 | 65.387 | 1.4211e-13 | -0.01085 | -0.011795 | 0.015516 | -0.038079 | 0.030167 | -0.0084697 | -0.014513 | 0.010448 | 0.034923 | -0.0020213 | 0.03777 | -56.8946 | -1.711 | -56.9714 | 65.3857 | 65.3508 | 65.3642 | -56.9562 | -56.9352 | 0.087354 | -57.043 | 65.1999 | 65.3962 | 65.2712 | -57.1429 | -0.03786 | -0.001241 | 0.023757 | -0.053041 | -0.015181 | -0.036193 | -0.022804 | -0.22462 | -0.1871 | -0.016874 | -0.12464 | 0.099976 | 0.009187 | -0.11581 | 122.3041 | 122.2691 | 122.2825 | 55.2073 | -122.3432 | 122.1182 | 122.3145 | 122.1895 | 57.0057 | -122.5299
1062.125 | 122.493 | -56.8497 | 65.5518 | 1.4211e-13 | -0.010423 | -0.011795 | 0.015943 | -0.038079 | 0.029953 | 0.0067908 | -0.014726 | 0.010234 | 0.035136 | -0.0018077 | 0.037983 | -56.8076 | -1.7522 | -56.8981 | 65.459 | 65.4332 | 65.4466 | -56.8829 | -56.862 | 0.082776 | -56.9697 | 65.2777 | 65.4786 | 65.2757 | -57.0743 | -0.033262 | -0.092781 | 0.042081 | -0.048453 | -0.015191 | -0.11857 | -0.10518 | -0.2246 | -0.27406 | -0.01228 | -0.12004 | 0.10455 | -0.073193 | -0.27603 | 122.3086 | 122.2829 | 122.2962 | 55.0975 | -122.4347 | 122.1274 | 122.3282 | 122.1254 | 56.9324 | -122.626
1063.9219 | 122.6074 | -56.781 | 65.5655 | 1.4211e-13 | -0.010423 | -0.012009 | 0.015943 | -0.038079 | 0.02974 | 0.0067908 | -0.014726 | 0.010021 | 0.034923 | -0.0022349 | 0.037556 | -56.7572 | -1.7842 | -56.8432 | 65.5093 | 65.4881 | 65.5015 | -56.828 | -56.807 | 0.078197 | -56.9056 | 65.3372 | 65.5381 | 65.3353 | -57.0102 | -0.046979 | -0.056152 | 0.023779 | -0.062178 | -0.015199 | -0.077353 | -0.063974 | -0.22916 | -0.22827 | -0.026 | -0.12461 | 0.10455 | -0.027404 | -0.23024 | 122.2903 | 122.2691 | 122.2825 | 54.9968 | -122.3935 | 122.1182 | 122.3191 | 122.1163 | 56.8592 | -122.5757
1065.7188 | 122.5708 | -56.7169 | 65.6021 | 1.4211e-13 | -0.01085 | -0.012009 | 0.015516 | -0.038506 | 0.029953 | -0.0084697 | -0.014726 | 0.010021 | 0.035136 | -0.0022349 | 0.03777 | -56.6748 | -1.8392 | -56.7562 | 65.5963 | 65.5751 | 65.5885 | -56.7318 | -56.7154 | 0.082776 | -56.8278 | 65.4242 | 65.6159 | 65.4451 | -56.9277 | -0.014908 | -0.005784 | 0.042103 | -0.039278 | -0.02437 | -0.026975 | -0.013602 | -0.21083 | -0.1779 | 0.001488 | -0.11086 | 0.099971 | 0.013811 | -0.15697 | 122.3132 | 122.2921 | 122.3054 | 54.8777 | -122.3339 | 122.1411 | 122.3328 | 122.1621 | 56.7997 | -122.5299
1067.5 | 122.5342 | -56.575 | 65.8081 | 1.4211e-13 | -0.010637 | -0.011795 | 0.015516 | -0.038293 | 0.029526 | -0.0084697 | -0.014513 | 0.010234 | 0.034923 | -0.0018077 | 0.037342 | -56.4917 | -1.8941 | -56.5822 | 65.7795 | 65.7583 | 65.7533 | -56.567 | -56.546 | 0.078197 | -56.6538 | 65.5936 | 65.7945 | 65.6329 | -56.7583 | 0.008026 | -0.028641 | 0.083332 | -0.00721 | -0.015236 | -0.049811 | -0.054765 | -0.18332 | -0.21449 | 0.028993 | -0.078772 | 0.10455 | -0.013616 | -0.17524 | 122.3545 | 122.3333 | 122.3284 | 54.6809 | -122.3751 | 122.1686 | 122.3695 | 122.2079 | 56.6532 | -122.5664
1069.2031 | 122.5891 | -56.5613 | 65.7852 | 1.4211e-13 | -0.01085 | -0.011795 | 0.015516 | -0.038079 | 0.030167 | -0.0084697 | -0.014513 | 0.010021 | 0.034923 | -0.0022349 | 0.03777 | -56.4825 | -1.9308 | -56.5685 | 65.7932 | 65.7675 | 65.7808 | -56.5578 | -56.5277 | 0.078197 | -56.6446 | 65.6074 | 65.8082 | 65.6054 | -56.7354 | 0.003451 | 0.007982 | 0.078756 | -0.007208 | -0.010659 | -0.017765 | -0.004405 | -0.17416 | -0.17786 | 0.033575 | -0.083347 | 0.090809 | 0.023008 | -0.17983 | 122.3545 | 122.3287 | 122.3421 | 54.6305 | -122.343 | 122.1686 | 122.3695 | 122.1667 | 56.6395 | -122.5207
1070.9844 | 122.6166 | -56.337 | 65.9546 | 1.4211e-13 | -0.01085 | -0.011795 | 0.015516 | -0.038293 | 0.02974 | 0.014421 | -0.014726 | 0.010448 | 0.034709 | -0.0020213 | 0.037342 | -56.336 | -1.9857 | -56.4174 | 65.9534 | 65.9231 | 65.9365 | -56.3976 | -56.372 | 0.082776 | -56.4844 | 65.7676 | 65.9639 | 65.7977 | -56.5798 | -0.060591 | -0.001147 | 0.00096 | -0.080429 | -0.019838 | -0.031454 | -0.018106 | -0.24278 | -0.18699 | -0.035053 | -0.1474 | 0.095384 | 0.009307 | -0.1569 | 122.2904 | 122.2601 | 122.2735 | 54.3513 | -122.3522 | 122.1046 | 122.3009 | 122.1347 | 56.4198 | -122.5343
1072.7812 | 122.4884 | -56.2729 | 66.1011 | 1.4211e-13 | -0.010637 | -0.011795 | 0.015729 | -0.038293 | 0.029953 | -0.0161 | -0.014726 | 0.010021 | 0.034923 | -0.0020213 | 0.037129 | -56.217 | -2.0361 | -56.2984 | 66.0542 | 66.033 | 66.0464 | -56.2831 | -56.2576 | 0.082776 | -56.3791 | 65.8866 | 66.0875 | 65.8984 | -56.4744 | -0.010205 | -0.046907 | 0.055911 | -0.025481 | -0.015276 | -0.068044 | -0.054703 | -0.20155 | -0.21443 | 0.015328 | -0.10617 | 0.095382 | -0.013555 | -0.20265 | 122.3271 | 122.3059 | 122.3193 | 54.2368 | -122.3842 | 122.1595 | 122.3604 | 122.1713 | 56.3557 | -122.5755
1074.5469 | 122.493 | -56.131 | 66.2521 | 1.4211e-13 | -0.01085 | -0.011795 | 0.015516 | -0.038293 | 0.029953 | -0.0084697 | -0.014726 | 0.010448 | 0.034709 | -0.0018077 | 0.037556 | -56.0979 | -2.1414 | -56.1839 | 66.1686 | 66.1521 | 66.1608 | -56.164 | -56.1385 | 0.078197 | -56.26 | 65.9919 | 66.1974 | 66.0129 | -56.3508 | -0.03306 | -0.083509 | 0.033042 | -0.052931 | -0.019871 | -0.10005 | -0.0913 | -0.21983 | -0.26019 | -0.007533 | -0.12903 | 0.0908 | -0.05473 | -0.23925 | 122.2996 | 122.2831 | 122.2918 | 53.9896 | -122.4162 | 122.1229 | 122.3284 | 122.1439 | 56.2092 | -122.603
1076.3281 | 122.5937 | -56.0028 | 66.3025 | 1.4211e-13 | -0.011064 | -0.011795 | 0.015729 | -0.038293 | 0.029953 | -0.00083919 | -0.014726 | 0.010234 | 0.034709 | -0.0018077 | 0.037556 | -55.9697 | -2.1734 | -56.0466 | 66.306 | 66.2849 | 66.2936 | -56.0404 | -56.0149 | 0.078197 | -56.1272 | 66.1247 | 66.3165 | 66.164 | -56.2272 | -0.037602 | 0.003488 | 0.033064 | -0.043755 | -0.006153 | -0.017619 | -0.008875 | -0.22438 | -0.17777 | -0.012081 | -0.12442 | 0.099955 | 0.01396 | -0.13851 | 122.3088 | 122.2877 | 122.2964 | 53.8294 | -122.3429 | 122.1275 | 122.3193 | 122.1668 | 56.081 | -122.5297
1078.1406 | 122.5662 | -55.9479 | 66.3712 | 1.4211e-13 | -0.011278 | -0.012222 | 0.015516 | -0.038506 | 0.02974 | -0.00083919 | -0.014513 | 0.010448 | 0.034923 | -0.0018077 | 0.037556 | -55.8965 | -2.2787 | -55.987 | 66.3747 | 66.3536 | 66.3623 | -55.9809 | -55.9508 | 0.082776 | -56.0586 | 66.1934 | 66.3851 | 66.2739 | -56.1631 | -0.033008 | 0.003499 | 0.051386 | -0.03917 | -0.006162 | -0.0176 | -0.008861 | -0.21521 | -0.17776 | -0.002911 | -0.11068 | 0.10453 | 0.013974 | -0.09729 | 122.3225 | 122.3014 | 122.3102 | 53.6691 | -122.352 | 122.1413 | 122.333 | 122.2217 | 56.0307 | -122.5342
1079.8594 | 122.5021 | -55.6732 | 66.7053 | 1.4211e-13 | -0.01085 | -0.012009 | 0.015516 | -0.038079 | 0.030167 | 0.0067908 | -0.014726 | 0.010448 | 0.034923 | -0.0018077 | 0.037556 | -55.6447 | -2.3199 | -55.7352 | 66.631 | 66.5962 | 66.6004 | -55.7153 | -55.6944 | 0.078197 | -55.8067 | 66.4452 | 66.6415 | 66.4524 | -55.9021 | -0.042088 | -0.074278 | 0.028539 | -0.062022 | -0.019934 | -0.10908 | -0.10494 | -0.22887 | -0.2601 | -0.021161 | -0.1335 | 0.095368 | -0.063792 | -0.25289 | 122.3043 | 122.2695 | 122.2736 | 53.3533 | -122.4206 | 122.1184 | 122.3147 | 122.1256 | 55.7514 | -122.6074
1081.6406 | 122.612 | -55.5588 | 66.7419 | 1.4211e-13 | -0.011064 | -0.011795 | 0.015729 | -0.038506 | 0.030167 | -0.0161 | -0.014513 | 0.010448 | 0.035136 | -0.0018077 | 0.037556 | -55.4936 | -2.4024 | -55.5796 | 66.7821 | 66.7519 | 66.7652 | -55.5688 | -55.5479 | 0.073618 | -55.6465 | 66.6009 | 66.7972 | 66.6402 | -55.751 | -0.010004 | 0.040188 | 0.065185 | -0.020802 | -0.010798 | 0.009978 | 0.023268 | -0.19221 | -0.14106 | 0.010917 | -0.08769 | 0.10452 | 0.05526 | -0.10179 | 122.3409 | 122.3107 | 122.324 | 53.1564 | -122.3107 | 122.1597 | 122.356 | 122.1989 | 55.6324 | -122.4929
1083.4375 | 122.5159 | -55.3757 | 67.0074 | 1.4211e-13 | -0.011064 | -0.012009 | 0.015516 | -0.038293 | 0.029953 | -0.0084697 | -0.014513 | 0.010234 | 0.034709 | -0.0020213 | 0.03777 | -55.3242 | -2.4344 | -55.4193 | 66.9424 | 66.9168 | 66.9255 | -55.3948 | -55.383 | 0.082776 | -55.4954 | 66.7611 | 66.9575 | 66.8279 | -55.5907 | -0.01911 | -0.065072 | 0.05148 | -0.043668 | -0.024558 | -0.090684 | -0.081984 | -0.21506 | -0.24631 | -0.007356 | -0.1197 | 0.095361 | -0.049992 | -0.17957 | 122.318 | 122.2924 | 122.3011 | 52.9413 | -122.4022 | 122.1368 | 122.3331 | 122.2035 | 55.4584 | -122.5982
1085.1562 | 122.58 | -55.3207 | 66.9983 | 1.4211e-13 | -0.010637 | -0.011795 | 0.015088 | -0.038079 | 0.029953 | -0.0084697 | -0.01494 | 0.010234 | 0.034496 | -0.0018077 | 0.037556 | -55.2601 | -2.5351 | -55.3507 | 67.0202 | 66.99 | 66.9987 | -55.3398 | -55.3143 | 0.078197 | -55.4221 | 66.8252 | 67.0216 | 66.9011 | -55.5129 | -0.019094 | 0.021916 | 0.060646 | -0.029925 | -0.010831 | -0.008266 | 0.000429 | -0.19215 | -0.17306 | 0.006394 | -0.10137 | 0.09078 | 0.023263 | -0.097158 | 122.3409 | 122.3108 | 122.3195 | 52.7856 | -122.3381 | 122.146 | 122.3423 | 122.2219 | 55.3989 | -122.5112
1086.9375 | 122.4701 | -55.1605 | 67.2318 | 1.4211e-13 | -0.01085 | -0.011795 | 0.015302 | -0.038293 | 0.030167 | -0.0084697 | -0.014513 | 0.010021 | 0.034923 | -0.0018077 | 0.037342 | -55.1182 | -2.5947 | -55.2042 | 67.153 | 67.1274 | 67.1452 | -55.1842 | -55.1816 | 0.073618 | -55.2847 | 66.9763 | 67.1726 | 67.0385 | -55.3801 | -0.023629 | -0.07877 | 0.042358 | -0.043638 | -0.020009 | -0.10436 | -0.086515 | -0.21958 | -0.25543 | -0.021042 | -0.12423 | 0.095356 | -0.059102 | -0.19326 | 122.3135 | 122.2879 | 122.3058 | 52.5659 | -122.4159 | 122.1368 | 122.3332 | 122.199 | 55.2341 | -122.6119
1088.7344 | 122.58 | -55.1239 | 67.1997 | 1.4211e-13 | -0.011491 | -0.012009 | 0.015729 | -0.038293 | 0.02974 | 0.0067908 | -0.01494 | 0.010448 | 0.03535 | -0.0020213 | 0.03777 | -55.0815 | -2.6817 | -55.1721 | 67.1896 | 67.164 | 67.1819 | -55.1567 | -55.1404 | 0.078197 | -55.2481 | 66.9992 | 67.2001 | 67.0568 | -55.3435 | -0.032776 | -0.0101 | 0.042364 | -0.048211 | -0.015435 | -0.035683 | -0.017843 | -0.21957 | -0.20049 | -0.016454 | -0.12422 | 0.095355 | 0.000413 | -0.1429 | 122.3135 | 122.2879 | 122.3058 | 52.4422 | -122.3564 | 122.1231 | 122.324 | 122.1807 | 55.2021 | -122.5432
1090.5312 | 122.4884 | -55.1697 | 67.2409 | 1.4211e-13 | -0.011278 | -0.011581 | 0.015729 | -0.038293 | 0.02974 | -0.00083919 | -0.014513 | 0.010448 | 0.034709 | -0.0015939 | 0.03777 | -55.0953 | -2.8099 | -55.1904 | 67.1713 | 67.1411 | 67.1544 | -55.1704 | -55.1587 | 0.087354 | -55.2619 | 66.9855 | 67.191 | 67.0385 | -55.3572 | -0.000736 | -0.069612 | 0.074406 | -0.020747 | -0.020011 | -0.099776 | -0.086514 | -0.18753 | -0.25543 | 0.011008 | -0.092178 | 0.095355 | -0.049943 | -0.20241 | 122.341 | 122.3108 | 122.3241 | 52.3598 | -122.4113 | 122.1552 | 122.3606 | 122.2082 | 55.257 | -122.5981
1092.2344 | 122.5342 | -55.014 | 67.3874 | 1.4211e-13 | -0.010637 | -0.012009 | 0.015516 | -0.038293 | 0.030167 | -0.00083919 | -0.014513 | 0.010234 | 0.034923 | -0.0018077 | 0.037556 | -54.9625 | -2.874 | -55.0531 | 67.3041 | 67.2739 | 67.2918 | -55.0376 | -55.0259 | 0.082776 | -55.1337 | 67.1228 | 67.3237 | 67.153 | -55.2198 | -0.023587 | -0.083323 | 0.051539 | -0.039038 | -0.015451 | -0.11347 | -0.095639 | -0.20581 | -0.26456 | -0.011849 | -0.11961 | 0.086195 | -0.063648 | -0.23443 | 122.3181 | 122.288 | 122.3058 | 52.1401 | -122.425 | 122.1369 | 122.3378 | 122.167 | 55.0968 | -122.6072
1094.0156 | 122.6028 | -54.9637 | 67.3279 | 1.4211e-13 | -0.011064 | -0.012009 | 0.015302 | -0.038506 | 0.029953 | -0.00083919 | -0.014726 | 0.010234 | 0.034923 | -0.0018077 | 0.037983 | -54.9076 | -2.9243 | -55.0027 | 67.359 | 67.3334 | 67.3513 | -54.9918 | -54.9664 | 0.082776 | -55.0879 | 67.1686 | 67.3741 | 67.2125 | -55.1649 | -0.028152 | 0.031127 | 0.056126 | -0.039031 | -0.010879 | 0.005563 | 0.023391 | -0.20122 | -0.15926 | -0.00268 | -0.12418 | 0.077036 | 0.046226 | -0.1154 | 122.3227 | 122.2971 | 122.315 | 52.0394 | -122.3197 | 122.1323 | 122.3378 | 122.1762 | 55.0465 | -122.4928
1095.8125 | 122.5159 | -54.7485 | 67.6117 | 1.4211e-13 | -0.011278 | -0.011795 | 0.015302 | -0.038079 | 0.029953 | -0.00083919 | -0.014726 | 0.010234 | 0.034923 | -0.0020213 | 0.037556 | -54.7015 | -3.0434 | -54.8013 | 67.5696 | 67.5395 | 67.5436 | -54.7812 | -54.7695 | 0.078197 | -54.8864 | 67.3884 | 67.5756 | 67.4551 | -54.9589 | -0.032671 | -0.042081 | 0.047004 | -0.052736 | -0.020065 | -0.072198 | -0.06812 | -0.21032 | -0.22331 | -0.020945 | -0.13787 | 0.072452 | -0.036129 | -0.15655 | 122.3181 | 122.288 | 122.2921 | 51.7052 | -122.3929 | 122.1369 | 122.3241 | 122.2037 | 54.8267 | -122.5705
1097.6094 | 122.612 | -54.4739 | 67.8497 | 1.4211e-13 | -0.01085 | -0.011795 | 0.015516 | -0.038079 | 0.030167 | -0.0084697 | -0.014726 | 0.010234 | 0.034709 | -0.0018077 | 0.037342 | -54.4268 | -3.0892 | -54.5174 | 67.8489 | 67.8234 | 67.8229 | -54.4973 | -54.4948 | 0.082776 | -54.6025 | 67.6677 | 67.8594 | 67.7253 | -54.6933 | -0.023435 | -0.000836 | 0.04705 | -0.04354 | -0.020105 | -0.026342 | -0.026863 | -0.21941 | -0.18206 | -0.02088 | -0.12864 | 0.090761 | 0.009708 | -0.12445 | 122.3228 | 122.2973 | 122.2967 | 51.3847 | -122.347 | 122.1416 | 122.3333 | 122.1992 | 54.5567 | -122.543
1099.3281 | 122.4564 | -54.4281 | 67.9413 | 1.4211e-13 | -0.011064 | -0.011795 | 0.015302 | -0.038079 | 0.030167 | -0.00083919 | -0.014513 | 0.010234 | 0.034709 | -0.0015939 | 0.037556 | -54.3536 | -3.1807 | -54.4487 | 67.9084 | 67.8783 | 67.887 | -54.4378 | -54.4307 | 0.087354 | -54.5384 | 67.7226 | 67.9281 | 67.7756 | -54.6292 | -0.009685 | -0.03287 | 0.074528 | -0.020642 | -0.010957 | -0.062948 | -0.054315 | -0.20108 | -0.21867 | -0.002554 | -0.11032 | 0.090759 | -0.013166 | -0.16564 | 122.3365 | 122.3064 | 122.3151 | 51.2474 | -122.3791 | 122.1507 | 122.3562 | 122.2037 | 54.5155 | -122.5705
1101.125 | 122.4701 | -54.6433 | 67.7628 | 1.4211e-13 | -0.01085 | -0.012009 | 0.015302 | -0.038293 | 0.02974 | -0.0084697 | -0.014299 | 0.010021 | 0.034923 | -0.0015939 | 0.037342 | -54.5504 | -3.3227 | -54.6456 | 67.7115 | 67.686 | 67.6992 | -54.6301 | -54.6138 | 0.082776 | -54.7261 | 67.5349 | 67.7358 | 67.6108 | -54.8169 | 0.013149 | -0.051213 | 0.092806 | -0.002359 | -0.015508 | -0.076734 | -0.06351 | -0.17366 | -0.22786 | 0.029446 | -0.082897 | 0.090764 | -0.02694 | -0.15194 | 122.3548 | 122.3293 | 122.3425 | 51.3206 | -122.3929 | 122.1781 | 122.3791 | 122.2541 | 54.726 | -122.5797
1102.9219 | 122.4655 | -54.3961 | 68.0099 | 1.4211e-13 | -0.011064 | -0.012009 | 0.015516 | -0.038293 | 0.02974 | 0.0067908 | -0.014726 | 0.010021 | 0.035136 | -0.0015939 | 0.037556 | -54.3582 | -3.4509 | -54.4671 | 67.9038 | 67.8738 | 67.8824 | -54.4378 | -54.4307 | 0.082776 | -54.5476 | 67.7272 | 67.9144 | 67.739 | -54.6338 | -0.041729 | -0.10611 | 0.037905 | -0.070999 | -0.02927 | -0.13619 | -0.12756 | -0.2377 | -0.28275 | -0.034598 | -0.15152 | 0.086181 | -0.095567 | -0.27093 | 122.2999 | 122.2698 | 122.2784 | 50.9452 | -122.4477 | 122.1233 | 122.3104 | 122.1351 | 54.4788 | -122.6437
1104.7188 | 122.5937 | -54.2679 | 68.042 | 1.4211e-13 | -0.011064 | -0.012009 | 0.015302 | -0.038293 | 0.02974 | -0.00083919 | -0.01494 | 0.010234 | 0.03535 | -0.0018077 | 0.037342 | -54.23 | -3.5104 | -54.3297 | 68.032 | 68.0065 | 68.0106 | -54.305 | -54.307 | 0.087354 | -54.4148 | 67.8462 | 68.0426 | 67.9084 | -54.501 | -0.037114 | -0.009961 | 0.037926 | -0.061825 | -0.024711 | -0.035446 | -0.031401 | -0.23309 | -0.19575 | -0.039147 | -0.14691 | 0.086178 | 0.000591 | -0.13357 | 122.2999 | 122.2744 | 122.2785 | 50.7575 | -122.347 | 122.1141 | 122.3105 | 122.1763 | 54.3552 | -122.543
1106.5 | 122.5754 | -53.6682 | 68.6691 | 1.4211e-13 | -0.011278 | -0.012222 | 0.015088 | -0.038079 | 0.02974 | -0.0084697 | -0.014726 | 0.010021 | 0.034923 | -0.0015939 | 0.037556 | -53.6256 | -3.5379 | -53.7254 | 68.641 | 68.6018 | 68.6195 | -53.7097 | -53.7072 | 0.087354 | -53.815 | 68.4506 | 68.647 | 68.4899 | -53.8874 | -0.041524 | -0.028172 | 0.042604 | -0.057162 | -0.015638 | -0.067322 | -0.049583 | -0.2192 | -0.21853 | -0.039006 | -0.14677 | 0.072428 | -0.02217 | -0.17922 | 122.3092 | 122.27 | 122.2878 | 50.1304 | -122.3789 | 122.1188 | 122.3152 | 122.1581 | 53.7556 | -122.5565
1108.2188 | 122.5296 | -53.4531 | 68.9438 | 1.4211e-13 | -0.011064 | -0.012222 | 0.015302 | -0.038506 | 0.030167 | -0.00083919 | -0.01494 | 0.010234 | 0.034496 | -0.0015939 | 0.037129 | -53.383 | -3.634 | -53.4919 | 68.8882 | 68.8582 | 68.8714 | -53.4533 | -53.4508 | 0.082776 | -53.5769 | 68.6933 | 68.8942 | 68.7463 | -53.6493 | -0.000253 | -0.055598 | 0.070109 | -0.038819 | -0.038566 | -0.085561 | -0.072419 | -0.19625 | -0.25053 | 0.002253 | -0.12383 | 0.072421 | -0.049584 | -0.19748 | 122.3413 | 122.3113 | 122.3244 | 49.8191 | -122.3971 | 122.1463 | 122.3473 | 122.1994 | 53.5358 | -122.5931
1110 | 122.4792 | -53.7735 | 68.6325 | 1.4211e-13 | -0.011278 | -0.012009 | 0.015516 | -0.038293 | 0.030167 | -0.00083919 | -0.01494 | 0.010234 | 0.035136 | -0.0013803 | 0.037342 | -53.7034 | -3.6889 | -53.8215 | 68.5494 | 68.524 | 68.5326 | -53.7876 | -53.7896 | 0.078197 | -53.8974 | 68.3728 | 68.5691 | 68.3525 | -53.979 | -0.01408 | -0.083119 | 0.070057 | -0.04802 | -0.03394 | -0.10854 | -0.099955 | -0.20549 | -0.25974 | -0.016137 | -0.1239 | 0.081587 | -0.063385 | -0.27996 | 122.3229 | 122.2975 | 122.3061 | 50.0846 | -122.4201 | 122.1463 | 122.3426 | 122.126 | 53.8517 | -122.6115
1111.7656 | 122.4792 | -53.5675 | 68.8339 | 1.4211e-13 | -0.011278 | -0.012009 | 0.015516 | -0.038506 | 0.029953 | -0.0084697 | -0.014726 | 0.010448 | 0.035136 | -0.0013803 | 0.037129 | -53.5203 | -3.7118 | -53.6338 | 68.7371 | 68.7117 | 68.7249 | -53.6044 | -53.5973 | 0.078197 | -53.7143 | 68.5513 | 68.7568 | 68.5906 | -53.7867 | -0.036917 | -0.096821 | 0.047198 | -0.066304 | -0.029387 | -0.12222 | -0.10907 | -0.21917 | -0.2826 | -0.029825 | -0.14675 | 0.072425 | -0.077078 | -0.24329 | 122.3046 | 122.2792 | 122.2924 | 49.8557 | -122.4383 | 122.1188 | 122.3243 | 122.1581 | 53.6457 | -122.6206
1113.5625 | 122.6028 | -53.1967 | 69.104 | 1.4211e-13 | -0.011278 | -0.012009 | 0.015302 | -0.038506 | 0.029953 | -0.0084697 | -0.01494 | 0.010448 | 0.035136 | -0.0018077 | 0.037556 | -53.1632 | -3.8034 | -53.2721 | 69.1034 | 69.0643 | 69.082 | -53.2518 | -53.2402 | 0.087354 | -53.3617 | 68.9084 | 69.114 | 68.9981 | -53.4295 | -0.055129 | -0.000631 | 0.033524 | -0.075409 | -0.02028 | -0.039726 | -0.02202 | -0.23281 | -0.19556 | -0.043475 | -0.16497 | 0.067838 | 0.009972 | -0.10587 | 122.3001 | 122.261 | 122.2787 | 49.3933 | -122.3558 | 122.1052 | 122.3107 | 122.1948 | 53.2841 | -122.5335
1115.3438 | 122.6303 | -53.0182 | 69.2825 | 1.4211e-13 | -0.011278 | -0.012009 | 0.015516 | -0.038079 | 0.029953 | 0.0067908 | -0.014513 | 0.010021 | 0.03535 | -0.0013803 | 0.03777 | -53.0075 | -3.8171 | -53.1073 | 69.259 | 69.2245 | 69.2377 | -53.0916 | -53.0845 | 0.082776 | -53.1969 | 69.0824 | 69.2788 | 69.1263 | -53.2693 | -0.073394 | -0.023493 | 0.010661 | -0.089119 | -0.015725 | -0.057992 | -0.044875 | -0.25108 | -0.2001 | -0.066326 | -0.17867 | 0.072413 | -0.003727 | -0.1562 | 122.2772 | 122.2427 | 122.2558 | 49.201 | -122.3741 | 122.1006 | 122.297 | 122.1445 | 53.101 | -122.5518
1117.0469 | 122.5296 | -52.7115 | 69.6762 | 1.4211e-13 | -0.011705 | -0.011795 | 0.015729 | -0.038293 | 0.030167 | 0.0067908 | -0.014726 | 0.010234 | 0.034709 | -0.0015939 | 0.037342 | -52.6779 | -3.8996 | -52.7868 | 69.5841 | 69.5405 | 69.5582 | -52.7756 | -52.764 | 0.087354 | -52.8809 | 69.3892 | 69.5947 | 69.4285 | -52.9488 | -0.06415 | -0.092104 | 0.033604 | -0.07534 | -0.01119 | -0.13572 | -0.11805 | -0.23727 | -0.28702 | -0.052518 | -0.16944 | 0.067826 | -0.081479 | -0.24769 | 122.2956 | 122.252 | 122.2696 | 48.8119 | -122.4518 | 122.1007 | 122.3062 | 122.14 | 52.7988 | -122.625
1118.8281 | 122.5021 | -52.4414 | 69.9738 | 1.4211e-13 | -0.011491 | -0.011581 | 0.015302 | -0.038079 | 0.029953 | -0.0161 | -0.01494 | 0.010234 | 0.03535 | -0.0013803 | 0.037556 | -52.3574 | -3.9362 | -52.4618 | 69.9092 | 69.8747 | 69.8878 | -52.4322 | -52.4435 | 0.073618 | -52.5513 | 69.7188 | 69.9244 | 69.804 | -52.6237 | 0.009189 | -0.064585 | 0.08401 | -0.020364 | -0.029553 | -0.099008 | -0.085937 | -0.18225 | -0.25491 | -0.002089 | -0.10985 | 0.072397 | -0.049367 | -0.16979 | 122.3506 | 122.3162 | 122.3292 | 48.5052 | -122.406 | 122.1602 | 122.3658 | 122.2454 | 52.515 | -122.5974
1120.625 | 122.4701 | -52.6245 | 69.7906 | 1.4211e-13 | -0.011491 | -0.011795 | 0.015302 | -0.038293 | 0.029953 | -0.00083919 | -0.01494 | 0.010234 | 0.034923 | -0.0013803 | 0.037342 | -52.6046 | -4.1239 | -52.709 | 69.6528 | 69.6275 | 69.636 | -52.6932 | -52.6953 | 0.087354 | -52.7939 | 69.4624 | 69.6771 | 69.5018 | -52.8755 | -0.068704 | -0.13787 | 0.019883 | -0.084485 | -0.015781 | -0.16316 | -0.15465 | -0.25098 | -0.3282 | -0.070812 | -0.16942 | 0.081561 | -0.11351 | -0.28887 | 122.2773 | 122.252 | 122.2605 | 48.5006 | -122.4839 | 122.087 | 122.3017 | 122.1263 | 52.7119 | -122.6661
1122.4062 | 122.6212 | -52.2858 | 70.0607 | 1.4211e-13 | -0.011491 | -0.012009 | 0.015516 | -0.038079 | 0.030381 | -0.0161 | -0.01494 | 0.010234 | 0.034923 | -0.0015939 | 0.037556 | -52.2246 | -4.2292 | -52.3473 | 70.0236 | 70.003 | 70.0069 | -52.3177 | -52.3153 | 0.091933 | -52.4322 | 69.847 | 70.0389 | 69.9139 | -52.5092 | -0.031977 | -0.037101 | 0.061144 | -0.061546 | -0.029569 | -0.057773 | -0.053868 | -0.22342 | -0.21369 | -0.029524 | -0.14645 | 0.076974 | -0.021877 | -0.14688 | 122.3094 | 122.2887 | 122.2926 | 48.0565 | -122.3785 | 122.1328 | 122.3246 | 122.1996 | 52.3777 | -122.5699
1124.1406 | 122.493 | -51.9836 | 70.4178 | 1.4211e-13 | -0.011278 | -0.012009 | 0.015302 | -0.038293 | 0.02974 | -0.00083919 | -0.014726 | 0.010234 | 0.034923 | -0.0013803 | 0.037342 | -51.9179 | -4.2933 | -52.036 | 70.335 | 70.3097 | 70.3182 | -52.011 | -52.0085 | 0.096512 | -52.1346 | 70.1538 | 70.3502 | 70.2389 | -52.1932 | -0.027313 | -0.082826 | 0.065772 | -0.052346 | -0.025033 | -0.10804 | -0.099579 | -0.20961 | -0.26399 | -0.024875 | -0.15095 | 0.058652 | -0.067588 | -0.17885 | 122.3186 | 122.2934 | 122.3019 | 47.6903 | -122.4287 | 122.1374 | 122.3338 | 122.2226 | 52.0802 | -122.611
1125.9375 | 122.5525 | -51.6861 | 70.7062 | 1.4211e-13 | -0.011491 | -0.011795 | 0.014875 | -0.038293 | 0.02974 | -0.0084697 | -0.014726 | 0.010234 | 0.034923 | -0.0013803 | 0.037342 | -51.6432 | -4.3345 | -51.7476 | 70.6188 | 70.5891 | 70.5929 | -51.7225 | -51.7246 | 0.091933 | -51.8461 | 70.4331 | 70.6295 | 70.4724 | -51.9094 | -0.036388 | -0.087357 | 0.042928 | -0.061462 | -0.025074 | -0.11712 | -0.11325 | -0.22327 | -0.27309 | -0.038542 | -0.16004 | 0.063224 | -0.076684 | -0.23373 | 122.3049 | 122.2752 | 122.279 | 47.3516 | -122.4287 | 122.1192 | 122.3156 | 122.1585 | 51.778 | -122.6155
1127.7344 | 122.5662 | -51.3702 | 71.0083 | 1.4211e-13 | -0.011705 | -0.011581 | 0.015088 | -0.038506 | 0.029953 | -0.00083919 | -0.014726 | 0.010448 | 0.034923 | -0.0015939 | 0.037342 | -51.2998 | -4.3528 | -51.4317 | 70.9622 | 70.9233 | 70.9317 | -51.3928 | -51.4041 | 0.096512 | -51.5165 | 70.7627 | 70.9683 | 70.825 | -51.5705 | -0.022562 | -0.046102 | 0.070451 | -0.061417 | -0.038855 | -0.08498 | -0.076561 | -0.20029 | -0.24556 | -0.033889 | -0.14623 | 0.054058 | -0.039991 | -0.18331 | 122.3324 | 122.2936 | 122.302 | 47.0174 | -122.4011 | 122.133 | 122.3385 | 122.1952 | 51.4668 | -122.5788
1129.5156 | 122.5983 | -50.9628 | 71.3425 | 1.4211e-13 | -0.011278 | -0.012009 | 0.015516 | -0.038079 | 0.029953 | 0.0067908 | -0.01494 | 0.010448 | 0.035136 | -0.0015939 | 0.037556 | -50.9198 | -4.4627 | -51.0242 | 71.3514 | 71.3171 | 71.3255 | -50.999 | -51.0104 | 0.096512 | -51.1319 | 71.1519 | 71.3621 | 71.2233 | -51.1905 | -0.036184 | 0.008894 | 0.043048 | -0.061359 | -0.025175 | -0.025359 | -0.016969 | -0.22766 | -0.19056 | -0.047529 | -0.16903 | 0.058628 | 0.019602 | -0.11913 | 122.3142 | 122.2799 | 122.2883 | 46.5001 | -122.3415 | 122.1147 | 122.3249 | 122.1862 | 51.0593 | -122.533
1131.2969 | 122.5204 | -50.4044 | 71.9513 | 1.4211e-13 | -0.011491 | -0.011581 | 0.015088 | -0.038293 | 0.029953 | 0.0067908 | -0.014513 | 0.010234 | 0.034923 | -0.0013803 | 0.037556 | -50.4024 | -4.5314 | -50.5114 | 71.8687 | 71.8299 | 71.8383 | -50.4816 | -50.4975 | 0.096512 | -50.6145 | 71.6647 | 71.8703 | 71.727 | -50.6731 | -0.077237 | -0.082574 | 0.001934 | -0.10706 | -0.029827 | -0.12135 | -0.11299 | -0.26872 | -0.28659 | -0.093185 | -0.21011 | 0.058616 | -0.081 | -0.22431 | 122.2731 | 122.2343 | 122.2427 | 45.8729 | -122.4329 | 122.0691 | 122.2747 | 122.1313 | 50.5009 | -122.6244
1133.0938 | 122.5571 | -49.9054 | 72.4319 | 1.4211e-13 | -0.011705 | -0.011795 | 0.015302 | -0.038506 | 0.029953 | -0.0084697 | -0.014726 | 0.010021 | 0.034923 | -0.0013803 | 0.037342 | -49.8484 | -4.5589 | -49.962 | 72.4227 | 72.384 | 72.3877 | -49.9367 | -49.9527 | 0.10567 | -50.065 | 72.2279 | 72.4197 | 72.2901 | -50.1145 | -0.031307 | -0.009241 | 0.056957 | -0.056632 | -0.025325 | -0.047948 | -0.044211 | -0.20907 | -0.20409 | -0.047281 | -0.15962 | 0.049446 | -0.012219 | -0.1418 | 122.3281 | 122.2894 | 122.2931 | 45.3465 | -122.3686 | 122.1333 | 122.3251 | 122.1955 | 50.0111 | -122.5464
1134.8125 | 122.5021 | -49.6811 | 72.6974 | 1.4211e-13 | -0.011491 | -0.011795 | 0.015516 | -0.038079 | 0.029953 | 0.0067908 | -0.014726 | 0.010448 | 0.034709 | -0.0011667 | 0.037342 | -49.6195 | -4.5497 | -49.7377 | 72.6425 | 72.6084 | 72.6212 | -49.7032 | -49.7237 | 0.10109 | -49.8452 | 72.4568 | 72.6578 | 72.4962 | -49.8855 | -0.022087 | -0.054982 | 0.061571 | -0.056602 | -0.034515 | -0.089084 | -0.076205 | -0.20443 | -0.24067 | -0.04265 | -0.16415 | 0.040283 | -0.039635 | -0.20126 | 122.3236 | 122.2895 | 122.3023 | 45.1314 | -122.4006 | 122.1379 | 122.3389 | 122.1773 | 49.7822 | -122.583
1136.5938 | 122.5571 | -49.2096 | 73.1461 | 1.4211e-13 | -0.011491 | -0.011795 | 0.015516 | -0.038934 | 0.029526 | -0.00083919 | -0.014513 | 0.010234 | 0.035136 | -0.0013803 | 0.037129 | -49.1571 | -4.5726 | -49.2799 | 73.1095 | 73.0846 | 73.0791 | -49.2453 | -49.2567 | 0.10567 | -49.3782 | 72.9146 | 73.1203 | 72.9632 | -49.4231 | -0.035691 | -0.036594 | 0.052492 | -0.07027 | -0.034579 | -0.061483 | -0.066953 | -0.21347 | -0.23143 | -0.047118 | -0.16862 | 0.04485 | -0.025804 | -0.18285 | 122.3191 | 122.2942 | 122.2887 | 44.637 | -122.3913 | 122.1242 | 122.3298 | 122.1728 | 49.3153 | -122.5691
1138.3125 | 122.5708 | -48.8022 | 73.4711 | 1.4211e-13 | -0.011705 | -0.011795 | 0.015302 | -0.038506 | 0.029953 | 0.0067908 | -0.014513 | 0.010448 | 0.035136 | -0.0013803 | 0.037556 | -48.7542 | -4.6276 | -48.877 | 73.5078 | 73.4784 | 73.482 | -48.8378 | -48.8629 | 0.096512 | -48.9753 | 73.3175 | 73.5186 | 73.3982 | -49.0247 | -0.035576 | 0.036714 | 0.04798 | -0.074791 | -0.039215 | 0.007292 | 0.010952 | -0.22252 | -0.15353 | -0.060759 | -0.1731 | 0.04942 | 0.047522 | -0.072899 | 122.31 | 122.2805 | 122.2842 | 44.1746 | -122.3088 | 122.1197 | 122.3208 | 122.2004 | 48.8987 | -122.4958
1140.1094 | 122.525 | -48.2071 | 74.1943 | 1.4211e-13 | -0.011705 | -0.011795 | 0.015302 | -0.038506 | 0.030381 | -0.00083919 | -0.014513 | 0.010234 | 0.035136 | -0.0011667 | 0.037342 | -48.1544 | -4.5131 | -48.2726 | 74.1213 | 74.0874 | 74.0818 | -48.2288 | -48.2586 | 0.10567 | -48.3709 | 73.9219 | 74.1321 | 73.9476 | -48.4157 | -0.021673 | -0.073049 | 0.052656 | -0.065551 | -0.043878 | -0.10698 | -0.11252 | -0.20863 | -0.27244 | -0.051462 | -0.1638 | 0.044827 | -0.062212 | -0.24673 | 122.3284 | 122.2944 | 122.2889 | 43.694 | -122.4231 | 122.129 | 122.3392 | 122.1547 | 48.3128 | -122.6101
1141.8906 | 122.4518 | -47.7356 | 74.7025 | 1.4211e-13 | -0.011705 | -0.012009 | 0.016157 | -0.038506 | 0.02974 | -0.00083919 | -0.014513 | 0.010448 | 0.035136 | -0.0011667 | 0.037342 | -47.6554 | -4.4627 | -47.7873 | 74.6203 | 74.5819 | 74.5809 | -47.7342 | -47.7641 | 0.10109 | -47.881 | 74.4164 | 74.6266 | 74.4421 | -47.9212 | 0.001355 | -0.082123 | 0.080204 | -0.051749 | -0.053104 | -0.12057 | -0.12157 | -0.18562 | -0.28608 | -0.028458 | -0.14538 | 0.040236 | -0.075841 | -0.26036 | 122.3559 | 122.3175 | 122.3165 | 43.2729 | -122.4367 | 122.152 | 122.3622 | 122.1777 | 47.8367 | -122.6237
1143.625 | 122.5113 | -47.9645 | 74.4232 | 1.4211e-13 | -0.011705 | -0.012009 | 0.015729 | -0.038079 | 0.02974 | 0.014421 | -0.014726 | 0.010021 | 0.034923 | -0.0018077 | 0.037129 | -47.9118 | -4.6047 | -48.03 | 74.3548 | 74.3255 | 74.3291 | -47.9998 | -48.025 | 0.096512 | -48.1465 | 74.16 | 74.3702 | 74.2177 | -48.1822 | -0.03534 | -0.068434 | 0.052697 | -0.065516 | -0.030176 | -0.097756 | -0.094155 | -0.21773 | -0.26324 | -0.060562 | -0.18206 | 0.035664 | -0.053007 | -0.20548 | 122.3193 | 122.2899 | 122.2935 | 43.3598 | -122.423 | 122.1245 | 122.3347 | 122.1822 | 48.061 | -122.6054
1145.4219 | 122.525 | -48.3261 | 74.0616 | 1.4211e-13 | -0.011491 | -0.011795 | 0.015729 | -0.038506 | 0.030167 | 0.0067908 | -0.014726 | 0.010448 | 0.035136 | -0.0015939 | 0.037342 | -48.2552 | -4.8061 | -48.3779 | 73.9977 | 73.9729 | 73.9719 | -48.3478 | -48.3684 | 0.091933 | -48.4945 | 73.812 | 74.0177 | 73.856 | -48.5302 | -0.021706 | -0.063914 | 0.07095 | -0.051832 | -0.030126 | -0.088699 | -0.089652 | -0.20408 | -0.24957 | -0.042332 | -0.16841 | 0.035672 | -0.043925 | -0.20555 | 122.3238 | 122.299 | 122.298 | 43.52 | -122.4094 | 122.1381 | 122.3438 | 122.1821 | 48.418 | -122.5918
1147.2031 | 122.5616 | -48.7885 | 73.5535 | 1.4211e-13 | -0.011491 | -0.011581 | 0.015302 | -0.038506 | 0.02974 | -0.00083919 | -0.014513 | 0.010234 | 0.035136 | -0.0013803 | 0.037129 | -48.7222 | -5.2594 | -48.8495 | 73.5307 | 73.5013 | 73.5049 | -48.824 | -48.8309 | 0.091933 | -48.9616 | 73.3404 | 73.5415 | 73.3295 | -49.0064 | -0.035573 | -0.022793 | 0.066296 | -0.061054 | -0.025481 | -0.052211 | -0.048553 | -0.21794 | -0.21304 | -0.042441 | -0.1731 | 0.044841 | -0.011983 | -0.22398 | 122.3191 | 122.2897 | 122.2934 | 43.529 | -122.3775 | 122.1289 | 122.3299 | 122.1179 | 48.8804 | -122.5599
1148.9375 | 122.5845 | -47.7585 | 74.5468 | 1.4211e-13 | -0.011919 | -0.012009 | 0.015302 | -0.038506 | 0.030167 | -0.00083919 | -0.014513 | 0.010234 | 0.035136 | -0.0013803 | 0.037556 | -47.8019 | -5.209 | -47.9338 | 74.4509 | 74.417 | 74.4161 | -47.8945 | -47.9152 | 0.10567 | -48.0367 | 74.2516 | 74.4618 | 74.2773 | -48.0723 | -0.13602 | -0.095884 | -0.043416 | -0.17537 | -0.039347 | -0.12977 | -0.13076 | -0.31383 | -0.29526 | -0.15667 | -0.27817 | 0.035661 | -0.085031 | -0.26955 | 122.2094 | 122.1755 | 122.1745 | 42.5494 | -122.4413 | 122.01 | 122.2203 | 122.0357 | 47.8642 | -122.6191
1150.7344 | 122.5525 | -47.4655 | 74.8764 | 1.4211e-13 | -0.011705 | -0.011795 | 0.015516 | -0.038293 | 0.029953 | -0.00083919 | -0.01494 | 0.010662 | 0.034923 | -0.0013803 | 0.037556 | -47.399 | -5.2457 | -47.5264 | 74.8676 | 74.8383 | 74.8281 | -47.487 | -47.5214 | 0.10567 | -47.6337 | 74.6682 | 74.8784 | 74.6939 | -47.6694 | -0.021464 | -0.00884 | 0.066513 | -0.060868 | -0.039404 | -0.038102 | -0.048274 | -0.20386 | -0.20821 | -0.055867 | -0.16821 | 0.035652 | 0.002032 | -0.18249 | 122.3331 | 122.3038 | 122.2936 | 42.2198 | -122.3634 | 122.1337 | 122.344 | 122.1594 | 47.5712 | -122.5458
1152.4531 | 122.6074 | -47.612 | 74.7299 | 1.4211e-13 | -0.011491 | -0.012222 | 0.015516 | -0.038506 | 0.02974 | -0.00083919 | -0.01494 | 0.010448 | 0.034923 | -0.00095292 | 0.037556 | -47.6142 | -5.3739 | -47.7324 | 74.6432 | 74.6185 | 74.6175 | -47.7022 | -47.732 | 0.10567 | -47.8535 | 74.453 | 74.6587 | 74.5245 | -47.8892 | -0.090188 | -0.086696 | -0.002186 | -0.12041 | -0.030218 | -0.11141 | -0.1124 | -0.27716 | -0.27691 | -0.12 | -0.2415 | 0.035657 | -0.071256 | -0.20541 | 122.2552 | 122.2305 | 122.2295 | 42.2381 | -122.4321 | 122.065 | 122.2707 | 122.1365 | 47.7177 | -122.6191
1154.25 | 122.5479 | -47.1771 | 75.1877 | 1.4211e-13 | -0.011919 | -0.011795 | 0.015516 | -0.038293 | 0.030381 | -0.00083919 | -0.01494 | 0.010234 | 0.034709 | -0.0011667 | 0.037342 | -47.1197 | -5.5387 | -47.2471 | 75.1377 | 75.113 | 75.112 | -47.2214 | -47.2467 | 0.10567 | -47.3636 | 74.9337 | 75.144 | 74.9915 | -47.3946 | -0.044277 | -0.049994 | 0.057404 | -0.069984 | -0.025707 | -0.074646 | -0.075679 | -0.21752 | -0.25394 | -0.069535 | -0.18646 | 0.031067 | -0.043688 | -0.19616 | 122.3148 | 122.2902 | 122.2891 | 41.6384 | -122.4091 | 122.1109 | 122.3211 | 122.1686 | 47.2828 | -122.5823
1156.0469 | 122.4976 | -46.7926 | 75.6088 | 1.4211e-13 | -0.011491 | -0.011795 | 0.015516 | -0.038506 | 0.029953 | 0.0067908 | -0.01494 | 0.010234 | 0.034923 | -0.0011667 | 0.037129 | -46.6665 | -5.5067 | -46.7939 | 75.5909 | 75.5664 | 75.5607 | -46.7635 | -46.7979 | 0.096512 | -46.9194 | 75.3962 | 75.5973 | 75.4631 | -46.9413 | 0.029094 | -0.017877 | 0.12614 | -0.001255 | -0.030349 | -0.042475 | -0.048119 | -0.14874 | -0.21265 | -0.005343 | -0.12684 | 0.021899 | -0.011549 | -0.14571 | 122.3836 | 122.359 | 122.3533 | 41.286 | -122.3723 | 122.1888 | 122.3899 | 122.2557 | 46.8891 | -122.5502
1157.7656 | 122.6074 | -46.6141 | 75.7324 | 1.4211e-13 | -0.011705 | -0.011795 | 0.015729 | -0.038293 | 0.02974 | -0.0084697 | -0.01494 | 0.010234 | 0.034923 | -0.00095292 | 0.037556 | -46.6024 | -5.7539 | -46.7389 | 75.6459 | 75.6213 | 75.6111 | -46.7086 | -46.7384 | 0.10109 | -46.8599 | 75.4465 | 75.6614 | 75.4585 | -46.8864 | -0.094487 | -0.086532 | 0.011713 | -0.12484 | -0.030357 | -0.11112 | -0.12135 | -0.27232 | -0.28588 | -0.12435 | -0.24585 | 0.026476 | -0.071045 | -0.27388 | 122.26 | 122.2354 | 122.2251 | 40.8602 | -122.441 | 122.0606 | 122.2755 | 122.0726 | 46.7152 | -122.6188
1159.5469 | 122.6074 | -46.4355 | 75.8698 | 1.4211e-13 | -0.011491 | -0.011795 | 0.015943 | -0.038293 | 0.029953 | -0.0084697 | -0.015153 | 0.010234 | 0.034923 | -0.0011667 | 0.037129 | -46.3689 | -5.8638 | -46.5008 | 75.8885 | 75.8548 | 75.8537 | -46.475 | -46.4958 | 0.10109 | -46.6264 | 75.6938 | 75.8857 | 75.7516 | -46.6529 | -0.039489 | 0.018793 | 0.066682 | -0.065301 | -0.025812 | -0.014928 | -0.016014 | -0.21733 | -0.17597 | -0.060204 | -0.19086 | 0.026471 | 0.015978 | -0.11818 | 122.3241 | 122.2904 | 122.2893 | 40.5718 | -122.3448 | 122.1293 | 122.3213 | 122.1871 | 46.5366 | -122.5226
1161.3281 | 122.4655 | -46.2982 | 76.1078 | 1.4211e-13 | -0.012132 | -0.011795 | 0.015943 | -0.038079 | 0.02974 | 0.0067908 | -0.014726 | 0.010448 | 0.034709 | -0.0011667 | 0.037342 | -46.1766 | -6.024 | -46.3086 | 76.0763 | 76.0471 | 76.0369 | -46.2781 | -46.3218 | 0.10567 | -46.4387 | 75.8769 | 76.0918 | 75.9622 | -46.4606 | 0.020075 | -0.03153 | 0.12165 | -0.010342 | -0.030417 | -0.06065 | -0.070907 | -0.16235 | -0.23087 | -0.023542 | -0.14046 | 0.021887 | -0.016022 | -0.1456 | 122.3745 | 122.3454 | 122.3351 | 40.2742 | -122.3859 | 122.1751 | 122.39 | 122.2604 | 46.4039 | -122.5684
1163.0469 | 122.4701 | -46.051 | 76.3275 | 1.4211e-13 | -0.011705 | -0.011795 | 0.015729 | -0.037865 | 0.030167 | 0.0067908 | -0.01494 | 0.010021 | 0.03535 | -0.0013803 | 0.037342 | -45.9064 | -6.0927 | -46.0247 | 76.3647 | 76.3219 | 76.3253 | -45.9988 | -46.0379 | 0.10109 | -46.1594 | 76.1608 | 76.3665 | 76.2461 | -46.1767 | 0.052197 | 0.037182 | 0.14458 | 0.026318 | -0.025879 | -0.005642 | -0.002182 | -0.12566 | -0.16673 | 0.013145 | -0.10836 | 0.017302 | 0.038967 | -0.081454 | 122.4157 | 122.3729 | 122.3764 | 39.9583 | -122.3263 | 122.2118 | 122.4175 | 122.2971 | 46.1521 | -122.5042
1164.8438 | 122.525 | -46.9803 | 75.4532 | 1.4211e-13 | -0.012132 | -0.011581 | 0.015302 | -0.038293 | 0.02974 | -0.00083919 | -0.014726 | 0.010021 | 0.034923 | -0.0011667 | 0.037129 | -46.9045 | -6.5139 | -47.0274 | 75.3437 | 75.3099 | 75.318 | -47.0062 | -47.0406 | 0.10567 | -47.1667 | 75.1489 | 75.3592 | 75.225 | -47.1886 | -0.025906 | -0.10947 | 0.07575 | -0.047065 | -0.021159 | -0.14325 | -0.13515 | -0.20831 | -0.30425 | -0.060331 | -0.18641 | 0.021904 | -0.093996 | -0.22815 | 122.324 | 122.2902 | 122.2983 | 40.4663 | -122.4594 | 122.1292 | 122.3395 | 122.2053 | 47.086 | -122.6418
1166.6406 | 122.4792 | -46.907 | 75.5127 | 1.4211e-13 | -0.011919 | -0.011795 | 0.015943 | -0.038293 | 0.029953 | -0.0084697 | -0.014726 | 0.010234 | 0.034923 | -0.0011667 | 0.037342 | -46.7992 | -6.7154 | -46.9404 | 75.4353 | 75.4015 | 75.4005 | -46.9192 | -46.9536 | 0.096512 | -47.0797 | 75.2359 | 75.437 | 75.3303 | -47.1062 | -0.012149 | -0.077411 | 0.10781 | -0.03332 | -0.021171 | -0.11119 | -0.11224 | -0.19914 | -0.27677 | -0.046579 | -0.17266 | 0.026482 | -0.075669 | -0.18235 | 122.3423 | 122.3086 | 122.3075 | 40.1916 | -122.4319 | 122.143 | 122.3441 | 122.2374 | 47.0036 | -122.6189
1168.4219 | 122.5845 | -42.2287 | 80.1132 | 1.4211e-13 | -0.011491 | -0.011581 | 0.015516 | -0.03872 | 0.029953 | -0.0084697 | -0.014726 | 0.010448 | 0.03535 | -0.0011667 | 0.037342 | -42.5871 | -5.7218 | -42.7283 | 79.6657 | 79.637 | 79.6128 | -42.6745 | -42.7137 | 0.15604 | -42.8536 | 79.4573 | 79.6677 | 79.5655 | -42.8433 | -0.44583 | -0.44751 | -0.35842 | -0.49965 | -0.053816 | -0.4762 | -0.50045 | -0.61461 | -0.65592 | -0.48504 | -0.62485 | -0.010248 | -0.44557 | -0.54767 | 121.8944 | 121.8657 | 121.8415 | 36.5069 | -122.7877 | 121.686 | 121.8964 | 121.7942 | 42.3847 | -122.9565
1170.2031 | 122.4335 | -38.1134 | 84.3475 | 1.4211e-13 | -0.011491 | -0.012009 | 0.015516 | -0.038506 | 0.02974 | 0.0067908 | -0.014513 | 0.010021 | 0.034709 | -0.00095292 | 0.037129 | -38.1644 | -4.8748 | -38.292 | 84.1342 | 84.0923 | 84.0723 | -38.2192 | -38.3044 | 0.16519 | -38.4351 | 83.9122 | 84.1409 | 83.9976 | -38.4019 | -0.10583 | -0.21331 | -0.050991 | -0.17859 | -0.072756 | -0.25523 | -0.2752 | -0.28845 | -0.43536 | -0.19104 | -0.32169 | -0.033246 | -0.20658 | -0.3499 | 122.2476 | 122.2057 | 122.1857 | 33.2386 | -122.5668 | 122.0256 | 122.2544 | 122.111 | 38.2786 | -122.7494
1171.9844 | 122.5845 | -35.7239 | 86.618 | 1.4211e-13 | -0.011491 | -0.011795 | 0.015729 | -0.03872 | 0.029312 | 0.0067908 | -0.014726 | 0.010662 | 0.035136 | -0.0011667 | 0.037129 | -35.7745 | -4.4627 | -35.9021 | 86.5379 | 86.4962 | 86.4715 | -35.8336 | -35.9189 | 0.16977 | -36.0496 | 86.3159 | 86.5447 | 86.3877 | -35.9247 | -0.10974 | -0.080168 | -0.050598 | -0.17825 | -0.068513 | -0.1218 | -0.14653 | -0.20083 | -0.30216 | -0.19505 | -0.32571 | -0.12488 | -0.073327 | -0.23038 | 122.2618 | 122.2201 | 122.1954 | 31.2611 | -122.4517 | 122.0398 | 122.2686 | 122.1115 | 35.8936 | -122.5428
1173.7031 | 122.5067 | -34.0347 | 88.3301 | 1.4211e-13 | -0.011705 | -0.011581 | 0.015516 | -0.03872 | 0.030167 | -0.00083919 | -0.014726 | 0.010448 | 0.035136 | -0.0011667 | 0.037129 | -34.0347 | -4.1376 | -34.167 | 88.2914 | 88.25 | 88.2251 | -34.089 | -34.1653 | 0.17435 | -34.3188 | 88.0695 | 88.2937 | 88.155 | -34.1893 | -0.054317 | -0.038681 | 4.1e-05 | -0.13223 | -0.077914 | -0.080106 | -0.10496 | -0.15461 | -0.26063 | -0.13056 | -0.28411 | -0.1295 | -0.036336 | -0.17507 | 122.3261 | 122.2847 | 122.2599 | 29.8971 | -122.4191 | 122.1042 | 122.3285 | 122.1897 | 34.2091 | -122.5194
1175.5 | 122.4976 | -33.2703 | 89.1724 | 1.4211e-13 | -0.011705 | -0.011368 | 0.015729 | -0.038293 | 0.030167 | -0.0161 | -0.014726 | 0.010662 | 0.035136 | -0.0011667 | 0.037342 | -33.1465 | -4.0461 | -33.2696 | 89.1842 | 89.1474 | 89.1225 | -33.2007 | -33.2908 | 0.15146 | -33.4306 | 88.9577 | 89.1957 | 89.0478 | -33.2965 | 0.06953 | 0.01182 | 0.12378 | 0.000646 | -0.068884 | -0.024922 | -0.049836 | -0.026206 | -0.21469 | -0.020488 | -0.1603 | -0.1341 | 0.023363 | -0.12453 | 122.4544 | 122.4177 | 122.3928 | 29.2242 | -122.3731 | 122.2279 | 122.466 | 122.3181 | 33.4217 | -122.4688
1177.2188 | 122.5479 | -33.2703 | 89.0945 | 1.4211e-13 | -0.011278 | -0.011795 | 0.015729 | -0.03872 | 0.029526 | 0.0067908 | -0.014726 | 0.010234 | 0.035136 | -0.00095292 | 0.036915 | -33.4029 | -4.2842 | -33.5306 | 88.9553 | 88.9048 | 88.8844 | -33.4892 | -33.5472 | 0.17435 | -33.6824 | 88.7104 | 88.9393 | 88.8372 | -33.5849 | -0.21894 | -0.13928 | -0.13261 | -0.26032 | -0.041373 | -0.18979 | -0.2101 | -0.31467 | -0.3841 | -0.2769 | -0.41213 | -0.097461 | -0.15522 | -0.25733 | 122.2255 | 122.175 | 122.1547 | 28.9861 | -122.5837 | 121.9807 | 122.2096 | 122.1075 | 33.4446 | -122.6795
1179 | 122.4976 | -45.4102 | 76.9363 | 1.4211e-13 | -0.011919 | -0.011581 | 0.015302 | -0.038293 | 0.029953 | 0.0067908 | -0.01494 | 0.010448 | 0.035136 | -0.0011667 | 0.037342 | -45.2929 | -7.654 | -45.4387 | 76.9187 | 76.8897 | 76.9389 | -45.4448 | -45.4564 | 0.087354 | -45.5825 | 76.7239 | 76.9296 | 76.7818 | -45.5998 | -0.034622 | -0.017659 | 0.11721 | -0.028531 | 0.006091 | -0.04668 | 0.002526 | -0.1896 | -0.2124 | -0.046228 | -0.17231 | 0.017289 | -0.00669 | -0.15458 | 122.3288 | 122.2998 | 122.349 | 37.7561 | -122.3811 | 122.1341 | 122.3398 | 122.1919 | 45.4975 | -122.5361
1180.7969 | 122.5479 | -75.8743 | 46.2341 | 1.4211e-13 | -0.012346 | -0.012009 | 0.015302 | -0.038293 | 0.030167 | -0.0084697 | -0.014726 | 0.010234 | 0.034923 | -0.00095292 | 0.037556 | -74.6908 | -16.9623 | -74.9182 | 47.2278 | 47.2823 | 47.3336 | -75.0521 | -74.9295 | -0.068322 | -75.0236 | 47.0965 | 47.274 | 47.0666 | -75.2476 | 0.82223 | 0.99371 | 1.1836 | 0.95609 | 0.13387 | 1.0482 | 1.0995 | 0.62674 | 0.86237 | 0.94479 | 0.85076 | 0.22402 | 1.0399 | 0.8325 | 123.1022 | 123.1567 | 123.208 | 58.912 | -121.2862 | 122.9708 | 123.1484 | 122.941 | 75.806 | -121.4817
1182.5156 | 122.5388 | -108.4808 | 14.1357 | 1.4211e-13 | -0.01256 | -0.012436 | 0.015088 | -0.038506 | 0.030594 | -0.0161 | -0.015153 | 0.009807 | 0.034496 | -0.00095292 | 0.038624 | -109.1111 | -28.2028 | -109.4247 | 12.574 | 12.5558 | 12.7331 | -109.742 | -109.4576 | -0.39799 | -109.515 | 12.4052 | 12.6003 | 12.5348 | -109.8543 | -1.2612 | -1.5617 | -0.63026 | -0.9439 | 0.3173 | -1.58 | -1.4026 | -1.3735 | -1.7305 | -0.97675 | -1.0342 | 0.3393 | -1.5355 | -1.6009 | 121.0549 | 121.0366 | 121.214 | 80.2781 | -123.8778 | 120.8861 | 121.0811 | 121.0156 | 108.0828 | -123.99
1184.3281 | 122.4518 | -107.0892 | 15.2527 | 1.4211e-13 | -0.012346 | -0.012863 | 0.015088 | -0.038293 | 0.030594 | -0.00083919 | -0.015153 | 0.0095932 | 0.034282 | -0.00095292 | 0.038838 | -107.8978 | -28.1249 | -108.1566 | 13.9384 | 13.8745 | 14.1159 | -108.5286 | -108.2488 | -0.34304 | -108.3199 | 13.7422 | 13.9372 | 13.858 | -108.6409 | -1.4394 | -1.3143 | -0.80859 | -1.0673 | 0.37207 | -1.3782 | -1.1368 | -1.5517 | -1.5105 | -1.1596 | -1.2307 | 0.32096 | -1.3154 | -1.3947 | 121.0276 | 120.9637 | 121.2051 | 78.9643 | -123.7813 | 120.8314 | 121.0265 | 120.9473 | 106.7462 | -123.8936
1186.0469 | 122.5937 | -118.9499 | 3.3463 | 1.4211e-13 | -0.012773 | -0.01265 | 0.015088 | -0.038079 | 0.030808 | -0.00083919 | -0.015153 | 0.010021 | 0.034282 | -0.0011667 | 0.038838 | -118.3594 | -31.9893 | -118.7461 | 3.3211 | 3.4025 | 3.5256 | -119.0922 | -118.7066 | -0.30184 | -118.8143 | 3.2528 | 3.3973 | 3.3959 | -119.2317 | -0.14231 | -0.025155 | 0.59045 | 0.20377 | 0.34609 | 0.056248 | 0.1793 | -0.28182 | -0.093425 | 0.24331 | 0.13554 | 0.41736 | 0.051042 | 0.049665 | 122.271 | 122.3524 | 122.4754 | 86.9606 | -122.4385 | 122.2027 | 122.3472 | 122.3458 | 118.6481 | -122.578
1187.8438 | 122.6852 | -117.6086 | 4.6509 | 1.4211e-13 | -0.012346 | -0.012436 | 0.015088 | -0.038506 | 0.030594 | 0.0067908 | -0.015367 | 0.0093796 | 0.034496 | -0.00073932 | 0.038838 | -117.2881 | -32.1633 | -117.684 | 4.3879 | 4.4511 | 4.5969 | -118.0345 | -117.6397 | -0.26978 | -117.7521 | 4.3105 | 4.4595 | 4.2842 | -118.1648 | -0.42583 | -0.26302 | 0.32055 | -0.075311 | 0.35052 | -0.1998 | -0.053933 | -0.5562 | -0.34042 | -0.031102 | -0.14344 | 0.41276 | -0.19135 | -0.36671 | 121.9965 | 122.0597 | 122.2056 | 85.4454 | -122.6853 | 121.9191 | 122.0682 | 121.8928 | 117.3389 | -122.8157
1189.5625 | 122.2641 | -115.8188 | 6.2347 | 1.4211e-13 | -0.012773 | -0.012436 | 0.015088 | -0.038079 | 0.031235 | -0.00083919 | -0.015367 | 0.0095932 | 0.034282 | -0.00095292 | 0.038838 | -114.3167 | -32.003 | -114.7218 | 7.405 | 7.4182 | 7.5593 | -115.0399 | -114.6865 | -0.22858 | -114.7668 | 7.2819 | 7.4356 | 7.4251 | -115.1703 | 0.77893 | 1.1703 | 1.5021 | 1.097 | 0.31805 | 1.1835 | 1.3246 | 0.64849 | 1.0472 | 1.1323 | 1.052 | 0.40353 | 1.2009 | 1.1903 | 123.2238 | 123.237 | 123.3781 | 83.8158 | -121.2746 | 123.1007 | 123.2544 | 123.2439 | 115.5902 | -121.405
1191.3594 | 122.5159 | -116.7023 | 5.777 | 1.4211e-13 | -0.012346 | -0.012436 | 0.014875 | -0.038293 | 0.030594 | -0.0084697 | -0.015153 | 0.009807 | 0.034282 | -0.00073932 | 0.038838 | -109.3034 | -30.863 | -109.6994 | 12.4046 | 12.4047 | 12.5591 | -110.003 | -109.6865 | -0.1599 | -109.7577 | 12.277 | 12.4263 | 12.3974 | -110.1382 | 6.6992 | 6.6276 | 7.3989 | 7.0028 | 0.3036 | 6.6277 | 6.7822 | 6.5641 | 6.5001 | 7.0157 | 6.9446 | 0.38052 | 6.6493 | 6.6205 | 129.1069 | 129.1069 | 129.2614 | 85.8393 | -115.78 | 128.9793 | 129.1286 | 129.0997 | 116.5424 | -115.9152
1193.0781 | 122.5662 | -119.0231 | 3.2547 | 1.4211e-13 | -0.012132 | -0.012436 | 0.014661 | -0.038079 | 0.030381 | -0.00083919 | -0.015581 | 0.0095932 | 0.034282 | -0.00073932 | 0.039052 | -118.0069 | -34.535 | -118.4027 | 3.637 | 3.7093 | 3.8461 | -118.7717 | -118.3632 | -0.25605 | -118.4801 | 3.5687 | 3.7224 | 3.7118 | -118.902 | 0.25146 | 0.3823 | 1.0162 | 0.62039 | 0.36893 | 0.45459 | 0.59135 | 0.1211 | 0.31404 | 0.65995 | 0.54303 | 0.42193 | 0.46767 | 0.45714 | 122.6601 | 122.7324 | 122.8692 | 84.4881 | -122.0264 | 122.5919 | 122.7455 | 122.735 | 118.7671 | -122.1567
1194.8594 | 122.5616 | -118.8583 | 3.4607 | 1.4211e-13 | -0.01256 | -0.012436 | 0.015088 | -0.038293 | 0.030808 | -0.0161 | -0.015367 | 0.009807 | 0.034282 | -0.00073932 | 0.038624 | -118.2587 | -35.0295 | -118.6637 | 3.3806 | 3.3063 | 3.5897 | -119.0327 | -118.6196 | -0.22858 | -118.7411 | 3.3123 | 3.4614 | 3.2494 | -119.163 | -0.17434 | -0.080077 | 0.59963 | 0.19463 | 0.36897 | -0.15435 | 0.12896 | -0.30469 | -0.14835 | 0.23875 | 0.11725 | 0.42194 | 0.000701 | -0.21129 | 122.239 | 122.1647 | 122.448 | 83.8289 | -122.4934 | 122.1707 | 122.3197 | 122.1077 | 118.6298 | -122.6237
1196.6562 | 122.4014 | -118.483 | 3.6896 | 1.4211e-13 | -0.012773 | -0.01265 | 0.015088 | -0.038079 | 0.030594 | -0.00083919 | -0.015153 | 0.0095932 | 0.034282 | -0.00095292 | 0.038624 | -118.1259 | -35.7117 | -118.5447 | 3.4951 | 3.4758 | 3.6904 | -118.9182 | -118.5234 | -0.21942 | -118.6312 | 3.4177 | 3.5759 | 3.3593 | -119.0623 | -0.43523 | -0.1945 | 0.35703 | -0.0617 | 0.37353 | -0.21381 | 0.000808 | -0.57932 | -0.27192 | -0.040465 | -0.14823 | 0.43109 | -0.11372 | -0.33029 | 121.978 | 121.9587 | 122.1734 | 82.7713 | -122.6078 | 121.9006 | 122.0588 | 121.8423 | 118.2636 | -122.7519
1198.375 | 122.4426 | -57.1426 | 65.1993 | 1.4211e-13 | -0.012346 | -0.012009 | 0.015516 | -0.038506 | 0.030381 | 0.0067908 | -0.01494 | 0.010448 | 0.034923 | -0.0011667 | 0.037556 | -57.4394 | -13.4231 | -57.6993 | 64.5296 | 64.5586 | 64.508 | -57.6842 | -57.6586 | 0.44449 | -57.7344 | 64.4078 | 64.5628 | 64.4012 | -57.8847 | -0.5416 | -0.66972 | -0.29677 | -0.55668 | -0.015078 | -0.64066 | -0.69132 | -0.74208 | -0.79149 | -0.51601 | -0.59172 | 0.15036 | -0.63644 | -0.79806 | 121.6722 | 121.7013 | 121.6506 | 43.7196 | -122.8835 | 121.5504 | 121.7055 | 121.5439 | 57.5871 | -123.084
1200.1719 | 122.3694 | -56.955 | 65.4419 | 1.4211e-13 | -0.012132 | -0.012009 | 0.015516 | -0.038293 | 0.029953 | -0.00083919 | -0.014726 | 0.010234 | 0.034923 | -0.00095292 | 0.037556 | -56.6886 | -13.7344 | -56.8935 | 65.3491 | 65.3325 | 65.3458 | -56.9333 | -56.9352 | 0.18809 | -57.0109 | 65.1724 | 65.3778 | 65.1246 | -57.1246 | 0.021656 | -0.0928 | 0.26641 | 0.061411 | 0.039755 | -0.10944 | -0.096051 | -0.16968 | -0.2695 | 0.019747 | -0.055967 | 0.11371 | -0.064059 | -0.31726 | 122.3041 | 122.2874 | 122.3008 | 43.2206 | -122.3752 | 122.1274 | 122.3328 | 122.0796 | 57.143 | -122.5665
1201.9062 | 122.3831 | -56.6574 | 65.6982 | 1.4211e-13 | -0.011919 | -0.011795 | 0.015516 | -0.038506 | 0.029953 | 0.0067908 | -0.01494 | 0.009807 | 0.034496 | -0.0011667 | 0.037342 | -56.4596 | -13.9908 | -56.628 | 65.5826 | 65.566 | 65.5794 | -56.7044 | -56.7154 | 0.13772 | -56.7911 | 65.4105 | 65.6068 | 65.3627 | -56.9049 | -0.046944 | -0.11565 | 0.19778 | 0.029405 | 0.076349 | -0.13226 | -0.11889 | -0.24744 | -0.28776 | -0.058021 | -0.13374 | 0.11371 | -0.091476 | -0.33552 | 122.24 | 122.2234 | 122.2368 | 42.6666 | -122.4026 | 122.0679 | 122.2642 | 122.0201 | 56.7951 | -122.6031
1203.7031 | 122.4243 | -56.4835 | 65.8905 | 1.4211e-13 | -0.011919 | -0.012009 | 0.015516 | -0.038293 | 0.029953 | 0.022052 | -0.014726 | 0.010234 | 0.034709 | -0.00073932 | 0.037129 | -56.2765 | -14.1282 | -56.4449 | 65.784 | 65.7537 | 65.7717 | -56.5166 | -56.5369 | 0.11025 | -56.6034 | 65.5982 | 65.7991 | 65.5825 | -56.7171 | -0.033159 | -0.10646 | 0.20696 | 0.038585 | 0.071744 | -0.13679 | -0.11885 | -0.23366 | -0.29231 | -0.053403 | -0.11996 | 0.1137 | -0.091436 | -0.30801 | 122.2675 | 122.2372 | 122.2551 | 42.3553 | -122.4071 | 122.0817 | 122.2825 | 122.066 | 56.5937 | -122.6076
1205.4375 | 122.4609 | -56.369 | 65.9821 | 1.4211e-13 | -0.011919 | -0.011795 | 0.015516 | -0.03872 | 0.030167 | 0.0067908 | -0.01494 | 0.010021 | 0.034709 | -0.00095292 | 0.037556 | -56.1666 | -14.728 | -56.3258 | 65.8848 | 65.8682 | 65.8815 | -56.4159 | -56.3858 | 0.10109 | -56.4935 | 65.7127 | 65.9044 | 65.7153 | -56.6072 | -0.046863 | -0.097289 | 0.2024 | 0.043181 | 0.090044 | -0.11387 | -0.10052 | -0.23821 | -0.2694 | -0.016745 | -0.12451 | 0.1137 | -0.077681 | -0.26678 | 122.2538 | 122.2372 | 122.2506 | 41.6411 | -122.3979 | 122.0817 | 122.2734 | 122.0843 | 56.4701 | -122.5893
1207.2344 | 122.4289 | -56.2042 | 66.1926 | 1.4211e-13 | -0.011919 | -0.011795 | 0.015516 | -0.038506 | 0.030167 | -0.0084697 | -0.01494 | 0.009807 | 0.034923 | -0.00095292 | 0.037129 | -55.9377 | -15.2224 | -56.1061 | 66.1183 | 66.0971 | 66.0967 | -56.2053 | -56.1706 | 0.087354 | -56.2783 | 65.937 | 66.1333 | 65.9442 | -56.3966 | -0.001027 | -0.074362 | 0.26653 | 0.098143 | 0.09917 | -0.095492 | -0.095892 | -0.19238 | -0.25562 | 0.033659 | -0.074105 | 0.11827 | -0.059322 | -0.24842 | 122.3225 | 122.3014 | 122.301 | 40.9818 | -122.3979 | 122.1412 | 122.3375 | 122.1484 | 56.2916 | -122.5892
1209.0312 | 122.4838 | -56.0394 | 66.3254 | 1.4211e-13 | -0.012132 | -0.011795 | 0.015943 | -0.038506 | 0.030167 | -0.00083919 | -0.01494 | 0.010234 | 0.035136 | -0.00073932 | 0.037129 | -55.8141 | -15.607 | -56.0008 | 66.2327 | 66.2116 | 66.2158 | -56.0908 | -56.0653 | 0.087354 | -56.173 | 66.0515 | 66.2478 | 66.0312 | -56.2821 | -0.051349 | -0.092654 | 0.22535 | 0.038649 | 0.089998 | -0.11377 | -0.1096 | -0.2427 | -0.27391 | -0.025826 | -0.13359 | 0.10911 | -0.077607 | -0.29418 | 122.2722 | 122.251 | 122.2552 | 40.4324 | -122.4162 | 122.0909 | 122.2872 | 122.0706 | 56.1268 | -122.6075
1210.7656 | 122.4197 | -55.8701 | 66.5405 | 1.4211e-13 | -0.011919 | -0.012009 | 0.015729 | -0.038293 | 0.029953 | 0.0067908 | -0.01494 | 0.010234 | 0.034923 | -0.00052552 | 0.037556 | -55.6676 | -15.6208 | -55.8589 | 66.3747 | 66.3673 | 66.376 | -55.9488 | -55.9187 | 0.082776 | -56.0357 | 66.198 | 66.3989 | 66.1731 | -56.1356 | -0.078775 | -0.16587 | 0.20249 | 0.011202 | 0.089977 | -0.17324 | -0.1645 | -0.26555 | -0.34255 | -0.04868 | -0.1656 | 0.099952 | -0.14166 | -0.36739 | 122.2447 | 122.2373 | 122.2461 | 40.2493 | -122.4894 | 122.068 | 122.2689 | 122.0432 | 55.9528 | -122.6761
1212.5625 | 122.5388 | -55.8243 | 66.5359 | 1.4211e-13 | -0.012132 | -0.012222 | 0.015516 | -0.03872 | 0.029953 | -0.00083919 | -0.014726 | 0.010662 | 0.034709 | -0.00073932 | 0.037342 | -55.5668 | -16.0283 | -55.7627 | 66.4754 | 66.4543 | 66.463 | -55.8573 | -55.8363 | 0.073618 | -55.9578 | 66.2941 | 66.4859 | 66.2418 | -56.0578 | -0.032973 | -0.060571 | 0.25743 | 0.06157 | 0.094543 | -0.081659 | -0.072927 | -0.23349 | -0.24182 | -0.012039 | -0.13354 | 0.09995 | -0.050092 | -0.29413 | 122.2997 | 122.2786 | 122.2873 | 39.796 | -122.3932 | 122.1184 | 122.3101 | 122.0661 | 55.8979 | -122.5937
1214.3438 | 122.5571 | -55.7373 | 66.5863 | 1.4211e-13 | -0.012132 | -0.012009 | 0.015516 | -0.038506 | 0.029953 | -0.00083919 | -0.014726 | 0.009807 | 0.03535 | -0.00073932 | 0.03777 | -55.5027 | -16.2068 | -55.7169 | 66.5303 | 66.5092 | 66.518 | -55.8115 | -55.786 | 0.073618 | -55.9029 | 66.3445 | 66.5454 | 66.3288 | -56.0028 | -0.074159 | -0.055985 | 0.23456 | 0.020378 | 0.094537 | -0.077066 | -0.068337 | -0.26552 | -0.24181 | -0.048648 | -0.16557 | 0.099949 | -0.040924 | -0.2575 | 122.2676 | 122.2465 | 122.2553 | 39.5305 | -122.3978 | 122.0818 | 122.2827 | 122.0661 | 55.8109 | -122.5891
1216.1406 | 122.5708 | -55.7098 | 66.6092 | 1.4211e-13 | -0.012346 | -0.012009 | 0.015729 | -0.03872 | 0.029953 | 0.0067908 | -0.01494 | 0.010021 | 0.034923 | -0.00095292 | 0.037342 | -55.4387 | -16.4816 | -55.6528 | 66.5898 | 66.5688 | 66.5821 | -55.7565 | -55.7264 | 0.06904 | -55.8296 | 66.4086 | 66.6049 | 66.3883 | -55.9479 | -0.046677 | -0.019354 | 0.27119 | 0.057008 | 0.10368 | -0.040428 | -0.027125 | -0.23804 | -0.2006 | -0.016591 | -0.11978 | 0.11826 | -0.00429 | -0.22086 | 122.2997 | 122.2786 | 122.2919 | 39.2283 | -122.3657 | 122.1184 | 122.3147 | 122.0982 | 55.7789 | -122.5571
1217.8594 | 122.5204 | -55.5817 | 66.7831 | 1.4211e-13 | -0.012346 | -0.012222 | 0.015302 | -0.038506 | 0.029953 | -0.00083919 | -0.01494 | 0.010234 | 0.034709 | -0.00031192 | 0.037556 | -55.3196 | -16.6372 | -55.5338 | 66.7089 | 66.6787 | 66.6874 | -55.6375 | -55.612 | 0.064461 | -55.7243 | 66.5185 | 66.7194 | 66.5257 | -55.8243 | -0.055799 | -0.074265 | 0.26205 | 0.047869 | 0.10367 | -0.10448 | -0.095767 | -0.24259 | -0.26467 | -0.030297 | -0.14264 | 0.099945 | -0.063775 | -0.25745 | 122.2905 | 122.2603 | 122.269 | 38.9444 | -122.4206 | 122.1001 | 122.301 | 122.1074 | 55.6461 | -122.6074
1219.6406 | 122.4838 | -55.545 | 66.8472 | 1.4211e-13 | -0.012346 | -0.011581 | 0.015516 | -0.038293 | 0.029953 | -0.00083919 | -0.014726 | 0.010234 | 0.035136 | -0.00073932 | 0.037556 | -55.2693 | -16.5777 | -55.488 | 66.7638 | 66.729 | 66.7469 | -55.5825 | -55.5708 | 0.073618 | -55.6785 | 66.5734 | 66.7697 | 66.5715 | -55.783 | -0.037473 | -0.083412 | 0.27579 | 0.057031 | 0.094504 | -0.1182 | -0.10033 | -0.238 | -0.27381 | -0.02571 | -0.13347 | 0.10452 | -0.077498 | -0.27576 | 122.3089 | 122.2741 | 122.2919 | 38.9673 | -122.4297 | 122.1185 | 122.3148 | 122.1165 | 55.6187 | -122.6303
1221.4219 | 122.5296 | -55.4626 | 66.8976 | 1.4211e-13 | -0.012346 | -0.011795 | 0.015302 | -0.038506 | 0.030167 | -0.0084697 | -0.01494 | 0.010021 | 0.034923 | -0.00073932 | 0.037129 | -55.2418 | -16.6052 | -55.4651 | 66.7776 | 66.7473 | 66.7606 | -55.5642 | -55.5524 | 0.06904 | -55.6556 | 66.5872 | 66.7926 | 66.5989 | -55.7693 | -0.10156 | -0.12003 | 0.22087 | -0.002476 | 0.09908 | -0.15024 | -0.13695 | -0.30666 | -0.31043 | -0.089793 | -0.19298 | 0.11368 | -0.10496 | -0.29864 | 122.2402 | 122.21 | 122.2233 | 38.8575 | -122.4618 | 122.0498 | 122.2553 | 122.0616 | 55.5317 | -122.6669
1223.1406 | 122.4655 | -55.4855 | 66.9022 | 1.4211e-13 | -0.012346 | -0.011795 | 0.015729 | -0.038506 | 0.030167 | -0.00083919 | -0.01494 | 0.010448 | 0.03535 | -0.00073932 | 0.037342 | -55.1868 | -16.596 | -55.3873 | 66.8325 | 66.816 | 66.8247 | -55.5001 | -55.4883 | 0.06904 | -55.6053 | 66.6558 | 66.8476 | 66.6539 | -55.7098 | -0.014562 | -0.069668 | 0.2987 | 0.098244 | 0.11281 | -0.086135 | -0.077428 | -0.22425 | -0.24633 | -0.002802 | -0.11972 | 0.10452 | -0.054594 | -0.24827 | 122.318 | 122.3016 | 122.3103 | 38.8895 | -122.4023 | 122.1414 | 122.3331 | 122.1394 | 55.5546 | -122.6119
1224.9219 | 122.6212 | -55.8517 | 66.4856 | 1.4211e-13 | -0.012346 | -0.011795 | 0.015516 | -0.038293 | 0.030167 | -0.0084697 | -0.015153 | 0.010021 | 0.035136 | -0.00073932 | 0.03777 | -55.3288 | -16.4266 | -55.5613 | 66.6677 | 66.6466 | 66.6645 | -55.6787 | -55.6486 | 0.073618 | -55.7655 | 66.4864 | 66.6873 | 66.5257 | -55.87 | 0.17307 | 0.18207 | 0.52298 | 0.29048 | 0.11741 | 0.16101 | 0.17889 | -0.018293 | 0.000828 | 0.20315 | 0.086232 | 0.10452 | 0.20172 | 0.040092 | 122.5194 | 122.4984 | 122.5162 | 39.4251 | -122.1643 | 122.3382 | 122.5391 | 122.3774 | 55.9254 | -122.3556
1226.6562 | 122.6212 | -55.4535 | 66.9067 | 1.4211e-13 | -0.012346 | -0.011795 | 0.015729 | -0.038506 | 0.030381 | 0.0067908 | -0.015367 | 0.010021 | 0.034923 | -0.00073932 | 0.037556 | -55.1136 | -16.39 | -55.3369 | 66.8874 | 66.871 | 66.8843 | -55.4589 | -55.4334 | 0.059882 | -55.5549 | 66.7108 | 66.9025 | 66.7134 | -55.664 | -0.005395 | -0.019304 | 0.33991 | 0.11656 | 0.12196 | -0.035765 | -0.022483 | -0.2105 | -0.19597 | 0.020098 | -0.1014 | 0.1091 | -0.004227 | -0.19333 | 122.3409 | 122.3245 | 122.3377 | 39.0635 | -122.3656 | 122.1643 | 122.356 | 122.1669 | 55.5134 | -122.5707
1228.4375 | 122.5433 | -55.22 | 67.1585 | 1.4211e-13 | -0.012773 | -0.012009 | 0.015516 | -0.038293 | 0.029953 | -0.00083919 | -0.01494 | 0.010234 | 0.034709 | -0.00095292 | 0.037556 | -54.8847 | -16.4587 | -55.1218 | 67.1072 | 67.0908 | 67.0994 | -55.2391 | -55.2136 | 0.06904 | -55.3305 | 66.9305 | 67.1177 | 66.9835 | -55.4351 | -0.019066 | -0.051312 | 0.33537 | 0.098281 | 0.11735 | -0.067747 | -0.059059 | -0.21502 | -0.22797 | 0.006417 | -0.1105 | 0.10451 | -0.040803 | -0.17496 | 122.3272 | 122.3108 | 122.3195 | 38.7614 | -122.3976 | 122.1506 | 122.3377 | 122.2036 | 55.2891 | -122.5936
1230.1406 | 122.5021 | -55.0964 | 67.3187 | 1.4211e-13 | -0.01256 | -0.012009 | 0.015516 | -0.038293 | 0.030167 | -0.0161 | -0.01494 | 0.010021 | 0.034709 | -0.00052552 | 0.037556 | -54.8023 | -16.4404 | -55.0348 | 67.1988 | 67.1732 | 67.1819 | -55.1704 | -55.1358 | 0.064461 | -55.2481 | 67.013 | 67.2093 | 67.0797 | -55.3481 | -0.073978 | -0.11996 | 0.29418 | 0.061673 | 0.13565 | -0.14554 | -0.13686 | -0.25162 | -0.30577 | -0.03934 | -0.15168 | 0.099934 | -0.10945 | -0.23903 | 122.2952 | 122.2696 | 122.2783 | 38.6561 | -122.4891 | 122.1094 | 122.3057 | 122.1761 | 55.1609 | -122.6668
1231.9219 | 122.5388 | -55.3162 | 67.0395 | 1.4211e-13 | -0.012346 | -0.011795 | 0.015729 | -0.038506 | 0.029953 | 0.0067908 | -0.01494 | 0.010021 | 0.034709 | -0.00052552 | 0.037342 | -54.9488 | -16.6464 | -55.1813 | 67.0339 | 67.0175 | 67.0308 | -55.3124 | -55.2915 | 0.06904 | -55.4038 | 66.8573 | 67.0536 | 66.8737 | -55.5129 | 0.003801 | -0.005548 | 0.3674 | 0.13489 | 0.13109 | -0.021991 | -0.00872 | -0.19673 | -0.18221 | 0.024709 | -0.087634 | 0.1091 | 0.014115 | -0.16583 | 122.3501 | 122.3337 | 122.3469 | 38.6698 | -122.3519 | 122.1734 | 122.3698 | 122.1898 | 55.3852 | -122.5524
1233.7031 | 122.5571 | -55.4031 | 66.9342 | 1.4211e-13 | -0.012132 | -0.012009 | 0.015516 | -0.03872 | 0.030167 | 0.0067908 | -0.014726 | 0.010234 | 0.034923 | -0.0011667 | 0.037129 | -55.0174 | -16.6601 | -55.2683 | 66.9607 | 66.9397 | 66.9575 | -55.4039 | -55.3739 | 0.055303 | -55.4771 | 66.7703 | 66.9712 | 66.8416 | -55.5953 | -0.000802 | 0.026484 | 0.3857 | 0.13488 | 0.13568 | 0.005453 | 0.023309 | -0.19217 | -0.16391 | 0.029268 | -0.073918 | 0.11825 | 0.036986 | -0.092592 | 122.3638 | 122.3428 | 122.3607 | 38.743 | -122.3381 | 122.1734 | 122.3743 | 122.2447 | 55.4584 | -122.5295
1235.4062 | 122.5159 | -55.5771 | 66.8106 | 1.4211e-13 | -0.012132 | -0.011795 | 0.015516 | -0.03872 | 0.029953 | 0.014421 | -0.01494 | 0.010234 | 0.035136 | -0.0011667 | 0.037129 | -55.3059 | -16.6739 | -55.543 | 66.6722 | 66.6558 | 66.6599 | -55.6833 | -55.6577 | 0.055303 | -55.7838 | 66.5002 | 66.6873 | 66.5303 | -55.8746 | -0.10617 | -0.13836 | 0.27121 | 0.034135 | 0.1403 | -0.15484 | -0.15071 | -0.29753 | -0.31045 | -0.080662 | -0.20674 | 0.090789 | -0.12329 | -0.28034 | 122.2493 | 122.2329 | 122.237 | 38.9032 | -122.4939 | 122.0772 | 122.2644 | 122.1074 | 55.6324 | -122.6852
1237.1875 | 122.5021 | -55.7556 | 66.6321 | 1.4211e-13 | -0.01256 | -0.011795 | 0.015516 | -0.038293 | 0.029953 | -0.00083919 | -0.01494 | 0.010234 | 0.034709 | -0.00052552 | 0.037342 | -55.3929 | -16.9669 | -55.6345 | 66.5853 | 66.5596 | 66.5821 | -55.784 | -55.7493 | 0.055303 | -55.8617 | 66.3994 | 66.5957 | 66.4204 | -55.9708 | -0.028375 | -0.04682 | 0.36275 | 0.1211 | 0.14947 | -0.072474 | -0.050013 | -0.21516 | -0.23265 | 0.006291 | -0.10605 | 0.10911 | -0.036336 | -0.2117 | 122.3409 | 122.3152 | 122.3377 | 38.7887 | -122.4161 | 122.155 | 122.3514 | 122.176 | 55.8109 | -122.6029
1238.9062 | 122.5159 | -56.1218 | 66.2613 | 1.4211e-13 | -0.01256 | -0.011795 | 0.015516 | -0.038506 | 0.030167 | 0.0067908 | -0.01494 | 0.010448 | 0.034709 | -0.00073932 | 0.037129 | -55.7362 | -17.3332 | -55.987 | 66.2236 | 66.2116 | 66.2249 | -56.1411 | -56.1019 | 0.050725 | -56.228 | 66.0469 | 66.2432 | 66.077 | -56.3279 | -0.01932 | -0.037725 | 0.38558 | 0.13478 | 0.1541 | -0.049684 | -0.036356 | -0.20609 | -0.2144 | 0.019942 | -0.10614 | 0.099956 | -0.0181 | -0.18431 | 122.3454 | 122.3334 | 122.3468 | 38.7886 | -122.4024 | 122.1687 | 122.365 | 122.1988 | 56.1726 | -122.5892
1240.6875 | 122.4884 | -56.0257 | 66.394 | 1.4211e-13 | -0.012346 | -0.011795 | 0.015302 | -0.038506 | 0.029953 | 0.0067908 | -0.01494 | 0.010234 | 0.034923 | -0.00073932 | 0.037129 | -55.6355 | -17.2691 | -55.8863 | 66.3106 | 66.2986 | 66.3119 | -56.0404 | -56.0103 | 0.059882 | -56.1272 | 66.1385 | 66.3393 | 66.1457 | -56.2226 | -0.014714 | -0.083486 | 0.39017 | 0.13937 | 0.15409 | -0.095436 | -0.082113 | -0.19691 | -0.25558 | 0.015386 | -0.10154 | 0.095376 | -0.0547 | -0.24838 | 122.3363 | 122.3243 | 122.3376 | 38.7566 | -122.4345 | 122.1642 | 122.365 | 122.1714 | 56.0856 | -122.6167
1242.4844 | 122.612 | -56.0623 | 66.2521 | 1.4211e-13 | -0.012346 | -0.011581 | 0.015302 | -0.03872 | 0.030381 | 0.0067908 | -0.01494 | 0.010234 | 0.034923 | -0.00073932 | 0.036915 | -55.6538 | -17.8185 | -55.9275 | 66.2739 | 66.2574 | 66.2753 | -56.0816 | -56.0607 | 0.050725 | -56.1776 | 66.0881 | 66.2844 | 66.0724 | -56.2821 | -0.019303 | 0.021794 | 0.40848 | 0.13479 | 0.15409 | 0.005261 | 0.023165 | -0.21981 | -0.16404 | 0.001641 | -0.11528 | 0.10453 | 0.032263 | -0.17973 | 122.3362 | 122.3197 | 122.3376 | 38.2438 | -122.3338 | 122.1504 | 122.3467 | 122.1347 | 56.113 | -122.5343
1244.2656 | 122.6486 | -56.0394 | 66.3345 | 1.4211e-13 | -0.01256 | -0.011795 | 0.015729 | -0.038293 | 0.030167 | -0.0084697 | -0.014726 | 0.010021 | 0.034709 | -0.00073932 | 0.037129 | -55.5852 | -18.1024 | -55.8543 | 66.3334 | 66.3123 | 66.3302 | -56.0221 | -55.9966 | 0.050725 | -56.1135 | 66.1568 | 66.3485 | 66.2006 | -56.2272 | 0.017335 | -0.001085 | 0.45427 | 0.18515 | 0.16782 | -0.02219 | -0.00429 | -0.18776 | -0.17776 | 0.042855 | -0.074067 | 0.11369 | 0.013966 | -0.13393 | 122.3729 | 122.3518 | 122.3697 | 37.937 | -122.3566 | 122.1962 | 122.3879 | 122.24 | 56.0902 | -122.5617
1246 | 122.5204 | -56.1584 | 66.2064 | 1.4211e-13 | -0.01256 | -0.012009 | 0.015516 | -0.03872 | 0.029953 | 0.0067908 | -0.01494 | 0.010021 | 0.035136 | -0.00095292 | 0.036701 | -55.7225 | -17.8506 | -56.0099 | 66.1778 | 66.1567 | 66.1837 | -56.1824 | -56.1477 | 0.046146 | -56.26 | 66.0057 | 66.1928 | 66.0083 | -56.3691 | -0.023909 | -0.028576 | 0.43594 | 0.14851 | 0.17242 | -0.049699 | -0.022631 | -0.21068 | -0.20068 | 0.010776 | -0.10157 | 0.10911 | -0.013533 | -0.19805 | 122.3362 | 122.3151 | 122.3422 | 38.3079 | -122.3887 | 122.1641 | 122.3513 | 122.1668 | 56.2046 | -122.5755
1247.7969 | 122.5433 | -56.4514 | 65.9637 | 1.4211e-13 | -0.012346 | -0.011795 | 0.015516 | -0.038506 | 0.030167 | 0.022052 | -0.01494 | 0.010021 | 0.035136 | -0.00052552 | 0.037342 | -55.9835 | -18.6839 | -56.2846 | 65.9122 | 65.8865 | 65.9044 | -56.4525 | -56.4316 | 0.046146 | -56.5393 | 65.7264 | 65.9227 | 65.7565 | -56.6484 | -0.001097 | -0.051508 | 0.46794 | 0.16678 | 0.16788 | -0.077241 | -0.059311 | -0.19702 | -0.23735 | 0.019865 | -0.0879 | 0.10912 | -0.041055 | -0.20726 | 122.3637 | 122.3379 | 122.3559 | 37.7675 | -122.4163 | 122.1778 | 122.3741 | 122.2079 | 56.4976 | -122.6122
1249.5781 | 122.699 | -104.0817 | 18.1595 | 1.4211e-13 | -0.012987 | -0.011795 | 0.015516 | -0.038293 | 0.030808 | -0.00083919 | -0.015367 | 0.0093796 | 0.034282 | -0.00052552 | 0.03777 | -103.1546 | -45.2947 | -103.6927 | 18.3474 | 18.3618 | 18.4838 | -104.1512 | -103.8029 | -0.34762 | -103.9244 | 18.197 | 18.3556 | 18.3496 | -104.2865 | -0.069444 | 0.18788 | 0.92712 | 0.389 | 0.45844 | 0.20236 | 0.32436 | -0.20473 | 0.03755 | 0.27884 | 0.15734 | 0.36207 | 0.1961 | 0.19015 | 122.4291 | 122.4436 | 122.5656 | 58.787 | -122.3107 | 122.2788 | 122.4373 | 122.4314 | 103.7341 | -122.4459
1251.3125 | 122.5937 | -105.4138 | 16.9418 | 1.4211e-13 | -0.012987 | -0.011795 | 0.015088 | -0.038506 | 0.030381 | -0.00083919 | -0.015153 | 0.0095932 | 0.034282 | -0.00052552 | 0.037342 | -104.5098 | -46.0135 | -105.0799 | 16.9006 | 16.979 | 17.0828 | -105.5523 | -105.1902 | -0.27894 | -105.3026 | 16.8098 | 16.9637 | 16.9715 | -105.6738 | -0.1385 | -0.041238 | 0.90401 | 0.33387 | 0.47237 | 0.037178 | 0.14096 | -0.26001 | -0.13208 | 0.22358 | 0.11124 | 0.37126 | 0.02186 | 0.02964 | 122.3144 | 122.3928 | 122.4966 | 59.4003 | -122.4942 | 122.2236 | 122.3775 | 122.3853 | 105.1349 | -122.6157
1253.0938 | 122.6715 | -106.3568 | 15.9622 | 1.4211e-13 | -0.013201 | -0.012436 | 0.015302 | -0.038293 | 0.030808 | -0.00083919 | -0.015153 | 0.009807 | 0.034282 | -9.8318e-05 | 0.037556 | -105.4163 | -46.2516 | -105.9956 | 15.9803 | 16.0449 | 16.1579 | -106.3765 | -106.1197 | -0.26063 | -106.2321 | 15.8849 | 16.0434 | 15.8177 | -106.6125 | -0.019715 | 0.01812 | 0.94048 | 0.36121 | 0.38092 | 0.082692 | 0.1957 | -0.25568 | -0.077324 | 0.2371 | 0.12476 | 0.38044 | 0.081175 | -0.14455 | 122.3372 | 122.4017 | 122.5147 | 60.1052 | -122.3387 | 122.2417 | 122.4002 | 122.1745 | 106.0962 | -122.5747
1254.8125 | 122.6624 | -106.7139 | 15.6052 | 1.4211e-13 | -0.013201 | -0.012009 | 0.015302 | -0.038293 | 0.030808 | -0.00083919 | -0.015367 | 0.0093796 | 0.034496 | -0.00031192 | 0.037556 | -105.7231 | -46.8102 | -106.3161 | 15.6507 | 15.5458 | 15.8283 | -106.7108 | -106.4356 | -0.23316 | -106.5526 | 15.5598 | 15.7137 | 15.4972 | -106.9376 | 0.003078 | 0.045531 | 0.99078 | 0.39778 | 0.39471 | -0.059356 | 0.22309 | -0.22372 | -0.045342 | 0.27822 | 0.1613 | 0.38502 | 0.10857 | -0.108 | 122.3646 | 122.2597 | 122.5421 | 59.9036 | -122.316 | 122.2737 | 122.4276 | 122.211 | 106.4807 | -122.5428
1256.5938 | 122.5433 | -106.9153 | 15.5045 | 1.4211e-13 | -0.012987 | -0.012222 | 0.014875 | -0.038293 | 0.030594 | -0.0084697 | -0.015367 | 0.009807 | 0.034282 | -0.00031192 | 0.037983 | -105.9245 | -47.8404 | -106.545 | 15.4172 | 15.3169 | 15.5993 | -106.9397 | -106.6692 | -0.224 | -106.7861 | 15.3309 | 15.4802 | 15.2499 | -107.1757 | -0.024452 | -0.087259 | 0.99075 | 0.37028 | 0.39474 | -0.18759 | 0.094872 | -0.2604 | -0.17356 | 0.24613 | 0.1292 | 0.38961 | -0.02423 | -0.25454 | 122.3325 | 122.2321 | 122.5146 | 59.0749 | -122.4442 | 122.2462 | 122.3955 | 122.1652 | 106.6913 | -122.6801
1258.375 | 122.5662 | -107.4371 | 14.9826 | 1.4211e-13 | -0.013201 | -0.012436 | 0.015088 | -0.038506 | 0.030808 | 0.0067908 | -0.015367 | 0.009807 | 0.034496 | -9.8318e-05 | 0.03777 | -106.3549 | -47.8496 | -106.9982 | 14.9594 | 14.8544 | 15.1415 | -107.4022 | -107.1453 | -0.224 | -107.2439 | 14.8685 | 15.0178 | 14.7921 | -107.6336 | 0.034928 | -0.023246 | 1.0822 | 0.43889 | 0.40396 | -0.12821 | 0.15886 | -0.19643 | -0.11414 | 0.29179 | 0.19318 | 0.38962 | 0.035182 | -0.19055 | 122.3965 | 122.2915 | 122.5786 | 59.5876 | -122.3848 | 122.3056 | 122.4549 | 122.2292 | 107.2131 | -122.6162
1260.1562 | 122.58 | -107.46 | 14.9323 | 1.4211e-13 | -0.013414 | -0.012222 | 0.015302 | -0.038506 | 0.030808 | -0.00083919 | -0.015367 | 0.009807 | 0.034709 | -0.00031192 | 0.03777 | -106.3274 | -48.2662 | -106.9799 | 14.9685 | 14.8819 | 15.146 | -107.3976 | -107.1224 | -0.21484 | -107.2348 | 14.8776 | 15.0269 | 14.8241 | -107.6336 | 0.062395 | 0.036264 | 1.1326 | 0.48009 | 0.41769 | -0.050387 | 0.21379 | -0.17355 | -0.054625 | 0.33757 | 0.22523 | 0.39878 | 0.094693 | -0.10814 | 122.4285 | 122.3419 | 122.6061 | 59.1938 | -122.3299 | 122.3376 | 122.487 | 122.2841 | 107.2452 | -122.5658
1261.875 | 122.6303 | -107.9224 | 14.4516 | 1.4211e-13 | -0.012773 | -0.012222 | 0.015516 | -0.038293 | 0.030808 | 0.0067908 | -0.015367 | 0.009807 | 0.034282 | -9.8318e-05 | 0.037556 | -106.8494 | -48.1243 | -107.4927 | 14.442 | 14.3461 | 14.6332 | -107.915 | -107.6398 | -0.224 | -107.7568 | 14.3648 | 14.5141 | 14.3159 | -108.151 | 0.007317 | -0.009598 | 1.073 | 0.42966 | 0.42234 | -0.10547 | 0.18164 | -0.22861 | -0.086764 | 0.28252 | 0.1656 | 0.39421 | 0.062542 | -0.13571 | 122.3644 | 122.2685 | 122.5556 | 59.7981 | -122.3666 | 122.2872 | 122.4365 | 122.2382 | 107.6984 | -122.6026
1263.6562 | 122.5067 | -108.1924 | 14.2548 | 1.4211e-13 | -0.013201 | -0.012009 | 0.015302 | -0.038293 | 0.030808 | -0.00083919 | -0.015153 | 0.0093796 | 0.034709 | -0.00052552 | 0.03777 | -107.0737 | -48.8019 | -107.717 | 14.2085 | 14.108 | 14.3952 | -108.1577 | -107.8917 | -0.21942 | -107.9949 | 14.1176 | 14.2669 | 14.0732 | -108.3937 | 0.034715 | -0.046258 | 1.1187 | 0.47541 | 0.44069 | -0.14674 | 0.14039 | -0.20121 | -0.13716 | 0.30077 | 0.19759 | 0.39879 | 0.012135 | -0.18154 | 122.4009 | 122.3005 | 122.5876 | 59.3905 | -122.4125 | 122.31 | 122.4593 | 122.2657 | 107.973 | -122.6484
1265.4375 | 122.6486 | -108.5907 | 13.765 | 1.4211e-13 | -0.012987 | -0.012009 | 0.015302 | -0.038506 | 0.031022 | -0.00083919 | -0.015367 | 0.009807 | 0.034709 | -0.00031192 | 0.03777 | -107.4812 | -49.4796 | -108.1474 | 13.769 | 13.6684 | 13.9556 | -108.5973 | -108.3221 | -0.21484 | -108.4344 | 13.6781 | 13.8365 | 13.6108 | -108.8241 | -0.006608 | 0.004024 | 1.1095 | 0.4433 | 0.44991 | -0.096505 | 0.19066 | -0.23336 | -0.086894 | 0.26863 | 0.15628 | 0.38965 | 0.071554 | -0.15417 | 122.3597 | 122.2591 | 122.5463 | 59.1111 | -122.3623 | 122.2688 | 122.4272 | 122.2015 | 108.3759 | -122.589
1267.1562 | 122.644 | -108.5037 | 13.8519 | 1.4211e-13 | -0.013414 | -0.012222 | 0.015088 | -0.038293 | 0.030808 | -0.00083919 | -0.015153 | 0.010021 | 0.034496 | -9.8318e-05 | 0.03777 | -107.3713 | -49.8687 | -108.0375 | 13.8743 | 13.7738 | 14.0609 | -108.492 | -108.2213 | -0.21484 | -108.3291 | 13.7834 | 13.9327 | 13.7115 | -108.7233 | 0.011733 | 0.022352 | 1.1324 | 0.46621 | 0.45447 | -0.078165 | 0.20899 | -0.2196 | -0.068563 | 0.28238 | 0.17462 | 0.39422 | 0.080729 | -0.14042 | 122.378 | 122.2775 | 122.5646 | 58.635 | -122.3439 | 122.2871 | 122.4364 | 122.2152 | 108.2889 | -122.5753
1268.9375 | 122.6715 | -108.9661 | 13.4033 | 1.4211e-13 | -0.012987 | -0.012009 | 0.015302 | -0.038506 | 0.030808 | -0.00083919 | -0.015153 | 0.0095932 | 0.034282 | -0.00031192 | 0.03777 | -107.8108 | -50.7341 | -108.4862 | 13.4073 | 13.3067 | 13.5893 | -108.9499 | -108.6884 | -0.22858 | -108.7916 | 13.3164 | 13.4702 | 13.2536 | -109.1949 | 0.016181 | 0.003965 | 1.1552 | 0.47988 | 0.4637 | -0.096606 | 0.186 | -0.22888 | -0.086961 | 0.2777 | 0.17451 | 0.40339 | 0.066899 | -0.14967 | 122.3733 | 122.2728 | 122.5554 | 58.232 | -122.3532 | 122.2824 | 122.4363 | 122.2197 | 108.7375 | -122.5983
1270.75 | 122.5342 | -108.8882 | 13.4949 | 1.4211e-13 | -0.013201 | -0.012222 | 0.015516 | -0.038506 | 0.030594 | -0.0084697 | -0.015581 | 0.0095932 | 0.034496 | -0.00031192 | 0.037342 | -107.7193 | -51.1691 | -108.4587 | 13.4302 | 13.3433 | 13.6214 | -108.9407 | -108.6426 | -0.21942 | -108.7595 | 13.353 | 13.4931 | 13.2949 | -109.1675 | -0.05248 | -0.064696 | 1.169 | 0.42953 | 0.48201 | -0.15153 | 0.1265 | -0.27923 | -0.14189 | 0.24567 | 0.12874 | 0.40797 | -0.001761 | -0.20002 | 122.3184 | 122.2316 | 122.5096 | 57.7192 | -122.4356 | 122.2412 | 122.3814 | 122.1831 | 108.6688 | -122.6623
1272.4688 | 122.5296 | -109.1537 | 13.3026 | 1.4211e-13 | -0.013201 | -0.012009 | 0.014661 | -0.038293 | 0.030808 | 0.014421 | -0.015367 | 0.0095932 | 0.034709 | 0.00011548 | 0.03777 | -107.8978 | -51.2973 | -108.651 | 13.2379 | 13.1327 | 13.365 | -109.1285 | -108.8578 | -0.224 | -108.9701 | 13.147 | 13.2962 | 13.0705 | -109.3735 | 0.025287 | -0.064727 | 1.2559 | 0.50274 | 0.47745 | -0.1699 | 0.062358 | -0.21977 | -0.15566 | 0.29597 | 0.18363 | 0.4034 | -0.00638 | -0.23211 | 122.3916 | 122.2865 | 122.5187 | 57.8565 | -122.4311 | 122.3007 | 122.45 | 122.2243 | 108.9297 | -122.6761
1274.2969 | 122.5571 | -109.2957 | 13.1149 | 1.4211e-13 | -0.013414 | -0.012009 | 0.015302 | -0.038293 | 0.031022 | 0.014421 | -0.014726 | 0.0095932 | 0.034282 | -0.00031192 | 0.03777 | -108.081 | -52.0069 | -108.8479 | 13.0273 | 12.9267 | 13.1544 | -109.3482 | -109.0638 | -0.224 | -109.1716 | 12.9363 | 13.0856 | 12.8645 | -109.575 | -0.052595 | -0.08765 | 1.2147 | 0.44778 | 0.50038 | -0.18827 | 0.039425 | -0.27933 | -0.17858 | 0.23183 | 0.12407 | 0.4034 | -0.029312 | -0.25046 | 122.3229 | 122.2223 | 122.45 | 57.2887 | -122.4632 | 122.232 | 122.3813 | 122.1601 | 109.0717 | -122.6899
1276.0625 | 122.644 | -109.2682 | 13.0783 | 1.4211e-13 | -0.013414 | -0.012009 | 0.015302 | -0.038293 | 0.030808 | -0.00083919 | -0.015367 | 0.009807 | 0.034496 | -9.8318e-05 | 0.037983 | -108.0123 | -52.245 | -108.7975 | 13.0685 | 12.9633 | 13.1956 | -109.2979 | -109.0226 | -0.22858 | -109.1304 | 12.9867 | 13.1268 | 12.9103 | -109.5384 | -0.029693 | -0.009824 | 1.2559 | 0.47068 | 0.50037 | -0.11501 | 0.11725 | -0.27017 | -0.091601 | 0.24557 | 0.13781 | 0.40798 | 0.048516 | -0.16805 | 122.3367 | 122.2315 | 122.4638 | 57.0232 | -122.3762 | 122.2549 | 122.395 | 122.1784 | 109.0396 | -122.6167
1277.7656 | 122.5845 | -109.2819 | 13.092 | 1.4211e-13 | -0.013201 | -0.012222 | 0.015302 | -0.038506 | 0.031022 | 0.0067908 | -0.015581 | 0.010021 | 0.034709 | -9.8318e-05 | 0.037983 | -107.9482 | -52.4236 | -108.7472 | 13.1005 | 13.0045 | 13.2368 | -109.2658 | -108.9814 | -0.22858 | -109.0937 | 13.0233 | 13.168 | 12.9515 | -109.4926 | 0.016092 | 0.008492 | 1.3337 | 0.53477 | 0.51868 | -0.087536 | 0.14473 | -0.21065 | -0.068706 | 0.30052 | 0.18817 | 0.39882 | 0.075991 | -0.14058 | 122.3825 | 122.2864 | 122.5187 | 56.8583 | -122.3579 | 122.3053 | 122.45 | 122.2334 | 109.0533 | -122.5846
1279.4688 | 122.5021 | -109.4879 | 12.9364 | 1.4211e-13 | -0.013414 | -0.012009 | 0.015302 | -0.038506 | 0.031022 | -0.00083919 | -0.015367 | 0.0095932 | 0.034709 | -9.8318e-05 | 0.037983 | -108.0947 | -52.7761 | -108.9257 | 12.9174 | 12.8213 | 13.0445 | -109.4536 | -109.1737 | -0.21942 | -109.2861 | 12.831 | 12.9803 | 12.7546 | -109.694 | 0.03435 | -0.019003 | 1.3932 | 0.56221 | 0.52786 | -0.11505 | 0.10807 | -0.20612 | -0.10536 | 0.31421 | 0.20186 | 0.40798 | 0.043908 | -0.18182 | 122.4053 | 122.3093 | 122.5324 | 56.7118 | -122.39 | 122.319 | 122.4682 | 122.2425 | 109.2685 | -122.6304
1281.1719 | 122.58 | -109.5749 | 12.8082 | 1.4211e-13 | -0.013201 | -0.012009 | 0.015088 | -0.038079 | 0.031235 | -0.00083919 | -0.015367 | 0.009807 | 0.034496 | -9.8318e-05 | 0.03777 | -108.2275 | -53.5591 | -109.0722 | 12.7617 | 12.6611 | 12.8934 | -109.6047 | -109.3157 | -0.22858 | -109.428 | 12.6799 | 12.8292 | 12.6126 | -109.8406 | -0.029779 | -0.046496 | 1.3474 | 0.50268 | 0.53246 | -0.14714 | 0.085146 | -0.26567 | -0.12828 | 0.25924 | 0.1469 | 0.41256 | 0.020987 | -0.19558 | 122.3366 | 122.236 | 122.4683 | 56.0158 | -122.4129 | 122.2548 | 122.4041 | 122.1875 | 109.3463 | -122.6488
1282.8906 | 122.6212 | -109.227 | 13.1104 | 1.4211e-13 | -0.012773 | -0.012009 | 0.015088 | -0.038506 | 0.030808 | -0.00083919 | -0.015367 | 0.0095932 | 0.034496 | -0.00031192 | 0.037556 | -107.9024 | -52.9318 | -108.7472 | 13.0776 | 12.977 | 13.2093 | -109.2933 | -109.0089 | -0.22858 | -109.1258 | 12.9867 | 13.136 | 12.9331 | -109.5292 | -0.066312 | -0.032711 | 1.3246 | 0.47984 | 0.54615 | -0.13332 | 0.098946 | -0.30221 | -0.12365 | 0.21811 | 0.10119 | 0.4034 | 0.025629 | -0.17721 | 122.3046 | 122.204 | 122.4363 | 56.2952 | -122.4037 | 122.2137 | 122.363 | 122.1601 | 108.9984 | -122.6395
1284.6406 | 122.5342 | -109.4925 | 12.8998 | 1.4211e-13 | -0.013628 | -0.012222 | 0.015516 | -0.038293 | 0.031022 | -0.0084697 | -0.015367 | 0.009807 | 0.034282 | -9.8318e-05 | 0.037556 | -108.081 | -53.0051 | -108.9623 | 12.8487 | 12.7481 | 12.9804 | -109.5177 | -109.2332 | -0.24231 | -109.3547 | 12.7669 | 12.9162 | 12.6905 | -109.7581 | -0.025177 | -0.051058 | 1.4115 | 0.53016 | 0.55534 | -0.1517 | 0.080587 | -0.26565 | -0.13284 | 0.25926 | 0.13776 | 0.4034 | 0.016428 | -0.2093 | 122.3412 | 122.2406 | 122.4729 | 56.4874 | -122.4175 | 122.2594 | 122.4087 | 122.183 | 109.2502 | -122.6579
1286.4062 | 122.5021 | -109.7992 | 12.6389 | 1.4211e-13 | -0.013201 | -0.012222 | 0.015302 | -0.038293 | 0.031235 | -0.0084697 | -0.015581 | 0.010021 | 0.034496 | -0.00031192 | 0.037983 | -108.3557 | -53.0875 | -109.2599 | 12.5374 | 12.4459 | 12.6828 | -109.8245 | -109.54 | -0.23316 | -109.6478 | 12.4648 | 12.614 | 12.3883 | -110.0558 | -0.025263 | -0.10146 | 1.4435 | 0.53928 | 0.56454 | -0.19298 | 0.043903 | -0.25657 | -0.1741 | 0.25919 | 0.15142 | 0.40799 | -0.024834 | -0.25056 | 122.3366 | 122.2451 | 122.482 | 56.7117 | -122.4633 | 122.264 | 122.4132 | 122.1875 | 109.566 | -122.6946
1288.1562 | 122.6486 | -109.6664 | 12.6709 | 1.4211e-13 | -0.013201 | -0.012009 | 0.015088 | -0.038293 | 0.031022 | -0.0084697 | -0.015153 | 0.0095932 | 0.034709 | -0.00031192 | 0.03777 | -108.2366 | -52.8174 | -109.1317 | 12.6519 | 12.5558 | 12.7789 | -109.7191 | -109.4347 | -0.24231 | -109.547 | 12.5655 | 12.7102 | 12.4844 | -109.955 | -0.052699 | -0.019047 | 1.4298 | 0.53472 | 0.58742 | -0.11513 | 0.10801 | -0.28858 | -0.10541 | 0.23175 | 0.1194 | 0.40799 | 0.039273 | -0.18645 | 122.3183 | 122.2222 | 122.4454 | 56.8491 | -122.39 | 122.2319 | 122.3766 | 122.1509 | 109.4241 | -122.6259
1289.875 | 122.6532 | -109.9319 | 12.4237 | 1.4211e-13 | -0.013201 | -0.012436 | 0.015302 | -0.038506 | 0.031235 | 0.0067908 | -0.015581 | 0.009807 | 0.034496 | -0.00031192 | 0.03777 | -108.4335 | -52.8906 | -109.379 | 12.4 | 12.3085 | 12.5408 | -109.9664 | -109.6865 | -0.24231 | -109.7897 | 12.3228 | 12.4675 | 12.2418 | -110.2069 | -0.034458 | -0.023666 | 1.4985 | 0.55299 | 0.58745 | -0.1152 | 0.11712 | -0.27492 | -0.10088 | 0.24542 | 0.14223 | 0.41715 | 0.043799 | -0.18193 | 122.332 | 122.2405 | 122.4728 | 57.0413 | -122.3901 | 122.2548 | 122.3995 | 122.1737 | 109.6896 | -122.6306
1291.5938 | 122.5067 | -110.2386 | 12.2086 | 1.4211e-13 | -0.012987 | -0.012222 | 0.014661 | -0.037865 | 0.031022 | -0.0084697 | -0.015581 | 0.009807 | 0.034496 | -9.8318e-05 | 0.03777 | -108.7128 | -54.2825 | -109.6491 | 12.1253 | 12.0292 | 12.2569 | -110.2411 | -109.9521 | -0.24689 | -110.0782 | 12.0481 | 12.1791 | 11.9579 | -110.4862 | -0.002493 | -0.083221 | 1.5259 | 0.58957 | 0.59207 | -0.17936 | 0.048391 | -0.24752 | -0.16044 | 0.28656 | 0.16048 | 0.408 | -0.029504 | -0.25065 | 122.364 | 122.2678 | 122.4956 | 55.9561 | -122.4497 | 122.2868 | 122.4177 | 122.1966 | 109.9918 | -122.6947
1293.2969 | 122.6212 | -109.7351 | 12.6297 | 1.4211e-13 | -0.013414 | -0.012009 | 0.015302 | -0.038079 | 0.031449 | -0.0084697 | -0.015581 | 0.010021 | 0.034496 | -9.8318e-05 | 0.038197 | -108.2229 | -55.2257 | -109.1821 | 12.5878 | 12.4917 | 12.7194 | -109.7924 | -109.4988 | -0.24231 | -109.6157 | 12.4968 | 12.6506 | 12.4295 | -110.0283 | -0.057298 | -0.041946 | 1.5122 | 0.55302 | 0.61032 | -0.13804 | 0.089687 | -0.29318 | -0.13289 | 0.23631 | 0.11939 | 0.41257 | 0.020949 | -0.2002 | 122.3229 | 122.2268 | 122.4545 | 54.5094 | -122.4221 | 122.2319 | 122.3858 | 122.1646 | 109.4928 | -122.658
1295 | 122.6761 | -108.728 | 13.5086 | 1.4211e-13 | -0.013414 | -0.012009 | 0.014875 | -0.038293 | 0.031449 | 0.0067908 | -0.015367 | 0.009807 | 0.034496 | -9.8318e-05 | 0.038624 | -107.2477 | -55.0334 | -108.2023 | 13.6042 | 13.6227 | 13.7404 | -108.9087 | -108.5327 | -0.24689 | -108.6496 | 13.4674 | 13.6122 | 13.6245 | -109.053 | -0.18065 | 0.09555 | 1.4803 | 0.52569 | 0.70634 | 0.11405 | 0.23181 | -0.32497 | -0.041157 | 0.19534 | 0.078414 | 0.40339 | 0.10355 | 0.11591 | 122.3322 | 122.3507 | 122.4684 | 53.6946 | -122.4173 | 122.1955 | 122.3402 | 122.3525 | 108.4811 | -122.5616
1296.7188 | 122.5891 | -109.021 | 13.3255 | 1.4211e-13 | -0.013201 | -0.011795 | 0.015088 | -0.038293 | 0.031235 | 0.0067908 | -0.015367 | 0.009807 | 0.034709 | 0.00011548 | 0.038838 | -107.5224 | -55.1982 | -108.477 | 13.2608 | 13.3342 | 13.4336 | -109.2063 | -108.8211 | -0.24231 | -108.9243 | 13.1744 | 13.3283 | 13.3406 | -109.346 | -0.18531 | -0.064723 | 1.4986 | 0.54396 | 0.72927 | 0.008687 | 0.10815 | -0.32505 | -0.15107 | 0.19985 | 0.096661 | 0.42171 | 0.002783 | 0.015141 | 122.2818 | 122.3552 | 122.4546 | 53.8228 | -122.5318 | 122.1954 | 122.3493 | 122.3616 | 108.7787 | -122.6715
1298.4375 | 122.6212 | -109.1812 | 13.1699 | 1.4211e-13 | -0.013414 | -0.012009 | 0.015302 | -0.038079 | 0.031235 | 0.0067908 | -0.015367 | 0.0095932 | 0.034282 | 0.00011548 | 0.038197 | -107.5773 | -55.7019 | -108.5457 | 13.1875 | 13.2609 | 13.3741 | -109.1697 | -108.8944 | -0.24689 | -109.0068 | 13.1057 | 13.2596 | 13.2536 | -109.4147 | 0.011542 | 0.017661 | 1.6039 | 0.63551 | 0.62396 | 0.091063 | 0.20427 | -0.23351 | -0.064113 | 0.2868 | 0.17446 | 0.40797 | 0.089743 | 0.083787 | 122.3687 | 122.4421 | 122.5553 | 53.4793 | -122.3395 | 122.287 | 122.4408 | 122.4349 | 108.9343 | -122.5846
1300.1406 | 122.58 | -109.3643 | 13.028 | 1.4211e-13 | -0.013201 | -0.011795 | 0.015088 | -0.038293 | 0.031235 | -0.00083919 | -0.015153 | 0.0093796 | 0.034709 | -9.8318e-05 | 0.037556 | -107.7467 | -56.2788 | -108.7334 | 12.9907 | 12.8992 | 13.1772 | -109.3666 | -109.0913 | -0.24689 | -109.1991 | 12.9043 | 13.0627 | 12.837 | -109.607 | -0.002246 | -0.037302 | 1.6176 | 0.6309 | 0.63315 | -0.12876 | 0.14929 | -0.24272 | -0.12366 | 0.27303 | 0.16526 | 0.40798 | 0.03477 | -0.19096 | 122.355 | 122.2635 | 122.5416 | 53.0855 | -122.3945 | 122.2686 | 122.427 | 122.2013 | 109.1174 | -122.635
1301.8438 | 122.6624 | -109.2865 | 13.0142 | 1.4211e-13 | -0.013201 | -0.012009 | 0.015302 | -0.038293 | 0.031449 | 0.0067908 | -0.015581 | 0.009807 | 0.034496 | 0.00011548 | 0.037983 | -107.6918 | -57.0114 | -108.6922 | 13.0364 | 13.1007 | 13.2139 | -109.4261 | -109.0592 | -0.26521 | -109.1624 | 12.9501 | 13.0994 | 13.1026 | -109.5841 | -0.13959 | 0.022215 | 1.5947 | 0.59429 | 0.73388 | 0.086441 | 0.19966 | -0.29764 | -0.064141 | 0.22726 | 0.12407 | 0.42171 | 0.085132 | 0.088333 | 122.3229 | 122.3872 | 122.5004 | 52.2751 | -122.4403 | 122.2366 | 122.3859 | 122.3891 | 109.0213 | -122.5984
1303.5469 | 122.5891 | -109.053 | 13.3347 | 1.4211e-13 | -0.013628 | -0.011795 | 0.015088 | -0.038293 | 0.031235 | -0.00083919 | -0.015153 | 0.0095932 | 0.034496 | -9.8318e-05 | 0.03777 | -107.4034 | -57.8309 | -108.4221 | 13.2837 | 13.1831 | 13.4703 | -109.0781 | -108.7937 | -0.26521 | -108.9106 | 13.2019 | 13.3512 | 13.1254 | -109.3232 | -0.025053 | -0.050987 | 1.6497 | 0.63095 | 0.656 | -0.15157 | 0.13562 | -0.27011 | -0.13276 | 0.25936 | 0.14244 | 0.41255 | 0.01652 | -0.20921 | 122.3367 | 122.2361 | 122.5233 | 51.2221 | -122.4127 | 122.2549 | 122.4042 | 122.1785 | 108.7878 | -122.6578
1305.2812 | 122.2458 | -78.7582 | 43.7302 | 1.4211e-13 | -0.013628 | -0.011795 | 0.015516 | -0.038293 | 0.030808 | -0.0084697 | -0.01494 | 0.0095932 | 0.034709 | 0.00011548 | 0.037556 | -77.7903 | -37.4928 | -78.6541 | 43.1714 | 43.1796 | 43.222 | -79.1457 | -79.0137 | 0.082776 | -79.0849 | 43.0583 | 43.2174 | 42.9963 | -79.3685 | -0.38742 | -0.55878 | 0.9679 | 0.10413 | 0.49155 | -0.55055 | -0.50813 | -0.61029 | -0.6719 | -0.25551 | -0.32664 | 0.28365 | -0.51276 | -0.73391 | 121.9296 | 121.9379 | 121.9803 | 41.2655 | -122.8758 | 121.8165 | 121.9756 | 121.7545 | 78.841 | -123.0987
1307.0312 | 122.4335 | -86.8332 | 35.5453 | 1.4211e-13 | -0.013201 | -0.011368 | 0.015302 | -0.038079 | 0.031235 | 0.0067908 | -0.015153 | 0.010448 | 0.034496 | -9.8318e-05 | 0.037556 | -85.7476 | -42.6116 | -86.6249 | 35.0814 | 35.0566 | 35.1454 | -87.232 | -87.0311 | -0.086637 | -87.1297 | 34.9589 | 35.1179 | 34.8875 | -87.3677 | -0.39885 | -0.46398 | 1.0856 | 0.20829 | 0.60715 | -0.48874 | -0.39997 | -0.53453 | -0.58644 | -0.19788 | -0.29649 | 0.23805 | -0.4275 | -0.6578 | 121.9146 | 121.8898 | 121.9786 | 44.2215 | -122.7774 | 121.7921 | 121.951 | 121.7207 | 86.7466 | -122.9131
1308.7188 | 122.5479 | -81.2805 | 40.9927 | 1.4211e-13 | -0.013414 | -0.011368 | 0.015729 | -0.038293 | 0.030594 | -0.00083919 | -0.015153 | 0.009807 | 0.034709 | -9.8318e-05 | 0.037342 | -76.2841 | -36.4122 | -77.07 | 44.6639 | 44.6082 | 44.7101 | -77.6804 | -77.5486 | -0.1599 | -77.6655 | 44.4593 | 44.6551 | 44.4339 | -77.9125 | 3.6001 | 3.6712 | 4.9965 | 4.2105 | 0.61038 | 3.6155 | 3.7173 | 3.3681 | 3.4665 | 3.732 | 3.615 | 0.24698 | 3.6623 | 3.4412 | 125.9445 | 125.8888 | 125.9906 | 44.8683 | -118.6731 | 125.7398 | 125.9356 | 125.7144 | 81.1206 | -118.9052
1310.4219 | 122.5204 | -91.7221 | 30.5191 | 1.4211e-13 | -0.013628 | -0.011581 | 0.015516 | -0.03872 | 0.031022 | 0.0067908 | -0.015367 | 0.0093796 | 0.034923 | 0.00011548 | 0.03777 | -90.2481 | -45.6747 | -91.1711 | 30.4572 | 30.4502 | 30.5851 | -91.811 | -91.6052 | -0.17821 | -91.7084 | 30.33 | 30.4843 | 30.2586 | -92.0335 | -0.088861 | -0.061903 | 1.474 | 0.55098 | 0.63984 | -0.068897 | 0.06599 | -0.31143 | -0.18906 | 0.11691 | 0.013721 | 0.32515 | -0.034798 | -0.26053 | 122.1793 | 122.1723 | 122.3072 | 46.0474 | -122.3301 | 122.0522 | 122.2064 | 121.9807 | 91.5439 | -122.5526
1312.1406 | 122.5296 | -93.3884 | 28.775 | 1.4211e-13 | -0.013201 | -0.011795 | 0.015516 | -0.038506 | 0.031022 | -0.00083919 | -0.015367 | 0.009807 | 0.034496 | -9.8318e-05 | 0.037342 | -91.846 | -45.7114 | -92.7964 | 28.7861 | 28.7652 | 28.8727 | -93.464 | -93.2261 | -0.17363 | -93.3384 | 28.6772 | 28.8452 | 28.6149 | -93.6819 | -0.075593 | 0.011066 | 1.5424 | 0.59195 | 0.66754 | -0.009861 | 0.097673 | -0.29354 | -0.097814 | 0.1623 | 0.04996 | 0.3435 | 0.070143 | -0.16016 | 122.1745 | 122.1535 | 122.2611 | 47.677 | -122.239 | 122.0656 | 122.2335 | 122.0032 | 93.2147 | -122.4569
1313.9688 | 122.3877 | -81.4316 | 40.8875 | 1.4211e-13 | -0.013201 | -0.011795 | 0.015516 | -0.038293 | 0.030808 | -0.0084697 | -0.015153 | 0.010021 | 0.034709 | 0.00011548 | 0.037556 | -79.7636 | -37.7766 | -80.6457 | 40.9738 | 40.9634 | 41.0289 | -81.2978 | -81.1062 | -0.086637 | -81.2048 | 40.8331 | 40.9922 | 40.8626 | -81.4977 | 0.13382 | 0.086307 | 1.668 | 0.78592 | 0.65209 | 0.075967 | 0.14144 | -0.066099 | -0.054336 | 0.32536 | 0.22675 | 0.29285 | 0.10475 | -0.02483 | 122.4053 | 122.395 | 122.4605 | 43.6549 | -122.1852 | 122.2647 | 122.4238 | 122.2942 | 81.3449 | -122.3851
1315.7812 | 122.4564 | -87.7716 | 34.4376 | 1.4211e-13 | -0.013201 | -0.011368 | 0.015302 | -0.038293 | 0.031235 | -0.00083919 | -0.015153 | 0.009807 | 0.034709 | 0.00011548 | 0.03777 | -87.0982 | -42.2408 | -88.1312 | 33.4835 | 33.5044 | 33.5474 | -88.7385 | -88.542 | -0.091215 | -88.604 | 33.4068 | 33.5382 | 33.3629 | -88.9474 | -0.9669 | -0.95405 | 0.6734 | -0.35955 | 0.60736 | -0.93321 | -0.89011 | -1.1758 | -1.0308 | -0.77044 | -0.83241 | 0.34339 | -0.89933 | -1.0747 | 121.2551 | 121.276 | 121.3191 | 45.5308 | -123.1761 | 121.1784 | 121.3098 | 121.1345 | 87.6804 | -123.385
1317.5625 | 122.4197 | -88.06 | 34.1949 | 1.4211e-13 | -0.013414 | -0.011368 | 0.015302 | -0.037865 | 0.031022 | -0.00083919 | -0.015153 | 0.010234 | 0.034282 | -9.8318e-05 | 0.037342 | -86.6175 | -41.3663 | -87.6047 | 33.9459 | 33.9302 | 34.0145 | -88.2806 | -88.0842 | -0.14616 | -88.1874 | 33.828 | 33.9824 | 33.7749 | -88.5124 | -0.22062 | -0.24901 | 1.4425 | 0.45535 | 0.67597 | -0.26476 | -0.18048 | -0.45243 | -0.36693 | -0.024175 | -0.12736 | 0.32507 | -0.21259 | -0.42 | 122.0059 | 121.9902 | 122.0745 | 46.6937 | -122.4756 | 121.888 | 122.0424 | 121.8349 | 87.9138 | -122.7074
1319.3594 | 122.5067 | -91.7358 | 30.3955 | 1.4211e-13 | -0.013414 | -0.011795 | 0.015302 | -0.038079 | 0.031022 | -0.0084697 | -0.015367 | 0.010021 | 0.034282 | 0.00011548 | 0.037342 | -90.2573 | -43.6968 | -91.2581 | 30.2558 | 30.2442 | 30.3378 | -91.9804 | -91.7563 | -0.20568 | -91.8595 | 30.1332 | 30.2966 | 30.0983 | -92.1984 | -0.24455 | -0.13976 | 1.4785 | 0.47772 | 0.72227 | -0.15135 | -0.057658 | -0.46253 | -0.26234 | -0.020458 | -0.12364 | 0.33889 | -0.098924 | -0.29718 | 121.9916 | 121.98 | 122.0737 | 48.0391 | -122.3759 | 121.869 | 122.0324 | 121.8342 | 91.5302 | -122.5939
1321.1406 | 122.4014 | -94.7296 | 27.4979 | 1.4211e-13 | -0.013201 | -0.011795 | 0.015302 | -0.038506 | 0.031235 | -0.00083919 | -0.015153 | 0.009807 | 0.034496 | -9.8318e-05 | 0.037342 | -93.0547 | -45.6518 | -94.1012 | 27.3759 | 27.332 | 27.4716 | -94.8239 | -94.5997 | -0.20568 | -94.712 | 27.2716 | 27.4304 | 27.1955 | -95.0556 | -0.094287 | -0.12192 | 1.6749 | 0.62838 | 0.72267 | -0.1659 | -0.02622 | -0.32594 | -0.22625 | 0.12994 | 0.017594 | 0.34354 | -0.067486 | -0.30237 | 122.1056 | 122.0616 | 122.2013 | 49.0778 | -122.3218 | 122.0012 | 122.16 | 121.9251 | 94.5239 | -122.5534
1322.9375 | 122.4152 | -100.4105 | 21.7987 | 1.4211e-13 | -0.013201 | -0.011795 | 0.015302 | -0.03872 | 0.031235 | -0.00083919 | -0.015367 | 0.009807 | 0.034709 | 0.00032908 | 0.037342 | -98.5808 | -48.9805 | -99.6867 | 21.7537 | 21.6541 | 21.872 | -100.4514 | -100.1949 | -0.25605 | -100.3118 | 21.6492 | 21.8079 | 21.5821 | -100.6829 | -0.040938 | -0.04502 | 1.8297 | 0.72373 | 0.76467 | -0.14461 | 0.073308 | -0.27246 | -0.14949 | 0.2156 | 0.098679 | 0.37114 | 0.009148 | -0.21658 | 122.1641 | 122.0646 | 122.2825 | 51.43 | -122.2501 | 122.0597 | 122.2183 | 121.9926 | 100.1544 | -122.4816
1324.7188 | 122.406 | -80.5801 | 41.748 | 1.4211e-13 | -0.013201 | -0.011581 | 0.015302 | -0.038506 | 0.031022 | -0.00083919 | -0.01494 | 0.010021 | 0.034709 | 0.00011548 | 0.037342 | -74.178 | -34.0909 | -75.138 | 46.4449 | 46.4078 | 46.4866 | -75.9267 | -75.7537 | -0.10495 | -75.8203 | 46.2174 | 46.395 | 46.3478 | -76.0718 | 4.6535 | 4.6969 | 6.4021 | 5.4421 | 0.78869 | 4.6597 | 4.7385 | 4.5084 | 4.4694 | 4.8264 | 4.7599 | 0.25152 | 4.6469 | 4.5997 | 127.0251 | 126.9879 | 127.0667 | 46.4893 | -117.6747 | 126.7976 | 126.9751 | 126.9279 | 80.4752 | -117.8198
1326.5 | 122.3282 | -90.6876 | 31.8878 | 1.4211e-13 | -0.013201 | -0.011795 | 0.015088 | -0.038079 | 0.031449 | -0.0084697 | -0.015367 | 0.010234 | 0.034496 | 0.00032908 | 0.037129 | -90.9898 | -46.1005 | -92.2058 | 29.1844 | 29.3513 | 29.2619 | -92.9786 | -92.5896 | 0.10567 | -92.6562 | 29.1992 | 29.2756 | 29.4207 | -93.0775 | -2.291 | -2.7034 | -0.30227 | -1.5183 | 0.77277 | -2.5366 | -2.6259 | -2.3899 | -2.6887 | -1.9021 | -1.9686 | 0.42133 | -2.6123 | -2.4671 | 119.872 | 120.0388 | 119.9494 | 44.587 | -124.8664 | 119.8867 | 119.9631 | 120.1083 | 90.7932 | -124.9653
1328.2188 | 122.4472 | -71.7316 | 50.5875 | 1.4211e-13 | -0.013201 | -0.011581 | 0.015516 | -0.038293 | 0.031235 | -0.0084697 | -0.014726 | 0.010021 | 0.034496 | 0.00032908 | 0.037129 | -75.3409 | -35.7575 | -76.3421 | 45.1355 | 45.1348 | 45.2 | -77.1493 | -76.9304 | 0.17435 | -76.9833 | 44.9767 | 45.1633 | 45.1436 | -77.2348 | -5.4177 | -5.4519 | -3.6093 | -4.6105 | 0.80717 | -5.4526 | -5.3875 | -5.5032 | -5.6108 | -5.1989 | -5.2517 | 0.25155 | -5.4242 | -5.4438 | 116.8671 | 116.8664 | 116.9316 | 35.9741 | -127.7367 | 116.7082 | 116.8949 | 116.8752 | 71.9059 | -127.8223
1330 | 122.3145 | -73.5077 | 48.5504 | 1.4211e-13 | -0.013414 | -0.011581 | 0.015729 | -0.038293 | 0.031235 | -0.00083919 | -0.015581 | 0.010234 | 0.034709 | 0.00011548 | 0.037342 | -71.0097 | -33.2118 | -71.979 | 49.5399 | 49.494 | 49.6046 | -72.813 | -72.6539 | -0.027113 | -72.7067 | 49.3125 | 49.5176 | 49.4521 | -72.9216 | 0.69468 | 0.98951 | 2.4979 | 1.5287 | 0.83403 | 0.94354 | 1.0542 | 0.58614 | 0.76207 | 0.85377 | 0.80095 | 0.21481 | 0.96714 | 0.90166 | 123.0476 | 123.0016 | 123.1123 | 40.2959 | -121.3634 | 122.8202 | 123.0252 | 122.9598 | 73.4806 | -121.472
1331.7812 | 122.4106 | -50.4135 | 71.6812 | 1.4211e-13 | -0.013414 | -0.011368 | 0.015516 | -0.038293 | 0.030381 | 0.0067908 | -0.01494 | 0.010021 | 0.034923 | 0.00011548 | 0.036915 | -56.5741 | -23.2671 | -57.5299 | 64.0488 | 64.0458 | 64.0226 | -58.2475 | -58.1303 | 0.22014 | -58.206 | 63.8492 | 64.0363 | 64.0303 | -58.3472 | -7.8339 | -7.6324 | -6.1606 | -7.1164 | 0.71752 | -7.6354 | -7.6586 | -7.9337 | -7.832 | -7.7167 | -7.7925 | 0.14121 | -7.6449 | -7.6509 | 114.4623 | 114.4593 | 114.4361 | 27.1465 | -129.9287 | 114.2627 | 114.4498 | 114.4439 | 50.6337 | -130.0284
1333.5 | 122.081 | -51.3428 | 71.9788 | 1.4211e-13 | -0.012773 | -0.01094 | 0.015943 | -0.038506 | 0.030808 | -0.00083919 | -0.01494 | 0.010021 | 0.034282 | 0.00032908 | 0.036701 | -48.9099 | -18.2306 | -49.8522 | 71.7726 | 71.7201 | 71.733 | -50.5411 | -50.5021 | 0.11025 | -50.5824 | 71.5182 | 71.7238 | 71.6812 | -50.6685 | 0.80165 | -0.20619 | 2.4329 | 1.4906 | 0.68897 | -0.25871 | -0.24576 | 0.67427 | -0.46057 | 0.84065 | 0.76036 | 0.086088 | -0.25498 | -0.29757 | 123.1153 | 123.0628 | 123.0758 | 33.1122 | -122.5199 | 122.861 | 123.0666 | 123.024 | 51.453 | -122.6473
1335.2812 | 122.3648 | -47.7493 | 74.3408 | 1.4211e-13 | -0.013201 | -0.01094 | 0.015943 | -0.038293 | 0.030594 | -0.00083919 | -0.014726 | 0.010448 | 0.034923 | 0.00011548 | 0.036915 | -47.4356 | -17.2508 | -48.3917 | 73.1781 | 73.1853 | 73.1753 | -49.0575 | -49.0095 | 0.22014 | -49.0898 | 72.9833 | 73.1798 | 73.1372 | -49.1666 | -1.3082 | -1.1627 | 0.3137 | -0.64235 | 0.66587 | -1.1555 | -1.1656 | -1.4173 | -1.3575 | -1.2601 | -1.3404 | 0.076895 | -1.161 | -1.2036 | 120.9275 | 120.9346 | 120.9246 | 30.4986 | -123.3984 | 120.7326 | 120.9291 | 120.8865 | 47.9695 | -123.5075
1337.0625 | 122.0856 | -63.9542 | 57.8979 | 1.4211e-13 | -0.012987 | -0.011154 | 0.015516 | -0.038293 | 0.030808 | -0.00083919 | -0.01494 | 0.010021 | 0.034496 | 0.00032908 | 0.036915 | -60.8411 | -26.7056 | -61.8701 | 59.3606 | 59.3799 | 59.3982 | -62.6157 | -62.5029 | 0.041567 | -62.5832 | 59.2112 | 59.3753 | 59.2594 | -62.7703 | 1.3384 | 1.4626 | 3.113 | 2.084 | 0.74561 | 1.4819 | 1.5003 | 1.1838 | 1.3132 | 1.4512 | 1.371 | 0.1871 | 1.4773 | 1.3615 | 123.3147 | 123.334 | 123.3524 | 37.2486 | -120.5137 | 123.1654 | 123.3295 | 123.2136 | 63.9957 | -120.6683
1338.7969 | 121.8246 | -61.4136 | 60.7864 | 1.4211e-13 | -0.012987 | -0.011154 | 0.015302 | -0.038293 | 0.030808 | 0.0067908 | -0.015153 | 0.010021 | 0.034496 | -9.8318e-05 | 0.036488 | -62.1506 | -27.2504 | -63.1246 | 57.8176 | 57.8322 | 57.8736 | -64.0123 | -63.8445 | 0.009516 | -63.9431 | 57.6225 | 57.8186 | 57.7165 | -64.1256 | -2.5987 | -2.9688 | -0.73699 | -1.711 | 0.88773 | -2.9543 | -2.9129 | -2.7121 | -3.164 | -2.4309 | -2.5295 | 0.18256 | -2.9679 | -3.07 | 119.2312 | 119.2457 | 119.2871 | 34.1631 | -124.7988 | 119.036 | 119.2321 | 119.13 | 61.4231 | -124.9121
1340.5781 | 122.3511 | -65.0162 | 56.7261 | 1.4211e-13 | -0.013628 | -0.011154 | 0.015516 | -0.038506 | 0.030808 | -0.00083919 | -0.01494 | 0.009807 | 0.034923 | -9.8318e-05 | 0.036915 | -58.0621 | -24.1782 | -59.0499 | 62.277 | 62.2371 | 62.2873 | -59.9142 | -59.8198 | -0.077479 | -59.8955 | 62.0178 | 62.214 | 62.1852 | -60.0505 | 5.102 | 5.5509 | 6.9541 | 5.9663 | 0.86427 | 5.511 | 5.5613 | 4.9657 | 5.2917 | 5.1964 | 5.1207 | 0.15499 | 5.4879 | 5.4591 | 127.2932 | 127.2533 | 127.3035 | 40.838 | -116.6403 | 127.034 | 127.2302 | 127.2013 | 64.9387 | -116.7766
1342.3594 | 122.2366 | -66.0919 | 55.838 | 1.4211e-13 | -0.012987 | -0.010727 | 0.015943 | -0.038293 | 0.030808 | 0.0067908 | -0.01494 | 0.009807 | 0.035136 | -9.8318e-05 | 0.036701 | -47.3029 | -16.7105 | -48.3505 | 73.0957 | 73.1487 | 73.0471 | -49.0392 | -48.9774 | 0.29797 | -49.0669 | 72.9146 | 73.0699 | 73.1463 | -49.1438 | 17.0527 | 17.2577 | 18.7891 | 17.7414 | 0.68876 | 17.3107 | 17.209 | 16.9482 | 17.0766 | 17.1145 | 17.0251 | 0.076895 | 17.2319 | 17.3083 | 139.1876 | 139.2406 | 139.139 | 49.3814 | -104.8772 | 139.0066 | 139.1618 | 139.2383 | 66.3899 | -104.9818
1344.0625 | 122.4426 | -38.5941 | 83.2581 | 1.4211e-13 | -0.013414 | -0.01094 | 0.015516 | -0.038293 | 0.030808 | -0.0084697 | -0.01494 | 0.010234 | 0.034923 | 0.00032908 | 0.036915 | -46.1537 | -16.0191 | -47.2288 | 74.2083 | 74.3117 | 74.1597 | -47.8899 | -47.7961 | 0.51317 | -47.8764 | 74.1005 | 74.2329 | 74.3597 | -47.9624 | -9.2959 | -9.0498 | -7.5596 | -8.6347 | 0.66113 | -8.9463 | -9.0984 | -9.3684 | -9.1576 | -9.202 | -9.2823 | 0.086024 | -9.0252 | -8.8984 | 112.8023 | 112.9058 | 112.7537 | 22.5749 | -131.148 | 112.6945 | 112.8269 | 112.9537 | 39.1072 | -131.2205
1345.8438 | 121.8338 | -33.5678 | 87.7762 | 1.4211e-13 | -0.013201 | -0.01094 | 0.015729 | -0.038079 | 0.031022 | -0.0084697 | -0.015153 | 0.010234 | 0.034923 | 0.00032908 | 0.037342 | -66.5229 | -29.8007 | -67.4099 | 53.9214 | 53.7569 | 54.0275 | -68.518 | -68.4552 | -0.52619 | -68.5081 | 53.5384 | 53.8352 | 53.582 | -68.6724 | -34.9502 | -33.8547 | -32.9551 | -33.842 | 1.1081 | -34.0193 | -33.7486 | -35.1046 | -34.2377 | -34.8874 | -34.9403 | 0.16435 | -33.941 | -34.1942 | 87.4892 | 87.3247 | 87.5953 | 3.7671 | -156.2942 | 87.1062 | 87.403 | 87.1498 | 33.0416 | -156.4486
1347.625 | 122.3969 | -27.182 | 94.4733 | 1.4211e-13 | -0.012773 | -0.010727 | 0.016157 | -0.038506 | 0.030381 | -0.0084697 | -0.01494 | 0.010234 | 0.034923 | 0.00054268 | 0.036701 | -27.7669 | -2.7503 | -28.8562 | 92.6638 | 92.7236 | 92.5015 | -29.4414 | -29.3943 | 0.49944 | -29.5203 | 92.4785 | 92.6022 | 92.7886 | -29.5327 | -2.2594 | -1.8095 | -0.58487 | -1.6741 | 0.58528 | -1.7497 | -1.9717 | -2.3507 | -1.9947 | -2.2123 | -2.3383 | 0.012333 | -1.8711 | -1.6847 | 119.8458 | 119.9056 | 119.6835 | 24.4317 | -123.9147 | 119.6605 | 119.7842 | 119.9706 | 27.6814 | -124.0059
1349.4062 | 122.5159 | -77.3804 | 44.8288 | 1.4211e-13 | -0.013414 | -0.01094 | 0.015729 | -0.038293 | 0.030808 | -0.00083919 | -0.015153 | 0.010021 | 0.035136 | 0.00032908 | 0.036915 | -64.6137 | -29.32 | -65.606 | 55.6383 | 55.5931 | 55.6896 | -66.6406 | -66.5093 | -0.24689 | -66.5942 | 55.3744 | 55.5888 | 55.5096 | -66.7814 | 10.7398 | 10.8095 | 12.7666 | 11.7744 | 1.0346 | 10.7643 | 10.8608 | 10.599 | 10.5456 | 10.8711 | 10.7862 | 0.1872 | 10.76 | 10.6808 | 133.0187 | 132.9735 | 133.0699 | 48.0604 | -111.4694 | 132.7548 | 132.9692 | 132.8899 | 77.1335 | -111.6102
1351.1094 | 122.2458 | -0.43488 | 99.4263 | 1.4211e-13 | -0.012773 | -0.010299 | 0.015943 | -0.038506 | 0.029953 | -0.00083919 | -0.014299 | 0.010448 | 0.034923 | 0.00032908 | 0.036274 | 0.9442 | 16.8781 | 0.009904 | 121.2695 | 121.1908 | 121.0766 | -0.72242 | -0.60334 | 0.7879 | -0.71569 | 120.9705 | 121.2185 | 121.1164 | -0.86929 | -0.28755 | 21.8433 | 1.3791 | 0.44478 | 0.73233 | 21.7645 | 21.6503 | -0.43441 | 21.5442 | -0.16847 | -0.28081 | 0.1536 | 21.7922 | 21.6901 | 121.7044 | 121.6256 | 121.5115 | 17.313 | -100.1487 | 121.4054 | 121.6533 | 121.5512 | 1.2228 | -100.2956
1352.8906 | 121.9666 | -1.1398 | 120.3003 | 1.4211e-13 | -0.01256 | -0.010299 | 0.01637 | -0.03872 | 0.030167 | 0.0067908 | -0.014299 | 0.010448 | 0.035136 | -0.00031192 | 0.036274 | 0.5413 | 16.7591 | -0.37467 | 121.1001 | 121.0213 | 120.9392 | -1.1574 | -1.0429 | 0.52691 | -1.1461 | 120.8057 | 121.0765 | 120.9057 | -1.2264 | -0.017588 | 0.79983 | 1.6811 | 0.76516 | 0.78275 | 0.72104 | 0.63894 | -0.086602 | 0.5054 | 0.096934 | -0.006252 | 0.08035 | 0.77624 | 0.60546 | 122.24 | 122.1612 | 122.0791 | 17.8989 | -121.4577 | 121.9455 | 122.2164 | 122.0456 | 1.6667 | -121.5267
1354.5938 | 106.9336 | -2.504 | 99.1608 | 1.4211e-13 | -0.012773 | -0.010513 | 0.01637 | -0.038293 | 0.029953 | -0.00083919 | -0.014513 | 0.010662 | 0.035136 | -9.8318e-05 | 0.036488 | -0.41559 | 16.1456 | -1.3315 | 120.1707 | 120.0827 | 120.0235 | -2.1327 | -2.0273 | 0.43992 | -2.1351 | 119.8625 | 120.1379 | 119.9488 | -2.22 | 0.37124 | 21.0099 | 2.0884 | 1.1724 | 0.8012 | 20.9219 | 20.8627 | 0.28393 | 20.7018 | 0.47665 | 0.36888 | 0.084953 | 20.9772 | 20.7881 | 122.6747 | 122.5866 | 122.5275 | 18.6495 | -101.2935 | 122.3665 | 122.6419 | 122.4528 | 2.9439 | -101.3808
1356.375 | 121.5866 | -3.6804 | 117.7963 | 1.4211e-13 | -0.013201 | -0.010513 | 0.016157 | -0.03872 | 0.030167 | -0.00083919 | -0.014513 | 0.010448 | 0.035136 | 0.00054268 | 0.036274 | -2.0821 | 15.0559 | -2.9797 | 118.4813 | 118.4113 | 118.3386 | -3.8269 | -3.7169 | 0.43992 | -3.8384 | 118.1868 | 118.4484 | 118.2914 | -3.8913 | -0.14651 | 0.68496 | 1.5983 | 0.70071 | 0.84722 | 0.61502 | 0.54226 | -0.21089 | 0.39047 | -0.036445 | -0.15795 | 0.052941 | 0.65209 | 0.49504 | 122.1617 | 122.0918 | 122.019 | 18.7363 | -121.6233 | 121.8672 | 122.1288 | 121.9718 | 4.1203 | -121.6876
1358.1094 | 104.8004 | -4.3259 | 117.1143 | 1.4211e-13 | -0.012987 | -0.010513 | 0.016157 | -0.038506 | 0.029953 | -0.00083919 | -0.014513 | 0.010662 | 0.035136 | 0.00032908 | 0.036274 | -3.7212 | 14.0257 | -4.6279 | 116.8285 | 116.7629 | 116.6903 | -5.4753 | -5.3927 | 0.40329 | -5.5233 | 116.5523 | 116.8093 | 116.6431 | -5.5488 | -1.1495 | -0.28577 | 0.60468 | -0.30203 | 0.84745 | -0.35132 | -0.42397 | -1.223 | -0.56199 | -1.0668 | -1.1975 | 0.025507 | -0.30498 | -0.47119 | 121.1544 | 121.0888 | 121.0162 | 18.3515 | -122.5896 | 120.8781 | 121.1351 | 120.9689 | 4.7292 | -122.6631
1359.8906 | 122.4243 | -5.9738 | 107.8766 | 1.4211e-13 | -0.012773 | -0.010299 | 0.016157 | -0.03872 | 0.030381 | 0.014421 | -0.014513 | 0.010662 | 0.03535 | 0.00032908 | 0.036274 | -4.179 | 13.5815 | -5.0766 | 116.3706 | 116.305 | 116.237 | -5.9378 | -5.8597 | 0.38497 | -5.9949 | 116.0898 | 116.3606 | 116.1806 | -6.0205 | 0.035999 | 8.4941 | 1.7948 | 0.89725 | 0.86125 | 8.4285 | 8.3604 | -0.04664 | 8.2133 | 0.11411 | -0.021122 | 0.025518 | 8.484 | 8.304 | 122.3445 | 122.2789 | 122.2108 | 19.5554 | -113.8144 | 122.0637 | 122.3344 | 122.1544 | 6.3588 | -113.897
1361.6562 | 122.0535 | -3.8681 | 118.5242 | 1.4211e-13 | -0.01256 | -0.010299 | 0.016584 | -0.038506 | 0.030381 | 0.0067908 | -0.014726 | 0.010448 | 0.03535 | 0.00054268 | 0.036915 | -1.2122 | 15.4313 | -2.119 | 119.3832 | 119.3088 | 119.236 | -2.9707 | -2.8698 | 0.42618 | -2.9867 | 119.0796 | 119.3596 | 119.175 | -3.0763 | 0.89743 | 0.85906 | 2.6559 | 1.7491 | 0.85168 | 0.78465 | 0.71183 | 0.79183 | 0.55543 | 0.9983 | 0.88138 | 0.089552 | 0.83539 | 0.65087 | 123.2513 | 123.1769 | 123.1041 | 19.2994 | -121.4948 | 122.9477 | 123.2277 | 123.0431 | 4.2943 | -121.6004
1363.4531 | 122.438 | -11.4349 | 110.8383 | 1.4211e-13 | -0.012773 | -0.010513 | 0.016584 | -0.038506 | 0.030594 | -0.00083919 | -0.014513 | 0.010234 | 0.034923 | 0.00011548 | 0.036488 | -9.7784 | 9.2731 | -10.7033 | 110.7942 | 110.7325 | 110.6832 | -11.5012 | -11.4778 | 0.33003 | -11.6588 | 110.5315 | 110.7884 | 110.6222 | -11.6478 | -0.066274 | -0.044145 | 1.6565 | 0.73166 | 0.79794 | -0.10583 | -0.15515 | -0.21288 | -0.30677 | -0.042841 | -0.22386 | -0.01098 | -0.049902 | -0.21611 | 122.2291 | 122.1674 | 122.1181 | 20.708 | -122.3395 | 121.9665 | 122.2234 | 122.0571 | 11.765 | -122.4861
1365.1719 | 122.2046 | -11.1832 | 110.8978 | 1.4211e-13 | -0.012773 | -0.010299 | 0.01637 | -0.038293 | 0.030381 | -0.00083919 | -0.014726 | 0.010021 | 0.034923 | 0.00011548 | 0.036488 | -9.4396 | 9.5203 | -10.3599 | 111.1238 | 111.0576 | 110.9991 | -11.1761 | -11.1618 | 0.3346 | -11.3383 | 110.8475 | 111.1089 | 110.9519 | -11.3365 | 0.00706 | 0.22599 | 1.7436 | 0.82326 | 0.81621 | 0.15977 | 0.10126 | -0.1533 | -0.050363 | 0.02132 | -0.15512 | -0.001829 | 0.21109 | 0.054041 | 122.307 | 122.2408 | 122.1823 | 20.7035 | -122.0739 | 122.0306 | 122.2921 | 122.135 | 11.5178 | -122.2343
1366.9531 | 121.669 | -10.7986 | 111.5662 | 1.4211e-13 | -0.01256 | -0.010513 | 0.01637 | -0.038506 | 0.030381 | -0.0084697 | -0.014299 | 0.010234 | 0.035136 | 0.00054268 | 0.036701 | -9.0825 | 9.8179 | -10.0165 | 111.4489 | 111.3919 | 111.3287 | -10.8647 | -10.8368 | 0.33918 | -11.0086 | 111.1817 | 111.4386 | 111.2724 | -11.0068 | -0.066095 | -0.11728 | 1.7162 | 0.78211 | 0.84821 | -0.17431 | -0.23741 | -0.20814 | -0.38447 | -0.038114 | -0.20998 | -0.001837 | -0.12759 | -0.29379 | 122.2475 | 122.1905 | 122.1274 | 20.6166 | -122.4309 | 121.9803 | 122.2372 | 122.071 | 11.1378 | -122.573
1368.7344 | 121.5317 | -10.6247 | 111.5112 | 1.4211e-13 | -0.012773 | -0.010299 | 0.01637 | -0.038079 | 0.030594 | -0.00083919 | -0.014513 | 0.010662 | 0.034923 | 0.00032908 | 0.036701 | -8.8032 | 10.2437 | -9.6961 | 111.7327 | 111.6712 | 111.6172 | -10.5763 | -10.5483 | 0.34376 | -10.7293 | 111.461 | 111.7133 | 111.5608 | -10.7321 | 0.048427 | 0.22151 | 1.8215 | 0.92864 | 0.88022 | 0.15994 | 0.10597 | -0.10736 | -0.050248 | 0.076395 | -0.10463 | 0.002735 | 0.20206 | 0.049592 | 122.3574 | 122.2959 | 122.2419 | 20.8684 | -122.0875 | 122.0857 | 122.338 | 122.1855 | 10.9685 | -122.2433
1370.5156 | 122.3694 | -10.5698 | 111.7401 | 1.4211e-13 | -0.01256 | -0.010299 | 0.016798 | -0.038079 | 0.030381 | -0.00083919 | -0.014513 | 0.010662 | 0.035136 | 0.00032908 | 0.036701 | -8.7803 | 10.1567 | -9.6457 | 111.7831 | 111.7124 | 111.663 | -10.5488 | -10.5162 | 0.34376 | -10.6927 | 111.5068 | 111.7682 | 111.602 | -10.6954 | 0.020969 | 0.042993 | 1.7895 | 0.92407 | 0.9031 | -0.027731 | -0.077124 | -0.12566 | -0.23334 | 0.053514 | -0.12293 | 0.002734 | 0.028125 | -0.13808 | 122.3529 | 122.2821 | 122.2328 | 20.7265 | -122.2889 | 122.0765 | 122.338 | 122.1718 | 10.9135 | -122.4355
1372.2969 | 117.1097 | -9.8282 | 112.4359 | 1.4211e-13 | -0.012987 | -0.010299 | 0.016157 | -0.038293 | 0.030381 | -0.00083919 | -0.014513 | 0.010448 | 0.035136 | 0.00054268 | 0.036488 | -8.121 | 10.5093 | -8.991 | 112.4241 | 112.358 | 112.304 | -9.9169 | -9.8661 | 0.34376 | -10.0471 | 112.1432 | 112.4138 | 112.243 | -10.059 | -0.088717 | -0.011834 | 1.7072 | 0.83719 | 0.92591 | -0.077904 | -0.13192 | -0.23079 | -0.29273 | -0.037886 | -0.21891 | 0.011877 | -0.022093 | -0.19288 | 122.2523 | 122.1862 | 122.1322 | 20.3375 | -122.3528 | 121.9714 | 122.242 | 122.0712 | 10.1719 | -122.4949
1374.0781 | 121.8201 | -9.5581 | 112.262 | 1.4211e-13 | -0.01256 | -0.010727 | 0.016798 | -0.038293 | 0.030381 | 0.014421 | -0.014513 | 0.010448 | 0.034923 | 0.00011548 | 0.036488 | -7.8326 | 10.5551 | -8.7346 | 112.6896 | 112.6236 | 112.5604 | -9.6513 | -9.6097 | 0.34834 | -9.7724 | 112.4225 | 112.6748 | 112.5178 | -9.7934 | -0.09322 | 0.42766 | 1.7255 | 0.82349 | 0.91671 | 0.36162 | 0.29843 | -0.2353 | 0.1605 | -0.051559 | -0.21427 | 0.021028 | 0.41284 | 0.25579 | 122.2477 | 122.1817 | 122.1185 | 20.1132 | -121.9133 | 121.9806 | 122.2329 | 122.0759 | 9.9064 | -122.0554
1375.7969 | 122.1268 | -1.5152 | 120.7626 | 1.4211e-13 | -0.012773 | -0.010299 | 0.016584 | -0.038293 | 0.030381 | -0.0084697 | -0.01494 | 0.010234 | 0.03535 | 0.00054268 | 0.036701 | -0.42932 | 16.1089 | -1.2812 | 120.1158 | 120.0689 | 119.9548 | -2.2152 | -2.1143 | 0.49028 | -2.2358 | 119.8488 | 120.0921 | 119.9855 | -2.3482 | -0.69995 | -0.64686 | 1.0859 | 0.23403 | 0.93398 | -0.69372 | -0.8078 | -0.83305 | -0.91385 | -0.59912 | -0.72062 | 0.11243 | -0.6705 | -0.77718 | 121.631 | 121.5841 | 121.47 | 17.6241 | -122.9778 | 121.364 | 121.6073 | 121.5006 | 2.0055 | -123.1109
1377.5781 | 95.9793 | -1.3367 | 120.3094 | 1.4211e-13 | -0.012987 | -0.010299 | 0.01637 | -0.038293 | 0.030381 | 0.0067908 | -0.014299 | 0.010662 | 0.035136 | 0.00032908 | 0.036701 | 0.43599 | 16.7454 | -0.37009 | 121.0223 | 120.9481 | 120.8751 | -1.3864 | -1.2352 | 0.43076 | -1.375 | 120.737 | 121.0079 | 120.8279 | -1.5241 | -0.049696 | 0.71284 | 1.7727 | 0.96658 | 1.0163 | 0.63862 | 0.56569 | -0.18739 | 0.42757 | 0.10147 | -0.03835 | 0.14904 | 0.69841 | 0.51847 | 122.359 | 122.2847 | 122.2118 | 18.082 | -121.6958 | 122.0737 | 122.3445 | 122.1646 | 1.7674 | -121.8335
1379.2969 | 107.0709 | -1.3779 | 120.1355 | 1.4211e-13 | -0.012773 | -0.010086 | 0.016584 | -0.038293 | 0.029953 | -0.00083919 | -0.014299 | 0.010448 | 0.03535 | 0.00011548 | 0.036274 | 0.3078 | 16.782 | -0.48455 | 120.8849 | 120.8061 | 120.7378 | -1.5146 | -1.3634 | 0.40786 | -1.517 | 120.5951 | 120.8705 | 120.686 | -1.6523 | -0.13671 | 0.74944 | 1.6857 | 0.89332 | 1.03 | 0.67063 | 0.60228 | -0.27439 | 0.45958 | 0.014461 | -0.13909 | 0.1353 | 0.735 | 0.55048 | 122.2628 | 122.184 | 122.1156 | 18.1599 | -121.6501 | 121.9729 | 122.2484 | 122.0638 | 1.7857 | -121.7878
1381.0781 | 121.8658 | -1.8082 | 120.282 | 1.4211e-13 | -0.01256 | -0.010299 | 0.016798 | -0.038506 | 0.030381 | -0.0084697 | -0.014299 | 0.010448 | 0.035136 | 0.00011548 | 0.036488 | 0.033096 | 16.7866 | -0.74093 | 120.5873 | 120.5177 | 120.4539 | -1.8214 | -1.6839 | 0.41244 | -1.8192 | 120.2975 | 120.5729 | 120.3929 | -1.9636 | -0.013197 | 0.30536 | 1.8413 | 1.0672 | 1.0804 | 0.23567 | 0.17192 | -0.15546 | 0.015496 | 0.12425 | -0.010987 | 0.14447 | 0.29091 | 0.11097 | 122.3955 | 122.3258 | 122.2621 | 18.5947 | -122.1033 | 122.1056 | 122.3811 | 122.2011 | 2.2206 | -122.2456
1382.7969 | 122.2229 | -2.7603 | 119.22 | 1.4211e-13 | -0.012987 | -0.010299 | 0.017011 | -0.038293 | 0.030381 | -0.0084697 | -0.01494 | 0.010021 | 0.035136 | 0.00054268 | 0.036488 | -0.82764 | 16.3791 | -1.6108 | 119.6991 | 119.6339 | 119.5611 | -2.7005 | -2.6042 | 0.39871 | -2.7212 | 119.4047 | 119.6846 | 119.5093 | -2.8428 | 0.059797 | 0.47917 | 1.9327 | 1.1495 | 1.0897 | 0.41395 | 0.34111 | -0.082442 | 0.1847 | 0.15608 | 0.039155 | 0.1216 | 0.46467 | 0.2893 | 122.4595 | 122.3942 | 122.3214 | 19.1394 | -121.9205 | 122.165 | 122.445 | 122.2696 | 3.159 | -122.0627
1384.5938 | 103.9673 | -2.7145 | 118.7164 | 1.4211e-13 | -0.01256 | -0.010299 | 0.016584 | -0.038293 | 0.030381 | -0.0084697 | -0.014299 | 0.010448 | 0.035136 | 0.00054268 | 0.036488 | -1.0382 | 16.1959 | -1.8123 | 119.4656 | 119.4004 | 119.3276 | -2.9295 | -2.7965 | 0.39871 | -2.9501 | 119.1849 | 119.4511 | 119.2712 | -3.0671 | -0.21493 | 0.74921 | 1.6763 | 0.90229 | 1.1172 | 0.68396 | 0.61114 | -0.35258 | 0.46847 | -0.082005 | -0.23556 | 0.11702 | 0.7347 | 0.55476 | 122.1802 | 122.1149 | 122.0421 | 18.9105 | -121.6459 | 121.8994 | 122.1657 | 121.9857 | 3.1132 | -121.7836
1386.3125 | 122.3877 | -4.0421 | 118.3411 | 1.4211e-13 | -0.012773 | -0.010513 | 0.016584 | -0.038293 | 0.030381 | -0.00083919 | -0.014513 | 0.010875 | 0.03535 | 0.00054268 | 0.036488 | -2.0821 | 15.5137 | -2.8927 | 118.3714 | 118.306 | 118.2424 | -4.0192 | -3.9 | 0.38497 | -4.0581 | 118.0952 | 118.3568 | 118.1815 | -4.1615 | 0.022805 | 0.030341 | 1.9599 | 1.1493 | 1.1265 | -0.035032 | -0.098625 | -0.1194 | -0.24584 | 0.14204 | -0.016091 | 0.10331 | 0.015782 | -0.15958 | 122.4135 | 122.3481 | 122.2845 | 19.5558 | -122.3603 | 122.1373 | 122.3989 | 122.2235 | 4.427 | -122.5025
1388.0781 | 122.4106 | -3.7949 | 118.2449 | 1.4211e-13 | -0.012773 | -0.010513 | 0.016584 | -0.037865 | 0.030381 | 0.0067908 | -0.014726 | 0.010448 | 0.035136 | 0.00054268 | 0.036274 | -2.0089 | 15.5412 | -2.8332 | 118.4172 | 118.3427 | 118.2836 | -3.978 | -3.8496 | 0.38955 | -4.0124 | 118.1364 | 118.4026 | 118.2273 | -4.1157 | -0.18318 | 0.17225 | 1.786 | 0.96165 | 1.1448 | 0.09773 | 0.038713 | -0.32081 | -0.10851 | -0.054786 | -0.21749 | 0.10331 | 0.1577 | -0.017666 | 122.212 | 122.1375 | 122.0785 | 19.336 | -122.223 | 121.9313 | 122.1975 | 122.0221 | 4.1844 | -122.3606
1389.875 | 122.168 | -3.4378 | 118.396 | 1.4211e-13 | -0.012773 | -0.010086 | 0.016798 | -0.038293 | 0.030594 | -0.0084697 | -0.014513 | 0.010662 | 0.03535 | 0.00032908 | 0.036488 | -1.084 | 16.0952 | -1.9267 | 119.3191 | 119.2539 | 119.1856 | -3.0943 | -2.9568 | 0.39413 | -3.1058 | 119.0338 | 119.3 | 119.1338 | -3.232 | 0.3435 | 0.92314 | 2.3538 | 1.5111 | 1.1676 | 0.85787 | 0.78964 | 0.20585 | 0.63782 | 0.48101 | 0.33203 | 0.12618 | 0.90404 | 0.73784 | 122.7569 | 122.6917 | 122.6234 | 19.533 | -121.4903 | 122.4716 | 122.7378 | 122.5716 | 3.8319 | -121.628
1391.5938 | 122.3007 | -3.3463 | 118.6157 | 1.4211e-13 | -0.01256 | -0.010299 | 0.016798 | -0.038079 | 0.030594 | -0.0084697 | -0.014726 | 0.010662 | 0.03535 | 0.00054268 | 0.036915 | -1.2901 | 15.7426 | -2.1556 | 119.0902 | 119.0341 | 118.9521 | -3.3278 | -3.1949 | 0.40329 | -3.3484 | 118.8095 | 119.0757 | 118.9003 | -3.4563 | 0.018422 | 0.47449 | 2.0562 | 1.1906 | 1.1722 | 0.41836 | 0.3364 | -0.11007 | 0.19374 | 0.15136 | -0.002191 | 0.10787 | 0.45996 | 0.2846 | 122.4365 | 122.3803 | 122.2984 | 19.0889 | -121.9436 | 122.1557 | 122.4219 | 122.2466 | 3.7495 | -122.072
1393.3281 | 122.0947 | -5.8044 | 116.0934 | 1.4211e-13 | -0.012773 | -0.010086 | 0.017011 | -0.038293 | 0.030594 | -0.00083919 | -0.014726 | 0.010662 | 0.035564 | 0.00032908 | 0.036488 | -3.7303 | 13.8059 | -4.6325 | 116.6041 | 116.5294 | 116.4751 | -5.7913 | -5.6903 | 0.37581 | -5.8576 | 116.3233 | 116.5895 | 116.4141 | -5.938 | 0.013151 | 0.5107 | 2.0741 | 1.172 | 1.1588 | 0.43596 | 0.38165 | -0.13359 | 0.2299 | 0.11415 | -0.053133 | 0.080461 | 0.49606 | 0.3207 | 122.4086 | 122.3339 | 122.2795 | 19.6103 | -121.8847 | 122.1278 | 122.3939 | 122.2186 | 6.1803 | -122.0315
1395.0938 | 122.4792 | -5.484 | 116.478 | 1.4211e-13 | -0.012773 | -0.010086 | 0.01637 | -0.038506 | 0.030594 | -0.0084697 | -0.014299 | 0.010448 | 0.035564 | 0.00054268 | 0.036701 | -3.3641 | 13.8654 | -4.2845 | 116.9384 | 116.8774 | 116.8139 | -5.457 | -5.356 | 0.38497 | -5.5233 | 116.6576 | 116.9283 | 116.753 | -5.6038 | 0.026979 | 0.4604 | 2.1199 | 1.1995 | 1.1725 | 0.39944 | 0.33595 | -0.11977 | 0.17961 | 0.12797 | -0.039322 | 0.080453 | 0.45036 | 0.27499 | 122.4224 | 122.3614 | 122.2979 | 19.3494 | -121.935 | 122.1416 | 122.4123 | 122.237 | 5.869 | -122.0817
1396.875 | 121.962 | -5.1132 | 116.89 | 1.4211e-13 | -0.012987 | -0.010299 | 0.016584 | -0.038079 | 0.030381 | -0.00083919 | -0.014299 | 0.010234 | 0.035564 | 0.00054268 | 0.036488 | -3.0344 | 13.9753 | -3.9595 | 117.2451 | 117.1842 | 117.1115 | -5.1502 | -5.0584 | 0.38497 | -5.2074 | 116.9735 | 117.2397 | 117.0551 | -5.297 | -0.037022 | 0.35517 | 2.0788 | 1.1538 | 1.1908 | 0.29424 | 0.22157 | -0.18378 | 0.083536 | 0.054793 | -0.09418 | 0.089603 | 0.34971 | 0.16519 | 122.3583 | 122.2974 | 122.2247 | 19.0885 | -122.0402 | 122.0867 | 122.3529 | 122.1684 | 5.4982 | -122.187
1398.5938 | 121.9208 | -4.8843 | 117.5537 | 1.4211e-13 | -0.012773 | -0.010086 | 0.017011 | -0.038293 | 0.030594 | -0.00083919 | -0.014299 | 0.010448 | 0.03535 | 0.00054268 | 0.036701 | -2.7139 | 13.957 | -3.6573 | 117.5519 | 117.4772 | 117.4137 | -4.8663 | -4.7608 | 0.39413 | -4.9144 | 117.2665 | 117.5281 | 117.3528 | -5.0085 | 0.017989 | -0.001837 | 2.1704 | 1.227 | 1.209 | -0.076464 | -0.14 | -0.1242 | -0.2872 | 0.12353 | -0.030024 | 0.094175 | -0.025592 | -0.20096 | 122.4362 | 122.3616 | 122.2981 | 18.8413 | -122.4201 | 122.1509 | 122.4125 | 122.2371 | 5.2785 | -122.5622
1400.2969 | 122.4838 | -4.8477 | 117.5766 | 1.4211e-13 | -0.012987 | -0.010086 | 0.017011 | -0.038079 | 0.030594 | 0.0067908 | -0.014513 | 0.010448 | 0.035136 | 0.00054268 | 0.036488 | -2.6407 | 13.9661 | -3.6115 | 117.5793 | 117.5139 | 117.4503 | -4.8297 | -4.7242 | 0.38955 | -4.8777 | 117.294 | 117.5647 | 117.3894 | -4.9673 | 0.017999 | 0.002745 | 2.207 | 1.2362 | 1.2182 | -0.062721 | -0.12626 | -0.11961 | -0.28261 | 0.12354 | -0.030016 | 0.089595 | -0.011851 | -0.18722 | 122.4271 | 122.3616 | 122.2981 | 18.8139 | -122.4063 | 122.1417 | 122.4125 | 122.2371 | 5.2373 | -122.5439
1402.0781 | 122.5021 | -4.5776 | 117.8101 | 1.4211e-13 | -0.012987 | -0.010299 | 0.017011 | -0.037865 | 0.030594 | -0.00083919 | -0.014513 | 0.010662 | 0.03535 | 0.00075648 | 0.036701 | -2.3339 | 14.1539 | -3.3277 | 117.8495 | 117.7886 | 117.7159 | -4.5733 | -4.4632 | 0.39871 | -4.6213 | 117.5595 | 117.8349 | 117.6595 | -4.7109 | 0.004339 | 0.03941 | 2.2437 | 1.25 | 1.2456 | -0.021445 | -0.094159 | -0.13328 | -0.25052 | 0.11444 | -0.043688 | 0.089589 | 0.024826 | -0.15054 | 122.4271 | 122.3663 | 122.2935 | 18.7315 | -122.3834 | 122.1372 | 122.4125 | 122.2372 | 4.9763 | -122.521
1403.8594 | 122.0032 | -4.7928 | 117.2287 | 1.4211e-13 | -0.013201 | -0.0096583 | 0.016798 | -0.038293 | 0.030808 | -0.00083919 | -0.014513 | 0.010662 | 0.035564 | 0.00054268 | 0.036488 | -2.6132 | 13.783 | -3.6344 | 117.5244 | 117.4544 | 117.3954 | -4.8984 | -4.7883 | 0.38039 | -4.9556 | 117.2528 | 117.5052 | 117.3253 | -5.0406 | -0.10562 | 0.2957 | 2.1796 | 1.1584 | 1.264 | 0.22565 | 0.1667 | -0.2478 | 0.024079 | 0.004503 | -0.16278 | 0.085018 | 0.27653 | 0.096584 | 122.3172 | 122.2471 | 122.1882 | 18.5758 | -122.1271 | 122.0456 | 122.298 | 122.1181 | 5.1732 | -122.2693
1405.6406 | 121.7926 | -5.6625 | 116.4917 | 1.4211e-13 | -0.012987 | -0.010086 | 0.017011 | -0.037865 | 0.031022 | -0.00083919 | -0.01494 | 0.010234 | 0.03535 | 0.00054268 | 0.036701 | -3.3183 | 12.968 | -4.3624 | 116.7735 | 116.7034 | 116.6445 | -5.6539 | -5.5529 | 0.38497 | -5.7111 | 116.4882 | 116.7498 | 116.5744 | -5.7915 | 0.008613 | 0.28185 | 2.3443 | 1.3002 | 1.2916 | 0.21171 | 0.15281 | -0.12898 | -0.003529 | 0.10961 | -0.048521 | 0.080457 | 0.25806 | 0.082693 | 122.4361 | 122.3659 | 122.307 | 18.6305 | -122.1456 | 122.1507 | 122.4123 | 122.2369 | 6.0475 | -122.2832
1407.4219 | 122.3694 | -5.4703 | 116.9449 | 1.4211e-13 | -0.012773 | -0.0098719 | 0.017011 | -0.038079 | 0.030381 | 0.0067908 | -0.014726 | 0.010662 | 0.03535 | 0.00054268 | 0.036701 | -3.1123 | 12.9451 | -4.1609 | 116.9567 | 116.8957 | 116.8185 | -5.4662 | -5.3606 | 0.38039 | -5.5188 | 116.6713 | 116.9329 | 116.7667 | -5.6038 | 0.004088 | 0.011798 | 2.358 | 1.3094 | 1.3053 | -0.049161 | -0.12639 | -0.13351 | -0.27358 | 0.10965 | -0.048476 | 0.085032 | -0.011985 | -0.17819 | 122.427 | 122.366 | 122.2888 | 18.4154 | -122.4111 | 122.1416 | 122.4032 | 122.237 | 5.8507 | -122.5487
1409.1406 | 121.6919 | -5.2368 | 116.5604 | 1.4211e-13 | -0.013201 | -0.0096583 | 0.017225 | -0.038079 | 0.030808 | -0.0084697 | -0.014085 | 0.010448 | 0.035136 | 0.00075648 | 0.036915 | -2.8376 | 12.9634 | -3.9045 | 117.1856 | 117.1247 | 117.052 | -5.2418 | -5.1363 | 0.39413 | -5.2944 | 116.9048 | 117.171 | 116.9956 | -5.3794 | -0.005005 | 0.62524 | 2.3993 | 1.3323 | 1.3373 | 0.56431 | 0.49164 | -0.14261 | 0.34445 | 0.10055 | -0.057579 | 0.085027 | 0.61062 | 0.43526 | 122.4224 | 122.3615 | 122.2888 | 18.2002 | -121.8022 | 122.1416 | 122.4078 | 122.2324 | 5.6309 | -121.9398
1410.9375 | 122.5479 | -4.985 | 117.3111 | 1.4211e-13 | -0.013414 | -0.0098719 | 0.017011 | -0.038079 | 0.030808 | 0.014421 | -0.01494 | 0.010448 | 0.03535 | 0.00054268 | 0.036488 | -2.5766 | 12.9222 | -3.6481 | 117.4328 | 117.3582 | 117.2992 | -5.0037 | -4.889 | 0.39871 | -5.0471 | 117.1429 | 117.4137 | 117.2291 | -5.1459 | -0.018671 | 0.12174 | 2.4085 | 1.3369 | 1.3556 | 0.047099 | -0.011849 | -0.16086 | -0.1682 | 0.096031 | -0.062099 | 0.098757 | 0.10256 | -0.081964 | 122.4179 | 122.3432 | 122.2843 | 17.9073 | -122.3148 | 122.1279 | 122.3987 | 122.2142 | 5.3838 | -122.457
1412.7188 | 121.6507 | -5.1819 | 116.6977 | 1.4211e-13 | -0.012987 | -0.0098719 | 0.016798 | -0.038079 | 0.030808 | -0.00083919 | -0.014513 | 0.010021 | 0.035136 | 0.00032908 | 0.036701 | -2.6727 | 12.6658 | -3.7626 | 117.3001 | 117.2346 | 117.1756 | -5.1273 | -5.0218 | 0.39413 | -5.1937 | 117.0239 | 117.2855 | 117.1101 | -5.2741 | 0.054537 | 0.60237 | 2.5092 | 1.4193 | 1.3647 | 0.53687 | 0.47793 | -0.092224 | 0.32616 | 0.16009 | -0.011779 | 0.080445 | 0.58776 | 0.4124 | 122.4819 | 122.4164 | 122.3575 | 17.8477 | -121.825 | 122.2057 | 122.4673 | 122.292 | 5.576 | -121.9718
1414.4531 | 122.4701 | -5.0903 | 117.2333 | 1.4211e-13 | -0.013414 | -0.010299 | 0.017225 | -0.038506 | 0.031022 | 0.0067908 | -0.014513 | 0.010875 | 0.035136 | 0.00097008 | 0.036915 | -2.5629 | 12.5056 | -3.671 | 117.3642 | 117.3032 | 117.2397 | -5.0816 | -4.9714 | 0.39871 | -5.125 | 117.0925 | 117.3496 | 117.1788 | -5.21 | 0.008773 | 0.13088 | 2.5275 | 1.4193 | 1.4105 | 0.069972 | 0.006449 | -0.11967 | -0.14075 | 0.1189 | -0.034651 | 0.085022 | 0.11628 | -0.054508 | 122.4545 | 122.3936 | 122.3301 | 17.5959 | -122.3148 | 122.1829 | 122.4399 | 122.2691 | 5.489 | -122.4433
1416.2344 | 122.4838 | -4.7745 | 117.6224 | 1.4211e-13 | -0.012987 | -0.0096583 | 0.017225 | -0.038079 | 0.030808 | -0.00083919 | -0.014726 | 0.010662 | 0.035136 | 0.00054268 | 0.036488 | -2.2515 | 12.5788 | -3.4101 | 117.6068 | 117.5551 | 117.487 | -4.8206 | -4.7059 | 0.40329 | -4.8777 | 117.3306 | 117.6014 | 117.426 | -4.9627 | -0.046085 | -0.015561 | 2.523 | 1.3644 | 1.4105 | -0.067286 | -0.13541 | -0.18827 | -0.29176 | 0.068609 | -0.10326 | 0.085016 | -0.020999 | -0.19636 | 122.3813 | 122.3296 | 122.2614 | 17.3533 | -122.4429 | 122.1051 | 122.3759 | 122.2005 | 5.1778 | -122.5851
1418.0312 | 121.6919 | -4.5685 | 117.5949 | 1.4211e-13 | -0.013201 | -0.010086 | 0.017225 | -0.037865 | 0.031022 | 0.0067908 | -0.014513 | 0.010448 | 0.035564 | 0.00075648 | 0.036488 | -1.9219 | 12.6292 | -3.0804 | 117.9136 | 117.8527 | 117.7846 | -4.5321 | -4.4082 | 0.40329 | -4.5801 | 117.6328 | 117.899 | 117.7236 | -4.6651 | 0.036393 | 0.31866 | 2.6466 | 1.488 | 1.4517 | 0.25781 | 0.18967 | -0.096645 | 0.037883 | 0.16023 | -0.011635 | 0.08501 | 0.30408 | 0.12871 | 122.482 | 122.4212 | 122.3531 | 17.1977 | -122.127 | 122.2013 | 122.4675 | 122.2921 | 4.9718 | -122.26
1419.8125 | 121.9666 | -4.1107 | 118.3868 | 1.4211e-13 | -0.013414 | -0.0098719 | 0.017225 | -0.037865 | 0.031022 | -0.00083919 | -0.014726 | 0.011089 | 0.035564 | 0.00097008 | 0.036701 | -1.4457 | 12.8169 | -2.5906 | 118.3577 | 118.3015 | 118.2379 | -4.0834 | -3.9595 | 0.40329 | -4.1222 | 118.0861 | 118.3477 | 118.1723 | -4.221 | 0.027365 | -0.029171 | 2.665 | 1.5202 | 1.4928 | -0.085388 | -0.14898 | -0.11026 | -0.30078 | 0.15118 | -0.011527 | 0.098736 | -0.039152 | -0.21452 | 122.4684 | 122.4122 | 122.3486 | 16.9276 | -122.4702 | 122.1968 | 122.4584 | 122.283 | 4.514 | -122.6078
1421.5312 | 122.5479 | -3.8727 | 118.5242 | 1.4211e-13 | -0.013414 | -0.0096583 | 0.017011 | -0.038079 | 0.031022 | -0.00083919 | -0.014726 | 0.010448 | 0.035136 | 0.00097008 | 0.036701 | -1.226 | 12.8032 | -2.3708 | 118.5545 | 118.4938 | 118.421 | -3.9002 | -3.7718 | 0.41702 | -3.9345 | 118.2646 | 118.54 | 118.3646 | -4.0332 | -0.027515 | 0.030371 | 2.6467 | 1.5019 | 1.5294 | -0.030402 | -0.10317 | -0.16057 | -0.25954 | 0.10087 | -0.061837 | 0.098731 | 0.01582 | -0.15954 | 122.4272 | 122.3664 | 122.2937 | 16.6759 | -122.4244 | 122.1373 | 122.4127 | 122.2373 | 4.2897 | -122.5574
1423.3125 | 121.9437 | -3.9047 | 118.6295 | 1.4211e-13 | -0.013201 | -0.0098719 | 0.017225 | -0.037865 | 0.031022 | -0.0084697 | -0.014513 | 0.010234 | 0.034923 | 0.00075648 | 0.036488 | -1.1252 | 12.7345 | -2.2838 | 118.6095 | 118.5441 | 118.4805 | -3.8498 | -3.7214 | 0.41702 | -3.875 | 118.3196 | 118.5904 | 118.4058 | -3.9783 | 0.054896 | -0.019975 | 2.7795 | 1.6209 | 1.566 | -0.08532 | -0.14893 | -0.073579 | -0.30989 | 0.18328 | 0.029729 | 0.10331 | -0.039101 | -0.22362 | 122.5142 | 122.4489 | 122.3853 | 16.6392 | -122.4793 | 122.2243 | 122.4951 | 122.3106 | 4.3217 | -122.6078
1425.0312 | 122.4335 | -3.8956 | 118.4372 | 1.4211e-13 | -0.012987 | -0.010086 | 0.016798 | -0.037865 | 0.030808 | -0.0084697 | -0.014513 | 0.010448 | 0.03535 | 0.00075648 | 0.036488 | -1.0886 | 12.6567 | -2.238 | 118.6003 | 118.5396 | 118.4759 | -3.8498 | -3.726 | 0.41702 | -3.8887 | 118.3241 | 118.5904 | 118.4104 | -3.9875 | 0.045741 | 0.16313 | 2.807 | 1.6575 | 1.6118 | 0.10236 | 0.038753 | -0.091892 | -0.11305 | 0.16955 | 0.006838 | 0.09873 | 0.15316 | -0.026783 | 122.4959 | 122.4351 | 122.3715 | 16.5522 | -122.287 | 122.2197 | 122.4859 | 122.306 | 4.3126 | -122.4247
1426.7969 | 121.6965 | -56.3004 | 65.1352 | 1.4211e-13 | -0.013201 | -0.010299 | 0.015729 | -0.037224 | 0.031449 | -0.0161 | -0.015153 | 0.010021 | 0.034282 | 0.00075648 | 0.036488 | -48.745 | -25.6479 | -49.9895 | 69.2957 | 69.2383 | 69.3384 | -51.9926 | -51.9444 | -0.4392 | -52.0247 | 69.0183 | 69.2559 | 69.1263 | -52.0971 | 4.3077 | 4.1605 | 7.5553 | 6.3109 | 2.0031 | 4.1031 | 4.2032 | 4.2033 | 3.8831 | 4.3559 | 4.2756 | 0.072385 | 4.1207 | 3.9911 | 125.596 | 125.5386 | 125.6387 | 30.6524 | -117.1278 | 125.3187 | 125.5563 | 125.4267 | 55.8612 | -117.2323
1428.5938 | 121.7468 | -61.4685 | 60.0998 | 1.4211e-13 | -0.013628 | -0.010513 | 0.016157 | -0.037652 | 0.03209 | -0.0084697 | -0.01494 | 0.0095932 | 0.034282 | 0.00032908 | 0.036701 | -59.1014 | -32.8409 | -60.4783 | 58.9348 | 58.9998 | 58.9907 | -62.6478 | -62.5167 | -0.21484 | -62.5924 | 58.7762 | 58.9449 | 58.9802 | -62.7474 | -1.1793 | -1.165 | 2.3671 | 0.99017 | 2.1695 | -1.1 | -1.109 | -1.2789 | -1.3236 | -1.0482 | -1.1239 | 0.15505 | -1.1549 | -1.1196 | 120.4033 | 120.4683 | 120.4592 | 28.6276 | -122.7476 | 120.2447 | 120.4134 | 120.4487 | 61.2537 | -122.8472
1430.3281 | 121.5134 | -53.8513 | 67.1585 | 1.4211e-13 | -0.013414 | -0.010299 | 0.015943 | -0.037438 | 0.031876 | 0.0067908 | -0.015153 | 0.009807 | 0.034496 | 0.00097008 | 0.036701 | -46.7763 | -23.3678 | -48.0437 | 71.4292 | 71.3492 | 71.4674 | -50.1885 | -50.1679 | -0.26978 | -50.2573 | 71.1199 | 71.3621 | 71.2325 | -50.3068 | 3.6628 | 4.2707 | 7.075 | 5.8076 | 2.1448 | 4.1907 | 4.3089 | 3.5445 | 3.9614 | 3.6834 | 3.594 | 0.04945 | 4.2036 | 4.074 | 125.2805 | 125.2005 | 125.3188 | 30.4835 | -117.3471 | 124.9712 | 125.2134 | 125.0838 | 53.5815 | -117.4653
1432.1094 | 119.4031 | -80.4977 | 38.9145 | 1.4211e-13 | -0.014055 | -0.010727 | 0.014875 | -0.036797 | 0.031449 | -0.00083919 | -0.015367 | 0.009807 | 0.033 | 0.00075648 | 0.035419 | -74.5672 | -45.5236 | -76.0216 | 40.7952 | 40.8215 | 40.8824 | -78.5138 | -78.2857 | -0.47125 | -78.3706 | 40.6179 | 40.7953 | 40.7939 | -78.6268 | 1.984 | 1.8807 | 5.9306 | 4.4761 | 2.4922 | 1.907 | 1.9679 | 1.871 | 1.7034 | 2.212 | 2.1271 | 0.25616 | 1.8808 | 1.8795 | 121.2929 | 121.3192 | 121.3801 | 34.9741 | -117.4283 | 121.1157 | 121.2931 | 121.2917 | 80.0265 | -117.5413
1433.8281 | 121.0281 | -66.7511 | 54.0894 | 1.4211e-13 | -0.013842 | -0.010513 | 0.015943 | -0.037011 | 0.03209 | 0.0067908 | -0.015153 | 0.009807 | 0.033641 | 0.00097008 | 0.036274 | -71.3165 | -42.9138 | -72.9908 | 45.3461 | 45.5881 | 45.3419 | -75.3635 | -75.0211 | 0.21556 | -75.1014 | 45.4116 | 45.4563 | 45.7159 | -75.4124 | -8.6124 | -8.7432 | -4.5654 | -6.2397 | 2.3727 | -8.5012 | -8.7474 | -8.6613 | -8.6777 | -8.27 | -8.3503 | 0.31103 | -8.633 | -8.3734 | 112.0972 | 112.3392 | 112.093 | 23.8373 | -129.4528 | 112.1627 | 112.2074 | 112.467 | 66.9667 | -129.5018
1435.625 | 121.3028 | -63.6246 | 57.3578 | 1.4211e-13 | -0.013414 | -0.010086 | 0.016157 | -0.037224 | 0.032304 | 0.0067908 | -0.015367 | 0.010021 | 0.034282 | 0.00097008 | 0.036488 | -57.9247 | -32.8501 | -59.3933 | 59.4063 | 59.4485 | 59.4166 | -61.7595 | -61.633 | -0.17821 | -61.7133 | 59.2112 | 59.3753 | 59.4243 | -61.8866 | 1.8651 | 2.0486 | 5.6999 | 4.2313 | 2.3662 | 2.0907 | 2.0588 | 1.738 | 1.8534 | 1.9916 | 1.9113 | 0.17335 | 2.0175 | 2.0665 | 123.0309 | 123.0731 | 123.0411 | 30.7745 | -119.1173 | 122.8358 | 122.9999 | 123.0488 | 63.4464 | -119.2444
1437.3594 | 121.312 | -120.0439 | 0.82855 | 1.4211e-13 | -0.014483 | -0.011154 | 0.015088 | -0.03637 | 0.034013 | -0.0084697 | -0.015581 | 0.0093796 | 0.033641 | 0.0011837 | 0.03777 | -114.8844 | -76.2644 | -116.7271 | 1.0273 | 1.0444 | 1.2088 | -120.0584 | -119.6544 | -1.0665 | -119.7713 | 0.88575 | 1.0485 | 1.0288 | -120.1978 | -0.014409 | 0.19877 | 5.1595 | 3.3169 | 3.3313 | 0.2158 | 0.38023 | -0.1539 | 0.057193 | 0.38957 | 0.27265 | 0.42654 | 0.21992 | 0.20023 | 121.0713 | 121.0883 | 121.2527 | 43.7796 | -120.8869 | 120.9297 | 121.0924 | 121.0727 | 118.9775 | -121.0264
1439.1406 | 121.4539 | -120.3644 | 0.84686 | 1.4211e-13 | -0.014269 | -0.010727 | 0.015302 | -0.036583 | 0.034227 | -0.0084697 | -0.015367 | 0.0095932 | 0.034068 | 0.0011837 | 0.037983 | -115.1591 | -76.8642 | -117.0567 | 0.88997 | 0.92072 | 1.0943 | -120.475 | -120.0665 | -0.85586 | -120.188 | 0.77128 | 0.92027 | 0.92347 | -120.6191 | -0.11066 | 0.04311 | 5.2052 | 3.3076 | 3.4183 | 0.07386 | 0.24745 | -0.25471 | -0.075581 | 0.29792 | 0.17642 | 0.43113 | 0.073407 | 0.076608 | 121.2544 | 121.2851 | 121.4587 | 43.5002 | -121.3219 | 121.1357 | 121.2846 | 121.2879 | 119.5085 | -121.466
1440.875 | 121.5866 | -120.3598 | 0.92468 | 1.4211e-13 | -0.014269 | -0.01094 | 0.015302 | -0.036583 | 0.034013 | 0.0067908 | -0.015581 | 0.0095932 | 0.033855 | 0.0011837 | 0.037983 | -115.0676 | -76.9649 | -116.9697 | 0.90371 | 0.97567 | 1.1355 | -120.4888 | -120.0756 | -0.80549 | -120.1971 | 0.82165 | 0.97979 | 0.97841 | -120.6374 | -0.12897 | -0.020975 | 5.2922 | 3.3901 | 3.519 | 0.050987 | 0.21084 | -0.27761 | -0.10304 | 0.28418 | 0.16268 | 0.44029 | 0.055109 | 0.053731 | 121.2635 | 121.3355 | 121.4953 | 43.3949 | -121.4135 | 121.1814 | 121.3396 | 121.3382 | 119.5543 | -121.5621
1442.6562 | 121.463 | -120.1401 | 1.3275 | 1.4211e-13 | -0.014269 | -0.011368 | 0.015302 | -0.03637 | 0.034227 | -0.0084697 | -0.015581 | 0.0095932 | 0.033855 | 0.0011837 | 0.037983 | -114.6509 | -77.1023 | -116.5852 | 1.2608 | 1.3374 | 1.4972 | -120.1728 | -119.7597 | -0.77344 | -119.8812 | 1.1833 | 1.3415 | 1.3355 | -120.326 | -0.032751 | -0.066693 | 5.4891 | 3.5549 | 3.5877 | 0.00989 | 0.16972 | -0.18597 | -0.14417 | 0.38039 | 0.25889 | 0.44486 | 0.013986 | 0.00803 | 121.4009 | 121.4775 | 121.6373 | 43.0378 | -121.5003 | 121.3234 | 121.4816 | 121.4756 | 119.3666 | -121.6536
1444.3906 | 121.5454 | -119.9158 | 1.506 | 1.4211e-13 | -0.014055 | -0.011368 | 0.015943 | -0.03637 | 0.03444 | -0.0084697 | -0.015794 | 0.009807 | 0.034068 | 0.0011837 | 0.03777 | -114.3076 | -77.1114 | -116.2784 | 1.5126 | 1.5984 | 1.7399 | -119.8523 | -119.5445 | -0.76886 | -119.666 | 1.4352 | 1.6025 | 1.3722 | -120.1154 | 0.063469 | 0.006591 | 5.6082 | 3.6373 | 3.5739 | 0.092362 | 0.23386 | -0.19965 | -0.070878 | 0.37128 | 0.24978 | 0.44943 | 0.09644 | -0.13387 | 121.4284 | 121.5142 | 121.6557 | 42.8044 | -121.3583 | 121.3509 | 121.5183 | 121.2879 | 119.1469 | -121.6215
1446.1562 | 121.6415 | -119.7464 | 1.6479 | 1.4211e-13 | -0.014055 | -0.01094 | 0.015516 | -0.03637 | 0.03444 | -0.00083919 | -0.015581 | 0.009166 | 0.033427 | 0.00097008 | 0.038197 | -114.1473 | -77.2167 | -116.1548 | 1.5722 | 1.4885 | 1.7948 | -119.8248 | -119.517 | -0.76429 | -119.6339 | 1.5038 | 1.6574 | 1.4363 | -120.0742 | -0.07843 | -0.075797 | 5.5991 | 3.5916 | 3.67 | -0.15944 | 0.14689 | -0.32781 | -0.14411 | 0.22938 | 0.11246 | 0.44027 | 0.009476 | -0.21167 | 121.3186 | 121.2349 | 121.5412 | 42.5297 | -121.4728 | 121.2502 | 121.4038 | 121.1827 | 118.9821 | -121.7222
1447.9375 | 121.6187 | -118.2312 | 3.2043 | 1.4211e-13 | -0.014055 | -0.01094 | 0.015729 | -0.035942 | 0.034868 | -0.00083919 | -0.015367 | 0.009166 | 0.033641 | 0.00075648 | 0.037983 | -112.5037 | -76.2552 | -114.5204 | 3.1517 | 3.0591 | 3.3653 | -118.268 | -117.9603 | -0.72766 | -118.0818 | 3.0788 | 3.237 | 3.0022 | -118.5083 | -0.036793 | -0.05265 | 5.7275 | 3.7108 | 3.7476 | -0.14527 | 0.16096 | -0.27706 | -0.1255 | 0.27095 | 0.14945 | 0.4265 | 0.032697 | -0.20219 | 121.3829 | 121.2903 | 121.5965 | 41.976 | -121.4723 | 121.31 | 121.4682 | 121.2334 | 117.5035 | -121.7126
1449.6562 | 121.6507 | -117.9565 | 3.5385 | 1.4211e-13 | -0.014269 | -0.010299 | 0.015729 | -0.035729 | 0.035081 | -0.00083919 | -0.015581 | 0.0095932 | 0.033855 | 0.0011837 | 0.037983 | -112.0596 | -76.2506 | -114.1587 | 3.4722 | 3.3842 | 3.6904 | -117.9749 | -117.6581 | -0.72766 | -117.775 | 3.3902 | 3.5484 | 3.3272 | -118.2198 | -0.0184 | -0.06633 | 5.897 | 3.7979 | 3.8163 | -0.15433 | 0.15187 | -0.26325 | -0.14833 | 0.29848 | 0.18156 | 0.44481 | 0.009875 | -0.21128 | 121.4287 | 121.3407 | 121.6469 | 41.7059 | -121.5135 | 121.3467 | 121.5049 | 121.2838 | 117.2289 | -121.7583
1451.4375 | 121.5866 | -115.5991 | 5.9647 | 1.4211e-13 | -0.014055 | -0.010513 | 0.015516 | -0.03637 | 0.035081 | -0.0084697 | -0.01494 | 0.0095932 | 0.033641 | 0.0011837 | 0.037983 | -109.5552 | -74.3734 | -111.6223 | 5.9354 | 5.8522 | 6.1628 | -115.5069 | -115.2084 | -0.68645 | -115.3254 | 5.8534 | 6.0163 | 5.7905 | -115.761 | 0.092157 | -0.029305 | 6.0439 | 3.9767 | 3.8846 | -0.11244 | 0.19817 | -0.16191 | -0.11125 | 0.39061 | 0.27369 | 0.4356 | 0.051593 | -0.17414 | 121.5344 | 121.4513 | 121.7619 | 41.2256 | -121.4716 | 121.4525 | 121.6153 | 121.3896 | 114.9126 | -121.7256
1453.1562 | 121.6049 | -120.3552 | 1.2314 | 1.4211e-13 | -0.014483 | -0.010513 | 0.015943 | -0.035942 | 0.034868 | 0.0067908 | -0.015367 | 0.0095932 | 0.033427 | 0.00097008 | 0.038197 | -114.1153 | -78.1324 | -116.3059 | 1.1464 | 1.2229 | 1.3782 | -120.3514 | -120.0344 | -0.76886 | -120.1513 | 1.0689 | 1.2316 | 1.1845 | -120.6054 | 0.00382 | -0.085022 | 6.24 | 4.0493 | 4.0455 | -0.008452 | 0.14681 | -0.25013 | -0.1625 | 0.32082 | 0.20389 | 0.45402 | 0.000231 | -0.046932 | 121.5016 | 121.5782 | 121.7334 | 42.2228 | -121.5828 | 121.4241 | 121.5868 | 121.5397 | 119.5864 | -121.8367
1454.9531 | 121.6553 | -120.282 | 1.268 | 1.4211e-13 | -0.014055 | -0.010727 | 0.015943 | -0.03637 | 0.035295 | -0.0084697 | -0.015581 | 0.0093796 | 0.033855 | 0.0013975 | 0.037983 | -113.9047 | -78.192 | -116.1685 | 1.2196 | 1.1176 | 1.4377 | -120.301 | -119.984 | -0.75971 | -120.1101 | 1.1467 | 1.2957 | 1.0654 | -120.5641 | -0.019055 | -0.048388 | 6.3773 | 4.1134 | 4.1325 | -0.15039 | 0.1697 | -0.28217 | -0.12129 | 0.29794 | 0.17186 | 0.45402 | 0.02771 | -0.2026 | 121.5016 | 121.3996 | 121.7197 | 42.09 | -121.569 | 121.4287 | 121.5777 | 121.3474 | 119.5223 | -121.8322
1456.6562 | 121.7194 | -120.2362 | 1.3 | 1.4211e-13 | -0.014483 | -0.010513 | 0.015943 | -0.035729 | 0.035722 | -0.0084697 | -0.015581 | 0.0095932 | 0.033855 | 0.00097008 | 0.038197 | -113.7261 | -78.0363 | -116.0312 | 1.2746 | 1.1909 | 1.4972 | -120.2736 | -119.9428 | -0.76429 | -120.0598 | 1.1971 | 1.3552 | 1.1341 | -120.5138 | -0.037357 | -0.025492 | 6.5101 | 4.205 | 4.2424 | -0.10917 | 0.19718 | -0.27757 | -0.10297 | 0.29337 | 0.17645 | 0.45402 | 0.055188 | -0.16596 | 121.5108 | 121.4271 | 121.7334 | 42.1999 | -121.5736 | 121.4333 | 121.5914 | 121.3703 | 119.4719 | -121.8138
1458.4375 | 121.7834 | -120.8176 | 0.73242 | 1.4211e-13 | -0.014269 | -0.010299 | 0.015943 | -0.035729 | 0.035722 | -0.0084697 | -0.015794 | 0.0095932 | 0.033855 | 0.00075648 | 0.037983 | -114.129 | -78.5537 | -116.5119 | 0.70684 | 0.60478 | 0.92949 | -120.8551 | -120.5289 | -0.76886 | -120.6504 | 0.62935 | 0.78749 | 0.5526 | -121.109 | -0.037521 | -0.025585 | 6.6886 | 4.3057 | 4.3432 | -0.12765 | 0.19706 | -0.29146 | -0.10307 | 0.28866 | 0.16715 | 0.45861 | 0.055068 | -0.17982 | 121.5244 | 121.4223 | 121.7471 | 42.2639 | -121.5875 | 121.4469 | 121.6051 | 121.3702 | 120.0487 | -121.8414
1460.1719 | 121.7834 | -120.9412 | 0.61798 | 1.4211e-13 | -0.014055 | -0.010513 | 0.016157 | -0.035942 | 0.035722 | -0.0084697 | -0.015367 | 0.0095932 | 0.034068 | 0.0011837 | 0.038197 | -114.1015 | -78.5491 | -116.5623 | 0.58322 | 0.49946 | 0.8196 | -120.9925 | -120.6617 | -0.77802 | -120.7832 | 0.52404 | 0.66845 | 0.43814 | -121.2418 | -0.051292 | -0.03476 | 6.8396 | 4.3789 | 4.4302 | -0.11852 | 0.20162 | -0.30065 | -0.093937 | 0.27947 | 0.15797 | 0.45862 | 0.050466 | -0.17984 | 121.5244 | 121.4406 | 121.7608 | 42.3921 | -121.6104 | 121.4652 | 121.6096 | 121.3793 | 120.1631 | -121.8598
1461.9531 | 121.669 | -121.0831 | 0.58594 | 1.4211e-13 | -0.014483 | -0.010086 | 0.01637 | -0.035515 | 0.035722 | -0.00083919 | -0.015581 | 0.0095932 | 0.033641 | 0.0013975 | 0.038411 | -114.0054 | -78.4667 | -116.5485 | 0.53286 | 0.43994 | 0.7555 | -121.0611 | -120.735 | -0.77344 | -120.8565 | 0.46452 | 0.62266 | 0.38777 | -121.3059 | 0.021931 | -0.053079 | 7.0777 | 4.5345 | 4.5126 | -0.146 | 0.16956 | -0.22285 | -0.12141 | 0.34812 | 0.22662 | 0.44946 | 0.036724 | -0.19816 | 121.6159 | 121.523 | 121.8386 | 42.6164 | -121.6471 | 121.5476 | 121.7057 | 121.4708 | 120.3096 | -121.8919
1463.7188 | 121.7514 | -121.2433 | 0.3891 | 1.4211e-13 | -0.014269 | -0.010086 | 0.016584 | -0.035301 | 0.036577 | -0.00083919 | -0.016008 | 0.0093796 | 0.033641 | 0.00097008 | 0.037342 | -114.0283 | -78.5491 | -116.6538 | 0.35888 | 0.29341 | 0.58151 | -121.2489 | -120.9273 | -0.77802 | -121.0442 | 0.28596 | 0.43494 | 0.24126 | -121.4982 | -0.005588 | -0.030219 | 7.215 | 4.5894 | 4.595 | -0.095689 | 0.19241 | -0.25494 | -0.10314 | 0.31603 | 0.19911 | 0.45405 | 0.045839 | -0.14784 | 121.6022 | 121.5367 | 121.8248 | 42.6942 | -121.638 | 121.5292 | 121.6782 | 121.4845 | 120.4653 | -121.8873
1465.4375 | 121.7331 | -121.2753 | 0.40283 | 1.4211e-13 | -0.014055 | -0.010086 | 0.01637 | -0.035301 | 0.035936 | 0.014421 | -0.015581 | 0.009807 | 0.033427 | 0.0011837 | 0.037129 | -113.955 | -78.3019 | -116.5989 | 0.34972 | 0.27967 | 0.56778 | -121.2718 | -120.9547 | -0.78718 | -121.0717 | 0.27223 | 0.43036 | 0.2321 | -121.5257 | 0.003561 | -0.053109 | 7.3203 | 4.6764 | 4.6729 | -0.12316 | 0.16494 | -0.25037 | -0.13061 | 0.3206 | 0.20368 | 0.45405 | 0.027527 | -0.17073 | 121.6251 | 121.555 | 121.8431 | 42.9735 | -121.6746 | 121.5476 | 121.7057 | 121.5074 | 120.4882 | -121.9285
1467.2031 | 121.701 | -121.2845 | 0.39825 | 1.4211e-13 | -0.014483 | -0.010086 | 0.01637 | -0.035301 | 0.036363 | -0.00083919 | -0.015367 | 0.0095932 | 0.033855 | 0.0013975 | 0.037342 | -113.7673 | -77.9264 | -116.4982 | 0.35888 | 0.28425 | 0.57235 | -121.2855 | -120.9593 | -0.79176 | -121.0808 | 0.27681 | 0.43036 | 0.24126 | -121.5394 | -0.001021 | -0.039374 | 7.5172 | 4.7863 | 4.7873 | -0.114 | 0.1741 | -0.25495 | -0.12145 | 0.32518 | 0.20368 | 0.45862 | 0.032105 | -0.15699 | 121.6434 | 121.5687 | 121.8568 | 43.3581 | -121.6838 | 121.5613 | 121.7148 | 121.5257 | 120.4927 | -121.9377
1468.9844 | 121.7697 | -121.2433 | 0.41657 | 1.4211e-13 | -0.014269 | -0.0098719 | 0.01637 | -0.035301 | 0.036363 | 0.0067908 | -0.015794 | 0.0093796 | 0.033641 | 0.0016111 | 0.036915 | -113.6529 | -77.6837 | -116.3883 | 0.36804 | 0.29341 | 0.58609 | -121.2809 | -120.9639 | -0.79634 | -121.0854 | 0.2997 | 0.43952 | 0.24126 | -121.5394 | -0.037641 | -0.048529 | 7.5904 | 4.855 | 4.8926 | -0.12316 | 0.16952 | -0.29615 | -0.11687 | 0.2794 | 0.1579 | 0.45405 | 0.022952 | -0.17531 | 121.6113 | 121.5367 | 121.8294 | 43.5595 | -121.6975 | 121.543 | 121.6828 | 121.4845 | 120.4469 | -121.956
1470.7656 | 121.7377 | -121.2753 | 0.43488 | 1.4211e-13 | -0.014269 | -0.010086 | 0.016584 | -0.035301 | 0.036577 | 0.014421 | -0.015581 | 0.010021 | 0.034282 | 0.0011837 | 0.03777 | -113.4835 | -77.3816 | -116.2693 | 0.38177 | 0.30715 | 0.59983 | -121.2855 | -120.9593 | -0.80549 | -121.0808 | 0.30885 | 0.44867 | 0.255 | -121.544 | -0.010176 | -0.053103 | 7.7919 | 5.0061 | 5.0162 | -0.12773 | 0.16495 | -0.26868 | -0.12602 | 0.31602 | 0.19452 | 0.4632 | 0.013799 | -0.17988 | 121.6571 | 121.5825 | 121.8752 | 43.8938 | -121.7204 | 121.5842 | 121.724 | 121.5303 | 120.4698 | -121.9789
1472.4844 | 121.7239 | -121.2799 | 0.46234 | 1.4211e-13 | -0.014269 | -0.0096583 | 0.016798 | -0.035088 | 0.036791 | 0.0067908 | -0.015581 | 0.0093796 | 0.034068 | 0.0013975 | 0.037556 | -113.2912 | -77.1114 | -116.1731 | 0.39551 | 0.30715 | 0.61356 | -121.2809 | -120.9502 | -0.80549 | -121.0808 | 0.31801 | 0.47614 | 0.25957 | -121.5394 | -0.00102 | -0.066834 | 7.9887 | 5.1068 | 5.1078 | -0.15519 | 0.15122 | -0.25953 | -0.14433 | 0.32975 | 0.1991 | 0.45862 | 0.013804 | -0.20277 | 121.6754 | 121.5871 | 121.8935 | 44.1685 | -121.7433 | 121.5979 | 121.7561 | 121.5395 | 120.4744 | -122.0018
1474.2656 | 121.875 | -121.2387 | 0.42114 | 1.4211e-13 | -0.014696 | -0.0098719 | 0.01637 | -0.035301 | 0.037218 | -0.0084697 | -0.015581 | 0.009807 | 0.033855 | 0.0016111 | 0.037342 | -113.108 | -77.0839 | -116.0953 | 0.39093 | 0.32088 | 0.61356 | -121.2901 | -120.9685 | -0.81007 | -121.09 | 0.32717 | 0.46699 | 0.255 | -121.5532 | -0.051377 | -0.030215 | 8.1307 | 5.1434 | 5.1948 | -0.10026 | 0.19242 | -0.31446 | -0.093975 | 0.27024 | 0.14874 | 0.4632 | 0.045845 | -0.16615 | 121.6296 | 121.5596 | 121.8523 | 44.1548 | -121.7112 | 121.5659 | 121.7057 | 121.4937 | 120.4286 | -121.9743
1476 | 121.8887 | -121.2799 | 0.40283 | 1.4211e-13 | -0.014055 | -0.0094445 | 0.017011 | -0.034874 | 0.037218 | 0.0067908 | -0.015794 | 0.0093796 | 0.034282 | 0.0011837 | 0.03777 | -112.9524 | -77.0611 | -116.0175 | 0.39093 | 0.30257 | 0.59983 | -121.313 | -120.9914 | -0.81465 | -121.1174 | 0.2997 | 0.45325 | 0.25042 | -121.5715 | -0.033072 | -0.011904 | 8.3275 | 5.2624 | 5.2955 | -0.10026 | 0.19699 | -0.29158 | -0.10314 | 0.28855 | 0.16247 | 0.45405 | 0.05042 | -0.15242 | 121.6708 | 121.5825 | 121.8797 | 44.2189 | -121.7158 | 121.5796 | 121.7332 | 121.5303 | 120.4653 | -121.9743
1477.7656 | 121.7651 | -121.344 | 0.46234 | 1.4211e-13 | -0.014055 | -0.0092309 | 0.017225 | -0.034874 | 0.037218 | -0.0084697 | -0.015367 | 0.0095932 | 0.033855 | 0.0011837 | 0.037342 | -112.7555 | -77.0015 | -115.9122 | 0.37261 | 0.30257 | 0.6044 | -121.3313 | -121.0005 | -0.81923 | -121.122 | 0.30885 | 0.45325 | 0.24584 | -121.5898 | 0.012699 | -0.089726 | 8.5885 | 5.4318 | 5.4191 | -0.15977 | 0.14206 | -0.24581 | -0.15349 | 0.34348 | 0.22198 | 0.46778 | -0.009089 | -0.2165 | 121.7166 | 121.6466 | 121.9484 | 44.3425 | -121.7936 | 121.6528 | 121.7972 | 121.5898 | 120.5248 | -122.0521
1479.4844 | 121.907 | -121.2936 | 0.38452 | 1.4211e-13 | -0.014055 | -0.0092309 | 0.017439 | -0.034874 | 0.037859 | -0.0084697 | -0.015794 | 0.0093796 | 0.034282 | 0.0011837 | 0.037342 | -112.5586 | -76.7589 | -115.7931 | 0.38635 | 0.30257 | 0.59525 | -121.3405 | -121.0143 | -0.82839 | -121.1403 | 0.30428 | 0.46241 | 0.25042 | -121.599 | -0.046813 | 0.001829 | 8.735 | 5.5005 | 5.5473 | -0.081953 | 0.21073 | -0.30532 | -0.080245 | 0.27939 | 0.15331 | 0.45863 | 0.077889 | -0.1341 | 121.68 | 121.5962 | 121.8889 | 44.5348 | -121.725 | 121.5979 | 121.7561 | 121.5441 | 120.4653 | -121.9835
1481.2656 | 121.7834 | -121.3257 | 0.42572 | 1.4211e-13 | -0.014055 | -0.0096583 | 0.017439 | -0.03466 | 0.037645 | 0.0067908 | -0.015367 | 0.0095932 | 0.034282 | 0.0013975 | 0.037129 | -112.4258 | -76.5803 | -115.6832 | 0.38177 | 0.30715 | 0.59525 | -121.3496 | -121.0234 | -0.83297 | -121.1403 | 0.31343 | 0.45325 | 0.25042 | -121.6081 | -0.023927 | -0.043948 | 8.8998 | 5.6424 | 5.6664 | -0.11857 | 0.16953 | -0.28243 | -0.11229 | 0.30227 | 0.18535 | 0.46778 | 0.027532 | -0.1753 | 121.7075 | 121.6328 | 121.9209 | 44.7454 | -121.7753 | 121.6391 | 121.7789 | 121.5761 | 120.4927 | -122.0338
1482.9844 | 121.9208 | -121.3165 | 0.38452 | 1.4211e-13 | -0.014055 | -0.0094445 | 0.017439 | -0.03466 | 0.038073 | -0.00083919 | -0.015794 | 0.009807 | 0.034068 | 0.0016111 | 0.037342 | -112.2564 | -76.4567 | -115.6237 | 0.37261 | 0.29799 | 0.59525 | -121.3679 | -121.0326 | -0.84212 | -121.1586 | 0.30428 | 0.45325 | 0.24584 | -121.6219 | -0.051398 | -0.011906 | 9.0601 | 5.6928 | 5.7442 | -0.086532 | 0.21073 | -0.30533 | -0.080245 | 0.28396 | 0.15788 | 0.46321 | 0.068731 | -0.13868 | 121.6891 | 121.6145 | 121.9118 | 44.8599 | -121.7524 | 121.6208 | 121.7698 | 121.5624 | 120.4744 | -122.0064
1484.7656 | 121.8521 | -121.0327 | 0.76446 | 1.4211e-13 | -0.014055 | -0.0094445 | 0.017439 | -0.03466 | 0.037859 | -0.0084697 | -0.015367 | 0.0095932 | 0.034068 | 0.00097008 | 0.037342 | -111.8444 | -75.8019 | -115.2941 | 0.63358 | 0.54067 | 0.85165 | -121.1069 | -120.7762 | -0.83297 | -120.8977 | 0.56525 | 0.71423 | 0.4885 | -121.3654 | -0.074213 | -0.13088 | 9.1883 | 5.7386 | 5.8128 | -0.22379 | 0.087184 | -0.33273 | -0.19921 | 0.25655 | 0.13505 | 0.46778 | -0.050232 | -0.27596 | 121.6663 | 121.5734 | 121.8844 | 45.2308 | -121.8714 | 121.598 | 121.7469 | 121.5212 | 120.1997 | -122.1299
1486.5625 | 121.8246 | -121.0236 | 0.79193 | 1.4211e-13 | -0.014055 | -0.0092309 | 0.017439 | -0.034447 | 0.038073 | -0.0084697 | -0.015581 | 0.0095932 | 0.033641 | 0.0013975 | 0.037129 | -111.675 | -75.3395 | -115.1659 | 0.72973 | 0.63225 | 0.9478 | -121.0245 | -120.6983 | -0.8467 | -120.8244 | 0.66598 | 0.81496 | 0.58008 | -121.2876 | -0.000947 | -0.062202 | 9.3486 | 5.8577 | 5.8586 | -0.15968 | 0.15587 | -0.26404 | -0.12595 | 0.32524 | 0.19916 | 0.4632 | 0.023031 | -0.21186 | 121.7533 | 121.6558 | 121.9714 | 45.6841 | -121.8164 | 121.6895 | 121.8385 | 121.6036 | 120.1769 | -122.0795
1488.2969 | 121.8292 | -120.9183 | 0.88348 | 1.4211e-13 | -0.013628 | -0.0090171 | 0.017652 | -0.034874 | 0.0385 | -0.0084697 | -0.016008 | 0.0093796 | 0.033855 | 0.0016111 | 0.03777 | -111.6155 | -75.2708 | -115.024 | 0.81672 | 0.72841 | 1.0348 | -120.9421 | -120.6067 | -0.85128 | -120.7328 | 0.74839 | 0.90653 | 0.68538 | -121.196 | -0.023812 | -0.066766 | 9.3028 | 5.8943 | 5.9181 | -0.15508 | 0.15131 | -0.27775 | -0.13509 | 0.31153 | 0.18545 | 0.4632 | 0.02305 | -0.1981 | 121.735 | 121.6467 | 121.9531 | 45.6475 | -121.8256 | 121.6667 | 121.8248 | 121.6037 | 120.067 | -122.0795
1490.0781 | 121.9666 | -120.7993 | 0.97046 | 1.4211e-13 | -0.014055 | -0.0094445 | 0.017652 | -0.035088 | 0.037859 | -0.00083919 | -0.015367 | 0.0095932 | 0.033855 | 0.0013975 | 0.037129 | -111.6292 | -75.4082 | -114.9049 | 0.94491 | 0.84288 | 1.163 | -120.8368 | -120.5106 | -0.86044 | -120.6321 | 0.86743 | 1.0118 | 0.79069 | -121.0999 | -0.037516 | -0.025546 | 9.1701 | 5.8943 | 5.9318 | -0.12758 | 0.19254 | -0.30061 | -0.10303 | 0.28866 | 0.16716 | 0.46777 | 0.041383 | -0.17977 | 121.7442 | 121.6421 | 121.9622 | 45.3911 | -121.8072 | 121.6667 | 121.8111 | 121.5899 | 119.9388 | -122.0703
1491.8594 | 121.994 | -120.7535 | 0.99792 | 1.4211e-13 | -0.013414 | -0.0092309 | 0.017652 | -0.034447 | 0.0385 | 0.0067908 | -0.015367 | 0.0095932 | 0.034282 | 0.0016111 | 0.037342 | -111.2263 | -73.183 | -114.7126 | 0.96781 | 0.87035 | 1.1859 | -120.8139 | -120.4877 | -0.86044 | -120.6138 | 0.89032 | 1.0347 | 0.80901 | -121.0724 | -0.060397 | -0.03012 | 9.5272 | 6.0408 | 6.1012 | -0.12757 | 0.18796 | -0.31892 | -0.1076 | 0.26578 | 0.1397 | 0.45861 | 0.03681 | -0.18892 | 121.7213 | 121.6238 | 121.9394 | 47.5705 | -121.8118 | 121.6438 | 121.7882 | 121.5625 | 119.893 | -122.0703
1493.6406 | 121.907 | -120.7123 | 1.0941 | 1.4211e-13 | -0.013414 | -0.0088035 | 0.01808 | -0.034447 | 0.038927 | -0.00083919 | -0.015581 | 0.0095932 | 0.033855 | 0.0013975 | 0.037556 | -110.8875 | -72.6015 | -114.5433 | 1.0411 | 0.9482 | 1.2637 | -120.7452 | -120.4236 | -0.8696 | -120.5451 | 0.96816 | 1.1126 | 0.896 | -121.0083 | -0.032912 | -0.052996 | 9.8248 | 6.169 | 6.2019 | -0.14586 | 0.16967 | -0.29601 | -0.1259 | 0.28868 | 0.16718 | 0.46319 | 0.018516 | -0.19805 | 121.7533 | 121.6605 | 121.976 | 48.1108 | -121.8392 | 121.6804 | 121.8249 | 121.6083 | 119.8427 | -122.1023
1495.4219 | 121.9666 | -120.6985 | 1.0574 | 1.4211e-13 | -0.012773 | -0.0088035 | 0.017652 | -0.034447 | 0.039141 | -0.00083919 | -0.015581 | 0.0095932 | 0.033855 | 0.0011837 | 0.037342 | -110.6677 | -72.3039 | -114.5249 | 1.0319 | 0.93904 | 1.25 | -120.7589 | -120.4419 | -0.87875 | -120.5588 | 0.95442 | 1.1126 | 0.89142 | -121.0358 | -0.060382 | -0.025531 | 10.0308 | 6.1736 | 6.234 | -0.1184 | 0.19255 | -0.33722 | -0.10301 | 0.25663 | 0.13971 | 0.47693 | 0.055137 | -0.16601 | 121.7305 | 121.6376 | 121.9485 | 48.3947 | -121.8164 | 121.653 | 121.8111 | 121.59 | 119.8198 | -122.0932
1497.1875 | 121.9528 | -120.6757 | 1.1169 | 1.4211e-13 | -0.012773 | -0.0090171 | 0.017652 | -0.034233 | 0.039568 | -0.00083919 | -0.015794 | 0.0093796 | 0.034068 | 0.0011837 | 0.037342 | -110.4663 | -71.8414 | -114.4608 | 1.0777 | 0.98483 | 1.2958 | -120.7269 | -120.4007 | -0.88791 | -120.5176 | 1.0048 | 1.1584 | 0.92347 | -120.9854 | -0.051218 | -0.039256 | 10.2094 | 6.2148 | 6.266 | -0.13211 | 0.17883 | -0.30974 | -0.11216 | 0.27495 | 0.15803 | 0.46777 | 0.041414 | -0.19347 | 121.7533 | 121.6605 | 121.9714 | 48.8342 | -121.8438 | 121.6804 | 121.834 | 121.5991 | 119.7877 | -122.1023
1498.9688 | 121.8979 | -120.6024 | 1.2543 | 1.4211e-13 | -0.012773 | -0.0092309 | 0.017866 | -0.034233 | 0.039355 | -0.0084697 | -0.015794 | 0.0095932 | 0.033855 | 0.00097008 | 0.037556 | -110.2053 | -71.7316 | -114.3464 | 1.183 | 1.0764 | 1.3965 | -120.6307 | -120.3091 | -0.88791 | -120.4215 | 1.1101 | 1.2591 | 1.0334 | -120.8938 | -0.028302 | -0.071283 | 10.3971 | 6.256 | 6.2843 | -0.17787 | 0.14223 | -0.2914 | -0.14418 | 0.29328 | 0.18094 | 0.47235 | 0.004814 | -0.22091 | 121.7854 | 121.6788 | 121.9989 | 48.8709 | -121.885 | 121.7125 | 121.8615 | 121.6358 | 119.7145 | -122.1481
1500.75 | 121.9894 | -120.4422 | 1.3412 | 1.4211e-13 | -0.012773 | -0.0090171 | 0.017439 | -0.034447 | 0.039782 | -0.00083919 | -0.015794 | 0.0095932 | 0.034496 | 0.0013975 | 0.037342 | -109.8482 | -71.6263 | -114.1907 | 1.2929 | 1.2 | 1.5018 | -120.5254 | -120.1992 | -0.90165 | -120.3207 | 1.22 | 1.369 | 1.1524 | -120.7885 | -0.083204 | -0.048377 | 10.594 | 6.2515 | 6.3347 | -0.14121 | 0.16056 | -0.34631 | -0.12127 | 0.24296 | 0.12146 | 0.46776 | 0.027725 | -0.18885 | 121.7351 | 121.6422 | 121.944 | 48.8159 | -121.8667 | 121.6622 | 121.8112 | 121.5946 | 119.5406 | -122.1298
1502.5156 | 122.0352 | -120.4514 | 1.3367 | 1.4211e-13 | -0.012773 | -0.0088035 | 0.01808 | -0.034233 | 0.039996 | -0.00083919 | -0.015794 | 0.0095932 | 0.034068 | 0.0020385 | 0.037556 | -109.6468 | -71.0539 | -114.1953 | 1.3295 | 1.2412 | 1.5476 | -120.5025 | -120.1672 | -0.9108 | -120.2841 | 1.2566 | 1.4102 | 1.1845 | -120.761 | -0.051154 | -0.007172 | 10.8046 | 6.2561 | 6.3072 | -0.095422 | 0.21093 | -0.30968 | -0.080067 | 0.28416 | 0.16724 | 0.47692 | 0.07351 | -0.15222 | 121.7809 | 121.6926 | 121.999 | 49.3974 | -121.8392 | 121.708 | 121.8615 | 121.6358 | 119.5406 | -122.0977
1504.2344 | 121.9254 | -120.3369 | 1.5335 | 1.4211e-13 | -0.01256 | -0.0088035 | 0.017652 | -0.034233 | 0.040209 | 0.0067908 | -0.015581 | 0.0093796 | 0.034282 | 0.0013975 | 0.037342 | -109.308 | -69.7994 | -114.0717 | 1.4806 | 1.3924 | 1.6941 | -120.3606 | -120.0344 | -0.91538 | -120.1513 | 1.4123 | 1.5659 | 1.3401 | -120.6191 | -0.023649 | -0.052923 | 11.029 | 6.2652 | 6.2889 | -0.14116 | 0.1606 | -0.28218 | -0.12124 | 0.3025 | 0.18558 | 0.46776 | 0.032345 | -0.19338 | 121.8175 | 121.7293 | 122.031 | 50.5375 | -121.8941 | 121.7492 | 121.9028 | 121.677 | 119.4215 | -122.1526
1506.0156 | 122.0352 | -120.1996 | 1.6296 | 1.4211e-13 | -0.012132 | -0.0085899 | 0.017652 | -0.034447 | 0.040209 | 0.0067908 | -0.015794 | 0.0095932 | 0.034068 | 0.0016111 | 0.037342 | -108.9966 | -69.3232 | -113.9206 | 1.5859 | 1.4885 | 1.804 | -120.2507 | -119.9291 | -0.91538 | -120.0414 | 1.513 | 1.662 | 1.4363 | -120.5229 | -0.051084 | -0.043751 | 11.203 | 6.279 | 6.3301 | -0.14113 | 0.17436 | -0.32335 | -0.11664 | 0.27048 | 0.15814 | 0.48149 | 0.032364 | -0.19336 | 121.7855 | 121.6881 | 122.0036 | 50.8764 | -121.8803 | 121.7126 | 121.8616 | 121.6359 | 119.2842 | -122.1526
1507.7969 | 121.9757 | -119.957 | 1.8951 | 1.4211e-13 | -0.012132 | -0.0088035 | 0.017439 | -0.034447 | 0.040209 | -0.00083919 | -0.015581 | 0.0095932 | 0.034068 | 0.0016111 | 0.037342 | -108.6578 | -68.6868 | -113.6139 | 1.8102 | 1.7266 | 2.0375 | -120.0171 | -119.6956 | -0.92912 | -119.8171 | 1.7557 | 1.9001 | 1.6652 | -120.2894 | -0.060173 | -0.084913 | 11.2991 | 6.3431 | 6.4033 | -0.16853 | 0.14237 | -0.33245 | -0.13948 | 0.26139 | 0.13988 | 0.47233 | 0.004949 | -0.22994 | 121.7672 | 121.6836 | 121.9945 | 51.2702 | -121.9123 | 121.7126 | 121.8571 | 121.6222 | 119.0279 | -122.1846
1509.5156 | 121.9437 | -119.8563 | 2.0279 | 1.4211e-13 | -0.012346 | -0.0083761 | 0.017652 | -0.034233 | 0.040637 | -0.0084697 | -0.015794 | 0.009807 | 0.033855 | 0.0013975 | 0.037342 | -108.5159 | -68.1328 | -113.3941 | 1.9659 | 1.8731 | 2.1794 | -119.8889 | -119.5582 | -0.93828 | -119.6843 | 1.8976 | 2.042 | 1.8209 | -120.1475 | -0.032672 | -0.061999 | 11.3404 | 6.4622 | 6.4948 | -0.15475 | 0.15155 | -0.29121 | -0.1303 | 0.29804 | 0.17196 | 0.46317 | 0.014134 | -0.20702 | 121.8222 | 121.7294 | 122.0357 | 51.7235 | -121.9168 | 121.7539 | 121.8983 | 121.6771 | 118.918 | -122.1754
1511.2969 | 122.0764 | -119.7556 | 2.1103 | 1.4211e-13 | -0.012346 | -0.0085899 | 0.018293 | -0.034447 | 0.040637 | -0.00083919 | -0.015581 | 0.0093796 | 0.034068 | 0.0013975 | 0.037129 | -108.319 | -67.8306 | -113.2751 | 2.0758 | 1.983 | 2.2939 | -119.779 | -119.4483 | -0.9337 | -119.5653 | 2.0029 | 2.1565 | 1.9582 | -120.0422 | -0.023485 | -0.034516 | 11.4365 | 6.4805 | 6.504 | -0.12726 | 0.18362 | -0.28661 | -0.10739 | 0.30722 | 0.1903 | 0.47691 | 0.046201 | -0.15206 | 121.8313 | 121.7386 | 122.0495 | 51.925 | -121.8893 | 121.7585 | 121.912 | 121.7138 | 118.8219 | -122.1525
1513.0781 | 121.9208 | -119.8563 | 2.0828 | 1.4211e-13 | -0.012132 | -0.0085899 | 0.017866 | -0.034233 | 0.040637 | -0.00083919 | -0.015581 | 0.009166 | 0.034282 | 0.0018249 | 0.037342 | -108.3373 | -67.913 | -113.3392 | 1.9888 | 1.9052 | 2.2115 | -119.8798 | -119.5491 | -0.94285 | -119.6706 | 1.9159 | 2.0787 | 1.8621 | -120.1383 | -0.023514 | -0.094039 | 11.5189 | 6.5171 | 6.5406 | -0.17763 | 0.12867 | -0.28205 | -0.16692 | 0.3072 | 0.18569 | 0.46775 | -0.004169 | -0.22074 | 121.845 | 121.7615 | 122.0678 | 51.9433 | -121.9626 | 121.7722 | 121.9349 | 121.7183 | 118.9134 | -122.2211
1514.8594 | 122.0901 | -119.7601 | 2.0737 | 1.4211e-13 | -0.012132 | -0.0081625 | 0.017866 | -0.034447 | 0.040637 | -0.0084697 | -0.015581 | 0.009166 | 0.034282 | 0.0013975 | 0.037556 | -108.1908 | -67.7848 | -113.3575 | 1.9567 | 1.8731 | 2.1794 | -119.9072 | -119.5765 | -0.95659 | -119.698 | 1.893 | 2.0466 | 1.8117 | -120.1749 | -0.14712 | -0.11693 | 11.5693 | 6.4027 | 6.5498 | -0.20053 | 0.10577 | -0.41482 | -0.18066 | 0.18359 | 0.062092 | 0.47691 | -0.027063 | -0.26195 | 121.7169 | 121.6333 | 121.9396 | 51.9753 | -121.9809 | 121.6531 | 121.8067 | 121.5719 | 118.8035 | -122.2486
1516.5781 | 121.9986 | -119.6503 | 2.2751 | 1.4211e-13 | -0.011705 | -0.0083761 | 0.017652 | -0.034233 | 0.040637 | -0.00083919 | -0.015367 | 0.009807 | 0.034068 | 0.0013975 | 0.037342 | -107.8749 | -67.5971 | -113.1194 | 2.2269 | 2.125 | 2.4496 | -119.6554 | -119.3201 | -0.96575 | -119.4416 | 2.1586 | 2.3122 | 2.0773 | -119.9231 | -0.005139 | -0.048223 | 11.7753 | 6.5309 | 6.536 | -0.1501 | 0.1745 | -0.27284 | -0.11652 | 0.33014 | 0.20864 | 0.48148 | 0.03708 | -0.19781 | 121.8771 | 121.7752 | 122.0999 | 52.0532 | -121.9305 | 121.8088 | 121.9624 | 121.7275 | 118.6845 | -122.1982
1518.375 | 121.9574 | -119.6274 | 2.3346 | 1.4211e-13 | -0.011919 | -0.0081625 | 0.017866 | -0.034233 | 0.041064 | 0.0067908 | -0.015581 | 0.0093796 | 0.033855 | 0.0018249 | 0.037342 | -107.7101 | -67.2949 | -113.0736 | 2.2818 | 2.1891 | 2.4954 | -119.6096 | -119.2835 | -0.97491 | -119.3958 | 2.2089 | 2.3671 | 2.1414 | -119.8727 | 0.017761 | -0.052792 | 11.9173 | 6.5538 | 6.536 | -0.14551 | 0.16077 | -0.24537 | -0.12567 | 0.34388 | 0.23154 | 0.4769 | 0.032513 | -0.19322 | 121.9092 | 121.8165 | 122.1227 | 52.3325 | -121.9442 | 121.8363 | 121.9945 | 121.7688 | 118.6525 | -122.2073
1520.1562 | 121.9803 | -119.577 | 2.3621 | 1.4211e-13 | -0.011705 | -0.0081625 | 0.01808 | -0.034019 | 0.041278 | 0.014421 | -0.015581 | 0.0095932 | 0.033855 | 0.0016111 | 0.03777 | -107.4766 | -67.1896 | -113.005 | 2.3001 | 2.2028 | 2.5183 | -119.5959 | -119.2652 | -0.97491 | -119.3775 | 2.2318 | 2.3854 | 2.1551 | -119.8636 | -0.018856 | -0.061945 | 12.1004 | 6.5721 | 6.5909 | -0.15924 | 0.1562 | -0.28656 | -0.13024 | 0.31184 | 0.1995 | 0.48606 | 0.023362 | -0.20695 | 121.8771 | 121.7798 | 122.0953 | 52.3874 | -121.9579 | 121.8088 | 121.9624 | 121.7321 | 118.6021 | -122.2256
1521.875 | 121.9757 | -119.5038 | 2.4857 | 1.4211e-13 | -0.011705 | -0.0083761 | 0.018293 | -0.033806 | 0.041064 | 0.0067908 | -0.015581 | 0.0093796 | 0.034068 | 0.0018249 | 0.03777 | -107.2523 | -67.1163 | -112.8997 | 2.3779 | 2.2807 | 2.6007 | -119.518 | -119.1965 | -0.97949 | -119.3134 | 2.3051 | 2.4633 | 2.2421 | -119.7857 | -0.014257 | -0.10771 | 12.2515 | 6.6041 | 6.6184 | -0.20499 | 0.11502 | -0.28196 | -0.18058 | 0.30728 | 0.19036 | 0.47232 | -0.022398 | -0.24355 | 121.8817 | 121.7844 | 122.1045 | 52.3875 | -122.0037 | 121.8089 | 121.967 | 121.7459 | 118.5243 | -122.2714
1523.6562 | 122.1039 | -119.7372 | 2.1835 | 1.4211e-13 | -0.011919 | -0.0083761 | 0.01808 | -0.034233 | 0.041278 | 0.0067908 | -0.015581 | 0.0093796 | 0.033855 | 0.0016111 | 0.037129 | -107.2706 | -66.9561 | -113.0553 | 2.1628 | 2.0746 | 2.3809 | -119.7424 | -119.4071 | -0.9978 | -119.5332 | 2.1036 | 2.2526 | 2.0178 | -120.0055 | -0.005164 | -0.020769 | 12.4667 | 6.6819 | 6.6871 | -0.10892 | 0.19737 | -0.26829 | -0.079909 | 0.33012 | 0.20404 | 0.47232 | 0.06911 | -0.16578 | 121.9 | 121.8119 | 122.1181 | 52.7812 | -121.9259 | 121.8409 | 121.9899 | 121.755 | 118.7394 | -122.1891
1525.4531 | 122.0215 | -119.9707 | 2.005 | 1.4211e-13 | -0.011919 | -0.0077351 | 0.017866 | -0.033806 | 0.041491 | -0.0084697 | -0.015581 | 0.0095932 | 0.034282 | 0.0016111 | 0.037556 | -107.3759 | -67.4094 | -113.2156 | 1.9293 | 1.8457 | 2.1566 | -119.9851 | -119.6498 | -1.0115 | -119.7667 | 1.8701 | 2.0283 | 1.7842 | -120.2436 | -0.014388 | -0.075738 | 12.5948 | 6.7552 | 6.7695 | -0.15934 | 0.15155 | -0.27293 | -0.13488 | 0.3209 | 0.20398 | 0.47691 | 0.023287 | -0.22076 | 121.9 | 121.8164 | 122.1273 | 52.5613 | -121.9901 | 121.8408 | 121.999 | 121.755 | 118.9592 | -122.2486
1527.1719 | 122.0856 | -120.0073 | 1.9089 | 1.4211e-13 | -0.012132 | -0.0077351 | 0.017652 | -0.033806 | 0.041064 | -0.0084697 | -0.015794 | 0.0095932 | 0.034068 | 0.0016111 | 0.037556 | -107.2706 | -67.2079 | -113.2339 | 1.8743 | 1.777 | 2.0925 | -120.0538 | -119.7185 | -1.0253 | -119.8446 | 1.8014 | 1.9505 | 1.7476 | -120.3169 | -0.046451 | -0.034549 | 12.7367 | 6.7735 | 6.8199 | -0.13189 | 0.18358 | -0.30957 | -0.10743 | 0.28884 | 0.16277 | 0.47233 | 0.04158 | -0.16126 | 121.8816 | 121.7843 | 122.0998 | 52.7994 | -121.9626 | 121.8088 | 121.9578 | 121.7549 | 118.9821 | -122.2258
1528.9531 | 122.1313 | -119.9982 | 1.9135 | 1.4211e-13 | -0.012132 | -0.0077351 | 0.01808 | -0.033592 | 0.041705 | 0.0067908 | -0.015581 | 0.0095932 | 0.034068 | 0.0013975 | 0.037342 | -107.0371 | -66.8233 | -113.0965 | 1.8835 | 1.7907 | 2.097 | -120.0446 | -119.7139 | -1.039 | -119.8308 | 1.8014 | 1.9642 | 1.7476 | -120.3077 | -0.046448 | -0.029969 | 12.9611 | 6.9017 | 6.9481 | -0.12273 | 0.18358 | -0.30956 | -0.11201 | 0.28427 | 0.16735 | 0.47691 | 0.050739 | -0.16583 | 121.8817 | 121.7889 | 122.0952 | 53.1749 | -121.9581 | 121.7996 | 121.9624 | 121.7458 | 118.9592 | -122.2212
1530.7344 | 122.0123 | -120.0714 | 1.8951 | 1.4211e-13 | -0.012132 | -0.0079487 | 0.01808 | -0.034019 | 0.041491 | -0.00083919 | -0.015581 | 0.0093796 | 0.034068 | 0.0018249 | 0.037556 | -106.8906 | -66.6264 | -113.0324 | 1.8377 | 1.7449 | 2.0558 | -120.0996 | -119.7643 | -1.039 | -119.8903 | 1.7786 | 1.9184 | 1.6835 | -120.3718 | -0.028153 | -0.057443 | 13.1808 | 7.039 | 7.0671 | -0.15021 | 0.16068 | -0.30043 | -0.11659 | 0.30714 | 0.18107 | 0.48149 | 0.023263 | -0.21162 | 121.9091 | 121.8163 | 122.1272 | 53.445 | -121.9947 | 121.85 | 121.9898 | 121.7549 | 119.0324 | -122.267
1532.4688 | 122.1634 | -120.0485 | 1.8539 | 1.4211e-13 | -0.011705 | -0.0077351 | 0.018293 | -0.033592 | 0.041919 | 0.0067908 | -0.015581 | 0.0095932 | 0.034496 | 0.0016111 | 0.03777 | -106.7258 | -66.4982 | -112.95 | 1.8194 | 1.7266 | 2.0329 | -120.1225 | -119.7872 | -1.0482 | -119.9041 | 1.7557 | 1.9001 | 1.6744 | -120.3947 | -0.073936 | -0.034558 | 13.3228 | 7.0985 | 7.1724 | -0.12733 | 0.17899 | -0.34621 | -0.098284 | 0.26136 | 0.14444 | 0.49065 | 0.046148 | -0.17958 | 121.8679 | 121.7751 | 122.0815 | 53.5503 | -121.9764 | 121.8042 | 121.9486 | 121.7229 | 119.0004 | -122.2487
1534.25 | 122.168 | -120.2133 | 1.7441 | 1.4211e-13 | -0.011919 | -0.0073077 | 0.017866 | -0.033592 | 0.042132 | 0.0067908 | -0.015794 | 0.0093796 | 0.034282 | 0.0013975 | 0.037342 | -106.6296 | -66.3151 | -112.8676 | 1.8102 | 1.7175 | 2.0238 | -120.1408 | -119.8146 | -1.0619 | -119.9224 | 1.7419 | 1.8955 | 1.6881 | -120.4085 | 0.072544 | 0.066149 | 13.5837 | 7.3457 | 7.2732 | -0.026624 | 0.27969 | -0.19515 | -0.002157 | 0.39869 | 0.29092 | 0.48607 | 0.15143 | -0.055982 | 122.0235 | 121.9308 | 122.2371 | 53.8982 | -121.8849 | 121.9552 | 122.1088 | 121.9014 | 119.1514 | -122.1525
1536.0469 | 122.1863 | -120.163 | 1.7487 | 1.4211e-13 | -0.011919 | -0.0077351 | 0.018293 | -0.033378 | 0.041919 | -0.0084697 | -0.015581 | 0.010021 | 0.034068 | 0.0018249 | 0.037556 | -106.593 | -65.9717 | -112.7898 | 1.7553 | 1.6671 | 1.9688 | -120.2003 | -119.8696 | -1.0711 | -119.9957 | 1.687 | 1.8451 | 1.6103 | -120.4726 | -0.037336 | 0.006631 | 13.57 | 7.3732 | 7.4105 | -0.081569 | 0.22017 | -0.30961 | -0.061676 | 0.29339 | 0.16731 | 0.47692 | 0.096491 | -0.13839 | 121.9183 | 121.8301 | 122.1318 | 54.1913 | -121.949 | 121.8499 | 122.0081 | 121.7732 | 119.0919 | -122.2212
1537.7656 | 122.0581 | -120.0897 | 1.8906 | 1.4211e-13 | -0.012132 | -0.0077351 | 0.018293 | -0.032951 | 0.042346 | -0.00083919 | -0.015794 | 0.0095932 | 0.034496 | 0.0016111 | 0.037342 | -106.387 | -65.7977 | -112.6662 | 1.8194 | 1.7312 | 2.0329 | -120.1408 | -119.8146 | -1.0711 | -119.927 | 1.7465 | 1.9001 | 1.6835 | -120.4176 | -0.051052 | -0.071179 | 13.7028 | 7.4236 | 7.4746 | -0.15937 | 0.14237 | -0.3279 | -0.14406 | 0.27509 | 0.16275 | 0.49065 | 0.009527 | -0.20704 | 121.9091 | 121.8209 | 122.1227 | 54.292 | -122.0313 | 121.8362 | 121.9898 | 121.7732 | 119.0187 | -122.3082
1539.5469 | 122.1451 | -120.076 | 1.8906 | 1.4211e-13 | -0.011491 | -0.0075215 | 0.01808 | -0.033378 | 0.04256 | -0.0084697 | -0.015794 | 0.009807 | 0.034068 | 0.0022521 | 0.037556 | -106.2771 | -65.4543 | -112.5059 | 1.8697 | 1.777 | 2.0879 | -120.0996 | -119.7643 | -1.0802 | -119.8812 | 1.806 | 1.9642 | 1.7293 | -120.3673 | -0.023575 | -0.020816 | 13.7989 | 7.5701 | 7.5936 | -0.11358 | 0.19731 | -0.29127 | -0.084542 | 0.31172 | 0.1948 | 0.48607 | 0.073627 | -0.16126 | 121.9457 | 121.853 | 122.1639 | 54.6217 | -121.9901 | 121.882 | 122.0402 | 121.8053 | 118.9958 | -122.2578
1541.2812 | 122.0261 | -120.1859 | 1.8585 | 1.4211e-13 | -0.011491 | -0.0075215 | 0.018293 | -0.033592 | 0.04256 | -0.00083919 | -0.015581 | 0.0093796 | 0.034282 | 0.0013975 | 0.037342 | -106.3091 | -65.5001 | -112.5105 | 1.7828 | 1.6854 | 1.9917 | -120.2049 | -119.8604 | -1.0985 | -119.9865 | 1.7099 | 1.868 | 1.6377 | -120.4634 | -0.019027 | -0.075763 | 13.8767 | 7.6754 | 7.6944 | -0.17312 | 0.1332 | -0.27756 | -0.14865 | 0.32543 | 0.19935 | 0.47692 | 0.00952 | -0.22079 | 121.9686 | 121.8713 | 122.1776 | 54.6858 | -122.0634 | 121.8957 | 122.0539 | 121.8236 | 119.0873 | -122.3219
1543.0469 | 122.049 | -120.1492 | 1.8677 | 1.4211e-13 | -0.011705 | -0.0075215 | 0.018507 | -0.033378 | 0.04256 | -0.00083919 | -0.015581 | 0.0095932 | 0.034068 | 0.0018249 | 0.03777 | -106.1947 | -65.5138 | -112.364 | 1.8148 | 1.722 | 2.0238 | -120.1682 | -119.8329 | -1.1031 | -119.9544 | 1.7419 | 1.8955 | 1.6698 | -120.4451 | -0.019017 | -0.052869 | 13.9546 | 7.7852 | 7.8043 | -0.14564 | 0.1561 | -0.29587 | -0.12575 | 0.31628 | 0.19478 | 0.49065 | 0.027836 | -0.19789 | 121.964 | 121.8713 | 122.173 | 54.6354 | -122.0359 | 121.8912 | 122.0447 | 121.819 | 119.0461 | -122.3128
1544.8125 | 122.0535 | -120.2179 | 1.8585 | 1.4211e-13 | -0.011705 | -0.0070941 | 0.01808 | -0.033165 | 0.042346 | -0.00083919 | -0.015367 | 0.0095932 | 0.033855 | 0.0018249 | 0.037342 | -106.2588 | -65.4497 | -112.3594 | 1.7461 | 1.6534 | 1.9643 | -120.2369 | -119.9016 | -1.1214 | -120.0231 | 1.6778 | 1.8268 | 1.6057 | -120.5046 | -0.019036 | -0.11239 | 13.9591 | 7.8585 | 7.8775 | -0.20517 | 0.10573 | -0.28673 | -0.1807 | 0.31627 | 0.19477 | 0.48149 | -0.031688 | -0.25284 | 121.964 | 121.8712 | 122.1821 | 54.7682 | -122.0955 | 121.8957 | 122.0447 | 121.8236 | 119.0965 | -122.3631
1546.5938 | 122.1817 | -120.163 | 1.8127 | 1.4211e-13 | -0.011919 | -0.0073077 | 0.018293 | -0.032951 | 0.042773 | -0.00083919 | -0.015367 | 0.0095932 | 0.034068 | 0.0018249 | 0.037556 | -106.1947 | -65.555 | -112.2587 | 1.7599 | 1.6717 | 1.9826 | -120.2278 | -119.8787 | -1.1306 | -120.0048 | 1.7007 | 1.8543 | 1.6194 | -120.4955 | -0.06481 | -0.052878 | 13.9683 | 7.9043 | 7.9691 | -0.14108 | 0.16982 | -0.3325 | -0.11203 | 0.28423 | 0.15815 | 0.49065 | 0.041561 | -0.19332 | 121.9228 | 121.8346 | 122.1455 | 54.6079 | -122.0405 | 121.8637 | 122.0173 | 121.7824 | 119.0324 | -122.3082
1548.3125 | 122.1451 | -120.108 | 1.918 | 1.4211e-13 | -0.012132 | -0.0073077 | 0.018293 | -0.032951 | 0.04256 | -0.00083919 | -0.015794 | 0.0093796 | 0.033855 | 0.0013975 | 0.037556 | -106.0756 | -65.7519 | -112.0847 | 1.8514 | 1.7587 | 2.0696 | -120.1454 | -119.7963 | -1.1352 | -119.9224 | 1.7877 | 1.9413 | 1.7064 | -120.413 | -0.037321 | -0.066596 | 14.0324 | 8.0233 | 8.0606 | -0.15936 | 0.15153 | -0.30501 | -0.13032 | 0.31171 | 0.18564 | 0.49065 | 0.023268 | -0.21162 | 121.9595 | 121.8667 | 122.1776 | 54.3561 | -122.0634 | 121.8957 | 122.0493 | 121.8144 | 118.9729 | -122.3311
1550.0781 | 122.2137 | -119.9982 | 1.9775 | 1.4211e-13 | -0.011919 | -0.0073077 | 0.018293 | -0.032951 | 0.042773 | -0.00083919 | -0.015794 | 0.0095932 | 0.034068 | 0.0018249 | 0.037129 | -105.8055 | -65.7656 | -111.9062 | 1.9567 | 1.864 | 2.1657 | -120.04 | -119.7047 | -1.1489 | -119.8217 | 1.8884 | 2.0466 | 1.8117 | -120.3169 | -0.041869 | -0.020802 | 14.1927 | 8.092 | 8.1339 | -0.11356 | 0.18817 | -0.31872 | -0.089104 | 0.29343 | 0.1765 | 0.49523 | 0.069067 | -0.16582 | 121.9549 | 121.8621 | 122.1639 | 54.2325 | -122.0176 | 121.8866 | 122.0448 | 121.8099 | 118.8493 | -122.2944
1551.8438 | 122.1085 | -119.9615 | 2.0691 | 1.4211e-13 | -0.012132 | -0.0073077 | 0.018507 | -0.032951 | 0.042987 | 0.014421 | -0.015367 | 0.0095932 | 0.034282 | 0.0020385 | 0.037342 | -105.6407 | -65.8572 | -111.7917 | 2.0117 | 1.9189 | 2.2252 | -119.9942 | -119.6544 | -1.1672 | -119.7713 | 1.9388 | 2.0878 | 1.8712 | -120.2619 | -0.032701 | -0.057414 | 14.3209 | 8.1698 | 8.2025 | -0.15016 | 0.15614 | -0.3004 | -0.13029 | 0.30717 | 0.19025 | 0.49065 | 0.018721 | -0.19785 | 121.9732 | 121.8805 | 122.1868 | 54.1043 | -122.0633 | 121.9003 | 122.0494 | 121.8328 | 118.7943 | -122.331
1553.6406 | 122.1451 | -120.0302 | 1.9775 | 1.4211e-13 | -0.011919 | -0.0077351 | 0.018293 | -0.032524 | 0.043414 | -0.0084697 | -0.015794 | 0.0093796 | 0.034282 | 0.0018249 | 0.037556 | -105.7094 | -66.37 | -111.8054 | 1.9338 | 1.8457 | 2.1474 | -120.0812 | -119.7505 | -1.1764 | -119.8629 | 1.8655 | 2.01 | 1.798 | -120.3444 | -0.051036 | -0.043694 | 14.3209 | 8.2248 | 8.2758 | -0.13187 | 0.16985 | -0.31415 | -0.112 | 0.27968 | 0.16734 | 0.48149 | 0.032438 | -0.17955 | 121.9641 | 121.8759 | 122.1776 | 53.6602 | -122.0588 | 121.8958 | 122.0402 | 121.8282 | 118.8538 | -122.3219
1555.3594 | 122.0947 | -120.0668 | 1.9821 | 1.4211e-13 | -0.011919 | -0.0073077 | 0.018293 | -0.032951 | 0.043628 | -0.00083919 | -0.015581 | 0.0093796 | 0.034282 | 0.0016111 | 0.037129 | -105.6407 | -67.0202 | -111.7917 | 1.9338 | 1.8411 | 2.1474 | -120.0812 | -119.7551 | -1.1809 | -119.872 | 1.8701 | 2.0146 | 1.7934 | -120.3581 | -0.014415 | -0.048272 | 14.4262 | 8.2751 | 8.2895 | -0.14103 | 0.16528 | -0.29127 | -0.112 | 0.31172 | 0.1948 | 0.48607 | 0.032439 | -0.18871 | 122.0007 | 121.9079 | 122.2142 | 53.0467 | -122.0634 | 121.937 | 122.0814 | 121.8602 | 118.8859 | -122.3402
1557.1562 | 122.2412 | -120.0027 | 2.0004 | 1.4211e-13 | -0.011919 | -0.0075215 | 0.01808 | -0.032737 | 0.043628 | -0.00083919 | -0.015794 | 0.0093796 | 0.034496 | 0.0020385 | 0.037556 | -105.5857 | -67.3727 | -111.7139 | 1.9842 | 1.8869 | 2.1886 | -120.04 | -119.7093 | -1.1947 | -119.8217 | 1.9159 | 2.0649 | 1.8346 | -120.3123 | -0.037291 | -0.01622 | 14.417 | 8.2889 | 8.3262 | -0.11355 | 0.18817 | -0.30957 | -0.084521 | 0.29342 | 0.18108 | 0.49065 | 0.064493 | -0.16581 | 121.987 | 121.8896 | 122.1913 | 52.63 | -122.0405 | 121.9187 | 122.0677 | 121.8374 | 118.8081 | -122.3127
1558.875 | 122.2092 | -120.1035 | 1.8951 | 1.4211e-13 | -0.011919 | -0.0075215 | 0.018293 | -0.032737 | 0.043628 | -0.00083919 | -0.015794 | 0.0095932 | 0.034282 | 0.0018249 | 0.037556 | -105.6865 | -67.7894 | -111.8009 | 1.8835 | 1.7953 | 2.1016 | -120.1408 | -119.8055 | -1.1993 | -119.9224 | 1.8152 | 1.9642 | 1.7385 | -120.413 | -0.037319 | -0.011659 | 14.417 | 8.3026 | 8.3399 | -0.099845 | 0.20647 | -0.30959 | -0.079963 | 0.29798 | 0.18106 | 0.49065 | 0.069049 | -0.15668 | 121.9869 | 121.8988 | 122.2051 | 52.3141 | -122.0359 | 121.9186 | 122.0676 | 121.8419 | 118.9042 | -122.3082
1560.6562 | 122.2321 | -119.9341 | 2.0782 | 1.4211e-13 | -0.011705 | -0.0075215 | 0.01808 | -0.032951 | 0.043414 | -0.0084697 | -0.015794 | 0.0093796 | 0.034068 | 0.0020385 | 0.03777 | -105.5766 | -68.1694 | -111.6727 | 2.0163 | 1.9281 | 2.2298 | -120.0171 | -119.6773 | -1.213 | -119.7988 | 1.948 | 2.097 | 1.8758 | -120.2803 | -0.083061 | -0.061991 | 14.3575 | 8.2614 | 8.3445 | -0.15016 | 0.15156 | -0.34618 | -0.13029 | 0.25681 | 0.13531 | 0.48149 | 0.018724 | -0.20243 | 121.9503 | 121.8622 | 122.1639 | 51.7647 | -122.0954 | 121.882 | 122.0311 | 121.8099 | 118.7211 | -122.3585
1562.4375 | 122.0901 | -119.9661 | 2.1149 | 1.4211e-13 | -0.011491 | -0.0073077 | 0.018507 | -0.032737 | 0.043628 | -0.0084697 | -0.015367 | 0.009807 | 0.034068 | 0.0018249 | 0.037556 | -105.453 | -68.3434 | -111.6818 | 2.0483 | 1.9647 | 2.2664 | -119.9942 | -119.6498 | -1.2222 | -119.7805 | 1.9846 | 2.1244 | 1.9124 | -120.2619 | -0.028124 | -0.066563 | 14.5132 | 8.2843 | 8.3124 | -0.15015 | 0.15157 | -0.29582 | -0.13028 | 0.31633 | 0.18567 | 0.48149 | 0.009574 | -0.20242 | 122.0144 | 121.9308 | 122.2326 | 51.6227 | -122.1091 | 121.9507 | 122.0906 | 121.8786 | 118.744 | -122.3768
1564.1562 | 122.0993 | -120.0211 | 2.0828 | 1.4211e-13 | -0.011919 | -0.0075215 | 0.018507 | -0.032737 | 0.043628 | -0.0084697 | -0.015794 | 0.0093796 | 0.034282 | 0.0022521 | 0.037556 | -105.4346 | -68.7097 | -111.6589 | 2.0529 | 1.9556 | 2.2619 | -119.9942 | -119.6544 | -1.2313 | -119.7759 | 1.98 | 2.1336 | 1.917 | -120.2619 | 0.026808 | -0.029942 | 14.5864 | 8.3621 | 8.3353 | -0.12727 | 0.17903 | -0.24089 | -0.10282 | 0.36668 | 0.24518 | 0.48607 | 0.050774 | -0.1658 | 122.0739 | 121.9766 | 122.2829 | 51.3114 | -122.0771 | 122.0011 | 122.1547 | 121.9381 | 118.7897 | -122.3448
1565.9375 | 122.2504 | -119.9661 | 2.0508 | 1.4211e-13 | -0.012346 | -0.0079487 | 0.018293 | -0.032737 | 0.043842 | -0.0084697 | -0.015581 | 0.0093796 | 0.034282 | 0.0016111 | 0.037342 | -105.5674 | -69.488 | -111.9062 | 2.0071 | 1.9143 | 2.2161 | -120.0538 | -119.7139 | -1.2588 | -119.8217 | 1.9342 | 2.0832 | 1.8667 | -120.3169 | -0.08765 | -0.043682 | 14.3987 | 8.06 | 8.1476 | -0.13643 | 0.16529 | -0.35077 | -0.11656 | 0.25223 | 0.14446 | 0.49523 | 0.032454 | -0.18412 | 121.9732 | 121.8805 | 122.1822 | 50.4781 | -122.1046 | 121.9003 | 122.0494 | 121.8328 | 118.7073 | -122.3677
1567.6719 | 122.2504 | -119.6274 | 2.417 | 1.4211e-13 | -0.012132 | -0.0075215 | 0.01808 | -0.026114 | 0.043628 | -0.00083919 | -0.015794 | 0.0095932 | 0.034282 | 0.0020385 | 0.03777 | -105.1325 | -68.6822 | -102.507 | 2.3871 | 2.2944 | 2.5961 | -119.6508 | -119.3247 | -1.2496 | -119.4462 | 2.3097 | 2.4678 | 2.2421 | -119.9368 | -0.02345 | -0.029886 | 14.4949 | 17.1204 | 17.1439 | -0.12259 | 0.1791 | -0.30947 | -0.10733 | 0.30267 | 0.18117 | 0.49064 | 0.050845 | -0.17488 | 122.0145 | 121.9218 | 122.2235 | 50.9452 | -122.0678 | 121.937 | 122.0952 | 121.8695 | 118.3778 | -122.3538
1569.4531 | 122.2275 | -120.4742 | 1.5839 | 1.4211e-13 | -0.0014487 | -0.013077 | -0.04517 | -0.039788 | -0.010856 | 0.014421 | -0.015794 | 0.010021 | 0.034496 | 0.0020385 | 0.037556 | -0.26908 | -0.168 | -0.28311 | -0.057754 | -0.036272 | 0.11907 | -0.34237 | -120.1718 | -1.2679 | -120.2841 | 1.4901 | 1.6483 | 1.418 | -120.7794 | 120.1319 | -1.6416 | 120.2052 | 120.1911 | 0.059266 | -1.6201 | -1.4648 | -0.30511 | -0.093756 | 0.30247 | 0.19013 | 0.49524 | 0.064406 | -0.1659 | 120.4165 | 120.438 | 120.5933 | 120.3062 | -1.9262 | 121.9643 | 122.1225 | 121.8922 | 119.2063 | -122.3632
1571.2344 | 122.1634 | -120.0302 | 2.1103 | 1.4211e-13 | -0.0016625 | -0.012863 | -0.04517 | -0.039575 | -0.010856 | 0.014421 | -0.015794 | 0.0093796 | 0.034496 | 0.0018249 | 0.037556 | -0.19582 | -0.12679 | -0.21443 | -0.03944 | -0.04543 | 0.12823 | -0.28742 | -119.7093 | -1.2771 | -119.8262 | 1.9525 | 2.1107 | 1.8758 | -120.3169 | 119.7428 | -2.1497 | 119.8344 | 119.8158 | 0.072993 | -2.1557 | -1.9821 | -0.28668 | -0.15776 | 0.32089 | 0.20397 | 0.49065 | 0.000415 | -0.23447 | 119.9908 | 119.9848 | 120.1584 | 119.9034 | -2.3977 | 121.9827 | 122.1409 | 121.906 | 118.7531 | -122.4272
1573.0156 | 122.2229 | -120.0302 | 2.0782 | 1.4211e-13 | -0.0012351 | -0.01265 | -0.044957 | -0.039361 | -0.011497 | -0.00083919 | -0.015367 | 0.0093796 | 0.034496 | 0.0020385 | 0.037556 | -0.1592 | -0.1039 | -0.17323 | -0.034862 | -0.054588 | 0.16028 | -0.26453 | -119.7139 | -1.2817 | -119.8262 | 1.9617 | 2.1061 | 1.8712 | -120.326 | 119.7657 | -2.1131 | 119.871 | 119.857 | 0.091303 | -2.1328 | -1.918 | -0.29584 | -0.11656 | 0.31631 | 0.20397 | 0.4998 | 0.027881 | -0.20701 | 119.9954 | 119.9756 | 120.1905 | 119.9263 | -2.3428 | 121.9919 | 122.1363 | 121.9015 | 118.7485 | -122.4043
1574.7188 | 122.1771 | -119.9524 | 2.1286 | 1.4211e-13 | -0.0012351 | -0.01265 | -0.044743 | -0.039575 | -0.010856 | -0.00083919 | -0.015581 | 0.0095932 | 0.034282 | 0.0022521 | 0.037556 | -0.12715 | -0.085587 | -0.15949 | -0.01197 | -0.054588 | 0.18317 | -0.23706 | -119.6727 | -1.2954 | -119.8033 | 2.0029 | 2.1611 | 1.9262 | -120.2894 | 119.7153 | -2.1406 | 119.8252 | 119.7929 | 0.077563 | -2.1832 | -1.9454 | -0.33702 | -0.1257 | 0.2797 | 0.14904 | 0.48607 | 0.03247 | -0.20242 | 119.9404 | 119.8978 | 120.1356 | 119.8668 | -2.3657 | 121.9553 | 122.1135 | 121.8786 | 118.657 | -122.418
1576.5 | 122.1725 | -119.8608 | 2.2614 | 1.4211e-13 | -0.0014487 | -0.012863 | -0.044957 | -0.040002 | -0.010429 | -0.00083919 | -0.015794 | 0.0095932 | 0.033855 | 0.0022521 | 0.037342 | -0.11799 | -0.081008 | -0.14576 | -0.007391 | -0.063746 | 0.1786 | -0.2279 | -119.5353 | -1.3092 | -119.6523 | 2.1311 | 2.2984 | 2.0635 | -120.1475 | 119.6329 | -2.2687 | 119.7428 | 119.7151 | 0.082141 | -2.3251 | -2.0828 | -0.28664 | -0.13026 | 0.32551 | 0.20859 | 0.49522 | 0.037076 | -0.19781 | 119.8534 | 119.7971 | 120.0394 | 119.7798 | -2.4893 | 121.9919 | 122.1593 | 121.9244 | 118.5517 | -122.4088
1578.2812 | 122.2366 | -119.9982 | 2.0828 | 1.4211e-13 | -0.0012351 | -0.012863 | -0.04517 | -0.039575 | -0.010002 | -0.00083919 | -0.015794 | 0.010021 | 0.034496 | 0.0022521 | 0.037556 | -0.10883 | -0.071851 | -0.14118 | 0.001765 | -0.068325 | 0.18775 | -0.22332 | -119.7047 | -1.3229 | -119.8217 | 1.9754 | 2.1336 | 1.9124 | -120.3215 | 119.7748 | -2.0811 | 119.8893 | 119.857 | 0.08214 | -2.1512 | -1.8951 | -0.3233 | -0.1074 | 0.29343 | 0.1765 | 0.49981 | 0.050774 | -0.17038 | 119.9999 | 119.9298 | 120.1859 | 119.9263 | -2.3061 | 121.9736 | 122.1318 | 121.9106 | 118.6753 | -122.4043
1580.0469 | 122.1497 | -120.0531 | 2.0691 | 1.4211e-13 | -0.0014487 | -0.012436 | -0.044743 | -0.039575 | -0.0097878 | 0.0067908 | -0.015794 | 0.0093796 | 0.034068 | 0.0020385 | 0.03777 | -0.099677 | -0.062694 | -0.12287 | 0.006344 | -0.063746 | 0.19233 | -0.20042 | -119.746 | -1.3458 | -119.872 | 1.9434 | 2.097 | 1.8621 | -120.3581 | 119.8527 | -2.0627 | 119.9534 | 119.9302 | 0.077559 | -2.1328 | -1.8768 | -0.305 | -0.12572 | 0.30715 | 0.18107 | 0.48607 | 0.027879 | -0.20701 | 120.0594 | 119.9894 | 120.2454 | 119.9904 | -2.2695 | 121.9965 | 122.1501 | 121.9152 | 118.7073 | -122.4272
1581.7656 | 122.2458 | -120.0394 | 2.0737 | 1.4211e-13 | -0.0018761 | -0.01265 | -0.044957 | -0.039788 | -0.0097878 | -0.00083919 | -0.016008 | 0.0095932 | 0.034068 | 0.0020385 | 0.037556 | -0.095099 | -0.062694 | -0.12287 | 0.015501 | -0.068325 | 0.20149 | -0.205 | -119.7322 | -1.3504 | -119.8537 | 1.9617 | 2.1153 | 1.885 | -120.3535 | 119.8344 | -2.0582 | 119.9443 | 119.9165 | 0.082138 | -2.142 | -1.8722 | -0.31415 | -0.11198 | 0.30715 | 0.18565 | 0.4998 | 0.041616 | -0.18869 | 120.0549 | 119.971 | 120.2409 | 119.9767 | -2.2787 | 122.0011 | 122.1547 | 121.9243 | 118.689 | -122.4272
1583.5469 | 122.2137 | -120.2637 | 1.8951 | 1.4211e-13 | -0.0016625 | -0.012863 | -0.04517 | -0.039575 | -0.010002 | -0.0084697 | -0.015794 | 0.0095932 | 0.034282 | 0.0022521 | 0.037342 | -0.085942 | -0.067272 | -0.11829 | 0.010922 | -0.082062 | 0.19691 | -0.205 | -119.9291 | -1.3641 | -120.0414 | 1.774 | 1.923 | 1.6927 | -120.5458 | 120.0587 | -1.8842 | 120.1777 | 120.1454 | 0.086716 | -1.9772 | -1.6982 | -0.28216 | -0.12117 | 0.33457 | 0.22223 | 0.50439 | 0.027842 | -0.20247 | 120.2746 | 120.1816 | 120.4606 | 120.1964 | -2.1001 | 122.0376 | 122.1867 | 121.9563 | 118.8996 | -122.441
1585.3281 | 122.2641 | -120.0394 | 2.0782 | 1.4211e-13 | -0.0016625 | -0.012863 | -0.044743 | -0.039575 | -0.010429 | -0.0084697 | -0.016008 | 0.009807 | 0.034282 | 0.0022521 | 0.03777 | -0.085942 | -0.058115 | -0.12745 | 0.015501 | -0.072904 | 0.20149 | -0.20042 | -119.7505 | -1.3733 | -119.872 | 1.948 | 2.1015 | 1.8804 | -120.3673 | 119.8389 | -2.0627 | 119.9534 | 119.9119 | 0.07298 | -2.1512 | -1.8768 | -0.32789 | -0.13029 | 0.28884 | 0.16734 | 0.49523 | 0.023302 | -0.19785 | 120.0549 | 119.9665 | 120.2409 | 119.9813 | -2.2787 | 121.9873 | 122.1409 | 121.9198 | 118.6661 | -122.4455
1587.0469 | 122.2366 | -120.1126 | 2.005 | 1.4211e-13 | -0.0012351 | -0.012863 | -0.044743 | -0.039788 | -0.010215 | -0.0084697 | -0.015794 | 0.009807 | 0.034068 | 0.0018249 | 0.037342 | -0.072207 | -0.053537 | -0.10913 | 0.020079 | -0.063746 | 0.21064 | -0.19585 | -119.778 | -1.3916 | -119.9041 | 1.9296 | 2.0832 | 1.8667 | -120.3902 | 119.9168 | -1.9849 | 120.0404 | 120.0035 | 0.086714 | -2.0688 | -1.7944 | -0.27754 | -0.075363 | 0.33461 | 0.20853 | 0.48607 | 0.07823 | -0.13834 | 120.1327 | 120.0489 | 120.3233 | 120.0591 | -2.2009 | 122.0423 | 122.1958 | 121.9793 | 118.721 | -122.3952
1588.8125 | 122.2641 | -120.5521 | 1.5472 | 1.4211e-13 | -0.0016625 | -0.01265 | -0.04517 | -0.040002 | -0.010002 | -0.00083919 | -0.015794 | 0.009166 | 0.034282 | 0.0022521 | 0.03777 | -0.072207 | -0.044379 | -0.099975 | 0.020079 | -0.068325 | 0.21064 | -0.18669 | -120.2405 | -1.4053 | -120.3574 | 1.4764 | 1.6254 | 1.4088 | -120.848 | 120.3654 | -1.5272 | 120.4799 | 120.4521 | 0.086713 | -1.6156 | -1.3366 | -0.29597 | -0.07087 | 0.31161 | 0.19469 | 0.49066 | 0.078134 | -0.13844 | 120.5721 | 120.4837 | 120.7627 | 120.5077 | -1.7339 | 122.0284 | 122.1774 | 121.9609 | 119.1468 | -122.3953
1590.5312 | 122.3282 | -121.376 | 0.737 | 1.4211e-13 | -0.0014487 | -0.012863 | -0.044957 | -0.039788 | -0.0097878 | -0.0084697 | -0.015581 | 0.0095932 | 0.034496 | 0.0022521 | 0.03777 | -0.067628 | -0.048958 | -0.099975 | 0.020079 | -0.068325 | 0.21522 | -0.18211 | -121.0967 | -1.4419 | -121.2136 | 0.63393 | 0.77833 | 0.55718 | -121.718 | 121.1939 | -0.71692 | 121.3084 | 121.2761 | 0.082134 | -0.80532 | -0.52178 | -0.34197 | -0.10307 | 0.27937 | 0.16244 | 0.50442 | 0.041333 | -0.17982 | 121.3961 | 121.3077 | 121.5913 | 121.3271 | -0.91911 | 122.01 | 122.1544 | 121.9332 | 119.9341 | -122.455
1592.25 | 122.3282 | -121.3989 | 0.70496 | 1.4211e-13 | -0.0016625 | -0.01265 | -0.044743 | -0.039788 | -0.010002 | 0.0067908 | -0.015581 | 0.0093796 | 0.034496 | 0.0022521 | 0.03777 | -0.072207 | -0.044379 | -0.10455 | 0.020079 | -0.068325 | 0.21522 | -0.17753 | -121.1104 | -1.4511 | -121.2319 | 0.62477 | 0.77375 | 0.53887 | -121.7317 | 121.2214 | -0.68488 | 121.3267 | 121.2944 | 0.072977 | -0.77328 | -0.48973 | -0.33282 | -0.080186 | 0.28852 | 0.16702 | 0.49984 | 0.068799 | -0.16609 | 121.419 | 121.3306 | 121.6142 | 121.3545 | -0.88249 | 122.0237 | 122.1727 | 121.9378 | 119.9478 | -122.4367
1594.0156 | 122.3373 | -121.3989 | 0.70496 | 1.4211e-13 | -0.0016625 | -0.012863 | -0.045384 | -0.039788 | -0.010215 | -0.00083919 | -0.015581 | 0.0095932 | 0.034496 | 0.0022521 | 0.037983 | -0.06305 | -0.044379 | -0.10455 | 0.024657 | -0.063746 | 0.21064 | -0.18669 | -121.1241 | -1.4648 | -121.2365 | 0.61103 | 0.76002 | 0.5526 | -121.7409 | 121.2122 | -0.6803 | 121.3359 | 121.2944 | 0.082135 | -0.7687 | -0.49431 | -0.34198 | -0.093921 | 0.27478 | 0.16244 | 0.50442 | 0.055063 | -0.15235 | 121.4236 | 121.3352 | 121.6096 | 121.3545 | -0.89164 | 122.01 | 122.1589 | 121.9515 | 119.9341 | -122.4459
1595.7812 | 122.2916 | -121.431 | 0.72327 | 1.4211e-13 | -0.0016625 | -0.012863 | -0.045384 | -0.039575 | -0.010002 | 0.0067908 | -0.015794 | 0.0095932 | 0.034282 | 0.0024659 | 0.03777 | -0.067628 | -0.044379 | -0.099975 | 0.020079 | -0.068325 | 0.2198 | -0.18211 | -121.1333 | -1.474 | -121.2456 | 0.61103 | 0.7646 | 0.53887 | -121.7546 | 121.2489 | -0.70319 | 121.3633 | 121.331 | 0.082134 | -0.79159 | -0.50347 | -0.32367 | -0.11223 | 0.29767 | 0.18533 | 0.50899 | 0.04133 | -0.1844 | 121.451 | 121.3626 | 121.6508 | 121.3866 | -0.90538 | 122.042 | 122.1956 | 121.9698 | 119.957 | -122.4779
1597.5781 | 122.3419 | -121.3943 | 0.71869 | 1.4211e-13 | -0.0018761 | -0.01265 | -0.044743 | -0.039788 | -0.010215 | 0.0067908 | -0.016222 | 0.0093796 | 0.033855 | 0.0020385 | 0.037556 | -0.06305 | -0.039801 | -0.099975 | 0.015501 | -0.059167 | 0.2198 | -0.17753 | -121.1196 | -1.4831 | -121.2456 | 0.62019 | 0.77375 | 0.54345 | -121.7363 | 121.2168 | -0.70319 | 121.3313 | 121.2944 | 0.077555 | -0.77786 | -0.49889 | -0.34198 | -0.098497 | 0.27478 | 0.1487 | 0.49068 | 0.055066 | -0.17524 | 121.4098 | 121.3352 | 121.6141 | 121.3545 | -0.89622 | 122.0145 | 122.1681 | 121.9378 | 119.9112 | -122.455
1599.2969 | 122.3419 | -121.4127 | 0.70953 | 1.4211e-13 | -0.0018761 | -0.01265 | -0.044957 | -0.039361 | -0.010002 | -0.0084697 | -0.016008 | 0.0095932 | 0.034282 | 0.0020385 | 0.037556 | -0.06305 | -0.035222 | -0.090818 | 0.024657 | -0.059167 | 0.21522 | -0.17753 | -121.1333 | -1.5015 | -121.2548 | 0.61561 | 0.77375 | 0.54803 | -121.7638 | 121.2351 | -0.68488 | 121.3496 | 121.3218 | 0.086712 | -0.7687 | -0.49431 | -0.35114 | -0.093921 | 0.27936 | 0.15786 | 0.509 | 0.064221 | -0.16151 | 121.4373 | 121.3535 | 121.6279 | 121.3774 | -0.88706 | 122.0283 | 122.1864 | 121.9607 | 119.9112 | -122.4733
1601.0625 | 122.3557 | -121.3943 | 0.73242 | 1.4211e-13 | -0.0016625 | -0.012436 | -0.044743 | -0.039788 | -0.010002 | -0.00083919 | -0.015794 | 0.0095932 | 0.034282 | 0.0020385 | 0.038197 | -0.058472 | -0.048958 | -0.095397 | 0.020079 | -0.059167 | 0.2198 | -0.17295 | -121.1287 | -1.506 | -121.2456 | 0.62477 | 0.77375 | 0.56176 | -121.7501 | 121.2214 | -0.71234 | 121.3359 | 121.299 | 0.077554 | -0.79159 | -0.51262 | -0.35571 | -0.10765 | 0.26563 | 0.1487 | 0.50442 | 0.041333 | -0.17066 | 121.4144 | 121.3352 | 121.6141 | 121.3454 | -0.90537 | 122.0191 | 122.1681 | 121.9561 | 119.8883 | -122.4825
1602.8438 | 122.2733 | -121.3943 | 0.80109 | 1.4211e-13 | -0.0020897 | -0.01265 | -0.044957 | -0.039788 | -0.010002 | -0.00083919 | -0.015367 | 0.0095932 | 0.034068 | 0.0022521 | 0.037983 | -0.053893 | -0.035222 | -0.090818 | 0.033814 | -0.063746 | 0.2198 | -0.16837 | -121.1196 | -1.5244 | -121.2411 | 0.63851 | 0.79207 | 0.56634 | -121.7455 | 121.226 | -0.76727 | 121.3405 | 121.3035 | 0.077555 | -0.86483 | -0.58128 | -0.35113 | -0.16258 | 0.27478 | 0.15328 | 0.50442 | -0.009017 | -0.23475 | 121.4282 | 121.3306 | 121.6141 | 121.3591 | -0.96946 | 122.0329 | 122.1864 | 121.9607 | 119.87 | -122.5466
1604.625 | 122.3602 | -121.3623 | 0.80109 | 1.4211e-13 | -0.0018761 | -0.012863 | -0.044957 | -0.039575 | -0.010002 | 0.0067908 | -0.015581 | 0.0093796 | 0.034068 | 0.0024659 | 0.03777 | -0.058472 | -0.035222 | -0.08624 | 0.029236 | -0.059167 | 0.22438 | -0.16379 | -121.06 | -1.5427 | -121.177 | 0.70718 | 0.85159 | 0.62128 | -121.686 | 121.1985 | -0.77185 | 121.3038 | 121.2761 | 0.077554 | -0.86025 | -0.57671 | -0.32365 | -0.093903 | 0.30226 | 0.18534 | 0.50899 | 0.050505 | -0.1798 | 121.3915 | 121.3031 | 121.5867 | 121.3271 | -0.96488 | 122.0695 | 122.2139 | 121.9836 | 119.8196 | -122.487
1606.4062 | 122.2733 | -121.4813 | 0.71869 | 1.4211e-13 | -0.0023035 | -0.01265 | -0.044957 | -0.039788 | -0.010002 | -0.00083919 | -0.015581 | 0.009166 | 0.034282 | 0.0024659 | 0.037342 | -0.053893 | -0.026065 | -0.077084 | 0.033814 | -0.054588 | 0.22438 | -0.16379 | -121.1562 | -1.5472 | -121.2731 | 0.61103 | 0.75544 | 0.53429 | -121.7821 | 121.3175 | -0.68488 | 121.4274 | 121.4042 | 0.08671 | -0.77328 | -0.49431 | -0.30079 | -0.10765 | 0.32513 | 0.20821 | 0.509 | 0.036751 | -0.1844 | 121.5151 | 121.4267 | 121.7057 | 121.4553 | -0.88248 | 122.0924 | 122.2368 | 122.0156 | 119.9341 | -122.5008
1608.1875 | 122.3648 | -121.4493 | 0.70496 | 1.4211e-13 | -0.0020897 | -0.013077 | -0.044743 | -0.040216 | -0.010002 | -0.0161 | -0.015581 | 0.0095932 | 0.034282 | 0.0020385 | 0.037983 | -0.058472 | -0.021486 | -0.08624 | 0.033814 | -0.059167 | 0.23354 | -0.16837 | -121.1608 | -1.5701 | -121.2823 | 0.61103 | 0.75544 | 0.56176 | -121.7867 | 121.2809 | -0.67114 | 121.3908 | 121.363 | 0.082133 | -0.76412 | -0.47142 | -0.33741 | -0.093921 | 0.28851 | 0.16701 | 0.50442 | 0.050484 | -0.14319 | 121.4831 | 121.3901 | 121.6828 | 121.4278 | -0.87333 | 122.0603 | 122.2047 | 122.011 | 119.8791 | -122.4916
1609.9062 | 122.2778 | -121.4951 | 0.71869 | 1.4211e-13 | -0.0020897 | -0.012863 | -0.04517 | -0.039361 | -0.010215 | -0.0084697 | -0.015581 | 0.0095932 | 0.034496 | 0.0022521 | 0.03777 | -0.040158 | -0.012329 | -0.077084 | 0.042971 | -0.031693 | 0.24727 | -0.15464 | -121.1837 | -1.5747 | -121.3052 | 0.58814 | 0.73713 | 0.51598 | -121.8142 | 121.3404 | -0.67572 | 121.4549 | 121.418 | 0.077552 | -0.75038 | -0.47142 | -0.31911 | -0.13055 | 0.31139 | 0.18989 | 0.509 | 0.018437 | -0.20271 | 121.538 | 121.4634 | 121.7423 | 121.4827 | -0.87333 | 122.0832 | 122.2322 | 122.011 | 119.9203 | -122.5329
1611.6875 | 122.2412 | -121.5363 | 0.70953 | 1.4211e-13 | -0.0016625 | -0.012436 | -0.044957 | -0.039575 | -0.010002 | -0.00083919 | -0.015794 | 0.009807 | 0.034496 | 0.0026795 | 0.037556 | -0.044736 | -0.026065 | -0.077084 | 0.042971 | -0.022536 | 0.23812 | -0.15921 | -121.202 | -1.6022 | -121.3143 | 0.57899 | 0.72797 | 0.54345 | -121.8187 | 121.377 | -0.66656 | 121.4915 | 121.4592 | 0.082131 | -0.73207 | -0.47142 | -0.28249 | -0.13055 | 0.33427 | 0.22193 | 0.50442 | 0.018434 | -0.16609 | 121.5792 | 121.5137 | 121.7744 | 121.5102 | -0.86875 | 122.1152 | 122.2642 | 122.0797 | 119.9341 | -122.5283
1613.4688 | 122.3648 | -121.5042 | 0.69122 | 1.4211e-13 | -0.0018761 | -0.012863 | -0.044957 | -0.039788 | -0.010002 | -0.0084697 | -0.015581 | 0.0095932 | 0.034496 | 0.0022521 | 0.037983 | -0.049315 | -0.026065 | -0.077084 | 0.038393 | -0.054588 | 0.22896 | -0.15464 | -121.2203 | -1.6068 | -121.3372 | 0.56983 | 0.71881 | 0.51598 | -121.8416 | 121.3496 | -0.65283 | 121.4549 | 121.4271 | 0.077552 | -0.74581 | -0.46226 | -0.33743 | -0.12139 | 0.28391 | 0.16699 | 0.50442 | 0.027588 | -0.17525 | 121.5426 | 121.4496 | 121.7332 | 121.4781 | -0.84586 | 122.074 | 122.223 | 122.0202 | 119.8974 | -122.5329
1615.1875 | 122.3465 | -121.5317 | 0.6546 | 1.4211e-13 | -0.0018761 | -0.012863 | -0.04517 | -0.039575 | -0.010002 | 0.0067908 | -0.015581 | 0.0095932 | 0.034282 | 0.0024659 | 0.037556 | -0.049315 | -0.016908 | -0.077084 | 0.038393 | -0.050009 | 0.23812 | -0.16379 | -121.2295 | -1.6297 | -121.351 | 0.56067 | 0.71881 | 0.4885 | -121.8554 | 121.3679 | -0.61621 | 121.4824 | 121.4546 | 0.08671 | -0.70461 | -0.41648 | -0.3237 | -0.09393 | 0.30222 | 0.18072 | 0.50442 | 0.064209 | -0.1661 | 121.5701 | 121.4817 | 121.7698 | 121.5148 | -0.8184 | 122.0923 | 122.2505 | 122.0202 | 119.902 | -122.51
1616.9531 | 122.406 | -121.5225 | 0.66376 | 1.4211e-13 | -0.0020897 | -0.01265 | -0.04517 | -0.039788 | -0.0097878 | -0.00083919 | -0.015581 | 0.0095932 | 0.034282 | 0.0024659 | 0.03777 | -0.044736 | -0.030644 | -0.077084 | 0.047549 | -0.008799 | 0.24269 | -0.15921 | -121.2157 | -1.6388 | -121.3418 | 0.57441 | 0.72797 | 0.49766 | -121.8508 | 121.3633 | -0.61621 | 121.4778 | 121.4454 | 0.082131 | -0.67256 | -0.42106 | -0.32827 | -0.08935 | 0.3068 | 0.18073 | 0.509 | 0.064211 | -0.1661 | 121.5701 | 121.5137 | 121.7652 | 121.4919 | -0.82297 | 122.0969 | 122.2505 | 122.0202 | 119.8837 | -122.5146
1618.7344 | 122.2961 | -121.5408 | 0.6958 | 1.4211e-13 | -0.0020897 | -0.012436 | -0.04517 | -0.039575 | -0.010002 | -0.00083919 | -0.015794 | 0.0093796 | 0.034496 | 0.0024659 | 0.037556 | -0.044736 | -0.035222 | -0.072505 | 0.056706 | -0.059167 | 0.23354 | -0.1409 | -121.234 | -1.6526 | -121.3418 | 0.56525 | 0.71881 | 0.50224 | -121.86 | 121.3999 | -0.63909 | 121.4961 | 121.4683 | 0.068394 | -0.75497 | -0.46226 | -0.31912 | -0.13055 | 0.3068 | 0.19904 | 0.51816 | 0.02301 | -0.19356 | 121.5975 | 121.4817 | 121.7744 | 121.5056 | -0.8367 | 122.1061 | 122.2596 | 122.0431 | 119.8883 | -122.5558
1620.5312 | 122.3923 | -121.5134 | 0.6546 | 1.4211e-13 | -0.0020897 | -0.013077 | -0.04517 | -0.039788 | -0.010002 | 0.0067908 | -0.015794 | 0.009166 | 0.034496 | 0.0026795 | 0.037342 | -0.031001 | -0.030644 | -0.072505 | 0.056706 | -0.017957 | 0.24727 | -0.15464 | -121.2432 | -1.6709 | -121.3693 | 0.55151 | 0.7005 | 0.47477 | -121.8828 | 121.3587 | -0.5979 | 121.4824 | 121.4409 | 0.082131 | -0.67256 | -0.40733 | -0.36948 | -0.10309 | 0.27018 | 0.1441 | 0.51358 | 0.045895 | -0.17983 | 121.5701 | 121.4954 | 121.7606 | 121.4827 | -0.80924 | 122.0649 | 122.2139 | 121.9881 | 119.8425 | -122.5374
1622.2812 | 122.3557 | -121.5775 | 0.62714 | 1.4211e-13 | -0.0023035 | -0.01265 | -0.045384 | -0.039788 | -0.010643 | -0.0084697 | -0.016008 | 0.0093796 | 0.034496 | 0.0022521 | 0.03777 | -0.040158 | -0.030644 | -0.067927 | 0.052128 | -0.050009 | 0.25185 | -0.15006 | -121.2523 | -1.68 | -121.3738 | 0.55151 | 0.69592 | 0.47935 | -121.8828 | 121.4274 | -0.57501 | 121.5373 | 121.5095 | 0.08213 | -0.67714 | -0.37528 | -0.30539 | -0.075621 | 0.32511 | 0.20361 | 0.509 | 0.068782 | -0.14779 | 121.6296 | 121.5274 | 121.8293 | 121.5468 | -0.77719 | 122.129 | 122.2734 | 122.0568 | 119.8974 | -122.51
1624.0625 | 122.2961 | -121.5866 | 0.68207 | 1.4211e-13 | -0.0025171 | -0.01265 | -0.04517 | -0.039575 | -0.010002 | -0.00083919 | -0.015794 | 0.009166 | 0.034068 | 0.0022521 | 0.03777 | -0.031001 | -0.030644 | -0.072505 | 0.052128 | 0.009517 | 0.25185 | -0.13632 | -121.2523 | -1.7029 | -121.3693 | 0.55609 | 0.70965 | 0.49308 | -121.8783 | 121.4503 | -0.62994 | 121.5556 | 121.5141 | 0.063815 | -0.67255 | -0.43022 | -0.29166 | -0.12598 | 0.33426 | 0.21734 | 0.509 | 0.027586 | -0.18899 | 121.6387 | 121.5961 | 121.8385 | 121.556 | -0.81839 | 122.1427 | 122.2963 | 122.0797 | 119.8837 | -122.5603
1625.8281 | 122.3373 | -121.6049 | 0.66834 | 1.4211e-13 | -0.0023035 | -0.01265 | -0.04517 | -0.039788 | -0.010215 | 0.0067908 | -0.015794 | 0.0095932 | 0.034282 | 0.0024659 | 0.037983 | -0.03558 | -0.035222 | -0.067927 | 0.061284 | -0.013378 | 0.24727 | -0.1409 | -121.2661 | -1.7167 | -121.383 | 0.54694 | 0.7005 | 0.46561 | -121.8966 | 121.464 | -0.60705 | 121.5693 | 121.537 | 0.072972 | -0.68171 | -0.42106 | -0.29166 | -0.1214 | 0.33884 | 0.22191 | 0.51358 | 0.032162 | -0.20272 | 121.6662 | 121.5915 | 121.8522 | 121.5697 | -0.80923 | 122.1519 | 122.3054 | 122.0705 | 119.8883 | -122.5649
1627.6094 | 122.3053 | -121.5775 | 0.68207 | 1.4211e-13 | -0.0023035 | -0.012436 | -0.044957 | -0.039788 | -0.0097878 | -0.00083919 | -0.015794 | 0.0093796 | 0.034282 | 0.0024659 | 0.037983 | -0.03558 | -0.016908 | -0.05877 | 0.056706 | 0.009517 | 0.25185 | -0.13632 | -121.2249 | -1.735 | -121.3464 | 0.59272 | 0.7417 | 0.52055 | -121.8508 | 121.4411 | -0.62536 | 121.5419 | 121.5187 | 0.07755 | -0.67255 | -0.43022 | -0.27334 | -0.089347 | 0.35258 | 0.23108 | 0.50442 | 0.059636 | -0.16151 | 121.6342 | 121.587 | 121.8293 | 121.5605 | -0.81839 | 122.1702 | 122.3192 | 122.098 | 119.8425 | -122.5329
1629.3906 | 122.4472 | -121.5042 | 0.6958 | 1.4211e-13 | -0.0020897 | -0.012863 | -0.04517 | -0.039788 | -0.0097878 | -0.00083919 | -0.015794 | 0.0093796 | 0.034496 | 0.0020385 | 0.037556 | -0.031001 | -0.026065 | -0.05877 | 0.056706 | 0.009517 | 0.25643 | -0.13632 | -121.2157 | -1.7487 | -121.3372 | 0.60646 | 0.76002 | 0.54345 | -121.8462 | 121.3679 | -0.63909 | 121.4732 | 121.4454 | 0.07755 | -0.68628 | -0.43937 | -0.34201 | -0.089345 | 0.28849 | 0.16699 | 0.509 | 0.064218 | -0.15235 | 121.5609 | 121.5137 | 121.7606 | 121.4781 | -0.83212 | 122.1107 | 122.2642 | 122.0477 | 119.7555 | -122.542
1631.1562 | 122.374 | -121.5225 | 0.71869 | 1.4211e-13 | -0.0029445 | -0.012863 | -0.045384 | -0.039788 | -0.010002 | 0.014421 | -0.016222 | 0.009166 | 0.034282 | 0.0026795 | 0.037556 | -0.026423 | -0.021486 | -0.054192 | 0.056706 | 0.014096 | 0.25643 | -0.13632 | -121.2249 | -1.7624 | -121.3418 | 0.5973 | 0.75086 | 0.52513 | -121.8554 | 121.3862 | -0.66198 | 121.4961 | 121.4683 | 0.082128 | -0.70459 | -0.46226 | -0.33285 | -0.12139 | 0.29765 | 0.18073 | 0.51358 | 0.032173 | -0.19356 | 121.5792 | 121.5366 | 121.779 | 121.501 | -0.85501 | 122.1198 | 122.2734 | 122.0477 | 119.7601 | -122.5741
1632.9375 | 122.4472 | -121.5042 | 0.70038 | 1.4211e-13 | -0.0027309 | -0.01265 | -0.04517 | -0.039788 | -0.010215 | 0.014421 | -0.015581 | 0.0095932 | 0.034068 | 0.0024659 | 0.037556 | -0.017266 | -0.016908 | -0.054192 | 0.061284 | 0.014096 | 0.25643 | -0.10885 | -121.234 | -1.7808 | -121.3555 | 0.5973 | 0.74628 | 0.57092 | -121.8645 | 121.3954 | -0.63909 | 121.4869 | 121.45 | 0.054655 | -0.68628 | -0.44395 | -0.36032 | -0.10308 | 0.27018 | 0.14868 | 0.509 | 0.045905 | -0.12946 | 121.5655 | 121.5183 | 121.7606 | 121.4873 | -0.80922 | 122.1015 | 122.2505 | 122.0751 | 119.7235 | -122.5649
1634.7188 | 122.3282 | -121.5454 | 0.71869 | 1.4211e-13 | -0.0023035 | -0.01265 | -0.04517 | -0.039575 | -0.0097878 | 0.014421 | -0.015794 | 0.0095932 | 0.034709 | 0.0026795 | 0.037556 | -0.021844 | -0.016908 | -0.05877 | 0.056706 | 0.014096 | 0.25643 | -0.13174 | -121.2295 | -1.7991 | -121.3555 | 0.60188 | 0.75086 | 0.56176 | -121.8645 | 121.4137 | -0.66198 | 121.5236 | 121.4866 | 0.072971 | -0.70459 | -0.46226 | -0.31912 | -0.11681 | 0.31596 | 0.18988 | 0.509 | 0.032173 | -0.15693 | 121.6021 | 121.5595 | 121.8018 | 121.5285 | -0.85043 | 122.1473 | 122.2963 | 122.1072 | 119.7463 | -122.5832
1636.5 | 122.4472 | -121.5271 | 0.70953 | 1.4211e-13 | -0.0025171 | -0.01265 | -0.04517 | -0.039575 | -0.010215 | 0.0067908 | -0.016008 | 0.0095932 | 0.034282 | 0.0026795 | 0.037556 | -0.021844 | -0.026065 | -0.054192 | 0.056706 | 0.03699 | 0.26559 | -0.13174 | -121.2203 | -1.8128 | -121.3372 | 0.61103 | 0.76002 | 0.54345 | -121.8554 | 121.3954 | -0.65283 | 121.5053 | 121.4729 | 0.077549 | -0.67254 | -0.44395 | -0.32827 | -0.098499 | 0.3068 | 0.18988 | 0.51816 | 0.050485 | -0.16609 | 121.5838 | 121.5641 | 121.7927 | 121.501 | -0.84127 | 122.1381 | 122.2871 | 122.0705 | 119.7143 | -122.5649
1638.2188 | 122.3328 | -121.6141 | 0.6958 | 1.4211e-13 | -0.0023035 | -0.012863 | -0.044957 | -0.039788 | -0.010002 | -0.00083919 | -0.015794 | 0.009166 | 0.034709 | 0.0024659 | 0.037556 | -0.017266 | -0.012329 | -0.049614 | 0.065863 | 0.018675 | 0.25643 | -0.13174 | -121.2844 | -1.8311 | -121.4059 | 0.55151 | 0.7005 | 0.5114 | -121.9241 | 121.4823 | -0.62994 | 121.5968 | 121.5645 | 0.082127 | -0.67713 | -0.43937 | -0.30998 | -0.14429 | 0.32968 | 0.20818 | 0.51816 | 0.004696 | -0.1844 | 121.6799 | 121.6328 | 121.8705 | 121.6017 | -0.82754 | 122.1656 | 122.3146 | 122.1255 | 119.7829 | -122.6199
1640 | 122.4564 | -121.6415 | 0.62714 | 1.4211e-13 | -0.0029445 | -0.01265 | -0.044743 | -0.039788 | -0.010215 | -0.00083919 | -0.016008 | 0.0093796 | 0.034068 | 0.0026795 | 0.03777 | -0.021844 | -0.021486 | -0.049614 | 0.065863 | 0.023254 | 0.26101 | -0.13174 | -121.3119 | -1.8494 | -121.4334 | 0.5332 | 0.68218 | 0.47935 | -121.9424 | 121.5098 | -0.56127 | 121.6197 | 121.5919 | 0.082127 | -0.60388 | -0.36613 | -0.30083 | -0.093935 | 0.32967 | 0.20817 | 0.509 | 0.055046 | -0.14779 | 121.7074 | 121.6648 | 121.9026 | 121.6201 | -0.75888 | 122.1747 | 122.3237 | 122.1209 | 119.7921 | -122.5695
1641.7344 | 122.4106 | -121.6278 | 0.63629 | 1.4211e-13 | -0.0025171 | -0.013077 | -0.045384 | -0.040002 | -0.010429 | 0.0067908 | -0.015794 | 0.0095932 | 0.034282 | 0.0024659 | 0.03777 | -0.012688 | -0.012329 | -0.049614 | 0.079598 | 0.041569 | 0.26101 | -0.118 | -121.3302 | -1.8678 | -121.4379 | 0.52404 | 0.66845 | 0.46561 | -121.9653 | 121.5098 | -0.55669 | 121.6151 | 121.5782 | 0.06839 | -0.59472 | -0.37528 | -0.33746 | -0.11225 | 0.29762 | 0.18986 | 0.52732 | 0.032155 | -0.17068 | 121.7074 | 121.6694 | 121.8888 | 121.6155 | -0.7543 | 122.1519 | 122.2963 | 122.0934 | 119.7601 | -122.6016
1643.5312 | 122.3053 | -121.6553 | 0.67291 | 1.4211e-13 | -0.0029445 | -0.012863 | -0.045598 | -0.039788 | -0.010002 | 0.0067908 | -0.015794 | 0.0095932 | 0.034282 | 0.0022521 | 0.037983 | -0.021844 | -0.012329 | -0.054192 | 0.070441 | 0.03699 | 0.27017 | -0.12258 | -121.3256 | -1.8861 | -121.4471 | 0.52404 | 0.68676 | 0.46103 | -121.9561 | 121.5327 | -0.60247 | 121.6334 | 121.6011 | 0.068391 | -0.63592 | -0.40275 | -0.30083 | -0.14887 | 0.32967 | 0.20817 | 0.509 | 0.013848 | -0.21188 | 121.7257 | 121.6923 | 121.9254 | 121.6429 | -0.7955 | 122.1793 | 122.342 | 122.1163 | 119.7692 | -122.629
1645.2656 | 122.406 | -121.6278 | 0.61798 | 1.4211e-13 | -0.0025171 | -0.013291 | -0.04517 | -0.040002 | -0.010215 | -0.00083919 | -0.015367 | 0.009807 | 0.034282 | 0.0024659 | 0.037556 | -0.017266 | -0.012329 | -0.040457 | 0.065863 | 0.041569 | 0.26559 | -0.11342 | -121.3256 | -1.909 | -121.4517 | 0.52404 | 0.69134 | 0.4473 | -121.9653 | 121.5144 | -0.55212 | 121.6105 | 121.5874 | 0.072968 | -0.57641 | -0.35239 | -0.33746 | -0.093937 | 0.3022 | 0.17612 | 0.51358 | 0.073359 | -0.17068 | 121.6937 | 121.6694 | 121.8934 | 121.6155 | -0.73141 | 122.1519 | 122.3191 | 122.0751 | 119.7188 | -122.5832
1647.0469 | 122.3831 | -121.6553 | 0.65918 | 1.4211e-13 | -0.0029445 | -0.013077 | -0.045384 | -0.039575 | -0.010215 | 0.0067908 | -0.015581 | 0.0095932 | 0.034282 | 0.0024659 | 0.037556 | -0.012688 | -0.003172 | -0.045036 | 0.07502 | 0.041569 | 0.26101 | -0.12716 | -121.3348 | -1.9181 | -121.4608 | 0.52404 | 0.68218 | 0.4473 | -121.9744 | 121.5281 | -0.58416 | 121.6426 | 121.6102 | 0.082126 | -0.61761 | -0.39817 | -0.31915 | -0.13514 | 0.32051 | 0.19443 | 0.51358 | 0.023002 | -0.21188 | 121.7303 | 121.6968 | 121.9163 | 121.6521 | -0.78634 | 122.1793 | 122.3375 | 122.1026 | 119.7372 | -122.6336
1648.7812 | 122.4701 | -121.5729 | 0.64545 | 1.4211e-13 | -0.0027309 | -0.01265 | -0.044743 | -0.040002 | -0.010215 | 0.0067908 | -0.015794 | 0.009166 | 0.034496 | 0.0024659 | 0.03777 | -0.017266 | -0.012329 | -0.040457 | 0.065863 | 0.03699 | 0.26101 | -0.11342 | -121.3027 | -1.9364 | -121.4196 | 0.55609 | 0.70508 | 0.4885 | -121.9424 | 121.4595 | -0.57958 | 121.5556 | 121.5324 | 0.072968 | -0.60846 | -0.38444 | -0.3695 | -0.089354 | 0.27016 | 0.15324 | 0.52274 | 0.059628 | -0.15694 | 121.6387 | 121.6099 | 121.8339 | 121.5605 | -0.75887 | 122.129 | 122.278 | 122.0614 | 119.6364 | -122.5878
1650.5156 | 122.4564 | -121.5958 | 0.64545 | 1.4211e-13 | -0.0027309 | -0.012863 | -0.044743 | -0.040216 | -0.010429 | 0.0067908 | -0.016008 | 0.0093796 | 0.034923 | 0.0026795 | 0.03777 | -0.021844 | -0.012329 | -0.045036 | 0.070441 | 0.041569 | 0.26101 | -0.09511 | -121.3119 | -1.9547 | -121.4334 | 0.55609 | 0.7005 | 0.48392 | -121.947 | 121.5007 | -0.57501 | 121.5739 | 121.5507 | 0.050074 | -0.60388 | -0.38444 | -0.35119 | -0.089354 | 0.28389 | 0.16239 | 0.51358 | 0.05505 | -0.16152 | 121.6662 | 121.6373 | 121.8568 | 121.5834 | -0.74056 | 122.1519 | 122.2963 | 122.0797 | 119.641 | -122.5924
1652.2969 | 122.4289 | -121.6049 | 0.67291 | 1.4211e-13 | -0.0027309 | -0.012863 | -0.04517 | -0.039788 | -0.010002 | -0.0084697 | -0.015794 | 0.009807 | 0.034068 | 0.0028931 | 0.037983 | -0.008109 | -0.003172 | -0.049614 | 0.07502 | 0.03699 | 0.27017 | -0.085952 | -121.3027 | -1.9731 | -121.4242 | 0.55609 | 0.71423 | 0.49766 | -121.9424 | 121.519 | -0.59789 | 121.5968 | 121.5553 | 0.036338 | -0.63592 | -0.40275 | -0.33745 | -0.11682 | 0.30221 | 0.18071 | 0.51816 | 0.04132 | -0.17525 | 121.6799 | 121.6419 | 121.8751 | 121.6017 | -0.75887 | 122.161 | 122.3192 | 122.1026 | 119.6319 | -122.6153
1654.0156 | 122.3511 | -121.6232 | 0.71869 | 1.4211e-13 | -0.0029445 | -0.013077 | -0.044957 | -0.040002 | -0.010429 | -0.00083919 | -0.015794 | 0.0093796 | 0.034282 | 0.0026795 | 0.037342 | -0.017266 | -0.012329 | -0.045036 | 0.070441 | 0.041569 | 0.26559 | -0.090531 | -121.2936 | -1.9731 | -121.4151 | 0.58356 | 0.71881 | 0.49308 | -121.9332 | 121.5327 | -0.64825 | 121.606 | 121.5782 | 0.045495 | -0.67712 | -0.4531 | -0.30998 | -0.13513 | 0.32968 | 0.20817 | 0.51816 | 0.000122 | -0.22561 | 121.6937 | 121.6648 | 121.8888 | 121.6109 | -0.80922 | 122.2068 | 122.342 | 122.1163 | 119.6502 | -122.6519
1655.7969 | 122.3969 | -120.9183 | 1.4008 | 1.4211e-13 | -0.0031581 | -0.012863 | -0.044957 | -0.039788 | -0.010429 | -0.0084697 | -0.015794 | 0.0095932 | 0.034496 | 0.0024659 | 0.037556 | -0.012688 | -0.007751 | -0.045036 | 0.070441 | 0.046148 | 0.27017 | -0.085952 | -120.6113 | -1.9822 | -120.7328 | 1.2612 | 1.4148 | 1.2302 | -121.2418 | 120.8323 | -1.3303 | 120.9056 | 120.8732 | 0.040916 | -1.3546 | -1.1306 | -0.32354 | -0.13958 | 0.30695 | 0.18545 | 0.50898 | 0.014002 | -0.17052 | 120.9887 | 120.9644 | 121.1884 | 120.9105 | -1.4867 | 122.1795 | 122.333 | 122.1485 | 118.9361 | -122.6426
1657.5938 | 122.438 | -120.9732 | 1.3138 | 1.4211e-13 | -0.0027309 | -0.01265 | -0.04517 | -0.039788 | -0.010429 | -0.0084697 | -0.016008 | 0.0095932 | 0.034282 | 0.0022521 | 0.03777 | -0.012688 | -0.012329 | -0.045036 | 0.079598 | 0.046148 | 0.26101 | -0.09511 | -120.6663 | -2.0051 | -120.7786 | 1.2062 | 1.3644 | 1.2073 | -121.3013 | 120.8781 | -1.2342 | 120.9605 | 120.9282 | 0.050074 | -1.2676 | -1.0528 | -0.32813 | -0.10754 | 0.30693 | 0.19459 | 0.52272 | 0.050612 | -0.10644 | 121.0528 | 121.0194 | 121.2342 | 120.9609 | -1.4089 | 122.1794 | 122.3376 | 122.1806 | 118.9681 | -122.6151
1659.3125 | 122.3511 | -121.019 | 1.3184 | 1.4211e-13 | -0.0027309 | -0.012863 | -0.044957 | -0.039575 | -0.010215 | -0.00083919 | -0.016008 | 0.009166 | 0.034496 | 0.0024659 | 0.037556 | -0.012688 | -0.012329 | -0.045036 | 0.079598 | 0.041569 | 0.27017 | -0.040163 | -120.6983 | -2.0189 | -120.8152 | 1.1788 | 1.3278 | 1.1158 | -121.338 | 120.9788 | -1.2388 | 121.0063 | 120.9739 | -0.004873 | -1.2768 | -1.0482 | -0.31899 | -0.13959 | 0.32066 | 0.20374 | 0.52272 | 0.009406 | -0.20259 | 121.0986 | 121.0606 | 121.2891 | 121.0067 | -1.3585 | 122.1977 | 122.3467 | 122.1348 | 119.0001 | -122.6563
1661.0938 | 122.438 | -120.9869 | 1.3 | 1.4211e-13 | -0.0023035 | -0.013077 | -0.044957 | -0.040002 | -0.010215 | 0.0067908 | -0.015581 | 0.009166 | 0.034282 | 0.0028931 | 0.03777 | -0.012688 | -0.007751 | -0.040457 | 0.070441 | 0.050727 | 0.23812 | -0.11342 | -120.7029 | -2.028 | -120.8198 | 1.1788 | 1.3323 | 1.1341 | -121.3471 | 120.8735 | -1.2296 | 120.9742 | 120.9465 | 0.072968 | -1.2493 | -1.0619 | -0.36019 | -0.12128 | 0.28404 | 0.16711 | 0.5273 | 0.032295 | -0.16596 | 121.0574 | 121.0377 | 121.2251 | 120.9792 | -1.4135 | 122.1657 | 122.3193 | 122.121 | 118.9589 | -122.6472
1662.875 | 122.4243 | -121.051 | 1.2726 | 1.4211e-13 | -0.0025171 | -0.01265 | -0.044957 | -0.039788 | -0.010429 | -0.0084697 | -0.015794 | 0.009166 | 0.034496 | 0.0026795 | 0.037556 | -0.021844 | -0.012329 | -0.035879 | 0.070441 | 0.041569 | 0.23812 | -0.081373 | -120.7304 | -2.0555 | -120.8473 | 1.1605 | 1.3049 | 1.1249 | -121.3654 | 120.9697 | -1.2021 | 121.0292 | 121.0151 | 0.045494 | -1.231 | -1.0345 | -0.31442 | -0.11213 | 0.32065 | 0.20373 | 0.51814 | 0.032289 | -0.14765 | 121.1215 | 121.0926 | 121.2891 | 121.0387 | -1.354 | 122.2115 | 122.3559 | 122.176 | 118.9955 | -122.638
1664.5938 | 122.3877 | -122.0123 | 0.33875 | 1.4211e-13 | -0.0025171 | -0.012863 | -0.044957 | -0.039788 | -0.010002 | -0.0084697 | -0.015794 | 0.0093796 | 0.034496 | 0.0028931 | 0.03777 | -0.012688 | -0.016908 | -0.045036 | 0.07502 | 0.041569 | 0.24727 | -0.067636 | -121.6782 | -2.0967 | -121.7997 | 0.21271 | 0.36626 | 0.19547 | -122.3224 | 121.9447 | -0.26372 | 121.9996 | 121.9673 | 0.0226 | -0.29718 | -0.091471 | -0.31008 | -0.12604 | 0.33416 | 0.21266 | 0.52275 | 0.027514 | -0.14327 | 122.0873 | 122.0539 | 122.2596 | 121.9954 | -0.40638 | 122.225 | 122.3786 | 122.2078 | 119.9156 | -122.6612
1666.3125 | 122.3877 | -122.0306 | 0.37537 | 1.4211e-13 | -0.0029445 | -0.012863 | -0.044743 | -0.039575 | -0.010002 | -0.0084697 | -0.015794 | 0.0093796 | 0.034282 | 0.0022521 | 0.037983 | -0.026423 | -0.007751 | -0.049614 | 0.079598 | 0.027833 | 0.23354 | -0.072215 | -121.6782 | -2.1104 | -121.7951 | 0.22186 | 0.37084 | 0.20005 | -122.3224 | 121.9584 | -0.29577 | 122.0042 | 121.981 | 0.022601 | -0.34753 | -0.14183 | -0.29177 | -0.1535 | 0.35247 | 0.23555 | 0.52732 | -0.004528 | -0.17531 | 122.1102 | 122.0585 | 122.2642 | 122.0229 | -0.44758 | 122.2525 | 122.4015 | 122.2307 | 119.9202 | -122.6978
1668.0938 | 122.4243 | -121.9391 | 0.40283 | 1.4211e-13 | -0.0027309 | -0.012863 | -0.044743 | -0.040002 | -0.0095742 | -0.00083919 | -0.015794 | 0.0093796 | 0.034282 | 0.0026795 | 0.03777 | -0.012688 | -0.012329 | -0.040457 | 0.07502 | 0.046148 | 0.23812 | -0.058478 | -121.6141 | -2.1287 | -121.7401 | 0.28138 | 0.43036 | 0.24126 | -122.2675 | 121.8806 | -0.32781 | 121.9264 | 121.8986 | 0.018021 | -0.35668 | -0.16472 | -0.32838 | -0.12145 | 0.32502 | 0.19894 | 0.52732 | 0.027527 | -0.16157 | 122.0141 | 121.9852 | 122.1772 | 121.9268 | -0.46131 | 122.2205 | 122.3694 | 122.1803 | 119.8103 | -122.6703
1669.875 | 122.3648 | -121.8521 | 0.53101 | 1.4211e-13 | -0.0029445 | -0.01265 | -0.044957 | -0.040002 | -0.010002 | 0.0067908 | -0.015367 | 0.0093796 | 0.034282 | 0.0028931 | 0.03777 | -0.003531 | -0.003172 | -0.035879 | 0.088755 | 0.050727 | 0.24269 | -0.076794 | -121.5133 | -2.1425 | -121.6394 | 0.38669 | 0.54025 | 0.37862 | -122.153 | 121.7753 | -0.44225 | 121.8486 | 121.8162 | 0.040915 | -0.48028 | -0.28831 | -0.30088 | -0.14432 | 0.33878 | 0.2127 | 0.51358 | 0.00924 | -0.15239 | 121.9409 | 121.9028 | 122.0948 | 121.8489 | -0.6078 | 122.2388 | 122.3924 | 122.2307 | 119.7096 | -122.684
1671.6562 | 122.5067 | -121.9757 | 0.31586 | 1.4211e-13 | -0.0027309 | -0.012863 | -0.044957 | -0.039575 | -0.010002 | -0.0084697 | -0.015794 | 0.009807 | 0.034068 | 0.0026795 | 0.03777 | -0.008109 | -0.003172 | -0.035879 | 0.07502 | 0.050727 | 0.24269 | -0.044742 | -121.6827 | -2.1745 | -121.8042 | 0.23102 | 0.38 | 0.20921 | -122.327 | 121.931 | -0.24084 | 121.9676 | 121.9398 | 0.008863 | -0.26513 | -0.073162 | -0.35128 | -0.084837 | 0.29296 | 0.17146 | 0.52275 | 0.064138 | -0.10665 | 122.0507 | 122.0264 | 122.2184 | 121.9725 | -0.3606 | 122.2067 | 122.3557 | 122.1849 | 119.8012 | -122.6428
1673.3906 | 122.5204 | -121.8063 | 0.4715 | 1.4211e-13 | -0.0031581 | -0.013077 | -0.044957 | -0.039788 | -0.010215 | -0.00083919 | -0.015794 | 0.0095932 | 0.034282 | 0.0026795 | 0.03777 | -0.003531 | -0.007751 | -0.035879 | 0.079598 | 0.046148 | 0.24269 | -0.00811 | -121.6095 | -2.1745 | -121.731 | 0.2997 | 0.4441 | 0.27331 | -122.2583 | 121.7982 | -0.3919 | 121.8028 | 121.7705 | -0.027769 | -0.42535 | -0.2288 | -0.45197 | -0.1718 | 0.19685 | 0.075348 | 0.52732 | -0.027402 | -0.19819 | 121.8859 | 121.8525 | 122.049 | 121.7986 | -0.47961 | 122.106 | 122.2504 | 122.0796 | 119.6318 | -122.7298
1675.1719 | 122.5113 | -121.7651 | 0.52185 | 1.4211e-13 | -0.0027309 | -0.013077 | -0.045384 | -0.039788 | -0.010215 | 0.0067908 | -0.016008 | 0.0095932 | 0.034496 | 0.0022521 | 0.03777 | -0.003531 | 0.005985 | -0.031301 | 0.093333 | 0.055306 | 0.24727 | -0.021847 | -121.4813 | -2.202 | -121.6028 | 0.4279 | 0.57688 | 0.37404 | -122.1347 | 121.7433 | -0.42852 | 121.7616 | 121.7338 | -0.009454 | -0.46654 | -0.27458 | -0.36954 | -0.093956 | 0.28386 | 0.16235 | 0.5319 | 0.055024 | -0.14781 | 121.8585 | 121.8204 | 122.0124 | 121.7711 | -0.5437 | 122.193 | 122.342 | 122.1392 | 119.5631 | -122.6565
1676.9531 | 122.4701 | -121.8475 | 0.50354 | 1.4211e-13 | -0.0029445 | -0.012863 | -0.044957 | -0.040002 | -0.010215 | -0.0084697 | -0.016008 | 0.0095932 | 0.034282 | 0.0028931 | 0.03777 | 0.001048 | 0.001407 | -0.031301 | 0.093333 | 0.050727 | 0.24727 | 0.010206 | -121.5042 | -2.2203 | -121.6303 | 0.40042 | 0.55398 | 0.38777 | -122.1667 | 121.8577 | -0.41021 | 121.8486 | 121.8162 | -0.041507 | -0.45281 | -0.25627 | -0.3192 | -0.10312 | 0.34336 | 0.21728 | 0.53648 | 0.050442 | -0.11577 | 121.9409 | 121.8983 | 122.0948 | 121.8489 | -0.49333 | 122.248 | 122.4015 | 122.2353 | 119.6272 | -122.6703
1678.7656 | 122.3969 | -121.8567 | 0.51727 | 1.4211e-13 | -0.0027309 | -0.01265 | -0.044743 | -0.039788 | -0.0097878 | -0.00083919 | -0.015794 | 0.0095932 | 0.034496 | 0.0028931 | 0.037556 | 0.001048 | 0.005985 | -0.026723 | 0.088755 | 0.055306 | 0.25643 | 0.005627 | -121.5316 | -2.2341 | -121.644 | 0.39127 | 0.54482 | 0.3191 | -122.1713 | 121.8623 | -0.42852 | 121.8577 | 121.83 | -0.03235 | -0.46197 | -0.26084 | -0.31462 | -0.12601 | 0.32504 | 0.2127 | 0.52732 | 0.027551 | -0.19818 | 121.9454 | 121.912 | 122.1131 | 121.8627 | -0.51165 | 122.248 | 122.4015 | 122.1758 | 119.6226 | -122.6886
1680.4844 | 122.5067 | -121.6782 | 0.65002 | 1.4211e-13 | -0.0027309 | -0.012863 | -0.044957 | -0.039788 | -0.010215 | -0.0161 | -0.016008 | 0.0095932 | 0.034496 | 0.0028931 | 0.037983 | 0.010204 | 0.010564 | -0.026723 | 0.093333 | 0.059885 | 0.26101 | 0.014784 | -121.3806 | -2.2524 | -121.4883 | 0.53778 | 0.69592 | 0.48392 | -122.0248 | 121.6929 | -0.55669 | 121.6884 | 121.6514 | -0.041507 | -0.59014 | -0.38901 | -0.34663 | -0.11225 | 0.29761 | 0.18985 | 0.53647 | 0.045894 | -0.1661 | 121.7715 | 121.738 | 121.9392 | 121.6887 | -0.63524 | 122.2159 | 122.3741 | 122.1621 | 119.4258 | -122.6748
1682.25 | 122.5342 | -121.701 | 0.63171 | 1.4211e-13 | -0.0029445 | -0.013291 | -0.044529 | -0.039788 | -0.010215 | -0.0161 | -0.016008 | 0.0093796 | 0.034282 | 0.0026795 | 0.037556 | 0.005626 | 0.019721 | -0.022144 | 0.10249 | 0.059885 | 0.26101 | 0.010206 | -121.3897 | -2.2707 | -121.5158 | 0.52404 | 0.69134 | 0.49766 | -122.0339 | 121.7113 | -0.52922 | 121.7067 | 121.6789 | -0.03235 | -0.57183 | -0.3707 | -0.3329 | -0.10767 | 0.31134 | 0.18526 | 0.51816 | 0.059626 | -0.13405 | 121.8035 | 121.7609 | 121.9621 | 121.7208 | -0.62151 | 122.2251 | 122.3924 | 122.1987 | 119.4304 | -122.6657
1683.9688 | 122.438 | -121.7422 | 0.63629 | 1.4211e-13 | -0.0031581 | -0.012863 | -0.044743 | -0.039575 | -0.010002 | -0.0084697 | -0.016008 | 0.0093796 | 0.034282 | 0.0033205 | 0.03777 | 0.005626 | 0.005985 | -0.026723 | 0.088755 | 0.059885 | 0.26559 | 0.019363 | -121.3851 | -2.289 | -121.5112 | 0.52862 | 0.68218 | 0.51598 | -122.0385 | 121.7616 | -0.54754 | 121.7479 | 121.7155 | -0.046086 | -0.57641 | -0.3707 | -0.29628 | -0.10767 | 0.35712 | 0.23104 | 0.52732 | 0.04589 | -0.12032 | 121.831 | 121.8021 | 122.0078 | 121.7482 | -0.61693 | 122.2709 | 122.4244 | 122.2582 | 119.4533 | -122.6748
1685.7656 | 122.4472 | -121.7194 | 0.6546 | 1.4211e-13 | -0.0033719 | -0.012863 | -0.04517 | -0.040002 | -0.010002 | -0.00083919 | -0.015794 | 0.0093796 | 0.034496 | 0.0028931 | 0.037556 | 0.010204 | 0.010564 | -0.017566 | 0.10249 | 0.059885 | 0.26101 | 0.028521 | -121.3897 | -2.3165 | -121.5066 | 0.54236 | 0.69592 | 0.4885 | -122.0339 | 121.7479 | -0.55211 | 121.7296 | 121.7018 | -0.046087 | -0.59472 | -0.39359 | -0.31459 | -0.11224 | 0.32965 | 0.21273 | 0.52732 | 0.041316 | -0.1661 | 121.8218 | 121.7792 | 121.9804 | 121.7299 | -0.62608 | 122.2617 | 122.4153 | 122.2079 | 119.4029 | -122.6885
1687.5625 | 122.3923 | -121.7468 | 0.64545 | 1.4211e-13 | -0.0033719 | -0.01265 | -0.044957 | -0.040216 | -0.010002 | -0.0161 | -0.015794 | 0.0093796 | 0.034496 | 0.0028931 | 0.037556 | 0.010204 | 0.019721 | -0.017566 | 0.093333 | 0.059885 | 0.25643 | 0.014784 | -121.4218 | -2.3394 | -121.5433 | 0.51031 | 0.65471 | 0.42898 | -122.0706 | 121.7616 | -0.55211 | 121.757 | 121.7293 | -0.03235 | -0.58556 | -0.38902 | -0.32375 | -0.13514 | 0.32507 | 0.20357 | 0.52732 | 0.009264 | -0.21647 | 121.8402 | 121.8067 | 122.0033 | 121.7665 | -0.63066 | 122.2571 | 122.4015 | 122.1758 | 119.4075 | -122.716
1689.3281 | 122.4106 | -121.7468 | 0.64087 | 1.4211e-13 | -0.0035855 | -0.012863 | -0.04517 | -0.040002 | -0.010429 | -0.0084697 | -0.015794 | 0.009807 | 0.034496 | 0.0028931 | 0.037556 | 0.005626 | 0.010564 | -0.017566 | 0.093333 | 0.064464 | 0.25643 | 0.001048 | -121.4355 | -2.3577 | -121.5524 | 0.51031 | 0.65013 | 0.44272 | -122.0889 | 121.7479 | -0.54754 | 121.7525 | 121.7293 | -0.018614 | -0.57641 | -0.38444 | -0.34207 | -0.13056 | 0.31133 | 0.19441 | 0.53648 | 0.009263 | -0.19815 | 121.8402 | 121.8113 | 122.0033 | 121.7574 | -0.63982 | 122.2571 | 122.397 | 122.1895 | 119.3891 | -122.7298
1691.0938 | 122.5204 | -121.6965 | 0.61798 | 1.4211e-13 | -0.0033719 | -0.013077 | -0.044743 | -0.040002 | -0.010429 | -0.0084697 | -0.015794 | 0.0095932 | 0.034923 | 0.0028931 | 0.03777 | 0.005626 | 0.019721 | -0.012988 | 0.10249 | 0.073622 | 0.26559 | 0.019363 | -121.4263 | -2.3806 | -121.5433 | 0.52404 | 0.66845 | 0.4473 | -122.0706 | 121.7158 | -0.51549 | 121.7021 | 121.6835 | -0.032351 | -0.54436 | -0.35239 | -0.37411 | -0.093937 | 0.27013 | 0.15321 | 0.52732 | 0.050466 | -0.17068 | 121.799 | 121.7701 | 121.9621 | 121.7162 | -0.59862 | 122.2205 | 122.3649 | 122.1438 | 119.3159 | -122.6886
1692.8125 | 122.5525 | -121.7331 | 0.59052 | 1.4211e-13 | -0.0035855 | -0.013077 | -0.04517 | -0.040002 | -0.010429 | -0.00083919 | -0.016222 | 0.0093796 | 0.034068 | 0.0033205 | 0.037983 | 0.005626 | 0.015142 | -0.017566 | 0.10707 | 0.073622 | 0.25643 | 0.014784 | -121.4355 | -2.3943 | -121.557 | 0.50573 | 0.65929 | 0.45188 | -122.0843 | 121.7479 | -0.48345 | 121.7387 | 121.7155 | -0.03235 | -0.51689 | -0.33408 | -0.35122 | -0.084785 | 0.2976 | 0.1761 | 0.52732 | 0.068774 | -0.13864 | 121.8402 | 121.8067 | 121.9895 | 121.7482 | -0.57573 | 122.2388 | 122.3924 | 122.185 | 119.3388 | -122.6748
1694.5312 | 122.5296 | -121.7331 | 0.59967 | 1.4211e-13 | -0.0035855 | -0.012863 | -0.044957 | -0.039575 | -0.010429 | -0.0161 | -0.015581 | 0.0095932 | 0.034068 | 0.0026795 | 0.03777 | 0.014783 | 0.015142 | -0.017566 | 0.10249 | 0.064464 | 0.26101 | 0.028521 | -121.4309 | -2.4126 | -121.5524 | 0.50573 | 0.65471 | 0.45188 | -122.0843 | 121.7616 | -0.49718 | 121.7479 | 121.7155 | -0.046087 | -0.53521 | -0.33866 | -0.35122 | -0.09394 | 0.30218 | 0.18068 | 0.5319 | 0.055041 | -0.1478 | 121.8356 | 121.7976 | 121.9941 | 121.7482 | -0.57115 | 122.2388 | 122.3878 | 122.185 | 119.3205 | -122.684
1696.2969 | 122.4884 | -121.7422 | 0.61798 | 1.4211e-13 | -0.0033719 | -0.01265 | -0.044743 | -0.039575 | -0.010215 | -0.0084697 | -0.015794 | 0.0093796 | 0.034496 | 0.0028931 | 0.03777 | 0.014783 | 0.015142 | -0.012988 | 0.097912 | 0.059885 | 0.26559 | 0.019363 | -121.4355 | -2.4447 | -121.5478 | 0.51031 | 0.65929 | 0.4473 | -122.0889 | 121.7616 | -0.52007 | 121.757 | 121.7293 | -0.032351 | -0.5581 | -0.35239 | -0.34664 | -0.10767 | 0.30675 | 0.19441 | 0.54106 | 0.041308 | -0.17068 | 121.8402 | 121.8021 | 122.0078 | 121.7574 | -0.59862 | 122.2526 | 122.4015 | 122.1895 | 119.2976 | -122.7069
1698.0781 | 122.5525 | -121.7239 | 0.6134 | 1.4211e-13 | -0.0033719 | -0.01265 | -0.044957 | -0.040002 | -0.010643 | -0.0084697 | -0.015794 | 0.0093796 | 0.034496 | 0.0028931 | 0.037983 | 0.005626 | 0.010564 | -0.012988 | 0.097912 | 0.069043 | 0.26101 | 0.019363 | -121.4355 | -2.463 | -121.5478 | 0.51489 | 0.66845 | 0.4473 | -122.0797 | 121.7433 | -0.51549 | 121.7296 | 121.7109 | -0.032351 | -0.54436 | -0.35239 | -0.3558 | -0.098516 | 0.28844 | 0.1761 | 0.5319 | 0.055044 | -0.16611 | 121.8218 | 121.793 | 121.9849 | 121.7345 | -0.59404 | 122.2388 | 122.3924 | 122.1712 | 119.261 | -122.6931
1699.8594 | 122.4335 | -121.7606 | 0.64545 | 1.4211e-13 | -0.0031581 | -0.012863 | -0.044957 | -0.039788 | -0.010215 | -0.0161 | -0.016008 | 0.0093796 | 0.034496 | 0.0031069 | 0.03777 | 0.019361 | 0.019721 | -0.017566 | 0.097912 | 0.073622 | 0.26559 | 0.023942 | -121.4309 | -2.4905 | -121.557 | 0.51946 | 0.67302 | 0.45188 | -122.0752 | 121.7845 | -0.54753 | 121.7799 | 121.743 | -0.041508 | -0.57183 | -0.37986 | -0.3146 | -0.12598 | 0.32964 | 0.20356 | 0.51816 | 0.027578 | -0.19357 | 121.8585 | 121.8342 | 122.0261 | 121.7803 | -0.6215 | 122.28 | 122.4336 | 122.2124 | 119.2701 | -122.7206
1701.6406 | 122.4655 | -121.7651 | 0.62714 | 1.4211e-13 | -0.0031581 | -0.012863 | -0.044743 | -0.039788 | -0.010429 | 0.0067908 | -0.015794 | 0.0093796 | 0.034282 | 0.0031069 | 0.037983 | 0.014783 | 0.019721 | -0.012988 | 0.10249 | 0.073622 | 0.27017 | 0.019363 | -121.4538 | -2.5088 | -121.5753 | 0.51031 | 0.65471 | 0.47019 | -122.0981 | 121.7845 | -0.52465 | 121.7799 | 121.7521 | -0.032351 | -0.55351 | -0.35697 | -0.33291 | -0.11683 | 0.31133 | 0.18983 | 0.52274 | 0.027575 | -0.15695 | 121.8676 | 121.8388 | 122.0353 | 121.7849 | -0.60777 | 122.2754 | 122.4198 | 122.2353 | 119.2564 | -122.7252
1703.375 | 122.5525 | -121.7285 | 0.59967 | 1.4211e-13 | -0.0037991 | -0.012863 | -0.044743 | -0.040002 | -0.010215 | -0.0084697 | -0.016435 | 0.0095932 | 0.034496 | 0.0028931 | 0.03777 | 0.014783 | 0.028878 | -0.008409 | 0.097912 | 0.073622 | 0.26559 | 0.019363 | -121.4492 | -2.5317 | -121.5753 | 0.51031 | 0.65471 | 0.49308 | -122.1072 | 121.7479 | -0.50176 | 121.7433 | 121.7201 | -0.027772 | -0.52605 | -0.33408 | -0.37869 | -0.089362 | 0.27929 | 0.1532 | 0.5319 | 0.055041 | -0.10659 | 121.8264 | 121.8021 | 121.9941 | 121.7574 | -0.58031 | 122.2388 | 122.3832 | 122.2216 | 119.1968 | -122.7069
1705.1406 | 122.5479 | -121.7422 | 0.59967 | 1.4211e-13 | -0.0035855 | -0.013077 | -0.044743 | -0.040002 | -0.010429 | -0.00083919 | -0.016008 | 0.0093796 | 0.034496 | 0.0031069 | 0.037556 | 0.014783 | 0.015142 | -0.012988 | 0.11165 | 0.073622 | 0.26559 | 0.028521 | -121.4538 | -2.5591 | -121.5799 | 0.51031 | 0.65471 | 0.45645 | -122.1072 | 121.7708 | -0.48802 | 121.757 | 121.7293 | -0.041509 | -0.52605 | -0.33408 | -0.36496 | -0.089362 | 0.28844 | 0.16236 | 0.52732 | 0.055041 | -0.14322 | 121.8539 | 121.8159 | 122.0078 | 121.7574 | -0.57115 | 122.2526 | 122.397 | 122.1987 | 119.1831 | -122.7069
1706.8594 | 122.4701 | -121.8109 | 0.62256 | 1.4211e-13 | -0.0033719 | -0.01265 | -0.044957 | -0.039575 | -0.010002 | -0.0084697 | -0.015794 | 0.009166 | 0.034282 | 0.0028931 | 0.037556 | 0.005626 | 0.028878 | -0.003831 | 0.10707 | 0.073622 | 0.26559 | 0.042258 | -121.4721 | -2.5729 | -121.5982 | 0.47826 | 0.6364 | 0.41983 | -122.1301 | 121.8532 | -0.51549 | 121.8165 | 121.8071 | -0.046089 | -0.54894 | -0.35697 | -0.31919 | -0.1443 | 0.33879 | 0.21271 | 0.5319 | 0.013837 | -0.20273 | 121.918 | 121.8845 | 122.0765 | 121.8398 | -0.5803 | 122.2892 | 122.4473 | 122.2307 | 119.238 | -122.7527
1708.6406 | 122.4838 | -121.8018 | 0.62256 | 1.4211e-13 | -0.0031581 | -0.012863 | -0.044957 | -0.039788 | -0.010002 | -0.0161 | -0.016222 | 0.009166 | 0.034709 | 0.0028931 | 0.037556 | 0.014783 | 0.0243 | -0.003831 | 0.097912 | 0.073622 | 0.26559 | 0.0331 | -121.4904 | -2.5958 | -121.6074 | 0.48284 | 0.62724 | 0.41067 | -122.1301 | 121.8349 | -0.52465 | 121.8165 | 121.7979 | -0.036931 | -0.54894 | -0.35697 | -0.32834 | -0.13972 | 0.31132 | 0.1944 | 0.52274 | 0.00468 | -0.21189 | 121.8997 | 121.8754 | 122.0673 | 121.8261 | -0.58946 | 122.2846 | 122.429 | 122.2124 | 119.206 | -122.7527
1710.3594 | 122.4472 | -121.8292 | 0.61798 | 1.4211e-13 | -0.0033719 | -0.013077 | -0.044957 | -0.039788 | -0.010215 | -0.00083919 | -0.016008 | 0.0095932 | 0.034282 | 0.0028931 | 0.037556 | 0.014783 | 0.019721 | -0.003831 | 0.11165 | 0.073622 | 0.26101 | 0.028521 | -121.4859 | -2.6187 | -121.6074 | 0.47826 | 0.6364 | 0.41525 | -122.1347 | 121.8577 | -0.50633 | 121.844 | 121.8254 | -0.032352 | -0.54436 | -0.35697 | -0.30546 | -0.13972 | 0.34336 | 0.22186 | 0.52732 | 0.018415 | -0.20273 | 121.9409 | 121.9028 | 122.0902 | 121.8489 | -0.58946 | 122.3075 | 122.4656 | 122.2445 | 119.2106 | -122.7527
1712.125 | 122.4976 | -121.8109 | 0.62256 | 1.4211e-13 | -0.0035855 | -0.01265 | -0.044743 | -0.039788 | -0.010215 | 0.0067908 | -0.015581 | 0.009807 | 0.034282 | 0.0031069 | 0.03777 | 0.019361 | 0.0243 | -0.008409 | 0.10249 | 0.064464 | 0.26559 | 0.065153 | -121.4767 | -2.6461 | -121.589 | 0.50115 | 0.65013 | 0.4244 | -122.1255 | 121.8761 | -0.52007 | 121.8303 | 121.8025 | -0.073562 | -0.5581 | -0.35697 | -0.31461 | -0.12141 | 0.33421 | 0.22187 | 0.53648 | 0.027573 | -0.19816 | 121.9134 | 121.8754 | 122.0765 | 121.8352 | -0.55741 | 122.3121 | 122.461 | 122.2353 | 119.1648 | -122.7481
1713.9062 | 122.4655 | -121.8018 | 0.63171 | 1.4211e-13 | -0.0033719 | -0.013077 | -0.04517 | -0.040002 | -0.0097878 | -0.0084697 | -0.016008 | 0.009807 | 0.034709 | 0.0031069 | 0.037342 | 0.014783 | 0.0243 | -0.017566 | 0.10707 | 0.073622 | 0.27475 | 0.0331 | -121.4767 | -2.6644 | -121.5982 | 0.48742 | 0.64097 | 0.43814 | -122.1301 | 121.8349 | -0.52465 | 121.8165 | 121.7842 | -0.050666 | -0.55809 | -0.35697 | -0.32834 | -0.1443 | 0.32505 | 0.20355 | 0.5319 | 0.009261 | -0.19357 | 121.9088 | 121.8754 | 122.0765 | 121.8261 | -0.59861 | 122.2892 | 122.4427 | 122.2399 | 119.1373 | -122.7618
1715.6406 | 122.4472 | -121.8018 | 0.62714 | 1.4211e-13 | -0.0031581 | -0.013077 | -0.04517 | -0.040002 | -0.010002 | -0.00083919 | -0.016222 | 0.009166 | 0.034709 | 0.0033205 | 0.03777 | 0.019361 | 0.028878 | -0.008409 | 0.11165 | 0.069043 | 0.26559 | 0.042258 | -121.4721 | -2.6919 | -121.5936 | 0.49657 | 0.65929 | 0.50224 | -122.1301 | 121.844 | -0.51549 | 121.8211 | 121.7933 | -0.050667 | -0.55809 | -0.36155 | -0.32834 | -0.13056 | 0.32963 | 0.20813 | 0.53648 | 0.032153 | -0.1249 | 121.9134 | 121.8708 | 122.0673 | 121.8306 | -0.58488 | 122.2983 | 122.461 | 122.304 | 119.1098 | -122.7572
1717.4375 | 122.4609 | -121.8521 | 0.62256 | 1.4211e-13 | -0.0035855 | -0.012863 | -0.044957 | -0.039788 | -0.010002 | 0.0067908 | -0.016008 | 0.0095932 | 0.034709 | 0.0028931 | 0.037556 | 0.014783 | 0.019721 | -0.003831 | 0.10707 | 0.073622 | 0.27475 | 0.051416 | -121.495 | -2.7148 | -121.6165 | 0.48284 | 0.64097 | 0.47019 | -122.1393 | 121.9035 | -0.51549 | 121.8669 | 121.8483 | -0.055247 | -0.54894 | -0.34781 | -0.28715 | -0.13972 | 0.35709 | 0.23559 | 0.52274 | 0.018416 | -0.15237 | 121.9592 | 121.9257 | 122.1269 | 121.8718 | -0.57114 | 122.3349 | 122.4931 | 122.3223 | 119.1373 | -122.7618
1719.2188 | 122.5754 | -121.7834 | 0.5722 | 1.4211e-13 | -0.0035855 | -0.012863 | -0.044957 | -0.039788 | -0.010429 | -0.00083919 | -0.016008 | 0.0093796 | 0.034496 | 0.0031069 | 0.037556 | 0.023939 | 0.028878 | -0.008409 | 0.11622 | 0.069043 | 0.27475 | 0.042258 | -121.5042 | -2.7423 | -121.6257 | 0.47826 | 0.63182 | 0.44272 | -122.1576 | 121.8257 | -0.45598 | 121.8074 | 121.775 | -0.050667 | -0.50316 | -0.29746 | -0.37413 | -0.093946 | 0.27927 | 0.15777 | 0.5319 | 0.059613 | -0.12949 | 121.8997 | 121.8525 | 122.0582 | 121.8123 | -0.52995 | 122.2617 | 122.4153 | 122.2262 | 119.0412 | -122.7298
1721.0156 | 122.5296 | -121.8292 | 0.58136 | 1.4211e-13 | -0.0031581 | -0.013505 | -0.04517 | -0.040002 | -0.010002 | -0.00083919 | -0.016008 | 0.0093796 | 0.034496 | 0.0031069 | 0.03777 | 0.019361 | 0.0243 | -0.008409 | 0.11622 | 0.073622 | 0.27017 | 0.060574 | -121.5042 | -2.756 | -121.6303 | 0.4691 | 0.62724 | 0.4244 | -122.1576 | 121.8898 | -0.46513 | 121.8486 | 121.8208 | -0.068983 | -0.50774 | -0.31119 | -0.32835 | -0.11226 | 0.32505 | 0.19897 | 0.52732 | 0.045879 | -0.15696 | 121.9454 | 121.9028 | 122.0994 | 121.8535 | -0.52079 | 122.2983 | 122.4565 | 122.2536 | 119.0732 | -122.7389
1722.75 | 122.493 | -121.8613 | 0.59052 | 1.4211e-13 | -0.0033719 | -0.013291 | -0.044957 | -0.039788 | -0.010215 | -0.023731 | -0.015794 | 0.0095932 | 0.034496 | 0.0031069 | 0.03777 | 0.019361 | 0.028878 | 0.000747 | 0.11165 | 0.069043 | 0.27475 | 0.0331 | -121.5088 | -2.7835 | -121.6348 | 0.48284 | 0.62724 | 0.41067 | -122.1622 | 121.8944 | -0.47887 | 121.8806 | 121.862 | -0.032353 | -0.52147 | -0.31577 | -0.30089 | -0.10768 | 0.35251 | 0.22643 | 0.52732 | 0.036724 | -0.17985 | 121.9729 | 121.9303 | 122.136 | 121.8901 | -0.55741 | 122.3441 | 122.4885 | 122.2719 | 119.0778 | -122.7527
1724.5312 | 122.4792 | -121.8384 | 0.58136 | 1.4211e-13 | -0.0033719 | -0.013077 | -0.044957 | -0.040002 | -0.010002 | -0.00083919 | -0.015794 | 0.0093796 | 0.034709 | 0.0028931 | 0.037983 | 0.014783 | 0.0243 | -0.008409 | 0.11165 | 0.069043 | 0.27017 | 0.046837 | -121.5088 | -2.8155 | -121.644 | 0.47368 | 0.61808 | 0.43356 | -122.1759 | 121.8852 | -0.46971 | 121.8532 | 121.83 | -0.055246 | -0.51232 | -0.31119 | -0.33751 | -0.10768 | 0.32963 | 0.19439 | 0.5319 | 0.036722 | -0.1478 | 121.95 | 121.9074 | 122.1085 | 121.8627 | -0.53452 | 122.3121 | 122.4565 | 122.2719 | 119.0228 | -122.7573
1726.2969 | 122.5754 | -121.8109 | 0.55389 | 1.4211e-13 | -0.0035855 | -0.012863 | -0.044743 | -0.039788 | -0.010215 | 0.0067908 | -0.015794 | 0.0095932 | 0.034496 | 0.0031069 | 0.03777 | 0.014783 | 0.0243 | -0.008409 | 0.10707 | 0.078201 | 0.27475 | 0.060574 | -121.5316 | -2.8247 | -121.6486 | 0.47368 | 0.6135 | 0.39693 | -122.1759 | 121.8715 | -0.44683 | 121.8257 | 121.8025 | -0.068983 | -0.47569 | -0.27915 | -0.36498 | -0.080214 | 0.27926 | 0.16234 | 0.52732 | 0.059609 | -0.15696 | 121.918 | 121.8891 | 122.0857 | 121.8352 | -0.49332 | 122.2846 | 122.4244 | 122.2078 | 118.9862 | -122.7298
1728.0625 | 122.4792 | -121.8567 | 0.58136 | 1.4211e-13 | -0.0035855 | -0.012863 | -0.044957 | -0.040002 | -0.010429 | -0.00083919 | -0.016008 | 0.0095932 | 0.034496 | 0.0035341 | 0.037342 | 0.014783 | 0.028878 | -0.008409 | 0.11165 | 0.078201 | 0.26559 | 0.055995 | -121.5271 | -2.8476 | -121.6486 | 0.4691 | 0.62266 | 0.40609 | -122.1805 | 121.9127 | -0.46971 | 121.8715 | 121.8483 | -0.064404 | -0.50316 | -0.31577 | -0.32378 | -0.11226 | 0.32962 | 0.20812 | 0.5319 | 0.041301 | -0.17527 | 121.9683 | 121.9349 | 122.1223 | 121.8856 | -0.52536 | 122.3258 | 122.4793 | 122.2628 | 119.0091 | -122.7618
1729.7812 | 122.612 | -121.8109 | 0.55847 | 1.4211e-13 | -0.0035855 | -0.012863 | -0.045384 | -0.039788 | -0.010215 | -0.00083919 | -0.015794 | 0.0093796 | 0.034709 | 0.0031069 | 0.037556 | 0.023939 | 0.042614 | -0.003831 | 0.11165 | 0.08278 | 0.27017 | 0.078889 | -121.5316 | -2.8613 | -121.6394 | 0.46452 | 0.61808 | 0.39235 | -122.1805 | 121.8898 | -0.44682 | 121.8349 | 121.8071 | -0.08272 | -0.47569 | -0.2883 | -0.36956 | -0.093949 | 0.27926 | 0.1715 | 0.54106 | 0.05961 | -0.16612 | 121.9226 | 121.8937 | 122.0811 | 121.8535 | -0.47958 | 122.2754 | 122.429 | 122.2033 | 118.9496 | -122.7389
1731.5625 | 122.493 | -121.8887 | 0.58594 | 1.4211e-13 | -0.0035855 | -0.013077 | -0.04517 | -0.040429 | -0.010215 | -0.0084697 | -0.016008 | 0.0095932 | 0.034282 | 0.0033205 | 0.03777 | 0.014783 | 0.038035 | -0.003831 | 0.11622 | 0.073622 | 0.27475 | 0.088047 | -121.5362 | -2.8842 | -121.6577 | 0.46452 | 0.61808 | 0.3832 | -122.1896 | 121.9768 | -0.46971 | 121.9035 | 121.8849 | -0.091878 | -0.51232 | -0.31119 | -0.30089 | -0.12141 | 0.35251 | 0.23101 | 0.5319 | 0.032145 | -0.20274 | 122.005 | 121.9624 | 122.1635 | 121.9268 | -0.49789 | 122.3533 | 122.5068 | 122.2719 | 119.0045 | -122.7756
1733.3438 | 122.4792 | -121.8704 | 0.58136 | 1.4211e-13 | -0.0035855 | -0.013077 | -0.044957 | -0.040002 | -0.010429 | 0.014421 | -0.015794 | 0.0095932 | 0.034496 | 0.0031069 | 0.037983 | 0.019361 | 0.028878 | 0.005325 | 0.1208 | 0.078201 | 0.27017 | 0.078889 | -121.5362 | -2.9025 | -121.6577 | 0.45994 | 0.6135 | 0.39235 | -122.185 | 121.9493 | -0.46056 | 121.8898 | 121.8757 | -0.073564 | -0.50316 | -0.31119 | -0.31463 | -0.12141 | 0.3342 | 0.2127 | 0.52732 | 0.032143 | -0.18901 | 121.9912 | 121.9486 | 122.1406 | 121.8993 | -0.50247 | 122.3304 | 122.4839 | 122.2628 | 118.9679 | -122.7664
1735.125 | 122.5662 | -121.8246 | 0.56305 | 1.4211e-13 | -0.0033719 | -0.013077 | -0.044743 | -0.039575 | -0.010429 | 0.0067908 | -0.015581 | 0.009166 | 0.034709 | 0.0031069 | 0.037556 | 0.023939 | 0.038035 | 0.005325 | 0.11622 | 0.078201 | 0.27475 | 0.11094 | -121.5454 | -2.93 | -121.6577 | 0.4691 | 0.6135 | 0.3832 | -122.1988 | 121.9356 | -0.44682 | 121.8486 | 121.83 | -0.10562 | -0.48485 | -0.2883 | -0.37414 | -0.093947 | 0.27926 | 0.16692 | 0.54106 | 0.050454 | -0.17985 | 121.9409 | 121.9028 | 122.0994 | 121.8627 | -0.45211 | 122.2937 | 122.4381 | 122.2078 | 118.8946 | -122.7618
1736.8594 | 122.5021 | -121.8842 | 0.59509 | 1.4211e-13 | -0.0037991 | -0.013077 | -0.04517 | -0.040002 | -0.010215 | -0.00083919 | -0.016008 | 0.009807 | 0.034709 | 0.0033205 | 0.03777 | 0.023939 | 0.038035 | -0.008409 | 0.11165 | 0.078201 | 0.27475 | 0.10636 | -121.5454 | -2.9575 | -121.6623 | 0.46452 | 0.6135 | 0.40609 | -122.2034 | 121.9905 | -0.48345 | 121.9081 | 121.8757 | -0.11477 | -0.51689 | -0.32035 | -0.31921 | -0.13057 | 0.33877 | 0.22185 | 0.54106 | 0.01841 | -0.189 | 121.9958 | 121.9624 | 122.1589 | 121.9222 | -0.48873 | 122.3487 | 122.4977 | 122.2902 | 118.9267 | -122.7985
1738.6406 | 122.5845 | -121.8338 | 0.55847 | 1.4211e-13 | -0.0035855 | -0.012863 | -0.04517 | -0.040002 | -0.010215 | -0.00083919 | -0.016008 | 0.0093796 | 0.034496 | 0.0037479 | 0.037556 | 0.019361 | 0.0243 | 0.000747 | 0.1208 | 0.078201 | 0.27475 | 0.10178 | -121.5545 | -2.985 | -121.6669 | 0.45537 | 0.60435 | 0.41525 | -122.2079 | 121.9356 | -0.43767 | 121.8532 | 121.8345 | -0.10104 | -0.48027 | -0.28373 | -0.37414 | -0.10311 | 0.27926 | 0.16692 | 0.54106 | 0.045874 | -0.14323 | 121.9546 | 121.912 | 122.1085 | 121.8581 | -0.45669 | 122.2892 | 122.4381 | 122.249 | 118.8488 | -122.7664
1740.4375 | 122.4838 | -121.9025 | 0.60883 | 1.4211e-13 | -0.0037991 | -0.013077 | -0.044957 | -0.040002 | -0.010429 | 0.0067908 | -0.015794 | 0.0095932 | 0.034709 | 0.0031069 | 0.03777 | 0.028518 | 0.028878 | 0.000747 | 0.11622 | 0.087359 | 0.27932 | 0.088047 | -121.5454 | -3.0124 | -121.6623 | 0.46452 | 0.6135 | 0.47019 | -122.2079 | 121.9905 | -0.4926 | 121.931 | 121.9032 | -0.0873 | -0.52147 | -0.3295 | -0.30548 | -0.1443 | 0.35708 | 0.24016 | 0.54564 | 0.004677 | -0.13864 | 122.0187 | 121.9898 | 122.1818 | 121.9313 | -0.52078 | 122.367 | 122.516 | 122.3727 | 118.89 | -122.8168
1742.1562 | 122.644 | -121.843 | 0.56763 | 1.4211e-13 | -0.0037991 | -0.013077 | -0.04517 | -0.039788 | -0.010215 | -0.00083919 | -0.016222 | 0.009166 | 0.034496 | 0.0033205 | 0.037556 | 0.028518 | 0.028878 | 0.000747 | 0.1208 | 0.08278 | 0.2839 | 0.078889 | -121.5362 | -3.0307 | -121.6623 | 0.47368 | 0.6135 | 0.40609 | -122.1988 | 121.9218 | -0.44682 | 121.8715 | 121.8437 | -0.078142 | -0.48485 | -0.28372 | -0.35583 | -0.093947 | 0.30673 | 0.18065 | 0.53648 | 0.045876 | -0.16154 | 121.9638 | 121.9257 | 122.1269 | 121.8718 | -0.48874 | 122.3166 | 122.4565 | 122.249 | 118.8122 | -122.7664
1743.9375 | 122.6074 | -121.8567 | 0.5722 | 1.4211e-13 | -0.0035855 | -0.013077 | -0.044957 | -0.040002 | -0.010429 | 0.0067908 | -0.015794 | 0.0093796 | 0.034709 | 0.0033205 | 0.037556 | 0.033096 | 0.033457 | 0.009904 | 0.1208 | 0.078201 | 0.27475 | 0.07431 | -121.5545 | -3.0628 | -121.6669 | 0.45994 | 0.6135 | 0.40609 | -122.2079 | 121.931 | -0.4514 | 121.8898 | 121.8666 | -0.064406 | -0.494 | -0.29746 | -0.35125 | -0.11226 | 0.30215 | 0.1898 | 0.54106 | 0.041298 | -0.16612 | 121.9775 | 121.9349 | 122.1314 | 121.8901 | -0.49789 | 122.3166 | 122.4702 | 122.2628 | 118.7939 | -122.7801
1745.7031 | 122.6624 | -121.8613 | 0.54932 | 1.4211e-13 | -0.0035855 | -0.013077 | -0.044743 | -0.040216 | -0.010429 | 0.0067908 | -0.016008 | 0.0093796 | 0.034496 | 0.0031069 | 0.037983 | 0.028518 | 0.042614 | 0.009904 | 0.12538 | 0.08278 | 0.27017 | 0.11552 | -121.5637 | -3.0903 | -121.6806 | 0.45994 | 0.60893 | 0.3832 | -122.2263 | 121.9768 | -0.42393 | 121.8898 | 121.8712 | -0.10562 | -0.46654 | -0.27915 | -0.36499 | -0.089371 | 0.29757 | 0.18065 | 0.54564 | 0.059609 | -0.16612 | 121.9866 | 121.944 | 122.1314 | 121.9039 | -0.4338 | 122.3212 | 122.4702 | 122.2445 | 118.771 | -122.7756
1747.4844 | 122.5296 | -121.875 | 0.59052 | 1.4211e-13 | -0.0035855 | -0.012863 | -0.04517 | -0.039788 | -0.010002 | -0.0161 | -0.016008 | 0.0093796 | 0.034923 | 0.0033205 | 0.037983 | 0.028518 | 0.038035 | 0.000747 | 0.11622 | 0.08278 | 0.27475 | 0.11094 | -121.5637 | -3.1086 | -121.6806 | 0.45994 | 0.60435 | 0.38777 | -122.2217 | 121.9859 | -0.47429 | 121.9035 | 121.8757 | -0.1102 | -0.50774 | -0.31577 | -0.34668 | -0.13057 | 0.3113 | 0.19438 | 0.54106 | 0.013831 | -0.20274 | 121.9912 | 121.9578 | 122.1497 | 121.913 | -0.47957 | 122.3349 | 122.4793 | 122.2628 | 118.7664 | -122.8122
1749.2031 | 122.5479 | -121.8979 | 0.60425 | 1.4211e-13 | -0.0035855 | -0.013077 | -0.044957 | -0.039788 | -0.010429 | -0.0084697 | -0.016008 | 0.0093796 | 0.034496 | 0.0031069 | 0.037556 | 0.033096 | 0.042614 | 0.005325 | 0.1208 | 0.078201 | 0.2839 | 0.10636 | -121.5637 | -3.1315 | -121.6898 | 0.45994 | 0.60893 | 0.3832 | -122.2308 | 122.0043 | -0.48344 | 121.931 | 121.9032 | -0.10104 | -0.52605 | -0.32034 | -0.33295 | -0.1443 | 0.33419 | 0.20811 | 0.54106 | 0.004677 | -0.22105 | 122.0187 | 121.9761 | 122.1818 | 121.9405 | -0.49789 | 122.3578 | 122.5068 | 122.2811 | 118.7664 | -122.8351
1750.9844 | 122.5296 | -121.9162 | 0.5722 | 1.4211e-13 | -0.0037991 | -0.013077 | -0.04517 | -0.040216 | -0.010215 | -0.00083919 | -0.016008 | 0.0093796 | 0.034282 | 0.0035341 | 0.03777 | 0.023939 | 0.038035 | 0.005325 | 0.12538 | 0.08278 | 0.27475 | 0.10636 | -121.5774 | -3.1635 | -121.6989 | 0.44621 | 0.59519 | 0.40609 | -122.24 | 122.0226 | -0.44682 | 121.9401 | 121.9215 | -0.10104 | -0.48942 | -0.29746 | -0.32379 | -0.126 | 0.33876 | 0.21726 | 0.54106 | 0.022984 | -0.16612 | 122.0416 | 121.999 | 122.1909 | 121.9542 | -0.46584 | 122.3624 | 122.5114 | 122.3223 | 118.7527 | -122.8122
1752.7812 | 122.6212 | -121.8567 | 0.52643 | 1.4211e-13 | -0.0040129 | -0.012863 | -0.044957 | -0.040002 | -0.010643 | -0.00083919 | -0.016222 | 0.0093796 | 0.034709 | 0.0035341 | 0.037556 | 0.037675 | 0.033457 | 0.000747 | 0.1208 | 0.08278 | 0.27932 | 0.10636 | -121.5912 | -3.2002 | -121.7035 | 0.43247 | 0.59519 | 0.37404 | -122.2492 | 121.9631 | -0.40562 | 121.8944 | 121.8574 | -0.10562 | -0.44365 | -0.2471 | -0.39246 | -0.093954 | 0.26552 | 0.15318 | 0.54564 | 0.068761 | -0.15239 | 121.9775 | 121.9395 | 122.136 | 121.8901 | -0.42007 | 122.2892 | 122.4519 | 122.2307 | 118.6565 | -122.7756
1754.5781 | 122.6669 | -121.8613 | 0.53101 | 1.4211e-13 | -0.0037991 | -0.013077 | -0.044529 | -0.040002 | -0.010002 | -0.0084697 | -0.016008 | 0.0095932 | 0.034282 | 0.0035341 | 0.03777 | 0.028518 | 0.038035 | 0.005325 | 0.12538 | 0.08278 | 0.29306 | 0.11552 | -121.5866 | -3.2276 | -121.6989 | 0.44163 | 0.59519 | 0.36946 | -122.2492 | 121.9768 | -0.40562 | 121.8898 | 121.8666 | -0.1102 | -0.44823 | -0.23795 | -0.38788 | -0.089375 | 0.27467 | 0.16233 | 0.55022 | 0.064183 | -0.16155 | 121.9866 | 121.944 | 122.1543 | 121.8993 | -0.41548 | 122.3029 | 122.4565 | 122.2307 | 118.6336 | -122.7802
1756.2812 | 122.4747 | -121.9299 | 0.5722 | 1.4211e-13 | -0.0037991 | -0.01265 | -0.044957 | -0.040002 | -0.010215 | -0.00083919 | -0.015794 | 0.009807 | 0.034709 | 0.0035341 | 0.03777 | 0.033096 | 0.038035 | 0.009904 | 0.12538 | 0.073622 | 0.27932 | 0.11094 | -121.6003 | -3.2551 | -121.7081 | 0.43705 | 0.59519 | 0.37862 | -122.2537 | 122.0409 | -0.44682 | 121.963 | 121.9398 | -0.10104 | -0.49858 | -0.29288 | -0.3238 | -0.13515 | 0.3296 | 0.22184 | 0.54564 | 0.022984 | -0.19359 | 122.0553 | 122.0036 | 122.2093 | 121.968 | -0.46126 | 122.367 | 122.5251 | 122.3085 | 118.6748 | -122.8259
1758.0469 | 122.493 | -121.9574 | 0.56305 | 1.4211e-13 | -0.0037991 | -0.012863 | -0.04517 | -0.039788 | -0.010643 | -0.00083919 | -0.015794 | 0.0093796 | 0.034709 | 0.0031069 | 0.03777 | 0.033096 | 0.038035 | 0.009904 | 0.11622 | 0.08278 | 0.2839 | 0.11094 | -121.6095 | -3.2917 | -121.7218 | 0.4279 | 0.58145 | 0.38777 | -122.272 | 122.0683 | -0.44682 | 121.9905 | 121.9673 | -0.10104 | -0.48027 | -0.27915 | -0.31465 | -0.13515 | 0.34791 | 0.23557 | 0.55022 | 0.018404 | -0.17527 | 122.0736 | 122.0402 | 122.2413 | 121.9954 | -0.45211 | 122.3853 | 122.5388 | 122.3452 | 118.6657 | -122.8351
1759.8281 | 122.5525 | -121.962 | 0.53101 | 1.4211e-13 | -0.0037991 | -0.012863 | -0.044957 | -0.040002 | -0.010429 | -0.0084697 | -0.015794 | 0.0095932 | 0.034923 | 0.0037479 | 0.037556 | 0.028518 | 0.038035 | 0.009904 | 0.12538 | 0.08278 | 0.2839 | 0.11552 | -121.6095 | -3.3146 | -121.731 | 0.42332 | 0.5723 | 0.34657 | -122.2858 | 122.0775 | -0.40562 | 121.9905 | 121.9719 | -0.10562 | -0.44823 | -0.2471 | -0.32381 | -0.10769 | 0.35249 | 0.23099 | 0.55479 | 0.04129 | -0.18444 | 122.0874 | 122.0448 | 122.2459 | 122 | -0.41548 | 122.3853 | 122.5343 | 122.3085 | 118.6473 | -122.8168
1761.6094 | 122.5891 | -121.9391 | 0.52643 | 1.4211e-13 | -0.0040129 | -0.012863 | -0.04517 | -0.040002 | -0.010643 | -0.0084697 | -0.016008 | 0.0095932 | 0.034709 | 0.0035341 | 0.03777 | 0.033096 | 0.042614 | 0.005325 | 0.11622 | 0.078201 | 0.27932 | 0.11552 | -121.6186 | -3.3421 | -121.731 | 0.41416 | 0.5723 | 0.34657 | -122.2812 | 122.0546 | -0.4102 | 121.9722 | 121.9444 | -0.1102 | -0.44823 | -0.2471 | -0.34212 | -0.11227 | 0.32044 | 0.2081 | 0.55022 | 0.045868 | -0.17986 | 122.0553 | 122.0173 | 122.2184 | 121.9817 | -0.41091 | 122.3532 | 122.5114 | 122.2857 | 118.597 | -122.8076
1763.3906 | 122.5388 | -121.9711 | 0.52643 | 1.4211e-13 | -0.0040129 | -0.01265 | -0.044743 | -0.039788 | -0.010429 | -0.0084697 | -0.016435 | 0.0095932 | 0.034282 | 0.0028931 | 0.03777 | 0.033096 | 0.038035 | 0.005325 | 0.12538 | 0.078201 | 0.27932 | 0.10636 | -121.6232 | -3.3696 | -121.7401 | 0.41416 | 0.56772 | 0.34199 | -122.2904 | 122.0775 | -0.40105 | 122.0042 | 121.9765 | -0.10104 | -0.44823 | -0.2471 | -0.31923 | -0.11227 | 0.34791 | 0.23099 | 0.55022 | 0.041289 | -0.18444 | 122.0965 | 122.0493 | 122.2505 | 122.0092 | -0.42007 | 122.3853 | 122.5388 | 122.3131 | 118.6016 | -122.8168
1765.1719 | 122.5571 | -121.9574 | 0.56763 | 1.4211e-13 | -0.0040129 | -0.012863 | -0.044957 | -0.040002 | -0.010215 | 0.0067908 | -0.015581 | 0.0095932 | 0.034496 | 0.0035341 | 0.037556 | 0.028518 | 0.042614 | 0.000747 | 0.1208 | 0.087359 | 0.2839 | 0.11094 | -121.6003 | -3.4016 | -121.7218 | 0.43705 | 0.58603 | 0.35572 | -122.272 | 122.0683 | -0.44682 | 121.9859 | 121.9581 | -0.1102 | -0.48027 | -0.28372 | -0.31465 | -0.13057 | 0.35707 | 0.23557 | 0.55022 | 0.018405 | -0.2119 | 122.0782 | 122.0448 | 122.2413 | 122 | -0.45669 | 122.3944 | 122.5434 | 122.3131 | 118.5558 | -122.8397
1766.8906 | 122.6486 | -121.8796 | 0.58136 | 1.4211e-13 | -0.0037991 | -0.013077 | -0.044957 | -0.039575 | -0.010643 | 0.0067908 | -0.016435 | 0.009166 | 0.034496 | 0.0035341 | 0.037556 | 0.033096 | 0.038035 | 0.014482 | 0.11622 | 0.091937 | 0.2839 | 0.11552 | -121.5729 | -3.4428 | -121.6898 | 0.4691 | 0.62724 | 0.38777 | -122.24 | 121.9951 | -0.46513 | 121.9127 | 121.8941 | -0.10104 | -0.48942 | -0.29746 | -0.36042 | -0.11226 | 0.30672 | 0.1898 | 0.55022 | 0.045879 | -0.19359 | 121.9958 | 121.9715 | 122.1635 | 121.9176 | -0.46584 | 122.3487 | 122.5068 | 122.2674 | 118.4367 | -122.8214
1768.6719 | 122.6303 | -121.8933 | 0.54474 | 1.4211e-13 | -0.0035855 | -0.012863 | -0.044957 | -0.039788 | -0.010643 | 0.0067908 | -0.015794 | 0.009807 | 0.034923 | 0.0035341 | 0.037556 | 0.033096 | 0.042614 | 0.005325 | 0.12538 | 0.087359 | 0.28848 | 0.11094 | -121.5912 | -3.4795 | -121.6989 | 0.45537 | 0.6135 | 0.39693 | -122.2537 | 122.0043 | -0.41936 | 121.9264 | 121.8986 | -0.10562 | -0.45738 | -0.25626 | -0.36042 | -0.089373 | 0.30214 | 0.19437 | 0.55479 | 0.068764 | -0.14781 | 122.0187 | 121.9807 | 122.1818 | 121.9359 | -0.4338 | 122.3487 | 122.5068 | 122.2902 | 118.4138 | -122.7985
1770.3906 | 122.5937 | -121.9116 | 0.57678 | 1.4211e-13 | -0.0040129 | -0.013077 | -0.04517 | -0.040216 | -0.010429 | -0.0084697 | -0.015794 | 0.0095932 | 0.034709 | 0.0035341 | 0.037556 | 0.037675 | 0.047193 | 0.005325 | 0.12538 | 0.087359 | 0.2839 | 0.1201 | -121.5774 | -3.5024 | -121.6989 | 0.46452 | 0.62724 | 0.39693 | -122.2537 | 122.0317 | -0.4514 | 121.9493 | 121.9169 | -0.11478 | -0.48942 | -0.29288 | -0.34211 | -0.11226 | 0.33419 | 0.21268 | 0.55479 | 0.050457 | -0.17985 | 122.037 | 121.999 | 122.1955 | 121.9588 | -0.45668 | 122.3761 | 122.5389 | 122.3086 | 118.4093 | -122.8305
1772.1562 | 122.5342 | -121.9345 | 0.59052 | 1.4211e-13 | -0.0035855 | -0.012863 | -0.044743 | -0.040002 | -0.010429 | -0.00083919 | -0.015794 | 0.0095932 | 0.034496 | 0.0035341 | 0.03777 | 0.037675 | 0.042614 | 0.014482 | 0.12538 | 0.08278 | 0.28848 | 0.11094 | -121.5866 | -3.5298 | -121.7035 | 0.46452 | 0.61808 | 0.38777 | -122.2537 | 122.0455 | -0.46513 | 121.9722 | 121.949 | -0.09646 | -0.50774 | -0.30203 | -0.31922 | -0.12599 | 0.34792 | 0.231 | 0.55022 | 0.027567 | -0.20274 | 122.0599 | 122.0173 | 122.223 | 121.9771 | -0.47957 | 122.399 | 122.5526 | 122.3223 | 118.4047 | -122.8442
1773.875 | 122.6074 | -121.9116 | 0.55389 | 1.4211e-13 | -0.0042265 | -0.013077 | -0.04517 | -0.040216 | -0.010429 | -0.00083919 | -0.016222 | 0.0095932 | 0.034709 | 0.0035341 | 0.037983 | 0.033096 | 0.042614 | 0.005325 | 0.1208 | 0.078201 | 0.27932 | 0.1201 | -121.5912 | -3.5756 | -121.7127 | 0.45537 | 0.60435 | 0.37862 | -122.2537 | 122.0317 | -0.43309 | 121.9447 | 121.9169 | -0.11478 | -0.47569 | -0.27457 | -0.34211 | -0.098528 | 0.32045 | 0.19895 | 0.54106 | 0.050452 | -0.17528 | 122.0324 | 121.9898 | 122.1909 | 121.9542 | -0.43379 | 122.367 | 122.516 | 122.2902 | 118.336 | -122.8076
1775.6719 | 122.6166 | -121.9162 | 0.5722 | 1.4211e-13 | -0.0037991 | -0.013077 | -0.04517 | -0.040002 | -0.010002 | -0.00083919 | -0.016222 | 0.0093796 | 0.034709 | 0.0031069 | 0.03777 | 0.037675 | 0.051771 | 0.014482 | 0.1208 | 0.08278 | 0.28848 | 0.1201 | -121.5957 | -3.6031 | -121.7218 | 0.45079 | 0.60893 | 0.37862 | -122.2675 | 122.0363 | -0.4514 | 121.9539 | 121.9307 | -0.10562 | -0.48942 | -0.28372 | -0.35127 | -0.12142 | 0.32045 | 0.19437 | 0.54564 | 0.03672 | -0.19359 | 122.037 | 121.999 | 122.2047 | 121.968 | -0.4521 | 122.367 | 122.5251 | 122.2948 | 118.3131 | -122.8397
1777.4531 | 122.6212 | -121.9208 | 0.53558 | 1.4211e-13 | -0.0040129 | -0.012863 | -0.044743 | -0.040216 | -0.010429 | -0.00083919 | -0.016222 | 0.009166 | 0.034496 | 0.0033205 | 0.037556 | 0.033096 | 0.051771 | 0.005325 | 0.1208 | 0.087359 | 0.28848 | 0.11094 | -121.6095 | -3.6397 | -121.7264 | 0.44621 | 0.59977 | 0.37862 | -122.2812 | 122.0317 | -0.41478 | 121.9539 | 121.9261 | -0.10562 | -0.44822 | -0.2471 | -0.36043 | -0.089374 | 0.31129 | 0.19437 | 0.55479 | 0.064185 | -0.15697 | 122.0416 | 122.0081 | 122.2093 | 121.9725 | -0.42464 | 122.367 | 122.5205 | 122.2994 | 118.2811 | -122.8168
1779.2188 | 122.5433 | -121.9849 | 0.56305 | 1.4211e-13 | -0.0040129 | -0.012863 | -0.044529 | -0.039788 | -0.010215 | 0.0067908 | -0.016008 | 0.0095932 | 0.034068 | 0.0037479 | 0.037983 | 0.033096 | 0.038035 | 0.014482 | 0.1208 | 0.08278 | 0.27932 | 0.11094 | -121.6186 | -3.6855 | -121.7401 | 0.43247 | 0.59061 | 0.37404 | -122.2949 | 122.0958 | -0.44224 | 122.018 | 121.9993 | -0.09646 | -0.48027 | -0.28373 | -0.31008 | -0.13057 | 0.36622 | 0.24472 | 0.5548 | 0.027561 | -0.18901 | 122.1057 | 122.0676 | 122.2642 | 122.0229 | -0.45211 | 122.4173 | 122.5755 | 122.3589 | 118.2994 | -122.858
1780.9531 | 122.6669 | -121.9574 | 0.48523 | 1.4211e-13 | -0.0042265 | -0.012863 | -0.044743 | -0.040002 | -0.010429 | -0.0084697 | -0.016222 | 0.0093796 | 0.034496 | 0.0033205 | 0.037556 | 0.037675 | 0.033457 | 0.014482 | 0.1208 | 0.08278 | 0.28848 | 0.10636 | -121.6644 | -3.7221 | -121.7722 | 0.39127 | 0.55398 | 0.3191 | -122.327 | 122.0638 | -0.36442 | 121.9951 | 121.9719 | -0.091881 | -0.40245 | -0.19675 | -0.3696 | -0.093962 | 0.29297 | 0.1852 | 0.5548 | 0.068753 | -0.16613 | 122.0782 | 122.0402 | 122.2459 | 121.9909 | -0.37887 | 122.3487 | 122.5114 | 122.2765 | 118.2353 | -122.8122
1782.7344 | 122.6166 | -121.9849 | 0.51727 | 1.4211e-13 | -0.0040129 | -0.013077 | -0.04517 | -0.040429 | -0.010643 | -0.00083919 | -0.016008 | 0.0093796 | 0.034923 | 0.0037479 | 0.03777 | 0.037675 | 0.042614 | 0.005325 | 0.1208 | 0.08278 | 0.28848 | 0.10636 | -121.6599 | -3.7633 | -121.763 | 0.40958 | 0.55398 | 0.33741 | -122.3224 | 122.0912 | -0.39647 | 122.0225 | 121.9902 | -0.10104 | -0.43449 | -0.22879 | -0.33755 | -0.10769 | 0.32501 | 0.22183 | 0.55938 | 0.036709 | -0.17986 | 122.1057 | 122.0676 | 122.2733 | 122.0275 | -0.41091 | 122.3944 | 122.5388 | 122.3223 | 118.2215 | -122.8397
1784.5156 | 122.5754 | -121.9849 | 0.55389 | 1.4211e-13 | -0.0042265 | -0.01265 | -0.044743 | -0.040002 | -0.010002 | -0.0084697 | -0.016435 | 0.009166 | 0.034709 | 0.0035341 | 0.037556 | 0.028518 | 0.038035 | 0.014482 | 0.12538 | 0.08278 | 0.2839 | 0.1201 | -121.6507 | -3.8 | -121.7722 | 0.40958 | 0.55856 | 0.35572 | -122.3316 | 122.105 | -0.42851 | 122.0134 | 121.9993 | -0.10562 | -0.47111 | -0.26999 | -0.34671 | -0.14431 | 0.33417 | 0.21267 | 0.55938 | 0.004666 | -0.19817 | 122.1102 | 122.0676 | 122.2688 | 122.0229 | -0.43379 | 122.3944 | 122.5434 | 122.3406 | 118.1849 | -122.8855
1786.2344 | 122.5525 | -122.0261 | 0.50812 | 1.4211e-13 | -0.0040129 | -0.013291 | -0.044957 | -0.040216 | -0.010215 | -0.0084697 | -0.016222 | 0.0095932 | 0.034496 | 0.0037479 | 0.037556 | 0.028518 | 0.042614 | 0.009904 | 0.12538 | 0.08278 | 0.27932 | 0.10636 | -121.6827 | -3.8412 | -121.7905 | 0.38669 | 0.53109 | 0.30994 | -122.3545 | 122.1324 | -0.38274 | 122.0546 | 122.036 | -0.096459 | -0.42534 | -0.22879 | -0.3284 | -0.12143 | 0.34332 | 0.23555 | 0.56395 | 0.022971 | -0.19818 | 122.1514 | 122.1088 | 122.3054 | 122.0687 | -0.40175 | 122.4128 | 122.5572 | 122.336 | 118.1849 | -122.8626
1788 | 122.5845 | -122.0306 | 0.50354 | 1.4211e-13 | -0.0044401 | -0.013077 | -0.04517 | -0.040002 | -0.010215 | -0.0161 | -0.016222 | 0.009166 | 0.034496 | 0.0035341 | 0.037556 | 0.033096 | 0.038035 | 0.009904 | 0.11622 | 0.073622 | 0.2839 | 0.1201 | -121.6873 | -3.8778 | -121.8042 | 0.37753 | 0.52651 | 0.2962 | -122.3545 | 122.1507 | -0.38731 | 122.0637 | 122.0405 | -0.1102 | -0.42992 | -0.21964 | -0.32382 | -0.12601 | 0.34332 | 0.22639 | 0.55022 | 0.02297 | -0.20734 | 122.1469 | 122.1043 | 122.3145 | 122.0687 | -0.38344 | 122.4082 | 122.5572 | 122.3268 | 118.1528 | -122.858
1789.7812 | 122.6486 | -121.9986 | 0.48065 | 1.4211e-13 | -0.0044401 | -0.012863 | -0.04517 | -0.040002 | -0.010429 | 0.0067908 | -0.015794 | 0.009166 | 0.034709 | 0.0037479 | 0.03777 | 0.037675 | 0.042614 | 0.005325 | 0.12538 | 0.078201 | 0.2839 | 0.11094 | -121.7056 | -3.9328 | -121.8134 | 0.37295 | 0.51277 | 0.30078 | -122.3728 | 122.1095 | -0.35527 | 122.0363 | 122.0039 | -0.10562 | -0.40245 | -0.19675 | -0.37418 | -0.1077 | 0.29296 | 0.18519 | 0.55938 | 0.032122 | -0.17987 | 122.124 | 122.0768 | 122.2825 | 122.0412 | -0.36971 | 122.3715 | 122.5114 | 122.2994 | 118.0658 | -122.8534
1791.5625 | 122.5937 | -122.0444 | 0.48065 | 1.4211e-13 | -0.0042265 | -0.01265 | -0.04517 | -0.040002 | -0.010429 | -0.0084697 | -0.016008 | 0.0093796 | 0.034282 | 0.0037479 | 0.03777 | 0.033096 | 0.038035 | 0.009904 | 0.11622 | 0.087359 | 0.2839 | 0.10178 | -121.6919 | -3.9648 | -121.818 | 0.35922 | 0.5082 | 0.2962 | -122.3819 | 122.1462 | -0.36443 | 122.0775 | 122.0543 | -0.09188 | -0.39329 | -0.19675 | -0.33756 | -0.12143 | 0.35247 | 0.22639 | 0.56395 | 0.027544 | -0.18445 | 122.1606 | 122.1317 | 122.3283 | 122.0824 | -0.37887 | 122.4036 | 122.5526 | 122.3406 | 118.0796 | -122.8626
1793.3438 | 122.6761 | -122.0032 | 0.45776 | 1.4211e-13 | -0.0040129 | -0.013077 | -0.04517 | -0.040002 | -0.010215 | -0.0161 | -0.016008 | 0.0095932 | 0.034709 | 0.0035341 | 0.03777 | 0.028518 | 0.038035 | 0.009904 | 0.1208 | 0.078201 | 0.28848 | 0.11094 | -121.7056 | -4.006 | -121.8226 | 0.35922 | 0.5082 | 0.28704 | -122.3819 | 122.1141 | -0.33696 | 122.0317 | 122.0131 | -0.10104 | -0.37956 | -0.16928 | -0.37876 | -0.098546 | 0.29753 | 0.18061 | 0.55938 | 0.050432 | -0.17072 | 122.124 | 122.0814 | 122.2917 | 122.0412 | -0.34682 | 122.3624 | 122.5114 | 122.2902 | 117.9972 | -122.8397
1795.125 | 122.6303 | -122.0444 | 0.46234 | 1.4211e-13 | -0.0042265 | -0.01265 | -0.045384 | -0.040429 | -0.010215 | 0.0067908 | -0.015794 | 0.0093796 | 0.034709 | 0.0039615 | 0.037556 | 0.028518 | 0.042614 | 0.000747 | 0.11622 | 0.078201 | 0.2839 | 0.11552 | -121.7148 | -4.0381 | -121.8317 | 0.35006 | 0.51277 | 0.28247 | -122.3957 | 122.1599 | -0.34612 | 122.0729 | 122.0451 | -0.11477 | -0.38414 | -0.17844 | -0.3513 | -0.11228 | 0.32958 | 0.21265 | 0.56396 | 0.050433 | -0.17987 | 122.1606 | 122.1226 | 122.3283 | 122.087 | -0.34682 | 122.3944 | 122.5571 | 122.3268 | 118.0063 | -122.858
1796.8594 | 122.6074 | -122.0306 | 0.48981 | 1.4211e-13 | -0.0042265 | -0.012863 | -0.044957 | -0.040002 | -0.010002 | -0.0084697 | -0.016008 | 0.0093796 | 0.034709 | 0.0035341 | 0.037556 | 0.023939 | 0.033457 | 0.005325 | 0.1208 | 0.08278 | 0.2839 | 0.11094 | -121.7056 | -4.0884 | -121.8363 | 0.3638 | 0.5082 | 0.29162 | -122.3819 | 122.1416 | -0.369 | 122.0546 | 122.036 | -0.10562 | -0.40703 | -0.2059 | -0.3513 | -0.12601 | 0.325 | 0.19434 | 0.54564 | 0.018389 | -0.19818 | 122.1514 | 122.1134 | 122.3145 | 122.0641 | -0.37887 | 122.3944 | 122.5388 | 122.3223 | 117.9422 | -122.8717
1798.6406 | 122.6395 | -122.0581 | 0.4715 | 1.4211e-13 | -0.0042265 | -0.012863 | -0.044957 | -0.040216 | -0.010429 | -0.00083919 | -0.015794 | 0.0093796 | 0.034709 | 0.0037479 | 0.03777 | 0.028518 | 0.042614 | 0.005325 | 0.1208 | 0.08278 | 0.27932 | 0.11552 | -121.7148 | -4.1342 | -121.8409 | 0.35464 | 0.50362 | 0.28247 | -122.3957 | 122.1736 | -0.35069 | 122.0866 | 122.0634 | -0.1102 | -0.38872 | -0.19217 | -0.33757 | -0.11686 | 0.34331 | 0.21723 | 0.5548 | 0.03212 | -0.18903 | 122.1789 | 122.1409 | 122.3374 | 122.1007 | -0.35598 | 122.4127 | 122.5617 | 122.3406 | 117.9239 | -122.8672
1800.375 | 122.6807 | -122.0078 | 0.45319 | 1.4211e-13 | -0.0042265 | -0.013291 | -0.044957 | -0.040002 | -0.010643 | -0.00083919 | -0.016008 | 0.009807 | 0.034709 | 0.0035341 | 0.03777 | 0.028518 | 0.047193 | 0.009904 | 0.11622 | 0.08278 | 0.27475 | 0.10178 | -121.7194 | -4.18 | -121.8317 | 0.35922 | 0.51735 | 0.27789 | -122.3865 | 122.1095 | -0.33696 | 122.0363 | 122.0177 | -0.09188 | -0.37041 | -0.17844 | -0.37877 | -0.093968 | 0.28838 | 0.17603 | 0.5548 | 0.064167 | -0.1753 | 122.124 | 122.0905 | 122.2825 | 122.0549 | -0.3514 | 122.367 | 122.5251 | 122.2856 | 117.8277 | -122.8397
1802.1562 | 122.6486 | -122.081 | 0.43945 | 1.4211e-13 | -0.0044401 | -0.012863 | -0.04517 | -0.039788 | -0.010429 | -0.0084697 | -0.016222 | 0.0093796 | 0.034709 | 0.0037479 | 0.03777 | 0.023939 | 0.042614 | 0.014482 | 0.11622 | 0.08278 | 0.2839 | 0.097205 | -121.7194 | -4.2166 | -121.85 | 0.35006 | 0.49904 | 0.28704 | -122.414 | 122.1782 | -0.32323 | 122.1049 | 122.0955 | -0.082723 | -0.35667 | -0.15555 | -0.33299 | -0.089392 | 0.36162 | 0.23096 | 0.56396 | 0.059585 | -0.15241 | 122.1972 | 122.1638 | 122.3649 | 122.1236 | -0.34225 | 122.4311 | 122.58 | 122.368 | 117.8644 | -122.8534
1803.8906 | 122.7081 | -122.0398 | 0.43488 | 1.4211e-13 | -0.0042265 | -0.013077 | -0.045384 | -0.040002 | -0.010856 | 0.0067908 | -0.016222 | 0.009807 | 0.034923 | 0.0037479 | 0.03777 | 0.019361 | 0.042614 | 0.000747 | 0.12538 | 0.078201 | 0.27475 | 0.11552 | -121.7331 | -4.2716 | -121.85 | 0.34548 | 0.48988 | 0.27331 | -122.4094 | 122.1553 | -0.30949 | 122.0592 | 122.0405 | -0.11477 | -0.35667 | -0.16013 | -0.36961 | -0.089393 | 0.30668 | 0.18976 | 0.55938 | 0.055006 | -0.16157 | 122.1652 | 122.118 | 122.3145 | 122.0824 | -0.31935 | 122.3853 | 122.5297 | 122.3131 | 117.7682 | -122.8443
1805.6875 | 122.5754 | -122.0993 | 0.48523 | 1.4211e-13 | -0.0046539 | -0.013077 | -0.04517 | -0.039788 | -0.010215 | -0.0084697 | -0.015794 | 0.0093796 | 0.034923 | 0.0037479 | 0.03777 | 0.023939 | 0.033457 | 0.000747 | 0.1208 | 0.078201 | 0.27017 | 0.10636 | -121.7377 | -4.3128 | -121.8546 | 0.35006 | 0.49446 | 0.27789 | -122.4186 | 122.2057 | -0.36442 | 122.1232 | 122.1001 | -0.10562 | -0.40703 | -0.21506 | -0.31926 | -0.13517 | 0.36161 | 0.24469 | 0.56396 | 0.009231 | -0.20734 | 122.2201 | 122.1775 | 122.3695 | 122.1328 | -0.37887 | 122.4494 | 122.5938 | 122.3772 | 117.7865 | -122.9038
1807.4688 | 122.6624 | -122.0673 | 0.45776 | 1.4211e-13 | -0.0044401 | -0.013077 | -0.044743 | -0.039788 | -0.010643 | -0.0084697 | -0.015794 | 0.0095932 | 0.034709 | 0.0041753 | 0.03777 | 0.033096 | 0.042614 | 0.009904 | 0.11622 | 0.08278 | 0.27932 | 0.11552 | -121.7331 | -4.3677 | -121.8546 | 0.35464 | 0.49904 | 0.28704 | -122.4094 | 122.1828 | -0.34154 | 122.1004 | 122.0772 | -0.10562 | -0.37498 | -0.17844 | -0.34215 | -0.10312 | 0.33415 | 0.21265 | 0.5548 | 0.041274 | -0.17072 | 122.1835 | 122.15 | 122.3466 | 122.1099 | -0.34224 | 122.4219 | 122.5663 | 122.3543 | 117.6995 | -122.8672
1809.1875 | 122.5571 | -122.0947 | 0.48981 | 1.4211e-13 | -0.0046539 | -0.013077 | -0.04517 | -0.040429 | -0.010215 | -0.00083919 | -0.016222 | 0.009166 | 0.034496 | 0.0037479 | 0.037556 | 0.028518 | 0.038035 | 0.000747 | 0.1208 | 0.078201 | 0.27475 | 0.12468 | -121.724 | -4.4135 | -121.8546 | 0.35464 | 0.50362 | 0.27789 | -122.4094 | 122.2194 | -0.369 | 122.1232 | 122.0955 | -0.12393 | -0.41161 | -0.21506 | -0.31468 | -0.13517 | 0.37077 | 0.24012 | 0.5548 | 0.01381 | -0.21192 | 122.2155 | 122.1729 | 122.3695 | 122.1328 | -0.36513 | 122.4494 | 122.5983 | 122.3726 | 117.6812 | -122.8992
1810.9844 | 122.6532 | -122.0947 | 0.46692 | 1.4211e-13 | -0.0046539 | -0.013291 | -0.044743 | -0.040002 | -0.010429 | 0.014421 | -0.015581 | 0.0093796 | 0.034923 | 0.0039615 | 0.037556 | 0.028518 | 0.033457 | 0.009904 | 0.11622 | 0.073622 | 0.27475 | 0.092626 | -121.7377 | -4.4593 | -121.85 | 0.35464 | 0.5082 | 0.27331 | -122.4186 | 122.1874 | -0.35069 | 122.1232 | 122.1046 | -0.082722 | -0.3933 | -0.19217 | -0.32384 | -0.11228 | 0.35704 | 0.24469 | 0.56853 | 0.041277 | -0.19361 | 122.211 | 122.1683 | 122.3695 | 122.1282 | -0.37429 | 122.4494 | 122.6029 | 122.368 | 117.6354 | -122.8855
1812.7656 | 122.7173 | -122.0215 | 0.45776 | 1.4211e-13 | -0.0046539 | -0.013077 | -0.044957 | -0.040216 | -0.010215 | -0.00083919 | -0.016222 | 0.0095932 | 0.034282 | 0.0037479 | 0.037556 | 0.028518 | 0.033457 | 0.009904 | 0.11622 | 0.08278 | 0.27475 | 0.11552 | -121.7377 | -4.5188 | -121.85 | 0.34548 | 0.49446 | 0.28247 | -122.414 | 122.137 | -0.34154 | 122.05 | 122.0314 | -0.10562 | -0.37498 | -0.18302 | -0.3925 | -0.11228 | 0.28379 | 0.17145 | 0.56396 | 0.036696 | -0.1753 | 122.1377 | 122.1043 | 122.2962 | 122.0549 | -0.34224 | 122.367 | 122.5159 | 122.304 | 117.5027 | -122.8718
1814.5 | 122.7127 | -122.0581 | 0.43488 | 1.4211e-13 | -0.0046539 | -0.013291 | -0.04517 | -0.040216 | -0.010215 | -0.00083919 | -0.016222 | 0.0093796 | 0.034496 | 0.0035341 | 0.03777 | 0.028518 | 0.038035 | 0.009904 | 0.1208 | 0.073622 | 0.27932 | 0.10636 | -121.7468 | -4.5646 | -121.8683 | 0.3409 | 0.49446 | 0.26873 | -122.4277 | 122.1645 | -0.31407 | 122.0866 | 122.068 | -0.096459 | -0.36125 | -0.15555 | -0.36962 | -0.093971 | 0.31126 | 0.18976 | 0.55938 | 0.059585 | -0.16614 | 122.1789 | 122.1317 | 122.3374 | 122.0961 | -0.32851 | 122.399 | 122.5526 | 122.3268 | 117.4935 | -122.8626
1816.2812 | 122.58 | -122.1405 | 0.46234 | 1.4211e-13 | -0.0044401 | -0.013291 | -0.04517 | -0.040002 | -0.010215 | -0.00083919 | -0.016222 | 0.009166 | 0.034709 | 0.0035341 | 0.037556 | 0.028518 | 0.042614 | 0.005325 | 0.11622 | 0.073622 | 0.27475 | 0.11094 | -121.7514 | -4.6104 | -121.8729 | 0.33632 | 0.4853 | 0.26873 | -122.4323 | 122.2514 | -0.34612 | 122.169 | 122.1458 | -0.10562 | -0.38872 | -0.1876 | -0.2918 | -0.12602 | 0.38908 | 0.26758 | 0.55938 | 0.022962 | -0.19361 | 122.2567 | 122.2141 | 122.4152 | 122.1831 | -0.3514 | 122.4768 | 122.6258 | 122.4092 | 117.5301 | -122.8946
1818.0469 | 122.6349 | -122.1268 | 0.46234 | 1.4211e-13 | -0.0044401 | -0.012863 | -0.04517 | -0.039788 | -0.010643 | 0.0067908 | -0.016008 | 0.0093796 | 0.034709 | 0.0037479 | 0.037983 | 0.019361 | 0.033457 | 0.005325 | 0.11622 | 0.073622 | 0.27475 | 0.10636 | -121.7697 | -4.6653 | -121.8867 | 0.32717 | 0.47614 | 0.255 | -122.4506 | 122.2331 | -0.34612 | 122.1461 | 122.1321 | -0.10104 | -0.38872 | -0.1876 | -0.32385 | -0.13517 | 0.35703 | 0.24011 | 0.56396 | 0.013804 | -0.20735 | 122.243 | 122.2004 | 122.4015 | 122.1602 | -0.35598 | 122.4539 | 122.6029 | 122.3818 | 117.4614 | -122.913
1819.7656 | 122.7036 | -122.0764 | 0.42114 | 1.4211e-13 | -0.0046539 | -0.013291 | -0.044957 | -0.040216 | -0.010429 | -0.0161 | -0.015794 | 0.0095932 | 0.034709 | 0.0037479 | 0.037556 | 0.028518 | 0.0243 | 0.000747 | 0.11622 | 0.078201 | 0.27475 | 0.088047 | -121.7743 | -4.7157 | -121.8958 | 0.32717 | 0.47157 | 0.25957 | -122.4552 | 122.1645 | -0.30492 | 122.1049 | 122.0772 | -0.0873 | -0.34294 | -0.1464 | -0.37878 | -0.093975 | 0.3021 | 0.1806 | 0.55938 | 0.050424 | -0.16157 | 122.1926 | 122.1546 | 122.3512 | 122.1007 | -0.3331 | 122.4036 | 122.548 | 122.336 | 117.3607 | -122.8763
1821.5625 | 122.7356 | -122.0947 | 0.42114 | 1.4211e-13 | -0.0044401 | -0.013077 | -0.045384 | -0.040002 | -0.010429 | -0.0161 | -0.016008 | 0.0093796 | 0.034709 | 0.0039615 | 0.037983 | 0.023939 | 0.038035 | 0.009904 | 0.11622 | 0.078201 | 0.27017 | 0.092626 | -121.7697 | -4.7615 | -121.8958 | 0.31801 | 0.47614 | 0.255 | -122.4598 | 122.1874 | -0.30492 | 122.1187 | 122.1046 | -0.082722 | -0.34294 | -0.15098 | -0.36505 | -0.10313 | 0.32499 | 0.19891 | 0.56396 | 0.055002 | -0.16615 | 122.211 | 122.1729 | 122.3649 | 122.1328 | -0.32852 | 122.4127 | 122.5709 | 122.3497 | 117.3332 | -122.8809
1823.2656 | 122.699 | -122.0901 | 0.40283 | 1.4211e-13 | -0.0048675 | -0.013291 | -0.04517 | -0.040216 | -0.010215 | -0.0161 | -0.016008 | 0.0093796 | 0.034709 | 0.0035341 | 0.037556 | 0.023939 | 0.028878 | 0.005325 | 0.11622 | 0.069043 | 0.27475 | 0.11552 | -121.7835 | -4.8119 | -121.9004 | 0.31343 | 0.46699 | 0.25957 | -122.4689 | 122.2057 | -0.28661 | 122.1141 | 122.0955 | -0.1102 | -0.33379 | -0.12809 | -0.37879 | -0.089399 | 0.30667 | 0.18975 | 0.56854 | 0.064156 | -0.14326 | 122.2064 | 122.1592 | 122.3649 | 122.119 | -0.28731 | 122.4036 | 122.5571 | 122.3497 | 117.2783 | -122.8718
1825.0469 | 122.699 | -122.1268 | 0.3891 | 1.4211e-13 | -0.0048675 | -0.012863 | -0.044743 | -0.040216 | -0.010643 | -0.00083919 | -0.016008 | 0.0095932 | 0.034709 | 0.0041753 | 0.03777 | 0.023939 | 0.033457 | 0.005325 | 0.10707 | 0.073622 | 0.27017 | 0.10178 | -121.7926 | -4.8714 | -121.9233 | 0.29512 | 0.4441 | 0.23668 | -122.4873 | 122.2286 | -0.28203 | 122.1507 | 122.1321 | -0.096459 | -0.31548 | -0.11893 | -0.36048 | -0.09398 | 0.33413 | 0.20348 | 0.56396 | 0.054996 | -0.15242 | 122.2338 | 122.2004 | 122.3969 | 122.1602 | -0.28731 | 122.4219 | 122.5709 | 122.3635 | 117.2554 | -122.8763
1826.7656 | 122.7173 | -122.1176 | 0.36163 | 1.4211e-13 | -0.0046539 | -0.013077 | -0.044957 | -0.039788 | -0.010643 | 0.0067908 | -0.016222 | 0.0093796 | 0.034282 | 0.0037479 | 0.037983 | 0.019361 | 0.028878 | 0.005325 | 0.11165 | 0.078201 | 0.27475 | 0.11552 | -121.8064 | -4.9218 | -121.937 | 0.28596 | 0.44867 | 0.23668 | -122.4964 | 122.2331 | -0.24999 | 122.137 | 122.1229 | -0.1102 | -0.28343 | -0.086888 | -0.37879 | -0.075671 | 0.31124 | 0.18059 | 0.55938 | 0.087041 | -0.12495 | 122.2293 | 122.1958 | 122.3924 | 122.1465 | -0.24611 | 122.4036 | 122.5663 | 122.3543 | 117.1959 | -122.858
1828.5625 | 122.6395 | -122.1588 | 0.41657 | 1.4211e-13 | -0.0050813 | -0.013077 | -0.04517 | -0.040429 | -0.010215 | -0.00083919 | -0.016222 | 0.0089522 | 0.034496 | 0.0035341 | 0.03777 | 0.014783 | 0.0243 | -0.003831 | 0.11622 | 0.069043 | 0.27017 | 0.097205 | -121.8064 | -4.9813 | -121.937 | 0.28596 | 0.43494 | 0.2321 | -122.501 | 122.256 | -0.30034 | 122.1736 | 122.155 | -0.10104 | -0.34752 | -0.1464 | -0.34217 | -0.1306 | 0.35244 | 0.22178 | 0.56396 | 0.018373 | -0.18446 | 122.275 | 122.2279 | 122.429 | 122.1831 | -0.31936 | 122.4448 | 122.5938 | 122.3909 | 117.1775 | -122.9176
1830.2812 | 122.7081 | -122.0947 | 0.4303 | 1.4211e-13 | -0.0048675 | -0.013077 | -0.044957 | -0.040002 | -0.010215 | -0.00083919 | -0.016222 | 0.009166 | 0.034282 | 0.0037479 | 0.037983 | 0.010204 | 0.033457 | -0.003831 | 0.10707 | 0.064464 | 0.26101 | 0.088047 | -121.7652 | -5.0316 | -121.8867 | 0.33632 | 0.48072 | 0.25957 | -122.4598 | 122.1828 | -0.32323 | 122.1049 | 122.0909 | -0.091878 | -0.36583 | -0.16929 | -0.36505 | -0.093973 | 0.32957 | 0.20806 | 0.57311 | 0.050426 | -0.17072 | 122.2018 | 122.1592 | 122.3557 | 122.1282 | -0.34225 | 122.4311 | 122.5755 | 122.3543 | 117.0631 | -122.8901
1832.0469 | 122.6028 | -122.1405 | 0.45776 | 1.4211e-13 | -0.0046539 | -0.013077 | -0.04517 | -0.040002 | -0.010429 | -0.00083919 | -0.015794 | 0.009166 | 0.034709 | 0.0037479 | 0.03777 | 0.014783 | 0.028878 | -0.003831 | 0.10249 | 0.069043 | 0.27017 | 0.10178 | -121.7743 | -5.0912 | -121.8912 | 0.33175 | 0.48072 | 0.26415 | -122.4506 | 122.2423 | -0.35527 | 122.1553 | 122.1367 | -0.10562 | -0.38872 | -0.1876 | -0.31012 | -0.12602 | 0.36618 | 0.24926 | 0.55938 | 0.02296 | -0.19361 | 122.243 | 122.2095 | 122.4107 | 122.1694 | -0.35598 | 122.4723 | 122.6212 | 122.4047 | 117.0493 | -122.9084
1833.8281 | 122.6028 | -122.1313 | 0.45776 | 1.4211e-13 | -0.0050813 | -0.013077 | -0.044957 | -0.040002 | -0.010002 | -0.00083919 | -0.016008 | 0.0093796 | 0.034496 | 0.0037479 | 0.037556 | 0.019361 | 0.028878 | 0.000747 | 0.11165 | 0.073622 | 0.27017 | 0.088047 | -121.7789 | -5.1553 | -121.9004 | 0.31801 | 0.47614 | 0.26415 | -122.4689 | 122.2194 | -0.34612 | 122.1507 | 122.1321 | -0.0873 | -0.38414 | -0.1876 | -0.33759 | -0.13975 | 0.35245 | 0.23095 | 0.56854 | 0.018381 | -0.19361 | 122.243 | 122.205 | 122.4015 | 122.1602 | -0.36972 | 122.4494 | 122.6075 | 122.3955 | 116.9761 | -122.9267
1835.6094 | 122.7264 | -122.0993 | 0.42114 | 1.4211e-13 | -0.0046539 | -0.013077 | -0.045384 | -0.039788 | -0.010429 | -0.00083919 | -0.016008 | 0.0095932 | 0.034496 | 0.0039615 | 0.037129 | 0.010204 | 0.028878 | 0.000747 | 0.10249 | 0.073622 | 0.26101 | 0.11094 | -121.7835 | -5.2056 | -121.8958 | 0.32259 | 0.4853 | 0.26873 | -122.4735 | 122.2102 | -0.31865 | 122.1095 | 122.1001 | -0.1102 | -0.34752 | -0.16013 | -0.37421 | -0.098553 | 0.31583 | 0.20348 | 0.57769 | 0.06416 | -0.15241 | 122.2018 | 122.1729 | 122.3603 | 122.1282 | -0.3102 | 122.4219 | 122.5846 | 122.368 | 116.8937 | -122.8947
1837.3906 | 122.6074 | -122.1497 | 0.45776 | 1.4211e-13 | -0.0048675 | -0.013077 | -0.044957 | -0.040429 | -0.010643 | -0.00083919 | -0.016222 | 0.0093796 | 0.034282 | 0.0039615 | 0.037983 | 0.014783 | 0.028878 | 0.005325 | 0.10249 | 0.064464 | 0.26559 | 0.10636 | -121.7835 | -5.2697 | -121.905 | 0.31343 | 0.47157 | 0.26415 | -122.4735 | 122.256 | -0.35527 | 122.1644 | 122.155 | -0.10104 | -0.3933 | -0.19218 | -0.32386 | -0.14433 | 0.36618 | 0.24468 | 0.56854 | 0.013803 | -0.19361 | 122.2521 | 122.2141 | 122.4152 | 122.1785 | -0.3514 | 122.4631 | 122.6212 | 122.4138 | 116.8799 | -122.9313
1839.0938 | 122.7219 | -122.0901 | 0.41199 | 1.4211e-13 | -0.0050813 | -0.013077 | -0.045384 | -0.040216 | -0.010856 | -0.00083919 | -0.016008 | 0.0095932 | 0.034709 | 0.0039615 | 0.037556 | 0.014783 | 0.028878 | 0.005325 | 0.10707 | 0.069043 | 0.25643 | 0.11094 | -121.7881 | -5.3338 | -121.9096 | 0.31801 | 0.46699 | 0.26415 | -122.4735 | 122.2011 | -0.30492 | 122.1049 | 122.0955 | -0.10562 | -0.34294 | -0.15556 | -0.38336 | -0.093976 | 0.30209 | 0.18059 | 0.56396 | 0.055001 | -0.14783 | 122.1972 | 122.1592 | 122.3466 | 122.119 | -0.30105 | 122.4082 | 122.5571 | 122.3543 | 116.7563 | -122.8855
1840.875 | 122.7356 | -122.0947 | 0.44403 | 1.4211e-13 | -0.0044401 | -0.013077 | -0.045384 | -0.040216 | -0.010429 | -0.00083919 | -0.015794 | 0.0093796 | 0.034496 | 0.0041753 | 0.03777 | 0.014783 | 0.0243 | 0.009904 | 0.10707 | 0.073622 | 0.26101 | 0.12468 | -121.7743 | -5.3888 | -121.8958 | 0.33175 | 0.47614 | 0.26873 | -122.4644 | 122.2194 | -0.33696 | 122.1095 | 122.1046 | -0.11478 | -0.37041 | -0.18302 | -0.36963 | -0.11228 | 0.32041 | 0.19891 | 0.56854 | 0.032114 | -0.1753 | 122.2018 | 122.1683 | 122.3557 | 122.119 | -0.31935 | 122.4265 | 122.5709 | 122.3635 | 116.7059 | -122.9084
1842.6719 | 122.6807 | -122.1176 | 0.42572 | 1.4211e-13 | -0.0050813 | -0.013077 | -0.045384 | -0.040216 | -0.010643 | -0.0084697 | -0.016222 | 0.0093796 | 0.034709 | 0.0039615 | 0.03777 | 0.010204 | 0.028878 | 0.005325 | 0.10707 | 0.069043 | 0.26559 | 0.10178 | -121.8018 | -5.4575 | -121.9096 | 0.31801 | 0.47614 | 0.255 | -122.4918 | 122.2194 | -0.31865 | 122.1278 | 122.1229 | -0.096459 | -0.35668 | -0.16013 | -0.37421 | -0.10771 | 0.31582 | 0.20806 | 0.58227 | 0.050425 | -0.17072 | 122.2247 | 122.1867 | 122.3832 | 122.1465 | -0.32394 | 122.4356 | 122.5938 | 122.3726 | 116.6602 | -122.9175
1844.3906 | 122.7402 | -122.0947 | 0.40741 | 1.4211e-13 | -0.0046539 | -0.013077 | -0.044957 | -0.040216 | -0.010429 | -0.0084697 | -0.016435 | 0.0095932 | 0.034709 | 0.0041753 | 0.037342 | 0.019361 | 0.028878 | 0.014482 | 0.10707 | 0.08278 | 0.26559 | 0.11552 | -121.7881 | -5.5078 | -121.9096 | 0.31343 | 0.47157 | 0.25957 | -122.4781 | 122.2102 | -0.30034 | 122.1141 | 122.1092 | -0.10104 | -0.32463 | -0.14182 | -0.38336 | -0.093977 | 0.30667 | 0.18517 | 0.56854 | 0.064157 | -0.14784 | 122.2018 | 122.1775 | 122.3603 | 122.1236 | -0.29189 | 122.4082 | 122.5663 | 122.3543 | 116.5869 | -122.8855
1846.1719 | 122.699 | -122.1222 | 0.40283 | 1.4211e-13 | -0.0048675 | -0.01265 | -0.044957 | -0.040429 | -0.010429 | -0.0084697 | -0.016435 | 0.0095932 | 0.034709 | 0.0041753 | 0.037983 | 0.019361 | 0.033457 | 0.009904 | 0.10707 | 0.078201 | 0.25643 | 0.10636 | -121.7972 | -5.5857 | -121.9187 | 0.30885 | 0.45325 | 0.255 | -122.4964 | 122.2286 | -0.29576 | 122.1416 | 122.1321 | -0.096459 | -0.32463 | -0.1464 | -0.37422 | -0.093978 | 0.32498 | 0.20348 | 0.57769 | 0.05042 | -0.14784 | 122.2293 | 122.2004 | 122.3786 | 122.1556 | -0.29647 | 122.431 | 122.5754 | 122.3772 | 116.5365 | -122.8992
1847.9688 | 122.7219 | -122.113 | 0.41657 | 1.4211e-13 | -0.0050813 | -0.013077 | -0.04517 | -0.040002 | -0.010429 | -0.0161 | -0.016222 | 0.0095932 | 0.034709 | 0.0035341 | 0.03777 | 0.010204 | 0.028878 | 0.005325 | 0.10707 | 0.073622 | 0.27475 | 0.11552 | -121.7972 | -5.6498 | -121.9187 | 0.31343 | 0.45783 | 0.255 | -122.501 | 122.2286 | -0.3095 | 122.1232 | 122.1184 | -0.1102 | -0.34294 | -0.14182 | -0.38795 | -0.10313 | 0.31582 | 0.19432 | 0.58227 | 0.041266 | -0.16157 | 122.2201 | 122.1867 | 122.3878 | 122.1419 | -0.30104 | 122.4265 | 122.5709 | 122.368 | 116.4633 | -122.9176
1849.6875 | 122.7402 | -122.113 | 0.41657 | 1.4211e-13 | -0.0048675 | -0.013077 | -0.04517 | -0.040216 | -0.010643 | -0.00083919 | -0.015794 | 0.0095932 | 0.034709 | 0.0037479 | 0.03777 | 0.019361 | 0.028878 | 0.009904 | 0.11622 | 0.073622 | 0.27017 | 0.097205 | -121.8064 | -5.7139 | -121.9233 | 0.30885 | 0.45325 | 0.25957 | -122.501 | 122.2102 | -0.30034 | 122.1324 | 122.1229 | -0.087301 | -0.34294 | -0.1464 | -0.38795 | -0.10771 | 0.30667 | 0.18974 | 0.57769 | 0.036687 | -0.15699 | 122.2293 | 122.1867 | 122.3832 | 122.1419 | -0.31936 | 122.4219 | 122.5663 | 122.3726 | 116.3992 | -122.9176
1851.4688 | 122.6395 | -122.1588 | 0.4303 | 1.4211e-13 | -0.0050813 | -0.013291 | -0.04517 | -0.039788 | -0.010856 | -0.00083919 | -0.016222 | 0.0089522 | 0.034496 | 0.0039615 | 0.037983 | 0.023939 | 0.028878 | 0.009904 | 0.10249 | 0.073622 | 0.27017 | 0.1201 | -121.8018 | -5.7826 | -121.9279 | 0.30428 | 0.45325 | 0.25042 | -122.5056 | 122.2789 | -0.32781 | 122.1828 | 122.1687 | -0.1102 | -0.35668 | -0.16013 | -0.34675 | -0.12602 | 0.35702 | 0.23094 | 0.57769 | 0.022954 | -0.17988 | 122.2613 | 122.2324 | 122.429 | 122.1877 | -0.3102 | 122.4631 | 122.6121 | 122.4092 | 116.3763 | -122.9359
1853.25 | 122.6212 | -122.168 | 0.43945 | 1.4211e-13 | -0.0048675 | -0.013077 | -0.045384 | -0.040002 | -0.010643 | 0.014421 | -0.015794 | 0.009166 | 0.034709 | 0.0039615 | 0.037556 | 0.023939 | 0.0243 | 0.005325 | 0.10707 | 0.078201 | 0.27475 | 0.12468 | -121.8201 | -5.8512 | -121.937 | 0.29512 | 0.43952 | 0.24584 | -122.5193 | 122.2926 | -0.33238 | 122.1919 | 122.1733 | -0.11935 | -0.36125 | -0.16471 | -0.35133 | -0.14433 | 0.34786 | 0.23094 | 0.58227 | 6.4e-05 | -0.19361 | 122.275 | 122.2462 | 122.4427 | 122.1923 | -0.31477 | 122.4631 | 122.6075 | 122.4138 | 116.3167 | -122.9588
1854.9844 | 122.5891 | -122.1725 | 0.42572 | 1.4211e-13 | -0.0048675 | -0.013077 | -0.044957 | -0.040216 | -0.010429 | -0.0161 | -0.016222 | 0.0095932 | 0.034496 | 0.0043889 | 0.037983 | 0.023939 | 0.019721 | 0.009904 | 0.11165 | 0.073622 | 0.25643 | 0.1201 | -121.8201 | -5.9291 | -121.937 | 0.28596 | 0.4441 | 0.24584 | -122.5239 | 122.2926 | -0.31407 | 122.1965 | 122.1825 | -0.1102 | -0.3521 | -0.16929 | -0.35134 | -0.13976 | 0.35244 | 0.23552 | 0.58685 | 0.018375 | -0.17988 | 122.2842 | 122.2462 | 122.429 | 122.1923 | -0.30562 | 122.4585 | 122.6166 | 122.4184 | 116.2435 | -122.9496
1856.7812 | 122.7448 | -122.1771 | 0.37537 | 1.4211e-13 | -0.0044401 | -0.012863 | -0.044957 | -0.040216 | -0.010643 | -0.0084697 | -0.016008 | 0.0093796 | 0.034496 | 0.0041753 | 0.037983 | 0.019361 | 0.033457 | 0.014482 | 0.10707 | 0.078201 | 0.27017 | 0.11552 | -121.8247 | -5.9932 | -121.9416 | 0.29512 | 0.43952 | 0.25042 | -122.5239 | 122.2926 | -0.2683 | 122.1965 | 122.1916 | -0.10104 | -0.29716 | -0.1052 | -0.34676 | -0.080247 | 0.35244 | 0.23552 | 0.58227 | 0.064151 | -0.12495 | 122.2842 | 122.2553 | 122.4473 | 122.2106 | -0.25984 | 122.4722 | 122.6166 | 122.4275 | 116.184 | -122.8992
1858.5 | 122.7127 | -122.1588 | 0.37994 | 1.4211e-13 | -0.0050813 | -0.013077 | -0.04517 | -0.040002 | -0.010643 | -0.00083919 | -0.016435 | 0.0095932 | 0.034496 | 0.0039615 | 0.037983 | 0.019361 | 0.038035 | 0.009904 | 0.10707 | 0.078201 | 0.27017 | 0.1201 | -121.8201 | -6.0664 | -121.9462 | 0.28596 | 0.45783 | 0.24584 | -122.5193 | 122.2789 | -0.27288 | 122.1782 | 122.1687 | -0.1102 | -0.30174 | -0.10978 | -0.36049 | -0.093982 | 0.33871 | 0.21263 | 0.57312 | 0.077887 | -0.13411 | 122.2659 | 122.237 | 122.429 | 122.1968 | -0.25984 | 122.4448 | 122.6166 | 122.4047 | 116.0924 | -122.8992
1860.2812 | 122.7448 | -122.1497 | 0.38452 | 1.4211e-13 | -0.0048675 | -0.01265 | -0.04517 | -0.040429 | -0.010429 | 0.0067908 | -0.016435 | 0.010021 | 0.034496 | 0.0041753 | 0.03777 | 0.023939 | 0.0243 | 0.01906 | 0.10707 | 0.069043 | 0.27475 | 0.1201 | -121.8247 | -6.1351 | -121.9416 | 0.29512 | 0.43952 | 0.24584 | -122.5285 | 122.2698 | -0.27745 | 122.1736 | 122.1687 | -0.10104 | -0.31548 | -0.10978 | -0.3788 | -0.089402 | 0.32497 | 0.20805 | 0.58685 | 0.054996 | -0.13868 | 122.2567 | 122.2187 | 122.4244 | 122.174 | -0.26442 | 122.4448 | 122.5892 | 122.3955 | 116.0145 | -122.913
1862.0781 | 122.6212 | -122.2046 | 0.43488 | 1.4211e-13 | -0.0048675 | -0.01265 | -0.04517 | -0.040216 | -0.010856 | -0.0084697 | -0.016435 | 0.0093796 | 0.034496 | 0.0039615 | 0.037342 | 0.023939 | 0.028878 | 0.005325 | 0.10249 | 0.073622 | 0.27017 | 0.11552 | -121.8293 | -6.2038 | -121.9508 | 0.2997 | 0.4441 | 0.24126 | -122.533 | 122.3201 | -0.33239 | 122.2285 | 122.2099 | -0.1102 | -0.36125 | -0.16471 | -0.32845 | -0.13518 | 0.37533 | 0.25382 | 0.58227 | 0.00922 | -0.19362 | 122.3071 | 122.2782 | 122.4748 | 122.2335 | -0.31935 | 122.5043 | 122.6487 | 122.4458 | 116.0008 | -122.9679
1863.875 | 122.6761 | -122.1909 | 0.4303 | 1.4211e-13 | -0.0048675 | -0.012863 | -0.04517 | -0.040429 | -0.010643 | -0.0084697 | -0.016222 | 0.0095932 | 0.034496 | 0.0041753 | 0.037983 | 0.019361 | 0.028878 | 0.009904 | 0.10707 | 0.073622 | 0.27475 | 0.11552 | -121.8293 | -6.2862 | -121.9416 | 0.2997 | 0.44867 | 0.24126 | -122.533 | 122.3064 | -0.32323 | 122.2102 | 122.2008 | -0.10562 | -0.35668 | -0.15555 | -0.34218 | -0.1306 | 0.36159 | 0.24925 | 0.59143 | 0.018376 | -0.18904 | 122.2979 | 122.2645 | 122.4656 | 122.2197 | -0.31478 | 122.4906 | 122.6395 | 122.4321 | 115.9046 | -122.9633
1865.6562 | 122.6807 | -122.1817 | 0.4303 | 1.4211e-13 | -0.0050813 | -0.013077 | -0.04517 | -0.040002 | -0.010429 | -0.0084697 | -0.016008 | 0.0093796 | 0.034709 | 0.0039615 | 0.037556 | 0.019361 | 0.0243 | 0.009904 | 0.11165 | 0.069043 | 0.2839 | 0.11552 | -121.8109 | -6.3595 | -121.9325 | 0.30885 | 0.46241 | 0.24584 | -122.5147 | 122.2972 | -0.31865 | 122.2011 | 122.1916 | -0.10562 | -0.36125 | -0.14639 | -0.33302 | -0.12144 | 0.37075 | 0.24925 | 0.58227 | 0.032112 | -0.18446 | 122.2933 | 122.2507 | 122.4656 | 122.206 | -0.31478 | 122.4906 | 122.6441 | 122.4275 | 115.8222 | -122.945
1867.375 | 122.6898 | -122.168 | 0.41199 | 1.4211e-13 | -0.0050813 | -0.012863 | -0.044957 | -0.040002 | -0.010856 | -0.00083919 | -0.016222 | 0.0095932 | 0.034709 | 0.0041753 | 0.03777 | 0.023939 | 0.033457 | 0.014482 | 0.11622 | 0.078201 | 0.27017 | 0.11552 | -121.8155 | -6.4327 | -121.9416 | 0.2997 | 0.45783 | 0.255 | -122.5193 | 122.2835 | -0.29576 | 122.1919 | 122.1825 | -0.10104 | -0.33379 | -0.14182 | -0.35133 | -0.11229 | 0.35244 | 0.22636 | 0.57769 | 0.045844 | -0.15699 | 122.2842 | 122.2462 | 122.4381 | 122.2014 | -0.29647 | 122.4677 | 122.6258 | 122.423 | 115.7352 | -122.9313
1869.1406 | 122.6303 | -122.1634 | 0.45319 | 1.4211e-13 | -0.0050813 | -0.013291 | -0.045598 | -0.040216 | -0.010643 | -0.00083919 | -0.016008 | 0.0093796 | 0.034709 | 0.0039615 | 0.03777 | 0.019361 | 0.038035 | 0.009904 | 0.10707 | 0.08278 | 0.27475 | 0.11552 | -121.8201 | -6.5151 | -121.9416 | 0.30428 | 0.45325 | 0.24126 | -122.5285 | 122.2789 | -0.34612 | 122.1828 | 122.1733 | -0.10562 | -0.37041 | -0.17844 | -0.36507 | -0.14891 | 0.34328 | 0.22178 | 0.58685 | 6.6e-05 | -0.21193 | 122.2705 | 122.2462 | 122.4381 | 122.2014 | -0.33766 | 122.4677 | 122.6166 | 122.4047 | 115.6482 | -122.9816
1870.875 | 122.7219 | -122.1588 | 0.40283 | 1.4211e-13 | -0.0050813 | -0.012863 | -0.044957 | -0.040429 | -0.010856 | -0.00083919 | -0.016222 | 0.009166 | 0.034923 | 0.0041753 | 0.037983 | 0.028518 | 0.028878 | 0.01906 | 0.11165 | 0.078201 | 0.27932 | 0.11094 | -121.8201 | -6.6113 | -121.937 | 0.30428 | 0.45783 | 0.24584 | -122.5239 | 122.2698 | -0.29119 | 122.1873 | 122.1779 | -0.091882 | -0.32463 | -0.12351 | -0.36507 | -0.098556 | 0.33871 | 0.22178 | 0.58685 | 0.054999 | -0.15699 | 122.2705 | 122.237 | 122.4381 | 122.1877 | -0.29189 | 122.4631 | 122.6166 | 122.4047 | 115.5475 | -122.9267
1872.6719 | 122.7585 | -121.9299 | 0.59052 | 1.4211e-13 | -0.0052949 | -0.013077 | -0.044957 | -0.040002 | -0.010643 | -0.0084697 | -0.016649 | 0.009166 | 0.034496 | 0.0039615 | 0.03777 | 0.028518 | 0.033457 | 0.023639 | 0.12538 | 0.073622 | 0.28848 | 0.11552 | -121.6278 | -6.6617 | -121.7539 | 0.49657 | 0.65471 | 0.41983 | -122.3453 | 122.0455 | -0.46513 | 121.9584 | 121.9536 | -0.091882 | -0.51689 | -0.30203 | -0.41538 | -0.093942 | 0.30213 | 0.17605 | 0.59143 | 0.064196 | -0.17069 | 122.0553 | 122.0036 | 122.2184 | 121.9634 | -0.47499 | 122.4265 | 122.5846 | 122.3498 | 115.2683 | -122.9358
1874.4375 | 122.6669 | -122.0032 | 0.6134 | 1.4211e-13 | -0.0055085 | -0.013077 | -0.04517 | -0.040216 | -0.010429 | -0.0084697 | -0.016222 | 0.0095932 | 0.034923 | 0.0041753 | 0.03777 | 0.033096 | 0.033457 | 0.028217 | 0.11622 | 0.078201 | 0.27475 | 0.12468 | -121.6415 | -6.7532 | -121.763 | 0.48284 | 0.63182 | 0.40151 | -122.359 | 122.1279 | -0.49718 | 122.0363 | 122.0314 | -0.096462 | -0.5352 | -0.33866 | -0.35587 | -0.13057 | 0.36164 | 0.24014 | 0.59601 | 0.018415 | -0.21189 | 122.1194 | 122.0814 | 122.2779 | 122.0366 | -0.48872 | 122.486 | 122.635 | 122.4047 | 115.2499 | -122.9724
1876.1406 | 122.6212 | -122.0123 | 0.61798 | 1.4211e-13 | -0.0055085 | -0.013077 | -0.045384 | -0.040429 | -0.010429 | -0.00083919 | -0.016008 | 0.0093796 | 0.034496 | 0.0046025 | 0.037983 | 0.028518 | 0.038035 | 0.032795 | 0.11622 | 0.078201 | 0.2839 | 0.11552 | -121.6415 | -6.8402 | -121.763 | 0.47826 | 0.64097 | 0.40151 | -122.3682 | 122.1278 | -0.50176 | 122.0408 | 122.0451 | -0.082726 | -0.53978 | -0.33408 | -0.35587 | -0.13972 | 0.37079 | 0.24929 | 0.60516 | 0.022994 | -0.21647 | 122.1286 | 122.0905 | 122.2962 | 122.0504 | -0.50246 | 122.4906 | 122.6533 | 122.4138 | 115.1721 | -122.9862
1877.9375 | 122.6532 | -122.0261 | 0.60425 | 1.4211e-13 | -0.0055085 | -0.013077 | -0.045384 | -0.040429 | -0.010643 | -0.0084697 | -0.016222 | 0.0095932 | 0.034923 | 0.0041753 | 0.037556 | 0.033096 | 0.042614 | 0.032795 | 0.12538 | 0.078201 | 0.2839 | 0.1201 | -121.6415 | -6.9226 | -121.7585 | 0.48742 | 0.64097 | 0.40151 | -122.3453 | 122.1462 | -0.47887 | 122.0592 | 122.0589 | -0.087305 | -0.52605 | -0.32034 | -0.31925 | -0.11683 | 0.38452 | 0.2676 | 0.58685 | 0.036727 | -0.20274 | 122.1514 | 122.1043 | 122.31 | 122.0687 | -0.48415 | 122.5135 | 122.667 | 122.4276 | 115.1034 | -122.9496
1879.7188 | 122.6715 | -122.0444 | 0.60425 | 1.4211e-13 | -0.0050813 | -0.013077 | -0.04517 | -0.040216 | -0.010643 | -0.00083919 | -0.016222 | 0.0093796 | 0.034923 | 0.0043889 | 0.03777 | 0.023939 | 0.042614 | 0.028217 | 0.1208 | 0.073622 | 0.2839 | 0.11552 | -121.6461 | -7.0096 | -121.7676 | 0.48284 | 0.63182 | 0.41067 | -122.359 | 122.1599 | -0.48344 | 122.0683 | 122.0726 | -0.087304 | -0.53063 | -0.32034 | -0.31467 | -0.12141 | 0.39826 | 0.27676 | 0.59143 | 0.02757 | -0.19358 | 122.1652 | 122.118 | 122.3283 | 122.087 | -0.48873 | 122.5272 | 122.6762 | 122.455 | 115.0347 | -122.9633
1881.5156 | 122.6395 | -122.0352 | 0.62256 | 1.4211e-13 | -0.0052949 | -0.01265 | -0.045384 | -0.040429 | -0.010429 | 0.0067908 | -0.016008 | 0.0093796 | 0.034709 | 0.0043889 | 0.038197 | 0.014783 | 0.033457 | 0.028217 | 0.12538 | 0.078201 | 0.27932 | 0.12468 | -121.6507 | -7.0875 | -121.7676 | 0.48284 | 0.6364 | 0.41067 | -122.359 | 122.1599 | -0.49718 | 122.05 | 122.0634 | -0.096462 | -0.54436 | -0.34323 | -0.32383 | -0.13972 | 0.38452 | 0.2676 | 0.59143 | 0.013837 | -0.21189 | 122.1606 | 122.1134 | 122.3145 | 122.0687 | -0.49788 | 122.5181 | 122.6716 | 122.4459 | 114.9477 | -122.9816
1883.2344 | 122.6303 | -122.0169 | 0.60883 | 1.4211e-13 | -0.0055085 | -0.013077 | -0.04517 | -0.040429 | -0.010429 | -0.0161 | -0.016008 | 0.0095932 | 0.034923 | 0.0043889 | 0.03777 | 0.023939 | 0.038035 | 0.037373 | 0.1208 | 0.08278 | 0.27475 | 0.11094 | -121.6415 | -7.1836 | -121.7768 | 0.46452 | 0.63182 | 0.40609 | -122.3636 | 122.1278 | -0.48802 | 122.0408 | 122.0543 | -0.073569 | -0.52605 | -0.33408 | -0.34672 | -0.1443 | 0.37537 | 0.24013 | 0.58685 | 0.022992 | -0.20274 | 122.1377 | 122.0997 | 122.2917 | 122.0549 | -0.49788 | 122.4814 | 122.6487 | 122.423 | 114.8333 | -122.9724
1885.0156 | 122.7768 | -121.9849 | 0.59052 | 1.4211e-13 | -0.0052949 | -0.013077 | -0.044957 | -0.040429 | -0.010429 | -0.00083919 | -0.016222 | 0.0095932 | 0.034709 | 0.0043889 | 0.03777 | 0.023939 | 0.047193 | 0.028217 | 0.11622 | 0.08278 | 0.28848 | 0.1201 | -121.6415 | -7.2752 | -121.7676 | 0.48284 | 0.62724 | 0.41067 | -122.3728 | 122.105 | -0.47429 | 122.0088 | 122.0131 | -0.091883 | -0.50774 | -0.30203 | -0.38792 | -0.10768 | 0.34333 | 0.21725 | 0.60516 | 0.036724 | -0.17985 | 122.1011 | 122.0676 | 122.2733 | 122.0321 | -0.47042 | 122.4677 | 122.6121 | 122.3955 | 114.7097 | -122.9633
1886.7969 | 122.7539 | -122.0123 | 0.58594 | 1.4211e-13 | -0.0057223 | -0.013077 | -0.045384 | -0.040429 | -0.010856 | -0.0084697 | -0.016008 | 0.0093796 | 0.034923 | 0.0041753 | 0.037556 | 0.023939 | 0.038035 | 0.023639 | 0.12538 | 0.08278 | 0.2839 | 0.1201 | -121.6507 | -7.3668 | -121.7768 | 0.47368 | 0.62724 | 0.41525 | -122.3819 | 122.1324 | -0.46056 | 122.0363 | 122.036 | -0.096461 | -0.50316 | -0.30203 | -0.36961 | -0.11226 | 0.36163 | 0.23555 | 0.60516 | 0.041302 | -0.17069 | 122.1377 | 122.0951 | 122.2962 | 122.0504 | -0.46584 | 122.486 | 122.6396 | 122.4276 | 114.6455 | -122.9679
1888.5156 | 122.6212 | -122.0398 | 0.59509 | 1.4211e-13 | -0.0055085 | -0.013505 | -0.045598 | -0.040429 | -0.010643 | -0.00083919 | -0.016222 | 0.0093796 | 0.034496 | 0.0043889 | 0.037556 | 0.033096 | 0.033457 | 0.028217 | 0.11622 | 0.073622 | 0.27932 | 0.11552 | -121.6599 | -7.4584 | -121.7676 | 0.4691 | 0.62724 | 0.40151 | -122.3682 | 122.1553 | -0.47887 | 122.0729 | 122.068 | -0.087304 | -0.52147 | -0.31577 | -0.32841 | -0.12599 | 0.37994 | 0.27218 | 0.60058 | 0.032146 | -0.19358 | 122.156 | 122.1134 | 122.3191 | 122.0733 | -0.47957 | 122.5089 | 122.667 | 122.4413 | 114.5814 | -122.9633
1890.2812 | 122.7264 | -122.0032 | 0.56305 | 1.4211e-13 | -0.0050813 | -0.013077 | -0.045384 | -0.040216 | -0.010643 | -0.00083919 | -0.016222 | 0.0093796 | 0.034709 | 0.0043889 | 0.037556 | 0.028518 | 0.033457 | 0.028217 | 0.1208 | 0.08278 | 0.28848 | 0.1201 | -121.6599 | -7.5545 | -121.7814 | 0.4691 | 0.62266 | 0.4473 | -122.3774 | 122.1233 | -0.44224 | 122.0317 | 122.0314 | -0.091883 | -0.48027 | -0.27457 | -0.37418 | -0.093947 | 0.34332 | 0.22182 | 0.59601 | 0.059612 | -0.11575 | 122.124 | 122.086 | 122.2917 | 122.0366 | -0.44295 | 122.4723 | 122.6258 | 122.4505 | 114.4487 | -122.9404
1892.0781 | 122.6852 | -122.0444 | 0.58594 | 1.4211e-13 | -0.0055085 | -0.01265 | -0.045384 | -0.040216 | -0.010429 | -0.00083919 | -0.016435 | 0.0095932 | 0.034496 | 0.0043889 | 0.037983 | 0.023939 | 0.038035 | 0.023639 | 0.11622 | 0.078201 | 0.2839 | 0.11552 | -121.6599 | -7.6552 | -121.7814 | 0.46452 | 0.60893 | 0.39693 | -122.3774 | 122.1599 | -0.46971 | 122.0683 | 122.068 | -0.091882 | -0.50774 | -0.30203 | -0.33299 | -0.12141 | 0.38452 | 0.26302 | 0.59601 | 0.022988 | -0.18901 | 122.1606 | 122.1226 | 122.3283 | 122.0824 | -0.47042 | 122.5089 | 122.6533 | 122.4413 | 114.3891 | -122.9633
1893.8594 | 122.6257 | -122.0215 | 0.62256 | 1.4211e-13 | -0.0055085 | -0.013077 | -0.045598 | -0.040216 | -0.010643 | -0.0161 | -0.016222 | 0.0093796 | 0.034709 | 0.0041753 | 0.03777 | 0.023939 | 0.033457 | 0.028217 | 0.11622 | 0.078201 | 0.2839 | 0.11552 | -121.6644 | -7.7514 | -121.7722 | 0.4691 | 0.61808 | 0.40609 | -122.3865 | 122.137 | -0.50633 | 122.0454 | 122.0497 | -0.087304 | -0.54436 | -0.33866 | -0.36503 | -0.15346 | 0.35705 | 0.24929 | 0.61432 | -0.004477 | -0.21647 | 122.1377 | 122.0997 | 122.3054 | 122.0549 | -0.50704 | 122.4906 | 122.6396 | 122.4276 | 114.2701 | -123.0091
1895.5938 | 122.6486 | -122.0306 | 0.61798 | 1.4211e-13 | -0.0052949 | -0.012863 | -0.044957 | -0.040216 | -0.010856 | -0.023731 | -0.016222 | 0.009807 | 0.034709 | 0.0043889 | 0.037983 | 0.023939 | 0.042614 | 0.028217 | 0.11622 | 0.08278 | 0.27932 | 0.11094 | -121.6553 | -7.8521 | -121.7676 | 0.47826 | 0.62724 | 0.41525 | -122.3774 | 122.1416 | -0.50176 | 122.0546 | 122.0589 | -0.082725 | -0.5352 | -0.33866 | -0.34672 | -0.13972 | 0.37537 | 0.26302 | 0.60974 | 0.009258 | -0.20273 | 122.1469 | 122.1134 | 122.31 | 122.0733 | -0.50704 | 122.5089 | 122.6579 | 122.4459 | 114.1785 | -122.9953
1897.375 | 122.6532 | -122.0581 | 0.6134 | 1.4211e-13 | -0.0055085 | -0.013077 | -0.045384 | -0.040429 | -0.010856 | -0.00083919 | -0.016222 | 0.0095932 | 0.034709 | 0.0046025 | 0.03777 | 0.023939 | 0.042614 | 0.032795 | 0.1208 | 0.08278 | 0.2839 | 0.11552 | -121.6644 | -7.9437 | -121.7859 | 0.47368 | 0.62724 | 0.41525 | -122.3911 | 122.1736 | -0.4926 | 122.082 | 122.0909 | -0.082726 | -0.53062 | -0.3295 | -0.33299 | -0.13972 | 0.39367 | 0.27217 | 0.60516 | 0.013836 | -0.19816 | 122.1789 | 122.1409 | 122.342 | 122.1007 | -0.49788 | 122.5318 | 122.6853 | 122.4734 | 114.1144 | -123.0045
1899.1406 | 122.6578 | -122.2504 | 0.40741 | 1.4211e-13 | -0.0055085 | -0.013077 | -0.04517 | -0.040002 | -0.010856 | -0.0084697 | -0.016008 | 0.0093796 | 0.034923 | 0.0043889 | 0.037556 | 0.028518 | 0.038035 | 0.023639 | 0.1208 | 0.078201 | 0.27932 | 0.1201 | -121.8567 | -8.0765 | -121.9782 | 0.27681 | 0.43494 | 0.23668 | -122.5834 | 122.3705 | -0.28661 | 122.2789 | 122.274 | -0.096461 | -0.32921 | -0.12809 | -0.33304 | -0.1306 | 0.39363 | 0.27213 | 0.60517 | 0.027528 | -0.17073 | 122.3712 | 122.3286 | 122.5297 | 122.2884 | -0.28731 | 122.5272 | 122.6853 | 122.487 | 114.1739 | -122.9908
1900.9375 | 122.6578 | -122.2595 | 0.41657 | 1.4211e-13 | -0.0057223 | -0.013077 | -0.045384 | -0.040643 | -0.010643 | -0.0084697 | -0.016222 | 0.0095932 | 0.034709 | 0.0046025 | 0.03777 | 0.023939 | 0.051771 | 0.01906 | 0.11165 | 0.078201 | 0.2839 | 0.1201 | -121.8613 | -8.1818 | -121.9737 | 0.27681 | 0.43494 | 0.22752 | -122.5834 | 122.3796 | -0.30492 | 122.2835 | 122.2786 | -0.10104 | -0.33836 | -0.13266 | -0.32388 | -0.13976 | 0.39821 | 0.28586 | 0.60975 | 0.018373 | -0.18904 | 122.3712 | 122.3377 | 122.5434 | 122.3113 | -0.29647 | 122.5363 | 122.6945 | 122.487 | 114.0777 | -123
1902.75 | 122.7997 | -122.2 | 0.36621 | 1.4211e-13 | -0.0057223 | -0.012863 | -0.04517 | -0.040216 | -0.01107 | 0.0067908 | -0.016435 | 0.0093796 | 0.034496 | 0.0041753 | 0.037983 | 0.028518 | 0.038035 | 0.028217 | 0.11622 | 0.078201 | 0.27475 | 0.11552 | -121.8567 | -8.3054 | -121.9782 | 0.29054 | 0.43494 | 0.23668 | -122.588 | 122.3155 | -0.24999 | 122.2285 | 122.2282 | -0.087304 | -0.28801 | -0.091466 | -0.38797 | -0.075671 | 0.34328 | 0.22178 | 0.60975 | 0.068727 | -0.12953 | 122.3162 | 122.2782 | 122.4748 | 122.238 | -0.25069 | 122.4906 | 122.635 | 122.4367 | 113.8946 | -122.9542
1904.4688 | 122.7722 | -122.1176 | 0.46692 | 1.4211e-13 | -0.0055085 | -0.013077 | -0.04517 | -0.040002 | -0.010643 | -0.0084697 | -0.016435 | 0.0095932 | 0.034923 | 0.0043889 | 0.037983 | 0.028518 | 0.028878 | 0.009904 | 0.1208 | 0.078201 | 0.2839 | 0.1201 | -121.7652 | -8.4062 | -121.8867 | 0.37295 | 0.52193 | 0.30536 | -122.4918 | 122.2377 | -0.34611 | 122.1461 | 122.1275 | -0.1102 | -0.38872 | -0.18302 | -0.37421 | -0.093966 | 0.35245 | 0.23095 | 0.60517 | 0.055012 | -0.16156 | 122.2384 | 122.1958 | 122.4015 | 122.1465 | -0.34682 | 122.4906 | 122.6395 | 122.423 | 113.7115 | -122.9587
1906.2344 | 122.6852 | -122.2733 | 0.39825 | 1.4211e-13 | -0.0057223 | -0.013077 | -0.04517 | -0.040216 | -0.010429 | -0.0084697 | -0.016222 | 0.009807 | 0.034709 | 0.0043889 | 0.03777 | 0.028518 | 0.047193 | 0.01906 | 0.11165 | 0.073622 | 0.2839 | 0.12468 | -121.8796 | -8.5389 | -122.0103 | 0.24933 | 0.40289 | 0.20921 | -122.6155 | 122.3979 | -0.28661 | 122.3018 | 122.2923 | -0.10562 | -0.32463 | -0.11435 | -0.3422 | -0.14892 | 0.39362 | 0.26297 | 0.60517 | 0.004634 | -0.18904 | 122.3849 | 122.3469 | 122.5572 | 122.3204 | -0.27358 | 122.5226 | 122.6761 | 122.4825 | 113.7343 | -123.0137
1908.0469 | 122.7631 | -121.994 | 0.55389 | 1.4211e-13 | -0.0055085 | -0.01265 | -0.045384 | -0.040002 | -0.010429 | -0.00083919 | -0.016008 | 0.0095932 | 0.034709 | 0.0046025 | 0.037983 | 0.033096 | 0.033457 | 0.023639 | 0.11622 | 0.08278 | 0.27932 | 0.11094 | -121.6507 | -8.6397 | -121.7676 | 0.48742 | 0.6364 | 0.41525 | -122.3819 | 122.105 | -0.43767 | 122.0271 | 122.0177 | -0.087303 | -0.47111 | -0.27457 | -0.38792 | -0.066478 | 0.34332 | 0.2264 | 0.61432 | 0.082502 | -0.13865 | 122.1102 | 122.0768 | 122.2733 | 122.0275 | -0.44295 | 122.4814 | 122.6304 | 122.4093 | 113.3544 | -122.9358
1909.7656 | 122.7219 | -122.2595 | 0.40283 | 1.4211e-13 | -0.0057223 | -0.012863 | -0.045384 | -0.040643 | -0.010643 | 0.0067908 | -0.016435 | 0.0093796 | 0.034923 | 0.0041753 | 0.03777 | 0.028518 | 0.047193 | 0.028217 | 0.1208 | 0.08278 | 0.27932 | 0.11094 | -121.8659 | -8.777 | -121.9966 | 0.26765 | 0.41662 | 0.22295 | -122.6109 | 122.3705 | -0.28203 | 122.288 | 122.2877 | -0.082725 | -0.32005 | -0.12351 | -0.35136 | -0.13518 | 0.39363 | 0.26297 | 0.61433 | 0.013792 | -0.17989 | 122.3803 | 122.3423 | 122.5388 | 122.3067 | -0.29189 | 122.5272 | 122.6761 | 122.4825 | 113.4825 | -123.0137
1911.5469 | 122.7448 | -122.2366 | 0.36621 | 1.4211e-13 | -0.0055085 | -0.013077 | -0.045384 | -0.040216 | -0.010429 | 0.0067908 | -0.016222 | 0.0093796 | 0.034496 | 0.0046025 | 0.037983 | 0.023939 | 0.047193 | 0.023639 | 0.1208 | 0.08278 | 0.27475 | 0.11094 | -121.8659 | -8.9098 | -121.9966 | 0.25849 | 0.4212 | 0.22752 | -122.6017 | 122.3476 | -0.24541 | 122.2606 | 122.2603 | -0.087303 | -0.28343 | -0.091466 | -0.36509 | -0.10772 | 0.37074 | 0.24008 | 0.60517 | 0.054991 | -0.13869 | 122.3574 | 122.3194 | 122.5114 | 122.2838 | -0.25527 | 122.4951 | 122.6578 | 122.4642 | 113.3268 | -122.9679
1913.3438 | 122.6578 | -122.2824 | 0.39825 | 1.4211e-13 | -0.0059359 | -0.013291 | -0.04517 | -0.040429 | -0.010643 | -0.00083919 | -0.015794 | 0.0093796 | 0.034709 | 0.0041753 | 0.038197 | 0.028518 | 0.042614 | 0.023639 | 0.11165 | 0.073622 | 0.27017 | 0.1201 | -121.8751 | -9.0518 | -121.992 | 0.26307 | 0.41662 | 0.21379 | -122.6063 | 122.4025 | -0.28661 | 122.3109 | 122.306 | -0.096461 | -0.32463 | -0.12809 | -0.32389 | -0.13518 | 0.40736 | 0.29044 | 0.61433 | 0.01837 | -0.18447 | 122.3941 | 122.356 | 122.5526 | 122.325 | -0.27815 | 122.5455 | 122.699 | 122.4962 | 113.2307 | -123.0046
1915.0469 | 122.7127 | -122.1451 | 0.50812 | 1.4211e-13 | -0.0059359 | -0.012863 | -0.044957 | -0.040216 | -0.010429 | -0.0084697 | -0.016008 | 0.0095932 | 0.034923 | 0.0046025 | 0.037983 | 0.028518 | 0.038035 | 0.028217 | 0.12538 | 0.087359 | 0.2839 | 0.12468 | -121.7743 | -9.1616 | -121.9004 | 0.35464 | 0.50362 | 0.32825 | -122.5193 | 122.2698 | -0.38274 | 122.1736 | 122.1733 | -0.096462 | -0.42076 | -0.22421 | -0.37422 | -0.15348 | 0.37076 | 0.24468 | 0.6189 | -0.004501 | -0.17986 | 122.2705 | 122.2324 | 122.429 | 122.1831 | -0.38344 | 122.4997 | 122.6487 | 122.4733 | 112.9834 | -123.0274
1916.8281 | 122.7676 | -121.9437 | 0.63171 | 1.4211e-13 | -0.0059359 | -0.013291 | -0.04517 | -0.040643 | -0.010643 | -0.0084697 | -0.016222 | 0.0095932 | 0.034923 | 0.0043889 | 0.03777 | 0.023939 | 0.0243 | 0.023639 | 0.1208 | 0.08278 | 0.27475 | 0.11094 | -121.6049 | -9.2807 | -121.7127 | 0.53778 | 0.68676 | 0.46561 | -122.3361 | 122.0546 | -0.51091 | 121.9676 | 121.9673 | -0.087303 | -0.54893 | -0.35697 | -0.39248 | -0.093935 | 0.33876 | 0.23099 | 0.62348 | 0.055047 | -0.1661 | 122.0645 | 122.0264 | 122.2184 | 121.968 | -0.52077 | 122.4814 | 122.6304 | 122.4093 | 112.663 | -122.9679
1918.5625 | 122.6761 | -122.0627 | 0.60425 | 1.4211e-13 | -0.0057223 | -0.012863 | -0.045598 | -0.040216 | -0.010643 | -0.0161 | -0.016222 | 0.0093796 | 0.034709 | 0.0043889 | 0.037556 | 0.023939 | 0.033457 | 0.028217 | 0.1208 | 0.078201 | 0.2839 | 0.1201 | -121.669 | -9.4226 | -121.7814 | 0.47826 | 0.62724 | 0.38777 | -122.4094 | 122.1828 | -0.48344 | 122.0866 | 122.0909 | -0.091883 | -0.52605 | -0.32034 | -0.34673 | -0.12599 | 0.39367 | 0.28133 | 0.62806 | 0.022991 | -0.21647 | 122.1835 | 122.1409 | 122.3466 | 122.0961 | -0.48415 | 122.5409 | 122.6899 | 122.4505 | 112.6401 | -123.0137
1920.3438 | 122.6807 | -122.0627 | 0.62714 | 1.4211e-13 | -0.0055085 | -0.013077 | -0.045384 | -0.040216 | -0.010856 | -0.00083919 | -0.016435 | 0.0095932 | 0.034709 | 0.0043889 | 0.037983 | 0.023939 | 0.033457 | 0.023639 | 0.11622 | 0.087359 | 0.2839 | 0.11094 | -121.6415 | -9.5737 | -121.7722 | 0.49199 | 0.64555 | 0.43356 | -122.3865 | 122.1736 | -0.51091 | 122.0866 | 122.0863 | -0.087303 | -0.53978 | -0.34323 | -0.32383 | -0.13514 | 0.42115 | 0.29049 | 0.61432 | 0.018418 | -0.19358 | 122.1789 | 122.15 | 122.3466 | 122.0961 | -0.51619 | 122.5547 | 122.7082 | 122.4962 | 112.489 | -123.0137
1922.1406 | 122.8134 | -122.2412 | 0.36621 | 1.4211e-13 | -0.0059359 | -0.01265 | -0.045384 | -0.040002 | -0.010643 | -0.0084697 | -0.016435 | 0.0095932 | 0.034923 | 0.0048163 | 0.037556 | 0.023939 | 0.033457 | 0.037373 | 0.11622 | 0.073622 | 0.27932 | 0.11094 | -121.8659 | -9.734 | -121.9874 | 0.27223 | 0.4212 | 0.23668 | -122.6109 | 122.3522 | -0.24999 | 122.2652 | 122.2786 | -0.073569 | -0.29259 | -0.086887 | -0.36967 | -0.093985 | 0.37532 | 0.25382 | 0.62348 | 0.054991 | -0.12953 | 122.3574 | 122.3148 | 122.5205 | 122.2747 | -0.25527 | 122.5134 | 122.6624 | 122.4779 | 112.5072 | -122.9771
1923.8594 | 122.6715 | -122.2229 | 0.43945 | 1.4211e-13 | -0.0057223 | -0.013077 | -0.04517 | -0.040429 | -0.010429 | 0.0067908 | -0.015794 | 0.0093796 | 0.034496 | 0.0043889 | 0.03777 | 0.033096 | 0.028878 | 0.028217 | 0.1208 | 0.078201 | 0.27475 | 0.11552 | -121.843 | -9.8576 | -121.9645 | 0.29054 | 0.44867 | 0.24584 | -122.588 | 122.3384 | -0.31865 | 122.256 | 122.2511 | -0.087304 | -0.36125 | -0.16471 | -0.36508 | -0.14891 | 0.3799 | 0.2584 | 0.62348 | 0.009221 | -0.19361 | 122.3437 | 122.3011 | 122.4976 | 122.2518 | -0.32393 | 122.5134 | 122.6716 | 122.4687 | 112.3653 | -123.0274
1925.6562 | 122.7493 | -121.9437 | 0.66834 | 1.4211e-13 | -0.0059359 | -0.01265 | -0.04517 | -0.040429 | -0.010643 | -0.00083919 | -0.016435 | 0.009166 | 0.034709 | 0.0046025 | 0.03777 | 0.019361 | 0.033457 | 0.028217 | 0.1208 | 0.078201 | 0.27932 | 0.11094 | -121.7697 | -10.0087 | -121.8912 | 0.37295 | 0.51735 | 0.30536 | -122.5147 | 122.0546 | -0.54753 | 121.963 | 121.9719 | -0.082725 | -0.59013 | -0.38901 | -0.57106 | -0.29538 | 0.17392 | 0.052423 | 0.62348 | -0.15098 | -0.36297 | 122.0645 | 122.0219 | 122.223 | 121.9771 | -0.55739 | 122.3166 | 122.461 | 122.249 | 111.935 | -123.1831
1927.375 | 122.7539 | -122.2 | 0.4303 | 1.4211e-13 | -0.0057223 | -0.01265 | -0.044957 | -0.040429 | -0.010429 | -0.00083919 | -0.016222 | 0.0093796 | 0.034496 | 0.0046025 | 0.038197 | 0.023939 | 0.0243 | 0.014482 | 0.1208 | 0.078201 | 0.27017 | 0.1201 | -121.8293 | -10.1827 | -121.9462 | 0.30885 | 0.47614 | 0.25042 | -122.5742 | 122.3201 | -0.30949 | 122.224 | 122.2145 | -0.10562 | -0.3521 | -0.16013 | -0.37424 | -0.12144 | 0.37075 | 0.25383 | 0.62806 | 0.045847 | -0.17988 | 122.3208 | 122.2782 | 122.4702 | 122.2243 | -0.3102 | 122.5089 | 122.6762 | 122.4504 | 112.0173 | -123.0045
1929.1406 | 122.7905 | -122.0581 | 0.56763 | 1.4211e-13 | -0.0057223 | -0.012863 | -0.045384 | -0.039788 | -0.010643 | 0.0067908 | -0.015794 | 0.0093796 | 0.034709 | 0.0048163 | 0.03777 | 0.028518 | 0.0243 | 0.01906 | 0.11165 | 0.08278 | 0.27475 | 0.10636 | -121.7194 | -10.3292 | -121.8455 | 0.41874 | 0.56314 | 0.33283 | -122.4781 | 122.1645 | -0.45598 | 122.0866 | 122.0772 | -0.087303 | -0.48485 | -0.29288 | -0.41999 | -0.14889 | 0.33873 | 0.21265 | 0.63264 | -0.004488 | -0.2348 | 122.1698 | 122.1409 | 122.3328 | 122.0824 | -0.46126 | 122.4768 | 122.6212 | 122.3909 | 111.7289 | -123.0457
1930.8594 | 122.7951 | -122.2916 | 0.33875 | 1.4211e-13 | -0.0061495 | -0.012863 | -0.045384 | -0.040643 | -0.010643 | -0.00083919 | -0.016222 | 0.009166 | 0.034923 | 0.0046025 | 0.037983 | 0.028518 | 0.038035 | 0.014482 | 0.11622 | 0.078201 | 0.27475 | 0.11094 | -121.8979 | -10.4986 | -122.0194 | 0.2356 | 0.39373 | 0.22295 | -122.6521 | 122.4025 | -0.22252 | 122.3201 | 122.306 | -0.09646 | -0.26054 | -0.064 | -0.36052 | -0.10315 | 0.39362 | 0.27212 | 0.63264 | 0.054986 | -0.1158 | 122.4078 | 122.3698 | 122.5663 | 122.3296 | -0.2278 | 122.5272 | 122.6853 | 122.5145 | 111.7929 | -122.9908
1932.6562 | 122.7402 | -122.0261 | 0.64087 | 1.4211e-13 | -0.0059359 | -0.013291 | -0.044957 | -0.040216 | -0.010429 | 0.0067908 | -0.016008 | 0.0089522 | 0.034709 | 0.0046025 | 0.037983 | 0.023939 | 0.028878 | 0.01906 | 0.11165 | 0.078201 | 0.27475 | 0.11552 | -121.6186 | -10.6222 | -121.7447 | 0.51031 | 0.66387 | 0.43356 | -122.3819 | 122.1416 | -0.52922 | 122.05 | 122.0451 | -0.096461 | -0.56267 | -0.36612 | -0.35587 | -0.13056 | 0.40742 | 0.28134 | 0.63721 | 0.022999 | -0.20731 | 122.1377 | 122.1043 | 122.3008 | 122.0549 | -0.52535 | 122.5364 | 122.6899 | 122.4596 | 111.4038 | -123.0228
1934.4531 | 122.8088 | -122.2366 | 0.36621 | 1.4211e-13 | -0.0059359 | -0.012863 | -0.045384 | -0.040429 | -0.010643 | -0.00083919 | -0.016222 | 0.0095932 | 0.034496 | 0.0043889 | 0.037983 | 0.019361 | 0.033457 | 0.014482 | 0.097912 | 0.069043 | 0.27475 | 0.1201 | -121.8751 | -10.8237 | -121.992 | 0.26307 | 0.41662 | 0.22295 | -122.6338 | 122.3567 | -0.2683 | 122.256 | 122.2511 | -0.10562 | -0.29717 | -0.091466 | -0.39714 | -0.10314 | 0.36158 | 0.24466 | 0.6418 | 0.050413 | -0.14327 | 122.3345 | 122.3057 | 122.5114 | 122.2701 | -0.24611 | 122.4997 | 122.6533 | 122.4596 | 111.4129 | -123
1936.2344 | 122.6852 | -122.2549 | 0.45319 | 1.4211e-13 | -0.0059359 | -0.013077 | -0.045384 | -0.040429 | -0.010215 | -0.00083919 | -0.016222 | 0.009807 | 0.034709 | 0.0050299 | 0.03777 | 0.019361 | 0.0243 | 0.01906 | 0.11622 | 0.078201 | 0.26559 | 0.11094 | -121.8201 | -10.9657 | -121.9462 | 0.32259 | 0.47614 | 0.26873 | -122.5742 | 122.3659 | -0.33696 | 122.2743 | 122.274 | -0.091882 | -0.37498 | -0.1876 | -0.3193 | -0.1306 | 0.43484 | 0.30876 | 0.62806 | 0.022959 | -0.18445 | 122.3712 | 122.3331 | 122.5205 | 122.2792 | -0.34224 | 122.5775 | 122.7311 | 122.5237 | 111.2893 | -123.0274
1938.0312 | 122.7448 | -122.1497 | 0.49439 | 1.4211e-13 | -0.0059359 | -0.013077 | -0.045598 | -0.040429 | -0.010429 | -0.00083919 | -0.016435 | 0.0093796 | 0.034923 | 0.0048163 | 0.037983 | 0.019361 | 0.028878 | 0.014482 | 0.10707 | 0.069043 | 0.27017 | 0.11552 | -121.7606 | -11.103 | -121.8821 | 0.37295 | 0.53109 | 0.30536 | -122.5285 | 122.2652 | -0.38732 | 122.169 | 122.1641 | -0.10104 | -0.42534 | -0.22422 | -0.3788 | -0.12143 | 0.38907 | 0.26757 | 0.64637 | 0.036704 | -0.18902 | 122.2567 | 122.2187 | 122.4198 | 122.1785 | -0.37886 | 122.5226 | 122.6807 | 122.455 | 111.0466 | -123.0228
1939.75 | 122.6944 | -122.0856 | 0.59052 | 1.4211e-13 | -0.0057223 | -0.013077 | -0.045598 | -0.040429 | -0.010429 | -0.0084697 | -0.016008 | 0.0093796 | 0.034923 | 0.0046025 | 0.03777 | 0.019361 | 0.028878 | 0.023639 | 0.10707 | 0.064464 | 0.27932 | 0.1201 | -121.6965 | -11.2541 | -121.8134 | 0.45079 | 0.60435 | 0.36488 | -122.4506 | 122.2057 | -0.48345 | 122.1049 | 122.1092 | -0.096461 | -0.52605 | -0.31119 | -0.36505 | -0.13973 | 0.38909 | 0.27217 | 0.63722 | 0.013831 | -0.22563 | 122.1926 | 122.15 | 122.3649 | 122.1144 | -0.47042 | 122.5364 | 122.6899 | 122.4505 | 110.8315 | -123.0411
1941.5312 | 122.818 | -122.1313 | 0.50354 | 1.4211e-13 | -0.0061495 | -0.013291 | -0.045811 | -0.040216 | -0.010643 | -0.00083919 | -0.016008 | 0.0093796 | 0.034709 | 0.0048163 | 0.03777 | 0.019361 | 0.038035 | 0.009904 | 0.10707 | 0.073622 | 0.27475 | 0.11094 | -121.7148 | -11.4052 | -121.8363 | 0.41874 | 0.5723 | 0.34199 | -122.4827 | 122.2423 | -0.39647 | 122.1507 | 122.1413 | -0.10104 | -0.42992 | -0.22879 | -0.35132 | -0.084802 | 0.41655 | 0.29505 | 0.64637 | 0.068756 | -0.16155 | 122.2384 | 122.205 | 122.4061 | 122.1694 | -0.3926 | 122.5501 | 122.7036 | 122.4733 | 110.7261 | -122.9862
1943.3125 | 122.8363 | -122.1222 | 0.47607 | 1.4211e-13 | -0.0059359 | -0.01265 | -0.045598 | -0.040643 | -0.010429 | -0.00083919 | -0.015794 | 0.0095932 | 0.034496 | 0.0043889 | 0.03777 | 0.023939 | 0.028878 | 0.01906 | 0.11622 | 0.08278 | 0.27017 | 0.11094 | -121.7697 | -11.5655 | -121.8867 | 0.3638 | 0.52193 | 0.29162 | -122.533 | 122.2331 | -0.35985 | 122.1461 | 122.1413 | -0.091882 | -0.39329 | -0.20591 | -0.41085 | -0.11228 | 0.35245 | 0.23553 | 0.64638 | 0.045857 | -0.18445 | 122.2384 | 122.205 | 122.3924 | 122.1511 | -0.36513 | 122.486 | 122.6441 | 122.4138 | 110.5567 | -123.0091
1945.0938 | 122.8043 | -122.168 | 0.42572 | 1.4211e-13 | -0.0063633 | -0.012863 | -0.045811 | -0.040643 | -0.010856 | -0.0161 | -0.016435 | 0.0093796 | 0.034496 | 0.0048163 | 0.037983 | 0.014783 | 0.028878 | 0.014482 | 0.11622 | 0.073622 | 0.27017 | 0.11552 | -121.8018 | -11.712 | -121.9233 | 0.33632 | 0.48988 | 0.27331 | -122.5742 | 122.2835 | -0.30949 | 122.1828 | 122.1825 | -0.10104 | -0.3521 | -0.15555 | -0.40628 | -0.089395 | 0.36618 | 0.24468 | 0.65095 | 0.064161 | -0.15241 | 122.2842 | 122.2416 | 122.4381 | 122.1968 | -0.3102 | 122.5043 | 122.6578 | 122.4413 | 110.456 | -123
1946.875 | 122.7585 | -122.2137 | 0.42114 | 1.4211e-13 | -0.0061495 | -0.012863 | -0.045598 | -0.040857 | -0.010429 | -0.0084697 | -0.016222 | 0.0093796 | 0.034709 | 0.0046025 | 0.037983 | 0.019361 | 0.028878 | 0.014482 | 0.11165 | 0.08278 | 0.27475 | 0.11094 | -121.8293 | -11.8768 | -121.9508 | 0.31343 | 0.46241 | 0.24584 | -122.5926 | 122.3247 | -0.3095 | 122.2331 | 122.2282 | -0.09646 | -0.33836 | -0.1464 | -0.37882 | -0.10771 | 0.38448 | 0.26298 | 0.6418 | 0.041267 | -0.1753 | 122.3254 | 122.2965 | 122.4885 | 122.2426 | -0.3102 | 122.5272 | 122.6762 | 122.4596 | 110.3369 | -123.0137
1948.6094 | 122.7036 | -122.2046 | 0.48065 | 1.4211e-13 | -0.0057223 | -0.013077 | -0.045384 | -0.040429 | -0.010856 | -0.00083919 | -0.016008 | 0.0095932 | 0.034282 | 0.0048163 | 0.03777 | 0.014783 | 0.0243 | 0.01906 | 0.11622 | 0.073622 | 0.2839 | 0.11552 | -121.7881 | -12.005 | -121.9187 | 0.34548 | 0.50362 | 0.26873 | -122.5605 | 122.3201 | -0.36443 | 122.2194 | 122.2236 | -0.096461 | -0.40703 | -0.19675 | -0.35592 | -0.13517 | 0.41653 | 0.28588 | 0.6418 | 0.022965 | -0.21192 | 122.3208 | 122.2782 | 122.4885 | 122.2289 | -0.36513 | 122.5501 | 122.7082 | 122.4733 | 110.1996 | -123.0412
1950.3906 | 122.7127 | -122.287 | 0.40283 | 1.4211e-13 | -0.0059359 | -0.013077 | -0.045384 | -0.040002 | -0.010856 | -0.00083919 | -0.016649 | 0.0095932 | 0.034496 | 0.0048163 | 0.03777 | 0.023939 | 0.028878 | 0.01906 | 0.10707 | 0.078201 | 0.27932 | 0.11552 | -121.8613 | -12.1882 | -121.9828 | 0.28596 | 0.43494 | 0.23668 | -122.6292 | 122.4025 | -0.29576 | 122.3109 | 122.306 | -0.096461 | -0.32463 | -0.12351 | -0.34221 | -0.11687 | 0.42567 | 0.30417 | 0.64638 | 0.032106 | -0.16615 | 122.3941 | 122.3652 | 122.5663 | 122.3159 | -0.28731 | 122.5729 | 122.7219 | 122.5237 | 110.0988 | -123.032
1952.1094 | 122.7814 | -122.2778 | 0.36163 | 1.4211e-13 | -0.0063633 | -0.013077 | -0.045811 | -0.040429 | -0.010856 | -0.0084697 | -0.016222 | 0.0093796 | 0.034496 | 0.0050299 | 0.037556 | 0.023939 | 0.033457 | 0.009904 | 0.11165 | 0.069043 | 0.27932 | 0.11094 | -121.8796 | -12.3209 | -121.9966 | 0.26307 | 0.4212 | 0.22295 | -122.6521 | 122.3888 | -0.24999 | 122.3018 | 122.2877 | -0.10104 | -0.29259 | -0.082309 | -0.37426 | -0.098564 | 0.3982 | 0.28128 | 0.65554 | 0.059569 | -0.13869 | 122.3895 | 122.3469 | 122.5572 | 122.3113 | -0.25069 | 122.5409 | 122.699 | 122.5008 | 109.9569 | -123.0137
1953.9062 | 122.8271 | -122.2641 | 0.34332 | 1.4211e-13 | -0.0061495 | -0.012863 | -0.045384 | -0.040429 | -0.010856 | -0.00083919 | -0.016435 | 0.0093796 | 0.034496 | 0.0048163 | 0.037556 | 0.010204 | 0.028878 | 0.014482 | 0.10707 | 0.073622 | 0.27475 | 0.11094 | -121.8979 | -12.4629 | -122.0194 | 0.24476 | 0.40747 | 0.20921 | -122.6658 | 122.375 | -0.23625 | 122.2743 | 122.2786 | -0.09646 | -0.2697 | -0.068578 | -0.40172 | -0.098568 | 0.36615 | 0.24465 | 0.64638 | 0.064143 | -0.13411 | 122.3712 | 122.3377 | 122.5388 | 122.293 | -0.23238 | 122.5089 | 122.6716 | 122.4733 | 109.8012 | -123.0091
1955.7031 | 122.7127 | -122.3007 | 0.42114 | 1.4211e-13 | -0.0063633 | -0.012863 | -0.045384 | -0.040429 | -0.010643 | 0.0067908 | -0.016008 | 0.0093796 | 0.034496 | 0.0046025 | 0.03777 | 0.023939 | 0.0243 | 0.009904 | 0.10707 | 0.073622 | 0.27475 | 0.11552 | -121.8613 | -12.6277 | -121.9874 | 0.27223 | 0.43494 | 0.22752 | -122.6384 | 122.4162 | -0.31407 | 122.3247 | 122.3106 | -0.10562 | -0.34752 | -0.1464 | -0.33763 | -0.14892 | 0.4394 | 0.31332 | 0.65096 | 0.013795 | -0.19362 | 122.4078 | 122.3743 | 122.5755 | 122.325 | -0.30562 | 122.5729 | 122.7357 | 122.5282 | 109.673 | -123.0595
1957.4844 | 122.7997 | -122.1817 | 0.44403 | 1.4211e-13 | -0.0057223 | -0.013077 | -0.045598 | -0.040216 | -0.010643 | -0.00083919 | -0.016222 | 0.009166 | 0.034709 | 0.0048163 | 0.03777 | 0.019361 | 0.0243 | 0.014482 | 0.10707 | 0.073622 | 0.26559 | 0.1201 | -121.8018 | -12.7513 | -121.9279 | 0.3409 | 0.48988 | 0.27331 | -122.5834 | 122.3018 | -0.33696 | 122.2011 | 122.1962 | -0.10562 | -0.37041 | -0.17844 | -0.4017 | -0.10313 | 0.37991 | 0.25383 | 0.65553 | 0.04585 | -0.17072 | 122.2888 | 122.2553 | 122.4473 | 122.206 | -0.32393 | 122.5226 | 122.6716 | 122.455 | 109.4304 | -123.0274
1959.2031 | 122.6852 | -122.2183 | 0.46234 | 1.4211e-13 | -0.0063633 | -0.013077 | -0.04517 | -0.040429 | -0.010429 | -0.00083919 | -0.016435 | 0.009166 | 0.034709 | 0.0046025 | 0.038197 | 0.019361 | 0.015142 | 0.014482 | 0.11165 | 0.073622 | 0.27475 | 0.10636 | -121.8293 | -12.9024 | -121.9462 | 0.31343 | 0.46241 | 0.25957 | -122.6063 | 122.3247 | -0.35069 | 122.2377 | 122.2328 | -0.091881 | -0.38872 | -0.1876 | -0.38798 | -0.14891 | 0.38906 | 0.27214 | 0.66011 | 6.9e-05 | -0.20277 | 122.33 | 122.2919 | 122.4931 | 122.2335 | -0.35598 | 122.5318 | 122.6807 | 122.4779 | 109.3159 | -123.0686
1961 | 122.8134 | -122.0581 | 0.54016 | 1.4211e-13 | -0.0061495 | -0.012863 | -0.045598 | -0.040216 | -0.010429 | -0.0084697 | -0.016222 | 0.0093796 | 0.034709 | 0.0050299 | 0.037983 | 0.014783 | 0.0243 | 0.009904 | 0.11165 | 0.073622 | 0.27017 | 0.092626 | -121.6599 | -13.0261 | -121.7768 | 0.48742 | 0.63182 | 0.41525 | -122.4277 | 122.1507 | -0.42851 | 122.0729 | 122.068 | -0.082722 | -0.46654 | -0.26999 | -0.36962 | -0.052745 | 0.39825 | 0.28133 | 0.65095 | 0.091657 | -0.12491 | 122.1698 | 122.1317 | 122.3283 | 122.0824 | -0.44754 | 122.5455 | 122.6899 | 122.4734 | 109.032 | -122.9679
1962.7344 | 122.8317 | -121.9986 | 0.60425 | 1.4211e-13 | -0.0063633 | -0.013077 | -0.045598 | -0.040429 | -0.010856 | -0.0084697 | -0.016008 | 0.0095932 | 0.034709 | 0.0046025 | 0.03777 | 0.023939 | 0.0243 | 0.009904 | 0.11165 | 0.078201 | 0.27017 | 0.10636 | -121.6324 | -13.168 | -121.7539 | 0.50573 | 0.65471 | 0.44272 | -122.4094 | 122.105 | -0.4926 | 122.0225 | 122.0085 | -0.096459 | -0.52605 | -0.33408 | -0.41081 | -0.098518 | 0.36622 | 0.24472 | 0.65553 | 0.050463 | -0.16153 | 122.1102 | 122.0768 | 122.2688 | 122.0229 | -0.49789 | 122.5043 | 122.6533 | 122.4413 | 108.8306 | -123.0137
1964.5312 | 122.7997 | -122.0718 | 0.56763 | 1.4211e-13 | -0.0061495 | -0.013077 | -0.045598 | -0.040216 | -0.010856 | -0.00083919 | -0.016649 | 0.0095932 | 0.034709 | 0.0046025 | 0.037983 | 0.028518 | 0.028878 | 0.005325 | 0.11165 | 0.073622 | 0.27475 | 0.11552 | -121.6644 | -13.3328 | -121.7768 | 0.47826 | 0.6364 | 0.40609 | -122.4415 | 122.1874 | -0.45598 | 122.1004 | 122.0772 | -0.1102 | -0.494 | -0.29288 | -0.36962 | -0.089368 | 0.40741 | 0.29506 | 0.66469 | 0.068769 | -0.16154 | 122.1835 | 122.1455 | 122.3466 | 122.1007 | -0.45211 | 122.5501 | 122.7082 | 122.4779 | 108.739 | -123.0091
1966.25 | 122.7539 | -122.0764 | 0.6134 | 1.4211e-13 | -0.0063633 | -0.013291 | -0.045598 | -0.040429 | -0.010643 | -0.0084697 | -0.016222 | 0.0095932 | 0.034496 | 0.0048163 | 0.03777 | 0.010204 | 0.0243 | 0.009904 | 0.11165 | 0.069043 | 0.27017 | 0.092626 | -121.6644 | -13.3969 | -121.7814 | 0.47368 | 0.62266 | 0.39693 | -122.4369 | 122.169 | -0.50176 | 122.0866 | 122.0863 | -0.082722 | -0.54436 | -0.34324 | -0.36047 | -0.13972 | 0.41199 | 0.29506 | 0.65553 | 0.009258 | -0.21647 | 122.1881 | 122.1455 | 122.3466 | 122.1007 | -0.52078 | 122.5501 | 122.6991 | 122.4733 | 108.6795 | -123.0503
1968.0469 | 122.7448 | -122.168 | 0.52643 | 1.4211e-13 | -0.0065769 | -0.012863 | -0.045384 | -0.040643 | -0.010643 | 0.0067908 | -0.016222 | 0.009166 | 0.034709 | 0.0050299 | 0.037556 | 0.014783 | 0.033457 | 0.014482 | 0.10707 | 0.073622 | 0.27475 | 0.11552 | -121.7102 | -13.5526 | -121.8363 | 0.41874 | 0.57688 | 0.35572 | -122.4964 | 122.2835 | -0.41936 | 122.1828 | 122.1825 | -0.10104 | -0.45281 | -0.25168 | -0.32844 | -0.10769 | 0.45775 | 0.33167 | 0.66011 | 0.050447 | -0.1707 | 122.275 | 122.2416 | 122.4427 | 122.2014 | -0.41091 | 122.5867 | 122.7448 | 122.5237 | 108.6153 | -123.0228
1969.8281 | 122.731 | -122.1497 | 0.53558 | 1.4211e-13 | -0.0063633 | -0.013291 | -0.046025 | -0.040643 | -0.010643 | -0.00083919 | -0.016222 | 0.0093796 | 0.034923 | 0.0043889 | 0.037556 | 0.019361 | 0.019721 | 0.009904 | 0.10249 | 0.073622 | 0.27932 | 0.11094 | -121.7056 | -13.7037 | -121.8271 | 0.44163 | 0.58603 | 0.3603 | -122.4918 | 122.2606 | -0.43309 | 122.169 | 122.1596 | -0.10104 | -0.46196 | -0.25626 | -0.34217 | -0.093952 | 0.44402 | 0.32252 | 0.66469 | 0.050449 | -0.17528 | 122.2521 | 122.2233 | 122.429 | 122.1694 | -0.42464 | 122.5913 | 122.7357 | 122.51 | 108.4459 | -123.0274
1971.5625 | 122.7493 | -122.0581 | 0.66376 | 1.4211e-13 | -0.0063633 | -0.012436 | -0.045598 | -0.040429 | -0.010856 | -0.0084697 | -0.016435 | 0.0093796 | 0.034923 | 0.0048163 | 0.037983 | 0.014783 | 0.019721 | 0.009904 | 0.10707 | 0.069043 | 0.27017 | 0.11552 | -121.6415 | -13.8273 | -121.7676 | 0.50115 | 0.65013 | 0.41983 | -122.4323 | 122.1736 | -0.55669 | 122.0729 | 122.068 | -0.10562 | -0.59471 | -0.39359 | -0.3742 | -0.16261 | 0.41657 | 0.29049 | 0.66469 | -0.013625 | -0.24393 | 122.1652 | 122.1271 | 122.3283 | 122.0778 | -0.54824 | 122.5593 | 122.7082 | 122.4779 | 108.2308 | -123.0961
1973.3594 | 122.7676 | -122.0581 | 0.65002 | 1.4211e-13 | -0.0065769 | -0.012863 | -0.045598 | -0.040643 | -0.010643 | -0.0161 | -0.016222 | 0.0095932 | 0.034709 | 0.0050299 | 0.037983 | 0.023939 | 0.0243 | 0.000747 | 0.10707 | 0.073622 | 0.27017 | 0.10636 | -121.6232 | -13.9235 | -121.7447 | 0.51489 | 0.66387 | 0.4473 | -122.4094 | 122.1645 | -0.54296 | 122.082 | 122.0589 | -0.10562 | -0.5764 | -0.37986 | -0.3513 | -0.13514 | 0.43488 | 0.31338 | 0.66469 | 0.013844 | -0.20273 | 122.1652 | 122.1317 | 122.3283 | 122.0824 | -0.54366 | 122.573 | 122.722 | 122.5054 | 108.1346 | -123.0594
1975.1562 | 122.731 | -122.0673 | 0.63171 | 1.4211e-13 | -0.0063633 | -0.012863 | -0.045598 | -0.040216 | -0.010856 | 0.0067908 | -0.016435 | 0.0093796 | 0.034709 | 0.0050299 | 0.03777 | 0.019361 | 0.0243 | 0.014482 | 0.11165 | 0.069043 | 0.27475 | 0.088047 | -121.6186 | -14.0654 | -121.7447 | 0.51489 | 0.66845 | 0.44272 | -122.4186 | 122.1553 | -0.52007 | 122.0866 | 122.0817 | -0.073565 | -0.56267 | -0.35697 | -0.35131 | -0.11683 | 0.44862 | 0.32254 | 0.67385 | 0.036733 | -0.189 | 122.1789 | 122.1363 | 122.342 | 122.0916 | -0.54367 | 122.5821 | 122.7357 | 122.51 | 108.0018 | -123.0503
1976.9531 | 122.7539 | -122.0764 | 0.60883 | 1.4211e-13 | -0.0063633 | -0.013291 | -0.045598 | -0.040643 | -0.010429 | -0.00083919 | -0.016649 | 0.009166 | 0.034923 | 0.0048163 | 0.037556 | 0.014783 | 0.019721 | 0.009904 | 0.10707 | 0.069043 | 0.27475 | 0.11094 | -121.6324 | -14.2211 | -121.763 | 0.50115 | 0.65471 | 0.4244 | -122.4277 | 122.1874 | -0.50176 | 122.0912 | 122.0863 | -0.10104 | -0.53978 | -0.33408 | -0.35131 | -0.10767 | 0.44404 | 0.31338 | 0.66469 | 0.045885 | -0.18442 | 122.1835 | 122.1455 | 122.3512 | 122.0961 | -0.49788 | 122.5776 | 122.7311 | 122.5008 | 107.8553 | -123.0366
1978.6875 | 122.8455 | -122.0535 | 0.58594 | 1.4211e-13 | -0.0065769 | -0.012863 | -0.045811 | -0.040643 | -0.010856 | -0.0161 | -0.016435 | 0.009166 | 0.034709 | 0.0048163 | 0.037983 | 0.014783 | 0.0243 | 0.005325 | 0.10249 | 0.073622 | 0.27017 | 0.11552 | -121.6324 | -14.331 | -121.7539 | 0.49657 | 0.65013 | 0.4244 | -122.4323 | 122.169 | -0.48345 | 122.0683 | 122.0589 | -0.1102 | -0.51232 | -0.31577 | -0.37878 | -0.089364 | 0.42115 | 0.29965 | 0.67842 | 0.064195 | -0.16153 | 122.156 | 122.1272 | 122.3237 | 122.0778 | -0.47042 | 122.5501 | 122.7037 | 122.4779 | 107.7225 | -123.0182
1980.4844 | 122.8088 | -122.0444 | 0.59967 | 1.4211e-13 | -0.0065769 | -0.012863 | -0.045598 | -0.040429 | -0.010429 | -0.00083919 | -0.015794 | 0.009166 | 0.034923 | 0.0048163 | 0.037983 | 0.019361 | 0.015142 | 0.009904 | 0.10707 | 0.069043 | 0.26559 | 0.097205 | -121.6415 | -14.505 | -121.763 | 0.49199 | 0.64097 | 0.41983 | -122.4415 | 122.1416 | -0.4926 | 122.0637 | 122.0543 | -0.087301 | -0.53063 | -0.33408 | -0.39709 | -0.10768 | 0.40284 | 0.28133 | 0.67842 | 0.041305 | -0.17985 | 122.1514 | 122.1134 | 122.31 | 122.0595 | -0.50247 | 122.5364 | 122.6853 | 122.4642 | 107.5394 | -123.0411
1982.2031 | 122.8638 | -122.0581 | 0.58136 | 1.4211e-13 | -0.0063633 | -0.013077 | -0.045384 | -0.040429 | -0.010856 | 0.014421 | -0.016649 | 0.0095932 | 0.034709 | 0.0046025 | 0.037983 | 0.010204 | 0.0243 | 0.009904 | 0.10707 | 0.073622 | 0.27017 | 0.10178 | -121.6461 | -14.6195 | -121.7768 | 0.48284 | 0.6364 | 0.40609 | -122.446 | 122.1599 | -0.47429 | 122.0683 | 122.068 | -0.09188 | -0.50774 | -0.31119 | -0.38794 | -0.098523 | 0.41199 | 0.28133 | 0.66927 | 0.055036 | -0.17527 | 122.1652 | 122.1317 | 122.3283 | 122.0824 | -0.47958 | 122.5409 | 122.6945 | 122.4642 | 107.4386 | -123.0274
1984 | 122.7264 | -122.1085 | 0.62256 | 1.4211e-13 | -0.0067905 | -0.013291 | -0.045384 | -0.040643 | -0.010429 | -0.00083919 | -0.016222 | 0.009807 | 0.034709 | 0.0050299 | 0.03777 | 0.019361 | 0.0243 | 0.014482 | 0.10249 | 0.064464 | 0.26559 | 0.088047 | -121.6553 | -14.7202 | -121.7859 | 0.47368 | 0.62724 | 0.40151 | -122.4552 | 122.1965 | -0.52007 | 122.1278 | 122.1229 | -0.073565 | -0.5581 | -0.35697 | -0.34674 | -0.14888 | 0.45319 | 0.32253 | 0.66927 | 0.00468 | -0.22105 | 122.2109 | 122.1729 | 122.374 | 122.1328 | -0.53451 | 122.5821 | 122.7357 | 122.51 | 107.3883 | -123.0778
1985.7812 | 122.7264 | -122.1405 | 0.59052 | 1.4211e-13 | -0.0063633 | -0.013077 | -0.045384 | -0.040643 | -0.010856 | -0.00083919 | -0.016435 | 0.009807 | 0.035136 | 0.0050299 | 0.03777 | 0.010204 | 0.0243 | 0.009904 | 0.11165 | 0.073622 | 0.26559 | 0.092626 | -121.6507 | -14.8621 | -121.7859 | 0.47368 | 0.62266 | 0.39235 | -122.4552 | 122.2331 | -0.47887 | 122.1507 | 122.1504 | -0.082722 | -0.51689 | -0.32493 | -0.3147 | -0.11684 | 0.48981 | 0.35457 | 0.66927 | 0.032146 | -0.19816 | 122.2522 | 122.2141 | 122.4061 | 122.1648 | -0.49789 | 122.6142 | 122.7632 | 122.5329 | 107.2784 | -123.0457
1987.5625 | 122.8455 | -122.0718 | 0.55389 | 1.4211e-13 | -0.0067905 | -0.013077 | -0.045598 | -0.040643 | -0.010643 | -0.0084697 | -0.016222 | 0.0093796 | 0.034709 | 0.0052435 | 0.03777 | 0.010204 | 0.028878 | 0.009904 | 0.10707 | 0.069043 | 0.27017 | 0.10178 | -121.6644 | -14.972 | -121.7905 | 0.46452 | 0.62266 | 0.39235 | -122.4644 | 122.1736 | -0.44683 | 122.082 | 122.0817 | -0.09188 | -0.48485 | -0.28373 | -0.39252 | -0.089371 | 0.40741 | 0.28133 | 0.67385 | 0.068767 | -0.16154 | 122.1789 | 122.1409 | 122.342 | 122.1007 | -0.45211 | 122.5364 | 122.6945 | 122.4642 | 107.0998 | -123.0182
1989.3438 | 122.7127 | -122.1588 | 0.59509 | 1.4211e-13 | -0.0063633 | -0.013077 | -0.045384 | -0.040429 | -0.010429 | 0.0067908 | -0.016435 | 0.009166 | 0.034923 | 0.0052435 | 0.037983 | 0.019361 | 0.019721 | 0.014482 | 0.11165 | 0.069043 | 0.27017 | 0.097205 | -121.6736 | -15.1506 | -121.8042 | 0.45079 | 0.60435 | 0.39693 | -122.4781 | 122.256 | -0.48345 | 122.1782 | 122.1733 | -0.082723 | -0.52605 | -0.32493 | -0.31928 | -0.1443 | 0.48522 | 0.35457 | 0.67385 | 0.009253 | -0.19816 | 122.2705 | 122.2279 | 122.429 | 122.1785 | -0.49789 | 122.6096 | 122.7632 | 122.5557 | 107.0082 | -123.0732
1991.1406 | 122.8271 | -122.1176 | 0.54932 | 1.4211e-13 | -0.0063633 | -0.013077 | -0.045598 | -0.040857 | -0.010643 | -0.00083919 | -0.016222 | 0.0093796 | 0.034923 | 0.0050299 | 0.037983 | 0.023939 | 0.028878 | 0.009904 | 0.10707 | 0.073622 | 0.27475 | 0.083468 | -121.6827 | -15.2422 | -121.8134 | 0.44621 | 0.60435 | 0.37404 | -122.4918 | 122.2011 | -0.44225 | 122.1416 | 122.1275 | -0.073564 | -0.47569 | -0.27457 | -0.37421 | -0.10311 | 0.43487 | 0.30421 | 0.67842 | 0.05503 | -0.17528 | 122.2247 | 122.1912 | 122.3924 | 122.1465 | -0.46585 | 122.5638 | 122.722 | 122.4917 | 106.8754 | -123.0411
1992.8906 | 122.7997 | -122.1268 | 0.54932 | 1.4211e-13 | -0.0065769 | -0.012863 | -0.045598 | -0.040643 | -0.010643 | 0.0067908 | -0.016649 | 0.0093796 | 0.034709 | 0.0050299 | 0.037983 | 0.014783 | 0.028878 | 0.009904 | 0.10707 | 0.078201 | 0.27017 | 0.092626 | -121.6919 | -15.3933 | -121.818 | 0.43705 | 0.59519 | 0.37404 | -122.4964 | 122.2194 | -0.44225 | 122.1416 | 122.1367 | -0.082722 | -0.47112 | -0.27915 | -0.36964 | -0.11226 | 0.43487 | 0.30879 | 0.67843 | 0.045873 | -0.17528 | 122.2338 | 122.205 | 122.3969 | 122.1556 | -0.45669 | 122.5638 | 122.722 | 122.5008 | 106.7335 | -123.0457
1994.6875 | 122.7951 | -122.0901 | 0.55389 | 1.4211e-13 | -0.0063633 | -0.013077 | -0.045811 | -0.040429 | -0.010856 | 0.0067908 | -0.016222 | 0.0093796 | 0.035136 | 0.0048163 | 0.037983 | 0.019361 | 0.019721 | 0.009904 | 0.10707 | 0.073622 | 0.27932 | 0.078889 | -121.6827 | -15.5444 | -121.818 | 0.44163 | 0.59977 | 0.36946 | -122.5056 | 122.169 | -0.44683 | 122.1095 | 122.1001 | -0.068985 | -0.48027 | -0.27457 | -0.41542 | -0.11226 | 0.4074 | 0.27217 | 0.68758 | 0.045874 | -0.18443 | 122.1972 | 122.1638 | 122.3695 | 122.1099 | -0.47501 | 122.5318 | 122.6899 | 122.4596 | 106.5458 | -123.0595
1996.4688 | 122.7631 | -122.1451 | 0.55389 | 1.4211e-13 | -0.0063633 | -0.012863 | -0.045598 | -0.040643 | -0.010856 | -0.0084697 | -0.016222 | 0.009807 | 0.034709 | 0.0052435 | 0.037983 | 0.010204 | 0.0243 | 0.005325 | 0.10249 | 0.073622 | 0.26559 | 0.10178 | -121.6873 | -15.6405 | -121.8226 | 0.44163 | 0.59061 | 0.35572 | -122.5147 | 122.2469 | -0.4514 | 122.1553 | 122.1504 | -0.096459 | -0.48027 | -0.28831 | -0.36964 | -0.11226 | 0.45776 | 0.32252 | 0.69216 | 0.036716 | -0.19817 | 122.2476 | 122.2187 | 122.4107 | 122.1694 | -0.45211 | 122.5867 | 122.7357 | 122.5008 | 106.5046 | -123.0686
1998.1875 | 122.8409 | -122.1268 | 0.54016 | 1.4211e-13 | -0.0065769 | -0.013505 | -0.045598 | -0.040643 | -0.010856 | -0.0084697 | -0.016222 | 0.0095932 | 0.034923 | 0.0050299 | 0.03777 | 0.019361 | 0.0243 | 0.014482 | 0.10707 | 0.073622 | 0.27017 | 0.097205 | -121.6919 | -15.7596 | -121.8271 | 0.44163 | 0.59061 | 0.35572 | -122.5101 | 122.224 | -0.43309 | 122.1461 | 122.1413 | -0.082723 | -0.46654 | -0.26999 | -0.38337 | -0.09853 | 0.43487 | 0.29963 | 0.683 | 0.050449 | -0.18444 | 122.2338 | 122.2004 | 122.3969 | 122.1511 | -0.44296 | 122.5684 | 122.7174 | 122.4825 | 106.3672 | -123.0503
1999.9844 | 122.8592 | -122.1176 | 0.49896 | 1.4211e-13 | -0.0067905 | -0.013077 | -0.045811 | -0.040216 | -0.010643 | -0.00083919 | -0.016435 | 0.0095932 | 0.034709 | 0.0050299 | 0.037983 | 0.010204 | 0.019721 | 0.009904 | 0.10707 | 0.073622 | 0.26559 | 0.088047 | -121.6965 | -15.8878 | -121.8317 | 0.4279 | 0.57688 | 0.35572 | -122.5239 | 122.2057 | -0.39189 | 122.1278 | 122.1275 | -0.078143 | -0.42534 | -0.23337 | -0.40627 | -0.071067 | 0.42113 | 0.2859 | 0.69216 | 0.077913 | -0.14324 | 122.2247 | 122.1912 | 122.3832 | 122.1373 | -0.41092 | 122.5455 | 122.6945 | 122.4733 | 106.2299 | -123.0228
2001.7188 | 122.8546 | -122.1405 | 0.5127 | 1.4211e-13 | -0.0067905 | -0.012863 | -0.045384 | -0.040216 | -0.010856 | -0.0084697 | -0.016222 | 0.0093796 | 0.034709 | 0.0050299 | 0.037983 | 0.014783 | 0.028878 | 0.014482 | 0.11165 | 0.073622 | 0.27017 | 0.083468 | -121.6919 | -15.9793 | -121.8271 | 0.4279 | 0.58603 | 0.3603 | -122.5239 | 122.224 | -0.40105 | 122.1553 | 122.155 | -0.068986 | -0.43907 | -0.24253 | -0.38338 | -0.0848 | 0.4486 | 0.31336 | 0.69674 | 0.073337 | -0.15239 | 122.2522 | 122.2141 | 122.4107 | 122.1694 | -0.42923 | 122.5684 | 122.7265 | 122.5008 | 106.1612 | -123.0366
2003.5156 | 122.7631 | -122.1634 | 0.54932 | 1.4211e-13 | -0.0067905 | -0.013077 | -0.045384 | -0.040429 | -0.011284 | -0.00083919 | -0.016008 | 0.009166 | 0.034709 | 0.0052435 | 0.03777 | 0.010204 | 0.019721 | 0.000747 | 0.097912 | 0.073622 | 0.27017 | 0.088047 | -121.6965 | -16.1259 | -121.8363 | 0.4279 | 0.57688 | 0.35572 | -122.5239 | 122.2514 | -0.4514 | 122.1736 | 122.1641 | -0.0873 | -0.47569 | -0.27915 | -0.36049 | -0.12142 | 0.46691 | 0.32709 | 0.68758 | 0.027559 | -0.19359 | 122.2613 | 122.237 | 122.4336 | 122.1831 | -0.46127 | 122.5913 | 122.7403 | 122.5191 | 106.0375 | -123.0732
2005.2344 | 122.731 | -122.1634 | 0.54932 | 1.4211e-13 | -0.0065769 | -0.013505 | -0.045598 | -0.040643 | -0.010856 | -0.00083919 | -0.016008 | 0.0095932 | 0.034923 | 0.0054573 | 0.037983 | 0.019361 | 0.028878 | 0.009904 | 0.10707 | 0.078201 | 0.27017 | 0.10178 | -121.7056 | -16.2312 | -121.8409 | 0.41874 | 0.5723 | 0.34657 | -122.5239 | 122.2652 | -0.44225 | 122.1828 | 122.1733 | -0.09188 | -0.47112 | -0.27915 | -0.36049 | -0.13058 | 0.45775 | 0.32252 | 0.68301 | 0.02298 | -0.20275 | 122.2705 | 122.2416 | 122.4336 | 122.1923 | -0.44753 | 122.5821 | 122.7357 | 122.51 | 105.9322 | -123.0732
2007.0156 | 122.7631 | -122.1817 | 0.54932 | 1.4211e-13 | -0.0067905 | -0.013077 | -0.045384 | -0.040429 | -0.010643 | -0.00083919 | -0.016222 | 0.009166 | 0.034709 | 0.0048163 | 0.03777 | 0.014783 | 0.015142 | 0.009904 | 0.10707 | 0.069043 | 0.27932 | 0.097205 | -121.7011 | -16.4281 | -121.8546 | 0.41874 | 0.56772 | 0.34199 | -122.5239 | 122.2789 | -0.44225 | 122.1965 | 122.1916 | -0.087301 | -0.48027 | -0.26999 | -0.34218 | -0.13058 | 0.48064 | 0.32709 | 0.66927 | 0.018401 | -0.20733 | 122.2888 | 122.2507 | 122.461 | 122.1968 | -0.45211 | 122.6004 | 122.7494 | 122.5237 | 105.7536 | -123.0732
2008.7969 | 122.8729 | -122.1451 | 0.50354 | 1.4211e-13 | -0.0065769 | -0.013505 | -0.045598 | -0.040216 | -0.010643 | -0.00083919 | -0.016222 | 0.0095932 | 0.034709 | 0.0052435 | 0.037983 | 0.010204 | 0.028878 | 0.014482 | 0.11165 | 0.064464 | 0.27017 | 0.069732 | -121.7194 | -16.5791 | -121.8409 | 0.40958 | 0.56772 | 0.34199 | -122.5376 | 122.2148 | -0.39189 | 122.1553 | 122.1596 | -0.05525 | -0.43908 | -0.23337 | -0.39254 | -0.093959 | 0.42571 | 0.30421 | 0.69674 | 0.064177 | -0.16155 | 122.2567 | 122.2095 | 122.4152 | 122.174 | -0.43381 | 122.5547 | 122.7128 | 122.4871 | 105.5659 | -123.0412
2010.5938 | 122.8317 | -122.1542 | 0.50354 | 1.4211e-13 | -0.0067905 | -0.013291 | -0.045384 | -0.040857 | -0.010856 | 0.0067908 | -0.016222 | 0.009166 | 0.034496 | 0.0054573 | 0.03777 | 0.019361 | 0.0243 | 0.005325 | 0.11165 | 0.064464 | 0.27932 | 0.083468 | -121.724 | -16.7211 | -121.8592 | 0.40042 | 0.55856 | 0.33283 | -122.5422 | 122.2377 | -0.39189 | 122.1736 | 122.1596 | -0.078143 | -0.43908 | -0.22422 | -0.38796 | -0.10312 | 0.43028 | 0.29505 | 0.68301 | 0.05502 | -0.17071 | 122.2659 | 122.2187 | 122.4336 | 122.1785 | -0.42007 | 122.5547 | 122.7128 | 122.4871 | 105.4331 | -123.0457
2012.3125 | 122.7585 | -122.1817 | 0.52643 | 1.4211e-13 | -0.0072179 | -0.013505 | -0.045384 | -0.040216 | -0.011284 | -0.0161 | -0.016222 | 0.0089522 | 0.034709 | 0.0052435 | 0.037983 | 0.019361 | 0.0243 | 0.005325 | 0.10707 | 0.078201 | 0.27017 | 0.065153 | -121.7194 | -16.8539 | -121.8546 | 0.405 | 0.55398 | 0.37404 | -122.5514 | 122.2469 | -0.41936 | 122.2011 | 122.187 | -0.059828 | -0.44823 | -0.25626 | -0.36965 | -0.12143 | 0.46233 | 0.32709 | 0.69674 | 0.027554 | -0.15239 | 122.2888 | 122.2599 | 122.4519 | 122.206 | -0.46127 | 122.5867 | 122.7357 | 122.5557 | 105.3278 | -123.0778
2014.125 | 122.8683 | -122.1725 | 0.5127 | 1.4211e-13 | -0.0067905 | -0.013505 | -0.045384 | -0.040857 | -0.010643 | -0.00083919 | -0.016435 | 0.0095932 | 0.034496 | 0.0054573 | 0.03777 | 0.014783 | 0.028878 | 0.009904 | 0.11165 | 0.069043 | 0.27475 | 0.10636 | -121.7194 | -16.9958 | -121.8455 | 0.40042 | 0.56772 | 0.36946 | -122.5514 | 122.2789 | -0.40105 | 122.1873 | 122.1825 | -0.096459 | -0.44365 | -0.23795 | -0.37881 | -0.11227 | 0.45317 | 0.32709 | 0.7059 | 0.055022 | -0.14324 | 122.2842 | 122.2416 | 122.4473 | 122.2014 | -0.40633 | 122.573 | 122.7403 | 122.542 | 105.1767 | -123.064
2015.8438 | 122.7402 | -122.2137 | 0.53101 | 1.4211e-13 | -0.0065769 | -0.013291 | -0.046025 | -0.040429 | -0.010856 | -0.00083919 | -0.016435 | 0.0093796 | 0.035136 | 0.0052435 | 0.037983 | 0.010204 | 0.0243 | 0.014482 | 0.11165 | 0.073622 | 0.26559 | 0.088047 | -121.7102 | -17.1606 | -121.8546 | 0.40958 | 0.55856 | 0.34657 | -122.5468 | 122.3018 | -0.41936 | 122.2239 | 122.2282 | -0.073565 | -0.45738 | -0.26542 | -0.33303 | -0.12143 | 0.50353 | 0.35913 | 0.69216 | 0.027554 | -0.18444 | 122.3254 | 122.2874 | 122.4793 | 122.238 | -0.44296 | 122.6233 | 122.7723 | 122.5603 | 105.0531 | -123.0778
2017.6406 | 122.8592 | -122.1542 | 0.5127 | 1.4211e-13 | -0.0065769 | -0.013077 | -0.045598 | -0.040857 | -0.010856 | -0.00083919 | -0.016435 | 0.0095932 | 0.034709 | 0.0050299 | 0.03777 | 0.019361 | 0.0243 | 0.01906 | 0.10707 | 0.064464 | 0.27017 | 0.097205 | -121.7102 | -17.3072 | -121.85 | 0.41416 | 0.56314 | 0.39693 | -122.5514 | 122.2514 | -0.40563 | 122.1736 | 122.1733 | -0.078145 | -0.44823 | -0.24253 | -0.39712 | -0.098535 | 0.44402 | 0.3042 | 0.70132 | 0.050444 | -0.11576 | 122.2613 | 122.2187 | 122.4244 | 122.1785 | -0.41549 | 122.5684 | 122.7174 | 122.5512 | 104.8471 | -123.064
2019.4219 | 122.8592 | -122.1497 | 0.5127 | 1.4211e-13 | -0.0067905 | -0.013077 | -0.045811 | -0.040643 | -0.01107 | -0.00083919 | -0.016222 | 0.0093796 | 0.034709 | 0.0056709 | 0.037556 | 0.019361 | 0.028878 | 0.009904 | 0.11165 | 0.069043 | 0.27475 | 0.092626 | -121.7148 | -17.4583 | -121.8455 | 0.40958 | 0.55856 | 0.35115 | -122.5514 | 122.2423 | -0.40105 | 122.169 | 122.1596 | -0.082722 | -0.44365 | -0.23795 | -0.4017 | -0.10311 | 0.43486 | 0.3042 | 0.7059 | 0.045865 | -0.16155 | 122.2613 | 122.2187 | 122.4244 | 122.1785 | -0.42007 | 122.5592 | 122.7082 | 122.5008 | 104.6914 | -123.064
2021.1562 | 122.8043 | -122.1771 | 0.5127 | 1.4211e-13 | -0.0065769 | -0.013291 | -0.04517 | -0.040643 | -0.01107 | -0.00083919 | -0.016222 | 0.0093796 | 0.034923 | 0.0052435 | 0.037983 | 0.019361 | 0.019721 | 0.01906 | 0.10707 | 0.073622 | 0.27017 | 0.078889 | -121.7102 | -17.6231 | -121.8363 | 0.41416 | 0.56314 | 0.34657 | -122.5514 | 122.256 | -0.40563 | 122.1965 | 122.1962 | -0.059829 | -0.43907 | -0.24253 | -0.37423 | -0.098535 | 0.46691 | 0.34083 | 0.71506 | 0.050444 | -0.16613 | 122.2842 | 122.2507 | 122.4473 | 122.1968 | -0.43381 | 122.5913 | 122.7403 | 122.5237 | 104.554 | -123.064
2022.9375 | 122.8821 | -122.1588 | 0.50354 | 1.4211e-13 | -0.0070043 | -0.013077 | -0.045598 | -0.040429 | -0.010856 | -0.0084697 | -0.016435 | 0.0095932 | 0.034709 | 0.0054573 | 0.03777 | 0.023939 | 0.0243 | 0.009904 | 0.11165 | 0.073622 | 0.26559 | 0.11094 | -121.7102 | -17.7605 | -121.8455 | 0.40042 | 0.56314 | 0.42898 | -122.5559 | 122.2698 | -0.39189 | 122.1828 | 122.1687 | -0.10104 | -0.42992 | -0.23795 | -0.39712 | -0.10312 | 0.44859 | 0.31336 | 0.71048 | 0.059599 | -0.074558 | 122.2705 | 122.2324 | 122.4244 | 122.1831 | -0.3926 | 122.5592 | 122.722 | 122.5878 | 104.3984 | -123.0595
2024.7344 | 122.8317 | -122.1954 | 0.49439 | 1.4211e-13 | -0.0070043 | -0.013077 | -0.045598 | -0.040643 | -0.01107 | -0.00083919 | -0.016008 | 0.0093796 | 0.035136 | 0.0054573 | 0.037556 | 0.019361 | 0.019721 | 0.01906 | 0.11165 | 0.069043 | 0.26559 | 0.092626 | -121.7194 | -17.9207 | -121.85 | 0.405 | 0.55856 | 0.35572 | -122.5697 | 122.2881 | -0.38274 | 122.2148 | 122.2145 | -0.073566 | -0.42534 | -0.2288 | -0.37423 | -0.089382 | 0.47606 | 0.3454 | 0.71964 | 0.064175 | -0.13866 | 122.3071 | 122.2645 | 122.461 | 122.2152 | -0.40176 | 122.6004 | 122.754 | 122.5512 | 104.2747 | -123.0641
2026.5156 | 122.7814 | -122.2092 | 0.53558 | 1.4211e-13 | -0.0074317 | -0.013291 | -0.045384 | -0.040643 | -0.010643 | -0.0084697 | -0.016435 | 0.0089522 | 0.034923 | 0.0054573 | 0.038197 | 0.019361 | 0.0243 | 0.005325 | 0.10707 | 0.069043 | 0.27475 | 0.10178 | -121.7194 | -18.0855 | -121.85 | 0.39585 | 0.55398 | 0.32825 | -122.5697 | 122.311 | -0.42852 | 122.2285 | 122.2145 | -0.096459 | -0.46654 | -0.26084 | -0.3605 | -0.13974 | 0.48979 | 0.35913 | 0.71964 | 0.018399 | -0.20733 | 122.3162 | 122.2782 | 122.4839 | 122.2335 | -0.4338 | 122.605 | 122.7631 | 122.5374 | 104.1236 | -123.1053
2028.2812 | 122.7905 | -122.2046 | 0.50812 | 1.4211e-13 | -0.0072179 | -0.013291 | -0.045384 | -0.040216 | -0.01107 | -0.00083919 | -0.016222 | 0.0095932 | 0.034709 | 0.0052435 | 0.037983 | 0.019361 | 0.019721 | 0.014482 | 0.11165 | 0.069043 | 0.27475 | 0.092626 | -121.7194 | -18.2366 | -121.8546 | 0.39585 | 0.5494 | 0.35115 | -122.5605 | 122.2972 | -0.39647 | 122.224 | 122.2191 | -0.078144 | -0.43907 | -0.23337 | -0.35592 | -0.11227 | 0.48521 | 0.34998 | 0.7059 | 0.041285 | -0.15697 | 122.3162 | 122.2736 | 122.4793 | 122.2243 | -0.41549 | 122.6004 | 122.754 | 122.5557 | 103.9679 | -123.0686
2030.0625 | 122.7768 | -122.2046 | 0.5127 | 1.4211e-13 | -0.0070043 | -0.013291 | -0.045598 | -0.040643 | -0.010643 | -0.0161 | -0.015794 | 0.009166 | 0.034496 | 0.0052435 | 0.038197 | 0.019361 | 0.028878 | 0.005325 | 0.10707 | 0.069043 | 0.27475 | 0.083468 | -121.7194 | -18.342 | -121.85 | 0.40042 | 0.5494 | 0.34657 | -122.5697 | 122.2881 | -0.40563 | 122.224 | 122.2099 | -0.078143 | -0.44365 | -0.23795 | -0.36508 | -0.11227 | 0.48521 | 0.35456 | 0.71964 | 0.036708 | -0.16613 | 122.3117 | 122.2736 | 122.4793 | 122.2335 | -0.42923 | 122.605 | 122.754 | 122.5512 | 103.8626 | -123.0824
2031.8438 | 122.8958 | -122.1771 | 0.47607 | 1.4211e-13 | -0.0070043 | -0.013291 | -0.045384 | -0.04107 | -0.010643 | -0.00083919 | -0.016222 | 0.0093796 | 0.034923 | 0.0054573 | 0.038197 | 0.023939 | 0.015142 | 0.014482 | 0.11165 | 0.08278 | 0.27475 | 0.069732 | -121.7194 | -18.5388 | -121.8592 | 0.38211 | 0.54025 | 0.39693 | -122.5788 | 122.2469 | -0.36443 | 122.2011 | 122.1916 | -0.05525 | -0.39329 | -0.20133 | -0.4017 | -0.093964 | 0.45775 | 0.31793 | 0.71964 | 0.064172 | -0.079142 | 122.2888 | 122.2599 | 122.4519 | 122.1923 | -0.40634 | 122.5592 | 122.7174 | 122.5741 | 103.6383 | -123.0549
2033.5625 | 122.7448 | -122.2504 | 0.53101 | 1.4211e-13 | -0.0070043 | -0.013077 | -0.04517 | -0.040643 | -0.010856 | -0.0161 | -0.016649 | 0.009807 | 0.035136 | 0.0052435 | 0.037983 | 0.014783 | 0.0243 | 0.009904 | 0.11165 | 0.073622 | 0.27475 | 0.097205 | -121.7285 | -18.7037 | -121.8592 | 0.38669 | 0.54025 | 0.36946 | -122.5834 | 122.3476 | -0.41936 | 122.2651 | 122.2603 | -0.087301 | -0.45738 | -0.25626 | -0.33304 | -0.14432 | 0.52183 | 0.39118 | 0.72421 | 0.00924 | -0.16155 | 122.362 | 122.324 | 122.5251 | 122.2747 | -0.4338 | 122.6371 | 122.7906 | 122.6198 | 103.5467 | -123.1144
2035.3438 | 122.8775 | -122.1725 | 0.48065 | 1.4211e-13 | -0.0072179 | -0.013077 | -0.04517 | -0.04107 | -0.010856 | -0.00083919 | -0.016649 | 0.0093796 | 0.034496 | 0.0054573 | 0.038197 | 0.019361 | 0.0243 | 0.028217 | 0.11165 | 0.069043 | 0.27475 | 0.088047 | -121.724 | -18.8731 | -121.8638 | 0.38211 | 0.54482 | 0.3603 | -122.5834 | 122.2606 | -0.36901 | 122.1919 | 122.2008 | -0.05983 | -0.41161 | -0.20591 | -0.41086 | -0.098542 | 0.44859 | 0.30878 | 0.71964 | 0.064172 | -0.12035 | 122.2842 | 122.2416 | 122.4473 | 122.1968 | -0.39261 | 122.5547 | 122.7174 | 122.5328 | 103.2995 | -123.0641
2037.125 | 122.7493 | -122.2321 | 0.53101 | 1.4211e-13 | -0.0072179 | -0.013291 | -0.045598 | -0.040643 | -0.010856 | -0.0084697 | -0.016222 | 0.0095932 | 0.034709 | 0.0058847 | 0.037983 | 0.019361 | 0.019721 | 0.014482 | 0.11165 | 0.08278 | 0.27475 | 0.051416 | -121.7285 | -19.0242 | -121.8638 | 0.38211 | 0.54025 | 0.3603 | -122.5926 | 122.2835 | -0.41936 | 122.2514 | 122.2465 | -0.036934 | -0.44823 | -0.25626 | -0.36051 | -0.1489 | 0.50352 | 0.36829 | 0.72879 | 0.00924 | -0.1707 | 122.3437 | 122.3148 | 122.5068 | 122.2518 | -0.47959 | 122.6142 | 122.7723 | 122.5924 | 103.2079 | -123.1236
2038.8438 | 122.8775 | -122.1909 | 0.48065 | 1.4211e-13 | -0.0074317 | -0.013291 | -0.045384 | -0.040643 | -0.011284 | -0.00083919 | -0.016222 | 0.0093796 | 0.034709 | 0.0054573 | 0.038197 | 0.014783 | 0.0243 | 0.009904 | 0.11622 | 0.069043 | 0.27017 | 0.078889 | -121.7331 | -19.1936 | -121.8638 | 0.37753 | 0.54025 | 0.39693 | -122.5971 | 122.2697 | -0.36443 | 122.2056 | 122.2008 | -0.068985 | -0.41161 | -0.21049 | -0.40629 | -0.10312 | 0.45775 | 0.32709 | 0.73337 | 0.059594 | -0.08372 | 122.3071 | 122.2599 | 122.461 | 122.2152 | -0.40176 | 122.5684 | 122.7311 | 122.5878 | 102.9973 | -123.0778
2040.6406 | 122.818 | -122.2321 | 0.50354 | 1.4211e-13 | -0.0070043 | -0.013291 | -0.04517 | -0.040429 | -0.010856 | -0.0084697 | -0.016649 | 0.009807 | 0.034923 | 0.0056709 | 0.037556 | 0.019361 | 0.0243 | 0.009904 | 0.11622 | 0.064464 | 0.27475 | 0.069732 | -121.7423 | -19.3493 | -121.8729 | 0.37753 | 0.53567 | 0.33741 | -122.6017 | 122.3018 | -0.38731 | 122.2514 | 122.242 | -0.059828 | -0.43908 | -0.22879 | -0.36966 | -0.12601 | 0.48979 | 0.35913 | 0.72879 | 0.032127 | -0.16613 | 122.3483 | 122.2965 | 122.5068 | 122.2564 | -0.43381 | 122.6096 | 122.7677 | 122.5695 | 102.8828 | -123.1053
2042.4219 | 122.8592 | -122.2321 | 0.48065 | 1.4211e-13 | -0.0072179 | -0.013077 | -0.045598 | -0.040643 | -0.01107 | -0.0084697 | -0.016435 | 0.009807 | 0.034923 | 0.0052435 | 0.038197 | 0.023939 | 0.019721 | 0.009904 | 0.10707 | 0.078201 | 0.27017 | 0.069732 | -121.7468 | -19.5462 | -121.8775 | 0.36838 | 0.53567 | 0.3191 | -122.6109 | 122.3018 | -0.37358 | 122.256 | 122.242 | -0.059828 | -0.40245 | -0.21049 | -0.37882 | -0.11228 | 0.48521 | 0.35455 | 0.73337 | 0.055015 | -0.16156 | 122.3391 | 122.3103 | 122.5022 | 122.2518 | -0.41092 | 122.6004 | 122.7677 | 122.5512 | 102.6859 | -123.0915
2044.1562 | 122.7676 | -122.2595 | 0.48523 | 1.4211e-13 | -0.0067905 | -0.013077 | -0.045598 | -0.040429 | -0.010856 | -0.0161 | -0.016222 | 0.009166 | 0.035136 | 0.0056709 | 0.037983 | 0.010204 | 0.028878 | 0.009904 | 0.10707 | 0.069043 | 0.27932 | 0.083468 | -121.7468 | -19.7293 | -121.8821 | 0.36838 | 0.52651 | 0.30078 | -122.6155 | 122.343 | -0.37816 | 122.2697 | 122.2694 | -0.073564 | -0.41619 | -0.20591 | -0.35594 | -0.11685 | 0.51267 | 0.37744 | 0.73337 | 0.041281 | -0.18445 | 122.3666 | 122.3286 | 122.5388 | 122.2884 | -0.40176 | 122.6279 | 122.786 | 122.5603 | 102.5302 | -123.1007
2045.9531 | 122.7951 | -122.2549 | 0.48981 | 1.4211e-13 | -0.0072179 | -0.013291 | -0.045384 | -0.040216 | -0.010856 | -0.00083919 | -0.016008 | 0.009166 | 0.034709 | 0.0056709 | 0.037983 | 0.019361 | 0.028878 | 0.009904 | 0.10249 | 0.073622 | 0.27932 | 0.088047 | -121.7423 | -19.8163 | -121.8775 | 0.37295 | 0.52193 | 0.31452 | -122.6109 | 122.343 | -0.38732 | 122.2743 | 122.2648 | -0.078143 | -0.41618 | -0.21048 | -0.35593 | -0.11685 | 0.51268 | 0.37744 | 0.73337 | 0.032124 | -0.17529 | 122.3574 | 122.3286 | 122.5343 | 122.2838 | -0.40176 | 122.6279 | 122.7769 | 122.5695 | 102.4386 | -123.1007
2047.7344 | 122.8363 | -122.2275 | 0.44403 | 1.4211e-13 | -0.0070043 | -0.013291 | -0.04517 | -0.040643 | -0.010856 | -0.0084697 | -0.016649 | 0.009807 | 0.034709 | 0.0056709 | 0.038197 | 0.019361 | 0.028878 | 0.005325 | 0.10707 | 0.073622 | 0.27475 | 0.069732 | -121.7423 | -20.0681 | -121.8821 | 0.35922 | 0.51735 | 0.36946 | -122.6246 | 122.2972 | -0.33696 | 122.2468 | 122.2328 | -0.064407 | -0.37041 | -0.16929 | -0.39714 | -0.084813 | 0.48521 | 0.34539 | 0.74253 | 0.073322 | -0.074571 | 122.3345 | 122.3011 | 122.5022 | 122.2564 | -0.3743 | 122.5867 | 122.7448 | 122.5969 | 102.1594 | -123.0686
2049.4531 | 122.8912 | -122.2092 | 0.45776 | 1.4211e-13 | -0.0074317 | -0.013291 | -0.045598 | -0.040643 | -0.011284 | -0.00083919 | -0.016435 | 0.0093796 | 0.034709 | 0.0058847 | 0.037983 | 0.019361 | 0.019721 | 0.014482 | 0.11165 | 0.064464 | 0.27932 | 0.07431 | -121.7468 | -20.2055 | -121.8821 | 0.35922 | 0.52651 | 0.30536 | -122.6246 | 122.2835 | -0.34612 | 122.2285 | 122.2236 | -0.059828 | -0.3933 | -0.17844 | -0.41545 | -0.098546 | 0.46232 | 0.32708 | 0.74253 | 0.068746 | -0.1524 | 122.3208 | 122.2736 | 122.4885 | 122.2289 | -0.38345 | 122.5684 | 122.7357 | 122.5145 | 102.0037 | -123.0824
2051.2188 | 122.8775 | -122.2321 | 0.45319 | 1.4211e-13 | -0.0074317 | -0.013077 | -0.045384 | -0.040643 | -0.01107 | -0.0084697 | -0.016435 | 0.0093796 | 0.035136 | 0.0058847 | 0.037983 | 0.019361 | 0.019721 | 0.014482 | 0.11165 | 0.078201 | 0.27475 | 0.083468 | -121.7468 | -20.3795 | -121.8867 | 0.34548 | 0.50362 | 0.29162 | -122.6338 | 122.3155 | -0.34154 | 122.2514 | 122.2465 | -0.068986 | -0.37498 | -0.17844 | -0.40172 | -0.1077 | 0.48521 | 0.34539 | 0.74711 | 0.050431 | -0.16156 | 122.3437 | 122.3103 | 122.5068 | 122.2518 | -0.36972 | 122.5775 | 122.7357 | 122.5237 | 101.8526 | -123.087
2052.9531 | 122.8775 | -122.2412 | 0.44861 | 1.4211e-13 | -0.0074317 | -0.01265 | -0.045598 | -0.040857 | -0.010643 | -0.00083919 | -0.016008 | 0.0093796 | 0.034923 | 0.0054573 | 0.038197 | 0.019361 | 0.0243 | 0.009904 | 0.10707 | 0.078201 | 0.27932 | 0.10178 | -121.756 | -20.5535 | -121.8867 | 0.35006 | 0.5082 | 0.28247 | -122.6384 | 122.343 | -0.34154 | 122.2606 | 122.2511 | -0.09188 | -0.37041 | -0.16928 | -0.39714 | -0.098547 | 0.48521 | 0.35455 | 0.75169 | 0.059588 | -0.16614 | 122.3483 | 122.3194 | 122.5205 | 122.2655 | -0.34682 | 122.5913 | 122.7494 | 122.5237 | 101.6877 | -123.087
2054.7344 | 122.8455 | -122.2412 | 0.42572 | 1.4211e-13 | -0.0074317 | -0.013505 | -0.045384 | -0.040643 | -0.010856 | -0.0084697 | -0.016649 | 0.0093796 | 0.034923 | 0.0056709 | 0.037983 | 0.019361 | 0.019721 | 0.014482 | 0.11622 | 0.069043 | 0.27932 | 0.088047 | -121.7606 | -20.7732 | -121.8912 | 0.34548 | 0.49904 | 0.31452 | -122.6429 | 122.3293 | -0.30949 | 122.2606 | 122.2557 | -0.073565 | -0.35668 | -0.1464 | -0.40172 | -0.080238 | 0.48063 | 0.34997 | 0.75169 | 0.073318 | -0.1112 | 122.3574 | 122.3103 | 122.5205 | 122.2609 | -0.33767 | 122.5867 | 122.7402 | 122.5557 | 101.468 | -123.0687
2056.5156 | 122.8546 | -122.2595 | 0.45776 | 1.4211e-13 | -0.0074317 | -0.013291 | -0.045598 | -0.040857 | -0.011284 | -0.00083919 | -0.016649 | 0.0095932 | 0.034709 | 0.0060983 | 0.038197 | 0.019361 | 0.0243 | 0.014482 | 0.11165 | 0.08278 | 0.27017 | 0.10178 | -121.7606 | -20.9335 | -121.9004 | 0.34548 | 0.49904 | 0.3603 | -122.6429 | 122.3613 | -0.34612 | 122.2789 | 122.274 | -0.087302 | -0.37498 | -0.1876 | -0.38341 | -0.11228 | 0.49894 | 0.35912 | 0.74253 | 0.041274 | -0.097461 | 122.3712 | 122.3423 | 122.5297 | 122.2838 | -0.35598 | 122.605 | 122.7586 | 122.6198 | 101.326 | -123.1007
2058.2969 | 122.9004 | -122.2275 | 0.44403 | 1.4211e-13 | -0.0074317 | -0.013077 | -0.045384 | -0.040429 | -0.01107 | -0.0084697 | -0.016649 | 0.010021 | 0.034923 | 0.0056709 | 0.038411 | 0.014783 | 0.019721 | 0.009904 | 0.11165 | 0.078201 | 0.27932 | 0.042258 | -121.7606 | -21.1075 | -121.8912 | 0.3409 | 0.49446 | 0.33283 | -122.6475 | 122.2697 | -0.33238 | 122.2423 | 122.2374 | -0.032354 | -0.36583 | -0.16471 | -0.42003 | -0.10313 | 0.46689 | 0.33624 | 0.75627 | 0.050429 | -0.1112 | 122.3391 | 122.3057 | 122.5068 | 122.2472 | -0.40177 | 122.5684 | 122.7219 | 122.5603 | 101.12 | -123.0915
2060.0938 | 122.9004 | -122.2595 | 0.43945 | 1.4211e-13 | -0.0074317 | -0.01265 | -0.045598 | -0.040643 | -0.01107 | 0.014421 | -0.016222 | 0.009166 | 0.034923 | 0.0058847 | 0.037983 | 0.019361 | 0.0243 | 0.005325 | 0.10249 | 0.073622 | 0.27017 | 0.078889 | -121.7606 | -21.3502 | -121.9004 | 0.3409 | 0.49904 | 0.30994 | -122.6521 | 122.3384 | -0.33696 | 122.2789 | 122.2648 | -0.073564 | -0.36583 | -0.16929 | -0.39257 | -0.098549 | 0.49894 | 0.35912 | 0.75169 | 0.059585 | -0.12951 | 122.362 | 122.3331 | 122.5297 | 122.2838 | -0.36056 | 122.6004 | 122.7586 | 122.5695 | 100.9094 | -123.0915
2061.8125 | 122.7722 | -122.287 | 0.46692 | 1.4211e-13 | -0.0072179 | -0.012863 | -0.045384 | -0.040643 | -0.01107 | -0.00083919 | -0.016649 | 0.0095932 | 0.034709 | 0.0056709 | 0.037983 | 0.019361 | 0.0243 | 0.005325 | 0.10707 | 0.073622 | 0.26559 | 0.083468 | -121.7606 | -21.5287 | -121.9004 | 0.33632 | 0.48988 | 0.27789 | -122.6567 | 122.3705 | -0.35985 | 122.3063 | 122.2923 | -0.078143 | -0.3933 | -0.20133 | -0.36968 | -0.13059 | 0.5264 | 0.38659 | 0.75627 | 0.022962 | -0.18903 | 122.3941 | 122.3606 | 122.5526 | 122.3113 | -0.38345 | 122.6233 | 122.7769 | 122.5649 | 100.7583 | -123.1236
2063.5938 | 122.8683 | -122.2504 | 0.45319 | 1.4211e-13 | -0.0074317 | -0.013077 | -0.045384 | -0.040857 | -0.01107 | 0.0067908 | -0.016222 | 0.0095932 | 0.034923 | 0.0060983 | 0.037983 | 0.014783 | 0.0243 | 0.01906 | 0.1208 | 0.073622 | 0.27932 | 0.07431 | -121.7652 | -21.6615 | -121.905 | 0.33175 | 0.48988 | 0.27331 | -122.6658 | 122.3247 | -0.33238 | 122.2651 | 122.2694 | -0.05525 | -0.37956 | -0.17386 | -0.41546 | -0.12144 | 0.4852 | 0.34539 | 0.76085 | 0.036695 | -0.17988 | 122.3712 | 122.324 | 122.5297 | 122.2747 | -0.37888 | 122.5821 | 122.7402 | 122.5237 | 100.5888 | -123.119
2065.3906 | 122.7585 | -122.2824 | 0.47607 | 1.4211e-13 | -0.0072179 | -0.013291 | -0.045598 | -0.040643 | -0.010856 | -0.0084697 | -0.016222 | 0.0093796 | 0.034496 | 0.0056709 | 0.03777 | 0.014783 | 0.0243 | 0.014482 | 0.11165 | 0.064464 | 0.27932 | 0.055995 | -121.7606 | -21.8859 | -121.9004 | 0.3409 | 0.48988 | 0.2962 | -122.6612 | 122.3384 | -0.36443 | 122.2972 | 122.2969 | -0.041513 | -0.41161 | -0.19675 | -0.37883 | -0.13517 | 0.52183 | 0.38201 | 0.76085 | 0.013807 | -0.17987 | 122.3941 | 122.3469 | 122.5617 | 122.3067 | -0.42008 | 122.6233 | 122.7723 | 122.5786 | 100.3965 | -123.1373
2067.1719 | 122.8317 | -122.2733 | 0.45776 | 1.4211e-13 | -0.0076453 | -0.013077 | -0.045384 | -0.040857 | -0.010856 | -0.0161 | -0.016435 | 0.0093796 | 0.034923 | 0.0058847 | 0.037983 | 0.019361 | 0.028878 | 0.005325 | 0.10249 | 0.073622 | 0.27475 | 0.092626 | -121.7606 | -22.0599 | -121.8958 | 0.33632 | 0.4853 | 0.27331 | -122.6658 | 122.3659 | -0.35527 | 122.2926 | 122.2786 | -0.087301 | -0.38414 | -0.18302 | -0.39257 | -0.12144 | 0.51267 | 0.37743 | 0.77 | 0.027539 | -0.18445 | 122.3757 | 122.3469 | 122.548 | 122.3021 | -0.36514 | 122.6096 | 122.7586 | 122.5466 | 100.2134 | -123.1236
2068.8906 | 122.8546 | -122.2595 | 0.45319 | 1.4211e-13 | -0.0072179 | -0.013077 | -0.045384 | -0.04107 | -0.01107 | -0.0084697 | -0.016435 | 0.0087386 | 0.035136 | 0.0060983 | 0.038197 | 0.019361 | 0.028878 | 0.009904 | 0.11165 | 0.069043 | 0.27017 | 0.060574 | -121.7606 | -22.2476 | -121.9004 | 0.33175 | 0.4853 | 0.27789 | -122.6612 | 122.3201 | -0.34154 | 122.2789 | 122.2694 | -0.05067 | -0.38414 | -0.18302 | -0.40172 | -0.12144 | 0.49894 | 0.35912 | 0.76085 | 0.032117 | -0.1753 | 122.3712 | 122.3286 | 122.5297 | 122.2884 | -0.39261 | 122.5913 | 122.7448 | 122.5374 | 100.0119 | -123.1144
2070.6719 | 122.8363 | -122.3007 | 0.4303 | 1.4211e-13 | -0.0076453 | -0.013291 | -0.04517 | -0.040643 | -0.010643 | 0.0067908 | -0.016649 | 0.0095932 | 0.034923 | 0.0056709 | 0.037983 | 0.019361 | 0.028878 | 0.009904 | 0.11622 | 0.08278 | 0.27475 | 0.051416 | -121.7606 | -22.4262 | -121.905 | 0.33175 | 0.4853 | 0.30078 | -122.675 | 122.3521 | -0.31407 | 122.3201 | 122.3106 | -0.041512 | -0.34752 | -0.15555 | -0.37426 | -0.098551 | 0.54014 | 0.39574 | 0.77 | 0.055005 | -0.12952 | 122.4169 | 122.3835 | 122.5755 | 122.3296 | -0.37888 | 122.6325 | 122.786 | 122.6015 | 99.8746 | -123.1053
2072.4531 | 122.905 | -122.2733 | 0.3891 | 1.4211e-13 | -0.0076453 | -0.013291 | -0.045384 | -0.040643 | -0.010856 | 0.0067908 | -0.016222 | 0.0093796 | 0.034923 | 0.0058847 | 0.03777 | 0.019361 | 0.019721 | 0.014482 | 0.11165 | 0.069043 | 0.27475 | 0.078889 | -121.8018 | -22.6688 | -121.937 | 0.29054 | 0.43952 | 0.255 | -122.7116 | 122.3521 | -0.27745 | 122.2926 | 122.2877 | -0.064407 | -0.32006 | -0.11435 | -0.43836 | -0.098559 | 0.47146 | 0.33622 | 0.77458 | 0.050418 | -0.1341 | 122.3849 | 122.3423 | 122.548 | 122.293 | -0.31021 | 122.5638 | 122.7128 | 122.5282 | 99.6044 | -123.1007
2074.1719 | 122.7722 | -122.3328 | 0.41199 | 1.4211e-13 | -0.0078589 | -0.013077 | -0.045384 | -0.040643 | -0.010856 | 0.0067908 | -0.016435 | 0.0093796 | 0.034923 | 0.0058847 | 0.037556 | 0.014783 | 0.033457 | 0.014482 | 0.11165 | 0.078201 | 0.27932 | 0.088047 | -121.7972 | -22.8566 | -121.9325 | 0.29512 | 0.45783 | 0.27789 | -122.7025 | 122.4208 | -0.30034 | 122.3475 | 122.3472 | -0.073565 | -0.33379 | -0.13266 | -0.36969 | -0.11687 | 0.53555 | 0.40031 | 0.77 | 0.045844 | -0.1341 | 122.4444 | 122.411 | 122.6121 | 122.3662 | -0.32394 | 122.6279 | 122.7906 | 122.6107 | 99.4762 | -123.1144
2075.9688 | 122.905 | -122.2687 | 0.42572 | 1.4211e-13 | -0.0078589 | -0.013077 | -0.04517 | -0.040857 | -0.011284 | -0.00083919 | -0.016222 | 0.009807 | 0.034709 | 0.0063119 | 0.03777 | 0.019361 | 0.028878 | 0.000747 | 0.10707 | 0.073622 | 0.2839 | 0.07431 | -121.7743 | -22.9893 | -121.9096 | 0.31343 | 0.46699 | 0.2962 | -122.6841 | 122.343 | -0.31865 | 122.288 | 122.2694 | -0.073563 | -0.3521 | -0.14182 | -0.41546 | -0.11229 | 0.49436 | 0.35912 | 0.77458 | 0.041268 | -0.12952 | 122.3757 | 122.3423 | 122.5526 | 122.2976 | -0.35141 | 122.5821 | 122.7357 | 122.5649 | 99.2793 | -123.1099
2077.75 | 122.8867 | -122.287 | 0.42114 | 1.4211e-13 | -0.0072179 | -0.013505 | -0.04517 | -0.040429 | -0.011284 | -0.00083919 | -0.016008 | 0.0095932 | 0.034709 | 0.0060983 | 0.038197 | 0.019361 | 0.0243 | 0.009904 | 0.11165 | 0.078201 | 0.27932 | 0.083468 | -121.7743 | -23.2183 | -121.905 | 0.31801 | 0.47614 | 0.34199 | -122.6933 | 122.3705 | -0.3095 | 122.3063 | 122.2969 | -0.073564 | -0.34294 | -0.14182 | -0.40631 | -0.10313 | 0.51267 | 0.38201 | 0.78832 | 0.055002 | -0.079154 | 122.3986 | 122.3652 | 122.5663 | 122.3113 | -0.33768 | 122.605 | 122.7631 | 122.629 | 99.0687 | -123.1144
2079.5156 | 122.8683 | -122.2824 | 0.41657 | 1.4211e-13 | -0.0076453 | -0.013291 | -0.045598 | -0.040643 | -0.011284 | -0.0084697 | -0.016222 | 0.009807 | 0.034923 | 0.0060983 | 0.038197 | 0.019361 | 0.028878 | 0.014482 | 0.10249 | 0.073622 | 0.27475 | 0.078889 | -121.7789 | -23.3648 | -121.9141 | 0.32717 | 0.47157 | 0.30536 | -122.6887 | 122.3613 | -0.31407 | 122.3018 | 122.2969 | -0.064407 | -0.34294 | -0.14182 | -0.40631 | -0.089397 | 0.50351 | 0.36827 | 0.77458 | 0.055002 | -0.1112 | 122.3849 | 122.356 | 122.5572 | 122.3113 | -0.33768 | 122.6096 | 122.754 | 122.5878 | 98.9176 | -123.1053
2081.3125 | 122.7722 | -122.319 | 0.44403 | 1.4211e-13 | -0.0076453 | -0.012863 | -0.045384 | -0.040429 | -0.011284 | 0.014421 | -0.016435 | 0.0095932 | 0.034923 | 0.0063119 | 0.03777 | 0.014783 | 0.028878 | 0.009904 | 0.10707 | 0.078201 | 0.27932 | 0.07431 | -121.7743 | -23.5754 | -121.9096 | 0.30885 | 0.46241 | 0.30078 | -122.6979 | 122.3933 | -0.33696 | 122.3338 | 122.3289 | -0.064406 | -0.36583 | -0.16471 | -0.37884 | -0.13518 | 0.54471 | 0.40948 | 0.78832 | 0.018379 | -0.14325 | 122.4261 | 122.3972 | 122.5984 | 122.3479 | -0.36972 | 122.6279 | 122.7814 | 122.6198 | 98.7436 | -123.1419
2083.0938 | 122.8226 | -122.3145 | 0.43488 | 1.4211e-13 | -0.0080727 | -0.013077 | -0.045384 | -0.040643 | -0.010856 | -0.00083919 | -0.016222 | 0.0095932 | 0.035136 | 0.0063119 | 0.038197 | 0.010204 | 0.015142 | 0.014482 | 0.10707 | 0.069043 | 0.27475 | 0.078889 | -121.7881 | -23.7723 | -121.9141 | 0.31343 | 0.46699 | 0.25957 | -122.6979 | 122.3933 | -0.32781 | 122.3247 | 122.3289 | -0.064407 | -0.36583 | -0.16013 | -0.38342 | -0.12144 | 0.5264 | 0.40032 | 0.78374 | 0.032113 | -0.1753 | 122.4215 | 122.3835 | 122.5892 | 122.3296 | -0.35599 | 122.6279 | 122.7814 | 122.574 | 98.5421 | -123.1328
2084.8125 | 122.8363 | -122.4792 | 0.27924 | 1.4211e-13 | -0.0074317 | -0.013505 | -0.045384 | -0.040643 | -0.01107 | -0.00083919 | -0.016222 | 0.0093796 | 0.034496 | 0.0058847 | 0.037983 | 0.014783 | 0.019721 | 0.009904 | 0.11165 | 0.078201 | 0.2839 | 0.11094 | -121.9529 | -24.0012 | -122.0744 | 0.14861 | 0.29758 | 0.14969 | -122.8673 | 122.5902 | -0.16759 | 122.494 | 122.4892 | -0.10104 | -0.20103 | 0.004667 | -0.38804 | -0.13063 | 0.52636 | 0.40486 | 0.7929 | 0.018344 | -0.12955 | 122.5909 | 122.5574 | 122.7632 | 122.499 | -0.16829 | 122.6279 | 122.7768 | 122.6289 | 98.478 | -123.1465
2086.5938 | 122.8958 | -122.4655 | 0.2243 | 1.4211e-13 | -0.0078589 | -0.013077 | -0.04517 | -0.040857 | -0.010856 | -0.00083919 | -0.016222 | 0.009166 | 0.034496 | 0.0060983 | 0.03777 | 0.010204 | 0.019721 | 0.005325 | 0.11165 | 0.078201 | 0.27475 | 0.10636 | -121.9346 | -24.189 | -122.0744 | 0.14861 | 0.30674 | 0.1909 | -122.8673 | 122.5719 | -0.11266 | 122.4757 | 122.4708 | -0.10104 | -0.1461 | 0.050441 | -0.40178 | -0.075697 | 0.53094 | 0.39113 | 0.7929 | 0.082433 | -0.033409 | 122.5772 | 122.5437 | 122.7403 | 122.4852 | -0.11794 | 122.6141 | 122.7723 | 122.6564 | 98.2766 | -123.0916
2088.375 | 122.8271 | -122.3145 | 0.41657 | 1.4211e-13 | -0.0078589 | -0.012863 | -0.04517 | -0.040643 | -0.010856 | -0.023731 | -0.016435 | 0.0093796 | 0.034923 | 0.0060983 | 0.03777 | 0.023939 | 0.015142 | 0.009904 | 0.11622 | 0.073622 | 0.27017 | 0.07431 | -121.8201 | -24.2714 | -121.9553 | 0.27223 | 0.43036 | 0.28704 | -122.7528 | 122.3888 | -0.30034 | 122.3384 | 122.3244 | -0.064406 | -0.34294 | -0.1464 | -0.43837 | -0.14434 | 0.49435 | 0.35911 | 0.79748 | 0.013794 | -0.12952 | 122.4307 | 122.3881 | 122.5846 | 122.3296 | -0.34226 | 122.5867 | 122.7448 | 122.6015 | 98.0431 | -123.1694
2090.1719 | 122.7631 | -122.3419 | 0.4303 | 1.4211e-13 | -0.0072179 | -0.013077 | -0.045598 | -0.040857 | -0.011497 | -0.00083919 | -0.016222 | 0.0093796 | 0.034709 | 0.0060983 | 0.037983 | 0.019361 | 0.019721 | 0.009904 | 0.11165 | 0.073622 | 0.27475 | 0.069732 | -121.7789 | -24.4454 | -121.9141 | 0.30428 | 0.47614 | 0.35115 | -122.707 | 122.4117 | -0.31865 | 122.3613 | 122.3518 | -0.059828 | -0.35668 | -0.15555 | -0.36511 | -0.12602 | 0.56302 | 0.42778 | 0.7929 | 0.045847 | -0.079152 | 122.4536 | 122.4155 | 122.6167 | 122.3616 | -0.36057 | 122.6462 | 122.8181 | 122.6931 | 97.8965 | -123.1373
2091.9062 | 122.8271 | -122.438 | 0.32959 | 1.4211e-13 | -0.0076453 | -0.013077 | -0.045384 | -0.040857 | -0.011284 | -0.00083919 | -0.016649 | 0.0093796 | 0.034709 | 0.0060983 | 0.038411 | 0.014783 | 0.0243 | 0.005325 | 0.10707 | 0.073622 | 0.2839 | 0.069732 | -121.8751 | -24.7338 | -122.0057 | 0.19439 | 0.36168 | 0.2321 | -122.8078 | 122.5078 | -0.22252 | 122.4528 | 122.4434 | -0.064407 | -0.25597 | -0.045687 | -0.36972 | -0.1352 | 0.563 | 0.43234 | 0.80206 | 0.03209 | -0.097488 | 122.5451 | 122.5117 | 122.722 | 122.4623 | -0.25986 | 122.6324 | 122.7997 | 122.6702 | 97.7042 | -123.1374
2093.6875 | 122.9141 | -122.2961 | 0.3891 | 1.4211e-13 | -0.0076453 | -0.013077 | -0.045384 | -0.040216 | -0.010856 | 0.0067908 | -0.016435 | 0.009166 | 0.034709 | 0.0060983 | 0.037983 | 0.019361 | 0.0243 | 0.014482 | 0.11165 | 0.073622 | 0.27932 | 0.07431 | -121.7789 | -24.8529 | -121.9141 | 0.29512 | 0.46241 | 0.2962 | -122.7253 | 122.3705 | -0.27745 | 122.3155 | 122.3106 | -0.059828 | -0.31548 | -0.10977 | -0.42921 | -0.09398 | 0.51725 | 0.38201 | 0.81121 | 0.073311 | -0.092896 | 122.4078 | 122.3698 | 122.5755 | 122.3204 | -0.31479 | 122.5913 | 122.7586 | 122.5923 | 97.4433 | -123.1144
2095.4688 | 122.9004 | -122.2961 | 0.3891 | 1.4211e-13 | -0.0076453 | -0.013291 | -0.044957 | -0.040643 | -0.011497 | 0.0067908 | -0.016222 | 0.0093796 | 0.034709 | 0.0063119 | 0.038411 | 0.019361 | 0.0243 | 0.014482 | 0.11622 | 0.078201 | 0.27475 | 0.083468 | -121.7835 | -25.0772 | -121.9096 | 0.29512 | 0.44867 | 0.28704 | -122.7208 | 122.3796 | -0.27287 | 122.3155 | 122.3106 | -0.068986 | -0.3109 | -0.11435 | -0.42463 | -0.09398 | 0.51267 | 0.38659 | 0.81121 | 0.059575 | -0.10205 | 122.4124 | 122.3743 | 122.5709 | 122.3204 | -0.30563 | 122.5913 | 122.7448 | 122.5832 | 97.2189 | -123.1099
2097.25 | 122.8638 | -122.3465 | 0.40283 | 1.4211e-13 | -0.0078589 | -0.013505 | -0.045598 | -0.040857 | -0.011497 | -0.0161 | -0.016435 | 0.009166 | 0.034923 | 0.0063119 | 0.037983 | 0.019361 | 0.010564 | 0.01906 | 0.10707 | 0.073622 | 0.27475 | 0.088047 | -121.7881 | -25.2054 | -121.9233 | 0.29512 | 0.44867 | 0.25042 | -122.7208 | 122.4345 | -0.29576 | 122.3659 | 122.3656 | -0.068987 | -0.32921 | -0.12809 | -0.37427 | -0.10771 | 0.55844 | 0.4232 | 0.79748 | 0.045842 | -0.15242 | 122.4536 | 122.4201 | 122.6212 | 122.3571 | -0.31479 | 122.6416 | 122.7952 | 122.5969 | 97.1411 | -123.1236
2098.9844 | 122.7814 | -122.3923 | 0.39368 | 1.4211e-13 | -0.0080727 | -0.013505 | -0.04517 | -0.040643 | -0.01107 | -0.00083919 | -0.016863 | 0.0095932 | 0.034923 | 0.0065257 | 0.037983 | 0.014783 | 0.019721 | 0.005325 | 0.11622 | 0.073622 | 0.27475 | 0.055995 | -121.8201 | -25.3977 | -121.9599 | 0.26307 | 0.41662 | 0.23668 | -122.762 | 122.4483 | -0.27745 | 122.4071 | 122.3976 | -0.05067 | -0.32005 | -0.11893 | -0.36971 | -0.13061 | 0.57217 | 0.43235 | 0.80206 | 0.022947 | -0.157 | 122.5085 | 122.4659 | 122.667 | 122.412 | -0.33768 | 122.6553 | 122.8089 | 122.629 | 96.9945 | -123.1557
2100.7812 | 122.7951 | -122.4655 | 0.32044 | 1.4211e-13 | -0.0080727 | -0.013077 | -0.04517 | -0.040643 | -0.011497 | -0.0161 | -0.016222 | 0.0093796 | 0.035136 | 0.0063119 | 0.037983 | 0.019361 | 0.019721 | 0.009904 | 0.11165 | 0.069043 | 0.27932 | 0.10178 | -121.8934 | -25.6862 | -122.024 | 0.18981 | 0.33879 | 0.18174 | -122.8398 | 122.5673 | -0.20879 | 122.4849 | 122.4754 | -0.09188 | -0.25139 | -0.041111 | -0.3743 | -0.13062 | 0.57215 | 0.44149 | 0.8158 | 0.018352 | -0.1387 | 122.5772 | 122.5346 | 122.7448 | 122.4852 | -0.21865 | 122.6553 | 122.8043 | 122.6473 | 96.7793 | -123.1603
2102.5625 | 122.818 | -122.5113 | 0.27466 | 1.4211e-13 | -0.0082863 | -0.013291 | -0.045598 | -0.040643 | -0.011284 | 0.0067908 | -0.016435 | 0.0095932 | 0.034709 | 0.0063119 | 0.037983 | 0.019361 | 0.019721 | 0.005325 | 0.10707 | 0.073622 | 0.27932 | 0.088047 | -121.9483 | -25.8922 | -122.0881 | 0.12114 | 0.28384 | 0.13595 | -122.8948 | 122.5993 | -0.16759 | 122.5307 | 122.5166 | -0.082722 | -0.20104 | 0.004666 | -0.38347 | -0.15352 | 0.56298 | 0.42317 | 0.80664 | 0.009186 | -0.13871 | 122.6184 | 122.5849 | 122.7906 | 122.531 | -0.18661 | 122.6324 | 122.7951 | 122.6472 | 96.619 | -123.1694
2104.2812 | 122.9233 | -122.4289 | 0.27924 | 1.4211e-13 | -0.0074317 | -0.013291 | -0.045384 | -0.040643 | -0.010856 | -0.00083919 | -0.016435 | 0.0095932 | 0.034923 | 0.0065257 | 0.03777 | 0.014783 | 0.0243 | 0.01906 | 0.10707 | 0.08278 | 0.27017 | 0.097205 | -121.9117 | -26.0067 | -122.0423 | 0.1715 | 0.31132 | 0.17716 | -122.8627 | 122.5261 | -0.17217 | 122.4437 | 122.448 | -0.078145 | -0.19646 | -0.009069 | -0.43382 | -0.10774 | 0.51721 | 0.38656 | 0.82037 | 0.03208 | -0.10208 | 122.536 | 122.5117 | 122.6991 | 122.4532 | -0.18203 | 122.6004 | 122.7402 | 122.6061 | 96.4222 | -123.1419
2106.0781 | 122.8592 | -122.3969 | 0.32501 | 1.4211e-13 | -0.0078589 | -0.013077 | -0.045598 | -0.040643 | -0.01107 | -0.0084697 | -0.016222 | 0.0093796 | 0.035136 | 0.0060983 | 0.037983 | 0.010204 | 0.019721 | 0.014482 | 0.11165 | 0.078201 | 0.27475 | 0.060574 | -121.8705 | -26.1487 | -122.0011 | 0.20813 | 0.36626 | 0.21837 | -122.8215 | 122.4574 | -0.21337 | 122.4071 | 122.4113 | -0.046092 | -0.24681 | -0.050267 | -0.42465 | -0.11689 | 0.52638 | 0.39572 | 0.82037 | 0.041247 | -0.10665 | 122.5085 | 122.4751 | 122.6716 | 122.4166 | -0.26444 | 122.605 | 122.7631 | 122.6152 | 96.2482 | -123.1465
2107.8594 | 122.7859 | -122.5571 | 0.25177 | 1.4211e-13 | -0.0080727 | -0.013291 | -0.045384 | -0.040429 | -0.01107 | 0.0067908 | -0.016008 | 0.0093796 | 0.034923 | 0.0060983 | 0.038197 | 0.010204 | 0.019721 | 0.009904 | 0.11165 | 0.073622 | 0.27932 | 0.088047 | -121.9254 | -26.4646 | -122.0652 | 0.14403 | 0.293 | 0.15427 | -122.8856 | 122.6451 | -0.14012 | 122.5673 | 122.567 | -0.078143 | -0.17815 | 0.027554 | -0.32854 | -0.10774 | 0.63165 | 0.49183 | 0.82037 | 0.041231 | -0.097504 | 122.6687 | 122.6307 | 122.8364 | 122.5768 | -0.16372 | 122.7011 | 122.8501 | 122.7113 | 96.0925 | -123.1374
2109.6406 | 122.8638 | -122.3969 | 0.3479 | 1.4211e-13 | -0.0080727 | -0.013077 | -0.045384 | -0.040643 | -0.01107 | -0.00083919 | -0.016222 | 0.0093796 | 0.034923 | 0.0065257 | 0.038411 | 0.019361 | 0.0243 | 0.005325 | 0.11165 | 0.073622 | 0.27932 | 0.051416 | -121.8338 | -26.5745 | -121.9782 | 0.22186 | 0.38457 | 0.25957 | -122.8032 | 122.4483 | -0.23625 | 122.4162 | 122.4022 | -0.046091 | -0.27428 | -0.068576 | -0.40634 | -0.12604 | 0.56301 | 0.41861 | 0.82495 | 0.036673 | -0.088326 | 122.5085 | 122.4705 | 122.6762 | 122.4212 | -0.29648 | 122.6187 | 122.7814 | 122.6564 | 95.8224 | -123.1511
2111.4219 | 122.9141 | -122.4792 | 0.21057 | 1.4211e-13 | -0.0080727 | -0.012863 | -0.045384 | -0.040857 | -0.01107 | 0.0067908 | -0.016435 | 0.009807 | 0.034923 | 0.0065257 | 0.038197 | 0.014783 | 0.028878 | 0.009904 | 0.10707 | 0.078201 | 0.27475 | 0.11094 | -121.9437 | -26.808 | -122.079 | 0.12571 | 0.26553 | 0.12222 | -122.9177 | 122.5902 | -0.1035 | 122.494 | 122.4892 | -0.10104 | -0.13237 | 0.064174 | -0.43841 | -0.084857 | 0.53552 | 0.40028 | 0.83869 | 0.054959 | -0.088355 | 122.5863 | 122.5574 | 122.754 | 122.5081 | -0.099629 | 122.605 | 122.7448 | 122.6015 | 95.6713 | -123.1282
2113.2031 | 122.9187 | -122.3923 | 0.28839 | 1.4211e-13 | -0.0082863 | -0.013505 | -0.04517 | -0.040857 | -0.01107 | -0.00083919 | -0.016435 | 0.0095932 | 0.035136 | 0.0063119 | 0.037983 | 0.014783 | 0.0243 | 0.009904 | 0.11165 | 0.069043 | 0.27475 | 0.07431 | -121.8522 | -26.9362 | -121.9966 | 0.20813 | 0.3571 | 0.20463 | -122.8215 | 122.4666 | -0.17674 | 122.4071 | 122.4022 | -0.064406 | -0.21935 | -0.013646 | -0.42923 | -0.080264 | 0.54012 | 0.39572 | 0.82495 | 0.068711 | -0.08376 | 122.5039 | 122.4613 | 122.667 | 122.4166 | -0.21408 | 122.6004 | 122.7494 | 122.5969 | 95.4561 | -123.1099
2114.9844 | 122.7722 | -122.5204 | 0.25177 | 1.4211e-13 | -0.0078589 | -0.013077 | -0.044957 | -0.040857 | -0.011497 | -0.0084697 | -0.016222 | 0.0095932 | 0.035136 | 0.0063119 | 0.037556 | 0.010204 | 0.019721 | 0.005325 | 0.10249 | 0.073622 | 0.27475 | 0.088047 | -121.9392 | -27.1422 | -122.079 | 0.11656 | 0.27469 | 0.12679 | -122.9131 | 122.6085 | -0.14928 | 122.5307 | 122.5258 | -0.082722 | -0.17815 | 0.022975 | -0.39263 | -0.13521 | 0.58129 | 0.44148 | 0.83411 | 0.022917 | -0.12498 | 122.6229 | 122.5941 | 122.7952 | 122.5402 | -0.16372 | 122.637 | 122.7951 | 122.6472 | 95.3782 | -123.1648
2116.7656 | 122.9141 | -122.4884 | 0.23804 | 1.4211e-13 | -0.0078589 | -0.013077 | -0.045598 | -0.040429 | -0.010856 | -0.00083919 | -0.016649 | 0.0093796 | 0.034923 | 0.0065257 | 0.038197 | 0.014783 | 0.019721 | 0.005325 | 0.097912 | 0.069043 | 0.27932 | 0.092626 | -121.9117 | -27.4261 | -122.0561 | 0.14403 | 0.293 | 0.15427 | -122.8948 | 122.581 | -0.14012 | 122.5032 | 122.4937 | -0.087301 | -0.16899 | 0.041287 | -0.40636 | -0.094009 | 0.57672 | 0.43233 | 0.83869 | 0.054964 | -0.083771 | 122.5863 | 122.5574 | 122.7677 | 122.5081 | -0.14541 | 122.6324 | 122.7814 | 122.6427 | 95.0623 | -123.1328
2118.5469 | 122.85 | -122.4838 | 0.23346 | 1.4211e-13 | -0.0084999 | -0.013505 | -0.045384 | -0.040643 | -0.011497 | -0.00083919 | -0.016649 | 0.009166 | 0.034923 | 0.0067393 | 0.037983 | 0.014783 | 0.028878 | 0.000747 | 0.11622 | 0.073622 | 0.27932 | 0.092626 | -121.9163 | -27.4582 | -122.0561 | 0.14861 | 0.30216 | 0.15427 | -122.8902 | 122.5765 | -0.11723 | 122.4986 | 122.4846 | -0.091879 | -0.15984 | 0.045865 | -0.40636 | -0.084852 | 0.56757 | 0.42775 | 0.83411 | 0.068699 | -0.079193 | 122.6001 | 122.5574 | 122.7631 | 122.5127 | -0.14083 | 122.6324 | 122.786 | 122.6381 | 95.0257 | -123.1236
2120.2656 | 122.8683 | -122.4792 | 0.22888 | 1.4211e-13 | -0.0080727 | -0.013291 | -0.045384 | -0.04107 | -0.01107 | -0.00083919 | -0.016649 | 0.0093796 | 0.035136 | 0.0067393 | 0.037983 | 0.019361 | 0.019721 | 0.014482 | 0.10707 | 0.078201 | 0.27932 | 0.07431 | -121.9208 | -27.6779 | -122.0652 | 0.13487 | 0.293 | 0.14053 | -122.9085 | 122.5536 | -0.12181 | 122.4986 | 122.4937 | -0.059828 | -0.15068 | 0.050442 | -0.42925 | -0.094011 | 0.55841 | 0.41401 | 0.84327 | 0.064119 | -0.088352 | 122.5863 | 122.5574 | 122.7586 | 122.499 | -0.15457 | 122.6141 | 122.7722 | 122.6198 | 94.8013 | -123.1374
2122.0469 | 122.9095 | -122.4106 | 0.27008 | 1.4211e-13 | -0.0080727 | -0.013505 | -0.045598 | -0.040857 | -0.01107 | -0.0161 | -0.016222 | 0.0093796 | 0.034923 | 0.0065257 | 0.038197 | 0.019361 | 0.019721 | 0.014482 | 0.10707 | 0.073622 | 0.27475 | 0.060574 | -121.8842 | -27.8061 | -122.0194 | 0.1715 | 0.32963 | 0.20921 | -122.8581 | 122.4712 | -0.16301 | 122.4299 | 122.4251 | -0.046092 | -0.19646 | 0.004664 | -0.44755 | -0.098582 | 0.52637 | 0.39114 | 0.83869 | 0.059549 | -0.060872 | 122.5177 | 122.4842 | 122.6853 | 122.4303 | -0.20951 | 122.5821 | 122.7402 | 122.6198 | 94.6044 | -123.1282
2123.8281 | 122.7722 | -122.4289 | 0.37079 | 1.4211e-13 | -0.0082863 | -0.013291 | -0.045598 | -0.040857 | -0.010856 | -0.0084697 | -0.016435 | 0.009166 | 0.034923 | 0.0063119 | 0.03777 | 0.014783 | 0.028878 | 0.014482 | 0.11622 | 0.078201 | 0.27932 | 0.060574 | -121.8155 | -27.9801 | -121.9553 | 0.22644 | 0.37542 | 0.22752 | -122.8078 | 122.4895 | -0.25456 | 122.4437 | 122.4434 | -0.046092 | -0.29259 | -0.091465 | -0.37887 | -0.14435 | 0.61337 | 0.47355 | 0.85242 | 0.004627 | -0.14326 | 122.5451 | 122.5071 | 122.7082 | 122.4578 | -0.31021 | 122.6553 | 122.8043 | 122.6564 | 94.4488 | -123.1786
2125.5625 | 122.8226 | -122.3831 | 0.37994 | 1.4211e-13 | -0.0080727 | -0.013505 | -0.045598 | -0.04107 | -0.01107 | -0.0084697 | -0.016435 | 0.0093796 | 0.034709 | 0.0063119 | 0.038197 | 0.014783 | 0.019721 | 0.014482 | 0.10707 | 0.069043 | 0.27475 | 0.083468 | -121.7835 | -28.1816 | -121.9279 | 0.26765 | 0.4212 | 0.27331 | -122.7711 | 122.4666 | -0.27288 | 122.3979 | 122.3976 | -0.068986 | -0.3109 | -0.1052 | -0.38802 | -0.1123 | 0.59964 | 0.45525 | 0.84327 | 0.041258 | -0.10663 | 122.4902 | 122.4522 | 122.6579 | 122.4028 | -0.29648 | 122.6508 | 122.8043 | 122.6564 | 94.2015 | -123.1511
2127.3281 | 122.8409 | -122.3694 | 0.39368 | 1.4211e-13 | -0.0084999 | -0.013077 | -0.045384 | -0.040857 | -0.011284 | -0.00083919 | -0.016435 | 0.0095932 | 0.035136 | 0.0067393 | 0.037983 | 0.014783 | 0.019721 | 0.014482 | 0.11622 | 0.073622 | 0.27475 | 0.046837 | -121.7835 | -28.3327 | -121.9279 | 0.28138 | 0.42578 | 0.2962 | -122.7666 | 122.4162 | -0.27745 | 122.3842 | 122.3839 | -0.032355 | -0.32005 | -0.11893 | -0.39717 | -0.11229 | 0.58591 | 0.44151 | 0.83869 | 0.032104 | -0.097474 | 122.4856 | 122.443 | 122.6441 | 122.3891 | -0.34684 | 122.6508 | 122.7952 | 122.6656 | 94.0367 | -123.1602
2129.1094 | 122.9416 | -122.3373 | 0.36163 | 1.4211e-13 | -0.0082863 | -0.013291 | -0.04517 | -0.040643 | -0.011284 | -0.0084697 | -0.016435 | 0.0093796 | 0.034923 | 0.0067393 | 0.038197 | 0.019361 | 0.0243 | 0.014482 | 0.11165 | 0.078201 | 0.27932 | 0.042258 | -121.7789 | -28.6395 | -121.9233 | 0.26765 | 0.43494 | 0.28704 | -122.7711 | 122.3796 | -0.24999 | 122.3567 | 122.3518 | -0.027776 | -0.28343 | -0.082309 | -0.4338 | -0.093985 | 0.55844 | 0.41405 | 0.84784 | 0.073305 | -0.074588 | 122.449 | 122.4155 | 122.6167 | 122.3616 | -0.31938 | 122.605 | 122.7723 | 122.6244 | 93.6979 | -123.1328
2130.8906 | 122.8043 | -122.4655 | 0.3067 | 1.4211e-13 | -0.0084999 | -0.013077 | -0.045598 | -0.040857 | -0.01107 | -0.00083919 | -0.016435 | 0.009166 | 0.034709 | 0.0065257 | 0.03777 | 0.010204 | 0.028878 | 0.005325 | 0.11165 | 0.073622 | 0.27475 | 0.07431 | -121.8476 | -28.7356 | -121.992 | 0.20355 | 0.34794 | 0.18632 | -122.8444 | 122.5398 | -0.19505 | 122.4757 | 122.4708 | -0.068985 | -0.23308 | -0.031957 | -0.37888 | -0.10315 | 0.61794 | 0.47354 | 0.85242 | 0.041242 | -0.12039 | 122.5772 | 122.5391 | 122.7403 | 122.4944 | -0.23239 | 122.6691 | 122.8135 | 122.6518 | 93.7299 | -123.1511
2132.6094 | 122.8317 | -122.3831 | 0.39368 | 1.4211e-13 | -0.0087137 | -0.013077 | -0.045384 | -0.040857 | -0.011284 | -0.0084697 | -0.016222 | 0.0093796 | 0.034923 | 0.0065257 | 0.038411 | 0.010204 | 0.015142 | 0.005325 | 0.10707 | 0.069043 | 0.27017 | 0.083468 | -121.7789 | -28.9142 | -121.9279 | 0.26765 | 0.41204 | 0.26873 | -122.7895 | 122.4666 | -0.28661 | 122.3933 | 122.3884 | -0.078143 | -0.32463 | -0.12351 | -0.40633 | -0.12603 | 0.60422 | 0.45525 | 0.86158 | 0.018368 | -0.12495 | 122.4902 | 122.4522 | 122.6533 | 122.3983 | -0.31021 | 122.6508 | 122.7952 | 122.6518 | 93.4689 | -123.1831
2134.375 | 122.7997 | -122.4014 | 0.40283 | 1.4211e-13 | -0.0082863 | -0.013505 | -0.04517 | -0.04107 | -0.01107 | -0.0161 | -0.016435 | 0.0093796 | 0.034923 | 0.0069529 | 0.03777 | 0.019361 | 0.015142 | 0.009904 | 0.10249 | 0.078201 | 0.27475 | 0.065153 | -121.7789 | -29.1798 | -121.9141 | 0.26307 | 0.4212 | 0.2321 | -122.7895 | 122.4666 | -0.30034 | 122.4208 | 122.4113 | -0.055249 | -0.32463 | -0.12809 | -0.38802 | -0.13976 | 0.62253 | 0.48729 | 0.87532 | 0.01837 | -0.17073 | 122.5039 | 122.4796 | 122.6762 | 122.4166 | -0.33768 | 122.6645 | 122.8226 | 122.6335 | 93.2217 | -123.1923
2136.0938 | 122.937 | -122.3465 | 0.3479 | 1.4211e-13 | -0.0087137 | -0.013291 | -0.045384 | -0.040643 | -0.011497 | -0.0084697 | -0.016222 | 0.0095932 | 0.034923 | 0.0067393 | 0.038197 | 0.023939 | 0.015142 | 0.014482 | 0.10249 | 0.073622 | 0.26559 | 0.046837 | -121.7789 | -29.395 | -121.9279 | 0.26307 | 0.41204 | 0.25042 | -122.794 | 122.3933 | -0.24541 | 122.3704 | 122.361 | -0.032355 | -0.27428 | -0.082312 | -0.44753 | -0.084831 | 0.5676 | 0.41863 | 0.86616 | 0.064145 | -0.097483 | 122.449 | 122.4201 | 122.6121 | 122.3616 | -0.30106 | 122.6096 | 122.7585 | 122.5969 | 92.9515 | -123.1419
2137.875 | 122.85 | -122.406 | 0.37079 | 1.4211e-13 | -0.0087137 | -0.013077 | -0.045384 | -0.040857 | -0.01107 | -0.0161 | -0.016222 | 0.0093796 | 0.035136 | 0.0065257 | 0.037983 | 0.019361 | 0.019721 | 0.000747 | 0.10707 | 0.069043 | 0.27475 | 0.069732 | -121.7789 | -29.4591 | -121.937 | 0.24933 | 0.41204 | 0.24126 | -122.7895 | 122.4757 | -0.26372 | 122.4254 | 122.4068 | -0.068985 | -0.30175 | -0.096044 | -0.38345 | -0.12145 | 0.62711 | 0.46898 | 0.85242 | 0.041256 | -0.12953 | 122.5131 | 122.475 | 122.6808 | 122.4257 | -0.30106 | 122.6553 | 122.8181 | 122.6473 | 92.9469 | -123.1602
2139.5938 | 122.9279 | -122.3511 | 0.35706 | 1.4211e-13 | -0.0080727 | -0.013505 | -0.045384 | -0.040643 | -0.011284 | -0.0084697 | -0.016008 | 0.010021 | 0.035136 | 0.0067393 | 0.037983 | 0.014783 | 0.019721 | 0.009904 | 0.10707 | 0.069043 | 0.27475 | 0.060574 | -121.7743 | -29.6605 | -121.9279 | 0.25849 | 0.41204 | 0.2321 | -122.794 | 122.4116 | -0.24999 | 122.3659 | 122.361 | -0.05067 | -0.28801 | -0.082311 | -0.44296 | -0.098565 | 0.57675 | 0.4232 | 0.86616 | 0.054989 | -0.12495 | 122.4581 | 122.4201 | 122.6258 | 122.3708 | -0.29648 | 122.6096 | 122.7631 | 122.5832 | 92.6906 | -123.1511
2141.375 | 122.8134 | -122.4197 | 0.3891 | 1.4211e-13 | -0.0084999 | -0.012863 | -0.045384 | -0.040643 | -0.01107 | -0.023731 | -0.016649 | 0.009807 | 0.035564 | 0.0067393 | 0.037983 | 0.005626 | 0.0243 | 0.009904 | 0.10707 | 0.069043 | 0.27475 | 0.046837 | -121.7652 | -29.9673 | -121.9187 | 0.26307 | 0.41204 | 0.28247 | -122.7895 | 122.4666 | -0.28203 | 122.4254 | 122.4296 | -0.036933 | -0.32006 | -0.11435 | -0.36971 | -0.12603 | 0.65458 | 0.50103 | 0.87074 | 0.022946 | -0.10663 | 122.5268 | 122.4888 | 122.6945 | 122.444 | -0.34226 | 122.6828 | 122.8318 | 122.7022 | 92.4524 | -123.1786
2143.1562 | 122.7951 | -122.3923 | 0.39825 | 1.4211e-13 | -0.0082863 | -0.013077 | -0.04517 | -0.040643 | -0.01107 | -0.0161 | -0.016435 | 0.009807 | 0.034709 | 0.0069529 | 0.038197 | 0.014783 | 0.019721 | 0.014482 | 0.10249 | 0.073622 | 0.27932 | 0.055995 | -121.7606 | -30.1917 | -121.9187 | 0.25849 | 0.41662 | 0.255 | -122.7986 | 122.4483 | -0.29576 | 122.4071 | 122.4068 | -0.041513 | -0.32463 | -0.11893 | -0.40634 | -0.13976 | 0.63169 | 0.47356 | 0.8799 | 0.01837 | -0.14326 | 122.4948 | 122.4659 | 122.6716 | 122.412 | -0.34226 | 122.6508 | 122.8089 | 122.6473 | 92.2006 | -123.1969
2144.8906 | 122.8043 | -122.406 | 0.39368 | 1.4211e-13 | -0.0084999 | -0.013291 | -0.04517 | -0.040857 | -0.011497 | 0.0067908 | -0.016435 | 0.009807 | 0.034709 | 0.0069529 | 0.037983 | 0.010204 | 0.019721 | 0.014482 | 0.10249 | 0.073622 | 0.27475 | 0.069732 | -121.7697 | -30.3656 | -121.9141 | 0.25391 | 0.40747 | 0.26415 | -122.7986 | 122.4757 | -0.29119 | 122.4162 | 122.4205 | -0.05525 | -0.32005 | -0.11893 | -0.3926 | -0.13976 | 0.63627 | 0.49187 | 0.88447 | 0.013789 | -0.12953 | 122.5085 | 122.4796 | 122.6808 | 122.4257 | -0.32394 | 122.6599 | 122.8135 | 122.6702 | 92.0404 | -123.1923
2146.6719 | 122.9416 | -122.3877 | 0.34332 | 1.4211e-13 | -0.0084999 | -0.013077 | -0.04517 | -0.040857 | -0.011284 | -0.0084697 | -0.016649 | 0.0093796 | 0.034496 | 0.0067393 | 0.037983 | 0.014783 | 0.0243 | 0.009904 | 0.11165 | 0.073622 | 0.26559 | 0.051416 | -121.7652 | -30.5625 | -121.9187 | 0.25849 | 0.41204 | 0.28247 | -122.794 | 122.4391 | -0.23168 | 122.4025 | 122.3976 | -0.041512 | -0.2697 | -0.077735 | -0.40634 | -0.084832 | 0.62253 | 0.46898 | 0.87532 | 0.068722 | -0.060856 | 122.4993 | 122.4613 | 122.6533 | 122.412 | -0.29191 | 122.6462 | 122.7997 | 122.6702 | 91.8252 | -123.1374
2148.4531 | 122.8455 | -122.4243 | 0.37537 | 1.4211e-13 | -0.0089273 | -0.013505 | -0.045384 | -0.040643 | -0.011284 | -0.0084697 | -0.016222 | 0.0093796 | 0.034282 | 0.0067393 | 0.038411 | 0.019361 | 0.0243 | 0.009904 | 0.11165 | 0.073622 | 0.27475 | 0.055995 | -121.7652 | -30.8373 | -121.9187 | 0.24933 | 0.40747 | 0.27789 | -122.8032 | 122.4803 | -0.26372 | 122.4437 | 122.4342 | -0.046091 | -0.30174 | -0.10062 | -0.37887 | -0.12603 | 0.65915 | 0.5056 | 0.88448 | 0.0321 | -0.097478 | 122.536 | 122.4979 | 122.6991 | 122.4486 | -0.31937 | 122.6737 | 122.8318 | 122.7022 | 91.5871 | -123.1786
2150.2656 | 122.8409 | -122.4106 | 0.36621 | 1.4211e-13 | -0.0084999 | -0.012863 | -0.04517 | -0.040857 | -0.01107 | -0.00083919 | -0.016222 | 0.0095932 | 0.034923 | 0.0065257 | 0.037983 | 0.014783 | 0.015142 | 0.009904 | 0.10707 | 0.073622 | 0.27475 | 0.060574 | -121.7652 | -31.025 | -121.9141 | 0.25391 | 0.40747 | 0.255 | -122.7986 | 122.4712 | -0.25914 | 122.4254 | 122.4205 | -0.05067 | -0.29259 | -0.091466 | -0.38803 | -0.1123 | 0.64542 | 0.49645 | 0.88447 | 0.041255 | -0.11122 | 122.5177 | 122.4842 | 122.6853 | 122.4257 | -0.30564 | 122.6645 | 122.818 | 122.6656 | 91.3856 | -123.1648
2152.0469 | 122.7859 | -122.4152 | 0.37079 | 1.4211e-13 | -0.0089273 | -0.013291 | -0.045384 | -0.040857 | -0.011284 | -0.0161 | -0.016435 | 0.010021 | 0.035136 | 0.0069529 | 0.038411 | 0.014783 | 0.015142 | 0.01906 | 0.11165 | 0.069043 | 0.27017 | 0.065153 | -121.7606 | -31.2448 | -121.9187 | 0.24476 | 0.40289 | 0.22295 | -122.8032 | 122.4803 | -0.25914 | 122.4299 | 122.4342 | -0.046093 | -0.30175 | -0.10062 | -0.38803 | -0.12603 | 0.65458 | 0.49645 | 0.88448 | 0.032099 | -0.14784 | 122.5268 | 122.4842 | 122.6853 | 122.4303 | -0.30564 | 122.6599 | 122.818 | 122.6381 | 91.1704 | -123.174
2153.8281 | 122.8134 | -122.4152 | 0.37994 | 1.4211e-13 | -0.0084999 | -0.013505 | -0.04517 | -0.040216 | -0.01107 | -0.00083919 | -0.016435 | 0.0093796 | 0.034709 | 0.0069529 | 0.038197 | 0.005626 | 0.0243 | 0.014482 | 0.10249 | 0.078201 | 0.26559 | 0.07431 | -121.756 | -31.4371 | -121.9187 | 0.25391 | 0.41204 | 0.23668 | -122.8032 | 122.4895 | -0.27745 | 122.4208 | 122.4296 | -0.059828 | -0.30174 | -0.11436 | -0.38803 | -0.12603 | 0.65916 | 0.49645 | 0.88448 | 0.032101 | -0.14326 | 122.5177 | 122.4934 | 122.6807 | 122.4395 | -0.30563 | 122.6691 | 122.8272 | 122.6518 | 90.9781 | -123.1831
2155.5469 | 122.8363 | -122.4014 | 0.37537 | 1.4211e-13 | -0.0087137 | -0.013291 | -0.045384 | -0.040857 | -0.01107 | -0.0161 | -0.016435 | 0.0095932 | 0.034709 | 0.0069529 | 0.037983 | 0.014783 | 0.015142 | 0.009904 | 0.10707 | 0.069043 | 0.27017 | 0.046837 | -121.7606 | -31.6797 | -121.9096 | 0.24933 | 0.39831 | 0.2321 | -122.8123 | 122.4483 | -0.2683 | 122.4162 | 122.4113 | -0.036933 | -0.30632 | -0.1052 | -0.41092 | -0.12603 | 0.64084 | 0.49187 | 0.90279 | 0.022943 | -0.14326 | 122.5085 | 122.4705 | 122.6716 | 122.4166 | -0.32853 | 122.6508 | 122.7997 | 122.6335 | 90.7217 | -123.1877
2157.3438 | 122.8912 | -122.406 | 0.37079 | 1.4211e-13 | -0.0089273 | -0.013291 | -0.045384 | -0.040857 | -0.011497 | -0.00083919 | -0.016435 | 0.0095932 | 0.03535 | 0.0071667 | 0.037983 | 0.014783 | 0.028878 | 0.014482 | 0.11165 | 0.078201 | 0.27017 | 0.07431 | -121.7606 | -31.9361 | -121.9141 | 0.24933 | 0.41204 | 0.21837 | -122.8123 | 122.4803 | -0.25914 | 122.4208 | 122.4205 | -0.059828 | -0.29259 | -0.10062 | -0.40634 | -0.12145 | 0.64542 | 0.49187 | 0.89821 | 0.041256 | -0.15242 | 122.5177 | 122.4842 | 122.6762 | 122.4349 | -0.29648 | 122.6553 | 122.8181 | 122.6244 | 90.4699 | -123.1831
2159.125 | 122.7905 | -122.4426 | 0.39368 | 1.4211e-13 | -0.0089273 | -0.013291 | -0.04517 | -0.04107 | -0.01107 | -0.0084697 | -0.016435 | 0.0093796 | 0.034923 | 0.0067393 | 0.038197 | 0.010204 | 0.019721 | 0.014482 | 0.11622 | 0.073622 | 0.27932 | 0.092626 | -121.7514 | -32.1559 | -121.9141 | 0.24933 | 0.40289 | 0.24584 | -122.8078 | 122.5353 | -0.27745 | 122.4528 | 122.4571 | -0.078144 | -0.32005 | -0.11435 | -0.36514 | -0.14434 | 0.6912 | 0.52849 | 0.89363 | 0.009211 | -0.14784 | 122.5589 | 122.5162 | 122.722 | 122.4623 | -0.30105 | 122.692 | 122.8455 | 122.6885 | 90.2867 | -123.2014
2160.8438 | 122.9233 | -122.3923 | 0.36621 | 1.4211e-13 | -0.0091411 | -0.013077 | -0.045384 | -0.04107 | -0.011497 | -0.0161 | -0.016649 | 0.0095932 | 0.034709 | 0.0071667 | 0.038197 | 0.014783 | 0.028878 | 0.005325 | 0.10249 | 0.078201 | 0.27017 | 0.055995 | -121.7606 | -32.3528 | -121.905 | 0.25391 | 0.39831 | 0.27789 | -122.8078 | 122.4483 | -0.26372 | 122.4071 | 122.3976 | -0.05067 | -0.28801 | -0.096044 | -0.41549 | -0.1123 | 0.63169 | 0.4873 | 0.90279 | 0.032098 | -0.088323 | 122.4948 | 122.4705 | 122.6624 | 122.4212 | -0.31022 | 122.6462 | 122.7906 | 122.6702 | 90.0395 | -123.174
2162.625 | 122.8592 | -122.3969 | 0.37079 | 1.4211e-13 | -0.0089273 | -0.013291 | -0.04517 | -0.040643 | -0.011284 | -0.00083919 | -0.016222 | 0.0095932 | 0.034923 | 0.0071667 | 0.038197 | 0.014783 | 0.019721 | 0.005325 | 0.11165 | 0.08278 | 0.27017 | 0.051416 | -121.7514 | -32.5817 | -121.9141 | 0.24476 | 0.39373 | 0.28247 | -122.8078 | 122.4483 | -0.25914 | 122.4116 | 122.4022 | -0.046091 | -0.28801 | -0.10062 | -0.41092 | -0.12603 | 0.64543 | 0.48272 | 0.89363 | 0.022942 | -0.088322 | 122.5085 | 122.4796 | 122.667 | 122.4166 | -0.31937 | 122.6416 | 122.7906 | 122.6793 | 89.8151 | -123.1786
2164.3438 | 122.85 | -122.4197 | 0.35706 | 1.4211e-13 | -0.0091411 | -0.013291 | -0.04517 | -0.041284 | -0.011284 | -0.00083919 | -0.016435 | 0.0093796 | 0.034709 | 0.0069529 | 0.037983 | 0.010204 | 0.019721 | 0.009904 | 0.11165 | 0.073622 | 0.27475 | 0.069732 | -121.7514 | -32.7374 | -121.905 | 0.24933 | 0.40289 | 0.30536 | -122.8169 | 122.4895 | -0.24541 | 122.4299 | 122.4296 | -0.059828 | -0.28343 | -0.082311 | -0.39719 | -0.10772 | 0.66831 | 0.51476 | 0.91195 | 0.045832 | -0.051696 | 122.5314 | 122.4934 | 122.6945 | 122.4395 | -0.28732 | 122.6691 | 122.8226 | 122.7251 | 89.6823 | -123.174
2166.125 | 122.818 | -122.406 | 0.37079 | 1.4211e-13 | -0.0087137 | -0.013077 | -0.04517 | -0.040857 | -0.011284 | -0.0084697 | -0.016435 | 0.0095932 | 0.034923 | 0.0069529 | 0.038411 | 0.019361 | 0.019721 | 0.009904 | 0.11165 | 0.078201 | 0.27475 | 0.065153 | -121.7514 | -33.0671 | -121.9004 | 0.24476 | 0.39831 | 0.27789 | -122.8215 | 122.4712 | -0.25914 | 122.4254 | 122.4159 | -0.055249 | -0.29259 | -0.096044 | -0.4155 | -0.12603 | 0.65458 | 0.50561 | 0.92111 | 0.02752 | -0.092901 | 122.5177 | 122.4842 | 122.6808 | 122.4257 | -0.30564 | 122.6508 | 122.8043 | 122.6839 | 89.3389 | -123.1923
2167.8438 | 122.8409 | -122.4335 | 0.37079 | 1.4211e-13 | -0.0089273 | -0.013291 | -0.045384 | -0.040643 | -0.011284 | -0.00083919 | -0.016435 | 0.009807 | 0.034923 | 0.0071667 | 0.037983 | 0.014783 | 0.019721 | 0.009904 | 0.10249 | 0.073622 | 0.27017 | 0.060574 | -121.7377 | -33.1495 | -121.8958 | 0.25849 | 0.40289 | 0.22752 | -122.8123 | 122.494 | -0.2683 | 122.4483 | 122.4434 | -0.05067 | -0.29717 | -0.10062 | -0.37887 | -0.1123 | 0.69578 | 0.53765 | 0.91653 | 0.032099 | -0.14326 | 122.536 | 122.5071 | 122.7036 | 122.4532 | -0.31021 | 122.692 | 122.8364 | 122.661 | 89.284 | -123.1831
2169.625 | 122.9462 | -122.4152 | 0.3479 | 1.4211e-13 | -0.0089273 | -0.012863 | -0.045384 | -0.040857 | -0.011284 | -0.00083919 | -0.016649 | 0.009807 | 0.03535 | 0.0069529 | 0.038197 | 0.014783 | 0.0243 | 0.009904 | 0.11165 | 0.073622 | 0.26101 | 0.065153 | -121.7377 | -33.5112 | -121.8912 | 0.25391 | 0.40289 | 0.21837 | -122.8169 | 122.4803 | -0.23625 | 122.4299 | 122.4251 | -0.055249 | -0.27428 | -0.08689 | -0.40176 | -0.093988 | 0.67747 | 0.52392 | 0.92568 | 0.054988 | -0.12953 | 122.5268 | 122.4888 | 122.6762 | 122.4395 | -0.28275 | 122.6691 | 122.818 | 122.6335 | 88.9039 | -123.1648
2171.4062 | 122.8271 | -122.4243 | 0.41199 | 1.4211e-13 | -0.0091411 | -0.013077 | -0.045384 | -0.04107 | -0.011284 | -0.00083919 | -0.016649 | 0.009807 | 0.034923 | 0.0069529 | 0.037983 | 0.014783 | 0.019721 | 0.009904 | 0.11165 | 0.073622 | 0.27932 | 0.060574 | -121.7331 | -33.6806 | -121.8958 | 0.24933 | 0.40289 | 0.21379 | -122.8169 | 122.4849 | -0.30034 | 122.4391 | 122.4342 | -0.05067 | -0.33836 | -0.13266 | -0.39261 | -0.16265 | 0.69121 | 0.5285 | 0.9211 | -0.009099 | -0.1982 | 122.536 | 122.4979 | 122.7036 | 122.444 | -0.35141 | 122.6737 | 122.8272 | 122.6381 | 88.7437 | -123.2289
2173.1719 | 122.8592 | -122.4197 | 0.37537 | 1.4211e-13 | -0.0089273 | -0.013077 | -0.045384 | -0.041284 | -0.011284 | -0.0084697 | -0.016435 | 0.0093796 | 0.035136 | 0.0067393 | 0.037983 | 0.014783 | 0.015142 | 0.005325 | 0.10249 | 0.078201 | 0.27475 | 0.069732 | -121.7377 | -33.7447 | -121.8912 | 0.24476 | 0.39831 | 0.23668 | -122.8169 | 122.4895 | -0.27288 | 122.4345 | 122.4251 | -0.064407 | -0.29716 | -0.10062 | -0.39719 | -0.13061 | 0.68205 | 0.5285 | 0.92568 | 0.022943 | -0.13868 | 122.5222 | 122.4979 | 122.6945 | 122.4349 | -0.30563 | 122.6645 | 122.818 | 122.6564 | 88.675 | -123.1923
2174.9688 | 122.937 | -122.3694 | 0.34332 | 1.4211e-13 | -0.0089273 | -0.013291 | -0.045384 | -0.04107 | -0.011284 | -0.023731 | -0.016435 | 0.0093796 | 0.034923 | 0.0071667 | 0.038197 | 0.019361 | 0.0243 | 0.005325 | 0.11622 | 0.078201 | 0.27017 | 0.078889 | -121.7377 | -34.0378 | -121.8912 | 0.24476 | 0.40289 | 0.25957 | -122.8215 | 122.4483 | -0.2271 | 122.3887 | 122.3747 | -0.073564 | -0.26512 | -0.073156 | -0.45212 | -0.098568 | 0.63169 | 0.47814 | 0.93026 | 0.059565 | -0.083749 | 122.4856 | 122.4476 | 122.6396 | 122.3937 | -0.26443 | 122.6141 | 122.7723 | 122.629 | 88.3316 | -123.1648
2176.75 | 122.9507 | -122.3923 | 0.32959 | 1.4211e-13 | -0.0087137 | -0.01265 | -0.04517 | -0.040857 | -0.011284 | -0.00083919 | -0.016222 | 0.0093796 | 0.034923 | 0.0073803 | 0.038197 | 0.019361 | 0.0243 | 0.014482 | 0.11165 | 0.073622 | 0.27475 | 0.055995 | -121.724 | -34.285 | -121.8958 | 0.24476 | 0.39373 | 0.22295 | -122.8261 | 122.4483 | -0.21794 | 122.4116 | 122.4068 | -0.041513 | -0.25597 | -0.054845 | -0.43381 | -0.084835 | 0.66832 | 0.49645 | 0.93026 | 0.064141 | -0.10664 | 122.5039 | 122.4659 | 122.667 | 122.4166 | -0.27359 | 122.637 | 122.786 | 122.6152 | 88.1073 | -123.1557
2178.4688 | 122.8683 | -122.438 | 0.37079 | 1.4211e-13 | -0.0084999 | -0.013291 | -0.045384 | -0.040643 | -0.01107 | -0.00083919 | -0.016222 | 0.0093796 | 0.035136 | 0.0069529 | 0.037983 | 0.019361 | 0.019721 | 0.01906 | 0.10249 | 0.069043 | 0.27475 | 0.065153 | -121.724 | -34.4453 | -121.8958 | 0.24933 | 0.39831 | 0.2321 | -122.8261 | 122.5032 | -0.2683 | 122.4574 | 122.4571 | -0.046093 | -0.30175 | -0.096044 | -0.38803 | -0.12145 | 0.7141 | 0.54223 | 0.93026 | 0.02752 | -0.13869 | 122.5405 | 122.5071 | 122.7128 | 122.4578 | -0.30564 | 122.6874 | 122.8364 | 122.6702 | 87.9928 | -123.1969
2180.2656 | 122.85 | -122.4289 | 0.36163 | 1.4211e-13 | -0.0089273 | -0.012863 | -0.045384 | -0.040857 | -0.011497 | 0.0067908 | -0.016649 | 0.0095932 | 0.034923 | 0.0071667 | 0.03777 | 0.019361 | 0.015142 | 0.009904 | 0.10249 | 0.069043 | 0.27932 | 0.065153 | -121.7194 | -34.6879 | -121.8912 | 0.24018 | 0.39831 | 0.25042 | -122.8307 | 122.494 | -0.25914 | 122.4483 | 122.4388 | -0.055249 | -0.29259 | -0.082309 | -0.40177 | -0.12146 | 0.70952 | 0.53765 | 0.93942 | 0.036676 | -0.11122 | 122.5314 | 122.4979 | 122.7082 | 122.444 | -0.29648 | 122.6691 | 122.8272 | 122.6793 | 87.7409 | -123.1923
2182.0625 | 122.8363 | -122.4426 | 0.37537 | 1.4211e-13 | -0.0087137 | -0.013077 | -0.04517 | -0.04107 | -0.011497 | -0.0084697 | -0.016435 | 0.009166 | 0.03535 | 0.0067393 | 0.038197 | 0.014783 | 0.0243 | 0.009904 | 0.11622 | 0.073622 | 0.2839 | 0.065153 | -121.7194 | -34.9856 | -121.8867 | 0.2356 | 0.40289 | 0.23668 | -122.8307 | 122.5078 | -0.25914 | 122.4574 | 122.4525 | -0.055249 | -0.30174 | -0.091463 | -0.38803 | -0.13977 | 0.72325 | 0.55596 | 0.944 | 0.027522 | -0.13868 | 122.5589 | 122.5162 | 122.7265 | 122.4669 | -0.31021 | 122.6782 | 122.8455 | 122.6793 | 87.4571 | -123.206
2183.8438 | 122.9782 | -122.4106 | 0.32959 | 1.4211e-13 | -0.0089273 | -0.013291 | -0.045384 | -0.040643 | -0.011284 | 0.014421 | -0.016649 | 0.0095932 | 0.035136 | 0.0071667 | 0.037983 | 0.014783 | 0.0243 | 0.005325 | 0.10707 | 0.073622 | 0.27475 | 0.060574 | -121.724 | -35.1779 | -121.8958 | 0.2356 | 0.39373 | 0.26873 | -122.8398 | 122.4712 | -0.22252 | 122.4254 | 122.4159 | -0.055249 | -0.25597 | -0.054845 | -0.42924 | -0.093992 | 0.68663 | 0.51476 | 0.944 | 0.064141 | -0.060859 | 122.5177 | 122.4842 | 122.6853 | 122.4349 | -0.26902 | 122.6462 | 122.8043 | 122.6793 | 87.2327 | -123.1694
2185.625 | 122.8043 | -122.4564 | 0.36163 | 1.4211e-13 | -0.0091411 | -0.013077 | -0.045384 | -0.040643 | -0.011497 | 0.0067908 | -0.016649 | 0.009807 | 0.034709 | 0.0069529 | 0.038624 | 0.019361 | 0.0243 | 0.000747 | 0.11165 | 0.073622 | 0.27017 | 0.092626 | -121.7148 | -35.4343 | -121.8867 | 0.24018 | 0.39831 | 0.24126 | -122.8398 | 122.549 | -0.24999 | 122.4757 | 122.4571 | -0.091879 | -0.28801 | -0.091466 | -0.38346 | -0.12146 | 0.74156 | 0.5697 | 0.95316 | 0.036676 | -0.12037 | 122.568 | 122.53 | 122.7265 | 122.4807 | -0.26901 | 122.6965 | 122.8547 | 122.6976 | 87.0221 | -123.2015
2187.4219 | 122.9645 | -122.3923 | 0.31128 | 1.4211e-13 | -0.0093547 | -0.013291 | -0.04517 | -0.040643 | -0.01107 | -0.0084697 | -0.016435 | 0.009166 | 0.035136 | 0.0071667 | 0.038197 | 0.019361 | 0.015142 | 0.005325 | 0.10707 | 0.073622 | 0.27475 | 0.060574 | -121.7194 | -35.6998 | -121.8821 | 0.2356 | 0.39373 | 0.22752 | -122.8398 | 122.4528 | -0.20421 | 122.4116 | 122.3976 | -0.055249 | -0.23766 | -0.036534 | -0.44755 | -0.075681 | 0.6729 | 0.51019 | 0.95773 | 0.082452 | -0.083755 | 122.4993 | 122.4659 | 122.667 | 122.4074 | -0.2507 | 122.6279 | 122.786 | 122.6198 | 86.6924 | -123.1511
2189.125 | 122.8043 | -122.4335 | 0.37537 | 1.4211e-13 | -0.0089273 | -0.013077 | -0.044957 | -0.040643 | -0.011497 | 0.0067908 | -0.016222 | 0.0095932 | 0.034923 | 0.0073803 | 0.038197 | 0.010204 | 0.0243 | 0.009904 | 0.11165 | 0.073622 | 0.2839 | 0.0331 | -121.7194 | -35.8006 | -121.8958 | 0.23102 | 0.38457 | 0.2321 | -122.8444 | 122.4666 | -0.26372 | 122.4437 | 122.4434 | -0.023196 | -0.30174 | -0.091463 | -0.41093 | -0.14435 | 0.7141 | 0.53765 | 0.94858 | 0.009207 | -0.14326 | 122.5451 | 122.5071 | 122.7174 | 122.4578 | -0.34227 | 122.6645 | 122.818 | 122.6656 | 86.6329 | -123.2198
2190.9062 | 122.8592 | -122.4289 | 0.36163 | 1.4211e-13 | -0.0093547 | -0.013077 | -0.044957 | -0.04107 | -0.011284 | -0.0161 | -0.016222 | 0.0095932 | 0.035136 | 0.0069529 | 0.037983 | 0.014783 | 0.028878 | 0.005325 | 0.11165 | 0.073622 | 0.27475 | 0.060574 | -121.7194 | -36.0249 | -121.8821 | 0.24018 | 0.38915 | 0.27789 | -122.8398 | 122.4895 | -0.24999 | 122.4437 | 122.4342 | -0.055249 | -0.28801 | -0.086888 | -0.41093 | -0.12146 | 0.70952 | 0.54681 | 0.95773 | 0.027519 | -0.083745 | 122.5405 | 122.5025 | 122.7036 | 122.4578 | -0.30106 | 122.6691 | 122.818 | 122.7068 | 86.404 | -123.2015
2192.6406 | 122.9141 | -122.406 | 0.32044 | 1.4211e-13 | -0.0091411 | -0.012863 | -0.045598 | -0.04107 | -0.011497 | -0.0084697 | -0.016863 | 0.0095932 | 0.035136 | 0.0073803 | 0.038624 | 0.019361 | 0.028878 | 0.005325 | 0.11165 | 0.073622 | 0.27932 | 0.060574 | -121.7194 | -36.2218 | -121.8821 | 0.2356 | 0.38457 | 0.2321 | -122.8444 | 122.4666 | -0.20879 | 122.4254 | 122.4113 | -0.055249 | -0.24681 | -0.041111 | -0.43839 | -0.084837 | 0.68663 | 0.52392 | 0.96231 | 0.064138 | -0.088333 | 122.5177 | 122.4796 | 122.6853 | 122.4349 | -0.25986 | 122.6416 | 122.7906 | 122.6381 | 86.1842 | -123.1648
2194.4219 | 122.8455 | -122.4243 | 0.36163 | 1.4211e-13 | -0.0091411 | -0.013077 | -0.04517 | -0.040857 | -0.011497 | -0.00083919 | -0.016222 | 0.0093796 | 0.034496 | 0.0071667 | 0.038197 | 0.023939 | 0.015142 | 0.005325 | 0.11165 | 0.073622 | 0.27475 | 0.046837 | -121.7148 | -36.3729 | -121.8821 | 0.2356 | 0.38915 | 0.20921 | -122.849 | 122.4712 | -0.24999 | 122.4483 | 122.4296 | -0.041512 | -0.28801 | -0.086888 | -0.42466 | -0.12603 | 0.70952 | 0.54223 | 0.96689 | 0.027519 | -0.15242 | 122.536 | 122.4979 | 122.6991 | 122.4395 | -0.3148 | 122.6599 | 122.8135 | 122.6335 | 86.0514 | -123.2106
2196.2031 | 122.8409 | -122.4518 | 0.35248 | 1.4211e-13 | -0.0091411 | -0.013505 | -0.045384 | -0.040857 | -0.011497 | -0.0084697 | -0.016008 | 0.0095932 | 0.034923 | 0.0073803 | 0.038624 | 0.019361 | 0.0243 | 0.009904 | 0.10707 | 0.073622 | 0.27475 | 0.060574 | -121.7148 | -36.5606 | -121.8867 | 0.2356 | 0.38 | 0.22752 | -122.8536 | 122.5124 | -0.24541 | 122.4711 | 122.4617 | -0.05067 | -0.27886 | -0.077733 | -0.40177 | -0.11688 | 0.73699 | 0.56512 | 0.96689 | 0.027517 | -0.12495 | 122.5588 | 122.5254 | 122.7265 | 122.4761 | -0.2919 | 122.6874 | 122.8318 | 122.6793 | 85.8911 | -123.206
2198.0156 | 122.9095 | -122.406 | 0.32501 | 1.4211e-13 | -0.0091411 | -0.013077 | -0.044957 | -0.040857 | -0.011711 | -0.0084697 | -0.016435 | 0.009807 | 0.035136 | 0.0071667 | 0.038197 | 0.010204 | 0.019721 | 0.009904 | 0.10707 | 0.069043 | 0.27475 | 0.051416 | -121.7194 | -36.8628 | -121.8821 | 0.23102 | 0.38 | 0.21379 | -122.8536 | 122.4574 | -0.21794 | 122.4162 | 122.4159 | -0.041512 | -0.25597 | -0.050267 | -0.44755 | -0.093992 | 0.68663 | 0.52392 | 0.97147 | 0.054983 | -0.11122 | 122.5131 | 122.475 | 122.6808 | 122.4257 | -0.2736 | 122.637 | 122.786 | 122.6198 | 85.5432 | -123.1786
2199.7344 | 122.8912 | -122.4335 | 0.32501 | 1.4211e-13 | -0.0093547 | -0.013077 | -0.04517 | -0.040857 | -0.011284 | 0.0067908 | -0.016649 | 0.0093796 | 0.034923 | 0.0071667 | 0.038624 | 0.014783 | 0.019721 | 0.009904 | 0.097912 | 0.078201 | 0.27017 | 0.037679 | -121.7102 | -36.9315 | -121.8867 | 0.23102 | 0.38 | 0.20463 | -122.8536 | 122.4712 | -0.2271 | 122.4483 | 122.4434 | -0.027775 | -0.24681 | -0.054845 | -0.42008 | -0.093992 | 0.72325 | 0.54681 | 0.96689 | 0.054983 | -0.12038 | 122.5314 | 122.5117 | 122.7036 | 122.4532 | -0.28733 | 122.6645 | 122.8135 | 122.6381 | 85.502 | -123.1786
2201.4531 | 122.8134 | -122.4701 | 0.37994 | 1.4211e-13 | -0.0091411 | -0.013291 | -0.04517 | -0.040857 | -0.011284 | -0.0084697 | -0.016435 | 0.0095932 | 0.035136 | 0.0071667 | 0.038197 | 0.010204 | 0.019721 | 0.009904 | 0.10249 | 0.073622 | 0.27932 | 0.055995 | -121.7011 | -37.0689 | -121.8821 | 0.23102 | 0.37542 | 0.20005 | -122.8581 | 122.5261 | -0.27745 | 122.4803 | 122.48 | -0.046091 | -0.30632 | -0.10062 | -0.38804 | -0.14892 | 0.76903 | 0.58801 | 0.97605 | -0.004528 | -0.17989 | 122.5726 | 122.5437 | 122.7494 | 122.4898 | -0.32395 | 122.7011 | 122.8455 | 122.6701 | 85.4012 | -123.2381
2203.2344 | 122.8958 | -122.4472 | 0.31128 | 1.4211e-13 | -0.0093547 | -0.013077 | -0.04517 | -0.04107 | -0.011284 | -0.0084697 | -0.016863 | 0.009807 | 0.035136 | 0.0073803 | 0.038197 | 0.014783 | 0.0243 | 0.005325 | 0.11165 | 0.073622 | 0.27475 | 0.060574 | -121.7011 | -37.3344 | -121.8729 | 0.22186 | 0.37084 | 0.22295 | -122.8627 | 122.5078 | -0.19963 | 122.462 | 122.4525 | -0.055249 | -0.23766 | -0.036534 | -0.41551 | -0.089416 | 0.74614 | 0.57428 | 0.98979 | 0.059559 | -0.088334 | 122.5589 | 122.5208 | 122.7219 | 122.4715 | -0.2507 | 122.6691 | 122.818 | 122.6701 | 85.1128 | -123.174
2205.0312 | 122.905 | -122.4289 | 0.31586 | 1.4211e-13 | -0.0091411 | -0.013077 | -0.04517 | -0.04107 | -0.011497 | -0.00083919 | -0.016649 | 0.0095932 | 0.034923 | 0.0073803 | 0.038197 | 0.001048 | 0.0243 | 0.009904 | 0.10249 | 0.069043 | 0.27017 | 0.055995 | -121.7102 | -37.4398 | -121.8729 | 0.22186 | 0.37084 | 0.21379 | -122.8581 | 122.4849 | -0.21337 | 122.4299 | 122.4388 | -0.046091 | -0.24681 | -0.04569 | -0.42924 | -0.093994 | 0.71868 | 0.55597 | 0.98521 | 0.054981 | -0.10207 | 122.5314 | 122.4979 | 122.6991 | 122.4532 | -0.25986 | 122.6508 | 122.7997 | 122.6427 | 84.9891 | -123.174
2206.8125 | 122.8226 | -122.4701 | 0.33875 | 1.4211e-13 | -0.0093547 | -0.013291 | -0.04517 | -0.04107 | -0.011284 | -0.023731 | -0.016435 | 0.0093796 | 0.034709 | 0.0073803 | 0.037983 | 0.010204 | 0.019721 | 0.009904 | 0.10707 | 0.073622 | 0.27017 | 0.055995 | -121.7056 | -37.7236 | -121.8638 | 0.22644 | 0.38 | 0.1909 | -122.8673 | 122.5261 | -0.23168 | 122.4803 | 122.48 | -0.046091 | -0.26512 | -0.068578 | -0.3972 | -0.1123 | 0.76445 | 0.60632 | 1.0035 | 0.04125 | -0.14785 | 122.5772 | 122.5437 | 122.7403 | 122.4898 | -0.28275 | 122.6965 | 122.8501 | 122.661 | 84.7465 | -123.206
2208.5938 | 122.9095 | -122.4197 | 0.32044 | 1.4211e-13 | -0.0089273 | -0.013291 | -0.044957 | -0.040857 | -0.011284 | -0.0084697 | -0.016649 | 0.0095932 | 0.035136 | 0.0071667 | 0.038197 | 0.019361 | 0.0243 | 0.014482 | 0.11165 | 0.078201 | 0.27475 | 0.060574 | -121.6919 | -38.0121 | -121.8729 | 0.22644 | 0.37542 | 0.21379 | -122.8627 | 122.4803 | -0.20879 | 122.4391 | 122.4342 | -0.046092 | -0.24223 | -0.04569 | -0.44297 | -0.093994 | 0.72784 | 0.54681 | 0.98979 | 0.054981 | -0.10665 | 122.5314 | 122.4979 | 122.6945 | 122.444 | -0.25986 | 122.6462 | 122.7952 | 122.6335 | 84.4076 | -123.1831
2210.3438 | 122.9233 | -122.438 | 0.31128 | 1.4211e-13 | -0.0091411 | -0.013077 | -0.04517 | -0.04107 | -0.011284 | -0.0084697 | -0.016649 | 0.0095932 | 0.034709 | 0.0071667 | 0.038197 | 0.014783 | 0.028878 | 0.009904 | 0.11165 | 0.073622 | 0.27475 | 0.037679 | -121.7011 | -38.2685 | -121.8683 | 0.22644 | 0.38 | 0.28247 | -122.8627 | 122.4757 | -0.19963 | 122.4528 | 122.448 | -0.027775 | -0.23766 | -0.036534 | -0.42466 | -0.084838 | 0.73699 | 0.5697 | 0.99437 | 0.068716 | -0.028812 | 122.5497 | 122.5117 | 122.7128 | 122.4669 | -0.2736 | 122.6645 | 122.818 | 122.7205 | 84.1696 | -123.174
2212.125 | 122.9645 | -122.4106 | 0.29755 | 1.4211e-13 | -0.0097821 | -0.013077 | -0.04517 | -0.040857 | -0.01107 | 0.0067908 | -0.017076 | 0.0095932 | 0.034923 | 0.0073803 | 0.038411 | 0.014783 | 0.0243 | 0.009904 | 0.11622 | 0.073622 | 0.27475 | 0.083468 | -121.6965 | -38.5249 | -121.8592 | 0.22644 | 0.37084 | 0.27331 | -122.8719 | 122.4941 | -0.18132 | 122.4254 | 122.4205 | -0.073564 | -0.22392 | -0.022801 | -0.46129 | -0.071105 | 0.7141 | 0.55139 | 1.0127 | 0.073292 | -0.024236 | 122.5268 | 122.4842 | 122.6853 | 122.4349 | -0.21408 | 122.637 | 122.7814 | 122.6839 | 83.8857 | -123.1694
2213.8906 | 122.8226 | -122.4701 | 0.36163 | 1.4211e-13 | -0.0093547 | -0.012863 | -0.045598 | -0.04107 | -0.011497 | 0.0067908 | -0.016649 | 0.009166 | 0.034923 | 0.0073803 | 0.038197 | 0.005626 | 0.028878 | 0.005325 | 0.10707 | 0.078201 | 0.27475 | 0.042258 | -121.6919 | -38.7218 | -121.8638 | 0.21728 | 0.37084 | 0.22295 | -122.8719 | 122.5124 | -0.25456 | 122.4757 | 122.4754 | -0.036933 | -0.28343 | -0.086888 | -0.40178 | -0.14435 | 0.77819 | 0.60632 | 1.0081 | 0.009205 | -0.13869 | 122.5772 | 122.5483 | 122.7448 | 122.499 | -0.31938 | 122.6874 | 122.8409 | 122.693 | 83.7483 | -123.2335
2215.6719 | 122.9187 | -122.4655 | 0.3067 | 1.4211e-13 | -0.0093547 | -0.013291 | -0.04517 | -0.040857 | -0.011497 | 0.0067908 | -0.016649 | 0.0093796 | 0.034923 | 0.0073803 | 0.038197 | 0.014783 | 0.015142 | 0.005325 | 0.097912 | 0.073622 | 0.27932 | 0.042258 | -121.6873 | -38.9095 | -121.8592 | 0.21728 | 0.36626 | 0.21837 | -122.8765 | 122.5078 | -0.20879 | 122.4803 | 122.4708 | -0.036933 | -0.23308 | -0.027378 | -0.41094 | -0.089418 | 0.77819 | 0.60632 | 1.0173 | 0.059557 | -0.088336 | 122.5634 | 122.5391 | 122.7448 | 122.4807 | -0.26444 | 122.6828 | 122.8318 | 122.6839 | 83.556 | -123.1832
2217.3906 | 122.8317 | -122.4792 | 0.3479 | 1.4211e-13 | -0.0095683 | -0.013077 | -0.044743 | -0.04107 | -0.011497 | -0.00083919 | -0.016435 | 0.009807 | 0.034709 | 0.0075939 | 0.038411 | 0.019361 | 0.028878 | 0.009904 | 0.11165 | 0.078201 | 0.27475 | 0.069732 | -121.6919 | -39.2071 | -121.8546 | 0.21728 | 0.37084 | 0.22295 | -122.8719 | 122.549 | -0.23625 | 122.4986 | 122.4892 | -0.059828 | -0.2697 | -0.073155 | -0.39262 | -0.13062 | 0.78735 | 0.62464 | 1.0173 | 0.022938 | -0.12495 | 122.5909 | 122.5574 | 122.754 | 122.5081 | -0.27817 | 122.6965 | 122.8501 | 122.7022 | 83.2721 | -123.2198
2219.1562 | 122.8638 | -122.4701 | 0.35706 | 1.4211e-13 | -0.0093547 | -0.013077 | -0.045384 | -0.040857 | -0.011497 | -0.00083919 | -0.016649 | 0.009166 | 0.035136 | 0.0075939 | 0.038411 | 0.014783 | 0.019721 | 0.009904 | 0.10707 | 0.073622 | 0.27475 | 0.065153 | -121.6782 | -39.4452 | -121.8638 | 0.21271 | 0.36626 | 0.19547 | -122.8765 | 122.5352 | -0.24999 | 122.4849 | 122.48 | -0.055249 | -0.28343 | -0.082311 | -0.40636 | -0.14435 | 0.79193 | 0.60632 | 1.0127 | 0.009203 | -0.16158 | 122.5772 | 122.5437 | 122.7448 | 122.4898 | -0.2919 | 122.6828 | 122.8364 | 122.6656 | 83.0249 | -123.2335
2220.9375 | 122.9416 | -122.4609 | 0.31586 | 1.4211e-13 | -0.0093547 | -0.013505 | -0.04517 | -0.040857 | -0.011497 | -0.0084697 | -0.016649 | 0.0093796 | 0.034923 | 0.0078077 | 0.038197 | 0.010204 | 0.028878 | 0.005325 | 0.11165 | 0.069043 | 0.27475 | 0.055995 | -121.6827 | -39.5917 | -121.85 | 0.21728 | 0.37084 | 0.18174 | -122.881 | 122.5169 | -0.20421 | 122.4711 | 122.4663 | -0.05067 | -0.24681 | -0.041112 | -0.42009 | -0.098573 | 0.77819 | 0.6109 | 1.031 | 0.054981 | -0.13412 | 122.5726 | 122.53 | 122.7357 | 122.4898 | -0.25986 | 122.6782 | 122.8318 | 122.6427 | 82.8692 | -123.1969
2222.7344 | 122.9233 | -122.438 | 0.30212 | 1.4211e-13 | -0.0093547 | -0.012863 | -0.04517 | -0.040643 | -0.011284 | -0.0084697 | -0.016435 | 0.0093796 | 0.034923 | 0.0078077 | 0.037983 | 0.019361 | 0.0243 | 0.000747 | 0.10707 | 0.073622 | 0.27932 | 0.065153 | -121.6736 | -39.8756 | -121.85 | 0.20355 | 0.37084 | 0.19547 | -122.881 | 122.5032 | -0.19506 | 122.4574 | 122.4388 | -0.064406 | -0.2285 | -0.0228 | -0.44298 | -0.098575 | 0.76446 | 0.58802 | 1.031 | 0.068714 | -0.10665 | 122.5451 | 122.5117 | 122.7174 | 122.4623 | -0.23697 | 122.6416 | 122.8089 | 122.6335 | 82.5624 | -123.1832
2224.4531 | 122.9187 | -122.4564 | 0.29755 | 1.4211e-13 | -0.0093547 | -0.013077 | -0.044957 | -0.04107 | -0.011497 | -0.00083919 | -0.016649 | 0.0095932 | 0.034923 | 0.0075939 | 0.038197 | 0.010204 | 0.019721 | 0.005325 | 0.10707 | 0.073622 | 0.27932 | 0.097205 | -121.6827 | -40.1229 | -121.85 | 0.20813 | 0.36168 | 0.19547 | -122.881 | 122.5536 | -0.19048 | 122.4666 | 122.4617 | -0.09188 | -0.22392 | -0.018222 | -0.42467 | -0.089419 | 0.77362 | 0.60633 | 1.031 | 0.064134 | -0.10207 | 122.5634 | 122.53 | 122.7357 | 122.4761 | -0.20034 | 122.6645 | 122.818 | 122.6518 | 82.3335 | -123.1786
2226.2344 | 122.8134 | -122.5021 | 0.34332 | 1.4211e-13 | -0.0095683 | -0.013077 | -0.04517 | -0.040643 | -0.01107 | 0.0067908 | -0.016649 | 0.0093796 | 0.034709 | 0.0073803 | 0.037983 | 0.010204 | 0.019721 | 0.014482 | 0.10707 | 0.073622 | 0.27932 | 0.037679 | -121.6736 | -40.3564 | -121.85 | 0.21271 | 0.36168 | 0.18632 | -122.8856 | 122.5398 | -0.23625 | 122.5123 | 122.5166 | -0.023197 | -0.2697 | -0.063999 | -0.38347 | -0.13062 | 0.82855 | 0.6521 | 1.0356 | 0.018357 | -0.15701 | 122.6092 | 122.5758 | 122.7815 | 122.5219 | -0.30564 | 122.7148 | 122.8638 | 122.6885 | 82.1457 | -123.2289
2227.9688 | 122.9416 | -122.4289 | 0.3067 | 1.4211e-13 | -0.0091411 | -0.013291 | -0.04517 | -0.041284 | -0.011284 | -0.0084697 | -0.016649 | 0.0093796 | 0.034923 | 0.0075939 | 0.037983 | 0.014783 | 0.0243 | 0.009904 | 0.11165 | 0.069043 | 0.27932 | 0.042258 | -121.669 | -40.5533 | -121.8409 | 0.20813 | 0.36168 | 0.1909 | -122.8948 | 122.4712 | -0.19505 | 122.4437 | 122.4388 | -0.032354 | -0.23766 | -0.027378 | -0.46587 | -0.098575 | 0.75988 | 0.58802 | 1.0539 | 0.054978 | -0.11581 | 122.5405 | 122.4979 | 122.7082 | 122.4532 | -0.26444 | 122.637 | 122.7906 | 122.6198 | 81.8756 | -123.2015
2229.75 | 122.9279 | -122.4426 | 0.31128 | 1.4211e-13 | -0.0095683 | -0.013291 | -0.04517 | -0.040857 | -0.011711 | -0.00083919 | -0.016435 | 0.0095932 | 0.034923 | 0.0078077 | 0.038411 | 0.019361 | 0.0243 | 0.009904 | 0.10707 | 0.078201 | 0.26559 | 0.042258 | -121.6736 | -40.8463 | -121.8409 | 0.20355 | 0.36168 | 0.22295 | -122.8948 | 122.4849 | -0.20421 | 122.462 | 122.4525 | -0.032354 | -0.23308 | -0.045691 | -0.45214 | -0.10773 | 0.76904 | 0.60175 | 1.0539 | 0.050401 | -0.088334 | 122.5497 | 122.5208 | 122.7082 | 122.4669 | -0.26902 | 122.6462 | 122.8043 | 122.6656 | 81.5963 | -123.206
2231.4688 | 122.8821 | -122.4701 | 0.32501 | 1.4211e-13 | -0.0095683 | -0.013291 | -0.04517 | -0.040857 | -0.01107 | -0.0084697 | -0.016649 | 0.0093796 | 0.034923 | 0.0073803 | 0.038624 | 0.014783 | 0.0243 | 0.000747 | 0.11165 | 0.08278 | 0.27932 | 0.028521 | -121.6736 | -41.034 | -121.8409 | 0.20813 | 0.3571 | 0.24126 | -122.8902 | 122.4986 | -0.21337 | 122.4849 | 122.4708 | -0.027774 | -0.24223 | -0.045688 | -0.42009 | -0.11689 | 0.79651 | 0.62922 | 1.0493 | 0.03209 | -0.083753 | 122.5817 | 122.5529 | 122.7494 | 122.4944 | -0.29649 | 122.6782 | 122.8272 | 122.7114 | 81.4361 | -123.2152
2233.2656 | 122.8226 | -122.5159 | 0.33875 | 1.4211e-13 | -0.0091411 | -0.013505 | -0.044957 | -0.040643 | -0.01107 | -0.00083919 | -0.016435 | 0.0095932 | 0.034923 | 0.0073803 | 0.038411 | 0.005626 | 0.019721 | 0.005325 | 0.11622 | 0.073622 | 0.27932 | 0.051416 | -121.669 | -41.2035 | -121.8363 | 0.19897 | 0.36168 | 0.18174 | -122.8948 | 122.5673 | -0.22252 | 122.5215 | 122.5212 | -0.046091 | -0.26512 | -0.059421 | -0.3789 | -0.13978 | 0.84686 | 0.67957 | 1.0585 | 0.022935 | -0.15701 | 122.6321 | 122.5895 | 122.7952 | 122.5356 | -0.28733 | 122.7148 | 122.8775 | 122.6976 | 81.3124 | -123.2335
2235.0625 | 122.9187 | -122.4976 | 0.3067 | 1.4211e-13 | -0.0093547 | -0.013077 | -0.045384 | -0.04107 | -0.011497 | 0.0067908 | -0.016649 | 0.0095932 | 0.034709 | 0.0073803 | 0.038411 | 0.010204 | 0.019721 | 0.009904 | 0.11165 | 0.073622 | 0.27932 | 0.037679 | -121.669 | -41.469 | -121.8271 | 0.20355 | 0.36168 | 0.20463 | -122.8856 | 122.5352 | -0.19505 | 122.5078 | 122.5075 | -0.027775 | -0.23308 | -0.027378 | -0.38805 | -0.10315 | 0.82855 | 0.67042 | 1.0585 | 0.054978 | -0.10207 | 122.6092 | 122.5712 | 122.7769 | 122.5173 | -0.26902 | 122.7011 | 122.8592 | 122.7022 | 81.0285 | -123.1923
2236.7812 | 122.85 | -122.4747 | 0.33417 | 1.4211e-13 | -0.0095683 | -0.013291 | -0.044957 | -0.040857 | -0.011497 | -0.00083919 | -0.016649 | 0.0093796 | 0.035136 | 0.0075939 | 0.038197 | 0.014783 | 0.010564 | 0.005325 | 0.11165 | 0.069043 | 0.27017 | 0.051416 | -121.6644 | -41.7163 | -121.8226 | 0.21271 | 0.36168 | 0.19547 | -122.8902 | 122.5261 | -0.22252 | 122.4895 | 122.48 | -0.046091 | -0.26512 | -0.064 | -0.41552 | -0.12146 | 0.81024 | 0.65211 | 1.0676 | 0.027513 | -0.13869 | 122.5863 | 122.5437 | 122.7448 | 122.4852 | -0.28275 | 122.6874 | 122.8364 | 122.6701 | 80.7584 | -123.2244
2238.5625 | 122.8683 | -122.4976 | 0.32044 | 1.4211e-13 | -0.0095683 | -0.013291 | -0.04517 | -0.040857 | -0.011284 | -0.00083919 | -0.016435 | 0.0093796 | 0.034923 | 0.0075939 | 0.038197 | 0.014783 | 0.0243 | 0.005325 | 0.10707 | 0.078201 | 0.27475 | 0.065153 | -121.6644 | -42.0047 | -121.818 | 0.21271 | 0.36168 | 0.18632 | -122.8948 | 122.5627 | -0.21337 | 122.5123 | 122.5029 | -0.059828 | -0.24223 | -0.04569 | -0.39721 | -0.10773 | 0.83313 | 0.67958 | 1.0768 | 0.041245 | -0.13412 | 122.6046 | 122.5758 | 122.7723 | 122.5219 | -0.25528 | 122.7103 | 122.8592 | 122.6839 | 80.4928 | -123.2152
2240.3594 | 122.9553 | -122.4518 | 0.27924 | 1.4211e-13 | -0.0095683 | -0.013291 | -0.044957 | -0.040857 | -0.011497 | -0.0084697 | -0.016649 | 0.009166 | 0.035136 | 0.0078077 | 0.038411 | 0.010204 | 0.015142 | -0.003831 | 0.10249 | 0.073622 | 0.27017 | 0.037679 | -121.6507 | -42.2657 | -121.8088 | 0.20813 | 0.36168 | 0.20463 | -122.8948 | 122.4895 | -0.17675 | 122.462 | 122.448 | -0.04151 | -0.20561 | -0.009069 | -0.44298 | -0.071109 | 0.80109 | 0.64296 | 1.0859 | 0.082444 | -0.074605 | 122.5543 | 122.5254 | 122.7219 | 122.4669 | -0.24156 | 122.6599 | 122.8135 | 122.6564 | 80.1861 | -123.174
2242.1406 | 122.8683 | -122.493 | 0.32959 | 1.4211e-13 | -0.0093547 | -0.012863 | -0.04517 | -0.04107 | -0.011497 | -0.0084697 | -0.016222 | 0.0093796 | 0.035136 | 0.0075939 | 0.038411 | 0.005626 | 0.0243 | 0.005325 | 0.11165 | 0.073622 | 0.27475 | 0.046837 | -121.6507 | -42.4855 | -121.8134 | 0.21271 | 0.35252 | 0.20005 | -122.8902 | 122.5398 | -0.21794 | 122.4986 | 122.4983 | -0.041512 | -0.25597 | -0.054845 | -0.3972 | -0.11688 | 0.84229 | 0.67958 | 1.0768 | 0.022933 | -0.12954 | 122.6046 | 122.5666 | 122.7677 | 122.5173 | -0.28275 | 122.7057 | 122.8455 | 122.693 | 80.0075 | -123.2198
2243.9375 | 122.8775 | -122.4884 | 0.32959 | 1.4211e-13 | -0.0093547 | -0.013077 | -0.04517 | -0.040857 | -0.011284 | -0.0084697 | -0.016649 | 0.009166 | 0.035136 | 0.0080213 | 0.038197 | 0.014783 | 0.0243 | 0.005325 | 0.11165 | 0.073622 | 0.27475 | 0.065153 | -121.6461 | -42.7511 | -121.818 | 0.20355 | 0.3571 | 0.18174 | -122.9039 | 122.5536 | -0.21794 | 122.5032 | 122.4937 | -0.059828 | -0.25597 | -0.054845 | -0.41552 | -0.12604 | 0.84229 | 0.67042 | 1.0859 | 0.027512 | -0.14785 | 122.6001 | 122.562 | 122.7631 | 122.5127 | -0.26444 | 122.692 | 122.8455 | 122.6701 | 79.7373 | -123.2335
2245.6562 | 122.9691 | -122.4655 | 0.32044 | 1.4211e-13 | -0.0095683 | -0.013291 | -0.045384 | -0.041284 | -0.011711 | 0.0067908 | -0.016649 | 0.0095932 | 0.03535 | 0.0075939 | 0.038411 | 0.010204 | 0.028878 | 0.005325 | 0.10707 | 0.069043 | 0.27017 | 0.060574 | -121.6415 | -42.9891 | -121.8134 | 0.20355 | 0.3571 | 0.1909 | -122.8993 | 122.5261 | -0.21337 | 122.4757 | 122.4708 | -0.055249 | -0.25139 | -0.050268 | -0.43383 | -0.11689 | 0.82398 | 0.65211 | 1.0859 | 0.036667 | -0.12954 | 122.5726 | 122.5346 | 122.7357 | 122.4944 | -0.25986 | 122.6691 | 122.8226 | 122.6564 | 79.4764 | -123.2198
2247.4375 | 122.9233 | -122.4701 | 0.31128 | 1.4211e-13 | -0.0097821 | -0.013291 | -0.045384 | -0.04107 | -0.011284 | 0.0067908 | -0.016222 | 0.0093796 | 0.034923 | 0.0073803 | 0.038197 | 0.014783 | 0.019721 | 0.005325 | 0.10707 | 0.073622 | 0.27475 | 0.078889 | -121.6507 | -43.241 | -121.8042 | 0.20355 | 0.3571 | 0.20005 | -122.9039 | 122.549 | -0.20421 | 122.4849 | 122.4754 | -0.073564 | -0.23766 | -0.036534 | -0.43383 | -0.10773 | 0.8194 | 0.66585 | 1.0997 | 0.045823 | -0.11123 | 122.5772 | 122.5437 | 122.7448 | 122.4898 | -0.23239 | 122.6736 | 122.8272 | 122.6701 | 79.2291 | -123.2152
2249.2188 | 122.9553 | -122.4655 | 0.29297 | 1.4211e-13 | -0.0095683 | -0.013291 | -0.044957 | -0.040857 | -0.011284 | -0.00083919 | -0.016649 | 0.0095932 | 0.034923 | 0.0080213 | 0.038624 | 0.014783 | 0.0243 | 0.000747 | 0.11165 | 0.073622 | 0.27932 | 0.051416 | -121.6278 | -43.4562 | -121.7997 | 0.20355 | 0.3571 | 0.20005 | -122.9039 | 122.5169 | -0.18132 | 122.4803 | 122.4663 | -0.050669 | -0.21935 | -0.013645 | -0.43841 | -0.08942 | 0.83771 | 0.66585 | 1.1043 | 0.064133 | -0.092917 | 122.5772 | 122.5391 | 122.7448 | 122.4898 | -0.24155 | 122.6691 | 122.8226 | 122.6656 | 79.0093 | -123.1969
2250.9375 | 122.9187 | -122.4747 | 0.29297 | 1.4211e-13 | -0.0097821 | -0.013077 | -0.045384 | -0.040857 | -0.011711 | -0.0084697 | -0.016863 | 0.0093796 | 0.034923 | 0.0080213 | 0.038411 | 0.014783 | 0.015142 | 0.005325 | 0.10707 | 0.078201 | 0.27932 | 0.055995 | -121.6278 | -43.7538 | -121.7859 | 0.20355 | 0.3571 | 0.22295 | -122.9131 | 122.5307 | -0.1859 | 122.4895 | 122.48 | -0.05067 | -0.21477 | -0.013645 | -0.43841 | -0.08942 | 0.84687 | 0.68874 | 1.1271 | 0.064133 | -0.070024 | 122.5817 | 122.5529 | 122.754 | 122.4898 | -0.23697 | 122.6782 | 122.8318 | 122.6976 | 78.7209 | -123.206
2252.7188 | 122.85 | -122.4884 | 0.31128 | 1.4211e-13 | -0.0093547 | -0.013077 | -0.045384 | -0.040857 | -0.011497 | -0.00083919 | -0.016649 | 0.009166 | 0.03535 | 0.0078077 | 0.038411 | 0.010204 | 0.0243 | 0.009904 | 0.10249 | 0.08278 | 0.27475 | 0.037679 | -121.6324 | -43.9461 | -121.7997 | 0.20355 | 0.35252 | 0.25042 | -122.9131 | 122.5261 | -0.20879 | 122.4986 | 122.4983 | -0.027775 | -0.2285 | -0.036534 | -0.42468 | -0.10773 | 0.85602 | 0.68874 | 1.1134 | 0.041244 | -0.060862 | 122.5909 | 122.5712 | 122.7631 | 122.5127 | -0.2736 | 122.692 | 122.8409 | 122.7388 | 78.5423 | -123.2244
2254.5 | 122.8775 | -122.4747 | 0.32501 | 1.4211e-13 | -0.0093547 | -0.013077 | -0.045384 | -0.040857 | -0.011711 | -0.0084697 | -0.016435 | 0.0093796 | 0.034923 | 0.0078077 | 0.038411 | 0.005626 | 0.0243 | 0.014482 | 0.11165 | 0.073622 | 0.27932 | 0.046837 | -121.6232 | -44.2117 | -121.7859 | 0.20355 | 0.3571 | 0.20005 | -122.9085 | 122.5215 | -0.21337 | 122.4803 | 122.4892 | -0.032355 | -0.25139 | -0.045688 | -0.43383 | -0.12146 | 0.85145 | 0.68874 | 1.1226 | 0.03209 | -0.12496 | 122.5863 | 122.5483 | 122.754 | 122.499 | -0.27818 | 122.6782 | 122.8318 | 122.6747 | 78.263 | -123.2335
2256.2812 | 122.9187 | -122.4838 | 0.31128 | 1.4211e-13 | -0.0095683 | -0.013077 | -0.04517 | -0.04107 | -0.011711 | -0.00083919 | -0.016649 | 0.0093796 | 0.035136 | 0.0080213 | 0.038197 | 0.014783 | 0.019721 | 0.005325 | 0.10707 | 0.073622 | 0.27932 | 0.055995 | -121.6232 | -44.3216 | -121.7814 | 0.20355 | 0.36168 | 0.18632 | -122.9131 | 122.5398 | -0.20421 | 122.4986 | 122.4892 | -0.05067 | -0.23766 | -0.031955 | -0.42925 | -0.10773 | 0.8606 | 0.70247 | 1.1317 | 0.050401 | -0.12496 | 122.5909 | 122.5574 | 122.7631 | 122.5035 | -0.25528 | 122.6874 | 122.8455 | 122.6701 | 78.1623 | -123.2244
2258.0156 | 122.8546 | -122.4701 | 0.31128 | 1.4211e-13 | -0.0093547 | -0.012863 | -0.04517 | -0.040857 | -0.011497 | -0.0084697 | -0.016435 | 0.0093796 | 0.035136 | 0.0078077 | 0.038411 | 0.005626 | 0.028878 | 0.005325 | 0.10707 | 0.073622 | 0.27017 | 0.042258 | -121.6141 | -44.6329 | -121.7859 | 0.20813 | 0.36626 | 0.1909 | -122.9085 | 122.5124 | -0.20421 | 122.4757 | 122.4754 | -0.036933 | -0.23766 | -0.041112 | -0.43841 | -0.10315 | 0.85603 | 0.68416 | 1.1226 | 0.05498 | -0.12038 | 122.5772 | 122.5437 | 122.7403 | 122.499 | -0.26902 | 122.6782 | 122.8364 | 122.661 | 77.8372 | -123.2198
2259.7969 | 122.9507 | -122.4289 | 0.29755 | 1.4211e-13 | -0.0091411 | -0.013077 | -0.04517 | -0.041284 | -0.011284 | -0.0161 | -0.016649 | 0.0095932 | 0.035136 | 0.0075939 | 0.038197 | 0.010204 | 0.015142 | 0.005325 | 0.11165 | 0.078201 | 0.27475 | 0.037679 | -121.6049 | -44.7794 | -121.763 | 0.20355 | 0.3571 | 0.22752 | -122.8993 | 122.4666 | -0.1859 | 122.4391 | 122.4342 | -0.032354 | -0.21934 | -0.022801 | -0.47045 | -0.093997 | 0.82399 | 0.66586 | 1.1363 | 0.059556 | -0.070022 | 122.5405 | 122.5071 | 122.7036 | 122.444 | -0.25987 | 122.6324 | 122.786 | 122.6564 | 77.6495 | -123.1969
2261.5 | 122.937 | -122.4838 | 0.30212 | 1.4211e-13 | -0.0097821 | -0.013077 | -0.04517 | -0.040857 | -0.011497 | -0.00083919 | -0.016222 | 0.0093796 | 0.035136 | 0.0080213 | 0.038411 | 0.010204 | 0.0243 | 0.005325 | 0.10249 | 0.073622 | 0.27017 | 0.037679 | -121.6003 | -44.9443 | -121.7676 | 0.20355 | 0.37542 | 0.19547 | -122.9131 | 122.5215 | -0.19963 | 122.494 | 122.4892 | -0.032354 | -0.2285 | -0.031957 | -0.42925 | -0.098575 | 0.8835 | 0.71621 | 1.1455 | 0.073292 | -0.10665 | 122.5863 | 122.5574 | 122.754 | 122.5081 | -0.26444 | 122.6874 | 122.8592 | 122.6793 | 77.5396 | -123.2152
2263.2812 | 122.9462 | -122.4655 | 0.31128 | 1.4211e-13 | -0.0097821 | -0.013291 | -0.044743 | -0.040857 | -0.011284 | -0.0084697 | -0.016649 | 0.0093796 | 0.034923 | 0.0078077 | 0.038197 | 0.010204 | 0.0243 | 0.009904 | 0.11165 | 0.078201 | 0.2839 | 0.042258 | -121.5957 | -45.2968 | -121.7585 | 0.19897 | 0.36168 | 0.20005 | -122.9131 | 122.5078 | -0.19963 | 122.4757 | 122.4754 | -0.032354 | -0.23308 | -0.027376 | -0.44756 | -0.11231 | 0.86977 | 0.70706 | 1.1546 | 0.050401 | -0.11123 | 122.5772 | 122.5437 | 122.7494 | 122.4898 | -0.26902 | 122.6645 | 122.8272 | 122.6656 | 77.1687 | -123.2244
2265.0625 | 122.9095 | -122.5113 | 0.30212 | 1.4211e-13 | -0.0095683 | -0.013077 | -0.044957 | -0.040857 | -0.011711 | -0.0084697 | -0.016649 | 0.009807 | 0.034923 | 0.0075939 | 0.038197 | 0.010204 | 0.019721 | 0.009904 | 0.11165 | 0.078201 | 0.27932 | 0.028521 | -121.6003 | -45.4617 | -121.7585 | 0.20355 | 0.35252 | 0.20005 | -122.9085 | 122.5398 | -0.19048 | 122.5215 | 122.5212 | -0.018617 | -0.22392 | -0.0228 | -0.39721 | -0.098575 | 0.91096 | 0.75283 | 1.15 | 0.050399 | -0.10207 | 122.6229 | 122.5895 | 122.7906 | 122.531 | -0.2736 | 122.7148 | 122.8638 | 122.7113 | 77.0496 | -123.2106
2266.7812 | 122.9645 | -122.4564 | 0.2655 | 1.4211e-13 | -0.0097821 | -0.013291 | -0.04517 | -0.04107 | -0.011497 | -0.0084697 | -0.016222 | 0.0093796 | 0.035136 | 0.0078077 | 0.038197 | 0.005626 | 0.0243 | 0.000747 | 0.10707 | 0.078201 | 0.2839 | 0.037679 | -121.5957 | -45.6448 | -121.7539 | 0.19897 | 0.3571 | 0.21379 | -122.9268 | 122.494 | -0.15843 | 122.462 | 122.4571 | -0.036932 | -0.1873 | 0.0184 | -0.47046 | -0.066533 | 0.86061 | 0.70248 | 1.1729 | 0.091599 | -0.051715 | 122.5634 | 122.5346 | 122.7403 | 122.4807 | -0.22782 | 122.6553 | 122.8135 | 122.6701 | 76.8116 | -123.1923
2268.5469 | 123.0011 | -122.4884 | 0.28839 | 1.4211e-13 | -0.0093547 | -0.013291 | -0.044957 | -0.04107 | -0.011284 | -0.0084697 | -0.016222 | 0.009166 | 0.035136 | 0.0078077 | 0.038197 | 0.014783 | 0.015142 | 0.005325 | 0.10707 | 0.069043 | 0.27017 | 0.037679 | -121.5957 | -45.9516 | -121.7585 | 0.19439 | 0.35252 | 0.17716 | -122.9222 | 122.5261 | -0.18132 | 122.5032 | 122.4937 | -0.032354 | -0.21935 | -0.018224 | -0.43383 | -0.093999 | 0.89265 | 0.72994 | 1.1638 | 0.064132 | -0.11123 | 122.5955 | 122.5574 | 122.7586 | 122.5035 | -0.25071 | 122.6828 | 122.8409 | 122.6656 | 76.5368 | -123.2106
2270.3281 | 122.8867 | -122.525 | 0.33417 | 1.4211e-13 | -0.0095683 | -0.013077 | -0.04517 | -0.040857 | -0.011284 | -0.00083919 | -0.016435 | 0.0095932 | 0.034923 | 0.0082351 | 0.038411 | 0.014783 | 0.019721 | 0.000747 | 0.10707 | 0.078201 | 0.27932 | 0.060574 | -121.5957 | -46.1393 | -121.7493 | 0.18981 | 0.34794 | 0.20005 | -122.9268 | 122.5856 | -0.2271 | 122.5398 | 122.5258 | -0.059827 | -0.25597 | -0.054843 | -0.40179 | -0.14435 | 0.92927 | 0.77572 | 1.1775 | 0.013777 | -0.13411 | 122.6321 | 122.6032 | 122.8043 | 122.5447 | -0.27359 | 122.7148 | 122.873 | 122.7251 | 76.3857 | -123.261
2272.0469 | 122.9462 | -122.4792 | 0.29755 | 1.4211e-13 | -0.0097821 | -0.013077 | -0.04517 | -0.04107 | -0.011497 | 0.0067908 | -0.016649 | 0.0095932 | 0.03535 | 0.0078077 | 0.038411 | 0.019361 | 0.0243 | 0.005325 | 0.10707 | 0.073622 | 0.27932 | 0.042258 | -121.5866 | -46.4232 | -121.7493 | 0.19439 | 0.34337 | 0.17716 | -122.9268 | 122.5215 | -0.19048 | 122.4986 | 122.4846 | -0.036933 | -0.22392 | -0.018222 | -0.44757 | -0.10315 | 0.89266 | 0.72995 | 1.1775 | 0.04582 | -0.12039 | 122.5863 | 122.5529 | 122.7586 | 122.5035 | -0.25529 | 122.6736 | 122.8226 | 122.6564 | 76.0561 | -123.2244
2273.8438 | 122.9416 | -122.4701 | 0.28381 | 1.4211e-13 | -0.0097821 | -0.013718 | -0.044957 | -0.040857 | -0.01107 | -0.00083919 | -0.016649 | 0.0093796 | 0.035136 | 0.0080213 | 0.038411 | 0.014783 | 0.019721 | 0.005325 | 0.11165 | 0.08278 | 0.27475 | 0.083468 | -121.582 | -46.6384 | -121.7447 | 0.19439 | 0.34337 | 0.20463 | -122.9314 | 122.5536 | -0.17217 | 122.4849 | 122.4754 | -0.078143 | -0.20103 | -0.009068 | -0.4613 | -0.089421 | 0.88808 | 0.72537 | 1.1867 | 0.059553 | -0.079182 | 122.5817 | 122.5529 | 122.7448 | 122.4898 | -0.20034 | 122.6645 | 122.8135 | 122.6747 | 75.8317 | -123.2152
2275.625 | 122.9553 | -122.493 | 0.27924 | 1.4211e-13 | -0.0095683 | -0.013291 | -0.044957 | -0.04107 | -0.011711 | -0.0084697 | -0.016435 | 0.0093796 | 0.035136 | 0.0078077 | 0.038411 | 0.010204 | 0.019721 | 0.005325 | 0.11165 | 0.073622 | 0.27475 | 0.051416 | -121.5866 | -46.8627 | -121.7447 | 0.18981 | 0.33879 | 0.18632 | -122.9314 | 122.5444 | -0.16759 | 122.5032 | 122.4983 | -0.046091 | -0.20561 | -0.004491 | -0.43841 | -0.089423 | 0.90639 | 0.74826 | 1.1867 | 0.059551 | -0.09292 | 122.6046 | 122.5666 | 122.7677 | 122.5127 | -0.22782 | 122.6828 | 122.8318 | 122.6793 | 75.6302 | -123.2106
2277.3594 | 122.85 | -122.5159 | 0.32501 | 1.4211e-13 | -0.0097821 | -0.013077 | -0.04517 | -0.040643 | -0.011497 | -0.00083919 | -0.016435 | 0.0093796 | 0.034709 | 0.0082351 | 0.038197 | 0.010204 | 0.010564 | 0.005325 | 0.10707 | 0.069043 | 0.27475 | 0.0331 | -121.5866 | -47.2107 | -121.7447 | 0.18066 | 0.34337 | 0.19547 | -122.936 | 122.549 | -0.21794 | 122.5261 | 122.5212 | -0.027775 | -0.25597 | -0.050267 | -0.42011 | -0.14436 | 0.92928 | 0.77115 | 1.1913 | 0.018354 | -0.12954 | 122.6229 | 122.5849 | 122.7906 | 122.5264 | -0.29191 | 122.6965 | 122.8592 | 122.7113 | 75.3052 | -123.261
2279.1406 | 122.8592 | -122.5113 | 0.3067 | 1.4211e-13 | -0.0099957 | -0.013077 | -0.04517 | -0.040857 | -0.011284 | -0.00083919 | -0.016222 | 0.0095932 | 0.035136 | 0.0078077 | 0.038197 | 0.005626 | 0.028878 | 0.005325 | 0.11165 | 0.073622 | 0.27475 | 0.060574 | -121.5729 | -47.3023 | -121.731 | 0.18981 | 0.34337 | 0.18632 | -122.9406 | 122.5719 | -0.19505 | 122.5169 | 122.5166 | -0.055249 | -0.23308 | -0.031957 | -0.42926 | -0.11689 | 0.93844 | 0.7803 | 1.2096 | 0.036664 | -0.12039 | 122.6229 | 122.5849 | 122.786 | 122.5402 | -0.24613 | 122.7011 | 122.8547 | 122.6976 | 75.209 | -123.2473
2280.9219 | 122.8363 | -122.5296 | 0.32501 | 1.4211e-13 | -0.0099957 | -0.013077 | -0.045384 | -0.04107 | -0.011284 | -0.0084697 | -0.016649 | 0.0093796 | 0.03535 | 0.0084487 | 0.038624 | 0.010204 | 0.0243 | 0.009904 | 0.11165 | 0.073622 | 0.27932 | 0.055995 | -121.5729 | -47.5816 | -121.7401 | 0.18524 | 0.34794 | 0.168 | -122.9451 | 122.5856 | -0.21337 | 122.5398 | 122.5395 | -0.046091 | -0.25139 | -0.045688 | -0.41553 | -0.13978 | 0.95675 | 0.78946 | 1.205 | 0.022932 | -0.15701 | 122.6412 | 122.6032 | 122.8089 | 122.5539 | -0.26902 | 122.7148 | 122.8775 | 122.6976 | 74.948 | -123.2701
2282.6406 | 122.9141 | -122.5113 | 0.28381 | 1.4211e-13 | -0.0097821 | -0.013291 | -0.04517 | -0.04107 | -0.011497 | -0.00083919 | -0.016649 | 0.009166 | 0.034923 | 0.0080213 | 0.038411 | 0.019361 | 0.0243 | 0.009904 | 0.11165 | 0.078201 | 0.27017 | 0.042258 | -121.5729 | -47.9296 | -121.731 | 0.17608 | 0.34337 | 0.22752 | -122.9406 | 122.5536 | -0.17217 | 122.5307 | 122.5212 | -0.032354 | -0.20561 | -0.013646 | -0.42926 | -0.10773 | 0.93844 | 0.7803 | 1.2096 | 0.059553 | -0.056289 | 122.6229 | 122.5895 | 122.7815 | 122.5356 | -0.24155 | 122.6874 | 122.8547 | 122.7388 | 74.5817 | -123.2244
2284.4375 | 122.8912 | -122.4976 | 0.29297 | 1.4211e-13 | -0.0099957 | -0.013505 | -0.045384 | -0.04107 | -0.011711 | 0.0067908 | -0.016435 | 0.0095932 | 0.035136 | 0.0080213 | 0.038624 | 0.010204 | 0.015142 | 0.009904 | 0.10249 | 0.078201 | 0.27932 | 0.046837 | -121.5591 | -48.099 | -121.7264 | 0.18524 | 0.34794 | 0.17716 | -122.9451 | 122.5444 | -0.19048 | 122.5078 | 122.5075 | -0.036933 | -0.21477 | -0.013645 | -0.44757 | -0.10773 | 0.93844 | 0.77115 | 1.2187 | 0.054975 | -0.11581 | 122.6 | 122.5758 | 122.7769 | 122.5127 | -0.24613 | 122.6828 | 122.8455 | 122.6747 | 74.3986 | -123.2381
2286.1562 | 122.9279 | -122.4747 | 0.27008 | 1.4211e-13 | -0.0099957 | -0.013077 | -0.045384 | -0.04107 | -0.011497 | -0.00083919 | -0.016649 | 0.009807 | 0.03535 | 0.0080213 | 0.038411 | 0.014783 | 0.0243 | 0.009904 | 0.10707 | 0.073622 | 0.27932 | 0.0331 | -121.5591 | -48.3874 | -121.7173 | 0.18066 | 0.34337 | 0.18632 | -122.9451 | 122.5078 | -0.16301 | 122.4895 | 122.4846 | -0.023196 | -0.19646 | 0.009243 | -0.47046 | -0.089425 | 0.91555 | 0.75742 | 1.2279 | 0.073285 | -0.083765 | 122.5817 | 122.5483 | 122.754 | 122.499 | -0.23698 | 122.6553 | 122.818 | 122.661 | 74.0872 | -123.2152
2287.9531 | 122.9233 | -122.493 | 0.28381 | 1.4211e-13 | -0.0099957 | -0.013505 | -0.044957 | -0.040857 | -0.011711 | 0.0067908 | -0.016435 | 0.0095932 | 0.035136 | 0.0080213 | 0.038624 | 0.010204 | 0.028878 | 0.005325 | 0.10707 | 0.069043 | 0.27475 | 0.028521 | -121.5591 | -48.6255 | -121.7081 | 0.18066 | 0.34337 | 0.17716 | -122.9406 | 122.5215 | -0.17674 | 122.5032 | 122.4983 | -0.023196 | -0.21477 | -0.009068 | -0.44757 | -0.10316 | 0.93386 | 0.78489 | 1.2325 | 0.059553 | -0.10665 | 122.6 | 122.562 | 122.7677 | 122.5219 | -0.25529 | 122.6736 | 122.8363 | 122.6701 | 73.8674 | -123.2244
2289.7344 | 122.9874 | -122.4747 | 0.27924 | 1.4211e-13 | -0.0097821 | -0.013077 | -0.04517 | -0.040857 | -0.011711 | -0.0161 | -0.016649 | 0.010021 | 0.03535 | 0.0080213 | 0.038411 | 0.010204 | 0.0243 | 0.009904 | 0.10707 | 0.069043 | 0.27475 | 0.037679 | -121.5454 | -48.8636 | -121.7127 | 0.18066 | 0.34337 | 0.18632 | -122.9451 | 122.5123 | -0.17217 | 122.4849 | 122.4846 | -0.027775 | -0.21019 | -0.004491 | -0.47046 | -0.09858 | 0.92929 | 0.762 | 1.2325 | 0.06413 | -0.09292 | 122.5817 | 122.5437 | 122.7494 | 122.499 | -0.24156 | 122.6553 | 122.818 | 122.661 | 73.611 | -123.2244
2291.4688 | 122.8867 | -122.5204 | 0.31128 | 1.4211e-13 | -0.0099957 | -0.013291 | -0.045598 | -0.040643 | -0.011284 | -0.00083919 | -0.016649 | 0.0093796 | 0.03535 | 0.0082351 | 0.038411 | 0.019361 | 0.019721 | 0.009904 | 0.093333 | 0.073622 | 0.27475 | 0.051416 | -121.55 | -49.033 | -121.7081 | 0.1715 | 0.33879 | 0.17258 | -122.9543 | 122.5719 | -0.21795 | 122.5398 | 122.5304 | -0.041512 | -0.23766 | -0.036534 | -0.43384 | -0.13978 | 0.97048 | 0.81235 | 1.2462 | 0.027508 | -0.1387 | 122.6138 | 122.5941 | 122.7952 | 122.5402 | -0.25986 | 122.6919 | 122.8592 | 122.693 | 73.4874 | -123.2656
2293.25 | 122.9691 | -122.5021 | 0.26093 | 1.4211e-13 | -0.0093547 | -0.013505 | -0.04517 | -0.040857 | -0.011497 | -0.0084697 | -0.016649 | 0.0095932 | 0.035136 | 0.0080213 | 0.038411 | 0.014783 | 0.0243 | 0.009904 | 0.10707 | 0.073622 | 0.27017 | 0.046837 | -121.5408 | -49.294 | -121.7035 | 0.18524 | 0.33421 | 0.17258 | -122.9497 | 122.549 | -0.15386 | 122.5169 | 122.512 | -0.036933 | -0.1873 | 0.009242 | -0.44758 | -0.07569 | 0.96133 | 0.79862 | 1.2462 | 0.073284 | -0.088345 | 122.6092 | 122.5758 | 122.7723 | 122.5264 | -0.21409 | 122.6874 | 122.8363 | 122.6747 | 73.2081 | -123.2106
2295.0312 | 122.9279 | -122.525 | 0.2655 | 1.4211e-13 | -0.0099957 | -0.013291 | -0.04517 | -0.04107 | -0.011711 | -0.00083919 | -0.016435 | 0.0095932 | 0.034923 | 0.0080213 | 0.038624 | 0.014783 | 0.019721 | 0.005325 | 0.11165 | 0.078201 | 0.2839 | 0.023942 | -121.5271 | -49.4497 | -121.6989 | 0.18066 | 0.33421 | 0.20921 | -122.9497 | 122.549 | -0.15386 | 122.5398 | 122.5303 | -0.018617 | -0.1873 | 0.0184 | -0.42469 | -0.084847 | 0.99796 | 0.82609 | 1.2508 | 0.068706 | -0.056294 | 122.6367 | 122.6032 | 122.8089 | 122.5447 | -0.24156 | 122.7057 | 122.8592 | 122.7342 | 73.0753 | -123.2152
2296.7344 | 122.9828 | -122.4884 | 0.29297 | 1.4211e-13 | -0.0099957 | -0.013291 | -0.04517 | -0.04107 | -0.011497 | -0.00083919 | -0.016435 | 0.0095932 | 0.03535 | 0.0080213 | 0.038624 | 0.019361 | 0.0243 | 0.005325 | 0.11165 | 0.073622 | 0.27475 | 0.037679 | -121.5179 | -49.6878 | -121.6944 | 0.18066 | 0.32505 | 0.168 | -122.9543 | 122.5261 | -0.18132 | 122.5078 | 122.4937 | -0.032354 | -0.21935 | -0.018224 | -0.46589 | -0.11231 | 0.97049 | 0.79405 | 1.2599 | 0.032082 | -0.12497 | 122.6001 | 122.562 | 122.7631 | 122.5127 | -0.25529 | 122.6691 | 122.8135 | 122.6564 | 72.8006 | -123.2473
2298.5312 | 122.8455 | -122.5296 | 0.32044 | 1.4211e-13 | -0.0097821 | -0.013505 | -0.045384 | -0.041284 | -0.01107 | -0.00083919 | -0.016649 | 0.009166 | 0.034709 | 0.0080213 | 0.038411 | 0.019361 | 0.019721 | 0.000747 | 0.11165 | 0.073622 | 0.27932 | 0.055995 | -121.5133 | -49.99 | -121.6898 | 0.1715 | 0.33879 | 0.15884 | -122.9497 | 122.5856 | -0.20879 | 122.549 | 122.5303 | -0.055248 | -0.24681 | -0.041111 | -0.42011 | -0.14894 | 1.0163 | 0.83982 | 1.2599 | 0.018352 | -0.16159 | 122.6412 | 122.6032 | 122.8089 | 122.5493 | -0.26444 | 122.7011 | 122.8684 | 122.6884 | 72.5396 | -123.2701
2300.2656 | 122.9599 | -122.5159 | 0.27466 | 1.4211e-13 | -0.0099957 | -0.013505 | -0.045384 | -0.041284 | -0.011497 | -0.00083919 | -0.016435 | 0.0093796 | 0.035136 | 0.0082351 | 0.038624 | 0.005626 | 0.028878 | 0.005325 | 0.11165 | 0.073622 | 0.2839 | 0.0331 | -121.5179 | -50.1915 | -121.6806 | 0.18066 | 0.33421 | 0.18174 | -122.9451 | 122.549 | -0.16301 | 122.5215 | 122.5212 | -0.027775 | -0.20104 | 0.009245 | -0.42926 | -0.094002 | 0.99796 | 0.83525 | 1.2645 | 0.059551 | -0.09292 | 122.6275 | 122.5895 | 122.7998 | 122.5447 | -0.24156 | 122.6965 | 122.8501 | 122.6976 | 72.3244 | -123.2198
2302.0312 | 122.9645 | -122.493 | 0.26093 | 1.4211e-13 | -0.0099957 | -0.013505 | -0.04517 | -0.040643 | -0.011497 | -0.0161 | -0.016435 | 0.0095932 | 0.034923 | 0.0080213 | 0.038624 | 0.014783 | 0.015142 | 0.000747 | 0.11165 | 0.073622 | 0.27932 | 0.046837 | -121.5042 | -50.4067 | -121.6806 | 0.17608 | 0.33421 | 0.1909 | -122.9543 | 122.5398 | -0.14928 | 122.5078 | 122.4937 | -0.04609 | -0.1873 | 0.018399 | -0.46131 | -0.084847 | 0.9888 | 0.81236 | 1.2737 | 0.073284 | -0.07003 | 122.6046 | 122.5666 | 122.7723 | 122.5081 | -0.21409 | 122.6691 | 122.8272 | 122.6839 | 72.0863 | -123.2152
2303.8125 | 122.8912 | -122.525 | 0.3067 | 1.4211e-13 | -0.0099957 | -0.013291 | -0.044957 | -0.04107 | -0.011284 | -0.00083919 | -0.016008 | 0.009807 | 0.03535 | 0.0075939 | 0.038624 | 0.010204 | 0.0243 | 0.009904 | 0.10707 | 0.073622 | 0.26559 | 0.046837 | -121.4996 | -50.6448 | -121.676 | 0.18066 | 0.32963 | 0.18632 | -122.9589 | 122.5719 | -0.19963 | 122.5352 | 122.5349 | -0.036933 | -0.23308 | -0.041114 | -0.43384 | -0.12605 | 1.0254 | 0.84898 | 1.2828 | 0.022928 | -0.12039 | 122.6321 | 122.5986 | 122.7906 | 122.5493 | -0.25986 | 122.7057 | 122.8547 | 122.7113 | 71.8803 | -123.2656
2305.5312 | 123.0148 | -122.4655 | 0.25177 | 1.4211e-13 | -0.0099957 | -0.013505 | -0.04517 | -0.04107 | -0.011497 | 0.0067908 | -0.016649 | 0.0095932 | 0.034709 | 0.0078077 | 0.038411 | 0.014783 | 0.0243 | 0.005325 | 0.10707 | 0.073622 | 0.27475 | 0.0331 | -121.5042 | -50.8004 | -121.6715 | 0.18066 | 0.32963 | 0.168 | -122.9589 | 122.4986 | -0.1447 | 122.4803 | 122.4708 | -0.027775 | -0.17815 | 0.022975 | -0.49335 | -0.071114 | 0.96134 | 0.79405 | 1.2874 | 0.07786 | -0.083768 | 122.5726 | 122.5391 | 122.7403 | 122.4898 | -0.21867 | 122.6462 | 122.7951 | 122.6335 | 71.6651 | -123.2106
2307.3125 | 122.8409 | -122.5204 | 0.3067 | 1.4211e-13 | -0.010209 | -0.013291 | -0.045384 | -0.041284 | -0.011497 | -0.0084697 | -0.016649 | 0.0095932 | 0.034923 | 0.0082351 | 0.038411 | 0.010204 | 0.0243 | 0.005325 | 0.10249 | 0.069043 | 0.27932 | 0.037679 | -121.495 | -50.9836 | -121.676 | 0.17608 | 0.32963 | 0.16342 | -122.9589 | 122.5581 | -0.20421 | 122.5307 | 122.5258 | -0.032354 | -0.23766 | -0.027378 | -0.43842 | -0.13062 | 1.0254 | 0.84441 | 1.2828 | 0.022928 | -0.14328 | 122.6229 | 122.5895 | 122.7998 | 122.5447 | -0.26902 | 122.6965 | 122.8501 | 122.6839 | 71.5369 | -123.2656
2309.0938 | 122.8729 | -122.525 | 0.29755 | 1.4211e-13 | -0.010209 | -0.013505 | -0.045384 | -0.040857 | -0.011497 | -0.0084697 | -0.016435 | 0.0095932 | 0.034923 | 0.0082351 | 0.037983 | 0.010204 | 0.028878 | 0.009904 | 0.11165 | 0.073622 | 0.27475 | 0.042258 | -121.4859 | -51.1438 | -121.6669 | 0.1715 | 0.32505 | 0.1909 | -122.9589 | 122.5673 | -0.1859 | 122.5352 | 122.5349 | -0.032354 | -0.22392 | -0.022801 | -0.43384 | -0.12605 | 1.0392 | 0.85814 | 1.292 | 0.027505 | -0.10665 | 122.6367 | 122.5986 | 122.7998 | 122.5539 | -0.25529 | 122.6965 | 122.8501 | 122.7159 | 71.3812 | -123.2564
2310.875 | 122.9553 | -122.4838 | 0.26093 | 1.4211e-13 | -0.0097821 | -0.013291 | -0.045384 | -0.040857 | -0.011284 | -0.00083919 | -0.016435 | 0.0093796 | 0.034923 | 0.0080213 | 0.037983 | 0.010204 | 0.0243 | 0.005325 | 0.10707 | 0.073622 | 0.27932 | 0.028521 | -121.4904 | -51.4186 | -121.6623 | 0.16692 | 0.32505 | 0.16342 | -122.9634 | 122.5123 | -0.15386 | 122.494 | 122.4892 | -0.023196 | -0.1873 | 0.018399 | -0.47962 | -0.094004 | 0.99339 | 0.82152 | 1.3011 | 0.064126 | -0.097502 | 122.5909 | 122.5574 | 122.7631 | 122.5081 | -0.2324 | 122.6507 | 122.8089 | 122.6472 | 71.0653 | -123.2244
2312.6719 | 122.8638 | -122.5525 | 0.29755 | 1.4211e-13 | -0.010423 | -0.013077 | -0.04517 | -0.04107 | -0.011284 | 0.0067908 | -0.016649 | 0.0093796 | 0.034923 | 0.0082351 | 0.038411 | 0.010204 | 0.019721 | 0.005325 | 0.10707 | 0.069043 | 0.27475 | 0.055995 | -121.4813 | -51.675 | -121.6531 | 0.1715 | 0.32047 | 0.18174 | -122.968 | 122.6085 | -0.19048 | 122.5627 | 122.5578 | -0.05067 | -0.2285 | -0.022801 | -0.41554 | -0.12605 | 1.0712 | 0.89934 | 1.3149 | 0.022927 | -0.11581 | 122.6596 | 122.6215 | 122.8272 | 122.5722 | -0.24155 | 122.724 | 122.873 | 122.7342 | 70.8775 | -123.2656
2314.4062 | 122.9416 | -122.5342 | 0.27008 | 1.4211e-13 | -0.010637 | -0.013291 | -0.04517 | -0.041284 | -0.011284 | -0.0084697 | -0.016649 | 0.009166 | 0.034923 | 0.0082351 | 0.038838 | 0.010204 | 0.028878 | 0.005325 | 0.11165 | 0.069043 | 0.27475 | 0.042258 | -121.4767 | -51.9039 | -121.6486 | 0.16692 | 0.32047 | 0.17258 | -122.9589 | 122.5764 | -0.15843 | 122.5444 | 122.5395 | -0.036933 | -0.20104 | 0.004664 | -0.42469 | -0.10316 | 1.0575 | 0.88561 | 1.3103 | 0.050392 | -0.097501 | 122.6458 | 122.6032 | 122.8089 | 122.5631 | -0.22782 | 122.7011 | 122.8547 | 122.7068 | 70.6303 | -123.2289
2316.1719 | 122.8729 | -122.5525 | 0.28839 | 1.4211e-13 | -0.0099957 | -0.013291 | -0.045384 | -0.040857 | -0.011284 | -0.0084697 | -0.016435 | 0.009807 | 0.035136 | 0.0080213 | 0.038197 | 0.005626 | 0.0243 | 0.005325 | 0.10707 | 0.073622 | 0.27475 | 0.0331 | -121.4675 | -52.1603 | -121.6486 | 0.1715 | 0.32963 | 0.15427 | -122.9726 | 122.5856 | -0.18132 | 122.5581 | 122.5578 | -0.027775 | -0.21477 | -0.013646 | -0.42011 | -0.11689 | 1.0849 | 0.90392 | 1.324 | 0.041239 | -0.13413 | 122.6596 | 122.6261 | 122.8272 | 122.5768 | -0.25529 | 122.724 | 122.8821 | 122.7068 | 70.3922 | -123.261
2317.9688 | 122.9553 | -122.5021 | 0.26093 | 1.4211e-13 | -0.0099957 | -0.013291 | -0.04517 | -0.04107 | -0.011711 | 0.0067908 | -0.016222 | 0.0095932 | 0.035136 | 0.0080213 | 0.038411 | 0.010204 | 0.0243 | 0.005325 | 0.10707 | 0.073622 | 0.27932 | 0.042258 | -121.4538 | -52.403 | -121.6394 | 0.16692 | 0.32505 | 0.15884 | -122.9634 | 122.5444 | -0.15386 | 122.5123 | 122.5075 | -0.036933 | -0.1873 | 0.018399 | -0.46131 | -0.094004 | 1.0483 | 0.86272 | 1.324 | 0.064126 | -0.10208 | 122.6092 | 122.5758 | 122.7815 | 122.5264 | -0.21867 | 122.6691 | 122.8272 | 122.661 | 70.0992 | -123.2244
2319.6875 | 122.9279 | -122.5296 | 0.2655 | 1.4211e-13 | -0.0099957 | -0.013291 | -0.045384 | -0.040857 | -0.011711 | -0.0084697 | -0.016222 | 0.0095932 | 0.034923 | 0.0086623 | 0.038624 | 0.014783 | 0.028878 | 0.014482 | 0.10249 | 0.078201 | 0.27932 | 0.065153 | -121.4492 | -52.664 | -121.6394 | 0.16234 | 0.32047 | 0.16342 | -122.9726 | 122.5948 | -0.16301 | 122.5444 | 122.5441 | -0.050671 | -0.1873 | 0.013821 | -0.443 | -0.10316 | 1.0804 | 0.89019 | 1.3332 | 0.05497 | -0.10208 | 122.6321 | 122.6078 | 122.8089 | 122.5585 | -0.20035 | 122.6919 | 122.8501 | 122.693 | 69.8656 | -123.2381
2321.4688 | 123.0148 | -122.5159 | 0.24261 | 1.4211e-13 | -0.010209 | -0.013291 | -0.045384 | -0.04107 | -0.011497 | -0.00083919 | -0.016435 | 0.0093796 | 0.035136 | 0.0082351 | 0.038197 | 0.014783 | 0.0243 | 0.000747 | 0.10249 | 0.069043 | 0.2839 | 0.042258 | -121.4447 | -52.9066 | -121.6303 | 0.1715 | 0.32047 | 0.16342 | -122.9726 | 122.5581 | -0.14012 | 122.5307 | 122.5166 | -0.041511 | -0.17357 | 0.041288 | -0.45674 | -0.071116 | 1.0712 | 0.88561 | 1.3423 | 0.077858 | -0.079192 | 122.6184 | 122.5849 | 122.7998 | 122.5402 | -0.20036 | 122.6874 | 122.8363 | 122.6793 | 69.6092 | -123.2152
2323.25 | 122.8409 | -122.5616 | 0.29297 | 1.4211e-13 | -0.010423 | -0.013505 | -0.04517 | -0.040643 | -0.011497 | -0.00083919 | -0.016863 | 0.0093796 | 0.035136 | 0.0084487 | 0.038411 | 0.001048 | 0.0243 | 0.014482 | 0.10249 | 0.078201 | 0.27932 | 0.028521 | -121.4401 | -53.0989 | -121.6303 | 0.16692 | 0.32505 | 0.18174 | -122.968 | 122.5902 | -0.19048 | 122.5627 | 122.5761 | -0.014039 | -0.21477 | -0.013645 | -0.40638 | -0.12605 | 1.1216 | 0.93139 | 1.3378 | 0.032082 | -0.11123 | 122.6641 | 122.6398 | 122.841 | 122.5859 | -0.26445 | 122.7286 | 122.8867 | 122.7434 | 69.4627 | -123.261
2324.9844 | 122.9279 | -122.5571 | 0.26093 | 1.4211e-13 | -0.0099957 | -0.013505 | -0.04517 | -0.04107 | -0.011497 | -0.0084697 | -0.017076 | 0.0095932 | 0.034923 | 0.0084487 | 0.038197 | 0.010204 | 0.019721 | 0.000747 | 0.10707 | 0.069043 | 0.27475 | 0.042258 | -121.4263 | -53.2684 | -121.6211 | 0.16234 | 0.31589 | 0.16342 | -122.9634 | 122.5993 | -0.15386 | 122.5673 | 122.5578 | -0.041511 | -0.19188 | 0.01382 | -0.40638 | -0.098583 | 1.1307 | 0.93597 | 1.3423 | 0.054969 | -0.097502 | 122.6641 | 122.6261 | 122.8318 | 122.5768 | -0.21867 | 122.7194 | 122.873 | 122.7205 | 69.2887 | -123.2244
2326.75 | 122.9416 | -122.525 | 0.24261 | 1.4211e-13 | -0.010423 | -0.013505 | -0.045384 | -0.04107 | -0.011284 | -0.0084697 | -0.016222 | 0.009807 | 0.03535 | 0.0082351 | 0.038624 | 0.005626 | 0.0243 | 0.005325 | 0.10249 | 0.073622 | 0.27475 | 0.042258 | -121.4218 | -53.4973 | -121.6165 | 0.16692 | 0.32047 | 0.16342 | -122.9772 | 122.5673 | -0.14012 | 122.5307 | 122.5303 | -0.036933 | -0.16899 | 0.03213 | -0.45216 | -0.075694 | 1.1033 | 0.90851 | 1.3607 | 0.077858 | -0.079192 | 122.6275 | 122.5986 | 122.7998 | 122.5493 | -0.20036 | 122.6919 | 122.8455 | 122.6884 | 69.0277 | -123.2198
2328.5469 | 122.8683 | -122.5571 | 0.28839 | 1.4211e-13 | -0.010209 | -0.013291 | -0.045384 | -0.04107 | -0.011497 | -0.00083919 | -0.016222 | 0.0089522 | 0.035136 | 0.0080213 | 0.038624 | 0.005626 | 0.019721 | 0.000747 | 0.10707 | 0.073622 | 0.27932 | 0.060574 | -121.4126 | -53.6942 | -121.6074 | 0.16234 | 0.31132 | 0.15427 | -122.9772 | 122.6176 | -0.18132 | 122.5627 | 122.5578 | -0.059827 | -0.21477 | -0.009067 | -0.42012 | -0.12605 | 1.1445 | 0.94971 | 1.3698 | 0.022925 | -0.13413 | 122.6641 | 122.6307 | 122.8364 | 122.5768 | -0.22782 | 122.7194 | 122.8684 | 122.7113 | 68.8629 | -123.2656
2330.2656 | 122.9279 | -122.525 | 0.27008 | 1.4211e-13 | -0.010637 | -0.013077 | -0.045598 | -0.041284 | -0.011497 | -0.0084697 | -0.016435 | 0.009807 | 0.035136 | 0.0082351 | 0.038624 | 0.010204 | 0.0243 | 0.005325 | 0.11165 | 0.078201 | 0.27475 | 0.019363 | -121.4172 | -53.859 | -121.5982 | 0.16692 | 0.31132 | 0.18174 | -122.9772 | 122.5444 | -0.15843 | 122.5352 | 122.5303 | -0.014038 | -0.19188 | 0.004664 | -0.45216 | -0.10316 | 1.1078 | 0.92682 | 1.379 | 0.041235 | -0.088343 | 122.6367 | 122.6032 | 122.7998 | 122.5493 | -0.25072 | 122.6919 | 122.8363 | 122.7068 | 68.666 | -123.2473
2332.0469 | 122.8729 | -122.5433 | 0.29297 | 1.4211e-13 | -0.0099957 | -0.013291 | -0.045384 | -0.04107 | -0.011711 | -0.0084697 | -0.016435 | 0.0095932 | 0.034923 | 0.0084487 | 0.038411 | 0.019361 | 0.010564 | 0.005325 | 0.11622 | 0.073622 | 0.27475 | 0.046837 | -121.3989 | -53.9918 | -121.6028 | 0.16234 | 0.32047 | 0.16342 | -122.9726 | 122.5902 | -0.17674 | 122.5627 | 122.5487 | -0.041512 | -0.21935 | -0.018224 | -0.42927 | -0.13063 | 1.1445 | 0.94055 | 1.3698 | 0.027504 | -0.12955 | 122.6596 | 122.617 | 122.8181 | 122.5539 | -0.24613 | 122.7057 | 122.8638 | 122.7068 | 68.5515 | -123.2656
2333.8281 | 122.8638 | -122.5479 | 0.31128 | 1.4211e-13 | -0.0099957 | -0.013291 | -0.044957 | -0.040857 | -0.011497 | 0.0067908 | -0.016435 | 0.0095932 | 0.034923 | 0.0086623 | 0.038838 | 0.005626 | 0.028878 | 0.005325 | 0.11165 | 0.08278 | 0.27475 | 0.028521 | -121.3943 | -54.3031 | -121.5982 | 0.16234 | 0.31589 | 0.15427 | -122.9818 | 122.5764 | -0.19963 | 122.5535 | 122.5532 | -0.023196 | -0.2285 | -0.036534 | -0.43385 | -0.14894 | 1.1536 | 0.94971 | 1.3836 | 0.004615 | -0.15701 | 122.6596 | 122.6307 | 122.8227 | 122.5768 | -0.28276 | 122.7103 | 122.8638 | 122.7022 | 68.2448 | -123.293
2335.6094 | 122.8638 | -122.5388 | 0.29297 | 1.4211e-13 | -0.010209 | -0.013291 | -0.045384 | -0.040857 | -0.01107 | -0.0161 | -0.016435 | 0.0095932 | 0.034923 | 0.0084487 | 0.038624 | 0.014783 | 0.019721 | 0.005325 | 0.10249 | 0.078201 | 0.27475 | 0.051416 | -121.3943 | -54.587 | -121.5936 | 0.16234 | 0.31589 | 0.16342 | -122.9772 | 122.5902 | -0.19048 | 122.5535 | 122.5441 | -0.046091 | -0.21477 | -0.018224 | -0.43843 | -0.13063 | 1.1445 | 0.94513 | 1.3836 | 0.022925 | -0.12955 | 122.6412 | 122.617 | 122.8135 | 122.5585 | -0.24155 | 122.7011 | 122.8547 | 122.7022 | 67.9517 | -123.2702
2337.3906 | 122.9782 | -122.5342 | 0.27466 | 1.4211e-13 | -0.010209 | -0.013077 | -0.045384 | -0.041284 | -0.011497 | -0.00083919 | -0.016435 | 0.0095932 | 0.035136 | 0.0086623 | 0.038411 | 0.010204 | 0.019721 | 0.005325 | 0.10249 | 0.073622 | 0.27932 | 0.046837 | -121.3851 | -54.7244 | -121.5845 | 0.15318 | 0.31132 | 0.15427 | -122.9726 | 122.581 | -0.17217 | 122.5444 | 122.5395 | -0.041512 | -0.20104 | 0.004666 | -0.43842 | -0.12147 | 1.1491 | 0.94971 | 1.3881 | 0.036658 | -0.12039 | 122.6367 | 122.6078 | 122.8135 | 122.5539 | -0.22782 | 122.6874 | 122.8455 | 122.6884 | 67.8098 | -123.2473
2339.1094 | 122.8546 | -122.5479 | 0.27924 | 1.4211e-13 | -0.0099957 | -0.013077 | -0.045384 | -0.041284 | -0.011497 | -0.0084697 | -0.016649 | 0.009807 | 0.034709 | 0.0086623 | 0.038197 | 0.001048 | 0.019721 | 0.009904 | 0.10249 | 0.08278 | 0.27932 | 0.028521 | -121.376 | -54.9854 | -121.5845 | 0.15776 | 0.31132 | 0.19547 | -122.9772 | 122.5764 | -0.17675 | 122.549 | 122.5578 | -0.018617 | -0.19646 | 8.8e-05 | -0.42927 | -0.12147 | 1.1719 | 0.96344 | 1.3927 | 0.03208 | -0.083763 | 122.6504 | 122.6307 | 122.8272 | 122.5676 | -0.25071 | 122.7057 | 122.8592 | 122.7434 | 67.5625 | -123.2564
2340.8906 | 122.9233 | -122.5479 | 0.24719 | 1.4211e-13 | -0.010209 | -0.013077 | -0.044957 | -0.041284 | -0.01107 | -0.00083919 | -0.016435 | 0.0095932 | 0.035136 | 0.0084487 | 0.038624 | 0.010204 | 0.019721 | 0.005325 | 0.11165 | 0.078201 | 0.27932 | 0.0331 | -121.3622 | -55.1777 | -121.5707 | 0.16234 | 0.31589 | 0.15884 | -122.9818 | 122.581 | -0.13554 | 122.5581 | 122.5532 | -0.027775 | -0.16899 | 0.032132 | -0.43385 | -0.08485 | 1.1857 | 0.97718 | 1.411 | 0.068702 | -0.088347 | 122.6596 | 122.6261 | 122.8272 | 122.5676 | -0.21409 | 122.7103 | 122.8638 | 122.7068 | 67.3702 | -123.229
2342.6719 | 122.9965 | -122.5113 | 0.24261 | 1.4211e-13 | -0.010423 | -0.013077 | -0.04517 | -0.04107 | -0.011711 | -0.00083919 | -0.016435 | 0.0093796 | 0.034923 | 0.0084487 | 0.038624 | 0.005626 | 0.0243 | 0.009904 | 0.10707 | 0.078201 | 0.2839 | 0.046837 | -121.3531 | -55.3608 | -121.5707 | 0.15776 | 0.32047 | 0.15884 | -122.9863 | 122.5581 | -0.13555 | 122.5169 | 122.5212 | -0.036933 | -0.16441 | 0.041288 | -0.47505 | -0.084851 | 1.1582 | 0.94056 | 1.4156 | 0.077858 | -0.08377 | 122.6184 | 122.5895 | 122.7952 | 122.5356 | -0.19578 | 122.6691 | 122.8318 | 122.6701 | 67.1505 | -123.229
2344.4844 | 122.8638 | -122.5479 | 0.27924 | 1.4211e-13 | -0.010423 | -0.013291 | -0.044957 | -0.041498 | -0.011711 | 0.0067908 | -0.016222 | 0.0095932 | 0.034709 | 0.0084487 | 0.038411 | 0.019361 | 0.015142 | 0.000747 | 0.10707 | 0.078201 | 0.27932 | 0.055995 | -121.3485 | -55.5943 | -121.5662 | 0.16234 | 0.31589 | 0.15884 | -122.9818 | 122.6039 | -0.17217 | 122.5673 | 122.5487 | -0.055248 | -0.20103 | 8.8e-05 | -0.43385 | -0.11689 | 1.1994 | 0.98176 | 1.4156 | 0.036658 | -0.12039 | 122.655 | 122.6261 | 122.8272 | 122.5631 | -0.22324 | 122.7103 | 122.8638 | 122.7068 | 66.9536 | -123.261
2346.2031 | 122.8958 | -122.5662 | 0.30212 | 1.4211e-13 | -0.0099957 | -0.013291 | -0.045384 | -0.040643 | -0.011711 | -0.00083919 | -0.016435 | 0.009807 | 0.034923 | 0.0086623 | 0.038624 | 0.005626 | 0.0243 | 0.000747 | 0.10707 | 0.073622 | 0.27932 | 0.060574 | -121.3393 | -55.7958 | -121.557 | 0.15776 | 0.30674 | 0.15427 | -122.9772 | 122.6268 | -0.19506 | 122.5718 | 122.567 | -0.059827 | -0.2285 | -0.0228 | -0.41096 | -0.14436 | 1.2269 | 1.0092 | 1.4202 | 0.004613 | -0.14786 | 122.6733 | 122.6398 | 122.8455 | 122.5905 | -0.24155 | 122.724 | 122.873 | 122.7205 | 66.7704 | -123.2793
2348 | 122.8363 | -122.5662 | 0.27924 | 1.4211e-13 | -0.0099957 | -0.013077 | -0.045384 | -0.041284 | -0.011497 | -0.00083919 | -0.016649 | 0.0095932 | 0.035136 | 0.0086623 | 0.038624 | 0.010204 | 0.019721 | 0.005325 | 0.10707 | 0.08278 | 0.27932 | 0.046837 | -121.3256 | -55.9881 | -121.5524 | 0.15776 | 0.31589 | 0.15884 | -122.9818 | 122.6131 | -0.17217 | 122.5764 | 122.5715 | -0.041512 | -0.19646 | 8.8e-05 | -0.41554 | -0.12147 | 1.2406 | 1.0138 | 1.4293 | 0.036658 | -0.12039 | 122.6733 | 122.649 | 122.8455 | 122.5859 | -0.2324 | 122.724 | 122.8821 | 122.7251 | 66.5781 | -123.261
2349.7812 | 122.9507 | -122.5159 | 0.24719 | 1.4211e-13 | -0.010423 | -0.013291 | -0.044957 | -0.040857 | -0.011284 | -0.00083919 | -0.016435 | 0.0095932 | 0.034709 | 0.0084487 | 0.038411 | 0.014783 | 0.0243 | 0.009904 | 0.11165 | 0.073622 | 0.27932 | 0.051416 | -121.3164 | -56.1575 | -121.5524 | 0.15318 | 0.30674 | 0.15427 | -122.9818 | 122.5673 | -0.13554 | 122.5307 | 122.5258 | -0.041512 | -0.17357 | 0.032132 | -0.46589 | -0.094007 | 1.1994 | 0.96345 | 1.4293 | 0.059545 | -0.092926 | 122.6275 | 122.5895 | 122.7952 | 122.5402 | -0.19578 | 122.6691 | 122.8226 | 122.6701 | 66.3584 | -123.229
2351.5781 | 122.9095 | -122.5388 | 0.27466 | 1.4211e-13 | -0.010637 | -0.013505 | -0.045384 | -0.04107 | -0.011284 | -0.0161 | -0.016435 | 0.010021 | 0.035136 | 0.0084487 | 0.038411 | 0.019361 | 0.019721 | 0.005325 | 0.10707 | 0.078201 | 0.2839 | 0.046837 | -121.3073 | -56.3178 | -121.5433 | 0.16234 | 0.31132 | 0.14969 | -122.9955 | 122.5856 | -0.16759 | 122.5581 | 122.5441 | -0.041512 | -0.19646 | 0.009245 | -0.45674 | -0.11232 | 1.2315 | 0.9955 | 1.4522 | 0.036658 | -0.12497 | 122.6458 | 122.617 | 122.8227 | 122.5585 | -0.22782 | 122.7011 | 122.8501 | 122.6884 | 66.221 | -123.2702
2353.3594 | 122.9782 | -122.5296 | 0.24719 | 1.4211e-13 | -0.010209 | -0.013291 | -0.045384 | -0.04107 | -0.011497 | -0.0084697 | -0.016435 | 0.0093796 | 0.035136 | 0.0086623 | 0.038624 | 0.010204 | 0.0243 | 0.000747 | 0.10707 | 0.073622 | 0.27932 | 0.051416 | -121.3027 | -56.4506 | -121.5387 | 0.15318 | 0.31132 | 0.14511 | -122.9863 | 122.581 | -0.14012 | 122.5398 | 122.5303 | -0.050669 | -0.17357 | 0.032132 | -0.45674 | -0.094007 | 1.2269 | 0.99092 | 1.4477 | 0.064124 | -0.10208 | 122.6367 | 122.6032 | 122.8089 | 122.5539 | -0.19578 | 122.6828 | 122.8409 | 122.6747 | 66.079 | -123.2335
2355.1562 | 122.9599 | -122.5342 | 0.25177 | 1.4211e-13 | -0.010423 | -0.013291 | -0.04517 | -0.04107 | -0.011497 | 0.0067908 | -0.016435 | 0.0093796 | 0.035136 | 0.0084487 | 0.038624 | 0.014783 | 0.0243 | 0.005325 | 0.10707 | 0.069043 | 0.27932 | 0.042258 | -121.2844 | -56.6749 | -121.5341 | 0.16692 | 0.31589 | 0.14969 | -122.9863 | 122.5764 | -0.1447 | 122.549 | 122.5395 | -0.036933 | -0.18273 | 0.027554 | -0.45216 | -0.084849 | 1.2498 | 1.0001 | 1.4522 | 0.064124 | -0.10208 | 122.6412 | 122.6032 | 122.8135 | 122.5585 | -0.20951 | 122.7011 | 122.8501 | 122.6839 | 65.8593 | -123.2381
2356.9531 | 122.8821 | -122.5754 | 0.27924 | 1.4211e-13 | -0.010423 | -0.013077 | -0.045384 | -0.040643 | -0.011711 | -0.00083919 | -0.016222 | 0.0093796 | 0.034709 | 0.0084487 | 0.038624 | 0.010204 | 0.015142 | 0.005325 | 0.10707 | 0.078201 | 0.27017 | 0.042258 | -121.289 | -56.794 | -121.5295 | 0.15318 | 0.30674 | 0.15427 | -122.9863 | 122.6176 | -0.17217 | 122.5856 | 122.5807 | -0.036933 | -0.20103 | -0.009069 | -0.41096 | -0.12605 | 1.2864 | 1.0459 | 1.4568 | 0.027501 | -0.12497 | 122.6824 | 122.6536 | 122.8455 | 122.5905 | -0.23698 | 122.7286 | 122.8821 | 122.7296 | 65.7814 | -123.2656
2358.7344 | 122.9828 | -122.5204 | 0.25177 | 1.4211e-13 | -0.01085 | -0.013291 | -0.045598 | -0.041284 | -0.011711 | 0.0067908 | -0.016008 | 0.0095932 | 0.034923 | 0.0086623 | 0.038838 | 0.005626 | 0.019721 | 0.005325 | 0.10707 | 0.078201 | 0.27475 | 0.028521 | -121.2752 | -56.9634 | -121.5204 | 0.15318 | 0.31132 | 0.14053 | -122.9863 | 122.549 | -0.1447 | 122.5261 | 122.5258 | -0.023196 | -0.17357 | 0.022975 | -0.46589 | -0.098585 | 1.2452 | 1.0001 | 1.466 | 0.059546 | -0.11124 | 122.6275 | 122.5986 | 122.7952 | 122.5402 | -0.22325 | 122.6736 | 122.8318 | 122.661 | 65.5571 | -123.2381
2360.4688 | 122.9187 | -122.5433 | 0.25635 | 1.4211e-13 | -0.010637 | -0.013291 | -0.045598 | -0.04107 | -0.011924 | 0.0067908 | -0.016649 | 0.009807 | 0.03535 | 0.0084487 | 0.038411 | 0.014783 | 0.0243 | 0.000747 | 0.11622 | 0.073622 | 0.27475 | 0.060574 | -121.2707 | -57.2244 | -121.5204 | 0.16234 | 0.31589 | 0.16342 | -122.9909 | 122.6039 | -0.14012 | 122.5581 | 122.5441 | -0.059827 | -0.18273 | 0.018397 | -0.44759 | -0.094006 | 1.2727 | 1.023 | 1.4706 | 0.059546 | -0.092925 | 122.6596 | 122.617 | 122.8181 | 122.5676 | -0.19577 | 122.7057 | 122.8592 | 122.7068 | 65.319 | -123.2473
2362.25 | 122.8867 | -122.5571 | 0.27924 | 1.4211e-13 | -0.010209 | -0.013291 | -0.045384 | -0.04107 | -0.011284 | -0.00083919 | -0.016649 | 0.0095932 | 0.034923 | 0.0086623 | 0.038624 | 0.010204 | 0.0243 | 0.005325 | 0.11622 | 0.073622 | 0.2839 | 0.023942 | -121.2523 | -57.3434 | -121.5158 | 0.15776 | 0.31132 | 0.14511 | -122.9955 | 122.581 | -0.16301 | 122.5673 | 122.5624 | -0.018617 | -0.20561 | 0.004667 | -0.43843 | -0.12147 | 1.3047 | 1.0413 | 1.4797 | 0.03208 | -0.13413 | 122.6733 | 122.6307 | 122.841 | 122.5814 | -0.25529 | 122.7148 | 122.8684 | 122.7022 | 65.2137 | -123.2747
2363.9844 | 122.8638 | -122.5342 | 0.27466 | 1.4211e-13 | -0.01085 | -0.013291 | -0.04517 | -0.040857 | -0.011924 | -0.00083919 | -0.016435 | 0.0093796 | 0.034923 | 0.0082351 | 0.038624 | 0.010204 | 0.019721 | 0.000747 | 0.10707 | 0.078201 | 0.27932 | 0.028521 | -121.2523 | -57.522 | -121.5066 | 0.15776 | 0.32047 | 0.15427 | -122.9909 | 122.5627 | -0.16759 | 122.5444 | 122.5349 | -0.027774 | -0.19646 | 0.004666 | -0.45674 | -0.11689 | 1.2818 | 1.0276 | 1.4843 | 0.045815 | -0.12039 | 122.6412 | 122.6124 | 122.8135 | 122.5539 | -0.24614 | 122.6919 | 122.8547 | 122.6884 | 65.0122 | -123.2656
2365.7656 | 122.9507 | -122.58 | 0.25177 | 1.4211e-13 | -0.010637 | -0.013077 | -0.045384 | -0.04107 | -0.011711 | -0.0084697 | -0.016435 | 0.0093796 | 0.03535 | 0.0082351 | 0.038838 | 0.010204 | 0.015142 | 0.005325 | 0.11165 | 0.069043 | 0.27475 | 0.023942 | -121.2386 | -57.7143 | -121.4883 | 0.15318 | 0.30674 | 0.15884 | -122.9909 | 122.6039 | -0.14012 | 122.5902 | 122.5853 | -0.018617 | -0.18273 | 0.022975 | -0.41096 | -0.098585 | 1.3413 | 1.0916 | 1.5026 | 0.054967 | -0.092925 | 122.6916 | 122.649 | 122.8547 | 122.5951 | -0.22783 | 122.7331 | 122.8867 | 122.7388 | 64.8657 | -123.2427
2367.5625 | 122.9233 | -122.5388 | 0.25177 | 1.4211e-13 | -0.010423 | -0.013077 | -0.045384 | -0.040857 | -0.011711 | -0.00083919 | -0.016649 | 0.0093796 | 0.03535 | 0.0084487 | 0.038624 | 0.014783 | 0.0243 | 0.000747 | 0.10707 | 0.078201 | 0.28848 | 0.046837 | -121.2249 | -57.9112 | -121.4883 | 0.16234 | 0.31132 | 0.14969 | -122.9909 | 122.5856 | -0.1447 | 122.5535 | 122.5395 | -0.04609 | -0.17357 | 0.036711 | -0.45216 | -0.089428 | 1.3139 | 1.0504 | 1.5026 | 0.059546 | -0.10208 | 122.6458 | 122.617 | 122.8272 | 122.5631 | -0.20493 | 122.7011 | 122.8501 | 122.6884 | 64.6276 | -123.2427
2369.3438 | 122.8546 | -122.5708 | 0.27466 | 1.4211e-13 | -0.010637 | -0.013077 | -0.04517 | -0.041284 | -0.011497 | 0.0067908 | -0.016222 | 0.0095932 | 0.035136 | 0.0086623 | 0.039052 | 0.010204 | 0.019721 | 0.009904 | 0.11165 | 0.087359 | 0.27932 | 0.023942 | -121.2157 | -58.108 | -121.4837 | 0.16692 | 0.31132 | 0.168 | -122.9863 | 122.5947 | -0.16301 | 122.581 | 122.5807 | -0.014038 | -0.1873 | 0.004666 | -0.41554 | -0.10774 | 1.3551 | 1.0871 | 1.5026 | 0.036658 | -0.10666 | 122.6824 | 122.6582 | 122.8501 | 122.5905 | -0.25072 | 122.7377 | 122.8821 | 122.7388 | 64.4628 | -123.261
2371.0625 | 122.9416 | -122.5479 | 0.25177 | 1.4211e-13 | -0.01085 | -0.013291 | -0.04517 | -0.040857 | -0.011497 | 0.0067908 | -0.016008 | 0.009166 | 0.03535 | 0.0086623 | 0.038624 | 0.014783 | 0.019721 | 0.009904 | 0.10707 | 0.073622 | 0.2839 | 0.037679 | -121.2157 | -58.2775 | -121.4837 | 0.15318 | 0.30674 | 0.14969 | -122.9955 | 122.5856 | -0.1447 | 122.5627 | 122.5578 | -0.027775 | -0.17815 | 0.032133 | -0.44759 | -0.098585 | 1.3322 | 1.0642 | 1.5118 | 0.054967 | -0.10208 | 122.655 | 122.6215 | 122.8318 | 122.5676 | -0.21409 | 122.7011 | 122.8546 | 122.6976 | 64.2705 | -123.2473
2372.8281 | 122.905 | -122.5433 | 0.25635 | 1.4211e-13 | -0.01085 | -0.013505 | -0.045384 | -0.040643 | -0.011711 | -0.0084697 | -0.016435 | 0.0093796 | 0.035136 | 0.0084487 | 0.038197 | 0.010204 | 0.015142 | 0.000747 | 0.11165 | 0.069043 | 0.27932 | 0.023942 | -121.2066 | -58.4148 | -121.47 | 0.15318 | 0.31132 | 0.15427 | -122.9863 | 122.5673 | -0.1447 | 122.5535 | 122.5441 | -0.023195 | -0.18731 | 0.022976 | -0.44301 | -0.10316 | 1.3368 | 1.0733 | 1.5163 | 0.054968 | -0.10208 | 122.655 | 122.6124 | 122.8227 | 122.5585 | -0.23241 | 122.6965 | 122.8547 | 122.6976 | 64.1285 | -123.2427
2374.625 | 122.9782 | -122.5433 | 0.24261 | 1.4211e-13 | -0.010637 | -0.013291 | -0.04517 | -0.041284 | -0.011711 | -0.00083919 | -0.016222 | 0.0095932 | 0.034923 | 0.0084487 | 0.038624 | 0.010204 | 0.028878 | 0.005325 | 0.097912 | 0.078201 | 0.27932 | 0.023942 | -121.1882 | -58.5934 | -121.4608 | 0.15318 | 0.32047 | 0.15427 | -122.9955 | 122.5673 | -0.1447 | 122.5535 | 122.5487 | -0.018617 | -0.16441 | 0.036709 | -0.45216 | -0.08943 | 1.3551 | 1.0825 | 1.5347 | 0.077858 | -0.088349 | 122.6412 | 122.6215 | 122.8227 | 122.5722 | -0.21867 | 122.6965 | 122.8638 | 122.6976 | 63.9499 | -123.2381
2376.4062 | 122.8409 | -122.5754 | 0.29297 | 1.4211e-13 | -0.01085 | -0.013291 | -0.045384 | -0.04107 | -0.011284 | -0.0084697 | -0.016649 | 0.0095932 | 0.035136 | 0.0084487 | 0.038411 | 0.005626 | 0.019721 | 0.005325 | 0.10707 | 0.08278 | 0.27932 | 0.0331 | -121.1745 | -58.7033 | -121.4563 | 0.15776 | 0.31132 | 0.15884 | -122.9909 | 122.6085 | -0.1859 | 122.581 | 122.5807 | -0.027775 | -0.21019 | -0.013645 | -0.41554 | -0.1352 | 1.4009 | 1.1191 | 1.5347 | 0.018347 | -0.13412 | 122.6824 | 122.6582 | 122.8547 | 122.5951 | -0.25987 | 122.7331 | 122.8867 | 122.7342 | 63.8721 | -123.2839
2378.125 | 122.9187 | -122.5525 | 0.26093 | 1.4211e-13 | -0.01085 | -0.013505 | -0.04517 | -0.04107 | -0.011497 | -0.0084697 | -0.016435 | 0.009807 | 0.035136 | 0.0086623 | 0.038624 | 0.010204 | 0.019721 | 0.000747 | 0.10707 | 0.073622 | 0.27475 | 0.051416 | -121.1699 | -58.8773 | -121.4608 | 0.15776 | 0.31589 | 0.15427 | -122.9909 | 122.6039 | -0.15386 | 122.5627 | 122.5532 | -0.050669 | -0.1873 | 0.01382 | -0.43843 | -0.10316 | 1.3826 | 1.0916 | 1.5301 | 0.054969 | -0.10666 | 122.6596 | 122.6261 | 122.8272 | 122.5722 | -0.20951 | 122.7103 | 122.8684 | 122.7068 | 63.6752 | -123.2518
2379.9062 | 122.9691 | -122.5479 | 0.23346 | 1.4211e-13 | -0.010637 | -0.013505 | -0.045384 | -0.040857 | -0.011497 | -0.0084697 | -0.016649 | 0.009166 | 0.035136 | 0.0086623 | 0.038838 | 0.001048 | 0.019721 | 0.014482 | 0.10249 | 0.073622 | 0.27932 | 0.042258 | -121.1608 | -59.0009 | -121.4425 | 0.14861 | 0.31589 | 0.14969 | -122.9955 | 122.5902 | -0.13097 | 122.549 | 122.5624 | -0.027776 | -0.15984 | 0.045865 | -0.44759 | -0.084852 | 1.3871 | 1.1054 | 1.553 | 0.082435 | -0.083772 | 122.6504 | 122.6215 | 122.8272 | 122.5676 | -0.1912 | 122.6965 | 122.8638 | 122.6976 | 63.547 | -123.229
2381.6875 | 122.8409 | -122.5708 | 0.29755 | 1.4211e-13 | -0.010423 | -0.013077 | -0.04517 | -0.040643 | -0.011284 | 0.0067908 | -0.016649 | 0.0095932 | 0.03535 | 0.0086623 | 0.038838 | 0.005626 | 0.028878 | 0.005325 | 0.10249 | 0.073622 | 0.27932 | 0.037679 | -121.1516 | -59.1657 | -121.4517 | 0.14861 | 0.31589 | 0.15427 | -122.9909 | 122.6085 | -0.19506 | 122.5764 | 122.5761 | -0.032354 | -0.22392 | -0.018222 | -0.42012 | -0.14894 | 1.4192 | 1.1191 | 1.5392 | 0.018348 | -0.14328 | 122.6733 | 122.6444 | 122.8501 | 122.5997 | -0.25987 | 122.7194 | 122.8867 | 122.7251 | 63.4051 | -123.2885
2383.4688 | 122.9782 | -122.525 | 0.25635 | 1.4211e-13 | -0.01085 | -0.013505 | -0.04517 | -0.040857 | -0.011497 | -0.00083919 | -0.016222 | 0.0093796 | 0.035136 | 0.0086623 | 0.038411 | 0.014783 | 0.019721 | 0.009904 | 0.11165 | 0.073622 | 0.27932 | 0.051416 | -121.1379 | -59.2848 | -121.4288 | 0.15318 | 0.31589 | 0.14511 | -122.9909 | 122.5764 | -0.1447 | 122.5398 | 122.5349 | -0.041512 | -0.18273 | 0.022976 | -0.4659 | -0.10316 | 1.3871 | 1.0962 | 1.5621 | 0.059546 | -0.11124 | 122.6367 | 122.5986 | 122.8043 | 122.5447 | -0.20493 | 122.6782 | 122.8409 | 122.6701 | 63.2402 | -123.2473
2385.1875 | 122.9004 | -122.5616 | 0.2655 | 1.4211e-13 | -0.010423 | -0.013077 | -0.045598 | -0.040857 | -0.011711 | -0.0084697 | -0.016222 | 0.0095932 | 0.034923 | 0.0090897 | 0.038411 | 0.014783 | 0.0243 | 0.000747 | 0.10249 | 0.069043 | 0.27475 | 0.037679 | -121.1287 | -59.4313 | -121.4334 | 0.16234 | 0.30674 | 0.14511 | -123.0001 | 122.5993 | -0.16301 | 122.5764 | 122.5624 | -0.036932 | -0.19646 | 0.009242 | -0.43843 | -0.10316 | 1.4329 | 1.1283 | 1.5667 | 0.041234 | -0.12039 | 122.6641 | 122.6307 | 122.8364 | 122.5859 | -0.22782 | 122.724 | 122.8684 | 122.7068 | 63.1304 | -123.2656
2386.9688 | 122.9965 | -122.5479 | 0.24719 | 1.4211e-13 | -0.010423 | -0.013077 | -0.045384 | -0.04107 | -0.011284 | -0.00083919 | -0.016222 | 0.0095932 | 0.035136 | 0.0090897 | 0.038624 | 0.010204 | 0.015142 | 0.005325 | 0.10249 | 0.078201 | 0.27475 | 0.042258 | -121.1241 | -59.6099 | -121.4196 | 0.15318 | 0.31589 | 0.14969 | -122.9955 | 122.5902 | -0.1447 | 122.5581 | 122.5532 | -0.036933 | -0.16899 | 0.027553 | -0.44759 | -0.094007 | 1.4238 | 1.1283 | 1.5759 | 0.068702 | -0.097505 | 122.6504 | 122.6261 | 122.8227 | 122.5631 | -0.20493 | 122.7011 | 122.8638 | 122.6976 | 62.938 | -123.2427
2388.75 | 122.9324 | -122.5388 | 0.24261 | 1.4211e-13 | -0.010637 | -0.013291 | -0.045384 | -0.040643 | -0.011711 | 0.0067908 | -0.016222 | 0.009807 | 0.035136 | 0.0088761 | 0.038411 | 0.014783 | 0.019721 | 0.009904 | 0.11165 | 0.078201 | 0.2839 | 0.051416 | -121.1058 | -59.8342 | -121.4105 | 0.15318 | 0.31589 | 0.14511 | -122.9909 | 122.5902 | -0.13097 | 122.5535 | 122.5487 | -0.041512 | -0.16441 | 0.041288 | -0.45216 | -0.08943 | 1.4329 | 1.1283 | 1.5804 | 0.073279 | -0.097506 | 122.6504 | 122.617 | 122.8227 | 122.5585 | -0.1912 | 122.6919 | 122.8547 | 122.6839 | 62.7045 | -123.2335
2390.5625 | 122.9095 | -122.5616 | 0.27924 | 1.4211e-13 | -0.010637 | -0.013077 | -0.04517 | -0.040857 | -0.011284 | -0.0084697 | -0.016222 | 0.0095932 | 0.035136 | 0.0088761 | 0.038624 | -0.003531 | 0.019721 | 0.009904 | 0.11165 | 0.069043 | 0.27475 | 0.042258 | -121.1012 | -60.0174 | -121.4013 | 0.15776 | 0.31589 | 0.15427 | -122.9909 | 122.6039 | -0.16759 | 122.5581 | 122.5716 | -0.032354 | -0.21019 | -0.004491 | -0.42927 | -0.12147 | 1.4604 | 1.1603 | 1.5896 | 0.036658 | -0.12497 | 122.6733 | 122.6307 | 122.8364 | 122.5814 | -0.23698 | 122.7194 | 122.8775 | 122.7159 | 62.5443 | -123.2702
2392.2812 | 122.8729 | -122.58 | 0.27466 | 1.4211e-13 | -0.011064 | -0.013505 | -0.045384 | -0.040857 | -0.011497 | -0.00083919 | -0.016649 | 0.0095932 | 0.035136 | 0.0086623 | 0.038838 | 0.005626 | 0.019721 | 0.000747 | 0.10707 | 0.069043 | 0.27932 | 0.028521 | -121.0875 | -60.1914 | -121.3922 | 0.15318 | 0.31132 | 0.14969 | -122.9955 | 122.6085 | -0.16759 | 122.5856 | 122.5807 | -0.027774 | -0.20562 | 0.004666 | -0.41554 | -0.12147 | 1.4924 | 1.1878 | 1.6033 | 0.036658 | -0.12497 | 122.687 | 122.649 | 122.8593 | 122.5997 | -0.24614 | 122.7331 | 122.8913 | 122.7296 | 62.3886 | -123.2702
2394.0625 | 122.9324 | -122.5296 | 0.24719 | 1.4211e-13 | -0.010637 | -0.013291 | -0.044957 | -0.040643 | -0.011284 | 0.0067908 | -0.016863 | 0.0093796 | 0.034923 | 0.0086623 | 0.039052 | 0.010204 | 0.019721 | 0.005325 | 0.10707 | 0.078201 | 0.27932 | 0.046837 | -121.0829 | -60.3791 | -121.3967 | 0.15318 | 0.31132 | 0.15884 | -123.0001 | 122.5764 | -0.14012 | 122.5398 | 122.5349 | -0.041512 | -0.16899 | 0.032132 | -0.47048 | -0.094007 | 1.4467 | 1.1329 | 1.6033 | 0.064124 | -0.088347 | 122.6367 | 122.6078 | 122.8089 | 122.5493 | -0.20036 | 122.6828 | 122.8409 | 122.6884 | 62.1505 | -123.2473
2395.8438 | 122.9507 | -122.5342 | 0.25635 | 1.4211e-13 | -0.010637 | -0.013505 | -0.045384 | -0.040643 | -0.011497 | -0.00083919 | -0.016649 | 0.0093796 | 0.035136 | 0.0086623 | 0.039052 | 0.010204 | 0.0243 | 0.005325 | 0.10707 | 0.078201 | 0.27932 | 0.028521 | -121.0646 | -60.5256 | -121.383 | 0.14861 | 0.31132 | 0.16342 | -123.0001 | 122.5627 | -0.14928 | 122.5444 | 122.5395 | -0.023196 | -0.17815 | 0.022976 | -0.4659 | -0.10774 | 1.4696 | 1.1512 | 1.6171 | 0.054968 | -0.092925 | 122.6412 | 122.6124 | 122.8135 | 122.5585 | -0.22783 | 122.6828 | 122.8455 | 122.6976 | 62.0086 | -123.2564
2397.6406 | 122.937 | -122.5433 | 0.2655 | 1.4211e-13 | -0.010637 | -0.013505 | -0.04517 | -0.04107 | -0.011711 | -0.0084697 | -0.016435 | 0.009807 | 0.035136 | 0.0086623 | 0.038838 | 0.010204 | 0.015142 | 0.005325 | 0.11165 | 0.078201 | 0.27932 | 0.028521 | -121.0646 | -60.6859 | -121.3738 | 0.16234 | 0.31589 | 0.14969 | -122.9909 | 122.5719 | -0.15386 | 122.5535 | 122.5487 | -0.023196 | -0.1873 | 0.013821 | -0.44759 | -0.10316 | 1.4787 | 1.1695 | 1.6171 | 0.050391 | -0.11582 | 122.655 | 122.6215 | 122.8227 | 122.5585 | -0.23698 | 122.7057 | 122.8592 | 122.693 | 61.8575 | -123.2564
2399.375 | 122.9324 | -122.5388 | 0.23804 | 1.4211e-13 | -0.01085 | -0.013505 | -0.04517 | -0.04107 | -0.011711 | 0.0067908 | -0.016649 | 0.009807 | 0.035136 | 0.0088761 | 0.039052 | 0.010204 | 0.0243 | 0.005325 | 0.11165 | 0.073622 | 0.27475 | 0.046837 | -121.0463 | -60.8324 | -121.3693 | 0.15776 | 0.31589 | 0.14511 | -122.9863 | 122.5856 | -0.12639 | 122.549 | 122.5441 | -0.041512 | -0.16441 | 0.036708 | -0.44758 | -0.080273 | 1.4925 | 1.1695 | 1.6171 | 0.077857 | -0.092928 | 122.6504 | 122.6124 | 122.8135 | 122.5631 | -0.1912 | 122.6965 | 122.8547 | 122.6839 | 61.7064 | -123.2244
2401.1719 | 122.9691 | -122.5616 | 0.26093 | 1.4211e-13 | -0.01085 | -0.013505 | -0.04517 | -0.040857 | -0.01107 | -0.00083919 | -0.016649 | 0.0093796 | 0.03535 | 0.0084487 | 0.039052 | 0.014783 | 0.0243 | 0.009904 | 0.10707 | 0.08278 | 0.28848 | 0.037679 | -121.0371 | -60.9789 | -121.3601 | 0.15318 | 0.31589 | 0.15427 | -123.0001 | 122.5993 | -0.15386 | 122.5764 | 122.5716 | -0.027775 | -0.17814 | 0.027556 | -0.43843 | -0.10774 | 1.5245 | 1.2015 | 1.64 | 0.054969 | -0.10666 | 122.6687 | 122.6444 | 122.8501 | 122.5859 | -0.22325 | 122.7148 | 122.8775 | 122.7159 | 61.5827 | -123.261
2402.9062 | 122.9141 | -122.5296 | 0.2655 | 1.4211e-13 | -0.010637 | -0.013077 | -0.045598 | -0.04107 | -0.011711 | 0.0067908 | -0.016222 | 0.0095932 | 0.034923 | 0.0086623 | 0.038411 | 0.010204 | 0.0243 | 0.005325 | 0.10707 | 0.08278 | 0.27475 | 0.028521 | -121.028 | -61.1712 | -121.351 | 0.14861 | 0.30674 | 0.15427 | -122.9955 | 122.5581 | -0.15843 | 122.5398 | 122.5349 | -0.023196 | -0.18272 | 0.009242 | -0.4659 | -0.1169 | 1.5016 | 1.1786 | 1.6445 | 0.041234 | -0.11124 | 122.6367 | 122.6124 | 122.8043 | 122.5539 | -0.23698 | 122.6782 | 122.8363 | 122.6839 | 61.3584 | -123.261
2404.6875 | 122.8958 | -122.5983 | 0.28839 | 1.4211e-13 | -0.010637 | -0.013291 | -0.045598 | -0.04107 | -0.011284 | -0.00083919 | -0.016008 | 0.010021 | 0.03535 | 0.0088761 | 0.038624 | 0.014783 | 0.015142 | 0.005325 | 0.10707 | 0.073622 | 0.27932 | 0.028521 | -121.0143 | -61.3315 | -121.3372 | 0.15318 | 0.31132 | 0.14511 | -122.9955 | 122.6268 | -0.18132 | 122.6131 | 122.6036 | -0.023196 | -0.21477 | -0.009067 | -0.39723 | -0.13521 | 1.584 | 1.261 | 1.6583 | 0.022925 | -0.14328 | 122.7053 | 122.6719 | 122.8776 | 122.6134 | -0.25987 | 122.7515 | 122.9096 | 122.7434 | 61.2668 | -123.2839
2406.4688 | 122.8546 | -122.5754 | 0.27466 | 1.4211e-13 | -0.010637 | -0.013077 | -0.044957 | -0.040857 | -0.011497 | -0.00083919 | -0.016435 | 0.0093796 | 0.03535 | 0.0088761 | 0.038838 | 0.001048 | 0.019721 | 0.000747 | 0.097912 | 0.078201 | 0.27475 | 0.028521 | -121.0143 | -61.4688 | -121.3372 | 0.15318 | 0.30674 | 0.14511 | -122.9955 | 122.6039 | -0.17675 | 122.5764 | 122.5761 | -0.027774 | -0.19646 | 8.7e-05 | -0.42012 | -0.12147 | 1.5611 | 1.2382 | 1.6583 | 0.032079 | -0.12955 | 122.6733 | 122.6536 | 122.8501 | 122.5951 | -0.24614 | 122.7286 | 122.8821 | 122.7205 | 61.1066 | -123.2702
2408.1875 | 122.8363 | -122.58 | 0.28381 | 1.4211e-13 | -0.010637 | -0.013291 | -0.045384 | -0.04107 | -0.011711 | -0.00083919 | -0.016222 | 0.0093796 | 0.035136 | 0.0090897 | 0.038624 | 0.005626 | 0.019721 | 0.000747 | 0.10707 | 0.078201 | 0.27475 | 0.028521 | -120.9959 | -61.6016 | -121.3281 | 0.14861 | 0.31132 | 0.14969 | -123.0047 | 122.6085 | -0.17674 | 122.5856 | 122.5807 | -0.027774 | -0.20561 | -0.009068 | -0.4247 | -0.13521 | 1.584 | 1.2519 | 1.6766 | 0.027503 | -0.13413 | 122.687 | 122.6582 | 122.8547 | 122.5997 | -0.25529 | 122.7286 | 122.8913 | 122.7296 | 60.9784 | -123.2885
2409.9688 | 122.8409 | -122.58 | 0.27008 | 1.4211e-13 | -0.01085 | -0.013291 | -0.04517 | -0.040857 | -0.011711 | -0.0161 | -0.016649 | 0.009807 | 0.034923 | 0.0088761 | 0.038838 | 0.005626 | 0.019721 | 0.009904 | 0.10707 | 0.078201 | 0.27017 | 0.023942 | -120.9868 | -61.7802 | -121.3097 | 0.15318 | 0.30216 | 0.14969 | -122.9909 | 122.6039 | -0.16301 | 122.5856 | 122.5899 | -0.014038 | -0.19188 | 8.6e-05 | -0.41096 | -0.1169 | 1.5932 | 1.2702 | 1.6812 | 0.032077 | -0.12039 | 122.687 | 122.6582 | 122.8501 | 122.5997 | -0.24614 | 122.7331 | 122.8821 | 122.7296 | 60.7998 | -123.261
2411.7656 | 122.8317 | -122.58 | 0.27924 | 1.4211e-13 | -0.010637 | -0.013291 | -0.04517 | -0.04107 | -0.011497 | -0.0084697 | -0.016222 | 0.0095932 | 0.035136 | 0.0088761 | 0.038624 | 0.019361 | 0.015142 | 0.000747 | 0.11165 | 0.073622 | 0.27932 | 0.0331 | -120.973 | -61.8901 | -121.3006 | 0.15318 | 0.31132 | 0.15427 | -122.9955 | 122.6131 | -0.16759 | 122.5993 | 122.5807 | -0.032353 | -0.20561 | 8.8e-05 | -0.41554 | -0.12605 | 1.6069 | 1.2794 | 1.6949 | 0.03208 | -0.12497 | 122.6916 | 122.6536 | 122.8593 | 122.5951 | -0.24614 | 122.7331 | 122.8913 | 122.7342 | 60.6899 | -123.2747
2413.4844 | 122.8592 | -122.5937 | 0.27008 | 1.4211e-13 | -0.010637 | -0.013505 | -0.04517 | -0.040857 | -0.011711 | -0.00083919 | -0.016435 | 0.0095932 | 0.035136 | 0.0090897 | 0.038838 | 0.010204 | 0.0243 | 0.005325 | 0.10707 | 0.069043 | 0.27475 | 0.0331 | -120.9685 | -62.0183 | -121.3052 | 0.15776 | 0.30216 | 0.14053 | -123.0001 | 122.6268 | -0.16301 | 122.6039 | 122.599 | -0.027775 | -0.20104 | 0.004664 | -0.40639 | -0.11232 | 1.6252 | 1.2885 | 1.6949 | 0.032077 | -0.12955 | 122.7008 | 122.6627 | 122.8684 | 122.618 | -0.23698 | 122.7515 | 122.8958 | 122.7342 | 60.5754 | -123.2702
2415.2812 | 122.937 | -122.5388 | 0.2655 | 1.4211e-13 | -0.011064 | -0.013291 | -0.04517 | -0.04107 | -0.011284 | 0.0067908 | -0.016222 | 0.009807 | 0.035136 | 0.0086623 | 0.038624 | 0.010204 | 0.0243 | 0.009904 | 0.10707 | 0.069043 | 0.27932 | 0.028521 | -120.9593 | -62.1282 | -121.2823 | 0.15318 | 0.30216 | 0.15427 | -123.0092 | 122.5673 | -0.15843 | 122.549 | 122.5487 | -0.018617 | -0.19646 | 0.013821 | -0.47048 | -0.11232 | 1.5794 | 1.2565 | 1.727 | 0.036655 | -0.11124 | 122.6458 | 122.6078 | 122.8181 | 122.5631 | -0.23698 | 122.6919 | 122.8409 | 122.693 | 60.4106 | -123.2747
2417.0156 | 122.9874 | -122.5479 | 0.24261 | 1.4211e-13 | -0.01085 | -0.013291 | -0.04517 | -0.040857 | -0.011497 | 0.0067908 | -0.016222 | 0.009807 | 0.035136 | 0.0088761 | 0.038624 | 0.005626 | 0.0243 | 0.009904 | 0.10707 | 0.078201 | 0.27932 | 0.051416 | -120.9456 | -62.325 | -121.2731 | 0.15318 | 0.31132 | 0.14053 | -123.0047 | 122.5993 | -0.13555 | 122.5535 | 122.5578 | -0.041512 | -0.16441 | 0.036709 | -0.45674 | -0.08943 | 1.6023 | 1.2748 | 1.7315 | 0.068701 | -0.10209 | 122.655 | 122.6261 | 122.8272 | 122.5722 | -0.1912 | 122.7011 | 122.8592 | 122.6884 | 60.2229 | -123.2473
2418.7969 | 122.8409 | -122.5891 | 0.28381 | 1.4211e-13 | -0.01085 | -0.013291 | -0.04517 | -0.04107 | -0.011497 | -0.00083919 | -0.016222 | 0.009807 | 0.03535 | 0.0090897 | 0.038838 | 0.005626 | 0.019721 | 0.005325 | 0.10707 | 0.078201 | 0.2839 | 0.019363 | -120.9364 | -62.4487 | -121.264 | 0.14861 | 0.31589 | 0.15427 | -123.0001 | 122.6085 | -0.17674 | 122.5947 | 122.5944 | -0.014038 | -0.20561 | 9e-05 | -0.41097 | -0.13521 | 1.6527 | 1.3252 | 1.7361 | 0.032081 | -0.12955 | 122.6962 | 122.6673 | 122.873 | 122.6088 | -0.26445 | 122.7377 | 122.905 | 122.7434 | 60.1404 | -123.2839
2420.6094 | 122.8821 | -122.5937 | 0.28381 | 1.4211e-13 | -0.01085 | -0.012863 | -0.045598 | -0.040643 | -0.011497 | -0.00083919 | -0.016435 | 0.009807 | 0.035136 | 0.0088761 | 0.038624 | 0.005626 | 0.015142 | 0.005325 | 0.11165 | 0.069043 | 0.2839 | 0.023942 | -120.9135 | -62.6089 | -121.2731 | 0.13945 | 0.31132 | 0.15427 | -123.0001 | 122.6176 | -0.17217 | 122.5993 | 122.599 | -0.018617 | -0.21477 | 9e-05 | -0.40639 | -0.14436 | 1.6802 | 1.3206 | 1.727 | 0.027503 | -0.12955 | 122.7053 | 122.6627 | 122.8776 | 122.6088 | -0.25987 | 122.7331 | 122.905 | 122.748 | 59.9848 | -123.2839
2422.3281 | 122.8912 | -122.58 | 0.27008 | 1.4211e-13 | -0.010637 | -0.013505 | -0.04517 | -0.040643 | -0.011924 | 0.0067908 | -0.016008 | 0.0095932 | 0.035136 | 0.0086623 | 0.039052 | 0.010204 | 0.0243 | 0.000747 | 0.10249 | 0.078201 | 0.27932 | 0.037679 | -120.9227 | -62.8104 | -121.2548 | 0.14861 | 0.30674 | 0.14053 | -123.0047 | 122.6176 | -0.16759 | 122.5902 | 122.5807 | -0.036932 | -0.19188 | 0.009243 | -0.4247 | -0.12147 | 1.6573 | 1.3252 | 1.7499 | 0.036656 | -0.12955 | 122.6824 | 122.6582 | 122.8593 | 122.6043 | -0.2324 | 122.7286 | 122.8867 | 122.7205 | 59.7696 | -123.2747
2424.125 | 122.8455 | -122.5937 | 0.27924 | 1.4211e-13 | -0.011278 | -0.013505 | -0.04517 | -0.040857 | -0.011284 | -0.0084697 | -0.016008 | 0.0095932 | 0.035136 | 0.0088761 | 0.038624 | 0.005626 | 0.019721 | 0.009904 | 0.10707 | 0.078201 | 0.27932 | 0.042258 | -120.9044 | -62.9386 | -121.2502 | 0.14861 | 0.31132 | 0.14053 | -122.9955 | 122.6359 | -0.17217 | 122.5993 | 122.6036 | -0.032354 | -0.20103 | 8.8e-05 | -0.40181 | -0.13063 | 1.6893 | 1.3435 | 1.7453 | 0.03208 | -0.13871 | 122.7008 | 122.6719 | 122.873 | 122.6134 | -0.23698 | 122.7423 | 122.905 | 122.7342 | 59.6551 | -123.2747
2425.9219 | 122.8592 | -122.5983 | 0.27466 | 1.4211e-13 | -0.011064 | -0.013505 | -0.044957 | -0.04107 | -0.011497 | -0.00083919 | -0.016008 | 0.0093796 | 0.03535 | 0.0088761 | 0.039052 | 0.001048 | 0.019721 | 0.009904 | 0.10707 | 0.078201 | 0.2839 | 0.028521 | -120.8906 | -63.0759 | -121.2411 | 0.14861 | 0.31132 | 0.13595 | -123.0092 | 122.6268 | -0.16759 | 122.5993 | 122.6082 | -0.018617 | -0.19646 | 0.009245 | -0.41097 | -0.12605 | 1.7076 | 1.3572 | 1.7682 | 0.036658 | -0.13871 | 122.7053 | 122.6765 | 122.8822 | 122.618 | -0.24614 | 122.7469 | 122.9096 | 122.7342 | 59.5223 | -123.2839
2427.7031 | 122.8546 | -122.5845 | 0.27924 | 1.4211e-13 | -0.01085 | -0.013077 | -0.04517 | -0.040857 | -0.011497 | -0.00083919 | -0.016008 | 0.0095932 | 0.034923 | 0.0088761 | 0.038624 | 0.005626 | 0.0243 | 0.005325 | 0.10707 | 0.078201 | 0.27475 | 0.037679 | -120.8723 | -63.2545 | -121.2228 | 0.14861 | 0.30216 | 0.14053 | -123.0092 | 122.6222 | -0.17217 | 122.5902 | 122.5899 | -0.032354 | -0.20103 | -0.004491 | -0.4247 | -0.13063 | 1.7122 | 1.3618 | 1.7865 | 0.022922 | -0.13871 | 122.6916 | 122.6627 | 122.8593 | 122.6088 | -0.24156 | 122.7331 | 122.8867 | 122.7251 | 59.33 | -123.2885
2429.4219 | 122.8363 | -122.5891 | 0.29297 | 1.4211e-13 | -0.01085 | -0.013505 | -0.045598 | -0.04107 | -0.011497 | -0.00083919 | -0.016435 | 0.0095932 | 0.035136 | 0.0090897 | 0.038838 | 0.010204 | 0.015142 | 0.000747 | 0.10707 | 0.078201 | 0.27932 | 0.019363 | -120.8677 | -63.3781 | -121.2182 | 0.14861 | 0.31132 | 0.14511 | -123.0138 | 122.6085 | -0.1859 | 122.5993 | 122.5899 | -0.018616 | -0.21477 | -0.013645 | -0.4247 | -0.14436 | 1.7214 | 1.3709 | 1.7956 | 0.018347 | -0.14786 | 122.6962 | 122.6673 | 122.8684 | 122.6043 | -0.27361 | 122.7377 | 122.9004 | 122.7342 | 59.211 | -123.3068
2431.2188 | 122.9095 | -122.5754 | 0.27466 | 1.4211e-13 | -0.011064 | -0.013077 | -0.045384 | -0.040857 | -0.011711 | -0.00083919 | -0.016008 | 0.0093796 | 0.03535 | 0.0090897 | 0.038838 | 0.010204 | 0.028878 | 0.005325 | 0.11165 | 0.078201 | 0.2839 | 0.028521 | -120.8494 | -63.5521 | -121.2182 | 0.14861 | 0.30674 | 0.15884 | -123.0047 | 122.6039 | -0.16301 | 122.5856 | 122.5807 | -0.023196 | -0.19646 | 0.009245 | -0.42928 | -0.12605 | 1.726 | 1.3572 | 1.7865 | 0.032079 | -0.11581 | 122.687 | 122.6536 | 122.8593 | 122.6043 | -0.24614 | 122.724 | 122.8821 | 122.7342 | 59.0232 | -123.2793
2433.0156 | 122.905 | -122.58 | 0.25177 | 1.4211e-13 | -0.011064 | -0.012863 | -0.045384 | -0.041284 | -0.011924 | -0.0161 | -0.015794 | 0.009807 | 0.034923 | 0.0093033 | 0.038838 | 0.010204 | 0.019721 | 0.009904 | 0.11165 | 0.069043 | 0.27932 | 0.042258 | -120.8403 | -63.6758 | -121.1999 | 0.14403 | 0.30674 | 0.14511 | -123.0092 | 122.6222 | -0.14012 | 122.5902 | 122.5899 | -0.032354 | -0.18273 | 0.027554 | -0.42928 | -0.10774 | 1.7397 | 1.3801 | 1.8094 | 0.054967 | -0.10666 | 122.6916 | 122.649 | 122.8593 | 122.5997 | -0.20951 | 122.724 | 122.8867 | 122.7251 | 58.9042 | -123.261
2434.7344 | 122.8683 | -122.5662 | 0.27466 | 1.4211e-13 | -0.011064 | -0.013077 | -0.045384 | -0.04107 | -0.011284 | -0.00083919 | -0.016435 | 0.0095932 | 0.035136 | 0.0095171 | 0.038838 | 0.010204 | 0.019721 | 0.005325 | 0.11165 | 0.073622 | 0.2839 | 0.010206 | -120.8311 | -63.836 | -121.1861 | 0.15776 | 0.31132 | 0.14511 | -123.0138 | 122.5764 | -0.16301 | 122.5764 | 122.5715 | -0.004881 | -0.20104 | 0.009245 | -0.44759 | -0.11689 | 1.7351 | 1.3801 | 1.8277 | 0.036658 | -0.12955 | 122.6779 | 122.6398 | 122.8501 | 122.5859 | -0.26445 | 122.724 | 122.8775 | 122.7113 | 58.7302 | -123.2885
2436.5469 | 122.8729 | -122.58 | 0.2655 | 1.4211e-13 | -0.011064 | -0.013505 | -0.04517 | -0.041498 | -0.011497 | -0.0084697 | -0.016222 | 0.010021 | 0.03535 | 0.0090897 | 0.038838 | 0.005626 | 0.019721 | 0.000747 | 0.10249 | 0.069043 | 0.2839 | 0.014784 | -120.8174 | -63.9963 | -121.177 | 0.13945 | 0.30216 | 0.14511 | -123.0092 | 122.5947 | -0.16301 | 122.5856 | 122.5807 | -0.014037 | -0.19646 | 0.0184 | -0.42928 | -0.12605 | 1.7626 | 1.403 | 1.8323 | 0.036655 | -0.12039 | 122.6824 | 122.649 | 122.8639 | 122.5997 | -0.25072 | 122.7194 | 122.8821 | 122.7251 | 58.5837 | -123.2747
2438.3281 | 122.9919 | -122.5479 | 0.2243 | 1.4211e-13 | -0.011491 | -0.013505 | -0.045598 | -0.04107 | -0.011497 | -0.0084697 | -0.016008 | 0.010021 | 0.03535 | 0.0090897 | 0.038838 | 0.014783 | 0.019721 | 0.009904 | 0.11165 | 0.073622 | 0.28848 | 0.042258 | -120.7945 | -64.1565 | -121.1632 | 0.14403 | 0.30674 | 0.14511 | -123.0138 | 122.5902 | -0.11266 | 122.5627 | 122.5578 | -0.032354 | -0.15068 | 0.064177 | -0.4659 | -0.080276 | 1.7534 | 1.3847 | 1.8506 | 0.082433 | -0.079195 | 122.6596 | 122.6215 | 122.8364 | 122.5676 | -0.18205 | 122.6919 | 122.8546 | 122.693 | 58.3914 | -123.2381
2440.1094 | 122.9416 | -122.5662 | 0.23804 | 1.4211e-13 | -0.011064 | -0.013077 | -0.045384 | -0.040857 | -0.011497 | 0.0067908 | -0.016008 | 0.0095932 | 0.03535 | 0.0090897 | 0.039052 | 0.010204 | 0.0243 | 0.005325 | 0.11165 | 0.073622 | 0.2839 | 0.0331 | -120.7945 | -64.3351 | -121.1541 | 0.14861 | 0.30216 | 0.14511 | -123.0138 | 122.5993 | -0.12639 | 122.5764 | 122.5715 | -0.027775 | -0.16441 | 0.045866 | -0.44759 | -0.08943 | 1.7717 | 1.4122 | 1.8597 | 0.064121 | -0.092928 | 122.6779 | 122.6398 | 122.8501 | 122.5905 | -0.20494 | 122.7148 | 122.8684 | 122.7113 | 58.2311 | -123.2519
2441.8906 | 122.9233 | -122.6028 | 0.28381 | 1.4211e-13 | -0.01085 | -0.013291 | -0.045384 | -0.040857 | -0.011497 | -0.00083919 | -0.016649 | 0.0095932 | 0.035136 | 0.0090897 | 0.039265 | 0.005626 | 0.019721 | 0.005325 | 0.10707 | 0.073622 | 0.27932 | 0.037679 | -120.7716 | -64.4908 | -121.1358 | 0.14403 | 0.30674 | 0.14511 | -123.0138 | 122.6405 | -0.17674 | 122.6085 | 122.6082 | -0.032354 | -0.21019 | -0.004489 | -0.41097 | -0.13978 | 1.8313 | 1.4671 | 1.8781 | 0.022924 | -0.1387 | 122.7099 | 122.6765 | 122.8822 | 122.6226 | -0.24613 | 122.7469 | 122.9096 | 122.748 | 58.1121 | -123.2976
2443.6719 | 123.0057 | -122.5388 | 0.24261 | 1.4211e-13 | -0.011278 | -0.013077 | -0.045384 | -0.04107 | -0.011497 | 0.0067908 | -0.016222 | 0.009807 | 0.034923 | 0.0093033 | 0.039052 | 0.010204 | 0.0243 | 0.005325 | 0.10707 | 0.08278 | 0.27475 | 0.037679 | -120.7533 | -64.6144 | -121.1266 | 0.14403 | 0.30216 | 0.14053 | -123.023 | 122.5764 | -0.13555 | 122.549 | 122.5441 | -0.032354 | -0.15984 | 0.03213 | -0.48421 | -0.098587 | 1.7855 | 1.4122 | 1.8964 | 0.059543 | -0.10209 | 122.6458 | 122.6215 | 122.8135 | 122.5631 | -0.20494 | 122.6828 | 122.8409 | 122.6793 | 57.9244 | -123.2656
2445.4062 | 122.9095 | -122.58 | 0.27008 | 1.4211e-13 | -0.011278 | -0.013718 | -0.04517 | -0.041284 | -0.011924 | 0.0067908 | -0.016222 | 0.0095932 | 0.03535 | 0.0093033 | 0.039052 | 0.005626 | 0.0243 | 0.009904 | 0.11165 | 0.078201 | 0.27932 | 0.019363 | -120.735 | -64.7243 | -121.1174 | 0.15318 | 0.30216 | 0.14053 | -123.0138 | 122.5993 | -0.15843 | 122.5856 | 122.5899 | -0.009459 | -0.19188 | 0.009243 | -0.43386 | -0.1169 | 1.845 | 1.4625 | 1.8964 | 0.032077 | -0.12955 | 122.6916 | 122.6582 | 122.8593 | 122.6043 | -0.25072 | 122.7331 | 122.8821 | 122.7205 | 57.8557 | -123.2839
2447.2031 | 122.9187 | -122.5662 | 0.27008 | 1.4211e-13 | -0.011278 | -0.013291 | -0.045384 | -0.040857 | -0.011497 | 0.0067908 | -0.016008 | 0.010021 | 0.035136 | 0.0088761 | 0.039052 | 0.005626 | 0.0243 | 0.005325 | 0.10249 | 0.078201 | 0.27475 | 0.046837 | -120.7304 | -64.8204 | -121.1129 | 0.13945 | 0.30216 | 0.14511 | -123.0184 | 122.6131 | -0.16759 | 122.5718 | 122.5715 | -0.041512 | -0.19188 | 0.004664 | -0.45217 | -0.13063 | 1.8358 | 1.4534 | 1.9055 | 0.032077 | -0.12497 | 122.6687 | 122.6444 | 122.841 | 122.5905 | -0.22324 | 122.7057 | 122.8684 | 122.7113 | 57.7458 | -123.2885
2448.9844 | 122.8912 | -122.5983 | 0.27466 | 1.4211e-13 | -0.011278 | -0.013291 | -0.044957 | -0.04107 | -0.011497 | -0.00083919 | -0.016222 | 0.009807 | 0.035136 | 0.0090897 | 0.039265 | 0.005626 | 0.028878 | 0.005325 | 0.10707 | 0.073622 | 0.27932 | 0.042258 | -120.7166 | -65.0082 | -121.0991 | 0.14403 | 0.31589 | 0.13595 | -123.0184 | 122.6405 | -0.16759 | 122.6039 | 122.6036 | -0.036933 | -0.20104 | 0.004666 | -0.42013 | -0.13063 | 1.8816 | 1.4991 | 1.9193 | 0.041236 | -0.13871 | 122.7053 | 122.6719 | 122.8776 | 122.6271 | -0.2324 | 122.7423 | 122.9142 | 122.7342 | 57.5901 | -123.2931
2450.6875 | 122.9187 | -122.5479 | 0.25635 | 1.4211e-13 | -0.011278 | -0.013718 | -0.04517 | -0.040857 | -0.011497 | -0.0084697 | -0.016435 | 0.009807 | 0.035136 | 0.0093033 | 0.039265 | 0.014783 | 0.028878 | 0.009904 | 0.11622 | 0.078201 | 0.2839 | 0.014784 | -120.7121 | -65.1501 | -121.0854 | 0.14861 | 0.29758 | 0.14053 | -123.0184 | 122.5627 | -0.14012 | 122.5627 | 122.5578 | -0.00488 | -0.17815 | 0.027555 | -0.47048 | -0.10774 | 1.8359 | 1.4625 | 1.933 | 0.041232 | -0.11582 | 122.6641 | 122.6261 | 122.8318 | 122.5768 | -0.24156 | 122.6965 | 122.8455 | 122.6884 | 57.3978 | -123.2747
2452.6875 | 122.9828 | -122.5571 | 0.24261 | 1.4211e-13 | -0.011064 | -0.013291 | -0.04517 | -0.04107 | -0.011711 | -0.0161 | -0.016222 | 0.0095932 | 0.034923 | 0.0093033 | 0.039052 | 0.010204 | 0.0243 | 0.009904 | 0.10707 | 0.073622 | 0.27475 | 0.023942 | -120.6892 | -65.2829 | -121.0762 | 0.14861 | 0.29758 | 0.13595 | -123.0184 | 122.581 | -0.13555 | 122.5673 | 122.567 | -0.014038 | -0.16899 | 0.03213 | -0.46133 | -0.094008 | 1.8679 | 1.4808 | 1.9422 | 0.054965 | -0.10666 | 122.6641 | 122.6307 | 122.8318 | 122.5814 | -0.21867 | 122.7057 | 122.8546 | 122.693 | 57.2742 | -123.261
2456.5938 | 122.9691 | -122.5845 | 0.24261 | 1.4211e-13 | -0.011491 | -0.013291 | -0.045384 | -0.040857 | -0.011924 | -0.00083919 | -0.016008 | 0.009807 | 0.03535 | 0.0090897 | 0.039052 | 0.010204 | 0.0243 | 0.005325 | 0.10707 | 0.078201 | 0.27932 | 0.028521 | -120.6571 | -65.6354 | -121.0396 | 0.13487 | 0.29758 | 0.14053 | -123.0184 | 122.6131 | -0.13555 | 122.5947 | 122.5899 | -0.023196 | -0.16441 | 0.036709 | -0.43386 | -0.10774 | 1.9274 | 1.5449 | 1.9788 | 0.054965 | -0.10209 | 122.6916 | 122.6627 | 122.8639 | 122.6088 | -0.21409 | 122.7194 | 122.8821 | 122.7251 | 56.9491 | -123.261
2460.1719 | 122.8683 | -122.5845 | 0.27466 | 1.4211e-13 | -0.011278 | -0.013291 | -0.045384 | -0.04107 | -0.011711 | -0.00083919 | -0.016008 | 0.0095932 | 0.03535 | 0.0095171 | 0.038838 | 0.010204 | 0.0243 | 0.000747 | 0.10707 | 0.078201 | 0.2839 | 0.042258 | -120.6296 | -65.8827 | -121.0259 | 0.13029 | 0.30674 | 0.14511 | -123.0276 | 122.6268 | -0.16759 | 122.5947 | 122.5853 | -0.041511 | -0.19646 | 0.009245 | -0.44302 | -0.14437 | 1.9549 | 1.5587 | 2.0017 | 0.032079 | -0.12955 | 122.6916 | 122.6627 | 122.8684 | 122.6088 | -0.2324 | 122.7148 | 122.8913 | 122.7296 | 56.7018 | -123.3022
2465.9375 | 122.8683 | -122.5891 | 0.27008 | 1.4211e-13 | -0.011278 | -0.013291 | -0.045384 | -0.041284 | -0.011497 | -0.0084697 | -0.016435 | 0.009807 | 0.035136 | 0.0093033 | 0.038838 | 0.005626 | 0.019721 | 0.005325 | 0.11165 | 0.069043 | 0.27932 | 0.046837 | -120.5839 | -66.3085 | -120.9847 | 0.14403 | 0.28842 | 0.13595 | -123.0276 | 122.6359 | -0.15843 | 122.5947 | 122.5944 | -0.041512 | -0.20104 | 0.009243 | -0.43844 | -0.12605 | 2.0053 | 1.6045 | 2.0429 | 0.018342 | -0.13413 | 122.7008 | 122.6582 | 122.8684 | 122.6088 | -0.22324 | 122.7331 | 122.8775 | 122.7251 | 56.2806 | -123.2976
2467.7344 | 122.8729 | -122.6257 | 0.26093 | 1.4211e-13 | -0.011278 | -0.013505 | -0.045598 | -0.04107 | -0.011924 | 0.0067908 | -0.015581 | 0.009807 | 0.035136 | 0.0095171 | 0.039052 | 0.019361 | 0.019721 | 0.005325 | 0.10249 | 0.078201 | 0.2839 | 0.023942 | -120.561 | -66.4688 | -120.9709 | 0.13487 | 0.30216 | 0.13137 | -123.0276 | 122.6497 | -0.15844 | 122.6451 | 122.6311 | -0.018617 | -0.18272 | 0.022978 | -0.40182 | -0.12605 | 2.0648 | 1.6548 | 2.0566 | 0.041233 | -0.12955 | 122.7282 | 122.7039 | 122.9096 | 122.6455 | -0.23698 | 122.7606 | 122.9279 | 122.7571 | 56.157 | -123.2885
2469.5156 | 122.8638 | -122.612 | 0.25177 | 1.4211e-13 | -0.011491 | -0.013718 | -0.045598 | -0.040857 | -0.011711 | 0.014421 | -0.016008 | 0.009807 | 0.03535 | 0.0095171 | 0.039265 | 0.010204 | 0.019721 | 0.009904 | 0.10249 | 0.078201 | 0.28848 | 0.042258 | -120.5472 | -66.6016 | -120.9526 | 0.13945 | 0.293 | 0.14053 | -123.023 | 122.6543 | -0.14928 | 122.6222 | 122.6219 | -0.032354 | -0.17357 | 0.036711 | -0.41097 | -0.11232 | 2.0648 | 1.6594 | 2.0704 | 0.041231 | -0.11124 | 122.7145 | 122.6902 | 122.9005 | 122.6317 | -0.20951 | 122.7514 | 122.905 | 122.7525 | 56.0104 | -123.2747
2471.2344 | 122.9736 | -122.5937 | 0.21973 | 1.4211e-13 | -0.011278 | -0.013291 | -0.045598 | -0.040857 | -0.011711 | -0.00083919 | -0.015794 | 0.009807 | 0.03535 | 0.0093033 | 0.039052 | 0.014783 | 0.019721 | 0.014482 | 0.10707 | 0.078201 | 0.2839 | 0.023942 | -120.5426 | -66.7801 | -120.9343 | 0.14403 | 0.30216 | 0.13595 | -123.0321 | 122.6176 | -0.11266 | 122.6085 | 122.6082 | -0.00946 | -0.14153 | 0.064176 | -0.43844 | -0.075699 | 2.051 | 1.6594 | 2.0978 | 0.082431 | -0.083775 | 122.7008 | 122.6719 | 122.8776 | 122.6134 | -0.19579 | 122.7377 | 122.8958 | 122.7296 | 55.8136 | -123.2519
2473.0469 | 122.8683 | -122.6349 | 0.26093 | 1.4211e-13 | -0.011491 | -0.013505 | -0.04517 | -0.040857 | -0.011711 | 0.0067908 | -0.016435 | 0.010021 | 0.03535 | 0.0093033 | 0.039265 | 0.010204 | 0.0243 | 0.009904 | 0.11165 | 0.073622 | 0.2839 | 0.023942 | -120.5152 | -66.9221 | -120.9297 | 0.13487 | 0.293 | 0.14511 | -123.0367 | 122.6588 | -0.14928 | 122.6451 | 122.6448 | -0.014038 | -0.1873 | 0.022978 | -0.40182 | -0.12605 | 2.1197 | 1.7052 | 2.107 | 0.032076 | -0.11582 | 122.7465 | 122.7085 | 122.9188 | 122.6592 | -0.23698 | 122.7698 | 122.9279 | 122.78 | 55.7128 | -123.2976
2474.8281 | 122.9462 | -122.58 | 0.23346 | 1.4211e-13 | -0.011064 | -0.013505 | -0.04517 | -0.041498 | -0.011497 | -0.00083919 | -0.016222 | 0.009807 | 0.035564 | 0.0095171 | 0.039479 | 0.010204 | 0.019721 | 0.009904 | 0.11165 | 0.08278 | 0.28848 | 0.019363 | -120.4923 | -67.0045 | -120.9022 | 0.13945 | 0.29758 | 0.14053 | -123.0321 | 122.5993 | -0.12181 | 122.5902 | 122.5899 | -0.009459 | -0.15068 | 0.055022 | -0.45217 | -0.094009 | 2.0877 | 1.6777 | 2.1299 | 0.064121 | -0.092929 | 122.6916 | 122.6627 | 122.8684 | 122.5997 | -0.2141 | 122.7194 | 122.8775 | 122.7205 | 55.5755 | -123.2656
2476.6094 | 122.8638 | -122.6074 | 0.2655 | 1.4211e-13 | -0.011705 | -0.013505 | -0.04517 | -0.04107 | -0.011711 | -0.0084697 | -0.016008 | 0.0095932 | 0.035564 | 0.0095171 | 0.039479 | 0.014783 | 0.019721 | 0.005325 | 0.10249 | 0.078201 | 0.27932 | 0.028521 | -120.4785 | -67.1556 | -120.8977 | 0.13945 | 0.293 | 0.13595 | -123.0321 | 122.6359 | -0.16301 | 122.6222 | 122.6127 | -0.023196 | -0.1873 | 0.013821 | -0.42471 | -0.12605 | 2.1289 | 1.7098 | 2.1345 | 0.027498 | -0.12955 | 122.7099 | 122.6856 | 122.8867 | 122.6271 | -0.23698 | 122.7469 | 122.9004 | 122.7434 | 55.4518 | -123.2976
2478.3438 | 122.9874 | -122.5662 | 0.2243 | 1.4211e-13 | -0.011064 | -0.013505 | -0.04517 | -0.040857 | -0.011711 | -0.00083919 | -0.016008 | 0.010021 | 0.03535 | 0.0097307 | 0.039052 | 0.010204 | 0.015142 | 0.005325 | 0.10707 | 0.08278 | 0.27932 | 0.028521 | -120.4785 | -67.2792 | -120.8793 | 0.13487 | 0.29758 | 0.14511 | -123.0367 | 122.5947 | -0.11724 | 122.5764 | 122.5715 | -0.023196 | -0.14152 | 0.05502 | -0.47049 | -0.089433 | 2.0877 | 1.6869 | 2.1574 | 0.073276 | -0.079195 | 122.6733 | 122.649 | 122.8455 | 122.5814 | -0.19578 | 122.7011 | 122.8638 | 122.7113 | 55.287 | -123.261
2480.0625 | 122.9233 | -122.5845 | 0.24261 | 1.4211e-13 | -0.011278 | -0.013291 | -0.045384 | -0.041284 | -0.011711 | -0.0084697 | -0.016222 | 0.010021 | 0.03535 | 0.0095171 | 0.039479 | 0.010204 | 0.019721 | 0.000747 | 0.10707 | 0.073622 | 0.27932 | 0.023942 | -120.4557 | -67.4532 | -120.8656 | 0.13487 | 0.28384 | 0.13137 | -123.0321 | 122.6085 | -0.13555 | 122.5947 | 122.5853 | -0.023195 | -0.16899 | 0.036709 | -0.44759 | -0.10774 | 2.1289 | 1.7189 | 2.1665 | 0.041229 | -0.11124 | 122.6916 | 122.6582 | 122.8639 | 122.6043 | -0.21867 | 122.7194 | 122.8684 | 122.7159 | 55.1313 | -123.2747
2481.7812 | 122.9828 | -122.5525 | 0.21515 | 1.4211e-13 | -0.011491 | -0.013505 | -0.04517 | -0.040643 | -0.011711 | -0.00083919 | -0.016008 | 0.009807 | 0.035136 | 0.0095171 | 0.039052 | 0.005626 | 0.019721 | 0.014482 | 0.10707 | 0.08278 | 0.2839 | 0.010206 | -120.4373 | -67.5493 | -120.8473 | 0.13945 | 0.28842 | 0.13595 | -123.0321 | 122.5627 | -0.10808 | 122.5581 | 122.567 | 0.004276 | -0.13237 | 0.068754 | -0.47964 | -0.075699 | 2.1152 | 1.7052 | 2.1848 | 0.073274 | -0.079197 | 122.6596 | 122.6353 | 122.8364 | 122.5722 | -0.20494 | 122.6919 | 122.8409 | 122.6884 | 55.0031 | -123.2473
2483.5 | 122.9965 | -122.5983 | 0.21973 | 1.4211e-13 | -0.011491 | -0.013718 | -0.04517 | -0.04107 | -0.011711 | -0.0084697 | -0.016435 | 0.010021 | 0.03535 | 0.0095171 | 0.039479 | 0.005626 | 0.0243 | 0.014482 | 0.10249 | 0.078201 | 0.2839 | 0.028521 | -120.4144 | -67.6776 | -120.8381 | 0.13029 | 0.28842 | 0.13137 | -123.0367 | 122.6268 | -0.11724 | 122.6039 | 122.6127 | -0.014039 | -0.14153 | 0.064176 | -0.43844 | -0.089434 | 2.1838 | 1.7601 | 2.1986 | 0.068696 | -0.088354 | 122.7008 | 122.6765 | 122.8822 | 122.6226 | -0.19121 | 122.7286 | 122.8867 | 122.7296 | 54.9207 | -123.2564
2485.2188 | 122.8821 | -122.612 | 0.25635 | 1.4211e-13 | -0.011278 | -0.013291 | -0.045384 | -0.041284 | -0.011497 | 0.0067908 | -0.015581 | 0.010021 | 0.035564 | 0.0099443 | 0.039693 | 0.014783 | 0.019721 | 0.005325 | 0.10707 | 0.08278 | 0.2839 | 0.023942 | -120.4099 | -67.8286 | -120.8198 | 0.13487 | 0.293 | 0.15884 | -123.0413 | 122.6359 | -0.14928 | 122.6268 | 122.6173 | -0.018617 | -0.17357 | 0.027555 | -0.42929 | -0.12148 | 2.2021 | 1.7922 | 2.2215 | 0.036653 | -0.097503 | 122.7191 | 122.6948 | 122.8959 | 122.6317 | -0.23241 | 122.7469 | 122.905 | 122.7708 | 54.7834 | -123.2976
2487 | 122.8821 | -122.6212 | 0.26093 | 1.4211e-13 | -0.011491 | -0.013505 | -0.045598 | -0.04107 | -0.011711 | -0.00083919 | -0.016222 | 0.010021 | 0.035777 | 0.0095171 | 0.039479 | 0.005626 | 0.0243 | 0.000747 | 0.10707 | 0.073622 | 0.27932 | 0.019363 | -120.387 | -67.9797 | -120.8152 | 0.13487 | 0.28842 | 0.13595 | -123.0321 | 122.6405 | -0.15386 | 122.6268 | 122.6219 | -0.018616 | -0.1873 | 0.018399 | -0.41097 | -0.12605 | 2.2342 | 1.8059 | 2.2169 | 0.027498 | -0.12497 | 122.7282 | 122.6948 | 122.9005 | 122.6455 | -0.24156 | 122.756 | 122.9096 | 122.7571 | 54.6414 | -123.2931
2488.7188 | 122.937 | -122.58 | 0.2243 | 1.4211e-13 | -0.011705 | -0.013718 | -0.044957 | -0.040857 | -0.011711 | -0.00083919 | -0.016008 | 0.010021 | 0.03535 | 0.0097307 | 0.039693 | 0.005626 | 0.019721 | 0.005325 | 0.10707 | 0.08278 | 0.2839 | 0.037679 | -120.3778 | -68.0347 | -120.8015 | 0.13487 | 0.28842 | 0.13137 | -123.0413 | 122.6176 | -0.11724 | 122.5856 | 122.5853 | -0.032354 | -0.14152 | 0.059599 | -0.46133 | -0.089433 | 2.2021 | 1.7784 | 2.2398 | 0.064119 | -0.092931 | 122.687 | 122.6627 | 122.8639 | 122.5997 | -0.18663 | 122.7148 | 122.8684 | 122.7113 | 54.5453 | -123.2656
2490.5156 | 122.8867 | -122.6028 | 0.26093 | 1.4211e-13 | -0.011705 | -0.013077 | -0.045598 | -0.04107 | -0.011497 | -0.0084697 | -0.015794 | 0.010021 | 0.03535 | 0.0097307 | 0.039052 | 0.005626 | 0.010564 | 0.009904 | 0.10707 | 0.073622 | 0.27932 | 0.019363 | -120.3412 | -68.1858 | -120.7832 | 0.12571 | 0.28842 | 0.13137 | -123.0413 | 122.6222 | -0.15386 | 122.6085 | 122.6127 | -0.009459 | -0.1873 | 0.018399 | -0.43844 | -0.13521 | 2.2617 | 1.8197 | 2.2581 | 0.027498 | -0.12955 | 122.7099 | 122.6765 | 122.8822 | 122.6134 | -0.24156 | 122.7286 | 122.8913 | 122.7342 | 54.4171 | -123.3022
2492.2969 | 122.9599 | -122.58 | 0.24261 | 1.4211e-13 | -0.011705 | -0.013932 | -0.045384 | -0.04107 | -0.011497 | -0.00083919 | -0.016008 | 0.0095932 | 0.03535 | 0.0097307 | 0.039265 | 0.005626 | 0.0243 | 0.000747 | 0.11622 | 0.08278 | 0.2839 | 0.037679 | -120.3274 | -68.3506 | -120.7649 | 0.12571 | 0.28384 | 0.13595 | -123.0459 | 122.6176 | -0.12639 | 122.5856 | 122.5807 | -0.036932 | -0.15984 | 0.041288 | -0.46591 | -0.1169 | 2.2525 | 1.8151 | 2.281 | 0.041229 | -0.10666 | 122.6962 | 122.6627 | 122.8639 | 122.6043 | -0.20494 | 122.7057 | 122.8638 | 122.7159 | 54.2293 | -123.2885
2494.0781 | 122.9874 | -122.5616 | 0.21515 | 1.4211e-13 | -0.011919 | -0.013718 | -0.045384 | -0.04107 | -0.011711 | -0.00083919 | -0.016222 | 0.0095932 | 0.03535 | 0.0097307 | 0.039479 | 0.005626 | 0.0243 | 0.009904 | 0.11165 | 0.078201 | 0.28848 | 0.028521 | -120.2954 | -68.4697 | -120.7466 | 0.13029 | 0.293 | 0.13137 | -123.0367 | 122.5902 | -0.1035 | 122.5673 | 122.5716 | -0.018617 | -0.13695 | 0.073332 | -0.47506 | -0.084856 | 2.2662 | 1.8151 | 2.2901 | 0.077852 | -0.083776 | 122.6733 | 122.6398 | 122.8501 | 122.5859 | -0.18663 | 122.6919 | 122.8546 | 122.693 | 54.092 | -123.2519
2495.8438 | 122.9645 | -122.6028 | 0.22888 | 1.4211e-13 | -0.011491 | -0.013505 | -0.04517 | -0.04107 | -0.011711 | -0.0084697 | -0.016008 | 0.0095932 | 0.03535 | 0.0095171 | 0.039693 | 0.005626 | 0.028878 | 0.014482 | 0.11165 | 0.078201 | 0.29306 | 0.028521 | -120.2862 | -68.5841 | -120.7374 | 0.12571 | 0.28384 | 0.12222 | -123.0459 | 122.6314 | -0.11724 | 122.6085 | 122.6173 | -0.014039 | -0.15068 | 0.064178 | -0.44302 | -0.10317 | 2.3166 | 1.8654 | 2.3085 | 0.054962 | -0.10667 | 122.7145 | 122.681 | 122.8959 | 122.6317 | -0.20036 | 122.7286 | 122.8867 | 122.7251 | 54.0187 | -123.2747
2497.6562 | 123.0148 | -122.5891 | 0.21973 | 1.4211e-13 | -0.011491 | -0.013932 | -0.04517 | -0.040857 | -0.011711 | 0.0067908 | -0.016008 | 0.010021 | 0.03535 | 0.0095171 | 0.039265 | 0.010204 | 0.019721 | 0.014482 | 0.11165 | 0.073622 | 0.27475 | 0.019363 | -120.2725 | -68.7764 | -120.7282 | 0.13029 | 0.28842 | 0.12679 | -123.0459 | 122.6085 | -0.10808 | 122.5993 | 122.6036 | -0.004881 | -0.1461 | 0.055018 | -0.45676 | -0.089434 | 2.3166 | 1.8609 | 2.3176 | 0.068696 | -0.092933 | 122.7008 | 122.6627 | 122.8639 | 122.6088 | -0.20036 | 122.7194 | 122.8775 | 122.7159 | 53.8127 | -123.2656
2499.3906 | 122.9095 | -122.5937 | 0.25177 | 1.4211e-13 | -0.011278 | -0.013291 | -0.045384 | -0.040643 | -0.011497 | 0.0067908 | -0.015794 | 0.009807 | 0.035564 | 0.0097307 | 0.039265 | 0.014783 | 0.0243 | 0.000747 | 0.10707 | 0.073622 | 0.27932 | 0.046837 | -120.245 | -68.9275 | -120.6916 | 0.12571 | 0.293 | 0.13137 | -123.0459 | 122.6405 | -0.1447 | 122.6085 | 122.5944 | -0.04609 | -0.17815 | 0.027554 | -0.45218 | -0.12606 | 2.3487 | 1.9021 | 2.3542 | 0.041231 | -0.1204 | 122.7008 | 122.6673 | 122.873 | 122.618 | -0.20493 | 122.7194 | 122.8867 | 122.7251 | 53.6662 | -123.2976
2501.1562 | 122.85 | -122.612 | 0.25635 | 1.4211e-13 | -0.011705 | -0.013505 | -0.045811 | -0.040643 | -0.011497 | -0.0161 | -0.015794 | 0.010021 | 0.035564 | 0.0097307 | 0.039479 | 0.001048 | 0.0243 | 0.014482 | 0.11165 | 0.073622 | 0.27932 | 0.051416 | -120.2405 | -69.0191 | -120.6825 | 0.13029 | 0.27926 | 0.13595 | -123.0459 | 122.6634 | -0.1447 | 122.613 | 122.6265 | -0.036934 | -0.18273 | 0.022976 | -0.43387 | -0.12606 | 2.3715 | 1.9295 | 2.3634 | 0.022917 | -0.1204 | 122.7236 | 122.6856 | 122.8913 | 122.6363 | -0.20493 | 122.7423 | 122.8913 | 122.748 | 53.5929 | -123.3022
2502.9531 | 122.9874 | -122.58 | 0.21515 | 1.4211e-13 | -0.011491 | -0.013291 | -0.045384 | -0.041284 | -0.011924 | -0.00083919 | -0.015794 | 0.009807 | 0.035777 | 0.0097307 | 0.039479 | 0.019361 | 0.0243 | 0.009904 | 0.11622 | 0.08278 | 0.27932 | 0.023942 | -120.213 | -69.1153 | -120.6687 | 0.12571 | 0.27926 | 0.13137 | -123.0459 | 122.6039 | -0.098924 | 122.5993 | 122.5899 | -0.014038 | -0.13237 | 0.064175 | -0.46591 | -0.089435 | 2.367 | 1.9112 | 2.3771 | 0.064116 | -0.083776 | 122.6962 | 122.6627 | 122.8593 | 122.6043 | -0.19121 | 122.7057 | 122.8592 | 122.7113 | 53.4647 | -123.261
2504.7344 | 122.9233 | -122.6074 | 0.27008 | 1.4211e-13 | -0.011491 | -0.013077 | -0.045384 | -0.040857 | -0.011711 | -0.00083919 | -0.015794 | 0.0095932 | 0.03535 | 0.0095171 | 0.039693 | 0.010204 | 0.0243 | 0.005325 | 0.11622 | 0.073622 | 0.2839 | 0.019363 | -120.1901 | -69.2755 | -120.6504 | 0.12571 | 0.28384 | 0.13137 | -123.0459 | 122.6268 | -0.15386 | 122.6176 | 122.6127 | -0.014038 | -0.19646 | 0.013822 | -0.43844 | -0.14437 | 2.4173 | 1.957 | 2.3955 | 0.013763 | -0.13871 | 122.7236 | 122.681 | 122.8913 | 122.6317 | -0.25072 | 122.7331 | 122.8913 | 122.7388 | 53.3319 | -123.3159
2506.4531 | 122.9187 | -122.5891 | 0.24261 | 1.4211e-13 | -0.011919 | -0.013505 | -0.045384 | -0.040643 | -0.011924 | -0.0084697 | -0.016008 | 0.009807 | 0.035564 | 0.0099443 | 0.039479 | 0.005626 | 0.019721 | 0.005325 | 0.11165 | 0.073622 | 0.27932 | 0.019363 | -120.1672 | -69.3854 | -120.6367 | 0.12114 | 0.27926 | 0.12679 | -123.0504 | 122.6085 | -0.13097 | 122.5947 | 122.5944 | -0.014038 | -0.16899 | 0.036709 | -0.46133 | -0.12148 | 2.4219 | 1.9524 | 2.4138 | 0.03665 | -0.11582 | 122.7008 | 122.6627 | 122.8684 | 122.6088 | -0.22325 | 122.7102 | 122.8684 | 122.7159 | 53.2037 | -123.2931
2508.1719 | 122.8683 | -122.6028 | 0.24719 | 1.4211e-13 | -0.011491 | -0.013505 | -0.045598 | -0.04107 | -0.011711 | -0.0084697 | -0.015794 | 0.0095932 | 0.035564 | 0.0099443 | 0.039265 | 0.001048 | 0.019721 | 0.005325 | 0.10249 | 0.078201 | 0.28848 | 0.019363 | -120.1489 | -69.5182 | -120.6229 | 0.12571 | 0.27469 | 0.12679 | -123.055 | 122.6222 | -0.1447 | 122.6039 | 122.6082 | -0.014038 | -0.16899 | 0.041289 | -0.45218 | -0.12148 | 2.454 | 1.9799 | 2.4321 | 0.027495 | -0.1204 | 122.7053 | 122.681 | 122.8913 | 122.6226 | -0.22783 | 122.7286 | 122.8775 | 122.7296 | 53.0847 | -123.3022
2509.8906 | 123.0331 | -122.5708 | 0.23346 | 1.4211e-13 | -0.011491 | -0.013291 | -0.04517 | -0.040857 | -0.011711 | -0.00083919 | -0.016008 | 0.010234 | 0.03535 | 0.0097307 | 0.039693 | 0.001048 | 0.019721 | 0.014482 | 0.11165 | 0.08278 | 0.2839 | 0.023942 | -120.126 | -69.6372 | -120.6046 | 0.12114 | 0.28842 | 0.13137 | -123.0504 | 122.5947 | -0.12181 | 122.5718 | 122.5853 | -0.00946 | -0.15068 | 0.050444 | -0.47964 | -0.11232 | 2.4448 | 1.9662 | 2.4458 | 0.054964 | -0.10209 | 122.6824 | 122.6536 | 122.8547 | 122.5905 | -0.20952 | 122.6919 | 122.8592 | 122.7022 | 52.9336 | -123.2839
2511.6875 | 122.9874 | -122.5937 | 0.2243 | 1.4211e-13 | -0.011491 | -0.013505 | -0.045598 | -0.04107 | -0.011711 | -0.00083919 | -0.016222 | 0.010234 | 0.03535 | 0.0099443 | 0.039265 | 0.005626 | 0.033457 | 0.009904 | 0.10707 | 0.08278 | 0.28848 | 0.019363 | -120.1077 | -69.7654 | -120.5817 | 0.12571 | 0.28384 | 0.13137 | -123.0504 | 122.6131 | -0.11724 | 122.5993 | 122.6036 | -0.009459 | -0.14152 | 0.064177 | -0.45676 | -0.09859 | 2.486 | 2.012 | 2.4687 | 0.05954 | -0.092931 | 122.7008 | 122.6765 | 122.8822 | 122.6271 | -0.20494 | 122.7194 | 122.8775 | 122.7251 | 52.8282 | -123.2747
2513.4844 | 122.9782 | -122.5708 | 0.19684 | 1.4211e-13 | -0.011705 | -0.013505 | -0.045811 | -0.040857 | -0.011924 | -0.00083919 | -0.016008 | 0.010021 | 0.03535 | 0.0099443 | 0.039479 | 0.005626 | 0.019721 | 0.009904 | 0.10249 | 0.078201 | 0.27932 | 0.023942 | -120.0756 | -69.77 | -120.568 | 0.12114 | 0.27469 | 0.13137 | -123.0596 | 122.5947 | -0.094348 | 122.5764 | 122.5807 | -0.014038 | -0.11864 | 0.082486 | -0.4888 | -0.075702 | 2.4952 | 2.0028 | 2.4916 | 0.077849 | -0.065465 | 122.6733 | 122.649 | 122.8501 | 122.5905 | -0.1729 | 122.6919 | 122.8455 | 122.7022 | 52.8008 | -123.2564
2515.2656 | 122.9141 | -122.6257 | 0.23346 | 1.4211e-13 | -0.011491 | -0.013077 | -0.045598 | -0.040857 | -0.011497 | 0.0067908 | -0.016008 | 0.009807 | 0.035777 | 0.0099443 | 0.039906 | 0.001048 | 0.019721 | 0.005325 | 0.11165 | 0.078201 | 0.2839 | 0.037679 | -120.0481 | -69.9165 | -120.5497 | 0.11656 | 0.28384 | 0.13137 | -123.055 | 122.6634 | -0.12181 | 122.6268 | 122.6311 | -0.032354 | -0.15526 | 0.050444 | -0.42929 | -0.1169 | 2.5776 | 2.0761 | 2.5053 | 0.050385 | -0.10209 | 122.7374 | 122.7039 | 122.9096 | 122.6455 | -0.19578 | 122.7423 | 122.9096 | 122.7571 | 52.7092 | -123.2885
2516.9844 | 122.9141 | -122.6303 | 0.2655 | 1.4211e-13 | -0.011705 | -0.013505 | -0.04517 | -0.040857 | -0.011497 | -0.0084697 | -0.015581 | 0.010021 | 0.035564 | 0.0097307 | 0.039693 | 0.010204 | 0.015142 | 0.014482 | 0.10707 | 0.078201 | 0.27475 | 0.014784 | -120.0298 | -69.9944 | -120.5314 | 0.12571 | 0.28384 | 0.12222 | -123.0596 | 122.6451 | -0.15843 | 122.6405 | 122.6448 | -0.000302 | -0.1873 | 0.009242 | -0.42929 | -0.13979 | 2.6005 | 2.0989 | 2.5282 | 0.018341 | -0.14329 | 122.7374 | 122.7085 | 122.9051 | 122.6455 | -0.25072 | 122.756 | 122.9142 | 122.7525 | 52.6359 | -123.3251
2518.7656 | 122.9599 | -122.5616 | 0.21515 | 1.4211e-13 | -0.011705 | -0.013505 | -0.045598 | -0.041284 | -0.011711 | -0.00083919 | -0.015581 | 0.010021 | 0.035564 | 0.010158 | 0.039479 | 0.014783 | 0.0243 | 0.000747 | 0.11165 | 0.073622 | 0.27932 | 0.0331 | -120.0069 | -70.0951 | -120.5176 | 0.12571 | 0.27469 | 0.13137 | -123.055 | 122.5947 | -0.1035 | 122.5764 | 122.5624 | -0.032353 | -0.14153 | 0.064175 | -0.49338 | -0.089435 | 2.5547 | 2.044 | 2.5374 | 0.059538 | -0.083776 | 122.6733 | 122.6353 | 122.841 | 122.5859 | -0.18205 | 122.6874 | 122.8363 | 122.693 | 52.4665 | -123.2702
2520.5625 | 122.9919 | -122.612 | 0.21057 | 1.4211e-13 | -0.011491 | -0.013291 | -0.04517 | -0.041284 | -0.011497 | -0.0084697 | -0.016008 | 0.009807 | 0.035564 | 0.0099443 | 0.039693 | 0.014783 | 0.0243 | 0.000747 | 0.10249 | 0.078201 | 0.2839 | 0.019363 | -119.984 | -70.2142 | -120.4947 | 0.12571 | 0.27926 | 0.12679 | -123.055 | 122.6314 | -0.10808 | 122.6268 | 122.6127 | -0.018616 | -0.13237 | 0.073332 | -0.44302 | -0.084857 | 2.628 | 2.1173 | 2.5603 | 0.068694 | -0.083777 | 122.7145 | 122.6902 | 122.8959 | 122.6363 | -0.19121 | 122.7377 | 122.8913 | 122.7388 | 52.3978 | -123.2656
2522.2812 | 122.9782 | -122.6166 | 0.2243 | 1.4211e-13 | -0.011278 | -0.013291 | -0.045384 | -0.041284 | -0.011497 | 0.0067908 | -0.015794 | 0.010021 | 0.035564 | 0.010158 | 0.039479 | 0.019361 | 0.019721 | 0.009904 | 0.11165 | 0.078201 | 0.2839 | 0.014784 | -119.9566 | -70.324 | -120.4718 | 0.12571 | 0.28384 | 0.12679 | -123.0596 | 122.6314 | -0.11266 | 122.6359 | 122.6265 | -0.00488 | -0.1461 | 0.059599 | -0.44302 | -0.09859 | 2.66 | 2.1447 | 2.5878 | 0.05954 | -0.09751 | 122.7282 | 122.6948 | 122.9005 | 122.6363 | -0.20952 | 122.7423 | 122.9004 | 122.7434 | 52.2925 | -123.2839
2524.0625 | 122.8638 | -122.6212 | 0.24719 | 1.4211e-13 | -0.011278 | -0.013291 | -0.04517 | -0.041284 | -0.011711 | -0.0084697 | -0.015794 | 0.009807 | 0.03535 | 0.0097307 | 0.039906 | 0.005626 | 0.019721 | 0.009904 | 0.10707 | 0.078201 | 0.27932 | 0.0331 | -119.9383 | -70.4019 | -120.4673 | 0.11656 | 0.27926 | 0.13137 | -123.0642 | 122.6543 | -0.14012 | 122.6268 | 122.6311 | -0.023196 | -0.16899 | 0.032132 | -0.44303 | -0.13064 | 2.6829 | 2.1539 | 2.5969 | 0.032073 | -0.11582 | 122.7282 | 122.6994 | 122.9005 | 122.6409 | -0.21409 | 122.7377 | 122.9004 | 122.7525 | 52.2193 | -123.3114
2525.8438 | 122.9141 | -122.6303 | 0.22888 | 1.4211e-13 | -0.011705 | -0.013077 | -0.045384 | -0.040857 | -0.011711 | -0.00083919 | -0.015794 | 0.010234 | 0.035777 | 0.0097307 | 0.039906 | 0.014783 | 0.015142 | 0.009904 | 0.10707 | 0.073622 | 0.27932 | 0.037679 | -119.9154 | -70.4797 | -120.4398 | 0.12571 | 0.27926 | 0.12679 | -123.0596 | 122.668 | -0.12181 | 122.6451 | 122.6402 | -0.027775 | -0.15526 | 0.050442 | -0.42929 | -0.10317 | 2.7149 | 2.1905 | 2.6198 | 0.050383 | -0.10209 | 122.7374 | 122.7039 | 122.9096 | 122.6455 | -0.1912 | 122.756 | 122.9096 | 122.7571 | 52.1506 | -123.2885
2527.6406 | 122.9874 | -122.5754 | 0.21057 | 1.4211e-13 | -0.011705 | -0.013291 | -0.04517 | -0.040857 | -0.011711 | 0.0067908 | -0.015581 | 0.010234 | 0.035564 | 0.0099443 | 0.039906 | 0.005626 | 0.0243 | 0.005325 | 0.11165 | 0.08278 | 0.2839 | 0.023942 | -119.8925 | -70.5209 | -120.4261 | 0.12571 | 0.28384 | 0.13137 | -123.0688 | 122.5993 | -0.098924 | 122.581 | 122.5807 | -0.018617 | -0.12779 | 0.073332 | -0.49338 | -0.084857 | 2.6829 | 2.1493 | 2.6427 | 0.073273 | -0.079198 | 122.687 | 122.6582 | 122.8593 | 122.5997 | -0.18663 | 122.7011 | 122.8592 | 122.7068 | 52.0544 | -123.2793
2529.4219 | 122.9599 | -122.5937 | 0.19684 | 1.4211e-13 | -0.011705 | -0.013077 | -0.045384 | -0.04107 | -0.011711 | -0.0161 | -0.016008 | 0.010021 | 0.035777 | 0.0099443 | 0.039906 | 0.010204 | 0.019721 | 0.009904 | 0.10707 | 0.069043 | 0.28848 | 0.019363 | -119.8604 | -70.5988 | -120.3986 | 0.11656 | 0.27926 | 0.11764 | -123.0642 | 122.6131 | -0.08977 | 122.6039 | 122.6036 | -0.009459 | -0.1278 | 0.091643 | -0.47049 | -0.080281 | 2.7333 | 2.1951 | 2.6656 | 0.082427 | -0.079201 | 122.7008 | 122.6627 | 122.8822 | 122.6134 | -0.17748 | 122.7102 | 122.873 | 122.7113 | 51.9949 | -123.261
2531.2031 | 123.0011 | -122.6212 | 0.20599 | 1.4211e-13 | -0.011705 | -0.013291 | -0.045384 | -0.04107 | -0.011711 | -0.0161 | -0.016222 | 0.010021 | 0.035777 | 0.010158 | 0.04012 | 0.010204 | 0.0243 | 0.005325 | 0.10707 | 0.073622 | 0.28848 | 0.023942 | -119.8375 | -70.5576 | -120.4032 | 0.11656 | 0.27926 | 0.11764 | -123.0688 | 122.6451 | -0.098926 | 122.6314 | 122.6265 | -0.018617 | -0.13237 | 0.082487 | -0.4476 | -0.089437 | 2.7836 | 2.218 | 2.6656 | 0.073271 | -0.088357 | 122.7282 | 122.6948 | 122.9096 | 122.6455 | -0.18205 | 122.7377 | 122.9004 | 122.7388 | 52.0636 | -123.2748
2533 | 123.0103 | -122.5937 | 0.20599 | 1.4211e-13 | -0.011705 | -0.013932 | -0.045384 | -0.04107 | -0.011711 | -0.00083919 | -0.016008 | 0.010021 | 0.035777 | 0.0099443 | 0.039906 | 0.014783 | 0.0243 | 0.009904 | 0.10707 | 0.078201 | 0.27932 | 0.014784 | -119.8192 | -70.7224 | -120.3757 | 0.11198 | 0.27926 | 0.12222 | -123.0642 | 122.6085 | -0.098926 | 122.6085 | 122.6036 | -0.00488 | -0.12779 | 0.07333 | -0.47049 | -0.094015 | 2.7745 | 2.218 | 2.6885 | 0.073271 | -0.083778 | 122.7008 | 122.6719 | 122.873 | 122.618 | -0.19121 | 122.7057 | 122.873 | 122.7159 | 51.8713 | -123.2702
2534.7812 | 122.9279 | -122.6074 | 0.23804 | 1.4211e-13 | -0.011919 | -0.013291 | -0.04517 | -0.040643 | -0.011711 | -0.0161 | -0.015794 | 0.010021 | 0.035564 | 0.010158 | 0.039906 | 0.014783 | 0.019721 | 0.009904 | 0.11165 | 0.073622 | 0.27932 | 0.019363 | -119.7963 | -70.8002 | -120.3482 | 0.11198 | 0.27469 | 0.12222 | -123.0688 | 122.6268 | -0.12639 | 122.6222 | 122.6173 | -0.009459 | -0.16441 | 0.041287 | -0.46134 | -0.12606 | 2.8111 | 2.2592 | 2.7205 | 0.03665 | -0.11582 | 122.7191 | 122.681 | 122.8867 | 122.6271 | -0.21867 | 122.7194 | 122.8821 | 122.7296 | 51.8072 | -123.3068
2536.5 | 122.8958 | -122.6395 | 0.23346 | 1.4211e-13 | -0.011919 | -0.013291 | -0.045384 | -0.040643 | -0.011497 | 0.0067908 | -0.015581 | 0.009807 | 0.035564 | 0.0099443 | 0.039693 | 0.010204 | 0.019721 | 0.009904 | 0.10707 | 0.073622 | 0.2839 | 0.028521 | -119.7643 | -70.814 | -120.3391 | 0.11198 | 0.27469 | 0.11764 | -123.0688 | 122.668 | -0.12639 | 122.6497 | 122.6494 | -0.018617 | -0.15984 | 0.050444 | -0.42929 | -0.12148 | 2.8752 | 2.3004 | 2.7297 | 0.041228 | -0.11582 | 122.7465 | 122.7131 | 122.9234 | 122.6592 | -0.20494 | 122.7514 | 122.9142 | 122.7571 | 51.8255 | -123.3022
2538.2656 | 122.9507 | -122.6257 | 0.21973 | 1.4211e-13 | -0.011705 | -0.013505 | -0.045384 | -0.040857 | -0.011497 | -0.00083919 | -0.015794 | 0.010234 | 0.035777 | 0.010158 | 0.040334 | 0.010204 | 0.0243 | 0.014482 | 0.11165 | 0.08278 | 0.28848 | 0.014784 | -119.746 | -70.9147 | -120.3116 | 0.11656 | 0.27011 | 0.12679 | -123.0642 | 122.6405 | -0.10808 | 122.6359 | 122.6402 | -0.000302 | -0.13695 | 0.068754 | -0.43845 | -0.10317 | 2.8798 | 2.3141 | 2.7526 | 0.050381 | -0.092933 | 122.7374 | 122.7085 | 122.9142 | 122.65 | -0.20494 | 122.7423 | 122.8958 | 122.7525 | 51.711 | -123.2839
2539.9844 | 122.9004 | -122.6166 | 0.22888 | 1.4211e-13 | -0.011705 | -0.013291 | -0.04517 | -0.040857 | -0.011711 | -0.00083919 | -0.015581 | 0.010021 | 0.036205 | 0.0099443 | 0.04012 | 0.010204 | 0.015142 | 0.000747 | 0.11165 | 0.08278 | 0.29306 | 0.023942 | -119.7139 | -70.9925 | -120.3024 | 0.11656 | 0.27011 | 0.11306 | -123.0733 | 122.6405 | -0.11724 | 122.6268 | 122.6173 | -0.023195 | -0.1461 | 0.064178 | -0.45676 | -0.11233 | 2.9027 | 2.3141 | 2.7709 | 0.041226 | -0.11582 | 122.7282 | 122.6994 | 122.9096 | 122.6317 | -0.20494 | 122.7331 | 122.8867 | 122.7296 | 51.624 | -123.3022
2541.7656 | 122.9919 | -122.5891 | 0.21515 | 1.4211e-13 | -0.011705 | -0.013505 | -0.04517 | -0.041284 | -0.011711 | -0.0084697 | -0.015581 | 0.010448 | 0.035777 | 0.0099443 | 0.04012 | 0.005626 | 0.019721 | 0.009904 | 0.10707 | 0.08278 | 0.29306 | 0.037679 | -119.691 | -71.0429 | -120.2887 | 0.11656 | 0.26553 | 0.11764 | -123.0642 | 122.6268 | -0.10808 | 122.5947 | 122.599 | -0.027775 | -0.13237 | 0.077911 | -0.47507 | -0.098592 | 2.8981 | 2.3004 | 2.7755 | 0.050381 | -0.097512 | 122.6962 | 122.6719 | 122.8822 | 122.6088 | -0.17747 | 122.7057 | 122.8546 | 122.7067 | 51.5462 | -123.2793
2543.4844 | 122.9874 | -122.5891 | 0.21057 | 1.4211e-13 | -0.012132 | -0.013505 | -0.045384 | -0.04107 | -0.011497 | -0.00083919 | -0.015581 | 0.010021 | 0.035564 | 0.010585 | 0.039906 | 0.005626 | 0.028878 | 0.005325 | 0.11622 | 0.087359 | 0.2839 | 0.014784 | -119.659 | -71.0154 | -120.2612 | 0.11198 | 0.27011 | 0.11764 | -123.0733 | 122.6039 | -0.094346 | 122.5947 | 122.5944 | -0.009459 | -0.12321 | 0.073332 | -0.48423 | -0.098592 | 2.9302 | 2.3279 | 2.8121 | 0.059537 | -0.092934 | 122.7053 | 122.6765 | 122.873 | 122.618 | -0.19579 | 122.7011 | 122.8592 | 122.7067 | 51.5737 | -123.2839
2545.2812 | 122.9599 | -122.6166 | 0.21515 | 1.4211e-13 | -0.011491 | -0.013505 | -0.045384 | -0.040857 | -0.011711 | -0.00083919 | -0.015794 | 0.010234 | 0.035777 | 0.010372 | 0.04012 | 0.010204 | 0.0243 | 0.014482 | 0.11622 | 0.078201 | 0.27932 | 0.023942 | -119.6406 | -70.9834 | -120.2475 | 0.10282 | 0.26553 | 0.11764 | -123.0779 | 122.6405 | -0.098924 | 122.6268 | 122.6311 | -0.00946 | -0.13695 | 0.064175 | -0.46134 | -0.11233 | 2.9759 | 2.3691 | 2.8304 | 0.050381 | -0.097512 | 122.7328 | 122.6948 | 122.8959 | 122.6409 | -0.19121 | 122.7194 | 122.8821 | 122.7342 | 51.6332 | -123.2931
2547.0625 | 122.9324 | -122.6349 | 0.21515 | 1.4211e-13 | -0.011919 | -0.013505 | -0.045598 | -0.04107 | -0.011924 | -0.00083919 | -0.015794 | 0.009807 | 0.035777 | 0.010372 | 0.039906 | 0.001048 | 0.0243 | 0.005325 | 0.10707 | 0.073622 | 0.27932 | 0.019363 | -119.6132 | -70.9834 | -120.2292 | 0.11656 | 0.26553 | 0.11306 | -123.0733 | 122.6543 | -0.10808 | 122.6359 | 122.6402 | -0.014038 | -0.14153 | 0.064175 | -0.43845 | -0.098592 | 3.0217 | 2.4057 | 2.8442 | 0.050381 | -0.10209 | 122.742 | 122.7085 | 122.9142 | 122.6592 | -0.19579 | 122.7514 | 122.9004 | 122.7479 | 51.6515 | -123.2885
2548.8594 | 122.9095 | -122.6303 | 0.22888 | 1.4211e-13 | -0.011919 | -0.013077 | -0.045598 | -0.04107 | -0.011711 | 0.014421 | -0.015794 | 0.010234 | 0.035564 | 0.0099443 | 0.04012 | 0.005626 | 0.019721 | 0.014482 | 0.11165 | 0.078201 | 0.2839 | 0.037679 | -119.5903 | -70.8643 | -120.2017 | 0.11198 | 0.27011 | 0.11306 | -123.0779 | 122.668 | -0.11724 | 122.6359 | 122.6448 | -0.023197 | -0.15068 | 0.055021 | -0.44761 | -0.1169 | 3.04 | 2.4286 | 2.8762 | 0.041226 | -0.11582 | 122.742 | 122.7085 | 122.9142 | 122.65 | -0.1912 | 122.7423 | 122.9004 | 122.7434 | 51.766 | -123.3068
2550.6562 | 122.9919 | -122.5983 | 0.1831 | 1.4211e-13 | -0.011705 | -0.013291 | -0.04517 | -0.040857 | -0.011284 | -0.0084697 | -0.015153 | 0.010021 | 0.035564 | 0.0099443 | 0.04012 | 0.010204 | 0.015142 | 0.005325 | 0.11165 | 0.08278 | 0.27932 | 0.019363 | -119.5491 | -70.9742 | -120.188 | 0.1074 | 0.27011 | 0.11306 | -123.0688 | 122.6176 | -0.071458 | 122.6085 | 122.6036 | -0.014038 | -0.10032 | 0.096219 | -0.47049 | -0.075704 | 3.0492 | 2.4103 | 2.8808 | 0.087003 | -0.070046 | 122.7099 | 122.681 | 122.8776 | 122.6134 | -0.16374 | 122.7057 | 122.8684 | 122.7113 | 51.624 | -123.2519
2552.4375 | 122.9004 | -122.6395 | 0.21973 | 1.4211e-13 | -0.011919 | -0.013291 | -0.04517 | -0.040857 | -0.011711 | -0.0084697 | -0.015581 | 0.010021 | 0.035991 | 0.010585 | 0.04012 | 0.005626 | 0.010564 | 0.009904 | 0.11165 | 0.078201 | 0.2839 | 0.023942 | -119.5262 | -70.933 | -120.1605 | 0.11656 | 0.27469 | 0.10848 | -123.0688 | 122.6634 | -0.10808 | 122.6451 | 122.6494 | -0.014038 | -0.14153 | 0.064176 | -0.42929 | -0.10317 | 3.1133 | 2.479 | 2.9083 | 0.05496 | -0.11125 | 122.7511 | 122.7177 | 122.9234 | 122.65 | -0.19579 | 122.756 | 122.9142 | 122.7479 | 51.7065 | -123.2885
2554.1562 | 122.8409 | -122.6715 | 0.23346 | 1.4211e-13 | -0.011491 | -0.013077 | -0.044957 | -0.040643 | -0.012138 | 0.0067908 | -0.016008 | 0.010021 | 0.036205 | 0.010158 | 0.04012 | 0.005626 | 0.015142 | 0.005325 | 0.10249 | 0.078201 | 0.28848 | 0.028521 | -119.5033 | -70.9559 | -120.1605 | 0.089087 | 0.25637 | 0.10848 | -123.0917 | 122.7 | -0.13097 | 122.6771 | 122.6768 | -0.023196 | -0.15526 | 0.055022 | -0.42015 | -0.14437 | 3.1682 | 2.511 | 2.9312 | 0.022913 | -0.12498 | 122.774 | 122.7497 | 122.96 | 122.6867 | -0.20494 | 122.7606 | 122.9279 | 122.78 | 51.7156 | -123.3251
2555.9375 | 122.9553 | -122.6166 | 0.16022 | 1.4211e-13 | -0.011919 | -0.013291 | -0.044529 | -0.040857 | -0.011924 | -0.0084697 | -0.015581 | 0.010021 | 0.035564 | 0.0099443 | 0.040547 | 0.010204 | 0.0243 | 0.005325 | 0.11165 | 0.08278 | 0.28848 | 0.023942 | -119.4712 | -70.9834 | -120.1468 | 0.07993 | 0.24264 | 0.099323 | -123.1054 | 122.6405 | -0.04857 | 122.6268 | 122.6219 | -0.018617 | -0.077437 | 0.12826 | -0.48881 | -0.080287 | 3.1453 | 2.4698 | 2.9586 | 0.08242 | -0.060894 | 122.7282 | 122.6994 | 122.9051 | 122.6409 | -0.13628 | 122.6965 | 122.8592 | 122.7159 | 51.6332 | -123.2656
2557.7188 | 122.8775 | -122.6257 | 0.21057 | 1.4211e-13 | -0.011919 | -0.013505 | -0.045384 | -0.04107 | -0.011497 | -0.0084697 | -0.015794 | 0.010021 | 0.035777 | 0.0097307 | 0.04012 | 0.005626 | 0.019721 | 0.014482 | 0.11622 | 0.08278 | 0.28848 | 0.023942 | -119.4254 | -70.9284 | -120.133 | 0.084508 | 0.24264 | 0.099323 | -123.0962 | 122.6497 | -0.094346 | 122.6314 | 122.6402 | -0.00946 | -0.12779 | 0.07791 | -0.4705 | -0.12606 | 3.2003 | 2.4927 | 2.9632 | 0.032066 | -0.11125 | 122.742 | 122.7085 | 122.9142 | 122.6455 | -0.18663 | 122.7102 | 122.8684 | 122.7251 | 51.6973 | -123.3068
2559.5156 | 122.8821 | -122.6944 | 0.20142 | 1.4211e-13 | -0.012132 | -0.013718 | -0.045384 | -0.040857 | -0.011924 | 0.0067908 | -0.015581 | 0.010448 | 0.035564 | 0.010585 | 0.04012 | 0.014783 | 0.015142 | 0.005325 | 0.097912 | 0.073622 | 0.2839 | 0.023942 | -119.4117 | -70.8872 | -120.1284 | 0.057037 | 0.2289 | 0.085587 | -123.1145 | 122.7183 | -0.1035 | 122.7092 | 122.6997 | -0.018617 | -0.12779 | 0.082487 | -0.42015 | -0.14438 | 3.2827 | 2.566 | 2.9861 | 0.027485 | -0.11583 | 122.7923 | 122.768 | 122.9783 | 122.7095 | -0.17747 | 122.7514 | 122.9233 | 122.78 | 51.8072 | -123.316
2561.2344 | 122.9782 | -122.6761 | 0.14648 | 1.4211e-13 | -0.011705 | -0.013291 | -0.045384 | -0.041284 | -0.011711 | -0.00083919 | -0.016008 | 0.010021 | 0.035564 | 0.010585 | 0.040334 | 0.010204 | 0.019721 | 0.009904 | 0.11165 | 0.078201 | 0.2839 | 0.0331 | -119.3522 | -70.9239 | -120.0964 | 0.070773 | 0.21974 | 0.090166 | -123.1145 | 122.7092 | -0.034837 | 122.6863 | 122.686 | -0.023196 | -0.068283 | 0.13742 | -0.43846 | -0.075711 | 3.3239 | 2.5797 | 3.0182 | 0.07326 | -0.056318 | 122.7877 | 122.7543 | 122.96 | 122.6958 | -0.11338 | 122.7469 | 122.8958 | 122.7663 | 51.7522 | -123.261
2563.0156 | 123.0103 | -122.6395 | 0.15106 | 1.4211e-13 | -0.012132 | -0.013505 | -0.045384 | -0.040857 | -0.011711 | -0.0161 | -0.015367 | 0.010234 | 0.035777 | 0.010372 | 0.040334 | 0.005626 | 0.015142 | 0.005325 | 0.11622 | 0.08278 | 0.28848 | 0.019363 | -119.3201 | -70.8826 | -120.0689 | 0.066194 | 0.22432 | 0.090166 | -123.1145 | 122.6588 | -0.034837 | 122.6451 | 122.6448 | -0.014038 | -0.068282 | 0.13742 | -0.47508 | -0.084868 | 3.3193 | 2.5705 | 3.0456 | 0.07326 | -0.060896 | 122.7557 | 122.7222 | 122.9279 | 122.6546 | -0.1317 | 122.7057 | 122.8638 | 122.7296 | 51.7568 | -123.2656
2564.7969 | 123.0194 | -122.6578 | 0.12817 | 1.4211e-13 | -0.011705 | -0.013291 | -0.04517 | -0.041284 | -0.011711 | -0.0084697 | -0.015153 | 0.010234 | 0.035777 | 0.010372 | 0.040547 | 0.001048 | 0.0243 | 0.009904 | 0.11165 | 0.073622 | 0.28848 | 0.023942 | -119.2835 | -70.8598 | -120.0552 | 0.052459 | 0.21974 | 0.085587 | -123.1237 | 122.6817 | -0.016527 | 122.6588 | 122.6677 | -0.014038 | -0.054552 | 0.16031 | -0.46593 | -0.075715 | 3.3743 | 2.6026 | 3.0685 | 0.09157 | -0.042587 | 122.7694 | 122.7314 | 122.9463 | 122.6821 | -0.10423 | 122.7102 | 122.8775 | 122.7434 | 51.798 | -123.2519
2566.5781 | 122.9507 | -122.6578 | 0.14191 | 1.4211e-13 | -0.011919 | -0.013291 | -0.04517 | -0.04107 | -0.011497 | 0.0067908 | -0.015581 | 0.010234 | 0.035991 | 0.010372 | 0.040761 | 0.010204 | 0.0243 | 0.009904 | 0.10707 | 0.08278 | 0.28848 | 0.019363 | -119.2515 | -70.846 | -120.0277 | 0.052459 | 0.20601 | 0.071851 | -123.1329 | 122.6771 | -0.034839 | 122.668 | 122.6677 | -0.009459 | -0.059127 | 0.14657 | -0.47509 | -0.089448 | 3.4063 | 2.6301 | 3.1052 | 0.064101 | -0.070056 | 122.7648 | 122.7406 | 122.9463 | 122.6821 | -0.12254 | 122.7102 | 122.8638 | 122.7296 | 51.8118 | -123.2748
2568.2969 | 122.9782 | -122.6624 | 0.16022 | 1.4211e-13 | -0.011919 | -0.013291 | -0.04517 | -0.04107 | -0.011924 | -0.00083919 | -0.015367 | 0.010234 | 0.036205 | 0.010372 | 0.040334 | 0.005626 | 0.015142 | 0.000747 | 0.11622 | 0.073622 | 0.27932 | 0.0331 | -119.224 | -70.8094 | -120.0185 | 0.04788 | 0.21059 | 0.058115 | -123.142 | 122.6955 | -0.043992 | 122.668 | 122.6631 | -0.032353 | -0.086595 | 0.11911 | -0.47967 | -0.11234 | 3.4384 | 2.6438 | 3.1235 | 0.050369 | -0.1021 | 122.7786 | 122.736 | 122.9417 | 122.6775 | -0.12712 | 122.7102 | 122.8729 | 122.7205 | 51.853 | -123.3022
2570.0938 | 122.9874 | -122.6761 | 0.14191 | 1.4211e-13 | -0.011919 | -0.013718 | -0.045598 | -0.04107 | -0.011284 | -0.0084697 | -0.015367 | 0.010448 | 0.035777 | 0.010799 | 0.04012 | 0.010204 | 0.028878 | 0.005325 | 0.11165 | 0.08278 | 0.2839 | 0.019363 | -119.1782 | -70.846 | -119.9911 | 0.057037 | 0.20143 | 0.062694 | -123.1374 | 122.6954 | -0.03026 | 122.6863 | 122.6814 | -0.014038 | -0.059127 | 0.142 | -0.46136 | -0.08487 | 3.4979 | 2.685 | 3.1464 | 0.059522 | -0.079213 | 122.7877 | 122.7589 | 122.96 | 122.705 | -0.12254 | 122.7331 | 122.8775 | 122.7388 | 51.8301 | -123.2793
2571.875 | 122.9279 | -122.7264 | 0.18768 | 1.4211e-13 | -0.012132 | -0.013718 | -0.045598 | -0.040857 | -0.011924 | -0.0084697 | -0.015367 | 0.010234 | 0.035777 | 0.010372 | 0.040547 | 0.005626 | 0.019721 | 0.005325 | 0.097912 | 0.078201 | 0.2839 | 0.023942 | -119.1416 | -70.7316 | -119.959 | 0.04788 | 0.20601 | 0.067272 | -123.142 | 122.7504 | -0.089771 | 122.7321 | 122.7318 | -0.018617 | -0.10948 | 0.09622 | -0.41558 | -0.1398 | 3.5849 | 2.7674 | 3.183 | 0.018325 | -0.12041 | 122.8244 | 122.8046 | 123.0103 | 122.7462 | -0.16374 | 122.7743 | 122.9324 | 122.7937 | 51.9949 | -123.3297
2573.6562 | 122.9553 | -122.644 | 0.13733 | 1.4211e-13 | -0.012132 | -0.013505 | -0.04517 | -0.041284 | -0.012138 | -0.0084697 | -0.015794 | 0.010662 | 0.035777 | 0.010585 | 0.040547 | 0.005626 | 0.015142 | 0.009904 | 0.10707 | 0.078201 | 0.2839 | 0.010206 | -119.1095 | -70.7041 | -119.9361 | 0.052459 | 0.20601 | 0.058115 | -123.1374 | 122.6542 | -0.030261 | 122.6497 | 122.6539 | -0.000302 | -0.059128 | 0.14657 | -0.4934 | -0.08487 | 3.5345 | 2.7079 | 3.2013 | 0.068679 | -0.079214 | 122.7511 | 122.7222 | 122.9279 | 122.6592 | -0.12712 | 122.6965 | 122.8501 | 122.7022 | 51.94 | -123.2748
2575.3906 | 122.8867 | -122.7219 | 0.17395 | 1.4211e-13 | -0.011919 | -0.013505 | -0.045384 | -0.040857 | -0.011497 | -0.0084697 | -0.015581 | 0.010448 | 0.035777 | 0.010372 | 0.040547 | 0.010204 | 0.015142 | 0.000747 | 0.10249 | 0.078201 | 0.2839 | 0.046837 | -119.0866 | -70.5759 | -119.8995 | 0.038723 | 0.20143 | 0.021486 | -123.1466 | 122.7687 | -0.07146 | 122.7321 | 122.7226 | -0.04609 | -0.095749 | 0.10995 | -0.42474 | -0.13523 | 3.6352 | 2.8224 | 3.2471 | 0.027479 | -0.15246 | 122.8244 | 122.8001 | 123.0058 | 122.737 | -0.12711 | 122.7606 | 122.9233 | 122.7433 | 52.146 | -123.3206
2577.1562 | 122.8867 | -122.699 | 0.1831 | 1.4211e-13 | -0.011919 | -0.013718 | -0.045384 | -0.04107 | -0.011711 | -0.0084697 | -0.015367 | 0.010662 | 0.035777 | 0.011013 | 0.040761 | 0.010204 | 0.015142 | 0.000747 | 0.11165 | 0.078201 | 0.2839 | 0.037679 | -119.0454 | -70.5301 | -119.8629 | 0.04788 | 0.20601 | 0.058115 | -123.1329 | 122.7367 | -0.071458 | 122.7092 | 122.6997 | -0.036932 | -0.1049 | 0.1008 | -0.43389 | -0.13522 | 3.6536 | 2.8361 | 3.27 | 0.022903 | -0.12499 | 122.8106 | 122.7772 | 122.9829 | 122.7141 | -0.14543 | 122.7469 | 122.905 | 122.7571 | 52.1689 | -123.316
2578.9375 | 122.9462 | -122.6669 | 0.16937 | 1.4211e-13 | -0.012132 | -0.013505 | -0.045384 | -0.04107 | -0.011711 | 0.0067908 | -0.015581 | 0.010234 | 0.035991 | 0.010799 | 0.040547 | 0.001048 | 0.019721 | 0.009904 | 0.11165 | 0.073622 | 0.28848 | 0.0331 | -118.9767 | -70.4706 | -119.8262 | 0.061616 | 0.21516 | 0.07643 | -123.1329 | 122.7 | -0.057726 | 122.668 | 122.6768 | -0.023196 | -0.095751 | 0.11911 | -0.46593 | -0.10776 | 3.6902 | 2.8407 | 3.3066 | 0.045792 | -0.092943 | 122.7786 | 122.7406 | 122.9554 | 122.6867 | -0.13627 | 122.7285 | 122.8821 | 122.7434 | 52.1964 | -123.3022
2580.75 | 123.0011 | -122.6349 | 0.14191 | 1.4211e-13 | -0.011919 | -0.013932 | -0.045384 | -0.041284 | -0.011711 | -0.0084697 | -0.015794 | 0.010234 | 0.036205 | 0.010799 | 0.040974 | 0.005626 | 0.019721 | 0.009904 | 0.10707 | 0.08278 | 0.28848 | 0.019363 | -118.583 | -70.5072 | -119.8125 | 0.057037 | 0.21974 | 0.090166 | -123.1237 | 122.6543 | -0.034839 | 122.6405 | 122.6448 | -0.009459 | -0.059127 | 0.14657 | -0.48882 | -0.08487 | 4.0519 | 2.8224 | 3.3112 | 0.077837 | -0.051741 | 122.742 | 122.7177 | 122.9234 | 122.6546 | -0.12254 | 122.6919 | 122.8546 | 122.7251 | 52.1277 | -123.2656
2582.4688 | 122.9462 | -122.6578 | 0.15564 | 1.4211e-13 | -0.012132 | -0.013291 | -0.045384 | -0.041284 | -0.011924 | -0.0084697 | -0.015367 | 0.010662 | 0.036418 | 0.010585 | 0.040974 | 0.005626 | 0.019721 | 0.005325 | 0.10707 | 0.08278 | 0.2839 | 0.019363 | -118.4868 | -70.64 | -119.7621 | 0.057037 | 0.22432 | 0.07643 | -123.1237 | 122.6771 | -0.048572 | 122.6634 | 122.6631 | -0.014038 | -0.07286 | 0.12826 | -0.46593 | -0.098603 | 4.171 | 2.8956 | 3.3616 | 0.068682 | -0.07921 | 122.7648 | 122.7406 | 122.9417 | 122.6775 | -0.13628 | 122.7148 | 122.8821 | 122.7342 | 52.0178 | -123.2793
2584.2344 | 122.8867 | -122.6852 | 0.1831 | 1.4211e-13 | -0.012132 | -0.013077 | -0.045598 | -0.04107 | -0.012138 | 0.0067908 | -0.015153 | 0.010662 | 0.036205 | 0.011226 | 0.040974 | 0.010204 | 0.028878 | 0.000747 | 0.10707 | 0.073622 | 0.28848 | 0.028521 | -118.4227 | -73.1079 | -119.4874 | 0.061616 | 0.21516 | 0.081008 | -123.1329 | 122.7138 | -0.076037 | 122.6954 | 122.686 | -0.027774 | -0.10948 | 0.10538 | -0.44762 | -0.12149 | 4.2625 | 3.1978 | 3.6454 | 0.03206 | -0.1021 | 122.7923 | 122.7589 | 122.9737 | 122.7141 | -0.15458 | 122.7469 | 122.9004 | 122.7662 | 49.5773 | -123.316
2586.0312 | 122.8729 | -122.6761 | 0.19226 | 1.4211e-13 | -0.011919 | -0.013505 | -0.04517 | -0.040857 | -0.011711 | 0.0067908 | -0.015367 | 0.010448 | 0.036632 | 0.010799 | 0.040974 | 0.010204 | 0.015142 | 0.005325 | 0.11165 | 0.073622 | 0.28848 | 0.010206 | -118.3357 | -73.4147 | -119.405 | 0.057037 | 0.21974 | 0.094744 | -123.1283 | 122.6863 | -0.080614 | 122.6863 | 122.6814 | -0.004881 | -0.11864 | 0.09622 | -0.4522 | -0.13522 | 4.3404 | 3.2711 | 3.7233 | 0.027483 | -0.097517 | 122.7877 | 122.7497 | 122.9646 | 122.6912 | -0.18205 | 122.7331 | 122.8958 | 122.7708 | 49.2614 | -123.3205
2587.75 | 122.9462 | -122.6395 | 0.1831 | 1.4211e-13 | -0.012132 | -0.013291 | -0.04517 | -0.041284 | -0.011924 | -0.00083919 | -0.015581 | 0.010448 | 0.036205 | 0.011226 | 0.040974 | 0.014783 | 0.010564 | 0.005325 | 0.11165 | 0.073622 | 0.28848 | 0.023942 | -118.1938 | -74.683 | -119.373 | 0.07993 | 0.23806 | 0.1039 | -123.1008 | 122.6634 | -0.071458 | 122.6542 | 122.6448 | -0.018617 | -0.10948 | 0.10538 | -0.46135 | -0.10317 | 4.4457 | 3.2665 | 3.7279 | 0.054953 | -0.079204 | 122.7511 | 122.7131 | 122.9279 | 122.65 | -0.15916 | 122.7194 | 122.8775 | 122.7434 | 47.9565 | -123.2839
2589.4688 | 122.8821 | -122.6624 | 0.21973 | 1.4211e-13 | -0.012132 | -0.013291 | -0.045384 | -0.040857 | -0.011711 | -0.0161 | -0.015367 | 0.010662 | 0.035991 | 0.011013 | 0.041402 | 0.005626 | 0.0243 | 0.005325 | 0.11165 | 0.08278 | 0.2839 | 0.023942 | -118.093 | -74.9394 | -119.3134 | 0.089087 | 0.25179 | 0.1039 | -123.1008 | 122.6863 | -0.10808 | 122.668 | 122.6677 | -0.018617 | -0.13695 | 0.064176 | -0.43846 | -0.13064 | 4.5693 | 3.3489 | 3.7874 | 0.032067 | -0.11583 | 122.774 | 122.7451 | 122.9463 | 122.6867 | -0.19579 | 122.7514 | 122.9141 | 122.7663 | 47.723 | -123.3205
2591.25 | 122.905 | -122.6578 | 0.21515 | 1.4211e-13 | -0.011919 | -0.013718 | -0.045384 | -0.040857 | -0.011711 | 0.0067908 | -0.015153 | 0.010234 | 0.036205 | 0.01144 | 0.041188 | 0.010204 | 0.019721 | 0.009904 | 0.11165 | 0.078201 | 0.28848 | 0.019363 | -117.9648 | -75.118 | -119.2493 | 0.084508 | 0.25179 | 0.099323 | -123.1008 | 122.6771 | -0.1035 | 122.668 | 122.6677 | -0.009459 | -0.13695 | 0.073332 | -0.44304 | -0.13064 | 4.6929 | 3.4085 | 3.8515 | 0.036645 | -0.11583 | 122.7694 | 122.736 | 122.9463 | 122.6775 | -0.19579 | 122.7423 | 122.9096 | 122.7571 | 47.5398 | -123.316
2592.9844 | 122.9279 | -122.6257 | 0.21057 | 1.4211e-13 | -0.011919 | -0.013291 | -0.04517 | -0.041284 | -0.011711 | -0.00083919 | -0.015367 | 0.010875 | 0.036205 | 0.011226 | 0.041188 | 0.005626 | 0.028878 | 0.005325 | 0.11165 | 0.087359 | 0.28848 | 0.023942 | -117.8687 | -75.3423 | -119.1806 | 0.093665 | 0.25637 | 0.11306 | -123.0962 | 122.6497 | -0.098924 | 122.6314 | 122.6311 | -0.018617 | -0.12321 | 0.07791 | -0.4705 | -0.11691 | 4.7571 | 3.4451 | 3.9156 | 0.045801 | -0.097512 | 122.7374 | 122.7131 | 122.9142 | 122.6546 | -0.18663 | 122.7194 | 122.8821 | 122.7388 | 47.2834 | -123.3068
2594.7812 | 122.9874 | -122.6303 | 0.1831 | 1.4211e-13 | -0.012346 | -0.013505 | -0.045384 | -0.040857 | -0.011711 | -0.0161 | -0.015367 | 0.010875 | 0.036205 | 0.011226 | 0.041402 | 0.010204 | 0.0243 | 0.005325 | 0.10707 | 0.078201 | 0.2839 | 0.028521 | -117.7817 | -75.6079 | -119.1349 | 0.093665 | 0.24264 | 0.099323 | -123.1008 | 122.6588 | -0.076037 | 122.6405 | 122.6356 | -0.023196 | -0.1049 | 0.1008 | -0.4705 | -0.08944 | 4.8486 | 3.4955 | 3.966 | 0.059532 | -0.083782 | 122.7374 | 122.7085 | 122.9142 | 122.6546 | -0.15458 | 122.724 | 122.8729 | 122.7296 | 47.0224 | -123.2839
2596.5625 | 122.9279 | -122.6578 | 0.20142 | 1.4211e-13 | -0.01256 | -0.013505 | -0.045384 | -0.040857 | -0.011711 | -0.00083919 | -0.015153 | 0.010662 | 0.036205 | 0.011226 | 0.041188 | 0.005626 | 0.019721 | 0.005325 | 0.11165 | 0.078201 | 0.28848 | 0.0331 | -117.6672 | -75.6903 | -119.0662 | 0.084508 | 0.24721 | 0.094744 | -123.1008 | 122.6909 | -0.089769 | 122.6634 | 122.6631 | -0.027775 | -0.12322 | 0.087065 | -0.44304 | -0.11691 | 4.9906 | 3.5916 | 4.0346 | 0.045799 | -0.10667 | 122.7694 | 122.736 | 122.9463 | 122.6775 | -0.16832 | 122.7423 | 122.905 | 122.7525 | 46.9675 | -123.3022
2598.3594 | 122.9782 | -122.6166 | 0.16937 | 1.4211e-13 | -0.012346 | -0.013291 | -0.045598 | -0.041284 | -0.011711 | -0.0084697 | -0.015367 | 0.010875 | 0.036418 | 0.011226 | 0.041615 | 0.005626 | 0.015142 | 0.009904 | 0.10707 | 0.078201 | 0.29306 | 0.014784 | -117.5573 | -75.8505 | -118.9883 | 0.089087 | 0.25179 | 0.1039 | -123.0962 | 122.6314 | -0.062305 | 122.6222 | 122.6265 | -0.00488 | -0.091172 | 0.12369 | -0.47966 | -0.080286 | 5.0592 | 3.6282 | 4.1079 | 0.082421 | -0.065472 | 122.7236 | 122.6948 | 122.9096 | 122.6317 | -0.15459 | 122.7057 | 122.8684 | 122.7205 | 46.766 | -123.2656
2600.0781 | 122.9919 | -122.6303 | 0.16022 | 1.4211e-13 | -0.012346 | -0.013932 | -0.045384 | -0.04107 | -0.011711 | -0.00083919 | -0.015153 | 0.010875 | 0.036418 | 0.01144 | 0.041615 | 0.010204 | 0.0243 | 0.005325 | 0.10707 | 0.078201 | 0.2839 | 0.010206 | -117.452 | -76.0337 | -118.9242 | 0.084508 | 0.23806 | 0.094744 | -123.1054 | 122.6405 | -0.053149 | 122.6405 | 122.6356 | -0.004881 | -0.082016 | 0.12369 | -0.47508 | -0.075709 | 5.1783 | 3.7061 | 4.1812 | 0.077841 | -0.065473 | 122.7374 | 122.7085 | 122.9142 | 122.6546 | -0.15001 | 122.7148 | 122.8684 | 122.7251 | 46.5966 | -123.2656
2601.8594 | 122.9965 | -122.6532 | 0.15564 | 1.4211e-13 | -0.012132 | -0.013505 | -0.045384 | -0.041498 | -0.011924 | -0.0084697 | -0.015367 | 0.010662 | 0.036632 | 0.01144 | 0.041402 | 0.005626 | 0.0243 | 0.000747 | 0.10707 | 0.078201 | 0.28848 | 0.028521 | -117.333 | -75.2004 | -118.8327 | 0.07993 | 0.24264 | 0.10848 | -123.0962 | 122.6817 | -0.048572 | 122.6588 | 122.6539 | -0.027774 | -0.077439 | 0.13284 | -0.44303 | -0.07571 | 5.3202 | 3.8205 | 4.2636 | 0.086997 | -0.04716 | 122.7603 | 122.7314 | 122.9417 | 122.6775 | -0.12712 | 122.7331 | 122.8958 | 122.7617 | 47.4528 | -123.2519
2603.6406 | 123.024 | -122.6212 | 0.1831 | 1.4211e-13 | -0.012132 | -0.013932 | -0.045384 | -0.04107 | -0.011924 | 0.0067908 | -0.015367 | 0.010662 | 0.036632 | 0.011654 | 0.041829 | 0.005626 | 0.015142 | 0.005325 | 0.11165 | 0.078201 | 0.29306 | 0.014784 | -117.4886 | -76.6976 | -118.8052 | 0.084508 | 0.24721 | 0.090166 | -123.1054 | 122.6359 | -0.071458 | 122.6268 | 122.6265 | -0.009459 | -0.1049 | 0.10995 | -0.48423 | -0.098597 | 5.1325 | 3.816 | 4.3002 | 0.06411 | -0.092939 | 122.7328 | 122.6994 | 122.9142 | 122.6363 | -0.16832 | 122.7057 | 122.8684 | 122.7113 | 45.9235 | -123.2885
2605.4375 | 122.9279 | -122.6624 | 0.19684 | 1.4211e-13 | -0.012346 | -0.013718 | -0.045598 | -0.04107 | -0.011711 | -0.0161 | -0.015153 | 0.010662 | 0.036632 | 0.011226 | 0.042256 | 0.010204 | 0.0243 | 0.005325 | 0.11622 | 0.073622 | 0.2839 | 0.019363 | -117.4245 | -77.3707 | -118.7365 | 0.093665 | 0.24264 | 0.1039 | -123.0962 | 122.6817 | -0.080613 | 122.6726 | 122.6677 | -0.014038 | -0.12322 | 0.087065 | -0.43388 | -0.10317 | 5.2378 | 3.9258 | 4.3597 | 0.045799 | -0.092937 | 122.7786 | 122.736 | 122.9463 | 122.6867 | -0.17748 | 122.756 | 122.905 | 122.7663 | 45.2917 | -123.2931
2607.1562 | 122.9965 | -122.644 | 0.1831 | 1.4211e-13 | -0.011919 | -0.013291 | -0.045384 | -0.041284 | -0.011924 | -0.00083919 | -0.015153 | 0.010875 | 0.037059 | 0.011654 | 0.042256 | 0.010204 | 0.019721 | 0.000747 | 0.11622 | 0.073622 | 0.28848 | 0.028521 | -117.3375 | -77.7232 | -118.6633 | 0.084508 | 0.24721 | 0.099323 | -123.1054 | 122.6726 | -0.06688 | 122.6542 | 122.6448 | -0.027774 | -0.10948 | 0.10538 | -0.46135 | -0.098597 | 5.3065 | 3.9808 | 4.4421 | 0.06411 | -0.083782 | 122.7603 | 122.7177 | 122.9325 | 122.6638 | -0.15458 | 122.7286 | 122.8913 | 122.7434 | 44.9208 | -123.2885
2608.9375 | 122.9187 | -122.6578 | 0.19226 | 1.4211e-13 | -0.012346 | -0.013505 | -0.045598 | -0.04107 | -0.011711 | -0.0084697 | -0.015153 | 0.010875 | 0.036846 | 0.011867 | 0.042256 | 0.010204 | 0.019721 | 0.005325 | 0.10707 | 0.069043 | 0.27932 | 0.014784 | -117.2414 | -78.0071 | -118.5854 | 0.089087 | 0.24264 | 0.099323 | -123.1054 | 122.6726 | -0.085193 | 122.668 | 122.6631 | -0.009459 | -0.12322 | 0.087063 | -0.44761 | -0.10317 | 5.4164 | 4.0724 | 4.52 | 0.050376 | -0.092938 | 122.7648 | 122.7268 | 122.9371 | 122.6775 | -0.17748 | 122.7469 | 122.9004 | 122.7571 | 44.6507 | -123.2977
2610.7344 | 122.8867 | -122.6624 | 0.21057 | 1.4211e-13 | -0.012346 | -0.013718 | -0.04517 | -0.040857 | -0.011711 | -0.0084697 | -0.015153 | 0.010875 | 0.037273 | 0.011867 | 0.042043 | 0.010204 | 0.0243 | -0.003831 | 0.10707 | 0.078201 | 0.2839 | 0.028521 | -117.1315 | -78.2681 | -118.4984 | 0.084508 | 0.23806 | 0.099323 | -123.0962 | 122.6909 | -0.1035 | 122.6726 | 122.6585 | -0.032352 | -0.13237 | 0.073332 | -0.43388 | -0.12606 | 5.5308 | 4.1639 | 4.5978 | 0.027487 | -0.11125 | 122.7694 | 122.7406 | 122.9463 | 122.6867 | -0.18205 | 122.7469 | 122.9004 | 122.7617 | 44.3942 | -123.3068
2612.5312 | 122.9874 | -122.6303 | 0.1831 | 1.4211e-13 | -0.012346 | -0.013718 | -0.045598 | -0.04107 | -0.012138 | -0.00083919 | -0.015153 | 0.010875 | 0.037273 | 0.011867 | 0.04247 | 0.005626 | 0.0243 | 0.005325 | 0.11165 | 0.08278 | 0.28848 | 0.023942 | -117.0308 | -78.4879 | -118.4252 | 0.084508 | 0.24264 | 0.094744 | -123.11 | 122.6543 | -0.071458 | 122.6359 | 122.6356 | -0.018617 | -0.10032 | 0.10538 | -0.47966 | -0.098597 | 5.5995 | 4.2052 | 4.6848 | 0.059532 | -0.088361 | 122.742 | 122.7131 | 122.9188 | 122.6546 | -0.15916 | 122.7148 | 122.8729 | 122.7251 | 44.1424 | -123.2931
2614.2656 | 122.9874 | -122.6349 | 0.18768 | 1.4211e-13 | -0.012346 | -0.013291 | -0.045384 | -0.04107 | -0.011711 | -0.00083919 | -0.015153 | 0.010662 | 0.037487 | 0.012081 | 0.042256 | 0.001048 | 0.015142 | 0.005325 | 0.11165 | 0.08278 | 0.27475 | 0.014784 | -116.9255 | -78.6344 | -118.329 | 0.093665 | 0.23806 | 0.1039 | -123.1054 | 122.6497 | -0.076036 | 122.6359 | 122.6402 | -0.009459 | -0.1049 | 0.087062 | -0.4705 | -0.094018 | 5.7094 | 4.3059 | 4.7764 | 0.050375 | -0.083782 | 122.7465 | 122.7177 | 122.9096 | 122.65 | -0.1729 | 122.7286 | 122.8729 | 122.7388 | 44.0005 | -123.2931
2616.0312 | 122.9874 | -122.6624 | 0.16937 | 1.4211e-13 | -0.012346 | -0.013291 | -0.04517 | -0.040857 | -0.011711 | -0.00083919 | -0.015153 | 0.011303 | 0.037273 | 0.012081 | 0.042897 | 0.005626 | 0.0243 | 0.009904 | 0.11165 | 0.078201 | 0.28848 | 0.023942 | -116.7377 | -78.4146 | -118.2924 | 0.075351 | 0.23348 | 0.085587 | -123.1145 | 122.6863 | -0.057726 | 122.668 | 122.6723 | -0.014038 | -0.091172 | 0.11911 | -0.45219 | -0.094022 | 5.9246 | 4.37 | 4.8222 | 0.064106 | -0.083786 | 122.774 | 122.7406 | 122.9508 | 122.6867 | -0.14543 | 122.7377 | 122.8958 | 122.7479 | 44.2477 | -123.2839
2617.8125 | 123.0011 | -122.6578 | 0.15106 | 1.4211e-13 | -0.012346 | -0.013505 | -0.045384 | -0.04107 | -0.011924 | -0.00083919 | -0.015153 | 0.011303 | 0.037273 | 0.012295 | 0.042684 | 0.005626 | 0.019721 | 0.009904 | 0.10707 | 0.078201 | 0.28848 | 0.023942 | -116.5775 | -78.4879 | -118.21 | 0.066194 | 0.23806 | 0.085587 | -123.1237 | 122.6817 | -0.043994 | 122.6634 | 122.6677 | -0.014038 | -0.072861 | 0.13742 | -0.46593 | -0.084868 | 6.0803 | 4.4478 | 4.9137 | 0.086996 | -0.065475 | 122.7648 | 122.736 | 122.9463 | 122.6775 | -0.12712 | 122.724 | 122.8958 | 122.7434 | 44.1699 | -123.2748
2619.6094 | 123.0148 | -122.6532 | 0.14648 | 1.4211e-13 | -0.012132 | -0.013291 | -0.04517 | -0.041284 | -0.011711 | -0.00083919 | -0.01494 | 0.01173 | 0.037487 | 0.012295 | 0.042684 | 0.010204 | 0.010564 | 0.000747 | 0.10707 | 0.078201 | 0.29306 | 0.014784 | -116.4447 | -78.5428 | -118.1092 | 0.052459 | 0.21059 | 0.081008 | -123.1329 | 122.668 | -0.039416 | 122.6634 | 122.6539 | -0.014037 | -0.068283 | 0.14658 | -0.47966 | -0.094025 | 6.2085 | 4.544 | 5.0236 | 0.064102 | -0.065476 | 122.7603 | 122.7314 | 122.9463 | 122.6638 | -0.1317 | 122.7057 | 122.8638 | 122.7342 | 44.1104 | -123.2793
2621.3438 | 122.9279 | -122.6715 | 0.17395 | 1.4211e-13 | -0.011919 | -0.013505 | -0.045384 | -0.040857 | -0.012138 | 0.0067908 | -0.014726 | 0.011516 | 0.037273 | 0.012081 | 0.042897 | 0.010204 | 0.015142 | 0.009904 | 0.11165 | 0.073622 | 0.2839 | 0.019363 | -116.2936 | -78.5199 | -118.0405 | 0.057037 | 0.21059 | 0.07643 | -123.142 | 122.6909 | -0.062303 | 122.6817 | 122.6814 | -0.009459 | -0.10033 | 0.10995 | -0.47051 | -0.11691 | 6.3779 | 4.631 | 5.1015 | 0.036636 | -0.09752 | 122.7832 | 122.7451 | 122.9554 | 122.6867 | -0.15459 | 122.7285 | 122.8821 | 122.7479 | 44.1516 | -123.316
2623.125 | 122.9141 | -122.6761 | 0.1831 | 1.4211e-13 | -0.012346 | -0.013291 | -0.045384 | -0.04107 | -0.012138 | -0.00083919 | -0.01494 | 0.01173 | 0.037487 | 0.012295 | 0.043538 | 0.010204 | 0.015142 | 0.000747 | 0.11165 | 0.078201 | 0.27932 | 0.019363 | -116.1562 | -78.6207 | -117.9536 | 0.052459 | 0.21974 | 0.071851 | -123.1374 | 122.6954 | -0.071458 | 122.6863 | 122.6768 | -0.018616 | -0.1049 | 0.096219 | -0.46136 | -0.13065 | 6.5198 | 4.7225 | 5.1839 | 0.036639 | -0.11125 | 122.7877 | 122.7543 | 122.9554 | 122.6912 | -0.16374 | 122.7285 | 122.8958 | 122.7479 | 44.0554 | -123.3205
2624.8438 | 123.0057 | -122.6257 | 0.15106 | 1.4211e-13 | -0.01256 | -0.013505 | -0.045384 | -0.041498 | -0.011924 | -0.0161 | -0.01494 | 0.011944 | 0.037487 | 0.012722 | 0.043111 | 0.005626 | 0.0243 | 0.005325 | 0.10707 | 0.08278 | 0.28848 | 0.0331 | -116.0006 | -78.6985 | -117.8574 | 0.052459 | 0.21516 | 0.07643 | -123.142 | 122.6588 | -0.043994 | 122.6314 | 122.6311 | -0.027775 | -0.068282 | 0.13742 | -0.51629 | -0.098603 | 6.6252 | 4.7683 | 5.2846 | 0.064103 | -0.074632 | 122.7328 | 122.7085 | 122.9142 | 122.65 | -0.11796 | 122.6782 | 122.8409 | 122.7022 | 43.9272 | -123.2931
2626.6406 | 122.9645 | -122.6532 | 0.16022 | 1.4211e-13 | -0.012346 | -0.013505 | -0.04517 | -0.04107 | -0.012138 | -0.0084697 | -0.015153 | 0.01173 | 0.0377 | 0.012508 | 0.043752 | 0.010204 | 0.019721 | 0.009904 | 0.10707 | 0.078201 | 0.29306 | 0.014784 | -115.854 | -78.7443 | -117.7704 | 0.057037 | 0.21974 | 0.081008 | -123.1329 | 122.668 | -0.053149 | 122.6634 | 122.6631 | -0.00488 | -0.082016 | 0.13284 | -0.47966 | -0.10318 | 6.7991 | 4.8828 | 5.3625 | 0.059527 | -0.079209 | 122.7603 | 122.7314 | 122.9463 | 122.6729 | -0.14543 | 122.7102 | 122.8729 | 122.7342 | 43.9089 | -123.2931
2628.4219 | 122.85 | -122.7081 | 0.19226 | 1.4211e-13 | -0.01256 | -0.013077 | -0.044957 | -0.040643 | -0.011711 | -0.00083919 | -0.014726 | 0.011944 | 0.037914 | 0.012508 | 0.043538 | 0.005626 | 0.019721 | 0.000747 | 0.10249 | 0.078201 | 0.2839 | 0.019363 | -115.6892 | -78.758 | -117.6559 | 0.052459 | 0.21974 | 0.085587 | -123.142 | 122.7275 | -0.089771 | 122.7138 | 122.7089 | -0.018616 | -0.11406 | 0.091642 | -0.43389 | -0.1398 | 7.0189 | 5.0522 | 5.4861 | 0.027483 | -0.10667 | 122.8106 | 122.7863 | 122.992 | 122.7279 | -0.1729 | 122.7606 | 122.9279 | 122.7937 | 43.9501 | -123.3343
2630.1562 | 122.9599 | -122.6486 | 0.13275 | 1.4211e-13 | -0.01256 | -0.013291 | -0.045598 | -0.041498 | -0.011711 | -0.00083919 | -0.01494 | 0.01173 | 0.037914 | 0.012722 | 0.044179 | 0.010204 | 0.015142 | 0.009904 | 0.11165 | 0.08278 | 0.28848 | 0.019363 | -115.5427 | -78.7214 | -117.5781 | 0.057037 | 0.21516 | 0.081008 | -123.1374 | 122.668 | -0.021104 | 122.6588 | 122.6585 | -0.009459 | -0.049971 | 0.15573 | -0.48882 | -0.075714 | 7.1059 | 5.0705 | 5.5593 | 0.082414 | -0.051743 | 122.7603 | 122.7314 | 122.9371 | 122.6638 | -0.11339 | 122.7057 | 122.8638 | 122.7296 | 43.9272 | -123.2702
2631.9375 | 122.9828 | -122.6852 | 0.16022 | 1.4211e-13 | -0.01256 | -0.013505 | -0.04517 | -0.040857 | -0.011924 | -0.00083919 | -0.015153 | 0.011944 | 0.038341 | 0.012508 | 0.044179 | 0.014783 | 0.028878 | 0.005325 | 0.10707 | 0.078201 | 0.28848 | 0.014784 | -115.3824 | -78.7397 | -117.4728 | 0.052459 | 0.21516 | 0.081008 | -123.142 | 122.7 | -0.053149 | 122.7 | 122.6906 | -0.009459 | -0.082016 | 0.12826 | -0.45678 | -0.10776 | 7.3028 | 5.2125 | 5.6692 | 0.054948 | -0.079209 | 122.7923 | 122.7634 | 122.9737 | 122.7141 | -0.14543 | 122.7377 | 122.9004 | 122.7662 | 43.9455 | -123.3022
2633.7344 | 123.0011 | -122.6578 | 0.12817 | 1.4211e-13 | -0.012346 | -0.013291 | -0.045384 | -0.041284 | -0.011924 | -0.00083919 | -0.015153 | 0.012157 | 0.038341 | 0.012722 | 0.044393 | 0.010204 | 0.019721 | 0.009904 | 0.10707 | 0.078201 | 0.28848 | 0.010206 | -115.2176 | -78.6527 | -117.3904 | 0.052459 | 0.21974 | 0.071851 | -123.1374 | 122.668 | -0.021106 | 122.668 | 122.6677 | -0.000302 | -0.049973 | 0.16031 | -0.47967 | -0.075715 | 7.4402 | 5.2674 | 5.7471 | 0.09157 | -0.056323 | 122.7648 | 122.736 | 122.9463 | 122.6775 | -0.11797 | 122.7102 | 122.8775 | 122.7296 | 44.0051 | -123.2656
2635.5312 | 122.9965 | -122.6807 | 0.14648 | 1.4211e-13 | -0.012346 | -0.013505 | -0.044957 | -0.04107 | -0.012138 | -0.00083919 | -0.01494 | 0.012157 | 0.037914 | 0.012722 | 0.044393 | 0.014783 | 0.0243 | 0.009904 | 0.11622 | 0.073622 | 0.2839 | 0.019363 | -115.0528 | -78.6069 | -117.2805 | 0.052459 | 0.21516 | 0.035222 | -123.1374 | 122.7 | -0.030259 | 122.6954 | 122.6906 | -0.009459 | -0.072862 | 0.13742 | -0.45678 | -0.094025 | 7.6279 | 5.4002 | 5.857 | 0.068681 | -0.11126 | 122.7969 | 122.7543 | 122.9646 | 122.705 | -0.12712 | 122.7331 | 122.8958 | 122.7159 | 44.0737 | -123.2839
2637.25 | 122.9507 | -122.6486 | 0.13733 | 1.4211e-13 | -0.012773 | -0.013505 | -0.045384 | -0.041498 | -0.011924 | -0.00083919 | -0.014726 | 0.012584 | 0.038341 | 0.012936 | 0.044607 | 0.010204 | 0.019721 | 0.005325 | 0.10249 | 0.08278 | 0.28848 | 0.019363 | -114.8879 | -78.6756 | -117.1523 | 0.052459 | 0.21516 | 0.081008 | -123.1512 | 122.668 | -0.034839 | 122.6588 | 122.6539 | -0.014038 | -0.054549 | 0.15115 | -0.50256 | -0.08487 | 7.7607 | 5.4963 | 5.9989 | 0.077836 | -0.056321 | 122.7511 | 122.7314 | 122.9371 | 122.6683 | -0.11797 | 122.7011 | 122.8638 | 122.7296 | 43.973 | -123.2885
2639.0156 | 123.024 | -122.6624 | 0.14648 | 1.4211e-13 | -0.012773 | -0.013718 | -0.045384 | -0.040857 | -0.011711 | 0.0067908 | -0.01494 | 0.012584 | 0.038555 | 0.013149 | 0.04482 | 0.010204 | 0.019721 | 0.005325 | 0.11165 | 0.078201 | 0.2839 | 0.014784 | -114.7231 | -78.5428 | -117.0836 | 0.043302 | 0.21516 | 0.067272 | -123.142 | 122.6771 | -0.034837 | 122.6726 | 122.6677 | -0.009459 | -0.068283 | 0.13742 | -0.47967 | -0.10318 | 7.9392 | 5.5788 | 6.0584 | 0.068681 | -0.079212 | 122.774 | 122.7406 | 122.9463 | 122.6821 | -0.1317 | 122.7057 | 122.8775 | 122.7296 | 44.1195 | -123.2885
2640.7656 | 123.0194 | -122.6669 | 0.12817 | 1.4211e-13 | -0.01256 | -0.013505 | -0.04517 | -0.041498 | -0.012138 | -0.00083919 | -0.014726 | 0.012371 | 0.038768 | 0.013363 | 0.045034 | 0.005626 | 0.019721 | 0.000747 | 0.10707 | 0.078201 | 0.28848 | 0.019363 | -114.6132 | -78.552 | -116.9508 | 0.043302 | 0.21059 | 0.07643 | -123.1512 | 122.6863 | -0.021106 | 122.6726 | 122.6677 | -0.018616 | -0.049973 | 0.16031 | -0.48425 | -0.084872 | 8.0537 | 5.7161 | 6.2004 | 0.082412 | -0.051744 | 122.774 | 122.7451 | 122.9554 | 122.6867 | -0.10881 | 122.7102 | 122.8775 | 122.7434 | 44.1149 | -123.2794
2642.5625 | 123.0103 | -122.6761 | 0.13733 | 1.4211e-13 | -0.012346 | -0.013505 | -0.04517 | -0.041284 | -0.011497 | -0.0084697 | -0.01494 | 0.012798 | 0.038555 | 0.013149 | 0.045248 | 0.010204 | 0.0243 | 0.009904 | 0.10707 | 0.078201 | 0.2839 | 0.0331 | -114.4209 | -78.584 | -116.8547 | 0.04788 | 0.21516 | 0.07643 | -123.142 | 122.7092 | -0.030261 | 122.6863 | 122.686 | -0.023196 | -0.059128 | 0.14657 | -0.46594 | -0.089449 | 8.2552 | 5.8214 | 6.2874 | 0.077836 | -0.060899 | 122.7832 | 122.7543 | 122.96 | 122.7004 | -0.10423 | 122.724 | 122.8913 | 122.7525 | 44.092 | -123.2793
2644.3438 | 122.8867 | -122.7127 | 0.16022 | 1.4211e-13 | -0.012773 | -0.013718 | -0.04517 | -0.041284 | -0.011711 | 0.0067908 | -0.014726 | 0.013012 | 0.038768 | 0.013149 | 0.045461 | 0.010204 | 0.019721 | 0.005325 | 0.11165 | 0.08278 | 0.28848 | 0.014784 | -114.311 | -78.639 | -116.731 | 0.04788 | 0.21974 | 0.071851 | -123.1466 | 122.7275 | -0.04857 | 122.7229 | 122.718 | -0.009459 | -0.077437 | 0.12826 | -0.43389 | -0.11234 | 8.4017 | 5.9817 | 6.4156 | 0.059527 | -0.088366 | 122.8244 | 122.7955 | 123.0012 | 122.7324 | -0.14543 | 122.7606 | 122.9325 | 122.7846 | 44.0737 | -123.3068
2646.1406 | 122.8775 | -122.6944 | 0.1831 | 1.4211e-13 | -0.012773 | -0.013291 | -0.045384 | -0.04107 | -0.012138 | 0.0067908 | -0.01494 | 0.013225 | 0.038982 | 0.013363 | 0.045675 | 0.005626 | 0.015142 | 0.009904 | 0.10707 | 0.073622 | 0.2839 | 0.019363 | -114.1416 | -78.6024 | -116.5937 | 0.052459 | 0.21059 | 0.062694 | -123.142 | 122.7138 | -0.076037 | 122.7 | 122.7043 | -0.009459 | -0.10948 | 0.1008 | -0.44762 | -0.13065 | 8.5528 | 6.1007 | 6.5483 | 0.027481 | -0.12041 | 122.8015 | 122.768 | 122.9783 | 122.7095 | -0.16374 | 122.7469 | 122.905 | 122.7571 | 44.092 | -123.3251
2647.9219 | 122.937 | -122.6761 | 0.16937 | 1.4211e-13 | -0.012773 | -0.013932 | -0.044957 | -0.04107 | -0.011924 | -0.0161 | -0.014513 | 0.013225 | 0.038768 | 0.013363 | 0.045675 | 0.001048 | 0.0243 | 0.014482 | 0.11622 | 0.069043 | 0.28848 | 0.028521 | -114.0088 | -78.639 | -116.4655 | 0.04788 | 0.20601 | 0.071851 | -123.142 | 122.7046 | -0.053148 | 122.6771 | 122.6906 | -0.014039 | -0.10033 | 0.11911 | -0.46594 | -0.12149 | 8.6673 | 6.2106 | 6.6766 | 0.036635 | -0.097522 | 122.7923 | 122.7451 | 122.9646 | 122.7004 | -0.14085 | 122.724 | 122.8821 | 122.7479 | 44.0371 | -123.3114
2649.7031 | 123.0011 | -122.6669 | 0.11444 | 1.4211e-13 | -0.01256 | -0.013505 | -0.04517 | -0.041284 | -0.011711 | -0.00083919 | -0.01494 | 0.013439 | 0.038982 | 0.01379 | 0.046102 | 0.005626 | 0.019721 | 0.000747 | 0.10707 | 0.091937 | 0.2839 | 0.014784 | -113.8532 | -78.552 | -116.3418 | 0.038723 | 0.20601 | 0.071851 | -123.142 | 122.6817 | -0.007373 | 122.6726 | 122.6677 | -0.014037 | -0.022504 | 0.16946 | -0.47509 | -0.075718 | 8.8138 | 6.3251 | 6.8002 | 0.091567 | -0.04259 | 122.774 | 122.7589 | 122.9508 | 122.6867 | -0.099657 | 122.7057 | 122.8729 | 122.7388 | 44.1149 | -123.2565
2651.4375 | 123.0148 | -122.6807 | 0.1236 | 1.4211e-13 | -0.01256 | -0.013718 | -0.045384 | -0.041284 | -0.011924 | -0.00083919 | -0.01494 | 0.013439 | 0.039196 | 0.01379 | 0.046316 | 0.014783 | 0.019721 | 0.005325 | 0.10707 | 0.078201 | 0.29306 | 0.023942 | -113.7112 | -78.584 | -116.2182 | 0.043302 | 0.20601 | 0.044379 | -123.1512 | 122.7046 | -0.016528 | 122.6954 | 122.686 | -0.018617 | -0.045395 | 0.16946 | -0.47052 | -0.080294 | 8.9695 | 6.4624 | 6.933 | 0.082412 | -0.079217 | 122.7877 | 122.7589 | 122.9737 | 122.7004 | -0.099654 | 122.724 | 122.8867 | 122.725 | 44.0966 | -123.2748
2653.2031 | 122.8821 | -122.731 | 0.16937 | 1.4211e-13 | -0.01256 | -0.013505 | -0.04517 | -0.04107 | -0.012138 | -0.0084697 | -0.014513 | 0.013653 | 0.039623 | 0.01379 | 0.046316 | 0.014783 | 0.0243 | 0.009904 | 0.11165 | 0.08278 | 0.28848 | 0.023942 | -113.5464 | -78.6344 | -116.1083 | 0.04788 | 0.20601 | 0.012329 | -123.1466 | 122.755 | -0.057726 | 122.7458 | 122.7409 | -0.014038 | -0.086593 | 0.11911 | -0.41558 | -0.12149 | 9.1846 | 6.6227 | 7.0383 | 0.036635 | -0.15704 | 122.8427 | 122.8138 | 123.0195 | 122.7553 | -0.14543 | 122.7789 | 122.937 | 122.7433 | 44.0966 | -123.316
2654.9375 | 122.8043 | -122.7127 | 0.17853 | 1.4211e-13 | -0.01256 | -0.013718 | -0.04517 | -0.041284 | -0.011924 | -0.00083919 | -0.014726 | 0.013439 | 0.039196 | 0.014004 | 0.046529 | 0.005626 | 0.019721 | 0.000747 | 0.10707 | 0.073622 | 0.29306 | 0.010206 | -113.4228 | -78.6207 | -115.9664 | 0.038723 | 0.19685 | 0.067272 | -123.1512 | 122.7229 | -0.07146 | 122.7183 | 122.7135 | -0.009459 | -0.10491 | 0.11453 | -0.43847 | -0.1398 | 9.29 | 6.7463 | 7.1848 | 0.018323 | -0.11126 | 122.8198 | 122.7863 | 123.0058 | 122.7324 | -0.16832 | 122.7514 | 122.9096 | 122.78 | 44.092 | -123.3297
2656.7188 | 123.0194 | -122.6761 | 0.13275 | 1.4211e-13 | -0.01256 | -0.013291 | -0.04517 | -0.041284 | -0.011497 | -0.00083919 | -0.014726 | 0.013653 | 0.039623 | 0.014004 | 0.046529 | 0.010204 | 0.019721 | 0.000747 | 0.10707 | 0.073622 | 0.27932 | 0.023942 | -113.3037 | -78.8084 | -115.8382 | 0.04788 | 0.21059 | 0.062694 | -123.1512 | 122.7 | -0.025683 | 122.6863 | 122.6768 | -0.023195 | -0.059129 | 0.14657 | -0.47509 | -0.084871 | 9.3724 | 6.8379 | 7.313 | 0.077835 | -0.070057 | 122.7832 | 122.7497 | 122.9554 | 122.6958 | -0.10881 | 122.724 | 122.8867 | 122.7388 | 43.8677 | -123.2839
2658.4375 | 122.9141 | -122.7402 | 0.1831 | 1.4211e-13 | -0.01256 | -0.013718 | -0.045384 | -0.04107 | -0.011711 | -0.00083919 | -0.014726 | 0.013439 | 0.039837 | 0.014218 | 0.046529 | 0.010204 | 0.019721 | 0.009904 | 0.10707 | 0.069043 | 0.28848 | 0.019363 | -113.1526 | -78.8267 | -115.7008 | 0.043302 | 0.20601 | 0.053537 | -123.142 | 122.7595 | -0.076037 | 122.7504 | 122.7501 | -0.009459 | -0.11406 | 0.10538 | -0.40185 | -0.1398 | 9.5876 | 7.0393 | 7.4412 | 0.022903 | -0.12957 | 122.8472 | 122.8092 | 123.0287 | 122.7599 | -0.16374 | 122.7835 | 122.9462 | 122.7937 | 43.9135 | -123.3251
2660.2188 | 123.0011 | -122.6669 | 0.13275 | 1.4211e-13 | -0.01256 | -0.013505 | -0.04517 | -0.04107 | -0.011497 | -0.00083919 | -0.014726 | 0.014294 | 0.039409 | 0.014645 | 0.046743 | 0.010204 | 0.0243 | 0.009904 | 0.11165 | 0.078201 | 0.28848 | 0.019363 | -113.0336 | -78.9183 | -115.5635 | 0.04788 | 0.21516 | 0.07643 | -123.1466 | 122.6863 | -0.021104 | 122.6771 | 122.6768 | -0.009459 | -0.05455 | 0.15573 | -0.47967 | -0.084871 | 9.6334 | 7.1035 | 7.5831 | 0.082414 | -0.056321 | 122.7786 | 122.7451 | 122.9554 | 122.6912 | -0.11339 | 122.7148 | 122.8821 | 122.7434 | 43.7486 | -123.2794
2662.0156 | 123.0331 | -122.6852 | 0.13733 | 1.4211e-13 | -0.012773 | -0.013291 | -0.04517 | -0.041284 | -0.011924 | 0.0067908 | -0.01494 | 0.013866 | 0.04005 | 0.014645 | 0.04717 | 0.014783 | 0.0243 | 0.009904 | 0.11165 | 0.08278 | 0.28848 | 0.023942 | -112.9145 | -78.9366 | -115.4398 | 0.04788 | 0.20601 | 0.026065 | -123.142 | 122.7092 | -0.025682 | 122.7 | 122.6951 | -0.014038 | -0.054549 | 0.15115 | -0.45678 | -0.089449 | 9.7707 | 7.2454 | 7.7022 | 0.068679 | -0.11126 | 122.7969 | 122.768 | 122.9737 | 122.7095 | -0.11339 | 122.7331 | 122.8912 | 122.7113 | 43.7486 | -123.2793
2663.75 | 123.0011 | -122.6669 | 0.13275 | 1.4211e-13 | -0.01256 | -0.013505 | -0.04517 | -0.04107 | -0.011711 | -0.0084697 | -0.014085 | 0.014294 | 0.04005 | 0.014431 | 0.047598 | 0.010204 | 0.0243 | 0.005325 | 0.11622 | 0.073622 | 0.2839 | 0.023942 | -112.8 | -78.9961 | -115.3299 | 0.038723 | 0.20601 | 0.035222 | -123.1558 | 122.6909 | -0.016526 | 122.6771 | 122.6723 | -0.018617 | -0.059129 | 0.15115 | -0.48883 | -0.094028 | 9.8669 | 7.337 | 7.8258 | 0.073257 | -0.097529 | 122.7832 | 122.7406 | 122.9508 | 122.6912 | -0.10881 | 122.7057 | 122.8729 | 122.7022 | 43.6708 | -123.2885
2665.5469 | 122.9233 | -122.6898 | 0.16479 | 1.4211e-13 | -0.012773 | -0.013505 | -0.045384 | -0.041284 | -0.011924 | 0.0067908 | -0.014299 | 0.014294 | 0.040264 | 0.014645 | 0.047811 | 0.010204 | 0.019721 | 0.005325 | 0.11622 | 0.08278 | 0.28848 | 0.014784 | -112.6581 | -78.9229 | -115.2063 | 0.043302 | 0.20601 | 0.003172 | -123.1512 | 122.7046 | -0.04857 | 122.7 | 122.6951 | -0.009459 | -0.082015 | 0.12369 | -0.46136 | -0.12149 | 10.0317 | 7.4835 | 7.9449 | 0.041213 | -0.16162 | 122.806 | 122.7726 | 122.9783 | 122.7095 | -0.15001 | 122.7331 | 122.8958 | 122.693 | 43.767 | -123.316
2667.3281 | 122.9095 | -122.6852 | 0.17395 | 1.4211e-13 | -0.012773 | -0.013505 | -0.045384 | -0.041498 | -0.011924 | -0.0161 | -0.014513 | 0.014507 | 0.04005 | 0.015072 | 0.047598 | 0.005626 | 0.019721 | 0.000747 | 0.10707 | 0.08278 | 0.29306 | 0.014784 | -112.5162 | -78.9137 | -115.0919 | 0.043302 | 0.20601 | 0.067272 | -123.1512 | 122.7 | -0.066882 | 122.6909 | 122.686 | -0.014037 | -0.09117 | 0.11911 | -0.46594 | -0.13065 | 10.1691 | 7.5934 | 8.0593 | 0.032058 | -0.10668 | 122.7923 | 122.768 | 122.9783 | 122.705 | -0.15917 | 122.7285 | 122.8912 | 122.7525 | 43.7715 | -123.3251
2669.0938 | 122.8729 | -122.731 | 0.16937 | 1.4211e-13 | -0.012773 | -0.013505 | -0.044957 | -0.04107 | -0.011711 | 0.0067908 | -0.014299 | 0.014294 | 0.040264 | 0.014859 | 0.048025 | 0.005626 | 0.019721 | 0.005325 | 0.10707 | 0.078201 | 0.2839 | 0.019363 | -112.388 | -78.8496 | -114.9957 | 0.038723 | 0.20143 | 0.071851 | -123.1512 | 122.7504 | -0.062305 | 122.7366 | 122.7363 | -0.014038 | -0.091172 | 0.11453 | -0.42016 | -0.13065 | 10.3431 | 7.7353 | 8.1555 | 0.032056 | -0.097522 | 122.8381 | 122.8092 | 123.0149 | 122.7507 | -0.15001 | 122.7697 | 122.9324 | 122.8029 | 43.8814 | -123.3206
2670.9219 | 122.9233 | -122.6898 | 0.16022 | 1.4211e-13 | -0.012987 | -0.013505 | -0.045384 | -0.041284 | -0.011924 | -0.00083919 | -0.014726 | 0.014294 | 0.04005 | 0.014859 | 0.048025 | 0.010204 | 0.019721 | 0.009904 | 0.11165 | 0.08278 | 0.28848 | 0.019363 | -112.2506 | -78.8633 | -114.8767 | 0.04788 | 0.20601 | 0.062694 | -123.1558 | 122.7092 | -0.04857 | 122.7 | 122.6997 | -0.009459 | -0.077437 | 0.12826 | -0.46594 | -0.11234 | 10.4392 | 7.8132 | 8.2791 | 0.045791 | -0.097523 | 122.8015 | 122.7726 | 122.9783 | 122.7095 | -0.14085 | 122.7377 | 122.8958 | 122.7525 | 43.8265 | -123.316
2672.7188 | 123.0148 | -122.644 | 0.1236 | 1.4211e-13 | -0.01256 | -0.013505 | -0.045384 | -0.041498 | -0.011711 | -0.0161 | -0.014726 | 0.014507 | 0.040691 | 0.014645 | 0.048452 | 0.005626 | 0.019721 | 0.009904 | 0.11165 | 0.078201 | 0.28848 | 0.014784 | -112.0949 | -78.8221 | -114.7942 | 0.038723 | 0.20601 | 0.030644 | -123.1466 | 122.6588 | -0.011949 | 122.6497 | 122.6539 | -0.00488 | -0.045395 | 0.16489 | -0.50256 | -0.084873 | 10.5491 | 7.8498 | 8.3524 | 0.082412 | -0.092952 | 122.7557 | 122.7222 | 122.9325 | 122.6638 | -0.10881 | 122.6828 | 122.8501 | 122.6747 | 43.8219 | -123.2702
2674.5 | 122.9187 | -122.7173 | 0.16022 | 1.4211e-13 | -0.012773 | -0.013505 | -0.045384 | -0.04107 | -0.011711 | -0.0084697 | -0.014726 | 0.014721 | 0.040691 | 0.014859 | 0.048666 | 0.001048 | 0.019721 | 0.000747 | 0.11165 | 0.08278 | 0.29306 | 0.014784 | -111.9805 | -78.5749 | -114.6844 | 0.043302 | 0.20143 | 0.039801 | -123.1466 | 122.7321 | -0.04857 | 122.7183 | 122.718 | -0.014037 | -0.077437 | 0.13284 | -0.42932 | -0.11691 | 10.7368 | 8.0329 | 8.4622 | 0.041212 | -0.12042 | 122.8289 | 122.8001 | 123.0103 | 122.737 | -0.14543 | 122.7606 | 122.9187 | 122.7571 | 44.1424 | -123.3068
2676.2188 | 123.0011 | -122.6715 | 0.12817 | 1.4211e-13 | -0.013414 | -0.013505 | -0.045384 | -0.041284 | -0.011711 | 0.0067908 | -0.014513 | 0.014935 | 0.040478 | 0.015286 | 0.04888 | 0.014783 | 0.028878 | 0.005325 | 0.10707 | 0.08278 | 0.2839 | 0.014784 | -111.8065 | -78.4604 | -114.5699 | 0.038723 | 0.20601 | 0.048958 | -123.1466 | 122.6863 | -0.021106 | 122.6863 | 122.6768 | -0.009459 | -0.045394 | 0.15573 | -0.47509 | -0.089451 | 10.865 | 8.1016 | 8.5767 | 0.077834 | -0.079216 | 122.7786 | 122.7543 | 122.9554 | 122.7004 | -0.11339 | 122.7102 | 122.8775 | 122.7205 | 44.2111 | -123.2748
2678 | 122.9965 | -122.6761 | 0.13275 | 1.4211e-13 | -0.012773 | -0.013718 | -0.045384 | -0.041284 | -0.012138 | -0.0084697 | -0.014085 | 0.014935 | 0.040691 | 0.015072 | 0.04888 | 0.014783 | 0.019721 | 0.005325 | 0.11165 | 0.078201 | 0.2839 | 0.014784 | -111.5958 | -78.2361 | -114.4783 | 0.04788 | 0.20143 | 0.026065 | -123.1512 | 122.6909 | -0.021104 | 122.6909 | 122.6814 | -0.009459 | -0.05455 | 0.15115 | -0.47509 | -0.084871 | 11.0802 | 8.1978 | 8.6729 | 0.068678 | -0.10669 | 122.7877 | 122.7543 | 122.96 | 122.6958 | -0.11797 | 122.724 | 122.8775 | 122.7022 | 44.44 | -123.2839
2679.7812 | 122.9645 | -122.6898 | 0.14191 | 1.4211e-13 | -0.01256 | -0.013505 | -0.045598 | -0.041498 | -0.011711 | -0.0084697 | -0.014085 | 0.015148 | 0.041119 | 0.015286 | 0.049521 | 0.014783 | 0.019721 | 0.000747 | 0.11622 | 0.069043 | 0.28848 | 0.019363 | -111.4035 | -77.9568 | -114.3455 | 0.038723 | 0.21059 | 0.062694 | -123.142 | 122.7092 | -0.025682 | 122.7046 | 122.6906 | -0.018616 | -0.072864 | 0.14657 | -0.4522 | -0.10318 | 11.2863 | 8.3443 | 8.7965 | 0.068679 | -0.079213 | 122.806 | 122.7589 | 122.9783 | 122.7095 | -0.12254 | 122.7285 | 122.9004 | 122.7525 | 44.7331 | -123.2839
2681.5781 | 122.8912 | -122.699 | 0.17853 | 1.4211e-13 | -0.012987 | -0.013505 | -0.045384 | -0.041498 | -0.011711 | -0.00083919 | -0.013872 | 0.015148 | 0.040478 | 0.015713 | 0.049307 | 0.014783 | 0.0243 | 0.009904 | 0.11622 | 0.078201 | 0.28848 | 0.019363 | -111.2524 | -77.8927 | -114.199 | 0.043302 | 0.21059 | 0.067272 | -123.1466 | 122.7183 | -0.062303 | 122.7138 | 122.7089 | -0.009459 | -0.10033 | 0.10995 | -0.44763 | -0.13523 | 11.4465 | 8.5 | 8.9476 | 0.032058 | -0.11126 | 122.8152 | 122.7772 | 122.9875 | 122.7233 | -0.15917 | 122.7423 | 122.9096 | 122.7662 | 44.8063 | -123.3251
2683.2969 | 122.9416 | -122.6944 | 0.15106 | 1.4211e-13 | -0.012773 | -0.013291 | -0.04517 | -0.041498 | -0.011497 | -0.0084697 | -0.014299 | 0.014935 | 0.040905 | 0.015927 | 0.049093 | 0.005626 | 0.0243 | 0.005325 | 0.10707 | 0.078201 | 0.28848 | 0.019363 | -111.0739 | -77.7232 | -114.112 | 0.038723 | 0.20143 | 0.071851 | -123.1466 | 122.7138 | -0.043994 | 122.7 | 122.6997 | -0.014038 | -0.072861 | 0.13742 | -0.4522 | -0.11234 | 11.6205 | 8.5824 | 9.0346 | 0.050367 | -0.079211 | 122.8015 | 122.7726 | 122.9829 | 122.7187 | -0.1317 | 122.7331 | 122.8958 | 122.7662 | 44.9712 | -123.2977
2685.0625 | 122.8638 | -122.699 | 0.16937 | 1.4211e-13 | -0.013201 | -0.013505 | -0.045384 | -0.041498 | -0.011924 | -0.0084697 | -0.014085 | 0.015148 | 0.041332 | 0.015713 | 0.049734 | 0.005626 | 0.019721 | 0.014482 | 0.10707 | 0.078201 | 0.27932 | 0.019363 | -110.8678 | -77.5538 | -113.9884 | 0.034145 | 0.20601 | 0.062694 | -123.1512 | 122.7183 | -0.062305 | 122.7046 | 122.7135 | -0.004881 | -0.091172 | 0.10995 | -0.4522 | -0.13523 | 11.8311 | 8.7106 | 9.1628 | 0.036635 | -0.10668 | 122.806 | 122.7772 | 122.9783 | 122.7187 | -0.15001 | 122.7331 | 122.905 | 122.7617 | 45.1451 | -123.3206
2686.8594 | 123.0057 | -122.644 | 0.13275 | 1.4211e-13 | -0.01256 | -0.013505 | -0.045384 | -0.041498 | -0.011924 | -0.0084697 | -0.014085 | 0.015789 | 0.041119 | 0.015713 | 0.049948 | 0.005626 | 0.019721 | 0.005325 | 0.11622 | 0.08278 | 0.28848 | 0.023942 | -110.6709 | -77.3661 | -113.9106 | 0.04788 | 0.20143 | 0.071851 | -123.1466 | 122.668 | -0.016526 | 122.6497 | 122.6494 | -0.018617 | -0.049971 | 0.15573 | -0.50256 | -0.084871 | 11.9731 | 8.7335 | 9.2361 | 0.068678 | -0.0609 | 122.7603 | 122.7268 | 122.9325 | 122.6638 | -0.10881 | 122.6919 | 122.8455 | 122.7159 | 45.2779 | -123.2794
2688.5938 | 122.8867 | -122.7219 | 0.18768 | 1.4211e-13 | -0.012773 | -0.013291 | -0.044957 | -0.041284 | -0.012138 | -0.0084697 | -0.013872 | 0.015576 | 0.041332 | 0.015927 | 0.050162 | 0.005626 | 0.019721 | 0.005325 | 0.11165 | 0.087359 | 0.29306 | 0.019363 | -110.4832 | -77.1967 | -113.8052 | 0.038723 | 0.21059 | 0.053537 | -123.1558 | 122.7412 | -0.076036 | 122.7275 | 122.7272 | -0.014038 | -0.10032 | 0.10538 | -0.43389 | -0.14896 | 12.2386 | 8.9166 | 9.3505 | 0.022903 | -0.13415 | 122.8335 | 122.8092 | 123.0149 | 122.7416 | -0.16832 | 122.7606 | 122.9324 | 122.7754 | 45.5252 | -123.3434
2690.375 | 122.9919 | -122.6715 | 0.13733 | 1.4211e-13 | -0.012987 | -0.013505 | -0.04517 | -0.041284 | -0.012138 | -0.00083919 | -0.013444 | 0.015576 | 0.041119 | 0.015927 | 0.050589 | 0.010204 | 0.0243 | 0.014482 | 0.11165 | 0.08278 | 0.28848 | 0.037679 | -110.2772 | -77.1097 | -113.6633 | 0.043302 | 0.20601 | 0.071851 | -123.1512 | 122.7092 | -0.025682 | 122.6817 | 122.686 | -0.023197 | -0.054549 | 0.15115 | -0.47967 | -0.094027 | 12.3943 | 9.0082 | 9.4879 | 0.068679 | -0.065478 | 122.7832 | 122.7543 | 122.96 | 122.6958 | -0.09965 | 122.7148 | 122.8775 | 122.7434 | 45.5618 | -123.2885
2692.1562 | 122.8867 | -122.7081 | 0.16479 | 1.4211e-13 | -0.012987 | -0.013505 | -0.045384 | -0.041284 | -0.011924 | -0.00083919 | -0.014085 | 0.015576 | 0.041119 | 0.015927 | 0.050375 | 0.005626 | 0.0243 | 0.005325 | 0.10707 | 0.08278 | 0.2839 | 0.014784 | -110.0757 | -76.9723 | -113.5946 | 0.043302 | 0.20143 | 0.039801 | -123.1466 | 122.7229 | -0.057727 | 122.7138 | 122.7135 | -0.009459 | -0.082015 | 0.11911 | -0.43847 | -0.12149 | 12.6324 | 9.1135 | 9.552 | 0.036634 | -0.12499 | 122.8152 | 122.7909 | 122.992 | 122.7324 | -0.15001 | 122.7514 | 122.9096 | 122.7479 | 45.7358 | -123.3114
2693.9531 | 122.8775 | -122.7081 | 0.16937 | 1.4211e-13 | -0.012987 | -0.013505 | -0.045384 | -0.040857 | -0.011924 | -0.0084697 | -0.013231 | 0.015362 | 0.041546 | 0.015927 | 0.050803 | 0.014783 | 0.019721 | 0.009904 | 0.11165 | 0.078201 | 0.28848 | 0.023942 | -109.8468 | -76.8579 | -113.503 | 0.043302 | 0.21059 | 0.071851 | -123.1512 | 122.7321 | -0.057726 | 122.7229 | 122.718 | -0.014038 | -0.091172 | 0.11911 | -0.44305 | -0.12607 | 12.8614 | 9.2051 | 9.6481 | 0.041213 | -0.097522 | 122.8198 | 122.7863 | 122.9966 | 122.7279 | -0.14543 | 122.7514 | 122.9187 | 122.78 | 45.8503 | -123.3206
2695.75 | 122.9279 | -122.699 | 0.17395 | 1.4211e-13 | -0.012987 | -0.013291 | -0.04517 | -0.04107 | -0.011711 | -0.0084697 | -0.013658 | 0.016003 | 0.04176 | 0.016354 | 0.050803 | 0.005626 | 0.015142 | 0.009904 | 0.10249 | 0.08278 | 0.2839 | 0.0331 | -109.5766 | -76.6518 | -113.4023 | 0.057037 | 0.21059 | 0.067272 | -123.142 | 122.7321 | -0.07146 | 122.7046 | 122.7089 | -0.023196 | -0.09117 | 0.10995 | -0.44305 | -0.11691 | 13.1223 | 9.2967 | 9.7397 | 0.036636 | -0.10668 | 122.8015 | 122.7818 | 122.9829 | 122.7141 | -0.14085 | 122.756 | 122.9096 | 122.7662 | 46.0472 | -123.316
2697.4844 | 122.9965 | -122.6578 | 0.11902 | 1.4211e-13 | -0.012987 | -0.013505 | -0.04517 | -0.04107 | -0.012138 | -0.0084697 | -0.013444 | 0.015789 | 0.041546 | 0.016354 | 0.051016 | 0.005626 | 0.015142 | 0.009904 | 0.11622 | 0.078201 | 0.2839 | 0.019363 | -109.334 | -76.519 | -113.297 | 0.04788 | 0.21059 | 0.062694 | -123.1466 | 122.6771 | -0.002794 | 122.6634 | 122.6677 | -0.009459 | -0.040818 | 0.16488 | -0.48882 | -0.071139 | 13.3238 | 9.3608 | 9.8496 | 0.091567 | -0.056325 | 122.774 | 122.736 | 122.9417 | 122.6729 | -0.099656 | 122.7057 | 122.8684 | 122.7205 | 46.1387 | -123.2656
2699.25 | 123.0194 | -122.6715 | 0.12817 | 1.4211e-13 | -0.012987 | -0.013077 | -0.04517 | -0.041284 | -0.011924 | -0.0084697 | -0.013231 | 0.015576 | 0.041973 | 0.016141 | 0.051443 | 0.005626 | 0.019721 | 0.005325 | 0.11165 | 0.08278 | 0.28848 | 0.019363 | -109.1462 | -76.3405 | -113.1825 | 0.04788 | 0.21516 | 0.071851 | -123.1466 | 122.6909 | -0.016527 | 122.6771 | 122.6768 | -0.014038 | -0.045394 | 0.16031 | -0.47509 | -0.080294 | 13.5253 | 9.489 | 9.9641 | 0.086991 | -0.056323 | 122.7832 | 122.7543 | 122.96 | 122.6912 | -0.10881 | 122.7194 | 122.8867 | 122.7434 | 46.331 | -123.2748
2701.0469 | 122.9782 | -122.6486 | 0.14191 | 1.4211e-13 | -0.013201 | -0.013718 | -0.045384 | -0.041284 | -0.011497 | -0.00083919 | -0.013017 | 0.016003 | 0.04176 | 0.016354 | 0.051657 | 0.005626 | 0.0243 | 0.005325 | 0.11622 | 0.08278 | 0.28848 | 0.019363 | -108.931 | -76.3405 | -113.0772 | 0.052459 | 0.21059 | 0.07643 | -123.1512 | 122.668 | -0.025682 | 122.6542 | 122.6539 | -0.014038 | -0.059127 | 0.14657 | -0.50256 | -0.089448 | 13.7176 | 9.5714 | 10.074 | 0.068679 | -0.065477 | 122.7648 | 122.7314 | 122.9371 | 122.6729 | -0.12254 | 122.7011 | 122.8592 | 122.7251 | 46.3082 | -123.2931
2702.7812 | 122.8867 | -122.6578 | 0.16022 | 1.4211e-13 | -0.012987 | -0.013077 | -0.04517 | -0.04107 | -0.012138 | -0.0084697 | -0.012803 | 0.01643 | 0.041973 | 0.016354 | 0.051871 | 0.001048 | 0.019721 | 0.005325 | 0.11165 | 0.08278 | 0.28848 | 0.019363 | -108.6517 | -76.2901 | -113.0177 | 0.052459 | 0.21059 | 0.071851 | -123.142 | 122.6771 | -0.04857 | 122.6588 | 122.6631 | -0.014038 | -0.077437 | 0.12826 | -0.48425 | -0.10776 | 14.006 | 9.6401 | 10.1243 | 0.050369 | -0.088366 | 122.7694 | 122.7406 | 122.9463 | 122.6775 | -0.14085 | 122.7102 | 122.8684 | 122.7296 | 46.3677 | -123.3022
2704.5 | 122.8729 | -122.7081 | 0.20142 | 1.4211e-13 | -0.012987 | -0.013505 | -0.045384 | -0.04107 | -0.011924 | -0.0084697 | -0.012803 | 0.015789 | 0.041973 | 0.016782 | 0.051657 | 0.010204 | 0.019721 | -0.003831 | 0.10707 | 0.078201 | 0.28848 | 0.019363 | -108.3862 | -76.2443 | -112.9536 | 0.057037 | 0.21059 | 0.067272 | -123.142 | 122.7275 | -0.094348 | 122.7183 | 122.7043 | -0.023194 | -0.12322 | 0.087065 | -0.43389 | -0.14438 | 14.322 | 9.7545 | 10.1884 | 0.00917 | -0.13414 | 122.8152 | 122.7863 | 122.9966 | 122.7279 | -0.18205 | 122.7652 | 122.9187 | 122.7754 | 46.4638 | -123.3434
2706.2969 | 122.9004 | -122.6944 | 0.19684 | 1.4211e-13 | -0.013201 | -0.013718 | -0.045384 | -0.04107 | -0.011711 | -0.0084697 | -0.013017 | 0.01643 | 0.04176 | 0.016568 | 0.052512 | 0.005626 | 0.019721 | 0.009904 | 0.11165 | 0.078201 | 0.28848 | 0.019363 | -108.1801 | -76.1985 | -112.8162 | 0.052459 | 0.20601 | 0.07643 | -123.1466 | 122.7138 | -0.085191 | 122.7 | 122.7043 | -0.009459 | -0.11864 | 0.091643 | -0.4522 | -0.14438 | 14.5143 | 9.8782 | 10.3304 | 0.00917 | -0.12041 | 122.806 | 122.7726 | 122.9829 | 122.7141 | -0.17748 | 122.7469 | 122.9004 | 122.7708 | 46.4959 | -123.3434
2708.0156 | 122.9736 | -122.6852 | 0.15564 | 1.4211e-13 | -0.013201 | -0.013505 | -0.04517 | -0.041284 | -0.012138 | 0.0067908 | -0.012803 | 0.016644 | 0.04176 | 0.016354 | 0.052298 | 0.010204 | 0.028878 | -0.003831 | 0.11622 | 0.078201 | 0.28848 | 0.019363 | -107.9832 | -76.1848 | -112.775 | 0.052459 | 0.21516 | 0.058115 | -123.142 | 122.7046 | -0.039415 | 122.6954 | 122.6814 | -0.023194 | -0.077439 | 0.13284 | -0.45678 | -0.10318 | 14.702 | 9.9102 | 10.367 | 0.059525 | -0.097525 | 122.8015 | 122.7634 | 122.9737 | 122.7141 | -0.13628 | 122.7377 | 122.9004 | 122.7434 | 46.5004 | -123.2977
2709.7969 | 122.8958 | -122.7081 | 0.19684 | 1.4211e-13 | -0.013201 | -0.013718 | -0.044957 | -0.041498 | -0.012138 | -0.00083919 | -0.01259 | 0.016217 | 0.04176 | 0.016782 | 0.052725 | 0.001048 | 0.010564 | 0.009904 | 0.10707 | 0.08278 | 0.28848 | 0.019363 | -107.7131 | -76.2214 | -112.6743 | 0.052459 | 0.21974 | 0.071851 | -123.1329 | 122.7275 | -0.08977 | 122.7092 | 122.718 | -0.009459 | -0.11406 | 0.091643 | -0.42473 | -0.14438 | 14.995 | 10.0338 | 10.4586 | 0.022906 | -0.12499 | 122.8152 | 122.7909 | 122.9966 | 122.7187 | -0.17748 | 122.7606 | 122.9279 | 122.78 | 46.4867 | -123.3297
2711.5781 | 122.8821 | -122.6898 | 0.18768 | 1.4211e-13 | -0.013201 | -0.013505 | -0.045598 | -0.041498 | -0.011924 | -0.00083919 | -0.012162 | 0.016003 | 0.04176 | 0.016996 | 0.052939 | 0.014783 | 0.019721 | 0.009904 | 0.11165 | 0.078201 | 0.2839 | 0.019363 | -107.4842 | -76.2397 | -112.5553 | 0.061616 | 0.22432 | 0.07643 | -123.1329 | 122.7092 | -0.076036 | 122.7046 | 122.6997 | -0.009459 | -0.10948 | 0.09622 | -0.44304 | -0.12607 | 15.2057 | 10.1346 | 10.5776 | 0.036639 | -0.11125 | 122.8015 | 122.768 | 122.9737 | 122.7095 | -0.16832 | 122.7514 | 122.9141 | 122.7662 | 46.4501 | -123.3205
2713.3594 | 122.8821 | -122.699 | 0.17395 | 1.4211e-13 | -0.013201 | -0.013291 | -0.04517 | -0.041284 | -0.012138 | -0.00083919 | -0.012803 | 0.01643 | 0.041973 | 0.016996 | 0.053366 | 0.010204 | 0.015142 | 0.000747 | 0.11622 | 0.087359 | 0.28848 | 0.019363 | -107.2735 | -76.2306 | -112.4591 | 0.066194 | 0.21974 | 0.081008 | -123.1283 | 122.7183 | -0.057725 | 122.7092 | 122.6997 | -0.018616 | -0.086591 | 0.11453 | -0.42931 | -0.10776 | 15.4254 | 10.2399 | 10.6692 | 0.045794 | -0.092942 | 122.8152 | 122.7863 | 122.9875 | 122.7141 | -0.15459 | 122.7652 | 122.9187 | 122.78 | 46.4684 | -123.3022
2715.125 | 123.0286 | -122.6349 | 0.16937 | 1.4211e-13 | -0.012987 | -0.013718 | -0.04517 | -0.041284 | -0.012138 | -0.0161 | -0.012162 | 0.016858 | 0.04176 | 0.016996 | 0.052939 | 0.010204 | 0.019721 | 0.005325 | 0.11622 | 0.073622 | 0.2839 | 0.014784 | -107.0767 | -76.2901 | -112.3584 | 0.057037 | 0.21974 | 0.067272 | -123.1329 | 122.6497 | -0.053148 | 122.6451 | 122.6402 | -0.009459 | -0.095751 | 0.11453 | -0.49797 | -0.11234 | 15.5582 | 10.2765 | 10.7745 | 0.050371 | -0.1021 | 122.7511 | 122.7085 | 122.9188 | 122.6546 | -0.15459 | 122.6919 | 122.8546 | 122.7022 | 46.3448 | -123.3022
2716.8594 | 123.0103 | -122.6212 | 0.13733 | 1.4211e-13 | -0.013201 | -0.013505 | -0.04517 | -0.04107 | -0.012138 | -0.0084697 | -0.01259 | 0.016858 | 0.042187 | 0.016782 | 0.05358 | 0.010204 | 0.0243 | 0.005325 | 0.10707 | 0.087359 | 0.2839 | 0.014784 | -106.9118 | -76.4 | -112.3217 | 0.057037 | 0.21974 | 0.085587 | -123.1329 | 122.6359 | -0.030261 | 122.6314 | 122.6265 | -0.009459 | -0.04997 | 0.14657 | -0.51171 | -0.080292 | 15.7093 | 10.2994 | 10.8111 | 0.082415 | -0.051742 | 122.7282 | 122.7085 | 122.9051 | 122.6455 | -0.12255 | 122.6782 | 122.8409 | 122.7067 | 46.2212 | -123.2702
2718.6406 | 123.0011 | -122.6486 | 0.16479 | 1.4211e-13 | -0.013201 | -0.013291 | -0.045384 | -0.04107 | -0.012138 | -0.00083919 | -0.012376 | 0.016858 | 0.041973 | 0.016996 | 0.053366 | 0.005626 | 0.019721 | 0.000747 | 0.11165 | 0.08278 | 0.29306 | 0.014784 | -106.7607 | -76.4961 | -112.2118 | 0.057037 | 0.21974 | 0.090166 | -123.1283 | 122.6634 | -0.053148 | 122.6542 | 122.6494 | -0.014037 | -0.082015 | 0.12826 | -0.47966 | -0.10776 | 15.8879 | 10.4368 | 10.9164 | 0.054949 | -0.074629 | 122.7603 | 122.7314 | 122.9417 | 122.6683 | -0.15001 | 122.7057 | 122.8684 | 122.7388 | 46.1525 | -123.2931
2720.3594 | 122.8775 | -122.7081 | 0.17853 | 1.4211e-13 | -0.012987 | -0.013291 | -0.04517 | -0.041284 | -0.011924 | -0.00083919 | -0.012162 | 0.016644 | 0.041973 | 0.017423 | 0.053794 | 0.010204 | 0.015142 | 0.005325 | 0.11165 | 0.073622 | 0.28848 | 0.019363 | -106.6188 | -76.5557 | -112.1569 | 0.061616 | 0.22432 | 0.07643 | -123.1283 | 122.7275 | -0.066881 | 122.7183 | 122.7135 | -0.014038 | -0.10491 | 0.10995 | -0.42016 | -0.11691 | 16.0893 | 10.5512 | 10.9714 | 0.045794 | -0.1021 | 122.8198 | 122.7818 | 122.9966 | 122.7233 | -0.15917 | 122.7697 | 122.9325 | 122.7846 | 46.1525 | -123.3068
2722.1562 | 122.9965 | -122.6395 | 0.16479 | 1.4211e-13 | -0.012987 | -0.013718 | -0.04517 | -0.041498 | -0.011711 | -0.00083919 | -0.012376 | 0.016858 | 0.041973 | 0.017637 | 0.05358 | 0.005626 | 0.019721 | 0.009904 | 0.11165 | 0.078201 | 0.28848 | 0.014784 | -106.4631 | -76.6701 | -112.0836 | 0.066194 | 0.22432 | 0.081008 | -123.1283 | 122.6542 | -0.053148 | 122.6451 | 122.6494 | -0.00488 | -0.086594 | 0.12369 | -0.48882 | -0.098601 | 16.1764 | 10.5558 | 11.0446 | 0.059527 | -0.083787 | 122.7511 | 122.7177 | 122.9279 | 122.6592 | -0.15001 | 122.7057 | 122.8638 | 122.7205 | 45.9693 | -123.2931
2723.8906 | 122.9141 | -122.6944 | 0.16479 | 1.4211e-13 | -0.013201 | -0.013718 | -0.045384 | -0.041284 | -0.012352 | -0.0084697 | -0.012376 | 0.017071 | 0.041973 | 0.017423 | 0.053794 | 0.005626 | 0.015142 | 0.014482 | 0.11622 | 0.087359 | 0.28848 | 0.014784 | -106.3441 | -76.8533 | -112.0012 | 0.057037 | 0.22432 | 0.090166 | -123.1237 | 122.7092 | -0.04857 | 122.7 | 122.7089 | -0.000302 | -0.077436 | 0.12369 | -0.42931 | -0.10776 | 16.3503 | 10.6932 | 11.1225 | 0.059527 | -0.074629 | 122.8106 | 122.7818 | 122.9829 | 122.7095 | -0.15001 | 122.7514 | 122.9187 | 122.7846 | 45.8411 | -123.2885
2725.6719 | 123.0011 | -122.6486 | 0.14191 | 1.4211e-13 | -0.013201 | -0.013291 | -0.045598 | -0.041284 | -0.011924 | -0.00083919 | -0.012162 | 0.017285 | 0.041973 | 0.017423 | 0.05358 | 0.010204 | 0.019721 | 0.009904 | 0.11165 | 0.08278 | 0.29306 | 0.014784 | -106.2296 | -76.9586 | -111.9234 | 0.057037 | 0.21974 | 0.090166 | -123.1283 | 122.6634 | -0.03026 | 122.6588 | 122.6585 | -0.00488 | -0.059127 | 0.15115 | -0.47966 | -0.08487 | 16.419 | 10.7252 | 11.2049 | 0.077837 | -0.051741 | 122.7603 | 122.7314 | 122.9417 | 122.6683 | -0.12712 | 122.7057 | 122.8684 | 122.7388 | 45.69 | -123.2702
2727.4688 | 122.9507 | -122.6486 | 0.16479 | 1.4211e-13 | -0.013201 | -0.013505 | -0.045384 | -0.040857 | -0.011711 | -0.0161 | -0.012376 | 0.017071 | 0.042187 | 0.017423 | 0.054007 | 0.001048 | 0.019721 | 0.009904 | 0.11165 | 0.087359 | 0.29306 | 0.014784 | -106.1334 | -77.1509 | -111.8776 | 0.052459 | 0.21516 | 0.090166 | -123.1283 | 122.6634 | -0.053148 | 122.6497 | 122.6585 | -0.00488 | -0.077436 | 0.12826 | -0.47966 | -0.11234 | 16.5152 | 10.771 | 11.2507 | 0.05037 | -0.074629 | 122.7603 | 122.736 | 122.9417 | 122.6683 | -0.15001 | 122.7011 | 122.8638 | 122.7388 | 45.4977 | -123.2931
2729.25 | 122.905 | -122.6715 | 0.1831 | 1.4211e-13 | -0.013414 | -0.013505 | -0.045384 | -0.041498 | -0.012138 | 0.0067908 | -0.012162 | 0.017071 | 0.042401 | 0.017637 | 0.054007 | 0.001048 | 0.0243 | 0.005325 | 0.11622 | 0.078201 | 0.28848 | 0.019363 | -106.0739 | -77.2791 | -111.8364 | 0.061616 | 0.21974 | 0.085587 | -123.1374 | 122.6909 | -0.06688 | 122.6726 | 122.6768 | -0.014038 | -0.1049 | 0.10538 | -0.46593 | -0.12149 | 16.5976 | 10.8351 | 11.301 | 0.036639 | -0.097518 | 122.7877 | 122.7497 | 122.96 | 122.6958 | -0.16374 | 122.7331 | 122.8913 | 122.7571 | 45.3924 | -123.3205
2730.9688 | 123.0057 | -122.6257 | 0.15106 | 1.4211e-13 | -0.012987 | -0.013718 | -0.04517 | -0.041284 | -0.011924 | -0.0161 | -0.012162 | 0.016644 | 0.041546 | 0.017423 | 0.054007 | 0.001048 | 0.015142 | 0.014482 | 0.10707 | 0.078201 | 0.28848 | 0.028521 | -105.9961 | -77.3661 | -111.7677 | 0.057037 | 0.21516 | 0.085587 | -123.1329 | 122.6543 | -0.043994 | 122.6268 | 122.6402 | -0.014039 | -0.072861 | 0.13742 | -0.50713 | -0.094025 | 16.6296 | 10.858 | 11.3651 | 0.064103 | -0.065475 | 122.7328 | 122.7039 | 122.9142 | 122.6409 | -0.12254 | 122.6828 | 122.8409 | 122.7113 | 45.2596 | -123.2839
2732.7656 | 122.9004 | -122.6807 | 0.16479 | 1.4211e-13 | -0.013628 | -0.013077 | -0.045598 | -0.040857 | -0.011711 | -0.00083919 | -0.012162 | 0.016644 | 0.041973 | 0.017423 | 0.053794 | 0.010204 | 0.019721 | 0.005325 | 0.1208 | 0.08278 | 0.2839 | 0.019363 | -105.932 | -77.5676 | -111.7173 | 0.061616 | 0.21516 | 0.071851 | -123.1329 | 122.7 | -0.043991 | 122.6909 | 122.686 | -0.014038 | -0.082015 | 0.11911 | -0.4522 | -0.10318 | 16.7487 | 10.9633 | 11.4155 | 0.05037 | -0.092944 | 122.8015 | 122.7634 | 122.9646 | 122.7004 | -0.14543 | 122.7423 | 122.8958 | 122.7525 | 45.1131 | -123.2977
2734.5469 | 122.9691 | -122.6532 | 0.17395 | 1.4211e-13 | -0.013201 | -0.013718 | -0.045384 | -0.04107 | -0.012138 | -0.0084697 | -0.012376 | 0.016858 | 0.041973 | 0.017423 | 0.054435 | 0.010204 | 0.019721 | 0.000747 | 0.11165 | 0.091937 | 0.2839 | 0.023942 | -105.8587 | -77.6546 | -111.6761 | 0.066194 | 0.21974 | 0.07643 | -123.1237 | 122.6771 | -0.062303 | 122.6634 | 122.6539 | -0.023195 | -0.082013 | 0.10995 | -0.47051 | -0.10776 | 16.7945 | 10.9771 | 11.4476 | 0.045794 | -0.09752 | 122.7648 | 122.7451 | 122.9371 | 122.6729 | -0.15001 | 122.7194 | 122.8729 | 122.7296 | 44.9986 | -123.2977
2736.2656 | 123.0057 | -122.6349 | 0.13733 | 1.4211e-13 | -0.013201 | -0.013505 | -0.045598 | -0.041498 | -0.011924 | -0.0161 | -0.011735 | 0.016858 | 0.042187 | 0.017423 | 0.054007 | 0.010204 | 0.015142 | 0.005325 | 0.10707 | 0.078201 | 0.29306 | 0.019363 | -105.8358 | -77.8514 | -111.5937 | 0.057037 | 0.21974 | 0.081008 | -123.1374 | 122.6543 | -0.030261 | 122.6451 | 122.6402 | -0.014038 | -0.059128 | 0.15573 | -0.50255 | -0.080292 | 16.7991 | 11.0412 | 11.5437 | 0.082415 | -0.056321 | 122.742 | 122.7131 | 122.9279 | 122.65 | -0.11797 | 122.6919 | 122.8546 | 122.7159 | 44.7834 | -123.2748
2738.0625 | 122.9416 | -122.6532 | 0.17853 | 1.4211e-13 | -0.013628 | -0.013291 | -0.04517 | -0.041284 | -0.011924 | -0.0161 | -0.011949 | 0.017071 | 0.042187 | 0.01785 | 0.054221 | 0.005626 | 0.019721 | 0.005325 | 0.11622 | 0.078201 | 0.2839 | 0.014784 | -105.7763 | -78.0025 | -111.5891 | 0.066194 | 0.21974 | 0.081008 | -123.1237 | 122.668 | -0.062303 | 122.6588 | 122.6585 | -0.009459 | -0.10033 | 0.10538 | -0.47051 | -0.11233 | 16.8769 | 11.0641 | 11.5346 | 0.041216 | -0.09752 | 122.7694 | 122.7314 | 122.9371 | 122.6729 | -0.16374 | 122.7194 | 122.8729 | 122.7342 | 44.6507 | -123.3022
2739.8438 | 122.8867 | -122.6944 | 0.19226 | 1.4211e-13 | -0.013628 | -0.013505 | -0.045384 | -0.04107 | -0.011924 | -0.0161 | -0.012162 | 0.016858 | 0.041973 | 0.017423 | 0.054221 | 0.014783 | 0.0243 | 0.009904 | 0.11165 | 0.08278 | 0.30222 | 0.019363 | -105.7076 | -78.0987 | -111.5296 | 0.066194 | 0.22432 | 0.085587 | -123.1191 | 122.7138 | -0.080614 | 122.7092 | 122.7043 | -0.009459 | -0.10948 | 0.10996 | -0.42473 | -0.12607 | 16.9868 | 11.1648 | 11.5895 | 0.032061 | -0.10667 | 122.806 | 122.7772 | 122.9966 | 122.7187 | -0.1729 | 122.7606 | 122.9187 | 122.78 | 44.5957 | -123.3114
2741.5781 | 122.8683 | -122.6898 | 0.1831 | 1.4211e-13 | -0.013201 | -0.013505 | -0.045384 | -0.041284 | -0.012138 | -0.00083919 | -0.012376 | 0.016644 | 0.04176 | 0.017637 | 0.054435 | 0.005626 | 0.019721 | 0.005325 | 0.11622 | 0.091937 | 0.29764 | 0.0331 | -105.6802 | -78.2544 | -111.4747 | 0.066194 | 0.23348 | 0.081008 | -123.1191 | 122.7229 | -0.06688 | 122.6954 | 122.6951 | -0.027775 | -0.091168 | 0.11453 | -0.42931 | -0.11691 | 17.0097 | 11.2151 | 11.6445 | 0.050374 | -0.1021 | 122.806 | 122.7818 | 122.9875 | 122.7095 | -0.15 | 122.756 | 122.9233 | 122.7708 | 44.4354 | -123.3022
2743.375 | 122.9416 | -122.6303 | 0.16022 | 1.4211e-13 | -0.013628 | -0.013291 | -0.04517 | -0.041284 | -0.011924 | 0.0067908 | -0.012162 | 0.016644 | 0.04176 | 0.01785 | 0.054435 | 0.014783 | 0.015142 | 0.005325 | 0.11622 | 0.078201 | 0.29764 | 0.014784 | -105.6389 | -78.3688 | -111.4289 | 0.070773 | 0.22432 | 0.085587 | -123.1329 | 122.6451 | -0.043992 | 122.6451 | 122.6356 | -0.009459 | -0.082016 | 0.13742 | -0.50255 | -0.089444 | 16.9914 | 11.2014 | 11.704 | 0.064105 | -0.07463 | 122.7465 | 122.7085 | 122.9279 | 122.6455 | -0.14543 | 122.7011 | 122.8546 | 122.7159 | 44.2615 | -123.2931
2745.0938 | 122.905 | -122.6807 | 0.21515 | 1.4211e-13 | -0.013628 | -0.013718 | -0.045384 | -0.041498 | -0.012138 | 0.0067908 | -0.011949 | 0.016858 | 0.04176 | 0.017637 | 0.053794 | 0.010204 | 0.019721 | 0.005325 | 0.1208 | 0.08278 | 0.2839 | 0.019363 | -105.6252 | -78.4741 | -111.4014 | 0.075351 | 0.23348 | 0.090166 | -123.1145 | 122.7 | -0.094345 | 122.6909 | 122.686 | -0.014038 | -0.13237 | 0.068754 | -0.43388 | -0.1398 | 17.0555 | 11.2792 | 11.7131 | 0.01833 | -0.12498 | 122.8015 | 122.7634 | 122.9646 | 122.7004 | -0.19579 | 122.756 | 122.9141 | 122.7708 | 44.2065 | -123.3297
2746.8906 | 122.8867 | -122.6669 | 0.19226 | 1.4211e-13 | -0.013201 | -0.013718 | -0.045384 | -0.041498 | -0.011711 | -0.00083919 | -0.012162 | 0.016858 | 0.041546 | 0.01785 | 0.054221 | 0.010204 | 0.019721 | 0.005325 | 0.11165 | 0.078201 | 0.2839 | 0.019363 | -105.5748 | -78.584 | -111.3602 | 0.070773 | 0.22432 | 0.090166 | -123.1191 | 122.6863 | -0.080614 | 122.6771 | 122.6723 | -0.014038 | -0.11406 | 0.091642 | -0.4522 | -0.12149 | 17.0921 | 11.3067 | 11.7589 | 0.032061 | -0.10209 | 122.7786 | 122.7451 | 122.9508 | 122.6867 | -0.1729 | 122.7377 | 122.8913 | 122.7571 | 44.0829 | -123.3114
2748.6719 | 122.9233 | -122.6028 | 0.11902 | 1.4211e-13 | -0.013414 | -0.013718 | -0.045384 | -0.041284 | -0.012138 | -0.0084697 | -0.012162 | 0.016644 | 0.041546 | 0.01785 | 0.054862 | 0.014783 | 0.038035 | 0.005325 | 0.10707 | 0.16978 | 0.32969 | -0.13632 | -105.4512 | -78.3414 | -111.2045 | 0.04788 | 0.21059 | 0.1909 | -123.0779 | 122.4665 | -0.011951 | 122.6176 | 122.6082 | 0.14164 | 0.05076 | 0.21067 | -0.47507 | -0.071139 | 17.1516 | 11.3983 | 11.8734 | 0.091567 | 0.071876 | 122.7099 | 122.7726 | 122.9325 | 122.6409 | -0.25534 | 122.6507 | 122.8134 | 122.7937 | 44.2615 | -123.1969
2750.4688 | 122.8546 | -122.7036 | 0.15564 | 1.4211e-13 | -0.013628 | -0.013505 | -0.044957 | -0.040857 | -0.011924 | -0.0084697 | -0.012376 | 0.016858 | 0.041973 | 0.018278 | 0.054221 | 0.010204 | 0.015142 | 0.000747 | 0.11165 | 0.08278 | 0.32511 | 0.019363 | -105.4924 | -78.5108 | -111.2366 | 0.024988 | 0.17854 | 0.17716 | -123.1374 | 122.7229 | -0.043993 | 122.7138 | 122.7043 | -0.018616 | -0.07286 | 0.16947 | -0.43389 | -0.13065 | 17.2111 | 11.467 | 11.9009 | 0.022896 | 0.021519 | 122.8152 | 122.7863 | 123.0287 | 122.7187 | -0.13628 | 122.7285 | 122.8821 | 122.8807 | 44.1928 | -123.2931
2752.1875 | 123.0103 | -122.6486 | 0.10529 | 1.4211e-13 | -0.013414 | -0.013291 | -0.04517 | -0.041284 | -0.011924 | 0.0067908 | -0.011522 | 0.016644 | 0.041546 | 0.018064 | 0.054435 | 0.014783 | 0.015142 | 0.005325 | 0.11165 | 0.078201 | 0.32511 | 0.014784 | -105.1078 | -78.1445 | -111.145 | 0.024988 | 0.18769 | 0.17716 | -123.142 | 122.6634 | 0.006361 | 122.6634 | 122.6539 | -0.009459 | -0.027085 | 0.21982 | -0.4934 | -0.080298 | 17.5408 | 11.5036 | 11.997 | 0.082407 | 0.071873 | 122.7603 | 122.7268 | 122.9737 | 122.6638 | -0.090502 | 122.6736 | 122.8363 | 122.8258 | 44.5041 | -123.2473
2753.9844 | 122.9553 | -122.6669 | 0.11902 | 1.4211e-13 | -0.013414 | -0.013291 | -0.04517 | -0.041284 | -0.011711 | 0.0067908 | -0.011308 | 0.016644 | 0.041973 | 0.018278 | 0.054648 | 0.005626 | 0.019721 | 0.005325 | 0.11622 | 0.08278 | 0.32511 | 0.014784 | -105.0162 | -78.1582 | -111.0626 | 0.024988 | 0.18311 | 0.18174 | -123.1603 | 122.6817 | -0.002794 | 122.6726 | 122.6723 | -0.009459 | -0.036239 | 0.20609 | -0.4934 | -0.094031 | 17.6507 | 11.6043 | 12.0977 | 0.064096 | 0.062719 | 122.7832 | 122.7497 | 122.992 | 122.6867 | -0.10423 | 122.6919 | 122.85 | 122.8487 | 44.5087 | -123.2794
2755.7656 | 122.8775 | -122.7036 | 0.14191 | 1.4211e-13 | -0.013628 | -0.013718 | -0.04517 | -0.04107 | -0.011924 | -0.00083919 | -0.011308 | 0.016644 | 0.041332 | 0.018491 | 0.054862 | 0.019361 | 0.019721 | 0.000747 | 0.10707 | 0.078201 | 0.32053 | 0.010206 | -104.943 | -78.2498 | -111.0305 | 0.015831 | 0.18311 | -0.060928 | -123.1558 | 122.7138 | -0.034839 | 122.7229 | 122.7043 | -0.009459 | -0.063706 | 0.17862 | -0.4522 | -0.12608 | 17.7606 | 11.673 | 12.1252 | 0.041208 | -0.20284 | 122.8106 | 122.7818 | 123.0241 | 122.7233 | -0.1317 | 122.7194 | 122.8867 | 122.6426 | 44.4538 | -123.2977
2757.5 | 122.9599 | -122.6944 | 0.13733 | 1.4211e-13 | -0.013414 | -0.013505 | -0.045598 | -0.041284 | -0.012138 | -0.0084697 | -0.010881 | 0.016644 | 0.041546 | 0.018064 | 0.054862 | 0.014783 | 0.015142 | 0.005325 | 0.11165 | 0.08278 | 0.32511 | 0.019363 | -104.888 | -78.1948 | -110.9664 | 0.020409 | 0.18311 | -0.070086 | -123.1558 | 122.7138 | -0.025682 | 122.7092 | 122.6997 | -0.014038 | -0.054549 | 0.18778 | -0.46136 | -0.11692 | 17.8064 | 11.728 | 12.1893 | 0.045786 | -0.20742 | 122.806 | 122.7772 | 123.0195 | 122.7095 | -0.11797 | 122.7148 | 122.8775 | 122.6243 | 44.4995 | -123.2931
2759.2812 | 122.8821 | -122.7402 | 0.13275 | 1.4211e-13 | -0.013201 | -0.013718 | -0.044957 | -0.041284 | -0.011924 | -0.0161 | -0.011094 | 0.01643 | 0.041332 | 0.018064 | 0.055076 | 0.019361 | 0.019721 | 0.009904 | 0.1208 | 0.078201 | 0.33427 | 0.019363 | -104.8423 | -78.0804 | -110.9161 | 0.020409 | 0.18311 | -0.083821 | -123.1649 | 122.7595 | -0.011947 | 122.7595 | 122.7501 | -0.009459 | -0.05455 | 0.20152 | -0.42474 | -0.11234 | 17.8979 | 11.8241 | 12.2488 | 0.050364 | -0.21657 | 122.861 | 122.8184 | 123.0744 | 122.7599 | -0.11339 | 122.7606 | 122.9233 | 122.6564 | 44.6598 | -123.2977
2761 | 122.9782 | -122.6807 | 0.10986 | 1.4211e-13 | -0.013842 | -0.013505 | -0.04517 | -0.04107 | -0.012138 | 0.0067908 | -0.011308 | 0.01643 | 0.041332 | 0.018064 | 0.054862 | 0.014783 | 0.019721 | 0.000747 | 0.11622 | 0.078201 | 0.32511 | 0.019363 | -104.7736 | -78.0117 | -110.8474 | 0.024988 | 0.18311 | -0.11129 | -123.1695 | 122.7 | 0.006362 | 122.6954 | 122.6814 | -0.018616 | -0.031662 | 0.21525 | -0.48883 | -0.084875 | 17.9071 | 11.8333 | 12.3221 | 0.073252 | -0.22116 | 122.7969 | 122.7589 | 123.0058 | 122.7004 | -0.0905 | 122.7057 | 122.8638 | 122.5694 | 44.669 | -123.2794
2762.7969 | 122.8867 | -122.7356 | 0.15564 | 1.4211e-13 | -0.013201 | -0.013505 | -0.04517 | -0.04107 | -0.011711 | -0.0084697 | -0.010881 | 0.016217 | 0.041546 | 0.018491 | 0.055076 | 0.010204 | 0.019721 | -0.003831 | 0.11165 | 0.078201 | 0.32969 | 0.019363 | -104.7278 | -77.9155 | -110.7696 | 0.020409 | 0.17854 | -0.070086 | -123.1695 | 122.755 | -0.043993 | 122.7458 | 122.7318 | -0.023194 | -0.077439 | 0.17405 | -0.4339 | -0.13523 | 18.0078 | 11.966 | 12.3999 | 0.022896 | -0.22573 | 122.8472 | 122.8138 | 123.0653 | 122.7553 | -0.13628 | 122.756 | 122.9141 | 122.6655 | 44.82 | -123.3251
2764.5156 | 122.8775 | -122.7631 | 0.15564 | 1.4211e-13 | -0.013628 | -0.013505 | -0.044957 | -0.041284 | -0.011924 | -0.00083919 | -0.011308 | 0.016858 | 0.041332 | 0.018278 | 0.055289 | 0.019361 | 0.0243 | 0.009904 | 0.11165 | 0.073622 | 0.30222 | 0.019363 | -104.6774 | -77.7782 | -110.71 | 0.029566 | 0.17854 | -0.074664 | -123.1832 | 122.7824 | -0.043993 | 122.7824 | 122.773 | -0.009459 | -0.082018 | 0.14658 | -0.42017 | -0.12607 | 18.0856 | 12.053 | 12.4732 | 0.022896 | -0.2303 | 122.8747 | 122.8367 | 123.0653 | 122.7874 | -0.13628 | 122.7926 | 122.9416 | 122.6884 | 44.9849 | -123.3389
2766.3125 | 122.9279 | -122.7493 | 0.13733 | 1.4211e-13 | -0.013414 | -0.013932 | -0.045811 | -0.04107 | -0.011924 | 0.0067908 | -0.011094 | 0.016644 | 0.041332 | 0.018491 | 0.055289 | 0.014783 | 0.010564 | 0.009904 | 0.10707 | 0.073622 | 0.28848 | 0.019363 | -104.5996 | -77.5905 | -110.6642 | 0.015831 | 0.18311 | -0.11129 | -123.1832 | 122.7687 | -0.030261 | 122.7641 | 122.7592 | -0.009459 | -0.063707 | 0.15115 | -0.4339 | -0.1215 | 18.1497 | 12.0851 | 12.519 | 0.045786 | -0.24862 | 122.8564 | 122.823 | 123.0378 | 122.7599 | -0.11797 | 122.7652 | 122.9324 | 122.638 | 45.1589 | -123.3206
2768.1094 | 122.9462 | -122.7539 | 0.14191 | 1.4211e-13 | -0.013414 | -0.013505 | -0.045384 | -0.041498 | -0.011497 | -0.00083919 | -0.010453 | 0.01643 | 0.041546 | 0.018705 | 0.055717 | 0.014783 | 0.019721 | 0.005325 | 0.11622 | 0.073622 | 0.29306 | 0.019363 | -104.5538 | -77.4073 | -110.591 | 0.024988 | 0.17396 | -0.05635 | -123.1787 | 122.7733 | -0.025682 | 122.7687 | 122.7592 | -0.014038 | -0.068285 | 0.15115 | -0.42475 | -0.11692 | 18.2001 | 12.1629 | 12.5877 | 0.032051 | -0.19826 | 122.8701 | 122.8275 | 123.047 | 122.7736 | -0.12254 | 122.7789 | 122.9279 | 122.6976 | 45.3466 | -123.3206
2769.8281 | 122.9736 | -122.7219 | 0.15106 | 1.4211e-13 | -0.013628 | -0.013291 | -0.045384 | -0.04107 | -0.012138 | -0.00083919 | -0.011094 | 0.016217 | 0.041119 | 0.018491 | 0.055717 | 0.019361 | 0.019721 | 0.005325 | 0.11165 | 0.073622 | 0.29306 | 0.019363 | -104.508 | -77.1784 | -110.536 | 0.024988 | 0.18311 | -0.10214 | -123.1832 | 122.7412 | -0.039415 | 122.7412 | 122.7272 | -0.014038 | -0.07744 | 0.142 | -0.46137 | -0.12607 | 18.2139 | 12.1858 | 12.6472 | 0.032053 | -0.2532 | 122.8335 | 122.7955 | 123.0149 | 122.7416 | -0.1317 | 122.7469 | 122.905 | 122.6197 | 45.5435 | -123.3343
2771.625 | 122.8867 | -122.7448 | 0.14648 | 1.4211e-13 | -0.013201 | -0.013505 | -0.04517 | -0.041498 | -0.011924 | 0.0067908 | -0.010453 | 0.016217 | 0.041119 | 0.018919 | 0.055289 | 0.014783 | 0.015142 | 0.000747 | 0.11165 | 0.078201 | 0.29306 | 0.019363 | -104.4714 | -77.0227 | -110.4536 | 0.015831 | 0.18769 | -0.097557 | -123.1832 | 122.7641 | -0.034837 | 122.7595 | 122.7455 | -0.018616 | -0.068283 | 0.14658 | -0.43848 | -0.13065 | 18.2734 | 12.2911 | 12.7296 | 0.041209 | -0.24404 | 122.8564 | 122.823 | 123.0378 | 122.7599 | -0.12712 | 122.7606 | 122.9324 | 122.6472 | 45.7221 | -123.3297
2773.4219 | 122.8958 | -122.7493 | 0.13275 | 1.4211e-13 | -0.013628 | -0.013077 | -0.04517 | -0.04107 | -0.012138 | -0.00083919 | -0.010453 | 0.01643 | 0.041119 | 0.018705 | 0.055289 | 0.014783 | 0.015142 | 0.005325 | 0.11165 | 0.08278 | 0.29306 | 0.014784 | -104.421 | -76.7938 | -110.4262 | 0.020409 | 0.18769 | -0.092979 | -123.1878 | 122.7641 | -0.021104 | 122.7641 | 122.7547 | -0.009459 | -0.049971 | 0.16031 | -0.43848 | -0.11234 | 18.3283 | 12.3232 | 12.7617 | 0.054942 | -0.22573 | 122.861 | 122.8321 | 123.0424 | 122.7645 | -0.11797 | 122.7697 | 122.937 | 122.6564 | 45.9556 | -123.3206
2775.125 | 123.0103 | -122.731 | 0.11444 | 1.4211e-13 | -0.014055 | -0.013505 | -0.044957 | -0.041284 | -0.011711 | -0.00083919 | -0.010453 | 0.016217 | 0.041119 | 0.018919 | 0.05593 | 0.014783 | 0.0243 | 0.005325 | 0.11165 | 0.078201 | 0.28848 | 0.019363 | -104.3661 | -76.6335 | -110.3254 | 0.015831 | 0.18311 | -0.10671 | -123.1878 | 122.7504 | -0.002794 | 122.7458 | 122.7363 | -0.014038 | -0.03624 | 0.17404 | -0.45679 | -0.09861 | 18.365 | 12.4056 | 12.8624 | 0.068674 | -0.22115 | 122.8427 | 122.8092 | 123.0195 | 122.7553 | -0.095078 | 122.7468 | 122.9141 | 122.6243 | 46.0975 | -123.3023
2776.9219 | 123.0194 | -122.699 | 0.10529 | 1.4211e-13 | -0.013414 | -0.013291 | -0.045384 | -0.041284 | -0.011711 | -0.00083919 | -0.01024 | 0.016003 | 0.041119 | 0.019132 | 0.05593 | 0.019361 | 0.015142 | 0.005325 | 0.11165 | 0.08278 | 0.28848 | 0.019363 | -104.3157 | -76.2809 | -110.2338 | 0.024988 | 0.19227 | -0.11587 | -123.1832 | 122.7183 | 0.006361 | 122.7183 | 122.7043 | -0.014038 | -0.022506 | 0.18319 | -0.48425 | -0.080298 | 18.3833 | 12.4651 | 12.9494 | 0.086986 | -0.22116 | 122.8106 | 122.7818 | 122.9875 | 122.7141 | -0.085923 | 122.724 | 122.8912 | 122.5831 | 46.418 | -123.2885
2778.7031 | 122.9416 | -122.7173 | 0.12817 | 1.4211e-13 | -0.013628 | -0.013505 | -0.045598 | -0.041498 | -0.011924 | -0.00083919 | -0.010667 | 0.01643 | 0.040905 | 0.019132 | 0.056144 | 0.010204 | 0.0243 | 0.009904 | 0.10707 | 0.08278 | 0.28848 | 0.014784 | -104.2333 | -75.9925 | -110.1697 | 0.020409 | 0.18769 | -0.0884 | -123.1878 | 122.7321 | -0.021106 | 122.7275 | 122.7272 | -0.00488 | -0.045394 | 0.16031 | -0.47052 | -0.10777 | 18.484 | 12.5475 | 13.0181 | 0.059519 | -0.21657 | 122.8244 | 122.8001 | 123.0058 | 122.7416 | -0.11339 | 122.7377 | 122.905 | 122.6289 | 46.7248 | -123.316
2780.4844 | 122.612 | -122.3831 | 0.1236 | 1.4211e-13 | -0.013628 | -0.013718 | -0.04517 | -0.041498 | -0.011711 | -0.00083919 | -0.0095988 | 0.01643 | 0.041119 | 0.019132 | 0.055503 | 0.019361 | 0.019721 | 0.000747 | 0.10707 | 0.078201 | 0.28848 | 0.010206 | -103.9219 | -75.4568 | -109.7989 | 0.015831 | 0.17854 | -0.11129 | -122.8536 | 122.3933 | -0.016528 | 122.4025 | 122.3839 | -0.009459 | -0.045395 | 0.16489 | -0.47044 | -0.10776 | 18.4612 | 12.5842 | 13.0547 | 0.05494 | -0.23489 | 122.4902 | 122.4613 | 122.6716 | 122.4028 | -0.11339 | 122.3989 | 122.5617 | 122.2718 | 46.9263 | -122.9772
2782.25 | 122.8134 | -122.4655 | 0.10071 | 1.4211e-13 | -0.013842 | -0.013291 | -0.045384 | -0.041284 | -0.011924 | -0.00083919 | -0.0098124 | 0.016217 | 0.040905 | 0.018919 | 0.05593 | 0.014783 | 0.019721 | 0.005325 | 0.11165 | 0.08278 | 0.29764 | 0.005627 | -103.9815 | -75.2004 | -109.776 | 0.015831 | 0.18311 | -0.11587 | -122.9634 | 122.4711 | 0.010939 | 122.4803 | 122.4708 | -0.000302 | -0.017928 | 0.19693 | -0.49793 | -0.084877 | 18.4841 | 12.6895 | 13.1875 | 0.082407 | -0.21658 | 122.5772 | 122.5483 | 122.7632 | 122.4852 | -0.095081 | 122.4813 | 122.6486 | 122.3496 | 47.2651 | -123.0642
2784.0469 | 122.7951 | -122.5204 | 0.11444 | 1.4211e-13 | -0.013842 | -0.013505 | -0.04517 | -0.041498 | -0.011924 | -0.00083919 | -0.010026 | 0.016217 | 0.041119 | 0.019346 | 0.056144 | 0.019361 | 0.015142 | 0.005325 | 0.11622 | 0.078201 | 0.29306 | 0.019363 | -103.9586 | -74.9073 | -109.7439 | 0.015831 | 0.19227 | -0.11129 | -123.0001 | 122.5398 | 0.001784 | 122.5398 | 122.5258 | -0.014038 | -0.03624 | 0.17862 | -0.47963 | -0.09861 | 18.5619 | 12.7765 | 13.2562 | 0.077831 | -0.22573 | 122.6367 | 122.5986 | 122.8135 | 122.5356 | -0.095078 | 122.5363 | 122.7127 | 122.4092 | 47.6131 | -123.1145
2785.8281 | 122.8134 | -122.5342 | 0.09613 | 1.4211e-13 | -0.013842 | -0.013291 | -0.04517 | -0.041711 | -0.011924 | 0.014421 | -0.0095988 | 0.016003 | 0.040905 | 0.01956 | 0.056144 | 0.023939 | 0.0243 | 0.005325 | 0.10707 | 0.078201 | 0.28848 | 0.005627 | -103.8945 | -74.4861 | -109.6981 | 0.024988 | 0.19227 | -0.11129 | -123.0138 | 122.5398 | 0.010938 | 122.5581 | 122.5395 | -0.000302 | -0.017929 | 0.19235 | -0.47963 | -0.071142 | 18.6397 | 12.836 | 13.3157 | 0.096142 | -0.20742 | 122.6412 | 122.6124 | 122.8227 | 122.5585 | -0.090503 | 122.5592 | 122.7265 | 122.4229 | 48.0481 | -123.1099
2787.5469 | 122.8912 | -122.5525 | 0.086975 | 1.4211e-13 | -0.013414 | -0.013718 | -0.044957 | -0.04107 | -0.011924 | -0.0084697 | -0.0098124 | 0.016217 | 0.040478 | 0.01956 | 0.05593 | 0.019361 | 0.015142 | 0.005325 | 0.11165 | 0.078201 | 0.28848 | 0.028521 | -103.8716 | -74.0877 | -109.5882 | 0.029566 | 0.18311 | -0.11129 | -123.0276 | 122.581 | 0.024672 | 122.5719 | 122.5578 | -0.023196 | -0.008774 | 0.20151 | -0.47506 | -0.057409 | 18.6809 | 12.9642 | 13.4393 | 0.09614 | -0.19827 | 122.6641 | 122.6307 | 122.841 | 122.5676 | -0.058454 | 122.5821 | 122.7356 | 122.4412 | 48.4647 | -123.1145
2789.3438 | 122.8638 | -122.5662 | 0.1236 | 1.4211e-13 | -0.013842 | -0.013505 | -0.04517 | -0.041284 | -0.011924 | -0.00083919 | -0.0098124 | 0.016003 | 0.040691 | 0.019346 | 0.056144 | 0.023939 | 0.019721 | 0.014482 | 0.11165 | 0.078201 | 0.28848 | 0.010206 | -103.8075 | -73.5795 | -109.46 | 0.015831 | 0.18311 | -0.074664 | -123.0413 | 122.5764 | -0.011949 | 122.5902 | 122.5807 | 0.004276 | -0.045395 | 0.16489 | -0.47506 | -0.10776 | 18.7588 | 13.1062 | 13.5812 | 0.059519 | -0.19826 | 122.6779 | 122.6444 | 122.8547 | 122.5859 | -0.11339 | 122.5821 | 122.7493 | 122.4916 | 48.9867 | -123.1649
2791.125 | 122.8729 | -122.58 | 0.10529 | 1.4211e-13 | -0.013842 | -0.013291 | -0.045384 | -0.040857 | -0.011924 | -0.0084697 | -0.0093852 | 0.016217 | 0.040478 | 0.01956 | 0.056144 | 0.014783 | 0.019721 | 0.000747 | 0.11622 | 0.078201 | 0.29306 | 0.014784 | -103.7479 | -73.1262 | -109.3547 | 0.015831 | 0.18311 | -0.10214 | -123.055 | 122.5947 | 0.010939 | 122.5947 | 122.5807 | -0.014037 | -0.027085 | 0.18777 | -0.47507 | -0.089455 | 18.832 | 13.2252 | 13.7003 | 0.077829 | -0.20742 | 122.6962 | 122.6582 | 122.873 | 122.5997 | -0.090502 | 122.5958 | 122.7631 | 122.4778 | 49.4537 | -123.1603
2792.8594 | 122.8867 | -122.58 | 0.11444 | 1.4211e-13 | -0.013842 | -0.013291 | -0.044957 | -0.040857 | -0.011711 | -0.0084697 | -0.0093852 | 0.015789 | 0.040691 | 0.019773 | 0.056571 | 0.014783 | 0.019721 | 0.005325 | 0.11622 | 0.073622 | 0.28848 | 0.014784 | -103.7022 | -72.7279 | -109.2632 | 0.020409 | 0.18769 | -0.11129 | -123.0596 | 122.5947 | 0.001784 | 122.5947 | 122.5853 | -0.009459 | -0.040819 | 0.17404 | -0.47965 | -0.094032 | 18.8778 | 13.3168 | 13.7964 | 0.073252 | -0.22573 | 122.6962 | 122.6536 | 122.8684 | 122.5997 | -0.099657 | 122.6004 | 122.7676 | 122.4687 | 49.8521 | -123.174
2794.6406 | 122.7402 | -122.6212 | 0.14191 | 1.4211e-13 | -0.013628 | -0.013505 | -0.045598 | -0.041498 | -0.011924 | -0.0084697 | -0.0091716 | 0.016003 | 0.040691 | 0.01956 | 0.056357 | 0.019361 | 0.015142 | 0.005325 | 0.11622 | 0.078201 | 0.28848 | 0.014784 | -103.6793 | -72.3158 | -109.1533 | 0.020409 | 0.19227 | -0.10214 | -123.0688 | 122.6359 | -0.025682 | 122.6405 | 122.6265 | -0.009459 | -0.063706 | 0.14657 | -0.4476 | -0.1215 | 18.9419 | 13.4679 | 13.9155 | 0.050365 | -0.24404 | 122.7374 | 122.6994 | 122.9096 | 122.6363 | -0.12712 | 122.6416 | 122.8134 | 122.519 | 50.3054 | -123.2107
2796.3594 | 122.0627 | -121.9254 | 0.14191 | 1.4211e-13 | -0.013628 | -0.013718 | -0.044957 | -0.041284 | -0.011924 | -0.00083919 | -0.0093852 | 0.016003 | 0.040478 | 0.019773 | 0.055717 | 0.010204 | 0.010564 | 0.005325 | 0.10707 | 0.078201 | 0.29306 | 0.005627 | -102.9604 | -71.487 | -108.3612 | 0.024988 | 0.18311 | -0.097557 | -122.2904 | 121.931 | -0.034839 | 121.9356 | 121.9307 | -0.000302 | -0.063706 | 0.15115 | -0.36501 | -0.11692 | 18.965 | 13.5642 | 13.9292 | 0.041208 | -0.23946 | 122.0324 | 122.0036 | 122.2184 | 121.9359 | -0.13628 | 121.9503 | 122.1085 | 121.8278 | 50.4383 | -122.4323
2798.1406 | 122.3419 | -122.0764 | 0.11902 | 1.4211e-13 | -0.013842 | -0.013718 | -0.04517 | -0.041711 | -0.012138 | -0.0161 | -0.008958 | 0.016003 | 0.040478 | 0.020201 | 0.056357 | 0.019361 | 0.0243 | 0.009904 | 0.10707 | 0.08278 | 0.28848 | 0.019363 | -103.1207 | -71.2489 | -108.4573 | 0.024988 | 0.17396 | -0.11129 | -122.5514 | 122.0958 | -0.011951 | 122.0958 | 122.0863 | -0.009459 | -0.036239 | 0.16946 | -0.47494 | -0.094031 | 18.9558 | 13.6191 | 14.094 | 0.054939 | -0.23031 | 122.1835 | 122.1592 | 122.3649 | 122.1007 | -0.099656 | 122.1014 | 122.2504 | 121.9651 | 50.8275 | -122.6704
2799.9219 | 121.8933 | -121.6324 | 0.14191 | 1.4211e-13 | -0.014055 | -0.013505 | -0.044957 | -0.04107 | -0.011924 | -0.0084697 | -0.0085306 | 0.015789 | 0.040264 | 0.020201 | 0.055717 | 0.014783 | 0.0243 | 0.000747 | 0.11165 | 0.078201 | 0.28848 | 0.019363 | -102.4705 | -70.3561 | -107.6881 | 0.024988 | 0.18769 | -0.11587 | -121.8233 | 121.6517 | -0.03026 | 121.6472 | 121.6331 | -0.018616 | -0.063706 | 0.14657 | -0.19094 | -0.11692 | 19.1619 | 13.9443 | 14.1352 | 0.045786 | -0.25778 | 121.744 | 121.7106 | 121.9209 | 121.6567 | -0.12254 | 121.6574 | 121.8201 | 121.5165 | 51.2763 | -121.9652
2801.7188 | 122.1909 | -122.0215 | 0.15106 | 1.4211e-13 | -0.013842 | -0.013718 | -0.044957 | -0.041498 | -0.011711 | -0.0084697 | -0.0087442 | 0.015576 | 0.04005 | 0.020201 | 0.056357 | 0.023939 | 0.015142 | 0.005325 | 0.11165 | 0.08278 | 0.2839 | 0.019363 | -102.9329 | -70.3332 | -108.1231 | 0.024988 | 0.18311 | -0.11587 | -122.4644 | 122.0408 | -0.039415 | 122.0454 | 122.0268 | -0.014038 | -0.068282 | 0.13284 | -0.44287 | -0.12607 | 19.0886 | 13.8984 | 14.3413 | 0.032053 | -0.26693 | 122.1331 | 122.1043 | 122.3054 | 122.0366 | -0.1317 | 122.0465 | 122.2046 | 121.9056 | 51.6883 | -122.6154
2803.4531 | 121.8475 | -121.6049 | 0.16022 | 1.4211e-13 | -0.013842 | -0.013291 | -0.045384 | -0.041284 | -0.011711 | -0.00083919 | -0.0087442 | 0.015789 | 0.039409 | 0.020201 | 0.055717 | 0.014783 | 0.028878 | 0.000747 | 0.10249 | 0.08278 | 0.29306 | 0.019363 | -102.5437 | -69.6601 | -107.656 | 0.029566 | 0.19227 | -0.038035 | -122.0614 | 121.6243 | -0.057727 | 121.6197 | 121.6057 | -0.018616 | -0.077437 | 0.13284 | -0.4565 | -0.13065 | 19.0612 | 13.9489 | 14.4054 | 0.032055 | -0.19825 | 121.7074 | 121.6877 | 121.898 | 121.6338 | -0.14085 | 121.6345 | 121.7972 | 121.5669 | 51.9448 | -122.2216
2805.2344 | 122.0261 | -121.7697 | 0.15106 | 1.4211e-13 | -0.013842 | -0.013718 | -0.045384 | -0.041284 | -0.011924 | -0.0161 | -0.0091716 | 0.015789 | 0.039623 | 0.020201 | 0.056144 | 0.010204 | 0.019721 | 0.009904 | 0.11165 | 0.087359 | 0.29764 | 0.014784 | -102.649 | -69.3488 | -107.6743 | 0.029566 | 0.19227 | -0.028878 | -122.24 | 121.7845 | -0.039415 | 121.7799 | 121.7796 | -0.00488 | -0.063703 | 0.14658 | -0.47028 | -0.1215 | 19.1207 | 14.0954 | 14.5656 | 0.04121 | -0.17994 | 121.8814 | 121.8571 | 122.0674 | 121.7894 | -0.13628 | 121.7993 | 121.962 | 121.7408 | 52.4209 | -122.3911
2806.9688 | 117.366 | -117.0273 | 0.086975 | 1.4211e-13 | -0.014269 | -0.013718 | -0.045384 | -0.04107 | -0.012352 | -0.00083919 | -0.0087442 | 0.015789 | 0.038982 | 0.019987 | 0.055289 | 0.014783 | 0.0243 | 0.009904 | 0.11165 | 0.08278 | 0.28848 | 0.019363 | -101.5502 | -68.1354 | -106.406 | 0.020409 | 0.17854 | -0.019721 | -120.9717 | 117.0466 | 0.024672 | 117.0421 | 117.0372 | -0.009459 | -0.004195 | 0.20151 | -3.9444 | -0.066566 | 15.4771 | 10.6212 | 14.5656 | 0.091561 | -0.1067 | 117.1389 | 117.1101 | 117.3158 | 117.0516 | -0.067612 | 117.0477 | 117.2058 | 117.0076 | 48.8919 | -121.0586
2808.75 | 121.8933 | -121.5088 | 0.13733 | 1.4211e-13 | -0.014055 | -0.013505 | -0.045384 | -0.041284 | -0.011924 | 0.0067908 | -0.008958 | 0.016003 | 0.039837 | 0.020628 | 0.05593 | 0.014783 | 0.0243 | 0.009904 | 0.10707 | 0.087359 | 0.29764 | 0.019363 | -102.2782 | -68.1904 | -107.07 | 0.024988 | 0.20143 | -0.033457 | -121.9927 | 121.5282 | -0.030261 | 121.5236 | 121.5187 | -0.009459 | -0.04997 | 0.16031 | -0.48395 | -0.11234 | 19.2306 | 14.4388 | 14.9228 | 0.0641 | -0.17079 | 121.6159 | 121.5961 | 121.8064 | 121.5331 | -0.11797 | 121.5338 | 121.7102 | 121.4753 | 53.3184 | -122.1301
2810.5469 | 121.8567 | -121.6873 | 0.14191 | 1.4211e-13 | -0.013842 | -0.013505 | -0.04517 | -0.041498 | -0.012138 | -0.00083919 | -0.0085306 | 0.015789 | 0.039409 | 0.020842 | 0.056357 | 0.014783 | 0.019721 | 0.009904 | 0.11165 | 0.087359 | 0.29306 | 0.014784 | -102.2599 | -67.7783 | -106.9784 | 0.029566 | 0.20143 | 0.030644 | -122.1118 | 121.7021 | -0.03026 | 121.7021 | 121.6972 | -0.00488 | -0.054548 | 0.15115 | -0.42447 | -0.11234 | 19.4275 | 14.7089 | 15.1334 | 0.059522 | -0.11126 | 121.799 | 121.7747 | 121.9804 | 121.707 | -0.12712 | 121.7169 | 121.8887 | 121.718 | 53.909 | -122.2537
2812.2656 | 121.9437 | -121.7148 | 0.15106 | 1.4211e-13 | -0.013628 | -0.013505 | -0.045384 | -0.041711 | -0.011711 | -0.0084697 | -0.0085306 | 0.015789 | 0.039837 | 0.021055 | 0.056785 | 0.019361 | 0.028878 | 0.005325 | 0.11165 | 0.087359 | 0.29764 | 0.023942 | -102.3102 | -67.3204 | -106.8364 | 0.038723 | 0.20143 | 0.021486 | -122.1576 | 121.7387 | -0.039415 | 121.7341 | 121.7201 | -0.018617 | -0.063703 | 0.14658 | -0.44279 | -0.11234 | 19.4046 | 14.8783 | 15.3211 | 0.050367 | -0.12958 | 121.8264 | 121.8021 | 122.0124 | 121.7437 | -0.12712 | 121.7535 | 121.9162 | 121.7363 | 54.3944 | -122.3086
2814.0312 | 122.049 | -121.7285 | 0.12817 | 1.4211e-13 | -0.013842 | -0.013718 | -0.04517 | -0.041711 | -0.012138 | 0.0067908 | -0.008317 | 0.015789 | 0.039837 | 0.021055 | 0.056571 | 0.019361 | 0.028878 | 0.005325 | 0.11622 | 0.087359 | 0.29306 | 0.014784 | -102.2919 | -66.8396 | -106.7174 | 0.038723 | 0.20143 | 0.039801 | -122.1942 | 121.7433 | -0.011949 | 121.7479 | 121.7338 | -0.009459 | -0.040815 | 0.16489 | -0.46569 | -0.089451 | 19.4366 | 15.0111 | 15.4768 | 0.073255 | -0.088373 | 121.8447 | 121.8159 | 122.0216 | 121.7574 | -0.11339 | 121.7672 | 121.9299 | 121.7683 | 54.8889 | -122.3224
2815.8281 | 121.994 | -121.2753 | 0.41199 | 1.4211e-13 | -0.013628 | -0.013718 | -0.045384 | -0.041498 | -0.011924 | -0.00083919 | -0.0085306 | 0.015362 | 0.039837 | 0.020628 | 0.056785 | 0.033096 | 0.042614 | 0.01906 | 0.13454 | 0.10567 | 0.32053 | -0.044742 | -102.0859 | -66.2994 | -106.3877 | 0.21728 | 0.38457 | 0.21379 | -122.0294 | 121.2306 | -0.27745 | 121.3084 | 121.2944 | 0.063802 | -0.30631 | -0.091456 | -0.75404 | -0.1947 | 19.1895 | 14.8876 | 15.6416 | -0.027414 | -0.1982 | 121.4099 | 121.381 | 121.5959 | 121.3179 | -0.45673 | 121.4926 | 121.6599 | 121.4891 | 54.976 | -122.4414
2817.5625 | 120.7718 | -120.4605 | 0.10529 | 1.4211e-13 | -0.0065769 | -0.0094445 | -0.057778 | -0.041498 | -0.012352 | 0.0067908 | -0.0087442 | 0.01643 | 0.039623 | 0.020201 | 0.055076 | 1.8232 | 1.7825 | 1.8458 | 1.9567 | 1.9143 | 2.152 | 1.567 | -83.2216 | -50.8416 | -87.3037 | 18.2337 | 18.6944 | 18.0749 | -101.7361 | 122.0276 | 1.8515 | 122.2838 | 122.3063 | 0.27875 | 1.8091 | 2.0467 | 18.7245 | 18.1284 | 37.2389 | 33.1568 | 14.4324 | 18.5891 | 17.9696 | 122.4172 | 122.3749 | 122.6125 | 122.243 | 1.4618 | 138.6942 | 139.1549 | 138.5354 | 69.6189 | -101.8413
2819.3594 | 121.3852 | -121.0464 | 0.11444 | 1.4211e-13 | -0.014055 | -0.013505 | -0.04517 | -0.041711 | -0.011924 | -0.00083919 | -0.0085306 | 0.014935 | 0.039196 | 0.021055 | 0.057426 | 0.014783 | 0.015142 | 0.000747 | 0.11165 | 0.08278 | 0.29306 | 0.019363 | -101.6051 | -65.2417 | -105.6139 | 0.029566 | 0.18311 | 0.18174 | -121.5394 | 121.0658 | -0.002794 | 121.0612 | 121.0472 | -0.018616 | -0.031661 | 0.17862 | -0.49299 | -0.084875 | 19.4413 | 15.4325 | 15.9255 | 0.068674 | 0.067297 | 121.1581 | 121.1292 | 121.3395 | 121.0616 | -0.095078 | 121.076 | 121.2296 | 121.2282 | 55.8048 | -121.6539
2821.1406 | 121.4447 | -121.1746 | 0.11902 | 1.4211e-13 | -0.013842 | -0.013505 | -0.04517 | -0.041284 | -0.011924 | -0.00083919 | -0.008317 | 0.015576 | 0.039409 | 0.021483 | 0.057212 | 0.014783 | 0.019721 | 0.005325 | 0.11165 | 0.08278 | 0.28848 | 0.010206 | -101.5364 | -64.7884 | -105.5269 | 0.011252 | 0.18311 | 0.17716 | -121.6447 | 121.1848 | -0.007372 | 121.1894 | 121.1799 | -0.004881 | -0.036239 | 0.16946 | -0.47013 | -0.10777 | 19.6382 | 15.6477 | 16.1178 | 0.064096 | 0.05814 | 121.2863 | 121.2574 | 121.4631 | 121.1943 | -0.10881 | 121.1859 | 121.3577 | 121.3518 | 56.3862 | -121.7638
2822.875 | 121.4676 | -121.2616 | 0.13733 | 1.4211e-13 | -0.014055 | -0.013505 | -0.045384 | -0.041284 | -0.011711 | -0.00083919 | -0.008317 | 0.015362 | 0.039409 | 0.021483 | 0.057639 | 0.010204 | 0.019721 | 0.005325 | 0.11622 | 0.078201 | 0.30222 | 0.023942 | -101.4815 | -64.4221 | -105.417 | 0.024988 | 0.18311 | 0.17716 | -121.7043 | 121.2855 | -0.021104 | 121.2718 | 121.2669 | -0.018617 | -0.059128 | 0.16489 | -0.44268 | -0.11234 | 19.7801 | 15.8446 | 16.2872 | 0.045786 | 0.03983 | 121.3778 | 121.3398 | 121.5638 | 121.2813 | -0.11339 | 121.2866 | 121.4447 | 121.4388 | 56.8395 | -121.8416
2824.6719 | 121.5912 | -121.2845 | 0.10529 | 1.4211e-13 | -0.013842 | -0.013291 | -0.045384 | -0.041284 | -0.011924 | -0.0084697 | -0.008317 | 0.015576 | 0.039196 | 0.02191 | 0.057853 | 0.001048 | 0.019721 | 0.005325 | 0.11622 | 0.08278 | 0.29306 | 0.028521 | -101.2938 | -63.9367 | -105.2476 | 0.020409 | 0.17854 | -0.11129 | -121.7592 | 121.313 | 0.010939 | 121.2855 | 121.2898 | -0.023196 | -0.022506 | 0.18777 | -0.47473 | -0.084877 | 19.9907 | 16.0369 | 16.5116 | 0.07325 | -0.21658 | 121.4007 | 121.3673 | 121.5775 | 121.3042 | -0.076765 | 121.3049 | 121.463 | 121.1732 | 57.3477 | -121.8645
2826.3906 | 121.5958 | -121.344 | 0.12817 | 1.4211e-13 | -0.014055 | -0.013077 | -0.044957 | -0.041498 | -0.011924 | -0.00083919 | -0.0081034 | 0.015148 | 0.039409 | 0.02191 | 0.058067 | 0.001048 | 0.0243 | 0.000747 | 0.10707 | 0.087359 | 0.29764 | 0.014784 | -101.0648 | -63.4789 | -105.0828 | 0.015831 | 0.18311 | -0.019721 | -121.7958 | 121.3588 | -0.021106 | 121.345 | 121.3447 | -0.014037 | -0.040815 | 0.16946 | -0.45186 | -0.11234 | 20.2792 | 16.2612 | 16.7131 | 0.054941 | -0.14789 | 121.4511 | 121.4314 | 121.6416 | 121.3683 | -0.11339 | 121.3598 | 121.5271 | 121.3243 | 57.8651 | -121.924
2828.1719 | 121.6599 | -121.3577 | 0.11444 | 1.4211e-13 | -0.014269 | -0.013718 | -0.04517 | -0.041284 | -0.012138 | -0.00083919 | -0.0081034 | 0.015148 | 0.038982 | 0.022124 | 0.057639 | 0.005626 | 0.019721 | 0.000747 | 0.11165 | 0.073622 | 0.29306 | 0.019363 | -100.845 | -63.0118 | -104.8676 | 0.024988 | 0.17854 | -0.11587 | -121.8371 | 121.3771 | -0.002794 | 121.3634 | 121.3585 | -0.018616 | -0.040819 | 0.17862 | -0.47933 | -0.089453 | 20.5127 | 16.4901 | 16.9695 | 0.064095 | -0.23031 | 121.4694 | 121.4313 | 121.6508 | 121.3774 | -0.095078 | 121.3827 | 121.5363 | 121.2419 | 58.3459 | -121.9515
2829.9062 | 121.6507 | -121.3669 | 0.12817 | 1.4211e-13 | -0.014269 | -0.013718 | -0.044957 | -0.041284 | -0.012138 | -0.0084697 | -0.0078898 | 0.015148 | 0.039409 | 0.022337 | 0.05828 | 0.010204 | 0.0243 | 0.000747 | 0.10707 | 0.08278 | 0.30222 | 0.014784 | -100.4146 | -62.4945 | -104.6478 | 0.020409 | 0.18769 | -0.12045 | -121.86 | 121.3817 | -0.021106 | 121.3771 | 121.3676 | -0.014037 | -0.045394 | 0.17404 | -0.49307 | -0.10777 | 20.9522 | 16.7191 | 17.2121 | 0.059519 | -0.24862 | 121.474 | 121.4497 | 121.6691 | 121.3912 | -0.11339 | 121.3873 | 121.5546 | 121.2464 | 58.8724 | -121.9881
2831.6875 | 121.6049 | -121.4401 | 0.12817 | 1.4211e-13 | -0.014269 | -0.013718 | -0.045384 | -0.04107 | -0.012138 | -0.00083919 | -0.0074624 | 0.014935 | 0.039196 | 0.022551 | 0.058708 | 0.010204 | 0.019721 | 0.009904 | 0.11622 | 0.08278 | 0.29764 | 0.014784 | -99.6363 | -61.7527 | -104.4143 | 0.020409 | 0.18311 | -0.10671 | -121.892 | 121.4549 | -0.011949 | 121.4503 | 121.45 | -0.00488 | -0.045394 | 0.16946 | -0.45188 | -0.10777 | 21.8039 | 17.0258 | 17.4777 | 0.054941 | -0.23489 | 121.5563 | 121.5229 | 121.7378 | 121.4598 | -0.11339 | 121.4605 | 121.6232 | 121.3334 | 59.6874 | -122.0202
2833.4844 | 121.6553 | -121.463 | 0.13275 | 1.4211e-13 | -0.013842 | -0.013505 | -0.045598 | -0.041498 | -0.012352 | -0.00083919 | -0.0081034 | 0.015362 | 0.039196 | 0.022765 | 0.059349 | 0.005626 | 0.010564 | 0.014482 | 0.11622 | 0.08278 | 0.29306 | 0.028521 | -98.7984 | -61.3635 | -104.0938 | 0.029566 | 0.18311 | 0.016908 | -121.9149 | 121.4915 | -0.016526 | 121.4686 | 121.4775 | -0.014039 | -0.049971 | 0.16031 | -0.45188 | -0.10319 | 22.6647 | 17.3692 | 17.8211 | 0.050364 | -0.11584 | 121.5792 | 121.5458 | 121.7561 | 121.4736 | -0.10423 | 121.4926 | 121.6461 | 121.4799 | 60.0995 | -122.0476
2835.1875 | 121.7194 | -121.463 | 0.1236 | 1.4211e-13 | -0.014055 | -0.013291 | -0.04517 | -0.041498 | -0.011924 | -0.0084697 | -0.0078898 | 0.015148 | 0.039409 | 0.023192 | 0.059349 | 0.010204 | 0.019721 | 0.005325 | 0.11165 | 0.08278 | 0.28848 | 0.014784 | -98.4595 | -60.8278 | -103.8008 | 0.020409 | 0.18769 | -0.079243 | -121.9286 | 121.4778 | -0.011949 | 121.4732 | 121.4683 | -0.009459 | -0.040816 | 0.16489 | -0.46562 | -0.10319 | 23.0035 | 17.6623 | 18.1279 | 0.064097 | -0.20284 | 121.5747 | 121.5458 | 121.7515 | 121.4827 | -0.10881 | 121.4834 | 121.6507 | 121.3838 | 60.6352 | -122.0522
2836.9844 | 121.7606 | -121.4584 | 0.13275 | 1.4211e-13 | -0.014055 | -0.013505 | -0.045811 | -0.041498 | -0.011711 | -0.00083919 | -0.0078898 | 0.015148 | 0.039196 | 0.023619 | 0.059776 | 0.010204 | 0.0243 | 0.005325 | 0.11622 | 0.078201 | 0.29764 | 0.023942 | -98.3771 | -60.5119 | -103.4161 | 0.020409 | 0.18311 | -0.015142 | -121.9515 | 121.4824 | -0.016526 | 121.4686 | 121.4638 | -0.018617 | -0.05455 | 0.16489 | -0.49309 | -0.11234 | 23.0813 | 18.0423 | 18.5354 | 0.050364 | -0.14789 | 121.5747 | 121.5366 | 121.7561 | 121.4827 | -0.10881 | 121.4788 | 121.6415 | 121.4433 | 60.9466 | -122.0843
2838.7812 | 121.7422 | -121.4905 | 0.11902 | 1.4211e-13 | -0.014055 | -0.013718 | -0.04517 | -0.041284 | -0.011711 | -0.00083919 | -0.007676 | 0.014935 | 0.039196 | 0.023619 | 0.060417 | 0.005626 | 0.0243 | 0.005325 | 0.11622 | 0.087359 | 0.30222 | 0.010206 | -98.2398 | -59.9395 | -103.0315 | 0.024988 | 0.17854 | -0.065507 | -121.9698 | 121.5007 | -0.002794 | 121.4961 | 121.4958 | -0.004881 | -0.03166 | 0.1832 | -0.47937 | -0.094031 | 23.2507 | 18.4589 | 18.9383 | 0.059517 | -0.18453 | 121.6067 | 121.5778 | 121.7927 | 121.5148 | -0.10881 | 121.5155 | 121.669 | 121.425 | 61.5509 | -122.0889
2840.5781 | 121.7926 | -121.5088 | 0.11902 | 1.4211e-13 | -0.014269 | -0.013505 | -0.045598 | -0.041284 | -0.011924 | -0.00083919 | -0.007676 | 0.015148 | 0.039409 | 0.023833 | 0.060203 | 0.010204 | 0.019721 | 0.009904 | 0.11165 | 0.08278 | 0.29306 | 0.028521 | -98.1619 | -59.3764 | -102.6149 | 0.024988 | 0.19227 | -0.065507 | -121.9882 | 121.5373 | -0.007372 | 121.519 | 121.5187 | -0.018617 | -0.036239 | 0.17404 | -0.47937 | -0.094031 | 23.3469 | 18.8939 | 19.3733 | 0.073253 | -0.18453 | 121.6204 | 121.5916 | 121.8018 | 121.5285 | -0.090498 | 121.5338 | 121.7011 | 121.4433 | 62.1324 | -122.1072
2842.3125 | 121.8018 | -121.5363 | 0.11444 | 1.4211e-13 | -0.014269 | -0.013291 | -0.045384 | -0.041284 | -0.012138 | -0.0084697 | -0.007676 | 0.014935 | 0.039196 | 0.02426 | 0.060203 | 0.005626 | 0.015142 | 0.005325 | 0.11165 | 0.078201 | 0.29764 | 0.019363 | -98.0703 | -58.9597 | -102.3218 | 0.024988 | 0.19227 | -0.019721 | -122.0065 | 121.5556 | -0.002794 | 121.5419 | 121.5416 | -0.014038 | -0.03624 | 0.1832 | -0.47022 | -0.089453 | 23.4659 | 19.2144 | 19.6846 | 0.077831 | -0.13416 | 121.6479 | 121.6145 | 121.8339 | 121.5514 | -0.095078 | 121.5612 | 121.7285 | 121.5165 | 62.5766 | -122.1209
2844.0938 | 121.8155 | -121.5546 | 0.11444 | 1.4211e-13 | -0.014483 | -0.013505 | -0.045384 | -0.041498 | -0.011924 | -0.0084697 | -0.0078898 | 0.014935 | 0.039623 | 0.024688 | 0.061058 | 0.005626 | 0.0243 | 0.000747 | 0.11165 | 0.087359 | 0.29306 | 0.014784 | -97.7819 | -58.3416 | -102.1936 | 0.020409 | 0.18769 | -0.047193 | -122.0248 | 121.5693 | -0.002794 | 121.5602 | 121.5553 | -0.014037 | -0.027082 | 0.17862 | -0.47022 | -0.094032 | 23.7727 | 19.3609 | 19.8312 | 0.073252 | -0.16163 | 121.6662 | 121.6419 | 121.8476 | 121.5789 | -0.099657 | 121.575 | 121.7423 | 121.5074 | 63.213 | -122.1392
2845.875 | 121.7285 | -121.6049 | 0.16022 | 1.4211e-13 | -0.014055 | -0.013291 | -0.044743 | -0.041498 | -0.011924 | -0.0161 | -0.0074624 | 0.015148 | 0.038768 | 0.024688 | 0.061272 | 0.014783 | 0.019721 | 0.000747 | 0.1208 | 0.08278 | 0.30222 | 0.019363 | -97.5255 | -57.8196 | -101.7999 | 0.029566 | 0.19227 | -0.042614 | -122.0339 | 121.6243 | -0.039413 | 121.6197 | 121.6057 | -0.018616 | -0.077437 | 0.142 | -0.42903 | -0.13065 | 24.0794 | 19.8051 | 20.2341 | 0.032055 | -0.20283 | 121.7257 | 121.6877 | 121.9071 | 121.6246 | -0.14085 | 121.6345 | 121.7972 | 121.5623 | 63.7853 | -122.1942
2847.6719 | 121.8842 | -121.5637 | 0.11902 | 1.4211e-13 | -0.014483 | -0.013505 | -0.045811 | -0.041711 | -0.012138 | 0.0067908 | -0.0072488 | 0.014721 | 0.038982 | 0.024901 | 0.061058 | 0.005626 | 0.019721 | 0.000747 | 0.11622 | 0.08278 | 0.29306 | 0.014784 | -97.3103 | -58.1401 | -101.374 | 0.024988 | 0.18769 | -0.005985 | -122.0477 | 121.5785 | -0.002794 | 121.5693 | 121.5645 | -0.014037 | -0.036239 | 0.17404 | -0.48396 | -0.094031 | 24.2534 | 20.1897 | 20.6736 | 0.068674 | -0.125 | 121.6799 | 121.6465 | 121.8568 | 121.5834 | -0.10423 | 121.5887 | 121.7514 | 121.5577 | 63.4236 | -122.1667
2849.4062 | 121.7743 | -121.6187 | 0.16479 | 1.4211e-13 | -0.014055 | -0.013718 | -0.045384 | -0.041498 | -0.012138 | -0.00083919 | -0.0074624 | 0.014721 | 0.038768 | 0.025756 | 0.061699 | 0.005626 | 0.015142 | 0.009904 | 0.11622 | 0.08278 | 0.29306 | 0.014784 | -96.9806 | -57.8974 | -100.907 | 0.029566 | 0.19227 | -0.038035 | -122.0706 | 121.6334 | -0.04857 | 121.6243 | 121.6286 | -0.00488 | -0.082015 | 0.12826 | -0.45193 | -0.13523 | 24.638 | 20.7116 | 21.1636 | 0.027477 | -0.20283 | 121.7349 | 121.7014 | 121.9117 | 121.6338 | -0.15001 | 121.6482 | 121.8109 | 121.5806 | 63.7212 | -122.2354
2851.1719 | 121.8613 | -121.6003 | 0.1236 | 1.4211e-13 | -0.014269 | -0.013718 | -0.045384 | -0.041498 | -0.012138 | 0.0067908 | -0.007676 | 0.014721 | 0.039409 | 0.02597 | 0.06234 | 0.005626 | 0.019721 | 0.009904 | 0.11165 | 0.091937 | 0.29306 | 0.019363 | -96.4586 | -57.5311 | -100.3988 | 0.020409 | 0.18311 | -0.015142 | -122.066 | 121.6197 | -0.011949 | 121.606 | 121.6102 | -0.009459 | -0.031659 | 0.16946 | -0.46566 | -0.10319 | 25.1417 | 21.2016 | 21.6672 | 0.059519 | -0.13874 | 121.712 | 121.6923 | 121.8934 | 121.6201 | -0.10423 | 121.6208 | 121.7835 | 121.5852 | 64.0692 | -122.1896
2852.9062 | 121.9208 | -121.5866 | 0.12817 | 1.4211e-13 | -0.014269 | -0.013718 | -0.045384 | -0.041284 | -0.011924 | -0.00083919 | -0.0074624 | 0.014721 | 0.038555 | 0.02597 | 0.062981 | 0.005626 | 0.0243 | 0.009904 | 0.1208 | 0.087359 | 0.29764 | 0.0331 | -95.7398 | -57.0458 | -100.2111 | 0.024988 | 0.19227 | -0.001407 | -122.0752 | 121.6197 | -0.00737 | 121.5922 | 121.5965 | -0.023196 | -0.040815 | 0.16946 | -0.48855 | -0.10319 | 25.8468 | 21.3756 | 21.8641 | 0.064098 | -0.12958 | 121.7074 | 121.674 | 121.8842 | 121.6109 | -0.095074 | 121.6116 | 121.7789 | 121.5852 | 64.5408 | -122.2033
2854.7031 | 121.8796 | -121.6232 | 0.11902 | 1.4211e-13 | -0.014055 | -0.013291 | -0.04517 | -0.041498 | -0.012352 | -0.0084697 | -0.0074624 | 0.014935 | 0.038982 | 0.026611 | 0.063408 | 0.010204 | 0.019721 | 0.009904 | 0.1208 | 0.078201 | 0.29306 | 0.014784 | -94.563 | -56.794 | -99.625 | 0.024988 | 0.19685 | -0.038035 | -122.1026 | 121.638 | 0.001785 | 121.6334 | 121.6331 | -0.00488 | -0.040818 | 0.17404 | -0.4794 | -0.094031 | 27.0602 | 21.9983 | 22.4777 | 0.077832 | -0.15705 | 121.744 | 121.7014 | 121.9163 | 121.643 | -0.10423 | 121.6482 | 121.8201 | 121.5852 | 64.8293 | -122.2216
2856.5 | 121.8658 | -121.6553 | 0.13733 | 1.4211e-13 | -0.014483 | -0.013718 | -0.045598 | -0.041284 | -0.012138 | 0.0067908 | -0.0070352 | 0.014507 | 0.039196 | 0.027465 | 0.06469 | 0.005626 | 0.019721 | 0.009904 | 0.11165 | 0.078201 | 0.29764 | 0.005627 | -93.4596 | -56.4277 | -98.5261 | 0.029566 | 0.19685 | 0.039801 | -122.1118 | 121.6609 | -0.025682 | 121.6609 | 121.6652 | 0.004277 | -0.059128 | 0.16031 | -0.45651 | -0.10776 | 28.1957 | 23.1292 | 23.5857 | 0.059522 | -0.097528 | 121.7669 | 121.7335 | 121.9529 | 121.675 | -0.1317 | 121.6848 | 121.8521 | 121.6951 | 65.2276 | -122.2491
2858.2188 | 121.9849 | -121.5912 | 0.16937 | 1.4211e-13 | -0.014483 | -0.013291 | -0.045598 | -0.041711 | -0.011711 | 0.0067908 | -0.010453 | 0.014721 | 0.035564 | 0.10011 | 0.066613 | 0.010204 | 0.0243 | 0.014482 | 0.1208 | 0.087359 | 0.30222 | 0.042258 | -91.7609 | -34.9398 | -4.0352 | 0.07993 | 0.25179 | 0.090166 | -122.0568 | 121.6334 | -0.048569 | 121.6014 | 121.6057 | -0.027776 | -0.082014 | 0.13284 | -0.46565 | -0.089443 | 29.8303 | 117.5559 | 118.0216 | 0.082421 | -0.079207 | 121.712 | 121.6785 | 121.8934 | 121.6155 | -0.12712 | 121.6711 | 121.843 | 121.6814 | 86.6514 | -122.2262
2860.0156 | 121.9574 | -121.6003 | 0.1831 | 1.4211e-13 | -0.014483 | -0.013505 | -0.045598 | -0.041284 | -0.012138 | -0.0084697 | -0.010667 | 0.014294 | 0.035991 | 0.10076 | 0.067681 | 0.014783 | 0.0243 | 0.005325 | 0.11622 | 0.091937 | 0.30222 | 0.019363 | -90.5292 | -34.6971 | -2.8539 | 0.084508 | 0.24721 | 0.094744 | -122.0752 | 121.6197 | -0.06688 | 121.6151 | 121.6057 | -0.014038 | -0.091168 | 0.11911 | -0.47482 | -0.098597 | 31.0711 | 118.7464 | 119.2212 | 0.06411 | -0.088361 | 121.7166 | 121.6923 | 121.9026 | 121.6246 | -0.16374 | 121.6848 | 121.8476 | 121.6951 | 86.9032 | -122.2583
2861.7969 | 121.8475 | -121.6507 | 0.20599 | 1.4211e-13 | -0.014483 | -0.013718 | -0.04517 | -0.041284 | -0.011711 | -0.0084697 | -0.010453 | 0.01408 | 0.035777 | 0.1014 | 0.068749 | 0.019361 | 0.019721 | 0.01906 | 0.1208 | 0.091937 | 0.29764 | 0.023942 | -89.3616 | -34.4361 | -2.19 | 0.084508 | 0.25637 | 0.1039 | -122.0752 | 121.6746 | -0.08519 | 121.6701 | 121.6698 | -0.004882 | -0.11406 | 0.091644 | -0.42446 | -0.12149 | 32.2891 | 119.4607 | 119.8851 | 0.050378 | -0.10209 | 121.7715 | 121.7426 | 121.9483 | 121.6704 | -0.18205 | 121.7352 | 121.9071 | 121.7546 | 87.2146 | -122.2812
2863.5938 | 121.9711 | -121.6049 | 0.17853 | 1.4211e-13 | -0.014483 | -0.013718 | -0.04517 | -0.041498 | -0.012138 | -0.0084697 | -0.010667 | 0.01408 | 0.035991 | 0.10118 | 0.069604 | 0.010204 | 0.028878 | 0.01906 | 0.1208 | 0.096516 | 0.30222 | 0.037679 | -88.4276 | -34.1843 | -1.7642 | 0.07993 | 0.25179 | 0.099323 | -122.0889 | 121.6426 | -0.057724 | 121.6151 | 121.624 | -0.018619 | -0.082012 | 0.12369 | -0.48397 | -0.098598 | 33.1773 | 119.8407 | 120.3247 | 0.073266 | -0.079205 | 121.7257 | 121.7014 | 121.9071 | 121.6338 | -0.14085 | 121.6848 | 121.8567 | 121.7042 | 87.4206 | -122.2674
2865.3125 | 121.9711 | -121.6324 | 0.19684 | 1.4211e-13 | -0.014696 | -0.013505 | -0.04517 | -0.041498 | -0.012138 | 0.0067908 | -0.010667 | 0.01408 | 0.035777 | 0.10161 | 0.070031 | 0.014783 | 0.028878 | 0.023639 | 0.1208 | 0.087359 | 0.30222 | 0.028521 | -87.8415 | -34.079 | -1.3109 | 0.089087 | 0.24264 | 0.1039 | -122.0935 | 121.6609 | -0.076034 | 121.6472 | 121.656 | -0.004882 | -0.10948 | 0.10538 | -0.46109 | -0.10775 | 33.7909 | 120.3215 | 120.7826 | 0.045799 | -0.092937 | 121.7532 | 121.7197 | 121.9346 | 121.6613 | -0.16832 | 121.7215 | 121.875 | 121.7363 | 87.5534 | -122.2903
2867.0938 | 121.9757 | -121.6324 | 0.1831 | 1.4211e-13 | -0.014483 | -0.013505 | -0.045384 | -0.041498 | -0.012138 | -0.0084697 | -0.010667 | 0.014294 | 0.035777 | 0.10161 | 0.070672 | 0.010204 | 0.028878 | 0.023639 | 0.12538 | 0.087359 | 0.30222 | 0.023942 | -86.9624 | -33.818 | -0.95836 | 0.07993 | 0.25637 | 0.099323 | -122.1072 | 121.6563 | -0.057723 | 121.6426 | 121.656 | -0.000303 | -0.095746 | 0.11911 | -0.47482 | -0.10317 | 34.67 | 120.674 | 121.1489 | 0.073267 | -0.083782 | 121.7578 | 121.7197 | 121.9346 | 121.6613 | -0.15916 | 121.7123 | 121.8888 | 121.7317 | 87.8144 | -122.2903
2868.8906 | 122.0398 | -121.6553 | 0.1831 | 1.4211e-13 | -0.014483 | -0.013291 | -0.045384 | -0.041498 | -0.012352 | 0.0067908 | -0.010026 | 0.013866 | 0.035777 | 0.10182 | 0.071741 | 0.019361 | 0.0243 | 0.014482 | 0.1208 | 0.087359 | 0.30222 | 0.014784 | -86.0329 | -33.8317 | -0.71111 | 0.089087 | 0.25637 | 0.1039 | -122.1118 | 121.6701 | -0.062301 | 121.6746 | 121.6698 | -0.000302 | -0.095746 | 0.11911 | -0.45651 | -0.094018 | 35.6224 | 120.9442 | 121.4007 | 0.073267 | -0.079204 | 121.7761 | 121.7426 | 121.9575 | 121.6796 | -0.16832 | 121.7444 | 121.9116 | 121.7592 | 87.8235 | -122.2949
2870.7031 | 121.994 | -121.6736 | 0.17853 | 1.4211e-13 | -0.014483 | -0.013291 | -0.04517 | -0.041498 | -0.012138 | 0.014421 | -0.011094 | 0.01408 | 0.035777 | 0.10182 | 0.073663 | 0.014783 | 0.033457 | 0.023639 | 0.12538 | 0.091937 | 0.29764 | 0.0331 | -85.1721 | -10.201 | -0.51422 | 0.084508 | 0.25637 | 0.099323 | -122.1209 | 121.7067 | -0.053146 | 121.6884 | 121.6972 | -0.009461 | -0.086591 | 0.11911 | -0.44736 | -0.09402 | 36.5015 | 121.1594 | 121.6067 | 0.077844 | -0.079205 | 121.799 | 121.7655 | 121.9712 | 121.707 | -0.14543 | 121.7581 | 121.93 | 121.7729 | 111.4726 | -122.2995
2872.5 | 121.9208 | -121.6644 | 0.21057 | 1.4211e-13 | -0.014483 | -0.013718 | -0.04517 | -0.041284 | -0.012138 | 0.0067908 | -0.011308 | 0.014294 | 0.035564 | 0.10204 | 0.074304 | 0.014783 | 0.0243 | 0.009904 | 0.11622 | 0.091937 | 0.29764 | 0.042258 | -84.2976 | -4.4044 | -0.37228 | 0.084508 | 0.25179 | 0.10848 | -122.1255 | 121.7067 | -0.094346 | 121.6792 | 121.6743 | -0.032354 | -0.11863 | 0.087067 | -0.4611 | -0.12606 | 37.3668 | 121.2921 | 121.7532 | 0.041223 | -0.10209 | 121.7807 | 121.7564 | 121.9621 | 121.6887 | -0.16831 | 121.7489 | 121.9162 | 121.7729 | 117.2601 | -122.3361
2874.2188 | 121.9482 | -121.7331 | 0.20599 | 1.4211e-13 | -0.014269 | -0.013505 | -0.045598 | -0.041498 | -0.011711 | -0.00083919 | -0.011308 | 0.013866 | 0.03535 | 0.10204 | 0.074945 | 0.014783 | 0.038035 | 0.014482 | 0.12538 | 0.091937 | 0.29764 | 0.051416 | -83.9313 | -3.0262 | -0.28071 | 0.093665 | 0.25179 | 0.10848 | -122.1393 | 121.7845 | -0.080612 | 121.7479 | 121.7476 | -0.036934 | -0.11406 | 0.091644 | -0.40617 | -0.11233 | 37.8018 | 121.4524 | 121.8586 | 0.0458 | -0.097514 | 121.8585 | 121.825 | 122.0307 | 121.7711 | -0.15458 | 121.8268 | 121.9849 | 121.8416 | 118.7069 | -122.3453
2876.0312 | 121.962 | -121.6965 | 0.20599 | 1.4211e-13 | -0.014269 | -0.013291 | -0.04517 | -0.04107 | -0.011924 | -0.00083919 | -0.011094 | 0.01408 | 0.03535 | 0.10182 | 0.075159 | 0.014783 | 0.019721 | 0.009904 | 0.11622 | 0.091937 | 0.30222 | 0.0331 | -84.1511 | -2.5546 | -0.2395 | 0.098244 | 0.26095 | 0.099323 | -122.153 | 121.7296 | -0.089769 | 121.7113 | 121.7064 | -0.023196 | -0.11406 | 0.096223 | -0.45652 | -0.10775 | 37.5454 | 121.457 | 121.9135 | 0.054957 | -0.10667 | 121.8127 | 121.7884 | 121.9987 | 121.7162 | -0.17289 | 121.7947 | 121.9574 | 121.7958 | 119.1419 | -122.359
2877.8281 | 121.9849 | -121.7331 | 0.19684 | 1.4211e-13 | -0.014055 | -0.013505 | -0.04517 | -0.041284 | -0.011924 | 0.0067908 | -0.011094 | 0.013866 | 0.035777 | 0.10161 | 0.074304 | 0.014783 | 0.028878 | 0.009904 | 0.12538 | 0.091937 | 0.30222 | 0.051416 | -84.9111 | -2.5729 | -0.19829 | 0.098244 | 0.25637 | 0.11306 | -122.1576 | 121.7845 | -0.071456 | 121.7479 | 121.743 | -0.041512 | -0.1049 | 0.10538 | -0.42448 | -0.098594 | 36.822 | 121.5348 | 121.9593 | 0.059534 | -0.083779 | 121.8585 | 121.825 | 122.0353 | 121.762 | -0.14542 | 121.8313 | 121.9895 | 121.8462 | 119.1602 | -122.3544
2879.6406 | 122.1085 | -121.6873 | 0.17395 | 1.4211e-13 | -0.014269 | -0.013718 | -0.04517 | -0.041498 | -0.011924 | -0.00083919 | -0.010881 | 0.013866 | 0.03535 | 0.10182 | 0.075159 | 0.014783 | 0.033457 | 0.009904 | 0.1208 | 0.08278 | 0.30222 | 0.051416 | -85.0027 | -1.8906 | -0.17998 | 0.089087 | 0.25637 | 0.099323 | -122.1667 | 121.7387 | -0.053146 | 121.7021 | 121.6972 | -0.041512 | -0.09117 | 0.12827 | -0.47942 | -0.084863 | 36.6846 | 121.5073 | 121.9868 | 0.082422 | -0.074627 | 121.8081 | 121.7701 | 121.9895 | 121.7208 | -0.12253 | 121.7764 | 121.9437 | 121.7866 | 119.7967 | -122.3407
2881.3594 | 122.0352 | -121.7056 | 0.20599 | 1.4211e-13 | -0.014696 | -0.013505 | -0.045384 | -0.041498 | -0.011924 | -0.0084697 | -0.011308 | 0.013866 | 0.035777 | 0.10182 | 0.075373 | 0.019361 | 0.028878 | 0.01906 | 0.1208 | 0.096516 | 0.3068 | 0.028521 | -84.8058 | -1.8311 | -0.1754 | 0.093665 | 0.26095 | 0.10848 | -122.1713 | 121.7341 | -0.08519 | 121.725 | 121.7247 | -0.009461 | -0.10948 | 0.1008 | -0.46568 | -0.11233 | 36.8998 | 121.5302 | 121.9959 | 0.054957 | -0.097514 | 121.8264 | 121.8021 | 122.0124 | 121.7345 | -0.17747 | 121.7993 | 121.9666 | 121.8141 | 119.8745 | -122.3773
2883.1406 | 122.0306 | -121.7285 | 0.17853 | 1.4211e-13 | -0.014483 | -0.013291 | -0.045384 | -0.041711 | -0.012138 | -0.0084697 | -0.011094 | 0.014294 | 0.035564 | 0.1014 | 0.075586 | 0.023939 | 0.019721 | 0.01906 | 0.1208 | 0.091937 | 0.3068 | 0.046837 | -84.7005 | -0.73223 | -0.17082 | 0.089087 | 0.25179 | 0.099323 | -122.1759 | 121.7754 | -0.057724 | 121.7525 | 121.7476 | -0.027777 | -0.086591 | 0.12827 | -0.44737 | -0.089441 | 37.028 | 121.5577 | 122.0051 | 0.073266 | -0.079205 | 121.8493 | 121.8205 | 122.0353 | 121.7482 | -0.13169 | 121.8176 | 121.9803 | 121.8278 | 120.9963 | -122.3544
2884.875 | 122.0306 | -121.7331 | 0.20142 | 1.4211e-13 | -0.014483 | -0.013718 | -0.04517 | -0.041498 | -0.011924 | -0.0084697 | -0.010881 | 0.013866 | 0.03535 | 0.10118 | 0.076014 | 0.010204 | 0.0243 | 0.009904 | 0.11165 | 0.087359 | 0.31137 | 0.037679 | -84.5219 | -0.42088 | -0.16624 | 0.093665 | 0.25179 | 0.10848 | -122.185 | 121.7708 | -0.089769 | 121.7433 | 121.743 | -0.027775 | -0.11406 | 0.10996 | -0.45195 | -0.10775 | 37.2112 | 121.5669 | 122.0188 | 0.050378 | -0.092936 | 121.8447 | 121.8205 | 122.0445 | 121.7574 | -0.16374 | 121.8268 | 121.9849 | 121.8416 | 121.3122 | -122.3865
2886.6719 | 121.9711 | -121.7789 | 0.21057 | 1.4211e-13 | -0.014483 | -0.013505 | -0.045598 | -0.041498 | -0.012138 | 0.0067908 | -0.011094 | 0.01408 | 0.03535 | 0.10118 | 0.076868 | 0.014783 | 0.028878 | 0.014482 | 0.12538 | 0.091937 | 0.30222 | 0.019363 | -84.2564 | -0.24231 | -0.16166 | 0.093665 | 0.25179 | 0.10848 | -122.1942 | 121.7982 | -0.085189 | 121.7937 | 121.7934 | -0.004881 | -0.11863 | 0.091646 | -0.41534 | -0.11691 | 37.5225 | 121.6172 | 122.0325 | 0.041223 | -0.10209 | 121.9043 | 121.8708 | 122.0811 | 121.8077 | -0.19121 | 121.8725 | 122.0307 | 121.8873 | 121.5366 | -122.4048
2888.4688 | 121.994 | -121.7468 | 0.20599 | 1.4211e-13 | -0.014483 | -0.013505 | -0.044957 | -0.041711 | -0.011924 | -0.0084697 | -0.01024 | 0.013653 | 0.035564 | 0.10097 | 0.077295 | 0.010204 | 0.028878 | 0.014482 | 0.11622 | 0.087359 | 0.30222 | 0.0331 | -84.0778 | -0.16448 | -0.14793 | 0.089087 | 0.24721 | 0.099323 | -122.2034 | 121.7799 | -0.089769 | 121.757 | 121.7613 | -0.018618 | -0.11864 | 0.096223 | -0.45654 | -0.11691 | 37.669 | 121.5989 | 122.0554 | 0.041221 | -0.10667 | 121.8631 | 121.8342 | 122.049 | 121.7757 | -0.17289 | 121.8359 | 121.994 | 121.8461 | 121.5824 | -122.4094
2890.2656 | 122.0032 | -121.7834 | 0.21515 | 1.4211e-13 | -0.014483 | -0.013718 | -0.045811 | -0.041498 | -0.011924 | -0.0084697 | -0.010881 | 0.013439 | 0.035777 | 0.10118 | 0.077723 | 0.010204 | 0.0243 | 0.014482 | 0.1208 | 0.087359 | 0.29764 | 0.046837 | -83.0934 | -0.10953 | -0.14793 | 0.098244 | 0.24721 | 0.10848 | -122.2034 | 121.8303 | -0.094345 | 121.7937 | 121.7979 | -0.032355 | -0.12779 | 0.082489 | -0.41992 | -0.11691 | 38.6901 | 121.6355 | 122.0554 | 0.032066 | -0.10667 | 121.9043 | 121.8708 | 122.0811 | 121.8077 | -0.16831 | 121.8817 | 122.0307 | 121.8919 | 121.6739 | -122.4185
2891.9844 | 122.1268 | -121.7285 | 0.19226 | 1.4211e-13 | -0.014483 | -0.013718 | -0.04517 | -0.041284 | -0.011711 | -0.00083919 | -0.010667 | 0.013653 | 0.03535 | 0.10118 | 0.078364 | 0.005626 | 0.028878 | 0.014482 | 0.1208 | 0.087359 | 0.3068 | 0.046837 | -82.5531 | -0.10037 | -0.14793 | 0.093665 | 0.26553 | 0.1039 | -122.2171 | 121.7754 | -0.071457 | 121.7341 | 121.743 | -0.032355 | -0.1049 | 0.11454 | -0.48858 | -0.098596 | 39.1754 | 121.5806 | 122.0692 | 0.073269 | -0.08836 | 121.8493 | 121.8159 | 122.0353 | 121.7574 | -0.14542 | 121.8222 | 121.994 | 121.8324 | 121.6281 | -122.4094
2893.7812 | 122.0947 | -121.7606 | 0.19226 | 1.4211e-13 | -0.014269 | -0.013718 | -0.04517 | -0.041498 | -0.011924 | -0.0161 | -0.010667 | 0.013439 | 0.035564 | 0.10118 | 0.079218 | 0.014783 | 0.028878 | 0.01906 | 0.12538 | 0.091937 | 0.29764 | 0.046837 | -82.3608 | -0.0729 | -0.13877 | 0.093665 | 0.25179 | 0.1039 | -122.2217 | 121.8074 | -0.066879 | 121.7753 | 121.7796 | -0.027777 | -0.10032 | 0.10538 | -0.46112 | -0.098596 | 39.3998 | 121.6218 | 122.0829 | 0.059533 | -0.08836 | 121.8859 | 121.8525 | 122.0582 | 121.7894 | -0.14542 | 121.8542 | 122.0124 | 121.8645 | 121.6877 | -122.4139
2895.5781 | 122.0718 | -121.7514 | 0.19226 | 1.4211e-13 | -0.014269 | -0.013505 | -0.04517 | -0.041498 | -0.011924 | -0.0084697 | -0.010667 | 0.013653 | 0.03535 | 0.10076 | 0.079646 | 0.019361 | 0.0243 | 0.009904 | 0.1208 | 0.091937 | 0.30222 | 0.0331 | -81.6923 | -0.040849 | -0.13877 | 0.093665 | 0.26095 | 0.11306 | -122.2263 | 121.7845 | -0.071457 | 121.7708 | 121.7613 | -0.023196 | -0.10032 | 0.10996 | -0.47485 | -0.098596 | 40.0591 | 121.6126 | 122.0875 | 0.06869 | -0.079202 | 121.8722 | 121.8433 | 122.0536 | 121.7757 | -0.15916 | 121.8451 | 122.0124 | 121.8645 | 121.7106 | -122.4185
2897.3594 | 122.0215 | -121.8018 | 0.21515 | 1.4211e-13 | -0.014696 | -0.013505 | -0.045384 | -0.041498 | -0.011711 | 0.014421 | -0.010667 | 0.01408 | 0.03535 | 0.10076 | 0.080928 | 0.010204 | 0.019721 | 0.01906 | 0.1208 | 0.091937 | 0.29764 | 0.0331 | -81.0696 | -0.031692 | -0.13877 | 0.10282 | 0.26553 | 0.11306 | -122.2263 | 121.8349 | -0.094345 | 121.812 | 121.8208 | -0.01404 | -0.12321 | 0.082489 | -0.4245 | -0.11233 | 40.7322 | 121.663 | 122.0875 | 0.050381 | -0.10209 | 121.9226 | 121.8937 | 122.0994 | 121.8215 | -0.18205 | 121.9046 | 122.0673 | 121.9148 | 121.7701 | -122.4414
2899.0781 | 122.0169 | -121.8063 | 0.2243 | 1.4211e-13 | -0.014269 | -0.013077 | -0.045384 | -0.041498 | -0.012138 | -0.00083919 | -0.01024 | 0.01408 | 0.035564 | 0.10097 | 0.081569 | 0.019361 | 0.0243 | 0.014482 | 0.1208 | 0.091937 | 0.30222 | 0.0331 | -80.4469 | -0.027113 | -0.14335 | 0.10282 | 0.26553 | 0.11306 | -122.24 | 121.8394 | -0.1035 | 121.8257 | 121.8208 | -0.018618 | -0.13237 | 0.077913 | -0.43366 | -0.12148 | 41.3595 | 121.663 | 122.0966 | 0.041226 | -0.11124 | 121.9271 | 121.8983 | 122.1086 | 121.8306 | -0.1912 | 121.9092 | 122.0719 | 121.9194 | 121.7792 | -122.4643
2900.8906 | 122.0993 | -121.8246 | 0.17853 | 1.4211e-13 | -0.014483 | -0.013505 | -0.045384 | -0.041284 | -0.012138 | -0.00083919 | 0.035265 | 0.013866 | 0.035136 | 0.10097 | 0.082637 | 0.010204 | 0.019721 | 0.009904 | 0.1208 | 0.078201 | 0.30222 | 0.019363 | -79.6868 | 0.091933 | -0.12045 | 0.061616 | 0.24264 | 0.081008 | -122.272 | 121.844 | -0.057724 | 121.8349 | 121.8346 | -0.009459 | -0.10033 | 0.12369 | -0.4474 | -0.11691 | 42.1378 | 121.7042 | 122.1516 | 0.064109 | -0.09752 | 121.9455 | 121.9028 | 122.1269 | 121.8444 | -0.15917 | 121.8863 | 122.0673 | 121.9057 | 121.9166 | -122.4506
2902.6875 | 122.0673 | -121.8521 | 0.17395 | 1.4211e-13 | -0.014696 | -0.013718 | -0.045384 | -0.041711 | -0.011497 | -0.00083919 | 0.063252 | 0.013866 | 0.035136 | 0.10054 | 0.083919 | 0.005626 | 0.0243 | 0.009904 | 0.1208 | 0.08278 | 0.29764 | 0.023942 | -78.739 | 0.091933 | -0.1113 | 0.04788 | 0.21059 | 0.053537 | -122.2904 | 121.8761 | -0.053146 | 121.8577 | 121.862 | -0.014038 | -0.09117 | 0.12369 | -0.43825 | -0.12607 | 43.1131 | 121.7408 | 122.1791 | 0.036636 | -0.12041 | 121.9729 | 121.9349 | 122.1498 | 121.8764 | -0.15001 | 121.9 | 122.0627 | 121.9056 | 121.944 | -122.4643
2904.4844 | 122.0627 | -121.8842 | 0.16479 | 1.4211e-13 | -0.01491 | -0.013505 | -0.045384 | -0.041711 | -0.011924 | -0.00083919 | 0.06667 | 0.013439 | 0.035136 | 0.10076 | 0.085201 | 0.005626 | 0.028878 | 0.009904 | 0.1208 | 0.08278 | 0.29764 | 0.028521 | -77.5943 | 0.091933 | -0.1113 | 0.052459 | 0.20601 | 0.067272 | -122.2995 | 121.9127 | -0.043991 | 121.8898 | 121.8941 | -0.018617 | -0.082015 | 0.13284 | -0.41536 | -0.11234 | 44.2898 | 121.7729 | 122.1882 | 0.041213 | -0.097523 | 122.005 | 121.9669 | 122.1818 | 121.913 | -0.13627 | 121.9366 | 122.0902 | 121.9514 | 121.9761 | -122.4643
2906.2188 | 122.1863 | -121.8567 | 0.14191 | 1.4211e-13 | -0.014483 | -0.013505 | -0.045384 | -0.041498 | -0.011924 | -0.0084697 | 0.076711 | 0.013653 | 0.03535 | 0.10054 | 0.08691 | 0.014783 | 0.028878 | 0.01906 | 0.1208 | 0.091937 | 0.31137 | 0.019363 | -76.6374 | 0.091933 | -0.10214 | 0.038723 | 0.20601 | 0.053537 | -122.3133 | 121.8761 | -0.021103 | 121.8715 | 121.8757 | -0.000303 | -0.04997 | 0.16947 | -0.45657 | -0.10318 | 45.2193 | 121.7546 | 122.2111 | 0.064101 | -0.08837 | 121.9775 | 121.9486 | 122.1681 | 121.8856 | -0.12254 | 121.8954 | 122.0627 | 121.9102 | 121.9486 | -122.4552
2908.0156 | 122.0856 | -121.8887 | 0.15564 | 1.4211e-13 | -0.01491 | -0.013505 | -0.044957 | -0.041498 | -0.011924 | -0.0084697 | 0.081625 | 0.013866 | 0.035564 | 0.10054 | 0.088619 | 0.010204 | 0.019721 | 0.014482 | 0.11165 | 0.078201 | 0.29764 | 0.019363 | -74.8654 | 0.078197 | -0.097559 | 0.038723 | 0.20143 | -0.028878 | -122.3224 | 121.9081 | -0.043993 | 121.8989 | 121.9032 | -0.004881 | -0.077439 | 0.142 | -0.43368 | -0.11692 | 47.0233 | 121.7912 | 122.2249 | 0.045789 | -0.18452 | 122.0004 | 121.9669 | 122.1864 | 121.9085 | -0.13628 | 121.9275 | 122.0902 | 121.8599 | 121.9669 | -122.4781
2909.8125 | 122.2 | -121.8887 | 0.14191 | 1.4211e-13 | -0.014696 | -0.013718 | -0.04517 | -0.041498 | -0.011924 | 0.0067908 | 0.085684 | 0.013653 | 0.035564 | 0.10033 | 0.090756 | 0.010204 | 0.0243 | 0.009904 | 0.1208 | 0.073622 | 0.29764 | 0.019363 | -73.3545 | 0.091933 | -0.10214 | 0.029566 | 0.20143 | 0.021486 | -122.3316 | 121.9081 | -0.021103 | 121.8989 | 121.8986 | -0.009459 | -0.068285 | 0.15573 | -0.44284 | -0.11234 | 48.5343 | 121.7866 | 122.2294 | 0.059522 | -0.12042 | 122.0095 | 121.9624 | 122.1864 | 121.913 | -0.12254 | 121.9183 | 122.0902 | 121.9102 | 121.9807 | -122.4735
2911.5312 | 122.081 | -121.8979 | 0.17853 | 1.4211e-13 | -0.014483 | -0.013505 | -0.04517 | -0.041498 | -0.011924 | -0.00083919 | 0.12905 | 0.010448 | 0.034923 | 0.10011 | 0.13285 | 0.005626 | 0.0243 | 0.005325 | 0.11165 | 0.087359 | 0.30222 | 0.019363 | -1.8854 | 0.087354 | -0.1113 | 0.034145 | 0.20143 | -0.038035 | -122.3224 | 121.9173 | -0.066881 | 121.9035 | 121.9032 | -0.014038 | -0.091169 | 0.12369 | -0.42453 | -0.14438 | 120.0125 | 121.7866 | 122.2111 | 0.022901 | -0.21656 | 122.0095 | 121.9852 | 122.2001 | 121.9222 | -0.15917 | 121.932 | 122.0993 | 121.8599 | 121.9852 | -122.5009
2913.3281 | 122.1954 | -121.8567 | 0.13733 | 1.4211e-13 | -0.014483 | -0.013291 | -0.045598 | -0.04107 | -0.011924 | -0.0084697 | 0.12991 | 0.010234 | 0.034923 | 0.10033 | 0.13455 | 0.010204 | 0.0243 | 0.005325 | 0.11622 | 0.08278 | 0.3068 | 0.023942 | -1.4504 | 0.078197 | -0.10214 | 0.043302 | 0.19685 | -0.042614 | -122.327 | 121.8806 | -0.021104 | 121.8669 | 121.862 | -0.018617 | -0.054549 | 0.16947 | -0.4703 | -0.094027 | 120.4063 | 121.7546 | 122.2249 | 0.059522 | -0.17994 | 121.9729 | 121.9395 | 122.1635 | 121.881 | -0.11339 | 121.9 | 122.0535 | 121.8141 | 121.9349 | -122.4643
2915.125 | 122.0718 | -121.9025 | 0.18768 | 1.4211e-13 | -0.014483 | -0.013505 | -0.045384 | -0.041284 | -0.011497 | -0.00083919 | 0.13204 | 0.010021 | 0.035136 | 0.10011 | 0.13562 | 0.001048 | 0.019721 | 0.009904 | 0.1208 | 0.08278 | 0.29306 | 0.019363 | -1.4504 | 0.06904 | -0.10214 | 0.034145 | 0.20601 | -0.079243 | -122.327 | 121.9218 | -0.066879 | 121.9035 | 121.9124 | -0.009459 | -0.1049 | 0.10538 | -0.42453 | -0.15354 | 120.4521 | 121.8003 | 122.2249 | 0.018325 | -0.26693 | 122.0233 | 121.9852 | 122.1955 | 121.9222 | -0.16832 | 121.9366 | 122.1085 | 121.8232 | 121.9715 | -122.5147
2916.9219 | 122.1313 | -121.9299 | 0.13733 | 1.4211e-13 | -0.014696 | -0.013291 | -0.045384 | -0.041498 | -0.012138 | -0.00083919 | 0.013474 | 0.0070294 | -0.03494 | 0.010585 | -0.019703 | -0.003531 | 0.015142 | 0.005325 | 0.11165 | 0.087359 | 0.29306 | 0.010206 | 0.014784 | 0.091933 | -0.079245 | 0.020409 | 0.18769 | -0.11587 | -0.39767 | 121.9401 | -0.025682 | 121.9264 | 121.9353 | -0.004881 | -0.04997 | 0.15573 | 121.5323 | -0.11692 | 121.9447 | 121.8507 | 0.31842 | 0.050364 | -0.2532 | 122.0416 | 122.0173 | 122.223 | 121.9451 | -0.12712 | 121.9503 | 122.1176 | 121.8141 | 122.0219 | -0.535
2918.7188 | 122.1909 | -121.9482 | 0.10071 | 1.4211e-13 | -0.014696 | -0.013718 | -0.045598 | -0.041498 | -0.011924 | 0.0067908 | 0.01561 | 0.0070294 | -0.035154 | 0.010585 | -0.019917 | 0.001048 | 0.015142 | 0.005325 | 0.11165 | 0.08278 | 0.29306 | 0.014784 | 0.019362 | 0.091933 | -0.079245 | 0.020409 | 0.18311 | -0.092979 | -0.32441 | 121.963 | 0.010939 | 121.9493 | 121.9536 | -0.009459 | -0.017928 | 0.19235 | 121.6238 | -0.080299 | 121.9676 | 121.869 | 0.24516 | 0.082407 | -0.19369 | 122.0599 | 122.031 | 122.2413 | 121.9634 | -0.085924 | 121.9687 | 122.1314 | 121.8553 | 122.0402 | -0.42512
2920.4531 | 122.168 | -121.9528 | 0.13275 | 1.4211e-13 | -0.014696 | -0.013505 | -0.045598 | -0.041284 | -0.011284 | -0.00083919 | 0.01732 | 0.007243 | -0.035154 | 0.010372 | -0.019703 | -0.003531 | 0.010564 | -0.003831 | 0.11622 | 0.078201 | 0.29306 | 0.023942 | 0.023941 | 0.082776 | -0.074666 | 0.024988 | 0.18311 | -0.083821 | -0.31525 | 121.9768 | -0.016526 | 121.9493 | 121.949 | -0.027773 | -0.05455 | 0.16031 | 121.6376 | -0.10776 | 121.9768 | 121.8782 | 0.24058 | 0.050364 | -0.21657 | 122.069 | 122.031 | 122.2459 | 121.9634 | -0.10881 | 121.9778 | 122.1359 | 121.869 | 122.0356 | -0.448
2922.2344 | 122.2366 | -121.962 | 0.09613 | 1.4211e-13 | -0.014696 | -0.013291 | -0.045598 | -0.041498 | -0.011924 | -0.00083919 | 0.018815 | 0.0068158 | -0.035154 | 0.010585 | -0.019489 | 0.005626 | 0.019721 | 0.005325 | 0.11165 | 0.087359 | 0.29764 | 0.010206 | 0.019362 | 0.087354 | -0.074666 | 0.024988 | 0.18311 | -0.11129 | -0.30609 | 121.9722 | 0.015517 | 121.9676 | 121.9673 | -0.004881 | -0.008771 | 0.20151 | 121.6559 | -0.071142 | 121.9813 | 121.8873 | 0.23143 | 0.086985 | -0.20742 | 122.0736 | 122.0493 | 122.2596 | 121.9817 | -0.085924 | 121.987 | 122.1451 | 121.8507 | 122.0493 | -0.40222
2924.0469 | 122.2 | -121.9803 | 0.14191 | 1.4211e-13 | -0.014696 | -0.013718 | -0.04517 | -0.041711 | -0.011924 | 0.0067908 | 0.020311 | 0.0070294 | -0.035367 | 0.010585 | -0.019489 | 0.010204 | 0.019721 | 0.005325 | 0.11165 | 0.08278 | 0.28848 | 0.010206 | 0.019362 | 0.091933 | -0.070087 | 0.020409 | 0.18311 | -0.083821 | -0.30609 | 121.9905 | -0.03026 | 121.9905 | 121.9856 | -0.004881 | -0.059127 | 0.14657 | 121.6742 | -0.1215 | 121.9996 | 121.9102 | 0.236 | 0.041208 | -0.22573 | 122.0919 | 122.0631 | 122.2688 | 122 | -0.1317 | 122.0007 | 122.1634 | 121.8965 | 122.0722 | -0.448
2925.8438 | 122.1451 | -122.0078 | 0.12817 | 1.4211e-13 | -0.014269 | -0.013932 | -0.045384 | -0.041498 | -0.011924 | -0.0161 | 0.02202 | 0.0074566 | -0.035154 | 0.010585 | -0.019489 | 0.005626 | 0.015142 | 0.005325 | 0.10707 | 0.078201 | 0.30222 | 0.019363 | 0.023941 | 0.087354 | -0.06093 | 0.024988 | 0.18769 | -0.0884 | -0.30609 | 122.0271 | -0.021106 | 122.0134 | 122.0131 | -0.014038 | -0.049973 | 0.17404 | 121.7017 | -0.10319 | 122.0317 | 121.9468 | 0.24516 | 0.059519 | -0.21657 | 122.1148 | 122.086 | 122.31 | 122.0229 | -0.10881 | 122.0327 | 122.1954 | 121.9194 | 122.0951 | -0.43427
2927.6406 | 122.2183 | -122.0078 | 0.12817 | 1.4211e-13 | -0.014696 | -0.013718 | -0.045384 | -0.041498 | -0.011924 | -0.0084697 | 0.02437 | 0.006602 | -0.035154 | 0.010799 | -0.019489 | 0.001048 | 0.0243 | 0.000747 | 0.10707 | 0.087359 | 0.29764 | 0.019363 | 0.023941 | 0.082776 | -0.070087 | 0.020409 | 0.17854 | -0.11587 | -0.30151 | 122.0271 | -0.021106 | 122.0088 | 122.0085 | -0.018616 | -0.040815 | 0.16946 | 121.7062 | -0.10777 | 122.0317 | 121.9377 | 0.23143 | 0.050362 | -0.24405 | 122.1148 | 122.0951 | 122.3054 | 122.0321 | -0.10881 | 122.0282 | 122.1863 | 121.8919 | 122.0905 | -0.42969
2929.3594 | 122.3007 | -121.9757 | 0.091553 | 1.4211e-13 | -0.014483 | -0.013718 | -0.045384 | -0.041284 | -0.011924 | 0.0067908 | 0.026079 | 0.0070294 | -0.03494 | 0.010585 | -0.019703 | 0.005626 | 0.0243 | 0.005325 | 0.10707 | 0.08278 | 0.30222 | 0.014784 | 0.023941 | 0.091933 | -0.065509 | 0.020409 | 0.17854 | -0.092979 | -0.30151 | 121.9905 | 0.015515 | 121.9813 | 121.981 | -0.009459 | -0.008773 | 0.21066 | 121.6742 | -0.071144 | 121.9996 | 121.9102 | 0.236 | 0.086983 | -0.18453 | 122.0828 | 122.0585 | 122.2779 | 122 | -0.076769 | 121.9961 | 122.1542 | 121.8827 | 122.0676 | -0.39307
2931.1562 | 122.3145 | -121.9803 | 0.10986 | 1.4211e-13 | -0.014696 | -0.013932 | -0.04517 | -0.041498 | -0.011711 | -0.0084697 | 0.02907 | 0.0070294 | -0.03494 | 0.010585 | -0.019703 | 0.005626 | 0.0243 | 0.000747 | 0.1208 | 0.078201 | 0.29306 | 0.019363 | 0.023941 | 0.087354 | -0.065509 | 0.029566 | 0.18311 | -0.11129 | -0.30151 | 121.9996 | 0.010941 | 121.9859 | 121.981 | -0.018616 | -0.031662 | 0.1832 | 121.6788 | -0.080297 | 122.0042 | 121.9148 | 0.236 | 0.073252 | -0.22116 | 122.1011 | 122.0585 | 122.2733 | 122.0046 | -0.0905 | 122.0099 | 122.1634 | 121.869 | 122.0676 | -0.41138
2932.9531 | 122.1725 | -122.0306 | 0.15106 | 1.4211e-13 | -0.014696 | -0.013932 | -0.045598 | -0.041925 | -0.011924 | -0.0084697 | 0.032702 | 0.0070294 | -0.03494 | 0.010799 | -0.02013 | -0.003531 | 0.015142 | 0.009904 | 0.11165 | 0.078201 | 0.29306 | 0.019363 | 0.019362 | 0.091933 | -0.065509 | 0.029566 | 0.18769 | -0.051771 | -0.29693 | 122.05 | -0.039415 | 122.0271 | 122.0405 | -0.009459 | -0.072861 | 0.142 | 121.7337 | -0.1215 | 122.05 | 121.9651 | 0.23142 | 0.036631 | -0.20283 | 122.1423 | 122.1088 | 122.3237 | 122.0458 | -0.1317 | 122.0602 | 122.2183 | 121.9789 | 122.1226 | -0.448
2934.7344 | 122.2733 | -122.0032 | 0.13733 | 1.4211e-13 | -0.014696 | -0.013505 | -0.04517 | -0.041498 | -0.011924 | -0.0161 | 0.036761 | 0.007243 | -0.03494 | 0.011013 | -0.019703 | 0.010204 | 0.028878 | 0.009904 | 0.11165 | 0.08278 | 0.29306 | 0.019363 | 0.033099 | 0.091933 | -0.06093 | 0.034145 | 0.19685 | -0.038035 | -0.29236 | 122.0225 | -0.025682 | 122.0134 | 122.0131 | -0.009459 | -0.054549 | 0.15573 | 121.7108 | -0.10318 | 122.0363 | 121.9422 | 0.23143 | 0.059522 | -0.17536 | 122.1148 | 122.086 | 122.2962 | 122.0321 | -0.11797 | 122.0373 | 122.2 | 121.9651 | 122.0951 | -0.42968
2936.4688 | 122.2916 | -121.962 | 0.12817 | 1.4211e-13 | -0.014696 | -0.013718 | -0.045384 | -0.041711 | -0.011924 | -0.0084697 | 0.043383 | 0.0070294 | -0.035154 | 0.010585 | -0.019703 | 0.010204 | 0.015142 | 0.009904 | 0.11622 | 0.091937 | 0.29306 | 0.019363 | 0.02852 | 0.091933 | -0.065509 | 0.029566 | 0.19685 | 0.062694 | -0.29236 | 121.9813 | -0.011949 | 121.9722 | 121.9719 | -0.009459 | -0.036237 | 0.16489 | 121.6696 | -0.098608 | 121.9905 | 121.8965 | 0.22685 | 0.068677 | -0.06548 | 122.0782 | 122.0539 | 122.255 | 121.9771 | -0.10881 | 121.9915 | 122.1588 | 122.0247 | 122.0539 | -0.42053
2938.25 | 122.2504 | -121.9711 | 0.16022 | 1.4211e-13 | -0.014696 | -0.013718 | -0.045384 | -0.041284 | -0.011924 | -0.0084697 | 0.066029 | 0.0070294 | -0.035367 | 0.010585 | -0.019489 | 0.010204 | 0.019721 | 0.009904 | 0.1208 | 0.087359 | 0.29764 | 0.014784 | 0.042256 | 0.10109 | -0.056351 | 0.04788 | 0.21059 | 0.053537 | -0.27862 | 121.9859 | -0.039413 | 121.9813 | 121.981 | -0.00488 | -0.072858 | 0.13742 | 121.6925 | -0.11234 | 122.0134 | 121.9148 | 0.22227 | 0.050369 | -0.10668 | 122.0919 | 122.0585 | 122.2688 | 121.9909 | -0.14543 | 122.019 | 122.1817 | 122.0247 | 122.0722 | -0.43884
2940.0469 | 121.8887 | -120.5383 | 1.3229 | 1.4211e-13 | -0.014055 | -0.013291 | -0.046025 | -0.041498 | -0.011924 | -0.0084697 | 2.835 | 0.007884 | -0.034513 | 0.010799 | -0.019703 | 0.15213 | 0.15708 | 0.1381 | 0.26273 | 0.21099 | 0.435 | 0.078889 | 0.3765 | 0.33918 | 0.24127 | 0.98189 | 1.1721 | 0.96926 | 0.019004 | 120.6172 | -1.0602 | 120.6905 | 120.6764 | 0.059207 | -1.1119 | -0.88794 | 120.5573 | -0.34104 | 120.9148 | 120.7796 | 0.22226 | -0.15084 | -0.35368 | 120.8011 | 120.7493 | 120.9733 | 120.6954 | -1.244 | 121.5202 | 121.7104 | 121.5076 | 120.8775 | -1.3039
2941.8438 | 122.0901 | -121.7834 | 0.09613 | 1.4211e-13 | -0.015124 | -0.013718 | -0.044957 | -0.041498 | -0.011711 | -0.00083919 | 0.029924 | 0.0070294 | -0.030881 | 0.010799 | -0.019703 | 0.001048 | 0.019721 | -0.003831 | 0.11165 | 0.087359 | 0.28848 | 0.010206 | 0.019362 | 0.078197 | -0.074666 | 0.006674 | 0.17396 | -0.0884 | -0.33814 | 121.7937 | 0.015517 | 121.7845 | 121.7796 | -0.014037 | -0.008771 | 0.19235 | 121.4453 | -0.089456 | 121.8028 | 121.7088 | 0.26348 | 0.077828 | -0.18453 | 121.8951 | 121.8708 | 122.0719 | 121.8032 | -0.085924 | 121.7901 | 121.9574 | 121.695 | 121.8616 | -0.43427
2943.6406 | 122.1954 | -121.8979 | 0.086975 | 1.4211e-13 | -0.015337 | -0.013505 | -0.045384 | -0.041284 | -0.011711 | -0.00083919 | 0.025438 | 0.007243 | -0.028103 | 0.010585 | -0.019917 | 0.001048 | 0.019721 | 0.000747 | 0.10707 | 0.08278 | 0.29306 | 0.019363 | 0.014784 | 0.082776 | -0.065509 | 0.011252 | 0.16938 | -0.11587 | -0.33814 | 121.9173 | 0.020093 | 121.8989 | 121.8986 | -0.018616 | -0.004195 | 0.20608 | 121.5597 | -0.075723 | 121.9127 | 121.8324 | 0.27264 | 0.082404 | -0.20285 | 122.005 | 121.9807 | 122.1909 | 121.9176 | -0.067612 | 121.9091 | 122.0673 | 121.782 | 121.9807 | -0.42512
2945.375 | 122.0993 | -121.9894 | 0.15106 | 1.4211e-13 | -0.01491 | -0.013505 | -0.04517 | -0.041498 | -0.012138 | -0.0161 | 0.025011 | 0.0070294 | -0.027249 | 0.010585 | -0.019703 | 0.005626 | 0.019721 | -0.008409 | 0.11165 | 0.078201 | 0.29306 | 0.014784 | 0.014784 | 0.078197 | -0.074666 | 0.015831 | 0.17396 | -0.11587 | -0.34272 | 122.0042 | -0.039415 | 121.9951 | 121.981 | -0.023193 | -0.072861 | 0.142 | 121.6467 | -0.13523 | 122.0042 | 121.9148 | 0.26806 | 0.022896 | -0.26693 | 122.1011 | 122.0676 | 122.2825 | 122.0092 | -0.13628 | 122.0053 | 122.1634 | 121.8736 | 122.0676 | -0.49379
2947.1719 | 122.2366 | -121.9528 | 0.091553 | 1.4211e-13 | -0.015124 | -0.013505 | -0.04517 | -0.041284 | -0.011924 | -0.0161 | 0.02437 | 0.0070294 | -0.026394 | 0.010799 | -0.019489 | 0.001048 | 0.015142 | -0.003831 | 0.11622 | 0.078201 | 0.29764 | 0.014784 | 0.014784 | 0.091933 | -0.079245 | 0.015831 | 0.17854 | -0.11587 | -0.33357 | 121.9676 | 0.024672 | 121.9539 | 121.949 | -0.018615 | -0.013352 | 0.20609 | 121.6193 | -0.075722 | 121.9676 | 121.8736 | 0.25432 | 0.086983 | -0.20742 | 122.069 | 122.031 | 122.2505 | 121.968 | -0.076769 | 121.9687 | 122.1314 | 121.8369 | 122.0448 | -0.42512
2948.9688 | 122.2824 | -121.9711 | 0.10529 | 1.4211e-13 | -0.01491 | -0.013505 | -0.045598 | -0.041498 | -0.011924 | -0.0161 | 0.024583 | 0.0070294 | -0.026394 | 0.010799 | -0.019489 | 0.005626 | 0.015142 | -0.003831 | 0.11165 | 0.091937 | 0.29306 | 0.023942 | 0.019362 | 0.073618 | -0.079245 | 0.011252 | 0.17396 | -0.12961 | -0.33814 | 121.9951 | 0.006361 | 121.9768 | 121.9673 | -0.027773 | -0.013349 | 0.18777 | 121.633 | -0.094034 | 121.9905 | 121.8919 | 0.2589 | 0.068672 | -0.23489 | 122.0828 | 122.0631 | 122.2642 | 121.9863 | -0.081344 | 121.9824 | 122.1451 | 121.8415 | 122.0447 | -0.44343
2950.6875 | 122.1542 | -122.0215 | 0.13733 | 1.4211e-13 | -0.014696 | -0.013505 | -0.04517 | -0.041711 | -0.011924 | 0.0067908 | 0.025438 | 0.0070294 | -0.026608 | 0.010585 | -0.019489 | 0.001048 | 0.015142 | -0.003831 | 0.11165 | 0.08278 | 0.28848 | 0.010206 | 0.019362 | 0.082776 | -0.070087 | 0.006674 | 0.17854 | -0.11129 | -0.33814 | 122.0317 | -0.025682 | 122.0225 | 122.0177 | -0.014037 | -0.054549 | 0.15115 | 121.6833 | -0.13065 | 122.0408 | 121.9514 | 0.26806 | 0.041207 | -0.24862 | 122.1331 | 122.1043 | 122.31 | 122.0366 | -0.12712 | 122.0282 | 122.2 | 121.9102 | 122.1043 | -0.47547
2952.4688 | 122.2 | -122.0169 | 0.11444 | 1.4211e-13 | -0.01491 | -0.013505 | -0.045598 | -0.041498 | -0.011711 | 0.0067908 | 0.026506 | 0.0068158 | -0.027462 | 0.010799 | -0.02013 | 0.005626 | 0.015142 | 0.000747 | 0.11622 | 0.087359 | 0.29306 | 0.019363 | 0.023941 | 0.078197 | -0.079245 | 0.011252 | 0.18311 | -0.11587 | -0.33814 | 122.0363 | 0.001784 | 122.0225 | 122.0177 | -0.018616 | -0.027082 | 0.17862 | 121.6788 | -0.10319 | 122.0408 | 121.9377 | 0.2589 | 0.068674 | -0.23031 | 122.1331 | 122.1043 | 122.31 | 122.032 | -0.095078 | 122.0282 | 122.2 | 121.901 | 122.0951 | -0.45259
2954.2344 | 122.2321 | -122.049 | 0.1236 | 1.4211e-13 | -0.01491 | -0.013718 | -0.045598 | -0.041498 | -0.011924 | -0.0084697 | 0.026933 | 0.006602 | -0.027676 | 0.010799 | -0.019917 | 0.001048 | 0.015142 | 0.000747 | 0.10707 | 0.078201 | 0.29764 | 0.010206 | 0.023941 | 0.082776 | -0.074666 | 0.006674 | 0.16938 | -0.12045 | -0.33814 | 122.0592 | -0.016528 | 122.05 | 122.0497 | -0.009459 | -0.045395 | 0.17404 | 121.7108 | -0.11692 | 122.0729 | 121.9743 | 0.26348 | 0.045783 | -0.24405 | 122.156 | 122.1272 | 122.3466 | 122.0641 | -0.11339 | 122.0556 | 122.2183 | 121.9285 | 122.1317 | -0.46174
2956.0312 | 122.1954 | -122.0352 | 0.11902 | 1.4211e-13 | -0.01491 | -0.013932 | -0.045384 | -0.041498 | -0.012352 | -0.00083919 | 0.027361 | 0.0070294 | -0.029385 | 0.010799 | -0.019276 | 0.005626 | 0.0243 | -0.003831 | 0.11622 | 0.087359 | 0.30222 | 0.019363 | 0.019362 | 0.073618 | -0.074666 | 0.011252 | 0.17396 | -0.11129 | -0.32899 | 122.0546 | -0.002794 | 122.0408 | 122.0314 | -0.023194 | -0.03166 | 0.1832 | 121.7062 | -0.10777 | 122.0546 | 121.9606 | 0.25432 | 0.054939 | -0.23031 | 122.1514 | 122.1226 | 122.3374 | 122.0595 | -0.099656 | 122.0465 | 122.2092 | 121.9239 | 122.1088 | -0.448
2957.8281 | 122.2 | -122.0627 | 0.13733 | 1.4211e-13 | -0.01491 | -0.013505 | -0.04517 | -0.041711 | -0.011711 | -0.0084697 | 0.030138 | 0.0070294 | -0.032804 | 0.010799 | -0.019703 | 0.005626 | 0.019721 | -0.003831 | 0.11622 | 0.087359 | 0.30222 | 0.019363 | 0.014784 | 0.082776 | -0.074666 | 0.011252 | 0.17854 | -0.060928 | -0.32441 | 122.082 | -0.021104 | 122.0683 | 122.0589 | -0.023194 | -0.04997 | 0.16489 | 121.7383 | -0.12608 | 122.0775 | 121.988 | 0.24974 | 0.041207 | -0.19826 | 122.1789 | 122.15 | 122.3649 | 122.0824 | -0.11797 | 122.0739 | 122.2412 | 122.0018 | 122.1455 | -0.46174
2959.625 | 122.3145 | -122.0169 | 0.10529 | 1.4211e-13 | -0.01491 | -0.013505 | -0.045598 | -0.041498 | -0.011711 | -0.0084697 | 0.030138 | 0.007243 | -0.032376 | 0.010799 | -0.019489 | 0.005626 | 0.019721 | 0.000747 | 0.11165 | 0.087359 | 0.29306 | 0.014784 | 0.023941 | 0.082776 | -0.070087 | 0.006674 | 0.16938 | -0.11129 | -0.32899 | 122.0317 | 0.006361 | 122.0225 | 122.0177 | -0.014037 | -0.017927 | 0.18777 | 121.6879 | -0.098612 | 122.0408 | 121.9468 | 0.2589 | 0.064093 | -0.21658 | 122.1286 | 122.1043 | 122.31 | 122.0366 | -0.090502 | 122.0236 | 122.1863 | 121.9056 | 122.0997 | -0.43427
2961.3594 | 122.2092 | -122.0901 | 0.12817 | 1.4211e-13 | -0.015337 | -0.013505 | -0.045384 | -0.041498 | -0.012138 | -0.00083919 | 0.03142 | 0.0074566 | -0.034513 | 0.010799 | -0.019917 | 0.001048 | 0.019721 | -0.008409 | 0.11165 | 0.08278 | 0.29764 | 0.019363 | 0.014784 | 0.087354 | -0.074666 | 0.015831 | 0.17854 | -0.083821 | -0.32899 | 122.1095 | -0.016527 | 122.0912 | 122.0817 | -0.027772 | -0.045394 | 0.16946 | 121.7612 | -0.11234 | 122.1049 | 122.0155 | 0.25432 | 0.050362 | -0.212 | 122.2018 | 122.1729 | 122.3878 | 122.1099 | -0.10881 | 122.106 | 122.2687 | 122.0063 | 122.1775 | -0.45716
2963.1406 | 122.3557 | -122.0261 | 0.082397 | 1.4211e-13 | -0.014696 | -0.014146 | -0.045384 | -0.041498 | -0.011924 | -0.0084697 | 0.031633 | 0.0083114 | -0.034726 | 0.010585 | -0.019703 | 0.001048 | 0.010564 | 0.000747 | 0.11165 | 0.08278 | 0.29306 | 0.010206 | 0.019362 | 0.087354 | -0.074666 | 0.015831 | 0.16938 | -0.10671 | -0.32441 | 122.0363 | 0.02925 | 122.0271 | 122.0268 | -0.009459 | 0.000383 | 0.21066 | 121.7017 | -0.066566 | 122.0454 | 121.9514 | 0.24974 | 0.086982 | -0.18911 | 122.1377 | 122.1088 | 122.3191 | 122.0366 | -0.072191 | 122.0419 | 122.1954 | 121.9193 | 122.1134 | -0.4068
2964.8594 | 122.2916 | -122.0627 | 0.10529 | 1.4211e-13 | -0.015124 | -0.013505 | -0.045384 | -0.041498 | -0.012138 | -0.00083919 | 0.03142 | 0.0087386 | -0.035154 | 0.010799 | -0.019703 | 0.005626 | 0.015142 | 0.005325 | 0.10707 | 0.08278 | 0.29764 | 0.023942 | 0.019362 | 0.082776 | -0.074666 | 0.020409 | 0.17396 | -0.12045 | -0.32899 | 122.0866 | 0.001782 | 122.0683 | 122.068 | -0.018617 | -0.022506 | 0.19235 | 121.7337 | -0.084877 | 122.082 | 121.988 | 0.25432 | 0.068672 | -0.22574 | 122.1698 | 122.1455 | 122.3603 | 122.0778 | -0.081344 | 122.0831 | 122.2366 | 121.9422 | 122.1455 | -0.43427
2966.5938 | 122.3373 | -122.0627 | 0.091553 | 1.4211e-13 | -0.015337 | -0.013291 | -0.04517 | -0.041711 | -0.011711 | -0.0084697 | 0.03142 | 0.009166 | -0.034726 | 0.011013 | -0.019489 | 0.005626 | 0.015142 | -0.003831 | 0.11622 | 0.087359 | 0.29306 | 0.010206 | 0.019362 | 0.082776 | -0.074666 | 0.011252 | 0.17854 | -0.11587 | -0.32899 | 122.0729 | 0.024672 | 122.0683 | 122.0589 | -0.014037 | -0.004194 | 0.20151 | 121.7337 | -0.080301 | 122.082 | 121.988 | 0.25432 | 0.086983 | -0.20742 | 122.1789 | 122.15 | 122.3557 | 122.0778 | -0.081347 | 122.0739 | 122.2412 | 121.9468 | 122.1455 | -0.42054
2968.375 | 122.3328 | -122.0581 | 0.11902 | 1.4211e-13 | -0.015124 | -0.013718 | -0.044957 | -0.041711 | -0.011924 | -0.0084697 | 0.031633 | 0.009807 | -0.035154 | 0.010585 | -0.019489 | 0.005626 | 0.0243 | 0.000747 | 0.11622 | 0.08278 | 0.29306 | 0.014784 | 0.023941 | 0.082776 | -0.074666 | 0.011252 | 0.17396 | -0.092979 | -0.32899 | 122.0729 | -0.002794 | 122.0637 | 122.0589 | -0.014037 | -0.036239 | 0.17404 | 121.7291 | -0.10777 | 122.082 | 121.9834 | 0.25432 | 0.054939 | -0.212 | 122.1743 | 122.1409 | 122.3512 | 122.0824 | -0.10423 | 122.0694 | 122.2321 | 121.9651 | 122.1409 | -0.448
2970.1562 | 122.2412 | -122.1313 | 0.12817 | 1.4211e-13 | -0.014696 | -0.013505 | -0.04517 | -0.041498 | -0.011924 | -0.0084697 | 0.032061 | 0.0095932 | -0.03494 | 0.010585 | -0.019917 | 0.005626 | 0.015142 | -0.003831 | 0.11622 | 0.073622 | 0.29306 | 0.019363 | 0.019362 | 0.078197 | -0.074666 | 0.015831 | 0.17854 | -0.10671 | -0.32899 | 122.1507 | -0.011949 | 122.137 | 122.1275 | -0.023194 | -0.054552 | 0.16489 | 121.8024 | -0.11234 | 122.1507 | 122.0567 | 0.25432 | 0.050362 | -0.23489 | 122.2476 | 122.205 | 122.4244 | 122.1465 | -0.10881 | 122.1472 | 122.3099 | 122.0246 | 122.2095 | -0.45716
2971.9531 | 122.3877 | -122.0627 | 0.091553 | 1.4211e-13 | -0.015124 | -0.013718 | -0.04517 | -0.041711 | -0.011711 | -0.0084697 | 0.030138 | 0.0093796 | -0.034513 | 0.010799 | -0.019489 | -0.003531 | 0.015142 | -0.003831 | 0.11165 | 0.08278 | 0.29764 | 0.019363 | 0.019362 | 0.078197 | -0.065509 | 0.015831 | 0.17396 | -0.11129 | -0.31983 | 122.082 | 0.020094 | 122.0592 | 122.0589 | -0.023194 | -0.008773 | 0.20609 | 121.7429 | -0.075722 | 122.082 | 121.9972 | 0.25432 | 0.082405 | -0.20285 | 122.1743 | 122.1455 | 122.3603 | 122.0778 | -0.07219 | 122.0785 | 122.2366 | 121.9514 | 122.1409 | -0.41138
2973.6719 | 122.3648 | -122.0718 | 0.1236 | 1.4211e-13 | -0.015551 | -0.013718 | -0.045384 | -0.041498 | -0.011924 | -0.00083919 | 0.031206 | 0.009166 | -0.035154 | 0.010799 | -0.019489 | 0.005626 | 0.019721 | -0.003831 | 0.10707 | 0.087359 | 0.29306 | 0.023942 | 0.023941 | 0.082776 | -0.074666 | 0.015831 | 0.18311 | -0.10214 | -0.31983 | 122.0958 | -0.016528 | 122.0775 | 122.068 | -0.027773 | -0.036237 | 0.16946 | 121.752 | -0.10776 | 122.0958 | 121.9972 | 0.24516 | 0.059519 | -0.22573 | 122.1789 | 122.1592 | 122.3649 | 122.0916 | -0.099654 | 122.0877 | 122.255 | 121.9697 | 122.1546 | -0.44342
2975.4531 | 122.3465 | -122.0993 | 0.091553 | 1.4211e-13 | -0.014696 | -0.013718 | -0.045384 | -0.041284 | -0.011711 | -0.00083919 | 0.031847 | 0.010021 | -0.034726 | 0.010799 | -0.019703 | 0.005626 | 0.019721 | 0.000747 | 0.11165 | 0.087359 | 0.30222 | 0.019363 | 0.019362 | 0.073618 | -0.074666 | 0.015831 | 0.17854 | -0.12503 | -0.31983 | 122.1187 | 0.020094 | 122.1049 | 122.1001 | -0.018616 | -0.004194 | 0.21066 | 121.7795 | -0.075722 | 122.1187 | 122.0246 | 0.24516 | 0.086983 | -0.21658 | 122.211 | 122.1867 | 122.4015 | 122.119 | -0.07219 | 122.1151 | 122.2778 | 121.9743 | 122.1729 | -0.41138
2977.1719 | 122.3648 | -122.0535 | 0.10071 | 1.4211e-13 | -0.015124 | -0.013718 | -0.04517 | -0.041498 | -0.012352 | -0.0084697 | 0.031847 | 0.010021 | -0.035154 | 0.010799 | -0.019703 | 0.010204 | 0.019721 | -0.003831 | 0.1208 | 0.087359 | 0.29306 | 0.001048 | 0.02852 | 0.078197 | -0.070087 | 0.024988 | 0.18311 | -0.083821 | -0.31983 | 122.0546 | 0.020096 | 122.0637 | 122.0497 | -0.004879 | -0.013349 | 0.19235 | 121.7337 | -0.07572 | 122.082 | 121.9834 | 0.24974 | 0.082407 | -0.18453 | 122.1743 | 122.1409 | 122.3466 | 122.0732 | -0.09966 | 122.0785 | 122.2366 | 121.9697 | 122.1317 | -0.42054
2978.9688 | 122.3969 | -122.0901 | 0.10986 | 1.4211e-13 | -0.015124 | -0.013291 | -0.04517 | -0.041925 | -0.011924 | -0.00083919 | 0.030992 | 0.010875 | -0.034726 | 0.010799 | -0.019489 | -0.003531 | 0.0243 | -0.008409 | 0.11622 | 0.087359 | 0.28848 | 0.014784 | 0.023941 | 0.078197 | -0.070087 | 0.015831 | 0.17854 | -0.10671 | -0.31983 | 122.1049 | 0.006362 | 122.0866 | 122.0817 | -0.023193 | -0.022504 | 0.17862 | 121.7703 | -0.094032 | 122.1141 | 122.0201 | 0.24974 | 0.068673 | -0.21658 | 122.2064 | 122.1775 | 122.3786 | 122.1144 | -0.095079 | 122.106 | 122.2687 | 121.9834 | 122.1683 | -0.42969
2980.7656 | 122.3145 | -122.1039 | 0.1236 | 1.4211e-13 | -0.015124 | -0.013932 | -0.045598 | -0.041498 | -0.011711 | -0.0161 | 0.030565 | 0.010875 | -0.034513 | 0.010799 | -0.019489 | 0.001048 | 0.015142 | -0.003831 | 0.11165 | 0.08278 | 0.29306 | 0.014784 | 0.023941 | 0.087354 | -0.074666 | 0.020409 | 0.18311 | -0.097557 | -0.31525 | 122.1187 | -0.011949 | 122.1049 | 122.1001 | -0.018615 | -0.040816 | 0.16946 | 121.7886 | -0.10319 | 122.1278 | 122.0292 | 0.24058 | 0.059519 | -0.22115 | 122.2155 | 122.1867 | 122.3969 | 122.119 | -0.10881 | 122.1243 | 122.287 | 122.0063 | 122.1912 | -0.43885
2982.5 | 122.4106 | -122.1085 | 0.10529 | 1.4211e-13 | -0.015124 | -0.013718 | -0.045384 | -0.041711 | -0.011924 | -0.00083919 | 0.030992 | 0.010662 | -0.034726 | 0.010799 | -0.019703 | 0.014783 | 0.019721 | 0.000747 | 0.11165 | 0.087359 | 0.29764 | 0.023942 | 0.02852 | 0.078197 | -0.065509 | 0.020409 | 0.17854 | -0.10214 | -0.31525 | 122.1324 | 0.006361 | 122.1232 | 122.1092 | -0.023195 | -0.017927 | 0.19235 | 121.7932 | -0.084877 | 122.137 | 122.0429 | 0.24974 | 0.07325 | -0.20742 | 122.2201 | 122.1958 | 122.4061 | 122.1282 | -0.081344 | 122.1289 | 122.287 | 122.0063 | 122.1867 | -0.42054
2984.2812 | 122.2824 | -122.1451 | 0.13733 | 1.4211e-13 | -0.015124 | -0.013505 | -0.04517 | -0.041925 | -0.011711 | -0.00083919 | 0.033129 | 0.011944 | -0.034726 | 0.011013 | -0.019917 | 0.005626 | 0.019721 | -0.003831 | 0.10707 | 0.087359 | 0.29306 | 0.010206 | 0.019362 | 0.073618 | -0.065509 | 0.020409 | 0.19227 | -0.10671 | -0.30609 | 122.1553 | -0.030261 | 122.1507 | 122.1412 | -0.014037 | -0.04997 | 0.15573 | 121.839 | -0.11692 | 122.1644 | 122.0796 | 0.24058 | 0.054943 | -0.24404 | 122.2521 | 122.2324 | 122.4381 | 122.1648 | -0.12712 | 122.1655 | 122.3374 | 122.0384 | 122.2187 | -0.44342
2986.0625 | 122.4289 | -122.0947 | 0.11444 | 1.4211e-13 | -0.015337 | -0.013505 | -0.04517 | -0.041284 | -0.011924 | -0.00083919 | 0.031633 | 0.011944 | -0.034726 | 0.010585 | -0.019703 | 0.010204 | 0.0243 | -0.003831 | 0.11165 | 0.078201 | 0.29306 | 0.014784 | 0.02852 | 0.082776 | -0.070087 | 0.024988 | 0.18311 | -0.092979 | -0.31067 | 122.1095 | -0.002794 | 122.1049 | 122.0909 | -0.018615 | -0.03624 | 0.17862 | 121.7841 | -0.089453 | 122.1232 | 122.0246 | 0.24058 | 0.068674 | -0.20742 | 122.2064 | 122.1729 | 122.3878 | 122.119 | -0.099657 | 122.1197 | 122.2778 | 122.0017 | 122.1775 | -0.42511
2987.8438 | 122.3877 | -122.1085 | 0.10986 | 1.4211e-13 | -0.015124 | -0.013505 | -0.045384 | -0.041498 | -0.011924 | -0.0084697 | 0.03142 | 0.011944 | -0.034726 | 0.011013 | -0.019489 | 0.005626 | 0.019721 | -0.003831 | 0.10707 | 0.078201 | 0.29764 | 0.010206 | 0.033099 | 0.078197 | -0.070087 | 0.024988 | 0.18311 | -0.10214 | -0.31525 | 122.1187 | -0.002795 | 122.1141 | 122.1046 | -0.014037 | -0.031662 | 0.18778 | 121.7932 | -0.084875 | 122.1416 | 122.0384 | 0.24516 | 0.073252 | -0.212 | 122.2155 | 122.1867 | 122.4061 | 122.1282 | -0.099657 | 122.1334 | 122.2916 | 122.0063 | 122.1867 | -0.42511
2989.5625 | 122.4289 | -122.1176 | 0.11444 | 1.4211e-13 | -0.015337 | -0.013718 | -0.044957 | -0.041498 | -0.012138 | -0.00083919 | 0.030779 | 0.012157 | -0.034726 | 0.010585 | -0.019703 | 0.010204 | 0.019721 | -0.008409 | 0.11622 | 0.087359 | 0.29306 | 0.010206 | 0.02852 | 0.078197 | -0.074666 | 0.024988 | 0.18311 | -0.11587 | -0.31525 | 122.1278 | 0.001784 | 122.1278 | 122.1092 | -0.018615 | -0.027082 | 0.17862 | 121.8024 | -0.089453 | 122.1461 | 122.0429 | 0.24058 | 0.068674 | -0.23031 | 122.2338 | 122.205 | 122.4107 | 122.1373 | -0.10423 | 122.1426 | 122.3007 | 122.0017 | 122.1958 | -0.42969
2991.3438 | 122.4243 | -122.0947 | 0.10529 | 1.4211e-13 | -0.015337 | -0.013932 | -0.044957 | -0.041498 | -0.011924 | -0.0084697 | 0.029924 | 0.012157 | -0.034726 | 0.010799 | -0.019703 | 0.010204 | 0.0243 | -0.003831 | 0.1208 | 0.091937 | 0.30222 | 0.010206 | 0.02852 | 0.078197 | -0.074666 | 0.015831 | 0.18769 | -0.0884 | -0.31067 | 122.1049 | 0.015518 | 122.1049 | 122.0909 | -0.014037 | -0.013349 | 0.19693 | 121.7841 | -0.089455 | 122.1232 | 122.0201 | 0.236 | 0.082407 | -0.19369 | 122.2155 | 122.1867 | 122.3969 | 122.119 | -0.09508 | 122.1106 | 122.2824 | 122.0063 | 122.1729 | -0.41596
2993.0625 | 122.3831 | -122.1451 | 0.10071 | 1.4211e-13 | -0.015124 | -0.013932 | -0.04517 | -0.041284 | -0.011711 | -0.00083919 | 0.030138 | 0.010662 | -0.034086 | 0.010799 | -0.019703 | 0.005626 | 0.0243 | 0.005325 | 0.10707 | 0.091937 | 0.30222 | 0.014784 | 0.037677 | 0.087354 | -0.070087 | 0.029566 | 0.18311 | -0.092979 | -0.31067 | 122.1599 | 0.00636 | 122.1507 | 122.1504 | -0.009459 | -0.008771 | 0.20151 | 121.8344 | -0.071142 | 122.1828 | 122.075 | 0.24058 | 0.082407 | -0.19369 | 122.2521 | 122.237 | 122.4473 | 122.1694 | -0.085924 | 122.1746 | 122.3282 | 122.0521 | 122.2324 | -0.41138
2994.8438 | 122.3465 | -122.1588 | 0.15106 | 1.4211e-13 | -0.015124 | -0.013505 | -0.04517 | -0.041498 | -0.011711 | -0.0084697 | 0.029924 | 0.009166 | -0.033017 | 0.011013 | -0.019489 | 0.010204 | 0.015142 | 0.005325 | 0.1208 | 0.08278 | 0.28848 | 0.019363 | 0.02852 | 0.078197 | -0.070087 | 0.029566 | 0.18311 | -0.083821 | -0.31525 | 122.1782 | -0.030258 | 122.169 | 122.1641 | -0.014038 | -0.068282 | 0.13742 | 121.8436 | -0.1215 | 122.1873 | 122.0887 | 0.24516 | 0.032053 | -0.23488 | 122.2796 | 122.2416 | 122.4473 | 122.174 | -0.1317 | 122.1884 | 122.3419 | 122.075 | 122.237 | -0.46631
2996.6406 | 122.3145 | -122.1588 | 0.14191 | 1.4211e-13 | -0.01491 | -0.013291 | -0.045384 | -0.041711 | -0.012138 | -0.023731 | 0.032274 | 0.010448 | -0.03259 | 0.010799 | -0.019489 | 0.001048 | 0.019721 | -0.003831 | 0.11622 | 0.08278 | 0.29764 | 0.019363 | 0.037677 | 0.082776 | -0.070087 | 0.029566 | 0.19685 | -0.028878 | -0.30609 | 122.1782 | -0.025682 | 122.1599 | 122.155 | -0.023194 | -0.059127 | 0.15573 | 121.8527 | -0.11234 | 122.1965 | 122.0887 | 0.236 | 0.054944 | -0.17079 | 122.275 | 122.2416 | 122.4565 | 122.1785 | -0.12254 | 122.1884 | 122.3557 | 122.1299 | 122.2416 | -0.448
2998.3594 | 122.319 | -122.1771 | 0.16022 | 1.4211e-13 | -0.015124 | -0.013932 | -0.045384 | -0.041498 | -0.012138 | 0.0067908 | 0.03377 | 0.010234 | -0.031949 | 0.010799 | -0.019489 | 0.005626 | 0.019721 | -0.017566 | 0.11622 | 0.091937 | 0.30222 | 0.019363 | 0.033099 | 0.06904 | -0.070087 | 0.029566 | 0.18311 | 0.039801 | -0.30151 | 122.1965 | -0.043992 | 122.1828 | 122.1596 | -0.036929 | -0.06828 | 0.142 | 121.8756 | -0.13065 | 122.2102 | 122.107 | 0.23143 | 0.022898 | -0.12042 | 122.2933 | 122.2691 | 122.4793 | 122.1968 | -0.14085 | 122.2067 | 122.3602 | 122.2169 | 122.2462 | -0.46173
3000.1406 | 122.4152 | -122.168 | 0.10529 | 1.4211e-13 | -0.015124 | -0.013291 | -0.045384 | -0.041498 | -0.012138 | -0.00083919 | 0.030138 | 0.010021 | -0.032376 | 0.011013 | -0.019703 | 0.005626 | 0.019721 | -0.008409 | 0.11622 | 0.087359 | 0.29764 | 0.019363 | 0.042256 | 0.082776 | -0.074666 | 0.034145 | 0.19685 | -0.019721 | -0.29693 | 122.1873 | 0.010939 | 122.1736 | 122.1596 | -0.027772 | -0.017927 | 0.19235 | 121.871 | -0.071141 | 122.2102 | 122.0933 | 0.22227 | 0.091565 | -0.12501 | 122.2842 | 122.2553 | 122.4656 | 122.1877 | -0.085923 | 122.2021 | 122.3648 | 122.1482 | 122.2507 | -0.40222
3001.875 | 122.3465 | -122.1771 | 0.14648 | 1.4211e-13 | -0.015124 | -0.013718 | -0.04517 | -0.041498 | -0.011711 | -0.00083919 | 0.023942 | 0.009166 | -0.032376 | 0.01144 | -0.019489 | 0.010204 | 0.019721 | -0.003831 | 0.1208 | 0.096516 | 0.29764 | 0.014784 | 0.051413 | 0.082776 | -0.074666 | 0.052459 | 0.21059 | 0.026065 | -0.28778 | 122.1919 | -0.02568 | 122.1873 | 122.1733 | -0.018615 | -0.049968 | 0.15115 | 121.8893 | -0.094025 | 122.2285 | 122.1025 | 0.21311 | 0.064102 | -0.12042 | 122.2979 | 122.2736 | 122.4748 | 122.1968 | -0.1317 | 122.2296 | 122.3877 | 122.2032 | 122.2599 | -0.43426
3003.6719 | 122.3236 | -122.1863 | 0.17395 | 1.4211e-13 | -0.015337 | -0.013505 | -0.04517 | -0.041711 | -0.011711 | -0.0084697 | 0.01796 | 0.008525 | -0.033658 | 0.011226 | -0.019703 | 0.005626 | 0.0243 | 0.005325 | 0.11622 | 0.091937 | 0.30222 | 0.014784 | 0.06515 | 0.073618 | -0.083823 | 0.052459 | 0.21974 | 0.081008 | -0.27404 | 122.2011 | -0.057725 | 122.1919 | 122.1916 | -0.009459 | -0.082013 | 0.12827 | 121.9122 | -0.12149 | 122.2514 | 122.1025 | 0.19022 | 0.045794 | -0.092942 | 122.3025 | 122.2782 | 122.4885 | 122.2106 | -0.15917 | 122.2387 | 122.406 | 122.2673 | 122.2599 | -0.44799
3005.4688 | 122.4792 | -122.0947 | 0.15564 | 1.4211e-13 | -0.015337 | -0.013718 | -0.04517 | -0.041711 | -0.011924 | -0.00083919 | 0.013688 | 0.007884 | -0.034726 | 0.011013 | -0.019489 | 0.010204 | 0.0243 | 0.005325 | 0.1208 | 0.091937 | 0.3068 | 0.014784 | 0.078886 | 0.078197 | -0.074666 | 0.066194 | 0.2289 | 0.090166 | -0.2603 | 122.1095 | -0.034836 | 122.1049 | 122.1001 | -0.009459 | -0.063703 | 0.15116 | 121.8344 | -0.089446 | 122.1736 | 122.0201 | 0.18564 | 0.073261 | -0.065474 | 122.2155 | 122.1867 | 122.4015 | 122.119 | -0.14086 | 122.1609 | 122.3236 | 122.1849 | 122.1729 | -0.41594
3007.2656 | 122.374 | -122.1405 | 0.17853 | 1.4211e-13 | -0.015124 | -0.013718 | -0.04517 | -0.041284 | -0.011711 | -0.0084697 | 0.013047 | 0.0074566 | -0.034513 | 0.011226 | -0.019917 | 0.010204 | 0.019721 | -0.008409 | 0.12538 | 0.091937 | 0.29306 | 0.023942 | 0.083464 | 0.073618 | -0.079245 | 0.070773 | 0.23348 | 0.085587 | -0.25115 | 122.1644 | -0.053146 | 122.1507 | 122.1321 | -0.032351 | -0.086591 | 0.11453 | 121.8894 | -0.10775 | 122.224 | 122.0613 | 0.1719 | 0.054951 | -0.092941 | 122.2659 | 122.2324 | 122.4336 | 122.1602 | -0.15459 | 122.2113 | 122.374 | 122.2261 | 122.2141 | -0.42967
3008.9844 | 122.4472 | -122.0947 | 0.17853 | 1.4211e-13 | -0.015337 | -0.013718 | -0.045384 | -0.041711 | -0.012138 | -0.0084697 | 0.013474 | 0.0074566 | -0.034513 | 0.011013 | -0.019917 | 0.014783 | 0.0243 | 0.009904 | 0.1208 | 0.096516 | 0.30222 | 0.019363 | 0.10178 | 0.078197 | -0.074666 | 0.093665 | 0.24721 | 0.10848 | -0.24199 | 122.1141 | -0.057724 | 122.1095 | 122.1046 | -0.009459 | -0.082012 | 0.12369 | 121.8527 | -0.084863 | 122.1965 | 122.0201 | 0.16732 | 0.068687 | -0.070048 | 122.2155 | 122.1912 | 122.3969 | 122.119 | -0.15917 | 122.1884 | 122.3419 | 122.2032 | 122.1729 | -0.42052
3010.7656 | 122.3602 | -121.7789 | 0.51727 | 1.4211e-13 | -0.014696 | -0.013505 | -0.045598 | -0.041498 | -0.011924 | 0.0067908 | 0.01262 | 0.0074566 | -0.034299 | 0.010799 | -0.019489 | 0.037675 | 0.047193 | 0.041952 | 0.14369 | 0.11941 | 0.33427 | 0.10178 | 0.36277 | 0.073618 | -0.079245 | 0.34548 | 0.51277 | 0.32367 | 0.028162 | 121.8807 | -0.37358 | 121.8165 | 121.8208 | -0.059832 | -0.39786 | -0.18301 | 121.807 | -0.17179 | 122.1416 | 121.6996 | -0.10741 | -0.004499 | -0.1936 | 121.9226 | 121.8983 | 122.1131 | 121.8261 | -0.41549 | 122.1244 | 122.2916 | 122.1025 | 121.8525 | -0.48911
3012.4844 | 122.4426 | -121.6507 | 0.58136 | 1.4211e-13 | -0.01491 | -0.013505 | -0.045384 | -0.041498 | -0.011924 | -0.00083919 | 0.01262 | 0.0074566 | -0.034726 | 0.010585 | -0.019489 | 0.037675 | 0.05635 | 0.028217 | 0.15743 | 0.11483 | 0.32969 | 0.023942 | 0.38108 | 0.073618 | -0.079245 | 0.3638 | 0.53567 | 0.32825 | 0.046477 | 121.6746 | -0.42393 | 121.6884 | 121.6789 | 0.004275 | -0.46653 | -0.25167 | 121.6972 | -0.21756 | 122.0318 | 121.5715 | -0.12572 | -0.045693 | -0.25311 | 121.8081 | 121.7655 | 121.9804 | 121.707 | -0.55742 | 122.0145 | 122.1864 | 121.9789 | 121.7243 | -0.53488
3014.2656 | 122.2595 | -120.5246 | 1.5793 | 1.4211e-13 | -0.014269 | -0.013505 | -0.046025 | -0.041498 | -0.011497 | -0.0084697 | 0.014115 | 0.0083114 | -0.033017 | 0.0097307 | -0.018421 | 0.15671 | 0.16166 | 0.15183 | 0.26273 | 0.21557 | 0.45331 | 0.069732 | 1.5074 | 0.073618 | -0.074666 | 1.4901 | 1.6528 | 1.4592 | 1.1683 | 120.5943 | -1.3166 | 120.6813 | 120.6764 | 0.082098 | -1.3637 | -1.126 | 121.6929 | -0.089179 | 122.032 | 120.4499 | -1.243 | 0.073561 | -0.12012 | 120.7873 | 120.7402 | 120.9779 | 120.6863 | -1.5096 | 122.0147 | 122.1774 | 121.9838 | 120.5982 | -0.411
3015.9844 | 122.2549 | -121.4859 | 0.54474 | 1.4211e-13 | -0.015124 | -0.013932 | -0.045598 | -0.041925 | -0.012138 | -0.0084697 | 0.26215 | 0.077537 | 0.024668 | 0.011013 | -0.019489 | 0.05141 | 0.065507 | 0.051108 | 0.17117 | 0.14231 | 0.35258 | 0.055995 | 0.43602 | 0.16061 | -0.079245 | 0.4691 | 0.64097 | 0.49766 | 0.11058 | 121.5419 | -0.37357 | 121.5373 | 121.537 | -0.004887 | -0.40243 | -0.19216 | 121.5965 | -0.075637 | 121.9219 | 121.4067 | -0.18982 | 0.096236 | -0.047078 | 121.6571 | 121.6282 | 121.8385 | 121.5514 | -0.48874 | 121.955 | 122.1269 | 121.9836 | 121.6465 | -0.43416
3017.7812 | 121.9528 | -120.6665 | 1.2909 | 1.4211e-13 | -0.014696 | -0.013291 | -0.045811 | -0.041925 | -0.011924 | -0.00083919 | 1.7662 | 0.23458 | 0.19623 | 0.010585 | -0.019276 | 0.13382 | 0.13876 | 0.1152 | 0.23984 | 0.1881 | 0.42584 | 0.083468 | 0.60086 | 0.31629 | -0.070087 | 0.959 | 1.1355 | 1.0105 | 0.26168 | 120.75 | -1.0511 | 120.8003 | 120.7817 | 0.031736 | -1.1028 | -0.86505 | 120.9282 | -0.33189 | 121.2674 | 120.5964 | -0.33177 | -0.15543 | -0.28043 | 120.9063 | 120.8546 | 121.0923 | 120.8053 | -1.2074 | 121.6255 | 121.802 | 121.677 | 120.9828 | -1.0292
3019.5625 | 122.3099 | -122.0764 | 0.11902 | 1.4211e-13 | -0.015551 | -0.013505 | -0.044743 | -0.041284 | -0.012138 | -0.00083919 | 0.025011 | 0.011089 | -0.032163 | 0.011013 | -0.019917 | 0.010204 | 0.015142 | -0.003831 | 0.11622 | 0.091937 | 0.29764 | 0.019363 | 0.02852 | 0.082776 | -0.083823 | 0.015831 | 0.17854 | -0.11129 | -0.30151 | 122.0958 | -0.002794 | 122.0866 | 122.0726 | -0.023194 | -0.027082 | 0.17862 | 121.7749 | -0.10319 | 122.1049 | 121.9926 | 0.21769 | 0.059517 | -0.23031 | 122.1926 | 122.1684 | 122.3741 | 122.0916 | -0.099656 | 122.0922 | 122.255 | 121.9651 | 122.1592 | -0.42053
3021.2656 | 122.3831 | -122.049 | 0.13733 | 1.4211e-13 | -0.015337 | -0.013932 | -0.045384 | -0.041711 | -0.012352 | 0.0067908 | 0.063893 | 0.019635 | -0.023403 | 0.010799 | -0.019703 | 0.005626 | 0.019721 | 0.005325 | 0.11622 | 0.096516 | 0.29764 | 0.014784 | 0.042256 | 0.087354 | -0.083823 | 0.043302 | 0.21516 | -0.015142 | -0.29693 | 122.0637 | -0.021104 | 122.0546 | 122.0543 | -0.009459 | -0.040813 | 0.16031 | 121.752 | -0.094027 | 122.0912 | 121.9651 | 0.21311 | 0.077836 | -0.15247 | 122.1652 | 122.1455 | 122.3466 | 122.0687 | -0.12255 | 122.0923 | 122.2641 | 122.0338 | 122.1363 | -0.43426
3023.0625 | 122.4152 | -122.0901 | 0.1236 | 1.4211e-13 | -0.015124 | -0.013291 | -0.04517 | -0.041498 | -0.012138 | -0.00083919 | 0.049579 | 0.015789 | -0.021694 | 0.011226 | -0.019703 | 0.005626 | 0.0243 | 0.000747 | 0.11622 | 0.087359 | 0.29764 | 0.010206 | 0.02852 | 0.087354 | -0.083823 | 0.034145 | 0.19685 | -0.001407 | -0.29236 | 122.1004 | -0.007371 | 122.0958 | 122.0909 | -0.009459 | -0.036237 | 0.17404 | 121.7978 | -0.089451 | 122.1187 | 122.0063 | 0.20853 | 0.073255 | -0.125 | 122.2064 | 122.1775 | 122.3878 | 122.1144 | -0.11339 | 122.1243 | 122.287 | 122.0887 | 122.1775 | -0.41595
3024.8594 | 122.3465 | -122.0947 | 0.18768 | 1.4211e-13 | -0.01491 | -0.013505 | -0.04517 | -0.041284 | -0.012138 | -0.0084697 | 0.073293 | 0.025404 | -0.0088749 | 0.01144 | -0.019703 | 0.010204 | 0.019721 | 0.009904 | 0.1208 | 0.091937 | 0.30222 | 0.019363 | 0.051413 | 0.096512 | -0.088402 | 0.04788 | 0.21516 | 0.071851 | -0.27862 | 122.1141 | -0.066879 | 122.1049 | 122.1046 | -0.009459 | -0.095746 | 0.11453 | 121.8161 | -0.1398 | 122.1461 | 122.0063 | 0.19022 | 0.027482 | -0.11583 | 122.2155 | 122.1867 | 122.3969 | 122.1144 | -0.16832 | 122.1426 | 122.3099 | 122.1666 | 122.1912 | -0.4663
3026.6406 | 122.438 | -122.1451 | 0.09613 | 1.4211e-13 | -0.015337 | -0.013505 | -0.044957 | -0.041284 | -0.011924 | -0.0084697 | 0.023942 | 0.010448 | -0.029813 | 0.011226 | -0.019703 | 0.001048 | 0.0243 | -0.003831 | 0.11165 | 0.087359 | 0.29306 | 0.019363 | 0.019362 | 0.091933 | -0.074666 | 0.029566 | 0.18311 | -0.12045 | -0.29693 | 122.1644 | 0.015517 | 122.1461 | 122.1412 | -0.023194 | -0.008771 | 0.19693 | 121.8481 | -0.066564 | 122.1644 | 122.0704 | 0.22227 | 0.086985 | -0.21658 | 122.2567 | 122.2324 | 122.4381 | 122.1694 | -0.076767 | 122.1746 | 122.3282 | 122.0246 | 122.237 | -0.39306
3028.3594 | 122.4518 | -122.1451 | 0.10986 | 1.4211e-13 | -0.015124 | -0.013718 | -0.045384 | -0.041284 | -0.012138 | -0.00083919 | 0.023729 | 0.010662 | -0.029385 | 0.011013 | -0.019489 | 0.001048 | 0.0243 | -0.003831 | 0.11165 | 0.087359 | 0.29306 | 0.019363 | 0.02852 | 0.087354 | -0.083823 | 0.015831 | 0.18311 | -0.097557 | -0.30151 | 122.1644 | 0.001784 | 122.1461 | 122.1412 | -0.023194 | -0.022504 | 0.1832 | 121.8436 | -0.094032 | 122.1736 | 122.0613 | 0.21769 | 0.073252 | -0.20742 | 122.2567 | 122.2324 | 122.4381 | 122.1694 | -0.0905 | 122.1609 | 122.3282 | 122.0475 | 122.2324 | -0.41138
3030.1406 | 122.4609 | -122.0718 | 0.16479 | 1.4211e-13 | -0.015124 | -0.013505 | -0.045384 | -0.041284 | -0.012138 | 0.0067908 | 0.08312 | 0.02519 | -0.00011532 | 0.010799 | -0.019489 | 0.014783 | 0.0243 | 0.005325 | 0.1208 | 0.096516 | 0.30222 | 0.014784 | 0.083464 | 0.12856 | -0.083823 | 0.07993 | 0.24721 | 0.099323 | -0.24657 | 122.0866 | -0.043991 | 122.0866 | 122.0772 | -0.009459 | -0.068279 | 0.13742 | 121.8253 | -0.084865 | 122.1553 | 121.988 | 0.16274 | 0.08242 | -0.065472 | 122.1926 | 122.1684 | 122.3741 | 122.0961 | -0.15001 | 122.1518 | 122.3191 | 122.1712 | 122.2004 | -0.41136
3031.875 | 122.2549 | -121.9299 | 0.37079 | 1.4211e-13 | -0.015337 | -0.013291 | -0.045384 | -0.041284 | -0.011924 | -0.00083919 | 0.19165 | 0.057453 | 0.059065 | 0.010799 | -0.019917 | 0.028518 | 0.042614 | 0.01906 | 0.13912 | 0.11025 | 0.31595 | 0.028521 | 0.15215 | 0.17893 | -0.088402 | 0.18066 | 0.33421 | 0.18174 | -0.17331 | 121.9585 | -0.23167 | 121.9584 | 121.949 | -0.009461 | -0.26054 | -0.054836 | 121.7566 | -0.19013 | 122.0821 | 121.8415 | 0.084904 | -0.03658 | -0.18905 | 122.069 | 122.0402 | 122.2459 | 121.9725 | -0.34227 | 122.1106 | 122.2641 | 122.1117 | 122.1089 | -0.54409
3033.6719 | 122.4564 | -122.1542 | 0.09613 | 1.4211e-13 | -0.015337 | -0.013077 | -0.04517 | -0.041498 | -0.011924 | -0.00083919 | 0.082266 | 0.023054 | 0.0039439 | 0.011226 | -0.019703 | 0.010204 | 0.0243 | 0.005325 | 0.12538 | 0.096516 | 0.3068 | -0.035584 | 0.069728 | 0.11025 | -0.079245 | 0.075351 | 0.23806 | 0.099323 | -0.26488 | 122.1187 | 0.029252 | 122.1644 | 122.1596 | 0.040909 | 0.000386 | 0.21067 | 121.8894 | -0.020779 | 122.224 | 122.075 | 0.18564 | 0.14193 | 0.003193 | 122.2796 | 122.2508 | 122.461 | 122.1785 | -0.13171 | 122.2296 | 122.3923 | 122.2536 | 122.2645 | -0.36101
3035.3906 | 122.4655 | -122.1359 | 0.086975 | 1.4211e-13 | -0.015337 | -0.013291 | -0.04517 | -0.041925 | -0.012138 | -0.0084697 | 0.020738 | 0.009807 | -0.029599 | 0.010799 | -0.019703 | 0.001048 | 0.019721 | 0.000747 | 0.11165 | 0.091937 | 0.29764 | 0.010206 | 0.023941 | 0.078197 | -0.083823 | 0.011252 | 0.17854 | -0.11129 | -0.30609 | 122.1461 | 0.024672 | 122.137 | 122.1367 | -0.009459 | 0.004962 | 0.21066 | 121.8298 | -0.075723 | 122.1599 | 122.0521 | 0.22227 | 0.091561 | -0.19827 | 122.2476 | 122.2279 | 122.4336 | 122.1556 | -0.076769 | 122.1472 | 122.3145 | 122.0246 | 122.2141 | -0.39307
3037.1875 | 122.3557 | -122.2366 | 0.14191 | 1.4211e-13 | -0.015337 | -0.013077 | -0.045384 | -0.041711 | -0.012138 | 0.0067908 | 0.020951 | 0.009166 | -0.028744 | 0.010799 | -0.019276 | 0.005626 | 0.019721 | -0.003831 | 0.1208 | 0.078201 | 0.29764 | 0.019363 | 0.023941 | 0.082776 | -0.088402 | 0.011252 | 0.17396 | -0.0884 | -0.30609 | 122.256 | -0.021103 | 122.2423 | 122.2328 | -0.023194 | -0.063706 | 0.15573 | 121.9305 | -0.13065 | 122.2606 | 122.1482 | 0.21769 | 0.032051 | -0.23031 | 122.3574 | 122.3148 | 122.5343 | 122.2564 | -0.12254 | 122.2479 | 122.4106 | 122.1482 | 122.3194 | -0.448
3038.9219 | 122.4747 | -122.1817 | 0.07782 | 1.4211e-13 | -0.015124 | -0.013077 | -0.044957 | -0.041711 | -0.011924 | 0.014421 | 0.022447 | 0.009166 | -0.029172 | 0.011013 | -0.019917 | 0.005626 | 0.015142 | 0.000747 | 0.11622 | 0.096516 | 0.30222 | 0.005627 | 0.023941 | 0.087354 | -0.074666 | 0.015831 | 0.18311 | -0.0243 | -0.30151 | 122.1873 | 0.038405 | 122.1873 | 122.1824 | -0.00488 | 0.018696 | 0.2244 | 121.8802 | -0.061989 | 122.2056 | 122.107 | 0.22685 | 0.10529 | -0.10212 | 122.2979 | 122.2782 | 122.4839 | 122.1968 | -0.072193 | 122.1975 | 122.3648 | 122.1574 | 122.2691 | -0.37933
3040.7031 | 122.406 | -122.2183 | 0.16937 | 1.4211e-13 | -0.015124 | -0.013077 | -0.04517 | -0.041284 | -0.011284 | -0.00083919 | 0.03847 | 0.010021 | -0.025967 | 0.011226 | -0.019917 | 0.005626 | 0.019721 | 0.000747 | 0.11622 | 0.078201 | 0.30222 | 0.010206 | 0.023941 | 0.087354 | -0.083823 | 0.020409 | 0.19227 | -0.092979 | -0.29693 | 122.2285 | -0.053148 | 122.2239 | 122.2191 | -0.009459 | -0.091172 | 0.13284 | 121.9214 | -0.14896 | 122.2423 | 122.1345 | 0.21311 | 0.022899 | -0.26235 | 122.3345 | 122.2965 | 122.5205 | 122.238 | -0.15917 | 122.2387 | 122.4106 | 122.1253 | 122.3057 | -0.46631
3042.5 | 122.4426 | -122.2046 | 0.11444 | 1.4211e-13 | -0.015337 | -0.013077 | -0.044957 | -0.041284 | -0.012138 | -0.0084697 | 0.028215 | 0.0093796 | -0.031949 | 0.011226 | -0.019489 | 0.005626 | 0.019721 | 0.005325 | 0.11165 | 0.08278 | 0.29764 | 0.014784 | 0.02852 | 0.082776 | -0.079245 | 0.015831 | 0.17396 | -0.12045 | -0.30151 | 122.2194 | -0.002794 | 122.2102 | 122.2099 | -0.009459 | -0.031661 | 0.1832 | 121.9031 | -0.09861 | 122.2331 | 122.1253 | 0.22227 | 0.059517 | -0.23489 | 122.3162 | 122.2874 | 122.5022 | 122.2243 | -0.099657 | 122.2204 | 122.3785 | 122.0841 | 122.2874 | -0.41595
3044.2344 | 122.3877 | -122.2458 | 0.13733 | 1.4211e-13 | -0.015337 | -0.013291 | -0.044957 | -0.041498 | -0.011711 | -0.00083919 | 0.028215 | 0.0087386 | -0.032376 | 0.011226 | -0.019917 | 0.005626 | 0.019721 | -0.003831 | 0.11165 | 0.087359 | 0.29764 | 0.010206 | 0.019362 | 0.078197 | -0.070087 | 0.015831 | 0.17854 | -0.11587 | -0.30151 | 122.256 | -0.025682 | 122.2514 | 122.242 | -0.014037 | -0.04997 | 0.16031 | 121.9443 | -0.1215 | 122.2652 | 122.1757 | 0.23143 | 0.041207 | -0.2532 | 122.3574 | 122.3331 | 122.5434 | 122.2655 | -0.12712 | 122.2616 | 122.4243 | 122.1299 | 122.324 | -0.43884
3046.0156 | 122.4976 | -121.9299 | 0.32501 | 1.4211e-13 | -0.015124 | -0.013505 | -0.04517 | -0.041498 | -0.011711 | -0.0084697 | 0.33222 | 0.047411 | 0.011635 | 0.011226 | -0.019917 | 0.019361 | 0.042614 | 0.032795 | 0.13912 | 0.10567 | 0.32511 | 0.069732 | 0.13841 | 0.15604 | 0.021487 | 0.19439 | 0.36168 | 0.21837 | -0.18704 | 121.9997 | -0.1859 | 121.9493 | 121.9627 | -0.036937 | -0.21934 | 9.8e-05 | 121.7429 | -0.13062 | 122.0683 | 121.9514 | 0.20853 | 0.036668 | -0.10665 | 122.069 | 122.0356 | 122.255 | 121.9725 | -0.25528 | 122.1243 | 122.2916 | 122.1483 | 122.086 | -0.51206
3047.8125 | 122.3923 | -121.7743 | 0.43488 | 1.4211e-13 | -0.015337 | -0.013291 | -0.045384 | -0.041711 | -0.011924 | -0.00083919 | 0.46639 | 0.09762 | 0.01249 | 0.011226 | -0.019917 | 0.033096 | 0.051771 | 0.032795 | 0.15285 | 0.11941 | 0.33427 | 0.078889 | 0.19335 | 0.16061 | 0.067274 | 0.27223 | 0.4441 | 0.30078 | -0.14125 | 121.8532 | -0.28202 | 121.8074 | 121.8071 | -0.046094 | -0.31546 | -0.10061 | 121.633 | -0.16265 | 121.9676 | 121.8416 | 0.20853 | 0.00922 | -0.13409 | 121.9271 | 121.8937 | 122.1086 | 121.8261 | -0.35599 | 122.0465 | 122.2184 | 122.0751 | 121.9349 | -0.57613
3049.5938 | 122.3099 | -121.669 | 0.45776 | 1.4211e-13 | -0.015124 | -0.013291 | -0.045598 | -0.041498 | -0.012138 | -0.0084697 | 0.58132 | 0.11471 | -0.0031065 | 0.011226 | -0.019703 | 0.046831 | 0.060928 | 0.037373 | 0.14827 | 0.12857 | 0.33885 | 0.11552 | 0.22083 | 0.19267 | 0.094746 | 0.33175 | 0.49446 | 0.3603 | -0.11378 | 121.7845 | -0.30949 | 121.7158 | 121.7064 | -0.078148 | -0.3292 | -0.11892 | 121.5552 | -0.12602 | 121.8898 | 121.7638 | 0.20853 | 0.036696 | -0.097461 | 121.8173 | 121.7976 | 122.0079 | 121.7299 | -0.34224 | 122.0008 | 122.1635 | 122.0293 | 121.8617 | -0.57155
3051.375 | 122.3145 | -121.4493 | 0.6546 | 1.4211e-13 | -0.015124 | -0.013077 | -0.045384 | -0.041711 | -0.011711 | -0.00083919 | 0.81504 | 0.17304 | 0.012276 | 0.011226 | -0.019917 | 0.065145 | 0.065507 | 0.055687 | 0.16659 | 0.13773 | 0.35258 | 0.11094 | 0.26203 | 0.18809 | 0.14053 | 0.43247 | 0.59977 | 0.49766 | -0.049678 | 121.5602 | -0.48801 | 121.5144 | 121.505 | -0.055255 | -0.51687 | -0.30202 | 121.3996 | -0.22213 | 121.7113 | 121.5898 | 0.19021 | -0.054834 | -0.15694 | 121.6159 | 121.587 | 121.8019 | 121.5148 | -0.54366 | 121.8818 | 122.049 | 121.9469 | 121.6374 | -0.70428
3053.1719 | 122.2 | -121.3531 | 0.71411 | 1.4211e-13 | -0.015124 | -0.013505 | -0.046025 | -0.041498 | -0.012138 | -0.00083919 | 0.91951 | 0.24248 | 0.02424 | 0.01144 | -0.019489 | 0.074302 | 0.079243 | 0.060265 | 0.16659 | 0.13773 | 0.36174 | 0.11094 | 0.28035 | 0.20182 | 0.14511 | 0.4691 | 0.64097 | 0.48392 | -0.0451 | 121.4641 | -0.54752 | 121.4275 | 121.4134 | -0.050677 | -0.57638 | -0.35237 | 121.308 | -0.24501 | 121.6335 | 121.4983 | 0.19021 | -0.073136 | -0.23019 | 121.5197 | 121.4909 | 121.7149 | 121.4324 | -0.60317 | 121.8223 | 121.9941 | 121.8371 | 121.555 | -0.75921
3054.9688 | 122.0764 | -121.2524 | 0.76446 | 1.4211e-13 | -0.015124 | -0.013291 | -0.045811 | -0.041498 | -0.012565 | -0.0084697 | 1.1913 | 0.1974 | 0.01719 | 0.010799 | -0.019917 | 0.074302 | 0.083821 | 0.069421 | 0.1849 | 0.15146 | 0.36632 | 0.10178 | 0.27577 | 0.18351 | 0.14969 | 0.51946 | 0.68676 | 0.52513 | -0.049678 | 121.3542 | -0.57956 | 121.3267 | 121.3219 | -0.032363 | -0.613 | -0.39815 | 121.2028 | -0.245 | 121.5282 | 121.4021 | 0.19937 | -0.077704 | -0.23933 | 121.4373 | 121.4039 | 121.6188 | 121.3363 | -0.66268 | 121.7719 | 121.9392 | 121.7776 | 121.4359 | -0.81414
3056.7656 | 122.0123 | -121.0602 | 0.90179 | 1.4211e-13 | -0.015124 | -0.012863 | -0.045811 | -0.041498 | -0.012138 | -0.00083919 | 1.3479 | 0.36362 | 0.079148 | 0.011226 | -0.019489 | 0.07888 | 0.0884 | 0.074 | 0.19406 | 0.15146 | 0.37548 | 0.097205 | 0.28035 | 0.18351 | 0.13595 | 0.56067 | 0.73255 | 0.5755 | -0.049678 | 121.1574 | -0.70774 | 121.1391 | 121.1342 | -0.023205 | -0.75033 | -0.52632 | 121.0105 | -0.34112 | 121.3405 | 121.1961 | 0.18563 | -0.16925 | -0.3263 | 121.2542 | 121.2116 | 121.4357 | 121.1486 | -0.80459 | 121.6209 | 121.7927 | 121.6357 | 121.2437 | -0.95147
3058.5625 | 122.0856 | -120.9412 | 0.89264 | 1.4211e-13 | -0.01491 | -0.013077 | -0.046025 | -0.041498 | -0.011924 | -0.00083919 | 1.5831 | 0.21406 | 0.076584 | 0.011226 | -0.019489 | 0.088037 | 0.097557 | 0.083156 | 0.19864 | 0.16062 | 0.37548 | 0.10178 | 0.26661 | 0.18351 | 0.11306 | 0.58814 | 0.77375 | 0.5526 | -0.063415 | 121.0429 | -0.694 | 121.0292 | 121.0243 | -0.018628 | -0.73202 | -0.51716 | 120.8777 | -0.3045 | 121.2078 | 121.0542 | 0.17648 | -0.11888 | -0.34003 | 121.1398 | 121.1018 | 121.3166 | 121.0387 | -0.79085 | 121.5293 | 121.7149 | 121.4938 | 121.1247 | -0.95605
3060.2812 | 122.0306 | -121.17 | 0.60425 | 1.4211e-13 | -0.015337 | -0.013505 | -0.04517 | -0.041498 | -0.012138 | -0.00083919 | 1.2047 | 0.15787 | 0.016335 | 0.01144 | -0.019917 | 0.074302 | 0.074664 | 0.064843 | 0.18032 | 0.13773 | 0.36174 | 0.10636 | 0.20709 | 0.1423 | 0.067274 | 0.46452 | 0.64097 | 0.4885 | -0.10462 | 121.2764 | -0.42392 | 121.2443 | 121.2349 | -0.04152 | -0.46652 | -0.24251 | 121.0654 | -0.13972 | 121.3771 | 121.2373 | 0.1719 | 0.036727 | -0.11574 | 121.3504 | 121.3078 | 121.5318 | 121.2447 | -0.49789 | 121.6346 | 121.811 | 121.6585 | 121.3123 | -0.70887
3062.0625 | 122.0078 | -120.8176 | 0.94299 | 1.4211e-13 | -0.01491 | -0.013718 | -0.045811 | -0.041284 | -0.011924 | -0.00083919 | 1.6044 | 0.20723 | 0.036632 | 0.011013 | -0.019489 | 0.088037 | 0.097557 | 0.083156 | 0.20321 | 0.16062 | 0.37548 | 0.10178 | 0.16588 | 0.16519 | 0.10848 | 0.61561 | 0.79207 | 0.6167 | -0.040521 | 120.9193 | -0.73978 | 120.9056 | 120.9007 | -0.018628 | -0.78237 | -0.56752 | 120.777 | -0.32738 | 120.9834 | 120.926 | 0.149 | -0.15092 | -0.32629 | 121.0208 | 120.9782 | 121.193 | 120.9151 | -0.84121 | 121.4332 | 121.6096 | 121.4343 | 120.9828 | -0.98351
3063.8594 | 121.843 | -120.3186 | 1.3184 | 1.4211e-13 | -0.014483 | -0.013077 | -0.045598 | -0.041498 | -0.011924 | -0.0084697 | 2.5494 | 0.20958 | -0.0099431 | 0.011013 | -0.019703 | 0.1384 | 0.13876 | 0.12436 | 0.23984 | 0.19267 | 0.42584 | 0.088047 | 0.21625 | 0.18351 | 0.13595 | 0.91779 | 1.108 | 0.95094 | 0.064792 | 120.4067 | -1.0785 | 120.457 | 120.443 | 0.036314 | -1.1257 | -0.89252 | 120.3834 | -0.40057 | 120.5349 | 120.4546 | 0.071163 | -0.21037 | -0.36742 | 120.5584 | 120.5113 | 120.7444 | 120.4574 | -1.2303 | 121.2364 | 121.4266 | 121.2695 | 120.5021 | -1.2536
3065.6562 | 121.756 | -120.7764 | 0.86517 | 1.4211e-13 | -0.014696 | -0.013291 | -0.045384 | -0.041498 | -0.012138 | -0.00083919 | 2.2941 | 0.30572 | 0.0283 | 0.01144 | -0.019703 | 0.12009 | 0.12045 | 0.10605 | 0.22153 | 0.18352 | 0.40295 | 0.088047 | 0.14299 | 0.16519 | 0.016908 | 0.75755 | 0.94774 | 0.79527 | -0.049678 | 120.8644 | -0.64365 | 120.8965 | 120.8824 | 0.018001 | -0.68166 | -0.46223 | 120.7267 | -0.10763 | 120.9194 | 120.7933 | 0.066586 | 0.082568 | -0.069903 | 120.9979 | 120.9599 | 121.1793 | 120.8968 | -0.77713 | 121.5339 | 121.7241 | 121.5716 | 120.9416 | -0.91485
3067.375 | 121.7285 | -120.7672 | 0.93384 | 1.4211e-13 | -0.015124 | -0.013077 | -0.045811 | -0.041711 | -0.011924 | -0.00083919 | 1.6957 | 0.36127 | -0.0054565 | 0.01144 | -0.019703 | 0.092615 | 0.083821 | 0.074 | 0.19406 | 0.16062 | 0.38463 | 0.10636 | 0.1613 | 0.15604 | 0.026066 | 0.55151 | 0.73713 | 0.56634 | -0.1321 | 120.8736 | -0.73978 | 120.8598 | 120.8412 | -0.032363 | -0.77322 | -0.54921 | 120.6351 | -0.38232 | 120.9285 | 120.7933 | 0.15816 | -0.19671 | -0.3675 | 120.9613 | 120.9278 | 121.1518 | 120.851 | -0.82747 | 121.3187 | 121.5043 | 121.3336 | 120.9232 | -1.0659
3069.1719 | 121.5134 | -118.602 | 2.7878 | 1.4211e-13 | -0.014483 | -0.01265 | -0.046666 | -0.041284 | -0.012138 | -0.0084697 | 3.7227 | 0.12967 | -0.0058839 | 0.011013 | -0.019703 | 0.22081 | 0.22118 | 0.21135 | 0.32683 | 0.26594 | 0.51283 | 0.046837 | 0.64665 | 0.12398 | 0.23211 | 1.6091 | 1.8039 | 1.6698 | 0.49978 | 118.6488 | -2.4609 | 118.8228 | 118.8133 | 0.16451 | -2.5218 | -2.2749 | 119.1018 | -1.1786 | 119.2486 | 118.8341 | -0.26767 | -0.98384 | -1.118 | 118.9288 | 118.8679 | 119.1148 | 118.8232 | -2.7409 | 120.2111 | 120.4059 | 120.2718 | 118.726 | -2.288
3070.9531 | 121.3898 | -120.3232 | 0.99335 | 1.4211e-13 | -0.01491 | -0.013077 | -0.045598 | -0.041711 | -0.011924 | -0.00083919 | 1.8781 | 0.012798 | 0.32442 | 0.011013 | -0.02013 | 0.088037 | 0.092979 | 0.074 | 0.19406 | 0.15604 | 0.38005 | 0.10636 | 0.15672 | 0.1194 | 0.003172 | 0.55609 | 0.72797 | 0.54345 | -0.15957 | 120.4295 | -0.79929 | 120.4112 | 120.3972 | -0.032363 | -0.8373 | -0.61329 | 120.1636 | -0.43725 | 120.4799 | 120.3264 | 0.16274 | -0.26538 | -0.4499 | 120.5172 | 120.4792 | 120.7032 | 120.4162 | -0.88698 | 120.8793 | 121.0511 | 120.8666 | 120.4426 | -1.1529
3072.75 | 121.6507 | -120.6665 | 0.70953 | 1.4211e-13 | -0.015124 | -0.013291 | -0.045384 | -0.041711 | -0.012138 | -0.00083919 | 1.4401 | 0.009807 | 0.15606 | 0.011013 | -0.019703 | 0.069723 | 0.074664 | 0.055687 | 0.18032 | 0.14688 | 0.36174 | 0.10178 | 0.088043 | 0.11483 | 0.003172 | 0.43705 | 0.6135 | 0.43356 | -0.18246 | 120.7683 | -0.52921 | 120.7362 | 120.7222 | -0.046097 | -0.56265 | -0.3478 | 120.484 | -0.27248 | 120.7545 | 120.6697 | 0.18564 | -0.096031 | -0.27597 | 120.8468 | 120.8134 | 121.0282 | 120.7412 | -0.60775 | 121.1036 | 121.28 | 121.1001 | 120.7813 | -0.892
3074.4844 | 121.5866 | -121.5408 | 0.10529 | 1.4211e-13 | -0.015337 | -0.013718 | -0.04517 | -0.041711 | -0.011924 | -0.00083919 | 0.082693 | 0.0089522 | -0.027035 | 0.011226 | -0.019489 | 0.010204 | 0.015142 | 0.005325 | 0.11622 | 0.096516 | 0.3068 | -0.081373 | 0.014784 | 0.082776 | -0.070087 | 0.024988 | 0.19227 | -0.060928 | -0.28778 | 121.4595 | 0.010939 | 121.551 | 121.5462 | 0.086698 | -0.00877 | 0.20151 | 121.2531 | -0.080298 | 121.5556 | 121.4707 | 0.21769 | 0.086986 | -0.16621 | 121.6571 | 121.6373 | 121.8476 | 121.556 | -0.18666 | 121.5658 | 121.7331 | 121.4799 | 121.6236 | -0.39306
3076.2656 | 121.8109 | -121.5317 | 0.091553 | 1.4211e-13 | -0.015551 | -0.013291 | -0.04517 | -0.041498 | -0.012138 | -0.00083919 | 0.09722 | 0.0083114 | -0.016139 | 0.01144 | -0.02013 | 0.005626 | 0.019721 | 0.005325 | 0.11622 | 0.096516 | 0.3068 | 0.001048 | 0.014784 | 0.082776 | -0.065509 | 0.038723 | 0.20143 | -0.038035 | -0.29236 | 121.5327 | 0.024672 | 121.5373 | 121.537 | 0.004277 | 0.004963 | 0.21524 | 121.2393 | -0.05283 | 121.5465 | 121.4662 | 0.22685 | 0.10988 | -0.12959 | 121.6479 | 121.6282 | 121.8385 | 121.5514 | -0.090505 | 121.5704 | 121.7331 | 121.4936 | 121.6145 | -0.38391
3078 | 121.7651 | -121.4218 | 0.2243 | 1.4211e-13 | -0.015765 | -0.013718 | -0.04517 | -0.041711 | -0.011924 | -0.00083919 | 0.2034 | 0.0087386 | 0.021036 | 0.011226 | -0.019703 | 0.019361 | 0.028878 | 0.009904 | 0.1208 | 0.096516 | 0.31137 | 0.001048 | 0.02852 | 0.082776 | -0.051772 | 0.075351 | 0.23348 | 0.044379 | -0.27862 | 121.4229 | -0.1035 | 121.4412 | 121.4317 | 0.008856 | -0.12779 | 0.08707 | 121.1432 | -0.14895 | 121.4503 | 121.37 | 0.22685 | 0.009175 | -0.17993 | 121.5426 | 121.5183 | 121.7332 | 121.4507 | -0.22326 | 121.4972 | 121.6553 | 121.4662 | 121.5046 | -0.50292
3079.7969 | 121.7285 | -121.6232 | 0.14191 | 1.4211e-13 | -0.015124 | -0.013505 | -0.04517 | -0.041498 | -0.011924 | 0.0067908 | 0.038042 | 0.008525 | -0.028103 | 0.01144 | -0.019917 | 0.001048 | 0.015142 | 0.000747 | 0.1208 | 0.091937 | 0.3068 | 0.023942 | 0.014784 | 0.078197 | -0.074666 | 0.020409 | 0.18769 | -0.0884 | -0.29236 | 121.6472 | -0.021103 | 121.6243 | 121.624 | -0.023195 | -0.04997 | 0.16489 | 121.3309 | -0.1215 | 121.638 | 121.5486 | 0.21769 | 0.045786 | -0.23031 | 121.744 | 121.7152 | 121.93 | 121.6384 | -0.11797 | 121.6436 | 121.8109 | 121.5348 | 121.7014 | -0.43426
3081.5938 | 121.907 | -121.756 | 0.13733 | 1.4211e-13 | -0.015765 | -0.013077 | -0.044743 | -0.041498 | -0.011924 | -0.00083919 | 0.024797 | 0.0083114 | -0.030881 | 0.01144 | -0.019489 | -0.003531 | 0.015142 | -0.003831 | 0.10707 | 0.096516 | 0.30222 | 0.005627 | 0.010205 | 0.078197 | -0.074666 | 0.020409 | 0.18311 | -0.12045 | -0.29236 | 121.7616 | -0.030261 | 121.7525 | 121.7522 | -0.009458 | -0.040813 | 0.16489 | 121.4636 | -0.11692 | 121.7662 | 121.6813 | 0.21769 | 0.045786 | -0.25778 | 121.863 | 121.8525 | 122.0582 | 121.7711 | -0.1317 | 121.7764 | 121.9391 | 121.6355 | 121.8342 | -0.42968
3083.375 | 121.907 | -121.5637 | 0.1236 | 1.4211e-13 | -0.015551 | -0.013291 | -0.044957 | -0.041498 | -0.011924 | -0.00083919 | 0.094443 | 0.008525 | -0.012934 | 0.011226 | -0.019917 | 0.010204 | 0.0243 | 0.000747 | 0.1208 | 0.087359 | 0.30222 | 0.014784 | 0.014784 | 0.087354 | -0.065509 | 0.038723 | 0.20143 | 0.012329 | -0.29236 | 121.5785 | -0.002792 | 121.5739 | 121.5645 | -0.014037 | -0.036237 | 0.17862 | 121.2714 | -0.084873 | 121.5785 | 121.4982 | 0.22685 | 0.077833 | -0.11127 | 121.6845 | 121.6511 | 121.8659 | 121.588 | -0.10881 | 121.6024 | 121.7652 | 121.576 | 121.6511 | -0.41595
3085.1562 | 121.6003 | -121.3028 | 0.13275 | 1.4211e-13 | -0.015337 | -0.013291 | -0.04517 | -0.041498 | -0.011924 | -0.0161 | 0.17392 | 0.0080976 | 9.828e-05 | 0.01144 | -0.019703 | 0.014783 | 0.028878 | 0.005325 | 0.11622 | 0.096516 | 0.31595 | 0.005627 | 0.042256 | 0.087354 | -0.070087 | 0.066194 | 0.23348 | 0.071851 | -0.27862 | 121.3084 | -0.016526 | 121.3176 | 121.3081 | -0.000302 | -0.036235 | 0.1832 | 121.0242 | -0.066557 | 121.3451 | 121.2327 | 0.20853 | 0.10073 | -0.0609 | 121.419 | 121.3993 | 121.6187 | 121.3317 | -0.12712 | 121.369 | 121.5363 | 121.3746 | 121.3901 | -0.41137
3086.8906 | 118.3273 | -118.2953 | 0.21057 | 1.4211e-13 | -0.015337 | -0.013291 | -0.045384 | -0.04107 | -0.012352 | -0.00083919 | 0.12777 | 0.008525 | -0.016353 | 0.01144 | -0.019703 | 0.010204 | 0.028878 | 0.005325 | 0.12538 | 0.091937 | 0.31137 | 0.001048 | 0.02852 | 0.087354 | -0.074666 | 0.061616 | 0.22432 | 0.030644 | -0.27862 | 118.2963 | -0.085189 | 118.3055 | 118.3006 | 0.004277 | -0.11863 | 0.1008 | 118.0167 | -0.14896 | 118.3238 | 118.2206 | 0.20395 | 0.013751 | -0.17993 | 118.4207 | 118.3872 | 118.6067 | 118.3242 | -0.20952 | 118.3569 | 118.5196 | 118.3259 | 118.3826 | -0.48919
3088.6875 | 121.5134 | -120.726 | 0.55847 | 1.4211e-13 | -0.015124 | -0.013077 | -0.045384 | -0.041498 | -0.012138 | -0.0084697 | 0.91567 | 0.0089522 | 0.14217 | 0.01144 | -0.019489 | 0.05141 | 0.070086 | 0.041952 | 0.15743 | 0.12857 | 0.348 | 0.10636 | 0.17504 | 0.13772 | -0.028879 | 0.35006 | 0.53109 | 0.4244 | -0.15499 | 120.8324 | -0.40104 | 120.7774 | 120.768 | -0.064411 | -0.4299 | -0.21047 | 120.571 | -0.20841 | 120.9011 | 120.6971 | 0.12611 | -0.027383 | -0.13407 | 120.8834 | 120.8546 | 121.074 | 120.7961 | -0.45211 | 121.0761 | 121.2571 | 121.1504 | 120.8637 | -0.71346
3090.4062 | 121.3257 | -120.7031 | 0.39825 | 1.4211e-13 | -0.015337 | -0.013291 | -0.045598 | -0.041284 | -0.012352 | -0.00083919 | 0.73173 | 0.0087386 | 0.13854 | 0.011654 | -0.019703 | 0.033096 | 0.051771 | 0.037373 | 0.15285 | 0.12857 | 0.33427 | 0.11094 | 0.14299 | 0.12856 | -0.038036 | 0.29512 | 0.46241 | 0.3603 | -0.17331 | 120.8141 | -0.2454 | 120.7362 | 120.7405 | -0.073569 | -0.26969 | -0.063987 | 120.5298 | -0.10313 | 120.8461 | 120.6651 | 0.13527 | 0.064156 | -0.037951 | 120.856 | 120.8317 | 121.0374 | 120.7549 | -0.28731 | 120.9982 | 121.1655 | 121.0634 | 120.8317 | -0.57156
3092.1875 | 121.138 | -120.8679 | 0.2243 | 1.4211e-13 | -0.015337 | -0.013505 | -0.04517 | -0.041711 | -0.011924 | -0.00083919 | 0.27475 | 0.0087386 | 0.036205 | 0.011867 | -0.019703 | 0.014783 | 0.038035 | 0.009904 | 0.12996 | 0.1011 | 0.31137 | 0.019363 | 0.060571 | 0.096512 | -0.06093 | 0.11198 | 0.27469 | 0.094744 | -0.25115 | 120.8873 | -0.094344 | 120.8827 | 120.8778 | -0.009459 | -0.12321 | 0.08707 | 120.6168 | -0.11233 | 120.9285 | 120.807 | 0.19022 | 0.050383 | -0.12956 | 120.9979 | 120.969 | 121.1793 | 120.906 | -0.20494 | 120.9799 | 121.1426 | 120.9627 | 120.9644 | -0.47545
3093.9844 | 121.4447 | -121.2799 | 0.11444 | 1.4211e-13 | -0.015551 | -0.013505 | -0.04517 | -0.041711 | -0.011924 | -0.00083919 | 0.027574 | 0.008525 | -0.031522 | 0.01144 | -0.019489 | 0.005626 | 0.019721 | 0.000747 | 0.11165 | 0.087359 | 0.30222 | 0.010206 | 0.02852 | 0.073618 | -0.070087 | 0.020409 | 0.18311 | -0.10671 | -0.29693 | 121.2901 | -0.002794 | 121.2855 | 121.2807 | -0.009459 | -0.027082 | 0.18778 | 120.983 | -0.094032 | 121.3084 | 121.2098 | 0.22685 | 0.068674 | -0.22115 | 121.3916 | 121.3673 | 121.5821 | 121.2996 | -0.10423 | 121.3003 | 121.463 | 121.1732 | 121.3535 | -0.41137
3095.7188 | 121.2524 | -120.9641 | 0.09613 | 1.4211e-13 | -0.015337 | -0.013291 | -0.04517 | -0.041711 | -0.012138 | 0.0067908 | 0.16153 | 0.0083114 | 0.0069351 | 0.011226 | -0.019703 | 0.010204 | 0.028878 | 0.009904 | 0.12996 | 0.087359 | 0.29764 | -0.003531 | 0.023941 | 0.087354 | -0.065509 | 0.052459 | 0.2289 | 0.090166 | -0.26946 | 120.9605 | 0.03383 | 120.9743 | 120.974 | 0.013435 | -0.008771 | 0.20151 | 120.6946 | -0.043671 | 120.988 | 120.8985 | 0.20395 | 0.13277 | -0.005964 | 121.094 | 121.0514 | 121.2617 | 120.9929 | -0.099661 | 121.0165 | 121.193 | 121.0542 | 121.0514 | -0.36559
3097.5156 | 121.0007 | -120.845 | 0.14191 | 1.4211e-13 | -0.015551 | -0.012863 | -0.044957 | -0.041711 | -0.011924 | -0.00083919 | 0.033983 | 0.0080976 | -0.028103 | 0.01144 | -0.019489 | 0.001048 | 0.015142 | 0.005325 | 0.11622 | 0.08278 | 0.3068 | -0.017268 | 0.014784 | 0.073618 | -0.070087 | 0.024988 | 0.18769 | -0.12045 | -0.29693 | 120.8278 | -0.025682 | 120.8461 | 120.8504 | 0.022593 | -0.059127 | 0.16489 | 120.5481 | -0.11692 | 120.8598 | 120.7749 | 0.22685 | 0.045786 | -0.26236 | 120.9613 | 120.9278 | 121.1518 | 120.8602 | -0.15918 | 120.87 | 121.0327 | 120.7246 | 120.9186 | -0.43884
3099.25 | 121.2708 | -121.0968 | 0.12817 | 1.4211e-13 | -0.015551 | -0.013291 | -0.04517 | -0.041498 | -0.011924 | 0.0067908 | 0.020524 | 0.0083114 | -0.032376 | 0.011654 | -0.02013 | -0.003531 | 0.015142 | -0.003831 | 0.1208 | 0.08278 | 0.30222 | 0.019363 | 0.019362 | 0.078197 | -0.074666 | 0.011252 | 0.17854 | -0.12045 | -0.30151 | 121.1162 | -0.00737 | 121.0933 | 121.093 | -0.023194 | -0.045394 | 0.17404 | 120.7953 | -0.11692 | 121.1162 | 121.0221 | 0.22685 | 0.050362 | -0.24862 | 121.2176 | 121.1796 | 121.399 | 121.1119 | -0.10881 | 121.1081 | 121.2753 | 120.9764 | 121.175 | -0.42969
3101.0312 | 121.4905 | -121.3303 | 0.09613 | 1.4211e-13 | -0.015337 | -0.013718 | -0.044957 | -0.041284 | -0.011711 | -0.0084697 | 0.020097 | 0.008525 | -0.032804 | 0.01144 | -0.019917 | 0.005626 | 0.010564 | 0.000747 | 0.12538 | 0.096516 | 0.30222 | 0.010206 | 0.014784 | 0.078197 | -0.070087 | 0.006674 | 0.17396 | -0.12045 | -0.29693 | 121.3405 | 0.029252 | 121.3359 | 121.331 | -0.009459 | 0.000386 | 0.20609 | 121.0333 | -0.089456 | 121.345 | 121.2602 | 0.22685 | 0.077828 | -0.21658 | 121.4556 | 121.4268 | 121.6325 | 121.3408 | -0.085924 | 121.3369 | 121.5042 | 121.2098 | 121.4085 | -0.39306
3102.8281 | 121.5134 | -121.3898 | 0.11902 | 1.4211e-13 | -0.015551 | -0.013291 | -0.045384 | -0.041498 | -0.012138 | -0.00083919 | 0.020738 | 0.0087386 | -0.032376 | 0.01144 | -0.02013 | 0.010204 | 0.019721 | -0.008409 | 0.11165 | 0.091937 | 0.3068 | 0.010206 | 0.023941 | 0.082776 | -0.074666 | 0.011252 | 0.17854 | -0.11129 | -0.29236 | 121.4 | -0.007372 | 121.4 | 121.3814 | -0.018615 | -0.027082 | 0.18778 | 121.0974 | -0.10777 | 121.4137 | 121.3151 | 0.21769 | 0.059517 | -0.23031 | 121.5014 | 121.4817 | 121.6966 | 121.4095 | -0.10881 | 121.401 | 121.5683 | 121.2785 | 121.4725 | -0.41137
3104.5469 | 121.7285 | -121.3852 | 0.091553 | 1.4211e-13 | -0.015765 | -0.013077 | -0.045384 | -0.041498 | -0.012138 | 0.0067908 | 0.020097 | 0.0089522 | -0.032163 | 0.01144 | -0.019703 | 0.001048 | 0.019721 | 0.000747 | 0.11165 | 0.087359 | 0.3068 | 0.010206 | 0.023941 | 0.073618 | -0.074666 | 0.006674 | 0.17396 | -0.11587 | -0.30151 | 121.3954 | 0.020094 | 121.3862 | 121.3859 | -0.009459 | -0.004194 | 0.21524 | 121.0837 | -0.084879 | 121.4091 | 121.3105 | 0.22685 | 0.082405 | -0.20742 | 121.4968 | 121.4726 | 121.692 | 121.4049 | -0.081347 | 121.3919 | 121.5592 | 121.2693 | 121.4588 | -0.39307
3106.3281 | 121.7514 | -121.4172 | 0.086975 | 1.4211e-13 | -0.015765 | -0.013291 | -0.04517 | -0.041711 | -0.012138 | -0.0161 | 0.020097 | 0.0093796 | -0.03259 | 0.01144 | -0.019703 | 0.010204 | 0.015142 | -0.003831 | 0.11622 | 0.087359 | 0.29764 | 0.005627 | 0.010205 | 0.087354 | -0.079245 | 0.015831 | 0.17854 | -0.11129 | -0.29236 | 121.4229 | 0.02925 | 121.4274 | 121.4134 | -0.009458 | 0.000384 | 0.21066 | 121.1249 | -0.071144 | 121.4274 | 121.338 | 0.21311 | 0.091561 | -0.19827 | 121.5335 | 121.5046 | 121.7149 | 121.4324 | -0.081348 | 121.4331 | 121.5958 | 121.3059 | 121.5046 | -0.37933
3108.1094 | 121.7514 | -121.4447 | 0.07782 | 1.4211e-13 | -0.015765 | -0.013505 | -0.044957 | -0.041711 | -0.011924 | -0.00083919 | 0.020311 | 0.0095932 | -0.032376 | 0.011226 | -0.019703 | 0.001048 | 0.0243 | 0.000747 | 0.11622 | 0.091937 | 0.30222 | 0.010206 | 0.014784 | 0.082776 | -0.074666 | 0.015831 | 0.17854 | -0.12045 | -0.30151 | 121.4549 | 0.038405 | 121.4458 | 121.4454 | -0.009459 | 0.014117 | 0.2244 | 121.1432 | -0.061989 | 121.4595 | 121.37 | 0.22685 | 0.10072 | -0.19827 | 121.5609 | 121.5366 | 121.7469 | 121.469 | -0.067614 | 121.4605 | 121.6232 | 121.3243 | 121.5275 | -0.37933
3109.9062 | 121.7194 | -121.5271 | 0.1236 | 1.4211e-13 | -0.015551 | -0.013291 | -0.04517 | -0.041498 | -0.011497 | -0.00083919 | 0.020951 | 0.0093796 | -0.032163 | 0.011226 | -0.019703 | 0.005626 | 0.019721 | -0.003831 | 0.1208 | 0.087359 | 0.30222 | 0.010206 | 0.019362 | 0.073618 | -0.074666 | 0.015831 | 0.16938 | -0.11587 | -0.29693 | 121.5373 | -0.002792 | 121.5327 | 121.5233 | -0.014037 | -0.036237 | 0.17862 | 121.2302 | -0.10776 | 121.5465 | 121.4524 | 0.22227 | 0.045783 | -0.23947 | 121.6479 | 121.6145 | 121.8293 | 121.5468 | -0.11339 | 121.5429 | 121.6965 | 121.4112 | 121.6007 | -0.42053
3111.6875 | 121.6965 | -121.5546 | 0.12817 | 1.4211e-13 | -0.015765 | -0.013077 | -0.04517 | -0.041498 | -0.012138 | 0.0067908 | 0.020951 | 0.009166 | -0.031522 | 0.011226 | -0.019489 | -0.003531 | 0.015142 | -0.003831 | 0.11622 | 0.08278 | 0.30222 | 0.019363 | 0.023941 | 0.078197 | -0.074666 | 0.015831 | 0.18311 | -0.12045 | -0.29236 | 121.5739 | -0.011949 | 121.551 | 121.5507 | -0.023194 | -0.045394 | 0.17404 | 121.2622 | -0.11234 | 121.5785 | 121.4799 | 0.21769 | 0.054941 | -0.24862 | 121.6708 | 121.6373 | 121.8568 | 121.5697 | -0.10881 | 121.5704 | 121.7377 | 121.4341 | 121.6328 | -0.42053
3113.4062 | 121.7606 | -121.5546 | 0.13275 | 1.4211e-13 | -0.015551 | -0.013291 | -0.044743 | -0.041925 | -0.011924 | 0.0067908 | 0.020738 | 0.009166 | -0.031522 | 0.011867 | -0.019917 | 0.005626 | 0.019721 | -0.003831 | 0.11165 | 0.08278 | 0.29306 | 0.014784 | 0.010205 | 0.073618 | -0.074666 | 0.011252 | 0.17854 | -0.12045 | -0.28778 | 121.5693 | -0.021104 | 121.5602 | 121.5507 | -0.018615 | -0.049971 | 0.16031 | 121.2668 | -0.1215 | 121.5648 | 121.4799 | 0.21311 | 0.045785 | -0.2532 | 121.6662 | 121.6373 | 121.8476 | 121.5743 | -0.11797 | 121.5658 | 121.7331 | 121.4341 | 121.6282 | -0.42053
3115.1875 | 121.7789 | -121.582 | 0.09613 | 1.4211e-13 | -0.015765 | -0.013077 | -0.044957 | -0.041498 | -0.011924 | -0.00083919 | 0.019883 | 0.010234 | -0.030881 | 0.011654 | -0.019703 | -0.003531 | 0.019721 | 0.000747 | 0.11622 | 0.08278 | 0.28848 | 0.014784 | 0.019362 | 0.078197 | -0.079245 | 0.002095 | 0.17854 | -0.12045 | -0.28778 | 121.5968 | 0.020095 | 121.5785 | 121.5828 | -0.014037 | -0.01335 | 0.19235 | 121.2943 | -0.094035 | 121.6014 | 121.5028 | 0.20853 | 0.082406 | -0.21658 | 121.6983 | 121.6648 | 121.8705 | 121.6018 | -0.081346 | 121.5841 | 121.7606 | 121.4616 | 121.6602 | -0.38391
3116.9531 | 121.7972 | -121.6187 | 0.12817 | 1.4211e-13 | -0.015337 | -0.013505 | -0.04517 | -0.041711 | -0.011711 | -0.0084697 | 0.019456 | 0.010234 | -0.031308 | 0.011654 | -0.019703 | 0.001048 | 0.010564 | -0.003831 | 0.11165 | 0.087359 | 0.29764 | 0.014784 | 0.019362 | 0.078197 | -0.079245 | 0.015831 | 0.17396 | -0.12045 | -0.29693 | 121.6334 | -0.016527 | 121.6197 | 121.6148 | -0.018615 | -0.040815 | 0.16946 | 121.3217 | -0.11234 | 121.638 | 121.5394 | 0.21769 | 0.045784 | -0.24862 | 121.7303 | 121.706 | 121.9163 | 121.6292 | -0.11339 | 121.6345 | 121.7926 | 121.4982 | 121.6968 | -0.42511
3118.7344 | 121.7834 | -121.6278 | 0.11902 | 1.4211e-13 | -0.015551 | -0.013077 | -0.044957 | -0.041498 | -0.012138 | 0.0067908 | 0.019456 | 0.009807 | -0.031094 | 0.011654 | -0.019703 | 0.001048 | 0.015142 | 0.000747 | 0.11165 | 0.091937 | 0.30222 | 0.010206 | 0.023941 | 0.073618 | -0.070087 | 0.011252 | 0.18769 | -0.12045 | -0.29236 | 121.638 | -0.007372 | 121.6289 | 121.6286 | -0.009459 | -0.027082 | 0.1832 | 121.3355 | -0.10777 | 121.6517 | 121.5577 | 0.22227 | 0.068674 | -0.23947 | 121.7395 | 121.7197 | 121.93 | 121.6429 | -0.10881 | 121.6391 | 121.8155 | 121.5074 | 121.7014 | -0.41137
3120.5312 | 121.788 | -121.6599 | 0.14648 | 1.4211e-13 | -0.015551 | -0.013291 | -0.04517 | -0.041711 | -0.012138 | -0.00083919 | 0.019883 | 0.0095932 | -0.031522 | 0.01144 | -0.019917 | 0.001048 | 0.015142 | -0.003831 | 0.1208 | 0.087359 | 0.3068 | 0.014784 | 0.019362 | 0.073618 | -0.083823 | 0.006674 | 0.17396 | -0.12045 | -0.29693 | 121.6746 | -0.02568 | 121.6609 | 121.656 | -0.018615 | -0.059125 | 0.16031 | 121.3629 | -0.13981 | 121.6792 | 121.576 | 0.21311 | 0.027474 | -0.26693 | 121.7807 | 121.7472 | 121.9666 | 121.675 | -0.1317 | 121.6665 | 121.8338 | 121.5394 | 121.7335 | -0.44342
3122.2656 | 121.9299 | -121.6049 | 0.086975 | 1.4211e-13 | -0.015551 | -0.013505 | -0.044957 | -0.041498 | -0.011924 | 0.0067908 | 0.020097 | 0.010021 | -0.031522 | 0.011867 | -0.019703 | -0.008109 | 0.010564 | 0.009904 | 0.11622 | 0.091937 | 0.29764 | 0.010206 | 0.019362 | 0.073618 | -0.079245 | 0.006674 | 0.17396 | -0.11587 | -0.29693 | 121.6151 | 0.02925 | 121.5968 | 121.6148 | -0.000302 | 0.004962 | 0.21066 | 121.308 | -0.080301 | 121.6243 | 121.5257 | 0.21769 | 0.086983 | -0.20285 | 121.7211 | 121.6969 | 121.9026 | 121.6155 | -0.076769 | 121.6116 | 121.7789 | 121.489 | 121.6785 | -0.38391
3124.0469 | 121.8842 | -121.6507 | 0.10986 | 1.4211e-13 | -0.015551 | -0.013505 | -0.04517 | -0.041711 | -0.012138 | -0.0084697 | 0.020738 | 0.010662 | -0.031735 | 0.011654 | -0.019917 | 0.005626 | 0.019721 | -0.003831 | 0.11622 | 0.091937 | 0.30222 | 0.014784 | 0.014784 | 0.078197 | -0.079245 | 0.011252 | 0.17854 | -0.11587 | -0.29236 | 121.6655 | 0.006362 | 121.6563 | 121.6469 | -0.018615 | -0.017926 | 0.19235 | 121.3583 | -0.098611 | 121.6655 | 121.5715 | 0.21311 | 0.068673 | -0.22574 | 121.7669 | 121.7426 | 121.9529 | 121.6704 | -0.095079 | 121.6619 | 121.8292 | 121.5348 | 121.7289 | -0.40222
3125.8281 | 121.8246 | -121.7102 | 0.1236 | 1.4211e-13 | -0.015765 | -0.013291 | -0.04517 | -0.041711 | -0.012138 | 0.014421 | 0.020524 | 0.010875 | -0.031735 | 0.011226 | -0.019703 | 0.005626 | 0.019721 | -0.003831 | 0.11622 | 0.091937 | 0.29764 | 0.010206 | 0.023941 | 0.073618 | -0.074666 | 0.011252 | 0.16938 | -0.074664 | -0.29693 | 121.7204 | -0.007371 | 121.7158 | 121.7064 | -0.014037 | -0.031659 | 0.17404 | 121.4133 | -0.11234 | 121.7341 | 121.6355 | 0.22227 | 0.045783 | -0.19826 | 121.8264 | 121.8021 | 122.0078 | 121.7299 | -0.11339 | 121.7215 | 121.8796 | 121.6355 | 121.7838 | -0.42053
3127.6094 | 121.9299 | -121.6736 | 0.10986 | 1.4211e-13 | -0.015978 | -0.013718 | -0.044957 | -0.041498 | -0.012138 | -0.0084697 | 0.020311 | 0.010234 | -0.031094 | 0.01144 | -0.019703 | 0.005626 | 0.015142 | 0.005325 | 0.1208 | 0.087359 | 0.29764 | 0.010206 | 0.014784 | 0.082776 | -0.070087 | 0.011252 | 0.18769 | -0.092979 | -0.29236 | 121.6838 | 0.010941 | 121.6792 | 121.6789 | -0.004881 | -0.022504 | 0.18778 | 121.3812 | -0.098611 | 121.6884 | 121.6035 | 0.22227 | 0.07783 | -0.20284 | 121.7944 | 121.7609 | 121.9712 | 121.6887 | -0.099657 | 121.6848 | 121.8613 | 121.5806 | 121.7564 | -0.40222
3129.4062 | 121.9849 | -121.6782 | 0.09613 | 1.4211e-13 | -0.015765 | -0.013291 | -0.044957 | -0.041498 | -0.012565 | -0.0084697 | 0.020311 | 0.010448 | -0.031522 | 0.011654 | -0.019703 | 0.005626 | 0.019721 | -0.003831 | 0.11165 | 0.087359 | 0.30222 | 0.010206 | 0.019362 | 0.073618 | -0.074666 | 0.011252 | 0.17854 | -0.11587 | -0.28778 | 121.6884 | 0.015517 | 121.6838 | 121.6743 | -0.014037 | -0.008771 | 0.20609 | 121.3904 | -0.084878 | 121.6975 | 121.6035 | 0.21311 | 0.082406 | -0.212 | 121.7898 | 121.7655 | 121.9804 | 121.6979 | -0.085924 | 121.6894 | 121.8567 | 121.5623 | 121.7518 | -0.38391
3131.1875 | 121.8567 | -121.7148 | 0.11902 | 1.4211e-13 | -0.015551 | -0.013505 | -0.045384 | -0.041711 | -0.012138 | -0.0161 | 0.020311 | 0.010234 | -0.030453 | 0.011654 | -0.019703 | 0.005626 | 0.015142 | -0.008409 | 0.11165 | 0.087359 | 0.29764 | 0.010206 | 0.014784 | 0.078197 | -0.074666 | 0.015831 | 0.17854 | -0.11587 | -0.28778 | 121.725 | -0.007372 | 121.7204 | 121.7064 | -0.018615 | -0.03166 | 0.17862 | 121.427 | -0.10319 | 121.7296 | 121.6401 | 0.21311 | 0.059517 | -0.23489 | 121.8264 | 121.8021 | 122.0124 | 121.7299 | -0.10881 | 121.7306 | 121.8933 | 121.5989 | 121.793 | -0.4068
3132.9844 | 121.9711 | -121.7285 | 0.10071 | 1.4211e-13 | -0.015551 | -0.013291 | -0.04517 | -0.041925 | -0.011924 | 0.0067908 | 0.019883 | 0.010662 | -0.030881 | 0.01144 | -0.019917 | 0.010204 | 0.019721 | -0.003831 | 0.1208 | 0.091937 | 0.29306 | 0.014784 | 0.019362 | 0.078197 | -0.070087 | 0.020409 | 0.16938 | -0.11129 | -0.28778 | 121.7433 | 0.020096 | 121.7387 | 121.7247 | -0.018615 | -0.008771 | 0.19235 | 121.4407 | -0.080299 | 121.7479 | 121.6584 | 0.21769 | 0.068671 | -0.212 | 121.8493 | 121.8205 | 122.0216 | 121.7482 | -0.085924 | 121.7489 | 121.8979 | 121.6172 | 121.8067 | -0.38849
3134.7656 | 122.0444 | -121.7056 | 0.10529 | 1.4211e-13 | -0.015551 | -0.013718 | -0.044957 | -0.041925 | -0.011924 | -0.0084697 | 0.020524 | 0.010875 | -0.031949 | 0.011226 | -0.019276 | 0.001048 | 0.019721 | 0.000747 | 0.1208 | 0.091937 | 0.30222 | 0.014784 | 0.02852 | 0.073618 | -0.074666 | 0.015831 | 0.17396 | -0.11587 | -0.29693 | 121.7204 | 0.015518 | 121.7067 | 121.7064 | -0.014037 | -0.013349 | 0.19693 | 121.4087 | -0.089455 | 121.7341 | 121.631 | 0.22227 | 0.068672 | -0.22116 | 121.8264 | 121.7976 | 122.0078 | 121.7253 | -0.090502 | 121.7215 | 121.8796 | 121.5898 | 121.7792 | -0.40222
3136.4844 | 121.9345 | -121.7606 | 0.12817 | 1.4211e-13 | -0.015337 | -0.013291 | -0.04517 | -0.041711 | -0.012352 | -0.00083919 | 0.020738 | 0.010662 | -0.032804 | 0.01144 | -0.02013 | 0.010204 | 0.0243 | 0.000747 | 0.11622 | 0.087359 | 0.30222 | 0.014784 | 0.014784 | 0.078197 | -0.083823 | 0.015831 | 0.17396 | -0.12045 | -0.28778 | 121.7753 | -0.011949 | 121.7708 | 121.7613 | -0.014037 | -0.040815 | 0.17404 | 121.4728 | -0.11234 | 121.7753 | 121.6767 | 0.20395 | 0.045784 | -0.24862 | 121.8768 | 121.8479 | 122.0628 | 121.7849 | -0.11339 | 121.7764 | 121.9345 | 121.6401 | 121.8388 | -0.41595
3138.2656 | 121.9299 | -121.7743 | 0.1236 | 1.4211e-13 | -0.015765 | -0.013718 | -0.044957 | -0.041711 | -0.011924 | -0.00083919 | 0.020524 | 0.011516 | -0.032163 | 0.012081 | -0.019917 | 0.005626 | 0.019721 | -0.003831 | 0.1208 | 0.087359 | 0.30222 | 0.014784 | 0.023941 | 0.078197 | -0.074666 | 0.015831 | 0.17854 | -0.11587 | -0.29236 | 121.7891 | -0.002792 | 121.7799 | 121.7705 | -0.018615 | -0.036237 | 0.17862 | 121.4819 | -0.10776 | 121.7982 | 121.6996 | 0.21769 | 0.05494 | -0.23947 | 121.8951 | 121.8617 | 122.0765 | 121.794 | -0.10881 | 121.7901 | 121.9528 | 121.6584 | 121.8525 | -0.41595
3140 | 121.9391 | -121.8018 | 0.11444 | 1.4211e-13 | -0.015765 | -0.013077 | -0.04517 | -0.041711 | -0.012352 | 0.014421 | 0.020097 | 0.011303 | -0.031949 | 0.011867 | -0.02013 | 0.014783 | 0.019721 | 0.000747 | 0.1208 | 0.087359 | 0.29764 | 0.014784 | 0.023941 | 0.087354 | -0.074666 | 0.011252 | 0.17396 | -0.11587 | -0.28778 | 121.8165 | 0.006363 | 121.8165 | 121.8025 | -0.014037 | -0.027082 | 0.1832 | 121.514 | -0.10319 | 121.8257 | 121.7271 | 0.21311 | 0.059517 | -0.23031 | 121.9226 | 121.8891 | 122.0994 | 121.8215 | -0.099657 | 121.813 | 121.9757 | 121.6859 | 121.8891 | -0.40222
3141.7812 | 122.0398 | -121.7697 | 0.082397 | 1.4211e-13 | -0.015978 | -0.013291 | -0.044957 | -0.041498 | -0.012352 | -0.0084697 | 0.020951 | 0.01173 | -0.03259 | 0.011654 | -0.019917 | 0.001048 | 0.0243 | 0.005325 | 0.1208 | 0.087359 | 0.30222 | 0.014784 | 0.023941 | 0.082776 | -0.074666 | 0.011252 | 0.17396 | -0.11587 | -0.2832 | 121.7845 | 0.038407 | 121.7708 | 121.775 | -0.009459 | 0.004962 | 0.21982 | 121.4865 | -0.071145 | 121.7937 | 121.695 | 0.20853 | 0.091561 | -0.19827 | 121.8905 | 121.8571 | 122.0719 | 121.794 | -0.067613 | 121.781 | 121.9437 | 121.6538 | 121.8525 | -0.3656
3143.5625 | 122.0627 | -121.7606 | 0.09613 | 1.4211e-13 | -0.015551 | -0.013077 | -0.044957 | -0.042139 | -0.011924 | -0.00083919 | 0.021806 | 0.011944 | -0.033445 | 0.011867 | -0.019703 | 0.001048 | 0.019721 | 0.000747 | 0.11165 | 0.087359 | 0.29764 | 0.014784 | 0.033099 | 0.082776 | -0.079245 | 0.015831 | 0.16938 | -0.12045 | -0.28778 | 121.7753 | 0.015517 | 121.7616 | 121.7613 | -0.014037 | -0.008771 | 0.20151 | 121.4728 | -0.080299 | 121.7937 | 121.6813 | 0.20853 | 0.073249 | -0.21658 | 121.8722 | 121.8479 | 122.0582 | 121.7803 | -0.081346 | 121.7764 | 121.9299 | 121.6401 | 121.8433 | -0.38391
3145.2969 | 122.0306 | -121.7834 | 0.10529 | 1.4211e-13 | -0.015551 | -0.013077 | -0.04517 | -0.041925 | -0.011924 | -0.0084697 | 0.022874 | 0.01173 | -0.034299 | 0.011654 | -0.02013 | 0.005626 | 0.019721 | 0.000747 | 0.11165 | 0.087359 | 0.29306 | 0.010206 | 0.023941 | 0.082776 | -0.074666 | 0.015831 | 0.17854 | -0.11129 | -0.28778 | 121.7937 | 0.006361 | 121.7891 | 121.7842 | -0.009459 | -0.017927 | 0.18777 | 121.4957 | -0.089455 | 121.8074 | 121.7088 | 0.21311 | 0.07325 | -0.21658 | 121.8951 | 121.8708 | 122.0765 | 121.8032 | -0.09508 | 121.7993 | 121.962 | 121.6722 | 121.8662 | -0.39306
3147.0938 | 122.081 | -121.7789 | 0.086975 | 1.4211e-13 | -0.015765 | -0.013505 | -0.044743 | -0.042139 | -0.012138 | -0.0084697 | 0.023088 | 0.011944 | -0.034513 | 0.011654 | -0.019917 | 0.001048 | 0.019721 | -0.003831 | 0.11622 | 0.087359 | 0.30222 | 0.014784 | 0.019362 | 0.073618 | -0.074666 | 0.015831 | 0.16938 | -0.11587 | -0.29236 | 121.7937 | 0.02925 | 121.7799 | 121.775 | -0.018615 | 0.000384 | 0.21524 | 121.4865 | -0.071144 | 121.7982 | 121.7042 | 0.21769 | 0.082404 | -0.20285 | 121.8951 | 121.8662 | 122.0811 | 121.7986 | -0.072191 | 121.7947 | 121.9482 | 121.663 | 121.8525 | -0.37933
3148.9062 | 122.0993 | -121.8063 | 0.10071 | 1.4211e-13 | -0.015765 | -0.013291 | -0.044957 | -0.041711 | -0.011924 | -0.0161 | 0.023301 | 0.01173 | -0.034513 | 0.01144 | -0.019703 | 0.005626 | 0.015142 | 0.000747 | 0.11622 | 0.091937 | 0.29764 | 0.014784 | 0.019362 | 0.087354 | -0.074666 | 0.011252 | 0.16938 | -0.10214 | -0.28778 | 121.8211 | 0.015517 | 121.812 | 121.8071 | -0.014037 | -0.008771 | 0.19693 | 121.5186 | -0.089456 | 121.8257 | 121.7317 | 0.21311 | 0.068671 | -0.20284 | 121.9226 | 121.8983 | 122.104 | 121.8215 | -0.085924 | 121.8176 | 121.9757 | 121.7042 | 121.8937 | -0.38849
3150.6406 | 121.9803 | -121.843 | 0.10529 | 1.4211e-13 | -0.015551 | -0.013291 | -0.044957 | -0.041498 | -0.012138 | 0.0067908 | 0.022447 | 0.012584 | -0.034726 | 0.011867 | -0.019917 | 0.005626 | 0.010564 | -0.008409 | 0.11165 | 0.091937 | 0.29764 | 0.010206 | 0.02852 | 0.06904 | -0.070087 | 0.011252 | 0.17854 | -0.0884 | -0.29236 | 121.8532 | 0.006361 | 121.8486 | 121.8345 | -0.018615 | -0.013349 | 0.19235 | 121.5506 | -0.094034 | 121.8715 | 121.7729 | 0.22227 | 0.07325 | -0.19369 | 121.9546 | 121.9349 | 122.1406 | 121.8535 | -0.09508 | 121.8542 | 122.0215 | 121.7546 | 121.912 | -0.39764
3152.4219 | 122.0078 | -121.8796 | 0.14191 | 1.4211e-13 | -0.015978 | -0.013291 | -0.045384 | -0.041925 | -0.011711 | -0.0084697 | 0.022447 | 0.012157 | -0.034726 | 0.01144 | -0.02013 | -0.003531 | 0.010564 | 0.000747 | 0.11622 | 0.087359 | 0.30222 | 0.014784 | 0.023941 | 0.087354 | -0.079245 | 0.020409 | 0.17854 | -0.11587 | -0.28778 | 121.8944 | -0.025682 | 121.876 | 121.8803 | -0.014037 | -0.054548 | 0.16031 | 121.5918 | -0.1215 | 121.9035 | 121.8003 | 0.20853 | 0.036629 | -0.25778 | 121.9958 | 121.9669 | 122.1818 | 121.8901 | -0.12712 | 121.9 | 122.0581 | 121.7637 | 121.9669 | -0.42968
3154.2031 | 122.0856 | -121.8475 | 0.10529 | 1.4211e-13 | -0.015765 | -0.013505 | -0.044957 | -0.041498 | -0.011711 | -0.00083919 | 0.023301 | 0.01173 | -0.034299 | 0.011226 | -0.019489 | 0.005626 | 0.019721 | 0.005325 | 0.11165 | 0.091937 | 0.30222 | 0.010206 | 0.019362 | 0.082776 | -0.074666 | 0.015831 | 0.17396 | -0.10671 | -0.28778 | 121.8577 | 0.006361 | 121.8532 | 121.8529 | -0.004881 | -0.013349 | 0.19693 | 121.5598 | -0.089455 | 121.8669 | 121.7729 | 0.21311 | 0.068672 | -0.212 | 121.9592 | 121.9395 | 122.1498 | 121.8673 | -0.09508 | 121.8634 | 122.0215 | 121.7408 | 121.9303 | -0.39306
3155.9219 | 122.1588 | -121.843 | 0.09613 | 1.4211e-13 | -0.015765 | -0.013291 | -0.045384 | -0.041498 | -0.011924 | -0.00083919 | 0.022661 | 0.012157 | -0.034299 | 0.011226 | -0.019703 | 0.010204 | 0.0243 | -0.003831 | 0.11165 | 0.087359 | 0.29764 | 0.014784 | 0.023941 | 0.082776 | -0.079245 | 0.011252 | 0.17396 | -0.10671 | -0.28778 | 121.8577 | 0.015517 | 121.8532 | 121.8391 | -0.018615 | -0.008771 | 0.20151 | 121.5552 | -0.084878 | 121.8669 | 121.7637 | 0.20853 | 0.077828 | -0.20284 | 121.9546 | 121.9303 | 122.1406 | 121.8673 | -0.081346 | 121.8542 | 122.0169 | 121.7362 | 121.9257 | -0.38391
3157.7031 | 122.1405 | -121.8521 | 0.091553 | 1.4211e-13 | -0.015765 | -0.013505 | -0.04517 | -0.041711 | -0.011924 | -0.00083919 | 0.022661 | 0.012371 | -0.034726 | 0.01144 | -0.019703 | 0.005626 | 0.015142 | 0.000747 | 0.1208 | 0.08278 | 0.30222 | 0.010206 | 0.019362 | 0.078197 | -0.070087 | 0.015831 | 0.17854 | -0.11129 | -0.2832 | 121.8623 | 0.029251 | 121.8577 | 121.8529 | -0.009459 | -0.008773 | 0.21066 | 121.5689 | -0.075722 | 121.8715 | 121.782 | 0.21311 | 0.086983 | -0.20285 | 121.9729 | 121.9349 | 122.1543 | 121.8673 | -0.081347 | 121.8679 | 122.0306 | 121.7408 | 121.9303 | -0.37475
3159.4844 | 122.1542 | -121.8521 | 0.07782 | 1.4211e-13 | -0.015765 | -0.013505 | -0.044957 | -0.041498 | -0.012138 | -0.00083919 | 0.022874 | 0.012157 | -0.034299 | 0.011654 | -0.019489 | 0.001048 | 0.010564 | 0.000747 | 0.11165 | 0.091937 | 0.30222 | 0.019363 | 0.019362 | 0.082776 | -0.079245 | 0.015831 | 0.17854 | -0.10671 | -0.27862 | 121.8715 | 0.033827 | 121.8532 | 121.8529 | -0.018616 | 0.014117 | 0.2244 | 121.5735 | -0.061989 | 121.8715 | 121.7729 | 0.19937 | 0.10072 | -0.18453 | 121.9638 | 121.944 | 122.1543 | 121.8627 | -0.058457 | 121.8679 | 122.0306 | 121.7454 | 121.9349 | -0.35644
3161.2031 | 122.1268 | -121.8613 | 0.09613 | 1.4211e-13 | -0.015978 | -0.013505 | -0.044957 | -0.04107 | -0.011924 | 0.0067908 | 0.022233 | 0.012584 | -0.034086 | 0.011654 | -0.019703 | 0.005626 | 0.019721 | -0.003831 | 0.10707 | 0.087359 | 0.31137 | 0.010206 | 0.019362 | 0.082776 | -0.074666 | 0.015831 | 0.17854 | -0.092979 | -0.29236 | 121.8715 | 0.010938 | 121.8669 | 121.8574 | -0.014037 | -0.008771 | 0.21524 | 121.5689 | -0.080299 | 121.8806 | 121.7866 | 0.21769 | 0.082406 | -0.18911 | 121.9683 | 121.9486 | 122.1726 | 121.881 | -0.085924 | 121.8771 | 122.0398 | 121.7683 | 121.944 | -0.38849
3162.9844 | 122.1222 | -121.8933 | 0.068665 | 1.4211e-13 | -0.015551 | -0.013505 | -0.044957 | -0.041284 | -0.012138 | -0.00083919 | 0.021806 | 0.012371 | -0.033658 | 0.012081 | -0.019703 | 0.005626 | 0.019721 | 0.000747 | 0.1208 | 0.087359 | 0.29764 | 0.014784 | 0.023941 | 0.087354 | -0.070087 | 0.020409 | 0.17396 | -0.10214 | -0.28778 | 121.9081 | 0.052139 | 121.8989 | 121.8941 | -0.014037 | 0.018694 | 0.22897 | 121.6055 | -0.048256 | 121.9173 | 121.8232 | 0.21769 | 0.10529 | -0.1708 | 122.0141 | 121.9807 | 122.1909 | 121.913 | -0.053881 | 121.9137 | 122.0673 | 121.7912 | 121.9807 | -0.35644
3164.7812 | 122.1725 | -121.8704 | 0.091553 | 1.4211e-13 | -0.015978 | -0.013077 | -0.04517 | -0.041284 | -0.011924 | -0.0084697 | 0.021165 | 0.012584 | -0.033017 | 0.011654 | -0.02013 | 0.010204 | 0.015142 | 0.005325 | 0.1208 | 0.087359 | 0.29764 | 0.005627 | 0.023941 | 0.082776 | -0.074666 | 0.015831 | 0.16938 | -0.12045 | -0.2832 | 121.876 | 0.029251 | 121.8806 | 121.8757 | -0.000302 | -0.004194 | 0.20609 | 121.5872 | -0.075722 | 121.8944 | 121.7958 | 0.20853 | 0.077826 | -0.212 | 121.9912 | 121.9578 | 122.1681 | 121.8856 | -0.085926 | 121.8863 | 122.0398 | 121.75 | 121.9532 | -0.37475
3166.5156 | 122.2 | -121.8979 | 0.10071 | 1.4211e-13 | -0.015978 | -0.013505 | -0.04517 | -0.041711 | -0.012352 | -0.00083919 | 0.021379 | 0.012584 | -0.033445 | 0.01144 | -0.019489 | -0.003531 | 0.019721 | 0.000747 | 0.1208 | 0.091937 | 0.29764 | 0.014784 | 0.023941 | 0.078197 | -0.074666 | 0.011252 | 0.17854 | -0.12045 | -0.28778 | 121.9127 | 0.020096 | 121.8944 | 121.8986 | -0.014037 | -0.008771 | 0.19693 | 121.6101 | -0.089456 | 121.9218 | 121.8232 | 0.21311 | 0.077828 | -0.22116 | 122.0187 | 121.9898 | 122.1955 | 121.9176 | -0.085924 | 121.9091 | 122.0764 | 121.7774 | 121.9761 | -0.38849
3168.3125 | 122.1222 | -121.9254 | 0.11444 | 1.4211e-13 | -0.015978 | -0.013291 | -0.044957 | -0.041284 | -0.012138 | 0.0067908 | 0.021592 | 0.011944 | -0.033017 | 0.01144 | -0.019917 | -0.003531 | 0.0243 | 0.000747 | 0.11165 | 0.087359 | 0.30222 | 0.014784 | 0.023941 | 0.078197 | -0.079245 | 0.015831 | 0.17396 | -0.12503 | -0.27862 | 121.9401 | -0.002794 | 121.9218 | 121.9261 | -0.014037 | -0.027082 | 0.18778 | 121.6467 | -0.09861 | 121.9493 | 121.8461 | 0.19937 | 0.059517 | -0.23947 | 122.037 | 122.0127 | 122.2276 | 121.9497 | -0.099657 | 121.9412 | 122.0993 | 121.8003 | 122.0036 | -0.39306
3170.0312 | 122.1268 | -121.9345 | 0.10071 | 1.4211e-13 | -0.015551 | -0.013505 | -0.044743 | -0.041498 | -0.012138 | -0.00083919 | 0.021592 | 0.01173 | -0.033017 | 0.011654 | -0.019062 | 0.005626 | 0.019721 | 0.009904 | 0.11165 | 0.08278 | 0.30222 | 0.010206 | 0.023941 | 0.082776 | -0.074666 | 0.011252 | 0.17396 | -0.12045 | -0.2832 | 121.9447 | 0.010939 | 121.9401 | 121.9444 | -0.000302 | -0.017928 | 0.20151 | 121.6513 | -0.089456 | 121.9584 | 121.8598 | 0.20853 | 0.07325 | -0.22116 | 122.0462 | 122.0173 | 122.2367 | 121.9542 | -0.090502 | 121.9458 | 122.1085 | 121.8141 | 122.0173 | -0.38391
3171.8281 | 122.1359 | -121.9116 | 0.1236 | 1.4211e-13 | -0.015978 | -0.013932 | -0.044957 | -0.041711 | -0.012138 | -0.0084697 | 0.02202 | 0.010662 | -0.033231 | 0.012081 | -0.019062 | 0.001048 | 0.0243 | 0.009904 | 0.11622 | 0.091937 | 0.30222 | 0.014784 | 0.02852 | 0.078197 | -0.065509 | 0.020409 | 0.17854 | -0.12045 | -0.28778 | 121.9264 | -0.007371 | 121.9127 | 121.9215 | -0.00488 | -0.031659 | 0.17862 | 121.6238 | -0.10319 | 121.9401 | 121.8461 | 0.22227 | 0.05494 | -0.24405 | 122.0278 | 122.0036 | 122.2138 | 121.9359 | -0.10881 | 121.932 | 122.0902 | 121.7912 | 121.9898 | -0.41137
3173.5625 | 122.1497 | -121.9528 | 0.10986 | 1.4211e-13 | -0.015765 | -0.013505 | -0.044957 | -0.041498 | -0.011924 | -0.0084697 | 0.022447 | 0.009807 | -0.033445 | 0.012081 | -0.019276 | -0.003531 | 0.015142 | 0.005325 | 0.11622 | 0.091937 | 0.29764 | 0.019363 | 0.023941 | 0.064461 | -0.079245 | 0.011252 | 0.16938 | -0.0884 | -0.29236 | 121.9722 | 0.006362 | 121.9493 | 121.9581 | -0.014038 | -0.017926 | 0.18778 | 121.6605 | -0.098611 | 121.9768 | 121.8736 | 0.21311 | 0.059516 | -0.19826 | 122.069 | 122.0448 | 122.2505 | 121.968 | -0.0905 | 121.9641 | 122.1222 | 121.8644 | 122.0173 | -0.40222
3175.3594 | 122.1359 | -121.9849 | 0.13275 | 1.4211e-13 | -0.015978 | -0.013505 | -0.04517 | -0.041711 | -0.011924 | -0.0161 | 0.023515 | 0.0087386 | -0.033445 | 0.011867 | -0.019276 | 0.001048 | 0.019721 | 0.000747 | 0.12538 | 0.091937 | 0.30222 | 0.014784 | 0.019362 | 0.064461 | -0.074666 | 0.011252 | 0.17854 | -0.12045 | -0.2832 | 121.9996 | -0.007369 | 121.9859 | 121.9856 | -0.014037 | -0.040814 | 0.16947 | 121.7017 | -0.1215 | 122.0042 | 121.9102 | 0.20853 | 0.045785 | -0.2532 | 122.1102 | 122.0768 | 122.2871 | 122.0046 | -0.11797 | 121.9961 | 122.1634 | 121.8644 | 122.0493 | -0.41595
3177.1406 | 122.2458 | -121.9666 | 0.086975 | 1.4211e-13 | -0.015978 | -0.013505 | -0.04517 | -0.041498 | -0.012138 | -0.00083919 | 0.023301 | 0.008525 | -0.033658 | 0.011654 | -0.019062 | 0.010204 | 0.015142 | 0.005325 | 0.11165 | 0.08278 | 0.30222 | 0.019363 | 0.023941 | 0.082776 | -0.070087 | 0.011252 | 0.16938 | -0.10671 | -0.2832 | 121.9859 | 0.024672 | 121.9768 | 121.9719 | -0.014038 | -0.004195 | 0.21524 | 121.6834 | -0.075723 | 121.9905 | 121.8965 | 0.21311 | 0.082404 | -0.19369 | 122.0782 | 122.0493 | 122.2688 | 121.9817 | -0.067612 | 121.9778 | 122.1359 | 121.8598 | 122.0493 | -0.37017
3178.9375 | 122.2137 | -121.9666 | 0.09613 | 1.4211e-13 | -0.015978 | -0.013505 | -0.044957 | -0.041711 | -0.012352 | -0.00083919 | 0.023729 | 0.0089522 | -0.033445 | 0.011867 | -0.019489 | 0.005626 | 0.019721 | 0.005325 | 0.1208 | 0.091937 | 0.30222 | 0.014784 | 0.019362 | 0.082776 | -0.065509 | 0.011252 | 0.17854 | -0.12045 | -0.28778 | 121.9813 | 0.024674 | 121.9722 | 121.9719 | -0.009459 | -0.004193 | 0.20609 | 121.6788 | -0.084878 | 121.9859 | 121.901 | 0.22227 | 0.082406 | -0.21658 | 122.0874 | 122.0585 | 122.2688 | 121.9863 | -0.081346 | 121.9778 | 122.1451 | 121.8461 | 122.0493 | -0.38391
3180.6719 | 122.0993 | -121.9986 | 0.12817 | 1.4211e-13 | -0.015765 | -0.013077 | -0.04517 | -0.041498 | -0.012138 | -0.0084697 | 0.023942 | 0.009166 | -0.033658 | 0.011654 | -0.019062 | 0.001048 | 0.0243 | 0.009904 | 0.11622 | 0.08278 | 0.3068 | 0.019363 | 0.019362 | 0.082776 | -0.079245 | 0.020409 | 0.17396 | -0.10671 | -0.28778 | 122.018 | -0.011949 | 121.9996 | 122.0085 | -0.009459 | -0.045394 | 0.17862 | 121.7108 | -0.10777 | 122.018 | 121.9194 | 0.20853 | 0.045784 | -0.23489 | 122.1148 | 122.0814 | 122.3054 | 122.0229 | -0.10881 | 122.019 | 122.1726 | 121.8919 | 122.0814 | -0.41595
3182.4531 | 122.2183 | -121.9894 | 0.11444 | 1.4211e-13 | -0.015765 | -0.013718 | -0.044957 | -0.041925 | -0.012138 | -0.00083919 | 0.023942 | 0.0095932 | -0.033231 | 0.011654 | -0.019276 | 0.001048 | 0.028878 | 0.000747 | 0.11165 | 0.091937 | 0.30222 | 0.010206 | 0.023941 | 0.078197 | -0.070087 | 0.020409 | 0.17854 | -0.12045 | -0.28778 | 121.9996 | -0.002794 | 121.9905 | 121.9902 | -0.009459 | -0.022504 | 0.18778 | 121.7017 | -0.094032 | 122.0134 | 121.9194 | 0.21769 | 0.064095 | -0.23489 | 122.1011 | 122.0814 | 122.2917 | 122.0183 | -0.10423 | 122.0099 | 122.168 | 121.869 | 122.0676 | -0.40222
3184.25 | 122.2183 | -121.9894 | 0.09613 | 1.4211e-13 | -0.016192 | -0.013932 | -0.04517 | -0.041711 | -0.012352 | -0.0084697 | 0.02437 | 0.009807 | -0.033445 | 0.011654 | -0.018848 | 0.005626 | 0.019721 | 0.005325 | 0.11622 | 0.087359 | 0.30222 | 0.010206 | 0.019362 | 0.078197 | -0.079245 | 0.015831 | 0.18311 | -0.11129 | -0.2832 | 121.9996 | 0.020095 | 121.9951 | 121.9948 | -0.004881 | -0.008771 | 0.20609 | 121.7062 | -0.080299 | 122.0088 | 121.9102 | 0.20395 | 0.086985 | -0.20742 | 122.1057 | 122.0768 | 122.2917 | 122.0092 | -0.085924 | 122.0053 | 122.1726 | 121.8781 | 122.0676 | -0.37933
3186 | 122.2641 | -121.9849 | 0.082397 | 1.4211e-13 | -0.016192 | -0.013505 | -0.044957 | -0.041711 | -0.012138 | -0.00083919 | 0.023301 | 0.010234 | -0.033658 | 0.012081 | -0.019062 | -0.003531 | 0.019721 | -0.003831 | 0.10707 | 0.08278 | 0.29764 | 0.014784 | 0.014784 | 0.073618 | -0.079245 | 0.015831 | 0.17854 | -0.12503 | -0.28778 | 121.9996 | 0.024671 | 121.9813 | 121.981 | -0.018615 | 0.000383 | 0.21524 | 121.6971 | -0.066566 | 121.9996 | 121.9056 | 0.20853 | 0.096139 | -0.20743 | 122.0919 | 122.0676 | 122.2825 | 122.0046 | -0.067613 | 122.0007 | 122.1634 | 121.8598 | 122.0585 | -0.37017
3187.7812 | 122.1954 | -122.0215 | 0.11902 | 1.4211e-13 | -0.016192 | -0.013505 | -0.045384 | -0.041711 | -0.012138 | -0.00083919 | 0.024583 | 0.010234 | -0.033445 | 0.012081 | -0.019276 | 0.001048 | 0.015142 | 0.000747 | 0.11165 | 0.08278 | 0.30222 | 0.023942 | 0.023941 | 0.078197 | -0.079245 | 0.015831 | 0.17396 | -0.11587 | -0.27862 | 122.0454 | -0.007372 | 122.0225 | 122.0222 | -0.023195 | -0.036239 | 0.1832 | 121.7429 | -0.10319 | 122.0454 | 121.9422 | 0.19937 | 0.054939 | -0.23489 | 122.1331 | 122.1043 | 122.3237 | 122.0366 | -0.095077 | 122.0373 | 122.1954 | 121.9056 | 122.0997 | -0.39764
3189.5781 | 122.2824 | -121.9849 | 0.10529 | 1.4211e-13 | -0.016192 | -0.012863 | -0.045384 | -0.041711 | -0.011924 | 0.0067908 | 0.024156 | 0.010234 | -0.033658 | 0.011654 | -0.019062 | 0.001048 | 0.015142 | -0.003831 | 0.11622 | 0.091937 | 0.30222 | 0.014784 | 0.019362 | 0.087354 | -0.074666 | 0.015831 | 0.17396 | -0.12045 | -0.27862 | 121.9996 | 0.010939 | 121.9859 | 121.981 | -0.018615 | -0.013349 | 0.19693 | 121.7062 | -0.089455 | 122.0042 | 121.9102 | 0.20395 | 0.068672 | -0.22574 | 122.1011 | 122.0768 | 122.2871 | 122 | -0.090502 | 122.0007 | 122.1588 | 121.8644 | 122.0722 | -0.3839
3191.2969 | 122.2321 | -122.0078 | 0.10986 | 1.4211e-13 | -0.015765 | -0.013077 | -0.04517 | -0.041925 | -0.012138 | 0.0067908 | 0.024156 | 0.010448 | -0.033445 | 0.012081 | -0.019276 | -0.003531 | 0.019721 | -0.003831 | 0.11622 | 0.087359 | 0.31137 | 0.005627 | 0.019362 | 0.078197 | -0.079245 | 0.015831 | 0.17854 | -0.11587 | -0.2832 | 122.0134 | 0.006362 | 122.0042 | 122.0039 | -0.009458 | -0.022504 | 0.20151 | 121.7246 | -0.094032 | 122.0271 | 121.9285 | 0.20395 | 0.068673 | -0.22574 | 122.124 | 122.0951 | 122.3191 | 122.0275 | -0.10424 | 122.0236 | 122.1863 | 121.8919 | 122.0859 | -0.39306
3193.0625 | 122.2733 | -122.0261 | 0.091553 | 1.4211e-13 | -0.015765 | -0.013718 | -0.04517 | -0.041498 | -0.012352 | -0.00083919 | 0.024797 | 0.010662 | -0.033872 | 0.011654 | -0.018848 | -0.003531 | 0.019721 | -0.003831 | 0.11165 | 0.087359 | 0.3068 | 0.014784 | 0.019362 | 0.078197 | -0.088402 | 0.015831 | 0.18311 | -0.11129 | -0.28778 | 122.0408 | 0.020094 | 122.0225 | 122.0222 | -0.018615 | -0.004194 | 0.21524 | 121.7383 | -0.075722 | 122.0454 | 121.9377 | 0.19937 | 0.091562 | -0.20285 | 122.1377 | 122.1134 | 122.3329 | 122.0458 | -0.076769 | 122.0419 | 122.2092 | 121.9148 | 122.1043 | -0.37933
3194.8594 | 122.1863 | -122.0398 | 0.14648 | 1.4211e-13 | -0.015765 | -0.013505 | -0.04517 | -0.041711 | -0.012352 | 0.0067908 | 0.024156 | 0.011516 | -0.033872 | 0.011867 | -0.019062 | 0.005626 | 0.0243 | 0.000747 | 0.1208 | 0.087359 | 0.29764 | 0.019363 | 0.019362 | 0.073618 | -0.074666 | 0.020409 | 0.18311 | -0.12045 | -0.2832 | 122.0592 | -0.02568 | 122.0454 | 122.0405 | -0.018616 | -0.059125 | 0.15115 | 121.7566 | -0.12607 | 122.0592 | 121.9651 | 0.20853 | 0.036631 | -0.26693 | 122.1606 | 122.1272 | 122.3374 | 122.0641 | -0.12712 | 122.0602 | 122.2229 | 121.9193 | 122.1134 | -0.42968
3196.5781 | 122.1725 | -122.0673 | 0.12817 | 1.4211e-13 | -0.016192 | -0.013291 | -0.04517 | -0.041711 | -0.011924 | -0.00083919 | 0.023942 | 0.01173 | -0.033872 | 0.012081 | -0.019062 | 0.005626 | 0.0243 | 0.000747 | 0.11165 | 0.091937 | 0.3068 | 0.014784 | 0.019362 | 0.078197 | -0.065509 | 0.006674 | 0.17854 | -0.11587 | -0.28778 | 122.082 | -0.016527 | 122.0729 | 122.068 | -0.014037 | -0.036237 | 0.17862 | 121.7795 | -0.1215 | 122.0866 | 122.0018 | 0.22227 | 0.050362 | -0.24405 | 122.1789 | 122.1592 | 122.3741 | 122.0916 | -0.11339 | 122.0739 | 122.2458 | 121.9514 | 122.1455 | -0.41595
3198.3594 | 122.2183 | -122.0444 | 0.11444 | 1.4211e-13 | -0.015765 | -0.013505 | -0.044957 | -0.041925 | -0.012138 | -0.00083919 | 0.023729 | 0.011089 | -0.033658 | 0.011654 | -0.018848 | 0.005626 | 0.028878 | 0.000747 | 0.11622 | 0.096516 | 0.3068 | 0.005627 | 0.010205 | 0.078197 | -0.074666 | 0.011252 | 0.17396 | -0.11587 | -0.27862 | 122.05 | 0.001784 | 122.05 | 122.0451 | -0.00488 | -0.017925 | 0.19235 | 121.7658 | -0.10319 | 122.0546 | 121.9697 | 0.20395 | 0.059517 | -0.23031 | 122.1606 | 122.1409 | 122.3512 | 122.0733 | -0.10881 | 122.0556 | 122.2183 | 121.9285 | 122.1226 | -0.39306
3200.1406 | 122.3099 | -122.0169 | 0.10071 | 1.4211e-13 | -0.015765 | -0.013505 | -0.044743 | -0.041498 | -0.011924 | -0.00083919 | 0.023515 | 0.011089 | -0.033658 | 0.011654 | -0.018848 | 0.001048 | 0.015142 | 0.005325 | 0.11622 | 0.091937 | 0.30222 | 0.014784 | 0.02852 | 0.082776 | -0.079245 | 0.015831 | 0.18311 | -0.11587 | -0.2832 | 122.0317 | 0.015517 | 122.018 | 122.0222 | -0.009459 | -0.008771 | 0.20151 | 121.7337 | -0.084877 | 122.0454 | 121.9377 | 0.20395 | 0.082407 | -0.21658 | 122.1331 | 122.1088 | 122.3191 | 122.032 | -0.085924 | 122.0327 | 122.2 | 121.901 | 122.0997 | -0.38391
3201.8906 | 122.3328 | -122.0398 | 0.086975 | 1.4211e-13 | -0.015978 | -0.013291 | -0.044957 | -0.041711 | -0.011924 | -0.00083919 | 0.023729 | 0.011516 | -0.034513 | 0.012081 | -0.019062 | 0.005626 | 0.019721 | 0.000747 | 0.11165 | 0.096516 | 0.29764 | 0.005627 | 0.023941 | 0.078197 | -0.074666 | 0.015831 | 0.17854 | -0.11587 | -0.2832 | 122.0454 | 0.024672 | 122.0454 | 122.0405 | -0.00488 | 0.009541 | 0.21066 | 121.7566 | -0.071144 | 122.0637 | 121.9651 | 0.20853 | 0.091561 | -0.20285 | 122.1514 | 122.1363 | 122.3374 | 122.0595 | -0.081348 | 122.0556 | 122.2183 | 121.9239 | 122.118 | -0.37017
3203.6719 | 122.2275 | -122.1085 | 0.13275 | 1.4211e-13 | -0.015765 | -0.013077 | -0.04517 | -0.041711 | -0.011924 | -0.0084697 | 0.023515 | 0.011516 | -0.034299 | 0.011654 | -0.018848 | 0.001048 | 0.015142 | 0.005325 | 0.1208 | 0.087359 | 0.30222 | 0.010206 | 0.023941 | 0.073618 | -0.070087 | 0.020409 | 0.18311 | -0.11587 | -0.28778 | 122.1187 | -0.011947 | 122.1095 | 122.1138 | -0.004881 | -0.045392 | 0.16947 | 121.8207 | -0.11234 | 122.1324 | 122.0384 | 0.21769 | 0.050364 | -0.24862 | 122.2293 | 122.1958 | 122.4107 | 122.1236 | -0.12255 | 122.1289 | 122.2916 | 121.9926 | 122.1821 | -0.42053
3205.4062 | 122.2961 | -122.0718 | 0.10529 | 1.4211e-13 | -0.015765 | -0.013505 | -0.044957 | -0.041284 | -0.012352 | -0.00083919 | 0.023301 | 0.012584 | -0.034299 | 0.012081 | -0.019276 | 0.001048 | 0.019721 | 0.000747 | 0.11165 | 0.087359 | 0.30222 | 0.014784 | 0.023941 | 0.073618 | -0.074666 | 0.015831 | 0.18311 | -0.074664 | -0.27862 | 122.0866 | 0.006361 | 122.0729 | 122.0726 | -0.014037 | -0.017927 | 0.19693 | 121.7932 | -0.089455 | 122.0958 | 121.9972 | 0.20395 | 0.077829 | -0.17995 | 122.1835 | 122.1592 | 122.3741 | 122.0916 | -0.090502 | 122.0877 | 122.255 | 121.9972 | 122.1455 | -0.3839
3207.1875 | 122.2549 | -122.0856 | 0.14191 | 1.4211e-13 | -0.015978 | -0.013505 | -0.045384 | -0.041498 | -0.011924 | -0.00083919 | 0.023729 | 0.012798 | -0.034299 | 0.011654 | -0.019062 | 0.005626 | 0.010564 | 0.000747 | 0.11165 | 0.091937 | 0.29764 | 0.014784 | 0.014784 | 0.078197 | -0.070087 | 0.015831 | 0.17854 | -0.11129 | -0.28778 | 122.1004 | -0.03026 | 122.0912 | 122.0863 | -0.014037 | -0.04997 | 0.15573 | 121.7978 | -0.12608 | 122.1004 | 122.0155 | 0.21769 | 0.036629 | -0.2532 | 122.1972 | 122.1775 | 122.3832 | 122.0961 | -0.12712 | 122.1014 | 122.2641 | 121.9743 | 122.1638 | -0.42968
3208.9844 | 122.2366 | -122.0993 | 0.11902 | 1.4211e-13 | -0.016192 | -0.013718 | -0.04517 | -0.041711 | -0.012138 | -0.00083919 | 0.023515 | 0.01173 | -0.034086 | 0.012081 | -0.019489 | 0.001048 | 0.0243 | 0.000747 | 0.11622 | 0.091937 | 0.31137 | 0.019363 | 0.014784 | 0.082776 | -0.079245 | 0.020409 | 0.18769 | -0.097557 | -0.2832 | 122.1187 | -0.002794 | 122.1004 | 122.1001 | -0.018616 | -0.027082 | 0.19235 | 121.8161 | -0.09861 | 122.1141 | 122.0201 | 0.20395 | 0.068674 | -0.21658 | 122.2155 | 122.1912 | 122.4107 | 122.1236 | -0.099656 | 122.1197 | 122.287 | 122.0017 | 122.1821 | -0.40222
3210.7656 | 122.374 | -122.0856 | 0.10071 | 1.4211e-13 | -0.015978 | -0.013718 | -0.04517 | -0.041498 | -0.011924 | -0.00083919 | 0.023515 | 0.011944 | -0.033872 | 0.012081 | -0.019489 | 0.001048 | 0.019721 | 0.000747 | 0.11165 | 0.091937 | 0.29764 | 0.010206 | 0.019362 | 0.073618 | -0.074666 | 0.011252 | 0.18769 | -0.0884 | -0.27404 | 122.0958 | 0.010939 | 122.0866 | 122.0863 | -0.009459 | -0.008771 | 0.19693 | 121.8115 | -0.089456 | 122.1049 | 122.0109 | 0.19937 | 0.086985 | -0.18911 | 122.1972 | 122.1775 | 122.3832 | 122.1053 | -0.090502 | 122.0968 | 122.2733 | 121.9972 | 122.1592 | -0.37475
3212.5469 | 122.3557 | -122.081 | 0.086975 | 1.4211e-13 | -0.015765 | -0.012863 | -0.04517 | -0.041711 | -0.012565 | -0.0084697 | 0.023729 | 0.011944 | -0.034299 | 0.011867 | -0.019062 | 0.001048 | 0.010564 | -0.003831 | 0.11622 | 0.087359 | 0.30222 | 0.010206 | 0.023941 | 0.078197 | -0.070087 | 0.015831 | 0.17854 | -0.10214 | -0.2832 | 122.0912 | 0.02925 | 122.082 | 122.0772 | -0.014037 | 0.000384 | 0.21524 | 121.7978 | -0.071144 | 122.1049 | 122.0109 | 0.21311 | 0.091561 | -0.18911 | 122.1972 | 122.1684 | 122.3832 | 122.0916 | -0.076769 | 122.0968 | 122.2595 | 121.9789 | 122.1592 | -0.37017
3214.2656 | 122.2916 | -122.1039 | 0.10986 | 1.4211e-13 | -0.016192 | -0.013505 | -0.04517 | -0.041711 | -0.012352 | -0.00083919 | 0.023942 | 0.011089 | -0.033872 | 0.011867 | -0.019062 | 0.001048 | 0.0243 | -0.003831 | 0.11165 | 0.087359 | 0.30222 | 0.019363 | 0.019362 | 0.073618 | -0.079245 | 0.020409 | 0.17854 | -0.11129 | -0.27862 | 122.1232 | 0.001784 | 122.1049 | 122.1001 | -0.023194 | -0.022504 | 0.19235 | 121.8253 | -0.089454 | 122.1232 | 122.0246 | 0.19937 | 0.068673 | -0.22116 | 122.2155 | 122.1912 | 122.4061 | 122.1282 | -0.0905 | 122.1243 | 122.2824 | 121.9926 | 122.1775 | -0.38848
3216.0469 | 122.3877 | -122.0993 | 0.091553 | 1.4211e-13 | -0.016192 | -0.013505 | -0.044957 | -0.041711 | -0.012138 | -0.0084697 | 0.023301 | 0.010448 | -0.032804 | 0.011654 | -0.019489 | 0.001048 | 0.0243 | -0.003831 | 0.12538 | 0.087359 | 0.29764 | 0.019363 | 0.019362 | 0.073618 | -0.074666 | 0.015831 | 0.18311 | -0.083821 | -0.27862 | 122.1187 | 0.033829 | 122.1004 | 122.0955 | -0.023194 | -0.004194 | 0.20609 | 121.8207 | -0.075722 | 122.1187 | 122.0246 | 0.20395 | 0.091562 | -0.17537 | 122.2247 | 122.1867 | 122.3969 | 122.1236 | -0.07219 | 122.1151 | 122.2824 | 122.0155 | 122.1729 | -0.37017
3217.8281 | 122.3557 | -122.0856 | 0.082397 | 1.4211e-13 | -0.016192 | -0.013291 | -0.04517 | -0.041925 | -0.011924 | -0.0084697 | 0.022661 | 0.010875 | -0.03259 | 0.011867 | -0.019062 | 0.005626 | 0.019721 | 0.000747 | 0.11622 | 0.087359 | 0.29764 | 0.010206 | 0.019362 | 0.082776 | -0.074666 | 0.020409 | 0.18311 | -0.12045 | -0.27862 | 122.0958 | 0.033828 | 122.0912 | 122.0863 | -0.009459 | 0.004962 | 0.21524 | 121.807 | -0.061988 | 122.1049 | 122.0109 | 0.20395 | 0.10072 | -0.20285 | 122.2018 | 122.1729 | 122.3832 | 122.1053 | -0.072191 | 122.106 | 122.2687 | 121.9651 | 122.1683 | -0.36102
3219.5469 | 122.2961 | -122.1085 | 0.11902 | 1.4211e-13 | -0.016192 | -0.013505 | -0.044957 | -0.041711 | -0.012138 | -0.00083919 | 0.02202 | 0.011303 | -0.031949 | 0.011867 | -0.019062 | 0.005626 | 0.019721 | 0.009904 | 0.11622 | 0.091937 | 0.30222 | -0.003531 | 0.023941 | 0.078197 | -0.074666 | 0.011252 | 0.17396 | -0.12045 | -0.27862 | 122.1049 | -0.002794 | 122.1141 | 122.1184 | 0.013435 | -0.027082 | 0.1832 | 121.8298 | -0.10777 | 122.1324 | 122.0338 | 0.20395 | 0.054939 | -0.23947 | 122.2247 | 122.2004 | 122.4107 | 122.1282 | -0.12255 | 122.1197 | 122.2824 | 121.988 | 122.1867 | -0.39764
3221.3281 | 122.2504 | -122.1268 | 0.12817 | 1.4211e-13 | -0.015765 | -0.013505 | -0.044743 | -0.041498 | -0.011924 | -0.0084697 | 0.02202 | 0.011089 | -0.032376 | 0.012081 | -0.019062 | 0.001048 | 0.010564 | -0.003831 | 0.1208 | 0.08278 | 0.30222 | 0.019363 | 0.019362 | 0.082776 | -0.074666 | 0.020409 | 0.17396 | -0.051771 | -0.2832 | 122.1461 | -0.00737 | 122.1278 | 122.1229 | -0.023194 | -0.045394 | 0.17404 | 121.8436 | -0.10777 | 122.1461 | 122.0521 | 0.20853 | 0.045784 | -0.17995 | 122.2476 | 122.2095 | 122.429 | 122.1373 | -0.10881 | 122.1472 | 122.3007 | 122.075 | 122.2095 | -0.41137
3223.1094 | 122.2916 | -122.1359 | 0.13733 | 1.4211e-13 | -0.015978 | -0.013505 | -0.044743 | -0.041711 | -0.012138 | -0.0084697 | 0.022447 | 0.011303 | -0.032163 | 0.012081 | -0.019276 | 0.001048 | 0.010564 | 0.000747 | 0.1208 | 0.08278 | 0.3068 | 0.019363 | 0.023941 | 0.082776 | -0.074666 | 0.015831 | 0.17854 | -0.033457 | -0.2832 | 122.1553 | -0.016525 | 122.137 | 122.1367 | -0.018616 | -0.054549 | 0.16947 | 121.8527 | -0.1215 | 122.1599 | 122.0613 | 0.20853 | 0.041207 | -0.17079 | 122.2567 | 122.2187 | 122.4427 | 122.1465 | -0.11797 | 122.1518 | 122.3145 | 122.1025 | 122.2187 | -0.42053
3224.8281 | 122.3328 | -122.1405 | 0.12817 | 1.4211e-13 | -0.015978 | -0.013077 | -0.044743 | -0.041925 | -0.012138 | -0.0084697 | 0.022233 | 0.010875 | -0.031735 | 0.012081 | -0.019489 | 0.005626 | 0.015142 | 0.000747 | 0.11622 | 0.087359 | 0.29764 | 0.005627 | 0.023941 | 0.078197 | -0.079245 | 0.015831 | 0.17396 | -0.10671 | -0.27404 | 122.1461 | -0.011949 | 122.1461 | 122.1412 | -0.00488 | -0.040815 | 0.16946 | 121.8665 | -0.11234 | 122.1644 | 122.0613 | 0.19479 | 0.045784 | -0.23489 | 122.2567 | 122.2279 | 122.4381 | 122.1556 | -0.12255 | 122.1563 | 122.3145 | 122.0338 | 122.2187 | -0.40221
3226.6094 | 122.4243 | -122.0947 | 0.082397 | 1.4211e-13 | -0.016192 | -0.013718 | -0.044957 | -0.041711 | -0.012352 | -0.0161 | 0.020524 | 0.012798 | -0.031094 | 0.012081 | -0.019489 | 0.001048 | 0.0243 | 0.000747 | 0.11622 | 0.091937 | 0.29764 | 0.005627 | 0.023941 | 0.078197 | -0.074666 | 0.002095 | 0.17396 | -0.11129 | -0.27404 | 122.1004 | 0.033828 | 122.0958 | 122.0955 | -0.00488 | 0.00954 | 0.21524 | 121.8207 | -0.080302 | 122.1187 | 122.0201 | 0.19937 | 0.091561 | -0.19369 | 122.211 | 122.1867 | 122.3924 | 122.119 | -0.07677 | 122.0968 | 122.2687 | 121.9834 | 122.1729 | -0.35644
3228.4062 | 122.3969 | -122.0947 | 0.068665 | 1.4211e-13 | -0.016192 | -0.013291 | -0.04517 | -0.041711 | -0.012138 | 0.0067908 | 0.019883 | 0.013012 | -0.031094 | 0.012081 | -0.019276 | 0.005626 | 0.0243 | 0.000747 | 0.11622 | 0.091937 | 0.29764 | 0.014784 | 0.033099 | 0.078197 | -0.070087 | 0.011252 | 0.17396 | -0.11587 | -0.27404 | 122.1095 | 0.04756 | 122.1004 | 122.0955 | -0.014037 | 0.023272 | 0.22897 | 121.8207 | -0.057413 | 122.1278 | 122.0246 | 0.20395 | 0.10529 | -0.18454 | 122.211 | 122.1867 | 122.3924 | 122.119 | -0.053881 | 122.106 | 122.2687 | 121.9789 | 122.1729 | -0.34271
3230.1875 | 122.2916 | -122.1954 | 0.14191 | 1.4211e-13 | -0.016192 | -0.013077 | -0.044957 | -0.041711 | -0.012138 | 0.0067908 | 0.020311 | 0.013439 | -0.030881 | 0.011867 | -0.019062 | 0.001048 | 0.019721 | 0.000747 | 0.11622 | 0.087359 | 0.3068 | 0.014784 | 0.019362 | 0.078197 | -0.070087 | 0.015831 | 0.18311 | -0.079243 | -0.27862 | 122.2102 | -0.025682 | 122.1965 | 122.1962 | -0.014037 | -0.054548 | 0.16489 | 121.9168 | -0.12608 | 122.2148 | 122.1253 | 0.20853 | 0.041208 | -0.22115 | 122.3117 | 122.2828 | 122.5022 | 122.2152 | -0.12712 | 122.2113 | 122.3786 | 122.1162 | 122.2736 | -0.42053
3231.9219 | 122.3145 | -122.1863 | 0.12817 | 1.4211e-13 | -0.015978 | -0.013505 | -0.04517 | -0.041711 | -0.012352 | -0.00083919 | 0.01967 | 0.013439 | -0.030667 | 0.012295 | -0.019276 | 0.001048 | 0.015142 | 0.000747 | 0.11622 | 0.087359 | 0.3068 | 0.014784 | 0.019362 | 0.082776 | -0.074666 | 0.011252 | 0.18311 | -0.0884 | -0.27404 | 122.2011 | -0.011949 | 122.1873 | 122.187 | -0.014037 | -0.040815 | 0.17862 | 121.9122 | -0.11692 | 122.2056 | 122.1116 | 0.19937 | 0.054941 | -0.21657 | 122.3025 | 122.2736 | 122.4931 | 122.2014 | -0.11339 | 122.1975 | 122.3694 | 122.0979 | 122.2691 | -0.40221
3233.7031 | 122.4243 | -122.1588 | 0.10071 | 1.4211e-13 | -0.016192 | -0.013505 | -0.04517 | -0.041711 | -0.012352 | -0.0161 | 0.01967 | 0.013653 | -0.030453 | 0.011867 | -0.019276 | 0.001048 | 0.015142 | 0.005325 | 0.11622 | 0.08278 | 0.3068 | 0.010206 | 0.023941 | 0.078197 | -0.079245 | 0.011252 | 0.17854 | -0.092979 | -0.2832 | 122.169 | 0.015517 | 122.1599 | 122.1641 | -0.004881 | -0.017928 | 0.20609 | 121.8756 | -0.089456 | 122.1828 | 122.0796 | 0.20395 | 0.077828 | -0.19369 | 122.275 | 122.2416 | 122.4656 | 122.174 | -0.090502 | 122.1701 | 122.3373 | 122.0658 | 122.237 | -0.38391
3235.5 | 122.4472 | -122.1268 | 0.10529 | 1.4211e-13 | -0.015978 | -0.013291 | -0.04517 | -0.041925 | -0.011924 | 0.0067908 | 0.019242 | 0.013653 | -0.029813 | 0.012081 | -0.019062 | 0.001048 | 0.015142 | -0.003831 | 0.1208 | 0.08278 | 0.3068 | 0.019363 | 0.023941 | 0.082776 | -0.065509 | 0.015831 | 0.17396 | -0.097557 | -0.2832 | 122.1461 | 0.015518 | 122.1278 | 122.1229 | -0.023194 | -0.022506 | 0.20151 | 121.8436 | -0.089455 | 122.1507 | 122.0613 | 0.21769 | 0.068672 | -0.20284 | 122.2476 | 122.2095 | 122.4336 | 122.1419 | -0.085923 | 122.1426 | 122.3007 | 122.0292 | 122.2095 | -0.38848
3237.2969 | 122.4701 | -122.1451 | 0.086975 | 1.4211e-13 | -0.015765 | -0.013718 | -0.04517 | -0.041498 | -0.012138 | -0.00083919 | 0.019456 | 0.013866 | -0.030453 | 0.012081 | -0.019276 | 0.001048 | 0.019721 | 0.000747 | 0.1208 | 0.096516 | 0.3068 | 0.010206 | 0.023941 | 0.087354 | -0.070087 | 0.015831 | 0.17854 | -0.11587 | -0.27862 | 122.1553 | 0.033829 | 122.1461 | 122.1458 | -0.009459 | 0.009541 | 0.21982 | 121.8665 | -0.071144 | 122.169 | 122.075 | 0.20853 | 0.091561 | -0.20285 | 122.2659 | 122.2416 | 122.4519 | 122.1648 | -0.076769 | 122.1609 | 122.3236 | 122.0292 | 122.2324 | -0.36559
3239.0938 | 122.4472 | -122.1359 | 0.091553 | 1.4211e-13 | -0.016192 | -0.013505 | -0.044957 | -0.041711 | -0.012138 | -0.0161 | 0.020311 | 0.013866 | -0.030026 | 0.011867 | -0.019276 | 0.001048 | 0.010564 | 0.000747 | 0.1208 | 0.096516 | 0.30222 | 0.023942 | 0.023941 | 0.078197 | -0.074666 | 0.015831 | 0.17854 | -0.11129 | -0.27862 | 122.1599 | 0.029251 | 122.137 | 122.1367 | -0.023195 | 0.004963 | 0.21066 | 121.8573 | -0.075722 | 122.1599 | 122.0613 | 0.20395 | 0.086983 | -0.20285 | 122.2567 | 122.2324 | 122.4381 | 122.1465 | -0.067611 | 122.1518 | 122.3145 | 122.0246 | 122.2141 | -0.37017
3240.8906 | 122.3557 | -122.1725 | 0.12817 | 1.4211e-13 | -0.015978 | -0.013505 | -0.044957 | -0.041711 | -0.012352 | -0.00083919 | 0.01967 | 0.014935 | -0.030026 | 0.012081 | -0.019062 | 0.001048 | 0.019721 | 0.000747 | 0.11165 | 0.091937 | 0.29764 | 0.019363 | 0.023941 | 0.078197 | -0.065509 | 0.011252 | 0.17854 | -0.097557 | -0.27404 | 122.1919 | -0.016527 | 122.1736 | 122.1733 | -0.018616 | -0.036237 | 0.16946 | 121.8985 | -0.11692 | 122.1965 | 122.107 | 0.20853 | 0.050362 | -0.22573 | 122.2842 | 122.2645 | 122.4702 | 122.1923 | -0.10881 | 122.1838 | 122.3511 | 122.075 | 122.2507 | -0.40221
3242.6719 | 122.406 | -122.1588 | 0.091553 | 1.4211e-13 | -0.015978 | -0.013291 | -0.044957 | -0.041498 | -0.012352 | -0.0084697 | 0.019456 | 0.015362 | -0.029385 | 0.011867 | -0.019062 | 0.005626 | 0.019721 | 0.000747 | 0.12538 | 0.091937 | 0.30222 | 0.005627 | 0.023941 | 0.082776 | -0.070087 | 0.011252 | 0.17854 | -0.079243 | -0.27404 | 122.1644 | 0.033829 | 122.1644 | 122.1596 | -0.00488 | 0.000384 | 0.21066 | 121.8848 | -0.080301 | 122.1828 | 122.0887 | 0.20395 | 0.086983 | -0.1708 | 122.2842 | 122.2507 | 122.461 | 122.1785 | -0.085926 | 122.1701 | 122.3373 | 122.0796 | 122.2416 | -0.36559
3244.4062 | 122.406 | -122.1725 | 0.11444 | 1.4211e-13 | -0.015978 | -0.013718 | -0.044743 | -0.041711 | -0.012138 | -0.0084697 | 0.019456 | 0.015362 | -0.029172 | 0.012081 | -0.019276 | 0.001048 | 0.019721 | 0.005325 | 0.11622 | 0.1011 | 0.3068 | 0.014784 | 0.023941 | 0.082776 | -0.065509 | 0.006674 | 0.17396 | -0.11587 | -0.26946 | 122.1873 | 0.001784 | 122.1736 | 122.1779 | -0.009459 | -0.013346 | 0.19235 | 121.9031 | -0.10777 | 122.1965 | 122.107 | 0.20395 | 0.059517 | -0.23031 | 122.2888 | 122.2736 | 122.4793 | 122.1923 | -0.099657 | 122.1792 | 122.3465 | 122.0567 | 122.2553 | -0.3839
3246.2031 | 122.4564 | -122.1771 | 0.10071 | 1.4211e-13 | -0.016192 | -0.013505 | -0.045384 | -0.041284 | -0.012352 | -0.0084697 | 0.020097 | 0.015576 | -0.029172 | 0.011867 | -0.019276 | 0.001048 | 0.015142 | -0.008409 | 0.11622 | 0.091937 | 0.30222 | 0.010206 | 0.014784 | 0.078197 | -0.065509 | 0.020409 | 0.17396 | -0.019721 | -0.2832 | 122.1873 | 0.015517 | 122.1782 | 122.1687 | -0.018615 | -0.008771 | 0.20151 | 121.8939 | -0.080299 | 122.1919 | 122.1116 | 0.21769 | 0.07325 | -0.12043 | 122.2933 | 122.2691 | 122.4793 | 122.1923 | -0.090502 | 122.1975 | 122.3511 | 122.1574 | 122.2553 | -0.38391
3247.9219 | 122.4838 | -122.1954 | 0.09613 | 1.4211e-13 | -0.016192 | -0.013291 | -0.044957 | -0.041711 | -0.012565 | 0.014421 | 0.020524 | 0.016217 | -0.028744 | 0.011867 | -0.019276 | 0.005626 | 0.019721 | -0.003831 | 0.12538 | 0.091937 | 0.3068 | 0.014784 | 0.019362 | 0.078197 | -0.070087 | 0.011252 | 0.18311 | -0.097557 | -0.27862 | 122.2102 | 0.029252 | 122.2011 | 122.1916 | -0.018615 | -0.004193 | 0.21067 | 121.9168 | -0.084878 | 122.2148 | 122.1253 | 0.20853 | 0.086985 | -0.19369 | 122.3208 | 122.2874 | 122.5022 | 122.2152 | -0.081346 | 122.2067 | 122.3786 | 122.0979 | 122.2736 | -0.37475
3249.7031 | 122.4335 | -122.1817 | 0.10529 | 1.4211e-13 | -0.016406 | -0.013077 | -0.04517 | -0.041925 | -0.012352 | 0.0067908 | 0.020951 | 0.016644 | -0.028744 | 0.012081 | -0.019276 | 0.005626 | 0.015142 | -0.003831 | 0.11622 | 0.096516 | 0.30222 | 0.005627 | 0.019362 | 0.082776 | -0.070087 | 0.011252 | 0.18311 | -0.079243 | -0.27404 | 122.1873 | 0.010939 | 122.1873 | 122.1779 | -0.009458 | -0.00877 | 0.19693 | 121.9077 | -0.094034 | 122.2011 | 122.1116 | 0.20395 | 0.077829 | -0.18453 | 122.2979 | 122.2782 | 122.4839 | 122.1968 | -0.099659 | 122.193 | 122.3648 | 122.1025 | 122.2645 | -0.37933
3251.5156 | 122.4792 | -122.1588 | 0.07782 | 1.4211e-13 | -0.016406 | -0.013505 | -0.044957 | -0.041498 | -0.012138 | 0.0067908 | 0.021806 | 0.017499 | -0.028103 | 0.011867 | -0.019276 | 0.001048 | 0.019721 | 0.000747 | 0.1208 | 0.096516 | 0.3068 | 0.010206 | 0.019362 | 0.078197 | -0.070087 | 0.011252 | 0.16938 | -0.051771 | -0.26946 | 122.169 | 0.042984 | 122.1599 | 122.1596 | -0.009459 | 0.018696 | 0.22898 | 121.8894 | -0.066568 | 122.1782 | 122.0887 | 0.19937 | 0.091559 | -0.12959 | 122.2796 | 122.2553 | 122.4656 | 122.1785 | -0.067614 | 122.1701 | 122.3282 | 122.107 | 122.237 | -0.34728
3253.2344 | 122.493 | -122.1634 | 0.082397 | 1.4211e-13 | -0.015765 | -0.013718 | -0.044957 | -0.041925 | -0.012138 | 0.0067908 | 0.022661 | 0.018567 | -0.027035 | 0.011867 | -0.019276 | 0.005626 | 0.015142 | -0.003831 | 0.11622 | 0.087359 | 0.31137 | 0.005627 | 0.019362 | 0.082776 | -0.070087 | 0.020409 | 0.17854 | -0.074664 | -0.27862 | 122.169 | 0.033828 | 122.169 | 122.1596 | -0.009458 | 0.004962 | 0.22898 | 121.8848 | -0.061988 | 122.1828 | 122.0933 | 0.20853 | 0.096139 | -0.15706 | 122.2796 | 122.2508 | 122.4748 | 122.1785 | -0.07677 | 122.1838 | 122.3419 | 122.0887 | 122.2462 | -0.36102
3255.0156 | 122.3648 | -122.2137 | 0.11444 | 1.4211e-13 | -0.015978 | -0.013291 | -0.044957 | -0.041498 | -0.012565 | -0.0084697 | 0.024797 | 0.02049 | -0.025753 | 0.011654 | -0.019489 | 0.010204 | 0.019721 | 0.000747 | 0.11622 | 0.091937 | 0.30222 | 0.014784 | 0.02852 | 0.078197 | -0.070087 | 0.020409 | 0.18311 | -0.042614 | -0.26946 | 122.2285 | 0.001784 | 122.2239 | 122.2145 | -0.014037 | -0.022504 | 0.18778 | 121.9443 | -0.094032 | 122.2423 | 122.1437 | 0.19937 | 0.068674 | -0.15706 | 122.33 | 122.3057 | 122.516 | 122.2335 | -0.099657 | 122.2342 | 122.3969 | 122.1711 | 122.2919 | -0.3839
3256.8125 | 122.406 | -122.2275 | 0.13733 | 1.4211e-13 | -0.016192 | -0.013291 | -0.045384 | -0.041498 | -0.012138 | -0.00083919 | 0.02907 | 0.025618 | -0.021908 | 0.011867 | -0.019276 | 0.005626 | 0.028878 | 0.000747 | 0.12538 | 0.091937 | 0.31137 | 0.019363 | 0.023941 | 0.078197 | -0.070087 | 0.024988 | 0.18769 | -0.060928 | -0.27862 | 122.2468 | -0.011947 | 122.2331 | 122.2282 | -0.018616 | -0.045392 | 0.17404 | 121.9489 | -0.11234 | 122.2514 | 122.1574 | 0.20853 | 0.050364 | -0.19826 | 122.3529 | 122.3194 | 122.5389 | 122.2564 | -0.11797 | 122.2525 | 122.4152 | 122.1666 | 122.3057 | -0.41595
3258.5312 | 122.493 | -122.1817 | 0.10071 | 1.4211e-13 | -0.016406 | -0.013505 | -0.044957 | -0.041711 | -0.012138 | -0.0084697 | 0.089529 | 0.087151 | 0.018899 | 0.011867 | -0.019276 | 0.010204 | 0.019721 | -0.003831 | 0.11622 | 0.1011 | 0.3068 | 0.010206 | 0.02852 | 0.087354 | -0.065509 | 0.034145 | 0.20601 | -0.010564 | -0.27404 | 122.1919 | 0.015517 | 122.1919 | 122.1779 | -0.014037 | 0.000387 | 0.20609 | 121.9077 | -0.066563 | 122.2102 | 122.1162 | 0.20853 | 0.1053 | -0.11127 | 122.2979 | 122.2828 | 122.4885 | 122.2014 | -0.090502 | 122.2158 | 122.3877 | 122.1711 | 122.2691 | -0.37475
3260.3281 | 122.374 | -122.2275 | 0.12817 | 1.4211e-13 | -0.015765 | -0.013291 | -0.04517 | -0.041711 | -0.012352 | -0.0161 | 0.028215 | 0.02519 | -0.023189 | 0.012081 | -0.019276 | 0.005626 | 0.019721 | 0.000747 | 0.11622 | 0.087359 | 0.29764 | 0.023942 | 0.019362 | 0.073618 | -0.070087 | 0.024988 | 0.18769 | -0.074664 | -0.27404 | 122.2514 | -0.011949 | 122.2331 | 122.2282 | -0.023195 | -0.040815 | 0.16946 | 121.9534 | -0.10319 | 122.2468 | 122.1574 | 0.20395 | 0.059519 | -0.20284 | 122.3437 | 122.3148 | 122.5251 | 122.2472 | -0.10423 | 122.2525 | 122.4152 | 122.1528 | 122.3011 | -0.40221
3262.125 | 122.3969 | -122.2549 | 0.13275 | 1.4211e-13 | -0.015978 | -0.013505 | -0.04517 | -0.041711 | -0.012138 | 0.0067908 | 0.019883 | 0.016003 | -0.029172 | 0.012081 | -0.019062 | 0.001048 | 0.0243 | -0.003831 | 0.11165 | 0.091937 | 0.30222 | 0.014784 | 0.019362 | 0.073618 | -0.070087 | 0.011252 | 0.18311 | -0.079243 | -0.27862 | 122.2697 | -0.021104 | 122.256 | 122.2511 | -0.018615 | -0.040814 | 0.16947 | 121.9763 | -0.1215 | 122.2743 | 122.1849 | 0.20853 | 0.050364 | -0.21199 | 122.3666 | 122.3469 | 122.5572 | 122.2792 | -0.11797 | 122.2662 | 122.4381 | 122.1757 | 122.3286 | -0.41137
3263.8438 | 122.493 | -122.1909 | 0.086975 | 1.4211e-13 | -0.016192 | -0.013505 | -0.044957 | -0.041925 | -0.012138 | 0.0067908 | 0.019883 | 0.016217 | -0.029385 | 0.011867 | -0.019062 | -0.003531 | 0.015142 | 0.000747 | 0.1208 | 0.096516 | 0.30222 | 0.014784 | 0.023941 | 0.078197 | -0.065509 | 0.011252 | 0.18311 | -0.10214 | -0.27404 | 122.2056 | 0.033829 | 122.1873 | 122.1916 | -0.014037 | 0.009541 | 0.21524 | 121.9168 | -0.075723 | 122.2148 | 122.1253 | 0.20853 | 0.09614 | -0.18911 | 122.3117 | 122.2874 | 122.4931 | 122.206 | -0.072191 | 122.2021 | 122.374 | 122.0887 | 122.2691 | -0.36101
3265.625 | 122.3831 | -122.2366 | 0.14648 | 1.4211e-13 | -0.015978 | -0.013291 | -0.04517 | -0.041925 | -0.011924 | -0.00083919 | 0.019883 | 0.015789 | -0.029599 | 0.012081 | -0.019062 | 0.005626 | 0.015142 | -0.003831 | 0.10707 | 0.087359 | 0.30222 | 0.014784 | 0.023941 | 0.078197 | -0.070087 | 0.011252 | 0.18311 | -0.083821 | -0.27862 | 122.2514 | -0.039416 | 122.2423 | 122.2328 | -0.018615 | -0.059125 | 0.15573 | 121.958 | -0.13523 | 122.2606 | 122.1665 | 0.20853 | 0.036631 | -0.23031 | 122.3437 | 122.324 | 122.5388 | 122.2518 | -0.1317 | 122.2479 | 122.4197 | 122.1528 | 122.3148 | -0.4251
3267.4219 | 122.4564 | -122.2 | 0.091553 | 1.4211e-13 | -0.015978 | -0.013291 | -0.04517 | -0.041711 | -0.012352 | -0.0084697 | 0.01967 | 0.015576 | -0.029599 | 0.011867 | -0.019276 | 0.001048 | 0.015142 | 0.000747 | 0.12538 | 0.091937 | 0.30222 | 0.010206 | 0.019362 | 0.082776 | -0.079245 | 0.020409 | 0.17854 | -0.12045 | -0.27404 | 122.2102 | 0.033829 | 122.2011 | 122.2008 | -0.009459 | 0.000384 | 0.21066 | 121.926 | -0.071144 | 122.2194 | 122.1208 | 0.19479 | 0.086983 | -0.212 | 122.3254 | 122.2919 | 122.5022 | 122.2152 | -0.081347 | 122.2204 | 122.3785 | 122.0796 | 122.2828 | -0.36559
3269.2031 | 122.525 | -122.2229 | 0.091553 | 1.4211e-13 | -0.015551 | -0.013505 | -0.044957 | -0.041284 | -0.011924 | -0.00083919 | 0.01967 | 0.015362 | -0.03024 | 0.011654 | -0.019276 | 0.005626 | 0.019721 | -0.003831 | 0.11622 | 0.087359 | 0.29764 | 0.019363 | 0.023941 | 0.078197 | -0.070087 | 0.011252 | 0.18311 | -0.12045 | -0.2832 | 122.2423 | 0.024672 | 122.2285 | 122.2191 | -0.023194 | -0.004194 | 0.20609 | 121.9397 | -0.080301 | 122.2468 | 122.1528 | 0.21311 | 0.091562 | -0.212 | 122.3391 | 122.3103 | 122.5205 | 122.2426 | -0.07219 | 122.2342 | 122.406 | 122.1024 | 122.3011 | -0.37475
3271 | 122.4838 | -122.2229 | 0.086975 | 1.4211e-13 | -0.016192 | -0.013718 | -0.044743 | -0.041711 | -0.012138 | -0.0161 | 0.01967 | 0.015576 | -0.029813 | 0.012295 | -0.019489 | 0.005626 | 0.019721 | 0.000747 | 0.12996 | 0.08278 | 0.30222 | 0.014784 | 0.019362 | 0.073618 | -0.070087 | 0.015831 | 0.19227 | -0.070086 | -0.27862 | 122.2377 | 0.042985 | 122.2285 | 122.2236 | -0.014037 | -0.004195 | 0.21524 | 121.9443 | -0.071144 | 122.2423 | 122.1528 | 0.20853 | 0.1053 | -0.15706 | 122.3529 | 122.3057 | 122.5251 | 122.2426 | -0.072191 | 122.2387 | 122.4152 | 122.1528 | 122.2965 | -0.36559
3272.7344 | 122.525 | -122.2183 | 0.091553 | 1.4211e-13 | -0.016192 | -0.013505 | -0.045384 | -0.041498 | -0.012138 | -0.00083919 | 0.019883 | 0.015789 | -0.030026 | 0.012081 | -0.019276 | 0.001048 | 0.0243 | 0.000747 | 0.11622 | 0.091937 | 0.3068 | 0.010206 | 0.019362 | 0.073618 | -0.074666 | 0.020409 | 0.17854 | -0.079243 | -0.27404 | 122.2285 | 0.024672 | 122.2194 | 122.2191 | -0.009459 | 0.000384 | 0.21524 | 121.9443 | -0.071144 | 122.2377 | 122.1437 | 0.19937 | 0.086983 | -0.1708 | 122.3345 | 122.3103 | 122.5251 | 122.2426 | -0.081347 | 122.2387 | 122.3969 | 122.1391 | 122.2919 | -0.36559
3274.4844 | 122.5113 | -122.2641 | 0.10071 | 1.4211e-13 | -0.016192 | -0.013505 | -0.044957 | -0.041711 | -0.012138 | -0.0084697 | 0.01967 | 0.015789 | -0.030026 | 0.011867 | -0.019276 | 0.005626 | 0.015142 | 0.000747 | 0.1208 | 0.091937 | 0.3068 | 0.010206 | 0.023941 | 0.073618 | -0.074666 | 0.011252 | 0.18769 | -0.11129 | -0.27404 | 122.2743 | 0.020096 | 122.2697 | 122.2648 | -0.009459 | -0.008771 | 0.20609 | 121.9901 | -0.089456 | 122.288 | 122.1894 | 0.19937 | 0.086985 | -0.212 | 122.3849 | 122.356 | 122.5709 | 122.2792 | -0.090502 | 122.2754 | 122.4518 | 122.1528 | 122.3377 | -0.37475
3276.2812 | 122.4838 | -122.2595 | 0.09613 | 1.4211e-13 | -0.016192 | -0.013505 | -0.044743 | -0.041711 | -0.012352 | -0.00083919 | 0.019883 | 0.015789 | -0.030026 | 0.012081 | -0.018848 | 0.005626 | 0.015142 | -0.003831 | 0.11165 | 0.091937 | 0.29764 | 0.014784 | 0.033099 | 0.073618 | -0.06093 | 0.020409 | 0.18769 | -0.074664 | -0.27404 | 122.2743 | 0.015517 | 122.2651 | 122.2557 | -0.018615 | -0.004193 | 0.20151 | 121.9855 | -0.075721 | 122.2926 | 122.1986 | 0.21311 | 0.091563 | -0.17079 | 122.3712 | 122.3515 | 122.5572 | 122.2747 | -0.081346 | 122.2799 | 122.4472 | 122.1849 | 122.3331 | -0.37017
3278.0156 | 122.525 | -122.2275 | 0.091553 | 1.4211e-13 | -0.015765 | -0.013718 | -0.04517 | -0.041711 | -0.012352 | -0.0161 | 0.01967 | 0.015576 | -0.029813 | 0.012081 | -0.019062 | 0.005626 | 0.0243 | -0.003831 | 0.11622 | 0.091937 | 0.30222 | 0.010206 | 0.023941 | 0.082776 | -0.065509 | 0.020409 | 0.18311 | -0.11129 | -0.27404 | 122.2377 | 0.024672 | 122.2331 | 122.2236 | -0.014037 | 0.000384 | 0.21066 | 121.9534 | -0.071144 | 122.2514 | 122.162 | 0.20853 | 0.091562 | -0.20285 | 122.3437 | 122.3194 | 122.5297 | 122.2518 | -0.081347 | 122.2479 | 122.4106 | 122.1162 | 122.3103 | -0.36559
3279.75 | 122.438 | -122.287 | 0.11444 | 1.4211e-13 | -0.016192 | -0.013291 | -0.04517 | -0.042139 | -0.012352 | -0.0084697 | 0.019883 | 0.016217 | -0.029813 | 0.012081 | -0.019489 | -0.003531 | 0.019721 | -0.003831 | 0.11622 | 0.091937 | 0.30222 | 0.005627 | 0.023941 | 0.078197 | -0.074666 | 0.015831 | 0.18311 | -0.11129 | -0.27404 | 122.2926 | 0.001784 | 122.2835 | 122.2832 | -0.009458 | -0.022504 | 0.18778 | 122.0129 | -0.09861 | 122.3109 | 122.2123 | 0.19937 | 0.068674 | -0.22573 | 122.4032 | 122.3789 | 122.5892 | 122.3067 | -0.10881 | 122.3028 | 122.4701 | 122.1757 | 122.3652 | -0.38848
3281.5469 | 122.5937 | -122.2595 | 0.091553 | 1.4211e-13 | -0.016192 | -0.013718 | -0.045598 | -0.041498 | -0.012352 | -0.0084697 | 0.020097 | 0.015576 | -0.029599 | 0.011867 | -0.019276 | 0.005626 | 0.015142 | -0.003831 | 0.11622 | 0.08278 | 0.30222 | 0.014784 | 0.019362 | 0.073618 | -0.070087 | 0.011252 | 0.18311 | -0.10214 | -0.27404 | 122.2743 | 0.024672 | 122.2651 | 122.2557 | -0.018615 | -0.008773 | 0.21066 | 121.9855 | -0.080301 | 122.2789 | 122.1894 | 0.20395 | 0.091562 | -0.19369 | 122.3757 | 122.3423 | 122.5617 | 122.2747 | -0.076769 | 122.2708 | 122.4426 | 122.1574 | 122.3331 | -0.36559
3283.3281 | 122.4152 | -122.2504 | 0.11902 | 1.4211e-13 | -0.015765 | -0.013505 | -0.044957 | -0.041498 | -0.012138 | -0.0084697 | 0.019883 | 0.016003 | -0.029813 | 0.011867 | -0.019276 | -0.003531 | 0.015142 | 0.005325 | 0.12538 | 0.087359 | 0.31137 | 0.014784 | 0.023941 | 0.073618 | -0.070087 | 0.020409 | 0.18311 | -0.10214 | -0.27404 | 122.2652 | 0.006363 | 122.2468 | 122.2557 | -0.009459 | -0.03166 | 0.19235 | 121.9763 | -0.09861 | 122.2743 | 122.1803 | 0.20395 | 0.064096 | -0.22115 | 122.3757 | 122.3377 | 122.5617 | 122.2655 | -0.10423 | 122.2708 | 122.4335 | 122.1482 | 122.324 | -0.39306
3285.0625 | 122.4976 | -122.2961 | 0.10986 | 1.4211e-13 | -0.016192 | -0.013291 | -0.04517 | -0.041498 | -0.012138 | 0.0067908 | 0.020311 | 0.015789 | -0.029813 | 0.01144 | -0.019062 | 0.005626 | 0.015142 | -0.003831 | 0.1208 | 0.08278 | 0.3068 | 0.010206 | 0.023941 | 0.078197 | -0.070087 | 0.011252 | 0.17854 | -0.065507 | -0.27404 | 122.3063 | 0.010941 | 122.3018 | 122.2923 | -0.014037 | -0.027083 | 0.19693 | 122.0221 | -0.098611 | 122.3201 | 122.2261 | 0.20395 | 0.068673 | -0.17537 | 122.4169 | 122.3789 | 122.6029 | 122.3113 | -0.099657 | 122.3074 | 122.4747 | 122.2306 | 122.3743 | -0.3839
3286.8594 | 122.5662 | -122.2687 | 0.082397 | 1.4211e-13 | -0.015765 | -0.013291 | -0.04517 | -0.041498 | -0.012352 | -0.00083919 | 0.020311 | 0.015789 | -0.029599 | 0.012081 | -0.019276 | 0.001048 | 0.0243 | -0.008409 | 0.11622 | 0.087359 | 0.30222 | 0.019363 | 0.023941 | 0.082776 | -0.070087 | 0.015831 | 0.18311 | -0.12045 | -0.27862 | 122.288 | 0.033828 | 122.2697 | 122.2603 | -0.027772 | 0.004962 | 0.21982 | 121.9901 | -0.066566 | 122.2926 | 122.1986 | 0.20853 | 0.10072 | -0.20285 | 122.3849 | 122.356 | 122.5709 | 122.293 | -0.063034 | 122.2845 | 122.4518 | 122.1482 | 122.3515 | -0.36102
3288.6406 | 122.4884 | -122.2733 | 0.11902 | 1.4211e-13 | -0.016192 | -0.013291 | -0.044743 | -0.041711 | -0.012138 | -0.0084697 | 0.019883 | 0.015789 | -0.029385 | 0.012081 | -0.019062 | 0.001048 | 0.019721 | 0.005325 | 0.11622 | 0.096516 | 0.3068 | 0.014784 | 0.02852 | 0.078197 | -0.079245 | 0.020409 | 0.18311 | -0.10214 | -0.27404 | 122.288 | -0.002794 | 122.2743 | 122.2786 | -0.009459 | -0.022503 | 0.18778 | 121.9992 | -0.09861 | 122.3018 | 122.194 | 0.19479 | 0.064096 | -0.22115 | 122.3895 | 122.3698 | 122.58 | 122.293 | -0.10423 | 122.2937 | 122.4564 | 122.1711 | 122.3515 | -0.39306
3290.4219 | 122.4792 | -122.3099 | 0.11444 | 1.4211e-13 | -0.016192 | -0.012863 | -0.04517 | -0.041711 | -0.012138 | -0.0084697 | 0.019883 | 0.016003 | -0.029385 | 0.012081 | -0.019489 | 0.001048 | 0.019721 | 0.009904 | 0.11622 | 0.091937 | 0.30222 | 0.010206 | 0.019362 | 0.078197 | -0.070087 | 0.015831 | 0.18311 | -0.0884 | -0.27862 | 122.3201 | 0.001784 | 122.3109 | 122.3198 | -0.000302 | -0.022504 | 0.18778 | 122.0313 | -0.09861 | 122.3292 | 122.2398 | 0.20853 | 0.068674 | -0.20284 | 122.4261 | 122.4018 | 122.6121 | 122.3296 | -0.10423 | 122.3257 | 122.493 | 122.2215 | 122.3881 | -0.39306
3292.1562 | 122.58 | -122.2778 | 0.07782 | 1.4211e-13 | -0.016406 | -0.013505 | -0.044743 | -0.041925 | -0.012138 | -0.00083919 | 0.019883 | 0.016003 | -0.030026 | 0.012081 | -0.019489 | 0.010204 | 0.019721 | 0.000747 | 0.11622 | 0.091937 | 0.3068 | 0.010206 | 0.023941 | 0.078197 | -0.074666 | 0.020409 | 0.17396 | -0.097557 | -0.27404 | 122.288 | 0.038405 | 122.288 | 122.2786 | -0.009459 | 0.014117 | 0.22898 | 122.0038 | -0.057411 | 122.3018 | 122.2032 | 0.19937 | 0.096138 | -0.17538 | 122.3941 | 122.3698 | 122.5846 | 122.2976 | -0.067614 | 122.2982 | 122.4518 | 122.1803 | 122.356 | -0.35186
3293.9531 | 122.4289 | -122.3236 | 0.1236 | 1.4211e-13 | -0.015978 | -0.013718 | -0.044957 | -0.041711 | -0.012138 | -0.0084697 | 0.020311 | 0.016217 | -0.029385 | 0.012081 | -0.019489 | 0.010204 | 0.015142 | -0.008409 | 0.11165 | 0.087359 | 0.29764 | 0.010206 | 0.033099 | 0.087354 | -0.070087 | 0.020409 | 0.18311 | -0.083821 | -0.27862 | 122.3338 | -0.011949 | 122.3338 | 122.3152 | -0.018615 | -0.036237 | 0.17404 | 122.045 | -0.10319 | 122.3567 | 122.2535 | 0.20853 | 0.059519 | -0.20742 | 122.4353 | 122.411 | 122.6212 | 122.3388 | -0.11339 | 122.344 | 122.5067 | 122.2398 | 122.411 | -0.40221
3295.6719 | 122.4564 | -122.3282 | 0.10986 | 1.4211e-13 | -0.016192 | -0.013291 | -0.045598 | -0.041711 | -0.011924 | -0.00083919 | 0.020097 | 0.016217 | -0.029172 | 0.012295 | -0.019276 | 0.001048 | 0.015142 | 0.000747 | 0.1208 | 0.087359 | 0.3068 | 0.014784 | 0.019362 | 0.082776 | -0.079245 | 0.020409 | 0.17854 | -0.10671 | -0.27862 | 122.343 | 0.010941 | 122.3292 | 122.3289 | -0.014037 | -0.022504 | 0.19693 | 122.0496 | -0.089454 | 122.3475 | 122.2489 | 0.19937 | 0.068673 | -0.21658 | 122.449 | 122.4155 | 122.635 | 122.3433 | -0.095079 | 122.3486 | 122.5067 | 122.2215 | 122.411 | -0.38848
3297.4531 | 122.5342 | -122.2961 | 0.10986 | 1.4211e-13 | -0.015978 | -0.013505 | -0.04517 | -0.041711 | -0.011711 | -0.0161 | 0.020097 | 0.016003 | -0.029599 | 0.012081 | -0.019062 | -0.003531 | 0.019721 | -0.008409 | 0.11622 | 0.096516 | 0.29764 | 0.005627 | 0.019362 | 0.082776 | -0.056351 | 0.011252 | 0.17854 | -0.092979 | -0.27404 | 122.3018 | 0.006362 | 122.2926 | 122.2877 | -0.014036 | -0.013347 | 0.18778 | 122.0221 | -0.098611 | 122.3155 | 122.2398 | 0.21769 | 0.068673 | -0.20284 | 122.4124 | 122.3927 | 122.5938 | 122.3159 | -0.10424 | 122.3074 | 122.4747 | 122.2032 | 122.3789 | -0.3839
3299.1719 | 122.5021 | -122.3053 | 0.13275 | 1.4211e-13 | -0.015978 | -0.013505 | -0.044957 | -0.041925 | -0.011924 | -0.0084697 | 0.020311 | 0.01643 | -0.028958 | 0.012295 | -0.019062 | 0.005626 | 0.019721 | -0.008409 | 0.11622 | 0.091937 | 0.3068 | 0.014784 | 0.019362 | 0.078197 | -0.074666 | 0.015831 | 0.18311 | -0.05635 | -0.27404 | 122.3201 | -0.016526 | 122.3109 | 122.2969 | -0.023193 | -0.040814 | 0.17405 | 122.0313 | -0.11692 | 122.3247 | 122.2306 | 0.19937 | 0.050364 | -0.1891 | 122.4215 | 122.3972 | 122.6121 | 122.325 | -0.11797 | 122.3211 | 122.4884 | 122.2489 | 122.3835 | -0.40679
3300.9688 | 122.4747 | -122.3419 | 0.11902 | 1.4211e-13 | -0.016192 | -0.013291 | -0.044957 | -0.041711 | -0.012352 | 0.0067908 | 0.020311 | 0.016217 | -0.029599 | 0.012081 | -0.019489 | 0.005626 | 0.019721 | 0.000747 | 0.11165 | 0.091937 | 0.29764 | 0.010206 | 0.023941 | 0.082776 | -0.065509 | 0.015831 | 0.17854 | -0.070086 | -0.27404 | 122.3521 | -0.007372 | 122.3475 | 122.3427 | -0.009459 | -0.027082 | 0.17862 | 122.0679 | -0.10319 | 122.3659 | 122.2764 | 0.20853 | 0.059517 | -0.1891 | 122.4536 | 122.4339 | 122.6396 | 122.3616 | -0.10881 | 122.3578 | 122.5205 | 122.2718 | 122.4247 | -0.39306
3302.7656 | 122.4884 | -122.3373 | 0.13733 | 1.4211e-13 | -0.016192 | -0.013505 | -0.045384 | -0.041711 | -0.012352 | -0.0084697 | 0.024583 | 0.020917 | -0.027035 | 0.011867 | -0.019276 | 0.001048 | 0.019721 | 0.000747 | 0.11165 | 0.087359 | 0.30222 | 0.019363 | 0.014784 | 0.078197 | -0.074666 | 0.015831 | 0.17396 | -0.051771 | -0.26946 | 122.3567 | -0.025682 | 122.3384 | 122.3381 | -0.018616 | -0.04997 | 0.16489 | 122.0679 | -0.1215 | 122.3521 | 122.2627 | 0.1948 | 0.036629 | -0.1891 | 122.449 | 122.4247 | 122.6396 | 122.3571 | -0.11797 | 122.3532 | 122.5113 | 122.2856 | 122.4155 | -0.40679
3304.5781 | 122.5525 | -122.287 | 0.10529 | 1.4211e-13 | -0.015978 | -0.013505 | -0.044957 | -0.041498 | -0.012565 | 0.014421 | 0.025011 | 0.020917 | -0.026608 | 0.012081 | -0.019062 | 0.010204 | 0.019721 | 0.005325 | 0.11622 | 0.087359 | 0.3068 | 0.014784 | 0.023941 | 0.082776 | -0.06093 | 0.024988 | 0.18311 | -0.097557 | -0.27404 | 122.3018 | 0.010939 | 122.2972 | 122.2923 | -0.009459 | -0.017927 | 0.20151 | 122.0129 | -0.080298 | 122.3109 | 122.2261 | 0.21311 | 0.077829 | -0.20284 | 122.4032 | 122.3743 | 122.5938 | 122.3067 | -0.090502 | 122.312 | 122.4701 | 122.1894 | 122.3698 | -0.37933
3306.2969 | 122.5479 | -122.3145 | 0.12817 | 1.4211e-13 | -0.016406 | -0.013505 | -0.044957 | -0.041498 | -0.012138 | 0.0067908 | 0.02202 | 0.017712 | -0.028958 | 0.012295 | -0.019062 | 0.005626 | 0.019721 | 0.000747 | 0.1208 | 0.087359 | 0.30222 | 0.014784 | 0.019362 | 0.064461 | -0.070087 | 0.011252 | 0.18311 | -0.070086 | -0.26946 | 122.3292 | -0.00737 | 122.3201 | 122.3152 | -0.014037 | -0.040815 | 0.17404 | 122.045 | -0.11692 | 122.3338 | 122.2444 | 0.19937 | 0.054941 | -0.19826 | 122.4353 | 122.4018 | 122.6167 | 122.3342 | -0.11339 | 122.3257 | 122.4976 | 122.2444 | 122.3789 | -0.39764
3308.0938 | 122.6074 | -122.3145 | 0.086975 | 1.4211e-13 | -0.016192 | -0.013505 | -0.044957 | -0.041711 | -0.012565 | -0.00083919 | 0.020738 | 0.016644 | -0.029172 | 0.012295 | -0.019276 | -0.003531 | 0.010564 | -0.003831 | 0.1208 | 0.087359 | 0.30222 | 0.005627 | 0.019362 | 0.073618 | -0.070087 | 0.011252 | 0.18769 | -0.051771 | -0.27404 | 122.3201 | 0.033829 | 122.3109 | 122.3106 | -0.009458 | 0.000384 | 0.21524 | 122.0404 | -0.075723 | 122.3338 | 122.2444 | 0.20395 | 0.10072 | -0.13875 | 122.4353 | 122.4018 | 122.6167 | 122.325 | -0.081348 | 122.3257 | 122.5021 | 122.2627 | 122.3881 | -0.36101
3309.8906 | 122.5067 | -122.3282 | 0.1236 | 1.4211e-13 | -0.016192 | -0.013718 | -0.04517 | -0.041498 | -0.012352 | -0.0084697 | 0.021806 | 0.017499 | -0.028958 | 0.011867 | -0.019062 | 0.005626 | 0.019721 | -0.008409 | 0.12538 | 0.087359 | 0.30222 | 0.019363 | 0.019362 | 0.073618 | -0.074666 | 0.015831 | 0.17396 | -0.0884 | -0.26946 | 122.3475 | 0.001786 | 122.3338 | 122.3198 | -0.027772 | -0.036237 | 0.17862 | 122.0587 | -0.10776 | 122.3475 | 122.2535 | 0.1948 | 0.050362 | -0.212 | 122.4536 | 122.4155 | 122.6304 | 122.3479 | -0.10423 | 122.344 | 122.5021 | 122.2398 | 122.4018 | -0.39306
3311.6094 | 122.5891 | -122.3053 | 0.10071 | 1.4211e-13 | -0.016406 | -0.013505 | -0.04517 | -0.041498 | -0.012138 | -0.00083919 | 0.021165 | 0.017071 | -0.029599 | 0.012081 | -0.018848 | 0.005626 | 0.028878 | 0.000747 | 0.11622 | 0.091937 | 0.3068 | 0.010206 | 0.023941 | 0.078197 | -0.070087 | 0.015831 | 0.18311 | -0.092979 | -0.27404 | 122.3155 | 0.015517 | 122.3109 | 122.306 | -0.009459 | -0.008771 | 0.20609 | 122.0313 | -0.084877 | 122.3292 | 122.2352 | 0.20395 | 0.082407 | -0.19369 | 122.4215 | 122.3972 | 122.6121 | 122.3342 | -0.090502 | 122.3211 | 122.4884 | 122.2123 | 122.3835 | -0.37475
3313.4062 | 122.5021 | -122.3877 | 0.11902 | 1.4211e-13 | -0.016619 | -0.013505 | -0.044957 | -0.041498 | -0.012138 | 0.0067908 | 0.020524 | 0.01643 | -0.029813 | 0.012508 | -0.019276 | 0.010204 | 0.019721 | 0.005325 | 0.11622 | 0.1011 | 0.30222 | 0.005627 | 0.023941 | 0.078197 | -0.079245 | 0.020409 | 0.17396 | -0.047193 | -0.26488 | 122.3933 | -0.002794 | 122.3979 | 122.393 | -0.000302 | -0.017924 | 0.1832 | 122.1228 | -0.09861 | 122.4116 | 122.3084 | 0.18564 | 0.054939 | -0.16621 | 122.5039 | 122.4888 | 122.6899 | 122.4074 | -0.11339 | 122.4081 | 122.5617 | 122.3405 | 122.4659 | -0.3839
3315.1875 | 122.5845 | -122.3373 | 0.09613 | 1.4211e-13 | -0.016406 | -0.013718 | -0.04517 | -0.041925 | -0.012352 | -0.0084697 | 0.020738 | 0.01643 | -0.03024 | 0.012081 | -0.019062 | 0.001048 | 0.015142 | 0.000747 | 0.11165 | 0.096516 | 0.31137 | 0.010206 | 0.019362 | 0.073618 | -0.070087 | 0.006674 | 0.17396 | -0.11129 | -0.26946 | 122.3475 | 0.015517 | 122.3384 | 122.3381 | -0.009459 | 0.000386 | 0.21524 | 122.0679 | -0.089456 | 122.3567 | 122.2673 | 0.19937 | 0.077828 | -0.20742 | 122.449 | 122.4339 | 122.6487 | 122.3525 | -0.085924 | 122.344 | 122.5113 | 122.226 | 122.411 | -0.36559
3316.9375 | 122.6166 | -122.3282 | 0.10071 | 1.4211e-13 | -0.016406 | -0.013932 | -0.045384 | -0.041711 | -0.012138 | -0.00083919 | 0.020524 | 0.016858 | -0.030026 | 0.011867 | -0.019276 | 0.005626 | 0.019721 | 0.000747 | 0.11622 | 0.091937 | 0.30222 | 0.019363 | 0.019362 | 0.082776 | -0.074666 | 0.020409 | 0.17854 | -0.11587 | -0.26488 | 122.3475 | 0.015517 | 122.3338 | 122.3289 | -0.018616 | -0.008771 | 0.20151 | 122.0633 | -0.080299 | 122.3475 | 122.2535 | 0.19022 | 0.077828 | -0.21658 | 122.4444 | 122.4201 | 122.6304 | 122.3479 | -0.081345 | 122.3486 | 122.5067 | 122.2123 | 122.411 | -0.36559
3318.7188 | 122.493 | -122.3877 | 0.10986 | 1.4211e-13 | -0.016406 | -0.013505 | -0.044957 | -0.041711 | -0.012352 | -0.00083919 | 0.020738 | 0.016644 | -0.030026 | 0.012081 | -0.019062 | -0.003531 | 0.010564 | 0.005325 | 0.11165 | 0.087359 | 0.3068 | 0.005627 | 0.014784 | 0.078197 | -0.06093 | 0.011252 | 0.17396 | -0.10671 | -0.26946 | 122.3933 | 0.001784 | 122.3842 | 122.393 | -0.000302 | -0.022504 | 0.19693 | 122.1182 | -0.098611 | 122.4025 | 122.3268 | 0.20853 | 0.064095 | -0.21658 | 122.4993 | 122.4751 | 122.6945 | 122.3983 | -0.10424 | 122.3989 | 122.5617 | 122.281 | 122.4659 | -0.37932
3320.4531 | 122.644 | -122.3145 | 0.091553 | 1.4211e-13 | -0.016406 | -0.013718 | -0.04517 | -0.041925 | -0.012352 | -0.00083919 | 0.020738 | 0.016858 | -0.03024 | 0.012295 | -0.019062 | 0.005626 | 0.019721 | -0.003831 | 0.1208 | 0.087359 | 0.30222 | 0.005627 | 0.014784 | 0.078197 | -0.070087 | 0.015831 | 0.17396 | -0.10671 | -0.26946 | 122.3201 | 0.029251 | 122.3201 | 122.3106 | -0.009458 | -0.004194 | 0.21066 | 122.045 | -0.075722 | 122.3292 | 122.2444 | 0.19937 | 0.082405 | -0.19827 | 122.4353 | 122.4018 | 122.6167 | 122.3342 | -0.085926 | 122.3303 | 122.4884 | 122.2077 | 122.3927 | -0.36101
3322.2344 | 122.6166 | -122.3511 | 0.091553 | 1.4211e-13 | -0.016406 | -0.013932 | -0.045384 | -0.041925 | -0.012138 | -0.00083919 | 0.020738 | 0.017285 | -0.029813 | 0.012081 | -0.019276 | -0.003531 | 0.019721 | 0.005325 | 0.1208 | 0.091937 | 0.30222 | 0.010206 | 0.023941 | 0.078197 | -0.070087 | 0.015831 | 0.17854 | -0.12045 | -0.27404 | 122.3613 | 0.029251 | 122.3475 | 122.3564 | -0.004881 | 0.000384 | 0.21066 | 122.077 | -0.075722 | 122.375 | 122.281 | 0.20395 | 0.086983 | -0.212 | 122.4719 | 122.443 | 122.6533 | 122.3708 | -0.081347 | 122.3669 | 122.5296 | 122.2306 | 122.4293 | -0.36559
3323.9531 | 122.612 | -122.3328 | 0.09613 | 1.4211e-13 | -0.016619 | -0.013505 | -0.04517 | -0.041925 | -0.012352 | 0.0067908 | 0.020951 | 0.016858 | -0.029813 | 0.012081 | -0.019276 | 0.005626 | 0.0243 | -0.003831 | 0.11622 | 0.091937 | 0.3068 | 0.023942 | 0.019362 | 0.073618 | -0.065509 | 0.015831 | 0.18311 | -0.0884 | -0.27404 | 122.3567 | 0.020095 | 122.3384 | 122.3289 | -0.027773 | -0.004193 | 0.21067 | 122.0587 | -0.080299 | 122.3521 | 122.2673 | 0.20853 | 0.086985 | -0.18453 | 122.449 | 122.4247 | 122.6396 | 122.3571 | -0.072188 | 122.3486 | 122.5159 | 122.2444 | 122.4064 | -0.37017
3325.7344 | 122.6074 | -122.3373 | 0.10071 | 1.4211e-13 | -0.016619 | -0.013932 | -0.044957 | -0.041498 | -0.012565 | -0.0161 | 0.020738 | 0.016644 | -0.030026 | 0.012081 | -0.019276 | 0.005626 | 0.019721 | -0.003831 | 0.1208 | 0.1011 | 0.29764 | 0.010206 | 0.02852 | 0.082776 | -0.070087 | 0.015831 | 0.17854 | -0.11587 | -0.26946 | 122.3475 | 0.020096 | 122.343 | 122.3335 | -0.014037 | 0.000387 | 0.19693 | 122.0679 | -0.084877 | 122.3659 | 122.2673 | 0.19937 | 0.077828 | -0.21658 | 122.4581 | 122.4384 | 122.635 | 122.3571 | -0.090502 | 122.3532 | 122.5159 | 122.2215 | 122.4201 | -0.37017
3327.5469 | 122.5388 | -122.3557 | 0.10986 | 1.4211e-13 | -0.016406 | -0.013932 | -0.044957 | -0.041925 | -0.012565 | 0.0067908 | 0.021165 | 0.017071 | -0.03024 | 0.012081 | -0.019489 | 0.001048 | 0.019721 | -0.003831 | 0.11165 | 0.087359 | 0.31137 | 0.010206 | 0.023941 | 0.073618 | -0.070087 | 0.015831 | 0.18311 | -0.079243 | -0.26946 | 122.3659 | 0.001784 | 122.3567 | 122.3518 | -0.014037 | -0.022504 | 0.20151 | 122.0862 | -0.094032 | 122.3796 | 122.2856 | 0.19937 | 0.073252 | -0.18911 | 122.4673 | 122.443 | 122.667 | 122.3754 | -0.099657 | 122.3715 | 122.5388 | 122.2764 | 122.4293 | -0.37932
3329.2656 | 122.6303 | -122.3465 | 0.091553 | 1.4211e-13 | -0.016192 | -0.013505 | -0.044957 | -0.041711 | -0.011924 | -0.00083919 | 0.020738 | 0.017071 | -0.03024 | 0.012295 | -0.019276 | 0.005626 | 0.019721 | 0.000747 | 0.12538 | 0.087359 | 0.31595 | 0.005627 | 0.02852 | 0.082776 | -0.079245 | 0.015831 | 0.18311 | -0.11129 | -0.27404 | 122.3521 | 0.033829 | 122.3521 | 122.3472 | -0.00488 | -0.004194 | 0.2244 | 122.0725 | -0.075722 | 122.375 | 122.2673 | 0.19479 | 0.091562 | -0.20285 | 122.4719 | 122.4339 | 122.6624 | 122.3662 | -0.085926 | 122.3623 | 122.5296 | 122.2352 | 122.4293 | -0.36559
3331.0469 | 122.644 | -122.3373 | 0.091553 | 1.4211e-13 | -0.016833 | -0.014146 | -0.044957 | -0.041498 | -0.012138 | -0.0084697 | 0.021165 | 0.016858 | -0.030026 | 0.012508 | -0.019489 | 0.005626 | 0.0243 | 0.000747 | 0.1208 | 0.091937 | 0.30222 | 0.010206 | 0.019362 | 0.078197 | -0.070087 | 0.011252 | 0.18311 | -0.097557 | -0.26946 | 122.3475 | 0.029251 | 122.343 | 122.3381 | -0.009459 | 0.000384 | 0.21066 | 122.0679 | -0.080301 | 122.3567 | 122.2673 | 0.19937 | 0.091562 | -0.18911 | 122.4581 | 122.4293 | 122.6396 | 122.3616 | -0.081347 | 122.3486 | 122.5205 | 122.2398 | 122.4155 | -0.36101
3332.7812 | 122.6669 | -122.3465 | 0.073242 | 1.4211e-13 | -0.016406 | -0.013505 | -0.04517 | -0.041925 | -0.011924 | -0.00083919 | 0.021165 | 0.017285 | -0.029813 | 0.012081 | -0.019276 | 0.001048 | 0.0243 | 0.005325 | 0.1208 | 0.087359 | 0.30222 | 0.010206 | 0.023941 | 0.078197 | -0.074666 | 0.020409 | 0.18311 | -0.12503 | -0.27404 | 122.3567 | 0.047562 | 122.3475 | 122.3518 | -0.004881 | 0.014117 | 0.22898 | 122.0725 | -0.052833 | 122.3704 | 122.2718 | 0.19937 | 0.10987 | -0.19827 | 122.4673 | 122.4339 | 122.6487 | 122.3708 | -0.063036 | 122.3669 | 122.5296 | 122.2215 | 122.4247 | -0.34728
3334.5938 | 122.5204 | -122.4014 | 0.13275 | 1.4211e-13 | -0.016406 | -0.013505 | -0.04517 | -0.041711 | -0.012138 | 0.0067908 | 0.020951 | 0.017499 | -0.029813 | 0.012295 | -0.019276 | 0.005626 | 0.028878 | 0.005325 | 0.11622 | 0.096516 | 0.30222 | 0.005627 | 0.023941 | 0.078197 | -0.074666 | 0.015831 | 0.18311 | -0.11129 | -0.27404 | 122.4071 | -0.016526 | 122.4071 | 122.4068 | -0.000302 | -0.036235 | 0.16947 | 122.1274 | -0.11692 | 122.4254 | 122.3268 | 0.19937 | 0.050364 | -0.24404 | 122.5177 | 122.4979 | 122.7036 | 122.4303 | -0.12712 | 122.4173 | 122.5845 | 122.2901 | 122.4796 | -0.40679
3336.3906 | 122.644 | -122.3877 | 0.082397 | 1.4211e-13 | -0.016619 | -0.013291 | -0.045598 | -0.041711 | -0.011924 | -0.00083919 | 0.021165 | 0.017285 | -0.03024 | 0.012081 | -0.019489 | 0.005626 | 0.019721 | 0.000747 | 0.1208 | 0.091937 | 0.3068 | 0.014784 | 0.019362 | 0.078197 | -0.070087 | 0.015831 | 0.17396 | -0.092979 | -0.26946 | 122.4025 | 0.038407 | 122.3933 | 122.3884 | -0.014037 | 0.00954 | 0.2244 | 122.1182 | -0.066566 | 122.4071 | 122.3176 | 0.19937 | 0.091561 | -0.17538 | 122.5085 | 122.4796 | 122.6945 | 122.4074 | -0.067613 | 122.4035 | 122.5617 | 122.2947 | 122.4659 | -0.35186
3338.125 | 122.6257 | -122.3648 | 0.07782 | 1.4211e-13 | -0.016619 | -0.013505 | -0.04517 | -0.042139 | -0.012138 | -0.0084697 | 0.021592 | 0.017712 | -0.029599 | 0.012081 | -0.019276 | 0.005626 | 0.0243 | 0.000747 | 0.1208 | 0.096516 | 0.3068 | 0.010206 | 0.023941 | 0.087354 | -0.070087 | 0.015831 | 0.17396 | -0.11587 | -0.26946 | 122.375 | 0.042984 | 122.3704 | 122.3656 | -0.009459 | 0.018696 | 0.22898 | 122.0953 | -0.061989 | 122.3887 | 122.2947 | 0.19937 | 0.096138 | -0.19369 | 122.4856 | 122.4613 | 122.6716 | 122.3891 | -0.067614 | 122.3806 | 122.5388 | 122.2489 | 122.4522 | -0.34728
3339.9219 | 122.6349 | -122.3373 | 0.11444 | 1.4211e-13 | -0.016406 | -0.013505 | -0.044957 | -0.041711 | -0.012138 | -0.0161 | 0.021379 | 0.017499 | -0.029813 | 0.012081 | -0.019489 | 0.010204 | 0.010564 | 0.000747 | 0.11165 | 0.091937 | 0.30222 | 0.010206 | 0.023941 | 0.082776 | -0.079245 | 0.015831 | 0.18769 | -0.097557 | -0.26946 | 122.3475 | -0.002794 | 122.3475 | 122.3381 | -0.009459 | -0.022504 | 0.18778 | 122.0679 | -0.09861 | 122.3613 | 122.2581 | 0.19022 | 0.073252 | -0.212 | 122.449 | 122.4293 | 122.6396 | 122.3479 | -0.10423 | 122.3532 | 122.525 | 122.2398 | 122.4201 | -0.3839
3341.6562 | 122.6578 | -122.3969 | 0.086975 | 1.4211e-13 | -0.016406 | -0.013505 | -0.045384 | -0.042139 | -0.012352 | -0.00083919 | 0.021592 | 0.017712 | -0.029599 | 0.012081 | -0.019276 | 0.005626 | 0.019721 | 0.005325 | 0.11622 | 0.096516 | 0.29764 | 0.010206 | 0.023941 | 0.078197 | -0.079245 | 0.015831 | 0.16938 | -0.11587 | -0.26946 | 122.4071 | 0.02925 | 122.4025 | 122.4022 | -0.004881 | 0.009541 | 0.21066 | 122.1274 | -0.071144 | 122.4208 | 122.3176 | 0.19022 | 0.082404 | -0.20285 | 122.5131 | 122.4934 | 122.6945 | 122.4166 | -0.076769 | 122.4127 | 122.5662 | 122.281 | 122.475 | -0.35644
3343.4531 | 122.6578 | -122.3969 | 0.086975 | 1.4211e-13 | -0.016406 | -0.013077 | -0.044529 | -0.041711 | -0.012138 | -0.0084697 | 0.021592 | 0.017712 | -0.030026 | 0.012081 | -0.019062 | 0.001048 | 0.015142 | -0.003831 | 0.1208 | 0.08278 | 0.30222 | 0.014784 | 0.023941 | 0.087354 | -0.070087 | 0.020409 | 0.18769 | -0.11587 | -0.26946 | 122.4116 | 0.033829 | 122.3979 | 122.393 | -0.018615 | -0.004195 | 0.21524 | 122.1274 | -0.066566 | 122.4208 | 122.3268 | 0.19937 | 0.10072 | -0.20285 | 122.5177 | 122.4796 | 122.6991 | 122.412 | -0.072191 | 122.4173 | 122.5845 | 122.281 | 122.4842 | -0.35644
3345.1719 | 122.6486 | -122.3923 | 0.082397 | 1.4211e-13 | -0.016406 | -0.013505 | -0.045384 | -0.041284 | -0.012138 | -0.0161 | 0.021165 | 0.017285 | -0.029172 | 0.012081 | -0.019489 | 0.001048 | 0.0243 | 0.005325 | 0.11622 | 0.1011 | 0.31137 | 0.014784 | 0.019362 | 0.078197 | -0.070087 | 0.020409 | 0.17854 | -0.11587 | -0.26488 | 122.4071 | 0.033828 | 122.3933 | 122.3976 | -0.009459 | 0.018698 | 0.22898 | 122.1274 | -0.061988 | 122.4116 | 122.3222 | 0.1948 | 0.096139 | -0.19827 | 122.5085 | 122.4934 | 122.7036 | 122.4166 | -0.067613 | 122.4127 | 122.5708 | 122.2764 | 122.4705 | -0.34728
3346.9688 | 122.5296 | -122.4289 | 0.12817 | 1.4211e-13 | -0.016619 | -0.013505 | -0.044957 | -0.041498 | -0.012352 | -0.0084697 | 0.021165 | 0.017285 | -0.028958 | 0.012295 | -0.019489 | 0.001048 | 0.015142 | -0.003831 | 0.11622 | 0.091937 | 0.3068 | 0.005627 | 0.019362 | 0.078197 | -0.074666 | 0.020409 | 0.18769 | -0.11129 | -0.26488 | 122.4345 | -0.011949 | 122.4299 | 122.4251 | -0.009458 | -0.036237 | 0.17862 | 122.164 | -0.10777 | 122.4483 | 122.3542 | 0.19022 | 0.059519 | -0.23947 | 122.5451 | 122.5208 | 122.7357 | 122.444 | -0.12255 | 122.4493 | 122.6166 | 122.3176 | 122.5071 | -0.39306
3348.7656 | 122.6852 | -122.4014 | 0.082397 | 1.4211e-13 | -0.016619 | -0.013291 | -0.044957 | -0.041925 | -0.011924 | -0.0084697 | 0.021379 | 0.017499 | -0.029172 | 0.012081 | -0.019489 | 0.001048 | 0.0243 | -0.008409 | 0.11622 | 0.091937 | 0.3068 | 0.010206 | 0.023941 | 0.078197 | -0.070087 | 0.020409 | 0.18311 | -0.092979 | -0.26488 | 122.4116 | 0.033828 | 122.4025 | 122.393 | -0.018615 | 0.00954 | 0.2244 | 122.1365 | -0.061988 | 122.4254 | 122.3313 | 0.1948 | 0.10072 | -0.17538 | 122.5177 | 122.4934 | 122.7082 | 122.4257 | -0.072191 | 122.4218 | 122.5845 | 122.3084 | 122.4796 | -0.34728
3350.5 | 122.5204 | -121.9482 | 0.36163 | 1.4211e-13 | -0.016619 | -0.013505 | -0.04517 | -0.042139 | -0.012565 | -0.00083919 | 0.5747 | 0.58006 | 0.32057 | 0.012295 | -0.019062 | 0.028518 | 0.047193 | 0.01906 | 0.14827 | 0.11483 | 0.32969 | 0.023942 | 0.042256 | 0.096512 | -0.047194 | 0.14861 | 0.31132 | 0.14053 | -0.25572 | 121.9722 | -0.21336 | 121.9768 | 121.9673 | -0.004882 | -0.2468 | -0.031944 | 121.6925 | -0.21303 | 121.9905 | 121.901 | 0.20853 | -0.050317 | -0.2211 | 122.0965 | 122.0631 | 122.2779 | 121.9954 | -0.33769 | 122.0968 | 122.2596 | 122.0888 | 122.0448 | -0.61736
3352.2812 | 119.7144 | -91.1819 | 28.3218 | 1.4211e-13 | 0.0081665 | -0.047052 | -0.036837 | -0.041284 | -0.012993 | 0.0067908 | 0.010056 | 0.03566 | -0.027249 | 0.012508 | -0.019276 | 0.65576 | 0.6241 | 0.64628 | 0.78009 | 0.73757 | 0.97527 | 0.44978 | -0.003531 | 0.046146 | -0.097559 | -0.016219 | 0.15564 | -0.13876 | -0.29693 | 91.6317 | -27.5417 | 91.8377 | 91.8282 | 0.1965 | -27.5843 | -27.3466 | 90.885 | -28.3381 | 91.1784 | 91.0844 | 0.19937 | -28.1662 | -28.4606 | 91.962 | 91.9195 | 92.1572 | 91.806 | -27.8721 | 91.1657 | 91.3376 | 91.0432 | 91.2281 | -28.6188
3354.0781 | 122.1451 | -121.6003 | 0.24261 | 1.4211e-13 | -0.016406 | -0.013505 | -0.044957 | -0.041498 | -0.012352 | -0.0084697 | 0.0096286 | 0.034591 | -0.026821 | 0.012295 | -0.019276 | 0.010204 | 0.019721 | 0.005325 | 0.1208 | 0.091937 | 0.31137 | 0.010206 | 0.019362 | 0.078197 | -0.074666 | 0.015831 | 0.18311 | -0.11129 | -0.27404 | 121.6105 | -0.12181 | 121.6105 | 121.6057 | -0.004881 | -0.15068 | 0.068759 | 121.3263 | -0.22678 | 121.6197 | 121.5257 | 0.19937 | -0.0595 | -0.35391 | 121.7211 | 121.6923 | 121.9117 | 121.6201 | -0.23241 | 121.6162 | 121.7835 | 121.489 | 121.6785 | -0.51665
3355.7969 | 122.0673 | -121.3898 | 0.50354 | 1.4211e-13 | -0.016619 | -0.013718 | -0.04517 | -0.041498 | -0.012138 | 0.0067908 | 0.0098422 | 0.034378 | -0.027035 | 0.012508 | -0.019489 | 0.005626 | 0.019721 | 0.005325 | 0.1208 | 0.096516 | 0.3068 | -0.017268 | 0.019362 | 0.078197 | -0.074666 | 0.020409 | 0.18311 | -0.12045 | -0.27862 | 121.3725 | -0.38274 | 121.3954 | 121.3951 | 0.022593 | -0.40702 | -0.19674 | 121.1112 | -0.48313 | 121.4091 | 121.3151 | 0.20395 | -0.32042 | -0.62399 | 121.5106 | 121.4863 | 121.6966 | 121.4095 | -0.52081 | 121.4102 | 121.5729 | 121.2693 | 121.468 | -0.78216
3357.5938 | 122.2137 | -122.0123 | 0.1236 | 1.4211e-13 | -0.016619 | -0.013505 | -0.044957 | -0.041925 | -0.012138 | -0.0084697 | 0.0098422 | 0.034164 | -0.026821 | 0.012508 | -0.019062 | 0.005626 | 0.028878 | -0.003831 | 0.1208 | 0.091937 | 0.3068 | 0.014784 | 0.014784 | 0.082776 | -0.070087 | 0.020409 | 0.18311 | -0.12045 | -0.26946 | 122.0271 | -0.002792 | 122.018 | 122.0085 | -0.018615 | -0.031659 | 0.1832 | 121.7429 | -0.10319 | 122.0271 | 121.9422 | 0.19937 | 0.059519 | -0.24405 | 122.1331 | 122.1043 | 122.3191 | 122.0412 | -0.10881 | 122.0327 | 122.1954 | 121.8919 | 122.0951 | -0.39306
3359.3906 | 122.1176 | -121.8933 | 0.21057 | 1.4211e-13 | -0.016619 | -0.013291 | -0.04517 | -0.041498 | -0.011924 | -0.00083919 | 0.0096286 | 0.034805 | -0.026608 | 0.012508 | -0.018848 | 0.010204 | 0.019721 | 0.000747 | 0.11165 | 0.087359 | 0.3068 | -0.003531 | 0.014784 | 0.078197 | -0.079245 | 0.006674 | 0.18311 | -0.11129 | -0.27404 | 121.8898 | -0.098924 | 121.9035 | 121.8941 | 0.004278 | -0.12321 | 0.096225 | 121.6193 | -0.2039 | 121.9081 | 121.8141 | 0.19479 | -0.027456 | -0.32186 | 122.005 | 121.9807 | 122.2001 | 121.913 | -0.2141 | 121.9 | 122.0764 | 121.782 | 121.9715 | -0.48461
3361.1719 | 122.3145 | -121.9803 | 0.09613 | 1.4211e-13 | -0.016406 | -0.013718 | -0.044957 | -0.041925 | -0.012138 | -0.00083919 | 0.009415 | 0.034378 | -0.026821 | 0.012081 | -0.019276 | 0.005626 | 0.015142 | 0.000747 | 0.11165 | 0.1011 | 0.3068 | -0.00811 | 0.023941 | 0.082776 | -0.074666 | 0.011252 | 0.17854 | -0.12045 | -0.26946 | 121.9722 | 0.015517 | 121.9859 | 121.981 | 0.008857 | 0.004965 | 0.21067 | 121.7108 | -0.084878 | 122.0042 | 121.9056 | 0.1948 | 0.082406 | -0.21658 | 122.0919 | 122.0814 | 122.2871 | 121.9954 | -0.10424 | 121.9915 | 122.1588 | 121.8598 | 122.0631 | -0.36559
3362.9062 | 122.2595 | -122.049 | 0.10986 | 1.4211e-13 | -0.016406 | -0.013291 | -0.04517 | -0.041711 | -0.012138 | 0.0067908 | 0.0089876 | 0.034591 | -0.026608 | 0.012295 | -0.019062 | 0.001048 | 0.015142 | 0.000747 | 0.11622 | 0.091937 | 0.30222 | 0.005627 | 0.019362 | 0.078197 | -0.074666 | 0.015831 | 0.17396 | -0.11587 | -0.26488 | 122.0546 | 0.006362 | 122.05 | 122.0497 | -0.00488 | -0.017926 | 0.19235 | 121.7841 | -0.094032 | 122.0683 | 121.9743 | 0.19022 | 0.064095 | -0.22574 | 122.1652 | 122.1409 | 122.3512 | 122.0641 | -0.10424 | 122.0648 | 122.2229 | 121.9331 | 122.1271 | -0.37475
3364.6875 | 122.3419 | -122.0261 | 0.07782 | 1.4211e-13 | -0.016619 | -0.014146 | -0.045384 | -0.041498 | -0.012352 | -0.0084697 | 0.0098422 | 0.034805 | -0.026821 | 0.012295 | -0.019276 | 0.005626 | 0.015142 | 0.000747 | 0.1208 | 0.096516 | 0.3068 | -0.012689 | 0.023941 | 0.073618 | -0.065509 | 0.020409 | 0.18311 | -0.12045 | -0.26946 | 122.0134 | 0.042984 | 122.0317 | 122.0268 | 0.013436 | 0.018696 | 0.22898 | 121.7566 | -0.057411 | 122.05 | 121.9606 | 0.20395 | 0.10529 | -0.19827 | 122.1469 | 122.1226 | 122.3329 | 122.0412 | -0.090509 | 122.0465 | 122.2092 | 121.9056 | 122.0997 | -0.34728
3366.4688 | 122.2183 | -122.0444 | 0.15564 | 1.4211e-13 | -0.016406 | -0.013505 | -0.044957 | -0.041925 | -0.011924 | -0.0084697 | 0.0096286 | 0.034591 | -0.027035 | 0.012508 | -0.019276 | -0.003531 | 0.015142 | 0.000747 | 0.11622 | 0.091937 | 0.31137 | -0.012689 | 0.023941 | 0.078197 | -0.074666 | 0.011252 | 0.17396 | -0.10671 | -0.26946 | 122.0317 | -0.039415 | 122.0408 | 122.0451 | 0.013436 | -0.063703 | 0.15573 | 121.7749 | -0.14439 | 122.0683 | 121.9697 | 0.1948 | 0.018318 | -0.26235 | 122.1606 | 122.1363 | 122.3557 | 122.0595 | -0.16833 | 122.0556 | 122.2183 | 121.9377 | 122.1226 | -0.4251
3368.25 | 122.2549 | -122.1176 | 0.13733 | 1.4211e-13 | -0.016619 | -0.013932 | -0.04517 | -0.041711 | -0.011711 | -0.00083919 | 0.009415 | 0.034378 | -0.026821 | 0.012081 | -0.019062 | 0.005626 | 0.028878 | 0.000747 | 0.12538 | 0.096516 | 0.31595 | 0.001048 | 0.019362 | 0.078197 | -0.070087 | 0.011252 | 0.18311 | -0.11587 | -0.26946 | 122.1187 | -0.011947 | 122.1232 | 122.1184 | -0.000301 | -0.040813 | 0.17862 | 121.8482 | -0.12608 | 122.137 | 122.0475 | 0.19937 | 0.045786 | -0.2532 | 122.243 | 122.2141 | 122.4336 | 122.1465 | -0.13628 | 122.1289 | 122.3007 | 122.0017 | 122.1958 | -0.40679
3370.0469 | 122.1817 | -122.0901 | 0.10071 | 1.4211e-13 | -0.016619 | -0.013505 | -0.04517 | -0.042139 | -0.012352 | -0.00083919 | 0.0096286 | 0.034378 | -0.026821 | 0.012081 | -0.019276 | 0.001048 | 0.015142 | -0.008409 | 0.1208 | 0.091937 | 0.31137 | -0.031005 | 0.023941 | 0.082776 | -0.065509 | 0.020409 | 0.18311 | -0.12045 | -0.26488 | 122.0591 | 0.020096 | 122.0912 | 122.0817 | 0.022596 | -0.008771 | 0.21067 | 121.8253 | -0.080299 | 122.1141 | 122.0246 | 0.19937 | 0.082407 | -0.22116 | 122.211 | 122.1821 | 122.4015 | 122.1053 | -0.13171 | 122.1106 | 122.2733 | 121.9697 | 122.1729 | -0.36559
3371.7812 | 122.2687 | -122.1268 | 0.13733 | 1.4211e-13 | -0.016833 | -0.013505 | -0.044957 | -0.041498 | -0.012138 | -0.00083919 | 0.009415 | 0.034164 | -0.027035 | 0.012295 | -0.019276 | 0.001048 | 0.019721 | 0.000747 | 0.11165 | 0.091937 | 0.29764 | 0.005627 | 0.023941 | 0.078197 | -0.070087 | 0.011252 | 0.18311 | -0.10214 | -0.27404 | 122.1324 | -0.025682 | 122.1278 | 122.1275 | -0.00488 | -0.045392 | 0.16031 | 121.8527 | -0.12608 | 122.1507 | 122.0567 | 0.20395 | 0.045786 | -0.23947 | 122.2384 | 122.2187 | 122.4244 | 122.1465 | -0.1317 | 122.138 | 122.3099 | 122.0246 | 122.205 | -0.41137
3373.5781 | 122.3602 | -122.1222 | 0.12817 | 1.4211e-13 | -0.016833 | -0.013505 | -0.04517 | -0.041711 | -0.012138 | -0.00083919 | 0.0092014 | 0.034805 | -0.026821 | 0.012295 | -0.019276 | 0.001048 | 0.019721 | 0.000747 | 0.11622 | 0.091937 | 0.31137 | 0.010206 | 0.023941 | 0.078197 | -0.065509 | 0.011252 | 0.18311 | -0.12045 | -0.27862 | 122.1324 | -0.011949 | 122.1232 | 122.1229 | -0.009459 | -0.036237 | 0.1832 | 121.8436 | -0.11692 | 122.1461 | 122.0567 | 0.21311 | 0.054941 | -0.24862 | 122.2384 | 122.2141 | 122.4336 | 122.1419 | -0.11797 | 122.1334 | 122.3053 | 122.0017 | 122.2004 | -0.40679
3375.3594 | 122.4152 | -122.1039 | 0.10986 | 1.4211e-13 | -0.016619 | -0.013718 | -0.045384 | -0.041284 | -0.011924 | -0.0084697 | 0.009415 | 0.034378 | -0.026821 | 0.012508 | -0.019489 | 0.005626 | 0.019721 | 0.000747 | 0.11165 | 0.087359 | 0.3068 | 0.005627 | 0.023941 | 0.087354 | -0.070087 | 0.015831 | 0.18311 | -0.060928 | -0.27404 | 122.1095 | 0.001784 | 122.1095 | 122.1046 | -0.00488 | -0.022504 | 0.19693 | 121.8298 | -0.094032 | 122.1278 | 122.0338 | 0.20395 | 0.073252 | -0.17079 | 122.2155 | 122.1912 | 122.4107 | 122.1236 | -0.10424 | 122.1197 | 122.287 | 122.043 | 122.1912 | -0.3839
3377.0781 | 122.438 | -122.1313 | 0.09613 | 1.4211e-13 | -0.016619 | -0.013718 | -0.04517 | -0.041498 | -0.012352 | -0.00083919 | 0.0089876 | 0.034591 | -0.027035 | 0.012081 | -0.019489 | 0.005626 | 0.0243 | 0.000747 | 0.11622 | 0.087359 | 0.31137 | -0.00811 | 0.023941 | 0.073618 | -0.06093 | 0.015831 | 0.18311 | -0.042614 | -0.26946 | 122.1232 | 0.020095 | 122.137 | 122.1321 | 0.008857 | -0.008771 | 0.21524 | 121.8619 | -0.080299 | 122.1553 | 122.0704 | 0.20853 | 0.086985 | -0.13874 | 122.2476 | 122.2187 | 122.4427 | 122.1556 | -0.10424 | 122.1472 | 122.3145 | 122.0887 | 122.205 | -0.36559
3378.875 | 122.2778 | -122.1588 | 0.14191 | 1.4211e-13 | -0.016619 | -0.013718 | -0.04517 | -0.041711 | -0.011924 | -0.0084697 | 0.0092014 | 0.034378 | -0.026821 | 0.012295 | -0.019062 | 0.001048 | 0.015142 | 0.000747 | 0.11622 | 0.087359 | 0.3068 | 0.010206 | 0.023941 | 0.073618 | -0.074666 | 0.020409 | 0.18769 | -0.11587 | -0.26488 | 122.169 | -0.025682 | 122.1599 | 122.1596 | -0.009459 | -0.054548 | 0.16489 | 121.8939 | -0.1215 | 122.1828 | 122.0841 | 0.19022 | 0.045786 | -0.25778 | 122.275 | 122.2462 | 122.4656 | 122.174 | -0.1317 | 122.1792 | 122.3465 | 122.0429 | 122.2324 | -0.40679
3380.6562 | 122.4106 | -122.1268 | 0.086975 | 1.4211e-13 | -0.016619 | -0.013718 | -0.044743 | -0.041925 | -0.012138 | 0.0067908 | 0.0096286 | 0.033309 | -0.026821 | 0.012508 | -0.019489 | 0.010204 | 0.019721 | -0.003831 | 0.11622 | 0.087359 | 0.31595 | -0.003531 | 0.019362 | 0.078197 | -0.079245 | 0.011252 | 0.18769 | -0.11587 | -0.26488 | 122.1232 | 0.02925 | 122.137 | 122.1229 | -0.0003 | 0.000384 | 0.22898 | 121.8619 | -0.075723 | 122.1461 | 122.0475 | 0.18564 | 0.10072 | -0.20285 | 122.243 | 122.2141 | 122.4427 | 122.1465 | -0.090506 | 122.138 | 122.3145 | 122.0109 | 122.205 | -0.35186
3382.4531 | 122.3785 | -121.6187 | 0.54016 | 1.4211e-13 | -0.016192 | -0.013932 | -0.044957 | -0.041711 | -0.012138 | -0.00083919 | 0.009415 | 0.033523 | -0.026821 | 0.012295 | -0.019276 | 0.014783 | 0.028878 | 0.005325 | 0.12538 | 0.1011 | 0.31595 | 0.037679 | 0.019362 | 0.078197 | -0.074666 | 0.006674 | 0.17854 | -0.11587 | -0.26946 | 121.6563 | -0.41478 | 121.6334 | 121.624 | -0.032354 | -0.43907 | -0.22421 | 121.3492 | -0.53349 | 121.638 | 121.544 | 0.1948 | -0.36162 | -0.65603 | 121.744 | 121.7197 | 121.9346 | 121.6475 | -0.50248 | 121.6253 | 121.7972 | 121.5028 | 121.6968 | -0.80962
3384.1875 | 122.4335 | -122.1497 | 0.09613 | 1.4211e-13 | -0.016406 | -0.013291 | -0.044957 | -0.041498 | -0.012352 | 0.0067908 | 0.009415 | 0.033523 | -0.026821 | 0.012295 | -0.018848 | 0.005626 | 0.019721 | -0.003831 | 0.11622 | 0.091937 | 0.31137 | 0.001048 | 0.023941 | 0.082776 | -0.070087 | 0.011252 | 0.17854 | -0.11129 | -0.26946 | 122.1507 | 0.020095 | 122.1553 | 122.1458 | -0.004879 | -0.004193 | 0.21524 | 121.8802 | -0.084878 | 122.1736 | 122.0796 | 0.19937 | 0.082406 | -0.20742 | 122.2659 | 122.2416 | 122.461 | 122.1694 | -0.095082 | 122.1609 | 122.3282 | 122.0384 | 122.2324 | -0.36559
3385.9688 | 122.3419 | -122.2321 | 0.13733 | 1.4211e-13 | -0.016406 | -0.013505 | -0.044957 | -0.041925 | -0.012138 | -0.00083919 | 0.0092014 | 0.033309 | -0.026821 | 0.012295 | -0.019489 | 0.005626 | 0.015142 | -0.003831 | 0.11622 | 0.096516 | 0.31137 | 0.001048 | 0.02852 | 0.06904 | -0.065509 | 0.015831 | 0.17396 | -0.11129 | -0.27404 | 122.2331 | -0.021104 | 122.2377 | 122.2282 | -0.004879 | -0.040813 | 0.17404 | 121.958 | -0.1215 | 122.2606 | 122.1665 | 0.20853 | 0.036629 | -0.24862 | 122.3483 | 122.3286 | 122.5434 | 122.2472 | -0.13628 | 122.2479 | 122.406 | 122.1208 | 122.3011 | -0.41137
3387.75 | 122.4747 | -122.1588 | 0.10529 | 1.4211e-13 | -0.016619 | -0.013505 | -0.044957 | -0.041711 | -0.011924 | 0.0067908 | 0.009415 | 0.033523 | -0.027035 | 0.012295 | -0.019062 | 0.001048 | 0.019721 | -0.003831 | 0.1208 | 0.091937 | 0.31137 | 0.001048 | 0.033099 | 0.078197 | -0.074666 | 0.011252 | 0.18311 | -0.11587 | -0.26946 | 122.1599 | 0.015518 | 122.1599 | 122.155 | -0.004879 | -0.013349 | 0.20609 | 121.8894 | -0.094034 | 122.1919 | 122.0841 | 0.1948 | 0.077829 | -0.22116 | 122.2796 | 122.2507 | 122.4702 | 122.1785 | -0.10424 | 122.1701 | 122.3419 | 122.0429 | 122.237 | -0.37475
3389.4844 | 122.4197 | -122.1313 | 0.16937 | 1.4211e-13 | -0.016619 | -0.013291 | -0.044957 | -0.041711 | -0.012138 | -0.00083919 | 0.009415 | 0.033309 | -0.026821 | 0.012508 | -0.019276 | 0.010204 | 0.0243 | 0.005325 | 0.11622 | 0.091937 | 0.30222 | -0.017268 | 0.014784 | 0.078197 | -0.065509 | 0.015831 | 0.17854 | -0.11587 | -0.26488 | 122.1141 | -0.053148 | 122.1416 | 122.1367 | 0.022593 | -0.077436 | 0.13284 | 121.8665 | -0.15354 | 122.1461 | 122.0658 | 0.19937 | 0.009163 | -0.28524 | 122.2476 | 122.2233 | 122.4336 | 122.1556 | -0.18664 | 122.1472 | 122.3099 | 122.0155 | 122.2095 | -0.43426
3391.2656 | 122.3785 | -122.2046 | 0.12817 | 1.4211e-13 | -0.016406 | -0.013932 | -0.045384 | -0.041711 | -0.012565 | -0.0084697 | 0.0092014 | 0.033523 | -0.026821 | 0.012081 | -0.019489 | 0.005626 | 0.015142 | 0.000747 | 0.11622 | 0.091937 | 0.31137 | 0.001048 | 0.023941 | 0.078197 | -0.079245 | 0.011252 | 0.18311 | -0.05635 | -0.26946 | 122.2056 | -0.011949 | 122.2102 | 122.2053 | -0.000301 | -0.036237 | 0.1832 | 121.9351 | -0.11692 | 122.2285 | 122.1253 | 0.19022 | 0.054941 | -0.18452 | 122.3208 | 122.2965 | 122.516 | 122.2197 | -0.12713 | 122.2158 | 122.3877 | 122.1482 | 122.2828 | -0.39764
3393 | 122.374 | -122.2229 | 0.14191 | 1.4211e-13 | -0.016406 | -0.013291 | -0.04517 | -0.041711 | -0.011924 | -0.0084697 | 0.0092014 | 0.033523 | -0.027035 | 0.012508 | -0.019276 | 0.010204 | 0.0243 | 0.000747 | 0.1208 | 0.091937 | 0.3068 | 0.014784 | 0.014784 | 0.06904 | -0.070087 | 0.011252 | 0.17854 | -0.11129 | -0.26488 | 122.2377 | -0.021103 | 122.2331 | 122.2236 | -0.014037 | -0.04997 | 0.16489 | 121.958 | -0.13065 | 122.2377 | 122.1528 | 0.1948 | 0.036629 | -0.2532 | 122.3437 | 122.3148 | 122.5297 | 122.2472 | -0.12712 | 122.2342 | 122.4014 | 122.1116 | 122.2919 | -0.40679
3394.7969 | 122.4884 | -122.1909 | 0.09613 | 1.4211e-13 | -0.017047 | -0.013505 | -0.044957 | -0.042139 | -0.012352 | 0.0067908 | 0.0092014 | 0.033523 | -0.026821 | 0.012722 | -0.019489 | 0.005626 | 0.0243 | 0.000747 | 0.1208 | 0.091937 | 0.30222 | 0.014784 | 0.019362 | 0.078197 | -0.065509 | 0.006674 | 0.17854 | -0.11587 | -0.26946 | 122.2056 | 0.024674 | 122.1965 | 122.1916 | -0.014037 | -0.004193 | 0.20609 | 121.9214 | -0.089456 | 122.2102 | 122.1253 | 0.20395 | 0.082406 | -0.212 | 122.3117 | 122.2828 | 122.4931 | 122.2152 | -0.081346 | 122.1975 | 122.3694 | 122.075 | 122.2691 | -0.36559
3396.5938 | 122.5159 | -122.2183 | 0.07782 | 1.4211e-13 | -0.016833 | -0.013505 | -0.044957 | -0.041498 | -0.012352 | -0.00083919 | 0.0092014 | 0.033523 | -0.027249 | 0.012295 | -0.019489 | 0.005626 | 0.019721 | 0.005325 | 0.11622 | 0.091937 | 0.3068 | 0.010206 | 0.019362 | 0.078197 | -0.070087 | 0.015831 | 0.16938 | -0.12503 | -0.26488 | 122.2285 | 0.038405 | 122.2239 | 122.2236 | -0.004881 | 0.014117 | 0.22898 | 121.9534 | -0.061989 | 122.2377 | 122.1482 | 0.1948 | 0.091559 | -0.20285 | 122.3345 | 122.3103 | 122.5251 | 122.238 | -0.067614 | 122.2342 | 122.3877 | 122.0933 | 122.2965 | -0.3427
3398.3906 | 122.3465 | -122.2229 | 0.17395 | 1.4211e-13 | -0.016833 | -0.013505 | -0.04517 | -0.041925 | -0.012352 | -0.0084697 | 0.0092014 | 0.033737 | -0.027035 | 0.012508 | -0.019489 | 0.005626 | 0.0243 | -0.003831 | 0.11165 | 0.091937 | 0.3068 | -0.040163 | 0.023941 | 0.078197 | -0.06093 | 0.015831 | 0.18311 | -0.11129 | -0.26946 | 122.1827 | -0.062303 | 122.2285 | 122.2191 | 0.036332 | -0.082013 | 0.13285 | 121.9534 | -0.15812 | 122.2468 | 122.162 | 0.20853 | 0.009165 | -0.28524 | 122.3345 | 122.3148 | 122.5297 | 122.2472 | -0.21411 | 122.2387 | 122.406 | 122.1116 | 122.3011 | -0.44341
3400.1094 | 122.4243 | -121.8887 | 0.32501 | 1.4211e-13 | -0.016833 | -0.013505 | -0.045384 | -0.041711 | -0.012352 | -0.0084697 | 0.0096286 | 0.033523 | -0.026608 | 0.012508 | -0.019489 | 0.001048 | 0.015142 | 0.005325 | 0.1208 | 0.091937 | 0.3068 | -0.044742 | 0.019362 | 0.078197 | -0.065509 | 0.015831 | 0.17854 | -0.11129 | -0.26488 | 121.844 | -0.20421 | 121.8898 | 121.8941 | 0.050067 | -0.23308 | -0.018216 | 121.6239 | -0.30918 | 121.9081 | 121.8232 | 0.19937 | -0.14648 | -0.43631 | 122.0095 | 121.9807 | 122.1955 | 121.9039 | -0.36975 | 121.9046 | 122.0673 | 121.7774 | 121.9669 | -0.5899
3401.9062 | 122.2641 | -121.6736 | 0.47607 | 1.4211e-13 | -0.016406 | -0.013505 | -0.04517 | -0.041925 | -0.012138 | -0.00083919 | 0.0098422 | 0.033737 | -0.026821 | 0.012508 | -0.019489 | 0.005626 | 0.0243 | 0.014482 | 0.12538 | 0.1011 | 0.32053 | -0.003531 | 0.023941 | 0.073618 | -0.074666 | 0.015831 | 0.17396 | -0.11587 | -0.26946 | 121.6701 | -0.35069 | 121.6792 | 121.6881 | 0.018013 | -0.37498 | -0.15554 | 121.4041 | -0.46024 | 121.6975 | 121.5989 | 0.1948 | -0.30212 | -0.59195 | 121.799 | 121.7747 | 121.9941 | 121.6979 | -0.47961 | 121.6894 | 121.8475 | 121.5577 | 121.7472 | -0.74554
3403.6562 | 122.2229 | -121.2936 | 0.72784 | 1.4211e-13 | -0.016833 | -0.013291 | -0.044957 | -0.041925 | -0.012565 | 0.0067908 | 0.0089876 | 0.033523 | -0.027035 | 0.012508 | -0.019062 | 0.014783 | 0.033457 | 0.014482 | 0.12538 | 0.10567 | 0.31595 | -0.00811 | 0.014784 | 0.078197 | -0.070087 | 0.006674 | 0.17396 | -0.10671 | -0.26488 | 121.2855 | -0.60246 | 121.3084 | 121.3081 | 0.022592 | -0.62217 | -0.41189 | 121.0288 | -0.72117 | 121.3084 | 121.2236 | 0.1948 | -0.55389 | -0.83456 | 121.419 | 121.3993 | 121.6096 | 121.3271 | -0.73595 | 121.3003 | 121.4676 | 121.1869 | 121.3718 | -0.99273
3405.4531 | 121.8842 | -120.9137 | 1.0437 | 1.4211e-13 | -0.016619 | -0.013291 | -0.045384 | -0.041711 | -0.012352 | -0.00083919 | 0.0089876 | 0.033523 | -0.026821 | 0.012295 | -0.019062 | 0.014783 | 0.033457 | 0.01906 | 0.13912 | 0.11483 | 0.32969 | 0.005627 | 0.023941 | 0.06904 | -0.074666 | 0.011252 | 0.17854 | -0.097557 | -0.2603 | 120.9193 | -0.90458 | 120.9285 | 120.9328 | 0.013433 | -0.92887 | -0.71401 | 120.6534 | -1.0324 | 120.9376 | 120.839 | 0.18564 | -0.86516 | -1.1413 | 121.0528 | 121.0285 | 121.2434 | 120.9472 | -1.0381 | 120.9249 | 121.0922 | 120.8161 | 120.9827 | -1.304
3407.2344 | 121.788 | -121.3348 | 0.15564 | 1.4211e-13 | -0.016619 | -0.013718 | -0.044957 | -0.041925 | -0.012138 | -0.00083919 | 0.0089876 | 0.033523 | -0.026608 | 0.012508 | -0.019276 | 0.010204 | 0.0243 | 0.005325 | 0.1208 | 0.091937 | 0.31137 | -0.003531 | 0.019362 | 0.082776 | -0.070087 | 0.020409 | 0.17396 | -0.12503 | -0.26488 | 121.3313 | -0.034836 | 121.345 | 121.3402 | 0.008856 | -0.063703 | 0.15573 | 121.07 | -0.13523 | 121.3542 | 121.2648 | 0.1948 | 0.018318 | -0.28067 | 121.4556 | 121.4268 | 121.6462 | 121.3591 | -0.15917 | 121.3552 | 121.5088 | 121.2098 | 121.4176 | -0.42052
3409.0469 | 121.8796 | -121.7148 | 0.11902 | 1.4211e-13 | -0.016833 | -0.013505 | -0.044957 | -0.041925 | -0.012138 | -0.00083919 | 0.0092014 | 0.033523 | -0.026608 | 0.012295 | -0.019276 | 0.005626 | 0.0243 | 0.000747 | 0.11622 | 0.091937 | 0.29764 | 0.005627 | 0.019362 | 0.078197 | -0.070087 | 0.015831 | 0.17396 | -0.11587 | -0.26946 | 121.7204 | -0.002794 | 121.7204 | 121.7155 | -0.00488 | -0.027082 | 0.17862 | 121.4453 | -0.10319 | 121.7341 | 121.6447 | 0.19937 | 0.054939 | -0.23489 | 121.831 | 121.8067 | 122.0124 | 121.7391 | -0.11339 | 121.7306 | 121.8887 | 121.5989 | 121.793 | -0.38848
3410.8281 | 122.1222 | -121.8155 | 0.091553 | 1.4211e-13 | -0.016619 | -0.013505 | -0.044957 | -0.042139 | -0.012352 | -0.0084697 | 0.009415 | 0.033737 | -0.026821 | 0.012295 | -0.019276 | 0.005626 | 0.010564 | -0.003831 | 0.12538 | 0.087359 | 0.30222 | 0.014784 | 0.02852 | 0.078197 | -0.065509 | 0.011252 | 0.18311 | -0.11587 | -0.26946 | 121.8303 | 0.033829 | 121.8211 | 121.8117 | -0.018615 | -0.004194 | 0.21066 | 121.546 | -0.080301 | 121.844 | 121.75 | 0.20395 | 0.091562 | -0.20742 | 121.9409 | 121.9029 | 122.1177 | 121.8261 | -0.076769 | 121.8267 | 121.9986 | 121.6996 | 121.8937 | -0.36101
3412.5625 | 122.1634 | -121.8567 | 0.086975 | 1.4211e-13 | -0.016619 | -0.013291 | -0.045384 | -0.041925 | -0.012352 | -0.00083919 | 0.0089876 | 0.033523 | -0.026821 | 0.012295 | -0.019489 | 0.010204 | 0.0243 | 0.009904 | 0.11165 | 0.096516 | 0.31595 | 0.014784 | 0.023941 | 0.082776 | -0.065509 | 0.015831 | 0.18311 | -0.11587 | -0.27404 | 121.8715 | 0.024672 | 121.8669 | 121.8666 | -0.00488 | 0.009541 | 0.22898 | 121.5826 | -0.071144 | 121.8806 | 121.7912 | 0.20853 | 0.09614 | -0.20285 | 121.9683 | 121.9532 | 122.1726 | 121.881 | -0.072191 | 121.8725 | 122.0398 | 121.7408 | 121.9395 | -0.36101
3414.3594 | 122.1909 | -121.9162 | 0.10071 | 1.4211e-13 | -0.016833 | -0.013505 | -0.04517 | -0.041925 | -0.011924 | -0.0084697 | 0.0089876 | 0.033309 | -0.026821 | 0.012508 | -0.019276 | 0.001048 | 0.019721 | -0.003831 | 0.11622 | 0.087359 | 0.30222 | 0.014784 | 0.023941 | 0.082776 | -0.074666 | 0.015831 | 0.17396 | -0.083821 | -0.26488 | 121.931 | 0.015517 | 121.9172 | 121.9124 | -0.018615 | -0.013349 | 0.20151 | 121.6513 | -0.084877 | 121.9401 | 121.8415 | 0.19022 | 0.07325 | -0.18453 | 122.0324 | 122.0036 | 122.2184 | 121.9359 | -0.085924 | 121.932 | 122.0902 | 121.8324 | 121.999 | -0.36559
3416.0781 | 122.1313 | -121.9345 | 0.1236 | 1.4211e-13 | -0.016833 | -0.013291 | -0.04517 | -0.042139 | -0.012138 | 0.0067908 | 0.0092014 | 0.033309 | -0.026608 | 0.012508 | -0.019062 | 0.001048 | 0.019721 | 0.000747 | 0.12538 | 0.091937 | 0.31137 | 0.001048 | 0.019362 | 0.078197 | -0.070087 | 0.020409 | 0.18311 | -0.10214 | -0.27404 | 121.9356 | 0.001786 | 121.9356 | 121.9353 | -0.000301 | -0.031659 | 0.18778 | 121.6605 | -0.10319 | 121.9539 | 121.8644 | 0.20395 | 0.059519 | -0.22573 | 122.0599 | 122.0264 | 122.2459 | 121.9542 | -0.12255 | 121.9549 | 122.1176 | 121.8324 | 122.0127 | -0.39764
3417.8438 | 122.1542 | -121.962 | 0.13275 | 1.4211e-13 | -0.016833 | -0.013505 | -0.044957 | -0.042139 | -0.012138 | -0.0084697 | 0.0096286 | 0.033309 | -0.026821 | 0.012508 | -0.019062 | 0.001048 | 0.015142 | -0.003831 | 0.1208 | 0.096516 | 0.30222 | -0.00811 | 0.023941 | 0.06904 | -0.070087 | 0.015831 | 0.17396 | -0.11587 | -0.25572 | 121.9539 | -0.011947 | 121.963 | 121.9581 | 0.004279 | -0.036235 | 0.16947 | 121.7062 | -0.11692 | 121.9859 | 121.8919 | 0.18564 | 0.041207 | -0.24862 | 122.0828 | 122.0585 | 122.2642 | 121.9771 | -0.14086 | 121.9778 | 122.1359 | 121.8461 | 122.031 | -0.38848
3419.6562 | 122.1909 | -121.994 | 0.11902 | 1.4211e-13 | -0.017047 | -0.013718 | -0.04517 | -0.041498 | -0.012352 | -0.00083919 | 0.0096286 | 0.033523 | -0.026821 | 0.012508 | -0.019062 | 0.001048 | 0.0243 | -0.003831 | 0.11622 | 0.087359 | 0.3068 | 0.014784 | 0.023941 | 0.082776 | -0.070087 | 0.015831 | 0.17854 | -0.083821 | -0.2603 | 122.0088 | -0.002794 | 121.9951 | 121.9902 | -0.018615 | -0.03166 | 0.18778 | 121.7337 | -0.10319 | 122.018 | 121.9239 | 0.19022 | 0.059517 | -0.20284 | 122.1102 | 122.0814 | 122.3008 | 122.0183 | -0.10423 | 122.0099 | 122.1726 | 121.9102 | 122.0768 | -0.37932
3421.3906 | 122.1313 | -121.994 | 0.13275 | 1.4211e-13 | -0.016619 | -0.013291 | -0.04517 | -0.041925 | -0.012138 | -0.0084697 | 0.0092014 | 0.033523 | -0.027035 | 0.012508 | -0.019276 | 0.010204 | 0.019721 | 0.000747 | 0.11622 | 0.096516 | 0.30222 | 0.014784 | 0.023941 | 0.078197 | -0.074666 | 0.011252 | 0.17396 | -0.10671 | -0.26488 | 122.0088 | -0.016526 | 122.0042 | 121.9948 | -0.014037 | -0.036235 | 0.16947 | 121.7291 | -0.1215 | 122.018 | 121.9194 | 0.19022 | 0.041207 | -0.23947 | 122.1102 | 122.0905 | 122.2962 | 122.0137 | -0.11797 | 122.0053 | 122.168 | 121.8873 | 122.0722 | -0.39763
3423.1875 | 122.2137 | -122.0032 | 0.10071 | 1.4211e-13 | -0.016619 | -0.013718 | -0.04517 | -0.041711 | -0.012352 | 0.0067908 | 0.009415 | 0.03395 | -0.026394 | 0.012508 | -0.019062 | 0.005626 | 0.0243 | -0.003831 | 0.11165 | 0.1011 | 0.3068 | 0.010206 | 0.02852 | 0.078197 | -0.074666 | 0.024988 | 0.17854 | -0.11587 | -0.2603 | 122.0134 | 0.010939 | 122.0088 | 121.9993 | -0.014037 | 0.000387 | 0.20609 | 121.7429 | -0.07572 | 122.0317 | 121.9285 | 0.18564 | 0.077828 | -0.21658 | 122.1148 | 122.1043 | 122.31 | 122.0275 | -0.090502 | 122.0282 | 122.1817 | 121.8873 | 122.0814 | -0.36101
3424.9219 | 122.2961 | -122.0169 | 0.091553 | 1.4211e-13 | -0.016833 | -0.013291 | -0.044743 | -0.041711 | -0.012352 | -0.0084697 | 0.009415 | 0.033309 | -0.026821 | 0.012722 | -0.019062 | 0.001048 | 0.019721 | 0.000747 | 0.12538 | 0.096516 | 0.3068 | 0.010206 | 0.019362 | 0.078197 | -0.074666 | 0.015831 | 0.17854 | -0.11129 | -0.26488 | 122.0271 | 0.033829 | 122.018 | 122.0177 | -0.009459 | 0.004963 | 0.21524 | 121.752 | -0.075722 | 122.0363 | 121.9422 | 0.19022 | 0.086983 | -0.20285 | 122.1423 | 122.1134 | 122.3237 | 122.0366 | -0.081347 | 122.0327 | 122.1954 | 121.9056 | 122.0951 | -0.35644
3426.7188 | 122.2321 | -122.0169 | 0.11444 | 1.4211e-13 | -0.017047 | -0.013505 | -0.04517 | -0.041498 | -0.012138 | -0.0161 | 0.009415 | 0.033309 | -0.026821 | 0.012508 | -0.019276 | 0.005626 | 0.0243 | 0.005325 | 0.11622 | 0.091937 | 0.3068 | 0.014784 | 0.014784 | 0.073618 | -0.070087 | 0.011252 | 0.18311 | -0.11587 | -0.2603 | 122.0317 | 0.001784 | 122.0225 | 122.0222 | -0.009459 | -0.022504 | 0.19235 | 121.7566 | -0.10319 | 122.0317 | 121.9468 | 0.19022 | 0.068674 | -0.23031 | 122.1331 | 122.1088 | 122.3237 | 122.0412 | -0.099657 | 122.0282 | 122.2 | 121.901 | 122.0905 | -0.37474
3428.5156 | 122.3419 | -122.0352 | 0.091553 | 1.4211e-13 | -0.016619 | -0.013505 | -0.04517 | -0.041711 | -0.012138 | -0.0084697 | 0.0089876 | 0.033523 | -0.026821 | 0.012508 | -0.019489 | 0.001048 | 0.019721 | 0.000747 | 0.12538 | 0.091937 | 0.3068 | 0.010206 | 0.019362 | 0.082776 | -0.079245 | 0.020409 | 0.17396 | -0.11129 | -0.2603 | 122.0454 | 0.033829 | 122.0363 | 122.036 | -0.009459 | 0.000384 | 0.21524 | 121.7749 | -0.071144 | 122.0546 | 121.956 | 0.18106 | 0.082405 | -0.20285 | 122.1606 | 122.1272 | 122.342 | 122.0549 | -0.081347 | 122.0556 | 122.2092 | 121.9239 | 122.118 | -0.35186
3430.3125 | 122.2137 | -122.081 | 0.11902 | 1.4211e-13 | -0.016833 | -0.013505 | -0.044957 | -0.041284 | -0.012138 | -0.0161 | 0.009415 | 0.033309 | -0.026821 | 0.012508 | -0.019062 | 0.001048 | 0.019721 | -0.008409 | 0.1208 | 0.091937 | 0.3068 | 0.010206 | 0.019362 | 0.078197 | -0.074666 | 0.015831 | 0.17854 | -0.11129 | -0.26488 | 122.0912 | 0.001785 | 122.082 | 122.0726 | -0.018615 | -0.027082 | 0.18778 | 121.8161 | -0.10319 | 122.1004 | 122.0063 | 0.19022 | 0.059517 | -0.23031 | 122.2018 | 122.1729 | 122.3878 | 122.1007 | -0.10881 | 122.0968 | 122.2595 | 121.9697 | 122.1592 | -0.3839
3432.0938 | 122.3648 | -122.049 | 0.09613 | 1.4211e-13 | -0.016833 | -0.013505 | -0.044957 | -0.041711 | -0.012138 | -0.00083919 | 0.009415 | 0.033096 | -0.026608 | 0.012508 | -0.019062 | 0.001048 | 0.019721 | -0.003831 | 0.1208 | 0.087359 | 0.30222 | 0.019363 | 0.023941 | 0.073618 | -0.070087 | 0.015831 | 0.18769 | -0.12503 | -0.26488 | 122.0683 | 0.024674 | 122.05 | 122.0451 | -0.023194 | -0.008771 | 0.20609 | 121.7841 | -0.080299 | 122.0729 | 121.9789 | 0.1948 | 0.091563 | -0.22116 | 122.1698 | 122.1363 | 122.3512 | 122.0687 | -0.076767 | 122.0648 | 122.2366 | 121.9239 | 122.1226 | -0.36101
3433.8125 | 122.2824 | -121.9666 | 0.14648 | 1.4211e-13 | -0.016619 | -0.013505 | -0.04517 | -0.041925 | -0.012138 | -0.0084697 | 0.0089876 | 0.033523 | -0.026608 | 0.012508 | -0.019276 | 0.001048 | 0.010564 | 0.000747 | 0.1208 | 0.091937 | 0.3068 | 0.005627 | 0.02852 | 0.082776 | -0.074666 | 0.015831 | 0.18769 | -0.11587 | -0.25572 | 121.9722 | -0.02568 | 121.9676 | 121.9673 | -0.00488 | -0.054547 | 0.16031 | 121.7108 | -0.13065 | 121.9951 | 121.8919 | 0.18106 | 0.041209 | -0.26236 | 122.0874 | 122.0585 | 122.2733 | 121.9771 | -0.14086 | 121.9824 | 122.1542 | 121.8507 | 122.0493 | -0.40221
3435.6094 | 122.3877 | -122.0627 | 0.07782 | 1.4211e-13 | -0.016833 | -0.013505 | -0.04517 | -0.041498 | -0.012352 | -0.00083919 | 0.0089876 | 0.033309 | -0.026608 | 0.012508 | -0.019276 | 0.005626 | 0.010564 | 0.005325 | 0.12538 | 0.087359 | 0.3068 | 0.005627 | 0.023941 | 0.078197 | -0.070087 | 0.011252 | 0.17854 | -0.11129 | -0.26488 | 122.0683 | 0.047562 | 122.0683 | 122.068 | -0.000302 | 0.009539 | 0.22898 | 121.7978 | -0.066568 | 122.0866 | 121.9926 | 0.1948 | 0.10072 | -0.18911 | 122.1881 | 122.15 | 122.3695 | 122.0732 | -0.072193 | 122.0739 | 122.2412 | 121.9514 | 122.1409 | -0.3427
3437.4062 | 122.3465 | -122.0856 | 0.091553 | 1.4211e-13 | -0.016619 | -0.013505 | -0.044743 | -0.041925 | -0.012138 | -0.00083919 | 0.0092014 | 0.033309 | -0.026608 | 0.012722 | -0.019276 | 0.010204 | 0.0243 | -0.003831 | 0.11622 | 0.096516 | 0.31137 | 0.010206 | 0.023941 | 0.082776 | -0.070087 | 0.020409 | 0.18311 | -0.11587 | -0.26946 | 122.0958 | 0.024672 | 122.0958 | 122.0817 | -0.014037 | 0.004963 | 0.21982 | 121.8161 | -0.071144 | 122.1095 | 122.0155 | 0.19937 | 0.091562 | -0.20742 | 122.2018 | 122.1821 | 122.3969 | 122.1099 | -0.081347 | 122.106 | 122.2687 | 121.9697 | 122.1683 | -0.36101
3439.2031 | 122.406 | -122.081 | 0.11444 | 1.4211e-13 | -0.016619 | -0.013505 | -0.04517 | -0.041498 | -0.012138 | 0.0067908 | 0.0092014 | 0.033309 | -0.026608 | 0.012722 | -0.019276 | 0.001048 | 0.015142 | -0.008409 | 0.11622 | 0.087359 | 0.3068 | 0.010206 | 0.02852 | 0.082776 | -0.070087 | 0.020409 | 0.17396 | -0.092979 | -0.26946 | 122.0912 | 0.001784 | 122.082 | 122.0726 | -0.018615 | -0.027082 | 0.19235 | 121.8115 | -0.094032 | 122.1095 | 122.0109 | 0.19937 | 0.059517 | -0.20742 | 122.1972 | 122.1684 | 122.3878 | 122.0961 | -0.10423 | 122.1014 | 122.255 | 121.988 | 122.1638 | -0.3839
3440.9219 | 122.374 | -122.0993 | 0.082397 | 1.4211e-13 | -0.017047 | -0.013505 | -0.044957 | -0.041925 | -0.012352 | 0.0067908 | 0.0089876 | 0.033523 | -0.027035 | 0.012722 | -0.019703 | 0.005626 | 0.019721 | -0.003831 | 0.12538 | 0.096516 | 0.3068 | 0.010206 | 0.014784 | 0.078197 | -0.070087 | 0.020409 | 0.18769 | -0.12045 | -0.2603 | 122.1095 | 0.042985 | 122.1049 | 122.0955 | -0.014037 | 0.014119 | 0.2244 | 121.839 | -0.061988 | 122.1141 | 122.0292 | 0.19022 | 0.1053 | -0.20285 | 122.2247 | 122.1958 | 122.4061 | 122.119 | -0.072191 | 122.1197 | 122.287 | 121.9789 | 122.1775 | -0.3427
3442.7031 | 122.2824 | -122.1451 | 0.13733 | 1.4211e-13 | -0.016619 | -0.013718 | -0.044957 | -0.041711 | -0.012565 | -0.0084697 | 0.0092014 | 0.033523 | -0.027035 | 0.012508 | -0.019062 | -0.003531 | 0.015142 | -0.003831 | 0.12538 | 0.08278 | 0.3068 | 0.005627 | 0.023941 | 0.073618 | -0.074666 | 0.015831 | 0.17854 | -0.097557 | -0.2603 | 122.1507 | -0.011947 | 122.1416 | 122.1412 | -0.009458 | -0.054549 | 0.16947 | 121.8848 | -0.1215 | 122.169 | 122.0704 | 0.18564 | 0.041207 | -0.23489 | 122.2705 | 122.2279 | 122.4519 | 122.1602 | -0.1317 | 122.1609 | 122.3236 | 122.0475 | 122.2187 | -0.39763
3444.5156 | 122.4197 | -122.113 | 0.11444 | 1.4211e-13 | -0.017047 | -0.013932 | -0.044957 | -0.041925 | -0.012352 | -0.00083919 | 0.0092014 | 0.033523 | -0.026394 | 0.012508 | -0.019062 | 0.001048 | 0.019721 | 0.000747 | 0.11622 | 0.091937 | 0.3068 | 0.014784 | 0.023941 | 0.082776 | -0.065509 | 0.011252 | 0.18311 | -0.11129 | -0.26946 | 122.1278 | 0.001784 | 122.1141 | 122.1138 | -0.014037 | -0.022504 | 0.19235 | 121.8436 | -0.10319 | 122.137 | 122.0475 | 0.20395 | 0.068674 | -0.22573 | 122.2293 | 122.205 | 122.4198 | 122.1328 | -0.099657 | 122.1243 | 122.2962 | 122.0017 | 122.1958 | -0.3839
3446.2969 | 122.4106 | -122.1313 | 0.09613 | 1.4211e-13 | -0.016619 | -0.013505 | -0.044957 | -0.041711 | -0.012565 | -0.0084697 | 0.0089876 | 0.033523 | -0.026821 | 0.012508 | -0.019062 | 0.001048 | 0.019721 | -0.003831 | 0.1208 | 0.1011 | 0.3068 | 0.005627 | 0.019362 | 0.082776 | -0.074666 | 0.020409 | 0.17854 | -0.10671 | -0.2603 | 122.137 | 0.024674 | 122.1324 | 122.1275 | -0.009458 | 0.004965 | 0.21067 | 121.871 | -0.075721 | 122.1507 | 122.0567 | 0.18564 | 0.082406 | -0.20284 | 122.2522 | 122.2324 | 122.4381 | 122.1511 | -0.090503 | 122.1518 | 122.3099 | 122.0246 | 122.2141 | -0.35643
3448.0781 | 122.3465 | -122.1588 | 0.10071 | 1.4211e-13 | -0.017047 | -0.013718 | -0.045598 | -0.041498 | -0.012352 | -0.0084697 | 0.0092014 | 0.033309 | -0.026608 | 0.012722 | -0.019062 | 0.001048 | 0.0243 | -0.008409 | 0.11622 | 0.091937 | 0.31137 | -0.003531 | 0.023941 | 0.078197 | -0.070087 | 0.011252 | 0.17854 | -0.0243 | -0.26488 | 122.1553 | 0.015517 | 122.1599 | 122.1504 | -0.004878 | -0.008771 | 0.21067 | 121.8939 | -0.089456 | 122.1828 | 122.0887 | 0.1948 | 0.077828 | -0.12501 | 122.275 | 122.2507 | 122.4702 | 122.1831 | -0.10424 | 122.1701 | 122.3373 | 122.1345 | 122.237 | -0.36559
3449.875 | 122.3419 | -122.1817 | 0.11902 | 1.4211e-13 | -0.01726 | -0.013505 | -0.045384 | -0.041925 | -0.012352 | -0.00083919 | 0.0089876 | 0.033737 | -0.026608 | 0.012722 | -0.019276 | 0.001048 | 0.010564 | 0.005325 | 0.1208 | 0.087359 | 0.31137 | 0.005627 | 0.019362 | 0.078197 | -0.070087 | 0.006674 | 0.17854 | -0.10671 | -0.26488 | 122.1873 | 0.001785 | 122.1827 | 122.187 | -0.000302 | -0.03166 | 0.19235 | 121.9168 | -0.11235 | 122.2011 | 122.1116 | 0.1948 | 0.059517 | -0.22573 | 122.3025 | 122.2691 | 122.4931 | 122.1923 | -0.11339 | 122.1884 | 122.3602 | 122.075 | 122.2599 | -0.3839
3451.6719 | 122.4106 | -122.1771 | 0.086975 | 1.4211e-13 | -0.016833 | -0.013291 | -0.04517 | -0.041925 | -0.012352 | -0.00083919 | 0.0092014 | 0.033523 | -0.026608 | 0.012722 | -0.019489 | 0.001048 | 0.015142 | -0.012988 | 0.11622 | 0.091937 | 0.3068 | 0.010206 | 0.019362 | 0.078197 | -0.070087 | 0.011252 | 0.16938 | -0.10671 | -0.26488 | 122.1873 | 0.02925 | 122.1782 | 122.1641 | -0.023194 | 0.004962 | 0.21982 | 121.9122 | -0.075723 | 122.1965 | 122.107 | 0.1948 | 0.082404 | -0.19369 | 122.2933 | 122.2691 | 122.4839 | 122.1923 | -0.076769 | 122.1884 | 122.3465 | 122.0704 | 122.2553 | -0.35186
3453.3906 | 122.3282 | -122.2229 | 0.14648 | 1.4211e-13 | -0.017047 | -0.013505 | -0.04517 | -0.041711 | -0.012352 | -0.00083919 | 0.0092014 | 0.033096 | -0.026608 | 0.012295 | -0.019062 | 0.005626 | 0.019721 | 0.005325 | 0.12996 | 0.091937 | 0.31137 | 0.001048 | 0.02852 | 0.087354 | -0.074666 | 0.015831 | 0.18769 | -0.10214 | -0.26488 | 122.2239 | -0.016524 | 122.2285 | 122.2282 | 0.004277 | -0.054547 | 0.16489 | 121.958 | -0.13065 | 122.2514 | 122.1482 | 0.19022 | 0.041209 | -0.24862 | 122.3529 | 122.3148 | 122.5343 | 122.2426 | -0.14544 | 122.2387 | 122.4106 | 122.1208 | 122.3103 | -0.41137
3455.1719 | 122.4747 | -122.1542 | 0.086975 | 1.4211e-13 | -0.016619 | -0.013505 | -0.045384 | -0.041925 | -0.012352 | -0.00083919 | 0.009415 | 0.033523 | -0.026821 | 0.012508 | -0.019276 | 0.005626 | 0.019721 | -0.003831 | 0.11622 | 0.091937 | 0.31137 | 0.005627 | 0.023941 | 0.073618 | -0.065509 | 0.020409 | 0.18769 | -0.10671 | -0.26488 | 122.1599 | 0.02925 | 122.1599 | 122.1504 | -0.009458 | 0.004962 | 0.2244 | 121.8894 | -0.066566 | 122.1782 | 122.0887 | 0.19937 | 0.10072 | -0.19369 | 122.2705 | 122.2462 | 122.4656 | 122.174 | -0.081348 | 122.1746 | 122.3419 | 122.0475 | 122.2279 | -0.35186
3456.9688 | 122.4014 | -122.1909 | 0.11902 | 1.4211e-13 | -0.017047 | -0.013505 | -0.045384 | -0.041711 | -0.011924 | -0.00083919 | 0.0089876 | 0.033737 | -0.026608 | 0.012295 | -0.019276 | -0.003531 | 0.015142 | -0.008409 | 0.11622 | 0.096516 | 0.3068 | 0.010206 | 0.019362 | 0.078197 | -0.074666 | 0.011252 | 0.17854 | -0.11587 | -0.27862 | 122.2011 | -0.002794 | 122.1873 | 122.1824 | -0.018615 | -0.022503 | 0.18778 | 121.9122 | -0.10777 | 122.2102 | 122.1162 | 0.20395 | 0.059517 | -0.23489 | 122.3071 | 122.2874 | 122.4977 | 122.206 | -0.10881 | 122.2021 | 122.3694 | 122.075 | 122.2691 | -0.39764
3458.7031 | 122.3648 | -122.2275 | 0.13275 | 1.4211e-13 | -0.016833 | -0.013505 | -0.04517 | -0.042139 | -0.012138 | -0.00083919 | 0.009415 | 0.033309 | -0.026608 | 0.012508 | -0.019062 | 0.001048 | 0.015142 | -0.003831 | 0.11622 | 0.091937 | 0.30222 | 0.010206 | 0.014784 | 0.06904 | -0.079245 | 0.015831 | 0.18311 | -0.079243 | -0.26488 | 122.2377 | -0.016526 | 122.2285 | 122.2236 | -0.014037 | -0.040814 | 0.16947 | 121.9626 | -0.11692 | 122.2423 | 122.1482 | 0.18564 | 0.050364 | -0.21199 | 122.3437 | 122.3194 | 122.5297 | 122.2426 | -0.12255 | 122.2433 | 122.4106 | 122.1482 | 122.2965 | -0.39763
3460.5 | 122.4609 | -122.1909 | 0.082397 | 1.4211e-13 | -0.017047 | -0.013505 | -0.044957 | -0.041711 | -0.012352 | -0.00083919 | 0.0089876 | 0.033523 | -0.026821 | 0.012722 | -0.019062 | -0.008109 | 0.019721 | 0.000747 | 0.1208 | 0.091937 | 0.31137 | 0.001048 | 0.019362 | 0.06904 | -0.070087 | 0.011252 | 0.17854 | -0.079243 | -0.26488 | 122.1919 | 0.038407 | 122.1827 | 122.1916 | -0.000301 | 0.00954 | 0.22898 | 121.926 | -0.071145 | 122.2102 | 122.1208 | 0.1948 | 0.096139 | -0.16164 | 122.3117 | 122.2828 | 122.5022 | 122.2106 | -0.081349 | 122.2021 | 122.3694 | 122.1116 | 122.2599 | -0.34728
3462.2969 | 122.4701 | -122.1954 | 0.068665 | 1.4211e-13 | -0.017047 | -0.013505 | -0.04517 | -0.041925 | -0.012565 | 0.014421 | 0.0092014 | 0.033737 | -0.026608 | 0.012722 | -0.019489 | 0.010204 | 0.005985 | 0.000747 | 0.1208 | 0.091937 | 0.31595 | -0.003531 | 0.02852 | 0.078197 | -0.079245 | 0.006674 | 0.17854 | -0.092979 | -0.2603 | 122.1919 | 0.052139 | 122.2056 | 122.1962 | 0.004278 | 0.023272 | 0.24729 | 121.9351 | -0.061991 | 122.224 | 122.1162 | 0.18106 | 0.10987 | -0.16164 | 122.3162 | 122.2874 | 122.5114 | 122.2014 | -0.072196 | 122.2021 | 122.374 | 122.1025 | 122.2736 | -0.32897
3464.0781 | 122.3785 | -122.2458 | 0.13275 | 1.4211e-13 | -0.01726 | -0.013718 | -0.04517 | -0.042139 | -0.012138 | -0.0084697 | 0.0092014 | 0.033523 | -0.026608 | 0.012722 | -0.019062 | -0.003531 | 0.010564 | -0.003831 | 0.11165 | 0.087359 | 0.30222 | 0.014784 | 0.023941 | 0.073618 | -0.074666 | 0.015831 | 0.1648 | -0.0884 | -0.26946 | 122.2606 | -0.021104 | 122.2423 | 122.242 | -0.018615 | -0.045392 | 0.16947 | 121.9763 | -0.11692 | 122.2697 | 122.1711 | 0.1948 | 0.032049 | -0.22115 | 122.3574 | 122.3331 | 122.548 | 122.2564 | -0.11797 | 122.2616 | 122.4106 | 122.1574 | 122.3194 | -0.40221
3465.8125 | 122.4426 | -122.2092 | 0.091553 | 1.4211e-13 | -0.01726 | -0.013718 | -0.04517 | -0.041925 | -0.012352 | -0.00083919 | 0.0089876 | 0.033309 | -0.026608 | 0.012936 | -0.019276 | 0.001048 | 0.0243 | -0.003831 | 0.12538 | 0.091937 | 0.3068 | 0.001048 | 0.023941 | 0.073618 | -0.070087 | 0.011252 | 0.18311 | -0.097557 | -0.2603 | 122.2102 | 0.033829 | 122.2102 | 122.2053 | -0.004879 | 0.000384 | 0.21524 | 121.9489 | -0.080301 | 122.2331 | 122.1391 | 0.19022 | 0.091562 | -0.18911 | 122.3345 | 122.3011 | 122.516 | 122.2335 | -0.090505 | 122.2204 | 122.3923 | 122.1116 | 122.2828 | -0.35186
3467.6094 | 122.4243 | -122.2412 | 0.09613 | 1.4211e-13 | -0.016833 | -0.013291 | -0.044957 | -0.041498 | -0.012138 | -0.0084697 | 0.0089876 | 0.033523 | -0.026821 | 0.012508 | -0.019276 | 0.001048 | 0.019721 | 0.000747 | 0.12538 | 0.087359 | 0.30222 | 0.005627 | 0.023941 | 0.082776 | -0.074666 | 0.015831 | 0.18769 | -0.065507 | -0.2603 | 122.2468 | 0.029252 | 122.2423 | 122.242 | -0.00488 | -0.008771 | 0.20609 | 121.9809 | -0.080299 | 122.2652 | 122.1665 | 0.18564 | 0.091563 | -0.16164 | 122.3666 | 122.3286 | 122.5434 | 122.2609 | -0.090503 | 122.257 | 122.4289 | 122.1757 | 122.324 | -0.35643
3469.3438 | 122.4426 | -122.2275 | 0.086975 | 1.4211e-13 | -0.01726 | -0.013505 | -0.044743 | -0.041925 | -0.011924 | -0.00083919 | 0.008774 | 0.033309 | -0.026608 | 0.012722 | -0.019276 | 0.001048 | 0.019721 | -0.003831 | 0.11622 | 0.091937 | 0.30222 | 0.005627 | 0.023941 | 0.078197 | -0.070087 | 0.020409 | 0.18311 | -0.070086 | -0.26946 | 122.2331 | 0.02925 | 122.2285 | 122.2236 | -0.009458 | 0.004962 | 0.21524 | 121.958 | -0.066566 | 122.2514 | 122.1574 | 0.19937 | 0.09614 | -0.15706 | 122.3437 | 122.3194 | 122.5297 | 122.2472 | -0.081348 | 122.2479 | 122.4106 | 122.1574 | 122.3057 | -0.35644
3471.125 | 122.4335 | -122.2549 | 0.12817 | 1.4211e-13 | -0.01726 | -0.013505 | -0.044957 | -0.041711 | -0.012352 | -0.0084697 | 0.0092014 | 0.033737 | -0.026608 | 0.012295 | -0.019489 | 0.005626 | 0.015142 | 0.000747 | 0.1208 | 0.096516 | 0.3068 | 0.014784 | 0.014784 | 0.078197 | -0.070087 | 0.015831 | 0.18311 | -0.10671 | -0.26946 | 122.2697 | -0.00737 | 122.2606 | 122.2557 | -0.014037 | -0.031658 | 0.17862 | 121.9855 | -0.11234 | 122.2697 | 122.1849 | 0.19937 | 0.054941 | -0.23489 | 122.3757 | 122.3515 | 122.5617 | 122.2701 | -0.11339 | 122.2708 | 122.4381 | 122.1482 | 122.3331 | -0.39764
3472.9062 | 122.525 | -122.2092 | 0.086975 | 1.4211e-13 | -0.016833 | -0.013291 | -0.044743 | -0.041711 | -0.012138 | -0.00083919 | 0.0092014 | 0.033737 | -0.026608 | 0.012722 | -0.019062 | 0.001048 | 0.015142 | 0.000747 | 0.11165 | 0.091937 | 0.29764 | 0.005627 | 0.023941 | 0.082776 | -0.079245 | 0.011252 | 0.18769 | -0.11129 | -0.2603 | 122.2148 | 0.024672 | 122.2102 | 122.2099 | -0.00488 | 0.004962 | 0.21066 | 121.9489 | -0.075723 | 122.2331 | 122.1299 | 0.18106 | 0.10072 | -0.19827 | 122.3208 | 122.3011 | 122.5068 | 122.2243 | -0.081348 | 122.2204 | 122.3969 | 122.0979 | 122.2919 | -0.34728
3474.7031 | 122.5296 | -122.2092 | 0.086975 | 1.4211e-13 | -0.017474 | -0.013505 | -0.04517 | -0.041711 | -0.012138 | 0.0067908 | 0.0089876 | 0.033737 | -0.027035 | 0.012081 | -0.019276 | 0.010204 | 0.015142 | 0.005325 | 0.1208 | 0.096516 | 0.31595 | 0.010206 | 0.02852 | 0.078197 | -0.070087 | 0.015831 | 0.18311 | -0.11587 | -0.2603 | 122.2194 | 0.033829 | 122.2194 | 122.2145 | -0.004881 | 0.009541 | 0.22898 | 121.9489 | -0.071144 | 122.2377 | 122.1391 | 0.19022 | 0.09614 | -0.20285 | 122.33 | 122.3057 | 122.5251 | 122.2243 | -0.076769 | 122.225 | 122.3923 | 122.0933 | 122.2874 | -0.34728
3476.4375 | 122.5296 | -122.2275 | 0.10529 | 1.4211e-13 | -0.017047 | -0.013291 | -0.045384 | -0.041498 | -0.012565 | -0.00083919 | 0.0089876 | 0.033309 | -0.026608 | 0.012722 | -0.019062 | 0.001048 | 0.019721 | -0.003831 | 0.12538 | 0.087359 | 0.31595 | 0.014784 | 0.019362 | 0.082776 | -0.070087 | 0.015831 | 0.17854 | -0.11587 | -0.26488 | 122.2423 | 0.020096 | 122.2285 | 122.2236 | -0.018615 | -0.017927 | 0.21067 | 121.9626 | -0.089455 | 122.2468 | 122.1574 | 0.1948 | 0.07325 | -0.22116 | 122.3529 | 122.3148 | 122.5434 | 122.2472 | -0.090502 | 122.2433 | 122.406 | 122.1116 | 122.3103 | -0.37017
3478.2188 | 122.3648 | -122.0718 | 0.22888 | 1.4211e-13 | -0.017047 | -0.013291 | -0.045384 | -0.041711 | -0.012352 | -0.00083919 | 0.008774 | 0.033309 | -0.026821 | 0.012936 | -0.019062 | 0.005626 | 0.015142 | 0.000747 | 0.12538 | 0.096516 | 0.31137 | 0.005627 | 0.02852 | 0.078197 | -0.070087 | 0.011252 | 0.17396 | -0.10671 | -0.26488 | 122.0775 | -0.1035 | 122.0775 | 122.0726 | -0.00488 | -0.13237 | 0.082492 | 121.807 | -0.21763 | 122.1004 | 122.0018 | 0.1948 | -0.054924 | -0.3356 | 122.1972 | 122.1684 | 122.3832 | 122.087 | -0.22326 | 122.0831 | 122.2458 | 121.9651 | 122.15 | -0.49377
3480.0156 | 122.3099 | -122.1313 | 0.20599 | 1.4211e-13 | -0.01726 | -0.013291 | -0.045384 | -0.041498 | -0.012352 | -0.00083919 | 0.009415 | 0.033523 | -0.026821 | 0.012722 | -0.019276 | 0.005626 | 0.015142 | 0.005325 | 0.1208 | 0.096516 | 0.3068 | -0.00811 | 0.019362 | 0.073618 | -0.074666 | 0.015831 | 0.18311 | -0.11129 | -0.2603 | 122.1232 | -0.08519 | 122.137 | 122.1367 | 0.013435 | -0.10948 | 0.1008 | 121.871 | -0.19016 | 122.1507 | 122.0567 | 0.18564 | -0.022879 | -0.31729 | 122.2522 | 122.2279 | 122.4381 | 122.1465 | -0.2141 | 122.1472 | 122.3145 | 122.0201 | 122.205 | -0.4663
3481.8125 | 122.4792 | -122.1313 | 0.10529 | 1.4211e-13 | -0.017047 | -0.013077 | -0.045384 | -0.041925 | -0.012138 | 0.014421 | 0.0089876 | 0.033309 | -0.027035 | 0.012936 | -0.019276 | -0.003531 | 0.019721 | 0.000747 | 0.1208 | 0.096516 | 0.31137 | -0.021847 | 0.019362 | 0.078197 | -0.074666 | 0.015831 | 0.18769 | -0.065507 | -0.2603 | 122.1095 | 0.015518 | 122.1278 | 122.1321 | 0.022594 | -0.00877 | 0.20609 | 121.871 | -0.089455 | 122.1507 | 122.0567 | 0.18564 | 0.082407 | -0.17079 | 122.2522 | 122.2279 | 122.4427 | 122.1511 | -0.12713 | 122.1472 | 122.319 | 122.0658 | 122.2095 | -0.36559
3483.6094 | 121.8201 | -121.5683 | 0.15564 | 1.4211e-13 | -0.016833 | -0.013718 | -0.044957 | -0.041925 | -0.012352 | -0.00083919 | 0.0089876 | 0.033309 | -0.026821 | 0.012722 | -0.019062 | 0.005626 | 0.015142 | 0.000747 | 0.1208 | 0.096516 | 0.3068 | -0.049321 | 0.014784 | 0.078197 | -0.074666 | 0.020409 | 0.17854 | -0.097557 | -0.26488 | 121.519 | -0.034836 | 121.5739 | 121.569 | 0.050068 | -0.059124 | 0.15116 | 121.3034 | -0.13523 | 121.5831 | 121.4936 | 0.19022 | 0.022896 | -0.2532 | 121.6891 | 121.6648 | 121.8751 | 121.5834 | -0.20496 | 121.5887 | 121.7468 | 121.4707 | 121.6465 | -0.42052
3485.4062 | 122.1863 | -121.8796 | 0.073242 | 1.4211e-13 | -0.016833 | -0.013718 | -0.04517 | -0.041711 | -0.012352 | -0.00083919 | 0.0089876 | 0.033523 | -0.026821 | 0.012722 | -0.019062 | 0.005626 | 0.019721 | 0.000747 | 0.1208 | 0.096516 | 0.31137 | -0.003531 | 0.019362 | 0.082776 | -0.070087 | 0.020409 | 0.17854 | -0.097557 | -0.26946 | 121.876 | 0.047562 | 121.8852 | 121.8803 | 0.004278 | 0.023274 | 0.23813 | 121.6101 | -0.052833 | 121.8989 | 121.8095 | 0.19937 | 0.10529 | -0.1708 | 122.0004 | 121.9761 | 122.191 | 121.8993 | -0.076773 | 121.9 | 122.0581 | 121.782 | 121.9624 | -0.3427
3487.125 | 122.2321 | -121.9482 | 0.091553 | 1.4211e-13 | -0.016833 | -0.013505 | -0.044957 | -0.041711 | -0.012352 | -0.00083919 | 0.0092014 | 0.033096 | -0.027035 | 0.012936 | -0.019062 | 0.005626 | 0.019721 | 0.009904 | 0.12538 | 0.1011 | 0.3068 | 0.014784 | 0.019362 | 0.06904 | -0.070087 | 0.011252 | 0.17854 | -0.11587 | -0.2603 | 121.963 | 0.033829 | 121.9539 | 121.9581 | -0.00488 | 0.009542 | 0.21524 | 121.6879 | -0.080301 | 121.9676 | 121.8782 | 0.19022 | 0.086983 | -0.20742 | 122.0736 | 122.0493 | 122.255 | 121.968 | -0.076769 | 121.9595 | 122.1268 | 121.8324 | 122.0173 | -0.35186
3488.9062 | 122.1634 | -122.0261 | 0.13733 | 1.4211e-13 | -0.017047 | -0.013077 | -0.044957 | -0.041711 | -0.012352 | -0.00083919 | 0.0092014 | 0.033523 | -0.026608 | 0.012508 | -0.019703 | 0.005626 | 0.019721 | 0.000747 | 0.1208 | 0.1011 | 0.30222 | 0.010206 | 0.023941 | 0.078197 | -0.070087 | 0.015831 | 0.17396 | -0.10214 | -0.2603 | 122.0363 | -0.016525 | 122.0317 | 122.0268 | -0.009459 | -0.036234 | 0.16489 | 121.7658 | -0.1215 | 122.05 | 121.956 | 0.19022 | 0.036629 | -0.23947 | 122.1469 | 122.1272 | 122.3283 | 122.0458 | -0.12712 | 122.0419 | 122.2 | 121.9239 | 122.1043 | -0.39763
3490.6406 | 122.2824 | -122.0261 | 0.082397 | 1.4211e-13 | -0.01726 | -0.013932 | -0.044957 | -0.041711 | -0.012565 | 0.0067908 | 0.0092014 | 0.033737 | -0.026821 | 0.012508 | -0.019917 | 0.001048 | 0.015142 | 0.000747 | 0.11622 | 0.091937 | 0.3068 | -0.00811 | 0.023941 | 0.082776 | -0.074666 | 0.011252 | 0.17396 | -0.11587 | -0.2603 | 122.018 | 0.033828 | 122.0271 | 122.0268 | 0.008857 | 0.00954 | 0.2244 | 121.7658 | -0.071145 | 122.05 | 121.9514 | 0.18564 | 0.091561 | -0.19827 | 122.1423 | 122.118 | 122.3329 | 122.0412 | -0.090507 | 122.0373 | 122.2 | 121.9102 | 122.1088 | -0.3427
3492.3594 | 122.2275 | -122.081 | 0.12817 | 1.4211e-13 | -0.017047 | -0.013718 | -0.04517 | -0.041711 | -0.012138 | -0.00083919 | 0.0092014 | 0.033309 | -0.026608 | 0.012722 | -0.019276 | 0.005626 | 0.015142 | -0.003831 | 0.11622 | 0.08278 | 0.31137 | 0.010206 | 0.014784 | 0.078197 | -0.074666 | 0.015831 | 0.18311 | -0.070086 | -0.26488 | 122.0912 | -0.011949 | 122.0866 | 122.0772 | -0.014037 | -0.045394 | 0.1832 | 121.8161 | -0.11234 | 122.0958 | 122.0063 | 0.19022 | 0.054941 | -0.19826 | 122.1972 | 122.1638 | 122.3924 | 122.0961 | -0.11797 | 122.0968 | 122.2641 | 122.0109 | 122.1592 | -0.39306
3494.1406 | 122.3282 | -122.0581 | 0.09613 | 1.4211e-13 | -0.017474 | -0.013718 | -0.044957 | -0.041925 | -0.012565 | -0.0084697 | 0.0092014 | 0.033309 | -0.027035 | 0.012722 | -0.019489 | 0.010204 | 0.019721 | -0.012988 | 0.1208 | 0.091937 | 0.31137 | 0.010206 | 0.023941 | 0.078197 | -0.074666 | 0.011252 | 0.17854 | -0.083821 | -0.26488 | 122.0683 | 0.024674 | 122.0683 | 122.0451 | -0.023194 | -0.004193 | 0.21524 | 121.7932 | -0.084878 | 122.082 | 121.9834 | 0.19022 | 0.082406 | -0.17995 | 122.1789 | 122.15 | 122.3695 | 122.0778 | -0.085924 | 122.0694 | 122.2366 | 121.9743 | 122.1363 | -0.36101
3495.8594 | 122.2366 | -122.0535 | 0.15106 | 1.4211e-13 | -0.017047 | -0.013505 | -0.04517 | -0.041925 | -0.011924 | 0.0067908 | 0.0092014 | 0.033309 | -0.026608 | 0.012508 | -0.019489 | 0.005626 | 0.019721 | 0.009904 | 0.12538 | 0.096516 | 0.31137 | -0.072215 | 0.023941 | 0.073618 | -0.074666 | 0.011252 | 0.18311 | -0.033457 | -0.25572 | 121.9813 | -0.02568 | 122.0592 | 122.0634 | 0.082119 | -0.054546 | 0.16031 | 121.7978 | -0.13981 | 122.0775 | 121.9789 | 0.18106 | 0.032053 | -0.18452 | 122.1789 | 122.15 | 122.3649 | 122.0732 | -0.22328 | 122.0648 | 122.2366 | 122.0201 | 122.1271 | -0.40679
3497.6562 | 122.3145 | -121.8109 | 0.28839 | 1.4211e-13 | -0.017047 | -0.013505 | -0.045384 | -0.041711 | -0.012565 | -0.0161 | 0.0089876 | 0.033309 | -0.026394 | 0.012722 | -0.019062 | 0.010204 | 0.0243 | -0.003831 | 0.1208 | 0.1011 | 0.32053 | -0.017268 | 0.019362 | 0.073618 | -0.070087 | 0.006674 | 0.17854 | -0.0884 | -0.2603 | 121.7936 | -0.16759 | 121.8211 | 121.8071 | 0.013437 | -0.1873 | 0.03214 | 121.5506 | -0.28172 | 121.8303 | 121.7408 | 0.19022 | -0.10986 | -0.37679 | 121.9317 | 121.912 | 122.1314 | 121.8352 | -0.30566 | 121.8176 | 121.9894 | 121.7225 | 121.8845 | -0.54869
3499.4531 | 122.2046 | -122.0718 | 0.11444 | 1.4211e-13 | -0.01726 | -0.013718 | -0.044957 | -0.041711 | -0.012138 | -0.0084697 | 0.008774 | 0.033523 | -0.026821 | 0.012722 | -0.019489 | 0.005626 | 0.019721 | -0.003831 | 0.11622 | 0.087359 | 0.30222 | -0.063057 | 0.023941 | 0.082776 | -0.070087 | 0.015831 | 0.17854 | -0.033457 | -0.26946 | 122.0088 | 0.001784 | 122.0775 | 122.068 | 0.059226 | -0.027082 | 0.18778 | 121.8024 | -0.09861 | 122.0958 | 122.0018 | 0.19937 | 0.064095 | -0.1479 | 122.1881 | 122.1592 | 122.3741 | 122.0916 | -0.1775 | 122.0877 | 122.2504 | 122.0384 | 122.1546 | -0.3839
3501.1719 | 122.3785 | -122.2137 | 0.086975 | 1.4211e-13 | -0.017047 | -0.013718 | -0.04517 | -0.041925 | -0.012138 | -0.0084697 | 0.0089876 | 0.033523 | -0.027249 | 0.012722 | -0.019276 | 0.005626 | 0.019721 | 0.005325 | 0.1208 | 0.096516 | 0.3068 | -0.035584 | 0.019362 | 0.073618 | -0.070087 | 0.011252 | 0.17854 | -0.097557 | -0.25572 | 122.1782 | 0.033829 | 122.2194 | 122.2191 | 0.040909 | 0.009541 | 0.21982 | 121.958 | -0.075723 | 122.2331 | 122.1437 | 0.18564 | 0.091561 | -0.18453 | 122.3345 | 122.3103 | 122.5205 | 122.2335 | -0.12256 | 122.225 | 122.3923 | 122.1162 | 122.2874 | -0.3427
3502.9531 | 122.2916 | -122.0261 | 0.18768 | 1.4211e-13 | -0.01726 | -0.013718 | -0.04517 | -0.042139 | -0.012138 | -0.00083919 | 0.0089876 | 0.033523 | -0.026608 | 0.012508 | -0.019276 | 0.005626 | 0.0243 | 0.009904 | 0.12538 | 0.1011 | 0.31137 | -0.090531 | 0.023941 | 0.087354 | -0.070087 | 0.011252 | 0.17396 | -0.11129 | -0.26488 | 121.9355 | -0.062301 | 122.0317 | 122.036 | 0.10043 | -0.086588 | 0.12369 | 121.7612 | -0.17643 | 122.05 | 121.956 | 0.1948 | -0.013725 | -0.29898 | 122.1514 | 122.1272 | 122.3374 | 122.0504 | -0.27821 | 122.0373 | 122.2 | 121.9148 | 122.1134 | -0.45257
3504.6875 | 122.3511 | -122.0169 | 0.16479 | 1.4211e-13 | -0.017047 | -0.013077 | -0.044743 | -0.041711 | -0.012138 | -0.0084697 | 0.0092014 | 0.033737 | -0.026608 | 0.012722 | -0.019276 | -0.003531 | 0.019721 | -0.003831 | 0.1208 | 0.091937 | 0.31137 | -0.10427 | 0.019362 | 0.082776 | -0.065509 | 0.015831 | 0.18311 | -0.10214 | -0.25572 | 121.9126 | -0.043991 | 122.0134 | 122.0131 | 0.10044 | -0.072858 | 0.14658 | 121.7612 | -0.14896 | 122.0363 | 121.9514 | 0.19022 | 0.01832 | -0.26693 | 122.1377 | 122.1088 | 122.3283 | 122.0366 | -0.26906 | 122.0327 | 122.2 | 121.9148 | 122.0997 | -0.42052
3506.4844 | 122.1542 | -121.9482 | 0.21973 | 1.4211e-13 | -0.01726 | -0.013505 | -0.04517 | -0.041498 | -0.012352 | -0.00083919 | 0.0092014 | 0.033309 | -0.026608 | 0.012722 | -0.019062 | 0.001048 | 0.015142 | 0.005325 | 0.1208 | 0.096516 | 0.3068 | -0.031005 | 0.019362 | 0.073618 | -0.070087 | 0.020409 | 0.17854 | -0.092979 | -0.25572 | 121.9172 | -0.098923 | 121.9493 | 121.9536 | 0.03633 | -0.12321 | 0.087069 | 121.6925 | -0.19932 | 121.9676 | 121.8782 | 0.18564 | -0.041191 | -0.31271 | 122.069 | 122.0448 | 122.255 | 121.9634 | -0.25073 | 121.9687 | 122.1268 | 121.8553 | 122.0219 | -0.47545
3508.2656 | 121.0236 | -120.5887 | 0.16022 | 1.4211e-13 | -0.01256 | -0.011368 | -0.052649 | -0.041711 | -0.01342 | -0.00083919 | 0.008774 | 0.033523 | -0.026608 | 0.012722 | -0.019062 | 0.1796 | 0.19371 | 0.18388 | 0.30852 | 0.29341 | 0.4991 | 0.037679 | 0.005626 | 0.064461 | -0.092981 | -0.007062 | 0.16022 | -0.12961 | -0.27862 | 120.6264 | 0.1483 | 120.7683 | 120.7726 | 0.1462 | 0.13319 | 0.33888 | 120.3101 | -0.16728 | 120.5943 | 120.4957 | 0.18564 | 5e-06 | -0.28982 | 120.8972 | 120.8821 | 121.0878 | 120.7824 | -0.12254 | 120.5816 | 120.7489 | 120.4591 | 120.6531 | -0.43884
3510.0469 | 121.2158 | -116.8213 | 4.6097 | 1.4211e-13 | -0.015551 | -0.01265 | -0.047521 | -0.041925 | -0.012565 | 0.014421 | 0.0089876 | 0.033309 | -0.026608 | 0.012936 | -0.019276 | 0.069723 | 0.083821 | 0.069421 | 0.19406 | 0.15604 | 0.37548 | 0.023942 | 0.014784 | 0.06904 | -0.074666 | -0.002483 | 0.17396 | -0.11129 | -0.26946 | 116.8452 | -4.4156 | 116.891 | 116.8907 | 0.045479 | -4.4536 | -4.2342 | 116.5518 | -4.6122 | 116.8361 | 116.7466 | 0.1948 | -4.4357 | -4.721 | 117.0153 | 116.9773 | 117.1968 | 116.9051 | -4.5857 | 116.8188 | 116.9952 | 116.71 | 116.8903 | -4.8791
3511.8438 | 121.756 | -121.6599 | 0.12817 | 1.4211e-13 | -0.01726 | -0.013718 | -0.04517 | -0.041925 | -0.012352 | -0.00083919 | 0.0089876 | 0.033737 | -0.027035 | 0.012936 | -0.019276 | 0.001048 | 0.015142 | -0.003831 | 0.1208 | 0.087359 | 0.31137 | 0.001048 | 0.02852 | 0.073618 | -0.074666 | 0.020409 | 0.18311 | -0.11587 | -0.25572 | 121.6609 | -0.00737 | 121.6609 | 121.656 | -0.004879 | -0.040815 | 0.1832 | 121.4041 | -0.10777 | 121.6884 | 121.5852 | 0.18106 | 0.054941 | -0.24405 | 121.7807 | 121.7472 | 121.9712 | 121.675 | -0.12713 | 121.6803 | 121.843 | 121.544 | 121.7335 | -0.3839
3513.5781 | 122.0535 | -121.6415 | 0.13275 | 1.4211e-13 | -0.017047 | -0.013505 | -0.044957 | -0.041925 | -0.012352 | -0.00083919 | 0.0089876 | 0.03395 | -0.027035 | 0.013149 | -0.019062 | 0.001048 | 0.015142 | 0.000747 | 0.12538 | 0.087359 | 0.3068 | -0.003531 | 0.023941 | 0.078197 | -0.079245 | 0.015831 | 0.17854 | -0.12045 | -0.25572 | 121.638 | -0.007369 | 121.6426 | 121.6423 | 0.004278 | -0.045392 | 0.17405 | 121.3858 | -0.11692 | 121.6655 | 121.5623 | 0.17648 | 0.045785 | -0.2532 | 121.7669 | 121.7289 | 121.9483 | 121.6567 | -0.13628 | 121.6574 | 121.8201 | 121.5211 | 121.7197 | -0.38848
3515.375 | 122.0123 | -121.7926 | 0.086975 | 1.4211e-13 | -0.017474 | -0.013718 | -0.04517 | -0.042139 | -0.012352 | -0.00083919 | 0.0092014 | 0.033096 | -0.026608 | 0.012936 | -0.019489 | 0.005626 | 0.015142 | -0.003831 | 0.1208 | 0.1011 | 0.31595 | -0.012689 | 0.023941 | 0.078197 | -0.074666 | 0.015831 | 0.18769 | -0.097557 | -0.25572 | 121.7799 | 0.033829 | 121.7982 | 121.7888 | 0.008858 | 0.01412 | 0.22898 | 121.5369 | -0.071144 | 121.8165 | 121.7179 | 0.18106 | 0.10072 | -0.18453 | 121.9134 | 121.8937 | 122.1086 | 121.8077 | -0.099664 | 121.8084 | 121.9803 | 121.695 | 121.8708 | -0.3427
3517.1562 | 121.9894 | -121.8018 | 0.12817 | 1.4211e-13 | -0.017047 | -0.013505 | -0.044957 | -0.041925 | -0.012352 | -0.00083919 | 0.0092014 | 0.033523 | -0.026608 | 0.012936 | -0.019489 | 0.010204 | 0.010564 | -0.003831 | 0.11165 | 0.096516 | 0.30222 | 0.005627 | 0.023941 | 0.078197 | -0.070087 | 0.015831 | 0.18769 | -0.10671 | -0.25572 | 121.8074 | -0.016527 | 121.812 | 121.7979 | -0.009458 | -0.031658 | 0.17404 | 121.546 | -0.11234 | 121.8257 | 121.7317 | 0.18564 | 0.059519 | -0.23489 | 121.9134 | 121.8983 | 122.104 | 121.8123 | -0.12255 | 121.8176 | 121.9895 | 121.695 | 121.88 | -0.3839
3518.9375 | 121.2296 | -118.0618 | 3.2501 | 1.4211e-13 | -0.016192 | -0.013077 | -0.046453 | -0.041498 | -0.012352 | -0.0084697 | 0.0089876 | 0.033309 | -0.026608 | 0.012936 | -0.019062 | 0.037675 | 0.051771 | 0.032795 | 0.16201 | 0.12857 | 0.348 | 0.0331 | 0.019362 | 0.082776 | -0.074666 | 0.011252 | 0.17854 | -0.097557 | -0.26488 | 118.0949 | -3.0881 | 118.0995 | 118.0946 | -0.000305 | -3.1216 | -2.9021 | 117.7969 | -3.2389 | 118.0812 | 117.9872 | 0.19022 | -3.0716 | -3.3477 | 118.2238 | 118.1904 | 118.4098 | 118.1136 | -3.217 | 118.0731 | 118.2404 | 117.9643 | 118.1446 | -3.515
3520.6719 | 121.6141 | -121.4355 | 0.11902 | 1.4211e-13 | -0.01726 | -0.013718 | -0.044743 | -0.042139 | -0.012352 | -0.0084697 | 0.009415 | 0.033309 | -0.026608 | 0.012508 | -0.019276 | 0.005626 | 0.015142 | 0.000747 | 0.12538 | 0.091937 | 0.3068 | 0.005627 | 0.023941 | 0.078197 | -0.070087 | 0.011252 | 0.18311 | -0.047193 | -0.2603 | 121.4412 | 0.006363 | 121.4412 | 121.4363 | -0.00488 | -0.027082 | 0.18778 | 121.1752 | -0.10777 | 121.4595 | 121.3655 | 0.19022 | 0.064096 | -0.16621 | 121.5609 | 121.5275 | 121.7423 | 121.4507 | -0.11339 | 121.4468 | 121.6187 | 121.3884 | 121.5137 | -0.37932
3522.4531 | 121.8887 | -121.6049 | 0.086975 | 1.4211e-13 | -0.01726 | -0.013718 | -0.044957 | -0.042139 | -0.012352 | -0.00083919 | 0.0089876 | 0.033523 | -0.026394 | 0.012936 | -0.019276 | 0.005626 | 0.015142 | -0.003831 | 0.11622 | 0.096516 | 0.3068 | 0.010206 | 0.023941 | 0.073618 | -0.070087 | 0.015831 | 0.18311 | -0.092979 | -0.25572 | 121.6151 | 0.02925 | 121.6105 | 121.6011 | -0.014037 | 0.009541 | 0.21982 | 121.3492 | -0.071144 | 121.6289 | 121.5348 | 0.18564 | 0.09614 | -0.17995 | 121.7211 | 121.7014 | 121.9117 | 121.6201 | -0.076769 | 121.6208 | 121.788 | 121.5119 | 121.6785 | -0.3427
3524.25 | 121.8933 | -121.637 | 0.09613 | 1.4211e-13 | -0.01726 | -0.013505 | -0.044957 | -0.041925 | -0.011924 | -0.00083919 | 0.0089876 | 0.033523 | -0.026821 | 0.012936 | -0.019276 | 0.005626 | 0.015142 | -0.003831 | 0.11622 | 0.096516 | 0.3068 | 0.010206 | 0.02852 | 0.073618 | -0.070087 | 0.015831 | 0.18311 | -0.065507 | -0.2603 | 121.6472 | 0.020095 | 121.6426 | 121.6331 | -0.014037 | 0.000386 | 0.21067 | 121.3767 | -0.080299 | 121.6655 | 121.5669 | 0.19022 | 0.086985 | -0.16164 | 121.7532 | 121.7335 | 121.9438 | 121.6521 | -0.085924 | 121.6528 | 121.8201 | 121.5715 | 121.7106 | -0.35643
3525.9688 | 121.8704 | -121.7377 | 0.12817 | 1.4211e-13 | -0.01726 | -0.013291 | -0.04517 | -0.041711 | -0.012352 | -0.00083919 | 0.009415 | 0.033523 | -0.027035 | 0.012722 | -0.019703 | 0.001048 | 0.0243 | 0.000747 | 0.1208 | 0.087359 | 0.31137 | 0.010206 | 0.023941 | 0.073618 | -0.070087 | 0.020409 | 0.18769 | -0.10214 | -0.25572 | 121.7479 | -0.00737 | 121.7387 | 121.7384 | -0.009459 | -0.040815 | 0.1832 | 121.4819 | -0.10777 | 121.7616 | 121.6676 | 0.18564 | 0.059519 | -0.23031 | 121.8585 | 121.825 | 122.049 | 121.762 | -0.11797 | 121.7581 | 121.9254 | 121.6355 | 121.8113 | -0.3839
3527.75 | 121.5317 | -121.3486 | 0.11902 | 1.4211e-13 | -0.01726 | -0.013718 | -0.045384 | -0.041925 | -0.012565 | 0.0067908 | 0.0092014 | 0.033309 | -0.026608 | 0.012936 | -0.019276 | 0.005626 | 0.019721 | -0.003831 | 0.1208 | 0.091937 | 0.31137 | -0.012689 | 0.019362 | 0.06904 | -0.074666 | 0.020409 | 0.17854 | -0.083821 | -0.26488 | 121.3359 | 0.001785 | 121.3542 | 121.3447 | 0.008858 | -0.027082 | 0.19235 | 121.0837 | -0.09861 | 121.3679 | 121.2739 | 0.19022 | 0.059517 | -0.20284 | 121.4694 | 121.4405 | 121.6599 | 121.3683 | -0.13171 | 121.369 | 121.5271 | 121.2648 | 121.4176 | -0.3839
3529.5469 | 121.7743 | -121.5775 | 0.10529 | 1.4211e-13 | -0.01726 | -0.013505 | -0.045598 | -0.041711 | -0.012352 | -0.00083919 | 0.0089876 | 0.033309 | -0.026608 | 0.012722 | -0.019276 | 0.010204 | 0.028878 | 0.000747 | 0.12996 | 0.1011 | 0.31595 | -0.063057 | 0.019362 | 0.078197 | -0.079245 | 0.011252 | 0.18311 | -0.11129 | -0.2603 | 121.5144 | 0.024674 | 121.5877 | 121.5782 | 0.063804 | -0.004191 | 0.21067 | 121.3171 | -0.094034 | 121.5968 | 121.4982 | 0.18106 | 0.077829 | -0.21658 | 121.7074 | 121.6785 | 121.8934 | 121.6063 | -0.16834 | 121.5887 | 121.7606 | 121.4662 | 121.6557 | -0.36559
3531.3438 | 121.5042 | -121.4767 | 0.12817 | 1.4211e-13 | -0.017474 | -0.013932 | -0.044957 | -0.042139 | -0.012352 | -0.00083919 | 0.008774 | 0.033523 | -0.026608 | 0.012936 | -0.019276 | 0.001048 | 0.0243 | -0.003831 | 0.1208 | 0.091937 | 0.3068 | 0.005627 | 0.019362 | 0.06904 | -0.070087 | 0.002095 | 0.17854 | -0.083821 | -0.2603 | 121.4824 | -0.00737 | 121.4778 | 121.4729 | -0.009458 | -0.036237 | 0.17862 | 121.2164 | -0.12608 | 121.4961 | 121.4067 | 0.19022 | 0.050362 | -0.212 | 121.5976 | 121.5687 | 121.7835 | 121.501 | -0.12255 | 121.4788 | 121.6553 | 121.3929 | 121.5458 | -0.38848
3533.125 | 121.6553 | -121.5546 | 0.12817 | 1.4211e-13 | -0.01726 | -0.013505 | -0.04517 | -0.041925 | -0.012565 | -0.00083919 | 0.0089876 | 0.033309 | -0.026608 | 0.013149 | -0.019276 | 0.001048 | 0.015142 | -0.003831 | 0.1208 | 0.096516 | 0.3068 | -0.003531 | 0.023941 | 0.073618 | -0.070087 | 0.020409 | 0.17854 | -0.10671 | -0.26946 | 121.551 | -0.00737 | 121.5556 | 121.5507 | -0.0003 | -0.031658 | 0.17862 | 121.2851 | -0.10777 | 121.5785 | 121.4845 | 0.19937 | 0.050362 | -0.23489 | 121.6754 | 121.6511 | 121.8614 | 121.5697 | -0.13171 | 121.575 | 121.7331 | 121.4479 | 121.6282 | -0.39764
3534.8594 | 121.6827 | -121.6232 | 0.12817 | 1.4211e-13 | -0.017474 | -0.013718 | -0.04517 | -0.042139 | -0.012138 | 0.0067908 | 0.0092014 | 0.033309 | -0.027035 | 0.012936 | -0.019703 | 0.005626 | 0.015142 | -0.003831 | 0.1208 | 0.096516 | 0.31137 | 0.001048 | 0.023941 | 0.078197 | -0.074666 | 0.015831 | 0.17854 | -0.065507 | -0.25572 | 121.6243 | -0.00737 | 121.6289 | 121.6194 | -0.004879 | -0.031658 | 0.1832 | 121.3675 | -0.11234 | 121.6472 | 121.5486 | 0.18106 | 0.050362 | -0.19368 | 121.744 | 121.7197 | 121.9346 | 121.6384 | -0.12713 | 121.6391 | 121.8018 | 121.5577 | 121.7014 | -0.3839
3536.6562 | 121.8384 | -121.6095 | 0.11444 | 1.4211e-13 | -0.01726 | -0.013932 | -0.044957 | -0.041925 | -0.012352 | -0.00083919 | 0.0089876 | 0.033523 | -0.027035 | 0.013149 | -0.019276 | 0.005626 | 0.010564 | 0.009904 | 0.12538 | 0.087359 | 0.31137 | 0.005627 | 0.023941 | 0.078197 | -0.065509 | 0.020409 | 0.17854 | -0.051771 | -0.25572 | 121.6151 | 0.010941 | 121.6151 | 121.6194 | 0.004277 | -0.027082 | 0.19693 | 121.3538 | -0.094032 | 121.6334 | 121.544 | 0.19022 | 0.064095 | -0.16621 | 121.7349 | 121.6969 | 121.9209 | 121.6201 | -0.10881 | 121.6299 | 121.788 | 121.5577 | 121.6877 | -0.37017
3538.4531 | 121.843 | -121.6599 | 0.1236 | 1.4211e-13 | -0.01726 | -0.013932 | -0.04517 | -0.041711 | -0.012352 | -0.0084697 | 0.0089876 | 0.033737 | -0.027035 | 0.013149 | -0.019276 | 0.001048 | 0.010564 | 0.005325 | 0.11622 | 0.1011 | 0.31137 | 0.010206 | 0.023941 | 0.082776 | -0.070087 | 0.015831 | 0.17854 | -0.015142 | -0.25572 | 121.6701 | -0.007371 | 121.6609 | 121.6652 | -0.004881 | -0.022501 | 0.18778 | 121.4041 | -0.10776 | 121.6838 | 121.5898 | 0.18564 | 0.05494 | -0.13874 | 121.7761 | 121.7609 | 121.9712 | 121.6704 | -0.11339 | 121.6757 | 121.8384 | 121.6447 | 121.7426 | -0.37932
3540.2344 | 121.9345 | -121.6415 | 0.09613 | 1.4211e-13 | -0.01726 | -0.013505 | -0.04517 | -0.041711 | -0.012352 | 0.0067908 | 0.0089876 | 0.033737 | -0.026821 | 0.012722 | -0.019276 | 0.001048 | 0.019721 | 0.005325 | 0.1208 | 0.091937 | 0.3068 | 0.014784 | 0.019362 | 0.082776 | -0.070087 | 0.024988 | 0.17854 | -0.097557 | -0.25572 | 121.6563 | 0.024674 | 121.6426 | 121.6469 | -0.009459 | -0.004193 | 0.21067 | 121.3858 | -0.071142 | 121.6609 | 121.5715 | 0.18564 | 0.082406 | -0.19369 | 121.7623 | 121.7335 | 121.9483 | 121.6613 | -0.081346 | 121.6665 | 121.8201 | 121.544 | 121.7243 | -0.35185
3542.0469 | 121.8384 | -121.7056 | 0.14191 | 1.4211e-13 | -0.01726 | -0.013718 | -0.044743 | -0.041498 | -0.012138 | -0.0161 | 0.0092014 | 0.033523 | -0.026821 | 0.012722 | -0.019276 | 0.010204 | 0.015142 | 0.005325 | 0.11622 | 0.091937 | 0.31595 | 0.010206 | 0.023941 | 0.082776 | -0.065509 | 0.015831 | 0.17854 | -0.047193 | -0.2603 | 121.7158 | -0.025682 | 121.7158 | 121.711 | -0.004881 | -0.04997 | 0.17405 | 121.4453 | -0.12608 | 121.7296 | 121.6401 | 0.19479 | 0.036629 | -0.1891 | 121.8219 | 121.7976 | 122.0216 | 121.7208 | -0.1317 | 121.7215 | 121.8842 | 121.6584 | 121.7884 | -0.40221
3543.8438 | 121.9803 | -121.669 | 0.07782 | 1.4211e-13 | -0.01726 | -0.013932 | -0.044957 | -0.041711 | -0.012352 | -0.0084697 | 0.0092014 | 0.033523 | -0.026821 | 0.012722 | -0.019276 | 0.014783 | 0.010564 | -0.008409 | 0.11622 | 0.091937 | 0.31137 | 0.005627 | 0.019362 | 0.073618 | -0.074666 | 0.011252 | 0.18311 | -0.10671 | -0.26488 | 121.6746 | 0.038405 | 121.6838 | 121.6606 | -0.014036 | 0.014117 | 0.23355 | 121.4041 | -0.066568 | 121.6884 | 121.5943 | 0.19022 | 0.10529 | -0.18453 | 121.7852 | 121.7609 | 121.9804 | 121.6796 | -0.072193 | 121.6803 | 121.8521 | 121.5623 | 121.7426 | -0.3427
3545.5781 | 121.9711 | -121.7285 | 0.09613 | 1.4211e-13 | -0.017047 | -0.013718 | -0.04517 | -0.041925 | -0.012565 | 0.0067908 | 0.0092014 | 0.033737 | -0.026608 | 0.012936 | -0.019489 | 0.010204 | 0.0243 | -0.003831 | 0.1208 | 0.096516 | 0.31595 | 0.005627 | 0.023941 | 0.078197 | -0.070087 | 0.011252 | 0.17854 | -0.11587 | -0.2603 | 121.7341 | 0.024674 | 121.7387 | 121.7247 | -0.009458 | 0.000386 | 0.21982 | 121.4682 | -0.084878 | 121.7525 | 121.6584 | 0.19022 | 0.082406 | -0.212 | 121.8493 | 121.825 | 122.0445 | 121.7528 | -0.090503 | 121.7398 | 121.9071 | 121.6126 | 121.8067 | -0.35643
3547.375 | 121.9757 | -121.7422 | 0.10529 | 1.4211e-13 | -0.01726 | -0.013718 | -0.04517 | -0.041925 | -0.012352 | -0.0084697 | 0.0089876 | 0.033737 | -0.026821 | 0.012936 | -0.019062 | 0.001048 | 0.019721 | 0.005325 | 0.1208 | 0.091937 | 0.31137 | 0.001048 | 0.019362 | 0.078197 | -0.079245 | 0.020409 | 0.18311 | -0.12045 | -0.2603 | 121.7433 | 0.015518 | 121.7433 | 121.7476 | 0.004277 | -0.013349 | 0.20609 | 121.4819 | -0.084877 | 121.7616 | 121.663 | 0.18106 | 0.077829 | -0.22574 | 121.8631 | 121.8342 | 122.0536 | 121.762 | -0.10424 | 121.7627 | 121.9254 | 121.6218 | 121.8204 | -0.36559
3549.0938 | 121.9208 | -121.7834 | 0.11902 | 1.4211e-13 | -0.017474 | -0.013718 | -0.044957 | -0.041711 | -0.012352 | -0.00083919 | 0.0092014 | 0.033523 | -0.026608 | 0.012722 | -0.019489 | 0.005626 | 0.019721 | -0.008409 | 0.1208 | 0.10567 | 0.31595 | 0.010206 | 0.023941 | 0.082776 | -0.074666 | 0.020409 | 0.17854 | -0.10671 | -0.25572 | 121.7937 | 0.001785 | 121.7891 | 121.775 | -0.018615 | -0.013345 | 0.19693 | 121.5277 | -0.09861 | 121.8074 | 121.7088 | 0.18106 | 0.059517 | -0.22573 | 121.9043 | 121.8891 | 122.0994 | 121.8032 | -0.10881 | 121.8039 | 121.962 | 121.6767 | 121.8662 | -0.37474
3550.8906 | 122.0123 | -121.7514 | 0.086975 | 1.4211e-13 | -0.017688 | -0.013932 | -0.044957 | -0.042139 | -0.012352 | -0.0084697 | 0.0089876 | 0.033309 | -0.026608 | 0.012936 | -0.019489 | 0.001048 | 0.019721 | 0.000747 | 0.11622 | 0.1011 | 0.31595 | 0.001048 | 0.023941 | 0.082776 | -0.070087 | 0.020409 | 0.17854 | -0.060928 | -0.2603 | 121.7525 | 0.02925 | 121.7525 | 121.7522 | -0.000301 | 0.01412 | 0.22898 | 121.4911 | -0.066566 | 121.7753 | 121.6813 | 0.19022 | 0.091561 | -0.1479 | 121.8676 | 121.8525 | 122.0674 | 121.7711 | -0.085927 | 121.7718 | 121.9299 | 121.6905 | 121.8342 | -0.34728
3552.6406 | 121.9437 | -121.8018 | 0.11444 | 1.4211e-13 | -0.017474 | -0.013932 | -0.04517 | -0.041925 | -0.012352 | -0.0084697 | 0.0092014 | 0.033309 | -0.026394 | 0.013149 | -0.019276 | 0.001048 | 0.019721 | 0.000747 | 0.11622 | 0.096516 | 0.31595 | 0.010206 | 0.019362 | 0.073618 | -0.065509 | 0.015831 | 0.18311 | -0.097557 | -0.25572 | 121.812 | 0.001784 | 121.8028 | 121.8025 | -0.009459 | -0.017925 | 0.20151 | 121.546 | -0.09861 | 121.8211 | 121.7362 | 0.19022 | 0.068674 | -0.212 | 121.918 | 121.8983 | 122.1177 | 121.8215 | -0.10423 | 121.8176 | 121.9849 | 121.7042 | 121.8754 | -0.37017
3554.4375 | 121.9849 | -121.7926 | 0.1236 | 1.4211e-13 | -0.017474 | -0.013505 | -0.044957 | -0.041925 | -0.012138 | 0.014421 | 0.0089876 | 0.033309 | -0.026608 | 0.012936 | -0.019062 | 0.001048 | 0.010564 | 0.000747 | 0.1208 | 0.091937 | 0.31595 | 0.010206 | 0.019362 | 0.087354 | -0.065509 | 0.011252 | 0.17854 | -0.042614 | -0.25572 | 121.8028 | -0.002792 | 121.7937 | 121.7934 | -0.009459 | -0.031659 | 0.19236 | 121.5369 | -0.11234 | 121.812 | 121.7271 | 0.19022 | 0.05494 | -0.16621 | 121.9134 | 121.8845 | 122.1086 | 121.8032 | -0.11339 | 121.8039 | 121.9711 | 121.75 | 121.88 | -0.37932
3556.1719 | 122.0306 | -121.8201 | 0.10071 | 1.4211e-13 | -0.017474 | -0.013505 | -0.04517 | -0.042139 | -0.012565 | 0.0067908 | 0.0092014 | 0.033523 | -0.026394 | 0.013149 | -0.019276 | 0.005626 | 0.015142 | 0.000747 | 0.12538 | 0.096516 | 0.31137 | 0.005627 | 0.023941 | 0.078197 | -0.065509 | 0.015831 | 0.18311 | -0.092979 | -0.26488 | 121.8257 | 0.024674 | 121.8257 | 121.8208 | -0.00488 | -0.004192 | 0.21067 | 121.5552 | -0.084877 | 121.844 | 121.7546 | 0.19937 | 0.082407 | -0.19369 | 121.9455 | 121.9166 | 122.1314 | 121.8352 | -0.095081 | 121.8359 | 122.0032 | 121.7271 | 121.8983 | -0.36559
3557.9531 | 121.9849 | -121.8475 | 0.10986 | 1.4211e-13 | -0.017688 | -0.013932 | -0.044743 | -0.041925 | -0.012138 | -0.00083919 | 0.0089876 | 0.033309 | -0.026821 | 0.012936 | -0.019062 | 0.005626 | 0.015142 | 0.000747 | 0.11165 | 0.1011 | 0.31137 | 0.014784 | 0.023941 | 0.073618 | -0.070087 | 0.011252 | 0.18311 | -0.047193 | -0.25572 | 121.8623 | 0.001784 | 121.8532 | 121.8483 | -0.014037 | -0.008768 | 0.20151 | 121.5918 | -0.098611 | 121.8715 | 121.7774 | 0.18564 | 0.073252 | -0.15706 | 121.9592 | 121.9486 | 122.1589 | 121.8627 | -0.095079 | 121.8588 | 122.0306 | 121.8003 | 121.9212 | -0.36559
3559.75 | 122.1085 | -121.8292 | 0.091553 | 1.4211e-13 | -0.017047 | -0.013077 | -0.04517 | -0.042352 | -0.012352 | -0.0084697 | 0.0089876 | 0.033523 | -0.027035 | 0.013149 | -0.019489 | 0.005626 | 0.019721 | 0.000747 | 0.12538 | 0.096516 | 0.32053 | 0.001048 | 0.014784 | 0.078197 | -0.070087 | 0.015831 | 0.17854 | -0.047193 | -0.26488 | 121.8303 | 0.033829 | 121.8349 | 121.83 | -0.000301 | 0.004963 | 0.22898 | 121.5643 | -0.075722 | 121.844 | 121.7591 | 0.1948 | 0.086983 | -0.13875 | 121.9546 | 121.9257 | 122.1498 | 121.8489 | -0.090505 | 121.8451 | 122.0078 | 121.782 | 121.9074 | -0.35644
3561.4844 | 122.1039 | -121.8338 | 0.091553 | 1.4211e-13 | -0.017474 | -0.013505 | -0.045384 | -0.041925 | -0.012565 | -0.00083919 | 0.0092014 | 0.033523 | -0.026608 | 0.012936 | -0.019489 | 0.001048 | 0.019721 | 0.000747 | 0.1208 | 0.1011 | 0.3068 | 0.014784 | 0.023941 | 0.082776 | -0.070087 | 0.020409 | 0.17854 | -0.083821 | -0.26488 | 121.8486 | 0.029251 | 121.8348 | 121.8345 | -0.014037 | 0.009542 | 0.21524 | 121.5689 | -0.071144 | 121.8577 | 121.7637 | 0.1948 | 0.086983 | -0.17537 | 121.9546 | 121.9349 | 122.1406 | 121.8535 | -0.076769 | 121.8542 | 122.0123 | 121.75 | 121.9166 | -0.35644
3563.2656 | 122.0169 | -121.8796 | 0.14191 | 1.4211e-13 | -0.017474 | -0.013932 | -0.044743 | -0.041925 | -0.012352 | 0.0067908 | 0.008774 | 0.033523 | -0.026821 | 0.012936 | -0.019917 | 0.001048 | 0.019721 | 0.000747 | 0.12538 | 0.096516 | 0.32053 | 0.014784 | 0.023941 | 0.078197 | -0.074666 | 0.011252 | 0.17854 | -0.070086 | -0.2603 | 121.8944 | -0.016525 | 121.8806 | 121.8803 | -0.014037 | -0.045391 | 0.17862 | 121.6193 | -0.13065 | 121.9035 | 121.8049 | 0.18564 | 0.036629 | -0.21199 | 122.005 | 121.9761 | 122.2001 | 121.8993 | -0.12712 | 121.8908 | 122.0581 | 121.8095 | 121.9578 | -0.40221
3565.0625 | 122.1085 | -121.875 | 0.086975 | 1.4211e-13 | -0.017474 | -0.013505 | -0.04517 | -0.041925 | -0.011711 | 0.022052 | 0.008774 | 0.033523 | -0.026608 | 0.013149 | -0.019276 | 0.010204 | 0.015142 | -0.003831 | 0.1208 | 0.1011 | 0.31595 | 0.005627 | 0.019362 | 0.078197 | -0.074666 | 0.015831 | 0.18311 | -0.10214 | -0.25572 | 121.8806 | 0.033829 | 121.8852 | 121.8712 | -0.009458 | 0.01412 | 0.22898 | 121.6193 | -0.071144 | 121.8944 | 121.8003 | 0.18106 | 0.09614 | -0.18911 | 121.9958 | 121.9761 | 122.191 | 121.8901 | -0.081348 | 121.8908 | 122.0581 | 121.7729 | 121.9532 | -0.3427
3566.875 | 122.168 | -121.843 | 0.07782 | 1.4211e-13 | -0.017688 | -0.013718 | -0.045384 | -0.041925 | -0.012352 | 0.0067908 | 0.0089876 | 0.033523 | -0.026821 | 0.013149 | -0.019062 | 0.001048 | 0.015142 | 0.000747 | 0.11622 | 0.096516 | 0.3068 | 0.001048 | 0.023941 | 0.073618 | -0.079245 | 0.015831 | 0.17854 | -0.092979 | -0.2603 | 121.844 | 0.038405 | 121.844 | 121.8437 | -0.000301 | 0.018696 | 0.22898 | 121.5827 | -0.061989 | 121.8669 | 121.7637 | 0.18106 | 0.10072 | -0.1708 | 121.9592 | 121.9395 | 122.1498 | 121.8581 | -0.076772 | 121.8588 | 122.0215 | 121.75 | 121.9166 | -0.33812
3568.6094 | 122.0398 | -121.9299 | 0.11902 | 1.4211e-13 | -0.017474 | -0.013505 | -0.04517 | -0.041925 | -0.012565 | -0.00083919 | 0.0092014 | 0.033309 | -0.026608 | 0.012936 | -0.019489 | 0.001048 | 0.015142 | 0.000747 | 0.12538 | 0.096516 | 0.32053 | 0.010206 | 0.019362 | 0.073618 | -0.070087 | 0.006674 | 0.18311 | -0.10214 | -0.25572 | 121.9401 | 0.006363 | 121.931 | 121.9307 | -0.009459 | -0.022503 | 0.20151 | 121.6742 | -0.11235 | 121.9493 | 121.8598 | 0.18564 | 0.064096 | -0.22115 | 122.0553 | 122.0264 | 122.2505 | 121.9451 | -0.10881 | 121.9366 | 122.113 | 121.8278 | 122.0035 | -0.37474
3570.3906 | 122.2046 | -121.8887 | 0.091553 | 1.4211e-13 | -0.017474 | -0.013718 | -0.04517 | -0.041498 | -0.012565 | 0.0067908 | 0.0089876 | 0.033523 | -0.027035 | 0.012936 | -0.019276 | 0.005626 | 0.028878 | 0.000747 | 0.12538 | 0.096516 | 0.31137 | 0.014784 | 0.010205 | 0.06904 | -0.074666 | 0.015831 | 0.18311 | -0.060928 | -0.25572 | 121.9035 | 0.033829 | 121.8944 | 121.8895 | -0.014037 | 0.004963 | 0.21982 | 121.633 | -0.075722 | 121.8989 | 121.8141 | 0.18106 | 0.091562 | -0.15248 | 122.0141 | 121.9852 | 122.2001 | 121.9176 | -0.076769 | 121.9046 | 122.0718 | 121.8278 | 121.9578 | -0.34728
3572.1719 | 122.1909 | -121.8933 | 0.07782 | 1.4211e-13 | -0.017474 | -0.014146 | -0.044957 | -0.041711 | -0.012779 | -0.0084697 | 0.0092014 | 0.033523 | -0.026608 | 0.013149 | -0.019276 | 0.005626 | 0.015142 | 0.005325 | 0.1208 | 0.1011 | 0.31137 | 0.005627 | 0.023941 | 0.078197 | -0.079245 | 0.006674 | 0.18311 | -0.0884 | -0.2603 | 121.8989 | 0.042984 | 121.8989 | 121.8986 | -0.000302 | 0.023275 | 0.23355 | 121.633 | -0.071146 | 121.9173 | 121.8141 | 0.18106 | 0.10529 | -0.16622 | 122.0141 | 121.9944 | 122.2047 | 121.9085 | -0.072193 | 121.9 | 122.0764 | 121.8049 | 121.9715 | -0.33812
3573.8906 | 122.2275 | -121.8933 | 0.11444 | 1.4211e-13 | -0.01726 | -0.013718 | -0.04517 | -0.042139 | -0.012352 | -0.00083919 | 0.009415 | 0.033737 | -0.026394 | 0.013363 | -0.019489 | 0.001048 | 0.019721 | 0.005325 | 0.11622 | 0.091937 | 0.3068 | 0.010206 | 0.019362 | 0.082776 | -0.074666 | 0.011252 | 0.18311 | -0.10214 | -0.25572 | 121.9035 | 0.001784 | 121.8944 | 121.8986 | -0.004881 | -0.022504 | 0.19235 | 121.6376 | -0.10319 | 121.9127 | 121.8186 | 0.18106 | 0.068674 | -0.21658 | 122.0095 | 121.9852 | 122.2001 | 121.913 | -0.10423 | 121.9046 | 122.0764 | 121.7912 | 121.9761 | -0.37017
3575.6875 | 122.2046 | -121.9391 | 0.10071 | 1.4211e-13 | -0.017474 | -0.013932 | -0.044529 | -0.041711 | -0.012565 | -0.0084697 | 0.0089876 | 0.033523 | -0.026821 | 0.012936 | -0.019276 | -0.003531 | 0.019721 | -0.003831 | 0.12538 | 0.096516 | 0.31137 | 0.014784 | 0.02852 | 0.073618 | -0.074666 | 0.015831 | 0.18311 | -0.065507 | -0.26488 | 121.9539 | 0.024674 | 121.9356 | 121.9353 | -0.018615 | -0.004192 | 0.21067 | 121.6742 | -0.084877 | 121.9676 | 121.8644 | 0.19022 | 0.082407 | -0.16622 | 122.0645 | 122.0356 | 122.2505 | 121.9588 | -0.085924 | 121.9549 | 122.1222 | 121.8736 | 122.0127 | -0.36559
3577.4844 | 122.1451 | -121.9299 | 0.10986 | 1.4211e-13 | -0.017474 | -0.013932 | -0.04517 | -0.041711 | -0.012352 | -0.0084697 | 0.008774 | 0.033523 | -0.026608 | 0.013363 | -0.019062 | -0.003531 | 0.015142 | -0.003831 | 0.1208 | 0.087359 | 0.31137 | -0.003531 | 0.023941 | 0.078197 | -0.074666 | 0.020409 | 0.18769 | -0.038035 | -0.25572 | 121.9264 | 0.010941 | 121.9264 | 121.9261 | -0.0003 | -0.022504 | 0.20151 | 121.6742 | -0.089454 | 121.9539 | 121.8553 | 0.18106 | 0.07783 | -0.1479 | 122.0507 | 122.0173 | 122.2413 | 121.9451 | -0.11339 | 121.9503 | 122.1176 | 121.8919 | 122.0081 | -0.36559
3579.2656 | 122.1542 | -121.9528 | 0.12817 | 1.4211e-13 | -0.017474 | -0.013505 | -0.04517 | -0.041711 | -0.012138 | -0.00083919 | 0.0089876 | 0.033309 | -0.027035 | 0.013149 | -0.019276 | 0.001048 | 0.019721 | 0.000747 | 0.1208 | 0.091937 | 0.31137 | 0.005627 | 0.033099 | 0.078197 | -0.070087 | 0.015831 | 0.17854 | -0.047193 | -0.2603 | 121.9584 | -0.00737 | 121.9539 | 121.9536 | -0.00488 | -0.036237 | 0.1832 | 121.6925 | -0.11234 | 121.9859 | 121.8827 | 0.19022 | 0.050362 | -0.17537 | 122.0736 | 122.0448 | 122.2642 | 121.9725 | -0.12255 | 121.9687 | 122.1314 | 121.9056 | 122.031 | -0.38848
3580.9844 | 122.1222 | -121.994 | 0.10529 | 1.4211e-13 | -0.017474 | -0.013932 | -0.04517 | -0.041498 | -0.012565 | -0.00083919 | 0.008774 | 0.033096 | -0.026821 | 0.012936 | -0.019276 | 0.001048 | 0.010564 | 0.000747 | 0.12538 | 0.096516 | 0.31595 | -0.00811 | 0.023941 | 0.078197 | -0.079245 | 0.011252 | 0.18311 | -0.051771 | -0.25115 | 121.9859 | 0.020096 | 121.9951 | 121.9948 | 0.008857 | -0.00877 | 0.21067 | 121.7429 | -0.094034 | 122.018 | 121.9148 | 0.1719 | 0.077829 | -0.15706 | 122.1194 | 122.0905 | 122.31 | 122.0046 | -0.1134 | 122.0053 | 122.1771 | 121.9422 | 122.0722 | -0.35643
3582.7812 | 122.2366 | -121.9528 | 0.09613 | 1.4211e-13 | -0.017474 | -0.013718 | -0.04517 | -0.042139 | -0.012779 | -0.00083919 | 0.0089876 | 0.033523 | -0.026394 | 0.013363 | -0.019276 | 0.001048 | 0.010564 | -0.008409 | 0.12538 | 0.1011 | 0.31595 | 0.010206 | 0.023941 | 0.082776 | -0.074666 | 0.011252 | 0.18311 | -0.038035 | -0.25572 | 121.963 | 0.029252 | 121.9539 | 121.9444 | -0.018615 | 0.004965 | 0.21982 | 121.6971 | -0.084878 | 121.9768 | 121.8782 | 0.18106 | 0.086985 | -0.13416 | 122.0782 | 122.0539 | 122.2688 | 121.9634 | -0.085924 | 121.9641 | 122.1359 | 121.9148 | 122.0356 | -0.35185
3584.5781 | 122.2366 | -121.9757 | 0.091553 | 1.4211e-13 | -0.017688 | -0.013932 | -0.04517 | -0.041925 | -0.012352 | -0.00083919 | 0.0089876 | 0.033309 | -0.026394 | 0.013149 | -0.019276 | 0.001048 | 0.0243 | -0.003831 | 0.1208 | 0.091937 | 0.31595 | 0.010206 | 0.023941 | 0.082776 | -0.065509 | 0.015831 | 0.17396 | -0.019721 | -0.26488 | 121.9859 | 0.029251 | 121.9768 | 121.9719 | -0.014037 | 0.000384 | 0.2244 | 121.7108 | -0.075722 | 121.9996 | 121.9102 | 0.19937 | 0.082405 | -0.11127 | 122.0965 | 122.0676 | 122.2917 | 122 | -0.081347 | 121.9915 | 122.1497 | 121.956 | 122.0585 | -0.35644
3586.2969 | 122.2687 | -121.9574 | 0.086975 | 1.4211e-13 | -0.017688 | -0.013932 | -0.044529 | -0.041925 | -0.012565 | -0.00083919 | 0.0092014 | 0.033523 | -0.026821 | 0.013363 | -0.019062 | 0.005626 | 0.015142 | 0.000747 | 0.1208 | 0.1011 | 0.3068 | 0.014784 | 0.023941 | 0.082776 | -0.065509 | 0.015831 | 0.17854 | -0.051771 | -0.25572 | 121.9722 | 0.033829 | 121.963 | 121.9581 | -0.014037 | 0.01412 | 0.21982 | 121.7017 | -0.071144 | 121.9813 | 121.8919 | 0.19022 | 0.091561 | -0.13875 | 122.0782 | 122.0585 | 122.2642 | 121.9725 | -0.072191 | 121.9732 | 122.1359 | 121.9056 | 122.0402 | -0.3427
3588.0781 | 122.2275 | -121.9666 | 0.082397 | 1.4211e-13 | -0.017474 | -0.013718 | -0.044743 | -0.042139 | -0.012565 | -0.00083919 | 0.0089876 | 0.033309 | -0.026608 | 0.013149 | -0.019276 | 0.001048 | 0.0243 | 0.005325 | 0.1208 | 0.10567 | 0.31595 | 0.001048 | 0.023941 | 0.078197 | -0.065509 | 0.011252 | 0.17854 | -0.079243 | -0.25572 | 121.9676 | 0.038407 | 121.9676 | 121.9719 | 0.004277 | 0.023277 | 0.23356 | 121.7108 | -0.071145 | 121.9905 | 121.901 | 0.19022 | 0.096139 | -0.16164 | 122.0874 | 122.0722 | 122.2825 | 121.9909 | -0.081349 | 121.9778 | 122.1451 | 121.8873 | 122.0448 | -0.33812
3589.875 | 122.2549 | -121.9894 | 0.09613 | 1.4211e-13 | -0.017474 | -0.013718 | -0.04517 | -0.041925 | -0.012565 | -0.00083919 | 0.008774 | 0.033523 | -0.026608 | 0.013149 | -0.018848 | 0.005626 | 0.0243 | 0.000747 | 0.11622 | 0.096516 | 0.31137 | 0.010206 | 0.02852 | 0.078197 | -0.065509 | 0.015831 | 0.17854 | -0.051771 | -0.26488 | 121.9996 | 0.020095 | 121.9951 | 121.9902 | -0.009459 | 0.000386 | 0.21524 | 121.7246 | -0.080299 | 122.018 | 121.9239 | 0.19937 | 0.082406 | -0.1479 | 122.1057 | 122.086 | 122.3008 | 122.0137 | -0.085924 | 122.0053 | 122.168 | 121.9377 | 122.0676 | -0.36101
3591.625 | 122.2229 | -121.994 | 0.091553 | 1.4211e-13 | -0.017688 | -0.013932 | -0.044957 | -0.042139 | -0.012779 | -0.00083919 | 0.0089876 | 0.033523 | -0.026821 | 0.013149 | -0.019489 | -0.003531 | 0.019721 | -0.003831 | 0.12538 | 0.10567 | 0.31137 | 0.005627 | 0.023941 | 0.082776 | -0.079245 | 0.015831 | 0.18311 | -0.074664 | -0.2603 | 121.9996 | 0.033829 | 121.9905 | 121.9902 | -0.009458 | 0.014121 | 0.21982 | 121.7337 | -0.075722 | 122.018 | 121.9148 | 0.18106 | 0.091562 | -0.16622 | 122.1194 | 122.0997 | 122.3054 | 122.0137 | -0.085926 | 122.0099 | 122.1771 | 121.9194 | 122.0768 | -0.35186
3593.4219 | 122.3007 | -121.9803 | 0.091553 | 1.4211e-13 | -0.017688 | -0.013718 | -0.044529 | -0.041925 | -0.012779 | -0.00083919 | 0.008774 | 0.033737 | -0.026821 | 0.013149 | -0.019062 | 0.001048 | 0.015142 | 0.000747 | 0.12538 | 0.1011 | 0.31595 | 0.005627 | 0.019362 | 0.082776 | -0.070087 | 0.015831 | 0.17854 | -0.11587 | -0.2603 | 121.9859 | 0.033829 | 121.9813 | 121.981 | -0.00488 | 0.009542 | 0.2244 | 121.72 | -0.075722 | 121.9996 | 121.9102 | 0.19022 | 0.086983 | -0.20742 | 122.1057 | 122.0814 | 122.2962 | 121.9954 | -0.085926 | 121.9961 | 122.1588 | 121.8644 | 122.0631 | -0.35186
3595.2031 | 122.3099 | -121.9986 | 0.086975 | 1.4211e-13 | -0.017474 | -0.013718 | -0.045384 | -0.041498 | -0.012779 | 0.0067908 | 0.008774 | 0.033737 | -0.026608 | 0.013149 | -0.019062 | 0.005626 | 0.0243 | 0.000747 | 0.12538 | 0.091937 | 0.31595 | 0.014784 | 0.033099 | 0.082776 | -0.074666 | 0.020409 | 0.17854 | -0.05635 | -0.2603 | 122.0134 | 0.038407 | 122.0042 | 121.9993 | -0.014037 | 0.004962 | 0.22898 | 121.7383 | -0.066566 | 122.0317 | 121.9239 | 0.18564 | 0.091561 | -0.14332 | 122.124 | 122.0905 | 122.3145 | 122.0229 | -0.072191 | 122.019 | 122.1771 | 121.9422 | 122.0814 | -0.34728
3597.0156 | 122.2 | -122.0398 | 0.10529 | 1.4211e-13 | -0.017688 | -0.014146 | -0.045598 | -0.042139 | -0.012565 | 0.0067908 | 0.0089876 | 0.033523 | -0.026394 | 0.013363 | -0.019703 | 0.001048 | 0.015142 | 0.000747 | 0.12538 | 0.091937 | 0.31137 | 0.005627 | 0.023941 | 0.078197 | -0.074666 | 0.020409 | 0.17854 | -0.070086 | -0.25572 | 122.0454 | 0.020096 | 122.0408 | 122.0405 | -0.00488 | -0.013349 | 0.20609 | 121.7841 | -0.084877 | 122.0637 | 121.9651 | 0.18106 | 0.07325 | -0.17537 | 122.1652 | 122.1317 | 122.3512 | 122.0549 | -0.099659 | 122.0602 | 122.2183 | 121.9697 | 122.118 | -0.36101
3598.75 | 122.2275 | -122.0398 | 0.11902 | 1.4211e-13 | -0.017902 | -0.013291 | -0.044957 | -0.041925 | -0.012565 | -0.00083919 | 0.0092014 | 0.033737 | -0.026394 | 0.012936 | -0.019276 | 0.001048 | 0.015142 | 0.000747 | 0.12538 | 0.096516 | 0.31137 | 0.010206 | 0.019362 | 0.078197 | -0.065509 | 0.015831 | 0.17396 | -0.033457 | -0.26488 | 122.05 | 0.006363 | 122.0408 | 122.0405 | -0.009459 | -0.022503 | 0.19235 | 121.7749 | -0.10319 | 122.0592 | 121.9743 | 0.19937 | 0.054939 | -0.15248 | 122.1652 | 122.1363 | 122.3512 | 122.0549 | -0.10881 | 122.0556 | 122.2138 | 122.0063 | 122.118 | -0.3839
3600.5469 | 122.1909 | -122.0581 | 0.1236 | 1.4211e-13 | -0.017688 | -0.014146 | -0.04517 | -0.041711 | -0.012352 | 0.0067908 | 0.008774 | 0.033523 | -0.026608 | 0.013363 | -0.019062 | 0.005626 | 0.010564 | 0.000747 | 0.1208 | 0.091937 | 0.31595 | 0.010206 | 0.019362 | 0.082776 | -0.070087 | 0.015831 | 0.17854 | -0.060928 | -0.25572 | 122.0683 | -0.002792 | 122.0637 | 122.0589 | -0.009459 | -0.031659 | 0.19236 | 121.8024 | -0.10776 | 122.0775 | 121.988 | 0.18564 | 0.05494 | -0.18452 | 122.1789 | 122.15 | 122.3741 | 122.0687 | -0.11339 | 122.0739 | 122.2366 | 121.9972 | 122.1409 | -0.37932
3602.3438 | 122.2458 | -122.0535 | 0.11902 | 1.4211e-13 | -0.017474 | -0.014146 | -0.044743 | -0.042139 | -0.012565 | -0.0084697 | 0.0085604 | 0.03395 | -0.026608 | 0.013363 | -0.018848 | 0.005626 | 0.019721 | -0.003831 | 0.1208 | 0.096516 | 0.31137 | 0.014784 | 0.023941 | 0.078197 | -0.070087 | 0.024988 | 0.18311 | -0.065507 | -0.25115 | 122.0683 | 0.001785 | 122.0592 | 122.0497 | -0.018615 | -0.022503 | 0.19235 | 121.8024 | -0.094031 | 122.0775 | 121.9834 | 0.18106 | 0.064096 | -0.18453 | 122.1743 | 122.15 | 122.3649 | 122.0732 | -0.10423 | 122.0785 | 122.2366 | 121.988 | 122.1317 | -0.37016
3604.0625 | 122.2504 | -122.0627 | 0.11444 | 1.4211e-13 | -0.017474 | -0.013932 | -0.04517 | -0.042139 | -0.012352 | -0.00083919 | 0.008774 | 0.03395 | -0.026394 | 0.013149 | -0.019276 | 0.005626 | 0.019721 | 0.000747 | 0.12538 | 0.091937 | 0.31595 | -0.00811 | 0.019362 | 0.073618 | -0.065509 | 0.020409 | 0.18311 | 0.035222 | -0.25572 | 122.0546 | 0.010941 | 122.0683 | 122.0634 | 0.008857 | -0.022504 | 0.20151 | 121.807 | -0.094032 | 122.082 | 121.9972 | 0.19022 | 0.068674 | -0.079219 | 122.1881 | 122.1546 | 122.3786 | 122.0824 | -0.12255 | 122.0831 | 122.2458 | 122.0979 | 122.1363 | -0.37017
3605.8594 | 122.2595 | -122.0627 | 0.12817 | 1.4211e-13 | -0.017688 | -0.013932 | -0.04517 | -0.041925 | -0.012565 | 0.0067908 | 0.0085604 | 0.033309 | -0.026821 | 0.013363 | -0.019276 | 0.005626 | 0.0243 | 0.000747 | 0.12996 | 0.091937 | 0.31595 | 0.001048 | 0.019362 | 0.073618 | -0.065509 | 0.020409 | 0.18311 | -0.047193 | -0.25572 | 122.0637 | 0.001786 | 122.0683 | 122.0634 | -0.000301 | -0.036237 | 0.18778 | 121.807 | -0.10777 | 122.082 | 121.9972 | 0.19022 | 0.054941 | -0.17537 | 122.1926 | 122.1546 | 122.3786 | 122.087 | -0.12713 | 122.0831 | 122.2458 | 122.0155 | 122.1363 | -0.3839
3607.5938 | 122.2366 | -122.0856 | 0.13733 | 1.4211e-13 | -0.017688 | -0.013718 | -0.044957 | -0.041925 | -0.012352 | -0.0084697 | 0.0083468 | 0.033737 | -0.026394 | 0.013577 | -0.019276 | 0.001048 | 0.015142 | 0.000747 | 0.11622 | 0.096516 | 0.31137 | -0.017268 | 0.019362 | 0.082776 | -0.065509 | 0.020409 | 0.19227 | 0.003172 | -0.25572 | 122.0683 | -0.021104 | 122.0866 | 122.0863 | 0.018015 | -0.040813 | 0.17404 | 121.8298 | -0.11692 | 122.1049 | 122.0201 | 0.19022 | 0.054943 | -0.13416 | 122.2018 | 122.1821 | 122.3969 | 122.1007 | -0.1546 | 122.106 | 122.2778 | 122.0887 | 122.1683 | -0.39305
3609.3906 | 122.3236 | -122.0398 | 0.091553 | 1.4211e-13 | -0.017902 | -0.013718 | -0.044743 | -0.041925 | -0.012565 | -0.0084697 | 0.0089876 | 0.033737 | -0.026394 | 0.013149 | -0.019062 | -0.003531 | 0.019721 | 0.005325 | 0.11165 | 0.096516 | 0.32511 | 0.005627 | 0.02852 | 0.087354 | -0.070087 | 0.011252 | 0.18769 | -0.033457 | -0.25572 | 122.0454 | 0.020094 | 122.0363 | 122.0451 | -0.000302 | 0.004963 | 0.23356 | 121.7841 | -0.080301 | 122.0683 | 121.9697 | 0.18564 | 0.09614 | -0.12501 | 122.1514 | 122.1363 | 122.3649 | 122.0595 | -0.085926 | 122.051 | 122.2275 | 122.0063 | 122.1271 | -0.34728
3611.1719 | 122.3557 | -122.049 | 0.068665 | 1.4211e-13 | -0.017474 | -0.013932 | -0.04517 | -0.041925 | -0.012352 | 0.0067908 | 0.0085604 | 0.03395 | -0.026394 | 0.013149 | -0.019276 | 0.001048 | 0.0243 | 0.000747 | 0.1208 | 0.096516 | 0.31595 | -0.021847 | 0.019362 | 0.073618 | -0.065509 | 0.015831 | 0.18311 | -0.051771 | -0.25572 | 122.0271 | 0.052139 | 122.05 | 122.0497 | 0.022594 | 0.027851 | 0.24729 | 121.7932 | -0.052834 | 122.0683 | 121.9834 | 0.19022 | 0.11445 | -0.12044 | 122.1698 | 122.1455 | 122.3649 | 122.0733 | -0.090512 | 122.0648 | 122.2321 | 121.9972 | 122.1226 | -0.32439
3612.9688 | 122.2778 | -122.113 | 0.1236 | 1.4211e-13 | -0.017688 | -0.013505 | -0.04517 | -0.041711 | -0.012352 | -0.00083919 | 0.0083468 | 0.033523 | -0.026394 | 0.013149 | -0.019062 | 0.001048 | 0.019721 | 0.000747 | 0.1208 | 0.1011 | 0.31595 | 0.001048 | 0.019362 | 0.082776 | -0.065509 | 0.024988 | 0.17854 | -0.033457 | -0.25115 | 122.1141 | -0.002792 | 122.1141 | 122.1138 | -0.000301 | -0.022501 | 0.19236 | 121.8619 | -0.098608 | 122.1324 | 122.0475 | 0.18564 | 0.05494 | -0.15705 | 122.2338 | 122.2141 | 122.429 | 122.1328 | -0.12255 | 122.138 | 122.2916 | 122.0796 | 122.1958 | -0.37474
3614.7031 | 122.287 | -122.0947 | 0.10071 | 1.4211e-13 | -0.017902 | -0.013718 | -0.04517 | -0.041711 | -0.012565 | 0.0067908 | 0.0085604 | 0.033737 | -0.026608 | 0.013363 | -0.019276 | 0.005626 | 0.019721 | 0.005325 | 0.11622 | 0.096516 | 0.31595 | 0.014784 | 0.02852 | 0.06904 | -0.074666 | 0.020409 | 0.17854 | -0.074664 | -0.25572 | 122.1095 | 0.015517 | 122.1004 | 122.1001 | -0.009459 | -0.004192 | 0.21524 | 121.839 | -0.080299 | 122.1232 | 122.0201 | 0.18106 | 0.077828 | -0.17537 | 122.211 | 122.1912 | 122.4107 | 122.1144 | -0.085924 | 122.1151 | 122.2733 | 122.0201 | 122.1638 | -0.35643
3616.5 | 122.2458 | -122.1222 | 0.1236 | 1.4211e-13 | -0.017688 | -0.013505 | -0.044957 | -0.041711 | -0.012779 | 0.014421 | 0.0089876 | 0.033523 | -0.026394 | 0.013577 | -0.019062 | 0.005626 | 0.019721 | 0.000747 | 0.1208 | 0.091937 | 0.3068 | 0.005627 | 0.019362 | 0.078197 | -0.06093 | 0.015831 | 0.18769 | -0.015142 | -0.25115 | 122.1278 | -0.002792 | 122.1278 | 122.1229 | -0.00488 | -0.031659 | 0.1832 | 121.871 | -0.10776 | 122.1416 | 122.0613 | 0.19022 | 0.064097 | -0.13874 | 122.243 | 122.2141 | 122.429 | 122.1419 | -0.11797 | 122.138 | 122.3099 | 122.1071 | 122.2004 | -0.37474
3618.2344 | 122.287 | -122.1176 | 0.1236 | 1.4211e-13 | -0.017902 | -0.013718 | -0.044957 | -0.041711 | -0.012565 | -0.0084697 | 0.0085604 | 0.03395 | -0.026394 | 0.013577 | -0.019062 | 0.001048 | 0.010564 | -0.003831 | 0.1208 | 0.096516 | 0.31137 | 0.010206 | 0.023941 | 0.073618 | -0.06093 | 0.020409 | 0.18311 | -0.033457 | -0.25115 | 122.1278 | -0.002792 | 122.1187 | 122.1138 | -0.014037 | -0.02708 | 0.18778 | 121.8665 | -0.10319 | 122.1416 | 122.0567 | 0.19022 | 0.059519 | -0.15705 | 122.2384 | 122.2141 | 122.429 | 122.1282 | -0.11339 | 122.138 | 122.3007 | 122.0842 | 122.1912 | -0.37474
3620.0156 | 122.3923 | -122.0764 | 0.091553 | 1.4211e-13 | -0.017902 | -0.013718 | -0.045384 | -0.042139 | -0.012352 | -0.00083919 | 0.0085604 | 0.033737 | -0.026181 | 0.013577 | -0.019062 | 0.001048 | 0.010564 | -0.003831 | 0.12538 | 0.096516 | 0.31595 | 0.010206 | 0.023941 | 0.073618 | -0.065509 | 0.015831 | 0.18769 | -0.083821 | -0.25572 | 122.0866 | 0.033829 | 122.0775 | 122.0726 | -0.014037 | 0.004963 | 0.2244 | 121.8207 | -0.075722 | 122.1004 | 122.0109 | 0.19022 | 0.09614 | -0.17537 | 122.2018 | 122.1729 | 122.3924 | 122.087 | -0.081347 | 122.0922 | 122.2641 | 121.9926 | 122.15 | -0.34728
3621.8125 | 122.4014 | -122.0856 | 0.07782 | 1.4211e-13 | -0.017688 | -0.013718 | -0.04517 | -0.041925 | -0.012565 | -0.00083919 | 0.0089876 | 0.033523 | -0.026394 | 0.013363 | -0.019062 | 0.005626 | 0.015142 | -0.003831 | 0.1208 | 0.091937 | 0.32053 | -0.00811 | 0.023941 | 0.082776 | -0.065509 | 0.015831 | 0.17854 | 0.021486 | -0.25572 | 122.0775 | 0.042984 | 122.0912 | 122.0817 | 0.004279 | 0.014117 | 0.24271 | 121.8298 | -0.061989 | 122.1095 | 122.0201 | 0.19022 | 0.10072 | -0.056334 | 122.2064 | 122.1775 | 122.4061 | 122.1007 | -0.08593 | 122.1014 | 122.2641 | 122.1071 | 122.1683 | -0.33354
3623.5469 | 122.3328 | -122.168 | 0.11444 | 1.4211e-13 | -0.018115 | -0.013932 | -0.044957 | -0.041711 | -0.012779 | -0.00083919 | 0.0083468 | 0.033737 | -0.026394 | 0.013577 | -0.019062 | 0.001048 | 0.015142 | 0.000747 | 0.11622 | 0.096516 | 0.31595 | -0.003531 | 0.019362 | 0.091933 | -0.074666 | 0.024988 | 0.17854 | 0.012329 | -0.25572 | 122.1644 | 0.001784 | 122.169 | 122.1687 | 0.004278 | -0.017925 | 0.20151 | 121.9122 | -0.089453 | 122.1873 | 122.0933 | 0.18106 | 0.064095 | -0.10211 | 122.2842 | 122.2645 | 122.4839 | 122.1831 | -0.11797 | 122.193 | 122.3465 | 122.1803 | 122.2599 | -0.37017
3625.3281 | 122.2687 | -122.1588 | 0.12817 | 1.4211e-13 | -0.018115 | -0.014146 | -0.04517 | -0.042139 | -0.012138 | -0.00083919 | 0.0085604 | 0.03395 | -0.026394 | 0.013149 | -0.019276 | 0.001048 | 0.015142 | -0.008409 | 0.1208 | 0.096516 | 0.31137 | 0.014784 | 0.023941 | 0.078197 | -0.070087 | 0.020409 | 0.18311 | -0.0243 | -0.25115 | 122.1736 | -0.00737 | 122.1599 | 122.1504 | -0.023193 | -0.031658 | 0.1832 | 121.9077 | -0.10777 | 122.1828 | 122.0887 | 0.18106 | 0.054941 | -0.15247 | 122.2796 | 122.2553 | 122.4702 | 122.174 | -0.11339 | 122.1792 | 122.3419 | 122.1345 | 122.237 | -0.37932
3627.1094 | 122.4243 | -122.1039 | 0.091553 | 1.4211e-13 | -0.017688 | -0.013718 | -0.045384 | -0.041925 | -0.012565 | -0.00083919 | 0.0085604 | 0.033737 | -0.026181 | 0.013149 | -0.019489 | -0.003531 | 0.019721 | 0.005325 | 0.1208 | 0.1011 | 0.31595 | 0.001048 | 0.023941 | 0.078197 | -0.065509 | 0.011252 | 0.18311 | -0.028878 | -0.24657 | 122.1049 | 0.029251 | 122.1004 | 122.1092 | 0.004277 | 0.009542 | 0.2244 | 121.8573 | -0.080301 | 122.1278 | 122.0384 | 0.18106 | 0.091562 | -0.12043 | 122.2247 | 122.205 | 122.4198 | 122.1236 | -0.090505 | 122.1151 | 122.287 | 122.075 | 122.1821 | -0.33812
3628.8594 | 122.319 | -122.1725 | 0.10071 | 1.4211e-13 | -0.018115 | -0.013932 | -0.044957 | -0.041711 | -0.012565 | -0.0084697 | 0.0081332 | 0.03395 | -0.026608 | 0.013149 | -0.019276 | -0.003531 | 0.010564 | -0.008409 | 0.12538 | 0.091937 | 0.31595 | 0.001048 | 0.023941 | 0.078197 | -0.070087 | 0.020409 | 0.18769 | -0.015142 | -0.24657 | 122.1736 | 0.024674 | 122.169 | 122.1641 | -0.009457 | -0.008771 | 0.21524 | 121.926 | -0.080299 | 122.1965 | 122.1025 | 0.17648 | 0.086985 | -0.11585 | 122.2979 | 122.2645 | 122.4885 | 122.1831 | -0.09966 | 122.193 | 122.3602 | 122.1574 | 122.2507 | -0.34728
3630.6562 | 122.4106 | -122.168 | 0.082397 | 1.4211e-13 | -0.017688 | -0.013718 | -0.04517 | -0.041925 | -0.012779 | -0.0084697 | 0.0083468 | 0.033737 | -0.026821 | 0.013363 | -0.019062 | 0.005626 | 0.019721 | 0.000747 | 0.12538 | 0.096516 | 0.3068 | -0.012689 | 0.019362 | 0.073618 | -0.070087 | 0.029566 | 0.18311 | -0.019721 | -0.25115 | 122.1553 | 0.042985 | 122.1736 | 122.1687 | 0.013436 | 0.014119 | 0.2244 | 121.9168 | -0.052831 | 122.1873 | 122.0979 | 0.18106 | 0.10072 | -0.10212 | 122.2934 | 122.2645 | 122.4748 | 122.1877 | -0.095086 | 122.1975 | 122.3511 | 122.1482 | 122.2416 | -0.33354
3632.4375 | 122.3465 | -122.1588 | 0.11902 | 1.4211e-13 | -0.017902 | -0.013718 | -0.04517 | -0.041711 | -0.012565 | 0.0067908 | 0.0085604 | 0.033737 | -0.026394 | 0.013577 | -0.019489 | 0.005626 | 0.019721 | 0.000747 | 0.11622 | 0.091937 | 0.3068 | 0.010206 | 0.023941 | 0.082776 | -0.070087 | 0.015831 | 0.17396 | 0.021486 | -0.2603 | 122.169 | -0.002794 | 122.1644 | 122.1596 | -0.009459 | -0.027082 | 0.18778 | 121.8985 | -0.10319 | 122.1828 | 122.0887 | 0.19022 | 0.054939 | -0.097533 | 122.275 | 122.2507 | 122.4656 | 122.1785 | -0.10881 | 122.1746 | 122.3328 | 122.1803 | 122.2416 | -0.37932
3634.2188 | 122.3145 | -122.1909 | 0.10529 | 1.4211e-13 | -0.017902 | -0.014146 | -0.044957 | -0.041711 | -0.012565 | -0.0084697 | 0.0085604 | 0.033737 | -0.026394 | 0.013363 | -0.019276 | 0.001048 | 0.019721 | -0.003831 | 0.1208 | 0.087359 | 0.31137 | 0.010206 | 0.023941 | 0.073618 | -0.070087 | 0.015831 | 0.18311 | -0.028878 | -0.25115 | 122.2011 | 0.015518 | 122.1919 | 122.187 | -0.014037 | -0.017927 | 0.20609 | 121.9397 | -0.089455 | 122.2148 | 122.1208 | 0.18106 | 0.077829 | -0.13416 | 122.3117 | 122.2782 | 122.5022 | 122.2106 | -0.09508 | 122.2067 | 122.374 | 122.162 | 122.2645 | -0.35643
3635.9688 | 122.4518 | -122.1497 | 0.082397 | 1.4211e-13 | -0.017902 | -0.013932 | -0.044957 | -0.041925 | -0.012138 | -0.00083919 | 0.0083468 | 0.033737 | -0.026394 | 0.013577 | -0.019489 | 0.010204 | 0.0243 | -0.003831 | 0.12538 | 0.096516 | 0.31595 | -0.00811 | 0.023941 | 0.078197 | -0.074666 | 0.015831 | 0.17854 | -0.019721 | -0.25115 | 122.1415 | 0.042985 | 122.1599 | 122.1458 | 0.004279 | 0.014119 | 0.23356 | 121.8985 | -0.066566 | 122.1736 | 122.075 | 0.17648 | 0.096139 | -0.10212 | 122.275 | 122.2462 | 122.4656 | 122.174 | -0.090507 | 122.1655 | 122.3282 | 122.1299 | 122.2279 | -0.33354
3637.75 | 122.4106 | -122.1359 | 0.091553 | 1.4211e-13 | -0.017902 | -0.013718 | -0.044957 | -0.041925 | -0.012565 | -0.00083919 | 0.0081332 | 0.033737 | -0.026181 | 0.013149 | -0.019062 | 0.001048 | 0.010564 | 0.005325 | 0.12538 | 0.1011 | 0.31595 | 0.010206 | 0.023941 | 0.082776 | -0.070087 | 0.011252 | 0.18311 | -0.019721 | -0.25115 | 122.1461 | 0.033829 | 122.137 | 122.1412 | -0.004881 | 0.009542 | 0.2244 | 121.8848 | -0.080301 | 122.1599 | 122.0658 | 0.18106 | 0.091562 | -0.11127 | 122.2613 | 122.237 | 122.4519 | 122.1465 | -0.081347 | 122.1472 | 122.319 | 122.1162 | 122.2187 | -0.3427
3639.5469 | 122.3328 | -122.1863 | 0.13275 | 1.4211e-13 | -0.018115 | -0.014146 | -0.04517 | -0.041711 | -0.012565 | -0.00083919 | 0.0085604 | 0.034164 | -0.026608 | 0.013577 | -0.019062 | 0.005626 | 0.019721 | 0.005325 | 0.1208 | 0.091937 | 0.32511 | 0.001048 | 0.023941 | 0.078197 | -0.074666 | 0.020409 | 0.18311 | -0.010564 | -0.25572 | 122.1873 | -0.011947 | 122.1919 | 122.1916 | 0.004277 | -0.040814 | 0.19236 | 121.9306 | -0.11234 | 122.2102 | 122.1116 | 0.18106 | 0.050364 | -0.14331 | 122.3071 | 122.2782 | 122.5114 | 122.206 | -0.1317 | 122.2067 | 122.3694 | 122.1757 | 122.2645 | -0.38848
3641.2656 | 122.3557 | -122.1542 | 0.10529 | 1.4211e-13 | -0.017902 | -0.013718 | -0.04517 | -0.042139 | -0.012565 | -0.00083919 | 0.0083468 | 0.033737 | -0.026394 | 0.013577 | -0.019489 | 0.001048 | 0.019721 | -0.003831 | 0.1208 | 0.1011 | 0.32053 | -0.026426 | 0.019362 | 0.078197 | -0.070087 | 0.020409 | 0.17854 | 0.039801 | -0.25115 | 122.1278 | 0.015518 | 122.1553 | 122.1504 | 0.022595 | -0.004191 | 0.21525 | 121.9031 | -0.084877 | 122.1736 | 122.0841 | 0.18106 | 0.07325 | -0.065485 | 122.275 | 122.2553 | 122.4748 | 122.174 | -0.13171 | 122.1746 | 122.3328 | 122.194 | 122.2324 | -0.35643
3643.0625 | 122.3511 | -122.2 | 0.1236 | 1.4211e-13 | -0.018115 | -0.013932 | -0.04517 | -0.041925 | -0.012352 | -0.0084697 | 0.008774 | 0.033523 | -0.026394 | 0.013577 | -0.019703 | 0.005626 | 0.0243 | 0.000747 | 0.1208 | 0.091937 | 0.31137 | 0.001048 | 0.023941 | 0.082776 | -0.070087 | 0.015831 | 0.18311 | 0.026065 | -0.24657 | 122.2011 | -0.002792 | 122.2056 | 122.2008 | -0.000301 | -0.031659 | 0.18778 | 121.9534 | -0.10776 | 122.224 | 122.1299 | 0.17648 | 0.059519 | -0.097531 | 122.3208 | 122.2919 | 122.5114 | 122.2243 | -0.12255 | 122.2158 | 122.3831 | 122.2261 | 122.2828 | -0.37016
3644.8438 | 122.4014 | -122.2046 | 0.11444 | 1.4211e-13 | -0.017902 | -0.013932 | -0.045384 | -0.042139 | -0.012352 | 0.0067908 | 0.0081332 | 0.033737 | -0.026608 | 0.01379 | -0.019276 | 0.001048 | 0.015142 | -0.003831 | 0.12538 | 0.096516 | 0.31595 | 0.001048 | 0.019362 | 0.082776 | -0.074666 | 0.011252 | 0.18311 | 0.003172 | -0.25572 | 122.2056 | 0.010941 | 122.2056 | 122.2008 | -0.004879 | -0.017925 | 0.20151 | 121.9489 | -0.10319 | 122.224 | 122.1299 | 0.18106 | 0.068674 | -0.11127 | 122.33 | 122.3011 | 122.5205 | 122.2197 | -0.11339 | 122.2158 | 122.3877 | 122.2078 | 122.2874 | -0.37017
3646.6406 | 122.3236 | -122.2 | 0.12817 | 1.4211e-13 | -0.017902 | -0.013718 | -0.045384 | -0.042566 | -0.012352 | -0.00083919 | 0.0085604 | 0.03395 | -0.026394 | 0.013149 | -0.019276 | 0.005626 | 0.019721 | 0.000747 | 0.1208 | 0.1011 | 0.32053 | 0.005627 | 0.02852 | 0.078197 | -0.074666 | 0.015831 | 0.18311 | 0.035222 | -0.25115 | 122.2056 | -0.00737 | 122.2056 | 122.2008 | -0.00488 | -0.027079 | 0.19236 | 121.9489 | -0.11234 | 122.2285 | 122.1253 | 0.17648 | 0.054941 | -0.092952 | 122.3208 | 122.3011 | 122.5205 | 122.2197 | -0.12255 | 122.2158 | 122.3831 | 122.2352 | 122.2782 | -0.37932
3648.4531 | 122.3648 | -122.2366 | 0.12817 | 1.4211e-13 | -0.018115 | -0.013932 | -0.04517 | -0.041925 | -0.012565 | -0.00083919 | 0.0085604 | 0.033523 | -0.026821 | 0.013149 | -0.019489 | 0.001048 | 0.015142 | -0.003831 | 0.1208 | 0.096516 | 0.31137 | 0.005627 | 0.023941 | 0.078197 | -0.070087 | 0.011252 | 0.17854 | -0.005985 | -0.25572 | 122.2423 | -0.00737 | 122.2377 | 122.2328 | -0.009458 | -0.031658 | 0.1832 | 121.9809 | -0.11692 | 122.2606 | 122.1665 | 0.18564 | 0.050362 | -0.13416 | 122.3574 | 122.3331 | 122.548 | 122.2518 | -0.12255 | 122.2479 | 122.4152 | 122.2306 | 122.3148 | -0.3839
3650.2344 | 122.3602 | -122.2137 | 0.11902 | 1.4211e-13 | -0.017902 | -0.013718 | -0.044743 | -0.042139 | -0.012565 | -0.00083919 | 0.0083468 | 0.033737 | -0.026394 | 0.013577 | -0.019276 | -0.003531 | 0.019721 | -0.003831 | 0.12996 | 0.096516 | 0.32053 | 0.010206 | 0.023941 | 0.06904 | -0.065509 | 0.015831 | 0.17854 | -0.042614 | -0.25572 | 122.224 | 0.010941 | 122.2102 | 122.2099 | -0.014037 | -0.022503 | 0.20151 | 121.958 | -0.10319 | 122.2377 | 122.1482 | 0.19022 | 0.059517 | -0.16163 | 122.3437 | 122.3103 | 122.5343 | 122.2335 | -0.10881 | 122.2296 | 122.3923 | 122.1711 | 122.2828 | -0.37474
3651.9844 | 122.4472 | -122.2092 | 0.10986 | 1.4211e-13 | -0.018115 | -0.013505 | -0.044957 | -0.042139 | -0.012565 | -0.0161 | 0.0081332 | 0.03395 | -0.026394 | 0.01379 | -0.019062 | 0.001048 | 0.015142 | 0.000747 | 0.1208 | 0.091937 | 0.31137 | -0.026426 | 0.023941 | 0.082776 | -0.070087 | 0.015831 | 0.18769 | 0.007751 | -0.25115 | 122.1827 | 0.010941 | 122.2102 | 122.2099 | 0.027173 | -0.017926 | 0.20151 | 121.958 | -0.094032 | 122.2331 | 122.1391 | 0.18106 | 0.07783 | -0.10211 | 122.33 | 122.3011 | 122.5205 | 122.2243 | -0.13629 | 122.225 | 122.3969 | 122.2169 | 122.2919 | -0.36101
3653.7812 | 122.374 | -122.2412 | 0.11444 | 1.4211e-13 | -0.018329 | -0.013932 | -0.044957 | -0.041925 | -0.012779 | -0.0084697 | 0.008774 | 0.033309 | -0.026394 | 0.013577 | -0.019276 | 0.001048 | 0.015142 | -0.003831 | 0.1208 | 0.1011 | 0.31137 | -0.003531 | 0.019362 | 0.078197 | -0.074666 | 0.020409 | 0.18311 | 0.007751 | -0.2603 | 122.2377 | 0.006363 | 122.2423 | 122.2374 | -0.0003 | -0.013346 | 0.19693 | 121.9809 | -0.094032 | 122.2606 | 122.1665 | 0.18564 | 0.068674 | -0.10669 | 122.362 | 122.3423 | 122.5526 | 122.2564 | -0.11797 | 122.2616 | 122.4243 | 122.249 | 122.3194 | -0.37474
3655.5781 | 122.3557 | -122.2458 | 0.14648 | 1.4211e-13 | -0.017902 | -0.013718 | -0.044743 | -0.042352 | -0.012779 | -0.0084697 | 0.0085604 | 0.033523 | -0.026394 | 0.013363 | -0.019276 | -0.003531 | 0.015142 | -0.003831 | 0.1208 | 0.096516 | 0.31595 | 0.005627 | 0.02852 | 0.082776 | -0.065509 | 0.020409 | 0.17854 | 0.007751 | -0.25115 | 122.2514 | -0.02568 | 122.2423 | 122.242 | -0.009458 | -0.049968 | 0.16947 | 121.9946 | -0.12607 | 122.2743 | 122.1803 | 0.18564 | 0.032052 | -0.13873 | 122.3666 | 122.3423 | 122.5617 | 122.2609 | -0.14086 | 122.2662 | 122.4243 | 122.2535 | 122.3286 | -0.39763
3657.3281 | 122.5204 | -122.2092 | 0.091553 | 1.4211e-13 | -0.017902 | -0.013932 | -0.044743 | -0.041925 | -0.012779 | 0.0067908 | 0.0085604 | 0.03395 | -0.026608 | 0.013363 | -0.019062 | 0.001048 | 0.015142 | -0.003831 | 0.1208 | 0.091937 | 0.31595 | 0.005627 | 0.023941 | 0.082776 | -0.074666 | 0.015831 | 0.17854 | -0.015142 | -0.25572 | 122.2148 | 0.029251 | 122.2102 | 122.2053 | -0.009458 | 0.000384 | 0.2244 | 121.9534 | -0.075722 | 122.2331 | 122.1345 | 0.18106 | 0.086983 | -0.10669 | 122.33 | 122.3011 | 122.5251 | 122.2243 | -0.085926 | 122.225 | 122.3877 | 122.194 | 122.2919 | -0.34728
3659.1094 | 122.3831 | -122.2687 | 0.10071 | 1.4211e-13 | -0.017902 | -0.013718 | -0.044743 | -0.041925 | -0.012779 | -0.0084697 | 0.0085604 | 0.033737 | -0.026608 | 0.01379 | -0.019276 | -0.003531 | 0.019721 | -0.003831 | 0.1208 | 0.10567 | 0.31595 | -0.012689 | 0.023941 | 0.082776 | -0.06093 | 0.015831 | 0.18769 | -0.028878 | -0.24657 | 122.256 | 0.020096 | 122.2651 | 122.2648 | 0.008858 | 0.004966 | 0.21524 | 122.0221 | -0.084877 | 122.2926 | 122.2077 | 0.18564 | 0.086985 | -0.12959 | 122.3895 | 122.3744 | 122.5846 | 122.2884 | -0.1134 | 122.2845 | 122.4564 | 122.2398 | 122.3515 | -0.34728
3660.8594 | 122.4014 | -122.2687 | 0.12817 | 1.4211e-13 | -0.017688 | -0.013718 | -0.045384 | -0.042139 | -0.012352 | -0.0161 | 0.0085604 | 0.033737 | -0.026181 | 0.013577 | -0.019276 | 0.005626 | 0.019721 | -0.003831 | 0.12538 | 0.096516 | 0.31595 | -0.017268 | 0.023941 | 0.073618 | -0.070087 | 0.011252 | 0.17854 | 0.021486 | -0.25115 | 122.2514 | -0.002792 | 122.2743 | 122.2648 | 0.013437 | -0.031658 | 0.18778 | 122.0175 | -0.11692 | 122.2926 | 122.1986 | 0.18106 | 0.050362 | -0.10669 | 122.3941 | 122.3652 | 122.5846 | 122.2884 | -0.14544 | 122.2799 | 122.4472 | 122.2902 | 122.3423 | -0.37932
3662.6562 | 122.4197 | -122.2321 | 0.11444 | 1.4211e-13 | -0.018115 | -0.013718 | -0.044529 | -0.041711 | -0.012565 | -0.00083919 | 0.0089876 | 0.033523 | -0.026608 | 0.013363 | -0.019276 | 0.005626 | 0.028878 | 0.000747 | 0.11622 | 0.091937 | 0.32053 | -0.031005 | 0.023941 | 0.082776 | -0.065509 | 0.020409 | 0.18311 | 0.021486 | -0.25115 | 122.2011 | 0.001784 | 122.2377 | 122.2328 | 0.031752 | -0.022504 | 0.20609 | 121.9809 | -0.094032 | 122.256 | 122.1665 | 0.18564 | 0.068674 | -0.092955 | 122.3483 | 122.324 | 122.5526 | 122.2609 | -0.14545 | 122.2525 | 122.4152 | 122.2535 | 122.3148 | -0.36559
3664.4531 | 122.4518 | -122.2412 | 0.10071 | 1.4211e-13 | -0.018329 | -0.013505 | -0.045384 | -0.041925 | -0.012352 | -0.0084697 | 0.0085604 | 0.033737 | -0.026608 | 0.013363 | -0.019489 | 0.010204 | 0.005985 | -0.003831 | 0.12996 | 0.091937 | 0.31137 | 0.014784 | 0.019362 | 0.078197 | -0.070087 | 0.015831 | 0.18769 | -0.015142 | -0.25572 | 122.256 | 0.029252 | 122.2514 | 122.2374 | -0.018615 | -0.008771 | 0.21067 | 121.9855 | -0.084877 | 122.2606 | 122.1711 | 0.18564 | 0.086985 | -0.11585 | 122.3712 | 122.3331 | 122.5526 | 122.2472 | -0.085924 | 122.257 | 122.4289 | 122.2261 | 122.3194 | -0.35643
3666.2344 | 122.4152 | -122.2504 | 0.1236 | 1.4211e-13 | -0.017902 | -0.013718 | -0.044743 | -0.041925 | -0.012565 | 0.014421 | 0.0085604 | 0.033737 | -0.026181 | 0.01379 | -0.019276 | 0.010204 | 0.010564 | -0.003831 | 0.12996 | 0.096516 | 0.31595 | 0.001048 | 0.019362 | 0.078197 | -0.065509 | 0.020409 | 0.17854 | -0.019721 | -0.25572 | 122.2514 | 0.006364 | 122.2606 | 122.2465 | -0.004879 | -0.02708 | 0.19236 | 121.9946 | -0.10319 | 122.2697 | 122.1849 | 0.19022 | 0.05494 | -0.14332 | 122.3803 | 122.3469 | 122.5663 | 122.2609 | -0.12255 | 122.2708 | 122.4289 | 122.2306 | 122.3286 | -0.37932
3667.9688 | 122.3923 | -122.2733 | 0.12817 | 1.4211e-13 | -0.018115 | -0.013932 | -0.04517 | -0.041925 | -0.012565 | -0.0084697 | 0.008774 | 0.033737 | -0.026394 | 0.013363 | -0.019276 | -0.003531 | 0.019721 | -0.003831 | 0.12996 | 0.096516 | 0.31137 | 0.010206 | 0.023941 | 0.06904 | -0.074666 | 0.020409 | 0.17854 | -0.028878 | -0.25115 | 122.2835 | 0.001786 | 122.2697 | 122.2694 | -0.014037 | -0.031658 | 0.1832 | 122.0221 | -0.10777 | 122.2972 | 122.1986 | 0.17648 | 0.050362 | -0.15705 | 122.4032 | 122.3698 | 122.5846 | 122.293 | -0.11797 | 122.2937 | 122.4518 | 122.2444 | 122.3423 | -0.37932
3669.75 | 122.5342 | -122.2275 | 0.07782 | 1.4211e-13 | -0.018329 | -0.013718 | -0.044957 | -0.041925 | -0.012565 | -0.00083919 | 0.0085604 | 0.03395 | -0.026181 | 0.013363 | -0.019489 | 0.001048 | 0.019721 | 0.005325 | 0.11622 | 0.091937 | 0.31595 | -0.00811 | 0.023941 | 0.087354 | -0.074666 | 0.015831 | 0.18311 | 0.003172 | -0.25115 | 122.2194 | 0.038405 | 122.2285 | 122.2328 | 0.013435 | 0.014117 | 0.23813 | 121.9763 | -0.061989 | 122.2514 | 122.1528 | 0.17648 | 0.10529 | -0.074648 | 122.3437 | 122.3194 | 122.5434 | 122.2472 | -0.08593 | 122.2433 | 122.4106 | 122.2307 | 122.3148 | -0.32897
3671.5469 | 122.4106 | -122.3007 | 0.12817 | 1.4211e-13 | -0.017902 | -0.013932 | -0.04517 | -0.041925 | -0.012352 | -0.0084697 | 0.008774 | 0.033737 | -0.026181 | 0.013577 | -0.019276 | -0.003531 | 0.019721 | -0.003831 | 0.1208 | 0.091937 | 0.31595 | -0.021847 | 0.019362 | 0.082776 | -0.074666 | 0.024988 | 0.18311 | -0.05635 | -0.25572 | 122.2789 | -0.00737 | 122.2972 | 122.2969 | 0.018016 | -0.036237 | 0.18778 | 122.045 | -0.10319 | 122.3201 | 122.2261 | 0.18106 | 0.054941 | -0.18452 | 122.4215 | 122.3927 | 122.6167 | 122.3204 | -0.15002 | 122.3257 | 122.4838 | 122.2444 | 122.3835 | -0.3839
3673.3438 | 122.438 | -122.3053 | 0.12817 | 1.4211e-13 | -0.017902 | -0.013932 | -0.044957 | -0.041925 | -0.012779 | -0.0161 | 0.0085604 | 0.033523 | -0.026608 | 0.013363 | -0.019276 | 0.001048 | 0.019721 | 0.000747 | 0.12538 | 0.1011 | 0.31595 | 0.014784 | 0.019362 | 0.082776 | -0.074666 | 0.020409 | 0.18311 | -0.019721 | -0.25572 | 122.3201 | -0.002792 | 122.3063 | 122.306 | -0.014037 | -0.027079 | 0.18778 | 122.0496 | -0.10777 | 122.3247 | 122.2306 | 0.18106 | 0.054941 | -0.14789 | 122.4307 | 122.4064 | 122.6213 | 122.325 | -0.11339 | 122.3257 | 122.4884 | 122.2856 | 122.3881 | -0.3839
3675.1406 | 122.4197 | -122.3053 | 0.1236 | 1.4211e-13 | -0.018115 | -0.013932 | -0.04517 | -0.041925 | -0.012565 | -0.00083919 | 0.0083468 | 0.033737 | -0.026394 | 0.012936 | -0.019276 | 0.001048 | 0.019721 | -0.003831 | 0.12996 | 0.10567 | 0.31595 | 0.001048 | 0.019362 | 0.078197 | -0.070087 | 0.011252 | 0.18769 | -0.015142 | -0.25115 | 122.3063 | 0.006364 | 122.3063 | 122.3015 | -0.004879 | -0.017922 | 0.19236 | 122.0542 | -0.11234 | 122.3247 | 122.2352 | 0.18106 | 0.064097 | -0.13874 | 122.4353 | 122.411 | 122.6213 | 122.325 | -0.12255 | 122.3165 | 122.493 | 122.2902 | 122.3835 | -0.37474
3676.9375 | 122.4747 | -122.3007 | 0.11902 | 1.4211e-13 | -0.018543 | -0.013932 | -0.044957 | -0.041711 | -0.012352 | 0.0067908 | 0.008774 | 0.033737 | -0.026608 | 0.013363 | -0.019062 | 0.001048 | 0.015142 | -0.003831 | 0.12538 | 0.087359 | 0.31137 | 0.001048 | 0.023941 | 0.078197 | -0.074666 | 0.020409 | 0.18311 | -0.079243 | -0.25572 | 122.3018 | 0.006363 | 122.3018 | 122.2969 | -0.004879 | -0.03166 | 0.19235 | 122.045 | -0.09861 | 122.3247 | 122.2261 | 0.18106 | 0.064096 | -0.19826 | 122.4261 | 122.3881 | 122.6121 | 122.3159 | -0.11797 | 122.3211 | 122.4838 | 122.2215 | 122.3789 | -0.37474
3678.6719 | 122.4747 | -122.287 | 0.09613 | 1.4211e-13 | -0.018329 | -0.013718 | -0.044957 | -0.042139 | -0.012565 | -0.00083919 | 0.008774 | 0.03395 | -0.026608 | 0.01379 | -0.019703 | 0.005626 | 0.019721 | -0.008409 | 0.12538 | 0.096516 | 0.31595 | -0.003531 | 0.019362 | 0.087354 | -0.070087 | 0.015831 | 0.18311 | -0.0243 | -0.25572 | 122.2835 | 0.029252 | 122.2926 | 122.2786 | -0.004878 | 0.000386 | 0.21982 | 122.0313 | -0.080299 | 122.3063 | 122.2169 | 0.18564 | 0.086985 | -0.12043 | 122.4124 | 122.3835 | 122.6029 | 122.3067 | -0.099661 | 122.3028 | 122.4701 | 122.2627 | 122.3743 | -0.35185
3680.4688 | 122.5616 | -122.2412 | 0.07782 | 1.4211e-13 | -0.018115 | -0.013718 | -0.044743 | -0.042139 | -0.012779 | -0.00083919 | 0.0083468 | 0.033737 | -0.026394 | 0.013577 | -0.019276 | 0.005626 | 0.019721 | -0.003831 | 0.1208 | 0.091937 | 0.31137 | -0.012689 | 0.019362 | 0.082776 | -0.070087 | 0.015831 | 0.17854 | -0.051771 | -0.25572 | 122.2285 | 0.042984 | 122.2468 | 122.2374 | 0.008858 | 0.014117 | 0.23355 | 121.9855 | -0.061989 | 122.2606 | 122.1711 | 0.18564 | 0.10072 | -0.12959 | 122.362 | 122.3331 | 122.5526 | 122.2609 | -0.090509 | 122.257 | 122.4197 | 122.1894 | 122.324 | -0.33354
3682.2031 | 122.5571 | -122.2778 | 0.07782 | 1.4211e-13 | -0.018329 | -0.013291 | -0.044957 | -0.041925 | -0.012565 | -0.0084697 | 0.008774 | 0.03395 | -0.026608 | 0.013363 | -0.019276 | 0.001048 | 0.019721 | 0.005325 | 0.1208 | 0.096516 | 0.32053 | 0.001048 | 0.02852 | 0.073618 | -0.070087 | 0.006674 | 0.18311 | -0.074664 | -0.25115 | 122.2789 | 0.042984 | 122.2789 | 122.2832 | 0.004277 | 0.018696 | 0.24271 | 122.0267 | -0.071146 | 122.3064 | 122.2077 | 0.18106 | 0.10529 | -0.15248 | 122.3986 | 122.3743 | 122.5984 | 122.2976 | -0.076772 | 122.2845 | 122.4609 | 122.2032 | 122.3514 | -0.32897
3684.0156 | 122.4792 | -122.2687 | 0.11444 | 1.4211e-13 | -0.018329 | -0.014359 | -0.04517 | -0.041925 | -0.012779 | -0.00083919 | 0.008774 | 0.033737 | -0.026608 | 0.013577 | -0.019489 | 0.001048 | 0.015142 | 0.000747 | 0.11622 | 0.096516 | 0.31595 | 0.001048 | 0.019362 | 0.078197 | -0.070087 | 0.015831 | 0.18311 | -0.097557 | -0.25572 | 122.2697 | 0.001784 | 122.2697 | 122.2694 | -0.000301 | -0.017925 | 0.20151 | 122.013 | -0.09861 | 122.288 | 122.1986 | 0.18564 | 0.068674 | -0.212 | 122.3849 | 122.3652 | 122.5846 | 122.2838 | -0.11339 | 122.2845 | 122.4518 | 122.1711 | 122.3469 | -0.37017
3685.75 | 122.4426 | -122.3099 | 0.12817 | 1.4211e-13 | -0.017902 | -0.013932 | -0.045384 | -0.041925 | -0.012565 | -0.00083919 | 0.008774 | 0.033523 | -0.026394 | 0.013577 | -0.019489 | 0.001048 | 0.019721 | -0.003831 | 0.12996 | 0.10567 | 0.31137 | 0.010206 | 0.019362 | 0.078197 | -0.070087 | 0.015831 | 0.18769 | -0.074664 | -0.25115 | 122.3201 | 0.001786 | 122.3109 | 122.306 | -0.014037 | -0.0225 | 0.1832 | 122.0587 | -0.11234 | 122.3292 | 122.2398 | 0.18106 | 0.059519 | -0.20284 | 122.4398 | 122.4155 | 122.6212 | 122.3296 | -0.11797 | 122.3257 | 122.4976 | 122.2352 | 122.3881 | -0.37932
3687.5469 | 122.4426 | -122.3145 | 0.12817 | 1.4211e-13 | -0.018329 | -0.013718 | -0.045598 | -0.042352 | -0.012779 | -0.00083919 | 0.0089876 | 0.033523 | -0.026608 | 0.013363 | -0.019062 | 0.001048 | 0.015142 | 0.000747 | 0.12996 | 0.096516 | 0.31137 | 0.014784 | 0.019362 | 0.078197 | -0.074666 | 0.015831 | 0.18311 | -0.10671 | -0.25115 | 122.3292 | 0.001786 | 122.3155 | 122.3152 | -0.014037 | -0.031658 | 0.1832 | 122.0633 | -0.11234 | 122.3338 | 122.2398 | 0.17648 | 0.054941 | -0.23489 | 122.4444 | 122.411 | 122.6258 | 122.3296 | -0.11339 | 122.3303 | 122.4976 | 122.2077 | 122.3927 | -0.37932
3689.2656 | 122.6028 | -122.2778 | 0.091553 | 1.4211e-13 | -0.018115 | -0.013718 | -0.04517 | -0.041925 | -0.012779 | -0.00083919 | 0.008774 | 0.033523 | -0.026608 | 0.013363 | -0.019489 | 0.005626 | 0.015142 | 0.000747 | 0.12538 | 0.087359 | 0.31595 | 0.014784 | 0.019362 | 0.078197 | -0.065509 | 0.020409 | 0.18769 | -0.060928 | -0.25115 | 122.2926 | 0.033829 | 122.2835 | 122.2786 | -0.014037 | -0.004194 | 0.2244 | 122.0267 | -0.071144 | 122.2972 | 122.2123 | 0.18564 | 0.09614 | -0.15248 | 122.4032 | 122.3652 | 122.5938 | 122.293 | -0.076769 | 122.2982 | 122.4655 | 122.2169 | 122.356 | -0.3427
3691.0781 | 122.5983 | -122.2916 | 0.091553 | 1.4211e-13 | -0.018115 | -0.013932 | -0.04517 | -0.041925 | -0.012779 | -0.0084697 | 0.0092014 | 0.033523 | -0.026394 | 0.01379 | -0.019489 | 0.001048 | 0.010564 | -0.008409 | 0.12538 | 0.087359 | 0.32053 | 0.010206 | 0.023941 | 0.087354 | -0.070087 | 0.015831 | 0.18769 | -0.074664 | -0.2603 | 122.3018 | 0.033829 | 122.2926 | 122.2832 | -0.018615 | -0.004194 | 0.22898 | 122.0313 | -0.075722 | 122.3155 | 122.2215 | 0.19022 | 0.09614 | -0.16622 | 122.4169 | 122.3789 | 122.6121 | 122.3021 | -0.081347 | 122.3074 | 122.4793 | 122.2169 | 122.3789 | -0.35186
3692.875 | 122.4747 | -122.3236 | 0.1236 | 1.4211e-13 | -0.018115 | -0.013505 | -0.04517 | -0.041711 | -0.012565 | -0.00083919 | 0.008774 | 0.033523 | -0.026394 | 0.01379 | -0.019489 | 0.005626 | 0.015142 | -0.003831 | 0.1208 | 0.1011 | 0.31595 | -0.003531 | 0.019362 | 0.078197 | -0.070087 | 0.015831 | 0.19227 | -0.047193 | -0.25115 | 122.3201 | -0.002792 | 122.3292 | 122.3198 | -0.0003 | -0.022501 | 0.19236 | 122.0725 | -0.10776 | 122.343 | 122.2535 | 0.18106 | 0.068676 | -0.17079 | 122.4444 | 122.4247 | 122.6396 | 122.3388 | -0.12713 | 122.3394 | 122.5159 | 122.2764 | 122.4018 | -0.37474
3694.6719 | 122.4747 | -122.3282 | 0.12817 | 1.4211e-13 | -0.018329 | -0.013718 | -0.04517 | -0.041925 | -0.012565 | 0.0067908 | 0.0089876 | 0.033096 | -0.026608 | 0.01379 | -0.019276 | 0.005626 | 0.0243 | -0.008409 | 0.12538 | 0.1011 | 0.31595 | 0.005627 | 0.023941 | 0.082776 | -0.074666 | 0.015831 | 0.18769 | -0.042614 | -0.25572 | 122.3338 | -0.002792 | 122.3338 | 122.3198 | -0.014036 | -0.027079 | 0.18778 | 122.0725 | -0.11234 | 122.3521 | 122.2535 | 0.18106 | 0.059519 | -0.17079 | 122.4536 | 122.4293 | 122.6441 | 122.3525 | -0.12255 | 122.344 | 122.5159 | 122.2856 | 122.411 | -0.3839
3696.4688 | 122.5708 | -122.3145 | 0.07782 | 1.4211e-13 | -0.018115 | -0.013932 | -0.04517 | -0.042139 | -0.012352 | -0.00083919 | 0.008774 | 0.033523 | -0.026608 | 0.013363 | -0.019062 | 0.005626 | 0.0243 | -0.003831 | 0.11622 | 0.1011 | 0.31137 | -0.017268 | 0.02852 | 0.082776 | -0.065509 | 0.011252 | 0.19227 | -0.015142 | -0.25115 | 122.2972 | 0.038405 | 122.3201 | 122.3106 | 0.013437 | 0.023275 | 0.23355 | 122.0633 | -0.066568 | 122.343 | 122.2489 | 0.18564 | 0.11445 | -0.092962 | 122.4307 | 122.4155 | 122.6258 | 122.3388 | -0.095088 | 122.3257 | 122.5067 | 122.2993 | 122.3972 | -0.32897
3698.1875 | 122.5159 | -122.3282 | 0.11902 | 1.4211e-13 | -0.018115 | -0.013932 | -0.044957 | -0.041925 | -0.012779 | -0.00083919 | 0.0092014 | 0.033737 | -0.026608 | 0.013363 | -0.019276 | 0.005626 | 0.019721 | 0.000747 | 0.1208 | 0.091937 | 0.31595 | -0.012689 | 0.019362 | 0.073618 | -0.070087 | 0.015831 | 0.18769 | -0.0243 | -0.25115 | 122.3155 | 0.001785 | 122.3338 | 122.3289 | 0.013436 | -0.027082 | 0.19693 | 122.077 | -0.10319 | 122.3475 | 122.2581 | 0.18106 | 0.068674 | -0.14332 | 122.449 | 122.4201 | 122.6441 | 122.3479 | -0.13171 | 122.344 | 122.5159 | 122.3039 | 122.4018 | -0.37016
3700 | 122.4747 | -122.3419 | 0.11902 | 1.4211e-13 | -0.018115 | -0.013932 | -0.04517 | -0.041925 | -0.012565 | -0.00083919 | 0.0085604 | 0.033523 | -0.026394 | 0.014004 | -0.019917 | -0.003531 | 0.015142 | -0.003831 | 0.12996 | 0.096516 | 0.31595 | -0.012689 | 0.023941 | 0.073618 | -0.070087 | 0.020409 | 0.18769 | -0.047193 | -0.25572 | 122.3292 | 0.010941 | 122.3384 | 122.3381 | 0.008858 | -0.022503 | 0.19693 | 122.0862 | -0.09861 | 122.3659 | 122.2718 | 0.18564 | 0.068674 | -0.16621 | 122.4719 | 122.4384 | 122.6579 | 122.3571 | -0.13171 | 122.3623 | 122.5296 | 122.2947 | 122.4155 | -0.37474
3701.7969 | 122.4701 | -122.3328 | 0.1236 | 1.4211e-13 | -0.018115 | -0.013505 | -0.04517 | -0.041925 | -0.012565 | 0.0067908 | 0.0089876 | 0.033523 | -0.026608 | 0.01379 | -0.019489 | 0.001048 | 0.015142 | 0.000747 | 0.12538 | 0.1011 | 0.31595 | -0.012689 | 0.023941 | 0.073618 | -0.074666 | 0.015831 | 0.18311 | -0.010564 | -0.25115 | 122.3201 | 0.001786 | 122.3338 | 122.3335 | 0.013436 | -0.022501 | 0.19236 | 122.0816 | -0.10776 | 122.3567 | 122.2581 | 0.17648 | 0.059519 | -0.13416 | 122.4581 | 122.4339 | 122.6487 | 122.3479 | -0.13628 | 122.3486 | 122.5159 | 122.3222 | 122.4064 | -0.37474
3703.6094 | 122.493 | -122.3328 | 0.12817 | 1.4211e-13 | -0.018115 | -0.013718 | -0.044957 | -0.041925 | -0.012779 | -0.0084697 | 0.0089876 | 0.033737 | -0.026608 | 0.013577 | -0.019489 | 0.010204 | 0.019721 | -0.003831 | 0.12538 | 0.10567 | 0.32053 | 0.010206 | 0.023941 | 0.078197 | -0.06093 | 0.020409 | 0.18311 | -0.070086 | -0.25115 | 122.343 | -0.002792 | 122.343 | 122.3289 | -0.014037 | -0.0225 | 0.19236 | 122.0816 | -0.10777 | 122.3567 | 122.2718 | 0.19022 | 0.054941 | -0.19826 | 122.4581 | 122.4384 | 122.6533 | 122.3525 | -0.11797 | 122.3532 | 122.5159 | 122.2627 | 122.411 | -0.37932
3705.3906 | 122.5571 | -122.3694 | 0.10529 | 1.4211e-13 | -0.018115 | -0.013718 | -0.044957 | -0.041925 | -0.012779 | -0.00083919 | 0.0089876 | 0.033523 | -0.026394 | 0.013577 | -0.019489 | 0.005626 | 0.0243 | -0.008409 | 0.12538 | 0.096516 | 0.31595 | 0.001048 | 0.023941 | 0.078197 | -0.070087 | 0.015831 | 0.18311 | 0.044379 | -0.26488 | 122.3704 | 0.020096 | 122.375 | 122.361 | -0.009457 | -0.00877 | 0.21067 | 122.1045 | -0.089455 | 122.3933 | 122.2993 | 0.1948 | 0.077829 | -0.060907 | 122.4948 | 122.4659 | 122.6853 | 122.3937 | -0.10424 | 122.3852 | 122.5525 | 122.4138 | 122.4476 | -0.37017
3707.125 | 122.5342 | -122.3602 | 0.10986 | 1.4211e-13 | -0.018115 | -0.014146 | -0.044957 | -0.041925 | -0.012352 | -0.0084697 | 0.0089876 | 0.033523 | -0.026394 | 0.01379 | -0.019489 | -0.003531 | 0.019721 | 0.000747 | 0.12538 | 0.1011 | 0.31595 | -0.00811 | 0.023941 | 0.078197 | -0.070087 | 0.011252 | 0.17854 | -0.010564 | -0.25115 | 122.3521 | 0.015519 | 122.3567 | 122.361 | 0.008857 | -0.008768 | 0.20609 | 122.1091 | -0.098611 | 122.3842 | 122.2901 | 0.18106 | 0.068673 | -0.12043 | 122.4856 | 122.4613 | 122.6762 | 122.38 | -0.11797 | 122.3715 | 122.5388 | 122.3497 | 122.4384 | -0.36101
3708.9375 | 122.6074 | -122.3236 | 0.091553 | 1.4211e-13 | -0.018329 | -0.013718 | -0.045384 | -0.042352 | -0.012779 | -0.0084697 | 0.008774 | 0.033309 | -0.026821 | 0.01379 | -0.019276 | 0.001048 | 0.019721 | -0.003831 | 0.12538 | 0.1011 | 0.32053 | -0.00811 | 0.02852 | 0.082776 | -0.074666 | 0.015831 | 0.18311 | -0.05635 | -0.25572 | 122.3155 | 0.033829 | 122.3247 | 122.3198 | 0.004279 | 0.009542 | 0.22898 | 122.0679 | -0.075722 | 122.3521 | 122.2489 | 0.18106 | 0.091562 | -0.1479 | 122.449 | 122.4247 | 122.6441 | 122.3433 | -0.099663 | 122.3394 | 122.5067 | 122.2673 | 122.4064 | -0.34728
3710.6719 | 122.5021 | -122.374 | 0.1236 | 1.4211e-13 | -0.018756 | -0.013718 | -0.045384 | -0.041925 | -0.012779 | 0.0067908 | 0.0089876 | 0.033309 | -0.026608 | 0.014004 | -0.019276 | 0.001048 | 0.0243 | -0.003831 | 0.12538 | 0.1011 | 0.31137 | -0.031005 | 0.019362 | 0.078197 | -0.074666 | 0.020409 | 0.17396 | 0.003172 | -0.25572 | 122.343 | 0.001786 | 122.375 | 122.3701 | 0.027174 | -0.022501 | 0.18778 | 122.1182 | -0.10319 | 122.3933 | 122.2993 | 0.18106 | 0.050362 | -0.12042 | 122.4993 | 122.4751 | 122.6853 | 122.3983 | -0.1546 | 122.3944 | 122.5479 | 122.3771 | 122.4522 | -0.37932
3712.4531 | 122.6303 | -122.3145 | 0.086975 | 1.4211e-13 | -0.018115 | -0.013505 | -0.04517 | -0.042352 | -0.012779 | -0.0084697 | 0.0089876 | 0.033523 | -0.027035 | 0.013577 | -0.019917 | 0.005626 | 0.019721 | -0.003831 | 0.1208 | 0.096516 | 0.31137 | 0.001048 | 0.023941 | 0.078197 | -0.070087 | 0.015831 | 0.18311 | -0.033457 | -0.25115 | 122.3155 | 0.033829 | 122.3201 | 122.3106 | -0.004879 | 0.009541 | 0.2244 | 122.0633 | -0.071144 | 122.3384 | 122.2444 | 0.18106 | 0.09614 | -0.12043 | 122.4353 | 122.411 | 122.6258 | 122.3342 | -0.085927 | 122.3303 | 122.4976 | 122.281 | 122.3927 | -0.33812
3714.1719 | 122.5204 | -122.3557 | 0.11902 | 1.4211e-13 | -0.017902 | -0.013718 | -0.04517 | -0.041925 | -0.012352 | -0.00083919 | 0.0085604 | 0.033523 | -0.026394 | 0.013363 | -0.019489 | 0.005626 | 0.0243 | 0.000747 | 0.12538 | 0.096516 | 0.32053 | -0.012689 | 0.019362 | 0.073618 | -0.065509 | 0.020409 | 0.18311 | 0.003172 | -0.24657 | 122.343 | 0.006363 | 122.3613 | 122.3564 | 0.013436 | -0.022503 | 0.20151 | 122.1091 | -0.09861 | 122.375 | 122.2901 | 0.18106 | 0.064096 | -0.11585 | 122.481 | 122.4522 | 122.6762 | 122.38 | -0.13171 | 122.3761 | 122.5388 | 122.3588 | 122.4293 | -0.36559
3715.9688 | 122.6395 | -122.3053 | 0.086975 | 1.4211e-13 | -0.018115 | -0.013718 | -0.04517 | -0.042139 | -0.012565 | -0.00083919 | 0.008774 | 0.033523 | -0.026608 | 0.013363 | -0.019276 | 0.005626 | 0.0243 | -0.003831 | 0.1208 | 0.1011 | 0.32053 | -0.031005 | 0.023941 | 0.078197 | -0.070087 | 0.015831 | 0.18769 | 0.016908 | -0.24657 | 122.2743 | 0.033829 | 122.3109 | 122.3015 | 0.027174 | 0.01412 | 0.23356 | 122.0587 | -0.071144 | 122.3292 | 122.2352 | 0.17648 | 0.10072 | -0.070067 | 122.4261 | 122.4064 | 122.6258 | 122.3296 | -0.11798 | 122.3211 | 122.493 | 122.3222 | 122.3835 | -0.33354
3717.7656 | 122.4747 | -122.3831 | 0.13733 | 1.4211e-13 | -0.018115 | -0.013718 | -0.044957 | -0.041925 | -0.012565 | -0.00083919 | 0.0089876 | 0.033523 | -0.026608 | 0.01379 | -0.019276 | 0.001048 | 0.015142 | -0.008409 | 0.11622 | 0.1011 | 0.31595 | -0.00811 | 0.023941 | 0.078197 | -0.070087 | 0.015831 | 0.17854 | -0.028878 | -0.24657 | 122.375 | -0.021104 | 122.3842 | 122.3747 | -0.000299 | -0.036234 | 0.17862 | 122.1366 | -0.1215 | 122.4071 | 122.313 | 0.17648 | 0.041207 | -0.16621 | 122.4993 | 122.4842 | 122.6991 | 122.3983 | -0.14544 | 122.3989 | 122.5617 | 122.3542 | 122.4613 | -0.3839
3719.5 | 122.5525 | -122.3785 | 0.11444 | 1.4211e-13 | -0.018115 | -0.013505 | -0.04517 | -0.041925 | -0.013206 | -0.00083919 | 0.0089876 | 0.03395 | -0.026394 | 0.01379 | -0.019489 | 0.001048 | 0.019721 | -0.008409 | 0.12538 | 0.1011 | 0.32053 | 0.005627 | 0.023941 | 0.078197 | -0.079245 | 0.015831 | 0.18769 | -0.028878 | -0.25572 | 122.3842 | 0.010941 | 122.3796 | 122.3701 | -0.014036 | -0.013346 | 0.20609 | 122.1228 | -0.09861 | 122.4025 | 122.2993 | 0.17648 | 0.073252 | -0.14332 | 122.5039 | 122.4796 | 122.6991 | 122.3983 | -0.10881 | 122.3944 | 122.5662 | 122.3497 | 122.4567 | -0.37017
3721.2969 | 122.5571 | -122.3831 | 0.13275 | 1.4211e-13 | -0.017902 | -0.013718 | -0.045384 | -0.042139 | -0.012779 | -0.0084697 | 0.008774 | 0.033737 | -0.026608 | 0.013577 | -0.019489 | 0.005626 | 0.015142 | -0.003831 | 0.12538 | 0.096516 | 0.31137 | -0.021847 | 0.023941 | 0.082776 | -0.074666 | 0.020409 | 0.19685 | -0.079243 | -0.25115 | 122.3613 | -0.007369 | 122.3887 | 122.3793 | 0.018016 | -0.036235 | 0.17862 | 122.132 | -0.11234 | 122.4071 | 122.3085 | 0.17648 | 0.0641 | -0.21199 | 122.5085 | 122.4796 | 122.6945 | 122.3983 | -0.1546 | 122.4035 | 122.58 | 122.3039 | 122.4659 | -0.3839
3723.1094 | 122.5754 | -122.3694 | 0.11902 | 1.4211e-13 | -0.018329 | -0.013718 | -0.04517 | -0.041711 | -0.012779 | 0.0067908 | 0.0092014 | 0.033737 | -0.026821 | 0.01379 | -0.019276 | 0.005626 | 0.019721 | -0.003831 | 0.12538 | 0.096516 | 0.31137 | 0.019363 | 0.023941 | 0.073618 | -0.070087 | 0.020409 | 0.17854 | -0.019721 | -0.24657 | 122.3887 | 0.006363 | 122.375 | 122.3656 | -0.023194 | -0.022503 | 0.19235 | 122.1228 | -0.09861 | 122.3933 | 122.2993 | 0.17648 | 0.059517 | -0.13874 | 122.4948 | 122.4659 | 122.6808 | 122.3891 | -0.099656 | 122.3898 | 122.5479 | 122.3497 | 122.443 | -0.36559
3727.5781 | 122.6624 | -122.3602 | 0.064087 | 1.4211e-13 | -0.018115 | -0.013932 | -0.044743 | -0.042139 | -0.012779 | -0.00083919 | 0.0085604 | 0.033523 | -0.026608 | 0.013577 | -0.019276 | 0.005626 | 0.0243 | 0.000747 | 0.1208 | 0.091937 | 0.31137 | 0.005627 | 0.014784 | 0.078197 | -0.070087 | 0.015831 | 0.18311 | -0.051771 | -0.25115 | 122.3659 | 0.056717 | 122.3659 | 122.361 | -0.00488 | 0.02785 | 0.24729 | 122.1091 | -0.048256 | 122.375 | 122.2901 | 0.18106 | 0.11903 | -0.11586 | 122.481 | 122.4522 | 122.6716 | 122.3845 | -0.05846 | 122.3761 | 122.5433 | 122.3085 | 122.4384 | -0.31523
3729.625 | 122.612 | -122.3694 | 0.11902 | 1.4211e-13 | -0.018329 | -0.013505 | -0.04517 | -0.042139 | -0.012779 | -0.00083919 | 0.008774 | 0.033523 | -0.027035 | 0.01379 | -0.019489 | 0.005626 | 0.0243 | 0.000747 | 0.12996 | 0.10567 | 0.31595 | -0.003531 | 0.019362 | 0.078197 | -0.065509 | 0.020409 | 0.18769 | -0.074664 | -0.24199 | 122.3659 | 0.010941 | 122.375 | 122.3701 | 0.004278 | -0.013345 | 0.19693 | 122.1274 | -0.09861 | 122.3887 | 122.3039 | 0.17648 | 0.068674 | -0.19368 | 122.4993 | 122.4751 | 122.6853 | 122.3937 | -0.12255 | 122.3898 | 122.5571 | 122.2947 | 122.4476 | -0.36101
3732.25 | 122.6761 | -122.3877 | 0.09613 | 1.4211e-13 | -0.018329 | -0.013718 | -0.045384 | -0.042139 | -0.012779 | -0.0084697 | 0.0089876 | 0.033737 | -0.026608 | 0.014004 | -0.019276 | 0.005626 | 0.019721 | -0.003831 | 0.12538 | 0.087359 | 0.31137 | 0.005627 | 0.019362 | 0.078197 | -0.065509 | 0.011252 | 0.18311 | -0.015142 | -0.25115 | 122.3933 | 0.029252 | 122.3933 | 122.3839 | -0.009458 | -0.008771 | 0.21524 | 122.1365 | -0.084878 | 122.4071 | 122.3222 | 0.18564 | 0.086985 | -0.11127 | 122.5131 | 122.4751 | 122.6991 | 122.4074 | -0.090503 | 122.3989 | 122.5708 | 122.3726 | 122.4659 | -0.34728
3734.1406 | 122.5113 | -122.4197 | 0.1236 | 1.4211e-13 | -0.017902 | -0.013505 | -0.04517 | -0.041925 | -0.012565 | -0.0084697 | 0.0085604 | 0.033523 | -0.026608 | 0.01379 | -0.019276 | 0.010204 | 0.015142 | -0.008409 | 0.12538 | 0.10567 | 0.31595 | 0.001048 | 0.023941 | 0.082776 | -0.070087 | 0.011252 | 0.18769 | -0.042614 | -0.25115 | 122.4208 | 0.001786 | 122.4299 | 122.4113 | -0.009457 | -0.017922 | 0.19236 | 122.1686 | -0.11234 | 122.4437 | 122.3497 | 0.18106 | 0.064097 | -0.16621 | 122.5451 | 122.5254 | 122.7357 | 122.4349 | -0.12255 | 122.431 | 122.6074 | 122.3771 | 122.5025 | -0.37474
3735.9375 | 122.5433 | -122.4289 | 0.1236 | 1.4211e-13 | -0.018115 | -0.013291 | -0.044957 | -0.041711 | -0.012779 | -0.0084697 | 0.0089876 | 0.033096 | -0.027035 | 0.014004 | -0.019489 | 0.001048 | 0.019721 | 0.000747 | 0.1208 | 0.096516 | 0.31595 | -0.003531 | 0.023941 | 0.078197 | -0.074666 | 0.015831 | 0.18769 | -0.033457 | -0.24657 | 122.4254 | -0.002792 | 122.4299 | 122.4296 | 0.004278 | -0.02708 | 0.19236 | 122.1823 | -0.10776 | 122.4528 | 122.3542 | 0.1719 | 0.064097 | -0.15705 | 122.5497 | 122.5254 | 122.7448 | 122.4486 | -0.12713 | 122.4447 | 122.6166 | 122.3954 | 122.5071 | -0.37016
3737.7656 | 122.6257 | -122.3923 | 0.10071 | 1.4211e-13 | -0.018115 | -0.013505 | -0.044743 | -0.042566 | -0.012993 | 0.0067908 | 0.008774 | 0.033309 | -0.026608 | 0.013363 | -0.019489 | 0.001048 | 0.0243 | -0.003831 | 0.1208 | 0.091937 | 0.31595 | 0.010206 | 0.023941 | 0.078197 | -0.070087 | 0.006674 | 0.18311 | -0.028878 | -0.25115 | 122.4025 | 0.020096 | 122.3933 | 122.3884 | -0.014037 | -0.008771 | 0.21524 | 122.1411 | -0.094034 | 122.4162 | 122.3222 | 0.18106 | 0.082407 | -0.12959 | 122.5131 | 122.4842 | 122.7082 | 122.4166 | -0.090502 | 122.3989 | 122.5754 | 122.3634 | 122.4705 | -0.35185
3739.6094 | 122.5479 | -122.4243 | 0.11902 | 1.4211e-13 | -0.018115 | -0.013505 | -0.044957 | -0.042352 | -0.012993 | -0.0161 | 0.0092014 | 0.033309 | -0.026608 | 0.013577 | -0.019703 | 0.010204 | 0.015142 | -0.003831 | 0.12996 | 0.096516 | 0.31137 | -0.00811 | 0.019362 | 0.073618 | -0.070087 | 0.020409 | 0.18311 | -0.05635 | -0.25115 | 122.4162 | 0.010941 | 122.4345 | 122.4205 | 0.004279 | -0.022503 | 0.19235 | 122.1732 | -0.09861 | 122.4437 | 122.3542 | 0.18106 | 0.064096 | -0.17537 | 122.5543 | 122.5208 | 122.7357 | 122.4395 | -0.12713 | 122.4447 | 122.6074 | 122.368 | 122.4979 | -0.37016
3741.4062 | 122.6303 | -122.3877 | 0.091553 | 1.4211e-13 | -0.017902 | -0.013718 | -0.04517 | -0.042352 | -0.012993 | -0.0084697 | 0.008774 | 0.033523 | -0.026821 | 0.014004 | -0.019062 | 0.010204 | 0.0243 | -0.003831 | 0.1208 | 0.096516 | 0.32053 | -0.00811 | 0.019362 | 0.087354 | -0.065509 | 0.020409 | 0.18311 | -0.0884 | -0.25572 | 122.3796 | 0.029251 | 122.3979 | 122.3839 | 0.004279 | 0.004963 | 0.22898 | 122.132 | -0.071144 | 122.4071 | 122.3222 | 0.19022 | 0.091562 | -0.17995 | 122.5085 | 122.4842 | 122.7082 | 122.412 | -0.099663 | 122.4081 | 122.5708 | 122.2993 | 122.475 | -0.34728
3743.2812 | 122.6761 | -122.3648 | 0.10986 | 1.4211e-13 | -0.018115 | -0.014146 | -0.044957 | -0.042352 | -0.012565 | 0.0067908 | 0.008774 | 0.033523 | -0.027035 | 0.013363 | -0.019489 | 0.010204 | 0.0243 | -0.003831 | 0.12538 | 0.1011 | 0.32053 | 0.005627 | 0.02852 | 0.073618 | -0.070087 | 0.011252 | 0.18769 | -0.033457 | -0.24657 | 122.3704 | 0.015519 | 122.375 | 122.361 | -0.009458 | -0.008768 | 0.21067 | 122.1182 | -0.098611 | 122.3933 | 122.2947 | 0.17648 | 0.07783 | -0.14332 | 122.4902 | 122.4659 | 122.6853 | 122.3891 | -0.10424 | 122.3761 | 122.5525 | 122.3314 | 122.4384 | -0.35643
3745.0625 | 122.6807 | -122.3831 | 0.064087 | 1.4211e-13 | -0.018115 | -0.013932 | -0.044957 | -0.042352 | -0.012352 | -0.00083919 | 0.0092014 | 0.033309 | -0.026394 | 0.013577 | -0.019489 | 0.005626 | 0.019721 | -0.003831 | 0.11165 | 0.10567 | 0.31595 | 0.005627 | 0.023941 | 0.073618 | -0.070087 | 0.020409 | 0.18311 | -0.065507 | -0.24657 | 122.3887 | 0.04756 | 122.3887 | 122.3793 | -0.009458 | 0.041587 | 0.25187 | 122.1366 | -0.043678 | 122.4071 | 122.313 | 0.17648 | 0.11903 | -0.12959 | 122.4948 | 122.4888 | 122.6991 | 122.4028 | -0.05846 | 122.4035 | 122.5662 | 122.3176 | 122.4567 | -0.31065
3746.8438 | 122.6028 | -122.4197 | 0.13275 | 1.4211e-13 | -0.017688 | -0.013291 | -0.044743 | -0.042139 | -0.012779 | 0.0067908 | 0.0089876 | 0.033309 | -0.026821 | 0.013577 | -0.019276 | 0.005626 | 0.019721 | -0.012988 | 0.1208 | 0.096516 | 0.31137 | 0.001048 | 0.019362 | 0.078197 | -0.079245 | 0.015831 | 0.18311 | -0.033457 | -0.24199 | 122.4208 | -0.011947 | 122.4254 | 122.4068 | -0.014036 | -0.036235 | 0.17862 | 122.1778 | -0.11692 | 122.4391 | 122.3405 | 0.16274 | 0.050364 | -0.16621 | 122.5405 | 122.5163 | 122.7311 | 122.4395 | -0.1317 | 122.4356 | 122.6029 | 122.3863 | 122.4979 | -0.37474
3748.7188 | 122.6624 | -122.4197 | 0.073242 | 1.4211e-13 | -0.018115 | -0.013505 | -0.044957 | -0.042139 | -0.012779 | -0.0084697 | 0.0089876 | 0.033309 | -0.026821 | 0.013577 | -0.019489 | 0.010204 | 0.019721 | -0.003831 | 0.12996 | 0.1011 | 0.31137 | -0.026426 | 0.023941 | 0.078197 | -0.065509 | 0.015831 | 0.18311 | -0.028878 | -0.25115 | 122.3933 | 0.056718 | 122.4299 | 122.4159 | 0.022595 | 0.027853 | 0.23813 | 122.1686 | -0.057411 | 122.4437 | 122.3542 | 0.18564 | 0.10987 | -0.10212 | 122.5497 | 122.5208 | 122.7311 | 122.4395 | -0.099668 | 122.4356 | 122.6029 | 122.3909 | 122.4979 | -0.32439
3750.5469 | 122.7036 | -122.3969 | 0.064087 | 1.4211e-13 | -0.017902 | -0.013932 | -0.044743 | -0.041925 | -0.012779 | -0.00083919 | 0.0092014 | 0.033309 | -0.026608 | 0.013577 | -0.019489 | 0.005626 | 0.019721 | -0.003831 | 0.12538 | 0.1011 | 0.32511 | 0.001048 | 0.019362 | 0.078197 | -0.070087 | 0.015831 | 0.18769 | -0.070086 | -0.25572 | 122.3979 | 0.061295 | 122.4025 | 122.393 | -0.004879 | 0.037008 | 0.26102 | 122.1411 | -0.048256 | 122.4162 | 122.3268 | 0.18564 | 0.12361 | -0.13417 | 122.5222 | 122.4979 | 122.722 | 122.4166 | -0.063039 | 122.4127 | 122.5845 | 122.3268 | 122.475 | -0.31981
3752.2969 | 122.6852 | -122.4014 | 0.082397 | 1.4211e-13 | -0.018115 | -0.013718 | -0.04517 | -0.041925 | -0.012779 | -0.00083919 | 0.0089876 | 0.033309 | -0.026821 | 0.01379 | -0.019276 | 0.005626 | 0.028878 | 0.000747 | 0.11622 | 0.096516 | 0.31595 | -0.017268 | 0.019362 | 0.078197 | -0.065509 | 0.011252 | 0.19227 | -0.019721 | -0.2603 | 122.3842 | 0.033828 | 122.4071 | 122.4022 | 0.018015 | 0.014119 | 0.23356 | 122.1411 | -0.071145 | 122.4208 | 122.3359 | 0.19479 | 0.10988 | -0.10212 | 122.5177 | 122.4979 | 122.7174 | 122.4303 | -0.099665 | 122.4127 | 122.5937 | 122.3817 | 122.4796 | -0.3427
3754.0938 | 122.5708 | -122.4564 | 0.11902 | 1.4211e-13 | -0.017902 | -0.013932 | -0.04517 | -0.042566 | -0.012565 | -0.00083919 | 0.008774 | 0.033096 | -0.026608 | 0.014004 | -0.019489 | 0.001048 | 0.019721 | -0.003831 | 0.1208 | 0.1011 | 0.31137 | -0.017268 | 0.023941 | 0.078197 | -0.070087 | 0.015831 | 0.18311 | -0.047193 | -0.24657 | 122.4391 | 0.001785 | 122.4574 | 122.4525 | 0.013437 | -0.017924 | 0.19235 | 122.2098 | -0.10319 | 122.4803 | 122.3863 | 0.17648 | 0.064096 | -0.16621 | 122.5772 | 122.5575 | 122.7677 | 122.4761 | -0.13629 | 122.4722 | 122.6395 | 122.4092 | 122.5346 | -0.36559
3755.9219 | 122.6624 | -122.4197 | 0.091553 | 1.4211e-13 | -0.017902 | -0.013932 | -0.045384 | -0.042139 | -0.012779 | -0.00083919 | 0.0092014 | 0.033523 | -0.027035 | 0.01379 | -0.019276 | 0.005626 | 0.0243 | -0.003831 | 0.1208 | 0.1011 | 0.31137 | 0.001048 | 0.023941 | 0.078197 | -0.070087 | 0.011252 | 0.18311 | 0.016908 | -0.25115 | 122.4208 | 0.029251 | 122.4254 | 122.4159 | -0.004879 | 0.009542 | 0.21982 | 122.1686 | -0.080301 | 122.4437 | 122.3497 | 0.18106 | 0.091562 | -0.074645 | 122.5405 | 122.5208 | 122.7311 | 122.444 | -0.090505 | 122.431 | 122.6029 | 122.4366 | 122.4979 | -0.3427
3758.6094 | 122.7402 | -122.406 | 0.091553 | 1.4211e-13 | -0.017902 | -0.013932 | -0.04517 | -0.042139 | -0.012779 | 0.0067908 | 0.0092014 | 0.033523 | -0.026821 | 0.014218 | -0.019489 | 0.001048 | 0.0243 | 0.000747 | 0.12538 | 0.096516 | 0.31595 | 0.001048 | 0.02852 | 0.078197 | -0.070087 | 0.015831 | 0.18769 | 0.012329 | -0.25115 | 122.4071 | 0.033829 | 122.4071 | 122.4068 | -0.000301 | 0.004963 | 0.2244 | 122.1549 | -0.075722 | 122.4345 | 122.3359 | 0.18106 | 0.09614 | -0.079224 | 122.5314 | 122.5025 | 122.722 | 122.4303 | -0.090505 | 122.4218 | 122.5937 | 122.4183 | 122.4842 | -0.3427
3761 | 122.6898 | -122.406 | 0.086975 | 1.4211e-13 | -0.018329 | -0.013718 | -0.044957 | -0.042139 | -0.012779 | -0.0084697 | 0.0089876 | 0.033309 | -0.027035 | 0.013363 | -0.019276 | 0.001048 | 0.0243 | -0.003831 | 0.12538 | 0.096516 | 0.31595 | -0.012689 | 0.02852 | 0.078197 | -0.070087 | 0.020409 | 0.18311 | 0.021486 | -0.25572 | 122.3933 | 0.038407 | 122.4071 | 122.4022 | 0.008858 | 0.009541 | 0.22898 | 122.1503 | -0.066566 | 122.4345 | 122.3359 | 0.18564 | 0.09614 | -0.065489 | 122.5314 | 122.5025 | 122.722 | 122.4303 | -0.099664 | 122.4264 | 122.5891 | 122.4275 | 122.4842 | -0.3427
3762.8125 | 122.612 | -122.4472 | 0.12817 | 1.4211e-13 | -0.018329 | -0.013718 | -0.04517 | -0.042352 | -0.012565 | -0.00083919 | 0.0092014 | 0.033309 | -0.026821 | 0.01379 | -0.019489 | 0.001048 | 0.019721 | -0.003831 | 0.12538 | 0.1011 | 0.31137 | -0.00811 | 0.02852 | 0.078197 | -0.070087 | 0.015831 | 0.18769 | -0.019721 | -0.26488 | 122.4391 | -0.002792 | 122.4483 | 122.4434 | 0.004279 | -0.027079 | 0.1832 | 122.1823 | -0.11234 | 122.4757 | 122.3771 | 0.1948 | 0.059519 | -0.14789 | 122.5726 | 122.5483 | 122.7586 | 122.4669 | -0.13628 | 122.463 | 122.6349 | 122.4275 | 122.5254 | -0.39306
3764.75 | 122.6761 | -122.4335 | 0.09613 | 1.4211e-13 | -0.018115 | -0.013932 | -0.04517 | -0.041925 | -0.012993 | -0.00083919 | 0.0089876 | 0.033096 | -0.026608 | 0.01379 | -0.019276 | -0.003531 | 0.0243 | -0.008409 | 0.12538 | 0.096516 | 0.31595 | 0.001048 | 0.023941 | 0.078197 | -0.074666 | 0.015831 | 0.18769 | -0.079243 | -0.25572 | 122.4345 | 0.029252 | 122.4299 | 122.4251 | -0.009457 | 0.000386 | 0.21982 | 122.1777 | -0.080299 | 122.4574 | 122.3588 | 0.18106 | 0.091563 | -0.17537 | 122.5589 | 122.53 | 122.7494 | 122.4578 | -0.095082 | 122.4493 | 122.6212 | 122.3542 | 122.5117 | -0.35185
3766.5469 | 122.6395 | -122.4335 | 0.10071 | 1.4211e-13 | -0.018329 | -0.013505 | -0.044957 | -0.042139 | -0.012993 | -0.0084697 | 0.009415 | 0.033309 | -0.027035 | 0.013577 | -0.019703 | 0.001048 | 0.0243 | -0.003831 | 0.1208 | 0.1011 | 0.32053 | 0.014784 | 0.023941 | 0.078197 | -0.070087 | 0.011252 | 0.18311 | -0.038035 | -0.25115 | 122.4483 | 0.020096 | 122.4345 | 122.4296 | -0.018615 | 0.000387 | 0.21982 | 122.1823 | -0.089456 | 122.4574 | 122.3634 | 0.18106 | 0.082407 | -0.13874 | 122.5543 | 122.5346 | 122.754 | 122.4578 | -0.085924 | 122.4447 | 122.6166 | 122.3954 | 122.5117 | -0.35185
3768.5 | 122.6486 | -122.4426 | 0.10986 | 1.4211e-13 | -0.018115 | -0.013718 | -0.045384 | -0.041925 | -0.012565 | -0.0084697 | 0.0089876 | 0.033096 | -0.026394 | 0.014004 | -0.019489 | 0.001048 | 0.010564 | -0.008409 | 0.1208 | 0.096516 | 0.31137 | 0.010206 | 0.023941 | 0.082776 | -0.065509 | 0.024988 | 0.18769 | -0.079243 | -0.25115 | 122.4528 | 0.010941 | 122.4437 | 122.4342 | -0.018615 | -0.013347 | 0.20151 | 122.1915 | -0.084875 | 122.4666 | 122.3771 | 0.18564 | 0.07783 | -0.18911 | 122.5634 | 122.5391 | 122.754 | 122.4532 | -0.099657 | 122.4676 | 122.6303 | 122.3634 | 122.5254 | -0.36101
3771.0312 | 122.7356 | -122.4518 | 0.09613 | 1.4211e-13 | -0.018115 | -0.013718 | -0.044957 | -0.041925 | -0.012993 | -0.00083919 | 0.0089876 | 0.033737 | -0.026821 | 0.013577 | -0.019703 | 0.005626 | 0.015142 | -0.003831 | 0.1208 | 0.096516 | 0.31595 | -0.021847 | 0.023941 | 0.082776 | -0.065509 | 0.015831 | 0.18769 | 0.012329 | -0.25115 | 122.4299 | 0.024674 | 122.4574 | 122.448 | 0.018016 | 0.000386 | 0.21982 | 122.2006 | -0.080299 | 122.4757 | 122.3863 | 0.18564 | 0.091563 | -0.083801 | 122.5726 | 122.5483 | 122.7677 | 122.4669 | -0.11798 | 122.4676 | 122.6395 | 122.4641 | 122.5346 | -0.34728
3773.7031 | 122.6349 | -122.4701 | 0.11444 | 1.4211e-13 | -0.018543 | -0.013505 | -0.04517 | -0.041925 | -0.012993 | -0.00083919 | 0.009415 | 0.033737 | -0.026394 | 0.013577 | -0.019489 | 0.001048 | 0.019721 | -0.003831 | 0.12538 | 0.1011 | 0.32053 | -0.026426 | 0.023941 | 0.082776 | -0.070087 | 0.015831 | 0.18311 | 0.007751 | -0.2603 | 122.4437 | 0.010941 | 122.4711 | 122.4663 | 0.022595 | -0.013346 | 0.20609 | 122.2098 | -0.09861 | 122.494 | 122.4 | 0.19022 | 0.068674 | -0.10669 | 122.5955 | 122.5712 | 122.7906 | 122.4898 | -0.14087 | 122.4859 | 122.6532 | 122.4778 | 122.5529 | -0.37474
3776.3281 | 122.7493 | -122.4426 | 0.086975 | 1.4211e-13 | -0.017902 | -0.013932 | -0.044957 | -0.041925 | -0.012779 | -0.0161 | 0.009415 | 0.033523 | -0.026608 | 0.01379 | -0.019703 | 0.010204 | 0.0243 | -0.003831 | 0.12538 | 0.091937 | 0.31595 | -0.017268 | 0.023941 | 0.078197 | -0.070087 | 0.011252 | 0.17854 | 0.021486 | -0.25115 | 122.4254 | 0.038407 | 122.4528 | 122.4388 | 0.013437 | 0.004962 | 0.22898 | 122.1915 | -0.075723 | 122.4666 | 122.3725 | 0.18106 | 0.091561 | -0.065489 | 122.568 | 122.5346 | 122.7586 | 122.4669 | -0.10424 | 122.4539 | 122.6212 | 122.4641 | 122.5208 | -0.33812
3778.7656 | 122.7036 | -122.4564 | 0.10071 | 1.4211e-13 | -0.017688 | -0.013718 | -0.044957 | -0.042352 | -0.012565 | 0.0067908 | 0.0096286 | 0.033309 | -0.027035 | 0.014004 | -0.019489 | 0.001048 | 0.028878 | 0.000747 | 0.1208 | 0.1011 | 0.32053 | -0.003531 | 0.023941 | 0.078197 | -0.065509 | 0.015831 | 0.18311 | 0.026065 | -0.25572 | 122.4528 | 0.020096 | 122.4574 | 122.4571 | 0.004278 | 0.000387 | 0.21982 | 122.2006 | -0.084877 | 122.4803 | 122.3909 | 0.19022 | 0.082407 | -0.074643 | 122.5772 | 122.5575 | 122.7769 | 122.4852 | -0.10424 | 122.4722 | 122.6395 | 122.4824 | 122.5346 | -0.35643
3781.2188 | 122.7585 | -122.4518 | 0.073242 | 1.4211e-13 | -0.018115 | -0.013932 | -0.044529 | -0.042352 | -0.012993 | -0.00083919 | 0.0089876 | 0.033309 | -0.027035 | 0.014004 | -0.019276 | 0.001048 | 0.0243 | -0.008409 | 0.12538 | 0.1011 | 0.32511 | -0.017268 | 0.023941 | 0.078197 | -0.070087 | 0.020409 | 0.18311 | 0.026065 | -0.25115 | 122.4345 | 0.05214 | 122.4528 | 122.4434 | 0.008859 | 0.027853 | 0.25187 | 122.2006 | -0.052833 | 122.4757 | 122.3817 | 0.18106 | 0.10987 | -0.047177 | 122.5772 | 122.5529 | 122.7769 | 122.4761 | -0.09051 | 122.4722 | 122.6349 | 122.4778 | 122.53 | -0.32439
3783.125 | 122.644 | -122.4838 | 0.1236 | 1.4211e-13 | -0.017902 | -0.013932 | -0.045384 | -0.041925 | -0.012565 | -0.00083919 | 0.008774 | 0.033309 | -0.027035 | 0.014218 | -0.019276 | 0.001048 | 0.019721 | 0.000747 | 0.12538 | 0.096516 | 0.32053 | -0.044742 | 0.023941 | 0.078197 | -0.074666 | 0.015831 | 0.18311 | -0.028878 | -0.25115 | 122.4391 | 0.001786 | 122.4849 | 122.4846 | 0.045489 | -0.02708 | 0.19694 | 122.2327 | -0.10776 | 122.5078 | 122.4092 | 0.17648 | 0.059519 | -0.15247 | 122.6092 | 122.5803 | 122.8044 | 122.5035 | -0.16834 | 122.4997 | 122.6669 | 122.4549 | 122.562 | -0.37474
3784.9062 | 122.7356 | -122.4655 | 0.10071 | 1.4211e-13 | -0.018329 | -0.013932 | -0.044957 | -0.041925 | -0.013206 | -0.00083919 | 0.0089876 | 0.033523 | -0.027249 | 0.013363 | -0.019489 | 0.010204 | 0.019721 | -0.012988 | 0.1208 | 0.096516 | 0.31595 | -0.017268 | 0.023941 | 0.082776 | -0.074666 | 0.015831 | 0.18769 | 0.026065 | -0.24657 | 122.4482 | 0.020096 | 122.4757 | 122.4525 | 0.00428 | -0.004192 | 0.21524 | 122.2189 | -0.084877 | 122.4895 | 122.3908 | 0.1719 | 0.086985 | -0.074643 | 122.5863 | 122.562 | 122.7815 | 122.4852 | -0.11798 | 122.4813 | 122.6532 | 122.4916 | 122.5483 | -0.34728
3787 | 122.6349 | -122.493 | 0.1236 | 1.4211e-13 | -0.017902 | -0.013932 | -0.04517 | -0.042352 | -0.012779 | -0.00083919 | 0.009415 | 0.033523 | -0.026608 | 0.013577 | -0.019276 | 0.005626 | 0.015142 | 0.000747 | 0.12538 | 0.091937 | 0.31137 | -0.021847 | 0.02852 | 0.082776 | -0.070087 | 0.020409 | 0.19227 | 0.016908 | -0.24657 | 122.4711 | 0.001786 | 122.4986 | 122.4937 | 0.022594 | -0.031659 | 0.18778 | 122.2464 | -0.10319 | 122.5215 | 122.4229 | 0.17648 | 0.068676 | -0.10669 | 122.6184 | 122.5849 | 122.8044 | 122.5081 | -0.14544 | 122.5134 | 122.6853 | 122.5099 | 122.5758 | -0.37016
3788.8594 | 122.6807 | -122.4747 | 0.13275 | 1.4211e-13 | -0.017902 | -0.013718 | -0.04517 | -0.041925 | -0.012565 | -0.00083919 | 0.0089876 | 0.033523 | -0.026394 | 0.014004 | -0.019489 | 0.005626 | 0.015142 | 0.000747 | 0.12538 | 0.1011 | 0.32053 | 0.001048 | 0.019362 | 0.087354 | -0.074666 | 0.011252 | 0.18769 | -0.010564 | -0.25115 | 122.4757 | -0.007369 | 122.4803 | 122.4754 | -0.000301 | -0.031656 | 0.18778 | 122.2235 | -0.1215 | 122.494 | 122.4 | 0.17648 | 0.054942 | -0.14331 | 122.6001 | 122.5758 | 122.7952 | 122.4898 | -0.1317 | 122.4859 | 122.6624 | 122.4641 | 122.562 | -0.3839
3790.6406 | 122.6852 | -122.4838 | 0.09613 | 1.4211e-13 | -0.017688 | -0.013932 | -0.044743 | -0.042352 | -0.013206 | -0.00083919 | 0.0092014 | 0.033309 | -0.026821 | 0.01379 | -0.019276 | 0.001048 | 0.015142 | 0.005325 | 0.1208 | 0.096516 | 0.32053 | 0.005627 | 0.02852 | 0.073618 | -0.065509 | 0.020409 | 0.18311 | -0.028878 | -0.25115 | 122.4895 | 0.024674 | 122.4849 | 122.4892 | -0.000302 | 0.000386 | 0.2244 | 122.2327 | -0.075721 | 122.5123 | 122.4183 | 0.18564 | 0.086985 | -0.12501 | 122.6046 | 122.5803 | 122.8044 | 122.499 | -0.090503 | 122.5042 | 122.6669 | 122.4549 | 122.5574 | -0.34728
3792.5469 | 122.7585 | -122.4655 | 0.07782 | 1.4211e-13 | -0.017688 | -0.013932 | -0.04517 | -0.041925 | -0.012993 | -0.0084697 | 0.0092014 | 0.033309 | -0.026608 | 0.014004 | -0.019703 | 0.001048 | 0.033457 | 0.000747 | 0.12538 | 0.11025 | 0.32053 | -0.031005 | 0.02852 | 0.082776 | -0.074666 | 0.015831 | 0.17854 | -0.0243 | -0.25115 | 122.4345 | 0.047562 | 122.4666 | 122.4663 | 0.031752 | 0.032433 | 0.24271 | 122.2144 | -0.061989 | 122.494 | 122.3908 | 0.17648 | 0.10072 | -0.10212 | 122.5909 | 122.5758 | 122.786 | 122.499 | -0.10883 | 122.4813 | 122.6441 | 122.4412 | 122.5483 | -0.32897
3794.2656 | 122.6257 | -122.5159 | 0.11902 | 1.4211e-13 | -0.017902 | -0.013932 | -0.04517 | -0.042352 | -0.012993 | -0.0084697 | 0.0089876 | 0.033523 | -0.027249 | 0.013363 | -0.019276 | 0.001048 | 0.019721 | 0.005325 | 0.11622 | 0.096516 | 0.32053 | 0.010206 | 0.023941 | 0.078197 | -0.070087 | 0.015831 | 0.17854 | 0.030644 | -0.25115 | 122.5261 | -0.002794 | 122.5169 | 122.5212 | -0.004881 | -0.022503 | 0.20151 | 122.2647 | -0.10319 | 122.5398 | 122.4458 | 0.18106 | 0.059517 | -0.088375 | 122.6321 | 122.6124 | 122.8364 | 122.5356 | -0.10881 | 122.5317 | 122.6944 | 122.5465 | 122.5941 | -0.37016
3796.0469 | 122.7493 | -122.4655 | 0.10071 | 1.4211e-13 | -0.017688 | -0.013932 | -0.045384 | -0.042139 | -0.012779 | -0.00083919 | 0.009415 | 0.033523 | -0.026821 | 0.01379 | -0.019276 | 0.005626 | 0.019721 | -0.008409 | 0.1208 | 0.096516 | 0.31595 | -0.021847 | 0.02852 | 0.082776 | -0.065509 | 0.015831 | 0.17854 | 0.021486 | -0.24657 | 122.4437 | 0.020096 | 122.4711 | 122.4571 | 0.013438 | -0.004192 | 0.21524 | 122.2189 | -0.084877 | 122.494 | 122.4 | 0.18106 | 0.077828 | -0.079222 | 122.5863 | 122.562 | 122.7815 | 122.4852 | -0.12255 | 122.4813 | 122.6441 | 122.487 | 122.5483 | -0.34728
3797.7656 | 122.7448 | -122.4609 | 0.091553 | 1.4211e-13 | -0.017688 | -0.013932 | -0.044957 | -0.042352 | -0.012779 | 0.0067908 | 0.009415 | 0.033309 | -0.026821 | 0.014004 | -0.019489 | 0.010204 | 0.015142 | -0.003831 | 0.12538 | 0.1011 | 0.31137 | -0.017268 | 0.023941 | 0.082776 | -0.070087 | 0.011252 | 0.17854 | -0.019721 | -0.24657 | 122.4437 | 0.033829 | 122.4711 | 122.4571 | 0.013437 | 0.009542 | 0.21982 | 122.2144 | -0.080301 | 122.4849 | 122.3909 | 0.17648 | 0.086983 | -0.11127 | 122.5863 | 122.562 | 122.7723 | 122.4761 | -0.10882 | 122.4722 | 122.6395 | 122.4412 | 122.5437 | -0.33812
3799.4844 | 122.7859 | -122.493 | 0.07782 | 1.4211e-13 | -0.017902 | -0.013718 | -0.044957 | -0.042352 | -0.012993 | -0.00083919 | 0.0089876 | 0.033523 | -0.027035 | 0.013577 | -0.019276 | 0.005626 | 0.0243 | -0.003831 | 0.12538 | 0.1011 | 0.32053 | -0.017268 | 0.02852 | 0.082776 | -0.070087 | 0.020409 | 0.18311 | -0.0243 | -0.24657 | 122.4757 | 0.047562 | 122.4986 | 122.4891 | 0.013437 | 0.023275 | 0.24271 | 122.2464 | -0.057411 | 122.5215 | 122.4229 | 0.17648 | 0.10529 | -0.10212 | 122.6184 | 122.5941 | 122.8135 | 122.5173 | -0.095088 | 122.5134 | 122.6761 | 122.4687 | 122.5758 | -0.32439
3801.2344 | 122.6395 | -122.5067 | 0.12817 | 1.4211e-13 | -0.017688 | -0.013505 | -0.045384 | -0.041925 | -0.012993 | -0.00083919 | 0.0089876 | 0.033309 | -0.026821 | 0.014004 | -0.019489 | 0.005626 | 0.0243 | 0.000747 | 0.12538 | 0.1011 | 0.32053 | 0.010206 | 0.023941 | 0.073618 | -0.06093 | 0.015831 | 0.17854 | -0.010564 | -0.24657 | 122.5169 | -0.002792 | 122.5123 | 122.5075 | -0.009459 | -0.027079 | 0.19236 | 122.2601 | -0.11234 | 122.5307 | 122.4458 | 0.18564 | 0.050362 | -0.13874 | 122.6321 | 122.6078 | 122.8272 | 122.531 | -0.11797 | 122.5225 | 122.6852 | 122.4962 | 122.5803 | -0.37474
3802.9375 | 122.7951 | -122.4792 | 0.10529 | 1.4211e-13 | -0.017902 | -0.013718 | -0.04517 | -0.041925 | -0.012993 | -0.00083919 | 0.0092014 | 0.033309 | -0.027249 | 0.014004 | -0.019276 | 0.001048 | 0.015142 | 0.005325 | 0.11622 | 0.1011 | 0.31595 | -0.012689 | 0.023941 | 0.087354 | -0.065509 | 0.015831 | 0.18311 | 0.003172 | -0.25115 | 122.4666 | 0.010939 | 122.4803 | 122.4846 | 0.018014 | -0.004191 | 0.21067 | 122.2281 | -0.089455 | 122.5032 | 122.4137 | 0.18564 | 0.077829 | -0.10211 | 122.5955 | 122.5803 | 122.7952 | 122.4944 | -0.11798 | 122.4951 | 122.6624 | 122.4824 | 122.5666 | -0.35643
3804.7031 | 122.6807 | -122.5296 | 0.12817 | 1.4211e-13 | -0.017902 | -0.013718 | -0.045384 | -0.042139 | -0.012779 | 0.0067908 | 0.0092014 | 0.033309 | -0.027035 | 0.01379 | -0.019276 | 0.001048 | 0.0243 | 0.000747 | 0.1208 | 0.096516 | 0.31595 | 0.005627 | 0.023941 | 0.078197 | -0.070087 | 0.020409 | 0.17854 | 0.003172 | -0.25115 | 122.5352 | -0.00737 | 122.5306 | 122.5303 | -0.00488 | -0.031658 | 0.18778 | 122.2785 | -0.10777 | 122.5535 | 122.4595 | 0.18106 | 0.050362 | -0.125 | 122.6504 | 122.6261 | 122.8456 | 122.5539 | -0.12255 | 122.55 | 122.7081 | 122.5328 | 122.6078 | -0.37932
3806.4062 | 122.8043 | -122.4976 | 0.07782 | 1.4211e-13 | -0.017902 | -0.013932 | -0.044529 | -0.041711 | -0.012779 | -0.0084697 | 0.0089876 | 0.033309 | -0.026821 | 0.014004 | -0.019062 | 0.001048 | 0.019721 | -0.003831 | 0.1208 | 0.096516 | 0.31595 | -0.021847 | 0.023941 | 0.073618 | -0.079245 | 0.011252 | 0.18769 | 0.007751 | -0.25115 | 122.4757 | 0.042984 | 122.4986 | 122.4937 | 0.018016 | 0.018696 | 0.23813 | 122.2464 | -0.066568 | 122.5215 | 122.4183 | 0.1719 | 0.10987 | -0.070069 | 122.6184 | 122.5941 | 122.8135 | 122.5173 | -0.099667 | 122.5088 | 122.6853 | 122.5053 | 122.5712 | -0.32897
3808.2031 | 122.7997 | -122.4564 | 0.082397 | 1.4211e-13 | -0.017902 | -0.013505 | -0.044957 | -0.042139 | -0.012993 | -0.0084697 | 0.0092014 | 0.033737 | -0.026821 | 0.01379 | -0.019489 | 0.010204 | 0.019721 | -0.008409 | 0.12538 | 0.1011 | 0.31595 | -0.044742 | 0.02852 | 0.078197 | -0.074666 | 0.015831 | 0.18769 | -0.015142 | -0.24657 | 122.4116 | 0.042985 | 122.4666 | 122.448 | 0.036333 | 0.018698 | 0.23356 | 122.2098 | -0.066566 | 122.4849 | 122.3817 | 0.1719 | 0.1053 | -0.097539 | 122.5817 | 122.5575 | 122.7723 | 122.4761 | -0.12714 | 122.4722 | 122.6441 | 122.4412 | 122.5346 | -0.32896
3810 | 122.7997 | -122.4564 | 0.073242 | 1.4211e-13 | -0.017902 | -0.013718 | -0.044957 | -0.041925 | -0.012993 | -0.00083919 | 0.0092014 | 0.033523 | -0.026821 | 0.01379 | -0.019703 | 0.005626 | 0.0243 | -0.003831 | 0.1208 | 0.10567 | 0.32053 | -0.026426 | 0.019362 | 0.082776 | -0.065509 | 0.020409 | 0.18311 | 0.016908 | -0.24657 | 122.4299 | 0.047562 | 122.462 | 122.4525 | 0.022595 | 0.032432 | 0.24729 | 122.2098 | -0.052833 | 122.4757 | 122.3909 | 0.18106 | 0.10987 | -0.056334 | 122.5772 | 122.562 | 122.7769 | 122.4807 | -0.099668 | 122.4768 | 122.6395 | 122.4733 | 122.5391 | -0.31981
3811.9531 | 122.6578 | -122.525 | 0.1236 | 1.4211e-13 | -0.017902 | -0.013718 | -0.044957 | -0.041925 | -0.012352 | 0.0067908 | 0.0092014 | 0.033309 | -0.027035 | 0.014004 | -0.019489 | 0.001048 | 0.0243 | 0.000747 | 0.1208 | 0.11025 | 0.31595 | -0.017268 | 0.019362 | 0.082776 | -0.065509 | 0.015831 | 0.18311 | 0.053537 | -0.25115 | 122.5078 | -0.002792 | 122.5261 | 122.5258 | 0.018015 | -0.013343 | 0.19236 | 122.2739 | -0.10776 | 122.5444 | 122.4595 | 0.18564 | 0.059519 | -0.070059 | 122.6458 | 122.6353 | 122.841 | 122.5493 | -0.14086 | 122.5409 | 122.7081 | 122.5786 | 122.6078 | -0.37474
3813.8594 | 122.6761 | -122.5571 | 0.12817 | 1.4211e-13 | -0.017474 | -0.013505 | -0.044743 | -0.042139 | -0.012993 | -0.0084697 | 0.0089876 | 0.033309 | -0.026821 | 0.013577 | -0.019703 | 0.005626 | 0.015142 | -0.003831 | 0.12538 | 0.096516 | 0.32511 | -0.003531 | 0.023941 | 0.073618 | -0.074666 | 0.020409 | 0.17854 | 0.039801 | -0.25115 | 122.5535 | -0.002792 | 122.5627 | 122.5532 | -0.0003 | -0.031658 | 0.19694 | 122.3059 | -0.10777 | 122.581 | 122.4824 | 0.17648 | 0.050362 | -0.088373 | 122.6825 | 122.6536 | 122.8822 | 122.5722 | -0.13171 | 122.5775 | 122.7356 | 122.5969 | 122.6307 | -0.37932
3815.7188 | 122.6715 | -122.5525 | 0.13275 | 1.4211e-13 | -0.017688 | -0.013932 | -0.04517 | -0.042352 | -0.012565 | -0.0084697 | 0.0092014 | 0.033096 | -0.027249 | 0.01379 | -0.019062 | -0.003531 | 0.0243 | 0.000747 | 0.12538 | 0.096516 | 0.31595 | 0.001048 | 0.02852 | 0.078197 | -0.070087 | 0.015831 | 0.18769 | -0.038035 | -0.25115 | 122.5535 | -0.007369 | 122.549 | 122.5532 | -0.000301 | -0.036235 | 0.1832 | 122.3013 | -0.11692 | 122.581 | 122.4824 | 0.18106 | 0.054942 | -0.17079 | 122.6779 | 122.649 | 122.8684 | 122.5768 | -0.1317 | 122.5683 | 122.7402 | 122.5145 | 122.6307 | -0.3839
3817.5469 | 122.6669 | -122.58 | 0.11902 | 1.4211e-13 | -0.017902 | -0.013718 | -0.04517 | -0.042139 | -0.012993 | -0.00083919 | 0.008774 | 0.033096 | -0.026821 | 0.01379 | -0.019489 | -0.003531 | 0.0243 | -0.003831 | 0.12996 | 0.1011 | 0.31595 | -0.012689 | 0.023941 | 0.078197 | -0.074666 | 0.024988 | 0.17396 | -0.005985 | -0.24657 | 122.5673 | 0.010941 | 122.5764 | 122.5761 | 0.008858 | -0.017924 | 0.19693 | 122.3334 | -0.094031 | 122.6039 | 122.5053 | 0.1719 | 0.054939 | -0.125 | 122.7099 | 122.6811 | 122.8959 | 122.6043 | -0.13171 | 122.6049 | 122.7539 | 122.574 | 122.6582 | -0.36559
3819.5156 | 122.6486 | -122.5479 | 0.13733 | 1.4211e-13 | -0.017902 | -0.013932 | -0.04517 | -0.041925 | -0.012779 | -0.00083919 | 0.0092014 | 0.033523 | -0.027035 | 0.013363 | -0.019489 | 0.005626 | 0.0243 | -0.003831 | 0.1208 | 0.096516 | 0.31595 | -0.012689 | 0.023941 | 0.078197 | -0.065509 | 0.015831 | 0.18311 | -0.015142 | -0.25572 | 122.5352 | -0.016525 | 122.5535 | 122.5441 | 0.008858 | -0.040813 | 0.17862 | 122.2922 | -0.1215 | 122.5719 | 122.4824 | 0.19022 | 0.045786 | -0.15247 | 122.6687 | 122.6444 | 122.8639 | 122.5722 | -0.15002 | 122.5637 | 122.731 | 122.5328 | 122.6261 | -0.39305
3821.7812 | 122.7905 | -122.5067 | 0.086975 | 1.4211e-13 | -0.017474 | -0.013932 | -0.044957 | -0.041925 | -0.012779 | 0.0067908 | 0.0092014 | 0.033523 | -0.027035 | 0.01379 | -0.019489 | 0.001048 | 0.0243 | -0.008409 | 0.1208 | 0.096516 | 0.32053 | -0.003531 | 0.019362 | 0.082776 | -0.065509 | 0.015831 | 0.18311 | 0.007751 | -0.25115 | 122.5032 | 0.033829 | 122.5078 | 122.4983 | -0.004878 | 0.009541 | 0.23356 | 122.2556 | -0.071144 | 122.5261 | 122.4412 | 0.18564 | 0.09614 | -0.079224 | 122.6275 | 122.6032 | 122.8272 | 122.531 | -0.090506 | 122.5225 | 122.6898 | 122.5145 | 122.5895 | -0.33812
3823.5625 | 122.8317 | -122.493 | 0.073242 | 1.4211e-13 | -0.017688 | -0.013291 | -0.04517 | -0.042139 | -0.012779 | -0.00083919 | 0.008774 | 0.033096 | -0.026821 | 0.013577 | -0.019276 | 0.005626 | 0.019721 | -0.008409 | 0.1208 | 0.1011 | 0.32053 | -0.012689 | 0.02852 | 0.078197 | -0.070087 | 0.020409 | 0.18311 | -0.033457 | -0.25115 | 122.4803 | 0.047562 | 122.4986 | 122.4846 | 0.00428 | 0.027853 | 0.24729 | 122.2418 | -0.052833 | 122.5215 | 122.4229 | 0.18106 | 0.10987 | -0.1067 | 122.6138 | 122.5941 | 122.8135 | 122.5127 | -0.085931 | 122.5134 | 122.6761 | 122.4595 | 122.5712 | -0.32439
3825.5 | 122.7631 | -122.525 | 0.07782 | 1.4211e-13 | -0.017902 | -0.013718 | -0.044743 | -0.041925 | -0.012993 | -0.00083919 | 0.0089876 | 0.033523 | -0.027035 | 0.01379 | -0.019489 | 0.014783 | 0.019721 | 0.000747 | 0.12996 | 0.10567 | 0.31595 | -0.021847 | 0.019362 | 0.082776 | -0.070087 | 0.011252 | 0.18769 | -0.019721 | -0.24657 | 122.5032 | 0.05214 | 122.5398 | 122.5258 | 0.022594 | 0.027854 | 0.23813 | 122.2785 | -0.066568 | 122.5444 | 122.4549 | 0.17648 | 0.10987 | -0.097541 | 122.655 | 122.6307 | 122.841 | 122.5447 | -0.099667 | 122.5363 | 122.7127 | 122.5053 | 122.6078 | -0.32439
3827.2969 | 122.7676 | -122.5433 | 0.11902 | 1.4211e-13 | -0.018115 | -0.013718 | -0.044957 | -0.041925 | -0.012565 | -0.00083919 | 0.009415 | 0.033309 | -0.026821 | 0.013577 | -0.019489 | 0.001048 | 0.015142 | -0.003831 | 0.12538 | 0.096516 | 0.31137 | 0.005627 | 0.023941 | 0.087354 | -0.065509 | 0.015831 | 0.17854 | -0.001407 | -0.25115 | 122.549 | 0.006363 | 122.5444 | 122.5395 | -0.009458 | -0.022503 | 0.19235 | 122.2922 | -0.10319 | 122.5673 | 122.4778 | 0.18564 | 0.059517 | -0.12043 | 122.6687 | 122.6399 | 122.8547 | 122.5585 | -0.11339 | 122.5592 | 122.7219 | 122.5419 | 122.6307 | -0.37016
3829.1094 | 122.8363 | -122.4884 | 0.082397 | 1.4211e-13 | -0.017688 | -0.013718 | -0.04517 | -0.041711 | -0.012779 | 0.0067908 | 0.008774 | 0.033309 | -0.026821 | 0.01379 | -0.019276 | 0.001048 | 0.015142 | 0.000747 | 0.12996 | 0.1011 | 0.32053 | -0.012689 | 0.014784 | 0.078197 | -0.065509 | 0.015831 | 0.18311 | -0.010564 | -0.25115 | 122.4757 | 0.047563 | 122.4895 | 122.4892 | 0.013436 | 0.018698 | 0.23813 | 122.2373 | -0.066566 | 122.5032 | 122.4229 | 0.18564 | 0.10072 | -0.092961 | 122.6184 | 122.5895 | 122.8089 | 122.5035 | -0.095086 | 122.5042 | 122.6715 | 122.4778 | 122.5666 | -0.33354
3830.9062 | 122.6852 | -122.525 | 0.11902 | 1.4211e-13 | -0.017688 | -0.013505 | -0.04517 | -0.042352 | -0.012993 | -0.0084697 | 0.0089876 | 0.033523 | -0.026608 | 0.01379 | -0.019489 | 0.005626 | 0.019721 | 0.000747 | 0.12538 | 0.1011 | 0.32053 | -0.012689 | 0.02852 | 0.073618 | -0.083823 | 0.015831 | 0.17854 | 0.003172 | -0.25115 | 122.5123 | 0.006363 | 122.5307 | 122.5258 | 0.013436 | -0.017924 | 0.20151 | 122.2739 | -0.10319 | 122.5535 | 122.4412 | 0.16732 | 0.059517 | -0.11585 | 122.6504 | 122.6261 | 122.8456 | 122.5447 | -0.13171 | 122.5409 | 122.7036 | 122.5282 | 122.5986 | -0.37016
3832.8438 | 122.7722 | -122.5204 | 0.082397 | 1.4211e-13 | -0.017902 | -0.013932 | -0.044957 | -0.042352 | -0.012779 | -0.00083919 | 0.0092014 | 0.033309 | -0.027035 | 0.01379 | -0.019489 | 0.005626 | 0.0243 | 0.000747 | 0.12538 | 0.096516 | 0.32053 | -0.012689 | 0.023941 | 0.078197 | -0.074666 | 0.011252 | 0.18769 | -0.038035 | -0.24657 | 122.5078 | 0.042985 | 122.5261 | 122.5212 | 0.013436 | 0.014119 | 0.23813 | 122.2739 | -0.071145 | 122.5444 | 122.4458 | 0.1719 | 0.1053 | -0.12043 | 122.6458 | 122.617 | 122.841 | 122.5447 | -0.095086 | 122.5317 | 122.7081 | 122.4824 | 122.5986 | -0.32896
3834.5938 | 122.8363 | -122.5113 | 0.10071 | 1.4211e-13 | -0.017902 | -0.013718 | -0.04517 | -0.041925 | -0.012779 | -0.00083919 | 0.0089876 | 0.033096 | -0.026821 | 0.014004 | -0.019489 | 0.001048 | 0.019721 | -0.003831 | 0.12538 | 0.087359 | 0.32511 | -0.017268 | 0.023941 | 0.078197 | -0.079245 | 0.020409 | 0.18311 | 0.021486 | -0.24657 | 122.494 | 0.024674 | 122.5123 | 122.5075 | 0.013437 | -0.013349 | 0.2244 | 122.2647 | -0.080299 | 122.5352 | 122.432 | 0.16732 | 0.082407 | -0.079222 | 122.6367 | 122.5987 | 122.8364 | 122.531 | -0.11798 | 122.5317 | 122.6944 | 122.5328 | 122.5895 | -0.34728
3836.4688 | 122.7676 | -122.5433 | 0.10529 | 1.4211e-13 | -0.017688 | -0.013505 | -0.044957 | -0.042139 | -0.012779 | 0.0067908 | 0.008774 | 0.033523 | -0.026608 | 0.01379 | -0.019276 | -0.003531 | 0.019721 | -0.008409 | 0.12538 | 0.096516 | 0.32053 | 0.010206 | 0.019362 | 0.078197 | -0.070087 | 0.020409 | 0.18311 | 0.026065 | -0.25115 | 122.5535 | 0.020096 | 122.5398 | 122.5349 | -0.018615 | -0.00877 | 0.21525 | 122.2922 | -0.084877 | 122.5627 | 122.4732 | 0.18106 | 0.077829 | -0.079221 | 122.6687 | 122.6399 | 122.8639 | 122.5631 | -0.09508 | 122.5637 | 122.7264 | 122.5694 | 122.6215 | -0.35643
3838.3125 | 122.7859 | -122.5159 | 0.09613 | 1.4211e-13 | -0.017688 | -0.013505 | -0.04517 | -0.042139 | -0.012779 | -0.00083919 | 0.0089876 | 0.033309 | -0.026821 | 0.01379 | -0.019489 | 0.010204 | 0.019721 | -0.008409 | 0.11622 | 0.10567 | 0.32053 | 0.005627 | 0.023941 | 0.078197 | -0.074666 | 0.011252 | 0.18769 | -0.047193 | -0.24657 | 122.5215 | 0.020095 | 122.5261 | 122.5075 | -0.014036 | 0.009544 | 0.2244 | 122.2693 | -0.084878 | 122.5398 | 122.4412 | 0.1719 | 0.091563 | -0.14332 | 122.6321 | 122.6215 | 122.8364 | 122.5356 | -0.090503 | 122.5271 | 122.7036 | 122.4687 | 122.5941 | -0.3427
3840.0781 | 122.8043 | -122.5479 | 0.09613 | 1.4211e-13 | -0.017902 | -0.013718 | -0.04517 | -0.042352 | -0.013206 | -0.0084697 | 0.009415 | 0.033523 | -0.027035 | 0.014004 | -0.019276 | 0.010204 | 0.0243 | -0.003831 | 0.12538 | 0.1011 | 0.32053 | 0.005627 | 0.023941 | 0.073618 | -0.065509 | 0.015831 | 0.18311 | -0.065507 | -0.24657 | 122.5535 | 0.029252 | 122.5581 | 122.5441 | -0.009458 | 0.004965 | 0.2244 | 122.3013 | -0.080299 | 122.5719 | 122.4824 | 0.18106 | 0.086985 | -0.16164 | 122.6733 | 122.649 | 122.8684 | 122.5722 | -0.090503 | 122.5637 | 122.731 | 122.4824 | 122.6215 | -0.3427
3841.9219 | 122.7859 | -122.5159 | 0.10071 | 1.4211e-13 | -0.017902 | -0.013077 | -0.045384 | -0.042139 | -0.012993 | -0.00083919 | 0.0089876 | 0.033096 | -0.026608 | 0.01379 | -0.019276 | -0.003531 | 0.028878 | -0.003831 | 0.11622 | 0.096516 | 0.31595 | 0.001048 | 0.019362 | 0.082776 | -0.070087 | 0.015831 | 0.18311 | 0.030644 | -0.24657 | 122.5169 | 0.015517 | 122.5123 | 122.512 | -0.004879 | -0.004192 | 0.21524 | 122.2693 | -0.084877 | 122.5352 | 122.4458 | 0.17648 | 0.082407 | -0.070064 | 122.6321 | 122.6124 | 122.8318 | 122.5447 | -0.09966 | 122.5317 | 122.699 | 122.5465 | 122.5986 | -0.34728
3843.875 | 122.8638 | -122.525 | 0.091553 | 1.4211e-13 | -0.017474 | -0.014146 | -0.04517 | -0.042139 | -0.012779 | -0.00083919 | 0.009415 | 0.033309 | -0.026821 | 0.01379 | -0.019276 | 0.010204 | 0.0243 | 0.000747 | 0.12538 | 0.091937 | 0.32053 | 0.005627 | 0.023941 | 0.078197 | -0.070087 | 0.015831 | 0.18311 | 0.012329 | -0.24657 | 122.5307 | 0.033829 | 122.5352 | 122.5258 | -0.00488 | 0.000384 | 0.22898 | 122.2785 | -0.075722 | 122.549 | 122.4549 | 0.17648 | 0.091562 | -0.079224 | 122.6504 | 122.617 | 122.8456 | 122.5493 | -0.085926 | 122.5409 | 122.7081 | 122.5374 | 122.6032 | -0.33812
3846 | 122.7585 | -122.5525 | 0.11444 | 1.4211e-13 | -0.017688 | -0.013932 | -0.045384 | -0.042352 | -0.012779 | -0.00083919 | 0.0092014 | 0.033309 | -0.027035 | 0.01379 | -0.019703 | 0.005626 | 0.028878 | 0.000747 | 0.12538 | 0.1011 | 0.31137 | -0.00811 | 0.023941 | 0.082776 | -0.074666 | 0.020409 | 0.18311 | 0.035222 | -0.24657 | 122.5444 | 0.010941 | 122.5581 | 122.5532 | 0.008857 | -0.013346 | 0.19693 | 122.3059 | -0.094032 | 122.5764 | 122.4778 | 0.1719 | 0.068674 | -0.079219 | 122.6779 | 122.6536 | 122.8639 | 122.5814 | -0.12255 | 122.5729 | 122.7356 | 122.5877 | 122.6353 | -0.36101
3848.0781 | 122.7036 | -122.5891 | 0.11902 | 1.4211e-13 | -0.017688 | -0.013718 | -0.044957 | -0.042352 | -0.012779 | -0.0084697 | 0.0092014 | 0.033523 | -0.026821 | 0.013577 | -0.019276 | 0.001048 | 0.0243 | 0.000747 | 0.1208 | 0.1011 | 0.31595 | -0.00811 | 0.023941 | 0.082776 | -0.070087 | 0.015831 | 0.16938 | -0.010564 | -0.24657 | 122.581 | 0.001785 | 122.5902 | 122.5899 | 0.008857 | -0.017924 | 0.19693 | 122.3425 | -0.10319 | 122.6131 | 122.519 | 0.17648 | 0.05036 | -0.12958 | 122.7099 | 122.6902 | 122.9051 | 122.6134 | -0.12713 | 122.6049 | 122.7585 | 122.5785 | 122.6719 | -0.36559
3849.875 | 122.8409 | -122.5433 | 0.086975 | 1.4211e-13 | -0.017902 | -0.013718 | -0.044957 | -0.042139 | -0.012779 | -0.00083919 | 0.0089876 | 0.033309 | -0.026821 | 0.01379 | -0.019276 | 0.005626 | 0.0243 | -0.003831 | 0.12538 | 0.096516 | 0.32969 | -0.003531 | 0.023941 | 0.082776 | -0.070087 | 0.015831 | 0.18311 | -0.042614 | -0.24657 | 122.5398 | 0.038407 | 122.549 | 122.5395 | -0.0003 | 0.009541 | 0.24271 | 122.2968 | -0.071144 | 122.5673 | 122.4732 | 0.17648 | 0.09614 | -0.12959 | 122.6687 | 122.6399 | 122.873 | 122.5676 | -0.090506 | 122.5592 | 122.7264 | 122.5007 | 122.6261 | -0.33354
3851.6875 | 122.7219 | -122.58 | 0.13733 | 1.4211e-13 | -0.017688 | -0.014573 | -0.045384 | -0.042139 | -0.013206 | -0.0161 | 0.0089876 | 0.033737 | -0.026821 | 0.01379 | -0.019062 | 0.010204 | 0.0243 | -0.012988 | 0.12538 | 0.091937 | 0.31595 | 0.005627 | 0.033099 | 0.078197 | -0.070087 | 0.011252 | 0.18311 | -0.005985 | -0.24199 | 122.5856 | -0.011947 | 122.5902 | 122.567 | -0.018615 | -0.045392 | 0.17862 | 122.338 | -0.12608 | 122.6131 | 122.5099 | 0.1719 | 0.045786 | -0.14331 | 122.7053 | 122.6719 | 122.8959 | 122.6043 | -0.1317 | 122.5912 | 122.7631 | 122.574 | 122.6582 | -0.37932
3853.5469 | 122.731 | -122.5708 | 0.13733 | 1.4211e-13 | -0.017688 | -0.013718 | -0.04517 | -0.042139 | -0.012779 | -0.00083919 | 0.0092014 | 0.033309 | -0.027035 | 0.013577 | -0.019489 | -0.003531 | 0.028878 | -0.003831 | 0.12538 | 0.1011 | 0.31595 | -0.00811 | 0.023941 | 0.06904 | -0.06093 | 0.015831 | 0.18311 | -0.019721 | -0.25115 | 122.5627 | -0.011947 | 122.5673 | 122.567 | 0.004279 | -0.036234 | 0.17862 | 122.3197 | -0.1215 | 122.5947 | 122.5099 | 0.19022 | 0.045786 | -0.15705 | 122.6962 | 122.6719 | 122.8868 | 122.5997 | -0.14544 | 122.5866 | 122.7539 | 122.5511 | 122.6398 | -0.38848
3855.2656 | 122.8134 | -122.5708 | 0.10986 | 1.4211e-13 | -0.017688 | -0.013718 | -0.04517 | -0.041925 | -0.012779 | -0.0084697 | 0.0092014 | 0.033096 | -0.027035 | 0.013577 | -0.019489 | 0.010204 | 0.019721 | 0.000747 | 0.12996 | 0.091937 | 0.32053 | -0.021847 | 0.02852 | 0.078197 | -0.070087 | 0.020409 | 0.18311 | 0.007751 | -0.24199 | 122.549 | 0.020097 | 122.581 | 122.5715 | 0.022594 | -0.017926 | 0.21067 | 122.3288 | -0.089454 | 122.5993 | 122.5007 | 0.1719 | 0.073252 | -0.10211 | 122.7008 | 122.6627 | 122.8913 | 122.5905 | -0.13171 | 122.5912 | 122.7539 | 122.5786 | 122.649 | -0.35185
3856.9844 | 122.7356 | -122.5754 | 0.12817 | 1.4211e-13 | -0.017688 | -0.013932 | -0.044957 | -0.042352 | -0.012993 | -0.00083919 | 0.0089876 | 0.033523 | -0.027035 | 0.01379 | -0.019489 | -0.003531 | 0.019721 | 0.000747 | 0.12996 | 0.1011 | 0.32053 | -0.00811 | 0.019362 | 0.082776 | -0.074666 | 0.020409 | 0.18311 | -0.070086 | -0.2603 | 122.5673 | 0.001786 | 122.5718 | 122.5761 | 0.008857 | -0.027079 | 0.19236 | 122.3151 | -0.10777 | 122.5947 | 122.5007 | 0.18564 | 0.054941 | -0.19826 | 122.7053 | 122.6765 | 122.8959 | 122.5951 | -0.13628 | 122.5958 | 122.7585 | 122.5053 | 122.6582 | -0.38848
3858.7188 | 122.7402 | -122.5983 | 0.11902 | 1.4211e-13 | -0.017902 | -0.013718 | -0.04517 | -0.042352 | -0.012779 | -0.0084697 | 0.0096286 | 0.033309 | -0.027035 | 0.014004 | -0.019489 | 0.001048 | 0.0243 | -0.003831 | 0.12538 | 0.1011 | 0.31137 | 0.001048 | 0.02852 | 0.087354 | -0.065509 | 0.020409 | 0.18311 | -0.051771 | -0.25572 | 122.5993 | 0.006363 | 122.5993 | 122.5944 | -0.004879 | -0.017924 | 0.19235 | 122.3425 | -0.09861 | 122.6268 | 122.5328 | 0.19022 | 0.064096 | -0.17079 | 122.7236 | 122.6994 | 122.9096 | 122.6226 | -0.11797 | 122.6187 | 122.7814 | 122.5465 | 122.6856 | -0.37474
3860.4688 | 122.8455 | -122.5342 | 0.073242 | 1.4211e-13 | -0.017688 | -0.013932 | -0.044957 | -0.041925 | -0.012779 | -0.00083919 | 0.0092014 | 0.033096 | -0.026821 | 0.01379 | -0.019489 | 0.001048 | 0.019721 | 0.000747 | 0.12538 | 0.1011 | 0.31137 | -0.003531 | 0.023941 | 0.073618 | -0.074666 | 0.011252 | 0.18311 | -0.005985 | -0.25115 | 122.5306 | 0.05214 | 122.5352 | 122.5349 | 0.004278 | 0.027853 | 0.23813 | 122.283 | -0.06199 | 122.5581 | 122.4595 | 0.17648 | 0.10987 | -0.079227 | 122.6596 | 122.6353 | 122.8456 | 122.5539 | -0.076773 | 122.5454 | 122.7173 | 122.5282 | 122.6078 | -0.32439
3862.1719 | 122.85 | -122.5662 | 0.086975 | 1.4211e-13 | -0.017688 | -0.014146 | -0.044957 | -0.042352 | -0.013206 | -0.00083919 | 0.009415 | 0.033096 | -0.027035 | 0.01379 | -0.019276 | 0.005626 | 0.0243 | 0.000747 | 0.12996 | 0.096516 | 0.32969 | -0.026426 | 0.023941 | 0.078197 | -0.070087 | 0.020409 | 0.19227 | 0.026065 | -0.25115 | 122.5398 | 0.042985 | 122.5718 | 122.567 | 0.027173 | 0.009541 | 0.24271 | 122.3151 | -0.066566 | 122.5902 | 122.4961 | 0.18106 | 0.1053 | -0.06091 | 122.6962 | 122.6627 | 122.8959 | 122.5905 | -0.1134 | 122.5866 | 122.7585 | 122.5923 | 122.6444 | -0.33812
3863.8906 | 122.8592 | -122.5754 | 0.09613 | 1.4211e-13 | -0.017474 | -0.013718 | -0.04517 | -0.041925 | -0.013206 | -0.0084697 | 0.009415 | 0.033309 | -0.027035 | 0.01379 | -0.019276 | 0.001048 | 0.0243 | -0.003831 | 0.1208 | 0.091937 | 0.31595 | 0.001048 | 0.033099 | 0.06904 | -0.070087 | 0.024988 | 0.17854 | -0.010564 | -0.24657 | 122.5764 | 0.024674 | 122.5764 | 122.5715 | -0.004879 | -0.004193 | 0.21982 | 122.3288 | -0.071142 | 122.6085 | 122.5053 | 0.17648 | 0.082406 | -0.10669 | 122.6962 | 122.6673 | 122.8913 | 122.5997 | -0.095082 | 122.6004 | 122.7539 | 122.5648 | 122.6444 | -0.3427
3865.6562 | 122.8729 | -122.5616 | 0.082397 | 1.4211e-13 | -0.017474 | -0.013932 | -0.04517 | -0.042352 | -0.012993 | -0.00083919 | 0.008774 | 0.033309 | -0.027035 | 0.014218 | -0.019703 | 0.005626 | 0.019721 | 0.000747 | 0.12538 | 0.10567 | 0.32053 | -0.021847 | 0.023941 | 0.078197 | -0.065509 | 0.015831 | 0.17854 | -0.010564 | -0.24657 | 122.5398 | 0.042985 | 122.5673 | 122.5624 | 0.022594 | 0.023277 | 0.23813 | 122.3151 | -0.066566 | 122.5856 | 122.4961 | 0.18106 | 0.096139 | -0.092961 | 122.687 | 122.6673 | 122.8822 | 122.5814 | -0.10424 | 122.5775 | 122.7402 | 122.5511 | 122.6398 | -0.32896
3867.4219 | 122.7631 | -122.5937 | 0.12817 | 1.4211e-13 | -0.017902 | -0.013077 | -0.044957 | -0.042566 | -0.012779 | -0.00083919 | 0.0092014 | 0.033309 | -0.027035 | 0.013577 | -0.019276 | 0.005626 | 0.015142 | -0.008409 | 0.12538 | 0.1011 | 0.32053 | -0.00811 | 0.023941 | 0.078197 | -0.074666 | 0.015831 | 0.18769 | -0.065507 | -0.24657 | 122.5856 | -0.002792 | 122.5993 | 122.5853 | -0.000299 | -0.027079 | 0.19236 | 122.3471 | -0.11234 | 122.6176 | 122.519 | 0.1719 | 0.059519 | -0.19368 | 122.7191 | 122.6948 | 122.9142 | 122.6088 | -0.13628 | 122.6095 | 122.7814 | 122.5282 | 122.6719 | -0.37474
3869.1406 | 122.7905 | -122.5662 | 0.10529 | 1.4211e-13 | -0.017688 | -0.013505 | -0.04517 | -0.042139 | -0.012779 | -0.00083919 | 0.0092014 | 0.033096 | -0.026821 | 0.01379 | -0.019276 | 0.005626 | 0.0243 | 0.000747 | 0.12538 | 0.096516 | 0.32053 | -0.012689 | 0.023941 | 0.082776 | -0.070087 | 0.020409 | 0.18769 | 0.039801 | -0.24657 | 122.5535 | 0.020096 | 122.5718 | 122.567 | 0.013436 | -0.00877 | 0.21525 | 122.3197 | -0.084877 | 122.5902 | 122.4961 | 0.17648 | 0.082407 | -0.065485 | 122.6916 | 122.6627 | 122.8868 | 122.5905 | -0.11798 | 122.5866 | 122.7539 | 122.606 | 122.649 | -0.35185
3870.8438 | 122.7768 | -122.58 | 0.1236 | 1.4211e-13 | -0.017688 | -0.013505 | -0.044957 | -0.041925 | -0.013206 | 0.0067908 | 0.0092014 | 0.033523 | -0.026821 | 0.01379 | -0.019489 | -0.003531 | 0.0243 | 0.000747 | 0.12996 | 0.096516 | 0.31595 | -0.012689 | 0.023941 | 0.082776 | -0.070087 | 0.024988 | 0.18311 | 0.026065 | -0.24657 | 122.5673 | 0.006364 | 122.5764 | 122.5807 | 0.013436 | -0.02708 | 0.19236 | 122.3334 | -0.098608 | 122.6039 | 122.5099 | 0.17648 | 0.059519 | -0.097531 | 122.7099 | 122.6765 | 122.8959 | 122.6043 | -0.13628 | 122.6049 | 122.7631 | 122.606 | 122.6627 | -0.37016
3872.5625 | 122.8363 | -122.5754 | 0.091553 | 1.4211e-13 | -0.017688 | -0.013718 | -0.044743 | -0.042352 | -0.012993 | -0.0084697 | 0.0092014 | 0.033309 | -0.026821 | 0.014004 | -0.019062 | 0.001048 | 0.015142 | 0.000747 | 0.12538 | 0.096516 | 0.31595 | -0.012689 | 0.02852 | 0.082776 | -0.070087 | 0.015831 | 0.18311 | -0.015142 | -0.24657 | 122.5627 | 0.033829 | 122.5764 | 122.5761 | 0.013436 | 0.004963 | 0.2244 | 122.3288 | -0.075722 | 122.6039 | 122.5053 | 0.17648 | 0.091562 | -0.10669 | 122.7008 | 122.6719 | 122.8913 | 122.5905 | -0.10424 | 122.5912 | 122.7585 | 122.5602 | 122.6582 | -0.33812
3874.2812 | 122.7676 | -122.5891 | 0.10529 | 1.4211e-13 | -0.017688 | -0.013718 | -0.044957 | -0.041925 | -0.012993 | -0.00083919 | 0.0089876 | 0.033737 | -0.027249 | 0.014004 | -0.019062 | 0.001048 | 0.0243 | -0.003831 | 0.12538 | 0.10567 | 0.32511 | -0.012689 | 0.023941 | 0.078197 | -0.074666 | 0.011252 | 0.18311 | -0.015142 | -0.24657 | 122.5764 | 0.020096 | 122.5902 | 122.5853 | 0.008858 | 0.000388 | 0.21982 | 122.3425 | -0.094034 | 122.6131 | 122.5144 | 0.1719 | 0.077829 | -0.12043 | 122.7145 | 122.6948 | 122.9142 | 122.6134 | -0.11798 | 122.6004 | 122.7722 | 122.574 | 122.6673 | -0.35185
3876.0312 | 122.7905 | -122.5708 | 0.11902 | 1.4211e-13 | -0.017688 | -0.013718 | -0.045384 | -0.042139 | -0.012779 | -0.00083919 | 0.0092014 | 0.033309 | -0.026608 | 0.013577 | -0.019276 | 0.005626 | 0.019721 | -0.003831 | 0.12538 | 0.10567 | 0.32053 | -0.003531 | 0.023941 | 0.078197 | -0.070087 | 0.015831 | 0.17854 | -0.0243 | -0.25115 | 122.5673 | 0.006363 | 122.5764 | 122.567 | -0.0003 | -0.013345 | 0.20151 | 122.3197 | -0.10319 | 122.5947 | 122.5007 | 0.18106 | 0.059517 | -0.14332 | 122.6962 | 122.6765 | 122.8913 | 122.5905 | -0.12255 | 122.5866 | 122.7493 | 122.5465 | 122.649 | -0.37016
3877.75 | 122.7676 | -122.6028 | 0.1236 | 1.4211e-13 | -0.01726 | -0.013505 | -0.044957 | -0.041925 | -0.012565 | -0.00083919 | 0.0092014 | 0.033309 | -0.027035 | 0.014004 | -0.019703 | 0.005626 | 0.015142 | 0.000747 | 0.12996 | 0.091937 | 0.31595 | 0.010206 | 0.019362 | 0.078197 | -0.070087 | 0.015831 | 0.17854 | -0.005985 | -0.24657 | 122.6131 | 0.006364 | 122.6085 | 122.6036 | -0.009459 | -0.031659 | 0.19236 | 122.3563 | -0.10776 | 122.6222 | 122.5328 | 0.17648 | 0.05494 | -0.12958 | 122.7328 | 122.6948 | 122.9188 | 122.618 | -0.11339 | 122.6187 | 122.7814 | 122.5969 | 122.681 | -0.37016
3879.4844 | 122.8409 | -122.5708 | 0.10986 | 1.4211e-13 | -0.017688 | -0.013932 | -0.04517 | -0.041925 | -0.012779 | -0.0084697 | 0.009415 | 0.033523 | -0.026608 | 0.01379 | -0.019489 | 0.005626 | 0.019721 | -0.003831 | 0.11622 | 0.1011 | 0.31595 | -0.049321 | 0.014784 | 0.078197 | -0.070087 | 0.024988 | 0.17854 | 0.053537 | -0.25115 | 122.5215 | 0.006362 | 122.5764 | 122.567 | 0.04549 | -0.008768 | 0.20609 | 122.3197 | -0.084875 | 122.5856 | 122.5007 | 0.18106 | 0.068673 | -0.056326 | 122.687 | 122.6719 | 122.8868 | 122.5905 | -0.15918 | 122.5958 | 122.7493 | 122.6243 | 122.649 | -0.36101
3881.2031 | 122.7493 | -122.6257 | 0.13275 | 1.4211e-13 | -0.017688 | -0.013932 | -0.045384 | -0.041711 | -0.012779 | 0.0067908 | 0.0096286 | 0.033523 | -0.027035 | 0.014004 | -0.019276 | 0.001048 | 0.0243 | -0.008409 | 0.12996 | 0.10567 | 0.31595 | -0.026426 | 0.023941 | 0.073618 | -0.074666 | 0.020409 | 0.18311 | -0.001407 | -0.25572 | 122.5993 | -0.002791 | 122.6268 | 122.6173 | 0.018017 | -0.027077 | 0.1832 | 122.37 | -0.11234 | 122.6497 | 122.5511 | 0.18106 | 0.050364 | -0.13416 | 122.7557 | 122.7314 | 122.9417 | 122.65 | -0.15918 | 122.6461 | 122.8088 | 122.6243 | 122.6993 | -0.38848
3882.9688 | 122.8363 | -122.6028 | 0.10071 | 1.4211e-13 | -0.017474 | -0.013291 | -0.04517 | -0.042139 | -0.012993 | 0.0067908 | 0.0092014 | 0.033309 | -0.026394 | 0.01379 | -0.019276 | 0.005626 | 0.019721 | -0.003831 | 0.1208 | 0.1011 | 0.31595 | 0.005627 | 0.02852 | 0.06904 | -0.070087 | 0.015831 | 0.18311 | -0.005985 | -0.25115 | 122.6085 | 0.020096 | 122.6085 | 122.599 | -0.009458 | 0.000387 | 0.21524 | 122.3517 | -0.084877 | 122.6314 | 122.5328 | 0.18106 | 0.082407 | -0.10669 | 122.7236 | 122.7039 | 122.9188 | 122.6226 | -0.095081 | 122.6187 | 122.786 | 122.5969 | 122.6719 | -0.35185
3884.7344 | 122.8592 | -122.5937 | 0.091553 | 1.4211e-13 | -0.017474 | -0.013718 | -0.045384 | -0.042352 | -0.012993 | -0.023731 | 0.0092014 | 0.033096 | -0.026821 | 0.014004 | -0.019276 | 0.005626 | 0.019721 | -0.003831 | 0.12538 | 0.096516 | 0.32053 | -0.00811 | 0.02852 | 0.078197 | -0.070087 | 0.015831 | 0.18311 | -0.051771 | -0.24657 | 122.5856 | 0.033829 | 122.5993 | 122.5899 | 0.004279 | 0.004963 | 0.22898 | 122.3471 | -0.075722 | 122.6222 | 122.5236 | 0.17648 | 0.091562 | -0.14332 | 122.7191 | 122.6902 | 122.9142 | 122.6134 | -0.099663 | 122.6095 | 122.7768 | 122.5419 | 122.6719 | -0.33812
3886.4531 | 122.8867 | -122.58 | 0.082397 | 1.4211e-13 | -0.017474 | -0.014146 | -0.045384 | -0.042139 | -0.012779 | -0.0084697 | 0.009415 | 0.033309 | -0.027035 | 0.01379 | -0.019062 | 0.010204 | 0.019721 | -0.003831 | 0.12538 | 0.091937 | 0.31595 | -0.049321 | 0.023941 | 0.082776 | -0.074666 | 0.020409 | 0.17854 | 0.039801 | -0.25115 | 122.5306 | 0.042985 | 122.5902 | 122.5761 | 0.04549 | 0.00954 | 0.23356 | 122.3288 | -0.061988 | 122.6039 | 122.5053 | 0.17648 | 0.096139 | -0.042596 | 122.7053 | 122.6719 | 122.8959 | 122.5997 | -0.13172 | 122.6004 | 122.7585 | 122.6198 | 122.6627 | -0.33354
3888.2188 | 122.7448 | -122.612 | 0.13733 | 1.4211e-13 | -0.017688 | -0.014359 | -0.04517 | -0.042139 | -0.012779 | 0.0067908 | 0.009415 | 0.033096 | -0.026821 | 0.01379 | -0.019489 | 0.001048 | 0.015142 | -0.003831 | 0.1208 | 0.10567 | 0.32511 | -0.026426 | 0.023941 | 0.073618 | -0.070087 | 0.020409 | 0.18311 | -0.038035 | -0.25115 | 122.5856 | -0.016525 | 122.613 | 122.6082 | 0.022595 | -0.031655 | 0.18778 | 122.3609 | -0.11692 | 122.6359 | 122.5419 | 0.18106 | 0.045786 | -0.17536 | 122.7328 | 122.7177 | 122.9371 | 122.6271 | -0.16376 | 122.6324 | 122.7951 | 122.574 | 122.6856 | -0.38848
3889.9219 | 122.85 | -122.5845 | 0.091553 | 1.4211e-13 | -0.017474 | -0.013718 | -0.044957 | -0.041711 | -0.012779 | -0.00083919 | 0.0096286 | 0.033309 | -0.026608 | 0.013577 | -0.019703 | 0.005626 | 0.019721 | -0.012988 | 0.12996 | 0.1011 | 0.32053 | -0.00811 | 0.023941 | 0.078197 | -0.065509 | 0.020409 | 0.18311 | 0.030644 | -0.25115 | 122.5764 | 0.038407 | 122.5902 | 122.5715 | -0.004878 | 0.009542 | 0.22898 | 122.3334 | -0.071144 | 122.6085 | 122.519 | 0.18564 | 0.091562 | -0.060909 | 122.7145 | 122.6856 | 122.9051 | 122.6043 | -0.099663 | 122.6049 | 122.7676 | 122.6152 | 122.6627 | -0.3427
3891.6406 | 122.8226 | -122.612 | 0.10071 | 1.4211e-13 | -0.017688 | -0.013718 | -0.04517 | -0.041925 | -0.012779 | -0.0084697 | 0.009415 | 0.033309 | -0.027035 | 0.013577 | -0.019703 | -0.003531 | 0.019721 | 0.000747 | 0.1208 | 0.10567 | 0.32053 | -0.021847 | 0.033099 | 0.078197 | -0.070087 | 0.015831 | 0.19227 | 0.035222 | -0.25115 | 122.5902 | 0.020096 | 122.6085 | 122.6127 | 0.022594 | 0.004966 | 0.21982 | 122.3609 | -0.084877 | 122.6451 | 122.5419 | 0.18106 | 0.091564 | -0.065486 | 122.7328 | 122.7177 | 122.9325 | 122.6317 | -0.12255 | 122.6278 | 122.8043 | 122.6472 | 122.6902 | -0.35185
3893.375 | 122.7814 | -122.6257 | 0.13275 | 1.4211e-13 | -0.017902 | -0.013932 | -0.044743 | -0.042566 | -0.012565 | 0.0067908 | 0.0089876 | 0.033309 | -0.026608 | 0.01379 | -0.019489 | 0.001048 | 0.015142 | -0.003831 | 0.1208 | 0.1011 | 0.31595 | -0.026426 | 0.02852 | 0.073618 | -0.070087 | 0.020409 | 0.17854 | 0.030644 | -0.24657 | 122.5993 | -0.011947 | 122.6268 | 122.6219 | 0.022595 | -0.031656 | 0.1832 | 122.3792 | -0.11234 | 122.6543 | 122.5556 | 0.17648 | 0.045785 | -0.10211 | 122.7465 | 122.7268 | 122.9417 | 122.6409 | -0.15918 | 122.6461 | 122.8043 | 122.6564 | 122.6993 | -0.37932
3895.125 | 122.7676 | -122.6395 | 0.12817 | 1.4211e-13 | -0.017474 | -0.013932 | -0.044957 | -0.042139 | -0.012993 | -0.0161 | 0.009415 | 0.033523 | -0.026821 | 0.01379 | -0.019276 | 0.001048 | 0.019721 | -0.012988 | 0.12538 | 0.1011 | 0.32053 | -0.00811 | 0.023941 | 0.078197 | -0.065509 | 0.011252 | 0.17854 | 0.016908 | -0.24199 | 122.6314 | -0.002792 | 122.6405 | 122.6265 | -0.004878 | -0.027079 | 0.19236 | 122.3975 | -0.11692 | 122.6634 | 122.574 | 0.17648 | 0.050362 | -0.11127 | 122.7648 | 122.7406 | 122.96 | 122.6592 | -0.13628 | 122.6507 | 122.818 | 122.6564 | 122.7177 | -0.37016
3896.8438 | 122.9141 | -122.5754 | 0.091553 | 1.4211e-13 | -0.01726 | -0.013932 | -0.04517 | -0.041925 | -0.012779 | -0.00083919 | 0.0092014 | 0.033096 | -0.026821 | 0.01379 | -0.019703 | 0.005626 | 0.019721 | 0.000747 | 0.11165 | 0.096516 | 0.32053 | 0.001048 | 0.019362 | 0.078197 | -0.070087 | 0.024988 | 0.18311 | -0.079243 | -0.25115 | 122.5764 | 0.020094 | 122.581 | 122.5761 | -0.000301 | 0.004963 | 0.22898 | 122.3242 | -0.066565 | 122.5947 | 122.5053 | 0.18106 | 0.091562 | -0.1708 | 122.687 | 122.6719 | 122.8959 | 122.5951 | -0.090505 | 122.6004 | 122.7585 | 122.4961 | 122.6536 | -0.3427
3898.6094 | 122.7722 | -122.6074 | 0.12817 | 1.4211e-13 | -0.017688 | -0.013718 | -0.04517 | -0.041925 | -0.012565 | -0.00083919 | 0.0096286 | 0.033309 | -0.026821 | 0.014004 | -0.019276 | -0.003531 | 0.019721 | -0.008409 | 0.12538 | 0.091937 | 0.31137 | -0.00811 | 0.023941 | 0.078197 | -0.070087 | 0.015831 | 0.18769 | -0.028878 | -0.25115 | 122.5993 | -0.002792 | 122.6039 | 122.599 | -0.000299 | -0.036237 | 0.1832 | 122.3563 | -0.11234 | 122.6314 | 122.5373 | 0.18106 | 0.059519 | -0.15705 | 122.7328 | 122.6994 | 122.9188 | 122.6271 | -0.13628 | 122.6233 | 122.7951 | 122.5785 | 122.6856 | -0.37932
3900.5 | 122.7768 | -122.6349 | 0.11444 | 1.4211e-13 | -0.01726 | -0.013718 | -0.044957 | -0.042139 | -0.012993 | -0.00083919 | 0.0092014 | 0.033096 | -0.026821 | 0.01379 | -0.019489 | -0.003531 | 0.010564 | -0.008409 | 0.12996 | 0.096516 | 0.31595 | -0.026426 | 0.023941 | 0.078197 | -0.074666 | 0.024988 | 0.18311 | -0.015142 | -0.24657 | 122.6085 | 0.015519 | 122.6314 | 122.6265 | 0.018017 | -0.017925 | 0.20151 | 122.3883 | -0.089453 | 122.6588 | 122.5602 | 0.1719 | 0.068674 | -0.12958 | 122.7648 | 122.7314 | 122.9508 | 122.6455 | -0.14087 | 122.6599 | 122.818 | 122.6197 | 122.7131 | -0.36101
3902.3125 | 122.8088 | -122.6578 | 0.13733 | 1.4211e-13 | -0.017688 | -0.013718 | -0.044957 | -0.041925 | -0.012565 | -0.0084697 | 0.009415 | 0.033523 | -0.027249 | 0.013577 | -0.019062 | 0.001048 | 0.010564 | 0.005325 | 0.1208 | 0.1011 | 0.31137 | -0.003531 | 0.02852 | 0.073618 | -0.074666 | 0.029566 | 0.18769 | 0.026065 | -0.25115 | 122.6542 | -0.016525 | 122.6588 | 122.6631 | 0.008856 | -0.036234 | 0.17404 | 122.4066 | -0.10776 | 122.6863 | 122.5831 | 0.17648 | 0.050364 | -0.11126 | 122.7786 | 122.7589 | 122.9691 | 122.6683 | -0.14086 | 122.6873 | 122.8455 | 122.6838 | 122.7314 | -0.38848
3904.0469 | 122.8867 | -122.5891 | 0.07782 | 1.4211e-13 | -0.017474 | -0.013505 | -0.04517 | -0.042352 | -0.013206 | 0.014421 | 0.0092014 | 0.033309 | -0.026821 | 0.01379 | -0.019489 | 0.005626 | 0.019721 | -0.008409 | 0.12538 | 0.1011 | 0.32969 | -0.017268 | 0.019362 | 0.078197 | -0.065509 | 0.011252 | 0.19227 | -0.005985 | -0.25115 | 122.5718 | 0.047562 | 122.5947 | 122.5807 | 0.008859 | 0.023275 | 0.25187 | 122.338 | -0.066568 | 122.6085 | 122.5236 | 0.18564 | 0.11445 | -0.083805 | 122.7145 | 122.6902 | 122.9188 | 122.6088 | -0.095088 | 122.6004 | 122.7814 | 122.5831 | 122.6673 | -0.32897
3905.8438 | 122.8317 | -122.644 | 0.11902 | 1.4211e-13 | -0.017047 | -0.013718 | -0.04517 | -0.042352 | -0.012779 | -0.00083919 | 0.0092014 | 0.032882 | -0.026608 | 0.013577 | -0.019489 | 0.005626 | 0.019721 | 0.005325 | 0.1208 | 0.1011 | 0.32053 | 0.001048 | 0.023941 | 0.073618 | -0.070087 | 0.015831 | 0.18311 | 0.044379 | -0.24199 | 122.6451 | 0.001785 | 122.6497 | 122.6494 | 0.004277 | -0.017924 | 0.20151 | 122.4021 | -0.10319 | 122.668 | 122.574 | 0.1719 | 0.064096 | -0.07464 | 122.7648 | 122.7451 | 122.9646 | 122.6638 | -0.11797 | 122.6599 | 122.8272 | 122.6884 | 122.7177 | -0.36101
3907.6562 | 122.9279 | -122.5937 | 0.091553 | 1.4211e-13 | -0.017047 | -0.013505 | -0.04517 | -0.042352 | -0.012779 | -0.0084697 | 0.0092014 | 0.032882 | -0.027249 | 0.01379 | -0.019489 | 0.005626 | 0.019721 | 0.000747 | 0.1208 | 0.096516 | 0.31595 | -0.026426 | 0.023941 | 0.073618 | -0.070087 | 0.015831 | 0.18311 | -0.051771 | -0.25115 | 122.5673 | 0.029251 | 122.5993 | 122.5944 | 0.027173 | 0.004963 | 0.2244 | 122.3425 | -0.075722 | 122.6176 | 122.5236 | 0.18106 | 0.091562 | -0.14332 | 122.7145 | 122.6902 | 122.9096 | 122.6134 | -0.11798 | 122.6095 | 122.7768 | 122.5419 | 122.6673 | -0.3427
3909.3906 | 122.7722 | -122.6166 | 0.13733 | 1.4211e-13 | -0.017474 | -0.013932 | -0.045598 | -0.042139 | -0.012993 | -0.0084697 | 0.0092014 | 0.033309 | -0.027249 | 0.01379 | -0.019489 | -0.003531 | 0.015142 | -0.003831 | 0.12996 | 0.10567 | 0.32511 | -0.017268 | 0.019362 | 0.082776 | -0.074666 | 0.015831 | 0.18769 | -0.065507 | -0.24657 | 122.5993 | -0.007369 | 122.613 | 122.6127 | 0.013437 | -0.031655 | 0.18778 | 122.37 | -0.1215 | 122.6359 | 122.5419 | 0.1719 | 0.050364 | -0.20284 | 122.7465 | 122.7223 | 122.9417 | 122.6317 | -0.1546 | 122.6324 | 122.8043 | 122.5511 | 122.6994 | -0.3839
3911.1875 | 122.9141 | -122.6212 | 0.07782 | 1.4211e-13 | -0.01726 | -0.013932 | -0.04517 | -0.042352 | -0.012779 | -0.00083919 | 0.009415 | 0.033523 | -0.027035 | 0.01379 | -0.019489 | -0.008109 | 0.010564 | -0.008409 | 0.12538 | 0.10567 | 0.31137 | -0.026426 | 0.02852 | 0.082776 | -0.065509 | 0.020409 | 0.18311 | 0.003172 | -0.24657 | 122.5947 | 0.047562 | 122.613 | 122.6127 | 0.018017 | 0.027854 | 0.23355 | 122.3746 | -0.057411 | 122.6497 | 122.5556 | 0.18106 | 0.10529 | -0.074648 | 122.7465 | 122.7268 | 122.9325 | 122.6317 | -0.10425 | 122.6416 | 122.8043 | 122.6243 | 122.7039 | -0.32439
3912.9219 | 122.9187 | -122.58 | 0.073242 | 1.4211e-13 | -0.017474 | -0.013505 | -0.045384 | -0.042139 | -0.012993 | -0.00083919 | 0.0092014 | 0.033096 | -0.027035 | 0.013577 | -0.019276 | 0.005626 | 0.0243 | -0.003831 | 0.12538 | 0.1011 | 0.32969 | -0.026426 | 0.023941 | 0.073618 | -0.065509 | 0.020409 | 0.18769 | 0.021486 | -0.24657 | 122.5535 | 0.05214 | 122.5856 | 122.5761 | 0.022595 | 0.027853 | 0.25645 | 122.3334 | -0.052833 | 122.6039 | 122.5144 | 0.18106 | 0.11445 | -0.051756 | 122.7053 | 122.6811 | 122.9096 | 122.6043 | -0.099668 | 122.6004 | 122.7676 | 122.6014 | 122.6536 | -0.31981
3914.7188 | 122.8363 | -122.6395 | 0.12817 | 1.4211e-13 | -0.017047 | -0.013932 | -0.044957 | -0.042139 | -0.012565 | 0.0067908 | 0.0092014 | 0.033523 | -0.026821 | 0.01379 | -0.019703 | 0.001048 | 0.019721 | -0.003831 | 0.1208 | 0.1011 | 0.32053 | -0.058478 | 0.019362 | 0.078197 | -0.070087 | 0.015831 | 0.19227 | -0.001407 | -0.25115 | 122.581 | -0.00737 | 122.6405 | 122.6356 | 0.054647 | -0.027079 | 0.19236 | 122.3883 | -0.11234 | 122.6588 | 122.5694 | 0.18106 | 0.064098 | -0.12958 | 122.7603 | 122.7406 | 122.96 | 122.6592 | -0.18665 | 122.6553 | 122.8317 | 122.6381 | 122.7177 | -0.37932
3916.5156 | 122.9187 | -122.6303 | 0.09613 | 1.4211e-13 | -0.017047 | -0.013718 | -0.045384 | -0.042566 | -0.012779 | -0.00083919 | 0.0092014 | 0.033523 | -0.027035 | 0.01379 | -0.019489 | -0.003531 | 0.0243 | 0.000747 | 0.12538 | 0.1011 | 0.31595 | -0.031005 | 0.02852 | 0.078197 | -0.070087 | 0.015831 | 0.18311 | 0.039801 | -0.24657 | 122.5993 | 0.029252 | 122.6268 | 122.6311 | 0.031752 | 0.004965 | 0.21982 | 122.3837 | -0.080299 | 122.6588 | 122.5602 | 0.17648 | 0.086985 | -0.056329 | 122.7557 | 122.7314 | 122.9463 | 122.6546 | -0.12713 | 122.6461 | 122.8134 | 122.6701 | 122.7085 | -0.3427
3918.2344 | 122.7859 | -122.6486 | 0.13733 | 1.4211e-13 | -0.01726 | -0.013718 | -0.044957 | -0.041711 | -0.012993 | 0.0067908 | 0.0092014 | 0.033096 | -0.026821 | 0.013363 | -0.019703 | -0.003531 | 0.019721 | -0.003831 | 0.12538 | 0.096516 | 0.31595 | -0.017268 | 0.019362 | 0.082776 | -0.070087 | 0.015831 | 0.18311 | 0.003172 | -0.24657 | 122.6314 | -0.011947 | 122.6451 | 122.6448 | 0.013437 | -0.040813 | 0.17862 | 122.4021 | -0.1215 | 122.668 | 122.5785 | 0.17648 | 0.045786 | -0.13416 | 122.774 | 122.7451 | 122.9646 | 122.6683 | -0.1546 | 122.6645 | 122.8317 | 122.6518 | 122.7314 | -0.3839
3920.0156 | 122.8088 | -122.6486 | 0.12817 | 1.4211e-13 | -0.017047 | -0.013505 | -0.045384 | -0.042352 | -0.012993 | -0.00083919 | 0.0089876 | 0.033309 | -0.026608 | 0.01379 | -0.019489 | -0.003531 | 0.019721 | -0.008409 | 0.12538 | 0.1011 | 0.32053 | -0.012689 | 0.019362 | 0.078197 | -0.070087 | 0.015831 | 0.18769 | -0.038035 | -0.24199 | 122.6359 | -0.002792 | 122.6451 | 122.6402 | 0.00428 | -0.027079 | 0.19236 | 122.4066 | -0.11234 | 122.668 | 122.5785 | 0.1719 | 0.059519 | -0.16621 | 122.774 | 122.7497 | 122.9692 | 122.6683 | -0.14086 | 122.6645 | 122.8363 | 122.6106 | 122.7268 | -0.37016
3921.7969 | 122.9187 | -122.6257 | 0.086975 | 1.4211e-13 | -0.01726 | -0.014359 | -0.045384 | -0.042139 | -0.012993 | -0.00083919 | 0.0089876 | 0.033523 | -0.027035 | 0.01379 | -0.019703 | 0.001048 | 0.0243 | -0.003831 | 0.1208 | 0.11025 | 0.31137 | -0.031005 | 0.023941 | 0.082776 | -0.070087 | 0.020409 | 0.18769 | 0.021486 | -0.24657 | 122.5947 | 0.033829 | 122.6268 | 122.6219 | 0.027174 | 0.023278 | 0.2244 | 122.3792 | -0.066566 | 122.6497 | 122.5556 | 0.17648 | 0.10072 | -0.065489 | 122.7465 | 122.736 | 122.9371 | 122.65 | -0.11798 | 122.6461 | 122.8134 | 122.6472 | 122.7085 | -0.33354
3923.5781 | 122.8775 | -122.6349 | 0.091553 | 1.4211e-13 | -0.017047 | -0.013505 | -0.04517 | -0.042139 | -0.012565 | -0.00083919 | 0.0089876 | 0.033737 | -0.027249 | 0.013577 | -0.019489 | -0.003531 | 0.015142 | -0.008409 | 0.12996 | 0.1011 | 0.31595 | -0.017268 | 0.023941 | 0.078197 | -0.070087 | 0.020409 | 0.19227 | 0.035222 | -0.24657 | 122.6176 | 0.038407 | 122.6314 | 122.6265 | 0.008859 | 0.009542 | 0.2244 | 122.3883 | -0.071144 | 122.6588 | 122.5648 | 0.17648 | 0.10072 | -0.056331 | 122.7648 | 122.736 | 122.9508 | 122.65 | -0.10882 | 122.6553 | 122.8272 | 122.6701 | 122.7131 | -0.33812
3925.3125 | 122.937 | -122.6212 | 0.086975 | 1.4211e-13 | -0.01726 | -0.013932 | -0.045598 | -0.042566 | -0.012779 | -0.0084697 | 0.008774 | 0.033096 | -0.026608 | 0.01379 | -0.019489 | -0.003531 | 0.010564 | 0.000747 | 0.12538 | 0.1011 | 0.31137 | -0.063057 | 0.023941 | 0.073618 | -0.070087 | 0.015831 | 0.19685 | 0.012329 | -0.24657 | 122.5581 | 0.038407 | 122.6176 | 122.6219 | 0.063804 | 0.01412 | 0.2244 | 122.3746 | -0.071144 | 122.6451 | 122.5511 | 0.17648 | 0.10988 | -0.074646 | 122.7465 | 122.7223 | 122.9325 | 122.6317 | -0.15003 | 122.637 | 122.818 | 122.6335 | 122.6948 | -0.33354
3927.1094 | 122.818 | -122.6532 | 0.11902 | 1.4211e-13 | -0.01726 | -0.013932 | -0.044957 | -0.042139 | -0.012779 | -0.0084697 | 0.0089876 | 0.033737 | -0.027035 | 0.014004 | -0.019276 | -0.003531 | 0.015142 | 0.000747 | 0.11622 | 0.1011 | 0.32053 | -0.035584 | 0.023941 | 0.073618 | -0.070087 | 0.020409 | 0.19227 | -0.005985 | -0.24657 | 122.6176 | -0.002794 | 122.6497 | 122.6539 | 0.036331 | -0.017924 | 0.20151 | 122.4066 | -0.09861 | 122.6771 | 122.5831 | 0.17648 | 0.073253 | -0.125 | 122.7694 | 122.7543 | 122.9737 | 122.6683 | -0.1546 | 122.6736 | 122.8455 | 122.6472 | 122.7268 | -0.36559
3928.9062 | 122.8912 | -122.6578 | 0.10529 | 1.4211e-13 | -0.01726 | -0.013505 | -0.04517 | -0.042352 | -0.012993 | -0.00083919 | 0.0089876 | 0.033309 | -0.026821 | 0.013577 | -0.019489 | 0.005626 | 0.019721 | -0.008409 | 0.12996 | 0.10567 | 0.32511 | -0.003531 | 0.019362 | 0.078197 | -0.070087 | 0.015831 | 0.17854 | -0.065507 | -0.24199 | 122.6542 | 0.024674 | 122.6634 | 122.6494 | -0.004878 | 0.000388 | 0.21982 | 122.4158 | -0.089455 | 122.6771 | 122.5877 | 0.1719 | 0.07325 | -0.17079 | 122.7877 | 122.7634 | 122.9829 | 122.6775 | -0.10882 | 122.6736 | 122.8363 | 122.5923 | 122.736 | -0.34728
3930.7031 | 122.8271 | -122.6944 | 0.10986 | 1.4211e-13 | -0.017047 | -0.013505 | -0.045384 | -0.042139 | -0.012993 | 0.0067908 | 0.0092014 | 0.033096 | -0.027035 | 0.014004 | -0.019276 | -0.003531 | 0.015142 | -0.008409 | 0.1208 | 0.096516 | 0.31595 | -0.031005 | 0.023941 | 0.082776 | -0.074666 | 0.024988 | 0.17854 | 0.003172 | -0.24657 | 122.6634 | 0.010941 | 122.6909 | 122.686 | 0.022596 | -0.013347 | 0.20609 | 122.4478 | -0.084875 | 122.7183 | 122.6197 | 0.1719 | 0.068673 | -0.10669 | 122.8152 | 122.7909 | 123.0103 | 122.7095 | -0.14087 | 122.7194 | 122.8729 | 122.6976 | 122.7772 | -0.35643
3932.5 | 122.937 | -122.6074 | 0.068665 | 1.4211e-13 | -0.01726 | -0.013932 | -0.045384 | -0.042139 | -0.012779 | 0.0067908 | 0.0089876 | 0.033309 | -0.026821 | 0.013363 | -0.019489 | -0.003531 | 0.019721 | -0.008409 | 0.12996 | 0.1011 | 0.32053 | 0.005627 | 0.023941 | 0.078197 | -0.065509 | 0.015831 | 0.19685 | -0.010564 | -0.24657 | 122.613 | 0.061295 | 122.6039 | 122.599 | -0.014036 | 0.03243 | 0.25187 | 122.3609 | -0.052834 | 122.6314 | 122.5419 | 0.18106 | 0.12819 | -0.079229 | 122.7374 | 122.7085 | 122.928 | 122.6271 | -0.063038 | 122.6233 | 122.8043 | 122.5969 | 122.6856 | -0.31523
3934.2812 | 122.9507 | -122.6395 | 0.086975 | 1.4211e-13 | -0.01726 | -0.013932 | -0.04517 | -0.042352 | -0.012565 | -0.0084697 | 0.0092014 | 0.033523 | -0.027249 | 0.01379 | -0.019489 | -0.003531 | 0.015142 | -0.008409 | 0.12538 | 0.1011 | 0.32053 | -0.00811 | 0.023941 | 0.082776 | -0.070087 | 0.020409 | 0.18769 | -0.079243 | -0.24657 | 122.6314 | 0.038407 | 122.6359 | 122.6311 | -0.000299 | 0.01412 | 0.23356 | 122.3929 | -0.066566 | 122.6634 | 122.5694 | 0.17648 | 0.10072 | -0.16622 | 122.7648 | 122.7406 | 122.96 | 122.6546 | -0.095085 | 122.6599 | 122.8272 | 122.5602 | 122.7222 | -0.33354
3936.0156 | 122.9553 | -122.6028 | 0.10071 | 1.4211e-13 | -0.01726 | -0.013505 | -0.045384 | -0.042139 | -0.012565 | 0.014421 | 0.0092014 | 0.032882 | -0.027035 | 0.013577 | -0.019489 | 0.001048 | 0.015142 | -0.003831 | 0.12538 | 0.1011 | 0.31595 | 0.001048 | 0.023941 | 0.078197 | -0.070087 | 0.024988 | 0.19227 | -0.038035 | -0.25115 | 122.6039 | 0.024674 | 122.6039 | 122.599 | -0.004879 | 0.000387 | 0.21524 | 122.3517 | -0.07572 | 122.6268 | 122.5328 | 0.18106 | 0.091564 | -0.13874 | 122.7282 | 122.7039 | 122.9188 | 122.618 | -0.09966 | 122.6278 | 122.7951 | 122.5648 | 122.681 | -0.35185
3937.7969 | 122.9553 | -122.6166 | 0.091553 | 1.4211e-13 | -0.016833 | -0.013505 | -0.045598 | -0.042139 | -0.012993 | -0.00083919 | 0.0092014 | 0.033096 | -0.026821 | 0.013577 | -0.019276 | 0.001048 | 0.0243 | -0.008409 | 0.12996 | 0.096516 | 0.32511 | -0.00811 | 0.019362 | 0.078197 | -0.065509 | 0.020409 | 0.18769 | -0.015142 | -0.24199 | 122.6085 | 0.038407 | 122.6176 | 122.6082 | -0.000299 | 0.004963 | 0.23356 | 122.3746 | -0.071144 | 122.6359 | 122.5511 | 0.17648 | 0.09614 | -0.10669 | 122.7465 | 122.7131 | 122.9417 | 122.6409 | -0.099663 | 122.637 | 122.8043 | 122.6014 | 122.6948 | -0.33354
3939.5938 | 122.9553 | -122.6578 | 0.082397 | 1.4211e-13 | -0.017047 | -0.013718 | -0.04517 | -0.042139 | -0.013206 | 0.0067908 | 0.0089876 | 0.033309 | -0.027249 | 0.013577 | -0.019276 | 0.005626 | 0.0243 | -0.012988 | 0.12538 | 0.096516 | 0.32511 | 0.001048 | 0.023941 | 0.078197 | -0.070087 | 0.020409 | 0.18769 | 0.007751 | -0.24199 | 122.6588 | 0.042985 | 122.6634 | 122.6448 | -0.014036 | 0.014119 | 0.24271 | 122.4158 | -0.061988 | 122.6817 | 122.5877 | 0.1719 | 0.1053 | -0.074646 | 122.7832 | 122.7543 | 122.9829 | 122.6821 | -0.081349 | 122.6782 | 122.8455 | 122.6655 | 122.736 | -0.32439
3941.4062 | 122.7951 | -122.6944 | 0.10986 | 1.4211e-13 | -0.01726 | -0.013505 | -0.04517 | -0.042566 | -0.013206 | 0.0067908 | 0.009415 | 0.033523 | -0.027035 | 0.013363 | -0.019062 | -0.003531 | 0.019721 | -0.003831 | 0.1208 | 0.1011 | 0.31595 | 0.005627 | 0.023941 | 0.087354 | -0.070087 | 0.020409 | 0.18311 | 0.030644 | -0.24657 | 122.7 | 0.010941 | 122.6909 | 122.6906 | -0.009458 | -0.008768 | 0.20609 | 122.4478 | -0.089454 | 122.7183 | 122.6243 | 0.17648 | 0.073252 | -0.079219 | 122.8152 | 122.7955 | 123.0103 | 122.7141 | -0.10424 | 122.7148 | 122.8775 | 122.725 | 122.7818 | -0.35643
3943.125 | 122.8958 | -122.6578 | 0.086975 | 1.4211e-13 | -0.01726 | -0.013505 | -0.045384 | -0.042139 | -0.012565 | -0.0084697 | 0.0092014 | 0.033309 | -0.026821 | 0.01379 | -0.019703 | -0.003531 | 0.019721 | -0.003831 | 0.1208 | 0.096516 | 0.32053 | -0.021847 | 0.023941 | 0.087354 | -0.070087 | 0.011252 | 0.18311 | 0.030644 | -0.24657 | 122.6359 | 0.033829 | 122.6542 | 122.6539 | 0.018016 | 0.009541 | 0.23356 | 122.4112 | -0.075723 | 122.6817 | 122.5877 | 0.17648 | 0.09614 | -0.056331 | 122.7786 | 122.7543 | 122.9783 | 122.6775 | -0.10882 | 122.669 | 122.8409 | 122.6884 | 122.7451 | -0.33354
3944.9375 | 122.9507 | -122.644 | 0.086975 | 1.4211e-13 | -0.016833 | -0.013505 | -0.045598 | -0.042139 | -0.012779 | -0.00083919 | 0.009415 | 0.033309 | -0.026608 | 0.01379 | -0.019489 | 0.005626 | 0.010564 | 0.005325 | 0.12996 | 0.096516 | 0.31595 | -0.003531 | 0.02852 | 0.082776 | -0.074666 | 0.011252 | 0.19685 | 0.030644 | -0.24199 | 122.6405 | 0.042985 | 122.6497 | 122.6494 | 0.008856 | 0.009541 | 0.22898 | 122.4021 | -0.075723 | 122.6726 | 122.5694 | 0.16732 | 0.10988 | -0.056331 | 122.774 | 122.7406 | 122.96 | 122.6546 | -0.090506 | 122.6553 | 122.8409 | 122.6747 | 122.7268 | -0.32896
3946.7344 | 122.818 | -122.6898 | 0.1236 | 1.4211e-13 | -0.017047 | -0.013718 | -0.04517 | -0.041711 | -0.012993 | 0.0067908 | 0.0092014 | 0.033096 | -0.026821 | 0.013577 | -0.019276 | 0.010204 | 0.019721 | -0.003831 | 0.12996 | 0.096516 | 0.32053 | -0.026426 | 0.019362 | 0.082776 | -0.065509 | 0.020409 | 0.18311 | 0.044379 | -0.24657 | 122.6634 | 0.006364 | 122.7 | 122.686 | 0.022595 | -0.02708 | 0.19694 | 122.4433 | -0.10319 | 122.7092 | 122.6243 | 0.18106 | 0.059519 | -0.079217 | 122.8198 | 122.7863 | 123.0104 | 122.7095 | -0.15002 | 122.7102 | 122.8729 | 122.7342 | 122.7726 | -0.37016
3948.5312 | 122.8455 | -122.6898 | 0.10986 | 1.4211e-13 | -0.017474 | -0.013718 | -0.045384 | -0.042566 | -0.012779 | -0.0084697 | 0.009415 | 0.033523 | -0.026821 | 0.01379 | -0.019062 | 0.001048 | 0.019721 | -0.017566 | 0.12996 | 0.1011 | 0.32511 | -0.049321 | 0.023941 | 0.082776 | -0.074666 | 0.020409 | 0.19227 | 0.048958 | -0.24657 | 122.6405 | 0.020097 | 122.6909 | 122.6723 | 0.031755 | -0.008768 | 0.21525 | 122.4433 | -0.089454 | 122.7138 | 122.6152 | 0.1719 | 0.082409 | -0.060905 | 122.8198 | 122.7909 | 123.0149 | 122.7095 | -0.15918 | 122.7102 | 122.8821 | 122.7388 | 122.7726 | -0.35643
3950.2656 | 122.8592 | -122.6852 | 0.10071 | 1.4211e-13 | -0.017047 | -0.013291 | -0.04517 | -0.042352 | -0.012779 | -0.00083919 | 0.0096286 | 0.033309 | -0.026394 | 0.013577 | -0.019489 | 0.001048 | 0.019721 | -0.012988 | 0.12996 | 0.091937 | 0.31595 | -0.00811 | 0.014784 | 0.073618 | -0.065509 | 0.015831 | 0.18311 | 0.016908 | -0.24199 | 122.6771 | 0.029252 | 122.6863 | 122.6723 | -0.004878 | -0.008771 | 0.21524 | 122.4433 | -0.084877 | 122.7 | 122.6197 | 0.17648 | 0.082407 | -0.0838 | 122.8152 | 122.7772 | 123.0012 | 122.705 | -0.10882 | 122.7011 | 122.8684 | 122.7022 | 122.7589 | -0.3427
3952.0625 | 122.9187 | -122.6624 | 0.07782 | 1.4211e-13 | -0.01726 | -0.013291 | -0.04517 | -0.042139 | -0.013206 | -0.00083919 | 0.0089876 | 0.033309 | -0.026608 | 0.01379 | -0.019489 | 0.001048 | 0.019721 | -0.012988 | 0.1208 | 0.1011 | 0.32053 | -0.026426 | 0.023941 | 0.078197 | -0.070087 | 0.020409 | 0.18311 | 0.012329 | -0.24657 | 122.6359 | 0.042984 | 122.6634 | 122.6494 | 0.013438 | 0.023275 | 0.24271 | 122.4158 | -0.057411 | 122.6863 | 122.5923 | 0.17648 | 0.10529 | -0.065491 | 122.7832 | 122.7634 | 122.9829 | 122.6821 | -0.10425 | 122.6828 | 122.8455 | 122.6747 | 122.7406 | -0.32439
3953.7969 | 122.9187 | -122.6486 | 0.10071 | 1.4211e-13 | -0.017474 | -0.013291 | -0.045598 | -0.042139 | -0.012779 | 0.014421 | 0.009415 | 0.033309 | -0.026821 | 0.01379 | -0.019703 | 0.005626 | 0.0243 | -0.012988 | 0.12538 | 0.1011 | 0.31595 | -0.026426 | 0.019362 | 0.082776 | -0.070087 | 0.015831 | 0.19227 | 0.026065 | -0.24657 | 122.6222 | 0.024674 | 122.6542 | 122.6356 | 0.013438 | 0.000387 | 0.21524 | 122.4021 | -0.084877 | 122.668 | 122.5785 | 0.17648 | 0.091564 | -0.074643 | 122.774 | 122.7497 | 122.9646 | 122.6729 | -0.12713 | 122.6645 | 122.8409 | 122.6747 | 122.7314 | -0.34728
3955.5781 | 122.9233 | -122.6532 | 0.07782 | 1.4211e-13 | -0.017474 | -0.012863 | -0.045384 | -0.041925 | -0.012779 | -0.00083919 | 0.0092014 | 0.033309 | -0.027035 | 0.013577 | -0.019703 | -0.003531 | 0.019721 | -0.008409 | 0.1208 | 0.1011 | 0.32969 | -0.035584 | 0.023941 | 0.082776 | -0.070087 | 0.015831 | 0.19227 | 0.003172 | -0.24657 | 122.6176 | 0.042984 | 122.6497 | 122.6448 | 0.027175 | 0.023275 | 0.25187 | 122.4066 | -0.061989 | 122.6771 | 122.5831 | 0.17648 | 0.11445 | -0.074648 | 122.774 | 122.7543 | 122.9829 | 122.6729 | -0.1134 | 122.669 | 122.8455 | 122.6564 | 122.736 | -0.32439
3957.375 | 122.9187 | -122.6532 | 0.10986 | 1.4211e-13 | -0.017474 | -0.013718 | -0.045598 | -0.042139 | -0.012779 | 0.0067908 | 0.0092014 | 0.033309 | -0.027249 | 0.013363 | -0.019703 | 0.001048 | 0.019721 | -0.003831 | 0.11622 | 0.096516 | 0.32053 | -0.003531 | 0.02852 | 0.078197 | -0.065509 | 0.029566 | 0.18769 | 0.012329 | -0.24199 | 122.6497 | 0.006362 | 122.6542 | 122.6494 | -0.0003 | -0.013347 | 0.21067 | 122.4112 | -0.080297 | 122.6817 | 122.5877 | 0.17648 | 0.07783 | -0.097534 | 122.7694 | 122.7497 | 122.9737 | 122.6729 | -0.11339 | 122.6828 | 122.8409 | 122.6655 | 122.7314 | -0.35185
3959.1094 | 122.9553 | -122.6532 | 0.10071 | 1.4211e-13 | -0.01726 | -0.013505 | -0.045811 | -0.042352 | -0.012993 | -0.0084697 | 0.0089876 | 0.033523 | -0.027035 | 0.013577 | -0.019489 | 0.005626 | 0.019721 | -0.003831 | 0.1208 | 0.096516 | 0.31137 | -0.031005 | 0.019362 | 0.073618 | -0.070087 | 0.020409 | 0.19685 | 0.016908 | -0.24657 | 122.6222 | 0.020096 | 122.6588 | 122.6494 | 0.027174 | -0.004192 | 0.21067 | 122.4066 | -0.080299 | 122.6726 | 122.5831 | 0.17648 | 0.096143 | -0.0838 | 122.774 | 122.7497 | 122.9646 | 122.6729 | -0.13171 | 122.6736 | 122.85 | 122.6701 | 122.7268 | -0.34728
3960.9062 | 122.8271 | -122.6852 | 0.13275 | 1.4211e-13 | -0.017474 | -0.013077 | -0.045384 | -0.042352 | -0.012779 | -0.0084697 | 0.009415 | 0.033309 | -0.027035 | 0.01379 | -0.019276 | -0.008109 | 0.019721 | -0.012988 | 0.12538 | 0.096516 | 0.32053 | -0.017268 | 0.023941 | 0.082776 | -0.074666 | 0.015831 | 0.18769 | 0.021486 | -0.25115 | 122.668 | -0.007369 | 122.6771 | 122.6723 | 0.00428 | -0.036235 | 0.18778 | 122.4341 | -0.11692 | 122.7092 | 122.6106 | 0.17648 | 0.054942 | -0.11127 | 122.8106 | 122.7818 | 123.0058 | 122.705 | -0.15002 | 122.7011 | 122.8729 | 122.7067 | 122.768 | -0.3839
3962.7031 | 122.9782 | -122.6486 | 0.073242 | 1.4211e-13 | -0.017047 | -0.013718 | -0.044957 | -0.042139 | -0.012565 | -0.00083919 | 0.009415 | 0.032882 | -0.027035 | 0.013577 | -0.019489 | 0.001048 | 0.019721 | -0.008409 | 0.12538 | 0.1011 | 0.31595 | -0.012689 | 0.02852 | 0.078197 | -0.074666 | 0.011252 | 0.18769 | 0.016908 | -0.24657 | 122.6359 | 0.05214 | 122.6497 | 122.6402 | 0.00428 | 0.027853 | 0.24271 | 122.4021 | -0.06199 | 122.6771 | 122.574 | 0.1719 | 0.11445 | -0.056334 | 122.774 | 122.7497 | 122.9646 | 122.6683 | -0.085931 | 122.6599 | 122.8363 | 122.6655 | 122.7268 | -0.31981
3964.5 | 122.937 | -122.6761 | 0.09613 | 1.4211e-13 | -0.01726 | -0.013505 | -0.04517 | -0.042139 | -0.012779 | 0.0067908 | 0.0089876 | 0.033523 | -0.026821 | 0.013577 | -0.019703 | -0.003531 | 0.019721 | -0.008409 | 0.12538 | 0.091937 | 0.32511 | -0.00811 | 0.02852 | 0.078197 | -0.065509 | 0.024988 | 0.18311 | 0.039801 | -0.24657 | 122.668 | 0.029252 | 122.6726 | 122.6677 | -0.000299 | -0.004193 | 0.22898 | 122.4295 | -0.071142 | 122.7046 | 122.6106 | 0.18106 | 0.086985 | -0.056329 | 122.8015 | 122.768 | 123.0012 | 122.6958 | -0.10424 | 122.7011 | 122.8592 | 122.7159 | 122.7543 | -0.3427
3966.3125 | 122.8409 | -122.6944 | 0.11444 | 1.4211e-13 | -0.016833 | -0.013718 | -0.04517 | -0.041925 | -0.012779 | -0.00083919 | 0.0092014 | 0.033096 | -0.026608 | 0.01379 | -0.019276 | 0.001048 | 0.015142 | -0.008409 | 0.12538 | 0.1011 | 0.31595 | -0.012689 | 0.019362 | 0.073618 | -0.070087 | 0.015831 | 0.18769 | -0.060928 | -0.24657 | 122.6817 | 0.010941 | 122.6954 | 122.686 | 0.00428 | -0.013346 | 0.20151 | 122.4478 | -0.09861 | 122.7138 | 122.6243 | 0.17648 | 0.073252 | -0.17537 | 122.8198 | 122.7955 | 123.0103 | 122.7095 | -0.12713 | 122.7102 | 122.8821 | 122.6335 | 122.768 | -0.36101
3968.0469 | 122.8409 | -122.7127 | 0.14191 | 1.4211e-13 | -0.017047 | -0.013505 | -0.04517 | -0.042139 | -0.012352 | 0.0067908 | 0.0092014 | 0.033523 | -0.027035 | 0.014004 | -0.019917 | 0.001048 | 0.0243 | -0.017566 | 0.12996 | 0.1011 | 0.32053 | 0.005627 | 0.023941 | 0.078197 | -0.065509 | 0.015831 | 0.18311 | -0.05635 | -0.24199 | 122.7183 | -0.011947 | 122.7138 | 122.6951 | -0.023193 | -0.040812 | 0.17862 | 122.4707 | -0.12608 | 122.7366 | 122.6472 | 0.17648 | 0.041208 | -0.19826 | 122.8427 | 122.8138 | 123.0332 | 122.737 | -0.13628 | 122.7285 | 122.8958 | 122.6564 | 122.7909 | -0.3839
3969.8438 | 122.8592 | -122.7264 | 0.13733 | 1.4211e-13 | -0.017047 | -0.013505 | -0.045384 | -0.042352 | -0.012993 | 0.0067908 | 0.0089876 | 0.033096 | -0.026608 | 0.013577 | -0.019489 | -0.008109 | 0.015142 | -0.012988 | 0.12538 | 0.1011 | 0.31137 | -0.00811 | 0.023941 | 0.078197 | -0.070087 | 0.015831 | 0.17396 | -0.079243 | -0.24199 | 122.7183 | -0.011947 | 122.7183 | 122.7135 | -0.004878 | -0.036234 | 0.17404 | 122.4845 | -0.1215 | 122.7504 | 122.6564 | 0.1719 | 0.036629 | -0.21657 | 122.8518 | 122.8275 | 123.0378 | 122.7416 | -0.14544 | 122.7423 | 122.9004 | 122.6472 | 122.8046 | -0.37932
3971.6406 | 122.9691 | -122.6669 | 0.082397 | 1.4211e-13 | -0.017047 | -0.013505 | -0.045384 | -0.041925 | -0.012779 | -0.0084697 | 0.0092014 | 0.033309 | -0.027035 | 0.014004 | -0.019276 | 0.001048 | 0.019721 | -0.017566 | 0.12996 | 0.10567 | 0.31595 | -0.026426 | 0.019362 | 0.078197 | -0.070087 | 0.015831 | 0.18311 | -0.038035 | -0.25115 | 122.6405 | 0.047563 | 122.668 | 122.6494 | 0.00886 | 0.023277 | 0.23356 | 122.4158 | -0.066566 | 122.6863 | 122.5968 | 0.18106 | 0.10072 | -0.12043 | 122.7969 | 122.7726 | 122.9829 | 122.6867 | -0.10882 | 122.6828 | 122.85 | 122.6289 | 122.7451 | -0.33354
3973.4375 | 122.9553 | -122.6944 | 0.09613 | 1.4211e-13 | -0.01726 | -0.013718 | -0.045384 | -0.042139 | -0.012779 | -0.0084697 | 0.009415 | 0.033523 | -0.026821 | 0.01379 | -0.019276 | 0.001048 | 0.015142 | -0.022144 | 0.1208 | 0.1011 | 0.32053 | -0.035584 | 0.023941 | 0.073618 | -0.065509 | 0.015831 | 0.18311 | -0.028878 | -0.24199 | 122.6588 | 0.024674 | 122.6954 | 122.6723 | 0.01344 | 0.004965 | 0.2244 | 122.4524 | -0.080299 | 122.7183 | 122.6289 | 0.17648 | 0.086985 | -0.12501 | 122.8152 | 122.7955 | 123.0149 | 122.7095 | -0.13171 | 122.7102 | 122.8775 | 122.6655 | 122.768 | -0.33812
3975.2344 | 122.8592 | -122.699 | 0.10529 | 1.4211e-13 | -0.017688 | -0.013932 | -0.045384 | -0.041925 | -0.012565 | 0.0067908 | 0.0092014 | 0.033096 | -0.026821 | 0.01379 | -0.019276 | 0.005626 | 0.019721 | -0.017566 | 0.12538 | 0.1011 | 0.32053 | -0.017268 | 0.023941 | 0.078197 | -0.065509 | 0.024988 | 0.18311 | -0.019721 | -0.24657 | 122.6817 | 0.020096 | 122.7046 | 122.6814 | -0.000298 | -0.004191 | 0.21525 | 122.4524 | -0.080298 | 122.7229 | 122.6335 | 0.18106 | 0.077829 | -0.12501 | 122.8244 | 122.8001 | 123.0195 | 122.7187 | -0.12255 | 122.724 | 122.8821 | 122.6793 | 122.7772 | -0.35185
3976.9688 | 122.8958 | -122.6669 | 0.1236 | 1.4211e-13 | -0.0059359 | -0.021411 | -0.049017 | -0.042139 | 0.043414 | 0.0067908 | 0.009415 | 0.032882 | -0.027035 | 0.013577 | -0.019489 | -0.012688 | -0.021486 | -0.045036 | 0.093333 | 0.073622 | 0.29306 | -0.17753 | 0.023941 | 0.073618 | -0.070087 | 0.015831 | 0.18311 | -0.060928 | -0.24657 | 122.4894 | -0.030263 | 122.6542 | 122.6219 | 0.13249 | -0.049974 | 0.16946 | 122.4204 | -0.10776 | 122.6909 | 122.5968 | 0.17648 | 0.059519 | -0.18452 | 122.7603 | 122.7406 | 122.96 | 122.6454 | -0.30113 | 122.6828 | 122.85 | 122.606 | 122.7405 | -0.37016
3978.75 | 122.8592 | -122.7081 | 0.11444 | 1.4211e-13 | -0.016406 | -0.013505 | -0.04517 | -0.042139 | -0.012565 | -0.0084697 | 0.009415 | 0.033523 | -0.026821 | 0.01379 | -0.019489 | -0.003531 | 0.019721 | -0.008409 | 0.1208 | 0.1011 | 0.31595 | 0.001048 | 0.023941 | 0.078197 | -0.070087 | 0.020409 | 0.18769 | -0.042614 | -0.24199 | 122.7092 | 0.006363 | 122.7046 | 122.6997 | -0.009457 | -0.013346 | 0.20151 | 122.4661 | -0.094032 | 122.7321 | 122.638 | 0.1719 | 0.073252 | -0.15706 | 122.8289 | 122.8092 | 123.0241 | 122.7279 | -0.11339 | 122.7285 | 122.8958 | 122.6655 | 122.7863 | -0.35643
3980.5625 | 122.9965 | -122.6715 | 0.07782 | 1.4211e-13 | -0.017047 | -0.013505 | -0.045384 | -0.042139 | -0.012779 | 0.0067908 | 0.008774 | 0.033096 | -0.027035 | 0.01379 | -0.019276 | -0.003531 | 0.015142 | -0.022144 | 0.1208 | 0.1011 | 0.32511 | -0.021847 | 0.019362 | 0.073618 | -0.070087 | 0.015831 | 0.18311 | -0.051771 | -0.24199 | 122.6497 | 0.042984 | 122.668 | 122.6494 | -0.000297 | 0.023275 | 0.24729 | 122.4295 | -0.061989 | 122.6909 | 122.6014 | 0.1719 | 0.10529 | -0.12959 | 122.7923 | 122.7726 | 122.9966 | 122.6867 | -0.099667 | 122.6873 | 122.8546 | 122.6197 | 122.7451 | -0.31981
3982.2812 | 122.8912 | -122.7127 | 0.10986 | 1.4211e-13 | -0.016833 | -0.013077 | -0.045384 | -0.041925 | -0.012779 | 0.0067908 | 0.0092014 | 0.033523 | -0.027035 | 0.013577 | -0.019062 | 0.001048 | 0.019721 | -0.012988 | 0.12538 | 0.10567 | 0.31595 | -0.044742 | 0.02852 | 0.06904 | -0.074666 | 0.020409 | 0.18311 | -0.001407 | -0.25115 | 122.668 | 0.015519 | 122.7138 | 122.6997 | 0.031754 | -0.004189 | 0.20609 | 122.4616 | -0.089454 | 122.7412 | 122.638 | 0.17648 | 0.073252 | -0.11127 | 122.8381 | 122.8184 | 123.0287 | 122.7324 | -0.1546 | 122.7331 | 122.8958 | 122.7113 | 122.7817 | -0.36101
3984.0781 | 122.9782 | -122.6349 | 0.086975 | 1.4211e-13 | -0.017047 | -0.013718 | -0.045384 | -0.042139 | -0.012352 | -0.0084697 | 0.011979 | 0.032455 | -0.028317 | 0.013577 | 0.038411 | -0.003531 | 0.010564 | -0.012988 | 0.1208 | 0.1011 | 0.31595 | -0.044742 | 0.019362 | 0.055303 | -0.065509 | 0.006674 | 0.16938 | -0.047193 | -0.27862 | 122.5901 | 0.033829 | 122.6314 | 122.6219 | 0.031754 | 0.01412 | 0.22898 | 122.3563 | -0.080301 | 122.6543 | 122.5694 | 0.21311 | 0.082404 | -0.13417 | 122.7557 | 122.736 | 122.9508 | 122.6455 | -0.13172 | 122.6416 | 122.8043 | 122.5877 | 122.6902 | -0.36559
3985.875 | 122.9874 | -122.6669 | 0.086975 | 1.4211e-13 | -0.016833 | -0.013718 | -0.045384 | -0.042139 | -0.012779 | -0.0084697 | 0.0092014 | 0.033309 | -0.027035 | 0.013363 | -0.019062 | -0.008109 | 0.019721 | -0.026723 | 0.1208 | 0.096516 | 0.32053 | -0.031005 | 0.023941 | 0.073618 | -0.065509 | 0.020409 | 0.18311 | 0.007751 | -0.24657 | 122.6359 | 0.033829 | 122.6588 | 122.6402 | 0.004282 | 0.009541 | 0.23356 | 122.4204 | -0.066566 | 122.6909 | 122.6014 | 0.18106 | 0.09614 | -0.079224 | 122.7877 | 122.7634 | 122.9875 | 122.6867 | -0.11798 | 122.6873 | 122.85 | 122.6747 | 122.7405 | -0.33354
3987.6719 | 122.9782 | -122.6807 | 0.091553 | 1.4211e-13 | -0.017047 | -0.013932 | -0.045384 | -0.041711 | -0.012779 | -0.00083919 | 0.0092014 | 0.033096 | -0.027035 | 0.01379 | -0.019276 | -0.008109 | 0.019721 | -0.017566 | 0.12538 | 0.1011 | 0.31595 | -0.012689 | 0.023941 | 0.078197 | -0.06093 | 0.024988 | 0.17854 | 0.026065 | -0.25115 | 122.668 | 0.033829 | 122.6726 | 122.6631 | -0.004877 | 0.009542 | 0.2244 | 122.4295 | -0.066565 | 122.7046 | 122.6197 | 0.19022 | 0.086983 | -0.065488 | 122.806 | 122.7818 | 122.9966 | 122.7004 | -0.10424 | 122.7057 | 122.8592 | 122.7067 | 122.7589 | -0.3427
3989.4688 | 122.8638 | -122.7219 | 0.10529 | 1.4211e-13 | -0.016833 | -0.013291 | -0.045598 | -0.042139 | -0.012565 | -0.0084697 | 0.0092014 | 0.033309 | -0.027035 | 0.014004 | -0.019489 | -0.008109 | 0.019721 | -0.026723 | 0.12996 | 0.10567 | 0.32511 | -0.021847 | 0.02852 | 0.082776 | -0.065509 | 0.024988 | 0.17854 | -0.042614 | -0.24657 | 122.7 | 0.024674 | 122.7138 | 122.6951 | -0.004876 | 0.000388 | 0.21982 | 122.4753 | -0.080298 | 122.7504 | 122.6564 | 0.18106 | 0.07325 | -0.1479 | 122.8518 | 122.8275 | 123.047 | 122.7416 | -0.12713 | 122.7469 | 122.9004 | 122.6792 | 122.8046 | -0.35185
3991.2656 | 122.9645 | -122.6852 | 0.091553 | 1.4211e-13 | -0.01726 | -0.013505 | -0.04517 | -0.042352 | -0.013206 | -0.0084697 | 0.0092014 | 0.033309 | -0.026821 | 0.01379 | -0.019276 | -0.003531 | 0.0243 | -0.017566 | 0.1208 | 0.096516 | 0.32511 | -0.035584 | 0.023941 | 0.078197 | -0.070087 | 0.011252 | 0.18769 | 0.021486 | -0.24199 | 122.6497 | 0.029251 | 122.6817 | 122.6677 | 0.018018 | 0.004963 | 0.23356 | 122.4433 | -0.080301 | 122.7092 | 122.6152 | 0.1719 | 0.09614 | -0.070067 | 122.806 | 122.7818 | 123.0104 | 122.7095 | -0.12714 | 122.6965 | 122.8729 | 122.7067 | 122.7634 | -0.33354
3993.0156 | 122.9507 | -122.7173 | 0.10071 | 1.4211e-13 | -0.01726 | -0.013505 | -0.04517 | -0.042352 | -0.012565 | -0.0084697 | 0.0089876 | 0.033096 | -0.027035 | 0.01379 | -0.019703 | -0.003531 | 0.019721 | -0.017566 | 0.12538 | 0.11025 | 0.31595 | -0.031005 | 0.023941 | 0.078197 | -0.070087 | 0.020409 | 0.18311 | -0.0243 | -0.25115 | 122.6863 | 0.024674 | 122.7138 | 122.6997 | 0.013439 | 0.009545 | 0.21524 | 122.4661 | -0.080299 | 122.7412 | 122.6472 | 0.18106 | 0.082407 | -0.12501 | 122.8427 | 122.8275 | 123.0332 | 122.737 | -0.13171 | 122.7377 | 122.9004 | 122.693 | 122.7955 | -0.35185
3994.8125 | 122.8821 | -122.7127 | 0.11444 | 1.4211e-13 | -0.017047 | -0.013291 | -0.04517 | -0.042352 | -0.012779 | -0.0084697 | 0.0092014 | 0.033309 | -0.026821 | 0.013577 | -0.019062 | 0.005626 | 0.005985 | -0.017566 | 0.12538 | 0.1011 | 0.31595 | -0.021847 | 0.019362 | 0.078197 | -0.070087 | 0.015831 | 0.17854 | 0.003172 | -0.24657 | 122.6909 | 0.010941 | 122.7183 | 122.6951 | 0.004281 | -0.013346 | 0.20151 | 122.4661 | -0.09861 | 122.7321 | 122.6426 | 0.17648 | 0.064095 | -0.11127 | 122.8381 | 122.8138 | 123.0287 | 122.7187 | -0.13629 | 122.7285 | 122.8912 | 122.7159 | 122.7909 | -0.36101
3996.5625 | 122.8455 | -122.7493 | 0.10986 | 1.4211e-13 | -0.016833 | -0.013505 | -0.045598 | -0.041925 | -0.012779 | 0.0067908 | 0.009415 | 0.033523 | -0.026821 | 0.014004 | -0.019489 | 0.001048 | 0.0243 | -0.017566 | 0.1208 | 0.1011 | 0.31595 | -0.012689 | 0.02852 | 0.082776 | -0.070087 | 0.011252 | 0.18769 | -0.010564 | -0.24199 | 122.7366 | 0.010941 | 122.7504 | 122.7318 | -0.004877 | -0.008768 | 0.20609 | 122.5073 | -0.098611 | 122.7778 | 122.6792 | 0.1719 | 0.07783 | -0.12043 | 122.8701 | 122.8504 | 123.0653 | 122.7736 | -0.12255 | 122.7606 | 122.937 | 122.7388 | 122.8321 | -0.35185
3998.3438 | 122.8821 | -122.7448 | 0.11902 | 1.4211e-13 | -0.01726 | -0.013291 | -0.045598 | -0.04278 | -0.012779 | -0.0084697 | 0.0092014 | 0.033309 | -0.026608 | 0.01379 | -0.019276 | -0.003531 | 0.019721 | -0.017566 | 0.1208 | 0.096516 | 0.31595 | -0.063057 | 0.023941 | 0.078197 | -0.070087 | 0.015831 | 0.17854 | 0.053537 | -0.24199 | 122.6817 | 0.001785 | 122.7412 | 122.7272 | 0.045491 | -0.022503 | 0.19693 | 122.5028 | -0.10319 | 122.7687 | 122.6747 | 0.1719 | 0.059517 | -0.065482 | 122.8656 | 122.8413 | 123.0607 | 122.7645 | -0.18208 | 122.7606 | 122.9233 | 122.7983 | 122.8229 | -0.36101
4000.125 | 122.9691 | -122.7036 | 0.09613 | 1.4211e-13 | -0.017474 | -0.013291 | -0.04517 | -0.042139 | -0.012993 | 0.014421 | 0.0089876 | 0.033309 | -0.026821 | 0.013577 | -0.019489 | 0.001048 | 0.015142 | -0.017566 | 0.12996 | 0.096516 | 0.32053 | -0.00811 | 0.023941 | 0.082776 | -0.074666 | 0.015831 | 0.18769 | 0.030644 | -0.23741 | 122.6954 | 0.03383 | 122.7046 | 122.686 | -0.009456 | 0.000386 | 0.2244 | 122.4661 | -0.080299 | 122.7275 | 122.6289 | 0.16274 | 0.091563 | -0.065486 | 122.8335 | 122.8001 | 123.0241 | 122.7187 | -0.10424 | 122.7194 | 122.8912 | 122.7342 | 122.7863 | -0.33354
4001.8594 | 122.905 | -122.7173 | 0.13275 | 1.4211e-13 | -0.017474 | -0.013291 | -0.045598 | -0.042139 | -0.012779 | -0.0084697 | 0.009415 | 0.033523 | -0.026821 | 0.01379 | -0.019489 | 0.001048 | 0.019721 | -0.026723 | 0.12538 | 0.1011 | 0.32511 | -0.031005 | 0.019362 | 0.078197 | -0.079245 | 0.020409 | 0.18311 | -0.005985 | -0.24657 | 122.6863 | -0.007369 | 122.7183 | 122.6906 | 0.004282 | -0.031656 | 0.19236 | 122.4707 | -0.11234 | 122.7366 | 122.638 | 0.16732 | 0.050364 | -0.13874 | 122.8427 | 122.8184 | 123.0424 | 122.737 | -0.16376 | 122.7377 | 122.9004 | 122.7113 | 122.7955 | -0.37932
4003.6406 | 122.9874 | -122.6852 | 0.086975 | 1.4211e-13 | -0.017474 | -0.013077 | -0.045384 | -0.041925 | -0.012779 | 0.0067908 | 0.0092014 | 0.033523 | -0.026821 | 0.013577 | -0.019703 | 0.001048 | 0.015142 | -0.026723 | 0.1208 | 0.1011 | 0.32511 | -0.031005 | 0.023941 | 0.082776 | -0.070087 | 0.015831 | 0.18311 | -0.001407 | -0.24199 | 122.6542 | 0.033829 | 122.6863 | 122.6585 | 0.004282 | 0.01412 | 0.23814 | 122.4433 | -0.071144 | 122.7092 | 122.6152 | 0.1719 | 0.09614 | -0.088382 | 122.806 | 122.7863 | 123.0104 | 122.7004 | -0.11798 | 122.7011 | 122.8684 | 122.6838 | 122.768 | -0.32896
4005.4375 | 122.9462 | -122.7127 | 0.11444 | 1.4211e-13 | -0.01726 | -0.013291 | -0.04517 | -0.041925 | -0.012779 | 0.0067908 | 0.0092014 | 0.033309 | -0.026821 | 0.014004 | -0.019703 | 0.005626 | 0.019721 | -0.022144 | 0.12538 | 0.1011 | 0.31595 | -0.012689 | 0.02852 | 0.078197 | -0.074666 | 0.015831 | 0.17854 | -0.005985 | -0.25115 | 122.7 | 0.010941 | 122.7183 | 122.6906 | -0.009455 | -0.013346 | 0.20151 | 122.4616 | -0.09861 | 122.7412 | 122.638 | 0.17648 | 0.064095 | -0.12043 | 122.8381 | 122.8138 | 123.0287 | 122.7324 | -0.12713 | 122.7285 | 122.8912 | 122.7067 | 122.7909 | -0.36559
4007.2344 | 122.9141 | -122.7219 | 0.13275 | 1.4211e-13 | -0.017688 | -0.013077 | -0.045384 | -0.041925 | -0.013206 | -0.00083919 | 0.0092014 | 0.033096 | -0.027035 | 0.01379 | -0.019489 | -0.008109 | 0.019721 | -0.017566 | 0.12538 | 0.1011 | 0.31595 | -0.00811 | 0.023941 | 0.073618 | -0.065509 | 0.015831 | 0.17396 | -0.0884 | -0.24199 | 122.7138 | -0.007369 | 122.7138 | 122.7043 | -0.009456 | -0.031656 | 0.1832 | 122.4799 | -0.11692 | 122.7458 | 122.6564 | 0.17648 | 0.041207 | -0.22115 | 122.8472 | 122.823 | 123.0378 | 122.7416 | -0.14086 | 122.7377 | 122.8958 | 122.6335 | 122.7955 | -0.37474
4008.9688 | 122.9416 | -122.7081 | 0.11902 | 1.4211e-13 | -0.01726 | -0.013077 | -0.045384 | -0.042139 | -0.012993 | -0.00083919 | 0.0089876 | 0.033096 | -0.027035 | 0.01379 | -0.019276 | 0.005626 | 0.019721 | -0.022144 | 0.1208 | 0.1011 | 0.31595 | -0.00811 | 0.019362 | 0.073618 | -0.074666 | 0.020409 | 0.18769 | -0.005985 | -0.24199 | 122.7 | 0.001785 | 122.7138 | 122.686 | -0.014034 | -0.017924 | 0.19693 | 122.4661 | -0.09861 | 122.7275 | 122.6335 | 0.16732 | 0.068674 | -0.125 | 122.8289 | 122.8092 | 123.0241 | 122.7279 | -0.12713 | 122.7285 | 122.8958 | 122.7021 | 122.7817 | -0.36101
4010.7656 | 122.8912 | -122.7219 | 0.11902 | 1.4211e-13 | -0.01726 | -0.012863 | -0.045598 | -0.041925 | -0.012779 | -0.00083919 | 0.009415 | 0.033309 | -0.027035 | 0.014004 | -0.019703 | -0.003531 | 0.015142 | -0.022144 | 0.12538 | 0.1011 | 0.31595 | -0.026426 | 0.02852 | 0.078197 | -0.065509 | 0.015831 | 0.18311 | -0.015142 | -0.24657 | 122.6954 | 0.006363 | 122.7183 | 122.6997 | 0.004282 | -0.017924 | 0.19693 | 122.4753 | -0.10319 | 122.7504 | 122.6564 | 0.18106 | 0.064096 | -0.13416 | 122.8472 | 122.823 | 123.0378 | 122.737 | -0.14544 | 122.7377 | 122.905 | 122.7067 | 122.8001 | -0.36559
4012.5781 | 122.9782 | -122.7402 | 0.10529 | 1.4211e-13 | -0.017474 | -0.013291 | -0.045384 | -0.042139 | -0.012779 | 0.0067908 | 0.009415 | 0.033309 | -0.026821 | 0.01379 | -0.019489 | 0.001048 | 0.019721 | -0.012988 | 0.12538 | 0.1011 | 0.31595 | -0.026426 | 0.02852 | 0.078197 | -0.079245 | 0.020409 | 0.17854 | 0.039801 | -0.24657 | 122.7137 | 0.020096 | 122.7412 | 122.7272 | 0.013438 | -0.004191 | 0.21067 | 122.4936 | -0.084877 | 122.7687 | 122.6609 | 0.16732 | 0.07325 | -0.065485 | 122.8656 | 122.8413 | 123.0561 | 122.7599 | -0.13171 | 122.7606 | 122.9187 | 122.78 | 122.8184 | -0.35185
4014.3125 | 122.8867 | -122.7539 | 0.13275 | 1.4211e-13 | -0.017474 | -0.012863 | -0.045384 | -0.042139 | -0.012779 | 0.0067908 | 0.0092014 | 0.033309 | -0.026394 | 0.01379 | -0.019703 | -0.003531 | 0.010564 | -0.022144 | 0.12538 | 0.1011 | 0.31595 | -0.058478 | 0.02852 | 0.073618 | -0.070087 | 0.020409 | 0.18311 | -0.001407 | -0.24199 | 122.6954 | -0.007369 | 122.7504 | 122.7318 | 0.036334 | -0.031656 | 0.1832 | 122.5119 | -0.11234 | 122.7824 | 122.6838 | 0.1719 | 0.050364 | -0.13416 | 122.8793 | 122.855 | 123.0699 | 122.7645 | -0.19123 | 122.7743 | 122.937 | 122.7525 | 122.8275 | -0.37474
4016.1094 | 122.9233 | -122.7402 | 0.11444 | 1.4211e-13 | -0.01726 | -0.013077 | -0.04517 | -0.041925 | -0.012779 | 0.0067908 | 0.008774 | 0.033737 | -0.026608 | 0.013363 | -0.019489 | 0.001048 | 0.019721 | -0.026723 | 0.12538 | 0.096516 | 0.31595 | -0.00811 | 0.02852 | 0.082776 | -0.074666 | 0.020409 | 0.17396 | -0.028878 | -0.24199 | 122.7321 | 0.010941 | 122.7412 | 122.7134 | -0.018613 | -0.017925 | 0.20151 | 122.4982 | -0.094032 | 122.7687 | 122.6655 | 0.16732 | 0.059517 | -0.14332 | 122.8656 | 122.8367 | 123.0561 | 122.7599 | -0.12255 | 122.7606 | 122.9141 | 122.7113 | 122.8229 | -0.35643
4017.9062 | 122.8775 | -122.7493 | 0.12817 | 1.4211e-13 | -0.01726 | -0.013077 | -0.04517 | -0.042352 | -0.012779 | -0.00083919 | 0.008774 | 0.033523 | -0.026394 | 0.01379 | -0.019276 | 0.001048 | 0.010564 | -0.026723 | 0.12996 | 0.1011 | 0.32053 | -0.017268 | 0.033099 | 0.073618 | -0.070087 | 0.015831 | 0.17854 | 0.007751 | -0.24199 | 122.7321 | 0.001786 | 122.7504 | 122.7226 | -0.009455 | -0.027079 | 0.19236 | 122.5073 | -0.11234 | 122.7824 | 122.6792 | 0.1719 | 0.050362 | -0.12042 | 122.8793 | 122.8504 | 123.0699 | 122.7599 | -0.14544 | 122.7652 | 122.9279 | 122.7571 | 122.8229 | -0.37016
4019.6875 | 122.905 | -122.7539 | 0.13275 | 1.4211e-13 | -0.017688 | -0.012863 | -0.045384 | -0.042139 | -0.012993 | -0.00083919 | 0.0092014 | 0.033523 | -0.026608 | 0.013577 | -0.019489 | 0.001048 | 0.010564 | -0.022144 | 0.11622 | 0.10567 | 0.31595 | -0.031005 | 0.023941 | 0.073618 | -0.083823 | 0.015831 | 0.18311 | 0.048958 | -0.24199 | 122.7229 | -0.016526 | 122.755 | 122.7318 | 0.008861 | -0.027077 | 0.1832 | 122.5119 | -0.11692 | 122.7778 | 122.6701 | 0.15817 | 0.050364 | -0.083793 | 122.8701 | 122.8596 | 123.0699 | 122.7645 | -0.16376 | 122.7697 | 122.937 | 122.8029 | 122.8275 | -0.37474
4021.4219 | 122.9828 | -122.7081 | 0.10986 | 1.4211e-13 | -0.01726 | -0.013077 | -0.045384 | -0.041925 | -0.012565 | -0.00083919 | 0.008774 | 0.033737 | -0.026821 | 0.01379 | -0.019489 | -0.003531 | 0.0243 | -0.022144 | 0.12538 | 0.1011 | 0.32053 | -0.026426 | 0.019362 | 0.078197 | -0.065509 | 0.015831 | 0.17854 | 0.039801 | -0.24657 | 122.6817 | 0.015519 | 122.7046 | 122.686 | 0.004282 | -0.008768 | 0.21067 | 122.4616 | -0.094032 | 122.7275 | 122.6426 | 0.18106 | 0.068673 | -0.070062 | 122.8335 | 122.8092 | 123.0287 | 122.7324 | -0.13629 | 122.724 | 122.8867 | 122.7479 | 122.7863 | -0.35643
4023.2344 | 123.0331 | -122.7036 | 0.091553 | 1.4211e-13 | -0.017474 | -0.012863 | -0.045384 | -0.042352 | -0.012779 | -0.00083919 | 0.0092014 | 0.033309 | -0.027035 | 0.013577 | -0.019276 | 0.001048 | 0.019721 | -0.022144 | 0.1208 | 0.096516 | 0.32053 | -0.063057 | 0.02852 | 0.078197 | -0.070087 | 0.024988 | 0.17854 | 0.048958 | -0.24199 | 122.6405 | 0.029251 | 122.7046 | 122.6814 | 0.040913 | 0.004963 | 0.22898 | 122.4616 | -0.066565 | 122.7321 | 122.6335 | 0.1719 | 0.086983 | -0.042595 | 122.8244 | 122.8001 | 123.0241 | 122.7233 | -0.15461 | 122.7285 | 122.8821 | 122.7525 | 122.7817 | -0.33354
4025.0156 | 123.0011 | -122.731 | 0.09613 | 1.4211e-13 | -0.017688 | -0.013077 | -0.045384 | -0.042139 | -0.012993 | 0.0067908 | 0.009415 | 0.033523 | -0.026394 | 0.013363 | -0.019489 | 0.001048 | 0.0243 | -0.022144 | 0.1208 | 0.096516 | 0.31595 | -0.040163 | 0.019362 | 0.078197 | -0.074666 | 0.015831 | 0.18769 | 0.030644 | -0.24199 | 122.6909 | 0.024674 | 122.7321 | 122.7089 | 0.018019 | 0.000386 | 0.21982 | 122.489 | -0.080299 | 122.7504 | 122.6564 | 0.16732 | 0.091563 | -0.065486 | 122.8518 | 122.8275 | 123.047 | 122.7553 | -0.13629 | 122.7468 | 122.9187 | 122.7617 | 122.8092 | -0.33812
4026.75 | 122.9828 | -122.7036 | 0.07782 | 1.4211e-13 | -0.01726 | -0.013291 | -0.045384 | -0.041925 | -0.012993 | -0.00083919 | 0.0092014 | 0.033309 | -0.026821 | 0.013577 | -0.019276 | 0.005626 | 0.015142 | -0.017566 | 0.12538 | 0.11483 | 0.32511 | -0.053899 | 0.02852 | 0.078197 | -0.070087 | 0.020409 | 0.17854 | 0.021486 | -0.23741 | 122.6497 | 0.047562 | 122.7092 | 122.686 | 0.036333 | 0.037012 | 0.24729 | 122.4661 | -0.057411 | 122.7321 | 122.6335 | 0.16732 | 0.10072 | -0.056334 | 122.8289 | 122.8184 | 123.0287 | 122.7187 | -0.13172 | 122.724 | 122.8821 | 122.725 | 122.7817 | -0.31523
4028.5469 | 122.9965 | -122.7127 | 0.091553 | 1.4211e-13 | -0.017474 | -0.013077 | -0.045384 | -0.042139 | -0.013206 | -0.00083919 | 0.0089876 | 0.033523 | -0.026608 | 0.013577 | -0.019062 | -0.008109 | 0.015142 | -0.022144 | 0.12538 | 0.10567 | 0.32053 | -0.021847 | 0.019362 | 0.06904 | -0.070087 | 0.011252 | 0.18311 | 0.035222 | -0.24657 | 122.6909 | 0.033829 | 122.7046 | 122.6906 | -0.000297 | 0.014121 | 0.22898 | 122.4661 | -0.080301 | 122.7321 | 122.6426 | 0.17648 | 0.091562 | -0.056331 | 122.8381 | 122.8184 | 123.0332 | 122.7279 | -0.1134 | 122.724 | 122.8958 | 122.7479 | 122.7817 | -0.33812
4030.3438 | 123.0194 | -122.6715 | 0.086975 | 1.4211e-13 | -0.017047 | -0.013718 | -0.044957 | -0.042139 | -0.012779 | -0.00083919 | 0.0092014 | 0.033309 | -0.026608 | 0.01379 | -0.019489 | -0.003531 | 0.0243 | -0.026723 | 0.1208 | 0.096516 | 0.31595 | -0.035584 | 0.023941 | 0.078197 | -0.070087 | 0.020409 | 0.18311 | 0.035222 | -0.24657 | 122.6359 | 0.033829 | 122.668 | 122.6448 | 0.008861 | 0.009541 | 0.22898 | 122.4249 | -0.066566 | 122.6954 | 122.6014 | 0.17648 | 0.09614 | -0.051753 | 122.7923 | 122.768 | 122.9875 | 122.6958 | -0.12256 | 122.6919 | 122.8546 | 122.7067 | 122.7497 | -0.33354
4032.1406 | 122.8958 | -122.7448 | 0.10986 | 1.4211e-13 | -0.017474 | -0.013077 | -0.04517 | -0.041925 | -0.012779 | -0.00083919 | 0.009415 | 0.033523 | -0.027035 | 0.013577 | -0.019276 | -0.008109 | 0.015142 | -0.022144 | 0.12996 | 0.10567 | 0.31595 | 0.005627 | 0.02852 | 0.073618 | -0.070087 | 0.015831 | 0.19227 | 0.044379 | -0.24199 | 122.7504 | 0.020097 | 122.7366 | 122.7226 | -0.027771 | -0.004189 | 0.20609 | 122.5028 | -0.094032 | 122.7733 | 122.6747 | 0.1719 | 0.082409 | -0.065484 | 122.8747 | 122.8504 | 123.0607 | 122.7599 | -0.10424 | 122.7606 | 122.937 | 122.7891 | 122.8184 | -0.35185
4033.8594 | 122.9691 | -122.7264 | 0.07782 | 1.4211e-13 | -0.017047 | -0.013291 | -0.045384 | -0.042352 | -0.012779 | -0.00083919 | 0.0092014 | 0.033096 | -0.027035 | 0.01379 | -0.019062 | -0.008109 | 0.015142 | -0.017566 | 0.1208 | 0.1011 | 0.32053 | -0.044742 | 0.02852 | 0.082776 | -0.070087 | 0.011252 | 0.18311 | 0.058115 | -0.24199 | 122.6817 | 0.042984 | 122.7183 | 122.7089 | 0.027176 | 0.023275 | 0.24271 | 122.4845 | -0.066568 | 122.755 | 122.6564 | 0.1719 | 0.10529 | -0.019705 | 122.8472 | 122.8275 | 123.047 | 122.7416 | -0.12256 | 122.7377 | 122.9096 | 122.7846 | 122.8092 | -0.31981
4035.6562 | 122.9416 | -122.7402 | 0.13733 | 1.4211e-13 | -0.017047 | -0.013077 | -0.045384 | -0.042139 | -0.012779 | -0.0084697 | 0.009415 | 0.033523 | -0.026608 | 0.013577 | -0.019703 | 0.001048 | 0.019721 | -0.022144 | 0.11622 | 0.1011 | 0.31137 | -0.026426 | 0.014784 | 0.078197 | -0.070087 | 0.020409 | 0.18311 | 0.016908 | -0.25115 | 122.7137 | -0.021104 | 122.7412 | 122.718 | 0.004282 | -0.036234 | 0.17404 | 122.489 | -0.11692 | 122.755 | 122.6701 | 0.18106 | 0.045786 | -0.12042 | 122.8564 | 122.8413 | 123.0515 | 122.7599 | -0.16376 | 122.7606 | 122.9233 | 122.7571 | 122.8184 | -0.38848
4037.4531 | 122.9919 | -122.7081 | 0.091553 | 1.4211e-13 | -0.01726 | -0.013291 | -0.045598 | -0.042139 | -0.012565 | -0.0084697 | 0.0092014 | 0.033309 | -0.026821 | 0.01379 | -0.019489 | 0.001048 | 0.015142 | -0.022144 | 0.11165 | 0.1011 | 0.32053 | -0.017268 | 0.023941 | 0.087354 | -0.070087 | 0.015831 | 0.18311 | 0.026065 | -0.23741 | 122.6909 | 0.020094 | 122.7092 | 122.686 | -0.004876 | 0.009542 | 0.22898 | 122.4707 | -0.075722 | 122.7321 | 122.638 | 0.16732 | 0.091562 | -0.065488 | 122.8198 | 122.8092 | 123.0287 | 122.7233 | -0.10882 | 122.724 | 122.8912 | 122.7342 | 122.7955 | -0.32896
4039.25 | 123.0194 | -122.7173 | 0.09613 | 1.4211e-13 | -0.017688 | -0.012863 | -0.045384 | -0.042139 | -0.012993 | -0.00083919 | 0.0092014 | 0.033309 | -0.027035 | 0.01379 | -0.019276 | 0.001048 | 0.010564 | -0.022144 | 0.12996 | 0.087359 | 0.32053 | -0.035584 | 0.019362 | 0.078197 | -0.065509 | 0.020409 | 0.18769 | 0.048958 | -0.25115 | 122.6817 | 0.03383 | 122.7183 | 122.6951 | 0.01344 | -0.008771 | 0.2244 | 122.4661 | -0.075721 | 122.7366 | 122.6518 | 0.18564 | 0.091563 | -0.047172 | 122.8472 | 122.8046 | 123.0378 | 122.7278 | -0.13171 | 122.7377 | 122.905 | 122.7662 | 122.7955 | -0.34728
4041.0312 | 122.9095 | -122.7402 | 0.14191 | 1.4211e-13 | -0.01726 | -0.013505 | -0.045384 | -0.041925 | -0.012993 | -0.00083919 | 0.0089876 | 0.033096 | -0.026821 | 0.013577 | -0.019276 | -0.003531 | 0.010564 | -0.022144 | 0.11622 | 0.10567 | 0.31595 | -0.072215 | 0.019362 | 0.078197 | -0.070087 | 0.024988 | 0.18769 | 0.044379 | -0.24199 | 122.668 | -0.025682 | 122.7366 | 122.718 | 0.050071 | -0.036233 | 0.17405 | 122.4982 | -0.11692 | 122.7595 | 122.6701 | 0.1719 | 0.045786 | -0.097528 | 122.8564 | 122.8458 | 123.0561 | 122.7507 | -0.21412 | 122.7652 | 122.9279 | 122.7846 | 122.8184 | -0.3839
4042.7656 | 122.9919 | -122.7356 | 0.082397 | 1.4211e-13 | -0.017047 | -0.013291 | -0.04517 | -0.042139 | -0.012779 | -0.00083919 | 0.009415 | 0.033309 | -0.027035 | 0.013577 | -0.019276 | -0.003531 | 0.015142 | -0.026723 | 0.1208 | 0.10567 | 0.31595 | -0.044742 | 0.02852 | 0.078197 | -0.074666 | 0.020409 | 0.19227 | 0.007751 | -0.24199 | 122.6909 | 0.038407 | 122.7321 | 122.7089 | 0.018019 | 0.023277 | 0.23356 | 122.4936 | -0.061988 | 122.7641 | 122.6609 | 0.16732 | 0.10988 | -0.074646 | 122.8564 | 122.8413 | 123.0515 | 122.7507 | -0.12714 | 122.756 | 122.9279 | 122.7433 | 122.8138 | -0.32439
4044.5625 | 123.0469 | -122.7173 | 0.068665 | 1.4211e-13 | -0.017474 | -0.013291 | -0.04517 | -0.041925 | -0.012779 | 0.0067908 | 0.0092014 | 0.033096 | -0.026821 | 0.01379 | -0.019276 | -0.003531 | 0.019721 | -0.022144 | 0.1208 | 0.096516 | 0.32511 | -0.053899 | 0.023941 | 0.078197 | -0.074666 | 0.011252 | 0.19227 | -0.001407 | -0.24657 | 122.6634 | 0.052139 | 122.7138 | 122.6951 | 0.031755 | 0.027851 | 0.25645 | 122.4707 | -0.057413 | 122.7412 | 122.6426 | 0.1719 | 0.12361 | -0.070072 | 122.8381 | 122.8138 | 123.0424 | 122.737 | -0.12256 | 122.7285 | 122.9096 | 122.7159 | 122.7955 | -0.31523
4046.2969 | 122.9095 | -122.7905 | 0.13275 | 1.4211e-13 | -0.01726 | -0.012863 | -0.045598 | -0.041925 | -0.012565 | -0.00083919 | 0.009415 | 0.033523 | -0.026608 | 0.013363 | -0.019489 | -0.008109 | 0.010564 | -0.026723 | 0.12538 | 0.10567 | 0.31137 | -0.012689 | 0.02852 | 0.078197 | -0.079245 | 0.011252 | 0.18769 | 0.016908 | -0.24199 | 122.7778 | -0.007369 | 122.7824 | 122.7638 | -0.014034 | -0.027077 | 0.17862 | 122.5485 | -0.1215 | 122.819 | 122.7113 | 0.16274 | 0.054942 | -0.11584 | 122.9159 | 122.8962 | 123.1019 | 122.8011 | -0.14544 | 122.8018 | 122.9782 | 122.8074 | 122.8687 | -0.37474
4048.1094 | 122.905 | -122.7676 | 0.10986 | 1.4211e-13 | -0.01726 | -0.013291 | -0.044957 | -0.041925 | -0.012779 | -0.00083919 | 0.009415 | 0.033523 | -0.026608 | 0.013577 | -0.019276 | 0.001048 | 0.019721 | -0.022144 | 0.1208 | 0.096516 | 0.32053 | -0.031005 | 0.019362 | 0.082776 | -0.070087 | 0.015831 | 0.17854 | -0.005985 | -0.24199 | 122.7366 | 0.010941 | 122.7687 | 122.7455 | 0.008861 | -0.013347 | 0.21067 | 122.5256 | -0.094032 | 122.787 | 122.6976 | 0.1719 | 0.068673 | -0.11585 | 122.8884 | 122.8642 | 123.0882 | 122.7874 | -0.14087 | 122.7835 | 122.9462 | 122.7617 | 122.8504 | -0.35185
4049.8906 | 122.9507 | -122.7539 | 0.11902 | 1.4211e-13 | -0.017047 | -0.013291 | -0.045384 | -0.042139 | -0.012993 | -0.00083919 | 0.0092014 | 0.033309 | -0.027035 | 0.013577 | -0.019489 | 0.005626 | 0.019721 | -0.022144 | 0.12538 | 0.10567 | 0.31595 | -0.017268 | 0.023941 | 0.082776 | -0.079245 | 0.011252 | 0.18769 | -0.038035 | -0.24199 | 122.7366 | 0.006363 | 122.7595 | 122.7318 | -0.004876 | -0.013345 | 0.19693 | 122.5119 | -0.10777 | 122.7778 | 122.6747 | 0.16274 | 0.068674 | -0.15705 | 122.8793 | 122.8596 | 123.0699 | 122.7736 | -0.13629 | 122.7652 | 122.9416 | 122.7159 | 122.8367 | -0.36101
4051.6875 | 122.9462 | -122.7356 | 0.10986 | 1.4211e-13 | -0.01726 | -0.013077 | -0.045384 | -0.041925 | -0.012993 | -0.00083919 | 0.0092014 | 0.033309 | -0.026608 | 0.013363 | -0.019489 | 0.010204 | 0.019721 | -0.026723 | 0.1208 | 0.1011 | 0.31595 | 0.001048 | 0.023941 | 0.078197 | -0.065509 | 0.015831 | 0.18769 | -0.074664 | -0.24199 | 122.7366 | 0.010941 | 122.7458 | 122.7089 | -0.027771 | -0.008768 | 0.20609 | 122.4936 | -0.094032 | 122.7595 | 122.6701 | 0.17648 | 0.07783 | -0.18453 | 122.8564 | 122.8367 | 123.0515 | 122.7553 | -0.10882 | 122.7514 | 122.9233 | 122.6609 | 122.8138 | -0.35185
4053.4219 | 123.0331 | -122.731 | 0.086975 | 1.4211e-13 | -0.016833 | -0.013505 | -0.045598 | -0.042352 | -0.012779 | 0.0067908 | 0.009415 | 0.033309 | -0.026821 | 0.013363 | -0.019489 | 0.001048 | 0.019721 | -0.026723 | 0.12538 | 0.1011 | 0.32053 | -0.044742 | 0.02852 | 0.082776 | -0.070087 | 0.011252 | 0.18311 | -0.001407 | -0.25115 | 122.6863 | 0.038407 | 122.7321 | 122.7043 | 0.018019 | 0.01412 | 0.23356 | 122.4799 | -0.075723 | 122.7595 | 122.6609 | 0.18106 | 0.09614 | -0.088382 | 122.8564 | 122.8321 | 123.0515 | 122.7507 | -0.13172 | 122.7423 | 122.9141 | 122.7296 | 122.8138 | -0.33812
4055.2188 | 123.0377 | -122.7631 | 0.09613 | 1.4211e-13 | -0.017047 | -0.013505 | -0.045811 | -0.041925 | -0.012779 | 0.014421 | 0.008774 | 0.033523 | -0.027035 | 0.013577 | -0.019276 | 0.005626 | 0.010564 | -0.022144 | 0.1208 | 0.1011 | 0.32053 | -0.040163 | 0.02852 | 0.064461 | -0.070087 | 0.020409 | 0.19227 | -0.028878 | -0.24657 | 122.7229 | 0.024674 | 122.7687 | 122.7409 | 0.018019 | 0.004965 | 0.2244 | 122.5165 | -0.075721 | 122.7916 | 122.693 | 0.17648 | 0.096142 | -0.12501 | 122.8839 | 122.8642 | 123.0836 | 122.7736 | -0.13629 | 122.7835 | 122.9553 | 122.7342 | 122.8275 | -0.3427
4056.9531 | 122.9965 | -122.7402 | 0.10071 | 1.4211e-13 | -0.016619 | -0.013291 | -0.04517 | -0.041925 | -0.012779 | 0.0067908 | 0.0092014 | 0.033309 | -0.027035 | 0.013577 | -0.019276 | 0.001048 | 0.010564 | -0.022144 | 0.12538 | 0.096516 | 0.32053 | -0.049321 | 0.023941 | 0.073618 | -0.070087 | 0.015831 | 0.18769 | 0.026065 | -0.24657 | 122.6909 | 0.024674 | 122.7412 | 122.718 | 0.027177 | -0.004192 | 0.21982 | 122.4936 | -0.084877 | 122.7641 | 122.6701 | 0.17648 | 0.086985 | -0.074643 | 122.8656 | 122.8367 | 123.0607 | 122.7507 | -0.15003 | 122.756 | 122.9279 | 122.7662 | 122.8138 | -0.34728
4058.7344 | 122.9324 | -122.7859 | 0.13275 | 1.4211e-13 | -0.016833 | -0.013291 | -0.045598 | -0.041925 | -0.012779 | -0.0084697 | 0.009415 | 0.033523 | -0.026821 | 0.013577 | -0.019489 | 0.001048 | 0.019721 | -0.017566 | 0.11165 | 0.1011 | 0.32053 | -0.021847 | 0.023941 | 0.078197 | -0.070087 | 0.020409 | 0.18311 | -0.001407 | -0.24657 | 122.7641 | -0.021104 | 122.787 | 122.7684 | 0.004281 | -0.031656 | 0.18778 | 122.5394 | -0.11234 | 122.8099 | 122.7159 | 0.17648 | 0.050364 | -0.13416 | 122.8976 | 122.887 | 123.1065 | 122.8057 | -0.1546 | 122.8064 | 122.9691 | 122.7845 | 122.8641 | -0.37932
4060.4688 | 123.0057 | -122.7585 | 0.10071 | 1.4211e-13 | -0.017047 | -0.013291 | -0.044957 | -0.041925 | -0.012779 | -0.00083919 | 0.0092014 | 0.033523 | -0.027035 | 0.013577 | -0.019062 | 0.005626 | 0.010564 | -0.026723 | 0.1208 | 0.10567 | 0.32053 | -0.026426 | 0.023941 | 0.073618 | -0.070087 | 0.020409 | 0.19227 | -0.005985 | -0.24199 | 122.7321 | 0.020096 | 122.7641 | 122.7318 | -0.000297 | 0.004966 | 0.21982 | 122.5165 | -0.080299 | 122.7824 | 122.6884 | 0.1719 | 0.091564 | -0.10669 | 122.8793 | 122.8642 | 123.079 | 122.769 | -0.12713 | 122.7789 | 122.9508 | 122.7525 | 122.8321 | -0.3427
4062.2656 | 123.0377 | -122.7356 | 0.082397 | 1.4211e-13 | -0.016833 | -0.013291 | -0.04517 | -0.041711 | -0.013206 | 0.0067908 | 0.008774 | 0.033523 | -0.026821 | 0.01379 | -0.019276 | 0.001048 | 0.019721 | -0.026723 | 0.1208 | 0.096516 | 0.32053 | -0.035584 | 0.019362 | 0.073618 | -0.065509 | 0.015831 | 0.17854 | 0.044379 | -0.24657 | 122.7 | 0.038407 | 122.7366 | 122.7089 | 0.008861 | 0.014119 | 0.23813 | 122.489 | -0.066566 | 122.755 | 122.6701 | 0.18106 | 0.096139 | -0.038018 | 122.8564 | 122.8321 | 123.0561 | 122.7553 | -0.11798 | 122.7514 | 122.9141 | 122.78 | 122.8092 | -0.32896
4064.0469 | 123.0515 | -122.7539 | 0.10071 | 1.4211e-13 | -0.01726 | -0.013505 | -0.04517 | -0.042352 | -0.013206 | -0.00083919 | 0.008774 | 0.033523 | -0.026821 | 0.01379 | -0.019276 | 0.001048 | 0.010564 | -0.022144 | 0.12538 | 0.1011 | 0.32511 | -0.067636 | 0.02852 | 0.082776 | -0.070087 | 0.020409 | 0.18311 | 0.053537 | -0.25115 | 122.6863 | 0.024674 | 122.755 | 122.7318 | 0.045492 | 0.000387 | 0.2244 | 122.5028 | -0.080299 | 122.7824 | 122.6838 | 0.18106 | 0.082407 | -0.047171 | 122.8793 | 122.855 | 123.079 | 122.7645 | -0.16834 | 122.7743 | 122.937 | 122.8074 | 122.8367 | -0.35185
4065.7812 | 123.0057 | -122.7448 | 0.068665 | 1.4211e-13 | -0.016833 | -0.013505 | -0.045811 | -0.041925 | -0.013206 | 0.0067908 | 0.008774 | 0.033737 | -0.026608 | 0.014218 | -0.019276 | -0.003531 | 0.019721 | -0.017566 | 0.12538 | 0.10567 | 0.31595 | -0.031005 | 0.02852 | 0.078197 | -0.070087 | 0.015831 | 0.18769 | -0.028878 | -0.24657 | 122.7137 | 0.056717 | 122.7412 | 122.7272 | 0.013439 | 0.037009 | 0.24729 | 122.4982 | -0.052834 | 122.7733 | 122.6747 | 0.17648 | 0.11903 | -0.097543 | 122.8701 | 122.8504 | 123.0607 | 122.7645 | -0.09967 | 122.7606 | 122.9324 | 122.7159 | 122.8229 | -0.31523
4067.5938 | 123.0011 | -122.7631 | 0.082397 | 1.4211e-13 | -0.016619 | -0.013291 | -0.045384 | -0.041925 | -0.012565 | 0.0067908 | 0.0085604 | 0.033309 | -0.026608 | 0.013577 | -0.019276 | 0.001048 | 0.015142 | -0.022144 | 0.12538 | 0.1011 | 0.31595 | -0.072215 | 0.033099 | 0.082776 | -0.070087 | 0.015831 | 0.19227 | 0.058115 | -0.24199 | 122.6908 | 0.042985 | 122.7641 | 122.7409 | 0.050071 | 0.018698 | 0.23356 | 122.5211 | -0.066566 | 122.7962 | 122.693 | 0.1719 | 0.10988 | -0.024282 | 122.8884 | 122.8642 | 123.079 | 122.7782 | -0.15461 | 122.7789 | 122.9553 | 122.8212 | 122.8458 | -0.32439
4069.3906 | 122.9004 | -122.7951 | 0.13733 | 1.4211e-13 | -0.01726 | -0.013291 | -0.04517 | -0.041925 | -0.012779 | -0.00083919 | 0.0089876 | 0.033523 | -0.026821 | 0.01379 | -0.019276 | 0.001048 | 0.015142 | -0.026723 | 0.1208 | 0.11025 | 0.32053 | -0.031005 | 0.023941 | 0.078197 | -0.070087 | 0.020409 | 0.19227 | 0.007751 | -0.24199 | 122.7641 | -0.016525 | 122.7962 | 122.7684 | 0.004282 | -0.027076 | 0.1832 | 122.5531 | -0.11692 | 122.819 | 122.725 | 0.1719 | 0.054943 | -0.12958 | 122.9159 | 122.9054 | 123.1156 | 122.8102 | -0.16833 | 122.8155 | 122.9874 | 122.8029 | 122.8733 | -0.37932
4071.125 | 122.9233 | -122.7585 | 0.11444 | 1.4211e-13 | -0.016192 | -0.013505 | -0.04517 | -0.042139 | -0.012779 | 0.0067908 | 0.008774 | 0.033737 | -0.026394 | 0.01379 | -0.019489 | -0.003531 | 0.019721 | -0.022144 | 0.12996 | 0.096516 | 0.32511 | -0.049321 | 0.023941 | 0.073618 | -0.074666 | 0.020409 | 0.18769 | 0.021486 | -0.24657 | 122.7092 | 0.015519 | 122.755 | 122.7363 | 0.027177 | -0.017925 | 0.21067 | 122.5119 | -0.094032 | 122.7824 | 122.6838 | 0.1719 | 0.073252 | -0.092955 | 122.8884 | 122.855 | 123.0836 | 122.7782 | -0.16376 | 122.7789 | 122.9462 | 122.78 | 122.8321 | -0.36101
4072.9375 | 122.937 | -122.7905 | 0.1236 | 1.4211e-13 | -0.016833 | -0.013291 | -0.045811 | -0.041925 | -0.012993 | -0.00083919 | 0.008774 | 0.033737 | -0.026821 | 0.01379 | -0.019276 | -0.008109 | 0.019721 | -0.017566 | 0.11622 | 0.096516 | 0.32053 | -0.021847 | 0.023941 | 0.073618 | -0.065509 | 0.011252 | 0.18769 | -0.051771 | -0.24199 | 122.7687 | -0.007371 | 122.7824 | 122.773 | 0.004281 | -0.02708 | 0.19694 | 122.5485 | -0.11234 | 122.8145 | 122.725 | 0.17648 | 0.064097 | -0.17537 | 122.9068 | 122.887 | 123.1111 | 122.8102 | -0.14544 | 122.8018 | 122.9782 | 122.7388 | 122.8641 | -0.36558
4074.7188 | 122.937 | -122.7722 | 0.13275 | 1.4211e-13 | -0.016833 | -0.013291 | -0.045598 | -0.041925 | -0.012779 | 0.0067908 | 0.008774 | 0.033523 | -0.026821 | 0.013363 | -0.019062 | -0.003531 | 0.019721 | -0.026723 | 0.1208 | 0.096516 | 0.32053 | -0.035584 | 0.023941 | 0.073618 | -0.06093 | 0.020409 | 0.18769 | 0.016908 | -0.24199 | 122.7366 | -0.011947 | 122.7687 | 122.7455 | 0.008861 | -0.036235 | 0.18778 | 122.5302 | -0.11234 | 122.7962 | 122.7113 | 0.18106 | 0.054942 | -0.11584 | 122.893 | 122.8687 | 123.0927 | 122.7919 | -0.16834 | 122.7926 | 122.9599 | 122.7891 | 122.8458 | -0.37474
4076.4531 | 123.056 | -122.7539 | 0.091553 | 1.4211e-13 | -0.016833 | -0.013291 | -0.04517 | -0.042139 | -0.012993 | -0.00083919 | 0.0089876 | 0.03395 | -0.026608 | 0.013577 | -0.019276 | -0.003531 | 0.019721 | -0.017566 | 0.1208 | 0.096516 | 0.32053 | -0.053899 | 0.023941 | 0.082776 | -0.070087 | 0.015831 | 0.19227 | 0.021486 | -0.25115 | 122.7 | 0.029251 | 122.7504 | 122.7363 | 0.036333 | 0.004963 | 0.22898 | 122.5028 | -0.075722 | 122.7778 | 122.6838 | 0.18106 | 0.10072 | -0.070067 | 122.8747 | 122.8504 | 123.0744 | 122.7736 | -0.14545 | 122.7697 | 122.9462 | 122.7754 | 122.8367 | -0.3427
4078.25 | 122.9233 | -122.7997 | 0.1236 | 1.4211e-13 | -0.016619 | -0.013505 | -0.045598 | -0.042139 | -0.012993 | -0.00083919 | 0.0096286 | 0.033523 | -0.026821 | 0.01379 | -0.019703 | 0.001048 | 0.010564 | -0.017566 | 0.12538 | 0.1011 | 0.32511 | -0.021847 | 0.023941 | 0.073618 | -0.079245 | 0.020409 | 0.18769 | -0.010564 | -0.24199 | 122.7778 | 0.001786 | 122.8007 | 122.7821 | 0.004281 | -0.022501 | 0.20151 | 122.5577 | -0.10319 | 122.8236 | 122.7204 | 0.16274 | 0.064097 | -0.13416 | 122.9251 | 122.9008 | 123.1248 | 122.8102 | -0.14544 | 122.8201 | 122.9874 | 122.7891 | 122.8733 | -0.36558
4080.0312 | 122.9324 | -122.8134 | 0.13275 | 1.4211e-13 | -0.016833 | -0.013291 | -0.044957 | -0.041925 | -0.012779 | -0.00083919 | 0.0092014 | 0.033309 | -0.026821 | 0.013363 | -0.019062 | 0.001048 | 0.0243 | -0.017566 | 0.1208 | 0.1011 | 0.31595 | 0.005627 | 0.02852 | 0.078197 | -0.06093 | 0.015831 | 0.18769 | -0.038035 | -0.24199 | 122.819 | -0.011947 | 122.8145 | 122.7959 | -0.023193 | -0.031656 | 0.1832 | 122.5714 | -0.11692 | 122.8419 | 122.7525 | 0.18106 | 0.054942 | -0.17079 | 122.9342 | 122.9145 | 123.1294 | 122.8377 | -0.12712 | 122.8292 | 123.0011 | 122.7754 | 122.8916 | -0.37474
4081.8125 | 123.0469 | -122.7402 | 0.082397 | 1.4211e-13 | -0.017047 | -0.013077 | -0.04517 | -0.041925 | -0.012779 | -0.0084697 | 0.0092014 | 0.033096 | -0.027035 | 0.01379 | -0.019489 | -0.003531 | 0.019721 | -0.017566 | 0.1208 | 0.10567 | 0.32053 | -0.072215 | 0.02852 | 0.073618 | -0.070087 | 0.024988 | 0.18311 | 0.021486 | -0.24199 | 122.668 | 0.038407 | 122.7366 | 122.7226 | 0.054649 | 0.023277 | 0.23813 | 122.4982 | -0.057409 | 122.7687 | 122.6701 | 0.1719 | 0.10072 | -0.060911 | 122.861 | 122.8458 | 123.0607 | 122.7599 | -0.15461 | 122.7652 | 122.9233 | 122.7617 | 122.8138 | -0.32439
4083.6094 | 122.9782 | -122.7814 | 0.13733 | 1.4211e-13 | -0.016833 | -0.013077 | -0.045384 | -0.042352 | -0.012993 | -0.00083919 | 0.0092014 | 0.033309 | -0.026608 | 0.013577 | -0.019489 | -0.003531 | 0.010564 | -0.022144 | 0.12996 | 0.091937 | 0.31595 | -0.072215 | 0.023941 | 0.073618 | -0.065509 | 0.020409 | 0.19227 | 0.039801 | -0.24199 | 122.7092 | -0.007369 | 122.7778 | 122.7592 | 0.050071 | -0.045392 | 0.17862 | 122.5394 | -0.11692 | 122.8053 | 122.7159 | 0.17648 | 0.054943 | -0.097528 | 122.9113 | 122.8733 | 123.0973 | 122.7919 | -0.20954 | 122.8018 | 122.9736 | 122.8212 | 122.855 | -0.37932
4085.3438 | 123.0515 | -122.7631 | 0.09613 | 1.4211e-13 | -0.016406 | -0.013291 | -0.04517 | -0.041925 | -0.012993 | 0.0067908 | 0.0096286 | 0.033737 | -0.026821 | 0.013363 | -0.019489 | -0.008109 | 0.019721 | -0.026723 | 0.12538 | 0.10567 | 0.32053 | -0.044742 | 0.023941 | 0.073618 | -0.070087 | 0.015831 | 0.18769 | 0.048958 | -0.24657 | 122.7183 | 0.029252 | 122.755 | 122.7363 | 0.018019 | 0.009544 | 0.2244 | 122.5165 | -0.080299 | 122.787 | 122.693 | 0.17648 | 0.091563 | -0.047172 | 122.8884 | 122.8687 | 123.0836 | 122.7828 | -0.14087 | 122.7789 | 122.9508 | 122.812 | 122.8367 | -0.3427
4087.125 | 123.0743 | -122.7448 | 0.091553 | 1.4211e-13 | -0.016619 | -0.013505 | -0.045384 | -0.042139 | -0.012993 | -0.0084697 | 0.009415 | 0.033309 | -0.026821 | 0.01379 | -0.019489 | 0.010204 | 0.019721 | -0.017566 | 0.12996 | 0.1011 | 0.32053 | -0.031005 | 0.023941 | 0.078197 | -0.070087 | 0.015831 | 0.19685 | -0.028878 | -0.24657 | 122.7137 | 0.038407 | 122.755 | 122.7272 | 0.013439 | 0.009542 | 0.22898 | 122.4982 | -0.075722 | 122.7687 | 122.6747 | 0.17648 | 0.1053 | -0.12043 | 122.8747 | 122.8458 | 123.0653 | 122.7645 | -0.12256 | 122.7606 | 122.9416 | 122.7159 | 122.8229 | -0.33812
4088.875 | 123.0606 | -122.7585 | 0.10529 | 1.4211e-13 | -0.016619 | -0.013291 | -0.045384 | -0.042139 | -0.012779 | -0.00083919 | 0.0092014 | 0.032882 | -0.027035 | 0.013577 | -0.019276 | -0.008109 | 0.0243 | -0.022144 | 0.12996 | 0.1011 | 0.32511 | -0.026426 | 0.023941 | 0.078197 | -0.079245 | 0.011252 | 0.18769 | 0.016908 | -0.24199 | 122.7321 | 0.024674 | 122.7504 | 122.7363 | 0.004282 | -0.004191 | 0.21982 | 122.5165 | -0.094034 | 122.7824 | 122.6792 | 0.16274 | 0.082407 | -0.088378 | 122.8884 | 122.8596 | 123.0836 | 122.7828 | -0.13171 | 122.7697 | 122.9462 | 122.7754 | 122.8367 | -0.34728
4090.6875 | 123.0606 | -122.7493 | 0.086975 | 1.4211e-13 | -0.016619 | -0.013505 | -0.04517 | -0.042352 | -0.012565 | 0.0067908 | 0.009415 | 0.033523 | -0.026608 | 0.01379 | -0.019489 | 0.005626 | 0.015142 | -0.022144 | 0.12538 | 0.1011 | 0.32053 | -0.081373 | 0.019362 | 0.073618 | -0.074666 | 0.020409 | 0.18769 | 0.012329 | -0.24199 | 122.668 | 0.038407 | 122.755 | 122.7272 | 0.059229 | 0.01412 | 0.23356 | 122.5073 | -0.066566 | 122.7687 | 122.6747 | 0.16732 | 0.10072 | -0.074646 | 122.8747 | 122.8504 | 123.0699 | 122.7645 | -0.16835 | 122.7697 | 122.937 | 122.7617 | 122.8229 | -0.32896
4092.5 | 122.9599 | -122.7997 | 0.11902 | 1.4211e-13 | -0.016619 | -0.013291 | -0.045598 | -0.041711 | -0.012779 | 0.0067908 | 0.0096286 | 0.033309 | -0.027035 | 0.01379 | -0.019489 | 0.005626 | 0.019721 | -0.022144 | 0.12538 | 0.1011 | 0.32511 | -0.003531 | 0.023941 | 0.082776 | -0.065509 | 0.015831 | 0.18769 | -0.001407 | -0.24199 | 122.7962 | 0.006363 | 122.8053 | 122.7775 | -0.018613 | -0.017924 | 0.20609 | 122.5577 | -0.10319 | 122.8236 | 122.7342 | 0.17648 | 0.068674 | -0.12043 | 122.9251 | 122.9008 | 123.1248 | 122.8194 | -0.12255 | 122.8155 | 122.9874 | 122.7983 | 122.8825 | -0.36101
4094.2812 | 122.9691 | -122.7951 | 0.11902 | 1.4211e-13 | -0.016833 | -0.013077 | -0.04517 | -0.042352 | -0.012993 | -0.0084697 | 0.0092014 | 0.033309 | -0.027249 | 0.01379 | -0.019489 | 0.001048 | 0.015142 | -0.017566 | 0.1208 | 0.10567 | 0.32511 | -0.021847 | 0.033099 | 0.078197 | -0.065509 | 0.020409 | 0.19227 | -0.005985 | -0.24199 | 122.7733 | 0.001785 | 122.7962 | 122.7775 | 0.004281 | -0.013345 | 0.20609 | 122.5531 | -0.09861 | 122.8282 | 122.7296 | 0.17648 | 0.073253 | -0.125 | 122.9159 | 122.9008 | 123.1202 | 122.8102 | -0.14087 | 122.8155 | 122.9874 | 122.7891 | 122.8733 | -0.36101
4096.0625 | 122.937 | -122.8226 | 0.13733 | 1.4211e-13 | -0.016619 | -0.013291 | -0.04517 | -0.041925 | -0.012993 | -0.00083919 | 0.0089876 | 0.033309 | -0.026821 | 0.01379 | -0.019489 | 0.001048 | 0.015142 | -0.026723 | 0.12538 | 0.1011 | 0.32511 | -0.035584 | 0.023941 | 0.078197 | -0.065509 | 0.011252 | 0.18769 | 0.016908 | -0.24657 | 122.787 | -0.011947 | 122.8236 | 122.7958 | 0.008861 | -0.036234 | 0.18778 | 122.576 | -0.12608 | 122.8465 | 122.7571 | 0.18106 | 0.050364 | -0.12042 | 122.948 | 122.9237 | 123.1477 | 122.8377 | -0.17291 | 122.8338 | 123.0103 | 122.8395 | 122.9008 | -0.3839
4097.8594 | 123.056 | -122.7585 | 0.086975 | 1.4211e-13 | -0.016406 | -0.013291 | -0.045598 | -0.042139 | -0.012779 | -0.00083919 | 0.0092014 | 0.033309 | -0.026821 | 0.01379 | -0.019276 | -0.003531 | 0.015142 | -0.026723 | 0.12538 | 0.091937 | 0.32511 | -0.035584 | 0.02852 | 0.082776 | -0.065509 | 0.020409 | 0.18311 | 0.016908 | -0.24199 | 122.7229 | 0.038407 | 122.755 | 122.7318 | 0.008861 | 0.004962 | 0.23814 | 122.5165 | -0.066566 | 122.787 | 122.693 | 0.17648 | 0.09614 | -0.070067 | 122.8839 | 122.8504 | 123.0836 | 122.7736 | -0.12256 | 122.7789 | 122.9416 | 122.7754 | 122.8413 | -0.32896
4099.5938 | 122.9874 | -122.7997 | 0.11444 | 1.4211e-13 | -0.016619 | -0.013077 | -0.045598 | -0.041925 | -0.012993 | -0.00083919 | 0.009415 | 0.033309 | -0.027249 | 0.013577 | -0.019489 | 0.001048 | 0.019721 | -0.022144 | 0.12996 | 0.10567 | 0.32511 | -0.058478 | 0.019362 | 0.06904 | -0.074666 | 0.015831 | 0.18769 | 0.030644 | -0.24199 | 122.7412 | 0.015519 | 122.8007 | 122.7775 | 0.036334 | -0.008767 | 0.21067 | 122.5577 | -0.09861 | 122.819 | 122.725 | 0.16732 | 0.073252 | -0.083797 | 122.9296 | 122.9054 | 123.1248 | 122.8194 | -0.17292 | 122.8155 | 122.9874 | 122.8303 | 122.8687 | -0.35643
4101.4062 | 123.024 | -122.7951 | 0.091553 | 1.4211e-13 | -0.016406 | -0.013077 | -0.04517 | -0.042139 | -0.012993 | -0.00083919 | 0.0092014 | 0.033309 | -0.026821 | 0.01379 | -0.019276 | 0.001048 | 0.019721 | -0.022144 | 0.1208 | 0.10567 | 0.32511 | -0.040163 | 0.02852 | 0.078197 | -0.074666 | 0.020409 | 0.18311 | 0.053537 | -0.24199 | 122.7549 | 0.029251 | 122.7962 | 122.773 | 0.018019 | 0.014121 | 0.23356 | 122.5531 | -0.071144 | 122.8236 | 122.7204 | 0.16732 | 0.091562 | -0.038016 | 122.9159 | 122.9008 | 123.1202 | 122.8148 | -0.13172 | 122.8155 | 122.9782 | 122.8486 | 122.8733 | -0.33354
4103.2031 | 122.9965 | -122.7859 | 0.11444 | 1.4211e-13 | -0.016833 | -0.013077 | -0.04517 | -0.041711 | -0.012993 | -0.00083919 | 0.0092014 | 0.033096 | -0.027035 | 0.013577 | -0.019489 | 0.001048 | 0.019721 | -0.017566 | 0.11622 | 0.1011 | 0.33427 | -0.031005 | 0.023941 | 0.078197 | -0.065509 | 0.020409 | 0.17854 | 0.030644 | -0.24199 | 122.7549 | 0.001784 | 122.787 | 122.7684 | 0.013439 | -0.013346 | 0.21983 | 122.544 | -0.094032 | 122.8099 | 122.7204 | 0.17648 | 0.064095 | -0.083797 | 122.9022 | 122.887 | 123.1202 | 122.8057 | -0.14545 | 122.8064 | 122.9645 | 122.8166 | 122.8641 | -0.35643
4104.9219 | 123.0606 | -122.7768 | 0.086975 | 1.4211e-13 | -0.016619 | -0.013505 | -0.044957 | -0.042352 | -0.01342 | 0.014421 | 0.009415 | 0.033309 | -0.026821 | 0.01379 | -0.019276 | -0.008109 | 0.019721 | -0.017566 | 0.12996 | 0.10567 | 0.32511 | -0.017268 | 0.023941 | 0.078197 | -0.070087 | 0.015831 | 0.18311 | 0.039801 | -0.24657 | 122.7595 | 0.042985 | 122.7687 | 122.7592 | -0.000298 | 0.018699 | 0.23814 | 122.5302 | -0.071144 | 122.8007 | 122.7067 | 0.17648 | 0.09614 | -0.047174 | 122.9068 | 122.8825 | 123.1019 | 122.7965 | -0.10424 | 122.7926 | 122.9599 | 122.8166 | 122.855 | -0.33354
4106.7188 | 122.9874 | -122.7768 | 0.10986 | 1.4211e-13 | -0.016619 | -0.013291 | -0.04517 | -0.042352 | -0.012565 | -0.00083919 | 0.0096286 | 0.033309 | -0.026394 | 0.013363 | -0.019703 | -0.003531 | 0.019721 | -0.022144 | 0.11622 | 0.096516 | 0.31595 | -0.017268 | 0.02852 | 0.078197 | -0.074666 | 0.015831 | 0.18311 | 0.021486 | -0.24657 | 122.7595 | 0.006362 | 122.7733 | 122.7546 | -0.004876 | -0.013347 | 0.20609 | 122.5302 | -0.094032 | 122.8053 | 122.7021 | 0.1719 | 0.073252 | -0.088377 | 122.893 | 122.8733 | 123.0927 | 122.7965 | -0.12713 | 122.7926 | 122.9599 | 122.7983 | 122.855 | -0.35643
4108.5156 | 123.0881 | -122.7676 | 0.086975 | 1.4211e-13 | -0.016406 | -0.012863 | -0.04517 | -0.042139 | -0.012779 | -0.00083919 | 0.0092014 | 0.033523 | -0.027035 | 0.013577 | -0.019276 | -0.003531 | 0.0243 | -0.022144 | 0.1208 | 0.091937 | 0.32511 | 0.010206 | 0.033099 | 0.073618 | -0.06093 | 0.024988 | 0.17854 | -0.005985 | -0.24199 | 122.7778 | 0.033829 | 122.7641 | 122.7455 | -0.03235 | 0.004962 | 0.23814 | 122.5256 | -0.061987 | 122.8007 | 122.7067 | 0.18106 | 0.091561 | -0.09296 | 122.8884 | 122.8596 | 123.0927 | 122.7919 | -0.076769 | 122.7926 | 122.9462 | 122.7617 | 122.8413 | -0.32896
4110.2344 | 123.0057 | -122.8226 | 0.14191 | 1.4211e-13 | -0.015978 | -0.013291 | -0.045384 | -0.041925 | -0.012993 | -0.0084697 | 0.009415 | 0.033096 | -0.026608 | 0.01379 | -0.019276 | -0.003531 | 0.019721 | -0.026723 | 0.1208 | 0.096516 | 0.32053 | -0.012689 | 0.014784 | 0.091933 | -0.070087 | 0.029566 | 0.17854 | -0.001407 | -0.24657 | 122.8099 | -0.021103 | 122.819 | 122.7958 | -0.014034 | -0.045391 | 0.17862 | 122.576 | -0.11234 | 122.8374 | 122.7525 | 0.17648 | 0.036629 | -0.14331 | 122.9434 | 122.9191 | 123.1431 | 122.8423 | -0.1546 | 122.8521 | 123.0011 | 122.8212 | 122.9145 | -0.38847
4112.0312 | 123.0972 | -122.7859 | 0.086975 | 1.4211e-13 | -0.016833 | -0.013077 | -0.04517 | -0.042139 | -0.012779 | -0.00083919 | 0.0096286 | 0.033737 | -0.026821 | 0.01379 | -0.019703 | 0.010204 | 0.015142 | -0.017566 | 0.12538 | 0.1011 | 0.32511 | -0.067636 | 0.023941 | 0.082776 | -0.070087 | 0.015831 | 0.18769 | 0.048958 | -0.24657 | 122.7183 | 0.038407 | 122.7962 | 122.7684 | 0.05007 | 0.01412 | 0.23814 | 122.5394 | -0.071144 | 122.8099 | 122.7159 | 0.17648 | 0.10072 | -0.038017 | 122.9113 | 122.887 | 123.1111 | 122.8011 | -0.15461 | 122.8018 | 122.9736 | 122.8349 | 122.8687 | -0.33354
4113.8281 | 123.0331 | -122.7905 | 0.10529 | 1.4211e-13 | -0.017047 | -0.013505 | -0.045384 | -0.042139 | -0.012993 | 0.0067908 | 0.0098422 | 0.033523 | -0.026821 | 0.013577 | -0.019489 | -0.003531 | 0.019721 | -0.017566 | 0.1208 | 0.1011 | 0.32053 | -0.058478 | 0.023941 | 0.073618 | -0.070087 | 0.024988 | 0.18311 | 0.048958 | -0.24657 | 122.732 | 0.015518 | 122.787 | 122.773 | 0.040912 | -0.004191 | 0.21525 | 122.544 | -0.080298 | 122.8145 | 122.7204 | 0.17648 | 0.077829 | -0.056328 | 122.9113 | 122.8916 | 123.1111 | 122.8102 | -0.16376 | 122.8155 | 122.9736 | 122.8395 | 122.8641 | -0.35185
4115.5781 | 123.0835 | -122.7951 | 0.082397 | 1.4211e-13 | -0.016619 | -0.013291 | -0.04517 | -0.042139 | -0.012993 | -0.00083919 | 0.0096286 | 0.033309 | -0.026608 | 0.01379 | -0.019276 | 0.001048 | 0.019721 | -0.012988 | 0.1208 | 0.1011 | 0.32053 | -0.003531 | 0.02852 | 0.078197 | -0.074666 | 0.015831 | 0.18311 | 0.003172 | -0.24199 | 122.7916 | 0.038407 | 122.7962 | 122.7821 | -0.009457 | 0.018698 | 0.23813 | 122.5531 | -0.066566 | 122.8236 | 122.7204 | 0.16732 | 0.10072 | -0.079225 | 122.9159 | 122.8962 | 123.1156 | 122.8148 | -0.085928 | 122.8109 | 122.9782 | 122.7983 | 122.8733 | -0.32439
4117.375 | 123.0835 | -122.7585 | 0.082397 | 1.4211e-13 | -0.016619 | -0.013505 | -0.045598 | -0.041925 | -0.012993 | -0.00083919 | 0.0096286 | 0.033096 | -0.027249 | 0.013363 | -0.019489 | 0.001048 | 0.019721 | -0.026723 | 0.12996 | 0.10567 | 0.32969 | -0.044742 | 0.023941 | 0.087354 | -0.070087 | 0.020409 | 0.18311 | 0.016908 | -0.24657 | 122.7137 | 0.047563 | 122.7595 | 122.7318 | 0.018019 | 0.023277 | 0.24729 | 122.5119 | -0.061988 | 122.7824 | 122.6884 | 0.17648 | 0.10072 | -0.065489 | 122.8884 | 122.8642 | 123.0882 | 122.7782 | -0.12714 | 122.7789 | 122.9416 | 122.7754 | 122.8458 | -0.32896
4119.1719 | 122.9553 | -122.7951 | 0.1236 | 1.4211e-13 | -0.016192 | -0.013291 | -0.045598 | -0.042139 | -0.013206 | -0.00083919 | 0.0096286 | 0.033309 | -0.027249 | 0.013577 | -0.019489 | -0.003531 | 0.019721 | -0.017566 | 0.12538 | 0.096516 | 0.32511 | -0.040163 | 0.023941 | 0.073618 | -0.065509 | 0.020409 | 0.18311 | 0.035222 | -0.23741 | 122.7549 | 0.001786 | 122.7916 | 122.7775 | 0.022597 | -0.02708 | 0.20151 | 122.5577 | -0.10319 | 122.819 | 122.7296 | 0.1719 | 0.059519 | -0.088374 | 122.9205 | 122.8916 | 123.1202 | 122.8148 | -0.16376 | 122.8155 | 122.9782 | 122.8303 | 122.8687 | -0.36101
4120.9844 | 123.0835 | -122.7997 | 0.07782 | 1.4211e-13 | -0.017047 | -0.013291 | -0.04517 | -0.042139 | -0.013206 | 0.0067908 | 0.009415 | 0.033096 | -0.026608 | 0.01379 | -0.019276 | 0.001048 | 0.019721 | -0.026723 | 0.11622 | 0.10567 | 0.32511 | 0.001048 | 0.02852 | 0.073618 | -0.070087 | 0.024988 | 0.18769 | 0.021486 | -0.24657 | 122.8007 | 0.038405 | 122.8007 | 122.773 | -0.027771 | 0.027854 | 0.24729 | 122.5531 | -0.052832 | 122.8282 | 122.7296 | 0.17648 | 0.10987 | -0.056334 | 122.9159 | 122.9054 | 123.1248 | 122.8194 | -0.076772 | 122.8247 | 122.9874 | 122.8212 | 122.8733 | -0.32439
4122.7188 | 122.9828 | -122.8088 | 0.11444 | 1.4211e-13 | -0.016833 | -0.013505 | -0.045598 | -0.042352 | -0.013206 | -0.00083919 | 0.009415 | 0.032882 | -0.027035 | 0.01379 | -0.019489 | -0.003531 | 0.019721 | -0.026723 | 0.12996 | 0.11025 | 0.31595 | -0.081373 | 0.02852 | 0.073618 | -0.074666 | 0.015831 | 0.18769 | 0.016908 | -0.24199 | 122.7275 | 0.015519 | 122.8053 | 122.7821 | 0.05465 | -0.004188 | 0.20151 | 122.5668 | -0.09861 | 122.8374 | 122.7342 | 0.16732 | 0.073252 | -0.097533 | 122.9388 | 122.9191 | 123.1248 | 122.8286 | -0.19581 | 122.8247 | 122.9965 | 122.8257 | 122.8825 | -0.35643
4124.5156 | 122.9874 | -122.8088 | 0.09613 | 1.4211e-13 | -0.016619 | -0.013077 | -0.04517 | -0.041925 | -0.012779 | -0.0084697 | 0.0096286 | 0.033096 | -0.026821 | 0.013363 | -0.019276 | -0.003531 | 0.0243 | -0.022144 | 0.1208 | 0.096516 | 0.32053 | -0.076794 | 0.023941 | 0.078197 | -0.070087 | 0.015831 | 0.18311 | 0.030644 | -0.23741 | 122.732 | 0.024674 | 122.8053 | 122.7867 | 0.05465 | 0.000386 | 0.2244 | 122.5714 | -0.080299 | 122.8328 | 122.7388 | 0.16732 | 0.086985 | -0.065486 | 122.9296 | 122.9054 | 123.1294 | 122.8331 | -0.17292 | 122.8247 | 122.992 | 122.8395 | 122.887 | -0.33354
4126.2344 | 123.1155 | -122.7631 | 0.10071 | 1.4211e-13 | -0.017047 | -0.013291 | -0.04517 | -0.042139 | -0.012779 | -0.0161 | 0.0096286 | 0.033096 | -0.027249 | 0.013577 | -0.019276 | 0.005626 | 0.019721 | -0.017566 | 0.12538 | 0.10567 | 0.32053 | -0.00811 | 0.023941 | 0.073618 | -0.070087 | 0.015831 | 0.18769 | 0.035222 | -0.23741 | 122.755 | 0.024674 | 122.7687 | 122.7455 | -0.009456 | 0.004966 | 0.21982 | 122.5257 | -0.084877 | 122.787 | 122.693 | 0.16732 | 0.086985 | -0.065486 | 122.8884 | 122.8687 | 123.0836 | 122.7828 | -0.10882 | 122.7789 | 122.9508 | 122.7983 | 122.8367 | -0.33812
4128.0469 | 123.056 | -122.7951 | 0.09613 | 1.4211e-13 | -0.016833 | -0.013291 | -0.045384 | -0.042139 | -0.012993 | -0.0084697 | 0.0096286 | 0.033309 | -0.026821 | 0.01379 | -0.019276 | 0.001048 | 0.019721 | -0.022144 | 0.1208 | 0.1011 | 0.32053 | -0.031005 | 0.023941 | 0.073618 | -0.065509 | 0.024988 | 0.18311 | 0.021486 | -0.24657 | 122.7641 | 0.024674 | 122.7962 | 122.773 | 0.008861 | 0.004965 | 0.2244 | 122.5485 | -0.071142 | 122.819 | 122.7296 | 0.18106 | 0.086985 | -0.074644 | 122.9159 | 122.8962 | 123.1156 | 122.8148 | -0.12713 | 122.8201 | 122.9782 | 122.8166 | 122.8687 | -0.3427
4129.8281 | 123.0057 | -122.8363 | 0.10986 | 1.4211e-13 | -0.016619 | -0.013077 | -0.04517 | -0.041925 | -0.012565 | -0.00083919 | 0.0098422 | 0.032882 | -0.026821 | 0.013363 | -0.019489 | 0.001048 | 0.019721 | -0.017566 | 0.12538 | 0.10567 | 0.32511 | -0.021847 | 0.02852 | 0.082776 | -0.079245 | 0.020409 | 0.19227 | 0.007751 | -0.24199 | 122.8145 | 0.015519 | 122.8374 | 122.8187 | 0.004281 | -0.004189 | 0.21525 | 122.5943 | -0.089454 | 122.8648 | 122.7571 | 0.16274 | 0.082409 | -0.10211 | 122.9617 | 122.942 | 123.1614 | 122.856 | -0.13171 | 122.8567 | 123.0286 | 122.8441 | 122.9191 | -0.35185
4131.5625 | 123.0927 | -122.7768 | 0.086975 | 1.4211e-13 | -0.016619 | -0.013077 | -0.045384 | -0.041925 | -0.012993 | -0.00083919 | 0.0096286 | 0.033096 | -0.027035 | 0.013577 | -0.019276 | 0.001048 | 0.0243 | -0.026723 | 0.12538 | 0.10567 | 0.32053 | -0.09511 | 0.023941 | 0.078197 | -0.070087 | 0.020409 | 0.18311 | -0.015142 | -0.24199 | 122.6817 | 0.038407 | 122.7778 | 122.7501 | 0.068387 | 0.018699 | 0.23356 | 122.5348 | -0.066566 | 122.8007 | 122.7067 | 0.1719 | 0.09614 | -0.10212 | 122.9022 | 122.8825 | 123.0973 | 122.8011 | -0.18208 | 122.7972 | 122.9599 | 122.7617 | 122.855 | -0.32896
4133.3594 | 122.9828 | -122.8271 | 0.10986 | 1.4211e-13 | -0.016619 | -0.013291 | -0.045384 | -0.041925 | -0.012565 | -0.0084697 | 0.009415 | 0.032882 | -0.027249 | 0.013577 | -0.019062 | 0.005626 | 0.015142 | -0.022144 | 0.12996 | 0.10567 | 0.32511 | -0.044742 | 0.02852 | 0.06904 | -0.065509 | 0.020409 | 0.18769 | 0.048958 | -0.24199 | 122.7824 | 0.020097 | 122.8328 | 122.805 | 0.022598 | -0.004189 | 0.21525 | 122.5852 | -0.089454 | 122.8557 | 122.7616 | 0.17648 | 0.07783 | -0.060905 | 122.9571 | 122.9328 | 123.1523 | 122.8423 | -0.1546 | 122.8476 | 123.0148 | 122.8761 | 122.8962 | -0.35185
4135.1562 | 122.9828 | -122.8271 | 0.11902 | 1.4211e-13 | -0.016406 | -0.013291 | -0.045598 | -0.042139 | -0.012993 | -0.00083919 | 0.010056 | 0.033309 | -0.026608 | 0.014004 | -0.019489 | 0.001048 | 0.019721 | -0.031301 | 0.12538 | 0.10567 | 0.31595 | -0.063057 | 0.023941 | 0.078197 | -0.065509 | 0.011252 | 0.18769 | 0.044379 | -0.24199 | 122.7641 | 0.006363 | 122.8282 | 122.7958 | 0.031756 | -0.013345 | 0.19693 | 122.5852 | -0.10777 | 122.8511 | 122.7616 | 0.17648 | 0.068674 | -0.07464 | 122.9525 | 122.9328 | 123.1431 | 122.8469 | -0.18208 | 122.8384 | 123.0148 | 122.8715 | 122.9053 | -0.36101
4136.9688 | 123.1018 | -122.7722 | 0.10529 | 1.4211e-13 | -0.016619 | -0.013291 | -0.045598 | -0.041925 | -0.012779 | -0.0084697 | 0.010056 | 0.033096 | -0.027035 | 0.01379 | -0.019703 | 0.005626 | 0.015142 | -0.022144 | 0.12538 | 0.10567 | 0.32511 | -0.063057 | 0.023941 | 0.082776 | -0.074666 | 0.011252 | 0.17396 | 0.003172 | -0.24657 | 122.7092 | 0.020096 | 122.7778 | 122.7501 | 0.040913 | 0.000388 | 0.21982 | 122.5256 | -0.094034 | 122.7962 | 122.6976 | 0.1719 | 0.068672 | -0.10211 | 122.8976 | 122.8779 | 123.0973 | 122.7874 | -0.16834 | 122.7835 | 122.9462 | 122.7754 | 122.855 | -0.35185
4138.7031 | 123.0927 | -122.7859 | 0.10529 | 1.4211e-13 | -0.016406 | -0.013291 | -0.04517 | -0.042352 | -0.012779 | 0.0067908 | 0.0096286 | 0.033309 | -0.026821 | 0.014004 | -0.019489 | 0.001048 | 0.019721 | -0.022144 | 0.1208 | 0.1011 | 0.32511 | -0.049321 | 0.02852 | 0.073618 | -0.074666 | 0.020409 | 0.18311 | -0.015142 | -0.24199 | 122.7366 | 0.015518 | 122.787 | 122.7638 | 0.027177 | -0.004191 | 0.21982 | 122.544 | -0.084877 | 122.8145 | 122.7113 | 0.16732 | 0.077829 | -0.12043 | 122.9068 | 122.887 | 123.1111 | 122.8057 | -0.15461 | 122.8064 | 122.9691 | 122.7708 | 122.8596 | -0.34728
4140.5 | 123.0927 | -122.7676 | 0.086975 | 1.4211e-13 | -0.016406 | -0.013077 | -0.04517 | -0.042352 | -0.012993 | -0.00083919 | 0.010056 | 0.033096 | -0.027035 | 0.013577 | -0.019489 | -0.003531 | 0.015142 | -0.026723 | 0.12538 | 0.10567 | 0.32511 | -0.040163 | 0.033099 | 0.073618 | -0.070087 | 0.015831 | 0.18311 | 0.035222 | -0.24657 | 122.7275 | 0.038407 | 122.7641 | 122.7409 | 0.01344 | 0.018699 | 0.23814 | 122.5211 | -0.071144 | 122.8007 | 122.6976 | 0.17648 | 0.09614 | -0.051753 | 122.893 | 122.8733 | 123.0927 | 122.7828 | -0.12714 | 122.7835 | 122.9508 | 122.8029 | 122.8413 | -0.33354
4142.2969 | 122.9736 | -122.8455 | 0.12817 | 1.4211e-13 | -0.016619 | -0.013505 | -0.045384 | -0.041925 | -0.012993 | -0.0084697 | 0.0096286 | 0.033096 | -0.027035 | 0.013577 | -0.019703 | 0.001048 | 0.010564 | -0.026723 | 0.12538 | 0.1011 | 0.32511 | -0.003531 | 0.023941 | 0.082776 | -0.070087 | 0.020409 | 0.18311 | 0.026065 | -0.24199 | 122.8419 | -0.002792 | 122.8465 | 122.8187 | -0.023192 | -0.027079 | 0.19694 | 122.6035 | -0.10777 | 122.8694 | 122.7754 | 0.1719 | 0.054941 | -0.10211 | 122.9708 | 122.9466 | 123.1706 | 122.856 | -0.13171 | 122.8659 | 123.0286 | 122.8715 | 122.9282 | -0.37016
4144.0938 | 122.9736 | -122.8455 | 0.14191 | 1.4211e-13 | -0.016619 | -0.013291 | -0.045384 | -0.042139 | -0.012993 | -0.0084697 | 0.0096286 | 0.033309 | -0.026821 | 0.01379 | -0.019276 | 0.001048 | 0.019721 | -0.026723 | 0.1208 | 0.096516 | 0.32969 | -0.063057 | 0.02852 | 0.078197 | -0.079245 | 0.020409 | 0.18311 | 0.030644 | -0.24657 | 122.7824 | -0.021103 | 122.8465 | 122.8187 | 0.036334 | -0.045391 | 0.18778 | 122.5989 | -0.1215 | 122.874 | 122.7662 | 0.16732 | 0.041208 | -0.11126 | 122.9663 | 122.942 | 123.1751 | 122.8652 | -0.20496 | 122.8659 | 123.0286 | 122.8761 | 122.9237 | -0.38847
4145.8906 | 123.0057 | -122.818 | 0.10986 | 1.4211e-13 | -0.016619 | -0.013291 | -0.045384 | -0.042139 | -0.012779 | -0.00083919 | 0.009415 | 0.033737 | -0.026608 | 0.013577 | -0.019489 | 0.001048 | 0.015142 | -0.026723 | 0.12996 | 0.10567 | 0.32053 | -0.063057 | 0.023941 | 0.082776 | -0.074666 | 0.011252 | 0.18311 | 0.035222 | -0.24199 | 122.7549 | 0.020097 | 122.819 | 122.7913 | 0.036334 | -0.004189 | 0.21067 | 122.576 | -0.098611 | 122.8419 | 122.7433 | 0.16732 | 0.073252 | -0.074641 | 122.948 | 122.9237 | 123.1385 | 122.8331 | -0.17292 | 122.8292 | 123.0011 | 122.8532 | 122.9008 | -0.35185
4147.7031 | 123.0881 | -122.7768 | 0.086975 | 1.4211e-13 | -0.016619 | -0.013077 | -0.04517 | -0.041925 | -0.012565 | -0.0084697 | 0.010056 | 0.033309 | -0.026608 | 0.013363 | -0.019489 | 0.005626 | 0.019721 | -0.022144 | 0.1208 | 0.10567 | 0.32511 | -0.049321 | 0.02852 | 0.078197 | -0.065509 | 0.020409 | 0.18311 | 0.016908 | -0.24199 | 122.7275 | 0.033829 | 122.7824 | 122.7546 | 0.027177 | 0.018699 | 0.23814 | 122.5348 | -0.066566 | 122.8053 | 122.7113 | 0.17648 | 0.09614 | -0.070067 | 122.8976 | 122.8825 | 123.1019 | 122.7965 | -0.1363 | 122.7972 | 122.9599 | 122.7937 | 122.855 | -0.32896
4149.4531 | 123.024 | -122.8317 | 0.11902 | 1.4211e-13 | -0.016406 | -0.013291 | -0.045384 | -0.042352 | -0.012779 | -0.00083919 | 0.0096286 | 0.033309 | -0.027249 | 0.013577 | -0.019276 | 0.005626 | 0.019721 | -0.017566 | 0.12538 | 0.1011 | 0.32969 | -0.044742 | 0.023941 | 0.078197 | -0.070087 | 0.011252 | 0.18311 | 0.021486 | -0.24199 | 122.787 | 0.006363 | 122.8374 | 122.8142 | 0.027176 | -0.017924 | 0.21067 | 122.5897 | -0.10777 | 122.8557 | 122.7616 | 0.1719 | 0.064096 | -0.097533 | 122.9571 | 122.9328 | 123.1614 | 122.8514 | -0.16376 | 122.843 | 123.0148 | 122.8532 | 122.9099 | -0.36101
4151.25 | 123.1018 | -122.7905 | 0.082397 | 1.4211e-13 | -0.016406 | -0.013077 | -0.045598 | -0.041925 | -0.013206 | -0.00083919 | 0.009415 | 0.033096 | -0.026608 | 0.013577 | -0.019489 | 0.001048 | 0.015142 | -0.012988 | 0.12996 | 0.10567 | 0.32053 | -0.058478 | 0.033099 | 0.082776 | -0.070087 | 0.015831 | 0.18311 | 0.053537 | -0.24199 | 122.732 | 0.047563 | 122.7916 | 122.7775 | 0.04549 | 0.023277 | 0.23813 | 122.5485 | -0.066566 | 122.8236 | 122.7204 | 0.1719 | 0.10072 | -0.02886 | 122.9205 | 122.8962 | 123.1111 | 122.8057 | -0.14088 | 122.8064 | 122.9736 | 122.8441 | 122.8733 | -0.32439
4152.9844 | 122.9919 | -122.8363 | 0.10529 | 1.4211e-13 | -0.016833 | -0.013077 | -0.045598 | -0.041925 | -0.012779 | -0.00083919 | 0.0096286 | 0.033096 | -0.027249 | 0.01379 | -0.019276 | -0.003531 | 0.010564 | -0.026723 | 0.12538 | 0.1011 | 0.31595 | -0.058478 | 0.023941 | 0.078197 | -0.074666 | 0.020409 | 0.18311 | -0.005985 | -0.23741 | 122.7778 | 0.020096 | 122.8328 | 122.8096 | 0.031755 | -0.004191 | 0.21067 | 122.5989 | -0.084877 | 122.8602 | 122.7616 | 0.16274 | 0.077829 | -0.11127 | 122.9617 | 122.9374 | 123.1523 | 122.8469 | -0.16376 | 122.8567 | 123.0194 | 122.8303 | 122.9145 | -0.3427
4154.7656 | 123.0881 | -122.7905 | 0.086975 | 1.4211e-13 | -0.016619 | -0.013505 | -0.045384 | -0.041925 | -0.012779 | -0.00083919 | 0.009415 | 0.033096 | -0.026608 | 0.013577 | -0.019703 | -0.003531 | 0.019721 | -0.017566 | 0.12538 | 0.10567 | 0.32511 | -0.067636 | 0.023941 | 0.082776 | -0.070087 | 0.020409 | 0.17854 | 0.003172 | -0.23741 | 122.7229 | 0.038407 | 122.787 | 122.773 | 0.05007 | 0.018699 | 0.23814 | 122.5531 | -0.066566 | 122.8145 | 122.7204 | 0.16732 | 0.091561 | -0.083803 | 122.9159 | 122.8962 | 123.1156 | 122.8102 | -0.15461 | 122.8109 | 122.9691 | 122.7937 | 122.8733 | -0.32439
4156.5 | 123.0606 | -122.818 | 0.10529 | 1.4211e-13 | -0.016833 | -0.013505 | -0.045384 | -0.042352 | -0.012779 | -0.00083919 | 0.0096286 | 0.032882 | -0.026608 | 0.013577 | -0.019489 | 0.001048 | 0.019721 | -0.022144 | 0.1208 | 0.10567 | 0.32969 | -0.072215 | 0.023941 | 0.078197 | -0.065509 | 0.020409 | 0.18311 | 0.026065 | -0.24657 | 122.7458 | 0.015518 | 122.819 | 122.7958 | 0.050071 | 0.000388 | 0.2244 | 122.5714 | -0.084877 | 122.8419 | 122.7525 | 0.18106 | 0.077829 | -0.079221 | 122.9388 | 122.9237 | 123.1477 | 122.8377 | -0.1775 | 122.8384 | 123.0011 | 122.8441 | 122.8962 | -0.35185
4158.3125 | 123.0652 | -122.8088 | 0.09613 | 1.4211e-13 | -0.016619 | -0.013077 | -0.044743 | -0.042352 | -0.012779 | -0.00083919 | 0.0089876 | 0.033523 | -0.026821 | 0.013577 | -0.019489 | -0.008109 | 0.015142 | -0.026723 | 0.12538 | 0.10567 | 0.32511 | -0.067636 | 0.02852 | 0.078197 | -0.065509 | 0.020409 | 0.19227 | 0.035222 | -0.24199 | 122.7412 | 0.029252 | 122.8007 | 122.7821 | 0.040913 | 0.009544 | 0.22898 | 122.5668 | -0.075721 | 122.8374 | 122.7433 | 0.17648 | 0.096142 | -0.060908 | 122.9342 | 122.9145 | 123.1339 | 122.824 | -0.16377 | 122.8292 | 123.0011 | 122.8441 | 122.887 | -0.33812
4160.1094 | 123.1064 | -122.8043 | 0.09613 | 1.4211e-13 | -0.016619 | -0.013077 | -0.045384 | -0.041925 | -0.012779 | -0.0084697 | 0.0098422 | 0.033096 | -0.026181 | 0.01379 | -0.019276 | -0.008109 | 0.015142 | -0.017566 | 0.11622 | 0.10567 | 0.31595 | -0.090531 | 0.02852 | 0.078197 | -0.070087 | 0.015831 | 0.17854 | 0.035222 | -0.24657 | 122.7137 | 0.020095 | 122.7962 | 122.7867 | 0.072965 | 0.009544 | 0.21982 | 122.5577 | -0.080299 | 122.8328 | 122.7342 | 0.17648 | 0.082406 | -0.060908 | 122.9205 | 122.9099 | 123.1202 | 122.8194 | -0.18666 | 122.8201 | 122.9828 | 122.8395 | 122.8825 | -0.3427
4161.8281 | 123.0743 | -122.8226 | 0.086975 | 1.4211e-13 | -0.016406 | -0.013077 | -0.045384 | -0.041925 | -0.012779 | 0.0067908 | 0.009415 | 0.033096 | -0.026821 | 0.01379 | -0.019489 | 0.001048 | 0.0243 | -0.026723 | 0.1208 | 0.1011 | 0.32511 | -0.049321 | 0.02852 | 0.078197 | -0.070087 | 0.024988 | 0.18311 | 0.048958 | -0.23741 | 122.7732 | 0.033829 | 122.8236 | 122.7958 | 0.022598 | 0.01412 | 0.23814 | 122.5852 | -0.061987 | 122.8511 | 122.7525 | 0.16732 | 0.09614 | -0.038017 | 122.9434 | 122.9237 | 123.1477 | 122.8469 | -0.1363 | 122.8476 | 123.0057 | 122.8715 | 122.9008 | -0.32439
4163.6406 | 122.9782 | -122.8683 | 0.11444 | 1.4211e-13 | -0.016619 | -0.013291 | -0.045384 | -0.042139 | -0.012779 | 0.014421 | 0.0096286 | 0.033309 | -0.026821 | 0.013363 | -0.019062 | 0.001048 | 0.0243 | -0.017566 | 0.1208 | 0.10567 | 0.32511 | -0.00811 | 0.033099 | 0.082776 | -0.070087 | 0.020409 | 0.18311 | 0.021486 | -0.24657 | 122.8602 | 0.006363 | 122.8694 | 122.8508 | -0.009456 | -0.008767 | 0.21067 | 122.6218 | -0.094032 | 122.9014 | 122.7983 | 0.17648 | 0.068674 | -0.092955 | 122.9892 | 122.974 | 123.1935 | 122.8926 | -0.12255 | 122.8888 | 123.0515 | 122.8898 | 122.9511 | -0.36101
4165.3906 | 123.024 | -122.8226 | 0.09613 | 1.4211e-13 | -0.016619 | -0.013291 | -0.04517 | -0.041711 | -0.012779 | -0.00083919 | 0.009415 | 0.033096 | -0.026821 | 0.013577 | -0.019489 | -0.003531 | 0.015142 | -0.026723 | 0.12538 | 0.1011 | 0.32053 | -0.017268 | 0.019362 | 0.082776 | -0.065509 | 0.029566 | 0.18769 | 0.048958 | -0.24657 | 122.8053 | 0.029252 | 122.819 | 122.7958 | -0.009455 | 0.004965 | 0.2244 | 122.576 | -0.066564 | 122.8419 | 122.7571 | 0.18106 | 0.091563 | -0.047172 | 122.948 | 122.9237 | 123.1431 | 122.8377 | -0.1134 | 122.8521 | 123.0103 | 122.8715 | 122.9053 | -0.3427
4167.1875 | 123.1018 | -122.8088 | 0.086975 | 1.4211e-13 | -0.016406 | -0.013077 | -0.045384 | -0.041925 | -0.012993 | -0.00083919 | 0.009415 | 0.033096 | -0.026821 | 0.013577 | -0.019276 | 0.001048 | 0.0243 | -0.022144 | 0.1208 | 0.10567 | 0.32053 | -0.072215 | 0.023941 | 0.078197 | -0.074666 | 0.011252 | 0.18311 | 0.003172 | -0.23741 | 122.7366 | 0.033829 | 122.8099 | 122.7867 | 0.050071 | 0.018699 | 0.23356 | 122.5714 | -0.075723 | 122.8328 | 122.7342 | 0.16274 | 0.09614 | -0.083803 | 122.9296 | 122.9145 | 123.1294 | 122.8331 | -0.15919 | 122.8201 | 122.992 | 122.812 | 122.887 | -0.32439
4168.9844 | 123.111 | -122.7997 | 0.09613 | 1.4211e-13 | -0.016619 | -0.013505 | -0.044957 | -0.041925 | -0.012993 | -0.0084697 | 0.0096286 | 0.033309 | -0.026821 | 0.013363 | -0.019489 | 0.005626 | 0.019721 | -0.026723 | 0.12538 | 0.1011 | 0.31595 | -0.031005 | 0.023941 | 0.082776 | -0.070087 | 0.015831 | 0.18311 | -0.005985 | -0.23741 | 122.7687 | 0.029252 | 122.8053 | 122.773 | 0.004282 | 0.004965 | 0.21982 | 122.5623 | -0.080299 | 122.8236 | 122.7296 | 0.16732 | 0.086985 | -0.10211 | 122.9251 | 122.9008 | 123.1156 | 122.8194 | -0.12713 | 122.8155 | 122.9828 | 122.7937 | 122.8825 | -0.33354
4170.7188 | 123.056 | -122.8134 | 0.086975 | 1.4211e-13 | -0.016619 | -0.013291 | -0.045384 | -0.041925 | -0.012565 | -0.00083919 | 0.0096286 | 0.033096 | -0.027035 | 0.013363 | -0.019276 | -0.003531 | 0.0243 | -0.017566 | 0.1208 | 0.1011 | 0.32511 | -0.021847 | 0.019362 | 0.078197 | -0.065509 | 0.020409 | 0.18311 | 0.039801 | -0.24199 | 122.7916 | 0.033829 | 122.8099 | 122.7959 | 0.004281 | 0.01412 | 0.23814 | 122.5714 | -0.066566 | 122.8328 | 122.7479 | 0.17648 | 0.09614 | -0.047174 | 122.9342 | 122.9145 | 123.1385 | 122.8377 | -0.10882 | 122.8338 | 122.9965 | 122.8532 | 122.8916 | -0.32896
4172.5156 | 123.1247 | -122.7997 | 0.091553 | 1.4211e-13 | -0.016406 | -0.013077 | -0.04517 | -0.042352 | -0.012565 | 0.0067908 | 0.009415 | 0.033309 | -0.026608 | 0.01379 | -0.019276 | 0.001048 | 0.010564 | -0.022144 | 0.12538 | 0.10567 | 0.32053 | -0.072215 | 0.023941 | 0.078197 | -0.079245 | 0.015831 | 0.18311 | -0.010564 | -0.23741 | 122.7275 | 0.033829 | 122.8007 | 122.7775 | 0.050071 | 0.014121 | 0.22898 | 122.5623 | -0.075722 | 122.8236 | 122.7204 | 0.15817 | 0.091562 | -0.10212 | 122.9251 | 122.9054 | 123.1202 | 122.8102 | -0.16377 | 122.8155 | 122.9828 | 122.7891 | 122.8779 | -0.32896
4174.25 | 122.9782 | -122.8592 | 0.13275 | 1.4211e-13 | -0.016192 | -0.013291 | -0.04517 | -0.042139 | -0.012993 | -0.00083919 | 0.009415 | 0.033096 | -0.026821 | 0.013577 | -0.019489 | -0.008109 | 0.0243 | -0.017566 | 0.1208 | 0.10567 | 0.32053 | -0.044742 | 0.019362 | 0.082776 | -0.070087 | 0.020409 | 0.18311 | 0.016908 | -0.24657 | 122.8144 | -0.011947 | 122.8511 | 122.8416 | 0.027176 | -0.027077 | 0.18778 | 122.6126 | -0.11234 | 122.8786 | 122.7891 | 0.17648 | 0.050364 | -0.11584 | 122.98 | 122.9649 | 123.1797 | 122.8835 | -0.17749 | 122.8796 | 123.0423 | 122.8761 | 122.942 | -0.37932
4176.0469 | 123.1201 | -122.7859 | 0.082397 | 1.4211e-13 | -0.016406 | -0.013505 | -0.045384 | -0.042139 | -0.012779 | -0.00083919 | 0.009415 | 0.033309 | -0.026608 | 0.013577 | -0.019489 | 0.001048 | 0.0243 | -0.022144 | 0.12996 | 0.1011 | 0.32511 | -0.044742 | 0.019362 | 0.078197 | -0.065509 | 0.020409 | 0.18311 | -0.010564 | -0.24199 | 122.7412 | 0.047563 | 122.787 | 122.7638 | 0.022598 | 0.018698 | 0.24271 | 122.544 | -0.061988 | 122.8053 | 122.7204 | 0.17648 | 0.10072 | -0.092961 | 122.9159 | 122.887 | 123.1111 | 122.8102 | -0.12714 | 122.8064 | 122.9691 | 122.7754 | 122.8641 | -0.32439
4177.8438 | 122.9965 | -122.8729 | 0.1236 | 1.4211e-13 | -0.016833 | -0.013718 | -0.045384 | -0.042566 | -0.012993 | -0.00083919 | 0.009415 | 0.033096 | -0.026608 | 0.013577 | -0.019276 | 0.001048 | 0.019721 | -0.017566 | 0.1208 | 0.10567 | 0.32053 | -0.040163 | 0.023941 | 0.082776 | -0.065509 | 0.015831 | 0.19227 | 0.030644 | -0.23741 | 122.8328 | -0.002792 | 122.874 | 122.8554 | 0.022597 | -0.017922 | 0.19694 | 122.6355 | -0.10776 | 122.8969 | 122.8074 | 0.1719 | 0.068676 | -0.092952 | 122.9937 | 122.9786 | 123.1935 | 122.8926 | -0.16376 | 122.8888 | 123.0652 | 122.9036 | 122.9557 | -0.36101
4179.5938 | 123.0103 | -122.8683 | 0.11902 | 1.4211e-13 | -0.016406 | -0.013291 | -0.04517 | -0.041925 | -0.012993 | -0.00083919 | 0.009415 | 0.033096 | -0.026821 | 0.013577 | -0.019489 | 0.005626 | 0.0243 | -0.017566 | 0.1208 | 0.1011 | 0.31595 | -0.035584 | 0.019362 | 0.078197 | -0.06093 | 0.020409 | 0.17854 | 0.021486 | -0.24199 | 122.8328 | 0.001785 | 122.874 | 122.8508 | 0.018018 | -0.017924 | 0.19693 | 122.6264 | -0.09861 | 122.8877 | 122.8074 | 0.18106 | 0.059517 | -0.097533 | 122.9892 | 122.9694 | 123.1843 | 122.8926 | -0.1546 | 122.8888 | 123.0469 | 122.8898 | 122.9465 | -0.36101
4181.4062 | 123.0469 | -122.85 | 0.12817 | 1.4211e-13 | -0.016619 | -0.013505 | -0.045384 | -0.041925 | -0.012993 | -0.00083919 | 0.009415 | 0.033096 | -0.026821 | 0.013363 | -0.019917 | 0.001048 | 0.019721 | -0.026723 | 0.12538 | 0.1011 | 0.31595 | -0.040163 | 0.019362 | 0.073618 | -0.065509 | 0.015831 | 0.18311 | 0.035222 | -0.24657 | 122.8099 | -0.002792 | 122.8511 | 122.8233 | 0.01344 | -0.027079 | 0.18778 | 122.6035 | -0.11234 | 122.8694 | 122.7845 | 0.18106 | 0.054941 | -0.092952 | 122.9754 | 122.9511 | 123.166 | 122.8698 | -0.16834 | 122.8659 | 123.0332 | 122.8853 | 122.9237 | -0.37474
4183.2031 | 123.1018 | -122.8271 | 0.09613 | 1.4211e-13 | -0.016406 | -0.013291 | -0.045384 | -0.042139 | -0.012779 | -0.0084697 | 0.0096286 | 0.033096 | -0.027035 | 0.013577 | -0.019276 | 0.001048 | 0.0243 | -0.026723 | 0.12538 | 0.10567 | 0.32511 | -0.040163 | 0.019362 | 0.073618 | -0.070087 | 0.024988 | 0.18311 | 0.058115 | -0.24199 | 122.787 | 0.029252 | 122.8282 | 122.8004 | 0.01344 | 0.009544 | 0.22898 | 122.5852 | -0.071142 | 122.8465 | 122.7571 | 0.1719 | 0.086985 | -0.038015 | 122.9525 | 122.9328 | 123.1523 | 122.8514 | -0.13629 | 122.8521 | 123.0103 | 122.8853 | 122.9008 | -0.33812
4185.0156 | 122.9828 | -122.8775 | 0.12817 | 1.4211e-13 | -0.016406 | -0.013718 | -0.04517 | -0.042352 | -0.012779 | 0.0067908 | 0.0096286 | 0.032882 | -0.026608 | 0.013363 | -0.019489 | 0.005626 | 0.019721 | -0.022144 | 0.1208 | 0.096516 | 0.32511 | -0.044742 | 0.023941 | 0.073618 | -0.070087 | 0.015831 | 0.18311 | 0.039801 | -0.24657 | 122.8328 | -0.00737 | 122.8831 | 122.8554 | 0.022598 | -0.031658 | 0.19694 | 122.6309 | -0.11234 | 122.9014 | 122.8074 | 0.17648 | 0.054941 | -0.088373 | 122.9983 | 122.974 | 123.2026 | 122.8972 | -0.17292 | 122.8933 | 123.0606 | 122.9173 | 122.9511 | -0.37474
4186.7656 | 123.0011 | -122.8546 | 0.13733 | 1.4211e-13 | -0.016406 | -0.013718 | -0.04517 | -0.042139 | -0.012779 | -0.0084697 | 0.0096286 | 0.033309 | -0.026821 | 0.01379 | -0.019276 | 0.001048 | 0.015142 | -0.026723 | 0.12538 | 0.1011 | 0.31595 | -0.044742 | 0.023941 | 0.06904 | -0.074666 | 0.024988 | 0.18311 | 0.048958 | -0.25115 | 122.8099 | -0.011947 | 122.8557 | 122.8279 | 0.018019 | -0.036234 | 0.17862 | 122.6035 | -0.11234 | 122.8786 | 122.7799 | 0.17648 | 0.045786 | -0.088371 | 122.98 | 122.9557 | 123.1706 | 122.8698 | -0.18207 | 122.8796 | 123.0377 | 122.9036 | 122.9237 | -0.38848
4188.5625 | 123.0148 | -122.8409 | 0.11902 | 1.4211e-13 | -0.016406 | -0.013291 | -0.045384 | -0.041925 | -0.012779 | 0.0067908 | 0.009415 | 0.033309 | -0.027035 | 0.013577 | -0.019489 | -0.003531 | 0.019721 | -0.022144 | 0.1208 | 0.096516 | 0.32053 | -0.049321 | 0.014784 | 0.073618 | -0.074666 | 0.020409 | 0.18769 | 0.039801 | -0.24657 | 122.7916 | 0.001785 | 122.8374 | 122.8187 | 0.027177 | -0.022503 | 0.20151 | 122.5943 | -0.09861 | 122.8557 | 122.7662 | 0.1719 | 0.068674 | -0.079218 | 122.9617 | 122.9374 | 123.1614 | 122.8606 | -0.16834 | 122.8613 | 123.0286 | 122.8807 | 122.9145 | -0.36559
4190.3125 | 123.0423 | -122.85 | 0.1236 | 1.4211e-13 | -0.017047 | -0.013505 | -0.045598 | -0.042139 | -0.012565 | -0.00083919 | 0.0092014 | 0.033523 | -0.026821 | 0.013363 | -0.019276 | 0.001048 | 0.015142 | -0.017566 | 0.1208 | 0.1011 | 0.31595 | -0.026426 | 0.019362 | 0.082776 | -0.070087 | 0.015831 | 0.19227 | 0.026065 | -0.24199 | 122.8236 | -0.002792 | 122.8511 | 122.8325 | 0.00886 | -0.022501 | 0.19236 | 122.608 | -0.10776 | 122.8694 | 122.7799 | 0.1719 | 0.068676 | -0.097531 | 122.9708 | 122.9511 | 123.166 | 122.8652 | -0.15002 | 122.8659 | 123.0423 | 122.8761 | 122.9328 | -0.36558
4192.1094 | 123.1293 | -122.8546 | 0.086975 | 1.4211e-13 | -0.016619 | -0.013505 | -0.04517 | -0.042352 | -0.012779 | -0.00083919 | 0.009415 | 0.033309 | -0.026821 | 0.013577 | -0.019489 | -0.003531 | 0.015142 | -0.026723 | 0.11622 | 0.10567 | 0.31595 | -0.040163 | 0.023941 | 0.078197 | -0.074666 | 0.015831 | 0.18769 | 0.062694 | -0.23741 | 122.8145 | 0.02925 | 122.8511 | 122.8279 | 0.01344 | 0.018699 | 0.22898 | 122.6172 | -0.071144 | 122.8786 | 122.7799 | 0.16274 | 0.10072 | -0.024281 | 122.9708 | 122.9603 | 123.1706 | 122.8698 | -0.12714 | 122.8704 | 123.0423 | 122.9173 | 122.9328 | -0.32439
4193.9062 | 123.1338 | -122.8088 | 0.086975 | 1.4211e-13 | -0.016619 | -0.013505 | -0.045384 | -0.042352 | -0.012779 | 0.0067908 | 0.0092014 | 0.033309 | -0.026821 | 0.013577 | -0.019703 | 0.005626 | 0.0243 | -0.026723 | 0.1208 | 0.10567 | 0.32511 | -0.040163 | 0.023941 | 0.078197 | -0.074666 | 0.011252 | 0.18311 | 0.016908 | -0.23283 | 122.7687 | 0.033829 | 122.8145 | 122.7821 | 0.01344 | 0.018699 | 0.23814 | 122.576 | -0.075723 | 122.8328 | 122.7342 | 0.15817 | 0.09614 | -0.070067 | 122.9296 | 122.9145 | 123.1339 | 122.8331 | -0.12714 | 122.8201 | 122.992 | 122.8257 | 122.887 | -0.31981
4195.6562 | 122.9965 | -122.8592 | 0.13275 | 1.4211e-13 | -0.016619 | -0.013505 | -0.045384 | -0.042139 | -0.012779 | 0.0067908 | 0.009415 | 0.033309 | -0.026608 | 0.01379 | -0.019489 | -0.003531 | 0.015142 | -0.035879 | 0.12538 | 0.10567 | 0.32511 | 0.001048 | 0.023941 | 0.078197 | -0.079245 | 0.015831 | 0.18311 | -0.005985 | -0.23741 | 122.8602 | -0.007369 | 122.8557 | 122.8233 | -0.036927 | -0.027077 | 0.19236 | 122.6218 | -0.11692 | 122.8831 | 122.7799 | 0.15817 | 0.050364 | -0.13874 | 122.9846 | 122.9649 | 123.1843 | 122.8743 | -0.1317 | 122.875 | 123.0423 | 122.8532 | 122.9374 | -0.37016
4197.4375 | 123.0331 | -122.8134 | 0.11902 | 1.4211e-13 | -0.016619 | -0.013077 | -0.045384 | -0.041711 | -0.012779 | -0.0084697 | 0.009415 | 0.033309 | -0.026821 | 0.013577 | -0.019276 | -0.003531 | 0.019721 | -0.026723 | 0.1208 | 0.096516 | 0.32511 | -0.063057 | 0.023941 | 0.073618 | -0.070087 | 0.015831 | 0.19227 | 0.030644 | -0.23741 | 122.7504 | 0.001785 | 122.8099 | 122.7867 | 0.036334 | -0.022503 | 0.20609 | 122.576 | -0.10319 | 122.8374 | 122.7433 | 0.16732 | 0.073253 | -0.088375 | 122.9342 | 122.9099 | 123.1385 | 122.8331 | -0.18208 | 122.8292 | 123.0057 | 122.8441 | 122.887 | -0.35643
4199.1719 | 123.0927 | -122.8317 | 0.10986 | 1.4211e-13 | -0.016619 | -0.013718 | -0.04517 | -0.041925 | -0.012352 | 0.0067908 | 0.0092014 | 0.033309 | -0.027035 | 0.013577 | -0.019276 | -0.008109 | 0.019721 | -0.017566 | 0.1208 | 0.1011 | 0.32053 | -0.049321 | 0.02852 | 0.078197 | -0.074666 | 0.015831 | 0.18769 | 0.016908 | -0.24657 | 122.7824 | 0.010941 | 122.8236 | 122.8142 | 0.031755 | -0.008768 | 0.21067 | 122.5852 | -0.094032 | 122.8602 | 122.7571 | 0.1719 | 0.07783 | -0.092955 | 122.9525 | 122.9328 | 123.1523 | 122.8514 | -0.15918 | 122.8476 | 123.0194 | 122.8486 | 122.9099 | -0.35643
4200.9062 | 123.0515 | -122.8592 | 0.10529 | 1.4211e-13 | -0.016619 | -0.013932 | -0.045384 | -0.042566 | -0.012779 | -0.00083919 | 0.009415 | 0.033096 | -0.027035 | 0.013363 | -0.019062 | 0.010204 | 0.019721 | -0.017566 | 0.12996 | 0.10567 | 0.31595 | -0.053899 | 0.023941 | 0.06904 | -0.070087 | 0.020409 | 0.17396 | 0.053537 | -0.24657 | 122.8053 | 0.024674 | 122.8694 | 122.8416 | 0.036333 | 0.000388 | 0.21067 | 122.6126 | -0.084877 | 122.8831 | 122.7891 | 0.17648 | 0.068672 | -0.051749 | 122.9892 | 122.9649 | 123.1751 | 122.8789 | -0.15919 | 122.8796 | 123.0331 | 122.9127 | 122.9282 | -0.35185
4202.7031 | 123.0286 | -122.8775 | 0.10529 | 1.4211e-13 | -0.016619 | -0.013505 | -0.045384 | -0.041925 | -0.012779 | 0.0067908 | 0.0092014 | 0.033096 | -0.026821 | 0.013149 | -0.019489 | 0.001048 | 0.015142 | -0.022144 | 0.1208 | 0.10567 | 0.32511 | -0.058478 | 0.023941 | 0.078197 | -0.070087 | 0.015831 | 0.19227 | 0.044379 | -0.24199 | 122.819 | 0.015518 | 122.8786 | 122.8554 | 0.036334 | 0.000388 | 0.21982 | 122.6355 | -0.089455 | 122.9014 | 122.8074 | 0.1719 | 0.086986 | -0.060907 | 122.9983 | 122.9832 | 123.2026 | 122.8926 | -0.16376 | 122.8933 | 123.0698 | 122.9219 | 122.9557 | -0.34728
4204.5 | 123.0927 | -122.8638 | 0.10529 | 1.4211e-13 | -0.017047 | -0.013505 | -0.045384 | -0.042139 | -0.012565 | 0.0067908 | 0.0096286 | 0.032882 | -0.026821 | 0.013363 | -0.019489 | -0.008109 | 0.019721 | -0.026723 | 0.12538 | 0.10567 | 0.32511 | -0.085952 | 0.023941 | 0.078197 | -0.065509 | 0.011252 | 0.19227 | 0.007751 | -0.23741 | 122.7778 | 0.020096 | 122.8557 | 122.837 | 0.059229 | 0.000388 | 0.21982 | 122.6264 | -0.094034 | 122.8877 | 122.7983 | 0.1719 | 0.086986 | -0.097535 | 122.9892 | 122.9694 | 123.1889 | 122.8835 | -0.19124 | 122.875 | 123.056 | 122.8715 | 122.942 | -0.3427
4206.2344 | 123.024 | -122.8867 | 0.1236 | 1.4211e-13 | -0.016833 | -0.013505 | -0.045598 | -0.042352 | -0.012779 | -0.00083919 | 0.0092014 | 0.033096 | -0.026821 | 0.013577 | -0.019489 | -0.003531 | 0.019721 | -0.022144 | 0.12538 | 0.11025 | 0.32053 | -0.049321 | 0.019362 | 0.078197 | -0.065509 | 0.020409 | 0.18311 | -0.028878 | -0.24199 | 122.8373 | 0.001786 | 122.8831 | 122.8645 | 0.027177 | -0.013343 | 0.19694 | 122.6447 | -0.10319 | 122.906 | 122.8211 | 0.17648 | 0.059519 | -0.15247 | 123.012 | 122.9969 | 123.2072 | 122.9064 | -0.17292 | 122.9071 | 123.0698 | 122.8578 | 122.9649 | -0.36558
4208.0312 | 123.0286 | -122.8683 | 0.14191 | 1.4211e-13 | -0.016406 | -0.013291 | -0.045384 | -0.041711 | -0.012565 | -0.0084697 | 0.0096286 | 0.033523 | -0.026821 | 0.013363 | -0.019489 | -0.003531 | 0.019721 | -0.022144 | 0.1208 | 0.1011 | 0.32053 | -0.049321 | 0.019362 | 0.073618 | -0.074666 | 0.015831 | 0.18311 | 0.053537 | -0.24657 | 122.819 | -0.021103 | 122.8648 | 122.8462 | 0.027177 | -0.040812 | 0.17862 | 122.6218 | -0.12608 | 122.8877 | 122.7937 | 0.1719 | 0.041208 | -0.08837 | 122.9892 | 122.9694 | 123.1889 | 122.8881 | -0.19123 | 122.8842 | 123.0515 | 122.9219 | 122.942 | -0.38847
4209.8438 | 123.056 | -122.8683 | 0.10529 | 1.4211e-13 | -0.016833 | -0.013505 | -0.04517 | -0.042139 | -0.012779 | -0.00083919 | 0.009415 | 0.033523 | -0.026821 | 0.013363 | -0.019276 | 0.005626 | 0.015142 | -0.026723 | 0.12538 | 0.11025 | 0.32053 | -0.044742 | 0.023941 | 0.078197 | -0.074666 | 0.015831 | 0.19227 | 0.021486 | -0.24657 | 122.8236 | 0.020096 | 122.874 | 122.8416 | 0.018019 | 0.004967 | 0.21525 | 122.6218 | -0.089455 | 122.8923 | 122.7937 | 0.1719 | 0.086986 | -0.0838 | 122.9937 | 122.9786 | 123.1889 | 122.8835 | -0.15003 | 122.8842 | 123.0606 | 122.8898 | 122.9465 | -0.35185
4211.5781 | 123.0698 | -122.8592 | 0.12817 | 1.4211e-13 | -0.016619 | -0.013291 | -0.04517 | -0.041925 | -0.012993 | -0.0084697 | 0.0096286 | 0.033309 | -0.026821 | 0.013363 | -0.019489 | 0.001048 | 0.019721 | -0.022144 | 0.11622 | 0.10567 | 0.32053 | -0.058478 | 0.019362 | 0.073618 | -0.070087 | 0.015831 | 0.18769 | 0.012329 | -0.23283 | 122.8007 | -0.011949 | 122.8602 | 122.837 | 0.036334 | -0.0225 | 0.19236 | 122.6264 | -0.11234 | 122.8786 | 122.7891 | 0.16274 | 0.059519 | -0.11585 | 122.9754 | 122.9649 | 123.1797 | 122.8789 | -0.18665 | 122.875 | 123.0469 | 122.8715 | 122.9328 | -0.36101
4213.3594 | 123.0469 | -122.8683 | 0.13733 | 1.4211e-13 | -0.016406 | -0.013505 | -0.045384 | -0.041711 | -0.012993 | -0.00083919 | 0.0096286 | 0.033096 | -0.026821 | 0.013363 | -0.019276 | 0.001048 | 0.019721 | -0.022144 | 0.12996 | 0.091937 | 0.31595 | -0.049321 | 0.019362 | 0.073618 | -0.070087 | 0.020409 | 0.19685 | 0.012329 | -0.24199 | 122.819 | -0.007369 | 122.8694 | 122.8462 | 0.027177 | -0.045392 | 0.17862 | 122.6264 | -0.11692 | 122.8877 | 122.7983 | 0.1719 | 0.059522 | -0.125 | 122.9983 | 122.9603 | 123.1843 | 122.8881 | -0.18665 | 122.8888 | 123.0652 | 122.8807 | 122.942 | -0.37932
4215.1562 | 123.0469 | -122.8958 | 0.11444 | 1.4211e-13 | -0.016619 | -0.013505 | -0.045598 | -0.042139 | -0.012779 | 0.0067908 | 0.009415 | 0.032882 | -0.027035 | 0.013577 | -0.019276 | -0.008109 | 0.010564 | -0.022144 | 0.12538 | 0.1011 | 0.32511 | -0.031005 | 0.023941 | 0.073618 | -0.079245 | 0.015831 | 0.18311 | 0.039801 | -0.24199 | 122.8648 | 0.010941 | 122.8877 | 122.8737 | 0.008861 | -0.013346 | 0.21067 | 122.6538 | -0.09861 | 122.9198 | 122.8166 | 0.16274 | 0.068674 | -0.07464 | 123.0212 | 122.9969 | 123.2209 | 122.9064 | -0.14545 | 122.9116 | 123.0789 | 122.9356 | 122.9694 | -0.35643
4216.9531 | 123.024 | -122.8912 | 0.13275 | 1.4211e-13 | -0.016406 | -0.013291 | -0.045598 | -0.042139 | -0.012779 | -0.0084697 | 0.0092014 | 0.033096 | -0.026821 | 0.013363 | -0.019489 | 0.005626 | 0.015142 | -0.031301 | 0.1208 | 0.096516 | 0.32969 | -0.017268 | 0.023941 | 0.073618 | -0.06093 | 0.015831 | 0.18769 | 0.003172 | -0.24199 | 122.874 | -0.011947 | 122.8969 | 122.8599 | -0.014033 | -0.036235 | 0.19694 | 122.6492 | -0.11692 | 122.9152 | 122.8303 | 0.18106 | 0.054942 | -0.12958 | 123.012 | 122.9878 | 123.2209 | 122.9064 | -0.15002 | 122.9071 | 123.0789 | 122.8944 | 122.9649 | -0.37474
4218.75 | 123.1338 | -122.8317 | 0.082397 | 1.4211e-13 | -0.016406 | -0.013505 | -0.04517 | -0.042352 | -0.012565 | -0.0084697 | 0.0092014 | 0.033309 | -0.026608 | 0.013577 | -0.019062 | 0.001048 | 0.0243 | -0.017566 | 0.1208 | 0.10567 | 0.32969 | -0.081373 | 0.023941 | 0.078197 | -0.070087 | 0.015831 | 0.18769 | 0.053537 | -0.24199 | 122.7504 | 0.038407 | 122.8328 | 122.8142 | 0.063807 | 0.023277 | 0.24729 | 122.5897 | -0.066566 | 122.8557 | 122.7616 | 0.1719 | 0.1053 | -0.02886 | 122.9525 | 122.9374 | 123.1614 | 122.856 | -0.16377 | 122.8476 | 123.0194 | 122.8853 | 122.9099 | -0.32439
4220.5625 | 123.143 | -122.8363 | 0.068665 | 1.4211e-13 | -0.016406 | -0.013505 | -0.045384 | -0.042139 | -0.012565 | 0.0067908 | 0.009415 | 0.033309 | -0.026821 | 0.013363 | -0.019703 | 0.001048 | 0.0243 | -0.022144 | 0.12538 | 0.10567 | 0.32053 | -0.040163 | 0.023941 | 0.073618 | -0.074666 | 0.015831 | 0.18311 | 0.039801 | -0.24199 | 122.7961 | 0.056717 | 122.8374 | 122.8142 | 0.018019 | 0.037009 | 0.25187 | 122.5943 | -0.052834 | 122.8602 | 122.7616 | 0.16732 | 0.11445 | -0.028864 | 122.9617 | 122.942 | 123.1568 | 122.8606 | -0.10883 | 122.8521 | 123.0194 | 122.8761 | 122.9099 | -0.31065
4222.2969 | 123.0286 | -122.8912 | 0.1236 | 1.4211e-13 | -0.016406 | -0.013505 | -0.04517 | -0.041925 | -0.012779 | -0.0084697 | 0.0092014 | 0.033096 | -0.026608 | 0.013577 | -0.019489 | -0.012688 | 0.015142 | -0.026723 | 0.12538 | 0.096516 | 0.31595 | -0.058478 | 0.023941 | 0.073618 | -0.074666 | 0.015831 | 0.18311 | 0.003172 | -0.23741 | 122.8328 | 0.001786 | 122.8785 | 122.8645 | 0.031755 | -0.02708 | 0.19236 | 122.6538 | -0.10776 | 122.9152 | 122.8166 | 0.16274 | 0.059519 | -0.12042 | 123.0166 | 122.9878 | 123.2072 | 122.9064 | -0.18207 | 122.9071 | 123.0743 | 122.8944 | 122.9649 | -0.36101
4224.0625 | 123.1155 | -122.8546 | 0.10529 | 1.4211e-13 | -0.016406 | -0.013505 | -0.04517 | -0.042139 | -0.012993 | 0.0067908 | 0.0092014 | 0.033096 | -0.026821 | 0.013363 | -0.019276 | 0.001048 | 0.019721 | -0.022144 | 0.12996 | 0.10567 | 0.31595 | -0.067636 | 0.023941 | 0.082776 | -0.070087 | 0.015831 | 0.19227 | 0.030644 | -0.24199 | 122.787 | 0.024674 | 122.8557 | 122.8325 | 0.045492 | 0.000388 | 0.21067 | 122.6126 | -0.089455 | 122.8786 | 122.7845 | 0.1719 | 0.086986 | -0.074642 | 122.9846 | 122.9603 | 123.1706 | 122.8743 | -0.17292 | 122.8704 | 123.0469 | 122.8853 | 122.9374 | -0.34728
4225.8125 | 123.024 | -122.8821 | 0.11902 | 1.4211e-13 | -0.016406 | -0.013291 | -0.045384 | -0.042139 | -0.012565 | -0.0084697 | 0.009415 | 0.032882 | -0.026608 | 0.013149 | -0.018848 | 0.001048 | 0.019721 | -0.022144 | 0.1208 | 0.096516 | 0.32053 | -0.090531 | 0.023941 | 0.078197 | -0.074666 | 0.029566 | 0.18769 | 0.058115 | -0.24199 | 122.7915 | 0.001785 | 122.8831 | 122.8599 | 0.068387 | -0.022503 | 0.20151 | 122.6401 | -0.089453 | 122.906 | 122.8074 | 0.16732 | 0.068674 | -0.060904 | 123.0029 | 122.9786 | 123.2026 | 122.9018 | -0.20955 | 122.9116 | 123.0698 | 122.9402 | 122.9603 | -0.36101
4227.6094 | 123.0057 | -122.9095 | 0.11444 | 1.4211e-13 | -0.016619 | -0.013291 | -0.045384 | -0.041711 | -0.012779 | 0.0067908 | 0.0092014 | 0.033737 | -0.027035 | 0.013363 | -0.019276 | -0.008109 | 0.015142 | -0.017566 | 0.1208 | 0.1011 | 0.32053 | -0.072215 | 0.019362 | 0.073618 | -0.070087 | 0.011252 | 0.19227 | 0.048958 | -0.23741 | 122.8373 | 0.006363 | 122.9014 | 122.892 | 0.054649 | -0.013346 | 0.20609 | 122.6721 | -0.10319 | 122.9289 | 122.8395 | 0.16732 | 0.077831 | -0.065483 | 123.0304 | 123.0106 | 123.2301 | 122.9247 | -0.18666 | 122.9208 | 123.1018 | 122.9585 | 122.9832 | -0.35185
4229.3438 | 123.0148 | -122.8912 | 0.12817 | 1.4211e-13 | -0.016619 | -0.012863 | -0.045598 | -0.042352 | -0.012779 | 0.0067908 | 0.009415 | 0.033096 | -0.026608 | 0.013363 | -0.019489 | -0.003531 | 0.019721 | -0.026723 | 0.12538 | 0.096516 | 0.32511 | -0.067636 | 0.019362 | 0.078197 | -0.070087 | 0.011252 | 0.19227 | 0.012329 | -0.23741 | 122.8236 | -0.002792 | 122.8877 | 122.8645 | 0.040913 | -0.031658 | 0.19694 | 122.6538 | -0.11692 | 122.9106 | 122.8211 | 0.16732 | 0.064098 | -0.11585 | 123.0166 | 122.9878 | 123.2163 | 122.911 | -0.19581 | 122.9025 | 123.0835 | 122.9036 | 122.9694 | -0.36558
4231.125 | 123.1476 | -122.8455 | 0.11444 | 1.4211e-13 | -0.016192 | -0.013505 | -0.045598 | -0.042139 | -0.012565 | 0.0067908 | 0.0092014 | 0.032882 | -0.026821 | 0.013363 | -0.019489 | -0.003531 | 0.0243 | -0.022144 | 0.12538 | 0.10567 | 0.32053 | -0.049321 | 0.023941 | 0.078197 | -0.074666 | 0.024988 | 0.19227 | 0.053537 | -0.24199 | 122.7961 | 0.010941 | 122.8419 | 122.8233 | 0.027177 | -0.008767 | 0.20609 | 122.6035 | -0.089453 | 122.8694 | 122.7708 | 0.16732 | 0.077831 | -0.060904 | 122.9708 | 122.9511 | 123.166 | 122.8698 | -0.16376 | 122.8704 | 123.0377 | 122.899 | 122.9237 | -0.35643
4232.9219 | 123.143 | -122.8363 | 0.082397 | 1.4211e-13 | -0.016406 | -0.013291 | -0.045384 | -0.042352 | -0.012565 | -0.00083919 | 0.0089876 | 0.033096 | -0.026821 | 0.013577 | -0.019276 | -0.008109 | 0.015142 | -0.022144 | 0.11622 | 0.1011 | 0.32511 | -0.067636 | 0.023941 | 0.082776 | -0.070087 | 0.015831 | 0.18311 | 0.039801 | -0.23741 | 122.7687 | 0.033828 | 122.8282 | 122.8142 | 0.045492 | 0.018698 | 0.24271 | 122.5989 | -0.066566 | 122.8602 | 122.7662 | 0.16732 | 0.10072 | -0.042596 | 122.9525 | 122.9374 | 123.1614 | 122.8514 | -0.15003 | 122.8521 | 123.0194 | 122.8761 | 122.9191 | -0.31981
4234.7031 | 123.0972 | -122.8455 | 0.09613 | 1.4211e-13 | -0.016619 | -0.013718 | -0.045384 | -0.042139 | -0.012565 | -0.0084697 | 0.0092014 | 0.033523 | -0.026821 | 0.013577 | -0.019276 | -0.003531 | 0.015142 | -0.022144 | 0.1208 | 0.10567 | 0.32053 | -0.031005 | 0.02852 | 0.082776 | -0.070087 | 0.011252 | 0.19227 | 0.044379 | -0.24657 | 122.8145 | 0.024674 | 122.8419 | 122.8233 | 0.008861 | 0.009544 | 0.2244 | 122.5989 | -0.084878 | 122.874 | 122.7754 | 0.17648 | 0.096142 | -0.051751 | 122.9663 | 122.9511 | 123.166 | 122.8606 | -0.12713 | 122.8567 | 123.0377 | 122.8898 | 122.9282 | -0.3427
4236.5 | 123.0286 | -122.8958 | 0.13275 | 1.4211e-13 | -0.016406 | -0.013291 | -0.045384 | -0.042352 | -0.012993 | 0.0067908 | 0.0092014 | 0.033309 | -0.026608 | 0.013577 | -0.019276 | -0.003531 | 0.015142 | -0.031301 | 0.1208 | 0.10567 | 0.32511 | -0.063057 | 0.023941 | 0.073618 | -0.070087 | 0.020409 | 0.18769 | 0.053537 | -0.24199 | 122.8328 | -0.011947 | 122.8923 | 122.8645 | 0.031756 | -0.027077 | 0.19236 | 122.6538 | -0.11234 | 122.9198 | 122.8257 | 0.1719 | 0.054942 | -0.079214 | 123.0166 | 123.0015 | 123.2209 | 122.911 | -0.19581 | 122.9162 | 123.0835 | 122.9494 | 122.9694 | -0.37474
4238.2969 | 123.0377 | -122.8729 | 0.10986 | 1.4211e-13 | -0.016192 | -0.013505 | -0.04517 | -0.042139 | -0.012779 | 0.0067908 | 0.0092014 | 0.033523 | -0.027035 | 0.013149 | -0.019489 | 0.001048 | 0.015142 | -0.022144 | 0.1208 | 0.11025 | 0.32053 | -0.040163 | 0.019362 | 0.078197 | -0.070087 | 0.020409 | 0.18769 | -0.010564 | -0.23741 | 122.8328 | 0.010941 | 122.874 | 122.8508 | 0.018019 | 0.00039 | 0.21067 | 122.6355 | -0.089454 | 122.8923 | 122.8028 | 0.16732 | 0.07783 | -0.12043 | 122.9937 | 122.9832 | 123.1935 | 122.8881 | -0.15003 | 122.8933 | 123.0606 | 122.8624 | 122.9511 | -0.34727
4240.0312 | 123.0423 | -122.8775 | 0.12817 | 1.4211e-13 | -0.016619 | -0.013505 | -0.045384 | -0.041925 | -0.012565 | 0.0067908 | 0.0092014 | 0.033523 | -0.026608 | 0.013363 | -0.019276 | -0.003531 | 0.019721 | -0.022144 | 0.1208 | 0.1011 | 0.32053 | -0.072215 | 0.023941 | 0.082776 | -0.070087 | 0.024988 | 0.18769 | 0.026065 | -0.23741 | 122.8053 | -0.00737 | 122.874 | 122.8554 | 0.050071 | -0.027079 | 0.19236 | 122.6401 | -0.10319 | 122.9014 | 122.8074 | 0.16732 | 0.059519 | -0.10211 | 122.9983 | 122.9786 | 123.198 | 122.8972 | -0.20039 | 122.9025 | 123.0652 | 122.9036 | 122.9603 | -0.36558
4241.8281 | 123.0835 | -122.8958 | 0.1236 | 1.4211e-13 | -0.016406 | -0.013291 | -0.045384 | -0.041925 | -0.012779 | -0.0084697 | 0.009415 | 0.033523 | -0.026821 | 0.013149 | -0.019276 | 0.001048 | 0.015142 | -0.017566 | 0.1208 | 0.1011 | 0.32511 | -0.044742 | 0.02852 | 0.06904 | -0.070087 | 0.029566 | 0.19227 | 0.053537 | -0.24199 | 122.8511 | -0.002792 | 122.8969 | 122.8782 | 0.027176 | -0.022501 | 0.20151 | 122.6538 | -0.09403 | 122.9243 | 122.8257 | 0.1719 | 0.068676 | -0.070059 | 123.0166 | 122.9969 | 123.2209 | 122.911 | -0.16834 | 122.9254 | 123.0881 | 122.9494 | 122.9649 | -0.36558
4243.625 | 123.1201 | -122.85 | 0.09613 | 1.4211e-13 | -0.016406 | -0.013505 | -0.044957 | -0.042352 | -0.012779 | 0.0067908 | 0.0089876 | 0.033096 | -0.026394 | 0.013363 | -0.019703 | -0.003531 | 0.010564 | -0.017566 | 0.12996 | 0.11025 | 0.32511 | -0.058478 | 0.019362 | 0.082776 | -0.074666 | 0.011252 | 0.18769 | 0.053537 | -0.23741 | 122.7916 | 0.03383 | 122.8465 | 122.8325 | 0.040912 | 0.014123 | 0.22898 | 122.6126 | -0.084878 | 122.8694 | 122.7754 | 0.16274 | 0.091563 | -0.042593 | 122.98 | 122.9603 | 123.1751 | 122.8606 | -0.15461 | 122.8613 | 123.0377 | 122.9036 | 122.9328 | -0.33354
4245.4375 | 123.1064 | -122.8271 | 0.091553 | 1.4211e-13 | -0.016406 | -0.013291 | -0.045384 | -0.041925 | -0.012779 | -0.0084697 | 0.0092014 | 0.033309 | -0.027035 | 0.01379 | -0.019062 | 0.001048 | 0.0243 | -0.017566 | 0.12538 | 0.10567 | 0.32969 | -0.063057 | 0.02852 | 0.078197 | -0.079245 | 0.020409 | 0.18769 | 0.030644 | -0.24199 | 122.7641 | 0.033829 | 122.8282 | 122.8096 | 0.045491 | 0.014121 | 0.23814 | 122.5852 | -0.071144 | 122.8557 | 122.7479 | 0.16274 | 0.09614 | -0.060909 | 122.9525 | 122.9328 | 123.1568 | 122.8514 | -0.15461 | 122.8476 | 123.0148 | 122.8578 | 122.9053 | -0.33354
4247.2344 | 123.1567 | -122.8271 | 0.091553 | 1.4211e-13 | -0.016406 | -0.013505 | -0.045384 | -0.042139 | -0.012779 | -0.00083919 | 0.0092014 | 0.033309 | -0.027035 | 0.013577 | -0.019489 | 0.001048 | 0.015142 | -0.022144 | 0.1208 | 0.10567 | 0.32511 | -0.063057 | 0.019362 | 0.078197 | -0.070087 | 0.015831 | 0.18311 | -0.001407 | -0.23741 | 122.7641 | 0.029251 | 122.8282 | 122.805 | 0.040913 | 0.014121 | 0.23356 | 122.5897 | -0.075722 | 122.8465 | 122.7571 | 0.16732 | 0.091562 | -0.09296 | 122.948 | 122.9328 | 123.1523 | 122.8423 | -0.15461 | 122.843 | 123.0103 | 122.8257 | 122.9053 | -0.32896
4248.9688 | 123.0972 | -122.8683 | 0.10986 | 1.4211e-13 | -0.016406 | -0.013291 | -0.045384 | -0.042139 | -0.012993 | 0.0067908 | 0.008774 | 0.033309 | -0.026821 | 0.013577 | -0.019062 | -0.003531 | 0.005985 | -0.026723 | 0.12996 | 0.096516 | 0.32511 | -0.067636 | 0.023941 | 0.073618 | -0.079245 | 0.015831 | 0.18769 | 0.007751 | -0.23741 | 122.8007 | 0.020097 | 122.8648 | 122.8416 | 0.040913 | -0.013347 | 0.21525 | 122.6309 | -0.094032 | 122.8923 | 122.7891 | 0.15817 | 0.07783 | -0.10211 | 122.9983 | 122.9649 | 123.1935 | 122.8743 | -0.1775 | 122.8842 | 123.056 | 122.8761 | 122.942 | -0.34727
4250.7656 | 123.0423 | -122.905 | 0.12817 | 1.4211e-13 | -0.016406 | -0.013077 | -0.04517 | -0.042139 | -0.012993 | -0.0084697 | 0.0092014 | 0.033309 | -0.026608 | 0.013577 | -0.019276 | 0.005626 | 0.015142 | -0.022144 | 0.12538 | 0.10567 | 0.32511 | -0.099689 | 0.02852 | 0.073618 | -0.070087 | 0.020409 | 0.18311 | 0.048958 | -0.25115 | 122.8053 | -0.002792 | 122.9106 | 122.8828 | 0.077545 | -0.0225 | 0.19694 | 122.6538 | -0.10777 | 122.9335 | 122.8349 | 0.18106 | 0.054941 | -0.079216 | 123.0303 | 123.0106 | 123.2301 | 122.9201 | -0.22786 | 122.9254 | 123.0881 | 122.9539 | 122.9786 | -0.37932
4252.5 | 123.1705 | -122.8546 | 0.07782 | 1.4211e-13 | -0.016406 | -0.013505 | -0.045598 | -0.041925 | -0.012993 | -0.00083919 | 0.009415 | 0.033737 | -0.026821 | 0.013363 | -0.019062 | 0.001048 | 0.015142 | -0.017566 | 0.12538 | 0.1011 | 0.32053 | -0.076794 | 0.023941 | 0.087354 | -0.074666 | 0.024988 | 0.18769 | 0.021486 | -0.23741 | 122.7778 | 0.047562 | 122.8557 | 122.837 | 0.059228 | 0.023275 | 0.24271 | 122.6172 | -0.052832 | 122.8786 | 122.7799 | 0.16274 | 0.10987 | -0.056334 | 122.98 | 122.9557 | 123.1751 | 122.8698 | -0.15461 | 122.8796 | 123.0423 | 122.8761 | 122.942 | -0.31523
4254.2812 | 123.0972 | -122.8683 | 0.10071 | 1.4211e-13 | -0.016192 | -0.013291 | -0.045384 | -0.041711 | -0.012565 | -0.0084697 | 0.0092014 | 0.033309 | -0.026394 | 0.013363 | -0.019489 | 0.005626 | 0.0243 | -0.017566 | 0.12996 | 0.10567 | 0.32969 | -0.053899 | 0.019362 | 0.078197 | -0.074666 | 0.015831 | 0.18769 | 0.044379 | -0.23741 | 122.8144 | 0.029252 | 122.874 | 122.8508 | 0.036333 | 0.004966 | 0.22898 | 122.6309 | -0.084877 | 122.8877 | 122.7937 | 0.16274 | 0.086985 | -0.056329 | 122.9983 | 122.974 | 123.198 | 122.8926 | -0.15461 | 122.8842 | 123.056 | 122.9127 | 122.9465 | -0.33812
4256.0156 | 123.0972 | -122.8775 | 0.11902 | 1.4211e-13 | -0.016192 | -0.013291 | -0.045384 | -0.042139 | -0.012779 | 0.0067908 | 0.0092014 | 0.033523 | -0.026394 | 0.013363 | -0.019703 | -0.003531 | 0.019721 | -0.026723 | 0.12538 | 0.10567 | 0.32511 | -0.040163 | 0.023941 | 0.082776 | -0.074666 | 0.024988 | 0.19227 | 0.021486 | -0.24199 | 122.8373 | 0.006363 | 122.874 | 122.8508 | 0.01344 | -0.013345 | 0.20609 | 122.6355 | -0.094031 | 122.9014 | 122.8028 | 0.16732 | 0.073253 | -0.097533 | 123.0029 | 122.9832 | 123.2026 | 122.8972 | -0.15918 | 122.9025 | 123.0698 | 122.899 | 122.9603 | -0.36101
4257.8281 | 123.0789 | -122.905 | 0.10071 | 1.4211e-13 | -0.016406 | -0.013291 | -0.04517 | -0.042352 | -0.012779 | -0.00083919 | 0.0092014 | 0.033096 | -0.026821 | 0.012936 | -0.019276 | -0.003531 | 0.0243 | -0.026723 | 0.1208 | 0.1011 | 0.32053 | -0.063057 | 0.019362 | 0.078197 | -0.070087 | 0.015831 | 0.18311 | 0.030644 | -0.24199 | 122.8419 | 0.020096 | 122.9014 | 122.8782 | 0.036334 | 0.000387 | 0.21982 | 122.663 | -0.084877 | 122.9243 | 122.8349 | 0.1719 | 0.082407 | -0.070064 | 123.0258 | 123.0061 | 123.2255 | 122.9293 | -0.16376 | 122.9208 | 123.0881 | 122.9356 | 122.9832 | -0.3427
4259.5625 | 123.1155 | -122.8683 | 0.10071 | 1.4211e-13 | -0.016192 | -0.013505 | -0.045384 | -0.042139 | -0.012779 | 0.0067908 | 0.0089876 | 0.033309 | -0.026181 | 0.013577 | -0.019489 | 0.001048 | 0.019721 | -0.022144 | 0.12538 | 0.096516 | 0.32511 | -0.085952 | 0.014784 | 0.087354 | -0.070087 | 0.020409 | 0.18769 | 0.021486 | -0.23283 | 122.7824 | 0.024674 | 122.8694 | 122.8462 | 0.063808 | -0.004192 | 0.2244 | 122.6355 | -0.080299 | 122.8831 | 122.7983 | 0.16274 | 0.086985 | -0.079222 | 122.9937 | 122.9649 | 123.1935 | 122.8881 | -0.18666 | 122.8888 | 123.056 | 122.8898 | 122.9557 | -0.33354
4261.3438 | 123.1293 | -122.8683 | 0.091553 | 1.4211e-13 | -0.016406 | -0.013505 | -0.04517 | -0.042352 | -0.012779 | -0.00083919 | 0.0092014 | 0.033309 | -0.026394 | 0.013363 | -0.019703 | 0.005626 | 0.0243 | -0.026723 | 0.12538 | 0.1011 | 0.32053 | -0.076794 | 0.019362 | 0.078197 | -0.074666 | 0.011252 | 0.19227 | 0.053537 | -0.24199 | 122.7916 | 0.033829 | 122.874 | 122.8416 | 0.050071 | 0.009542 | 0.22898 | 122.6264 | -0.080301 | 122.8877 | 122.7937 | 0.16732 | 0.10072 | -0.038016 | 122.9937 | 122.9694 | 123.1889 | 122.8926 | -0.16835 | 122.8796 | 123.0606 | 122.9219 | 122.9465 | -0.33354
4263.125 | 123.1476 | -122.8546 | 0.086975 | 1.4211e-13 | -0.016406 | -0.013291 | -0.045384 | -0.041925 | -0.012779 | 0.0067908 | 0.009415 | 0.033309 | -0.026608 | 0.013363 | -0.019703 | 0.001048 | 0.015142 | -0.026723 | 0.1208 | 0.096516 | 0.32053 | -0.044742 | 0.023941 | 0.082776 | -0.074666 | 0.015831 | 0.18311 | 0.058115 | -0.23283 | 122.8099 | 0.033829 | 122.8557 | 122.8279 | 0.018019 | 0.009541 | 0.23356 | 122.6218 | -0.071144 | 122.8786 | 122.7799 | 0.15817 | 0.09614 | -0.02886 | 122.9754 | 122.9511 | 123.1751 | 122.8698 | -0.13172 | 122.8704 | 123.0377 | 122.9127 | 122.9374 | -0.31981
4264.8594 | 123.1888 | -122.8729 | 0.082397 | 1.4211e-13 | -0.016192 | -0.013291 | -0.045598 | -0.042139 | -0.013206 | -0.00083919 | 0.0092014 | 0.033309 | -0.026394 | 0.013363 | -0.019276 | -0.003531 | 0.019721 | -0.022144 | 0.1208 | 0.10567 | 0.32511 | -0.040163 | 0.023941 | 0.082776 | -0.074666 | 0.020409 | 0.18769 | 0.016908 | -0.24657 | 122.8328 | 0.038407 | 122.8694 | 122.8508 | 0.018019 | 0.023277 | 0.24271 | 122.6264 | -0.061988 | 122.8969 | 122.7983 | 0.1719 | 0.1053 | -0.065489 | 122.9937 | 122.9786 | 123.198 | 122.8926 | -0.12256 | 122.8933 | 123.0606 | 122.8898 | 122.9557 | -0.32896
4266.6562 | 123.0881 | -122.8592 | 0.10529 | 1.4211e-13 | -0.016192 | -0.012863 | -0.045598 | -0.041925 | -0.012993 | -0.0084697 | 0.009415 | 0.033309 | -0.026821 | 0.01379 | -0.019276 | -0.003531 | 0.015142 | -0.022144 | 0.12538 | 0.1011 | 0.32053 | -0.058478 | 0.02852 | 0.073618 | -0.070087 | 0.020409 | 0.19227 | 0.048958 | -0.24199 | 122.8007 | 0.020096 | 122.8557 | 122.837 | 0.036334 | -0.004191 | 0.21525 | 122.6172 | -0.084877 | 122.8877 | 122.7891 | 0.1719 | 0.086986 | -0.056328 | 122.9846 | 122.9603 | 123.1797 | 122.8743 | -0.16376 | 122.8796 | 123.0515 | 122.9081 | 122.9328 | -0.34728
4268.4531 | 123.0698 | -122.9004 | 0.1236 | 1.4211e-13 | -0.016406 | -0.013291 | -0.045598 | -0.042139 | -0.012779 | -0.00083919 | 0.0092014 | 0.033096 | -0.026608 | 0.01379 | -0.019489 | -0.003531 | 0.015142 | -0.026723 | 0.12538 | 0.096516 | 0.31595 | -0.067636 | 0.019362 | 0.082776 | -0.070087 | 0.020409 | 0.18769 | 0.012329 | -0.23741 | 122.8328 | 0.001786 | 122.8969 | 122.8737 | 0.040913 | -0.02708 | 0.19236 | 122.663 | -0.10319 | 122.9198 | 122.8303 | 0.16732 | 0.064097 | -0.11127 | 123.0258 | 122.9969 | 123.2163 | 122.9155 | -0.19123 | 122.9208 | 123.0881 | 122.9127 | 122.9832 | -0.36101
4270.1719 | 123.0743 | -122.8958 | 0.11444 | 1.4211e-13 | -0.016406 | -0.013077 | -0.045384 | -0.042352 | -0.012779 | -0.00083919 | 0.009415 | 0.033523 | -0.026608 | 0.013577 | -0.019489 | 0.005626 | 0.015142 | -0.017566 | 0.1208 | 0.10567 | 0.32511 | -0.044742 | 0.023941 | 0.087354 | -0.070087 | 0.020409 | 0.19227 | 0.053537 | -0.24199 | 122.8511 | 0.006363 | 122.9014 | 122.8782 | 0.027176 | -0.008767 | 0.21067 | 122.6538 | -0.094032 | 122.9198 | 122.8257 | 0.1719 | 0.077831 | -0.060904 | 123.0166 | 123.0015 | 123.2209 | 122.911 | -0.15918 | 122.9162 | 123.0881 | 122.9494 | 122.9832 | -0.35643
4271.9688 | 123.0927 | -122.8775 | 0.10529 | 1.4211e-13 | -0.016619 | -0.013505 | -0.045384 | -0.042352 | -0.012779 | -0.00083919 | 0.0089876 | 0.033523 | -0.026181 | 0.013363 | -0.019489 | 0.001048 | 0.015142 | -0.026723 | 0.13454 | 0.1011 | 0.31595 | -0.063057 | 0.023941 | 0.087354 | -0.074666 | 0.020409 | 0.18769 | -0.001407 | -0.23283 | 122.8144 | 0.029253 | 122.8786 | 122.8508 | 0.036334 | -0.004191 | 0.21067 | 122.6447 | -0.084877 | 122.9014 | 122.8028 | 0.15817 | 0.082407 | -0.10669 | 123.012 | 122.9786 | 123.1935 | 122.8926 | -0.16834 | 122.8979 | 123.0652 | 122.8761 | 122.9649 | -0.33812
4273.7031 | 123.0423 | -122.905 | 0.11902 | 1.4211e-13 | -0.016406 | -0.013505 | -0.045384 | -0.042352 | -0.013206 | -0.00083919 | 0.0089876 | 0.033096 | -0.026608 | 0.013577 | -0.019062 | 0.001048 | 0.019721 | -0.026723 | 0.12996 | 0.096516 | 0.31595 | -0.017268 | 0.019362 | 0.073618 | -0.074666 | 0.015831 | 0.18311 | 0.030644 | -0.24657 | 122.8877 | 0.010941 | 122.906 | 122.8782 | -0.009455 | -0.022503 | 0.19693 | 122.6584 | -0.10319 | 122.9243 | 122.8303 | 0.1719 | 0.064096 | -0.088375 | 123.0349 | 123.0015 | 123.2209 | 122.9247 | -0.13629 | 122.9208 | 123.0881 | 122.9356 | 122.9786 | -0.36559
4275.4844 | 123.1476 | -122.8821 | 0.082397 | 1.4211e-13 | -0.016619 | -0.013505 | -0.045598 | -0.042139 | -0.012993 | -0.00083919 | 0.008774 | 0.033309 | -0.026608 | 0.013577 | -0.019703 | 0.005626 | 0.019721 | -0.017566 | 0.11622 | 0.096516 | 0.32053 | -0.076794 | 0.023941 | 0.073618 | -0.074666 | 0.020409 | 0.18311 | 0.035222 | -0.24657 | 122.8053 | 0.033828 | 122.8877 | 122.8645 | 0.059228 | 0.014119 | 0.23813 | 122.6355 | -0.061988 | 122.906 | 122.8074 | 0.1719 | 0.10072 | -0.047175 | 122.9983 | 122.9786 | 123.2026 | 122.9018 | -0.15919 | 122.9025 | 123.0652 | 122.9173 | 122.9557 | -0.32896
4277.2031 | 123.1293 | -122.8912 | 0.091553 | 1.4211e-13 | -0.016192 | -0.013718 | -0.045384 | -0.041925 | -0.012565 | 0.014421 | 0.009415 | 0.033096 | -0.026608 | 0.01379 | -0.019276 | 0.005626 | 0.019721 | -0.022144 | 0.12538 | 0.10567 | 0.32511 | -0.035584 | 0.023941 | 0.082776 | -0.065509 | 0.024988 | 0.17854 | 0.039801 | -0.24657 | 122.8557 | 0.033829 | 122.8969 | 122.8691 | 0.01344 | 0.014121 | 0.23356 | 122.6447 | -0.066565 | 122.9152 | 122.8257 | 0.18106 | 0.086983 | -0.051752 | 123.0166 | 122.9969 | 123.2163 | 122.911 | -0.12714 | 122.9162 | 123.0698 | 122.931 | 122.974 | -0.33812
4279 | 123.0423 | -122.9095 | 0.1236 | 1.4211e-13 | -0.016406 | -0.013718 | -0.044957 | -0.041925 | -0.01342 | 0.0067908 | 0.0092014 | 0.033523 | -0.026821 | 0.013577 | -0.019276 | 0.001048 | 0.015142 | -0.022144 | 0.12996 | 0.096516 | 0.32053 | -0.049321 | 0.019362 | 0.06904 | -0.065509 | 0.020409 | 0.17854 | -0.005985 | -0.24199 | 122.8602 | 0.006364 | 122.9106 | 122.8874 | 0.027177 | -0.02708 | 0.19694 | 122.6676 | -0.10319 | 122.9289 | 122.844 | 0.17648 | 0.05494 | -0.12958 | 123.0395 | 123.0061 | 123.2301 | 122.9247 | -0.17292 | 122.93 | 123.0881 | 122.9036 | 122.9786 | -0.36558
4280.75 | 123.0789 | -122.905 | 0.13275 | 1.4211e-13 | -0.016406 | -0.013932 | -0.04517 | -0.042139 | -0.012993 | -0.0084697 | 0.0096286 | 0.033096 | -0.027035 | 0.013149 | -0.019062 | 0.001048 | 0.019721 | -0.017566 | 0.12538 | 0.10567 | 0.32969 | -0.076794 | 0.02852 | 0.082776 | -0.070087 | 0.020409 | 0.18311 | 0.044379 | -0.24199 | 122.8282 | -0.007369 | 122.906 | 122.8874 | 0.059228 | -0.027077 | 0.19694 | 122.663 | -0.11234 | 122.9335 | 122.8349 | 0.1719 | 0.050364 | -0.088372 | 123.0303 | 123.0106 | 123.2347 | 122.9247 | -0.20955 | 122.9254 | 123.0881 | 122.9493 | 122.9877 | -0.37474
4282.5469 | 123.0469 | -122.905 | 0.12817 | 1.4211e-13 | -0.016192 | -0.013077 | -0.045598 | -0.042352 | -0.012993 | -0.0084697 | 0.0096286 | 0.033096 | -0.027249 | 0.013577 | -0.019489 | -0.003531 | 0.0243 | -0.022144 | 0.12538 | 0.11025 | 0.32511 | -0.053899 | 0.02852 | 0.082776 | -0.070087 | 0.020409 | 0.18311 | 0.039801 | -0.24199 | 122.8511 | -0.002792 | 122.9014 | 122.8828 | 0.031755 | -0.017921 | 0.19694 | 122.663 | -0.10777 | 122.9335 | 122.8349 | 0.1719 | 0.054941 | -0.088373 | 123.0303 | 123.0152 | 123.2301 | 122.9293 | -0.18207 | 122.9254 | 123.0881 | 122.9448 | 122.9877 | -0.37016
4284.3594 | 123.0469 | -122.905 | 0.10529 | 1.4211e-13 | -0.016619 | -0.013291 | -0.045384 | -0.042139 | -0.012779 | 0.0067908 | 0.009415 | 0.032882 | -0.027035 | 0.013363 | -0.019703 | -0.008109 | 0.0243 | -0.022144 | 0.1208 | 0.096516 | 0.32969 | -0.053899 | 0.019362 | 0.078197 | -0.070087 | 0.020409 | 0.17854 | 0.003172 | -0.23283 | 122.8511 | 0.015518 | 122.8969 | 122.8828 | 0.031755 | -0.00877 | 0.2244 | 122.6721 | -0.084877 | 122.9243 | 122.8349 | 0.16274 | 0.07325 | -0.10211 | 123.0258 | 123.0015 | 123.2347 | 122.9293 | -0.15919 | 122.9254 | 123.0835 | 122.9081 | 122.9832 | -0.33812
4286.0938 | 123.1659 | -122.8775 | 0.09613 | 1.4211e-13 | -0.016619 | -0.013718 | -0.04517 | -0.041711 | -0.012779 | 0.0067908 | 0.0096286 | 0.033309 | -0.027035 | 0.013363 | -0.019489 | 0.005626 | 0.019721 | -0.026723 | 0.1208 | 0.091937 | 0.32511 | -0.031005 | 0.02852 | 0.078197 | -0.070087 | 0.015831 | 0.19685 | -0.065507 | -0.23741 | 122.8465 | 0.024674 | 122.8831 | 122.8508 | 0.004282 | -0.004193 | 0.22898 | 122.6401 | -0.080299 | 122.906 | 122.8074 | 0.16732 | 0.10072 | -0.16164 | 122.9983 | 122.9694 | 123.2026 | 122.8972 | -0.12713 | 122.8933 | 123.0744 | 122.812 | 122.9557 | -0.33354
4287.875 | 123.0606 | -122.9187 | 0.12817 | 1.4211e-13 | -0.016406 | -0.013291 | -0.045384 | -0.042139 | -0.012993 | -0.00083919 | 0.009415 | 0.033309 | -0.027035 | 0.013577 | -0.019489 | -0.003531 | 0.015142 | -0.012988 | 0.11622 | 0.10567 | 0.33427 | -0.044742 | 0.019362 | 0.078197 | -0.074666 | 0.020409 | 0.18769 | 0.048958 | -0.23741 | 122.874 | -0.011949 | 122.9152 | 122.9057 | 0.031754 | -0.0225 | 0.20609 | 122.6813 | -0.10777 | 122.9381 | 122.844 | 0.16274 | 0.059519 | -0.079216 | 123.0349 | 123.0244 | 123.253 | 122.9338 | -0.17292 | 122.9391 | 123.1064 | 122.9677 | 122.9969 | -0.36558
4289.6719 | 123.0789 | -122.9095 | 0.10986 | 1.4211e-13 | -0.015978 | -0.013291 | -0.045384 | -0.042139 | -0.012993 | -0.0084697 | 0.0092014 | 0.033096 | -0.026821 | 0.012936 | -0.019276 | 0.005626 | 0.010564 | -0.017566 | 0.11622 | 0.11025 | 0.32053 | -0.053899 | 0.019362 | 0.078197 | -0.074666 | 0.020409 | 0.18311 | 0.035222 | -0.23741 | 122.8556 | 0.006362 | 122.9152 | 122.892 | 0.036333 | 0.00039 | 0.21067 | 122.6721 | -0.089454 | 122.9289 | 122.8349 | 0.16274 | 0.073252 | -0.074641 | 123.0258 | 123.0198 | 123.2301 | 122.9201 | -0.16376 | 122.93 | 123.0927 | 122.9448 | 122.9877 | -0.34727
4291.4062 | 123.1705 | -122.8912 | 0.082397 | 1.4211e-13 | -0.016619 | -0.013505 | -0.045384 | -0.041925 | -0.012779 | -0.0161 | 0.0092014 | 0.033309 | -0.026821 | 0.013363 | -0.019276 | 0.001048 | 0.015142 | -0.022144 | 0.1208 | 0.1011 | 0.32511 | -0.076794 | 0.019362 | 0.073618 | -0.074666 | 0.015831 | 0.18769 | 0.044379 | -0.24657 | 122.8144 | 0.038407 | 122.8923 | 122.8691 | 0.05465 | 0.018698 | 0.24271 | 122.6447 | -0.066566 | 122.9106 | 122.8166 | 0.1719 | 0.1053 | -0.038018 | 123.012 | 122.9923 | 123.2163 | 122.9064 | -0.15919 | 122.9071 | 123.0789 | 122.9356 | 122.9649 | -0.32896
4293.2031 | 123.1888 | -122.8867 | 0.07782 | 1.4211e-13 | -0.016406 | -0.013291 | -0.045384 | -0.042139 | -0.012779 | 0.014421 | 0.0096286 | 0.033096 | -0.027249 | 0.013577 | -0.019062 | 0.005626 | 0.019721 | -0.022144 | 0.11622 | 0.096516 | 0.32511 | -0.085952 | 0.02852 | 0.082776 | -0.070087 | 0.011252 | 0.18769 | -0.047193 | -0.22825 | 122.8007 | 0.038405 | 122.8923 | 122.8645 | 0.063808 | 0.018696 | 0.24729 | 122.6584 | -0.066568 | 122.9152 | 122.8166 | 0.15817 | 0.10987 | -0.12501 | 123.0029 | 122.9832 | 123.2118 | 122.9064 | -0.16377 | 122.8979 | 123.0744 | 122.8395 | 122.9694 | -0.30607
4294.9375 | 123.111 | -122.9324 | 0.12817 | 1.4211e-13 | -0.016406 | -0.013291 | -0.04517 | -0.042352 | -0.012565 | -0.00083919 | 0.009415 | 0.033523 | -0.026608 | 0.013577 | -0.019489 | -0.003531 | 0.015142 | -0.026723 | 0.12538 | 0.096516 | 0.32969 | -0.040163 | 0.02852 | 0.078197 | -0.074666 | 0.020409 | 0.18769 | 0.053537 | -0.24657 | 122.8923 | -0.002792 | 122.9289 | 122.9057 | 0.01344 | -0.031658 | 0.20151 | 122.6859 | -0.10777 | 122.961 | 122.8578 | 0.1719 | 0.059519 | -0.074637 | 123.0578 | 123.0289 | 123.2621 | 122.9476 | -0.16834 | 122.9528 | 123.1201 | 122.986 | 123.0106 | -0.37474
4296.7344 | 123.143 | -122.8775 | 0.07782 | 1.4211e-13 | -0.016619 | -0.013291 | -0.04517 | -0.041925 | -0.012779 | 0.0067908 | 0.009415 | 0.033737 | -0.026821 | 0.013363 | -0.019276 | -0.003531 | 0.019721 | -0.017566 | 0.1208 | 0.096516 | 0.32969 | -0.067636 | 0.023941 | 0.073618 | -0.070087 | 0.020409 | 0.18311 | 0.058115 | -0.24657 | 122.8099 | 0.042984 | 122.874 | 122.8599 | 0.05007 | 0.018696 | 0.25187 | 122.6309 | -0.057411 | 122.9014 | 122.8074 | 0.17648 | 0.10529 | -0.019705 | 122.9983 | 122.974 | 123.2072 | 122.8972 | -0.14546 | 122.8979 | 123.0606 | 122.9356 | 122.9511 | -0.32439
4298.5312 | 123.0972 | -122.9279 | 0.11444 | 1.4211e-13 | -0.016406 | -0.013718 | -0.045384 | -0.041925 | -0.012779 | -0.00083919 | 0.009415 | 0.033096 | -0.026821 | 0.013363 | -0.019276 | -0.003531 | 0.010564 | -0.026723 | 0.12996 | 0.10567 | 0.32511 | -0.072215 | 0.023941 | 0.078197 | -0.070087 | 0.011252 | 0.17854 | 0.044379 | -0.23741 | 122.8556 | 0.015519 | 122.9243 | 122.9011 | 0.045492 | -0.008767 | 0.21067 | 122.6904 | -0.10319 | 122.9518 | 122.8578 | 0.16732 | 0.064095 | -0.070062 | 123.0578 | 123.0335 | 123.253 | 122.9384 | -0.18666 | 122.9391 | 123.1064 | 122.9722 | 123.0061 | -0.35185
4300.25 | 123.0789 | -122.9004 | 0.10986 | 1.4211e-13 | -0.016192 | -0.013505 | -0.045598 | -0.041925 | -0.012565 | 0.0067908 | 0.009415 | 0.033309 | -0.026821 | 0.013149 | -0.019276 | -0.003531 | 0.015142 | -0.022144 | 0.12996 | 0.10567 | 0.32053 | -0.072215 | 0.019362 | 0.078197 | -0.06093 | 0.020409 | 0.18311 | 0.058115 | -0.23741 | 122.8282 | 0.020097 | 122.8969 | 122.8782 | 0.050071 | -0.004189 | 0.21067 | 122.663 | -0.089454 | 122.9198 | 122.8395 | 0.17648 | 0.073252 | -0.051748 | 123.0304 | 123.0061 | 123.2209 | 122.9155 | -0.18208 | 122.9208 | 123.0835 | 122.9585 | 122.9786 | -0.34727
4302.0312 | 123.0423 | -122.8958 | 0.1236 | 1.4211e-13 | -0.016192 | -0.013505 | -0.045384 | -0.042139 | -0.012779 | -0.00083919 | 0.0096286 | 0.033309 | -0.026821 | 0.013577 | -0.019276 | 0.001048 | 0.019721 | -0.022144 | 0.12996 | 0.1011 | 0.32511 | -0.076794 | 0.019362 | 0.078197 | -0.070087 | 0.020409 | 0.18769 | 0.016908 | -0.23283 | 122.819 | 0.006364 | 122.8969 | 122.8737 | 0.05465 | -0.022501 | 0.20151 | 122.663 | -0.10319 | 122.9152 | 122.8257 | 0.16274 | 0.064097 | -0.10669 | 123.0258 | 122.9969 | 123.2209 | 122.9155 | -0.20039 | 122.9162 | 123.0835 | 122.9127 | 122.974 | -0.35643
4303.8281 | 123.1522 | -122.8912 | 0.09613 | 1.4211e-13 | -0.016619 | -0.013505 | -0.045384 | -0.042139 | -0.012993 | -0.0084697 | 0.0092014 | 0.033096 | -0.027035 | 0.013363 | -0.019489 | -0.003531 | 0.019721 | -0.017566 | 0.12996 | 0.096516 | 0.32053 | -0.053899 | 0.02852 | 0.078197 | -0.065509 | 0.015831 | 0.17854 | 0.039801 | -0.23283 | 122.8373 | 0.03383 | 122.8877 | 122.8737 | 0.036333 | 0.000386 | 0.2244 | 122.6584 | -0.080299 | 122.9198 | 122.8257 | 0.16732 | 0.082406 | -0.056329 | 123.0212 | 122.9878 | 123.2118 | 122.911 | -0.15003 | 122.9071 | 123.0698 | 122.931 | 122.9694 | -0.32896
4305.5781 | 123.0606 | -122.8958 | 0.10986 | 1.4211e-13 | -0.016406 | -0.013291 | -0.045384 | -0.042139 | -0.012779 | 0.0067908 | 0.0096286 | 0.033096 | -0.026821 | 0.013363 | -0.019276 | 0.001048 | 0.015142 | -0.026723 | 0.12538 | 0.10567 | 0.32053 | -0.09511 | 0.023941 | 0.078197 | -0.070087 | 0.020409 | 0.18769 | 0.039801 | -0.23741 | 122.8007 | 0.015519 | 122.8969 | 122.8691 | 0.068387 | -0.004189 | 0.21067 | 122.6584 | -0.089454 | 122.9198 | 122.8257 | 0.16732 | 0.07783 | -0.070062 | 123.0212 | 123.0015 | 123.2163 | 122.911 | -0.20497 | 122.9162 | 123.0835 | 122.9356 | 122.974 | -0.34727
4307.375 | 123.0377 | -122.9416 | 0.10071 | 1.4211e-13 | -0.016619 | -0.013291 | -0.04517 | -0.042566 | -0.012779 | -0.00083919 | 0.0096286 | 0.033523 | -0.027035 | 0.013363 | -0.019276 | -0.003531 | 0.019721 | -0.026723 | 0.1208 | 0.10567 | 0.32511 | -0.081373 | 0.033099 | 0.087354 | -0.065509 | 0.011252 | 0.17854 | 0.048958 | -0.24657 | 122.8602 | 0.020096 | 122.9381 | 122.9149 | 0.05465 | 0.004966 | 0.2244 | 122.695 | -0.089456 | 122.9747 | 122.8761 | 0.18106 | 0.077828 | -0.05175 | 123.0624 | 123.0473 | 123.2667 | 122.9613 | -0.18208 | 122.9528 | 123.1201 | 122.9905 | 123.0289 | -0.34728
4309.1562 | 123.1842 | -122.9004 | 0.07782 | 1.4211e-13 | -0.016833 | -0.013077 | -0.045384 | -0.041711 | -0.012779 | -0.00083919 | 0.0092014 | 0.033523 | -0.026821 | 0.013363 | -0.019489 | 0.001048 | 0.015142 | -0.017566 | 0.12538 | 0.096516 | 0.32053 | -0.058478 | 0.023941 | 0.082776 | -0.074666 | 0.020409 | 0.18311 | 0.053537 | -0.23741 | 122.8419 | 0.047562 | 122.9014 | 122.8828 | 0.040912 | 0.018696 | 0.24271 | 122.663 | -0.057411 | 122.9243 | 122.8257 | 0.16274 | 0.10529 | -0.024283 | 123.0258 | 122.9969 | 123.2209 | 122.9155 | -0.1363 | 122.9208 | 123.0835 | 122.9539 | 122.9832 | -0.31523
4310.9062 | 123.1613 | -122.9095 | 0.10986 | 1.4211e-13 | -0.016406 | -0.013291 | -0.045384 | -0.042139 | -0.012779 | 0.0067908 | 0.009415 | 0.033096 | -0.026821 | 0.013577 | -0.019276 | -0.012688 | 0.019721 | -0.022144 | 0.12538 | 0.11025 | 0.32053 | -0.040163 | 0.019362 | 0.078197 | -0.065509 | 0.024988 | 0.18769 | 0.007751 | -0.24199 | 122.8694 | 0.015519 | 122.8969 | 122.8874 | 0.018019 | 0.00039 | 0.21067 | 122.6676 | -0.084875 | 122.9289 | 122.844 | 0.17648 | 0.07783 | -0.10211 | 123.0349 | 123.0198 | 123.2301 | 122.9293 | -0.15003 | 122.9345 | 123.0972 | 122.9173 | 122.9877 | -0.35185
4312.7031 | 123.0789 | -122.9279 | 0.11444 | 1.4211e-13 | -0.016406 | -0.013505 | -0.045384 | -0.041925 | -0.012352 | -0.0084697 | 0.0096286 | 0.033309 | -0.026821 | 0.013363 | -0.019276 | -0.003531 | 0.0243 | -0.026723 | 0.11622 | 0.10567 | 0.32053 | -0.067636 | 0.033099 | 0.082776 | -0.065509 | 0.015831 | 0.19227 | 0.053537 | -0.23741 | 122.8602 | 0.001784 | 122.9243 | 122.9011 | 0.040913 | -0.008767 | 0.20609 | 122.6904 | -0.09861 | 122.961 | 122.8623 | 0.1719 | 0.077831 | -0.060904 | 123.0441 | 123.0335 | 123.2484 | 122.9522 | -0.18208 | 122.9437 | 123.1201 | 122.9814 | 123.0106 | -0.35185
4314.5 | 123.1567 | -122.8683 | 0.09613 | 1.4211e-13 | -0.016619 | -0.013505 | -0.045384 | -0.042352 | -0.012993 | 0.014421 | 0.0089876 | 0.033309 | -0.026608 | 0.013577 | -0.019276 | 0.005626 | 0.015142 | -0.022144 | 0.1208 | 0.10567 | 0.32511 | -0.067636 | 0.014784 | 0.082776 | -0.065509 | 0.015831 | 0.18311 | 0.030644 | -0.23741 | 122.8007 | 0.024674 | 122.874 | 122.8462 | 0.045492 | 0.009544 | 0.22898 | 122.6309 | -0.080299 | 122.8831 | 122.8028 | 0.1719 | 0.086985 | -0.065486 | 122.9892 | 122.974 | 123.1935 | 122.8835 | -0.16377 | 122.8842 | 123.0515 | 122.899 | 122.9511 | -0.33354
4316.2344 | 123.1613 | -122.8958 | 0.09613 | 1.4211e-13 | -0.016619 | -0.013505 | -0.045384 | -0.042139 | -0.012993 | -0.00083919 | 0.0092014 | 0.033309 | -0.026821 | 0.01379 | -0.019062 | 0.005626 | 0.015142 | -0.017566 | 0.1208 | 0.10567 | 0.32511 | -0.081373 | 0.019362 | 0.078197 | -0.06093 | 0.024988 | 0.17854 | 0.058115 | -0.23741 | 122.8144 | 0.024674 | 122.9014 | 122.8782 | 0.063807 | 0.009544 | 0.22898 | 122.6584 | -0.071142 | 122.9152 | 122.8349 | 0.17648 | 0.082406 | -0.038015 | 123.0166 | 123.0015 | 123.2209 | 122.911 | -0.1775 | 122.9208 | 123.0743 | 122.9539 | 122.974 | -0.33354
4318.0312 | 123.1842 | -122.8867 | 0.073242 | 1.4211e-13 | -0.016406 | -0.013505 | -0.045384 | -0.042139 | -0.012779 | -0.00083919 | 0.0092014 | 0.033523 | -0.026821 | 0.013363 | -0.019276 | 0.001048 | 0.015142 | -0.017566 | 0.1208 | 0.10567 | 0.32511 | -0.076794 | 0.023941 | 0.082776 | -0.065509 | 0.024988 | 0.18311 | 0.039801 | -0.23741 | 122.8099 | 0.047562 | 122.8877 | 122.8691 | 0.059228 | 0.032432 | 0.25187 | 122.6492 | -0.048254 | 122.9106 | 122.8211 | 0.1719 | 0.10987 | -0.033441 | 123.0075 | 122.9923 | 123.2118 | 122.9018 | -0.15004 | 122.9116 | 123.0698 | 122.9265 | 122.9694 | -0.31065
4319.8281 | 123.1888 | -122.8683 | 0.07782 | 1.4211e-13 | -0.016192 | -0.013291 | -0.045811 | -0.042352 | -0.012779 | -0.00083919 | 0.009415 | 0.033309 | -0.026608 | 0.013577 | -0.019489 | 0.001048 | 0.019721 | -0.022144 | 0.12996 | 0.11025 | 0.32511 | -0.053899 | 0.023941 | 0.078197 | -0.079245 | 0.011252 | 0.18769 | 0.039801 | -0.23741 | 122.8144 | 0.05214 | 122.8694 | 122.8462 | 0.031755 | 0.032433 | 0.24729 | 122.6309 | -0.066568 | 122.8923 | 122.7891 | 0.15817 | 0.10987 | -0.038019 | 122.9983 | 122.9786 | 123.1935 | 122.8881 | -0.13172 | 122.8796 | 123.056 | 122.9081 | 122.9465 | -0.31523
4321.5781 | 123.2208 | -122.9004 | 0.07782 | 1.4211e-13 | -0.016406 | -0.013505 | -0.045384 | -0.042139 | -0.012993 | -0.0084697 | 0.0092014 | 0.033309 | -0.026608 | 0.013363 | -0.019276 | 0.005626 | 0.019721 | -0.017566 | 0.12996 | 0.096516 | 0.32053 | -0.063057 | 0.02852 | 0.078197 | -0.070087 | 0.020409 | 0.19227 | 0.021486 | -0.24199 | 122.8373 | 0.05214 | 122.906 | 122.8828 | 0.045491 | 0.018696 | 0.24271 | 122.6584 | -0.057411 | 122.9289 | 122.8303 | 0.1719 | 0.11445 | -0.056334 | 123.0304 | 122.9969 | 123.2209 | 122.9201 | -0.14088 | 122.9208 | 123.0927 | 122.9219 | 122.9786 | -0.31981
4323.3594 | 123.0652 | -122.9141 | 0.12817 | 1.4211e-13 | -0.016406 | -0.013505 | -0.045384 | -0.042139 | -0.012993 | -0.0084697 | 0.0092014 | 0.033096 | -0.027035 | 0.013363 | -0.019062 | -0.003531 | 0.015142 | -0.026723 | 0.12538 | 0.10567 | 0.32053 | -0.035584 | 0.023941 | 0.087354 | -0.070087 | 0.024988 | 0.18311 | 0.048958 | -0.24657 | 122.8785 | -0.002792 | 122.9106 | 122.8874 | 0.008861 | -0.0225 | 0.19236 | 122.6676 | -0.10319 | 122.9381 | 122.844 | 0.17648 | 0.054941 | -0.079216 | 123.0395 | 123.0198 | 123.2347 | 122.9293 | -0.16376 | 122.9391 | 123.0972 | 122.9631 | 123.0015 | -0.37474
4325.1406 | 123.0881 | -122.9233 | 0.10529 | 1.4211e-13 | -0.016406 | -0.013291 | -0.045598 | -0.042139 | -0.012565 | -0.00083919 | 0.0092014 | 0.032668 | -0.026608 | 0.013149 | -0.019276 | 0.001048 | 0.015142 | -0.022144 | 0.13454 | 0.10567 | 0.32053 | -0.067636 | 0.02852 | 0.073618 | -0.074666 | 0.020409 | 0.19227 | 0.035222 | -0.23741 | 122.8556 | 0.029253 | 122.9243 | 122.9011 | 0.045492 | 0.000388 | 0.21525 | 122.6859 | -0.084877 | 122.9518 | 122.8486 | 0.16274 | 0.086986 | -0.070064 | 123.0578 | 123.029 | 123.2438 | 122.9384 | -0.17292 | 122.9437 | 123.1156 | 122.9585 | 122.9969 | -0.3427
4326.9531 | 123.1705 | -122.8958 | 0.09613 | 1.4211e-13 | -0.016619 | -0.013505 | -0.044957 | -0.041925 | -0.013206 | -0.00083919 | 0.0089876 | 0.033096 | -0.026821 | 0.013577 | -0.018848 | 0.001048 | 0.015142 | -0.022144 | 0.12538 | 0.10567 | 0.32511 | -0.081373 | 0.033099 | 0.073618 | -0.065509 | 0.024988 | 0.18769 | 0.016908 | -0.24199 | 122.8144 | 0.029252 | 122.8969 | 122.8737 | 0.059229 | 0.009544 | 0.22898 | 122.6538 | -0.071142 | 122.9289 | 122.8303 | 0.17648 | 0.091563 | -0.079222 | 123.0212 | 123.0015 | 123.2209 | 122.911 | -0.1775 | 122.9208 | 123.0835 | 122.9127 | 122.9694 | -0.33812
4328.7656 | 123.2025 | -122.8775 | 0.07782 | 1.4211e-13 | -0.016406 | -0.013291 | -0.045598 | -0.042139 | -0.012779 | -0.0084697 | 0.0089876 | 0.033309 | -0.026394 | 0.013363 | -0.019276 | -0.008109 | 0.0243 | -0.022144 | 0.12538 | 0.10567 | 0.32053 | -0.063057 | 0.033099 | 0.078197 | -0.065509 | 0.020409 | 0.18769 | 0.058115 | -0.23283 | 122.8144 | 0.047562 | 122.8694 | 122.8554 | 0.040913 | 0.027854 | 0.24271 | 122.6447 | -0.057411 | 122.9106 | 122.812 | 0.16732 | 0.10987 | -0.019705 | 123.0029 | 122.9832 | 123.198 | 122.9018 | -0.14088 | 122.8979 | 123.0652 | 122.9356 | 122.9557 | -0.31065
4330.5625 | 123.0881 | -122.9233 | 0.13733 | 1.4211e-13 | -0.016406 | -0.013291 | -0.045384 | -0.042139 | -0.012993 | -0.00083919 | 0.0089876 | 0.033309 | -0.026608 | 0.013363 | -0.019276 | -0.003531 | 0.019721 | -0.022144 | 0.12538 | 0.11025 | 0.32053 | -0.072215 | 0.023941 | 0.078197 | -0.079245 | 0.020409 | 0.18769 | 0.044379 | -0.24199 | 122.8511 | -0.011947 | 122.9197 | 122.9011 | 0.050071 | -0.027076 | 0.1832 | 122.6813 | -0.11692 | 122.9472 | 122.844 | 0.16274 | 0.050364 | -0.09295 | 123.0487 | 123.0335 | 123.2438 | 122.943 | -0.20954 | 122.9437 | 123.111 | 122.9677 | 123.0015 | -0.37932
4332.3594 | 123.1476 | -122.9141 | 0.07782 | 1.4211e-13 | -0.016619 | -0.013291 | -0.045384 | -0.042139 | -0.012565 | -0.00083919 | 0.0092014 | 0.033096 | -0.027035 | 0.013577 | -0.019276 | -0.008109 | 0.019721 | -0.022144 | 0.12538 | 0.11025 | 0.32969 | -0.081373 | 0.02852 | 0.078197 | -0.074666 | 0.020409 | 0.18311 | 0.058115 | -0.23283 | 122.8328 | 0.047562 | 122.906 | 122.892 | 0.059229 | 0.032433 | 0.25187 | 122.6813 | -0.057411 | 122.9426 | 122.8395 | 0.15817 | 0.10529 | -0.019705 | 123.0395 | 123.0244 | 123.2438 | 122.9338 | -0.15919 | 122.9345 | 123.0972 | 122.9722 | 122.9923 | -0.31065
4334.0625 | 123.2071 | -122.8775 | 0.068665 | 1.4211e-13 | -0.016619 | -0.013077 | -0.045384 | -0.041925 | -0.012993 | -0.0084697 | 0.0092014 | 0.033737 | -0.026608 | 0.013363 | -0.019062 | 0.001048 | 0.010564 | -0.017566 | 0.12538 | 0.11025 | 0.32511 | -0.076794 | 0.023941 | 0.082776 | -0.074666 | 0.015831 | 0.19227 | 0.053537 | -0.23741 | 122.8007 | 0.056717 | 122.8786 | 122.8599 | 0.059228 | 0.041588 | 0.25645 | 122.6401 | -0.052834 | 122.9014 | 122.8028 | 0.16274 | 0.12361 | -0.015128 | 123.0029 | 122.9878 | 123.2026 | 122.8881 | -0.14546 | 122.8933 | 123.0698 | 122.931 | 122.9603 | -0.30607
4335.8594 | 123.1934 | -122.9095 | 0.082397 | 1.4211e-13 | -0.016406 | -0.013077 | -0.04517 | -0.042352 | -0.012779 | 0.0067908 | 0.0092014 | 0.033309 | -0.026821 | 0.013363 | -0.019276 | 0.005626 | 0.010564 | -0.026723 | 0.12538 | 0.10567 | 0.33427 | -0.035584 | 0.023941 | 0.082776 | -0.070087 | 0.015831 | 0.18769 | 0.035222 | -0.24199 | 122.874 | 0.042985 | 122.9152 | 122.8828 | 0.008861 | 0.023277 | 0.25187 | 122.6676 | -0.066566 | 122.9335 | 122.8395 | 0.1719 | 0.1053 | -0.047175 | 123.0349 | 123.0152 | 123.2438 | 122.9201 | -0.11798 | 122.9254 | 123.0972 | 122.9448 | 122.9923 | -0.32439
4337.6719 | 123.1934 | -122.8912 | 0.091553 | 1.4211e-13 | -0.016406 | -0.013077 | -0.04517 | -0.041711 | -0.012565 | -0.0084697 | 0.0089876 | 0.033309 | -0.026608 | 0.013363 | -0.019276 | 0.001048 | 0.0243 | -0.022144 | 0.1208 | 0.1011 | 0.32969 | -0.031005 | 0.02852 | 0.082776 | -0.06093 | 0.020409 | 0.18769 | 0.053537 | -0.24199 | 122.8602 | 0.029251 | 122.8923 | 122.8691 | 0.008861 | 0.009542 | 0.23814 | 122.6492 | -0.071144 | 122.9198 | 122.8303 | 0.18106 | 0.09614 | -0.038016 | 123.012 | 122.9923 | 123.2209 | 122.9155 | -0.12256 | 122.9116 | 123.0789 | 122.9448 | 122.974 | -0.33354
4339.4688 | 123.175 | -122.905 | 0.064087 | 1.4211e-13 | -0.016192 | -0.013291 | -0.045598 | -0.042139 | -0.012779 | -0.00083919 | 0.0092014 | 0.032882 | -0.026608 | 0.012936 | -0.019276 | 0.001048 | 0.019721 | -0.022144 | 0.11622 | 0.1011 | 0.32053 | -0.081373 | 0.02852 | 0.087354 | -0.074666 | 0.020409 | 0.18769 | 0.062694 | -0.23283 | 122.8236 | 0.052138 | 122.906 | 122.8828 | 0.059229 | 0.037008 | 0.25644 | 122.6721 | -0.043678 | 122.9335 | 122.8303 | 0.15817 | 0.12361 | -0.001393 | 123.0212 | 123.0061 | 123.2255 | 122.9247 | -0.14546 | 122.9254 | 123.0927 | 122.9677 | 122.9923 | -0.29692
4341.1875 | 123.1384 | -122.905 | 0.09613 | 1.4211e-13 | -0.016406 | -0.013505 | -0.04517 | -0.041925 | -0.012565 | -0.0084697 | 0.009415 | 0.033096 | -0.026821 | 0.013363 | -0.019489 | 0.001048 | 0.019721 | -0.017566 | 0.12538 | 0.11025 | 0.32969 | -0.090531 | 0.023941 | 0.078197 | -0.074666 | 0.020409 | 0.18311 | 0.035222 | -0.23741 | 122.8144 | 0.029252 | 122.906 | 122.8874 | 0.072965 | 0.014123 | 0.23356 | 122.6676 | -0.075721 | 122.9289 | 122.8303 | 0.16274 | 0.086985 | -0.060908 | 123.0303 | 123.0152 | 123.2347 | 122.9247 | -0.18666 | 122.9254 | 123.0881 | 122.9402 | 122.9832 | -0.33354
4343 | 123.1064 | -122.9324 | 0.10071 | 1.4211e-13 | -0.016406 | -0.013291 | -0.045384 | -0.042139 | -0.012779 | -0.00083919 | 0.009415 | 0.033096 | -0.027035 | 0.013363 | -0.019489 | 0.001048 | 0.019721 | -0.022144 | 0.1208 | 0.10567 | 0.32053 | -0.076794 | 0.023941 | 0.082776 | -0.070087 | 0.020409 | 0.18311 | 0.007751 | -0.23741 | 122.8556 | 0.020096 | 122.9335 | 122.9103 | 0.05465 | 0.004966 | 0.21982 | 122.695 | -0.080299 | 122.9564 | 122.8623 | 0.16732 | 0.082407 | -0.092957 | 123.0532 | 123.0381 | 123.253 | 122.9522 | -0.1775 | 122.9528 | 123.1155 | 122.9402 | 123.0152 | -0.33812
4344.7969 | 123.0652 | -122.9279 | 0.11444 | 1.4211e-13 | -0.016619 | -0.013505 | -0.045384 | -0.041711 | -0.012565 | -0.00083919 | 0.009415 | 0.033309 | -0.026821 | 0.013363 | -0.019703 | -0.003531 | 0.019721 | -0.022144 | 0.12538 | 0.1011 | 0.32511 | -0.063057 | 0.019362 | 0.073618 | -0.074666 | 0.020409 | 0.18311 | 0.058115 | -0.23283 | 122.8648 | 0.010941 | 122.9243 | 122.9057 | 0.040913 | -0.013346 | 0.21067 | 122.695 | -0.094032 | 122.9472 | 122.8532 | 0.15817 | 0.068674 | -0.056326 | 123.0532 | 123.029 | 123.253 | 122.9476 | -0.1775 | 122.9483 | 123.111 | 122.986 | 123.0015 | -0.34727
4346.5312 | 123.1567 | -122.9141 | 0.10529 | 1.4211e-13 | -0.016192 | -0.013291 | -0.04517 | -0.042139 | -0.012779 | -0.0084697 | 0.0092014 | 0.033309 | -0.026608 | 0.013363 | -0.019489 | -0.003531 | 0.015142 | -0.022144 | 0.12538 | 0.1011 | 0.32511 | -0.063057 | 0.023941 | 0.073618 | -0.065509 | 0.015831 | 0.18311 | 0.058115 | -0.23283 | 122.8511 | 0.020096 | 122.9106 | 122.892 | 0.040913 | -0.004191 | 0.21982 | 122.6813 | -0.089455 | 122.9381 | 122.8486 | 0.16732 | 0.077829 | -0.047171 | 123.0395 | 123.0152 | 123.2392 | 122.9293 | -0.16834 | 122.93 | 123.0972 | 122.9722 | 122.9877 | -0.33812
4348.3281 | 123.1934 | -122.9004 | 0.10529 | 1.4211e-13 | -0.016192 | -0.013077 | -0.045384 | -0.041711 | -0.012993 | -0.0084697 | 0.0092014 | 0.033523 | -0.026394 | 0.013363 | -0.019276 | 0.001048 | 0.019721 | -0.022144 | 0.12996 | 0.10567 | 0.32511 | -0.053899 | 0.023941 | 0.082776 | -0.074666 | 0.020409 | 0.19227 | 0.035222 | -0.23741 | 122.8465 | 0.024674 | 122.9014 | 122.8782 | 0.031755 | 0.000388 | 0.21982 | 122.663 | -0.084877 | 122.9243 | 122.8257 | 0.16274 | 0.086986 | -0.070064 | 123.0304 | 123.0061 | 123.2255 | 122.9201 | -0.15919 | 122.9208 | 123.0927 | 122.9356 | 122.9832 | -0.3427
4350.1094 | 123.0789 | -122.9416 | 0.10986 | 1.4211e-13 | -0.016406 | -0.013505 | -0.045384 | -0.042352 | -0.012993 | -0.00083919 | 0.0092014 | 0.033096 | -0.026821 | 0.013363 | -0.019276 | 0.005626 | 0.019721 | -0.017566 | 0.12538 | 0.1011 | 0.32053 | -0.053899 | 0.023941 | 0.078197 | -0.065509 | 0.015831 | 0.19227 | 0.035222 | -0.23741 | 122.8877 | 0.015519 | 122.9472 | 122.924 | 0.036333 | -0.008768 | 0.21067 | 122.7042 | -0.094032 | 122.9655 | 122.8761 | 0.1719 | 0.082409 | -0.074641 | 123.067 | 123.0427 | 123.2621 | 122.9613 | -0.16376 | 122.9574 | 123.1339 | 122.9768 | 123.0198 | -0.34727
4351.8438 | 123.1796 | -122.9141 | 0.07782 | 1.4211e-13 | -0.016406 | -0.013077 | -0.045598 | -0.041711 | -0.013206 | -0.0084697 | 0.0096286 | 0.033523 | -0.026394 | 0.013577 | -0.019276 | 0.005626 | 0.0243 | -0.017566 | 0.12538 | 0.11025 | 0.32511 | -0.081373 | 0.02852 | 0.087354 | -0.06093 | 0.015831 | 0.18769 | 0.058115 | -0.23741 | 122.8328 | 0.047562 | 122.9198 | 122.8966 | 0.063807 | 0.032433 | 0.24729 | 122.6767 | -0.061989 | 122.9426 | 122.8532 | 0.17648 | 0.10987 | -0.019705 | 123.0395 | 123.0244 | 123.2392 | 122.9384 | -0.15919 | 122.93 | 123.1018 | 122.9722 | 123.0015 | -0.31523
4353.6406 | 123.0927 | -122.9324 | 0.09613 | 1.4211e-13 | -0.015978 | -0.013291 | -0.04517 | -0.042139 | -0.012779 | -0.00083919 | 0.0092014 | 0.032882 | -0.026608 | 0.01379 | -0.019489 | 0.001048 | 0.019721 | -0.022144 | 0.11622 | 0.1011 | 0.32969 | -0.081373 | 0.02852 | 0.082776 | -0.079245 | 0.020409 | 0.19227 | 0.035222 | -0.24199 | 122.8511 | 0.020095 | 122.9335 | 122.9103 | 0.059229 | 0.004965 | 0.23356 | 122.6904 | -0.075721 | 122.961 | 122.8532 | 0.16274 | 0.096142 | -0.060908 | 123.0487 | 123.0335 | 123.2621 | 122.9522 | -0.1775 | 122.9528 | 123.1247 | 122.9677 | 123.0152 | -0.33812
4355.4219 | 123.1522 | -122.905 | 0.091553 | 1.4211e-13 | -0.016406 | -0.013291 | -0.04517 | -0.042139 | -0.012352 | -0.00083919 | 0.0092014 | 0.033309 | -0.026608 | 0.013363 | -0.019489 | 0.001048 | 0.0243 | -0.022144 | 0.12538 | 0.10567 | 0.32511 | -0.076794 | 0.02852 | 0.078197 | -0.079245 | 0.011252 | 0.18769 | 0.058115 | -0.24657 | 122.8282 | 0.033829 | 122.906 | 122.8828 | 0.05465 | 0.014121 | 0.23356 | 122.6584 | -0.080301 | 122.9335 | 122.8257 | 0.16732 | 0.09614 | -0.033438 | 123.0303 | 123.0106 | 123.2301 | 122.9293 | -0.16835 | 122.9162 | 123.0927 | 122.9631 | 122.9832 | -0.33812
4357.1562 | 123.2162 | -122.9004 | 0.091553 | 1.4211e-13 | -0.016406 | -0.013291 | -0.04517 | -0.042139 | -0.012993 | 0.0067908 | 0.0092014 | 0.033096 | -0.026394 | 0.013363 | -0.019489 | -0.003531 | 0.019721 | -0.022144 | 0.12996 | 0.1011 | 0.32511 | -0.063057 | 0.02852 | 0.073618 | -0.074666 | 0.011252 | 0.19227 | 0.058115 | -0.24199 | 122.8373 | 0.038407 | 122.8969 | 122.8782 | 0.040913 | 0.009542 | 0.23356 | 122.6584 | -0.080301 | 122.9289 | 122.8257 | 0.16732 | 0.10072 | -0.033438 | 123.0304 | 123.0015 | 123.2255 | 122.9201 | -0.15461 | 122.9116 | 123.0927 | 122.9585 | 122.974 | -0.33354
4358.9531 | 123.1247 | -122.9645 | 0.09613 | 1.4211e-13 | -0.015978 | -0.013505 | -0.045384 | -0.042352 | -0.012565 | -0.00083919 | 0.009415 | 0.033096 | -0.026608 | 0.013149 | -0.019276 | -0.008109 | 0.015142 | -0.022144 | 0.11622 | 0.1011 | 0.32053 | -0.044742 | 0.033099 | 0.078197 | -0.065509 | 0.020409 | 0.17854 | 0.044379 | -0.24199 | 122.9197 | 0.020095 | 122.9564 | 122.9423 | 0.022598 | 0.004965 | 0.2244 | 122.7225 | -0.075721 | 122.9976 | 122.899 | 0.17648 | 0.082406 | -0.051751 | 123.0807 | 123.0656 | 123.285 | 122.9796 | -0.14087 | 122.9849 | 123.143 | 123.0089 | 123.0427 | -0.33812
4360.6875 | 123.1613 | -122.9233 | 0.082397 | 1.4211e-13 | -0.016619 | -0.013077 | -0.045384 | -0.042352 | -0.012565 | -0.00083919 | 0.0089876 | 0.032882 | -0.026608 | 0.013577 | -0.019276 | 0.010204 | 0.019721 | -0.017566 | 0.12538 | 0.1011 | 0.32053 | -0.021847 | 0.02852 | 0.078197 | -0.065509 | 0.015831 | 0.18769 | 0.021486 | -0.22825 | 122.9014 | 0.042985 | 122.9335 | 122.9057 | 0.004281 | 0.018698 | 0.23813 | 122.695 | -0.066566 | 122.9518 | 122.8578 | 0.16274 | 0.1053 | -0.060911 | 123.0487 | 123.0244 | 123.2438 | 122.943 | -0.10424 | 122.9391 | 123.111 | 122.9448 | 123.0015 | -0.31065
4362.4844 | 123.1201 | -122.9141 | 0.10529 | 1.4211e-13 | -0.016406 | -0.013291 | -0.045384 | -0.041925 | -0.012565 | -0.00083919 | 0.0096286 | 0.033309 | -0.026608 | 0.013577 | -0.019062 | 0.001048 | 0.0243 | -0.026723 | 0.12538 | 0.1011 | 0.32511 | -0.099689 | 0.033099 | 0.082776 | -0.070087 | 0.024988 | 0.18769 | 0.053537 | -0.24657 | 122.8144 | 0.020096 | 122.9152 | 122.8874 | 0.072966 | -0.004191 | 0.21982 | 122.6676 | -0.080298 | 122.9472 | 122.844 | 0.17648 | 0.082407 | -0.051749 | 123.0395 | 123.0152 | 123.2392 | 122.9384 | -0.20498 | 122.9391 | 123.1018 | 122.9677 | 122.9969 | -0.35185
4364.2812 | 123.1384 | -122.9462 | 0.11444 | 1.4211e-13 | -0.016406 | -0.013077 | -0.04517 | -0.041711 | -0.012779 | -0.00083919 | 0.0092014 | 0.033309 | -0.026181 | 0.013577 | -0.019062 | 0.001048 | 0.019721 | -0.022144 | 0.11622 | 0.10567 | 0.32969 | -0.067636 | 0.023941 | 0.078197 | -0.070087 | 0.011252 | 0.18769 | 0.053537 | -0.24657 | 122.8785 | 0.001784 | 122.9472 | 122.924 | 0.045492 | -0.008767 | 0.21525 | 122.6996 | -0.10319 | 122.9701 | 122.8761 | 0.17648 | 0.073252 | -0.060904 | 123.0624 | 123.0518 | 123.2759 | 122.9659 | -0.18208 | 122.9574 | 123.1339 | 122.9997 | 123.0244 | -0.36101
4366.0156 | 123.0469 | -122.9507 | 0.1236 | 1.4211e-13 | -0.016619 | -0.013718 | -0.045384 | -0.042352 | -0.012779 | 0.014421 | 0.0092014 | 0.033096 | -0.026608 | 0.013577 | -0.019489 | -0.003531 | 0.019721 | -0.022144 | 0.12538 | 0.1011 | 0.32053 | -0.090531 | 0.02852 | 0.073618 | -0.074666 | 0.024988 | 0.18769 | 0.058115 | -0.24199 | 122.8602 | 0.001786 | 122.9472 | 122.9286 | 0.068387 | -0.022501 | 0.19694 | 122.7088 | -0.098608 | 122.9793 | 122.8761 | 0.16732 | 0.064097 | -0.065481 | 123.0761 | 123.0518 | 123.2713 | 122.9705 | -0.21413 | 122.9757 | 123.1384 | 123.0089 | 123.0244 | -0.36558
4367.8281 | 123.0927 | -122.9279 | 0.1236 | 1.4211e-13 | -0.016406 | -0.013077 | -0.045384 | -0.041711 | -0.012779 | -0.0084697 | 0.008774 | 0.033096 | -0.026608 | 0.013363 | -0.019276 | 0.005626 | 0.015142 | -0.017566 | 0.11622 | 0.1011 | 0.32511 | -0.044742 | 0.023941 | 0.073618 | -0.074666 | 0.020409 | 0.18311 | 0.039801 | -0.23741 | 122.8831 | -0.007371 | 122.9335 | 122.9103 | 0.027176 | -0.022501 | 0.20151 | 122.6904 | -0.10319 | 122.9518 | 122.8532 | 0.16274 | 0.059519 | -0.083795 | 123.0441 | 123.029 | 123.253 | 122.943 | -0.16834 | 122.9483 | 123.111 | 122.9677 | 123.0015 | -0.36101
4369.5781 | 123.1064 | -122.9462 | 0.1236 | 1.4211e-13 | -0.016192 | -0.013077 | -0.04517 | -0.042139 | -0.012352 | -0.00083919 | 0.0089876 | 0.032668 | -0.026394 | 0.013363 | -0.019062 | -0.003531 | 0.019721 | -0.022144 | 0.12538 | 0.1011 | 0.32511 | -0.099689 | 0.02852 | 0.082776 | -0.070087 | 0.024988 | 0.19227 | 0.053537 | -0.23283 | 122.8465 | 0.001786 | 122.9426 | 122.924 | 0.077545 | -0.022501 | 0.20151 | 122.7133 | -0.098608 | 122.9747 | 122.8761 | 0.16274 | 0.068676 | -0.070059 | 123.0715 | 123.0473 | 123.2713 | 122.9659 | -0.22329 | 122.9712 | 123.1384 | 122.9997 | 123.0289 | -0.35643
4371.3594 | 123.1934 | -122.9233 | 0.1236 | 1.4211e-13 | -0.016406 | -0.013505 | -0.045384 | -0.042352 | -0.012993 | -0.0084697 | 0.009415 | 0.033737 | -0.026821 | 0.013149 | -0.019276 | -0.003531 | 0.015142 | -0.017566 | 0.12996 | 0.11025 | 0.32969 | -0.085952 | 0.023941 | 0.087354 | -0.074666 | 0.015831 | 0.17854 | 0.053537 | -0.23741 | 122.8373 | 0.006364 | 122.9197 | 122.9057 | 0.068386 | -0.013343 | 0.20609 | 122.6859 | -0.10776 | 122.9472 | 122.8486 | 0.16274 | 0.05494 | -0.070059 | 123.0532 | 123.0335 | 123.253 | 122.9384 | -0.20955 | 122.9391 | 123.1018 | 122.9768 | 123.0106 | -0.36101
4373.1562 | 123.23 | -122.8958 | 0.086975 | 1.4211e-13 | -0.016192 | -0.013077 | -0.04517 | -0.042139 | -0.012779 | 0.0067908 | 0.0092014 | 0.033523 | -0.026608 | 0.013363 | -0.019703 | 0.001048 | 0.019721 | -0.022144 | 0.12538 | 0.10567 | 0.31595 | -0.090531 | 0.02852 | 0.082776 | -0.074666 | 0.020409 | 0.19227 | 0.062694 | -0.22825 | 122.8053 | 0.038407 | 122.8969 | 122.8737 | 0.068387 | 0.018699 | 0.22898 | 122.6676 | -0.066566 | 122.9243 | 122.8211 | 0.15359 | 0.1053 | -0.024281 | 123.0212 | 123.0015 | 123.2118 | 122.9155 | -0.17751 | 122.9162 | 123.0881 | 122.9585 | 122.9786 | -0.31523
4374.9531 | 123.0743 | -122.9691 | 0.12817 | 1.4211e-13 | -0.016406 | -0.013505 | -0.045384 | -0.042139 | -0.012993 | 0.014421 | 0.0089876 | 0.033096 | -0.026821 | 0.013363 | -0.019276 | -0.008109 | 0.015142 | -0.026723 | 0.12996 | 0.11025 | 0.32969 | -0.072215 | 0.02852 | 0.073618 | -0.065509 | 0.020409 | 0.18311 | 0.016908 | -0.23283 | 122.8968 | 0.001786 | 122.9609 | 122.9423 | 0.045492 | -0.017921 | 0.20151 | 122.7362 | -0.10777 | 122.9976 | 122.9035 | 0.16732 | 0.054941 | -0.11127 | 123.099 | 123.0793 | 123.2987 | 122.9842 | -0.20039 | 122.9895 | 123.1522 | 122.986 | 123.0427 | -0.36101
4376.75 | 123.0881 | -122.9462 | 0.12817 | 1.4211e-13 | -0.016406 | -0.013291 | -0.045384 | -0.041925 | -0.012993 | -0.00083919 | 0.009415 | 0.033309 | -0.026608 | 0.013363 | -0.019489 | 0.005626 | 0.019721 | -0.026723 | 0.12538 | 0.10567 | 0.32511 | -0.058478 | 0.02852 | 0.078197 | -0.074666 | 0.011252 | 0.19227 | 0.053537 | -0.23283 | 122.8877 | -0.002792 | 122.9518 | 122.9194 | 0.031755 | -0.0225 | 0.19694 | 122.7133 | -0.11692 | 122.9747 | 122.8715 | 0.15817 | 0.064098 | -0.074637 | 123.0715 | 123.0518 | 123.2713 | 122.9659 | -0.18665 | 122.9574 | 123.1384 | 122.9997 | 123.0244 | -0.36101
4378.5 | 123.0698 | -122.9782 | 0.11444 | 1.4211e-13 | -0.016406 | -0.013291 | -0.045811 | -0.041925 | -0.012565 | 0.0067908 | 0.0089876 | 0.033523 | -0.026821 | 0.013577 | -0.019062 | 0.001048 | 0.019721 | -0.031301 | 0.11622 | 0.096516 | 0.32969 | -0.049321 | 0.023941 | 0.078197 | -0.074666 | 0.015831 | 0.18769 | 0.030644 | -0.23283 | 122.9289 | 0.001784 | 122.9793 | 122.9469 | 0.01802 | -0.017925 | 0.21525 | 122.7454 | -0.09861 | 123.0022 | 122.9035 | 0.15817 | 0.073252 | -0.083797 | 123.0944 | 123.0747 | 123.3079 | 122.9979 | -0.16376 | 122.994 | 123.1659 | 123.0089 | 123.0564 | -0.34727
4380.2969 | 123.1338 | -122.9599 | 0.11444 | 1.4211e-13 | -0.016833 | -0.013505 | -0.045384 | -0.041711 | -0.012779 | 0.0067908 | 0.0089876 | 0.033096 | -0.026608 | 0.013577 | -0.019276 | -0.003531 | 0.015142 | -0.026723 | 0.12996 | 0.1011 | 0.32053 | -0.017268 | 0.023941 | 0.082776 | -0.074666 | 0.015831 | 0.19227 | 0.030644 | -0.22825 | 122.9426 | 0.015519 | 122.9564 | 122.9332 | -0.009455 | -0.013346 | 0.20609 | 122.7316 | -0.09861 | 122.9838 | 122.8852 | 0.15359 | 0.077831 | -0.083797 | 123.0899 | 123.061 | 123.2804 | 122.975 | -0.13171 | 122.9757 | 123.1522 | 122.9905 | 123.0427 | -0.34269
4382.0156 | 123.1705 | -122.9462 | 0.10071 | 1.4211e-13 | -0.016619 | -0.013505 | -0.045598 | -0.041925 | -0.012993 | 0.0067908 | 0.0089876 | 0.033309 | -0.026394 | 0.013363 | -0.019062 | 0.001048 | 0.019721 | -0.022144 | 0.1208 | 0.1011 | 0.32511 | -0.053899 | 0.02852 | 0.082776 | -0.074666 | 0.020409 | 0.18769 | 0.067272 | -0.23741 | 122.8923 | 0.020096 | 122.9472 | 122.924 | 0.031755 | 0.000387 | 0.2244 | 122.7088 | -0.080299 | 122.9747 | 122.8715 | 0.16274 | 0.086985 | -0.033436 | 123.067 | 123.0473 | 123.2713 | 122.9659 | -0.15461 | 122.9666 | 123.1339 | 123.0134 | 123.0289 | -0.33812
4383.8125 | 123.175 | -122.937 | 0.10529 | 1.4211e-13 | -0.016406 | -0.013291 | -0.04517 | -0.041925 | -0.012779 | -0.00083919 | 0.0089876 | 0.033309 | -0.026394 | 0.013363 | -0.019276 | 0.001048 | 0.019721 | -0.022144 | 0.12538 | 0.1011 | 0.32969 | -0.072215 | 0.02852 | 0.082776 | -0.074666 | 0.011252 | 0.19685 | 0.058115 | -0.23741 | 122.8648 | 0.020096 | 122.9381 | 122.9149 | 0.050071 | -0.004191 | 0.2244 | 122.6996 | -0.094034 | 122.9655 | 122.8623 | 0.16274 | 0.091565 | -0.047171 | 123.0624 | 123.0381 | 123.2667 | 122.9567 | -0.1775 | 122.9483 | 123.1339 | 122.9951 | 123.0198 | -0.3427
4385.5469 | 123.0972 | -122.9507 | 0.13275 | 1.4211e-13 | -0.016192 | -0.013291 | -0.045598 | -0.041925 | -0.012565 | 0.0067908 | 0.008774 | 0.033309 | -0.026821 | 0.01379 | -0.019276 | 0.001048 | 0.028878 | -0.026723 | 0.12538 | 0.10567 | 0.32053 | -0.058478 | 0.023941 | 0.078197 | -0.070087 | 0.011252 | 0.18769 | 0.053537 | -0.23741 | 122.8923 | -0.007369 | 122.9518 | 122.924 | 0.031755 | -0.027077 | 0.18778 | 122.7133 | -0.1215 | 122.9747 | 122.8807 | 0.16732 | 0.054942 | -0.079214 | 123.0761 | 123.0564 | 123.2713 | 122.9796 | -0.19123 | 122.962 | 123.1384 | 123.0043 | 123.0289 | -0.37016
4387.3438 | 123.23 | -122.9279 | 0.086975 | 1.4211e-13 | -0.016406 | -0.013291 | -0.044957 | -0.042139 | -0.012779 | 0.0067908 | 0.0089876 | 0.033309 | -0.026394 | 0.014218 | -0.019276 | 0.001048 | 0.0243 | -0.017566 | 0.12996 | 0.1011 | 0.31595 | -0.072215 | 0.023941 | 0.082776 | -0.074666 | 0.015831 | 0.18769 | 0.026065 | -0.23283 | 122.8556 | 0.042985 | 122.9289 | 122.9103 | 0.054649 | 0.01412 | 0.22898 | 122.695 | -0.071144 | 122.9518 | 122.8532 | 0.15817 | 0.10072 | -0.06091 | 123.0578 | 123.029 | 123.2438 | 122.9522 | -0.15919 | 122.9437 | 123.1155 | 122.9539 | 123.0106 | -0.31981
4389.0781 | 123.2071 | -122.9141 | 0.10071 | 1.4211e-13 | -0.016192 | -0.013077 | -0.045384 | -0.042139 | -0.012779 | 0.0067908 | 0.009415 | 0.033309 | -0.026821 | 0.013363 | -0.019062 | 0.005626 | 0.015142 | -0.017566 | 0.12996 | 0.1011 | 0.32511 | -0.072215 | 0.023941 | 0.082776 | -0.070087 | 0.020409 | 0.17854 | 0.026065 | -0.23283 | 122.8419 | 0.029252 | 122.9198 | 122.8966 | 0.054649 | 0.000387 | 0.2244 | 122.6813 | -0.080299 | 122.9381 | 122.844 | 0.16274 | 0.077828 | -0.074643 | 123.0441 | 123.0152 | 123.2392 | 122.9293 | -0.17292 | 122.9345 | 123.0927 | 122.9402 | 122.9969 | -0.33354
4390.875 | 123.0789 | -122.9233 | 0.12817 | 1.4211e-13 | -0.016619 | -0.013718 | -0.045598 | -0.042352 | -0.012779 | -0.0084697 | 0.008774 | 0.033737 | -0.026394 | 0.013363 | -0.019276 | 0.001048 | 0.019721 | -0.017566 | 0.12996 | 0.1011 | 0.32511 | -0.053899 | 0.019362 | 0.078197 | -0.070087 | 0.020409 | 0.18311 | 0.062694 | -0.23283 | 122.8694 | 0.001786 | 122.9243 | 122.9057 | 0.036333 | -0.027079 | 0.19694 | 122.6904 | -0.10777 | 122.9426 | 122.8532 | 0.16274 | 0.054941 | -0.06548 | 123.0532 | 123.0244 | 123.2484 | 122.943 | -0.18207 | 122.9437 | 123.1064 | 122.986 | 123.0015 | -0.36101
4392.6094 | 123.1842 | -122.9416 | 0.11444 | 1.4211e-13 | -0.016406 | -0.013505 | -0.04517 | -0.042139 | -0.012993 | 0.0067908 | 0.0089876 | 0.033096 | -0.026608 | 0.013363 | -0.019062 | 0.001048 | 0.019721 | -0.022144 | 0.12538 | 0.1011 | 0.32053 | -0.063057 | 0.019362 | 0.06904 | -0.074666 | 0.024988 | 0.17854 | 0.058115 | -0.23741 | 122.8785 | 0.010941 | 122.9426 | 122.9194 | 0.040913 | -0.013346 | 0.20609 | 122.7042 | -0.089453 | 122.961 | 122.8669 | 0.16274 | 0.064095 | -0.056326 | 123.067 | 123.0427 | 123.2621 | 122.9613 | -0.1775 | 122.9666 | 123.1201 | 122.9997 | 123.0106 | -0.35185
4394.4219 | 123.2391 | -122.9187 | 0.091553 | 1.4211e-13 | -0.015978 | -0.013077 | -0.04517 | -0.042352 | -0.012779 | -0.0084697 | 0.0089876 | 0.033309 | -0.026608 | 0.013363 | -0.019062 | -0.003531 | 0.019721 | -0.022144 | 0.1208 | 0.10567 | 0.32511 | -0.076794 | 0.02852 | 0.078197 | -0.070087 | 0.020409 | 0.18311 | 0.062694 | -0.23741 | 122.8419 | 0.029251 | 122.9152 | 122.8966 | 0.05465 | 0.014121 | 0.23356 | 122.6813 | -0.071144 | 122.9472 | 122.8486 | 0.16732 | 0.091562 | -0.028859 | 123.0395 | 123.0244 | 123.2438 | 122.9384 | -0.16835 | 122.9391 | 123.1018 | 122.9814 | 122.9969 | -0.32896
4396.2031 | 123.111 | -122.9553 | 0.1236 | 1.4211e-13 | -0.016406 | -0.013077 | -0.045598 | -0.042139 | -0.012565 | -0.00083919 | 0.0089876 | 0.033309 | -0.026608 | 0.013577 | -0.019276 | -0.003531 | 0.015142 | -0.017566 | 0.12538 | 0.1011 | 0.32969 | -0.053899 | 0.014784 | 0.078197 | -0.070087 | 0.020409 | 0.18769 | 0.039801 | -0.23283 | 122.9014 | 0.001786 | 122.9518 | 122.9378 | 0.036333 | -0.022501 | 0.20609 | 122.7225 | -0.10319 | 122.9701 | 122.8852 | 0.16274 | 0.064097 | -0.083795 | 123.0807 | 123.0564 | 123.285 | 122.9705 | -0.1775 | 122.9757 | 123.143 | 122.9951 | 123.0335 | -0.35643
4398 | 123.2346 | -122.9187 | 0.086975 | 1.4211e-13 | -0.016192 | -0.01265 | -0.045384 | -0.041925 | -0.012565 | -0.0084697 | 0.009415 | 0.033523 | -0.026608 | 0.013577 | -0.019703 | 0.001048 | 0.0243 | -0.022144 | 0.12996 | 0.10567 | 0.32511 | -0.076794 | 0.023941 | 0.078197 | -0.074666 | 0.011252 | 0.18769 | 0.048958 | -0.23741 | 122.8419 | 0.042985 | 122.9197 | 122.8966 | 0.05465 | 0.018699 | 0.23814 | 122.6813 | -0.075723 | 122.9426 | 122.844 | 0.16274 | 0.10072 | -0.038017 | 123.0487 | 123.0244 | 123.2438 | 122.943 | -0.16377 | 122.93 | 123.1064 | 122.9677 | 122.9969 | -0.32439
4399.7969 | 123.2025 | -122.9324 | 0.07782 | 1.4211e-13 | -0.015978 | -0.013505 | -0.04517 | -0.042139 | -0.012565 | -0.00083919 | 0.008774 | 0.033096 | -0.026608 | 0.013363 | -0.019489 | -0.008109 | 0.015142 | -0.017566 | 0.12538 | 0.096516 | 0.32511 | -0.044742 | 0.023941 | 0.073618 | -0.065509 | 0.020409 | 0.18769 | 0.044379 | -0.24199 | 122.8877 | 0.047562 | 122.9243 | 122.9149 | 0.027176 | 0.018696 | 0.24729 | 122.6904 | -0.057411 | 122.9564 | 122.8669 | 0.17648 | 0.10987 | -0.033441 | 123.0578 | 123.0289 | 123.2575 | 122.9476 | -0.12256 | 122.9528 | 123.1201 | 122.9768 | 123.0061 | -0.31981
4401.5938 | 123.2208 | -122.9233 | 0.07782 | 1.4211e-13 | -0.016406 | -0.013291 | -0.045384 | -0.042139 | -0.012993 | -0.0084697 | 0.0089876 | 0.033737 | -0.026608 | 0.013577 | -0.019276 | 0.005626 | 0.0243 | -0.017566 | 0.12538 | 0.10567 | 0.32511 | -0.099689 | 0.033099 | 0.082776 | -0.070087 | 0.020409 | 0.18769 | 0.053537 | -0.24199 | 122.8236 | 0.047562 | 122.9289 | 122.9057 | 0.082123 | 0.027854 | 0.24729 | 122.6813 | -0.057411 | 122.9564 | 122.8532 | 0.1719 | 0.10987 | -0.024283 | 123.0487 | 123.029 | 123.2484 | 122.9476 | -0.17751 | 122.9437 | 123.111 | 122.9768 | 123.0061 | -0.31981
4403.3438 | 123.1888 | -122.9279 | 0.09613 | 1.4211e-13 | -0.016406 | -0.013291 | -0.045384 | -0.041925 | -0.012779 | 0.0067908 | 0.0092014 | 0.033309 | -0.026821 | 0.013577 | -0.019489 | 0.001048 | 0.019721 | -0.022144 | 0.12996 | 0.10567 | 0.32511 | -0.076794 | 0.023941 | 0.073618 | -0.065509 | 0.020409 | 0.18769 | 0.062694 | -0.23741 | 122.8511 | 0.03383 | 122.9289 | 122.9057 | 0.05465 | 0.009544 | 0.22898 | 122.6904 | -0.075721 | 122.9518 | 122.8623 | 0.1719 | 0.091563 | -0.033436 | 123.0578 | 123.0335 | 123.253 | 122.9476 | -0.17292 | 122.9483 | 123.1155 | 122.9905 | 123.0015 | -0.33354
4405.1406 | 123.1155 | -122.9691 | 0.1236 | 1.4211e-13 | -0.016833 | -0.013291 | -0.045384 | -0.042139 | -0.012779 | 0.0067908 | 0.009415 | 0.033096 | -0.026394 | 0.013363 | -0.019276 | 0.005626 | 0.010564 | -0.017566 | 0.1208 | 0.10567 | 0.32969 | -0.085952 | 0.023941 | 0.073618 | -0.074666 | 0.011252 | 0.19227 | 0.053537 | -0.24199 | 122.8831 | -0.002792 | 122.9747 | 122.9515 | 0.068386 | -0.017922 | 0.20609 | 122.7271 | -0.11234 | 122.993 | 122.8944 | 0.16732 | 0.068676 | -0.070059 | 123.0899 | 123.0747 | 123.2987 | 122.9796 | -0.20955 | 122.9803 | 123.1613 | 123.0226 | 123.0427 | -0.36558
4406.875 | 123.2346 | -122.937 | 0.086975 | 1.4211e-13 | -0.016619 | -0.013505 | -0.045384 | -0.042139 | -0.012565 | 0.0067908 | 0.0089876 | 0.033737 | -0.026608 | 0.013577 | -0.019276 | 0.005626 | 0.019721 | -0.022144 | 0.1208 | 0.10567 | 0.32053 | -0.10427 | 0.019362 | 0.078197 | -0.070087 | 0.020409 | 0.18769 | 0.058115 | -0.24657 | 122.8327 | 0.033829 | 122.9426 | 122.9149 | 0.082124 | 0.018699 | 0.23356 | 122.6904 | -0.066566 | 122.9564 | 122.8669 | 0.17648 | 0.10072 | -0.02886 | 123.0578 | 123.0427 | 123.2575 | 122.9567 | -0.19124 | 122.9574 | 123.1247 | 122.9951 | 123.0152 | -0.33354
4408.6719 | 123.1384 | -122.9736 | 0.11444 | 1.4211e-13 | -0.016406 | -0.013505 | -0.045384 | -0.041925 | -0.012565 | -0.0084697 | 0.0089876 | 0.033096 | -0.026181 | 0.013363 | -0.019276 | -0.003531 | 0.010564 | -0.022144 | 0.12538 | 0.10567 | 0.32053 | -0.072215 | 0.019362 | 0.082776 | -0.074666 | 0.020409 | 0.18311 | 0.053537 | -0.24657 | 122.9014 | 0.010941 | 122.9701 | 122.9515 | 0.050071 | -0.008767 | 0.20609 | 122.7271 | -0.094032 | 122.993 | 122.899 | 0.1719 | 0.068674 | -0.060904 | 123.099 | 123.0793 | 123.2942 | 122.9842 | -0.18666 | 122.994 | 123.1567 | 123.0272 | 123.0564 | -0.36101
4410.4688 | 123.2346 | -122.9233 | 0.082397 | 1.4211e-13 | -0.016406 | -0.013505 | -0.045384 | -0.041925 | -0.012779 | -0.00083919 | 0.0092014 | 0.033309 | -0.026608 | 0.013149 | -0.019489 | -0.003531 | 0.0243 | -0.022144 | 0.12996 | 0.11025 | 0.32053 | -0.072215 | 0.023941 | 0.087354 | -0.074666 | 0.020409 | 0.18769 | 0.053537 | -0.23741 | 122.8511 | 0.047563 | 122.9197 | 122.9011 | 0.050071 | 0.027856 | 0.23813 | 122.6859 | -0.061988 | 122.9472 | 122.8486 | 0.16274 | 0.1053 | -0.02886 | 123.0532 | 123.0335 | 123.2438 | 122.9476 | -0.15461 | 122.9437 | 123.111 | 122.9768 | 123.0106 | -0.31981
4412.25 | 123.1338 | -122.9645 | 0.11902 | 1.4211e-13 | -0.016406 | -0.013505 | -0.045384 | -0.042352 | -0.012565 | 0.0067908 | 0.0089876 | 0.033523 | -0.026394 | 0.013363 | -0.019489 | -0.008109 | 0.010564 | -0.026723 | 0.12538 | 0.1011 | 0.32511 | -0.049321 | 0.02852 | 0.06904 | -0.074666 | 0.020409 | 0.18311 | 0.048958 | -0.23741 | 122.9152 | 0.006363 | 122.9564 | 122.9378 | 0.022598 | -0.017924 | 0.20609 | 122.7271 | -0.09861 | 122.993 | 122.8898 | 0.16274 | 0.064096 | -0.070061 | 123.0899 | 123.0656 | 123.2896 | 122.975 | -0.16834 | 122.9849 | 123.1476 | 123.0134 | 123.0335 | -0.35643
4414 | 123.111 | -122.9874 | 0.13275 | 1.4211e-13 | -0.016406 | -0.013291 | -0.04517 | -0.042139 | -0.012779 | -0.0161 | 0.008774 | 0.033309 | -0.026394 | 0.013149 | -0.019489 | 0.001048 | 0.010564 | -0.017566 | 0.12996 | 0.10567 | 0.31595 | -0.053899 | 0.02852 | 0.082776 | -0.070087 | 0.015831 | 0.19227 | 0.062694 | -0.23741 | 122.9335 | -0.002791 | 122.9884 | 122.9698 | 0.036333 | -0.027077 | 0.1832 | 122.75 | -0.11692 | 123.0159 | 122.9173 | 0.16732 | 0.059521 | -0.070057 | 123.1173 | 123.093 | 123.3033 | 122.9979 | -0.18665 | 123.0032 | 123.1796 | 123.0501 | 123.0701 | -0.37016
4415.7969 | 123.1064 | -122.9553 | 0.11444 | 1.4211e-13 | -0.016406 | -0.013291 | -0.045384 | -0.041925 | -0.012779 | 0.0067908 | 0.0092014 | 0.033523 | -0.026821 | 0.013363 | -0.019276 | -0.003531 | 0.015142 | -0.017566 | 0.1208 | 0.10567 | 0.32511 | -0.026426 | 0.019362 | 0.078197 | -0.065509 | 0.020409 | 0.18769 | 0.048958 | -0.22825 | 122.9289 | 0.006363 | 122.9518 | 122.9378 | 0.00886 | -0.008767 | 0.21067 | 122.7271 | -0.094032 | 122.9747 | 122.8898 | 0.16274 | 0.073252 | -0.065483 | 123.0761 | 123.061 | 123.2804 | 122.9705 | -0.14087 | 122.9757 | 123.143 | 123.0043 | 123.0335 | -0.34269
4417.6094 | 123.2346 | -122.9279 | 0.091553 | 1.4211e-13 | -0.016833 | -0.013505 | -0.045811 | -0.042352 | -0.012565 | 0.0067908 | 0.008774 | 0.033309 | -0.026394 | 0.013577 | -0.019489 | -0.003531 | 0.015142 | -0.022144 | 0.1208 | 0.11025 | 0.32511 | -0.040163 | 0.023941 | 0.078197 | -0.070087 | 0.015831 | 0.18769 | 0.058115 | -0.23741 | 122.8877 | 0.029251 | 122.9243 | 122.9057 | 0.018019 | 0.0187 | 0.23356 | 122.6904 | -0.075722 | 122.9518 | 122.8578 | 0.16732 | 0.09614 | -0.033438 | 123.0487 | 123.0381 | 123.253 | 122.943 | -0.13172 | 122.9437 | 123.1155 | 122.986 | 123.0061 | -0.32896
4419.3438 | 123.1155 | -122.9599 | 0.10071 | 1.4211e-13 | -0.017047 | -0.013291 | -0.04517 | -0.042352 | -0.012993 | -0.00083919 | 0.0092014 | 0.033523 | -0.026608 | 0.013577 | -0.019489 | 0.001048 | 0.015142 | -0.017566 | 0.12538 | 0.10567 | 0.32969 | -0.063057 | 0.02852 | 0.087354 | -0.070087 | 0.015831 | 0.19227 | 0.058115 | -0.23741 | 122.8968 | 0.024674 | 122.9609 | 122.9423 | 0.045491 | 0.004966 | 0.22898 | 122.7225 | -0.084877 | 122.9884 | 122.8898 | 0.16732 | 0.091564 | -0.042593 | 123.0853 | 123.0656 | 123.2896 | 122.975 | -0.16376 | 122.9757 | 123.1522 | 123.018 | 123.0473 | -0.33812
4421.125 | 123.1522 | -122.9691 | 0.11902 | 1.4211e-13 | -0.016619 | -0.013291 | -0.045384 | -0.042139 | -0.012779 | -0.00083919 | 0.0092014 | 0.033309 | -0.026394 | 0.013149 | -0.019276 | -0.008109 | 0.015142 | -0.017566 | 0.12538 | 0.10567 | 0.32511 | -0.081373 | 0.019362 | 0.078197 | -0.065509 | 0.024988 | 0.18769 | 0.053537 | -0.23741 | 122.8877 | 0.006363 | 122.9609 | 122.9515 | 0.063807 | -0.013345 | 0.20609 | 122.7316 | -0.094031 | 122.9884 | 122.9035 | 0.1719 | 0.068674 | -0.065482 | 123.0944 | 123.0747 | 123.2942 | 122.9842 | -0.20039 | 122.994 | 123.1567 | 123.0226 | 123.0473 | -0.35643
4422.9219 | 123.23 | -122.9141 | 0.086975 | 1.4211e-13 | -0.016619 | -0.013505 | -0.04517 | -0.042139 | -0.013206 | -0.00083919 | 0.008774 | 0.033096 | -0.027035 | 0.013577 | -0.018848 | 0.001048 | 0.019721 | -0.022144 | 0.11165 | 0.11025 | 0.32053 | -0.058478 | 0.023941 | 0.082776 | -0.070087 | 0.020409 | 0.18769 | 0.048958 | -0.23741 | 122.8556 | 0.024672 | 122.9152 | 122.892 | 0.036334 | 0.023278 | 0.23356 | 122.6767 | -0.066566 | 122.9381 | 122.844 | 0.16732 | 0.10072 | -0.038017 | 123.0258 | 123.0244 | 123.2347 | 122.9338 | -0.14545 | 122.9345 | 123.1018 | 122.9631 | 122.9969 | -0.32439
4424.6562 | 123.2254 | -122.937 | 0.091553 | 1.4211e-13 | -0.016619 | -0.013505 | -0.045598 | -0.042352 | -0.012352 | 0.0067908 | 0.0092014 | 0.033096 | -0.026394 | 0.013363 | -0.019489 | 0.001048 | 0.019721 | -0.017566 | 0.1208 | 0.10567 | 0.32969 | -0.081373 | 0.02852 | 0.078197 | -0.065509 | 0.020409 | 0.19685 | 0.035222 | -0.23741 | 122.8556 | 0.029251 | 122.9381 | 122.9194 | 0.063807 | 0.014121 | 0.23814 | 122.6996 | -0.071144 | 122.9655 | 122.8715 | 0.1719 | 0.1053 | -0.056331 | 123.0578 | 123.0427 | 123.2667 | 122.9567 | -0.17293 | 122.9574 | 123.1339 | 122.9722 | 123.0152 | -0.32896
4426.4531 | 123.1155 | -122.9691 | 0.1236 | 1.4211e-13 | -0.016406 | -0.013077 | -0.045598 | -0.042566 | -0.012779 | 0.0067908 | 0.0092014 | 0.033309 | -0.026394 | 0.013363 | -0.019276 | 0.001048 | 0.015142 | -0.022144 | 0.12538 | 0.10567 | 0.32053 | -0.044742 | 0.02852 | 0.078197 | -0.070087 | 0.020409 | 0.20143 | 0.048958 | -0.23283 | 122.9243 | 0.001786 | 122.9701 | 122.9469 | 0.022598 | -0.017922 | 0.19694 | 122.7362 | -0.10319 | 122.9976 | 122.899 | 0.16274 | 0.077833 | -0.074638 | 123.0944 | 123.0747 | 123.2896 | 122.9842 | -0.16834 | 122.9895 | 123.1705 | 123.018 | 123.0473 | -0.35643
4428.25 | 123.111 | -123.0011 | 0.13733 | 1.4211e-13 | -0.016833 | -0.013291 | -0.045811 | -0.042139 | -0.012779 | 0.0067908 | 0.0089876 | 0.033309 | -0.026608 | 0.013149 | -0.019276 | -0.008109 | 0.028878 | -0.022144 | 0.12538 | 0.1011 | 0.32969 | -0.085952 | 0.023941 | 0.073618 | -0.079245 | 0.020409 | 0.19227 | 0.044379 | -0.23283 | 122.9151 | -0.011947 | 122.993 | 122.979 | 0.063808 | -0.036234 | 0.19236 | 122.7683 | -0.11692 | 123.025 | 122.9219 | 0.15359 | 0.054943 | -0.09295 | 123.1265 | 123.1022 | 123.3308 | 123.03 | -0.22328 | 123.0215 | 123.1934 | 123.0455 | 123.0747 | -0.37016
4430.0625 | 123.1064 | -122.9874 | 0.11902 | 1.4211e-13 | -0.016833 | -0.013291 | -0.045384 | -0.041925 | -0.012779 | -0.00083919 | 0.0092014 | 0.033523 | -0.026608 | 0.014004 | -0.019062 | -0.003531 | 0.010564 | -0.017566 | 0.1208 | 0.1011 | 0.32511 | -0.067636 | 0.023941 | 0.078197 | -0.065509 | 0.020409 | 0.18769 | 0.016908 | -0.23283 | 122.9197 | 0.001785 | 122.9838 | 122.9698 | 0.05007 | -0.017924 | 0.20609 | 122.7545 | -0.09861 | 123.0113 | 122.9219 | 0.16732 | 0.068674 | -0.10211 | 123.1082 | 123.0885 | 123.3125 | 122.9979 | -0.18666 | 123.0078 | 123.1751 | 123.0043 | 123.0656 | -0.35185
4431.7969 | 123.1659 | -122.937 | 0.10071 | 1.4211e-13 | -0.016619 | -0.013718 | -0.04517 | -0.041925 | -0.012779 | 0.0067908 | 0.0092014 | 0.033523 | -0.026608 | 0.013363 | -0.019276 | 0.005626 | 0.019721 | -0.017566 | 0.13454 | 0.10567 | 0.32969 | -0.076794 | 0.019362 | 0.082776 | -0.065509 | 0.015831 | 0.18769 | 0.053537 | -0.23283 | 122.8602 | 0.033831 | 122.9426 | 122.9194 | 0.059228 | 0.004966 | 0.22898 | 122.7042 | -0.084877 | 122.9564 | 122.8715 | 0.16732 | 0.086985 | -0.047171 | 123.0716 | 123.0427 | 123.2667 | 122.9567 | -0.1775 | 122.9528 | 123.1247 | 122.9905 | 123.0198 | -0.33354
4433.5938 | 123.1613 | -122.9462 | 0.10986 | 1.4211e-13 | -0.016406 | -0.012863 | -0.045384 | -0.041925 | -0.012565 | 0.0067908 | 0.009415 | 0.033523 | -0.026608 | 0.013577 | -0.019276 | 0.005626 | 0.015142 | -0.022144 | 0.12538 | 0.10567 | 0.32511 | -0.081373 | 0.02852 | 0.087354 | -0.065509 | 0.015831 | 0.20143 | 0.053537 | -0.23283 | 122.8648 | 0.015519 | 122.9518 | 122.924 | 0.059229 | -0.004189 | 0.21525 | 122.7133 | -0.094032 | 122.9747 | 122.8807 | 0.16732 | 0.091566 | -0.056326 | 123.0715 | 123.0518 | 123.2713 | 122.9613 | -0.19124 | 122.962 | 123.1476 | 122.9997 | 123.0335 | -0.34269
4435.3906 | 123.1247 | -122.9828 | 0.11902 | 1.4211e-13 | -0.016619 | -0.013291 | -0.04517 | -0.041925 | -0.012779 | -0.00083919 | 0.0092014 | 0.033096 | -0.026821 | 0.01379 | -0.019276 | 0.005626 | 0.019721 | -0.017566 | 0.12996 | 0.096516 | 0.33885 | -0.058478 | 0.033099 | 0.073618 | -0.065509 | 0.020409 | 0.18769 | 0.058115 | -0.23741 | 122.9243 | 0.010941 | 122.9884 | 122.9652 | 0.040912 | -0.022503 | 0.21983 | 122.7454 | -0.09861 | 123.0159 | 122.9173 | 0.1719 | 0.068674 | -0.060904 | 123.1127 | 123.0793 | 123.3216 | 123.0025 | -0.1775 | 123.0032 | 123.1705 | 123.0409 | 123.0564 | -0.35643
4437.1094 | 123.1659 | -122.9599 | 0.12817 | 1.4211e-13 | -0.016406 | -0.013077 | -0.045384 | -0.042352 | -0.012993 | -0.00083919 | 0.0089876 | 0.033309 | -0.026394 | 0.013577 | -0.019276 | 0.001048 | 0.019721 | -0.026723 | 0.12538 | 0.10567 | 0.32511 | -0.058478 | 0.02852 | 0.087354 | -0.065509 | 0.020409 | 0.18769 | 0.053537 | -0.23741 | 122.9014 | -0.002792 | 122.9609 | 122.9332 | 0.031755 | -0.0225 | 0.19694 | 122.7225 | -0.10777 | 122.9884 | 122.8944 | 0.1719 | 0.059519 | -0.074637 | 123.0853 | 123.0656 | 123.285 | 122.9796 | -0.18665 | 122.9803 | 123.1476 | 123.0134 | 123.0473 | -0.36558
4438.9062 | 123.1888 | -122.9507 | 0.073242 | 1.4211e-13 | -0.016619 | -0.013077 | -0.045384 | -0.041925 | -0.012993 | 0.0067908 | 0.0092014 | 0.033096 | -0.026608 | 0.013577 | -0.019062 | 0.005626 | 0.015142 | -0.022144 | 0.12538 | 0.11025 | 0.32969 | -0.076794 | 0.023941 | 0.082776 | -0.074666 | 0.015831 | 0.19227 | 0.053537 | -0.23741 | 122.874 | 0.05214 | 122.9564 | 122.9286 | 0.05465 | 0.037011 | 0.25645 | 122.7133 | -0.057411 | 122.9747 | 122.8761 | 0.16274 | 0.11903 | -0.019705 | 123.0761 | 123.061 | 123.2804 | 122.9659 | -0.15004 | 122.9666 | 123.143 | 123.0043 | 123.0335 | -0.31065
4440.6406 | 123.2208 | -122.9416 | 0.07782 | 1.4211e-13 | -0.016406 | -0.013291 | -0.045384 | -0.041925 | -0.012993 | -0.0161 | 0.0089876 | 0.033309 | -0.026608 | 0.013363 | -0.019276 | -0.003531 | 0.015142 | -0.017566 | 0.12538 | 0.11025 | 0.32511 | -0.081373 | 0.023941 | 0.082776 | -0.070087 | 0.020409 | 0.18311 | 0.044379 | -0.23741 | 122.8602 | 0.047562 | 122.9381 | 122.924 | 0.063807 | 0.032433 | 0.24729 | 122.7042 | -0.057411 | 122.9655 | 122.8715 | 0.16732 | 0.10529 | -0.033441 | 123.067 | 123.0518 | 123.2667 | 122.9567 | -0.15919 | 122.962 | 123.1247 | 122.986 | 123.0244 | -0.31523
4442.4219 | 123.1842 | -122.9645 | 0.091553 | 1.4211e-13 | -0.016833 | -0.013505 | -0.045384 | -0.042139 | -0.012565 | -0.0161 | 0.009415 | 0.033523 | -0.026821 | 0.013149 | -0.019276 | 0.001048 | 0.0243 | -0.017566 | 0.12538 | 0.10567 | 0.31595 | -0.076794 | 0.023941 | 0.087354 | -0.070087 | 0.020409 | 0.18769 | 0.053537 | -0.23741 | 122.8877 | 0.033829 | 122.9655 | 122.9469 | 0.059228 | 0.014121 | 0.2244 | 122.7271 | -0.071144 | 122.9884 | 122.8944 | 0.16732 | 0.09614 | -0.038016 | 123.0899 | 123.0702 | 123.2804 | 122.9888 | -0.16835 | 122.9849 | 123.1522 | 123.018 | 123.0518 | -0.32896
4444.2188 | 123.1247 | -122.9874 | 0.12817 | 1.4211e-13 | -0.016406 | -0.013505 | -0.045811 | -0.042139 | -0.012565 | -0.0084697 | 0.0089876 | 0.033309 | -0.026821 | 0.013577 | -0.019276 | -0.003531 | 0.015142 | -0.022144 | 0.13454 | 0.10567 | 0.31595 | -0.076794 | 0.02852 | 0.078197 | -0.074666 | 0.020409 | 0.18311 | 0.048958 | -0.23741 | 122.9106 | 0.006365 | 122.9838 | 122.9652 | 0.05465 | -0.0225 | 0.18778 | 122.75 | -0.10777 | 123.0159 | 122.9127 | 0.16274 | 0.054941 | -0.079216 | 123.1219 | 123.093 | 123.3033 | 123.0025 | -0.20497 | 123.0078 | 123.1705 | 123.0363 | 123.0656 | -0.36558
4445.9531 | 123.1842 | -122.9645 | 0.082397 | 1.4211e-13 | -0.016619 | -0.013505 | -0.045384 | -0.042139 | -0.012993 | -0.00083919 | 0.0092014 | 0.033523 | -0.026608 | 0.013577 | -0.019276 | -0.003531 | 0.019721 | -0.022144 | 0.12538 | 0.1011 | 0.32053 | -0.053899 | 0.033099 | 0.078197 | -0.070087 | 0.024988 | 0.18769 | 0.053537 | -0.23283 | 122.9106 | 0.042985 | 122.9609 | 122.9423 | 0.031755 | 0.018698 | 0.23813 | 122.7316 | -0.057409 | 122.9976 | 122.8944 | 0.16274 | 0.1053 | -0.02886 | 123.0899 | 123.0656 | 123.285 | 122.9842 | -0.1363 | 122.9895 | 123.1522 | 123.018 | 123.0427 | -0.31523
4447.75 | 123.1659 | -122.9691 | 0.1236 | 1.4211e-13 | -0.016619 | -0.013505 | -0.045811 | -0.04278 | -0.012779 | -0.00083919 | 0.0092014 | 0.033309 | -0.026394 | 0.013577 | -0.019276 | -0.003531 | 0.019721 | -0.022144 | 0.12996 | 0.1011 | 0.32053 | -0.063057 | 0.023941 | 0.078197 | -0.079245 | 0.015831 | 0.18769 | 0.053537 | -0.23283 | 122.906 | 0.006364 | 122.9655 | 122.9469 | 0.040913 | -0.022501 | 0.19694 | 122.7362 | -0.10776 | 122.993 | 122.8898 | 0.15359 | 0.064097 | -0.070059 | 123.099 | 123.0701 | 123.2896 | 122.9888 | -0.18665 | 122.9849 | 123.1567 | 123.0226 | 123.0473 | -0.35643
4449.4844 | 123.2117 | -122.9324 | 0.10071 | 1.4211e-13 | -0.016619 | -0.013505 | -0.045384 | -0.042352 | -0.012779 | -0.00083919 | 0.0092014 | 0.033309 | -0.026608 | 0.01379 | -0.019062 | 0.001048 | 0.019721 | -0.022144 | 0.12538 | 0.1011 | 0.32511 | -0.072215 | 0.023941 | 0.082776 | -0.070087 | 0.015831 | 0.18311 | 0.058115 | -0.23741 | 122.8602 | 0.024674 | 122.9335 | 122.9103 | 0.050071 | 0.000387 | 0.2244 | 122.695 | -0.084877 | 122.9564 | 122.8623 | 0.16732 | 0.082407 | -0.042593 | 123.0578 | 123.0335 | 123.2575 | 122.9522 | -0.17292 | 122.9483 | 123.1155 | 122.9905 | 123.0152 | -0.33812
4451.2656 | 123.1979 | -122.9645 | 0.082397 | 1.4211e-13 | -0.016619 | -0.013505 | -0.04517 | -0.042139 | -0.012779 | 0.0067908 | 0.0092014 | 0.033096 | -0.026608 | 0.013149 | -0.019489 | 0.001048 | 0.019721 | -0.017566 | 0.12996 | 0.11025 | 0.32969 | -0.076794 | 0.033099 | 0.082776 | -0.065509 | 0.015831 | 0.19227 | 0.048958 | -0.23283 | 122.8877 | 0.047563 | 122.9655 | 122.9469 | 0.059228 | 0.027856 | 0.24729 | 122.7316 | -0.066566 | 122.9976 | 122.899 | 0.16732 | 0.10988 | -0.033439 | 123.0944 | 123.0747 | 123.2942 | 122.9842 | -0.15919 | 122.9803 | 123.1568 | 123.0134 | 123.0473 | -0.31523
4453.0625 | 123.111 | -122.9828 | 0.10986 | 1.4211e-13 | -0.016619 | -0.013291 | -0.04517 | -0.041925 | -0.012993 | 0.0067908 | 0.0092014 | 0.033523 | -0.026608 | 0.013149 | -0.019703 | -0.003531 | 0.019721 | -0.022144 | 0.12538 | 0.10567 | 0.32969 | -0.10427 | 0.023941 | 0.078197 | -0.070087 | 0.020409 | 0.18769 | 0.058115 | -0.22825 | 122.8785 | 0.015519 | 122.9793 | 122.9606 | 0.082124 | -0.004189 | 0.21983 | 122.7545 | -0.089454 | 123.0067 | 122.9127 | 0.15817 | 0.07783 | -0.051748 | 123.1082 | 123.0885 | 123.3125 | 123.0025 | -0.21413 | 123.0032 | 123.1705 | 123.0409 | 123.061 | -0.33811
4454.8125 | 123.1018 | -122.9919 | 0.10986 | 1.4211e-13 | -0.016619 | -0.013291 | -0.045384 | -0.042352 | -0.012993 | 0.0067908 | 0.0092014 | 0.032882 | -0.026608 | 0.01379 | -0.019276 | 0.001048 | 0.019721 | -0.012988 | 0.12538 | 0.10567 | 0.32053 | -0.063057 | 0.023941 | 0.087354 | -0.074666 | 0.024988 | 0.18769 | 0.062694 | -0.24199 | 122.9289 | 0.015519 | 122.993 | 122.979 | 0.050069 | -0.004189 | 0.21067 | 122.75 | -0.084875 | 123.0159 | 122.9173 | 0.16732 | 0.07783 | -0.047169 | 123.1173 | 123.0976 | 123.3125 | 123.0117 | -0.17292 | 123.0169 | 123.1796 | 123.0546 | 123.0793 | -0.35185
4456.6094 | 123.23 | -122.9553 | 0.09613 | 1.4211e-13 | -0.016192 | -0.013505 | -0.045384 | -0.041711 | -0.012779 | -0.00083919 | 0.0089876 | 0.033737 | -0.026608 | 0.01379 | -0.019489 | 0.005626 | 0.019721 | -0.022144 | 0.1208 | 0.1011 | 0.32511 | -0.076794 | 0.019362 | 0.082776 | -0.065509 | 0.020409 | 0.19685 | 0.062694 | -0.22825 | 122.8785 | 0.024674 | 122.9609 | 122.9332 | 0.05465 | 0.004965 | 0.22898 | 122.7271 | -0.075721 | 122.9747 | 122.8898 | 0.16274 | 0.10072 | -0.033436 | 123.0761 | 123.0564 | 123.2804 | 122.975 | -0.17292 | 122.9757 | 123.1522 | 123.018 | 123.0381 | -0.32438
4458.3906 | 123.262 | -122.9462 | 0.086975 | 1.4211e-13 | -0.016406 | -0.013505 | -0.045598 | -0.042139 | -0.012779 | -0.00083919 | 0.0092014 | 0.033737 | -0.026608 | 0.01379 | -0.019489 | 0.001048 | 0.0243 | -0.017566 | 0.12538 | 0.1011 | 0.32511 | -0.090531 | 0.02852 | 0.082776 | -0.06093 | 0.020409 | 0.17854 | 0.053537 | -0.23283 | 122.8556 | 0.038407 | 122.9472 | 122.9286 | 0.072965 | 0.01412 | 0.23814 | 122.7133 | -0.066566 | 122.9747 | 122.8852 | 0.1719 | 0.091561 | -0.033438 | 123.0715 | 123.0473 | 123.2713 | 122.9705 | -0.17751 | 122.9666 | 123.1247 | 122.9997 | 123.0289 | -0.31981
4460.1875 | 123.1522 | -122.9507 | 0.11902 | 1.4211e-13 | -0.016406 | -0.013077 | -0.045384 | -0.042139 | -0.012993 | -0.00083919 | 0.0092014 | 0.033523 | -0.026394 | 0.013577 | -0.019062 | -0.008109 | 0.019721 | -0.012988 | 0.12538 | 0.1011 | 0.32053 | -0.081373 | 0.023941 | 0.078197 | -0.074666 | 0.020409 | 0.18769 | 0.053537 | -0.23283 | 122.8694 | 0.006363 | 122.9426 | 122.9378 | 0.068385 | -0.017924 | 0.20151 | 122.7179 | -0.09861 | 122.9747 | 122.8761 | 0.15817 | 0.068674 | -0.065482 | 123.0761 | 123.0518 | 123.2713 | 122.9705 | -0.20039 | 122.9712 | 123.1384 | 123.0043 | 123.0289 | -0.35185
4461.9375 | 123.1567 | -122.9782 | 0.10986 | 1.4211e-13 | -0.016619 | -0.013718 | -0.04517 | -0.042352 | -0.012779 | -0.0084697 | 0.0092014 | 0.033523 | -0.026608 | 0.013577 | -0.019062 | 0.001048 | 0.0243 | -0.026723 | 0.1208 | 0.1011 | 0.32511 | -0.085952 | 0.02852 | 0.078197 | -0.074666 | 0.020409 | 0.19227 | 0.058115 | -0.23283 | 122.8923 | 0.010941 | 122.9793 | 122.9515 | 0.059229 | -0.008768 | 0.21525 | 122.7454 | -0.089454 | 123.0067 | 122.9035 | 0.15817 | 0.082409 | -0.051748 | 123.099 | 123.0793 | 123.3033 | 123.0025 | -0.19582 | 122.9986 | 123.1705 | 123.0363 | 123.0564 | -0.34269
4463.7344 | 123.1247 | -123.0011 | 0.11902 | 1.4211e-13 | -0.016619 | -0.013505 | -0.045384 | -0.042352 | -0.012565 | 0.0067908 | 0.009415 | 0.033523 | -0.026821 | 0.013577 | -0.019276 | 0.001048 | 0.0243 | -0.022144 | 0.12538 | 0.1011 | 0.32053 | -0.072215 | 0.033099 | 0.06904 | -0.065509 | 0.020409 | 0.19227 | 0.062694 | -0.23741 | 122.9289 | 0.006363 | 123.0021 | 122.979 | 0.050071 | -0.017924 | 0.20151 | 122.7637 | -0.09861 | 123.0342 | 122.9356 | 0.1719 | 0.073253 | -0.056325 | 123.1265 | 123.1022 | 123.3216 | 123.0254 | -0.19123 | 123.0215 | 123.1934 | 123.0638 | 123.0701 | -0.35643
4465.5312 | 123.2758 | -122.9507 | 0.082397 | 1.4211e-13 | -0.016192 | -0.013291 | -0.045598 | -0.041925 | -0.012565 | -0.0084697 | 0.0089876 | 0.033096 | -0.026608 | 0.013149 | -0.019489 | 0.001048 | 0.015142 | -0.017566 | 0.11622 | 0.1011 | 0.32053 | -0.067636 | 0.023941 | 0.078197 | -0.070087 | 0.020409 | 0.19227 | 0.058115 | -0.24199 | 122.8831 | 0.033828 | 122.9518 | 122.9332 | 0.05007 | 0.018698 | 0.23813 | 122.7088 | -0.061988 | 122.9747 | 122.8807 | 0.1719 | 0.10988 | -0.024282 | 123.067 | 123.0518 | 123.2713 | 122.9659 | -0.15003 | 122.9712 | 123.143 | 123.0089 | 123.0289 | -0.32439
4467.2656 | 123.2529 | -122.9324 | 0.091553 | 1.4211e-13 | -0.016406 | -0.013291 | -0.045598 | -0.042139 | -0.012993 | -0.00083919 | 0.009415 | 0.033737 | -0.026394 | 0.013577 | -0.018848 | 0.001048 | 0.019721 | -0.026723 | 0.12996 | 0.10567 | 0.32511 | -0.09511 | 0.023941 | 0.082776 | -0.065509 | 0.029566 | 0.19227 | 0.058115 | -0.23283 | 122.8373 | 0.038407 | 122.9335 | 122.9057 | 0.068387 | 0.014121 | 0.23356 | 122.6996 | -0.061987 | 122.9564 | 122.8669 | 0.16732 | 0.10072 | -0.033438 | 123.0624 | 123.0381 | 123.2575 | 122.9522 | -0.18666 | 122.962 | 123.1247 | 122.9905 | 123.0152 | -0.32438
4469.0781 | 123.2666 | -122.9691 | 0.082397 | 1.4211e-13 | -0.016619 | -0.013505 | -0.04517 | -0.042139 | -0.012993 | 0.0067908 | 0.008774 | 0.033309 | -0.026608 | 0.013363 | -0.019062 | 0.005626 | 0.015142 | -0.017566 | 0.12538 | 0.10567 | 0.32511 | -0.076794 | 0.019362 | 0.082776 | -0.065509 | 0.015831 | 0.20143 | 0.048958 | -0.23741 | 122.8923 | 0.042985 | 122.9747 | 122.9515 | 0.059228 | 0.023277 | 0.24271 | 122.7316 | -0.066566 | 122.9884 | 122.9035 | 0.1719 | 0.11903 | -0.033439 | 123.0944 | 123.0747 | 123.2942 | 122.9842 | -0.15919 | 122.9849 | 123.1705 | 123.018 | 123.0518 | -0.31981
4470.8125 | 123.2208 | -122.9553 | 0.10529 | 1.4211e-13 | -0.016619 | -0.013077 | -0.045384 | -0.042352 | -0.013206 | 0.0067908 | 0.009415 | 0.033523 | -0.026821 | 0.013577 | -0.019489 | 0.001048 | 0.015142 | -0.022144 | 0.12538 | 0.096516 | 0.32511 | -0.090531 | 0.02852 | 0.082776 | -0.065509 | 0.024988 | 0.19685 | 0.053537 | -0.23283 | 122.8648 | 0.020096 | 122.9564 | 122.9332 | 0.068387 | -0.00877 | 0.21982 | 122.7225 | -0.080298 | 122.9838 | 122.8898 | 0.16732 | 0.091565 | -0.051749 | 123.0807 | 123.0518 | 123.2804 | 122.9705 | -0.19582 | 122.9803 | 123.1522 | 123.0089 | 123.0381 | -0.33812
4472.6094 | 123.1979 | -122.9691 | 0.082397 | 1.4211e-13 | -0.016833 | -0.013291 | -0.045384 | -0.041925 | -0.012565 | -0.0084697 | 0.0092014 | 0.033523 | -0.027035 | 0.01379 | -0.019276 | 0.001048 | 0.015142 | -0.022144 | 0.12996 | 0.096516 | 0.32511 | -0.063057 | 0.019362 | 0.078197 | -0.065509 | 0.020409 | 0.19227 | 0.030644 | -0.23283 | 122.906 | 0.047563 | 122.9701 | 122.9469 | 0.040913 | 0.014119 | 0.24271 | 122.7362 | -0.061988 | 122.9884 | 122.9035 | 0.16732 | 0.10988 | -0.051753 | 123.099 | 123.0656 | 123.2942 | 122.9842 | -0.14545 | 122.9895 | 123.1613 | 122.9997 | 123.0473 | -0.31523
4474.4062 | 123.2483 | -122.937 | 0.091553 | 1.4211e-13 | -0.016406 | -0.013291 | -0.045384 | -0.042139 | -0.012565 | 0.0067908 | 0.0092014 | 0.033309 | -0.026608 | 0.01379 | -0.019489 | -0.003531 | 0.019721 | -0.017566 | 0.12996 | 0.11025 | 0.32511 | -0.090531 | 0.023941 | 0.082776 | -0.074666 | 0.020409 | 0.19227 | 0.062694 | -0.24199 | 122.8465 | 0.038407 | 122.9335 | 122.9194 | 0.072965 | 0.0187 | 0.23356 | 122.695 | -0.071144 | 122.961 | 122.8623 | 0.16732 | 0.10072 | -0.028859 | 123.067 | 123.0473 | 123.2621 | 122.9567 | -0.18208 | 122.9574 | 123.1293 | 122.9997 | 123.0198 | -0.33354
4476.125 | 123.1979 | -122.9691 | 0.086975 | 1.4211e-13 | -0.016833 | -0.013505 | -0.045598 | -0.042139 | -0.012779 | 0.0067908 | 0.0092014 | 0.033737 | -0.026821 | 0.013149 | -0.019489 | 0.001048 | 0.0243 | -0.017566 | 0.12538 | 0.10567 | 0.32969 | -0.072215 | 0.023941 | 0.082776 | -0.074666 | 0.020409 | 0.18769 | 0.030644 | -0.23283 | 122.8968 | 0.038407 | 122.9701 | 122.9515 | 0.054649 | 0.018699 | 0.24271 | 122.7362 | -0.066566 | 122.993 | 122.8944 | 0.15817 | 0.10072 | -0.056331 | 123.0944 | 123.0747 | 123.2987 | 122.9934 | -0.15919 | 122.9895 | 123.1567 | 122.9997 | 123.0518 | -0.31981
4477.9219 | 123.111 | -123.0148 | 0.10529 | 1.4211e-13 | -0.016833 | -0.013505 | -0.044957 | -0.042566 | -0.012352 | -0.00083919 | 0.0092014 | 0.033309 | -0.026821 | 0.01379 | -0.019276 | 0.005626 | 0.0243 | -0.012988 | 0.12538 | 0.10567 | 0.32053 | -0.076794 | 0.023941 | 0.06904 | -0.065509 | 0.015831 | 0.18769 | 0.053537 | -0.23741 | 122.938 | 0.020096 | 123.0205 | 123.0018 | 0.063806 | 0.000388 | 0.21525 | 122.7774 | -0.089455 | 123.0388 | 122.9493 | 0.1719 | 0.082407 | -0.051749 | 123.1402 | 123.1205 | 123.3354 | 123.0391 | -0.18208 | 123.0307 | 123.2025 | 123.0684 | 123.0839 | -0.3427
4479.7344 | 123.2391 | -122.9645 | 0.082397 | 1.4211e-13 | -0.016619 | -0.013291 | -0.045384 | -0.042139 | -0.012993 | -0.0084697 | 0.009415 | 0.033096 | -0.026821 | 0.013577 | -0.019276 | 0.001048 | 0.0243 | -0.022144 | 0.12538 | 0.096516 | 0.32969 | -0.067636 | 0.023941 | 0.078197 | -0.065509 | 0.024988 | 0.19227 | 0.053537 | -0.23283 | 122.8968 | 0.042985 | 122.9655 | 122.9423 | 0.045492 | 0.014119 | 0.24729 | 122.7316 | -0.057409 | 122.9884 | 122.899 | 0.16732 | 0.10988 | -0.02886 | 123.0899 | 123.061 | 123.2942 | 122.9888 | -0.15003 | 122.9895 | 123.1568 | 123.018 | 123.0427 | -0.31523
4481.4688 | 123.2071 | -122.9645 | 0.07782 | 1.4211e-13 | -0.017047 | -0.013291 | -0.045384 | -0.042139 | -0.012993 | -0.0084697 | 0.009415 | 0.033096 | -0.026394 | 0.013577 | -0.019276 | 0.010204 | 0.019721 | -0.017566 | 0.12996 | 0.1011 | 0.32969 | -0.076794 | 0.023941 | 0.082776 | -0.074666 | 0.024988 | 0.19227 | 0.053537 | -0.23283 | 122.8877 | 0.05214 | 122.9747 | 122.9469 | 0.059228 | 0.023275 | 0.25187 | 122.7316 | -0.052832 | 122.9884 | 122.8898 | 0.15817 | 0.11445 | -0.024283 | 123.0944 | 123.0656 | 123.2942 | 122.9842 | -0.15461 | 122.9895 | 123.1568 | 123.018 | 123.0473 | -0.31065
4483.25 | 123.1888 | -122.9553 | 0.082397 | 1.4211e-13 | -0.016833 | -0.013291 | -0.045384 | -0.042352 | -0.012779 | 0.014421 | 0.0089876 | 0.033309 | -0.026608 | 0.013577 | -0.019276 | 0.001048 | 0.019721 | -0.017566 | 0.12538 | 0.1011 | 0.32969 | -0.072215 | 0.023941 | 0.078197 | -0.065509 | 0.020409 | 0.19685 | 0.062694 | -0.23283 | 122.8831 | 0.042985 | 122.9564 | 122.9378 | 0.054649 | 0.018698 | 0.24729 | 122.7225 | -0.061988 | 122.9793 | 122.8898 | 0.16732 | 0.11445 | -0.019703 | 123.0807 | 123.0564 | 123.285 | 122.975 | -0.15461 | 122.9757 | 123.1522 | 123.018 | 123.0335 | -0.31523
4485.0469 | 123.23 | -122.9279 | 0.091553 | 1.4211e-13 | -0.016406 | -0.013505 | -0.045598 | -0.042139 | -0.012993 | 0.014421 | 0.0089876 | 0.033309 | -0.026608 | 0.013363 | -0.019276 | 0.001048 | 0.015142 | -0.022144 | 0.12538 | 0.10567 | 0.32053 | -0.081373 | 0.02852 | 0.078197 | -0.070087 | 0.024988 | 0.19685 | 0.062694 | -0.23283 | 122.8465 | 0.033829 | 122.9289 | 122.9057 | 0.059229 | 0.014121 | 0.22898 | 122.695 | -0.066565 | 122.9564 | 122.8578 | 0.16274 | 0.1053 | -0.028859 | 123.0532 | 123.0335 | 123.2484 | 122.943 | -0.17293 | 122.9528 | 123.1247 | 122.9905 | 123.0061 | -0.32438
4486.7812 | 123.2483 | -122.9553 | 0.082397 | 1.4211e-13 | -0.016619 | -0.013291 | -0.045598 | -0.042139 | -0.013206 | -0.00083919 | 0.0092014 | 0.033737 | -0.026821 | 0.013577 | -0.019276 | 0.010204 | 0.028878 | -0.022144 | 0.12538 | 0.096516 | 0.32511 | -0.085952 | 0.023941 | 0.078197 | -0.065509 | 0.024988 | 0.18311 | 0.058115 | -0.22825 | 122.8694 | 0.042985 | 122.9655 | 122.9332 | 0.063808 | 0.014119 | 0.24271 | 122.7271 | -0.057409 | 122.9793 | 122.8898 | 0.16274 | 0.10072 | -0.024282 | 123.0807 | 123.0518 | 123.2804 | 122.9842 | -0.16835 | 122.9803 | 123.1384 | 123.0134 | 123.0335 | -0.31065
4488.5781 | 123.175 | -123.0011 | 0.10986 | 1.4211e-13 | -0.016619 | -0.013718 | -0.045384 | -0.042352 | -0.012993 | -0.00083919 | 0.0092014 | 0.033523 | -0.026608 | 0.013363 | -0.019276 | -0.003531 | 0.0243 | -0.017566 | 0.12538 | 0.1011 | 0.32511 | -0.053899 | 0.023941 | 0.073618 | -0.070087 | 0.020409 | 0.18769 | 0.058115 | -0.23283 | 122.9472 | 0.015519 | 122.9976 | 122.9835 | 0.036333 | -0.008768 | 0.21525 | 122.7683 | -0.089454 | 123.025 | 122.931 | 0.16274 | 0.07783 | -0.051748 | 123.1265 | 123.1022 | 123.3262 | 123.0254 | -0.16376 | 123.0215 | 123.1888 | 123.0592 | 123.0747 | -0.34269
4490.3594 | 123.2529 | -122.9279 | 0.064087 | 1.4211e-13 | -0.016833 | -0.013291 | -0.04517 | -0.042352 | -0.012779 | 0.0067908 | 0.0092014 | 0.033523 | -0.026181 | 0.01379 | -0.019489 | -0.003531 | 0.019721 | -0.022144 | 0.11622 | 0.1011 | 0.32969 | -0.063057 | 0.02852 | 0.087354 | -0.070087 | 0.024988 | 0.18769 | 0.067272 | -0.22825 | 122.8648 | 0.052138 | 122.9243 | 122.9057 | 0.040913 | 0.037008 | 0.2656 | 122.6996 | -0.039099 | 122.9564 | 122.8578 | 0.15817 | 0.12361 | 0.003185 | 123.0441 | 123.029 | 123.2575 | 122.9476 | -0.12714 | 122.9528 | 123.1155 | 122.9951 | 123.0152 | -0.29234
4492.1562 | 123.2391 | -122.9507 | 0.091553 | 1.4211e-13 | -0.016833 | -0.012863 | -0.045384 | -0.041925 | -0.012779 | -0.00083919 | 0.009415 | 0.033523 | -0.026608 | 0.013363 | -0.019276 | 0.001048 | 0.015142 | -0.017566 | 0.12538 | 0.11025 | 0.32511 | -0.085952 | 0.02852 | 0.078197 | -0.070087 | 0.020409 | 0.18769 | 0.067272 | -0.23283 | 122.8648 | 0.033829 | 122.9518 | 122.9332 | 0.068386 | 0.0187 | 0.23356 | 122.7179 | -0.071144 | 122.9793 | 122.8807 | 0.16274 | 0.09614 | -0.024281 | 123.0761 | 123.061 | 123.2759 | 122.9659 | -0.1775 | 122.9712 | 123.1384 | 123.018 | 123.0289 | -0.32438
4493.8906 | 123.1796 | -122.9919 | 0.10986 | 1.4211e-13 | -0.016833 | -0.013077 | -0.04517 | -0.041925 | -0.012993 | -0.0084697 | 0.0089876 | 0.033096 | -0.026608 | 0.013577 | -0.019276 | 0.005626 | 0.019721 | -0.022144 | 0.12538 | 0.11025 | 0.32053 | -0.058478 | 0.02852 | 0.082776 | -0.074666 | 0.015831 | 0.19227 | 0.053537 | -0.23283 | 122.9335 | 0.015519 | 122.9976 | 122.9698 | 0.036334 | 0.00039 | 0.21067 | 122.7591 | -0.094032 | 123.0205 | 122.9173 | 0.15817 | 0.082409 | -0.056326 | 123.1173 | 123.1022 | 123.3125 | 123.0117 | -0.16834 | 123.0078 | 123.1842 | 123.0455 | 123.0747 | -0.34269
4495.6875 | 123.2071 | -122.9645 | 0.10986 | 1.4211e-13 | -0.016833 | -0.013291 | -0.04517 | -0.042566 | -0.012779 | 0.0067908 | 0.009415 | 0.033523 | -0.026608 | 0.013577 | -0.019703 | 0.001048 | 0.0243 | -0.026723 | 0.11622 | 0.10567 | 0.32053 | -0.085952 | 0.023941 | 0.082776 | -0.06093 | 0.020409 | 0.18769 | 0.048958 | -0.23283 | 122.8785 | 0.006362 | 122.9655 | 122.9378 | 0.059229 | -0.004189 | 0.21067 | 122.7316 | -0.089454 | 122.9884 | 122.9035 | 0.1719 | 0.07783 | -0.060905 | 123.0807 | 123.0702 | 123.285 | 122.9888 | -0.19582 | 122.9849 | 123.1522 | 123.0134 | 123.0473 | -0.34269
4497.4844 | 123.2712 | -122.9507 | 0.064087 | 1.4211e-13 | -0.016406 | -0.013505 | -0.045384 | -0.042139 | -0.012779 | -0.00083919 | 0.0092014 | 0.033523 | -0.026821 | 0.013363 | -0.019489 | -0.003531 | 0.019721 | -0.012988 | 0.12538 | 0.1011 | 0.32969 | -0.09511 | 0.023941 | 0.078197 | -0.065509 | 0.020409 | 0.19227 | 0.048958 | -0.23741 | 122.8556 | 0.061295 | 122.9472 | 122.9378 | 0.082122 | 0.037008 | 0.2656 | 122.7133 | -0.043678 | 122.9747 | 122.8852 | 0.1719 | 0.12818 | -0.015129 | 123.0761 | 123.0518 | 123.2804 | 122.9705 | -0.1592 | 122.9712 | 123.143 | 122.9997 | 123.0289 | -0.3015
4499.2656 | 123.1338 | -122.9874 | 0.11902 | 1.4211e-13 | -0.016619 | -0.013505 | -0.04517 | -0.041925 | -0.012565 | 0.0067908 | 0.0089876 | 0.033309 | -0.026608 | 0.013363 | -0.019062 | -0.003531 | 0.0243 | -0.026723 | 0.12996 | 0.10567 | 0.32969 | -0.072215 | 0.02852 | 0.078197 | -0.065509 | 0.020409 | 0.18769 | 0.062694 | -0.23283 | 122.9152 | 0.010941 | 122.9838 | 122.9606 | 0.045492 | -0.013345 | 0.21067 | 122.7545 | -0.09861 | 123.0159 | 122.9219 | 0.16732 | 0.068674 | -0.056325 | 123.1173 | 123.093 | 123.3171 | 123.0117 | -0.19123 | 123.0078 | 123.1751 | 123.0501 | 123.0656 | -0.35185
4501 | 123.143 | -123.0148 | 0.1236 | 1.4211e-13 | -0.016833 | -0.013505 | -0.04517 | -0.042139 | -0.012565 | -0.0084697 | 0.0092014 | 0.033096 | -0.027035 | 0.01379 | -0.018848 | 0.001048 | 0.019721 | -0.012988 | 0.12538 | 0.10567 | 0.32969 | -0.076794 | 0.023941 | 0.078197 | -0.070087 | 0.015831 | 0.19227 | 0.058115 | -0.23283 | 122.938 | 0.001786 | 123.0159 | 123.0018 | 0.063806 | -0.017922 | 0.20609 | 122.782 | -0.10776 | 123.0388 | 122.9447 | 0.16274 | 0.068676 | -0.065481 | 123.1402 | 123.1205 | 123.3445 | 123.0346 | -0.20039 | 123.0307 | 123.2071 | 123.0729 | 123.093 | -0.35643

## Thermal Data
Fire Time | B Position - Middle | D Position - 3' | D Position - Middle | D Position - 7'
-0.8708 | 13.7945 | 13.8555 | 13.6501 | 13.3753
0.1292 | 13.7801 | 13.853 | 13.6607 | 13.379
1.1292 | 13.833 | 13.869 | 13.6622 | 13.3787
2.1292 | 13.7828 | 13.8669 | 13.6608 | 13.3738
3.1292 | 13.7546 | 13.8647 | 13.6803 | 13.3697
4.1292 | 13.7563 | 13.8657 | 13.6792 | 13.3712
5.1292 | 13.7724 | 13.8627 | 13.6914 | 13.3694
6.1292 | 13.7966 | 13.8927 | 13.7164 | 13.3735
7.1292 | 13.8906 | 13.8632 | 13.9248 | 13.4571
8.1292 | 14.2047 | 14.0485 | 14.6782 | 13.8355
9.1292 | 15.0359 | 14.9506 | 16.0409 | 14.8593
10.1292 | 16.3714 | 16.667 | 19.3255 | 17.7258
11.1292 | 18.1006 | 17.863 | 23.0924 | 20.4005
12.1292 | 20.8924 | 19.8433 | 28.4009 | 24.4665
13.1292 | 23.3311 | 21.0134 | 35.0865 | 29.9164
14.1292 | 26.4924 | 23.1818 | 40.4745 | 34.1206
15.1292 | 29.8732 | 25.7888 | 46.1515 | 38.1307
16.1292 | 33.2908 | 29.0381 | 51.9939 | 43.8155
17.1292 | 35.6068 | 30.5266 | 55.0672 | 46.8591
18.1292 | 37.5578 | 32.1277 | 57.9959 | 48.3883
19.1448 | 39.5921 | 33.4671 | 62.4385 | 51.2609
20.1292 | 41.4415 | 34.6939 | 64.3751 | 53.6767
21.1292 | 43.0797 | 37.0047 | 66.9537 | 56.3411
22.1292 | 44.4431 | 38.6482 | 69.7505 | 57.5981
23.1292 | 46.1314 | 39.9561 | 73.6011 | 60.9881
24.1292 | 47.3893 | 42.3501 | 76.7189 | 63.8434
25.1292 | 49.1759 | 43.8935 | 79.7633 | 66.5986
26.1292 | 50.8247 | 45.1137 | 83.106 | 69.6039
27.1292 | 53.0537 | 47.1881 | 86.542 | 72.9646
28.1292 | 54.961 | 49.0493 | 89.1495 | 75.7717
29.1292 | 56.4574 | 50.3455 | 91.5288 | 77.8041
30.1292 | 57.585 | 51.8382 | 93.7208 | 80.0172
31.1292 | 58.6379 | 53.7533 | 95.1221 | 81.3054
32.1292 | 60.2297 | 55.6936 | 96.9875 | 82.3802
33.1292 | 61.6156 | 57.5003 | 99.705 | 83.9898
34.1292 | 62.954 | 59.3262 | 102.1444 | 85.4682
35.1292 | 63.8523 | 61.5475 | 103.4823 | 87.492
36.1292 | 64.7835 | 63.2037 | 105.2495 | 88.5329
37.1292 | 65.775 | 65.6195 | 106.6556 | 90.2873
38.1292 | 66.4592 | 67.8906 | 108.1867 | 91.686
39.1292 | 67.4337 | 70.1432 | 108.8826 | 93.1486
40.1292 | 68.0382 | 71.2965 | 110.9026 | 94.4373
41.1292 | 68.9545 | 73.4003 | 112.0524 | 97.0642
42.1292 | 69.9164 | 74.5293 | 113.1769 | 98.019
43.1292 | 71.1869 | 79.3794 | 115.8054 | 98.5555
44.1448 | 72.1189 | 81.3678 | 116.8706 | 99.6278
45.1292 | 73.3237 | 83.0368 | 119.7829 | 101.8065
46.1292 | 74.0965 | 85.3966 | 121.6094 | 103.3135
47.1292 | 75.5821 | 87.1247 | 124.3148 | 106.7412
48.1448 | 76.9872 | 90.7235 | 127.9274 | 108.0103
49.1448 | 77.993 | 92.9654 | 130.8353 | 109.7173
50.1448 | 79.2296 | 97.131 | 132.8194 | 110.0606
51.1292 | 80.6962 | 100.5195 | 134.2327 | 110.4011
52.1292 | 82.0365 | 102.451 | 135.4517 | 110.5442
53.1292 | 83.801 | 104.7376 | 136.3556 | 111.3771
54.1292 | 84.659 | 106.4011 | 137.8119 | 113.0703
55.1292 | 85.3419 | 111.4876 | 139.2336 | 113.9978
56.1292 | 86.178 | 115.0705 | 141.907 | 117.3639
57.1292 | 87.5743 | 117.9628 | 143.6742 | 118.4061
58.1292 | 88.3365 | 119.5452 | 145.072 | 119.4222
59.1292 | 88.7796 | 120.5941 | 145.4631 | 120.1231
60.1292 | 89.1557 | 121.401 | 145.3593 | 121.7216
61.1292 | 89.8128 | 122.5174 | 146.5865 | 123.5707
62.1292 | 91.5214 | 122.9088 | 147.4614 | 124.6351
63.1292 | 92.3539 | 125.9878 | 150.8364 | 126.9917
64.1292 | 93.182 | 127.4463 | 151.5929 | 128.0802
65.1292 | 94.2908 | 129.4713 | 153.3059 | 128.7739
66.1292 | 94.8365 | 132.3337 | 154.8178 | 130.5611
67.1292 | 96.1212 | 132.4041 | 155.6808 | 134.1249
68.1292 | 97.3474 | 132.8679 | 156.6246 | 135.8726
69.1292 | 98.5962 | 133.9631 | 158.7264 | 136.8925
70.1292 | 99.6286 | 133.9807 | 160.0051 | 136.6802
71.1292 | 100.6856 | 134.5635 | 160.9996 | 137.6614
72.1292 | 101.5456 | 136.6729 | 162.5201 | 140.6902
73.1292 | 101.861 | 136.6771 | 163.5035 | 142.1184
74.1292 | 103.0578 | 136.6447 | 165.2586 | 143.2883
75.1292 | 103.7934 | 137.6821 | 166.0604 | 147.1035
76.1292 | 105.2822 | 138.9539 | 167.9867 | 151.0719
77.1292 | 106.368 | 138.9083 | 169.6869 | 152.9394
78.1292 | 107.7405 | 138.8087 | 169.8596 | 153.212
79.1292 | 108.406 | 139.1847 | 170.5579 | 155.1969
80.1292 | 109.3903 | 139.3225 | 170.4005 | 156.4763
81.1292 | 110.2467 | 139.7529 | 171.0925 | 156.7751
82.1292 | 110.9988 | 139.8461 | 172.5311 | 157.8255
83.1292 | 111.2907 | 142.701 | 173.8458 | 160.5741
84.1292 | 111.5094 | 141.9201 | 173.5223 | 163.4426
85.1292 | 112.212 | 142.2485 | 174.3379 | 163.7407
86.1292 | 112.6778 | 143.8958 | 173.6944 | 163.1548
87.1292 | 113.5584 | 145.8279 | 174.5415 | 163.4184
88.1292 | 114.4802 | 145.5298 | 175.7794 | 163.6273
89.1292 | 115.0693 | 145.7819 | 175.2479 | 164.4574
90.1292 | 116.1392 | 145.5679 | 175.802 | 166.5513
91.1292 | 116.1047 | 145.5632 | 176.8101 | 167.4002
92.1292 | 116.6315 | 146.8394 | 177.2952 | 170.1505
93.1292 | 116.9591 | 147.4351 | 178.2126 | 172.321
94.1292 | 117.5515 | 147.5804 | 178.5876 | 171.8911
95.1292 | 118.7735 | 147.1129 | 178.9402 | 173.0359
96.1292 | 119.4279 | 147.601 | 179.0723 | 173.9314
97.1292 | 120.3523 | 146.6612 | 179.2088 | 173.7459
98.1292 | 120.6767 | 146.9132 | 179.423 | 175.2755
99.1292 | 121.7584 | 146.3232 | 181.5555 | 175.3851
100.1292 | 122.3117 | 147.4527 | 181.7047 | 175.8848
101.1292 | 123.895 | 148.533 | 182.9443 | 176.581
102.1292 | 124.1472 | 149.1775 | 182.4292 | 177.2235
103.1292 | 124.7034 | 148.5561 | 183.4724 | 177.058
104.1292 | 124.5054 | 148.6416 | 184.3039 | 177.8885
105.1292 | 125.2389 | 148.5832 | 183.9904 | 177.76
106.1292 | 125.1245 | 148.6002 | 183.1807 | 175.8918
107.1292 | 125.3826 | 147.9094 | 183.183 | 174.7547
108.1292 | 125.5057 | 147.5103 | 182.6422 | 173.6859
109.1292 | 125.2789 | 146.9908 | 181.9682 | 171.4019
110.1292 | 125.542 | 146.8585 | 181.2112 | 171.3226
111.1292 | 126.2802 | 147.0228 | 180.5239 | 170.6776
112.1292 | 126.8319 | 147.1424 | 179.9167 | 170.2454
113.1292 | 127.3929 | 148.234 | 180.0828 | 170.1589
114.1292 | 127.3641 | 148.3764 | 179.8399 | 170.6301
115.1448 | 127.3337 | 149.456 | 179.5574 | 172.0881
116.1292 | 128.0319 | 148.7698 | 179.3377 | 172.6844
117.1292 | 128.958 | 149.4248 | 179.3579 | 172.2785
118.1292 | 129.1652 | 150.1844 | 179.9192 | 173.0446
119.1292 | 128.9896 | 150.2034 | 180.4678 | 174.6356
120.1292 | 128.8527 | 150.3834 | 180.2589 | 176.6699
121.1292 | 128.7459 | 150.8594 | 180.1578 | 177.1268
122.1292 | 128.8999 | 152.2395 | 179.9979 | 177.2148
123.1292 | 128.8716 | 152.0787 | 180.0345 | 175.1165
124.1292 | 128.5817 | 154.0389 | 180.3354 | 175.0077
125.1292 | 128.0683 | 154.4739 | 180.6704 | 176.0762
126.1292 | 127.6089 | 154.4806 | 179.8801 | 175.1343
127.1292 | 127.3938 | 153.6312 | 179.2072 | 176.6219
128.1292 | 127.1383 | 153.9867 | 178.6784 | 175.9418
129.1292 | 127.0737 | 155.2192 | 179.651 | 176.3043
130.1292 | 127.0393 | 154.9056 | 179.6992 | 177.6214
131.1292 | 127.1782 | 154.9252 | 179.5731 | 177.3918
132.1292 | 127.7086 | 154.6562 | 181.4692 | 177.9753
133.1292 | 127.8393 | 155.3851 | 181.5262 | 176.9607
134.1292 | 128.1924 | 155.2221 | 182.3469 | 176.5376
135.1292 | 128.4024 | 155.4212 | 182.2809 | 177.4288
136.1292 | 128.5703 | 155.3105 | 182.1023 | 177.0339
137.1292 | 128.3921 | 154.523 | 182.0024 | 178.5463
138.1292 | 128.9038 | 154.4211 | 183.0338 | 180.5618
139.1292 | 128.4445 | 155.3143 | 183.8365 | 181.5895
140.1292 | 128.6475 | 155.9995 | 185.0257 | 181.0797
141.1292 | 128.4232 | 156.4258 | 184.1958 | 180.1112
142.1292 | 128.4077 | 156.4081 | 184.6883 | 179.8561
143.1292 | 129.1877 | 156.7805 | 185.0503 | 179.8727
144.1292 | 129.1843 | 156.5267 | 184.9302 | 180.7782
145.1448 | 129.8991 | 157.1021 | 184.7053 | 181.0679
146.1292 | 130.3599 | 156.605 | 183.9947 | 180.9179
147.1292 | 130.6583 | 155.7004 | 185.1619 | 181.715
148.1292 | 130.9209 | 155.8524 | 184.7488 | 181.5299
149.1292 | 131.285 | 154.5139 | 183.8632 | 180.6077
150.1292 | 131.6555 | 153.8134 | 183.0149 | 180.1641
151.1292 | 131.7339 | 153.6694 | 182.2843 | 180.9745
152.1292 | 132.2375 | 153.9743 | 182.8208 | 182.5684
153.1292 | 132.3824 | 154.0895 | 182.7626 | 184.0875
154.1292 | 132.9893 | 154.4022 | 182.9859 | 184.5902
155.1292 | 133.2288 | 154.6373 | 184.2985 | 185.5948
156.1292 | 133.898 | 153.8531 | 184.7972 | 187.2704
157.1292 | 133.9663 | 152.6581 | 184.655 | 188.6635
158.1292 | 134.816 | 152.5783 | 185.3576 | 188.9162
159.1292 | 134.94 | 153.5236 | 186.3484 | 192.8039
160.1292 | 135.1707 | 153.7807 | 186.3157 | 193.1237
161.1292 | 135.7998 | 155.3951 | 188.0926 | 192.8556
162.1292 | 136.6739 | 155.4375 | 188.8387 | 193.1378
163.1292 | 137.6291 | 157.104 | 189.2038 | 194.7475
164.1292 | 138.0949 | 157.6844 | 189.4668 | 193.0167
165.1292 | 138.7047 | 158.6151 | 189.7832 | 193.6461
166.1292 | 139.4018 | 157.6077 | 190.0367 | 192.2217
167.1292 | 140.009 | 157.7143 | 190.5939 | 191.1698
168.1292 | 140.6256 | 157.614 | 190.3533 | 190.7674
169.1292 | 140.9513 | 158.1493 | 190.9453 | 190.9727
170.1292 | 140.8603 | 159.3077 | 191.32 | 191.7282
171.1292 | 141.2379 | 158.6582 | 192.3115 | 190.94
172.1292 | 141.8764 | 158.5075 | 192.2235 | 190.3355
173.1292 | 142.485 | 158.5317 | 193.7488 | 189.999
174.1292 | 142.6339 | 158.3115 | 195.2616 | 189.899
175.1292 | 142.7455 | 158.9124 | 194.8304 | 189.8674
176.1292 | 143.0743 | 159.2901 | 194.5655 | 189.9792
177.1292 | 143.3668 | 159.1156 | 194.8578 | 192.5238
178.1292 | 143.3093 | 159.9948 | 194.6386 | 194.5524
179.1292 | 143.4453 | 162.0791 | 196.0535 | 195.9085
180.1292 | 143.4277 | 161.3208 | 195.7204 | 195.5458
181.1292 | 143.5775 | 160.2606 | 195.2963 | 195.089
182.1292 | 144.0453 | 160.4767 | 195.0674 | 194.6063
183.1292 | 143.8834 | 160.83 | 194.4097 | 194.0796
184.1292 | 144.1474 | 163.5573 | 196.1612 | 194.9656
185.1292 | 144.5398 | 162.7978 | 197.3852 | 194.9933
186.1292 | 144.9413 | 163.1434 | 198.495 | 195.0289
187.1292 | 144.7613 | 162.9523 | 198.3326 | 195.2606
188.1292 | 144.8457 | 163.8156 | 198.6491 | 196.1339
189.1292 | 144.4958 | 164.0965 | 198.3176 | 198.6832
190.1292 | 144.7675 | 163.2959 | 198.1338 | 199.5214
191.1292 | 145.1295 | 165.033 | 197.7512 | 200.2754
192.1292 | 146.4768 | 164.4746 | 198.1874 | 201.4104
193.1292 | 146.5086 | 166.2379 | 198.9924 | 204.0649
194.1292 | 147.2562 | 168.4732 | 200.4581 | 205.7512
195.1292 | 147.4818 | 167.749 | 201.2182 | 203.9768
196.1292 | 147.653 | 167.9965 | 201.2129 | 203.3951
197.1292 | 147.7218 | 168.4786 | 201.6889 | 203.9221
198.1292 | 147.4397 | 168.6632 | 200.3912 | 203.014
199.1448 | 147.7963 | 169.652 | 200.134 | 203.5049
200.1292 | 147.6912 | 168.4728 | 200.1406 | 204.06
201.1292 | 147.6199 | 168.5144 | 200.4374 | 204.6482
202.1292 | 147.5196 | 170.0084 | 201.7743 | 204.167
203.1292 | 148.0698 | 169.3509 | 202.1729 | 204.9896
204.1292 | 149.129 | 168.5114 | 203.7777 | 206.2
205.1292 | 149.6197 | 168.3509 | 204.7537 | 207.3819
206.1292 | 149.7265 | 170.5418 | 204.7144 | 207.2376
207.1292 | 150.9003 | 171.8175 | 205.0697 | 210.4115
208.1292 | 151.824 | 170.8555 | 204.6068 | 210.73
209.1292 | 152.2727 | 171.0274 | 204.5022 | 209.9582
210.1292 | 152.5 | 170.3225 | 203.8832 | 210.4554
211.1292 | 152.3363 | 171.3457 | 203.7972 | 211.1832
212.1292 | 151.9537 | 171.3243 | 204.0379 | 211.0715
213.1292 | 152.0161 | 172.3937 | 205.7227 | 211.7977
214.1292 | 152.2195 | 172.9899 | 206.222 | 212.5497
215.1292 | 152.4363 | 172.2333 | 206.1301 | 211.5661
216.1292 | 152.9387 | 172.5778 | 206.4231 | 210.7237
217.1292 | 153.1145 | 172.6435 | 205.8354 | 211.3099
218.1292 | 153.5302 | 172.4368 | 205.3715 | 211.1385
219.1292 | 153.8979 | 171.6394 | 205.7425 | 210.767
220.1292 | 154.9647 | 171.1032 | 204.796 | 209.9147
221.1292 | 155.0785 | 170.9594 | 205.7619 | 210.2848
222.1292 | 155.595 | 170.2458 | 204.7902 | 210.4464
223.1292 | 156.3211 | 171.5038 | 206.5114 | 211.0112
224.1292 | 156.9833 | 172.2438 | 206.5583 | 210.9298
225.1292 | 157.1218 | 172.6505 | 206.3612 | 211.4565
226.1292 | 156.6708 | 172.2681 | 206.7688 | 211.5235
227.1292 | 155.6927 | 172.416 | 206.6007 | 210.1152
228.1292 | 154.8338 | 172.9348 | 206.4678 | 208.6359
229.1292 | 153.9547 | 173.4637 | 205.7898 | 206.6038
230.1292 | 153.8017 | 172.9601 | 205.8803 | 205.3487
231.1292 | 154.0224 | 173.7549 | 206.7447 | 206.0712
232.1292 | 154.0211 | 173.488 | 207.3416 | 206.2504
233.1292 | 154.669 | 174.6343 | 208.237 | 206.3308
234.1292 | 154.9921 | 174.0075 | 208.0912 | 207.2616
235.1292 | 155.0354 | 175.1084 | 207.9283 | 207.1491
236.1292 | 155.4491 | 176.7676 | 208.2413 | 207.2434
237.1292 | 155.1916 | 176.4703 | 208.3126 | 206.6701
238.1292 | 154.8356 | 176.5528 | 208.4239 | 206.2659
239.1292 | 154.7408 | 175.425 | 208.0863 | 205.2517
240.1292 | 155.7069 | 174.8594 | 208.0867 | 205.1116
241.1292 | 155.5635 | 174.5022 | 207.5907 | 204.0152
242.1292 | 155.8619 | 173.7396 | 207.9541 | 202.9769
243.1292 | 155.596 | 173.6297 | 207.4959 | 202.6012
244.1292 | 155.3002 | 173.4477 | 208.0313 | 202.9064
245.1292 | 154.8705 | 173.5443 | 208.4289 | 203.3876
246.1292 | 154.2125 | 173.7804 | 208.4539 | 204.4232
247.1292 | 154.4175 | 174.1088 | 209.1197 | 204.5905
248.1292 | 154.912 | 173.6168 | 209.7277 | 206.3787
249.1292 | 155.1845 | 173.183 | 208.9529 | 207.2356
250.1292 | 155.7868 | 172.9713 | 209.49 | 207.9061
251.1292 | 155.8268 | 172.9364 | 210.8355 | 208.8779
252.1292 | 156.559 | 173.5994 | 213.0114 | 209.4363
253.1292 | 156.8286 | 173.5773 | 212.1152 | 208.5511
254.1292 | 157.5327 | 175.0383 | 211.0617 | 208.2804
255.1292 | 157.6207 | 175.0179 | 210.2397 | 207.9756
256.1292 | 157.6521 | 174.4682 | 210.4863 | 208.4939
257.1292 | 158.7474 | 174.549 | 212.5179 | 207.6675
258.1292 | 159.3654 | 175.3127 | 213.426 | 208.4033
259.1292 | 159.2171 | 176.1052 | 214.0767 | 208.8405
260.1292 | 159.712 | 176.9876 | 215.9359 | 208.9882
261.1292 | 160.2501 | 177.4044 | 216.5626 | 209.4258
262.1292 | 160.9132 | 177.7045 | 216.9139 | 208.595
263.1292 | 162.2036 | 177.0879 | 217.8213 | 209.6637
264.1292 | 162.1491 | 178.1353 | 216.6876 | 209.394
265.1448 | 162.2221 | 178.6754 | 216.5643 | 208.2417
266.1292 | 162.9319 | 178.7397 | 216.4144 | 208.4086
267.1292 | 163.8778 | 180.956 | 217.5086 | 208.6321
268.1292 | 164.5996 | 182.3373 | 218.6096 | 209.8379
269.1292 | 165.1798 | 182.6524 | 219.4731 | 209.598
270.1292 | 165.3363 | 182.7776 | 220.0614 | 209.2587
271.1292 | 165.3651 | 183.4807 | 219.1798 | 209.1835
272.1292 | 164.8112 | 183.3053 | 219.0968 | 208.9608
273.1292 | 164.8076 | 186.1503 | 219.8068 | 207.7727
274.1292 | 165.5895 | 186.0426 | 219.4852 | 207.6699
275.1292 | 166.3936 | 184.9761 | 220.0356 | 207.2625
276.1292 | 166.8517 | 183.2635 | 220.663 | 209.0167
277.1292 | 167.0291 | 183.2618 | 221.9972 | 209.3701
278.1292 | 167.0732 | 182.9143 | 221.6769 | 208.8745
279.1292 | 167.5954 | 183.7935 | 223.4888 | 209.7746
280.1292 | 168.1317 | 185.0789 | 223.6054 | 209.5575
281.1292 | 168.3387 | 184.876 | 222.9464 | 208.6339
282.1292 | 168.4313 | 185.5258 | 223.8201 | 209.0301
283.1292 | 168.232 | 185.4674 | 223.4672 | 208.5903
284.1292 | 168.4456 | 185.322 | 223.946 | 209.3698
285.1292 | 168.5464 | 188.7384 | 224.3732 | 213.3807
286.1292 | 169.3137 | 188.1546 | 225.1555 | 213.7863
287.1292 | 169.6311 | 187.4997 | 224.8149 | 213.1734
288.1292 | 169.9582 | 189.3338 | 225.3981 | 215.4423
289.1292 | 170.3376 | 189.5846 | 225.8477 | 215.003
290.1448 | 170.7177 | 189.2458 | 226.9828 | 214.0286
291.1292 | 171.5769 | 189.3855 | 228.6726 | 213.9231
292.1292 | 171.9188 | 189.7024 | 228.2201 | 212.5573
293.1292 | 172.0003 | 189.3113 | 227.9553 | 212.6745
294.1292 | 171.8807 | 189.0248 | 227.2282 | 213.9904
295.1448 | 171.9318 | 189.8777 | 227.0498 | 214.69
296.1292 | 172.0989 | 188.9168 | 229.1628 | 214.4409
297.1292 | 172.4045 | 188.7516 | 228.8966 | 215.4756
298.1292 | 172.5008 | 189.3637 | 229.6973 | 215.5711
299.1292 | 172.7584 | 191.9978 | 230.7057 | 215.6233
300.1292 | 173.3155 | 192.628 | 230.8761 | 216.0203
301.1292 | 173.6532 | 192.2099 | 230.4762 | 217.3516
302.1292 | 173.4327 | 191.5906 | 229.3621 | 217.6515
303.1292 | 173.4766 | 191.5427 | 230.0785 | 218.072
304.1292 | 173.8403 | 190.8249 | 229.9098 | 218.6405
305.1292 | 174.1225 | 190.2836 | 229.8172 | 218.3517
306.1292 | 174.8945 | 190.125 | 228.9884 | 218.9014
307.1292 | 176.0958 | 189.0153 | 228.4745 | 221.4064
308.1292 | 176.4807 | 189.8275 | 229.4597 | 222.3371
309.1292 | 176.8797 | 190.7602 | 230.5995 | 223.9183
310.1292 | 177.0166 | 191.6946 | 231.4382 | 224.6405
311.1292 | 177.3601 | 191.0359 | 231.7624 | 222.8389
312.1292 | 177.4965 | 192.104 | 233.3457 | 222.7463
313.1292 | 177.7375 | 191.8787 | 232.6407 | 223.0725
314.1292 | 177.9656 | 191.4075 | 232.6072 | 223.3347
315.1292 | 178.1509 | 192.7087 | 231.7849 | 224.3662
316.1292 | 178.1287 | 193.0985 | 231.8428 | 224.6197
317.1292 | 177.9517 | 194.7349 | 230.7579 | 224.7303
318.1292 | 178.3886 | 195.9437 | 232.1845 | 225.5412
319.1292 | 178.4359 | 196.0697 | 232.9257 | 224.8726
320.1292 | 178.6606 | 195.4956 | 232.6281 | 223.4711
321.1292 | 178.7859 | 196.0219 | 233.2362 | 223.2988
322.1292 | 179.0813 | 195.2179 | 233.0246 | 223.5634
323.1292 | 179.6607 | 194.5813 | 232.8369 | 223.5917
324.1292 | 180.1116 | 193.6652 | 233.5523 | 224.4805
325.1292 | 180.2012 | 194.0764 | 233.8195 | 225.1065
326.1292 | 180.092 | 195.1134 | 233.7296 | 225.4362
327.1292 | 180.2177 | 194.0358 | 233.8353 | 225.2432
328.1292 | 180.303 | 193.2853 | 234.0877 | 226.1757
329.1292 | 179.957 | 192.7155 | 233.8636 | 225.6173
330.1292 | 179.7468 | 192.9005 | 233.1416 | 225.9754
331.1292 | 179.8227 | 193.3609 | 233.3613 | 227.5832
332.1292 | 180.7457 | 192.56 | 232.832 | 229.1588
333.1292 | 180.6867 | 192.3511 | 232.7139 | 229.0192
334.1292 | 181.1548 | 192.4372 | 233.5615 | 229.6105
335.1292 | 180.7637 | 192.4228 | 234.4571 | 230.4742
336.1292 | 180.0258 | 191.8627 | 234.1876 | 230.527
337.1292 | 180.8153 | 192.0216 | 234.8053 | 230.7544
338.1292 | 181.1537 | 191.3241 | 234.6406 | 230.8573
339.1292 | 180.7359 | 191.1673 | 234.7976 | 230.5074
340.1292 | 181.1421 | 193.3019 | 235.9771 | 231.301
341.1292 | 181.0058 | 194.092 | 236.1741 | 230.5198
342.1292 | 181.009 | 195.6244 | 235.4078 | 230.924
343.1292 | 181.1587 | 194.8659 | 236.6064 | 229.7429
344.1292 | 181.063 | 194.7931 | 235.3544 | 230.0783
345.1292 | 181.0371 | 194.5694 | 235.7084 | 229.702
346.1292 | 181.4328 | 196.915 | 235.3243 | 231.3686
347.1292 | 181.6911 | 197.963 | 235.4936 | 232.5126
348.1292 | 181.9766 | 198.726 | 235.8378 | 231.8375
349.1292 | 182.5867 | 199.1297 | 238.1253 | 233.8444
350.1292 | 183.2258 | 198.8738 | 238.3908 | 236.687
351.1292 | 183.6727 | 198.5367 | 238.9734 | 238.5256
352.1292 | 183.4405 | 198.8751 | 238.0772 | 240.4111
353.1292 | 183.8092 | 199.0223 | 237.688 | 240.2505
354.1292 | 184.0265 | 198.1727 | 237.9011 | 239.5563
355.1292 | 184.2164 | 197.0038 | 237.3517 | 239.4434
356.1292 | 183.9893 | 196.5821 | 239.0965 | 240.3461
357.1292 | 183.9421 | 197.809 | 240.6579 | 239.6599
358.1292 | 184.0945 | 198.9726 | 241.3813 | 239.1059
359.1292 | 185.6214 | 201.1653 | 240.9793 | 239.3894
360.1292 | 185.3477 | 200.9445 | 241.9861 | 239.4043
361.1292 | 185.3007 | 200.9905 | 243.0397 | 239.7267
362.1292 | 185.8357 | 202.1496 | 243.4474 | 240.1705
363.1292 | 185.6935 | 202.9259 | 243.9448 | 240.2934
364.1292 | 185.5815 | 203.4348 | 245.0704 | 240.5251
365.1292 | 186.018 | 202.7625 | 245.7049 | 239.6155
366.1292 | 186.459 | 203.4958 | 246.5111 | 240.6033
367.1292 | 186.7754 | 204.2873 | 245.9603 | 240.1367
368.1292 | 186.5353 | 205.0757 | 247.1308 | 239.7528
369.1292 | 186.9145 | 204.7506 | 247.406 | 241.2356
370.1292 | 187.3618 | 205.04 | 247.9276 | 241.1243
371.1292 | 187.466 | 205.1174 | 247.8097 | 240.0566
372.1292 | 187.7343 | 207.0294 | 248.3586 | 239.253
373.1292 | 187.3217 | 207.4874 | 248.2187 | 238.1759
374.1292 | 187.332 | 206.8253 | 248.6853 | 237.439
375.1292 | 187.4313 | 206.6557 | 249.542 | 238.4479
376.1292 | 186.8773 | 205.5187 | 250.6025 | 237.3288
377.1292 | 187.0512 | 206.1752 | 250.2741 | 237.4511
378.1292 | 187.1771 | 206.5916 | 250.688 | 237.4487
379.1448 | 187.6068 | 206.7761 | 249.9728 | 239.2605
380.1292 | 188.3638 | 208.1491 | 250.5015 | 241.315
381.1292 | 189.1838 | 207.8791 | 251.8151 | 241.727
382.1292 | 189.2857 | 208.2182 | 251.1288 | 240.366
383.1292 | 188.9087 | 207.247 | 251.4019 | 239.4291
384.1292 | 189.1905 | 206.5687 | 251.9105 | 242.3979
385.1292 | 189.3968 | 207.209 | 251.6404 | 242.8107
386.1292 | 190.0922 | 208.0943 | 252.3391 | 242.375
387.1292 | 190.482 | 208.3702 | 252.1452 | 243.0511
388.1292 | 190.8714 | 207.7639 | 252.8333 | 243.4285
389.1292 | 191.0257 | 207.5549 | 251.7197 | 245.1992
390.1292 | 191.5854 | 210.2378 | 252.0077 | 245.9938
391.1292 | 191.6082 | 211.4076 | 252.5278 | 246.2145
392.1292 | 192.1273 | 209.9741 | 253.2028 | 245.8816
393.1292 | 192.6759 | 210.2179 | 252.5433 | 246.7269
394.1292 | 192.7203 | 209.8269 | 253.4901 | 248.5102
395.1292 | 193.6219 | 209.5662 | 253.4911 | 248.1753
396.1292 | 194.2287 | 208.895 | 253.8809 | 246.8137
397.1292 | 195.0033 | 209.2908 | 255.1477 | 247.0214
398.1292 | 195.4699 | 209.2951 | 254.8891 | 246.6567
399.1292 | 195.6758 | 208.9794 | 255.1513 | 246.9994
400.1292 | 196.4578 | 209.8436 | 255.7058 | 245.5996
401.1292 | 197.0923 | 210.0565 | 257.4592 | 244.8966
402.1292 | 197.1308 | 209.8017 | 257.3311 | 244.6849
403.1292 | 196.9163 | 209.7547 | 257.0231 | 245.1544
404.1292 | 197.4549 | 208.3272 | 255.6579 | 244.2769
405.1292 | 197.2288 | 207.4248 | 255.6953 | 245.4325
406.1292 | 197.2001 | 207.5186 | 256.1858 | 245.8481
407.1292 | 197.2847 | 207.4909 | 257.3282 | 245.3924
408.1292 | 197.636 | 208.4466 | 259.2036 | 245.9811
409.1292 | 198.5665 | 210.5027 | 260.2582 | 246.5874
410.1292 | 199.3165 | 211.2509 | 259.8691 | 246.7609
411.1292 | 199.9984 | 210.9306 | 261.0063 | 247.5662
412.1292 | 200.0922 | 211.4328 | 261.9479 | 247.6194
413.1292 | 200.964 | 210.8968 | 262.4445 | 246.7124
414.1292 | 200.5202 | 210.5308 | 261.904 | 246.9583
415.1292 | 200.5362 | 211.5817 | 262.5885 | 246.471
416.1292 | 201.9724 | 212.1076 | 262.4887 | 248.8076
417.1292 | 202.2332 | 211.9535 | 263.0503 | 249.5381
418.1292 | 202.8229 | 213.0515 | 263.7261 | 251.0578
419.1292 | 202.985 | 212.972 | 263.6956 | 250.774
420.1292 | 203.2729 | 213.0631 | 264.9538 | 251.0184
421.1292 | 203.9427 | 212.7122 | 264.1556 | 250.7721
422.1292 | 203.821 | 211.8374 | 263.0736 | 251.2319
423.1292 | 204.2953 | 211.6696 | 264.4185 | 250.8316
424.1292 | 204.2266 | 210.9721 | 263.6614 | 250.6104
425.1292 | 204.4866 | 210.8865 | 264.3626 | 249.5512
426.1292 | 205.7509 | 211.0909 | 264.9459 | 249.3665
427.1292 | 207.0529 | 211.3481 | 265.3369 | 248.5486
428.1292 | 207.9497 | 213.4084 | 265.0854 | 249.2813
429.1292 | 207.4584 | 214.5389 | 265.1411 | 249.2381
430.1292 | 207.6702 | 217.8461 | 266.3566 | 250.6694
431.1292 | 208.1792 | 217.2718 | 267.155 | 251.6374
432.1292 | 209.0191 | 216.5999 | 267.1962 | 253.3867
433.1292 | 210.9293 | 217.0918 | 267.579 | 255.4242
434.1292 | 211.3654 | 216.8448 | 267.2073 | 257.032
435.1292 | 211.3964 | 216.6082 | 267.4134 | 256.1358
436.1292 | 212.223 | 216.2707 | 269.2451 | 257.0221
437.1292 | 212.8677 | 216.3845 | 270.2261 | 256.4767
438.1292 | 213.5695 | 216.1269 | 270.5326 | 257.402
439.1292 | 214.3887 | 216.816 | 271.5519 | 258.7234
440.1292 | 214.7613 | 217.1997 | 271.9532 | 258.5578
441.1292 | 214.7742 | 217.1494 | 273.7077 | 259.7576
442.1292 | 214.7741 | 216.7235 | 273.4062 | 260.1024
443.1292 | 215.5592 | 218.9139 | 272.7917 | 261.9143
444.1292 | 215.907 | 221.3626 | 272.4631 | 261.9072
445.1292 | 216.2839 | 223.6439 | 274.4021 | 261.9304
446.1292 | 216.6367 | 225.5816 | 275.7736 | 261.4802
447.1292 | 217.2687 | 225.6118 | 276.8963 | 263.3421
448.1292 | 217.1546 | 227.7664 | 277.1576 | 262.3134
449.1292 | 217.6257 | 227.6128 | 277.3352 | 262.0153
450.1292 | 218.0909 | 227.9398 | 277.2333 | 262.7808
451.1292 | 218.973 | 226.9943 | 276.5124 | 262.1387
452.1292 | 219.5482 | 226.3922 | 276.6494 | 262.5839
453.1292 | 220.0471 | 226.0285 | 277.5451 | 263.1464
454.1292 | 220.1376 | 225.3167 | 277.0924 | 262.9901
455.1292 | 221.1536 | 224.5919 | 277.3017 | 264.0355
456.1292 | 222.2153 | 223.5812 | 277.6501 | 263.9149
457.1292 | 222.9409 | 223.1248 | 278.8287 | 263.5819
458.1292 | 222.8637 | 222.9434 | 279.0475 | 262.7996
459.1292 | 222.9266 | 223.5581 | 278.4976 | 262.1747
460.1292 | 223.4682 | 223.8641 | 280.3454 | 261.4781
461.1292 | 223.9022 | 224.4234 | 280.4578 | 262.4346
462.1292 | 223.9727 | 224.1372 | 282.0813 | 261.6981
463.1292 | 224.6354 | 224.5326 | 282.2411 | 260.4446
464.1292 | 224.7522 | 224.1458 | 282.3846 | 262.3702
465.1292 | 225.6406 | 223.9765 | 283.4501 | 261.3036
466.1292 | 226.7995 | 222.3797 | 282.5508 | 260.2489
467.1292 | 226.9268 | 221.8233 | 282.9915 | 260.0322
468.1292 | 226.781 | 223.1679 | 283.4894 | 259.6313
469.1292 | 227.3724 | 222.7772 | 283.3845 | 260.5435
470.1292 | 228.3261 | 222.9598 | 284.1852 | 260.6348
471.1292 | 229.2619 | 223.7001 | 284.9402 | 260.8174
472.1292 | 230.1765 | 223.4238 | 286.0052 | 261.0786
473.1292 | 230.7152 | 223.2057 | 287.1777 | 261.4949
474.1292 | 231.4397 | 222.8955 | 287.676 | 261.1999
475.1292 | 231.8302 | 223.769 | 289.0582 | 261.8229
476.1292 | 232.6258 | 223.6923 | 288.7933 | 261.6852
477.1292 | 233.1495 | 224.1217 | 288.6703 | 262.967
478.1292 | 233.1217 | 224.2302 | 289.2494 | 262.3837
479.1292 | 233.4511 | 224.4156 | 290.003 | 263.3323
480.1292 | 234.0233 | 224.696 | 290.6135 | 263.982
481.1292 | 234.5355 | 224.3209 | 291.1262 | 264.534
482.1292 | 234.9186 | 224.6348 | 290.6513 | 265.3786
483.1292 | 235.3552 | 225.288 | 289.9826 | 265.8052
484.1292 | 235.3073 | 226.4581 | 290.263 | 265.572
485.1292 | 234.965 | 227.0973 | 289.5848 | 267.6695
486.1292 | 234.3728 | 228.1366 | 288.8783 | 268.4795
487.1292 | 234.1432 | 228.7604 | 289.3454 | 268.6297
488.1292 | 234.3744 | 230.2728 | 290.2599 | 269.1649
489.1292 | 234.3742 | 231.5391 | 290.4127 | 268.9997
490.1292 | 234.6167 | 231.7999 | 290.8666 | 270.4182
491.1448 | 234.6044 | 231.7347 | 291.0311 | 269.8306
492.1292 | 235.3474 | 233.2402 | 291.9127 | 271.789
493.1292 | 235.7126 | 235.2335 | 292.0282 | 274.8478
494.1292 | 235.9286 | 234.4604 | 291.8649 | 275.1218
495.1292 | 236.627 | 234.1793 | 291.9033 | 274.6263
496.1292 | 236.8551 | 232.9164 | 291.417 | 274.8778
497.1292 | 237.1434 | 233.44 | 293.7766 | 274.8846
498.1292 | 237.7825 | 232.6037 | 293.9641 | 274.6417
499.1292 | 236.9861 | 231.7145 | 294.3214 | 274.7024
500.1292 | 236.9764 | 231.1631 | 294.6527 | 275.696
501.1292 | 236.8598 | 230.8227 | 293.9081 | 276.6921
502.1292 | 236.4881 | 231.771 | 295.32 | 277.5282
503.1292 | 236.5188 | 232.2442 | 295.6199 | 279.4194
504.1292 | 236.0495 | 234.9382 | 296.687 | 280.1468
505.1292 | 236.1044 | 237.1189 | 297.3533 | 281.7278
506.1292 | 236.4348 | 236.9826 | 299.1333 | 283.8878
507.1292 | 237.0509 | 236.4066 | 298.8354 | 284.6334
508.1292 | 237.2614 | 238.2766 | 300.1181 | 284.801
509.1292 | 238.1423 | 238.415 | 300.0175 | 285.3583
510.1292 | 239.4688 | 236.5328 | 298.7708 | 285.2411
511.1292 | 239.5788 | 235.541 | 297.714 | 284.4466
512.1292 | 239.8589 | 234.8021 | 297.9177 | 283.9
513.1292 | 239.9033 | 234.4454 | 298.1277 | 283.9956
514.1292 | 240.3436 | 234.6856 | 298.5648 | 283.3283
515.1292 | 240.656 | 234.966 | 299.8102 | 284.0651
516.1292 | 241.2568 | 235.9006 | 301.5611 | 283.8251
517.1292 | 241.4102 | 235.6292 | 301.7246 | 283.6624
518.1292 | 242.1 | 235.5166 | 301.5 | 283.2148
519.1292 | 242.2893 | 236.0865 | 302.0563 | 282.7021
520.1292 | 242.5543 | 237.2372 | 302.3076 | 282.0396
521.1292 | 243.2555 | 237.4977 | 302.3708 | 281.3021
522.1292 | 243.1495 | 236.4154 | 302.9439 | 281.7102
523.1292 | 244.6327 | 235.535 | 302.7609 | 281.208
524.1292 | 244.8509 | 235.2697 | 304.6896 | 282.0529
525.1448 | 245.1337 | 234.406 | 303.4324 | 282.1947
526.1292 | 244.7779 | 234.0801 | 303.2784 | 282.1993
527.1292 | 245.0951 | 234.6588 | 302.3279 | 282.1339
528.1292 | 244.8553 | 233.7561 | 301.3712 | 282.9095
529.1292 | 244.6899 | 233.3366 | 300.7005 | 281.9423
530.1292 | 244.2772 | 233.7926 | 301.1658 | 282.2904
531.1292 | 244.9772 | 234.3993 | 301.2571 | 280.2994
532.1292 | 244.3147 | 234.5253 | 301.9757 | 278.9071
533.1292 | 244.4079 | 235.4272 | 302.5647 | 278.2567
534.1292 | 244.5238 | 235.876 | 303.5226 | 278.7372
535.1292 | 244.4331 | 236.6932 | 302.3807 | 277.2997
536.1292 | 244.7849 | 238.4505 | 302.8702 | 277.2117
537.1292 | 244.6253 | 238.4125 | 303.634 | 277.0234
538.1292 | 244.3459 | 238.4623 | 302.5459 | 276.4897
539.1292 | 244.8727 | 238.3762 | 302.9358 | 276.4819
540.1292 | 246.0695 | 237.8644 | 303.9377 | 278.5349
541.1292 | 245.9384 | 238.2346 | 304.7031 | 278.6141
542.1292 | 246.6348 | 239.1115 | 306.5293 | 279.833
543.1292 | 247.0745 | 239.1501 | 306.925 | 280.8956
544.1292 | 247.149 | 238.7205 | 307.1643 | 280.2309
545.1292 | 247.1291 | 240.181 | 307.9796 | 282.026
546.1292 | 247.6129 | 240.4408 | 309.7459 | 284.8192
547.1292 | 247.7961 | 242.2767 | 310.8304 | 285.4441
548.1292 | 248.0477 | 243.7035 | 311.5105 | 287.3339
549.1292 | 248.1457 | 246.872 | 311.824 | 289.9809
550.1292 | 248.5736 | 248.3651 | 312.9431 | 289.7244
551.1292 | 249.6663 | 251.2505 | 313.4883 | 291.7044
552.1292 | 249.8834 | 251.3964 | 313.7179 | 291.3354
553.1292 | 250.1573 | 251.5253 | 313.3727 | 291.6239
554.1292 | 251.2476 | 251.5337 | 313.8765 | 293.2005
555.1292 | 251.5596 | 251.6001 | 314.1556 | 294.4356
556.1292 | 251.2891 | 252.4757 | 313.4172 | 294.7717
557.1292 | 251.5282 | 252.6353 | 313.4899 | 295.325
558.1292 | 252.3179 | 254.1894 | 313.1623 | 297.721
559.1292 | 252.6188 | 253.3431 | 313.7855 | 298.4265
560.1292 | 252.7187 | 253.6153 | 314.0897 | 299.9287
561.1292 | 253.2946 | 255.6258 | 315.3615 | 301.8342
562.1292 | 253.537 | 256.8409 | 316.7958 | 300.8861
563.1292 | 254.7671 | 261.1324 | 318.2863 | 299.8277
564.1292 | 255.8195 | 260.7161 | 318.7384 | 299.5934
565.1292 | 256.9625 | 259.9969 | 319.4834 | 299.9908
566.1292 | 257.7373 | 259.2434 | 321.2364 | 300.0583
567.1292 | 258.2686 | 262.203 | 321.67 | 301.0489
568.1292 | 258.4418 | 262.1139 | 322.6863 | 303.7967
569.1292 | 257.8754 | 263.0091 | 321.7378 | 304.6024
570.1292 | 258.7108 | 262.1808 | 321.9785 | 307.195
571.1292 | 258.3689 | 261.6595 | 322.9349 | 307.8197
572.1292 | 258.6186 | 262.375 | 322.3459 | 307.918
573.1292 | 258.7824 | 262.6492 | 322.4241 | 309.116
574.1292 | 258.5034 | 261.8071 | 323.6869 | 308.1942
575.1292 | 258.1345 | 262.8886 | 323.0523 | 309.1749
576.1292 | 257.4093 | 262.0394 | 322.842 | 310.5342
577.1292 | 257.4765 | 262.5614 | 323.0034 | 311.0805
578.1292 | 257.8867 | 263.4788 | 324.1551 | 313.6485
579.1292 | 258.3584 | 265.9862 | 324.8425 | 314.6524
580.1292 | 258.9873 | 267.6216 | 325.7353 | 314.4854
581.1292 | 259.4521 | 266.802 | 326.1323 | 314.0952
582.1292 | 259.9327 | 269.6124 | 325.8642 | 313.4948
583.1292 | 260.3525 | 270.6862 | 325.9741 | 314.2437
584.1292 | 260.9153 | 268.6246 | 326.8261 | 312.7812
585.1292 | 261.3902 | 268.6001 | 326.2342 | 312.7929
586.1292 | 261.3733 | 268.4196 | 325.6476 | 313.8492
587.1292 | 261.7093 | 267.5556 | 325.5976 | 312.6848
588.1292 | 262.8753 | 266.7385 | 327.0521 | 312.5603
589.1292 | 264.1227 | 267.2997 | 327.9784 | 311.3646
590.1292 | 264.3579 | 268.6268 | 329.0144 | 309.7945
591.1292 | 264.7738 | 268.0174 | 329.3938 | 310.2009
592.1292 | 265.4062 | 268.6317 | 330.835 | 309.6435
593.1292 | 265.7785 | 268.7021 | 333.1362 | 311.0889
594.1292 | 265.8063 | 268.9091 | 333.7325 | 312.3676
595.1292 | 266.4828 | 269.4581 | 334.0132 | 314.0829
596.1292 | 266.8683 | 271.3624 | 332.9425 | 314.8302
597.1292 | 267.9254 | 273.3101 | 333.7332 | 317.0379
598.1292 | 269.0162 | 274.228 | 335.0674 | 317.2427
599.1292 | 270.5633 | 274.2765 | 337.0692 | 317.2691
600.1292 | 271.9728 | 273.4478 | 338.7166 | 315.994
601.1292 | 272.4267 | 274.0245 | 338.4181 | 317.422
602.1292 | 273.2667 | 276.1574 | 339.1322 | 317.6726
603.1292 | 273.7178 | 278.309 | 339.7323 | 320.2466
604.1292 | 274.3824 | 276.6294 | 339.7007 | 320.6684
605.1292 | 274.2085 | 277.1191 | 339.0741 | 320.6562
606.1292 | 274.4631 | 278.7159 | 339.9984 | 321.5238
607.1292 | 275.4834 | 279.8031 | 340.246 | 321.1197
608.1292 | 276.5535 | 281.1742 | 340.6961 | 319.6661
609.1292 | 278.5829 | 283.4119 | 341.0331 | 319.4799
610.1292 | 280.6343 | 283.2047 | 340.2879 | 317.2374
611.1292 | 280.3299 | 282.2073 | 340.2595 | 316.9653
612.1292 | 280.8245 | 280.9701 | 339.5227 | 316.2946
613.1292 | 280.8587 | 279.9535 | 338.7757 | 315.3592
614.1292 | 280.505 | 278.5853 | 339.5683 | 314.0074
615.1292 | 280.9649 | 277.6401 | 338.4697 | 313.6508
616.1292 | 281.9879 | 277.1105 | 339.6047 | 312.1177
617.1292 | 282.0516 | 278.9419 | 340.738 | 313.8538
618.1292 | 281.8379 | 278.968 | 342.4484 | 311.6183
619.1292 | 281.2584 | 277.967 | 341.5464 | 311.4766
620.1292 | 281.1979 | 278.3323 | 341.1752 | 314.5896
621.1292 | 281.8717 | 277.7924 | 341.6754 | 315.6434
622.1292 | 281.3358 | 278.5863 | 341.1186 | 316.6055
623.1292 | 281.4445 | 280.2794 | 341.2033 | 317.7642
624.1292 | 281.4614 | 283.072 | 342.1335 | 320.1391
625.1292 | 280.5775 | 282.152 | 341.7966 | 319.3764
626.1292 | 280.4186 | 280.6743 | 341.3505 | 319.015
627.1292 | 280.633 | 280.3416 | 341.2109 | 317.5294
628.1292 | 280.0851 | 283.5503 | 341.5895 | 317.1683
629.1292 | 280.1278 | 285.7475 | 341.0032 | 315.1893
630.1292 | 280.5902 | 284.6352 | 340.9824 | 314.0127
631.1292 | 280.6745 | 284.9698 | 340.9664 | 313.8177
632.1292 | 280.014 | 283.9899 | 342.7074 | 314.1097
633.1292 | 279.8351 | 283.2292 | 342.5705 | 314.1786
634.1292 | 280.2481 | 282.4297 | 343.0228 | 313.871
635.1292 | 280.3822 | 281.4452 | 342.0912 | 312.2867
636.1292 | 281.3355 | 281.5992 | 342.165 | 312.9429
637.1292 | 282.3759 | 281.1911 | 342.819 | 311.7736
638.1292 | 282.8777 | 280.5248 | 342.5791 | 311.0521
639.1292 | 283.2865 | 280.6066 | 343.6961 | 309.3627
640.1292 | 283.6727 | 278.7326 | 342.7142 | 308.0504
641.1292 | 284.9608 | 278.1928 | 343.0782 | 307.2242
642.1292 | 285.0926 | 278.1667 | 342.2504 | 305.6667
643.1292 | 286.9069 | 277.6885 | 341.6966 | 304.3373
644.1292 | 286.9012 | 277.1911 | 341.7439 | 304.6094
645.1292 | 286.2372 | 277.9438 | 341.5706 | 303.6826
646.1292 | 285.5879 | 278.6048 | 341.5584 | 303.2618
647.1292 | 285.6354 | 278.6101 | 341.4668 | 303.2595
648.1292 | 285.8406 | 279.2033 | 342.1875 | 303.1051
649.1292 | 287.4489 | 278.6073 | 343.4508 | 302.9707
650.1292 | 286.583 | 277.5435 | 343.0548 | 301.772
651.1292 | 285.9176 | 277.168 | 343.0003 | 300.8797
652.1292 | 286.8647 | 276.3576 | 342.6177 | 299.8645
653.1292 | 285.8486 | 277.0458 | 342.4795 | 299.6929
654.1292 | 286.2687 | 275.8445 | 342.7824 | 300.2374
655.1292 | 286.6854 | 275.9669 | 342.5444 | 299.6038
656.1292 | 286.3854 | 276.7413 | 341.6192 | 297.9512
657.1292 | 285.9546 | 275.3449 | 342.1777 | 299.1453
658.1292 | 285.5668 | 275.1724 | 342.1025 | 298.8837
659.1292 | 285.0583 | 274.8415 | 340.8639 | 297.4863
660.1292 | 285.5566 | 274.7491 | 341.4825 | 297.9556
661.1292 | 286.3267 | 275.634 | 341.0877 | 297.1002
662.1292 | 286.5701 | 274.3831 | 341.533 | 295.7097
663.1292 | 287.2315 | 274.4196 | 341.4392 | 294.5877
664.1292 | 287.3301 | 273.635 | 340.2203 | 293.6116
665.1292 | 286.7026 | 273.9925 | 340.0279 | 293.5796
666.1292 | 285.9659 | 277.1981 | 340.3508 | 296.6204
667.1292 | 285.6981 | 276.2068 | 339.8484 | 300.0125
668.1292 | 285.0731 | 275.8313 | 339.787 | 299.7877
669.1292 | 283.9594 | 276.4464 | 338.853 | 300.1113
670.1292 | 284.7893 | 277.3141 | 338.0199 | 301.3886
671.1292 | 283.7926 | 277.3093 | 337.26 | 302.7101
672.1292 | 283.4485 | 279.5723 | 337.0486 | 303.8921
673.1292 | 283.5702 | 279.4925 | 336.9799 | 302.7117
674.1292 | 283.5328 | 280.4514 | 335.5323 | 301.7514
675.1292 | 283.5421 | 279.8727 | 334.8644 | 301.7485
676.1292 | 283.752 | 278.7586 | 334.6959 | 299.8757
677.1292 | 283.9107 | 278.69 | 335.4322 | 300.296
678.1292 | 283.844 | 277.5684 | 335.7748 | 301.4645
679.1292 | 283.8833 | 277.7592 | 335.9628 | 302.1727
680.1292 | 284.588 | 280.2778 | 335.321 | 302.8121
681.1292 | 284.8436 | 281.092 | 335.7419 | 302.2134
682.1292 | 285.3568 | 281.9449 | 336.9323 | 301.959
683.1292 | 285.059 | 281.4768 | 336.6642 | 303.8378
684.1292 | 284.1333 | 281.3376 | 336.4166 | 304.6077
685.1292 | 283.6985 | 279.5166 | 335.9614 | 303.972
686.1292 | 283.7094 | 279.3145 | 336.3649 | 304.037
687.1292 | 283.347 | 278.9787 | 337.1996 | 302.5414
688.1292 | 282.7334 | 278.3927 | 338.0496 | 301.1484
689.1292 | 283.0906 | 278.5509 | 337.2132 | 300.3676
690.1292 | 282.8433 | 279.4636 | 338.1185 | 301.556
691.1292 | 282.6305 | 280.4327 | 338.7684 | 302.8148
692.1292 | 282.7282 | 281.8123 | 338.8446 | 303.2795
693.1292 | 282.0407 | 282.692 | 339.1391 | 304.6842
694.1292 | 281.7831 | 282.5602 | 338.7148 | 304.7177
695.1292 | 281.5413 | 282.6073 | 337.9714 | 305.2194
696.1292 | 281.9867 | 281.2323 | 335.8667 | 304.8022
697.1292 | 283.0616 | 280.426 | 336.0221 | 303.0364
698.1292 | 282.4138 | 282.8455 | 335.7204 | 301.8417
699.1292 | 282.3978 | 281.1996 | 336.1657 | 301.858
700.1292 | 283.1218 | 280.3551 | 336.959 | 301.2181
701.1292 | 284.967 | 279.4484 | 339.6369 | 302.0508
702.1292 | 285.6025 | 278.6564 | 339.2523 | 300.313
703.1292 | 287.0935 | 278.2601 | 339.4123 | 299.2785
704.1292 | 288.9679 | 278.0143 | 338.8541 | 297.998
705.1292 | 292.1887 | 278.719 | 338.7046 | 297.1029
706.1292 | 294.2375 | 280.0387 | 338.7631 | 295.6095
707.1292 | 294.4886 | 282.0782 | 340.915 | 296.1523
708.1292 | 296.1649 | 280.9959 | 341.2606 | 296.3197
709.1292 | 297.3631 | 281.6032 | 341.0987 | 296.8909
710.1292 | 298.1179 | 282.1223 | 341.1151 | 296.3019
711.1292 | 300.1492 | 282.5412 | 342.1553 | 296.4712
712.1292 | 301.6685 | 282.9425 | 341.6742 | 295.8609
713.1292 | 303.2286 | 283.5191 | 341.5522 | 294.9948
714.1292 | 303.3555 | 282.7953 | 341.0422 | 294.3945
715.1292 | 304.092 | 282.8738 | 341.886 | 292.3001
716.1292 | 303.4442 | 282.8011 | 340.7947 | 290.4399
717.1292 | 305.304 | 281.5064 | 339.4764 | 290.0844
718.1292 | 306.8812 | 281.1824 | 338.165 | 289.4608
719.1292 | 306.5687 | 280.1265 | 336.4479 | 289.3543
720.1292 | 308.9514 | 280.3583 | 336.4967 | 287.9004
721.1448 | 314.3262 | 279.2822 | 335.8095 | 287.1768
722.1292 | 319.7356 | 279.9624 | 336.5264 | 285.9007
723.1448 | 326.0269 | 280.0437 | 336.494 | 284.8968
724.1448 | 329.6567 | 280.0491 | 336.3658 | 285.2374
725.1448 | 332.0326 | 279.9274 | 336.1569 | 284.8041
726.1292 | 334.0207 | 280.158 | 336.8846 | 285.781
727.1292 | 334.8745 | 279.5135 | 337.365 | 285.1652
728.1292 | 335.2686 | 280.4492 | 336.9838 | 284.5071
729.1292 | 333.6979 | 280.8896 | 336.8629 | 285.1544
730.1292 | 332.7612 | 280.3594 | 336.1488 | 285.5236
731.1292 | 334.0358 | 282.2942 | 337.7369 | 287.2537
732.1292 | 334.6182 | 283.8762 | 339.1833 | 287.7437
733.1292 | 333.8324 | 286.1654 | 340.2434 | 291.538
734.1292 | 334.9111 | 285.5538 | 340.5535 | 292.5815
735.1292 | 336.653 | 286.704 | 340.9761 | 291.8455
736.1292 | 337.1514 | 287.8982 | 341.7895 | 294.203
737.1292 | 337.5894 | 289.2621 | 343.1458 | 293.5816
738.1292 | 338.7197 | 289.0563 | 343.5255 | 292.2218
739.1292 | 339.5444 | 290.17 | 344.2104 | 293.9283
740.1292 | 340.0914 | 289.7933 | 345.9722 | 295.0029
741.1292 | 339.1544 | 289.28 | 346.9782 | 295.3927
742.1292 | 340.0658 | 289.9451 | 347.7623 | 296.9723
743.1292 | 340.5261 | 292.8896 | 347.2846 | 298.1194
744.1292 | 340.1709 | 293.7683 | 347.2085 | 297.0821
745.1292 | 339.7 | 293.5838 | 346.1768 | 296.4821
746.1292 | 336.9822 | 292.4256 | 346.7691 | 295.9169
747.1292 | 336.3945 | 291.9593 | 345.5981 | 295.0077
748.1292 | 336.6569 | 291.8916 | 344.875 | 294.3162
749.1292 | 338.813 | 292.5336 | 345.494 | 293.9881
750.1292 | 338.1895 | 291.8994 | 345.4548 | 293.9665
751.1292 | 338.9404 | 291.4014 | 345.4828 | 293.7823
752.1292 | 339.3181 | 290.965 | 344.6779 | 294.3844
753.1292 | 340.5141 | 290.9629 | 344.7775 | 294.001
754.1292 | 340.9528 | 291.4498 | 345.0363 | 294.1443
755.1292 | 340.8753 | 291.2968 | 345.3296 | 295.0451
756.1292 | 338.6492 | 290.7914 | 347.2524 | 294.5396
757.1292 | 336.3715 | 290.4153 | 347.5014 | 294.528
758.1292 | 335.3946 | 291.0228 | 346.5003 | 296.2526
759.1292 | 335.4388 | 292.1183 | 348.4755 | 299.2705
760.1292 | 337.5483 | 294.5011 | 349.295 | 300.8462
761.1292 | 340.5873 | 295.4811 | 350.3543 | 300.2143
762.1292 | 340.481 | 295.5591 | 350.3239 | 300.7268
763.1292 | 339.216 | 296.2137 | 349.0756 | 301.9601
764.1292 | 337.6647 | 295.933 | 348.09 | 301.6096
765.1292 | 337.5477 | 296.7143 | 348.2569 | 303.5689
766.1292 | 337.2636 | 297.4822 | 347.4308 | 304.9661
767.1292 | 339.2511 | 297.3564 | 347.8094 | 305.8333
768.1292 | 339.9186 | 298.1469 | 349.4164 | 305.5454
769.1292 | 341.1506 | 297.7716 | 349.87 | 305.0528
770.1292 | 342.3067 | 297.1721 | 348.9714 | 304.085
771.1292 | 342.8453 | 298.4223 | 350.2407 | 304.8487
772.1292 | 345.4006 | 300.1858 | 350.4823 | 306.536
773.1292 | 345.3091 | 300.2857 | 350.8281 | 309.0796
774.1292 | 344.4316 | 299.7559 | 349.9931 | 308.9629
775.1292 | 342.9785 | 299.5266 | 350.5441 | 309.643
776.1292 | 344.756 | 298.4757 | 349.4084 | 308.021
777.1292 | 344.8605 | 298.0364 | 349.0014 | 306.4985
778.1292 | 343.27 | 298.9026 | 350.315 | 306.0142
779.1292 | 343.9005 | 297.8721 | 350.9316 | 305.7274
780.1292 | 343.4436 | 297.9046 | 350.6862 | 305.7205
781.1292 | 343.2875 | 297.6833 | 351.6335 | 304.9261
782.1292 | 342.3123 | 298.3207 | 351.5601 | 306.4854
783.1292 | 345.3667 | 297.6509 | 351.0396 | 307.5762
784.1292 | 343.3267 | 297.4792 | 350.4788 | 307.112
785.1292 | 342.108 | 296.9125 | 349.533 | 306.6708
786.1292 | 341.7244 | 298.5184 | 349.173 | 306.1864
787.1292 | 342.5273 | 298.2281 | 348.2284 | 305.8377
788.1292 | 344.1648 | 298.3563 | 347.7672 | 305.0013
789.1292 | 343.9375 | 297.6373 | 347.185 | 304.2208
790.1292 | 346.9796 | 298.2781 | 347.533 | 305.7217
791.1292 | 347.3563 | 299.0219 | 347.7293 | 306.1186
792.1292 | 349.2892 | 298.5676 | 346.8613 | 306.5278
793.1292 | 350.1446 | 298.9485 | 347.2711 | 307.287
794.1292 | 351.2377 | 301.0441 | 347.0463 | 306.2296
795.1292 | 351.389 | 299.9451 | 346.9796 | 305.806
796.1292 | 348.4574 | 300.4845 | 346.4239 | 307.1312
797.1292 | 346.3943 | 300.312 | 347.1314 | 306.097
798.1292 | 344.5825 | 299.7819 | 347.4163 | 307.0677
799.1292 | 343.8186 | 297.7421 | 347.2098 | 305.1839
800.1292 | 346.8518 | 297.1991 | 346.8083 | 304.3051
801.1292 | 347.2621 | 295.8651 | 346.3291 | 302.841
802.1292 | 344.9333 | 295.4476 | 346.0815 | 301.9858
803.1292 | 343.6154 | 295.9716 | 345.3532 | 302.3778
804.1292 | 343.2756 | 295.6944 | 346.0643 | 301.5027
805.1292 | 344.669 | 294.7009 | 346.1601 | 300.8022
806.1292 | 341.7134 | 294.699 | 346.6174 | 299.5034
807.1292 | 343.2532 | 293.5861 | 347.055 | 299.6974
808.1292 | 341.4732 | 293.6314 | 348.2084 | 299.9701
809.1292 | 341.1473 | 292.4728 | 348.6663 | 300.3056
810.1292 | 340.6791 | 292.6861 | 348.7432 | 299.2456
811.1292 | 341.5142 | 294.6197 | 348.5784 | 297.8195
812.1292 | 341.6676 | 293.126 | 347.9696 | 296.8152
813.1292 | 342.7451 | 292.2413 | 347.2343 | 296.2538
814.1292 | 342.417 | 292.5631 | 346.7506 | 295.2552
815.1292 | 341.8671 | 292.8842 | 346.0826 | 296.3778
816.1292 | 341.5731 | 292.0518 | 346.5219 | 296.516
817.1292 | 341.8423 | 291.3678 | 346.1594 | 297.1844
818.1292 | 341.2576 | 291.0877 | 345.5581 | 296.5966
819.1292 | 339.7475 | 290.3891 | 345.5242 | 297.6835
820.1292 | 341.8448 | 290.3168 | 345.4635 | 299.6135
821.1292 | 339.372 | 290.1438 | 344.9589 | 301.4318
822.1292 | 340.8508 | 290.4532 | 344.6181 | 304.175
823.1292 | 342.3682 | 289.9401 | 344.65 | 303.574
824.1292 | 343.2951 | 290.3974 | 344.541 | 304.0584
825.1292 | 342.1562 | 290.4742 | 344.2709 | 303.3127
826.1292 | 340.4424 | 290.6743 | 342.8296 | 304.5864
827.1292 | 344.1644 | 291.037 | 343.1291 | 305.7984
828.1292 | 344.8947 | 294.8645 | 344.1659 | 309.9977
829.1292 | 343.1346 | 293.9943 | 343.8433 | 309.8642
830.1292 | 342.4116 | 294.1796 | 344.3697 | 310.8177
831.1292 | 343.7067 | 293.3668 | 344.4642 | 312.2425
832.1292 | 341.1139 | 291.9417 | 343.2123 | 312.5385
833.1292 | 340.258 | 291.1079 | 342.997 | 313.569
834.1292 | 342.6535 | 292.6521 | 342.5958 | 313.822
835.1292 | 341.7804 | 292.5914 | 343.5765 | 315.5372
836.1292 | 343.4157 | 291.529 | 343.7542 | 315.8638
837.1292 | 344.6887 | 291.5684 | 344.2772 | 313.9992
838.1292 | 346.6883 | 291.0187 | 343.6887 | 313.7192
839.1292 | 343.8117 | 290.0528 | 344.2205 | 315.7489
840.1292 | 344.9034 | 289.6414 | 345.1435 | 314.7231
841.1292 | 347.2523 | 289.7689 | 345.6426 | 312.6888
842.1292 | 347.8915 | 290.2154 | 345.6778 | 311.9403
843.1292 | 347.93 | 290.5215 | 345.8853 | 310.5061
844.1292 | 350.591 | 290.207 | 346.0355 | 309.4202
845.1292 | 352.4716 | 291.1 | 345.903 | 307.8224
846.1292 | 353.6884 | 291.0243 | 346.182 | 307.2539
847.1292 | 354.3183 | 292.9982 | 346.7371 | 306.9549
848.1292 | 355.3808 | 294.4608 | 347.1882 | 309.2028
849.1292 | 355.7814 | 296.4735 | 347.8387 | 310.7007
850.1292 | 356.6887 | 296.2656 | 346.7931 | 311.6714
851.1292 | 356.3211 | 295.6339 | 348.2478 | 311.0159
852.1292 | 358.2349 | 295.5655 | 349.1157 | 311.1599
853.1292 | 357.6603 | 296.4318 | 349.6692 | 312.4025
854.1292 | 359.1608 | 295.6013 | 349.898 | 312.4878
855.1292 | 361.9523 | 295.4047 | 349.5884 | 311.3838
856.1292 | 364.0635 | 296.0133 | 350.5441 | 311.0837
857.1292 | 363.8093 | 296.6648 | 351.8887 | 310.2458
858.1292 | 363.1133 | 295.8228 | 352.4412 | 310.2795
859.1292 | 364.6475 | 295.4022 | 351.4066 | 309.4725
860.1292 | 367.6598 | 294.9335 | 350.8422 | 308.3236
861.1292 | 367.2203 | 295.7538 | 351.2833 | 309.027
862.1292 | 368.9512 | 294.9862 | 351.9464 | 309.3112
863.1292 | 370.621 | 294.2202 | 352.0244 | 309.0921
864.1292 | 368.7572 | 294.0731 | 352.8274 | 310.5412
865.1292 | 370.2406 | 292.8169 | 352.5853 | 309.8607
866.1292 | 369.4526 | 293.0652 | 351.8822 | 311.1939
867.1292 | 368.8644 | 293.5108 | 351.2743 | 312.0061
868.1292 | 369.4135 | 293.0863 | 351.2322 | 310.9712
869.1292 | 371.5056 | 294.4962 | 351.3296 | 310.4729
870.1292 | 371.7662 | 296.9308 | 352.8016 | 309.935
871.1292 | 372.7174 | 296.9326 | 353.3227 | 309.7051
872.1292 | 374.718 | 297.9957 | 354.0463 | 310.283
873.1292 | 375.9244 | 298.1946 | 355.6905 | 309.9766
874.1292 | 376.8923 | 296.7397 | 354.8152 | 309.1437
875.1292 | 378.1082 | 296.7891 | 355.5957 | 309.8019
876.1292 | 378.5874 | 296.9899 | 355.8325 | 309.9021
877.1292 | 378.6588 | 298.0205 | 355.8978 | 310.385
878.1292 | 379.6283 | 296.9012 | 356.6577 | 310.011
879.1292 | 379.4895 | 297.3877 | 356.4461 | 310.1111
880.1292 | 380.2877 | 296.9543 | 357.4654 | 310.5412
881.1292 | 379.9596 | 296.2873 | 357.0106 | 311.5996
882.1292 | 377.0997 | 296.7253 | 357.102 | 312.6967
883.1292 | 376.2673 | 295.8681 | 356.6174 | 313.01
884.1292 | 376.5152 | 290.8234 | 356.8283 | 310.5547
885.1292 | 376.9535 | 289.0615 | 358.1424 | 309.5199
886.1292 | 377.9046 | 290.8304 | 358.9641 | 309.948
887.1292 | 378.8321 | 290.9561 | 357.9311 | 310.1018
888.1292 | 379.7764 | 290.3995 | 358.9792 | 310.0253
889.1292 | 380.2211 | 292.8382 | 359.6692 | 311.0485
890.1292 | 378.2872 | 294.2908 | 360.0725 | 312.8928
891.1292 | 377.4666 | 292.9805 | 360.4828 | 312.587
892.1292 | 375.5411 | 294.7303 | 360.9521 | 314.302
893.1292 | 374.6247 | 298.0793 | 360.8419 | 316.0287
894.1292 | 374.4356 | 295.1472 | 361.2396 | 317.368
895.1292 | 373.3805 | 295.0229 | 360.4188 | 317.8688
896.1292 | 373.8565 | 298.0922 | 360.5983 | 317.9992
897.1292 | 377.2124 | 299.6818 | 362.185 | 301.7119
898.1292 | 376.7218 | 298.8871 | 362.806 | 317.2338
899.1292 | 376.1083 | 299.1845 | 363.746 | 317.6196
900.1292 | 376.5773 | 299.3696 | 361.9245 | 316.8044
901.1292 | 376.643 | 303.5953 | 361.1277 | 316.8893
902.1292 | 377.2151 | 308.9358 | 361.0298 | 319.3003
903.1448 | 377.8927 | 310.1933 | 360.9389 | 318.8254
904.1292 | 378.039 | 309.8501 | 360.8374 | 317.7535
905.1292 | 378.6636 | 310.0299 | 361.9106 | 321.5689
906.1292 | 379.6409 | 309.6718 | 362.3958 | 321.3667
907.1448 | 379.3241 | 312.3135 | 364.0431 | 324.6911
908.1448 | 378.6098 | 311.9501 | 364.8011 | 324.6061
909.1292 | 378.7161 | 311.0623 | 365.8764 | 322.9194
910.1292 | 380.6097 | 312.06 | 366.6568 | 321.5303
911.1292 | 380.6798 | 312.4273 | 366.2148 | 320.4029
912.1448 | 380.1226 | 314.1784 | 365.8715 | 322.2462
913.1292 | 380.9395 | 313.9244 | 365.2892 | 321.7298
914.1292 | 382.1689 | 313.5194 | 364.0499 | 320.1659
915.1292 | 382.9499 | 312.2856 | 362.6281 | 318.5833
916.1292 | 382.7942 | 312.3098 | 361.3714 | 317.7187
917.1292 | 383.4526 | 311.9386 | 361.4447 | 316.6564
918.1292 | 384.8675 | 311.68 | 362.6165 | 315.2859
919.1292 | 386.2497 | 311.4519 | 363.6585 | 315.4126
920.1292 | 387.4008 | 311.613 | 365.2777 | 315.7918
921.1292 | 387.297 | 312.3769 | 365.0441 | 316.7538
922.1292 | 388.5359 | 314.6937 | 366.39 | 319.4641
923.1292 | 389.0176 | 314.2598 | 366.7224 | 319.0915
924.1292 | 389.1736 | 314.0911 | 367.8742 | 318.3953
925.1292 | 388.2084 | 312.8909 | 366.9339 | 317.4545
926.1292 | 387.7642 | 312.2856 | 368.4495 | 319.1233
927.1292 | 387.6397 | 311.9384 | 369.4829 | 319.0106
928.1292 | 387.7506 | 311.6242 | 368.6675 | 319.7405
929.1292 | 388.7276 | 311.8764 | 369.5959 | 321.0321
930.1292 | 390.1265 | 313.5234 | 368.7463 | 321.7478
931.1292 | 390.0792 | 313.3867 | 370.0827 | 321.2026
932.1292 | 389.1894 | 313.7337 | 369.4377 | 321.3758
933.1292 | 388.4217 | 313.9979 | 368.1794 | 321.173
934.1292 | 388.0986 | 314.0809 | 368.591 | 322.9615
935.1292 | 388.9511 | 313.7848 | 367.0614 | 321.7582
936.1292 | 389.5574 | 314.3536 | 366.087 | 320.7139
937.1292 | 390.6353 | 314.5508 | 364.3444 | 318.6905
938.1292 | 390.8871 | 315.1265 | 362.4877 | 317.001
939.1292 | 390.1243 | 313.9205 | 361.3237 | 315.1663
940.1292 | 389.3209 | 312.7821 | 361.197 | 313.9486
941.1292 | 388.5963 | 312.8142 | 360.9913 | 312.5699
942.1292 | 387.918 | 312.3759 | 361.1441 | 311.2156
943.1292 | 388.7221 | 313.1137 | 361.7818 | 309.9221
944.1292 | 388.8696 | 312.9067 | 360.688 | 308.8611
945.1292 | 389.3291 | 313.8033 | 361.1777 | 308.2851
946.1292 | 388.7049 | 312.5526 | 360.0524 | 308.1056
947.1292 | 386.2501 | 311.5358 | 359.3014 | 308.1417
948.1292 | 385.8798 | 309.7545 | 357.9581 | 307.5417
949.1292 | 385.1964 | 307.877 | 356.3053 | 307.5006
950.1292 | 384.3655 | 306.6807 | 355.8559 | 306.8868
951.1292 | 382.2278 | 306.6637 | 355.1537 | 307.4744
952.1292 | 382.3547 | 305.765 | 354.7157 | 308.0813
953.1292 | 381.9785 | 305.4532 | 355.3887 | 307.3108
954.1292 | 382.187 | 305.4666 | 357.0904 | 308.8004
955.1292 | 382.6856 | 305.954 | 357.4832 | 309.1417
956.1292 | 383.2973 | 307.2051 | 359.2657 | 309.3187
957.1292 | 383.7669 | 308.9523 | 359.4621 | 309.3022
958.1292 | 384.6152 | 310.0285 | 360.0151 | 310.229
959.1292 | 385.3285 | 311.4752 | 360.8543 | 311.2002
960.1292 | 385.8143 | 311.1205 | 361.2953 | 310.78
961.1292 | 386.2246 | 311.0893 | 362.6009 | 311.4365
962.1292 | 386.3208 | 311.7216 | 364.2013 | 310.926
963.1292 | 386.6843 | 311.9828 | 363.359 | 310.4013
964.1292 | 386.5952 | 312.5092 | 362.8763 | 309.7051
965.1292 | 386.9553 | 312.7104 | 363.6994 | 309.452
966.1292 | 387.1749 | 312.4924 | 363.9573 | 311.2771
967.1292 | 387.1288 | 312.5555 | 365.6915 | 310.8625
968.1292 | 387.6407 | 313.8793 | 367.3281 | 310.8163
969.1292 | 388.6952 | 315.0856 | 368.5881 | 311.1023
970.1292 | 388.8905 | 314.9909 | 370.0532 | 311.0676
971.1292 | 388.9644 | 314.6649 | 369.5439 | 310.6139
972.1292 | 389.5491 | 315.0131 | 371.4297 | 310.3369
973.1292 | 390.4779 | 316.1378 | 373.3244 | 310.5845
974.1292 | 390.8167 | 315.7207 | 373.0501 | 310.9318
975.1292 | 390.7061 | 315.9473 | 372.5151 | 309.8101
976.1292 | 390.9052 | 315.7033 | 372.3032 | 309.9528
977.1292 | 391.4062 | 316.508 | 373.235 | 310.0772
978.1292 | 392.8738 | 317.1829 | 375.1833 | 310.3121
979.1292 | 392.7384 | 317.388 | 374.3892 | 312.3001
980.1292 | 392.3875 | 316.0822 | 371.829 | 311.8059
981.1292 | 392.6903 | 314.6976 | 370.9827 | 310.8548
982.1292 | 392.7135 | 314.7257 | 371.9494 | 309.6323
983.1292 | 394.2577 | 314.6068 | 371.7575 | 308.8561
984.1292 | 393.7949 | 313.8104 | 371.7353 | 308.4099
985.1292 | 394.1431 | 314.6589 | 372.1531 | 309.1982
986.1292 | 394.4103 | 315.283 | 372.8725 | 310.9377
987.1292 | 394.911 | 315.6992 | 373.4512 | 311.7231
988.1292 | 395.5292 | 316.5612 | 374.3594 | 312.4226
989.1292 | 395.5743 | 316.7577 | 376.8724 | 314.9358
990.1292 | 395.6076 | 316.1312 | 376.8498 | 315.6718
991.1292 | 395.7464 | 316.7602 | 378.0298 | 316.8711
992.1292 | 396.0812 | 318.6286 | 378.281 | 318.8982
993.1292 | 395.6672 | 318.0174 | 377.2447 | 318.0842
994.1292 | 395.9375 | 317.8016 | 377.8211 | 318.6147
995.1292 | 396.8844 | 320.6172 | 378.159 | 318.8004
996.1292 | 397.361 | 322.6175 | 377.6882 | 318.2995
997.1292 | 398.5004 | 323.6621 | 379.4635 | 319.0796
998.1292 | 398.2279 | 323.664 | 379.6846 | 318.489
999.1292 | 398.1877 | 324.8186 | 380.1272 | 317.9771
1000.1292 | 398.6979 | 325.4785 | 379.884 | 317.9224
1001.1292 | 399.123 | 325.7957 | 380.4569 | 317.9827
1002.1292 | 400.2967 | 326.5108 | 379.7817 | 316.8554
1003.1292 | 401.1839 | 328.1466 | 379.2555 | 315.4623
1004.1292 | 402.8585 | 330.1026 | 379.6908 | 314.547
1005.1292 | 403.7738 | 331.3193 | 380.851 | 314.2878
1006.1292 | 404.3481 | 332.092 | 382.2572 | 316.811
1007.1292 | 404.7616 | 332.0257 | 385.0423 | 319.6743
1008.1292 | 406.1117 | 333.0639 | 386.6264 | 320.2369
1009.1292 | 405.7452 | 334.5311 | 387.0827 | 321.3412
1010.1292 | 406.3266 | 335.4312 | 387.1252 | 321.5827
1011.1292 | 406.5797 | 336.2078 | 388.8833 | 322.3246
1012.1292 | 407.8284 | 337.1437 | 389.3453 | 322.1674
1013.1292 | 408.8512 | 337.6328 | 391.549 | 322.8299
1014.1292 | 408.8521 | 338.803 | 392.3232 | 324.3409
1015.1292 | 409.4012 | 338.5461 | 393.1874 | 325.1142
1016.1292 | 409.6625 | 340.2776 | 395.4708 | 328.7372
1017.1292 | 410.7876 | 340.4647 | 398.3747 | 330.7174
1018.1292 | 411.1606 | 341.0147 | 399.1102 | 332.1784
1019.1292 | 412.426 | 341.4312 | 400.8598 | 332.8544
1020.1292 | 412.9583 | 341.3922 | 402.03 | 335.75
1021.1292 | 412.5264 | 341.1921 | 400.4389 | 338.1441
1022.1292 | 411.2295 | 338.8387 | 398.9268 | 340.7593
1023.1292 | 410.0121 | 337.0338 | 398.1054 | 343.0142
1024.1292 | 410.7246 | 336.266 | 397.8859 | 344.6928
1025.1292 | 411.0947 | 335.8608 | 399.1332 | 344.1735
1026.1292 | 410.438 | 335.1465 | 398.5474 | 343.172
1027.1292 | 410.2025 | 335.4228 | 397.6375 | 344.0162
1028.1292 | 410.2803 | 334.7611 | 397.0826 | 344.6288
1029.1292 | 410.383 | 333.5382 | 396.2139 | 344.7351
1030.1292 | 411.1523 | 333.7146 | 396.6642 | 343.2773
1031.1292 | 412.6997 | 334.8272 | 397.3119 | 342.5115
1032.1292 | 413.8715 | 336.7389 | 398.5877 | 341.8429
1033.1292 | 414.7059 | 336.9922 | 398.6516 | 342.7614
1034.1292 | 414.2984 | 336.5958 | 398.1709 | 343.3422
1035.1292 | 414.6125 | 335.9244 | 397.7766 | 343.2649
1036.1292 | 415.6456 | 335.9395 | 399.365 | 342.9929
1037.1292 | 417.1494 | 338.1214 | 399.8085 | 341.9853
1038.1292 | 419.2832 | 340.0393 | 399.4803 | 341.1847
1039.1292 | 420.7787 | 341.4583 | 401.0949 | 340.6789
1040.1292 | 422.0848 | 341.3842 | 400.6001 | 341.349
1041.1292 | 422.877 | 341.6325 | 401.6389 | 341.9515
1042.1292 | 423.3217 | 342.5668 | 402.0102 | 342.0013
1043.1292 | 423.5601 | 343.5092 | 404.1741 | 341.6092
1044.1292 | 424.543 | 344.064 | 404.4648 | 340.7284
1045.1292 | 424.6681 | 344.074 | 403.8815 | 339.2396
1046.1292 | 425.3653 | 346.003 | 403.7632 | 339.6032
1047.1292 | 425.3312 | 349.3317 | 403.4433 | 341.0232
1048.1292 | 425.3427 | 350.8129 | 404.2552 | 340.7785
1049.1292 | 425.1138 | 351.5332 | 404.8295 | 341.2752
1050.1292 | 424.5571 | 353.1978 | 405.4152 | 341.583
1051.1292 | 424.3737 | 352.1961 | 405.59 | 342.389
1052.1292 | 424.3998 | 352.0014 | 406.0279 | 342.9098
1053.1292 | 425.0904 | 353.1461 | 406.6579 | 344.3223
1054.1292 | 424.9951 | 352.7823 | 407.3561 | 346.0253
1055.1292 | 425.3079 | 351.5435 | 409.0627 | 346.4969
1056.1292 | 424.2955 | 351.6428 | 409.972 | 347.4971
1057.1292 | 424.4347 | 350.9183 | 409.877 | 348.4075
1058.1292 | 423.9759 | 351.8948 | 410.6934 | 350.4075
1059.1292 | 423.5414 | 351.8717 | 410.4749 | 348.9431
1060.1292 | 423.0754 | 352.2118 | 408.7236 | 347.4997
1061.1292 | 423.9757 | 351.9875 | 407.7229 | 345.9639
1062.1292 | 424.3858 | 352.6709 | 406.9089 | 344.4771
1063.1292 | 425.4533 | 352.2943 | 405.3444 | 342.8851
1064.1292 | 426.5589 | 352.708 | 403.9209 | 342.4437
1065.1292 | 427.6974 | 352.9747 | 404.7719 | 341.8402
1066.1292 | 427.6847 | 351.6162 | 403.8136 | 340.7291
1067.1292 | 428.303 | 351.9391 | 406.7597 | 340.2095
1068.1292 | 428.6487 | 352.1397 | 407.1829 | 340.3075
1069.1292 | 429.635 | 352.9084 | 407.8948 | 341.0005
1070.1292 | 430.1799 | 352.8523 | 408.8483 | 340.8283
1071.1292 | 429.4902 | 353.0431 | 410.4532 | 343.4449
1072.1292 | 430.9604 | 353.6255 | 409.638 | 344.2372
1073.1292 | 431.6536 | 353.6173 | 408.9354 | 344.0509
1074.1292 | 432.2057 | 352.5563 | 408.8784 | 344.6191
1075.1292 | 431.4654 | 351.9532 | 408.7192 | 343.8146
1076.1292 | 431.4538 | 350.6402 | 409.0308 | 343.8159
1077.1292 | 431.8742 | 350.7095 | 409.6965 | 343.0516
1078.1292 | 432.7719 | 351.4359 | 409.6921 | 343.7886
1079.1292 | 434.1823 | 351.4048 | 411.3107 | 344.5322
1080.1292 | 435.8052 | 351.3599 | 411.5228 | 343.4049
1081.1292 | 436.3297 | 351.0657 | 410.8784 | 343.3388
1082.1292 | 436.8729 | 352.1577 | 411.6545 | 342.6001
1083.1292 | 437.1138 | 353.1743 | 412.0979 | 342.8792
1084.1292 | 436.6837 | 354.2164 | 413.1248 | 341.7494
1085.1292 | 436.8852 | 353.2065 | 412.4999 | 341.8993
1086.1292 | 437.6636 | 352.9387 | 414.3928 | 342.9569
1087.1292 | 437.3742 | 354.1484 | 417.3988 | 345.423
1088.1292 | 436.1933 | 353.5914 | 419.0615 | 346.6595
1089.1292 | 435.4423 | 352.2616 | 418.6311 | 348.5961
1090.1292 | 436.3595 | 350.6988 | 417.6918 | 348.3588
1091.1292 | 436.897 | 351.326 | 418.5335 | 347.8697
1092.1292 | 437.8372 | 352.9643 | 418.0275 | 347.5896
1093.1292 | 437.9682 | 352.1747 | 417.3966 | 347.4043
1094.1292 | 437.948 | 352.7408 | 418.8798 | 347.0413
1095.1292 | 438.5083 | 352.3431 | 420.0487 | 347.0106
1096.1292 | 439.3185 | 353.0148 | 421.3108 | 346.7439
1097.1292 | 439.0264 | 353.6509 | 421.6705 | 347.2882
1098.1292 | 438.4871 | 353.7016 | 423.8305 | 349.8781
1099.1292 | 439.5289 | 353.4665 | 428.4486 | 351.925
1100.1292 | 439.7665 | 352.7603 | 429.6826 | 352.9499
1101.1292 | 441.0002 | 352.909 | 429.6466 | 352.9535
1102.1292 | 442.1626 | 353.1456 | 429.44 | 352.6212
1103.1292 | 443.3179 | 354.1821 | 430.5486 | 352.8289
1104.1292 | 444.4374 | 355.4002 | 429.2037 | 351.3048
1105.1292 | 446.2182 | 355.2807 | 428.0567 | 350.3726
1106.1448 | 447.0215 | 356.8793 | 428.246 | 350.3872
1107.1292 | 447.9844 | 357.0855 | 428.2691 | 352.0291
1108.1292 | 447.9982 | 356.6871 | 426.9574 | 352.1036
1109.1292 | 447.7941 | 355.9468 | 425.8867 | 351.7604
1110.1292 | 448.6686 | 356.2996 | 428.9293 | 351.8588
1111.1292 | 449.3197 | 357.0032 | 428.4028 | 352.377
1112.1292 | 449.3444 | 357.7766 | 429.5704 | 351.6225
1113.1292 | 450.0052 | 359.4941 | 427.6725 | 351.2304
1114.1292 | 449.5457 | 361.2214 | 428.8037 | 350.6248
1115.1292 | 449.8278 | 361.4638 | 427.4538 | 350.6888
1116.1292 | 450.1241 | 361.7571 | 426.5359 | 349.8956
1117.1292 | 450.2441 | 361.1922 | 424.0003 | 348.4344
1118.1292 | 450.1645 | 361.2935 | 423.5858 | 347.765
1119.1292 | 451.3749 | 362.4995 | 431.1911 | 348.1175
1120.1292 | 451.494 | 362.8395 | 434.4452 | 350.1486
1121.1292 | 452.8547 | 363.0209 | 437.1423 | 352.0965
1122.1292 | 454.385 | 363.0089 | 438.6138 | 352.2431
1123.1292 | 454.707 | 364.9464 | 439.4019 | 352.7922
1124.1292 | 454.2969 | 364.4044 | 437.3261 | 354.6192
1125.1292 | 453.6986 | 362.861 | 434.6728 | 352.9908
1126.1292 | 454.6551 | 361.6561 | 433.0143 | 352.2812
1127.1292 | 454.6729 | 360.5234 | 435.2233 | 352.0905
1128.1292 | 453.9246 | 360.5618 | 434.5418 | 351.2972
1129.1292 | 453.2418 | 360.9003 | 435.3498 | 351.7473
1130.1292 | 452.8775 | 360.3736 | 433.2214 | 352.3906
1131.1292 | 453.6003 | 359.2225 | 431.6454 | 354.1328
1132.1292 | 451.5825 | 357.136 | 428.4145 | 355.6912
1133.1292 | 450.0451 | 355.1506 | 424.7234 | 359.2966
1134.1292 | 449.8103 | 353.9264 | 422.6284 | 361.5257
1135.1292 | 448.9337 | 352.3818 | 420.6922 | 361.7681
1136.1448 | 449.1827 | 351.5414 | 422.5001 | 363.278
1137.1292 | 451.0191 | 352.901 | 426.2201 | 364.7349
1138.1292 | 452.0873 | 352.9595 | 424.9438 | 363.6628
1139.1292 | 453.1735 | 353.395 | 423.4937 | 362.6146
1140.1292 | 453.4804 | 354.4392 | 422.9866 | 362.2989
1141.1292 | 452.6417 | 355.0028 | 424.1995 | 362.1379
1142.1292 | 452.8445 | 354.3846 | 425.3651 | 363.5467
1143.1292 | 453.6147 | 353.5617 | 424.3909 | 363.4181
1144.1292 | 454.1935 | 354.722 | 426.2114 | 364.4243
1145.1292 | 454.0606 | 353.722 | 426.4437 | 364.5899
1146.1292 | 454.2624 | 352.7078 | 426.4774 | 364.6544
1147.1448 | 454.9226 | 352.8053 | 426.6168 | 364.6293
1148.1448 | 455.1392 | 351.4461 | 426.9849 | 363.6075
1149.1292 | 455.4731 | 351.2684 | 425.6114 | 361.9872
1150.1292 | 457.3699 | 352.0959 | 423.6384 | 360.2896
1151.1448 | 458.9629 | 355.9825 | 430.0104 | 360.4463
1152.1448 | 459.0775 | 356.1484 | 432.4143 | 361.0591
1153.1448 | 458.9062 | 355.2605 | 431.0816 | 363.9808
1154.1448 | 459.7581 | 354.6689 | 435.3723 | 366.39
1155.1292 | 458.7254 | 353.2609 | 431.6549 | 365.5506
1156.1292 | 458.6719 | 352.5109 | 431.5548 | 364.9639
1157.1292 | 457.4966 | 352.3283 | 431.1239 | 365.6982
1158.1292 | 456.971 | 351.7624 | 430.0126 | 365.1397
1159.1292 | 456.3485 | 351.2474 | 427.8879 | 363.3429
1160.1292 | 456.2564 | 351.378 | 428.1975 | 364.1025
1161.1292 | 455.3489 | 351.1038 | 426.7478 | 364.3808
1162.1292 | 454.6345 | 349.3551 | 424.9896 | 363.78
1163.1292 | 456.3996 | 348.8684 | 424.5358 | 366.3429
1164.1292 | 457.1743 | 349.7385 | 425.1301 | 367.3593
1165.1292 | 458.0372 | 349.845 | 427.0852 | 365.8343
1166.1448 | 459.6439 | 350.7246 | 432.8799 | 365.6267
1167.1448 | 460.0478 | 353.1056 | 434.7359 | 366.3098
1168.1292 | 461.1883 | 354.3637 | 436.7217 | 366.6734
1169.1292 | 461.8374 | 357.0396 | 437.8061 | 366.7638
1170.1292 | 461.3053 | 359.3313 | 437.4315 | 366.0921
1171.1292 | 461.837 | 361.223 | 436.78 | 366.7102
1172.1292 | 461.8315 | 361.3417 | 437.6437 | 365.8206
1173.1292 | 462.0007 | 362.0877 | 435.7878 | 364.2663
1174.1292 | 462.931 | 363.2232 | 436.8877 | 363.6361
1175.1292 | 462.8403 | 364.617 | 435.8692 | 363.6177
1176.1292 | 461.403 | 363.311 | 434.0771 | 364.6727
1177.1292 | 460.741 | 361.7343 | 435.1761 | 365.8082
1178.1292 | 461.4145 | 361.7895 | 439.2191 | 368.2462
1179.1292 | 460.915 | 360.3083 | 437.1257 | 368.5256
1180.1292 | 461.4181 | 359.5148 | 435.5079 | 367.7956
1181.1292 | 462.2231 | 360.2855 | 435.247 | 366.2702
1182.1292 | 462.3149 | 360.6761 | 432.811 | 363.8515
1183.1292 | 463.1855 | 360.1597 | 432.9174 | 361.688
1184.1292 | 463.3508 | 362.045 | 432.1836 | 362.2428
1185.1292 | 463.396 | 362.8004 | 432.4386 | 361.8824
1186.1292 | 463.4945 | 362.3159 | 429.9149 | 360.9409
1187.1292 | 463.3993 | 361.4207 | 429.6657 | 360.2029
1188.1292 | 464.1976 | 361.4271 | 428.2776 | 359.3065
1189.1292 | 464.2342 | 361.716 | 428.6277 | 357.8129
1190.1292 | 465.3703 | 361.7375 | 428.6384 | 356.4513
1191.1292 | 465.9047 | 364.32 | 431.646 | 355.1372
1192.1292 | 465.5 | 364.5731 | 435.6779 | 356.3032
1193.1292 | 466.2409 | 363.8511 | 436.0451 | 355.7346
1194.1292 | 466.9808 | 363.8964 | 436.1934 | 356.026
1195.1292 | 466.853 | 364.1207 | 436.9531 | 356.4492
1196.1292 | 467.3917 | 363.4189 | 437.3909 | 356.5467
1197.1292 | 468.2366 | 365.6766 | 437.6164 | 356.095
1198.1292 | 470.6291 | 368.7426 | 441.2322 | 354.8877
1199.1292 | 472.6313 | 371.7749 | 441.7221 | 356.908
1200.1292 | 472.4723 | 373.1694 | 440.6269 | 356.5049
1201.1292 | 472.8774 | 373.4313 | 440.9111 | 356.3787
1202.1292 | 473.5408 | 373.4916 | 440.0772 | 355.2243
1203.1292 | 474.0092 | 374.058 | 438.7395 | 353.6806
1204.1292 | 475.4697 | 377.2953 | 440.8096 | 353.7172
1205.1292 | 476.6359 | 382.9429 | 444.8462 | 354.0561
1206.1292 | 476.8997 | 382.6628 | 442.7039 | 353.8933
1207.1292 | 476.9943 | 382.9291 | 444.5984 | 354.5552
1208.1292 | 478.1618 | 383.427 | 443.4398 | 355.2101
1209.1292 | 478.9661 | 383.807 | 442.1314 | 357.0562
1210.1292 | 478.6823 | 383.297 | 441.8487 | 357.6211
1211.1292 | 479.2756 | 384.9702 | 445.9674 | 360.7785
1212.1292 | 480.6541 | 383.3884 | 447.7543 | 362.3745
1213.1292 | 481.425 | 382.5631 | 450.5767 | 363.4733
1214.1292 | 481.5426 | 383.1748 | 451.3056 | 362.9655
1215.1292 | 480.5095 | 383.8562 | 450.4427 | 364.0079
1216.1292 | 479.3199 | 382.4646 | 449.3815 | 362.774
1217.1292 | 478.3723 | 382.0549 | 448.9462 | 364.7981
1218.1292 | 478.5993 | 382.026 | 448.2176 | 365.8405
1219.1292 | 477.664 | 381.2454 | 446.5573 | 367.2283
1220.1292 | 477.3562 | 378.9729 | 444.2987 | 366.792
1221.1292 | 478.8794 | 379.8622 | 452.1615 | 369.2693
1222.1292 | 480.565 | 379.3559 | 457.5694 | 370.33
1223.1292 | 481.914 | 378.2365 | 459.0294 | 370.3494
1224.1292 | 482.0835 | 377.4977 | 458.6979 | 372.874
1225.1292 | 483.1055 | 374.6919 | 457.5452 | 372.889
1226.1292 | 484.2186 | 373.404 | 458.9036 | 373.5138
1227.1292 | 484.0776 | 373.0397 | 460.8564 | 372.9936
1228.1292 | 485.5275 | 373.0951 | 462.6995 | 373.0601
1229.1292 | 486.302 | 375.2014 | 469.9808 | 374.2336
1230.1292 | 487.2914 | 376.3998 | 472.9565 | 375.1293
1231.1292 | 488.0797 | 376.2385 | 470.9058 | 376.8374
1232.1292 | 488.4811 | 375.9911 | 470.0676 | 376.1425
1233.1292 | 489.1278 | 377.4952 | 471.7979 | 377.5517
1234.1292 | 489.53 | 377.2903 | 471.8175 | 377.0024
1235.1292 | 489.1764 | 376.8787 | 470.0482 | 376.9957
1236.1292 | 488.6882 | 376.6532 | 467.0339 | 375.2479
1237.1292 | 488.4558 | 378.7271 | 469.7746 | 376.945
1238.1292 | 488.0306 | 377.4955 | 466.6333 | 376.0623
1239.1292 | 488.2147 | 375.8503 | 466.0784 | 376.039
1240.1292 | 487.4532 | 374.2753 | 462.5627 | 376.8795
1241.1292 | 488.8445 | 373.1712 | 462.9407 | 376.9069
1242.1292 | 489.83 | 374.4332 | 464.5967 | 376.2724
1243.1292 | 490.9093 | 375.2966 | 465.8383 | 375.1367
1244.1292 | 490.8863 | 376.5706 | 469.8982 | 376.6605
1245.1292 | 491.2724 | 376.9272 | 472.7185 | 378.6541
1246.1292 | 491.9895 | 378.1221 | 471.3666 | 379.5293
1247.1292 | 492.6433 | 377.385 | 468.4987 | 377.6602
1248.1292 | 494.5552 | 379.2495 | 474.332 | 377.232
1249.1292 | 494.5367 | 381.4405 | 472.7559 | 378.4106
1250.1448 | 494.4638 | 381.2898 | 470.8316 | 377.2049
1251.1292 | 493.6015 | 381.7402 | 468.1247 | 375.9292
1252.1292 | 492.9383 | 380.2846 | 465.5553 | 375.7927
1253.1292 | 493.0152 | 379.3253 | 464.12 | 374.5873
1254.1292 | 493.614 | 378.9786 | 470.1145 | 375.3724
1255.1292 | 495.6449 | 378.6686 | 472.784 | 375.6277
1256.1292 | 496.5664 | 384.8887 | 475.0978 | 375.8212
1257.1292 | 497.3956 | 386.9516 | 474.0217 | 376.0208
1258.1292 | 498.4387 | 387.3631 | 472.4419 | 375.3195
1259.1292 | 497.959 | 387.1129 | 472.0253 | 375.1037
1260.1292 | 498.6316 | 386.7218 | 471.2967 | 375.2077
1261.1292 | 499.4731 | 385.9165 | 470.5983 | 374.9981
1262.1292 | 500.2148 | 386.4983 | 471.046 | 374.914
1263.1292 | 500.8486 | 385.5285 | 468.3406 | 373.3338
1264.1292 | 501.1393 | 385.9005 | 465.9083 | 372.3158
1265.1292 | 501.11 | 385.1947 | 466.0178 | 371.089
1266.1292 | 501.842 | 384.789 | 466.8777 | 369.9073
1267.1292 | 503.7861 | 386.7435 | 478.6761 | 372.288
1268.1292 | 505.6494 | 390.8309 | 488.8118 | 371.8879
1269.1292 | 506.0324 | 392.9724 | 490.3591 | 371.3515
1270.1292 | 505.8623 | 392.3199 | 486.9139 | 370.5642
1271.1292 | 506.5168 | 393.4532 | 483.8077 | 368.3371
1272.1292 | 507.7521 | 396.6299 | 479.6347 | 367.0069
1273.1292 | 508.2033 | 402.3628 | 479.6767 | 366.2578
1274.1292 | 508.8598 | 407.2586 | 484.2459 | 366.4571
1275.1292 | 509.7147 | 411.9793 | 490.6992 | 367.4718
1276.1292 | 510.9176 | 415.5155 | 495.1983 | 367.3325
1277.1292 | 509.8196 | 416.1065 | 495.9002 | 367.6925
1278.1292 | 510.2829 | 414.6246 | 491.6062 | 366.488
1279.1292 | 509.8521 | 413.3832 | 488.3452 | 365.3096
1280.1292 | 509.2191 | 413.2708 | 484.6296 | 364.3397
1281.1292 | 509.3728 | 413.4219 | 482.3725 | 364.6951
1282.1292 | 510.6997 | 422.8863 | 490.3598 | 364.6998
1283.1292 | 509.82 | 423.1318 | 486.4311 | 365.832
1284.1292 | 509.0499 | 421.391 | 482.3948 | 366.3001
1285.1292 | 509.0908 | 420.1876 | 480.1626 | 366.5903
1286.1292 | 510.5067 | 422.8974 | 489.9725 | 369.8931
1287.1292 | 512.6866 | 422.7775 | 491.3148 | 372.0792
1288.1292 | 512.5506 | 421.658 | 490.197 | 373.228
1289.1292 | 513.9526 | 421.1137 | 488.2767 | 373.7324
1290.1292 | 514.1568 | 422.5229 | 491.4025 | 374.3817
1291.1292 | 514.3526 | 420.9859 | 492.8007 | 376.8217
1292.1292 | 514.2066 | 419.9456 | 494.8519 | 380.324
1293.1292 | 513.9375 | 418.6378 | 495.6431 | 381.9072
1294.1292 | 513.9753 | 417.1206 | 495.0942 | 383.1037
1295.1292 | 514.5949 | 416.1939 | 498.2148 | 383.2465
1296.1292 | 513.7113 | 415.6541 | 494.9675 | 381.6596
1297.1292 | 511.7755 | 412.7417 | 490.9418 | 382.2021
1298.1292 | 510.7414 | 409.2861 | 486.3415 | 382.0151
1299.1292 | 509.6074 | 406.2523 | 482.6961 | 380.7971
1300.1292 | 508.8034 | 403.4618 | 479.6148 | 381.333
1301.1292 | 507.903 | 400.4426 | 475.4743 | 380.7819
1302.1292 | 506.3181 | 397.1991 | 471.3047 | 380.2979
1303.1292 | 506.6654 | 394.523 | 467.8688 | 381.9473
1304.1292 | 508.4684 | 392.8344 | 468.369 | 386.5276
1305.1292 | 511.7799 | 393.7177 | 477.241 | 391.8861
1306.1292 | 511.5093 | 396.0561 | 480.1118 | 392.1401
1307.1292 | 512.1815 | 399.8116 | 482.6277 | 390.1328
1308.1292 | 512.4269 | 403.8555 | 485.6421 | 391.807
1309.1292 | 512.3809 | 403.927 | 489.7025 | 391.7931
1310.1292 | 511.9109 | 404.4949 | 490.7879 | 392.5691
1311.1292 | 512.0442 | 404.795 | 490.6307 | 392.1446
1312.1292 | 511.4445 | 406.4394 | 493.2572 | 393.272
1313.1292 | 512.0511 | 405.5278 | 492.768 | 392.5169
1314.1292 | 512.4532 | 406.0737 | 495.3084 | 392.9307
1315.1292 | 511.9767 | 405.3399 | 492.3236 | 390.8858
1316.1292 | 512.5495 | 407.338 | 491.8423 | 390.1987
1317.1292 | 512.6304 | 407.4199 | 489.1024 | 388.9967
1318.1292 | 513.6972 | 407.9296 | 488.8183 | 388.7412
1319.1292 | 513.7543 | 409.6195 | 484.9975 | 386.4193
1320.1292 | 513.9446 | 415.4686 | 481.6596 | 384.6977
1321.1292 | 513.5444 | 416.534 | 482.0158 | 383.5472
1322.1292 | 512.8412 | 415.8762 | 478.8147 | 382.8713
1323.1292 | 513.2922 | 414.7139 | 475.4723 | 382.0817
1324.1292 | 513.3989 | 415.1406 | 474.3897 | 380.1513
1325.1292 | 512.5172 | 415.3784 | 472.9639 | 379.6889
1326.1292 | 512.9456 | 414.3724 | 470.1691 | 379.5331
1327.1292 | 513.0468 | 414.5542 | 468.5691 | 378.2834
1328.1292 | 512.9363 | 412.8136 | 466.6699 | 378.0065
1329.1292 | 512.422 | 411.7484 | 462.9215 | 377.3882
1330.1292 | 511.4378 | 409.7307 | 462.3025 | 378.4541
1331.1292 | 511.0022 | 408.827 | 461.0062 | 379.0548
1332.1292 | 509.6332 | 407.9754 | 460.1929 | 379.3709
1333.1292 | 510.3839 | 407.4714 | 463.9437 | 379.0491
1334.1292 | 510.9894 | 408.508 | 465.867 | 378.3414
1335.1292 | 511.3622 | 409.1235 | 469.8469 | 378.6776
1336.1292 | 510.972 | 406.9985 | 469.3515 | 378.6231
1337.1292 | 510.2891 | 405.1997 | 468.8459 | 379.1829
1338.1292 | 509.4468 | 403.6769 | 468.7217 | 378.7195
1339.1292 | 508.4176 | 401.2611 | 466.2785 | 378.7459
1340.1292 | 509.5627 | 399.7974 | 463.1905 | 379.3155
1341.1292 | 509.6066 | 399.0745 | 463.2189 | 381.1082
1342.1292 | 510.0173 | 398.5147 | 464.5805 | 382.582
1343.1292 | 510.7181 | 397.684 | 464.0203 | 382.9666
1344.1292 | 511.8626 | 399.1008 | 468.4654 | 382.2407
1345.1292 | 511.5088 | 397.9655 | 468.4236 | 381.652
1346.1292 | 512.5369 | 398.3331 | 470.3094 | 381.6691
1347.1292 | 512.2899 | 399.038 | 472.8867 | 383.0238
1348.1292 | 512.0349 | 399.2875 | 471.5609 | 382.67
1349.1292 | 511.5346 | 399.0894 | 470.4077 | 381.2917
1350.1292 | 511.198 | 398.8574 | 469.0725 | 380.7391
1351.1292 | 511.2071 | 398.2005 | 467.8253 | 379.8468
1352.1292 | 511.0459 | 398.2697 | 468.7426 | 379.9071
1353.1292 | 511.0283 | 398.3753 | 468.5658 | 380.815
1354.1292 | 510.7747 | 397.883 | 467.639 | 381.7454
1355.1292 | 510.6503 | 397.97 | 467.2877 | 382.3033
1356.1292 | 511.0119 | 397.2124 | 465.1318 | 380.335
1357.1292 | 511.4083 | 396.4461 | 464.7615 | 381.2443
1358.1292 | 511.3218 | 396.5048 | 464.1214 | 382.5088
1359.1292 | 510.9018 | 396.0135 | 465.315 | 383.9212
1360.1292 | 511.8382 | 394.5776 | 468.9577 | 385.422
1361.1292 | 513.7079 | 394.4106 | 474.5997 | 389.1946
1362.1292 | 513.8068 | 395.0006 | 476.8063 | 391.5713
1363.1292 | 513.6204 | 393.9909 | 475.5733 | 389.8176
1364.1292 | 513.4466 | 394.5736 | 475.0434 | 390.4763
1365.1292 | 514.0239 | 395.097 | 475.8775 | 390.507
1366.1292 | 514.331 | 396.2586 | 478.0709 | 389.5428
1367.1292 | 513.4134 | 398.1327 | 477.1775 | 389.5955
1368.1292 | 512.466 | 397.805 | 476.4472 | 388.3945
1369.1292 | 511.6154 | 398.2847 | 475.4371 | 386.2515
1370.1292 | 512.7305 | 400.2274 | 477.0356 | 385.6038
1371.1292 | 512.9381 | 401.6068 | 476.9744 | 384.7984
1372.1292 | 512.9621 | 401.8786 | 475.6095 | 385.3625
1373.1292 | 512.3479 | 402.4588 | 473.1832 | 383.945
1374.1292 | 512.7739 | 403.5273 | 474.9007 | 384.7436
1375.1292 | 512.9409 | 404.1548 | 474.0212 | 385.5172
1376.1448 | 514.9231 | 405.5145 | 478.1139 | 387.7692
1377.1292 | 514.65 | 405.615 | 475.3778 | 387.4252
1378.1292 | 514.8083 | 404.8075 | 473.9609 | 386.7021
1379.1292 | 514.4712 | 404.1012 | 472.8844 | 386.17
1380.1292 | 513.9348 | 406.8986 | 472.4926 | 385.9319
1381.1292 | 513.809 | 408.5068 | 470.752 | 386.2078
1382.1292 | 512.976 | 408.11 | 467.6342 | 385.0339
1383.1292 | 512.8823 | 407.558 | 466.5945 | 383.8977
1384.1292 | 513.0987 | 406.5519 | 466.5421 | 384.1013
1385.1292 | 513.7876 | 407.5091 | 466.5373 | 384.5411
1386.1292 | 515.2005 | 408.2177 | 467.4059 | 385.0312
1387.1292 | 515.2845 | 408.4766 | 467.9909 | 385.8614
1388.1292 | 515.1162 | 406.974 | 468.659 | 386.4673
1389.1292 | 515.055 | 406.2856 | 467.319 | 386.4911
1390.1292 | 514.7846 | 404.237 | 466.2549 | 388.8526
1391.1448 | 515.3221 | 401.7922 | 465.668 | 390.8802
1392.1448 | 517.536 | 401.0798 | 471.3524 | 392.8671
1393.1292 | 517.0844 | 401.5806 | 475.7921 | 394.2083
1394.1292 | 516.6439 | 405.4101 | 477.8867 | 394.0785
1395.1448 | 516.09 | 407.3461 | 476.927 | 394.3752
1396.1448 | 516.0958 | 405.9525 | 476.7638 | 394.0633
1397.1448 | 515.9844 | 406.599 | 475.8726 | 393.6824
1398.1448 | 516.2977 | 405.0269 | 473.1883 | 393.6895
1399.1292 | 516.8839 | 406.0852 | 474.4464 | 393.8714
1400.1292 | 517.1639 | 405.547 | 475.2639 | 393.5501
1401.1292 | 517.3822 | 404.9824 | 474.4502 | 395.1723
1402.1292 | 517.8159 | 405.6704 | 476.417 | 394.7597
1403.1292 | 517.8171 | 405.782 | 475.3786 | 396.2781
1404.1292 | 517.4543 | 404.4065 | 473.0246 | 396.0111
1405.1292 | 517.2933 | 404.6146 | 472.4956 | 395.8378
1406.1292 | 517.5744 | 403.6555 | 470.9594 | 396.5149
1407.1292 | 517.0391 | 401.8538 | 468.4608 | 394.8801
1408.1292 | 516.5129 | 402.1915 | 467.2415 | 393.0581
1409.1292 | 516.4772 | 402.7964 | 466.1624 | 392.2009
1410.1292 | 518.0182 | 401.5834 | 463.5397 | 390.565
1411.1292 | 517.1208 | 401.1812 | 462.4341 | 389.4117
1412.1292 | 516.6714 | 402.9427 | 462.741 | 388.3803
1413.1292 | 516.535 | 402.8999 | 461.6958 | 388.813
1414.1292 | 517.2476 | 400.1988 | 459.0767 | 388.6662
1415.1292 | 517.262 | 398.2439 | 458.5478 | 388.1744
1416.1292 | 518.7739 | 396.9815 | 461.2709 | 386.9311
1417.1292 | 517.8146 | 399.6402 | 461.4578 | 386.2151
1418.1292 | 518.77 | 400.4738 | 459.6646 | 385.7069
1419.1292 | 518.3246 | 398.9644 | 457.82 | 384.66
1420.1292 | 519.4667 | 399.2813 | 459.8739 | 384.3811
1421.1292 | 520.2342 | 399.6739 | 460.5024 | 384.9548
1422.1292 | 521.1525 | 398.8971 | 461.1118 | 384.9215
1423.1292 | 521.4959 | 399.0869 | 463.3881 | 385.5152
1424.1292 | 522.4153 | 399.4772 | 464.642 | 386.6137
1425.1292 | 522.0007 | 398.1672 | 465.5044 | 386.9356
1426.1292 | 521.8862 | 397.4062 | 463.9943 | 386.2322
1427.1292 | 521.5416 | 396.2487 | 463.1488 | 385.5037
1428.1292 | 522.2978 | 396.7215 | 463.0694 | 386.4664
1429.1292 | 522.4603 | 398.5962 | 461.8394 | 385.1163
1430.1292 | 522.2875 | 399.2173 | 460.1898 | 384.3363
1431.1292 | 522.2106 | 400.2841 | 458.758 | 384.5943
1432.1292 | 522.9594 | 401.0233 | 458.0263 | 384.9676
1433.1292 | 524.4099 | 401.6036 | 456.7122 | 384.6156
1434.1292 | 524.58 | 401.8781 | 457.1845 | 385.7445
1435.1292 | 524.8606 | 401.6752 | 459.3035 | 385.5901
1436.1292 | 525.4383 | 400.6547 | 458.1931 | 385.4746
1437.1292 | 525.6448 | 400.606 | 458.9386 | 386.1718
1438.1292 | 525.0403 | 399.413 | 458.1888 | 385.5955
1439.1292 | 525.3657 | 399.5343 | 458.1832 | 385.2076
1440.1292 | 526.1786 | 399.5347 | 460.6801 | 386.122
1441.1292 | 525.9767 | 397.4373 | 459.9051 | 386.6611
1442.1292 | 525.5872 | 396.3412 | 457.6429 | 387.3902
1443.1292 | 525.8297 | 395.1266 | 457.5185 | 387.7882
1444.1292 | 526.0154 | 393.6038 | 457.2926 | 387.3094
1445.1292 | 526.841 | 393.6806 | 459.7805 | 388.355
1446.1292 | 526.9698 | 394.1326 | 460.2983 | 387.7722
1447.1292 | 526.7687 | 395.7447 | 460.494 | 387.9152
1448.1292 | 526.9059 | 396.7403 | 461.7577 | 388.8647
1449.1292 | 526.7711 | 398.4124 | 461.7128 | 389.0147
1450.1292 | 528.0807 | 399.6881 | 460.6529 | 387.6776
1451.1292 | 528.4834 | 399.6727 | 458.8512 | 386.5146
1452.1292 | 528.3816 | 398.064 | 456.3859 | 386.5293
1453.1292 | 528.5117 | 397.5219 | 455.2329 | 385.2955
1454.1292 | 530.6341 | 397.1015 | 454.7486 | 384.9238
1455.1292 | 530.5622 | 396.5458 | 455.3168 | 384.3696
1456.1292 | 530.3612 | 396.3766 | 454.399 | 383.4982
1457.1292 | 529.9117 | 397.1552 | 452.9157 | 381.8321
1458.1292 | 529.7069 | 397.6992 | 450.357 | 379.9032
1459.1292 | 531.8226 | 397.9579 | 447.8102 | 378.7849
1460.1292 | 531.8969 | 398.3766 | 448.7057 | 378.9761
1461.1292 | 531.954 | 398.3482 | 450.274 | 378.7618
1462.1292 | 531.4958 | 397.8406 | 449.0197 | 378.093
1463.1292 | 530.527 | 396.7213 | 448.8466 | 377.0607
1464.1292 | 530.0223 | 397.844 | 448.5008 | 376.6379
1465.1292 | 530.2147 | 397.9373 | 448.684 | 376.7464
1466.1448 | 530.6521 | 396.8045 | 449.113 | 377.2651
1467.1292 | 530.7571 | 396.3933 | 450.3579 | 378.5444
1468.1292 | 531.5282 | 395.9279 | 451.5324 | 379.613
1469.1292 | 531.5835 | 395.219 | 451.3146 | 379.817
1470.1292 | 530.8847 | 395.164 | 448.9985 | 378.7668
1471.1292 | 530.6772 | 395.4785 | 447.9585 | 377.8947
1472.1292 | 530.8017 | 395.8904 | 448.2163 | 378.942
1473.1292 | 530.5551 | 394.4694 | 446.2236 | 378.111
1474.1292 | 531.8842 | 395.1065 | 447.6665 | 378.349
1475.1292 | 531.3537 | 394.8158 | 448.6348 | 379.0893
1476.1292 | 531.0554 | 394.1065 | 447.6291 | 380.2688
1477.1292 | 532.4464 | 392.2066 | 446.721 | 379.6418
1478.1292 | 532.546 | 392.313 | 449.1588 | 380.9073
1479.1292 | 531.8069 | 392.0659 | 451.0423 | 380.8106
1480.1292 | 531.7743 | 391.4956 | 452.1197 | 381.9245
1481.1292 | 533.1481 | 392.3703 | 454.5441 | 383.2035
1482.1292 | 533.3806 | 391.5843 | 453.8115 | 383.8965
1483.1292 | 533.9551 | 391.9844 | 454.0425 | 383.9405
1484.1292 | 532.7176 | 393.8166 | 454.6655 | 384.2896
1485.1292 | 533.561 | 393.8563 | 454.4335 | 385.9455
1486.1292 | 535.3515 | 392.8481 | 454.3051 | 387.5742
1487.1292 | 540.4344 | 392.4086 | 455.9759 | 389.619
1488.1292 | 541.0413 | 394.2595 | 458.3632 | 390.0791
1489.1292 | 542.9431 | 395.0191 | 460.7776 | 392.3482
1490.1292 | 542.1672 | 395.1347 | 462.1048 | 394.4625
1491.1292 | 541.1567 | 396.0753 | 462.8435 | 393.3199
1492.1292 | 541.1095 | 396.5171 | 463.6471 | 393.1147
1493.1292 | 540.0841 | 397.0454 | 463.9394 | 392.4135
1494.1292 | 540.1111 | 397.8462 | 463.8767 | 392.7656
1495.1292 | 539.9229 | 398.1289 | 462.9111 | 393.3702
1496.1292 | 540.5007 | 396.3403 | 463.5566 | 393.4599
1497.1292 | 540.7769 | 395.8876 | 463.205 | 394.0956
1498.1292 | 542.2997 | 396.4426 | 461.8754 | 395.6476
1499.1292 | 543.5667 | 395.7005 | 460.2122 | 397.5543
1500.1292 | 544.1923 | 394.0144 | 458.8657 | 397.6676
1501.1292 | 545.7214 | 393.0782 | 458.6725 | 397.3877
1502.1292 | 545.9931 | 392.251 | 458.0193 | 397.2689
1503.1292 | 544.9493 | 393.2882 | 459.6073 | 397.0432
1504.1292 | 543.5917 | 393.4585 | 458.5735 | 397.2586
1505.1292 | 543.0725 | 393.7025 | 459.0394 | 397.3188
1506.1292 | 543.6385 | 393.079 | 460.615 | 397.3464
1507.1292 | 543.6953 | 393.7975 | 461.8968 | 398.0068
1508.1292 | 542.7163 | 394.0417 | 460.6971 | 396.8508
1509.1292 | 542.4268 | 395.1749 | 461.6815 | 397.3635
1510.1292 | 544.5641 | 394.0812 | 462.2908 | 397.2769
1511.1292 | 545.4003 | 394.1972 | 463.0502 | 398.3034
1512.1292 | 543.5561 | 394.4247 | 461.7531 | 397.7722
1513.1292 | 543.8744 | 395.4073 | 462.453 | 396.9798
1514.1292 | 542.2032 | 394.6435 | 461.5994 | 396.463
1515.1292 | 541.8677 | 392.8577 | 459.0267 | 394.4419
1516.1292 | 540.3837 | 393.4764 | 460.2334 | 393.1724
1517.1292 | 540.5834 | 393.9566 | 461.0121 | 392.1189
1518.1292 | 542.5755 | 393.203 | 460.376 | 391.645
1519.1292 | 541.3079 | 393.4729 | 460.0858 | 393.0466
1520.1292 | 541.8564 | 393.3593 | 460.5811 | 391.8802
1521.1292 | 541.7129 | 393.061 | 460.3904 | 390.6988
1522.1292 | 541.2792 | 394.2845 | 460.2201 | 390.3858
1523.1292 | 541.7526 | 397.0388 | 461.3442 | 390.3727
1524.1292 | 540.1125 | 396.5949 | 460.1613 | 390.3172
1525.1292 | 540.4913 | 395.3822 | 459.6517 | 389.6282
1526.1292 | 541.9971 | 395.5712 | 460.5862 | 390.2497
1527.1292 | 541.831 | 394.176 | 460.5159 | 389.4444
1528.1292 | 540.2339 | 393.7595 | 460.6241 | 389.7125
1529.1292 | 539.9262 | 393.2089 | 460.0655 | 389.1493
1530.1292 | 539.3825 | 394.2017 | 460.166 | 389.0302
1531.1292 | 539.2136 | 395.222 | 460.1665 | 388.7858
1532.1292 | 539.1357 | 395.2035 | 459.5184 | 388.0323
1533.1292 | 539.7244 | 395.3225 | 459.1246 | 387.6153
1534.1292 | 539.3553 | 396.4214 | 459.2971 | 389.1485
1535.1292 | 538.8532 | 395.8383 | 459.5169 | 389.4126
1536.1292 | 540.3464 | 395.3336 | 460.4396 | 389.1559
1537.1292 | 540.3911 | 394.6169 | 459.8298 | 389.5615
1538.1292 | 540.3295 | 393.8616 | 456.9785 | 388.5997
1539.1292 | 541.0718 | 394.0838 | 456.4583 | 388.091
1540.1292 | 540.8271 | 393.1629 | 454.8707 | 386.5022
1541.1292 | 539.9786 | 393.4989 | 453.1126 | 385.6758
1542.1292 | 541.1345 | 392.3148 | 452.8783 | 386.5667
1543.1292 | 542.5673 | 391.4607 | 451.9818 | 387.1125
1544.1292 | 543.2285 | 390.3726 | 451.7197 | 385.6119
1545.1292 | 541.3361 | 390.9036 | 451.6728 | 385.9722
1546.1292 | 539.9334 | 390.6461 | 451.9259 | 386.2575
1547.1292 | 539.2251 | 390.0387 | 452.5656 | 386.7883
1548.1292 | 538.7368 | 390.2446 | 454.7513 | 388.3349
1549.1292 | 540.3446 | 390.8903 | 455.3841 | 390.4828
1550.1292 | 541.9483 | 390.1335 | 456.0201 | 393.0578
1551.1292 | 542.4869 | 390.3211 | 457.3693 | 395.6789
1552.1292 | 542.4333 | 390.4487 | 458.0289 | 395.5911
1553.1292 | 542.614 | 392.1433 | 459.0159 | 396.119
1554.1292 | 541.3023 | 392.4796 | 458.1064 | 396.4816
1555.1292 | 541.2304 | 392.2853 | 458.8416 | 395.7343
1556.1292 | 541.8993 | 392.8413 | 458.7612 | 394.9714
1557.1292 | 545.392 | 392.3216 | 458.0829 | 394.9977
1558.1292 | 547.945 | 392.1909 | 460.5638 | 396.3461
1559.1292 | 549.3711 | 391.9305 | 460.8876 | 396.1327
1560.1292 | 548.3887 | 392.0908 | 460.9004 | 397.1597
1561.1292 | 548.4411 | 391.7038 | 459.3575 | 397.3617
1562.1292 | 548.0295 | 392.9734 | 460.6602 | 396.4619
1563.1292 | 545.1167 | 394.8269 | 460.5291 | 395.7754
1564.1292 | 544.3856 | 394.7812 | 461.0944 | 394.65
1565.1292 | 543.3678 | 397.0022 | 459.9253 | 394.7975
1566.1292 | 542.553 | 397.467 | 459.0892 | 394.2156
1567.1292 | 541.7744 | 397.1189 | 460.6391 | 393.9147
1568.1292 | 542.1318 | 395.2993 | 458.1457 | 393.7932
1569.1292 | 541.5313 | 393.2715 | 455.8449 | 393.1766
1570.1292 | 542.2796 | 393.0445 | 456.2601 | 394.5351
1571.1292 | 540.6278 | 393.4925 | 456.1939 | 393.5106
1572.1292 | 540.8723 | 395.9313 | 456.4028 | 393.1093
1573.1292 | 530.8901 | 398.1792 | 452.1357 | 392.1979
1574.1292 | 531.3136 | 398.7972 | 451.2347 | 391.0758
1575.1292 | 543.0525 | 399.9864 | 459.2797 | 392.8374
1576.1292 | 543.2846 | 400.3712 | 460.9452 | 393.3533
1577.1292 | 543.4074 | 398.9733 | 461.6458 | 393.6866
1578.1292 | 547.0123 | 397.3892 | 463.3073 | 395.0143
1579.1292 | 548.5754 | 396.8776 | 464.3273 | 396.9531
1580.1292 | 550.0225 | 396.3898 | 465.4253 | 397.1782
1581.1292 | 549.3863 | 396.3439 | 464.1226 | 395.8634
1582.1292 | 549.37 | 397.6349 | 462.8472 | 395.2358
1583.1292 | 548.0226 | 398.4502 | 463.6389 | 395.108
1584.1292 | 549.2089 | 399.5652 | 462.6804 | 394.4911
1585.1292 | 547.7818 | 401.1191 | 464.1118 | 395.7235
1586.1292 | 549.1162 | 401.744 | 463.9087 | 397.2301
1587.1292 | 548.7549 | 402.3042 | 464.6193 | 397.0985
1588.1292 | 548.7171 | 403.7437 | 465.0954 | 397.919
1589.1292 | 548.7693 | 402.7747 | 464.1187 | 396.9214
1590.1292 | 548.329 | 402.5522 | 464.7676 | 396.9737
1591.1292 | 549.0986 | 401.6919 | 464.4777 | 397.8484
1592.1292 | 550.1378 | 401.3743 | 466.6927 | 398.9928
1593.1292 | 551.0926 | 401.0971 | 466.4919 | 398.8516
1594.1292 | 549.7966 | 401.6716 | 467.3935 | 399.603
1595.1292 | 550.874 | 400.984 | 467.52 | 401.3565
1596.1292 | 552.455 | 399.8277 | 468.4231 | 403.1484
1597.1292 | 554.6979 | 399.9552 | 467.7177 | 406.9778
1598.1292 | 557.4202 | 399.0163 | 468.1559 | 407.0398
1599.1292 | 560.5096 | 400.1115 | 469.6133 | 409.6838
1600.1292 | 560.1702 | 401.7055 | 472.2063 | 411.6545
1601.1292 | 558.912 | 401.6911 | 473.8546 | 411.503
1602.1292 | 561.3246 | 400.8364 | 474.8217 | 413.5015
1603.1292 | 563.7729 | 400.203 | 476.2728 | 415.0193
1604.1292 | 568.515 | 399.3033 | 475.2934 | 415.4137
1605.1292 | 570.481 | 397.9643 | 474.0172 | 416.659
1606.1292 | 575.5233 | 397.1411 | 474.1404 | 420.3188
1607.1292 | 580.8805 | 396.8196 | 473.8719 | 423.0477
1608.1292 | 584.2009 | 396.6987 | 472.2128 | 425.8095
1609.1292 | 584.623 | 395.7947 | 469.8477 | 425.3949
1610.1292 | 587.0845 | 395.3056 | 469.4473 | 425.0091
1611.1292 | 586.894 | 394.5863 | 469.9844 | 425.0506
1612.1292 | 586.0609 | 393.8255 | 469.1581 | 424.8362
1613.1292 | 584.877 | 393.6675 | 469.3758 | 426.5377
1614.1292 | 580.337 | 394.406 | 471.5272 | 427.5734
1615.1292 | 576.9057 | 395.033 | 475.0109 | 428.4868
1616.1292 | 578.1906 | 396.0113 | 478.267 | 430.292
1617.1292 | 577.3207 | 395.7466 | 478.355 | 429.3641
1618.1292 | 578.2655 | 396.325 | 479.8831 | 429.8906
1619.1292 | 581.029 | 396.4547 | 479.7151 | 430.5469
1620.1292 | 579.0846 | 397.8535 | 482.4318 | 430.2495
1621.1292 | 575.8657 | 398.4801 | 483.467 | 430.0958
1622.1292 | 571.8181 | 400.7334 | 482.6848 | 428.1307
1623.1292 | 569.8296 | 402.9314 | 481.6005 | 425.2515
1624.1292 | 569.1892 | 405.2476 | 480.9222 | 423.7025
1625.1292 | 566.5094 | 407.9267 | 481.0781 | 422.7227
1626.1292 | 565.0129 | 409.426 | 481.2658 | 420.2699
1627.1292 | 562.3004 | 409.59 | 480.5271 | 418.3735
1628.1292 | 560.0654 | 413.0221 | 480.3095 | 417.4532
1629.1292 | 558.8408 | 414.8741 | 481.7072 | 416.8171
1630.1292 | 557.603 | 415.3273 | 481.0299 | 415.4911
1631.1292 | 557.2566 | 415.1691 | 482.4925 | 414.657
1632.1292 | 555.839 | 415.7154 | 484.2833 | 414.0601
1633.1292 | 557.3027 | 415.9294 | 483.7433 | 414.9943
1634.1292 | 557.3497 | 415.8776 | 482.51 | 419.2909
1635.1448 | 559.1182 | 414.8329 | 481.8123 | 420.9633
1636.1448 | 560.5022 | 413.6344 | 481.3395 | 421.4442
1637.1292 | 560.9863 | 413.7952 | 481.5254 | 422.4944
1638.1292 | 564.6816 | 411.6633 | 481.0598 | 424.6589
1639.1448 | 564.8923 | 410.9343 | 481.0549 | 425.9532
1640.1448 | 566.3501 | 409.7922 | 483.1654 | 430.5874
1641.1448 | 568.0749 | 408.0428 | 480.5627 | 430.3059
1642.1448 | 567.7611 | 407.5403 | 480.6957 | 430.887
1643.1292 | 566.2985 | 407.5098 | 480.6262 | 431.1434
1644.1292 | 566.3841 | 408.2116 | 483.0729 | 430.8096
1645.1292 | 565.7634 | 408.7932 | 485.9539 | 429.8195
1646.1292 | 564.0152 | 410.5505 | 487.0281 | 428.6012
1647.1292 | 563.2108 | 411.3196 | 486.4847 | 427.2906
1648.1292 | 560.7934 | 414.0049 | 486.5707 | 427.056
1649.1292 | 560.3546 | 414.707 | 486.887 | 425.8644
1650.1292 | 558.8724 | 415.4825 | 485.8197 | 424.2612
1651.1292 | 558.6262 | 416.4316 | 485.6773 | 423.2423
1652.1448 | 557.9999 | 418.0978 | 484.7721 | 422.041
1653.1292 | 556.242 | 418.0786 | 484.4418 | 421.3345
1654.1292 | 555.4115 | 418.233 | 485.9532 | 421.9047
1655.1292 | 554.7677 | 418.8062 | 488.4587 | 422.5275
1656.1292 | 554.1811 | 418.2386 | 486.7782 | 420.6121
1657.1292 | 553.2484 | 419.0493 | 485.9223 | 419.1431
1658.1292 | 552.564 | 421.2831 | 485.2279 | 417.8798
1659.1292 | 551.2622 | 423.3507 | 486.4252 | 417.1783
1660.1292 | 551.6821 | 423.3505 | 488.7435 | 417.8677
1661.1448 | 551.8975 | 423.857 | 491.862 | 419.0045
1662.1292 | 554.3101 | 424.5378 | 492.4222 | 421.8307
1663.1292 | 554.9673 | 425.5858 | 494.1568 | 423.7324
1664.1292 | 554.8096 | 424.3745 | 492.4849 | 423.5089
1665.1292 | 554.9175 | 425.1728 | 493.4524 | 424.0778
1666.1292 | 555.0433 | 426.3244 | 495.2964 | 426.0483
1667.1292 | 554.2217 | 426.3582 | 493.8766 | 425.2244
1668.1292 | 554.4332 | 426.9242 | 493.7644 | 423.1357
1669.1292 | 554.024 | 430.6844 | 496.4263 | 422.1629
1670.1292 | 554.6342 | 434.0639 | 499.7635 | 422.1419
1671.1292 | 554.3424 | 434.3274 | 503.0318 | 421.7993
1672.1292 | 554.6057 | 433.48 | 504.1205 | 420.4072
1673.1292 | 553.7351 | 432.9437 | 502.4635 | 420.4637
1674.1292 | 553.0675 | 433.505 | 501.7478 | 419.5764
1675.1292 | 552.0126 | 433.3985 | 500.133 | 418.2026
1676.1292 | 551.2403 | 432.7643 | 498.3063 | 416.7292
1677.1292 | 551.8281 | 431.8148 | 497.0355 | 416.9635
1678.1292 | 552.5818 | 432.5399 | 497.3371 | 417.1229
1679.1292 | 552.0802 | 433.8149 | 496.7971 | 419.3975
1680.1292 | 553.946 | 432.8414 | 496.498 | 419.8149
1681.1292 | 555.9714 | 432.5552 | 497.5536 | 420.0039
1682.1292 | 555.7942 | 434.3639 | 498.8577 | 421.9322
1683.1292 | 555.5361 | 436.7994 | 501.1782 | 422.8776
1684.1292 | 556.6169 | 435.8774 | 503.8567 | 425.603
1685.1292 | 557.3069 | 436.1942 | 504.5191 | 425.519
1686.1292 | 556.5163 | 436.5071 | 506.8094 | 424.9505
1687.1292 | 556.5998 | 438.1551 | 507.813 | 424.1038
1688.1292 | 556.2486 | 438.3161 | 506.8417 | 422.6516
1689.1292 | 556.8727 | 436.5921 | 504.9984 | 423.6587
1690.1292 | 556.4109 | 436.2962 | 503.8321 | 424.1825
1691.1292 | 558.0538 | 435.8953 | 503.2258 | 425.8843
1692.1292 | 561.8677 | 433.845 | 502.6605 | 429.8883
1693.1292 | 562.181 | 434.5389 | 503.5613 | 432.225
1694.1292 | 563.6794 | 435.1258 | 503.8194 | 431.4674
1695.1292 | 562.9768 | 436.0881 | 502.1018 | 430.2488
1696.1292 | 561.1837 | 436.8204 | 500.5247 | 429.1169
1697.1292 | 559.9548 | 437.1509 | 499.9618 | 428.1716
1698.1292 | 561.4724 | 437.7037 | 497.6409 | 426.539
1699.1292 | 561.9661 | 439.6533 | 500.0016 | 425.414
1700.1292 | 564.0764 | 438.195 | 500.3736 | 424.062
1701.1292 | 563.6933 | 438.8828 | 502.6146 | 424.4767
1702.1292 | 565.9116 | 437.2886 | 503.6809 | 426.2969
1703.1292 | 571.0815 | 437.4978 | 506.0437 | 429.5238
1704.1292 | 573.571 | 436.7677 | 510.2394 | 431.457
1705.1292 | 574.109 | 437.8447 | 516.5903 | 432.272
1706.1292 | 574.8294 | 438.4107 | 516.7843 | 430.7106
1707.1292 | 575.839 | 437.858 | 513.494 | 428.2745
1708.1292 | 573.6396 | 439.4951 | 511.5019 | 425.9933
1709.1292 | 573.1332 | 445.3956 | 517.0967 | 426.7926
1710.1292 | 572.6148 | 446.5234 | 520.0392 | 425.6625
1711.1292 | 571.5035 | 445.9761 | 518.7951 | 425.175
1712.1292 | 569.2711 | 447.8658 | 520.191 | 426.284
1713.1292 | 567.7104 | 449.4538 | 519.8889 | 428.3335
1714.1292 | 566.1112 | 450.1906 | 519.8831 | 428.0235
1715.1292 | 564.875 | 449.8827 | 518.9594 | 429.0959
1716.1292 | 563.0549 | 451.7489 | 516.8308 | 428.2914
1717.1292 | 562.1038 | 452.2636 | 516.6337 | 428.7421
1718.1292 | 561.223 | 452.0988 | 516.456 | 429.6167
1719.1292 | 561.8928 | 453.4124 | 516.4403 | 430.5451
1720.1292 | 560.9023 | 453.0821 | 514.7389 | 429.4341
1721.1292 | 560.1157 | 453.7454 | 513.3781 | 428.9781
1722.1292 | 560.0334 | 451.8834 | 513.2184 | 429.421
1723.1292 | 561.6206 | 451.758 | 515.6311 | 429.0667
1724.1292 | 561.6083 | 452.0473 | 515.1885 | 429.5454
1725.1292 | 561.5696 | 453.2371 | 514.9083 | 428.9253
1726.1292 | 560.4757 | 452.3154 | 515.0922 | 428.1978
1727.1292 | 560.2518 | 453.0229 | 519.2373 | 428.4941
1728.1292 | 560.9284 | 452.5088 | 520.334 | 428.5153
1729.1292 | 560.628 | 451.0445 | 520.4311 | 427.8709
1730.1292 | 560.4979 | 450.2299 | 518.9652 | 429.9401
1731.1292 | 562.4527 | 452.4991 | 522.0235 | 430.5336
1732.1292 | 564.2077 | 451.6206 | 521.2255 | 429.9163
1733.1292 | 563.4878 | 450.3207 | 521.9132 | 429.0434
1734.1292 | 564.7551 | 449.2971 | 524.4687 | 429.8369
1735.1292 | 566.2464 | 449.5669 | 525.5918 | 428.9934
1736.1292 | 567.1959 | 447.8077 | 530.4931 | 429.2064
1737.1292 | 565.9951 | 448.9581 | 530.3674 | 431.0057
1738.1292 | 566.7021 | 450.2702 | 531.1612 | 430.8389
1739.1292 | 565.3773 | 450.4249 | 530.3207 | 431.3837
1740.1292 | 565.7281 | 449.2858 | 528.3304 | 431.6362
1741.1292 | 565.3356 | 449.4039 | 529.6994 | 431.1086
1742.1292 | 566.7632 | 449.2207 | 529.0288 | 431.7182
1743.1292 | 565.7303 | 448.7288 | 530.53 | 432.3886
1744.1292 | 563.9687 | 447.998 | 528.7751 | 431.086
1745.1292 | 565.088 | 447.1218 | 527.633 | 429.7631
1746.1292 | 565.4467 | 448.9484 | 530.1448 | 432.0797
1747.1292 | 566.1223 | 448.8857 | 530.7805 | 431.718
1748.1292 | 568.6543 | 447.6677 | 530.7125 | 434.1778
1749.1292 | 568.4107 | 447.6179 | 532.8685 | 434.9681
1750.1292 | 568.1777 | 446.9989 | 533.7386 | 431.78
1751.1292 | 566.8436 | 447.1743 | 529.3459 | 429.7075
1752.1292 | 565.7738 | 448.4293 | 525.5886 | 427.591
1753.1292 | 565.6039 | 446.4241 | 524.1387 | 426.8389
1754.1292 | 564.2168 | 447.3657 | 524.1593 | 427.2599
1755.1292 | 563.5204 | 448.6532 | 528.057 | 428.0852
1756.1292 | 564.2479 | 452.8606 | 527.5718 | 428.9787
1757.1292 | 563.9291 | 454.099 | 525.6065 | 428.7884
1758.1292 | 565.8734 | 456.8636 | 525.0669 | 429.7107
1759.1292 | 566.0984 | 456.9117 | 522.4517 | 429.3903
1760.1292 | 566.9054 | 457.2455 | 521.959 | 427.9259
1761.1292 | 568.008 | 457.9135 | 521.131 | 429.6345
1762.1292 | 571.1504 | 460.0582 | 526.0847 | 431.6492
1763.1292 | 569.9825 | 463.4149 | 528.0075 | 431.9793
1764.1292 | 571.5032 | 465.3985 | 527.6512 | 433.7845
1765.1292 | 575.3795 | 464.1759 | 527.2748 | 434.615
1766.1292 | 577.8642 | 462.727 | 532.7546 | 434.6882
1767.1292 | 579.2645 | 464.0461 | 536.0719 | 434.8717
1768.1292 | 579.3837 | 465.5722 | 535.7758 | 437.7838
1769.1292 | 581.6159 | 468.0918 | 538.0684 | 439.9127
1770.1292 | 582.7987 | 471.4075 | 540.0318 | 443.4286
1771.1292 | 585.1043 | 472.4861 | 542.801 | 443.1018
1772.1292 | 586.1023 | 471.8332 | 545.4497 | 441.5817
1773.1292 | 584.6352 | 470.7285 | 548.3019 | 441.9992
1774.1292 | 583.4546 | 471.461 | 549.1787 | 439.9003
1775.1292 | 581.6691 | 475.9039 | 550.3455 | 440.8767
1776.1292 | 579.2155 | 477.3178 | 550.0353 | 441.2341
1777.1292 | 577.9514 | 477.8206 | 549.205 | 441.2851
1778.1292 | 578.3822 | 478.7913 | 557.3692 | 443.9304
1779.1292 | 577.9196 | 481.9995 | 557.9229 | 444.7472
1780.1292 | 577.7908 | 484.1855 | 559.0221 | 447.4244
1781.1292 | 577.9908 | 484.8801 | 558.6339 | 447.5882
1782.1292 | 578.1255 | 487.0639 | 561.5058 | 449.4771
1783.1292 | 577.5992 | 488.1221 | 562.7945 | 451.0872
1784.1292 | 577.1464 | 489.0038 | 565.3089 | 451.0617
1785.1292 | 575.9557 | 489.247 | 571.6722 | 451.1859
1786.1292 | 574.3523 | 488.8364 | 576.8761 | 450.9376
1787.1292 | 575.6856 | 487.9428 | 575.6259 | 451.0757
1788.1292 | 577.4507 | 489.6245 | 584.9988 | 452.5827
1789.1292 | 580.2325 | 487.2254 | 586.2233 | 452.1847
1790.1292 | 582.0599 | 485.516 | 586.7761 | 451.3173
1791.1292 | 581.1965 | 481.4552 | 584.9092 | 449.5128
1792.1292 | 582.128 | 480.6222 | 584.0664 | 448.3353
1793.1292 | 584.3666 | 482.675 | 587.0444 | 448.0533
1794.1292 | 586.7768 | 480.1027 | 591.2984 | 447.837
1795.1292 | 587.5672 | 479.2962 | 591.3009 | 449.1879
1796.1292 | 587.4734 | 478.5683 | 588.0629 | 448.5936
1797.1292 | 585.8593 | 478.3252 | 586.341 | 447.4569
1798.1292 | 584.5544 | 479.4124 | 581.9698 | 447.0078
1799.1292 | 583.651 | 477.9222 | 593.5034 | 445.6572
1800.1292 | 582.3842 | 478.5714 | 600.8948 | 445.6128
1801.1292 | 580.9488 | 477.3599 | 601.3825 | 445.7304
1802.1292 | 580.5827 | 475.7588 | 596.5282 | 445.3921
1803.1292 | 580.4147 | 475.0109 | 592.8175 | 446.2559
1804.1292 | 579.0164 | 475.5739 | 585.8115 | 446.98
1805.1292 | 578.8869 | 474.9001 | 580.42 | 446.8507
1806.1292 | 577.0746 | 474.4604 | 577.3132 | 444.3025
1807.1292 | 575.7866 | 471.6599 | 569.6682 | 443.3342
1808.1292 | 575.5662 | 470.763 | 566.3464 | 443.0847
1809.1292 | 576.5108 | 470.6638 | 567.3767 | 443.4257
1810.1292 | 575.7192 | 468.6493 | 569.0818 | 442.7526
1811.1292 | 576.9275 | 467.8032 | 572.1359 | 442.4816
1812.1292 | 577.051 | 465.8231 | 573.046 | 441.8877
1813.1292 | 576.2415 | 464.9811 | 570.0557 | 441.5365
1814.1292 | 574.9388 | 465.3626 | 570.5248 | 441.6838
1815.1292 | 574.2335 | 463.947 | 568.317 | 440.0623
1816.1292 | 574.1189 | 462.9055 | 563.763 | 439.4732
1817.1292 | 577.6747 | 465.9572 | 562.2252 | 442.289
1818.1292 | 579.5219 | 465.2345 | 562.6622 | 442.9112
1819.1292 | 579.5427 | 462.398 | 563.728 | 441.2214
1820.1292 | 577.7767 | 460.8098 | 562.2561 | 439.8824
1821.1292 | 576.8664 | 460.6242 | 561.5502 | 439.0531
1822.1292 | 575.8089 | 459.6368 | 558.2413 | 437.5599
1823.1292 | 577.5469 | 457.236 | 555.7743 | 437.6071
1824.1292 | 578.285 | 456.2951 | 556.8989 | 438.6555
1825.1292 | 577.5519 | 455.6802 | 556.8009 | 438.6013
1826.1292 | 576.1148 | 455.8167 | 552.7883 | 439.0783
1827.1292 | 577.1011 | 456.1413 | 550.5543 | 439.4732
1828.1292 | 577.1103 | 455.9564 | 548.4676 | 439.308
1829.1292 | 575.7934 | 455.2752 | 542.5124 | 435.8811
1830.1292 | 574.4739 | 457.0945 | 539.8405 | 434.9358
1831.1292 | 574.9798 | 458.9813 | 540.5636 | 435.4189
1832.1292 | 575.7497 | 458.1395 | 542.9858 | 435.6126
1833.1292 | 576.4582 | 458.4463 | 546.8689 | 437.0637
1834.1292 | 576.4385 | 458.703 | 548.4586 | 437.555
1835.1292 | 578.5431 | 460.2995 | 548.5509 | 437.1202
1836.1292 | 578.7915 | 462.2049 | 553.0499 | 440.1628
1837.1292 | 577.5657 | 464.2209 | 551.0027 | 441.2711
1838.1292 | 576.498 | 464.0226 | 548.3145 | 440.6547
1839.1292 | 574.8841 | 466.6731 | 544.0455 | 438.3857
1840.1292 | 573.4825 | 465.0147 | 540.3724 | 437.5383
1841.1292 | 572.6224 | 465.1124 | 540.1312 | 436.1498
1842.1292 | 571.1632 | 466.4155 | 540.9123 | 435.5945
1843.1292 | 570.1603 | 466.5518 | 540.1718 | 435.8018
1844.1292 | 571.4044 | 467.8486 | 536.7041 | 437.3664
1845.1292 | 570.5488 | 467.9129 | 538.9209 | 438.0153
1846.1292 | 569.3105 | 466.443 | 536.7522 | 437.2017
1847.1292 | 568.9806 | 468.0387 | 539.2257 | 435.8873
1848.1292 | 568.3541 | 466.5959 | 535.8439 | 434.4291
1849.1292 | 568.571 | 467.8394 | 533.7105 | 431.685
1850.1292 | 568.1487 | 467.5568 | 533.3346 | 433.1397
1851.1292 | 569.1826 | 468.2102 | 537.4713 | 435.5985
1852.1292 | 569.7071 | 468.5354 | 539.1247 | 436.8141
1853.1292 | 569.9079 | 467.4829 | 537.9913 | 436.5541
1854.1292 | 571.6418 | 467.3303 | 534.7471 | 433.6763
1855.1292 | 570.873 | 465.8222 | 535.4359 | 432.7377
1856.1292 | 572.6435 | 466.3148 | 534.5995 | 433.4269
1857.1292 | 573.1689 | 464.7082 | 531.4718 | 432.7436
1858.1292 | 572.5682 | 463.2897 | 531.5012 | 433.0138
1859.1292 | 574.0454 | 463.3889 | 542.1168 | 434.1963
1860.1292 | 575.3966 | 462.596 | 543.9714 | 434.0502
1861.1292 | 577.7243 | 461.5999 | 543.6177 | 432.8501
1862.1292 | 577.7056 | 462.0823 | 541.2904 | 432.3767
1863.1292 | 579.7575 | 460.9648 | 540.9844 | 431.911
1864.1292 | 581.0629 | 461.7638 | 542.9871 | 432.2869
1865.1292 | 581.7706 | 460.6993 | 542.5319 | 432.7089
1866.1292 | 580.521 | 462.0871 | 540.8715 | 433.2556
1867.1292 | 579.9337 | 460.0526 | 537.5214 | 434.6458
1868.1292 | 581.6963 | 457.5389 | 546.0479 | 436.5285
1869.1292 | 582.6388 | 455.1487 | 555.0788 | 437.483
1870.1292 | 582.1928 | 453.1238 | 556.1305 | 436.4076
1871.1292 | 582.4045 | 450.5467 | 550.4427 | 435.6701
1872.1292 | 580.6701 | 449.8197 | 546.7796 | 433.8017
1873.1448 | 579.8164 | 449.0566 | 544.8126 | 433.4795
1874.1448 | 579.3479 | 447.2802 | 542.8393 | 433.4566
1875.1292 | 580.2364 | 446.3567 | 544.1787 | 433.1485
1876.1292 | 580.8097 | 448.6187 | 548.5122 | 432.5691
1877.1448 | 580.4305 | 448.4523 | 546.9615 | 432.0068
1878.1292 | 581.7388 | 451.3042 | 543.3921 | 431.3697
1879.1448 | 581.2982 | 452.4034 | 542.8947 | 433.9158
1880.1292 | 580.0612 | 453.5999 | 542.9126 | 432.3559
1881.1292 | 579.6804 | 452.431 | 543.566 | 431.9505
1882.1292 | 580.2269 | 450.8828 | 544.7454 | 431.5615
1883.1292 | 582.067 | 453.1762 | 547.4889 | 430.9209
1884.1292 | 582.613 | 453.1273 | 547.6857 | 432.21
1885.1292 | 581.7996 | 453.43 | 543.6162 | 432.957
1886.1292 | 580.9318 | 453.8023 | 544.0814 | 432.7632
1887.1292 | 580.8491 | 453.4182 | 541.6503 | 431.4594
1888.1292 | 580.1727 | 452.9431 | 537.6479 | 430.7231
1889.1292 | 579.416 | 452.7928 | 534.855 | 429.4617
1890.1292 | 579.4768 | 452.9499 | 532.919 | 428.6777
1891.1292 | 579.3942 | 454.5605 | 531.7753 | 429.2295
1892.1292 | 578.3859 | 455.206 | 531.5886 | 429.1903
1893.1292 | 578.2349 | 456.4876 | 530.7867 | 429.2381
1894.1292 | 577.817 | 457.9975 | 531.2754 | 430.6236
1895.1292 | 579.61 | 455.5891 | 530.3807 | 432.188
1896.1292 | 582.0942 | 455.0384 | 532.3674 | 433.5256
1897.1292 | 583.1853 | 455.5655 | 532.2543 | 433.447
1898.1292 | 583.0933 | 456.1421 | 534.2902 | 433.9637
1899.1292 | 584.4458 | 459.4258 | 535.5981 | 433.2463
1900.1292 | 584.7901 | 460.5897 | 538.992 | 432.8953
1901.1292 | 583.825 | 461.2358 | 536.9385 | 433.0131
1902.1292 | 583.329 | 458.9262 | 533.989 | 433.2788
1903.1292 | 587.6127 | 456.5809 | 534.8862 | 434.9291
1904.1292 | 589.0214 | 457.1832 | 536.7928 | 435.9677
1905.1292 | 587.7181 | 457.7262 | 533.35 | 435.3338
1906.1292 | 586.8289 | 456.0504 | 530.0918 | 436.6545
1907.1292 | 585.8907 | 455.886 | 530.4352 | 435.9218
1908.1292 | 584.2482 | 457.0533 | 531.9344 | 435.6644
1909.1292 | 583.8979 | 457.1154 | 530.5584 | 435.03
1910.1292 | 584.7039 | 458.6682 | 527.6169 | 433.1565
1911.1292 | 584.062 | 458.59 | 524.8609 | 430.4528
1912.1292 | 582.6624 | 458.653 | 524.6521 | 430.2445
1913.1292 | 582.7707 | 459.6316 | 524.97 | 430.9229
1914.1292 | 582.3169 | 461.3488 | 526.3119 | 431.2513
1915.1292 | 581.3059 | 462.0648 | 527.7467 | 431.4774
1916.1292 | 580.1134 | 460.9116 | 525.1504 | 430.9428
1917.1292 | 579.4601 | 459.1964 | 522.9439 | 429.6171
1918.1292 | 579.8699 | 458.2776 | 520.6331 | 427.3161
1919.1292 | 578.9664 | 457.3659 | 519.2289 | 427.3272
1920.1292 | 581.1241 | 456.8623 | 517.316 | 429.7187
1921.1292 | 588.7411 | 456.4644 | 523.3179 | 432.3167
1922.1292 | 590.5256 | 456.7854 | 524.9775 | 432.8831
1923.1292 | 592.3508 | 457.8971 | 525.1199 | 435.1537
1924.1292 | 593.537 | 458.2467 | 527.7087 | 435.4394
1925.1292 | 593.7312 | 460.9688 | 527.589 | 434.1206
1926.1292 | 591.7904 | 463.109 | 526.6743 | 432.2588
1927.1292 | 590.9585 | 463.6363 | 529.6989 | 430.8643
1928.1292 | 591.1605 | 465.2292 | 529.6191 | 430.7716
1929.1292 | 589.7975 | 465.2875 | 529.5921 | 430.6637
1930.1292 | 589.0866 | 464.3233 | 529.4218 | 430.8693
1931.1292 | 590.6062 | 464.0339 | 529.5309 | 431.3783
1932.1292 | 591.4339 | 465.2578 | 527.2615 | 432.7374
1933.1292 | 590.4014 | 466.494 | 527.0946 | 433.0541
1934.1292 | 588.8415 | 467.4735 | 526.7699 | 431.5561
1935.1292 | 592.9258 | 466.8375 | 523.0582 | 433.0678
1936.1292 | 598.8172 | 467.5582 | 525.7981 | 437.1291
1937.1292 | 599.1601 | 468.4368 | 530.4865 | 440.6319
1938.1292 | 598.0723 | 469.5717 | 532.4165 | 439.6444
1939.1292 | 596.4837 | 470.2516 | 530.5818 | 440.0769
1940.1292 | 599.9725 | 469.8589 | 532.3177 | 438.3841
1941.1292 | 598.2481 | 471.5387 | 533.5075 | 437.5069
1942.1292 | 596.3798 | 470.1189 | 532.6212 | 436.9263
1943.1292 | 595.5063 | 470.8611 | 530.5658 | 435.4786
1944.1292 | 592.9636 | 471.7413 | 529.0362 | 436.042
1945.1292 | 591.689 | 470.1441 | 530.607 | 435.5931
1946.1292 | 590.4193 | 468.6348 | 531.7933 | 435.046
1947.1292 | 590.2062 | 471.5435 | 529.572 | 435.3244
1948.1292 | 589.5385 | 472.9072 | 537.7787 | 437.196
1949.1292 | 590.996 | 471.5182 | 536.7154 | 438.7998
1950.1292 | 590.4857 | 468.7069 | 542.4887 | 438.8062
1951.1292 | 590.1487 | 466.7273 | 544.3682 | 438.1599
1952.1292 | 590.3202 | 465.8157 | 541.137 | 436.4066
1953.1292 | 590.6789 | 467.2004 | 538.3218 | 435.6915
1954.1292 | 589.8207 | 468.5112 | 541.4626 | 435.8261
1955.1292 | 590.5599 | 469.8996 | 538.4377 | 434.7851
1956.1292 | 589.2672 | 471.5591 | 533.5615 | 433.3755
1957.1292 | 589.9341 | 470.046 | 530.2572 | 431.1087
1958.1292 | 590.0905 | 472.3047 | 531.4926 | 429.9493
1959.1292 | 589.227 | 470.4512 | 527.7414 | 430.2091
1960.1292 | 588.0804 | 468.2825 | 523.779 | 429.4378
1961.1292 | 594.8795 | 467.0069 | 520.8495 | 430.3242
1962.1292 | 596.4785 | 464.3914 | 521.2099 | 430.5131
1963.1292 | 600.4251 | 464.4168 | 523.3325 | 432.5627
1964.1292 | 600.1862 | 461.7053 | 526.6687 | 436.654
1965.1292 | 600.9984 | 463.2299 | 525.7785 | 437.6642
1966.1292 | 599.4908 | 465.8491 | 528.7601 | 438.2166
1967.1292 | 598.8769 | 467.1615 | 526.6614 | 437.7218
1968.1292 | 598.003 | 468.1241 | 525.471 | 438.9167
1969.1292 | 601.6966 | 465.6657 | 525.5327 | 438.2266
1970.1292 | 603.3993 | 464.5216 | 530.3912 | 440.0602
1971.1292 | 602.5061 | 466.0815 | 531.6201 | 439.1197
1972.1292 | 600.7146 | 466.5041 | 529.5016 | 440.3335
1973.1292 | 599.9759 | 465.88 | 527.8228 | 438.435
1974.1292 | 599.1982 | 464.6861 | 526.9154 | 436.6231
1975.1292 | 599.2978 | 466.3778 | 529.1589 | 440.3497
1976.1292 | 598.8765 | 464.2132 | 525.1271 | 439.0101
1977.1292 | 602.5638 | 462.9765 | 522.1542 | 436.562
1978.1292 | 601.1073 | 463.5267 | 520.253 | 435.2954
1979.1292 | 601.0717 | 462.7634 | 519.767 | 435.0152
1980.1292 | 599.4504 | 463.3616 | 523.1157 | 433.4958
1981.1292 | 601.7705 | 465.0195 | 523.2187 | 435.6158
1982.1292 | 601.8393 | 463.6527 | 519.2642 | 435.3535
1983.1292 | 598.8878 | 462.4413 | 516.7586 | 434.1409
1984.1292 | 598.478 | 461.3188 | 516.2099 | 434.0222
1985.1292 | 599.0267 | 460.8567 | 516.2615 | 434.5166
1986.1292 | 599.1952 | 463.0078 | 519.8057 | 435.9386
1987.1292 | 597.5265 | 463.7881 | 520.118 | 436.9559
1988.1292 | 595.3153 | 463.285 | 520.2109 | 435.5152
1989.1292 | 595.4854 | 462.7979 | 518.4149 | 434.9786
1990.1292 | 593.4407 | 462.0587 | 515.3472 | 434.3351
1991.1292 | 593.0612 | 461.2744 | 515.0203 | 433.2408
1992.1292 | 594.4234 | 460.5568 | 516.6417 | 433.8897
1993.1292 | 593.5708 | 461.0893 | 521.2411 | 433.7757
1994.1292 | 592.7566 | 460.7436 | 522.7146 | 433.3003
1995.1292 | 592.3994 | 461.0957 | 522.4906 | 432.9726
1996.1292 | 591.0003 | 460.5684 | 520.4539 | 432.6805
1997.1292 | 591.5227 | 459.5244 | 523.3913 | 431.6294
1998.1292 | 593.9843 | 459.1934 | 525.2003 | 431.6887
1999.1292 | 595.6329 | 458.5446 | 527.9886 | 432.8604
2000.1292 | 595.5744 | 459.1897 | 526.9479 | 431.7771
2001.1292 | 595.4818 | 459.5086 | 527.9814 | 431.5112
2002.1292 | 595.2062 | 458.1821 | 530.859 | 430.3358
2003.1292 | 595.5114 | 458.5899 | 534.6008 | 429.4982
2004.1292 | 594.7606 | 458.7453 | 533.7728 | 429.8722
2005.1292 | 594.7898 | 459.4301 | 533.3342 | 429.9657
2006.1292 | 594.4669 | 458.5002 | 535.0207 | 429.4814
2007.1292 | 593.2433 | 459.415 | 535.3101 | 430.4204
2008.1292 | 593.8096 | 459.5327 | 532.8764 | 429.6136
2009.1292 | 595.0631 | 461.8625 | 532.6063 | 430.0251
2010.1292 | 595.0293 | 462.7783 | 530.5343 | 429.4531
2011.1292 | 595.3095 | 465.6064 | 532.9283 | 429.6629
2012.1292 | 594.7218 | 466.5634 | 531.2695 | 429.4403
2013.1292 | 594.8506 | 468.2669 | 533.3682 | 430.2137
2014.1292 | 594.2978 | 467.9722 | 532.1408 | 430.3061
2015.1292 | 594.3675 | 471.0671 | 534.0962 | 430.638
2016.1292 | 593.5525 | 470.3234 | 534.3514 | 430.7593
2017.1292 | 592.4752 | 471.2343 | 532.73 | 431.0157
2018.1292 | 596.8018 | 471.7404 | 537.5837 | 431.1175
2019.1292 | 598.3672 | 470.2974 | 539.2971 | 431.5765
2020.1292 | 599.6412 | 470.5645 | 540.2447 | 430.9067
2021.1292 | 603.0578 | 470.6898 | 540.566 | 430.868
2022.1292 | 604.2225 | 471.3718 | 541.1872 | 431.8591
2023.1292 | 605.9971 | 470.9754 | 540.2258 | 433.1123
2024.1292 | 608.0951 | 470.2349 | 540.225 | 433.6012
2025.1292 | 609.0613 | 470.3026 | 542.0227 | 435.0302
2026.1292 | 612.4063 | 472.1401 | 541.3878 | 438.0373
2027.1292 | 613.8207 | 471.531 | 538.0934 | 438.9779
2028.1292 | 613.0983 | 470.4083 | 537.2711 | 439.4921
2029.1292 | 613.8507 | 468.6595 | 538.1173 | 439.0162
2030.1292 | 611.9151 | 468.0662 | 540.7777 | 440.1393
2031.1292 | 609.6367 | 470.4857 | 540.7291 | 441.4455
2032.1292 | 608.9451 | 469.3154 | 539.2428 | 440.4635
2033.1292 | 607.9493 | 469.1606 | 539.4676 | 440.7321
2034.1292 | 607.3486 | 469.8529 | 536.9937 | 439.9082
2035.1292 | 608.2588 | 471.3464 | 534.5789 | 440.1815
2036.1292 | 607.1523 | 472.5889 | 535.5353 | 439.5393
2037.1292 | 606.6241 | 470.0524 | 533.7489 | 439.508
2038.1292 | 606.5674 | 468.8818 | 535.7228 | 440.1154
2039.1292 | 610.0397 | 467.4869 | 534.6601 | 439.3899
2040.1292 | 609.2648 | 466.31 | 537.2527 | 441.0219
2041.1292 | 608.5638 | 466.7172 | 533.5099 | 441.359
2042.1292 | 606.8279 | 466.6154 | 530.47 | 439.6052
2043.1292 | 605.1263 | 468.9548 | 528.9403 | 438.9149
2044.1292 | 604.401 | 468.2806 | 530.0299 | 438.1147
2045.1292 | 605.6899 | 467.3241 | 532.6119 | 437.0444
2046.1292 | 606.6162 | 468.7585 | 534.3952 | 438.3721
2047.1292 | 605.69 | 470.4461 | 532.7551 | 438.45
2048.1292 | 604.1011 | 469.734 | 531.0531 | 436.8955
2049.1292 | 602.8604 | 469.4886 | 529.3985 | 435.5234
2050.1292 | 601.4206 | 467.8717 | 528.0326 | 433.9309
2051.1292 | 600.5973 | 467.8815 | 528.2494 | 434.275
2052.1292 | 599.8621 | 468.1853 | 527.4872 | 433.8892
2053.1292 | 599.3925 | 467.9845 | 525.3772 | 432.2616
2054.1292 | 600.4792 | 467.2541 | 524.7857 | 431.0159
2055.1292 | 600.0922 | 467.41 | 522.3189 | 430.0846
2056.1292 | 600.2886 | 467.0192 | 519.7656 | 428.9941
2057.1292 | 599.6193 | 465.3174 | 517.4452 | 428.6151
2058.1292 | 600.1937 | 466.7926 | 518.2761 | 429.2584
2059.1292 | 601.1399 | 465.2654 | 527.2277 | 430.0946
2060.1292 | 600.7369 | 465.6932 | 529.6661 | 432.4889
2061.1292 | 599.3744 | 466.2574 | 529.6135 | 432.2355
2062.1292 | 599.0152 | 465.8692 | 530.7772 | 431.9926
2063.1292 | 599.0733 | 465.574 | 533.0809 | 431.6932
2064.1292 | 599.6263 | 465.4299 | 530.2114 | 430.3188
2065.1292 | 600.8768 | 466.798 | 531.5922 | 429.9191
2066.1292 | 602.3171 | 468.9217 | 528.4438 | 428.9861
2067.1292 | 602.4915 | 468.7952 | 527.0768 | 429.2091
2068.1292 | 605.1628 | 468.5283 | 526.8776 | 429.2315
2069.1292 | 605.3807 | 469.9314 | 527.4198 | 429.2466
2070.1292 | 605.6165 | 470.6943 | 526.9373 | 429.2633
2071.1292 | 605.0549 | 470.9119 | 528.0373 | 428.8032
2072.1292 | 605.3164 | 470.8154 | 526.7349 | 427.4413
2073.1292 | 604.9213 | 470.276 | 526.0839 | 427.7615
2074.1292 | 606.9757 | 469.3793 | 524.6319 | 429.7278
2075.1292 | 607.4397 | 469.7458 | 525.7089 | 431.2054
2076.1292 | 606.7086 | 468.6003 | 529.8495 | 431.797
2077.1292 | 604.4516 | 467.314 | 534.218 | 431.9232
2078.1292 | 603.6349 | 466.185 | 531.1513 | 433.6679
2079.1292 | 602.0214 | 465.008 | 530.2634 | 434.0618
2080.1292 | 600.5482 | 465.6636 | 528.5584 | 433.6723
2081.1292 | 600.2908 | 465.8932 | 525.0817 | 433.1894
2082.1292 | 599.3045 | 463.9675 | 520.7058 | 431.9347
2083.1292 | 599.2582 | 462.8751 | 517.971 | 430.2576
2084.1292 | 599.0051 | 462.4585 | 515.7991 | 429.5354
2085.1292 | 597.7855 | 461.4715 | 514.9539 | 429.4364
2086.1292 | 597.4269 | 460.7978 | 521.1783 | 431.0765
2087.1292 | 598.3423 | 462.3742 | 520.7546 | 429.6154
2088.1292 | 602.4582 | 462.4883 | 518.534 | 428.7172
2089.1292 | 604.1185 | 461.1355 | 515.8626 | 428.3602
2090.1292 | 602.7403 | 461.5545 | 512.9822 | 426.7974
2091.1292 | 603.8383 | 462.7945 | 513.3002 | 426.805
2092.1292 | 603.8339 | 461.6116 | 514.582 | 426.6206
2093.1292 | 604.6808 | 461.4431 | 514.2966 | 426.7926
2094.1292 | 603.6841 | 462.7358 | 514.7938 | 427.8113
2095.1292 | 602.0745 | 460.7681 | 513.8901 | 426.9109
2096.1292 | 601.7284 | 461.0941 | 513.355 | 427.6238
2097.1292 | 600.9855 | 460.0472 | 516.3667 | 427.5154
2098.1292 | 601.7697 | 459.9087 | 516.6639 | 427.4005
2099.1292 | 602.1935 | 459.7835 | 517.708 | 427.0548
2100.1292 | 602.9443 | 461.4724 | 518.5484 | 427.7994
2101.1292 | 603.4871 | 461.8403 | 516.644 | 427.4361
2102.1292 | 603.3092 | 461.4026 | 518.6244 | 427.8975
2103.1292 | 602.5422 | 462.197 | 518.9413 | 429.2638
2104.1292 | 602.4134 | 460.8423 | 520.3311 | 429.2547
2105.1292 | 603.59 | 460.492 | 519.1597 | 429.053
2106.1292 | 602.1168 | 460.5118 | 517.1582 | 427.9579
2107.1292 | 600.0168 | 460.775 | 516.2526 | 427.5192
2108.1292 | 599.1764 | 461.3433 | 516.443 | 427.1519
2109.1292 | 597.4831 | 462.0311 | 517.6812 | 427.5976
2110.1292 | 596.2174 | 461.2147 | 515.1809 | 427.3104
2111.1292 | 596.4014 | 461.1771 | 520.6723 | 427.0347
2112.1292 | 594.9762 | 461.4449 | 518.3025 | 429.3148
2113.1292 | 594.9001 | 461.3343 | 516.2883 | 428.7249
2114.1292 | 595.2305 | 461.7915 | 516.8226 | 427.3517
2115.1292 | 597.1009 | 462.8592 | 514.4292 | 426.656
2116.1292 | 595.9656 | 462.9254 | 512.9536 | 427.3319
2117.1292 | 595.0336 | 463.135 | 512.788 | 427.4614
2118.1292 | 594.5012 | 465.1472 | 511.0465 | 428.3346
2119.1448 | 595.9143 | 463.1207 | 511.0893 | 428.1449
2120.1292 | 598.3751 | 462.3806 | 510.4559 | 427.4219
2121.1448 | 601.7219 | 461.0187 | 510.7931 | 428.5539
2122.1292 | 605.3868 | 459.3881 | 510.4096 | 428.6801
2123.1448 | 606.0502 | 462.654 | 509.9672 | 429.3652
2124.1292 | 607.6906 | 462.7686 | 509.614 | 427.9912
2125.1448 | 609.2531 | 466.7582 | 508.6866 | 428.4018
2126.1292 | 609.0144 | 484.4103 | 507.3172 | 428.7953
2127.1292 | 607.7938 | 483.1475 | 505.7189 | 427.7852
2128.1292 | 609.1512 | 480.7306 | 505.1665 | 428.1137
2129.1292 | 609.3374 | 477.2704 | 506.8715 | 428.3741
2130.1292 | 610.0861 | 473.0101 | 508.423 | 428.0804
2131.1292 | 616.4096 | 469.2962 | 508.2641 | 428.5174
2132.1292 | 617.2478 | 466.7764 | 509.0721 | 429.8551
2133.1292 | 616.6413 | 465.4112 | 509.3464 | 430.4841
2134.1292 | 616.178 | 463.3582 | 509.988 | 430.6691
2135.1292 | 615.0976 | 462.3623 | 508.5183 | 431.1844
2136.1292 | 615.0018 | 464.1414 | 508.5874 | 432.7177
2137.1292 | 614.688 | 464.9729 | 507.4777 | 432.151
2138.1292 | 614.0015 | 463.9949 | 505.1721 | 432.4199
2139.1292 | 612.8019 | 463.5439 | 504.851 | 433.2626
2140.1292 | 613.6572 | 463.1578 | 503.2244 | 434.9524
2141.1292 | 612.2681 | 463.7994 | 511.2519 | 435.6938
2142.1292 | 610.0816 | 466.442 | 512.9059 | 436.6736
2143.1292 | 608.8536 | 467.0848 | 512.5309 | 436.7505
2144.1292 | 607.65 | 467.1691 | 512.1015 | 436.2006
2145.1292 | 608.0401 | 468.967 | 511.9701 | 436.2622
2146.1292 | 611.9681 | 468.0908 | 512.3596 | 437.2254
2147.1292 | 614.7691 | 466.3443 | 511.1193 | 437.6713
2148.1292 | 615 | 465.0417 | 509.3169 | 437.0645
2149.1292 | 615.9682 | 464.7902 | 509.012 | 437.1779
2150.1292 | 615.4793 | 464.709 | 508.1407 | 436.821
2151.1292 | 615.0506 | 464.7184 | 507.551 | 435.4782
2152.1292 | 614.0536 | 464.1083 | 507.6966 | 435.6422
2153.1292 | 613.3501 | 464.5525 | 506.8625 | 435.389
2154.1292 | 613.6477 | 464.0333 | 507.6681 | 436.0133
2155.1292 | 614.1257 | 465.2624 | 509.3736 | 436.7561
2156.1292 | 615.367 | 465.0205 | 512.2975 | 437.03
2157.1292 | 614.3119 | 463.0771 | 513.2176 | 436.2239
2158.1292 | 612.5062 | 463.4754 | 511.9802 | 436.2079
2159.1292 | 611.305 | 462.6295 | 511.539 | 434.7534
2160.1292 | 611.1499 | 462.5671 | 511.4527 | 433.349
2161.1292 | 612.1632 | 462.7584 | 509.4949 | 433.6979
2162.1292 | 610.4369 | 462.2659 | 521.821 | 433.5967
2163.1292 | 612.8087 | 459.8034 | 518.884 | 433.7055
2164.1292 | 611.1635 | 461.4505 | 519.3971 | 433.5908
2165.1292 | 609.1372 | 462.3815 | 519.9337 | 434.9502
2166.1292 | 609.8206 | 460.7851 | 517.8965 | 435.7143
2167.1292 | 612.3289 | 460.12 | 518.4347 | 436.6006
2168.1292 | 614.2157 | 461.263 | 519.5276 | 437.8047
2169.1292 | 614.2396 | 461.2047 | 520.6595 | 439.5883
2170.1292 | 614.9165 | 460.0247 | 519.3382 | 440.6289
2171.1292 | 612.7085 | 460.8628 | 521.0474 | 440.6934
2172.1292 | 609.9622 | 460.9469 | 522.2866 | 439.6146
2173.1292 | 608.7335 | 461.2719 | 520.4658 | 439.6023
2174.1292 | 609.2602 | 461.0323 | 519.7285 | 438.9905
2175.1292 | 608.641 | 460.0119 | 517.6759 | 438.6703
2176.1292 | 607.1166 | 458.7018 | 517.4253 | 438.5805
2177.1292 | 607.6338 | 460.5997 | 516.7268 | 440.3922
2178.1292 | 609.9561 | 459.1109 | 515.1071 | 442.5038
2179.1292 | 610.0256 | 458.5552 | 514.9548 | 442.5136
2180.1292 | 611.0053 | 457.744 | 515.3689 | 442.4531
2181.1292 | 611.4103 | 458.3461 | 516.9352 | 440.565
2182.1292 | 610.4349 | 461.2399 | 516.915 | 440.4941
2183.1292 | 609.9139 | 460.7652 | 518.4437 | 441.5441
2184.1292 | 608.3237 | 461.1861 | 516.3818 | 441.9936
2185.1292 | 607.5912 | 462.0388 | 515.4011 | 442.3108
2186.1292 | 606.6583 | 462.8448 | 515.1425 | 443.5578
2187.1292 | 605.5167 | 462.2949 | 513.8374 | 442.2889
2188.1292 | 605.2376 | 462.3428 | 513.7912 | 442.8595
2189.1292 | 604.6736 | 462.4458 | 514.0633 | 441.7758
2190.1292 | 604.6403 | 462.8535 | 514.5576 | 442.4549
2191.1292 | 604.7729 | 461.4356 | 513.3356 | 441.2669
2192.1292 | 605.3126 | 460.1429 | 526.112 | 440.5193
2193.1292 | 604.8642 | 461.4263 | 528.8894 | 441.1394
2194.1292 | 602.7115 | 460.3818 | 526.575 | 441.2303
2195.1292 | 602.1275 | 460.3279 | 526.3179 | 441.9085
2196.1292 | 602.0488 | 458.8614 | 525.5133 | 443.1979
2197.1292 | 602.507 | 460.0504 | 526.4351 | 443.8566
2198.1292 | 602.6894 | 459.7692 | 524.4419 | 444.0741
2199.1292 | 601.5926 | 460.4303 | 523.3618 | 445.6684
2200.1292 | 600.955 | 460.4223 | 521.3144 | 447.4547
2201.1292 | 602.8941 | 459.8386 | 521.0171 | 447.3804
2202.1292 | 603.1522 | 458.4509 | 519.289 | 449.5733
2203.1292 | 603.4872 | 458.3594 | 519.5774 | 449.95
2204.1292 | 604.9512 | 456.5557 | 517.484 | 448.6352
2205.1292 | 605.3028 | 457.9435 | 519.6751 | 448.8486
2206.1292 | 606.3229 | 457.3745 | 518.582 | 450.1982
2207.1292 | 607.4324 | 455.4413 | 515.4751 | 450.5444
2208.1292 | 608.6255 | 453.5313 | 512.9485 | 450.3019
2209.1292 | 608.5474 | 453.2627 | 513.0032 | 451.4908
2210.1292 | 608.1952 | 453.0444 | 512.9882 | 453.4138
2211.1292 | 607.6481 | 452.1175 | 513.4005 | 453.2277
2212.1292 | 606.1279 | 452.2511 | 512.731 | 453.0536
2213.1292 | 604.4244 | 451.2377 | 512.3473 | 451.7459
2214.1292 | 604.5458 | 449.6943 | 512.1822 | 452.6814
2215.1292 | 605.3593 | 448.5533 | 512.1546 | 453.9795
2216.1292 | 607.003 | 449.1502 | 511.3646 | 456.5325
2217.1292 | 607.6624 | 447.9989 | 508.5545 | 456.2476
2218.1292 | 608.2498 | 448.7175 | 507.8732 | 458.347
2219.1292 | 610.1374 | 449.2269 | 507.2597 | 458.4379
2220.1292 | 609.5169 | 449.9759 | 509.225 | 458.2927
2221.1292 | 609.7715 | 450.6811 | 509.9389 | 457.3064
2222.1292 | 608.3548 | 455.3269 | 512.498 | 460.0775
2223.1292 | 606.2326 | 457.5329 | 514.1297 | 463.2699
2224.1292 | 604.9421 | 458.7121 | 514.4212 | 463.0066
2225.1292 | 604.3686 | 460.6335 | 516.4083 | 463.4778
2226.1292 | 604.1437 | 459.3981 | 517.7041 | 462.1273
2227.1292 | 603.9566 | 459.3161 | 519.7027 | 461.8576
2228.1292 | 603.5763 | 459.9458 | 521.6126 | 462.6512
2229.1292 | 603.3094 | 462.1017 | 522.4983 | 464.2205
2230.1292 | 603.7676 | 462.8371 | 521.1404 | 464.3565
2231.1292 | 602.6683 | 463.092 | 522.6799 | 467.2464
2232.1292 | 603.2941 | 461.529 | 523.7588 | 467.3434
2233.1292 | 603.4535 | 461.8609 | 526.0173 | 467.824
2234.1292 | 604.1468 | 463.0336 | 527.0995 | 467.113
2235.1292 | 605.3746 | 463.2767 | 528.1553 | 469.3467
2236.1292 | 606.0532 | 464.3523 | 530.8896 | 470.1391
2237.1292 | 605.2533 | 465.8033 | 531.7824 | 468.9265
2238.1292 | 604.7392 | 465.1438 | 530.9707 | 468.3261
2239.1292 | 604.1372 | 466.3296 | 532.9028 | 468.9513
2240.1292 | 603.4902 | 466.3818 | 535.38 | 469.4077
2241.1292 | 603.7508 | 467.5554 | 537.6985 | 469.8246
2242.1292 | 604.5653 | 468.8024 | 539.3035 | 470.1786
2243.1292 | 603.9106 | 468.5568 | 538.9123 | 469.5611
2244.1292 | 603.7901 | 469.5366 | 539.0614 | 470.0139
2245.1292 | 603.1975 | 470.1757 | 539.982 | 471.3421
2246.1292 | 603.4083 | 470.7069 | 542.1751 | 470.9382
2247.1292 | 602.9926 | 472.2514 | 542.1055 | 470.6034
2248.1292 | 602.6716 | 471.9089 | 542.3699 | 470.2168
2249.1292 | 602.3554 | 471.6028 | 541.6012 | 471.1591
2250.1292 | 602.2712 | 471.1138 | 541.2429 | 472.1939
2251.1292 | 603.6433 | 471.5675 | 540.0307 | 470.8731
2252.1292 | 604.027 | 470.3357 | 546.2842 | 471.0501
2253.1292 | 604.6448 | 471.5867 | 545.1979 | 470.4867
2254.1292 | 605.0215 | 473.2284 | 546.7385 | 472.7266
2255.1292 | 605.9166 | 474.4504 | 546.9492 | 472.1526
2256.1292 | 606.94 | 476.1908 | 544.5294 | 471.2357
2257.1292 | 608.8991 | 477.8775 | 541.9449 | 470.3694
2258.1292 | 610.6141 | 480.0407 | 540.0371 | 468.857
2259.1292 | 611.3208 | 480.1305 | 537.4344 | 467.9619
2260.1292 | 612.2595 | 481.8419 | 536.3358 | 468.5225
2261.1292 | 613.6505 | 482.9112 | 540.035 | 470.2242
2262.1292 | 613.5396 | 485.468 | 542.2895 | 471.1881
2263.1292 | 613.1829 | 485.4291 | 543.1979 | 471.4934
2264.1292 | 612.2311 | 486.8449 | 544.891 | 470.3813
2265.1292 | 611.1264 | 489.0033 | 544.4627 | 471.3364
2266.1292 | 610.2902 | 490.278 | 545.469 | 472.9702
2267.1292 | 609.8305 | 491.2919 | 547.094 | 472.8676
2268.1292 | 609.2919 | 490.0722 | 549.8911 | 471.741
2269.1292 | 608.639 | 491.1207 | 550.2989 | 471.1205
2270.1292 | 608.2473 | 491.6888 | 548.044 | 470.4982
2271.1292 | 608.7392 | 491.0334 | 547.1807 | 469.989
2272.1292 | 609.308 | 491.0855 | 548.6482 | 471.3706
2273.1292 | 608.5528 | 491.6308 | 548.8285 | 471.7427
2274.1292 | 607.5136 | 490.0106 | 548.2731 | 470.9454
2275.1292 | 606.3648 | 489.7217 | 550.1874 | 471.7478
2276.1292 | 606.2092 | 489.7688 | 551.1582 | 473.2138
2277.1292 | 607.3903 | 494.0385 | 556.9913 | 474.8394
2278.1292 | 608.1135 | 492.4732 | 556.1785 | 474.0432
2279.1292 | 608.6337 | 492.8403 | 556.4859 | 474.5658
2280.1292 | 608.5296 | 495.1279 | 558.0126 | 475.3858
2281.1292 | 607.5552 | 494.4231 | 556.5803 | 473.9608
2282.1292 | 606.7345 | 492.9243 | 556.3794 | 472.5045
2283.1292 | 606.3287 | 493.156 | 565.7181 | 472.2111
2284.1292 | 606.1587 | 494.9797 | 568.0672 | 472.8054
2285.1292 | 606.3515 | 495.3558 | 567.2558 | 474.3618
2286.1292 | 606.6366 | 496.9318 | 569.7377 | 476.323
2287.1292 | 605.4599 | 497.7579 | 568.7764 | 477.4844
2288.1292 | 607.0575 | 496.0698 | 566.4619 | 477.8136
2289.1292 | 608.381 | 494.5387 | 562.6584 | 477.6869
2290.1292 | 609.5213 | 501.5197 | 566.219 | 478.4981
2291.1292 | 608.9637 | 498.8572 | 563.8244 | 476.5223
2292.1292 | 609.1099 | 499.0361 | 564.6605 | 477.6175
2293.1292 | 606.9368 | 498.1965 | 562.6167 | 478.0942
2294.1292 | 606.7053 | 496.4109 | 566.2603 | 478.711
2295.1292 | 607.3453 | 501.7447 | 574.536 | 478.0568
2296.1292 | 608.8098 | 505.0614 | 582.1167 | 480.2863
2297.1292 | 610.165 | 507.6978 | 587.7657 | 479.9827
2298.1292 | 610.9203 | 507.5143 | 587.8153 | 480.5211
2299.1292 | 610.086 | 507.5069 | 589.1589 | 498.0277
2300.1292 | 611.472 | 508.4546 | 593.9038 | 499.0294
2301.1292 | 609.457 | 508.527 | 598.3339 | 501.1472
2302.1292 | 608.2658 | 513.4415 | 599.2656 | 507.0512
2303.1292 | 607.2082 | 513.186 | 611.3321 | 505.9985
2304.1292 | 609.1516 | 511.8457 | 610.6609 | 507.501
2305.1292 | 609.6738 | 513.1455 | 612.6296 | 517.7216
2306.1292 | 610.2474 | 512.747 | 607.3596 | 516.1755
2307.1292 | 611.6102 | 514.0618 | 602.3998 | 517.1474
2308.1292 | 611.7058 | 514.3421 | 598.1141 | 523.0054
2309.1292 | 611.7044 | 513.5294 | 595.6519 | 520.3067
2310.1292 | 611.4094 | 517.0581 | 600.0311 | 522.3587
2311.1292 | 610.7847 | 515.3593 | 595.9238 | 520.4112
2312.1292 | 609.8652 | 514.8906 | 607.4137 | 519.3853
2313.1292 | 609.9367 | 514.0217 | 607.0599 | 527.0386
2314.1292 | 609.3623 | 513.3435 | 599.384 | 525.5762
2315.1292 | 610.0334 | 515.4653 | 600.1609 | 522.8234
2316.1292 | 609.4786 | 516.2127 | 595.6607 | 518.9291
2317.1292 | 609.0086 | 515.5307 | 591.9009 | 516.4814
2318.1292 | 608.1479 | 516.0225 | 588.8201 | 514.445
2319.1292 | 608.6278 | 515.7159 | 593.2302 | 515.1609
2320.1292 | 608.2957 | 517.5928 | 593.8315 | 514.0165
2321.1292 | 607.708 | 517.3102 | 610.7907 | 512.107
2322.1292 | 607.3077 | 518.1324 | 621.8541 | 507.6051
2323.1292 | 607.8056 | 519.2678 | 622.3042 | 510.9625
2324.1292 | 607.8203 | 521.109 | 625.4622 | 518.85
2325.1292 | 608.2664 | 521.6814 | 619.614 | 522.1948
2326.1292 | 607.8229 | 521.1467 | 612.0367 | 519.3715
2327.1292 | 607.1331 | 519.941 | 607.1775 | 518.6152
2328.1292 | 607.1111 | 521.4138 | 602.9798 | 515.7919
2329.1292 | 606.9227 | 520.9734 | 598.3068 | 512.4327
2330.1292 | 608.0442 | 519.6861 | 606.8236 | 511.7762
2331.1292 | 609.1935 | 520.0458 | 604.3227 | 510.4284
2332.1292 | 609.729 | 520.0014 | 600.0675 | 506.7006
2333.1292 | 609.3499 | 519.3871 | 593.98 | 505.2624
2334.1448 | 608.8281 | 516.9181 | 588.7009 | 505.5341
2335.1292 | 609.326 | 516.2105 | 586.9563 | 505.0701
2336.1292 | 609.0988 | 517.0784 | 585.2875 | 503.5806
2337.1448 | 608.6972 | 517.1267 | 582.4413 | 502.7952
2338.1292 | 608.1344 | 516.7104 | 579.6449 | 502.3268
2339.1292 | 608.4986 | 515.325 | 576.3986 | 500.0672
2340.1292 | 608.5505 | 514.5033 | 576.0982 | 499.4145
2341.1292 | 608.2833 | 514.3525 | 574.6814 | 501.9462
2342.1292 | 607.9322 | 513.7405 | 575.2832 | 501.4858
2343.1292 | 609.0979 | 511.6445 | 573.2003 | 500.4604
2344.1292 | 610.4181 | 514.4611 | 575.6994 | 498.8734
2345.1292 | 610.2541 | 514.3343 | 574.4539 | 501.1413
2346.1292 | 611.4623 | 515.8154 | 573.6344 | 502.9497
2347.1292 | 611.2798 | 517.9262 | 576.815 | 502.1189
2348.1292 | 610.7457 | 516.8479 | 575.7911 | 499.1965
2349.1292 | 610.8091 | 517.7016 | 580.3709 | 500.5936
2350.1292 | 610.1416 | 517.6331 | 581.7273 | 500.7289
2351.1292 | 610.1835 | 524.1465 | 589.9959 | 502.4253
2352.1292 | 610.7913 | 528.0272 | 590.8597 | 502.5224
2353.1292 | 613.6644 | 530.7704 | 592.1833 | 503.2538
2354.1292 | 614.3717 | 529.4619 | 590.107 | 503.0056
2355.1292 | 613.302 | 529.8025 | 588.7115 | 503.6672
2356.1292 | 613.5522 | 529.1155 | 587.8745 | 505.8815
2357.1292 | 613.4281 | 537.1146 | 595.4732 | 515.5559
2358.1292 | 615.0315 | 542.9216 | 597.9303 | 515.9925
2359.1292 | 614.9456 | 541.2543 | 594.6254 | 514.3264
2360.1292 | 615.6489 | 538.664 | 593.6733 | 514.3588
2361.1292 | 615.8333 | 540.1136 | 592.3566 | 513.5641
2362.1448 | 616.3273 | 538.5843 | 593.0438 | 514.7428
2363.1292 | 617.7496 | 551.943 | 592.6546 | 531.2429
2364.1448 | 616.2006 | 550.1209 | 590.8436 | 532.7645
2365.1292 | 617.2489 | 555.8017 | 590.7217 | 530.6918
2366.1448 | 616.9626 | 555.0344 | 586.5293 | 529.6208
2367.1292 | 616.9227 | 552.6522 | 583.2786 | 533.4391
2368.1292 | 616.9616 | 551.3011 | 579.8708 | 531.3266
2369.1292 | 616.0293 | 548.8076 | 576.2951 | 529.9256
2370.1292 | 615.9756 | 547.8573 | 580.5139 | 529.5607
2371.1292 | 616.5434 | 547.1422 | 585.072 | 532.112
2372.1292 | 616.0268 | 545.6634 | 581.2475 | 531.4307
2373.1292 | 616.2954 | 542.7823 | 576.456 | 528.7999
2374.1448 | 616.5276 | 539.0987 | 572.5529 | 526.0029
2375.1292 | 615.658 | 536.1756 | 569.7242 | 524.3866
2376.1292 | 615.0377 | 534.5319 | 569.2182 | 524.3009
2377.1292 | 615.1788 | 532.6832 | 572.885 | 521.8551
2378.1292 | 614.5591 | 531.5623 | 571.0843 | 522.6124
2379.1292 | 614.3348 | 535.9934 | 572.5702 | 523.5616
2380.1292 | 614.8483 | 534.8502 | 570.7754 | 522.9267
2381.1292 | 614.2714 | 534.1257 | 567.3856 | 520.8872
2382.1292 | 613.9292 | 532.7175 | 566.4098 | 520.2299
2383.1292 | 612.9948 | 531.3969 | 567.2019 | 520.7573
2384.1292 | 612.6884 | 534.9013 | 572.2956 | 521.1601
2385.1292 | 612.1718 | 536.1059 | 579.5638 | 525.2725
2386.1292 | 613.0071 | 537.6749 | 581.0692 | 526.6667
2387.1292 | 615.4087 | 540.8944 | 583.3531 | 531.0143
2388.1292 | 616.1652 | 541.5097 | 581.0371 | 529.4128
2389.1292 | 616.5832 | 542.5458 | 582.0809 | 530.7253
2390.1292 | 616.6013 | 541.4912 | 580.4249 | 530.5729
2391.1292 | 616.9146 | 539.575 | 580.0297 | 531.3603
2392.1292 | 617.6757 | 538.0464 | 579.47 | 531.1821
2393.1292 | 618.1041 | 538.3898 | 579.4704 | 532.6242
2394.1292 | 618.3644 | 537.7577 | 578.6853 | 532.1945
2395.1292 | 618.7499 | 536.2376 | 577.3974 | 531.098
2396.1292 | 618.7355 | 534.1092 | 575.9957 | 531.5551
2397.1448 | 619.1461 | 535.2119 | 578.0585 | 532.1307
2398.1292 | 619.3286 | 536.5355 | 577.593 | 529.4419
2399.1292 | 619.1181 | 535.0956 | 582.9325 | 527.3986
2400.1292 | 619.3576 | 540.4267 | 598.9954 | 525.1114
2401.1292 | 618.9472 | 546.941 | 600.2882 | 524.9915
2402.1292 | 618.0861 | 552.3347 | 603.7239 | 527.8745
2403.1292 | 618.1188 | 562.1237 | 602.4723 | 534.6428
2404.1292 | 616.6068 | 565.3177 | 599.9277 | 533.9215
2405.1292 | 615.1288 | 566.0508 | 597.6146 | 534.9384
2406.1292 | 614.6426 | 566.5184 | 598.9288 | 535.2562
2407.1292 | 614.8544 | 568.1758 | 608.1496 | 537.0672
2408.1292 | 615.0618 | 571.3952 | 606.2374 | 539.6584
2409.1292 | 616.1258 | 574.7575 | 607.5138 | 539.3831
2410.1292 | 616.4936 | 573.129 | 607.902 | 542.0302
2411.1292 | 617.299 | 571.2792 | 604.233 | 556.7864
2412.1292 | 618.5495 | 575.9067 | 607.8709 | 569.8641
2413.1292 | 619.0695 | 576.6024 | 605.7422 | 565.3663
2414.1292 | 619.1718 | 573.9046 | 600.0365 | 561.7865
2415.1292 | 619.3489 | 571.2785 | 595.8243 | 558.4957
2416.1292 | 619.642 | 568.9492 | 599.2724 | 553.2394
2417.1292 | 618.8238 | 567.2504 | 595.9348 | 551.9189
2418.1292 | 619.4 | 565.4383 | 593.1486 | 548.6323
2419.1292 | 619.3701 | 569.3137 | 595.5813 | 548.02
2420.1292 | 619.6569 | 566.7809 | 595.1874 | 547.64
2421.1292 | 620.5589 | 568.9347 | 594.3716 | 547.2724
2422.1292 | 620.9851 | 568.5011 | 592.6161 | 545.2201
2423.1292 | 620.4154 | 564.2213 | 589.2206 | 545.5995
2424.1292 | 620.5498 | 562.1226 | 587.5724 | 542.3359
2425.1292 | 620.7054 | 558.3384 | 586.0446 | 542.4489
2426.1292 | 620.9697 | 557.1858 | 584.3877 | 542.1838
2427.1292 | 619.873 | 554.054 | 582.0592 | 539.5346
2428.1292 | 619.7683 | 552.9659 | 580.5263 | 537.7158
2429.1292 | 620.4083 | 551.9197 | 580.7284 | 539.6182
2430.1292 | 620.6203 | 552.9991 | 583.4922 | 538.4441
2431.1292 | 621.7573 | 555.1183 | 584.3607 | 551.3647
2432.1292 | 621.3869 | 554.599 | 583.9138 | 550.3702
2433.1292 | 621.5347 | 552.6899 | 581.0659 | 547.0539
2434.1292 | 622.1213 | 551.8533 | 580.771 | 545.9945
2435.1292 | 622.3638 | 550.622 | 577.3329 | 544.384
2436.1292 | 622.8398 | 551.0623 | 584.8059 | 553.1113
2437.1292 | 622.8598 | 550.0702 | 588.7849 | 550.9868
2438.1292 | 623.5789 | 556.9381 | 588.9464 | 549.6165
2439.1292 | 624.1462 | 560.0199 | 590.466 | 550.3243
2440.1292 | 623.8535 | 563.5645 | 591.6842 | 548.3656
2441.1292 | 624.8016 | 567.7152 | 593.9974 | 555.5888
2442.1292 | 625.4628 | 564.8497 | 590.4283 | 554.0646
2443.1292 | 624.9972 | 563.5785 | 587.6148 | 549.9245
2444.1292 | 624.4554 | 563.604 | 585.5376 | 563.6546
2445.1292 | 624.4011 | 561.4313 | 585.7313 | 581.5958
2446.1292 | 624.6531 | 562.7959 | 585.7618 | 589.3354
2447.1292 | 625.9427 | 561.665 | 585.6242 | 586.6307
2448.1292 | 626.3461 | 562.5975 | 585.3926 | 582.9703
2449.1292 | 626.4595 | 565.8115 | 588.0551 | 578.7341
2450.1292 | 626.8968 | 566.2171 | 587.7705 | 575.0988
2451.1292 | 629.081 | 567.3177 | 588.0241 | 575.0574
2452.1292 | 629.1111 | 565.6835 | 588.7501 | 572.9443
2453.1292 | 629.2135 | 567.2566 | 586.8822 | 568.7876
2454.1292 | 626.8036 | 579.1438 | 589.8683 | 567.8544
2455.1292 | 627.0867 | 579.7526 | 595.3825 | 576.0001
2456.1292 | 627.7029 | 584.5944 | 600.806 | 575.2336
2457.1448 | 628.2751 | 586.6505 | 598.7653 | 569.6245
2458.1292 | 627.8949 | 583.8639 | 598.278 | 567.1966
2459.1292 | 627.5801 | 580.8721 | 594.1532 | 574.8554
2460.1292 | 628.1089 | 578.4012 | 595.6268 | 592.2439
2461.1292 | 628.7542 | 578.7795 | 598.4473 | 600.4721
2462.1292 | 627.1004 | 575.4114 | 595.9705 | 595.2976
2463.1292 | 626.4863 | 577.3877 | 603.8466 | 601.0302
2464.1292 | 626.0752 | 580.2623 | 598.0351 | 597.2016
2465.1292 | 626.8945 | 581.0075 | 602.9409 | 599.0338
2466.1292 | 626.7571 | 583.7113 | 604.4763 | 593.9975
2467.1292 | 627.6925 | 583.8178 | 603.8026 | 601.7432
2468.1292 | 628.6804 | 581.277 | 599.6918 | 598.8089
2469.1292 | 628.9829 | 578.5731 | 596.5779 | 595.4642
2470.1292 | 630.5509 | 578.5677 | 597.185 | 593.0969
2471.1448 | 630.7493 | 577.5095 | 593.4396 | 588.5714
2472.1292 | 631.7923 | 578.1513 | 591.4565 | 582.6294
2473.1292 | 631.7795 | 579.6519 | 590.7772 | 578.5199
2474.1292 | 631.8353 | 578.2905 | 588.6516 | 577.1896
2475.1292 | 632.0413 | 577.8778 | 587.3623 | 576.8259
2476.1292 | 630.8075 | 577.4976 | 591.4732 | 578.1986
2477.1292 | 630.2694 | 579.3151 | 592.0781 | 579.2299
2478.1292 | 631.3244 | 587.6008 | 591.4774 | 579.4927
2479.1292 | 632.2187 | 593.3154 | 593.9181 | 576.1235
2480.1292 | 632.2825 | 592.9996 | 595.011 | 576.4594
2481.1292 | 632.6367 | 592.2913 | 595.3811 | 585.1769
2482.1292 | 632.6415 | 588.2501 | 593.5448 | 583.1205
2483.1292 | 631.4348 | 585.4199 | 592.5363 | 583.0259
2484.1292 | 631.3578 | 584.0053 | 592.4867 | 582.0033
2485.1292 | 628.5397 | 588.1003 | 591.0063 | 580.6981
2486.1292 | 628.2026 | 586.3575 | 589.1822 | 577.0776
2487.1448 | 628.7724 | 590.1193 | 588.3288 | 572.8259
2488.1292 | 629.2629 | 587.6106 | 586.8085 | 571.4372
2489.1292 | 629.8195 | 583.812 | 586.7631 | 569.9436
2490.1292 | 629.8546 | 582.6065 | 585.8417 | 571.0315
2491.1292 | 629.8809 | 578.5209 | 584.4782 | 572.2965
2492.1292 | 630.244 | 578.2256 | 586.876 | 570.6767
2493.1292 | 630.7766 | 579.2089 | 589.8525 | 572.4538
2494.1292 | 631.4891 | 577.4564 | 589.6242 | 571.2887
2495.1292 | 631.2324 | 577.075 | 589.57 | 569.7494
2496.1292 | 633.8875 | 575.2574 | 588.7289 | 569.5212
2497.1292 | 633.882 | 575.6734 | 587.8227 | 568.7403
2498.1292 | 633.1806 | 574.1415 | 589.3403 | 567.3457
2499.1292 | 634.1482 | 577.6392 | 594.0701 | 573.8097
2500.1292 | 635.3721 | 581.7719 | 595.7853 | 573.0299
2501.1292 | 635.091 | 583.9804 | 594.4052 | 571.1909
2502.1292 | 635.0913 | 584.7191 | 598.6376 | 575.3143
2503.1292 | 635.8241 | 587.4676 | 597.8428 | 577.162
2504.1292 | 635.8034 | 586.758 | 597.4478 | 575.5943
2505.1292 | 635.7733 | 588.6827 | 597.035 | 575.1293
2506.1292 | 636.5209 | 588.5431 | 597.141 | 574.5453
2507.1292 | 636.7058 | 589.1509 | 598.6121 | 575.2396
2508.1292 | 637.2239 | 589.5946 | 599.6036 | 578.0309
2509.1292 | 637.0666 | 589.4456 | 599.4337 | 578.9706
2510.1292 | 637.2528 | 587.7981 | 598.7024 | 579.2659
2511.1292 | 637.2849 | 593.1114 | 597.359 | 584.7692
2512.1292 | 637.3588 | 590.9974 | 598.3178 | 584.2447
2513.1292 | 636.4295 | 591.4792 | 599.3315 | 581.0402
2514.1292 | 636.4191 | 593.5402 | 600.4645 | 593.5672
2515.1292 | 635.9751 | 591.7181 | 600.2247 | 608.1795
2516.1292 | 636.2979 | 595.4442 | 600.6097 | 607.0896
2517.1292 | 635.9591 | 599.0357 | 601.9569 | 599.7092
2518.1292 | 636.1004 | 596.5361 | 613.9131 | 596.5144
2519.1292 | 636.2279 | 594.2952 | 610.6098 | 605.9386
2520.1292 | 635.3342 | 591.2818 | 606.4744 | 606.2967
2521.1292 | 634.7287 | 594.542 | 606.3123 | 610.7985
2522.1292 | 635.2547 | 598.4232 | 617.4776 | 610.4259
2523.1292 | 636.691 | 597.0281 | 618.8246 | 608.2608
2524.1292 | 636.4702 | 596.8654 | 616.6028 | 603.8625
2525.1292 | 637.6054 | 596.3966 | 613.7826 | 605.9504
2526.1292 | 637.2694 | 599.2429 | 612.536 | 604.3782
2527.1292 | 635.8388 | 598.6155 | 608.6647 | 599.6881
2528.1292 | 636.4839 | 604.2149 | 614.7486 | 597.6208
2529.1292 | 635.3816 | 605.8055 | 622.294 | 609.6427
2530.1292 | 635.4697 | 612.6508 | 631.5748 | 605.9404
2531.1292 | 635.0437 | 611.0127 | 627.6685 | 605.409
2532.1292 | 635.0657 | 608.2109 | 623.0517 | 604.1636
2533.1292 | 634.5751 | 605.8046 | 618.4671 | 599.7526
2534.1292 | 634.5112 | 601.1999 | 614.0792 | 594.7038
2535.1292 | 635.4927 | 599.8277 | 612.4939 | 589.8247
2536.1292 | 636.0894 | 598.9589 | 611.485 | 588.9411
2537.1292 | 636.0834 | 597.4827 | 614.3024 | 595.3334
2538.1292 | 637.0476 | 596.1392 | 611.5196 | 595.0171
2539.1292 | 638.2679 | 600.9169 | 609.2017 | 596.2168
2540.1292 | 638.6593 | 605.1497 | 612.0492 | 594.9902
2541.1292 | 638.7827 | 606.7464 | 609.6327 | 594.2064
2542.1292 | 639.6551 | 607.1561 | 605.8154 | 588.8929
2543.1292 | 638.7596 | 606.7106 | 604.4206 | 590.1749
2544.1292 | 638.7149 | 602.8765 | 602.249 | 593.0159
2545.1292 | 639.0145 | 608.8636 | 604.1654 | 592.1325
2546.1292 | 639.6331 | 605.1085 | 602.5692 | 588.4225
2547.1292 | 639.2558 | 603.9794 | 602.2286 | 597.7711
2548.1292 | 640.1384 | 604.4361 | 603.061 | 598.4529
2549.1292 | 640.06 | 604.1196 | 604.7777 | 600.7903
2550.1292 | 640.1088 | 603.1001 | 603.5239 | 615.4858
2551.1292 | 639.8984 | 602.5525 | 603.1019 | 619.8649
2552.1292 | 639.8165 | 601.0251 | 600.9473 | 614.7339
2553.1292 | 640.0654 | 604.2281 | 600.508 | 612.4836
2554.1292 | 639.6603 | 614.526 | 612.4582 | 622.9927
2555.1292 | 640.2692 | 627.5392 | 619.5242 | 623.7664
2556.1292 | 641.1733 | 624.1111 | 614.4127 | 621.6345
2557.1292 | 640.5155 | 620.5562 | 611.253 | 628.1235
2558.1292 | 640.467 | 617.1954 | 606.388 | 627.2766
2559.1292 | 640.2752 | 619.2144 | 602.257 | 618.0065
2560.1292 | 640.2983 | 613.6787 | 600.3038 | 611.358
2561.1292 | 639.7192 | 618.1288 | 600.4183 | 605.1877
2562.1292 | 640.8636 | 618.2681 | 601.1344 | 605.0762
2563.1292 | 641.2541 | 619.7743 | 602.5996 | 603.9624
2564.1292 | 641.7152 | 627.9867 | 603.2354 | 600.642
2565.1292 | 641.9189 | 633.0004 | 602.5198 | 597.3405
2566.1292 | 640.9595 | 635.4842 | 602.0885 | 598.8423
2567.1292 | 640.519 | 637.9956 | 606.9683 | 601.0099
2568.1292 | 641.7628 | 634.9025 | 608.7762 | 607.1188
2569.1292 | 641.5255 | 631.5282 | 609.8948 | 603.2628
2570.1292 | 641.2067 | 628.079 | 608.4641 | 601.3164
2571.1292 | 641.1439 | 624.2016 | 604.7276 | 598.6959
2572.1292 | 640.8295 | 625.0266 | 608.4071 | 603.9461
2573.1292 | 639.9541 | 622.6772 | 608.0798 | 607.7905
2574.1292 | 640.4868 | 627.4321 | 607.7634 | 604.3792
2575.1292 | 640.6979 | 635.5266 | 611.5262 | 606.8423
2576.1292 | 642.2497 | 633.325 | 613.2168 | 605.0959
2577.1292 | 642.4159 | 637.8049 | 613.9219 | 608.2874
2578.1292 | 642.9532 | 640.6099 | 622.4751 | 625.4551
2579.1292 | 641.6105 | 631.7188 | 617.7554 | 628.4114
2580.1292 | 640.8093 | 635.6578 | 616.9092 | 622.6594
2581.1292 | 640.625 | 638.7701 | 618.8979 | 621.5581
2582.1292 | 641.3267 | 638.5412 | 616.3747 | 613.4314
2583.1292 | 640.6888 | 638.6726 | 616.0623 | 614.2131
2584.1292 | 640.2207 | 633.0956 | 621.9822 | 613.9556
2585.1292 | 640.0355 | 631.7458 | 630.5344 | 627.6194
2586.1292 | 640.9542 | 631.6513 | 629.1498 | 634.3271
2587.1292 | 640.5566 | 639.031 | 626.5014 | 634.9143
2588.1292 | 639.5992 | 646.5537 | 628.1682 | 630.845
2589.1292 | 639.0226 | 649.7832 | 639.1573 | 631.9958
2590.1292 | 639.1271 | 648.2442 | 633.3564 | 629.6133
2591.1292 | 639.6197 | 647.7332 | 628.0105 | 622.1925
2592.1292 | 639.4108 | 649.6073 | 623.6624 | 619.9941
2593.1292 | 639.9626 | 655.8889 | 630.9553 | 619.2411
2594.1292 | 639.6027 | 653.8859 | 624.4816 | 631.7904
2595.1292 | 640.0962 | 651.4527 | 620.9103 | 621.4089
2596.1292 | 639.8923 | 643.0837 | 616.8184 | 616.3533
2597.1292 | 639.1708 | 636.0497 | 613.6513 | 610.9123
2598.1292 | 639.3099 | 639.6262 | 614.0483 | 609.0053
2599.1448 | 639.2794 | 637.7702 | 616.0987 | 605.469
2600.1448 | 640.3253 | 639.0951 | 620.4949 | 614.9584
2601.1292 | 639.8099 | 635.9367 | 619.4128 | 624.2955
2602.1292 | 638.576 | 628.8212 | 613.8963 | 624.1772
2603.1448 | 638.3685 | 628.8538 | 611.8785 | 624.9657
2604.1448 | 638.148 | 630.3971 | 617.8591 | 630.2292
2605.1448 | 638.7794 | 628.711 | 626.2903 | 627.9369
2606.1292 | 638.4715 | 629.8427 | 619.9313 | 621.8003
2607.1292 | 638.942 | 627.0497 | 615.6157 | 624.7913
2608.1292 | 638.7351 | 624.7924 | 615.6381 | 622.4061
2609.1292 | 639.0157 | 623.3933 | 613.8367 | 628.5838
2610.1292 | 639.1964 | 621.5778 | 610.3638 | 630.8341
2611.1292 | 640.1447 | 619.9761 | 613.2242 | 647.3347
2612.1292 | 640.6965 | 620.2785 | 614.9437 | 644.1169
2613.1292 | 640.4534 | 622.0164 | 617.9451 | 639.0203
2614.1292 | 640.7338 | 628.1194 | 619.304 | 630.6649
2615.1292 | 640.3342 | 627.1875 | 631.6118 | 632.6109
2616.1292 | 640.5875 | 631.0577 | 634.2077 | 641.2053
2617.1292 | 640.8959 | 636.5084 | 636.6412 | 653.0731
2618.1292 | 642.3915 | 641.45 | 637.6751 | 646.3313
2619.1292 | 642.4489 | 644.8206 | 633.3791 | 636.3467
2620.1292 | 642.9415 | 642.2058 | 630.8826 | 631.421
2621.1292 | 643.2977 | 636.9939 | 627.067 | 636.5845
2622.1292 | 643.5468 | 638.3397 | 624.6053 | 635.1288
2623.1292 | 642.8419 | 640.4469 | 626.8299 | 630.0843
2624.1292 | 642.7943 | 645.7748 | 626.9981 | 628.1786
2625.1292 | 642.2927 | 645.0216 | 639.5353 | 623.7258
2626.1292 | 642.6724 | 649.5315 | 635.3139 | 623.3912
2627.1292 | 643.0405 | 655.4533 | 633.3869 | 625.4821
2628.1292 | 644.1925 | 658.3968 | 630.42 | 622.8173
2629.1292 | 644.0269 | 657.4445 | 632.4411 | 633.3806
2630.1292 | 643.6196 | 654.9522 | 648.8774 | 636.3521
2631.1292 | 644.588 | 656.4112 | 648.4316 | 636.917
2632.1292 | 644.8285 | 662.1469 | 643.0477 | 633.788
2633.1292 | 645.1068 | 657.0236 | 640.1218 | 630.4362
2634.1292 | 645.3519 | 654.9008 | 637.7377 | 628.6661
2635.1292 | 645.3861 | 660.9157 | 635.7063 | 628.7736
2636.1292 | 645.1754 | 667.5042 | 634.6127 | 626.5362
2637.1292 | 645.5116 | 670.3834 | 638.3999 | 623.7689
2638.1292 | 645.6937 | 672.5278 | 636.7742 | 625.0343
2639.1292 | 645.7693 | 669.7996 | 633.0964 | 621.0547
2640.1292 | 646.7684 | 666.949 | 633.601 | 620.1546
2641.1292 | 646.1749 | 670.1332 | 635.3348 | 619.188
2642.1292 | 645.0473 | 669.978 | 637.3597 | 618.5396
2643.1292 | 644.4515 | 676.4052 | 637.6216 | 615.3089
2644.1292 | 644.2754 | 674.8717 | 640.686 | 610.6491
2645.1292 | 644.957 | 678.8098 | 639.0414 | 609.0083
2646.1292 | 645.7688 | 677.5223 | 638.2148 | 620.4033
2647.1292 | 646.3197 | 671.8045 | 635.7359 | 617.8361
2648.1292 | 646.0684 | 667.9043 | 638.1852 | 621.8574
2649.1292 | 646.6016 | 671.2949 | 640.7816 | 618.0789
2650.1292 | 647.4609 | 670.4691 | 642.2206 | 616.3709
2651.1292 | 646.6577 | 669.9467 | 647.6094 | 617.4853
2652.1292 | 648.0494 | 675.5758 | 652.0963 | 619.1148
2653.1292 | 648.3043 | 674.2537 | 649.0904 | 627.4346
2654.1292 | 648.1702 | 674.1167 | 653.0971 | 635.5723
2655.1292 | 649.0412 | 678.054 | 660.4372 | 629.2284
2656.1292 | 649.189 | 676.4976 | 660.7827 | 633.6486
2657.1292 | 649.8963 | 673.0581 | 655.0478 | 643.1675
2658.1292 | 650.3165 | 668.7068 | 657.5177 | 643.5013
2659.1292 | 649.8417 | 665.2974 | 651.0362 | 649.0812
2660.1292 | 650.1431 | 666.5296 | 659.8403 | 650.7148
2661.1292 | 651.4502 | 666.2245 | 653.2119 | 642.4678
2662.1292 | 652.0821 | 660.5852 | 647.741 | 638.8291
2663.1292 | 651.8978 | 657.7093 | 643.2682 | 632.1054
2664.1292 | 651.1678 | 664.1763 | 639.428 | 628.6729
2665.1292 | 650.0938 | 664.0631 | 635.1416 | 622.2561
2666.1292 | 648.8048 | 669.4644 | 640.8745 | 620.6252
2667.1292 | 648.0544 | 665.7871 | 640.8844 | 618.3198
2668.1292 | 648.5444 | 665.4029 | 644.7996 | 616.2795
2669.1292 | 649.1441 | 672.6766 | 641.9117 | 617.3821
2670.1292 | 650.8448 | 668.137 | 639.7997 | 617.281
2671.1292 | 651.8608 | 675.4202 | 638.4921 | 622.3727
2672.1292 | 653.036 | 680.122 | 636.6703 | 618.1113
2673.1292 | 653.7685 | 677.0651 | 635.6333 | 615.6716
2674.1292 | 655.538 | 670.5588 | 635.8279 | 614.8855
2675.1292 | 655.3289 | 672.4184 | 638.6158 | 613.3618
2676.1292 | 654.3798 | 670.4564 | 634.1663 | 610.1513
2677.1292 | 654.1291 | 672.8509 | 633.1363 | 613.2519
2678.1292 | 654.405 | 675.9807 | 634.7848 | 610.1899
2679.1292 | 654.5305 | 675.5768 | 633.3032 | 614.9964
2680.1292 | 653.2805 | 666.869 | 627.9893 | 612.6557
2681.1292 | 652.2311 | 663.872 | 625.5177 | 608.2515
2682.1292 | 652.1505 | 662.997 | 624.1034 | 608.4247
2683.1292 | 653.0127 | 661.7192 | 623.8746 | 608.8158
2684.1292 | 654.3722 | 661.8694 | 624.1874 | 609.0232
2685.1292 | 652.3391 | 658.045 | 623.1272 | 608.8258
2686.1292 | 651.5673 | 664.6767 | 622.7785 | 608.2284
2687.1292 | 651.5393 | 666.6745 | 623.6369 | 610.5883
2688.1292 | 651.9353 | 677.7836 | 624.8162 | 609.1247
2689.1292 | 652.6537 | 676.6832 | 624.1547 | 605.6736
2690.1292 | 652.2034 | 676.9286 | 621.3581 | 601.1982
2691.1292 | 650.742 | 680.7295 | 623.0033 | 602.7911
2692.1292 | 649.9511 | 679.702 | 622.4738 | 605.4437
2693.1292 | 650.1598 | 674.1196 | 619.6862 | 599.9304
2694.1292 | 649.7244 | 670.8627 | 620.3463 | 599.6744
2695.1292 | 648.971 | 666.2559 | 618.8003 | 598.4556
2696.1292 | 649.153 | 669.9311 | 625.1321 | 599.585
2697.1292 | 648.4708 | 670.6581 | 630.7335 | 602.1156
2698.1292 | 648.2798 | 672.6213 | 632.2653 | 606.7784
2699.1292 | 647.9804 | 668.2198 | 639.2195 | 620.6955
2700.1292 | 648.5219 | 674.5828 | 638.8104 | 621.426
2701.1292 | 648.8731 | 671.6608 | 638.4789 | 621.962
2702.1292 | 649.007 | 675.4893 | 638.3551 | 626.2771
2703.1292 | 649.891 | 677.2793 | 636.8859 | 622.3329
2704.1292 | 650.94 | 676.7305 | 637.0786 | 632.7276
2705.1292 | 651.804 | 681.3131 | 644.0922 | 634.2384
2706.1292 | 652.5746 | 679.6943 | 642.9731 | 630.8728
2707.1292 | 652.9901 | 675.0449 | 639.4995 | 625.0569
2708.1292 | 652.4393 | 670.2684 | 636.6331 | 618.471
2709.1292 | 652.2672 | 669.8302 | 632.2908 | 615.9882
2710.1292 | 652.1763 | 671.0171 | 630.26 | 615.5503
2711.1292 | 651.3209 | 666.7773 | 629.4573 | 613.2475
2712.1292 | 651.5696 | 665.8928 | 629.0772 | 611.2034
2713.1292 | 651.3035 | 671.9404 | 631.9516 | 611.4441
2714.1292 | 651.2299 | 669.3956 | 631.4039 | 611.1014
2715.1292 | 651.1823 | 672.4027 | 634.6402 | 610.4566
2716.1292 | 650.6892 | 677.3348 | 644.4986 | 611.4268
2717.1292 | 650.3781 | 678.4367 | 650.154 | 613.2627
2718.1292 | 649.5563 | 678.8303 | 656.0705 | 617.5263
2719.1292 | 649.1052 | 677.8169 | 669.8117 | 626.5151
2720.1292 | 648.6664 | 677.207 | 664.6283 | 633.6636
2721.1292 | 648.4771 | 684.9804 | 658.4473 | 637.7305
2722.1292 | 648.3037 | 684.6164 | 657 | 638.269
2723.1292 | 647.8836 | 684.8428 | 661.3822 | 633.1118
2724.1292 | 648.5247 | 685.5015 | 658.4841 | 630.7853
2725.1292 | 648.8939 | 682.341 | 660.293 | 631.8655
2726.1292 | 649.2573 | 679.6929 | 662.8218 | 631.4497
2727.1292 | 649.0251 | 680.6131 | 662.7339 | 631.2256
2728.1292 | 649.7751 | 684.104 | 660.2572 | 628.4829
2729.1292 | 649.1326 | 680.3386 | 656.6083 | 627.6098
2730.1292 | 649.1075 | 682.7569 | 666.5091 | 634.8469
2731.1292 | 648.78 | 681.7703 | 670.1707 | 640.8773
2732.1292 | 648.749 | 682.8295 | 661.9367 | 637.0949
2733.1292 | 648.2407 | 683.3178 | 661.7472 | 637.403
2734.1292 | 648.3348 | 683.641 | 667.7951 | 642.079
2735.1292 | 648.1306 | 686.9569 | 669.967 | 644.3607
2736.1292 | 648.7756 | 697.2383 | 666.3294 | 654.2015
2737.1292 | 649.0248 | 693.3205 | 659.4815 | 643.2784
2738.1292 | 648.7315 | 690.2398 | 660.6225 | 645.943
2739.1292 | 646.8256 | 691.6208 | 658.4175 | 646.0429
2740.1292 | 646.204 | 694.3405 | 655.0155 | 640.1766
2741.1292 | 646.4248 | 695.6736 | 654.7141 | 633.8701
2742.1292 | 646.8288 | 698.6902 | 651.1584 | 631.678
2743.1292 | 647.2944 | 697.225 | 646.0552 | 627.5805
2744.1292 | 648.2529 | 693.9041 | 647.1557 | 631.0472
2745.1292 | 647.7673 | 697.3037 | 644.405 | 630.4802
2746.1292 | 647.596 | 699.4594 | 643.6844 | 634.4715
2747.1292 | 647.7191 | 697.5784 | 644.7961 | 641.1659
2748.1292 | 648.4156 | 693.4796 | 644.3199 | 650.0777
2749.1292 | 648.5343 | 693.1798 | 640.6077 | 640.9733
2750.1292 | 647.4047 | 691.9589 | 637.6855 | 646.0548
2751.1292 | 646.6113 | 694.3251 | 642.1471 | 645.6179
2752.1292 | 647.3175 | 689.6952 | 644.0879 | 646.0355
2753.1292 | 647.8527 | 696.3065 | 642.8056 | 642.6788
2754.1448 | 647.6568 | 694.8813 | 638.5288 | 635.9917
2755.1292 | 647.8784 | 697.1463 | 635.8549 | 629.8646
2756.1292 | 647.2621 | 690.5358 | 632.4445 | 626.3205
2757.1292 | 647.4015 | 686.6944 | 627.8951 | 622.8319
2758.1292 | 647.1008 | 678.2974 | 625.6708 | 628.2902
2759.1292 | 647.9738 | 682.3747 | 623.7212 | 623.4483
2760.1292 | 649.3506 | 683.5079 | 627.1114 | 619.2023
2761.1292 | 650.8628 | 682.2105 | 633.9608 | 617.7851
2762.1292 | 651.3672 | 685.4411 | 632.9948 | 614.733
2763.1292 | 651.2776 | 686.73 | 640.1411 | 616.1355
2764.1292 | 650.0225 | 685.881 | 635.0459 | 631.6058
2765.1448 | 649.9841 | 691.0812 | 631.5551 | 639.8423
2766.1292 | 650.2687 | 683.7904 | 628.7381 | 631.104
2767.1292 | 650.2189 | 688.8341 | 627.1301 | 642.3711
2768.1292 | 650.3832 | 694.6738 | 625.8979 | 637.7031
2769.1292 | 649.5122 | 692.2523 | 627.8297 | 630.8745
2770.1292 | 649.0854 | 691.1387 | 629.8359 | 630.8345
2771.1292 | 649.1126 | 689.2104 | 640.0502 | 647.4894
2772.1292 | 648.1482 | 693.4067 | 639.8179 | 649.5681
2773.1292 | 648.1647 | 693.6661 | 639.9111 | 656.7857
2774.1292 | 647.8603 | 686.001 | 636.0896 | 648.7528
2775.1292 | 647.1076 | 681.155 | 632.3926 | 640.7627
2776.1292 | 646.7703 | 674.6812 | 629.1887 | 635.2933
2777.1292 | 646.3068 | 677.1246 | 629.3637 | 632.511
2778.1292 | 646.3016 | 682.6914 | 629.0086 | 632.9492
2779.1292 | 646.7523 | 692.2533 | 630.9184 | 650.9387
2780.1448 | 645.9335 | 693.6292 | 630.6243 | 651.869
2781.1292 | 646.2623 | 695.1009 | 631.1663 | 648.0459
2782.1292 | 646.3062 | 688.4802 | 628.6238 | 640.489
2783.1292 | 646.0495 | 684.9571 | 626.3338 | 635.8359
2784.1292 | 645.6565 | 683.914 | 628.875 | 632.0799
2785.1292 | 645.6373 | 689.5576 | 627.25 | 629.1327
2786.1292 | 646.359 | 687.5303 | 631.3165 | 626.4032
2787.1292 | 645.4439 | 684.0466 | 627.7024 | 639.3824
2788.1292 | 643.685 | 680.8748 | 628.5445 | 654.147
2789.1292 | 644.2609 | 684.0758 | 628.7966 | 660.4088
2790.1292 | 644.8777 | 678.8501 | 626.1586 | 654.3178
2791.1292 | 645.318 | 676.3406 | 623.0074 | 647.9235
2792.1292 | 645.8272 | 675.7241 | 626.0534 | 643.7551
2793.1292 | 644.6844 | 668.567 | 623.3242 | 641.0097
2794.1292 | 645.8892 | 666.1496 | 623.5393 | 637.2154
2795.1292 | 644.4322 | 670.6789 | 634.7993 | 648.0413
2796.1292 | 644.3261 | 670.6981 | 639.0887 | 651.3406
2797.1292 | 644.0426 | 669.0014 | 632.4903 | 642.5857
2798.1292 | 644.6077 | 667.0623 | 629.3522 | 636.1629
2799.1292 | 645.1054 | 664.7099 | 626.8516 | 631.0058
2800.1292 | 645.7471 | 657.8924 | 622.0507 | 624.4696
2801.1292 | 644.8938 | 660.1417 | 621.941 | 640.3476
2802.1292 | 644.3521 | 655.6597 | 620.3121 | 645.8537
2803.1292 | 643.9346 | 665.8499 | 617.8788 | 641.2746
2804.1292 | 644.083 | 663.5722 | 618.5465 | 649.2469
2805.1292 | 644.3724 | 663.4096 | 616.2454 | 654.8272
2806.1292 | 644.6995 | 662.5492 | 621.4413 | 657.9576
2807.1292 | 645.0017 | 661.0509 | 623.2806 | 667.4752
2808.1292 | 644.7953 | 663.7659 | 628.5651 | 662.3309
2809.1292 | 644.3149 | 670.4997 | 630.1331 | 657.5337
2810.1292 | 644.1921 | 669.051 | 634.9278 | 664.8322
2811.1292 | 644.084 | 674.0132 | 633.9496 | 658.6967
2812.1292 | 644.1836 | 676.6458 | 638.1273 | 671.0564
2813.1292 | 644.2351 | 679.1531 | 642.7274 | 663.8987
2814.1292 | 644.4538 | 681.5103 | 643.6592 | 662.9019
2815.1292 | 644.8425 | 681.2611 | 644.0765 | 653.5287
2816.1292 | 644.8672 | 676.7776 | 641.9441 | 659.6636
2817.1292 | 644.7556 | 678.2521 | 649.6557 | 652.5003
2818.1292 | 644.6364 | 678.1125 | 645.6258 | 651.3163
2819.1292 | 644.4111 | 674.9518 | 640.6943 | 645.7776
2820.1292 | 644.4179 | 679.6723 | 645.0108 | 652.9112
2821.1292 | 644.6116 | 679.2008 | 642.2668 | 646.6625
2822.1292 | 643.9534 | 677.3824 | 637.5075 | 639.4104
2823.1292 | 644.3601 | 673.767 | 635.1752 | 636.813
2824.1292 | 644.1566 | 676.8524 | 631.3553 | 636.6423
2825.1292 | 644.9298 | 678.0515 | 638.216 | 646.8604
2826.1292 | 643.9 | 678.413 | 637.5591 | 645.9276
2827.1292 | 644.2852 | 680.9164 | 634.0992 | 642.8689
2828.1448 | 644.5682 | 681.9133 | 639.0341 | 642.3919
2829.1292 | 644.0286 | 675.4817 | 639.1315 | 641.7341
2830.1292 | 644.751 | 679.1818 | 644.8975 | 637.2292
2831.1292 | 644.5128 | 674.1372 | 642.01 | 632.899
2832.1292 | 645.4476 | 671.712 | 637.7459 | 630.6834
2833.1292 | 646.0227 | 669.0035 | 638.2283 | 632.4759
2834.1292 | 645.9332 | 666.2728 | 637.698 | 628.2603
2835.1292 | 646.2376 | 664.7832 | 636.9386 | 627.95
2836.1292 | 646.7271 | 663.5726 | 640.5352 | 643.8
2837.1292 | 646.1126 | 669.9649 | 645.8356 | 642.0048
2838.1292 | 646.3844 | 675.2899 | 650.8308 | 640.4387
2839.1292 | 646.234 | 676.7911 | 652.9458 | 659.4483
2840.1448 | 645.9823 | 680.2033 | 649.5958 | 651.5572
2841.1292 | 645.8241 | 684.9331 | 656.6327 | 647.987
2842.1292 | 645.9768 | 695.5986 | 668.6313 | 646.2435
2843.1292 | 645.5609 | 695.3177 | 669.1456 | 649.6781
2844.1292 | 645.2085 | 698.4192 | 680.0989 | 645.9718
2845.1292 | 644.4219 | 694.4569 | 682.421 | 640.8776
2846.1292 | 643.9643 | 693.5876 | 684.0059 | 638.054
2847.1292 | 643.755 | 696.5309 | 677.8736 | 637.4946
2848.1292 | 643.5214 | 695.53 | 679.1064 | 637.7937
2849.1292 | 642.7991 | 693.2669 | 679.6146 | 641.9845
2850.1292 | 643.1177 | 696.1427 | 681.1617 | 658.2487
2851.1292 | 643.4792 | 692.0267 | 674.4608 | 658.3632
2852.1292 | 644.6286 | 687.7798 | 668.6446 | 651.5044
2853.1292 | 644.7225 | 685.0334 | 662.4975 | 643.9304
2854.1292 | 645.1296 | 687.3835 | 662.2269 | 639.0636
2855.1292 | 645.4726 | 692.0685 | 659.1516 | 635.2281
2856.1292 | 645.2426 | 691.8374 | 655.4957 | 633.91
2857.1292 | 645.3884 | 693.2039 | 657.4379 | 633.3959
2858.1292 | 645.2866 | 695.0605 | 659.9681 | 634.7596
2859.1292 | 644.7358 | 695.2823 | 661.0195 | 633.1383
2860.1292 | 644.5106 | 700.9693 | 669.9062 | 647.2226
2861.1292 | 644.4478 | 703.6418 | 673.5381 | 653.9249
2862.1292 | 644.2011 | 709.1671 | 675.826 | 658.1027
2863.1292 | 643.89 | 709.1598 | 668.7111 | 653.3066
2864.1292 | 643.7339 | 700.9484 | 662.0393 | 645.5575
2865.1292 | 643.5574 | 701.4301 | 659.7831 | 644.428
2866.1292 | 644.0735 | 712.9704 | 656.9125 | 643.6139
2867.1292 | 643.675 | 705.9335 | 654.4047 | 657.0946
2868.1292 | 643.4671 | 707.9158 | 652.1867 | 650.7078
2869.1292 | 643.5936 | 700.3372 | 651.4079 | 661.7585
2870.1292 | 643.7087 | 698.4979 | 649.0397 | 653.8097
2871.1292 | 644.5329 | 687.5082 | 645.936 | 649.718
2872.1292 | 645.4489 | 679.654 | 643.3998 | 644.3736
2873.1292 | 645.5294 | 675.5236 | 640.3229 | 640.4296
2874.1292 | 645.1616 | 674.7953 | 638.232 | 637.0646
2875.1292 | 645.1017 | 681.4009 | 653.2374 | 632.5307
2876.1292 | 644.7523 | 683.5 | 664.1772 | 653.7781
2877.1292 | 645.005 | 682.0889 | 660.5519 | 661.3921
2878.1292 | 646.005 | 675.0227 | 656.454 | 660.9862
2879.1292 | 647.4203 | 670.3384 | 652.9617 | 655.9963
2880.1292 | 647.3261 | 674.1553 | 648.6587 | 648.4635
2881.1292 | 647.3115 | 676.5123 | 652.8524 | 643.6332
2882.1292 | 647.098 | 675.8974 | 660.8783 | 640.4858
2883.1292 | 647.5833 | 684.7731 | 657.8498 | 640.6577
2884.1292 | 647.7751 | 689.9164 | 660.2337 | 645.6773
2885.1292 | 647.3819 | 695.7503 | 660.9689 | 644.003
2886.1292 | 647.1506 | 701.6651 | 659.1684 | 653.9931
2887.1292 | 645.8395 | 698.4106 | 668.2491 | 645.2682
2888.1292 | 645.7964 | 695.9147 | 667.652 | 660.1701
2889.1292 | 645.7528 | 694.5406 | 662.4621 | 658.6051
2890.1292 | 646.9029 | 694.6413 | 663.4864 | 651.1504
2891.1292 | 646.2865 | 689.093 | 658.7886 | 642.4617
2892.1292 | 645.3406 | 690.6333 | 658.5602 | 636.2017
2893.1292 | 645.1043 | 693.7558 | 673.4414 | 644.8112
2894.1292 | 645.2275 | 696.983 | 675.3426 | 648.0567
2895.1292 | 644.702 | 692.514 | 669.9664 | 649.2297
2896.1292 | 644.7761 | 690.453 | 665.7143 | 652.2761
2897.1292 | 644.4571 | 690.4476 | 670.8008 | 663.0763
2898.1292 | 644.4852 | 693.76 | 672.9726 | 657.6556
2899.1292 | 644.6681 | 693.032 | 680.986 | 658.6762
2900.1448 | 644.7015 | 700.298 | 685.4088 | 670.1483
2901.1292 | 644.7399 | 698.069 | 687.8234 | 661.6748
2902.1292 | 644.7156 | 702.0977 | 686.7616 | 668.6053
2903.1292 | 644.8836 | 702.7053 | 689.2692 | 678.3756
2904.1292 | 644.8204 | 707.6428 | 684.7434 | 679.6563
2905.1292 | 644.5202 | 704.8566 | 684.502 | 683.0947
2906.1292 | 644.2209 | 705.3006 | 680.6332 | 674.3519
2907.1292 | 643.6773 | 702.1502 | 683.0014 | 674.6564
2908.1292 | 643.1475 | 704.8932 | 690.1503 | 672.5957
2909.1292 | 642.78 | 702.3244 | 687.3161 | 676.9618
2910.1292 | 642.3606 | 702.1939 | 687.2777 | 679.7153
2911.1292 | 642.1029 | 699.8229 | 687.4203 | 680.5418
2912.1292 | 641.686 | 698.78 | 685.7847 | 682.6857
2913.1292 | 642.4696 | 697.2052 | 679.2687 | 681.4192
2914.1292 | 642.2481 | 699.5251 | 674.4808 | 675.1367
2915.1292 | 642.2096 | 701.6281 | 670.3322 | 682.1957
2916.1292 | 642.1346 | 695.3665 | 678.7765 | 685.7834
2917.1292 | 642.1446 | 691.6779 | 672.9446 | 681.9375
2918.1292 | 642.3297 | 687.9657 | 681.0628 | 695.2693
2919.1292 | 641.8884 | 688.1456 | 678.2134 | 693.7951
2920.1292 | 640.8961 | 690.9012 | 681.2149 | 688.1146
2921.1292 | 641.3563 | 688.8343 | 678.7391 | 689.1321
2922.1292 | 641.1233 | 691.7404 | 680.3742 | 694.8484
2923.1292 | 640.9578 | 692.9394 | 673.3159 | 692.4986
2924.1292 | 641.0258 | 695.4844 | 672.8462 | 689.3787
2925.1292 | 642.5893 | 694.5628 | 670.9621 | 688.6059
2926.1292 | 642.7631 | 697.7053 | 671.754 | 685.855
2927.1292 | 641.7847 | 697.82 | 681.6947 | 676.1752
2928.1292 | 640.7176 | 696.7513 | 686.136 | 675.7011
2929.1292 | 638.9034 | 693.1791 | 685.1195 | 678.8176
2930.1292 | 638.8292 | 693.753 | 684.9467 | 674.4552
2931.1292 | 639.5412 | 700.6472 | 683.5724 | 679.4328
2932.1292 | 640.1949 | 701.8692 | 675.1375 | 675.8113
2933.1292 | 640.7449 | 698.3494 | 678.3689 | 671.8013
2934.1292 | 640.4673 | 695.8984 | 675.7221 | 676.181
2935.1292 | 640.9858 | 698.5175 | 677.8621 | 685.8591
2936.1292 | 641.6166 | 708.9018 | 680.9596 | 689.4578
2937.1292 | 641.8114 | 715.744 | 672.3922 | 679.6231
2938.1292 | 642.1097 | 714.4387 | 668.77 | 670.0183
2939.1292 | 642.3558 | 711.4351 | 663.2666 | 664.0808
2940.1292 | 642.6187 | 723.9427 | 662.3748 | 658.7667
2941.1292 | 641.6797 | 713.6168 | 661.3551 | 669.9308
2942.1292 | 641.3317 | 712.8217 | 670.1545 | 677.0713
2943.1292 | 640.9511 | 718.1936 | 673.2514 | 668.5944
2944.1292 | 641.2291 | 712.9616 | 674.7274 | 659.619
2945.1292 | 641.2687 | 713.2352 | 669.2819 | 663.8266
2946.1292 | 641.7087 | 711.4824 | 671.7512 | 659.3759
2947.1292 | 642.3173 | 706.0612 | 666.9326 | 655.3005
2948.1292 | 642.7172 | 702.2552 | 661.5139 | 653.0526
2949.1292 | 644.9792 | 704.1758 | 656.6033 | 645.9001
2950.1292 | 645.3814 | 701.9582 | 652.2275 | 640.8545
2951.1292 | 645.3237 | 704.4746 | 649.0238 | 638.0598
2952.1292 | 645.1876 | 710.4132 | 649.0943 | 633.0825
2953.1292 | 645.2088 | 707.3356 | 651.0201 | 630.9642
2954.1292 | 643.7823 | 707.3814 | 662.3278 | 628.1978
2955.1292 | 643.9431 | 707.9562 | 664.0222 | 633.1858
2956.1292 | 643.6417 | 714.6173 | 673.8104 | 640.2302
2957.1292 | 643.9746 | 716.4673 | 675.8873 | 651.3189
2958.1292 | 643.9406 | 723.3996 | 683.2044 | 654.8762
2959.1292 | 644.9549 | 720.0639 | 682.5053 | 654.2127
2960.1448 | 644.5704 | 715.6371 | 678.1498 | 653.4636
2961.1292 | 644.6266 | 710.4698 | 671.6592 | 648.2027
2962.1292 | 643.8453 | 712.5662 | 664.2265 | 650.6013
2963.1292 | 643.1791 | 704.3417 | 665.8695 | 656.6737
2964.1292 | 642.7185 | 707.0898 | 663.7499 | 655.9031
2965.1292 | 642.0542 | 704.7287 | 661.585 | 650.9903
2966.1292 | 642.4909 | 712.5067 | 668.2131 | 647.57
2967.1292 | 642.3283 | 714.5741 | 673.2537 | 646.648
2968.1292 | 642.4 | 713.2943 | 682.3068 | 653.5785
2969.1292 | 642.3162 | 713.1966 | 682.6655 | 660.4927
2970.1292 | 642.7522 | 708.8368 | 681.0307 | 665.2606
2971.1292 | 643.0727 | 705.5034 | 675.2329 | 665.4452
2972.1292 | 643.8312 | 704.4732 | 670.0224 | 662.3127
2973.1292 | 643.2482 | 701.0531 | 663.3292 | 664.1269
2974.1292 | 642.6108 | 700.2511 | 674.9024 | 677.5103
2975.1292 | 642.656 | 711.1565 | 668.6918 | 673.6707
2976.1292 | 642.3006 | 708.3776 | 667.6034 | 677.8522
2977.1292 | 641.3711 | 704.3179 | 662.3437 | 670.6506
2978.1292 | 640.3314 | 696.5422 | 660.6363 | 663.5394
2979.1292 | 640.6531 | 695.8546 | 655.5702 | 665.6097
2980.1292 | 642.1282 | 690.9489 | 652.4531 | 669.0177
2981.1292 | 642.5147 | 684.4096 | 647.4501 | 664.6067
2982.1292 | 642.8505 | 679.4522 | 643.4308 | 662.5559
2983.1292 | 642.849 | 674.8688 | 642.5264 | 665.4911
2984.1292 | 643.099 | 687.1786 | 646.8828 | 667.5784
2985.1292 | 643.3038 | 688.7971 | 646.3456 | 665.7345
2986.1292 | 643.1266 | 687.944 | 644.0898 | 665.1652
2987.1292 | 643.3092 | 687.7307 | 649.2256 | 664.1246
2988.1292 | 643.0587 | 686.6274 | 648.0535 | 663.2791
2989.1292 | 643.5371 | 697.1591 | 650.928 | 667.3741
2990.1292 | 643.3541 | 700.4466 | 654.4036 | 682.3256
2991.1292 | 643.2942 | 700.0089 | 665.6309 | 675.0794
2992.1292 | 643.1816 | 701.8561 | 665.9354 | 676.5478
2993.1292 | 642.6782 | 698.2853 | 660.4479 | 667.3399
2994.1292 | 642.6105 | 690.5269 | 661.406 | 657.529
2995.1292 | 642.1208 | 695.1865 | 665.6629 | 659.9025
2996.1292 | 641.578 | 693.3849 | 664.2486 | 664.1861
2997.1292 | 641.8521 | 690.4213 | 660.0348 | 666.7706
2998.1292 | 643.0953 | 684.5667 | 663.8101 | 672.9889
2999.1292 | 643.7306 | 677.6315 | 658.1364 | 671.2534
3000.1292 | 643.6826 | 671.4505 | 653.628 | 675.0771
3001.1292 | 644.6307 | 674.6655 | 651.692 | 676.4433
3002.1292 | 645.1537 | 677.0168 | 650.4555 | 674.2319
3003.1292 | 645.6111 | 681.8472 | 648.6418 | 667.5355
3004.1292 | 645.4192 | 687.6532 | 649.3694 | 666.9068
3005.1292 | 645.3738 | 687.631 | 652.005 | 659.7526
3006.1292 | 645.7357 | 696.6907 | 660.0672 | 655.0952
3007.1292 | 646.021 | 699.1847 | 659.9212 | 650.4141
3008.1292 | 645.7889 | 704.1643 | 666.2055 | 648.2453
3009.1292 | 645.2685 | 710.1981 | 677.8398 | 654.5945
3010.1292 | 644.4492 | 704.9033 | 678.955 | 650.4134
3011.1292 | 643.5635 | 701.6551 | 686.7511 | 657.6117
3012.1292 | 643.5202 | 700.3936 | 683.0153 | 657.8539
3013.1292 | 642.9346 | 700.02 | 685.4702 | 660.2532
3014.1292 | 642.656 | 696.8029 | 682.1043 | 652.4893
3015.1292 | 642.2767 | 694.9652 | 675.804 | 653.4683
3016.1292 | 641.961 | 691.6103 | 685.7274 | 658.5516
3017.1292 | 640.592 | 692.7076 | 677.6647 | 662.7565
3018.1292 | 640.6795 | 695.9592 | 684.8489 | 659.5427
3019.1292 | 640.6349 | 695.8174 | 687.1624 | 651.1034
3020.1448 | 641.0368 | 698.5966 | 681.2071 | 646.1878
3021.1292 | 641.5726 | 704.0878 | 675.9528 | 645.901
3022.1292 | 641.6519 | 715.4499 | 670.9549 | 653.8029
3023.1292 | 641.6393 | 709.3934 | 678.8019 | 657.4797
3024.1292 | 642.0457 | 710.4882 | 678.8115 | 657.3743
3025.1292 | 642.655 | 707.9803 | 681.666 | 659.3349
3026.1292 | 643.2294 | 707.6395 | 685.6507 | 667.4588
3027.1292 | 642.8755 | 711.9182 | 680.5886 | 672.7303
3028.1292 | 642.7809 | 711.5429 | 681.1565 | 668.8505
3029.1292 | 642.3562 | 714.4039 | 685.0042 | 668.2605
3030.1292 | 642.159 | 715.3009 | 681.7469 | 670.0902
3031.1292 | 642.4616 | 714.6101 | 681.3651 | 677.5223
3032.1292 | 643.3875 | 706.112 | 675.3282 | 674.8156
3033.1292 | 644.1832 | 697.7495 | 672.7752 | 675.0297
3034.1292 | 644.6843 | 688.9131 | 664.8531 | 663.9047
3035.1292 | 644.0712 | 690.2227 | 665.4917 | 668.0829
3036.1292 | 643.3538 | 684.1762 | 665.2416 | 672.9661
3037.1292 | 642.8593 | 682.1435 | 658.2376 | 675.5179
3038.1292 | 642.8442 | 676.1947 | 654.5887 | 673.5566
3039.1292 | 642.829 | 671.2496 | 659.6406 | 672.9429
3040.1292 | 642.6202 | 671.2472 | 655.4631 | 669.4149
3041.1292 | 642.5236 | 677.0225 | 663.479 | 672.7039
3042.1292 | 642.2985 | 681.1824 | 668.784 | 675.1634
3043.1292 | 641.9783 | 681.7367 | 670.3037 | 676.0333
3044.1292 | 642.5969 | 679.5373 | 673.4036 | 674.3761
3045.1292 | 645.0456 | 677.9563 | 668.5925 | 667.488
3046.1292 | 645.944 | 685.4056 | 663.8606 | 658.3899
3047.1292 | 645.8016 | 688.0286 | 669.3642 | 662.7832
3048.1292 | 645.1097 | 683.3682 | 667.5134 | 658.1484
3049.1292 | 644.8435 | 684.1386 | 672.2004 | 665.8996
3050.1292 | 644.7049 | 691.0278 | 676.5052 | 660.0981
3051.1292 | 644.209 | 700.4898 | 675.1418 | 666.6107
3052.1292 | 644.2349 | 695.6279 | 669.4984 | 673.2515
3053.1292 | 643.6557 | 694.0375 | 664.8887 | 669.0431
3054.1292 | 643.6938 | 691.071 | 669.3423 | 671.9491
3055.1292 | 643.2562 | 693.5612 | 666.5851 | 666.3327
3056.1292 | 643.3978 | 702.4618 | 679.7768 | 660.7595
3057.1292 | 642.3821 | 698.5147 | 672.5413 | 651.3625
3058.1292 | 642.3048 | 692.758 | 678.693 | 645.132
3059.1292 | 642.0107 | 692.0668 | 676.9688 | 656.8067
3060.1292 | 642.5072 | 703.0726 | 671.1829 | 659.3144
3061.1292 | 643.2872 | 702.2987 | 673.3018 | 659.0376
3062.1292 | 644.0177 | 703.1093 | 675.6511 | 656.6573
3063.1292 | 644.2706 | 711.6722 | 682.2863 | 651.6386
3064.1292 | 643.9948 | 708.3122 | 686.8673 | 658.0501
3065.1292 | 643.4947 | 708.044 | 685.7803 | 649.311
3066.1292 | 643.4859 | 710.0793 | 687.7903 | 656.1262
3067.1292 | 644.1371 | 711.3788 | 682.78 | 663.4887
3068.1292 | 645.2955 | 709.762 | 693.6543 | 665.7269
3069.1292 | 645.7365 | 708.014 | 698.5011 | 669.517
3070.1292 | 645.848 | 708.9126 | 693.175 | 668.0549
3071.1292 | 646.4342 | 705.9451 | 691.128 | 675.7955
3072.1292 | 646.9964 | 704.4132 | 703.764 | 677.4986
3073.1292 | 646.9185 | 714.4198 | 698.8327 | 675.479
3074.1292 | 646.3466 | 714.6353 | 694.493 | 677.1145
3075.1292 | 645.4166 | 710.0096 | 698.2126 | 678.052
3076.1292 | 645.2089 | 708.3432 | 697.5993 | 687.4467
3077.1292 | 644.2439 | 699.6089 | 686.4668 | 686.1214
3078.1292 | 645.5565 | 697.831 | 681.7108 | 690.1465
3079.1292 | 646.7562 | 695.5448 | 676.5058 | 687.5354
3080.1292 | 648.2776 | 697.7349 | 671.2058 | 676.4179
3081.1292 | 650.1954 | 701.0189 | 664.9412 | 675.4741
3082.1292 | 649.0638 | 698.5667 | 663.5565 | 681.6101
3083.1292 | 648.085 | 693.9988 | 657.8667 | 682.3998
3084.1292 | 646.9766 | 695.0467 | 668.8308 | 675.8621
3085.1292 | 647.3098 | 699.7684 | 672.7596 | 671.1347
3086.1292 | 648.2656 | 708.535 | 677.2199 | 671.4894
3087.1292 | 648.4613 | 704.5747 | 678.4355 | 673.7943
3088.1292 | 648.4615 | 706.3697 | 674.8808 | 674.6424
3089.1292 | 648.3581 | 704.3176 | 675.2395 | 678.4546
3090.1292 | 647.6186 | 697.6307 | 678.3019 | 679.2144
3091.1292 | 647.6769 | 699.5883 | 676.382 | 678.311
3092.1292 | 647.704 | 707.2071 | 676.2807 | 678.5145
3093.1292 | 648.9826 | 703.1038 | 666.8508 | 673.3327
3094.1292 | 649.0322 | 697.2433 | 661.7175 | 672.0774
3095.1292 | 650.2157 | 690.6971 | 659.2553 | 676.2726
3096.1292 | 650.2557 | 684.8468 | 663.5627 | 682.1718
3097.1292 | 651.0059 | 677.2509 | 657.1494 | 678.2187
3098.1292 | 651.0349 | 670.4495 | 653.1442 | 672.6529
3099.1292 | 651.7387 | 674.8513 | 651.6403 | 665.5755
3100.1292 | 653.4481 | 683.1418 | 652.3241 | 662.6274
3101.1292 | 654.3201 | 683.493 | 654.4357 | 660.4771
3102.1292 | 653.273 | 688.3726 | 668.2907 | 663.8354
3103.1292 | 652.233 | 686.267 | 680.621 | 664.0426
3104.1292 | 651.4013 | 682.1611 | 674.5706 | 661.9089
3105.1292 | 651.2187 | 686.6919 | 676.8462 | 667.4186
3106.1292 | 651.2854 | 683.1715 | 669.3812 | 676.7224
3107.1292 | 650.4358 | 677.7764 | 666.4379 | 680.1847
3108.1292 | 650.128 | 675.1573 | 663.8151 | 682.1288
3109.1292 | 650.1374 | 667.648 | 656.1435 | 686.5622
3110.1292 | 650.5181 | 665.4865 | 651.2132 | 681.6678
3111.1292 | 650.9093 | 665.8716 | 644.985 | 678.2103
3112.1292 | 651.8918 | 662.8917 | 642.6966 | 672.3721
3113.1292 | 652.3295 | 660.5298 | 644.1487 | 673.2905
3114.1292 | 652.8219 | 662.5144 | 640.4778 | 671.4218
3115.1292 | 652.2117 | 665.5822 | 648.0441 | 667.2886
3116.1292 | 651.3506 | 669.275 | 660.3302 | 676.3889
3117.1292 | 651.7664 | 673.5018 | 662.4505 | 677.8063
3118.1292 | 652.81 | 684.0199 | 659.5364 | 685.062
3119.1292 | 652.1862 | 680.5364 | 661.8254 | 686.8485
3120.1292 | 651.3986 | 683.1792 | 670.4337 | 684.2497
3121.1292 | 651.3284 | 687.5052 | 672.7207 | 683.3025
3122.1292 | 650.3829 | 685.8205 | 680.6622 | 683.7145
3123.1292 | 649.6323 | 679.9765 | 675.1322 | 672.6262
3124.1292 | 649.5073 | 675.9538 | 666.0474 | 660.6805
3125.1292 | 648.2795 | 686.5351 | 660.6495 | 662.2954
3126.1292 | 648.7857 | 677.1352 | 659.58 | 672.3926
3127.1292 | 648.5399 | 670.8195 | 653.9003 | 663.3202
3128.1292 | 649.3332 | 673.482 | 648.3967 | 656.8147
3129.1292 | 649.6568 | 672.7559 | 646.3047 | 669.564
3130.1292 | 649.2949 | 680.3738 | 648.5284 | 675.6256
3131.1292 | 648.9493 | 675.1703 | 656.033 | 674.6798
3132.1292 | 649.2909 | 670.5506 | 651.3839 | 672.1935
3133.1292 | 649.3428 | 665.204 | 647.3044 | 670.9904
3134.1292 | 649.6107 | 661.9161 | 643.7047 | 660.5719
3135.1292 | 649.338 | 658.6425 | 638.2148 | 651.9558
3136.1292 | 648.8428 | 656.1281 | 645.6139 | 653.7392
3137.1292 | 648.7838 | 661.0307 | 649.5022 | 659.3047
3138.1292 | 648.654 | 663.5598 | 652.035 | 667.15
3139.1292 | 648.507 | 659.3143 | 654.03 | 672.4034
3140.1292 | 648.2006 | 654.7753 | 647.1901 | 677.0254
3141.1292 | 647.3119 | 653.4311 | 652.1371 | 673.9131
3142.1292 | 648.3614 | 652.704 | 650.2984 | 668.0129
3143.1292 | 648.6553 | 659.1 | 661.06 | 671.8385
3144.1292 | 648.9725 | 670.2851 | 669.4727 | 671.2066
3145.1292 | 649.3128 | 671.1857 | 667.1108 | 673.389
3146.1292 | 648.5735 | 676.1941 | 671.3258 | 665.2988
3147.1292 | 648.3391 | 679.3316 | 671.8397 | 664.8172
3148.1292 | 647.7793 | 681.7333 | 676.336 | 672.4598
3149.1292 | 648.3328 | 687.8995 | 687.256 | 676.7164
3150.1292 | 647.5625 | 690.4493 | 687.9709 | 674.8698
3151.1292 | 647.4407 | 691.1653 | 690.9609 | 675.7465
3152.1292 | 647.0181 | 692.8848 | 686.4059 | 676.4622
3153.1292 | 647.2705 | 698.3215 | 684.955 | 673.6871
3154.1292 | 646.9838 | 699.7891 | 683.3415 | 676.9894
3155.1292 | 646.4531 | 695.1374 | 683.6213 | 673.3397
3156.1292 | 646.3979 | 698.061 | 688.0683 | 668.1277
3157.1292 | 646.2295 | 697.488 | 683.9296 | 665.152
3158.1292 | 645.6169 | 698.5063 | 684.6071 | 670.8825
3159.1292 | 645.387 | 698.2416 | 684.9491 | 675.5059
3160.1292 | 644.3892 | 699.92 | 695.7318 | 678.4435
3161.1292 | 644.9524 | 695.802 | 691.0235 | 671.9309
3162.1292 | 645.6778 | 691.4834 | 687.7528 | 665.5747
3163.1292 | 646.0837 | 687.6125 | 684.4284 | 665.7433
3164.1292 | 645.6712 | 683.7728 | 675.7384 | 665.6885
3165.1292 | 645.5498 | 685.9292 | 670.2714 | 670.8518
3166.1292 | 645.0486 | 696.6208 | 669.4787 | 674.054
3167.1292 | 644.9993 | 691.8748 | 672.1891 | 672.3882
3168.1292 | 643.9888 | 681.0743 | 664.3176 | 661.5725
3169.1292 | 643.8556 | 682.225 | 668.8537 | 654.5761
3170.1292 | 643.5335 | 675.6884 | 670.7651 | 661.0725
3171.1292 | 643.1326 | 672.015 | 674.2923 | 668.1216
3172.1292 | 642.4804 | 670.4104 | 670.0103 | 671.2916
3173.1292 | 642.2957 | 664.3547 | 677.8811 | 674.4442
3174.1292 | 642.4315 | 662.9504 | 678.3817 | 672.2326
3175.1292 | 643.1858 | 657.8331 | 679.9124 | 679.9482
3176.1292 | 643.8539 | 652.7239 | 676.0244 | 676.4701
3177.1292 | 644.1678 | 650.6231 | 667.7086 | 667.8724
3178.1292 | 645.0298 | 657.1182 | 663.4893 | 662.9754
3179.1292 | 644.9814 | 663.1401 | 659.7808 | 654.8902
3180.1292 | 644.4277 | 659.2126 | 663.0195 | 657.7696
3181.1292 | 644.4291 | 660.7501 | 665.3873 | 666.1283
3182.1292 | 644.1822 | 666.3929 | 666.944 | 661.3135
3183.1448 | 645.2813 | 668.8392 | 663.5453 | 658.5554
3184.1292 | 645.596 | 662.8029 | 660.8884 | 658.0704
3185.1292 | 645.3433 | 656.1496 | 657.0717 | 655.1774
3186.1292 | 645.044 | 654.0139 | 657.6838 | 655.6618
3187.1292 | 645.4153 | 651.2172 | 660.432 | 656.9458
3188.1292 | 645.974 | 659.5142 | 663.8742 | 655.4993
3189.1448 | 645.6281 | 657.848 | 664.0536 | 658.1109
3190.1292 | 645.3024 | 664.2467 | 662.7208 | 661.2997
3191.1292 | 644.7494 | 672.0592 | 666.0195 | 665.6665
3192.1292 | 644.2353 | 675.0696 | 672.4549 | 673.6402
3193.1292 | 644.0321 | 673.75 | 679.0891 | 672.0315
3194.1292 | 643.7166 | 677.5118 | 679.7102 | 674.9393
3195.1292 | 643.8048 | 675.7078 | 680.3959 | 681.4548
3196.1292 | 644.0543 | 671.6493 | 689.0803 | 682.5669
3197.1292 | 644.4736 | 676.8864 | 691.5844 | 690.8988
3198.1292 | 645.0591 | 671.6028 | 685.1894 | 683.5739
3199.1292 | 644.7989 | 674.569 | 682.2287 | 672.0591
3200.1448 | 645.454 | 681.16 | 680.685 | 666.1642
3201.1292 | 645.267 | 678.6348 | 676.1562 | 673.6327
3202.1292 | 644.5306 | 673.8035 | 682.1062 | 669.6825
3203.1292 | 644.5797 | 677.0174 | 677.5013 | 666.4897
3204.1292 | 644.5218 | 671.208 | 672.8187 | 671.6806
3205.1292 | 645.0286 | 672.2578 | 672.4007 | 668.5009
3206.1292 | 645.521 | 673.1465 | 673.1752 | 660.766
3207.1292 | 644.7851 | 675.1282 | 675.9034 | 660.736
3208.1292 | 643.8803 | 669.5019 | 666.655 | 673.4282
3209.1292 | 643.282 | 664.359 | 662.2751 | 683.1166
3210.1292 | 643.2036 | 658.9505 | 654.5953 | 677.2979
3211.1292 | 643.643 | 654.5664 | 653.7329 | 680.0867
3212.1292 | 644.3186 | 665.1297 | 652.7666 | 676.2726
3213.1292 | 645.0752 | 664.9352 | 653.5503 | 674.2051
3214.1292 | 645.1806 | 658.1602 | 653.2216 | 680.5805
3215.1292 | 645.0237 | 657.203 | 657.1485 | 677.4427
3216.1292 | 644.3032 | 653.1334 | 657.4347 | 676.0938
3217.1292 | 644.1982 | 651.2605 | 662.8218 | 681.2781
3218.1292 | 643.5229 | 647.5633 | 654.8326 | 688.8112
3219.1292 | 643.3222 | 646.2423 | 653.9133 | 694.7328
3220.1292 | 642.8446 | 643.455 | 650.1234 | 684.4793
3221.1292 | 642.236 | 651.4437 | 651.207 | 683.638
3222.1292 | 642.6419 | 661.628 | 655.1765 | 678.5119
3223.1292 | 642.4525 | 655.824 | 650.3788 | 676.3183
3224.1292 | 642.6276 | 649.4553 | 646.2157 | 666.5447
3225.1292 | 642.9668 | 648.4809 | 647.6855 | 667.0325
3226.1292 | 642.9919 | 645.4719 | 653.264 | 674.9976
3227.1292 | 643.0194 | 659.2973 | 657.4163 | 678.2733
3228.1292 | 642.2795 | 661.5525 | 669.9599 | 681.6012
3229.1292 | 641.386 | 660.9133 | 679.3235 | 682.5821
3230.1292 | 641.4135 | 663.6606 | 677.3372 | 674.8751
3231.1292 | 641.5585 | 670.6111 | 673.7924 | 670.1247
3232.1292 | 641.8227 | 668.0446 | 680.1858 | 670.5996
3233.1292 | 641.5484 | 677.7318 | 688.9286 | 666.6797
3234.1292 | 641.1543 | 681.5477 | 691.4472 | 658.9863
3235.1292 | 640.4387 | 674.0068 | 697.1602 | 656.5814
3236.1292 | 639.7328 | 668.4817 | 692.1229 | 649.9925
3237.1292 | 639.6858 | 662.8862 | 684.8306 | 651.4978
3238.1292 | 639.3317 | 658.6087 | 681.5099 | 655.3436
3239.1292 | 639.1572 | 655.8322 | 689.0688 | 658.0093
3240.1292 | 638.718 | 651.1706 | 695.8446 | 652.12
3241.1292 | 638.0962 | 652.5246 | 686.8268 | 653.7557
3242.1292 | 638.5304 | 650.4659 | 683.2313 | 668.6866
3243.1292 | 638.4952 | 648.8856 | 676.865 | 662.5418
3244.1292 | 638.0305 | 644.5429 | 667.9568 | 655.9489
3245.1292 | 638.0252 | 640.2212 | 660.6758 | 654.8391
3246.1292 | 638.4597 | 641.7142 | 661.0521 | 654.2217
3247.1292 | 638.2949 | 644.2483 | 656.7639 | 646.3646
3248.1292 | 637.8029 | 648.1693 | 652.3688 | 643.6574
3249.1292 | 637.4616 | 644.6761 | 647.2487 | 641.1414
3250.1292 | 637.2835 | 642.0567 | 647.2239 | 655.3647
3251.1292 | 637.5946 | 645.743 | 644.6956 | 656.6734
3252.1292 | 637.5808 | 649.0046 | 648.5235 | 660.6735
3253.1292 | 637.4739 | 644.9877 | 646.3028 | 669.478
3254.1292 | 637.547 | 643.1103 | 646.6026 | 669.735
3255.1292 | 637.4195 | 650.1539 | 654.8234 | 672.966
3256.1292 | 637.5389 | 649.3424 | 661.3092 | 669.5198
3257.1292 | 637.6072 | 652.5815 | 659.0467 | 663.1419
3258.1292 | 638.017 | 649.1023 | 672.0068 | 666.5025
3259.1292 | 637.8018 | 653.4742 | 675.2699 | 665.0082
3260.1292 | 637.8871 | 652.3366 | 677.0589 | 661.0343
3261.1292 | 637.537 | 648.7131 | 679.6805 | 668.6589
3262.1292 | 637.6062 | 647.7474 | 680.2352 | 666.7851
3263.1292 | 637.8432 | 652.1076 | 674.7877 | 669.7706
3264.1292 | 637.7967 | 651.4738 | 671.9807 | 667.8977
3265.1292 | 638.2696 | 654.8407 | 673.2532 | 665.1416
3266.1292 | 639.4853 | 655.7393 | 666.7246 | 666.6003
3267.1292 | 640.1707 | 650.0853 | 659.5938 | 660.5105
3268.1292 | 640.2888 | 645.0286 | 654.9982 | 658.1619
3269.1292 | 640.3559 | 642.1311 | 652.1863 | 650.3982
3270.1292 | 640.2285 | 642.1071 | 650.2426 | 645.37
3271.1292 | 640.0785 | 654.6748 | 653.3164 | 639.3946
3272.1292 | 640.2615 | 654.5228 | 654.2968 | 645.8482
3273.1292 | 640.2728 | 648.8266 | 650.2863 | 649.0858
3274.1292 | 640.0317 | 653.0534 | 650.5757 | 651.3063
3275.1292 | 640.4171 | 662.9362 | 659.1672 | 659.4485
3276.1292 | 640.8159 | 662.5138 | 659.1037 | 661.1097
3277.1292 | 640.9585 | 657.0484 | 661.1191 | 666.2621
3278.1292 | 641.0441 | 651.9602 | 662.0366 | 662.4722
3279.1292 | 640.8653 | 647.6573 | 658.0741 | 668.0528
3280.1292 | 641.1713 | 652.634 | 655.5819 | 666.9268
3281.1292 | 640.7604 | 649.7592 | 649.4168 | 669.7139
3282.1292 | 640.6031 | 657.3858 | 644.8967 | 672.5663
3283.1292 | 640.1828 | 649.1818 | 641.5363 | 675.0139
3284.1292 | 639.941 | 643.3664 | 639.9099 | 675.8331
3285.1292 | 639.5766 | 652.6917 | 645.1641 | 673.832
3286.1292 | 639.1774 | 651.1709 | 653.1369 | 671.8346
3287.1292 | 638.2489 | 645.1903 | 652.4347 | 674.0357
3288.1292 | 637.7162 | 652.0833 | 652.6939 | 669.3989
3289.1292 | 636.943 | 654.456 | 654.8831 | 657.3421
3290.1292 | 636.6516 | 650.2835 | 657.7442 | 662.1013
3291.1292 | 635.8659 | 645.3756 | 672.4715 | 661.5039
3292.1292 | 636.8099 | 647.6317 | 672.0635 | 662.6506
3293.1292 | 637.0979 | 656.1869 | 678.4287 | 657.8501
3294.1292 | 637.4069 | 652.1756 | 674.1707 | 664.7957
3295.1292 | 637.5959 | 648.7665 | 671.6148 | 671.5141
3296.1292 | 637.7999 | 645.9593 | 671.095 | 671.6285
3297.1292 | 637.8192 | 643.7381 | 668.2001 | 672.9901
3298.1292 | 638.4355 | 650.9461 | 665.6275 | 674.0745
3299.1292 | 638.8607 | 657.1451 | 661.4614 | 676.8384
3300.1292 | 638.5233 | 655.3698 | 654.4044 | 666.7754
3301.1292 | 637.8092 | 650.303 | 655.1262 | 661.281
3302.1292 | 637.3298 | 647.7475 | 657.3464 | 667.8857
3303.1292 | 637.5976 | 644.7105 | 661.5899 | 666.459
3304.1292 | 637.4808 | 649.6598 | 667.3498 | 660.3883
3305.1292 | 636.7377 | 649.5048 | 673.6852 | 658.5418
3306.1292 | 636.5144 | 647.3324 | 672.8756 | 658.7373
3307.1292 | 635.9879 | 643.1001 | 677.4178 | 662.1157
3308.1292 | 635.9676 | 643.4699 | 682.5119 | 655.0036
3309.1292 | 635.9857 | 644.9944 | 674.4755 | 666.4254
3310.1292 | 636.7859 | 640.2985 | 665.8981 | 657.3711
3311.1292 | 636.7972 | 637.1305 | 657.6625 | 650.3449
3312.1292 | 637.9924 | 635.5031 | 657.1636 | 640.8867
3313.1292 | 638.5536 | 631.9796 | 652.4439 | 641.8411
3314.1292 | 638.1916 | 628.7018 | 646.0741 | 645.9029
3315.1292 | 638.7115 | 628.2457 | 645.3558 | 653.8651
3316.1292 | 638.911 | 625.3866 | 642.2394 | 657.2681
3317.1292 | 639.3514 | 623.8929 | 641.1936 | 647.9057
3318.1292 | 639.1334 | 626.4738 | 637.6033 | 642.863
3319.1292 | 639.5584 | 623.9084 | 634.4914 | 634.6435
3320.1292 | 638.9389 | 626.9131 | 637.3468 | 634.0971
3321.1292 | 638.9136 | 633.8179 | 635.1275 | 630.1105
3322.1292 | 639.4772 | 637.595 | 635.4266 | 627.3171
3323.1292 | 640.4359 | 633.7265 | 634.2937 | 621.8194
3324.1292 | 640.8898 | 633.188 | 635.7311 | 626.1166
3325.1292 | 640.8586 | 631.3816 | 634.1647 | 622.5605
3326.1292 | 640.4847 | 627.6614 | 633.7271 | 634.484
3327.1292 | 639.9009 | 628.1937 | 637.2423 | 644.9582
3328.1292 | 639.4778 | 627.0135 | 640.9568 | 653.4324
3329.1292 | 638.5208 | 629.8749 | 635.1636 | 643.8229
3330.1292 | 637.9297 | 630.0165 | 643.263 | 637.068
3331.1292 | 638.1853 | 627.4772 | 643.389 | 637.8302
3332.1292 | 638.4375 | 624.5344 | 640.2626 | 633.266
3333.1292 | 639.0854 | 623.1185 | 638.1547 | 631.7027
3334.1292 | 639.3268 | 623.0178 | 638.7801 | 628.8917
3335.1292 | 639.7335 | 633.2317 | 638.2396 | 625.4848
3336.1292 | 639.4096 | 642.1518 | 641.5904 | 624.5506
3337.1292 | 639.2807 | 637.8412 | 639.9665 | 628.1903
3338.1292 | 638.76 | 634.4284 | 635.7845 | 632.0239
3339.1292 | 638.6606 | 631.5191 | 632.9695 | 632.2358
3340.1292 | 638.6928 | 627.3658 | 630.3056 | 626.6126
3341.1292 | 638.9313 | 626.9974 | 631.1451 | 624.8735
3342.1292 | 638.7641 | 645.6939 | 632.6317 | 624.5226
3343.1292 | 638.3585 | 649.9607 | 634.0131 | 633.543
3344.1292 | 637.756 | 647.1428 | 635.061 | 636.8618
3345.1292 | 636.9835 | 647.1501 | 639.4472 | 635.3593
3346.1292 | 636.3418 | 646.589 | 637.6996 | 649.6067
3347.1292 | 635.1426 | 650.5196 | 639.4029 | 651.4337
3348.1292 | 634.3938 | 644.5179 | 634.8561 | 639.3366
3349.1292 | 634.4022 | 636.2314 | 631.0125 | 631.5277
3350.1292 | 633.4947 | 629.5636 | 627.8657 | 625.6594
3351.1292 | 634.1989 | 627.2753 | 625.6924 | 620.8468
3352.1292 | 634.7887 | 631.7931 | 624.5492 | 623.5345
3353.1292 | 635.2036 | 631.4227 | 625.0906 | 635.0298
3354.1292 | 634.718 | 630.4094 | 626.1342 | 636.656
3355.1292 | 634.4739 | 630.6961 | 631.4396 | 634.368
3356.1292 | 634.3394 | 628.8547 | 632.9409 | 637.4813
3357.1292 | 633.9186 | 625.7786 | 632.3284 | 641.6826
3358.1448 | 633.3139 | 622.8462 | 630.9206 | 646.6977
3359.1292 | 634.4048 | 621.7623 | 632.8067 | 654.1907
3360.1292 | 634.3762 | 618.8478 | 632.2079 | 659.159
3361.1292 | 634.2853 | 616.6353 | 632.0143 | 647.2689
3362.1292 | 634.0078 | 615.5876 | 637.8543 | 642.2955
3363.1292 | 633.9456 | 623.426 | 637.8474 | 647.3338
3364.1292 | 634.7877 | 629.5046 | 639.1728 | 648.7465
3365.1292 | 634.684 | 639.0612 | 638.1074 | 643.2393
3366.1292 | 634.5183 | 640.6903 | 636.8535 | 641.8403
3367.1292 | 635.2685 | 641.9972 | 643.9569 | 660.6364
3368.1292 | 635.6796 | 647.4158 | 644.2611 | 657.2439
3369.1292 | 635.9264 | 648.1385 | 646.5164 | 656.6235
3370.1292 | 636.2492 | 648.655 | 646.1554 | 652.2736
3371.1292 | 636.9871 | 641.6544 | 641.8598 | 655.4337
3372.1292 | 637.0726 | 636.7625 | 638.0348 | 653.7435
3373.1292 | 637.3536 | 632.7313 | 633.0844 | 657.437
3374.1292 | 637.3381 | 629.4183 | 634.4501 | 656.8381
3375.1292 | 638.585 | 627.3986 | 641.5543 | 657.571
3376.1292 | 639.4762 | 625.816 | 642.4108 | 663.805
3377.1292 | 641.3529 | 626.2596 | 651.1977 | 661.706
3378.1292 | 642.8828 | 629.4928 | 656.4361 | 658.8422
3379.1292 | 643.535 | 630.0266 | 652.041 | 659.0696
3380.1448 | 644.5064 | 630.761 | 649.9013 | 651.6891
3381.1292 | 643.6349 | 628.212 | 645.2984 | 645.3843
3382.1292 | 643.4794 | 626.6333 | 640.6618 | 642.7329
3383.1292 | 642.9042 | 623.7767 | 635.9682 | 635.1983
3384.1292 | 641.8927 | 624.8225 | 634.1279 | 628.6103
3385.1292 | 642.4362 | 621.8133 | 632.6302 | 636.5586
3386.1292 | 641.9468 | 619.4904 | 630.0675 | 632.9763
3387.1292 | 641.1384 | 616.4495 | 627.287 | 625.8486
3388.1448 | 641.246 | 614.3365 | 626.2442 | 627.5792
3389.1292 | 639.5721 | 613.2697 | 624.108 | 625.512
3390.1292 | 639.4427 | 609.7724 | 620.9887 | 617.4007
3391.1292 | 639.1635 | 607.9424 | 619.7736 | 611.8118
3392.1292 | 639.2823 | 620.8418 | 623.7404 | 613.5074
3393.1292 | 638.8771 | 616.6431 | 622.6251 | 607.5901
3394.1292 | 638.5416 | 618.7508 | 624.3269 | 605.7058
3395.1292 | 637.744 | 616.9007 | 622.4283 | 613.2385
3396.1292 | 636.8898 | 614.4189 | 623.9932 | 609.4048
3397.1292 | 637.1139 | 618.9115 | 624.6485 | 615.8773
3398.1292 | 636.3621 | 624.5306 | 622.7855 | 617.484
3399.1292 | 636.2034 | 622.846 | 624.5466 | 630.5978
3400.1292 | 636.1497 | 626.7396 | 623.591 | 635.623
3401.1292 | 635.6619 | 623.6958 | 623.6861 | 633.9619
3402.1292 | 634.8287 | 623.7935 | 629.2114 | 633.3049
3403.1292 | 634.4463 | 619.6735 | 635.39 | 625.2962
3404.1292 | 634.1402 | 615.9741 | 636.6275 | 624.6364
3405.1292 | 634.5548 | 614.1033 | 631.8235 | 631.7287
3406.1292 | 633.9836 | 613.4962 | 629.9274 | 637.1372
3407.1292 | 633.6314 | 614.8834 | 626.9075 | 633.4158
3408.1292 | 632.8587 | 615.8512 | 624.3859 | 637.4653
3409.1292 | 632.9461 | 618.0444 | 622.4287 | 630.7109
3410.1292 | 633.1367 | 616.7276 | 621.3651 | 634.4881
3411.1292 | 632.6565 | 619.3912 | 618.97 | 638.8804
3412.1292 | 632.296 | 617.4714 | 629.8812 | 640.626
3413.1292 | 632.0115 | 616.6223 | 637.1874 | 637.7218
3414.1292 | 632.357 | 615.1292 | 639.1853 | 640.3678
3415.1292 | 632.6653 | 612.3133 | 635.1434 | 639.4076
3416.1292 | 634.3236 | 613.2274 | 634.996 | 646.4062
3417.1292 | 635.296 | 611.908 | 634.361 | 653.2753
3418.1292 | 635.1102 | 611.1514 | 635.7415 | 649.3075
3419.1292 | 635.6131 | 618.4256 | 634.6513 | 651.8864
3420.1292 | 635.7043 | 624.6349 | 632.7523 | 662.543
3421.1292 | 635.8729 | 622.0336 | 628.4772 | 667.4805
3422.1292 | 635.8964 | 620.9417 | 629.4148 | 660.7195
3423.1292 | 637.4627 | 617.6597 | 627.1333 | 667.7918
3424.1292 | 638.3352 | 616.0404 | 628.414 | 664.4207
3425.1292 | 638.5959 | 615.4918 | 627.5477 | 655.2827
3426.1292 | 638.3947 | 612.3465 | 624.4213 | 643.5715
3427.1292 | 638.2184 | 609.4037 | 622.0536 | 637.9832
3428.1292 | 638.7202 | 609.2406 | 619.9889 | 630.6778
3429.1292 | 638.4208 | 608.0903 | 619.5617 | 625.5737
3430.1292 | 637.4918 | 607.7638 | 619.9902 | 636.8529
3431.1292 | 636.4434 | 604.9501 | 618.5431 | 639.466
3432.1292 | 637.1523 | 603.88 | 618.6482 | 636.7665
3433.1292 | 637.8889 | 605.3264 | 621.941 | 635.5471
3434.1292 | 638.7233 | 612.9829 | 625.3125 | 629.843
3435.1292 | 638.0053 | 618.2413 | 625.5604 | 622.3757
3436.1292 | 637.7998 | 620.8606 | 627.378 | 616.8478
3437.1292 | 637.4928 | 623.142 | 630.6733 | 619.6415
3438.1292 | 637.2188 | 621.291 | 632.0654 | 627.2127
3439.1292 | 636.6042 | 619.6511 | 629.4536 | 625.2916
3440.1448 | 635.9305 | 625.2726 | 630.7251 | 628.3984
3441.1292 | 636.1258 | 626.4373 | 637.6187 | 627.6458
3442.1292 | 635.5075 | 624.006 | 634.5867 | 627.3869
3443.1292 | 634.6713 | 620.5584 | 631.2406 | 632.8895
3444.1292 | 634.7301 | 617.0014 | 628.0682 | 637.8242
3445.1292 | 634.4854 | 619.9018 | 627.1493 | 635.3158
3446.1292 | 635.0522 | 616.5409 | 625.6264 | 630.155
3447.1292 | 635.1959 | 613.7822 | 622.7852 | 626.8909
3448.1292 | 634.9051 | 612.3278 | 621.6629 | 645.7025
3449.1292 | 634.9958 | 611.4382 | 618.2987 | 643.4752
3450.1292 | 635.9882 | 610.2748 | 616.8897 | 641.0376
3451.1292 | 637.4884 | 608.7646 | 618.2934 | 641.662
3452.1292 | 638.3773 | 607.0406 | 619.3403 | 635.2684
3453.1292 | 638.714 | 609.8338 | 618.4481 | 626.8396
3454.1292 | 638.6888 | 608.2394 | 617.3775 | 619.5063
3455.1292 | 638.3741 | 608.2265 | 614.6865 | 623.1455
3456.1292 | 637.7117 | 609.1919 | 616.1421 | 619.6066
3457.1292 | 636.9425 | 607.8327 | 616.0517 | 625.9267
3458.1292 | 636.9807 | 616.5693 | 623.5176 | 626.3276
3459.1292 | 637.6563 | 624.446 | 629.8216 | 630.9485
3460.1292 | 637.2951 | 633.0258 | 636.1377 | 631.619
3461.1292 | 637.3201 | 633.1341 | 632.9109 | 622.6645
3462.1292 | 636.6874 | 632.9838 | 632.3782 | 618.7861
3463.1292 | 636.206 | 628.8603 | 627.3182 | 625.8002
3464.1292 | 635.323 | 629.2862 | 627.8701 | 629.1073
3465.1292 | 636.1798 | 630.4736 | 625.3058 | 630.5823
3466.1292 | 636.6159 | 626.5966 | 622.7956 | 625.6099
3467.1292 | 637.9196 | 628.6924 | 622.8042 | 618.3449
3468.1292 | 638.0365 | 624.6967 | 622.0196 | 616.292
3469.1292 | 638.896 | 622.665 | 624.6289 | 612.605
3470.1292 | 638.8665 | 619.4959 | 623.3324 | 607.1419
3471.1292 | 640.0989 | 618.5322 | 623.0512 | 602.5718
3472.1292 | 641.1024 | 616.5957 | 621.1747 | 599.4196
3473.1292 | 641.2259 | 615.8608 | 622.42 | 596.6747
3474.1292 | 642.027 | 615.2516 | 620.3803 | 593.6238
3475.1292 | 641.7766 | 613.7021 | 620.1164 | 596.7854
3476.1292 | 642.4623 | 611.7026 | 619.4097 | 594.9122
3477.1292 | 641.1787 | 609.6258 | 618.213 | 598.0079
3478.1448 | 640.5301 | 606.4362 | 616.9834 | 595.2244
3479.1292 | 640.2509 | 603.1165 | 614.1506 | 592.4237
3480.1292 | 641.1959 | 603.2653 | 614.6303 | 589.4355
3481.1292 | 640.8801 | 601.9268 | 614.1558 | 588.8748
3482.1292 | 639.832 | 606.5661 | 614.5948 | 587.5187
3483.1292 | 639.2956 | 609.3871 | 613.261 | 584.01
3484.1292 | 638.2438 | 606.2635 | 611.7749 | 588.8537
3485.1292 | 637.4849 | 604.2286 | 613.0435 | 590.8709
3486.1292 | 637.6038 | 610.9346 | 616.4819 | 597.96
3487.1292 | 637.4287 | 611.8704 | 617.1197 | 595.3747
3488.1292 | 636.4319 | 610.0531 | 615.5359 | 597.0336
3489.1292 | 635.8502 | 610.5239 | 617.0857 | 597.2864
3490.1292 | 635.9917 | 617.5314 | 615.889 | 592.8839
3491.1292 | 635.722 | 615.9062 | 619.086 | 610.9889
3492.1292 | 635.2108 | 614.8112 | 618.4309 | 615.7247
3493.1292 | 635.7894 | 617.2106 | 623.0051 | 614.7824
3494.1292 | 635.2435 | 614.6931 | 620.138 | 614.235
3495.1292 | 635.1012 | 612.4971 | 617.9885 | 615.1946
3496.1292 | 634.6636 | 615.4915 | 615.1074 | 610.2697
3497.1292 | 634.7945 | 613.1811 | 612.3732 | 616.1793
3498.1292 | 634.5154 | 609.9532 | 610.9771 | 618.4546
3499.1292 | 634.66 | 608.6179 | 610.9621 | 611.215
3500.1448 | 634.6531 | 614.6928 | 609.5793 | 616.9201
3501.1292 | 634.9844 | 618.7462 | 611.7325 | 624.5291
3502.1292 | 634.9928 | 617.3217 | 613.343 | 627.5558
3503.1292 | 634.3013 | 614.5646 | 615.2614 | 631.2097
3504.1292 | 633.4551 | 611.5304 | 611.7353 | 628.8652
3505.1292 | 633.3191 | 633.4188 | 613.129 | 623.1656
3506.1292 | 633.159 | 631.3729 | 611.7152 | 614.8652
3507.1292 | 633.6376 | 626.5077 | 613.1997 | 618.002
3508.1448 | 633.5067 | 624.2959 | 611.8343 | 622.961
3509.1292 | 633.386 | 622.2962 | 612.1936 | 622.4858
3510.1292 | 633.4565 | 621.8465 | 612.0751 | 617.7398
3511.1292 | 633.9958 | 620.1119 | 611.1017 | 615.9924
3512.1292 | 633.7959 | 619.331 | 610.2912 | 615.4313
3513.1292 | 633.9868 | 616.8668 | 609.4242 | 614.8855
3514.1292 | 634.4593 | 624.2171 | 612.8517 | 613.5989
3515.1292 | 635.511 | 621.5263 | 613.6185 | 612.1748
3516.1292 | 636.1147 | 621.6162 | 615.6065 | 613.6008
3517.1292 | 635.8811 | 622.2629 | 615.1241 | 605.6068
3518.1292 | 635.8655 | 620.7884 | 613.2364 | 601.3494
3519.1292 | 635.8591 | 629.1627 | 614.2584 | 603.5371
3520.1292 | 635.3717 | 625.8768 | 611.1306 | 598.9024
3521.1292 | 635.0994 | 621.9877 | 608.1884 | 607.7471
3522.1292 | 635.4762 | 619.5339 | 607.2834 | 607.0897
3523.1292 | 636.1219 | 617.7427 | 608.1251 | 610.2326
3524.1292 | 637.5627 | 620.3881 | 610.7402 | 607.1427
3525.1292 | 636.9579 | 623.173 | 614.3081 | 605.4623
3526.1292 | 637.2625 | 631.7148 | 616.2979 | 606.1518
3527.1292 | 635.8949 | 627.8787 | 615.4243 | 609.1763
3528.1292 | 636.1686 | 628.2375 | 614.7343 | 609.2888
3529.1292 | 636.9505 | 629.2216 | 618.0152 | 613.3151
3530.1292 | 636.9222 | 629.6196 | 622.7775 | 613.4726
3531.1292 | 636.8978 | 632.2856 | 623.2312 | 616.0075
3532.1292 | 637.497 | 635.5604 | 628.1861 | 610.6574
3533.1292 | 637.609 | 634.8327 | 628.6885 | 606.7136
3534.1292 | 637.2417 | 632.9587 | 625.1645 | 608.0166
3535.1292 | 636.908 | 630.346 | 623.2355 | 606.0033
3536.1292 | 636.767 | 626.8917 | 622.5108 | 605.0713
3537.1292 | 636.4032 | 629.4175 | 620.4141 | 608.0793
3538.1292 | 636.8233 | 634.5328 | 620.092 | 611.1344
3539.1292 | 636.6487 | 630.0139 | 619.9467 | 623.0826
3540.1292 | 636.8228 | 626.3327 | 617.069 | 614.6506
3541.1292 | 636.7288 | 624.0915 | 616.9614 | 608.5158
3542.1292 | 636.8982 | 621.3222 | 616.8513 | 611.5289
3543.1292 | 636.6833 | 625.5658 | 617.1698 | 613.5218
3544.1292 | 637.1071 | 631.09 | 616.7222 | 609.5697
3545.1292 | 637.1823 | 626.0263 | 614.7673 | 602.66
3546.1292 | 636.9748 | 624.5626 | 614.7065 | 598.8682
3547.1292 | 637.2434 | 623.2442 | 615.6462 | 603.0369
3548.1292 | 637.5012 | 621.1948 | 617.7687 | 602.6346
3549.1292 | 637.521 | 618.2792 | 616.5423 | 603.2548
3550.1292 | 637.6306 | 617.1457 | 614.9918 | 597.6836
3551.1292 | 638.7897 | 616.4494 | 614.1483 | 593.2995
3552.1292 | 638.8614 | 621.7666 | 615.1603 | 604.0034
3553.1292 | 638.5435 | 620.7661 | 613.4876 | 597.4966
3554.1292 | 638.5568 | 624.0749 | 612.3918 | 593.225
3555.1292 | 638.6923 | 622.9621 | 610.1911 | 590.0771
3556.1292 | 639.221 | 620.3706 | 612.2008 | 596.6299
3557.1292 | 640.5581 | 622.6031 | 617.3483 | 602.465
3558.1292 | 640.1815 | 620.9145 | 618.0234 | 601.1906
3559.1292 | 639.5972 | 615.8465 | 616.3934 | 601.9176
3560.1448 | 637.9606 | 626.3127 | 619.1102 | 606.2891
3561.1292 | 639.3376 | 632.1615 | 622.076 | 610.1272
3562.1292 | 638.2325 | 632.4898 | 621.7633 | 607.984
3563.1292 | 638.3129 | 637.1027 | 620.979 | 604.0611
3564.1292 | 638.5809 | 642.8225 | 622.1859 | 602.8358
3565.1292 | 637.6943 | 648.3134 | 621.8332 | 595.8754
3566.1292 | 636.0915 | 647.6774 | 616.355 | 590.4113
3567.1292 | 635.4495 | 646.1846 | 613.5221 | 587.581
3568.1292 | 635.7658 | 639.3957 | 612.8133 | 584.4544
3569.1292 | 635.0916 | 634.1541 | 610.653 | 581.9311
3570.1292 | 635.4411 | 643.5846 | 610.4057 | 579.0987
3571.1292 | 636.0799 | 636.7644 | 610.3426 | 575.6636
3572.1292 | 636.7297 | 631.9399 | 610.395 | 574.1711
3573.1292 | 636.9075 | 633.2454 | 610.956 | 586.4165
3574.1292 | 637.6378 | 631.137 | 611.1959 | 588.0985
3575.1292 | 637.4214 | 627.0786 | 609.2417 | 590.3692
3576.1292 | 636.8915 | 624.6812 | 607.0866 | 590.6836
3577.1448 | 636.7951 | 620.9254 | 606.3763 | 592.3956
3578.1292 | 637.2287 | 627.3589 | 609.7619 | 591.118
3579.1292 | 636.9154 | 632.9938 | 610.0097 | 593.3501
3580.1292 | 636.5522 | 632.5555 | 613.3991 | 589.412
3581.1292 | 636.3625 | 633.3676 | 611.2978 | 592.0706
3582.1292 | 636.5351 | 633.9824 | 609.8086 | 594.4535
3583.1292 | 636.0746 | 629.194 | 608.273 | 602.2107
3584.1292 | 636.1568 | 632.8219 | 607.5766 | 606.6408
3585.1292 | 636.4017 | 631.3118 | 606.9991 | 603.9251
3586.1292 | 636.9059 | 638.3015 | 607.3745 | 601.1617
3587.1292 | 637.1545 | 640.0861 | 606.0152 | 596.2874
3588.1292 | 637.1844 | 636.822 | 608.516 | 597.4623
3589.1292 | 636.8033 | 639.2189 | 609.5936 | 600.4052
3590.1292 | 636.8985 | 646.4061 | 611.096 | 603.2012
3591.1292 | 637.1505 | 641.0574 | 611.8861 | 599.1399
3592.1292 | 636.9387 | 636.069 | 614.9946 | 597.3555
3593.1292 | 637.9638 | 638.6385 | 617.0891 | 594.4658
3594.1292 | 638.3223 | 638.6833 | 614.0105 | 591.9812
3595.1292 | 637.3682 | 633.2902 | 611.4826 | 597.3574
3596.1292 | 636.7404 | 627.1113 | 608.8472 | 598.5906
3597.1292 | 636.5004 | 622.2949 | 607.9951 | 606.8591
3598.1292 | 636.9979 | 619.9965 | 607.2319 | 606.6054
3599.1292 | 637.2754 | 623.0687 | 607.317 | 601.7354
3600.1292 | 639.4518 | 620.9544 | 610.8489 | 598.7527
3601.1292 | 639.8842 | 617.1206 | 609.5984 | 594.8405
3602.1292 | 640.4486 | 617.6006 | 609.7176 | 589.7397
3603.1292 | 640.4681 | 618.1606 | 607.7885 | 591.0779
3604.1292 | 639.9164 | 618.5586 | 607.3505 | 587.6458
3605.1292 | 640.41 | 616.9451 | 607.6052 | 589.258
3606.1292 | 639.7802 | 615.6971 | 605.9041 | 586.0562
3607.1292 | 638.9881 | 612.2364 | 603.7645 | 583.7114
3608.1292 | 639.0657 | 610.9821 | 603.5479 | 588.0267
3609.1292 | 638.8654 | 609.6162 | 603.535 | 585.8587
3610.1292 | 638.0954 | 610.4932 | 603.9303 | 588.2618
3611.1292 | 638.3224 | 611.2092 | 604.8929 | 588.548
3612.1292 | 637.6302 | 609.9545 | 604.1797 | 589.0102
3613.1292 | 636.6568 | 616.91 | 602.7008 | 586.0115
3614.1292 | 636.3464 | 614.2335 | 601.382 | 584.6926
3615.1292 | 636.7055 | 615.9136 | 601.5732 | 582.4207
3616.1292 | 637.2106 | 619.942 | 603.3971 | 584.8658
3617.1292 | 637.6717 | 619.7833 | 605.1251 | 584.8457
3618.1292 | 637.9791 | 626.3589 | 606.2462 | 583.8554
3619.1292 | 637.1772 | 637.137 | 606.889 | 583.7903
3620.1292 | 637.9045 | 640.0372 | 610.3421 | 583.8035
3621.1292 | 638.4181 | 645.2379 | 612.378 | 583.8386
3622.1292 | 638.1854 | 639.9985 | 613.0696 | 584.0069
3623.1292 | 636.8205 | 638.7013 | 611.5774 | 582.7295
3624.1292 | 636.4374 | 649.4888 | 612.7924 | 581.2622
3625.1292 | 637.3501 | 657.4329 | 616.4678 | 582.3321
3626.1292 | 638.2769 | 662.5719 | 618.6998 | 582.8893
3627.1292 | 638.2593 | 665.8221 | 616.5577 | 579.8436
3628.1292 | 637.4976 | 663.9828 | 618.0521 | 578.6534
3629.1292 | 636.8851 | 657.0837 | 617.3355 | 582.8645
3630.1292 | 637.6153 | 647.7096 | 614.802 | 585.284
3631.1292 | 637.4 | 643.2731 | 614.0287 | 582.9321
3632.1292 | 637.2918 | 637.5318 | 612.285 | 588.6758
3633.1292 | 637.5222 | 634.7376 | 611.4383 | 590.1746
3634.1292 | 637.497 | 644.9499 | 611.5005 | 587.9529
3635.1292 | 637.3484 | 648.6652 | 610.4578 | 584.5839
3636.1292 | 637.0327 | 650.3382 | 610.7059 | 581.5353
3637.1292 | 636.7564 | 646.6009 | 610.2764 | 582.0125
3638.1292 | 637.534 | 647.3611 | 614.9002 | 579.4825
3639.1292 | 638.1571 | 645.1233 | 614.6089 | 584.3743
3640.1292 | 638.1074 | 640.487 | 613.8173 | 582.6717
3641.1292 | 637.7899 | 637.7368 | 616.3147 | 588.7105
3642.1292 | 638.3115 | 640.2575 | 614.7534 | 585.9734
3643.1292 | 639.1331 | 641.3222 | 616.27 | 584.018
3644.1292 | 639.0131 | 643.469 | 617.6043 | 583.3376
3645.1292 | 639.0774 | 650.8895 | 617.1964 | 581.681
3646.1292 | 638.0351 | 655.6699 | 614.9506 | 581.5094
3647.1292 | 638.0594 | 652.2325 | 620.358 | 584.6405
3648.1292 | 637.9146 | 656.9667 | 620.7666 | 597.2821
3649.1292 | 637.9357 | 663.9546 | 618.1506 | 593.5801
3650.1292 | 637.2729 | 660.0611 | 617.0225 | 589.1776
3651.1292 | 637.1491 | 656.1931 | 616.1165 | 590.8416
3652.1292 | 637.4699 | 652.0442 | 616.0333 | 589.4953
3653.1292 | 638.3222 | 649.8732 | 617.7353 | 588.2476
3654.1292 | 638.1554 | 648.9848 | 616.6883 | 587.7639
3655.1292 | 638.1189 | 649.0055 | 616.6875 | 583.6192
3656.1292 | 637.9091 | 645.1366 | 615.5476 | 585.6798
3657.1292 | 636.9682 | 640.9647 | 615.0703 | 588.3548
3658.1448 | 636.7749 | 640.415 | 611.6038 | 587.5079
3659.1292 | 636.5994 | 640.0136 | 611.8307 | 586.8676
3660.1292 | 636.6073 | 635.3857 | 610.6102 | 590.6442
3661.1292 | 635.8857 | 630.5416 | 608.2175 | 593.3874
3662.1292 | 635.8787 | 626.1682 | 607.3241 | 593.3833
3663.1292 | 635.884 | 622.2843 | 607.6791 | 592.6697
3664.1292 | 636.1657 | 624.3099 | 609.9251 | 589.0776
3665.1292 | 636.3351 | 624.5142 | 609.2802 | 585.7918
3666.1292 | 636.0674 | 626.1787 | 609.3242 | 582.4689
3667.1292 | 635.5867 | 634.8948 | 607.8871 | 579.3273
3668.1292 | 635.3333 | 645.3594 | 605.3765 | 577.2325
3669.1292 | 635.6435 | 642.0597 | 606.142 | 577.0262
3670.1292 | 636.3992 | 645.0127 | 610.2654 | 586.5283
3671.1292 | 636.2797 | 645.8757 | 610.8294 | 582.9936
3672.1292 | 635.9595 | 651.4727 | 608.9325 | 578.2992
3673.1292 | 635.3308 | 644.8526 | 610.2036 | 574.8322
3674.1292 | 635.1906 | 638.3846 | 608.7159 | 578.7777
3675.1292 | 635.7885 | 637.9744 | 610.2569 | 588.4342
3676.1292 | 636.0267 | 640.4399 | 610.048 | 586.2489
3677.1292 | 636.6771 | 650.8397 | 611.8224 | 586.2158
3678.1292 | 636.8381 | 654.8574 | 612.0433 | 583.3265
3679.1292 | 637.2591 | 659.8716 | 614.2194 | 584.9174
3680.1292 | 637.0236 | 659.6036 | 617.988 | 585.0658
3681.1292 | 636.9067 | 659.0059 | 616.9066 | 582.606
3682.1292 | 637.8737 | 664.4083 | 616.5556 | 583.2716
3683.1292 | 637.6481 | 662.3833 | 617.8419 | 581.4693
3684.1292 | 636.1823 | 658.8307 | 615.8624 | 579.6136
3685.1292 | 635.9259 | 656.9367 | 615.2605 | 579.8096
3686.1292 | 635.9764 | 658.1081 | 613.4483 | 583.0526
3687.1292 | 636.1385 | 651.8485 | 612.6636 | 583.5994
3688.1292 | 635.9592 | 648.327 | 613.1894 | 581.767
3689.1292 | 636.0441 | 644.3608 | 611.5624 | 580.7567
3690.1292 | 636.5795 | 642.5179 | 610.9377 | 578.8996
3691.1292 | 636.8566 | 638.9304 | 609.4423 | 575.2075
3692.1292 | 636.6943 | 633.9635 | 608.2495 | 572.6166
3693.1292 | 636.3522 | 630.0679 | 604.9215 | 569.3345
3694.1292 | 635.1793 | 626.8756 | 604.726 | 576.6974
3695.1292 | 634.8033 | 630.4778 | 605.3166 | 578.6814
3696.1292 | 634.7453 | 627.3376 | 602.7298 | 577.1582
3697.1292 | 634.4096 | 625.5513 | 602.1026 | 575.1269
3698.1292 | 635.3026 | 625.8978 | 599.9787 | 578.1144
3699.1292 | 636.3722 | 624.2498 | 601.9487 | 576.5984
3700.1292 | 636.3569 | 621.9196 | 602.5486 | 575.6191
3701.1292 | 636.0117 | 618.4992 | 603.6913 | 574.2114
3702.1292 | 635.8577 | 631.0095 | 603.0788 | 574.4036
3703.1292 | 636.2922 | 643.0973 | 606.3202 | 575.3864
3704.1292 | 635.7232 | 646.6017 | 609.4825 | 578.5042
3705.1292 | 635.6827 | 649.2145 | 609.4429 | 577.0068
3706.1292 | 635.796 | 647.4812 | 607.5889 | 577.4098
3707.1292 | 635.2596 | 643.6575 | 606.6651 | 576.3528
3708.1292 | 635.0762 | 636.9669 | 604.536 | 572.9577
3709.1292 | 634.714 | 636.3569 | 604.3492 | 571.9714
3710.1292 | 633.7965 | 631.8619 | 603.3648 | 570.6293
3711.1292 | 633.8778 | 625.6982 | 600.9347 | 568.7575
3712.1292 | 634.0544 | 620.9119 | 600.4194 | 569.3298
3713.1292 | 633.9776 | 617.8721 | 599.9877 | 573.2485
3714.1292 | 634.4645 | 619.4617 | 600.3817 | 571.1676
3715.1292 | 634.1721 | 624.1228 | 600.8407 | 571.3048
3716.1292 | 633.996 | 621.277 | 600.4 | 576.1517
3717.1292 | 634.484 | 616.4624 | 599.4702 | 574.0849
3718.1292 | 634.4126 | 615.4826 | 597.9024 | 572.9911
3719.1292 | 634.5661 | 614.0472 | 597.5778 | 576.8498
3720.1292 | 635.2361 | 611.5937 | 596.7266 | 586.8608
3721.1292 | 635.9168 | 610.6149 | 597.1827 | 586.0318
3722.1292 | 637.9854 | 612.2524 | 599.1646 | 582.0956
3723.1292 | 638.6647 | 615.8577 | 600.0694 | 587.7601
3724.1292 | 637.964 | 616.9687 | 600.3544 | 583.9514
3725.1292 | 637.3486 | 620.5248 | 599.6266 | 585.2197
3726.1292 | 637.0157 | 621.0743 | 598.8635 | 580.247
3727.1292 | 636.749 | 620.9258 | 597.3181 | 578.2364
3728.1292 | 635.8883 | 619.6299 | 596.9232 | 575.1672
3729.1292 | 635.2106 | 616.0722 | 595.6967 | 575.2999
3730.1292 | 635.4836 | 612.8433 | 595.1528 | 575.3587
3731.1292 | 635.9253 | 612.5276 | 594.9145 | 576.0572
3732.1292 | 635.7035 | 610.6192 | 596.2641 | 575.5545
3733.1292 | 635.3844 | 608.3826 | 595.873 | 572.9502
3734.1292 | 636.0134 | 618.3462 | 599.8603 | 571.799
3735.1292 | 635.5445 | 616.6658 | 599.1695 | 569.0204
3736.1292 | 636.0681 | 615.7212 | 600.4514 | 567.5984
3737.1292 | 636.5754 | 616.198 | 600.8166 | 567.2692
3738.1292 | 636.6905 | 616.3897 | 600.7296 | 565.9434
3739.1292 | 636.4138 | 614.9513 | 600.8335 | 567.0357
3740.1292 | 636.2464 | 616.3697 | 600.9821 | 568.5313
3741.1292 | 636.5005 | 617.2647 | 602.0651 | 570.8763
3742.1292 | 636.1802 | 623.2106 | 601.4184 | 573.8847
3743.1292 | 635.3359 | 622.7548 | 599.907 | 572.8799
3744.1292 | 635.4386 | 620.9959 | 599.9849 | 570.8923
3745.1448 | 635.203 | 627.4225 | 598.8186 | 579.7468
3746.1292 | 635.3119 | 631.1399 | 597.5436 | 580.5324
3747.1292 | 634.0474 | 625.2339 | 597.0735 | 576.982
3748.1292 | 633.8398 | 625.9986 | 597.2069 | 584.2348
3749.1292 | 634.2651 | 622.1149 | 596.1989 | 581.2808
3750.1292 | 634.3316 | 618.4484 | 595.2528 | 577.018
3751.1292 | 635.2859 | 616.6491 | 593.955 | 571.7659
3752.1292 | 636.1016 | 613.6063 | 594.8124 | 579.2231
3753.1292 | 636.2974 | 611.7656 | 595.8215 | 578.2871
3754.1292 | 635.923 | 609.9335 | 594.7984 | 575.4828
3755.1292 | 635.8858 | 610.883 | 595.192 | 571.4167
3756.1292 | 635.468 | 610.3116 | 594.3209 | 571.6451
3757.1292 | 635.4948 | 609.9691 | 592.9531 | 576.1992
3758.1292 | 635.8511 | 614.9924 | 593.4718 | 572.3336
3759.1292 | 634.7016 | 616.3398 | 592.8522 | 569.5021
3760.1292 | 634.2503 | 613.3703 | 591.7445 | 570.7091
3761.1292 | 634.7029 | 609.9915 | 591.6924 | 571.6954
3762.1292 | 636.0381 | 608.8569 | 594.4703 | 576.2175
3763.1292 | 637.0087 | 608.9836 | 597.9818 | 576.8197
3764.1292 | 637.2282 | 608.0172 | 598.0053 | 574.5995
3765.1292 | 638.3912 | 609.1147 | 598.7537 | 572.0256
3766.1292 | 639.0227 | 611.0387 | 598.4425 | 571.0127
3767.1292 | 637.6674 | 610.9392 | 597.4082 | 572.9284
3768.1292 | 638.222 | 611.1568 | 596.7228 | 573.3675
3769.1448 | 638.0396 | 608.767 | 596.0217 | 569.7446
3770.1292 | 638.028 | 608.4253 | 594.833 | 570.6338
3771.1448 | 637.8074 | 608.8693 | 594.4619 | 567.4953
3772.1292 | 637.5993 | 607.604 | 593.8164 | 564.9869
3773.1292 | 637.4186 | 605.6139 | 593.92 | 564.2685
3774.1292 | 637.043 | 605.8539 | 593.8822 | 562.5715
3775.1292 | 635.8082 | 605.3658 | 592.4555 | 559.2455
3776.1292 | 635.4052 | 604.1406 | 591.9719 | 558.8032
3777.1292 | 635.4566 | 603.2915 | 592.4352 | 562.5612
3778.1292 | 635.4933 | 603.4686 | 592.0701 | 569.6251
3779.1292 | 635.1383 | 603.249 | 591.4434 | 574.1509
3780.1292 | 635.7889 | 604.9715 | 593.1584 | 575.3725
3781.1292 | 634.5983 | 604.7437 | 591.5775 | 573.1576
3782.1292 | 634.02 | 607.9257 | 591.9901 | 569.1911
3783.1292 | 633.5846 | 610.2164 | 589.1633 | 566.0222
3784.1292 | 633.9569 | 612.1954 | 589.8822 | 566.9425
3785.1292 | 634.7155 | 614.166 | 592.9701 | 567.3187
3786.1292 | 634.2956 | 612.7849 | 591.6175 | 563.253
3787.1292 | 633.7527 | 612.5326 | 590.9764 | 560.1438
3788.1292 | 633.506 | 611.6345 | 591.4436 | 559.8285
3789.1292 | 633.7473 | 608.7083 | 590.5932 | 567.3048
3790.1292 | 634.8103 | 607.1832 | 591.4331 | 564.9541
3791.1292 | 636.0596 | 609.7399 | 592.5793 | 563.5747
3792.1292 | 636.9502 | 611.6713 | 592.6069 | 566.7716
3793.1292 | 638.8105 | 610.8222 | 594.4624 | 564.6059
3794.1292 | 639.8966 | 612.1822 | 595.5673 | 565.2828
3795.1292 | 638.9759 | 611.3396 | 594.8119 | 567.1682
3796.1292 | 640.2849 | 610.2732 | 595.2143 | 565.8544
3797.1292 | 639.7118 | 611.1101 | 595.7227 | 565.031
3798.1292 | 638.7868 | 611.8795 | 594.6697 | 563.8722
3799.1292 | 638.1204 | 611.4435 | 593.2216 | 568.7798
3800.1292 | 638.1621 | 609.9862 | 591.7249 | 565.0707
3801.1292 | 638.0355 | 608.7474 | 591.1273 | 564.768
3802.1292 | 637.4687 | 610.0209 | 591.3414 | 564.7636
3803.1292 | 637.4657 | 613.8389 | 591.1257 | 567.276
3804.1292 | 637.1302 | 612.3829 | 592.8535 | 566.1678
3805.1292 | 637.7388 | 609.9057 | 593.3135 | 564.7657
3806.1292 | 639.6832 | 607.6456 | 594.6812 | 567.3862
3807.1292 | 640.8249 | 612.6895 | 596.4562 | 565.1861
3808.1292 | 640.2697 | 612.38 | 594.8123 | 562.8241
3809.1292 | 641.1415 | 609.9068 | 595.3835 | 561.6748
3810.1292 | 642.7421 | 609.9417 | 595.9705 | 561.1021
3811.1292 | 642.3379 | 611.2277 | 595.3944 | 558.8458
3812.1292 | 642.2627 | 610.9837 | 595.6696 | 563.8832
3813.1292 | 643.9479 | 609.2001 | 598.2245 | 565.4487
3814.1292 | 645.3012 | 609.7608 | 599.986 | 563.5806
3815.1292 | 645.1404 | 611.7935 | 600.8782 | 563.0078
3816.1292 | 644.9937 | 611.6105 | 600.0473 | 561.8111
3817.1292 | 644.0849 | 612.2707 | 601.9851 | 562.5224
3818.1292 | 643.2792 | 617.3986 | 602.8898 | 562.8184
3819.1292 | 643.0411 | 614.2505 | 601.2255 | 560.9354
3820.1292 | 642.0312 | 612.8632 | 600.9594 | 558.8333
3821.1292 | 641.9058 | 612.4952 | 600.7647 | 558.0885
3822.1292 | 641.5151 | 616.1654 | 602.1147 | 557.2193
3823.1292 | 640.1788 | 614.0971 | 599.0196 | 555.3243
3824.1292 | 639.2133 | 614.3117 | 598.1158 | 552.6673
3825.1292 | 638.2531 | 615.8741 | 596.1414 | 550.1007
3826.1292 | 637.3175 | 613.4521 | 594.405 | 548.2608
3827.1292 | 636.2108 | 609.8901 | 593.0475 | 547.0247
3828.1292 | 636.7068 | 608.353 | 593.8444 | 545.6726
3829.1292 | 637.4097 | 611.9301 | 596.2735 | 547.0215
3830.1292 | 637.5664 | 615.4372 | 598.0855 | 549.3967
3831.1292 | 637.8269 | 614.6387 | 598.9899 | 549.3594
3832.1292 | 637.5934 | 613.6065 | 598.5451 | 549.5052
3833.1292 | 637.0902 | 615.9905 | 598.8987 | 556.1489
3834.1292 | 637.3482 | 616.0229 | 599.2926 | 556.5052
3835.1292 | 637.259 | 616.6472 | 599.5018 | 558.5726
3836.1292 | 637.1925 | 617.4773 | 599.0732 | 559.3802
3837.1292 | 636.5871 | 621.2834 | 597.4838 | 558.8632
3838.1292 | 635.4913 | 620.4374 | 595.7872 | 558.4972
3839.1292 | 634.3953 | 618.4596 | 593.4625 | 556.0097
3840.1292 | 634.2979 | 619.6726 | 593.2267 | 555.8891
3841.1292 | 634.1867 | 617.6887 | 593.0055 | 555.7269
3842.1292 | 634.4285 | 615.5925 | 592.171 | 555.7404
3843.1292 | 634.6376 | 615.0109 | 592.5781 | 554.9289
3844.1292 | 634.9905 | 615.1412 | 594.3985 | 555.9785
3845.1292 | 634.9902 | 614.938 | 595.9077 | 558.4837
3846.1292 | 634.4046 | 616.8556 | 594.4938 | 558.5602
3847.1292 | 634.8039 | 615.2046 | 594.6397 | 557.0305
3848.1292 | 634.5286 | 612.7001 | 595.6144 | 558.6885
3849.1292 | 635.5825 | 611.6815 | 598.4051 | 560.9805
3850.1292 | 635.2144 | 609.7351 | 598.6383 | 560.7347
3851.1292 | 635.2937 | 607.9129 | 599.1846 | 559.876
3852.1292 | 634.0382 | 611.4392 | 598.2487 | 558.6466
3853.1292 | 633.7438 | 610.196 | 600.733 | 561.5073
3854.1292 | 634.1603 | 609.7877 | 604.1551 | 564.5627
3855.1292 | 634.3367 | 610.7633 | 604.896 | 562.7789
3856.1292 | 633.8499 | 609.952 | 604.5632 | 565.9675
3857.1292 | 633.7076 | 611.8034 | 604.8447 | 562.9055
3858.1292 | 634.6901 | 611.664 | 605.8399 | 561.2578
3859.1292 | 634.1429 | 614.923 | 606.5256 | 559.2818
3860.1292 | 635.3967 | 612.0226 | 604.9169 | 558.1229
3861.1292 | 635.9951 | 611.4179 | 606.05 | 556.6447
3862.1292 | 635.5343 | 610.5615 | 606.6432 | 557.5599
3863.1292 | 634.8122 | 610.9771 | 605.607 | 556.1659
3864.1292 | 635.5509 | 608.4462 | 604.1438 | 554.3062
3865.1292 | 634.9329 | 607.0917 | 603.761 | 553.4878
3866.1292 | 634.3612 | 605.6491 | 601.7153 | 552.2033
3867.1292 | 634.1734 | 602.8563 | 600.4126 | 550.0281
3868.1292 | 633.5269 | 602.8425 | 599.8814 | 549.987
3869.1292 | 633.5309 | 600.9623 | 598.3943 | 549.5213
3870.1292 | 634.8769 | 600.5689 | 600.2328 | 550.046
3871.1292 | 635.5795 | 601.6841 | 600.8308 | 550.0902
3872.1292 | 634.7817 | 600.4935 | 600.3413 | 548.6059
3873.1292 | 634.6667 | 599.0195 | 599.2768 | 547.392
3874.1292 | 634.2272 | 597.5409 | 598.5715 | 547.7113
3875.1292 | 633.2937 | 596.0089 | 596.7426 | 545.5572
3876.1292 | 632.4887 | 596.997 | 595.7813 | 543.7128
3877.1292 | 632.1567 | 597.5247 | 594.5037 | 542.6761
3878.1292 | 631.9487 | 597.8277 | 594.117 | 542.381
3879.1292 | 632.4387 | 596.7288 | 594.9938 | 542.3475
3880.1292 | 632.2587 | 595.5002 | 595.6773 | 543.7216
3881.1292 | 632.0239 | 594.402 | 596.8316 | 544.5585
3882.1292 | 631.5977 | 596.7452 | 599.0661 | 546.3408
3883.1292 | 631.7894 | 596.701 | 600.0121 | 547.8706
3884.1292 | 632.4915 | 596.1647 | 598.6583 | 548.7795
3885.1292 | 632.1782 | 596.2044 | 599.0866 | 555.8965
3886.1292 | 632.1624 | 600.7121 | 596.8054 | 559.4599
3887.1292 | 632.3392 | 600.6372 | 596.2292 | 556.4264
3888.1292 | 632.2323 | 599.0163 | 595.3827 | 555.0851
3889.1292 | 632.1677 | 598.618 | 596.2754 | 561.5585
3890.1292 | 633.0667 | 597.5753 | 598.0763 | 560.2746
3891.1292 | 632.335 | 595.7748 | 597.3836 | 559.2491
3892.1292 | 632.9819 | 596.6924 | 597.0522 | 557.2324
3893.1292 | 632.7617 | 597.087 | 597.85 | 556.283
3894.1292 | 631.9556 | 596.7325 | 596.3185 | 556.751
3895.1292 | 632.2334 | 596.6153 | 597.7365 | 556.3865
3896.1292 | 632.8704 | 595.9641 | 596.6269 | 554.7379
3897.1292 | 633.4068 | 594.1732 | 595.7381 | 553.5257
3898.1292 | 632.7217 | 594.675 | 595.3122 | 555.858
3899.1292 | 632.2101 | 593.0427 | 593.7335 | 554.6687
3900.1292 | 632.5754 | 592.4168 | 592.552 | 554.4338
3901.1292 | 632.2206 | 596.9334 | 593.4061 | 556.9107
3902.1292 | 632.9294 | 598.185 | 593.6398 | 557.0574
3903.1292 | 633.3364 | 600.8493 | 594.2774 | 557.0728
3904.1292 | 633.9355 | 601.2093 | 598.2238 | 557.5983
3905.1292 | 634.4886 | 599.0816 | 597.9157 | 557.9812
3906.1292 | 634.4621 | 597.5937 | 597.2243 | 558.1699
3907.1292 | 634.2149 | 599.0698 | 597.0738 | 556.1454
3908.1292 | 633.9855 | 598.4953 | 595.6771 | 555.2766
3909.1292 | 634.835 | 597.3094 | 595.2542 | 553.8722
3910.1292 | 635.8301 | 597.3719 | 595.7071 | 554.37
3911.1292 | 636.1056 | 597.7584 | 596.0489 | 555.0318
3912.1292 | 636.5263 | 596.9381 | 596.6619 | 554.9719
3913.1292 | 636.4902 | 595.7512 | 596.6558 | 556.7299
3914.1292 | 636.2732 | 594.5996 | 596.2647 | 558.8661
3915.1292 | 635.4951 | 592.788 | 594.2395 | 556.4262
3916.1292 | 635.7159 | 593.4574 | 595.9358 | 555.3187
3917.1292 | 636.3214 | 595.4615 | 596.6206 | 556.8476
3918.1292 | 635.9441 | 596.0479 | 597.0746 | 563.9543
3919.1292 | 636.5868 | 596.3235 | 597.5775 | 562.0263
3920.1292 | 636.7341 | 597.9838 | 599.6077 | 561.8063
3921.1292 | 636.8815 | 599.3964 | 601.9494 | 562.0076
3922.1292 | 635.996 | 604.4922 | 601.0409 | 561.024
3923.1292 | 635.9226 | 601.9374 | 599.498 | 559.1489
3924.1292 | 635.9693 | 601.4544 | 598.9762 | 563.4876
3925.1292 | 635.7383 | 601.8259 | 597.6326 | 561.1919
3926.1292 | 636.4127 | 603.6117 | 598.367 | 559.7931
3927.1292 | 636.6765 | 602.6884 | 598.6938 | 562.045
3928.1292 | 635.7217 | 601.3975 | 598.7756 | 559.3804
3929.1292 | 635.2922 | 600.2938 | 597.4747 | 562.1128
3930.1292 | 635.4227 | 599.4354 | 596.5014 | 559.2252
3931.1292 | 635.7036 | 597.9726 | 596.191 | 557.1592
3932.1292 | 635.8785 | 597.1965 | 596.4904 | 557.7775
3933.1292 | 635.5276 | 596.4639 | 596.3594 | 556.863
3934.1292 | 634.8982 | 595.3557 | 594.7663 | 557.0134
3935.1292 | 634.9652 | 593.5081 | 593.7688 | 555.2903
3936.1292 | 634.49 | 594.5382 | 594.1857 | 554.3621
3937.1292 | 634.3387 | 595.068 | 593.8981 | 556.112
3938.1292 | 634.1274 | 595.7094 | 593.4253 | 554.728
3939.1292 | 634.3193 | 596.4072 | 594.8169 | 556.0777
3940.1292 | 634.6342 | 599.2525 | 600.3112 | 559.3998
3941.1292 | 634.0104 | 599.8394 | 598.4639 | 557.3829
3942.1292 | 634.2234 | 597.5115 | 597.5125 | 556.0715
3943.1292 | 634.4775 | 597.993 | 598.486 | 555.4884
3944.1292 | 634.3094 | 597.521 | 597.9812 | 553.9021
3945.1292 | 634.9422 | 595.8073 | 597.7984 | 553.1508
3946.1292 | 635.466 | 598.2919 | 597.3143 | 552.466
3947.1292 | 634.4767 | 597.4898 | 594.6087 | 559.1073
3948.1292 | 634.1273 | 597.403 | 594.5172 | 558.7137
3949.1292 | 634.3675 | 595.8684 | 595.0368 | 556.4273
3950.1292 | 634.553 | 594.1025 | 595.2422 | 556.025
3951.1292 | 635.5926 | 594.4003 | 596.2779 | 555.3132
3952.1292 | 635.263 | 595.3812 | 595.228 | 557.3541
3953.1292 | 635.3633 | 595.9038 | 594.5553 | 554.041
3954.1292 | 635.2233 | 595.2795 | 595.4437 | 553.3594
3955.1292 | 635.0496 | 593.913 | 596.2491 | 553.0797
3956.1292 | 634.9802 | 591.1142 | 595.6147 | 553.8799
3957.1292 | 634.2279 | 589.6028 | 595.4224 | 557.226
3958.1292 | 634.2278 | 589.5984 | 595.763 | 556.9387
3959.1292 | 633.8022 | 591.203 | 597.8303 | 556.887
3960.1292 | 634.476 | 591.9126 | 597.661 | 556.225
3961.1292 | 633.3604 | 590.954 | 597.7671 | 557.5649
3962.1292 | 632.8433 | 589.0491 | 596.6773 | 556.3661
3963.1292 | 632.3214 | 588.2824 | 595.8962 | 556.448
3964.1292 | 631.5573 | 587.9692 | 595.1152 | 555.2723
3965.1292 | 629.6425 | 587.0829 | 592.0155 | 553.1481
3966.1292 | 629.5547 | 585.0346 | 589.6451 | 550.4294
3967.1292 | 629.5835 | 582.9112 | 588.7614 | 549.0271
3968.1292 | 629.3555 | 584.4223 | 589.2761 | 548.3055
3969.1292 | 628.9555 | 584.7317 | 589.6109 | 549.3785
3970.1292 | 630.137 | 585.5448 | 590.1813 | 549.1907
3971.1292 | 629.8404 | 584.8333 | 590.6809 | 550.5193
3972.1292 | 629.5136 | 584.8247 | 590.1218 | 555.0815
3973.1292 | 630.1066 | 583.8578 | 590.4925 | 555.0044
3974.1292 | 630.3395 | 584.6404 | 590.4428 | 555.087
3975.1292 | 630.87 | 584.629 | 591.6428 | 555.2217
3976.1292 | 631.6442 | 586.3605 | 594.0428 | 559.2737
3977.1292 | 631.8449 | 587.6385 | 595.1604 | 560.1674
3978.1292 | 632.2534 | 586.5915 | 595.3151 | 557.7201
3979.1292 | 632.3303 | 586.4012 | 595.8119 | 556.5103
3980.1292 | 631.3942 | 589.5288 | 594.4551 | 554.8555
3981.1292 | 630.8529 | 588.4461 | 593.65 | 555.8125
3982.1292 | 630.4362 | 586.2638 | 591.3656 | 554.3058
3983.1292 | 630.5196 | 586.752 | 589.7192 | 552.0139
3984.1448 | 629.9876 | 586.7549 | 588.5432 | 552.1268
3985.1292 | 629.8453 | 586.3456 | 588.0224 | 555.9512
3986.1292 | 629.6131 | 585.3887 | 588.4725 | 555.2176
3987.1292 | 629.8148 | 587.0551 | 589.6077 | 554.3011
3988.1292 | 629.9766 | 588.7439 | 589.7084 | 553.8564
3989.1292 | 629.4764 | 588.0818 | 588.5342 | 552.676
3990.1292 | 628.8583 | 585.87 | 586.3623 | 552.6944
3991.1292 | 627.4836 | 584.691 | 584.7542 | 553.1144
3992.1292 | 626.6982 | 587.2878 | 584.0676 | 553.2199
3993.1292 | 626.9057 | 587.6373 | 584.0411 | 556.3864
3994.1292 | 627.2434 | 585.8461 | 582.6506 | 553.8652
3995.1292 | 628.7188 | 586.7056 | 582.8306 | 552.2915
3996.1292 | 629.7155 | 587.6503 | 582.187 | 551.9074
3997.1292 | 630.7013 | 587.2147 | 583.715 | 551.2871
3998.1292 | 630.8511 | 586.5854 | 583.568 | 550.6689
3999.1292 | 631.2304 | 587.6204 | 584.286 | 550.1731
4000.1292 | 631.2723 | 587.7195 | 584.6263 | 551.3663
4001.1292 | 631.8373 | 589.2094 | 584.5738 | 550.0194
4002.1292 | 630.65 | 590.6436 | 583.4514 | 549.7661
4003.1292 | 630.0352 | 592.2735 | 583.9073 | 551.7084
4004.1292 | 630.3733 | 594.3525 | 584.422 | 549.3733
4005.1292 | 630.0612 | 595.2705 | 583.6871 | 548.5155
4006.1292 | 630.5384 | 593.2307 | 583.4733 | 547.5217
4007.1292 | 631.4154 | 592.4555 | 583.9333 | 547.1663
4008.1292 | 632.0631 | 592.6836 | 583.411 | 546.4668
4009.1292 | 633.269 | 592.0275 | 584.3179 | 546.9511
4010.1292 | 633.3059 | 591.8498 | 584.0654 | 547.4701
4011.1292 | 633.4382 | 591.9862 | 583.9431 | 546.2691
4012.1292 | 633.4593 | 592.4442 | 585.8613 | 550.6193
4013.1292 | 633.3818 | 592.5847 | 586.5301 | 549.4593
4014.1292 | 633.4287 | 592.8762 | 587.7281 | 549.2873
4015.1292 | 633.3209 | 594.4617 | 586.6233 | 547.9717
4016.1292 | 632.2602 | 592.1 | 585.4623 | 547.5104
4017.1292 | 632.3375 | 591.6827 | 585.569 | 546.2872
4018.1292 | 632.82 | 592.5098 | 587.409 | 547.8274
4019.1292 | 633.3477 | 592.6767 | 589.6875 | 549.1822
4020.1292 | 633.7445 | 592.5108 | 590.3706 | 547.9409
4021.1292 | 633.1924 | 591.8605 | 589.5423 | 546.6071
4022.1292 | 632.6104 | 591.6742 | 589.6136 | 546.1772
4023.1292 | 632.4446 | 592.278 | 588.1815 | 557.1095
4024.1292 | 632.1069 | 592.7811 | 587.2275 | 555.902
4025.1292 | 632.0427 | 590.5612 | 586.7072 | 557.6478
4026.1292 | 631.9339 | 588.8941 | 588.8113 | 556.753
4027.1292 | 631.9799 | 590.7828 | 588.0895 | 554.7931
4028.1292 | 631.838 | 591.3435 | 589.5836 | 553.2477
4029.1292 | 631.5385 | 590.0193 | 588.943 | 552.3296
4030.1292 | 632.3109 | 594.6235 | 595.0914 | 553.1619
4031.1292 | 631.8154 | 594.52 | 595.1134 | 556.0818
4032.1292 | 631.3358 | 593.0282 | 592.5928 | 556.0472
4033.1292 | 630.5221 | 593.6575 | 592.5379 | 556.4494
4034.1292 | 630.2785 | 592.1612 | 590.724 | 557.2799
4035.1292 | 629.9916 | 589.8051 | 589.5806 | 555.0188
4036.1292 | 630.0864 | 588.5538 | 589.2618 | 553.8754
4037.1292 | 630.6385 | 589.1445 | 588.5131 | 551.9357
4038.1292 | 630.7905 | 589.0714 | 589.3194 | 551.2358
4039.1292 | 631.1779 | 589.5205 | 589.6396 | 550.8019
4040.1292 | 630.8344 | 590.5211 | 589.6022 | 550.2436
4041.1292 | 630.9764 | 589.2149 | 589.3078 | 552.5345
4042.1292 | 631.6193 | 587.2454 | 589.1427 | 551.448
4043.1292 | 631.9521 | 587.4638 | 590.6639 | 550.8978
4044.1292 | 631.9989 | 586.5686 | 589.9166 | 550.7175
4045.1292 | 631.8382 | 588.4257 | 591.4097 | 551.4038
4046.1292 | 632.1189 | 588.6938 | 589.2292 | 549.2072
4047.1292 | 630.7135 | 589.633 | 588.0976 | 549.0127
4048.1292 | 630.2832 | 587.3195 | 585.9578 | 548.0214
4049.1292 | 629.7409 | 587.2892 | 585.563 | 546.9701
4050.1292 | 629.4187 | 588.5317 | 585.486 | 548.5024
4051.1292 | 629.9141 | 589.5439 | 586.0543 | 549.8747
4052.1292 | 629.4257 | 588.9325 | 585.8422 | 549.1808
4053.1292 | 629.1832 | 587.7309 | 585.0057 | 547.8323
4054.1292 | 628.6258 | 589.5336 | 584.1849 | 546.6149
4055.1292 | 629.142 | 589.4203 | 584.1335 | 545.6975
4056.1292 | 628.7154 | 588.9908 | 583.808 | 545.2683
4057.1292 | 628.7225 | 588.0203 | 583.6206 | 545.2454
4058.1292 | 628.8959 | 587.1014 | 583.9252 | 544.7357
4059.1292 | 628.3381 | 586.8256 | 583.482 | 544.6686
4060.1292 | 628.5961 | 585.3281 | 583.4563 | 544.1255
4061.1292 | 629.0151 | 584.7665 | 582.9005 | 544.7815
4062.1292 | 628.9177 | 584.728 | 583.7944 | 545.1364
4063.1292 | 628.8346 | 583.6114 | 583.6362 | 543.9378
4064.1292 | 629.1634 | 584.5126 | 583.522 | 543.8497
4065.1292 | 628.4864 | 586.4494 | 583.7892 | 543.2052
4066.1292 | 628.4894 | 585.8537 | 583.8227 | 543.0689
4067.1292 | 628.7174 | 587.3075 | 585.2951 | 543.1831
4068.1292 | 628.8598 | 589.1159 | 586.1503 | 544.7271
4069.1292 | 629.6033 | 591.643 | 591.2007 | 545.9571
4070.1292 | 630.1186 | 594.795 | 593.5657 | 548.8841
4071.1292 | 629.9958 | 595.7292 | 594.3603 | 548.4349
4072.1292 | 630.0954 | 594.9512 | 593.4451 | 547.2618
4073.1292 | 629.3067 | 594.3019 | 591.849 | 546.4245
4074.1292 | 628.6275 | 592.7089 | 589.8787 | 547.3482
4075.1292 | 628.2402 | 592.4699 | 588.6154 | 545.1637
4076.1292 | 627.9648 | 592.5987 | 589.9568 | 544.7696
4077.1292 | 627.7035 | 592.5042 | 588.4741 | 545.4
4078.1292 | 627.6237 | 592.3365 | 586.9166 | 544.1209
4079.1292 | 628.1679 | 592.084 | 586.2637 | 543.0702
4080.1292 | 628.5888 | 593.5729 | 583.9077 | 542.1734
4081.1292 | 628.3113 | 593.4003 | 583.2773 | 541.1775
4082.1292 | 627.6987 | 593.0995 | 582.3163 | 540.9584
4083.1292 | 628.3336 | 592.9721 | 581.3609 | 540.993
4084.1292 | 629.5737 | 592.8078 | 581.1199 | 541.651
4085.1292 | 630.2559 | 593.1445 | 582.6179 | 541.7736
4086.1292 | 629.7634 | 591.5456 | 582.7966 | 541.9425
4087.1292 | 629.6864 | 591.5416 | 582.3595 | 542.3985
4088.1292 | 628.9475 | 592.1835 | 581.8776 | 541.5945
4089.1292 | 628.9505 | 591.1405 | 582.2651 | 539.6732
4090.1292 | 629.3853 | 592.7 | 581.4114 | 538.2477
4091.1292 | 628.6559 | 594.1589 | 579.1646 | 542.8599
4092.1292 | 628.3138 | 593.6905 | 578.9645 | 541.7652
4093.1292 | 628.6048 | 595.076 | 584.5547 | 542.7315
4094.1292 | 628.428 | 595.0277 | 585.5599 | 542.7968
4095.1292 | 628.8119 | 593.7865 | 585.0995 | 541.7368
4096.1292 | 628.9707 | 593.4675 | 586.2014 | 543.7425
4097.1292 | 629.0729 | 594.3258 | 585.8092 | 542.8752
4098.1292 | 629.8701 | 595.1588 | 585.8979 | 542.3877
4099.1292 | 628.7582 | 595.9414 | 586.6138 | 542.8712
4100.1292 | 628.8292 | 595.5285 | 586.2865 | 542.5315
4101.1292 | 628.5284 | 594.0824 | 584.9941 | 542.6536
4102.1292 | 629.5972 | 592.0113 | 584.8855 | 541.2801
4103.1292 | 631.6562 | 593.96 | 588.1644 | 541.5769
4104.1292 | 632.5384 | 594.5965 | 589.9921 | 544.8925
4105.1292 | 632.3612 | 594.3054 | 590.1066 | 549.2046
4106.1292 | 632.1968 | 593.4468 | 592.9958 | 552.0601
4107.1292 | 632.9319 | 591.4243 | 592.8621 | 551.8018
4108.1292 | 632.9432 | 591.726 | 592.8554 | 552.151
4109.1292 | 633.3605 | 593.3794 | 592.456 | 550.852
4110.1292 | 634.0429 | 594.5503 | 591.9623 | 549.6798
4111.1292 | 633.7918 | 596.5451 | 593.9036 | 552.0514
4112.1292 | 633.8108 | 596.6157 | 594.3279 | 551.7889
4113.1292 | 633.9933 | 595.1623 | 593.4214 | 550.7904
4114.1292 | 634.0283 | 595.5359 | 593.6985 | 549.9904
4115.1292 | 633.8139 | 599.2316 | 594.9606 | 551.3365
4116.1292 | 633.5997 | 599.4962 | 597.0878 | 552.5205
4117.1292 | 633.5651 | 599.3565 | 598.1203 | 556.2211
4118.1292 | 634.6948 | 596.9333 | 598.6086 | 554.3272
4119.1292 | 635.7475 | 597.3449 | 600.4337 | 555.2271
4120.1292 | 636.1047 | 599.3352 | 600.981 | 556.072
4121.1292 | 635.4312 | 599.7002 | 601.5832 | 556.3596
4122.1292 | 635.4167 | 598.8959 | 601.3113 | 554.474
4123.1292 | 635.015 | 598.0215 | 599.8407 | 554.0726
4124.1292 | 636.9822 | 599.7816 | 602.0096 | 553.809
4125.1292 | 637.4391 | 597.74 | 601.996 | 555.2418
4126.1292 | 636.7903 | 596.7914 | 600.2188 | 554.7143
4127.1292 | 636.3044 | 597.066 | 600.9231 | 553.2289
4128.1292 | 636.2801 | 596.013 | 601.764 | 552.7888
4129.1292 | 636.5732 | 593.9672 | 601.4833 | 552.7997
4130.1292 | 636.518 | 598.0825 | 604.251 | 553.5417
4131.1292 | 635.9367 | 597.0886 | 603.3327 | 552.0434
4132.1292 | 636.3484 | 595.3043 | 603.0295 | 551.5869
4133.1292 | 638.2068 | 594.1039 | 602.275 | 552.7891
4134.1292 | 640.1183 | 595.9045 | 604.0381 | 553.6663
4135.1292 | 638.3004 | 595.6054 | 601.9469 | 555.1847
4136.1292 | 638.4507 | 596.0096 | 600.7504 | 552.5174
4137.1292 | 637.6634 | 597.5234 | 600.0916 | 552.0833
4138.1292 | 637.175 | 597.7338 | 598.5152 | 550.0641
4139.1292 | 637.5238 | 600.8864 | 599.5117 | 550.2132
4140.1292 | 637.9358 | 600.6432 | 599.9401 | 549.9936
4141.1292 | 637.8701 | 602.7205 | 600.1945 | 550.6038
4142.1292 | 637.3814 | 602.6155 | 599.5713 | 549.738
4143.1292 | 636.5588 | 602.2036 | 598.3551 | 548.7938
4144.1292 | 636.7173 | 604.3828 | 600.3618 | 549.4519
4145.1292 | 636.6856 | 606.011 | 601.1305 | 549.6386
4146.1292 | 636.4281 | 603.3992 | 599.6135 | 548.7951
4147.1292 | 636.9467 | 604.4727 | 598.7592 | 547.2761
4148.1292 | 637.6125 | 604.4861 | 598.8147 | 546.7122
4149.1292 | 637.7677 | 604.0269 | 598.3929 | 546.6207
4150.1292 | 637.7947 | 604.5614 | 599.4988 | 547.6285
4151.1292 | 638.1547 | 604.8852 | 598.7208 | 548.273
4152.1292 | 638.6137 | 606.2875 | 597.7343 | 547.7458
4153.1292 | 638.7399 | 607.0463 | 596.6071 | 546.5621
4154.1292 | 638.2579 | 605.5174 | 594.8565 | 545.1607
4155.1292 | 637.326 | 603.8747 | 594.8044 | 545.1989
4156.1292 | 637.9628 | 604.0104 | 596.0597 | 546.1793
4157.1292 | 638.4431 | 605.5321 | 596.5067 | 545.5673
4158.1292 | 637.7024 | 605.5959 | 596.39 | 546.0625
4159.1292 | 637.3235 | 605.3124 | 596.3598 | 546.1837
4160.1292 | 637.2496 | 605.3826 | 595.3381 | 544.5777
4161.1292 | 636.9873 | 604.7617 | 593.7976 | 544.312
4162.1292 | 638.3008 | 603.3229 | 593.1354 | 543.5257
4163.1292 | 638.9529 | 602.7306 | 593.4532 | 543.7425
4164.1448 | 638.5283 | 601.8339 | 593.7025 | 543.0535
4165.1292 | 637.8552 | 600.806 | 594.1379 | 543.6181
4166.1292 | 636.9082 | 598.7642 | 593.1733 | 543.9786
4167.1292 | 636.6952 | 597.7715 | 592.7031 | 544.7566
4168.1292 | 636.5707 | 597.8452 | 592.9227 | 544.7431
4169.1292 | 636.4379 | 598.2784 | 592.5826 | 548.2752
4170.1292 | 635.4751 | 599.3599 | 592.1382 | 546.7244
4171.1292 | 635.5175 | 601.0981 | 591.7911 | 546.9126
4172.1292 | 636.5874 | 599.5886 | 592.2852 | 546.0292
4173.1292 | 636.8792 | 598.0435 | 592.0366 | 545.8408
4174.1292 | 636.4858 | 597.5963 | 592.4223 | 544.8307
4175.1292 | 636.1602 | 595.3021 | 593.731 | 544.685
4176.1292 | 636.3265 | 594.1403 | 594.2864 | 544.9176
4177.1292 | 635.9539 | 591.9542 | 594.6101 | 547.3753
4178.1292 | 635.2684 | 590.4945 | 594.5266 | 548.6817
4179.1292 | 634.9401 | 588.3723 | 595.8984 | 549.5985
4180.1292 | 635.3444 | 585.3619 | 595.6428 | 549.2926
4181.1292 | 635.4435 | 585.9516 | 596.5708 | 549.0607
4182.1292 | 635.3862 | 588.783 | 598.5289 | 548.9941
4183.1292 | 634.9564 | 588.2312 | 600.4502 | 549.1742
4184.1292 | 634.3945 | 586.1725 | 598.8849 | 547.086
4185.1292 | 633.5747 | 584.493 | 597.3779 | 546.8757
4186.1292 | 632.7248 | 586.1732 | 597.5192 | 547.6776
4187.1292 | 632.3457 | 584.9579 | 595.9311 | 547.4972
4188.1292 | 632.1751 | 584.5878 | 594.3572 | 546.7726
4189.1292 | 632.0074 | 584.0433 | 594.5995 | 547.2661
4190.1292 | 632.8162 | 585.4497 | 596.0032 | 547.445
4191.1292 | 632.9197 | 587.2438 | 598.0075 | 548.4572
4192.1292 | 633.1602 | 587.9006 | 598.0157 | 549.7624
4193.1292 | 634.1667 | 587.7803 | 599.2501 | 550.9913
4194.1292 | 634.4309 | 590.7032 | 600.2642 | 551.3581
4195.1292 | 634.4705 | 592.0587 | 599.5726 | 549.7601
4196.1292 | 634.3723 | 590.6865 | 597.2396 | 546.8608
4197.1292 | 633.7265 | 592.3042 | 596.3626 | 545.1375
4198.1292 | 636.4725 | 594.2764 | 599.0511 | 544.7698
4199.1292 | 635.9717 | 592.1705 | 596.84 | 543.8493
4200.1292 | 635.2002 | 591.8707 | 597.3085 | 548.2314
4201.1292 | 634.8593 | 591.1674 | 597.909 | 547.7034
4202.1292 | 634.9159 | 590.4455 | 598.6021 | 549.6373
4203.1292 | 635.2304 | 589.4305 | 599.0144 | 551.7886
4204.1292 | 636.3341 | 587.6556 | 599.3278 | 553.4257
4205.1292 | 637.4041 | 588.9748 | 600.3225 | 553.2766
4206.1292 | 637.8018 | 590.1825 | 599.9655 | 552.5687
4207.1292 | 636.246 | 590.2285 | 597.6613 | 550.4472
4208.1292 | 635.7725 | 590.6554 | 596.4017 | 549.0287
4209.1292 | 636.4946 | 591.3556 | 596.269 | 549.9092
4210.1292 | 636.5614 | 590.2278 | 596.9697 | 553.1642
4211.1292 | 636.4313 | 592.8092 | 595.8197 | 552.2021
4212.1292 | 635.7408 | 593.6214 | 594.9124 | 550.9107
4213.1292 | 635.577 | 593.3247 | 594.5974 | 549.5285
4214.1292 | 635.5828 | 591.9194 | 593.4564 | 548.4447
4215.1292 | 636.9277 | 594.4507 | 593.6638 | 548.2969
4216.1292 | 636.7328 | 595.7606 | 592.8893 | 546.9985
4217.1292 | 637.5994 | 599.2796 | 593.6002 | 546.8871
4218.1292 | 640.1302 | 600.0842 | 593.5081 | 546.3725
4219.1292 | 641.2208 | 599.2518 | 593.9981 | 546.1564
4220.1292 | 639.6083 | 598.8015 | 592.6903 | 545.0571
4221.1292 | 639.5117 | 598.7522 | 591.9585 | 543.8469
4222.1292 | 638.7694 | 599.2882 | 590.1204 | 543.2307
4223.1292 | 638.0422 | 599.4523 | 589.8821 | 543.095
4224.1292 | 638.3818 | 601.554 | 591.2418 | 543.2248
4225.1292 | 639.912 | 603.326 | 592.186 | 543.4027
4226.1292 | 638.1503 | 600.8354 | 589.4584 | 542.0596
4227.1292 | 637.9044 | 600.647 | 590.5483 | 541.9213
4228.1292 | 638.3523 | 601.9879 | 595.006 | 543.2167
4229.1292 | 638.0442 | 601.2292 | 595.5623 | 542.9355
4230.1292 | 637.9897 | 599.9008 | 594.3944 | 541.9152
4231.1292 | 638.2296 | 599.941 | 594.1008 | 540.7305
4232.1292 | 639.2472 | 602.6998 | 593.5163 | 538.5216
4233.1292 | 640.5678 | 603.3291 | 593.5108 | 538.0414
4234.1292 | 641.7546 | 602.7261 | 595.6156 | 538.5136
4235.1292 | 640.8903 | 603.8047 | 598.0157 | 540.8947
4236.1292 | 640.3095 | 601.9544 | 597.4477 | 541.5746
4237.1292 | 640.6293 | 600.1572 | 598.2586 | 543.3474
4238.1292 | 639.7351 | 600.8451 | 596.9079 | 542.9228
4239.1292 | 638.8421 | 602.7173 | 597.2312 | 543.494
4240.1292 | 638.1881 | 601.5908 | 595.7508 | 542.341
4241.1292 | 638.0234 | 600.7337 | 594.9285 | 541.3842
4242.1292 | 637.2732 | 602.2428 | 593.0613 | 542.036
4243.1292 | 635.7886 | 600.6136 | 590.2227 | 540.146
4244.1292 | 634.6114 | 599.456 | 589.2855 | 539.5943
4245.1292 | 634.638 | 599.8656 | 589.9213 | 541.751
4246.1292 | 634.7758 | 598.7585 | 590.2265 | 540.8338
4247.1292 | 635.9645 | 599.3885 | 590.3265 | 540.6898
4248.1292 | 635.9383 | 600.5225 | 589.3141 | 540.6723
4249.1292 | 637.9212 | 600.4924 | 590.2162 | 540.1364
4250.1292 | 638.5493 | 600.2726 | 590.0068 | 540.4976
4251.1292 | 639.6172 | 601.6092 | 590.6376 | 541.5326
4252.1292 | 639.5503 | 600.6126 | 590.8492 | 541.7189
4253.1292 | 641.3802 | 599.8909 | 592.8223 | 544.1824
4254.1292 | 644.0682 | 602.7673 | 595.7445 | 546.2096
4255.1292 | 644.2358 | 603.583 | 596.1445 | 545.0937
4256.1292 | 644.8388 | 601.9743 | 596.6599 | 544.9473
4257.1292 | 644.8785 | 600.9433 | 597.7121 | 545.7521
4258.1292 | 643.8819 | 601.3636 | 597.8591 | 545.7582
4259.1292 | 643.9727 | 602.1213 | 599.8088 | 546.7849
4260.1292 | 643.5181 | 600.6789 | 599.342 | 546.7541
4261.1292 | 643.0465 | 598.4962 | 599.1459 | 546.5091
4262.1292 | 641.6915 | 596.4021 | 599.2516 | 546.1001
4263.1292 | 641.3557 | 594.8159 | 598.2665 | 544.6948
4264.1292 | 639.7155 | 593.0722 | 597.4084 | 543.8216
4265.1292 | 638.7606 | 592.7259 | 596.0868 | 542.5302
4266.1292 | 638.19 | 591.4473 | 594.2913 | 541.6275
4267.1292 | 636.6592 | 591.1691 | 593.1081 | 541.404
4268.1292 | 635.7773 | 590.6338 | 592.3776 | 540.7211
4269.1292 | 635.5147 | 591.1627 | 593.7427 | 541.1083
4270.1292 | 635.4395 | 590.8016 | 592.117 | 540.8929
4271.1292 | 635.1138 | 590.9211 | 592.9202 | 540.8694
4272.1292 | 635.8362 | 590.5485 | 591.9607 | 540.3178
4273.1292 | 636.4016 | 592.8016 | 592.8837 | 540.7909
4274.1292 | 635.9051 | 593.5074 | 593.027 | 540.268
4275.1292 | 635.2949 | 594.074 | 592.1849 | 539.7182
4276.1292 | 634.206 | 593.3835 | 590.6549 | 538.6288
4277.1292 | 633.8162 | 595.1496 | 591.6821 | 538.2101
4278.1292 | 633.7115 | 596.6704 | 591.7819 | 538.2031
4279.1292 | 633.1211 | 595.6301 | 590.5588 | 537.3185
4280.1292 | 632.3264 | 597.2857 | 591.0416 | 536.4391
4281.1292 | 631.8383 | 596.1464 | 590.3254 | 535.9586
4282.1292 | 632.5621 | 595.3539 | 589.6722 | 535.7829
4283.1292 | 632.3341 | 595.2708 | 588.9622 | 538.1034
4284.1292 | 633.3257 | 595.0902 | 589.618 | 538.7838
4285.1292 | 634.0938 | 594.9532 | 590.4325 | 539.0356
4286.1292 | 634.2166 | 595.389 | 592.2864 | 542.9852
4287.1292 | 635.4844 | 595.1382 | 594.5623 | 543.9771
4288.1292 | 635.5643 | 595.6426 | 595.8849 | 544.1314
4289.1292 | 634.8266 | 597.6204 | 594.5588 | 542.2527
4290.1292 | 632.5512 | 601.371 | 592.3618 | 540.5587
4291.1292 | 631.3444 | 601.1472 | 590.2809 | 538.6418
4292.1292 | 631.7004 | 600.8986 | 591.9167 | 537.2588
4293.1292 | 631.9926 | 600.3758 | 593.1796 | 536.9303
4294.1292 | 632.1257 | 600.2233 | 591.281 | 536.568
4295.1292 | 632.3506 | 599.7375 | 590.0959 | 536.1199
4296.1292 | 631.814 | 598.8717 | 588.3904 | 535.9474
4297.1292 | 631.9462 | 600.1391 | 589.0645 | 536.4014
4298.1292 | 631.8975 | 601.803 | 592.6066 | 536.6381
4299.1292 | 632.0927 | 600.4556 | 592.2557 | 537.2146
4300.1292 | 632.795 | 601.4261 | 592.2175 | 536.1486
4301.1292 | 632.7262 | 600.3339 | 591.3596 | 536.0354
4302.1292 | 633.1058 | 599.0828 | 591.1769 | 536.0929
4303.1292 | 633.7231 | 604.754 | 595.3804 | 538.2121
4304.1292 | 633.9799 | 603.8486 | 594.9978 | 541.5426
4305.1292 | 634.0948 | 601.8758 | 595.491 | 541.9214
4306.1292 | 634.4091 | 601.7616 | 599.2086 | 543.0518
4307.1292 | 633.8138 | 600.4815 | 602.3584 | 546.2865
4308.1292 | 634.2623 | 601.854 | 605.5348 | 552.1495
4309.1292 | 633.6032 | 602.6186 | 604.3235 | 549.0642
4310.1292 | 632.5022 | 603.0806 | 601.469 | 546.5151
4311.1292 | 632.3407 | 603.0982 | 599.6591 | 544.5043
4312.1292 | 632.054 | 601.0983 | 597.0327 | 542.2517
4313.1292 | 632.5222 | 599.8742 | 597.1568 | 541.6224
4314.1292 | 632.7679 | 599.8324 | 596.7799 | 541.2574
4315.1292 | 632.6866 | 599.9113 | 597.9892 | 541.928
4316.1292 | 632.3975 | 597.9704 | 596.2513 | 541.3456
4317.1292 | 634.6417 | 598.3323 | 598.5017 | 542.5042
4318.1292 | 636.1066 | 599.4252 | 602.3808 | 543.5814
4319.1292 | 636.2872 | 600.3225 | 603.7898 | 544.6164
4320.1292 | 636.0991 | 599.277 | 602.9583 | 544.0168
4321.1292 | 635.7051 | 597.3904 | 601.4617 | 543.605
4322.1292 | 635.2065 | 599.726 | 600.8056 | 543.2382
4323.1292 | 635.9085 | 600.0103 | 601.0348 | 543.7376
4324.1292 | 635.8686 | 597.7435 | 600.1233 | 543.8615
4325.1292 | 635.7462 | 597.6366 | 599.6717 | 543.8991
4326.1292 | 634.8047 | 596.4238 | 597.6911 | 542.4205
4327.1292 | 633.6315 | 599.3462 | 598.4114 | 542.0816
4328.1292 | 632.0333 | 600.8859 | 597.892 | 541.9244
4329.1292 | 630.9825 | 601.3385 | 595.7011 | 540.6558
4330.1292 | 630.459 | 600.6113 | 592.4931 | 539.9117
4331.1292 | 630.5167 | 599.0682 | 591.5333 | 538.4959
4332.1292 | 630.4418 | 596.896 | 590.2298 | 538.5783
4333.1292 | 631.1732 | 596.2172 | 591.0697 | 538.8781
4334.1292 | 633.3184 | 597.9744 | 591.48 | 540.0139
4335.1292 | 633.6911 | 597.5336 | 590.5271 | 537.5361
4336.1292 | 633.556 | 599.1041 | 590.4762 | 536.3017
4337.1292 | 632.6646 | 601.3722 | 592.7753 | 537.3422
4338.1292 | 633.3478 | 601.7547 | 594.8872 | 542.8609
4339.1292 | 633.9904 | 601.2324 | 596.5172 | 542.348
4340.1292 | 633.9917 | 601.7488 | 594.8835 | 541.8723
4341.1292 | 633.2527 | 601.8898 | 595.8078 | 541.6834
4342.1292 | 633.031 | 600.5615 | 594.6622 | 542.0488
4343.1292 | 632.782 | 597.4416 | 593.1985 | 540.6874
4344.1292 | 633.2954 | 596.9729 | 592.9549 | 539.3804
4345.1292 | 633.0586 | 598.0625 | 593.82 | 540.1689
4346.1292 | 633.2738 | 599.5006 | 594.5624 | 540.8485
4347.1292 | 633.5035 | 599.4883 | 594.2965 | 539.5356
4348.1292 | 634.4051 | 599.0981 | 594.0973 | 539.1477
4349.1448 | 633.9845 | 599.6249 | 594.7894 | 539.0592
4350.1292 | 634.0979 | 598.702 | 594.9144 | 539.7763
4351.1292 | 634.8628 | 597.2278 | 595.0037 | 540.7706
4352.1292 | 636.3174 | 597.7897 | 598.2466 | 543.4798
4353.1292 | 636.6395 | 597.3702 | 598.9119 | 543.5154
4354.1292 | 636.4932 | 598.9419 | 599.1184 | 543.3929
4355.1292 | 636.503 | 598.6304 | 598.9853 | 542.415
4356.1292 | 636.997 | 600.5957 | 599.912 | 542.1419
4357.1292 | 637.3583 | 601.1066 | 599.6504 | 541.6115
4358.1292 | 637.2838 | 601.6458 | 598.8099 | 541.0963
4359.1292 | 638.1034 | 601.0753 | 601.5003 | 542.7878
4360.1292 | 637.7429 | 600.6139 | 603.2801 | 546.1876
4361.1292 | 638.5664 | 600.0907 | 603.1621 | 545.5072
4362.1292 | 639.0405 | 599.364 | 603.1882 | 546.5792
4363.1292 | 639.6862 | 601.794 | 605.2528 | 547.625
4364.1292 | 640.3239 | 602.3391 | 605.281 | 549.9462
4365.1292 | 640.1473 | 603.1621 | 604.8172 | 550.309
4366.1292 | 639.1886 | 602.4572 | 601.6672 | 548.5362
4367.1292 | 641.7223 | 604.6677 | 605.0415 | 547.6221
4368.1292 | 642.3316 | 604.9069 | 605.6351 | 547.2775
4369.1292 | 640.8154 | 604.6236 | 603.0655 | 545.9735
4370.1292 | 639.7663 | 604.8941 | 602.0274 | 545.1531
4371.1292 | 639.1719 | 606.1688 | 602.4483 | 546.1247
4372.1292 | 638.732 | 604.5647 | 601.1601 | 545.5616
4373.1292 | 638.4799 | 603.1307 | 600.3309 | 544.9568
4374.1292 | 638.851 | 604.089 | 601.5886 | 544.8115
4375.1292 | 638.7819 | 606.3088 | 606.8155 | 547.0634
4376.1292 | 638.0755 | 605.1092 | 604.2156 | 545.8108
4377.1292 | 636.9977 | 605.2841 | 603.8211 | 544.4083
4378.1292 | 636.7919 | 604.3283 | 605.7024 | 545.5422
4379.1448 | 636.6633 | 601.8569 | 605.2054 | 544.5889
4380.1292 | 636.4798 | 599.5116 | 603.8399 | 542.8873
4381.1292 | 637.2747 | 599.5878 | 603.3558 | 541.7959
4382.1292 | 637.1581 | 598.7724 | 601.7844 | 541.4603
4383.1292 | 636.3753 | 598.4712 | 600.0525 | 540.6698
4384.1292 | 635.767 | 599.1485 | 597.9678 | 539.7657
4385.1292 | 634.5008 | 599.4303 | 595.5642 | 538.7462
4386.1292 | 634.3172 | 599.2707 | 594.5779 | 537.335
4387.1292 | 633.3137 | 599.0276 | 593.0534 | 536.1976
4388.1292 | 632.7218 | 598.3479 | 591.8147 | 535.182
4389.1292 | 632.7423 | 602.305 | 595.1481 | 536.7811
4390.1292 | 632.6454 | 599.8442 | 593.5296 | 536.353
4391.1292 | 632.5352 | 598.1463 | 591.6511 | 535.0605
4392.1292 | 632.6708 | 598.4703 | 590.9 | 533.3805
4393.1292 | 632.9784 | 598.3911 | 590.978 | 532.4399
4394.1292 | 633.0258 | 598.3976 | 594.1301 | 533.7862
4395.1292 | 633.0369 | 597.3931 | 592.6701 | 533.5994
4396.1292 | 633.832 | 597.0137 | 591.5151 | 532.9148
4397.1292 | 634.3407 | 598.5469 | 592.5809 | 533.526
4398.1292 | 633.2792 | 597.6624 | 591.6683 | 533.0027
4399.1292 | 634.6197 | 599.3404 | 592.919 | 532.5741
4400.1292 | 635.0015 | 599.4866 | 593.8538 | 532.5301
4401.1292 | 634.3858 | 599.0683 | 592.0551 | 531.1158
4402.1292 | 632.6021 | 597.9557 | 589.6024 | 529.5896
4403.1292 | 632.0399 | 597.9892 | 588.6884 | 528.9191
4404.1292 | 634.1748 | 600.0205 | 590.6615 | 529.5685
4405.1292 | 634.1782 | 599.2002 | 591.8988 | 529.9376
4406.1292 | 634.6482 | 599.0614 | 592.788 | 531.6544
4407.1292 | 636.2315 | 599.3923 | 594.3074 | 532.5153
4408.1292 | 635.8883 | 598.2804 | 594.5141 | 532.4349
4409.1292 | 636.7012 | 599.1209 | 595.4426 | 533.5305
4410.1292 | 635.9437 | 600.4519 | 595.897 | 533.9354
4411.1292 | 635.3866 | 599.5919 | 593.5328 | 532.4649
4412.1292 | 636.4945 | 599.8547 | 594.0517 | 532.4726
4413.1292 | 638.5502 | 600.4544 | 596.0991 | 533.1917
4414.1292 | 638.489 | 601.517 | 596.518 | 534.722
4415.1292 | 637.8287 | 601.0099 | 594.8249 | 533.2197
4416.1292 | 637.5466 | 601.8157 | 595.4786 | 533.0533
4417.1292 | 637.7851 | 602.3302 | 596.414 | 532.5271
4418.1292 | 637.9045 | 603.2583 | 596.8592 | 534.0007
4419.1292 | 637.8779 | 605.2469 | 598.8285 | 534.5333
4420.1292 | 638.5426 | 604.0729 | 599.8174 | 534.7267
4421.1292 | 638.3337 | 606.0858 | 601.0538 | 534.9123
4422.1292 | 637.9064 | 605.6584 | 601.2258 | 533.8439
4423.1292 | 637.0029 | 604.1142 | 599.4327 | 532.8765
4424.1292 | 636.5148 | 602.2914 | 597.5613 | 531.9803
4425.1292 | 636.6302 | 600.769 | 595.391 | 530.3529
4426.1292 | 636.8062 | 601.608 | 595.403 | 530.3078
4427.1292 | 635.4326 | 600.9872 | 594.6516 | 529.8989
4428.1292 | 635.6309 | 600.7217 | 594.2845 | 531.8379
4429.1292 | 635.9265 | 600.2095 | 594.6111 | 531.5473
4430.1292 | 636.3682 | 600.2744 | 596.3551 | 532.4273
4431.1292 | 636.6679 | 599.8757 | 598.0536 | 533.0459
4432.1292 | 636.9006 | 600.5098 | 598.8417 | 533.313
4433.1292 | 636.8887 | 599.2819 | 599.7349 | 533.7301
4434.1292 | 637.2804 | 598.317 | 598.3241 | 533.2942
4435.1292 | 637.2386 | 599.1851 | 598.2503 | 533.2421
4436.1292 | 636.7696 | 598.9626 | 597.9963 | 532.8227
4437.1292 | 636.5964 | 598.5026 | 598.3486 | 533.0984
4438.1292 | 636.81 | 598.589 | 598.448 | 534.0094
4439.1448 | 636.3802 | 598.6444 | 596.3159 | 533.2195
4440.1292 | 636.8755 | 597.4384 | 596.0457 | 533.5247
4441.1292 | 637.0592 | 597.0586 | 597.0347 | 535.2924
4442.1292 | 636.2086 | 600.2449 | 599.1439 | 537.786
4443.1292 | 635.201 | 598.2715 | 596.4022 | 536.7544
4444.1292 | 635.2143 | 597.6904 | 596.4038 | 536.2023
4445.1292 | 636.2841 | 597.2363 | 596.7699 | 537.6628
4446.1292 | 636.8611 | 597.1294 | 599.1517 | 539.398
4447.1292 | 637.657 | 596.1762 | 598.8111 | 538.6954
4448.1292 | 638.5489 | 597.435 | 602.5879 | 539.6485
4449.1292 | 638.8656 | 596.7644 | 604.1073 | 539.3359
4450.1292 | 639.5631 | 597.9694 | 603.7854 | 540.2271
4451.1292 | 640.1343 | 598.2212 | 603.1715 | 539.6835
4452.1292 | 639.7913 | 596.8404 | 603.2317 | 539.7781
4453.1292 | 639.3111 | 595.2425 | 602.501 | 540.4993
4454.1292 | 639.2325 | 595.7637 | 601.1433 | 539.6735
4455.1292 | 639.0452 | 597.616 | 602.9101 | 540.3805
4456.1292 | 638.3359 | 597.5378 | 603.4517 | 540.9891
4457.1292 | 637.267 | 596.7248 | 602.7542 | 540.8048
4458.1292 | 636.838 | 595.7148 | 602.3844 | 541.4345
4459.1292 | 636.6716 | 594.1539 | 602.8931 | 542.203
4460.1292 | 635.7584 | 592.4721 | 602.1306 | 543.9144
4461.1292 | 635.11 | 590.1134 | 599.766 | 542.2959
4462.1292 | 634.4094 | 589.8375 | 598.923 | 541.4409
4463.1292 | 633.4043 | 588.7397 | 597.9383 | 540.5451
4464.1292 | 632.9497 | 587.6378 | 597.628 | 540.3068
4465.1292 | 632.5934 | 589.4729 | 596.8794 | 539.0943
4466.1292 | 632.3078 | 588.7481 | 596.027 | 538.1084
4467.1292 | 631.7609 | 586.8075 | 593.9778 | 538.2582
4468.1292 | 631.5718 | 585.6503 | 593.5145 | 537.6446
4469.1448 | 631.8499 | 586.9176 | 595.3982 | 538.0471
4470.1292 | 631.741 | 588.6368 | 598.1984 | 538.5303
4471.1292 | 630.9203 | 588.2944 | 596.8033 | 538.221
4472.1292 | 631.04 | 587.983 | 595.6639 | 536.4531
4473.1292 | 632.0284 | 589.097 | 596.8723 | 538.8176
4474.1292 | 633.4413 | 589.661 | 597.7662 | 539.6884
4475.1292 | 632.6155 | 589.2807 | 595.1027 | 537.8835
4476.1292 | 632.2629 | 588.4094 | 592.64 | 537.2919
4477.1292 | 631.7444 | 588.2206 | 591.5659 | 536.0065
4478.1292 | 630.689 | 589.9567 | 591.2688 | 535.3812
4479.1292 | 631.4352 | 591.4458 | 591.038 | 535.1738
4480.1292 | 631.2456 | 592.8094 | 589.4286 | 534.6759
4481.1292 | 629.9054 | 591.9168 | 588.7802 | 533.2063
4482.1292 | 629.8764 | 592.2296 | 590.4615 | 534.5046
4483.1292 | 630.9205 | 594.942 | 593.3324 | 533.8949
4484.1292 | 631.5167 | 596.894 | 594.9085 | 536.3682
4485.1292 | 632.9111 | 596.6369 | 595.3824 | 536.4574
4486.1292 | 633.5666 | 597.7212 | 594.4244 | 535.6261
4487.1292 | 632.8154 | 597.4645 | 593.3871 | 534.9763
4488.1292 | 633.5202 | 598.8137 | 593.1258 | 535.4904
4489.1292 | 635.2521 | 598.8626 | 593.7207 | 536.2538
4490.1292 | 635.3632 | 598.2023 | 593.3346 | 535.2025
4491.1292 | 635.6105 | 599.6267 | 594.0249 | 535.5965
4492.1292 | 635.4428 | 600.9163 | 593.4833 | 536.0517
4493.1292 | 635.4431 | 600.2434 | 594.7028 | 535.1371
4494.1292 | 635.363 | 600.9266 | 594.5293 | 534.5439
4495.1292 | 634.8681 | 601.3883 | 594.6578 | 534.2111
4496.1292 | 634.6504 | 602.1254 | 595.1682 | 534.6032
4497.1292 | 634.1875 | 602.9817 | 595.059 | 534.597
4498.1292 | 634.3856 | 601.0913 | 594.7649 | 533.6809
4499.1448 | 635.6663 | 600.4582 | 597.4075 | 535.2268
4500.1292 | 637.7428 | 600.7835 | 598.7181 | 535.906
4501.1292 | 638.7549 | 602.6844 | 598.5495 | 536.2238