## Test Conditions
DESIREE-FIRE Intermediate Scale Test 12 - Circuit Simulator Data Only
Test Date: | 2009-11-23
DCSim DAQ Start Time | 15:07
DCSim Time for Synchronization | 15:08
Heat Source Synchronization | 0:01 | hours:minutes:seconds
Heat Source DAQ Start Time | 15:08
Fire Time | 15:57
Offset | 0:50 | hours:minutes:seconds | This is the time after the DCSim DAQ was started and the heat source was initiated.
| 3026 | seconds
Heat Source Offset | 0:50 | hours:minutes:seconds | This is the time after the Heat Source DAQ was started and the heat source was initiated.
| 2991 | seconds
Heat Source Stop Time | 17:02
Test Duration | 1:05 | hours:minutes:seconds
| 3894 | seconds
Cable Information: | Record info about cable type on each circuit and which of the cable thermocouples corresponds to cable and air temperature
Unit Number | Cable Type |  | Cable TC Channel | Air TC Channel
Intercable Configuration | EPR/CPE, 7c, 12AWG |  | Cable thermocouples were not used for this test. | Channel 0 which is defined as "A Position - Middle" in the Temperature Data File respresents the temperature in the center of the cable tray.
A Note on Data Conversion and Accuracy:
Two different types of voltage transducers were used for each circuit. A bidirectional transducer (Ohio Semitronics, model number VT7-005X5-11) produces a 0 - 5V output signal which is directly proportional to the DC input ranging from 0 - 150VDC. The accuracy of this device is +/-0.25% full scale at DC and the response time is 50 mircoseconds. The unidirectional DC voltage isolator (Ohio Semitronics, model number VTU-005X5) used throughout tests also produces a 0 - 5V output over a 0 - 150VDC range. The accuracy of this device is +/-0.25% Rdg., +/-1% full scale at DC and the response time is 500 microseconds.
The readings were monitored using a National Instruments SCXI-1100 modules attached to SCXI-1300 multiplexers and housed within a SCXI-1001, 12-slot chassis. The "Raw Data" worksheet has been previously converted by LabView program created for this test series. The nominal zero point readings for each current transducer was taken before each test due to an electromagnetic effect created by direct current power. Zero Point values are provided, and the full run is documented in a separate data sheet (see "Current Offsets" worksheet). The converted data are presented as nominal indications of circuit path voltage and current. The data gathering equipment (transducers and DAQ card) have not been subject to specific calibration beyond that provided by the manufacturers. The accuracy of the converted data is estimated at +/-2%.

## Electrical Data
Fire Time (s) | Ground_VT7_1 | Ground_VTU_1 | Ground_VTU_2 | Int-Cab_VT7-T1 | Int-Cab_VT7-T2 | Int-Cab_VT7-T3 | Int-Cab_VT7-T4 | Int-Cab_VT7-T5 | Int-Cab_VT7-T6 | Int-Cab_VT7-T7 | Int-Cab_VTU-S1+a | Int-Cab_VTU-S1+b | Int-Cab_VTU-S2+a | Int-Cab_VTU-S2+b | Int-Cab_VTU-S1-a | Int-Cab_VTU-S1-b | Int-Cab_VTU-S2-a | Int-Cab_VTU-S2-b | T1-V(Batt -) | T2 -V(Batt -) | T3 - V(Batt -) | T4 - V(Batt -) | T5 - V(Batt -) | T6 - V(Batt -) | T7 - V(Batt -) | {S1+a} - V(Batt - ) | {S1+b} - V(Batt - ) | {S2+a} - V(Batt - ) | {S2+b} - V(Batt - ) | {S1-a} - V(Batt -) | {S1-b} - V(Batt - ) | {S2-a} - V(Batt - ) | {S2-b} - V(Batt - ) | {S1+a} - {S1-a} | {S1+a} - {S2-a} | {S2+a} - {S1-a} | {S2+a} - {S2-a}
-1.3438 | 122.3145 | -62.2742 | 59.7427 | 0.12643 | 0.000689 | -0.016578 | -0.020438 | 0.031687 | 0.071848 | -0.067295 | 59.6508 | 59.6863 | 59.637 | 59.5538 | 62.2336 | 62.2941 | 62.0266 | 62.2325 | 0.15847 | 0.032732 | 0.015465 | 0.011605 | 0.06373 | 0.10389 | -0.035252 | 59.6828 | 59.7183 | 59.6691 | 59.5859 | 62.2656 | 62.3261 | 62.0586 | 62.2646 | -2.5828 | -2.3758 | -2.5965 | -2.3895
0.40625 | 122.2366 | -62.265 | 59.8068 | 0.11727 | 0.000689 | -0.021157 | -0.025017 | 0.045421 | 0.071848 | -0.067295 | 59.6508 | 59.6954 | 59.637 | 59.5584 | 62.2381 | 62.2941 | 62.0311 | 62.2417 | 0.14932 | 0.032732 | 0.010886 | 0.007026 | 0.077464 | 0.10389 | -0.035252 | 59.6828 | 59.7275 | 59.6691 | 59.5905 | 62.2702 | 62.3261 | 62.0632 | 62.2737 | -2.5874 | -2.3804 | -2.6011 | -2.3941
2.1406 | 122.2366 | -62.2833 | 59.8114 | 0.12185 | -0.00389 | -0.021157 | -0.025017 | 0.040843 | 0.071848 | -0.071874 | 59.6508 | 59.6863 | 59.6279 | 59.5493 | 62.2244 | 62.2987 | 62.0266 | 62.2417 | 0.15389 | 0.028153 | 0.010886 | 0.007026 | 0.072886 | 0.10389 | -0.039831 | 59.6828 | 59.7183 | 59.6599 | 59.5813 | 62.2564 | 62.3307 | 62.0586 | 62.2737 | -2.5736 | -2.3758 | -2.5965 | -2.3987
3.875 | 122.3419 | -62.265 | 59.7427 | 0.11727 | 0.000689 | -0.016578 | -0.020438 | 0.036265 | 0.071848 | -0.071874 | 59.6462 | 59.6954 | 59.6233 | 59.5538 | 62.2336 | 62.3032 | 62.0311 | 62.2463 | 0.14932 | 0.032732 | 0.015465 | 0.011605 | 0.068308 | 0.10389 | -0.039831 | 59.6782 | 59.7275 | 59.6553 | 59.5859 | 62.2656 | 62.3353 | 62.0632 | 62.2783 | -2.5874 | -2.385 | -2.6103 | -2.4078
5.5781 | 122.1817 | -62.2559 | 59.8022 | 0.12185 | 0.000689 | -0.021157 | -0.020438 | 0.036265 | 0.067269 | -0.067295 | 59.6508 | 59.6954 | 59.6279 | 59.5493 | 62.2427 | 62.2849 | 62.0357 | 62.2508 | 0.15389 | 0.032732 | 0.010886 | 0.011605 | 0.068308 | 0.099312 | -0.035252 | 59.6828 | 59.7275 | 59.6599 | 59.5813 | 62.2748 | 62.317 | 62.0678 | 62.2829 | -2.592 | -2.385 | -2.6148 | -2.4078
7.3281 | 122.2137 | -62.265 | 59.8068 | 0.11727 | 0.009846 | -0.016578 | -0.020438 | 0.036265 | 0.067269 | -0.071874 | 59.6508 | 59.6908 | 59.6325 | 59.5538 | 62.2336 | 62.2941 | 62.0357 | 62.2417 | 0.14932 | 0.041889 | 0.015465 | 0.011605 | 0.068308 | 0.099312 | -0.039831 | 59.6828 | 59.7229 | 59.6645 | 59.5859 | 62.2656 | 62.3261 | 62.0678 | 62.2737 | -2.5828 | -2.385 | -2.6011 | -2.4033
9.0156 | 122.1909 | -62.2833 | 59.8022 | 0.12185 | 0.005267 | -0.016578 | -0.020438 | 0.031687 | 0.071848 | -0.067295 | 59.6553 | 59.6817 | 59.6279 | 59.5493 | 62.2336 | 62.2941 | 62.0311 | 62.2371 | 0.15389 | 0.03731 | 0.015465 | 0.011605 | 0.06373 | 0.10389 | -0.035252 | 59.6874 | 59.7137 | 59.6599 | 59.5813 | 62.2656 | 62.3261 | 62.0632 | 62.2691 | -2.5782 | -2.3758 | -2.6057 | -2.4033
10.75 | 122.2733 | -62.2696 | 59.7473 | 0.12185 | 0.000689 | -0.021157 | -0.025017 | 0.036265 | 0.071848 | -0.062717 | 59.6416 | 59.6954 | 59.6325 | 59.5493 | 62.2336 | 62.2895 | 62.0311 | 62.2463 | 0.15389 | 0.032732 | 0.010886 | 0.007026 | 0.068308 | 0.10389 | -0.030674 | 59.6736 | 59.7275 | 59.6645 | 59.5813 | 62.2656 | 62.3215 | 62.0632 | 62.2783 | -2.592 | -2.3895 | -2.6011 | -2.3987
12.4844 | 122.2137 | -62.2925 | 59.8022 | 0.12643 | -0.00389 | -0.016578 | -0.01586 | 0.040843 | 0.076426 | -0.067295 | 59.6508 | 59.6954 | 59.6325 | 59.5538 | 62.2381 | 62.2895 | 62.0311 | 62.2371 | 0.15847 | 0.028153 | 0.015465 | 0.016183 | 0.072886 | 0.10847 | -0.035252 | 59.6828 | 59.7275 | 59.6645 | 59.5859 | 62.2702 | 62.3215 | 62.0632 | 62.2691 | -2.5874 | -2.3804 | -2.6057 | -2.3987
14.2344 | 122.2092 | -62.3016 | 59.8206 | 0.12185 | 0.000689 | -0.016578 | -0.01586 | 0.036265 | 0.071848 | -0.062717 | 59.6508 | 59.6908 | 59.6325 | 59.5538 | 62.2381 | 62.2895 | 62.0311 | 62.2417 | 0.15389 | 0.032732 | 0.015465 | 0.016183 | 0.068308 | 0.10389 | -0.030674 | 59.6828 | 59.7229 | 59.6645 | 59.5859 | 62.2702 | 62.3215 | 62.0632 | 62.2737 | -2.5874 | -2.3804 | -2.6057 | -2.3987
16 | 122.1909 | -62.3291 | 59.7885 | 0.12185 | 0.005267 | -0.021157 | -0.025017 | 0.036265 | 0.071848 | -0.062717 | 59.6416 | 59.6863 | 59.6325 | 59.5584 | 62.2381 | 62.2895 | 62.0311 | 62.2417 | 0.15389 | 0.03731 | 0.010886 | 0.007026 | 0.068308 | 0.10389 | -0.030674 | 59.6736 | 59.7183 | 59.6645 | 59.5905 | 62.2702 | 62.3215 | 62.0632 | 62.2737 | -2.5965 | -2.3895 | -2.6057 | -2.3987
17.6875 | 122.2549 | -62.3245 | 59.7702 | 0.11727 | 0.000689 | -0.016578 | -0.020438 | 0.045421 | 0.067269 | -0.067295 | 59.6462 | 59.6908 | 59.6233 | 59.5538 | 62.2336 | 62.2895 | 62.0403 | 62.2417 | 0.14932 | 0.032732 | 0.015465 | 0.011605 | 0.077464 | 0.099312 | -0.035252 | 59.6782 | 59.7229 | 59.6553 | 59.5859 | 62.2656 | 62.3215 | 62.0723 | 62.2737 | -2.5874 | -2.3941 | -2.6103 | -2.417
19.4219 | 122.2137 | -62.3154 | 59.7656 | 0.11727 | 0.000689 | -0.021157 | -0.01586 | 0.036265 | 0.081005 | -0.062717 | 59.6553 | 59.7 | 59.637 | 59.5538 | 62.2381 | 62.2987 | 62.0311 | 62.2463 | 0.14932 | 0.032732 | 0.010886 | 0.016183 | 0.068308 | 0.11305 | -0.030674 | 59.6874 | 59.732 | 59.6691 | 59.5859 | 62.2702 | 62.3307 | 62.0632 | 62.2783 | -2.5828 | -2.3758 | -2.6011 | -2.3941
21.1562 | 122.2549 | -62.2787 | 59.7839 | 0.11727 | 0.000689 | -0.016578 | -0.020438 | 0.036265 | 0.067269 | -0.058139 | 59.6508 | 59.6908 | 59.637 | 59.5538 | 62.2381 | 62.2895 | 62.0311 | 62.2371 | 0.14932 | 0.032732 | 0.015465 | 0.011605 | 0.068308 | 0.099312 | -0.026096 | 59.6828 | 59.7229 | 59.6691 | 59.5859 | 62.2702 | 62.3215 | 62.0632 | 62.2691 | -2.5874 | -2.3804 | -2.6011 | -2.3941
22.8906 | 122.2229 | -62.3108 | 59.7977 | 0.11727 | 0.000689 | -0.016578 | -0.025017 | 0.036265 | 0.067269 | -0.058139 | 59.6508 | 59.6954 | 59.6325 | 59.5538 | 62.2381 | 62.2941 | 62.0311 | 62.2371 | 0.14932 | 0.032732 | 0.015465 | 0.007026 | 0.068308 | 0.099312 | -0.026096 | 59.6828 | 59.7275 | 59.6645 | 59.5859 | 62.2702 | 62.3261 | 62.0632 | 62.2691 | -2.5874 | -2.3804 | -2.6057 | -2.3987
24.5625 | 122.3282 | -62.2559 | 59.7931 | 0.12643 | 0.005267 | -0.021157 | -0.025017 | 0.036265 | 0.071848 | -0.067295 | 59.6462 | 59.6863 | 59.6325 | 59.5538 | 62.2381 | 62.2941 | 62.0357 | 62.2417 | 0.15847 | 0.03731 | 0.010886 | 0.007026 | 0.068308 | 0.10389 | -0.035252 | 59.6782 | 59.7183 | 59.6645 | 59.5859 | 62.2702 | 62.3261 | 62.0678 | 62.2737 | -2.592 | -2.3895 | -2.6057 | -2.4033
26.25 | 122.3099 | -62.2742 | 59.7794 | 0.12185 | 0.005267 | -0.021157 | -0.01586 | 0.040843 | 0.062691 | -0.062717 | 59.6508 | 59.6863 | 59.6233 | 59.5493 | 62.2427 | 62.2941 | 62.0311 | 62.2371 | 0.15389 | 0.03731 | 0.010886 | 0.016183 | 0.072886 | 0.094734 | -0.030674 | 59.6828 | 59.7183 | 59.6553 | 59.5813 | 62.2748 | 62.3261 | 62.0632 | 62.2691 | -2.592 | -2.3804 | -2.6194 | -2.4078
27.9844 | 122.3282 | -62.2559 | 59.8022 | 0.12643 | -0.00389 | -0.025735 | -0.025017 | 0.036265 | 0.067269 | -0.067295 | 59.6553 | 59.6954 | 59.637 | 59.5584 | 62.2336 | 62.2941 | 62.0357 | 62.2417 | 0.15847 | 0.028153 | 0.006308 | 0.007026 | 0.068308 | 0.099312 | -0.035252 | 59.6874 | 59.7275 | 59.6691 | 59.5905 | 62.2656 | 62.3261 | 62.0678 | 62.2737 | -2.5782 | -2.3804 | -2.5965 | -2.3987
29.7188 | 122.3053 | -62.2925 | 59.7198 | 0.11727 | -0.00389 | -0.025735 | -0.020438 | 0.036265 | 0.076426 | -0.067295 | 59.6553 | 59.6954 | 59.6325 | 59.5493 | 62.2427 | 62.2987 | 62.0311 | 62.2463 | 0.14932 | 0.028153 | 0.006308 | 0.011605 | 0.068308 | 0.10847 | -0.035252 | 59.6874 | 59.7275 | 59.6645 | 59.5813 | 62.2748 | 62.3307 | 62.0632 | 62.2783 | -2.5874 | -2.3758 | -2.6103 | -2.3987
31.4688 | 122.2183 | -62.2925 | 59.8206 | 0.11727 | 0.005267 | -0.012 | -0.020438 | 0.040843 | 0.071848 | -0.062717 | 59.6508 | 59.6908 | 59.6325 | 59.5538 | 62.229 | 62.2895 | 62.0311 | 62.2417 | 0.14932 | 0.03731 | 0.020043 | 0.011605 | 0.072886 | 0.10389 | -0.030674 | 59.6828 | 59.7229 | 59.6645 | 59.5859 | 62.261 | 62.3215 | 62.0632 | 62.2737 | -2.5782 | -2.3804 | -2.5965 | -2.3987
33.1406 | 122.2549 | -62.2925 | 59.7794 | 0.11727 | 0.000689 | -0.021157 | -0.020438 | 0.036265 | 0.071848 | -0.067295 | 59.6553 | 59.6863 | 59.6325 | 59.5584 | 62.2336 | 62.2987 | 62.0357 | 62.2417 | 0.14932 | 0.032732 | 0.010886 | 0.011605 | 0.068308 | 0.10389 | -0.035252 | 59.6874 | 59.7183 | 59.6645 | 59.5905 | 62.2656 | 62.3307 | 62.0678 | 62.2737 | -2.5782 | -2.3804 | -2.6011 | -2.4033
34.875 | 122.3053 | -62.2879 | 59.729 | 0.11727 | 0.000689 | -0.016578 | -0.020438 | 0.036265 | 0.067269 | -0.067295 | 59.6599 | 59.6954 | 59.637 | 59.5538 | 62.2381 | 62.2941 | 62.0357 | 62.2417 | 0.14932 | 0.032732 | 0.015465 | 0.011605 | 0.068308 | 0.099312 | -0.035252 | 59.692 | 59.7275 | 59.6691 | 59.5859 | 62.2702 | 62.3261 | 62.0678 | 62.2737 | -2.5782 | -2.3758 | -2.6011 | -2.3987
36.5625 | 122.2458 | -62.2833 | 59.7885 | 0.12185 | 0.000689 | -0.025735 | -0.020438 | 0.040843 | 0.067269 | -0.067295 | 59.6462 | 59.6863 | 59.6325 | 59.5584 | 62.2336 | 62.2941 | 62.0403 | 62.2417 | 0.15389 | 0.032732 | 0.006308 | 0.011605 | 0.072886 | 0.099312 | -0.035252 | 59.6782 | 59.7183 | 59.6645 | 59.5905 | 62.2656 | 62.3261 | 62.0723 | 62.2737 | -2.5874 | -2.3941 | -2.6011 | -2.4078
38.3125 | 122.2549 | -62.2559 | 59.8297 | 0.11727 | 0.000689 | -0.016578 | -0.020438 | 0.036265 | 0.062691 | -0.062717 | 59.6462 | 59.6954 | 59.6325 | 59.5493 | 62.229 | 62.2941 | 62.0266 | 62.2508 | 0.14932 | 0.032732 | 0.015465 | 0.011605 | 0.068308 | 0.094734 | -0.030674 | 59.6782 | 59.7275 | 59.6645 | 59.5813 | 62.261 | 62.3261 | 62.0586 | 62.2829 | -2.5828 | -2.3804 | -2.5965 | -2.3941
40.0625 | 122.2504 | -62.2833 | 59.8114 | 0.12185 | -0.008469 | -0.012 | -0.025017 | 0.036265 | 0.081005 | -0.067295 | 59.6508 | 59.6908 | 59.637 | 59.563 | 62.2336 | 62.2987 | 62.0266 | 62.2463 | 0.15389 | 0.023574 | 0.020043 | 0.007026 | 0.068308 | 0.11305 | -0.035252 | 59.6828 | 59.7229 | 59.6691 | 59.595 | 62.2656 | 62.3307 | 62.0586 | 62.2783 | -2.5828 | -2.3758 | -2.5965 | -2.3895
41.8125 | 122.2275 | -62.2559 | 59.8526 | 0.11727 | -0.00389 | -0.021157 | -0.020438 | 0.036265 | 0.071848 | -0.071874 | 59.6553 | 59.7 | 59.6416 | 59.5584 | 62.229 | 62.2941 | 62.0266 | 62.2417 | 0.14932 | 0.028153 | 0.010886 | 0.011605 | 0.068308 | 0.10389 | -0.039831 | 59.6874 | 59.732 | 59.6737 | 59.5905 | 62.261 | 62.3261 | 62.0586 | 62.2737 | -2.5736 | -2.3712 | -2.5874 | -2.3849
43.4844 | 122.2 | -62.3062 | 59.8022 | 0.11727 | -0.00389 | -0.016578 | -0.020438 | 0.040843 | 0.071848 | -0.067295 | 59.6508 | 59.7 | 59.6325 | 59.5676 | 62.2336 | 62.2941 | 62.0357 | 62.2463 | 0.14932 | 0.028153 | 0.015465 | 0.011605 | 0.072886 | 0.10389 | -0.035252 | 59.6828 | 59.732 | 59.6645 | 59.5996 | 62.2656 | 62.3261 | 62.0678 | 62.2783 | -2.5828 | -2.385 | -2.6011 | -2.4033
45.2344 | 122.3099 | -62.265 | 59.761 | 0.11727 | 0.000689 | -0.030314 | -0.025017 | 0.036265 | 0.067269 | -0.067295 | 59.6508 | 59.6908 | 59.6279 | 59.5447 | 62.2336 | 62.2987 | 62.0266 | 62.2463 | 0.14932 | 0.032732 | 0.001729 | 0.007026 | 0.068308 | 0.099312 | -0.035252 | 59.6828 | 59.7229 | 59.6599 | 59.5767 | 62.2656 | 62.3307 | 62.0586 | 62.2783 | -2.5828 | -2.3758 | -2.6057 | -2.3987
46.9844 | 122.319 | -62.2467 | 59.7656 | 0.12643 | -0.00389 | -0.021157 | -0.01586 | 0.036265 | 0.071848 | -0.062717 | 59.6462 | 59.6908 | 59.637 | 59.5584 | 62.2336 | 62.2987 | 62.0357 | 62.2463 | 0.15847 | 0.028153 | 0.010886 | 0.016183 | 0.068308 | 0.10389 | -0.030674 | 59.6782 | 59.7229 | 59.6691 | 59.5905 | 62.2656 | 62.3307 | 62.0678 | 62.2783 | -2.5874 | -2.3895 | -2.5965 | -2.3987
48.6562 | 122.3465 | -62.2833 | 59.7382 | 0.12643 | 0.000689 | -0.021157 | -0.01586 | 0.031687 | 0.071848 | -0.062717 | 59.6416 | 59.6954 | 59.6279 | 59.5584 | 62.2427 | 62.2895 | 62.0266 | 62.2371 | 0.15847 | 0.032732 | 0.010886 | 0.016183 | 0.06373 | 0.10389 | -0.030674 | 59.6736 | 59.7275 | 59.6599 | 59.5905 | 62.2748 | 62.3215 | 62.0586 | 62.2691 | -2.6011 | -2.385 | -2.6148 | -2.3987
50.3438 | 122.2504 | -62.265 | 59.816 | 0.11269 | 0.005267 | -0.021157 | -0.01586 | 0.040843 | 0.076426 | -0.067295 | 59.6599 | 59.6908 | 59.637 | 59.5538 | 62.2336 | 62.2987 | 62.0266 | 62.2417 | 0.14474 | 0.03731 | 0.010886 | 0.016183 | 0.072886 | 0.10847 | -0.035252 | 59.692 | 59.7229 | 59.6691 | 59.5859 | 62.2656 | 62.3307 | 62.0586 | 62.2737 | -2.5736 | -2.3666 | -2.5965 | -2.3895
52.0938 | 122.2961 | -62.2833 | 59.7656 | 0.11727 | -0.00389 | -0.021157 | -0.029595 | 0.040843 | 0.071848 | -0.067295 | 59.6599 | 59.6908 | 59.637 | 59.5493 | 62.2427 | 62.2895 | 62.0311 | 62.2417 | 0.14932 | 0.028153 | 0.010886 | 0.002448 | 0.072886 | 0.10389 | -0.035252 | 59.692 | 59.7229 | 59.6691 | 59.5813 | 62.2748 | 62.3215 | 62.0632 | 62.2737 | -2.5828 | -2.3712 | -2.6057 | -2.3941
53.8281 | 122.3145 | -62.2879 | 59.7427 | 0.12185 | -0.00389 | -0.025735 | -0.025017 | 0.031687 | 0.067269 | -0.071874 | 59.6508 | 59.6908 | 59.6325 | 59.5447 | 62.2381 | 62.3032 | 62.0403 | 62.2508 | 0.15389 | 0.028153 | 0.006308 | 0.007026 | 0.06373 | 0.099312 | -0.039831 | 59.6828 | 59.7229 | 59.6645 | 59.5767 | 62.2702 | 62.3353 | 62.0723 | 62.2829 | -2.5874 | -2.3895 | -2.6057 | -2.4078
55.5 | 122.2412 | -62.2787 | 59.7839 | 0.12185 | 0.000689 | -0.030314 | -0.011281 | 0.040843 | 0.071848 | -0.062717 | 59.6508 | 59.7 | 59.637 | 59.5493 | 62.2336 | 62.3032 | 62.0311 | 62.2417 | 0.15389 | 0.032732 | 0.001729 | 0.020762 | 0.072886 | 0.10389 | -0.030674 | 59.6828 | 59.732 | 59.6691 | 59.5813 | 62.2656 | 62.3353 | 62.0632 | 62.2737 | -2.5828 | -2.3804 | -2.5965 | -2.3941
57.2344 | 122.3282 | -62.2833 | 59.7427 | 0.12185 | 0.000689 | -0.016578 | -0.020438 | 0.036265 | 0.067269 | -0.076452 | 59.6508 | 59.6954 | 59.6325 | 59.5538 | 62.2381 | 62.2895 | 62.0357 | 62.2325 | 0.15389 | 0.032732 | 0.015465 | 0.011605 | 0.068308 | 0.099312 | -0.044409 | 59.6828 | 59.7275 | 59.6645 | 59.5859 | 62.2702 | 62.3215 | 62.0678 | 62.2646 | -2.5874 | -2.385 | -2.6057 | -2.4033
58.9844 | 122.3419 | -62.2742 | 59.7382 | 0.12185 | -0.00389 | -0.021157 | -0.011281 | 0.045421 | 0.071848 | -0.062717 | 59.6553 | 59.6908 | 59.637 | 59.5447 | 62.2381 | 62.2987 | 62.0357 | 62.2371 | 0.15389 | 0.028153 | 0.010886 | 0.020762 | 0.077464 | 0.10389 | -0.030674 | 59.6874 | 59.7229 | 59.6691 | 59.5767 | 62.2702 | 62.3307 | 62.0678 | 62.2691 | -2.5828 | -2.3804 | -2.6011 | -2.3987
60.6719 | 122.2504 | -62.3016 | 59.8022 | 0.11727 | 0.005267 | -0.025735 | -0.025017 | 0.036265 | 0.076426 | -0.067295 | 59.6508 | 59.6954 | 59.637 | 59.5538 | 62.2473 | 62.2987 | 62.0311 | 62.2417 | 0.14932 | 0.03731 | 0.006308 | 0.007026 | 0.068308 | 0.10847 | -0.035252 | 59.6828 | 59.7275 | 59.6691 | 59.5859 | 62.2793 | 62.3307 | 62.0632 | 62.2737 | -2.5965 | -2.3804 | -2.6103 | -2.3941
62.4219 | 122.2046 | -62.3016 | 59.7931 | 0.13101 | 0.005267 | -0.016578 | -0.011281 | 0.040843 | 0.071848 | -0.067295 | 59.6553 | 59.6954 | 59.6416 | 59.5538 | 62.2381 | 62.2987 | 62.0403 | 62.2417 | 0.16305 | 0.03731 | 0.015465 | 0.020762 | 0.072886 | 0.10389 | -0.035252 | 59.6874 | 59.7275 | 59.6737 | 59.5859 | 62.2702 | 62.3307 | 62.0723 | 62.2737 | -2.5828 | -2.385 | -2.5965 | -2.3987
64.1562 | 122.3145 | -62.2696 | 59.7748 | 0.11727 | -0.00389 | -0.016578 | -0.01586 | 0.031687 | 0.071848 | -0.058139 | 59.6508 | 59.6908 | 59.637 | 59.5584 | 62.2381 | 62.2941 | 62.0311 | 62.2508 | 0.14932 | 0.028153 | 0.015465 | 0.016183 | 0.06373 | 0.10389 | -0.026096 | 59.6828 | 59.7229 | 59.6691 | 59.5905 | 62.2702 | 62.3261 | 62.0632 | 62.2829 | -2.5874 | -2.3804 | -2.6011 | -2.3941
65.8438 | 122.3373 | -62.265 | 59.7107 | 0.12185 | -0.00389 | -0.016578 | -0.020438 | 0.031687 | 0.076426 | -0.062717 | 59.6508 | 59.6954 | 59.6325 | 59.5584 | 62.2381 | 62.2987 | 62.0357 | 62.2417 | 0.15389 | 0.028153 | 0.015465 | 0.011605 | 0.06373 | 0.10847 | -0.030674 | 59.6828 | 59.7275 | 59.6645 | 59.5905 | 62.2702 | 62.3307 | 62.0678 | 62.2737 | -2.5874 | -2.385 | -2.6057 | -2.4033
67.5781 | 122.3145 | -62.2742 | 59.7519 | 0.11269 | -0.00389 | -0.016578 | -0.025017 | 0.040843 | 0.067269 | -0.062717 | 59.6553 | 59.6863 | 59.6416 | 59.5584 | 62.2336 | 62.3032 | 62.0357 | 62.2463 | 0.14474 | 0.028153 | 0.015465 | 0.007026 | 0.072886 | 0.099312 | -0.030674 | 59.6874 | 59.7183 | 59.6737 | 59.5905 | 62.2656 | 62.3353 | 62.0678 | 62.2783 | -2.5782 | -2.3804 | -2.5919 | -2.3941
69.25 | 122.2549 | -62.2787 | 59.8297 | 0.12185 | 0.000689 | -0.012 | -0.01586 | 0.027109 | 0.071848 | -0.058139 | 59.6462 | 59.6863 | 59.6416 | 59.5538 | 62.2336 | 62.2987 | 62.0311 | 62.2417 | 0.15389 | 0.032732 | 0.020043 | 0.016183 | 0.059152 | 0.10389 | -0.026096 | 59.6782 | 59.7183 | 59.6737 | 59.5859 | 62.2656 | 62.3307 | 62.0632 | 62.2737 | -2.5874 | -2.385 | -2.5919 | -2.3895
71 | 122.3053 | -62.2787 | 59.7519 | 0.12185 | 0.005267 | -0.021157 | -0.011281 | 0.036265 | 0.071848 | -0.062717 | 59.6553 | 59.7 | 59.6325 | 59.5538 | 62.2336 | 62.2987 | 62.0357 | 62.2417 | 0.15389 | 0.03731 | 0.010886 | 0.020762 | 0.068308 | 0.10389 | -0.030674 | 59.6874 | 59.732 | 59.6645 | 59.5859 | 62.2656 | 62.3307 | 62.0678 | 62.2737 | -2.5782 | -2.3804 | -2.6011 | -2.4033
72.6875 | 122.3785 | -62.2375 | 59.7656 | 0.11727 | -0.00389 | -0.021157 | -0.025017 | 0.036265 | 0.071848 | -0.071874 | 59.6508 | 59.6954 | 59.6416 | 59.5538 | 62.2381 | 62.3032 | 62.0266 | 62.2508 | 0.14932 | 0.028153 | 0.010886 | 0.007026 | 0.068308 | 0.10389 | -0.039831 | 59.6828 | 59.7275 | 59.6737 | 59.5859 | 62.2702 | 62.3353 | 62.0586 | 62.2829 | -2.5874 | -2.3758 | -2.5965 | -2.3849
74.4375 | 122.3602 | -62.2559 | 59.7794 | 0.12185 | -0.00389 | -0.016578 | -0.025017 | 0.040843 | 0.058113 | -0.071874 | 59.6553 | 59.6908 | 59.6325 | 59.5584 | 62.2336 | 62.2987 | 62.0266 | 62.2371 | 0.15389 | 0.028153 | 0.015465 | 0.007026 | 0.072886 | 0.090156 | -0.039831 | 59.6874 | 59.7229 | 59.6645 | 59.5905 | 62.2656 | 62.3307 | 62.0586 | 62.2691 | -2.5782 | -2.3712 | -2.6011 | -2.3941
76.125 | 122.2961 | -62.2833 | 59.7519 | 0.12643 | -0.00389 | -0.016578 | -0.01586 | 0.045421 | 0.071848 | -0.062717 | 59.6508 | 59.6954 | 59.637 | 59.5538 | 62.2381 | 62.3032 | 62.0266 | 62.2508 | 0.15847 | 0.028153 | 0.015465 | 0.016183 | 0.077464 | 0.10389 | -0.030674 | 59.6828 | 59.7275 | 59.6691 | 59.5859 | 62.2702 | 62.3353 | 62.0586 | 62.2829 | -2.5874 | -2.3758 | -2.6011 | -2.3895
77.8438 | 122.2229 | -62.265 | 59.8297 | 0.11727 | 0.000689 | -0.012 | -0.020438 | 0.036265 | 0.076426 | -0.058139 | 59.6508 | 59.6954 | 59.6416 | 59.563 | 62.2336 | 62.3032 | 62.0311 | 62.2463 | 0.14932 | 0.032732 | 0.020043 | 0.011605 | 0.068308 | 0.10847 | -0.026096 | 59.6828 | 59.7275 | 59.6737 | 59.595 | 62.2656 | 62.3353 | 62.0632 | 62.2783 | -2.5828 | -2.3804 | -2.5919 | -2.3895
79.5156 | 122.2961 | -62.2879 | 59.729 | 0.12185 | 0.009846 | -0.021157 | -0.01586 | 0.040843 | 0.071848 | -0.062717 | 59.6508 | 59.6908 | 59.6279 | 59.5538 | 62.2381 | 62.2987 | 62.0311 | 62.2371 | 0.15389 | 0.041889 | 0.010886 | 0.016183 | 0.072886 | 0.10389 | -0.030674 | 59.6828 | 59.7229 | 59.6599 | 59.5859 | 62.2702 | 62.3307 | 62.0632 | 62.2691 | -2.5874 | -2.3804 | -2.6103 | -2.4033
81.2656 | 122.2 | -62.2696 | 59.8526 | 0.12185 | -0.008469 | -0.021157 | -0.025017 | 0.036265 | 0.076426 | -0.067295 | 59.6462 | 59.7 | 59.6325 | 59.5493 | 62.2381 | 62.3078 | 62.0311 | 62.2417 | 0.15389 | 0.023574 | 0.010886 | 0.007026 | 0.068308 | 0.10847 | -0.035252 | 59.6782 | 59.732 | 59.6645 | 59.5813 | 62.2702 | 62.3398 | 62.0632 | 62.2737 | -2.592 | -2.385 | -2.6057 | -2.3987
83 | 122.2412 | -62.2559 | 59.7931 | 0.12185 | 0.000689 | -0.012 | -0.011281 | 0.040843 | 0.076426 | -0.067295 | 59.6553 | 59.6954 | 59.637 | 59.5538 | 62.2336 | 62.2987 | 62.0266 | 62.2417 | 0.15389 | 0.032732 | 0.020043 | 0.020762 | 0.072886 | 0.10847 | -0.035252 | 59.6874 | 59.7275 | 59.6691 | 59.5859 | 62.2656 | 62.3307 | 62.0586 | 62.2737 | -2.5782 | -2.3712 | -2.5965 | -2.3895
84.6719 | 122.3236 | -62.2604 | 59.7427 | 0.11269 | 0.000689 | -0.012 | -0.025017 | 0.036265 | 0.071848 | -0.067295 | 59.6508 | 59.6954 | 59.637 | 59.5538 | 62.2381 | 62.3032 | 62.0357 | 62.2417 | 0.14474 | 0.032732 | 0.020043 | 0.007026 | 0.068308 | 0.10389 | -0.035252 | 59.6828 | 59.7275 | 59.6691 | 59.5859 | 62.2702 | 62.3353 | 62.0678 | 62.2737 | -2.5874 | -2.385 | -2.6011 | -2.3987
86.4062 | 122.3145 | -62.2604 | 59.7794 | 0.11727 | 0.000689 | -0.016578 | -0.020438 | 0.040843 | 0.071848 | -0.071874 | 59.6508 | 59.6908 | 59.637 | 59.5538 | 62.2381 | 62.3032 | 62.0357 | 62.2417 | 0.14932 | 0.032732 | 0.015465 | 0.011605 | 0.072886 | 0.10389 | -0.039831 | 59.6828 | 59.7229 | 59.6691 | 59.5859 | 62.2702 | 62.3353 | 62.0678 | 62.2737 | -2.5874 | -2.385 | -2.6011 | -2.3987
88.1562 | 122.2504 | -62.2742 | 59.8251 | 0.11727 | -0.00389 | -0.021157 | -0.020438 | 0.040843 | 0.076426 | -0.067295 | 59.6508 | 59.6908 | 59.6279 | 59.5676 | 62.2381 | 62.2987 | 62.0266 | 62.2463 | 0.14932 | 0.028153 | 0.010886 | 0.011605 | 0.072886 | 0.10847 | -0.035252 | 59.6828 | 59.7229 | 59.6599 | 59.5996 | 62.2702 | 62.3307 | 62.0586 | 62.2783 | -2.5874 | -2.3758 | -2.6103 | -2.3987
89.9062 | 122.2412 | -62.2742 | 59.8022 | 0.12185 | 0.005267 | -0.007421 | -0.01586 | 0.036265 | 0.076426 | -0.058139 | 59.6508 | 59.6954 | 59.6416 | 59.5584 | 62.2336 | 62.2987 | 62.0357 | 62.2371 | 0.15389 | 0.03731 | 0.024622 | 0.016183 | 0.068308 | 0.10847 | -0.026096 | 59.6828 | 59.7275 | 59.6737 | 59.5905 | 62.2656 | 62.3307 | 62.0678 | 62.2691 | -2.5828 | -2.385 | -2.5919 | -2.3941
91.5938 | 122.3419 | -62.2513 | 59.7565 | 0.11727 | 0.005267 | -0.016578 | -0.020438 | 0.040843 | 0.071848 | -0.067295 | 59.6553 | 59.7 | 59.6279 | 59.5538 | 62.229 | 62.2987 | 62.0357 | 62.2417 | 0.14932 | 0.03731 | 0.015465 | 0.011605 | 0.072886 | 0.10389 | -0.035252 | 59.6874 | 59.732 | 59.6599 | 59.5859 | 62.261 | 62.3307 | 62.0678 | 62.2737 | -2.5736 | -2.3804 | -2.6011 | -2.4078
93.3438 | 122.3373 | -62.2284 | 59.7565 | 0.12185 | -0.00389 | -0.012 | -0.029595 | 0.040843 | 0.071848 | -0.062717 | 59.6508 | 59.6908 | 59.6279 | 59.5538 | 62.2381 | 62.2941 | 62.0311 | 62.2463 | 0.15389 | 0.028153 | 0.020043 | 0.002448 | 0.072886 | 0.10389 | -0.030674 | 59.6828 | 59.7229 | 59.6599 | 59.5859 | 62.2702 | 62.3261 | 62.0632 | 62.2783 | -2.5874 | -2.3804 | -2.6103 | -2.4033
95.0781 | 122.2092 | -62.3154 | 59.7794 | 0.12185 | 0.000689 | -0.016578 | -0.020438 | 0.045421 | 0.076426 | -0.058139 | 59.6508 | 59.6908 | 59.637 | 59.5538 | 62.2381 | 62.2941 | 62.0266 | 62.2417 | 0.15389 | 0.032732 | 0.015465 | 0.011605 | 0.077464 | 0.10847 | -0.026096 | 59.6828 | 59.7229 | 59.6691 | 59.5859 | 62.2702 | 62.3261 | 62.0586 | 62.2737 | -2.5874 | -2.3758 | -2.6011 | -2.3895
96.7656 | 122.2 | -62.2879 | 59.7931 | 0.12185 | 0.005267 | -0.012 | -0.020438 | 0.040843 | 0.071848 | -0.067295 | 59.6553 | 59.6954 | 59.637 | 59.5584 | 62.2427 | 62.3032 | 62.0266 | 62.2463 | 0.15389 | 0.03731 | 0.020043 | 0.011605 | 0.072886 | 0.10389 | -0.035252 | 59.6874 | 59.7275 | 59.6691 | 59.5905 | 62.2748 | 62.3353 | 62.0586 | 62.2783 | -2.5874 | -2.3712 | -2.6057 | -2.3895
98.5156 | 122.2824 | -62.2742 | 59.7702 | 0.12185 | -0.00389 | -0.025735 | -0.020438 | 0.036265 | 0.076426 | -0.071874 | 59.6553 | 59.7046 | 59.637 | 59.5538 | 62.2427 | 62.3032 | 62.0311 | 62.2417 | 0.15389 | 0.028153 | 0.006308 | 0.011605 | 0.068308 | 0.10847 | -0.039831 | 59.6874 | 59.7366 | 59.6691 | 59.5859 | 62.2748 | 62.3353 | 62.0632 | 62.2737 | -2.5874 | -2.3758 | -2.6057 | -2.3941
100.2031 | 122.2549 | -62.2604 | 59.8206 | 0.11727 | 0.000689 | -0.021157 | -0.01586 | 0.040843 | 0.076426 | -0.076452 | 59.6462 | 59.7046 | 59.6325 | 59.563 | 62.2381 | 62.2987 | 62.0357 | 62.2371 | 0.14932 | 0.032732 | 0.010886 | 0.016183 | 0.072886 | 0.10847 | -0.044409 | 59.6782 | 59.7366 | 59.6645 | 59.595 | 62.2702 | 62.3307 | 62.0678 | 62.2691 | -2.592 | -2.3895 | -2.6057 | -2.4033
101.9531 | 122.2916 | -62.2925 | 59.7702 | 0.11727 | 0.000689 | -0.016578 | -0.025017 | 0.036265 | 0.076426 | -0.062717 | 59.6553 | 59.7 | 59.6416 | 59.5584 | 62.2336 | 62.3032 | 62.0357 | 62.2463 | 0.14932 | 0.032732 | 0.015465 | 0.007026 | 0.068308 | 0.10847 | -0.030674 | 59.6874 | 59.732 | 59.6737 | 59.5905 | 62.2656 | 62.3353 | 62.0678 | 62.2783 | -2.5782 | -2.3804 | -2.5919 | -2.3941
103.625 | 122.2275 | -62.2742 | 59.8343 | 0.12185 | 0.000689 | -0.016578 | -0.01586 | 0.040843 | 0.076426 | -0.058139 | 59.6599 | 59.7 | 59.637 | 59.5538 | 62.2381 | 62.3032 | 62.0311 | 62.2463 | 0.15389 | 0.032732 | 0.015465 | 0.016183 | 0.072886 | 0.10847 | -0.026096 | 59.692 | 59.732 | 59.6691 | 59.5859 | 62.2702 | 62.3353 | 62.0632 | 62.2783 | -2.5782 | -2.3712 | -2.6011 | -2.3941
105.3125 | 122.3328 | -62.2833 | 59.7336 | 0.11269 | 0.005267 | -0.021157 | -0.011281 | 0.040843 | 0.076426 | -0.058139 | 59.6508 | 59.6908 | 59.6325 | 59.5493 | 62.2381 | 62.2987 | 62.0311 | 62.2371 | 0.14474 | 0.03731 | 0.010886 | 0.020762 | 0.072886 | 0.10847 | -0.026096 | 59.6828 | 59.7229 | 59.6645 | 59.5813 | 62.2702 | 62.3307 | 62.0632 | 62.2691 | -2.5874 | -2.3804 | -2.6057 | -2.3987
107.0625 | 122.2824 | -62.2604 | 59.7382 | 0.11727 | 0.000689 | -0.016578 | -0.025017 | 0.045421 | 0.071848 | -0.071874 | 59.6553 | 59.6954 | 59.6416 | 59.5493 | 62.2381 | 62.2987 | 62.0311 | 62.2417 | 0.14932 | 0.032732 | 0.015465 | 0.007026 | 0.077464 | 0.10389 | -0.039831 | 59.6874 | 59.7275 | 59.6737 | 59.5813 | 62.2702 | 62.3307 | 62.0632 | 62.2737 | -2.5828 | -2.3758 | -2.5965 | -2.3895
108.8125 | 122.3694 | -62.2467 | 59.7427 | 0.11727 | 0.000689 | -0.016578 | -0.034174 | 0.036265 | 0.076426 | -0.067295 | 59.6508 | 59.7 | 59.6325 | 59.5538 | 62.2427 | 62.2987 | 62.0311 | 62.2463 | 0.14932 | 0.032732 | 0.015465 | -0.002131 | 0.068308 | 0.10847 | -0.035252 | 59.6828 | 59.732 | 59.6645 | 59.5859 | 62.2748 | 62.3307 | 62.0632 | 62.2783 | -2.592 | -2.3804 | -2.6103 | -2.3987
110.5156 | 122.3053 | -62.2742 | 59.7473 | 0.12185 | 0.000689 | -0.016578 | -0.01586 | 0.036265 | 0.076426 | -0.062717 | 59.6508 | 59.6954 | 59.6325 | 59.5538 | 62.2381 | 62.2987 | 62.0311 | 62.2417 | 0.15389 | 0.032732 | 0.015465 | 0.016183 | 0.068308 | 0.10847 | -0.030674 | 59.6828 | 59.7275 | 59.6645 | 59.5859 | 62.2702 | 62.3307 | 62.0632 | 62.2737 | -2.5874 | -2.3804 | -2.6057 | -2.3987
112.2031 | 122.3373 | -62.2833 | 59.697 | 0.12643 | 0.005267 | -0.016578 | -0.020438 | 0.036265 | 0.076426 | -0.067295 | 59.6599 | 59.6908 | 59.6325 | 59.563 | 62.2381 | 62.3032 | 62.0357 | 62.2417 | 0.15847 | 0.03731 | 0.015465 | 0.011605 | 0.068308 | 0.10847 | -0.035252 | 59.692 | 59.7229 | 59.6645 | 59.595 | 62.2702 | 62.3353 | 62.0678 | 62.2737 | -2.5782 | -2.3758 | -2.6057 | -2.4033
113.9375 | 122.3053 | -62.2971 | 59.7473 | 0.11269 | 0.000689 | -0.021157 | -0.020438 | 0.036265 | 0.076426 | -0.071874 | 59.6553 | 59.7 | 59.637 | 59.5584 | 62.2336 | 62.3032 | 62.0266 | 62.2417 | 0.14474 | 0.032732 | 0.010886 | 0.011605 | 0.068308 | 0.10847 | -0.039831 | 59.6874 | 59.732 | 59.6691 | 59.5905 | 62.2656 | 62.3353 | 62.0586 | 62.2737 | -2.5782 | -2.3712 | -2.5965 | -2.3895
115.6719 | 122.2824 | -62.2742 | 59.7702 | 0.12643 | 0.000689 | -0.021157 | -0.020438 | 0.040843 | 0.076426 | -0.062717 | 59.6508 | 59.6954 | 59.637 | 59.5584 | 62.2381 | 62.2987 | 62.0311 | 62.2417 | 0.15847 | 0.032732 | 0.010886 | 0.011605 | 0.072886 | 0.10847 | -0.030674 | 59.6828 | 59.7275 | 59.6691 | 59.5905 | 62.2702 | 62.3307 | 62.0632 | 62.2737 | -2.5874 | -2.3804 | -2.6011 | -2.3941
117.3594 | 122.2412 | -62.2971 | 59.7656 | 0.12643 | -0.00389 | -0.021157 | -0.029595 | 0.040843 | 0.076426 | -0.062717 | 59.6508 | 59.6954 | 59.637 | 59.5538 | 62.2381 | 62.3032 | 62.0311 | 62.2463 | 0.15847 | 0.028153 | 0.010886 | 0.002448 | 0.072886 | 0.10847 | -0.030674 | 59.6828 | 59.7275 | 59.6691 | 59.5859 | 62.2702 | 62.3353 | 62.0632 | 62.2783 | -2.5874 | -2.3804 | -2.6011 | -2.3941
119.1094 | 122.2458 | -62.2742 | 59.7977 | 0.12185 | 0.005267 | -0.021157 | -0.020438 | 0.040843 | 0.085583 | -0.067295 | 59.6645 | 59.6954 | 59.6416 | 59.5538 | 62.2381 | 62.3032 | 62.0266 | 62.2417 | 0.15389 | 0.03731 | 0.010886 | 0.011605 | 0.072886 | 0.11763 | -0.035252 | 59.6965 | 59.7275 | 59.6737 | 59.5859 | 62.2702 | 62.3353 | 62.0586 | 62.2737 | -2.5736 | -2.3621 | -2.5965 | -2.3849
120.7969 | 122.2641 | -62.2467 | 59.8297 | 0.12643 | -0.00389 | -0.016578 | -0.020438 | 0.036265 | 0.076426 | -0.062717 | 59.6553 | 59.6908 | 59.6416 | 59.5584 | 62.2381 | 62.2987 | 62.0311 | 62.2371 | 0.15847 | 0.028153 | 0.015465 | 0.011605 | 0.068308 | 0.10847 | -0.030674 | 59.6874 | 59.7229 | 59.6737 | 59.5905 | 62.2702 | 62.3307 | 62.0632 | 62.2691 | -2.5828 | -2.3758 | -2.5965 | -2.3895
122.7031 | 122.2504 | -62.2467 | 59.8251 | 0.11727 | 0.000689 | -0.016578 | -0.020438 | 0.031687 | 0.076426 | -0.071874 | 59.6553 | 59.7 | 59.6416 | 59.5584 | 62.2381 | 62.3032 | 62.022 | 62.2417 | 0.14932 | 0.032732 | 0.015465 | 0.011605 | 0.06373 | 0.10847 | -0.039831 | 59.6874 | 59.732 | 59.6737 | 59.5905 | 62.2702 | 62.3353 | 62.054 | 62.2737 | -2.5828 | -2.3666 | -2.5965 | -2.3804
124.4688 | 122.2504 | -62.2833 | 59.7931 | 0.12643 | 0.005267 | -0.012 | -0.025017 | 0.036265 | 0.081005 | -0.071874 | 59.6553 | 59.6908 | 59.6416 | 59.5538 | 62.2427 | 62.2987 | 62.0311 | 62.2371 | 0.15847 | 0.03731 | 0.020043 | 0.007026 | 0.068308 | 0.11305 | -0.039831 | 59.6874 | 59.7229 | 59.6737 | 59.5859 | 62.2748 | 62.3307 | 62.0632 | 62.2691 | -2.5874 | -2.3758 | -2.6011 | -2.3895
126.1562 | 122.2961 | -62.2971 | 59.7656 | 0.12185 | 0.000689 | -0.016578 | -0.01586 | 0.040843 | 0.076426 | -0.067295 | 59.6553 | 59.6908 | 59.637 | 59.5538 | 62.2427 | 62.3078 | 62.0357 | 62.2417 | 0.15389 | 0.032732 | 0.015465 | 0.016183 | 0.072886 | 0.10847 | -0.035252 | 59.6874 | 59.7229 | 59.6691 | 59.5859 | 62.2748 | 62.3398 | 62.0678 | 62.2737 | -2.5874 | -2.3804 | -2.6057 | -2.3987
127.8906 | 122.3282 | -62.2467 | 59.7702 | 0.12643 | -0.00389 | -0.021157 | -0.01586 | 0.031687 | 0.071848 | -0.067295 | 59.6553 | 59.6954 | 59.637 | 59.5584 | 62.2336 | 62.3032 | 62.0266 | 62.2417 | 0.15847 | 0.028153 | 0.010886 | 0.016183 | 0.06373 | 0.10389 | -0.035252 | 59.6874 | 59.7275 | 59.6691 | 59.5905 | 62.2656 | 62.3353 | 62.0586 | 62.2737 | -2.5782 | -2.3712 | -2.5965 | -2.3895
129.625 | 122.2183 | -62.2238 | 59.8068 | 0.11269 | 0.009846 | -0.016578 | -0.025017 | 0.036265 | 0.076426 | -0.067295 | 59.6508 | 59.6954 | 59.6325 | 59.5538 | 62.2336 | 62.2941 | 62.0311 | 62.2371 | 0.14474 | 0.041889 | 0.015465 | 0.007026 | 0.068308 | 0.10847 | -0.035252 | 59.6828 | 59.7275 | 59.6645 | 59.5859 | 62.2656 | 62.3261 | 62.0632 | 62.2691 | -2.5828 | -2.3804 | -2.6011 | -2.3987
131.3125 | 122.3328 | -62.2971 | 59.7336 | 0.13101 | 0.005267 | -0.012 | -0.020438 | 0.036265 | 0.067269 | -0.071874 | 59.6599 | 59.6954 | 59.6325 | 59.5493 | 62.2381 | 62.2987 | 62.0266 | 62.2417 | 0.16305 | 0.03731 | 0.020043 | 0.011605 | 0.068308 | 0.099312 | -0.039831 | 59.692 | 59.7275 | 59.6645 | 59.5813 | 62.2702 | 62.3307 | 62.0586 | 62.2737 | -2.5782 | -2.3666 | -2.6057 | -2.3941
133.0625 | 122.3145 | -62.2971 | 59.7427 | 0.11727 | 0.005267 | -0.021157 | -0.020438 | 0.045421 | 0.071848 | -0.071874 | 59.6553 | 59.6954 | 59.637 | 59.5538 | 62.2427 | 62.2941 | 62.0357 | 62.2371 | 0.14932 | 0.03731 | 0.010886 | 0.011605 | 0.077464 | 0.10389 | -0.039831 | 59.6874 | 59.7275 | 59.6691 | 59.5859 | 62.2748 | 62.3261 | 62.0678 | 62.2691 | -2.5874 | -2.3804 | -2.6057 | -2.3987
134.75 | 122.3557 | -62.2467 | 59.7427 | 0.11727 | 0.000689 | -0.025735 | -0.025017 | 0.040843 | 0.067269 | -0.067295 | 59.6553 | 59.6954 | 59.6416 | 59.563 | 62.2427 | 62.3032 | 62.0357 | 62.2463 | 0.14932 | 0.032732 | 0.006308 | 0.007026 | 0.072886 | 0.099312 | -0.035252 | 59.6874 | 59.7275 | 59.6737 | 59.595 | 62.2748 | 62.3353 | 62.0678 | 62.2783 | -2.5874 | -2.3804 | -2.6011 | -2.3941
136.5 | 122.2549 | -62.2925 | 59.8251 | 0.11727 | 0.000689 | -0.016578 | -0.025017 | 0.040843 | 0.076426 | -0.067295 | 59.6553 | 59.6908 | 59.6416 | 59.5538 | 62.2427 | 62.2941 | 62.0266 | 62.2417 | 0.14932 | 0.032732 | 0.015465 | 0.007026 | 0.072886 | 0.10847 | -0.035252 | 59.6874 | 59.7229 | 59.6737 | 59.5859 | 62.2748 | 62.3261 | 62.0586 | 62.2737 | -2.5874 | -2.3712 | -2.6011 | -2.3849
138.1875 | 122.3602 | -62.2559 | 59.7565 | 0.12185 | 0.000689 | -0.021157 | -0.020438 | 0.036265 | 0.076426 | -0.071874 | 59.6553 | 59.6908 | 59.637 | 59.5584 | 62.2427 | 62.3078 | 62.0357 | 62.2417 | 0.15389 | 0.032732 | 0.010886 | 0.011605 | 0.068308 | 0.10847 | -0.039831 | 59.6874 | 59.7229 | 59.6691 | 59.5905 | 62.2748 | 62.3398 | 62.0678 | 62.2737 | -2.5874 | -2.3804 | -2.6057 | -2.3987
139.9219 | 122.3557 | -62.2375 | 59.7885 | 0.11727 | 0.000689 | -0.021157 | -0.020438 | 0.036265 | 0.081005 | -0.062717 | 59.6508 | 59.6908 | 59.637 | 59.5584 | 62.2381 | 62.2987 | 62.0357 | 62.2463 | 0.14932 | 0.032732 | 0.010886 | 0.011605 | 0.068308 | 0.11305 | -0.030674 | 59.6828 | 59.7229 | 59.6691 | 59.5905 | 62.2702 | 62.3307 | 62.0678 | 62.2783 | -2.5874 | -2.385 | -2.6011 | -2.3987
141.6562 | 122.2504 | -62.2559 | 59.8251 | 0.11727 | 0.005267 | -0.016578 | -0.025017 | 0.040843 | 0.081005 | -0.062717 | 59.6553 | 59.6954 | 59.637 | 59.5584 | 62.2381 | 62.2895 | 62.0403 | 62.2417 | 0.14932 | 0.03731 | 0.015465 | 0.007026 | 0.072886 | 0.11305 | -0.030674 | 59.6874 | 59.7275 | 59.6691 | 59.5905 | 62.2702 | 62.3215 | 62.0723 | 62.2737 | -2.5828 | -2.385 | -2.6011 | -2.4033
143.3438 | 122.2229 | -62.3154 | 59.7519 | 0.12643 | 0.000689 | -0.016578 | -0.020438 | 0.040843 | 0.076426 | -0.053561 | 59.6553 | 59.6954 | 59.6325 | 59.5584 | 62.2427 | 62.3032 | 62.0311 | 62.2371 | 0.15847 | 0.032732 | 0.015465 | 0.011605 | 0.072886 | 0.10847 | -0.021518 | 59.6874 | 59.7275 | 59.6645 | 59.5905 | 62.2748 | 62.3353 | 62.0632 | 62.2691 | -2.5874 | -2.3758 | -2.6103 | -2.3987
145.1094 | 122.2504 | -62.2925 | 59.7931 | 0.12185 | 0.005267 | -0.016578 | -0.020438 | 0.036265 | 0.076426 | -0.062717 | 59.6553 | 59.7046 | 59.6462 | 59.5538 | 62.2427 | 62.2987 | 62.022 | 62.2417 | 0.15389 | 0.03731 | 0.015465 | 0.011605 | 0.068308 | 0.10847 | -0.030674 | 59.6874 | 59.7366 | 59.6782 | 59.5859 | 62.2748 | 62.3307 | 62.054 | 62.2737 | -2.5874 | -2.3666 | -2.5965 | -2.3758
146.7969 | 122.2321 | -62.2604 | 59.8206 | 0.12643 | -0.00389 | -0.021157 | -0.025017 | 0.040843 | 0.076426 | -0.067295 | 59.6508 | 59.6908 | 59.637 | 59.5538 | 62.2427 | 62.2987 | 62.0357 | 62.2371 | 0.15847 | 0.028153 | 0.010886 | 0.007026 | 0.072886 | 0.10847 | -0.035252 | 59.6828 | 59.7229 | 59.6691 | 59.5859 | 62.2748 | 62.3307 | 62.0678 | 62.2691 | -2.592 | -2.385 | -2.6057 | -2.3987
148.5312 | 122.3602 | -62.2742 | 59.7931 | 0.11727 | 0.005267 | -0.021157 | -0.025017 | 0.031687 | 0.067269 | -0.067295 | 59.6599 | 59.7 | 59.6416 | 59.5493 | 62.2336 | 62.2895 | 62.0403 | 62.2417 | 0.14932 | 0.03731 | 0.010886 | 0.007026 | 0.06373 | 0.099312 | -0.035252 | 59.692 | 59.732 | 59.6737 | 59.5813 | 62.2656 | 62.3215 | 62.0723 | 62.2737 | -2.5736 | -2.3804 | -2.5919 | -2.3987
150.2188 | 122.2458 | -62.2833 | 59.7839 | 0.13101 | 0.009846 | -0.016578 | -0.01586 | 0.036265 | 0.071848 | -0.058139 | 59.6508 | 59.6954 | 59.637 | 59.5676 | 62.2381 | 62.2941 | 62.0311 | 62.2417 | 0.16305 | 0.041889 | 0.015465 | 0.016183 | 0.068308 | 0.10389 | -0.026096 | 59.6828 | 59.7275 | 59.6691 | 59.5996 | 62.2702 | 62.3261 | 62.0632 | 62.2737 | -2.5874 | -2.3804 | -2.6011 | -2.3941
151.9531 | 122.3465 | -62.2833 | 59.7153 | 0.11727 | -0.00389 | -0.021157 | -0.020438 | 0.036265 | 0.067269 | -0.067295 | 59.6508 | 59.6908 | 59.637 | 59.5493 | 62.2381 | 62.2987 | 62.0311 | 62.2371 | 0.14932 | 0.028153 | 0.010886 | 0.011605 | 0.068308 | 0.099312 | -0.035252 | 59.6828 | 59.7229 | 59.6691 | 59.5813 | 62.2702 | 62.3307 | 62.0632 | 62.2691 | -2.5874 | -2.3804 | -2.6011 | -2.3941
153.6875 | 122.3007 | -62.2833 | 59.761 | 0.11727 | 0.000689 | -0.025735 | -0.020438 | 0.031687 | 0.067269 | -0.062717 | 59.6599 | 59.7 | 59.6325 | 59.5493 | 62.2381 | 62.2987 | 62.0266 | 62.2463 | 0.14932 | 0.032732 | 0.006308 | 0.011605 | 0.06373 | 0.099312 | -0.030674 | 59.692 | 59.732 | 59.6645 | 59.5813 | 62.2702 | 62.3307 | 62.0586 | 62.2783 | -2.5782 | -2.3666 | -2.6057 | -2.3941
155.375 | 122.2321 | -62.2742 | 59.8343 | 0.12185 | 0.000689 | -0.016578 | -0.020438 | 0.040843 | 0.076426 | -0.071874 | 59.6645 | 59.6908 | 59.6416 | 59.5584 | 62.2427 | 62.2987 | 62.0311 | 62.2508 | 0.15389 | 0.032732 | 0.015465 | 0.011605 | 0.072886 | 0.10847 | -0.039831 | 59.6965 | 59.7229 | 59.6737 | 59.5905 | 62.2748 | 62.3307 | 62.0632 | 62.2829 | -2.5782 | -2.3666 | -2.6011 | -2.3895
157.125 | 122.3373 | -62.265 | 59.7382 | 0.12643 | 0.009846 | -0.016578 | -0.020438 | 0.036265 | 0.071848 | -0.067295 | 59.6553 | 59.6908 | 59.6416 | 59.5493 | 62.2336 | 62.2987 | 62.0403 | 62.2463 | 0.15847 | 0.041889 | 0.015465 | 0.011605 | 0.068308 | 0.10389 | -0.035252 | 59.6874 | 59.7229 | 59.6737 | 59.5813 | 62.2656 | 62.3307 | 62.0723 | 62.2783 | -2.5782 | -2.385 | -2.5919 | -2.3987
158.7969 | 122.2183 | -62.2833 | 59.8206 | 0.11727 | 0.000689 | -0.021157 | -0.01586 | 0.040843 | 0.081005 | -0.067295 | 59.6508 | 59.6908 | 59.637 | 59.5584 | 62.2427 | 62.3032 | 62.0311 | 62.2371 | 0.14932 | 0.032732 | 0.010886 | 0.016183 | 0.072886 | 0.11305 | -0.035252 | 59.6828 | 59.7229 | 59.6691 | 59.5905 | 62.2748 | 62.3353 | 62.0632 | 62.2691 | -2.592 | -2.3804 | -2.6057 | -2.3941
160.5469 | 122.2916 | -62.2833 | 59.7565 | 0.12185 | 0.000689 | -0.021157 | -0.025017 | 0.036265 | 0.071848 | -0.067295 | 59.6553 | 59.6954 | 59.6325 | 59.5493 | 62.2381 | 62.3032 | 62.0357 | 62.2417 | 0.15389 | 0.032732 | 0.010886 | 0.007026 | 0.068308 | 0.10389 | -0.035252 | 59.6874 | 59.7275 | 59.6645 | 59.5813 | 62.2702 | 62.3353 | 62.0678 | 62.2737 | -2.5828 | -2.3804 | -2.6057 | -2.4033
162.2969 | 122.2549 | -62.2467 | 59.8297 | 0.11727 | 0.000689 | -0.012 | -0.01586 | 0.036265 | 0.071848 | -0.067295 | 59.6553 | 59.7 | 59.637 | 59.5538 | 62.2427 | 62.3032 | 62.0357 | 62.2371 | 0.14932 | 0.032732 | 0.020043 | 0.016183 | 0.068308 | 0.10389 | -0.035252 | 59.6874 | 59.732 | 59.6691 | 59.5859 | 62.2748 | 62.3353 | 62.0678 | 62.2691 | -2.5874 | -2.3804 | -2.6057 | -2.3987
164.0312 | 122.2595 | -62.2879 | 59.8206 | 0.12185 | 0.005267 | -0.007421 | -0.020438 | 0.040843 | 0.076426 | -0.062717 | 59.6645 | 59.6954 | 59.6508 | 59.5538 | 62.2381 | 62.2987 | 62.0311 | 62.2417 | 0.15389 | 0.03731 | 0.024622 | 0.011605 | 0.072886 | 0.10847 | -0.030674 | 59.6965 | 59.7275 | 59.6828 | 59.5859 | 62.2702 | 62.3307 | 62.0632 | 62.2737 | -2.5736 | -2.3666 | -2.5874 | -2.3804
165.7031 | 122.2961 | -62.3016 | 59.7565 | 0.11727 | 0.005267 | -0.016578 | -0.025017 | 0.036265 | 0.076426 | -0.058139 | 59.6599 | 59.6908 | 59.637 | 59.5538 | 62.2427 | 62.2941 | 62.0266 | 62.2417 | 0.14932 | 0.03731 | 0.015465 | 0.007026 | 0.068308 | 0.10847 | -0.026096 | 59.692 | 59.7229 | 59.6691 | 59.5859 | 62.2748 | 62.3261 | 62.0586 | 62.2737 | -2.5828 | -2.3666 | -2.6057 | -2.3895
167.4531 | 122.3145 | -62.2421 | 59.7931 | 0.11727 | 0.005267 | -0.016578 | -0.025017 | 0.036265 | 0.071848 | -0.062717 | 59.6599 | 59.6954 | 59.6416 | 59.5584 | 62.2427 | 62.3032 | 62.0311 | 62.2417 | 0.14932 | 0.03731 | 0.015465 | 0.007026 | 0.068308 | 0.10389 | -0.030674 | 59.692 | 59.7275 | 59.6737 | 59.5905 | 62.2748 | 62.3353 | 62.0632 | 62.2737 | -2.5828 | -2.3712 | -2.6011 | -2.3895
169.2031 | 122.2046 | -62.2696 | 59.8297 | 0.12185 | 0.005267 | -0.016578 | -0.011281 | 0.040843 | 0.081005 | -0.067295 | 59.6508 | 59.6954 | 59.6416 | 59.5584 | 62.2427 | 62.3032 | 62.0311 | 62.2463 | 0.15389 | 0.03731 | 0.015465 | 0.020762 | 0.072886 | 0.11305 | -0.035252 | 59.6828 | 59.7275 | 59.6737 | 59.5905 | 62.2748 | 62.3353 | 62.0632 | 62.2783 | -2.592 | -2.3804 | -2.6011 | -2.3895
170.8906 | 122.3099 | -62.265 | 59.7931 | 0.11727 | 0.000689 | -0.030314 | -0.020438 | 0.036265 | 0.067269 | -0.071874 | 59.6599 | 59.6954 | 59.637 | 59.5493 | 62.2427 | 62.2987 | 62.0311 | 62.2417 | 0.14932 | 0.032732 | 0.001729 | 0.011605 | 0.068308 | 0.099312 | -0.039831 | 59.692 | 59.7275 | 59.6691 | 59.5813 | 62.2748 | 62.3307 | 62.0632 | 62.2737 | -2.5828 | -2.3712 | -2.6057 | -2.3941
172.6406 | 122.2824 | -62.2787 | 59.761 | 0.12185 | 0.009846 | -0.025735 | -0.025017 | 0.040843 | 0.076426 | -0.062717 | 59.6645 | 59.7 | 59.637 | 59.5538 | 62.2381 | 62.2941 | 62.022 | 62.2417 | 0.15389 | 0.041889 | 0.006308 | 0.007026 | 0.072886 | 0.10847 | -0.030674 | 59.6965 | 59.732 | 59.6691 | 59.5859 | 62.2702 | 62.3261 | 62.054 | 62.2737 | -2.5736 | -2.3575 | -2.6011 | -2.3849
174.375 | 122.3511 | -62.2513 | 59.7565 | 0.12185 | 0.000689 | -0.021157 | -0.011281 | 0.027109 | 0.067269 | -0.067295 | 59.6553 | 59.6908 | 59.6416 | 59.563 | 62.2381 | 62.2987 | 62.0357 | 62.2417 | 0.15389 | 0.032732 | 0.010886 | 0.020762 | 0.059152 | 0.099312 | -0.035252 | 59.6874 | 59.7229 | 59.6737 | 59.595 | 62.2702 | 62.3307 | 62.0678 | 62.2737 | -2.5828 | -2.3804 | -2.5965 | -2.3941
176.1094 | 122.3236 | -62.2421 | 59.7702 | 0.12185 | 0.009846 | -0.021157 | -0.020438 | 0.036265 | 0.071848 | -0.067295 | 59.6599 | 59.6908 | 59.637 | 59.5538 | 62.2381 | 62.2987 | 62.0311 | 62.2371 | 0.15389 | 0.041889 | 0.010886 | 0.011605 | 0.068308 | 0.10389 | -0.035252 | 59.692 | 59.7229 | 59.6691 | 59.5859 | 62.2702 | 62.3307 | 62.0632 | 62.2691 | -2.5782 | -2.3712 | -2.6011 | -2.3941
177.8594 | 122.2092 | -62.3199 | 59.8022 | 0.12185 | -0.00389 | -0.016578 | -0.01586 | 0.040843 | 0.081005 | -0.067295 | 59.6599 | 59.6954 | 59.637 | 59.5538 | 62.2427 | 62.3032 | 62.0311 | 62.2463 | 0.15389 | 0.028153 | 0.015465 | 0.016183 | 0.072886 | 0.11305 | -0.035252 | 59.692 | 59.7275 | 59.6691 | 59.5859 | 62.2748 | 62.3353 | 62.0632 | 62.2783 | -2.5828 | -2.3712 | -2.6057 | -2.3941
179.5469 | 122.3007 | -62.2604 | 59.7748 | 0.12185 | -0.00389 | -0.025735 | -0.020438 | 0.036265 | 0.071848 | -0.067295 | 59.6553 | 59.6954 | 59.637 | 59.5493 | 62.2381 | 62.3032 | 62.0357 | 62.2463 | 0.15389 | 0.028153 | 0.006308 | 0.011605 | 0.068308 | 0.10389 | -0.035252 | 59.6874 | 59.7275 | 59.6691 | 59.5813 | 62.2702 | 62.3353 | 62.0678 | 62.2783 | -2.5828 | -2.3804 | -2.6011 | -2.3987
181.2969 | 122.2961 | -62.2833 | 59.7153 | 0.11727 | 0.000689 | -0.016578 | -0.020438 | 0.036265 | 0.071848 | -0.062717 | 59.6599 | 59.6908 | 59.637 | 59.5538 | 62.2381 | 62.2987 | 62.0266 | 62.2417 | 0.14932 | 0.032732 | 0.015465 | 0.011605 | 0.068308 | 0.10389 | -0.030674 | 59.692 | 59.7229 | 59.6691 | 59.5859 | 62.2702 | 62.3307 | 62.0586 | 62.2737 | -2.5782 | -2.3666 | -2.6011 | -2.3895
183.0469 | 122.2916 | -62.2833 | 59.729 | 0.12643 | 0.000689 | -0.021157 | -0.025017 | 0.040843 | 0.076426 | -0.067295 | 59.6599 | 59.6908 | 59.6416 | 59.5538 | 62.2473 | 62.2987 | 62.0357 | 62.2463 | 0.15847 | 0.032732 | 0.010886 | 0.007026 | 0.072886 | 0.10847 | -0.035252 | 59.692 | 59.7229 | 59.6737 | 59.5859 | 62.2793 | 62.3307 | 62.0678 | 62.2783 | -2.5874 | -2.3758 | -2.6057 | -2.3941
184.7344 | 122.3373 | -62.2375 | 59.7885 | 0.12185 | 0.000689 | -0.021157 | -0.029595 | 0.040843 | 0.076426 | -0.062717 | 59.6553 | 59.6954 | 59.637 | 59.563 | 62.2336 | 62.2987 | 62.022 | 62.2463 | 0.15389 | 0.032732 | 0.010886 | 0.002448 | 0.072886 | 0.10847 | -0.030674 | 59.6874 | 59.7275 | 59.6691 | 59.595 | 62.2656 | 62.3307 | 62.054 | 62.2783 | -2.5782 | -2.3666 | -2.5965 | -2.3849
186.4844 | 122.3648 | -62.2696 | 59.7427 | 0.12185 | 0.005267 | -0.021157 | -0.020438 | 0.040843 | 0.071848 | -0.067295 | 59.6508 | 59.7 | 59.6462 | 59.563 | 62.2381 | 62.2987 | 62.0311 | 62.2508 | 0.15389 | 0.03731 | 0.010886 | 0.011605 | 0.072886 | 0.10389 | -0.035252 | 59.6828 | 59.732 | 59.6782 | 59.595 | 62.2702 | 62.3307 | 62.0632 | 62.2829 | -2.5874 | -2.3804 | -2.5919 | -2.3849
188.2344 | 122.3373 | -62.265 | 59.7702 | 0.11727 | 0.009846 | -0.021157 | -0.01586 | 0.036265 | 0.067269 | -0.062717 | 59.6599 | 59.6954 | 59.637 | 59.5538 | 62.2381 | 62.2987 | 62.0266 | 62.2417 | 0.14932 | 0.041889 | 0.010886 | 0.016183 | 0.068308 | 0.099312 | -0.030674 | 59.692 | 59.7275 | 59.6691 | 59.5859 | 62.2702 | 62.3307 | 62.0586 | 62.2737 | -2.5782 | -2.3666 | -2.6011 | -2.3895
189.9844 | 122.2183 | -62.265 | 59.7977 | 0.12643 | -0.00389 | -0.016578 | -0.020438 | 0.040843 | 0.071848 | -0.058139 | 59.6553 | 59.6954 | 59.6462 | 59.5584 | 62.2473 | 62.3032 | 62.0357 | 62.2508 | 0.15847 | 0.028153 | 0.015465 | 0.011605 | 0.072886 | 0.10389 | -0.026096 | 59.6874 | 59.7275 | 59.6782 | 59.5905 | 62.2793 | 62.3353 | 62.0678 | 62.2829 | -2.592 | -2.3804 | -2.6011 | -2.3895
191.6719 | 122.3602 | -62.2467 | 59.7473 | 0.11269 | 0.005267 | -0.021157 | -0.020438 | 0.040843 | 0.076426 | -0.067295 | 59.6645 | 59.7 | 59.637 | 59.5538 | 62.2427 | 62.3032 | 62.0357 | 62.2463 | 0.14474 | 0.03731 | 0.010886 | 0.011605 | 0.072886 | 0.10847 | -0.035252 | 59.6965 | 59.732 | 59.6691 | 59.5859 | 62.2748 | 62.3353 | 62.0678 | 62.2783 | -2.5782 | -2.3712 | -2.6057 | -2.3987
193.4062 | 122.2092 | -62.2787 | 59.8297 | 0.12185 | 0.005267 | -0.016578 | -0.025017 | 0.036265 | 0.076426 | -0.062717 | 59.6599 | 59.6908 | 59.637 | 59.5538 | 62.2381 | 62.3078 | 62.0311 | 62.2417 | 0.15389 | 0.03731 | 0.015465 | 0.007026 | 0.068308 | 0.10847 | -0.030674 | 59.692 | 59.7229 | 59.6691 | 59.5859 | 62.2702 | 62.3398 | 62.0632 | 62.2737 | -2.5782 | -2.3712 | -2.6011 | -2.3941
195.0781 | 122.2137 | -62.2879 | 59.7885 | 0.11727 | 0.005267 | -0.012 | -0.025017 | 0.036265 | 0.067269 | -0.058139 | 59.6599 | 59.6954 | 59.637 | 59.563 | 62.2381 | 62.2941 | 62.0311 | 62.2417 | 0.14932 | 0.03731 | 0.020043 | 0.007026 | 0.068308 | 0.099312 | -0.026096 | 59.692 | 59.7275 | 59.6691 | 59.595 | 62.2702 | 62.3261 | 62.0632 | 62.2737 | -2.5782 | -2.3712 | -2.6011 | -2.3941
196.8125 | 122.2229 | -62.2742 | 59.7931 | 0.12185 | 0.000689 | -0.012 | -0.011281 | 0.045421 | 0.071848 | -0.058139 | 59.6553 | 59.7046 | 59.6462 | 59.5584 | 62.2381 | 62.2987 | 62.0311 | 62.2371 | 0.15389 | 0.032732 | 0.020043 | 0.020762 | 0.077464 | 0.10389 | -0.026096 | 59.6874 | 59.7366 | 59.6782 | 59.5905 | 62.2702 | 62.3307 | 62.0632 | 62.2691 | -2.5828 | -2.3758 | -2.5919 | -2.3849
198.5 | 122.2046 | -62.2787 | 59.8206 | 0.11727 | 0.000689 | -0.012 | -0.020438 | 0.036265 | 0.071848 | -0.067295 | 59.6599 | 59.7 | 59.6416 | 59.5584 | 62.2427 | 62.3032 | 62.0357 | 62.2463 | 0.14932 | 0.032732 | 0.020043 | 0.011605 | 0.068308 | 0.10389 | -0.035252 | 59.692 | 59.732 | 59.6737 | 59.5905 | 62.2748 | 62.3353 | 62.0678 | 62.2783 | -2.5828 | -2.3758 | -2.6011 | -2.3941
200.25 | 122.3282 | -62.2787 | 59.7244 | 0.12185 | 0.000689 | -0.016578 | -0.01586 | 0.040843 | 0.076426 | -0.058139 | 59.6645 | 59.7046 | 59.6416 | 59.5584 | 62.2336 | 62.2987 | 62.0311 | 62.2417 | 0.15389 | 0.032732 | 0.015465 | 0.016183 | 0.072886 | 0.10847 | -0.026096 | 59.6965 | 59.7366 | 59.6737 | 59.5905 | 62.2656 | 62.3307 | 62.0632 | 62.2737 | -2.5691 | -2.3666 | -2.5919 | -2.3895
202 | 122.3282 | -62.2742 | 59.7382 | 0.11727 | 0.000689 | -0.021157 | -0.020438 | 0.040843 | 0.076426 | -0.062717 | 59.6599 | 59.6954 | 59.637 | 59.5584 | 62.2336 | 62.2987 | 62.0266 | 62.2417 | 0.14932 | 0.032732 | 0.010886 | 0.011605 | 0.072886 | 0.10847 | -0.030674 | 59.692 | 59.7275 | 59.6691 | 59.5905 | 62.2656 | 62.3307 | 62.0586 | 62.2737 | -2.5736 | -2.3666 | -2.5965 | -2.3895
203.6875 | 122.2595 | -62.265 | 59.8068 | 0.12643 | 0.000689 | -0.016578 | -0.029595 | 0.040843 | 0.071848 | -0.062717 | 59.6599 | 59.6908 | 59.637 | 59.5584 | 62.2427 | 62.2987 | 62.0311 | 62.2463 | 0.15847 | 0.032732 | 0.015465 | 0.002448 | 0.072886 | 0.10389 | -0.030674 | 59.692 | 59.7229 | 59.6691 | 59.5905 | 62.2748 | 62.3307 | 62.0632 | 62.2783 | -2.5828 | -2.3712 | -2.6057 | -2.3941
205.4375 | 122.3373 | -62.2787 | 59.7244 | 0.12185 | 0.000689 | -0.021157 | -0.020438 | 0.040843 | 0.071848 | -0.062717 | 59.6599 | 59.7 | 59.6416 | 59.5538 | 62.2427 | 62.3032 | 62.0266 | 62.2508 | 0.15389 | 0.032732 | 0.010886 | 0.011605 | 0.072886 | 0.10389 | -0.030674 | 59.692 | 59.732 | 59.6737 | 59.5859 | 62.2748 | 62.3353 | 62.0586 | 62.2829 | -2.5828 | -2.3666 | -2.6011 | -2.3849
207.1094 | 122.3145 | -62.2559 | 59.7565 | 0.12185 | 0.005267 | -0.016578 | -0.011281 | 0.036265 | 0.076426 | -0.062717 | 59.6599 | 59.7 | 59.637 | 59.5538 | 62.2381 | 62.2987 | 62.0311 | 62.2371 | 0.15389 | 0.03731 | 0.015465 | 0.020762 | 0.068308 | 0.10847 | -0.030674 | 59.692 | 59.732 | 59.6691 | 59.5859 | 62.2702 | 62.3307 | 62.0632 | 62.2691 | -2.5782 | -2.3712 | -2.6011 | -2.3941
208.8594 | 122.319 | -62.2787 | 59.7473 | 0.12185 | -0.00389 | -0.016578 | -0.020438 | 0.036265 | 0.071848 | -0.071874 | 59.6599 | 59.7 | 59.6416 | 59.563 | 62.2381 | 62.2987 | 62.0311 | 62.2463 | 0.15389 | 0.028153 | 0.015465 | 0.011605 | 0.068308 | 0.10389 | -0.039831 | 59.692 | 59.732 | 59.6737 | 59.595 | 62.2702 | 62.3307 | 62.0632 | 62.2783 | -2.5782 | -2.3712 | -2.5965 | -2.3895
210.625 | 122.2275 | -62.3108 | 59.7931 | 0.12185 | 0.005267 | -0.021157 | -0.020438 | 0.040843 | 0.071848 | -0.058139 | 59.6553 | 59.6954 | 59.6416 | 59.5584 | 62.2519 | 62.2987 | 62.0266 | 62.2417 | 0.15389 | 0.03731 | 0.010886 | 0.011605 | 0.072886 | 0.10389 | -0.026096 | 59.6874 | 59.7275 | 59.6737 | 59.5905 | 62.2839 | 62.3307 | 62.0586 | 62.2737 | -2.5965 | -2.3712 | -2.6103 | -2.3849
212.3125 | 122.2092 | -62.2742 | 59.8389 | 0.12185 | -0.00389 | -0.016578 | -0.01586 | 0.036265 | 0.071848 | -0.067295 | 59.6645 | 59.7 | 59.637 | 59.563 | 62.2473 | 62.2987 | 62.0311 | 62.2417 | 0.15389 | 0.028153 | 0.015465 | 0.016183 | 0.068308 | 0.10389 | -0.035252 | 59.6965 | 59.732 | 59.6691 | 59.595 | 62.2793 | 62.3307 | 62.0632 | 62.2737 | -2.5828 | -2.3666 | -2.6103 | -2.3941
214.0469 | 122.2412 | -62.2604 | 59.8389 | 0.12185 | 0.005267 | -0.021157 | -0.011281 | 0.040843 | 0.071848 | -0.062717 | 59.6599 | 59.6954 | 59.637 | 59.5538 | 62.2336 | 62.2987 | 62.0266 | 62.2463 | 0.15389 | 0.03731 | 0.010886 | 0.020762 | 0.072886 | 0.10389 | -0.030674 | 59.692 | 59.7275 | 59.6691 | 59.5859 | 62.2656 | 62.3307 | 62.0586 | 62.2783 | -2.5736 | -2.3666 | -2.5965 | -2.3895
215.7812 | 122.3419 | -62.265 | 59.7748 | 0.11727 | -0.00389 | -0.021157 | -0.029595 | 0.040843 | 0.076426 | -0.071874 | 59.6691 | 59.7 | 59.6325 | 59.563 | 62.2473 | 62.2987 | 62.0311 | 62.2417 | 0.14932 | 0.028153 | 0.010886 | 0.002448 | 0.072886 | 0.10847 | -0.039831 | 59.7011 | 59.732 | 59.6645 | 59.595 | 62.2793 | 62.3307 | 62.0632 | 62.2737 | -2.5782 | -2.3621 | -2.6148 | -2.3987
217.5469 | 122.3328 | -62.2971 | 59.7382 | 0.11727 | 0.000689 | -0.012 | -0.025017 | 0.045421 | 0.071848 | -0.062717 | 59.6553 | 59.7 | 59.6279 | 59.5493 | 62.2381 | 62.3032 | 62.0266 | 62.2463 | 0.14932 | 0.032732 | 0.020043 | 0.007026 | 0.077464 | 0.10389 | -0.030674 | 59.6874 | 59.732 | 59.6599 | 59.5813 | 62.2702 | 62.3353 | 62.0586 | 62.2783 | -2.5828 | -2.3712 | -2.6103 | -2.3987
219.2344 | 122.2321 | -62.2879 | 59.8022 | 0.12185 | -0.00389 | -0.016578 | -0.01586 | 0.036265 | 0.067269 | -0.062717 | 59.6645 | 59.6908 | 59.637 | 59.5493 | 62.2381 | 62.2987 | 62.0311 | 62.2417 | 0.15389 | 0.028153 | 0.015465 | 0.016183 | 0.068308 | 0.099312 | -0.030674 | 59.6965 | 59.7229 | 59.6691 | 59.5813 | 62.2702 | 62.3307 | 62.0632 | 62.2737 | -2.5736 | -2.3666 | -2.6011 | -2.3941
220.9844 | 122.3419 | -62.2559 | 59.761 | 0.12643 | -0.00389 | -0.021157 | -0.025017 | 0.036265 | 0.067269 | -0.067295 | 59.6599 | 59.6954 | 59.637 | 59.5538 | 62.2427 | 62.3032 | 62.0311 | 62.2463 | 0.15847 | 0.028153 | 0.010886 | 0.007026 | 0.068308 | 0.099312 | -0.035252 | 59.692 | 59.7275 | 59.6691 | 59.5859 | 62.2748 | 62.3353 | 62.0632 | 62.2783 | -2.5828 | -2.3712 | -2.6057 | -2.3941
222.75 | 122.3053 | -62.2833 | 59.7565 | 0.12643 | -0.00389 | -0.016578 | -0.025017 | 0.036265 | 0.076426 | -0.071874 | 59.6599 | 59.7046 | 59.637 | 59.563 | 62.2427 | 62.2987 | 62.0311 | 62.2508 | 0.15847 | 0.028153 | 0.015465 | 0.007026 | 0.068308 | 0.10847 | -0.039831 | 59.692 | 59.7366 | 59.6691 | 59.595 | 62.2748 | 62.3307 | 62.0632 | 62.2829 | -2.5828 | -2.3712 | -2.6057 | -2.3941
224.4375 | 122.2458 | -62.2604 | 59.8022 | 0.12643 | 0.000689 | -0.016578 | -0.01586 | 0.040843 | 0.071848 | -0.062717 | 59.6645 | 59.6954 | 59.637 | 59.5538 | 62.229 | 62.3032 | 62.0266 | 62.2371 | 0.15847 | 0.032732 | 0.015465 | 0.016183 | 0.072886 | 0.10389 | -0.030674 | 59.6965 | 59.7275 | 59.6691 | 59.5859 | 62.261 | 62.3353 | 62.0586 | 62.2691 | -2.5645 | -2.3621 | -2.5919 | -2.3895
226.1875 | 122.319 | -62.2833 | 59.7519 | 0.12643 | 0.000689 | -0.021157 | -0.020438 | 0.040843 | 0.071848 | -0.062717 | 59.6599 | 59.7 | 59.6416 | 59.5538 | 62.2381 | 62.3124 | 62.0266 | 62.2463 | 0.15847 | 0.032732 | 0.010886 | 0.011605 | 0.072886 | 0.10389 | -0.030674 | 59.692 | 59.732 | 59.6737 | 59.5859 | 62.2702 | 62.3444 | 62.0586 | 62.2783 | -2.5782 | -2.3666 | -2.5965 | -2.3849
227.8594 | 122.2183 | -62.2833 | 59.8343 | 0.12643 | -0.00389 | -0.012 | -0.020438 | 0.040843 | 0.076426 | -0.062717 | 59.6553 | 59.7 | 59.6462 | 59.5584 | 62.2473 | 62.2987 | 62.0311 | 62.2417 | 0.15847 | 0.028153 | 0.020043 | 0.011605 | 0.072886 | 0.10847 | -0.030674 | 59.6874 | 59.732 | 59.6782 | 59.5905 | 62.2793 | 62.3307 | 62.0632 | 62.2737 | -2.592 | -2.3758 | -2.6011 | -2.3849
229.5938 | 122.2458 | -62.2787 | 59.8206 | 0.12643 | 0.005267 | -0.025735 | -0.020438 | 0.036265 | 0.076426 | -0.067295 | 59.6599 | 59.7 | 59.637 | 59.5584 | 62.2473 | 62.3078 | 62.0311 | 62.2508 | 0.15847 | 0.03731 | 0.006308 | 0.011605 | 0.068308 | 0.10847 | -0.035252 | 59.692 | 59.732 | 59.6691 | 59.5905 | 62.2793 | 62.3398 | 62.0632 | 62.2829 | -2.5874 | -2.3712 | -2.6103 | -2.3941
231.3281 | 122.2092 | -62.2925 | 59.8389 | 0.13101 | -0.00389 | -0.012 | -0.011281 | 0.036265 | 0.071848 | -0.058139 | 59.6599 | 59.6954 | 59.637 | 59.5538 | 62.2381 | 62.2987 | 62.0311 | 62.2463 | 0.16305 | 0.028153 | 0.020043 | 0.020762 | 0.068308 | 0.10389 | -0.026096 | 59.692 | 59.7275 | 59.6691 | 59.5859 | 62.2702 | 62.3307 | 62.0632 | 62.2783 | -2.5782 | -2.3712 | -2.6011 | -2.3941
233.0625 | 122.2687 | -62.2742 | 59.7839 | 0.12185 | -0.00389 | -0.016578 | -0.020438 | 0.049999 | 0.081005 | -0.067295 | 59.6599 | 59.7 | 59.6416 | 59.5538 | 62.2427 | 62.3032 | 62.0266 | 62.2463 | 0.15389 | 0.028153 | 0.015465 | 0.011605 | 0.082042 | 0.11305 | -0.035252 | 59.692 | 59.732 | 59.6737 | 59.5859 | 62.2748 | 62.3353 | 62.0586 | 62.2783 | -2.5828 | -2.3666 | -2.6011 | -2.3849
234.7969 | 122.2733 | -62.2696 | 59.8206 | 0.11727 | -0.00389 | -0.021157 | -0.01586 | 0.040843 | 0.067269 | -0.062717 | 59.6599 | 59.7 | 59.6325 | 59.5538 | 62.2473 | 62.3032 | 62.0357 | 62.2508 | 0.14932 | 0.028153 | 0.010886 | 0.016183 | 0.072886 | 0.099312 | -0.030674 | 59.692 | 59.732 | 59.6645 | 59.5859 | 62.2793 | 62.3353 | 62.0678 | 62.2829 | -2.5874 | -2.3758 | -2.6148 | -2.4033
236.5312 | 122.3282 | -62.2971 | 59.7382 | 0.12643 | -0.008469 | -0.016578 | -0.01586 | 0.045421 | 0.067269 | -0.058139 | 59.6599 | 59.6954 | 59.6416 | 59.5493 | 62.2427 | 62.3032 | 62.0311 | 62.2508 | 0.15847 | 0.023574 | 0.015465 | 0.016183 | 0.077464 | 0.099312 | -0.026096 | 59.692 | 59.7275 | 59.6737 | 59.5813 | 62.2748 | 62.3353 | 62.0632 | 62.2829 | -2.5828 | -2.3712 | -2.6011 | -2.3895
238.2188 | 122.2046 | -62.2925 | 59.7885 | 0.12185 | -0.00389 | -0.016578 | -0.011281 | 0.040843 | 0.071848 | -0.062717 | 59.6645 | 59.7 | 59.637 | 59.5584 | 62.2427 | 62.3032 | 62.0357 | 62.2554 | 0.15389 | 0.028153 | 0.015465 | 0.020762 | 0.072886 | 0.10389 | -0.030674 | 59.6965 | 59.732 | 59.6691 | 59.5905 | 62.2748 | 62.3353 | 62.0678 | 62.2874 | -2.5782 | -2.3712 | -2.6057 | -2.3987
239.9531 | 122.2366 | -62.2742 | 59.8206 | 0.12643 | 0.000689 | -0.012 | -0.01586 | 0.045421 | 0.076426 | -0.062717 | 59.6599 | 59.7 | 59.6416 | 59.5538 | 62.2427 | 62.3032 | 62.0311 | 62.2508 | 0.15847 | 0.032732 | 0.020043 | 0.016183 | 0.077464 | 0.10847 | -0.030674 | 59.692 | 59.732 | 59.6737 | 59.5859 | 62.2748 | 62.3353 | 62.0632 | 62.2829 | -2.5828 | -2.3712 | -2.6011 | -2.3895
241.7031 | 122.3419 | -62.265 | 59.7382 | 0.12185 | -0.008469 | -0.021157 | -0.025017 | 0.045421 | 0.076426 | -0.058139 | 59.6599 | 59.6954 | 59.6416 | 59.563 | 62.2381 | 62.3032 | 62.022 | 62.2508 | 0.15389 | 0.023574 | 0.010886 | 0.007026 | 0.077464 | 0.10847 | -0.026096 | 59.692 | 59.7275 | 59.6737 | 59.595 | 62.2702 | 62.3353 | 62.054 | 62.2829 | -2.5782 | -2.3621 | -2.5965 | -2.3804
243.3906 | 122.2046 | -62.3245 | 59.8022 | 0.12185 | 0.000689 | -0.016578 | -0.01586 | 0.036265 | 0.071848 | -0.067295 | 59.6691 | 59.7046 | 59.6462 | 59.5538 | 62.2427 | 62.2987 | 62.0357 | 62.2463 | 0.15389 | 0.032732 | 0.015465 | 0.016183 | 0.068308 | 0.10389 | -0.035252 | 59.7011 | 59.7366 | 59.6782 | 59.5859 | 62.2748 | 62.3307 | 62.0678 | 62.2783 | -2.5736 | -2.3666 | -2.5965 | -2.3895
245.1406 | 122.2366 | -62.2833 | 59.816 | 0.11727 | -0.008469 | -0.012 | -0.011281 | 0.036265 | 0.076426 | -0.058139 | 59.6645 | 59.7 | 59.6462 | 59.5584 | 62.2473 | 62.3032 | 62.0357 | 62.2463 | 0.14932 | 0.023574 | 0.020043 | 0.020762 | 0.068308 | 0.10847 | -0.026096 | 59.6965 | 59.732 | 59.6782 | 59.5905 | 62.2793 | 62.3353 | 62.0678 | 62.2783 | -2.5828 | -2.3712 | -2.6011 | -2.3895
246.8906 | 122.2504 | -62.2787 | 59.7839 | 0.13101 | 0.000689 | -0.007421 | -0.01586 | 0.040843 | 0.076426 | -0.062717 | 59.6645 | 59.6908 | 59.6416 | 59.563 | 62.2381 | 62.2987 | 62.0266 | 62.2463 | 0.16305 | 0.032732 | 0.024622 | 0.016183 | 0.072886 | 0.10847 | -0.030674 | 59.6965 | 59.7229 | 59.6737 | 59.595 | 62.2702 | 62.3307 | 62.0586 | 62.2783 | -2.5736 | -2.3621 | -2.5965 | -2.3849
248.6406 | 122.319 | -62.2742 | 59.7931 | 0.12643 | -0.013048 | -0.016578 | -0.01586 | 0.040843 | 0.076426 | -0.071874 | 59.6553 | 59.7092 | 59.637 | 59.5493 | 62.2381 | 62.3032 | 62.0449 | 62.2463 | 0.15847 | 0.018995 | 0.015465 | 0.016183 | 0.072886 | 0.10847 | -0.039831 | 59.6874 | 59.7412 | 59.6691 | 59.5813 | 62.2702 | 62.3353 | 62.0769 | 62.2783 | -2.5828 | -2.3895 | -2.6011 | -2.4078
250.3281 | 122.3373 | -62.265 | 59.7427 | 0.12185 | 0.000689 | -0.021157 | -0.020438 | 0.045421 | 0.071848 | -0.062717 | 59.6553 | 59.7 | 59.6462 | 59.5538 | 62.2473 | 62.3078 | 62.0357 | 62.2508 | 0.15389 | 0.032732 | 0.010886 | 0.011605 | 0.077464 | 0.10389 | -0.030674 | 59.6874 | 59.732 | 59.6782 | 59.5859 | 62.2793 | 62.3398 | 62.0678 | 62.2829 | -2.592 | -2.3804 | -2.6011 | -2.3895
252.0781 | 122.3648 | -62.2604 | 59.7656 | 0.11727 | 0.000689 | -0.021157 | -0.020438 | 0.040843 | 0.071848 | -0.062717 | 59.6553 | 59.7 | 59.637 | 59.5538 | 62.2336 | 62.2987 | 62.0403 | 62.2508 | 0.14932 | 0.032732 | 0.010886 | 0.011605 | 0.072886 | 0.10389 | -0.030674 | 59.6874 | 59.732 | 59.6691 | 59.5859 | 62.2656 | 62.3307 | 62.0723 | 62.2829 | -2.5782 | -2.385 | -2.5965 | -2.4033
253.7656 | 122.2229 | -62.3154 | 59.7839 | 0.12643 | -0.00389 | -0.016578 | -0.025017 | 0.040843 | 0.076426 | -0.067295 | 59.6553 | 59.7 | 59.6416 | 59.5538 | 62.2427 | 62.3032 | 62.0266 | 62.2508 | 0.15847 | 0.028153 | 0.015465 | 0.007026 | 0.072886 | 0.10847 | -0.035252 | 59.6874 | 59.732 | 59.6737 | 59.5859 | 62.2748 | 62.3353 | 62.0586 | 62.2829 | -2.5874 | -2.3712 | -2.6011 | -2.3849
255.5 | 122.3145 | -62.2971 | 59.7473 | 0.12185 | 0.000689 | -0.007421 | -0.020438 | 0.036265 | 0.076426 | -0.058139 | 59.6553 | 59.6954 | 59.6462 | 59.5493 | 62.2519 | 62.2987 | 62.0311 | 62.2417 | 0.15389 | 0.032732 | 0.024622 | 0.011605 | 0.068308 | 0.10847 | -0.026096 | 59.6874 | 59.7275 | 59.6782 | 59.5813 | 62.2839 | 62.3307 | 62.0632 | 62.2737 | -2.5965 | -2.3758 | -2.6057 | -2.3849
257.1719 | 122.3419 | -62.2559 | 59.7656 | 0.11727 | -0.008469 | -0.016578 | -0.011281 | 0.036265 | 0.071848 | -0.067295 | 59.6645 | 59.6908 | 59.6416 | 59.563 | 62.2427 | 62.3032 | 62.0311 | 62.2463 | 0.14932 | 0.023574 | 0.015465 | 0.020762 | 0.068308 | 0.10389 | -0.035252 | 59.6965 | 59.7229 | 59.6737 | 59.595 | 62.2748 | 62.3353 | 62.0632 | 62.2783 | -2.5782 | -2.3666 | -2.6011 | -2.3895
258.9062 | 122.2366 | -62.2879 | 59.8206 | 0.11269 | -0.00389 | -0.012 | -0.01586 | 0.049999 | 0.081005 | -0.062717 | 59.6691 | 59.6954 | 59.637 | 59.563 | 62.2473 | 62.3032 | 62.0403 | 62.2417 | 0.14474 | 0.028153 | 0.020043 | 0.016183 | 0.082042 | 0.11305 | -0.030674 | 59.7011 | 59.7275 | 59.6691 | 59.595 | 62.2793 | 62.3353 | 62.0723 | 62.2737 | -2.5782 | -2.3712 | -2.6103 | -2.4033
260.6562 | 122.3145 | -62.2787 | 59.7198 | 0.12185 | 0.000689 | -0.021157 | -0.020438 | 0.036265 | 0.076426 | -0.067295 | 59.6599 | 59.6954 | 59.637 | 59.563 | 62.2427 | 62.2941 | 62.0311 | 62.2463 | 0.15389 | 0.032732 | 0.010886 | 0.011605 | 0.068308 | 0.10847 | -0.035252 | 59.692 | 59.7275 | 59.6691 | 59.595 | 62.2748 | 62.3261 | 62.0632 | 62.2783 | -2.5828 | -2.3712 | -2.6057 | -2.3941
262.3438 | 122.2046 | -62.3154 | 59.7977 | 0.12185 | 0.000689 | -0.012 | -0.020438 | 0.040843 | 0.071848 | -0.058139 | 59.6599 | 59.7 | 59.6416 | 59.5584 | 62.2427 | 62.3032 | 62.0311 | 62.2463 | 0.15389 | 0.032732 | 0.020043 | 0.011605 | 0.072886 | 0.10389 | -0.026096 | 59.692 | 59.732 | 59.6737 | 59.5905 | 62.2748 | 62.3353 | 62.0632 | 62.2783 | -2.5828 | -2.3712 | -2.6011 | -2.3895
264.0312 | 122.3511 | -62.2787 | 59.7656 | 0.11269 | -0.00389 | -0.025735 | -0.020438 | 0.036265 | 0.076426 | -0.067295 | 59.6599 | 59.7046 | 59.6416 | 59.563 | 62.2427 | 62.3032 | 62.0357 | 62.2371 | 0.14474 | 0.028153 | 0.006308 | 0.011605 | 0.068308 | 0.10847 | -0.035252 | 59.692 | 59.7366 | 59.6737 | 59.595 | 62.2748 | 62.3353 | 62.0678 | 62.2691 | -2.5828 | -2.3758 | -2.6011 | -2.3941
265.7812 | 122.3373 | -62.2513 | 59.7656 | 0.11727 | -0.008469 | -0.016578 | -0.01586 | 0.040843 | 0.076426 | -0.067295 | 59.6553 | 59.6954 | 59.637 | 59.563 | 62.2427 | 62.2987 | 62.0266 | 62.2371 | 0.14932 | 0.023574 | 0.015465 | 0.016183 | 0.072886 | 0.10847 | -0.035252 | 59.6874 | 59.7275 | 59.6691 | 59.595 | 62.2748 | 62.3307 | 62.0586 | 62.2691 | -2.5874 | -2.3712 | -2.6057 | -2.3895
267.5312 | 122.2183 | -62.3062 | 59.7931 | 0.12185 | 0.000689 | -0.021157 | -0.01586 | 0.045421 | 0.071848 | -0.067295 | 59.6645 | 59.7 | 59.6416 | 59.563 | 62.2519 | 62.3078 | 62.022 | 62.2417 | 0.15389 | 0.032732 | 0.010886 | 0.016183 | 0.077464 | 0.10389 | -0.035252 | 59.6965 | 59.732 | 59.6737 | 59.595 | 62.2839 | 62.3398 | 62.054 | 62.2737 | -2.5874 | -2.3575 | -2.6103 | -2.3804
269.2188 | 122.2321 | -62.2787 | 59.8389 | 0.13101 | -0.00389 | -0.016578 | -0.01586 | 0.040843 | 0.071848 | -0.053561 | 59.6645 | 59.6954 | 59.6462 | 59.5538 | 62.2473 | 62.2987 | 62.0266 | 62.2463 | 0.16305 | 0.028153 | 0.015465 | 0.016183 | 0.072886 | 0.10389 | -0.021518 | 59.6965 | 59.7275 | 59.6782 | 59.5859 | 62.2793 | 62.3307 | 62.0586 | 62.2783 | -2.5828 | -2.3621 | -2.6011 | -2.3804
270.9531 | 122.3007 | -62.2787 | 59.7794 | 0.12185 | 0.000689 | -0.021157 | -0.01586 | 0.040843 | 0.071848 | -0.058139 | 59.6553 | 59.6954 | 59.6416 | 59.563 | 62.2473 | 62.2987 | 62.022 | 62.2417 | 0.15389 | 0.032732 | 0.010886 | 0.016183 | 0.072886 | 0.10389 | -0.026096 | 59.6874 | 59.7275 | 59.6737 | 59.595 | 62.2793 | 62.3307 | 62.054 | 62.2737 | -2.592 | -2.3666 | -2.6057 | -2.3804
272.7031 | 122.2412 | -62.2787 | 59.8297 | 0.11269 | 0.005267 | -0.021157 | -0.011281 | 0.045421 | 0.081005 | -0.067295 | 59.6645 | 59.7 | 59.6462 | 59.5584 | 62.2427 | 62.2987 | 62.0311 | 62.2463 | 0.14474 | 0.03731 | 0.010886 | 0.020762 | 0.077464 | 0.11305 | -0.035252 | 59.6965 | 59.732 | 59.6782 | 59.5905 | 62.2748 | 62.3307 | 62.0632 | 62.2783 | -2.5782 | -2.3666 | -2.5965 | -2.3849
274.4531 | 122.3099 | -62.2787 | 59.7382 | 0.11727 | -0.008469 | -0.016578 | -0.01586 | 0.036265 | 0.071848 | -0.062717 | 59.6645 | 59.7 | 59.6462 | 59.5538 | 62.2381 | 62.3078 | 62.0311 | 62.2417 | 0.14932 | 0.023574 | 0.015465 | 0.016183 | 0.068308 | 0.10389 | -0.030674 | 59.6965 | 59.732 | 59.6782 | 59.5859 | 62.2702 | 62.3398 | 62.0632 | 62.2737 | -2.5736 | -2.3666 | -2.5919 | -2.3849
276.1875 | 122.2504 | -62.3108 | 59.7473 | 0.12185 | -0.00389 | -0.016578 | -0.01586 | 0.040843 | 0.071848 | -0.062717 | 59.6691 | 59.7 | 59.6416 | 59.563 | 62.2427 | 62.2941 | 62.0266 | 62.2463 | 0.15389 | 0.028153 | 0.015465 | 0.016183 | 0.072886 | 0.10389 | -0.030674 | 59.7011 | 59.732 | 59.6737 | 59.595 | 62.2748 | 62.3261 | 62.0586 | 62.2783 | -2.5736 | -2.3575 | -2.6011 | -2.3849
277.875 | 122.2641 | -62.2925 | 59.7702 | 0.12643 | 0.005267 | -0.021157 | -0.01586 | 0.031687 | 0.071848 | -0.067295 | 59.6645 | 59.6954 | 59.6416 | 59.5584 | 62.2473 | 62.3032 | 62.022 | 62.2463 | 0.15847 | 0.03731 | 0.010886 | 0.016183 | 0.06373 | 0.10389 | -0.035252 | 59.6965 | 59.7275 | 59.6737 | 59.5905 | 62.2793 | 62.3353 | 62.054 | 62.2783 | -2.5828 | -2.3575 | -2.6057 | -2.3804
279.625 | 122.3602 | -62.2604 | 59.7382 | 0.12643 | 0.005267 | -0.021157 | -0.020438 | 0.049999 | 0.071848 | -0.058139 | 59.6599 | 59.7 | 59.6554 | 59.5722 | 62.2427 | 62.3124 | 62.0311 | 62.2463 | 0.15847 | 0.03731 | 0.010886 | 0.011605 | 0.082042 | 0.10389 | -0.026096 | 59.692 | 59.732 | 59.6874 | 59.6042 | 62.2748 | 62.3444 | 62.0632 | 62.2783 | -2.5828 | -2.3712 | -2.5874 | -2.3758
281.375 | 122.3785 | -62.2238 | 59.7748 | 0.12643 | -0.013048 | -0.021157 | -0.020438 | 0.040843 | 0.071848 | -0.062717 | 59.6599 | 59.7 | 59.6462 | 59.5538 | 62.2473 | 62.3032 | 62.0357 | 62.2463 | 0.15847 | 0.018995 | 0.010886 | 0.011605 | 0.072886 | 0.10389 | -0.030674 | 59.692 | 59.732 | 59.6782 | 59.5859 | 62.2793 | 62.3353 | 62.0678 | 62.2783 | -2.5874 | -2.3758 | -2.6011 | -2.3895
283.1094 | 122.3282 | -62.3062 | 59.7244 | 0.12185 | -0.008469 | -0.016578 | -0.020438 | 0.040843 | 0.071848 | -0.062717 | 59.6645 | 59.7046 | 59.637 | 59.563 | 62.2381 | 62.3032 | 62.0311 | 62.2417 | 0.15389 | 0.023574 | 0.015465 | 0.011605 | 0.072886 | 0.10389 | -0.030674 | 59.6965 | 59.7366 | 59.6691 | 59.595 | 62.2702 | 62.3353 | 62.0632 | 62.2737 | -2.5736 | -2.3666 | -2.6011 | -2.3941
284.8594 | 122.2458 | -62.3062 | 59.7977 | 0.12185 | -0.00389 | -0.016578 | -0.01586 | 0.049999 | 0.081005 | -0.062717 | 59.6645 | 59.7 | 59.6462 | 59.5584 | 62.2427 | 62.2941 | 62.0266 | 62.2417 | 0.15389 | 0.028153 | 0.015465 | 0.016183 | 0.082042 | 0.11305 | -0.030674 | 59.6965 | 59.732 | 59.6782 | 59.5905 | 62.2748 | 62.3261 | 62.0586 | 62.2737 | -2.5782 | -2.3621 | -2.5965 | -2.3804
286.5469 | 122.3099 | -62.2925 | 59.7336 | 0.11727 | -0.008469 | -0.016578 | -0.020438 | 0.031687 | 0.076426 | -0.067295 | 59.6691 | 59.7 | 59.6462 | 59.563 | 62.2427 | 62.2987 | 62.0311 | 62.2417 | 0.14932 | 0.023574 | 0.015465 | 0.011605 | 0.06373 | 0.10847 | -0.035252 | 59.7011 | 59.732 | 59.6782 | 59.595 | 62.2748 | 62.3307 | 62.0632 | 62.2737 | -2.5736 | -2.3621 | -2.5965 | -2.3849
288.2969 | 122.2778 | -62.265 | 59.7794 | 0.12185 | 0.000689 | -0.016578 | -0.01586 | 0.040843 | 0.076426 | -0.071874 | 59.6645 | 59.6954 | 59.6462 | 59.563 | 62.2427 | 62.2987 | 62.0311 | 62.2554 | 0.15389 | 0.032732 | 0.015465 | 0.016183 | 0.072886 | 0.10847 | -0.039831 | 59.6965 | 59.7275 | 59.6782 | 59.595 | 62.2748 | 62.3307 | 62.0632 | 62.2874 | -2.5782 | -2.3666 | -2.5965 | -2.3849
290.0625 | 122.3557 | -62.2787 | 59.7748 | 0.12185 | -0.008469 | -0.016578 | -0.01586 | 0.036265 | 0.071848 | -0.067295 | 59.6645 | 59.6954 | 59.6416 | 59.563 | 62.2473 | 62.3032 | 62.0357 | 62.2417 | 0.15389 | 0.023574 | 0.015465 | 0.016183 | 0.068308 | 0.10389 | -0.035252 | 59.6965 | 59.7275 | 59.6737 | 59.595 | 62.2793 | 62.3353 | 62.0678 | 62.2737 | -2.5828 | -2.3712 | -2.6057 | -2.3941
291.75 | 122.2137 | -62.2787 | 59.8434 | 0.12643 | -0.00389 | -0.016578 | -0.020438 | 0.040843 | 0.071848 | -0.067295 | 59.6691 | 59.6954 | 59.6462 | 59.563 | 62.2473 | 62.3032 | 62.0266 | 62.2417 | 0.15847 | 0.028153 | 0.015465 | 0.011605 | 0.072886 | 0.10389 | -0.035252 | 59.7011 | 59.7275 | 59.6782 | 59.595 | 62.2793 | 62.3353 | 62.0586 | 62.2737 | -2.5782 | -2.3575 | -2.6011 | -2.3804
293.5 | 122.2092 | -62.2879 | 59.8389 | 0.12185 | -0.008469 | -0.012 | -0.006703 | 0.045421 | 0.076426 | -0.058139 | 59.6691 | 59.6908 | 59.6508 | 59.5676 | 62.2427 | 62.2941 | 62.0311 | 62.2508 | 0.15389 | 0.023574 | 0.020043 | 0.02534 | 0.077464 | 0.10847 | -0.026096 | 59.7011 | 59.7229 | 59.6828 | 59.5996 | 62.2748 | 62.3261 | 62.0632 | 62.2829 | -2.5736 | -2.3621 | -2.5919 | -2.3804
295.25 | 122.3465 | -62.2787 | 59.761 | 0.11727 | -0.00389 | -0.012 | -0.025017 | 0.040843 | 0.081005 | -0.062717 | 59.6691 | 59.7 | 59.6508 | 59.563 | 62.2381 | 62.2987 | 62.0266 | 62.2463 | 0.14932 | 0.028153 | 0.020043 | 0.007026 | 0.072886 | 0.11305 | -0.030674 | 59.7011 | 59.732 | 59.6828 | 59.595 | 62.2702 | 62.3307 | 62.0586 | 62.2783 | -2.5691 | -2.3575 | -2.5874 | -2.3758
296.9219 | 122.2916 | -62.2879 | 59.7656 | 0.12643 | -0.00389 | -0.012 | -0.020438 | 0.045421 | 0.076426 | -0.062717 | 59.6691 | 59.6954 | 59.6462 | 59.563 | 62.2427 | 62.3032 | 62.0266 | 62.2417 | 0.15847 | 0.028153 | 0.020043 | 0.011605 | 0.077464 | 0.10847 | -0.030674 | 59.7011 | 59.7275 | 59.6782 | 59.595 | 62.2748 | 62.3353 | 62.0586 | 62.2737 | -2.5736 | -2.3575 | -2.5965 | -2.3804
298.6719 | 122.2183 | -62.2833 | 59.816 | 0.12185 | 0.005267 | -0.016578 | -0.025017 | 0.045421 | 0.067269 | -0.062717 | 59.6691 | 59.6908 | 59.6462 | 59.5584 | 62.2381 | 62.3032 | 62.0357 | 62.2417 | 0.15389 | 0.03731 | 0.015465 | 0.007026 | 0.077464 | 0.099312 | -0.030674 | 59.7011 | 59.7229 | 59.6782 | 59.5905 | 62.2702 | 62.3353 | 62.0678 | 62.2737 | -2.5691 | -2.3666 | -2.5919 | -2.3895
300.4062 | 122.3648 | -62.2742 | 59.7748 | 0.13101 | -0.00389 | -0.021157 | -0.020438 | 0.045421 | 0.071848 | -0.067295 | 59.6645 | 59.7 | 59.6462 | 59.563 | 62.2381 | 62.3124 | 62.0403 | 62.2463 | 0.16305 | 0.028153 | 0.010886 | 0.011605 | 0.077464 | 0.10389 | -0.035252 | 59.6965 | 59.732 | 59.6782 | 59.595 | 62.2702 | 62.3444 | 62.0723 | 62.2783 | -2.5736 | -2.3758 | -2.5919 | -2.3941
302.1406 | 122.3007 | -62.2833 | 59.7748 | 0.12643 | -0.013048 | -0.021157 | -0.01586 | 0.036265 | 0.076426 | -0.062717 | 59.6691 | 59.7046 | 59.6462 | 59.5584 | 62.2473 | 62.2987 | 62.0311 | 62.2417 | 0.15847 | 0.018995 | 0.010886 | 0.016183 | 0.068308 | 0.10847 | -0.030674 | 59.7011 | 59.7366 | 59.6782 | 59.5905 | 62.2793 | 62.3307 | 62.0632 | 62.2737 | -2.5782 | -2.3621 | -2.6011 | -2.3849
303.8281 | 122.3373 | -62.2787 | 59.7382 | 0.13101 | -0.008469 | -0.016578 | -0.01586 | 0.040843 | 0.076426 | -0.062717 | 59.6645 | 59.7 | 59.6416 | 59.5584 | 62.2519 | 62.2987 | 62.0266 | 62.2463 | 0.16305 | 0.023574 | 0.015465 | 0.016183 | 0.072886 | 0.10847 | -0.030674 | 59.6965 | 59.732 | 59.6737 | 59.5905 | 62.2839 | 62.3307 | 62.0586 | 62.2783 | -2.5874 | -2.3621 | -2.6103 | -2.3849
305.5781 | 122.2778 | -62.2879 | 59.7473 | 0.12185 | -0.008469 | -0.021157 | -0.020438 | 0.036265 | 0.067269 | -0.067295 | 59.6691 | 59.6954 | 59.637 | 59.5584 | 62.2473 | 62.2941 | 62.0266 | 62.2417 | 0.15389 | 0.023574 | 0.010886 | 0.011605 | 0.068308 | 0.099312 | -0.035252 | 59.7011 | 59.7275 | 59.6691 | 59.5905 | 62.2793 | 62.3261 | 62.0586 | 62.2737 | -2.5782 | -2.3575 | -2.6103 | -2.3895
307.2656 | 122.2641 | -62.2971 | 59.761 | 0.12185 | -0.013048 | -0.021157 | -0.011281 | 0.045421 | 0.081005 | -0.062717 | 59.6737 | 59.6954 | 59.6462 | 59.563 | 62.2473 | 62.3032 | 62.0311 | 62.2463 | 0.15389 | 0.018995 | 0.010886 | 0.020762 | 0.077464 | 0.11305 | -0.030674 | 59.7057 | 59.7275 | 59.6782 | 59.595 | 62.2793 | 62.3353 | 62.0632 | 62.2783 | -2.5736 | -2.3575 | -2.6011 | -2.3849
309 | 122.2687 | -62.2879 | 59.7748 | 0.12643 | -0.008469 | -0.012 | -0.020438 | 0.045421 | 0.071848 | -0.062717 | 59.6691 | 59.7 | 59.6462 | 59.5538 | 62.2473 | 62.3032 | 62.0311 | 62.2508 | 0.15847 | 0.023574 | 0.020043 | 0.011605 | 0.077464 | 0.10389 | -0.030674 | 59.7011 | 59.732 | 59.6782 | 59.5859 | 62.2793 | 62.3353 | 62.0632 | 62.2829 | -2.5782 | -2.3621 | -2.6011 | -2.3849
310.75 | 122.2366 | -62.2879 | 59.7977 | 0.12643 | -0.00389 | -0.021157 | -0.01586 | 0.040843 | 0.071848 | -0.067295 | 59.6645 | 59.6954 | 59.6554 | 59.5584 | 62.2427 | 62.2987 | 62.022 | 62.2417 | 0.15847 | 0.028153 | 0.010886 | 0.016183 | 0.072886 | 0.10389 | -0.035252 | 59.6965 | 59.7275 | 59.6874 | 59.5905 | 62.2748 | 62.3307 | 62.054 | 62.2737 | -2.5782 | -2.3575 | -2.5874 | -2.3666
312.5 | 122.3053 | -62.2925 | 59.761 | 0.11727 | -0.00389 | -0.016578 | -0.020438 | 0.040843 | 0.071848 | -0.062717 | 59.6691 | 59.7 | 59.6462 | 59.5584 | 62.2381 | 62.3032 | 62.0266 | 62.2463 | 0.14932 | 0.028153 | 0.015465 | 0.011605 | 0.072886 | 0.10389 | -0.030674 | 59.7011 | 59.732 | 59.6782 | 59.5905 | 62.2702 | 62.3353 | 62.0586 | 62.2783 | -2.5691 | -2.3575 | -2.5919 | -2.3804
314.1875 | 122.3465 | -62.2925 | 59.7519 | 0.11727 | -0.008469 | -0.021157 | -0.01586 | 0.045421 | 0.076426 | -0.058139 | 59.6645 | 59.7 | 59.6416 | 59.5538 | 62.2336 | 62.3032 | 62.022 | 62.2417 | 0.14932 | 0.023574 | 0.010886 | 0.016183 | 0.077464 | 0.10847 | -0.026096 | 59.6965 | 59.732 | 59.6737 | 59.5859 | 62.2656 | 62.3353 | 62.054 | 62.2737 | -2.5691 | -2.3575 | -2.5919 | -2.3804
315.9219 | 122.2046 | -62.2833 | 59.816 | 0.12643 | -0.00389 | -0.021157 | -0.01586 | 0.049999 | 0.076426 | -0.058139 | 59.6737 | 59.7046 | 59.6416 | 59.5538 | 62.2427 | 62.3032 | 62.022 | 62.2463 | 0.15847 | 0.028153 | 0.010886 | 0.016183 | 0.082042 | 0.10847 | -0.026096 | 59.7057 | 59.7366 | 59.6737 | 59.5859 | 62.2748 | 62.3353 | 62.054 | 62.2783 | -2.5691 | -2.3483 | -2.6011 | -2.3804
317.5938 | 122.319 | -62.2971 | 59.729 | 0.12185 | -0.008469 | -0.021157 | -0.020438 | 0.045421 | 0.067269 | -0.062717 | 59.6691 | 59.7 | 59.6462 | 59.5676 | 62.2427 | 62.2987 | 62.022 | 62.2463 | 0.15389 | 0.023574 | 0.010886 | 0.011605 | 0.077464 | 0.099312 | -0.030674 | 59.7011 | 59.732 | 59.6782 | 59.5996 | 62.2748 | 62.3307 | 62.054 | 62.2783 | -2.5736 | -2.3529 | -2.5965 | -2.3758
319.2812 | 122.3053 | -62.2925 | 59.7519 | 0.12643 | -0.00389 | -0.016578 | -0.020438 | 0.045421 | 0.071848 | -0.062717 | 59.6645 | 59.6954 | 59.6462 | 59.5538 | 62.2381 | 62.3032 | 62.0311 | 62.2463 | 0.15847 | 0.028153 | 0.015465 | 0.011605 | 0.077464 | 0.10389 | -0.030674 | 59.6965 | 59.7275 | 59.6782 | 59.5859 | 62.2702 | 62.3353 | 62.0632 | 62.2783 | -2.5736 | -2.3666 | -2.5919 | -2.3849
321 | 122.2687 | -62.2696 | 59.8114 | 0.12185 | -0.008469 | -0.021157 | -0.01586 | 0.040843 | 0.067269 | -0.062717 | 59.6645 | 59.7 | 59.6462 | 59.5584 | 62.2473 | 62.3078 | 62.0311 | 62.2463 | 0.15389 | 0.023574 | 0.010886 | 0.016183 | 0.072886 | 0.099312 | -0.030674 | 59.6965 | 59.732 | 59.6782 | 59.5905 | 62.2793 | 62.3398 | 62.0632 | 62.2783 | -2.5828 | -2.3666 | -2.6011 | -2.3849
322.75 | 122.287 | -62.2787 | 59.7565 | 0.12643 | -0.013048 | -0.016578 | -0.020438 | 0.040843 | 0.081005 | -0.062717 | 59.6599 | 59.7 | 59.637 | 59.5584 | 62.2427 | 62.2987 | 62.0311 | 62.2371 | 0.15847 | 0.018995 | 0.015465 | 0.011605 | 0.072886 | 0.11305 | -0.030674 | 59.692 | 59.732 | 59.6691 | 59.5905 | 62.2748 | 62.3307 | 62.0632 | 62.2691 | -2.5828 | -2.3712 | -2.6057 | -2.3941
324.4844 | 122.374 | -62.2559 | 59.7931 | 0.11269 | -0.008469 | -0.025735 | -0.020438 | 0.040843 | 0.062691 | -0.062717 | 59.6737 | 59.7 | 59.6462 | 59.5538 | 62.2427 | 62.2987 | 62.0357 | 62.2417 | 0.14474 | 0.023574 | 0.006308 | 0.011605 | 0.072886 | 0.094734 | -0.030674 | 59.7057 | 59.732 | 59.6782 | 59.5859 | 62.2748 | 62.3307 | 62.0678 | 62.2737 | -2.5691 | -2.3621 | -2.5965 | -2.3895
326.2188 | 122.3602 | -62.2467 | 59.7839 | 0.11269 | -0.008469 | -0.021157 | -0.020438 | 0.040843 | 0.076426 | -0.067295 | 59.6691 | 59.7 | 59.6462 | 59.563 | 62.2381 | 62.2987 | 62.0266 | 62.2508 | 0.14474 | 0.023574 | 0.010886 | 0.011605 | 0.072886 | 0.10847 | -0.035252 | 59.7011 | 59.732 | 59.6782 | 59.595 | 62.2702 | 62.3307 | 62.0586 | 62.2829 | -2.5691 | -2.3575 | -2.5919 | -2.3804
327.9531 | 122.319 | -62.2879 | 59.7382 | 0.11727 | -0.013048 | -0.016578 | -0.020438 | 0.040843 | 0.071848 | -0.062717 | 59.6691 | 59.7 | 59.6462 | 59.563 | 62.2473 | 62.2987 | 62.0266 | 62.2417 | 0.14932 | 0.018995 | 0.015465 | 0.011605 | 0.072886 | 0.10389 | -0.030674 | 59.7011 | 59.732 | 59.6782 | 59.595 | 62.2793 | 62.3307 | 62.0586 | 62.2737 | -2.5782 | -2.3575 | -2.6011 | -2.3804
329.6406 | 122.2183 | -62.3016 | 59.7977 | 0.12185 | -0.013048 | -0.012 | -0.011281 | 0.049999 | 0.071848 | -0.062717 | 59.6691 | 59.6954 | 59.6462 | 59.563 | 62.2336 | 62.3078 | 62.0266 | 62.2417 | 0.15389 | 0.018995 | 0.020043 | 0.020762 | 0.082042 | 0.10389 | -0.030674 | 59.7011 | 59.7275 | 59.6782 | 59.595 | 62.2656 | 62.3398 | 62.0586 | 62.2737 | -2.5645 | -2.3575 | -2.5874 | -2.3804
331.375 | 122.1954 | -62.2833 | 59.8068 | 0.12643 | -0.008469 | -0.021157 | -0.011281 | 0.045421 | 0.081005 | -0.062717 | 59.6691 | 59.7 | 59.6508 | 59.5584 | 62.2427 | 62.3032 | 62.0311 | 62.2463 | 0.15847 | 0.023574 | 0.010886 | 0.020762 | 0.077464 | 0.11305 | -0.030674 | 59.7011 | 59.732 | 59.6828 | 59.5905 | 62.2748 | 62.3353 | 62.0632 | 62.2783 | -2.5736 | -2.3621 | -2.5919 | -2.3804
333.0469 | 122.287 | -62.2604 | 59.7794 | 0.12185 | -0.00389 | -0.016578 | -0.01586 | 0.031687 | 0.071848 | -0.067295 | 59.6691 | 59.7046 | 59.6416 | 59.5584 | 62.2473 | 62.3032 | 62.0266 | 62.2463 | 0.15389 | 0.028153 | 0.015465 | 0.016183 | 0.06373 | 0.10389 | -0.035252 | 59.7011 | 59.7366 | 59.6737 | 59.5905 | 62.2793 | 62.3353 | 62.0586 | 62.2783 | -2.5782 | -2.3575 | -2.6057 | -2.3849
334.8125 | 122.2961 | -62.2879 | 59.7702 | 0.12185 | -0.013048 | -0.021157 | -0.025017 | 0.040843 | 0.071848 | -0.062717 | 59.6737 | 59.7 | 59.6462 | 59.563 | 62.2473 | 62.3032 | 62.022 | 62.2417 | 0.15389 | 0.018995 | 0.010886 | 0.007026 | 0.072886 | 0.10389 | -0.030674 | 59.7057 | 59.732 | 59.6782 | 59.595 | 62.2793 | 62.3353 | 62.054 | 62.2737 | -2.5736 | -2.3483 | -2.6011 | -2.3758
336.4844 | 122.1954 | -62.2833 | 59.8251 | 0.12643 | -0.013048 | -0.025735 | -0.01586 | 0.036265 | 0.067269 | -0.058139 | 59.6691 | 59.7092 | 59.6416 | 59.5676 | 62.2473 | 62.3078 | 62.0311 | 62.2463 | 0.15847 | 0.018995 | 0.006308 | 0.016183 | 0.068308 | 0.099312 | -0.026096 | 59.7011 | 59.7412 | 59.6737 | 59.5996 | 62.2793 | 62.3398 | 62.0632 | 62.2783 | -2.5782 | -2.3621 | -2.6057 | -2.3895
338.1719 | 122.2092 | -62.3108 | 59.7839 | 0.13101 | -0.00389 | -0.021157 | -0.020438 | 0.045421 | 0.076426 | -0.067295 | 59.6691 | 59.7046 | 59.6462 | 59.563 | 62.2473 | 62.3032 | 62.022 | 62.2417 | 0.16305 | 0.028153 | 0.010886 | 0.011605 | 0.077464 | 0.10847 | -0.035252 | 59.7011 | 59.7366 | 59.6782 | 59.595 | 62.2793 | 62.3353 | 62.054 | 62.2737 | -2.5782 | -2.3529 | -2.6011 | -2.3758
339.9219 | 122.3236 | -62.2742 | 59.7153 | 0.12185 | -0.00389 | -0.021157 | -0.01586 | 0.040843 | 0.071848 | -0.067295 | 59.6737 | 59.7 | 59.6416 | 59.563 | 62.2473 | 62.3032 | 62.0311 | 62.2463 | 0.15389 | 0.028153 | 0.010886 | 0.016183 | 0.072886 | 0.10389 | -0.035252 | 59.7057 | 59.732 | 59.6737 | 59.595 | 62.2793 | 62.3353 | 62.0632 | 62.2783 | -2.5736 | -2.3575 | -2.6057 | -2.3895
341.6719 | 122.2229 | -62.2742 | 59.7885 | 0.11727 | -0.008469 | -0.016578 | -0.020438 | 0.045421 | 0.076426 | -0.062717 | 59.6691 | 59.7 | 59.6416 | 59.5676 | 62.2473 | 62.3078 | 62.0311 | 62.2371 | 0.14932 | 0.023574 | 0.015465 | 0.011605 | 0.077464 | 0.10847 | -0.030674 | 59.7011 | 59.732 | 59.6737 | 59.5996 | 62.2793 | 62.3398 | 62.0632 | 62.2691 | -2.5782 | -2.3621 | -2.6057 | -2.3895
343.4062 | 122.2183 | -62.3062 | 59.7931 | 0.12643 | -0.008469 | -0.021157 | -0.01586 | 0.036265 | 0.081005 | -0.062717 | 59.6737 | 59.6954 | 59.6554 | 59.5584 | 62.2473 | 62.3078 | 62.0357 | 62.2417 | 0.15847 | 0.023574 | 0.010886 | 0.016183 | 0.068308 | 0.11305 | -0.030674 | 59.7057 | 59.7275 | 59.6874 | 59.5905 | 62.2793 | 62.3398 | 62.0678 | 62.2737 | -2.5736 | -2.3621 | -2.5919 | -2.3804
345.1562 | 122.2 | -62.3108 | 59.816 | 0.11727 | -0.00389 | -0.016578 | -0.025017 | 0.040843 | 0.071848 | -0.071874 | 59.6645 | 59.7 | 59.6508 | 59.5584 | 62.2473 | 62.3124 | 62.0311 | 62.2417 | 0.14932 | 0.028153 | 0.015465 | 0.007026 | 0.072886 | 0.10389 | -0.039831 | 59.6965 | 59.732 | 59.6828 | 59.5905 | 62.2793 | 62.3444 | 62.0632 | 62.2737 | -2.5828 | -2.3666 | -2.5965 | -2.3804
346.8438 | 122.3328 | -62.2742 | 59.7244 | 0.11727 | -0.013048 | -0.021157 | -0.020438 | 0.036265 | 0.076426 | -0.062717 | 59.6645 | 59.7092 | 59.6416 | 59.563 | 62.2473 | 62.3078 | 62.0266 | 62.2463 | 0.14932 | 0.018995 | 0.010886 | 0.011605 | 0.068308 | 0.10847 | -0.030674 | 59.6965 | 59.7412 | 59.6737 | 59.595 | 62.2793 | 62.3398 | 62.0586 | 62.2783 | -2.5828 | -2.3621 | -2.6057 | -2.3849
348.5781 | 122.3419 | -62.2833 | 59.7473 | 0.11727 | -0.008469 | -0.012 | -0.01586 | 0.049999 | 0.067269 | -0.058139 | 59.6737 | 59.7 | 59.6462 | 59.5584 | 62.2473 | 62.3078 | 62.0311 | 62.2508 | 0.14932 | 0.023574 | 0.020043 | 0.016183 | 0.082042 | 0.099312 | -0.026096 | 59.7057 | 59.732 | 59.6782 | 59.5905 | 62.2793 | 62.3398 | 62.0632 | 62.2829 | -2.5736 | -2.3575 | -2.6011 | -2.3849
350.3281 | 122.3099 | -62.2559 | 59.7794 | 0.11727 | -0.008469 | -0.025735 | -0.020438 | 0.040843 | 0.067269 | -0.058139 | 59.6691 | 59.7 | 59.6416 | 59.563 | 62.2381 | 62.3032 | 62.022 | 62.2463 | 0.14932 | 0.023574 | 0.006308 | 0.011605 | 0.072886 | 0.099312 | -0.026096 | 59.7011 | 59.732 | 59.6737 | 59.595 | 62.2702 | 62.3353 | 62.054 | 62.2783 | -2.5691 | -2.3529 | -2.5965 | -2.3804
352.0781 | 122.3145 | -62.2833 | 59.7244 | 0.12185 | -0.008469 | -0.016578 | -0.020438 | 0.045421 | 0.081005 | -0.062717 | 59.6691 | 59.7046 | 59.6462 | 59.563 | 62.2427 | 62.3032 | 62.0266 | 62.2417 | 0.15389 | 0.023574 | 0.015465 | 0.011605 | 0.077464 | 0.11305 | -0.030674 | 59.7011 | 59.7366 | 59.6782 | 59.595 | 62.2748 | 62.3353 | 62.0586 | 62.2737 | -2.5736 | -2.3575 | -2.5965 | -2.3804
353.7656 | 122.2183 | -62.265 | 59.8297 | 0.12643 | -0.008469 | -0.016578 | -0.01586 | 0.040843 | 0.076426 | -0.058139 | 59.6691 | 59.6954 | 59.6554 | 59.5584 | 62.2473 | 62.3032 | 62.0266 | 62.2417 | 0.15847 | 0.023574 | 0.015465 | 0.016183 | 0.072886 | 0.10847 | -0.026096 | 59.7011 | 59.7275 | 59.6874 | 59.5905 | 62.2793 | 62.3353 | 62.0586 | 62.2737 | -2.5782 | -2.3575 | -2.5919 | -2.3712
355.5156 | 122.3465 | -62.2421 | 59.7748 | 0.12185 | -0.013048 | -0.012 | -0.025017 | 0.036265 | 0.071848 | -0.067295 | 59.6691 | 59.7046 | 59.6462 | 59.563 | 62.2427 | 62.3078 | 62.0266 | 62.2417 | 0.15389 | 0.018995 | 0.020043 | 0.007026 | 0.068308 | 0.10389 | -0.035252 | 59.7011 | 59.7366 | 59.6782 | 59.595 | 62.2748 | 62.3398 | 62.0586 | 62.2737 | -2.5736 | -2.3575 | -2.5965 | -2.3804
357.2031 | 122.2504 | -62.2787 | 59.8434 | 0.12185 | -0.008469 | -0.012 | -0.01586 | 0.049999 | 0.081005 | -0.058139 | 59.6691 | 59.7 | 59.6462 | 59.5584 | 62.2473 | 62.3032 | 62.022 | 62.2508 | 0.15389 | 0.023574 | 0.020043 | 0.016183 | 0.082042 | 0.11305 | -0.026096 | 59.7011 | 59.732 | 59.6782 | 59.5905 | 62.2793 | 62.3353 | 62.054 | 62.2829 | -2.5782 | -2.3529 | -2.6011 | -2.3758
358.9375 | 122.2046 | -62.265 | 59.8297 | 0.12643 | -0.00389 | -0.012 | -0.011281 | 0.040843 | 0.081005 | -0.062717 | 59.6691 | 59.7 | 59.6508 | 59.5538 | 62.2381 | 62.3078 | 62.0311 | 62.2417 | 0.15847 | 0.028153 | 0.020043 | 0.020762 | 0.072886 | 0.11305 | -0.030674 | 59.7011 | 59.732 | 59.6828 | 59.5859 | 62.2702 | 62.3398 | 62.0632 | 62.2737 | -2.5691 | -2.3621 | -2.5874 | -2.3804
360.6875 | 122.3007 | -62.2696 | 59.7565 | 0.11727 | -0.013048 | -0.016578 | -0.01586 | 0.040843 | 0.076426 | -0.058139 | 59.6645 | 59.7 | 59.6508 | 59.563 | 62.2427 | 62.3032 | 62.0357 | 62.2463 | 0.14932 | 0.018995 | 0.015465 | 0.016183 | 0.072886 | 0.10847 | -0.026096 | 59.6965 | 59.732 | 59.6828 | 59.595 | 62.2748 | 62.3353 | 62.0678 | 62.2783 | -2.5782 | -2.3712 | -2.5919 | -2.3849
362.3594 | 122.2137 | -62.3199 | 59.7885 | 0.12185 | -0.008469 | -0.016578 | -0.011281 | 0.045421 | 0.067269 | -0.067295 | 59.6737 | 59.7046 | 59.6508 | 59.5676 | 62.2427 | 62.3078 | 62.0266 | 62.2417 | 0.15389 | 0.023574 | 0.015465 | 0.020762 | 0.077464 | 0.099312 | -0.035252 | 59.7057 | 59.7366 | 59.6828 | 59.5996 | 62.2748 | 62.3398 | 62.0586 | 62.2737 | -2.5691 | -2.3529 | -2.5919 | -2.3758
364.1094 | 122.2 | -62.3016 | 59.816 | 0.12643 | -0.008469 | -0.012 | -0.020438 | 0.045421 | 0.071848 | -0.062717 | 59.6645 | 59.7046 | 59.6508 | 59.563 | 62.2427 | 62.3078 | 62.0266 | 62.2463 | 0.15847 | 0.023574 | 0.020043 | 0.011605 | 0.077464 | 0.10389 | -0.030674 | 59.6965 | 59.7366 | 59.6828 | 59.595 | 62.2748 | 62.3398 | 62.0586 | 62.2783 | -2.5782 | -2.3621 | -2.5919 | -2.3758
365.7969 | 122.2595 | -62.2879 | 59.8022 | 0.12185 | -0.013048 | -0.012 | -0.011281 | 0.049999 | 0.076426 | -0.058139 | 59.6691 | 59.7046 | 59.6645 | 59.563 | 62.2427 | 62.3078 | 62.0174 | 62.2463 | 0.15389 | 0.018995 | 0.020043 | 0.020762 | 0.082042 | 0.10847 | -0.026096 | 59.7011 | 59.7366 | 59.6966 | 59.595 | 62.2748 | 62.3398 | 62.0494 | 62.2783 | -2.5736 | -2.3483 | -2.5782 | -2.3529
367.5312 | 122.2046 | -62.2971 | 59.8068 | 0.12185 | -0.008469 | -0.021157 | -0.01586 | 0.045421 | 0.071848 | -0.053561 | 59.6691 | 59.7046 | 59.6508 | 59.563 | 62.2473 | 62.3124 | 62.022 | 62.2463 | 0.15389 | 0.023574 | 0.010886 | 0.016183 | 0.077464 | 0.10389 | -0.021518 | 59.7011 | 59.7366 | 59.6828 | 59.595 | 62.2793 | 62.3444 | 62.054 | 62.2783 | -2.5782 | -2.3529 | -2.5965 | -2.3712
369.2656 | 122.2137 | -62.2787 | 59.816 | 0.12185 | -0.00389 | -0.007421 | -0.01586 | 0.036265 | 0.071848 | -0.058139 | 59.6645 | 59.7 | 59.6508 | 59.563 | 62.2427 | 62.3078 | 62.0311 | 62.2463 | 0.15389 | 0.028153 | 0.024622 | 0.016183 | 0.068308 | 0.10389 | -0.026096 | 59.6965 | 59.732 | 59.6828 | 59.595 | 62.2748 | 62.3398 | 62.0632 | 62.2783 | -2.5782 | -2.3666 | -2.5919 | -2.3804
371 | 122.3328 | -62.2879 | 59.7473 | 0.11727 | -0.008469 | -0.021157 | -0.01586 | 0.045421 | 0.067269 | -0.058139 | 59.6691 | 59.7046 | 59.6508 | 59.563 | 62.2427 | 62.3078 | 62.022 | 62.2508 | 0.14932 | 0.023574 | 0.010886 | 0.016183 | 0.077464 | 0.099312 | -0.026096 | 59.7011 | 59.7366 | 59.6828 | 59.595 | 62.2748 | 62.3398 | 62.054 | 62.2829 | -2.5736 | -2.3529 | -2.5919 | -2.3712
372.6875 | 122.2275 | -62.2879 | 59.8297 | 0.12185 | -0.013048 | -0.016578 | -0.025017 | 0.040843 | 0.081005 | -0.058139 | 59.6691 | 59.7 | 59.6462 | 59.5584 | 62.2381 | 62.3078 | 62.0266 | 62.2371 | 0.15389 | 0.018995 | 0.015465 | 0.007026 | 0.072886 | 0.11305 | -0.026096 | 59.7011 | 59.732 | 59.6782 | 59.5905 | 62.2702 | 62.3398 | 62.0586 | 62.2691 | -2.5691 | -2.3575 | -2.5919 | -2.3804
374.4375 | 122.2412 | -62.2925 | 59.7748 | 0.11727 | -0.00389 | -0.016578 | -0.011281 | 0.040843 | 0.076426 | -0.062717 | 59.6737 | 59.7 | 59.6508 | 59.5676 | 62.2427 | 62.2987 | 62.0311 | 62.2508 | 0.14932 | 0.028153 | 0.015465 | 0.020762 | 0.072886 | 0.10847 | -0.030674 | 59.7057 | 59.732 | 59.6828 | 59.5996 | 62.2748 | 62.3307 | 62.0632 | 62.2829 | -2.5691 | -2.3575 | -2.5919 | -2.3804
376.1875 | 122.287 | -62.2971 | 59.7519 | 0.12185 | -0.008469 | -0.021157 | -0.011281 | 0.045421 | 0.076426 | -0.062717 | 59.6737 | 59.7046 | 59.6462 | 59.563 | 62.2427 | 62.3032 | 62.022 | 62.2463 | 0.15389 | 0.023574 | 0.010886 | 0.020762 | 0.077464 | 0.10847 | -0.030674 | 59.7057 | 59.7366 | 59.6782 | 59.595 | 62.2748 | 62.3353 | 62.054 | 62.2783 | -2.5691 | -2.3483 | -2.5965 | -2.3758
377.8594 | 122.3053 | -62.2833 | 59.761 | 0.12185 | -0.017627 | -0.021157 | -0.020438 | 0.045421 | 0.071848 | -0.062717 | 59.6737 | 59.7046 | 59.6462 | 59.5538 | 62.2473 | 62.3032 | 62.0311 | 62.2463 | 0.15389 | 0.014416 | 0.010886 | 0.011605 | 0.077464 | 0.10389 | -0.030674 | 59.7057 | 59.7366 | 59.6782 | 59.5859 | 62.2793 | 62.3353 | 62.0632 | 62.2783 | -2.5736 | -2.3575 | -2.6011 | -2.3849
379.6094 | 122.2229 | -62.2833 | 59.8297 | 0.12185 | 0.000689 | -0.021157 | -0.020438 | 0.040843 | 0.071848 | -0.062717 | 59.6737 | 59.6954 | 59.6462 | 59.563 | 62.2427 | 62.3124 | 62.0266 | 62.2463 | 0.15389 | 0.032732 | 0.010886 | 0.011605 | 0.072886 | 0.10389 | -0.030674 | 59.7057 | 59.7275 | 59.6782 | 59.595 | 62.2748 | 62.3444 | 62.0586 | 62.2783 | -2.5691 | -2.3529 | -2.5965 | -2.3804
381.3594 | 122.2961 | -62.2833 | 59.7473 | 0.11727 | -0.008469 | -0.016578 | -0.01586 | 0.045421 | 0.071848 | -0.062717 | 59.6737 | 59.7 | 59.6554 | 59.563 | 62.2381 | 62.3032 | 62.0266 | 62.2463 | 0.14932 | 0.023574 | 0.015465 | 0.016183 | 0.077464 | 0.10389 | -0.030674 | 59.7057 | 59.732 | 59.6874 | 59.595 | 62.2702 | 62.3353 | 62.0586 | 62.2783 | -2.5645 | -2.3529 | -2.5828 | -2.3712
383.1094 | 122.2046 | -62.3062 | 59.8022 | 0.12185 | -0.008469 | -0.016578 | -0.006703 | 0.040843 | 0.076426 | -0.058139 | 59.6782 | 59.7046 | 59.6462 | 59.5538 | 62.2473 | 62.3032 | 62.0311 | 62.2508 | 0.15389 | 0.023574 | 0.015465 | 0.02534 | 0.072886 | 0.10847 | -0.026096 | 59.7103 | 59.7366 | 59.6782 | 59.5859 | 62.2793 | 62.3353 | 62.0632 | 62.2829 | -2.5691 | -2.3529 | -2.6011 | -2.3849
384.8125 | 122.3282 | -62.2604 | 59.7748 | 0.12185 | -0.008469 | -0.016578 | -0.020438 | 0.045421 | 0.071848 | -0.062717 | 59.6691 | 59.7 | 59.6462 | 59.563 | 62.2473 | 62.3078 | 62.0266 | 62.2463 | 0.15389 | 0.023574 | 0.015465 | 0.011605 | 0.077464 | 0.10389 | -0.030674 | 59.7011 | 59.732 | 59.6782 | 59.595 | 62.2793 | 62.3398 | 62.0586 | 62.2783 | -2.5782 | -2.3575 | -2.6011 | -2.3804
386.5625 | 122.2916 | -62.2742 | 59.7656 | 0.12185 | -0.013048 | -0.025735 | -0.01586 | 0.040843 | 0.076426 | -0.067295 | 59.6782 | 59.7046 | 59.6508 | 59.563 | 62.2473 | 62.3078 | 62.022 | 62.2463 | 0.15389 | 0.018995 | 0.006308 | 0.016183 | 0.072886 | 0.10847 | -0.035252 | 59.7103 | 59.7366 | 59.6828 | 59.595 | 62.2793 | 62.3398 | 62.054 | 62.2783 | -2.5691 | -2.3438 | -2.5965 | -2.3712
388.3125 | 122.3969 | -62.2787 | 59.761 | 0.12185 | -0.013048 | -0.025735 | -0.025017 | 0.045421 | 0.071848 | -0.062717 | 59.6737 | 59.7046 | 59.6599 | 59.5584 | 62.2473 | 62.3078 | 62.0311 | 62.2463 | 0.15389 | 0.018995 | 0.006308 | 0.007026 | 0.077464 | 0.10389 | -0.030674 | 59.7057 | 59.7366 | 59.692 | 59.5905 | 62.2793 | 62.3398 | 62.0632 | 62.2783 | -2.5736 | -2.3575 | -2.5874 | -2.3712
390.0625 | 122.2229 | -62.2787 | 59.816 | 0.12643 | -0.008469 | -0.007421 | -0.020438 | 0.049999 | 0.081005 | -0.062717 | 59.6737 | 59.6908 | 59.6508 | 59.5584 | 62.2427 | 62.3078 | 62.0266 | 62.2417 | 0.15847 | 0.023574 | 0.024622 | 0.011605 | 0.082042 | 0.11305 | -0.030674 | 59.7057 | 59.7229 | 59.6828 | 59.5905 | 62.2748 | 62.3398 | 62.0586 | 62.2737 | -2.5691 | -2.3529 | -2.5919 | -2.3758
391.7344 | 122.3053 | -62.2787 | 59.7656 | 0.12185 | -0.00389 | -0.025735 | -0.01586 | 0.040843 | 0.062691 | -0.058139 | 59.6737 | 59.7046 | 59.6508 | 59.5538 | 62.2473 | 62.3124 | 62.0311 | 62.2508 | 0.15389 | 0.028153 | 0.006308 | 0.016183 | 0.072886 | 0.094734 | -0.026096 | 59.7057 | 59.7366 | 59.6828 | 59.5859 | 62.2793 | 62.3444 | 62.0632 | 62.2829 | -2.5736 | -2.3575 | -2.5965 | -2.3804
393.4688 | 122.3282 | -62.2742 | 59.7656 | 0.10812 | -0.013048 | -0.016578 | -0.020438 | 0.049999 | 0.076426 | -0.062717 | 59.6737 | 59.7 | 59.6554 | 59.5584 | 62.2427 | 62.3078 | 62.0266 | 62.2463 | 0.14016 | 0.018995 | 0.015465 | 0.011605 | 0.082042 | 0.10847 | -0.030674 | 59.7057 | 59.732 | 59.6874 | 59.5905 | 62.2748 | 62.3398 | 62.0586 | 62.2783 | -2.5691 | -2.3529 | -2.5874 | -2.3712
395.1562 | 122.2687 | -62.2742 | 59.7977 | 0.11727 | -0.00389 | -0.016578 | -0.01586 | 0.040843 | 0.071848 | -0.053561 | 59.6645 | 59.7 | 59.6554 | 59.563 | 62.2427 | 62.3078 | 62.0311 | 62.2463 | 0.14932 | 0.028153 | 0.015465 | 0.016183 | 0.072886 | 0.10389 | -0.021518 | 59.6965 | 59.732 | 59.6874 | 59.595 | 62.2748 | 62.3398 | 62.0632 | 62.2783 | -2.5782 | -2.3666 | -2.5874 | -2.3758
396.8906 | 122.2092 | -62.2833 | 59.8251 | 0.12185 | -0.008469 | -0.012 | -0.011281 | 0.045421 | 0.081005 | -0.053561 | 59.6782 | 59.7046 | 59.6554 | 59.563 | 62.2427 | 62.3078 | 62.0311 | 62.2463 | 0.15389 | 0.023574 | 0.020043 | 0.020762 | 0.077464 | 0.11305 | -0.021518 | 59.7103 | 59.7366 | 59.6874 | 59.595 | 62.2748 | 62.3398 | 62.0632 | 62.2783 | -2.5645 | -2.3529 | -2.5874 | -2.3758
398.625 | 122.2275 | -62.2833 | 59.8343 | 0.12185 | -0.008469 | -0.016578 | -0.020438 | 0.045421 | 0.076426 | -0.062717 | 59.6691 | 59.7 | 59.6462 | 59.563 | 62.2473 | 62.3078 | 62.0266 | 62.2463 | 0.15389 | 0.023574 | 0.015465 | 0.011605 | 0.077464 | 0.10847 | -0.030674 | 59.7011 | 59.732 | 59.6782 | 59.595 | 62.2793 | 62.3398 | 62.0586 | 62.2783 | -2.5782 | -2.3575 | -2.6011 | -2.3804
400.3281 | 122.3419 | -62.265 | 59.7839 | 0.12643 | -0.008469 | -0.025735 | -0.01586 | 0.036265 | 0.062691 | -0.067295 | 59.6645 | 59.7046 | 59.6599 | 59.5584 | 62.2473 | 62.3078 | 62.0357 | 62.2508 | 0.15847 | 0.023574 | 0.006308 | 0.016183 | 0.068308 | 0.094734 | -0.035252 | 59.6965 | 59.7366 | 59.692 | 59.5905 | 62.2793 | 62.3398 | 62.0678 | 62.2829 | -2.5828 | -2.3712 | -2.5874 | -2.3758
402.0625 | 122.2961 | -62.2787 | 59.7748 | 0.12185 | -0.00389 | -0.016578 | -0.020438 | 0.040843 | 0.071848 | -0.062717 | 59.6691 | 59.7137 | 59.6554 | 59.5493 | 62.2381 | 62.3032 | 62.0311 | 62.2417 | 0.15389 | 0.028153 | 0.015465 | 0.011605 | 0.072886 | 0.10389 | -0.030674 | 59.7011 | 59.7458 | 59.6874 | 59.5813 | 62.2702 | 62.3353 | 62.0632 | 62.2737 | -2.5691 | -2.3621 | -2.5828 | -2.3758
403.8125 | 122.2733 | -62.3016 | 59.7656 | 0.11727 | 0.000689 | -0.012 | -0.01586 | 0.045421 | 0.076426 | -0.058139 | 59.6691 | 59.7092 | 59.6508 | 59.563 | 62.2473 | 62.3032 | 62.0266 | 62.2508 | 0.14932 | 0.032732 | 0.020043 | 0.016183 | 0.077464 | 0.10847 | -0.026096 | 59.7011 | 59.7412 | 59.6828 | 59.595 | 62.2793 | 62.3353 | 62.0586 | 62.2829 | -2.5782 | -2.3575 | -2.5965 | -2.3758
405.5 | 122.2549 | -62.2879 | 59.7885 | 0.12185 | -0.008469 | -0.016578 | -0.011281 | 0.049999 | 0.071848 | -0.058139 | 59.6691 | 59.7046 | 59.6508 | 59.5722 | 62.2381 | 62.3078 | 62.0266 | 62.2508 | 0.15389 | 0.023574 | 0.015465 | 0.020762 | 0.082042 | 0.10389 | -0.026096 | 59.7011 | 59.7366 | 59.6828 | 59.6042 | 62.2702 | 62.3398 | 62.0586 | 62.2829 | -2.5691 | -2.3575 | -2.5874 | -2.3758
407.2344 | 122.2916 | -62.2833 | 59.7565 | 0.12185 | -0.00389 | -0.021157 | -0.025017 | 0.040843 | 0.067269 | -0.067295 | 59.6645 | 59.7 | 59.6462 | 59.5584 | 62.2519 | 62.3078 | 62.022 | 62.2417 | 0.15389 | 0.028153 | 0.010886 | 0.007026 | 0.072886 | 0.099312 | -0.035252 | 59.6965 | 59.732 | 59.6782 | 59.5905 | 62.2839 | 62.3398 | 62.054 | 62.2737 | -2.5874 | -2.3575 | -2.6057 | -2.3758
408.9062 | 122.2961 | -62.2971 | 59.7473 | 0.11727 | -0.013048 | -0.021157 | -0.01586 | 0.040843 | 0.071848 | -0.067295 | 59.6737 | 59.6908 | 59.6508 | 59.563 | 62.2473 | 62.3124 | 62.0266 | 62.2508 | 0.14932 | 0.018995 | 0.010886 | 0.016183 | 0.072886 | 0.10389 | -0.035252 | 59.7057 | 59.7229 | 59.6828 | 59.595 | 62.2793 | 62.3444 | 62.0586 | 62.2829 | -2.5736 | -2.3529 | -2.5965 | -2.3758
410.6562 | 122.3373 | -62.2879 | 59.7153 | 0.11727 | -0.008469 | -0.016578 | -0.020438 | 0.045421 | 0.076426 | -0.067295 | 59.6737 | 59.7046 | 59.6554 | 59.5584 | 62.2427 | 62.3078 | 62.0266 | 62.2463 | 0.14932 | 0.023574 | 0.015465 | 0.011605 | 0.077464 | 0.10847 | -0.035252 | 59.7057 | 59.7366 | 59.6874 | 59.5905 | 62.2748 | 62.3398 | 62.0586 | 62.2783 | -2.5691 | -2.3529 | -2.5874 | -2.3712
412.3438 | 122.2137 | -62.3108 | 59.7885 | 0.11727 | -0.00389 | -0.021157 | -0.011281 | 0.040843 | 0.081005 | -0.053561 | 59.6737 | 59.7 | 59.6554 | 59.5584 | 62.2473 | 62.3078 | 62.0311 | 62.2417 | 0.14932 | 0.028153 | 0.010886 | 0.020762 | 0.072886 | 0.11305 | -0.021518 | 59.7057 | 59.732 | 59.6874 | 59.5905 | 62.2793 | 62.3398 | 62.0632 | 62.2737 | -2.5736 | -2.3575 | -2.5919 | -2.3758
414.0938 | 122.2595 | -62.2742 | 59.7977 | 0.12643 | 0.000689 | -0.016578 | -0.01586 | 0.045421 | 0.081005 | -0.058139 | 59.6691 | 59.7092 | 59.6554 | 59.5676 | 62.2473 | 62.3032 | 62.022 | 62.2325 | 0.15847 | 0.032732 | 0.015465 | 0.016183 | 0.077464 | 0.11305 | -0.026096 | 59.7011 | 59.7412 | 59.6874 | 59.5996 | 62.2793 | 62.3353 | 62.054 | 62.2646 | -2.5782 | -2.3529 | -2.5919 | -2.3666
415.7969 | 122.319 | -62.2559 | 59.7931 | 0.12185 | -0.008469 | -0.021157 | -0.01586 | 0.036265 | 0.076426 | -0.058139 | 59.6691 | 59.7046 | 59.6462 | 59.5584 | 62.2427 | 62.3078 | 62.0311 | 62.2463 | 0.15389 | 0.023574 | 0.010886 | 0.016183 | 0.068308 | 0.10847 | -0.026096 | 59.7011 | 59.7366 | 59.6782 | 59.5905 | 62.2748 | 62.3398 | 62.0632 | 62.2783 | -2.5736 | -2.3621 | -2.5965 | -2.3849
417.4688 | 122.2229 | -62.3108 | 59.7931 | 0.12185 | -0.008469 | -0.021157 | -0.020438 | 0.045421 | 0.071848 | -0.058139 | 59.6782 | 59.7092 | 59.6554 | 59.5722 | 62.2427 | 62.3032 | 62.0266 | 62.2463 | 0.15389 | 0.023574 | 0.010886 | 0.011605 | 0.077464 | 0.10389 | -0.026096 | 59.7103 | 59.7412 | 59.6874 | 59.6042 | 62.2748 | 62.3353 | 62.0586 | 62.2783 | -2.5645 | -2.3483 | -2.5874 | -2.3712
419.2031 | 122.2778 | -62.3062 | 59.7748 | 0.12643 | -0.008469 | -0.016578 | -0.011281 | 0.049999 | 0.076426 | -0.058139 | 59.6737 | 59.7046 | 59.6554 | 59.5676 | 62.2427 | 62.317 | 62.0128 | 62.2508 | 0.15847 | 0.023574 | 0.015465 | 0.020762 | 0.082042 | 0.10847 | -0.026096 | 59.7057 | 59.7366 | 59.6874 | 59.5996 | 62.2748 | 62.349 | 62.0449 | 62.2829 | -2.5691 | -2.3392 | -2.5874 | -2.3575
420.8906 | 122.2504 | -62.2833 | 59.7931 | 0.12185 | -0.00389 | -0.016578 | -0.020438 | 0.045421 | 0.076426 | -0.053561 | 59.6691 | 59.7046 | 59.6462 | 59.5676 | 62.2473 | 62.3032 | 62.0266 | 62.2463 | 0.15389 | 0.028153 | 0.015465 | 0.011605 | 0.077464 | 0.10847 | -0.021518 | 59.7011 | 59.7366 | 59.6782 | 59.5996 | 62.2793 | 62.3353 | 62.0586 | 62.2783 | -2.5782 | -2.3575 | -2.6011 | -2.3804
422.6562 | 122.2321 | -62.3016 | 59.8572 | 0.12185 | -0.00389 | -0.012 | -0.01586 | 0.040843 | 0.076426 | -0.067295 | 59.6691 | 59.7 | 59.6508 | 59.563 | 62.2427 | 62.3078 | 62.022 | 62.2417 | 0.15389 | 0.028153 | 0.020043 | 0.016183 | 0.072886 | 0.10847 | -0.035252 | 59.7011 | 59.732 | 59.6828 | 59.595 | 62.2748 | 62.3398 | 62.054 | 62.2737 | -2.5736 | -2.3529 | -2.5919 | -2.3712
424.3438 | 122.2961 | -62.2833 | 59.7382 | 0.12643 | -0.008469 | -0.021157 | -0.020438 | 0.040843 | 0.076426 | -0.062717 | 59.6737 | 59.7092 | 59.6462 | 59.563 | 62.2381 | 62.3078 | 62.0266 | 62.2508 | 0.15847 | 0.023574 | 0.010886 | 0.011605 | 0.072886 | 0.10847 | -0.030674 | 59.7057 | 59.7412 | 59.6782 | 59.595 | 62.2702 | 62.3398 | 62.0586 | 62.2829 | -2.5645 | -2.3529 | -2.5919 | -2.3804
426.0781 | 122.2366 | -62.2742 | 59.8343 | 0.12185 | -0.008469 | -0.016578 | -0.01586 | 0.040843 | 0.081005 | -0.058139 | 59.6737 | 59.7 | 59.6462 | 59.563 | 62.2519 | 62.3124 | 62.0266 | 62.2508 | 0.15389 | 0.023574 | 0.015465 | 0.016183 | 0.072886 | 0.11305 | -0.026096 | 59.7057 | 59.732 | 59.6782 | 59.595 | 62.2839 | 62.3444 | 62.0586 | 62.2829 | -2.5782 | -2.3529 | -2.6057 | -2.3804
427.8281 | 122.2458 | -62.2925 | 59.8343 | 0.12643 | -0.013048 | -0.021157 | -0.01586 | 0.036265 | 0.071848 | -0.053561 | 59.6691 | 59.7137 | 59.6554 | 59.563 | 62.2473 | 62.3124 | 62.0311 | 62.2508 | 0.15847 | 0.018995 | 0.010886 | 0.016183 | 0.068308 | 0.10389 | -0.021518 | 59.7011 | 59.7458 | 59.6874 | 59.595 | 62.2793 | 62.3444 | 62.0632 | 62.2829 | -2.5782 | -2.3621 | -2.5919 | -2.3758
429.5156 | 122.3373 | -62.2696 | 59.7153 | 0.12185 | -0.00389 | -0.016578 | -0.025017 | 0.045421 | 0.076426 | -0.058139 | 59.6737 | 59.7046 | 59.6462 | 59.563 | 62.2473 | 62.3124 | 62.0266 | 62.2463 | 0.15389 | 0.028153 | 0.015465 | 0.007026 | 0.077464 | 0.10847 | -0.026096 | 59.7057 | 59.7366 | 59.6782 | 59.595 | 62.2793 | 62.3444 | 62.0586 | 62.2783 | -2.5736 | -2.3529 | -2.6011 | -2.3804
431.2812 | 122.2961 | -62.3062 | 59.7336 | 0.12643 | -0.008469 | -0.021157 | -0.011281 | 0.040843 | 0.071848 | -0.058139 | 59.6645 | 59.7 | 59.6508 | 59.5676 | 62.2473 | 62.317 | 62.0266 | 62.2508 | 0.15847 | 0.023574 | 0.010886 | 0.020762 | 0.072886 | 0.10389 | -0.026096 | 59.6965 | 59.732 | 59.6828 | 59.5996 | 62.2793 | 62.349 | 62.0586 | 62.2829 | -2.5828 | -2.3621 | -2.5965 | -2.3758
433.0312 | 122.2733 | -62.2787 | 59.816 | 0.11727 | -0.008469 | -0.021157 | -0.01586 | 0.054577 | 0.081005 | -0.058139 | 59.6737 | 59.6954 | 59.6508 | 59.563 | 62.2427 | 62.3078 | 62.0266 | 62.2371 | 0.14932 | 0.023574 | 0.010886 | 0.016183 | 0.08662 | 0.11305 | -0.026096 | 59.7057 | 59.7275 | 59.6828 | 59.595 | 62.2748 | 62.3398 | 62.0586 | 62.2691 | -2.5691 | -2.3529 | -2.5919 | -2.3758
434.7188 | 122.287 | -62.2742 | 59.8068 | 0.12185 | -0.013048 | -0.021157 | -0.025017 | 0.040843 | 0.081005 | -0.058139 | 59.6691 | 59.7137 | 59.6554 | 59.5584 | 62.2519 | 62.3124 | 62.0311 | 62.2508 | 0.15389 | 0.018995 | 0.010886 | 0.007026 | 0.072886 | 0.11305 | -0.026096 | 59.7011 | 59.7458 | 59.6874 | 59.5905 | 62.2839 | 62.3444 | 62.0632 | 62.2829 | -2.5828 | -2.3621 | -2.5965 | -2.3758
436.4531 | 122.2641 | -62.2696 | 59.8297 | 0.12185 | -0.013048 | -0.021157 | -0.01586 | 0.036265 | 0.081005 | -0.053561 | 59.6737 | 59.7092 | 59.6554 | 59.5676 | 62.2519 | 62.3078 | 62.0266 | 62.2508 | 0.15389 | 0.018995 | 0.010886 | 0.016183 | 0.068308 | 0.11305 | -0.021518 | 59.7057 | 59.7412 | 59.6874 | 59.5996 | 62.2839 | 62.3398 | 62.0586 | 62.2829 | -2.5782 | -2.3529 | -2.5965 | -2.3712
438.125 | 122.287 | -62.2833 | 59.7748 | 0.12643 | -0.008469 | -0.021157 | -0.020438 | 0.040843 | 0.067269 | -0.058139 | 59.6782 | 59.7046 | 59.6554 | 59.563 | 62.2381 | 62.3124 | 62.0311 | 62.2463 | 0.15847 | 0.023574 | 0.010886 | 0.011605 | 0.072886 | 0.099312 | -0.026096 | 59.7103 | 59.7366 | 59.6874 | 59.595 | 62.2702 | 62.3444 | 62.0632 | 62.2783 | -2.5599 | -2.3529 | -2.5828 | -2.3758
439.875 | 122.2321 | -62.2787 | 59.7931 | 0.12185 | -0.008469 | -0.016578 | -0.011281 | 0.045421 | 0.085583 | -0.058139 | 59.6691 | 59.7046 | 59.6508 | 59.5584 | 62.2519 | 62.317 | 62.022 | 62.2508 | 0.15389 | 0.023574 | 0.015465 | 0.020762 | 0.077464 | 0.11763 | -0.026096 | 59.7011 | 59.7366 | 59.6828 | 59.5905 | 62.2839 | 62.349 | 62.054 | 62.2829 | -2.5828 | -2.3529 | -2.6011 | -2.3712
441.6094 | 122.3099 | -62.2879 | 59.7656 | 0.12185 | -0.017627 | -0.025735 | -0.011281 | 0.040843 | 0.081005 | -0.062717 | 59.6782 | 59.7046 | 59.6599 | 59.563 | 62.2519 | 62.3032 | 62.0174 | 62.2417 | 0.15389 | 0.014416 | 0.006308 | 0.020762 | 0.072886 | 0.11305 | -0.030674 | 59.7103 | 59.7366 | 59.692 | 59.595 | 62.2839 | 62.3353 | 62.0494 | 62.2737 | -2.5736 | -2.3392 | -2.5919 | -2.3575
443.2812 | 122.2595 | -62.2787 | 59.816 | 0.12643 | -0.022205 | -0.016578 | -0.020438 | 0.040843 | 0.076426 | -0.058139 | 59.6737 | 59.7046 | 59.6508 | 59.5584 | 62.2473 | 62.3032 | 62.022 | 62.2508 | 0.15847 | 0.009838 | 0.015465 | 0.011605 | 0.072886 | 0.10847 | -0.026096 | 59.7057 | 59.7366 | 59.6828 | 59.5905 | 62.2793 | 62.3353 | 62.054 | 62.2829 | -2.5736 | -2.3483 | -2.5965 | -2.3712
445.0312 | 122.2046 | -62.2833 | 59.8434 | 0.12185 | -0.017627 | -0.025735 | -0.01586 | 0.045421 | 0.076426 | -0.058139 | 59.6737 | 59.7046 | 59.6508 | 59.5676 | 62.2473 | 62.3124 | 62.022 | 62.2554 | 0.15389 | 0.014416 | 0.006308 | 0.016183 | 0.077464 | 0.10847 | -0.026096 | 59.7057 | 59.7366 | 59.6828 | 59.5996 | 62.2793 | 62.3444 | 62.054 | 62.2874 | -2.5736 | -2.3483 | -2.5965 | -2.3712
446.7188 | 122.2733 | -62.265 | 59.8068 | 0.12185 | -0.013048 | -0.021157 | -0.01586 | 0.040843 | 0.071848 | -0.058139 | 59.6828 | 59.7046 | 59.6554 | 59.563 | 62.2473 | 62.3124 | 62.022 | 62.2508 | 0.15389 | 0.018995 | 0.010886 | 0.016183 | 0.072886 | 0.10389 | -0.026096 | 59.7149 | 59.7366 | 59.6874 | 59.595 | 62.2793 | 62.3444 | 62.054 | 62.2829 | -2.5645 | -2.3392 | -2.5919 | -2.3666
448.4531 | 122.2961 | -62.2696 | 59.7473 | 0.12185 | -0.017627 | -0.021157 | -0.011281 | 0.045421 | 0.071848 | -0.062717 | 59.6737 | 59.7137 | 59.6599 | 59.5584 | 62.2427 | 62.3124 | 62.0266 | 62.2554 | 0.15389 | 0.014416 | 0.010886 | 0.020762 | 0.077464 | 0.10389 | -0.030674 | 59.7057 | 59.7458 | 59.692 | 59.5905 | 62.2748 | 62.3444 | 62.0586 | 62.2874 | -2.5691 | -2.3529 | -2.5828 | -2.3666
450.2031 | 122.2321 | -62.2971 | 59.8022 | 0.13559 | -0.013048 | -0.021157 | -0.020438 | 0.045421 | 0.076426 | -0.053561 | 59.6737 | 59.7046 | 59.6462 | 59.563 | 62.2565 | 62.3124 | 62.0266 | 62.2508 | 0.16763 | 0.018995 | 0.010886 | 0.011605 | 0.077464 | 0.10847 | -0.021518 | 59.7057 | 59.7366 | 59.6782 | 59.595 | 62.2885 | 62.3444 | 62.0586 | 62.2829 | -2.5828 | -2.3529 | -2.6103 | -2.3804
451.8906 | 122.3419 | -62.2559 | 59.7794 | 0.12643 | -0.022205 | -0.021157 | -0.01586 | 0.045421 | 0.067269 | -0.062717 | 59.6737 | 59.7046 | 59.6554 | 59.5676 | 62.2427 | 62.3078 | 62.0311 | 62.2463 | 0.15847 | 0.009838 | 0.010886 | 0.016183 | 0.077464 | 0.099312 | -0.030674 | 59.7057 | 59.7366 | 59.6874 | 59.5996 | 62.2748 | 62.3398 | 62.0632 | 62.2783 | -2.5691 | -2.3575 | -2.5874 | -2.3758
453.6406 | 122.2778 | -62.2925 | 59.7931 | 0.13101 | -0.008469 | -0.021157 | -0.01586 | 0.040843 | 0.081005 | -0.058139 | 59.6691 | 59.7046 | 59.6508 | 59.5676 | 62.2519 | 62.3078 | 62.0266 | 62.2417 | 0.16305 | 0.023574 | 0.010886 | 0.016183 | 0.072886 | 0.11305 | -0.026096 | 59.7011 | 59.7366 | 59.6828 | 59.5996 | 62.2839 | 62.3398 | 62.0586 | 62.2737 | -2.5828 | -2.3575 | -2.6011 | -2.3758
455.375 | 122.2092 | -62.3062 | 59.8022 | 0.12185 | -0.017627 | -0.012 | -0.01586 | 0.049999 | 0.076426 | -0.058139 | 59.6737 | 59.7046 | 59.6508 | 59.563 | 62.2519 | 62.3032 | 62.0174 | 62.2417 | 0.15389 | 0.014416 | 0.020043 | 0.016183 | 0.082042 | 0.10847 | -0.026096 | 59.7057 | 59.7366 | 59.6828 | 59.595 | 62.2839 | 62.3353 | 62.0494 | 62.2737 | -2.5782 | -2.3438 | -2.6011 | -2.3666
457.1094 | 122.3099 | -62.2833 | 59.7565 | 0.12185 | -0.017627 | -0.021157 | -0.01586 | 0.040843 | 0.076426 | -0.058139 | 59.6782 | 59.7046 | 59.6554 | 59.563 | 62.2473 | 62.3124 | 62.0357 | 62.2417 | 0.15389 | 0.014416 | 0.010886 | 0.016183 | 0.072886 | 0.10847 | -0.026096 | 59.7103 | 59.7366 | 59.6874 | 59.595 | 62.2793 | 62.3444 | 62.0678 | 62.2737 | -2.5691 | -2.3575 | -2.5919 | -2.3804
458.8438 | 122.3053 | -62.2467 | 59.7473 | 0.12643 | -0.017627 | -0.021157 | -0.011281 | 0.049999 | 0.081005 | -0.062717 | 59.6737 | 59.7046 | 59.6508 | 59.5676 | 62.2519 | 62.317 | 62.0266 | 62.2463 | 0.15847 | 0.014416 | 0.010886 | 0.020762 | 0.082042 | 0.11305 | -0.030674 | 59.7057 | 59.7366 | 59.6828 | 59.5996 | 62.2839 | 62.349 | 62.0586 | 62.2783 | -2.5782 | -2.3529 | -2.6011 | -2.3758
460.5156 | 122.2366 | -62.265 | 59.816 | 0.12643 | -0.013048 | -0.025735 | -0.025017 | 0.049999 | 0.071848 | -0.053561 | 59.6782 | 59.7092 | 59.6554 | 59.5584 | 62.2519 | 62.3124 | 62.0357 | 62.2508 | 0.15847 | 0.018995 | 0.006308 | 0.007026 | 0.082042 | 0.10389 | -0.021518 | 59.7103 | 59.7412 | 59.6874 | 59.5905 | 62.2839 | 62.3444 | 62.0678 | 62.2829 | -2.5736 | -2.3575 | -2.5965 | -2.3804
462.2656 | 122.3145 | -62.2787 | 59.7473 | 0.12185 | -0.017627 | -0.021157 | -0.01586 | 0.040843 | 0.071848 | -0.062717 | 59.6737 | 59.7092 | 59.6508 | 59.5676 | 62.2473 | 62.3078 | 62.0266 | 62.2508 | 0.15389 | 0.014416 | 0.010886 | 0.016183 | 0.072886 | 0.10389 | -0.030674 | 59.7057 | 59.7412 | 59.6828 | 59.5996 | 62.2793 | 62.3398 | 62.0586 | 62.2829 | -2.5736 | -2.3529 | -2.5965 | -2.3758
464.0156 | 122.2641 | -62.2742 | 59.8022 | 0.12185 | -0.013048 | -0.016578 | -0.01586 | 0.049999 | 0.081005 | -0.062717 | 59.6645 | 59.7 | 59.6554 | 59.5676 | 62.2427 | 62.3078 | 62.0266 | 62.2463 | 0.15389 | 0.018995 | 0.015465 | 0.016183 | 0.082042 | 0.11305 | -0.030674 | 59.6965 | 59.732 | 59.6874 | 59.5996 | 62.2748 | 62.3398 | 62.0586 | 62.2783 | -2.5782 | -2.3621 | -2.5874 | -2.3712
465.7656 | 122.3099 | -62.2696 | 59.7839 | 0.12185 | -0.022205 | -0.016578 | -0.020438 | 0.040843 | 0.076426 | -0.062717 | 59.6828 | 59.7092 | 59.6554 | 59.5676 | 62.2473 | 62.3124 | 62.0266 | 62.2508 | 0.15389 | 0.009838 | 0.015465 | 0.011605 | 0.072886 | 0.10847 | -0.030674 | 59.7149 | 59.7412 | 59.6874 | 59.5996 | 62.2793 | 62.3444 | 62.0586 | 62.2829 | -2.5645 | -2.3438 | -2.5919 | -2.3712
467.4531 | 122.2321 | -62.2833 | 59.8022 | 0.12643 | -0.017627 | -0.021157 | -0.01586 | 0.045421 | 0.081005 | -0.058139 | 59.6691 | 59.7137 | 59.6554 | 59.563 | 62.2519 | 62.3215 | 62.0266 | 62.2554 | 0.15847 | 0.014416 | 0.010886 | 0.016183 | 0.077464 | 0.11305 | -0.026096 | 59.7011 | 59.7458 | 59.6874 | 59.595 | 62.2839 | 62.3536 | 62.0586 | 62.2874 | -2.5828 | -2.3575 | -2.5965 | -2.3712
469.1875 | 122.287 | -62.2513 | 59.8068 | 0.11269 | -0.013048 | -0.021157 | -0.011281 | 0.040843 | 0.076426 | -0.062717 | 59.6782 | 59.7092 | 59.6599 | 59.5584 | 62.2519 | 62.3078 | 62.0266 | 62.2463 | 0.14474 | 0.018995 | 0.010886 | 0.020762 | 0.072886 | 0.10847 | -0.030674 | 59.7103 | 59.7412 | 59.692 | 59.5905 | 62.2839 | 62.3398 | 62.0586 | 62.2783 | -2.5736 | -2.3483 | -2.5919 | -2.3666
470.875 | 122.3602 | -62.2604 | 59.761 | 0.12185 | -0.026784 | -0.021157 | -0.01586 | 0.040843 | 0.067269 | -0.062717 | 59.6782 | 59.7046 | 59.6554 | 59.563 | 62.2519 | 62.3078 | 62.022 | 62.2508 | 0.15389 | 0.005259 | 0.010886 | 0.016183 | 0.072886 | 0.099312 | -0.030674 | 59.7103 | 59.7366 | 59.6874 | 59.595 | 62.2839 | 62.3398 | 62.054 | 62.2829 | -2.5736 | -2.3438 | -2.5965 | -2.3666
472.625 | 122.3557 | -62.2696 | 59.7427 | 0.12185 | -0.017627 | -0.012 | -0.01586 | 0.045421 | 0.076426 | -0.062717 | 59.6782 | 59.7046 | 59.6599 | 59.563 | 62.2473 | 62.3124 | 62.022 | 62.2463 | 0.15389 | 0.014416 | 0.020043 | 0.016183 | 0.077464 | 0.10847 | -0.030674 | 59.7103 | 59.7366 | 59.692 | 59.595 | 62.2793 | 62.3444 | 62.054 | 62.2783 | -2.5691 | -2.3438 | -2.5874 | -2.3621
474.3594 | 122.3099 | -62.2833 | 59.7702 | 0.12643 | -0.017627 | -0.021157 | -0.011281 | 0.040843 | 0.071848 | -0.058139 | 59.6782 | 59.7092 | 59.6554 | 59.5676 | 62.2473 | 62.3124 | 62.022 | 62.2463 | 0.15847 | 0.014416 | 0.010886 | 0.020762 | 0.072886 | 0.10389 | -0.026096 | 59.7103 | 59.7412 | 59.6874 | 59.5996 | 62.2793 | 62.3444 | 62.054 | 62.2783 | -2.5691 | -2.3438 | -2.5919 | -2.3666
476.0938 | 122.3511 | -62.2879 | 59.7382 | 0.12185 | -0.022205 | -0.021157 | -0.01586 | 0.036265 | 0.076426 | -0.058139 | 59.6737 | 59.7046 | 59.6554 | 59.5676 | 62.2427 | 62.317 | 62.0311 | 62.2508 | 0.15389 | 0.009838 | 0.010886 | 0.016183 | 0.068308 | 0.10847 | -0.026096 | 59.7057 | 59.7366 | 59.6874 | 59.5996 | 62.2748 | 62.349 | 62.0632 | 62.2829 | -2.5691 | -2.3575 | -2.5874 | -2.3758
477.7656 | 122.2321 | -62.2696 | 59.8251 | 0.12185 | -0.017627 | -0.012 | -0.01586 | 0.036265 | 0.081005 | -0.062717 | 59.6737 | 59.7046 | 59.6599 | 59.5676 | 62.2427 | 62.3078 | 62.022 | 62.2554 | 0.15389 | 0.014416 | 0.020043 | 0.016183 | 0.068308 | 0.11305 | -0.030674 | 59.7057 | 59.7366 | 59.692 | 59.5996 | 62.2748 | 62.3398 | 62.054 | 62.2874 | -2.5691 | -2.3483 | -2.5828 | -2.3621
479.5156 | 122.2366 | -62.2787 | 59.816 | 0.12643 | -0.022205 | -0.030314 | -0.020438 | 0.045421 | 0.081005 | -0.062717 | 59.6691 | 59.7046 | 59.6554 | 59.563 | 62.2473 | 62.317 | 62.0266 | 62.2463 | 0.15847 | 0.009838 | 0.001729 | 0.011605 | 0.077464 | 0.11305 | -0.030674 | 59.7011 | 59.7366 | 59.6874 | 59.595 | 62.2793 | 62.349 | 62.0586 | 62.2783 | -2.5782 | -2.3575 | -2.5919 | -2.3712
481.2031 | 122.3419 | -62.2833 | 59.7427 | 0.12185 | -0.022205 | -0.025735 | -0.01586 | 0.040843 | 0.071848 | -0.058139 | 59.6737 | 59.7092 | 59.6554 | 59.563 | 62.2473 | 62.3124 | 62.0266 | 62.2508 | 0.15389 | 0.009838 | 0.006308 | 0.016183 | 0.072886 | 0.10389 | -0.026096 | 59.7057 | 59.7412 | 59.6874 | 59.595 | 62.2793 | 62.3444 | 62.0586 | 62.2829 | -2.5736 | -2.3529 | -2.5919 | -2.3712
482.9531 | 122.2275 | -62.3016 | 59.8434 | 0.12185 | -0.022205 | -0.021157 | -0.011281 | 0.045421 | 0.081005 | -0.048983 | 59.6782 | 59.7092 | 59.6508 | 59.563 | 62.2473 | 62.3124 | 62.022 | 62.2508 | 0.15389 | 0.009838 | 0.010886 | 0.020762 | 0.077464 | 0.11305 | -0.01694 | 59.7103 | 59.7412 | 59.6828 | 59.595 | 62.2793 | 62.3444 | 62.054 | 62.2829 | -2.5691 | -2.3438 | -2.5965 | -2.3712
484.6406 | 122.3511 | -62.2604 | 59.7473 | 0.12185 | -0.017627 | -0.021157 | -0.01586 | 0.045421 | 0.081005 | -0.062717 | 59.6782 | 59.7092 | 59.6508 | 59.5584 | 62.2473 | 62.3124 | 62.0357 | 62.2554 | 0.15389 | 0.014416 | 0.010886 | 0.016183 | 0.077464 | 0.11305 | -0.030674 | 59.7103 | 59.7412 | 59.6828 | 59.5905 | 62.2793 | 62.3444 | 62.0678 | 62.2874 | -2.5691 | -2.3575 | -2.5965 | -2.3849
486.3906 | 122.2595 | -62.2696 | 59.8206 | 0.13101 | -0.022205 | -0.025735 | -0.01586 | 0.045421 | 0.067269 | -0.053561 | 59.6782 | 59.7092 | 59.6554 | 59.5584 | 62.2473 | 62.3124 | 62.0266 | 62.2508 | 0.16305 | 0.009838 | 0.006308 | 0.016183 | 0.077464 | 0.099312 | -0.021518 | 59.7103 | 59.7412 | 59.6874 | 59.5905 | 62.2793 | 62.3444 | 62.0586 | 62.2829 | -2.5691 | -2.3483 | -2.5919 | -2.3712
488.125 | 122.2687 | -62.2742 | 59.8114 | 0.11727 | -0.013048 | -0.016578 | -0.011281 | 0.049999 | 0.071848 | -0.058139 | 59.6737 | 59.7137 | 59.6599 | 59.5676 | 62.2427 | 62.3124 | 62.0311 | 62.2463 | 0.14932 | 0.018995 | 0.015465 | 0.020762 | 0.082042 | 0.10389 | -0.026096 | 59.7057 | 59.7458 | 59.692 | 59.5996 | 62.2748 | 62.3444 | 62.0632 | 62.2783 | -2.5691 | -2.3575 | -2.5828 | -2.3712
489.8125 | 122.2137 | -62.2787 | 59.8343 | 0.12643 | -0.022205 | -0.016578 | -0.011281 | 0.049999 | 0.076426 | -0.053561 | 59.6874 | 59.7137 | 59.6508 | 59.563 | 62.2565 | 62.3124 | 62.0266 | 62.2554 | 0.15847 | 0.009838 | 0.015465 | 0.020762 | 0.082042 | 0.10847 | -0.021518 | 59.7194 | 59.7458 | 59.6828 | 59.595 | 62.2885 | 62.3444 | 62.0586 | 62.2874 | -2.5691 | -2.3392 | -2.6057 | -2.3758
491.5625 | 122.2824 | -62.2833 | 59.7885 | 0.12643 | -0.008469 | -0.030314 | -0.020438 | 0.040843 | 0.071848 | -0.067295 | 59.6828 | 59.7092 | 59.6599 | 59.5676 | 62.2519 | 62.3078 | 62.022 | 62.2463 | 0.15847 | 0.023574 | 0.001729 | 0.011605 | 0.072886 | 0.10389 | -0.035252 | 59.7149 | 59.7412 | 59.692 | 59.5996 | 62.2839 | 62.3398 | 62.054 | 62.2783 | -2.5691 | -2.3392 | -2.5919 | -2.3621
493.2969 | 122.2961 | -62.2879 | 59.7839 | 0.12185 | -0.013048 | -0.016578 | -0.006703 | 0.049999 | 0.067269 | -0.062717 | 59.6737 | 59.7092 | 59.6554 | 59.5584 | 62.2473 | 62.317 | 62.0266 | 62.2508 | 0.15389 | 0.018995 | 0.015465 | 0.02534 | 0.082042 | 0.099312 | -0.030674 | 59.7057 | 59.7412 | 59.6874 | 59.5905 | 62.2793 | 62.349 | 62.0586 | 62.2829 | -2.5736 | -2.3529 | -2.5919 | -2.3712
495.0469 | 122.2458 | -62.265 | 59.8297 | 0.12643 | -0.008469 | -0.021157 | -0.011281 | 0.045421 | 0.071848 | -0.053561 | 59.6782 | 59.7092 | 59.6554 | 59.5676 | 62.2519 | 62.3124 | 62.0266 | 62.2463 | 0.15847 | 0.023574 | 0.010886 | 0.020762 | 0.077464 | 0.10389 | -0.021518 | 59.7103 | 59.7412 | 59.6874 | 59.5996 | 62.2839 | 62.3444 | 62.0586 | 62.2783 | -2.5736 | -2.3483 | -2.5965 | -2.3712
496.7969 | 122.287 | -62.2787 | 59.7565 | 0.12185 | -0.017627 | -0.021157 | -0.011281 | 0.045421 | 0.076426 | -0.058139 | 59.6737 | 59.7092 | 59.6599 | 59.563 | 62.2519 | 62.3078 | 62.0311 | 62.2508 | 0.15389 | 0.014416 | 0.010886 | 0.020762 | 0.077464 | 0.10847 | -0.026096 | 59.7057 | 59.7412 | 59.692 | 59.595 | 62.2839 | 62.3398 | 62.0632 | 62.2829 | -2.5782 | -2.3575 | -2.5919 | -2.3712
498.4688 | 122.2366 | -62.2467 | 59.8389 | 0.12185 | -0.013048 | -0.021157 | -0.011281 | 0.054577 | 0.076426 | -0.058139 | 59.6828 | 59.7092 | 59.6508 | 59.5722 | 62.2519 | 62.3078 | 62.022 | 62.2463 | 0.15389 | 0.018995 | 0.010886 | 0.020762 | 0.08662 | 0.10847 | -0.026096 | 59.7149 | 59.7412 | 59.6828 | 59.6042 | 62.2839 | 62.3398 | 62.054 | 62.2783 | -2.5691 | -2.3392 | -2.6011 | -2.3712
500.2031 | 122.2595 | -62.2604 | 59.7885 | 0.12185 | -0.00389 | -0.016578 | -0.011281 | 0.049999 | 0.081005 | -0.062717 | 59.6782 | 59.7046 | 59.6599 | 59.563 | 62.2565 | 62.3078 | 62.0266 | 62.2463 | 0.15389 | 0.028153 | 0.015465 | 0.020762 | 0.082042 | 0.11305 | -0.030674 | 59.7103 | 59.7366 | 59.692 | 59.595 | 62.2885 | 62.3398 | 62.0586 | 62.2783 | -2.5782 | -2.3483 | -2.5965 | -2.3666
501.9375 | 122.3373 | -62.2971 | 59.7519 | 0.12643 | -0.013048 | -0.021157 | -0.01586 | 0.049999 | 0.076426 | -0.053561 | 59.6737 | 59.7183 | 59.6554 | 59.563 | 62.2473 | 62.3078 | 62.0266 | 62.2554 | 0.15847 | 0.018995 | 0.010886 | 0.016183 | 0.082042 | 0.10847 | -0.021518 | 59.7057 | 59.7504 | 59.6874 | 59.595 | 62.2793 | 62.3398 | 62.0586 | 62.2874 | -2.5736 | -2.3529 | -2.5919 | -2.3712
503.625 | 122.3236 | -62.2696 | 59.7885 | 0.12643 | -0.013048 | -0.025735 | -0.020438 | 0.040843 | 0.076426 | -0.058139 | 59.6828 | 59.7137 | 59.6462 | 59.5722 | 62.2473 | 62.3078 | 62.022 | 62.2554 | 0.15847 | 0.018995 | 0.006308 | 0.011605 | 0.072886 | 0.10847 | -0.026096 | 59.7149 | 59.7458 | 59.6782 | 59.6042 | 62.2793 | 62.3398 | 62.054 | 62.2874 | -2.5645 | -2.3392 | -2.6011 | -2.3758
505.375 | 122.3602 | -62.2559 | 59.7702 | 0.12643 | -0.013048 | -0.016578 | -0.01586 | 0.045421 | 0.076426 | -0.058139 | 59.6874 | 59.7092 | 59.6508 | 59.5722 | 62.2473 | 62.3124 | 62.0266 | 62.2508 | 0.15847 | 0.018995 | 0.015465 | 0.016183 | 0.077464 | 0.10847 | -0.026096 | 59.7194 | 59.7412 | 59.6828 | 59.6042 | 62.2793 | 62.3444 | 62.0586 | 62.2829 | -2.5599 | -2.3392 | -2.5965 | -2.3758
507.125 | 122.3511 | -62.2742 | 59.7244 | 0.12185 | -0.00389 | -0.016578 | -0.01586 | 0.045421 | 0.067269 | -0.048983 | 59.6737 | 59.7046 | 59.6599 | 59.5676 | 62.2519 | 62.3124 | 62.0128 | 62.2508 | 0.15389 | 0.028153 | 0.015465 | 0.016183 | 0.077464 | 0.099312 | -0.01694 | 59.7057 | 59.7366 | 59.692 | 59.5996 | 62.2839 | 62.3444 | 62.0449 | 62.2829 | -2.5782 | -2.3392 | -2.5919 | -2.3529
508.7969 | 122.2961 | -62.2742 | 59.7565 | 0.12185 | -0.013048 | -0.021157 | -0.01586 | 0.045421 | 0.067269 | -0.053561 | 59.6828 | 59.7092 | 59.6554 | 59.563 | 62.2381 | 62.3078 | 62.0266 | 62.2463 | 0.15389 | 0.018995 | 0.010886 | 0.016183 | 0.077464 | 0.099312 | -0.021518 | 59.7149 | 59.7412 | 59.6874 | 59.595 | 62.2702 | 62.3398 | 62.0586 | 62.2783 | -2.5553 | -2.3438 | -2.5828 | -2.3712
510.5312 | 122.3373 | -62.2559 | 59.7931 | 0.12643 | -0.022205 | -0.021157 | -0.029595 | 0.040843 | 0.071848 | -0.062717 | 59.6782 | 59.7046 | 59.6508 | 59.5584 | 62.2427 | 62.3124 | 62.0311 | 62.2463 | 0.15847 | 0.009838 | 0.010886 | 0.002448 | 0.072886 | 0.10389 | -0.030674 | 59.7103 | 59.7366 | 59.6828 | 59.5905 | 62.2748 | 62.3444 | 62.0632 | 62.2783 | -2.5645 | -2.3529 | -2.5919 | -2.3804
512.2812 | 122.3007 | -62.2925 | 59.7656 | 0.12185 | -0.017627 | -0.021157 | -0.01586 | 0.045421 | 0.071848 | -0.058139 | 59.6782 | 59.7137 | 59.6508 | 59.5676 | 62.2427 | 62.3078 | 62.0266 | 62.2508 | 0.15389 | 0.014416 | 0.010886 | 0.016183 | 0.077464 | 0.10389 | -0.026096 | 59.7103 | 59.7458 | 59.6828 | 59.5996 | 62.2748 | 62.3398 | 62.0586 | 62.2829 | -2.5645 | -2.3483 | -2.5919 | -2.3758
514.0156 | 122.3328 | -62.2513 | 59.7748 | 0.13101 | -0.008469 | -0.016578 | -0.020438 | 0.045421 | 0.076426 | -0.058139 | 59.6737 | 59.7046 | 59.6554 | 59.5722 | 62.2427 | 62.3124 | 62.0174 | 62.2463 | 0.16305 | 0.023574 | 0.015465 | 0.011605 | 0.077464 | 0.10847 | -0.026096 | 59.7057 | 59.7366 | 59.6874 | 59.6042 | 62.2748 | 62.3444 | 62.0494 | 62.2783 | -2.5691 | -2.3438 | -2.5874 | -2.3621
515.6875 | 122.2595 | -62.2833 | 59.816 | 0.13101 | -0.00389 | -0.016578 | -0.01586 | 0.049999 | 0.085583 | -0.053561 | 59.6782 | 59.7092 | 59.6645 | 59.5722 | 62.2427 | 62.3078 | 62.0128 | 62.2508 | 0.16305 | 0.028153 | 0.015465 | 0.016183 | 0.082042 | 0.11763 | -0.021518 | 59.7103 | 59.7412 | 59.6966 | 59.6042 | 62.2748 | 62.3398 | 62.0449 | 62.2829 | -2.5645 | -2.3346 | -2.5782 | -2.3483
517.4375 | 122.2595 | -62.2696 | 59.8068 | 0.12643 | -0.008469 | -0.021157 | -0.01586 | 0.040843 | 0.076426 | -0.058139 | 59.6737 | 59.7092 | 59.6599 | 59.563 | 62.2473 | 62.317 | 62.022 | 62.2508 | 0.15847 | 0.023574 | 0.010886 | 0.016183 | 0.072886 | 0.10847 | -0.026096 | 59.7057 | 59.7412 | 59.692 | 59.595 | 62.2793 | 62.349 | 62.054 | 62.2829 | -2.5736 | -2.3483 | -2.5874 | -2.3621
519.1719 | 122.2733 | -62.2971 | 59.7748 | 0.12185 | -0.008469 | -0.021157 | -0.020438 | 0.045421 | 0.076426 | -0.062717 | 59.6737 | 59.7046 | 59.6554 | 59.5676 | 62.2565 | 62.317 | 62.0266 | 62.2508 | 0.15389 | 0.023574 | 0.010886 | 0.011605 | 0.077464 | 0.10847 | -0.030674 | 59.7057 | 59.7366 | 59.6874 | 59.5996 | 62.2885 | 62.349 | 62.0586 | 62.2829 | -2.5828 | -2.3529 | -2.6011 | -2.3712
520.8594 | 122.2046 | -62.2833 | 59.8434 | 0.12643 | 0.000689 | -0.016578 | -0.020438 | 0.045421 | 0.071848 | -0.062717 | 59.6782 | 59.7092 | 59.6554 | 59.563 | 62.2427 | 62.3078 | 62.0266 | 62.2554 | 0.15847 | 0.032732 | 0.015465 | 0.011605 | 0.077464 | 0.10389 | -0.030674 | 59.7103 | 59.7412 | 59.6874 | 59.595 | 62.2748 | 62.3398 | 62.0586 | 62.2874 | -2.5645 | -2.3483 | -2.5874 | -2.3712
522.625 | 122.2137 | -62.2971 | 59.8022 | 0.13101 | -0.008469 | -0.021157 | -0.011281 | 0.040843 | 0.076426 | -0.053561 | 59.6782 | 59.7 | 59.6508 | 59.563 | 62.2473 | 62.3124 | 62.0266 | 62.2508 | 0.16305 | 0.023574 | 0.010886 | 0.020762 | 0.072886 | 0.10847 | -0.021518 | 59.7103 | 59.732 | 59.6828 | 59.595 | 62.2793 | 62.3444 | 62.0586 | 62.2829 | -2.5691 | -2.3483 | -2.5965 | -2.3758
524.3594 | 122.2366 | -62.3062 | 59.8114 | 0.12643 | 0.000689 | -0.016578 | -0.01586 | 0.045421 | 0.076426 | -0.053561 | 59.6782 | 59.7046 | 59.6554 | 59.5676 | 62.261 | 62.3078 | 61.9991 | 62.2554 | 0.15847 | 0.032732 | 0.015465 | 0.016183 | 0.077464 | 0.10847 | -0.021518 | 59.7103 | 59.7366 | 59.6874 | 59.5996 | 62.2931 | 62.3398 | 62.0311 | 62.2874 | -2.5828 | -2.3209 | -2.6057 | -2.3437
526.1094 | 122.2916 | -62.2879 | 59.7656 | 0.12643 | -0.00389 | -0.016578 | -0.01586 | 0.045421 | 0.071848 | -0.058139 | 59.6782 | 59.7092 | 59.6554 | 59.5676 | 62.2427 | 62.3032 | 62.022 | 62.2463 | 0.15847 | 0.028153 | 0.015465 | 0.016183 | 0.077464 | 0.10389 | -0.026096 | 59.7103 | 59.7412 | 59.6874 | 59.5996 | 62.2748 | 62.3353 | 62.054 | 62.2783 | -2.5645 | -2.3438 | -2.5874 | -2.3666
527.8594 | 122.2321 | -62.3108 | 59.8022 | 0.12185 | -0.008469 | -0.021157 | -0.020438 | 0.045421 | 0.076426 | -0.058139 | 59.6828 | 59.7046 | 59.6599 | 59.5676 | 62.2519 | 62.3124 | 62.022 | 62.2508 | 0.15389 | 0.023574 | 0.010886 | 0.011605 | 0.077464 | 0.10847 | -0.026096 | 59.7149 | 59.7366 | 59.692 | 59.5996 | 62.2839 | 62.3444 | 62.054 | 62.2829 | -2.5691 | -2.3392 | -2.5919 | -2.3621
529.5469 | 122.2321 | -62.2742 | 59.8389 | 0.12185 | -0.008469 | -0.012 | -0.006703 | 0.054577 | 0.081005 | -0.058139 | 59.6782 | 59.7092 | 59.6599 | 59.5676 | 62.2519 | 62.317 | 62.0266 | 62.2554 | 0.15389 | 0.023574 | 0.020043 | 0.02534 | 0.08662 | 0.11305 | -0.026096 | 59.7103 | 59.7412 | 59.692 | 59.5996 | 62.2839 | 62.349 | 62.0586 | 62.2874 | -2.5736 | -2.3483 | -2.5919 | -2.3666
531.2812 | 122.3465 | -62.2604 | 59.7702 | 0.12643 | -0.013048 | -0.016578 | -0.01586 | 0.040843 | 0.071848 | -0.058139 | 59.6737 | 59.7183 | 59.6508 | 59.5538 | 62.2473 | 62.317 | 62.0266 | 62.2554 | 0.15847 | 0.018995 | 0.015465 | 0.016183 | 0.072886 | 0.10389 | -0.026096 | 59.7057 | 59.7504 | 59.6828 | 59.5859 | 62.2793 | 62.349 | 62.0586 | 62.2874 | -2.5736 | -2.3529 | -2.5965 | -2.3758
533.0312 | 122.2549 | -62.2696 | 59.8022 | 0.12643 | -0.008469 | -0.021157 | -0.01586 | 0.045421 | 0.081005 | -0.058139 | 59.6782 | 59.7137 | 59.6599 | 59.5676 | 62.2519 | 62.3124 | 62.0266 | 62.2554 | 0.15847 | 0.023574 | 0.010886 | 0.016183 | 0.077464 | 0.11305 | -0.026096 | 59.7103 | 59.7458 | 59.692 | 59.5996 | 62.2839 | 62.3444 | 62.0586 | 62.2874 | -2.5736 | -2.3483 | -2.5919 | -2.3666
534.7188 | 122.374 | -62.265 | 59.7794 | 0.12185 | -0.00389 | -0.021157 | -0.020438 | 0.045421 | 0.076426 | -0.053561 | 59.6782 | 59.7046 | 59.6554 | 59.5538 | 62.2519 | 62.317 | 62.0311 | 62.2554 | 0.15389 | 0.028153 | 0.010886 | 0.011605 | 0.077464 | 0.10847 | -0.021518 | 59.7103 | 59.7366 | 59.6874 | 59.5859 | 62.2839 | 62.349 | 62.0632 | 62.2874 | -2.5736 | -2.3529 | -2.5965 | -2.3758
536.4531 | 122.2549 | -62.2696 | 59.8343 | 0.12185 | -0.013048 | -0.021157 | -0.020438 | 0.040843 | 0.081005 | -0.062717 | 59.6691 | 59.7137 | 59.6554 | 59.5722 | 62.2519 | 62.3078 | 62.022 | 62.2554 | 0.15389 | 0.018995 | 0.010886 | 0.011605 | 0.072886 | 0.11305 | -0.030674 | 59.7011 | 59.7458 | 59.6874 | 59.6042 | 62.2839 | 62.3398 | 62.054 | 62.2874 | -2.5828 | -2.3529 | -2.5965 | -2.3666
538.2031 | 122.2595 | -62.2604 | 59.8572 | 0.12643 | -0.013048 | -0.021157 | -0.011281 | 0.045421 | 0.085583 | -0.048983 | 59.6782 | 59.7092 | 59.6508 | 59.5722 | 62.2519 | 62.3124 | 62.022 | 62.2508 | 0.15847 | 0.018995 | 0.010886 | 0.020762 | 0.077464 | 0.11763 | -0.01694 | 59.7103 | 59.7412 | 59.6828 | 59.6042 | 62.2839 | 62.3444 | 62.054 | 62.2829 | -2.5736 | -2.3438 | -2.6011 | -2.3712
539.8906 | 122.3602 | -62.2879 | 59.729 | 0.12643 | -0.017627 | -0.021157 | -0.020438 | 0.049999 | 0.076426 | -0.053561 | 59.692 | 59.7092 | 59.6599 | 59.563 | 62.2473 | 62.3124 | 62.0128 | 62.2554 | 0.15847 | 0.014416 | 0.010886 | 0.011605 | 0.082042 | 0.10847 | -0.021518 | 59.724 | 59.7412 | 59.692 | 59.595 | 62.2793 | 62.3444 | 62.0449 | 62.2874 | -2.5553 | -2.3209 | -2.5874 | -2.3529
541.6406 | 122.2366 | -62.2971 | 59.8618 | 0.12185 | -0.008469 | -0.016578 | -0.020438 | 0.049999 | 0.081005 | -0.053561 | 59.6828 | 59.7092 | 59.6554 | 59.5676 | 62.2473 | 62.317 | 62.022 | 62.2463 | 0.15389 | 0.023574 | 0.015465 | 0.011605 | 0.082042 | 0.11305 | -0.021518 | 59.7149 | 59.7412 | 59.6874 | 59.5996 | 62.2793 | 62.349 | 62.054 | 62.2783 | -2.5645 | -2.3392 | -2.5919 | -2.3666
543.375 | 122.2549 | -62.2971 | 59.8022 | 0.13101 | -0.00389 | -0.016578 | -0.020438 | 0.045421 | 0.076426 | -0.058139 | 59.6737 | 59.7092 | 59.6645 | 59.563 | 62.2519 | 62.3124 | 62.0174 | 62.2508 | 0.16305 | 0.028153 | 0.015465 | 0.011605 | 0.077464 | 0.10847 | -0.026096 | 59.7057 | 59.7412 | 59.6966 | 59.595 | 62.2839 | 62.3444 | 62.0494 | 62.2829 | -2.5782 | -2.3438 | -2.5874 | -2.3529
545.125 | 122.2961 | -62.2879 | 59.7931 | 0.12643 | -0.008469 | -0.021157 | -0.025017 | 0.054577 | 0.081005 | -0.058139 | 59.6828 | 59.7092 | 59.6554 | 59.563 | 62.2473 | 62.317 | 62.0174 | 62.2508 | 0.15847 | 0.023574 | 0.010886 | 0.007026 | 0.08662 | 0.11305 | -0.026096 | 59.7149 | 59.7412 | 59.6874 | 59.595 | 62.2793 | 62.349 | 62.0494 | 62.2829 | -2.5645 | -2.3346 | -2.5919 | -2.3621
546.8125 | 122.2137 | -62.3199 | 59.7931 | 0.12185 | 0.000689 | -0.021157 | -0.01586 | 0.045421 | 0.071848 | -0.048983 | 59.6828 | 59.7137 | 59.6691 | 59.5722 | 62.2519 | 62.317 | 62.022 | 62.2417 | 0.15389 | 0.032732 | 0.010886 | 0.016183 | 0.077464 | 0.10389 | -0.01694 | 59.7149 | 59.7458 | 59.7011 | 59.6042 | 62.2839 | 62.349 | 62.054 | 62.2737 | -2.5691 | -2.3392 | -2.5828 | -2.3529
548.5469 | 122.287 | -62.2879 | 59.7656 | 0.12185 | -0.00389 | -0.021157 | -0.011281 | 0.049999 | 0.071848 | -0.048983 | 59.6828 | 59.7092 | 59.6645 | 59.5767 | 62.2565 | 62.3124 | 62.0128 | 62.2508 | 0.15389 | 0.028153 | 0.010886 | 0.020762 | 0.082042 | 0.10389 | -0.01694 | 59.7149 | 59.7412 | 59.6966 | 59.6088 | 62.2885 | 62.3444 | 62.0449 | 62.2829 | -2.5736 | -2.33 | -2.5919 | -2.3483
550.2188 | 122.3236 | -62.2559 | 59.7885 | 0.13101 | -0.013048 | -0.021157 | -0.020438 | 0.045421 | 0.071848 | -0.058139 | 59.6828 | 59.7137 | 59.6599 | 59.5584 | 62.2519 | 62.317 | 62.0311 | 62.2554 | 0.16305 | 0.018995 | 0.010886 | 0.011605 | 0.077464 | 0.10389 | -0.026096 | 59.7149 | 59.7458 | 59.692 | 59.5905 | 62.2839 | 62.349 | 62.0632 | 62.2874 | -2.5691 | -2.3483 | -2.5919 | -2.3712
551.9844 | 122.3373 | -62.2559 | 59.7839 | 0.12643 | -0.013048 | -0.025735 | -0.020438 | 0.040843 | 0.071848 | -0.053561 | 59.6737 | 59.7092 | 59.6599 | 59.563 | 62.2473 | 62.3078 | 62.022 | 62.2508 | 0.15847 | 0.018995 | 0.006308 | 0.011605 | 0.072886 | 0.10389 | -0.021518 | 59.7057 | 59.7412 | 59.692 | 59.595 | 62.2793 | 62.3398 | 62.054 | 62.2829 | -2.5736 | -2.3483 | -2.5874 | -2.3621
553.7188 | 122.3373 | -62.265 | 59.7931 | 0.11727 | -0.008469 | -0.021157 | -0.011281 | 0.049999 | 0.071848 | -0.053561 | 59.6782 | 59.7183 | 59.6599 | 59.563 | 62.2519 | 62.317 | 62.0266 | 62.2508 | 0.14932 | 0.023574 | 0.010886 | 0.020762 | 0.082042 | 0.10389 | -0.021518 | 59.7103 | 59.7504 | 59.692 | 59.595 | 62.2839 | 62.349 | 62.0586 | 62.2829 | -2.5736 | -2.3483 | -2.5919 | -2.3666
555.4688 | 122.3557 | -62.2284 | 59.761 | 0.12185 | -0.008469 | -0.021157 | -0.025017 | 0.036265 | 0.071848 | -0.053561 | 59.6828 | 59.7092 | 59.6554 | 59.5584 | 62.2565 | 62.3124 | 62.0266 | 62.2463 | 0.15389 | 0.023574 | 0.010886 | 0.007026 | 0.068308 | 0.10389 | -0.021518 | 59.7149 | 59.7412 | 59.6874 | 59.5905 | 62.2885 | 62.3444 | 62.0586 | 62.2783 | -2.5736 | -2.3438 | -2.6011 | -2.3712
557.2344 | 122.3694 | -62.2604 | 59.7748 | 0.12643 | -0.013048 | -0.021157 | -0.01586 | 0.040843 | 0.067269 | -0.062717 | 59.6782 | 59.7092 | 59.6554 | 59.5584 | 62.2519 | 62.3124 | 62.0082 | 62.2508 | 0.15847 | 0.018995 | 0.010886 | 0.016183 | 0.072886 | 0.099312 | -0.030674 | 59.7103 | 59.7412 | 59.6874 | 59.5905 | 62.2839 | 62.3444 | 62.0403 | 62.2829 | -2.5736 | -2.33 | -2.5965 | -2.3529
558.9062 | 122.2229 | -62.2787 | 59.8434 | 0.12643 | -0.008469 | -0.021157 | -0.011281 | 0.040843 | 0.076426 | -0.058139 | 59.6782 | 59.7046 | 59.6508 | 59.5676 | 62.2519 | 62.3124 | 62.022 | 62.2508 | 0.15847 | 0.023574 | 0.010886 | 0.020762 | 0.072886 | 0.10847 | -0.026096 | 59.7103 | 59.7366 | 59.6828 | 59.5996 | 62.2839 | 62.3444 | 62.054 | 62.2829 | -2.5736 | -2.3438 | -2.6011 | -2.3712
560.6562 | 122.3053 | -62.2742 | 59.7702 | 0.12643 | -0.013048 | -0.021157 | -0.01586 | 0.045421 | 0.071848 | -0.058139 | 59.6874 | 59.7183 | 59.6645 | 59.5676 | 62.2565 | 62.3124 | 62.0174 | 62.2508 | 0.15847 | 0.018995 | 0.010886 | 0.016183 | 0.077464 | 0.10389 | -0.026096 | 59.7194 | 59.7504 | 59.6966 | 59.5996 | 62.2885 | 62.3444 | 62.0494 | 62.2829 | -2.5691 | -2.33 | -2.5919 | -2.3529
562.4062 | 122.3145 | -62.2742 | 59.7519 | 0.13101 | -0.013048 | -0.016578 | -0.01586 | 0.040843 | 0.071848 | -0.062717 | 59.6828 | 59.7092 | 59.6508 | 59.5676 | 62.261 | 62.3215 | 62.0128 | 62.2554 | 0.16305 | 0.018995 | 0.015465 | 0.016183 | 0.072886 | 0.10389 | -0.030674 | 59.7149 | 59.7412 | 59.6828 | 59.5996 | 62.2931 | 62.3536 | 62.0449 | 62.2874 | -2.5782 | -2.33 | -2.6103 | -2.3621
564.1406 | 122.3236 | -62.2421 | 59.8068 | 0.11727 | -0.013048 | -0.021157 | -0.020438 | 0.045421 | 0.076426 | -0.058139 | 59.6782 | 59.7092 | 59.6599 | 59.563 | 62.2519 | 62.317 | 62.022 | 62.2554 | 0.14932 | 0.018995 | 0.010886 | 0.011605 | 0.077464 | 0.10847 | -0.026096 | 59.7103 | 59.7412 | 59.692 | 59.595 | 62.2839 | 62.349 | 62.054 | 62.2874 | -2.5736 | -2.3438 | -2.5919 | -2.3621
565.8125 | 122.2595 | -62.2559 | 59.7931 | 0.12643 | -0.00389 | -0.012 | -0.011281 | 0.049999 | 0.071848 | -0.048983 | 59.6782 | 59.7183 | 59.6599 | 59.5676 | 62.2473 | 62.317 | 62.0128 | 62.2508 | 0.15847 | 0.028153 | 0.020043 | 0.020762 | 0.082042 | 0.10389 | -0.01694 | 59.7103 | 59.7504 | 59.692 | 59.5996 | 62.2793 | 62.349 | 62.0449 | 62.2829 | -2.5691 | -2.3346 | -2.5874 | -2.3529
567.5781 | 122.3511 | -62.2879 | 59.7656 | 0.13101 | 0.000689 | -0.021157 | -0.020438 | 0.040843 | 0.071848 | -0.062717 | 59.6828 | 59.7046 | 59.6599 | 59.5722 | 62.2473 | 62.3078 | 62.022 | 62.2554 | 0.16305 | 0.032732 | 0.010886 | 0.011605 | 0.072886 | 0.10389 | -0.030674 | 59.7149 | 59.7366 | 59.692 | 59.6042 | 62.2793 | 62.3398 | 62.054 | 62.2874 | -2.5645 | -2.3392 | -2.5874 | -2.3621
569.2656 | 122.2137 | -62.2833 | 59.7839 | 0.13101 | -0.00389 | -0.016578 | -0.011281 | 0.049999 | 0.076426 | -0.058139 | 59.6737 | 59.7137 | 59.6645 | 59.5722 | 62.261 | 62.3078 | 62.0082 | 62.2554 | 0.16305 | 0.028153 | 0.015465 | 0.020762 | 0.082042 | 0.10847 | -0.026096 | 59.7057 | 59.7458 | 59.6966 | 59.6042 | 62.2931 | 62.3398 | 62.0403 | 62.2874 | -2.5874 | -2.3346 | -2.5965 | -2.3437
571.0156 | 122.3373 | -62.2696 | 59.7839 | 0.12185 | -0.008469 | -0.021157 | -0.020438 | 0.040843 | 0.076426 | -0.058139 | 59.6828 | 59.7183 | 59.6691 | 59.5722 | 62.2519 | 62.3215 | 62.022 | 62.2508 | 0.15389 | 0.023574 | 0.010886 | 0.011605 | 0.072886 | 0.10847 | -0.026096 | 59.7149 | 59.7504 | 59.7011 | 59.6042 | 62.2839 | 62.3536 | 62.054 | 62.2829 | -2.5691 | -2.3392 | -2.5828 | -2.3529
572.7656 | 122.2137 | -62.2925 | 59.8251 | 0.13559 | -0.00389 | -0.021157 | -0.01586 | 0.045421 | 0.085583 | -0.053561 | 59.6737 | 59.7046 | 59.6554 | 59.5767 | 62.2473 | 62.3124 | 62.0128 | 62.2508 | 0.16763 | 0.028153 | 0.010886 | 0.016183 | 0.077464 | 0.11763 | -0.021518 | 59.7057 | 59.7366 | 59.6874 | 59.6088 | 62.2793 | 62.3444 | 62.0449 | 62.2829 | -2.5736 | -2.3392 | -2.5919 | -2.3575
574.5156 | 122.2183 | -62.3062 | 59.7885 | 0.12185 | -0.013048 | -0.016578 | -0.020438 | 0.049999 | 0.085583 | -0.048983 | 59.6782 | 59.7183 | 59.6599 | 59.5676 | 62.2473 | 62.3215 | 62.0174 | 62.2417 | 0.15389 | 0.018995 | 0.015465 | 0.011605 | 0.082042 | 0.11763 | -0.01694 | 59.7103 | 59.7504 | 59.692 | 59.5996 | 62.2793 | 62.3536 | 62.0494 | 62.2737 | -2.5691 | -2.3392 | -2.5874 | -2.3575
576.2031 | 122.2412 | -62.2971 | 59.8114 | 0.13101 | -0.00389 | -0.016578 | -0.01586 | 0.054577 | 0.081005 | -0.053561 | 59.6828 | 59.7092 | 59.6508 | 59.5722 | 62.2519 | 62.3124 | 61.9991 | 62.2508 | 0.16305 | 0.028153 | 0.015465 | 0.016183 | 0.08662 | 0.11305 | -0.021518 | 59.7149 | 59.7412 | 59.6828 | 59.6042 | 62.2839 | 62.3444 | 62.0311 | 62.2829 | -2.5691 | -2.3163 | -2.6011 | -2.3483
577.9688 | 122.2275 | -62.2787 | 59.8251 | 0.13101 | -0.00389 | -0.021157 | -0.006703 | 0.049999 | 0.076426 | -0.062717 | 59.6828 | 59.7137 | 59.6599 | 59.5676 | 62.2519 | 62.3124 | 62.0174 | 62.26 | 0.16305 | 0.028153 | 0.010886 | 0.02534 | 0.082042 | 0.10847 | -0.030674 | 59.7149 | 59.7458 | 59.692 | 59.5996 | 62.2839 | 62.3444 | 62.0494 | 62.292 | -2.5691 | -2.3346 | -2.5919 | -2.3575
579.6562 | 122.3694 | -62.2559 | 59.7565 | 0.12185 | -0.008469 | -0.016578 | -0.020438 | 0.045421 | 0.076426 | -0.058139 | 59.6874 | 59.7092 | 59.6691 | 59.5676 | 62.2473 | 62.3124 | 62.0082 | 62.2554 | 0.15389 | 0.023574 | 0.015465 | 0.011605 | 0.077464 | 0.10847 | -0.026096 | 59.7194 | 59.7412 | 59.7011 | 59.5996 | 62.2793 | 62.3444 | 62.0403 | 62.2874 | -2.5599 | -2.3209 | -2.5782 | -2.3392
581.3906 | 122.2366 | -62.2879 | 59.8343 | 0.12643 | -0.008469 | -0.016578 | -0.020438 | 0.040843 | 0.071848 | -0.058139 | 59.6828 | 59.7092 | 59.6554 | 59.5676 | 62.2519 | 62.3124 | 61.9716 | 62.2554 | 0.15847 | 0.023574 | 0.015465 | 0.011605 | 0.072886 | 0.10389 | -0.026096 | 59.7149 | 59.7412 | 59.6874 | 59.5996 | 62.2839 | 62.3444 | 62.0037 | 62.2874 | -2.5691 | -2.2888 | -2.5965 | -2.3163
583.1406 | 122.2 | -62.3199 | 59.8114 | 0.12643 | -0.008469 | -0.016578 | -0.01586 | 0.045421 | 0.071848 | -0.053561 | 59.6782 | 59.7137 | 59.6599 | 59.5767 | 62.261 | 62.3124 | 61.9991 | 62.2508 | 0.15847 | 0.023574 | 0.015465 | 0.016183 | 0.077464 | 0.10389 | -0.021518 | 59.7103 | 59.7458 | 59.692 | 59.6088 | 62.2931 | 62.3444 | 62.0311 | 62.2829 | -2.5828 | -2.3209 | -2.6011 | -2.3392
584.8281 | 122.2229 | -62.2604 | 59.8526 | 0.13101 | -0.00389 | -0.016578 | -0.011281 | 0.045421 | 0.076426 | -0.053561 | 59.6828 | 59.7183 | 59.6599 | 59.5676 | 62.2519 | 62.3078 | 61.9625 | 62.2508 | 0.16305 | 0.028153 | 0.015465 | 0.020762 | 0.077464 | 0.10847 | -0.021518 | 59.7149 | 59.7504 | 59.692 | 59.5996 | 62.2839 | 62.3398 | 61.9945 | 62.2829 | -2.5691 | -2.2797 | -2.5919 | -2.3025
586.5625 | 122.2229 | -62.2696 | 59.8343 | 0.12185 | -0.00389 | -0.016578 | -0.011281 | 0.049999 | 0.071848 | -0.058139 | 59.6828 | 59.7092 | 59.6599 | 59.5722 | 62.2519 | 62.3078 | 61.9762 | 62.2508 | 0.15389 | 0.028153 | 0.015465 | 0.020762 | 0.082042 | 0.10389 | -0.026096 | 59.7149 | 59.7412 | 59.692 | 59.6042 | 62.2839 | 62.3398 | 62.0082 | 62.2829 | -2.5691 | -2.2934 | -2.5919 | -2.3163
588.25 | 122.2092 | -62.3062 | 59.8022 | 0.12643 | -0.008469 | -0.021157 | -0.01586 | 0.049999 | 0.081005 | -0.053561 | 59.6828 | 59.7137 | 59.6645 | 59.5676 | 62.2519 | 62.317 | 62.0174 | 62.2508 | 0.15847 | 0.023574 | 0.010886 | 0.016183 | 0.082042 | 0.11305 | -0.021518 | 59.7149 | 59.7458 | 59.6966 | 59.5996 | 62.2839 | 62.349 | 62.0494 | 62.2829 | -2.5691 | -2.3346 | -2.5874 | -2.3529
590 | 122.1954 | -62.3062 | 59.8068 | 0.12643 | -0.00389 | -0.012 | -0.01586 | 0.045421 | 0.076426 | -0.053561 | 59.6782 | 59.7137 | 59.6599 | 59.5676 | 62.2565 | 62.3124 | 62.022 | 62.2508 | 0.15847 | 0.028153 | 0.020043 | 0.016183 | 0.077464 | 0.10847 | -0.021518 | 59.7103 | 59.7458 | 59.692 | 59.5996 | 62.2885 | 62.3444 | 62.054 | 62.2829 | -2.5782 | -2.3438 | -2.5965 | -2.3621
591.7344 | 122.3328 | -62.265 | 59.7382 | 0.12185 | -0.00389 | -0.021157 | -0.025017 | 0.040843 | 0.071848 | -0.058139 | 59.6828 | 59.7092 | 59.6599 | 59.5722 | 62.2519 | 62.3078 | 61.9716 | 62.2508 | 0.15389 | 0.028153 | 0.010886 | 0.007026 | 0.072886 | 0.10389 | -0.026096 | 59.7149 | 59.7412 | 59.692 | 59.6042 | 62.2839 | 62.3398 | 62.0037 | 62.2829 | -2.5691 | -2.2888 | -2.5919 | -2.3117
593.4844 | 122.3557 | -62.2925 | 59.7382 | 0.12643 | -0.00389 | -0.016578 | -0.01586 | 0.040843 | 0.076426 | -0.053561 | 59.6828 | 59.7183 | 59.6554 | 59.563 | 62.2519 | 62.3124 | 62.0128 | 62.2554 | 0.15847 | 0.028153 | 0.015465 | 0.016183 | 0.072886 | 0.10847 | -0.021518 | 59.7149 | 59.7504 | 59.6874 | 59.595 | 62.2839 | 62.3444 | 62.0449 | 62.2874 | -2.5691 | -2.33 | -2.5965 | -2.3575
595.1562 | 122.3099 | -62.2833 | 59.7519 | 0.11727 | -0.008469 | -0.025735 | -0.020438 | 0.045421 | 0.076426 | -0.058139 | 59.6828 | 59.7137 | 59.6691 | 59.5584 | 62.2519 | 62.3124 | 61.9716 | 62.2554 | 0.14932 | 0.023574 | 0.006308 | 0.011605 | 0.077464 | 0.10847 | -0.026096 | 59.7149 | 59.7458 | 59.7011 | 59.5905 | 62.2839 | 62.3444 | 62.0037 | 62.2874 | -2.5691 | -2.2888 | -2.5828 | -2.3025
596.8906 | 122.2961 | -62.2742 | 59.7748 | 0.11727 | -0.008469 | -0.025735 | -0.01586 | 0.045421 | 0.067269 | -0.062717 | 59.6828 | 59.7137 | 59.6508 | 59.5676 | 62.2519 | 62.3078 | 61.9854 | 62.2508 | 0.14932 | 0.023574 | 0.006308 | 0.016183 | 0.077464 | 0.099312 | -0.030674 | 59.7149 | 59.7458 | 59.6828 | 59.5996 | 62.2839 | 62.3398 | 62.0174 | 62.2829 | -2.5691 | -2.3025 | -2.6011 | -2.3346
598.6406 | 122.2183 | -62.3016 | 59.8114 | 0.12185 | 0.000689 | -0.012 | -0.020438 | 0.036265 | 0.081005 | -0.053561 | 59.6782 | 59.7137 | 59.6554 | 59.5722 | 62.2473 | 62.317 | 61.9945 | 62.2554 | 0.15389 | 0.032732 | 0.020043 | 0.011605 | 0.068308 | 0.11305 | -0.021518 | 59.7103 | 59.7458 | 59.6874 | 59.6042 | 62.2793 | 62.349 | 62.0266 | 62.2874 | -2.5691 | -2.3163 | -2.5919 | -2.3392
600.3906 | 122.2183 | -62.2833 | 59.8434 | 0.12643 | -0.008469 | -0.016578 | -0.011281 | 0.045421 | 0.081005 | -0.053561 | 59.6828 | 59.7137 | 59.6599 | 59.5676 | 62.2519 | 62.3124 | 61.9762 | 62.26 | 0.15847 | 0.023574 | 0.015465 | 0.020762 | 0.077464 | 0.11305 | -0.021518 | 59.7149 | 59.7458 | 59.692 | 59.5996 | 62.2839 | 62.3444 | 62.0082 | 62.292 | -2.5691 | -2.2934 | -2.5919 | -2.3163
602.1406 | 122.2321 | -62.3108 | 59.7702 | 0.13101 | -0.00389 | -0.016578 | -0.01586 | 0.045421 | 0.076426 | -0.044405 | 59.692 | 59.7183 | 59.6554 | 59.5584 | 62.2473 | 62.317 | 61.9716 | 62.2508 | 0.16305 | 0.028153 | 0.015465 | 0.016183 | 0.077464 | 0.10847 | -0.012362 | 59.724 | 59.7504 | 59.6874 | 59.5905 | 62.2793 | 62.349 | 62.0037 | 62.2829 | -2.5553 | -2.2797 | -2.5919 | -2.3163
603.9062 | 122.2275 | -62.3108 | 59.7931 | 0.13101 | -0.00389 | -0.016578 | -0.01586 | 0.040843 | 0.081005 | -0.053561 | 59.6828 | 59.7137 | 59.6554 | 59.5676 | 62.2519 | 62.3078 | 62.0082 | 62.2508 | 0.16305 | 0.028153 | 0.015465 | 0.016183 | 0.072886 | 0.11305 | -0.021518 | 59.7149 | 59.7458 | 59.6874 | 59.5996 | 62.2839 | 62.3398 | 62.0403 | 62.2829 | -2.5691 | -2.3254 | -2.5965 | -2.3529
605.6562 | 122.3145 | -62.2879 | 59.7519 | 0.11727 | -0.00389 | -0.025735 | -0.020438 | 0.040843 | 0.071848 | -0.058139 | 59.6874 | 59.7183 | 59.6599 | 59.563 | 62.2519 | 62.317 | 61.9899 | 62.2463 | 0.14932 | 0.028153 | 0.006308 | 0.011605 | 0.072886 | 0.10389 | -0.026096 | 59.7194 | 59.7504 | 59.692 | 59.595 | 62.2839 | 62.349 | 62.022 | 62.2783 | -2.5645 | -2.3025 | -2.5919 | -2.33
607.3281 | 122.2687 | -62.2879 | 59.8618 | 0.12643 | -0.008469 | -0.012 | -0.01586 | 0.045421 | 0.076426 | -0.058139 | 59.6874 | 59.7092 | 59.6645 | 59.5676 | 62.2519 | 62.3078 | 61.967 | 62.2508 | 0.15847 | 0.023574 | 0.020043 | 0.016183 | 0.077464 | 0.10847 | -0.026096 | 59.7194 | 59.7412 | 59.6966 | 59.5996 | 62.2839 | 62.3398 | 61.9991 | 62.2829 | -2.5645 | -2.2797 | -2.5874 | -2.3025
609.0781 | 122.2733 | -62.2696 | 59.8297 | 0.13101 | 0.000689 | -0.016578 | -0.01586 | 0.045421 | 0.081005 | -0.048983 | 59.6874 | 59.7046 | 59.6599 | 59.5676 | 62.2565 | 62.3078 | 61.9854 | 62.2554 | 0.16305 | 0.032732 | 0.015465 | 0.016183 | 0.077464 | 0.11305 | -0.01694 | 59.7194 | 59.7366 | 59.692 | 59.5996 | 62.2885 | 62.3398 | 62.0174 | 62.2874 | -2.5691 | -2.298 | -2.5965 | -2.3254
610.75 | 122.2137 | -62.3016 | 59.8206 | 0.13101 | 0.000689 | -0.021157 | -0.020438 | 0.049999 | 0.081005 | -0.058139 | 59.692 | 59.7137 | 59.6599 | 59.563 | 62.2519 | 62.3078 | 61.9945 | 62.26 | 0.16305 | 0.032732 | 0.010886 | 0.011605 | 0.082042 | 0.11305 | -0.026096 | 59.724 | 59.7458 | 59.692 | 59.595 | 62.2839 | 62.3398 | 62.0266 | 62.292 | -2.5599 | -2.3025 | -2.5919 | -2.3346
612.5 | 122.3602 | -62.2742 | 59.7748 | 0.12185 | 0.000689 | -0.021157 | -0.020438 | 0.045421 | 0.071848 | -0.062717 | 59.6782 | 59.7137 | 59.6599 | 59.5722 | 62.2519 | 62.317 | 61.967 | 62.2554 | 0.15389 | 0.032732 | 0.010886 | 0.011605 | 0.077464 | 0.10389 | -0.030674 | 59.7103 | 59.7458 | 59.692 | 59.6042 | 62.2839 | 62.349 | 61.9991 | 62.2874 | -2.5736 | -2.2888 | -2.5919 | -2.3071
614.25 | 122.2366 | -62.3108 | 59.7885 | 0.12185 | -0.00389 | -0.016578 | -0.020438 | 0.049999 | 0.081005 | -0.053561 | 59.6782 | 59.7137 | 59.6599 | 59.5676 | 62.2519 | 62.3124 | 61.9487 | 62.2554 | 0.15389 | 0.028153 | 0.015465 | 0.011605 | 0.082042 | 0.11305 | -0.021518 | 59.7103 | 59.7458 | 59.692 | 59.5996 | 62.2839 | 62.3444 | 61.9808 | 62.2874 | -2.5736 | -2.2705 | -2.5919 | -2.2888
616 | 122.3511 | -62.2696 | 59.7702 | 0.12185 | -0.00389 | -0.012 | -0.01586 | 0.040843 | 0.071848 | -0.058139 | 59.6828 | 59.7229 | 59.6599 | 59.5676 | 62.2519 | 62.317 | 61.967 | 62.2554 | 0.15389 | 0.028153 | 0.020043 | 0.016183 | 0.072886 | 0.10389 | -0.026096 | 59.7149 | 59.7549 | 59.692 | 59.5996 | 62.2839 | 62.349 | 61.9991 | 62.2874 | -2.5691 | -2.2842 | -2.5919 | -2.3071
617.6875 | 122.2733 | -62.2925 | 59.8526 | 0.13101 | -0.008469 | -0.012 | -0.01586 | 0.045421 | 0.076426 | -0.053561 | 59.6782 | 59.7183 | 59.6599 | 59.563 | 62.2519 | 62.317 | 62.0037 | 62.26 | 0.16305 | 0.023574 | 0.020043 | 0.016183 | 0.077464 | 0.10847 | -0.021518 | 59.7103 | 59.7504 | 59.692 | 59.595 | 62.2839 | 62.349 | 62.0357 | 62.292 | -2.5736 | -2.3254 | -2.5919 | -2.3437
619.4531 | 122.3511 | -62.2467 | 59.761 | 0.11727 | -0.008469 | -0.016578 | -0.020438 | 0.049999 | 0.071848 | -0.058139 | 59.6828 | 59.7137 | 59.6508 | 59.5722 | 62.2519 | 62.317 | 61.9487 | 62.2508 | 0.14932 | 0.023574 | 0.015465 | 0.011605 | 0.082042 | 0.10389 | -0.026096 | 59.7149 | 59.7458 | 59.6828 | 59.6042 | 62.2839 | 62.349 | 61.9808 | 62.2829 | -2.5691 | -2.2659 | -2.6011 | -2.298
621.1406 | 122.2824 | -62.2604 | 59.8114 | 0.12643 | -0.008469 | -0.016578 | -0.025017 | 0.040843 | 0.071848 | -0.053561 | 59.6782 | 59.7137 | 59.6554 | 59.5722 | 62.2565 | 62.317 | 61.967 | 62.2554 | 0.15847 | 0.023574 | 0.015465 | 0.007026 | 0.072886 | 0.10389 | -0.021518 | 59.7103 | 59.7458 | 59.6874 | 59.6042 | 62.2885 | 62.349 | 61.9991 | 62.2874 | -2.5782 | -2.2888 | -2.6011 | -2.3117
622.8906 | 122.2229 | -62.2925 | 59.7977 | 0.12643 | 0.000689 | -0.007421 | -0.01586 | 0.045421 | 0.090161 | -0.053561 | 59.6874 | 59.7137 | 59.6645 | 59.5767 | 62.2519 | 62.3078 | 61.9945 | 62.2554 | 0.15847 | 0.032732 | 0.024622 | 0.016183 | 0.077464 | 0.1222 | -0.021518 | 59.7194 | 59.7458 | 59.6966 | 59.6088 | 62.2839 | 62.3398 | 62.0266 | 62.2874 | -2.5645 | -2.3071 | -2.5874 | -2.33
624.6406 | 122.3511 | -62.265 | 59.7839 | 0.12643 | 0.000689 | -0.016578 | -0.020438 | 0.045421 | 0.076426 | -0.067295 | 59.692 | 59.7137 | 59.6599 | 59.5676 | 62.2519 | 62.3078 | 61.9899 | 62.2554 | 0.15847 | 0.032732 | 0.015465 | 0.011605 | 0.077464 | 0.10847 | -0.035252 | 59.724 | 59.7458 | 59.692 | 59.5996 | 62.2839 | 62.3398 | 62.022 | 62.2874 | -2.5599 | -2.298 | -2.5919 | -2.33
626.3594 | 122.2137 | -62.2879 | 59.8297 | 0.12643 | -0.00389 | -0.016578 | -0.01586 | 0.040843 | 0.081005 | -0.058139 | 59.6874 | 59.7183 | 59.6645 | 59.5676 | 62.2519 | 62.3124 | 61.967 | 62.26 | 0.15847 | 0.028153 | 0.015465 | 0.016183 | 0.072886 | 0.11305 | -0.026096 | 59.7194 | 59.7504 | 59.6966 | 59.5996 | 62.2839 | 62.3444 | 61.9991 | 62.292 | -2.5645 | -2.2797 | -2.5874 | -2.3025
628.0625 | 122.3648 | -62.2559 | 59.761 | 0.12185 | -0.008469 | -0.030314 | -0.025017 | 0.040843 | 0.071848 | -0.062717 | 59.6828 | 59.7092 | 59.6645 | 59.563 | 62.2565 | 62.3124 | 61.9945 | 62.26 | 0.15389 | 0.023574 | 0.001729 | 0.007026 | 0.072886 | 0.10389 | -0.030674 | 59.7149 | 59.7412 | 59.6966 | 59.595 | 62.2885 | 62.3444 | 62.0266 | 62.292 | -2.5736 | -2.3117 | -2.5919 | -2.33
629.7969 | 122.2733 | -62.2787 | 59.816 | 0.12643 | 0.000689 | -0.016578 | -0.01586 | 0.049999 | 0.067269 | -0.058139 | 59.6828 | 59.7092 | 59.6599 | 59.5722 | 62.2519 | 62.3124 | 61.9533 | 62.2554 | 0.15847 | 0.032732 | 0.015465 | 0.016183 | 0.082042 | 0.099312 | -0.026096 | 59.7149 | 59.7412 | 59.692 | 59.6042 | 62.2839 | 62.3444 | 61.9854 | 62.2874 | -2.5691 | -2.2705 | -2.5919 | -2.2934
631.5312 | 122.3328 | -62.265 | 59.7702 | 0.13101 | 0.000689 | -0.016578 | -0.025017 | 0.040843 | 0.076426 | -0.053561 | 59.6782 | 59.7183 | 59.6645 | 59.5584 | 62.2519 | 62.3124 | 61.9716 | 62.2554 | 0.16305 | 0.032732 | 0.015465 | 0.007026 | 0.072886 | 0.10847 | -0.021518 | 59.7103 | 59.7504 | 59.6966 | 59.5905 | 62.2839 | 62.3444 | 62.0037 | 62.2874 | -2.5736 | -2.2934 | -2.5874 | -2.3071
633.2812 | 122.2275 | -62.2925 | 59.8022 | 0.12185 | 0.000689 | -0.012 | -0.01586 | 0.049999 | 0.076426 | -0.053561 | 59.6874 | 59.7183 | 59.6691 | 59.5722 | 62.2519 | 62.3124 | 61.967 | 62.2554 | 0.15389 | 0.032732 | 0.020043 | 0.016183 | 0.082042 | 0.10847 | -0.021518 | 59.7194 | 59.7504 | 59.7011 | 59.6042 | 62.2839 | 62.3444 | 61.9991 | 62.2874 | -2.5645 | -2.2797 | -2.5828 | -2.298
635.0469 | 122.2366 | -62.3108 | 59.816 | 0.12185 | -0.008469 | -0.012 | -0.020438 | 0.045421 | 0.076426 | -0.048983 | 59.6874 | 59.7183 | 59.6599 | 59.5722 | 62.2565 | 62.317 | 61.9533 | 62.2508 | 0.15389 | 0.023574 | 0.020043 | 0.011605 | 0.077464 | 0.10847 | -0.01694 | 59.7194 | 59.7504 | 59.692 | 59.6042 | 62.2885 | 62.349 | 61.9854 | 62.2829 | -2.5691 | -2.2659 | -2.5965 | -2.2934
636.7969 | 122.3465 | -62.2604 | 59.7336 | 0.12185 | 0.000689 | -0.012 | -0.020438 | 0.040843 | 0.081005 | -0.058139 | 59.6874 | 59.7183 | 59.6599 | 59.5722 | 62.2565 | 62.3078 | 61.9625 | 62.2463 | 0.15389 | 0.032732 | 0.020043 | 0.011605 | 0.072886 | 0.11305 | -0.026096 | 59.7194 | 59.7504 | 59.692 | 59.6042 | 62.2885 | 62.3398 | 61.9945 | 62.2783 | -2.5691 | -2.2751 | -2.5965 | -2.3025
638.4844 | 122.2229 | -62.2879 | 59.8022 | 0.13101 | -0.008469 | -0.007421 | -0.01586 | 0.054577 | 0.071848 | -0.058139 | 59.6874 | 59.7137 | 59.6691 | 59.5676 | 62.2519 | 62.317 | 61.9854 | 62.2554 | 0.16305 | 0.023574 | 0.024622 | 0.016183 | 0.08662 | 0.10389 | -0.026096 | 59.7194 | 59.7458 | 59.7011 | 59.5996 | 62.2839 | 62.349 | 62.0174 | 62.2874 | -2.5645 | -2.298 | -2.5828 | -2.3163
640.2188 | 122.2778 | -62.2787 | 59.8343 | 0.12185 | -0.00389 | -0.021157 | -0.020438 | 0.054577 | 0.071848 | -0.058139 | 59.692 | 59.7137 | 59.6599 | 59.5676 | 62.2565 | 62.3124 | 61.9579 | 62.26 | 0.15389 | 0.028153 | 0.010886 | 0.011605 | 0.08662 | 0.10389 | -0.026096 | 59.724 | 59.7458 | 59.692 | 59.5996 | 62.2885 | 62.3444 | 61.9899 | 62.292 | -2.5645 | -2.2659 | -2.5965 | -2.298
641.9531 | 122.2046 | -62.3108 | 59.8068 | 0.13101 | -0.00389 | -0.016578 | -0.020438 | 0.045421 | 0.081005 | -0.058139 | 59.6874 | 59.7183 | 59.6691 | 59.5676 | 62.2565 | 62.3215 | 61.9625 | 62.2554 | 0.16305 | 0.028153 | 0.015465 | 0.011605 | 0.077464 | 0.11305 | -0.026096 | 59.7194 | 59.7504 | 59.7011 | 59.5996 | 62.2885 | 62.3536 | 61.9945 | 62.2874 | -2.5691 | -2.2751 | -2.5874 | -2.2934
643.7031 | 122.3648 | -62.2604 | 59.7519 | 0.12643 | -0.008469 | -0.021157 | -0.011281 | 0.045421 | 0.071848 | -0.062717 | 59.6828 | 59.7137 | 59.6554 | 59.5722 | 62.2519 | 62.317 | 61.9487 | 62.2508 | 0.15847 | 0.023574 | 0.010886 | 0.020762 | 0.077464 | 0.10389 | -0.030674 | 59.7149 | 59.7458 | 59.6874 | 59.6042 | 62.2839 | 62.349 | 61.9808 | 62.2829 | -2.5691 | -2.2659 | -2.5965 | -2.2934
645.3906 | 122.2275 | -62.3016 | 59.8251 | 0.12643 | -0.008469 | -0.012 | -0.01586 | 0.045421 | 0.076426 | -0.062717 | 59.6874 | 59.7183 | 59.6599 | 59.5676 | 62.2565 | 62.317 | 61.9533 | 62.2554 | 0.15847 | 0.023574 | 0.020043 | 0.016183 | 0.077464 | 0.10847 | -0.030674 | 59.7194 | 59.7504 | 59.692 | 59.5996 | 62.2885 | 62.349 | 61.9854 | 62.2874 | -2.5691 | -2.2659 | -2.5965 | -2.2934
647.1406 | 122.1909 | -62.3154 | 59.816 | 0.13101 | -0.00389 | -0.016578 | -0.01586 | 0.045421 | 0.081005 | -0.053561 | 59.6828 | 59.7137 | 59.6599 | 59.5722 | 62.261 | 62.3215 | 61.9442 | 62.2554 | 0.16305 | 0.028153 | 0.015465 | 0.016183 | 0.077464 | 0.11305 | -0.021518 | 59.7149 | 59.7458 | 59.692 | 59.6042 | 62.2931 | 62.3536 | 61.9762 | 62.2874 | -2.5782 | -2.2613 | -2.6011 | -2.2842
648.8438 | 122.2183 | -62.2879 | 59.8389 | 0.12643 | -0.00389 | -0.021157 | -0.01586 | 0.045421 | 0.081005 | -0.058139 | 59.6874 | 59.7137 | 59.6645 | 59.5767 | 62.2565 | 62.3215 | 61.9487 | 62.26 | 0.15847 | 0.028153 | 0.010886 | 0.016183 | 0.077464 | 0.11305 | -0.026096 | 59.7194 | 59.7458 | 59.6966 | 59.6088 | 62.2885 | 62.3536 | 61.9808 | 62.292 | -2.5691 | -2.2613 | -2.5919 | -2.2842
650.5781 | 122.2595 | -62.2833 | 59.8572 | 0.12185 | -0.00389 | -0.016578 | -0.01586 | 0.045421 | 0.081005 | -0.053561 | 59.692 | 59.7183 | 59.6554 | 59.5767 | 62.261 | 62.3215 | 61.9808 | 62.2554 | 0.15389 | 0.028153 | 0.015465 | 0.016183 | 0.077464 | 0.11305 | -0.021518 | 59.724 | 59.7504 | 59.6874 | 59.6088 | 62.2931 | 62.3536 | 62.0128 | 62.2874 | -2.5691 | -2.2888 | -2.6057 | -2.3254
652.25 | 122.3602 | -62.2696 | 59.7427 | 0.11727 | 0.000689 | -0.021157 | -0.025017 | 0.049999 | 0.067269 | -0.058139 | 59.6874 | 59.7092 | 59.6645 | 59.5722 | 62.2565 | 62.317 | 61.9487 | 62.26 | 0.14932 | 0.032732 | 0.010886 | 0.007026 | 0.082042 | 0.099312 | -0.026096 | 59.7194 | 59.7412 | 59.6966 | 59.6042 | 62.2885 | 62.349 | 61.9808 | 62.292 | -2.5691 | -2.2613 | -2.5919 | -2.2842
654 | 122.2275 | -62.3016 | 59.7977 | 0.12643 | 0.000689 | -0.016578 | -0.01586 | 0.045421 | 0.085583 | -0.053561 | 59.6874 | 59.7092 | 59.6645 | 59.563 | 62.2565 | 62.3078 | 61.9533 | 62.2554 | 0.15847 | 0.032732 | 0.015465 | 0.016183 | 0.077464 | 0.11763 | -0.021518 | 59.7194 | 59.7412 | 59.6966 | 59.595 | 62.2885 | 62.3398 | 61.9854 | 62.2874 | -2.5691 | -2.2659 | -2.5919 | -2.2888
655.7344 | 122.2 | -62.3154 | 59.7931 | 0.12643 | -0.00389 | -0.016578 | -0.011281 | 0.049999 | 0.076426 | -0.053561 | 59.692 | 59.7137 | 59.6691 | 59.5722 | 62.2473 | 62.3124 | 61.9625 | 62.2554 | 0.15847 | 0.028153 | 0.015465 | 0.020762 | 0.082042 | 0.10847 | -0.021518 | 59.724 | 59.7458 | 59.7011 | 59.6042 | 62.2793 | 62.3444 | 61.9945 | 62.2874 | -2.5553 | -2.2705 | -2.5782 | -2.2934
657.4375 | 122.3328 | -62.2833 | 59.7565 | 0.12643 | -0.008469 | -0.016578 | -0.011281 | 0.045421 | 0.071848 | -0.058139 | 59.6874 | 59.7183 | 59.6599 | 59.5767 | 62.2519 | 62.317 | 61.9854 | 62.2646 | 0.15847 | 0.023574 | 0.015465 | 0.020762 | 0.077464 | 0.10389 | -0.026096 | 59.7194 | 59.7504 | 59.692 | 59.6088 | 62.2839 | 62.349 | 62.0174 | 62.2966 | -2.5645 | -2.298 | -2.5919 | -2.3254
659.1875 | 122.3236 | -62.2559 | 59.7931 | 0.12185 | 0.000689 | -0.021157 | -0.01586 | 0.045421 | 0.076426 | -0.062717 | 59.692 | 59.7183 | 59.6645 | 59.5767 | 62.2565 | 62.3124 | 61.9396 | 62.26 | 0.15389 | 0.032732 | 0.010886 | 0.016183 | 0.077464 | 0.10847 | -0.030674 | 59.724 | 59.7504 | 59.6966 | 59.6088 | 62.2885 | 62.3444 | 61.9716 | 62.292 | -2.5645 | -2.2476 | -2.5919 | -2.2751
660.875 | 122.3145 | -62.2971 | 59.729 | 0.13101 | -0.00389 | -0.016578 | -0.020438 | 0.045421 | 0.076426 | -0.053561 | 59.6828 | 59.7229 | 59.6599 | 59.563 | 62.2565 | 62.3124 | 61.9487 | 62.2508 | 0.16305 | 0.028153 | 0.015465 | 0.011605 | 0.077464 | 0.10847 | -0.021518 | 59.7149 | 59.7549 | 59.692 | 59.595 | 62.2885 | 62.3444 | 61.9808 | 62.2829 | -2.5736 | -2.2659 | -2.5965 | -2.2888
662.625 | 122.3282 | -62.2925 | 59.761 | 0.12643 | -0.00389 | -0.016578 | -0.01586 | 0.045421 | 0.071848 | -0.062717 | 59.692 | 59.7137 | 59.6691 | 59.5676 | 62.2565 | 62.3124 | 61.9396 | 62.26 | 0.15847 | 0.028153 | 0.015465 | 0.016183 | 0.077464 | 0.10389 | -0.030674 | 59.724 | 59.7458 | 59.7011 | 59.5996 | 62.2885 | 62.3444 | 61.9716 | 62.292 | -2.5645 | -2.2476 | -2.5874 | -2.2705
664.3281 | 122.3648 | -62.2879 | 59.7382 | 0.12185 | -0.00389 | -0.021157 | -0.020438 | 0.045421 | 0.076426 | -0.058139 | 59.6782 | 59.7229 | 59.6599 | 59.5676 | 62.261 | 62.3078 | 61.935 | 62.2554 | 0.15389 | 0.028153 | 0.010886 | 0.011605 | 0.077464 | 0.10847 | -0.026096 | 59.7103 | 59.7549 | 59.692 | 59.5996 | 62.2931 | 62.3398 | 61.967 | 62.2874 | -2.5828 | -2.2568 | -2.6011 | -2.2751
666.0625 | 122.2229 | -62.2879 | 59.8114 | 0.13101 | -0.00389 | -0.012 | -0.020438 | 0.045421 | 0.076426 | -0.053561 | 59.6965 | 59.7092 | 59.6645 | 59.5676 | 62.2519 | 62.317 | 61.9396 | 62.2554 | 0.16305 | 0.028153 | 0.020043 | 0.011605 | 0.077464 | 0.10847 | -0.021518 | 59.7286 | 59.7412 | 59.6966 | 59.5996 | 62.2839 | 62.349 | 61.9716 | 62.2874 | -2.5553 | -2.243 | -2.5874 | -2.2751
667.8125 | 122.2046 | -62.3062 | 59.8068 | 0.13559 | -0.00389 | -0.016578 | -0.01586 | 0.054577 | 0.076426 | -0.058139 | 59.692 | 59.7183 | 59.6599 | 59.5722 | 62.2473 | 62.3078 | 61.9487 | 62.2508 | 0.16763 | 0.028153 | 0.015465 | 0.016183 | 0.08662 | 0.10847 | -0.026096 | 59.724 | 59.7504 | 59.692 | 59.6042 | 62.2793 | 62.3398 | 61.9808 | 62.2829 | -2.5553 | -2.2568 | -2.5874 | -2.2888
669.5 | 122.2412 | -62.2742 | 59.7931 | 0.11727 | 0.005267 | -0.021157 | -0.020438 | 0.049999 | 0.067269 | -0.048983 | 59.6828 | 59.7137 | 59.6691 | 59.5767 | 62.2519 | 62.3124 | 61.9533 | 62.2554 | 0.14932 | 0.03731 | 0.010886 | 0.011605 | 0.082042 | 0.099312 | -0.01694 | 59.7149 | 59.7458 | 59.7011 | 59.6088 | 62.2839 | 62.3444 | 61.9854 | 62.2874 | -2.5691 | -2.2705 | -2.5828 | -2.2842
671.1719 | 122.3328 | -62.3062 | 59.7336 | 0.12643 | -0.008469 | -0.016578 | -0.01586 | 0.054577 | 0.076426 | -0.053561 | 59.6828 | 59.7092 | 59.6599 | 59.5813 | 62.2565 | 62.3215 | 61.9579 | 62.2554 | 0.15847 | 0.023574 | 0.015465 | 0.016183 | 0.08662 | 0.10847 | -0.021518 | 59.7149 | 59.7412 | 59.692 | 59.6134 | 62.2885 | 62.3536 | 61.9899 | 62.2874 | -2.5736 | -2.2751 | -2.5965 | -2.298
672.9219 | 122.3511 | -62.2421 | 59.7748 | 0.12185 | 0.000689 | -0.016578 | -0.020438 | 0.040843 | 0.071848 | -0.058139 | 59.6874 | 59.7229 | 59.6554 | 59.5676 | 62.2565 | 62.3124 | 61.9762 | 62.2554 | 0.15389 | 0.032732 | 0.015465 | 0.011605 | 0.072886 | 0.10389 | -0.026096 | 59.7194 | 59.7549 | 59.6874 | 59.5996 | 62.2885 | 62.3444 | 62.0082 | 62.2874 | -2.5691 | -2.2888 | -2.6011 | -2.3208
674.6094 | 122.2824 | -62.2787 | 59.8251 | 0.12185 | -0.013048 | -0.021157 | -0.025017 | 0.045421 | 0.076426 | -0.058139 | 59.692 | 59.7137 | 59.6599 | 59.5767 | 62.261 | 62.3124 | 61.9625 | 62.26 | 0.15389 | 0.018995 | 0.010886 | 0.007026 | 0.077464 | 0.10847 | -0.026096 | 59.724 | 59.7458 | 59.692 | 59.6088 | 62.2931 | 62.3444 | 61.9945 | 62.292 | -2.5691 | -2.2705 | -2.6011 | -2.3025
676.3438 | 122.319 | -62.2787 | 59.761 | 0.12185 | -0.00389 | -0.021157 | -0.020438 | 0.049999 | 0.076426 | -0.058139 | 59.6874 | 59.7137 | 59.6645 | 59.5722 | 62.2519 | 62.3124 | 61.9762 | 62.2554 | 0.15389 | 0.028153 | 0.010886 | 0.011605 | 0.082042 | 0.10847 | -0.026096 | 59.7194 | 59.7458 | 59.6966 | 59.6042 | 62.2839 | 62.3444 | 62.0082 | 62.2874 | -2.5645 | -2.2888 | -2.5874 | -2.3117
678.0781 | 122.2275 | -62.2925 | 59.8251 | 0.12643 | 0.000689 | -0.021157 | -0.01586 | 0.045421 | 0.076426 | -0.058139 | 59.6828 | 59.7137 | 59.6691 | 59.5767 | 62.2519 | 62.3215 | 61.9533 | 62.2508 | 0.15847 | 0.032732 | 0.010886 | 0.016183 | 0.077464 | 0.10847 | -0.026096 | 59.7149 | 59.7458 | 59.7011 | 59.6088 | 62.2839 | 62.3536 | 61.9854 | 62.2829 | -2.5691 | -2.2705 | -2.5828 | -2.2842
679.7656 | 122.2092 | -62.2971 | 59.8114 | 0.12643 | 0.000689 | -0.021157 | -0.01586 | 0.049999 | 0.081005 | -0.053561 | 59.6965 | 59.7183 | 59.6599 | 59.5722 | 62.2473 | 62.3078 | 61.9396 | 62.2508 | 0.15847 | 0.032732 | 0.010886 | 0.016183 | 0.082042 | 0.11305 | -0.021518 | 59.7286 | 59.7504 | 59.692 | 59.6042 | 62.2793 | 62.3398 | 61.9716 | 62.2829 | -2.5508 | -2.243 | -2.5874 | -2.2796
681.5 | 122.2183 | -62.3016 | 59.8114 | 0.13101 | 0.005267 | -0.012 | -0.01586 | 0.045421 | 0.081005 | -0.048983 | 59.6874 | 59.7183 | 59.6691 | 59.5722 | 62.2565 | 62.317 | 61.9487 | 62.2508 | 0.16305 | 0.03731 | 0.020043 | 0.016183 | 0.077464 | 0.11305 | -0.01694 | 59.7194 | 59.7504 | 59.7011 | 59.6042 | 62.2885 | 62.349 | 61.9808 | 62.2829 | -2.5691 | -2.2613 | -2.5874 | -2.2796
683.2344 | 122.3053 | -62.2879 | 59.7473 | 0.12643 | 0.005267 | -0.021157 | -0.011281 | 0.045421 | 0.076426 | -0.058139 | 59.692 | 59.7229 | 59.6599 | 59.5722 | 62.2473 | 62.3078 | 61.9442 | 62.2554 | 0.15847 | 0.03731 | 0.010886 | 0.020762 | 0.077464 | 0.10847 | -0.026096 | 59.724 | 59.7549 | 59.692 | 59.6042 | 62.2793 | 62.3398 | 61.9762 | 62.2874 | -2.5553 | -2.2522 | -2.5874 | -2.2842
684.9844 | 122.2229 | -62.2833 | 59.8114 | 0.12643 | 0.005267 | -0.012 | -0.011281 | 0.049999 | 0.085583 | -0.053561 | 59.6828 | 59.7183 | 59.6645 | 59.5676 | 62.2565 | 62.3124 | 61.9442 | 62.26 | 0.15847 | 0.03731 | 0.020043 | 0.020762 | 0.082042 | 0.11763 | -0.021518 | 59.7149 | 59.7504 | 59.6966 | 59.5996 | 62.2885 | 62.3444 | 61.9762 | 62.292 | -2.5736 | -2.2613 | -2.5919 | -2.2796
686.7188 | 122.2733 | -62.2696 | 59.8251 | 0.12643 | -0.00389 | -0.016578 | -0.020438 | 0.054577 | 0.085583 | -0.058139 | 59.692 | 59.7137 | 59.6691 | 59.5767 | 62.2565 | 62.3124 | 61.9396 | 62.26 | 0.15847 | 0.028153 | 0.015465 | 0.011605 | 0.08662 | 0.11763 | -0.026096 | 59.724 | 59.7458 | 59.7011 | 59.6088 | 62.2885 | 62.3444 | 61.9716 | 62.292 | -2.5645 | -2.2476 | -2.5874 | -2.2705
688.4062 | 122.2961 | -62.3016 | 59.7931 | 0.13101 | -0.008469 | -0.021157 | -0.020438 | 0.040843 | 0.071848 | -0.053561 | 59.6828 | 59.7183 | 59.6599 | 59.563 | 62.2519 | 62.3124 | 61.9533 | 62.26 | 0.16305 | 0.023574 | 0.010886 | 0.011605 | 0.072886 | 0.10389 | -0.021518 | 59.7149 | 59.7504 | 59.692 | 59.595 | 62.2839 | 62.3444 | 61.9854 | 62.292 | -2.5691 | -2.2705 | -2.5919 | -2.2934
690.1562 | 122.3145 | -62.2513 | 59.816 | 0.12643 | 0.000689 | -0.016578 | -0.01586 | 0.040843 | 0.076426 | -0.062717 | 59.6782 | 59.7183 | 59.6645 | 59.5767 | 62.261 | 62.317 | 61.9533 | 62.2554 | 0.15847 | 0.032732 | 0.015465 | 0.016183 | 0.072886 | 0.10847 | -0.030674 | 59.7103 | 59.7504 | 59.6966 | 59.6088 | 62.2931 | 62.349 | 61.9854 | 62.2874 | -2.5828 | -2.2751 | -2.5965 | -2.2888
691.8906 | 122.3373 | -62.2696 | 59.8114 | 0.12643 | -0.00389 | -0.025735 | -0.025017 | 0.040843 | 0.076426 | -0.053561 | 59.6965 | 59.7229 | 59.6599 | 59.5722 | 62.2519 | 62.3078 | 61.9487 | 62.2508 | 0.15847 | 0.028153 | 0.006308 | 0.007026 | 0.072886 | 0.10847 | -0.021518 | 59.7286 | 59.7549 | 59.692 | 59.6042 | 62.2839 | 62.3398 | 61.9808 | 62.2829 | -2.5553 | -2.2522 | -2.5919 | -2.2888
693.5781 | 122.2183 | -62.2833 | 59.7839 | 0.12643 | 0.000689 | -0.016578 | -0.011281 | 0.049999 | 0.071848 | -0.048983 | 59.692 | 59.7183 | 59.6691 | 59.5767 | 62.2519 | 62.3078 | 61.9396 | 62.26 | 0.15847 | 0.032732 | 0.015465 | 0.020762 | 0.082042 | 0.10389 | -0.01694 | 59.724 | 59.7504 | 59.7011 | 59.6088 | 62.2839 | 62.3398 | 61.9716 | 62.292 | -2.5599 | -2.2476 | -2.5828 | -2.2705
695.3281 | 122.2137 | -62.2879 | 59.8297 | 0.12643 | 0.009846 | -0.021157 | -0.020438 | 0.054577 | 0.071848 | -0.058139 | 59.6828 | 59.7092 | 59.6691 | 59.5767 | 62.2519 | 62.317 | 61.9625 | 62.26 | 0.15847 | 0.041889 | 0.010886 | 0.011605 | 0.08662 | 0.10389 | -0.026096 | 59.7149 | 59.7412 | 59.7011 | 59.6088 | 62.2839 | 62.349 | 61.9945 | 62.292 | -2.5691 | -2.2797 | -2.5828 | -2.2934
697.0625 | 122.2504 | -62.2879 | 59.8389 | 0.12185 | -0.00389 | -0.021157 | -0.020438 | 0.049999 | 0.076426 | -0.058139 | 59.6828 | 59.7137 | 59.6645 | 59.5767 | 62.261 | 62.3124 | 61.9442 | 62.26 | 0.15389 | 0.028153 | 0.010886 | 0.011605 | 0.082042 | 0.10847 | -0.026096 | 59.7149 | 59.7458 | 59.6966 | 59.6088 | 62.2931 | 62.3444 | 61.9762 | 62.292 | -2.5782 | -2.2613 | -2.5965 | -2.2796
698.7344 | 122.3145 | -62.3062 | 59.7336 | 0.13101 | 0.005267 | -0.021157 | -0.01586 | 0.045421 | 0.076426 | -0.058139 | 59.6828 | 59.7137 | 59.6691 | 59.5722 | 62.2565 | 62.317 | 61.967 | 62.26 | 0.16305 | 0.03731 | 0.010886 | 0.016183 | 0.077464 | 0.10847 | -0.026096 | 59.7149 | 59.7458 | 59.7011 | 59.6042 | 62.2885 | 62.349 | 61.9991 | 62.292 | -2.5736 | -2.2842 | -2.5874 | -2.298
700.4844 | 122.3373 | -62.2375 | 59.8022 | 0.12185 | -0.00389 | -0.016578 | -0.01586 | 0.049999 | 0.076426 | -0.058139 | 59.6782 | 59.7229 | 59.6645 | 59.5767 | 62.2519 | 62.3124 | 61.9625 | 62.2554 | 0.15389 | 0.028153 | 0.015465 | 0.016183 | 0.082042 | 0.10847 | -0.026096 | 59.7103 | 59.7549 | 59.6966 | 59.6088 | 62.2839 | 62.3444 | 61.9945 | 62.2874 | -2.5736 | -2.2842 | -2.5874 | -2.298
702.2344 | 122.2778 | -62.2833 | 59.8297 | 0.12643 | 0.000689 | -0.016578 | -0.020438 | 0.049999 | 0.076426 | -0.053561 | 59.6828 | 59.7137 | 59.6737 | 59.5767 | 62.2519 | 62.3124 | 61.9487 | 62.26 | 0.15847 | 0.032732 | 0.015465 | 0.011605 | 0.082042 | 0.10847 | -0.021518 | 59.7149 | 59.7458 | 59.7057 | 59.6088 | 62.2839 | 62.3444 | 61.9808 | 62.292 | -2.5691 | -2.2659 | -2.5782 | -2.2751
703.9844 | 122.2641 | -62.2559 | 59.8251 | 0.13559 | -0.008469 | -0.021157 | -0.01586 | 0.049999 | 0.085583 | -0.058139 | 59.692 | 59.7229 | 59.6599 | 59.5676 | 62.2519 | 62.3215 | 61.9533 | 62.26 | 0.16763 | 0.023574 | 0.010886 | 0.016183 | 0.082042 | 0.11763 | -0.026096 | 59.724 | 59.7549 | 59.692 | 59.5996 | 62.2839 | 62.3536 | 61.9854 | 62.292 | -2.5599 | -2.2613 | -2.5919 | -2.2934
705.6719 | 122.3648 | -62.2467 | 59.7656 | 0.12185 | 0.005267 | -0.016578 | -0.025017 | 0.045421 | 0.071848 | -0.058139 | 59.6874 | 59.7275 | 59.6599 | 59.5767 | 62.2565 | 62.3124 | 61.9533 | 62.26 | 0.15389 | 0.03731 | 0.015465 | 0.007026 | 0.077464 | 0.10389 | -0.026096 | 59.7194 | 59.7595 | 59.692 | 59.6088 | 62.2885 | 62.3444 | 61.9854 | 62.292 | -2.5691 | -2.2659 | -2.5965 | -2.2934
707.4062 | 122.2275 | -62.2971 | 59.8434 | 0.12643 | 0.000689 | -0.025735 | -0.020438 | 0.045421 | 0.081005 | -0.058139 | 59.6874 | 59.7137 | 59.6691 | 59.5767 | 62.261 | 62.3124 | 61.9533 | 62.2554 | 0.15847 | 0.032732 | 0.006308 | 0.011605 | 0.077464 | 0.11305 | -0.026096 | 59.7194 | 59.7458 | 59.7011 | 59.6088 | 62.2931 | 62.3444 | 61.9854 | 62.2874 | -2.5736 | -2.2659 | -2.5919 | -2.2842
709.1562 | 122.2412 | -62.3062 | 59.8068 | 0.13101 | 0.009846 | -0.021157 | -0.01586 | 0.049999 | 0.071848 | -0.053561 | 59.6874 | 59.7137 | 59.6599 | 59.5767 | 62.2565 | 62.3124 | 61.935 | 62.2554 | 0.16305 | 0.041889 | 0.010886 | 0.016183 | 0.082042 | 0.10389 | -0.021518 | 59.7194 | 59.7458 | 59.692 | 59.6088 | 62.2885 | 62.3444 | 61.967 | 62.2874 | -2.5691 | -2.2476 | -2.5965 | -2.2751
710.9062 | 122.3373 | -62.2467 | 59.8068 | 0.12185 | 0.005267 | -0.016578 | -0.020438 | 0.049999 | 0.076426 | -0.058139 | 59.692 | 59.7137 | 59.6645 | 59.5676 | 62.2565 | 62.3215 | 61.9487 | 62.2554 | 0.15389 | 0.03731 | 0.015465 | 0.011605 | 0.082042 | 0.10847 | -0.026096 | 59.724 | 59.7458 | 59.6966 | 59.5996 | 62.2885 | 62.3536 | 61.9808 | 62.2874 | -2.5645 | -2.2568 | -2.5919 | -2.2842
712.5938 | 122.2229 | -62.2742 | 59.8389 | 0.12185 | 0.005267 | -0.025735 | -0.011281 | 0.049999 | 0.081005 | -0.053561 | 59.692 | 59.7137 | 59.6691 | 59.5722 | 62.2565 | 62.3124 | 61.9533 | 62.26 | 0.15389 | 0.03731 | 0.006308 | 0.020762 | 0.082042 | 0.11305 | -0.021518 | 59.724 | 59.7458 | 59.7011 | 59.6042 | 62.2885 | 62.3444 | 61.9854 | 62.292 | -2.5645 | -2.2613 | -2.5874 | -2.2842
714.3281 | 122.2321 | -62.2833 | 59.8618 | 0.12643 | 0.005267 | -0.016578 | -0.025017 | 0.049999 | 0.081005 | -0.048983 | 59.6874 | 59.7183 | 59.6645 | 59.5676 | 62.2519 | 62.317 | 61.9442 | 62.2554 | 0.15847 | 0.03731 | 0.015465 | 0.007026 | 0.082042 | 0.11305 | -0.01694 | 59.7194 | 59.7504 | 59.6966 | 59.5996 | 62.2839 | 62.349 | 61.9762 | 62.2874 | -2.5645 | -2.2568 | -2.5874 | -2.2796
716.0781 | 122.319 | -62.2925 | 59.7885 | 0.12643 | 0.000689 | -0.021157 | -0.020438 | 0.045421 | 0.076426 | -0.062717 | 59.6828 | 59.7183 | 59.6691 | 59.5722 | 62.2565 | 62.3124 | 61.9442 | 62.2508 | 0.15847 | 0.032732 | 0.010886 | 0.011605 | 0.077464 | 0.10847 | -0.030674 | 59.7149 | 59.7504 | 59.7011 | 59.6042 | 62.2885 | 62.3444 | 61.9762 | 62.2829 | -2.5736 | -2.2613 | -2.5874 | -2.2751
717.7656 | 122.2595 | -62.2879 | 59.8022 | 0.13101 | 0.005267 | -0.012 | -0.011281 | 0.054577 | 0.076426 | -0.058139 | 59.692 | 59.7229 | 59.6645 | 59.5767 | 62.2519 | 62.3124 | 61.9396 | 62.2646 | 0.16305 | 0.03731 | 0.020043 | 0.020762 | 0.08662 | 0.10847 | -0.026096 | 59.724 | 59.7549 | 59.6966 | 59.6088 | 62.2839 | 62.3444 | 61.9716 | 62.2966 | -2.5599 | -2.2476 | -2.5874 | -2.2751
719.5 | 122.374 | -62.2787 | 59.7794 | 0.13101 | 0.005267 | -0.025735 | -0.011281 | 0.045421 | 0.071848 | -0.053561 | 59.6874 | 59.7229 | 59.6645 | 59.5676 | 62.2519 | 62.317 | 61.9533 | 62.2646 | 0.16305 | 0.03731 | 0.006308 | 0.020762 | 0.077464 | 0.10389 | -0.021518 | 59.7194 | 59.7549 | 59.6966 | 59.5996 | 62.2839 | 62.349 | 61.9854 | 62.2966 | -2.5645 | -2.2659 | -2.5874 | -2.2888
721.2344 | 122.3465 | -62.2696 | 59.7565 | 0.12185 | -0.00389 | -0.021157 | -0.006703 | 0.045421 | 0.076426 | -0.058139 | 59.6874 | 59.7183 | 59.6645 | 59.5722 | 62.2565 | 62.3215 | 61.9533 | 62.26 | 0.15389 | 0.028153 | 0.010886 | 0.02534 | 0.077464 | 0.10847 | -0.026096 | 59.7194 | 59.7504 | 59.6966 | 59.6042 | 62.2885 | 62.3536 | 61.9854 | 62.292 | -2.5691 | -2.2659 | -2.5919 | -2.2888
722.9844 | 122.3511 | -62.2696 | 59.7748 | 0.13559 | -0.008469 | -0.021157 | -0.01586 | 0.045421 | 0.067269 | -0.058139 | 59.6874 | 59.7229 | 59.6691 | 59.5722 | 62.2519 | 62.3078 | 61.967 | 62.26 | 0.16763 | 0.023574 | 0.010886 | 0.016183 | 0.077464 | 0.099312 | -0.026096 | 59.7194 | 59.7549 | 59.7011 | 59.6042 | 62.2839 | 62.3398 | 61.9991 | 62.292 | -2.5645 | -2.2797 | -2.5828 | -2.298
724.6719 | 122.3694 | -62.2559 | 59.7794 | 0.13101 | 0.009846 | -0.012 | -0.020438 | 0.049999 | 0.071848 | -0.058139 | 59.6828 | 59.7229 | 59.6645 | 59.5767 | 62.2565 | 62.3124 | 61.9487 | 62.26 | 0.16305 | 0.041889 | 0.020043 | 0.011605 | 0.082042 | 0.10389 | -0.026096 | 59.7149 | 59.7549 | 59.6966 | 59.6088 | 62.2885 | 62.3444 | 61.9808 | 62.292 | -2.5736 | -2.2659 | -2.5919 | -2.2842
726.4062 | 122.2961 | -62.2559 | 59.8251 | 0.12185 | 0.000689 | -0.021157 | -0.01586 | 0.049999 | 0.071848 | -0.058139 | 59.6874 | 59.7183 | 59.6691 | 59.5722 | 62.2565 | 62.3124 | 61.9579 | 62.26 | 0.15389 | 0.032732 | 0.010886 | 0.016183 | 0.082042 | 0.10389 | -0.026096 | 59.7194 | 59.7504 | 59.7011 | 59.6042 | 62.2885 | 62.3444 | 61.9899 | 62.292 | -2.5691 | -2.2705 | -2.5874 | -2.2888
728.1406 | 122.2778 | -62.2833 | 59.816 | 0.13101 | 0.005267 | -0.016578 | -0.01586 | 0.045421 | 0.081005 | -0.058139 | 59.6874 | 59.7275 | 59.6645 | 59.5722 | 62.2519 | 62.3124 | 61.9533 | 62.26 | 0.16305 | 0.03731 | 0.015465 | 0.016183 | 0.077464 | 0.11305 | -0.026096 | 59.7194 | 59.7595 | 59.6966 | 59.6042 | 62.2839 | 62.3444 | 61.9854 | 62.292 | -2.5645 | -2.2659 | -2.5874 | -2.2888
729.8281 | 122.2321 | -62.2879 | 59.8251 | 0.13101 | 0.005267 | -0.016578 | -0.01586 | 0.049999 | 0.076426 | -0.053561 | 59.6874 | 59.7229 | 59.6691 | 59.5767 | 62.2565 | 62.3215 | 61.9442 | 62.2554 | 0.16305 | 0.03731 | 0.015465 | 0.016183 | 0.082042 | 0.10847 | -0.021518 | 59.7194 | 59.7549 | 59.7011 | 59.6088 | 62.2885 | 62.3536 | 61.9762 | 62.2874 | -2.5691 | -2.2568 | -2.5874 | -2.2751
731.5625 | 122.3373 | -62.2971 | 59.7244 | 0.12643 | 0.005267 | -0.016578 | -0.01586 | 0.049999 | 0.076426 | -0.058139 | 59.6828 | 59.7183 | 59.6645 | 59.5676 | 62.261 | 62.317 | 61.9396 | 62.26 | 0.15847 | 0.03731 | 0.015465 | 0.016183 | 0.082042 | 0.10847 | -0.026096 | 59.7149 | 59.7504 | 59.6966 | 59.5996 | 62.2931 | 62.349 | 61.9716 | 62.292 | -2.5782 | -2.2568 | -2.5965 | -2.2751
733.3125 | 122.3465 | -62.2742 | 59.761 | 0.12643 | 0.009846 | -0.021157 | -0.011281 | 0.040843 | 0.076426 | -0.058139 | 59.692 | 59.7137 | 59.6737 | 59.5767 | 62.2519 | 62.3124 | 61.9442 | 62.26 | 0.15847 | 0.041889 | 0.010886 | 0.020762 | 0.072886 | 0.10847 | -0.026096 | 59.724 | 59.7458 | 59.7057 | 59.6088 | 62.2839 | 62.3444 | 61.9762 | 62.292 | -2.5599 | -2.2522 | -2.5782 | -2.2705
735.0625 | 122.3328 | -62.2879 | 59.7473 | 0.12185 | 0.014425 | -0.021157 | -0.020438 | 0.049999 | 0.076426 | -0.053561 | 59.6828 | 59.7275 | 59.6645 | 59.5676 | 62.2565 | 62.3124 | 61.9442 | 62.26 | 0.15389 | 0.046468 | 0.010886 | 0.011605 | 0.082042 | 0.10847 | -0.021518 | 59.7149 | 59.7595 | 59.6966 | 59.5996 | 62.2885 | 62.3444 | 61.9762 | 62.292 | -2.5736 | -2.2613 | -2.5919 | -2.2796
736.75 | 122.3465 | -62.2742 | 59.7794 | 0.12643 | -0.00389 | -0.021157 | -0.020438 | 0.045421 | 0.071848 | -0.058139 | 59.692 | 59.7137 | 59.6691 | 59.5767 | 62.2519 | 62.3215 | 61.9487 | 62.2508 | 0.15847 | 0.028153 | 0.010886 | 0.011605 | 0.077464 | 0.10389 | -0.026096 | 59.724 | 59.7458 | 59.7011 | 59.6088 | 62.2839 | 62.3536 | 61.9808 | 62.2829 | -2.5599 | -2.2568 | -2.5828 | -2.2796
738.4844 | 122.3099 | -62.2833 | 59.7794 | 0.13101 | 0.000689 | -0.021157 | -0.020438 | 0.045421 | 0.076426 | -0.058139 | 59.6965 | 59.7275 | 59.6599 | 59.5676 | 62.2565 | 62.3124 | 61.9396 | 62.2691 | 0.16305 | 0.032732 | 0.010886 | 0.011605 | 0.077464 | 0.10847 | -0.026096 | 59.7286 | 59.7595 | 59.692 | 59.5996 | 62.2885 | 62.3444 | 61.9716 | 62.3012 | -2.5599 | -2.243 | -2.5965 | -2.2796
740.2344 | 122.3282 | -62.3199 | 59.7473 | 0.12185 | -0.00389 | -0.025735 | -0.011281 | 0.040843 | 0.076426 | -0.058139 | 59.6874 | 59.7229 | 59.6645 | 59.5676 | 62.2565 | 62.317 | 61.9533 | 62.2646 | 0.15389 | 0.028153 | 0.006308 | 0.020762 | 0.072886 | 0.10847 | -0.026096 | 59.7194 | 59.7549 | 59.6966 | 59.5996 | 62.2885 | 62.349 | 61.9854 | 62.2966 | -2.5691 | -2.2659 | -2.5919 | -2.2888
741.9688 | 122.319 | -62.3199 | 59.761 | 0.13101 | 0.005267 | -0.021157 | -0.020438 | 0.045421 | 0.076426 | -0.062717 | 59.6965 | 59.7183 | 59.6691 | 59.5722 | 62.2519 | 62.317 | 61.9487 | 62.2508 | 0.16305 | 0.03731 | 0.010886 | 0.011605 | 0.077464 | 0.10847 | -0.030674 | 59.7286 | 59.7504 | 59.7011 | 59.6042 | 62.2839 | 62.349 | 61.9808 | 62.2829 | -2.5553 | -2.2522 | -2.5828 | -2.2796
743.6406 | 122.2458 | -62.265 | 59.8206 | 0.13559 | 0.005267 | -0.012 | -0.011281 | 0.045421 | 0.076426 | -0.048983 | 59.692 | 59.7229 | 59.6691 | 59.5767 | 62.2565 | 62.3215 | 61.9487 | 62.2554 | 0.16763 | 0.03731 | 0.020043 | 0.020762 | 0.077464 | 0.10847 | -0.01694 | 59.724 | 59.7549 | 59.7011 | 59.6088 | 62.2885 | 62.3536 | 61.9808 | 62.2874 | -2.5645 | -2.2568 | -2.5874 | -2.2796
745.3906 | 122.2183 | -62.2833 | 59.8251 | 0.12643 | 0.005267 | -0.016578 | -0.01586 | 0.045421 | 0.076426 | -0.048983 | 59.6874 | 59.7275 | 59.6599 | 59.5722 | 62.2565 | 62.3124 | 61.9533 | 62.26 | 0.15847 | 0.03731 | 0.015465 | 0.016183 | 0.077464 | 0.10847 | -0.01694 | 59.7194 | 59.7595 | 59.692 | 59.6042 | 62.2885 | 62.3444 | 61.9854 | 62.292 | -2.5691 | -2.2659 | -2.5965 | -2.2934
747.0625 | 122.2687 | -62.2787 | 59.816 | 0.12643 | 0.014425 | -0.016578 | -0.011281 | 0.049999 | 0.076426 | -0.053561 | 59.6965 | 59.7229 | 59.6645 | 59.5722 | 62.2519 | 62.317 | 61.9487 | 62.26 | 0.15847 | 0.046468 | 0.015465 | 0.020762 | 0.082042 | 0.10847 | -0.021518 | 59.7286 | 59.7549 | 59.6966 | 59.6042 | 62.2839 | 62.349 | 61.9808 | 62.292 | -2.5553 | -2.2522 | -2.5874 | -2.2842
748.7969 | 122.2733 | -62.2559 | 59.7977 | 0.12643 | 0.009846 | -0.021157 | -0.011281 | 0.045421 | 0.081005 | -0.048983 | 59.692 | 59.7183 | 59.6691 | 59.5767 | 62.2519 | 62.317 | 61.9533 | 62.2554 | 0.15847 | 0.041889 | 0.010886 | 0.020762 | 0.077464 | 0.11305 | -0.01694 | 59.724 | 59.7504 | 59.7011 | 59.6088 | 62.2839 | 62.349 | 61.9854 | 62.2874 | -2.5599 | -2.2613 | -2.5828 | -2.2842
750.5469 | 122.3465 | -62.2925 | 59.7473 | 0.12643 | 0.009846 | -0.016578 | -0.01586 | 0.045421 | 0.067269 | -0.053561 | 59.692 | 59.7137 | 59.6599 | 59.5813 | 62.2519 | 62.3124 | 61.9533 | 62.26 | 0.15847 | 0.041889 | 0.015465 | 0.016183 | 0.077464 | 0.099312 | -0.021518 | 59.724 | 59.7458 | 59.692 | 59.6134 | 62.2839 | 62.3444 | 61.9854 | 62.292 | -2.5599 | -2.2613 | -2.5919 | -2.2934
752.2969 | 122.2549 | -62.2696 | 59.8114 | 0.12643 | 0.000689 | -0.025735 | -0.006703 | 0.045421 | 0.071848 | -0.053561 | 59.6965 | 59.7137 | 59.6691 | 59.5767 | 62.2519 | 62.317 | 61.9487 | 62.2646 | 0.15847 | 0.032732 | 0.006308 | 0.02534 | 0.077464 | 0.10389 | -0.021518 | 59.7286 | 59.7458 | 59.7011 | 59.6088 | 62.2839 | 62.349 | 61.9808 | 62.2966 | -2.5553 | -2.2522 | -2.5828 | -2.2796
753.9688 | 122.3145 | -62.2925 | 59.7839 | 0.12185 | 0.005267 | -0.021157 | -0.011281 | 0.045421 | 0.076426 | -0.058139 | 59.692 | 59.7275 | 59.6645 | 59.5676 | 62.2656 | 62.3078 | 61.9442 | 62.2646 | 0.15389 | 0.03731 | 0.010886 | 0.020762 | 0.077464 | 0.10847 | -0.026096 | 59.724 | 59.7595 | 59.6966 | 59.5996 | 62.2977 | 62.3398 | 61.9762 | 62.2966 | -2.5736 | -2.2522 | -2.6011 | -2.2796
755.7188 | 122.3511 | -62.2513 | 59.761 | 0.12643 | 0.005267 | -0.012 | -0.020438 | 0.045421 | 0.071848 | -0.053561 | 59.692 | 59.7183 | 59.6645 | 59.5813 | 62.2519 | 62.317 | 61.9442 | 62.26 | 0.15847 | 0.03731 | 0.020043 | 0.011605 | 0.077464 | 0.10389 | -0.021518 | 59.724 | 59.7504 | 59.6966 | 59.6134 | 62.2839 | 62.349 | 61.9762 | 62.292 | -2.5599 | -2.2522 | -2.5874 | -2.2796
757.4688 | 122.2092 | -62.2833 | 59.8389 | 0.12185 | 0.009846 | -0.021157 | -0.011281 | 0.040843 | 0.081005 | -0.053561 | 59.6965 | 59.7137 | 59.6645 | 59.5813 | 62.2519 | 62.3215 | 61.9442 | 62.2646 | 0.15389 | 0.041889 | 0.010886 | 0.020762 | 0.072886 | 0.11305 | -0.021518 | 59.7286 | 59.7458 | 59.6966 | 59.6134 | 62.2839 | 62.3536 | 61.9762 | 62.2966 | -2.5553 | -2.2476 | -2.5874 | -2.2796
759.2188 | 122.3465 | -62.2375 | 59.7565 | 0.13101 | 0.005267 | -0.021157 | -0.011281 | 0.040843 | 0.076426 | -0.058139 | 59.692 | 59.7229 | 59.6554 | 59.5676 | 62.2519 | 62.317 | 61.9442 | 62.2554 | 0.16305 | 0.03731 | 0.010886 | 0.020762 | 0.072886 | 0.10847 | -0.026096 | 59.724 | 59.7549 | 59.6874 | 59.5996 | 62.2839 | 62.349 | 61.9762 | 62.2874 | -2.5599 | -2.2522 | -2.5965 | -2.2888
760.9688 | 122.3511 | -62.265 | 59.7794 | 0.13101 | 0.000689 | -0.025735 | -0.01586 | 0.049999 | 0.076426 | -0.058139 | 59.6874 | 59.7229 | 59.6645 | 59.5767 | 62.2565 | 62.317 | 61.9533 | 62.26 | 0.16305 | 0.032732 | 0.006308 | 0.016183 | 0.082042 | 0.10847 | -0.026096 | 59.7194 | 59.7549 | 59.6966 | 59.6088 | 62.2885 | 62.349 | 61.9854 | 62.292 | -2.5691 | -2.2659 | -2.5919 | -2.2888
762.6562 | 122.2183 | -62.3154 | 59.816 | 0.12185 | 0.014425 | -0.021157 | -0.011281 | 0.049999 | 0.085583 | -0.058139 | 59.692 | 59.7183 | 59.6645 | 59.5767 | 62.2519 | 62.317 | 61.9533 | 62.2554 | 0.15389 | 0.046468 | 0.010886 | 0.020762 | 0.082042 | 0.11763 | -0.026096 | 59.724 | 59.7504 | 59.6966 | 59.6088 | 62.2839 | 62.349 | 61.9854 | 62.2874 | -2.5599 | -2.2613 | -2.5874 | -2.2888
764.3906 | 122.2229 | -62.3062 | 59.8297 | 0.12185 | 0.009846 | -0.021157 | -0.025017 | 0.045421 | 0.076426 | -0.048983 | 59.692 | 59.7183 | 59.6691 | 59.5813 | 62.2473 | 62.3215 | 61.9487 | 62.2554 | 0.15389 | 0.041889 | 0.010886 | 0.007026 | 0.077464 | 0.10847 | -0.01694 | 59.724 | 59.7504 | 59.7011 | 59.6134 | 62.2793 | 62.3536 | 61.9808 | 62.2874 | -2.5553 | -2.2568 | -2.5782 | -2.2796
766.1406 | 122.3053 | -62.3016 | 59.7748 | 0.12185 | 0.005267 | -0.016578 | -0.011281 | 0.045421 | 0.076426 | -0.058139 | 59.692 | 59.7275 | 59.6645 | 59.5722 | 62.2565 | 62.3124 | 61.9487 | 62.2554 | 0.15389 | 0.03731 | 0.015465 | 0.020762 | 0.077464 | 0.10847 | -0.026096 | 59.724 | 59.7595 | 59.6966 | 59.6042 | 62.2885 | 62.3444 | 61.9808 | 62.2874 | -2.5645 | -2.2568 | -2.5919 | -2.2842
767.8125 | 122.2321 | -62.2925 | 59.7839 | 0.13101 | 0.009846 | -0.021157 | -0.01586 | 0.049999 | 0.071848 | -0.048983 | 59.692 | 59.7229 | 59.6691 | 59.5767 | 62.2565 | 62.3124 | 61.9442 | 62.2646 | 0.16305 | 0.041889 | 0.010886 | 0.016183 | 0.082042 | 0.10389 | -0.01694 | 59.724 | 59.7549 | 59.7011 | 59.6088 | 62.2885 | 62.3444 | 61.9762 | 62.2966 | -2.5645 | -2.2522 | -2.5874 | -2.2751
769.5625 | 122.3145 | -62.2879 | 59.7519 | 0.12185 | 0.005267 | -0.025735 | -0.01586 | 0.045421 | 0.081005 | -0.053561 | 59.692 | 59.732 | 59.6691 | 59.5767 | 62.2565 | 62.3215 | 61.9442 | 62.2554 | 0.15389 | 0.03731 | 0.006308 | 0.016183 | 0.077464 | 0.11305 | -0.021518 | 59.724 | 59.7641 | 59.7011 | 59.6088 | 62.2885 | 62.3536 | 61.9762 | 62.2874 | -2.5645 | -2.2522 | -2.5874 | -2.2751
771.2656 | 122.3053 | -62.2787 | 59.7198 | 0.12643 | 0.005267 | -0.025735 | -0.020438 | 0.036265 | 0.071848 | -0.062717 | 59.6965 | 59.7229 | 59.6645 | 59.5722 | 62.2473 | 62.3124 | 61.9442 | 62.2554 | 0.15847 | 0.03731 | 0.006308 | 0.011605 | 0.068308 | 0.10389 | -0.030674 | 59.7286 | 59.7549 | 59.6966 | 59.6042 | 62.2793 | 62.3444 | 61.9762 | 62.2874 | -2.5508 | -2.2476 | -2.5828 | -2.2796
773 | 122.3511 | -62.2925 | 59.7427 | 0.11727 | 0.005267 | -0.016578 | -0.025017 | 0.049999 | 0.076426 | -0.048983 | 59.7011 | 59.7183 | 59.6737 | 59.5722 | 62.2656 | 62.3124 | 61.9442 | 62.26 | 0.14932 | 0.03731 | 0.015465 | 0.007026 | 0.082042 | 0.10847 | -0.01694 | 59.7332 | 59.7504 | 59.7057 | 59.6042 | 62.2977 | 62.3444 | 61.9762 | 62.292 | -2.5645 | -2.243 | -2.5919 | -2.2705
774.75 | 122.3145 | -62.2971 | 59.7702 | 0.12185 | -0.00389 | -0.025735 | -0.01586 | 0.049999 | 0.067269 | -0.058139 | 59.692 | 59.7275 | 59.6691 | 59.5722 | 62.2519 | 62.317 | 61.9442 | 62.26 | 0.15389 | 0.028153 | 0.006308 | 0.016183 | 0.082042 | 0.099312 | -0.026096 | 59.724 | 59.7595 | 59.7011 | 59.6042 | 62.2839 | 62.349 | 61.9762 | 62.292 | -2.5599 | -2.2522 | -2.5828 | -2.2751
776.4375 | 122.2366 | -62.3062 | 59.7839 | 0.12643 | 0.009846 | -0.021157 | -0.011281 | 0.054577 | 0.076426 | -0.048983 | 59.6965 | 59.7229 | 59.6691 | 59.5767 | 62.2565 | 62.3124 | 61.9487 | 62.26 | 0.15847 | 0.041889 | 0.010886 | 0.020762 | 0.08662 | 0.10847 | -0.01694 | 59.7286 | 59.7549 | 59.7011 | 59.6088 | 62.2885 | 62.3444 | 61.9808 | 62.292 | -2.5599 | -2.2522 | -2.5874 | -2.2796
778.1875 | 122.374 | -62.265 | 59.7748 | 0.12185 | 0.005267 | -0.021157 | -0.020438 | 0.045421 | 0.081005 | -0.058139 | 59.692 | 59.7366 | 59.6645 | 59.5767 | 62.2565 | 62.317 | 61.9579 | 62.2554 | 0.15389 | 0.03731 | 0.010886 | 0.011605 | 0.077464 | 0.11305 | -0.026096 | 59.724 | 59.7687 | 59.6966 | 59.6088 | 62.2885 | 62.349 | 61.9899 | 62.2874 | -2.5645 | -2.2659 | -2.5919 | -2.2934
779.875 | 122.2961 | -62.2604 | 59.7656 | 0.12643 | 0.005267 | -0.025735 | -0.01586 | 0.049999 | 0.071848 | -0.058139 | 59.6874 | 59.7229 | 59.6599 | 59.5722 | 62.2519 | 62.317 | 61.9442 | 62.2554 | 0.15847 | 0.03731 | 0.006308 | 0.016183 | 0.082042 | 0.10389 | -0.026096 | 59.7194 | 59.7549 | 59.692 | 59.6042 | 62.2839 | 62.349 | 61.9762 | 62.2874 | -2.5645 | -2.2568 | -2.5919 | -2.2842
781.6094 | 122.3511 | -62.2787 | 59.7382 | 0.12643 | 0.000689 | -0.012 | -0.01586 | 0.049999 | 0.076426 | -0.053561 | 59.6828 | 59.7229 | 59.6691 | 59.5859 | 62.261 | 62.3078 | 61.9396 | 62.2646 | 0.15847 | 0.032732 | 0.020043 | 0.016183 | 0.082042 | 0.10847 | -0.021518 | 59.7149 | 59.7549 | 59.7011 | 59.6179 | 62.2931 | 62.3398 | 61.9716 | 62.2966 | -2.5782 | -2.2568 | -2.5919 | -2.2705
783.3594 | 122.3373 | -62.2833 | 59.7519 | 0.13101 | -0.008469 | -0.021157 | -0.025017 | 0.049999 | 0.081005 | -0.058139 | 59.692 | 59.7275 | 59.6737 | 59.5859 | 62.2519 | 62.3078 | 61.9487 | 62.2554 | 0.16305 | 0.023574 | 0.010886 | 0.007026 | 0.082042 | 0.11305 | -0.026096 | 59.724 | 59.7595 | 59.7057 | 59.6179 | 62.2839 | 62.3398 | 61.9808 | 62.2874 | -2.5599 | -2.2568 | -2.5782 | -2.2751
785.125 | 122.2687 | -62.3108 | 59.8022 | 0.13101 | 0.005267 | -0.012 | -0.011281 | 0.054577 | 0.076426 | -0.058139 | 59.692 | 59.7275 | 59.6737 | 59.5813 | 62.2565 | 62.3215 | 61.9442 | 62.26 | 0.16305 | 0.03731 | 0.020043 | 0.020762 | 0.08662 | 0.10847 | -0.026096 | 59.724 | 59.7595 | 59.7057 | 59.6134 | 62.2885 | 62.3536 | 61.9762 | 62.292 | -2.5645 | -2.2522 | -2.5828 | -2.2705
786.875 | 122.2321 | -62.2833 | 59.7931 | 0.12643 | 0.000689 | -0.016578 | -0.01586 | 0.049999 | 0.081005 | -0.053561 | 59.692 | 59.7275 | 59.6645 | 59.5767 | 62.2565 | 62.317 | 61.9487 | 62.26 | 0.15847 | 0.032732 | 0.015465 | 0.016183 | 0.082042 | 0.11305 | -0.021518 | 59.724 | 59.7595 | 59.6966 | 59.6088 | 62.2885 | 62.349 | 61.9808 | 62.292 | -2.5645 | -2.2568 | -2.5919 | -2.2842
788.5625 | 122.3099 | -62.2742 | 59.7656 | 0.12185 | 0.009846 | -0.012 | -0.020438 | 0.049999 | 0.076426 | -0.058139 | 59.6828 | 59.732 | 59.6691 | 59.5813 | 62.2565 | 62.317 | 61.9396 | 62.26 | 0.15389 | 0.041889 | 0.020043 | 0.011605 | 0.082042 | 0.10847 | -0.026096 | 59.7149 | 59.7641 | 59.7011 | 59.6134 | 62.2885 | 62.349 | 61.9716 | 62.292 | -2.5736 | -2.2568 | -2.5874 | -2.2705
790.3281 | 122.3053 | -62.2787 | 59.7885 | 0.13101 | 0.000689 | -0.025735 | -0.025017 | 0.045421 | 0.081005 | -0.053561 | 59.6874 | 59.7229 | 59.6691 | 59.5859 | 62.2565 | 62.3124 | 61.9533 | 62.2463 | 0.16305 | 0.032732 | 0.006308 | 0.007026 | 0.077464 | 0.11305 | -0.021518 | 59.7194 | 59.7549 | 59.7011 | 59.6179 | 62.2885 | 62.3444 | 61.9854 | 62.2783 | -2.5691 | -2.2659 | -2.5874 | -2.2842
792.0156 | 122.3099 | -62.2787 | 59.7656 | 0.12643 | 0.000689 | -0.021157 | -0.01586 | 0.054577 | 0.076426 | -0.058139 | 59.6965 | 59.7275 | 59.6737 | 59.5813 | 62.261 | 62.3078 | 61.9533 | 62.26 | 0.15847 | 0.032732 | 0.010886 | 0.016183 | 0.08662 | 0.10847 | -0.026096 | 59.7286 | 59.7595 | 59.7057 | 59.6134 | 62.2931 | 62.3398 | 61.9854 | 62.292 | -2.5645 | -2.2568 | -2.5874 | -2.2796
793.7656 | 122.2504 | -62.2742 | 59.7931 | 0.12643 | 0.000689 | -0.012 | -0.01586 | 0.049999 | 0.081005 | -0.044405 | 59.6965 | 59.7229 | 59.6645 | 59.5859 | 62.261 | 62.3078 | 61.935 | 62.2646 | 0.15847 | 0.032732 | 0.020043 | 0.016183 | 0.082042 | 0.11305 | -0.012362 | 59.7286 | 59.7549 | 59.6966 | 59.6179 | 62.2931 | 62.3398 | 61.967 | 62.2966 | -2.5645 | -2.2385 | -2.5965 | -2.2705
795.5156 | 122.2366 | -62.3062 | 59.8434 | 0.12643 | 0.000689 | -0.012 | -0.020438 | 0.040843 | 0.085583 | -0.053561 | 59.6965 | 59.7229 | 59.6691 | 59.5813 | 62.2565 | 62.3124 | 61.9442 | 62.2554 | 0.15847 | 0.032732 | 0.020043 | 0.011605 | 0.072886 | 0.11763 | -0.021518 | 59.7286 | 59.7549 | 59.7011 | 59.6134 | 62.2885 | 62.3444 | 61.9762 | 62.2874 | -2.5599 | -2.2476 | -2.5874 | -2.2751
797.2031 | 122.3099 | -62.2787 | 59.7702 | 0.13101 | 0.000689 | -0.025735 | -0.01586 | 0.049999 | 0.071848 | -0.053561 | 59.7011 | 59.7275 | 59.6691 | 59.5767 | 62.2565 | 62.3078 | 61.9487 | 62.26 | 0.16305 | 0.032732 | 0.006308 | 0.016183 | 0.082042 | 0.10389 | -0.021518 | 59.7332 | 59.7595 | 59.7011 | 59.6088 | 62.2885 | 62.3398 | 61.9808 | 62.292 | -2.5553 | -2.2476 | -2.5874 | -2.2796
798.9531 | 122.3557 | -62.2513 | 59.7931 | 0.13101 | 0.000689 | -0.016578 | -0.01586 | 0.049999 | 0.076426 | -0.053561 | 59.6874 | 59.7366 | 59.6737 | 59.5767 | 62.2565 | 62.3124 | 61.9487 | 62.2463 | 0.16305 | 0.032732 | 0.015465 | 0.016183 | 0.082042 | 0.10847 | -0.021518 | 59.7194 | 59.7687 | 59.7057 | 59.6088 | 62.2885 | 62.3444 | 61.9808 | 62.2783 | -2.5691 | -2.2613 | -2.5828 | -2.2751
800.6406 | 122.3099 | -62.3016 | 59.7382 | 0.13559 | 0.000689 | -0.021157 | -0.01586 | 0.045421 | 0.076426 | -0.058139 | 59.692 | 59.732 | 59.6691 | 59.5767 | 62.2565 | 62.317 | 61.9533 | 62.2554 | 0.16763 | 0.032732 | 0.010886 | 0.016183 | 0.077464 | 0.10847 | -0.026096 | 59.724 | 59.7641 | 59.7011 | 59.6088 | 62.2885 | 62.349 | 61.9854 | 62.2874 | -2.5645 | -2.2613 | -2.5874 | -2.2842
802.3281 | 122.2824 | -62.2742 | 59.8206 | 0.13101 | -0.00389 | -0.016578 | -0.011281 | 0.045421 | 0.081005 | -0.058139 | 59.6965 | 59.7275 | 59.6737 | 59.5813 | 62.2565 | 62.3124 | 61.9579 | 62.26 | 0.16305 | 0.028153 | 0.015465 | 0.020762 | 0.077464 | 0.11305 | -0.026096 | 59.7286 | 59.7595 | 59.7057 | 59.6134 | 62.2885 | 62.3444 | 61.9899 | 62.292 | -2.5599 | -2.2613 | -2.5828 | -2.2842
804.0781 | 122.2366 | -62.2833 | 59.8389 | 0.13101 | 0.005267 | -0.025735 | -0.01586 | 0.049999 | 0.085583 | -0.053561 | 59.7011 | 59.7275 | 59.6737 | 59.5722 | 62.2565 | 62.317 | 61.935 | 62.2554 | 0.16305 | 0.03731 | 0.006308 | 0.016183 | 0.082042 | 0.11763 | -0.021518 | 59.7332 | 59.7595 | 59.7057 | 59.6042 | 62.2885 | 62.349 | 61.967 | 62.2874 | -2.5553 | -2.2339 | -2.5828 | -2.2613
805.8438 | 122.2275 | -62.2971 | 59.8389 | 0.13101 | 0.000689 | -0.025735 | -0.01586 | 0.045421 | 0.085583 | -0.058139 | 59.7011 | 59.7275 | 59.6782 | 59.5813 | 62.2519 | 62.3078 | 61.9487 | 62.2508 | 0.16305 | 0.032732 | 0.006308 | 0.016183 | 0.077464 | 0.11763 | -0.026096 | 59.7332 | 59.7595 | 59.7103 | 59.6134 | 62.2839 | 62.3398 | 61.9808 | 62.2829 | -2.5508 | -2.2476 | -2.5736 | -2.2705
807.5938 | 122.287 | -62.2833 | 59.8206 | 0.14017 | 0.005267 | -0.021157 | -0.011281 | 0.049999 | 0.085583 | -0.044405 | 59.6965 | 59.7275 | 59.6737 | 59.5722 | 62.2565 | 62.317 | 61.9442 | 62.2508 | 0.17221 | 0.03731 | 0.010886 | 0.020762 | 0.082042 | 0.11763 | -0.012362 | 59.7286 | 59.7595 | 59.7057 | 59.6042 | 62.2885 | 62.349 | 61.9762 | 62.2829 | -2.5599 | -2.2476 | -2.5828 | -2.2705
809.2812 | 122.3557 | -62.2559 | 59.7656 | 0.13101 | 0.000689 | -0.016578 | -0.025017 | 0.045421 | 0.076426 | -0.053561 | 59.692 | 59.7275 | 59.6737 | 59.5767 | 62.2565 | 62.317 | 61.9442 | 62.2508 | 0.16305 | 0.032732 | 0.015465 | 0.007026 | 0.077464 | 0.10847 | -0.021518 | 59.724 | 59.7595 | 59.7057 | 59.6088 | 62.2885 | 62.349 | 61.9762 | 62.2829 | -2.5645 | -2.2522 | -2.5828 | -2.2705
811.0156 | 122.3419 | -62.2696 | 59.8022 | 0.13559 | 0.000689 | -0.021157 | -0.011281 | 0.045421 | 0.081005 | -0.058139 | 59.6965 | 59.7229 | 59.6691 | 59.5813 | 62.2565 | 62.3215 | 61.9533 | 62.2508 | 0.16763 | 0.032732 | 0.010886 | 0.020762 | 0.077464 | 0.11305 | -0.026096 | 59.7286 | 59.7549 | 59.7011 | 59.6134 | 62.2885 | 62.3536 | 61.9854 | 62.2829 | -2.5599 | -2.2568 | -2.5874 | -2.2842
812.75 | 122.3007 | -62.2696 | 59.7748 | 0.13559 | 0.005267 | -0.025735 | -0.020438 | 0.049999 | 0.071848 | -0.062717 | 59.7011 | 59.732 | 59.6691 | 59.5859 | 62.2519 | 62.3124 | 61.9396 | 62.2554 | 0.16763 | 0.03731 | 0.006308 | 0.011605 | 0.082042 | 0.10389 | -0.030674 | 59.7332 | 59.7641 | 59.7011 | 59.6179 | 62.2839 | 62.3444 | 61.9716 | 62.2874 | -2.5508 | -2.2385 | -2.5828 | -2.2705
814.4844 | 122.2046 | -62.2971 | 59.816 | 0.14017 | 0.014425 | -0.016578 | -0.006703 | 0.049999 | 0.090161 | -0.048983 | 59.7011 | 59.7458 | 59.6691 | 59.5859 | 62.2519 | 62.3078 | 61.9487 | 62.2554 | 0.17221 | 0.046468 | 0.015465 | 0.02534 | 0.082042 | 0.1222 | -0.01694 | 59.7332 | 59.7778 | 59.7011 | 59.6179 | 62.2839 | 62.3398 | 61.9808 | 62.2874 | -2.5508 | -2.2476 | -2.5828 | -2.2796
816.1719 | 122.2366 | -62.2833 | 59.8434 | 0.14017 | 0.000689 | -0.025735 | -0.01586 | 0.054577 | 0.076426 | -0.053561 | 59.6965 | 59.7275 | 59.6691 | 59.5813 | 62.2519 | 62.3032 | 61.9533 | 62.26 | 0.17221 | 0.032732 | 0.006308 | 0.016183 | 0.08662 | 0.10847 | -0.021518 | 59.7286 | 59.7595 | 59.7011 | 59.6134 | 62.2839 | 62.3353 | 61.9854 | 62.292 | -2.5553 | -2.2568 | -2.5828 | -2.2842
817.9219 | 122.3648 | -62.2421 | 59.7839 | 0.12643 | 0.005267 | -0.025735 | -0.025017 | 0.049999 | 0.085583 | -0.053561 | 59.7103 | 59.732 | 59.6828 | 59.5951 | 62.2565 | 62.3032 | 61.9487 | 62.2554 | 0.15847 | 0.03731 | 0.006308 | 0.007026 | 0.082042 | 0.11763 | -0.021518 | 59.7423 | 59.7641 | 59.7149 | 59.6271 | 62.2885 | 62.3353 | 61.9808 | 62.2874 | -2.5462 | -2.2385 | -2.5736 | -2.2659
819.6719 | 122.2733 | -62.265 | 59.8206 | 0.13101 | 0.005267 | -0.025735 | -0.025017 | 0.049999 | 0.090161 | -0.053561 | 59.7011 | 59.732 | 59.6782 | 59.5859 | 62.2519 | 62.3124 | 61.9396 | 62.2554 | 0.16305 | 0.03731 | 0.006308 | 0.007026 | 0.082042 | 0.1222 | -0.021518 | 59.7332 | 59.7641 | 59.7103 | 59.6179 | 62.2839 | 62.3444 | 61.9716 | 62.2874 | -2.5508 | -2.2385 | -2.5736 | -2.2613
821.3594 | 122.3694 | -62.2467 | 59.7885 | 0.14017 | -0.00389 | -0.021157 | -0.01586 | 0.049999 | 0.071848 | -0.058139 | 59.6965 | 59.732 | 59.6691 | 59.5813 | 62.2565 | 62.3078 | 61.9533 | 62.2646 | 0.17221 | 0.028153 | 0.010886 | 0.016183 | 0.082042 | 0.10389 | -0.026096 | 59.7286 | 59.7641 | 59.7011 | 59.6134 | 62.2885 | 62.3398 | 61.9854 | 62.2966 | -2.5599 | -2.2568 | -2.5874 | -2.2842
823.1094 | 122.3145 | -62.2696 | 59.8206 | 0.13559 | -0.00389 | -0.021157 | -0.020438 | 0.040843 | 0.071848 | -0.058139 | 59.7057 | 59.7366 | 59.6828 | 59.5859 | 62.2519 | 62.3124 | 61.9396 | 62.2508 | 0.16763 | 0.028153 | 0.010886 | 0.011605 | 0.072886 | 0.10389 | -0.026096 | 59.7377 | 59.7687 | 59.7149 | 59.6179 | 62.2839 | 62.3444 | 61.9716 | 62.2829 | -2.5462 | -2.2339 | -2.5691 | -2.2568
824.8594 | 122.3648 | -62.2787 | 59.7702 | 0.13101 | 0.005267 | -0.021157 | -0.020438 | 0.045421 | 0.071848 | -0.058139 | 59.6965 | 59.7412 | 59.6737 | 59.5813 | 62.2519 | 62.3078 | 61.9396 | 62.2554 | 0.16305 | 0.03731 | 0.010886 | 0.011605 | 0.077464 | 0.10389 | -0.026096 | 59.7286 | 59.7732 | 59.7057 | 59.6134 | 62.2839 | 62.3398 | 61.9716 | 62.2874 | -2.5553 | -2.243 | -2.5782 | -2.2659
826.6094 | 122.3099 | -62.2513 | 59.816 | 0.13559 | 0.000689 | -0.021157 | -0.020438 | 0.040843 | 0.071848 | -0.048983 | 59.7057 | 59.7366 | 59.6737 | 59.5813 | 62.2519 | 62.3078 | 61.935 | 62.26 | 0.16763 | 0.032732 | 0.010886 | 0.011605 | 0.072886 | 0.10389 | -0.01694 | 59.7377 | 59.7687 | 59.7057 | 59.6134 | 62.2839 | 62.3398 | 61.967 | 62.292 | -2.5462 | -2.2293 | -2.5782 | -2.2613
828.2969 | 122.3465 | -62.2742 | 59.7427 | 0.13101 | 0.000689 | -0.021157 | -0.011281 | 0.049999 | 0.076426 | -0.053561 | 59.7057 | 59.732 | 59.6737 | 59.5859 | 62.2473 | 62.3078 | 61.9304 | 62.2508 | 0.16305 | 0.032732 | 0.010886 | 0.020762 | 0.082042 | 0.10847 | -0.021518 | 59.7377 | 59.7641 | 59.7057 | 59.6179 | 62.2793 | 62.3398 | 61.9625 | 62.2829 | -2.5416 | -2.2247 | -2.5736 | -2.2567
830.0625 | 122.2275 | -62.2787 | 59.848 | 0.14017 | 0.000689 | -0.021157 | -0.011281 | 0.049999 | 0.081005 | -0.053561 | 59.7011 | 59.732 | 59.6782 | 59.5859 | 62.2473 | 62.3124 | 61.9442 | 62.2554 | 0.17221 | 0.032732 | 0.010886 | 0.020762 | 0.082042 | 0.11305 | -0.021518 | 59.7332 | 59.7641 | 59.7103 | 59.6179 | 62.2793 | 62.3444 | 61.9762 | 62.2874 | -2.5462 | -2.243 | -2.5691 | -2.2659
831.8125 | 122.319 | -62.2696 | 59.7702 | 0.13559 | 0.000689 | -0.016578 | -0.01586 | 0.040843 | 0.081005 | -0.048983 | 59.7103 | 59.7366 | 59.6828 | 59.5859 | 62.2473 | 62.3078 | 61.9396 | 62.2508 | 0.16763 | 0.032732 | 0.015465 | 0.016183 | 0.072886 | 0.11305 | -0.01694 | 59.7423 | 59.7687 | 59.7149 | 59.6179 | 62.2793 | 62.3398 | 61.9716 | 62.2829 | -2.537 | -2.2293 | -2.5645 | -2.2568
833.4844 | 122.2504 | -62.2787 | 59.848 | 0.14017 | -0.00389 | -0.030314 | -0.01586 | 0.049999 | 0.076426 | -0.053561 | 59.7057 | 59.7275 | 59.6782 | 59.5767 | 62.2427 | 62.3124 | 61.9442 | 62.2417 | 0.17221 | 0.028153 | 0.001729 | 0.016183 | 0.082042 | 0.10847 | -0.021518 | 59.7377 | 59.7595 | 59.7103 | 59.6088 | 62.2748 | 62.3444 | 61.9762 | 62.2737 | -2.537 | -2.2385 | -2.5645 | -2.2659
835.1562 | 122.3648 | -62.2559 | 59.7519 | 0.14017 | 0.000689 | -0.016578 | -0.020438 | 0.045421 | 0.076426 | -0.048983 | 59.7103 | 59.7412 | 59.6828 | 59.5905 | 62.2519 | 62.3078 | 61.9304 | 62.2508 | 0.17221 | 0.032732 | 0.015465 | 0.011605 | 0.077464 | 0.10847 | -0.01694 | 59.7423 | 59.7732 | 59.7149 | 59.6225 | 62.2839 | 62.3398 | 61.9625 | 62.2829 | -2.5416 | -2.2201 | -2.5691 | -2.2476
836.8438 | 122.2961 | -62.2604 | 59.7702 | 0.12643 | 0.000689 | -0.016578 | -0.025017 | 0.040843 | 0.076426 | -0.053561 | 59.7011 | 59.7366 | 59.6828 | 59.5951 | 62.2519 | 62.3032 | 61.935 | 62.2508 | 0.15847 | 0.032732 | 0.015465 | 0.007026 | 0.072886 | 0.10847 | -0.021518 | 59.7332 | 59.7687 | 59.7149 | 59.6271 | 62.2839 | 62.3353 | 61.967 | 62.2829 | -2.5508 | -2.2339 | -2.5691 | -2.2522
838.5312 | 122.2641 | -62.2696 | 59.8389 | 0.13559 | 0.005267 | -0.021157 | -0.011281 | 0.040843 | 0.081005 | -0.053561 | 59.7103 | 59.7412 | 59.6828 | 59.5905 | 62.2473 | 62.317 | 61.9396 | 62.2417 | 0.16763 | 0.03731 | 0.010886 | 0.020762 | 0.072886 | 0.11305 | -0.021518 | 59.7423 | 59.7732 | 59.7149 | 59.6225 | 62.2793 | 62.349 | 61.9716 | 62.2737 | -2.537 | -2.2293 | -2.5645 | -2.2568
840.2344 | 122.2229 | -62.2971 | 59.8389 | 0.13101 | 0.009846 | -0.021157 | -0.006703 | 0.040843 | 0.071848 | -0.048983 | 59.7057 | 59.7412 | 59.6874 | 59.5951 | 62.2473 | 62.3124 | 61.9396 | 62.2463 | 0.16305 | 0.041889 | 0.010886 | 0.02534 | 0.072886 | 0.10389 | -0.01694 | 59.7377 | 59.7732 | 59.7194 | 59.6271 | 62.2793 | 62.3444 | 61.9716 | 62.2783 | -2.5416 | -2.2339 | -2.5599 | -2.2522
841.9844 | 122.2321 | -62.265 | 59.8801 | 0.13559 | 0.000689 | -0.021157 | -0.020438 | 0.045421 | 0.085583 | -0.062717 | 59.7103 | 59.7412 | 59.6828 | 59.5951 | 62.2473 | 62.3078 | 61.9442 | 62.2417 | 0.16763 | 0.032732 | 0.010886 | 0.011605 | 0.077464 | 0.11763 | -0.030674 | 59.7423 | 59.7732 | 59.7149 | 59.6271 | 62.2793 | 62.3398 | 61.9762 | 62.2737 | -2.537 | -2.2339 | -2.5645 | -2.2613
843.7344 | 122.2229 | -62.2833 | 59.8022 | 0.13101 | 0.000689 | -0.016578 | -0.01586 | 0.049999 | 0.081005 | -0.048983 | 59.7103 | 59.7412 | 59.6828 | 59.5951 | 62.2427 | 62.3078 | 61.935 | 62.2463 | 0.16305 | 0.032732 | 0.015465 | 0.016183 | 0.082042 | 0.11305 | -0.01694 | 59.7423 | 59.7732 | 59.7149 | 59.6271 | 62.2748 | 62.3398 | 61.967 | 62.2783 | -2.5324 | -2.2247 | -2.5599 | -2.2522
845.4219 | 122.3236 | -62.2467 | 59.8068 | 0.13101 | 0.000689 | -0.016578 | -0.020438 | 0.049999 | 0.076426 | -0.058139 | 59.7057 | 59.732 | 59.6828 | 59.5859 | 62.2565 | 62.3078 | 61.9396 | 62.2508 | 0.16305 | 0.032732 | 0.015465 | 0.011605 | 0.082042 | 0.10847 | -0.026096 | 59.7377 | 59.7641 | 59.7149 | 59.6179 | 62.2885 | 62.3398 | 61.9716 | 62.2829 | -2.5508 | -2.2339 | -2.5736 | -2.2568
847.1562 | 122.2183 | -62.2925 | 59.8022 | 0.13559 | 0.009846 | -0.016578 | -0.011281 | 0.059155 | 0.081005 | -0.053561 | 59.7011 | 59.7366 | 59.6828 | 59.5905 | 62.2427 | 62.3032 | 61.935 | 62.2463 | 0.16763 | 0.041889 | 0.015465 | 0.020762 | 0.091198 | 0.11305 | -0.021518 | 59.7332 | 59.7687 | 59.7149 | 59.6225 | 62.2748 | 62.3353 | 61.967 | 62.2783 | -2.5416 | -2.2339 | -2.5599 | -2.2522
848.9062 | 122.374 | -62.2375 | 59.7794 | 0.13559 | -0.00389 | -0.021157 | -0.020438 | 0.049999 | 0.076426 | -0.053561 | 59.7057 | 59.7458 | 59.6874 | 59.5905 | 62.2519 | 62.2987 | 61.9304 | 62.2508 | 0.16763 | 0.028153 | 0.010886 | 0.011605 | 0.082042 | 0.10847 | -0.021518 | 59.7377 | 59.7778 | 59.7194 | 59.6225 | 62.2839 | 62.3307 | 61.9625 | 62.2829 | -2.5462 | -2.2247 | -2.5645 | -2.243
850.6562 | 122.2412 | -62.2604 | 59.8343 | 0.12643 | 0.005267 | -0.025735 | -0.011281 | 0.045421 | 0.081005 | -0.053561 | 59.7149 | 59.7412 | 59.692 | 59.5996 | 62.2427 | 62.3032 | 61.9258 | 62.2463 | 0.15847 | 0.03731 | 0.006308 | 0.020762 | 0.077464 | 0.11305 | -0.021518 | 59.7469 | 59.7732 | 59.724 | 59.6317 | 62.2748 | 62.3353 | 61.9579 | 62.2783 | -2.5279 | -2.211 | -2.5507 | -2.2339
852.3438 | 122.3557 | -62.2559 | 59.7565 | 0.13559 | -0.00389 | -0.021157 | -0.01586 | 0.049999 | 0.081005 | -0.048983 | 59.7149 | 59.7458 | 59.6874 | 59.5996 | 62.2427 | 62.3032 | 61.9258 | 62.2463 | 0.16763 | 0.028153 | 0.010886 | 0.016183 | 0.082042 | 0.11305 | -0.01694 | 59.7469 | 59.7778 | 59.7194 | 59.6317 | 62.2748 | 62.3353 | 61.9579 | 62.2783 | -2.5279 | -2.211 | -2.5553 | -2.2384
854.0938 | 122.3145 | -62.2559 | 59.7748 | 0.13559 | 0.000689 | -0.025735 | -0.011281 | 0.045421 | 0.076426 | -0.048983 | 59.7103 | 59.7504 | 59.692 | 59.5996 | 62.2381 | 62.3078 | 61.9304 | 62.2417 | 0.16763 | 0.032732 | 0.006308 | 0.020762 | 0.077464 | 0.10847 | -0.01694 | 59.7423 | 59.7824 | 59.724 | 59.6317 | 62.2702 | 62.3398 | 61.9625 | 62.2737 | -2.5279 | -2.2201 | -2.5462 | -2.2384
855.8438 | 122.3282 | -62.2192 | 59.816 | 0.13101 | -0.00389 | -0.021157 | -0.020438 | 0.040843 | 0.081005 | -0.048983 | 59.7103 | 59.7412 | 59.692 | 59.5996 | 62.2427 | 62.3078 | 61.9396 | 62.2417 | 0.16305 | 0.028153 | 0.010886 | 0.011605 | 0.072886 | 0.11305 | -0.01694 | 59.7423 | 59.7732 | 59.724 | 59.6317 | 62.2748 | 62.3398 | 61.9716 | 62.2737 | -2.5324 | -2.2293 | -2.5507 | -2.2476
857.5938 | 122.2824 | -62.265 | 59.8068 | 0.13559 | 0.005267 | -0.021157 | -0.006703 | 0.045421 | 0.081005 | -0.053561 | 59.7149 | 59.7458 | 59.6874 | 59.5996 | 62.2381 | 62.2987 | 61.9258 | 62.2371 | 0.16763 | 0.03731 | 0.010886 | 0.02534 | 0.077464 | 0.11305 | -0.021518 | 59.7469 | 59.7778 | 59.7194 | 59.6317 | 62.2702 | 62.3307 | 61.9579 | 62.2691 | -2.5233 | -2.211 | -2.5507 | -2.2384
859.2656 | 122.3236 | -62.2696 | 59.7839 | 0.13559 | -0.008469 | -0.025735 | -0.01586 | 0.040843 | 0.076426 | -0.058139 | 59.724 | 59.7504 | 59.692 | 59.5951 | 62.2381 | 62.2987 | 61.9258 | 62.2371 | 0.16763 | 0.023574 | 0.006308 | 0.016183 | 0.072886 | 0.10847 | -0.026096 | 59.7561 | 59.7824 | 59.724 | 59.6271 | 62.2702 | 62.3307 | 61.9579 | 62.2691 | -2.5141 | -2.2018 | -2.5462 | -2.2339
861.0156 | 122.2229 | -62.2559 | 59.8618 | 0.13559 | 0.000689 | -0.030314 | -0.020438 | 0.045421 | 0.076426 | -0.058139 | 59.7194 | 59.7504 | 59.6966 | 59.5996 | 62.2427 | 62.2987 | 61.9213 | 62.2371 | 0.16763 | 0.032732 | 0.001729 | 0.011605 | 0.077464 | 0.10847 | -0.026096 | 59.7515 | 59.7824 | 59.7286 | 59.6317 | 62.2748 | 62.3307 | 61.9533 | 62.2691 | -2.5233 | -2.2018 | -2.5462 | -2.2247
862.7656 | 122.2916 | -62.2467 | 59.848 | 0.13559 | 0.005267 | -0.016578 | -0.01586 | 0.049999 | 0.076426 | -0.058139 | 59.7194 | 59.7504 | 59.692 | 59.6088 | 62.2381 | 62.2987 | 61.9304 | 62.2371 | 0.16763 | 0.03731 | 0.015465 | 0.016183 | 0.082042 | 0.10847 | -0.026096 | 59.7515 | 59.7824 | 59.724 | 59.6408 | 62.2702 | 62.3307 | 61.9625 | 62.2691 | -2.5187 | -2.211 | -2.5462 | -2.2384
864.4531 | 122.2321 | -62.3016 | 59.8297 | 0.13559 | 0.005267 | -0.021157 | -0.01586 | 0.045421 | 0.076426 | -0.048983 | 59.724 | 59.7504 | 59.692 | 59.6134 | 62.2336 | 62.2895 | 61.935 | 62.2325 | 0.16763 | 0.03731 | 0.010886 | 0.016183 | 0.077464 | 0.10847 | -0.01694 | 59.7561 | 59.7824 | 59.724 | 59.6454 | 62.2656 | 62.3215 | 61.967 | 62.2646 | -2.5095 | -2.211 | -2.5416 | -2.243
866.2031 | 122.2687 | -62.2513 | 59.8389 | 0.13559 | 0.000689 | -0.012 | -0.01586 | 0.049999 | 0.081005 | -0.053561 | 59.724 | 59.7549 | 59.6966 | 59.6088 | 62.2336 | 62.2895 | 61.9258 | 62.2371 | 0.16763 | 0.032732 | 0.020043 | 0.016183 | 0.082042 | 0.11305 | -0.021518 | 59.7561 | 59.787 | 59.7286 | 59.6408 | 62.2656 | 62.3215 | 61.9579 | 62.2691 | -2.5095 | -2.2018 | -2.537 | -2.2293
867.9531 | 122.3145 | -62.2787 | 59.7748 | 0.13101 | 0.005267 | -0.025735 | -0.011281 | 0.040843 | 0.076426 | -0.048983 | 59.7286 | 59.7549 | 59.6966 | 59.6134 | 62.2336 | 62.2941 | 61.9258 | 62.2234 | 0.16305 | 0.03731 | 0.006308 | 0.020762 | 0.072886 | 0.10847 | -0.01694 | 59.7606 | 59.787 | 59.7286 | 59.6454 | 62.2656 | 62.3261 | 61.9579 | 62.2554 | -2.505 | -2.1972 | -2.537 | -2.2293
869.6406 | 122.287 | -62.2421 | 59.8434 | 0.13559 | 0.005267 | -0.021157 | -0.020438 | 0.049999 | 0.071848 | -0.058139 | 59.7332 | 59.7595 | 59.7057 | 59.6179 | 62.2336 | 62.2895 | 61.9213 | 62.2325 | 0.16763 | 0.03731 | 0.010886 | 0.011605 | 0.082042 | 0.10389 | -0.026096 | 59.7652 | 59.7916 | 59.7378 | 59.65 | 62.2656 | 62.3215 | 61.9533 | 62.2646 | -2.5004 | -2.1881 | -2.5278 | -2.2155
871.3281 | 122.2687 | -62.2467 | 59.8663 | 0.13101 | 0.005267 | -0.025735 | -0.01586 | 0.049999 | 0.076426 | -0.058139 | 59.7332 | 59.7641 | 59.7057 | 59.6134 | 62.229 | 62.2895 | 61.9121 | 62.2188 | 0.16305 | 0.03731 | 0.006308 | 0.016183 | 0.082042 | 0.10847 | -0.026096 | 59.7652 | 59.7961 | 59.7378 | 59.6454 | 62.261 | 62.3215 | 61.9441 | 62.2508 | -2.4958 | -2.1789 | -2.5233 | -2.2064
873.0625 | 122.319 | -62.2421 | 59.8022 | 0.13101 | 0.000689 | -0.021157 | -0.01586 | 0.040843 | 0.071848 | -0.048983 | 59.7332 | 59.7641 | 59.7057 | 59.6134 | 62.229 | 62.2941 | 61.9121 | 62.2234 | 0.16305 | 0.032732 | 0.010886 | 0.016183 | 0.072886 | 0.10389 | -0.01694 | 59.7652 | 59.7961 | 59.7378 | 59.6454 | 62.261 | 62.3261 | 61.9441 | 62.2554 | -2.4958 | -2.1789 | -2.5233 | -2.2064
874.8125 | 122.2595 | -62.2696 | 59.8572 | 0.14474 | 0.000689 | -0.025735 | -0.01586 | 0.045421 | 0.071848 | -0.053561 | 59.7378 | 59.7641 | 59.7011 | 59.6225 | 62.2152 | 62.2849 | 61.9167 | 62.2279 | 0.17679 | 0.032732 | 0.006308 | 0.016183 | 0.077464 | 0.10389 | -0.021518 | 59.7698 | 59.7961 | 59.7332 | 59.6546 | 62.2473 | 62.317 | 61.9487 | 62.26 | -2.4775 | -2.1789 | -2.5141 | -2.2155
876.5781 | 122.2321 | -62.2604 | 59.8389 | 0.12643 | 0.000689 | -0.025735 | -0.020438 | 0.036265 | 0.067269 | -0.053561 | 59.724 | 59.7641 | 59.7057 | 59.6179 | 62.2244 | 62.2849 | 61.9029 | 62.2279 | 0.15847 | 0.032732 | 0.006308 | 0.011605 | 0.068308 | 0.099312 | -0.021518 | 59.7561 | 59.7961 | 59.7378 | 59.65 | 62.2564 | 62.317 | 61.935 | 62.26 | -2.5004 | -2.1789 | -2.5187 | -2.1972
878.2656 | 122.2366 | -62.2421 | 59.8984 | 0.14474 | -0.00389 | -0.021157 | -0.011281 | 0.049999 | 0.067269 | -0.053561 | 59.7378 | 59.7687 | 59.7149 | 59.6317 | 62.2244 | 62.2758 | 61.9075 | 62.2096 | 0.17679 | 0.028153 | 0.010886 | 0.020762 | 0.082042 | 0.099312 | -0.021518 | 59.7698 | 59.8007 | 59.7469 | 59.6637 | 62.2564 | 62.3078 | 61.9396 | 62.2417 | -2.4867 | -2.1698 | -2.5095 | -2.1927
880.0156 | 122.319 | -62.233 | 59.7748 | 0.13101 | 0.005267 | -0.025735 | -0.025017 | 0.036265 | 0.076426 | -0.053561 | 59.7378 | 59.7778 | 59.7103 | 59.6225 | 62.2152 | 62.2712 | 61.9075 | 62.2142 | 0.16305 | 0.03731 | 0.006308 | 0.007026 | 0.068308 | 0.10847 | -0.021518 | 59.7698 | 59.8099 | 59.7423 | 59.6546 | 62.2473 | 62.3032 | 61.9396 | 62.2462 | -2.4775 | -2.1698 | -2.505 | -2.1972
881.7031 | 122.2137 | -62.233 | 59.8618 | 0.13101 | -0.00389 | -0.021157 | -0.01586 | 0.049999 | 0.085583 | -0.058139 | 59.7469 | 59.7778 | 59.7149 | 59.6317 | 62.2107 | 62.2758 | 61.9029 | 62.205 | 0.16305 | 0.028153 | 0.010886 | 0.016183 | 0.082042 | 0.11763 | -0.026096 | 59.779 | 59.8099 | 59.7469 | 59.6637 | 62.2427 | 62.3078 | 61.935 | 62.2371 | -2.4638 | -2.156 | -2.4958 | -2.1881
883.3906 | 122.2504 | -62.2192 | 59.8938 | 0.13559 | 0.000689 | -0.021157 | -0.020438 | 0.040843 | 0.076426 | -0.053561 | 59.7469 | 59.7778 | 59.7195 | 59.6363 | 62.2152 | 62.2666 | 61.9075 | 62.205 | 0.16763 | 0.032732 | 0.010886 | 0.011605 | 0.072886 | 0.10847 | -0.021518 | 59.779 | 59.8099 | 59.7515 | 59.6683 | 62.2473 | 62.2986 | 61.9396 | 62.2371 | -2.4683 | -2.1606 | -2.4958 | -2.1881
885.125 | 122.2229 | -62.2284 | 59.9121 | 0.13101 | 0.000689 | -0.025735 | -0.01586 | 0.045421 | 0.067269 | -0.053561 | 59.7469 | 59.7824 | 59.7195 | 59.6317 | 62.2015 | 62.2666 | 61.8984 | 62.2096 | 0.16305 | 0.032732 | 0.006308 | 0.016183 | 0.077464 | 0.099312 | -0.021518 | 59.779 | 59.8145 | 59.7515 | 59.6637 | 62.2336 | 62.2986 | 61.9304 | 62.2417 | -2.4546 | -2.1515 | -2.4821 | -2.1789
886.8125 | 122.3419 | -62.2147 | 59.8618 | 0.13101 | -0.00389 | -0.025735 | -0.01586 | 0.040843 | 0.062691 | -0.058139 | 59.7606 | 59.7916 | 59.7286 | 59.6363 | 62.2015 | 62.262 | 61.9029 | 62.2005 | 0.16305 | 0.028153 | 0.006308 | 0.016183 | 0.072886 | 0.094734 | -0.026096 | 59.7927 | 59.8236 | 59.7606 | 59.6683 | 62.2336 | 62.2941 | 61.935 | 62.2325 | -2.4409 | -2.1423 | -2.4729 | -2.1743
888.5 | 122.2778 | -62.1964 | 59.8938 | 0.12643 | -0.00389 | -0.030314 | -0.01586 | 0.045421 | 0.076426 | -0.058139 | 59.7561 | 59.8007 | 59.7423 | 59.65 | 62.2061 | 62.2574 | 61.8938 | 62.2005 | 0.15847 | 0.028153 | 0.001729 | 0.016183 | 0.077464 | 0.10847 | -0.026096 | 59.7881 | 59.8328 | 59.7744 | 59.682 | 62.2381 | 62.2895 | 61.9258 | 62.2325 | -2.45 | -2.1377 | -2.4638 | -2.1514
890.1875 | 122.2458 | -62.2375 | 59.903 | 0.14017 | -0.008469 | -0.025735 | -0.01586 | 0.036265 | 0.062691 | -0.053561 | 59.7698 | 59.8007 | 59.7378 | 59.6546 | 62.1924 | 62.2574 | 61.8846 | 62.1913 | 0.17221 | 0.023574 | 0.006308 | 0.016183 | 0.068308 | 0.094734 | -0.021518 | 59.8018 | 59.8328 | 59.7698 | 59.6866 | 62.2244 | 62.2895 | 61.9167 | 62.2234 | -2.4226 | -2.1148 | -2.4546 | -2.1469
891.9375 | 122.2366 | -62.2055 | 59.903 | 0.13559 | -0.008469 | -0.030314 | -0.01586 | 0.040843 | 0.076426 | -0.062717 | 59.7698 | 59.7962 | 59.7378 | 59.6546 | 62.1924 | 62.2483 | 61.8846 | 62.1913 | 0.16763 | 0.023574 | 0.001729 | 0.016183 | 0.072886 | 0.10847 | -0.030674 | 59.8018 | 59.8282 | 59.7698 | 59.6866 | 62.2244 | 62.2803 | 61.9167 | 62.2234 | -2.4226 | -2.1148 | -2.4546 | -2.1469
893.6094 | 122.319 | -62.2055 | 59.8297 | 0.13559 | -0.00389 | -0.025735 | -0.01586 | 0.040843 | 0.071848 | -0.058139 | 59.779 | 59.8007 | 59.7515 | 59.6592 | 62.1786 | 62.2391 | 61.8709 | 62.1822 | 0.16763 | 0.028153 | 0.006308 | 0.016183 | 0.072886 | 0.10389 | -0.026096 | 59.811 | 59.8328 | 59.7835 | 59.6912 | 62.2107 | 62.2712 | 61.9029 | 62.2142 | -2.3997 | -2.0919 | -2.4271 | -2.1194
895.3125 | 122.3282 | -62.2147 | 59.8572 | 0.13559 | -0.008469 | -0.025735 | -0.029595 | 0.027109 | 0.067269 | -0.058139 | 59.7835 | 59.8099 | 59.7469 | 59.6729 | 62.1786 | 62.2391 | 61.8709 | 62.1822 | 0.16763 | 0.023574 | 0.006308 | 0.002448 | 0.059152 | 0.099312 | -0.026096 | 59.8156 | 59.8419 | 59.779 | 59.7049 | 62.2107 | 62.2712 | 61.9029 | 62.2142 | -2.3951 | -2.0874 | -2.4317 | -2.124
897.0625 | 122.2733 | -62.2147 | 59.9075 | 0.13101 | -0.00389 | -0.030314 | -0.011281 | 0.036265 | 0.071848 | -0.058139 | 59.7835 | 59.819 | 59.7607 | 59.6683 | 62.1695 | 62.2391 | 61.8617 | 62.1776 | 0.16305 | 0.028153 | 0.001729 | 0.020762 | 0.068308 | 0.10389 | -0.026096 | 59.8156 | 59.8511 | 59.7927 | 59.7004 | 62.2015 | 62.2712 | 61.8938 | 62.2096 | -2.3859 | -2.0782 | -2.4088 | -2.1011
898.75 | 122.2687 | -62.178 | 59.935 | 0.13101 | -0.008469 | -0.030314 | -0.029595 | 0.040843 | 0.062691 | -0.062717 | 59.7881 | 59.8236 | 59.7607 | 59.6729 | 62.174 | 62.23 | 61.8663 | 62.173 | 0.16305 | 0.023574 | 0.001729 | 0.002448 | 0.072886 | 0.094734 | -0.030674 | 59.8202 | 59.8557 | 59.7927 | 59.7049 | 62.2061 | 62.262 | 61.8984 | 62.205 | -2.3859 | -2.0782 | -2.4134 | -2.1057
900.4375 | 122.3602 | -62.2055 | 59.8343 | 0.13101 | -0.00389 | -0.034893 | -0.025017 | 0.036265 | 0.062691 | -0.053561 | 59.7881 | 59.8282 | 59.7652 | 59.6775 | 62.1603 | 62.2254 | 61.8434 | 62.1684 | 0.16305 | 0.028153 | -0.00285 | 0.007026 | 0.068308 | 0.094734 | -0.021518 | 59.8202 | 59.8602 | 59.7973 | 59.7095 | 62.1924 | 62.2574 | 61.8755 | 62.2005 | -2.3722 | -2.0553 | -2.3951 | -2.0782
902.2031 | 122.2778 | -62.1918 | 59.9213 | 0.13101 | -0.008469 | -0.030314 | -0.01586 | 0.036265 | 0.071848 | -0.058139 | 59.7973 | 59.8282 | 59.7698 | 59.6821 | 62.1603 | 62.2208 | 61.848 | 62.1638 | 0.16305 | 0.023574 | 0.001729 | 0.016183 | 0.068308 | 0.10389 | -0.026096 | 59.8293 | 59.8602 | 59.8019 | 59.7141 | 62.1924 | 62.2529 | 61.88 | 62.1959 | -2.363 | -2.0507 | -2.3905 | -2.0782
903.9375 | 122.287 | -62.178 | 59.9167 | 0.13559 | -0.008469 | -0.034893 | -0.020438 | 0.040843 | 0.067269 | -0.053561 | 59.8019 | 59.8374 | 59.7881 | 59.6958 | 62.1557 | 62.2117 | 61.848 | 62.1501 | 0.16763 | 0.023574 | -0.00285 | 0.011605 | 0.072886 | 0.099312 | -0.021518 | 59.8339 | 59.8694 | 59.8202 | 59.7278 | 62.1878 | 62.2437 | 61.88 | 62.1822 | -2.3539 | -2.0462 | -2.3676 | -2.0599
905.6719 | 122.2549 | -62.1872 | 59.9487 | 0.13101 | -0.00389 | -0.034893 | -0.01586 | 0.027109 | 0.062691 | -0.058139 | 59.8156 | 59.8465 | 59.779 | 59.6958 | 62.1466 | 62.2071 | 61.8434 | 62.1593 | 0.16305 | 0.028153 | -0.00285 | 0.016183 | 0.059152 | 0.094734 | -0.026096 | 59.8476 | 59.8786 | 59.811 | 59.7278 | 62.1786 | 62.2391 | 61.8755 | 62.1913 | -2.331 | -2.0278 | -2.3676 | -2.0645
907.3594 | 122.2137 | -62.2101 | 59.9258 | 0.13101 | -0.008469 | -0.030314 | -0.020438 | 0.045421 | 0.071848 | -0.058139 | 59.8202 | 59.8511 | 59.7881 | 59.7004 | 62.1374 | 62.2025 | 61.8343 | 62.1455 | 0.16305 | 0.023574 | 0.001729 | 0.011605 | 0.077464 | 0.10389 | -0.026096 | 59.8522 | 59.8831 | 59.8202 | 59.7324 | 62.1695 | 62.2346 | 61.8663 | 62.1776 | -2.3173 | -2.0141 | -2.3493 | -2.0461
909.0938 | 122.287 | -62.1368 | 59.935 | 0.13559 | -0.008469 | -0.025735 | -0.020438 | 0.036265 | 0.076426 | -0.058139 | 59.8156 | 59.8465 | 59.7927 | 59.7004 | 62.1374 | 62.1979 | 61.8343 | 62.141 | 0.16763 | 0.023574 | 0.006308 | 0.011605 | 0.068308 | 0.10847 | -0.026096 | 59.8476 | 59.8786 | 59.8247 | 59.7324 | 62.1695 | 62.23 | 61.8663 | 62.173 | -2.3218 | -2.0187 | -2.3447 | -2.0416
910.8438 | 122.3373 | -62.1552 | 59.8892 | 0.12643 | -0.008469 | -0.030314 | -0.020438 | 0.031687 | 0.058113 | -0.058139 | 59.8247 | 59.8648 | 59.8019 | 59.7095 | 62.1283 | 62.1979 | 61.8205 | 62.1318 | 0.15847 | 0.023574 | 0.001729 | 0.011605 | 0.06373 | 0.090156 | -0.026096 | 59.8568 | 59.8969 | 59.8339 | 59.7416 | 62.1603 | 62.23 | 61.8526 | 62.1638 | -2.3035 | -1.9958 | -2.3264 | -2.0187
912.6094 | 122.3282 | -62.1643 | 59.9213 | 0.13559 | -0.00389 | -0.025735 | -0.020438 | 0.036265 | 0.062691 | -0.062717 | 59.8385 | 59.8694 | 59.8019 | 59.7187 | 62.1237 | 62.1842 | 61.8114 | 62.1181 | 0.16763 | 0.028153 | 0.006308 | 0.011605 | 0.068308 | 0.094734 | -0.030674 | 59.8705 | 59.9015 | 59.8339 | 59.7507 | 62.1557 | 62.2162 | 61.8434 | 62.1501 | -2.2852 | -1.9729 | -2.3218 | -2.0095
914.3125 | 122.2778 | -62.1323 | 59.9808 | 0.13559 | -0.00389 | -0.034893 | -0.025017 | 0.040843 | 0.067269 | -0.062717 | 59.8431 | 59.8694 | 59.811 | 59.7278 | 62.1145 | 62.1796 | 61.8068 | 62.1272 | 0.16763 | 0.028153 | -0.00285 | 0.007026 | 0.072886 | 0.099312 | -0.030674 | 59.8751 | 59.9015 | 59.8431 | 59.7599 | 62.1466 | 62.2117 | 61.8388 | 62.1593 | -2.2715 | -1.9637 | -2.3035 | -1.9958
916.0625 | 122.3145 | -62.1094 | 59.9579 | 0.13559 | -0.013048 | -0.034893 | -0.029595 | 0.036265 | 0.062691 | -0.058139 | 59.8476 | 59.8831 | 59.8202 | 59.737 | 62.11 | 62.1705 | 61.8068 | 62.1135 | 0.16763 | 0.018995 | -0.00285 | 0.002448 | 0.068308 | 0.094734 | -0.026096 | 59.8797 | 59.9152 | 59.8522 | 59.769 | 62.142 | 62.2025 | 61.8388 | 62.1455 | -2.2623 | -1.9592 | -2.2898 | -1.9866
917.8281 | 122.3785 | -62.1094 | 59.935 | 0.13101 | -0.008469 | -0.025735 | -0.029595 | 0.031687 | 0.062691 | -0.067295 | 59.8568 | 59.8831 | 59.8248 | 59.7324 | 62.1054 | 62.1659 | 61.7976 | 62.0997 | 0.16305 | 0.023574 | 0.006308 | 0.002448 | 0.06373 | 0.094734 | -0.035252 | 59.8888 | 59.9152 | 59.8568 | 59.7645 | 62.1374 | 62.1979 | 61.8297 | 62.1318 | -2.2486 | -1.9409 | -2.2806 | -1.9729
919.5781 | 122.2275 | -62.1231 | 60.0357 | 0.13101 | -0.008469 | -0.034893 | -0.020438 | 0.027109 | 0.058113 | -0.062717 | 59.8659 | 59.8923 | 59.8339 | 59.7462 | 62.0962 | 62.1522 | 61.7885 | 62.0952 | 0.16305 | 0.023574 | -0.00285 | 0.011605 | 0.059152 | 0.090156 | -0.030674 | 59.898 | 59.9243 | 59.866 | 59.7782 | 62.1283 | 62.1842 | 61.8205 | 62.1272 | -2.2303 | -1.9225 | -2.2623 | -1.9546
921.25 | 122.319 | -62.1185 | 59.9442 | 0.12643 | -0.013048 | -0.04405 | -0.020438 | 0.031687 | 0.053534 | -0.062717 | 59.8659 | 59.906 | 59.8431 | 59.7553 | 62.0962 | 62.1476 | 61.7885 | 62.0997 | 0.15847 | 0.018995 | -0.012007 | 0.011605 | 0.06373 | 0.085577 | -0.030674 | 59.898 | 59.9381 | 59.8751 | 59.7874 | 62.1283 | 62.1796 | 61.8205 | 62.1318 | -2.2303 | -1.9225 | -2.2532 | -1.9454
923 | 122.2549 | -62.1185 | 60.0082 | 0.14017 | -0.00389 | -0.025735 | -0.029595 | 0.036265 | 0.067269 | -0.067295 | 59.8751 | 59.9015 | 59.8476 | 59.7645 | 62.0779 | 62.1476 | 61.7748 | 62.0906 | 0.17221 | 0.028153 | 0.006308 | 0.002448 | 0.068308 | 0.099312 | -0.035252 | 59.9071 | 59.9335 | 59.8797 | 59.7965 | 62.1099 | 62.1796 | 61.8068 | 62.1226 | -2.2028 | -1.8996 | -2.2303 | -1.9271
924.75 | 122.3099 | -62.114 | 59.9808 | 0.13559 | -0.013048 | -0.034893 | -0.029595 | 0.031687 | 0.053534 | -0.071874 | 59.8797 | 59.9152 | 59.8522 | 59.7645 | 62.0779 | 62.1293 | 61.7656 | 62.0769 | 0.16763 | 0.018995 | -0.00285 | 0.002448 | 0.06373 | 0.085577 | -0.039831 | 59.9117 | 59.9472 | 59.8843 | 59.7965 | 62.1099 | 62.1613 | 61.7976 | 62.1089 | -2.1982 | -1.8859 | -2.2257 | -1.9134
926.4375 | 122.2458 | -62.0911 | 60.022 | 0.13101 | -0.008469 | -0.039471 | -0.029595 | 0.027109 | 0.062691 | -0.058139 | 59.898 | 59.9244 | 59.8614 | 59.7828 | 62.0687 | 62.1338 | 61.761 | 62.0723 | 0.16305 | 0.023574 | -0.007428 | 0.002448 | 0.059152 | 0.094734 | -0.026096 | 59.93 | 59.9564 | 59.8934 | 59.8148 | 62.1008 | 62.1659 | 61.7931 | 62.1043 | -2.1707 | -1.863 | -2.2074 | -1.8996
928.1875 | 122.2916 | -62.0819 | 60.0082 | 0.13101 | -0.013048 | -0.030314 | -0.025017 | 0.036265 | 0.053534 | -0.067295 | 59.9072 | 59.9335 | 59.8751 | 59.7828 | 62.0596 | 62.111 | 61.7381 | 62.0585 | 0.16305 | 0.018995 | 0.001729 | 0.007026 | 0.068308 | 0.085577 | -0.035252 | 59.9392 | 59.9656 | 59.9072 | 59.8148 | 62.0916 | 62.143 | 61.7702 | 62.0906 | -2.1524 | -1.831 | -2.1845 | -1.863
929.9375 | 122.3511 | -62.0407 | 59.9487 | 0.13101 | -0.008469 | -0.034893 | -0.029595 | 0.027109 | 0.058113 | -0.067295 | 59.9163 | 59.9518 | 59.8843 | 59.7965 | 62.0413 | 62.0972 | 61.7244 | 62.0402 | 0.16305 | 0.023574 | -0.00285 | 0.002448 | 0.059152 | 0.090156 | -0.035252 | 59.9484 | 59.9839 | 59.9163 | 59.8286 | 62.0733 | 62.1293 | 61.7564 | 62.0723 | -2.125 | -1.8081 | -2.157 | -1.8401
931.6875 | 122.287 | -62.0453 | 60.0632 | 0.14017 | -0.017627 | -0.039471 | -0.025017 | 0.031687 | 0.053534 | -0.062717 | 59.9346 | 59.9701 | 59.9072 | 59.8148 | 62.023 | 62.0881 | 61.7152 | 62.0311 | 0.17221 | 0.014416 | -0.007428 | 0.007026 | 0.06373 | 0.085577 | -0.030674 | 59.9667 | 60.0022 | 59.9392 | 59.8469 | 62.055 | 62.1201 | 61.7473 | 62.0631 | -2.0883 | -1.7806 | -2.1158 | -1.8081
933.375 | 122.319 | -62.0132 | 60.0494 | 0.13101 | -0.017627 | -0.04405 | -0.025017 | 0.027109 | 0.058113 | -0.071874 | 59.9438 | 59.9793 | 59.9117 | 59.824 | 62.023 | 62.0697 | 61.7107 | 62.0128 | 0.16305 | 0.014416 | -0.012007 | 0.007026 | 0.059152 | 0.090156 | -0.039831 | 59.9758 | 60.0113 | 59.9438 | 59.856 | 62.055 | 62.1018 | 61.7427 | 62.0448 | -2.0792 | -1.7669 | -2.1112 | -1.7989
935.1094 | 122.2458 | -62.0224 | 60.0952 | 0.14017 | -0.013048 | -0.048628 | -0.034174 | 0.027109 | 0.062691 | -0.071874 | 59.9575 | 59.9885 | 59.9209 | 59.8469 | 62.0001 | 62.056 | 61.6969 | 62.0036 | 0.17221 | 0.018995 | -0.016585 | -0.002131 | 0.059152 | 0.094734 | -0.039831 | 59.9896 | 60.0205 | 59.9529 | 59.8789 | 62.0321 | 62.0881 | 61.729 | 62.0356 | -2.0426 | -1.7394 | -2.0792 | -1.776
936.7812 | 122.2092 | -62.0407 | 60.1044 | 0.13559 | -0.022205 | -0.04405 | -0.034174 | 0.031687 | 0.053534 | -0.071874 | 59.985 | 60.0205 | 59.9529 | 59.8652 | 61.9863 | 62.0331 | 61.6603 | 61.9807 | 0.16763 | 0.009838 | -0.012007 | -0.002131 | 0.06373 | 0.085577 | -0.039831 | 60.017 | 60.0526 | 59.985 | 59.8973 | 62.0184 | 62.0652 | 61.6923 | 62.0128 | -2.0014 | -1.6753 | -2.0334 | -1.7073
938.5312 | 122.2641 | -61.9858 | 60.141 | 0.12643 | -0.013048 | -0.048628 | -0.029595 | 0.022531 | 0.053534 | -0.076452 | 59.9987 | 60.0297 | 59.9758 | 59.8835 | 61.968 | 62.0194 | 61.6557 | 61.9578 | 0.15847 | 0.018995 | -0.016585 | 0.002448 | 0.054574 | 0.085577 | -0.044409 | 60.0308 | 60.0617 | 60.0079 | 59.9156 | 62.0001 | 62.0514 | 61.6878 | 61.9899 | -1.9693 | -1.657 | -1.9922 | -1.6799
940.2188 | 122.3373 | -61.9583 | 60.0815 | 0.13101 | -0.022205 | -0.048628 | -0.034174 | 0.017953 | 0.048956 | -0.076452 | 60.017 | 60.0434 | 59.9804 | 59.8881 | 61.9589 | 62.0194 | 61.642 | 61.9578 | 0.16305 | 0.009838 | -0.016585 | -0.002131 | 0.049996 | 0.080999 | -0.044409 | 60.0491 | 60.0755 | 60.0125 | 59.9202 | 61.9909 | 62.0514 | 61.674 | 61.9899 | -1.9418 | -1.6249 | -1.9785 | -1.6616
941.9688 | 122.3511 | -61.94 | 60.1044 | 0.13101 | -0.031363 | -0.053207 | -0.047909 | 0.027109 | 0.044377 | -0.08103 | 60.017 | 60.048 | 59.9941 | 59.9018 | 61.9451 | 62.0057 | 61.6282 | 61.9441 | 0.16305 | 0.00068 | -0.021164 | -0.015866 | 0.059152 | 0.07642 | -0.048987 | 60.0491 | 60.08 | 60.0262 | 59.9339 | 61.9772 | 62.0377 | 61.6603 | 61.9761 | -1.9281 | -1.6112 | -1.951 | -1.6341
943.7188 | 122.3419 | -61.9217 | 60.0952 | 0.14017 | -0.017627 | -0.048628 | -0.043331 | 0.022531 | 0.053534 | -0.076452 | 60.0445 | 60.0755 | 60.0125 | 59.9247 | 61.9268 | 61.9828 | 61.6008 | 61.9166 | 0.17221 | 0.014416 | -0.016585 | -0.011288 | 0.054574 | 0.085577 | -0.044409 | 60.0766 | 60.1075 | 60.0445 | 59.9568 | 61.9589 | 62.0148 | 61.6328 | 61.9487 | -1.8823 | -1.5563 | -1.9144 | -1.5883
945.4219 | 122.3557 | -61.8759 | 60.1456 | 0.13101 | -0.026784 | -0.04405 | -0.043331 | 0.013375 | 0.048956 | -0.08103 | 60.0491 | 60.0892 | 60.0262 | 59.9339 | 61.9039 | 61.9599 | 61.5916 | 61.9166 | 0.16305 | 0.005259 | -0.012007 | -0.011288 | 0.045418 | 0.080999 | -0.048987 | 60.0811 | 60.1212 | 60.0582 | 59.9659 | 61.936 | 61.9919 | 61.6237 | 61.9487 | -1.8548 | -1.5425 | -1.8777 | -1.5654
947.1719 | 122.2733 | -61.9171 | 60.2005 | 0.13101 | -0.026784 | -0.04405 | -0.034174 | 0.022531 | 0.048956 | -0.076452 | 60.0857 | 60.1029 | 60.0537 | 59.9614 | 61.8902 | 61.9416 | 61.5779 | 61.8846 | 0.16305 | 0.005259 | -0.012007 | -0.002131 | 0.054574 | 0.080999 | -0.044409 | 60.1178 | 60.135 | 60.0857 | 59.9934 | 61.9222 | 61.9736 | 61.6099 | 61.9166 | -1.8045 | -1.4922 | -1.8365 | -1.5242
948.9062 | 122.3373 | -61.8576 | 60.173 | 0.13559 | -0.022205 | -0.057786 | -0.038752 | 0.017953 | 0.039799 | -0.08103 | 60.0949 | 60.1304 | 60.0674 | 59.9797 | 61.8719 | 61.9232 | 61.555 | 61.8708 | 0.16763 | 0.009838 | -0.025743 | -0.006709 | 0.049996 | 0.071842 | -0.048987 | 60.1269 | 60.1624 | 60.0994 | 60.0117 | 61.9039 | 61.9553 | 61.587 | 61.9029 | -1.777 | -1.4601 | -1.8045 | -1.4876
950.6562 | 122.2778 | -61.8759 | 60.2463 | 0.13101 | -0.031363 | -0.053207 | -0.038752 | 0.013375 | 0.048956 | -0.076452 | 60.1086 | 60.1396 | 60.0811 | 59.9888 | 61.8627 | 61.9095 | 61.5458 | 61.8525 | 0.16305 | 0.00068 | -0.021164 | -0.006709 | 0.045418 | 0.080999 | -0.044409 | 60.1407 | 60.1716 | 60.1132 | 60.0209 | 61.8948 | 61.9416 | 61.5779 | 61.8846 | -1.7541 | -1.4372 | -1.7816 | -1.4647
952.3438 | 122.2275 | -61.8713 | 60.2737 | 0.13559 | -0.031363 | -0.053207 | -0.043331 | 0.004219 | 0.048956 | -0.08103 | 60.1407 | 60.1625 | 60.104 | 60.0163 | 61.8261 | 61.8912 | 61.5184 | 61.8296 | 0.16763 | 0.00068 | -0.021164 | -0.011288 | 0.036262 | 0.080999 | -0.048987 | 60.1727 | 60.1945 | 60.1361 | 60.0484 | 61.8581 | 61.9232 | 61.5504 | 61.8617 | -1.6854 | -1.3777 | -1.7221 | -1.4143
954.0938 | 122.3465 | -61.821 | 60.2234 | 0.12643 | -0.040521 | -0.053207 | -0.052488 | 0.008797 | 0.048956 | -0.085608 | 60.1636 | 60.1854 | 60.1315 | 60.0438 | 61.8078 | 61.8683 | 61.4955 | 61.8022 | 0.15847 | -0.008478 | -0.021164 | -0.020445 | 0.04084 | 0.080999 | -0.053565 | 60.1956 | 60.2174 | 60.1635 | 60.0758 | 61.8398 | 61.9004 | 61.5275 | 61.8342 | -1.6442 | -1.3319 | -1.6763 | -1.364
955.8438 | 122.2641 | -61.821 | 60.2829 | 0.13101 | -0.035942 | -0.053207 | -0.043331 | 0.017953 | 0.039799 | -0.085608 | 60.1956 | 60.2174 | 60.1544 | 60.0667 | 61.7849 | 61.8408 | 61.4634 | 61.7884 | 0.16305 | -0.003899 | -0.021164 | -0.011288 | 0.049996 | 0.071842 | -0.053565 | 60.2276 | 60.2494 | 60.1864 | 60.0987 | 61.8169 | 61.8729 | 61.4955 | 61.8205 | -1.5893 | -1.2678 | -1.6305 | -1.309
957.5938 | 122.2733 | -61.8027 | 60.2966 | 0.14017 | -0.031363 | -0.062364 | -0.052488 | 0.013375 | 0.039799 | -0.076452 | 60.2093 | 60.2357 | 60.1819 | 60.0804 | 61.7529 | 61.818 | 61.4451 | 61.7564 | 0.17221 | 0.00068 | -0.030321 | -0.020445 | 0.045418 | 0.071842 | -0.044409 | 60.2414 | 60.2678 | 60.2139 | 60.1125 | 61.7849 | 61.85 | 61.4772 | 61.7884 | -1.5435 | -1.2358 | -1.571 | -1.2633
959.2656 | 122.4014 | -61.7294 | 60.3653 | 0.13101 | -0.040521 | -0.062364 | -0.047909 | -0.000359 | 0.039799 | -0.094765 | 60.2368 | 60.2723 | 60.2093 | 60.1262 | 61.7162 | 61.7813 | 61.4131 | 61.7289 | 0.16305 | -0.008478 | -0.030321 | -0.015866 | 0.031684 | 0.071842 | -0.062722 | 60.2689 | 60.3044 | 60.2414 | 60.1583 | 61.7483 | 61.8134 | 61.4451 | 61.761 | -1.4794 | -1.1763 | -1.5069 | -1.2037
961 | 122.3282 | -61.7111 | 60.3241 | 0.14017 | -0.0451 | -0.062364 | -0.052488 | 0.004219 | 0.039799 | -0.085608 | 60.2597 | 60.2907 | 60.2231 | 60.14 | 61.7025 | 61.763 | 61.3947 | 61.706 | 0.17221 | -0.013057 | -0.030321 | -0.020445 | 0.036262 | 0.071842 | -0.053565 | 60.2917 | 60.3227 | 60.2551 | 60.172 | 61.7345 | 61.7951 | 61.4268 | 61.7381 | -1.4428 | -1.135 | -1.4794 | -1.1717
962.7344 | 122.2733 | -61.702 | 60.4294 | 0.13559 | -0.040521 | -0.062364 | -0.052488 | 0.004219 | 0.035221 | -0.090186 | 60.2963 | 60.3273 | 60.2688 | 60.1812 | 61.6659 | 61.7264 | 61.349 | 61.6694 | 0.16763 | -0.008478 | -0.030321 | -0.020445 | 0.036262 | 0.067264 | -0.058143 | 60.3284 | 60.3593 | 60.3009 | 60.2132 | 61.6979 | 61.7584 | 61.381 | 61.7014 | -1.3695 | -1.0526 | -1.397 | -1.0801
964.4219 | 122.3328 | -61.6882 | 60.3882 | 0.12643 | -0.040521 | -0.062364 | -0.061645 | -0.000359 | 0.026064 | -0.090186 | 60.3146 | 60.341 | 60.278 | 60.2041 | 61.6521 | 61.7127 | 61.3398 | 61.6511 | 0.15847 | -0.008478 | -0.030321 | -0.029602 | 0.031684 | 0.058107 | -0.058143 | 60.3467 | 60.3731 | 60.31 | 60.2361 | 61.6842 | 61.7447 | 61.3718 | 61.6831 | -1.3375 | -1.0252 | -1.3741 | -1.0618
966.1719 | 122.2412 | -61.6425 | 60.5026 | 0.13101 | -0.049678 | -0.066943 | -0.057066 | -0.004937 | 0.030642 | -0.090186 | 60.3421 | 60.3822 | 60.3192 | 60.2224 | 61.6201 | 61.6806 | 61.3078 | 61.619 | 0.16305 | -0.017635 | -0.0349 | -0.025023 | 0.027106 | 0.062685 | -0.058143 | 60.3742 | 60.4143 | 60.3512 | 60.2544 | 61.6521 | 61.7127 | 61.3398 | 61.6511 | -1.278 | -0.96564 | -1.3009 | -0.98855
967.9219 | 122.3099 | -61.6425 | 60.4523 | 0.13559 | -0.049678 | -0.066943 | -0.066223 | -0.004937 | 0.030642 | -0.094765 | 60.3787 | 60.4097 | 60.3375 | 60.2499 | 61.5972 | 61.644 | 61.2803 | 61.5916 | 0.16763 | -0.017635 | -0.0349 | -0.03418 | 0.027106 | 0.062685 | -0.062722 | 60.4108 | 60.4418 | 60.3696 | 60.2819 | 61.6292 | 61.676 | 61.3123 | 61.6236 | -1.2185 | -0.90155 | -1.2597 | -0.94277
969.6719 | 122.2412 | -61.5646 | 60.5759 | 0.13101 | -0.049678 | -0.071521 | -0.057066 | 0.004219 | 0.026064 | -0.090186 | 60.4016 | 60.4326 | 60.3787 | 60.2911 | 61.5606 | 61.6211 | 61.2437 | 61.5687 | 0.16305 | -0.017635 | -0.039478 | -0.025023 | 0.036262 | 0.058107 | -0.058143 | 60.4337 | 60.4646 | 60.4108 | 60.3231 | 61.5926 | 61.6531 | 61.2757 | 61.6007 | -1.1589 | -0.84203 | -1.1818 | -0.86494
971.3438 | 122.3145 | -61.5646 | 60.4889 | 0.13101 | -0.049678 | -0.080679 | -0.066223 | -0.004937 | 0.026064 | -0.099343 | 60.4337 | 60.4692 | 60.397 | 60.3185 | 61.5377 | 61.5891 | 61.2162 | 61.5366 | 0.16305 | -0.017635 | -0.048636 | -0.03418 | 0.027106 | 0.058107 | -0.0673 | 60.4657 | 60.5013 | 60.4291 | 60.3506 | 61.5697 | 61.6211 | 61.2482 | 61.5687 | -1.104 | -0.78251 | -1.1406 | -0.81915
973.0938 | 122.3282 | -61.5189 | 60.5347 | 0.12643 | -0.058836 | -0.085257 | -0.061645 | -0.009515 | 0.021485 | -0.099343 | 60.4703 | 60.5059 | 60.4382 | 60.3598 | 61.4965 | 61.557 | 61.1704 | 61.5 | 0.15847 | -0.026793 | -0.053214 | -0.029602 | 0.022528 | 0.053528 | -0.0673 | 60.5024 | 60.5379 | 60.4703 | 60.3918 | 61.5285 | 61.589 | 61.2024 | 61.532 | -1.0262 | -0.70009 | -1.0582 | -0.73216
974.8438 | 122.3465 | -61.4182 | 60.6262 | 0.14017 | -0.054257 | -0.071521 | -0.061645 | -0.009515 | 0.021485 | -0.099343 | 60.5253 | 60.5517 | 60.4932 | 60.4055 | 61.4415 | 61.4975 | 61.1292 | 61.4405 | 0.17221 | -0.022214 | -0.039478 | -0.029602 | 0.022528 | 0.053528 | -0.0673 | 60.5573 | 60.5837 | 60.5252 | 60.4376 | 61.4736 | 61.5295 | 61.1612 | 61.4725 | -0.91629 | -0.60395 | -0.94836 | -0.63602
976.5938 | 122.3236 | -61.3861 | 60.64 | 0.12643 | -0.058836 | -0.080679 | -0.070802 | -0.018671 | 0.016907 | -0.1085 | 60.5939 | 60.6295 | 60.5573 | 60.4696 | 61.3683 | 61.4242 | 61.0651 | 61.381 | 0.15847 | -0.026793 | -0.048636 | -0.038759 | 0.013372 | 0.04895 | -0.076456 | 60.626 | 60.6615 | 60.5893 | 60.5017 | 61.4003 | 61.4563 | 61.0971 | 61.413 | -0.77436 | -0.47117 | -0.81101 | -0.50783
978.2812 | 122.3557 | -61.3174 | 60.6995 | 0.13101 | -0.063415 | -0.0761 | -0.070802 | -0.009515 | 0.021485 | -0.1085 | 60.6672 | 60.6982 | 60.6351 | 60.5429 | 61.2996 | 61.3556 | 60.9827 | 61.2986 | 0.16305 | -0.031372 | -0.044057 | -0.038759 | 0.022528 | 0.053528 | -0.076456 | 60.6992 | 60.7302 | 60.6671 | 60.575 | 61.3317 | 61.3876 | 61.0147 | 61.3306 | -0.63243 | -0.31551 | -0.66451 | -0.34759
980.0312 | 122.2687 | -61.2946 | 60.7819 | 0.13101 | -0.058836 | -0.0761 | -0.061645 | -0.023249 | 0.016907 | -0.10392 | 60.6809 | 60.7073 | 60.6488 | 60.5566 | 61.2859 | 61.351 | 60.9644 | 61.2894 | 0.16305 | -0.026793 | -0.044057 | -0.029602 | 0.008794 | 0.04895 | -0.071878 | 60.713 | 60.7394 | 60.6809 | 60.5887 | 61.3179 | 61.383 | 60.9964 | 61.3215 | -0.60496 | -0.28346 | -0.63704 | -0.31554
981.7812 | 122.3373 | -61.3129 | 60.7727 | 0.12185 | -0.067994 | -0.089836 | -0.07538 | -0.018671 | 0.016907 | -0.1085 | 60.7038 | 60.7348 | 60.6672 | 60.5704 | 61.2676 | 61.3281 | 60.9552 | 61.2665 | 0.15389 | -0.035951 | -0.057793 | -0.043337 | 0.013372 | 0.04895 | -0.076456 | 60.7359 | 60.7669 | 60.6992 | 60.6024 | 61.2996 | 61.3601 | 60.9873 | 61.2986 | -0.56375 | -0.25141 | -0.60041 | -0.28807
983.5312 | 122.3145 | -61.2442 | 60.8047 | 0.14017 | -0.067994 | -0.089836 | -0.079959 | -0.014093 | 0.003172 | -0.1085 | 60.7404 | 60.776 | 60.7129 | 60.6208 | 61.2172 | 61.2732 | 60.9232 | 61.2207 | 0.17221 | -0.035951 | -0.057793 | -0.047916 | 0.01795 | 0.035215 | -0.076456 | 60.7725 | 60.8081 | 60.745 | 60.6528 | 61.2493 | 61.3052 | 60.9552 | 61.2528 | -0.47677 | -0.18273 | -0.50427 | -0.21023
985.2031 | 122.2733 | -61.171 | 60.9787 | 0.12643 | -0.063415 | -0.080679 | -0.070802 | -0.014093 | 0.016907 | -0.1085 | 60.8274 | 60.8493 | 60.7999 | 60.7078 | 61.144 | 61.1953 | 60.827 | 61.1475 | 0.15847 | -0.031372 | -0.048636 | -0.038759 | 0.01795 | 0.04895 | -0.076456 | 60.8595 | 60.8813 | 60.832 | 60.7398 | 61.176 | 61.2274 | 60.8591 | 61.1795 | -0.31652 | 0.000408 | -0.34403 | -0.0271
986.9531 | 122.2275 | -61.0931 | 60.9924 | 0.13101 | -0.072572 | -0.085257 | -0.07538 | -0.023249 | 0.00775 | -0.11308 | 60.8503 | 60.8768 | 60.8228 | 60.7352 | 61.1211 | 61.1679 | 60.8133 | 61.1154 | 0.16305 | -0.040529 | -0.053214 | -0.043337 | 0.008794 | 0.039793 | -0.081034 | 60.8824 | 60.9088 | 60.8549 | 60.7673 | 61.1531 | 61.1999 | 60.8453 | 61.1475 | -0.27074 | 0.037035 | -0.29825 | 0.009526
988.7031 | 122.2824 | -61.1069 | 60.965 | 0.13101 | -0.063415 | -0.094414 | -0.070802 | -0.018671 | 0.00775 | -0.11765 | 60.887 | 60.9134 | 60.8503 | 60.7581 | 61.089 | 61.145 | 60.7721 | 61.088 | 0.16305 | -0.031372 | -0.062371 | -0.038759 | 0.013372 | 0.039793 | -0.085612 | 60.919 | 60.9454 | 60.8823 | 60.7902 | 61.1211 | 61.177 | 60.8041 | 61.12 | -0.20207 | 0.11487 | -0.23873 | 0.078201
990.4688 | 122.287 | -61.0291 | 61.0794 | 0.13101 | -0.072572 | -0.089836 | -0.079959 | -0.027827 | 0.00775 | -0.11765 | 60.9511 | 60.9821 | 60.919 | 60.8268 | 61.0249 | 61.0763 | 60.7034 | 61.0147 | 0.16305 | -0.040529 | -0.057793 | -0.047916 | 0.004216 | 0.039793 | -0.085612 | 60.9831 | 61.0141 | 60.951 | 60.8589 | 61.057 | 61.1084 | 60.7355 | 61.0468 | -0.073873 | 0.24764 | -0.10597 | 0.21555
992.1562 | 122.2366 | -61.0016 | 61.1435 | 0.12643 | -0.077151 | -0.089836 | -0.084537 | -0.032405 | 0.003172 | -0.11765 | 60.9968 | 61.0279 | 60.9693 | 60.8863 | 60.9746 | 61.0305 | 60.6576 | 60.9735 | 0.15847 | -0.045108 | -0.057793 | -0.052494 | -0.000362 | 0.035215 | -0.085612 | 61.0289 | 61.0599 | 61.0014 | 60.9184 | 61.0066 | 61.0626 | 60.6897 | 61.0056 | 0.022272 | 0.33921 | -0.005244 | 0.3117
993.9062 | 122.3236 | -60.9558 | 61.1023 | 0.13101 | -0.077151 | -0.10357 | -0.079959 | -0.027827 | 0.003172 | -0.12223 | 61.0472 | 61.0736 | 61.0105 | 60.9184 | 60.9334 | 60.9893 | 60.621 | 60.9369 | 0.16305 | -0.045108 | -0.071529 | -0.047916 | 0.004216 | 0.035215 | -0.090191 | 61.0792 | 61.1057 | 61.0426 | 60.9504 | 60.9654 | 61.0214 | 60.653 | 60.9689 | 0.11384 | 0.4262 | 0.077164 | 0.38953
995.5938 | 122.2321 | -60.9238 | 61.1847 | 0.13101 | -0.067994 | -0.094414 | -0.084537 | -0.023249 | 0.00775 | -0.11765 | 61.0701 | 61.1103 | 61.0426 | 60.955 | 60.8922 | 60.9435 | 60.5844 | 60.8957 | 0.16305 | -0.035951 | -0.062371 | -0.052494 | 0.008794 | 0.039793 | -0.085612 | 61.1021 | 61.1423 | 61.0746 | 60.9871 | 60.9242 | 60.9756 | 60.6164 | 60.9277 | 0.17793 | 0.48572 | 0.15041 | 0.4582
997.2656 | 122.2916 | -60.8276 | 61.2854 | 0.13101 | -0.077151 | -0.098993 | -0.084537 | -0.032405 | 0.003172 | -0.12223 | 61.1662 | 61.1927 | 61.1341 | 61.042 | 60.8052 | 60.8611 | 60.4882 | 60.8087 | 0.16305 | -0.045108 | -0.06695 | -0.052494 | -0.000362 | 0.035215 | -0.090191 | 61.1983 | 61.2247 | 61.1662 | 61.0741 | 60.8372 | 60.8932 | 60.5203 | 60.8407 | 0.36107 | 0.67802 | 0.32897 | 0.64591
999.0312 | 122.2778 | -60.7773 | 61.3678 | 0.13559 | -0.077151 | -0.094414 | -0.084537 | -0.023249 | 0.003172 | -0.12223 | 61.2258 | 61.2614 | 61.1982 | 61.1061 | 60.7411 | 60.8016 | 60.4241 | 60.74 | 0.16763 | -0.045108 | -0.062371 | -0.052494 | 0.008794 | 0.035215 | -0.090191 | 61.2578 | 61.2934 | 61.2303 | 61.1382 | 60.7731 | 60.8337 | 60.4562 | 60.7721 | 0.48468 | 0.80164 | 0.45716 | 0.77411
1000.7188 | 122.3145 | -60.7178 | 61.377 | 0.12185 | -0.077151 | -0.10357 | -0.093694 | -0.036983 | -0.005985 | -0.12223 | 61.2853 | 61.3117 | 61.2532 | 61.1702 | 60.6816 | 60.7421 | 60.3738 | 60.6851 | 0.15389 | -0.045108 | -0.071529 | -0.061651 | -0.00494 | 0.026058 | -0.090191 | 61.3173 | 61.3438 | 61.2852 | 61.2023 | 60.7136 | 60.7742 | 60.4058 | 60.7171 | 0.60372 | 0.91152 | 0.57161 | 0.87941
1002.4062 | 122.3419 | -60.6262 | 61.409 | 0.12185 | -0.08173 | -0.10815 | -0.093694 | -0.036983 | -0.001406 | -0.13139 | 61.3494 | 61.3758 | 61.3173 | 61.2298 | 60.622 | 60.6826 | 60.3005 | 60.6302 | 0.15389 | -0.049687 | -0.076107 | -0.061651 | -0.00494 | 0.030637 | -0.099347 | 61.3814 | 61.4079 | 61.3493 | 61.2618 | 60.6541 | 60.7146 | 60.3326 | 60.6622 | 0.72734 | 1.0489 | 0.69522 | 1.0168
1004.1562 | 122.2137 | -60.5301 | 61.5967 | 0.12185 | -0.086309 | -0.10815 | -0.098273 | -0.041561 | -0.005985 | -0.13139 | 61.4501 | 61.4812 | 61.4088 | 61.3213 | 60.5259 | 60.5819 | 60.2181 | 60.5294 | 0.15389 | -0.054266 | -0.076107 | -0.06623 | -0.009518 | 0.026058 | -0.099347 | 61.4822 | 61.5132 | 61.4409 | 61.3534 | 60.5579 | 60.6139 | 60.2501 | 60.5615 | 0.9242 | 1.232 | 0.88293 | 1.1907
1005.9062 | 122.3373 | -60.4385 | 61.5967 | 0.12643 | -0.090888 | -0.11273 | -0.093694 | -0.041561 | -0.010563 | -0.13139 | 61.5508 | 61.5819 | 61.5141 | 61.4267 | 60.416 | 60.4766 | 60.1036 | 60.4196 | 0.15847 | -0.058845 | -0.080686 | -0.061651 | -0.009518 | 0.02148 | -0.099347 | 61.5829 | 61.6139 | 61.5462 | 61.4587 | 60.4481 | 60.5086 | 60.1357 | 60.4516 | 1.1348 | 1.4472 | 1.0981 | 1.4105
1007.6562 | 122.2137 | -60.347 | 61.7569 | 0.13101 | -0.090888 | -0.11731 | -0.098273 | -0.041561 | -0.015142 | -0.13597 | 61.6607 | 61.6964 | 61.6377 | 61.5457 | 60.3062 | 60.3667 | 60.0029 | 60.3097 | 0.16305 | -0.058845 | -0.085264 | -0.06623 | -0.009518 | 0.016901 | -0.10393 | 61.6928 | 61.7284 | 61.6698 | 61.5778 | 60.3382 | 60.3987 | 60.035 | 60.3417 | 1.3546 | 1.6578 | 1.3316 | 1.6348
1009.3438 | 122.2458 | -60.26 | 61.8576 | 0.13101 | -0.10004 | -0.11731 | -0.098273 | -0.050716 | -0.010563 | -0.14055 | 61.7294 | 61.765 | 61.6973 | 61.619 | 60.2375 | 60.3026 | 59.9342 | 60.2364 | 0.16305 | -0.068002 | -0.085264 | -0.06623 | -0.018673 | 0.02148 | -0.1085 | 61.7614 | 61.7971 | 61.7293 | 61.651 | 60.2695 | 60.3347 | 59.9663 | 60.2685 | 1.4919 | 1.7952 | 1.4598 | 1.763
1011.0938 | 122.3785 | -60.1273 | 61.9263 | 0.12185 | -0.10004 | -0.11273 | -0.10743 | -0.055294 | -0.015142 | -0.14055 | 61.821 | 61.8475 | 61.7888 | 61.6922 | 60.1551 | 60.2065 | 59.8381 | 60.1494 | 0.15389 | -0.068002 | -0.080686 | -0.075387 | -0.023251 | 0.016901 | -0.1085 | 61.853 | 61.8795 | 61.8209 | 61.7243 | 60.1871 | 60.2385 | 59.8701 | 60.1815 | 1.6659 | 1.9829 | 1.6338 | 1.9507
1012.8438 | 122.374 | -60.054 | 61.9766 | 0.12643 | -0.10462 | -0.11273 | -0.098273 | -0.046138 | -0.015142 | -0.14512 | 61.9263 | 61.9528 | 61.8987 | 61.8113 | 60.036 | 60.092 | 59.7282 | 60.0487 | 0.15847 | -0.072581 | -0.080686 | -0.06623 | -0.014095 | 0.016901 | -0.11308 | 61.9583 | 61.9848 | 61.9308 | 61.8433 | 60.0681 | 60.1241 | 59.7603 | 60.0808 | 1.8902 | 2.1981 | 1.8627 | 2.1705
1014.5781 | 122.3557 | -59.9716 | 62.0956 | 0.12643 | -0.10004 | -0.12189 | -0.10743 | -0.050716 | -0.01972 | -0.1497 | 62.0178 | 62.0398 | 61.9811 | 61.8937 | 59.9582 | 60.0142 | 59.6458 | 59.9572 | 0.15847 | -0.068002 | -0.089843 | -0.075387 | -0.018673 | 0.012323 | -0.11766 | 62.0499 | 62.0718 | 62.0132 | 61.9258 | 59.9903 | 60.0462 | 59.6778 | 59.9892 | 2.0596 | 2.372 | 2.0229 | 2.3353
1016.2656 | 122.3648 | -59.8434 | 62.1918 | 0.12185 | -0.10004 | -0.12189 | -0.10285 | -0.046138 | -0.01972 | -0.14512 | 62.1231 | 62.1588 | 62.0956 | 62.0174 | 59.8438 | 59.8997 | 59.5176 | 59.8427 | 0.15389 | -0.068002 | -0.089843 | -0.070808 | -0.014095 | 0.012323 | -0.11308 | 62.1552 | 62.1909 | 62.1276 | 62.0494 | 59.8758 | 59.9318 | 59.5496 | 59.8748 | 2.2794 | 2.6055 | 2.2518 | 2.578
1018.0312 | 122.3236 | -59.8022 | 62.2559 | 0.12185 | -0.10004 | -0.12189 | -0.11201 | -0.055294 | -0.01972 | -0.14055 | 62.201 | 62.2321 | 62.1734 | 62.086 | 59.7659 | 59.8265 | 59.4444 | 59.7649 | 0.15389 | -0.068002 | -0.089843 | -0.079965 | -0.023251 | 0.012323 | -0.1085 | 62.233 | 62.2641 | 62.2055 | 62.1181 | 59.798 | 59.8585 | 59.4764 | 59.7969 | 2.4351 | 2.7566 | 2.4075 | 2.7291
1019.7812 | 122.2504 | -59.761 | 62.3749 | 0.12643 | -0.10462 | -0.13562 | -0.11201 | -0.050716 | -0.01972 | -0.13139 | 62.233 | 62.2641 | 62.1963 | 62.1135 | 59.7385 | 59.799 | 59.4215 | 59.7328 | 0.15847 | -0.072581 | -0.10358 | -0.079965 | -0.018673 | 0.012323 | -0.099347 | 62.2651 | 62.2962 | 62.2283 | 62.1456 | 59.7705 | 59.8311 | 59.4535 | 59.7649 | 2.4946 | 2.8116 | 2.4578 | 2.7748
1021.4688 | 122.3557 | -59.6237 | 62.4115 | 0.12643 | -0.10004 | -0.12646 | -0.10743 | -0.050716 | -0.01972 | -0.14055 | 62.3521 | 62.3832 | 62.3153 | 62.2326 | 59.6148 | 59.68 | 59.2978 | 59.6184 | 0.15847 | -0.068002 | -0.094422 | -0.075387 | -0.018673 | 0.012323 | -0.1085 | 62.3841 | 62.4152 | 62.3474 | 62.2646 | 59.6469 | 59.712 | 59.3299 | 59.6504 | 2.7372 | 3.0542 | 2.7005 | 3.0175
1023.2188 | 122.3694 | -59.5047 | 62.5031 | 0.11269 | -0.10462 | -0.12646 | -0.10743 | -0.059872 | -0.010563 | -0.14055 | 62.4711 | 62.4977 | 62.4298 | 62.3425 | 59.505 | 59.561 | 59.188 | 59.5039 | 0.14474 | -0.072581 | -0.094422 | -0.075387 | -0.027829 | 0.02148 | -0.1085 | 62.5032 | 62.5297 | 62.4618 | 62.3745 | 59.537 | 59.593 | 59.22 | 59.536 | 2.9661 | 3.2832 | 2.9248 | 3.2418
1024.9688 | 122.2366 | -59.4086 | 62.7228 | 0.12185 | -0.10004 | -0.13562 | -0.10743 | -0.050716 | -0.01972 | -0.14512 | 62.6176 | 62.6442 | 62.5809 | 62.4982 | 59.3493 | 59.4145 | 59.0369 | 59.3574 | 0.15389 | -0.068002 | -0.10358 | -0.075387 | -0.018673 | 0.012323 | -0.11308 | 62.6497 | 62.6762 | 62.6129 | 62.5302 | 59.3814 | 59.4465 | 59.0689 | 59.3895 | 3.2683 | 3.5807 | 3.2316 | 3.544
1026.7031 | 122.3465 | -59.3262 | 62.7228 | 0.12643 | -0.10462 | -0.12646 | -0.11201 | -0.059872 | -0.01972 | -0.1497 | 62.6543 | 62.6854 | 62.6221 | 62.5302 | 59.3218 | 59.3778 | 59.0094 | 59.3116 | 0.15847 | -0.072581 | -0.094422 | -0.079965 | -0.027829 | 0.012323 | -0.11766 | 62.6863 | 62.7174 | 62.6541 | 62.5623 | 59.3539 | 59.4099 | 59.0414 | 59.3437 | 3.3324 | 3.6448 | 3.3002 | 3.6127
1028.3906 | 122.3053 | -59.2941 | 62.796 | 0.11269 | -0.1092 | -0.13104 | -0.11201 | -0.06445 | -0.024298 | -0.1497 | 62.7092 | 62.7495 | 62.6816 | 62.5897 | 59.2669 | 59.3229 | 58.9453 | 59.2659 | 0.14474 | -0.07716 | -0.099 | -0.079965 | -0.032407 | 0.007745 | -0.11766 | 62.7412 | 62.7815 | 62.7136 | 62.6218 | 59.2989 | 59.355 | 58.9774 | 59.2979 | 3.4423 | 3.7639 | 3.4147 | 3.7363
1030.125 | 122.2275 | -59.2072 | 62.9288 | 0.12185 | -0.10004 | -0.13562 | -0.11659 | -0.059872 | -0.01972 | -0.14512 | 62.7962 | 62.8365 | 62.764 | 62.6767 | 59.1708 | 59.2268 | 58.8583 | 59.1743 | 0.15389 | -0.068002 | -0.10358 | -0.084544 | -0.027829 | 0.012323 | -0.11308 | 62.8282 | 62.8685 | 62.7961 | 62.7088 | 59.2028 | 59.2588 | 58.8904 | 59.2063 | 3.6254 | 3.9379 | 3.5932 | 3.9057
1031.875 | 122.2321 | -59.0744 | 63.0295 | 0.11727 | -0.1092 | -0.13104 | -0.11659 | -0.059872 | -0.028877 | -0.1497 | 62.9152 | 62.9464 | 62.883 | 62.805 | 59.0609 | 59.1123 | 58.7393 | 59.0507 | 0.14932 | -0.07716 | -0.099 | -0.084544 | -0.027829 | 0.003166 | -0.11766 | 62.9473 | 62.9784 | 62.9151 | 62.837 | 59.0929 | 59.1444 | 58.7713 | 59.0827 | 3.8543 | 4.1759 | 3.8222 | 4.1438
1033.5625 | 122.2412 | -59.024 | 63.1302 | 0.11727 | -0.10462 | -0.13104 | -0.11659 | -0.055294 | -0.024298 | -0.1497 | 62.9702 | 62.9967 | 62.938 | 62.8507 | 59.0059 | 59.0574 | 58.6798 | 58.9957 | 0.14932 | -0.072581 | -0.099 | -0.084544 | -0.023251 | 0.007745 | -0.11766 | 63.0022 | 63.0288 | 62.97 | 62.8828 | 59.038 | 59.0894 | 58.7118 | 59.0278 | 3.9642 | 4.2904 | 3.932 | 4.2582
1035.25 | 122.3328 | -58.9645 | 63.0798 | 0.11727 | -0.11836 | -0.13104 | -0.11659 | -0.06445 | -0.038034 | -0.14512 | 63.0205 | 63.0517 | 62.9838 | 62.8965 | 58.9556 | 59.0116 | 58.6386 | 58.9545 | 0.14932 | -0.086318 | -0.099 | -0.084544 | -0.032407 | -0.005991 | -0.11308 | 63.0526 | 63.0837 | 63.0158 | 62.9286 | 58.9876 | 59.0436 | 58.6706 | 58.9866 | 4.0649 | 4.382 | 4.0282 | 4.3452
1037 | 122.3511 | -58.8821 | 63.1622 | 0.11269 | -0.11378 | -0.1402 | -0.11659 | -0.059872 | -0.024298 | -0.15886 | 63.1167 | 63.1524 | 63.0891 | 62.9927 | 58.8549 | 58.9155 | 58.5424 | 58.8492 | 0.14474 | -0.081739 | -0.10816 | -0.084544 | -0.027829 | 0.007745 | -0.12682 | 63.1487 | 63.1845 | 63.1211 | 63.0247 | 58.8869 | 58.9475 | 58.5745 | 58.8813 | 4.2618 | 4.5743 | 4.2342 | 4.5467
1038.75 | 122.2275 | -58.7769 | 63.3179 | 0.11727 | -0.10462 | -0.12646 | -0.11659 | -0.055294 | -0.028877 | -0.14512 | 63.222 | 63.2532 | 63.1806 | 63.098 | 58.7542 | 58.8102 | 58.4417 | 58.7577 | 0.14932 | -0.072581 | -0.094422 | -0.084544 | -0.023251 | 0.003166 | -0.11308 | 63.254 | 63.2852 | 63.2127 | 63.1301 | 58.7862 | 58.8422 | 58.4737 | 58.7897 | 4.4678 | 4.7803 | 4.4265 | 4.7389
1040.4531 | 122.2321 | -58.6899 | 63.4369 | 0.11269 | -0.11836 | -0.13104 | -0.11659 | -0.059872 | -0.024298 | -0.14512 | 63.3181 | 63.3493 | 63.2814 | 63.1987 | 58.6534 | 58.7186 | 58.3501 | 58.657 | 0.14474 | -0.086318 | -0.099 | -0.084544 | -0.027829 | 0.007745 | -0.11308 | 63.3502 | 63.3814 | 63.3134 | 63.2308 | 58.6855 | 58.7506 | 58.3822 | 58.689 | 4.6647 | 4.968 | 4.6279 | 4.9312
1042.2031 | 122.3511 | -58.6487 | 63.4048 | 0.11269 | -0.11378 | -0.13104 | -0.12116 | -0.059872 | -0.028877 | -0.1497 | 63.3548 | 63.3859 | 63.3271 | 63.2354 | 58.6122 | 58.6728 | 58.3043 | 58.6158 | 0.14474 | -0.081739 | -0.099 | -0.089122 | -0.027829 | 0.003166 | -0.11766 | 63.3868 | 63.418 | 63.3592 | 63.2674 | 58.6443 | 58.7049 | 58.3364 | 58.6478 | 4.7425 | 5.0504 | 4.7149 | 5.0228
1043.9531 | 122.2916 | -58.6029 | 63.5056 | 0.10812 | -0.10462 | -0.12646 | -0.11201 | -0.059872 | -0.024298 | -0.1497 | 63.3822 | 63.4134 | 63.3454 | 63.2583 | 58.5985 | 58.6454 | 58.2723 | 58.602 | 0.14016 | -0.072581 | -0.094422 | -0.079965 | -0.027829 | 0.007745 | -0.11766 | 63.4143 | 63.4455 | 63.3775 | 63.2903 | 58.6305 | 58.6774 | 58.3043 | 58.6341 | 4.7837 | 5.1099 | 4.747 | 5.0732
1045.6406 | 122.3648 | -58.5434 | 63.5193 | 0.11269 | -0.11378 | -0.13104 | -0.11201 | -0.059872 | -0.028877 | -0.15428 | 63.4418 | 63.4638 | 63.405 | 63.3086 | 58.5298 | 58.595 | 58.2265 | 58.5379 | 0.14474 | -0.081739 | -0.099 | -0.079965 | -0.027829 | 0.003166 | -0.12224 | 63.4738 | 63.4958 | 63.437 | 63.3407 | 58.5619 | 58.627 | 58.2585 | 58.57 | 4.9119 | 5.2153 | 4.8751 | 5.1785
1047.3281 | 122.3419 | -58.493 | 63.5193 | 0.11269 | -0.1092 | -0.13104 | -0.11201 | -0.055294 | -0.028877 | -0.1497 | 63.4784 | 63.5187 | 63.4553 | 63.359 | 58.4932 | 58.5446 | 58.1716 | 58.4921 | 0.14474 | -0.07716 | -0.099 | -0.079965 | -0.023251 | 0.003166 | -0.11766 | 63.5104 | 63.5508 | 63.4874 | 63.3911 | 58.5252 | 58.5767 | 58.2036 | 58.5242 | 4.9852 | 5.3068 | 4.9621 | 5.2838
1049.0781 | 122.2321 | -58.429 | 63.6841 | 0.10354 | -0.11378 | -0.12189 | -0.10285 | -0.06445 | -0.024298 | -0.14055 | 63.5745 | 63.6103 | 63.5377 | 63.446 | 58.3971 | 58.4577 | 58.0891 | 58.4052 | 0.13558 | -0.081739 | -0.089843 | -0.070808 | -0.032407 | 0.007745 | -0.1085 | 63.6066 | 63.6423 | 63.5698 | 63.4781 | 58.4291 | 58.4897 | 58.1212 | 58.4372 | 5.1775 | 5.4854 | 5.1407 | 5.4486
1050.7656 | 122.3785 | -58.2962 | 63.7619 | 0.10354 | -0.11836 | -0.13104 | -0.11201 | -0.055294 | -0.033455 | -0.1497 | 63.6478 | 63.679 | 63.6201 | 63.533 | 58.3146 | 58.3752 | 57.9976 | 58.3182 | 0.13558 | -0.086318 | -0.099 | -0.079965 | -0.023251 | -0.001412 | -0.11766 | 63.6798 | 63.711 | 63.6522 | 63.5651 | 58.3467 | 58.4073 | 58.0296 | 58.3502 | 5.3331 | 5.6502 | 5.3055 | 5.6226
1052.5156 | 122.2321 | -58.2367 | 63.9084 | 0.10812 | -0.11378 | -0.12189 | -0.11201 | -0.06445 | -0.024298 | -0.1497 | 63.7577 | 63.7843 | 63.7163 | 63.6338 | 58.2231 | 58.2745 | 57.9014 | 58.2175 | 0.14016 | -0.081739 | -0.089843 | -0.079965 | -0.032407 | 0.007745 | -0.11766 | 63.7897 | 63.8163 | 63.7483 | 63.6658 | 58.2551 | 58.3066 | 57.9335 | 58.2495 | 5.5346 | 5.8562 | 5.4932 | 5.8149
1054.2031 | 122.2275 | -58.2092 | 63.9542 | 0.098959 | -0.1092 | -0.12189 | -0.10743 | -0.055294 | -0.024298 | -0.14512 | 63.7943 | 63.8164 | 63.7529 | 63.6704 | 58.1865 | 58.2425 | 57.874 | 58.1808 | 0.131 | -0.07716 | -0.089843 | -0.075387 | -0.023251 | 0.007745 | -0.11308 | 63.8263 | 63.8484 | 63.785 | 63.7024 | 58.2185 | 58.2745 | 57.906 | 58.2129 | 5.6078 | 5.9203 | 5.5665 | 5.879
1055.9531 | 122.2778 | -58.1635 | 63.9542 | 0.098959 | -0.1092 | -0.12646 | -0.11201 | -0.055294 | -0.015142 | -0.1497 | 63.8309 | 63.8667 | 63.8079 | 63.7162 | 58.1361 | 58.1967 | 57.819 | 58.1396 | 0.131 | -0.07716 | -0.094422 | -0.079965 | -0.023251 | 0.016901 | -0.11766 | 63.863 | 63.8988 | 63.8399 | 63.7482 | 58.1681 | 58.2287 | 57.8511 | 58.1717 | 5.6948 | 6.0119 | 5.6718 | 5.9888
1057.6562 | 122.2641 | -58.0582 | 64.064 | 0.10354 | -0.1092 | -0.12189 | -0.11659 | -0.050716 | -0.024298 | -0.1497 | 63.9317 | 63.9537 | 63.8948 | 63.8123 | 58.0491 | 58.1051 | 57.7183 | 58.0435 | 0.13558 | -0.07716 | -0.089843 | -0.084544 | -0.018673 | 0.007745 | -0.11766 | 63.9637 | 63.9858 | 63.9269 | 63.8444 | 58.0812 | 58.1372 | 57.7503 | 58.0755 | 5.8825 | 6.2134 | 5.8457 | 6.1765
1059.4062 | 122.2824 | -58.0032 | 64.1052 | 0.098959 | -0.11378 | -0.12189 | -0.10285 | -0.055294 | -0.01972 | -0.13597 | 64.0003 | 64.027 | 63.9589 | 63.8764 | 57.9759 | 58.0319 | 57.6496 | 57.9794 | 0.131 | -0.081739 | -0.089843 | -0.070808 | -0.023251 | 0.012323 | -0.10393 | 64.0324 | 64.059 | 63.991 | 63.9085 | 58.0079 | 58.0639 | 57.6817 | 58.0114 | 6.0245 | 6.3507 | 5.9831 | 6.3093
1061.0938 | 122.2641 | -57.8796 | 64.2334 | 0.098959 | -0.1092 | -0.12189 | -0.11659 | -0.059872 | -0.024298 | -0.14512 | 64.1468 | 64.1689 | 64.0963 | 64.0184 | 57.8385 | 57.8854 | 57.5077 | 57.8329 | 0.131 | -0.07716 | -0.089843 | -0.084544 | -0.027829 | 0.007745 | -0.11308 | 64.1789 | 64.201 | 64.1283 | 64.0504 | 57.8706 | 57.9174 | 57.5397 | 57.8649 | 6.3083 | 6.6391 | 6.2578 | 6.5886
1062.8438 | 122.374 | -57.7057 | 64.3341 | 0.098959 | -0.11836 | -0.12646 | -0.10743 | -0.050716 | -0.024298 | -0.1497 | 64.2888 | 64.3246 | 64.2519 | 64.1695 | 57.6874 | 57.7389 | 57.352 | 57.6864 | 0.131 | -0.086318 | -0.094422 | -0.075387 | -0.018673 | 0.007745 | -0.11766 | 64.3208 | 64.3566 | 64.284 | 64.2015 | 57.7195 | 57.7709 | 57.3841 | 57.7184 | 6.6013 | 6.9367 | 6.5645 | 6.8999
1064.5312 | 122.2504 | -57.6187 | 64.5401 | 0.098959 | -0.10462 | -0.12646 | -0.11201 | -0.055294 | -0.015142 | -0.1497 | 64.4078 | 64.4391 | 64.3756 | 64.2794 | 57.5638 | 57.6199 | 57.2467 | 57.5719 | 0.131 | -0.072581 | -0.094422 | -0.079965 | -0.023251 | 0.016901 | -0.11766 | 64.4399 | 64.4711 | 64.4076 | 64.3114 | 57.5959 | 57.6519 | 57.2788 | 57.604 | 6.844 | 7.1611 | 6.8117 | 7.1288
1066.2188 | 122.3328 | -57.5317 | 64.5355 | 0.098959 | -0.10462 | -0.12189 | -0.10285 | -0.050716 | -0.01972 | -0.1497 | 64.4536 | 64.4894 | 64.4213 | 64.3298 | 57.5226 | 57.5741 | 57.2009 | 57.5216 | 0.131 | -0.072581 | -0.089843 | -0.070808 | -0.018673 | 0.012323 | -0.11766 | 64.4856 | 64.5215 | 64.4534 | 64.3618 | 57.5547 | 57.6061 | 57.233 | 57.5536 | 6.931 | 7.2527 | 6.8987 | 7.2204
1067.9688 | 122.3877 | -57.4493 | 64.595 | 0.098959 | -0.11378 | -0.12189 | -0.10285 | -0.050716 | -0.01972 | -0.14512 | 64.4994 | 64.5261 | 64.4625 | 64.3847 | 57.4768 | 57.5237 | 57.1506 | 57.4758 | 0.131 | -0.081739 | -0.089843 | -0.070808 | -0.018673 | 0.012323 | -0.11308 | 64.5314 | 64.5581 | 64.4946 | 64.4168 | 57.5089 | 57.5558 | 57.1826 | 57.5078 | 7.0225 | 7.3488 | 6.9857 | 7.312
1069.7344 | 122.3465 | -57.3441 | 64.7141 | 0.10354 | -0.10004 | -0.11731 | -0.11659 | -0.050716 | -0.015142 | -0.14055 | 64.6276 | 64.6726 | 64.5907 | 64.5084 | 57.3349 | 57.4001 | 57.0178 | 57.3476 | 0.13558 | -0.068002 | -0.085264 | -0.084544 | -0.018673 | 0.016901 | -0.1085 | 64.6596 | 64.7046 | 64.6228 | 64.5404 | 57.367 | 57.4322 | 57.0498 | 57.3796 | 7.2927 | 7.6098 | 7.2558 | 7.5729
1071.4062 | 122.3602 | -57.28 | 64.7873 | 0.089802 | -0.095467 | -0.11731 | -0.10743 | -0.055294 | -0.01972 | -0.14512 | 64.7329 | 64.7642 | 64.6869 | 64.6091 | 57.2525 | 57.3086 | 56.9217 | 57.2515 | 0.12185 | -0.063424 | -0.085264 | -0.075387 | -0.023251 | 0.012323 | -0.11308 | 64.7649 | 64.7962 | 64.7189 | 64.6411 | 57.2846 | 57.3406 | 56.9537 | 57.2835 | 7.4804 | 7.8112 | 7.4344 | 7.7652
1073.0938 | 122.2458 | -57.2021 | 64.9521 | 0.094381 | -0.095467 | -0.11273 | -0.10285 | -0.046138 | -0.005985 | -0.13597 | 64.829 | 64.8512 | 64.783 | 64.7053 | 57.1564 | 57.2124 | 56.8392 | 57.1599 | 0.12642 | -0.063424 | -0.080686 | -0.070808 | -0.014095 | 0.026058 | -0.10393 | 64.8611 | 64.8832 | 64.8151 | 64.7373 | 57.1884 | 57.2445 | 56.8713 | 57.1919 | 7.6727 | 7.9898 | 7.6267 | 7.9438
1074.8438 | 122.2549 | -57.0648 | 65.062 | 0.098959 | -0.10004 | -0.11731 | -0.098273 | -0.046138 | -0.010563 | -0.13597 | 64.9343 | 64.9656 | 64.8929 | 64.8151 | 57.0465 | 57.098 | 56.7248 | 57.0409 | 0.131 | -0.068002 | -0.085264 | -0.06623 | -0.014095 | 0.02148 | -0.10393 | 64.9664 | 64.9977 | 64.9249 | 64.8472 | 57.0785 | 57.13 | 56.7568 | 57.0729 | 7.8879 | 8.2096 | 7.8464 | 8.1681
1076.5938 | 122.2549 | -56.987 | 65.1169 | 0.094381 | -0.090888 | -0.10815 | -0.093694 | -0.041561 | 0.003172 | -0.13597 | 65.003 | 65.0297 | 64.9662 | 64.8793 | 56.9778 | 57.0476 | 56.6607 | 56.9768 | 0.12642 | -0.058845 | -0.076107 | -0.061651 | -0.009518 | 0.035215 | -0.10393 | 65.0351 | 65.0618 | 64.9982 | 64.9113 | 57.0099 | 57.0797 | 56.6927 | 57.0088 | 8.0252 | 8.3423 | 7.9883 | 8.3055
1078.2812 | 122.3007 | -56.9687 | 65.1581 | 0.098959 | -0.10004 | -0.10815 | -0.089116 | -0.046138 | -0.001406 | -0.13597 | 65.003 | 65.0297 | 64.9753 | 64.8793 | 56.9778 | 57.0247 | 56.647 | 56.9768 | 0.131 | -0.068002 | -0.076107 | -0.057073 | -0.014095 | 0.030637 | -0.10393 | 65.0351 | 65.0618 | 65.0074 | 64.9113 | 57.0099 | 57.0568 | 56.679 | 57.0088 | 8.0252 | 8.3561 | 7.9975 | 8.3284
1080.0312 | 122.3145 | -56.9366 | 65.1443 | 0.098959 | -0.10004 | -0.10815 | -0.093694 | -0.036983 | 0.003172 | -0.12223 | 65.0488 | 65.0801 | 65.0119 | 64.925 | 56.9275 | 56.9881 | 56.6012 | 56.9401 | 0.131 | -0.068002 | -0.076107 | -0.061651 | -0.00494 | 0.035215 | -0.090191 | 65.0808 | 65.1121 | 65.044 | 64.9571 | 56.9595 | 57.0201 | 56.6332 | 56.9722 | 8.1213 | 8.4476 | 8.0845 | 8.4108
1081.7031 | 122.2733 | -56.9458 | 65.1672 | 0.089802 | -0.090888 | -0.10357 | -0.089116 | -0.032405 | -0.010563 | -0.13597 | 65.0763 | 65.103 | 65.0394 | 64.9479 | 56.9046 | 56.9744 | 56.5783 | 56.9035 | 0.12185 | -0.058845 | -0.071529 | -0.057073 | -0.000362 | 0.02148 | -0.10393 | 65.1083 | 65.135 | 65.0715 | 64.98 | 56.9366 | 57.0064 | 56.6103 | 56.9356 | 8.1717 | 8.498 | 8.1348 | 8.4611
1083.3906 | 122.3557 | -56.6711 | 65.3595 | 0.098959 | -0.090888 | -0.098993 | -0.089116 | -0.036983 | 0.003172 | -0.12223 | 65.2869 | 65.3136 | 65.25 | 65.1632 | 56.694 | 56.75 | 56.3768 | 56.6929 | 0.131 | -0.058845 | -0.06695 | -0.057073 | -0.00494 | 0.035215 | -0.090191 | 65.3189 | 65.3457 | 65.2821 | 65.1952 | 56.726 | 56.7821 | 56.4089 | 56.725 | 8.5929 | 8.9101 | 8.556 | 8.8732
1085.0938 | 122.3602 | -56.6666 | 65.3549 | 0.094381 | -0.095467 | -0.098993 | -0.093694 | -0.036983 | -0.001406 | -0.12681 | 65.3006 | 65.3411 | 65.2683 | 65.1906 | 56.6711 | 56.7271 | 56.3539 | 56.6746 | 0.12642 | -0.063424 | -0.06695 | -0.061651 | -0.00494 | 0.030637 | -0.094769 | 65.3327 | 65.3731 | 65.3004 | 65.2227 | 56.7031 | 56.7592 | 56.386 | 56.7067 | 8.6295 | 8.9467 | 8.5972 | 8.9144
1086.8438 | 122.2458 | -56.543 | 65.5701 | 0.094381 | -0.086309 | -0.10357 | -0.089116 | -0.027827 | 0.003172 | -0.12681 | 65.4517 | 65.4876 | 65.4148 | 65.3372 | 56.5246 | 56.5806 | 56.2074 | 56.5235 | 0.12642 | -0.054266 | -0.071529 | -0.057073 | 0.004216 | 0.035215 | -0.094769 | 65.4838 | 65.5197 | 65.4469 | 65.3692 | 56.5566 | 56.6127 | 56.2395 | 56.5556 | 8.9271 | 9.2443 | 8.8903 | 9.2074
1088.5312 | 122.3373 | -56.3553 | 65.7211 | 0.094381 | -0.090888 | -0.094414 | -0.084537 | -0.023249 | 0.00775 | -0.12223 | 65.6394 | 65.6708 | 65.6071 | 65.5249 | 56.3277 | 56.3884 | 56.0197 | 56.3404 | 0.12642 | -0.058845 | -0.062371 | -0.052494 | 0.008794 | 0.039793 | -0.090191 | 65.6715 | 65.7028 | 65.6392 | 65.5569 | 56.3598 | 56.4204 | 56.0518 | 56.3724 | 9.3117 | 9.6197 | 9.2794 | 9.5874
1090.2188 | 122.2687 | -56.3004 | 65.8493 | 0.10354 | -0.08173 | -0.089836 | -0.07538 | -0.018671 | 0.00775 | -0.11765 | 65.7173 | 65.7532 | 65.6804 | 65.5982 | 56.259 | 56.3197 | 55.9419 | 56.2626 | 0.13558 | -0.049687 | -0.057793 | -0.043337 | 0.013372 | 0.039793 | -0.085612 | 65.7493 | 65.7852 | 65.7124 | 65.6302 | 56.2911 | 56.3517 | 55.9739 | 56.2946 | 9.4582 | 9.7754 | 9.4213 | 9.7385
1091.9688 | 122.3145 | -56.1813 | 65.918 | 0.098959 | -0.077151 | -0.089836 | -0.070802 | -0.018671 | 0.021485 | -0.1085 | 65.8363 | 65.8677 | 65.7994 | 65.7126 | 56.1354 | 56.2007 | 55.8183 | 56.1527 | 0.131 | -0.045108 | -0.057793 | -0.038759 | 0.013372 | 0.053528 | -0.076456 | 65.8684 | 65.8997 | 65.8315 | 65.7447 | 56.1675 | 56.2327 | 55.8503 | 56.1847 | 9.7009 | 10.018 | 9.664 | 9.9811
1093.6562 | 122.2366 | -56.0211 | 66.1285 | 0.10354 | -0.077151 | -0.085257 | -0.066223 | -0.009515 | 0.021485 | -0.1085 | 66.0057 | 66.0508 | 65.9688 | 65.8866 | 55.9706 | 56.0267 | 55.6534 | 55.9742 | 0.13558 | -0.045108 | -0.053214 | -0.03418 | 0.022528 | 0.053528 | -0.076456 | 66.0378 | 66.0829 | 66.0008 | 65.9187 | 56.0027 | 56.0587 | 55.6855 | 56.0062 | 10.0351 | 10.3523 | 9.9982 | 10.3154
1095.3438 | 122.3511 | -55.9113 | 66.1514 | 0.10354 | -0.063415 | -0.066943 | -0.061645 | -0.004937 | 0.030642 | -0.094765 | 66.1064 | 66.1332 | 66.0741 | 65.9782 | 55.8653 | 55.9351 | 55.5481 | 55.8872 | 0.13558 | -0.031372 | -0.0349 | -0.029602 | 0.027106 | 0.062685 | -0.062722 | 66.1385 | 66.1653 | 66.1061 | 66.0103 | 55.8974 | 55.9672 | 55.5802 | 55.9192 | 10.2411 | 10.5583 | 10.2088 | 10.526
1097.0938 | 122.3785 | -55.806 | 66.2476 | 0.098959 | -0.058836 | -0.0761 | -0.061645 | -0.000359 | 0.030642 | -0.094765 | 66.1843 | 66.2202 | 66.1519 | 66.0698 | 55.7875 | 55.8436 | 55.4657 | 55.791 | 0.131 | -0.026793 | -0.044057 | -0.029602 | 0.031684 | 0.062685 | -0.062722 | 66.2163 | 66.2523 | 66.184 | 66.1018 | 55.8195 | 55.8756 | 55.4978 | 55.8231 | 10.3968 | 10.7185 | 10.3644 | 10.6862
1098.8281 | 122.319 | -55.5405 | 66.5451 | 0.094381 | -0.063415 | -0.066943 | -0.057066 | -0.000359 | 0.026064 | -0.094765 | 66.4636 | 66.4858 | 66.4266 | 66.34 | 55.5265 | 55.5735 | 55.2002 | 55.5301 | 0.12642 | -0.031372 | -0.0349 | -0.025023 | 0.031684 | 0.058107 | -0.062722 | 66.4956 | 66.5178 | 66.4587 | 66.372 | 55.5586 | 55.6055 | 55.2322 | 55.5621 | 10.937 | 11.2634 | 10.9001 | 11.2264
1100.5938 | 122.3923 | -55.1743 | 66.8701 | 0.10354 | -0.054257 | -0.066943 | -0.052488 | 0.008797 | 0.035221 | -0.099343 | 66.7841 | 66.8155 | 66.7517 | 66.6651 | 55.1969 | 55.253 | 54.8751 | 55.1959 | 0.13558 | -0.022214 | -0.0349 | -0.020445 | 0.04084 | 0.067264 | -0.0673 | 66.8161 | 66.8475 | 66.7837 | 66.6971 | 55.229 | 55.285 | 54.9072 | 55.2279 | 11.5871 | 11.9089 | 11.5548 | 11.8766
1102.2812 | 122.2412 | -55.0369 | 67.1082 | 0.10812 | -0.049678 | -0.048628 | -0.047909 | 0.017953 | 0.039799 | -0.085608 | 66.9947 | 67.0215 | 66.9577 | 66.8757 | 54.9817 | 55.0333 | 54.6599 | 54.9853 | 0.14016 | -0.017635 | -0.016585 | -0.015866 | 0.049996 | 0.071842 | -0.053565 | 67.0267 | 67.0536 | 66.9898 | 66.9078 | 55.0138 | 55.0653 | 54.692 | 55.0173 | 12.0129 | 12.3347 | 11.976 | 12.2978
1104.0312 | 122.3328 | -54.9179 | 67.1356 | 0.10812 | -0.049678 | -0.062364 | -0.057066 | 0.004219 | 0.048956 | -0.085608 | 67.0725 | 67.0948 | 67.0355 | 66.9398 | 54.9131 | 54.9692 | 54.5867 | 54.9166 | 0.14016 | -0.017635 | -0.030321 | -0.025023 | 0.036262 | 0.080999 | -0.053565 | 67.1045 | 67.1268 | 67.0676 | 66.9719 | 54.9451 | 55.0012 | 54.6187 | 54.9486 | 12.1594 | 12.4858 | 12.1225 | 12.4489
1105.7812 | 122.2458 | -54.9316 | 67.1997 | 0.10354 | -0.0451 | -0.057786 | -0.052488 | 0.004219 | 0.048956 | -0.090186 | 67.0862 | 67.1085 | 67.0584 | 66.9581 | 54.8902 | 54.9463 | 54.5729 | 54.8937 | 0.13558 | -0.013057 | -0.025743 | -0.020445 | 0.036262 | 0.080999 | -0.058143 | 67.1183 | 67.1406 | 67.0905 | 66.9902 | 54.9222 | 54.9783 | 54.605 | 54.9257 | 12.1961 | 12.5133 | 12.1683 | 12.4855
1107.4844 | 122.2549 | -54.9545 | 67.1768 | 0.098959 | -0.0451 | -0.057786 | -0.043331 | 0.017953 | 0.053534 | -0.08103 | 67.0405 | 67.0627 | 66.9989 | 66.9169 | 54.9405 | 55.0012 | 54.6187 | 54.9532 | 0.131 | -0.013057 | -0.025743 | -0.011288 | 0.049996 | 0.085577 | -0.048987 | 67.0725 | 67.0948 | 67.031 | 66.949 | 54.9726 | 55.0333 | 54.6508 | 54.9853 | 12.0999 | 12.4217 | 12.0584 | 12.3802
1109.2188 | 122.2641 | -54.8218 | 67.2958 | 0.11269 | -0.026784 | -0.048628 | -0.038752 | 0.022531 | 0.058113 | -0.067295 | 67.1595 | 67.1955 | 67.1271 | 67.0406 | 54.8078 | 54.8822 | 54.4905 | 54.8205 | 0.14474 | 0.005259 | -0.016585 | -0.006709 | 0.054574 | 0.090156 | -0.035252 | 67.1915 | 67.2276 | 67.1592 | 67.0726 | 54.8398 | 54.9142 | 54.5226 | 54.8525 | 12.3517 | 12.669 | 12.3193 | 12.6366
1110.9688 | 122.2458 | -54.7943 | 67.3416 | 0.11269 | -0.026784 | -0.04405 | -0.034174 | 0.027109 | 0.062691 | -0.076452 | 67.2373 | 67.2596 | 67.2004 | 67.1092 | 54.7391 | 54.7998 | 54.4219 | 54.7518 | 0.14474 | 0.005259 | -0.012007 | -0.002131 | 0.059152 | 0.094734 | -0.044409 | 67.2694 | 67.2917 | 67.2324 | 67.1413 | 54.7711 | 54.8318 | 54.4539 | 54.7838 | 12.4982 | 12.8155 | 12.4613 | 12.7785
1112.6719 | 122.287 | -54.6295 | 67.4515 | 0.11269 | -0.035942 | -0.04405 | -0.038752 | 0.031687 | 0.071848 | -0.076452 | 67.3426 | 67.3787 | 67.3148 | 67.2237 | 54.6338 | 54.6991 | 54.3166 | 54.6419 | 0.14474 | -0.003899 | -0.012007 | -0.006709 | 0.06373 | 0.10389 | -0.044409 | 67.3747 | 67.4107 | 67.3469 | 67.2558 | 54.6658 | 54.7311 | 54.3486 | 54.6739 | 12.7088 | 13.0261 | 12.681 | 12.9983
1114.4375 | 122.2778 | -54.4373 | 67.6941 | 0.11269 | -0.017627 | -0.030314 | -0.029595 | 0.036265 | 0.067269 | -0.071874 | 67.5303 | 67.5618 | 67.4979 | 67.416 | 54.4461 | 54.5068 | 54.1243 | 54.4542 | 0.14474 | 0.014416 | 0.001729 | 0.002448 | 0.068308 | 0.099312 | -0.039831 | 67.5624 | 67.5939 | 67.53 | 67.4481 | 54.4781 | 54.5388 | 54.1563 | 54.4862 | 13.0843 | 13.4061 | 13.0519 | 13.3737
1116.125 | 122.3236 | -54.2084 | 67.8772 | 0.11269 | -0.031363 | -0.030314 | -0.025017 | 0.040843 | 0.071848 | -0.058139 | 67.773 | 67.8045 | 67.7406 | 67.6541 | 54.208 | 54.2641 | 53.8908 | 54.2161 | 0.14474 | 0.00068 | 0.001729 | 0.007026 | 0.072886 | 0.10389 | -0.026096 | 67.8051 | 67.8365 | 67.7726 | 67.6862 | 54.2401 | 54.2962 | 53.9228 | 54.2482 | 13.565 | 13.8822 | 13.5326 | 13.8498
1117.875 | 122.2916 | -53.9474 | 68.1702 | 0.10812 | -0.017627 | -0.030314 | -0.01586 | 0.031687 | 0.071848 | -0.053561 | 68.0569 | 68.0884 | 68.0199 | 67.938 | 53.9288 | 53.9849 | 53.6023 | 53.9323 | 0.14016 | 0.014416 | 0.001729 | 0.016183 | 0.06373 | 0.10389 | -0.021518 | 68.0889 | 68.1204 | 68.0519 | 67.9701 | 53.9608 | 54.0169 | 53.6344 | 53.9643 | 14.1281 | 14.4545 | 14.0911 | 14.4175
1119.625 | 122.2366 | -53.7643 | 68.3578 | 0.12185 | -0.013048 | -0.025735 | -0.011281 | 0.045421 | 0.081005 | -0.053561 | 68.2354 | 68.2624 | 68.203 | 68.1121 | 53.7411 | 53.8063 | 53.4284 | 53.7537 | 0.15389 | 0.018995 | 0.006308 | 0.020762 | 0.077464 | 0.11305 | -0.021518 | 68.2675 | 68.2944 | 68.235 | 68.1441 | 53.7731 | 53.8384 | 53.4604 | 53.7858 | 14.4944 | 14.8071 | 14.462 | 14.7747
1121.3125 | 122.3602 | -53.5263 | 68.5043 | 0.11269 | 0.005267 | -0.012 | -0.002124 | 0.054577 | 0.085583 | -0.048983 | 68.446 | 68.4684 | 68.4044 | 68.3135 | 53.5396 | 53.5957 | 53.2223 | 53.5569 | 0.14474 | 0.03731 | 0.020043 | 0.029919 | 0.08662 | 0.11763 | -0.01694 | 68.4781 | 68.5005 | 68.4365 | 68.3456 | 53.5717 | 53.6278 | 53.2544 | 53.5889 | 14.9064 | 15.2237 | 14.8648 | 15.1821
1123.0625 | 122.3557 | -53.1876 | 68.8522 | 0.11269 | -0.008469 | -0.021157 | -0.006703 | 0.054577 | 0.085583 | -0.048983 | 68.7482 | 68.7798 | 68.7112 | 68.6295 | 53.2329 | 53.2844 | 52.911 | 53.2318 | 0.14474 | 0.023574 | 0.010886 | 0.02534 | 0.08662 | 0.11763 | -0.01694 | 68.7803 | 68.8118 | 68.7432 | 68.6615 | 53.2649 | 53.3165 | 52.943 | 53.2639 | 15.5154 | 15.8372 | 15.4783 | 15.8002
1124.8125 | 122.2458 | -52.9678 | 69.1727 | 0.12185 | 0.000689 | -0.007421 | -0.002124 | 0.059155 | 0.1039 | -0.044405 | 69.0413 | 69.0774 | 69.0088 | 68.9225 | 52.9353 | 52.996 | 52.618 | 52.9434 | 0.15389 | 0.032732 | 0.024622 | 0.029919 | 0.091198 | 0.13594 | -0.012362 | 69.0733 | 69.1095 | 69.0408 | 68.9546 | 52.9673 | 53.0281 | 52.65 | 52.9754 | 16.106 | 16.4233 | 16.0735 | 16.3908
1126.5 | 122.3877 | -52.6794 | 69.3741 | 0.12185 | 0.005267 | -0.002842 | -0.006703 | 0.059155 | 0.090161 | -0.044405 | 69.2931 | 69.3201 | 69.256 | 69.1652 | 52.6927 | 52.7442 | 52.3707 | 52.6962 | 0.15389 | 0.03731 | 0.029201 | 0.02534 | 0.091198 | 0.1222 | -0.012362 | 69.3251 | 69.3521 | 69.2881 | 69.1973 | 52.7247 | 52.7763 | 52.4028 | 52.7282 | 16.6004 | 16.9223 | 16.5634 | 16.8853
1128.1875 | 122.2504 | -52.4048 | 69.7357 | 0.11727 | 0.014425 | 0.001736 | 0.007033 | 0.082044 | 0.1039 | -0.03067 | 69.5953 | 69.6223 | 69.5673 | 69.4674 | 52.3813 | 52.4375 | 52.064 | 52.3986 | 0.14932 | 0.046468 | 0.033779 | 0.039076 | 0.11409 | 0.13594 | 0.001373 | 69.6273 | 69.6543 | 69.5994 | 69.4995 | 52.4134 | 52.4695 | 52.096 | 52.4306 | 17.2139 | 17.5313 | 17.186 | 17.5033
1129.9531 | 122.2412 | -52.0157 | 70.1202 | 0.12643 | 0.023583 | 0.010893 | 0.025347 | 0.086622 | 0.12679 | -0.016936 | 69.989 | 70.0207 | 69.9565 | 69.8658 | 51.9876 | 52.0438 | 51.6611 | 51.9957 | 0.15847 | 0.055626 | 0.042936 | 0.05739 | 0.11867 | 0.15883 | 0.015107 | 70.021 | 70.0527 | 69.9885 | 69.8979 | 52.0197 | 52.0758 | 51.6931 | 52.0278 | 18.0014 | 18.3279 | 17.9689 | 18.2954
1131.7031 | 122.2778 | -51.5533 | 70.546 | 0.13101 | 0.019004 | 0.020051 | 0.025347 | 0.086622 | 0.12221 | -0.021514 | 70.4011 | 70.4282 | 70.364 | 70.2734 | 51.5802 | 51.6409 | 51.2628 | 51.5837 | 0.16305 | 0.051047 | 0.052094 | 0.05739 | 0.11867 | 0.15425 | 0.010529 | 70.4331 | 70.4602 | 70.396 | 70.3054 | 51.6122 | 51.673 | 51.2948 | 51.6157 | 18.8209 | 19.1383 | 18.7838 | 19.1012
1133.3906 | 122.319 | -51.3657 | 70.7108 | 0.13101 | 0.037319 | 0.033786 | 0.034504 | 0.10493 | 0.13137 | -0.012357 | 70.6391 | 70.6617 | 70.602 | 70.5069 | 51.3421 | 51.4029 | 51.0293 | 51.3502 | 0.16305 | 0.069362 | 0.065829 | 0.066547 | 0.13698 | 0.16341 | 0.019686 | 70.6712 | 70.6937 | 70.6341 | 70.5389 | 51.3741 | 51.4349 | 51.0613 | 51.3822 | 19.2971 | 19.6099 | 19.2599 | 19.5727
1135.1406 | 122.3419 | -51.0223 | 71.0083 | 0.13559 | 0.037319 | 0.029208 | 0.034504 | 0.095778 | 0.12679 | -0.016936 | 70.9368 | 70.973 | 70.9042 | 70.8228 | 51.0354 | 51.0961 | 50.7179 | 51.048 | 0.16763 | 0.069362 | 0.061251 | 0.066547 | 0.12782 | 0.15883 | 0.015107 | 70.9688 | 71.0051 | 70.9362 | 70.8549 | 51.0674 | 51.1282 | 50.75 | 51.0801 | 19.9014 | 20.2188 | 19.8688 | 20.1862
1136.8906 | 122.3511 | -50.6653 | 71.4203 | 0.14017 | 0.046477 | 0.042944 | 0.043661 | 0.11409 | 0.1451 | 0.010533 | 71.3122 | 71.3439 | 71.275 | 71.1892 | 50.6737 | 50.7207 | 50.3517 | 50.6772 | 0.17221 | 0.07852 | 0.074987 | 0.075704 | 0.14613 | 0.17714 | 0.042576 | 71.3442 | 71.376 | 71.3071 | 71.2212 | 50.7057 | 50.7528 | 50.3837 | 50.7092 | 20.6385 | 20.9605 | 20.6014 | 20.9234
1138.6406 | 122.3099 | -50.267 | 71.8094 | 0.14474 | 0.055634 | 0.042944 | 0.052818 | 0.10951 | 0.1451 | -0.003201 | 71.7059 | 71.7194 | 71.6642 | 71.5738 | 50.2845 | 50.3407 | 49.9717 | 50.2926 | 0.17679 | 0.087677 | 0.074987 | 0.084861 | 0.14155 | 0.17714 | 0.028842 | 71.738 | 71.7514 | 71.6962 | 71.6058 | 50.3166 | 50.3728 | 50.0037 | 50.3247 | 21.4214 | 21.7343 | 21.3797 | 21.6925
1140.3281 | 122.2458 | -49.9466 | 72.1893 | 0.14932 | 0.060213 | 0.056679 | 0.061975 | 0.11867 | 0.15884 | 0.01969 | 72.0219 | 72.0536 | 71.9938 | 71.9035 | 49.9549 | 50.0111 | 49.6374 | 49.963 | 0.18136 | 0.092256 | 0.088722 | 0.094018 | 0.15071 | 0.19088 | 0.051733 | 72.0539 | 72.0857 | 72.0259 | 71.9355 | 49.9869 | 50.0432 | 49.6695 | 49.9951 | 22.067 | 22.3844 | 22.0389 | 22.3564
1142.0625 | 122.2275 | -49.5163 | 72.6196 | 0.1539 | 0.087686 | 0.074994 | 0.07571 | 0.14156 | 0.17715 | 0.028846 | 72.4843 | 72.5115 | 72.4379 | 72.3522 | 49.5062 | 49.5533 | 49.1842 | 49.5189 | 0.18594 | 0.11973 | 0.10704 | 0.10775 | 0.1736 | 0.20919 | 0.060889 | 72.5163 | 72.5436 | 72.47 | 72.3843 | 49.5383 | 49.5854 | 49.2162 | 49.551 | 22.978 | 23.3001 | 22.9317 | 23.2537
1143.8125 | 122.319 | -48.9441 | 73.114 | 0.16764 | 0.087686 | 0.079572 | 0.084867 | 0.14614 | 0.18631 | 0.033424 | 73.0429 | 73.0747 | 73.0056 | 72.9109 | 48.9385 | 48.9902 | 48.6348 | 48.9467 | 0.19968 | 0.11973 | 0.11162 | 0.11691 | 0.17818 | 0.21835 | 0.065467 | 73.0749 | 73.1068 | 73.0377 | 72.9429 | 48.9706 | 49.0223 | 48.6668 | 48.9787 | 24.1043 | 24.4081 | 24.0671 | 24.3708
1145.5625 | 122.2412 | -48.4955 | 73.6816 | 0.16306 | 0.083107 | 0.070415 | 0.084867 | 0.14614 | 0.18173 | 0.028846 | 73.5007 | 73.528 | 73.468 | 73.3825 | 48.4762 | 48.5278 | 48.1678 | 48.4843 | 0.1951 | 0.11515 | 0.10246 | 0.11691 | 0.17818 | 0.21377 | 0.060889 | 73.5328 | 73.5601 | 73.5001 | 73.4146 | 48.5082 | 48.5599 | 48.1998 | 48.5163 | 25.0246 | 25.3329 | 24.9919 | 25.3002
1147.25 | 122.2321 | -47.9462 | 74.231 | 0.16764 | 0.092265 | 0.08873 | 0.098602 | 0.15071 | 0.19089 | 0.033424 | 74.0501 | 74.0683 | 74.0128 | 73.9137 | 47.9359 | 47.9922 | 47.623 | 47.9578 | 0.19968 | 0.12431 | 0.12077 | 0.13065 | 0.18276 | 0.22293 | 0.065467 | 74.0822 | 74.1004 | 74.0449 | 73.9457 | 47.968 | 48.0242 | 47.655 | 47.9898 | 26.1142 | 26.4272 | 26.0769 | 26.3899
1148.9844 | 122.2275 | -47.4289 | 74.7162 | 0.17221 | 0.11516 | 0.10704 | 0.098602 | 0.16903 | 0.20462 | 0.056315 | 74.6087 | 74.6224 | 74.5622 | 74.4769 | 47.3865 | 47.4337 | 47.0735 | 47.3947 | 0.20426 | 0.1472 | 0.13909 | 0.13065 | 0.20107 | 0.23666 | 0.088358 | 74.6407 | 74.6544 | 74.5943 | 74.5089 | 47.4186 | 47.4657 | 47.1056 | 47.4267 | 27.2222 | 27.5352 | 27.1757 | 27.4887
1150.7344 | 122.2733 | -46.7743 | 75.3616 | 0.17679 | 0.11974 | 0.11162 | 0.10776 | 0.16903 | 0.20462 | 0.056315 | 75.2543 | 75.2817 | 75.2124 | 75.1226 | 46.7319 | 46.7836 | 46.4188 | 46.74 | 0.20883 | 0.15178 | 0.14367 | 0.1398 | 0.20107 | 0.23666 | 0.088358 | 75.2863 | 75.3138 | 75.2444 | 75.1546 | 46.7639 | 46.8156 | 46.4509 | 46.772 | 28.5224 | 28.8354 | 28.4805 | 28.7935
1152.4219 | 122.3602 | -46.1288 | 75.9247 | 0.17221 | 0.11974 | 0.10704 | 0.098602 | 0.16903 | 0.20004 | 0.051737 | 75.8174 | 75.8312 | 75.7846 | 75.6858 | 46.1642 | 46.2205 | 45.8557 | 46.1769 | 0.20426 | 0.15178 | 0.13909 | 0.13065 | 0.20107 | 0.23209 | 0.08378 | 75.8495 | 75.8632 | 75.8167 | 75.7178 | 46.1962 | 46.2525 | 45.8877 | 46.2089 | 29.6533 | 29.9617 | 29.6205 | 29.9289
1154.1094 | 122.2321 | -45.5978 | 76.5335 | 0.18137 | 0.12432 | 0.11162 | 0.11692 | 0.18276 | 0.21378 | 0.074628 | 76.3989 | 76.4218 | 76.3569 | 76.2673 | 45.5919 | 45.6436 | 45.2788 | 45.6046 | 0.21341 | 0.15636 | 0.14367 | 0.14896 | 0.2148 | 0.24582 | 0.10667 | 76.4309 | 76.4539 | 76.389 | 76.2994 | 45.6239 | 45.6757 | 45.3109 | 45.6366 | 30.807 | 31.1201 | 30.765 | 31.0781
1155.8594 | 122.3465 | -44.8883 | 77.1927 | 0.19968 | 0.13347 | 0.12536 | 0.1215 | 0.19649 | 0.22751 | 0.083784 | 77.0994 | 77.1178 | 77.0437 | 76.9587 | 44.8914 | 44.9524 | 44.5921 | 44.9087 | 0.23173 | 0.16552 | 0.1574 | 0.15354 | 0.22854 | 0.25956 | 0.11583 | 77.1314 | 77.1499 | 77.0757 | 76.9908 | 44.9235 | 44.9844 | 44.6241 | 44.9408 | 32.208 | 32.5073 | 32.1522 | 32.4516
1157.6094 | 122.3373 | -44.101 | 78.0304 | 0.19511 | 0.14263 | 0.13452 | 0.13981 | 0.21023 | 0.23209 | 0.088362 | 77.8457 | 77.8642 | 77.8037 | 77.7189 | 44.1498 | 44.1924 | 43.8366 | 44.1442 | 0.22715 | 0.17468 | 0.16656 | 0.17185 | 0.24227 | 0.26413 | 0.1204 | 77.8777 | 77.8962 | 77.8357 | 77.7509 | 44.1818 | 44.2244 | 43.8687 | 44.1762 | 33.6959 | 34.0091 | 33.6539 | 33.967
1159.2969 | 122.3236 | -43.309 | 78.7811 | 0.19968 | 0.14263 | 0.13909 | 0.13065 | 0.20565 | 0.23667 | 0.092941 | 78.7019 | 78.725 | 78.6644 | 78.5751 | 43.2799 | 43.3363 | 42.9942 | 43.3109 | 0.23173 | 0.17468 | 0.17114 | 0.16269 | 0.23769 | 0.26871 | 0.12498 | 78.7339 | 78.757 | 78.6964 | 78.6072 | 43.312 | 43.3683 | 43.0262 | 43.343 | 35.422 | 35.7077 | 35.3845 | 35.6702
1161.0625 | 122.3557 | -42.2928 | 79.7745 | 0.20884 | 0.16553 | 0.15741 | 0.14439 | 0.21938 | 0.25498 | 0.1021 | 79.7137 | 79.7369 | 79.6762 | 79.5825 | 42.2727 | 42.32 | 41.9778 | 42.2854 | 0.24088 | 0.19757 | 0.18945 | 0.17643 | 0.25143 | 0.28703 | 0.13414 | 79.7458 | 79.7689 | 79.7082 | 79.6146 | 42.3048 | 42.352 | 42.0098 | 42.3175 | 37.441 | 37.7359 | 37.4034 | 37.6984
1162.8125 | 122.319 | -41.2582 | 80.8411 | 0.218 | 0.18384 | 0.17114 | 0.16728 | 0.23769 | 0.26872 | 0.12041 | 80.6981 | 80.7122 | 80.6559 | 80.5533 | 41.3022 | 41.3494 | 40.9889 | 41.3148 | 0.25004 | 0.21588 | 0.20319 | 0.19932 | 0.26974 | 0.30076 | 0.15245 | 80.7301 | 80.7442 | 80.688 | 80.5853 | 41.3342 | 41.3815 | 41.0209 | 41.3469 | 39.3959 | 39.7092 | 39.3538 | 39.6671
1164.5781 | 122.2092 | -40.2832 | 81.8802 | 0.23173 | 0.18384 | 0.1803 | 0.17644 | 0.24685 | 0.28703 | 0.12957 | 81.7145 | 81.7333 | 81.6723 | 81.5836 | 40.2766 | 40.3194 | 39.977 | 40.2893 | 0.26377 | 0.21588 | 0.21235 | 0.20848 | 0.27889 | 0.31907 | 0.16161 | 81.7466 | 81.7653 | 81.7043 | 81.6156 | 40.3087 | 40.3514 | 40.0091 | 40.3214 | 41.4379 | 41.7375 | 41.3957 | 41.6953
1166.2656 | 122.2504 | -39.3036 | 82.8598 | 0.22715 | 0.17926 | 0.18946 | 0.18559 | 0.26059 | 0.27787 | 0.13414 | 82.6714 | 82.6902 | 82.6337 | 82.5452 | 39.3152 | 39.3809 | 39.0156 | 39.3462 | 0.2592 | 0.21131 | 0.2215 | 0.21764 | 0.29263 | 0.30992 | 0.16619 | 82.7035 | 82.7223 | 82.6658 | 82.5772 | 39.3473 | 39.4129 | 39.0476 | 39.3783 | 43.3562 | 43.6558 | 43.3185 | 43.6182
1168.0156 | 122.2778 | -38.1775 | 83.9905 | 0.24089 | 0.19758 | 0.19862 | 0.19017 | 0.27432 | 0.28245 | 0.1433 | 83.8069 | 83.8166 | 83.7646 | 83.6762 | 38.1844 | 38.2363 | 37.8893 | 38.2063 | 0.27293 | 0.22962 | 0.23066 | 0.22221 | 0.30636 | 0.3145 | 0.17534 | 83.8389 | 83.8487 | 83.7966 | 83.7082 | 38.2165 | 38.2684 | 37.9213 | 38.2383 | 45.6225 | 45.9176 | 45.5802 | 45.8753
1169.75 | 122.2183 | -37.0743 | 85.1074 | 0.25005 | 0.21589 | 0.21693 | 0.20849 | 0.28805 | 0.29161 | 0.15704 | 84.9195 | 84.9384 | 84.8725 | 84.7843 | 37.0673 | 37.1284 | 36.7722 | 37.0983 | 0.28209 | 0.24794 | 0.24897 | 0.24053 | 0.32009 | 0.32365 | 0.18908 | 84.9515 | 84.9705 | 84.9046 | 84.8163 | 37.0994 | 37.1605 | 36.8042 | 37.1304 | 47.8521 | 48.1473 | 47.8052 | 48.1003
1171.4531 | 122.2275 | -35.9573 | 86.2244 | 0.26836 | 0.22505 | 0.23525 | 0.23596 | 0.30636 | 0.31908 | 0.17535 | 86.0275 | 86.0328 | 85.9805 | 85.8879 | 35.964 | 36.016 | 35.6688 | 35.9904 | 0.3004 | 0.25709 | 0.26729 | 0.268 | 0.33841 | 0.35112 | 0.20739 | 86.0595 | 86.0648 | 86.0125 | 85.9199 | 35.996 | 36.048 | 35.7008 | 36.0225 | 50.0635 | 50.3587 | 50.0165 | 50.3117
1173.1875 | 122.3236 | -34.8816 | 87.2406 | 0.27752 | 0.23879 | 0.24898 | 0.24054 | 0.3201 | 0.33739 | 0.18908 | 87.1034 | 87.118 | 87.0655 | 86.9731 | 34.8881 | 34.9356 | 34.5883 | 34.9146 | 0.30956 | 0.27083 | 0.28102 | 0.27258 | 0.35214 | 0.36944 | 0.22113 | 87.1355 | 87.15 | 87.0976 | 87.0051 | 34.9202 | 34.9676 | 34.6203 | 34.9466 | 52.2153 | 52.5151 | 52.1774 | 52.4772
1174.9219 | 122.3557 | -29.6402 | 92.5003 | 0.29125 | 0.26626 | 0.28103 | 0.27716 | 0.34757 | 0.35571 | 0.22113 | 89.3972 | 89.4028 | 89.3272 | 89.2534 | 32.5487 | 32.6557 | 32.3082 | 32.5934 | 0.32329 | 0.2983 | 0.31307 | 0.30921 | 0.37961 | 0.38775 | 0.25317 | 89.4293 | 89.4348 | 89.3592 | 89.2855 | 32.5807 | 32.6877 | 32.3403 | 32.6255 | 56.8486 | 57.089 | 56.7785 | 57.0189
1176.7031 | 122.1909 | -20.6772 | 101.5778 | 0.38282 | 0.40363 | 0.42297 | 0.40078 | 0.4849 | 0.49764 | 0.3539 | 101.2555 | 101.2619 | 101.2673 | 101.1772 | 20.4898 | 20.7344 | 20.496 | 20.594 | 0.41486 | 0.43567 | 0.45501 | 0.43283 | 0.51695 | 0.52968 | 0.38594 | 101.2876 | 101.294 | 101.2994 | 101.2093 | 20.5218 | 20.7664 | 20.5281 | 20.6261 | 80.7658 | 80.7595 | 80.7776 | 80.7713
1178.3906 | 122.3419 | -19.0521 | 103.1021 | 0.40571 | 0.43568 | 0.4596 | 0.43741 | 0.53068 | 0.52053 | 0.3951 | 102.8351 | 102.8416 | 102.8514 | 102.757 | 18.9057 | 19.155 | 18.9531 | 19.0329 | 0.43775 | 0.46772 | 0.49164 | 0.46945 | 0.56273 | 0.55257 | 0.42714 | 102.8672 | 102.8737 | 102.8835 | 102.7891 | 18.9378 | 19.187 | 18.9851 | 19.0649 | 83.9294 | 83.882 | 83.9457 | 83.8983
1180.1406 | 122.3099 | -17.8711 | 104.2648 | 0.4286 | 0.45399 | 0.47791 | 0.45572 | 0.53526 | 0.548 | 0.40884 | 104.0393 | 104.0458 | 104.0555 | 103.9613 | 17.6971 | 17.9509 | 17.7169 | 17.8197 | 0.46065 | 0.48603 | 0.50995 | 0.48777 | 0.56731 | 0.58004 | 0.44088 | 104.0713 | 104.0779 | 104.0876 | 103.9933 | 17.7291 | 17.983 | 17.749 | 17.8517 | 86.3422 | 86.3223 | 86.3584 | 86.3386
1181.875 | 122.3099 | -17.0151 | 105.162 | 0.44234 | 0.47231 | 0.49623 | 0.47862 | 0.549 | 0.56173 | 0.42715 | 104.9183 | 104.925 | 104.93 | 104.8359 | 16.8318 | 17.0674 | 16.8608 | 16.9544 | 0.47438 | 0.50435 | 0.52827 | 0.51066 | 0.58104 | 0.59378 | 0.45919 | 104.9504 | 104.957 | 104.962 | 104.8679 | 16.8639 | 17.0994 | 16.8928 | 16.9864 | 88.0865 | 88.0576 | 88.0982 | 88.0692
1183.625 | 122.319 | -16.3925 | 105.7571 | 0.44692 | 0.47231 | 0.5008 | 0.4832 | 0.57189 | 0.55716 | 0.43173 | 105.5731 | 105.5752 | 105.5892 | 105.4998 | 16.168 | 16.4081 | 16.2015 | 16.2905 | 0.47896 | 0.50435 | 0.53285 | 0.51524 | 0.60393 | 0.5892 | 0.46377 | 105.6051 | 105.6072 | 105.6213 | 105.5319 | 16.2 | 16.4402 | 16.2335 | 16.3226 | 89.4051 | 89.3716 | 89.4213 | 89.3878
1185.3594 | 122.3236 | -15.9485 | 106.2286 | 0.46523 | 0.49978 | 0.51454 | 0.49235 | 0.57646 | 0.58921 | 0.45004 | 106.0263 | 106.033 | 106.0379 | 105.9578 | 15.7147 | 15.9595 | 15.7482 | 15.8373 | 0.49727 | 0.53182 | 0.54658 | 0.5244 | 0.60851 | 0.62125 | 0.48208 | 106.0584 | 106.0651 | 106.07 | 105.9898 | 15.7468 | 15.9915 | 15.7803 | 15.8694 | 90.3116 | 90.2781 | 90.3232 | 90.2897
1187.0469 | 122.374 | -15.3534 | 106.8054 | 0.47439 | 0.49062 | 0.51912 | 0.50609 | 0.58562 | 0.58463 | 0.45919 | 106.6353 | 106.642 | 106.656 | 106.5668 | 15.1104 | 15.3414 | 15.1668 | 15.2284 | 0.50643 | 0.52267 | 0.55116 | 0.53813 | 0.61766 | 0.61667 | 0.49124 | 106.6673 | 106.6741 | 106.688 | 106.5988 | 15.1425 | 15.3735 | 15.1988 | 15.2605 | 91.5249 | 91.4685 | 91.5456 | 91.4892
1188.7812 | 122.2504 | -14.9414 | 107.2952 | 0.48354 | 0.51809 | 0.53743 | 0.51067 | 0.59935 | 0.6121 | 0.46835 | 107.0931 | 107.0953 | 107.1092 | 107.0247 | 14.6526 | 14.8974 | 14.7135 | 14.7797 | 0.51559 | 0.55014 | 0.56948 | 0.54271 | 0.6314 | 0.64414 | 0.50039 | 107.1252 | 107.1274 | 107.1413 | 107.0567 | 14.6847 | 14.9294 | 14.7455 | 14.8118 | 92.4405 | 92.3796 | 92.4566 | 92.3957
1190.5312 | 122.2412 | -14.534 | 107.6935 | 0.4927 | 0.52725 | 0.53743 | 0.51525 | 0.60851 | 0.60752 | 0.46835 | 107.4777 | 107.48 | 107.4938 | 107.4047 | 14.268 | 14.5174 | 14.3198 | 14.3952 | 0.52474 | 0.5593 | 0.56948 | 0.54729 | 0.64055 | 0.63956 | 0.50039 | 107.5098 | 107.512 | 107.5259 | 107.4368 | 14.3001 | 14.5494 | 14.3518 | 14.4272 | 93.2097 | 93.158 | 93.2258 | 93.174
1192.2188 | 122.3557 | -14.1449 | 108.0231 | 0.50186 | 0.52267 | 0.54201 | 0.5244 | 0.61309 | 0.60294 | 0.46835 | 107.8257 | 107.8371 | 107.8372 | 107.7527 | 13.9201 | 14.1649 | 13.9764 | 14.0472 | 0.5339 | 0.55472 | 0.57405 | 0.55645 | 0.64513 | 0.63498 | 0.50039 | 107.8577 | 107.8691 | 107.8692 | 107.7848 | 13.9521 | 14.1969 | 14.0084 | 14.0793 | 93.9056 | 93.8493 | 93.9171 | 93.8608
1193.9688 | 122.3648 | -13.8977 | 108.2428 | 0.51101 | 0.52725 | 0.54659 | 0.52898 | 0.62224 | 0.60752 | 0.48666 | 108.105 | 108.1073 | 108.1256 | 108.0321 | 13.6408 | 13.8764 | 13.7017 | 13.7634 | 0.54306 | 0.5593 | 0.57863 | 0.56102 | 0.65429 | 0.63956 | 0.51871 | 108.137 | 108.1393 | 108.1577 | 108.0641 | 13.6729 | 13.9085 | 13.7337 | 13.7954 | 94.4641 | 94.4033 | 94.4848 | 94.4239
1195.7344 | 122.3419 | -13.4583 | 108.6868 | 0.52475 | 0.52725 | 0.55575 | 0.53356 | 0.61767 | 0.62125 | 0.47751 | 108.5079 | 108.5056 | 108.5193 | 108.4396 | 13.2425 | 13.4782 | 13.2805 | 13.3651 | 0.55679 | 0.5593 | 0.58779 | 0.5656 | 0.64971 | 0.6533 | 0.50955 | 108.5399 | 108.5377 | 108.5514 | 108.4716 | 13.2746 | 13.5102 | 13.3125 | 13.3971 | 95.2654 | 95.2274 | 95.2768 | 95.2389
1197.4062 | 122.3053 | -13.3667 | 108.7784 | 0.54306 | 0.54557 | 0.5649 | 0.54729 | 0.6314 | 0.63499 | 0.49124 | 108.6407 | 108.643 | 108.6475 | 108.5632 | 13.1098 | 13.35 | 13.166 | 13.2232 | 0.57511 | 0.57761 | 0.59695 | 0.57934 | 0.66344 | 0.66703 | 0.52329 | 108.6727 | 108.675 | 108.6796 | 108.5953 | 13.1418 | 13.382 | 13.1981 | 13.2552 | 95.5309 | 95.4746 | 95.5378 | 95.4815
1199.1562 | 122.3694 | -13.0142 | 109.1629 | 0.53848 | 0.55473 | 0.58322 | 0.54729 | 0.64055 | 0.63957 | 0.50498 | 108.9886 | 108.9955 | 109.0001 | 108.9204 | 12.7572 | 13.002 | 12.8272 | 12.8798 | 0.57053 | 0.58677 | 0.61526 | 0.57934 | 0.6726 | 0.67161 | 0.53702 | 109.0207 | 109.0276 | 109.0321 | 108.9524 | 12.7893 | 13.0341 | 12.8592 | 12.9119 | 96.2314 | 96.1614 | 96.2428 | 96.1729
1200.8438 | 122.3053 | -12.6663 | 109.4925 | 0.5568 | 0.56388 | 0.59696 | 0.57019 | 0.65429 | 0.65788 | 0.52329 | 109.3503 | 109.3481 | 109.3572 | 109.273 | 12.4047 | 12.6449 | 12.4655 | 12.5273 | 0.58884 | 0.59593 | 0.629 | 0.60223 | 0.68633 | 0.68992 | 0.55533 | 109.3824 | 109.3802 | 109.3892 | 109.305 | 12.4368 | 12.677 | 12.4976 | 12.5593 | 96.9456 | 96.8848 | 96.9524 | 96.8917
1202.5781 | 122.3373 | -12.2681 | 109.8679 | 0.57053 | 0.57762 | 0.60153 | 0.58392 | 0.66344 | 0.67162 | 0.53244 | 109.6937 | 109.6961 | 109.7051 | 109.6256 | 12.0568 | 12.297 | 12.1176 | 12.1748 | 0.60258 | 0.60966 | 0.63358 | 0.61597 | 0.69549 | 0.70366 | 0.56449 | 109.7258 | 109.7281 | 109.7372 | 109.6576 | 12.0888 | 12.3291 | 12.1496 | 12.2068 | 97.6369 | 97.5762 | 97.6483 | 97.5876
1204.25 | 122.2733 | -11.9247 | 110.2844 | 0.57969 | 0.5822 | 0.61069 | 0.5885 | 0.6726 | 0.67619 | 0.5416 | 110.1012 | 110.0945 | 110.108 | 110.0239 | 11.6676 | 11.9033 | 11.7238 | 11.781 | 0.61173 | 0.61424 | 0.64273 | 0.62054 | 0.70464 | 0.70824 | 0.57365 | 110.1332 | 110.1265 | 110.14 | 110.056 | 11.6997 | 11.9353 | 11.7559 | 11.8131 | 98.4336 | 98.3774 | 98.4404 | 98.3842
1206.0156 | 122.3145 | -11.5356 | 110.6873 | 0.59342 | 0.59593 | 0.62901 | 0.59308 | 0.69091 | 0.68077 | 0.54618 | 110.4858 | 110.4974 | 110.5063 | 110.4269 | 11.251 | 11.4959 | 11.3255 | 11.3873 | 0.62547 | 0.62798 | 0.66105 | 0.62512 | 0.72296 | 0.71282 | 0.57822 | 110.5178 | 110.5294 | 110.5384 | 110.4589 | 11.2831 | 11.5279 | 11.3575 | 11.4194 | 99.2348 | 99.1603 | 99.2553 | 99.1808
1207.7031 | 122.2504 | -11.2244 | 111.0352 | 0.598 | 0.58678 | 0.61985 | 0.59308 | 0.68176 | 0.68535 | 0.5416 | 110.8338 | 110.8271 | 110.8451 | 110.7474 | 10.9122 | 11.1662 | 10.9913 | 11.0394 | 0.63005 | 0.61882 | 0.65189 | 0.62512 | 0.7138 | 0.7174 | 0.57365 | 110.8658 | 110.8591 | 110.8772 | 110.7795 | 10.9443 | 11.1983 | 11.0233 | 11.0714 | 99.9215 | 99.8425 | 99.9329 | 99.8538
1209.3906 | 122.2366 | -10.7941 | 111.438 | 0.63005 | 0.61425 | 0.64732 | 0.62055 | 0.70922 | 0.70824 | 0.56907 | 111.2458 | 111.2346 | 111.2388 | 111.1595 | 10.5139 | 10.7588 | 10.5884 | 10.6411 | 0.66209 | 0.64629 | 0.67936 | 0.65259 | 0.74127 | 0.74029 | 0.60111 | 111.2779 | 111.2666 | 111.2709 | 111.1916 | 10.546 | 10.7908 | 10.6204 | 10.6731 | 100.7319 | 100.6574 | 100.7249 | 100.6505
1211.1406 | 122.3145 | -10.5469 | 111.6531 | 0.63005 | 0.62341 | 0.6519 | 0.62971 | 0.71838 | 0.7174 | 0.57365 | 111.4747 | 111.4773 | 111.4861 | 111.3976 | 10.2759 | 10.5161 | 10.3183 | 10.3984 | 0.66209 | 0.65545 | 0.68394 | 0.66175 | 0.75042 | 0.74944 | 0.60569 | 111.5068 | 111.5093 | 111.5181 | 111.4297 | 10.3079 | 10.5482 | 10.3503 | 10.4305 | 101.1989 | 101.1565 | 101.2102 | 101.1678
1212.8906 | 122.3465 | -10.2722 | 111.9003 | 0.63005 | 0.62799 | 0.6519 | 0.62971 | 0.7138 | 0.71282 | 0.57823 | 111.7586 | 111.7566 | 111.7791 | 111.6815 | 9.9875 | 10.2415 | 10.071 | 10.1192 | 0.66209 | 0.66003 | 0.68394 | 0.66175 | 0.74585 | 0.74486 | 0.61027 | 111.7907 | 111.7886 | 111.8111 | 111.7136 | 10.0195 | 10.2735 | 10.1031 | 10.1512 | 101.7712 | 101.6876 | 101.7916 | 101.7081
1214.6406 | 122.3465 | -9.9609 | 112.2345 | 0.64837 | 0.65088 | 0.66105 | 0.63887 | 0.71838 | 0.73571 | 0.59196 | 112.0516 | 112.0588 | 112.0629 | 111.9746 | 9.699 | 9.9347 | 9.7734 | 9.8307 | 0.68041 | 0.68292 | 0.6931 | 0.67091 | 0.75042 | 0.76776 | 0.624 | 112.0837 | 112.0908 | 112.095 | 112.0066 | 9.7311 | 9.9668 | 9.8055 | 9.8628 | 102.3526 | 102.2782 | 102.3639 | 102.2895
1216.3438 | 122.3099 | -9.6817 | 112.5 | 0.6621 | 0.6463 | 0.67021 | 0.64802 | 0.74127 | 0.73571 | 0.60112 | 112.3355 | 112.3427 | 112.3468 | 112.2539 | 9.4106 | 9.66 | 9.485 | 9.5469 | 0.69414 | 0.67835 | 0.70226 | 0.68007 | 0.77331 | 0.76776 | 0.63316 | 112.3675 | 112.3747 | 112.3788 | 112.286 | 9.4426 | 9.6921 | 9.517 | 9.5789 | 102.9249 | 102.8505 | 102.9362 | 102.8618
1218.0938 | 122.3145 | -9.4254 | 112.7655 | 0.6621 | 0.6463 | 0.67937 | 0.65718 | 0.73211 | 0.74029 | 0.59654 | 112.5965 | 112.6037 | 112.6123 | 112.5241 | 9.1496 | 9.3991 | 9.224 | 9.2722 | 0.69414 | 0.67835 | 0.71141 | 0.68922 | 0.76416 | 0.77233 | 0.62858 | 112.6285 | 112.6357 | 112.6444 | 112.5561 | 9.1817 | 9.4311 | 9.2561 | 9.3042 | 103.4468 | 103.3725 | 103.4627 | 103.3883
1219.8438 | 122.3053 | -41.3452 | 80.9463 | 0.51101 | 0.46315 | 0.47791 | 0.45115 | 0.54442 | 0.55258 | 0.42257 | 85.3132 | 85.1994 | 85.3578 | 85.2147 | 36.6324 | 36.6111 | 36.5158 | 36.6359 | 0.54306 | 0.49519 | 0.50995 | 0.48319 | 0.57646 | 0.58462 | 0.45461 | 85.3453 | 85.2315 | 85.3899 | 85.2468 | 36.6645 | 36.6432 | 36.5478 | 36.668 | 48.6808 | 48.7974 | 48.7254 | 48.842
1221.5312 | 121.9894 | -29.4846 | 92.2943 | 1.0696 | 1.237 | 1.2563 | 1.2158 | 1.2723 | 1.3355 | 1.2146 | 98.014 | 97.9972 | 97.7009 | 97.5735 | 23.3145 | 23.353 | 23.6047 | 23.7118 | 1.1016 | 1.269 | 1.2883 | 1.2478 | 1.3044 | 1.3675 | 1.2466 | 98.046 | 98.0293 | 97.7329 | 97.6056 | 23.3466 | 23.3851 | 23.6368 | 23.7438 | 74.6995 | 74.4092 | 74.3864 | 74.0961
1223.2812 | 122.1588 | -0.49896 | 121.8384 | 0.85439 | 0.92103 | 0.93577 | 0.91815 | 0.95643 | 1.0058 | 0.87123 | 121.4101 | 121.4087 | 121.4026 | 121.3296 | 0.45569 | 0.50392 | 0.46556 | 0.49585 | 0.88644 | 0.95307 | 0.96781 | 0.9502 | 0.98848 | 1.0379 | 0.90327 | 121.4421 | 121.4408 | 121.4347 | 121.3616 | 0.48774 | 0.53596 | 0.4976 | 0.52789 | 120.9544 | 120.9445 | 120.9469 | 120.9371
1225.0312 | 122.1542 | -5.2917 | 116.748 | 1.2436 | 1.4568 | 1.4806 | 1.4493 | 1.5241 | 1.569 | 1.4298 | 116.2822 | 116.3537 | 116.1239 | 116.0591 | 5.2765 | 5.5215 | 5.456 | 5.6097 | 1.2756 | 1.4888 | 1.5127 | 1.4813 | 1.5561 | 1.601 | 1.4618 | 116.3142 | 116.3857 | 116.1559 | 116.0911 | 5.3086 | 5.5535 | 5.488 | 5.6417 | 111.0057 | 110.8262 | 110.8474 | 110.6679
1226.7969 | 122.1634 | -121.2158 | 0.73242 | -0.99528 | -1.405 | -1.4543 | -1.4123 | -1.4149 | -1.3795 | -1.4728 | 0.70263 | 0.78893 | 0.70541 | 0.67665 | -0.070797 | -0.022561 | 121.0099 | 121.0941 | -0.96323 | -1.373 | -1.4222 | -1.3803 | -1.3829 | -1.3475 | -1.4408 | 0.73468 | 0.82098 | 0.73746 | 0.70869 | -0.038754 | 0.009482 | 121.042 | 121.1261 | 0.77343 | -120.3073 | 0.77621 | -120.3045
1228.5625 | 122.2824 | -120.9778 | 0.97046 | -0.97238 | -1.3546 | -1.4085 | -1.3665 | -1.3692 | -1.32 | -1.4224 | 0.89493 | 0.98124 | 0.91144 | 0.86897 | -0.075375 | -0.027139 | 120.8909 | 120.9751 | -0.94034 | -1.3226 | -1.3764 | -1.3345 | -1.3371 | -1.2879 | -1.3904 | 0.92697 | 1.0133 | 0.94348 | 0.90101 | -0.043332 | 0.004904 | 120.9229 | 121.0071 | 0.97031 | -119.996 | 0.98681 | -119.9795
1230.25 | 122.2 | -120.932 | 1.1719 | -1.064 | -1.4554 | -1.5092 | -1.4718 | -1.4836 | -1.439 | -1.5369 | 1.1055 | 1.1919 | 1.1037 | 1.075 | -0.079953 | -0.027139 | 120.7032 | 120.7965 | -1.0319 | -1.4233 | -1.4772 | -1.4398 | -1.4516 | -1.407 | -1.5048 | 1.1376 | 1.2239 | 1.1358 | 1.1071 | -0.04791 | 0.004904 | 120.7352 | 120.8286 | 1.1855 | -119.5976 | 1.1837 | -119.5995
1232 | 122.3053 | -121.0373 | 1.0208 | -0.97238 | -1.3455 | -1.4039 | -1.3574 | -1.3554 | -1.32 | -1.4133 | 1.0048 | 1.082 | 1.003 | 0.97886 | -0.079953 | -0.027139 | 120.5933 | 120.911 | -0.94034 | -1.3134 | -1.3719 | -1.3253 | -1.3234 | -1.2879 | -1.3812 | 1.0369 | 1.114 | 1.035 | 1.0109 | -0.04791 | 0.004904 | 120.6253 | 120.943 | 1.0848 | -119.5885 | 1.083 | -119.5903
1233.75 | 122.2229 | -121.0693 | 1.0712 | -1.2425 | -1.6477 | -1.6969 | -1.6641 | -1.6805 | -1.6405 | -1.7292 | 1.0048 | 1.082 | 1.003 | 0.98344 | -0.079953 | -0.027139 | 120.6025 | 120.9201 | -1.2105 | -1.6156 | -1.6649 | -1.6321 | -1.6484 | -1.6084 | -1.6971 | 1.0369 | 1.114 | 1.035 | 1.0155 | -0.04791 | 0.004904 | 120.6345 | 120.9522 | 1.0848 | -119.5976 | 1.083 | -119.5995
1235.4375 | 122.2366 | -120.8633 | 1.2817 | -1.302 | -1.7164 | -1.7793 | -1.7236 | -1.7583 | -1.7183 | -1.7933 | 1.2383 | 1.3292 | 1.1861 | 1.2124 | -0.079953 | -0.027139 | 120.3598 | 120.6912 | -1.27 | -1.6843 | -1.7473 | -1.6916 | -1.7263 | -1.6863 | -1.7612 | 1.2704 | 1.3613 | 1.2182 | 1.2444 | -0.04791 | 0.004904 | 120.3918 | 120.7233 | 1.3183 | -119.1215 | 1.2661 | -119.1737
1237.1875 | 122.3328 | -121.0236 | 1.0757 | -1.2562 | -1.6431 | -1.6923 | -1.655 | -1.6667 | -1.6359 | -1.7292 | 1.0369 | 1.1323 | 0.99842 | 1.0201 | -0.079953 | -0.027139 | 120.575 | 120.8972 | -1.2242 | -1.6111 | -1.6603 | -1.6229 | -1.6347 | -1.6038 | -1.6971 | 1.0689 | 1.1644 | 1.0305 | 1.0521 | -0.04791 | 0.004904 | 120.607 | 120.9293 | 1.1168 | -119.5381 | 1.0784 | -119.5766
1238.9219 | 122.2412 | -120.5246 | 1.6022 | -1.2059 | -1.5744 | -1.6282 | -1.5817 | -1.5981 | -1.5535 | -1.6559 | 1.3482 | 1.4391 | 1.3052 | 1.3177 | -0.084531 | -0.031717 | 120.2591 | 120.5905 | -1.1738 | -1.5424 | -1.5962 | -1.5497 | -1.566 | -1.5214 | -1.6239 | 1.3802 | 1.4712 | 1.3372 | 1.3498 | -0.052488 | 0.000326 | 120.2911 | 120.6225 | 1.4327 | -118.9109 | 1.3897 | -118.9539
1240.6719 | 122.1909 | -120.6116 | 1.5335 | -1.3936 | -1.7759 | -1.8343 | -1.7969 | -1.8178 | -1.7824 | -1.8665 | 1.4627 | 1.5582 | 1.4196 | 1.4413 | -0.08911 | -0.027139 | 120.1538 | 120.4852 | -1.3616 | -1.7438 | -1.8022 | -1.7649 | -1.7858 | -1.7504 | -1.8345 | 1.4947 | 1.5902 | 1.4517 | 1.4734 | -0.057067 | 0.004904 | 120.1858 | 120.5172 | 1.5518 | -118.6911 | 1.5087 | -118.7341
1242.3594 | 122.2504 | -120.7901 | 1.3367 | -1.4806 | -1.8766 | -1.9304 | -1.9022 | -1.9277 | -1.8877 | -1.9581 | 1.2749 | 1.3613 | 1.2273 | 1.249 | -0.08911 | -0.027139 | 120.3415 | 120.6637 | -1.4485 | -1.8446 | -1.8984 | -1.8702 | -1.8956 | -1.8557 | -1.926 | 1.307 | 1.3933 | 1.2594 | 1.2811 | -0.057067 | 0.004904 | 120.3735 | 120.6958 | 1.3641 | -119.0665 | 1.3164 | -119.1142
1244.1094 | 122.2504 | -120.9915 | 1.1444 | -1.4943 | -1.8949 | -1.9396 | -1.9114 | -1.9277 | -1.9014 | -1.9901 | 1.0781 | 1.1736 | 1.0305 | 1.0659 | -0.079953 | -0.027139 | 120.5429 | 120.8698 | -1.4623 | -1.8629 | -1.9075 | -1.8793 | -1.8956 | -1.8694 | -1.9581 | 1.1101 | 1.2056 | 1.0625 | 1.0979 | -0.04791 | 0.004904 | 120.575 | 120.9018 | 1.158 | -119.4649 | 1.1104 | -119.5125
1245.8438 | 122.3328 | -121.0602 | 0.99335 | -1.5538 | -1.9453 | -1.99 | -1.9526 | -1.9735 | -1.9426 | -2.0176 | 0.95903 | 1.0545 | 0.91602 | 0.94681 | -0.084531 | -0.031717 | 120.662 | 120.9842 | -1.5218 | -1.9133 | -1.9579 | -1.9205 | -1.9414 | -1.9106 | -1.9856 | 0.99107 | 1.0865 | 0.94806 | 0.97886 | -0.052488 | 0.000326 | 120.694 | 121.0163 | 1.0436 | -119.7029 | 1.0005 | -119.746
1247.5938 | 122.3145 | -121.138 | 0.93842 | -1.6958 | -2.1056 | -2.1548 | -2.1082 | -2.152 | -2.112 | -2.187 | 0.91324 | 1.0041 | 0.86565 | 0.89186 | -0.084531 | -0.031717 | 120.7169 | 121.0437 | -1.6637 | -2.0735 | -2.1227 | -2.0762 | -2.12 | -2.08 | -2.1549 | 0.94529 | 1.0362 | 0.8977 | 0.92391 | -0.052488 | 0.000326 | 120.749 | 121.0758 | 0.99778 | -119.8037 | 0.95019 | -119.8513
1249.2812 | 122.2 | -121.2296 | 0.91095 | -1.769 | -2.1697 | -2.2189 | -2.1815 | -2.2207 | -2.1945 | -2.2602 | 0.83541 | 0.93088 | 0.80156 | 0.82318 | -0.079953 | -0.031717 | 120.781 | 121.1078 | -1.737 | -2.1376 | -2.1868 | -2.1494 | -2.1886 | -2.1624 | -2.2282 | 0.86745 | 0.96292 | 0.8336 | 0.85522 | -0.04791 | 0.000326 | 120.8131 | 121.1399 | 0.91536 | -119.9456 | 0.88151 | -119.9795
1251.0312 | 122.1863 | -121.2387 | 0.90637 | -1.7599 | -2.133 | -2.1914 | -2.1494 | -2.1978 | -2.1532 | -2.2236 | 0.82625 | 0.91256 | 0.77867 | 0.80944 | -0.079953 | -0.036295 | 120.7993 | 121.1216 | -1.7278 | -2.101 | -2.1594 | -2.1174 | -2.1657 | -2.1212 | -2.1916 | 0.8583 | 0.94461 | 0.81071 | 0.84148 | -0.04791 | -0.004252 | 120.8314 | 121.1536 | 0.90621 | -119.9731 | 0.85862 | -120.0207
1252.7969 | 122.2733 | -121.2067 | 0.90179 | -1.6225 | -1.9728 | -2.022 | -1.9755 | -2.0101 | -1.9838 | -2.0496 | 0.83083 | 0.93546 | 0.78782 | 0.82776 | -0.084531 | -0.027139 | 120.7719 | 121.0987 | -1.5905 | -1.9407 | -1.99 | -1.9434 | -1.978 | -1.9518 | -2.0176 | 0.86288 | 0.9675 | 0.81987 | 0.8598 | -0.052488 | 0.004904 | 120.8039 | 121.1307 | 0.91536 | -119.941 | 0.87235 | -119.984
1254.5625 | 122.3236 | -121.2204 | 0.82398 | -1.7187 | -2.0735 | -2.1182 | -2.0945 | -2.1291 | -2.0846 | -2.1549 | 0.79878 | 0.88967 | 0.75577 | 0.78655 | -0.079953 | -0.036295 | 120.8222 | 121.1536 | -1.6866 | -2.0415 | -2.0861 | -2.0625 | -2.0971 | -2.0525 | -2.1229 | 0.83083 | 0.92171 | 0.78782 | 0.81859 | -0.04791 | -0.004252 | 120.8543 | 121.1856 | 0.87874 | -120.0234 | 0.83573 | -120.0664
1256.2656 | 122.3236 | -121.2524 | 0.82855 | -1.7507 | -2.0964 | -2.141 | -2.1128 | -2.1474 | -2.112 | -2.1778 | 0.78047 | 0.87135 | 0.73746 | 0.76365 | -0.08911 | -0.027139 | 120.8405 | 121.1719 | -1.7187 | -2.0644 | -2.109 | -2.0808 | -2.1154 | -2.08 | -2.1458 | 0.81251 | 0.9034 | 0.7695 | 0.79569 | -0.057067 | 0.004904 | 120.8726 | 121.204 | 0.86958 | -120.0601 | 0.82657 | -120.1031
1258.0156 | 122.2046 | -121.2524 | 0.90637 | -1.7736 | -2.1056 | -2.1548 | -2.1128 | -2.1108 | -2.1166 | -2.187 | 0.80794 | 0.91714 | 0.76951 | 0.7957 | -0.079953 | -0.036295 | 120.8085 | 121.1399 | -1.7416 | -2.0735 | -2.1227 | -2.0808 | -2.0788 | -2.0846 | -2.1549 | 0.83998 | 0.94918 | 0.80155 | 0.82775 | -0.04791 | -0.004252 | 120.8405 | 121.1719 | 0.88789 | -120.0005 | 0.84946 | -120.039
1259.7656 | 122.3373 | -121.2616 | 0.7782 | -1.7828 | -2.0964 | -2.1502 | -2.1128 | -2.1154 | -2.112 | -2.187 | 0.74384 | 0.8393 | 0.70999 | 0.7316 | -0.084531 | -0.031717 | 120.8772 | 121.1994 | -1.7507 | -2.0644 | -2.1182 | -2.0808 | -2.0833 | -2.08 | -2.1549 | 0.77588 | 0.87134 | 0.74204 | 0.76364 | -0.052488 | 0.000326 | 120.9092 | 121.2314 | 0.82837 | -120.1333 | 0.79452 | -120.1672
1261.4688 | 122.1909 | -121.3211 | 0.8606 | -1.7873 | -2.101 | -2.141 | -2.1128 | -2.1154 | -2.1075 | -2.1778 | 0.76216 | 0.85304 | 0.71915 | 0.74533 | -0.084531 | -0.036295 | 120.8588 | 121.1857 | -1.7553 | -2.0689 | -2.109 | -2.0808 | -2.0833 | -2.0754 | -2.1458 | 0.7942 | 0.88508 | 0.75119 | 0.77738 | -0.052488 | -0.004252 | 120.8909 | 121.2177 | 0.84669 | -120.0967 | 0.80368 | -120.1397
1263.2031 | 122.2641 | -121.3257 | 0.76446 | -1.7965 | -2.0964 | -2.1456 | -2.1128 | -2.1062 | -2.1029 | -2.1733 | 0.71637 | 0.81641 | 0.67337 | 0.69954 | -0.084531 | -0.036295 | 120.9046 | 121.2269 | -1.7644 | -2.0644 | -2.1136 | -2.0808 | -2.0742 | -2.0708 | -2.1412 | 0.74841 | 0.84845 | 0.70541 | 0.73159 | -0.052488 | -0.004252 | 120.9367 | 121.2589 | 0.8009 | -120.1883 | 0.7579 | -120.2313
1264.9531 | 122.3328 | -121.2936 | 0.75531 | -1.8423 | -2.133 | -2.1731 | -2.1494 | -2.1566 | -2.1624 | -2.2328 | 0.71637 | 0.80725 | 0.66879 | 0.70412 | -0.08911 | -0.031717 | 120.8955 | 121.2269 | -1.8102 | -2.101 | -2.1411 | -2.1174 | -2.1245 | -2.1304 | -2.2007 | 0.74841 | 0.83929 | 0.70083 | 0.73617 | -0.057067 | 0.000326 | 120.9275 | 121.2589 | 0.80548 | -120.1791 | 0.7579 | -120.2267
1266.6406 | 122.3465 | -121.3165 | 0.76904 | -1.8056 | -2.101 | -2.1456 | -2.1037 | -2.12 | -2.1075 | -2.1778 | 0.72095 | 0.81641 | 0.66879 | 0.7087 | -0.084531 | -0.036295 | 120.9001 | 121.2269 | -1.7736 | -2.0689 | -2.1136 | -2.0716 | -2.0879 | -2.0754 | -2.1458 | 0.75299 | 0.84845 | 0.70083 | 0.74075 | -0.052488 | -0.004252 | 120.9321 | 121.2589 | 0.80548 | -120.1791 | 0.75332 | -120.2313
1268.3281 | 122.2733 | -121.2753 | 0.82398 | -1.8926 | -2.1834 | -2.2326 | -2.1952 | -2.2115 | -2.2128 | -2.2694 | 0.753 | 0.84846 | 0.70999 | 0.74076 | -0.084531 | -0.031717 | 120.8588 | 121.1948 | -1.8606 | -2.1514 | -2.2006 | -2.1632 | -2.1795 | -2.1807 | -2.2374 | 0.78504 | 0.8805 | 0.74204 | 0.7728 | -0.052488 | 0.000326 | 120.8909 | 121.2269 | 0.83753 | -120.1058 | 0.79452 | -120.1489
1270.0781 | 122.2412 | -121.225 | 0.86975 | -1.8697 | -2.1605 | -2.196 | -2.1769 | -2.1795 | -2.1807 | -2.2419 | 0.82168 | 0.90798 | 0.77409 | 0.80944 | -0.084531 | -0.031717 | 120.8039 | 121.1307 | -1.8377 | -2.1285 | -2.164 | -2.1449 | -2.1474 | -2.1487 | -2.2099 | 0.85372 | 0.94003 | 0.80613 | 0.84148 | -0.052488 | 0.000326 | 120.8359 | 121.1628 | 0.90621 | -119.9822 | 0.85862 | -120.0298
1271.8438 | 122.2687 | -121.1197 | 0.99335 | -1.9522 | -2.2384 | -2.2921 | -2.2502 | -2.2664 | -2.2631 | -2.3289 | 0.93156 | 1.0316 | 0.89312 | 0.91934 | -0.08911 | -0.031717 | 120.6849 | 121.0071 | -1.9201 | -2.2063 | -2.2601 | -2.2181 | -2.2344 | -2.2311 | -2.2969 | 0.9636 | 1.0637 | 0.92517 | 0.95138 | -0.057067 | 0.000326 | 120.7169 | 121.0391 | 1.0207 | -119.7533 | 0.98223 | -119.7917
1273.5938 | 122.3236 | -120.9091 | 1.149 | -1.9934 | -2.2979 | -2.3471 | -2.3097 | -2.3122 | -2.3226 | -2.3839 | 1.1284 | 1.2193 | 1.0854 | 1.1162 | -0.08911 | -0.022561 | 120.4788 | 120.8148 | -1.9613 | -2.2658 | -2.315 | -2.2776 | -2.2802 | -2.2906 | -2.3518 | 1.1605 | 1.2514 | 1.1175 | 1.1483 | -0.057067 | 0.009482 | 120.5109 | 120.8469 | 1.2175 | -119.3504 | 1.1745 | -119.3934
1275.2812 | 122.2458 | -121.0144 | 1.1078 | -2.062 | -2.3757 | -2.4203 | -2.3784 | -2.3946 | -2.4005 | -2.4617 | 1.014 | 1.1095 | 0.98011 | 0.99718 | -0.08911 | -0.036295 | 120.6025 | 120.9293 | -2.03 | -2.3437 | -2.3883 | -2.3463 | -2.3626 | -2.3684 | -2.4296 | 1.046 | 1.1415 | 1.0122 | 1.0292 | -0.057067 | -0.004252 | 120.6345 | 120.9613 | 1.1031 | -119.5885 | 1.0692 | -119.6223
1277.0156 | 122.2778 | -120.9915 | 1.0574 | -2.0483 | -2.3391 | -2.3883 | -2.3509 | -2.3672 | -2.3684 | -2.4251 | 1.0231 | 1.1095 | 0.96638 | 1.0063 | -0.084531 | -0.036295 | 120.5979 | 120.9201 | -2.0163 | -2.307 | -2.3563 | -2.3188 | -2.3351 | -2.3364 | -2.393 | 1.0552 | 1.1415 | 0.99842 | 1.0384 | -0.052488 | -0.004252 | 120.6299 | 120.9522 | 1.1077 | -119.5748 | 1.0509 | -119.6315
1278.7656 | 122.3236 | -119.5908 | 2.4948 | -2.0712 | -2.3666 | -2.4112 | -2.3784 | -2.3855 | -2.3959 | -2.4571 | 2.4882 | 2.5838 | 2.4543 | 2.4716 | -0.079953 | -0.040873 | 119.1007 | 119.2308 | -2.0392 | -2.3345 | -2.3791 | -2.3463 | -2.3534 | -2.3639 | -2.4251 | 2.5203 | 2.6159 | 2.4864 | 2.5037 | -0.04791 | -0.00883 | 119.1328 | 119.2628 | 2.5682 | -116.6125 | 2.5343 | -116.6464
1280.4531 | 122.2137 | -119.4717 | 2.6047 | -2.2543 | -2.5863 | -2.6264 | -2.5936 | -2.6052 | -2.6202 | -2.6814 | 2.6393 | 2.7349 | 2.5962 | 2.6273 | -0.084531 | -0.031717 | 118.9588 | 119.0797 | -2.2223 | -2.5543 | -2.5943 | -2.5615 | -2.5732 | -2.5882 | -2.6494 | 2.6714 | 2.767 | 2.6283 | 2.6594 | -0.052488 | 0.000326 | 118.9909 | 119.1117 | 2.7239 | -116.3195 | 2.6808 | -116.3626
1282.2188 | 122.2275 | -119.6823 | 2.4307 | -2.1948 | -2.5314 | -2.5806 | -2.5295 | -2.5503 | -2.5607 | -2.6265 | 2.3555 | 2.4419 | 2.3032 | 2.3343 | -0.08911 | -0.036295 | 119.2518 | 119.3681 | -2.1628 | -2.4994 | -2.5486 | -2.4974 | -2.5182 | -2.5287 | -2.5945 | 2.3875 | 2.4739 | 2.3353 | 2.3663 | -0.057067 | -0.004252 | 119.2839 | 119.4002 | 2.4446 | -116.8964 | 2.3923 | -116.9486
1283.9688 | 122.3145 | -120.5658 | 1.474 | -2.3963 | -2.7603 | -2.8049 | -2.7538 | -2.7792 | -2.8034 | -2.8646 | 1.4352 | 1.5353 | 1.3922 | 1.4322 | -0.084531 | -0.031717 | 120.1675 | 120.2838 | -2.3642 | -2.7283 | -2.7729 | -2.7218 | -2.7471 | -2.7713 | -2.8325 | 1.4672 | 1.5673 | 1.4242 | 1.4642 | -0.052488 | 0.000326 | 120.1996 | 120.3158 | 1.5197 | -118.7323 | 1.4767 | -118.7754
1285.7188 | 122.2092 | -120.7214 | 1.4236 | -2.3917 | -2.7695 | -2.8049 | -2.7584 | -2.77 | -2.7988 | -2.8691 | 1.339 | 1.4254 | 1.3052 | 1.3315 | -0.084531 | -0.036295 | 120.2728 | 120.3936 | -2.3596 | -2.7375 | -2.7729 | -2.7263 | -2.738 | -2.7668 | -2.8371 | 1.3711 | 1.4574 | 1.3372 | 1.3635 | -0.052488 | -0.004252 | 120.3049 | 120.4257 | 1.4236 | -118.9338 | 1.3897 | -118.9676
1287.4062 | 122.2137 | -120.7123 | 1.4328 | -2.3276 | -2.6871 | -2.7271 | -2.6805 | -2.7151 | -2.721 | -2.773 | 1.3436 | 1.43 | 1.2914 | 1.3269 | -0.079953 | -0.031717 | 120.2728 | 120.389 | -2.2955 | -2.655 | -2.6951 | -2.6485 | -2.683 | -2.6889 | -2.741 | 1.3757 | 1.462 | 1.3235 | 1.3589 | -0.04791 | 0.000326 | 120.3049 | 120.4211 | 1.4236 | -118.9292 | 1.3714 | -118.9814
1289.1562 | 122.2366 | -120.7031 | 1.442 | -2.3596 | -2.7329 | -2.7729 | -2.7492 | -2.77 | -2.7759 | -2.8279 | 1.3345 | 1.43 | 1.296 | 1.3315 | -0.08911 | -0.036295 | 120.2728 | 120.3936 | -2.3276 | -2.7008 | -2.7409 | -2.7172 | -2.738 | -2.7439 | -2.7959 | 1.3665 | 1.462 | 1.3281 | 1.3635 | -0.057067 | -0.004252 | 120.3049 | 120.4257 | 1.4236 | -118.9383 | 1.3851 | -118.9768
1290.9062 | 122.2549 | -120.7306 | 1.3687 | -2.2314 | -2.6138 | -2.6493 | -2.6027 | -2.6327 | -2.6431 | -2.6952 | 1.2978 | 1.3842 | 1.2502 | 1.2811 | -0.084531 | -0.027139 | 120.3232 | 120.4348 | -2.1994 | -2.5818 | -2.6172 | -2.5707 | -2.6006 | -2.6111 | -2.6631 | 1.3299 | 1.4162 | 1.2823 | 1.3131 | -0.052488 | 0.004904 | 120.3552 | 120.4669 | 1.3824 | -119.0253 | 1.3348 | -119.0729
1292.5938 | 122.2504 | -120.6802 | 1.4191 | -2.3551 | -2.7649 | -2.8095 | -2.7813 | -2.8066 | -2.8171 | -2.8691 | 1.3482 | 1.4483 | 1.3143 | 1.3452 | -0.08911 | -0.031717 | 120.2591 | 120.3616 | -2.323 | -2.7329 | -2.7775 | -2.7492 | -2.7746 | -2.7851 | -2.8371 | 1.3802 | 1.4803 | 1.3464 | 1.3772 | -0.057067 | 0.000326 | 120.2911 | 120.3936 | 1.4373 | -118.9109 | 1.4034 | -118.9448
1294.2812 | 122.2504 | -120.5704 | 1.5564 | -2.2955 | -2.7329 | -2.7729 | -2.7355 | -2.7609 | -2.7759 | -2.8234 | 1.3894 | 1.4803 | 1.3418 | 1.3818 | -0.084531 | -0.031717 | 120.2225 | 120.3341 | -2.2635 | -2.7008 | -2.7409 | -2.7034 | -2.7288 | -2.7439 | -2.7913 | 1.4215 | 1.5124 | 1.3738 | 1.4139 | -0.052488 | 0.000326 | 120.2545 | 120.3662 | 1.4739 | -118.833 | 1.4263 | -118.8807
1296.0312 | 122.2641 | -119.5038 | 2.5772 | -2.1399 | -2.5497 | -2.5943 | -2.5523 | -2.564 | -2.5836 | -2.6311 | 2.5432 | 2.6296 | 2.4909 | 2.5357 | -0.084531 | -0.027139 | 119.0641 | 119.1758 | -2.1078 | -2.5177 | -2.5623 | -2.5203 | -2.532 | -2.5516 | -2.599 | 2.5752 | 2.6617 | 2.523 | 2.5678 | -0.052488 | 0.004904 | 119.0962 | 119.2079 | 2.6277 | -116.5209 | 2.5755 | -116.5732
1297.7969 | 122.3328 | -119.7418 | 2.3117 | -2.1399 | -2.5451 | -2.5989 | -2.5478 | -2.5549 | -2.5836 | -2.6402 | 2.2822 | 2.3732 | 2.2346 | 2.2702 | -0.079953 | -0.036295 | 119.3251 | 119.4368 | -2.1078 | -2.5131 | -2.5669 | -2.5157 | -2.5228 | -2.5516 | -2.6082 | 2.3143 | 2.4052 | 2.2666 | 2.3022 | -0.04791 | -0.004252 | 119.3571 | 119.4688 | 2.3622 | -117.0429 | 2.3145 | -117.0905
1299.5469 | 122.1909 | -117.2516 | 4.866 | -2.0758 | -2.4856 | -2.5302 | -2.4745 | -2.4908 | -2.5149 | -2.5716 | 4.7958 | 4.887 | 4.7526 | 4.5734 | -0.084531 | -0.031717 | 116.7932 | 116.9142 | -2.0437 | -2.4536 | -2.4982 | -2.4425 | -2.4587 | -2.4829 | -2.5395 | 4.8279 | 4.919 | 4.7847 | 4.6054 | -0.052488 | 0.000326 | 116.8253 | 116.9463 | 4.8803 | -111.9974 | 4.8371 | -112.0406
1301.2188 | 122.2687 | -117.1555 | 4.9484 | -1.9979 | -2.4078 | -2.4524 | -2.3967 | -2.4038 | -2.428 | -2.48 | 4.8462 | 4.9328 | 4.803 | 4.6192 | -0.084531 | -0.036295 | 116.7566 | 116.873 | -1.9659 | -2.3757 | -2.4204 | -2.3646 | -2.3717 | -2.3959 | -2.448 | 4.8782 | 4.9648 | 4.835 | 4.6512 | -0.052488 | -0.004252 | 116.7887 | 116.9051 | 4.9307 | -111.9104 | 4.8875 | -111.9536
1302.9688 | 122.3099 | -116.716 | 5.3192 | -1.9155 | -2.3116 | -2.3517 | -2.3051 | -2.3031 | -2.3364 | -2.393 | 5.3498 | 5.4319 | 5.3524 | 5.3289 | -0.084531 | -0.031717 | 116.285 | 116.5754 | -1.8835 | -2.2796 | -2.3196 | -2.2731 | -2.271 | -2.3043 | -2.361 | 5.3819 | 5.4639 | 5.3844 | 5.361 | -0.052488 | 0.000326 | 116.3171 | 116.6075 | 5.4343 | -110.9352 | 5.4369 | -110.9327
1304.7188 | 122.319 | -115.6082 | 6.4362 | -1.8331 | -2.2155 | -2.2601 | -2.2044 | -2.2069 | -2.2311 | -2.2969 | 6.3937 | 6.485 | 6.3687 | 6.1806 | -0.079953 | -0.027139 | 115.1908 | 115.3119 | -1.8011 | -2.1834 | -2.2281 | -2.1723 | -2.1749 | -2.199 | -2.2648 | 6.4257 | 6.517 | 6.4008 | 6.2127 | -0.04791 | 0.004904 | 115.2228 | 115.3439 | 6.4737 | -108.7971 | 6.4487 | -108.8221
1306.4219 | 122.2 | -116.2766 | 5.8411 | -1.4165 | -1.7667 | -1.8022 | -1.742 | -1.7125 | -1.732 | -1.8436 | 5.771 | 5.8623 | 5.7324 | 5.5442 | -0.079953 | -0.031717 | 115.8226 | 115.9391 | -1.3844 | -1.7347 | -1.7702 | -1.7099 | -1.6805 | -1.7 | -1.8116 | 5.8031 | 5.8943 | 5.7644 | 5.5762 | -0.04791 | 0.000326 | 115.8547 | 115.9711 | 5.851 | -110.0516 | 5.8123 | -110.0903
1308.1719 | 122.287 | -116.5237 | 5.5206 | -1.5996 | -1.9682 | -2.0083 | -1.9434 | -1.9277 | -1.961 | -2.0313 | 5.4597 | 5.5555 | 5.4165 | 5.2374 | -0.079953 | -0.031717 | 116.1294 | 116.2458 | -1.5676 | -1.9362 | -1.9762 | -1.9114 | -1.8956 | -1.9289 | -1.9993 | 5.4917 | 5.5875 | 5.4485 | 5.2694 | -0.04791 | 0.000326 | 116.1614 | 116.2778 | 5.5396 | -110.6697 | 5.4964 | -110.7129
1309.9219 | 122.2733 | -116.7297 | 5.3467 | -1.3707 | -1.6981 | -1.7381 | -1.6779 | -1.6576 | -1.6725 | -1.7704 | 5.2811 | 5.3723 | 5.2379 | 5.0588 | -0.08911 | -0.031717 | 116.3125 | 116.4289 | -1.3387 | -1.666 | -1.7061 | -1.6458 | -1.6255 | -1.6405 | -1.7383 | 5.3132 | 5.4044 | 5.27 | 5.0908 | -0.057067 | 0.000326 | 116.3446 | 116.461 | 5.3702 | -111.0314 | 5.327 | -111.0746
1311.6875 | 122.2321 | -117.2653 | 4.8706 | -1.3753 | -1.6981 | -1.7427 | -1.6733 | -1.653 | -1.6679 | -1.7704 | 4.7958 | 4.8916 | 4.7663 | 4.5917 | -0.075375 | -0.027139 | 116.7932 | 116.9188 | -1.3432 | -1.666 | -1.7107 | -1.6412 | -1.621 | -1.6359 | -1.7383 | 4.8279 | 4.9236 | 4.7984 | 4.6238 | -0.043332 | 0.004904 | 116.8253 | 116.9508 | 4.8712 | -111.9974 | 4.8417 | -112.0269
1313.4375 | 122.2458 | -116.9586 | 5.1407 | -1.3982 | -1.7255 | -1.761 | -1.6962 | -1.685 | -1.7046 | -1.7933 | 5.0247 | 5.1205 | 4.9861 | 4.8161 | -0.079953 | -0.027139 | 116.5643 | 116.6853 | -1.3661 | -1.6935 | -1.729 | -1.6641 | -1.653 | -1.6725 | -1.7612 | 5.0568 | 5.1525 | 5.0181 | 4.8481 | -0.04791 | 0.004904 | 116.5964 | 116.7173 | 5.1047 | -111.5396 | 5.0661 | -111.5782
1315.125 | 122.3236 | -116.3177 | 5.6946 | -1.3661 | -1.6614 | -1.7107 | -1.6412 | -1.6255 | -1.6496 | -1.7383 | 5.6657 | 5.7478 | 5.6179 | 5.4434 | -0.075375 | -0.027139 | 115.9279 | 116.0398 | -1.3341 | -1.6294 | -1.6786 | -1.6092 | -1.5935 | -1.6176 | -1.7063 | 5.6978 | 5.7798 | 5.65 | 5.4755 | -0.043332 | 0.004904 | 115.96 | 116.0718 | 5.7411 | -110.2622 | 5.6933 | -110.31
1316.875 | 122.2092 | -116.3406 | 5.8182 | -1.4256 | -1.7209 | -1.761 | -1.7007 | -1.6988 | -1.7229 | -1.7978 | 5.684 | 5.7798 | 5.65 | 5.4801 | -0.084531 | -0.022561 | 115.905 | 116.0306 | -1.3936 | -1.6889 | -1.729 | -1.6687 | -1.6667 | -1.6908 | -1.7658 | 5.7161 | 5.8119 | 5.682 | 5.5121 | -0.052488 | 0.009482 | 115.9371 | 116.0627 | 5.7686 | -110.221 | 5.7345 | -110.2551
1318.5469 | 122.3007 | -116.4047 | 5.6396 | -1.4394 | -1.7347 | -1.7839 | -1.7191 | -1.7217 | -1.7412 | -1.8207 | 5.6154 | 5.7066 | 5.563 | 5.3885 | -0.079953 | -0.027139 | 115.9966 | 116.1085 | -1.4073 | -1.7026 | -1.7519 | -1.687 | -1.6896 | -1.7092 | -1.7887 | 5.6474 | 5.7386 | 5.595 | 5.4205 | -0.04791 | 0.004904 | 116.0286 | 116.1405 | 5.6953 | -110.3812 | 5.6429 | -110.4336
1320.2344 | 122.2733 | -118.8858 | 3.241 | -1.4943 | -1.7805 | -1.816 | -1.7557 | -1.7583 | -1.8007 | -1.8665 | 3.4085 | 3.4859 | 3.4112 | 3.186 | -0.079953 | -0.036295 | 118.2034 | 118.3106 | -1.4623 | -1.7484 | -1.7839 | -1.7236 | -1.7263 | -1.7687 | -1.8345 | 3.4406 | 3.5179 | 3.4432 | 3.218 | -0.04791 | -0.004252 | 118.2354 | 118.3426 | 3.4885 | -114.7949 | 3.4911 | -114.7922
1321.9844 | 122.3648 | -119.6411 | 2.4216 | -1.5218 | -1.7988 | -1.8343 | -1.7832 | -1.7858 | -1.8282 | -1.8894 | 2.4013 | 2.506 | 2.3719 | 2.1969 | -0.079953 | -0.027139 | 119.1923 | 119.304 | -1.4897 | -1.7667 | -1.8022 | -1.7511 | -1.7537 | -1.7961 | -1.8574 | 2.4333 | 2.538 | 2.404 | 2.2289 | -0.04791 | 0.004904 | 119.2244 | 119.3361 | 2.4812 | -116.7911 | 2.4519 | -116.8204
1323.7344 | 122.2412 | -119.9341 | 2.179 | -1.5264 | -1.7942 | -1.8251 | -1.7648 | -1.7858 | -1.8282 | -1.8894 | 2.0991 | 2.1855 | 2.0514 | 1.8809 | -0.079953 | -0.031717 | 119.5082 | 119.6245 | -1.4943 | -1.7622 | -1.7931 | -1.7328 | -1.7537 | -1.7961 | -1.8574 | 2.1311 | 2.2175 | 2.0835 | 1.913 | -0.04791 | 0.000326 | 119.5403 | 119.6565 | 2.179 | -117.4091 | 2.1314 | -117.4568
1325.4062 | 122.2046 | -119.9936 | 2.1881 | -1.5309 | -1.7759 | -1.816 | -1.7603 | -1.7766 | -1.8282 | -1.8803 | 2.0579 | 2.1534 | 2.0194 | 1.8397 | -0.079953 | -0.027139 | 119.5586 | 119.6749 | -1.4989 | -1.7438 | -1.7839 | -1.7282 | -1.7446 | -1.7961 | -1.8482 | 2.0899 | 2.1855 | 2.0514 | 1.8718 | -0.04791 | 0.004904 | 119.5906 | 119.7069 | 2.1378 | -117.5007 | 2.0993 | -117.5392
1327.1562 | 122.3419 | -119.7418 | 2.3254 | -1.5584 | -1.7988 | -1.8434 | -1.7877 | -1.8087 | -1.8511 | -1.9031 | 2.2822 | 2.3915 | 2.2391 | 2.0733 | -0.084531 | -0.027139 | 119.3205 | 119.4368 | -1.5264 | -1.7667 | -1.8114 | -1.7557 | -1.7766 | -1.819 | -1.8711 | 2.3143 | 2.4236 | 2.2712 | 2.1053 | -0.052488 | 0.004904 | 119.3526 | 119.4688 | 2.3667 | -117.0383 | 2.3237 | -117.0814
1328.9062 | 122.1863 | -120.1172 | 2.0325 | -1.595 | -1.8217 | -1.8618 | -1.7969 | -1.827 | -1.8694 | -1.926 | 1.9983 | 2.0939 | 1.9599 | 1.7894 | -0.084531 | -0.022561 | 119.6089 | 119.7298 | -1.563 | -1.7896 | -1.8297 | -1.7649 | -1.7949 | -1.8373 | -1.894 | 2.0304 | 2.1259 | 1.9919 | 1.8214 | -0.052488 | 0.009482 | 119.641 | 119.7618 | 2.0829 | -117.6106 | 2.0444 | -117.6491
1330.5938 | 122.2137 | -120.2591 | 1.9089 | -1.682 | -1.8904 | -1.9304 | -1.8793 | -1.9139 | -1.961 | -2.0084 | 1.8061 | 1.9016 | 1.7676 | 1.5925 | -0.079953 | -0.027139 | 119.8104 | 119.9267 | -1.65 | -1.8583 | -1.8984 | -1.8473 | -1.8819 | -1.9289 | -1.9764 | 1.8381 | 1.9336 | 1.7996 | 1.6245 | -0.04791 | 0.004904 | 119.8424 | 119.9587 | 1.886 | -118.0043 | 1.8475 | -118.0428
1332.2812 | 122.2504 | -120.2087 | 1.8997 | -1.7507 | -1.9453 | -1.9762 | -1.9205 | -1.9643 | -2.0205 | -2.0908 | 1.8244 | 1.9199 | 1.7813 | 1.6062 | -0.084531 | -0.027139 | 119.7829 | 119.8992 | -1.7187 | -1.9133 | -1.9442 | -1.8885 | -1.9323 | -1.9884 | -2.0588 | 1.8564 | 1.9519 | 1.8134 | 1.6382 | -0.052488 | 0.004904 | 119.815 | 119.9312 | 1.9089 | -117.9586 | 1.8658 | -118.0016
1334.0312 | 122.3328 | -120.0577 | 2.0279 | -1.7141 | -1.8949 | -1.9121 | -1.8793 | -1.9139 | -1.9747 | -2.0268 | 1.8381 | 1.9336 | 1.795 | 1.6337 | -0.079953 | -0.027139 | 119.7692 | 119.89 | -1.682 | -1.8629 | -1.8801 | -1.8473 | -1.8819 | -1.9426 | -1.9947 | 1.8701 | 1.9657 | 1.8271 | 1.6657 | -0.04791 | 0.004904 | 119.8012 | 119.9221 | 1.9181 | -117.9311 | 1.875 | -117.9741
1335.7188 | 122.2778 | -120.1401 | 1.9455 | -1.6271 | -1.7896 | -1.8114 | -1.7648 | -1.8041 | -1.8648 | -1.9169 | 1.8106 | 1.9107 | 1.7676 | 1.597 | -0.079953 | -0.022561 | 119.8012 | 119.9267 | -1.595 | -1.7576 | -1.7793 | -1.7328 | -1.772 | -1.8328 | -1.8848 | 1.8427 | 1.9428 | 1.7996 | 1.6291 | -0.04791 | 0.009482 | 119.8333 | 119.9587 | 1.8906 | -117.9906 | 1.8475 | -118.0337
1337.4062 | 122.3282 | -120.163 | 1.8906 | -1.65 | -1.7851 | -1.7977 | -1.7557 | -1.7903 | -1.8557 | -1.9215 | 1.8335 | 1.9336 | 1.7813 | 1.6108 | -0.079953 | -0.022561 | 119.7829 | 119.8946 | -1.6179 | -1.753 | -1.7656 | -1.7236 | -1.7583 | -1.8236 | -1.8894 | 1.8656 | 1.9657 | 1.8134 | 1.6428 | -0.04791 | 0.009482 | 119.815 | 119.9266 | 1.9135 | -117.9494 | 1.8613 | -118.0016
1339.1562 | 122.2275 | -120.1584 | 1.9867 | -1.6683 | -1.7713 | -1.7839 | -1.7328 | -1.7858 | -1.8557 | -1.9123 | 1.8839 | 1.9794 | 1.8362 | 1.6703 | -0.079953 | -0.027139 | 119.7326 | 119.8488 | -1.6363 | -1.7393 | -1.7519 | -1.7008 | -1.7537 | -1.8236 | -1.8803 | 1.9159 | 2.0115 | 1.8683 | 1.7023 | -0.04791 | 0.004904 | 119.7646 | 119.8809 | 1.9638 | -117.8487 | 1.9162 | -117.8963
1340.9062 | 122.168 | -120.1447 | 2.0142 | -1.5126 | -1.5836 | -1.5962 | -1.5588 | -1.5889 | -1.6588 | -1.7154 | 1.9571 | 2.0481 | 1.9141 | 1.7481 | -0.079953 | -0.027139 | 119.6547 | 119.7756 | -1.4806 | -1.5515 | -1.5642 | -1.5268 | -1.5569 | -1.6267 | -1.6834 | 1.9892 | 2.0802 | 1.9461 | 1.7802 | -0.04791 | 0.004904 | 119.6868 | 119.8076 | 2.0371 | -117.6976 | 1.994 | -117.7407
1342.6719 | 122.2916 | -120.1309 | 1.9547 | -1.563 | -1.6294 | -1.6328 | -1.5863 | -1.6164 | -1.6863 | -1.7704 | 1.893 | 1.9932 | 1.85 | 1.6795 | -0.08911 | -0.022561 | 119.7234 | 119.8397 | -1.531 | -1.5973 | -1.6008 | -1.5542 | -1.5843 | -1.6542 | -1.7383 | 1.9251 | 2.0252 | 1.882 | 1.7115 | -0.057067 | 0.009482 | 119.7554 | 119.8717 | 1.9822 | -117.8304 | 1.9391 | -117.8734
1344.4219 | 122.3328 | -120.2042 | 1.8723 | -1.5722 | -1.6065 | -1.5962 | -1.5497 | -1.5843 | -1.6588 | -1.7292 | 1.8289 | 1.9199 | 1.7813 | 1.6108 | -0.079953 | -0.027139 | 119.7921 | 119.9129 | -1.5401 | -1.5744 | -1.5642 | -1.5176 | -1.5523 | -1.6267 | -1.6971 | 1.861 | 1.9519 | 1.8134 | 1.6428 | -0.04791 | 0.004904 | 119.8241 | 119.945 | 1.9089 | -117.9631 | 1.8613 | -118.0108
1346.1094 | 122.3145 | -119.9158 | 2.1561 | -1.5035 | -1.5057 | -1.5138 | -1.4581 | -1.4974 | -1.5581 | -1.633 | 2.0808 | 2.1717 | 2.0377 | 1.8764 | -0.075375 | -0.031717 | 119.5265 | 119.6474 | -1.4714 | -1.4737 | -1.4817 | -1.426 | -1.4653 | -1.526 | -1.601 | 2.1128 | 2.2038 | 2.0697 | 1.9084 | -0.043332 | 0.000326 | 119.5586 | 119.6794 | 2.1561 | -117.4458 | 2.1131 | -117.4888
1347.8125 | 122.2733 | -118.7988 | 3.3279 | -1.1372 | -1.1852 | -1.1841 | -1.1147 | -1.0945 | -1.1506 | -1.2759 | 3.4406 | 3.5408 | 3.402 | 3.2363 | -0.079953 | -0.027139 | 118.1668 | 118.2877 | -1.1052 | -1.1532 | -1.1521 | -1.0827 | -1.0624 | -1.1185 | -1.2439 | 3.4726 | 3.5728 | 3.4341 | 3.2684 | -0.04791 | 0.004904 | 118.1988 | 118.3197 | 3.5205 | -114.7262 | 3.482 | -114.7647
1349.5625 | 122.3282 | -119.0414 | 3.0121 | -1.2608 | -1.2722 | -1.2665 | -1.1971 | -1.2089 | -1.2696 | -1.3767 | 2.9369 | 3.0326 | 2.8893 | 2.7189 | -0.079953 | -0.022561 | 118.675 | 118.7867 | -1.2288 | -1.2402 | -1.2345 | -1.1651 | -1.1769 | -1.2376 | -1.3446 | 2.969 | 3.0646 | 2.9213 | 2.7509 | -0.04791 | 0.009482 | 118.707 | 118.8187 | 3.0169 | -115.738 | 2.9692 | -115.7857
1351.25 | 122.2183 | -118.6615 | 3.4836 | -1.2288 | -1.2219 | -1.2162 | -1.1513 | -1.1494 | -1.2009 | -1.3263 | 3.4039 | 3.5042 | 3.37 | 3.1997 | -0.079953 | -0.022561 | 118.2034 | 118.3243 | -1.1967 | -1.1898 | -1.1841 | -1.1193 | -1.1174 | -1.1689 | -1.2942 | 3.436 | 3.5362 | 3.402 | 3.2317 | -0.04791 | 0.009482 | 118.2354 | 118.3563 | 3.4839 | -114.7994 | 3.4499 | -114.8334
1353 | 122.319 | -118.8171 | 3.2867 | -1.0868 | -1.0936 | -1.088 | -1.0231 | -1.0075 | -1.0499 | -1.1844 | 3.2254 | 3.321 | 3.1868 | 3.0165 | -0.084531 | -0.022561 | 118.3819 | 118.5028 | -1.0548 | -1.0616 | -1.0559 | -0.99109 | -0.97547 | -1.0178 | -1.1523 | 3.2574 | 3.3531 | 3.2189 | 3.0486 | -0.052488 | 0.009482 | 118.414 | 118.5349 | 3.3099 | -115.1566 | 3.2714 | -115.1951
1354.75 | 122.3236 | -118.5013 | 3.5706 | -1.2517 | -1.1944 | -1.1933 | -1.1284 | -1.1265 | -1.1781 | -1.2942 | 3.5459 | 3.637 | 3.5027 | 3.3279 | -0.070797 | -0.031717 | 118.0615 | 118.1732 | -1.2196 | -1.1623 | -1.1612 | -1.0964 | -1.0945 | -1.146 | -1.2622 | 3.5779 | 3.669 | 3.5348 | 3.36 | -0.038754 | 0.000326 | 118.0935 | 118.2053 | 3.6167 | -114.5156 | 3.5735 | -114.5587
1356.4375 | 122.2 | -118.4738 | 3.653 | -1.3432 | -1.2493 | -1.2391 | -1.1925 | -1.1952 | -1.2559 | -1.3492 | 3.5413 | 3.637 | 3.4936 | 3.3233 | -0.070797 | -0.022561 | 118.0615 | 118.1824 | -1.3112 | -1.2173 | -1.207 | -1.1605 | -1.1632 | -1.2238 | -1.3171 | 3.5733 | 3.669 | 3.5256 | 3.3554 | -0.038754 | 0.009482 | 118.0935 | 118.2144 | 3.6121 | -114.5202 | 3.5644 | -114.5679
1358.1875 | 122.1863 | -118.0618 | 4.0833 | -1.1921 | -1.0662 | -1.088 | -1.0552 | -1.0624 | -1.0911 | -1.1752 | 4.022 | 4.1177 | 3.9835 | 3.8087 | -0.070797 | -0.027139 | 117.5716 | 117.6925 | -1.1601 | -1.0341 | -1.0559 | -1.0231 | -1.0304 | -1.059 | -1.1432 | 4.0541 | 4.1498 | 4.0155 | 3.8407 | -0.038754 | 0.004904 | 117.6036 | 117.7245 | 4.0928 | -113.5495 | 4.0543 | -113.5881
1359.9375 | 122.2092 | -118.0344 | 4.0833 | -1.2425 | -1.1349 | -1.1246 | -1.0781 | -1.0899 | -1.1414 | -1.2439 | 4.0037 | 4.104 | 3.9606 | 3.7995 | -0.075375 | -0.017983 | 117.6036 | 117.9306 | -1.2105 | -1.1028 | -1.0926 | -1.046 | -1.0579 | -1.1094 | -1.2118 | 4.0358 | 4.136 | 3.9926 | 3.8316 | -0.043332 | 0.01406 | 117.6357 | 117.9626 | 4.0791 | -113.5999 | 4.0359 | -113.643
1361.7031 | 122.2137 | -117.4255 | 4.7287 | -1.3295 | -1.1623 | -1.1612 | -1.1193 | -1.1357 | -1.1918 | -1.2805 | 4.6401 | 4.7267 | 4.597 | 4.4223 | -0.075375 | -0.013405 | 116.9672 | 117.3034 | -1.2975 | -1.1303 | -1.1292 | -1.0872 | -1.1037 | -1.1597 | -1.2485 | 4.6722 | 4.7588 | 4.629 | 4.4543 | -0.043332 | 0.018638 | 116.9993 | 117.3354 | 4.7155 | -112.3271 | 4.6723 | -112.3703
1363.4062 | 122.2321 | -116.5283 | 5.6122 | -1.3753 | -1.1669 | -1.1795 | -1.1376 | -1.1632 | -1.2193 | -1.2942 | 5.4643 | 5.5646 | 5.4256 | 5.2511 | -0.079953 | -0.022561 | 116.1431 | 116.4656 | -1.3432 | -1.1349 | -1.1475 | -1.1055 | -1.1311 | -1.1872 | -1.2622 | 5.4963 | 5.5967 | 5.4577 | 5.2831 | -0.04791 | 0.009482 | 116.1752 | 116.4976 | 5.5442 | -110.6788 | 5.5056 | -110.7175
1365.1562 | 122.2137 | -113.681 | 8.4824 | -1.2379 | -1.0295 | -1.0468 | -1.0094 | -1.0212 | -1.059 | -1.1477 | 8.4769 | 8.5134 | 8.4381 | 8.2641 | -0.070797 | -0.008827 | 113.1168 | 113.2425 | -1.2059 | -0.9975 | -1.0147 | -0.97735 | -0.9892 | -1.027 | -1.1157 | 8.509 | 8.5454 | 8.4702 | 8.2961 | -0.038754 | 0.023216 | 113.1488 | 113.2746 | 8.5477 | -104.6399 | 8.5089 | -104.6787
1366.9062 | 122.319 | -114.4226 | 7.6263 | -1.389 | -1.1257 | -1.1383 | -1.1055 | -1.1311 | -1.1689 | -1.2393 | 7.5933 | 7.6388 | 7.5545 | 7.3804 | -0.066219 | -0.013405 | 113.9958 | 114.1215 | -1.357 | -1.0937 | -1.1063 | -1.0735 | -1.0991 | -1.1369 | -1.2073 | 7.6253 | 7.6709 | 7.5866 | 7.4124 | -0.034176 | 0.018638 | 114.0279 | 114.1536 | 7.6595 | -106.4026 | 7.6207 | -106.4413
1368.5938 | 122.2504 | -114.9261 | 7.196 | -1.3844 | -1.0936 | -1.12 | -1.0918 | -1.1128 | -1.1506 | -1.2073 | 7.1217 | 7.1443 | 7.0784 | 6.895 | -0.066219 | -0.008827 | 114.472 | 114.5977 | -1.3524 | -1.0616 | -1.088 | -1.0598 | -1.0808 | -1.1185 | -1.1752 | 7.1537 | 7.1764 | 7.1104 | 6.927 | -0.034176 | 0.023216 | 114.504 | 114.6297 | 7.1879 | -107.3503 | 7.1446 | -107.3936
1370.2812 | 122.2 | -113.6078 | 8.5098 | -1.3203 | -1.0204 | -1.0513 | -1.014 | -1.035 | -1.059 | -1.1111 | 8.2388 | 8.2753 | 8.2001 | 8.0306 | -0.057062 | -0.013405 | 113.3549 | 113.4852 | -1.2883 | -0.98835 | -1.0193 | -0.98193 | -1.0029 | -1.027 | -1.0791 | 8.2709 | 8.3073 | 8.2321 | 8.0626 | -0.025019 | 0.018638 | 113.3869 | 113.5172 | 8.2959 | -105.116 | 8.2571 | -105.1548
1372.0156 | 122.2366 | -113.7817 | 8.3313 | -1.2013 | -0.90592 | -0.95519 | -0.92698 | -0.92511 | -0.93998 | -0.98293 | 8.2388 | 8.2753 | 8.2046 | 8.0214 | -0.061641 | -0.004248 | 113.3594 | 113.476 | -1.1693 | -0.87387 | -0.92315 | -0.89494 | -0.89306 | -0.90793 | -0.95089 | 8.2709 | 8.3073 | 8.2367 | 8.0535 | -0.029598 | 0.027795 | 113.3915 | 113.5081 | 8.3005 | -105.1206 | 8.2663 | -105.1548
1373.7656 | 122.2504 | -113.1821 | 8.9172 | -1.1693 | -0.86013 | -0.92314 | -0.89951 | -0.88848 | -0.89877 | -0.90968 | 8.6921 | 8.7286 | 8.6625 | 8.4793 | -0.057062 | 0.00033 | 112.9016 | 113.0319 | -1.1372 | -0.82809 | -0.8911 | -0.86747 | -0.85644 | -0.86673 | -0.87764 | 8.7242 | 8.7606 | 8.6945 | 8.5114 | -0.025019 | 0.032373 | 112.9337 | 113.064 | 8.7492 | -104.2095 | 8.7195 | -104.2391
1375.4375 | 122.3053 | -112.9211 | 9.1644 | -1.0731 | -0.7365 | -0.81783 | -0.7942 | -0.77861 | -0.75684 | -0.76776 | 9.0767 | 9.1178 | 9.0379 | 8.8594 | -0.057062 | 0.004908 | 112.5216 | 112.6382 | -1.0411 | -0.70446 | -0.78579 | -0.76216 | -0.74657 | -0.7248 | -0.73571 | 9.1087 | 9.1498 | 9.0699 | 8.8914 | -0.025019 | 0.036951 | 112.5536 | 112.6702 | 9.1338 | -103.4449 | 9.0949 | -103.4837
1377.1875 | 122.2229 | -112.1567 | 9.9609 | -1.0044 | -0.65408 | -0.75831 | -0.74384 | -0.7191 | -0.67901 | -0.67161 | 9.8779 | 9.9511 | 9.8391 | 9.6653 | -0.057062 | -0.004248 | 111.7204 | 111.8462 | -0.97239 | -0.62204 | -0.72627 | -0.7118 | -0.68705 | -0.64696 | -0.63957 | 9.91 | 9.9832 | 9.8711 | 9.6973 | -0.025019 | 0.027795 | 111.7524 | 111.8782 | 9.935 | -101.8424 | 9.8961 | -101.8813
1378.875 | 122.2092 | -111.2412 | 10.881 | -1.0411 | -0.67698 | -0.78578 | -0.76673 | -0.74657 | -0.71106 | -0.68993 | 10.7982 | 10.8761 | 10.7547 | 10.5811 | -0.057062 | 0.00033 | 110.7956 | 110.9305 | -1.009 | -0.64493 | -0.75374 | -0.73469 | -0.71452 | -0.67901 | -0.65788 | 10.8303 | 10.9081 | 10.7868 | 10.6131 | -0.025019 | 0.032373 | 110.8276 | 110.9626 | 10.8553 | -99.9973 | 10.8118 | -100.0408
1380.625 | 122.319 | -111.026 | 10.9817 | -0.96781 | -0.62203 | -0.73542 | -0.72095 | -0.69163 | -0.64696 | -0.61668 | 10.9539 | 11.0272 | 10.9058 | 10.7185 | -0.057062 | 0.00033 | 110.6445 | 110.7703 | -0.93576 | -0.58999 | -0.70338 | -0.6889 | -0.65959 | -0.61492 | -0.58463 | 10.9859 | 11.0592 | 10.9379 | 10.7505 | -0.025019 | 0.032373 | 110.6765 | 110.8024 | 11.0109 | -99.6906 | 10.9629 | -99.7386
1382.3125 | 122.2046 | -111.676 | 10.4553 | -0.99528 | -0.59914 | -0.73084 | -0.71637 | -0.68705 | -0.62865 | -0.58463 | 10.377 | 10.4502 | 10.329 | 10.1507 | -0.057062 | -0.004248 | 111.2305 | 111.3563 | -0.96323 | -0.56709 | -0.6988 | -0.68433 | -0.65501 | -0.5966 | -0.55259 | 10.409 | 10.4823 | 10.361 | 10.1827 | -0.025019 | 0.027795 | 111.2625 | 111.3884 | 10.4341 | -100.8535 | 10.386 | -100.9015
1384.0625 | 122.2 | -111.5753 | 10.5606 | -0.98612 | -0.59456 | -0.73542 | -0.71637 | -0.68248 | -0.62865 | -0.5709 | 10.4823 | 10.5693 | 10.4434 | 10.2697 | -0.057062 | 0.00033 | 111.1069 | 111.2373 | -0.95408 | -0.56251 | -0.70338 | -0.68433 | -0.65043 | -0.5966 | -0.53885 | 10.5143 | 10.6013 | 10.4755 | 10.3018 | -0.025019 | 0.032373 | 111.1389 | 111.2693 | 10.5394 | -100.6246 | 10.5005 | -100.6635
1385.75 | 122.3099 | -111.5524 | 10.4919 | -0.98154 | -0.59456 | -0.74 | -0.71637 | -0.69163 | -0.62407 | -0.56632 | 10.4686 | 10.5601 | 10.4297 | 10.2468 | -0.057062 | 0.00033 | 111.116 | 111.2464 | -0.9495 | -0.56251 | -0.70795 | -0.68433 | -0.65959 | -0.59202 | -0.53427 | 10.5006 | 10.5922 | 10.4617 | 10.2789 | -0.025019 | 0.032373 | 111.1481 | 111.2785 | 10.5256 | -100.6475 | 10.4867 | -100.6864
1387.5 | 122.2137 | -111.9507 | 10.144 | -0.9907 | -0.5854 | -0.73542 | -0.71179 | -0.68248 | -0.61491 | -0.548 | 10.0336 | 10.1343 | 10.0039 | 9.8164 | -0.057062 | 0.004908 | 111.5556 | 111.6722 | -0.95865 | -0.55336 | -0.70338 | -0.67975 | -0.65043 | -0.58287 | -0.51596 | 10.0656 | 10.1663 | 10.0359 | 9.8484 | -0.025019 | 0.036951 | 111.5876 | 111.7043 | 10.0907 | -101.522 | 10.061 | -101.5517
1389.1875 | 122.3053 | -111.5982 | 10.4645 | -0.94949 | -0.56251 | -0.72168 | -0.70721 | -0.66874 | -0.58744 | -0.52511 | 10.3862 | 10.4686 | 10.3473 | 10.169 | -0.057062 | 0.00033 | 111.2168 | 111.338 | -0.91745 | -0.53046 | -0.68964 | -0.67517 | -0.6367 | -0.5554 | -0.49307 | 10.4182 | 10.5006 | 10.3793 | 10.201 | -0.025019 | 0.032373 | 111.2488 | 111.37 | 10.4432 | -100.8306 | 10.4043 | -100.8695
1390.9375 | 122.2412 | -111.1221 | 10.9863 | -0.97238 | -0.57624 | -0.74916 | -0.72095 | -0.68705 | -0.61033 | -0.54343 | 10.9447 | 11.0317 | 10.9104 | 10.7276 | -0.061641 | 0.00033 | 110.6445 | 110.7795 | -0.94034 | -0.5442 | -0.71711 | -0.6889 | -0.65501 | -0.57829 | -0.51138 | 10.9768 | 11.0638 | 10.9424 | 10.7597 | -0.029598 | 0.032373 | 110.6765 | 110.8115 | 11.0064 | -99.6997 | 10.972 | -99.7341
1392.625 | 122.3373 | -111.5387 | 10.524 | -0.96781 | -0.58082 | -0.75831 | -0.72095 | -0.69621 | -0.61491 | -0.54343 | 10.4686 | 10.5464 | 10.4251 | 10.2422 | -0.052484 | 0.004908 | 111.1344 | 111.2602 | -0.93576 | -0.54878 | -0.72627 | -0.6889 | -0.66417 | -0.58287 | -0.51138 | 10.5006 | 10.5784 | 10.4571 | 10.2743 | -0.020441 | 0.036951 | 111.1664 | 111.2922 | 10.521 | -100.6658 | 10.4776 | -100.7092
1394.3125 | 122.2916 | -111.8317 | 10.2127 | -1.0319 | -0.59456 | -0.78578 | -0.76673 | -0.73283 | -0.64238 | -0.55716 | 10.1847 | 10.2671 | 10.1367 | 9.9675 | -0.052484 | 0.00033 | 111.4136 | 111.5349 | -0.99986 | -0.56251 | -0.75374 | -0.73469 | -0.70079 | -0.61034 | -0.52512 | 10.2167 | 10.2991 | 10.1687 | 9.9995 | -0.020441 | 0.032373 | 111.4457 | 111.5669 | 10.2372 | -101.2289 | 10.1892 | -101.277
1396.0469 | 122.3465 | -112.2849 | 9.7641 | -1.0731 | -0.63119 | -0.82699 | -0.80336 | -0.7603 | -0.68359 | -0.58005 | 9.7223 | 9.8046 | 9.6834 | 9.505 | -0.052484 | 0.004908 | 111.8852 | 111.9973 | -1.0411 | -0.59914 | -0.79495 | -0.77132 | -0.72826 | -0.65154 | -0.54801 | 9.7543 | 9.8367 | 9.7155 | 9.5371 | -0.020441 | 0.036951 | 111.9172 | 112.0293 | 9.7748 | -102.1629 | 9.7359 | -102.2018
1397.7969 | 122.3602 | -112.4817 | 9.5673 | -1.0823 | -0.62203 | -0.83615 | -0.80794 | -0.76946 | -0.67443 | -0.57547 | 9.5162 | 9.5986 | 9.4728 | 9.2898 | -0.052484 | 0.004908 | 112.0912 | 112.2079 | -1.0502 | -0.58999 | -0.8041 | -0.7759 | -0.73741 | -0.64239 | -0.54343 | 9.5483 | 9.6306 | 9.5049 | 9.3219 | -0.020441 | 0.036951 | 112.1233 | 112.2399 | 9.5687 | -102.575 | 9.5253 | -102.6184
1399.5469 | 122.2916 | -113.0768 | 9.0088 | -0.95865 | -0.55793 | -0.78121 | -0.753 | -0.72368 | -0.60575 | -0.51138 | 8.8752 | 8.9621 | 8.8456 | 8.6625 | -0.043328 | 0.004908 | 112.7231 | 112.8534 | -0.9266 | -0.52588 | -0.74916 | -0.72095 | -0.69163 | -0.57371 | -0.47934 | 8.9073 | 8.9942 | 8.8776 | 8.6945 | -0.011285 | 0.036951 | 112.7551 | 112.8854 | 8.9186 | -103.8478 | 8.8889 | -103.8775
1401.2188 | 122.3419 | -113.8641 | 8.1482 | -1.0594 | -0.60372 | -0.82699 | -0.80794 | -0.78319 | -0.66069 | -0.53885 | 8.1335 | 8.2158 | 8.0902 | 7.9115 | -0.052484 | 0.00033 | 113.4739 | 113.5996 | -1.0273 | -0.57167 | -0.79495 | -0.7759 | -0.75115 | -0.62865 | -0.5068 | 8.1656 | 8.2478 | 8.1222 | 7.9436 | -0.020441 | 0.032373 | 113.5059 | 113.6317 | 8.186 | -105.3404 | 8.1427 | -105.3837
1402.9688 | 122.3328 | -114.0015 | 8.0383 | -1.0227 | -0.56708 | -0.8041 | -0.78047 | -0.74657 | -0.63322 | -0.5068 | 7.9595 | 8.0418 | 7.9116 | 7.7284 | -0.043328 | 0.018642 | 113.657 | 113.7782 | -0.9907 | -0.53504 | -0.77205 | -0.74843 | -0.71452 | -0.60118 | -0.47476 | 7.9916 | 8.0738 | 7.9437 | 7.7604 | -0.011285 | 0.050685 | 113.6891 | 113.8102 | 8.0029 | -105.6975 | 7.955 | -105.7454
1404.6562 | 122.2183 | -113.974 | 8.1802 | -1.0411 | -0.57166 | -0.8041 | -0.7942 | -0.7603 | -0.6378 | -0.49764 | 8.0008 | 8.0921 | 7.962 | 7.7833 | -0.052484 | 0.014064 | 113.5929 | 113.7232 | -1.009 | -0.53962 | -0.77205 | -0.76216 | -0.72826 | -0.60576 | -0.4656 | 8.0328 | 8.1242 | 7.994 | 7.8153 | -0.020441 | 0.046107 | 113.625 | 113.7553 | 8.0532 | -105.5922 | 8.0145 | -105.631
1406.3906 | 122.2916 | -114.4455 | 7.6401 | -0.90371 | -0.50298 | -0.73542 | -0.72553 | -0.69163 | -0.56913 | -0.42897 | 7.488 | 7.5793 | 7.4492 | 7.2613 | -0.043328 | 0.009486 | 114.1195 | 114.2406 | -0.87166 | -0.47094 | -0.70338 | -0.69348 | -0.65959 | -0.53708 | -0.39693 | 7.52 | 7.6114 | 7.4813 | 7.2933 | -0.011285 | 0.041529 | 114.1515 | 114.2726 | 7.5313 | -106.6315 | 7.4925 | -106.6702
1408.0938 | 122.3648 | -114.9857 | 7.077 | -0.93576 | -0.50756 | -0.74458 | -0.73926 | -0.70537 | -0.57828 | -0.43355 | 7.0759 | 7.1626 | 7.028 | 6.8538 | -0.057062 | 0.009486 | 114.5407 | 114.6618 | -0.90371 | -0.47552 | -0.71253 | -0.70722 | -0.67332 | -0.54624 | -0.40151 | 7.1079 | 7.1947 | 7.0601 | 6.8858 | -0.025019 | 0.041529 | 114.5727 | 114.6938 | 7.133 | -107.4648 | 7.0851 | -107.5127
1409.8438 | 122.2321 | -114.8529 | 7.3013 | -1.0136 | -0.55793 | -0.78121 | -0.77589 | -0.74657 | -0.62865 | -0.47475 | 7.259 | 7.3458 | 7.2157 | 7.0461 | -0.034171 | 0.014064 | 114.3575 | 114.4741 | -0.98155 | -0.52588 | -0.74916 | -0.74385 | -0.71452 | -0.5966 | -0.44271 | 7.2911 | 7.3778 | 7.2478 | 7.0781 | -0.002128 | 0.046107 | 114.3896 | 114.5061 | 7.2932 | -107.0985 | 7.2499 | -107.1418
1411.5469 | 122.2458 | -115.2603 | 6.8756 | -0.95407 | -0.52587 | -0.77205 | -0.76673 | -0.74657 | -0.60118 | -0.45186 | 6.76 | 6.865 | 6.7304 | 6.5515 | -0.03875 | 0.018642 | 114.8428 | 114.9685 | -0.92203 | -0.49383 | -0.74 | -0.73469 | -0.71452 | -0.56913 | -0.41982 | 6.792 | 6.8971 | 6.7625 | 6.5836 | -0.006707 | 0.050685 | 114.8749 | 115.0005 | 6.7987 | -108.0829 | 6.7692 | -108.1124
1413.2344 | 122.2183 | -115.2649 | 6.8756 | -0.99528 | -0.54419 | -0.80868 | -0.81252 | -0.78777 | -0.6378 | -0.47475 | 6.792 | 6.8742 | 6.7487 | 6.579 | -0.047906 | 0.014064 | 114.8245 | 114.941 | -0.96323 | -0.51215 | -0.77663 | -0.78047 | -0.75572 | -0.60576 | -0.44271 | 6.8241 | 6.9062 | 6.7808 | 6.6111 | -0.015863 | 0.046107 | 114.8566 | 114.9731 | 6.8399 | -108.0325 | 6.7967 | -108.0758
1414.9688 | 122.2275 | -115.3198 | 6.8207 | -1.0136 | -0.58082 | -0.82241 | -0.83083 | -0.80608 | -0.66069 | -0.49764 | 6.6959 | 6.7963 | 6.6618 | 6.4874 | -0.03875 | 0.02322 | 114.9161 | 115.028 | -0.98155 | -0.54878 | -0.79037 | -0.79879 | -0.77404 | -0.62865 | -0.4656 | 6.7279 | 6.8284 | 6.6938 | 6.5195 | -0.006707 | 0.055263 | 114.9481 | 115.0601 | 6.7346 | -108.2202 | 6.7005 | -108.2543
1416.7188 | 122.2961 | -115.567 | 6.514 | -0.7572 | -0.54877 | -0.79952 | -0.80794 | -0.79235 | -0.64238 | -0.47933 | 6.4441 | 6.5399 | 6.4145 | 6.2356 | -0.03875 | 0.018642 | 115.1633 | 115.289 | -0.72516 | -0.51673 | -0.76748 | -0.7759 | -0.7603 | -0.61034 | -0.44729 | 6.4761 | 6.572 | 6.4466 | 6.2676 | -0.006707 | 0.050685 | 115.1954 | 115.321 | 6.4828 | -108.7193 | 6.4533 | -108.7488
1418.4062 | 122.319 | -115.6769 | 6.3629 | -0.72515 | -0.51672 | -0.76747 | -0.78505 | -0.76946 | -0.61033 | -0.45186 | 6.3296 | 6.4071 | 6.2818 | 6.1028 | -0.034171 | 0.027798 | 115.2869 | 115.4126 | -0.69311 | -0.48468 | -0.73543 | -0.753 | -0.73741 | -0.57829 | -0.41982 | 6.3616 | 6.4392 | 6.3138 | 6.1348 | -0.002128 | 0.059841 | 115.319 | 115.4446 | 6.3638 | -108.9573 | 6.3159 | -109.0052
1420.1562 | 122.3145 | -115.5716 | 6.4957 | -0.71599 | -0.50298 | -0.75831 | -0.76673 | -0.7603 | -0.60118 | -0.43813 | 6.4761 | 6.5582 | 6.4328 | 6.2493 | -0.03875 | 0.018642 | 115.1404 | 115.2661 | -0.68395 | -0.47094 | -0.72627 | -0.73469 | -0.72826 | -0.56913 | -0.40609 | 6.5082 | 6.5903 | 6.4649 | 6.2814 | -0.006707 | 0.050685 | 115.1725 | 115.2981 | 6.5149 | -108.6643 | 6.4716 | -108.7076
1421.8594 | 122.3282 | -115.4022 | 6.6833 | -0.73889 | -0.51672 | -0.77205 | -0.80336 | -0.77403 | -0.61491 | -0.45186 | 6.6135 | 6.7002 | 6.5702 | 6.3959 | -0.029593 | 0.027798 | 114.9894 | 115.115 | -0.70684 | -0.48468 | -0.74 | -0.77132 | -0.74199 | -0.58287 | -0.41982 | 6.6455 | 6.7322 | 6.6022 | 6.4279 | 0.00245 | 0.059841 | 115.0214 | 115.147 | 6.6431 | -108.3759 | 6.5998 | -108.4192
1423.6094 | 122.2137 | -115.3564 | 6.8069 | -0.73431 | -0.50756 | -0.75831 | -0.78505 | -0.76946 | -0.59202 | -0.44728 | 6.6776 | 6.7643 | 6.6389 | 6.46 | -0.034171 | 0.02322 | 114.939 | 115.0601 | -0.70226 | -0.47552 | -0.72627 | -0.753 | -0.73741 | -0.55998 | -0.41524 | 6.7096 | 6.7963 | 6.6709 | 6.492 | -0.002128 | 0.055263 | 114.971 | 115.0921 | 6.7117 | -108.2614 | 6.673 | -108.3001
1425.2969 | 122.374 | -115.2878 | 6.7657 | -0.69768 | -0.46635 | -0.7171 | -0.753 | -0.73741 | -0.56913 | -0.42439 | 6.7188 | 6.8055 | 6.6755 | 6.4966 | -0.03875 | 0.027798 | 114.9024 | 115.0234 | -0.66564 | -0.43431 | -0.68506 | -0.72095 | -0.70537 | -0.53708 | -0.39235 | 6.7508 | 6.8375 | 6.7075 | 6.5286 | -0.006707 | 0.059841 | 114.9344 | 115.0555 | 6.7575 | -108.1836 | 6.7142 | -108.2269
1427.0625 | 122.2641 | -115.4526 | 6.665 | -0.66105 | -0.42056 | -0.6759 | -0.71637 | -0.69621 | -0.53708 | -0.39235 | 6.5723 | 6.659 | 6.5336 | 6.3546 | -0.029593 | 0.02322 | 115.0489 | 115.1608 | -0.62901 | -0.38852 | -0.64385 | -0.68433 | -0.66417 | -0.50504 | -0.3603 | 6.6043 | 6.691 | 6.5656 | 6.3867 | 0.00245 | 0.055263 | 115.0809 | 115.1928 | 6.6019 | -108.4766 | 6.5632 | -108.5153
1428.75 | 122.3602 | -115.9195 | 6.134 | -0.59696 | -0.38393 | -0.63469 | -0.67058 | -0.64127 | -0.49129 | -0.3603 | 6.1282 | 6.2103 | 6.0757 | 5.9013 | -0.025015 | 0.02322 | 115.4976 | 115.6232 | -0.56491 | -0.35189 | -0.60265 | -0.63854 | -0.60923 | -0.45925 | -0.32826 | 6.1602 | 6.2423 | 6.1078 | 5.9334 | 0.007028 | 0.055263 | 115.5296 | 115.6552 | 6.1532 | -109.3694 | 6.1008 | -109.4218
1430.4375 | 122.3511 | -116.1667 | 5.8594 | -0.47334 | -0.33357 | -0.53396 | -0.56986 | -0.52225 | -0.38599 | -0.3191 | 5.8305 | 5.9218 | 5.7873 | 5.6037 | -0.025015 | 0.027798 | 115.7906 | 115.907 | -0.4413 | -0.30152 | -0.50192 | -0.53781 | -0.4902 | -0.35395 | -0.28705 | 5.8626 | 5.9538 | 5.8193 | 5.6357 | 0.007028 | 0.059841 | 115.8226 | 115.9391 | 5.8556 | -109.96 | 5.8123 | -110.0033
1432.1875 | 122.3419 | -116.2125 | 5.8411 | -0.4825 | -0.34272 | -0.56143 | -0.56986 | -0.52225 | -0.38599 | -0.3191 | 5.7802 | 5.876 | 5.7461 | 5.5625 | -0.020437 | 0.02322 | 115.8364 | 115.962 | -0.45045 | -0.31068 | -0.52939 | -0.53781 | -0.4902 | -0.35395 | -0.28705 | 5.8122 | 5.908 | 5.7781 | 5.5945 | 0.011606 | 0.055263 | 115.8684 | 115.994 | 5.8006 | -110.0562 | 5.7665 | -110.0903
1433.9375 | 122.1954 | -116.153 | 5.9967 | -0.43671 | -0.32899 | -0.53396 | -0.54239 | -0.48105 | -0.34479 | -0.2962 | 5.8534 | 5.9493 | 5.8102 | 5.6312 | -0.025015 | 0.027798 | 115.7631 | 115.8795 | -0.40467 | -0.29694 | -0.50192 | -0.51034 | -0.449 | -0.31274 | -0.26416 | 5.8855 | 5.9813 | 5.8422 | 5.6632 | 0.007028 | 0.059841 | 115.7951 | 115.9116 | 5.8785 | -109.9097 | 5.8352 | -109.9529
1435.6875 | 122.3465 | -116.4871 | 5.5847 | -0.43213 | -0.32899 | -0.53854 | -0.53781 | -0.48105 | -0.33105 | -0.30078 | 5.5375 | 5.6287 | 5.4851 | 5.3152 | -0.020437 | 0.032376 | 116.0836 | 116.2092 | -0.40009 | -0.29694 | -0.5065 | -0.50576 | -0.449 | -0.29901 | -0.26874 | 5.5696 | 5.6608 | 5.5172 | 5.3473 | 0.011606 | 0.064419 | 116.1156 | 116.2412 | 5.558 | -110.5461 | 5.5056 | -110.5984
1437.375 | 122.2687 | -116.5558 | 5.5618 | -0.44129 | -0.32899 | -0.5477 | -0.55154 | -0.48562 | -0.32647 | -0.30078 | 5.4185 | 5.5097 | 5.3844 | 5.2007 | -0.020437 | 0.032376 | 116.1889 | 116.3099 | -0.40925 | -0.29694 | -0.51565 | -0.5195 | -0.45358 | -0.29443 | -0.26874 | 5.4505 | 5.5417 | 5.4165 | 5.2328 | 0.011606 | 0.064419 | 116.2209 | 116.3419 | 5.4389 | -110.7704 | 5.4049 | -110.8045
1439.125 | 122.2275 | -116.5375 | 5.6259 | -0.40009 | -0.30151 | -0.52022 | -0.51492 | -0.44442 | -0.28527 | -0.28705 | 5.4872 | 5.5875 | 5.4577 | 5.2877 | -0.011281 | 0.036954 | 116.1248 | 116.2458 | -0.36804 | -0.26947 | -0.48818 | -0.48287 | -0.41238 | -0.25322 | -0.25501 | 5.5192 | 5.6196 | 5.4897 | 5.3198 | 0.020762 | 0.068997 | 116.1568 | 116.2778 | 5.4984 | -110.6376 | 5.469 | -110.6671
1440.875 | 122.2595 | -116.5192 | 5.5893 | -0.34057 | -0.28778 | -0.47444 | -0.46913 | -0.39864 | -0.23948 | -0.26874 | 5.4963 | 5.6013 | 5.4622 | 5.2832 | -0.015859 | 0.041532 | 116.1202 | 116.2321 | -0.30852 | -0.25573 | -0.4424 | -0.43709 | -0.3666 | -0.20744 | -0.23669 | 5.5284 | 5.6333 | 5.4943 | 5.3152 | 0.016184 | 0.073575 | 116.1523 | 116.2641 | 5.5122 | -110.6239 | 5.4781 | -110.658
1442.625 | 122.2321 | -116.6931 | 5.4428 | -0.36804 | -0.30151 | -0.51107 | -0.4966 | -0.41237 | -0.25322 | -0.28247 | 5.3361 | 5.4364 | 5.2974 | 5.1275 | -0.011281 | 0.04611 | 116.285 | 116.3923 | -0.33599 | -0.26947 | -0.47902 | -0.46456 | -0.38033 | -0.22118 | -0.25043 | 5.3681 | 5.4685 | 5.3295 | 5.1595 | 0.020762 | 0.078153 | 116.3171 | 116.4243 | 5.3474 | -110.949 | 5.3087 | -110.9876
1444.3125 | 122.2366 | -116.9083 | 5.2597 | -0.32225 | -0.27404 | -0.47902 | -0.47371 | -0.38949 | -0.2349 | -0.26416 | 5.185 | 5.2808 | 5.1463 | 4.9718 | -0.011281 | 0.041532 | 116.4361 | 116.5525 | -0.29021 | -0.242 | -0.44697 | -0.44167 | -0.35744 | -0.20286 | -0.23211 | 5.217 | 5.3128 | 5.1784 | 5.0038 | 0.020762 | 0.073575 | 116.4682 | 116.5846 | 5.1963 | -111.2511 | 5.1576 | -111.2898
1446 | 122.3511 | -116.9952 | 5.0583 | -0.3131 | -0.27404 | -0.46986 | -0.45082 | -0.3666 | -0.20743 | -0.26416 | 5.0018 | 5.0976 | 4.9678 | 4.7795 | -0.006702 | 0.04611 | 116.6147 | 116.7357 | -0.28105 | -0.242 | -0.43782 | -0.41877 | -0.33455 | -0.17539 | -0.23211 | 5.0339 | 5.1296 | 4.9998 | 4.8115 | 0.025341 | 0.078153 | 116.6467 | 116.7677 | 5.0085 | -111.6128 | 4.9745 | -111.6469
1447.75 | 122.3373 | -117.16 | 4.8706 | -0.27189 | -0.26488 | -0.4607 | -0.42792 | -0.32997 | -0.16623 | -0.25958 | 4.8141 | 4.9144 | 4.7663 | 4.61 | -0.002124 | 0.04611 | 116.8116 | 116.9371 | -0.23985 | -0.23284 | -0.42866 | -0.39588 | -0.29793 | -0.13418 | -0.22754 | 4.8462 | 4.9465 | 4.7984 | 4.6421 | 0.029919 | 0.078153 | 116.8436 | 116.9691 | 4.8162 | -111.9974 | 4.7685 | -112.0452
1449.4531 | 122.3419 | -117.2882 | 4.7974 | -0.25816 | -0.2603 | -0.45154 | -0.41877 | -0.32082 | -0.15707 | -0.24584 | 4.718 | 4.8091 | 4.6794 | 4.5047 | -0.006702 | 0.055266 | 116.9031 | 117.0332 | -0.22611 | -0.22826 | -0.4195 | -0.38672 | -0.28877 | -0.12503 | -0.2138 | 4.75 | 4.8412 | 4.7114 | 4.5368 | 0.025341 | 0.087309 | 116.9352 | 117.0653 | 4.7247 | -112.1851 | 4.6861 | -112.2238
1451.1875 | 122.3145 | -117.3523 | 4.7287 | -0.14369 | -0.24657 | -0.41034 | -0.35925 | -0.21094 | -0.17081 | -0.255 | 4.6722 | 4.7633 | 4.6336 | 4.4589 | -0.002124 | 0.050688 | 116.9397 | 117.0745 | -0.11165 | -0.21452 | -0.37829 | -0.3272 | -0.1789 | -0.13876 | -0.22296 | 4.7042 | 4.7954 | 4.6656 | 4.491 | 0.029919 | 0.082731 | 116.9718 | 117.1065 | 4.6743 | -112.2676 | 4.6357 | -112.3062
1452.9375 | 122.2046 | -117.572 | 4.5639 | -0.1208 | -0.24657 | -0.40118 | -0.34093 | -0.20179 | -0.16165 | -0.255 | 4.4936 | 4.5848 | 4.4504 | 4.2758 | -0.002124 | 0.055266 | 117.1366 | 117.253 | -0.088761 | -0.21452 | -0.36914 | -0.30889 | -0.16975 | -0.12961 | -0.22296 | 4.5257 | 4.6168 | 4.4825 | 4.3078 | 0.029919 | 0.087309 | 117.1687 | 117.285 | 4.4958 | -112.643 | 4.4526 | -112.6862
1454.6875 | 122.3511 | -117.6315 | 4.4174 | -0.10249 | -0.23283 | -0.35997 | -0.29515 | -0.1789 | -0.14334 | -0.23211 | 4.3975 | 4.4932 | 4.3497 | 4.1796 | 0.002454 | 0.050688 | 117.2236 | 117.3446 | -0.070447 | -0.20079 | -0.32793 | -0.26311 | -0.14686 | -0.11129 | -0.20007 | 4.4295 | 4.5252 | 4.3818 | 4.2117 | 0.034497 | 0.082731 | 117.2557 | 117.3766 | 4.395 | -112.8261 | 4.3473 | -112.8739
1456.375 | 122.2687 | -117.746 | 4.3991 | -0.093333 | -0.20994 | -0.32792 | -0.24021 | -0.17432 | -0.13876 | -0.24127 | 4.2968 | 4.397 | 4.2582 | 4.0834 | -0.006702 | 0.04611 | 117.3426 | 117.4544 | -0.06129 | -0.17789 | -0.29588 | -0.20816 | -0.14228 | -0.10671 | -0.20922 | 4.3288 | 4.4291 | 4.2902 | 4.1155 | 0.025341 | 0.078153 | 117.3747 | 117.4865 | 4.3035 | -113.0459 | 4.2649 | -113.0845
1458.125 | 122.3511 | -117.8192 | 4.2526 | -0.084176 | -0.19162 | -0.30045 | -0.21274 | -0.16059 | -0.1296 | -0.22295 | 4.2189 | 4.31 | 4.1758 | 3.9919 | -0.006702 | 0.055266 | 117.4067 | 117.5323 | -0.052133 | -0.15958 | -0.26841 | -0.18069 | -0.12854 | -0.097558 | -0.19091 | 4.251 | 4.3421 | 4.2078 | 4.0239 | 0.025341 | 0.087309 | 117.4388 | 117.5643 | 4.2256 | -113.1878 | 4.1825 | -113.231
1459.875 | 122.3465 | -117.9611 | 4.1107 | -0.056706 | -0.17788 | -0.27298 | -0.18526 | -0.1377 | -0.097553 | -0.20464 | 4.077 | 4.1635 | 4.0384 | 3.8591 | -0.006702 | 0.050688 | 117.5487 | 117.6696 | -0.024663 | -0.14584 | -0.24094 | -0.15322 | -0.10565 | -0.06551 | -0.1726 | 4.109 | 4.1956 | 4.0704 | 3.8911 | 0.025341 | 0.082731 | 117.5807 | 117.7017 | 4.0837 | -113.4717 | 4.0451 | -113.5103
1461.625 | 122.3419 | -118.6295 | 3.4332 | -0.024657 | -0.15957 | -0.25467 | -0.15321 | -0.11023 | -0.074661 | -0.18175 | 3.3856 | 3.4813 | 3.3379 | 3.1631 | -0.006702 | 0.04611 | 118.2492 | 118.3747 | 0.007386 | -0.12753 | -0.22262 | -0.12117 | -0.078187 | -0.042618 | -0.14971 | 3.4177 | 3.5133 | 3.37 | 3.1951 | 0.025341 | 0.078153 | 118.2812 | 118.4067 | 3.3923 | -114.8635 | 3.3446 | -114.9112
1463.2969 | 122.2687 | -118.7485 | 3.3783 | -0.006344 | -0.15041 | -0.24093 | -0.13948 | -0.10107 | -0.060926 | -0.17717 | 3.2849 | 3.3897 | 3.2418 | 3.0761 | -0.011281 | 0.050688 | 118.359 | 118.4616 | 0.025699 | -0.11837 | -0.20889 | -0.10744 | -0.069031 | -0.028883 | -0.14513 | 3.3169 | 3.4217 | 3.2738 | 3.1081 | 0.020762 | 0.082731 | 118.3911 | 118.4937 | 3.2962 | -115.0741 | 3.2531 | -115.1173
1465.0469 | 122.2321 | -118.8812 | 3.3234 | 0.007391 | -0.1092 | -0.19972 | -0.12574 | -0.096496 | -0.04719 | -0.15428 | 3.2117 | 3.3027 | 3.1731 | 2.9982 | -0.006702 | 0.041532 | 118.4231 | 118.5486 | 0.039434 | -0.07716 | -0.16768 | -0.093701 | -0.064453 | -0.015147 | -0.12224 | 3.2437 | 3.3347 | 3.2051 | 3.0303 | 0.025341 | 0.073575 | 118.4552 | 118.5807 | 3.2184 | -115.2115 | 3.1798 | -115.25
1466.7969 | 122.3373 | -118.8126 | 3.2501 | 0.01197 | -0.10004 | -0.19514 | -0.12116 | -0.082762 | -0.04719 | -0.15428 | 3.1567 | 3.2615 | 3.1136 | 2.9387 | -0.015859 | 0.041532 | 118.4689 | 118.5898 | 0.044013 | -0.068002 | -0.1631 | -0.089122 | -0.050719 | -0.015147 | -0.12224 | 3.1888 | 3.2935 | 3.1456 | 2.9707 | 0.016184 | 0.073575 | 118.501 | 118.6219 | 3.1726 | -115.3122 | 3.1294 | -115.3553
1468.5625 | 122.2641 | -118.8904 | 3.2501 | 0.021127 | -0.086309 | -0.18599 | -0.11659 | -0.06445 | -0.028877 | -0.13139 | 3.1842 | 3.2844 | 3.1456 | 2.9753 | -0.020437 | 0.036954 | 118.4552 | 118.5761 | 0.05317 | -0.054266 | -0.15394 | -0.084544 | -0.032407 | 0.003166 | -0.099347 | 3.2162 | 3.3164 | 3.1777 | 3.0074 | 0.011606 | 0.068997 | 118.4872 | 118.6081 | 3.2046 | -115.271 | 3.1661 | -115.3096
1470.25 | 122.3145 | -118.8858 | 3.2318 | 0.030283 | -0.08173 | -0.17225 | -0.098273 | -0.069028 | -0.024298 | -0.13139 | 3.1933 | 3.2935 | 3.1502 | 2.9845 | -0.015859 | 0.032376 | 118.4323 | 118.5578 | 0.062326 | -0.049687 | -0.14021 | -0.06623 | -0.036985 | 0.007745 | -0.099347 | 3.2254 | 3.3256 | 3.1823 | 3.0165 | 0.016184 | 0.064419 | 118.4643 | 118.5898 | 3.2092 | -115.239 | 3.1661 | -115.2821
1472.0312 | 122.2412 | -118.9133 | 3.2547 | 0.03944 | -0.077151 | -0.16767 | -0.098273 | -0.055294 | -0.024298 | -0.13139 | 3.1659 | 3.2707 | 3.1319 | 2.957 | -0.020437 | 0.041532 | 118.4598 | 118.5852 | 0.071483 | -0.045108 | -0.13563 | -0.06623 | -0.023251 | 0.007745 | -0.099347 | 3.1979 | 3.3027 | 3.1639 | 2.989 | 0.011606 | 0.073575 | 118.4918 | 118.6173 | 3.1863 | -115.2939 | 3.1523 | -115.3279
1473.7812 | 122.2595 | -118.8995 | 3.2593 | 0.044018 | -0.077151 | -0.16309 | -0.093694 | -0.055294 | -0.015142 | -0.13597 | 3.1842 | 3.2798 | 3.1411 | 2.9707 | -0.029593 | 0.032376 | 118.4552 | 118.5807 | 0.076061 | -0.045108 | -0.13105 | -0.061651 | -0.023251 | 0.016901 | -0.10393 | 3.2162 | 3.3119 | 3.1731 | 3.0028 | 0.00245 | 0.064419 | 118.4872 | 118.6127 | 3.2138 | -115.271 | 3.1707 | -115.3141
1475.4688 | 122.2549 | -118.9682 | 3.1677 | 0.053175 | -0.072572 | -0.14478 | -0.089116 | -0.050716 | -0.001406 | -0.12223 | 3.0972 | 3.1974 | 3.0541 | 2.8837 | -0.029593 | 0.02322 | 118.5468 | 118.6585 | 0.085218 | -0.040529 | -0.11274 | -0.057073 | -0.018673 | 0.030637 | -0.090191 | 3.1292 | 3.2294 | 3.0861 | 2.9158 | 0.00245 | 0.055263 | 118.5788 | 118.6905 | 3.1268 | -115.4496 | 3.0837 | -115.4927
1477.2188 | 122.3236 | -118.9682 | 3.1265 | 0.053175 | -0.067994 | -0.14936 | -0.093694 | -0.050716 | -0.010563 | -0.12681 | 3.0514 | 3.1516 | 3.0083 | 2.838 | -0.025015 | 0.027798 | 118.588 | 118.7089 | 0.085218 | -0.035951 | -0.11731 | -0.061651 | -0.018673 | 0.02148 | -0.094769 | 3.0834 | 3.1836 | 3.0403 | 2.87 | 0.007028 | 0.059841 | 118.62 | 118.7409 | 3.0764 | -115.5366 | 3.0333 | -115.5797
1478.9844 | 122.2961 | -119.0781 | 3.0304 | 0.048597 | -0.072572 | -0.13562 | -0.093694 | -0.046138 | -0.010563 | -0.11765 | 2.9781 | 3.0738 | 2.9442 | 2.7693 | -0.020437 | 0.02322 | 118.6521 | 118.7775 | 0.08064 | -0.040529 | -0.10358 | -0.061651 | -0.014095 | 0.02148 | -0.085612 | 3.0102 | 3.1058 | 2.9762 | 2.8013 | 0.011606 | 0.055263 | 118.6841 | 118.8096 | 2.9986 | -115.6739 | 2.9646 | -115.7079
1480.6719 | 122.2458 | -119.3024 | 2.8519 | 0.048597 | -0.067994 | -0.13104 | -0.07538 | -0.036983 | -0.001406 | -0.11308 | 2.7767 | 2.8677 | 2.7336 | 2.5632 | -0.025015 | 0.027798 | 118.8581 | 118.9835 | 0.08064 | -0.035951 | -0.099 | -0.043337 | -0.00494 | 0.030637 | -0.081034 | 2.8087 | 2.8998 | 2.7656 | 2.5953 | 0.007028 | 0.059841 | 118.8901 | 119.0156 | 2.8017 | -116.0814 | 2.7586 | -116.1245
1482.3438 | 122.3557 | -119.3756 | 2.7145 | 0.057754 | -0.058836 | -0.13104 | -0.07538 | -0.036983 | -0.001406 | -0.11308 | 2.6531 | 2.7487 | 2.61 | 2.4442 | -0.025015 | 0.027798 | 118.9909 | 119.1072 | 0.089797 | -0.026793 | -0.099 | -0.043337 | -0.00494 | 0.030637 | -0.081034 | 2.6851 | 2.7807 | 2.642 | 2.4762 | 0.007028 | 0.059841 | 119.0229 | 119.1392 | 2.6781 | -116.3378 | 2.635 | -116.3809
1484.0938 | 122.3053 | -119.4855 | 2.623 | 0.06691 | -0.058836 | -0.12646 | -0.079959 | -0.032405 | -0.001406 | -0.11308 | 2.5615 | 2.6708 | 2.523 | 2.3434 | -0.029593 | 0.032376 | 119.0733 | 119.2033 | 0.098953 | -0.026793 | -0.094422 | -0.047916 | -0.000362 | 0.030637 | -0.081034 | 2.5935 | 2.7029 | 2.555 | 2.3755 | 0.00245 | 0.064419 | 119.1053 | 119.2353 | 2.5911 | -116.5118 | 2.5526 | -116.5503
1485.7656 | 122.2778 | -119.5404 | 2.6093 | 0.053175 | -0.054257 | -0.12189 | -0.07538 | -0.032405 | 0.003172 | -0.11308 | 2.4928 | 2.5976 | 2.4589 | 2.2839 | -0.025015 | 0.02322 | 119.1465 | 119.2628 | 0.085218 | -0.022214 | -0.089843 | -0.043337 | -0.000362 | 0.035215 | -0.081034 | 2.5249 | 2.6296 | 2.4909 | 2.3159 | 0.007028 | 0.055263 | 119.1786 | 119.2949 | 2.5178 | -116.6537 | 2.4839 | -116.6876
1487.4531 | 122.2687 | -119.7235 | 2.417 | 0.062332 | -0.054257 | -0.11731 | -0.066223 | -0.032405 | 0.016907 | -0.094765 | 2.3417 | 2.4419 | 2.3032 | 2.1374 | -0.025015 | 0.032376 | 119.2976 | 119.4231 | 0.094375 | -0.022214 | -0.085264 | -0.03418 | -0.000362 | 0.04895 | -0.062722 | 2.3738 | 2.4739 | 2.3353 | 2.1694 | 0.007028 | 0.064419 | 119.3297 | 119.4551 | 2.3667 | -116.9559 | 2.3282 | -116.9944
1489.1406 | 122.3648 | -119.751 | 2.3346 | 0.080646 | -0.054257 | -0.11731 | -0.066223 | -0.023249 | 0.012329 | -0.094765 | 2.2731 | 2.3778 | 2.23 | 2.0595 | -0.029593 | 0.032376 | 119.3663 | 119.4917 | 0.11269 | -0.022214 | -0.085264 | -0.03418 | 0.008794 | 0.044372 | -0.062722 | 2.3051 | 2.4098 | 2.262 | 2.0916 | 0.00245 | 0.064419 | 119.3983 | 119.5238 | 2.3027 | -117.0932 | 2.2596 | -117.1363
1490.8906 | 122.2275 | -119.8746 | 2.3163 | 0.080646 | -0.049678 | -0.11273 | -0.061645 | -0.023249 | 0.00775 | -0.090186 | 2.209 | 2.3137 | 2.1659 | 1.9954 | -0.025015 | 0.027798 | 119.435 | 119.5604 | 0.11269 | -0.017635 | -0.080686 | -0.029602 | 0.008794 | 0.039793 | -0.058143 | 2.241 | 2.3457 | 2.1979 | 2.0275 | 0.007028 | 0.059841 | 119.467 | 119.5924 | 2.234 | -117.226 | 2.1909 | -117.2691
1492.6406 | 122.3511 | -119.8837 | 2.211 | 0.080646 | -0.040521 | -0.10357 | -0.057066 | -0.018671 | 0.016907 | -0.090186 | 2.1494 | 2.245 | 2.1109 | 1.945 | -0.025015 | 0.036954 | 119.4853 | 119.6108 | 0.11269 | -0.008478 | -0.071529 | -0.025023 | 0.013372 | 0.04895 | -0.058143 | 2.1815 | 2.277 | 2.143 | 1.9771 | 0.007028 | 0.068997 | 119.5174 | 119.6428 | 2.1745 | -117.3359 | 2.136 | -117.3744
1494.3281 | 122.3236 | -119.9707 | 2.1423 | 0.076067 | -0.0451 | -0.10815 | -0.066223 | -0.023249 | 0.016907 | -0.099343 | 2.0716 | 2.1717 | 2.0285 | 1.8626 | -0.025015 | 0.027798 | 119.5723 | 119.6977 | 0.10811 | -0.013057 | -0.076107 | -0.03418 | 0.008794 | 0.04895 | -0.0673 | 2.1036 | 2.2038 | 2.0606 | 1.8947 | 0.007028 | 0.059841 | 119.6044 | 119.7298 | 2.0966 | -117.5007 | 2.0536 | -117.5438
1496.0781 | 122.2961 | -120.0256 | 2.0737 | 0.076067 | -0.040521 | -0.10815 | -0.057066 | -0.014093 | 0.016907 | -0.094765 | 2.0258 | 2.1259 | 1.9873 | 1.8031 | -0.015859 | 0.027798 | 119.6135 | 119.7344 | 0.10811 | -0.008478 | -0.076107 | -0.025023 | 0.01795 | 0.04895 | -0.062722 | 2.0579 | 2.158 | 2.0194 | 1.8351 | 0.016184 | 0.059841 | 119.6456 | 119.7664 | 2.0417 | -117.5877 | 2.0032 | -117.6262
1497.8125 | 122.2549 | -120.108 | 2.0737 | 0.080646 | -0.035942 | -0.098993 | -0.061645 | -0.018671 | 0.021485 | -0.090186 | 1.9755 | 2.071 | 1.9278 | 1.7665 | -0.020437 | 0.032376 | 119.6639 | 119.7847 | 0.11269 | -0.003899 | -0.06695 | -0.029602 | 0.013372 | 0.053528 | -0.058143 | 2.0075 | 2.103 | 1.9599 | 1.7985 | 0.011606 | 0.064419 | 119.6959 | 119.8168 | 1.9959 | -117.6884 | 1.9483 | -117.7361
1499.5781 | 122.3236 | -120.1218 | 1.9867 | 0.080646 | -0.040521 | -0.094414 | -0.061645 | -0.018671 | 0.026064 | -0.085608 | 1.9251 | 2.0252 | 1.882 | 1.7115 | -0.025015 | 0.027798 | 119.7143 | 119.8305 | 0.11269 | -0.008478 | -0.062371 | -0.029602 | 0.013372 | 0.058107 | -0.053565 | 1.9571 | 2.0573 | 1.9141 | 1.7436 | 0.007028 | 0.059841 | 119.7463 | 119.8626 | 1.9501 | -117.7892 | 1.907 | -117.8322
1501.2656 | 122.2641 | -120.1584 | 1.9958 | 0.085224 | -0.035942 | -0.080679 | -0.047909 | -0.004937 | 0.026064 | -0.076452 | 1.9114 | 2.0023 | 1.8591 | 1.6932 | -0.034171 | 0.02322 | 119.7417 | 119.8626 | 0.11727 | -0.003899 | -0.048636 | -0.015866 | 0.027106 | 0.058107 | -0.044409 | 1.9434 | 2.0344 | 1.8912 | 1.7252 | -0.002128 | 0.055263 | 119.7738 | 119.8946 | 1.9455 | -117.8304 | 1.8933 | -117.8826
1503.0312 | 122.2504 | -120.2087 | 1.9501 | 0.080646 | -0.031363 | -0.085257 | -0.047909 | -0.004937 | 0.030642 | -0.076452 | 1.8335 | 1.9428 | 1.7996 | 1.6337 | -0.029593 | 0.02322 | 119.8012 | 119.9221 | 0.11269 | 0.00068 | -0.053214 | -0.015866 | 0.027106 | 0.062685 | -0.044409 | 1.8656 | 1.9748 | 1.8317 | 1.6657 | 0.00245 | 0.055263 | 119.8333 | 119.9541 | 1.8631 | -117.9677 | 1.8292 | -118.0016
1504.7812 | 122.2641 | -120.2545 | 1.886 | 0.094381 | -0.026784 | -0.080679 | -0.047909 | -0.000359 | 0.030642 | -0.071874 | 1.7923 | 1.8924 | 1.763 | 1.5925 | -0.029593 | 0.027798 | 119.8424 | 119.977 | 0.12642 | 0.005259 | -0.048636 | -0.015866 | 0.031684 | 0.062685 | -0.039831 | 1.8244 | 1.9245 | 1.795 | 1.6245 | 0.00245 | 0.059841 | 119.8745 | 120.0091 | 1.8219 | -118.0501 | 1.7926 | -118.0794
1506.4688 | 122.2092 | -120.3186 | 1.8539 | 0.089802 | -0.026784 | -0.071521 | -0.047909 | 0.004219 | 0.039799 | -0.071874 | 1.7465 | 1.8421 | 1.7035 | 1.5421 | -0.034171 | 0.027798 | 119.8928 | 120.0091 | 0.12185 | 0.005259 | -0.039478 | -0.015866 | 0.036262 | 0.071842 | -0.039831 | 1.7786 | 1.8741 | 1.7355 | 1.5741 | -0.002128 | 0.059841 | 119.9249 | 120.0411 | 1.7807 | -118.1463 | 1.7376 | -118.1893
1508.2188 | 122.3602 | -120.3369 | 1.7624 | 0.085224 | -0.026784 | -0.0761 | -0.052488 | -0.004937 | 0.030642 | -0.071874 | 1.7053 | 1.8054 | 1.6669 | 1.4917 | -0.034171 | 0.027798 | 119.934 | 120.0594 | 0.11727 | 0.005259 | -0.044057 | -0.020445 | 0.027106 | 0.062685 | -0.039831 | 1.7374 | 1.8375 | 1.6989 | 1.5238 | -0.002128 | 0.059841 | 119.9661 | 120.0915 | 1.7395 | -118.2287 | 1.701 | -118.2672
1509.9688 | 122.3465 | -120.3369 | 1.7303 | 0.089802 | -0.031363 | -0.066943 | -0.052488 | -0.009515 | 0.030642 | -0.067295 | 1.6733 | 1.778 | 1.644 | 1.4688 | -0.025015 | 0.027798 | 119.9661 | 120.0869 | 0.12185 | 0.00068 | -0.0349 | -0.020445 | 0.022528 | 0.062685 | -0.035252 | 1.7053 | 1.81 | 1.676 | 1.5009 | 0.007028 | 0.059841 | 119.9981 | 120.1189 | 1.6983 | -118.2928 | 1.669 | -118.3221
1511.7188 | 122.2275 | -120.4147 | 1.7532 | 0.089802 | -0.031363 | -0.062364 | -0.047909 | -0.009515 | 0.035221 | -0.067295 | 1.6458 | 1.7505 | 1.6028 | 1.4322 | -0.020437 | 0.027798 | 119.9935 | 120.1235 | 0.12185 | 0.00068 | -0.030321 | -0.015866 | 0.022528 | 0.067264 | -0.035252 | 1.6778 | 1.7825 | 1.6348 | 1.4642 | 0.011606 | 0.059841 | 120.0256 | 120.1556 | 1.6662 | -118.3477 | 1.6232 | -118.3908
1513.4062 | 122.2183 | -120.4834 | 1.7166 | 0.080646 | -0.026784 | -0.071521 | -0.043331 | -0.004937 | 0.035221 | -0.067295 | 1.6046 | 1.7047 | 1.5661 | 1.4047 | -0.025015 | 0.027798 | 120.0485 | 120.1647 | 0.11269 | 0.005259 | -0.039478 | -0.011288 | 0.027106 | 0.067264 | -0.035252 | 1.6366 | 1.7367 | 1.5982 | 1.4368 | 0.007028 | 0.059841 | 120.0805 | 120.1968 | 1.6296 | -118.4439 | 1.5911 | -118.4823
1515.1562 | 122.3145 | -120.4422 | 1.6571 | 0.089802 | -0.031363 | -0.062364 | -0.047909 | -0.000359 | 0.030642 | -0.067295 | 1.5817 | 1.6818 | 1.5387 | 1.3681 | -0.025015 | 0.02322 | 120.0622 | 120.183 | 0.12185 | 0.00068 | -0.030321 | -0.015866 | 0.031684 | 0.062685 | -0.035252 | 1.6137 | 1.7138 | 1.5707 | 1.4001 | 0.007028 | 0.055263 | 120.0943 | 120.2151 | 1.6067 | -118.4805 | 1.5637 | -118.5235
1516.9219 | 122.3053 | -120.5063 | 1.6434 | 0.094381 | -0.026784 | -0.057786 | -0.047909 | -0.000359 | 0.030642 | -0.08103 | 1.5542 | 1.6589 | 1.5158 | 1.3452 | -0.015859 | 0.032376 | 120.0851 | 120.2105 | 0.12642 | 0.005259 | -0.025743 | -0.015866 | 0.031684 | 0.062685 | -0.048987 | 1.5863 | 1.691 | 1.5478 | 1.3772 | 0.016184 | 0.064419 | 120.1171 | 120.2425 | 1.5701 | -118.5309 | 1.5316 | -118.5693
1518.6719 | 122.287 | -120.5063 | 1.6067 | 0.098959 | -0.026784 | -0.057786 | -0.038752 | 0.004219 | 0.039799 | -0.08103 | 1.5405 | 1.6406 | 1.4975 | 1.3315 | -0.025015 | 0.032376 | 120.1126 | 120.2242 | 0.131 | 0.005259 | -0.025743 | -0.006709 | 0.036262 | 0.071842 | -0.048987 | 1.5725 | 1.6726 | 1.5295 | 1.3635 | 0.007028 | 0.064419 | 120.1446 | 120.2563 | 1.5655 | -118.5721 | 1.5225 | -118.6151
1520.3594 | 122.2412 | -120.5795 | 1.6159 | 0.098959 | -0.026784 | -0.057786 | -0.047909 | 0.008797 | 0.044377 | -0.085608 | 1.513 | 1.6085 | 1.47 | 1.304 | -0.020437 | 0.036954 | 120.14 | 120.2563 | 0.131 | 0.005259 | -0.025743 | -0.015866 | 0.04084 | 0.07642 | -0.053565 | 1.5451 | 1.6406 | 1.502 | 1.336 | 0.011606 | 0.068997 | 120.1721 | 120.2883 | 1.5335 | -118.627 | 1.4904 | -118.6701
1522.125 | 122.2092 | -120.5841 | 1.5656 | 0.098959 | -0.022205 | -0.048628 | -0.038752 | -0.004937 | 0.039799 | -0.076452 | 1.4856 | 1.5811 | 1.4425 | 1.2765 | -0.020437 | 0.032376 | 120.1629 | 120.2883 | 0.131 | 0.009838 | -0.016585 | -0.006709 | 0.027106 | 0.071842 | -0.044409 | 1.5176 | 1.6131 | 1.4746 | 1.3085 | 0.011606 | 0.064419 | 120.195 | 120.3204 | 1.506 | -118.6774 | 1.463 | -118.7204
1523.875 | 122.3099 | -120.6024 | 1.5518 | 0.094381 | -0.022205 | -0.057786 | -0.052488 | -0.000359 | 0.035221 | -0.08103 | 1.481 | 1.5719 | 1.4334 | 1.2628 | -0.025015 | 0.032376 | 120.1675 | 120.2975 | 0.12642 | 0.009838 | -0.025743 | -0.020445 | 0.031684 | 0.067264 | -0.048987 | 1.513 | 1.604 | 1.4654 | 1.2948 | 0.007028 | 0.064419 | 120.1996 | 120.3295 | 1.506 | -118.6865 | 1.4584 | -118.7341
1525.5625 | 122.3419 | -120.5978 | 1.5152 | 0.098959 | -0.031363 | -0.048628 | -0.043331 | 0.004219 | 0.035221 | -0.08103 | 1.4535 | 1.549 | 1.4013 | 1.2399 | -0.025015 | 0.032376 | 120.2041 | 120.3204 | 0.131 | 0.00068 | -0.016585 | -0.011288 | 0.036262 | 0.067264 | -0.048987 | 1.4856 | 1.5811 | 1.4334 | 1.2719 | 0.007028 | 0.064419 | 120.2362 | 120.3524 | 1.4785 | -118.7506 | 1.4263 | -118.8028
1527.25 | 122.3373 | -120.5933 | 1.5106 | 0.089802 | -0.017627 | -0.048628 | -0.038752 | -0.000359 | 0.035221 | -0.08103 | 1.4352 | 1.5353 | 1.4013 | 1.2261 | -0.025015 | 0.014064 | 120.2041 | 120.3295 | 0.12185 | 0.014416 | -0.016585 | -0.006709 | 0.031684 | 0.067264 | -0.048987 | 1.4672 | 1.5673 | 1.4334 | 1.2582 | 0.007028 | 0.046107 | 120.2362 | 120.3616 | 1.4602 | -118.7689 | 1.4263 | -118.8028
1529 | 122.3419 | -120.607 | 1.4969 | 0.098959 | -0.022205 | -0.048628 | -0.038752 | 0.004219 | 0.035221 | -0.071874 | 1.4398 | 1.5353 | 1.3967 | 1.2307 | -0.034171 | 0.027798 | 120.2179 | 120.3387 | 0.131 | 0.009838 | -0.016585 | -0.006709 | 0.036262 | 0.067264 | -0.039831 | 1.4718 | 1.5673 | 1.4288 | 1.2628 | -0.002128 | 0.059841 | 120.2499 | 120.3707 | 1.4739 | -118.7781 | 1.4309 | -118.8211
1530.75 | 122.2549 | -120.6573 | 1.5106 | 0.10354 | -0.035942 | -0.053207 | -0.047909 | -0.000359 | 0.039799 | -0.076452 | 1.4215 | 1.5261 | 1.383 | 1.2261 | -0.025015 | 0.02322 | 120.2362 | 120.3524 | 0.13558 | -0.003899 | -0.021164 | -0.015866 | 0.031684 | 0.071842 | -0.044409 | 1.4535 | 1.5582 | 1.415 | 1.2582 | 0.007028 | 0.055263 | 120.2682 | 120.3845 | 1.4465 | -118.8147 | 1.408 | -118.8532
1532.4375 | 122.3465 | -120.6024 | 1.4694 | 0.094381 | -0.022205 | -0.053207 | -0.047909 | -0.004937 | 0.035221 | -0.08103 | 1.4123 | 1.517 | 1.3693 | 1.2078 | -0.020437 | 0.027798 | 120.2362 | 120.357 | 0.12642 | 0.009838 | -0.021164 | -0.015866 | 0.027106 | 0.067264 | -0.048987 | 1.4443 | 1.549 | 1.4013 | 1.2399 | 0.011606 | 0.059841 | 120.2682 | 120.389 | 1.4327 | -118.8239 | 1.3897 | -118.8669
1534.2031 | 122.2687 | -120.607 | 1.5152 | 0.094381 | -0.017627 | -0.039471 | -0.043331 | -0.004937 | 0.030642 | -0.085608 | 1.4215 | 1.5261 | 1.3876 | 1.2124 | -0.020437 | 0.036954 | 120.227 | 120.3478 | 0.12642 | 0.014416 | -0.007428 | -0.011288 | 0.027106 | 0.062685 | -0.053565 | 1.4535 | 1.5582 | 1.4196 | 1.2444 | 0.011606 | 0.068997 | 120.2591 | 120.3799 | 1.4419 | -118.8056 | 1.408 | -118.8395
1535.8906 | 122.2595 | -120.6757 | 1.4923 | 0.094381 | -0.026784 | -0.048628 | -0.052488 | -0.004937 | 0.030642 | -0.090186 | 1.4031 | 1.5124 | 1.3601 | 1.1987 | -0.025015 | 0.036954 | 120.2499 | 120.3662 | 0.12642 | 0.005259 | -0.016585 | -0.020445 | 0.027106 | 0.062685 | -0.058143 | 1.4352 | 1.5444 | 1.3922 | 1.2307 | 0.007028 | 0.068997 | 120.282 | 120.3982 | 1.4282 | -118.8468 | 1.3851 | -118.8898
1537.6406 | 122.2961 | -120.6665 | 1.4465 | 0.089802 | -0.026784 | -0.053207 | -0.052488 | -0.009515 | 0.030642 | -0.090186 | 1.3848 | 1.4849 | 1.351 | 1.1849 | -0.025015 | 0.02322 | 120.2682 | 120.3799 | 0.12185 | 0.005259 | -0.021164 | -0.020445 | 0.022528 | 0.062685 | -0.058143 | 1.4169 | 1.517 | 1.383 | 1.217 | 0.007028 | 0.055263 | 120.3003 | 120.4119 | 1.4098 | -118.8834 | 1.376 | -118.9173
1539.3281 | 122.2229 | -120.7214 | 1.4648 | 0.089802 | -0.026784 | -0.053207 | -0.052488 | -0.009515 | 0.039799 | -0.08103 | 1.3757 | 1.4666 | 1.3326 | 1.162 | -0.025015 | 0.032376 | 120.2774 | 120.3845 | 0.12185 | 0.005259 | -0.021164 | -0.020445 | 0.022528 | 0.071842 | -0.048987 | 1.4077 | 1.4986 | 1.3647 | 1.1941 | 0.007028 | 0.064419 | 120.3094 | 120.4165 | 1.4007 | -118.9017 | 1.3577 | -118.9448
1541.0938 | 122.3465 | -120.6436 | 1.4465 | 0.085224 | -0.035942 | -0.048628 | -0.057066 | -0.014093 | 0.026064 | -0.085608 | 1.3711 | 1.4712 | 1.3326 | 1.1666 | -0.025015 | 0.036954 | 120.2728 | 120.3982 | 0.11727 | -0.003899 | -0.016585 | -0.025023 | 0.01795 | 0.058107 | -0.053565 | 1.4031 | 1.5032 | 1.3647 | 1.1986 | 0.007028 | 0.068997 | 120.3049 | 120.4302 | 1.3961 | -118.9017 | 1.3577 | -118.9402
1542.8438 | 122.2733 | -120.7169 | 1.4557 | 0.089802 | -0.035942 | -0.048628 | -0.047909 | -0.004937 | 0.035221 | -0.08103 | 1.3803 | 1.4712 | 1.3281 | 1.1712 | -0.03875 | 0.027798 | 120.2774 | 120.3982 | 0.12185 | -0.003899 | -0.016585 | -0.015866 | 0.027106 | 0.067264 | -0.048987 | 1.4123 | 1.5032 | 1.3601 | 1.2032 | -0.006707 | 0.059841 | 120.3094 | 120.4302 | 1.419 | -118.8971 | 1.3668 | -118.9493
1544.5312 | 122.2549 | -120.7123 | 1.4465 | 0.089802 | -0.026784 | -0.04405 | -0.047909 | -0.000359 | 0.030642 | -0.08103 | 1.3574 | 1.462 | 1.3189 | 1.1483 | -0.020437 | 0.036954 | 120.2865 | 120.4119 | 0.12185 | 0.005259 | -0.012007 | -0.015866 | 0.031684 | 0.062685 | -0.048987 | 1.3894 | 1.4941 | 1.3509 | 1.1803 | 0.011606 | 0.068997 | 120.3186 | 120.444 | 1.3778 | -118.9292 | 1.3393 | -118.9676
1546.2188 | 122.3557 | -120.6528 | 1.4282 | 0.10354 | -0.054257 | -0.053207 | -0.038752 | -0.000359 | 0.039799 | -0.076452 | 1.3665 | 1.4574 | 1.3189 | 1.1574 | -0.020437 | 0.027798 | 120.2911 | 120.4119 | 0.13558 | -0.022214 | -0.021164 | -0.006709 | 0.031684 | 0.071842 | -0.044409 | 1.3986 | 1.4895 | 1.3509 | 1.1895 | 0.011606 | 0.059841 | 120.3232 | 120.444 | 1.387 | -118.9246 | 1.3393 | -118.9722
1547.9688 | 122.2366 | -120.7489 | 1.4374 | 0.098959 | -0.058836 | -0.053207 | -0.038752 | -0.000359 | 0.035221 | -0.071874 | 1.3299 | 1.4345 | 1.3052 | 1.1391 | -0.025015 | 0.036954 | 120.3186 | 120.4394 | 0.131 | -0.026793 | -0.021164 | -0.006709 | 0.031684 | 0.067264 | -0.039831 | 1.3619 | 1.4666 | 1.3372 | 1.1712 | 0.007028 | 0.068997 | 120.3506 | 120.4715 | 1.3549 | -118.9887 | 1.3302 | -119.0134
1549.6562 | 122.2778 | -120.7123 | 1.4236 | 0.094381 | -0.031363 | -0.04405 | -0.052488 | -0.004937 | 0.030642 | -0.076452 | 1.3253 | 1.4254 | 1.2914 | 1.1208 | -0.020437 | 0.032376 | 120.3278 | 120.4531 | 0.12642 | 0.00068 | -0.012007 | -0.020445 | 0.027106 | 0.062685 | -0.044409 | 1.3574 | 1.4574 | 1.3235 | 1.1529 | 0.011606 | 0.064419 | 120.3598 | 120.4852 | 1.3457 | -119.0024 | 1.3119 | -119.0363
1551.3438 | 122.2961 | -120.7306 | 1.3687 | 0.085224 | -0.040521 | -0.048628 | -0.052488 | -0.009515 | 0.026064 | -0.085608 | 1.307 | 1.4071 | 1.2685 | 1.1071 | -0.034171 | 0.032376 | 120.3461 | 120.4669 | 0.11727 | -0.008478 | -0.016585 | -0.020445 | 0.022528 | 0.058107 | -0.053565 | 1.339 | 1.4391 | 1.3006 | 1.1391 | -0.002128 | 0.064419 | 120.3781 | 120.4989 | 1.3412 | -119.0391 | 1.3027 | -119.0775
1553.0938 | 122.2824 | -120.7626 | 1.3687 | 0.085224 | -0.031363 | -0.04405 | -0.061645 | -0.004937 | 0.021485 | -0.090186 | 1.2933 | 1.4025 | 1.264 | 1.0888 | -0.020437 | 0.032376 | 120.3506 | 120.4715 | 0.11727 | 0.00068 | -0.012007 | -0.029602 | 0.027106 | 0.053528 | -0.058143 | 1.3253 | 1.4345 | 1.296 | 1.1208 | 0.011606 | 0.064419 | 120.3827 | 120.5035 | 1.3137 | -119.0574 | 1.2844 | -119.0867
1554.8594 | 122.3602 | -120.7718 | 1.3504 | 0.080646 | -0.040521 | -0.053207 | -0.057066 | -0.009515 | 0.016907 | -0.094765 | 1.2795 | 1.3842 | 1.2319 | 1.0842 | -0.034171 | 0.032376 | 120.3644 | 120.4898 | 0.11269 | -0.008478 | -0.021164 | -0.025023 | 0.022528 | 0.04895 | -0.062722 | 1.3116 | 1.4162 | 1.264 | 1.1162 | -0.002128 | 0.064419 | 120.3964 | 120.5218 | 1.3137 | -119.0849 | 1.2661 | -119.1325
1556.6094 | 122.3511 | -120.7626 | 1.3184 | 0.080646 | -0.040521 | -0.04405 | -0.057066 | -0.018671 | 0.021485 | -0.094765 | 1.2612 | 1.3704 | 1.2228 | 1.0567 | -0.025015 | 0.018642 | 120.3873 | 120.5081 | 0.11269 | -0.008478 | -0.012007 | -0.025023 | 0.013372 | 0.053528 | -0.062722 | 1.2933 | 1.4025 | 1.2548 | 1.0888 | 0.007028 | 0.050685 | 120.4193 | 120.5401 | 1.2862 | -119.1261 | 1.2478 | -119.1645
1558.2969 | 122.2229 | -120.8496 | 1.355 | 0.085224 | -0.040521 | -0.048628 | -0.052488 | -0.018671 | 0.021485 | -0.094765 | 1.2429 | 1.3476 | 1.209 | 1.043 | -0.034171 | 0.02322 | 120.4102 | 120.5356 | 0.11727 | -0.008478 | -0.016585 | -0.020445 | 0.013372 | 0.053528 | -0.062722 | 1.2749 | 1.3796 | 1.2411 | 1.075 | -0.002128 | 0.055263 | 120.4422 | 120.5676 | 1.2771 | -119.1673 | 1.2432 | -119.2011
1560.0469 | 122.2733 | -120.726 | 1.442 | 0.076067 | -0.0451 | -0.039471 | -0.057066 | -0.018671 | 0.021485 | -0.090186 | 1.3574 | 1.4574 | 1.3143 | 1.1574 | -0.025015 | 0.041532 | 120.3094 | 120.4165 | 0.10811 | -0.013057 | -0.007428 | -0.025023 | 0.013372 | 0.053528 | -0.058143 | 1.3894 | 1.4895 | 1.3464 | 1.1895 | 0.007028 | 0.073575 | 120.3415 | 120.4486 | 1.3824 | -118.9521 | 1.3393 | -118.9951
1561.8125 | 122.2229 | -120.6848 | 1.506 | 0.076067 | -0.0451 | -0.039471 | -0.057066 | -0.018671 | 0.012329 | -0.099343 | 1.4077 | 1.5078 | 1.3647 | 1.1941 | -0.015859 | 0.032376 | 120.2408 | 120.3662 | 0.10811 | -0.013057 | -0.007428 | -0.025023 | 0.013372 | 0.044372 | -0.0673 | 1.4398 | 1.5399 | 1.3967 | 1.2261 | 0.016184 | 0.064419 | 120.2728 | 120.3982 | 1.4236 | -118.833 | 1.3805 | -118.8761
1563.5 | 122.2275 | -120.6573 | 1.5015 | 0.076067 | -0.054257 | -0.048628 | -0.061645 | -0.018671 | 0.026064 | -0.099343 | 1.4123 | 1.517 | 1.3738 | 1.2078 | -0.015859 | 0.036954 | 120.2362 | 120.357 | 0.10811 | -0.022214 | -0.016585 | -0.029602 | 0.013372 | 0.058107 | -0.0673 | 1.4443 | 1.549 | 1.4059 | 1.2399 | 0.016184 | 0.068997 | 120.2682 | 120.389 | 1.4282 | -118.8239 | 1.3897 | -118.8623
1565.1719 | 122.3053 | -120.8267 | 1.3046 | 0.098959 | -0.095467 | -0.04405 | -0.038752 | 0.004219 | 0.039799 | -0.076452 | 1.2383 | 1.3292 | 1.1907 | 1.0292 | -0.020437 | 0.027798 | 120.4147 | 120.5401 | 0.131 | -0.063424 | -0.012007 | -0.006709 | 0.036262 | 0.071842 | -0.044409 | 1.2704 | 1.3613 | 1.2228 | 1.0613 | 0.011606 | 0.059841 | 120.4468 | 120.5722 | 1.2588 | -119.1764 | 1.2111 | -119.224
1566.9219 | 122.2229 | -120.6528 | 1.5152 | 0.071489 | -0.0451 | -0.04405 | -0.061645 | -0.023249 | 0.021485 | -0.10392 | 1.4169 | 1.5215 | 1.383 | 1.2124 | -0.011281 | 0.04611 | 120.227 | 120.3524 | 0.10353 | -0.013057 | -0.012007 | -0.029602 | 0.008794 | 0.053528 | -0.071878 | 1.4489 | 1.5536 | 1.415 | 1.2444 | 0.020762 | 0.078153 | 120.2591 | 120.3845 | 1.4282 | -118.8102 | 1.3943 | -118.844
1568.6875 | 122.3053 | -120.5887 | 1.4694 | 0.071489 | -0.049678 | -0.04405 | -0.066223 | -0.027827 | 0.00775 | -0.099343 | 1.426 | 1.5307 | 1.3876 | 1.217 | -0.006702 | 0.055266 | 120.2133 | 120.3387 | 0.10353 | -0.017635 | -0.012007 | -0.03418 | 0.004216 | 0.039793 | -0.0673 | 1.4581 | 1.5627 | 1.4196 | 1.249 | 0.025341 | 0.087309 | 120.2453 | 120.3707 | 1.4327 | -118.7873 | 1.3943 | -118.8257
1570.4531 | 122.3053 | -120.6207 | 1.4786 | 0.06691 | -0.049678 | -0.04405 | -0.070802 | -0.023249 | 0.012329 | -0.099343 | 1.4215 | 1.5215 | 1.3876 | 1.217 | -0.002124 | 0.050688 | 120.2225 | 120.3478 | 0.098953 | -0.017635 | -0.012007 | -0.038759 | 0.008794 | 0.044372 | -0.0673 | 1.4535 | 1.5536 | 1.4196 | 1.249 | 0.029919 | 0.082731 | 120.2545 | 120.3799 | 1.4236 | -118.801 | 1.3897 | -118.8349
1572.1406 | 122.2046 | -120.694 | 1.4877 | 0.076067 | -0.054257 | -0.048628 | -0.066223 | -0.018671 | 0.016907 | -0.099343 | 1.394 | 1.4941 | 1.3601 | 1.1849 | 0.002454 | 0.059844 | 120.2453 | 120.3753 | 0.10811 | -0.022214 | -0.016585 | -0.03418 | 0.013372 | 0.04895 | -0.0673 | 1.426 | 1.5261 | 1.3922 | 1.217 | 0.034497 | 0.091887 | 120.2774 | 120.4074 | 1.3915 | -118.8514 | 1.3577 | -118.8852
1573.8281 | 122.2641 | -120.726 | 1.4374 | 0.076067 | -0.049678 | -0.048628 | -0.061645 | -0.018671 | 0.021485 | -0.094765 | 1.339 | 1.4437 | 1.3052 | 1.1391 | -0.015859 | 0.036954 | 120.3049 | 120.4257 | 0.10811 | -0.017635 | -0.016585 | -0.029602 | 0.013372 | 0.053528 | -0.062722 | 1.3711 | 1.4757 | 1.3372 | 1.1712 | 0.016184 | 0.068997 | 120.3369 | 120.4577 | 1.3549 | -118.9658 | 1.321 | -118.9997
1575.5938 | 122.2321 | -120.7123 | 1.474 | 0.089802 | -0.10462 | -0.057786 | -0.047909 | -0.004937 | 0.030642 | -0.085608 | 1.3665 | 1.462 | 1.3281 | 1.162 | -0.015859 | 0.04611 | 120.2865 | 120.4074 | 0.12185 | -0.072581 | -0.025743 | -0.015866 | 0.027106 | 0.062685 | -0.053565 | 1.3986 | 1.4941 | 1.3601 | 1.1941 | 0.016184 | 0.078153 | 120.3186 | 120.4394 | 1.3824 | -118.92 | 1.3439 | -118.9585
1577.2812 | 122.3465 | -120.8038 | 1.268 | 0.10354 | -0.1092 | -0.057786 | -0.043331 | -0.004937 | 0.035221 | -0.076452 | 1.1971 | 1.2972 | 1.1678 | 1.0018 | -0.006702 | 0.050688 | 120.4239 | 120.5401 | 0.13558 | -0.07716 | -0.025743 | -0.011288 | 0.027106 | 0.067264 | -0.044409 | 1.2292 | 1.3292 | 1.1999 | 1.0338 | 0.025341 | 0.082731 | 120.4559 | 120.5722 | 1.2038 | -119.2268 | 1.1745 | -119.2561
1579.0312 | 122.1954 | -120.7214 | 1.2405 | 0.098959 | -0.10004 | -0.053207 | -0.047909 | 0.004219 | 0.030642 | -0.08103 | 1.1147 | 1.2148 | 1.0854 | 0.91476 | -0.015859 | 0.041532 | 120.3781 | 120.5035 | 0.131 | -0.068002 | -0.021164 | -0.015866 | 0.036262 | 0.062685 | -0.048987 | 1.1467 | 1.2468 | 1.1175 | 0.9468 | 0.016184 | 0.073575 | 120.4102 | 120.5355 | 1.1306 | -119.2634 | 1.1013 | -119.2927
1580.7344 | 122.1588 | -120.9549 | 1.1627 | 0.098959 | -0.095467 | -0.057786 | -0.029595 | 0.008797 | 0.039799 | -0.08103 | 1.0826 | 1.1781 | 1.0442 | 0.86897 | -0.011281 | 0.036954 | 120.5155 | 120.6363 | 0.131 | -0.063424 | -0.025743 | 0.002448 | 0.04084 | 0.071842 | -0.048987 | 1.1147 | 1.2102 | 1.0763 | 0.90101 | 0.020762 | 0.068997 | 120.5475 | 120.6683 | 1.0939 | -119.4328 | 1.0555 | -119.4713
1582.4219 | 122.2733 | -120.5658 | 1.5244 | 0.062332 | -0.11378 | -0.080679 | -0.070802 | -0.027827 | 0.003172 | -0.1085 | 1.4398 | 1.5444 | 1.3967 | 1.2399 | 0.01161 | 0.064423 | 120.1629 | 120.2975 | 0.094375 | -0.081739 | -0.048636 | -0.038759 | 0.004216 | 0.035215 | -0.076456 | 1.4718 | 1.5765 | 1.4288 | 1.2719 | 0.043653 | 0.096466 | 120.195 | 120.3295 | 1.4282 | -118.7232 | 1.3851 | -118.7662
1584.1719 | 122.1909 | -120.6894 | 1.4832 | 0.071489 | -0.11836 | -0.071521 | -0.070802 | -0.027827 | 0.00775 | -0.11765 | 1.3619 | 1.4712 | 1.3281 | 1.1666 | 0.007032 | 0.073579 | 120.2637 | 120.3753 | 0.10353 | -0.086318 | -0.039478 | -0.038759 | 0.004216 | 0.039793 | -0.085612 | 1.394 | 1.5032 | 1.3601 | 1.1986 | 0.039075 | 0.10562 | 120.2957 | 120.4074 | 1.3549 | -118.9017 | 1.321 | -118.9356
1585.9219 | 122.2321 | -120.282 | 1.8677 | 0.044018 | -0.13668 | -0.085257 | -0.089116 | -0.041561 | -0.005985 | -0.13139 | 1.7557 | 1.8604 | 1.7172 | 1.5558 | 0.094017 | 0.15141 | 119.8653 | 119.9862 | 0.076061 | -0.10463 | -0.053214 | -0.057073 | -0.009518 | 0.026058 | -0.099347 | 1.7877 | 1.8924 | 1.7493 | 1.5879 | 0.12606 | 0.18345 | 119.8974 | 120.0182 | 1.6617 | -118.1096 | 1.6232 | -118.1481
1587.6719 | 122.2092 | -120.2637 | 1.8768 | 0.03944 | -0.15499 | -0.089836 | -0.093694 | -0.055294 | -0.01972 | -0.13139 | 1.774 | 1.8924 | 1.7447 | 1.5741 | 0.10775 | 0.15141 | 119.8424 | 119.9679 | 0.071483 | -0.12295 | -0.057793 | -0.061651 | -0.023251 | 0.012323 | -0.099347 | 1.806 | 1.9245 | 1.7767 | 1.6062 | 0.1398 | 0.18345 | 119.8745 | 119.9999 | 1.6663 | -118.0684 | 1.6369 | -118.0978
1589.4219 | 122.3236 | -120.4697 | 1.593 | 0.03944 | -0.15499 | -0.098993 | -0.093694 | -0.050716 | -0.015142 | -0.13139 | 1.6 | 1.7001 | 1.557 | 1.3818 | 0.11233 | 0.16972 | 120.0118 | 120.1464 | 0.071483 | -0.12295 | -0.06695 | -0.061651 | -0.018673 | 0.016901 | -0.099347 | 1.6321 | 1.7322 | 1.589 | 1.4139 | 0.14437 | 0.20176 | 120.0439 | 120.1784 | 1.4877 | -118.4118 | 1.4446 | -118.4549
1591.1094 | 122.2778 | -120.4926 | 1.5701 | 0.03944 | -0.14125 | -0.10815 | -0.093694 | -0.050716 | -0.01972 | -0.12681 | 1.4856 | 1.5948 | 1.47 | 1.2948 | 0.10775 | 0.16056 | 120.108 | 120.2242 | 0.071483 | -0.10921 | -0.076107 | -0.061651 | -0.018673 | 0.012323 | -0.094769 | 1.5176 | 1.6268 | 1.502 | 1.3269 | 0.1398 | 0.19261 | 120.14 | 120.2563 | 1.3778 | -118.6224 | 1.3622 | -118.638
1592.8594 | 122.3557 | -120.6436 | 1.4053 | 0.089802 | -0.1092 | -0.089836 | -0.052488 | -0.009515 | 0.030642 | -0.094765 | 1.3528 | 1.4574 | 1.3052 | 1.1529 | 0.071126 | 0.13309 | 120.2774 | 120.3936 | 0.12185 | -0.07716 | -0.057793 | -0.020445 | 0.022528 | 0.062685 | -0.062722 | 1.3848 | 1.4895 | 1.3372 | 1.1849 | 0.10317 | 0.16514 | 120.3094 | 120.4257 | 1.2817 | -118.9246 | 1.234 | -118.9722
1594.5625 | 122.2641 | -120.6665 | 1.4465 | 0.085224 | -0.1092 | -0.094414 | -0.057066 | -0.009515 | 0.026064 | -0.094765 | 1.3711 | 1.4758 | 1.3326 | 1.1712 | 0.075705 | 0.13309 | 120.2499 | 120.3707 | 0.11727 | -0.07716 | -0.062371 | -0.025023 | 0.022528 | 0.058107 | -0.062722 | 1.4031 | 1.5078 | 1.3647 | 1.2032 | 0.10775 | 0.16514 | 120.282 | 120.4028 | 1.2954 | -118.8788 | 1.2569 | -118.9173
1596.25 | 122.2366 | -120.6573 | 1.4694 | 0.071489 | -0.1092 | -0.098993 | -0.061645 | -0.027827 | 0.00775 | -0.1085 | 1.3803 | 1.4895 | 1.351 | 1.1758 | 0.080283 | 0.12851 | 120.227 | 120.3524 | 0.10353 | -0.07716 | -0.06695 | -0.029602 | 0.004216 | 0.039793 | -0.076456 | 1.4123 | 1.5215 | 1.383 | 1.2078 | 0.11233 | 0.16056 | 120.2591 | 120.3845 | 1.3 | -118.8468 | 1.2707 | -118.8761
1598.0156 | 122.3145 | -120.7169 | 1.3504 | 0.071489 | -0.095467 | -0.098993 | -0.057066 | -0.023249 | 0.012329 | -0.099343 | 1.3024 | 1.4025 | 1.264 | 1.1025 | 0.066548 | 0.12851 | 120.3186 | 120.4394 | 0.10353 | -0.063424 | -0.06695 | -0.025023 | 0.008794 | 0.044372 | -0.0673 | 1.3345 | 1.4345 | 1.296 | 1.1345 | 0.098591 | 0.16056 | 120.3506 | 120.4715 | 1.2359 | -119.0162 | 1.1974 | -119.0546
1599.7656 | 122.1863 | -120.5612 | 1.5839 | 0.080646 | -0.08173 | -0.098993 | -0.061645 | -0.014093 | 0.026064 | -0.090186 | 1.4718 | 1.5765 | 1.4379 | 1.2673 | 0.080283 | 0.12851 | 120.1263 | 120.2471 | 0.11269 | -0.049687 | -0.06695 | -0.029602 | 0.01795 | 0.058107 | -0.058143 | 1.5039 | 1.6085 | 1.47 | 1.2994 | 0.11233 | 0.16056 | 120.1583 | 120.2792 | 1.3915 | -118.6545 | 1.3577 | -118.6884
1601.4531 | 122.2275 | -120.401 | 1.6937 | 0.076067 | -0.077151 | -0.098993 | -0.061645 | -0.014093 | 0.016907 | -0.099343 | 1.5909 | 1.7001 | 1.557 | 1.3956 | 0.075705 | 0.12394 | 119.9935 | 120.1052 | 0.10811 | -0.045108 | -0.06695 | -0.029602 | 0.01795 | 0.04895 | -0.0673 | 1.6229 | 1.7322 | 1.589 | 1.4276 | 0.10775 | 0.15598 | 120.0256 | 120.1372 | 1.5152 | -118.4027 | 1.4813 | -118.4366
1603.1875 | 122.287 | -120.8084 | 1.2909 | 0.085224 | -0.077151 | -0.089836 | -0.052488 | -0.018671 | 0.026064 | -0.099343 | 1.2246 | 1.3155 | 1.1861 | 1.0155 | 0.071126 | 0.11936 | 120.3919 | 120.5127 | 0.11727 | -0.045108 | -0.057793 | -0.020445 | 0.013372 | 0.058107 | -0.0673 | 1.2566 | 1.3475 | 1.2182 | 1.0475 | 0.10317 | 0.1514 | 120.4239 | 120.5447 | 1.1535 | -119.1673 | 1.115 | -119.2057
1604.9375 | 122.2366 | -120.8176 | 1.2955 | 0.06691 | -0.054257 | -0.094414 | -0.047909 | -0.009515 | 0.021485 | -0.090186 | 1.2108 | 1.3109 | 1.1816 | 1.0109 | 0.075705 | 0.12851 | 120.4056 | 120.531 | 0.098953 | -0.022214 | -0.062371 | -0.015866 | 0.022528 | 0.053528 | -0.058143 | 1.2429 | 1.343 | 1.2136 | 1.043 | 0.10775 | 0.16056 | 120.4376 | 120.563 | 1.1351 | -119.1947 | 1.1058 | -119.224
1606.7031 | 122.1954 | -120.7718 | 1.3504 | 0.048597 | -0.058836 | -0.094414 | -0.089116 | -0.041561 | -0.010563 | -0.12681 | 1.2429 | 1.3521 | 1.2228 | 1.0521 | 0.080283 | 0.13309 | 120.3278 | 120.4577 | 0.08064 | -0.026793 | -0.062371 | -0.057073 | -0.009518 | 0.02148 | -0.094769 | 1.2749 | 1.3842 | 1.2548 | 1.0842 | 0.11233 | 0.16514 | 120.3598 | 120.4898 | 1.1626 | -119.0849 | 1.1425 | -119.105
1608.375 | 122.2092 | -120.7809 | 1.3229 | 0.044018 | -0.063415 | -0.089836 | -0.089116 | -0.046138 | -0.015142 | -0.13139 | 1.2383 | 1.3521 | 1.1999 | 1.0338 | 0.075705 | 0.12851 | 120.3506 | 120.476 | 0.076061 | -0.031372 | -0.057793 | -0.057073 | -0.014095 | 0.016901 | -0.099347 | 1.2704 | 1.3842 | 1.2319 | 1.0659 | 0.10775 | 0.16056 | 120.3827 | 120.5081 | 1.1626 | -119.1123 | 1.1242 | -119.1508
1610.125 | 122.1542 | -120.7169 | 1.3824 | -0.001765 | -0.063415 | -0.10815 | -0.13032 | -0.091918 | -0.056347 | -0.16801 | 1.2841 | 1.3888 | 1.2502 | 1.0888 | 0.094017 | 0.15141 | 120.2865 | 120.4119 | 0.030278 | -0.031372 | -0.076107 | -0.098279 | -0.059875 | -0.024304 | -0.13597 | 1.3161 | 1.4208 | 1.2823 | 1.1208 | 0.12606 | 0.18345 | 120.3186 | 120.444 | 1.1901 | -119.0024 | 1.1562 | -119.0363
1611.8906 | 122.1909 | -120.6848 | 1.3962 | -0.010922 | -0.072572 | -0.11731 | -0.13948 | -0.096496 | -0.065504 | -0.18633 | 1.2887 | 1.3933 | 1.2731 | 1.1071 | 0.089439 | 0.14683 | 120.2591 | 120.389 | 0.021121 | -0.040529 | -0.085264 | -0.10744 | -0.064453 | -0.033461 | -0.15429 | 1.3207 | 1.4254 | 1.3052 | 1.1391 | 0.12148 | 0.17887 | 120.2911 | 120.4211 | 1.1992 | -118.9704 | 1.1837 | -118.986
1613.6406 | 122.1771 | -120.5475 | 1.5106 | 0.03944 | -0.040521 | -0.098993 | -0.098273 | -0.050716 | -0.015142 | -0.13597 | 1.3207 | 1.43 | 1.2914 | 1.1254 | 0.066548 | 0.11478 | 120.2179 | 120.3478 | 0.071483 | -0.008478 | -0.06695 | -0.06623 | -0.018673 | 0.016901 | -0.10393 | 1.3528 | 1.462 | 1.3235 | 1.1574 | 0.098591 | 0.14682 | 120.2499 | 120.3799 | 1.2542 | -118.8971 | 1.2249 | -118.9264
1615.3281 | 122.1954 | -120.6345 | 1.4465 | 0.007391 | -0.049678 | -0.10815 | -0.12116 | -0.073606 | -0.038034 | -0.15886 | 1.3345 | 1.4391 | 1.3143 | 1.1529 | 0.089439 | 0.14225 | 120.2087 | 120.3387 | 0.039434 | -0.017635 | -0.076107 | -0.089122 | -0.041563 | -0.005991 | -0.12682 | 1.3665 | 1.4712 | 1.3464 | 1.1849 | 0.12148 | 0.17429 | 120.2408 | 120.3707 | 1.245 | -118.8742 | 1.2249 | -118.8944
1617.0938 | 122.168 | -120.5978 | 1.4786 | 0.007391 | -0.054257 | -0.10815 | -0.12574 | -0.08734 | -0.04719 | -0.16344 | 1.3528 | 1.4529 | 1.3464 | 1.1849 | 0.094017 | 0.14683 | 120.1629 | 120.2929 | 0.039434 | -0.022214 | -0.076107 | -0.093701 | -0.055297 | -0.015147 | -0.13139 | 1.3848 | 1.4849 | 1.3784 | 1.217 | 0.12606 | 0.17887 | 120.195 | 120.325 | 1.2588 | -118.8102 | 1.2524 | -118.8166
1618.8438 | 122.1725 | -120.5795 | 1.4923 | 0.002813 | -0.0451 | -0.098993 | -0.1349 | -0.08734 | -0.04719 | -0.16344 | 1.3757 | 1.4849 | 1.351 | 1.1758 | 0.089439 | 0.14683 | 120.1812 | 120.3021 | 0.034856 | -0.013057 | -0.06695 | -0.10286 | -0.055297 | -0.015147 | -0.13139 | 1.4077 | 1.517 | 1.383 | 1.2078 | 0.12148 | 0.17887 | 120.2133 | 120.3341 | 1.2862 | -118.8056 | 1.2615 | -118.8303
1620.5312 | 122.1634 | -120.5704 | 1.5472 | 0.01197 | -0.031363 | -0.085257 | -0.12116 | -0.073606 | -0.028877 | -0.15886 | 1.4535 | 1.5628 | 1.4288 | 1.2536 | 0.071126 | 0.11936 | 120.1171 | 120.238 | 0.044013 | 0.00068 | -0.053214 | -0.089122 | -0.041563 | 0.003166 | -0.12682 | 1.4856 | 1.5948 | 1.4608 | 1.2856 | 0.10317 | 0.1514 | 120.1492 | 120.27 | 1.3824 | -118.6636 | 1.3577 | -118.6884
1622.2188 | 122.1909 | -120.5521 | 1.4969 | 0.002813 | -0.035942 | -0.089836 | -0.12574 | -0.082762 | -0.042612 | -0.16801 | 1.4352 | 1.5444 | 1.4105 | 1.2307 | 0.075705 | 0.13309 | 120.1217 | 120.2425 | 0.034856 | -0.003899 | -0.057793 | -0.093701 | -0.050719 | -0.010569 | -0.13597 | 1.4672 | 1.5765 | 1.4425 | 1.2628 | 0.10775 | 0.16514 | 120.1538 | 120.2746 | 1.3595 | -118.6865 | 1.3348 | -118.7113
1623.9688 | 122.1268 | -120.5063 | 1.5793 | -0.001765 | -0.035942 | -0.080679 | -0.13032 | -0.082762 | -0.051769 | -0.16344 | 1.4947 | 1.5902 | 1.4517 | 1.2857 | 0.075705 | 0.12394 | 120.0805 | 120.2059 | 0.030278 | -0.003899 | -0.048636 | -0.098279 | -0.050719 | -0.019726 | -0.13139 | 1.5268 | 1.6223 | 1.4837 | 1.3177 | 0.10775 | 0.15598 | 120.1126 | 120.238 | 1.419 | -118.5858 | 1.376 | -118.6288
1625.7188 | 122.2046 | -120.3461 | 1.712 | 0.01197 | -0.022205 | -0.071521 | -0.11659 | -0.069028 | -0.042612 | -0.16344 | 1.6229 | 1.723 | 1.5844 | 1.4185 | 0.071126 | 0.12394 | 119.9523 | 120.0869 | 0.044013 | 0.009838 | -0.039478 | -0.084544 | -0.036985 | -0.010569 | -0.13139 | 1.655 | 1.7551 | 1.6165 | 1.4505 | 0.10317 | 0.15598 | 119.9844 | 120.1189 | 1.5518 | -118.3294 | 1.5133 | -118.3679
1627.4062 | 122.3007 | -120.3278 | 1.7075 | 0.002813 | -0.031363 | -0.080679 | -0.13032 | -0.08734 | -0.042612 | -0.16801 | 1.6366 | 1.7322 | 1.5936 | 1.4276 | 0.06197 | 0.11478 | 119.934 | 120.0594 | 0.034856 | 0.00068 | -0.048636 | -0.098279 | -0.055297 | -0.010569 | -0.13597 | 1.6687 | 1.7642 | 1.6256 | 1.4597 | 0.094013 | 0.14682 | 119.9661 | 120.0915 | 1.5747 | -118.2974 | 1.5316 | -118.3404
1629.1562 | 122.0947 | -120.4788 | 1.6067 | -0.006344 | -0.08173 | -0.0761 | -0.13948 | -0.10107 | -0.051769 | -0.17717 | 1.4993 | 1.604 | 1.47 | 1.3131 | 0.071126 | 0.11936 | 120.0622 | 120.357 | 0.025699 | -0.049687 | -0.044057 | -0.10744 | -0.069031 | -0.019726 | -0.14513 | 1.5313 | 1.636 | 1.502 | 1.3452 | 0.10317 | 0.1514 | 120.0943 | 120.389 | 1.4282 | -118.5629 | 1.3989 | -118.5922
1630.8594 | 122.1039 | -120.4651 | 1.5701 | -0.015501 | -0.054257 | -0.0761 | -0.14864 | -0.10107 | -0.060926 | -0.17717 | 1.3803 | 1.4758 | 1.4379 | 1.2857 | 0.06197 | 0.12394 | 119.9523 | 120.27 | 0.016542 | -0.022214 | -0.044057 | -0.11659 | -0.069031 | -0.028883 | -0.14513 | 1.4123 | 1.5078 | 1.47 | 1.3177 | 0.094013 | 0.15598 | 119.9844 | 120.3021 | 1.3183 | -118.5721 | 1.376 | -118.5144
1632.5469 | 122.168 | -120.4742 | 1.6479 | -0.084176 | -0.072572 | -0.089836 | -0.20358 | -0.16517 | -0.11587 | -0.24127 | 1.5359 | 1.6452 | 1.4975 | 1.3406 | 0.080283 | 0.13767 | 120.0256 | 120.357 | -0.052133 | -0.040529 | -0.057793 | -0.17153 | -0.13312 | -0.083823 | -0.20922 | 1.568 | 1.6772 | 1.5295 | 1.3727 | 0.11233 | 0.16972 | 120.0576 | 120.389 | 1.4556 | -118.4897 | 1.4172 | -118.5281
1634.2344 | 122.1039 | -120.4971 | 1.5518 | -0.024657 | -0.0451 | -0.0761 | -0.15779 | -0.10565 | -0.074661 | -0.19548 | 1.3803 | 1.4849 | 1.3784 | 1.2078 | 0.043657 | 0.10105 | 120.108 | 120.444 | 0.007386 | -0.013057 | -0.044057 | -0.12575 | -0.073609 | -0.042618 | -0.16344 | 1.4123 | 1.517 | 1.4105 | 1.2399 | 0.0757 | 0.13309 | 120.14 | 120.476 | 1.3366 | -118.7277 | 1.3348 | -118.7296
1635.9844 | 122.1863 | -120.4559 | 1.4923 | -0.033814 | -0.049678 | -0.071521 | -0.16695 | -0.12854 | -0.083817 | -0.20006 | 1.2749 | 1.3796 | 1.3555 | 1.1987 | 0.057392 | 0.11478 | 119.9661 | 120.2975 | -0.001771 | -0.017635 | -0.039478 | -0.13491 | -0.096499 | -0.051774 | -0.16802 | 1.307 | 1.4116 | 1.3876 | 1.2307 | 0.089435 | 0.14682 | 119.9981 | 120.3295 | 1.2176 | -118.6911 | 1.2981 | -118.6105
1637.7344 | 120.6665 | -119.0506 | 1.5839 | -0.033814 | -0.054257 | -0.071521 | -0.18069 | -0.1377 | -0.088396 | -0.20922 | -0.61139 | -0.52977 | 1.4517 | 1.2902 | 0.048236 | 0.11478 | 116.7154 | 116.8593 | -0.001771 | -0.022214 | -0.039478 | -0.14864 | -0.10565 | -0.056353 | -0.17718 | -0.57935 | -0.49772 | 1.4837 | 1.3223 | 0.080279 | 0.14682 | 116.7474 | 116.8913 | -0.65963 | -117.3268 | 1.4034 | -115.2637
1639.4219 | 121.9391 | -111.8866 | 10.0204 | -0.020079 | -0.026784 | 0.001736 | -0.14864 | -0.096496 | -0.060926 | -0.18175 | -9.1228 | -9.3898 | 9.6834 | 9.5096 | 0.098596 | 0.13767 | 111.5052 | 111.6356 | 0.011964 | 0.005259 | 0.033779 | -0.11659 | -0.064453 | -0.028883 | -0.14971 | -9.0908 | -9.3577 | 9.7155 | 9.5416 | 0.13064 | 0.16972 | 111.5372 | 111.6676 | -9.2214 | -120.628 | 9.5848 | -101.8218
1641.1719 | 121.9437 | -111.2686 | 10.6247 | 0.053175 | -0.008469 | 0.033786 | -0.084537 | -0.046138 | -0.010563 | -0.12681 | -9.1228 | -9.3669 | 10.3976 | 10.2194 | 0.084861 | 0.14225 | 110.7635 | 110.9031 | 0.085218 | 0.023574 | 0.065829 | -0.052494 | -0.014095 | 0.02148 | -0.094769 | -9.0908 | -9.3348 | 10.4297 | 10.2514 | 0.1169 | 0.17429 | 110.7955 | 110.9351 | -9.2077 | -119.8863 | 10.3128 | -100.3659
1642.8594 | 122.0581 | -108.934 | 12.8586 | 0.11727 | 0.023583 | 0.08873 | -0.025017 | 0.008797 | 0.058113 | -0.062717 | -9.1228 | -9.3715 | 12.6089 | 12.4264 | 0.075705 | 0.13767 | 108.5064 | 108.6415 | 0.14932 | 0.055626 | 0.12077 | 0.007026 | 0.04084 | 0.090156 | -0.030674 | -9.0908 | -9.3394 | 12.641 | 12.4585 | 0.10775 | 0.16972 | 108.5384 | 108.6735 | -9.1985 | -117.6292 | 12.5332 | -95.8974
1644.625 | 121.8658 | -115.535 | 6.2714 | -0.088755 | -0.054257 | -0.034893 | -0.21731 | -0.17432 | -0.1296 | -0.255 | -9.132 | -9.3852 | 6.4649 | 6.2951 | 0.089439 | 0.14225 | 114.504 | 114.6251 | -0.056712 | -0.022214 | -0.00285 | -0.18527 | -0.14228 | -0.097558 | -0.22296 | -9.0999 | -9.3532 | 6.4969 | 6.3272 | 0.12148 | 0.17429 | 114.5361 | 114.6572 | -9.2214 | -123.636 | 6.3755 | -108.0392
1646.3281 | 121.8384 | -117.2058 | 4.4678 | -0.20779 | -0.08173 | -0.089836 | -0.32262 | -0.27504 | -0.2349 | -0.3603 | -9.1182 | -9.3715 | 4.075 | 3.9094 | 0.10775 | 0.16514 | 116.633 | 116.754 | -0.17575 | -0.049687 | -0.057793 | -0.29058 | -0.24299 | -0.20286 | -0.32826 | -9.0862 | -9.3394 | 4.1071 | 3.9415 | 0.1398 | 0.19718 | 116.665 | 116.786 | -9.226 | -125.7512 | 3.9673 | -112.558
1648.0781 | 121.701 | -116.1804 | 5.452 | -0.1849 | -0.072572 | -0.071521 | -0.30888 | -0.26588 | -0.21659 | -0.34199 | -9.132 | -9.3806 | 4.8671 | 4.697 | 0.10775 | 0.16514 | 115.5571 | 115.907 | -0.15286 | -0.040529 | -0.039478 | -0.27684 | -0.23384 | -0.18455 | -0.30994 | -9.0999 | -9.3486 | 4.8991 | 4.7291 | 0.1398 | 0.19718 | 115.5891 | 115.9391 | -9.2397 | -124.689 | 4.7593 | -110.69
1649.7656 | 121.701 | -115.773 | 5.69 | -0.19406 | -0.086309 | -0.080679 | -0.31804 | -0.26588 | -0.2349 | -0.34656 | -9.132 | -9.3715 | 5.128 | 4.9672 | 0.10317 | 0.15598 | 114.9069 | 115.2432 | -0.16202 | -0.054266 | -0.048636 | -0.286 | -0.23384 | -0.20286 | -0.31452 | -9.0999 | -9.3394 | 5.1601 | 4.9992 | 0.13522 | 0.18803 | 114.939 | 115.2752 | -9.2351 | -124.0389 | 5.0249 | -109.7789
1651.4688 | 121.6232 | -117.2974 | 4.248 | -0.30394 | -0.1092 | -0.12189 | -0.40503 | -0.35286 | -0.31732 | -0.44271 | -9.1274 | -9.3806 | 3.5348 | 3.3737 | 0.094017 | 0.15598 | 116.7795 | 117.1019 | -0.2719 | -0.07716 | -0.089843 | -0.37299 | -0.32082 | -0.28527 | -0.41066 | -9.0954 | -9.3486 | 3.5668 | 3.4057 | 0.12606 | 0.18803 | 116.8115 | 117.134 | -9.2214 | -125.9069 | 3.4408 | -113.2447
1653.2188 | 121.4584 | -114.4775 | 6.7154 | -0.22611 | -0.086309 | -0.066943 | -0.34551 | -0.29335 | -0.24864 | -0.36945 | -9.132 | -9.3669 | 5.6866 | 5.5213 | 0.10775 | 0.15598 | 113.6387 | 113.9705 | -0.19406 | -0.054266 | -0.0349 | -0.31347 | -0.26131 | -0.2166 | -0.33741 | -9.0999 | -9.3348 | 5.7186 | 5.5533 | 0.1398 | 0.18803 | 113.6708 | 114.0025 | -9.2397 | -122.7707 | 5.5788 | -107.9521
1654.9688 | 121.5683 | -117.6956 | 3.6163 | -0.23069 | -0.095467 | -0.089836 | -0.35925 | -0.30708 | -0.26695 | -0.38777 | -9.1274 | -9.3715 | 3.6447 | 3.479 | 0.071126 | 0.11478 | 116.3308 | 116.5617 | -0.19864 | -0.063424 | -0.057793 | -0.3272 | -0.27504 | -0.23491 | -0.35573 | -9.0954 | -9.3394 | 3.6767 | 3.5111 | 0.10317 | 0.14682 | 116.3629 | 116.5937 | -9.1985 | -125.4582 | 3.5735 | -112.6862
1656.7344 | 121.3303 | -116.3361 | 4.9759 | -0.16659 | -0.072572 | -0.062364 | -0.28141 | -0.22926 | -0.19828 | -0.31452 | -9.1274 | -9.3898 | 4.2124 | 4.0331 | 0.080283 | 0.14225 | 115.5891 | 115.8383 | -0.13454 | -0.040529 | -0.030321 | -0.24937 | -0.19721 | -0.16623 | -0.28247 | -9.0954 | -9.3577 | 4.2444 | 4.0651 | 0.11233 | 0.17429 | 115.6212 | 115.8704 | -9.2077 | -124.7165 | 4.1321 | -111.3767
1658.4844 | 121.2387 | -114.4867 | 6.5643 | -0.11165 | -0.054257 | -0.030314 | -0.23563 | -0.19263 | -0.14334 | -0.26874 | -9.132 | -9.3852 | 5.6316 | 5.4434 | 0.094017 | 0.14225 | 113.3732 | 113.6774 | -0.079604 | -0.022214 | 0.001729 | -0.20359 | -0.16059 | -0.11129 | -0.23669 | -9.0999 | -9.3532 | 5.6637 | 5.4755 | 0.12606 | 0.17429 | 113.4052 | 113.7095 | -9.226 | -122.5052 | 5.5376 | -107.7415
1660.1719 | 121.0327 | -113.6856 | 7.251 | -0.13912 | -0.067994 | -0.030314 | -0.27226 | -0.2201 | -0.18454 | -0.30536 | -9.132 | -9.3944 | 5.8194 | 5.6495 | 0.080283 | 0.14683 | 112.7505 | 113.0365 | -0.10707 | -0.035951 | 0.001729 | -0.24021 | -0.18806 | -0.1525 | -0.27332 | -9.0999 | -9.3623 | 5.8514 | 5.6815 | 0.11233 | 0.17887 | 112.7826 | 113.0685 | -9.2123 | -121.8825 | 5.7391 | -106.9312
1661.9219 | 121.1334 | -115.5075 | 5.4245 | -0.1208 | -0.072572 | -0.048628 | -0.25394 | -0.20179 | -0.16165 | -0.27331 | -9.1366 | -9.3806 | 4.4688 | 4.2941 | 0.066548 | 0.12394 | 114.6918 | 114.7991 | -0.088761 | -0.040529 | -0.016585 | -0.2219 | -0.16975 | -0.12961 | -0.24127 | -9.1045 | -9.3486 | 4.5008 | 4.3261 | 0.098591 | 0.15598 | 114.7238 | 114.8311 | -9.2031 | -123.8283 | 4.4022 | -110.223
1663.6094 | 121.2891 | -118.8995 | 2.3483 | -0.19406 | -0.090888 | -0.094414 | -0.32262 | -0.27504 | -0.23033 | -0.35114 | -6.9251 | -7.0042 | 1.2731 | 1.1071 | 0.020767 | 0.082735 | 119.293 | 119.4093 | -0.16202 | -0.058845 | -0.062371 | -0.29058 | -0.24299 | -0.19828 | -0.3191 | -6.8931 | -6.9722 | 1.3052 | 1.1391 | 0.05281 | 0.11478 | 119.3251 | 119.4414 | -6.9459 | -126.2182 | 1.2524 | -118.0199
1665.2969 | 121.2067 | -117.4393 | 3.7125 | -0.26731 | -0.095467 | -0.085257 | -0.38214 | -0.32997 | -0.28985 | -0.41066 | -9.132 | -9.5592 | 2.8938 | 2.7235 | 0.066548 | 0.12394 | 116.8573 | 117.1569 | -0.23527 | -0.063424 | -0.053214 | -0.3501 | -0.29793 | -0.2578 | -0.37862 | -9.0999 | -9.5272 | 2.9259 | 2.7555 | 0.098591 | 0.15598 | 116.8894 | 117.1889 | -9.1985 | -125.9893 | 2.8273 | -113.9635
1667.0469 | 121.1929 | -116.7709 | 4.1748 | -0.25816 | -0.095467 | -0.071521 | -0.38672 | -0.33455 | -0.28985 | -0.40608 | -9.1274 | -9.55 | 3.5439 | 3.3737 | 0.057392 | 0.11478 | 115.8501 | 115.9436 | -0.22611 | -0.063424 | -0.039478 | -0.35468 | -0.30251 | -0.2578 | -0.37404 | -9.0954 | -9.518 | 3.576 | 3.4057 | 0.089435 | 0.14682 | 115.8821 | 115.9757 | -9.1848 | -124.9775 | 3.4866 | -112.3061
1668.7969 | 121.4447 | -119.7784 | 1.5106 | -0.249 | -0.11378 | -0.10357 | -0.3684 | -0.31624 | -0.28069 | -0.40608 | -4.9427 | -4.8339 | 1.0763 | 0.9056 | 0.075705 | 0.13767 | 119.4533 | 119.7481 | -0.21696 | -0.081739 | -0.071529 | -0.33636 | -0.2842 | -0.24865 | -0.37404 | -4.9106 | -4.8018 | 1.1083 | 0.93764 | 0.10775 | 0.16972 | 119.4853 | 119.7801 | -5.0184 | -124.3959 | 1.0006 | -118.377
1670.5469 | 121.4127 | -119.1147 | 2.1561 | -0.093333 | -0.08173 | -0.080679 | -0.22189 | -0.18348 | -0.1296 | -0.25958 | -7.5799 | -7.5079 | 1.676 | 1.5146 | 0.089439 | 0.13767 | 118.7299 | 118.9103 | -0.06129 | -0.049687 | -0.048636 | -0.18985 | -0.15143 | -0.097558 | -0.22754 | -7.5478 | -7.4758 | 1.7081 | 1.5467 | 0.12148 | 0.16972 | 118.7619 | 118.9423 | -7.6693 | -126.3098 | 1.5866 | -117.0539
1672.2344 | 121.2616 | -119.4214 | 1.8402 | -0.23984 | -0.1321 | -0.10357 | -0.37298 | -0.31166 | -0.26695 | -0.39235 | -6.8885 | -6.8577 | 1.6531 | 1.478 | 0.13522 | 0.18803 | 118.7711 | 118.8737 | -0.2078 | -0.10005 | -0.071529 | -0.34094 | -0.27962 | -0.23491 | -0.3603 | -6.8565 | -6.8256 | 1.6852 | 1.51 | 0.16726 | 0.22007 | 118.8031 | 118.9057 | -7.0237 | -125.6596 | 1.5179 | -117.118
1673.9219 | 121.2936 | -118.0756 | 3.0441 | -0.097912 | -0.08173 | -0.071521 | -0.23563 | -0.19263 | -0.13876 | -0.26416 | -8.958 | -9.1471 | 2.3765 | 2.206 | 0.11233 | 0.16972 | 117.6219 | 117.8665 | -0.065869 | -0.049687 | -0.039478 | -0.20359 | -0.16059 | -0.10671 | -0.23211 | -8.9259 | -9.1151 | 2.4085 | 2.2381 | 0.14437 | 0.20176 | 117.654 | 117.8985 | -9.0703 | -126.5799 | 2.2642 | -115.2454
1675.6719 | 121.1609 | -118.2861 | 2.8519 | -0.12996 | -0.10004 | -0.080679 | -0.25852 | -0.20637 | -0.15707 | -0.28247 | -8.9076 | -9.0326 | 2.3399 | 2.1786 | 0.11691 | 0.16972 | 117.5899 | 117.8665 | -0.097917 | -0.068002 | -0.048636 | -0.22648 | -0.17432 | -0.12503 | -0.25043 | -8.8756 | -9.0006 | 2.3719 | 2.2106 | 0.14895 | 0.20176 | 117.6219 | 117.8985 | -9.0245 | -126.4975 | 2.223 | -115.25
1677.4375 | 121.2479 | -118.6844 | 2.536 | -0.12538 | -0.095467 | -0.089836 | -0.2631 | -0.20637 | -0.16623 | -0.28705 | -8.5642 | -8.5656 | 2.0011 | 1.8351 | 0.1398 | 0.19719 | 118.0889 | 118.3884 | -0.093339 | -0.063424 | -0.057793 | -0.23106 | -0.17432 | -0.13418 | -0.25501 | -8.5322 | -8.5335 | 2.0331 | 1.8672 | 0.17184 | 0.22923 | 118.121 | 118.4204 | -8.704 | -126.6532 | 1.8613 | -116.0879
1679.125 | 121.1609 | -117.6956 | 3.3188 | -0.15743 | -0.10004 | -0.080679 | -0.28141 | -0.22468 | -0.17996 | -0.30994 | -9.1274 | -9.5455 | 2.8664 | 2.6868 | 0.14896 | 0.20176 | 116.8482 | 116.9417 | -0.12539 | -0.068002 | -0.048636 | -0.24937 | -0.19264 | -0.14792 | -0.2779 | -9.0954 | -9.5134 | 2.8984 | 2.7189 | 0.181 | 0.23381 | 116.8802 | 116.9737 | -9.2764 | -125.9756 | 2.7174 | -113.9818
1680.875 | 121.2204 | -118.103 | 3.0121 | -0.15743 | -0.12294 | -0.10815 | -0.28599 | -0.22926 | -0.18912 | -0.3191 | -8.4544 | -8.5335 | 2.024 | 1.8535 | 0.16269 | 0.22465 | 118.0523 | 118.1641 | -0.12539 | -0.090896 | -0.076107 | -0.25395 | -0.19721 | -0.15708 | -0.28705 | -8.4223 | -8.5015 | 2.056 | 1.8855 | 0.19473 | 0.2567 | 118.0843 | 118.1961 | -8.617 | -126.5067 | 1.8613 | -116.0283
1682.5781 | 121.106 | -116.1484 | 4.6692 | -0.23526 | -0.14125 | -0.085257 | -0.36383 | -0.3025 | -0.26238 | -0.38777 | -9.132 | -9.5638 | 3.4386 | 3.2821 | 0.11233 | 0.18345 | 115.8547 | 115.9665 | -0.20322 | -0.10921 | -0.053214 | -0.33178 | -0.27046 | -0.23033 | -0.35573 | -9.0999 | -9.5317 | 3.4707 | 3.3142 | 0.14437 | 0.21549 | 115.8867 | 115.9986 | -9.2443 | -124.9866 | 3.3263 | -112.416
1684.2656 | 120.9183 | -115.6448 | 5.1041 | -0.13454 | -0.10004 | -0.053207 | -0.26768 | -0.21094 | -0.17081 | -0.2962 | -9.132 | -9.5592 | 4.0705 | 3.8911 | 0.11691 | 0.16514 | 114.8795 | 114.9822 | -0.1025 | -0.068002 | -0.021164 | -0.23563 | -0.1789 | -0.13876 | -0.26416 | -9.0999 | -9.5272 | 4.1025 | 3.9232 | 0.14895 | 0.19718 | 114.9115 | 115.0143 | -9.2489 | -124.0114 | 3.9535 | -110.809
1685.9531 | 120.8221 | -114.4592 | 6.0745 | -0.13454 | -0.090888 | -0.034893 | -0.2631 | -0.21094 | -0.16623 | -0.28705 | -9.1274 | -9.5592 | 4.803 | 4.6238 | 0.098596 | 0.15141 | 113.5975 | 113.7232 | -0.1025 | -0.058845 | -0.00285 | -0.23106 | -0.1789 | -0.13418 | -0.25501 | -9.0954 | -9.5272 | 4.835 | 4.6558 | 0.13064 | 0.18345 | 113.6296 | 113.7553 | -9.226 | -122.7249 | 4.7044 | -108.7945
1687.6406 | 120.5704 | -113.4247 | 7.0816 | -0.13912 | -0.086309 | -0.021157 | -0.2631 | -0.21094 | -0.17539 | -0.2962 | -9.132 | -9.5592 | 5.5859 | 5.4022 | 0.089439 | 0.14683 | 112.4529 | 112.5787 | -0.10707 | -0.054266 | 0.010886 | -0.23106 | -0.1789 | -0.14334 | -0.26416 | -9.0999 | -9.5272 | 5.6179 | 5.4343 | 0.12148 | 0.17887 | 112.485 | 112.6107 | -9.2214 | -121.5849 | 5.4964 | -106.8671
1689.3438 | 120.4559 | -113.681 | 6.6971 | -0.25816 | -0.1092 | -0.039471 | -0.37756 | -0.32082 | -0.28527 | -0.41066 | -9.1228 | -9.5592 | 6.0116 | 5.8372 | 0.11233 | 0.16972 | 111.7479 | 111.9973 | -0.22611 | -0.07716 | -0.007428 | -0.34552 | -0.28877 | -0.25322 | -0.37862 | -9.0908 | -9.5272 | 6.0437 | 5.8693 | 0.14437 | 0.20176 | 111.7799 | 112.0293 | -9.2351 | -120.8707 | 5.8993 | -105.7362
1691.0938 | 120.7947 | -115.9653 | 4.5822 | -0.29478 | -0.14125 | -0.085257 | -0.40961 | -0.3666 | -0.32189 | -0.44728 | -9.1274 | -9.5592 | 3.3333 | 3.1676 | 0.098596 | 0.13767 | 115.9188 | 116.1451 | -0.26274 | -0.10921 | -0.053214 | -0.37757 | -0.33455 | -0.28985 | -0.41524 | -9.0954 | -9.5272 | 3.3654 | 3.1997 | 0.13064 | 0.16972 | 115.9508 | 116.1771 | -9.226 | -125.0462 | 3.2348 | -112.5854
1692.8594 | 120.5933 | -115.0314 | 5.4932 | -0.46418 | -0.16415 | -0.12189 | -0.56528 | -0.52682 | -0.47756 | -0.60294 | -9.1366 | -9.5592 | 4.5008 | 4.3307 | 0.1398 | 0.18345 | 113.9409 | 114.1261 | -0.43214 | -0.13211 | -0.089843 | -0.53324 | -0.49478 | -0.44552 | -0.5709 | -9.1045 | -9.5272 | 4.5329 | 4.3628 | 0.17184 | 0.21549 | 113.9729 | 114.1582 | -9.2764 | -123.0775 | 4.361 | -109.4401
1694.5625 | 120.6573 | -114.798 | 5.6259 | -0.55575 | -0.18246 | -0.13562 | -0.66143 | -0.59549 | -0.55997 | -0.68535 | -9.1274 | -9.5546 | 4.2261 | 4.056 | 0.13064 | 0.18345 | 114.4583 | 114.5977 | -0.52371 | -0.15042 | -0.10358 | -0.62938 | -0.56345 | -0.52793 | -0.65331 | -9.0954 | -9.5226 | 4.2582 | 4.088 | 0.16269 | 0.21549 | 114.4903 | 114.6297 | -9.258 | -123.5857 | 4.0955 | -110.2321
1696.25 | 120.4102 | -113.7772 | 6.5781 | -0.57406 | -0.17331 | -0.13562 | -0.68432 | -0.62296 | -0.58744 | -0.70366 | -9.132 | -9.5546 | 5.4073 | 5.2282 | 0.17642 | 0.22008 | 112.3568 | 112.4871 | -0.54202 | -0.14126 | -0.10358 | -0.65228 | -0.59092 | -0.5554 | -0.67162 | -9.0999 | -9.5226 | 5.4394 | 5.2603 | 0.20847 | 0.25212 | 112.3888 | 112.5192 | -9.3084 | -121.4888 | 5.2309 | -106.9495
1698 | 120.5933 | -116.4413 | 4.0878 | -0.29478 | -0.11836 | -0.098993 | -0.42335 | -0.36202 | -0.31732 | -0.44271 | -9.132 | -9.5546 | 3.4478 | 3.2684 | 0.12149 | 0.1743 | 115.493 | 115.6369 | -0.26274 | -0.086318 | -0.06695 | -0.3913 | -0.32998 | -0.28527 | -0.41066 | -9.0999 | -9.5226 | 3.4798 | 3.3004 | 0.15353 | 0.20634 | 115.525 | 115.6689 | -9.2535 | -124.6249 | 3.3263 | -112.0452
1699.6875 | 120.3094 | -113.1363 | 7.1365 | -0.32225 | -0.1092 | -0.071521 | -0.44166 | -0.38949 | -0.34021 | -0.46102 | -9.1366 | -9.5592 | 5.7141 | 5.5442 | 0.16269 | 0.20634 | 111.9676 | 112.2262 | -0.29021 | -0.07716 | -0.039478 | -0.40962 | -0.35744 | -0.30816 | -0.42897 | -9.1045 | -9.5272 | 5.7461 | 5.5762 | 0.19473 | 0.23839 | 111.9997 | 112.2582 | -9.2992 | -121.1042 | 5.5514 | -106.2536
1701.3906 | 120.8038 | -120.6253 | 0.10986 | 0.12643 | -0.008469 | -0.007421 | -0.002124 | 0.040843 | 0.071848 | -0.048983 | -0.25885 | -0.14057 | 0.21096 | 0.17753 | -0.093688 | -0.031717 | 2.8555 | 2.9452 | 0.15847 | 0.023574 | 0.024622 | 0.029919 | 0.072886 | 0.10389 | -0.01694 | -0.22681 | -0.10852 | 0.243 | 0.20958 | -0.061645 | 0.000326 | 2.8875 | 2.9772 | -0.16516 | -3.1143 | 0.30465 | -2.6445
1703.0781 | 121.1563 | -120.8313 | 0.082397 | 0.14474 | -0.00389 | -0.016578 | -0.006703 | 0.040843 | 0.081005 | -0.039826 | -0.011611 | 0.097532 | 0.032407 | 0.021847 | -0.08911 | -0.040873 | -0.024328 | 0.019719 | 0.17679 | 0.028153 | 0.015465 | 0.02534 | 0.072886 | 0.11305 | -0.007783 | 0.020432 | 0.12957 | 0.06445 | 0.05389 | -0.057067 | -0.00883 | 0.007715 | 0.051762 | 0.077499 | 0.012717 | 0.12152 | 0.056735
1704.7656 | 121.1151 | -120.9457 | 0.10986 | 0.14932 | -0.008469 | -0.007421 | -0.002124 | 0.040843 | 0.076426 | -0.039826 | -0.007033 | 0.097532 | 0.041563 | 0.026427 | -0.093688 | -0.040873 | -0.024328 | 0.010563 | 0.18136 | 0.023574 | 0.024622 | 0.029919 | 0.072886 | 0.10847 | -0.007783 | 0.02501 | 0.12957 | 0.073606 | 0.05847 | -0.061645 | -0.00883 | 0.007715 | 0.042606 | 0.086655 | 0.017295 | 0.13525 | 0.065891
1706.4531 | 121.2616 | -120.9595 | 0.059509 | 0.14474 | -0.022205 | -0.012 | -0.002124 | 0.036265 | 0.076426 | -0.044405 | -0.002454 | 0.097532 | 0.041563 | 0.017268 | -0.093688 | -0.040873 | -0.033484 | 0.005985 | 0.17679 | 0.009838 | 0.020043 | 0.029919 | 0.068308 | 0.10847 | -0.012362 | 0.029589 | 0.12957 | 0.073606 | 0.049311 | -0.061645 | -0.00883 | -0.001441 | 0.038028 | 0.091234 | 0.03103 | 0.13525 | 0.075047
1708.2031 | 121.1792 | -121.019 | 0.11444 | 0.14932 | -0.017627 | -0.002842 | -0.002124 | 0.049999 | 0.081005 | -0.044405 | -0.007033 | 0.10211 | 0.036985 | 0.017268 | -0.08911 | -0.036295 | -0.028906 | 0.001406 | 0.18136 | 0.014416 | 0.029201 | 0.029919 | 0.082042 | 0.11305 | -0.012362 | 0.02501 | 0.13415 | 0.069028 | 0.049311 | -0.057067 | -0.004252 | 0.003137 | 0.033449 | 0.082077 | 0.021873 | 0.12609 | 0.065891
1709.9531 | 121.3531 | -121.0144 | 0.082397 | 0.14474 | -0.008469 | -0.007421 | 0.002454 | 0.040843 | 0.081005 | -0.039826 | -0.002454 | 0.10669 | 0.036985 | 0.017268 | -0.093688 | -0.040873 | -0.028906 | -0.003172 | 0.17679 | 0.023574 | 0.024622 | 0.034497 | 0.072886 | 0.11305 | -0.007783 | 0.029589 | 0.13873 | 0.069028 | 0.049311 | -0.061645 | -0.00883 | 0.003137 | 0.028871 | 0.091234 | 0.026452 | 0.13067 | 0.065891
1711.6406 | 121.3531 | -121.0327 | 0.068665 | 0.14474 | -0.013048 | -0.016578 | -0.002124 | 0.040843 | 0.076426 | -0.039826 | -0.007033 | 0.10211 | 0.036985 | 0.017268 | -0.093688 | -0.040873 | -0.028906 | -0.003172 | 0.17679 | 0.018995 | 0.015465 | 0.029919 | 0.072886 | 0.10847 | -0.007783 | 0.02501 | 0.13415 | 0.069028 | 0.049311 | -0.061645 | -0.00883 | 0.003137 | 0.028871 | 0.086655 | 0.021873 | 0.13067 | 0.065891
1713.3281 | 121.2662 | -121.1426 | 0.10986 | 0.14474 | -0.008469 | -0.002842 | -0.011281 | 0.040843 | 0.081005 | -0.044405 | -0.002454 | 0.097532 | 0.032407 | 0.021847 | -0.093688 | -0.031717 | -0.033484 | -0.003172 | 0.17679 | 0.023574 | 0.029201 | 0.020762 | 0.072886 | 0.11305 | -0.012362 | 0.029589 | 0.12957 | 0.06445 | 0.05389 | -0.061645 | 0.000326 | -0.001441 | 0.028871 | 0.091234 | 0.03103 | 0.12609 | 0.065891
1715.0156 | 121.4264 | -121.0876 | 0.054932 | 0.14017 | -0.013048 | -0.012 | -0.002124 | 0.036265 | 0.090161 | -0.039826 | -0.01619 | 0.10211 | 0.036985 | 0.021847 | -0.093688 | -0.036295 | -0.038063 | -0.00775 | 0.17221 | 0.018995 | 0.020043 | 0.029919 | 0.068308 | 0.1222 | -0.007783 | 0.015853 | 0.13415 | 0.069028 | 0.05389 | -0.061645 | -0.004252 | -0.00602 | 0.024293 | 0.077498 | 0.021873 | 0.13067 | 0.075048
1716.7812 | 121.4401 | -121.1472 | 0.068665 | 0.14017 | -0.00389 | -0.016578 | -0.006703 | 0.036265 | 0.085583 | -0.039826 | -0.011611 | 0.097532 | 0.041563 | 0.021847 | -0.098266 | -0.040873 | -0.033484 | -0.003172 | 0.17221 | 0.028153 | 0.015465 | 0.02534 | 0.068308 | 0.11763 | -0.007783 | 0.020432 | 0.12957 | 0.073606 | 0.05389 | -0.066223 | -0.00883 | -0.001441 | 0.028871 | 0.086655 | 0.021873 | 0.13983 | 0.075047
1718.4688 | 121.3257 | -121.1884 | 0.1236 | 0.14932 | -0.013048 | -0.007421 | 0.002454 | 0.027109 | 0.076426 | -0.039826 | -0.007033 | 0.10669 | 0.032407 | 0.017268 | -0.08911 | -0.031717 | -0.038063 | -0.003172 | 0.18136 | 0.018995 | 0.024622 | 0.034497 | 0.059152 | 0.10847 | -0.007783 | 0.02501 | 0.13873 | 0.06445 | 0.049311 | -0.057067 | 0.000326 | -0.00602 | 0.028871 | 0.082077 | 0.03103 | 0.12152 | 0.07047
1720.2188 | 121.3623 | -121.1929 | 0.11902 | 0.14474 | -0.017627 | -0.002842 | -0.006703 | 0.040843 | 0.090161 | -0.039826 | 0.006703 | 0.097532 | 0.041563 | 0.017268 | -0.093688 | -0.040873 | -0.033484 | -0.003172 | 0.17679 | 0.014416 | 0.029201 | 0.02534 | 0.072886 | 0.1222 | -0.007783 | 0.038746 | 0.12957 | 0.073606 | 0.049311 | -0.061645 | -0.00883 | -0.001441 | 0.028871 | 0.10039 | 0.040187 | 0.13525 | 0.075047
1721.9688 | 121.4401 | -121.2341 | 0.09613 | 0.14474 | -0.008469 | -0.012 | -0.002124 | 0.040843 | 0.071848 | -0.044405 | -0.007033 | 0.10211 | 0.036985 | 0.012689 | -0.10284 | -0.040873 | -0.038063 | -0.00775 | 0.17679 | 0.023574 | 0.020043 | 0.029919 | 0.072886 | 0.10389 | -0.012362 | 0.02501 | 0.13415 | 0.069028 | 0.044732 | -0.070801 | -0.00883 | -0.00602 | 0.024293 | 0.095811 | 0.03103 | 0.13983 | 0.075048
1723.6562 | 121.5042 | -121.225 | 0.064087 | 0.14017 | -0.008469 | -0.007421 | 0.002454 | 0.036265 | 0.085583 | -0.035248 | -0.011611 | 0.10211 | 0.041563 | 0.017268 | -0.093688 | -0.036295 | -0.042641 | -0.00775 | 0.17221 | 0.023574 | 0.024622 | 0.034497 | 0.068308 | 0.11763 | -0.003205 | 0.020432 | 0.13415 | 0.073606 | 0.049311 | -0.061645 | -0.004252 | -0.010598 | 0.024293 | 0.082077 | 0.03103 | 0.13525 | 0.084204
1725.3438 | 121.4905 | -121.225 | 0.07782 | 0.1539 | -0.013048 | -0.012 | -0.002124 | 0.045421 | 0.081005 | -0.044405 | -0.007033 | 0.097532 | 0.036985 | 0.017268 | -0.098266 | -0.040873 | -0.038063 | -0.00775 | 0.18594 | 0.018995 | 0.020043 | 0.029919 | 0.077464 | 0.11305 | -0.012362 | 0.02501 | 0.12957 | 0.069028 | 0.049311 | -0.066223 | -0.00883 | -0.00602 | 0.024293 | 0.091233 | 0.03103 | 0.13525 | 0.075048
1727.0938 | 121.5546 | -121.2433 | 0.082397 | 0.14017 | -0.008469 | -0.021157 | -0.006703 | 0.045421 | 0.076426 | -0.035248 | -0.011611 | 0.10669 | 0.036985 | 0.012689 | -0.08911 | -0.031717 | -0.042641 | -0.003172 | 0.17221 | 0.023574 | 0.010886 | 0.02534 | 0.077464 | 0.10847 | -0.003205 | 0.020432 | 0.13873 | 0.069028 | 0.044732 | -0.057067 | 0.000326 | -0.010598 | 0.028871 | 0.077499 | 0.03103 | 0.12609 | 0.079626
1728.7812 | 121.4584 | -121.2845 | 0.10529 | 0.14474 | -0.013048 | -0.012 | -0.011281 | 0.040843 | 0.085583 | -0.035248 | 0.006703 | 0.10211 | 0.036985 | 0.017268 | -0.093688 | -0.040873 | -0.038063 | 0.001406 | 0.17679 | 0.018995 | 0.020043 | 0.020762 | 0.072886 | 0.11763 | -0.003205 | 0.038746 | 0.13415 | 0.069028 | 0.049311 | -0.061645 | -0.00883 | -0.00602 | 0.033449 | 0.10039 | 0.044766 | 0.13067 | 0.075048
1730.4688 | 121.4905 | -121.2891 | 0.10986 | 0.14932 | -0.013048 | -0.012 | -0.002124 | 0.040843 | 0.085583 | -0.039826 | -0.002454 | 0.10211 | 0.032407 | 0.017268 | -0.098266 | -0.040873 | -0.028906 | 0.001406 | 0.18136 | 0.018995 | 0.020043 | 0.029919 | 0.072886 | 0.11763 | -0.007783 | 0.029589 | 0.13415 | 0.06445 | 0.049311 | -0.066223 | -0.00883 | 0.003137 | 0.033449 | 0.095812 | 0.026452 | 0.13067 | 0.061313
1732.2344 | 121.582 | -121.2708 | 0.073242 | 0.14474 | -0.013048 | -0.007421 | -0.002124 | 0.040843 | 0.071848 | -0.044405 | -0.007033 | 0.10211 | 0.036985 | 0.017268 | -0.098266 | -0.040873 | -0.033484 | 0.001406 | 0.17679 | 0.018995 | 0.024622 | 0.029919 | 0.072886 | 0.10389 | -0.012362 | 0.02501 | 0.13415 | 0.069028 | 0.049311 | -0.066223 | -0.00883 | -0.001441 | 0.033449 | 0.091233 | 0.026451 | 0.13525 | 0.070469
1733.9844 | 121.5591 | -121.2936 | 0.09613 | 0.14474 | -0.017627 | -0.012 | -0.002124 | 0.045421 | 0.076426 | -0.039826 | 0.002124 | 0.097532 | 0.032407 | 0.012689 | -0.098266 | -0.036295 | -0.038063 | -0.003172 | 0.17679 | 0.014416 | 0.020043 | 0.029919 | 0.077464 | 0.10847 | -0.007783 | 0.034167 | 0.12957 | 0.06445 | 0.044732 | -0.066223 | -0.004252 | -0.00602 | 0.028871 | 0.10039 | 0.040187 | 0.13067 | 0.07047
1735.7344 | 121.5271 | -121.3623 | 0.10529 | 0.14932 | -0.017627 | -0.016578 | -0.002124 | 0.045421 | 0.081005 | -0.035248 | -0.007033 | 0.10211 | 0.036985 | 0.017268 | -0.08911 | -0.036295 | -0.038063 | -0.00775 | 0.18136 | 0.014416 | 0.015465 | 0.029919 | 0.077464 | 0.11305 | -0.003205 | 0.02501 | 0.13415 | 0.069028 | 0.049311 | -0.057067 | -0.004252 | -0.00602 | 0.024293 | 0.082077 | 0.03103 | 0.12609 | 0.075048
1737.4375 | 121.5088 | -121.344 | 0.11444 | 0.14474 | -0.022205 | -0.002842 | 0.002454 | 0.045421 | 0.081005 | -0.039826 | -0.002454 | 0.10669 | 0.032407 | 0.017268 | -0.098266 | -0.031717 | -0.038063 | -0.00775 | 0.17679 | 0.009838 | 0.029201 | 0.034497 | 0.077464 | 0.11305 | -0.007783 | 0.029589 | 0.13873 | 0.06445 | 0.049311 | -0.066223 | 0.000326 | -0.00602 | 0.024293 | 0.095812 | 0.035609 | 0.13067 | 0.07047
1739.1875 | 121.6324 | -121.3257 | 0.09613 | 0.14017 | -0.008469 | -0.012 | -0.002124 | 0.045421 | 0.076426 | -0.035248 | -0.002454 | 0.10211 | 0.032407 | 0.017268 | -0.08911 | -0.036295 | -0.042641 | 0.001406 | 0.17221 | 0.023574 | 0.020043 | 0.029919 | 0.077464 | 0.10847 | -0.003205 | 0.029589 | 0.13415 | 0.06445 | 0.049311 | -0.057067 | -0.004252 | -0.010598 | 0.033449 | 0.086656 | 0.040187 | 0.12152 | 0.075048
1740.875 | 121.6415 | -121.3394 | 0.073242 | 0.14932 | -0.017627 | -0.016578 | -0.006703 | 0.045421 | 0.076426 | -0.044405 | -0.007033 | 0.097532 | 0.032407 | 0.021847 | -0.093688 | -0.036295 | -0.042641 | -0.00775 | 0.18136 | 0.014416 | 0.015465 | 0.02534 | 0.077464 | 0.10847 | -0.012362 | 0.02501 | 0.12957 | 0.06445 | 0.05389 | -0.061645 | -0.004252 | -0.010598 | 0.024293 | 0.086655 | 0.035608 | 0.12609 | 0.075048
1742.625 | 121.5408 | -121.376 | 0.10529 | 0.14017 | -0.013048 | -0.012 | -0.006703 | 0.045421 | 0.081005 | -0.039826 | -0.011611 | 0.10211 | 0.036985 | 0.012689 | -0.093688 | -0.040873 | -0.042641 | -0.016906 | 0.17221 | 0.018995 | 0.020043 | 0.02534 | 0.077464 | 0.11305 | -0.007783 | 0.020432 | 0.13415 | 0.069028 | 0.044732 | -0.061645 | -0.00883 | -0.010598 | 0.015137 | 0.082077 | 0.03103 | 0.13067 | 0.079626
1744.3594 | 121.7056 | -121.3715 | 0.09613 | 0.14474 | -0.022205 | -0.007421 | -0.011281 | 0.045421 | 0.081005 | -0.039826 | -0.002454 | 0.10211 | 0.027829 | 0.021847 | -0.093688 | -0.031717 | -0.033484 | -0.00775 | 0.17679 | 0.009838 | 0.024622 | 0.020762 | 0.077464 | 0.11305 | -0.007783 | 0.029589 | 0.13415 | 0.059872 | 0.05389 | -0.061645 | 0.000326 | -0.001441 | 0.024293 | 0.091234 | 0.03103 | 0.12152 | 0.061313
1746.0625 | 121.6507 | -121.3852 | 0.086975 | 0.14474 | -0.013048 | -0.012 | -0.002124 | 0.045421 | 0.085583 | -0.044405 | 0.002124 | 0.097532 | 0.032407 | 0.017268 | -0.093688 | -0.040873 | -0.042641 | -0.016906 | 0.17679 | 0.018995 | 0.020043 | 0.029919 | 0.077464 | 0.11763 | -0.012362 | 0.034167 | 0.12957 | 0.06445 | 0.049311 | -0.061645 | -0.00883 | -0.010598 | 0.015137 | 0.095812 | 0.044765 | 0.12609 | 0.075048
1747.8125 | 121.6553 | -121.3943 | 0.07782 | 0.14474 | -0.013048 | -0.012 | -0.002124 | 0.036265 | 0.081005 | -0.044405 | -0.007033 | 0.10211 | 0.046142 | 0.021847 | -0.093688 | -0.040873 | -0.042641 | -0.012328 | 0.17679 | 0.018995 | 0.020043 | 0.029919 | 0.068308 | 0.11305 | -0.012362 | 0.02501 | 0.13415 | 0.078185 | 0.05389 | -0.061645 | -0.00883 | -0.010598 | 0.019715 | 0.086655 | 0.035608 | 0.13983 | 0.088783
1749.5 | 121.7148 | -121.3852 | 0.082397 | 0.14474 | -0.017627 | -0.016578 | -0.006703 | 0.040843 | 0.071848 | -0.035248 | 0.002124 | 0.10669 | 0.036985 | 0.00811 | -0.093688 | -0.031717 | -0.042641 | -0.003172 | 0.17679 | 0.014416 | 0.015465 | 0.02534 | 0.072886 | 0.10389 | -0.003205 | 0.034167 | 0.13873 | 0.069028 | 0.040153 | -0.061645 | 0.000326 | -0.010598 | 0.028871 | 0.095812 | 0.044765 | 0.13067 | 0.079626
1751.1875 | 121.5866 | -121.4447 | 0.10529 | 0.14932 | -0.008469 | -0.002842 | -0.002124 | 0.045421 | 0.081005 | -0.039826 | -0.007033 | 0.10669 | 0.041563 | 0.017268 | -0.08911 | -0.031717 | -0.04722 | -0.003172 | 0.18136 | 0.023574 | 0.029201 | 0.029919 | 0.077464 | 0.11305 | -0.007783 | 0.02501 | 0.13873 | 0.073606 | 0.049311 | -0.057067 | 0.000326 | -0.015177 | 0.028871 | 0.082077 | 0.040187 | 0.13067 | 0.088783
1752.9531 | 121.7102 | -121.4218 | 0.082397 | 0.14017 | -0.022205 | -0.007421 | -0.006703 | 0.040843 | 0.076426 | -0.044405 | -0.007033 | 0.097532 | 0.036985 | 0.012689 | -0.093688 | -0.036295 | -0.04722 | -0.012328 | 0.17221 | 0.009838 | 0.024622 | 0.02534 | 0.072886 | 0.10847 | -0.012362 | 0.02501 | 0.12957 | 0.069028 | 0.044732 | -0.061645 | -0.004252 | -0.015177 | 0.019715 | 0.086655 | 0.040187 | 0.13067 | 0.084205
1754.7031 | 121.6553 | -121.463 | 0.10986 | 0.13559 | -0.022205 | -0.007421 | -0.006703 | 0.045421 | 0.085583 | -0.044405 | -0.002454 | 0.10669 | 0.036985 | 0.026427 | -0.10284 | -0.036295 | -0.04722 | -0.00775 | 0.16763 | 0.009838 | 0.024622 | 0.02534 | 0.077464 | 0.11763 | -0.012362 | 0.029589 | 0.13873 | 0.069028 | 0.05847 | -0.070801 | -0.004252 | -0.015177 | 0.024293 | 0.10039 | 0.044766 | 0.13983 | 0.084205
1756.3906 | 121.6599 | -121.463 | 0.11444 | 0.13559 | -0.013048 | -0.016578 | 0.002454 | 0.036265 | 0.081005 | -0.039826 | 0.002124 | 0.11127 | 0.032407 | 0.012689 | -0.093688 | -0.040873 | -0.042641 | -0.00775 | 0.16763 | 0.018995 | 0.015465 | 0.034497 | 0.068308 | 0.11305 | -0.007783 | 0.034167 | 0.14331 | 0.06445 | 0.044732 | -0.061645 | -0.00883 | -0.010598 | 0.024293 | 0.095812 | 0.044765 | 0.12609 | 0.075048
1758.1406 | 121.7056 | -121.4493 | 0.09613 | 0.14017 | -0.022205 | -0.016578 | -0.006703 | 0.040843 | 0.076426 | -0.035248 | 0.006703 | 0.10211 | 0.041563 | 0.017268 | -0.093688 | -0.036295 | -0.04722 | -0.003172 | 0.17221 | 0.009838 | 0.015465 | 0.02534 | 0.072886 | 0.10847 | -0.003205 | 0.038746 | 0.13415 | 0.073606 | 0.049311 | -0.061645 | -0.004252 | -0.015177 | 0.028871 | 0.10039 | 0.053923 | 0.13525 | 0.088783
1759.8281 | 121.669 | -121.463 | 0.09613 | 0.14017 | -0.008469 | -0.007421 | 0.002454 | 0.040843 | 0.076426 | -0.035248 | -0.011611 | 0.11127 | 0.046142 | 0.021847 | -0.08911 | -0.036295 | -0.04722 | -0.012328 | 0.17221 | 0.023574 | 0.024622 | 0.034497 | 0.072886 | 0.10847 | -0.003205 | 0.020432 | 0.14331 | 0.078185 | 0.05389 | -0.057067 | -0.004252 | -0.015177 | 0.019715 | 0.077499 | 0.035609 | 0.13525 | 0.093362
1761.5156 | 121.6599 | -121.4905 | 0.1236 | 0.14017 | -0.017627 | -0.016578 | -0.006703 | 0.040843 | 0.076426 | -0.035248 | 0.002124 | 0.11127 | 0.032407 | 0.017268 | -0.10284 | -0.031717 | -0.042641 | -0.003172 | 0.17221 | 0.014416 | 0.015465 | 0.02534 | 0.072886 | 0.10847 | -0.003205 | 0.034167 | 0.14331 | 0.06445 | 0.049311 | -0.070801 | 0.000326 | -0.010598 | 0.028871 | 0.10497 | 0.044765 | 0.13525 | 0.075048
1763.2188 | 121.6507 | -121.4996 | 0.10986 | 0.14017 | -0.013048 | 0.001736 | 0.002454 | 0.040843 | 0.076426 | -0.039826 | 0.002124 | 0.10669 | 0.036985 | 0.017268 | -0.093688 | -0.040873 | -0.056376 | -0.012328 | 0.17221 | 0.018995 | 0.033779 | 0.034497 | 0.072886 | 0.10847 | -0.007783 | 0.034167 | 0.13873 | 0.069028 | 0.049311 | -0.061645 | -0.00883 | -0.024333 | 0.019715 | 0.095812 | 0.0585 | 0.13067 | 0.093361
1764.9688 | 121.7606 | -121.4859 | 0.09613 | 0.14474 | -0.017627 | -0.007421 | -0.006703 | 0.036265 | 0.081005 | -0.048983 | 0.011281 | 0.10669 | 0.036985 | 0.021847 | -0.093688 | -0.040873 | -0.038063 | -0.00775 | 0.17679 | 0.014416 | 0.024622 | 0.02534 | 0.068308 | 0.11305 | -0.01694 | 0.043324 | 0.13873 | 0.069028 | 0.05389 | -0.061645 | -0.00883 | -0.00602 | 0.024293 | 0.10497 | 0.049344 | 0.13067 | 0.075048
1766.7188 | 121.669 | -121.5271 | 0.12817 | 0.13559 | -0.017627 | -0.007421 | 0.002454 | 0.036265 | 0.081005 | -0.035248 | 0.002124 | 0.10211 | 0.036985 | 0.017268 | -0.093688 | -0.040873 | -0.042641 | -0.00775 | 0.16763 | 0.014416 | 0.024622 | 0.034497 | 0.068308 | 0.11305 | -0.003205 | 0.034167 | 0.13415 | 0.069028 | 0.049311 | -0.061645 | -0.00883 | -0.010598 | 0.024293 | 0.095812 | 0.044765 | 0.13067 | 0.079626
1768.4062 | 121.7239 | -121.5134 | 0.11902 | 0.14017 | -0.013048 | -0.012 | -0.002124 | 0.045421 | 0.081005 | -0.044405 | -0.002454 | 0.10211 | 0.032407 | 0.021847 | -0.093688 | -0.036295 | -0.04722 | -0.016906 | 0.17221 | 0.018995 | 0.020043 | 0.029919 | 0.077464 | 0.11305 | -0.012362 | 0.029589 | 0.13415 | 0.06445 | 0.05389 | -0.061645 | -0.004252 | -0.015177 | 0.015137 | 0.091234 | 0.044766 | 0.12609 | 0.079627
1770.1562 | 121.6782 | -121.5546 | 0.12817 | 0.14474 | -0.013048 | -0.007421 | 0.002454 | 0.036265 | 0.081005 | -0.035248 | -0.007033 | 0.10211 | 0.032407 | 0.012689 | -0.084531 | -0.031717 | -0.04722 | -0.003172 | 0.17679 | 0.018995 | 0.024622 | 0.034497 | 0.068308 | 0.11305 | -0.003205 | 0.02501 | 0.13415 | 0.06445 | 0.044732 | -0.052488 | 0.000326 | -0.015177 | 0.028871 | 0.077498 | 0.040187 | 0.11694 | 0.079627
1771.9219 | 121.7331 | -121.5408 | 0.11444 | 0.14474 | -0.013048 | -0.007421 | -0.002124 | 0.049999 | 0.076426 | -0.035248 | -0.002454 | 0.10211 | 0.036985 | 0.026427 | -0.084531 | -0.040873 | -0.038063 | -0.016906 | 0.17679 | 0.018995 | 0.024622 | 0.029919 | 0.082042 | 0.10847 | -0.003205 | 0.029589 | 0.13415 | 0.069028 | 0.05847 | -0.052488 | -0.00883 | -0.00602 | 0.015137 | 0.082077 | 0.035609 | 0.12152 | 0.075048
1773.6875 | 121.7102 | -121.5912 | 0.11902 | 0.13559 | -0.008469 | -0.007421 | 0.011611 | 0.049999 | 0.071848 | -0.039826 | -0.002454 | 0.10211 | 0.041563 | 0.021847 | -0.08911 | -0.036295 | -0.051798 | -0.012328 | 0.16763 | 0.023574 | 0.024622 | 0.043654 | 0.082042 | 0.10389 | -0.007783 | 0.029589 | 0.13415 | 0.073606 | 0.05389 | -0.057067 | -0.004252 | -0.019755 | 0.019715 | 0.086656 | 0.049344 | 0.13067 | 0.093361
1775.375 | 121.843 | -121.5179 | 0.082397 | 0.14474 | -0.008469 | -0.016578 | 0.002454 | 0.040843 | 0.076426 | -0.048983 | -0.007033 | 0.10669 | 0.032407 | 0.021847 | -0.098266 | -0.040873 | -0.038063 | -0.00775 | 0.17679 | 0.023574 | 0.015465 | 0.034497 | 0.072886 | 0.10847 | -0.01694 | 0.02501 | 0.13873 | 0.06445 | 0.05389 | -0.066223 | -0.00883 | -0.00602 | 0.024293 | 0.091233 | 0.03103 | 0.13067 | 0.07047
1777.125 | 121.843 | -121.5225 | 0.082397 | 0.14474 | -0.013048 | -0.012 | -0.002124 | 0.045421 | 0.085583 | -0.039826 | 0.002124 | 0.10669 | 0.041563 | 0.012689 | -0.093688 | -0.036295 | -0.033484 | -0.00775 | 0.17679 | 0.018995 | 0.020043 | 0.029919 | 0.077464 | 0.11763 | -0.007783 | 0.034167 | 0.13873 | 0.073606 | 0.044732 | -0.061645 | -0.004252 | -0.001441 | 0.024293 | 0.095812 | 0.035608 | 0.13525 | 0.075047
1778.875 | 121.8521 | -121.5271 | 0.059509 | 0.14474 | -0.013048 | -0.012 | -0.006703 | 0.040843 | 0.076426 | -0.039826 | 0.006703 | 0.10211 | 0.046142 | 0.017268 | -0.093688 | -0.036295 | -0.042641 | -0.012328 | 0.17679 | 0.018995 | 0.020043 | 0.02534 | 0.072886 | 0.10847 | -0.007783 | 0.038746 | 0.13415 | 0.078185 | 0.049311 | -0.061645 | -0.004252 | -0.010598 | 0.019715 | 0.10039 | 0.049344 | 0.13983 | 0.088783
1780.625 | 121.7651 | -121.5683 | 0.09613 | 0.14017 | -0.013048 | -0.007421 | 0.002454 | 0.045421 | 0.081005 | -0.044405 | -0.002454 | 0.10669 | 0.032407 | 0.012689 | -0.098266 | -0.040873 | -0.033484 | -0.012328 | 0.17221 | 0.018995 | 0.024622 | 0.034497 | 0.077464 | 0.11305 | -0.012362 | 0.029589 | 0.13873 | 0.06445 | 0.044732 | -0.066223 | -0.00883 | -0.001441 | 0.019715 | 0.095812 | 0.03103 | 0.13067 | 0.065891
1782.3281 | 121.7606 | -121.5866 | 0.10071 | 0.14017 | -0.013048 | -0.012 | -0.002124 | 0.049999 | 0.085583 | -0.044405 | -0.002454 | 0.11127 | 0.036985 | 0.017268 | -0.08911 | -0.036295 | -0.038063 | -0.012328 | 0.17221 | 0.018995 | 0.020043 | 0.029919 | 0.082042 | 0.11763 | -0.012362 | 0.029589 | 0.14331 | 0.069028 | 0.049311 | -0.057067 | -0.004252 | -0.00602 | 0.019715 | 0.086656 | 0.035609 | 0.12609 | 0.075048
1784.0938 | 121.8155 | -121.5958 | 0.086975 | 0.14017 | -0.013048 | -0.012 | 0.002454 | 0.040843 | 0.076426 | -0.044405 | -0.002454 | 0.10211 | 0.027829 | 0.021847 | -0.093688 | -0.036295 | -0.042641 | -0.012328 | 0.17221 | 0.018995 | 0.020043 | 0.034497 | 0.072886 | 0.10847 | -0.012362 | 0.029589 | 0.13415 | 0.059872 | 0.05389 | -0.061645 | -0.004252 | -0.010598 | 0.019715 | 0.091234 | 0.040187 | 0.12152 | 0.07047
1785.8438 | 121.7377 | -121.6003 | 0.10986 | 0.14474 | -0.008469 | -0.007421 | 0.002454 | 0.036265 | 0.071848 | -0.039826 | -0.007033 | 0.11127 | 0.027829 | 0.017268 | -0.093688 | -0.040873 | -0.042641 | -0.00775 | 0.17679 | 0.023574 | 0.024622 | 0.034497 | 0.068308 | 0.10389 | -0.007783 | 0.02501 | 0.14331 | 0.059872 | 0.049311 | -0.061645 | -0.00883 | -0.010598 | 0.024293 | 0.086655 | 0.035608 | 0.12152 | 0.07047
1787.6094 | 121.7514 | -121.5958 | 0.10529 | 0.14474 | -0.00389 | -0.002842 | -0.002124 | 0.040843 | 0.076426 | -0.044405 | 0.002124 | 0.11585 | 0.036985 | 0.021847 | -0.093688 | -0.031717 | -0.038063 | -0.016906 | 0.17679 | 0.028153 | 0.029201 | 0.029919 | 0.072886 | 0.10847 | -0.012362 | 0.034167 | 0.14789 | 0.069028 | 0.05389 | -0.061645 | 0.000326 | -0.00602 | 0.015137 | 0.095812 | 0.040187 | 0.13067 | 0.075048
1789.3125 | 121.7926 | -121.6049 | 0.11902 | 0.14932 | 0.000689 | -0.012 | -0.006703 | 0.040843 | 0.081005 | -0.039826 | -0.002454 | 0.10669 | 0.032407 | 0.021847 | -0.08911 | -0.031717 | -0.038063 | -0.003172 | 0.18136 | 0.032732 | 0.020043 | 0.02534 | 0.072886 | 0.11305 | -0.007783 | 0.029589 | 0.13873 | 0.06445 | 0.05389 | -0.057067 | 0.000326 | -0.00602 | 0.028871 | 0.086656 | 0.035609 | 0.12152 | 0.07047
1791.0625 | 121.907 | -121.5775 | 0.086975 | 0.14017 | -0.00389 | -0.012 | -0.002124 | 0.040843 | 0.076426 | -0.039826 | 0.002124 | 0.10211 | 0.036985 | 0.017268 | -0.093688 | -0.027139 | -0.038063 | -0.012328 | 0.17221 | 0.028153 | 0.020043 | 0.029919 | 0.072886 | 0.10847 | -0.007783 | 0.034167 | 0.13415 | 0.069028 | 0.049311 | -0.061645 | 0.004904 | -0.00602 | 0.019715 | 0.095812 | 0.040187 | 0.13067 | 0.075048
1792.75 | 121.8063 | -121.6141 | 0.086975 | 0.14017 | -0.00389 | -0.007421 | -0.002124 | 0.045421 | 0.085583 | -0.044405 | 0.002124 | 0.10669 | 0.032407 | 0.021847 | -0.098266 | -0.036295 | -0.04722 | -0.012328 | 0.17221 | 0.028153 | 0.024622 | 0.029919 | 0.077464 | 0.11763 | -0.012362 | 0.034167 | 0.13873 | 0.06445 | 0.05389 | -0.066223 | -0.004252 | -0.015177 | 0.019715 | 0.10039 | 0.049344 | 0.13067 | 0.079627
1794.4531 | 121.9116 | -121.5866 | 0.068665 | 0.14017 | -0.00389 | -0.016578 | -0.002124 | 0.045421 | 0.085583 | -0.039826 | 0.002124 | 0.11127 | 0.036985 | 0.021847 | -0.08911 | -0.036295 | -0.04722 | -0.012328 | 0.17221 | 0.028153 | 0.015465 | 0.029919 | 0.077464 | 0.11763 | -0.007783 | 0.034167 | 0.14331 | 0.069028 | 0.05389 | -0.057067 | -0.004252 | -0.015177 | 0.019715 | 0.091234 | 0.049344 | 0.12609 | 0.084205
1796.2031 | 121.843 | -121.6095 | 0.07782 | 0.14017 | -0.008469 | -0.012 | 0.002454 | 0.040843 | 0.085583 | -0.048983 | 0.006703 | 0.11127 | 0.032407 | 0.021847 | -0.08911 | -0.040873 | -0.042641 | -0.012328 | 0.17221 | 0.023574 | 0.020043 | 0.034497 | 0.072886 | 0.11763 | -0.01694 | 0.038746 | 0.14331 | 0.06445 | 0.05389 | -0.057067 | -0.00883 | -0.010598 | 0.019715 | 0.095813 | 0.049344 | 0.12152 | 0.075048
1797.9688 | 121.907 | -121.5958 | 0.068665 | 0.14474 | -0.008469 | -0.007421 | -0.002124 | 0.040843 | 0.081005 | -0.044405 | -0.007033 | 0.10669 | 0.032407 | 0.021847 | -0.079953 | -0.036295 | -0.04722 | -0.012328 | 0.17679 | 0.023574 | 0.024622 | 0.029919 | 0.072886 | 0.11305 | -0.012362 | 0.02501 | 0.13873 | 0.06445 | 0.05389 | -0.04791 | -0.004252 | -0.015177 | 0.019715 | 0.07292 | 0.040187 | 0.11236 | 0.079627
1799.7188 | 121.9116 | -121.582 | 0.082397 | 0.14474 | -0.008469 | -0.007421 | -0.006703 | 0.040843 | 0.076426 | -0.044405 | 0.006703 | 0.10669 | 0.032407 | 0.021847 | -0.093688 | -0.036295 | -0.038063 | -0.00775 | 0.17679 | 0.023574 | 0.024622 | 0.02534 | 0.072886 | 0.10847 | -0.012362 | 0.038746 | 0.13873 | 0.06445 | 0.05389 | -0.061645 | -0.004252 | -0.00602 | 0.024293 | 0.10039 | 0.044766 | 0.12609 | 0.07047
1801.4531 | 121.7651 | -121.6644 | 0.10529 | 0.14932 | -0.013048 | -0.012 | 0.002454 | 0.045421 | 0.081005 | -0.048983 | 0.002124 | 0.10211 | 0.032407 | 0.012689 | -0.093688 | -0.040873 | -0.04722 | -0.012328 | 0.18136 | 0.018995 | 0.020043 | 0.034497 | 0.077464 | 0.11305 | -0.01694 | 0.034167 | 0.13415 | 0.06445 | 0.044732 | -0.061645 | -0.00883 | -0.015177 | 0.019715 | 0.095812 | 0.049344 | 0.12609 | 0.079627
1803.1406 | 121.9254 | -121.6049 | 0.068665 | 0.14017 | -0.013048 | -0.007421 | -0.002124 | 0.045421 | 0.081005 | -0.044405 | -0.002454 | 0.11127 | 0.036985 | 0.021847 | -0.084531 | -0.040873 | -0.04722 | -0.00775 | 0.17221 | 0.018995 | 0.024622 | 0.029919 | 0.077464 | 0.11305 | -0.012362 | 0.029589 | 0.14331 | 0.069028 | 0.05389 | -0.052488 | -0.00883 | -0.015177 | 0.024293 | 0.082077 | 0.044766 | 0.12152 | 0.084205
1804.8906 | 121.8887 | -121.6461 | 0.082397 | 0.13559 | -0.022205 | -0.007421 | -0.002124 | 0.027109 | 0.076426 | -0.039826 | 0.002124 | 0.10669 | 0.032407 | 0.017268 | -0.08911 | -0.036295 | -0.04722 | -0.012328 | 0.16763 | 0.009838 | 0.024622 | 0.029919 | 0.059152 | 0.10847 | -0.007783 | 0.034167 | 0.13873 | 0.06445 | 0.049311 | -0.057067 | -0.004252 | -0.015177 | 0.019715 | 0.091234 | 0.049344 | 0.12152 | 0.079627
1806.6406 | 121.7972 | -121.6782 | 0.11444 | 0.14932 | -0.013048 | -0.012 | -0.011281 | 0.040843 | 0.081005 | -0.044405 | -0.002454 | 0.10211 | 0.027829 | 0.017268 | -0.08911 | -0.036295 | -0.042641 | -0.012328 | 0.18136 | 0.018995 | 0.020043 | 0.020762 | 0.072886 | 0.11305 | -0.012362 | 0.029589 | 0.13415 | 0.059872 | 0.049311 | -0.057067 | -0.004252 | -0.010598 | 0.019715 | 0.086656 | 0.040187 | 0.11694 | 0.07047
1808.3906 | 121.8063 | -121.6827 | 0.11902 | 0.14474 | -0.017627 | -0.016578 | -0.006703 | 0.040843 | 0.076426 | -0.039826 | 0.002124 | 0.10211 | 0.027829 | 0.021847 | -0.08911 | -0.036295 | -0.042641 | -0.00775 | 0.17679 | 0.014416 | 0.015465 | 0.02534 | 0.072886 | 0.10847 | -0.007783 | 0.034167 | 0.13415 | 0.059872 | 0.05389 | -0.057067 | -0.004252 | -0.010598 | 0.024293 | 0.091234 | 0.044765 | 0.11694 | 0.07047
1810.0781 | 121.9391 | -121.6141 | 0.073242 | 0.14017 | -0.008469 | -0.007421 | -0.006703 | 0.040843 | 0.081005 | -0.039826 | 0.006703 | 0.10669 | 0.027829 | 0.012689 | -0.084531 | -0.027139 | -0.042641 | -0.012328 | 0.17221 | 0.023574 | 0.024622 | 0.02534 | 0.072886 | 0.11305 | -0.007783 | 0.038746 | 0.13873 | 0.059872 | 0.044732 | -0.052488 | 0.004904 | -0.010598 | 0.019715 | 0.091234 | 0.049344 | 0.11236 | 0.07047
1811.8281 | 121.8796 | -121.637 | 0.10529 | 0.14474 | -0.013048 | -0.007421 | -0.006703 | 0.036265 | 0.085583 | -0.035248 | 0.002124 | 0.11585 | 0.032407 | 0.012689 | -0.093688 | -0.036295 | -0.04722 | -0.00775 | 0.17679 | 0.018995 | 0.024622 | 0.02534 | 0.068308 | 0.11763 | -0.003205 | 0.034167 | 0.14789 | 0.06445 | 0.044732 | -0.061645 | -0.004252 | -0.015177 | 0.024293 | 0.095812 | 0.049344 | 0.12609 | 0.079627
1813.5938 | 121.8246 | -121.6827 | 0.11902 | 0.14474 | -0.013048 | -0.012 | 0.002454 | 0.040843 | 0.076426 | -0.039826 | 0.002124 | 0.10211 | 0.036985 | 0.012689 | -0.079953 | -0.036295 | -0.038063 | -0.003172 | 0.17679 | 0.018995 | 0.020043 | 0.034497 | 0.072886 | 0.10847 | -0.007783 | 0.034167 | 0.13415 | 0.069028 | 0.044732 | -0.04791 | -0.004252 | -0.00602 | 0.028871 | 0.082077 | 0.040187 | 0.11694 | 0.075048
1815.2812 | 121.8475 | -121.6827 | 0.086975 | 0.14474 | -0.013048 | -0.002842 | -0.002124 | 0.045421 | 0.085583 | -0.039826 | -0.007033 | 0.10211 | 0.036985 | 0.021847 | -0.084531 | -0.036295 | -0.04722 | -0.016906 | 0.17679 | 0.018995 | 0.029201 | 0.029919 | 0.077464 | 0.11763 | -0.007783 | 0.02501 | 0.13415 | 0.069028 | 0.05389 | -0.052488 | -0.004252 | -0.015177 | 0.015137 | 0.077498 | 0.040187 | 0.12152 | 0.084205
1817.0312 | 121.9254 | -121.6827 | 0.091553 | 0.14017 | -0.017627 | -0.007421 | -0.002124 | 0.040843 | 0.081005 | -0.044405 | -0.002454 | 0.11127 | 0.036985 | 0.012689 | -0.08911 | -0.040873 | -0.042641 | -0.012328 | 0.17221 | 0.014416 | 0.024622 | 0.029919 | 0.072886 | 0.11305 | -0.012362 | 0.029589 | 0.14331 | 0.069028 | 0.044732 | -0.057067 | -0.00883 | -0.010598 | 0.019715 | 0.086656 | 0.040187 | 0.12609 | 0.079626
1818.7812 | 121.8842 | -121.6599 | 0.09613 | 0.13559 | -0.013048 | -0.012 | -0.002124 | 0.036265 | 0.085583 | -0.039826 | 0.002124 | 0.10669 | 0.041563 | 0.017268 | -0.093688 | -0.036295 | -0.051798 | -0.016906 | 0.16763 | 0.018995 | 0.020043 | 0.029919 | 0.068308 | 0.11763 | -0.007783 | 0.034167 | 0.13873 | 0.073606 | 0.049311 | -0.061645 | -0.004252 | -0.019755 | 0.015137 | 0.095812 | 0.053922 | 0.13525 | 0.093361
1820.5312 | 121.9757 | -121.6507 | 0.07782 | 0.14017 | -0.013048 | -0.016578 | -0.002124 | 0.040843 | 0.076426 | -0.039826 | 0.002124 | 0.10669 | 0.041563 | 0.012689 | -0.093688 | -0.036295 | -0.042641 | -0.012328 | 0.17221 | 0.018995 | 0.015465 | 0.029919 | 0.072886 | 0.10847 | -0.007783 | 0.034167 | 0.13873 | 0.073606 | 0.044732 | -0.061645 | -0.004252 | -0.010598 | 0.019715 | 0.095812 | 0.044765 | 0.13525 | 0.084204
1822.2188 | 121.9345 | -121.6644 | 0.082397 | 0.13559 | -0.013048 | -0.012 | -0.002124 | 0.031687 | 0.071848 | -0.039826 | 0.006703 | 0.10669 | 0.036985 | 0.021847 | -0.093688 | -0.036295 | -0.042641 | -0.00775 | 0.16763 | 0.018995 | 0.020043 | 0.029919 | 0.06373 | 0.10389 | -0.007783 | 0.038746 | 0.13873 | 0.069028 | 0.05389 | -0.061645 | -0.004252 | -0.010598 | 0.024293 | 0.10039 | 0.049344 | 0.13067 | 0.079626
1823.9688 | 122.0078 | -121.669 | 0.082397 | 0.14017 | -0.013048 | -0.007421 | -0.002124 | 0.045421 | 0.076426 | -0.044405 | 0.006703 | 0.10669 | 0.036985 | 0.012689 | -0.084531 | -0.036295 | -0.038063 | -0.016906 | 0.17221 | 0.018995 | 0.024622 | 0.029919 | 0.077464 | 0.10847 | -0.012362 | 0.038746 | 0.13873 | 0.069028 | 0.044732 | -0.052488 | -0.004252 | -0.00602 | 0.015137 | 0.091234 | 0.044766 | 0.12152 | 0.075048
1825.7188 | 121.9025 | -121.6873 | 0.09613 | 0.14474 | -0.008469 | -0.002842 | -0.006703 | 0.040843 | 0.081005 | -0.035248 | 0.002124 | 0.10669 | 0.036985 | 0.017268 | -0.093688 | -0.040873 | -0.04722 | -0.012328 | 0.17679 | 0.023574 | 0.029201 | 0.02534 | 0.072886 | 0.11305 | -0.003205 | 0.034167 | 0.13873 | 0.069028 | 0.049311 | -0.061645 | -0.00883 | -0.015177 | 0.019715 | 0.095812 | 0.049344 | 0.13067 | 0.084205
1827.4062 | 121.8613 | -121.7102 | 0.1236 | 0.14474 | -0.017627 | -0.007421 | -0.002124 | 0.036265 | 0.076426 | -0.044405 | -0.002454 | 0.10669 | 0.036985 | 0.017268 | -0.093688 | -0.036295 | -0.042641 | -0.016906 | 0.17679 | 0.014416 | 0.024622 | 0.029919 | 0.068308 | 0.10847 | -0.012362 | 0.029589 | 0.13873 | 0.069028 | 0.049311 | -0.061645 | -0.004252 | -0.010598 | 0.015137 | 0.091234 | 0.040187 | 0.13067 | 0.079626
1829.1562 | 121.9757 | -121.6736 | 0.068665 | 0.13559 | -0.013048 | -0.007421 | -0.006703 | 0.031687 | 0.081005 | -0.044405 | 0.002124 | 0.11127 | 0.032407 | 0.012689 | -0.084531 | -0.036295 | -0.051798 | -0.016906 | 0.16763 | 0.018995 | 0.024622 | 0.02534 | 0.06373 | 0.11305 | -0.012362 | 0.034167 | 0.14331 | 0.06445 | 0.044732 | -0.052488 | -0.004252 | -0.019755 | 0.015137 | 0.086655 | 0.053922 | 0.11694 | 0.084205
1830.8438 | 122.0078 | -121.6919 | 0.082397 | 0.14017 | -0.013048 | -0.012 | -0.002124 | 0.040843 | 0.081005 | -0.039826 | 0.006703 | 0.10669 | 0.032407 | 0.017268 | -0.08911 | -0.040873 | -0.038063 | -0.012328 | 0.17221 | 0.018995 | 0.020043 | 0.029919 | 0.072886 | 0.11305 | -0.007783 | 0.038746 | 0.13873 | 0.06445 | 0.049311 | -0.057067 | -0.00883 | -0.00602 | 0.019715 | 0.095813 | 0.044766 | 0.12152 | 0.07047
1832.5938 | 121.994 | -121.6965 | 0.073242 | 0.14017 | -0.013048 | -0.016578 | -0.006703 | 0.040843 | 0.076426 | -0.044405 | 0.002124 | 0.10211 | 0.036985 | 0.021847 | -0.08911 | -0.040873 | -0.04722 | -0.00775 | 0.17221 | 0.018995 | 0.015465 | 0.02534 | 0.072886 | 0.10847 | -0.012362 | 0.034167 | 0.13415 | 0.069028 | 0.05389 | -0.057067 | -0.00883 | -0.015177 | 0.024293 | 0.091234 | 0.049344 | 0.12609 | 0.084205
1834.3594 | 121.8521 | -121.7194 | 0.10986 | 0.14932 | -0.013048 | -0.012 | 0.002454 | 0.040843 | 0.081005 | -0.039826 | -0.007033 | 0.11127 | 0.036985 | 0.017268 | -0.08911 | -0.031717 | -0.051798 | -0.012328 | 0.18136 | 0.018995 | 0.020043 | 0.034497 | 0.072886 | 0.11305 | -0.007783 | 0.02501 | 0.14331 | 0.069028 | 0.049311 | -0.057067 | 0.000326 | -0.019755 | 0.019715 | 0.082077 | 0.044765 | 0.12609 | 0.088783
1836.0469 | 121.8887 | -121.7422 | 0.1236 | 0.14017 | -0.013048 | -0.007421 | -0.006703 | 0.040843 | 0.085583 | -0.039826 | 0.006703 | 0.11585 | 0.036985 | 0.017268 | -0.084531 | -0.040873 | -0.056376 | -0.016906 | 0.17221 | 0.018995 | 0.024622 | 0.02534 | 0.072886 | 0.11763 | -0.007783 | 0.038746 | 0.14789 | 0.069028 | 0.049311 | -0.052488 | -0.00883 | -0.024333 | 0.015137 | 0.091234 | 0.063079 | 0.12152 | 0.093361
1837.7969 | 121.9574 | -121.7468 | 0.068665 | 0.14017 | -0.017627 | -0.012 | 0.002454 | 0.040843 | 0.076426 | -0.048983 | 0.002124 | 0.11585 | 0.032407 | 0.017268 | -0.08911 | -0.031717 | -0.051798 | -0.012328 | 0.17221 | 0.014416 | 0.020043 | 0.034497 | 0.072886 | 0.10847 | -0.01694 | 0.034167 | 0.14789 | 0.06445 | 0.049311 | -0.057067 | 0.000326 | -0.019755 | 0.019715 | 0.091234 | 0.053922 | 0.12152 | 0.084205
1839.5625 | 121.8887 | -121.756 | 0.15106 | 0.14932 | -0.013048 | -0.007421 | -0.002124 | 0.036265 | 0.081005 | -0.039826 | 0.006703 | 0.11127 | 0.032407 | 0.017268 | -0.084531 | -0.031717 | -0.04722 | -0.00775 | 0.18136 | 0.018995 | 0.024622 | 0.029919 | 0.068308 | 0.11305 | -0.007783 | 0.038746 | 0.14331 | 0.06445 | 0.049311 | -0.052488 | 0.000326 | -0.015177 | 0.024293 | 0.091234 | 0.053923 | 0.11694 | 0.079627
1841.25 | 122.0078 | -121.7239 | 0.082397 | 0.14017 | -0.017627 | -0.012 | -0.006703 | 0.040843 | 0.085583 | -0.044405 | -0.002454 | 0.11127 | 0.036985 | 0.021847 | -0.08911 | -0.036295 | -0.051798 | -0.012328 | 0.17221 | 0.014416 | 0.020043 | 0.02534 | 0.072886 | 0.11763 | -0.012362 | 0.029589 | 0.14331 | 0.069028 | 0.05389 | -0.057067 | -0.004252 | -0.019755 | 0.019715 | 0.086656 | 0.049344 | 0.12609 | 0.088783
1843 | 121.9666 | -121.7468 | 0.091553 | 0.14474 | -0.013048 | -0.016578 | -0.006703 | 0.040843 | 0.076426 | -0.044405 | 0.002124 | 0.11127 | 0.032407 | 0.012689 | -0.08911 | -0.036295 | -0.04722 | -0.016906 | 0.17679 | 0.018995 | 0.015465 | 0.02534 | 0.072886 | 0.10847 | -0.012362 | 0.034167 | 0.14331 | 0.06445 | 0.044732 | -0.057067 | -0.004252 | -0.015177 | 0.015137 | 0.091234 | 0.049344 | 0.12152 | 0.079627
1844.75 | 121.9116 | -121.7697 | 0.10529 | 0.14932 | -0.008469 | -0.002842 | -0.002124 | 0.045421 | 0.081005 | -0.044405 | 0.002124 | 0.10211 | 0.036985 | 0.021847 | -0.08911 | -0.036295 | -0.04722 | -0.016906 | 0.18136 | 0.023574 | 0.029201 | 0.029919 | 0.077464 | 0.11305 | -0.012362 | 0.034167 | 0.13415 | 0.069028 | 0.05389 | -0.057067 | -0.004252 | -0.015177 | 0.015137 | 0.091234 | 0.049344 | 0.12609 | 0.084205
1846.4531 | 121.9162 | -121.7972 | 0.10529 | 0.14017 | -0.013048 | -0.007421 | -0.006703 | 0.049999 | 0.085583 | -0.039826 | 0.011281 | 0.11127 | 0.032407 | 0.017268 | -0.098266 | -0.045451 | -0.04722 | -0.00775 | 0.17221 | 0.018995 | 0.024622 | 0.02534 | 0.082042 | 0.11763 | -0.007783 | 0.043324 | 0.14331 | 0.06445 | 0.049311 | -0.066223 | -0.013408 | -0.015177 | 0.024293 | 0.10955 | 0.058501 | 0.13067 | 0.079627
1848.2031 | 121.8933 | -121.7514 | 0.10986 | 0.14932 | -0.008469 | -0.007421 | 0.002454 | 0.036265 | 0.081005 | -0.035248 | 0.002124 | 0.10669 | 0.032407 | 0.012689 | -0.08911 | -0.031717 | -0.042641 | -0.012328 | 0.18136 | 0.023574 | 0.024622 | 0.034497 | 0.068308 | 0.11305 | -0.003205 | 0.034167 | 0.13873 | 0.06445 | 0.044732 | -0.057067 | 0.000326 | -0.010598 | 0.019715 | 0.091234 | 0.044765 | 0.12152 | 0.075048
1849.9531 | 121.9528 | -121.7789 | 0.10529 | 0.14474 | -0.013048 | -0.007421 | 0.002454 | 0.040843 | 0.076426 | -0.035248 | -0.002454 | 0.11127 | 0.041563 | 0.021847 | -0.08911 | -0.036295 | -0.042641 | -0.00775 | 0.17679 | 0.018995 | 0.024622 | 0.034497 | 0.072886 | 0.10847 | -0.003205 | 0.029589 | 0.14331 | 0.073606 | 0.05389 | -0.057067 | -0.004252 | -0.010598 | 0.024293 | 0.086656 | 0.040187 | 0.13067 | 0.084204
1851.7031 | 121.9849 | -121.7239 | 0.10071 | 0.14017 | -0.013048 | -0.016578 | -0.002124 | 0.031687 | 0.076426 | -0.044405 | 0.006703 | 0.11127 | 0.032407 | 0.026427 | -0.093688 | -0.027139 | -0.04722 | -0.012328 | 0.17221 | 0.018995 | 0.015465 | 0.029919 | 0.06373 | 0.10847 | -0.012362 | 0.038746 | 0.14331 | 0.06445 | 0.05847 | -0.061645 | 0.004904 | -0.015177 | 0.019715 | 0.10039 | 0.053923 | 0.12609 | 0.079627
1853.3906 | 121.994 | -121.756 | 0.086975 | 0.14017 | -0.013048 | -0.007421 | -0.006703 | 0.036265 | 0.076426 | -0.039826 | 0.002124 | 0.11127 | 0.041563 | 0.017268 | -0.08911 | -0.036295 | -0.051798 | -0.012328 | 0.17221 | 0.018995 | 0.024622 | 0.02534 | 0.068308 | 0.10847 | -0.007783 | 0.034167 | 0.14331 | 0.073606 | 0.049311 | -0.057067 | -0.004252 | -0.019755 | 0.019715 | 0.091234 | 0.053922 | 0.13067 | 0.093361
1855.1406 | 121.994 | -121.7651 | 0.09613 | 0.14017 | -0.008469 | -0.007421 | -0.006703 | 0.040843 | 0.081005 | -0.048983 | 0.002124 | 0.11127 | 0.032407 | 0.012689 | -0.08911 | -0.036295 | -0.042641 | -0.00775 | 0.17221 | 0.023574 | 0.024622 | 0.02534 | 0.072886 | 0.11305 | -0.01694 | 0.034167 | 0.14331 | 0.06445 | 0.044732 | -0.057067 | -0.004252 | -0.010598 | 0.024293 | 0.091234 | 0.044765 | 0.12152 | 0.075048
1856.9062 | 121.9803 | -121.7377 | 0.086975 | 0.14017 | -0.013048 | -0.012 | -0.011281 | 0.036265 | 0.076426 | -0.035248 | 0.006703 | 0.11127 | 0.036985 | 0.026427 | -0.093688 | -0.040873 | -0.042641 | -0.016906 | 0.17221 | 0.018995 | 0.020043 | 0.020762 | 0.068308 | 0.10847 | -0.003205 | 0.038746 | 0.14331 | 0.069028 | 0.05847 | -0.061645 | -0.00883 | -0.010598 | 0.015137 | 0.10039 | 0.049344 | 0.13067 | 0.079626
1858.6094 | 122.0032 | -121.7422 | 0.091553 | 0.13101 | -0.008469 | -0.007421 | -0.002124 | 0.040843 | 0.076426 | -0.048983 | -0.002454 | 0.11585 | 0.036985 | 0.017268 | -0.08911 | -0.036295 | -0.042641 | -0.016906 | 0.16305 | 0.023574 | 0.024622 | 0.029919 | 0.072886 | 0.10847 | -0.01694 | 0.029589 | 0.14789 | 0.069028 | 0.049311 | -0.057067 | -0.004252 | -0.010598 | 0.015137 | 0.086656 | 0.040187 | 0.12609 | 0.079626
1860.2969 | 122.0261 | -121.7331 | 0.059509 | 0.13559 | -0.008469 | -0.012 | -0.002124 | 0.031687 | 0.081005 | -0.039826 | 0.002124 | 0.10669 | 0.036985 | 0.026427 | -0.08911 | -0.027139 | -0.04722 | -0.012328 | 0.16763 | 0.023574 | 0.020043 | 0.029919 | 0.06373 | 0.11305 | -0.007783 | 0.034167 | 0.13873 | 0.069028 | 0.05847 | -0.057067 | 0.004904 | -0.015177 | 0.019715 | 0.091234 | 0.049344 | 0.12609 | 0.084205
1862.0469 | 122.0032 | -121.7651 | 0.082397 | 0.14474 | -0.017627 | -0.012 | -0.002124 | 0.040843 | 0.071848 | -0.039826 | 0.006703 | 0.11127 | 0.036985 | 0.012689 | -0.098266 | -0.036295 | -0.042641 | -0.016906 | 0.17679 | 0.014416 | 0.020043 | 0.029919 | 0.072886 | 0.10389 | -0.007783 | 0.038746 | 0.14331 | 0.069028 | 0.044732 | -0.066223 | -0.004252 | -0.010598 | 0.015137 | 0.10497 | 0.049344 | 0.13525 | 0.079626
1863.7969 | 122.0627 | -121.7422 | 0.059509 | 0.14474 | -0.017627 | -0.007421 | -0.002124 | 0.036265 | 0.081005 | -0.039826 | 0.006703 | 0.10669 | 0.036985 | 0.021847 | -0.093688 | -0.040873 | -0.042641 | -0.016906 | 0.17679 | 0.014416 | 0.024622 | 0.029919 | 0.068308 | 0.11305 | -0.007783 | 0.038746 | 0.13873 | 0.069028 | 0.05389 | -0.061645 | -0.00883 | -0.010598 | 0.015137 | 0.10039 | 0.049344 | 0.13067 | 0.079626
1865.4844 | 121.9528 | -121.756 | 0.10986 | 0.14017 | -0.013048 | -0.007421 | -0.002124 | 0.040843 | 0.076426 | -0.044405 | 0.002124 | 0.11585 | 0.032407 | 0.017268 | -0.08911 | -0.036295 | -0.04722 | -0.016906 | 0.17221 | 0.018995 | 0.024622 | 0.029919 | 0.072886 | 0.10847 | -0.012362 | 0.034167 | 0.14789 | 0.06445 | 0.049311 | -0.057067 | -0.004252 | -0.015177 | 0.015137 | 0.091234 | 0.049344 | 0.12152 | 0.079627
1867.1875 | 121.9574 | -121.788 | 0.10071 | 0.14474 | -0.013048 | -0.007421 | -0.002124 | 0.040843 | 0.085583 | -0.048983 | 0.002124 | 0.10669 | 0.041563 | 0.017268 | -0.093688 | -0.036295 | -0.042641 | -0.012328 | 0.17679 | 0.018995 | 0.024622 | 0.029919 | 0.072886 | 0.11763 | -0.01694 | 0.034167 | 0.13873 | 0.073606 | 0.049311 | -0.061645 | -0.004252 | -0.010598 | 0.019715 | 0.095812 | 0.044765 | 0.13525 | 0.084204
1868.9531 | 122.0261 | -121.756 | 0.064087 | 0.14017 | -0.013048 | -0.012 | -0.002124 | 0.040843 | 0.081005 | -0.039826 | -0.002454 | 0.11127 | 0.041563 | 0.017268 | -0.08911 | -0.031717 | -0.04722 | -0.00775 | 0.17221 | 0.018995 | 0.020043 | 0.029919 | 0.072886 | 0.11305 | -0.007783 | 0.029589 | 0.14331 | 0.073606 | 0.049311 | -0.057067 | 0.000326 | -0.015177 | 0.024293 | 0.086656 | 0.044766 | 0.13067 | 0.088783
1870.625 | 121.9528 | -121.8109 | 0.11444 | 0.14474 | -0.013048 | -0.012 | 0.007033 | 0.045421 | 0.081005 | -0.039826 | 0.002124 | 0.11127 | 0.032407 | 0.012689 | -0.08911 | -0.031717 | -0.033484 | -0.016906 | 0.17679 | 0.018995 | 0.020043 | 0.039076 | 0.077464 | 0.11305 | -0.007783 | 0.034167 | 0.14331 | 0.06445 | 0.044732 | -0.057067 | 0.000326 | -0.001441 | 0.015137 | 0.091234 | 0.035608 | 0.12152 | 0.065891
1872.375 | 121.9299 | -121.8292 | 0.13733 | 0.14017 | -0.013048 | -0.016578 | 0.002454 | 0.045421 | 0.081005 | -0.03067 | -0.002454 | 0.10669 | 0.036985 | 0.021847 | -0.08911 | -0.031717 | -0.042641 | -0.021484 | 0.17221 | 0.018995 | 0.015465 | 0.034497 | 0.077464 | 0.11305 | 0.001373 | 0.029589 | 0.13873 | 0.069028 | 0.05389 | -0.057067 | 0.000326 | -0.010598 | 0.010559 | 0.086656 | 0.040187 | 0.12609 | 0.079626
1874.0781 | 121.9574 | -121.8109 | 0.091553 | 0.14017 | -0.008469 | -0.007421 | 0.002454 | 0.045421 | 0.076426 | -0.044405 | -0.002454 | 0.10669 | 0.041563 | 0.021847 | -0.098266 | -0.036295 | -0.051798 | -0.00775 | 0.17221 | 0.023574 | 0.024622 | 0.034497 | 0.077464 | 0.10847 | -0.012362 | 0.029589 | 0.13873 | 0.073606 | 0.05389 | -0.066223 | -0.004252 | -0.019755 | 0.024293 | 0.095812 | 0.049344 | 0.13983 | 0.093361
1875.8281 | 121.994 | -121.7926 | 0.10986 | 0.14474 | -0.013048 | -0.012 | 0.002454 | 0.040843 | 0.081005 | -0.044405 | 0.011281 | 0.11127 | 0.032407 | 0.012689 | -0.093688 | -0.040873 | -0.042641 | -0.016906 | 0.17679 | 0.018995 | 0.020043 | 0.034497 | 0.072886 | 0.11305 | -0.012362 | 0.043324 | 0.14331 | 0.06445 | 0.044732 | -0.061645 | -0.00883 | -0.010598 | 0.015137 | 0.10497 | 0.053922 | 0.12609 | 0.075048
1877.5156 | 121.962 | -121.843 | 0.12817 | 0.14017 | -0.017627 | -0.007421 | -0.002124 | 0.040843 | 0.081005 | -0.039826 | 0.006703 | 0.11127 | 0.036985 | 0.021847 | -0.08911 | -0.031717 | -0.042641 | -0.016906 | 0.17221 | 0.014416 | 0.024622 | 0.029919 | 0.072886 | 0.11305 | -0.007783 | 0.038746 | 0.14331 | 0.069028 | 0.05389 | -0.057067 | 0.000326 | -0.010598 | 0.015137 | 0.095813 | 0.049344 | 0.12609 | 0.079626
1879.2812 | 122.1085 | -121.7606 | 0.068665 | 0.14474 | -0.013048 | -0.016578 | -0.006703 | 0.040843 | 0.081005 | -0.039826 | -0.002454 | 0.11585 | 0.036985 | 0.017268 | -0.08911 | -0.031717 | -0.051798 | -0.021484 | 0.17679 | 0.018995 | 0.015465 | 0.02534 | 0.072886 | 0.11305 | -0.007783 | 0.029589 | 0.14789 | 0.069028 | 0.049311 | -0.057067 | 0.000326 | -0.019755 | 0.010559 | 0.086656 | 0.049344 | 0.12609 | 0.088783
1881.0312 | 122.0444 | -121.7972 | 0.086975 | 0.14474 | -0.017627 | -0.012 | -0.002124 | 0.045421 | 0.076426 | -0.039826 | 0.002124 | 0.11127 | 0.036985 | 0.021847 | -0.08911 | -0.036295 | -0.051798 | -0.012328 | 0.17679 | 0.014416 | 0.020043 | 0.029919 | 0.077464 | 0.10847 | -0.007783 | 0.034167 | 0.14331 | 0.069028 | 0.05389 | -0.057067 | -0.004252 | -0.019755 | 0.019715 | 0.091234 | 0.053922 | 0.12609 | 0.088783
1882.7656 | 122.0581 | -121.8246 | 0.10986 | 0.14017 | -0.022205 | -0.016578 | -0.002124 | 0.045421 | 0.081005 | -0.044405 | 0.011281 | 0.11127 | 0.036985 | 0.012689 | -0.08911 | -0.031717 | -0.04722 | -0.021484 | 0.17221 | 0.009838 | 0.015465 | 0.029919 | 0.077464 | 0.11305 | -0.012362 | 0.043324 | 0.14331 | 0.069028 | 0.044732 | -0.057067 | 0.000326 | -0.015177 | 0.010559 | 0.10039 | 0.058501 | 0.12609 | 0.084205
1884.4688 | 121.9437 | -121.8475 | 0.11444 | 0.14474 | -0.008469 | -0.007421 | -0.006703 | 0.040843 | 0.081005 | -0.039826 | 0.002124 | 0.11585 | 0.041563 | 0.017268 | -0.08911 | -0.036295 | -0.051798 | -0.016906 | 0.17679 | 0.023574 | 0.024622 | 0.02534 | 0.072886 | 0.11305 | -0.007783 | 0.034167 | 0.14789 | 0.073606 | 0.049311 | -0.057067 | -0.004252 | -0.019755 | 0.015137 | 0.091234 | 0.053922 | 0.13067 | 0.093361
1886.2188 | 122.0627 | -121.7789 | 0.082397 | 0.14017 | -0.017627 | -0.002842 | -0.002124 | 0.036265 | 0.081005 | -0.035248 | 0.002124 | 0.10669 | 0.041563 | 0.017268 | -0.08911 | -0.031717 | -0.056376 | -0.016906 | 0.17221 | 0.014416 | 0.029201 | 0.029919 | 0.068308 | 0.11305 | -0.003205 | 0.034167 | 0.13873 | 0.073606 | 0.049311 | -0.057067 | 0.000326 | -0.024333 | 0.015137 | 0.091234 | 0.0585 | 0.13067 | 0.097939
1887.9688 | 121.9711 | -121.843 | 0.10071 | 0.14017 | -0.013048 | -0.012 | -0.002124 | 0.040843 | 0.081005 | -0.039826 | 0.006703 | 0.11127 | 0.032407 | 0.017268 | -0.093688 | -0.031717 | -0.04722 | -0.00775 | 0.17221 | 0.018995 | 0.020043 | 0.029919 | 0.072886 | 0.11305 | -0.007783 | 0.038746 | 0.14331 | 0.06445 | 0.049311 | -0.061645 | 0.000326 | -0.015177 | 0.024293 | 0.10039 | 0.053923 | 0.12609 | 0.079627
1889.7344 | 122.0169 | -121.8155 | 0.09613 | 0.14017 | -0.022205 | -0.002842 | -0.002124 | 0.036265 | 0.081005 | -0.044405 | 0.006703 | 0.11127 | 0.032407 | 0.012689 | -0.093688 | -0.045451 | -0.042641 | -0.021484 | 0.17221 | 0.009838 | 0.029201 | 0.029919 | 0.068308 | 0.11305 | -0.012362 | 0.038746 | 0.14331 | 0.06445 | 0.044732 | -0.061645 | -0.013408 | -0.010598 | 0.010559 | 0.10039 | 0.049344 | 0.12609 | 0.075048
1891.5 | 121.9757 | -121.8704 | 0.11902 | 0.13559 | -0.013048 | -0.002842 | 0.007033 | 0.045421 | 0.081005 | -0.039826 | 0.011281 | 0.11585 | 0.032407 | 0.021847 | -0.08911 | -0.031717 | -0.042641 | -0.012328 | 0.16763 | 0.018995 | 0.029201 | 0.039076 | 0.077464 | 0.11305 | -0.007783 | 0.043324 | 0.14789 | 0.06445 | 0.05389 | -0.057067 | 0.000326 | -0.010598 | 0.019715 | 0.10039 | 0.053922 | 0.12152 | 0.075048
1893.1875 | 122.0673 | -121.8201 | 0.082397 | 0.14017 | -0.008469 | -0.002842 | -0.006703 | 0.049999 | 0.081005 | -0.039826 | 0.006703 | 0.11585 | 0.036985 | 0.017268 | -0.084531 | -0.031717 | -0.038063 | -0.016906 | 0.17221 | 0.023574 | 0.029201 | 0.02534 | 0.082042 | 0.11305 | -0.007783 | 0.038746 | 0.14789 | 0.069028 | 0.049311 | -0.052488 | 0.000326 | -0.00602 | 0.015137 | 0.091234 | 0.044766 | 0.12152 | 0.075048
1894.9375 | 122.1039 | -121.788 | 0.068665 | 0.13559 | -0.013048 | -0.016578 | 0.011611 | 0.036265 | 0.081005 | -0.039826 | 0.006703 | 0.11585 | 0.036985 | 0.017268 | -0.093688 | -0.036295 | -0.04722 | -0.021484 | 0.16763 | 0.018995 | 0.015465 | 0.043654 | 0.068308 | 0.11305 | -0.007783 | 0.038746 | 0.14789 | 0.069028 | 0.049311 | -0.061645 | -0.004252 | -0.015177 | 0.010559 | 0.10039 | 0.053923 | 0.13067 | 0.084205
1896.6875 | 122.0306 | -121.843 | 0.09613 | 0.14474 | -0.013048 | -0.012 | 0.007033 | 0.040843 | 0.076426 | -0.035248 | 0.006703 | 0.10669 | 0.032407 | 0.021847 | -0.093688 | -0.040873 | -0.042641 | -0.012328 | 0.17679 | 0.018995 | 0.020043 | 0.039076 | 0.072886 | 0.10847 | -0.003205 | 0.038746 | 0.13873 | 0.06445 | 0.05389 | -0.061645 | -0.00883 | -0.010598 | 0.019715 | 0.10039 | 0.049344 | 0.12609 | 0.075048
1898.3906 | 122.1176 | -121.8109 | 0.07782 | 0.13559 | -0.017627 | -0.012 | -0.002124 | 0.027109 | 0.071848 | -0.039826 | 0.002124 | 0.11127 | 0.041563 | 0.021847 | -0.084531 | -0.040873 | -0.051798 | -0.012328 | 0.16763 | 0.014416 | 0.020043 | 0.029919 | 0.059152 | 0.10389 | -0.007783 | 0.034167 | 0.14331 | 0.073606 | 0.05389 | -0.052488 | -0.00883 | -0.019755 | 0.019715 | 0.086655 | 0.053922 | 0.12609 | 0.093361
1900.1562 | 122.1176 | -121.788 | 0.068665 | 0.14474 | -0.017627 | -0.012 | 0.002454 | 0.036265 | 0.081005 | -0.039826 | 0.011281 | 0.11127 | 0.036985 | 0.012689 | -0.098266 | -0.036295 | -0.038063 | -0.016906 | 0.17679 | 0.014416 | 0.020043 | 0.034497 | 0.068308 | 0.11305 | -0.007783 | 0.043324 | 0.14331 | 0.069028 | 0.044732 | -0.066223 | -0.004252 | -0.00602 | 0.015137 | 0.10955 | 0.049344 | 0.13525 | 0.075048
1901.9219 | 122.1222 | -121.8201 | 0.064087 | 0.14474 | -0.017627 | -0.002842 | 0.002454 | 0.040843 | 0.071848 | -0.035248 | 0.011281 | 0.11127 | 0.032407 | 0.021847 | -0.08911 | -0.031717 | -0.042641 | -0.012328 | 0.17679 | 0.014416 | 0.029201 | 0.034497 | 0.072886 | 0.10389 | -0.003205 | 0.043324 | 0.14331 | 0.06445 | 0.05389 | -0.057067 | 0.000326 | -0.010598 | 0.019715 | 0.10039 | 0.053922 | 0.12152 | 0.075048
1903.6094 | 122.0123 | -121.8384 | 0.1236 | 0.14017 | -0.017627 | -0.007421 | -0.002124 | 0.045421 | 0.085583 | -0.035248 | 0.01586 | 0.11127 | 0.041563 | 0.021847 | -0.084531 | -0.031717 | -0.051798 | -0.012328 | 0.17221 | 0.014416 | 0.024622 | 0.029919 | 0.077464 | 0.11763 | -0.003205 | 0.047903 | 0.14331 | 0.073606 | 0.05389 | -0.052488 | 0.000326 | -0.019755 | 0.019715 | 0.10039 | 0.067658 | 0.12609 | 0.093361
1905.2969 | 122.1497 | -121.8201 | 0.073242 | 0.14474 | -0.022205 | -0.012 | -0.002124 | 0.045421 | 0.081005 | -0.03067 | 0.006703 | 0.11585 | 0.041563 | 0.017268 | -0.08911 | -0.036295 | -0.051798 | -0.00775 | 0.17679 | 0.009838 | 0.020043 | 0.029919 | 0.077464 | 0.11305 | 0.001373 | 0.038746 | 0.14789 | 0.073606 | 0.049311 | -0.057067 | -0.004252 | -0.019755 | 0.024293 | 0.095813 | 0.058501 | 0.13067 | 0.093361
1907.0469 | 121.9986 | -121.8521 | 0.11902 | 0.14017 | -0.013048 | -0.012 | -0.002124 | 0.040843 | 0.085583 | -0.039826 | 0.006703 | 0.11585 | 0.036985 | 0.017268 | -0.098266 | -0.036295 | -0.051798 | -0.026063 | 0.17221 | 0.018995 | 0.020043 | 0.029919 | 0.072886 | 0.11763 | -0.007783 | 0.038746 | 0.14789 | 0.069028 | 0.049311 | -0.066223 | -0.004252 | -0.019755 | 0.00598 | 0.10497 | 0.058501 | 0.13525 | 0.088783
1908.8125 | 122.0718 | -121.8201 | 0.082397 | 0.13559 | -0.017627 | -0.012 | -0.006703 | 0.040843 | 0.071848 | -0.035248 | 0.011281 | 0.11127 | 0.041563 | 0.021847 | -0.084531 | -0.031717 | -0.04722 | -0.016906 | 0.16763 | 0.014416 | 0.020043 | 0.02534 | 0.072886 | 0.10389 | -0.003205 | 0.043324 | 0.14331 | 0.073606 | 0.05389 | -0.052488 | 0.000326 | -0.015177 | 0.015137 | 0.095812 | 0.058501 | 0.12609 | 0.088783
1910.5625 | 122.0901 | -121.843 | 0.086975 | 0.14017 | -0.013048 | -0.012 | 0.002454 | 0.040843 | 0.081005 | -0.044405 | 0.006703 | 0.10669 | 0.036985 | 0.021847 | -0.08911 | -0.036295 | -0.04722 | -0.012328 | 0.17221 | 0.018995 | 0.020043 | 0.034497 | 0.072886 | 0.11305 | -0.012362 | 0.038746 | 0.13873 | 0.069028 | 0.05389 | -0.057067 | -0.004252 | -0.015177 | 0.019715 | 0.095813 | 0.053923 | 0.12609 | 0.084205
1912.25 | 122.081 | -121.8246 | 0.073242 | 0.13559 | -0.017627 | -0.012 | -0.006703 | 0.040843 | 0.081005 | -0.035248 | -0.002454 | 0.11127 | 0.036985 | 0.017268 | -0.093688 | -0.036295 | -0.038063 | -0.016906 | 0.16763 | 0.014416 | 0.020043 | 0.02534 | 0.072886 | 0.11305 | -0.003205 | 0.029589 | 0.14331 | 0.069028 | 0.049311 | -0.061645 | -0.004252 | -0.00602 | 0.015137 | 0.091234 | 0.035609 | 0.13067 | 0.075048
1914 | 122.1359 | -121.8246 | 0.068665 | 0.14017 | -0.017627 | -0.007421 | -0.002124 | 0.040843 | 0.076426 | -0.035248 | 0.006703 | 0.11585 | 0.032407 | 0.017268 | -0.093688 | -0.031717 | -0.04722 | -0.012328 | 0.17221 | 0.014416 | 0.024622 | 0.029919 | 0.072886 | 0.10847 | -0.003205 | 0.038746 | 0.14789 | 0.06445 | 0.049311 | -0.061645 | 0.000326 | -0.015177 | 0.019715 | 0.10039 | 0.053923 | 0.12609 | 0.079627
1915.75 | 122.0673 | -121.8658 | 0.10986 | 0.14474 | -0.013048 | -0.002842 | 0.002454 | 0.040843 | 0.076426 | -0.044405 | 0.006703 | 0.12501 | 0.036985 | 0.017268 | -0.08911 | -0.036295 | -0.04722 | -0.012328 | 0.17679 | 0.018995 | 0.029201 | 0.034497 | 0.072886 | 0.10847 | -0.012362 | 0.038746 | 0.15705 | 0.069028 | 0.049311 | -0.057067 | -0.004252 | -0.015177 | 0.019715 | 0.095813 | 0.053923 | 0.12609 | 0.084205
1917.4375 | 122.0398 | -121.875 | 0.10071 | 0.14474 | -0.017627 | -0.012 | -0.002124 | 0.040843 | 0.076426 | -0.039826 | 0.002124 | 0.11585 | 0.041563 | 0.017268 | -0.093688 | -0.031717 | -0.04722 | -0.016906 | 0.17679 | 0.014416 | 0.020043 | 0.029919 | 0.072886 | 0.10847 | -0.007783 | 0.034167 | 0.14789 | 0.073606 | 0.049311 | -0.061645 | 0.000326 | -0.015177 | 0.015137 | 0.095812 | 0.049344 | 0.13525 | 0.088783
1919.1875 | 122.0947 | -121.8704 | 0.082397 | 0.14474 | -0.017627 | -0.012 | 0.002454 | 0.040843 | 0.081005 | -0.03067 | 0.002124 | 0.11127 | 0.032407 | 0.017268 | -0.08911 | -0.036295 | -0.038063 | -0.012328 | 0.17679 | 0.014416 | 0.020043 | 0.034497 | 0.072886 | 0.11305 | 0.001373 | 0.034167 | 0.14331 | 0.06445 | 0.049311 | -0.057067 | -0.004252 | -0.00602 | 0.019715 | 0.091234 | 0.040187 | 0.12152 | 0.07047
1920.9375 | 122.0535 | -121.8567 | 0.10529 | 0.13559 | -0.017627 | -0.007421 | 0.002454 | 0.036265 | 0.076426 | -0.035248 | 0.006703 | 0.11585 | 0.036985 | 0.021847 | -0.093688 | -0.031717 | -0.042641 | -0.012328 | 0.16763 | 0.014416 | 0.024622 | 0.034497 | 0.068308 | 0.10847 | -0.003205 | 0.038746 | 0.14789 | 0.069028 | 0.05389 | -0.061645 | 0.000326 | -0.010598 | 0.019715 | 0.10039 | 0.049344 | 0.13067 | 0.079626
1922.625 | 122.1268 | -121.8796 | 0.086975 | 0.14474 | -0.017627 | -0.007421 | -0.002124 | 0.036265 | 0.076426 | -0.044405 | 0.002124 | 0.11585 | 0.041563 | 0.017268 | -0.08911 | -0.036295 | -0.04722 | -0.016906 | 0.17679 | 0.014416 | 0.024622 | 0.029919 | 0.068308 | 0.10847 | -0.012362 | 0.034167 | 0.14789 | 0.073606 | 0.049311 | -0.057067 | -0.004252 | -0.015177 | 0.015137 | 0.091234 | 0.049344 | 0.13067 | 0.088783
1924.3125 | 122.0352 | -121.8521 | 0.11902 | 0.14017 | -0.017627 | -0.012 | 0.002454 | 0.040843 | 0.081005 | -0.035248 | 0.006703 | 0.11585 | 0.036985 | 0.017268 | -0.08911 | -0.036295 | -0.04722 | -0.016906 | 0.17221 | 0.014416 | 0.020043 | 0.034497 | 0.072886 | 0.11305 | -0.003205 | 0.038746 | 0.14789 | 0.069028 | 0.049311 | -0.057067 | -0.004252 | -0.015177 | 0.015137 | 0.095813 | 0.053923 | 0.12609 | 0.084205
1926.0625 | 122.1542 | -121.8384 | 0.082397 | 0.13559 | -0.022205 | -0.016578 | -0.002124 | 0.040843 | 0.071848 | -0.035248 | 0.006703 | 0.11585 | 0.032407 | 0.017268 | -0.08911 | -0.031717 | -0.04722 | -0.00775 | 0.16763 | 0.009838 | 0.015465 | 0.029919 | 0.072886 | 0.10389 | -0.003205 | 0.038746 | 0.14789 | 0.06445 | 0.049311 | -0.057067 | 0.000326 | -0.015177 | 0.024293 | 0.095813 | 0.053923 | 0.12152 | 0.079627
1927.8125 | 122.0718 | -121.8842 | 0.091553 | 0.14474 | -0.013048 | -0.007421 | -0.002124 | 0.045421 | 0.071848 | -0.044405 | 0.011281 | 0.11585 | 0.041563 | 0.017268 | -0.084531 | -0.027139 | -0.04722 | -0.012328 | 0.17679 | 0.018995 | 0.024622 | 0.029919 | 0.077464 | 0.10389 | -0.012362 | 0.043324 | 0.14789 | 0.073606 | 0.049311 | -0.052488 | 0.004904 | -0.015177 | 0.019715 | 0.095812 | 0.058501 | 0.12609 | 0.088783
1929.5781 | 122.1588 | -121.843 | 0.082397 | 0.14017 | -0.017627 | -0.016578 | -0.002124 | 0.045421 | 0.076426 | -0.044405 | 0.011281 | 0.12043 | 0.036985 | 0.021847 | -0.093688 | -0.031717 | -0.04722 | -0.016906 | 0.17221 | 0.014416 | 0.015465 | 0.029919 | 0.077464 | 0.10847 | -0.012362 | 0.043324 | 0.15247 | 0.069028 | 0.05389 | -0.061645 | 0.000326 | -0.015177 | 0.015137 | 0.10497 | 0.058501 | 0.13067 | 0.084205
1931.2656 | 122.1359 | -121.8567 | 0.073242 | 0.14017 | -0.017627 | -0.016578 | -0.006703 | 0.040843 | 0.071848 | -0.039826 | 0.011281 | 0.11127 | 0.041563 | 0.021847 | -0.08911 | -0.040873 | -0.042641 | -0.026063 | 0.17221 | 0.014416 | 0.015465 | 0.02534 | 0.072886 | 0.10389 | -0.007783 | 0.043324 | 0.14331 | 0.073606 | 0.05389 | -0.057067 | -0.00883 | -0.010598 | 0.00598 | 0.10039 | 0.053922 | 0.13067 | 0.084204
1933.0312 | 122.1634 | -121.8475 | 0.082397 | 0.13559 | -0.022205 | -0.012 | -0.002124 | 0.036265 | 0.067269 | -0.048983 | 0.006703 | 0.11585 | 0.032407 | 0.021847 | -0.093688 | -0.031717 | -0.04722 | -0.012328 | 0.16763 | 0.009838 | 0.020043 | 0.029919 | 0.068308 | 0.099312 | -0.01694 | 0.038746 | 0.14789 | 0.06445 | 0.05389 | -0.061645 | 0.000326 | -0.015177 | 0.019715 | 0.10039 | 0.053923 | 0.12609 | 0.079627
1934.7969 | 122.0535 | -121.875 | 0.086975 | 0.14017 | -0.022205 | -0.012 | -0.002124 | 0.049999 | 0.076426 | -0.039826 | 0.006703 | 0.11585 | 0.041563 | 0.017268 | -0.098266 | -0.031717 | -0.042641 | -0.016906 | 0.17221 | 0.009838 | 0.020043 | 0.029919 | 0.082042 | 0.10847 | -0.007783 | 0.038746 | 0.14789 | 0.073606 | 0.049311 | -0.066223 | 0.000326 | -0.010598 | 0.015137 | 0.10497 | 0.049344 | 0.13983 | 0.084204
1936.4844 | 122.0352 | -121.907 | 0.10529 | 0.14017 | -0.022205 | -0.002842 | -0.006703 | 0.036265 | 0.076426 | -0.044405 | 0.006703 | 0.11127 | 0.032407 | 0.012689 | -0.08911 | -0.036295 | -0.051798 | -0.016906 | 0.17221 | 0.009838 | 0.029201 | 0.02534 | 0.068308 | 0.10847 | -0.012362 | 0.038746 | 0.14331 | 0.06445 | 0.044732 | -0.057067 | -0.004252 | -0.019755 | 0.015137 | 0.095813 | 0.058501 | 0.12152 | 0.084205
1938.25 | 122.168 | -121.8567 | 0.082397 | 0.13101 | -0.013048 | -0.012 | 0.002454 | 0.040843 | 0.076426 | -0.039826 | 0.006703 | 0.11585 | 0.041563 | 0.021847 | -0.084531 | -0.040873 | -0.051798 | -0.012328 | 0.16305 | 0.018995 | 0.020043 | 0.034497 | 0.072886 | 0.10847 | -0.007783 | 0.038746 | 0.14789 | 0.073606 | 0.05389 | -0.052488 | -0.00883 | -0.019755 | 0.019715 | 0.091234 | 0.058501 | 0.12609 | 0.093361
1940.0156 | 122.0352 | -121.8704 | 0.10071 | 0.14932 | -0.017627 | -0.016578 | 0.002454 | 0.045421 | 0.076426 | -0.035248 | 0.006703 | 0.11585 | 0.036985 | 0.012689 | -0.084531 | -0.031717 | -0.04722 | -0.021484 | 0.18136 | 0.014416 | 0.015465 | 0.034497 | 0.077464 | 0.10847 | -0.003205 | 0.038746 | 0.14789 | 0.069028 | 0.044732 | -0.052488 | 0.000326 | -0.015177 | 0.010559 | 0.091234 | 0.053923 | 0.12152 | 0.084205
1941.7031 | 122.1909 | -121.8521 | 0.073242 | 0.13559 | -0.008469 | -0.007421 | -0.006703 | 0.045421 | 0.076426 | -0.035248 | 0.011281 | 0.10669 | 0.041563 | 0.026427 | -0.08911 | -0.040873 | -0.04722 | -0.016906 | 0.16763 | 0.023574 | 0.024622 | 0.02534 | 0.077464 | 0.10847 | -0.003205 | 0.043324 | 0.13873 | 0.073606 | 0.05847 | -0.057067 | -0.00883 | -0.015177 | 0.015137 | 0.10039 | 0.058501 | 0.13067 | 0.088783
1943.4062 | 122.1771 | -121.8658 | 0.086975 | 0.14017 | -0.022205 | -0.007421 | -0.002124 | 0.040843 | 0.067269 | -0.039826 | 0.011281 | 0.11127 | 0.036985 | 0.026427 | -0.08911 | -0.036295 | -0.042641 | -0.00775 | 0.17221 | 0.009838 | 0.024622 | 0.029919 | 0.072886 | 0.099312 | -0.007783 | 0.043324 | 0.14331 | 0.069028 | 0.05847 | -0.057067 | -0.004252 | -0.010598 | 0.024293 | 0.10039 | 0.053922 | 0.12609 | 0.079626
1945.1562 | 122.1405 | -121.8704 | 0.086975 | 0.14017 | -0.022205 | -0.007421 | -0.002124 | 0.045421 | 0.071848 | -0.039826 | 0.006703 | 0.11127 | 0.041563 | 0.021847 | -0.093688 | -0.031717 | -0.042641 | -0.016906 | 0.17221 | 0.009838 | 0.024622 | 0.029919 | 0.077464 | 0.10389 | -0.007783 | 0.038746 | 0.14331 | 0.073606 | 0.05389 | -0.061645 | 0.000326 | -0.010598 | 0.015137 | 0.10039 | 0.049344 | 0.13525 | 0.084204
1946.8438 | 122.0215 | -121.907 | 0.11902 | 0.14932 | -0.017627 | -0.012 | 0.002454 | 0.045421 | 0.071848 | -0.035248 | 0.006703 | 0.11127 | 0.027829 | 0.021847 | -0.084531 | -0.031717 | -0.04722 | -0.016906 | 0.18136 | 0.014416 | 0.020043 | 0.034497 | 0.077464 | 0.10389 | -0.003205 | 0.038746 | 0.14331 | 0.059872 | 0.05389 | -0.052488 | 0.000326 | -0.015177 | 0.015137 | 0.091234 | 0.053923 | 0.11236 | 0.075049
1948.6094 | 122.1909 | -121.8613 | 0.082397 | 0.14932 | -0.022205 | -0.007421 | 0.002454 | 0.036265 | 0.071848 | -0.039826 | 0.006703 | 0.11127 | 0.032407 | 0.017268 | -0.084531 | -0.031717 | -0.04722 | -0.016906 | 0.18136 | 0.009838 | 0.024622 | 0.034497 | 0.068308 | 0.10389 | -0.007783 | 0.038746 | 0.14331 | 0.06445 | 0.049311 | -0.052488 | 0.000326 | -0.015177 | 0.015137 | 0.091234 | 0.053923 | 0.11694 | 0.079627
1950.2969 | 122.0901 | -121.8979 | 0.1236 | 0.14474 | -0.013048 | -0.016578 | -0.002124 | 0.036265 | 0.071848 | -0.035248 | 0.006703 | 0.11127 | 0.036985 | 0.012689 | -0.08911 | -0.027139 | -0.051798 | -0.00775 | 0.17679 | 0.018995 | 0.015465 | 0.029919 | 0.068308 | 0.10389 | -0.003205 | 0.038746 | 0.14331 | 0.069028 | 0.044732 | -0.057067 | 0.004904 | -0.019755 | 0.024293 | 0.095813 | 0.058501 | 0.12609 | 0.088783
1952.0625 | 122.0581 | -121.9025 | 0.1236 | 0.14017 | -0.022205 | -0.012 | 0.002454 | 0.036265 | 0.076426 | -0.039826 | 0.006703 | 0.10669 | 0.041563 | 0.017268 | -0.084531 | -0.031717 | -0.04722 | -0.016906 | 0.17221 | 0.009838 | 0.020043 | 0.034497 | 0.068308 | 0.10847 | -0.007783 | 0.038746 | 0.13873 | 0.073606 | 0.049311 | -0.052488 | 0.000326 | -0.015177 | 0.015137 | 0.091234 | 0.053923 | 0.12609 | 0.088783
1953.75 | 122.0901 | -121.9025 | 0.11444 | 0.13559 | -0.022205 | -0.007421 | -0.006703 | 0.040843 | 0.076426 | -0.039826 | 0.002124 | 0.10669 | 0.032407 | 0.017268 | -0.093688 | -0.036295 | -0.042641 | -0.021484 | 0.16763 | 0.009838 | 0.024622 | 0.02534 | 0.072886 | 0.10847 | -0.007783 | 0.034167 | 0.13873 | 0.06445 | 0.049311 | -0.061645 | -0.004252 | -0.010598 | 0.010559 | 0.095812 | 0.044765 | 0.12609 | 0.075048
1955.5 | 122.0947 | -121.8979 | 0.10529 | 0.14474 | -0.017627 | -0.012 | -0.006703 | 0.045421 | 0.071848 | -0.039826 | 0.006703 | 0.11127 | 0.032407 | 0.021847 | -0.084531 | -0.031717 | -0.042641 | -0.012328 | 0.17679 | 0.014416 | 0.020043 | 0.02534 | 0.077464 | 0.10389 | -0.007783 | 0.038746 | 0.14331 | 0.06445 | 0.05389 | -0.052488 | 0.000326 | -0.010598 | 0.019715 | 0.091234 | 0.049344 | 0.11694 | 0.075048
1957.1875 | 122.1909 | -121.8796 | 0.10071 | 0.13559 | -0.026784 | -0.007421 | -0.002124 | 0.031687 | 0.081005 | -0.039826 | 0.002124 | 0.10669 | 0.041563 | 0.017268 | -0.093688 | -0.040873 | -0.042641 | -0.012328 | 0.16763 | 0.005259 | 0.024622 | 0.029919 | 0.06373 | 0.11305 | -0.007783 | 0.034167 | 0.13873 | 0.073606 | 0.049311 | -0.061645 | -0.00883 | -0.010598 | 0.019715 | 0.095812 | 0.044765 | 0.13525 | 0.084204
1958.9375 | 122.2092 | -121.8842 | 0.086975 | 0.14017 | -0.017627 | -0.007421 | -0.002124 | 0.040843 | 0.076426 | -0.048983 | 0.006703 | 0.11585 | 0.036985 | 0.021847 | -0.08911 | -0.031717 | -0.04722 | -0.00775 | 0.17221 | 0.014416 | 0.024622 | 0.029919 | 0.072886 | 0.10847 | -0.01694 | 0.038746 | 0.14789 | 0.069028 | 0.05389 | -0.057067 | 0.000326 | -0.015177 | 0.024293 | 0.095813 | 0.053923 | 0.12609 | 0.084205
1960.6406 | 122.0718 | -121.9299 | 0.11902 | 0.14474 | -0.022205 | -0.012 | 0.002454 | 0.040843 | 0.076426 | -0.035248 | 0.011281 | 0.11585 | 0.036985 | 0.017268 | -0.093688 | -0.031717 | -0.051798 | -0.016906 | 0.17679 | 0.009838 | 0.020043 | 0.034497 | 0.072886 | 0.10847 | -0.003205 | 0.043324 | 0.14789 | 0.069028 | 0.049311 | -0.061645 | 0.000326 | -0.019755 | 0.015137 | 0.10497 | 0.063079 | 0.13067 | 0.088783
1962.4062 | 122.0993 | -121.8979 | 0.11444 | 0.14017 | -0.008469 | -0.012 | -0.006703 | 0.040843 | 0.081005 | -0.035248 | 0.006703 | 0.11585 | 0.036985 | 0.021847 | -0.08911 | -0.027139 | -0.04722 | -0.016906 | 0.17221 | 0.023574 | 0.020043 | 0.02534 | 0.072886 | 0.11305 | -0.003205 | 0.038746 | 0.14789 | 0.069028 | 0.05389 | -0.057067 | 0.004904 | -0.015177 | 0.015137 | 0.095813 | 0.053923 | 0.12609 | 0.084205
1964.1406 | 122.1405 | -121.8979 | 0.09613 | 0.14474 | -0.022205 | -0.016578 | 0.002454 | 0.045421 | 0.071848 | -0.039826 | 0.011281 | 0.11585 | 0.041563 | 0.012689 | -0.093688 | -0.036295 | -0.04722 | -0.026063 | 0.17679 | 0.009838 | 0.015465 | 0.034497 | 0.077464 | 0.10389 | -0.007783 | 0.043324 | 0.14789 | 0.073606 | 0.044732 | -0.061645 | -0.004252 | -0.015177 | 0.00598 | 0.10497 | 0.058501 | 0.13525 | 0.088783
1965.8281 | 122.2046 | -121.9025 | 0.09613 | 0.13101 | -0.017627 | -0.012 | -0.002124 | 0.036265 | 0.071848 | -0.039826 | 0.006703 | 0.11585 | 0.041563 | 0.021847 | -0.084531 | -0.031717 | -0.04722 | -0.012328 | 0.16305 | 0.014416 | 0.020043 | 0.029919 | 0.068308 | 0.10389 | -0.007783 | 0.038746 | 0.14789 | 0.073606 | 0.05389 | -0.052488 | 0.000326 | -0.015177 | 0.019715 | 0.091234 | 0.053923 | 0.12609 | 0.088783
1967.5781 | 122.1222 | -121.9208 | 0.091553 | 0.13559 | -0.017627 | -0.012 | -0.006703 | 0.040843 | 0.067269 | -0.039826 | 0.006703 | 0.11585 | 0.032407 | 0.017268 | -0.093688 | -0.031717 | -0.04722 | -0.016906 | 0.16763 | 0.014416 | 0.020043 | 0.02534 | 0.072886 | 0.099312 | -0.007783 | 0.038746 | 0.14789 | 0.06445 | 0.049311 | -0.061645 | 0.000326 | -0.015177 | 0.015137 | 0.10039 | 0.053923 | 0.12609 | 0.079627
1969.2812 | 122.081 | -121.9345 | 0.10986 | 0.14474 | -0.022205 | -0.012 | -0.006703 | 0.045421 | 0.071848 | -0.039826 | 0.011281 | 0.11127 | 0.041563 | 0.017268 | -0.08911 | -0.031717 | -0.038063 | -0.016906 | 0.17679 | 0.009838 | 0.020043 | 0.02534 | 0.077464 | 0.10389 | -0.007783 | 0.043324 | 0.14331 | 0.073606 | 0.049311 | -0.057067 | 0.000326 | -0.00602 | 0.015137 | 0.10039 | 0.049344 | 0.13067 | 0.079626
1971.0312 | 122.1954 | -121.8979 | 0.082397 | 0.14017 | -0.017627 | -0.012 | -0.002124 | 0.036265 | 0.071848 | -0.044405 | 0.011281 | 0.11585 | 0.032407 | 0.021847 | -0.08911 | -0.036295 | -0.04722 | -0.021484 | 0.17221 | 0.014416 | 0.020043 | 0.029919 | 0.068308 | 0.10389 | -0.012362 | 0.043324 | 0.14789 | 0.06445 | 0.05389 | -0.057067 | -0.004252 | -0.015177 | 0.010559 | 0.10039 | 0.058501 | 0.12152 | 0.079627
1972.7656 | 122.113 | -121.9345 | 0.11902 | 0.14474 | -0.013048 | -0.002842 | 0.002454 | 0.045421 | 0.071848 | -0.035248 | -0.002454 | 0.11127 | 0.027829 | 0.021847 | -0.10742 | -0.036295 | -0.04722 | -0.016906 | 0.17679 | 0.018995 | 0.029201 | 0.034497 | 0.077464 | 0.10389 | -0.003205 | 0.029589 | 0.14331 | 0.059872 | 0.05389 | -0.075379 | -0.004252 | -0.015177 | 0.015137 | 0.10497 | 0.044766 | 0.13525 | 0.075049
1974.5312 | 122.1954 | -121.875 | 0.086975 | 0.13559 | -0.017627 | -0.012 | -0.006703 | 0.045421 | 0.062691 | -0.035248 | 0.006703 | 0.11127 | 0.041563 | 0.017268 | -0.08911 | -0.036295 | -0.042641 | -0.00775 | 0.16763 | 0.014416 | 0.020043 | 0.02534 | 0.077464 | 0.094734 | -0.003205 | 0.038746 | 0.14331 | 0.073606 | 0.049311 | -0.057067 | -0.004252 | -0.010598 | 0.024293 | 0.095813 | 0.049344 | 0.13067 | 0.084204
1976.2344 | 122.1817 | -121.8887 | 0.091553 | 0.13559 | -0.017627 | -0.007421 | -0.006703 | 0.040843 | 0.067269 | -0.044405 | 0.006703 | 0.11127 | 0.036985 | 0.026427 | -0.093688 | -0.036295 | -0.038063 | -0.00775 | 0.16763 | 0.014416 | 0.024622 | 0.02534 | 0.072886 | 0.099312 | -0.012362 | 0.038746 | 0.14331 | 0.069028 | 0.05847 | -0.061645 | -0.004252 | -0.00602 | 0.024293 | 0.10039 | 0.044766 | 0.13067 | 0.075048
1977.9844 | 122.1268 | -121.9254 | 0.11902 | 0.14474 | -0.022205 | -0.007421 | -0.002124 | 0.045421 | 0.071848 | -0.035248 | 0.011281 | 0.11127 | 0.032407 | 0.021847 | -0.093688 | -0.040873 | -0.04722 | -0.021484 | 0.17679 | 0.009838 | 0.024622 | 0.029919 | 0.077464 | 0.10389 | -0.003205 | 0.043324 | 0.14331 | 0.06445 | 0.05389 | -0.061645 | -0.00883 | -0.015177 | 0.010559 | 0.10497 | 0.058501 | 0.12609 | 0.079627
1979.7344 | 122.0718 | -121.9345 | 0.10986 | 0.14017 | -0.022205 | -0.012 | -0.002124 | 0.040843 | 0.071848 | -0.044405 | 0.002124 | 0.11127 | 0.036985 | 0.021847 | -0.093688 | -0.031717 | -0.051798 | -0.026063 | 0.17221 | 0.009838 | 0.020043 | 0.029919 | 0.072886 | 0.10389 | -0.012362 | 0.034167 | 0.14331 | 0.069028 | 0.05389 | -0.061645 | 0.000326 | -0.019755 | 0.00598 | 0.095812 | 0.053922 | 0.13067 | 0.088783
1981.4844 | 122.2092 | -121.9208 | 0.073242 | 0.14474 | -0.022205 | -0.016578 | -0.002124 | 0.045421 | 0.081005 | -0.035248 | 0.006703 | 0.11585 | 0.032407 | 0.017268 | -0.08911 | -0.036295 | -0.051798 | -0.00775 | 0.17679 | 0.009838 | 0.015465 | 0.029919 | 0.077464 | 0.11305 | -0.003205 | 0.038746 | 0.14789 | 0.06445 | 0.049311 | -0.057067 | -0.004252 | -0.019755 | 0.024293 | 0.095813 | 0.058501 | 0.12152 | 0.084205
1983.2344 | 122.113 | -121.9299 | 0.10071 | 0.14017 | -0.017627 | -0.007421 | -0.002124 | 0.045421 | 0.076426 | -0.039826 | 0.002124 | 0.11127 | 0.041563 | 0.021847 | -0.084531 | -0.031717 | -0.042641 | -0.012328 | 0.17221 | 0.014416 | 0.024622 | 0.029919 | 0.077464 | 0.10847 | -0.007783 | 0.034167 | 0.14331 | 0.073606 | 0.05389 | -0.052488 | 0.000326 | -0.010598 | 0.019715 | 0.086655 | 0.044765 | 0.12609 | 0.084204
1984.9844 | 122.113 | -121.9391 | 0.10529 | 0.14474 | -0.013048 | -0.012 | -0.002124 | 0.040843 | 0.071848 | -0.039826 | 0.006703 | 0.11127 | 0.046142 | 0.021847 | -0.08911 | -0.031717 | -0.04722 | -0.016906 | 0.17679 | 0.018995 | 0.020043 | 0.029919 | 0.072886 | 0.10389 | -0.007783 | 0.038746 | 0.14331 | 0.078185 | 0.05389 | -0.057067 | 0.000326 | -0.015177 | 0.015137 | 0.095813 | 0.053923 | 0.13525 | 0.093362
1986.6719 | 122.1313 | -121.9345 | 0.10071 | 0.14017 | -0.017627 | -0.012 | -0.002124 | 0.036265 | 0.076426 | -0.039826 | 0.002124 | 0.11127 | 0.036985 | 0.021847 | -0.079953 | -0.031717 | -0.051798 | -0.012328 | 0.17221 | 0.014416 | 0.020043 | 0.029919 | 0.068308 | 0.10847 | -0.007783 | 0.034167 | 0.14331 | 0.069028 | 0.05389 | -0.04791 | 0.000326 | -0.019755 | 0.019715 | 0.082077 | 0.053922 | 0.11694 | 0.088783
1988.4219 | 122.1359 | -121.9208 | 0.10986 | 0.14474 | -0.022205 | -0.012 | -0.002124 | 0.031687 | 0.071848 | -0.039826 | 0.011281 | 0.11127 | 0.041563 | 0.017268 | -0.084531 | -0.036295 | -0.04722 | -0.021484 | 0.17679 | 0.009838 | 0.020043 | 0.029919 | 0.06373 | 0.10389 | -0.007783 | 0.043324 | 0.14331 | 0.073606 | 0.049311 | -0.052488 | -0.004252 | -0.015177 | 0.010559 | 0.095812 | 0.058501 | 0.12609 | 0.088783
1990.125 | 122.1085 | -121.9666 | 0.11902 | 0.13101 | -0.022205 | -0.012 | 0.002454 | 0.040843 | 0.076426 | -0.035248 | 0.002124 | 0.10211 | 0.036985 | 0.021847 | -0.084531 | -0.031717 | -0.042641 | -0.012328 | 0.16305 | 0.009838 | 0.020043 | 0.034497 | 0.072886 | 0.10847 | -0.003205 | 0.034167 | 0.13415 | 0.069028 | 0.05389 | -0.052488 | 0.000326 | -0.010598 | 0.019715 | 0.086655 | 0.044765 | 0.12152 | 0.079626
1991.875 | 122.1863 | -121.907 | 0.09613 | 0.13101 | -0.017627 | -0.016578 | -0.006703 | 0.036265 | 0.076426 | -0.039826 | 0.006703 | 0.11127 | 0.036985 | 0.021847 | -0.084531 | -0.036295 | -0.056376 | -0.016906 | 0.16305 | 0.014416 | 0.015465 | 0.02534 | 0.068308 | 0.10847 | -0.007783 | 0.038746 | 0.14331 | 0.069028 | 0.05389 | -0.052488 | -0.004252 | -0.024333 | 0.015137 | 0.091234 | 0.063079 | 0.12152 | 0.093361
1993.625 | 122.1542 | -121.9345 | 0.086975 | 0.14017 | -0.026784 | -0.012 | 0.002454 | 0.031687 | 0.076426 | -0.035248 | 0.011281 | 0.11585 | 0.041563 | 0.017268 | -0.08911 | -0.031717 | -0.042641 | -0.012328 | 0.17221 | 0.005259 | 0.020043 | 0.034497 | 0.06373 | 0.10847 | -0.003205 | 0.043324 | 0.14789 | 0.073606 | 0.049311 | -0.057067 | 0.000326 | -0.010598 | 0.019715 | 0.10039 | 0.053922 | 0.13067 | 0.084204
1995.375 | 122.2137 | -121.907 | 0.086975 | 0.14017 | -0.031363 | -0.012 | -0.006703 | 0.031687 | 0.071848 | -0.044405 | 0.002124 | 0.11585 | 0.036985 | 0.012689 | -0.093688 | -0.031717 | -0.051798 | -0.016906 | 0.17221 | 0.00068 | 0.020043 | 0.02534 | 0.06373 | 0.10389 | -0.012362 | 0.034167 | 0.14789 | 0.069028 | 0.044732 | -0.061645 | 0.000326 | -0.019755 | 0.015137 | 0.095812 | 0.053922 | 0.13067 | 0.088783
1997.125 | 122.1085 | -121.9528 | 0.10529 | 0.14017 | -0.022205 | -0.012 | 0.002454 | 0.045421 | 0.071848 | -0.03067 | 0.011281 | 0.11585 | 0.041563 | 0.017268 | -0.08911 | -0.031717 | -0.04722 | -0.016906 | 0.17221 | 0.009838 | 0.020043 | 0.034497 | 0.077464 | 0.10389 | 0.001373 | 0.043324 | 0.14789 | 0.073606 | 0.049311 | -0.057067 | 0.000326 | -0.015177 | 0.015137 | 0.10039 | 0.058501 | 0.13067 | 0.088783
1998.8125 | 122.1497 | -121.9299 | 0.09613 | 0.14017 | -0.017627 | -0.007421 | -0.002124 | 0.040843 | 0.076426 | -0.039826 | 0.002124 | 0.11585 | 0.027829 | 0.021847 | -0.08911 | -0.031717 | -0.042641 | -0.026063 | 0.17221 | 0.014416 | 0.024622 | 0.029919 | 0.072886 | 0.10847 | -0.007783 | 0.034167 | 0.14789 | 0.059872 | 0.05389 | -0.057067 | 0.000326 | -0.010598 | 0.00598 | 0.091234 | 0.044765 | 0.11694 | 0.07047
2000.5781 | 122.2229 | -121.9025 | 0.086975 | 0.14017 | -0.017627 | -0.012 | 0.002454 | 0.036265 | 0.071848 | -0.044405 | 0.011281 | 0.11585 | 0.041563 | 0.021847 | -0.084531 | -0.040873 | -0.04722 | -0.016906 | 0.17221 | 0.014416 | 0.020043 | 0.034497 | 0.068308 | 0.10389 | -0.012362 | 0.043324 | 0.14789 | 0.073606 | 0.05389 | -0.052488 | -0.00883 | -0.015177 | 0.015137 | 0.095812 | 0.058501 | 0.12609 | 0.088783
2002.2812 | 122.1863 | -121.9482 | 0.10071 | 0.14017 | -0.017627 | -0.012 | -0.006703 | 0.031687 | 0.067269 | -0.039826 | 0.011281 | 0.12043 | 0.036985 | 0.021847 | -0.079953 | -0.036295 | -0.04722 | -0.012328 | 0.17221 | 0.014416 | 0.020043 | 0.02534 | 0.06373 | 0.099312 | -0.007783 | 0.043324 | 0.15247 | 0.069028 | 0.05389 | -0.04791 | -0.004252 | -0.015177 | 0.019715 | 0.091234 | 0.058501 | 0.11694 | 0.084205
2004.0312 | 122.1405 | -121.9574 | 0.11444 | 0.14017 | -0.017627 | -0.012 | 0.002454 | 0.036265 | 0.076426 | -0.039826 | 0.006703 | 0.11127 | 0.032407 | 0.017268 | -0.093688 | -0.036295 | -0.04722 | -0.012328 | 0.17221 | 0.014416 | 0.020043 | 0.034497 | 0.068308 | 0.10847 | -0.007783 | 0.038746 | 0.14331 | 0.06445 | 0.049311 | -0.061645 | -0.004252 | -0.015177 | 0.019715 | 0.10039 | 0.053923 | 0.12609 | 0.079627
2005.7812 | 122.2321 | -121.9345 | 0.073242 | 0.13559 | -0.022205 | -0.012 | 0.002454 | 0.036265 | 0.076426 | -0.039826 | 0.011281 | 0.11585 | 0.032407 | 0.017268 | -0.08911 | -0.031717 | -0.042641 | -0.00775 | 0.16763 | 0.009838 | 0.020043 | 0.034497 | 0.068308 | 0.10847 | -0.007783 | 0.043324 | 0.14789 | 0.06445 | 0.049311 | -0.057067 | 0.000326 | -0.010598 | 0.024293 | 0.10039 | 0.053922 | 0.12152 | 0.075048
2007.5312 | 122.1268 | -121.9299 | 0.10986 | 0.14932 | -0.022205 | -0.007421 | -0.002124 | 0.040843 | 0.067269 | -0.044405 | 0.006703 | 0.11127 | 0.036985 | 0.026427 | -0.093688 | -0.031717 | -0.042641 | -0.021484 | 0.18136 | 0.009838 | 0.024622 | 0.029919 | 0.072886 | 0.099312 | -0.012362 | 0.038746 | 0.14331 | 0.069028 | 0.05847 | -0.061645 | 0.000326 | -0.010598 | 0.010559 | 0.10039 | 0.049344 | 0.13067 | 0.079626
2009.2812 | 122.1497 | -121.962 | 0.10529 | 0.14932 | -0.026784 | -0.007421 | -0.002124 | 0.031687 | 0.081005 | -0.039826 | 0.006703 | 0.11127 | 0.036985 | 0.021847 | -0.08911 | -0.031717 | -0.051798 | -0.012328 | 0.18136 | 0.005259 | 0.024622 | 0.029919 | 0.06373 | 0.11305 | -0.007783 | 0.038746 | 0.14331 | 0.069028 | 0.05389 | -0.057067 | 0.000326 | -0.019755 | 0.019715 | 0.095813 | 0.058501 | 0.12609 | 0.088783
2011.0312 | 122.2321 | -121.9116 | 0.086975 | 0.14474 | -0.022205 | -0.012 | -0.002124 | 0.036265 | 0.067269 | -0.048983 | 0.006703 | 0.11127 | 0.036985 | 0.017268 | -0.098266 | -0.036295 | -0.042641 | -0.016906 | 0.17679 | 0.009838 | 0.020043 | 0.029919 | 0.068308 | 0.099312 | -0.01694 | 0.038746 | 0.14331 | 0.069028 | 0.049311 | -0.066223 | -0.004252 | -0.010598 | 0.015137 | 0.10497 | 0.049344 | 0.13525 | 0.079626
2012.7812 | 122.1588 | -121.9482 | 0.10986 | 0.14017 | -0.026784 | -0.012 | 0.002454 | 0.040843 | 0.071848 | -0.044405 | 0.011281 | 0.10669 | 0.036985 | 0.026427 | -0.08911 | -0.031717 | -0.051798 | -0.012328 | 0.17221 | 0.005259 | 0.020043 | 0.034497 | 0.072886 | 0.10389 | -0.012362 | 0.043324 | 0.13873 | 0.069028 | 0.05847 | -0.057067 | 0.000326 | -0.019755 | 0.019715 | 0.10039 | 0.063079 | 0.12609 | 0.088783
2014.4688 | 122.1405 | -121.9666 | 0.11902 | 0.14474 | -0.017627 | -0.012 | -0.002124 | 0.045421 | 0.071848 | -0.039826 | 0.011281 | 0.12043 | 0.036985 | 0.017268 | -0.084531 | -0.031717 | -0.04722 | -0.016906 | 0.17679 | 0.014416 | 0.020043 | 0.029919 | 0.077464 | 0.10389 | -0.007783 | 0.043324 | 0.15247 | 0.069028 | 0.049311 | -0.052488 | 0.000326 | -0.015177 | 0.015137 | 0.095812 | 0.058501 | 0.12152 | 0.084205
2016.2188 | 122.1954 | -121.9391 | 0.09613 | 0.14017 | -0.022205 | -0.012 | 0.002454 | 0.036265 | 0.076426 | -0.039826 | 0.011281 | 0.11127 | 0.041563 | 0.021847 | -0.08911 | -0.027139 | -0.04722 | -0.016906 | 0.17221 | 0.009838 | 0.020043 | 0.034497 | 0.068308 | 0.10847 | -0.007783 | 0.043324 | 0.14331 | 0.073606 | 0.05389 | -0.057067 | 0.004904 | -0.015177 | 0.015137 | 0.10039 | 0.058501 | 0.13067 | 0.088783
2017.9844 | 122.1359 | -121.9711 | 0.10986 | 0.14017 | -0.022205 | -0.012 | -0.002124 | 0.040843 | 0.081005 | -0.044405 | 0.01586 | 0.11585 | 0.027829 | 0.026427 | -0.08911 | -0.040873 | -0.04722 | -0.021484 | 0.17221 | 0.009838 | 0.020043 | 0.029919 | 0.072886 | 0.11305 | -0.012362 | 0.047903 | 0.14789 | 0.059872 | 0.05847 | -0.057067 | -0.00883 | -0.015177 | 0.010559 | 0.10497 | 0.06308 | 0.11694 | 0.075049
2019.6719 | 122.0993 | -121.9574 | 0.11902 | 0.14474 | -0.026784 | -0.012 | -0.002124 | 0.040843 | 0.071848 | -0.039826 | 0.011281 | 0.10669 | 0.018672 | 0.017268 | -0.08911 | -0.040873 | -0.042641 | -0.021484 | 0.17679 | 0.005259 | 0.020043 | 0.029919 | 0.072886 | 0.10389 | -0.007783 | 0.043324 | 0.13873 | 0.050715 | 0.049311 | -0.057067 | -0.00883 | -0.010598 | 0.010559 | 0.10039 | 0.053922 | 0.10778 | 0.061313
2021.4219 | 122.0901 | -121.9803 | 0.1236 | 0.14017 | -0.022205 | -0.016578 | 0.002454 | 0.036265 | 0.071848 | -0.039826 | 0.011281 | 0.11585 | 0.009515 | 0.021847 | -0.08911 | -0.027139 | -0.051798 | -0.012328 | 0.17221 | 0.009838 | 0.015465 | 0.034497 | 0.068308 | 0.10389 | -0.007783 | 0.043324 | 0.14789 | 0.041558 | 0.05389 | -0.057067 | 0.004904 | -0.019755 | 0.019715 | 0.10039 | 0.063079 | 0.098625 | 0.061313
2023.1719 | 122.2 | -121.9528 | 0.091553 | 0.14017 | -0.022205 | -0.012 | -0.002124 | 0.045421 | 0.081005 | -0.039826 | 0.006703 | 0.12043 | 0.014094 | 0.017268 | -0.08911 | -0.036295 | -0.04722 | -0.016906 | 0.17221 | 0.009838 | 0.020043 | 0.029919 | 0.077464 | 0.11305 | -0.007783 | 0.038746 | 0.15247 | 0.046137 | 0.049311 | -0.057067 | -0.004252 | -0.015177 | 0.015137 | 0.095813 | 0.053923 | 0.1032 | 0.061314
2024.8594 | 122.1085 | -121.9757 | 0.10071 | 0.14017 | -0.026784 | -0.007421 | -0.006703 | 0.040843 | 0.071848 | -0.039826 | 0.006703 | 0.11585 | 0.018672 | 0.021847 | -0.079953 | -0.036295 | -0.04722 | -0.00775 | 0.17221 | 0.005259 | 0.024622 | 0.02534 | 0.072886 | 0.10389 | -0.007783 | 0.038746 | 0.14789 | 0.050715 | 0.05389 | -0.04791 | -0.004252 | -0.015177 | 0.024293 | 0.086656 | 0.053923 | 0.098625 | 0.065892
2026.6094 | 122.1817 | -121.9574 | 0.082397 | 0.14017 | -0.026784 | -0.012 | 0.002454 | 0.036265 | 0.071848 | -0.039826 | 0.006703 | 0.12043 | 0.014094 | 0.021847 | -0.084531 | -0.031717 | -0.056376 | -0.012328 | 0.17221 | 0.005259 | 0.020043 | 0.034497 | 0.068308 | 0.10389 | -0.007783 | 0.038746 | 0.15247 | 0.046137 | 0.05389 | -0.052488 | 0.000326 | -0.024333 | 0.019715 | 0.091234 | 0.063079 | 0.098625 | 0.07047
2028.2969 | 122.1588 | -121.962 | 0.10529 | 0.14017 | -0.026784 | -0.007421 | -0.006703 | 0.036265 | 0.071848 | -0.035248 | 0.006703 | 0.11127 | 0.014094 | 0.021847 | -0.084531 | -0.027139 | -0.04722 | -0.016906 | 0.17221 | 0.005259 | 0.024622 | 0.02534 | 0.068308 | 0.10389 | -0.003205 | 0.038746 | 0.14331 | 0.046137 | 0.05389 | -0.052488 | 0.004904 | -0.015177 | 0.015137 | 0.091234 | 0.053923 | 0.098625 | 0.061314
2030.0469 | 122.2366 | -121.9162 | 0.091553 | 0.14017 | -0.022205 | -0.012 | 0.007033 | 0.045421 | 0.067269 | -0.035248 | 0.006703 | 0.11585 | 0.018672 | 0.021847 | -0.08911 | -0.031717 | -0.051798 | -0.00775 | 0.17221 | 0.009838 | 0.020043 | 0.039076 | 0.077464 | 0.099312 | -0.003205 | 0.038746 | 0.14789 | 0.050715 | 0.05389 | -0.057067 | 0.000326 | -0.019755 | 0.024293 | 0.095813 | 0.058501 | 0.10778 | 0.07047
2031.7969 | 122.1405 | -121.9574 | 0.091553 | 0.14474 | -0.026784 | -0.012 | 0.007033 | 0.040843 | 0.071848 | -0.044405 | 0.006703 | 0.12043 | 0.014094 | 0.021847 | -0.08911 | -0.031717 | -0.038063 | -0.016906 | 0.17679 | 0.005259 | 0.020043 | 0.039076 | 0.072886 | 0.10389 | -0.012362 | 0.038746 | 0.15247 | 0.046137 | 0.05389 | -0.057067 | 0.000326 | -0.00602 | 0.015137 | 0.095813 | 0.044766 | 0.1032 | 0.052157
2033.5312 | 122.2046 | -121.9666 | 0.07782 | 0.14474 | -0.026784 | -0.007421 | -0.006703 | 0.040843 | 0.071848 | -0.048983 | 0.006703 | 0.11127 | 0.014094 | 0.017268 | -0.084531 | -0.036295 | -0.051798 | -0.016906 | 0.17679 | 0.005259 | 0.024622 | 0.02534 | 0.072886 | 0.10389 | -0.01694 | 0.038746 | 0.14331 | 0.046137 | 0.049311 | -0.052488 | -0.004252 | -0.019755 | 0.015137 | 0.091234 | 0.058501 | 0.098625 | 0.065892
2035.2656 | 122.1909 | -121.9574 | 0.073242 | 0.14017 | -0.026784 | -0.016578 | 0.002454 | 0.045421 | 0.071848 | -0.039826 | 0.011281 | 0.12043 | 0.018672 | 0.026427 | -0.08911 | -0.040873 | -0.042641 | -0.016906 | 0.17221 | 0.005259 | 0.015465 | 0.034497 | 0.077464 | 0.10389 | -0.007783 | 0.043324 | 0.15247 | 0.050715 | 0.05847 | -0.057067 | -0.00883 | -0.010598 | 0.015137 | 0.10039 | 0.053922 | 0.10778 | 0.061313
2037.0469 | 122.2778 | -121.9299 | 0.086975 | 0.14017 | -0.026784 | -0.016578 | -0.006703 | 0.036265 | 0.081005 | -0.039826 | 0.002124 | 0.11127 | 0.014094 | 0.021847 | -0.084531 | -0.031717 | -0.04722 | -0.016906 | 0.17221 | 0.005259 | 0.015465 | 0.02534 | 0.068308 | 0.11305 | -0.007783 | 0.034167 | 0.14331 | 0.046137 | 0.05389 | -0.052488 | 0.000326 | -0.015177 | 0.015137 | 0.086655 | 0.049344 | 0.098625 | 0.061314
2038.7344 | 122.1405 | -121.9803 | 0.09613 | 0.14474 | -0.026784 | -0.012 | 0.007033 | 0.045421 | 0.071848 | -0.044405 | 0.006703 | 0.10669 | 0.014094 | 0.017268 | -0.093688 | -0.040873 | -0.051798 | -0.026063 | 0.17679 | 0.005259 | 0.020043 | 0.039076 | 0.077464 | 0.10389 | -0.012362 | 0.038746 | 0.13873 | 0.046137 | 0.049311 | -0.061645 | -0.00883 | -0.019755 | 0.00598 | 0.10039 | 0.058501 | 0.10778 | 0.065892
2040.4844 | 122.2458 | -121.9437 | 0.082397 | 0.13559 | -0.022205 | -0.012 | -0.002124 | 0.045421 | 0.071848 | -0.044405 | 0.011281 | 0.11585 | 0.014094 | 0.021847 | -0.084531 | -0.031717 | -0.051798 | -0.012328 | 0.16763 | 0.009838 | 0.020043 | 0.029919 | 0.077464 | 0.10389 | -0.012362 | 0.043324 | 0.14789 | 0.046137 | 0.05389 | -0.052488 | 0.000326 | -0.019755 | 0.019715 | 0.095812 | 0.063079 | 0.098625 | 0.065892
2042.2344 | 122.1085 | -121.9849 | 0.10986 | 0.14017 | -0.031363 | -0.012 | 0.002454 | 0.036265 | 0.071848 | -0.039826 | 0.011281 | 0.11127 | 0.014094 | 0.021847 | -0.08911 | -0.031717 | -0.051798 | -0.00775 | 0.17221 | 0.00068 | 0.020043 | 0.034497 | 0.068308 | 0.10389 | -0.007783 | 0.043324 | 0.14331 | 0.046137 | 0.05389 | -0.057067 | 0.000326 | -0.019755 | 0.024293 | 0.10039 | 0.063079 | 0.1032 | 0.065892
2044 | 122.1176 | -121.994 | 0.10529 | 0.14474 | -0.026784 | -0.007421 | -0.006703 | 0.036265 | 0.071848 | -0.044405 | 0.011281 | 0.12043 | 0.009515 | 0.026427 | -0.093688 | -0.040873 | -0.04722 | -0.012328 | 0.17679 | 0.005259 | 0.024622 | 0.02534 | 0.068308 | 0.10389 | -0.012362 | 0.043324 | 0.15247 | 0.041558 | 0.05847 | -0.061645 | -0.00883 | -0.015177 | 0.019715 | 0.10497 | 0.058501 | 0.1032 | 0.056735
2045.75 | 122.1176 | -121.9986 | 0.11902 | 0.14017 | -0.031363 | -0.007421 | 0.002454 | 0.036265 | 0.076426 | -0.035248 | 0.01586 | 0.11127 | 0.014094 | 0.017268 | -0.08911 | -0.027139 | -0.04722 | -0.021484 | 0.17221 | 0.00068 | 0.024622 | 0.034497 | 0.068308 | 0.10847 | -0.003205 | 0.047903 | 0.14331 | 0.046137 | 0.049311 | -0.057067 | 0.004904 | -0.015177 | 0.010559 | 0.10497 | 0.06308 | 0.1032 | 0.061314
2047.4531 | 122.1817 | -121.9757 | 0.10986 | 0.14017 | -0.026784 | -0.007421 | -0.002124 | 0.045421 | 0.081005 | -0.035248 | 0.002124 | 0.11585 | 0.018672 | 0.026427 | -0.079953 | -0.031717 | -0.051798 | -0.012328 | 0.17221 | 0.005259 | 0.024622 | 0.029919 | 0.077464 | 0.11305 | -0.003205 | 0.034167 | 0.14789 | 0.050715 | 0.05847 | -0.04791 | 0.000326 | -0.019755 | 0.019715 | 0.082077 | 0.053922 | 0.098625 | 0.07047
2049.2031 | 122.1268 | -121.9986 | 0.10986 | 0.14017 | -0.022205 | -0.007421 | 0.002454 | 0.040843 | 0.076426 | -0.039826 | 0.006703 | 0.11585 | 0.018672 | 0.026427 | -0.084531 | -0.031717 | -0.051798 | -0.016906 | 0.17221 | 0.009838 | 0.024622 | 0.034497 | 0.072886 | 0.10847 | -0.007783 | 0.038746 | 0.14789 | 0.050715 | 0.05847 | -0.052488 | 0.000326 | -0.019755 | 0.015137 | 0.091234 | 0.058501 | 0.1032 | 0.07047
2050.9062 | 122.2275 | -121.9666 | 0.09613 | 0.14474 | -0.026784 | -0.012 | 0.002454 | 0.040843 | 0.071848 | -0.039826 | 0.006703 | 0.12043 | 0.018672 | 0.021847 | -0.084531 | -0.040873 | -0.051798 | -0.016906 | 0.17679 | 0.005259 | 0.020043 | 0.034497 | 0.072886 | 0.10389 | -0.007783 | 0.038746 | 0.15247 | 0.050715 | 0.05389 | -0.052488 | -0.00883 | -0.019755 | 0.015137 | 0.091234 | 0.058501 | 0.1032 | 0.07047
2052.6562 | 122.2961 | -121.9528 | 0.091553 | 0.14474 | -0.031363 | -0.012 | -0.002124 | 0.036265 | 0.076426 | -0.035248 | 0.020438 | 0.11585 | 0.018672 | 0.026427 | -0.093688 | -0.031717 | -0.056376 | -0.016906 | 0.17679 | 0.00068 | 0.020043 | 0.029919 | 0.068308 | 0.10847 | -0.003205 | 0.052481 | 0.14789 | 0.050715 | 0.05847 | -0.061645 | 0.000326 | -0.024333 | 0.015137 | 0.11413 | 0.076814 | 0.11236 | 0.075048
2054.4062 | 122.1268 | -122.0032 | 0.10529 | 0.14017 | -0.031363 | -0.012 | -0.002124 | 0.036265 | 0.067269 | -0.044405 | 0.006703 | 0.11585 | 0.018672 | 0.021847 | -0.08911 | -0.036295 | -0.04722 | -0.021484 | 0.17221 | 0.00068 | 0.020043 | 0.029919 | 0.068308 | 0.099312 | -0.012362 | 0.038746 | 0.14789 | 0.050715 | 0.05389 | -0.057067 | -0.004252 | -0.015177 | 0.010559 | 0.095813 | 0.053923 | 0.10778 | 0.065892
2056.1719 | 122.1817 | -121.9894 | 0.11444 | 0.14017 | -0.022205 | -0.007421 | 0.002454 | 0.040843 | 0.076426 | -0.039826 | 0.002124 | 0.11585 | 0.018672 | 0.017268 | -0.08911 | -0.031717 | -0.051798 | -0.012328 | 0.17221 | 0.009838 | 0.024622 | 0.034497 | 0.072886 | 0.10847 | -0.007783 | 0.034167 | 0.14789 | 0.050715 | 0.049311 | -0.057067 | 0.000326 | -0.019755 | 0.019715 | 0.091234 | 0.053922 | 0.10778 | 0.07047
2057.8594 | 122.2549 | -121.9574 | 0.07782 | 0.14474 | -0.026784 | -0.007421 | -0.006703 | 0.045421 | 0.076426 | -0.039826 | 0.006703 | 0.11585 | 0.014094 | 0.026427 | -0.08911 | -0.031717 | -0.04722 | -0.021484 | 0.17679 | 0.005259 | 0.024622 | 0.02534 | 0.077464 | 0.10847 | -0.007783 | 0.038746 | 0.14789 | 0.046137 | 0.05847 | -0.057067 | 0.000326 | -0.015177 | 0.010559 | 0.095813 | 0.053923 | 0.1032 | 0.061314
2059.625 | 122.1817 | -121.9757 | 0.10529 | 0.13559 | -0.031363 | -0.007421 | 0.002454 | 0.036265 | 0.076426 | -0.035248 | 0.006703 | 0.11585 | 0.014094 | 0.026427 | -0.08911 | -0.031717 | -0.042641 | -0.016906 | 0.16763 | 0.00068 | 0.024622 | 0.034497 | 0.068308 | 0.10847 | -0.003205 | 0.038746 | 0.14789 | 0.046137 | 0.05847 | -0.057067 | 0.000326 | -0.010598 | 0.015137 | 0.095813 | 0.049344 | 0.1032 | 0.056735
2061.3125 | 122.2549 | -121.9482 | 0.068665 | 0.14017 | -0.026784 | -0.012 | 0.002454 | 0.036265 | 0.067269 | -0.039826 | 0.006703 | 0.12043 | 0.009515 | 0.026427 | -0.08911 | -0.031717 | -0.042641 | -0.016906 | 0.17221 | 0.005259 | 0.020043 | 0.034497 | 0.068308 | 0.099312 | -0.007783 | 0.038746 | 0.15247 | 0.041558 | 0.05847 | -0.057067 | 0.000326 | -0.010598 | 0.015137 | 0.095813 | 0.049344 | 0.098625 | 0.052156
2063.0625 | 122.1497 | -121.9986 | 0.11444 | 0.14017 | -0.035942 | -0.012 | 0.002454 | 0.031687 | 0.076426 | -0.044405 | -0.002454 | 0.11127 | 0.018672 | 0.017268 | -0.08911 | -0.036295 | -0.042641 | -0.021484 | 0.17221 | -0.003899 | 0.020043 | 0.034497 | 0.06373 | 0.10847 | -0.012362 | 0.029589 | 0.14331 | 0.050715 | 0.049311 | -0.057067 | -0.004252 | -0.010598 | 0.010559 | 0.086656 | 0.040187 | 0.10778 | 0.061313
2064.75 | 122.1863 | -121.962 | 0.11444 | 0.13559 | -0.031363 | -0.012 | 0.002454 | 0.040843 | 0.067269 | -0.039826 | 0.01586 | 0.12043 | 0.009515 | 0.017268 | -0.098266 | -0.031717 | -0.04722 | -0.030641 | 0.16763 | 0.00068 | 0.020043 | 0.034497 | 0.072886 | 0.099312 | -0.007783 | 0.047903 | 0.15247 | 0.041558 | 0.049311 | -0.066223 | 0.000326 | -0.015177 | 0.001402 | 0.11413 | 0.06308 | 0.10778 | 0.056735
2066.5156 | 122.2504 | -121.962 | 0.091553 | 0.14474 | -0.026784 | -0.012 | -0.006703 | 0.040843 | 0.071848 | -0.048983 | 0.006703 | 0.12501 | 0.014094 | 0.021847 | -0.084531 | -0.036295 | -0.04722 | -0.030641 | 0.17679 | 0.005259 | 0.020043 | 0.02534 | 0.072886 | 0.10389 | -0.01694 | 0.038746 | 0.15705 | 0.046137 | 0.05389 | -0.052488 | -0.004252 | -0.015177 | 0.001402 | 0.091234 | 0.053923 | 0.098625 | 0.061314
2068.2656 | 122.1725 | -121.9711 | 0.10071 | 0.14017 | -0.031363 | -0.007421 | 0.002454 | 0.045421 | 0.071848 | -0.044405 | 0.011281 | 0.12043 | 0.02325 | 0.017268 | -0.084531 | -0.031717 | -0.042641 | -0.016906 | 0.17221 | 0.00068 | 0.024622 | 0.034497 | 0.077464 | 0.10389 | -0.012362 | 0.043324 | 0.15247 | 0.055293 | 0.049311 | -0.052488 | 0.000326 | -0.010598 | 0.015137 | 0.095812 | 0.053922 | 0.10778 | 0.065891
2070.0156 | 122.1222 | -122.0123 | 0.10986 | 0.14017 | -0.026784 | -0.007421 | 0.002454 | 0.036265 | 0.076426 | -0.035248 | 0.01586 | 0.12043 | 0.018672 | 0.021847 | -0.084531 | -0.022561 | -0.051798 | -0.016906 | 0.17221 | 0.005259 | 0.024622 | 0.034497 | 0.068308 | 0.10847 | -0.003205 | 0.047903 | 0.15247 | 0.050715 | 0.05389 | -0.052488 | 0.009482 | -0.019755 | 0.015137 | 0.10039 | 0.067658 | 0.1032 | 0.07047
2071.7031 | 122.2504 | -121.9803 | 0.073242 | 0.13559 | -0.031363 | -0.016578 | 0.011611 | 0.036265 | 0.067269 | -0.039826 | 0.006703 | 0.11585 | 0.018672 | 0.012689 | -0.084531 | -0.036295 | -0.04722 | -0.012328 | 0.16763 | 0.00068 | 0.015465 | 0.043654 | 0.068308 | 0.099312 | -0.007783 | 0.038746 | 0.14789 | 0.050715 | 0.044732 | -0.052488 | -0.004252 | -0.015177 | 0.019715 | 0.091234 | 0.053923 | 0.1032 | 0.065892
2073.4688 | 122.2275 | -121.9666 | 0.091553 | 0.14017 | -0.026784 | -0.016578 | 0.007033 | 0.045421 | 0.067269 | -0.044405 | 0.011281 | 0.11585 | 0.014094 | 0.026427 | -0.079953 | -0.036295 | -0.04722 | -0.021484 | 0.17221 | 0.005259 | 0.015465 | 0.039076 | 0.077464 | 0.099312 | -0.012362 | 0.043324 | 0.14789 | 0.046137 | 0.05847 | -0.04791 | -0.004252 | -0.015177 | 0.010559 | 0.091234 | 0.058501 | 0.094047 | 0.061314
2075.2031 | 122.2366 | -121.9711 | 0.091553 | 0.14474 | -0.031363 | -0.012 | -0.002124 | 0.045421 | 0.067269 | -0.039826 | 0.002124 | 0.11585 | 0.02325 | 0.026427 | -0.084531 | -0.022561 | -0.056376 | -0.016906 | 0.17679 | 0.00068 | 0.020043 | 0.029919 | 0.077464 | 0.099312 | -0.007783 | 0.034167 | 0.14789 | 0.055293 | 0.05847 | -0.052488 | 0.009482 | -0.024333 | 0.015137 | 0.086655 | 0.0585 | 0.10778 | 0.079626
2076.9062 | 122.2321 | -121.9666 | 0.082397 | 0.13559 | -0.031363 | -0.007421 | 0.002454 | 0.036265 | 0.081005 | -0.035248 | 0.011281 | 0.11585 | 0.018672 | 0.017268 | -0.084531 | -0.031717 | -0.04722 | -0.012328 | 0.16763 | 0.00068 | 0.024622 | 0.034497 | 0.068308 | 0.11305 | -0.003205 | 0.043324 | 0.14789 | 0.050715 | 0.049311 | -0.052488 | 0.000326 | -0.015177 | 0.019715 | 0.095812 | 0.058501 | 0.1032 | 0.065892
2078.6406 | 122.3007 | -121.962 | 0.07782 | 0.14017 | -0.026784 | -0.007421 | 0.007033 | 0.040843 | 0.067269 | -0.039826 | 0.006703 | 0.11127 | 0.018672 | 0.026427 | -0.08911 | -0.027139 | -0.056376 | -0.016906 | 0.17221 | 0.005259 | 0.024622 | 0.039076 | 0.072886 | 0.099312 | -0.007783 | 0.038746 | 0.14331 | 0.050715 | 0.05847 | -0.057067 | 0.004904 | -0.024333 | 0.015137 | 0.095813 | 0.063079 | 0.10778 | 0.075048
2080.3906 | 122.1954 | -122.0032 | 0.091553 | 0.14474 | -0.026784 | -0.012 | -0.002124 | 0.049999 | 0.067269 | -0.039826 | 0.006703 | 0.11585 | 0.02325 | 0.017268 | -0.084531 | -0.031717 | -0.042641 | -0.016906 | 0.17679 | 0.005259 | 0.020043 | 0.029919 | 0.082042 | 0.099312 | -0.007783 | 0.038746 | 0.14789 | 0.055293 | 0.049311 | -0.052488 | 0.000326 | -0.010598 | 0.015137 | 0.091234 | 0.049344 | 0.10778 | 0.065891
2082.1406 | 122.1451 | -122.0169 | 0.1236 | 0.13559 | -0.026784 | -0.016578 | 0.002454 | 0.036265 | 0.076426 | -0.03067 | 0.006703 | 0.11127 | 0.014094 | 0.026427 | -0.084531 | -0.027139 | -0.04722 | -0.016906 | 0.16763 | 0.005259 | 0.015465 | 0.034497 | 0.068308 | 0.10847 | 0.001373 | 0.038746 | 0.14331 | 0.046137 | 0.05847 | -0.052488 | 0.004904 | -0.015177 | 0.015137 | 0.091234 | 0.053923 | 0.098625 | 0.061314
2083.8906 | 122.2366 | -121.9711 | 0.073242 | 0.14017 | -0.031363 | -0.016578 | 0.007033 | 0.049999 | 0.058113 | -0.03067 | 0.011281 | 0.12043 | 0.014094 | 0.026427 | -0.08911 | -0.031717 | -0.042641 | -0.012328 | 0.17221 | 0.00068 | 0.015465 | 0.039076 | 0.082042 | 0.090156 | 0.001373 | 0.043324 | 0.15247 | 0.046137 | 0.05847 | -0.057067 | 0.000326 | -0.010598 | 0.019715 | 0.10039 | 0.053922 | 0.1032 | 0.056735
2085.5781 | 122.1268 | -122.0078 | 0.10986 | 0.13559 | -0.017627 | -0.007421 | 0.002454 | 0.045421 | 0.071848 | -0.039826 | 0.011281 | 0.11585 | 0.018672 | 0.021847 | -0.079953 | -0.036295 | -0.051798 | -0.012328 | 0.16763 | 0.014416 | 0.024622 | 0.034497 | 0.077464 | 0.10389 | -0.007783 | 0.043324 | 0.14789 | 0.050715 | 0.05389 | -0.04791 | -0.004252 | -0.019755 | 0.019715 | 0.091234 | 0.063079 | 0.098625 | 0.07047
2087.3281 | 122.2092 | -122.0078 | 0.09613 | 0.14474 | -0.031363 | -0.012 | -0.002124 | 0.036265 | 0.076426 | -0.035248 | 0.006703 | 0.12043 | 0.018672 | 0.021847 | -0.079953 | -0.031717 | -0.04722 | -0.026063 | 0.17679 | 0.00068 | 0.020043 | 0.029919 | 0.068308 | 0.10847 | -0.003205 | 0.038746 | 0.15247 | 0.050715 | 0.05389 | -0.04791 | 0.000326 | -0.015177 | 0.00598 | 0.086656 | 0.053923 | 0.098625 | 0.065892
2089.0938 | 122.2137 | -122.0032 | 0.10986 | 0.14017 | -0.026784 | -0.016578 | 0.011611 | 0.045421 | 0.067269 | -0.035248 | 0.006703 | 0.11127 | 0.009515 | 0.026427 | -0.084531 | -0.031717 | -0.056376 | -0.012328 | 0.17221 | 0.005259 | 0.015465 | 0.043654 | 0.077464 | 0.099312 | -0.003205 | 0.038746 | 0.14331 | 0.041558 | 0.05847 | -0.052488 | 0.000326 | -0.024333 | 0.019715 | 0.091234 | 0.063079 | 0.094046 | 0.065891
2090.7812 | 122.1497 | -122.0215 | 0.11902 | 0.14474 | -0.026784 | -0.012 | 0.007033 | 0.045421 | 0.076426 | -0.039826 | 0.002124 | 0.12501 | 0.018672 | 0.021847 | -0.079953 | -0.031717 | -0.051798 | -0.016906 | 0.17679 | 0.005259 | 0.020043 | 0.039076 | 0.077464 | 0.10847 | -0.007783 | 0.034167 | 0.15705 | 0.050715 | 0.05389 | -0.04791 | 0.000326 | -0.019755 | 0.015137 | 0.082077 | 0.053922 | 0.098625 | 0.07047
2092.5312 | 122.1588 | -122.0306 | 0.09613 | 0.14932 | -0.026784 | -0.007421 | 0.007033 | 0.040843 | 0.071848 | -0.039826 | 0.006703 | 0.12043 | 0.014094 | 0.031006 | -0.08911 | -0.031717 | -0.04722 | -0.012328 | 0.18136 | 0.005259 | 0.024622 | 0.039076 | 0.072886 | 0.10389 | -0.007783 | 0.038746 | 0.15247 | 0.046137 | 0.063049 | -0.057067 | 0.000326 | -0.015177 | 0.019715 | 0.095813 | 0.053923 | 0.1032 | 0.061314
2094.2812 | 122.2641 | -121.994 | 0.082397 | 0.13559 | -0.031363 | -0.012 | 0.002454 | 0.045421 | 0.076426 | -0.03067 | 0.01586 | 0.11585 | 0.018672 | 0.021847 | -0.079953 | -0.022561 | -0.04722 | -0.012328 | 0.16763 | 0.00068 | 0.020043 | 0.034497 | 0.077464 | 0.10847 | 0.001373 | 0.047903 | 0.14789 | 0.050715 | 0.05389 | -0.04791 | 0.009482 | -0.015177 | 0.019715 | 0.095813 | 0.06308 | 0.098625 | 0.065892
2096.0469 | 122.1359 | -122.0078 | 0.11902 | 0.14017 | -0.026784 | -0.012 | 0.002454 | 0.031687 | 0.067269 | -0.035248 | 0.01586 | 0.11585 | 0.018672 | 0.021847 | -0.08911 | -0.031717 | -0.04722 | -0.012328 | 0.17221 | 0.005259 | 0.020043 | 0.034497 | 0.06373 | 0.099312 | -0.003205 | 0.047903 | 0.14789 | 0.050715 | 0.05389 | -0.057067 | 0.000326 | -0.015177 | 0.019715 | 0.10497 | 0.06308 | 0.10778 | 0.065892
2097.7969 | 122.1954 | -122.0032 | 0.09613 | 0.14932 | -0.026784 | -0.012 | 0.007033 | 0.040843 | 0.071848 | -0.035248 | 0.011281 | 0.11585 | 0.009515 | 0.017268 | -0.084531 | -0.031717 | -0.051798 | -0.016906 | 0.18136 | 0.005259 | 0.020043 | 0.039076 | 0.072886 | 0.10389 | -0.003205 | 0.043324 | 0.14789 | 0.041558 | 0.049311 | -0.052488 | 0.000326 | -0.019755 | 0.015137 | 0.095812 | 0.063079 | 0.094046 | 0.061313
2099.4844 | 122.2733 | -121.9849 | 0.068665 | 0.14474 | -0.035942 | -0.016578 | -0.002124 | 0.036265 | 0.067269 | -0.039826 | 0.002124 | 0.11585 | 0.014094 | 0.026427 | -0.08911 | -0.036295 | -0.051798 | -0.012328 | 0.17679 | -0.003899 | 0.015465 | 0.029919 | 0.068308 | 0.099312 | -0.007783 | 0.034167 | 0.14789 | 0.046137 | 0.05847 | -0.057067 | -0.004252 | -0.019755 | 0.019715 | 0.091234 | 0.053922 | 0.1032 | 0.065892
2101.2344 | 122.2824 | -121.9894 | 0.07782 | 0.14474 | -0.031363 | -0.007421 | 0.002454 | 0.036265 | 0.071848 | -0.035248 | 0.01586 | 0.11127 | 0.014094 | 0.017268 | -0.08911 | -0.036295 | -0.060955 | -0.016906 | 0.17679 | 0.00068 | 0.024622 | 0.034497 | 0.068308 | 0.10389 | -0.003205 | 0.047903 | 0.14331 | 0.046137 | 0.049311 | -0.057067 | -0.004252 | -0.028912 | 0.015137 | 0.10497 | 0.076815 | 0.1032 | 0.075049
2102.9219 | 122.168 | -122.0306 | 0.10986 | 0.14017 | -0.031363 | -0.012 | 0.007033 | 0.045421 | 0.067269 | -0.039826 | 0.006703 | 0.11585 | 0.014094 | 0.021847 | -0.084531 | -0.027139 | -0.051798 | -0.021484 | 0.17221 | 0.00068 | 0.020043 | 0.039076 | 0.077464 | 0.099312 | -0.007783 | 0.038746 | 0.14789 | 0.046137 | 0.05389 | -0.052488 | 0.004904 | -0.019755 | 0.010559 | 0.091234 | 0.058501 | 0.098625 | 0.065892
2104.6719 | 122.2824 | -121.9803 | 0.09613 | 0.13559 | -0.035942 | -0.012 | 0.007033 | 0.031687 | 0.071848 | -0.039826 | 0.006703 | 0.11127 | 0.018672 | 0.021847 | -0.08911 | -0.036295 | -0.04722 | -0.016906 | 0.16763 | -0.003899 | 0.020043 | 0.039076 | 0.06373 | 0.10389 | -0.007783 | 0.038746 | 0.14331 | 0.050715 | 0.05389 | -0.057067 | -0.004252 | -0.015177 | 0.015137 | 0.095813 | 0.053923 | 0.10778 | 0.065892
2106.4375 | 122.319 | -121.9986 | 0.07782 | 0.13559 | -0.031363 | -0.012 | 0.007033 | 0.045421 | 0.071848 | -0.035248 | 0.006703 | 0.11585 | 0.02325 | 0.021847 | -0.08911 | -0.036295 | -0.051798 | -0.016906 | 0.16763 | 0.00068 | 0.020043 | 0.039076 | 0.077464 | 0.10389 | -0.003205 | 0.038746 | 0.14789 | 0.055293 | 0.05389 | -0.057067 | -0.004252 | -0.019755 | 0.015137 | 0.095813 | 0.058501 | 0.11236 | 0.075048
2108.1406 | 122.2778 | -121.9803 | 0.068665 | 0.14017 | -0.031363 | -0.012 | 0.002454 | 0.045421 | 0.076426 | -0.035248 | 0.011281 | 0.12043 | 0.014094 | 0.026427 | -0.084531 | -0.031717 | -0.04722 | -0.016906 | 0.17221 | 0.00068 | 0.020043 | 0.034497 | 0.077464 | 0.10847 | -0.003205 | 0.043324 | 0.15247 | 0.046137 | 0.05847 | -0.052488 | 0.000326 | -0.015177 | 0.015137 | 0.095812 | 0.058501 | 0.098625 | 0.061314
2109.875 | 122.3053 | -121.9849 | 0.09613 | 0.13559 | -0.026784 | -0.012 | 0.011611 | 0.036265 | 0.071848 | -0.039826 | 0.002124 | 0.11585 | 0.014094 | 0.012689 | -0.084531 | -0.031717 | -0.04722 | -0.021484 | 0.16763 | 0.005259 | 0.020043 | 0.043654 | 0.068308 | 0.10389 | -0.007783 | 0.034167 | 0.14789 | 0.046137 | 0.044732 | -0.052488 | 0.000326 | -0.015177 | 0.010559 | 0.086655 | 0.049344 | 0.098625 | 0.061314
2111.6406 | 122.2458 | -122.0078 | 0.086975 | 0.14017 | -0.026784 | -0.021157 | -0.002124 | 0.045421 | 0.076426 | -0.035248 | 0.011281 | 0.11585 | 0.018672 | 0.012689 | -0.084531 | -0.031717 | -0.051798 | -0.021484 | 0.17221 | 0.005259 | 0.010886 | 0.029919 | 0.077464 | 0.10847 | -0.003205 | 0.043324 | 0.14789 | 0.050715 | 0.044732 | -0.052488 | 0.000326 | -0.019755 | 0.010559 | 0.095812 | 0.063079 | 0.1032 | 0.07047
2113.4062 | 122.2137 | -121.994 | 0.10986 | 0.14017 | -0.031363 | -0.016578 | -0.002124 | 0.045421 | 0.076426 | -0.039826 | 0.01586 | 0.11585 | 0.02325 | 0.021847 | -0.08911 | -0.027139 | -0.060955 | -0.016906 | 0.17221 | 0.00068 | 0.015465 | 0.029919 | 0.077464 | 0.10847 | -0.007783 | 0.047903 | 0.14789 | 0.055293 | 0.05389 | -0.057067 | 0.004904 | -0.028912 | 0.015137 | 0.10497 | 0.076815 | 0.11236 | 0.084205
2115.0938 | 122.1588 | -122.0306 | 0.1236 | 0.14017 | -0.031363 | -0.012 | 0.002454 | 0.040843 | 0.076426 | -0.035248 | 0.011281 | 0.12043 | 0.018672 | 0.021847 | -0.084531 | -0.031717 | -0.042641 | -0.016906 | 0.17221 | 0.00068 | 0.020043 | 0.034497 | 0.072886 | 0.10847 | -0.003205 | 0.043324 | 0.15247 | 0.050715 | 0.05389 | -0.052488 | 0.000326 | -0.010598 | 0.015137 | 0.095812 | 0.053922 | 0.1032 | 0.061313
2116.8438 | 122.2641 | -121.9711 | 0.091553 | 0.13101 | -0.022205 | -0.007421 | 0.007033 | 0.049999 | 0.071848 | -0.039826 | 0.006703 | 0.11585 | 0.014094 | 0.026427 | -0.08911 | -0.031717 | -0.051798 | -0.016906 | 0.16305 | 0.009838 | 0.024622 | 0.039076 | 0.082042 | 0.10389 | -0.007783 | 0.038746 | 0.14789 | 0.046137 | 0.05847 | -0.057067 | 0.000326 | -0.019755 | 0.015137 | 0.095813 | 0.058501 | 0.1032 | 0.065892
2118.5938 | 122.3236 | -122.0078 | 0.068665 | 0.14017 | -0.026784 | -0.007421 | 0.007033 | 0.045421 | 0.071848 | -0.039826 | 0.006703 | 0.12043 | 0.018672 | 0.017268 | -0.08911 | -0.036295 | -0.04722 | -0.012328 | 0.17221 | 0.005259 | 0.024622 | 0.039076 | 0.077464 | 0.10389 | -0.007783 | 0.038746 | 0.15247 | 0.050715 | 0.049311 | -0.057067 | -0.004252 | -0.015177 | 0.019715 | 0.095813 | 0.053923 | 0.10778 | 0.065892
2120.2812 | 122.1817 | -122.0306 | 0.1236 | 0.13559 | -0.022205 | -0.016578 | 0.002454 | 0.045421 | 0.071848 | -0.044405 | 0.01586 | 0.12501 | 0.02325 | 0.026427 | -0.084531 | -0.031717 | -0.04722 | -0.021484 | 0.16763 | 0.009838 | 0.015465 | 0.034497 | 0.077464 | 0.10389 | -0.012362 | 0.047903 | 0.15705 | 0.055293 | 0.05847 | -0.052488 | 0.000326 | -0.015177 | 0.010559 | 0.10039 | 0.06308 | 0.10778 | 0.07047
2122.0469 | 122.2229 | -122.0123 | 0.10071 | 0.14017 | -0.035942 | -0.016578 | 0.007033 | 0.045421 | 0.076426 | -0.03067 | 0.006703 | 0.10669 | 0.018672 | 0.021847 | -0.084531 | -0.031717 | -0.056376 | -0.012328 | 0.17221 | -0.003899 | 0.015465 | 0.039076 | 0.077464 | 0.10847 | 0.001373 | 0.038746 | 0.13873 | 0.050715 | 0.05389 | -0.052488 | 0.000326 | -0.024333 | 0.019715 | 0.091234 | 0.063079 | 0.1032 | 0.075048
2123.7969 | 122.2916 | -121.9849 | 0.07782 | 0.14017 | -0.031363 | -0.007421 | 0.002454 | 0.040843 | 0.076426 | -0.035248 | 0.011281 | 0.11585 | 0.014094 | 0.021847 | -0.08911 | -0.027139 | -0.056376 | -0.016906 | 0.17221 | 0.00068 | 0.024622 | 0.034497 | 0.072886 | 0.10847 | -0.003205 | 0.043324 | 0.14789 | 0.046137 | 0.05389 | -0.057067 | 0.004904 | -0.024333 | 0.015137 | 0.10039 | 0.067657 | 0.1032 | 0.07047
2125.4844 | 122.1817 | -122.0078 | 0.11902 | 0.14017 | -0.026784 | -0.021157 | 0.002454 | 0.045421 | 0.071848 | -0.035248 | 0.011281 | 0.12043 | 0.014094 | 0.017268 | -0.084531 | -0.022561 | -0.056376 | -0.012328 | 0.17221 | 0.005259 | 0.010886 | 0.034497 | 0.077464 | 0.10389 | -0.003205 | 0.043324 | 0.15247 | 0.046137 | 0.049311 | -0.052488 | 0.009482 | -0.024333 | 0.019715 | 0.095812 | 0.067657 | 0.098625 | 0.07047
2127.2344 | 122.287 | -122.0169 | 0.07782 | 0.13559 | -0.022205 | -0.016578 | -0.002124 | 0.036265 | 0.071848 | -0.039826 | 0.011281 | 0.12043 | 0.014094 | 0.017268 | -0.075375 | -0.027139 | -0.051798 | -0.026063 | 0.16763 | 0.009838 | 0.015465 | 0.029919 | 0.068308 | 0.10389 | -0.007783 | 0.043324 | 0.15247 | 0.046137 | 0.049311 | -0.043332 | 0.004904 | -0.019755 | 0.00598 | 0.086656 | 0.063079 | 0.089469 | 0.065892
2129 | 122.1771 | -122.0352 | 0.10071 | 0.13559 | -0.026784 | -0.012 | 0.002454 | 0.040843 | 0.067269 | -0.03067 | 0.020438 | 0.12043 | 0.018672 | 0.021847 | -0.08911 | -0.027139 | -0.04722 | -0.016906 | 0.16763 | 0.005259 | 0.020043 | 0.034497 | 0.072886 | 0.099312 | 0.001373 | 0.052481 | 0.15247 | 0.050715 | 0.05389 | -0.057067 | 0.004904 | -0.015177 | 0.015137 | 0.10955 | 0.067658 | 0.10778 | 0.065892
2130.6875 | 122.1771 | -122.0215 | 0.10529 | 0.14017 | -0.022205 | -0.012 | 0.007033 | 0.040843 | 0.071848 | -0.035248 | 0.011281 | 0.12043 | 0.018672 | 0.017268 | -0.093688 | -0.036295 | -0.042641 | -0.021484 | 0.17221 | 0.009838 | 0.020043 | 0.039076 | 0.072886 | 0.10389 | -0.003205 | 0.043324 | 0.15247 | 0.050715 | 0.049311 | -0.061645 | -0.004252 | -0.010598 | 0.010559 | 0.10497 | 0.053922 | 0.11236 | 0.061313
2132.4531 | 122.287 | -121.9849 | 0.09613 | 0.14017 | -0.026784 | -0.012 | 0.002454 | 0.040843 | 0.067269 | -0.048983 | 0.006703 | 0.11585 | 0.014094 | 0.017268 | -0.084531 | -0.031717 | -0.051798 | -0.016906 | 0.17221 | 0.005259 | 0.020043 | 0.034497 | 0.072886 | 0.099312 | -0.01694 | 0.038746 | 0.14789 | 0.046137 | 0.049311 | -0.052488 | 0.000326 | -0.019755 | 0.015137 | 0.091234 | 0.058501 | 0.098625 | 0.065892
2134.2031 | 122.1725 | -122.0352 | 0.11902 | 0.14017 | -0.031363 | -0.012 | 0.002454 | 0.045421 | 0.067269 | -0.035248 | 0.011281 | 0.12043 | 0.018672 | 0.021847 | -0.084531 | -0.031717 | -0.04722 | -0.012328 | 0.17221 | 0.00068 | 0.020043 | 0.034497 | 0.077464 | 0.099312 | -0.003205 | 0.043324 | 0.15247 | 0.050715 | 0.05389 | -0.052488 | 0.000326 | -0.015177 | 0.019715 | 0.095812 | 0.058501 | 0.1032 | 0.065892
2135.875 | 122.2595 | -122.0078 | 0.086975 | 0.13559 | -0.031363 | -0.016578 | 0.002454 | 0.045421 | 0.071848 | -0.039826 | 0.011281 | 0.11127 | 0.02325 | 0.012689 | -0.08911 | -0.031717 | -0.04722 | -0.012328 | 0.16763 | 0.00068 | 0.015465 | 0.034497 | 0.077464 | 0.10389 | -0.007783 | 0.043324 | 0.14331 | 0.055293 | 0.044732 | -0.057067 | 0.000326 | -0.015177 | 0.019715 | 0.10039 | 0.058501 | 0.11236 | 0.07047
2137.6406 | 122.168 | -122.0581 | 0.1236 | 0.14017 | -0.035942 | -0.012 | 0.002454 | 0.036265 | 0.076426 | -0.03067 | 0.011281 | 0.11585 | 0.018672 | 0.017268 | -0.079953 | -0.022561 | -0.056376 | -0.021484 | 0.17221 | -0.003899 | 0.020043 | 0.034497 | 0.068308 | 0.10847 | 0.001373 | 0.043324 | 0.14789 | 0.050715 | 0.049311 | -0.04791 | 0.009482 | -0.024333 | 0.010559 | 0.091234 | 0.067657 | 0.098625 | 0.075048
2139.3438 | 122.2961 | -121.9803 | 0.064087 | 0.14474 | -0.022205 | -0.012 | 0.007033 | 0.040843 | 0.071848 | -0.044405 | 0.011281 | 0.11585 | 0.004937 | 0.017268 | -0.084531 | -0.027139 | -0.051798 | -0.016906 | 0.17679 | 0.009838 | 0.020043 | 0.039076 | 0.072886 | 0.10389 | -0.012362 | 0.043324 | 0.14789 | 0.03698 | 0.049311 | -0.052488 | 0.004904 | -0.019755 | 0.015137 | 0.095812 | 0.063079 | 0.089468 | 0.056735
2141.0938 | 122.287 | -122.0078 | 0.09613 | 0.14017 | -0.031363 | -0.012 | 0.007033 | 0.045421 | 0.067269 | -0.039826 | 0.006703 | 0.12043 | 0.014094 | 0.026427 | -0.08911 | -0.040873 | -0.04722 | -0.021484 | 0.17221 | 0.00068 | 0.020043 | 0.039076 | 0.077464 | 0.099312 | -0.007783 | 0.038746 | 0.15247 | 0.046137 | 0.05847 | -0.057067 | -0.00883 | -0.015177 | 0.010559 | 0.095813 | 0.053923 | 0.1032 | 0.061314
2142.8594 | 122.2824 | -121.9986 | 0.091553 | 0.14474 | -0.026784 | -0.012 | -0.002124 | 0.036265 | 0.076426 | -0.039826 | 0.006703 | 0.12043 | 0.014094 | 0.021847 | -0.084531 | -0.036295 | -0.04722 | -0.016906 | 0.17679 | 0.005259 | 0.020043 | 0.029919 | 0.068308 | 0.10847 | -0.007783 | 0.038746 | 0.15247 | 0.046137 | 0.05389 | -0.052488 | -0.004252 | -0.015177 | 0.015137 | 0.091234 | 0.053923 | 0.098625 | 0.061314
2144.6094 | 122.2641 | -122.0078 | 0.07782 | 0.14474 | -0.026784 | -0.012 | 0.011611 | 0.045421 | 0.067269 | -0.039826 | 0.011281 | 0.12043 | 0.014094 | 0.012689 | -0.084531 | -0.031717 | -0.051798 | -0.016906 | 0.17679 | 0.005259 | 0.020043 | 0.043654 | 0.077464 | 0.099312 | -0.007783 | 0.043324 | 0.15247 | 0.046137 | 0.044732 | -0.052488 | 0.000326 | -0.019755 | 0.015137 | 0.095812 | 0.063079 | 0.098625 | 0.065892
2146.2969 | 122.1909 | -122.0444 | 0.11444 | 0.14474 | -0.026784 | -0.012 | 0.002454 | 0.031687 | 0.067269 | -0.039826 | 0.011281 | 0.11127 | 0.014094 | 0.026427 | -0.084531 | -0.027139 | -0.056376 | -0.016906 | 0.17679 | 0.005259 | 0.020043 | 0.034497 | 0.06373 | 0.099312 | -0.007783 | 0.043324 | 0.14331 | 0.046137 | 0.05847 | -0.052488 | 0.004904 | -0.024333 | 0.015137 | 0.095812 | 0.067657 | 0.098625 | 0.07047
2148.0625 | 122.2458 | -122.0032 | 0.07782 | 0.14017 | -0.031363 | -0.012 | 0.002454 | 0.040843 | 0.067269 | -0.048983 | 0.006703 | 0.12043 | 0.004937 | 0.021847 | -0.08911 | -0.031717 | -0.04722 | -0.016906 | 0.17221 | 0.00068 | 0.020043 | 0.034497 | 0.072886 | 0.099312 | -0.01694 | 0.038746 | 0.15247 | 0.03698 | 0.05389 | -0.057067 | 0.000326 | -0.015177 | 0.015137 | 0.095813 | 0.053923 | 0.094047 | 0.052157
2149.75 | 122.3099 | -121.9803 | 0.054932 | 0.14474 | -0.026784 | -0.012 | 0.007033 | 0.045421 | 0.062691 | -0.039826 | 0.006703 | 0.11585 | 0.014094 | 0.021847 | -0.08911 | -0.031717 | -0.051798 | -0.012328 | 0.17679 | 0.005259 | 0.020043 | 0.039076 | 0.077464 | 0.094734 | -0.007783 | 0.038746 | 0.14789 | 0.046137 | 0.05389 | -0.057067 | 0.000326 | -0.019755 | 0.019715 | 0.095813 | 0.058501 | 0.1032 | 0.065892
2151.5 | 122.3007 | -122.0078 | 0.082397 | 0.14017 | -0.031363 | -0.016578 | 0.002454 | 0.040843 | 0.071848 | -0.039826 | 0.011281 | 0.11585 | 0.018672 | 0.021847 | -0.093688 | -0.027139 | -0.04722 | -0.026063 | 0.17221 | 0.00068 | 0.015465 | 0.034497 | 0.072886 | 0.10389 | -0.007783 | 0.043324 | 0.14789 | 0.050715 | 0.05389 | -0.061645 | 0.004904 | -0.015177 | 0.00598 | 0.10497 | 0.058501 | 0.11236 | 0.065892
2153.1875 | 122.1863 | -122.049 | 0.11444 | 0.14474 | -0.022205 | -0.012 | 0.002454 | 0.040843 | 0.076426 | -0.039826 | 0.011281 | 0.12501 | 0.014094 | 0.017268 | -0.084531 | -0.031717 | -0.051798 | -0.016906 | 0.17679 | 0.009838 | 0.020043 | 0.034497 | 0.072886 | 0.10847 | -0.007783 | 0.043324 | 0.15705 | 0.046137 | 0.049311 | -0.052488 | 0.000326 | -0.019755 | 0.015137 | 0.095812 | 0.063079 | 0.098625 | 0.065892
2154.9219 | 122.1771 | -122.0261 | 0.11444 | 0.14474 | -0.026784 | -0.012 | 0.011611 | 0.049999 | 0.071848 | -0.039826 | 0.011281 | 0.11585 | 0.018672 | 0.021847 | -0.084531 | -0.031717 | -0.04722 | -0.021484 | 0.17679 | 0.005259 | 0.020043 | 0.043654 | 0.082042 | 0.10389 | -0.007783 | 0.043324 | 0.14789 | 0.050715 | 0.05389 | -0.052488 | 0.000326 | -0.015177 | 0.010559 | 0.095812 | 0.058501 | 0.1032 | 0.065892
2156.6719 | 122.2321 | -121.9849 | 0.13275 | 0.14017 | -0.031363 | -0.012 | 0.002454 | 0.049999 | 0.076426 | -0.035248 | 0.01586 | 0.12043 | 0.027829 | 0.031006 | -0.12116 | -0.063763 | -0.070112 | -0.039797 | 0.17221 | 0.00068 | 0.020043 | 0.034497 | 0.082042 | 0.10847 | -0.003205 | 0.047903 | 0.15247 | 0.059872 | 0.063049 | -0.089114 | -0.03172 | -0.038069 | -0.007754 | 0.13702 | 0.085972 | 0.14899 | 0.097941
2158.4219 | 122.1863 | -121.994 | 0.16022 | 0.14017 | -0.026784 | -0.007421 | 0.011611 | 0.040843 | 0.076426 | -0.035248 | 0.025017 | 0.12501 | 0.05072 | 0.053901 | -0.075375 | -0.031717 | -0.051798 | -0.021484 | 0.17221 | 0.005259 | 0.024622 | 0.043654 | 0.072886 | 0.10847 | -0.003205 | 0.05706 | 0.15705 | 0.082763 | 0.085944 | -0.043332 | 0.000326 | -0.019755 | 0.010559 | 0.10039 | 0.076815 | 0.1261 | 0.10252
2160.1094 | 122.1634 | -121.9803 | 0.14191 | 0.13101 | -0.031363 | -0.007421 | 0.011611 | 0.040843 | 0.081005 | -0.039826 | 0.020438 | 0.13416 | 0.046142 | 0.053901 | -0.08911 | -0.036295 | -0.04722 | -0.021484 | 0.16305 | 0.00068 | 0.024622 | 0.043654 | 0.072886 | 0.11305 | -0.007783 | 0.052481 | 0.16621 | 0.078185 | 0.085944 | -0.057067 | -0.004252 | -0.015177 | 0.010559 | 0.10955 | 0.067658 | 0.13525 | 0.093362
2161.8594 | 122.2641 | -121.962 | 0.1236 | 0.14017 | -0.031363 | -0.012 | -0.002124 | 0.045421 | 0.076426 | -0.03067 | 0.020438 | 0.12958 | 0.05072 | 0.044743 | -0.08911 | -0.027139 | -0.04722 | -0.021484 | 0.17221 | 0.00068 | 0.020043 | 0.029919 | 0.077464 | 0.10847 | 0.001373 | 0.052481 | 0.16163 | 0.082763 | 0.076786 | -0.057067 | 0.004904 | -0.015177 | 0.010559 | 0.10955 | 0.067658 | 0.13983 | 0.09794
2163.5469 | 122.3236 | -121.9666 | 0.10986 | 0.14474 | -0.031363 | -0.007421 | 0.002454 | 0.040843 | 0.076426 | -0.03067 | 0.025017 | 0.12958 | 0.05072 | 0.049322 | -0.08911 | -0.031717 | -0.056376 | -0.021484 | 0.17679 | 0.00068 | 0.024622 | 0.034497 | 0.072886 | 0.10847 | 0.001373 | 0.05706 | 0.16163 | 0.082763 | 0.081365 | -0.057067 | 0.000326 | -0.024333 | 0.010559 | 0.11413 | 0.081393 | 0.13983 | 0.1071
2165.2969 | 122.2137 | -121.9528 | 0.14648 | 0.1539 | -0.026784 | -0.002842 | 0.007033 | 0.049999 | 0.076426 | -0.039826 | 0.020438 | 0.12958 | 0.05072 | 0.053901 | -0.08911 | -0.031717 | -0.04722 | -0.012328 | 0.18594 | 0.005259 | 0.029201 | 0.039076 | 0.082042 | 0.10847 | -0.007783 | 0.052481 | 0.16163 | 0.082763 | 0.085944 | -0.057067 | 0.000326 | -0.015177 | 0.019715 | 0.10955 | 0.067658 | 0.13983 | 0.09794
2167.0469 | 122.2641 | -121.962 | 0.11444 | 0.14474 | -0.031363 | -0.016578 | 0.002454 | 0.040843 | 0.076426 | -0.039826 | 0.025017 | 0.12501 | 0.05072 | 0.044743 | -0.084531 | -0.036295 | -0.051798 | -0.021484 | 0.17679 | 0.00068 | 0.015465 | 0.034497 | 0.072886 | 0.10847 | -0.007783 | 0.05706 | 0.15705 | 0.082763 | 0.076786 | -0.052488 | -0.004252 | -0.019755 | 0.010559 | 0.10955 | 0.076815 | 0.13525 | 0.10252
2168.7344 | 122.2458 | -121.9666 | 0.12817 | 0.14474 | -0.026784 | -0.007421 | 0.007033 | 0.049999 | 0.071848 | -0.039826 | 0.020438 | 0.12043 | 0.05072 | 0.049322 | -0.075375 | -0.031717 | -0.051798 | -0.021484 | 0.17679 | 0.005259 | 0.024622 | 0.039076 | 0.082042 | 0.10389 | -0.007783 | 0.052481 | 0.15247 | 0.082763 | 0.081365 | -0.043332 | 0.000326 | -0.019755 | 0.010559 | 0.095813 | 0.072236 | 0.1261 | 0.10252
2170.4844 | 122.2137 | -121.962 | 0.12817 | 0.14474 | -0.026784 | -0.012 | 0.011611 | 0.045421 | 0.081005 | -0.03067 | 0.025017 | 0.12958 | 0.055298 | 0.049322 | -0.08911 | -0.027139 | -0.051798 | -0.021484 | 0.17679 | 0.005259 | 0.020043 | 0.043654 | 0.077464 | 0.11305 | 0.001373 | 0.05706 | 0.16163 | 0.087341 | 0.081365 | -0.057067 | 0.004904 | -0.019755 | 0.010559 | 0.11413 | 0.076815 | 0.14441 | 0.1071
2172.1875 | 122.1542 | -121.9986 | 0.14191 | 0.14932 | -0.026784 | -0.016578 | 0.007033 | 0.045421 | 0.081005 | -0.039826 | 0.011281 | 0.12958 | 0.041563 | 0.049322 | -0.079953 | -0.027139 | -0.051798 | -0.026063 | 0.18136 | 0.005259 | 0.015465 | 0.039076 | 0.077464 | 0.11305 | -0.007783 | 0.043324 | 0.16163 | 0.073606 | 0.081365 | -0.04791 | 0.004904 | -0.019755 | 0.00598 | 0.091234 | 0.063079 | 0.12152 | 0.093361
2173.9375 | 122.1771 | -121.9986 | 0.16937 | 0.14017 | -0.022205 | -0.007421 | 0.007033 | 0.054577 | 0.076426 | -0.048983 | 0.025017 | 0.12043 | 0.05072 | 0.05848 | -0.084531 | -0.031717 | -0.04722 | -0.016906 | 0.17221 | 0.009838 | 0.024622 | 0.039076 | 0.08662 | 0.10847 | -0.01694 | 0.05706 | 0.15247 | 0.082763 | 0.090523 | -0.052488 | 0.000326 | -0.015177 | 0.015137 | 0.10955 | 0.072237 | 0.13525 | 0.09794
2175.6875 | 122.2275 | -121.9986 | 0.16022 | 0.13559 | -0.017627 | -0.012 | 0.002454 | 0.045421 | 0.071848 | -0.03067 | 0.01586 | 0.12958 | 0.046142 | 0.044743 | -0.08911 | -0.027139 | -0.056376 | -0.021484 | 0.16763 | 0.014416 | 0.020043 | 0.034497 | 0.077464 | 0.10389 | 0.001373 | 0.047903 | 0.16163 | 0.078185 | 0.076786 | -0.057067 | 0.004904 | -0.024333 | 0.010559 | 0.10497 | 0.072236 | 0.13525 | 0.10252
2177.4531 | 122.1771 | -121.9894 | 0.14648 | 0.14474 | -0.026784 | -0.007421 | 0.007033 | 0.045421 | 0.071848 | -0.03067 | 0.020438 | 0.12958 | 0.05072 | 0.049322 | -0.079953 | -0.031717 | -0.04722 | -0.021484 | 0.17679 | 0.005259 | 0.024622 | 0.039076 | 0.077464 | 0.10389 | 0.001373 | 0.052481 | 0.16163 | 0.082763 | 0.081365 | -0.04791 | 0.000326 | -0.015177 | 0.010559 | 0.10039 | 0.067658 | 0.13067 | 0.09794
2179.1875 | 122.2275 | -121.9482 | 0.15564 | 0.14017 | -0.022205 | -0.007421 | 0.007033 | 0.040843 | 0.071848 | -0.035248 | 0.020438 | 0.12501 | 0.05072 | 0.05848 | -0.08911 | -0.036295 | -0.051798 | -0.021484 | 0.17221 | 0.009838 | 0.024622 | 0.039076 | 0.072886 | 0.10389 | -0.003205 | 0.052481 | 0.15705 | 0.082763 | 0.090523 | -0.057067 | -0.004252 | -0.019755 | 0.010559 | 0.10955 | 0.072236 | 0.13983 | 0.10252
2180.875 | 122.1542 | -121.9894 | 0.14191 | 0.14017 | -0.026784 | -0.007421 | 0.002454 | 0.045421 | 0.062691 | -0.039826 | 0.020438 | 0.12958 | 0.055298 | 0.053901 | -0.084531 | -0.027139 | -0.051798 | -0.021484 | 0.17221 | 0.005259 | 0.024622 | 0.034497 | 0.077464 | 0.094734 | -0.007783 | 0.052481 | 0.16163 | 0.087341 | 0.085944 | -0.052488 | 0.004904 | -0.019755 | 0.010559 | 0.10497 | 0.072236 | 0.13983 | 0.1071
2182.6406 | 122.2961 | -121.9299 | 0.12817 | 0.14017 | -0.026784 | -0.012 | 0.007033 | 0.036265 | 0.067269 | -0.039826 | 0.020438 | 0.13416 | 0.046142 | 0.053901 | -0.079953 | -0.027139 | -0.051798 | -0.012328 | 0.17221 | 0.005259 | 0.020043 | 0.039076 | 0.068308 | 0.099312 | -0.007783 | 0.052481 | 0.16621 | 0.078185 | 0.085944 | -0.04791 | 0.004904 | -0.019755 | 0.019715 | 0.10039 | 0.072236 | 0.1261 | 0.09794
2184.3906 | 122.1771 | -122.0078 | 0.15564 | 0.13559 | -0.026784 | -0.012 | 0.007033 | 0.036265 | 0.071848 | -0.035248 | 0.01586 | 0.12958 | 0.059877 | 0.053901 | -0.084531 | -0.036295 | -0.056376 | -0.012328 | 0.16763 | 0.005259 | 0.020043 | 0.039076 | 0.068308 | 0.10389 | -0.003205 | 0.047903 | 0.16163 | 0.09192 | 0.085944 | -0.052488 | -0.004252 | -0.024333 | 0.019715 | 0.10039 | 0.072236 | 0.14441 | 0.11625
2186.1406 | 122.1771 | -121.9849 | 0.16022 | 0.14474 | -0.022205 | -0.002842 | 0.007033 | 0.040843 | 0.071848 | -0.035248 | 0.020438 | 0.12958 | 0.055298 | 0.049322 | -0.08911 | -0.031717 | -0.056376 | -0.016906 | 0.17679 | 0.009838 | 0.029201 | 0.039076 | 0.072886 | 0.10389 | -0.003205 | 0.052481 | 0.16163 | 0.087341 | 0.081365 | -0.057067 | 0.000326 | -0.024333 | 0.015137 | 0.10955 | 0.076814 | 0.14441 | 0.11167
2187.8281 | 122.1588 | -121.9986 | 0.14648 | 0.14474 | -0.031363 | -0.012 | -0.002124 | 0.049999 | 0.071848 | -0.035248 | 0.025017 | 0.13416 | 0.05072 | 0.049322 | -0.08911 | -0.027139 | -0.056376 | -0.030641 | 0.17679 | 0.00068 | 0.020043 | 0.029919 | 0.082042 | 0.10389 | -0.003205 | 0.05706 | 0.16621 | 0.082763 | 0.081365 | -0.057067 | 0.004904 | -0.024333 | 0.001402 | 0.11413 | 0.081393 | 0.13983 | 0.1071
2189.5781 | 122.2504 | -121.962 | 0.12817 | 0.14474 | -0.017627 | -0.012 | 0.007033 | 0.040843 | 0.067269 | -0.035248 | 0.020438 | 0.12958 | 0.059877 | 0.063059 | -0.084531 | -0.031717 | -0.04722 | -0.012328 | 0.17679 | 0.014416 | 0.020043 | 0.039076 | 0.072886 | 0.099312 | -0.003205 | 0.052481 | 0.16163 | 0.09192 | 0.095102 | -0.052488 | 0.000326 | -0.015177 | 0.019715 | 0.10497 | 0.067658 | 0.14441 | 0.1071
2191.3281 | 122.2046 | -121.9711 | 0.17395 | 0.13559 | -0.022205 | -0.012 | 0.002454 | 0.040843 | 0.071848 | -0.039826 | 0.025017 | 0.12501 | 0.046142 | 0.049322 | -0.084531 | -0.022561 | -0.04722 | -0.026063 | 0.16763 | 0.009838 | 0.020043 | 0.034497 | 0.072886 | 0.10389 | -0.007783 | 0.05706 | 0.15705 | 0.078185 | 0.081365 | -0.052488 | 0.009482 | -0.015177 | 0.00598 | 0.10955 | 0.072237 | 0.13067 | 0.093362
2193.0938 | 122.287 | -121.9391 | 0.11902 | 0.13559 | -0.026784 | -0.007421 | -0.002124 | 0.040843 | 0.076426 | -0.044405 | 0.025017 | 0.12043 | 0.055298 | 0.053901 | -0.079953 | -0.031717 | -0.051798 | -0.026063 | 0.16763 | 0.005259 | 0.024622 | 0.029919 | 0.072886 | 0.10847 | -0.012362 | 0.05706 | 0.15247 | 0.087341 | 0.085944 | -0.04791 | 0.000326 | -0.019755 | 0.00598 | 0.10497 | 0.076815 | 0.13525 | 0.1071
2194.7812 | 122.2137 | -121.9666 | 0.14191 | 0.14017 | -0.022205 | -0.012 | -0.002124 | 0.040843 | 0.067269 | -0.039826 | 0.01586 | 0.12501 | 0.059877 | 0.053901 | -0.084531 | -0.027139 | -0.04722 | -0.016906 | 0.17221 | 0.009838 | 0.020043 | 0.029919 | 0.072886 | 0.099312 | -0.007783 | 0.047903 | 0.15705 | 0.09192 | 0.085944 | -0.052488 | 0.004904 | -0.015177 | 0.015137 | 0.10039 | 0.06308 | 0.14441 | 0.1071
2196.5469 | 122.2504 | -121.9711 | 0.12817 | 0.14017 | -0.026784 | -0.012 | 0.007033 | 0.045421 | 0.071848 | -0.039826 | 0.020438 | 0.12958 | 0.055298 | 0.049322 | -0.079953 | -0.031717 | -0.04722 | -0.021484 | 0.17221 | 0.005259 | 0.020043 | 0.039076 | 0.077464 | 0.10389 | -0.007783 | 0.052481 | 0.16163 | 0.087341 | 0.081365 | -0.04791 | 0.000326 | -0.015177 | 0.010559 | 0.10039 | 0.067658 | 0.13525 | 0.10252
2198.2969 | 122.3099 | -121.9482 | 0.12817 | 0.14474 | -0.013048 | -0.007421 | 0.002454 | 0.045421 | 0.071848 | -0.039826 | 0.025017 | 0.12501 | 0.059877 | 0.044743 | -0.079953 | -0.036295 | -0.051798 | -0.021484 | 0.17679 | 0.018995 | 0.024622 | 0.034497 | 0.077464 | 0.10389 | -0.007783 | 0.05706 | 0.15705 | 0.09192 | 0.076786 | -0.04791 | -0.004252 | -0.019755 | 0.010559 | 0.10497 | 0.076815 | 0.13983 | 0.11167
2199.9844 | 122.1634 | -121.9894 | 0.15106 | 0.14017 | -0.031363 | -0.012 | 0.007033 | 0.045421 | 0.071848 | -0.03067 | 0.020438 | 0.12958 | 0.055298 | 0.049322 | -0.084531 | -0.027139 | -0.056376 | -0.021484 | 0.17221 | 0.00068 | 0.020043 | 0.039076 | 0.077464 | 0.10389 | 0.001373 | 0.052481 | 0.16163 | 0.087341 | 0.081365 | -0.052488 | 0.004904 | -0.024333 | 0.010559 | 0.10497 | 0.076814 | 0.13983 | 0.11167
2201.75 | 122.1954 | -121.9528 | 0.13733 | 0.14017 | -0.026784 | -0.016578 | 0.011611 | 0.049999 | 0.081005 | -0.035248 | 0.025017 | 0.12501 | 0.055298 | 0.053901 | -0.084531 | -0.027139 | -0.04722 | -0.012328 | 0.17221 | 0.005259 | 0.015465 | 0.043654 | 0.082042 | 0.11305 | -0.003205 | 0.05706 | 0.15705 | 0.087341 | 0.085944 | -0.052488 | 0.004904 | -0.015177 | 0.019715 | 0.10955 | 0.072237 | 0.13983 | 0.10252
2203.4531 | 122.2549 | -121.9757 | 0.12817 | 0.14017 | -0.022205 | -0.021157 | 0.002454 | 0.040843 | 0.067269 | -0.039826 | 0.020438 | 0.12501 | 0.05072 | 0.053901 | -0.08911 | -0.031717 | -0.04722 | -0.026063 | 0.17221 | 0.009838 | 0.010886 | 0.034497 | 0.072886 | 0.099312 | -0.007783 | 0.052481 | 0.15705 | 0.082763 | 0.085944 | -0.057067 | 0.000326 | -0.015177 | 0.00598 | 0.10955 | 0.067658 | 0.13983 | 0.09794
2205.125 | 122.2275 | -121.9666 | 0.15564 | 0.14932 | -0.026784 | -0.012 | 0.007033 | 0.045421 | 0.081005 | -0.035248 | 0.029595 | 0.12501 | 0.046142 | 0.053901 | -0.079953 | -0.031717 | -0.04722 | -0.021484 | 0.18136 | 0.005259 | 0.020043 | 0.039076 | 0.077464 | 0.11305 | -0.003205 | 0.061638 | 0.15705 | 0.078185 | 0.085944 | -0.04791 | 0.000326 | -0.015177 | 0.010559 | 0.10955 | 0.076815 | 0.1261 | 0.093362
2206.875 | 122.1863 | -122.0169 | 0.13275 | 0.14017 | -0.022205 | -0.012 | 0.002454 | 0.049999 | 0.076426 | -0.039826 | 0.020438 | 0.12958 | 0.05072 | 0.044743 | -0.084531 | -0.027139 | -0.056376 | -0.016906 | 0.17221 | 0.009838 | 0.020043 | 0.034497 | 0.082042 | 0.10847 | -0.007783 | 0.052481 | 0.16163 | 0.082763 | 0.076786 | -0.052488 | 0.004904 | -0.024333 | 0.015137 | 0.10497 | 0.076814 | 0.13525 | 0.1071
2208.625 | 122.3328 | -121.9437 | 0.1236 | 0.14017 | -0.022205 | -0.007421 | -0.002124 | 0.040843 | 0.076426 | -0.039826 | 0.029595 | 0.12501 | 0.05072 | 0.049322 | -0.093688 | -0.031717 | -0.051798 | -0.021484 | 0.17221 | 0.009838 | 0.024622 | 0.029919 | 0.072886 | 0.10847 | -0.007783 | 0.061638 | 0.15705 | 0.082763 | 0.081365 | -0.061645 | 0.000326 | -0.019755 | 0.010559 | 0.12328 | 0.081393 | 0.14441 | 0.10252
2210.3281 | 122.2549 | -121.9803 | 0.13733 | 0.14474 | -0.017627 | -0.012 | 0.002454 | 0.045421 | 0.076426 | -0.035248 | 0.020438 | 0.12501 | 0.05072 | 0.049322 | -0.084531 | -0.027139 | -0.051798 | -0.021484 | 0.17679 | 0.014416 | 0.020043 | 0.034497 | 0.077464 | 0.10847 | -0.003205 | 0.052481 | 0.15705 | 0.082763 | 0.081365 | -0.052488 | 0.004904 | -0.019755 | 0.010559 | 0.10497 | 0.072236 | 0.13525 | 0.10252
2212.0781 | 122.3053 | -121.9391 | 0.12817 | 0.14474 | -0.026784 | -0.012 | 0.002454 | 0.031687 | 0.076426 | -0.039826 | 0.020438 | 0.12958 | 0.05072 | 0.05848 | -0.079953 | -0.027139 | -0.051798 | -0.026063 | 0.17679 | 0.005259 | 0.020043 | 0.034497 | 0.06373 | 0.10847 | -0.007783 | 0.052481 | 0.16163 | 0.082763 | 0.090523 | -0.04791 | 0.004904 | -0.019755 | 0.00598 | 0.10039 | 0.072236 | 0.13067 | 0.10252
2213.8438 | 122.3007 | -121.9666 | 0.11902 | 0.13559 | -0.026784 | -0.012 | 0.011611 | 0.036265 | 0.076426 | -0.035248 | 0.025017 | 0.12958 | 0.05072 | 0.053901 | -0.079953 | -0.031717 | -0.051798 | -0.021484 | 0.16763 | 0.005259 | 0.020043 | 0.043654 | 0.068308 | 0.10847 | -0.003205 | 0.05706 | 0.16163 | 0.082763 | 0.085944 | -0.04791 | 0.000326 | -0.019755 | 0.010559 | 0.10497 | 0.076815 | 0.13067 | 0.10252
2215.5938 | 122.2916 | -121.9528 | 0.1236 | 0.14017 | -0.022205 | -0.016578 | 0.002454 | 0.045421 | 0.076426 | -0.039826 | 0.011281 | 0.12501 | 0.05072 | 0.053901 | -0.084531 | -0.027139 | -0.056376 | -0.016906 | 0.17221 | 0.009838 | 0.015465 | 0.034497 | 0.077464 | 0.10847 | -0.007783 | 0.043324 | 0.15705 | 0.082763 | 0.085944 | -0.052488 | 0.004904 | -0.024333 | 0.015137 | 0.095812 | 0.067657 | 0.13525 | 0.1071
2217.2812 | 122.2824 | -121.9666 | 0.09613 | 0.14474 | -0.031363 | -0.016578 | 0.002454 | 0.045421 | 0.071848 | -0.035248 | 0.020438 | 0.13416 | 0.055298 | 0.053901 | -0.084531 | -0.031717 | -0.051798 | -0.016906 | 0.17679 | 0.00068 | 0.015465 | 0.034497 | 0.077464 | 0.10389 | -0.003205 | 0.052481 | 0.16621 | 0.087341 | 0.085944 | -0.052488 | 0.000326 | -0.019755 | 0.015137 | 0.10497 | 0.072236 | 0.13983 | 0.1071
2219.0312 | 122.2046 | -121.9666 | 0.13733 | 0.14474 | -0.022205 | -0.012 | 0.002454 | 0.049999 | 0.071848 | -0.035248 | 0.01586 | 0.12958 | 0.05072 | 0.049322 | -0.084531 | -0.036295 | -0.056376 | -0.016906 | 0.17679 | 0.009838 | 0.020043 | 0.034497 | 0.082042 | 0.10389 | -0.003205 | 0.047903 | 0.16163 | 0.082763 | 0.081365 | -0.052488 | -0.004252 | -0.024333 | 0.015137 | 0.10039 | 0.072236 | 0.13525 | 0.1071
2220.7969 | 122.3053 | -121.9482 | 0.10529 | 0.14474 | -0.022205 | -0.012 | 0.002454 | 0.045421 | 0.076426 | -0.039826 | 0.01586 | 0.12958 | 0.05072 | 0.05848 | -0.08911 | -0.027139 | -0.051798 | -0.026063 | 0.17679 | 0.009838 | 0.020043 | 0.034497 | 0.077464 | 0.10847 | -0.007783 | 0.047903 | 0.16163 | 0.082763 | 0.090523 | -0.057067 | 0.004904 | -0.019755 | 0.00598 | 0.10497 | 0.067658 | 0.13983 | 0.10252
2222.5 | 122.1909 | -122.0535 | 0.14648 | 0.14474 | -0.031363 | -0.016578 | 0.007033 | 0.040843 | 0.076426 | -0.039826 | 0.025017 | 0.12501 | 0.055298 | 0.053901 | -0.084531 | -0.031717 | -0.056376 | -0.026063 | 0.17679 | 0.00068 | 0.015465 | 0.039076 | 0.072886 | 0.10847 | -0.007783 | 0.05706 | 0.15705 | 0.087341 | 0.085944 | -0.052488 | 0.000326 | -0.024333 | 0.00598 | 0.10955 | 0.081393 | 0.13983 | 0.11167
2224.25 | 122.2961 | -121.9574 | 0.11444 | 0.14932 | -0.017627 | -0.016578 | 0.002454 | 0.045421 | 0.071848 | -0.039826 | 0.025017 | 0.11585 | 0.046142 | 0.053901 | -0.084531 | -0.031717 | -0.056376 | -0.021484 | 0.18136 | 0.014416 | 0.015465 | 0.034497 | 0.077464 | 0.10389 | -0.007783 | 0.05706 | 0.14789 | 0.078185 | 0.085944 | -0.052488 | 0.000326 | -0.024333 | 0.010559 | 0.10955 | 0.081393 | 0.13067 | 0.10252
2226 | 122.2046 | -121.9849 | 0.14648 | 0.14474 | -0.031363 | -0.007421 | 0.002454 | 0.049999 | 0.076426 | -0.039826 | 0.020438 | 0.13416 | 0.05072 | 0.05848 | -0.084531 | -0.031717 | -0.04722 | -0.016906 | 0.17679 | 0.00068 | 0.024622 | 0.034497 | 0.082042 | 0.10847 | -0.007783 | 0.052481 | 0.16621 | 0.082763 | 0.090523 | -0.052488 | 0.000326 | -0.015177 | 0.015137 | 0.10497 | 0.067658 | 0.13525 | 0.09794
2227.6875 | 122.2 | -121.9986 | 0.14648 | 0.13559 | -0.026784 | -0.012 | 0.007033 | 0.040843 | 0.071848 | -0.03067 | 0.01586 | 0.12043 | 0.055298 | 0.049322 | -0.084531 | -0.031717 | -0.042641 | -0.016906 | 0.16763 | 0.005259 | 0.020043 | 0.039076 | 0.072886 | 0.10389 | 0.001373 | 0.047903 | 0.15247 | 0.087341 | 0.081365 | -0.052488 | 0.000326 | -0.010598 | 0.015137 | 0.10039 | 0.058501 | 0.13983 | 0.097939
2229.4688 | 122.2687 | -121.9711 | 0.12817 | 0.14017 | -0.026784 | -0.016578 | 0.002454 | 0.036265 | 0.081005 | -0.035248 | 0.020438 | 0.12958 | 0.046142 | 0.053901 | -0.08911 | -0.022561 | -0.051798 | -0.026063 | 0.17221 | 0.005259 | 0.015465 | 0.034497 | 0.068308 | 0.11305 | -0.003205 | 0.052481 | 0.16163 | 0.078185 | 0.085944 | -0.057067 | 0.009482 | -0.019755 | 0.00598 | 0.10955 | 0.072236 | 0.13525 | 0.09794
2231.2188 | 122.2 | -121.994 | 0.18768 | 0.14017 | -0.026784 | -0.012 | 0.011611 | 0.054577 | 0.085583 | -0.035248 | 0.020438 | 0.12958 | 0.059877 | 0.063059 | -0.084531 | -0.031717 | -0.056376 | -0.016906 | 0.17221 | 0.005259 | 0.020043 | 0.043654 | 0.08662 | 0.11763 | -0.003205 | 0.052481 | 0.16163 | 0.09192 | 0.095102 | -0.052488 | 0.000326 | -0.024333 | 0.015137 | 0.10497 | 0.076814 | 0.14441 | 0.11625
2232.9062 | 122.2183 | -121.4584 | 0.55389 | 0.14932 | -0.022205 | 0.010893 | 0.020768 | 0.054577 | 0.090161 | -0.021514 | 0.12574 | 0.23032 | 0.38494 | 0.41107 | -0.08911 | -0.036295 | -0.070112 | -0.039797 | 0.18136 | 0.009838 | 0.042936 | 0.052811 | 0.08662 | 0.1222 | 0.010529 | 0.15779 | 0.26236 | 0.41698 | 0.44311 | -0.057067 | -0.004252 | -0.038069 | -0.007754 | 0.21485 | 0.19586 | 0.47405 | 0.45505
2234.6562 | 122.2321 | -121.4127 | 0.53558 | 0.1539 | -0.013048 | 0.001736 | 0.020768 | 0.063733 | 0.090161 | -0.03067 | 0.11659 | 0.23032 | 0.38036 | 0.40649 | -0.08911 | -0.031717 | -0.060955 | -0.035219 | 0.18594 | 0.018995 | 0.033779 | 0.052811 | 0.095776 | 0.1222 | 0.001373 | 0.14863 | 0.26236 | 0.4124 | 0.43853 | -0.057067 | 0.000326 | -0.028912 | -0.003176 | 0.2057 | 0.17754 | 0.46947 | 0.44131
2236.4062 | 122.081 | -121.4584 | 0.55847 | 0.15848 | -0.017627 | 0.006315 | 0.020768 | 0.059155 | 0.090161 | -0.026092 | 0.13032 | 0.23032 | 0.38036 | 0.40191 | -0.08911 | -0.031717 | -0.060955 | -0.044375 | 0.19052 | 0.014416 | 0.038358 | 0.052811 | 0.091198 | 0.1222 | 0.005951 | 0.16236 | 0.26236 | 0.4124 | 0.43395 | -0.057067 | 0.000326 | -0.028912 | -0.012332 | 0.21943 | 0.19128 | 0.46947 | 0.44131
2238.1719 | 122.0856 | -121.4676 | 0.5722 | 0.1539 | -0.017627 | 0.001736 | 0.01619 | 0.06831 | 0.099318 | -0.021514 | 0.10743 | 0.22116 | 0.38036 | 0.39733 | -0.08911 | -0.040873 | -0.065533 | -0.035219 | 0.18594 | 0.014416 | 0.033779 | 0.048233 | 0.10035 | 0.13136 | 0.010529 | 0.13947 | 0.2532 | 0.4124 | 0.42937 | -0.057067 | -0.00883 | -0.03349 | -0.003176 | 0.19654 | 0.17296 | 0.46947 | 0.44589
2239.8594 | 122.1817 | -121.4401 | 0.5127 | 0.15848 | -0.013048 | -0.002842 | 0.020768 | 0.054577 | 0.085583 | -0.026092 | 0.12116 | 0.23032 | 0.36662 | 0.39733 | -0.08911 | -0.022561 | -0.070112 | -0.035219 | 0.19052 | 0.018995 | 0.029201 | 0.052811 | 0.08662 | 0.11763 | 0.005951 | 0.15321 | 0.26236 | 0.39866 | 0.42937 | -0.057067 | 0.009482 | -0.038069 | -0.003176 | 0.21027 | 0.19128 | 0.45573 | 0.43673
2241.6094 | 122.0718 | -121.4676 | 0.56305 | 0.1539 | -0.013048 | 0.001736 | 0.025347 | 0.063733 | 0.09474 | -0.021514 | 0.11659 | 0.22116 | 0.37578 | 0.39733 | -0.093688 | -0.040873 | -0.060955 | -0.039797 | 0.18594 | 0.018995 | 0.033779 | 0.05739 | 0.095776 | 0.12678 | 0.010529 | 0.14863 | 0.2532 | 0.40782 | 0.42937 | -0.061645 | -0.00883 | -0.028912 | -0.007754 | 0.21027 | 0.17754 | 0.46947 | 0.43673
2243.3594 | 122.0901 | -121.1105 | 0.54474 | 0.1539 | -0.017627 | 0.010893 | 0.01619 | 0.059155 | 0.09474 | -0.026092 | 0.11201 | 0.212 | 0.36662 | 0.38359 | -0.10284 | -0.036295 | -0.060955 | -0.044375 | 0.18594 | 0.014416 | 0.042936 | 0.048233 | 0.091198 | 0.12678 | 0.005951 | 0.14405 | 0.24405 | 0.39866 | 0.41563 | -0.070801 | -0.004252 | -0.028912 | -0.012332 | 0.21485 | 0.17296 | 0.46946 | 0.42758
2245.1094 | 122.1863 | -121.4172 | 0.50354 | 0.14932 | -0.017627 | 0.006315 | 0.025347 | 0.054577 | 0.090161 | -0.016936 | 0.12116 | 0.22116 | 0.35746 | 0.38359 | -0.08911 | -0.036295 | -0.070112 | -0.035219 | 0.18136 | 0.014416 | 0.038358 | 0.05739 | 0.08662 | 0.1222 | 0.015107 | 0.15321 | 0.2532 | 0.38951 | 0.41563 | -0.057067 | -0.004252 | -0.038069 | -0.003176 | 0.21027 | 0.19128 | 0.44657 | 0.42758
2246.7969 | 121.8475 | -121.1563 | 0.54474 | 0.15848 | -0.017627 | 0.001736 | 0.025347 | 0.063733 | 0.090161 | -0.03067 | 0.10743 | 0.21658 | 0.36204 | 0.39275 | -0.093688 | -0.031717 | -0.065533 | -0.035219 | 0.19052 | 0.014416 | 0.033779 | 0.05739 | 0.095776 | 0.1222 | 0.001373 | 0.13947 | 0.24862 | 0.39409 | 0.42479 | -0.061645 | 0.000326 | -0.03349 | -0.003176 | 0.20112 | 0.17296 | 0.45573 | 0.42758
2248.5469 | 121.4447 | -120.8267 | 0.54932 | 0.1539 | -0.017627 | 0.001736 | 0.025347 | 0.059155 | 0.090161 | -0.026092 | 0.10743 | 0.212 | 0.35289 | 0.38359 | -0.08911 | -0.031717 | -0.060955 | -0.035219 | 0.18594 | 0.014416 | 0.033779 | 0.05739 | 0.091198 | 0.1222 | 0.005951 | 0.13947 | 0.24405 | 0.38493 | 0.41563 | -0.057067 | 0.000326 | -0.028912 | -0.003176 | 0.19654 | 0.16839 | 0.442 | 0.41384
2250.2344 | 121.8292 | -121.2616 | 0.52643 | 0.15848 | -0.017627 | 0.001736 | 0.020768 | 0.049999 | 0.090161 | -0.035248 | 0.11201 | 0.22116 | 0.35746 | 0.37443 | -0.084531 | -0.031717 | -0.056376 | -0.044375 | 0.19052 | 0.014416 | 0.033779 | 0.052811 | 0.082042 | 0.1222 | -0.003205 | 0.14405 | 0.2532 | 0.38951 | 0.40648 | -0.052488 | 0.000326 | -0.024333 | -0.012332 | 0.19654 | 0.16838 | 0.442 | 0.41384
2252 | 122.168 | -121.4264 | 0.49439 | 0.15848 | -0.026784 | -0.002842 | 0.01619 | 0.059155 | 0.085583 | -0.021514 | 0.11201 | 0.21658 | 0.35289 | 0.37901 | -0.084531 | -0.036295 | -0.060955 | -0.035219 | 0.19052 | 0.005259 | 0.029201 | 0.048233 | 0.091198 | 0.11763 | 0.010529 | 0.14405 | 0.24862 | 0.38493 | 0.41106 | -0.052488 | -0.004252 | -0.028912 | -0.003176 | 0.19654 | 0.17296 | 0.43742 | 0.41384
2253.7031 | 122.1268 | -121.4493 | 0.52643 | 0.14932 | -0.013048 | 0.006315 | 0.025347 | 0.054577 | 0.090161 | -0.03067 | 0.10285 | 0.212 | 0.34831 | 0.37443 | -0.093688 | -0.031717 | -0.065533 | -0.039797 | 0.18136 | 0.018995 | 0.038358 | 0.05739 | 0.08662 | 0.1222 | 0.001373 | 0.13489 | 0.24405 | 0.38035 | 0.40648 | -0.061645 | 0.000326 | -0.03349 | -0.007754 | 0.19654 | 0.16838 | 0.442 | 0.41384
2255.4688 | 122.168 | -121.431 | 0.46692 | 0.14932 | -0.017627 | 0.001736 | 0.020768 | 0.054577 | 0.085583 | -0.026092 | 0.10743 | 0.20742 | 0.32999 | 0.35154 | -0.08911 | -0.027139 | -0.056376 | -0.044375 | 0.18136 | 0.014416 | 0.033779 | 0.052811 | 0.08662 | 0.11763 | 0.005951 | 0.13947 | 0.23947 | 0.36204 | 0.38358 | -0.057067 | 0.004904 | -0.024333 | -0.012332 | 0.19654 | 0.16381 | 0.4191 | 0.38637
2257.2188 | 122.1039 | -121.4401 | 0.50812 | 0.15848 | -0.022205 | 0.001736 | 0.020768 | 0.059155 | 0.090161 | -0.021514 | 0.098273 | 0.20742 | 0.34831 | 0.36985 | -0.084531 | -0.036295 | -0.065533 | -0.039797 | 0.19052 | 0.009838 | 0.033779 | 0.052811 | 0.091198 | 0.1222 | 0.010529 | 0.13032 | 0.23947 | 0.38035 | 0.4019 | -0.052488 | -0.004252 | -0.03349 | -0.007754 | 0.1828 | 0.16381 | 0.43284 | 0.41384
2258.9844 | 122.113 | -121.4172 | 0.50354 | 0.15848 | -0.013048 | 0.001736 | 0.01619 | 0.054577 | 0.085583 | -0.03067 | 0.10285 | 0.20742 | 0.34831 | 0.37443 | -0.08911 | -0.031717 | -0.060955 | -0.035219 | 0.19052 | 0.018995 | 0.033779 | 0.048233 | 0.08662 | 0.11763 | 0.001373 | 0.13489 | 0.23947 | 0.38035 | 0.40648 | -0.057067 | 0.000326 | -0.028912 | -0.003176 | 0.19196 | 0.16381 | 0.43742 | 0.40926
2260.6719 | 122.0993 | -121.3852 | 0.49439 | 0.15848 | -0.017627 | -0.002842 | 0.025347 | 0.054577 | 0.081005 | -0.03067 | 0.098273 | 0.20742 | 0.33915 | 0.36985 | -0.079953 | -0.031717 | -0.060955 | -0.030641 | 0.19052 | 0.014416 | 0.029201 | 0.05739 | 0.08662 | 0.11305 | 0.001373 | 0.13032 | 0.23947 | 0.37119 | 0.4019 | -0.04791 | 0.000326 | -0.028912 | 0.001402 | 0.17823 | 0.15923 | 0.41911 | 0.40011
2262.3594 | 122.1542 | -121.4172 | 0.49896 | 0.14932 | -0.022205 | 0.001736 | 0.01619 | 0.054577 | 0.090161 | -0.021514 | 0.098273 | 0.20742 | 0.33915 | 0.36528 | -0.079953 | -0.031717 | -0.070112 | -0.035219 | 0.18136 | 0.009838 | 0.033779 | 0.048233 | 0.08662 | 0.1222 | 0.010529 | 0.13032 | 0.23947 | 0.37119 | 0.39732 | -0.04791 | 0.000326 | -0.038069 | -0.003176 | 0.17823 | 0.16839 | 0.41911 | 0.40926
2264.1094 | 122.113 | -121.3943 | 0.5127 | 0.14932 | -0.017627 | 0.001736 | 0.025347 | 0.049999 | 0.081005 | -0.026092 | 0.11201 | 0.20284 | 0.34373 | 0.36528 | -0.098266 | -0.031717 | -0.060955 | -0.026063 | 0.18136 | 0.014416 | 0.033779 | 0.05739 | 0.082042 | 0.11305 | 0.005951 | 0.14405 | 0.23489 | 0.37577 | 0.39732 | -0.066223 | 0.000326 | -0.028912 | 0.00598 | 0.21027 | 0.17296 | 0.442 | 0.40468
2265.7969 | 121.8887 | -121.4035 | 0.52185 | 0.15848 | -0.022205 | 0.010893 | 0.020768 | 0.059155 | 0.09474 | -0.021514 | 0.093694 | 0.20284 | 0.33915 | 0.36985 | -0.08911 | -0.036295 | -0.060955 | -0.039797 | 0.19052 | 0.009838 | 0.042936 | 0.052811 | 0.091198 | 0.12678 | 0.010529 | 0.12574 | 0.23489 | 0.37119 | 0.4019 | -0.057067 | -0.004252 | -0.028912 | -0.007754 | 0.1828 | 0.15465 | 0.42826 | 0.40011
2267.5469 | 122.1313 | -121.3898 | 0.48065 | 0.14932 | -0.013048 | 0.006315 | 0.01619 | 0.054577 | 0.085583 | -0.03067 | 0.10743 | 0.212 | 0.33915 | 0.3607 | -0.098266 | -0.031717 | -0.060955 | -0.035219 | 0.18136 | 0.018995 | 0.038358 | 0.048233 | 0.08662 | 0.11763 | 0.001373 | 0.13947 | 0.24405 | 0.37119 | 0.39274 | -0.066223 | 0.000326 | -0.028912 | -0.003176 | 0.2057 | 0.16839 | 0.43742 | 0.40011
2269.2969 | 122.1085 | -121.4127 | 0.48065 | 0.1539 | -0.017627 | 0.001736 | 0.034504 | 0.059155 | 0.081005 | -0.016936 | 0.098273 | 0.20742 | 0.33457 | 0.36528 | -0.08911 | -0.036295 | -0.060955 | -0.035219 | 0.18594 | 0.014416 | 0.033779 | 0.066547 | 0.091198 | 0.11305 | 0.015107 | 0.13032 | 0.23947 | 0.36662 | 0.39732 | -0.057067 | -0.004252 | -0.028912 | -0.003176 | 0.18738 | 0.15923 | 0.42368 | 0.39553
2270.9688 | 121.701 | -121.0007 | 0.52643 | 0.15848 | -0.017627 | 0.010893 | 0.025347 | 0.059155 | 0.090161 | -0.035248 | 0.093694 | 0.20284 | 0.33457 | 0.35612 | -0.084531 | -0.031717 | -0.056376 | -0.030641 | 0.19052 | 0.014416 | 0.042936 | 0.05739 | 0.091198 | 0.1222 | -0.003205 | 0.12574 | 0.23489 | 0.36662 | 0.38816 | -0.052488 | 0.000326 | -0.024333 | 0.001402 | 0.17822 | 0.15007 | 0.4191 | 0.39095
2272.7188 | 122.0673 | -121.1975 | 0.50812 | 0.1539 | -0.008469 | 0.010893 | 0.020768 | 0.049999 | 0.09474 | -0.026092 | 0.098273 | 0.20284 | 0.32999 | 0.34696 | -0.098266 | -0.036295 | -0.065533 | -0.039797 | 0.18594 | 0.023574 | 0.042936 | 0.052811 | 0.082042 | 0.12678 | 0.005951 | 0.13032 | 0.23489 | 0.36204 | 0.379 | -0.066223 | -0.004252 | -0.03349 | -0.007754 | 0.19654 | 0.16381 | 0.42826 | 0.39553
2274.4688 | 121.9894 | -121.4081 | 0.50812 | 0.14932 | -0.013048 | 0.006315 | 0.01619 | 0.054577 | 0.085583 | -0.021514 | 0.098273 | 0.20742 | 0.32084 | 0.35154 | -0.08911 | -0.031717 | -0.070112 | -0.035219 | 0.18136 | 0.018995 | 0.038358 | 0.048233 | 0.08662 | 0.11763 | 0.010529 | 0.13032 | 0.23947 | 0.35288 | 0.38358 | -0.057067 | 0.000326 | -0.038069 | -0.003176 | 0.18738 | 0.16839 | 0.40995 | 0.39095
2276.1562 | 122.1176 | -121.4676 | 0.38452 | 0.1539 | -0.017627 | 0.001736 | 0.01619 | 0.049999 | 0.085583 | -0.035248 | 0.093694 | 0.19827 | 0.3071 | 0.32406 | -0.08911 | -0.036295 | -0.051798 | -0.035219 | 0.18594 | 0.014416 | 0.033779 | 0.048233 | 0.082042 | 0.11763 | -0.003205 | 0.12574 | 0.23031 | 0.33915 | 0.35611 | -0.057067 | -0.004252 | -0.019755 | -0.003176 | 0.1828 | 0.14549 | 0.39621 | 0.3589
2277.9062 | 122.0352 | -121.5591 | 0.39368 | 0.14932 | -0.022205 | 0.001736 | 0.01619 | 0.054577 | 0.081005 | -0.03067 | 0.057066 | 0.17079 | 0.22927 | 0.24164 | -0.10742 | -0.050029 | -0.065533 | -0.035219 | 0.18136 | 0.009838 | 0.033779 | 0.048233 | 0.08662 | 0.11305 | 0.001373 | 0.089109 | 0.20284 | 0.26132 | 0.27368 | -0.075379 | -0.017986 | -0.03349 | -0.003176 | 0.16449 | 0.1226 | 0.3367 | 0.29481
2279.6562 | 121.994 | -121.4493 | 0.49896 | 0.14932 | -0.017627 | 0.010893 | 0.020768 | 0.059155 | 0.09474 | -0.026092 | 0.093694 | 0.20742 | 0.31626 | 0.3378 | -0.084531 | -0.027139 | -0.060955 | -0.039797 | 0.18136 | 0.014416 | 0.042936 | 0.052811 | 0.091198 | 0.12678 | 0.005951 | 0.12574 | 0.23947 | 0.3483 | 0.36984 | -0.052488 | 0.004904 | -0.028912 | -0.007754 | 0.17822 | 0.15465 | 0.40079 | 0.37721
2281.3438 | 121.9894 | -121.4676 | 0.48523 | 0.1539 | -0.022205 | -0.002842 | 0.01619 | 0.059155 | 0.09474 | -0.021514 | 0.098273 | 0.19369 | 0.32084 | 0.3378 | -0.08911 | -0.036295 | -0.060955 | -0.030641 | 0.18594 | 0.009838 | 0.029201 | 0.048233 | 0.091198 | 0.12678 | 0.010529 | 0.13032 | 0.22573 | 0.35288 | 0.36984 | -0.057067 | -0.004252 | -0.028912 | 0.001402 | 0.18738 | 0.15923 | 0.40995 | 0.38179
2283.0938 | 122.0444 | -121.4493 | 0.48981 | 0.1539 | -0.013048 | 0.001736 | 0.01619 | 0.063733 | 0.09474 | -0.026092 | 0.093694 | 0.19827 | 0.3071 | 0.3378 | -0.084531 | -0.031717 | -0.060955 | -0.035219 | 0.18594 | 0.018995 | 0.033779 | 0.048233 | 0.095776 | 0.12678 | 0.005951 | 0.12574 | 0.23031 | 0.33915 | 0.36984 | -0.052488 | 0.000326 | -0.028912 | -0.003176 | 0.17822 | 0.15465 | 0.39163 | 0.36806
2284.8594 | 121.9986 | -121.7377 | 0.25177 | 0.13559 | -0.035942 | -0.002842 | 0.01619 | 0.049999 | 0.076426 | -0.035248 | 0.038752 | 0.14332 | 0.11939 | 0.12259 | -0.084531 | -0.027139 | -0.051798 | -0.016906 | 0.16763 | -0.003899 | 0.029201 | 0.048233 | 0.082042 | 0.10847 | -0.003205 | 0.070795 | 0.17536 | 0.15144 | 0.15463 | -0.052488 | 0.004904 | -0.019755 | 0.015137 | 0.12328 | 0.09055 | 0.20392 | 0.17119
2286.625 | 122.0627 | -121.7743 | 0.10986 | 0.14017 | -0.026784 | -0.012 | 0.002454 | 0.040843 | 0.076426 | -0.039826 | 0.025017 | 0.13416 | 0.055298 | 0.05848 | -0.084531 | -0.027139 | -0.051798 | -0.012328 | 0.17221 | 0.005259 | 0.020043 | 0.034497 | 0.072886 | 0.10847 | -0.007783 | 0.05706 | 0.16621 | 0.087341 | 0.090523 | -0.052488 | 0.004904 | -0.019755 | 0.019715 | 0.10955 | 0.076815 | 0.13983 | 0.1071
2288.375 | 121.9757 | -121.7651 | 0.15106 | 0.13559 | -0.026784 | -0.012 | 0.007033 | 0.049999 | 0.071848 | -0.035248 | 0.020438 | 0.12501 | 0.05072 | 0.049322 | -0.084531 | -0.031717 | -0.04722 | -0.012328 | 0.16763 | 0.005259 | 0.020043 | 0.039076 | 0.082042 | 0.10389 | -0.003205 | 0.052481 | 0.15705 | 0.082763 | 0.081365 | -0.052488 | 0.000326 | -0.015177 | 0.019715 | 0.10497 | 0.067658 | 0.13525 | 0.09794
2290.0625 | 122.0444 | -121.7606 | 0.10986 | 0.14017 | -0.026784 | -0.012 | 0.002454 | 0.045421 | 0.076426 | -0.044405 | 0.01586 | 0.12958 | 0.041563 | 0.044743 | -0.075375 | -0.027139 | -0.04722 | -0.012328 | 0.17221 | 0.005259 | 0.020043 | 0.034497 | 0.077464 | 0.10847 | -0.012362 | 0.047903 | 0.16163 | 0.073606 | 0.076786 | -0.043332 | 0.004904 | -0.015177 | 0.019715 | 0.091235 | 0.06308 | 0.11694 | 0.088783
2291.8125 | 122.0673 | -121.7285 | 0.10071 | 0.14017 | -0.026784 | -0.007421 | 0.002454 | 0.045421 | 0.071848 | -0.039826 | 0.020438 | 0.12501 | 0.041563 | 0.035585 | -0.079953 | -0.027139 | -0.051798 | -0.003172 | 0.17221 | 0.005259 | 0.024622 | 0.034497 | 0.077464 | 0.10389 | -0.007783 | 0.052481 | 0.15705 | 0.073606 | 0.067628 | -0.04791 | 0.004904 | -0.019755 | 0.028871 | 0.10039 | 0.072236 | 0.12152 | 0.093361
2293.5625 | 122.0673 | -121.7422 | 0.10986 | 0.13559 | -0.022205 | -0.007421 | -0.002124 | 0.049999 | 0.071848 | -0.035248 | 0.025017 | 0.12958 | 0.046142 | 0.044743 | -0.079953 | -0.022561 | -0.04722 | -0.012328 | 0.16763 | 0.009838 | 0.024622 | 0.029919 | 0.082042 | 0.10389 | -0.003205 | 0.05706 | 0.16163 | 0.078185 | 0.076786 | -0.04791 | 0.009482 | -0.015177 | 0.019715 | 0.10497 | 0.072237 | 0.1261 | 0.093362
2295.2656 | 121.994 | -121.7789 | 0.14648 | 0.13559 | -0.026784 | -0.012 | 0.002454 | 0.040843 | 0.071848 | -0.039826 | 0.01586 | 0.12958 | 0.041563 | 0.040164 | -0.084531 | -0.027139 | -0.056376 | -0.00775 | 0.16763 | 0.005259 | 0.020043 | 0.034497 | 0.072886 | 0.10389 | -0.007783 | 0.047903 | 0.16163 | 0.073606 | 0.072207 | -0.052488 | 0.004904 | -0.024333 | 0.024293 | 0.10039 | 0.072236 | 0.12609 | 0.097939
2297.0156 | 121.9299 | -121.7651 | 0.15106 | 0.14474 | -0.031363 | -0.007421 | -0.002124 | 0.040843 | 0.071848 | -0.039826 | 0.025017 | 0.12501 | 0.046142 | 0.049322 | -0.08911 | -0.022561 | -0.04722 | -0.021484 | 0.17679 | 0.00068 | 0.024622 | 0.029919 | 0.072886 | 0.10389 | -0.007783 | 0.05706 | 0.15705 | 0.078185 | 0.081365 | -0.057067 | 0.009482 | -0.015177 | 0.010559 | 0.11413 | 0.072237 | 0.13525 | 0.093362
2298.7812 | 122.0123 | -121.7285 | 0.1236 | 0.14017 | -0.017627 | -0.007421 | 0.007033 | 0.045421 | 0.071848 | -0.039826 | 0.01586 | 0.12501 | 0.046142 | 0.044743 | -0.084531 | -0.027139 | -0.04722 | -0.012328 | 0.17221 | 0.014416 | 0.024622 | 0.039076 | 0.077464 | 0.10389 | -0.007783 | 0.047903 | 0.15705 | 0.078185 | 0.076786 | -0.052488 | 0.004904 | -0.015177 | 0.019715 | 0.10039 | 0.06308 | 0.13067 | 0.093362
2300.5469 | 122.0215 | -121.7697 | 0.10529 | 0.14017 | -0.031363 | -0.012 | 0.002454 | 0.040843 | 0.071848 | -0.035248 | 0.01586 | 0.12501 | 0.041563 | 0.035585 | -0.084531 | -0.027139 | -0.051798 | -0.003172 | 0.17221 | 0.00068 | 0.020043 | 0.034497 | 0.072886 | 0.10389 | -0.003205 | 0.047903 | 0.15705 | 0.073606 | 0.067628 | -0.052488 | 0.004904 | -0.019755 | 0.028871 | 0.10039 | 0.067658 | 0.12609 | 0.093361
2302.2344 | 122.0718 | -121.7468 | 0.1236 | 0.14017 | -0.022205 | -0.016578 | -0.002124 | 0.045421 | 0.076426 | -0.039826 | 0.025017 | 0.12501 | 0.027829 | 0.040164 | -0.079953 | -0.027139 | -0.056376 | -0.012328 | 0.17221 | 0.009838 | 0.015465 | 0.029919 | 0.077464 | 0.10847 | -0.007783 | 0.05706 | 0.15705 | 0.059872 | 0.072207 | -0.04791 | 0.004904 | -0.024333 | 0.019715 | 0.10497 | 0.081393 | 0.10778 | 0.084205
2303.9844 | 122.0306 | -121.7514 | 0.10986 | 0.14017 | -0.031363 | -0.007421 | 0.002454 | 0.040843 | 0.067269 | -0.039826 | 0.01586 | 0.12501 | 0.036985 | 0.035585 | -0.084531 | -0.022561 | -0.056376 | -0.012328 | 0.17221 | 0.00068 | 0.024622 | 0.034497 | 0.072886 | 0.099312 | -0.007783 | 0.047903 | 0.15705 | 0.069028 | 0.067628 | -0.052488 | 0.009482 | -0.024333 | 0.019715 | 0.10039 | 0.072236 | 0.12152 | 0.093361
2305.6719 | 122.0215 | -121.7377 | 0.10071 | 0.13101 | -0.026784 | -0.007421 | -0.002124 | 0.036265 | 0.067269 | -0.044405 | 0.020438 | 0.13416 | 0.036985 | 0.044743 | -0.079953 | -0.017983 | -0.056376 | -0.003172 | 0.16305 | 0.005259 | 0.024622 | 0.029919 | 0.068308 | 0.099312 | -0.012362 | 0.052481 | 0.16621 | 0.069028 | 0.076786 | -0.04791 | 0.01406 | -0.024333 | 0.028871 | 0.10039 | 0.076814 | 0.11694 | 0.093361
2307.4375 | 122.0764 | -121.7194 | 0.086975 | 0.14017 | -0.022205 | -0.012 | 0.002454 | 0.040843 | 0.071848 | -0.03067 | 0.020438 | 0.12501 | 0.046142 | 0.035585 | -0.093688 | -0.022561 | -0.051798 | -0.016906 | 0.17221 | 0.009838 | 0.020043 | 0.034497 | 0.072886 | 0.10389 | 0.001373 | 0.052481 | 0.15705 | 0.078185 | 0.067628 | -0.061645 | 0.009482 | -0.019755 | 0.015137 | 0.11413 | 0.072236 | 0.13983 | 0.09794
2309.1406 | 122.0306 | -121.7331 | 0.11444 | 0.13559 | -0.035942 | -0.012 | 0.002454 | 0.036265 | 0.067269 | -0.035248 | 0.011281 | 0.12958 | 0.041563 | 0.049322 | -0.084531 | -0.022561 | -0.051798 | -0.012328 | 0.16763 | -0.003899 | 0.020043 | 0.034497 | 0.068308 | 0.099312 | -0.003205 | 0.043324 | 0.16163 | 0.073606 | 0.081365 | -0.052488 | 0.009482 | -0.019755 | 0.019715 | 0.095812 | 0.063079 | 0.12609 | 0.093361
2310.8906 | 121.9162 | -121.7606 | 0.14191 | 0.13559 | -0.026784 | -0.012 | -0.002124 | 0.049999 | 0.071848 | -0.039826 | 0.01586 | 0.12043 | 0.041563 | 0.044743 | -0.079953 | -0.027139 | -0.051798 | -0.016906 | 0.16763 | 0.005259 | 0.020043 | 0.029919 | 0.082042 | 0.10389 | -0.007783 | 0.047903 | 0.15247 | 0.073606 | 0.076786 | -0.04791 | 0.004904 | -0.019755 | 0.015137 | 0.095813 | 0.067658 | 0.12152 | 0.093361
2312.6562 | 122.0306 | -121.6965 | 0.13733 | 0.14017 | -0.022205 | -0.007421 | 0.002454 | 0.040843 | 0.071848 | -0.035248 | 0.01586 | 0.12958 | 0.05072 | 0.053901 | -0.08911 | -0.040873 | -0.060955 | -0.016906 | 0.17221 | 0.009838 | 0.024622 | 0.034497 | 0.072886 | 0.10389 | -0.003205 | 0.047903 | 0.16163 | 0.082763 | 0.085944 | -0.057067 | -0.00883 | -0.028912 | 0.015137 | 0.10497 | 0.076815 | 0.13983 | 0.11167
2314.3594 | 122.0306 | -121.4951 | 0.16479 | 0.14474 | -0.022205 | -0.002842 | 0.01619 | 0.059155 | 0.085583 | -0.03067 | 0.079959 | 0.18453 | 0.26132 | 0.25996 | -0.10742 | -0.054607 | -0.065533 | -0.044375 | 0.17679 | 0.009838 | 0.029201 | 0.048233 | 0.091198 | 0.11763 | 0.001373 | 0.112 | 0.21657 | 0.29336 | 0.292 | -0.075379 | -0.022564 | -0.03349 | -0.012332 | 0.18738 | 0.14549 | 0.36874 | 0.32685
2316.1094 | 121.9254 | -121.7148 | 0.14191 | 0.13101 | -0.031363 | -0.007421 | 0.007033 | 0.063733 | 0.071848 | -0.035248 | 0.025017 | 0.12501 | 0.041563 | 0.044743 | -0.084531 | -0.031717 | -0.056376 | -0.016906 | 0.16305 | 0.00068 | 0.024622 | 0.039076 | 0.095776 | 0.10389 | -0.003205 | 0.05706 | 0.15705 | 0.073606 | 0.076786 | -0.052488 | 0.000326 | -0.024333 | 0.015137 | 0.10955 | 0.081393 | 0.12609 | 0.097939
2317.8594 | 121.9437 | -121.7377 | 0.14191 | 0.13101 | -0.031363 | -0.012 | 0.011611 | 0.045421 | 0.071848 | -0.044405 | 0.020438 | 0.12958 | 0.041563 | 0.035585 | -0.079953 | -0.027139 | -0.051798 | -0.016906 | 0.16305 | 0.00068 | 0.020043 | 0.043654 | 0.077464 | 0.10389 | -0.012362 | 0.052481 | 0.16163 | 0.073606 | 0.067628 | -0.04791 | 0.004904 | -0.019755 | 0.015137 | 0.10039 | 0.072236 | 0.12152 | 0.093361
2319.5469 | 122.0123 | -121.7194 | 0.11444 | 0.13559 | -0.031363 | -0.021157 | 0.002454 | 0.040843 | 0.062691 | -0.039826 | 0.020438 | 0.12043 | 0.036985 | 0.040164 | -0.084531 | -0.027139 | -0.04722 | -0.00775 | 0.16763 | 0.00068 | 0.010886 | 0.034497 | 0.072886 | 0.094734 | -0.007783 | 0.052481 | 0.15247 | 0.069028 | 0.072207 | -0.052488 | 0.004904 | -0.015177 | 0.024293 | 0.10497 | 0.067658 | 0.12152 | 0.084205
2321.2344 | 121.875 | -121.7239 | 0.14191 | 0.14017 | -0.035942 | -0.012 | 0.007033 | 0.045421 | 0.067269 | -0.035248 | 0.025017 | 0.11585 | 0.046142 | 0.049322 | -0.079953 | -0.031717 | -0.051798 | -0.016906 | 0.17221 | -0.003899 | 0.020043 | 0.039076 | 0.077464 | 0.099312 | -0.003205 | 0.05706 | 0.14789 | 0.078185 | 0.081365 | -0.04791 | 0.000326 | -0.019755 | 0.015137 | 0.10497 | 0.076815 | 0.1261 | 0.09794
2323 | 121.9849 | -121.7468 | 0.14648 | 0.14017 | -0.026784 | -0.016578 | 0.007033 | 0.045421 | 0.071848 | -0.039826 | 0.01586 | 0.12043 | 0.036985 | 0.040164 | -0.093688 | -0.036295 | -0.065533 | -0.021484 | 0.17221 | 0.005259 | 0.015465 | 0.039076 | 0.077464 | 0.10389 | -0.007783 | 0.047903 | 0.15247 | 0.069028 | 0.072207 | -0.061645 | -0.004252 | -0.03349 | 0.010559 | 0.10955 | 0.081393 | 0.13067 | 0.10252
2324.7031 | 121.9299 | -121.701 | 0.10529 | 0.14017 | -0.035942 | -0.007421 | 0.007033 | 0.049999 | 0.071848 | -0.035248 | 0.025017 | 0.12958 | 0.055298 | 0.049322 | -0.08911 | -0.036295 | -0.065533 | -0.021484 | 0.17221 | -0.003899 | 0.024622 | 0.039076 | 0.082042 | 0.10389 | -0.003205 | 0.05706 | 0.16163 | 0.087341 | 0.081365 | -0.057067 | -0.004252 | -0.03349 | 0.010559 | 0.11413 | 0.09055 | 0.14441 | 0.12083
2326.4531 | 121.9254 | -121.7422 | 0.13275 | 0.14017 | -0.026784 | -0.012 | 0.002454 | 0.040843 | 0.076426 | -0.035248 | 0.020438 | 0.12501 | 0.041563 | 0.044743 | -0.079953 | -0.027139 | -0.051798 | -0.012328 | 0.17221 | 0.005259 | 0.020043 | 0.034497 | 0.072886 | 0.10847 | -0.003205 | 0.052481 | 0.15705 | 0.073606 | 0.076786 | -0.04791 | 0.004904 | -0.019755 | 0.019715 | 0.10039 | 0.072236 | 0.12152 | 0.093361
2328.2031 | 122.0169 | -121.669 | 0.10071 | 0.14932 | -0.031363 | -0.007421 | 0.011611 | 0.054577 | 0.090161 | -0.03067 | 0.079959 | 0.18453 | 0.3071 | 0.32406 | -0.084531 | -0.031717 | -0.060955 | -0.030641 | 0.18136 | 0.00068 | 0.024622 | 0.043654 | 0.08662 | 0.1222 | 0.001373 | 0.112 | 0.21657 | 0.33915 | 0.35611 | -0.052488 | 0.000326 | -0.028912 | 0.001402 | 0.16449 | 0.14091 | 0.39163 | 0.36806
2329.9688 | 121.962 | -121.7148 | 0.10529 | 0.13559 | -0.031363 | -0.016578 | 0.002454 | 0.040843 | 0.081005 | -0.039826 | 0.01586 | 0.12043 | 0.018672 | 0.017268 | -0.079953 | -0.031717 | -0.051798 | -0.003172 | 0.16763 | 0.00068 | 0.015465 | 0.034497 | 0.072886 | 0.11305 | -0.007783 | 0.047903 | 0.15247 | 0.050715 | 0.049311 | -0.04791 | 0.000326 | -0.019755 | 0.028871 | 0.095813 | 0.067658 | 0.098625 | 0.07047
2331.6562 | 121.9757 | -121.7331 | 0.086975 | 0.13559 | -0.035942 | -0.012 | 0.002454 | 0.040843 | 0.076426 | -0.035248 | 0.011281 | 0.12501 | 0.018672 | 0.017268 | -0.075375 | -0.022561 | -0.04722 | -0.012328 | 0.16763 | -0.003899 | 0.020043 | 0.034497 | 0.072886 | 0.10847 | -0.003205 | 0.043324 | 0.15705 | 0.050715 | 0.049311 | -0.043332 | 0.009482 | -0.015177 | 0.019715 | 0.086656 | 0.058501 | 0.094047 | 0.065892
2333.4062 | 122.0444 | -121.7148 | 0.07782 | 0.14932 | -0.026784 | -0.016578 | 0.002454 | 0.049999 | 0.062691 | -0.039826 | 0.011281 | 0.12043 | 0.018672 | 0.026427 | -0.075375 | -0.027139 | -0.051798 | -0.012328 | 0.18136 | 0.005259 | 0.015465 | 0.034497 | 0.082042 | 0.094734 | -0.007783 | 0.043324 | 0.15247 | 0.050715 | 0.05847 | -0.043332 | 0.004904 | -0.019755 | 0.019715 | 0.086656 | 0.063079 | 0.094047 | 0.07047
2335.1562 | 121.9986 | -121.7331 | 0.064087 | 0.14017 | -0.026784 | -0.025735 | -0.002124 | 0.036265 | 0.071848 | -0.035248 | 0.011281 | 0.12043 | 0.027829 | 0.021847 | -0.079953 | -0.031717 | -0.042641 | -0.021484 | 0.17221 | 0.005259 | 0.006308 | 0.029919 | 0.068308 | 0.10389 | -0.003205 | 0.043324 | 0.15247 | 0.059872 | 0.05389 | -0.04791 | 0.000326 | -0.010598 | 0.010559 | 0.091234 | 0.053922 | 0.10778 | 0.07047
2336.9219 | 121.8658 | -121.7651 | 0.10986 | 0.13559 | -0.026784 | -0.016578 | 0.002454 | 0.045421 | 0.076426 | -0.039826 | 0.011281 | 0.12043 | 0.014094 | 0.021847 | -0.084531 | -0.031717 | -0.04722 | -0.012328 | 0.16763 | 0.005259 | 0.015465 | 0.034497 | 0.077464 | 0.10847 | -0.007783 | 0.043324 | 0.15247 | 0.046137 | 0.05389 | -0.052488 | 0.000326 | -0.015177 | 0.019715 | 0.095812 | 0.058501 | 0.098625 | 0.061314
2338.6094 | 121.9345 | -121.7468 | 0.11444 | 0.14017 | -0.026784 | -0.016578 | 0.007033 | 0.040843 | 0.076426 | -0.035248 | 0.01586 | 0.12501 | 0.014094 | 0.021847 | -0.084531 | -0.027139 | -0.051798 | -0.00775 | 0.17221 | 0.005259 | 0.015465 | 0.039076 | 0.072886 | 0.10847 | -0.003205 | 0.047903 | 0.15705 | 0.046137 | 0.05389 | -0.052488 | 0.004904 | -0.019755 | 0.024293 | 0.10039 | 0.067658 | 0.098625 | 0.065892
2340.3594 | 121.962 | -121.7514 | 0.09613 | 0.14474 | -0.031363 | -0.016578 | 0.002454 | 0.040843 | 0.067269 | -0.039826 | 0.01586 | 0.12043 | 0.02325 | 0.021847 | -0.084531 | -0.031717 | -0.056376 | -0.012328 | 0.17679 | 0.00068 | 0.015465 | 0.034497 | 0.072886 | 0.099312 | -0.007783 | 0.047903 | 0.15247 | 0.055293 | 0.05389 | -0.052488 | 0.000326 | -0.024333 | 0.019715 | 0.10039 | 0.072236 | 0.10778 | 0.079626
2342.1094 | 121.9254 | -121.6919 | 0.10529 | 0.14017 | -0.026784 | -0.016578 | 0.002454 | 0.045421 | 0.081005 | -0.035248 | 0.020438 | 0.12043 | 0.018672 | 0.017268 | -0.08911 | -0.050029 | -0.065533 | -0.026063 | 0.17221 | 0.005259 | 0.015465 | 0.034497 | 0.077464 | 0.11305 | -0.003205 | 0.052481 | 0.15247 | 0.050715 | 0.049311 | -0.057067 | -0.017986 | -0.03349 | 0.00598 | 0.10955 | 0.085971 | 0.10778 | 0.084205
2343.7969 | 121.9711 | -121.8109 | 0.10529 | 0.13559 | -0.026784 | -0.007421 | -0.002124 | 0.040843 | 0.071848 | -0.044405 | 0.011281 | 0.11585 | 0.009515 | 0.012689 | -0.075375 | -0.027139 | -0.056376 | -0.012328 | 0.16763 | 0.005259 | 0.024622 | 0.029919 | 0.072886 | 0.10389 | -0.012362 | 0.043324 | 0.14789 | 0.041558 | 0.044732 | -0.043332 | 0.004904 | -0.024333 | 0.019715 | 0.086656 | 0.067657 | 0.08489 | 0.065891
2345.5625 | 122.1039 | -121.7926 | 0.086975 | 0.14017 | -0.026784 | -0.016578 | 0.002454 | 0.036265 | 0.071848 | -0.039826 | 0.011281 | 0.12501 | 0.009515 | 0.021847 | -0.08911 | -0.022561 | -0.051798 | -0.003172 | 0.17221 | 0.005259 | 0.015465 | 0.034497 | 0.068308 | 0.10389 | -0.007783 | 0.043324 | 0.15705 | 0.041558 | 0.05389 | -0.057067 | 0.009482 | -0.019755 | 0.028871 | 0.10039 | 0.063079 | 0.098625 | 0.061313
2347.25 | 122.1405 | -121.7972 | 0.07782 | 0.14474 | -0.031363 | -0.016578 | -0.002124 | 0.045421 | 0.076426 | -0.039826 | 0.01586 | 0.12043 | 0.004937 | 0.017268 | -0.079953 | -0.031717 | -0.051798 | -0.003172 | 0.17679 | 0.00068 | 0.015465 | 0.029919 | 0.077464 | 0.10847 | -0.007783 | 0.047903 | 0.15247 | 0.03698 | 0.049311 | -0.04791 | 0.000326 | -0.019755 | 0.028871 | 0.095813 | 0.067658 | 0.08489 | 0.056735
2349 | 122.1451 | -121.8155 | 0.086975 | 0.14474 | -0.022205 | -0.012 | 0.002454 | 0.045421 | 0.067269 | -0.035248 | 0.011281 | 0.12043 | 0.014094 | 0.012689 | -0.079953 | -0.027139 | -0.056376 | -0.012328 | 0.17679 | 0.009838 | 0.020043 | 0.034497 | 0.077464 | 0.099312 | -0.003205 | 0.043324 | 0.15247 | 0.046137 | 0.044732 | -0.04791 | 0.004904 | -0.024333 | 0.019715 | 0.091234 | 0.067657 | 0.094047 | 0.07047
2350.7656 | 122.0581 | -121.8613 | 0.07782 | 0.14474 | -0.031363 | -0.016578 | 0.002454 | 0.045421 | 0.071848 | -0.039826 | 0.006703 | 0.12043 | 0.004937 | 0.017268 | -0.084531 | -0.027139 | -0.051798 | -0.012328 | 0.17679 | 0.00068 | 0.015465 | 0.034497 | 0.077464 | 0.10389 | -0.007783 | 0.038746 | 0.15247 | 0.03698 | 0.049311 | -0.052488 | 0.004904 | -0.019755 | 0.019715 | 0.091234 | 0.058501 | 0.089468 | 0.056735
2352.5156 | 122.1268 | -121.843 | 0.091553 | 0.14017 | -0.031363 | -0.007421 | -0.006703 | 0.049999 | 0.071848 | -0.044405 | 0.01586 | 0.12043 | 0.014094 | 0.021847 | -0.084531 | -0.031717 | -0.042641 | -0.012328 | 0.17221 | 0.00068 | 0.024622 | 0.02534 | 0.082042 | 0.10389 | -0.012362 | 0.047903 | 0.15247 | 0.046137 | 0.05389 | -0.052488 | 0.000326 | -0.010598 | 0.019715 | 0.10039 | 0.058501 | 0.098625 | 0.056735
2354.2656 | 122.1588 | -121.8292 | 0.082397 | 0.14474 | -0.022205 | -0.016578 | -0.002124 | 0.045421 | 0.067269 | -0.039826 | 0.01586 | 0.12501 | 0.009515 | 0.00811 | -0.084531 | -0.031717 | -0.04722 | -0.012328 | 0.17679 | 0.009838 | 0.015465 | 0.029919 | 0.077464 | 0.099312 | -0.007783 | 0.047903 | 0.15705 | 0.041558 | 0.040153 | -0.052488 | 0.000326 | -0.015177 | 0.019715 | 0.10039 | 0.06308 | 0.094046 | 0.056735
2356.0312 | 122.1451 | -121.8704 | 0.07782 | 0.14474 | -0.026784 | -0.016578 | 0.002454 | 0.049999 | 0.071848 | -0.035248 | 0.01586 | 0.12043 | 0.009515 | 0.00811 | -0.079953 | -0.027139 | -0.051798 | -0.012328 | 0.17679 | 0.005259 | 0.015465 | 0.034497 | 0.082042 | 0.10389 | -0.003205 | 0.047903 | 0.15247 | 0.041558 | 0.040153 | -0.04791 | 0.004904 | -0.019755 | 0.019715 | 0.095813 | 0.067658 | 0.089468 | 0.061313
2357.7344 | 122.0398 | -121.9116 | 0.1236 | 0.14017 | -0.031363 | -0.016578 | -0.002124 | 0.045421 | 0.067269 | -0.039826 | 0.01586 | 0.12043 | 0.004937 | 0.00811 | -0.084531 | -0.022561 | -0.051798 | -0.012328 | 0.17221 | 0.00068 | 0.015465 | 0.029919 | 0.077464 | 0.099312 | -0.007783 | 0.047903 | 0.15247 | 0.03698 | 0.040153 | -0.052488 | 0.009482 | -0.019755 | 0.019715 | 0.10039 | 0.067658 | 0.089468 | 0.056735
2359.4844 | 122.2092 | -121.8613 | 0.059509 | 0.13559 | -0.026784 | -0.012 | -0.002124 | 0.045421 | 0.071848 | -0.039826 | 0.011281 | 0.12043 | 0.014094 | 0.021847 | -0.079953 | -0.027139 | -0.04722 | -0.00775 | 0.16763 | 0.005259 | 0.020043 | 0.029919 | 0.077464 | 0.10389 | -0.007783 | 0.043324 | 0.15247 | 0.046137 | 0.05389 | -0.04791 | 0.004904 | -0.015177 | 0.024293 | 0.091234 | 0.058501 | 0.094047 | 0.061314
2361.1719 | 122.0673 | -121.9116 | 0.091553 | 0.14474 | -0.031363 | -0.016578 | -0.002124 | 0.045421 | 0.071848 | -0.039826 | 0.011281 | 0.12043 | 0.004937 | 0.017268 | -0.08911 | -0.022561 | -0.051798 | -0.012328 | 0.17679 | 0.00068 | 0.015465 | 0.029919 | 0.077464 | 0.10389 | -0.007783 | 0.043324 | 0.15247 | 0.03698 | 0.049311 | -0.057067 | 0.009482 | -0.019755 | 0.019715 | 0.10039 | 0.063079 | 0.094047 | 0.056735
2362.9375 | 122.0901 | -121.8933 | 0.11444 | 0.14017 | -0.031363 | -0.012 | -0.002124 | 0.054577 | 0.081005 | -0.048983 | 0.011281 | 0.12043 | 0.009515 | 0.017268 | -0.084531 | -0.031717 | -0.051798 | -0.012328 | 0.17221 | 0.00068 | 0.020043 | 0.029919 | 0.08662 | 0.11305 | -0.01694 | 0.043324 | 0.15247 | 0.041558 | 0.049311 | -0.052488 | 0.000326 | -0.019755 | 0.019715 | 0.095812 | 0.063079 | 0.094046 | 0.061313
2364.6875 | 122.1451 | -121.9116 | 0.07782 | 0.14474 | -0.022205 | -0.016578 | 0.002454 | 0.049999 | 0.067269 | -0.035248 | 0.020438 | 0.12043 | 0.014094 | 0.017268 | -0.079953 | -0.022561 | -0.051798 | 0.005985 | 0.17679 | 0.009838 | 0.015465 | 0.034497 | 0.082042 | 0.099312 | -0.003205 | 0.052481 | 0.15247 | 0.046137 | 0.049311 | -0.04791 | 0.009482 | -0.019755 | 0.038028 | 0.10039 | 0.072236 | 0.094047 | 0.065892
2366.375 | 122.1405 | -121.9025 | 0.07782 | 0.14474 | -0.031363 | -0.012 | 0.002454 | 0.040843 | 0.076426 | -0.039826 | 0.01586 | 0.12501 | 0.014094 | 0.012689 | -0.079953 | -0.022561 | -0.04722 | -0.012328 | 0.17679 | 0.00068 | 0.020043 | 0.034497 | 0.072886 | 0.10847 | -0.007783 | 0.047903 | 0.15705 | 0.046137 | 0.044732 | -0.04791 | 0.009482 | -0.015177 | 0.019715 | 0.095813 | 0.06308 | 0.094047 | 0.061314
2368.125 | 122.1771 | -121.8704 | 0.073242 | 0.14017 | -0.022205 | -0.012 | 0.007033 | 0.045421 | 0.071848 | -0.039826 | 0.020438 | 0.11585 | 0.009515 | 0.00811 | -0.08911 | -0.022561 | -0.04722 | -0.00775 | 0.17221 | 0.009838 | 0.020043 | 0.039076 | 0.077464 | 0.10389 | -0.007783 | 0.052481 | 0.14789 | 0.041558 | 0.040153 | -0.057067 | 0.009482 | -0.015177 | 0.024293 | 0.10955 | 0.067658 | 0.098625 | 0.056735
2369.875 | 122.0764 | -121.962 | 0.10529 | 0.14932 | -0.031363 | -0.016578 | 0.007033 | 0.049999 | 0.071848 | -0.035248 | 0.01586 | 0.12043 | 0.018672 | 0.012689 | -0.079953 | -0.027139 | -0.042641 | -0.016906 | 0.18136 | 0.00068 | 0.015465 | 0.039076 | 0.082042 | 0.10389 | -0.003205 | 0.047903 | 0.15247 | 0.050715 | 0.044732 | -0.04791 | 0.004904 | -0.010598 | 0.015137 | 0.095813 | 0.058501 | 0.098625 | 0.061313
2371.5625 | 122.113 | -121.9162 | 0.09613 | 0.14474 | -0.022205 | -0.016578 | 0.007033 | 0.040843 | 0.071848 | -0.044405 | 0.01586 | 0.12958 | 0.014094 | 0.017268 | -0.079953 | -0.036295 | -0.04722 | -0.016906 | 0.17679 | 0.009838 | 0.015465 | 0.039076 | 0.072886 | 0.10389 | -0.012362 | 0.047903 | 0.16163 | 0.046137 | 0.049311 | -0.04791 | -0.004252 | -0.015177 | 0.015137 | 0.095813 | 0.06308 | 0.094047 | 0.061314
2373.3125 | 122.2 | -121.9162 | 0.068665 | 0.14017 | -0.026784 | -0.012 | 0.007033 | 0.045421 | 0.071848 | -0.039826 | 0.011281 | 0.12501 | 0.004937 | 0.012689 | -0.070797 | -0.027139 | -0.04722 | -0.00775 | 0.17221 | 0.005259 | 0.020043 | 0.039076 | 0.077464 | 0.10389 | -0.007783 | 0.043324 | 0.15705 | 0.03698 | 0.044732 | -0.038754 | 0.004904 | -0.015177 | 0.024293 | 0.082078 | 0.058501 | 0.075734 | 0.052157
2375.0781 | 122.0764 | -121.9482 | 0.11444 | 0.13559 | -0.026784 | -0.016578 | -0.006703 | 0.040843 | 0.071848 | -0.035248 | 0.011281 | 0.11585 | 0.014094 | 0.012689 | -0.075375 | -0.027139 | -0.051798 | -0.00775 | 0.16763 | 0.005259 | 0.015465 | 0.02534 | 0.072886 | 0.10389 | -0.003205 | 0.043324 | 0.14789 | 0.046137 | 0.044732 | -0.043332 | 0.004904 | -0.019755 | 0.024293 | 0.086656 | 0.063079 | 0.089469 | 0.065892
2376.7656 | 122.0718 | -121.9345 | 0.09613 | 0.14017 | -0.022205 | -0.012 | 0.002454 | 0.049999 | 0.076426 | -0.035248 | 0.01586 | 0.12501 | 0.018672 | 0.00811 | -0.079953 | -0.027139 | -0.042641 | -0.00775 | 0.17221 | 0.009838 | 0.020043 | 0.034497 | 0.082042 | 0.10847 | -0.003205 | 0.047903 | 0.15705 | 0.050715 | 0.040153 | -0.04791 | 0.004904 | -0.010598 | 0.024293 | 0.095813 | 0.058501 | 0.098625 | 0.061313
2378.5156 | 122.0764 | -121.9345 | 0.10986 | 0.14017 | -0.031363 | -0.012 | 0.002454 | 0.049999 | 0.081005 | -0.026092 | 0.006703 | 0.11585 | 0.018672 | 0.012689 | -0.084531 | -0.022561 | -0.04722 | -0.00775 | 0.17221 | 0.00068 | 0.020043 | 0.034497 | 0.082042 | 0.11305 | 0.005951 | 0.038746 | 0.14789 | 0.050715 | 0.044732 | -0.052488 | 0.009482 | -0.015177 | 0.024293 | 0.091234 | 0.053923 | 0.1032 | 0.065892
2380.2031 | 122.1817 | -121.9208 | 0.086975 | 0.14474 | -0.031363 | -0.021157 | 0.011611 | 0.036265 | 0.071848 | -0.039826 | 0.011281 | 0.11127 | 0.014094 | 0.012689 | -0.079953 | -0.027139 | -0.04722 | -0.012328 | 0.17679 | 0.00068 | 0.010886 | 0.043654 | 0.068308 | 0.10389 | -0.007783 | 0.043324 | 0.14331 | 0.046137 | 0.044732 | -0.04791 | 0.004904 | -0.015177 | 0.019715 | 0.091234 | 0.058501 | 0.094047 | 0.061314
2381.9531 | 122.0535 | -121.9345 | 0.11902 | 0.14474 | -0.026784 | -0.021157 | 0.002454 | 0.045421 | 0.081005 | -0.044405 | 0.006703 | 0.12043 | 0.009515 | 0.012689 | -0.075375 | -0.027139 | -0.051798 | -0.00775 | 0.17679 | 0.005259 | 0.010886 | 0.034497 | 0.077464 | 0.11305 | -0.012362 | 0.038746 | 0.15247 | 0.041558 | 0.044732 | -0.043332 | 0.004904 | -0.019755 | 0.024293 | 0.082078 | 0.058501 | 0.08489 | 0.061313
2383.7188 | 122.0901 | -121.962 | 0.10071 | 0.13559 | -0.022205 | -0.012 | 0.002454 | 0.045421 | 0.071848 | -0.03067 | 0.01586 | 0.11585 | 0.009515 | 0.00811 | -0.079953 | -0.022561 | -0.04722 | -0.003172 | 0.16763 | 0.009838 | 0.020043 | 0.034497 | 0.077464 | 0.10389 | 0.001373 | 0.047903 | 0.14789 | 0.041558 | 0.040153 | -0.04791 | 0.009482 | -0.015177 | 0.028871 | 0.095813 | 0.06308 | 0.089468 | 0.056735
2385.4844 | 122.1451 | -121.9116 | 0.10071 | 0.14474 | -0.031363 | -0.012 | 0.007033 | 0.040843 | 0.076426 | -0.03067 | 0.01586 | 0.11585 | 0.014094 | 0.012689 | -0.079953 | -0.027139 | -0.04722 | -0.00775 | 0.17679 | 0.00068 | 0.020043 | 0.039076 | 0.072886 | 0.10847 | 0.001373 | 0.047903 | 0.14789 | 0.046137 | 0.044732 | -0.04791 | 0.004904 | -0.015177 | 0.024293 | 0.095813 | 0.06308 | 0.094047 | 0.061314
2387.2344 | 122.1039 | -121.9711 | 0.09613 | 0.13559 | -0.026784 | -0.021157 | -0.006703 | 0.045421 | 0.071848 | -0.039826 | 0.011281 | 0.11585 | 0.000359 | 0.017268 | -0.084531 | -0.022561 | -0.042641 | -0.00775 | 0.16763 | 0.005259 | 0.010886 | 0.02534 | 0.077464 | 0.10389 | -0.007783 | 0.043324 | 0.14789 | 0.032402 | 0.049311 | -0.052488 | 0.009482 | -0.010598 | 0.024293 | 0.095812 | 0.053922 | 0.08489 | 0.043
2388.9219 | 122.2275 | -121.9162 | 0.064087 | 0.14017 | -0.026784 | -0.016578 | 0.002454 | 0.036265 | 0.071848 | -0.035248 | 0.01586 | 0.12501 | 0.000359 | 0.017268 | -0.08911 | -0.027139 | -0.056376 | -0.012328 | 0.17221 | 0.005259 | 0.015465 | 0.034497 | 0.068308 | 0.10389 | -0.003205 | 0.047903 | 0.15705 | 0.032402 | 0.049311 | -0.057067 | 0.004904 | -0.024333 | 0.019715 | 0.10497 | 0.072236 | 0.089469 | 0.056735
2390.6719 | 122.1771 | -121.9345 | 0.09613 | 0.13559 | -0.035942 | -0.016578 | 0.002454 | 0.040843 | 0.071848 | -0.035248 | 0.011281 | 0.12043 | 0.009515 | 0.003531 | -0.079953 | -0.027139 | -0.04722 | -0.016906 | 0.16763 | -0.003899 | 0.015465 | 0.034497 | 0.072886 | 0.10389 | -0.003205 | 0.043324 | 0.15247 | 0.041558 | 0.035574 | -0.04791 | 0.004904 | -0.015177 | 0.015137 | 0.091234 | 0.058501 | 0.089468 | 0.056735
2392.4219 | 122.0901 | -121.9437 | 0.10986 | 0.13559 | -0.035942 | -0.007421 | 0.007033 | 0.040843 | 0.071848 | -0.035248 | 0.011281 | 0.12043 | 0.004937 | 0.017268 | -0.093688 | -0.017983 | -0.051798 | -0.00775 | 0.16763 | -0.003899 | 0.024622 | 0.039076 | 0.072886 | 0.10389 | -0.003205 | 0.043324 | 0.15247 | 0.03698 | 0.049311 | -0.061645 | 0.01406 | -0.019755 | 0.024293 | 0.10497 | 0.063079 | 0.098625 | 0.056735
2394.1719 | 122.2 | -121.962 | 0.07782 | 0.14474 | -0.026784 | -0.016578 | -0.006703 | 0.040843 | 0.067269 | -0.035248 | 0.01586 | 0.11585 | 0.018672 | 0.021847 | -0.075375 | -0.036295 | -0.04722 | -0.00775 | 0.17679 | 0.005259 | 0.015465 | 0.02534 | 0.072886 | 0.099312 | -0.003205 | 0.047903 | 0.14789 | 0.050715 | 0.05389 | -0.043332 | -0.004252 | -0.015177 | 0.024293 | 0.091235 | 0.06308 | 0.094047 | 0.065892
2395.8594 | 122.1497 | -121.9528 | 0.10986 | 0.14932 | -0.031363 | -0.016578 | 0.002454 | 0.040843 | 0.071848 | -0.035248 | 0.01586 | 0.11585 | 0.009515 | 0.017268 | -0.084531 | -0.031717 | -0.051798 | -0.026063 | 0.18136 | 0.00068 | 0.015465 | 0.034497 | 0.072886 | 0.10389 | -0.003205 | 0.047903 | 0.14789 | 0.041558 | 0.049311 | -0.052488 | 0.000326 | -0.019755 | 0.00598 | 0.10039 | 0.067658 | 0.094046 | 0.061313
2397.6094 | 122.0901 | -121.9711 | 0.1236 | 0.13101 | -0.022205 | -0.016578 | 0.007033 | 0.040843 | 0.071848 | -0.035248 | 0.011281 | 0.12501 | 0.004937 | 0.012689 | -0.079953 | -0.017983 | -0.042641 | -0.00775 | 0.16305 | 0.009838 | 0.015465 | 0.039076 | 0.072886 | 0.10389 | -0.003205 | 0.043324 | 0.15705 | 0.03698 | 0.044732 | -0.04791 | 0.01406 | -0.010598 | 0.024293 | 0.091234 | 0.053922 | 0.08489 | 0.047578
2399.2969 | 122.1085 | -121.9849 | 0.10071 | 0.13101 | -0.022205 | -0.016578 | 0.007033 | 0.045421 | 0.076426 | -0.035248 | 0.020438 | 0.11585 | 0.014094 | 0.012689 | -0.084531 | -0.027139 | -0.056376 | -0.00775 | 0.16305 | 0.009838 | 0.015465 | 0.039076 | 0.077464 | 0.10847 | -0.003205 | 0.052481 | 0.14789 | 0.046137 | 0.044732 | -0.052488 | 0.004904 | -0.024333 | 0.024293 | 0.10497 | 0.076814 | 0.098625 | 0.07047
2401.0625 | 122.2366 | -121.9116 | 0.054932 | 0.14017 | -0.035942 | -0.007421 | 0.002454 | 0.045421 | 0.067269 | -0.035248 | 0.025017 | 0.12501 | 0.014094 | 0.00811 | -0.075375 | -0.022561 | -0.04722 | -0.012328 | 0.17221 | -0.003899 | 0.024622 | 0.034497 | 0.077464 | 0.099312 | -0.003205 | 0.05706 | 0.15705 | 0.046137 | 0.040153 | -0.043332 | 0.009482 | -0.015177 | 0.019715 | 0.10039 | 0.072237 | 0.089469 | 0.061314
2402.75 | 122.2275 | -121.9254 | 0.059509 | 0.14017 | -0.026784 | -0.016578 | 0.002454 | 0.045421 | 0.067269 | -0.03067 | 0.01586 | 0.12043 | 0.009515 | 0.017268 | -0.079953 | -0.031717 | -0.051798 | -0.012328 | 0.17221 | 0.005259 | 0.015465 | 0.034497 | 0.077464 | 0.099312 | 0.001373 | 0.047903 | 0.15247 | 0.041558 | 0.049311 | -0.04791 | 0.000326 | -0.019755 | 0.019715 | 0.095813 | 0.067658 | 0.089468 | 0.061313
2404.5 | 122.2412 | -121.8979 | 0.073242 | 0.13559 | -0.035942 | -0.016578 | -0.006703 | 0.045421 | 0.071848 | -0.035248 | 0.025017 | 0.12043 | 0.009515 | 0.021847 | -0.08911 | -0.031717 | -0.056376 | -0.00775 | 0.16763 | -0.003899 | 0.015465 | 0.02534 | 0.077464 | 0.10389 | -0.003205 | 0.05706 | 0.15247 | 0.041558 | 0.05389 | -0.057067 | 0.000326 | -0.024333 | 0.024293 | 0.11413 | 0.081393 | 0.098625 | 0.065891
2406.2031 | 122.1588 | -121.9437 | 0.091553 | 0.14474 | -0.026784 | -0.012 | 0.002454 | 0.036265 | 0.081005 | -0.035248 | 0.020438 | 0.12501 | 0.009515 | 0.012689 | -0.079953 | -0.017983 | -0.051798 | -0.00775 | 0.17679 | 0.005259 | 0.020043 | 0.034497 | 0.068308 | 0.11305 | -0.003205 | 0.052481 | 0.15705 | 0.041558 | 0.044732 | -0.04791 | 0.01406 | -0.019755 | 0.024293 | 0.10039 | 0.072236 | 0.089468 | 0.061313
2407.9531 | 122.1542 | -121.9849 | 0.10071 | 0.14474 | -0.026784 | -0.025735 | 0.002454 | 0.045421 | 0.076426 | -0.035248 | 0.01586 | 0.12043 | 0.014094 | 0.017268 | -0.079953 | -0.027139 | -0.056376 | -0.016906 | 0.17679 | 0.005259 | 0.006308 | 0.034497 | 0.077464 | 0.10847 | -0.003205 | 0.047903 | 0.15247 | 0.046137 | 0.049311 | -0.04791 | 0.004904 | -0.024333 | 0.015137 | 0.095813 | 0.072236 | 0.094047 | 0.07047
2409.7031 | 122.2504 | -121.9345 | 0.068665 | 0.13101 | -0.026784 | -0.025735 | 0.002454 | 0.040843 | 0.081005 | -0.044405 | 0.006703 | 0.12043 | 0.009515 | 0.021847 | -0.084531 | -0.027139 | -0.051798 | -0.00775 | 0.16305 | 0.005259 | 0.006308 | 0.034497 | 0.072886 | 0.11305 | -0.012362 | 0.038746 | 0.15247 | 0.041558 | 0.05389 | -0.052488 | 0.004904 | -0.019755 | 0.024293 | 0.091234 | 0.058501 | 0.094046 | 0.061313
2411.4688 | 122.2504 | -121.9666 | 0.07782 | 0.13559 | -0.026784 | -0.016578 | 0.002454 | 0.045421 | 0.076426 | -0.039826 | 0.025017 | 0.12501 | 0.004937 | 0.017268 | -0.079953 | -0.022561 | -0.051798 | -0.012328 | 0.16763 | 0.005259 | 0.015465 | 0.034497 | 0.077464 | 0.10847 | -0.007783 | 0.05706 | 0.15705 | 0.03698 | 0.049311 | -0.04791 | 0.009482 | -0.019755 | 0.019715 | 0.10497 | 0.076815 | 0.08489 | 0.056735
2413.2188 | 122.1039 | -121.9849 | 0.11444 | 0.14017 | -0.031363 | -0.012 | -0.002124 | 0.045421 | 0.071848 | -0.035248 | 0.01586 | 0.11585 | 0.009515 | 0.017268 | -0.079953 | -0.031717 | -0.051798 | -0.012328 | 0.17221 | 0.00068 | 0.020043 | 0.029919 | 0.077464 | 0.10389 | -0.003205 | 0.047903 | 0.14789 | 0.041558 | 0.049311 | -0.04791 | 0.000326 | -0.019755 | 0.019715 | 0.095813 | 0.067658 | 0.089468 | 0.061313
2414.9688 | 122.2778 | -121.9437 | 0.07782 | 0.13101 | -0.022205 | -0.016578 | 0.007033 | 0.049999 | 0.071848 | -0.039826 | 0.020438 | 0.12501 | 0.009515 | 0.012689 | -0.08911 | -0.027139 | -0.04722 | -0.012328 | 0.16305 | 0.009838 | 0.015465 | 0.039076 | 0.082042 | 0.10389 | -0.007783 | 0.052481 | 0.15705 | 0.041558 | 0.044732 | -0.057067 | 0.004904 | -0.015177 | 0.019715 | 0.10955 | 0.067658 | 0.098625 | 0.056735
2416.6562 | 122.1634 | -121.994 | 0.10986 | 0.14932 | -0.031363 | -0.016578 | 0.002454 | 0.045421 | 0.067269 | -0.044405 | 0.006703 | 0.12043 | 0.009515 | 0.017268 | -0.084531 | -0.027139 | -0.056376 | -0.016906 | 0.18136 | 0.00068 | 0.015465 | 0.034497 | 0.077464 | 0.099312 | -0.012362 | 0.038746 | 0.15247 | 0.041558 | 0.049311 | -0.052488 | 0.004904 | -0.024333 | 0.015137 | 0.091234 | 0.063079 | 0.094046 | 0.065891
2418.3438 | 122.2275 | -121.9894 | 0.068665 | 0.13559 | -0.031363 | -0.016578 | -0.002124 | 0.045421 | 0.076426 | -0.035248 | 0.020438 | 0.12043 | 0.004937 | 0.012689 | -0.084531 | -0.031717 | -0.051798 | -0.012328 | 0.16763 | 0.00068 | 0.015465 | 0.029919 | 0.077464 | 0.10847 | -0.003205 | 0.052481 | 0.15247 | 0.03698 | 0.044732 | -0.052488 | 0.000326 | -0.019755 | 0.019715 | 0.10497 | 0.072236 | 0.089468 | 0.056735
2420.0938 | 122.2687 | -121.9254 | 0.059509 | 0.14474 | -0.026784 | -0.025735 | -0.002124 | 0.031687 | 0.071848 | -0.044405 | 0.01586 | 0.12501 | 0.009515 | 0.021847 | -0.084531 | -0.027139 | -0.051798 | -0.012328 | 0.17679 | 0.005259 | 0.006308 | 0.029919 | 0.06373 | 0.10389 | -0.012362 | 0.047903 | 0.15705 | 0.041558 | 0.05389 | -0.052488 | 0.004904 | -0.019755 | 0.019715 | 0.10039 | 0.067658 | 0.094046 | 0.061313
2421.7969 | 122.3053 | -121.9574 | 0.054932 | 0.14017 | -0.026784 | -0.021157 | 0.002454 | 0.040843 | 0.071848 | -0.039826 | 0.011281 | 0.11585 | 0.009515 | 0.017268 | -0.075375 | -0.022561 | -0.060955 | -0.003172 | 0.17221 | 0.005259 | 0.010886 | 0.034497 | 0.072886 | 0.10389 | -0.007783 | 0.043324 | 0.14789 | 0.041558 | 0.049311 | -0.043332 | 0.009482 | -0.028912 | 0.028871 | 0.086656 | 0.072236 | 0.08489 | 0.07047
2423.5625 | 122.2733 | -121.9757 | 0.091553 | 0.14474 | -0.022205 | -0.016578 | -0.002124 | 0.040843 | 0.076426 | -0.039826 | 0.020438 | 0.12043 | 0.009515 | 0.012689 | -0.084531 | -0.027139 | -0.04722 | -0.00775 | 0.17679 | 0.009838 | 0.015465 | 0.029919 | 0.072886 | 0.10847 | -0.007783 | 0.052481 | 0.15247 | 0.041558 | 0.044732 | -0.052488 | 0.004904 | -0.015177 | 0.024293 | 0.10497 | 0.067658 | 0.094046 | 0.056735
2425.25 | 122.1405 | -121.9894 | 0.11444 | 0.14017 | -0.031363 | -0.016578 | 0.007033 | 0.045421 | 0.062691 | -0.026092 | 0.01586 | 0.12043 | 0.014094 | 0.017268 | -0.084531 | -0.027139 | -0.051798 | -0.012328 | 0.17221 | 0.00068 | 0.015465 | 0.039076 | 0.077464 | 0.094734 | 0.005951 | 0.047903 | 0.15247 | 0.046137 | 0.049311 | -0.052488 | 0.004904 | -0.019755 | 0.019715 | 0.10039 | 0.067658 | 0.098625 | 0.065892
2427 | 122.2595 | -121.9666 | 0.07782 | 0.14017 | -0.026784 | -0.016578 | -0.006703 | 0.045421 | 0.067269 | -0.035248 | 0.020438 | 0.12043 | 0.009515 | 0.012689 | -0.084531 | -0.022561 | -0.051798 | -0.012328 | 0.17221 | 0.005259 | 0.015465 | 0.02534 | 0.077464 | 0.099312 | -0.003205 | 0.052481 | 0.15247 | 0.041558 | 0.044732 | -0.052488 | 0.009482 | -0.019755 | 0.019715 | 0.10497 | 0.072236 | 0.094046 | 0.061313
2428.6875 | 122.2137 | -121.9666 | 0.068665 | 0.14017 | -0.031363 | -0.016578 | -0.002124 | 0.040843 | 0.067269 | -0.035248 | 0.011281 | 0.11585 | 0.004937 | 0.017268 | -0.075375 | -0.031717 | -0.042641 | -0.012328 | 0.17221 | 0.00068 | 0.015465 | 0.029919 | 0.072886 | 0.099312 | -0.003205 | 0.043324 | 0.14789 | 0.03698 | 0.049311 | -0.043332 | 0.000326 | -0.010598 | 0.019715 | 0.086656 | 0.053922 | 0.080312 | 0.047578
2430.4375 | 122.1771 | -121.994 | 0.10071 | 0.14474 | -0.026784 | -0.016578 | -0.002124 | 0.036265 | 0.076426 | -0.035248 | 0.01586 | 0.12958 | 0.004937 | 0.017268 | -0.079953 | -0.022561 | -0.051798 | -0.00775 | 0.17679 | 0.005259 | 0.015465 | 0.029919 | 0.068308 | 0.10847 | -0.003205 | 0.047903 | 0.16163 | 0.03698 | 0.049311 | -0.04791 | 0.009482 | -0.019755 | 0.024293 | 0.095813 | 0.067658 | 0.08489 | 0.056735
2432.2031 | 122.1817 | -121.9894 | 0.1236 | 0.14474 | -0.031363 | -0.012 | 0.011611 | 0.040843 | 0.076426 | -0.035248 | 0.011281 | 0.11585 | 0.014094 | 0.017268 | -0.084531 | -0.022561 | -0.04722 | -0.00775 | 0.17679 | 0.00068 | 0.020043 | 0.043654 | 0.072886 | 0.10847 | -0.003205 | 0.043324 | 0.14789 | 0.046137 | 0.049311 | -0.052488 | 0.009482 | -0.015177 | 0.024293 | 0.095812 | 0.058501 | 0.098625 | 0.061314
2433.8906 | 122.2183 | -121.9757 | 0.073242 | 0.14932 | -0.026784 | -0.016578 | -0.002124 | 0.040843 | 0.071848 | -0.039826 | 0.01586 | 0.12501 | 0.000359 | 0.017268 | -0.084531 | -0.022561 | -0.04722 | -0.021484 | 0.18136 | 0.005259 | 0.015465 | 0.029919 | 0.072886 | 0.10389 | -0.007783 | 0.047903 | 0.15705 | 0.032402 | 0.049311 | -0.052488 | 0.009482 | -0.015177 | 0.010559 | 0.10039 | 0.06308 | 0.08489 | 0.047579
2435.6562 | 122.2229 | -121.9711 | 0.086975 | 0.13559 | -0.026784 | -0.016578 | -0.002124 | 0.040843 | 0.076426 | -0.035248 | 0.011281 | 0.12501 | 0.009515 | 0.017268 | -0.08911 | -0.022561 | -0.04722 | -0.00775 | 0.16763 | 0.005259 | 0.015465 | 0.029919 | 0.072886 | 0.10847 | -0.003205 | 0.043324 | 0.15705 | 0.041558 | 0.049311 | -0.057067 | 0.009482 | -0.015177 | 0.024293 | 0.10039 | 0.058501 | 0.098625 | 0.056735
2437.4062 | 122.1497 | -122.0078 | 0.11902 | 0.14017 | -0.022205 | -0.016578 | 0.002454 | 0.045421 | 0.071848 | -0.039826 | 0.020438 | 0.12501 | 0.014094 | 0.017268 | -0.084531 | -0.027139 | -0.042641 | -0.003172 | 0.17221 | 0.009838 | 0.015465 | 0.034497 | 0.077464 | 0.10389 | -0.007783 | 0.052481 | 0.15705 | 0.046137 | 0.049311 | -0.052488 | 0.004904 | -0.010598 | 0.028871 | 0.10497 | 0.063079 | 0.098625 | 0.056735
2439.0938 | 122.2641 | -121.9894 | 0.073242 | 0.14474 | -0.031363 | -0.016578 | 0.007033 | 0.049999 | 0.071848 | -0.035248 | 0.01586 | 0.12501 | 0.018672 | 0.012689 | -0.079953 | -0.022561 | -0.051798 | -0.003172 | 0.17679 | 0.00068 | 0.015465 | 0.039076 | 0.082042 | 0.10389 | -0.003205 | 0.047903 | 0.15705 | 0.050715 | 0.044732 | -0.04791 | 0.009482 | -0.019755 | 0.028871 | 0.095813 | 0.067658 | 0.098625 | 0.07047
2440.8594 | 122.1634 | -122.0078 | 0.10529 | 0.14017 | -0.035942 | -0.016578 | 0.002454 | 0.040843 | 0.076426 | -0.035248 | 0.029595 | 0.12043 | 0.014094 | 0.012689 | -0.070797 | -0.022561 | -0.04722 | -0.003172 | 0.17221 | -0.003899 | 0.015465 | 0.034497 | 0.072886 | 0.10847 | -0.003205 | 0.061638 | 0.15247 | 0.046137 | 0.044732 | -0.038754 | 0.009482 | -0.015177 | 0.028871 | 0.10039 | 0.076815 | 0.084891 | 0.061314
2442.625 | 122.2595 | -121.9757 | 0.073242 | 0.14017 | -0.026784 | -0.021157 | 0.002454 | 0.045421 | 0.071848 | -0.035248 | 0.011281 | 0.12501 | 0.014094 | 0.012689 | -0.075375 | -0.022561 | -0.04722 | -0.00775 | 0.17221 | 0.005259 | 0.010886 | 0.034497 | 0.077464 | 0.10389 | -0.003205 | 0.043324 | 0.15705 | 0.046137 | 0.044732 | -0.043332 | 0.009482 | -0.015177 | 0.024293 | 0.086656 | 0.058501 | 0.089469 | 0.061314
2444.3125 | 122.2183 | -121.9666 | 0.091553 | 0.14474 | -0.031363 | -0.021157 | 0.002454 | 0.045421 | 0.071848 | -0.039826 | 0.020438 | 0.13416 | 0.009515 | 0.021847 | -0.079953 | -0.031717 | -0.04722 | -0.00775 | 0.17679 | 0.00068 | 0.010886 | 0.034497 | 0.077464 | 0.10389 | -0.007783 | 0.052481 | 0.16621 | 0.041558 | 0.05389 | -0.04791 | 0.000326 | -0.015177 | 0.024293 | 0.10039 | 0.067658 | 0.089468 | 0.056735
2446.0781 | 122.2092 | -122.0078 | 0.10529 | 0.14474 | -0.026784 | -0.016578 | 0.002454 | 0.045421 | 0.076426 | -0.044405 | 0.020438 | 0.12043 | 0.009515 | 0.017268 | -0.070797 | -0.022561 | -0.051798 | -0.003172 | 0.17679 | 0.005259 | 0.015465 | 0.034497 | 0.077464 | 0.10847 | -0.012362 | 0.052481 | 0.15247 | 0.041558 | 0.049311 | -0.038754 | 0.009482 | -0.019755 | 0.028871 | 0.091235 | 0.072236 | 0.080312 | 0.061313
2447.7656 | 122.2 | -122.0398 | 0.10071 | 0.13559 | -0.026784 | -0.012 | -0.002124 | 0.045421 | 0.076426 | -0.035248 | 0.011281 | 0.12501 | 0.009515 | 0.00811 | -0.084531 | -0.027139 | -0.051798 | -0.012328 | 0.16763 | 0.005259 | 0.020043 | 0.029919 | 0.077464 | 0.10847 | -0.003205 | 0.043324 | 0.15705 | 0.041558 | 0.040153 | -0.052488 | 0.004904 | -0.019755 | 0.019715 | 0.095812 | 0.063079 | 0.094046 | 0.061313
2449.5312 | 122.2412 | -121.9849 | 0.086975 | 0.14017 | -0.031363 | -0.012 | 0.002454 | 0.040843 | 0.062691 | -0.044405 | 0.01586 | 0.12958 | 0.018672 | 0.021847 | -0.079953 | -0.022561 | -0.04722 | -0.00775 | 0.17221 | 0.00068 | 0.020043 | 0.034497 | 0.072886 | 0.094734 | -0.012362 | 0.047903 | 0.16163 | 0.050715 | 0.05389 | -0.04791 | 0.009482 | -0.015177 | 0.024293 | 0.095813 | 0.06308 | 0.098625 | 0.065892
2451.2969 | 122.2504 | -121.9803 | 0.07782 | 0.13559 | -0.026784 | -0.016578 | -0.002124 | 0.040843 | 0.067269 | -0.035248 | 0.01586 | 0.12501 | 0.014094 | 0.021847 | -0.079953 | -0.031717 | -0.04722 | -0.012328 | 0.16763 | 0.005259 | 0.015465 | 0.029919 | 0.072886 | 0.099312 | -0.003205 | 0.047903 | 0.15705 | 0.046137 | 0.05389 | -0.04791 | 0.000326 | -0.015177 | 0.019715 | 0.095813 | 0.06308 | 0.094047 | 0.061314
2453.0781 | 122.1542 | -122.0261 | 0.091553 | 0.14474 | -0.026784 | -0.012 | -0.006703 | 0.040843 | 0.076426 | -0.039826 | 0.01586 | 0.12043 | 0.009515 | 0.021847 | -0.079953 | -0.022561 | -0.04722 | -0.00775 | 0.17679 | 0.005259 | 0.020043 | 0.02534 | 0.072886 | 0.10847 | -0.007783 | 0.047903 | 0.15247 | 0.041558 | 0.05389 | -0.04791 | 0.009482 | -0.015177 | 0.024293 | 0.095813 | 0.06308 | 0.089468 | 0.056735
2454.7656 | 122.2183 | -122.0032 | 0.086975 | 0.14474 | -0.026784 | -0.016578 | -0.002124 | 0.045421 | 0.071848 | -0.044405 | 0.011281 | 0.12501 | 0.004937 | 0.012689 | -0.075375 | -0.022561 | -0.051798 | -0.00775 | 0.17679 | 0.005259 | 0.015465 | 0.029919 | 0.077464 | 0.10389 | -0.012362 | 0.043324 | 0.15705 | 0.03698 | 0.044732 | -0.043332 | 0.009482 | -0.019755 | 0.024293 | 0.086656 | 0.063079 | 0.080312 | 0.056735
2456.5156 | 122.2641 | -122.0078 | 0.086975 | 0.14017 | -0.026784 | -0.016578 | -0.002124 | 0.040843 | 0.067269 | -0.035248 | 0.011281 | 0.12043 | 0.009515 | 0.017268 | -0.079953 | -0.027139 | -0.051798 | -0.012328 | 0.17221 | 0.005259 | 0.015465 | 0.029919 | 0.072886 | 0.099312 | -0.003205 | 0.043324 | 0.15247 | 0.041558 | 0.049311 | -0.04791 | 0.004904 | -0.019755 | 0.019715 | 0.091234 | 0.063079 | 0.089468 | 0.061313
2458.2031 | 122.3099 | -121.962 | 0.073242 | 0.14017 | -0.031363 | -0.016578 | 0.002454 | 0.045421 | 0.071848 | -0.044405 | 0.006703 | 0.11585 | 0.014094 | 0.021847 | -0.079953 | -0.017983 | -0.051798 | -0.012328 | 0.17221 | 0.00068 | 0.015465 | 0.034497 | 0.077464 | 0.10389 | -0.012362 | 0.038746 | 0.14789 | 0.046137 | 0.05389 | -0.04791 | 0.01406 | -0.019755 | 0.019715 | 0.086656 | 0.058501 | 0.094047 | 0.065892
2459.9531 | 122.3145 | -121.9894 | 0.082397 | 0.13559 | -0.022205 | -0.012 | -0.002124 | 0.045421 | 0.076426 | -0.035248 | 0.011281 | 0.12501 | 0.009515 | 0.012689 | -0.079953 | -0.031717 | -0.051798 | -0.00775 | 0.16763 | 0.009838 | 0.020043 | 0.029919 | 0.077464 | 0.10847 | -0.003205 | 0.043324 | 0.15705 | 0.041558 | 0.044732 | -0.04791 | 0.000326 | -0.019755 | 0.024293 | 0.091234 | 0.063079 | 0.089468 | 0.061313
2461.7188 | 122.168 | -122.0444 | 0.10071 | 0.14017 | -0.026784 | -0.016578 | 0.002454 | 0.040843 | 0.067269 | -0.039826 | 0.011281 | 0.12043 | 0.009515 | 0.017268 | -0.079953 | -0.022561 | -0.04722 | -0.012328 | 0.17221 | 0.005259 | 0.015465 | 0.034497 | 0.072886 | 0.099312 | -0.007783 | 0.043324 | 0.15247 | 0.041558 | 0.049311 | -0.04791 | 0.009482 | -0.015177 | 0.019715 | 0.091234 | 0.058501 | 0.089468 | 0.056735
2463.4062 | 122.2046 | -122.0078 | 0.10071 | 0.13559 | -0.031363 | -0.012 | 0.002454 | 0.049999 | 0.067269 | -0.039826 | 0.011281 | 0.12501 | 0.000359 | 0.00811 | -0.075375 | -0.027139 | -0.04722 | -0.012328 | 0.16763 | 0.00068 | 0.020043 | 0.034497 | 0.082042 | 0.099312 | -0.007783 | 0.043324 | 0.15705 | 0.032402 | 0.040153 | -0.043332 | 0.004904 | -0.015177 | 0.019715 | 0.086656 | 0.058501 | 0.075734 | 0.047579
2465.1562 | 122.1817 | -122.049 | 0.10529 | 0.14017 | -0.022205 | -0.016578 | 0.002454 | 0.040843 | 0.076426 | -0.03067 | 0.01586 | 0.12043 | 0.004937 | 0.017268 | -0.079953 | -0.027139 | -0.04722 | -0.00775 | 0.17221 | 0.009838 | 0.015465 | 0.034497 | 0.072886 | 0.10847 | 0.001373 | 0.047903 | 0.15247 | 0.03698 | 0.049311 | -0.04791 | 0.004904 | -0.015177 | 0.024293 | 0.095813 | 0.06308 | 0.08489 | 0.052157
2466.9219 | 122.2824 | -122.0078 | 0.09613 | 0.13559 | -0.026784 | -0.016578 | 0.007033 | 0.045421 | 0.076426 | -0.039826 | 0.01586 | 0.12501 | 0.009515 | 0.012689 | -0.084531 | -0.027139 | -0.051798 | -0.00775 | 0.16763 | 0.005259 | 0.015465 | 0.039076 | 0.077464 | 0.10847 | -0.007783 | 0.047903 | 0.15705 | 0.041558 | 0.044732 | -0.052488 | 0.004904 | -0.019755 | 0.024293 | 0.10039 | 0.067658 | 0.094046 | 0.061313
2468.6875 | 122.2916 | -122.0032 | 0.086975 | 0.14474 | -0.035942 | -0.016578 | -0.002124 | 0.036265 | 0.076426 | -0.039826 | 0.01586 | 0.12501 | 0.009515 | 0.012689 | -0.079953 | -0.031717 | -0.042641 | -0.012328 | 0.17679 | -0.003899 | 0.015465 | 0.029919 | 0.068308 | 0.10847 | -0.007783 | 0.047903 | 0.15705 | 0.041558 | 0.044732 | -0.04791 | 0.000326 | -0.010598 | 0.019715 | 0.095813 | 0.058501 | 0.089468 | 0.052156
2470.375 | 122.1817 | -122.0261 | 0.1236 | 0.14474 | -0.026784 | -0.012 | 0.002454 | 0.040843 | 0.076426 | -0.035248 | 0.01586 | 0.12043 | 0.009515 | 0.012689 | -0.075375 | -0.022561 | -0.056376 | -0.012328 | 0.17679 | 0.005259 | 0.020043 | 0.034497 | 0.072886 | 0.10847 | -0.003205 | 0.047903 | 0.15247 | 0.041558 | 0.044732 | -0.043332 | 0.009482 | -0.024333 | 0.019715 | 0.091235 | 0.072236 | 0.08489 | 0.065891
2472.1406 | 122.168 | -122.0444 | 0.11444 | 0.14017 | -0.026784 | -0.012 | 0.002454 | 0.049999 | 0.067269 | -0.035248 | 0.020438 | 0.12501 | 0.004937 | 0.017268 | -0.079953 | -0.027139 | -0.042641 | -0.003172 | 0.17221 | 0.005259 | 0.020043 | 0.034497 | 0.082042 | 0.099312 | -0.003205 | 0.052481 | 0.15705 | 0.03698 | 0.049311 | -0.04791 | 0.004904 | -0.010598 | 0.028871 | 0.10039 | 0.063079 | 0.08489 | 0.047578
2473.9062 | 122.1634 | -122.0352 | 0.11902 | 0.13559 | -0.031363 | -0.016578 | -0.002124 | 0.045421 | 0.071848 | -0.035248 | 0.025017 | 0.12043 | 0.018672 | 0.017268 | -0.079953 | -0.017983 | -0.04722 | -0.003172 | 0.16763 | 0.00068 | 0.015465 | 0.029919 | 0.077464 | 0.10389 | -0.003205 | 0.05706 | 0.15247 | 0.050715 | 0.049311 | -0.04791 | 0.01406 | -0.015177 | 0.028871 | 0.10497 | 0.072237 | 0.098625 | 0.065892
2475.6094 | 122.2183 | -121.9849 | 0.12817 | 0.13559 | -0.031363 | -0.016578 | 0.002454 | 0.040843 | 0.071848 | -0.035248 | 0.020438 | 0.12043 | 0.018672 | 0.012689 | -0.070797 | -0.022561 | -0.051798 | -0.00775 | 0.16763 | 0.00068 | 0.015465 | 0.034497 | 0.072886 | 0.10389 | -0.003205 | 0.052481 | 0.15247 | 0.050715 | 0.044732 | -0.038754 | 0.009482 | -0.019755 | 0.024293 | 0.091235 | 0.072236 | 0.089469 | 0.07047
2477.2969 | 122.2549 | -122.0261 | 0.064087 | 0.14017 | -0.026784 | -0.021157 | 0.007033 | 0.045421 | 0.071848 | -0.035248 | 0.020438 | 0.12043 | 0.004937 | 0.017268 | -0.070797 | -0.027139 | -0.04722 | -0.00775 | 0.17221 | 0.005259 | 0.010886 | 0.039076 | 0.077464 | 0.10389 | -0.003205 | 0.052481 | 0.15247 | 0.03698 | 0.049311 | -0.038754 | 0.004904 | -0.015177 | 0.024293 | 0.091235 | 0.067658 | 0.075734 | 0.052157
2479.0469 | 122.2549 | -122.0078 | 0.091553 | 0.14474 | -0.026784 | -0.016578 | 0.002454 | 0.049999 | 0.071848 | -0.039826 | 0.020438 | 0.12501 | 0.014094 | 0.017268 | -0.075375 | -0.013405 | -0.051798 | -0.00775 | 0.17679 | 0.005259 | 0.015465 | 0.034497 | 0.082042 | 0.10389 | -0.007783 | 0.052481 | 0.15705 | 0.046137 | 0.049311 | -0.043332 | 0.018638 | -0.019755 | 0.024293 | 0.095813 | 0.072236 | 0.089469 | 0.065892
2480.7969 | 122.2961 | -122.0032 | 0.068665 | 0.13559 | -0.026784 | -0.012 | -0.002124 | 0.045421 | 0.067269 | -0.039826 | 0.01586 | 0.12043 | 0.000359 | 0.017268 | -0.075375 | -0.022561 | -0.051798 | -0.00775 | 0.16763 | 0.005259 | 0.020043 | 0.029919 | 0.077464 | 0.099312 | -0.007783 | 0.047903 | 0.15247 | 0.032402 | 0.049311 | -0.043332 | 0.009482 | -0.019755 | 0.024293 | 0.091235 | 0.067658 | 0.075734 | 0.052157
2482.5 | 122.1771 | -122.0581 | 0.11444 | 0.13559 | -0.026784 | -0.016578 | 0.011611 | 0.040843 | 0.076426 | -0.044405 | 0.025017 | 0.12501 | 0.014094 | 0.026427 | -0.075375 | -0.022561 | -0.04722 | -0.00775 | 0.16763 | 0.005259 | 0.015465 | 0.043654 | 0.072886 | 0.10847 | -0.012362 | 0.05706 | 0.15705 | 0.046137 | 0.05847 | -0.043332 | 0.009482 | -0.015177 | 0.024293 | 0.10039 | 0.072237 | 0.089469 | 0.061314
2484.25 | 122.3145 | -122.0078 | 0.054932 | 0.13559 | -0.031363 | -0.012 | -0.002124 | 0.045421 | 0.076426 | -0.035248 | 0.020438 | 0.12958 | 0.004937 | 0.012689 | -0.079953 | -0.022561 | -0.051798 | -0.00775 | 0.16763 | 0.00068 | 0.020043 | 0.029919 | 0.077464 | 0.10847 | -0.003205 | 0.052481 | 0.16163 | 0.03698 | 0.044732 | -0.04791 | 0.009482 | -0.019755 | 0.024293 | 0.10039 | 0.072236 | 0.08489 | 0.056735
2486 | 122.2733 | -122.0078 | 0.082397 | 0.14474 | -0.026784 | -0.016578 | -0.002124 | 0.045421 | 0.071848 | -0.039826 | 0.011281 | 0.12501 | 0.004937 | 0.017268 | -0.075375 | -0.022561 | -0.042641 | -0.012328 | 0.17679 | 0.005259 | 0.015465 | 0.029919 | 0.077464 | 0.10389 | -0.007783 | 0.043324 | 0.15705 | 0.03698 | 0.049311 | -0.043332 | 0.009482 | -0.010598 | 0.019715 | 0.086656 | 0.053922 | 0.080312 | 0.047578
2487.7031 | 122.1909 | -122.0398 | 0.11444 | 0.14017 | -0.026784 | -0.016578 | -0.002124 | 0.036265 | 0.067269 | -0.039826 | 0.01586 | 0.12043 | 0.014094 | 0.012689 | -0.075375 | -0.022561 | -0.04722 | -0.00775 | 0.17221 | 0.005259 | 0.015465 | 0.029919 | 0.068308 | 0.099312 | -0.007783 | 0.047903 | 0.15247 | 0.046137 | 0.044732 | -0.043332 | 0.009482 | -0.015177 | 0.024293 | 0.091235 | 0.06308 | 0.089469 | 0.061314
2489.4531 | 122.1771 | -122.0535 | 0.12817 | 0.13559 | -0.031363 | -0.012 | 0.002454 | 0.045421 | 0.062691 | -0.035248 | 0.020438 | 0.12043 | 0.009515 | 0.017268 | -0.079953 | -0.031717 | -0.04722 | -0.012328 | 0.16763 | 0.00068 | 0.020043 | 0.034497 | 0.077464 | 0.094734 | -0.003205 | 0.052481 | 0.15247 | 0.041558 | 0.049311 | -0.04791 | 0.000326 | -0.015177 | 0.019715 | 0.10039 | 0.067658 | 0.089468 | 0.056735
2491.2031 | 122.3236 | -122.0078 | 0.07782 | 0.14474 | -0.026784 | -0.021157 | -0.002124 | 0.027109 | 0.071848 | -0.03067 | 0.01586 | 0.12501 | 0.009515 | 0.021847 | -0.075375 | -0.017983 | -0.051798 | -0.021484 | 0.17679 | 0.005259 | 0.010886 | 0.029919 | 0.059152 | 0.10389 | 0.001373 | 0.047903 | 0.15705 | 0.041558 | 0.05389 | -0.043332 | 0.01406 | -0.019755 | 0.010559 | 0.091235 | 0.067658 | 0.08489 | 0.061313
2492.8906 | 122.1863 | -122.0169 | 0.12817 | 0.14474 | -0.031363 | -0.021157 | -0.002124 | 0.036265 | 0.081005 | -0.035248 | 0.020438 | 0.12043 | 0.009515 | 0.021847 | -0.075375 | -0.027139 | -0.051798 | -0.012328 | 0.17679 | 0.00068 | 0.010886 | 0.029919 | 0.068308 | 0.11305 | -0.003205 | 0.052481 | 0.15247 | 0.041558 | 0.05389 | -0.043332 | 0.004904 | -0.019755 | 0.019715 | 0.095813 | 0.072236 | 0.08489 | 0.061313
2494.6406 | 122.2092 | -122.049 | 0.10986 | 0.14017 | -0.035942 | -0.021157 | 0.002454 | 0.045421 | 0.076426 | -0.035248 | 0.025017 | 0.12043 | 0.009515 | 0.012689 | -0.079953 | -0.027139 | -0.04722 | -0.00775 | 0.17221 | -0.003899 | 0.010886 | 0.034497 | 0.077464 | 0.10847 | -0.003205 | 0.05706 | 0.15247 | 0.041558 | 0.044732 | -0.04791 | 0.004904 | -0.015177 | 0.024293 | 0.10497 | 0.072237 | 0.089468 | 0.056735
2496.3281 | 122.1954 | -122.0581 | 0.11902 | 0.14017 | -0.022205 | -0.016578 | 0.002454 | 0.049999 | 0.081005 | -0.035248 | 0.01586 | 0.12501 | 0.009515 | 0.021847 | -0.079953 | -0.027139 | -0.056376 | -0.003172 | 0.17221 | 0.009838 | 0.015465 | 0.034497 | 0.082042 | 0.11305 | -0.003205 | 0.047903 | 0.15705 | 0.041558 | 0.05389 | -0.04791 | 0.004904 | -0.024333 | 0.028871 | 0.095813 | 0.072236 | 0.089468 | 0.065891
2498.1094 | 122.2229 | -122.049 | 0.10071 | 0.14017 | -0.026784 | -0.021157 | -0.002124 | 0.049999 | 0.067269 | -0.03067 | 0.025017 | 0.12501 | 0.004937 | 0.017268 | -0.084531 | -0.027139 | -0.051798 | -0.012328 | 0.17221 | 0.005259 | 0.010886 | 0.029919 | 0.082042 | 0.099312 | 0.001373 | 0.05706 | 0.15705 | 0.03698 | 0.049311 | -0.052488 | 0.004904 | -0.019755 | 0.019715 | 0.10955 | 0.076815 | 0.089468 | 0.056735
2499.7969 | 122.2046 | -122.081 | 0.10529 | 0.13559 | -0.026784 | -0.012 | -0.006703 | 0.040843 | 0.076426 | -0.039826 | 0.011281 | 0.12501 | 0.009515 | 0.021847 | -0.075375 | -0.017983 | -0.04722 | -0.012328 | 0.16763 | 0.005259 | 0.020043 | 0.02534 | 0.072886 | 0.10847 | -0.007783 | 0.043324 | 0.15705 | 0.041558 | 0.05389 | -0.043332 | 0.01406 | -0.015177 | 0.019715 | 0.086656 | 0.058501 | 0.08489 | 0.056735
2501.5469 | 122.3282 | -122.0123 | 0.086975 | 0.14017 | -0.035942 | -0.016578 | -0.006703 | 0.045421 | 0.067269 | -0.03067 | 0.020438 | 0.12501 | 0.014094 | 0.017268 | -0.079953 | -0.027139 | -0.04722 | -0.012328 | 0.17221 | -0.003899 | 0.015465 | 0.02534 | 0.077464 | 0.099312 | 0.001373 | 0.052481 | 0.15705 | 0.046137 | 0.049311 | -0.04791 | 0.004904 | -0.015177 | 0.019715 | 0.10039 | 0.067658 | 0.094047 | 0.061314
2503.2969 | 122.2733 | -122.0215 | 0.091553 | 0.14474 | -0.026784 | -0.012 | -0.002124 | 0.045421 | 0.067269 | -0.035248 | 0.029595 | 0.12043 | 0.000359 | 0.021847 | -0.075375 | -0.027139 | -0.04722 | -0.012328 | 0.17679 | 0.005259 | 0.020043 | 0.029919 | 0.077464 | 0.099312 | -0.003205 | 0.061638 | 0.15247 | 0.032402 | 0.05389 | -0.043332 | 0.004904 | -0.015177 | 0.019715 | 0.10497 | 0.076815 | 0.075734 | 0.047579
2505.0469 | 122.319 | -122.0169 | 0.082397 | 0.13559 | -0.017627 | -0.016578 | -0.006703 | 0.045421 | 0.067269 | -0.044405 | 0.01586 | 0.12958 | 0.018672 | 0.017268 | -0.075375 | -0.022561 | -0.051798 | -0.012328 | 0.16763 | 0.014416 | 0.015465 | 0.02534 | 0.077464 | 0.099312 | -0.012362 | 0.047903 | 0.16163 | 0.050715 | 0.049311 | -0.043332 | 0.009482 | -0.019755 | 0.019715 | 0.091235 | 0.067658 | 0.094047 | 0.07047
2506.7344 | 122.319 | -122.0261 | 0.086975 | 0.13101 | -0.031363 | -0.012 | -0.006703 | 0.040843 | 0.067269 | -0.035248 | 0.020438 | 0.12043 | 0.000359 | 0.012689 | -0.079953 | -0.017983 | -0.042641 | -0.012328 | 0.16305 | 0.00068 | 0.020043 | 0.02534 | 0.072886 | 0.099312 | -0.003205 | 0.052481 | 0.15247 | 0.032402 | 0.044732 | -0.04791 | 0.01406 | -0.010598 | 0.019715 | 0.10039 | 0.063079 | 0.080312 | 0.043
2508.5 | 122.1817 | -122.0535 | 0.1236 | 0.14017 | -0.026784 | -0.012 | 0.002454 | 0.045421 | 0.071848 | -0.039826 | 0.020438 | 0.12501 | 0.014094 | 0.026427 | -0.075375 | -0.022561 | -0.051798 | -0.012328 | 0.17221 | 0.005259 | 0.020043 | 0.034497 | 0.077464 | 0.10389 | -0.007783 | 0.052481 | 0.15705 | 0.046137 | 0.05847 | -0.043332 | 0.009482 | -0.019755 | 0.019715 | 0.095813 | 0.072236 | 0.089469 | 0.065892
2510.2031 | 122.3373 | -122.0306 | 0.086975 | 0.13559 | -0.031363 | -0.016578 | -0.002124 | 0.045421 | 0.071848 | -0.039826 | 0.01586 | 0.12043 | 0.004937 | 0.017268 | -0.075375 | -0.027139 | -0.051798 | -0.012328 | 0.16763 | 0.00068 | 0.015465 | 0.029919 | 0.077464 | 0.10389 | -0.007783 | 0.047903 | 0.15247 | 0.03698 | 0.049311 | -0.043332 | 0.004904 | -0.019755 | 0.019715 | 0.091235 | 0.067658 | 0.080312 | 0.056735
2511.9531 | 122.2687 | -122.0169 | 0.091553 | 0.14017 | -0.031363 | -0.021157 | -0.006703 | 0.045421 | 0.071848 | -0.044405 | 0.01586 | 0.12501 | 0.009515 | 0.017268 | -0.079953 | -0.022561 | -0.051798 | -0.012328 | 0.17221 | 0.00068 | 0.010886 | 0.02534 | 0.077464 | 0.10389 | -0.012362 | 0.047903 | 0.15705 | 0.041558 | 0.049311 | -0.04791 | 0.009482 | -0.019755 | 0.019715 | 0.095813 | 0.067658 | 0.089468 | 0.061313
2513.7031 | 122.3602 | -122.0261 | 0.082397 | 0.13559 | -0.031363 | -0.021157 | 0.007033 | 0.045421 | 0.067269 | -0.044405 | 0.020438 | 0.12958 | 0.009515 | 0.017268 | -0.075375 | -0.022561 | -0.04722 | -0.00775 | 0.16763 | 0.00068 | 0.010886 | 0.039076 | 0.077464 | 0.099312 | -0.012362 | 0.052481 | 0.16163 | 0.041558 | 0.049311 | -0.043332 | 0.009482 | -0.015177 | 0.024293 | 0.095813 | 0.067658 | 0.08489 | 0.056735
2515.3906 | 122.1954 | -122.0673 | 0.11902 | 0.13559 | -0.022205 | -0.021157 | 0.002454 | 0.045421 | 0.062691 | -0.035248 | 0.025017 | 0.12043 | 0.004937 | 0.012689 | -0.070797 | -0.022561 | -0.051798 | -0.00775 | 0.16763 | 0.009838 | 0.010886 | 0.034497 | 0.077464 | 0.094734 | -0.003205 | 0.05706 | 0.15247 | 0.03698 | 0.044732 | -0.038754 | 0.009482 | -0.019755 | 0.024293 | 0.095814 | 0.076815 | 0.075734 | 0.056735
2517.1406 | 122.2595 | -122.0535 | 0.10986 | 0.14017 | -0.035942 | -0.016578 | 0.002454 | 0.040843 | 0.081005 | -0.039826 | 0.01586 | 0.12043 | 0.014094 | 0.017268 | -0.070797 | -0.022561 | -0.04722 | -0.00775 | 0.17221 | -0.003899 | 0.015465 | 0.034497 | 0.072886 | 0.11305 | -0.007783 | 0.047903 | 0.15247 | 0.046137 | 0.049311 | -0.038754 | 0.009482 | -0.015177 | 0.024293 | 0.086657 | 0.06308 | 0.084891 | 0.061314
2518.8281 | 122.2595 | -122.0398 | 0.10986 | 0.14017 | -0.031363 | -0.021157 | 0.002454 | 0.045421 | 0.071848 | -0.035248 | 0.01586 | 0.12501 | 0.004937 | 0.017268 | -0.079953 | -0.036295 | -0.04722 | -0.012328 | 0.17221 | 0.00068 | 0.010886 | 0.034497 | 0.077464 | 0.10389 | -0.003205 | 0.047903 | 0.15705 | 0.03698 | 0.049311 | -0.04791 | -0.004252 | -0.015177 | 0.019715 | 0.095813 | 0.06308 | 0.08489 | 0.052157
2520.5781 | 122.319 | -122.0123 | 0.091553 | 0.13559 | -0.035942 | -0.016578 | -0.006703 | 0.049999 | 0.067269 | -0.039826 | 0.01586 | 0.13416 | 0.009515 | 0.021847 | -0.075375 | -0.022561 | -0.051798 | -0.00775 | 0.16763 | -0.003899 | 0.015465 | 0.02534 | 0.082042 | 0.099312 | -0.007783 | 0.047903 | 0.16621 | 0.041558 | 0.05389 | -0.043332 | 0.009482 | -0.019755 | 0.024293 | 0.091235 | 0.067658 | 0.08489 | 0.061313
2522.2812 | 122.3053 | -122.0215 | 0.086975 | 0.13559 | -0.022205 | -0.016578 | -0.006703 | 0.045421 | 0.067269 | -0.035248 | 0.01586 | 0.12958 | -0.008798 | 0.012689 | -0.079953 | -0.022561 | -0.04722 | -0.012328 | 0.16763 | 0.009838 | 0.015465 | 0.02534 | 0.077464 | 0.099312 | -0.003205 | 0.047903 | 0.16163 | 0.023245 | 0.044732 | -0.04791 | 0.009482 | -0.015177 | 0.019715 | 0.095813 | 0.06308 | 0.071155 | 0.038422
2524.0469 | 122.3511 | -122.0261 | 0.07782 | 0.14474 | -0.031363 | -0.012 | -0.006703 | 0.045421 | 0.067269 | -0.039826 | 0.020438 | 0.12958 | 0.004937 | 0.021847 | -0.075375 | -0.027139 | -0.051798 | -0.012328 | 0.17679 | 0.00068 | 0.020043 | 0.02534 | 0.077464 | 0.099312 | -0.007783 | 0.052481 | 0.16163 | 0.03698 | 0.05389 | -0.043332 | 0.004904 | -0.019755 | 0.019715 | 0.095813 | 0.072236 | 0.080312 | 0.056735
2525.7344 | 122.3557 | -122.0352 | 0.07782 | 0.13559 | -0.026784 | -0.016578 | -0.006703 | 0.036265 | 0.071848 | -0.039826 | 0.020438 | 0.12501 | 0.000359 | 0.021847 | -0.079953 | -0.022561 | -0.04722 | -0.012328 | 0.16763 | 0.005259 | 0.015465 | 0.02534 | 0.068308 | 0.10389 | -0.007783 | 0.052481 | 0.15705 | 0.032402 | 0.05389 | -0.04791 | 0.009482 | -0.015177 | 0.019715 | 0.10039 | 0.067658 | 0.080312 | 0.047579
2527.4844 | 122.3419 | -122.0261 | 0.086975 | 0.14017 | -0.031363 | -0.007421 | 0.002454 | 0.036265 | 0.071848 | -0.035248 | 0.01586 | 0.11585 | 0.000359 | 0.017268 | -0.08911 | -0.022561 | -0.04722 | -0.00775 | 0.17221 | 0.00068 | 0.024622 | 0.034497 | 0.068308 | 0.10389 | -0.003205 | 0.047903 | 0.14789 | 0.032402 | 0.049311 | -0.057067 | 0.009482 | -0.015177 | 0.024293 | 0.10497 | 0.06308 | 0.089469 | 0.047579
2529.2344 | 122.2549 | -122.0627 | 0.09613 | 0.14017 | -0.031363 | -0.007421 | 0.002454 | 0.045421 | 0.058113 | -0.035248 | 0.01586 | 0.12501 | 0.004937 | 0.017268 | -0.079953 | -0.022561 | -0.042641 | -0.012328 | 0.17221 | 0.00068 | 0.024622 | 0.034497 | 0.077464 | 0.090156 | -0.003205 | 0.047903 | 0.15705 | 0.03698 | 0.049311 | -0.04791 | 0.009482 | -0.010598 | 0.019715 | 0.095813 | 0.058501 | 0.08489 | 0.047578
2531 | 122.2504 | -122.0764 | 0.10986 | 0.13559 | -0.026784 | -0.012 | 0.002454 | 0.040843 | 0.071848 | -0.044405 | 0.01586 | 0.12501 | 0.014094 | 0.017268 | -0.079953 | -0.022561 | -0.04722 | -0.00775 | 0.16763 | 0.005259 | 0.020043 | 0.034497 | 0.072886 | 0.10389 | -0.012362 | 0.047903 | 0.15705 | 0.046137 | 0.049311 | -0.04791 | 0.009482 | -0.015177 | 0.024293 | 0.095813 | 0.06308 | 0.094047 | 0.061314
2532.7031 | 122.374 | -122.0261 | 0.082397 | 0.14017 | -0.031363 | -0.025735 | -0.002124 | 0.045421 | 0.076426 | -0.035248 | 0.011281 | 0.12501 | 0.004937 | 0.021847 | -0.075375 | -0.031717 | -0.056376 | -0.012328 | 0.17221 | 0.00068 | 0.006308 | 0.029919 | 0.077464 | 0.10847 | -0.003205 | 0.043324 | 0.15705 | 0.03698 | 0.05389 | -0.043332 | 0.000326 | -0.024333 | 0.019715 | 0.086656 | 0.067657 | 0.080312 | 0.061313
2534.4688 | 122.3282 | -122.0169 | 0.082397 | 0.14017 | -0.026784 | -0.016578 | 0.002454 | 0.045421 | 0.071848 | -0.039826 | 0.01586 | 0.11585 | 0.009515 | 0.017268 | -0.070797 | -0.022561 | -0.060955 | -0.00775 | 0.17221 | 0.005259 | 0.015465 | 0.034497 | 0.077464 | 0.10389 | -0.007783 | 0.047903 | 0.14789 | 0.041558 | 0.049311 | -0.038754 | 0.009482 | -0.028912 | 0.024293 | 0.086657 | 0.076815 | 0.080312 | 0.07047
2536.1562 | 122.3648 | -122.0215 | 0.073242 | 0.14474 | -0.022205 | -0.016578 | -0.002124 | 0.040843 | 0.067269 | -0.035248 | 0.020438 | 0.12501 | 0.004937 | 0.017268 | -0.079953 | -0.027139 | -0.051798 | -0.00775 | 0.17679 | 0.009838 | 0.015465 | 0.029919 | 0.072886 | 0.099312 | -0.003205 | 0.052481 | 0.15705 | 0.03698 | 0.049311 | -0.04791 | 0.004904 | -0.019755 | 0.024293 | 0.10039 | 0.072236 | 0.08489 | 0.056735
2537.9219 | 121.2524 | -50.7202 | 56.3553 | 0.14017 | -0.026784 | -0.021157 | 0.002454 | 0.054577 | 0.081005 | -0.026092 | 0.020438 | 0.12958 | 0.059877 | 0.021847 | -0.14863 | -0.09581 | -0.12047 | -0.094735 | 0.17221 | 0.005259 | 0.010886 | 0.034497 | 0.08662 | 0.11305 | 0.005951 | 0.052481 | 0.16163 | 0.09192 | 0.05389 | -0.11658 | -0.063767 | -0.088431 | -0.062692 | 0.16906 | 0.14091 | 0.2085 | 0.18035
2539.6719 | 121.6736 | -0.082397 | 121.2067 | 0.14017 | -0.031363 | -0.016578 | -0.002124 | 0.036265 | 0.067269 | -0.039826 | 0.011281 | 0.12958 | 0.000359 | 0.012689 | -0.070797 | -0.017983 | -0.04722 | -0.00775 | 0.17221 | 0.00068 | 0.015465 | 0.029919 | 0.068308 | 0.099312 | -0.007783 | 0.043324 | 0.16163 | 0.032402 | 0.044732 | -0.038754 | 0.01406 | -0.015177 | 0.024293 | 0.082078 | 0.058501 | 0.071156 | 0.047579
2541.4219 | 121.7697 | -0.09613 | 121.1334 | 0.14017 | -0.031363 | -0.021157 | 0.007033 | 0.036265 | 0.062691 | -0.035248 | 0.011281 | 0.12043 | -0.004219 | 0.00811 | -0.079953 | -0.017983 | -0.04722 | -0.00775 | 0.17221 | 0.00068 | 0.010886 | 0.039076 | 0.068308 | 0.094734 | -0.003205 | 0.043324 | 0.15247 | 0.027824 | 0.040153 | -0.04791 | 0.01406 | -0.015177 | 0.024293 | 0.091234 | 0.058501 | 0.075734 | 0.043001
2543.125 | 121.3348 | -0.054932 | 117.8741 | 0.14017 | -0.022205 | -0.021157 | -0.002124 | 0.040843 | 0.062691 | -0.035248 | 0.011281 | 0.12043 | -0.013376 | 0.003531 | -0.075375 | -0.022561 | -0.04722 | -0.00775 | 0.17221 | 0.009838 | 0.010886 | 0.029919 | 0.072886 | 0.094734 | -0.003205 | 0.043324 | 0.15247 | 0.018667 | 0.035574 | -0.043332 | 0.009482 | -0.015177 | 0.024293 | 0.086656 | 0.058501 | 0.061999 | 0.033844
2544.875 | 117.1509 | -40.6631 | 76.6342 | 0.13559 | -0.031363 | -0.021157 | -0.011281 | 0.036265 | 0.076426 | -0.035248 | 0.020438 | 0.12043 | -0.004219 | 0.003531 | -0.079953 | -0.022561 | -0.038063 | -0.012328 | 0.16763 | 0.00068 | 0.010886 | 0.020762 | 0.068308 | 0.10847 | -0.003205 | 0.052481 | 0.15247 | 0.027824 | 0.035574 | -0.04791 | 0.009482 | -0.00602 | 0.019715 | 0.10039 | 0.058501 | 0.075734 | 0.033844
2546.5625 | 121.3989 | -0.42572 | 120.0256 | 0.14017 | -0.026784 | -0.012 | -0.011281 | 0.045421 | 0.062691 | -0.035248 | 0.01586 | 0.12043 | -0.004219 | 0.003531 | -0.075375 | -0.017983 | -0.051798 | -0.00775 | 0.17221 | 0.005259 | 0.020043 | 0.020762 | 0.077464 | 0.094734 | -0.003205 | 0.047903 | 0.15247 | 0.027824 | 0.035574 | -0.043332 | 0.01406 | -0.019755 | 0.024293 | 0.091235 | 0.067658 | 0.071156 | 0.047579
2548.3125 | 121.2845 | -0.27466 | 115.8234 | 0.13559 | -0.026784 | -0.016578 | 0.002454 | 0.040843 | 0.076426 | -0.044405 | 0.011281 | 0.11585 | -0.004219 | 0.003531 | -0.075375 | -0.027139 | -0.056376 | -0.00775 | 0.16763 | 0.005259 | 0.015465 | 0.034497 | 0.072886 | 0.10847 | -0.012362 | 0.043324 | 0.14789 | 0.027824 | 0.035574 | -0.043332 | 0.004904 | -0.024333 | 0.024293 | 0.086656 | 0.067657 | 0.071156 | 0.052157
2550.0781 | 109.1034 | 0.091553 | 102.7176 | 0.14017 | -0.026784 | -0.021157 | -0.002124 | 0.036265 | 0.071848 | -0.039826 | 0.011281 | 0.12501 | -0.017954 | 0.00811 | -0.070797 | -0.017983 | -0.04722 | -0.00775 | 0.17221 | 0.005259 | 0.010886 | 0.029919 | 0.068308 | 0.10389 | -0.007783 | 0.043324 | 0.15705 | 0.014089 | 0.040153 | -0.038754 | 0.01406 | -0.015177 | 0.024293 | 0.082078 | 0.058501 | 0.052843 | 0.029266
2551.7969 | 121.2708 | -0.15564 | 121.0693 | 0.14017 | -0.026784 | -0.016578 | 0.002454 | 0.040843 | 0.071848 | -0.044405 | 0.020438 | 0.11127 | -0.008798 | 0.012689 | -0.070797 | -0.017983 | -0.051798 | -0.00775 | 0.17221 | 0.005259 | 0.015465 | 0.034497 | 0.072886 | 0.10389 | -0.012362 | 0.052481 | 0.14331 | 0.023245 | 0.044732 | -0.038754 | 0.01406 | -0.019755 | 0.024293 | 0.091235 | 0.072236 | 0.061999 | 0.043
2553.5625 | 121.2662 | -0.1831 | 120.3964 | 0.14932 | -0.026784 | -0.021157 | -0.002124 | 0.036265 | 0.067269 | -0.03067 | 0.01586 | 0.12043 | -0.017954 | 0.003531 | -0.075375 | -0.022561 | -0.051798 | -0.00775 | 0.18136 | 0.005259 | 0.010886 | 0.029919 | 0.068308 | 0.099312 | 0.001373 | 0.047903 | 0.15247 | 0.014089 | 0.035574 | -0.043332 | 0.009482 | -0.019755 | 0.024293 | 0.091235 | 0.067658 | 0.057421 | 0.033844
2555.3281 | 121.3211 | -0.19226 | 106.7551 | 0.14474 | -0.026784 | -0.016578 | -0.006703 | 0.036265 | 0.071848 | -0.039826 | 0.01586 | 0.12043 | -0.013376 | 0.003531 | -0.070797 | -0.027139 | -0.051798 | 0.001406 | 0.17679 | 0.005259 | 0.015465 | 0.02534 | 0.068308 | 0.10389 | -0.007783 | 0.047903 | 0.15247 | 0.018667 | 0.035574 | -0.038754 | 0.004904 | -0.019755 | 0.033449 | 0.086657 | 0.067658 | 0.057421 | 0.038422
2557.0938 | 120.7809 | -61.2076 | 59.0286 | 0.14017 | -0.017627 | -0.012 | -0.006703 | 0.045421 | 0.067269 | -0.039826 | 0.020438 | 0.12501 | -0.008798 | 0.00811 | -0.079953 | -0.022561 | -0.042641 | -0.003172 | 0.17221 | 0.014416 | 0.020043 | 0.02534 | 0.077464 | 0.099312 | -0.007783 | 0.052481 | 0.15705 | 0.023245 | 0.040153 | -0.04791 | 0.009482 | -0.010598 | 0.028871 | 0.10039 | 0.063079 | 0.071155 | 0.033843
2558.7969 | 120.9503 | -116.3452 | 4.1107 | 0.14474 | -0.031363 | -0.012 | 0.002454 | 0.036265 | 0.071848 | -0.039826 | 0.020438 | 0.12501 | 0.000359 | 0.003531 | -0.075375 | -0.022561 | -0.051798 | -0.012328 | 0.17679 | 0.00068 | 0.020043 | 0.034497 | 0.068308 | 0.10389 | -0.007783 | 0.052481 | 0.15705 | 0.032402 | 0.035574 | -0.043332 | 0.009482 | -0.019755 | 0.019715 | 0.095813 | 0.072236 | 0.075734 | 0.052157
2560.5625 | 120.9412 | -61.0428 | 59.4955 | 0.14017 | -0.031363 | -0.021157 | -0.006703 | 0.045421 | 0.071848 | -0.039826 | 0.01586 | 0.11585 | -0.008798 | 0.017268 | -0.079953 | -0.017983 | -0.042641 | -0.00775 | 0.17221 | 0.00068 | 0.010886 | 0.02534 | 0.077464 | 0.10389 | -0.007783 | 0.047903 | 0.14789 | 0.023245 | 0.049311 | -0.04791 | 0.01406 | -0.010598 | 0.024293 | 0.095813 | 0.058501 | 0.071155 | 0.033843
2562.2969 | 120.9091 | -114.4318 | 6.0104 | 0.14017 | -0.026784 | -0.016578 | -0.002124 | 0.036265 | 0.071848 | -0.035248 | 0.006703 | 0.12501 | -0.008798 | 0.012689 | -0.079953 | -0.017983 | -0.051798 | -0.012328 | 0.17221 | 0.005259 | 0.015465 | 0.029919 | 0.068308 | 0.10389 | -0.003205 | 0.038746 | 0.15705 | 0.023245 | 0.044732 | -0.04791 | 0.01406 | -0.019755 | 0.019715 | 0.086656 | 0.058501 | 0.071155 | 0.043
2564.0625 | 121.106 | -116.2079 | 4.4449 | 0.14474 | -0.026784 | -0.021157 | -0.002124 | 0.040843 | 0.071848 | -0.035248 | 0.020438 | 0.12043 | -0.013376 | 0.00811 | -0.079953 | -0.027139 | -0.038063 | -0.012328 | 0.17679 | 0.005259 | 0.010886 | 0.029919 | 0.072886 | 0.10389 | -0.003205 | 0.052481 | 0.15247 | 0.018667 | 0.040153 | -0.04791 | 0.004904 | -0.00602 | 0.019715 | 0.10039 | 0.058501 | 0.066577 | 0.024687
2565.75 | 120.1721 | -0.10529 | 120.3918 | 0.14474 | -0.026784 | -0.016578 | -0.006703 | 0.036265 | 0.067269 | -0.044405 | 0.01586 | 0.12501 | -0.004219 | -0.001048 | -0.075375 | -0.022561 | -0.042641 | -0.00775 | 0.17679 | 0.005259 | 0.015465 | 0.02534 | 0.068308 | 0.099312 | -0.012362 | 0.047903 | 0.15705 | 0.027824 | 0.030995 | -0.043332 | 0.009482 | -0.010598 | 0.024293 | 0.091235 | 0.058501 | 0.071156 | 0.038422
2567.5156 | 120.9045 | -0.10071 | 119.9387 | 0.13559 | -0.035942 | -0.021157 | 0.002454 | 0.031687 | 0.071848 | -0.039826 | 0.006703 | 0.12501 | -0.017954 | -0.001048 | -0.070797 | -0.013405 | -0.051798 | -0.00775 | 0.16763 | -0.003899 | 0.010886 | 0.034497 | 0.06373 | 0.10389 | -0.007783 | 0.038746 | 0.15705 | 0.014089 | 0.030995 | -0.038754 | 0.018638 | -0.019755 | 0.024293 | 0.0775 | 0.058501 | 0.052843 | 0.033844
2569.2188 | 121.5637 | 0.022888 | 91.3605 | 0.13101 | -0.022205 | -0.012 | -0.002124 | 0.040843 | 0.067269 | -0.039826 | 0.01586 | 0.12501 | -0.013376 | 0.003531 | -0.070797 | -0.013405 | -0.04722 | -0.00775 | 0.16305 | 0.009838 | 0.020043 | 0.029919 | 0.072886 | 0.099312 | -0.007783 | 0.047903 | 0.15705 | 0.018667 | 0.035574 | -0.038754 | 0.018638 | -0.015177 | 0.024293 | 0.086657 | 0.06308 | 0.057421 | 0.033844
2570.9688 | 120.4147 | -0.059509 | 120.2271 | 0.14017 | -0.031363 | -0.016578 | 0.002454 | 0.036265 | 0.062691 | -0.039826 | 0.011281 | 0.11585 | -0.013376 | -0.001048 | -0.070797 | -0.022561 | -0.04722 | -0.00775 | 0.17221 | 0.00068 | 0.015465 | 0.034497 | 0.068308 | 0.094734 | -0.007783 | 0.043324 | 0.14789 | 0.018667 | 0.030995 | -0.038754 | 0.009482 | -0.015177 | 0.024293 | 0.082078 | 0.058501 | 0.057421 | 0.033844
2572.7188 | 120.5612 | -0.07782 | 120.639 | 0.13559 | -0.031363 | -0.025735 | -0.002124 | 0.036265 | 0.062691 | -0.044405 | 0.020438 | 0.12501 | -0.013376 | 0.003531 | -0.070797 | -0.022561 | -0.04722 | -0.00775 | 0.16763 | 0.00068 | 0.006308 | 0.029919 | 0.068308 | 0.094734 | -0.012362 | 0.052481 | 0.15705 | 0.018667 | 0.035574 | -0.038754 | 0.009482 | -0.015177 | 0.024293 | 0.091235 | 0.067658 | 0.057421 | 0.033844
2574.4688 | 120.5383 | -0.032043 | 120.4926 | 0.14017 | -0.035942 | -0.021157 | -0.006703 | 0.036265 | 0.062691 | -0.044405 | 0.020438 | 0.12043 | -0.008798 | 0.003531 | -0.075375 | -0.022561 | -0.051798 | -0.00775 | 0.17221 | -0.003899 | 0.010886 | 0.02534 | 0.068308 | 0.094734 | -0.012362 | 0.052481 | 0.15247 | 0.023245 | 0.035574 | -0.043332 | 0.009482 | -0.019755 | 0.024293 | 0.095813 | 0.072236 | 0.066577 | 0.043
2576.2188 | 104.0359 | 0.09613 | 121.1472 | 0.13559 | -0.035942 | -0.021157 | 0.002454 | 0.040843 | 0.071848 | -0.039826 | 0.011281 | 0.12043 | -0.017954 | 0.003531 | -0.070797 | -0.022561 | -0.051798 | -0.00775 | 0.16763 | -0.003899 | 0.010886 | 0.034497 | 0.072886 | 0.10389 | -0.007783 | 0.043324 | 0.15247 | 0.014089 | 0.035574 | -0.038754 | 0.009482 | -0.019755 | 0.024293 | 0.082078 | 0.063079 | 0.052843 | 0.033844
2577.9844 | 120.4742 | -0.073242 | 120.2957 | 0.14017 | -0.026784 | -0.012 | -0.006703 | 0.040843 | 0.071848 | -0.03067 | 0.01586 | 0.12043 | -0.004219 | 0.003531 | -0.075375 | -0.022561 | -0.051798 | -0.003172 | 0.17221 | 0.005259 | 0.020043 | 0.02534 | 0.072886 | 0.10389 | 0.001373 | 0.047903 | 0.15247 | 0.027824 | 0.035574 | -0.043332 | 0.009482 | -0.019755 | 0.028871 | 0.091235 | 0.067658 | 0.071156 | 0.047579
2579.7344 | 112.7747 | 0.17853 | 105.4596 | 0.13559 | -0.026784 | -0.021157 | -0.006703 | 0.040843 | 0.067269 | -0.035248 | 0.011281 | 0.11585 | -0.017954 | 0.003531 | -0.079953 | -0.027139 | -0.042641 | -0.00775 | 0.16763 | 0.005259 | 0.010886 | 0.02534 | 0.072886 | 0.099312 | -0.003205 | 0.043324 | 0.14789 | 0.014089 | 0.035574 | -0.04791 | 0.004904 | -0.010598 | 0.024293 | 0.091234 | 0.053922 | 0.061999 | 0.024687
2581.4219 | 120.8771 | 0.050354 | 120.3232 | 0.13559 | -0.040521 | -0.025735 | -0.002124 | 0.036265 | 0.076426 | -0.035248 | 0.020438 | 0.11585 | -0.017954 | -0.001048 | -0.070797 | -0.017983 | -0.051798 | -0.00775 | 0.16763 | -0.008478 | 0.006308 | 0.029919 | 0.068308 | 0.10847 | -0.003205 | 0.052481 | 0.14789 | 0.014089 | 0.030995 | -0.038754 | 0.01406 | -0.019755 | 0.024293 | 0.091235 | 0.072236 | 0.052843 | 0.033844
2583.1875 | 121.3669 | 0.036621 | 106.7139 | 0.14017 | -0.035942 | -0.016578 | -0.006703 | 0.040843 | 0.076426 | -0.035248 | 0.01586 | 0.11127 | -0.017954 | 0.003531 | -0.075375 | -0.027139 | -0.042641 | -0.003172 | 0.17221 | -0.003899 | 0.015465 | 0.02534 | 0.072886 | 0.10847 | -0.003205 | 0.047903 | 0.14331 | 0.014089 | 0.035574 | -0.043332 | 0.004904 | -0.010598 | 0.028871 | 0.091235 | 0.058501 | 0.057421 | 0.024687
2584.875 | 121.2799 | -0.086975 | 113.1866 | 0.14017 | -0.035942 | -0.016578 | -0.002124 | 0.040843 | 0.071848 | -0.039826 | 0.020438 | 0.12043 | -0.013376 | 0.003531 | -0.079953 | -0.017983 | -0.042641 | -0.012328 | 0.17221 | -0.003899 | 0.015465 | 0.029919 | 0.072886 | 0.10389 | -0.007783 | 0.052481 | 0.15247 | 0.018667 | 0.035574 | -0.04791 | 0.01406 | -0.010598 | 0.019715 | 0.10039 | 0.063079 | 0.066577 | 0.029265
2586.625 | 121.051 | -0.018311 | 121.3623 | 0.14017 | -0.031363 | -0.016578 | -0.002124 | 0.036265 | 0.062691 | -0.039826 | 0.020438 | 0.12043 | -0.013376 | -0.001048 | -0.070797 | -0.022561 | -0.04722 | -0.003172 | 0.17221 | 0.00068 | 0.015465 | 0.029919 | 0.068308 | 0.094734 | -0.007783 | 0.052481 | 0.15247 | 0.018667 | 0.030995 | -0.038754 | 0.009482 | -0.015177 | 0.028871 | 0.091235 | 0.067658 | 0.057421 | 0.033844
2588.3906 | 121.4172 | -0.07782 | 121.2479 | 0.13559 | -0.035942 | -0.025735 | 0.002454 | 0.036265 | 0.076426 | -0.044405 | 0.025017 | 0.12501 | -0.022532 | 0.00811 | -0.079953 | -0.022561 | -0.04722 | 0.001406 | 0.16763 | -0.003899 | 0.006308 | 0.034497 | 0.068308 | 0.10847 | -0.012362 | 0.05706 | 0.15705 | 0.009511 | 0.040153 | -0.04791 | 0.009482 | -0.015177 | 0.033449 | 0.10497 | 0.072237 | 0.057421 | 0.024688
2590.1562 | 121.3303 | -0.12817 | 120.7443 | 0.13559 | -0.026784 | -0.012 | -0.002124 | 0.040843 | 0.067269 | -0.03067 | 0.025017 | 0.12501 | -0.017954 | 0.012689 | -0.079953 | -0.017983 | -0.04722 | -0.00775 | 0.16763 | 0.005259 | 0.020043 | 0.029919 | 0.072886 | 0.099312 | 0.001373 | 0.05706 | 0.15705 | 0.014089 | 0.044732 | -0.04791 | 0.01406 | -0.015177 | 0.024293 | 0.10497 | 0.072237 | 0.061999 | 0.029266
2591.9062 | 121.4859 | -0.19226 | 120.4971 | 0.14474 | -0.031363 | -0.016578 | -0.002124 | 0.036265 | 0.058113 | -0.035248 | 0.020438 | 0.11585 | 0.000359 | 0.00811 | -0.075375 | -0.027139 | -0.051798 | -0.003172 | 0.17679 | 0.00068 | 0.015465 | 0.029919 | 0.068308 | 0.090156 | -0.003205 | 0.052481 | 0.14789 | 0.032402 | 0.040153 | -0.043332 | 0.004904 | -0.019755 | 0.028871 | 0.095813 | 0.072236 | 0.075734 | 0.052157
2593.6094 | 120.6894 | -0.10071 | 116.7114 | 0.14017 | -0.035942 | -0.016578 | 0.011611 | 0.036265 | 0.071848 | -0.039826 | 0.011281 | 0.12043 | 0.004937 | 0.003531 | -0.079953 | -0.013405 | -0.04722 | -0.00775 | 0.17221 | -0.003899 | 0.015465 | 0.043654 | 0.068308 | 0.10389 | -0.007783 | 0.043324 | 0.15247 | 0.03698 | 0.035574 | -0.04791 | 0.018638 | -0.015177 | 0.024293 | 0.091234 | 0.058501 | 0.08489 | 0.052157
2595.3594 | 120.8725 | -0.13275 | 120.2911 | 0.13559 | -0.026784 | -0.025735 | 0.002454 | 0.045421 | 0.076426 | -0.03067 | 0.011281 | 0.11585 | -0.013376 | 0.003531 | -0.070797 | -0.017983 | -0.051798 | -0.00775 | 0.16763 | 0.005259 | 0.006308 | 0.034497 | 0.077464 | 0.10847 | 0.001373 | 0.043324 | 0.14789 | 0.018667 | 0.035574 | -0.038754 | 0.01406 | -0.019755 | 0.024293 | 0.082078 | 0.063079 | 0.057421 | 0.038422
2597.0469 | 120.8908 | -0.11444 | 120.2133 | 0.13559 | -0.031363 | -0.012 | 0.007033 | 0.040843 | 0.067269 | -0.03067 | 0.020438 | 0.12043 | -0.013376 | 0.003531 | -0.070797 | -0.022561 | -0.04722 | -0.003172 | 0.16763 | 0.00068 | 0.020043 | 0.039076 | 0.072886 | 0.099312 | 0.001373 | 0.052481 | 0.15247 | 0.018667 | 0.035574 | -0.038754 | 0.009482 | -0.015177 | 0.028871 | 0.091235 | 0.067658 | 0.057421 | 0.033844
2598.7969 | 120.7535 | -0.14191 | 120.1904 | 0.13559 | -0.035942 | -0.021157 | -0.011281 | 0.040843 | 0.062691 | -0.039826 | 0.01586 | 0.12043 | -0.017954 | 0.00811 | -0.075375 | -0.013405 | -0.042641 | -0.00775 | 0.16763 | -0.003899 | 0.010886 | 0.020762 | 0.072886 | 0.094734 | -0.007783 | 0.047903 | 0.15247 | 0.014089 | 0.040153 | -0.043332 | 0.018638 | -0.010598 | 0.024293 | 0.091235 | 0.058501 | 0.057421 | 0.024687
2600.5469 | 120.3415 | -0.11444 | 120.1767 | 0.13559 | -0.031363 | -0.021157 | -0.006703 | 0.036265 | 0.067269 | -0.035248 | 0.025017 | 0.11585 | -0.008798 | 0.00811 | -0.079953 | -0.022561 | -0.04722 | -0.00775 | 0.16763 | 0.00068 | 0.010886 | 0.02534 | 0.068308 | 0.099312 | -0.003205 | 0.05706 | 0.14789 | 0.023245 | 0.040153 | -0.04791 | 0.009482 | -0.015177 | 0.024293 | 0.10497 | 0.072237 | 0.071155 | 0.038422
2602.2969 | 121.1792 | -0.13275 | 120.6253 | 0.14474 | -0.026784 | -0.016578 | 0.002454 | 0.040843 | 0.071848 | -0.035248 | 0.01586 | 0.12958 | -0.004219 | 0.012689 | -0.075375 | -0.017983 | -0.051798 | -0.012328 | 0.17679 | 0.005259 | 0.015465 | 0.034497 | 0.072886 | 0.10389 | -0.003205 | 0.047903 | 0.16163 | 0.027824 | 0.044732 | -0.043332 | 0.01406 | -0.019755 | 0.019715 | 0.091235 | 0.067658 | 0.071156 | 0.047579
2604 | 121.0831 | -0.082397 | 121.0144 | 0.13101 | -0.031363 | -0.025735 | -0.006703 | 0.031687 | 0.067269 | -0.044405 | 0.01586 | 0.12043 | -0.022532 | 0.003531 | -0.066219 | -0.022561 | -0.056376 | -0.00775 | 0.16305 | 0.00068 | 0.006308 | 0.02534 | 0.06373 | 0.099312 | -0.012362 | 0.047903 | 0.15247 | 0.009511 | 0.035574 | -0.034176 | 0.009482 | -0.024333 | 0.024293 | 0.082079 | 0.072236 | 0.043687 | 0.033844
2605.75 | 120.8908 | -0.073242 | 120.6482 | 0.13559 | -0.031363 | -0.016578 | -0.006703 | 0.036265 | 0.067269 | -0.044405 | 0.01586 | 0.12501 | -0.017954 | 0.003531 | -0.066219 | -0.013405 | -0.04722 | -0.00775 | 0.16763 | 0.00068 | 0.015465 | 0.02534 | 0.068308 | 0.099312 | -0.012362 | 0.047903 | 0.15705 | 0.014089 | 0.035574 | -0.034176 | 0.018638 | -0.015177 | 0.024293 | 0.082079 | 0.06308 | 0.048265 | 0.029266
2607.5156 | 120.9641 | -0.10529 | 120.6116 | 0.14017 | -0.031363 | -0.025735 | -0.006703 | 0.040843 | 0.067269 | -0.039826 | 0.01586 | 0.12043 | -0.017954 | 0.003531 | -0.070797 | -0.017983 | -0.04722 | -0.003172 | 0.17221 | 0.00068 | 0.006308 | 0.02534 | 0.072886 | 0.099312 | -0.007783 | 0.047903 | 0.15247 | 0.014089 | 0.035574 | -0.038754 | 0.01406 | -0.015177 | 0.028871 | 0.086657 | 0.06308 | 0.052843 | 0.029266
2609.2188 | 120.8679 | -0.091553 | 120.3369 | 0.14474 | -0.035942 | -0.016578 | -0.006703 | 0.040843 | 0.067269 | -0.044405 | 0.020438 | 0.12043 | -0.017954 | 0.003531 | -0.079953 | -0.008827 | -0.042641 | -0.003172 | 0.17679 | -0.003899 | 0.015465 | 0.02534 | 0.072886 | 0.099312 | -0.012362 | 0.052481 | 0.15247 | 0.014089 | 0.035574 | -0.04791 | 0.023216 | -0.010598 | 0.028871 | 0.10039 | 0.063079 | 0.061999 | 0.024687
2610.9688 | 121.3852 | -0.07782 | 121.2799 | 0.13101 | -0.031363 | -0.021157 | 0.002454 | 0.040843 | 0.067269 | -0.039826 | 0.01586 | 0.12043 | -0.013376 | 0.003531 | -0.075375 | -0.022561 | -0.042641 | -0.012328 | 0.16305 | 0.00068 | 0.010886 | 0.034497 | 0.072886 | 0.099312 | -0.007783 | 0.047903 | 0.15247 | 0.018667 | 0.035574 | -0.043332 | 0.009482 | -0.010598 | 0.019715 | 0.091235 | 0.058501 | 0.061999 | 0.029265
2612.6562 | 121.0098 | -0.10071 | 120.4285 | 0.14017 | -0.035942 | -0.016578 | -0.002124 | 0.045421 | 0.058113 | -0.039826 | 0.011281 | 0.11585 | -0.004219 | 0.00811 | -0.075375 | -0.013405 | -0.038063 | 0.005985 | 0.17221 | -0.003899 | 0.015465 | 0.029919 | 0.077464 | 0.090156 | -0.007783 | 0.043324 | 0.14789 | 0.027824 | 0.040153 | -0.043332 | 0.018638 | -0.00602 | 0.038028 | 0.086656 | 0.049344 | 0.071156 | 0.033844
2614.4062 | 121.0144 | -0.1236 | 120.7443 | 0.13101 | -0.035942 | -0.016578 | 0.002454 | 0.036265 | 0.067269 | -0.039826 | 0.01586 | 0.12958 | -0.008798 | 0.003531 | -0.070797 | -0.017983 | -0.04722 | -0.003172 | 0.16305 | -0.003899 | 0.015465 | 0.034497 | 0.068308 | 0.099312 | -0.007783 | 0.047903 | 0.16163 | 0.023245 | 0.035574 | -0.038754 | 0.01406 | -0.015177 | 0.028871 | 0.086657 | 0.06308 | 0.061999 | 0.038422
2616.1562 | 120.7809 | -0.073242 | 120.7672 | 0.14017 | -0.035942 | -0.025735 | -0.006703 | 0.036265 | 0.067269 | -0.039826 | 0.020438 | 0.12958 | -0.008798 | 0.00811 | -0.075375 | -0.017983 | -0.051798 | -0.00775 | 0.17221 | -0.003899 | 0.006308 | 0.02534 | 0.068308 | 0.099312 | -0.007783 | 0.052481 | 0.16163 | 0.023245 | 0.040153 | -0.043332 | 0.01406 | -0.019755 | 0.024293 | 0.095813 | 0.072236 | 0.066577 | 0.043
2617.8438 | 121.106 | -0.091553 | 121.1975 | 0.12643 | -0.031363 | -0.021157 | -0.002124 | 0.036265 | 0.067269 | -0.039826 | 0.020438 | 0.12501 | -0.013376 | 0.003531 | -0.075375 | -0.022561 | -0.04722 | -0.012328 | 0.15847 | 0.00068 | 0.010886 | 0.029919 | 0.068308 | 0.099312 | -0.007783 | 0.052481 | 0.15705 | 0.018667 | 0.035574 | -0.043332 | 0.009482 | -0.015177 | 0.019715 | 0.095813 | 0.067658 | 0.061999 | 0.033844
2619.5938 | 121.0419 | -0.10071 | 120.9412 | 0.13101 | -0.031363 | -0.021157 | -0.002124 | 0.049999 | 0.071848 | -0.039826 | 0.020438 | 0.12043 | -0.008798 | 0.00811 | -0.084531 | -0.031717 | -0.065533 | -0.026063 | 0.16305 | 0.00068 | 0.010886 | 0.029919 | 0.082042 | 0.10389 | -0.007783 | 0.052481 | 0.15247 | 0.023245 | 0.040153 | -0.052488 | 0.000326 | -0.03349 | 0.00598 | 0.10497 | 0.085971 | 0.075733 | 0.056735
2621.2812 | 121.2387 | -0.11902 | 112.7792 | 0.14017 | -0.026784 | -0.016578 | 0.002454 | 0.045421 | 0.067269 | -0.035248 | 0.01586 | 0.12501 | -0.008798 | 0.003531 | -0.075375 | -0.017983 | -0.04722 | -0.00775 | 0.17221 | 0.005259 | 0.015465 | 0.034497 | 0.077464 | 0.099312 | -0.003205 | 0.047903 | 0.15705 | 0.023245 | 0.035574 | -0.043332 | 0.01406 | -0.015177 | 0.024293 | 0.091235 | 0.06308 | 0.066577 | 0.038422
2623.0312 | 121.2387 | -57.6324 | 63.0753 | 0.13559 | -0.026784 | -0.016578 | -0.002124 | 0.036265 | 0.062691 | -0.035248 | 0.020438 | 0.12501 | -0.008798 | 0.00811 | -0.075375 | -0.017983 | -0.051798 | -0.016906 | 0.16763 | 0.005259 | 0.015465 | 0.029919 | 0.068308 | 0.094734 | -0.003205 | 0.052481 | 0.15705 | 0.023245 | 0.040153 | -0.043332 | 0.01406 | -0.019755 | 0.015137 | 0.095813 | 0.072236 | 0.066577 | 0.043
2624.7969 | 120.4422 | -11.6135 | 109.1354 | 0.12643 | -0.026784 | -0.016578 | -0.002124 | 0.036265 | 0.067269 | -0.035248 | 0.01586 | 0.12958 | -0.017954 | 0.00811 | -0.075375 | -0.017983 | -0.04722 | -0.00775 | 0.15847 | 0.005259 | 0.015465 | 0.029919 | 0.068308 | 0.099312 | -0.003205 | 0.047903 | 0.16163 | 0.014089 | 0.040153 | -0.043332 | 0.01406 | -0.015177 | 0.024293 | 0.091235 | 0.06308 | 0.057421 | 0.029266
2626.5625 | 120.4926 | -12.6022 | 108.3481 | 0.13559 | -0.035942 | -0.016578 | -0.002124 | 0.036265 | 0.067269 | -0.035248 | 0.01586 | 0.12043 | -0.004219 | 0.00811 | -0.070797 | -0.013405 | -0.04722 | -0.003172 | 0.16763 | -0.003899 | 0.015465 | 0.029919 | 0.068308 | 0.099312 | -0.003205 | 0.047903 | 0.15247 | 0.027824 | 0.040153 | -0.038754 | 0.018638 | -0.015177 | 0.028871 | 0.086657 | 0.06308 | 0.066578 | 0.043001
2628.2656 | 121.0876 | -15.8386 | 105.3406 | 0.13101 | -0.035942 | -0.021157 | -0.002124 | 0.040843 | 0.081005 | -0.035248 | 0.01586 | 0.12958 | -0.017954 | 0.00811 | -0.070797 | -0.022561 | -0.060955 | -0.003172 | 0.16305 | -0.003899 | 0.010886 | 0.029919 | 0.072886 | 0.11305 | -0.003205 | 0.047903 | 0.16163 | 0.014089 | 0.040153 | -0.038754 | 0.009482 | -0.028912 | 0.028871 | 0.086657 | 0.076815 | 0.052843 | 0.043001
2630.0312 | 121.1426 | -16.8594 | 104.3884 | 0.14017 | -0.026784 | -0.021157 | 0.002454 | 0.040843 | 0.076426 | -0.039826 | 0.020438 | 0.12958 | -0.017954 | 0.003531 | -0.070797 | -0.027139 | -0.04722 | -0.00775 | 0.17221 | 0.005259 | 0.010886 | 0.034497 | 0.072886 | 0.10847 | -0.007783 | 0.052481 | 0.16163 | 0.014089 | 0.035574 | -0.038754 | 0.004904 | -0.015177 | 0.024293 | 0.091235 | 0.067658 | 0.052843 | 0.029266
2631.7812 | 121.3943 | -18.3151 | 102.9282 | 0.13559 | -0.031363 | -0.025735 | 0.002454 | 0.040843 | 0.067269 | -0.03067 | 0.011281 | 0.12043 | -0.008798 | 0.012689 | -0.070797 | -0.022561 | -0.056376 | -0.012328 | 0.16763 | 0.00068 | 0.006308 | 0.034497 | 0.072886 | 0.099312 | 0.001373 | 0.043324 | 0.15247 | 0.023245 | 0.044732 | -0.038754 | 0.009482 | -0.024333 | 0.019715 | 0.082078 | 0.067657 | 0.061999 | 0.047578
2633.5312 | 121.5271 | -58.1268 | 62.8738 | 0.13101 | -0.031363 | -0.016578 | -0.002124 | 0.045421 | 0.067269 | -0.035248 | 0.025017 | 0.12958 | -0.022532 | 0.00811 | -0.075375 | -0.013405 | -0.04722 | -0.00775 | 0.16305 | 0.00068 | 0.015465 | 0.029919 | 0.077464 | 0.099312 | -0.003205 | 0.05706 | 0.16163 | 0.009511 | 0.040153 | -0.043332 | 0.018638 | -0.015177 | 0.024293 | 0.10039 | 0.072237 | 0.052843 | 0.024688
2635.25 | 121.5317 | -58.3054 | 62.7502 | 0.13559 | -0.035942 | -0.021157 | 0.002454 | 0.040843 | 0.067269 | -0.044405 | 0.020438 | 0.12043 | -0.004219 | 0.003531 | -0.079953 | -0.022561 | -0.04722 | -0.003172 | 0.16763 | -0.003899 | 0.010886 | 0.034497 | 0.072886 | 0.099312 | -0.012362 | 0.052481 | 0.15247 | 0.027824 | 0.035574 | -0.04791 | 0.009482 | -0.015177 | 0.028871 | 0.10039 | 0.067658 | 0.075734 | 0.043001
2637 | 121.4081 | -58.5938 | 62.6404 | 0.13559 | -0.031363 | -0.012 | -0.006703 | 0.040843 | 0.071848 | -0.035248 | 0.025017 | 0.12501 | -0.008798 | 0.00811 | -0.079953 | -0.027139 | -0.042641 | -0.00775 | 0.16763 | 0.00068 | 0.020043 | 0.02534 | 0.072886 | 0.10389 | -0.003205 | 0.05706 | 0.15705 | 0.023245 | 0.040153 | -0.04791 | 0.004904 | -0.010598 | 0.024293 | 0.10497 | 0.067658 | 0.071155 | 0.033843
2638.6875 | 121.5088 | -58.1863 | 63.0386 | 0.13559 | -0.026784 | -0.016578 | -0.002124 | 0.045421 | 0.062691 | -0.03067 | 0.01586 | 0.12501 | -0.013376 | 0.003531 | -0.066219 | -0.022561 | -0.051798 | 0.001406 | 0.16763 | 0.005259 | 0.015465 | 0.029919 | 0.077464 | 0.094734 | 0.001373 | 0.047903 | 0.15705 | 0.018667 | 0.035574 | -0.034176 | 0.009482 | -0.019755 | 0.033449 | 0.082079 | 0.067658 | 0.052843 | 0.038422
2640.4531 | 121.4401 | -56.0394 | 65.2496 | 0.14474 | -0.031363 | -0.021157 | -0.002124 | 0.045421 | 0.067269 | -0.039826 | 0.025017 | 0.12501 | -0.004219 | 0.003531 | -0.079953 | -0.022561 | -0.042641 | -0.012328 | 0.17679 | 0.00068 | 0.010886 | 0.029919 | 0.077464 | 0.099312 | -0.007783 | 0.05706 | 0.15705 | 0.027824 | 0.035574 | -0.04791 | 0.009482 | -0.010598 | 0.019715 | 0.10497 | 0.067658 | 0.075734 | 0.038422
2642.2031 | 120.7031 | -33.0505 | 88.2385 | 0.13559 | -0.035942 | -0.016578 | -0.006703 | 0.045421 | 0.067269 | -0.039826 | 0.020438 | 0.12043 | -0.008798 | 0.003531 | -0.075375 | -0.013405 | -0.04722 | -0.012328 | 0.16763 | -0.003899 | 0.015465 | 0.02534 | 0.077464 | 0.099312 | -0.007783 | 0.052481 | 0.15247 | 0.023245 | 0.035574 | -0.043332 | 0.018638 | -0.015177 | 0.019715 | 0.095813 | 0.067658 | 0.066577 | 0.038422
2643.8906 | 121.3623 | -23.8174 | 97.5403 | 0.12643 | -0.031363 | -0.016578 | 0.002454 | 0.036265 | 0.071848 | -0.039826 | 0.01586 | 0.12501 | -0.004219 | 0.00811 | -0.079953 | -0.022561 | -0.051798 | -0.012328 | 0.15847 | 0.00068 | 0.015465 | 0.034497 | 0.068308 | 0.10389 | -0.007783 | 0.047903 | 0.15705 | 0.027824 | 0.040153 | -0.04791 | 0.009482 | -0.019755 | 0.019715 | 0.095813 | 0.067658 | 0.075734 | 0.047579
2645.6406 | 121.2341 | -15.1062 | 106.3477 | 0.14017 | -0.035942 | -0.012 | -0.002124 | 0.045421 | 0.062691 | -0.035248 | 0.025017 | 0.12958 | 0.000359 | 0.00811 | -0.075375 | -0.013405 | -0.051798 | 0.001406 | 0.17221 | -0.003899 | 0.020043 | 0.029919 | 0.077464 | 0.094734 | -0.003205 | 0.05706 | 0.16163 | 0.032402 | 0.040153 | -0.043332 | 0.018638 | -0.019755 | 0.033449 | 0.10039 | 0.076815 | 0.075734 | 0.052157
2647.3906 | 121.1243 | -13.5361 | 107.84 | 0.13101 | -0.035942 | -0.016578 | -0.002124 | 0.036265 | 0.067269 | -0.044405 | 0.01586 | 0.12958 | -0.013376 | 0.00811 | -0.066219 | -0.017983 | -0.056376 | -0.003172 | 0.16305 | -0.003899 | 0.015465 | 0.029919 | 0.068308 | 0.099312 | -0.012362 | 0.047903 | 0.16163 | 0.018667 | 0.040153 | -0.034176 | 0.01406 | -0.024333 | 0.028871 | 0.082079 | 0.072236 | 0.052843 | 0.043
2649.1406 | 121.3028 | -14.3509 | 107.016 | 0.14017 | -0.031363 | -0.012 | -0.002124 | 0.040843 | 0.062691 | -0.039826 | 0.01586 | 0.12043 | -0.013376 | 0.00811 | -0.070797 | -0.017983 | -0.051798 | 0.001406 | 0.17221 | 0.00068 | 0.020043 | 0.029919 | 0.072886 | 0.094734 | -0.007783 | 0.047903 | 0.15247 | 0.018667 | 0.040153 | -0.038754 | 0.01406 | -0.019755 | 0.033449 | 0.086657 | 0.067658 | 0.057421 | 0.038422
2650.8906 | 120.1721 | -23.259 | 97.5128 | 0.13101 | -0.035942 | -0.021157 | 0.002454 | 0.036265 | 0.067269 | -0.044405 | 0.025017 | 0.12501 | -0.013376 | 0.00811 | -0.075375 | -0.017983 | -0.04722 | -0.012328 | 0.16305 | -0.003899 | 0.010886 | 0.034497 | 0.068308 | 0.099312 | -0.012362 | 0.05706 | 0.15705 | 0.018667 | 0.040153 | -0.043332 | 0.01406 | -0.015177 | 0.019715 | 0.10039 | 0.072237 | 0.061999 | 0.033844
2652.5781 | 121.2662 | -15.1794 | 105.9814 | 0.13101 | -0.026784 | -0.016578 | 0.002454 | 0.045421 | 0.067269 | -0.039826 | 0.020438 | 0.12043 | -0.008798 | 0.00811 | -0.075375 | -0.013405 | -0.04722 | -0.012328 | 0.16305 | 0.005259 | 0.015465 | 0.034497 | 0.077464 | 0.099312 | -0.007783 | 0.052481 | 0.15247 | 0.023245 | 0.040153 | -0.043332 | 0.018638 | -0.015177 | 0.019715 | 0.095813 | 0.067658 | 0.066577 | 0.038422
2654.2812 | 120.5154 | -15.271 | 105.542 | 0.13559 | -0.031363 | -0.016578 | -0.006703 | 0.049999 | 0.067269 | -0.039826 | 0.020438 | 0.12501 | -0.008798 | 0.012689 | -0.070797 | -0.017983 | -0.04722 | -0.003172 | 0.16763 | 0.00068 | 0.015465 | 0.02534 | 0.082042 | 0.099312 | -0.007783 | 0.052481 | 0.15705 | 0.023245 | 0.044732 | -0.038754 | 0.01406 | -0.015177 | 0.028871 | 0.091235 | 0.067658 | 0.061999 | 0.038422
2656.0312 | 121.5179 | -59.3216 | 61.702 | 0.13559 | -0.026784 | -0.021157 | -0.002124 | 0.040843 | 0.076426 | -0.039826 | 0.01586 | 0.12043 | -0.004219 | 0.012689 | -0.079953 | -0.017983 | -0.051798 | -0.012328 | 0.16763 | 0.005259 | 0.010886 | 0.029919 | 0.072886 | 0.10847 | -0.007783 | 0.047903 | 0.15247 | 0.027824 | 0.044732 | -0.04791 | 0.01406 | -0.019755 | 0.019715 | 0.095813 | 0.067658 | 0.075734 | 0.047579
2657.7812 | 120.7672 | -18.6768 | 102.5757 | 0.13559 | -0.031363 | -0.021157 | -0.002124 | 0.040843 | 0.076426 | -0.035248 | 0.01586 | 0.12501 | -0.013376 | 0.012689 | -0.075375 | -0.022561 | -0.04722 | -0.003172 | 0.16763 | 0.00068 | 0.010886 | 0.029919 | 0.072886 | 0.10847 | -0.003205 | 0.047903 | 0.15705 | 0.018667 | 0.044732 | -0.043332 | 0.009482 | -0.015177 | 0.028871 | 0.091235 | 0.06308 | 0.061999 | 0.033844
2659.5469 | 121.5363 | -58.905 | 62.1735 | 0.13559 | -0.031363 | -0.025735 | -0.002124 | 0.040843 | 0.071848 | -0.039826 | 0.01586 | 0.12501 | -0.008798 | 0.00811 | -0.070797 | -0.017983 | -0.04722 | -0.00775 | 0.16763 | 0.00068 | 0.006308 | 0.029919 | 0.072886 | 0.10389 | -0.007783 | 0.047903 | 0.15705 | 0.023245 | 0.040153 | -0.038754 | 0.01406 | -0.015177 | 0.024293 | 0.086657 | 0.06308 | 0.061999 | 0.038422
2661.3125 | 121.5042 | -57.7286 | 63.414 | 0.14017 | -0.031363 | -0.021157 | 0.002454 | 0.040843 | 0.062691 | -0.039826 | 0.020438 | 0.12043 | -0.013376 | 0.00811 | -0.075375 | -0.017983 | -0.051798 | -0.003172 | 0.17221 | 0.00068 | 0.010886 | 0.034497 | 0.072886 | 0.094734 | -0.007783 | 0.052481 | 0.15247 | 0.018667 | 0.040153 | -0.043332 | 0.01406 | -0.019755 | 0.028871 | 0.095813 | 0.072236 | 0.061999 | 0.038422
2663.0781 | 121.5775 | -57.1289 | 64.0594 | 0.13559 | -0.035942 | -0.016578 | -0.011281 | 0.045421 | 0.067269 | -0.035248 | 0.020438 | 0.12501 | -0.004219 | 0.012689 | -0.075375 | -0.022561 | -0.051798 | -0.00775 | 0.16763 | -0.003899 | 0.015465 | 0.020762 | 0.077464 | 0.099312 | -0.003205 | 0.052481 | 0.15705 | 0.027824 | 0.044732 | -0.043332 | 0.009482 | -0.019755 | 0.024293 | 0.095813 | 0.072236 | 0.071156 | 0.047579
2664.7812 | 121.7194 | -43.4601 | 73.5443 | 0.14474 | -0.031363 | -0.021157 | 0.002454 | 0.036265 | 0.067269 | -0.035248 | 0.025017 | 0.12958 | -0.008798 | 0.00811 | -0.084531 | -0.027139 | -0.056376 | -0.012328 | 0.17679 | 0.00068 | 0.010886 | 0.034497 | 0.068308 | 0.099312 | -0.003205 | 0.05706 | 0.16163 | 0.023245 | 0.040153 | -0.052488 | 0.004904 | -0.024333 | 0.019715 | 0.10955 | 0.081393 | 0.075733 | 0.047578
2666.5312 | 121.637 | -59.6741 | 61.5555 | 0.13101 | -0.017627 | -0.016578 | -0.002124 | 0.040843 | 0.062691 | -0.039826 | 0.01586 | 0.12501 | -0.013376 | 0.00811 | -0.075375 | -0.017983 | -0.056376 | -0.016906 | 0.16305 | 0.014416 | 0.015465 | 0.029919 | 0.072886 | 0.094734 | -0.007783 | 0.047903 | 0.15705 | 0.018667 | 0.040153 | -0.043332 | 0.01406 | -0.024333 | 0.015137 | 0.091235 | 0.072236 | 0.061999 | 0.043
2668.2188 | 121.6324 | -58.5022 | 62.796 | 0.13559 | -0.031363 | -0.016578 | -0.006703 | 0.049999 | 0.071848 | -0.039826 | 0.020438 | 0.12043 | -0.013376 | 0.003531 | -0.079953 | -0.017983 | -0.051798 | -0.00775 | 0.16763 | 0.00068 | 0.015465 | 0.02534 | 0.082042 | 0.10389 | -0.007783 | 0.052481 | 0.15247 | 0.018667 | 0.035574 | -0.04791 | 0.01406 | -0.019755 | 0.024293 | 0.10039 | 0.072236 | 0.066577 | 0.038422
2669.9844 | 121.7422 | -53.1189 | 67.1265 | 0.13101 | -0.031363 | -0.016578 | -0.002124 | 0.036265 | 0.062691 | -0.044405 | 0.01586 | 0.12958 | -0.004219 | 0.00811 | -0.075375 | -0.017983 | -0.051798 | -0.003172 | 0.16305 | 0.00068 | 0.015465 | 0.029919 | 0.068308 | 0.094734 | -0.012362 | 0.047903 | 0.16163 | 0.027824 | 0.040153 | -0.043332 | 0.01406 | -0.019755 | 0.028871 | 0.091235 | 0.067658 | 0.071156 | 0.047579
2671.75 | 121.3989 | -13.9801 | 107.5058 | 0.13101 | -0.031363 | -0.016578 | 0.002454 | 0.036265 | 0.067269 | -0.035248 | 0.025017 | 0.12501 | -0.017954 | -0.001048 | -0.075375 | -0.022561 | -0.042641 | -0.00775 | 0.16305 | 0.00068 | 0.015465 | 0.034497 | 0.068308 | 0.099312 | -0.003205 | 0.05706 | 0.15705 | 0.014089 | 0.030995 | -0.043332 | 0.009482 | -0.010598 | 0.024293 | 0.10039 | 0.067658 | 0.057421 | 0.024687
2673.5 | 121.7468 | -57.724 | 63.5605 | 0.14017 | -0.031363 | -0.012 | -0.006703 | 0.040843 | 0.067269 | -0.035248 | 0.025017 | 0.12043 | -0.004219 | 0.00811 | -0.070797 | -0.022561 | -0.051798 | -0.00775 | 0.17221 | 0.00068 | 0.020043 | 0.02534 | 0.072886 | 0.099312 | -0.003205 | 0.05706 | 0.15247 | 0.027824 | 0.040153 | -0.038754 | 0.009482 | -0.019755 | 0.024293 | 0.095814 | 0.076815 | 0.066578 | 0.047579
2675.2812 | 121.6599 | -57.4356 | 63.9084 | 0.13559 | -0.026784 | -0.021157 | -0.002124 | 0.040843 | 0.071848 | -0.035248 | 0.025017 | 0.12501 | -0.008798 | 0.012689 | -0.075375 | -0.022561 | -0.051798 | -0.00775 | 0.16763 | 0.005259 | 0.010886 | 0.029919 | 0.072886 | 0.10389 | -0.003205 | 0.05706 | 0.15705 | 0.023245 | 0.044732 | -0.043332 | 0.009482 | -0.019755 | 0.024293 | 0.10039 | 0.076815 | 0.066577 | 0.043
2677.0469 | 121.6919 | -55.188 | 66.1697 | 0.13559 | -0.026784 | -0.021157 | -0.006703 | 0.040843 | 0.067269 | -0.044405 | 0.01586 | 0.12501 | -0.017954 | 0.012689 | -0.070797 | -0.027139 | -0.04722 | -0.003172 | 0.16763 | 0.005259 | 0.010886 | 0.02534 | 0.072886 | 0.099312 | -0.012362 | 0.047903 | 0.15705 | 0.014089 | 0.044732 | -0.038754 | 0.004904 | -0.015177 | 0.028871 | 0.086657 | 0.06308 | 0.052843 | 0.029266
2678.7344 | 121.6827 | -53.2791 | 68.161 | 0.13101 | -0.026784 | -0.021157 | -0.006703 | 0.031687 | 0.067269 | -0.044405 | 0.025017 | 0.12501 | -0.004219 | 0.012689 | -0.079953 | -0.017983 | -0.051798 | -0.003172 | 0.16305 | 0.005259 | 0.010886 | 0.02534 | 0.06373 | 0.099312 | -0.012362 | 0.05706 | 0.15705 | 0.027824 | 0.044732 | -0.04791 | 0.01406 | -0.019755 | 0.028871 | 0.10497 | 0.076815 | 0.075734 | 0.047579
2680.4844 | 121.6507 | -52.4094 | 69.0537 | 0.13101 | -0.026784 | -0.016578 | -0.002124 | 0.045421 | 0.067269 | -0.035248 | 0.025017 | 0.12958 | 0.000359 | 0.003531 | -0.070797 | -0.013405 | -0.042641 | -0.00775 | 0.16305 | 0.005259 | 0.015465 | 0.029919 | 0.077464 | 0.099312 | -0.003205 | 0.05706 | 0.16163 | 0.032402 | 0.035574 | -0.038754 | 0.018638 | -0.010598 | 0.024293 | 0.095814 | 0.067658 | 0.071156 | 0.043
2682.1875 | 121.7285 | -51.059 | 70.3537 | 0.13559 | -0.026784 | -0.016578 | -0.006703 | 0.040843 | 0.062691 | -0.039826 | 0.020438 | 0.12501 | -0.013376 | 0.00811 | -0.075375 | -0.022561 | -0.04722 | -0.00775 | 0.16763 | 0.005259 | 0.015465 | 0.02534 | 0.072886 | 0.094734 | -0.007783 | 0.052481 | 0.15705 | 0.018667 | 0.040153 | -0.043332 | 0.009482 | -0.015177 | 0.024293 | 0.095813 | 0.067658 | 0.061999 | 0.033844
2683.9531 | 121.6324 | -47.5845 | 73.9471 | 0.14017 | -0.031363 | -0.012 | 0.007033 | 0.054577 | 0.062691 | -0.039826 | 0.025017 | 0.12958 | -0.017954 | 0.00811 | -0.079953 | -0.022561 | -0.04722 | 0.001406 | 0.17221 | 0.00068 | 0.020043 | 0.039076 | 0.08662 | 0.094734 | -0.007783 | 0.05706 | 0.16163 | 0.014089 | 0.040153 | -0.04791 | 0.009482 | -0.015177 | 0.033449 | 0.10497 | 0.072237 | 0.061999 | 0.029266
2685.7188 | 121.756 | -44.2566 | 77.2202 | 0.12643 | -0.040521 | -0.025735 | -0.006703 | 0.036265 | 0.062691 | -0.044405 | 0.025017 | 0.12501 | -0.004219 | 0.012689 | -0.075375 | -0.017983 | -0.04722 | -0.00775 | 0.15847 | -0.008478 | 0.006308 | 0.02534 | 0.068308 | 0.094734 | -0.012362 | 0.05706 | 0.15705 | 0.027824 | 0.044732 | -0.043332 | 0.01406 | -0.015177 | 0.024293 | 0.10039 | 0.072237 | 0.071156 | 0.043001
2687.4062 | 121.6415 | -41.4871 | 80.04 | 0.13559 | -0.035942 | -0.016578 | -0.002124 | 0.036265 | 0.071848 | -0.035248 | 0.020438 | 0.12043 | -0.008798 | 0.012689 | -0.070797 | -0.022561 | -0.042641 | -0.012328 | 0.16763 | -0.003899 | 0.015465 | 0.029919 | 0.068308 | 0.10389 | -0.003205 | 0.052481 | 0.15247 | 0.023245 | 0.044732 | -0.038754 | 0.009482 | -0.010598 | 0.019715 | 0.091235 | 0.063079 | 0.061999 | 0.033843
2689.1562 | 121.669 | -38.6215 | 82.901 | 0.14017 | -0.035942 | -0.016578 | 0.002454 | 0.036265 | 0.067269 | -0.039826 | 0.020438 | 0.13416 | -0.008798 | 0.012689 | -0.061641 | -0.017983 | -0.04722 | -0.00775 | 0.17221 | -0.003899 | 0.015465 | 0.034497 | 0.068308 | 0.099312 | -0.007783 | 0.052481 | 0.16621 | 0.023245 | 0.044732 | -0.029598 | 0.01406 | -0.015177 | 0.024293 | 0.082079 | 0.067658 | 0.052843 | 0.038422
2690.9219 | 121.7514 | -45.5246 | 75.9796 | 0.13101 | -0.031363 | -0.021157 | -0.002124 | 0.036265 | 0.067269 | -0.039826 | 0.011281 | 0.12958 | -0.013376 | 0.00811 | -0.070797 | -0.027139 | -0.051798 | 0.001406 | 0.16305 | 0.00068 | 0.010886 | 0.029919 | 0.068308 | 0.099312 | -0.007783 | 0.043324 | 0.16163 | 0.018667 | 0.040153 | -0.038754 | 0.004904 | -0.019755 | 0.033449 | 0.082078 | 0.063079 | 0.057421 | 0.038422
2692.625 | 120.9274 | -41.9952 | 79.6143 | 0.14474 | -0.035942 | -0.016578 | -0.002124 | 0.040843 | 0.076426 | -0.048983 | 0.020438 | 0.12501 | -0.013376 | 0.012689 | -0.070797 | -0.013405 | -0.04722 | -0.003172 | 0.17679 | -0.003899 | 0.015465 | 0.029919 | 0.072886 | 0.10847 | -0.01694 | 0.052481 | 0.15705 | 0.018667 | 0.044732 | -0.038754 | 0.018638 | -0.015177 | 0.028871 | 0.091235 | 0.067658 | 0.057421 | 0.033844
2694.3594 | 121.4767 | -40.48 | 81.0745 | 0.14017 | -0.031363 | -0.021157 | -0.002124 | 0.045421 | 0.067269 | -0.035248 | 0.01586 | 0.12958 | 0.000359 | 0.00811 | -0.075375 | -0.013405 | -0.04722 | -0.003172 | 0.17221 | 0.00068 | 0.010886 | 0.029919 | 0.077464 | 0.099312 | -0.003205 | 0.047903 | 0.16163 | 0.032402 | 0.040153 | -0.043332 | 0.018638 | -0.015177 | 0.028871 | 0.091235 | 0.06308 | 0.075734 | 0.047579
2696.0781 | 121.756 | -43.2587 | 78.2867 | 0.13101 | -0.031363 | -0.016578 | -0.002124 | 0.040843 | 0.067269 | -0.039826 | 0.025017 | 0.12958 | -0.008798 | 0.00811 | -0.075375 | -0.022561 | -0.051798 | -0.003172 | 0.16305 | 0.00068 | 0.015465 | 0.029919 | 0.072886 | 0.099312 | -0.007783 | 0.05706 | 0.16163 | 0.023245 | 0.040153 | -0.043332 | 0.009482 | -0.019755 | 0.028871 | 0.10039 | 0.076815 | 0.066577 | 0.043
2697.8281 | 121.7926 | -40.8188 | 80.69 | 0.13559 | -0.035942 | -0.012 | -0.006703 | 0.040843 | 0.067269 | -0.035248 | 0.01586 | 0.12501 | -0.013376 | 0.00811 | -0.075375 | -0.017983 | -0.056376 | -0.003172 | 0.16763 | -0.003899 | 0.020043 | 0.02534 | 0.072886 | 0.099312 | -0.003205 | 0.047903 | 0.15705 | 0.018667 | 0.040153 | -0.043332 | 0.01406 | -0.024333 | 0.028871 | 0.091235 | 0.072236 | 0.061999 | 0.043
2699.5938 | 121.8018 | -39.949 | 81.4819 | 0.14017 | -0.031363 | -0.016578 | -0.006703 | 0.040843 | 0.058113 | -0.035248 | 0.01586 | 0.12958 | -0.008798 | 0.012689 | -0.075375 | -0.022561 | -0.04722 | -0.00775 | 0.17221 | 0.00068 | 0.015465 | 0.02534 | 0.072886 | 0.090156 | -0.003205 | 0.047903 | 0.16163 | 0.023245 | 0.044732 | -0.043332 | 0.009482 | -0.015177 | 0.024293 | 0.091235 | 0.06308 | 0.066577 | 0.038422
2701.2969 | 121.8201 | -44.1971 | 77.2888 | 0.14017 | -0.040521 | -0.016578 | 0.002454 | 0.036265 | 0.062691 | -0.039826 | 0.011281 | 0.12958 | -0.013376 | 0.00811 | -0.070797 | -0.013405 | -0.04722 | -0.00775 | 0.17221 | -0.008478 | 0.015465 | 0.034497 | 0.068308 | 0.094734 | -0.007783 | 0.043324 | 0.16163 | 0.018667 | 0.040153 | -0.038754 | 0.018638 | -0.015177 | 0.024293 | 0.082078 | 0.058501 | 0.057421 | 0.033844
2703.0469 | 121.6873 | -42.7277 | 79.0787 | 0.14017 | -0.026784 | -0.021157 | -0.006703 | 0.045421 | 0.062691 | -0.039826 | 0.020438 | 0.13416 | -0.004219 | 0.00811 | -0.070797 | -0.022561 | -0.04722 | -0.00775 | 0.17221 | 0.005259 | 0.010886 | 0.02534 | 0.077464 | 0.094734 | -0.007783 | 0.052481 | 0.16621 | 0.027824 | 0.040153 | -0.038754 | 0.009482 | -0.015177 | 0.024293 | 0.091235 | 0.067658 | 0.066578 | 0.043001
2704.8438 | 121.8567 | -38.4659 | 82.8415 | 0.13101 | -0.031363 | -0.016578 | 0.002454 | 0.036265 | 0.067269 | -0.026092 | 0.025017 | 0.12501 | -0.013376 | 0.012689 | -0.075375 | -0.017983 | -0.042641 | -0.00775 | 0.16305 | 0.00068 | 0.015465 | 0.034497 | 0.068308 | 0.099312 | 0.005951 | 0.05706 | 0.15705 | 0.018667 | 0.044732 | -0.043332 | 0.01406 | -0.010598 | 0.024293 | 0.10039 | 0.067658 | 0.061999 | 0.029265
2706.5312 | 121.7926 | -37.294 | 84.4116 | 0.13101 | -0.026784 | -0.016578 | -0.011281 | 0.036265 | 0.067269 | -0.039826 | 0.020438 | 0.12501 | -0.013376 | 0.00811 | -0.070797 | -0.027139 | -0.04722 | -0.00775 | 0.16305 | 0.005259 | 0.015465 | 0.020762 | 0.068308 | 0.099312 | -0.007783 | 0.052481 | 0.15705 | 0.018667 | 0.040153 | -0.038754 | 0.004904 | -0.015177 | 0.024293 | 0.091235 | 0.067658 | 0.057421 | 0.033844
2708.2969 | 120.9412 | -31.7368 | 89.9139 | 0.13101 | -0.026784 | -0.021157 | -0.006703 | 0.036265 | 0.067269 | -0.039826 | 0.01586 | 0.13416 | -0.017954 | 0.003531 | -0.075375 | -0.022561 | -0.042641 | -0.012328 | 0.16305 | 0.005259 | 0.010886 | 0.02534 | 0.068308 | 0.099312 | -0.007783 | 0.047903 | 0.16621 | 0.014089 | 0.035574 | -0.043332 | 0.009482 | -0.010598 | 0.019715 | 0.091235 | 0.058501 | 0.057421 | 0.024687
2710.0625 | 121.4996 | -30.5649 | 91.0721 | 0.13101 | -0.031363 | -0.012 | -0.006703 | 0.045421 | 0.062691 | -0.035248 | 0.01586 | 0.12958 | -0.008798 | 0.00811 | -0.070797 | -0.008827 | -0.042641 | -0.00775 | 0.16305 | 0.00068 | 0.020043 | 0.02534 | 0.077464 | 0.094734 | -0.003205 | 0.047903 | 0.16163 | 0.023245 | 0.040153 | -0.038754 | 0.023216 | -0.010598 | 0.024293 | 0.086657 | 0.058501 | 0.061999 | 0.033843
2711.7656 | 120.9595 | -29.0543 | 92.6834 | 0.13559 | -0.031363 | -0.016578 | -0.011281 | 0.031687 | 0.067269 | -0.044405 | 0.01586 | 0.12501 | -0.013376 | 0.00811 | -0.075375 | -0.022561 | -0.042641 | -0.00775 | 0.16763 | 0.00068 | 0.015465 | 0.020762 | 0.06373 | 0.099312 | -0.012362 | 0.047903 | 0.15705 | 0.018667 | 0.040153 | -0.043332 | 0.009482 | -0.010598 | 0.024293 | 0.091235 | 0.058501 | 0.061999 | 0.029265
2713.4688 | 121.756 | -41.1942 | 80.4474 | 0.14017 | -0.026784 | -0.016578 | 0.002454 | 0.040843 | 0.058113 | -0.039826 | 0.020438 | 0.12043 | -0.004219 | 0.00811 | -0.070797 | -0.017983 | -0.04722 | -0.00775 | 0.17221 | 0.005259 | 0.015465 | 0.034497 | 0.072886 | 0.090156 | -0.007783 | 0.052481 | 0.15247 | 0.027824 | 0.040153 | -0.038754 | 0.01406 | -0.015177 | 0.024293 | 0.091235 | 0.067658 | 0.066578 | 0.043001
2715.25 | 121.9116 | -120.0027 | 1.6067 | 0.13559 | -0.031363 | -0.012 | -0.002124 | 0.045421 | 0.071848 | -0.03067 | 0.025017 | 0.13416 | -0.013376 | 0.012689 | -0.084531 | -0.017983 | -0.051798 | -0.012328 | 0.16763 | 0.00068 | 0.020043 | 0.029919 | 0.077464 | 0.10389 | 0.001373 | 0.05706 | 0.16621 | 0.018667 | 0.044732 | -0.052488 | 0.01406 | -0.019755 | 0.019715 | 0.10955 | 0.076815 | 0.071155 | 0.038422
2717.0156 | 121.9757 | -121.1655 | 0.46692 | 0.14474 | -0.031363 | -0.021157 | -0.002124 | 0.040843 | 0.071848 | -0.03067 | 0.020438 | 0.13416 | -0.013376 | 0.012689 | -0.070797 | -0.013405 | -0.042641 | -0.003172 | 0.17679 | 0.00068 | 0.010886 | 0.029919 | 0.072886 | 0.10389 | 0.001373 | 0.052481 | 0.16621 | 0.018667 | 0.044732 | -0.038754 | 0.018638 | -0.010598 | 0.028871 | 0.091235 | 0.063079 | 0.057421 | 0.029265
2718.7031 | 121.843 | -121.2891 | 0.45319 | 0.13559 | -0.031363 | -0.016578 | -0.002124 | 0.045421 | 0.062691 | -0.035248 | 0.01586 | 0.12958 | -0.013376 | 0.00811 | -0.075375 | -0.022561 | -0.051798 | -0.012328 | 0.16763 | 0.00068 | 0.015465 | 0.029919 | 0.077464 | 0.094734 | -0.003205 | 0.047903 | 0.16163 | 0.018667 | 0.040153 | -0.043332 | 0.009482 | -0.019755 | 0.019715 | 0.091235 | 0.067658 | 0.061999 | 0.038422
2720.4062 | 121.9803 | -121.2112 | 0.48065 | 0.14474 | -0.026784 | -0.016578 | -0.002124 | 0.045421 | 0.071848 | -0.048983 | 0.020438 | 0.13416 | 0.000359 | 0.00811 | -0.070797 | -0.022561 | -0.051798 | -0.003172 | 0.17679 | 0.005259 | 0.015465 | 0.029919 | 0.077464 | 0.10389 | -0.01694 | 0.052481 | 0.16621 | 0.032402 | 0.040153 | -0.038754 | 0.009482 | -0.019755 | 0.028871 | 0.091235 | 0.072236 | 0.071156 | 0.052157
2722.1562 | 122.0306 | -120.9366 | 0.68665 | 0.14017 | -0.022205 | -0.021157 | -0.002124 | 0.040843 | 0.067269 | -0.03067 | 0.020438 | 0.13416 | -0.017954 | 0.012689 | -0.075375 | -0.017983 | -0.04722 | -0.00775 | 0.17221 | 0.009838 | 0.010886 | 0.029919 | 0.072886 | 0.099312 | 0.001373 | 0.052481 | 0.16621 | 0.014089 | 0.044732 | -0.043332 | 0.01406 | -0.015177 | 0.024293 | 0.095813 | 0.067658 | 0.057421 | 0.029266
2723.8438 | 102.681 | -61.9354 | 59.7519 | 0.14017 | -0.026784 | -0.016578 | -0.002124 | 0.045421 | 0.067269 | -0.039826 | 0.020438 | 0.13416 | -0.008798 | 0.012689 | -0.075375 | -0.017983 | -0.04722 | -0.00775 | 0.17221 | 0.005259 | 0.015465 | 0.029919 | 0.077464 | 0.099312 | -0.007783 | 0.052481 | 0.16621 | 0.023245 | 0.044732 | -0.043332 | 0.01406 | -0.015177 | 0.024293 | 0.095813 | 0.067658 | 0.066577 | 0.038422
2725.6094 | 121.4172 | -61.5005 | 60.1913 | 0.14017 | -0.022205 | -0.016578 | -0.006703 | 0.045421 | 0.067269 | -0.03067 | 0.020438 | 0.12958 | -0.004219 | 0.017268 | -0.075375 | -0.022561 | -0.056376 | -0.003172 | 0.17221 | 0.009838 | 0.015465 | 0.02534 | 0.077464 | 0.099312 | 0.001373 | 0.052481 | 0.16163 | 0.027824 | 0.049311 | -0.043332 | 0.009482 | -0.024333 | 0.028871 | 0.095813 | 0.076814 | 0.071156 | 0.052157
2727.2969 | 121.6324 | -61.3815 | 60.3149 | 0.14017 | -0.026784 | -0.021157 | -0.006703 | 0.040843 | 0.067269 | -0.03067 | 0.025017 | 0.12501 | -0.013376 | 0.012689 | -0.079953 | -0.022561 | -0.051798 | -0.016906 | 0.17221 | 0.005259 | 0.010886 | 0.02534 | 0.072886 | 0.099312 | 0.001373 | 0.05706 | 0.15705 | 0.018667 | 0.044732 | -0.04791 | 0.009482 | -0.019755 | 0.015137 | 0.10497 | 0.076815 | 0.066577 | 0.038422
2729.0469 | 121.907 | -61.8988 | 59.7382 | 0.13559 | -0.022205 | -0.012 | -0.002124 | 0.027109 | 0.062691 | -0.039826 | 0.029595 | 0.12501 | -0.013376 | 0.00811 | -0.075375 | -0.022561 | -0.051798 | 0.001406 | 0.16763 | 0.009838 | 0.020043 | 0.029919 | 0.059152 | 0.094734 | -0.007783 | 0.061638 | 0.15705 | 0.018667 | 0.040153 | -0.043332 | 0.009482 | -0.019755 | 0.033449 | 0.10497 | 0.081393 | 0.061999 | 0.038422
2730.75 | 121.669 | -61.8393 | 59.8572 | 0.13559 | -0.026784 | -0.016578 | -0.006703 | 0.045421 | 0.067269 | -0.039826 | 0.025017 | 0.12501 | -0.008798 | 0.012689 | -0.070797 | -0.022561 | -0.051798 | -0.00775 | 0.16763 | 0.005259 | 0.015465 | 0.02534 | 0.077464 | 0.099312 | -0.007783 | 0.05706 | 0.15705 | 0.023245 | 0.044732 | -0.038754 | 0.009482 | -0.019755 | 0.024293 | 0.095814 | 0.076815 | 0.061999 | 0.043
2732.4375 | 121.875 | -62.1048 | 59.6237 | 0.13559 | -0.031363 | -0.012 | -0.002124 | 0.040843 | 0.067269 | -0.044405 | 0.025017 | 0.12501 | -0.008798 | 0.003531 | -0.070797 | -0.022561 | -0.051798 | -0.012328 | 0.16763 | 0.00068 | 0.020043 | 0.029919 | 0.072886 | 0.099312 | -0.012362 | 0.05706 | 0.15705 | 0.023245 | 0.035574 | -0.038754 | 0.009482 | -0.019755 | 0.019715 | 0.095814 | 0.076815 | 0.061999 | 0.043
2734.1875 | 121.9162 | -62.059 | 59.6191 | 0.14017 | -0.035942 | -0.021157 | -0.006703 | 0.040843 | 0.067269 | -0.039826 | 0.020438 | 0.13416 | -0.013376 | 0.012689 | -0.075375 | -0.022561 | -0.056376 | -0.003172 | 0.17221 | -0.003899 | 0.010886 | 0.02534 | 0.072886 | 0.099312 | -0.007783 | 0.052481 | 0.16621 | 0.018667 | 0.044732 | -0.043332 | 0.009482 | -0.024333 | 0.028871 | 0.095813 | 0.076814 | 0.061999 | 0.043
2735.875 | 121.8613 | -62.2559 | 59.5047 | 0.13101 | -0.026784 | -0.016578 | 0.007033 | 0.049999 | 0.067269 | -0.044405 | 0.025017 | 0.13416 | -0.013376 | 0.003531 | -0.075375 | -0.017983 | -0.042641 | -0.00775 | 0.16305 | 0.005259 | 0.015465 | 0.039076 | 0.082042 | 0.099312 | -0.012362 | 0.05706 | 0.16621 | 0.018667 | 0.035574 | -0.043332 | 0.01406 | -0.010598 | 0.024293 | 0.10039 | 0.067658 | 0.061999 | 0.029265
2737.6406 | 121.9391 | -62.7457 | 58.9417 | 0.14017 | -0.031363 | -0.016578 | -0.006703 | 0.036265 | 0.058113 | -0.035248 | 0.025017 | 0.12043 | -0.008798 | 0.00811 | -0.075375 | -0.017983 | -0.051798 | 0.001406 | 0.17221 | 0.00068 | 0.015465 | 0.02534 | 0.068308 | 0.090156 | -0.003205 | 0.05706 | 0.15247 | 0.023245 | 0.040153 | -0.043332 | 0.01406 | -0.019755 | 0.033449 | 0.10039 | 0.076815 | 0.066577 | 0.043
2739.3281 | 121.8796 | -63.1851 | 58.6075 | 0.14017 | -0.031363 | -0.021157 | -0.006703 | 0.040843 | 0.071848 | -0.035248 | 0.025017 | 0.12043 | -0.004219 | -0.001048 | -0.075375 | -0.017983 | -0.04722 | -0.003172 | 0.17221 | 0.00068 | 0.010886 | 0.02534 | 0.072886 | 0.10389 | -0.003205 | 0.05706 | 0.15247 | 0.027824 | 0.030995 | -0.043332 | 0.01406 | -0.015177 | 0.028871 | 0.10039 | 0.072237 | 0.071156 | 0.043001
2741.0781 | 121.9025 | -63.9267 | 57.8293 | 0.13559 | -0.031363 | -0.021157 | -0.006703 | 0.040843 | 0.071848 | -0.035248 | 0.025017 | 0.12501 | -0.008798 | 0.012689 | -0.070797 | -0.013405 | -0.042641 | -0.003172 | 0.16763 | 0.00068 | 0.010886 | 0.02534 | 0.072886 | 0.10389 | -0.003205 | 0.05706 | 0.15705 | 0.023245 | 0.044732 | -0.038754 | 0.018638 | -0.010598 | 0.028871 | 0.095814 | 0.067658 | 0.061999 | 0.033843
2742.7656 | 121.8933 | -2.4399 | 119.014 | 0.13559 | -0.022205 | -0.021157 | -0.002124 | 0.045421 | 0.062691 | -0.035248 | 0.020438 | 0.12501 | -0.013376 | 0.003531 | -0.075375 | -0.022561 | -0.04722 | -0.00775 | 0.16763 | 0.009838 | 0.010886 | 0.029919 | 0.077464 | 0.094734 | -0.003205 | 0.052481 | 0.15705 | 0.018667 | 0.035574 | -0.043332 | 0.009482 | -0.015177 | 0.024293 | 0.095813 | 0.067658 | 0.061999 | 0.033844
2744.5156 | 121.9666 | -4.0054 | 117.453 | 0.14017 | -0.031363 | -0.016578 | -0.006703 | 0.045421 | 0.062691 | -0.039826 | 0.020438 | 0.12958 | -0.013376 | 0.00811 | -0.079953 | -0.022561 | -0.04722 | -0.00775 | 0.17221 | 0.00068 | 0.015465 | 0.02534 | 0.077464 | 0.094734 | -0.007783 | 0.052481 | 0.16163 | 0.018667 | 0.040153 | -0.04791 | 0.009482 | -0.015177 | 0.024293 | 0.10039 | 0.067658 | 0.066577 | 0.033844
2746.2812 | 121.788 | -116.5512 | 4.8019 | 0.13559 | -0.031363 | -0.021157 | -0.002124 | 0.045421 | 0.071848 | -0.035248 | 0.01586 | 0.12501 | -0.017954 | 0.012689 | -0.070797 | -0.022561 | -0.056376 | -0.012328 | 0.16763 | 0.00068 | 0.010886 | 0.029919 | 0.077464 | 0.10389 | -0.003205 | 0.047903 | 0.15705 | 0.014089 | 0.044732 | -0.038754 | 0.009482 | -0.024333 | 0.019715 | 0.086657 | 0.072236 | 0.052843 | 0.038422
2748.0469 | 121.756 | -117.2745 | 4.1199 | 0.13101 | -0.031363 | -0.021157 | -0.002124 | 0.040843 | 0.067269 | -0.039826 | 0.025017 | 0.12958 | -0.017954 | 0.017268 | -0.075375 | -0.017983 | -0.051798 | -0.00775 | 0.16305 | 0.00068 | 0.010886 | 0.029919 | 0.072886 | 0.099312 | -0.007783 | 0.05706 | 0.16163 | 0.014089 | 0.049311 | -0.043332 | 0.01406 | -0.019755 | 0.024293 | 0.10039 | 0.076815 | 0.057421 | 0.033844
2749.75 | 121.7377 | -117.5583 | 3.8452 | 0.14017 | -0.035942 | -0.012 | -0.006703 | 0.045421 | 0.062691 | -0.039826 | 0.020438 | 0.13416 | -0.013376 | 0.00811 | -0.070797 | -0.027139 | -0.04722 | -0.003172 | 0.17221 | -0.003899 | 0.020043 | 0.02534 | 0.077464 | 0.094734 | -0.007783 | 0.052481 | 0.16621 | 0.018667 | 0.040153 | -0.038754 | 0.004904 | -0.015177 | 0.028871 | 0.091235 | 0.067658 | 0.057421 | 0.033844
2751.5312 | 121.6599 | -117.7139 | 3.6484 | 0.14017 | -0.031363 | -0.021157 | -0.011281 | 0.040843 | 0.062691 | -0.035248 | 0.020438 | 0.12958 | -0.013376 | 0.012689 | -0.075375 | -0.017983 | -0.051798 | -0.012328 | 0.17221 | 0.00068 | 0.010886 | 0.020762 | 0.072886 | 0.094734 | -0.003205 | 0.052481 | 0.16163 | 0.018667 | 0.044732 | -0.043332 | 0.01406 | -0.019755 | 0.019715 | 0.095813 | 0.072236 | 0.061999 | 0.038422
2753.2188 | 121.5912 | -117.7826 | 3.6026 | 0.14017 | -0.031363 | -0.016578 | 0.002454 | 0.040843 | 0.058113 | -0.039826 | 0.020438 | 0.12501 | -0.008798 | 0.003531 | -0.070797 | -0.017983 | -0.04722 | -0.003172 | 0.17221 | 0.00068 | 0.015465 | 0.034497 | 0.072886 | 0.090156 | -0.007783 | 0.052481 | 0.15705 | 0.023245 | 0.035574 | -0.038754 | 0.01406 | -0.015177 | 0.028871 | 0.091235 | 0.067658 | 0.061999 | 0.038422
2754.9844 | 121.582 | -117.7277 | 3.5751 | 0.14017 | -0.026784 | -0.025735 | 0.002454 | 0.045421 | 0.067269 | -0.039826 | 0.011281 | 0.12958 | -0.013376 | 0.00811 | -0.066219 | -0.017983 | -0.04722 | -0.00775 | 0.17221 | 0.005259 | 0.006308 | 0.034497 | 0.077464 | 0.099312 | -0.007783 | 0.043324 | 0.16163 | 0.018667 | 0.040153 | -0.034176 | 0.01406 | -0.015177 | 0.024293 | 0.0775 | 0.058501 | 0.052843 | 0.033844
2756.75 | 121.5729 | -117.897 | 3.4287 | 0.14017 | -0.035942 | -0.021157 | -0.011281 | 0.040843 | 0.062691 | -0.039826 | 0.025017 | 0.12501 | -0.017954 | 0.012689 | -0.070797 | -0.017983 | -0.04722 | -0.012328 | 0.17221 | -0.003899 | 0.010886 | 0.020762 | 0.072886 | 0.094734 | -0.007783 | 0.05706 | 0.15705 | 0.014089 | 0.044732 | -0.038754 | 0.01406 | -0.015177 | 0.019715 | 0.095814 | 0.072237 | 0.052843 | 0.029266
2758.5156 | 121.5225 | -117.9749 | 3.2318 | 0.14017 | -0.031363 | -0.012 | 0.002454 | 0.045421 | 0.062691 | -0.035248 | 0.020438 | 0.12501 | -0.008798 | 0.012689 | -0.075375 | -0.017983 | -0.051798 | -0.012328 | 0.17221 | 0.00068 | 0.020043 | 0.034497 | 0.077464 | 0.094734 | -0.003205 | 0.052481 | 0.15705 | 0.023245 | 0.044732 | -0.043332 | 0.01406 | -0.019755 | 0.019715 | 0.095813 | 0.072236 | 0.066577 | 0.043
2760.2031 | 121.5683 | -118.0481 | 3.154 | 0.13559 | -0.022205 | -0.016578 | -0.006703 | 0.040843 | 0.062691 | -0.035248 | 0.025017 | 0.12958 | -0.004219 | 0.012689 | -0.070797 | -0.017983 | -0.04722 | -0.003172 | 0.16763 | 0.009838 | 0.015465 | 0.02534 | 0.072886 | 0.094734 | -0.003205 | 0.05706 | 0.16163 | 0.027824 | 0.044732 | -0.038754 | 0.01406 | -0.015177 | 0.028871 | 0.095814 | 0.072237 | 0.066578 | 0.043001
2761.9531 | 121.5729 | -118.1305 | 3.1128 | 0.13559 | -0.026784 | -0.021157 | -0.002124 | 0.045421 | 0.062691 | -0.039826 | 0.025017 | 0.12501 | -0.008798 | 0.017268 | -0.070797 | -0.017983 | -0.051798 | -0.012328 | 0.16763 | 0.005259 | 0.010886 | 0.029919 | 0.077464 | 0.094734 | -0.007783 | 0.05706 | 0.15705 | 0.023245 | 0.049311 | -0.038754 | 0.01406 | -0.019755 | 0.019715 | 0.095814 | 0.076815 | 0.061999 | 0.043
2763.7031 | 121.4539 | -118.1946 | 3.1219 | 0.14017 | -0.031363 | -0.021157 | -0.002124 | 0.040843 | 0.058113 | -0.03067 | 0.025017 | 0.13874 | -0.013376 | 0.00811 | -0.075375 | -0.013405 | -0.056376 | -0.00775 | 0.17221 | 0.00068 | 0.010886 | 0.029919 | 0.072886 | 0.090156 | 0.001373 | 0.05706 | 0.17079 | 0.018667 | 0.040153 | -0.043332 | 0.018638 | -0.024333 | 0.024293 | 0.10039 | 0.081393 | 0.061999 | 0.043
2765.4531 | 121.3989 | -118.2312 | 3.067 | 0.13559 | -0.031363 | -0.012 | 0.002454 | 0.045421 | 0.067269 | -0.03067 | 0.025017 | 0.12501 | -0.013376 | 0.00811 | -0.070797 | -0.027139 | -0.051798 | -0.012328 | 0.16763 | 0.00068 | 0.020043 | 0.034497 | 0.077464 | 0.099312 | 0.001373 | 0.05706 | 0.15705 | 0.018667 | 0.040153 | -0.038754 | 0.004904 | -0.019755 | 0.019715 | 0.095814 | 0.076815 | 0.057421 | 0.038422
2767.2188 | 121.4905 | -118.2312 | 2.9984 | 0.13559 | -0.031363 | -0.012 | -0.002124 | 0.036265 | 0.067269 | -0.039826 | 0.01586 | 0.13416 | -0.008798 | 0.017268 | -0.066219 | -0.017983 | -0.042641 | -0.012328 | 0.16763 | 0.00068 | 0.020043 | 0.029919 | 0.068308 | 0.099312 | -0.007783 | 0.047903 | 0.16621 | 0.023245 | 0.049311 | -0.034176 | 0.01406 | -0.010598 | 0.019715 | 0.082079 | 0.058501 | 0.057421 | 0.033843
2768.9062 | 121.4401 | -118.2541 | 2.9526 | 0.13559 | -0.035942 | -0.016578 | -0.002124 | 0.040843 | 0.062691 | -0.039826 | 0.025017 | 0.12958 | -0.017954 | 0.00811 | -0.075375 | -0.017983 | -0.051798 | -0.003172 | 0.16763 | -0.003899 | 0.015465 | 0.029919 | 0.072886 | 0.094734 | -0.007783 | 0.05706 | 0.16163 | 0.014089 | 0.040153 | -0.043332 | 0.01406 | -0.019755 | 0.028871 | 0.10039 | 0.076815 | 0.057421 | 0.033844
2770.6719 | 121.4539 | -118.2587 | 2.916 | 0.13101 | -0.026784 | -0.012 | -0.006703 | 0.040843 | 0.058113 | -0.03067 | 0.025017 | 0.12958 | -0.004219 | 0.012689 | -0.070797 | -0.017983 | -0.042641 | -0.00775 | 0.16305 | 0.005259 | 0.020043 | 0.02534 | 0.072886 | 0.090156 | 0.001373 | 0.05706 | 0.16163 | 0.027824 | 0.044732 | -0.038754 | 0.01406 | -0.010598 | 0.024293 | 0.095814 | 0.067658 | 0.066578 | 0.038422
2772.3906 | 121.3943 | -118.309 | 2.8931 | 0.13559 | -0.031363 | -0.030314 | -0.011281 | 0.040843 | 0.067269 | -0.039826 | 0.025017 | 0.12501 | -0.017954 | 0.012689 | -0.066219 | -0.013405 | -0.04722 | -0.00775 | 0.16763 | 0.00068 | 0.001729 | 0.020762 | 0.072886 | 0.099312 | -0.007783 | 0.05706 | 0.15705 | 0.014089 | 0.044732 | -0.034176 | 0.018638 | -0.015177 | 0.024293 | 0.091236 | 0.072237 | 0.048265 | 0.029266
2774.1562 | 121.376 | -118.3456 | 2.8427 | 0.13559 | -0.031363 | -0.025735 | -0.002124 | 0.045421 | 0.062691 | -0.039826 | 0.025017 | 0.13416 | -0.017954 | 0.012689 | -0.066219 | -0.017983 | -0.051798 | -0.003172 | 0.16763 | 0.00068 | 0.006308 | 0.029919 | 0.077464 | 0.094734 | -0.007783 | 0.05706 | 0.16621 | 0.014089 | 0.044732 | -0.034176 | 0.01406 | -0.019755 | 0.028871 | 0.091236 | 0.076815 | 0.048265 | 0.033844
2775.9219 | 121.0693 | -118.396 | 2.861 | 0.13101 | -0.022205 | -0.016578 | 0.002454 | 0.031687 | 0.062691 | -0.039826 | 0.025017 | 0.13874 | -0.013376 | 0.00811 | -0.070797 | -0.022561 | -0.042641 | -0.012328 | 0.16305 | 0.009838 | 0.015465 | 0.034497 | 0.06373 | 0.094734 | -0.007783 | 0.05706 | 0.17079 | 0.018667 | 0.040153 | -0.038754 | 0.009482 | -0.010598 | 0.019715 | 0.095814 | 0.067658 | 0.057421 | 0.029265
2777.6875 | 121.4035 | -118.3411 | 2.7878 | 0.13559 | -0.031363 | -0.012 | -0.006703 | 0.040843 | 0.062691 | -0.035248 | 0.029595 | 0.12958 | -0.017954 | -0.001048 | -0.070797 | -0.013405 | -0.04722 | 0.001406 | 0.16763 | 0.00068 | 0.020043 | 0.02534 | 0.072886 | 0.094734 | -0.003205 | 0.061638 | 0.16163 | 0.014089 | 0.030995 | -0.038754 | 0.018638 | -0.015177 | 0.033449 | 0.10039 | 0.076815 | 0.052843 | 0.029266
2779.3906 | 121.344 | -118.3731 | 2.7969 | 0.14017 | -0.031363 | -0.025735 | 0.002454 | 0.036265 | 0.062691 | -0.039826 | 0.029595 | 0.12958 | -0.017954 | 0.00811 | -0.070797 | -0.017983 | -0.042641 | -0.00775 | 0.17221 | 0.00068 | 0.006308 | 0.034497 | 0.068308 | 0.094734 | -0.007783 | 0.061638 | 0.16163 | 0.014089 | 0.040153 | -0.038754 | 0.01406 | -0.010598 | 0.024293 | 0.10039 | 0.072236 | 0.052843 | 0.024687
2781.1562 | 121.344 | -118.3823 | 2.7649 | 0.13559 | -0.026784 | -0.012 | -0.006703 | 0.045421 | 0.062691 | -0.039826 | 0.029595 | 0.12501 | -0.008798 | 0.012689 | -0.070797 | -0.017983 | -0.051798 | 0.001406 | 0.16763 | 0.005259 | 0.020043 | 0.02534 | 0.077464 | 0.094734 | -0.007783 | 0.061638 | 0.15705 | 0.023245 | 0.044732 | -0.038754 | 0.01406 | -0.019755 | 0.033449 | 0.10039 | 0.081393 | 0.061999 | 0.043
2782.8594 | 121.3303 | -118.3685 | 2.7695 | 0.14017 | -0.035942 | -0.016578 | 0.002454 | 0.040843 | 0.062691 | -0.039826 | 0.025017 | 0.12501 | -0.013376 | 0.00811 | -0.066219 | -0.013405 | -0.04722 | -0.00775 | 0.17221 | -0.003899 | 0.015465 | 0.034497 | 0.072886 | 0.094734 | -0.007783 | 0.05706 | 0.15705 | 0.018667 | 0.040153 | -0.034176 | 0.018638 | -0.015177 | 0.024293 | 0.091236 | 0.072237 | 0.052843 | 0.033844
2784.625 | 121.3303 | -118.3731 | 2.7512 | 0.14017 | -0.026784 | -0.016578 | 0.002454 | 0.031687 | 0.062691 | -0.039826 | 0.025017 | 0.12958 | -0.017954 | 0.00811 | -0.066219 | -0.022561 | -0.051798 | -0.00775 | 0.17221 | 0.005259 | 0.015465 | 0.034497 | 0.06373 | 0.094734 | -0.007783 | 0.05706 | 0.16163 | 0.014089 | 0.040153 | -0.034176 | 0.009482 | -0.019755 | 0.024293 | 0.091236 | 0.076815 | 0.048265 | 0.033844
2786.3906 | 121.0922 | -118.3273 | 2.8152 | 0.13101 | -0.035942 | -0.016578 | -0.002124 | 0.040843 | 0.062691 | -0.039826 | 0.020438 | 0.12958 | -0.013376 | 0.00811 | -0.070797 | -0.017983 | -0.051798 | -0.00775 | 0.16305 | -0.003899 | 0.015465 | 0.029919 | 0.072886 | 0.094734 | -0.007783 | 0.052481 | 0.16163 | 0.018667 | 0.040153 | -0.038754 | 0.01406 | -0.019755 | 0.024293 | 0.091235 | 0.072236 | 0.057421 | 0.038422
2788.1562 | 121.4493 | -118.3548 | 2.623 | 0.14017 | -0.031363 | -0.021157 | -0.002124 | 0.049999 | 0.067269 | -0.035248 | 0.025017 | 0.12958 | -0.004219 | 0.012689 | -0.075375 | -0.013405 | -0.056376 | -0.012328 | 0.17221 | 0.00068 | 0.010886 | 0.029919 | 0.082042 | 0.099312 | -0.003205 | 0.05706 | 0.16163 | 0.027824 | 0.044732 | -0.043332 | 0.018638 | -0.024333 | 0.019715 | 0.10039 | 0.081393 | 0.071156 | 0.052157
2789.8594 | 121.2891 | -118.4738 | 2.6321 | 0.13559 | -0.022205 | -0.016578 | -0.002124 | 0.045421 | 0.062691 | -0.039826 | 0.029595 | 0.12958 | -0.008798 | 0.00811 | -0.075375 | -0.017983 | -0.051798 | -0.003172 | 0.16763 | 0.009838 | 0.015465 | 0.029919 | 0.077464 | 0.094734 | -0.007783 | 0.061638 | 0.16163 | 0.023245 | 0.040153 | -0.043332 | 0.01406 | -0.019755 | 0.028871 | 0.10497 | 0.081393 | 0.066577 | 0.043
2791.625 | 121.376 | -118.4692 | 2.5543 | 0.13101 | -0.035942 | -0.021157 | -0.002124 | 0.045421 | 0.062691 | -0.035248 | 0.020438 | 0.12958 | -0.013376 | 0.00811 | -0.066219 | -0.017983 | -0.04722 | -0.00775 | 0.16305 | -0.003899 | 0.010886 | 0.029919 | 0.077464 | 0.094734 | -0.003205 | 0.052481 | 0.16163 | 0.018667 | 0.040153 | -0.034176 | 0.01406 | -0.015177 | 0.024293 | 0.086657 | 0.067658 | 0.052843 | 0.033844
2793.3125 | 121.3623 | -118.5013 | 2.5452 | 0.13559 | -0.026784 | -0.012 | -0.002124 | 0.036265 | 0.062691 | -0.035248 | 0.029595 | 0.12958 | -0.013376 | 0.012689 | -0.066219 | -0.017983 | -0.051798 | -0.00775 | 0.16763 | 0.005259 | 0.020043 | 0.029919 | 0.068308 | 0.094734 | -0.003205 | 0.061638 | 0.16163 | 0.018667 | 0.044732 | -0.034176 | 0.01406 | -0.019755 | 0.024293 | 0.095814 | 0.081393 | 0.052843 | 0.038422
2795.0781 | 121.3028 | -118.5379 | 2.5543 | 0.13101 | -0.031363 | -0.025735 | -0.006703 | 0.045421 | 0.067269 | -0.039826 | 0.025017 | 0.12958 | -0.008798 | 0.012689 | -0.075375 | -0.022561 | -0.051798 | -0.003172 | 0.16305 | 0.00068 | 0.006308 | 0.02534 | 0.077464 | 0.099312 | -0.007783 | 0.05706 | 0.16163 | 0.023245 | 0.044732 | -0.043332 | 0.009482 | -0.019755 | 0.028871 | 0.10039 | 0.076815 | 0.066577 | 0.043
2796.7812 | 121.2158 | -118.5745 | 2.5635 | 0.14017 | -0.031363 | -0.016578 | 0.002454 | 0.045421 | 0.071848 | -0.039826 | 0.029595 | 0.12958 | 0.004937 | 0.012689 | -0.070797 | -0.013405 | -0.04722 | 0.001406 | 0.17221 | 0.00068 | 0.015465 | 0.034497 | 0.077464 | 0.10389 | -0.007783 | 0.061638 | 0.16163 | 0.03698 | 0.044732 | -0.038754 | 0.018638 | -0.015177 | 0.033449 | 0.10039 | 0.076815 | 0.075734 | 0.052157
2798.5469 | 120.6757 | -1.0025 | 119.6411 | 0.14017 | -0.022205 | -0.025735 | -0.002124 | 0.040843 | 0.067269 | -0.039826 | 0.020438 | 0.12958 | -0.017954 | 0.003531 | -0.070797 | -0.008827 | -0.042641 | -0.00775 | 0.17221 | 0.009838 | 0.006308 | 0.029919 | 0.072886 | 0.099312 | -0.007783 | 0.052481 | 0.16163 | 0.014089 | 0.035574 | -0.038754 | 0.023216 | -0.010598 | 0.024293 | 0.091235 | 0.063079 | 0.052843 | 0.024687
2800.25 | 121.0327 | -1.0117 | 119.7418 | 0.12643 | -0.035942 | -0.021157 | 0.002454 | 0.040843 | 0.062691 | -0.039826 | 0.025017 | 0.12958 | -0.017954 | 0.00811 | -0.070797 | -0.017983 | -0.042641 | -0.00775 | 0.15847 | -0.003899 | 0.010886 | 0.034497 | 0.072886 | 0.094734 | -0.007783 | 0.05706 | 0.16163 | 0.014089 | 0.040153 | -0.038754 | 0.01406 | -0.010598 | 0.024293 | 0.095814 | 0.067658 | 0.052843 | 0.024687
2802 | 121.0693 | -0.93384 | 119.9707 | 0.13559 | -0.031363 | -0.016578 | -0.006703 | 0.036265 | 0.067269 | -0.035248 | 0.01586 | 0.13416 | -0.004219 | 0.00811 | -0.075375 | -0.013405 | -0.04722 | -0.003172 | 0.16763 | 0.00068 | 0.015465 | 0.02534 | 0.068308 | 0.099312 | -0.003205 | 0.047903 | 0.16621 | 0.027824 | 0.040153 | -0.043332 | 0.018638 | -0.015177 | 0.028871 | 0.091235 | 0.06308 | 0.071156 | 0.043001
2803.75 | 121.051 | -0.95673 | 120.0668 | 0.13559 | -0.035942 | -0.021157 | -0.002124 | 0.045421 | 0.058113 | -0.035248 | 0.025017 | 0.12501 | -0.008798 | 0.00811 | -0.070797 | -0.017983 | -0.042641 | -0.00775 | 0.16763 | -0.003899 | 0.010886 | 0.029919 | 0.077464 | 0.090156 | -0.003205 | 0.05706 | 0.15705 | 0.023245 | 0.040153 | -0.038754 | 0.01406 | -0.010598 | 0.024293 | 0.095814 | 0.067658 | 0.061999 | 0.033843
2805.4531 | 121.1288 | -1.1581 | 119.9432 | 0.14017 | -0.031363 | -0.016578 | -0.002124 | 0.040843 | 0.062691 | -0.035248 | 0.029595 | 0.12958 | -0.017954 | 0.012689 | -0.070797 | -0.017983 | -0.042641 | 0.001406 | 0.17221 | 0.00068 | 0.015465 | 0.029919 | 0.072886 | 0.094734 | -0.003205 | 0.061638 | 0.16163 | 0.014089 | 0.044732 | -0.038754 | 0.01406 | -0.010598 | 0.033449 | 0.10039 | 0.072236 | 0.052843 | 0.024687
2807.2031 | 121.1197 | -0.96588 | 120.1904 | 0.13559 | -0.031363 | -0.021157 | -0.002124 | 0.045421 | 0.062691 | -0.039826 | 0.020438 | 0.12501 | -0.013376 | 0.00811 | -0.066219 | -0.013405 | -0.042641 | -0.00775 | 0.16763 | 0.00068 | 0.010886 | 0.029919 | 0.077464 | 0.094734 | -0.007783 | 0.052481 | 0.15705 | 0.018667 | 0.040153 | -0.034176 | 0.018638 | -0.010598 | 0.024293 | 0.086657 | 0.063079 | 0.052843 | 0.029265
2808.9062 | 121.2479 | -0.93842 | 120.2133 | 0.13101 | -0.026784 | -0.025735 | -0.002124 | 0.036265 | 0.058113 | -0.039826 | 0.020438 | 0.13416 | -0.008798 | 0.00811 | -0.070797 | -0.017983 | -0.042641 | -0.012328 | 0.16305 | 0.005259 | 0.006308 | 0.029919 | 0.068308 | 0.090156 | -0.007783 | 0.052481 | 0.16621 | 0.023245 | 0.040153 | -0.038754 | 0.01406 | -0.010598 | 0.019715 | 0.091235 | 0.063079 | 0.061999 | 0.033843
2810.6562 | 121.2479 | -0.95673 | 120.282 | 0.13559 | -0.035942 | -0.016578 | -0.006703 | 0.036265 | 0.067269 | -0.039826 | 0.025017 | 0.12958 | -0.013376 | -0.001048 | -0.070797 | -0.008827 | -0.042641 | -0.003172 | 0.16763 | -0.003899 | 0.015465 | 0.02534 | 0.068308 | 0.099312 | -0.007783 | 0.05706 | 0.16163 | 0.018667 | 0.030995 | -0.038754 | 0.023216 | -0.010598 | 0.028871 | 0.095814 | 0.067658 | 0.057421 | 0.029265
2812.4219 | 121.3806 | -0.91095 | 120.3232 | 0.13101 | -0.026784 | -0.021157 | -0.011281 | 0.045421 | 0.067269 | -0.044405 | 0.029595 | 0.12501 | -0.017954 | 0.00811 | -0.070797 | -0.017983 | -0.042641 | -0.00775 | 0.16305 | 0.005259 | 0.010886 | 0.020762 | 0.077464 | 0.099312 | -0.012362 | 0.061638 | 0.15705 | 0.014089 | 0.040153 | -0.038754 | 0.01406 | -0.010598 | 0.024293 | 0.10039 | 0.072236 | 0.052843 | 0.024687
2814.1875 | 121.1884 | -0.93384 | 120.369 | 0.13559 | -0.031363 | -0.021157 | 0.002454 | 0.040843 | 0.071848 | -0.044405 | 0.025017 | 0.12501 | -0.013376 | 0.00811 | -0.066219 | -0.017983 | -0.04722 | -0.003172 | 0.16763 | 0.00068 | 0.010886 | 0.034497 | 0.072886 | 0.10389 | -0.012362 | 0.05706 | 0.15705 | 0.018667 | 0.040153 | -0.034176 | 0.01406 | -0.015177 | 0.028871 | 0.091236 | 0.072237 | 0.052843 | 0.033844
2815.9375 | 120.5566 | -0.95673 | 120.401 | 0.13559 | -0.026784 | -0.021157 | -0.006703 | 0.040843 | 0.067269 | -0.039826 | 0.025017 | 0.13416 | -0.004219 | 0.003531 | -0.070797 | -0.022561 | -0.042641 | -0.00775 | 0.16763 | 0.005259 | 0.010886 | 0.02534 | 0.072886 | 0.099312 | -0.007783 | 0.05706 | 0.16621 | 0.027824 | 0.035574 | -0.038754 | 0.009482 | -0.010598 | 0.024293 | 0.095814 | 0.067658 | 0.066578 | 0.038422
2817.6562 | 121.3989 | -0.92926 | 120.3827 | 0.13101 | -0.031363 | -0.016578 | -0.002124 | 0.036265 | 0.062691 | -0.039826 | 0.020438 | 0.13416 | -0.013376 | 0.012689 | -0.070797 | -0.022561 | -0.051798 | -0.00775 | 0.16305 | 0.00068 | 0.015465 | 0.029919 | 0.068308 | 0.094734 | -0.007783 | 0.052481 | 0.16621 | 0.018667 | 0.044732 | -0.038754 | 0.009482 | -0.019755 | 0.024293 | 0.091235 | 0.072236 | 0.057421 | 0.038422
2819.3594 | 121.463 | -0.90637 | 120.4422 | 0.13101 | -0.026784 | -0.021157 | -0.002124 | 0.045421 | 0.062691 | -0.048983 | 0.020438 | 0.12958 | -0.013376 | 0.00811 | -0.066219 | -0.017983 | -0.051798 | -0.00775 | 0.16305 | 0.005259 | 0.010886 | 0.029919 | 0.077464 | 0.094734 | -0.01694 | 0.052481 | 0.16163 | 0.018667 | 0.040153 | -0.034176 | 0.01406 | -0.019755 | 0.024293 | 0.086657 | 0.072236 | 0.052843 | 0.038422
2821.1094 | 121.431 | -0.93842 | 120.4468 | 0.14017 | -0.031363 | -0.016578 | -0.002124 | 0.045421 | 0.062691 | -0.039826 | 0.020438 | 0.12501 | -0.013376 | 0.012689 | -0.070797 | -0.017983 | -0.04722 | -0.003172 | 0.17221 | 0.00068 | 0.015465 | 0.029919 | 0.077464 | 0.094734 | -0.007783 | 0.052481 | 0.15705 | 0.018667 | 0.044732 | -0.038754 | 0.01406 | -0.015177 | 0.028871 | 0.091235 | 0.067658 | 0.057421 | 0.033844
2822.875 | 120.8221 | -0.97961 | 120.5292 | 0.14017 | -0.026784 | -0.016578 | -0.002124 | 0.040843 | 0.067269 | -0.035248 | 0.025017 | 0.12501 | -0.013376 | 0.003531 | -0.066219 | -0.022561 | -0.051798 | -0.003172 | 0.17221 | 0.005259 | 0.015465 | 0.029919 | 0.072886 | 0.099312 | -0.003205 | 0.05706 | 0.15705 | 0.018667 | 0.035574 | -0.034176 | 0.009482 | -0.019755 | 0.028871 | 0.091236 | 0.076815 | 0.052843 | 0.038422
2824.6406 | 121.3669 | -0.9201 | 120.5063 | 0.13559 | -0.031363 | -0.021157 | -0.002124 | 0.040843 | 0.067269 | -0.039826 | 0.029595 | 0.13874 | -0.008798 | 0.012689 | -0.066219 | -0.017983 | -0.042641 | -0.00775 | 0.16763 | 0.00068 | 0.010886 | 0.029919 | 0.072886 | 0.099312 | -0.007783 | 0.061638 | 0.17079 | 0.023245 | 0.044732 | -0.034176 | 0.01406 | -0.010598 | 0.024293 | 0.095814 | 0.072236 | 0.057421 | 0.033843
2826.3438 | 121.5637 | -0.9201 | 120.4834 | 0.13101 | -0.031363 | -0.016578 | -0.002124 | 0.045421 | 0.062691 | -0.035248 | 0.020438 | 0.13416 | -0.013376 | -0.001048 | -0.075375 | -0.017983 | -0.04722 | -0.00775 | 0.16305 | 0.00068 | 0.015465 | 0.029919 | 0.077464 | 0.094734 | -0.003205 | 0.052481 | 0.16621 | 0.018667 | 0.030995 | -0.043332 | 0.01406 | -0.015177 | 0.024293 | 0.095813 | 0.067658 | 0.061999 | 0.033844
2828.1094 | 121.2799 | -0.93384 | 120.2225 | 0.14474 | -0.031363 | -0.021157 | -0.002124 | 0.045421 | 0.067269 | -0.039826 | 0.029595 | 0.12958 | -0.008798 | 0.017268 | -0.070797 | -0.017983 | -0.051798 | -0.003172 | 0.17679 | 0.00068 | 0.010886 | 0.029919 | 0.077464 | 0.099312 | -0.007783 | 0.061638 | 0.16163 | 0.023245 | 0.049311 | -0.038754 | 0.01406 | -0.019755 | 0.028871 | 0.10039 | 0.081393 | 0.061999 | 0.043
2829.8125 | 120.6757 | -0.9613 | 119.7968 | 0.13559 | -0.031363 | -0.016578 | -0.002124 | 0.045421 | 0.071848 | -0.035248 | 0.025017 | 0.13874 | -0.013376 | 0.012689 | -0.061641 | -0.017983 | -0.04722 | -0.00775 | 0.16763 | 0.00068 | 0.015465 | 0.029919 | 0.077464 | 0.10389 | -0.003205 | 0.05706 | 0.17079 | 0.018667 | 0.044732 | -0.029598 | 0.01406 | -0.015177 | 0.024293 | 0.086658 | 0.072237 | 0.048265 | 0.033844
2831.5781 | 121.5408 | -0.9201 | 120.5154 | 0.13101 | -0.022205 | -0.021157 | 0.002454 | 0.045421 | 0.067269 | -0.03067 | 0.025017 | 0.12501 | -0.008798 | 0.012689 | -0.070797 | -0.013405 | -0.04722 | 0.001406 | 0.16305 | 0.009838 | 0.010886 | 0.034497 | 0.077464 | 0.099312 | 0.001373 | 0.05706 | 0.15705 | 0.023245 | 0.044732 | -0.038754 | 0.018638 | -0.015177 | 0.033449 | 0.095814 | 0.072237 | 0.061999 | 0.038422
2833.2812 | 121.1975 | -0.94299 | 120.575 | 0.13559 | -0.031363 | -0.016578 | -0.002124 | 0.040843 | 0.062691 | -0.039826 | 0.025017 | 0.12958 | -0.017954 | 0.00811 | -0.070797 | -0.013405 | -0.04722 | -0.00775 | 0.16763 | 0.00068 | 0.015465 | 0.029919 | 0.072886 | 0.094734 | -0.007783 | 0.05706 | 0.16163 | 0.014089 | 0.040153 | -0.038754 | 0.018638 | -0.015177 | 0.024293 | 0.095814 | 0.072237 | 0.052843 | 0.029266
2835.0469 | 120.8588 | -0.96588 | 120.5933 | 0.13559 | -0.031363 | -0.016578 | -0.006703 | 0.040843 | 0.071848 | -0.039826 | 0.029595 | 0.13416 | -0.017954 | 0.00811 | -0.075375 | -0.013405 | -0.04722 | -0.00775 | 0.16763 | 0.00068 | 0.015465 | 0.02534 | 0.072886 | 0.10389 | -0.007783 | 0.061638 | 0.16621 | 0.014089 | 0.040153 | -0.043332 | 0.018638 | -0.015177 | 0.024293 | 0.10497 | 0.076815 | 0.057421 | 0.029266
2836.8125 | 120.8176 | -0.92468 | 119.9707 | 0.14017 | -0.031363 | -0.016578 | -0.002124 | 0.049999 | 0.067269 | -0.048983 | 0.025017 | 0.12501 | -0.008798 | 0.012689 | -0.075375 | -0.017983 | -0.04722 | 0.001406 | 0.17221 | 0.00068 | 0.015465 | 0.029919 | 0.082042 | 0.099312 | -0.01694 | 0.05706 | 0.15705 | 0.023245 | 0.044732 | -0.043332 | 0.01406 | -0.015177 | 0.033449 | 0.10039 | 0.072237 | 0.066577 | 0.038422
2838.5156 | 121.1975 | -0.95215 | 120.6253 | 0.14017 | -0.031363 | -0.021157 | -0.002124 | 0.040843 | 0.067269 | -0.039826 | 0.029595 | 0.12501 | -0.013376 | 0.012689 | -0.061641 | -0.013405 | -0.042641 | 0.001406 | 0.17221 | 0.00068 | 0.010886 | 0.029919 | 0.072886 | 0.099312 | -0.007783 | 0.061638 | 0.15705 | 0.018667 | 0.044732 | -0.029598 | 0.018638 | -0.010598 | 0.033449 | 0.091236 | 0.072236 | 0.048265 | 0.029265
2840.2188 | 120.9091 | -0.97046 | 120.6711 | 0.13559 | -0.026784 | -0.030314 | -0.002124 | 0.040843 | 0.062691 | -0.03067 | 0.01586 | 0.12501 | -0.013376 | -0.001048 | -0.070797 | -0.017983 | -0.04722 | -0.00775 | 0.16763 | 0.005259 | 0.001729 | 0.029919 | 0.072886 | 0.094734 | 0.001373 | 0.047903 | 0.15705 | 0.018667 | 0.030995 | -0.038754 | 0.01406 | -0.015177 | 0.024293 | 0.086657 | 0.06308 | 0.057421 | 0.033844
2841.9844 | 121.3165 | -0.9613 | 120.5978 | 0.13101 | -0.031363 | -0.021157 | -0.006703 | 0.040843 | 0.067269 | -0.039826 | 0.020438 | 0.12501 | -0.013376 | 0.00811 | -0.070797 | -0.022561 | -0.04722 | -0.00775 | 0.16305 | 0.00068 | 0.010886 | 0.02534 | 0.072886 | 0.099312 | -0.007783 | 0.052481 | 0.15705 | 0.018667 | 0.040153 | -0.038754 | 0.009482 | -0.015177 | 0.024293 | 0.091235 | 0.067658 | 0.057421 | 0.033844
2843.7344 | 121.0236 | -0.95673 | 120.3323 | 0.13559 | -0.035942 | -0.016578 | -0.002124 | 0.040843 | 0.067269 | -0.039826 | 0.034174 | 0.13416 | -0.013376 | 0.012689 | -0.070797 | -0.013405 | -0.04722 | -0.003172 | 0.16763 | -0.003899 | 0.015465 | 0.029919 | 0.072886 | 0.099312 | -0.007783 | 0.066217 | 0.16621 | 0.018667 | 0.044732 | -0.038754 | 0.018638 | -0.015177 | 0.028871 | 0.10497 | 0.081394 | 0.057421 | 0.033844
2845.4375 | 121.2662 | -0.97961 | 120.4926 | 0.14017 | -0.035942 | -0.016578 | -0.006703 | 0.045421 | 0.067269 | -0.039826 | 0.01586 | 0.12501 | -0.013376 | 0.012689 | -0.061641 | -0.008827 | -0.042641 | -0.00775 | 0.17221 | -0.003899 | 0.015465 | 0.02534 | 0.077464 | 0.099312 | -0.007783 | 0.047903 | 0.15705 | 0.018667 | 0.044732 | -0.029598 | 0.023216 | -0.010598 | 0.024293 | 0.077501 | 0.058501 | 0.048265 | 0.029265
2847.2031 | 121.7102 | -0.93842 | 120.6528 | 0.13101 | -0.026784 | -0.016578 | -0.006703 | 0.045421 | 0.058113 | -0.039826 | 0.020438 | 0.12043 | -0.013376 | 0.00811 | -0.066219 | -0.022561 | -0.042641 | -0.003172 | 0.16305 | 0.005259 | 0.015465 | 0.02534 | 0.077464 | 0.090156 | -0.007783 | 0.052481 | 0.15247 | 0.018667 | 0.040153 | -0.034176 | 0.009482 | -0.010598 | 0.028871 | 0.086657 | 0.063079 | 0.052843 | 0.029265
2848.9062 | 121.019 | -0.9613 | 120.0577 | 0.14017 | -0.026784 | -0.012 | -0.006703 | 0.031687 | 0.081005 | -0.044405 | 0.025017 | 0.13416 | -0.008798 | 0.012689 | -0.066219 | -0.017983 | -0.04722 | -0.016906 | 0.17221 | 0.005259 | 0.020043 | 0.02534 | 0.06373 | 0.11305 | -0.012362 | 0.05706 | 0.16621 | 0.023245 | 0.044732 | -0.034176 | 0.01406 | -0.015177 | 0.015137 | 0.091236 | 0.072237 | 0.057421 | 0.038422
2850.6562 | 121.17 | -0.98877 | 120.2225 | 0.14017 | -0.026784 | -0.021157 | -0.011281 | 0.045421 | 0.076426 | -0.039826 | 0.025017 | 0.12958 | -0.017954 | 0.017268 | -0.075375 | -0.013405 | -0.04722 | 0.010563 | 0.17221 | 0.005259 | 0.010886 | 0.020762 | 0.077464 | 0.10847 | -0.007783 | 0.05706 | 0.16163 | 0.014089 | 0.049311 | -0.043332 | 0.018638 | -0.015177 | 0.042606 | 0.10039 | 0.072237 | 0.057421 | 0.029266
2852.4219 | 121.6919 | -0.93842 | 120.7031 | 0.13559 | -0.026784 | -0.021157 | -0.011281 | 0.045421 | 0.067269 | -0.039826 | 0.025017 | 0.12958 | -0.008798 | 0.012689 | -0.061641 | -0.013405 | -0.04722 | -0.003172 | 0.16763 | 0.005259 | 0.010886 | 0.020762 | 0.077464 | 0.099312 | -0.007783 | 0.05706 | 0.16163 | 0.023245 | 0.044732 | -0.029598 | 0.018638 | -0.015177 | 0.028871 | 0.086658 | 0.072237 | 0.052843 | 0.038422
2854.1875 | 121.7194 | -0.94299 | 120.7031 | 0.13101 | -0.035942 | -0.012 | -0.002124 | 0.045421 | 0.071848 | -0.044405 | 0.029595 | 0.12043 | -0.017954 | 0.00811 | -0.061641 | -0.017983 | -0.042641 | -0.00775 | 0.16305 | -0.003899 | 0.020043 | 0.029919 | 0.077464 | 0.10389 | -0.012362 | 0.061638 | 0.15247 | 0.014089 | 0.040153 | -0.029598 | 0.01406 | -0.010598 | 0.024293 | 0.091236 | 0.072236 | 0.043687 | 0.024687
2855.875 | 121.7422 | -0.9201 | 120.5521 | 0.13559 | -0.035942 | -0.012 | -0.011281 | 0.040843 | 0.071848 | -0.03067 | 0.025017 | 0.13416 | -0.008798 | 0.012689 | -0.061641 | -0.013405 | -0.04722 | -0.00775 | 0.16763 | -0.003899 | 0.020043 | 0.020762 | 0.072886 | 0.10389 | 0.001373 | 0.05706 | 0.16621 | 0.023245 | 0.044732 | -0.029598 | 0.018638 | -0.015177 | 0.024293 | 0.086658 | 0.072237 | 0.052843 | 0.038422
2857.6562 | 121.7468 | -0.95673 | 120.6345 | 0.14017 | -0.035942 | -0.025735 | -0.002124 | 0.040843 | 0.071848 | -0.044405 | 0.025017 | 0.12501 | -0.013376 | 0.012689 | -0.070797 | -0.008827 | -0.04722 | -0.00775 | 0.17221 | -0.003899 | 0.006308 | 0.029919 | 0.072886 | 0.10389 | -0.012362 | 0.05706 | 0.15705 | 0.018667 | 0.044732 | -0.038754 | 0.023216 | -0.015177 | 0.024293 | 0.095814 | 0.072237 | 0.057421 | 0.033844
2859.3594 | 121.3806 | -0.98877 | 120.6665 | 0.13101 | -0.026784 | -0.012 | 0.007033 | 0.040843 | 0.071848 | -0.03067 | 0.034174 | 0.12958 | -0.004219 | 0.012689 | -0.075375 | -0.013405 | -0.051798 | -0.00775 | 0.16305 | 0.005259 | 0.020043 | 0.039076 | 0.072886 | 0.10389 | 0.001373 | 0.066217 | 0.16163 | 0.027824 | 0.044732 | -0.043332 | 0.018638 | -0.019755 | 0.024293 | 0.10955 | 0.085972 | 0.071156 | 0.047579
2861.125 | 121.8109 | -0.9613 | 120.7397 | 0.14017 | -0.035942 | -0.016578 | -0.011281 | 0.049999 | 0.067269 | -0.039826 | 0.020438 | 0.13416 | 0.000359 | 0.012689 | -0.070797 | -0.008827 | -0.04722 | -0.012328 | 0.17221 | -0.003899 | 0.015465 | 0.020762 | 0.082042 | 0.099312 | -0.007783 | 0.052481 | 0.16621 | 0.032402 | 0.044732 | -0.038754 | 0.023216 | -0.015177 | 0.019715 | 0.091235 | 0.067658 | 0.071156 | 0.047579
2862.8906 | 121.1929 | -0.97961 | 120.6207 | 0.14017 | -0.031363 | -0.021157 | -0.002124 | 0.045421 | 0.067269 | -0.039826 | 0.025017 | 0.12958 | -0.004219 | 0.012689 | -0.066219 | -0.017983 | -0.042641 | 0.001406 | 0.17221 | 0.00068 | 0.010886 | 0.029919 | 0.077464 | 0.099312 | -0.007783 | 0.05706 | 0.16163 | 0.027824 | 0.044732 | -0.034176 | 0.01406 | -0.010598 | 0.033449 | 0.091236 | 0.067658 | 0.062 | 0.038422
2864.5781 | 121.3211 | -0.98877 | 120.7672 | 0.13559 | -0.035942 | -0.012 | -0.002124 | 0.045421 | 0.071848 | -0.039826 | 0.025017 | 0.12043 | -0.008798 | 0.012689 | -0.061641 | -0.013405 | -0.04722 | 0.001406 | 0.16763 | -0.003899 | 0.020043 | 0.029919 | 0.077464 | 0.10389 | -0.007783 | 0.05706 | 0.15247 | 0.023245 | 0.044732 | -0.029598 | 0.018638 | -0.015177 | 0.033449 | 0.086658 | 0.072237 | 0.052843 | 0.038422
2866.3281 | 121.6782 | -0.98419 | 120.7306 | 0.13559 | -0.026784 | -0.021157 | -0.002124 | 0.036265 | 0.067269 | -0.039826 | 0.025017 | 0.12958 | -0.013376 | 0.012689 | -0.079953 | -0.017983 | -0.04722 | -0.003172 | 0.16763 | 0.005259 | 0.010886 | 0.029919 | 0.068308 | 0.099312 | -0.007783 | 0.05706 | 0.16163 | 0.018667 | 0.044732 | -0.04791 | 0.01406 | -0.015177 | 0.028871 | 0.10497 | 0.072237 | 0.066577 | 0.033844
2868.0938 | 121.2296 | -0.98877 | 120.2637 | 0.14017 | -0.031363 | -0.012 | -0.002124 | 0.040843 | 0.062691 | -0.035248 | 0.029595 | 0.12958 | -0.017954 | 0.003531 | -0.070797 | -0.017983 | -0.042641 | 0.001406 | 0.17221 | 0.00068 | 0.020043 | 0.029919 | 0.072886 | 0.094734 | -0.003205 | 0.061638 | 0.16163 | 0.014089 | 0.035574 | -0.038754 | 0.01406 | -0.010598 | 0.033449 | 0.10039 | 0.072236 | 0.052843 | 0.024687
2869.7812 | 121.8338 | -0.95673 | 120.6985 | 0.12643 | -0.035942 | -0.016578 | -0.002124 | 0.040843 | 0.067269 | -0.039826 | 0.025017 | 0.12958 | -0.008798 | 0.012689 | -0.070797 | -0.013405 | -0.042641 | 0.005985 | 0.15847 | -0.003899 | 0.015465 | 0.029919 | 0.072886 | 0.099312 | -0.007783 | 0.05706 | 0.16163 | 0.023245 | 0.044732 | -0.038754 | 0.018638 | -0.010598 | 0.038028 | 0.095814 | 0.067658 | 0.061999 | 0.033843
2871.5312 | 121.843 | -0.97504 | 120.7855 | 0.13559 | -0.031363 | -0.025735 | -0.002124 | 0.040843 | 0.067269 | -0.039826 | 0.025017 | 0.13416 | -0.013376 | 0.003531 | -0.070797 | -0.022561 | -0.042641 | 0.001406 | 0.16763 | 0.00068 | 0.006308 | 0.029919 | 0.072886 | 0.099312 | -0.007783 | 0.05706 | 0.16621 | 0.018667 | 0.035574 | -0.038754 | 0.009482 | -0.010598 | 0.033449 | 0.095814 | 0.067658 | 0.057421 | 0.029265
2873.2344 | 121.8704 | -0.96588 | 120.7809 | 0.13559 | -0.022205 | -0.016578 | -0.006703 | 0.045421 | 0.062691 | -0.048983 | 0.020438 | 0.13874 | -0.008798 | 0.012689 | -0.061641 | -0.017983 | -0.051798 | 0.001406 | 0.16763 | 0.009838 | 0.015465 | 0.02534 | 0.077464 | 0.094734 | -0.01694 | 0.052481 | 0.17079 | 0.023245 | 0.044732 | -0.029598 | 0.01406 | -0.019755 | 0.033449 | 0.082079 | 0.072236 | 0.052843 | 0.043
2874.9844 | 121.6095 | -0.99792 | 120.845 | 0.14017 | -0.035942 | -0.016578 | -0.011281 | 0.045421 | 0.071848 | -0.035248 | 0.029595 | 0.12958 | -0.013376 | 0.012689 | -0.070797 | -0.013405 | -0.04722 | -0.00775 | 0.17221 | -0.003899 | 0.015465 | 0.020762 | 0.077464 | 0.10389 | -0.003205 | 0.061638 | 0.16163 | 0.018667 | 0.044732 | -0.038754 | 0.018638 | -0.015177 | 0.024293 | 0.10039 | 0.076815 | 0.057421 | 0.033844
2876.7344 | 121.8842 | -0.96588 | 120.7764 | 0.13101 | -0.031363 | -0.021157 | -0.002124 | 0.045421 | 0.071848 | -0.039826 | 0.025017 | 0.12501 | -0.008798 | 0.00811 | -0.061641 | -0.013405 | -0.051798 | -0.003172 | 0.16305 | 0.00068 | 0.010886 | 0.029919 | 0.077464 | 0.10389 | -0.007783 | 0.05706 | 0.15705 | 0.023245 | 0.040153 | -0.029598 | 0.018638 | -0.019755 | 0.028871 | 0.086658 | 0.076815 | 0.052843 | 0.043
2878.5 | 121.7697 | -0.99792 | 120.7855 | 0.13559 | -0.026784 | -0.016578 | -0.006703 | 0.036265 | 0.071848 | -0.039826 | 0.020438 | 0.13874 | -0.008798 | 0.012689 | -0.070797 | -0.013405 | -0.04722 | 0.001406 | 0.16763 | 0.005259 | 0.015465 | 0.02534 | 0.068308 | 0.10389 | -0.007783 | 0.052481 | 0.17079 | 0.023245 | 0.044732 | -0.038754 | 0.018638 | -0.015177 | 0.033449 | 0.091235 | 0.067658 | 0.061999 | 0.038422
2880.2656 | 121.8475 | -0.97504 | 120.7809 | 0.13559 | -0.026784 | -0.021157 | -0.002124 | 0.045421 | 0.067269 | -0.035248 | 0.025017 | 0.12043 | -0.017954 | 0.017268 | -0.070797 | -0.017983 | -0.051798 | -0.00775 | 0.16763 | 0.005259 | 0.010886 | 0.029919 | 0.077464 | 0.099312 | -0.003205 | 0.05706 | 0.15247 | 0.014089 | 0.049311 | -0.038754 | 0.01406 | -0.019755 | 0.024293 | 0.095814 | 0.076815 | 0.052843 | 0.033844
2882.0156 | 121.9254 | -0.97504 | 120.7809 | 0.13101 | -0.031363 | -0.021157 | -0.002124 | 0.054577 | 0.062691 | -0.044405 | 0.020438 | 0.13416 | -0.008798 | 0.003531 | -0.066219 | -0.008827 | -0.051798 | 0.001406 | 0.16305 | 0.00068 | 0.010886 | 0.029919 | 0.08662 | 0.094734 | -0.012362 | 0.052481 | 0.16621 | 0.023245 | 0.035574 | -0.034176 | 0.023216 | -0.019755 | 0.033449 | 0.086657 | 0.072236 | 0.057421 | 0.043
2883.7812 | 121.9116 | -0.97046 | 120.8084 | 0.13101 | -0.026784 | -0.012 | -0.002124 | 0.045421 | 0.067269 | -0.039826 | 0.029595 | 0.12958 | -0.013376 | 0.012689 | -0.070797 | -0.017983 | -0.051798 | -0.00775 | 0.16305 | 0.005259 | 0.020043 | 0.029919 | 0.077464 | 0.099312 | -0.007783 | 0.061638 | 0.16163 | 0.018667 | 0.044732 | -0.038754 | 0.01406 | -0.019755 | 0.024293 | 0.10039 | 0.081393 | 0.057421 | 0.038422
2885.5 | 121.788 | -1.0071 | 120.7443 | 0.13559 | -0.026784 | -0.021157 | -0.002124 | 0.049999 | 0.067269 | -0.039826 | 0.029595 | 0.12958 | -0.013376 | 0.00811 | -0.066219 | -0.017983 | -0.051798 | -0.00775 | 0.16763 | 0.005259 | 0.010886 | 0.029919 | 0.082042 | 0.099312 | -0.007783 | 0.061638 | 0.16163 | 0.018667 | 0.040153 | -0.034176 | 0.01406 | -0.019755 | 0.024293 | 0.095814 | 0.081393 | 0.052843 | 0.038422
2887.25 | 121.875 | -0.99792 | 120.845 | 0.13101 | -0.031363 | -0.021157 | -0.006703 | 0.040843 | 0.071848 | -0.035248 | 0.025017 | 0.12958 | -0.013376 | 0.00811 | -0.061641 | -0.013405 | -0.04722 | -0.00775 | 0.16305 | 0.00068 | 0.010886 | 0.02534 | 0.072886 | 0.10389 | -0.003205 | 0.05706 | 0.16163 | 0.018667 | 0.040153 | -0.029598 | 0.018638 | -0.015177 | 0.024293 | 0.086658 | 0.072237 | 0.048265 | 0.033844
2888.9375 | 90.3076 | -0.11902 | 89.5386 | 0.13559 | -0.035942 | -0.016578 | -0.006703 | 0.049999 | 0.067269 | -0.035248 | 0.029595 | 0.12958 | -0.008798 | 0.00811 | -0.070797 | -0.022561 | -0.051798 | -0.00775 | 0.16763 | -0.003899 | 0.015465 | 0.02534 | 0.082042 | 0.099312 | -0.003205 | 0.061638 | 0.16163 | 0.023245 | 0.040153 | -0.038754 | 0.009482 | -0.019755 | 0.024293 | 0.10039 | 0.081393 | 0.061999 | 0.043
2890.6875 | 118.2678 | -0.68207 | 95.6726 | 0.13559 | -0.026784 | -0.021157 | -0.01586 | 0.040843 | 0.071848 | -0.035248 | 0.029595 | 0.12958 | -0.004219 | 0.00811 | -0.075375 | -0.013405 | -0.042641 | -0.00775 | 0.16763 | 0.005259 | 0.010886 | 0.016183 | 0.072886 | 0.10389 | -0.003205 | 0.061638 | 0.16163 | 0.027824 | 0.040153 | -0.043332 | 0.018638 | -0.010598 | 0.024293 | 0.10497 | 0.072236 | 0.071156 | 0.038422
2892.4375 | 94.8257 | -0.98877 | 92.2897 | 0.13559 | -0.031363 | -0.016578 | -0.006703 | 0.040843 | 0.081005 | -0.035248 | 0.029595 | 0.12043 | -0.008798 | 0.012689 | -0.066219 | -0.013405 | -0.042641 | -0.003172 | 0.16763 | 0.00068 | 0.015465 | 0.02534 | 0.072886 | 0.11305 | -0.003205 | 0.061638 | 0.15247 | 0.023245 | 0.044732 | -0.034176 | 0.018638 | -0.010598 | 0.028871 | 0.095814 | 0.072236 | 0.057421 | 0.033843
2894.2031 | 121.4127 | -22.7417 | 88.3667 | 0.13101 | -0.035942 | -0.021157 | 0.002454 | 0.036265 | 0.067269 | -0.03067 | 0.025017 | 0.12958 | -0.008798 | 0.012689 | -0.070797 | -0.022561 | -0.051798 | -0.003172 | 0.16305 | -0.003899 | 0.010886 | 0.034497 | 0.068308 | 0.099312 | 0.001373 | 0.05706 | 0.16163 | 0.023245 | 0.044732 | -0.038754 | 0.009482 | -0.019755 | 0.028871 | 0.095814 | 0.076815 | 0.061999 | 0.043
2895.9062 | 121.9986 | -20.4483 | 88.0554 | 0.13101 | -0.031363 | -0.025735 | -0.006703 | 0.040843 | 0.067269 | -0.035248 | 0.025017 | 0.12958 | -0.013376 | 0.00811 | -0.066219 | -0.017983 | -0.04722 | -0.012328 | 0.16305 | 0.00068 | 0.006308 | 0.02534 | 0.072886 | 0.099312 | -0.003205 | 0.05706 | 0.16163 | 0.018667 | 0.040153 | -0.034176 | 0.01406 | -0.015177 | 0.019715 | 0.091236 | 0.072237 | 0.052843 | 0.033844
2897.6719 | 121.9345 | -0.86975 | 115.4388 | 0.14017 | -0.031363 | -0.016578 | -0.002124 | 0.045421 | 0.071848 | -0.039826 | 0.029595 | 0.12501 | -0.017954 | 0.021847 | -0.070797 | -0.017983 | -0.051798 | -0.016906 | 0.17221 | 0.00068 | 0.015465 | 0.029919 | 0.077464 | 0.10389 | -0.007783 | 0.061638 | 0.15705 | 0.014089 | 0.05389 | -0.038754 | 0.01406 | -0.019755 | 0.015137 | 0.10039 | 0.081393 | 0.052843 | 0.033844
2899.4219 | 121.9208 | -4.8843 | 116.5604 | 0.13101 | -0.031363 | -0.021157 | -0.006703 | 0.049999 | 0.071848 | -0.039826 | 0.029595 | 0.12958 | -0.008798 | 0.012689 | -0.075375 | -0.017983 | -0.051798 | -0.012328 | 0.16305 | 0.00068 | 0.010886 | 0.02534 | 0.082042 | 0.10389 | -0.007783 | 0.061638 | 0.16163 | 0.023245 | 0.044732 | -0.043332 | 0.01406 | -0.019755 | 0.019715 | 0.10497 | 0.081393 | 0.066577 | 0.043
2901.1719 | 121.6873 | -120.195 | 1.2405 | 0.14932 | -0.026784 | -0.012 | -0.011281 | 0.049999 | 0.071848 | -0.039826 | 0.025017 | 0.13416 | -0.004219 | 0.017268 | -0.075375 | -0.013405 | -0.04722 | -0.016906 | 0.18136 | 0.005259 | 0.020043 | 0.020762 | 0.082042 | 0.10389 | -0.007783 | 0.05706 | 0.16621 | 0.027824 | 0.049311 | -0.043332 | 0.018638 | -0.015177 | 0.015137 | 0.10039 | 0.072237 | 0.071156 | 0.043001
2902.9375 | 121.7285 | -120.1721 | 1.2314 | 0.14017 | -0.026784 | -0.021157 | -0.006703 | 0.049999 | 0.071848 | -0.039826 | 0.020438 | 0.12501 | -0.017954 | 0.012689 | -0.075375 | -0.017983 | -0.04722 | -0.012328 | 0.17221 | 0.005259 | 0.010886 | 0.02534 | 0.082042 | 0.10389 | -0.007783 | 0.052481 | 0.15705 | 0.014089 | 0.044732 | -0.043332 | 0.01406 | -0.015177 | 0.019715 | 0.095813 | 0.067658 | 0.057421 | 0.029266
2904.625 | 121.5683 | -120.1859 | 1.2405 | 0.14017 | -0.017627 | -0.012 | 0.002454 | 0.045421 | 0.076426 | -0.035248 | 0.029595 | 0.13416 | -0.004219 | 0.012689 | -0.070797 | -0.017983 | -0.051798 | -0.016906 | 0.17221 | 0.014416 | 0.020043 | 0.034497 | 0.077464 | 0.10847 | -0.003205 | 0.061638 | 0.16621 | 0.027824 | 0.044732 | -0.038754 | 0.01406 | -0.019755 | 0.015137 | 0.10039 | 0.081393 | 0.066578 | 0.047579
2906.3125 | 121.6003 | -120.163 | 1.1993 | 0.13559 | -0.026784 | -0.012 | -0.002124 | 0.045421 | 0.062691 | -0.039826 | 0.029595 | 0.13416 | -0.004219 | 0.017268 | -0.066219 | -0.017983 | -0.04722 | -0.016906 | 0.16763 | 0.005259 | 0.020043 | 0.029919 | 0.077464 | 0.094734 | -0.007783 | 0.061638 | 0.16621 | 0.027824 | 0.049311 | -0.034176 | 0.01406 | -0.015177 | 0.015137 | 0.095814 | 0.076815 | 0.062 | 0.043001
2908.0781 | 121.55 | -120.1309 | 1.2039 | 0.13559 | -0.026784 | -0.016578 | -0.011281 | 0.040843 | 0.071848 | -0.035248 | 0.034174 | 0.13416 | -0.004219 | 0.021847 | -0.070797 | -0.017983 | -0.060955 | -0.012328 | 0.16763 | 0.005259 | 0.015465 | 0.020762 | 0.072886 | 0.10389 | -0.003205 | 0.066217 | 0.16621 | 0.027824 | 0.05389 | -0.038754 | 0.01406 | -0.028912 | 0.019715 | 0.10497 | 0.095129 | 0.066578 | 0.056736
2909.8281 | 121.5134 | -120.1401 | 1.2039 | 0.14017 | -0.031363 | -0.016578 | -0.006703 | 0.040843 | 0.076426 | -0.039826 | 0.025017 | 0.12958 | -0.008798 | 0.017268 | -0.070797 | -0.008827 | -0.04722 | -0.016906 | 0.17221 | 0.00068 | 0.015465 | 0.02534 | 0.072886 | 0.10847 | -0.007783 | 0.05706 | 0.16163 | 0.023245 | 0.049311 | -0.038754 | 0.023216 | -0.015177 | 0.015137 | 0.095814 | 0.072237 | 0.061999 | 0.038422
2911.5781 | 121.5271 | -120.1035 | 1.2085 | 0.14017 | -0.031363 | -0.021157 | -0.006703 | 0.045421 | 0.071848 | -0.035248 | 0.029595 | 0.12958 | -0.004219 | 0.017268 | -0.17152 | -0.10497 | -0.17084 | -0.1222 | 0.17221 | 0.00068 | 0.010886 | 0.02534 | 0.077464 | 0.10389 | -0.003205 | 0.061638 | 0.16163 | 0.027824 | 0.049311 | -0.13947 | -0.072923 | -0.13879 | -0.090161 | 0.20111 | 0.20043 | 0.1673 | 0.16662
2913.2812 | 121.5134 | -120.0714 | 1.2039 | 0.14474 | -0.026784 | -0.012 | -0.002124 | 0.045421 | 0.076426 | -0.035248 | 0.029595 | 0.13416 | 0.000359 | 0.012689 | -0.070797 | -0.022561 | -0.042641 | -0.012328 | 0.17679 | 0.005259 | 0.020043 | 0.029919 | 0.077464 | 0.10847 | -0.003205 | 0.061638 | 0.16621 | 0.032402 | 0.044732 | -0.038754 | 0.009482 | -0.010598 | 0.019715 | 0.10039 | 0.072236 | 0.071156 | 0.043
2915.0312 | 121.344 | -120.0989 | 1.2268 | 0.13559 | -0.031363 | -0.016578 | -0.002124 | 0.045421 | 0.067269 | -0.035248 | 0.029595 | 0.12958 | -0.008798 | 0.012689 | -0.061641 | -0.017983 | -0.04722 | -0.00775 | 0.16763 | 0.00068 | 0.015465 | 0.029919 | 0.077464 | 0.099312 | -0.003205 | 0.061638 | 0.16163 | 0.023245 | 0.044732 | -0.029598 | 0.01406 | -0.015177 | 0.024293 | 0.091236 | 0.076815 | 0.052843 | 0.038422
2916.7344 | 121.431 | -120.0348 | 1.2131 | 0.14017 | -0.026784 | -0.016578 | -0.006703 | 0.045421 | 0.071848 | -0.035248 | 0.029595 | 0.12958 | -0.004219 | 0.012689 | -0.075375 | -0.013405 | -0.04722 | -0.016906 | 0.17221 | 0.005259 | 0.015465 | 0.02534 | 0.077464 | 0.10389 | -0.003205 | 0.061638 | 0.16163 | 0.027824 | 0.044732 | -0.043332 | 0.018638 | -0.015177 | 0.015137 | 0.10497 | 0.076815 | 0.071156 | 0.043001
2918.5 | 121.3715 | -120.0302 | 1.2314 | 0.14474 | -0.026784 | -0.021157 | 0.002454 | 0.054577 | 0.076426 | -0.035248 | 0.029595 | 0.12958 | 0.000359 | 0.017268 | -0.066219 | -0.013405 | -0.042641 | -0.016906 | 0.17679 | 0.005259 | 0.010886 | 0.034497 | 0.08662 | 0.10847 | -0.003205 | 0.061638 | 0.16163 | 0.032402 | 0.049311 | -0.034176 | 0.018638 | -0.010598 | 0.015137 | 0.095814 | 0.072236 | 0.066578 | 0.043
2920.2031 | 121.4127 | -119.9936 | 1.1993 | 0.13101 | -0.035942 | -0.021157 | 0.002454 | 0.045421 | 0.071848 | -0.03067 | 0.029595 | 0.13416 | -0.004219 | 0.017268 | -0.079953 | -0.017983 | -0.04722 | -0.016906 | 0.16305 | -0.003899 | 0.010886 | 0.034497 | 0.077464 | 0.10389 | 0.001373 | 0.061638 | 0.16621 | 0.027824 | 0.049311 | -0.04791 | 0.01406 | -0.015177 | 0.015137 | 0.10955 | 0.076815 | 0.075734 | 0.043001
2921.9688 | 121.3806 | -120.0073 | 1.181 | 0.14017 | -0.031363 | -0.016578 | -0.006703 | 0.045421 | 0.071848 | -0.044405 | 0.020438 | 0.13416 | -0.017954 | 0.012689 | -0.079953 | -0.017983 | -0.051798 | -0.012328 | 0.17221 | 0.00068 | 0.015465 | 0.02534 | 0.077464 | 0.10389 | -0.012362 | 0.052481 | 0.16621 | 0.014089 | 0.044732 | -0.04791 | 0.01406 | -0.019755 | 0.019715 | 0.10039 | 0.072236 | 0.061999 | 0.033844
2923.6719 | 121.3303 | -120.0027 | 1.2314 | 0.14017 | -0.031363 | -0.012 | -0.002124 | 0.049999 | 0.076426 | -0.035248 | 0.034174 | 0.13416 | -0.013376 | 0.017268 | -0.070797 | -0.022561 | -0.04722 | -0.016906 | 0.17221 | 0.00068 | 0.020043 | 0.029919 | 0.082042 | 0.10847 | -0.003205 | 0.066217 | 0.16621 | 0.018667 | 0.049311 | -0.038754 | 0.009482 | -0.015177 | 0.015137 | 0.10497 | 0.081394 | 0.057421 | 0.033844
2925.4219 | 121.2158 | -120.0119 | 1.2222 | 0.13559 | -0.035942 | -0.016578 | -0.002124 | 0.045421 | 0.076426 | -0.039826 | 0.020438 | 0.13874 | -0.004219 | 0.017268 | -0.070797 | -0.013405 | -0.04722 | -0.016906 | 0.16763 | -0.003899 | 0.015465 | 0.029919 | 0.077464 | 0.10847 | -0.007783 | 0.052481 | 0.17079 | 0.027824 | 0.049311 | -0.038754 | 0.018638 | -0.015177 | 0.015137 | 0.091235 | 0.067658 | 0.066578 | 0.043001
2927.1719 | 121.1609 | -119.9799 | 1.2222 | 0.13101 | -0.035942 | -0.016578 | -0.006703 | 0.045421 | 0.076426 | -0.035248 | 0.029595 | 0.13416 | -0.004219 | 0.012689 | -0.070797 | -0.013405 | -0.04722 | -0.016906 | 0.16305 | -0.003899 | 0.015465 | 0.02534 | 0.077464 | 0.10847 | -0.003205 | 0.061638 | 0.16621 | 0.027824 | 0.044732 | -0.038754 | 0.018638 | -0.015177 | 0.015137 | 0.10039 | 0.076815 | 0.066578 | 0.043001
2928.875 | 121.3531 | -119.9524 | 1.1856 | 0.13559 | -0.031363 | -0.025735 | -0.011281 | 0.045421 | 0.071848 | -0.044405 | 0.025017 | 0.12958 | -0.013376 | 0.012689 | -0.079953 | -0.013405 | -0.042641 | -0.016906 | 0.16763 | 0.00068 | 0.006308 | 0.020762 | 0.077464 | 0.10389 | -0.012362 | 0.05706 | 0.16163 | 0.018667 | 0.044732 | -0.04791 | 0.018638 | -0.010598 | 0.015137 | 0.10497 | 0.067658 | 0.066577 | 0.029265
2930.6406 | 121.344 | -119.9524 | 1.1948 | 0.13559 | -0.031363 | -0.021157 | -0.006703 | 0.045421 | 0.067269 | -0.039826 | 0.038752 | 0.13416 | -0.008798 | 0.017268 | -0.075375 | -0.013405 | -0.042641 | -0.021484 | 0.16763 | 0.00068 | 0.010886 | 0.02534 | 0.077464 | 0.099312 | -0.007783 | 0.070795 | 0.16621 | 0.023245 | 0.049311 | -0.043332 | 0.018638 | -0.010598 | 0.010559 | 0.11413 | 0.081393 | 0.066577 | 0.033843
2932.4062 | 121.344 | -119.9249 | 1.1948 | 0.14017 | -0.026784 | -0.016578 | -0.006703 | 0.040843 | 0.071848 | -0.035248 | 0.029595 | 0.14332 | 0.000359 | 0.017268 | -0.070797 | -0.017983 | -0.04722 | -0.00775 | 0.17221 | 0.005259 | 0.015465 | 0.02534 | 0.072886 | 0.10389 | -0.003205 | 0.061638 | 0.17536 | 0.032402 | 0.049311 | -0.038754 | 0.01406 | -0.015177 | 0.024293 | 0.10039 | 0.076815 | 0.071156 | 0.047579
2934.1719 | 121.344 | -119.9249 | 1.2085 | 0.14017 | -0.031363 | -0.021157 | -0.011281 | 0.049999 | 0.076426 | -0.039826 | 0.029595 | 0.13416 | -0.008798 | 0.012689 | -0.070797 | -0.022561 | -0.042641 | -0.016906 | 0.17221 | 0.00068 | 0.010886 | 0.020762 | 0.082042 | 0.10847 | -0.007783 | 0.061638 | 0.16621 | 0.023245 | 0.044732 | -0.038754 | 0.009482 | -0.010598 | 0.015137 | 0.10039 | 0.072236 | 0.061999 | 0.033843
2935.9375 | 121.3028 | -119.9158 | 1.2039 | 0.14017 | -0.026784 | -0.012 | -0.006703 | 0.040843 | 0.071848 | -0.048983 | 0.029595 | 0.12958 | -0.008798 | 0.012689 | -0.075375 | -0.008827 | -0.042641 | -0.021484 | 0.17221 | 0.005259 | 0.020043 | 0.02534 | 0.072886 | 0.10389 | -0.01694 | 0.061638 | 0.16163 | 0.023245 | 0.044732 | -0.043332 | 0.023216 | -0.010598 | 0.010559 | 0.10497 | 0.072236 | 0.066577 | 0.033843
2937.6406 | 121.3028 | -119.8883 | 1.2085 | 0.14017 | -0.040521 | -0.016578 | -0.011281 | 0.040843 | 0.071848 | -0.039826 | 0.029595 | 0.13416 | -0.017954 | 0.017268 | -0.079953 | -0.022561 | -0.056376 | -0.021484 | 0.17221 | -0.008478 | 0.015465 | 0.020762 | 0.072886 | 0.10389 | -0.007783 | 0.061638 | 0.16621 | 0.014089 | 0.049311 | -0.04791 | 0.009482 | -0.024333 | 0.010559 | 0.10955 | 0.085971 | 0.061999 | 0.038422
2939.4062 | 121.2158 | -119.6594 | 1.4282 | 0.13559 | -0.031363 | -0.016578 | -0.006703 | 0.049999 | 0.067269 | -0.039826 | 0.025017 | 0.12958 | -0.013376 | 0.00811 | -0.075375 | -0.022561 | -0.051798 | -0.016906 | 0.16763 | 0.00068 | 0.015465 | 0.02534 | 0.082042 | 0.099312 | -0.007783 | 0.05706 | 0.16163 | 0.018667 | 0.040153 | -0.043332 | 0.009482 | -0.019755 | 0.015137 | 0.10039 | 0.076815 | 0.061999 | 0.038422
2941.1562 | 121.5271 | -0.68207 | 120.5338 | 0.13559 | -0.035942 | -0.021157 | -0.006703 | 0.045421 | 0.076426 | -0.044405 | 0.029595 | 0.12958 | -0.004219 | 0.017268 | -0.075375 | -0.017983 | -0.051798 | -0.021484 | 0.16763 | -0.003899 | 0.010886 | 0.02534 | 0.077464 | 0.10847 | -0.012362 | 0.061638 | 0.16163 | 0.027824 | 0.049311 | -0.043332 | 0.01406 | -0.019755 | 0.010559 | 0.10497 | 0.081393 | 0.071156 | 0.047579
2942.9062 | 121.6278 | -0.45776 | 120.8954 | 0.14017 | -0.035942 | -0.021157 | -0.020438 | 0.045421 | 0.071848 | -0.039826 | 0.029595 | 0.12958 | -0.013376 | 0.012689 | -0.070797 | -0.013405 | -0.04722 | -0.021484 | 0.17221 | -0.003899 | 0.010886 | 0.011605 | 0.077464 | 0.10389 | -0.007783 | 0.061638 | 0.16163 | 0.018667 | 0.044732 | -0.038754 | 0.018638 | -0.015177 | 0.010559 | 0.10039 | 0.076815 | 0.057421 | 0.033844
2944.6094 | 115.9332 | -0.22888 | 115.8691 | 0.13559 | -0.026784 | -0.016578 | -0.006703 | 0.059155 | 0.076426 | -0.035248 | 0.029595 | 0.12958 | -0.008798 | 0.012689 | -0.075375 | -0.013405 | -0.04722 | -0.016906 | 0.16763 | 0.005259 | 0.015465 | 0.02534 | 0.091198 | 0.10847 | -0.003205 | 0.061638 | 0.16163 | 0.023245 | 0.044732 | -0.043332 | 0.018638 | -0.015177 | 0.015137 | 0.10497 | 0.076815 | 0.066577 | 0.038422
2946.375 | 120.9961 | -0.59967 | 120.4514 | 0.13559 | -0.031363 | -0.016578 | -0.011281 | 0.049999 | 0.071848 | -0.039826 | 0.029595 | 0.13416 | -0.008798 | 0.012689 | -0.075375 | -0.008827 | -0.051798 | -0.012328 | 0.16763 | 0.00068 | 0.015465 | 0.020762 | 0.082042 | 0.10389 | -0.007783 | 0.061638 | 0.16621 | 0.023245 | 0.044732 | -0.043332 | 0.023216 | -0.019755 | 0.019715 | 0.10497 | 0.081393 | 0.066577 | 0.043
2948.1406 | 121.1472 | -0.52643 | 120.5292 | 0.13101 | -0.031363 | -0.016578 | 0.002454 | 0.040843 | 0.071848 | -0.035248 | 0.025017 | 0.13416 | -0.013376 | 0.00811 | -0.075375 | -0.013405 | -0.04722 | -0.016906 | 0.16305 | 0.00068 | 0.015465 | 0.034497 | 0.072886 | 0.10389 | -0.003205 | 0.05706 | 0.16621 | 0.018667 | 0.040153 | -0.043332 | 0.018638 | -0.015177 | 0.015137 | 0.10039 | 0.072237 | 0.061999 | 0.033844
2949.8438 | 121.2158 | -0.52643 | 120.7764 | 0.13559 | -0.035942 | -0.016578 | -0.006703 | 0.049999 | 0.067269 | -0.035248 | 0.034174 | 0.12958 | -0.008798 | 0.012689 | -0.079953 | -0.017983 | -0.04722 | -0.016906 | 0.16763 | -0.003899 | 0.015465 | 0.02534 | 0.082042 | 0.099312 | -0.003205 | 0.066217 | 0.16163 | 0.023245 | 0.044732 | -0.04791 | 0.01406 | -0.015177 | 0.015137 | 0.11413 | 0.081394 | 0.071155 | 0.038422
2951.6094 | 120.8267 | -0.52643 | 120.8405 | 0.13101 | -0.031363 | -0.021157 | -0.006703 | 0.045421 | 0.071848 | -0.044405 | 0.029595 | 0.12958 | -0.017954 | 0.012689 | -0.079953 | -0.017983 | -0.04722 | -0.00775 | 0.16305 | 0.00068 | 0.010886 | 0.02534 | 0.077464 | 0.10389 | -0.012362 | 0.061638 | 0.16163 | 0.014089 | 0.044732 | -0.04791 | 0.01406 | -0.015177 | 0.024293 | 0.10955 | 0.076815 | 0.061999 | 0.029266
2953.375 | 120.8771 | -0.48065 | 120.7993 | 0.13559 | -0.031363 | -0.025735 | -0.002124 | 0.045421 | 0.067269 | -0.039826 | 0.034174 | 0.13416 | -0.008798 | 0.00811 | -0.075375 | -0.004248 | -0.04722 | -0.012328 | 0.16763 | 0.00068 | 0.006308 | 0.029919 | 0.077464 | 0.099312 | -0.007783 | 0.066217 | 0.16621 | 0.023245 | 0.040153 | -0.043332 | 0.027795 | -0.015177 | 0.019715 | 0.10955 | 0.081394 | 0.066577 | 0.038422
2955.1406 | 121.4218 | -0.46692 | 120.8771 | 0.14017 | -0.035942 | -0.016578 | -0.006703 | 0.040843 | 0.071848 | -0.039826 | 0.029595 | 0.12958 | -0.013376 | 0.00811 | -0.075375 | -0.013405 | -0.04722 | -0.016906 | 0.17221 | -0.003899 | 0.015465 | 0.02534 | 0.072886 | 0.10389 | -0.007783 | 0.061638 | 0.16163 | 0.018667 | 0.040153 | -0.043332 | 0.018638 | -0.015177 | 0.015137 | 0.10497 | 0.076815 | 0.061999 | 0.033844
2956.8906 | 121.0373 | -0.48065 | 120.7672 | 0.13559 | -0.035942 | -0.016578 | -0.002124 | 0.045421 | 0.071848 | -0.039826 | 0.029595 | 0.13416 | -0.004219 | 0.003531 | -0.075375 | -0.017983 | -0.042641 | -0.016906 | 0.16763 | -0.003899 | 0.015465 | 0.029919 | 0.077464 | 0.10389 | -0.007783 | 0.061638 | 0.16621 | 0.027824 | 0.035574 | -0.043332 | 0.01406 | -0.010598 | 0.015137 | 0.10497 | 0.072236 | 0.071156 | 0.038422
2958.5938 | 120.9091 | -0.48981 | 120.4834 | 0.13101 | -0.026784 | -0.021157 | -0.002124 | 0.040843 | 0.071848 | -0.035248 | 0.020438 | 0.12958 | -0.013376 | 0.012689 | -0.079953 | -0.017983 | -0.04722 | -0.00775 | 0.16305 | 0.005259 | 0.010886 | 0.029919 | 0.072886 | 0.10389 | -0.003205 | 0.052481 | 0.16163 | 0.018667 | 0.044732 | -0.04791 | 0.01406 | -0.015177 | 0.024293 | 0.10039 | 0.067658 | 0.066577 | 0.033844
2960.2969 | 120.8176 | -0.4715 | 120.7626 | 0.13101 | -0.026784 | -0.016578 | -0.011281 | 0.049999 | 0.071848 | -0.039826 | 0.029595 | 0.12958 | -0.008798 | 0.00811 | -0.070797 | -0.008827 | -0.042641 | -0.021484 | 0.16305 | 0.005259 | 0.015465 | 0.020762 | 0.082042 | 0.10389 | -0.007783 | 0.061638 | 0.16163 | 0.023245 | 0.040153 | -0.038754 | 0.023216 | -0.010598 | 0.010559 | 0.10039 | 0.072236 | 0.061999 | 0.033843
2962.0469 | 121.4035 | -0.42114 | 121.0098 | 0.14474 | -0.031363 | -0.021157 | -0.006703 | 0.040843 | 0.071848 | -0.039826 | 0.029595 | 0.12958 | -0.013376 | 0.012689 | -0.075375 | -0.013405 | -0.042641 | -0.016906 | 0.17679 | 0.00068 | 0.010886 | 0.02534 | 0.072886 | 0.10389 | -0.007783 | 0.061638 | 0.16163 | 0.018667 | 0.044732 | -0.043332 | 0.018638 | -0.010598 | 0.015137 | 0.10497 | 0.072236 | 0.061999 | 0.029265
2963.8125 | 120.7581 | -0.46692 | 120.4834 | 0.14017 | -0.035942 | -0.016578 | -0.006703 | 0.040843 | 0.067269 | -0.035248 | 0.029595 | 0.13416 | -0.004219 | 0.012689 | -0.079953 | -0.008827 | -0.056376 | -0.012328 | 0.17221 | -0.003899 | 0.015465 | 0.02534 | 0.072886 | 0.099312 | -0.003205 | 0.061638 | 0.16621 | 0.027824 | 0.044732 | -0.04791 | 0.023216 | -0.024333 | 0.019715 | 0.10955 | 0.085971 | 0.075734 | 0.052157
2965.5625 | 109.5978 | -0.38452 | 120.3873 | 0.13101 | -0.031363 | -0.025735 | -0.006703 | 0.049999 | 0.067269 | -0.044405 | 0.025017 | 0.13416 | -0.013376 | 0.017268 | -0.070797 | -0.022561 | -0.042641 | -0.016906 | 0.16305 | 0.00068 | 0.006308 | 0.02534 | 0.082042 | 0.099312 | -0.012362 | 0.05706 | 0.16621 | 0.018667 | 0.049311 | -0.038754 | 0.009482 | -0.010598 | 0.015137 | 0.095814 | 0.067658 | 0.057421 | 0.029265
2967.3125 | 120.8633 | -0.50354 | 121.0419 | 0.14017 | -0.035942 | -0.016578 | -0.006703 | 0.036265 | 0.076426 | -0.03067 | 0.034174 | 0.12958 | -0.004219 | 0.012689 | -0.075375 | -0.013405 | -0.051798 | -0.012328 | 0.17221 | -0.003899 | 0.015465 | 0.02534 | 0.068308 | 0.10847 | 0.001373 | 0.066217 | 0.16163 | 0.027824 | 0.044732 | -0.043332 | 0.018638 | -0.019755 | 0.019715 | 0.10955 | 0.085972 | 0.071156 | 0.047579
2969.0781 | 120.9778 | -0.48065 | 120.3735 | 0.13559 | -0.031363 | -0.012 | -0.006703 | 0.045421 | 0.076426 | -0.035248 | 0.020438 | 0.13416 | -0.008798 | 0.012689 | -0.070797 | -0.017983 | -0.04722 | -0.00775 | 0.16763 | 0.00068 | 0.020043 | 0.02534 | 0.077464 | 0.10847 | -0.003205 | 0.052481 | 0.16621 | 0.023245 | 0.044732 | -0.038754 | 0.01406 | -0.015177 | 0.024293 | 0.091235 | 0.067658 | 0.061999 | 0.038422
2970.8438 | 121.4996 | -0.45776 | 121.1105 | 0.13559 | -0.031363 | -0.021157 | -0.020438 | 0.040843 | 0.067269 | -0.039826 | 0.029595 | 0.13416 | -0.008798 | 0.00811 | -0.070797 | -0.017983 | -0.056376 | -0.016906 | 0.16763 | 0.00068 | 0.010886 | 0.011605 | 0.072886 | 0.099312 | -0.007783 | 0.061638 | 0.16621 | 0.023245 | 0.040153 | -0.038754 | 0.01406 | -0.024333 | 0.015137 | 0.10039 | 0.085971 | 0.061999 | 0.047578
2972.6094 | 121.8109 | -0.43945 | 120.6848 | 0.13101 | -0.031363 | -0.025735 | -0.006703 | 0.040843 | 0.067269 | -0.026092 | 0.029595 | 0.13416 | -0.004219 | 0.012689 | -0.075375 | -0.008827 | -0.04722 | -0.016906 | 0.16305 | 0.00068 | 0.006308 | 0.02534 | 0.072886 | 0.099312 | 0.005951 | 0.061638 | 0.16621 | 0.027824 | 0.044732 | -0.043332 | 0.023216 | -0.015177 | 0.015137 | 0.10497 | 0.076815 | 0.071156 | 0.043001
2974.3594 | 121.6873 | -0.45319 | 121.138 | 0.13101 | -0.031363 | -0.021157 | -0.006703 | 0.045421 | 0.067269 | -0.044405 | 0.025017 | 0.13416 | -0.004219 | 0.00811 | -0.075375 | -0.017983 | -0.04722 | -0.016906 | 0.16305 | 0.00068 | 0.010886 | 0.02534 | 0.077464 | 0.099312 | -0.012362 | 0.05706 | 0.16621 | 0.027824 | 0.040153 | -0.043332 | 0.01406 | -0.015177 | 0.015137 | 0.10039 | 0.072237 | 0.071156 | 0.043001
2976.0781 | 121.7285 | -0.45319 | 120.9457 | 0.13559 | -0.026784 | -0.021157 | -0.011281 | 0.045421 | 0.067269 | -0.039826 | 0.020438 | 0.13416 | -0.004219 | 0.00811 | -0.070797 | -0.008827 | -0.042641 | -0.021484 | 0.16763 | 0.005259 | 0.010886 | 0.020762 | 0.077464 | 0.099312 | -0.007783 | 0.052481 | 0.16621 | 0.027824 | 0.040153 | -0.038754 | 0.023216 | -0.010598 | 0.010559 | 0.091235 | 0.063079 | 0.066578 | 0.038422
2977.8281 | 121.1609 | -0.46234 | 121.0144 | 0.14017 | -0.031363 | -0.012 | -0.002124 | 0.049999 | 0.071848 | -0.039826 | 0.025017 | 0.12958 | -0.004219 | 0.017268 | -0.070797 | -0.013405 | -0.042641 | -0.016906 | 0.17221 | 0.00068 | 0.020043 | 0.029919 | 0.082042 | 0.10389 | -0.007783 | 0.05706 | 0.16163 | 0.027824 | 0.049311 | -0.038754 | 0.018638 | -0.010598 | 0.015137 | 0.095814 | 0.067658 | 0.066578 | 0.038422
2979.5938 | 121.7194 | -0.4715 | 120.9229 | 0.13559 | -0.035942 | -0.021157 | -0.011281 | 0.045421 | 0.062691 | -0.039826 | 0.034174 | 0.13416 | -0.008798 | 0.017268 | -0.075375 | -0.013405 | -0.051798 | -0.016906 | 0.16763 | -0.003899 | 0.010886 | 0.020762 | 0.077464 | 0.094734 | -0.007783 | 0.066217 | 0.16621 | 0.023245 | 0.049311 | -0.043332 | 0.018638 | -0.019755 | 0.015137 | 0.10955 | 0.085972 | 0.066577 | 0.043
2981.3438 | 121.7102 | -0.50354 | 121.138 | 0.14017 | -0.031363 | -0.021157 | -0.006703 | 0.045421 | 0.071848 | -0.039826 | 0.034174 | 0.13874 | -0.008798 | 0.012689 | -0.066219 | -0.013405 | -0.04722 | -0.00775 | 0.17221 | 0.00068 | 0.010886 | 0.02534 | 0.077464 | 0.10389 | -0.007783 | 0.066217 | 0.17079 | 0.023245 | 0.044732 | -0.034176 | 0.018638 | -0.015177 | 0.024293 | 0.10039 | 0.081394 | 0.057421 | 0.038422
2983.0938 | 121.7285 | -0.52185 | 120.8267 | 0.13559 | -0.031363 | -0.016578 | -0.01586 | 0.040843 | 0.071848 | -0.035248 | 0.029595 | 0.13416 | -0.004219 | 0.021847 | -0.070797 | -0.013405 | -0.051798 | -0.016906 | 0.16763 | 0.00068 | 0.015465 | 0.016183 | 0.072886 | 0.10389 | -0.003205 | 0.061638 | 0.16621 | 0.027824 | 0.05389 | -0.038754 | 0.018638 | -0.019755 | 0.015137 | 0.10039 | 0.081393 | 0.066578 | 0.047579
2984.8594 | 120.9549 | -0.59052 | 120.8221 | 0.13101 | -0.031363 | -0.012 | -0.006703 | 0.049999 | 0.076426 | -0.035248 | 0.029595 | 0.13416 | -0.004219 | 0.012689 | -0.070797 | -0.013405 | -0.04722 | -0.016906 | 0.16305 | 0.00068 | 0.020043 | 0.02534 | 0.082042 | 0.10847 | -0.003205 | 0.061638 | 0.16621 | 0.027824 | 0.044732 | -0.038754 | 0.018638 | -0.015177 | 0.015137 | 0.10039 | 0.076815 | 0.066578 | 0.043001
2986.5625 | 120.9137 | -0.56763 | 120.6848 | 0.13559 | -0.035942 | -0.016578 | -0.002124 | 0.045421 | 0.067269 | -0.039826 | 0.034174 | 0.12501 | -0.008798 | 0.012689 | -0.070797 | -0.017983 | -0.04722 | -0.021484 | 0.16763 | -0.003899 | 0.015465 | 0.029919 | 0.077464 | 0.099312 | -0.007783 | 0.066217 | 0.15705 | 0.023245 | 0.044732 | -0.038754 | 0.01406 | -0.015177 | 0.010559 | 0.10497 | 0.081394 | 0.061999 | 0.038422
2988.2656 | 121.5637 | -0.54932 | 121.1838 | 0.13559 | -0.035942 | -0.012 | -0.01586 | 0.036265 | 0.071848 | -0.035248 | 0.034174 | 0.12958 | -0.008798 | 0.012689 | -0.075375 | -0.008827 | -0.051798 | -0.016906 | 0.16763 | -0.003899 | 0.020043 | 0.016183 | 0.068308 | 0.10389 | -0.003205 | 0.066217 | 0.16163 | 0.023245 | 0.044732 | -0.043332 | 0.023216 | -0.019755 | 0.015137 | 0.10955 | 0.085972 | 0.066577 | 0.043
2990.0156 | 121.2387 | -0.54474 | 120.3781 | 0.13559 | -0.035942 | -0.021157 | -0.006703 | 0.040843 | 0.067269 | -0.035248 | 0.01586 | 0.13416 | -0.004219 | 0.017268 | -0.070797 | -0.013405 | -0.04722 | -0.021484 | 0.16763 | -0.003899 | 0.010886 | 0.02534 | 0.072886 | 0.099312 | -0.003205 | 0.047903 | 0.16621 | 0.027824 | 0.049311 | -0.038754 | 0.018638 | -0.015177 | 0.010559 | 0.086657 | 0.06308 | 0.066578 | 0.043001
2991.7656 | 120.9595 | -0.59967 | 120.6757 | 0.13559 | -0.022205 | -0.012 | -0.006703 | 0.045421 | 0.067269 | -0.03067 | 0.020438 | 0.12958 | -0.008798 | 0.012689 | -0.075375 | -0.004248 | -0.04722 | -0.021484 | 0.16763 | 0.009838 | 0.020043 | 0.02534 | 0.077464 | 0.099312 | 0.001373 | 0.052481 | 0.16163 | 0.023245 | 0.044732 | -0.043332 | 0.027795 | -0.015177 | 0.010559 | 0.095813 | 0.067658 | 0.066577 | 0.038422
2993.5156 | 120.9824 | -0.58136 | 121.0236 | 0.13101 | -0.035942 | -0.021157 | -0.011281 | 0.040843 | 0.071848 | -0.035248 | 0.038752 | 0.13416 | -0.008798 | 0.017268 | -0.070797 | -0.008827 | -0.04722 | -0.016906 | 0.16305 | -0.003899 | 0.010886 | 0.020762 | 0.072886 | 0.10389 | -0.003205 | 0.070795 | 0.16621 | 0.023245 | 0.049311 | -0.038754 | 0.023216 | -0.015177 | 0.015137 | 0.10955 | 0.085972 | 0.061999 | 0.038422
2995.2188 | 121.637 | -0.58136 | 121.1975 | 0.12643 | -0.040521 | -0.025735 | -0.006703 | 0.045421 | 0.067269 | -0.039826 | 0.034174 | 0.12501 | -0.017954 | 0.00811 | -0.075375 | -0.013405 | -0.04722 | -0.012328 | 0.15847 | -0.008478 | 0.006308 | 0.02534 | 0.077464 | 0.099312 | -0.007783 | 0.066217 | 0.15705 | 0.014089 | 0.040153 | -0.043332 | 0.018638 | -0.015177 | 0.019715 | 0.10955 | 0.081394 | 0.057421 | 0.029266
2996.9688 | 121.2982 | -0.60425 | 121.0144 | 0.13559 | -0.035942 | -0.007421 | -0.002124 | 0.040843 | 0.062691 | -0.026092 | 0.025017 | 0.13416 | -0.004219 | 0.00811 | -0.075375 | -0.013405 | -0.04722 | -0.016906 | 0.16763 | -0.003899 | 0.024622 | 0.029919 | 0.072886 | 0.094734 | 0.005951 | 0.05706 | 0.16621 | 0.027824 | 0.040153 | -0.043332 | 0.018638 | -0.015177 | 0.015137 | 0.10039 | 0.072237 | 0.071156 | 0.043001
2998.7344 | 121.3806 | -0.61798 | 121.1151 | 0.13101 | -0.031363 | -0.025735 | -0.006703 | 0.045421 | 0.071848 | -0.035248 | 0.034174 | 0.12958 | -0.008798 | 0.017268 | -0.070797 | -0.017983 | -0.04722 | -0.016906 | 0.16305 | 0.00068 | 0.006308 | 0.02534 | 0.077464 | 0.10389 | -0.003205 | 0.066217 | 0.16163 | 0.023245 | 0.049311 | -0.038754 | 0.01406 | -0.015177 | 0.015137 | 0.10497 | 0.081394 | 0.061999 | 0.038422
3000.5 | 121.8292 | -0.53101 | 121.225 | 0.13101 | -0.031363 | -0.021157 | -0.006703 | 0.040843 | 0.067269 | -0.044405 | 0.034174 | 0.12958 | -0.008798 | 0.003531 | -0.070797 | -0.013405 | -0.042641 | -0.012328 | 0.16305 | 0.00068 | 0.010886 | 0.02534 | 0.072886 | 0.099312 | -0.012362 | 0.066217 | 0.16163 | 0.023245 | 0.035574 | -0.038754 | 0.018638 | -0.010598 | 0.019715 | 0.10497 | 0.076815 | 0.061999 | 0.033843
3002.2031 | 121.9162 | -0.5127 | 121.2616 | 0.13559 | -0.031363 | -0.021157 | -0.006703 | 0.036265 | 0.076426 | -0.03067 | 0.034174 | 0.12958 | -0.004219 | 0.00811 | -0.070797 | -0.013405 | -0.042641 | -0.016906 | 0.16763 | 0.00068 | 0.010886 | 0.02534 | 0.068308 | 0.10847 | 0.001373 | 0.066217 | 0.16163 | 0.027824 | 0.040153 | -0.038754 | 0.018638 | -0.010598 | 0.015137 | 0.10497 | 0.076815 | 0.066578 | 0.038422
3003.9688 | 121.8475 | -0.48065 | 121.2936 | 0.13101 | -0.035942 | -0.016578 | -0.011281 | 0.045421 | 0.067269 | -0.044405 | 0.034174 | 0.12958 | -0.008798 | 0.012689 | -0.075375 | -0.013405 | -0.051798 | -0.012328 | 0.16305 | -0.003899 | 0.015465 | 0.020762 | 0.077464 | 0.099312 | -0.012362 | 0.066217 | 0.16163 | 0.023245 | 0.044732 | -0.043332 | 0.018638 | -0.019755 | 0.019715 | 0.10955 | 0.085972 | 0.066577 | 0.043
3005.6875 | 121.0922 | -0.54932 | 121.2662 | 0.13559 | -0.0451 | -0.025735 | -0.006703 | 0.049999 | 0.071848 | -0.035248 | 0.025017 | 0.13416 | -0.013376 | 0.00811 | -0.066219 | -0.013405 | -0.04722 | -0.016906 | 0.16763 | -0.013057 | 0.006308 | 0.02534 | 0.082042 | 0.10389 | -0.003205 | 0.05706 | 0.16621 | 0.018667 | 0.040153 | -0.034176 | 0.018638 | -0.015177 | 0.015137 | 0.091236 | 0.072237 | 0.052843 | 0.033844
3007.4375 | 121.312 | -0.54474 | 121.1929 | 0.12643 | -0.035942 | -0.016578 | -0.020438 | 0.040843 | 0.076426 | -0.039826 | 0.034174 | 0.12958 | -0.004219 | 0.012689 | -0.066219 | -0.008827 | -0.04722 | -0.021484 | 0.15847 | -0.003899 | 0.015465 | 0.011605 | 0.072886 | 0.10847 | -0.007783 | 0.066217 | 0.16163 | 0.027824 | 0.044732 | -0.034176 | 0.023216 | -0.015177 | 0.010559 | 0.10039 | 0.081394 | 0.062 | 0.043001
3009.1875 | 121.9208 | -0.6958 | 121.106 | 0.13559 | -0.035942 | -0.021157 | -0.006703 | 0.049999 | 0.067269 | -0.044405 | 0.034174 | 0.12043 | -0.004219 | 0.00811 | -0.075375 | -0.022561 | -0.051798 | -0.021484 | 0.16763 | -0.003899 | 0.010886 | 0.02534 | 0.082042 | 0.099312 | -0.012362 | 0.066217 | 0.15247 | 0.027824 | 0.040153 | -0.043332 | 0.009482 | -0.019755 | 0.010559 | 0.10955 | 0.085972 | 0.071156 | 0.047579
3010.8906 | 121.2982 | -0.7782 | 120.6573 | 0.14017 | -0.035942 | -0.016578 | -0.006703 | 0.045421 | 0.067269 | -0.03067 | 0.034174 | 0.13874 | -0.008798 | 0.00811 | -0.075375 | -0.013405 | -0.051798 | -0.00775 | 0.17221 | -0.003899 | 0.015465 | 0.02534 | 0.077464 | 0.099312 | 0.001373 | 0.066217 | 0.17079 | 0.023245 | 0.040153 | -0.043332 | 0.018638 | -0.019755 | 0.024293 | 0.10955 | 0.085972 | 0.066577 | 0.043
3012.6406 | 121.4081 | -1.1032 | 120.0577 | 0.13559 | -0.035942 | -0.016578 | -0.011281 | 0.049999 | 0.071848 | -0.039826 | 0.025017 | 0.13416 | -0.004219 | 0.00811 | -0.075375 | -0.013405 | -0.04722 | -0.016906 | 0.16763 | -0.003899 | 0.015465 | 0.020762 | 0.082042 | 0.10389 | -0.007783 | 0.05706 | 0.16621 | 0.027824 | 0.040153 | -0.043332 | 0.018638 | -0.015177 | 0.015137 | 0.10039 | 0.072237 | 0.071156 | 0.043001
3014.4062 | 121.312 | -1.2039 | 119.9341 | 0.13101 | -0.035942 | -0.021157 | -0.011281 | 0.040843 | 0.067269 | -0.039826 | 0.034174 | 0.12958 | -0.008798 | 0.017268 | -0.066219 | -0.013405 | -0.038063 | -0.00775 | 0.16305 | -0.003899 | 0.010886 | 0.020762 | 0.072886 | 0.099312 | -0.007783 | 0.066217 | 0.16163 | 0.023245 | 0.049311 | -0.034176 | 0.018638 | -0.00602 | 0.024293 | 0.10039 | 0.072237 | 0.057421 | 0.029265
3016.1719 | 121.907 | -1.1719 | 120.6436 | 0.13101 | -0.040521 | -0.025735 | -0.006703 | 0.040843 | 0.067269 | -0.039826 | 0.034174 | 0.13416 | -0.004219 | 0.012689 | -0.075375 | -0.008827 | -0.051798 | -0.016906 | 0.16305 | -0.008478 | 0.006308 | 0.02534 | 0.072886 | 0.099312 | -0.007783 | 0.066217 | 0.16621 | 0.027824 | 0.044732 | -0.043332 | 0.023216 | -0.019755 | 0.015137 | 0.10955 | 0.085972 | 0.071156 | 0.047579
3017.8594 | 121.9391 | -1.2085 | 120.639 | 0.13101 | -0.035942 | -0.016578 | -0.006703 | 0.045421 | 0.067269 | -0.039826 | 0.029595 | 0.12958 | -0.008798 | 0.012689 | -0.075375 | -0.022561 | -0.04722 | -0.016906 | 0.16305 | -0.003899 | 0.015465 | 0.02534 | 0.077464 | 0.099312 | -0.007783 | 0.061638 | 0.16163 | 0.023245 | 0.044732 | -0.043332 | 0.009482 | -0.015177 | 0.015137 | 0.10497 | 0.076815 | 0.066577 | 0.038422
3019.625 | 121.4676 | -1.2405 | 120.6482 | 0.14017 | -0.040521 | -0.016578 | -0.006703 | 0.049999 | 0.071848 | -0.035248 | 0.038752 | 0.13416 | -0.004219 | 0.012689 | -0.070797 | -0.022561 | -0.056376 | -0.012328 | 0.17221 | -0.008478 | 0.015465 | 0.02534 | 0.082042 | 0.10389 | -0.003205 | 0.070795 | 0.16621 | 0.027824 | 0.044732 | -0.038754 | 0.009482 | -0.024333 | 0.019715 | 0.10955 | 0.095128 | 0.066578 | 0.052157
3021.3281 | 121.9482 | -1.2177 | 120.607 | 0.14017 | -0.031363 | -0.016578 | -0.011281 | 0.040843 | 0.067269 | -0.035248 | 0.034174 | 0.13874 | -0.013376 | 0.017268 | -0.070797 | -0.017983 | -0.051798 | -0.012328 | 0.17221 | 0.00068 | 0.015465 | 0.020762 | 0.072886 | 0.099312 | -0.003205 | 0.066217 | 0.17079 | 0.018667 | 0.049311 | -0.038754 | 0.01406 | -0.019755 | 0.019715 | 0.10497 | 0.085972 | 0.057421 | 0.038422
3023.0781 | 121.9757 | -1.236 | 120.6024 | 0.14932 | -0.035942 | -0.021157 | -0.006703 | 0.045421 | 0.067269 | -0.035248 | 0.034174 | 0.12958 | -0.013376 | 0.012689 | -0.075375 | -0.013405 | -0.042641 | -0.012328 | 0.18136 | -0.003899 | 0.010886 | 0.02534 | 0.077464 | 0.099312 | -0.003205 | 0.066217 | 0.16163 | 0.018667 | 0.044732 | -0.043332 | 0.018638 | -0.010598 | 0.019715 | 0.10955 | 0.076815 | 0.061999 | 0.029265
3024.7812 | 121.4905 | -1.3 | 120.2133 | 0.13101 | -0.031363 | -0.012 | -0.011281 | 0.045421 | 0.076426 | -0.035248 | 0.025017 | 0.13874 | -0.004219 | 0.00811 | -0.070797 | -0.008827 | -0.051798 | -0.016906 | 0.16305 | 0.00068 | 0.020043 | 0.020762 | 0.077464 | 0.10847 | -0.003205 | 0.05706 | 0.17079 | 0.027824 | 0.040153 | -0.038754 | 0.023216 | -0.019755 | 0.015137 | 0.095814 | 0.076815 | 0.066578 | 0.047579
3026.5312 | 121.5317 | -1.3229 | 119.9524 | 0.13101 | -0.026784 | -0.016578 | -0.006703 | 0.049999 | 0.076426 | -0.039826 | 0.038752 | 0.12958 | 0.000359 | 0.017268 | -0.066219 | -0.008827 | -0.042641 | -0.021484 | 0.16305 | 0.005259 | 0.015465 | 0.02534 | 0.082042 | 0.10847 | -0.007783 | 0.070795 | 0.16163 | 0.032402 | 0.049311 | -0.034176 | 0.023216 | -0.010598 | 0.010559 | 0.10497 | 0.081393 | 0.066578 | 0.043
3028.2969 | 121.3577 | -1.3367 | 120.0577 | 0.11727 | -0.031363 | -0.021157 | -0.011281 | 0.040843 | 0.071848 | -0.035248 | 0.029595 | 0.13416 | 0.004937 | 0.012689 | -0.070797 | -0.013405 | -0.051798 | -0.012328 | 0.14932 | 0.00068 | 0.010886 | 0.020762 | 0.072886 | 0.10389 | -0.003205 | 0.061638 | 0.16621 | 0.03698 | 0.044732 | -0.038754 | 0.018638 | -0.019755 | 0.019715 | 0.10039 | 0.081393 | 0.075734 | 0.056735
3030.0781 | 122.0169 | -51.8005 | 69.7861 | 0.13101 | -0.035942 | -0.021157 | -0.006703 | 0.049999 | 0.076426 | -0.039826 | 0.029595 | 0.13416 | 0.000359 | 0.012689 | -0.070797 | -0.017983 | -0.04722 | -0.021484 | 0.16305 | -0.003899 | 0.010886 | 0.02534 | 0.082042 | 0.10847 | -0.007783 | 0.061638 | 0.16621 | 0.032402 | 0.044732 | -0.038754 | 0.01406 | -0.015177 | 0.010559 | 0.10039 | 0.076815 | 0.071156 | 0.047579
3031.7812 | 122.0306 | -0.1831 | 121.6003 | 0.13559 | -0.031363 | -0.016578 | -0.002124 | 0.040843 | 0.062691 | -0.03067 | 0.029595 | 0.13874 | -0.008798 | 0.012689 | -0.075375 | -0.013405 | -0.051798 | -0.016906 | 0.16763 | 0.00068 | 0.015465 | 0.029919 | 0.072886 | 0.094734 | 0.001373 | 0.061638 | 0.17079 | 0.023245 | 0.044732 | -0.043332 | 0.018638 | -0.019755 | 0.015137 | 0.10497 | 0.081393 | 0.066577 | 0.043
3033.5469 | 121.9437 | -0.13733 | 121.756 | 0.14017 | -0.031363 | -0.021157 | -0.006703 | 0.049999 | 0.071848 | -0.035248 | 0.029595 | 0.14332 | -0.008798 | 0.021847 | -0.075375 | -0.004248 | -0.04722 | -0.012328 | 0.17221 | 0.00068 | 0.010886 | 0.02534 | 0.082042 | 0.10389 | -0.003205 | 0.061638 | 0.17536 | 0.023245 | 0.05389 | -0.043332 | 0.027795 | -0.015177 | 0.019715 | 0.10497 | 0.076815 | 0.066577 | 0.038422
3035.25 | 121.9528 | -0.15106 | 121.7834 | 0.13559 | -0.031363 | -0.012 | -0.006703 | 0.045421 | 0.071848 | -0.035248 | 0.025017 | 0.13874 | -0.008798 | 0.003531 | -0.070797 | -0.008827 | -0.056376 | -0.016906 | 0.16763 | 0.00068 | 0.020043 | 0.02534 | 0.077464 | 0.10389 | -0.003205 | 0.05706 | 0.17079 | 0.023245 | 0.035574 | -0.038754 | 0.023216 | -0.024333 | 0.015137 | 0.095814 | 0.081393 | 0.061999 | 0.047578
3037 | 121.9254 | -0.12817 | 121.8109 | 0.13559 | -0.031363 | -0.025735 | -0.002124 | 0.040843 | 0.071848 | -0.03067 | 0.029595 | 0.12958 | -0.008798 | 0.012689 | -0.075375 | -0.013405 | -0.051798 | -0.016906 | 0.16763 | 0.00068 | 0.006308 | 0.029919 | 0.072886 | 0.10389 | 0.001373 | 0.061638 | 0.16163 | 0.023245 | 0.044732 | -0.043332 | 0.018638 | -0.019755 | 0.015137 | 0.10497 | 0.081393 | 0.066577 | 0.043
3038.75 | 121.9757 | -0.13733 | 121.8201 | 0.14017 | -0.031363 | -0.021157 | -0.011281 | 0.045421 | 0.076426 | -0.044405 | 0.029595 | 0.13874 | 0.000359 | 0.00811 | -0.075375 | -0.022561 | -0.056376 | -0.016906 | 0.17221 | 0.00068 | 0.010886 | 0.020762 | 0.077464 | 0.10847 | -0.012362 | 0.061638 | 0.17079 | 0.032402 | 0.040153 | -0.043332 | 0.009482 | -0.024333 | 0.015137 | 0.10497 | 0.085971 | 0.075734 | 0.056735
3040.5156 | 122.0261 | -0.09613 | 121.8384 | 0.13101 | -0.026784 | -0.021157 | -0.011281 | 0.045421 | 0.062691 | -0.039826 | 0.029595 | 0.13874 | -0.013376 | 0.017268 | -0.070797 | -0.017983 | -0.04722 | -0.021484 | 0.16305 | 0.005259 | 0.010886 | 0.020762 | 0.077464 | 0.094734 | -0.007783 | 0.061638 | 0.17079 | 0.018667 | 0.049311 | -0.038754 | 0.01406 | -0.015177 | 0.010559 | 0.10039 | 0.076815 | 0.057421 | 0.033844
3042.2656 | 122.0673 | -0.09613 | 121.8246 | 0.13101 | -0.035942 | -0.021157 | -0.01586 | 0.036265 | 0.062691 | -0.039826 | 0.025017 | 0.13874 | -0.013376 | 0.012689 | -0.070797 | -0.013405 | -0.04722 | -0.012328 | 0.16305 | -0.003899 | 0.010886 | 0.016183 | 0.068308 | 0.094734 | -0.007783 | 0.05706 | 0.17079 | 0.018667 | 0.044732 | -0.038754 | 0.018638 | -0.015177 | 0.019715 | 0.095814 | 0.072237 | 0.057421 | 0.033844
3044.0156 | 122.0306 | -0.11444 | 121.843 | 0.12643 | -0.040521 | -0.016578 | -0.011281 | 0.054577 | 0.071848 | -0.035248 | 0.034174 | 0.13416 | -0.008798 | 0.00811 | -0.075375 | -0.008827 | -0.051798 | -0.012328 | 0.15847 | -0.008478 | 0.015465 | 0.020762 | 0.08662 | 0.10389 | -0.003205 | 0.066217 | 0.16621 | 0.023245 | 0.040153 | -0.043332 | 0.023216 | -0.019755 | 0.019715 | 0.10955 | 0.085972 | 0.066577 | 0.043
3045.7188 | 121.9208 | -0.16479 | 121.8567 | 0.14017 | -0.035942 | -0.021157 | -0.006703 | 0.045421 | 0.067269 | -0.039826 | 0.038752 | 0.12958 | -0.013376 | 0.017268 | -0.070797 | -0.013405 | -0.04722 | -0.016906 | 0.17221 | -0.003899 | 0.010886 | 0.02534 | 0.077464 | 0.099312 | -0.007783 | 0.070795 | 0.16163 | 0.018667 | 0.049311 | -0.038754 | 0.018638 | -0.015177 | 0.015137 | 0.10955 | 0.085972 | 0.057421 | 0.033844
3047.4688 | 121.9574 | -0.14191 | 121.8338 | 0.14017 | -0.035942 | -0.016578 | -0.011281 | 0.045421 | 0.071848 | -0.035248 | 0.029595 | 0.13874 | -0.008798 | 0.017268 | -0.070797 | -0.013405 | -0.042641 | -0.012328 | 0.17221 | -0.003899 | 0.015465 | 0.020762 | 0.077464 | 0.10389 | -0.003205 | 0.061638 | 0.17079 | 0.023245 | 0.049311 | -0.038754 | 0.018638 | -0.010598 | 0.019715 | 0.10039 | 0.072236 | 0.061999 | 0.033843
3049.1562 | 121.2982 | -0.12817 | 121.2662 | 0.13559 | -0.026784 | -0.021157 | -0.002124 | 0.054577 | 0.067269 | -0.03067 | 0.029595 | 0.13874 | -0.008798 | 0.00811 | -0.075375 | -0.008827 | -0.04722 | -0.012328 | 0.16763 | 0.005259 | 0.010886 | 0.029919 | 0.08662 | 0.099312 | 0.001373 | 0.061638 | 0.17079 | 0.023245 | 0.040153 | -0.043332 | 0.023216 | -0.015177 | 0.019715 | 0.10497 | 0.076815 | 0.066577 | 0.038422
3050.9219 | 122.0718 | -0.082397 | 121.7331 | 0.13559 | -0.031363 | -0.021157 | -0.006703 | 0.049999 | 0.062691 | -0.03067 | 0.029595 | 0.13416 | -0.008798 | 0.003531 | -0.070797 | -0.013405 | -0.04722 | -0.00775 | 0.16763 | 0.00068 | 0.010886 | 0.02534 | 0.082042 | 0.094734 | 0.001373 | 0.061638 | 0.16621 | 0.023245 | 0.035574 | -0.038754 | 0.018638 | -0.015177 | 0.024293 | 0.10039 | 0.076815 | 0.061999 | 0.038422
3052.6719 | 121.4996 | -0.15106 | 121.344 | 0.13559 | -0.026784 | -0.025735 | -0.011281 | 0.049999 | 0.067269 | -0.035248 | 0.034174 | 0.13874 | -0.008798 | 0.00811 | -0.070797 | -0.008827 | -0.038063 | -0.016906 | 0.16763 | 0.005259 | 0.006308 | 0.020762 | 0.082042 | 0.099312 | -0.003205 | 0.066217 | 0.17079 | 0.023245 | 0.040153 | -0.038754 | 0.023216 | -0.00602 | 0.015137 | 0.10497 | 0.072237 | 0.061999 | 0.029265
3054.3594 | 121.431 | -0.15564 | 121.3257 | 0.13559 | -0.026784 | -0.030314 | -0.006703 | 0.045421 | 0.076426 | -0.035248 | 0.034174 | 0.12958 | -0.004219 | 0.012689 | -0.070797 | -0.008827 | -0.04722 | -0.012328 | 0.16763 | 0.005259 | 0.001729 | 0.02534 | 0.077464 | 0.10847 | -0.003205 | 0.066217 | 0.16163 | 0.027824 | 0.044732 | -0.038754 | 0.023216 | -0.015177 | 0.019715 | 0.10497 | 0.081394 | 0.066578 | 0.043001
3056.125 | 122.0764 | -0.091553 | 121.9162 | 0.13559 | -0.040521 | -0.016578 | -0.006703 | 0.045421 | 0.067269 | -0.035248 | 0.029595 | 0.13416 | -0.008798 | 0.00811 | -0.075375 | -0.017983 | -0.04722 | -0.00775 | 0.16763 | -0.008478 | 0.015465 | 0.02534 | 0.077464 | 0.099312 | -0.003205 | 0.061638 | 0.16621 | 0.023245 | 0.040153 | -0.043332 | 0.01406 | -0.015177 | 0.024293 | 0.10497 | 0.076815 | 0.066577 | 0.038422
3057.8281 | 121.6644 | -0.13733 | 121.9437 | 0.14017 | -0.035942 | -0.016578 | -0.011281 | 0.031687 | 0.076426 | -0.035248 | 0.025017 | 0.13874 | -0.004219 | 0.017268 | -0.075375 | -0.017983 | -0.04722 | -0.021484 | 0.17221 | -0.003899 | 0.015465 | 0.020762 | 0.06373 | 0.10847 | -0.003205 | 0.05706 | 0.17079 | 0.027824 | 0.049311 | -0.043332 | 0.01406 | -0.015177 | 0.010559 | 0.10039 | 0.072237 | 0.071156 | 0.043001
3059.5781 | 122.0718 | -0.10071 | 121.8979 | 0.13559 | -0.026784 | -0.016578 | -0.006703 | 0.040843 | 0.067269 | -0.039826 | 0.034174 | 0.12958 | -0.008798 | 0.012689 | -0.070797 | -0.017983 | -0.04722 | -0.016906 | 0.16763 | 0.005259 | 0.015465 | 0.02534 | 0.072886 | 0.099312 | -0.007783 | 0.066217 | 0.16163 | 0.023245 | 0.044732 | -0.038754 | 0.01406 | -0.015177 | 0.015137 | 0.10497 | 0.081394 | 0.061999 | 0.038422
3061.3438 | 122.0718 | -0.086975 | 121.9208 | 0.14017 | -0.031363 | -0.016578 | -0.002124 | 0.040843 | 0.067269 | -0.035248 | 0.034174 | 0.13874 | -0.004219 | 0.017268 | -0.066219 | -0.008827 | -0.038063 | -0.021484 | 0.17221 | 0.00068 | 0.015465 | 0.029919 | 0.072886 | 0.099312 | -0.003205 | 0.066217 | 0.17079 | 0.027824 | 0.049311 | -0.034176 | 0.023216 | -0.00602 | 0.010559 | 0.10039 | 0.072237 | 0.062 | 0.033844
3063.1094 | 122.1085 | -0.10071 | 121.8475 | 0.14017 | -0.031363 | -0.025735 | -0.011281 | 0.045421 | 0.076426 | -0.044405 | 0.038752 | 0.13874 | -0.008798 | 0.017268 | -0.070797 | -0.013405 | -0.04722 | -0.00775 | 0.17221 | 0.00068 | 0.006308 | 0.020762 | 0.077464 | 0.10847 | -0.012362 | 0.070795 | 0.17079 | 0.023245 | 0.049311 | -0.038754 | 0.018638 | -0.015177 | 0.024293 | 0.10955 | 0.085972 | 0.061999 | 0.038422
3064.8125 | 122.1359 | -0.082397 | 121.9391 | 0.14474 | -0.026784 | -0.021157 | -0.006703 | 0.040843 | 0.067269 | -0.039826 | 0.038752 | 0.13416 | -0.004219 | 0.012689 | -0.070797 | -0.013405 | -0.051798 | -0.016906 | 0.17679 | 0.005259 | 0.010886 | 0.02534 | 0.072886 | 0.099312 | -0.007783 | 0.070795 | 0.16621 | 0.027824 | 0.044732 | -0.038754 | 0.018638 | -0.019755 | 0.015137 | 0.10955 | 0.09055 | 0.066578 | 0.047579
3066.5781 | 121.4996 | -0.15564 | 121.3348 | 0.13101 | -0.035942 | -0.016578 | -0.002124 | 0.036265 | 0.071848 | -0.03067 | 0.029595 | 0.13416 | -0.013376 | 0.012689 | -0.075375 | -0.017983 | -0.04722 | -0.016906 | 0.16305 | -0.003899 | 0.015465 | 0.029919 | 0.068308 | 0.10389 | 0.001373 | 0.061638 | 0.16621 | 0.018667 | 0.044732 | -0.043332 | 0.01406 | -0.015177 | 0.015137 | 0.10497 | 0.076815 | 0.061999 | 0.033844
3068.2812 | 122.1222 | -0.10986 | 121.9391 | 0.14017 | -0.022205 | -0.021157 | -0.006703 | 0.040843 | 0.067269 | -0.039826 | 0.034174 | 0.14332 | -0.008798 | 0.012689 | -0.075375 | -0.017983 | -0.051798 | -0.016906 | 0.17221 | 0.009838 | 0.010886 | 0.02534 | 0.072886 | 0.099312 | -0.007783 | 0.066217 | 0.17536 | 0.023245 | 0.044732 | -0.043332 | 0.01406 | -0.019755 | 0.015137 | 0.10955 | 0.085972 | 0.066577 | 0.043
3070.0312 | 122.113 | -0.086975 | 121.9803 | 0.14017 | -0.035942 | -0.021157 | -0.011281 | 0.045421 | 0.076426 | -0.039826 | 0.034174 | 0.13874 | -0.008798 | 0.021847 | -0.070797 | -0.013405 | -0.051798 | -0.016906 | 0.17221 | -0.003899 | 0.010886 | 0.020762 | 0.077464 | 0.10847 | -0.007783 | 0.066217 | 0.17079 | 0.023245 | 0.05389 | -0.038754 | 0.018638 | -0.019755 | 0.015137 | 0.10497 | 0.085972 | 0.061999 | 0.043
3071.7969 | 121.5958 | -0.12817 | 121.6003 | 0.14017 | -0.031363 | -0.016578 | -0.006703 | 0.040843 | 0.071848 | -0.035248 | 0.034174 | 0.13416 | -0.008798 | 0.012689 | -0.066219 | -0.008827 | -0.04722 | -0.016906 | 0.17221 | 0.00068 | 0.015465 | 0.02534 | 0.072886 | 0.10389 | -0.003205 | 0.066217 | 0.16621 | 0.023245 | 0.044732 | -0.034176 | 0.023216 | -0.015177 | 0.015137 | 0.10039 | 0.081394 | 0.057421 | 0.038422
3073.5625 | 122.1176 | -0.10529 | 121.9574 | 0.13101 | -0.022205 | -0.016578 | -0.006703 | 0.040843 | 0.071848 | -0.03067 | 0.034174 | 0.13416 | -0.008798 | 0.012689 | -0.070797 | -0.013405 | -0.051798 | -0.012328 | 0.16305 | 0.009838 | 0.015465 | 0.02534 | 0.072886 | 0.10389 | 0.001373 | 0.066217 | 0.16621 | 0.023245 | 0.044732 | -0.038754 | 0.018638 | -0.019755 | 0.019715 | 0.10497 | 0.085972 | 0.061999 | 0.043
3075.2656 | 122.1222 | -0.068665 | 121.8292 | 0.14017 | -0.031363 | -0.021157 | -0.011281 | 0.045421 | 0.067269 | -0.044405 | 0.047909 | 0.12958 | -0.004219 | 0.017268 | -0.070797 | -0.013405 | -0.056376 | -0.021484 | 0.17221 | 0.00068 | 0.010886 | 0.020762 | 0.077464 | 0.099312 | -0.012362 | 0.079952 | 0.16163 | 0.027824 | 0.049311 | -0.038754 | 0.018638 | -0.024333 | 0.010559 | 0.11871 | 0.10429 | 0.066578 | 0.052157
3077.0312 | 122.0901 | -0.12817 | 121.7514 | 0.14474 | -0.022205 | -0.016578 | -0.006703 | 0.036265 | 0.067269 | -0.039826 | 0.034174 | 0.13874 | -0.004219 | 0.012689 | -0.075375 | -0.008827 | -0.042641 | -0.016906 | 0.17679 | 0.009838 | 0.015465 | 0.02534 | 0.068308 | 0.099312 | -0.007783 | 0.066217 | 0.17079 | 0.027824 | 0.044732 | -0.043332 | 0.023216 | -0.010598 | 0.015137 | 0.10955 | 0.076815 | 0.071156 | 0.038422
3078.7969 | 122.0398 | -0.12817 | 121.9711 | 0.13559 | -0.035942 | -0.016578 | -0.006703 | 0.040843 | 0.062691 | -0.035248 | 0.034174 | 0.13874 | -0.008798 | 0.017268 | -0.070797 | -0.013405 | -0.051798 | -0.016906 | 0.16763 | -0.003899 | 0.015465 | 0.02534 | 0.072886 | 0.094734 | -0.003205 | 0.066217 | 0.17079 | 0.023245 | 0.049311 | -0.038754 | 0.018638 | -0.019755 | 0.015137 | 0.10497 | 0.085972 | 0.061999 | 0.043
3080.5 | 122.1634 | -0.086975 | 121.9711 | 0.13101 | -0.031363 | -0.021157 | -0.006703 | 0.040843 | 0.071848 | -0.044405 | 0.034174 | 0.13416 | -0.008798 | 0.012689 | -0.079953 | -0.017983 | -0.04722 | -0.00775 | 0.16305 | 0.00068 | 0.010886 | 0.02534 | 0.072886 | 0.10389 | -0.012362 | 0.066217 | 0.16621 | 0.023245 | 0.044732 | -0.04791 | 0.01406 | -0.015177 | 0.024293 | 0.11413 | 0.081394 | 0.071155 | 0.038422
3082.2031 | 122.1771 | -0.07782 | 121.9711 | 0.13101 | -0.026784 | -0.016578 | -0.011281 | 0.045421 | 0.071848 | -0.035248 | 0.038752 | 0.13874 | -0.017954 | 0.012689 | -0.075375 | -0.008827 | -0.04722 | -0.021484 | 0.16305 | 0.005259 | 0.015465 | 0.020762 | 0.077464 | 0.10389 | -0.003205 | 0.070795 | 0.17079 | 0.014089 | 0.044732 | -0.043332 | 0.023216 | -0.015177 | 0.010559 | 0.11413 | 0.085972 | 0.057421 | 0.029266
3083.9688 | 122.0581 | -0.1236 | 122.0352 | 0.13559 | -0.031363 | -0.016578 | -0.006703 | 0.045421 | 0.071848 | -0.039826 | 0.029595 | 0.12958 | -0.004219 | 0.012689 | -0.079953 | -0.017983 | -0.038063 | -0.012328 | 0.16763 | 0.00068 | 0.015465 | 0.02534 | 0.077464 | 0.10389 | -0.007783 | 0.061638 | 0.16163 | 0.027824 | 0.044732 | -0.04791 | 0.01406 | -0.00602 | 0.019715 | 0.10955 | 0.067658 | 0.075734 | 0.033844
3085.6719 | 122.0627 | -0.13275 | 122.0444 | 0.13559 | -0.035942 | -0.016578 | -0.006703 | 0.049999 | 0.081005 | -0.035248 | 0.038752 | 0.12958 | -0.004219 | 0.012689 | -0.061641 | -0.008827 | -0.04722 | -0.00775 | 0.16763 | -0.003899 | 0.015465 | 0.02534 | 0.082042 | 0.11305 | -0.003205 | 0.070795 | 0.16163 | 0.027824 | 0.044732 | -0.029598 | 0.023216 | -0.015177 | 0.024293 | 0.10039 | 0.085972 | 0.057422 | 0.043001
3087.4375 | 122.1405 | -0.10071 | 122.0444 | 0.13559 | -0.035942 | -0.025735 | -0.01586 | 0.036265 | 0.067269 | -0.035248 | 0.034174 | 0.13416 | -0.013376 | 0.012689 | -0.070797 | -0.013405 | -0.042641 | -0.012328 | 0.16763 | -0.003899 | 0.006308 | 0.016183 | 0.068308 | 0.099312 | -0.003205 | 0.066217 | 0.16621 | 0.018667 | 0.044732 | -0.038754 | 0.018638 | -0.010598 | 0.019715 | 0.10497 | 0.076815 | 0.057421 | 0.029265
3089.1875 | 122.0993 | -0.11902 | 121.9162 | 0.14017 | -0.031363 | -0.016578 | -0.006703 | 0.045421 | 0.062691 | -0.03067 | 0.038752 | 0.13416 | -0.013376 | 0.017268 | -0.079953 | -0.027139 | -0.04722 | -0.016906 | 0.17221 | 0.00068 | 0.015465 | 0.02534 | 0.077464 | 0.094734 | 0.001373 | 0.070795 | 0.16621 | 0.018667 | 0.049311 | -0.04791 | 0.004904 | -0.015177 | 0.015137 | 0.11871 | 0.085972 | 0.066577 | 0.033844
3090.8906 | 122.0764 | -0.1236 | 122.0398 | 0.14017 | -0.026784 | -0.021157 | -0.011281 | 0.036265 | 0.067269 | -0.035248 | 0.034174 | 0.13416 | 0.000359 | 0.017268 | -0.070797 | -0.008827 | -0.042641 | -0.012328 | 0.17221 | 0.005259 | 0.010886 | 0.020762 | 0.068308 | 0.099312 | -0.003205 | 0.066217 | 0.16621 | 0.032402 | 0.049311 | -0.038754 | 0.023216 | -0.010598 | 0.019715 | 0.10497 | 0.076815 | 0.071156 | 0.043
3092.6406 | 122.1909 | -0.07782 | 122.0215 | 0.13101 | -0.035942 | -0.021157 | -0.020438 | 0.036265 | 0.067269 | -0.039826 | 0.043331 | 0.1479 | -0.013376 | 0.021847 | -0.070797 | -0.017983 | -0.042641 | -0.012328 | 0.16305 | -0.003899 | 0.010886 | 0.011605 | 0.068308 | 0.099312 | -0.007783 | 0.075374 | 0.17994 | 0.018667 | 0.05389 | -0.038754 | 0.01406 | -0.010598 | 0.019715 | 0.11413 | 0.085972 | 0.057421 | 0.029265
3094.3438 | 122.2229 | -0.086975 | 122.0032 | 0.14017 | -0.031363 | -0.021157 | -0.01586 | 0.040843 | 0.067269 | -0.035248 | 0.034174 | 0.13874 | -0.008798 | 0.00811 | -0.070797 | -0.013405 | -0.04722 | -0.021484 | 0.17221 | 0.00068 | 0.010886 | 0.016183 | 0.072886 | 0.099312 | -0.003205 | 0.066217 | 0.17079 | 0.023245 | 0.040153 | -0.038754 | 0.018638 | -0.015177 | 0.010559 | 0.10497 | 0.081394 | 0.061999 | 0.038422
3096.1094 | 122.0947 | -0.1236 | 122.0764 | 0.13101 | -0.031363 | -0.016578 | -0.011281 | 0.049999 | 0.071848 | -0.035248 | 0.034174 | 0.13416 | -0.013376 | 0.021847 | -0.070797 | -0.017983 | -0.051798 | -0.012328 | 0.16305 | 0.00068 | 0.015465 | 0.020762 | 0.082042 | 0.10389 | -0.003205 | 0.066217 | 0.16621 | 0.018667 | 0.05389 | -0.038754 | 0.01406 | -0.019755 | 0.019715 | 0.10497 | 0.085972 | 0.057421 | 0.038422
3097.875 | 122.2229 | -0.082397 | 121.9849 | 0.13559 | -0.031363 | -0.016578 | -0.006703 | 0.040843 | 0.071848 | -0.035248 | 0.034174 | 0.13874 | -0.004219 | 0.017268 | -0.070797 | -0.008827 | -0.04722 | -0.003172 | 0.16763 | 0.00068 | 0.015465 | 0.02534 | 0.072886 | 0.10389 | -0.003205 | 0.066217 | 0.17079 | 0.027824 | 0.049311 | -0.038754 | 0.023216 | -0.015177 | 0.028871 | 0.10497 | 0.081394 | 0.066578 | 0.043001
3099.5781 | 122.0535 | -0.1236 | 121.9299 | 0.14017 | -0.031363 | -0.016578 | -0.011281 | 0.049999 | 0.067269 | -0.035248 | 0.034174 | 0.13416 | 0.000359 | 0.017268 | -0.075375 | -0.017983 | -0.051798 | -0.016906 | 0.17221 | 0.00068 | 0.015465 | 0.020762 | 0.082042 | 0.099312 | -0.003205 | 0.066217 | 0.16621 | 0.032402 | 0.049311 | -0.043332 | 0.01406 | -0.019755 | 0.015137 | 0.10955 | 0.085972 | 0.075734 | 0.052157
3101.3281 | 122.168 | -0.091553 | 122.0398 | 0.14017 | -0.035942 | -0.021157 | -0.011281 | 0.036265 | 0.071848 | -0.039826 | 0.038752 | 0.13874 | 0.000359 | 0.021847 | -0.070797 | -0.008827 | -0.042641 | -0.016906 | 0.17221 | -0.003899 | 0.010886 | 0.020762 | 0.068308 | 0.10389 | -0.007783 | 0.070795 | 0.17079 | 0.032402 | 0.05389 | -0.038754 | 0.023216 | -0.010598 | 0.015137 | 0.10955 | 0.081393 | 0.071156 | 0.043
3103.0938 | 122.2092 | -0.086975 | 122.0581 | 0.13101 | -0.035942 | -0.016578 | -0.011281 | 0.036265 | 0.071848 | -0.039826 | 0.034174 | 0.13416 | -0.004219 | 0.00811 | -0.075375 | -0.013405 | -0.04722 | -0.012328 | 0.16305 | -0.003899 | 0.015465 | 0.020762 | 0.068308 | 0.10389 | -0.007783 | 0.066217 | 0.16621 | 0.027824 | 0.040153 | -0.043332 | 0.018638 | -0.015177 | 0.019715 | 0.10955 | 0.081394 | 0.071156 | 0.043001
3104.7969 | 121.9757 | -0.13275 | 121.756 | 0.14017 | -0.031363 | -0.021157 | -0.006703 | 0.040843 | 0.076426 | -0.035248 | 0.043331 | 0.13874 | -0.008798 | 0.017268 | -0.075375 | -0.017983 | -0.051798 | -0.012328 | 0.17221 | 0.00068 | 0.010886 | 0.02534 | 0.072886 | 0.10847 | -0.003205 | 0.075374 | 0.17079 | 0.023245 | 0.049311 | -0.043332 | 0.01406 | -0.019755 | 0.019715 | 0.11871 | 0.095129 | 0.066577 | 0.043
3106.5625 | 122.2 | -0.082397 | 122.0398 | 0.14017 | -0.031363 | -0.016578 | -0.006703 | 0.036265 | 0.062691 | -0.044405 | 0.034174 | 0.13874 | -0.008798 | 0.012689 | -0.070797 | -0.008827 | -0.051798 | -0.012328 | 0.17221 | 0.00068 | 0.015465 | 0.02534 | 0.068308 | 0.094734 | -0.012362 | 0.066217 | 0.17079 | 0.023245 | 0.044732 | -0.038754 | 0.023216 | -0.019755 | 0.019715 | 0.10497 | 0.085972 | 0.061999 | 0.043
3108.3281 | 122.2275 | -0.082397 | 122.0627 | 0.13101 | -0.031363 | -0.016578 | -0.006703 | 0.049999 | 0.062691 | -0.035248 | 0.029595 | 0.13416 | -0.013376 | 0.012689 | -0.079953 | -0.022561 | -0.051798 | -0.016906 | 0.16305 | 0.00068 | 0.015465 | 0.02534 | 0.082042 | 0.094734 | -0.003205 | 0.061638 | 0.16621 | 0.018667 | 0.044732 | -0.04791 | 0.009482 | -0.019755 | 0.015137 | 0.10955 | 0.081393 | 0.066577 | 0.038422
3110.0938 | 121.9299 | -0.13733 | 121.7148 | 0.13559 | -0.026784 | -0.021157 | 0.007033 | 0.045421 | 0.071848 | -0.035248 | 0.034174 | 0.14332 | -0.013376 | 0.012689 | -0.075375 | -0.013405 | -0.051798 | -0.016906 | 0.16763 | 0.005259 | 0.010886 | 0.039076 | 0.077464 | 0.10389 | -0.003205 | 0.066217 | 0.17536 | 0.018667 | 0.044732 | -0.043332 | 0.018638 | -0.019755 | 0.015137 | 0.10955 | 0.085972 | 0.061999 | 0.038422
3111.8594 | 122.1954 | -0.09613 | 122.0901 | 0.13559 | -0.026784 | -0.016578 | -0.002124 | 0.045421 | 0.076426 | -0.035248 | 0.038752 | 0.13416 | -0.004219 | 0.003531 | -0.070797 | -0.013405 | -0.04722 | -0.016906 | 0.16763 | 0.005259 | 0.015465 | 0.029919 | 0.077464 | 0.10847 | -0.003205 | 0.070795 | 0.16621 | 0.027824 | 0.035574 | -0.038754 | 0.018638 | -0.015177 | 0.015137 | 0.10955 | 0.085972 | 0.066578 | 0.043001
3113.5625 | 122.1313 | -0.13275 | 122.1176 | 0.13559 | -0.026784 | -0.021157 | -0.006703 | 0.045421 | 0.071848 | -0.044405 | 0.029595 | 0.12958 | -0.013376 | 0.003531 | -0.075375 | -0.022561 | -0.04722 | -0.021484 | 0.16763 | 0.005259 | 0.010886 | 0.02534 | 0.077464 | 0.10389 | -0.012362 | 0.061638 | 0.16163 | 0.018667 | 0.035574 | -0.043332 | 0.009482 | -0.015177 | 0.010559 | 0.10497 | 0.076815 | 0.061999 | 0.033844
3115.3281 | 121.9849 | -0.1236 | 122.1359 | 0.14017 | -0.031363 | -0.016578 | -0.006703 | 0.040843 | 0.071848 | -0.035248 | 0.034174 | 0.13874 | 0.000359 | 0.017268 | -0.079953 | -0.022561 | -0.04722 | -0.021484 | 0.17221 | 0.00068 | 0.015465 | 0.02534 | 0.072886 | 0.10389 | -0.003205 | 0.066217 | 0.17079 | 0.032402 | 0.049311 | -0.04791 | 0.009482 | -0.015177 | 0.010559 | 0.11413 | 0.081394 | 0.080312 | 0.047579
3117.0938 | 122.0627 | -0.10529 | 122.1222 | 0.14474 | -0.031363 | -0.025735 | -0.011281 | 0.049999 | 0.067269 | -0.03067 | 0.034174 | 0.13416 | 0.000359 | 0.017268 | -0.070797 | -0.013405 | -0.04722 | -0.021484 | 0.17679 | 0.00068 | 0.006308 | 0.020762 | 0.082042 | 0.099312 | 0.001373 | 0.066217 | 0.16621 | 0.032402 | 0.049311 | -0.038754 | 0.018638 | -0.015177 | 0.010559 | 0.10497 | 0.081394 | 0.071156 | 0.047579
3118.7812 | 122.287 | -0.091553 | 122.081 | 0.13559 | -0.026784 | -0.025735 | -0.011281 | 0.045421 | 0.067269 | -0.03067 | 0.034174 | 0.13874 | 0.000359 | 0.017268 | -0.070797 | -0.008827 | -0.042641 | -0.016906 | 0.16763 | 0.005259 | 0.006308 | 0.020762 | 0.077464 | 0.099312 | 0.001373 | 0.066217 | 0.17079 | 0.032402 | 0.049311 | -0.038754 | 0.023216 | -0.010598 | 0.015137 | 0.10497 | 0.076815 | 0.071156 | 0.043
3120.5469 | 122.2412 | -0.082397 | 122.0856 | 0.13559 | -0.026784 | -0.021157 | -0.01586 | 0.045421 | 0.062691 | -0.035248 | 0.034174 | 0.12958 | -0.004219 | 0.012689 | -0.075375 | -0.017983 | -0.042641 | -0.016906 | 0.16763 | 0.005259 | 0.010886 | 0.016183 | 0.077464 | 0.094734 | -0.003205 | 0.066217 | 0.16163 | 0.027824 | 0.044732 | -0.043332 | 0.01406 | -0.010598 | 0.015137 | 0.10955 | 0.076815 | 0.071156 | 0.038422
3122.25 | 122.0306 | -0.32501 | 121.8475 | 0.13559 | -0.031363 | -0.025735 | -0.006703 | 0.045421 | 0.076426 | -0.035248 | 0.034174 | 0.12958 | -0.004219 | 0.017268 | -0.070797 | -0.008827 | -0.04722 | -0.012328 | 0.16763 | 0.00068 | 0.006308 | 0.02534 | 0.077464 | 0.10847 | -0.003205 | 0.066217 | 0.16163 | 0.027824 | 0.049311 | -0.038754 | 0.023216 | -0.015177 | 0.019715 | 0.10497 | 0.081394 | 0.066578 | 0.043001
3124.0156 | 122.1359 | -1.03 | 120.9915 | 0.13559 | -0.017627 | -0.016578 | 0.002454 | 0.040843 | 0.067269 | -0.039826 | 0.034174 | 0.13416 | -0.004219 | 0.012689 | -0.070797 | -0.022561 | -0.056376 | -0.012328 | 0.16763 | 0.014416 | 0.015465 | 0.034497 | 0.072886 | 0.099312 | -0.007783 | 0.066217 | 0.16621 | 0.027824 | 0.044732 | -0.038754 | 0.009482 | -0.024333 | 0.019715 | 0.10497 | 0.09055 | 0.066578 | 0.052157
3125.7812 | 121.7789 | -1.7761 | 119.9112 | 0.13559 | -0.026784 | -0.021157 | -0.006703 | 0.045421 | 0.062691 | -0.035248 | 0.029595 | 0.13416 | -0.013376 | 0.012689 | -0.070797 | -0.017983 | -0.04722 | -0.016906 | 0.16763 | 0.005259 | 0.010886 | 0.02534 | 0.077464 | 0.094734 | -0.003205 | 0.061638 | 0.16621 | 0.018667 | 0.044732 | -0.038754 | 0.01406 | -0.015177 | 0.015137 | 0.10039 | 0.076815 | 0.057421 | 0.033844
3127.5 | 121.3165 | -2.8976 | 118.2358 | 0.13559 | -0.026784 | -0.021157 | -0.011281 | 0.045421 | 0.067269 | -0.035248 | 0.038752 | 0.13416 | -0.004219 | 0.012689 | -0.070797 | -0.013405 | -0.042641 | -0.021484 | 0.16763 | 0.005259 | 0.010886 | 0.020762 | 0.077464 | 0.099312 | -0.003205 | 0.070795 | 0.16621 | 0.027824 | 0.044732 | -0.038754 | 0.018638 | -0.010598 | 0.010559 | 0.10955 | 0.081393 | 0.066578 | 0.038422
3129.1875 | 121.7056 | -67.6666 | 54.9088 | 0.14474 | -0.031363 | -0.021157 | -0.002124 | 0.040843 | 0.071848 | -0.03067 | 0.034174 | 0.13416 | -0.008798 | 0.012689 | -0.066219 | -0.022561 | -0.04722 | -0.021484 | 0.17679 | 0.00068 | 0.010886 | 0.029919 | 0.072886 | 0.10389 | 0.001373 | 0.066217 | 0.16621 | 0.023245 | 0.044732 | -0.034176 | 0.009482 | -0.015177 | 0.010559 | 0.10039 | 0.081394 | 0.057421 | 0.038422
3130.9375 | 121.701 | -89.5203 | 32.0023 | 0.14017 | -0.022205 | -0.016578 | -0.002124 | 0.040843 | 0.071848 | -0.039826 | 0.038752 | 0.13874 | -0.008798 | 0.021847 | -0.066219 | -0.017983 | -0.051798 | -0.012328 | 0.17221 | 0.009838 | 0.015465 | 0.029919 | 0.072886 | 0.10389 | -0.007783 | 0.070795 | 0.17079 | 0.023245 | 0.05389 | -0.034176 | 0.01406 | -0.019755 | 0.019715 | 0.10497 | 0.09055 | 0.057421 | 0.043
3132.7031 | 121.8155 | -80.4565 | 40.8829 | 0.14474 | -0.026784 | -0.021157 | -0.011281 | 0.040843 | 0.067269 | -0.03067 | 0.038752 | 0.13416 | -0.008798 | 0.012689 | -0.066219 | -0.017983 | -0.04722 | -0.021484 | 0.17679 | 0.005259 | 0.010886 | 0.020762 | 0.072886 | 0.099312 | 0.001373 | 0.070795 | 0.16621 | 0.023245 | 0.044732 | -0.034176 | 0.01406 | -0.015177 | 0.010559 | 0.10497 | 0.085972 | 0.057421 | 0.038422
3134.4688 | 121.6141 | -85.1349 | 36.0718 | 0.13559 | -0.026784 | -0.016578 | -0.006703 | 0.045421 | 0.076426 | -0.039826 | 0.034174 | 0.13416 | -0.004219 | 0.017268 | -0.070797 | -0.013405 | -0.04722 | -0.012328 | 0.16763 | 0.005259 | 0.015465 | 0.02534 | 0.077464 | 0.10847 | -0.007783 | 0.066217 | 0.16621 | 0.027824 | 0.049311 | -0.038754 | 0.018638 | -0.015177 | 0.019715 | 0.10497 | 0.081394 | 0.066578 | 0.043001
3136.2344 | 121.5775 | -90.2847 | 31.0089 | 0.13101 | -0.040521 | -0.016578 | -0.006703 | 0.045421 | 0.067269 | -0.03067 | 0.038752 | 0.13416 | -0.004219 | 0.012689 | -0.070797 | -0.022561 | -0.04722 | -0.026063 | 0.16305 | -0.008478 | 0.015465 | 0.02534 | 0.077464 | 0.099312 | 0.001373 | 0.070795 | 0.16621 | 0.027824 | 0.044732 | -0.038754 | 0.009482 | -0.015177 | 0.00598 | 0.10955 | 0.085972 | 0.066578 | 0.043001
3137.9531 | 121.3074 | -63.533 | 57.5912 | 0.14017 | -0.026784 | -0.016578 | -0.006703 | 0.045421 | 0.067269 | -0.035248 | 0.034174 | 0.14332 | 0.000359 | 0.017268 | -0.066219 | -0.017983 | -0.051798 | -0.016906 | 0.17221 | 0.005259 | 0.015465 | 0.02534 | 0.077464 | 0.099312 | -0.003205 | 0.066217 | 0.17536 | 0.032402 | 0.049311 | -0.034176 | 0.01406 | -0.019755 | 0.015137 | 0.10039 | 0.085972 | 0.066578 | 0.052157
3139.7031 | 120.6573 | -46.2891 | 74.7162 | 0.14017 | -0.031363 | -0.012 | -0.002124 | 0.049999 | 0.071848 | -0.026092 | 0.034174 | 0.14332 | -0.004219 | 0.017268 | -0.070797 | -0.031717 | -0.060955 | -0.021484 | 0.17221 | 0.00068 | 0.020043 | 0.029919 | 0.082042 | 0.10389 | 0.005951 | 0.066217 | 0.17536 | 0.027824 | 0.049311 | -0.038754 | 0.000326 | -0.028912 | 0.010559 | 0.10497 | 0.095129 | 0.066578 | 0.056736
3141.4531 | 121.7651 | -72.757 | 48.5138 | 0.13559 | -0.026784 | -0.021157 | -0.002124 | 0.045421 | 0.071848 | -0.044405 | 0.038752 | 0.13874 | -0.013376 | 0.017268 | -0.061641 | -0.004248 | -0.051798 | -0.021484 | 0.16763 | 0.005259 | 0.010886 | 0.029919 | 0.077464 | 0.10389 | -0.012362 | 0.070795 | 0.17079 | 0.018667 | 0.049311 | -0.029598 | 0.027795 | -0.019755 | 0.010559 | 0.10039 | 0.09055 | 0.048265 | 0.038422
3143.2031 | 121.637 | -80.1453 | 41.2033 | 0.13559 | -0.026784 | -0.021157 | -0.002124 | 0.045421 | 0.076426 | -0.03067 | 0.038752 | 0.13874 | -0.004219 | 0.017268 | -0.061641 | -0.013405 | -0.051798 | -0.016906 | 0.16763 | 0.005259 | 0.010886 | 0.029919 | 0.077464 | 0.10847 | 0.001373 | 0.070795 | 0.17079 | 0.027824 | 0.049311 | -0.029598 | 0.018638 | -0.019755 | 0.015137 | 0.10039 | 0.09055 | 0.057422 | 0.047579
3144.8906 | 121.1517 | -1.3 | 120.52 | 0.13559 | -0.031363 | -0.025735 | -0.006703 | 0.049999 | 0.067269 | -0.039826 | 0.043331 | 0.13416 | 0.000359 | 0.017268 | -0.066219 | -0.013405 | -0.042641 | -0.016906 | 0.16763 | 0.00068 | 0.006308 | 0.02534 | 0.082042 | 0.099312 | -0.007783 | 0.075374 | 0.16621 | 0.032402 | 0.049311 | -0.034176 | 0.018638 | -0.010598 | 0.015137 | 0.10955 | 0.085972 | 0.066578 | 0.043
3146.6562 | 121.7422 | -83.8715 | 37.3489 | 0.13101 | -0.031363 | -0.021157 | -0.006703 | 0.045421 | 0.067269 | -0.035248 | 0.038752 | 0.13874 | -0.008798 | 0.012689 | -0.066219 | -0.008827 | -0.042641 | -0.016906 | 0.16305 | 0.00068 | 0.010886 | 0.02534 | 0.077464 | 0.099312 | -0.003205 | 0.070795 | 0.17079 | 0.023245 | 0.044732 | -0.034176 | 0.023216 | -0.010598 | 0.015137 | 0.10497 | 0.081393 | 0.057421 | 0.033843
3148.3438 | 121.637 | -97.5632 | 23.7213 | 0.14474 | -0.031363 | -0.021157 | -0.002124 | 0.040843 | 0.067269 | -0.035248 | 0.029595 | 0.13874 | 0.004937 | 0.00811 | -0.066219 | -0.017983 | -0.051798 | -0.012328 | 0.17679 | 0.00068 | 0.010886 | 0.029919 | 0.072886 | 0.099312 | -0.003205 | 0.061638 | 0.17079 | 0.03698 | 0.040153 | -0.034176 | 0.01406 | -0.019755 | 0.019715 | 0.095814 | 0.081393 | 0.071156 | 0.056735
3150.1094 | 121.5912 | -120.108 | 1.1627 | 0.14017 | -0.026784 | -0.025735 | -0.002124 | 0.040843 | 0.067269 | -0.035248 | 0.038752 | 0.1479 | -0.008798 | 0.021847 | -0.066219 | -0.013405 | -0.04722 | -0.016906 | 0.17221 | 0.005259 | 0.006308 | 0.029919 | 0.072886 | 0.099312 | -0.003205 | 0.070795 | 0.17994 | 0.023245 | 0.05389 | -0.034176 | 0.018638 | -0.015177 | 0.015137 | 0.10497 | 0.085972 | 0.057421 | 0.038422
3151.8125 | 121.5317 | -120.1401 | 1.1948 | 0.14017 | -0.026784 | -0.016578 | 0.002454 | 0.045421 | 0.067269 | -0.044405 | 0.038752 | 0.13416 | -0.004219 | 0.012689 | -0.070797 | -0.013405 | -0.04722 | -0.016906 | 0.17221 | 0.005259 | 0.015465 | 0.034497 | 0.077464 | 0.099312 | -0.012362 | 0.070795 | 0.16621 | 0.027824 | 0.044732 | -0.038754 | 0.018638 | -0.015177 | 0.015137 | 0.10955 | 0.085972 | 0.066578 | 0.043001
3153.5781 | 121.5683 | -120.108 | 1.1719 | 0.14017 | -0.026784 | -0.012 | -0.006703 | 0.036265 | 0.071848 | -0.039826 | 0.038752 | 0.13874 | -0.013376 | 0.012689 | -0.066219 | -0.013405 | -0.04722 | -0.016906 | 0.17221 | 0.005259 | 0.020043 | 0.02534 | 0.068308 | 0.10389 | -0.007783 | 0.070795 | 0.17079 | 0.018667 | 0.044732 | -0.034176 | 0.018638 | -0.015177 | 0.015137 | 0.10497 | 0.085972 | 0.052843 | 0.033844
3155.3438 | 121.0968 | -0.054932 | 121.6278 | 0.13559 | -0.031363 | -0.016578 | -0.011281 | 0.040843 | 0.067269 | -0.039826 | 0.043331 | 0.14332 | -0.004219 | 0.00811 | -0.061641 | -0.008827 | -0.051798 | -0.016906 | 0.16763 | 0.00068 | 0.015465 | 0.020762 | 0.072886 | 0.099312 | -0.007783 | 0.075374 | 0.17536 | 0.027824 | 0.040153 | -0.029598 | 0.023216 | -0.019755 | 0.015137 | 0.10497 | 0.095129 | 0.057422 | 0.047579
3157.0312 | 120.7535 | 0.11902 | 107.2815 | 0.14017 | -0.035942 | -0.021157 | -0.011281 | 0.040843 | 0.062691 | -0.035248 | 0.029595 | 0.13416 | -0.013376 | 0.021847 | -0.061641 | -0.013405 | -0.04722 | -0.016906 | 0.17221 | -0.003899 | 0.010886 | 0.020762 | 0.072886 | 0.094734 | -0.003205 | 0.061638 | 0.16621 | 0.018667 | 0.05389 | -0.029598 | 0.018638 | -0.015177 | 0.015137 | 0.091236 | 0.076815 | 0.048265 | 0.033844
3158.7969 | 119.4443 | 0.11902 | 116.6245 | 0.13559 | -0.026784 | -0.025735 | -0.006703 | 0.040843 | 0.067269 | -0.039826 | 0.034174 | 0.14332 | -0.004219 | 0.017268 | -0.057062 | -0.008827 | -0.056376 | -0.021484 | 0.16763 | 0.005259 | 0.006308 | 0.02534 | 0.072886 | 0.099312 | -0.007783 | 0.066217 | 0.17536 | 0.027824 | 0.049311 | -0.025019 | 0.023216 | -0.024333 | 0.010559 | 0.091236 | 0.09055 | 0.052843 | 0.052157
3160.5625 | 104.2145 | 0.17853 | 118.1534 | 0.14474 | -0.031363 | -0.021157 | -0.011281 | 0.040843 | 0.071848 | -0.035248 | 0.034174 | 0.13874 | -0.017954 | 0.017268 | -0.066219 | -0.008827 | -0.04722 | -0.00775 | 0.17679 | 0.00068 | 0.010886 | 0.020762 | 0.072886 | 0.10389 | -0.003205 | 0.066217 | 0.17079 | 0.014089 | 0.049311 | -0.034176 | 0.023216 | -0.015177 | 0.024293 | 0.10039 | 0.081394 | 0.048265 | 0.029266
3162.2656 | 98.6298 | 0.004578 | 106.6315 | 0.14017 | -0.026784 | -0.021157 | 0.002454 | 0.045421 | 0.067269 | -0.03067 | 0.029595 | 0.13874 | 0.000359 | 0.012689 | -0.052484 | -0.013405 | -0.042641 | -0.021484 | 0.17221 | 0.005259 | 0.010886 | 0.034497 | 0.077464 | 0.099312 | 0.001373 | 0.061638 | 0.17079 | 0.032402 | 0.044732 | -0.020441 | 0.018638 | -0.010598 | 0.010559 | 0.082079 | 0.072236 | 0.052843 | 0.043
3164.0156 | 91.0446 | -0.20142 | 91.571 | 0.13559 | -0.017627 | -0.012 | -0.006703 | 0.040843 | 0.076426 | -0.035248 | 0.034174 | 0.14332 | -0.013376 | 0.012689 | -0.057062 | -0.013405 | -0.04722 | -0.016906 | 0.16763 | 0.014416 | 0.020043 | 0.02534 | 0.072886 | 0.10847 | -0.003205 | 0.066217 | 0.17536 | 0.018667 | 0.044732 | -0.025019 | 0.018638 | -0.015177 | 0.015137 | 0.091236 | 0.081394 | 0.043686 | 0.033844
3165.7656 | 121.788 | 0.022888 | 115.8829 | 0.13559 | -0.031363 | -0.025735 | -0.002124 | 0.040843 | 0.076426 | -0.035248 | 0.038752 | 0.13874 | -0.008798 | 0.012689 | -0.070797 | -0.013405 | -0.04722 | -0.021484 | 0.16763 | 0.00068 | 0.006308 | 0.029919 | 0.072886 | 0.10847 | -0.003205 | 0.070795 | 0.17079 | 0.023245 | 0.044732 | -0.038754 | 0.018638 | -0.015177 | 0.010559 | 0.10955 | 0.085972 | 0.061999 | 0.038422
3167.4688 | 121.1426 | -0.013733 | 121.0327 | 0.14017 | -0.035942 | -0.025735 | -0.011281 | 0.040843 | 0.071848 | -0.039826 | 0.043331 | 0.13874 | 0.000359 | 0.012689 | -0.066219 | -0.013405 | -0.042641 | -0.012328 | 0.17221 | -0.003899 | 0.006308 | 0.020762 | 0.072886 | 0.10389 | -0.007783 | 0.075374 | 0.17079 | 0.032402 | 0.044732 | -0.034176 | 0.018638 | -0.010598 | 0.019715 | 0.10955 | 0.085972 | 0.066578 | 0.043
3169.2188 | 121.431 | -0.07782 | 121.2433 | 0.14017 | -0.035942 | -0.021157 | -0.006703 | 0.045421 | 0.067269 | -0.039826 | 0.043331 | 0.12958 | 0.000359 | 0.00811 | -0.057062 | -0.017983 | -0.04722 | -0.012328 | 0.17221 | -0.003899 | 0.010886 | 0.02534 | 0.077464 | 0.099312 | -0.007783 | 0.075374 | 0.16163 | 0.032402 | 0.040153 | -0.025019 | 0.01406 | -0.015177 | 0.019715 | 0.10039 | 0.090551 | 0.057421 | 0.047579
3170.9219 | 121.1929 | -0.018311 | 121.1105 | 0.13559 | -0.031363 | -0.021157 | -0.006703 | 0.045421 | 0.067269 | -0.03067 | 0.043331 | 0.13416 | -0.008798 | 0.00811 | -0.066219 | -0.013405 | -0.04722 | -0.021484 | 0.16763 | 0.00068 | 0.010886 | 0.02534 | 0.077464 | 0.099312 | 0.001373 | 0.075374 | 0.16621 | 0.023245 | 0.040153 | -0.034176 | 0.018638 | -0.015177 | 0.010559 | 0.10955 | 0.090551 | 0.057421 | 0.038422
3172.6875 | 121.2891 | -0.036621 | 121.0922 | 0.13559 | -0.026784 | -0.021157 | -0.006703 | 0.040843 | 0.062691 | -0.03067 | 0.038752 | 0.13874 | -0.008798 | 0.012689 | -0.057062 | -0.008827 | -0.038063 | -0.016906 | 0.16763 | 0.005259 | 0.010886 | 0.02534 | 0.072886 | 0.094734 | 0.001373 | 0.070795 | 0.17079 | 0.023245 | 0.044732 | -0.025019 | 0.023216 | -0.00602 | 0.015137 | 0.095814 | 0.076815 | 0.048264 | 0.029265
3174.4375 | 121.4401 | -0.10071 | 121.1655 | 0.13101 | -0.026784 | -0.021157 | -0.002124 | 0.036265 | 0.071848 | -0.035248 | 0.043331 | 0.13874 | -0.008798 | 0.012689 | -0.061641 | -0.008827 | -0.056376 | -0.016906 | 0.16305 | 0.005259 | 0.010886 | 0.029919 | 0.068308 | 0.10389 | -0.003205 | 0.075374 | 0.17079 | 0.023245 | 0.044732 | -0.029598 | 0.023216 | -0.024333 | 0.015137 | 0.10497 | 0.099707 | 0.052843 | 0.047578
3176.1875 | 121.4951 | -0.073242 | 121.17 | 0.13101 | -0.031363 | -0.025735 | -0.011281 | 0.036265 | 0.067269 | -0.035248 | 0.038752 | 0.13416 | 0.000359 | 0.00811 | -0.061641 | -0.013405 | -0.04722 | -0.012328 | 0.16305 | 0.00068 | 0.006308 | 0.020762 | 0.068308 | 0.099312 | -0.003205 | 0.070795 | 0.16621 | 0.032402 | 0.040153 | -0.029598 | 0.018638 | -0.015177 | 0.019715 | 0.10039 | 0.085972 | 0.062 | 0.047579
3177.9062 | 91.0492 | -0.10986 | 114.9902 | 0.14017 | -0.022205 | -0.012 | -0.006703 | 0.036265 | 0.067269 | -0.039826 | 0.043331 | 0.13874 | -0.008798 | 0.00811 | -0.057062 | -0.013405 | -0.042641 | -0.012328 | 0.17221 | 0.009838 | 0.020043 | 0.02534 | 0.068308 | 0.099312 | -0.007783 | 0.075374 | 0.17079 | 0.023245 | 0.040153 | -0.025019 | 0.018638 | -0.010598 | 0.019715 | 0.10039 | 0.085972 | 0.048264 | 0.033843
3179.6719 | 117.0639 | 0 | 118.1351 | 0.13559 | -0.031363 | -0.021157 | -0.002124 | 0.040843 | 0.076426 | -0.039826 | 0.043331 | 0.13874 | -0.004219 | 0.012689 | -0.061641 | -0.013405 | -0.051798 | -0.012328 | 0.16763 | 0.00068 | 0.010886 | 0.029919 | 0.072886 | 0.10847 | -0.007783 | 0.075374 | 0.17079 | 0.027824 | 0.044732 | -0.029598 | 0.018638 | -0.019755 | 0.019715 | 0.10497 | 0.095129 | 0.057422 | 0.047579
3181.4375 | 91.127 | -0.036621 | 109.433 | 0.13559 | -0.022205 | -0.016578 | -0.002124 | 0.036265 | 0.071848 | -0.039826 | 0.038752 | 0.14332 | 0.000359 | 0.017268 | -0.061641 | -0.008827 | -0.04722 | -0.016906 | 0.16763 | 0.009838 | 0.015465 | 0.029919 | 0.068308 | 0.10389 | -0.007783 | 0.070795 | 0.17536 | 0.032402 | 0.049311 | -0.029598 | 0.023216 | -0.015177 | 0.015137 | 0.10039 | 0.085972 | 0.062 | 0.047579
3183.2031 | 116.0706 | -0.041199 | 116.7572 | 0.14017 | -0.026784 | -0.025735 | -0.006703 | 0.045421 | 0.067269 | -0.03067 | 0.038752 | 0.13416 | -0.008798 | 0.012689 | -0.066219 | -0.013405 | -0.051798 | -0.012328 | 0.17221 | 0.005259 | 0.006308 | 0.02534 | 0.077464 | 0.099312 | 0.001373 | 0.070795 | 0.16621 | 0.023245 | 0.044732 | -0.034176 | 0.018638 | -0.019755 | 0.019715 | 0.10497 | 0.09055 | 0.057421 | 0.043
3184.9062 | 121.3715 | -0.064087 | 122.081 | 0.13559 | -0.031363 | -0.021157 | -0.006703 | 0.040843 | 0.071848 | -0.035248 | 0.043331 | 0.13874 | 0.000359 | 0.021847 | -0.061641 | -0.013405 | -0.051798 | -0.016906 | 0.16763 | 0.00068 | 0.010886 | 0.02534 | 0.072886 | 0.10389 | -0.003205 | 0.075374 | 0.17079 | 0.032402 | 0.05389 | -0.029598 | 0.018638 | -0.019755 | 0.015137 | 0.10497 | 0.095129 | 0.062 | 0.052157
3186.6562 | 121.4996 | -0.068665 | 121.2891 | 0.13101 | -0.026784 | -0.016578 | -0.011281 | 0.036265 | 0.067269 | -0.035248 | 0.034174 | 0.13874 | -0.008798 | 0.012689 | -0.061641 | -0.017983 | -0.04722 | -0.016906 | 0.16305 | 0.005259 | 0.015465 | 0.020762 | 0.068308 | 0.099312 | -0.003205 | 0.066217 | 0.17079 | 0.023245 | 0.044732 | -0.029598 | 0.01406 | -0.015177 | 0.015137 | 0.095815 | 0.081394 | 0.052843 | 0.038422
3188.4219 | 121.4905 | -0.073242 | 121.9711 | 0.14017 | -0.026784 | -0.021157 | -0.002124 | 0.040843 | 0.071848 | -0.035248 | 0.034174 | 0.14332 | -0.004219 | 0.012689 | -0.061641 | -0.013405 | -0.042641 | -0.021484 | 0.17221 | 0.005259 | 0.010886 | 0.029919 | 0.072886 | 0.10389 | -0.003205 | 0.066217 | 0.17536 | 0.027824 | 0.044732 | -0.029598 | 0.018638 | -0.010598 | 0.010559 | 0.095815 | 0.076815 | 0.057422 | 0.038422
3190.125 | 93.5349 | -0.036621 | 92.8757 | 0.13101 | -0.031363 | -0.021157 | -0.006703 | 0.040843 | 0.062691 | -0.044405 | 0.043331 | 0.13874 | -0.008798 | 0.012689 | -0.057062 | -0.013405 | -0.04722 | -0.012328 | 0.16305 | 0.00068 | 0.010886 | 0.02534 | 0.072886 | 0.094734 | -0.012362 | 0.075374 | 0.17079 | 0.023245 | 0.044732 | -0.025019 | 0.018638 | -0.015177 | 0.019715 | 0.10039 | 0.090551 | 0.048264 | 0.038422
3191.875 | 121.463 | -0.068665 | 121.4081 | 0.14017 | -0.026784 | -0.021157 | -0.011281 | 0.040843 | 0.071848 | -0.035248 | 0.034174 | 0.14332 | -0.013376 | 0.017268 | -0.066219 | -0.008827 | -0.051798 | -0.016906 | 0.17221 | 0.005259 | 0.010886 | 0.020762 | 0.072886 | 0.10389 | -0.003205 | 0.066217 | 0.17536 | 0.018667 | 0.049311 | -0.034176 | 0.023216 | -0.019755 | 0.015137 | 0.10039 | 0.085972 | 0.052843 | 0.038422
3193.6406 | 100.177 | 0.20142 | 111.7767 | 0.13101 | -0.026784 | -0.021157 | -0.002124 | 0.036265 | 0.071848 | -0.035248 | 0.029595 | 0.13874 | -0.013376 | 0.017268 | -0.066219 | -0.013405 | -0.04722 | -0.012328 | 0.16305 | 0.005259 | 0.010886 | 0.029919 | 0.068308 | 0.10389 | -0.003205 | 0.061638 | 0.17079 | 0.018667 | 0.049311 | -0.034176 | 0.018638 | -0.015177 | 0.019715 | 0.095814 | 0.076815 | 0.052843 | 0.033844
3195.3594 | 113.0859 | 0.013733 | 121.257 | 0.13559 | -0.022205 | -0.025735 | -0.002124 | 0.045421 | 0.062691 | -0.035248 | 0.043331 | 0.14332 | -0.008798 | 0.012689 | -0.061641 | -0.008827 | -0.051798 | -0.016906 | 0.16763 | 0.009838 | 0.006308 | 0.029919 | 0.077464 | 0.094734 | -0.003205 | 0.075374 | 0.17536 | 0.023245 | 0.044732 | -0.029598 | 0.023216 | -0.019755 | 0.015137 | 0.10497 | 0.095129 | 0.052843 | 0.043
3197.1094 | 121.5088 | -0.091553 | 121.5363 | 0.13559 | -0.035942 | -0.025735 | -0.002124 | 0.040843 | 0.062691 | -0.039826 | 0.043331 | 0.12958 | 0.000359 | 0.021847 | -0.052484 | -0.013405 | -0.051798 | -0.012328 | 0.16763 | -0.003899 | 0.006308 | 0.029919 | 0.072886 | 0.094734 | -0.007783 | 0.075374 | 0.16163 | 0.032402 | 0.05389 | -0.020441 | 0.018638 | -0.019755 | 0.019715 | 0.095815 | 0.095129 | 0.052843 | 0.052157
3198.8125 | 121.7606 | -0.07782 | 121.8063 | 0.14017 | -0.031363 | -0.016578 | -0.006703 | 0.045421 | 0.067269 | -0.039826 | 0.038752 | 0.13874 | -0.004219 | 0.017268 | -0.061641 | -0.013405 | -0.042641 | -0.012328 | 0.17221 | 0.00068 | 0.015465 | 0.02534 | 0.077464 | 0.099312 | -0.007783 | 0.070795 | 0.17079 | 0.027824 | 0.049311 | -0.029598 | 0.018638 | -0.010598 | 0.019715 | 0.10039 | 0.081393 | 0.057422 | 0.038422
3200.5781 | 93.6172 | 0.63171 | 121.4813 | 0.14017 | -0.022205 | -0.016578 | -0.006703 | 0.040843 | 0.071848 | -0.039826 | 0.034174 | 0.14332 | -0.008798 | 0.021847 | -0.061641 | -0.017983 | -0.042641 | -0.026063 | 0.17221 | 0.009838 | 0.015465 | 0.02534 | 0.072886 | 0.10389 | -0.007783 | 0.066217 | 0.17536 | 0.023245 | 0.05389 | -0.029598 | 0.01406 | -0.010598 | 0.00598 | 0.095815 | 0.076815 | 0.052843 | 0.033843
3202.2969 | 120.5933 | 0.004578 | 121.5683 | 0.13101 | -0.031363 | -0.016578 | -0.006703 | 0.036265 | 0.071848 | -0.039826 | 0.034174 | 0.14332 | -0.008798 | 0.017268 | -0.066219 | -0.017983 | -0.042641 | -0.00775 | 0.16305 | 0.00068 | 0.015465 | 0.02534 | 0.068308 | 0.10389 | -0.007783 | 0.066217 | 0.17536 | 0.023245 | 0.049311 | -0.034176 | 0.01406 | -0.010598 | 0.024293 | 0.10039 | 0.076815 | 0.057421 | 0.033843
3204.0625 | 121.5317 | -0.064087 | 121.7651 | 0.13559 | -0.031363 | -0.030314 | -0.002124 | 0.036265 | 0.071848 | -0.039826 | 0.029595 | 0.12958 | -0.008798 | 0.012689 | -0.057062 | -0.017983 | -0.051798 | -0.021484 | 0.16763 | 0.00068 | 0.001729 | 0.029919 | 0.068308 | 0.10389 | -0.007783 | 0.061638 | 0.16163 | 0.023245 | 0.044732 | -0.025019 | 0.01406 | -0.019755 | 0.010559 | 0.086657 | 0.081393 | 0.048264 | 0.043
3205.7656 | 121.4584 | -0.068665 | 121.8155 | 0.13559 | -0.026784 | -0.016578 | 0.002454 | 0.040843 | 0.067269 | -0.039826 | 0.038752 | 0.13874 | -0.004219 | 0.017268 | -0.066219 | -0.017983 | -0.051798 | -0.012328 | 0.16763 | 0.005259 | 0.015465 | 0.034497 | 0.072886 | 0.099312 | -0.007783 | 0.070795 | 0.17079 | 0.027824 | 0.049311 | -0.034176 | 0.01406 | -0.019755 | 0.019715 | 0.10497 | 0.09055 | 0.062 | 0.047579
3207.5156 | 96.8719 | 0.1831 | 121.3623 | 0.14017 | -0.031363 | -0.016578 | 0.002454 | 0.040843 | 0.071848 | -0.03067 | 0.038752 | 0.14332 | -0.008798 | 0.017268 | -0.057062 | -0.013405 | -0.04722 | -0.016906 | 0.17221 | 0.00068 | 0.015465 | 0.034497 | 0.072886 | 0.10389 | 0.001373 | 0.070795 | 0.17536 | 0.023245 | 0.049311 | -0.025019 | 0.018638 | -0.015177 | 0.015137 | 0.095814 | 0.085972 | 0.048264 | 0.038422
3209.2188 | 121.7468 | -0.07782 | 121.8842 | 0.13101 | -0.035942 | -0.016578 | 0.002454 | 0.040843 | 0.067269 | -0.035248 | 0.038752 | 0.13416 | -0.008798 | 0.017268 | -0.057062 | -0.013405 | -0.04722 | -0.016906 | 0.16305 | -0.003899 | 0.015465 | 0.034497 | 0.072886 | 0.099312 | -0.003205 | 0.070795 | 0.16621 | 0.023245 | 0.049311 | -0.025019 | 0.018638 | -0.015177 | 0.015137 | 0.095814 | 0.085972 | 0.048264 | 0.038422
3210.9844 | 121.8704 | -0.082397 | 122.0078 | 0.13101 | -0.035942 | -0.016578 | -0.011281 | 0.040843 | 0.062691 | -0.039826 | 0.043331 | 0.14332 | -0.004219 | 0.017268 | -0.057062 | -0.013405 | -0.051798 | -0.016906 | 0.16305 | -0.003899 | 0.015465 | 0.020762 | 0.072886 | 0.094734 | -0.007783 | 0.075374 | 0.17536 | 0.027824 | 0.049311 | -0.025019 | 0.018638 | -0.019755 | 0.015137 | 0.10039 | 0.095129 | 0.052843 | 0.047579
3212.75 | 111.2595 | 0.073242 | 121.4035 | 0.14017 | -0.026784 | -0.021157 | -0.002124 | 0.040843 | 0.067269 | -0.039826 | 0.034174 | 0.13874 | 0.000359 | 0.012689 | -0.057062 | -0.013405 | -0.04722 | -0.016906 | 0.17221 | 0.005259 | 0.010886 | 0.029919 | 0.072886 | 0.099312 | -0.007783 | 0.066217 | 0.17079 | 0.032402 | 0.044732 | -0.025019 | 0.018638 | -0.015177 | 0.015137 | 0.091236 | 0.081394 | 0.057421 | 0.047579
3214.4531 | 121.9116 | -0.082397 | 121.9803 | 0.14017 | -0.031363 | -0.016578 | -0.011281 | 0.045421 | 0.071848 | -0.039826 | 0.043331 | 0.13874 | -0.008798 | 0.021847 | -0.057062 | -0.013405 | -0.04722 | -0.021484 | 0.17221 | 0.00068 | 0.015465 | 0.020762 | 0.077464 | 0.10389 | -0.007783 | 0.075374 | 0.17079 | 0.023245 | 0.05389 | -0.025019 | 0.018638 | -0.015177 | 0.010559 | 0.10039 | 0.090551 | 0.048264 | 0.038422
3216.2031 | 121.7285 | -0.059509 | 122.0261 | 0.13101 | -0.022205 | -0.025735 | -0.006703 | 0.040843 | 0.067269 | -0.035248 | 0.038752 | 0.13416 | -0.004219 | 0.00811 | -0.066219 | -0.008827 | -0.038063 | -0.021484 | 0.16305 | 0.009838 | 0.006308 | 0.02534 | 0.072886 | 0.099312 | -0.003205 | 0.070795 | 0.16621 | 0.027824 | 0.040153 | -0.034176 | 0.023216 | -0.00602 | 0.010559 | 0.10497 | 0.076815 | 0.062 | 0.033844
3217.9844 | 121.8246 | -0.054932 | 121.9894 | 0.13559 | -0.031363 | -0.016578 | -0.002124 | 0.045421 | 0.062691 | -0.035248 | 0.034174 | 0.13874 | -0.004219 | 0.017268 | -0.057062 | -0.004248 | -0.042641 | -0.012328 | 0.16763 | 0.00068 | 0.015465 | 0.029919 | 0.077464 | 0.094734 | -0.003205 | 0.066217 | 0.17079 | 0.027824 | 0.049311 | -0.025019 | 0.027795 | -0.010598 | 0.019715 | 0.091236 | 0.076815 | 0.052843 | 0.038422
3219.75 | 121.9757 | -0.07782 | 122.0535 | 0.14017 | -0.026784 | -0.016578 | -0.006703 | 0.031687 | 0.067269 | -0.035248 | 0.034174 | 0.13416 | -0.004219 | 0.012689 | -0.066219 | -0.017983 | -0.04722 | -0.00775 | 0.17221 | 0.005259 | 0.015465 | 0.02534 | 0.06373 | 0.099312 | -0.003205 | 0.066217 | 0.16621 | 0.027824 | 0.044732 | -0.034176 | 0.01406 | -0.015177 | 0.024293 | 0.10039 | 0.081394 | 0.062 | 0.043001
3221.5312 | 121.4172 | -0.059509 | 121.7926 | 0.13559 | -0.026784 | -0.025735 | -0.006703 | 0.040843 | 0.062691 | -0.039826 | 0.038752 | 0.13874 | -0.004219 | 0.012689 | -0.057062 | -0.017983 | -0.056376 | -0.00775 | 0.16763 | 0.005259 | 0.006308 | 0.02534 | 0.072886 | 0.094734 | -0.007783 | 0.070795 | 0.17079 | 0.027824 | 0.044732 | -0.025019 | 0.01406 | -0.024333 | 0.024293 | 0.095814 | 0.095128 | 0.052843 | 0.052157
3223.2344 | 121.4493 | -0.07782 | 121.8887 | 0.14017 | -0.022205 | -0.021157 | -0.002124 | 0.040843 | 0.076426 | -0.044405 | 0.034174 | 0.13874 | -0.004219 | 0.012689 | -0.057062 | -0.017983 | -0.042641 | -0.012328 | 0.17221 | 0.009838 | 0.010886 | 0.029919 | 0.072886 | 0.10847 | -0.012362 | 0.066217 | 0.17079 | 0.027824 | 0.044732 | -0.025019 | 0.01406 | -0.010598 | 0.019715 | 0.091236 | 0.076815 | 0.052843 | 0.038422
3225.0156 | 122.0718 | -0.07782 | 122.0673 | 0.13559 | -0.040521 | -0.021157 | -0.011281 | 0.040843 | 0.058113 | -0.039826 | 0.043331 | 0.13416 | -0.013376 | 0.012689 | -0.061641 | -0.013405 | -0.04722 | -0.012328 | 0.16763 | -0.008478 | 0.010886 | 0.020762 | 0.072886 | 0.090156 | -0.007783 | 0.075374 | 0.16621 | 0.018667 | 0.044732 | -0.029598 | 0.018638 | -0.015177 | 0.019715 | 0.10497 | 0.090551 | 0.048265 | 0.033844
3226.7188 | 122.0078 | -0.022888 | 121.962 | 0.14017 | -0.035942 | -0.016578 | -0.002124 | 0.040843 | 0.067269 | -0.039826 | 0.034174 | 0.1479 | -0.008798 | 0.012689 | -0.066219 | -0.017983 | -0.042641 | -0.012328 | 0.17221 | -0.003899 | 0.015465 | 0.029919 | 0.072886 | 0.099312 | -0.007783 | 0.066217 | 0.17994 | 0.023245 | 0.044732 | -0.034176 | 0.01406 | -0.010598 | 0.019715 | 0.10039 | 0.076815 | 0.057421 | 0.033843
3228.4844 | 112.1429 | 0.013733 | 121.3898 | 0.14474 | -0.022205 | -0.021157 | -0.011281 | 0.040843 | 0.067269 | -0.035248 | 0.038752 | 0.13874 | 0.000359 | 0.021847 | -0.057062 | -0.022561 | -0.051798 | -0.00775 | 0.17679 | 0.009838 | 0.010886 | 0.020762 | 0.072886 | 0.099312 | -0.003205 | 0.070795 | 0.17079 | 0.032402 | 0.05389 | -0.025019 | 0.009482 | -0.019755 | 0.024293 | 0.095814 | 0.09055 | 0.057421 | 0.052157
3230.1719 | 114.4043 | -0.032043 | 121.431 | 0.13559 | -0.031363 | -0.021157 | 0.002454 | 0.040843 | 0.067269 | -0.035248 | 0.034174 | 0.14332 | -0.008798 | 0.012689 | -0.061641 | -0.008827 | -0.051798 | -0.012328 | 0.16763 | 0.00068 | 0.010886 | 0.034497 | 0.072886 | 0.099312 | -0.003205 | 0.066217 | 0.17536 | 0.023245 | 0.044732 | -0.029598 | 0.023216 | -0.019755 | 0.019715 | 0.095815 | 0.085972 | 0.052843 | 0.043
3231.9375 | 122.1725 | -0.073242 | 121.8475 | 0.13101 | -0.026784 | -0.021157 | -0.006703 | 0.040843 | 0.067269 | -0.039826 | 0.034174 | 0.14332 | 0.000359 | 0.021847 | -0.061641 | -0.017983 | -0.04722 | -0.021484 | 0.16305 | 0.005259 | 0.010886 | 0.02534 | 0.072886 | 0.099312 | -0.007783 | 0.066217 | 0.17536 | 0.032402 | 0.05389 | -0.029598 | 0.01406 | -0.015177 | 0.010559 | 0.095815 | 0.081394 | 0.062 | 0.047579
3233.7031 | 122.2229 | -0.091553 | 121.9025 | 0.14017 | -0.026784 | -0.012 | -0.002124 | 0.040843 | 0.062691 | -0.035248 | 0.038752 | 0.14332 | -0.008798 | 0.021847 | -0.061641 | -0.008827 | -0.04722 | -0.021484 | 0.17221 | 0.005259 | 0.020043 | 0.029919 | 0.072886 | 0.094734 | -0.003205 | 0.070795 | 0.17536 | 0.023245 | 0.05389 | -0.029598 | 0.023216 | -0.015177 | 0.010559 | 0.10039 | 0.085972 | 0.052843 | 0.038422
3235.3906 | 119.5496 | -0.032043 | 121.4813 | 0.14017 | -0.031363 | -0.021157 | -0.011281 | 0.045421 | 0.071848 | -0.035248 | 0.038752 | 0.13874 | -0.004219 | 0.017268 | -0.066219 | -0.013405 | -0.04722 | -0.012328 | 0.17221 | 0.00068 | 0.010886 | 0.020762 | 0.077464 | 0.10389 | -0.003205 | 0.070795 | 0.17079 | 0.027824 | 0.049311 | -0.034176 | 0.018638 | -0.015177 | 0.019715 | 0.10497 | 0.085972 | 0.062 | 0.043001
3237.1562 | 117.2012 | -0.045776 | 121.4767 | 0.14474 | -0.031363 | -0.012 | -0.011281 | 0.040843 | 0.071848 | -0.035248 | 0.038752 | 0.13874 | -0.004219 | 0.017268 | -0.061641 | -0.008827 | -0.056376 | -0.016906 | 0.17679 | 0.00068 | 0.020043 | 0.020762 | 0.072886 | 0.10389 | -0.003205 | 0.070795 | 0.17079 | 0.027824 | 0.049311 | -0.029598 | 0.023216 | -0.024333 | 0.015137 | 0.10039 | 0.095128 | 0.057422 | 0.052157
3238.9219 | 122.0215 | -0.086975 | 122.0306 | 0.14017 | -0.026784 | -0.016578 | -0.011281 | 0.040843 | 0.067269 | -0.035248 | 0.038752 | 0.13874 | -0.004219 | 0.017268 | -0.052484 | -0.017983 | -0.042641 | -0.012328 | 0.17221 | 0.005259 | 0.015465 | 0.020762 | 0.072886 | 0.099312 | -0.003205 | 0.070795 | 0.17079 | 0.027824 | 0.049311 | -0.020441 | 0.01406 | -0.010598 | 0.019715 | 0.091236 | 0.081393 | 0.048265 | 0.038422
3240.6875 | 122.2961 | -0.050354 | 121.4035 | 0.14017 | -0.031363 | -0.021157 | -0.006703 | 0.049999 | 0.076426 | -0.03067 | 0.038752 | 0.13874 | -0.008798 | 0.00811 | -0.052484 | -0.017983 | -0.038063 | -0.016906 | 0.17221 | 0.00068 | 0.010886 | 0.02534 | 0.082042 | 0.10847 | 0.001373 | 0.070795 | 0.17079 | 0.023245 | 0.040153 | -0.020441 | 0.01406 | -0.00602 | 0.015137 | 0.091236 | 0.076815 | 0.043686 | 0.029265
3242.4531 | 122.2092 | -0.073242 | 121.6599 | 0.13559 | -0.026784 | -0.025735 | -0.002124 | 0.040843 | 0.067269 | -0.035248 | 0.038752 | 0.14332 | -0.008798 | 0.00811 | -0.066219 | -0.017983 | -0.04722 | -0.016906 | 0.16763 | 0.005259 | 0.006308 | 0.029919 | 0.072886 | 0.099312 | -0.003205 | 0.070795 | 0.17536 | 0.023245 | 0.040153 | -0.034176 | 0.01406 | -0.015177 | 0.015137 | 0.10497 | 0.085972 | 0.057421 | 0.038422
3244.1562 | 121.669 | -0.11444 | 121.9116 | 0.13559 | -0.026784 | -0.021157 | -0.006703 | 0.045421 | 0.067269 | -0.035248 | 0.038752 | 0.13416 | -0.008798 | -0.10179 | -0.052484 | -0.008827 | -0.04722 | -0.016906 | 0.16763 | 0.005259 | 0.010886 | 0.02534 | 0.077464 | 0.099312 | -0.003205 | 0.070795 | 0.16621 | 0.023245 | -0.069743 | -0.020441 | 0.023216 | -0.015177 | 0.015137 | 0.091236 | 0.085972 | 0.043686 | 0.038422
3245.9219 | 121.6461 | -0.10071 | 121.5088 | 0.13559 | -0.026784 | -0.030314 | 0.002454 | 0.045421 | 0.067269 | -0.035248 | 0.038752 | 0.13874 | -0.008798 | -0.10179 | -0.057062 | -0.013405 | -0.051798 | -0.016906 | 0.16763 | 0.005259 | 0.001729 | 0.034497 | 0.077464 | 0.099312 | -0.003205 | 0.070795 | 0.17079 | 0.023245 | -0.069743 | -0.025019 | 0.018638 | -0.019755 | 0.015137 | 0.095814 | 0.09055 | 0.048264 | 0.043
3247.7031 | 121.4584 | -0.12817 | 121.8933 | 0.13559 | -0.026784 | -0.012 | -0.002124 | 0.036265 | 0.071848 | -0.03067 | 0.043331 | 0.14332 | -0.004219 | -0.092628 | -0.061641 | -0.013405 | -0.051798 | -0.012328 | 0.16763 | 0.005259 | 0.020043 | 0.029919 | 0.068308 | 0.10389 | 0.001373 | 0.075374 | 0.17536 | 0.027824 | -0.060585 | -0.029598 | 0.018638 | -0.019755 | 0.019715 | 0.10497 | 0.095129 | 0.057422 | 0.047579
3249.4844 | 122.1954 | -0.073242 | 122.1497 | 0.13101 | -0.026784 | -0.021157 | -0.002124 | 0.040843 | 0.071848 | -0.048983 | 0.038752 | 0.13874 | -0.004219 | -0.10179 | -0.057062 | -0.013405 | -0.04722 | -0.016906 | 0.16305 | 0.005259 | 0.010886 | 0.029919 | 0.072886 | 0.10389 | -0.01694 | 0.070795 | 0.17079 | 0.027824 | -0.069743 | -0.025019 | 0.018638 | -0.015177 | 0.015137 | 0.095814 | 0.085972 | 0.052843 | 0.043001
3251.1719 | 121.6095 | -0.11444 | 121.8613 | 0.14474 | -0.035942 | -0.025735 | -0.006703 | 0.040843 | 0.071848 | -0.03067 | 0.038752 | 0.14332 | -0.004219 | -0.10637 | -0.057062 | -0.013405 | -0.042641 | -0.016906 | 0.17679 | -0.003899 | 0.006308 | 0.02534 | 0.072886 | 0.10389 | 0.001373 | 0.070795 | 0.17536 | 0.027824 | -0.074322 | -0.025019 | 0.018638 | -0.010598 | 0.015137 | 0.095814 | 0.081393 | 0.052843 | 0.038422
3252.9844 | 122.2916 | -0.073242 | 121.962 | 0.14474 | -0.031363 | -0.021157 | -0.006703 | 0.049999 | 0.071848 | -0.035248 | 0.043331 | 0.13874 | -0.004219 | -0.10179 | -0.057062 | -0.017983 | -0.042641 | -0.016906 | 0.17679 | 0.00068 | 0.010886 | 0.02534 | 0.082042 | 0.10389 | -0.003205 | 0.075374 | 0.17079 | 0.027824 | -0.069743 | -0.025019 | 0.01406 | -0.010598 | 0.015137 | 0.10039 | 0.085972 | 0.052843 | 0.038422
3256.1875 | 121.9482 | -0.10529 | 122.1497 | 0.13559 | -0.031363 | -0.012 | -0.006703 | 0.040843 | 0.076426 | -0.035248 | 0.038752 | 0.13874 | 0.004937 | -0.088049 | -0.061641 | -0.008827 | -0.04722 | -0.021484 | 0.16763 | 0.00068 | 0.020043 | 0.02534 | 0.072886 | 0.10847 | -0.003205 | 0.070795 | 0.17079 | 0.03698 | -0.056006 | -0.029598 | 0.023216 | -0.015177 | 0.010559 | 0.10039 | 0.085972 | 0.066578 | 0.052157
3260.4844 | 121.9528 | -0.086975 | 122.2 | 0.14017 | -0.026784 | -0.016578 | -0.011281 | 0.045421 | 0.071848 | -0.03067 | 0.038752 | 0.13416 | -0.004219 | -0.092628 | -0.061641 | -0.008827 | -0.04722 | -0.016906 | 0.17221 | 0.005259 | 0.015465 | 0.020762 | 0.077464 | 0.10389 | 0.001373 | 0.070795 | 0.16621 | 0.027824 | -0.060585 | -0.029598 | 0.023216 | -0.015177 | 0.015137 | 0.10039 | 0.085972 | 0.057422 | 0.043001
3266.3125 | 121.4767 | -0.091553 | 122.0581 | 0.14017 | -0.026784 | -0.025735 | -0.006703 | 0.040843 | 0.076426 | -0.035248 | 0.043331 | 0.12958 | 0.000359 | -0.092628 | -0.057062 | -0.013405 | -0.051798 | -0.012328 | 0.17221 | 0.005259 | 0.006308 | 0.02534 | 0.072886 | 0.10847 | -0.003205 | 0.075374 | 0.16163 | 0.032402 | -0.060585 | -0.025019 | 0.018638 | -0.019755 | 0.019715 | 0.10039 | 0.095129 | 0.057421 | 0.052157
3268 | 122.2321 | -0.07782 | 122.1863 | 0.14017 | -0.017627 | -0.021157 | -0.006703 | 0.036265 | 0.071848 | -0.035248 | 0.047909 | 0.1479 | -0.013376 | -0.10179 | -0.057062 | -0.008827 | -0.04722 | -0.016906 | 0.17221 | 0.014416 | 0.010886 | 0.02534 | 0.068308 | 0.10389 | -0.003205 | 0.079952 | 0.17994 | 0.018667 | -0.069743 | -0.025019 | 0.023216 | -0.015177 | 0.015137 | 0.10497 | 0.095129 | 0.043686 | 0.033844
3269.6875 | 121.5912 | -0.11902 | 122.2595 | 0.13101 | -0.022205 | -0.025735 | -0.006703 | 0.040843 | 0.071848 | -0.035248 | 0.038752 | 0.14332 | -0.004219 | -0.10637 | -0.066219 | -0.013405 | -0.042641 | -0.016906 | 0.16305 | 0.009838 | 0.006308 | 0.02534 | 0.072886 | 0.10389 | -0.003205 | 0.070795 | 0.17536 | 0.027824 | -0.074322 | -0.034176 | 0.018638 | -0.010598 | 0.015137 | 0.10497 | 0.081393 | 0.062 | 0.038422
3271.4531 | 121.7422 | -0.1236 | 122.2549 | 0.14017 | -0.022205 | -0.016578 | -0.002124 | 0.049999 | 0.076426 | -0.03067 | 0.043331 | 0.13874 | -0.013376 | -0.097207 | -0.057062 | -0.013405 | -0.04722 | -0.00775 | 0.17221 | 0.009838 | 0.015465 | 0.029919 | 0.082042 | 0.10847 | 0.001373 | 0.075374 | 0.17079 | 0.018667 | -0.065164 | -0.025019 | 0.018638 | -0.015177 | 0.024293 | 0.10039 | 0.090551 | 0.043686 | 0.033844
3273.2188 | 121.7514 | -0.10529 | 122.2275 | 0.13559 | -0.022205 | -0.012 | -0.011281 | 0.040843 | 0.071848 | -0.035248 | 0.043331 | 0.14332 | 0.000359 | -0.088049 | -0.052484 | -0.013405 | -0.04722 | -0.021484 | 0.16763 | 0.009838 | 0.020043 | 0.020762 | 0.072886 | 0.10389 | -0.003205 | 0.075374 | 0.17536 | 0.032402 | -0.056006 | -0.020441 | 0.018638 | -0.015177 | 0.010559 | 0.095815 | 0.090551 | 0.052843 | 0.047579
3274.9844 | 121.6187 | -0.09613 | 121.7377 | 0.13559 | -0.026784 | -0.021157 | -0.006703 | 0.040843 | 0.062691 | -0.035248 | 0.038752 | 0.13416 | 0.000359 | -0.097207 | -0.066219 | -0.004248 | -0.051798 | -0.016906 | 0.16763 | 0.005259 | 0.010886 | 0.02534 | 0.072886 | 0.094734 | -0.003205 | 0.070795 | 0.16621 | 0.032402 | -0.065164 | -0.034176 | 0.027795 | -0.019755 | 0.015137 | 0.10497 | 0.09055 | 0.066578 | 0.052157
3276.75 | 121.7834 | -0.10529 | 122.2458 | 0.14017 | -0.022205 | -0.021157 | 0.002454 | 0.040843 | 0.067269 | -0.035248 | 0.043331 | 0.13416 | -0.004219 | -0.097207 | -0.061641 | -0.013405 | -0.051798 | -0.012328 | 0.17221 | 0.009838 | 0.010886 | 0.034497 | 0.072886 | 0.099312 | -0.003205 | 0.075374 | 0.16621 | 0.027824 | -0.065164 | -0.029598 | 0.018638 | -0.019755 | 0.019715 | 0.10497 | 0.095129 | 0.057422 | 0.047579
3278.4531 | 122.374 | -0.07782 | 122.2229 | 0.14474 | -0.031363 | -0.016578 | -0.006703 | 0.036265 | 0.071848 | -0.03067 | 0.047909 | 0.13874 | -0.004219 | -0.10637 | -0.057062 | -0.008827 | -0.042641 | -0.021484 | 0.17679 | 0.00068 | 0.015465 | 0.02534 | 0.068308 | 0.10389 | 0.001373 | 0.079952 | 0.17079 | 0.027824 | -0.074322 | -0.025019 | 0.023216 | -0.010598 | 0.010559 | 0.10497 | 0.09055 | 0.052843 | 0.038422
3280.2188 | 121.9437 | -0.10529 | 122.2412 | 0.14017 | -0.022205 | -0.016578 | 0.002454 | 0.045421 | 0.067269 | -0.035248 | 0.043331 | 0.14332 | -0.008798 | -0.10637 | -0.057062 | -0.013405 | -0.042641 | -0.00775 | 0.17221 | 0.009838 | 0.015465 | 0.034497 | 0.077464 | 0.099312 | -0.003205 | 0.075374 | 0.17536 | 0.023245 | -0.074322 | -0.025019 | 0.018638 | -0.010598 | 0.024293 | 0.10039 | 0.085972 | 0.048264 | 0.033843
3281.9219 | 122.3602 | -0.059509 | 122.2183 | 0.13101 | -0.031363 | -0.025735 | -0.011281 | 0.036265 | 0.071848 | -0.035248 | 0.043331 | 0.14332 | -0.004219 | -0.092628 | -0.066219 | -0.013405 | -0.051798 | -0.012328 | 0.16305 | 0.00068 | 0.006308 | 0.020762 | 0.068308 | 0.10389 | -0.003205 | 0.075374 | 0.17536 | 0.027824 | -0.060585 | -0.034176 | 0.018638 | -0.019755 | 0.019715 | 0.10955 | 0.095129 | 0.062 | 0.047579
3283.7031 | 122.3969 | -0.07782 | 122.2183 | 0.14017 | -0.026784 | -0.012 | -0.006703 | 0.040843 | 0.071848 | -0.03067 | 0.038752 | 0.14332 | -0.004219 | -0.10637 | -0.057062 | -0.013405 | -0.056376 | -0.016906 | 0.17221 | 0.005259 | 0.020043 | 0.02534 | 0.072886 | 0.10389 | 0.001373 | 0.070795 | 0.17536 | 0.027824 | -0.074322 | -0.025019 | 0.018638 | -0.024333 | 0.015137 | 0.095814 | 0.095128 | 0.052843 | 0.052157
3285.4219 | 122.0306 | -0.11444 | 122.2824 | 0.13559 | -0.031363 | -0.021157 | -0.01586 | 0.045421 | 0.067269 | -0.035248 | 0.034174 | 0.13874 | 0.004937 | -0.097207 | -0.066219 | -0.017983 | -0.042641 | -0.016906 | 0.16763 | 0.00068 | 0.010886 | 0.016183 | 0.077464 | 0.099312 | -0.003205 | 0.066217 | 0.17079 | 0.03698 | -0.065164 | -0.034176 | 0.01406 | -0.010598 | 0.015137 | 0.10039 | 0.076815 | 0.071156 | 0.047578
3287.1875 | 122.0673 | -0.11902 | 122.2458 | 0.13559 | -0.026784 | -0.021157 | -0.002124 | 0.040843 | 0.062691 | -0.03067 | 0.034174 | 0.14332 | -0.013376 | -0.10637 | -0.061641 | -0.013405 | -0.04722 | -0.016906 | 0.16763 | 0.005259 | 0.010886 | 0.029919 | 0.072886 | 0.094734 | 0.001373 | 0.066217 | 0.17536 | 0.018667 | -0.074322 | -0.029598 | 0.018638 | -0.015177 | 0.015137 | 0.095815 | 0.081394 | 0.048265 | 0.033844
3288.8906 | 122.3785 | -0.09613 | 122.2321 | 0.13101 | -0.031363 | -0.016578 | -0.006703 | 0.036265 | 0.067269 | -0.03067 | 0.034174 | 0.14332 | -0.008798 | -0.08347 | -0.057062 | -0.017983 | -0.04722 | -0.016906 | 0.16305 | 0.00068 | 0.015465 | 0.02534 | 0.068308 | 0.099312 | 0.001373 | 0.066217 | 0.17536 | 0.023245 | -0.051427 | -0.025019 | 0.01406 | -0.015177 | 0.015137 | 0.091236 | 0.081394 | 0.048264 | 0.038422
3290.6719 | 122.374 | -0.09613 | 122.2137 | 0.14017 | -0.031363 | -0.021157 | -0.011281 | 0.045421 | 0.071848 | -0.035248 | 0.043331 | 0.14332 | -0.008798 | -0.10179 | -0.061641 | -0.008827 | -0.051798 | -0.00775 | 0.17221 | 0.00068 | 0.010886 | 0.020762 | 0.077464 | 0.10389 | -0.003205 | 0.075374 | 0.17536 | 0.023245 | -0.069743 | -0.029598 | 0.023216 | -0.019755 | 0.024293 | 0.10497 | 0.095129 | 0.052843 | 0.043
3292.3594 | 121.8613 | -0.11444 | 121.6599 | 0.13101 | -0.026784 | -0.012 | -0.006703 | 0.040843 | 0.071848 | -0.039826 | 0.038752 | 0.1479 | -0.004219 | -0.10179 | -0.057062 | -0.013405 | -0.04722 | -0.016906 | 0.16305 | 0.005259 | 0.020043 | 0.02534 | 0.072886 | 0.10389 | -0.007783 | 0.070795 | 0.17994 | 0.027824 | -0.069743 | -0.025019 | 0.018638 | -0.015177 | 0.015137 | 0.095814 | 0.085972 | 0.052843 | 0.043001
3294.1094 | 122.374 | -0.082397 | 122.2458 | 0.13101 | -0.026784 | -0.025735 | -0.002124 | 0.040843 | 0.071848 | -0.039826 | 0.043331 | 0.13874 | 0.000359 | -0.10179 | -0.057062 | -0.013405 | -0.056376 | -0.012328 | 0.16305 | 0.005259 | 0.006308 | 0.029919 | 0.072886 | 0.10389 | -0.007783 | 0.075374 | 0.17079 | 0.032402 | -0.069743 | -0.025019 | 0.018638 | -0.024333 | 0.019715 | 0.10039 | 0.099707 | 0.057421 | 0.056735
3295.8125 | 122.4197 | -0.059509 | 122.2595 | 0.14017 | -0.031363 | -0.025735 | -0.011281 | 0.045421 | 0.067269 | -0.044405 | 0.034174 | 0.14332 | -0.004219 | -0.097207 | -0.052484 | -0.017983 | -0.04722 | -0.012328 | 0.17221 | 0.00068 | 0.006308 | 0.020762 | 0.077464 | 0.099312 | -0.012362 | 0.066217 | 0.17536 | 0.027824 | -0.065164 | -0.020441 | 0.01406 | -0.015177 | 0.019715 | 0.086658 | 0.081394 | 0.048265 | 0.043001
3297.5625 | 122.4106 | -0.068665 | 122.2549 | 0.13559 | -0.026784 | -0.021157 | -0.002124 | 0.040843 | 0.067269 | -0.039826 | 0.047909 | 0.13874 | -0.004219 | -0.10637 | -0.061641 | -0.008827 | -0.042641 | -0.012328 | 0.16763 | 0.005259 | 0.010886 | 0.029919 | 0.072886 | 0.099312 | -0.007783 | 0.079952 | 0.17079 | 0.027824 | -0.074322 | -0.029598 | 0.023216 | -0.010598 | 0.019715 | 0.10955 | 0.09055 | 0.057422 | 0.038422
3299.3281 | 122.4564 | -0.073242 | 122.2504 | 0.13559 | -0.035942 | -0.021157 | -0.002124 | 0.045421 | 0.071848 | -0.039826 | 0.038752 | 0.12958 | -0.004219 | -0.092628 | -0.061641 | -0.013405 | -0.042641 | -0.00775 | 0.16763 | -0.003899 | 0.010886 | 0.029919 | 0.077464 | 0.10389 | -0.007783 | 0.070795 | 0.16163 | 0.027824 | -0.060585 | -0.029598 | 0.018638 | -0.010598 | 0.024293 | 0.10039 | 0.081393 | 0.057422 | 0.038422
3301.1094 | 122.3785 | -0.091553 | 122.2595 | 0.14017 | -0.031363 | -0.016578 | -0.006703 | 0.045421 | 0.067269 | -0.035248 | 0.043331 | 0.13874 | -0.008798 | -0.10179 | -0.061641 | -0.022561 | -0.04722 | -0.021484 | 0.17221 | 0.00068 | 0.015465 | 0.02534 | 0.077464 | 0.099312 | -0.003205 | 0.075374 | 0.17079 | 0.023245 | -0.069743 | -0.029598 | 0.009482 | -0.015177 | 0.010559 | 0.10497 | 0.090551 | 0.052843 | 0.038422
3302.8125 | 122.0535 | -0.11902 | 121.8796 | 0.12643 | -0.026784 | -0.021157 | -0.002124 | 0.045421 | 0.067269 | -0.035248 | 0.038752 | 0.13874 | 0.000359 | -0.10179 | -0.061641 | -0.013405 | -0.051798 | -0.016906 | 0.15847 | 0.005259 | 0.010886 | 0.029919 | 0.077464 | 0.099312 | -0.003205 | 0.070795 | 0.17079 | 0.032402 | -0.069743 | -0.029598 | 0.018638 | -0.019755 | 0.015137 | 0.10039 | 0.09055 | 0.062 | 0.052157
3304.5781 | 121.8475 | -0.11444 | 121.5637 | 0.13101 | -0.026784 | -0.021157 | -0.011281 | 0.045421 | 0.067269 | -0.035248 | 0.038752 | 0.14332 | 0.000359 | -0.097207 | -0.057062 | -0.013405 | -0.051798 | -0.016906 | 0.16305 | 0.005259 | 0.010886 | 0.020762 | 0.077464 | 0.099312 | -0.003205 | 0.070795 | 0.17536 | 0.032402 | -0.065164 | -0.025019 | 0.018638 | -0.019755 | 0.015137 | 0.095814 | 0.09055 | 0.057421 | 0.052157
3306.3594 | 122.4152 | -0.07782 | 122.2229 | 0.14017 | -0.022205 | -0.016578 | -0.002124 | 0.049999 | 0.067269 | -0.035248 | 0.047909 | 0.14332 | -0.004219 | -0.10637 | -0.052484 | -0.013405 | -0.04722 | -0.021484 | 0.17221 | 0.009838 | 0.015465 | 0.029919 | 0.082042 | 0.099312 | -0.003205 | 0.079952 | 0.17536 | 0.027824 | -0.074322 | -0.020441 | 0.018638 | -0.015177 | 0.010559 | 0.10039 | 0.095129 | 0.048265 | 0.043001
3308.125 | 121.8338 | -0.10529 | 121.6965 | 0.13559 | -0.022205 | -0.025735 | -0.006703 | 0.036265 | 0.076426 | -0.03067 | 0.043331 | 0.12958 | 0.000359 | -0.10637 | -0.061641 | -0.013405 | -0.042641 | -0.021484 | 0.16763 | 0.009838 | 0.006308 | 0.02534 | 0.068308 | 0.10847 | 0.001373 | 0.075374 | 0.16163 | 0.032402 | -0.074322 | -0.029598 | 0.018638 | -0.010598 | 0.010559 | 0.10497 | 0.085972 | 0.062 | 0.043
3309.8906 | 122.4152 | -0.09613 | 122.2824 | 0.13101 | -0.031363 | -0.016578 | -0.006703 | 0.045421 | 0.067269 | -0.039826 | 0.038752 | 0.13874 | 0.000359 | -0.10179 | -0.061641 | -0.013405 | -0.04722 | -0.016906 | 0.16305 | 0.00068 | 0.015465 | 0.02534 | 0.077464 | 0.099312 | -0.007783 | 0.070795 | 0.17079 | 0.032402 | -0.069743 | -0.029598 | 0.018638 | -0.015177 | 0.015137 | 0.10039 | 0.085972 | 0.062 | 0.047579
3311.5938 | 122.4426 | -0.068665 | 122.049 | 0.14017 | -0.031363 | -0.025735 | -0.011281 | 0.036265 | 0.081005 | -0.035248 | 0.038752 | 0.15248 | -0.004219 | -0.10179 | -0.061641 | -0.008827 | -0.051798 | -0.012328 | 0.17221 | 0.00068 | 0.006308 | 0.020762 | 0.068308 | 0.11305 | -0.003205 | 0.070795 | 0.18452 | 0.027824 | -0.069743 | -0.029598 | 0.023216 | -0.019755 | 0.019715 | 0.10039 | 0.09055 | 0.057422 | 0.047579
3313.2812 | 122.4152 | -0.086975 | 122.3099 | 0.14017 | -0.026784 | -0.007421 | -0.006703 | 0.045421 | 0.067269 | -0.035248 | 0.047909 | 0.1479 | 0.000359 | -0.10637 | -0.070797 | -0.013405 | -0.04722 | -0.012328 | 0.17221 | 0.005259 | 0.024622 | 0.02534 | 0.077464 | 0.099312 | -0.003205 | 0.079952 | 0.17994 | 0.032402 | -0.074322 | -0.038754 | 0.018638 | -0.015177 | 0.019715 | 0.11871 | 0.095129 | 0.071156 | 0.047579
3315.0469 | 122.0078 | -0.10071 | 122.3328 | 0.14474 | -0.022205 | -0.016578 | -0.006703 | 0.049999 | 0.067269 | -0.035248 | 0.043331 | 0.14332 | -0.008798 | -0.097207 | -0.061641 | -0.013405 | -0.042641 | -0.016906 | 0.17679 | 0.009838 | 0.015465 | 0.02534 | 0.082042 | 0.099312 | -0.003205 | 0.075374 | 0.17536 | 0.023245 | -0.065164 | -0.029598 | 0.018638 | -0.010598 | 0.015137 | 0.10497 | 0.085972 | 0.052843 | 0.033843
3316.8125 | 122.4106 | -0.082397 | 122.2916 | 0.13559 | -0.022205 | -0.021157 | -0.002124 | 0.045421 | 0.067269 | -0.035248 | 0.043331 | 0.1479 | -0.008798 | -0.092628 | -0.057062 | -0.017983 | -0.051798 | -0.012328 | 0.16763 | 0.009838 | 0.010886 | 0.029919 | 0.077464 | 0.099312 | -0.003205 | 0.075374 | 0.17994 | 0.023245 | -0.060585 | -0.025019 | 0.01406 | -0.019755 | 0.019715 | 0.10039 | 0.095129 | 0.048264 | 0.043
3318.5781 | 122.3099 | -0.11902 | 122.319 | 0.13559 | -0.022205 | -0.012 | -0.011281 | 0.049999 | 0.067269 | -0.035248 | 0.043331 | 0.1479 | -0.008798 | -0.10179 | -0.061641 | -0.013405 | -0.04722 | -0.016906 | 0.16763 | 0.009838 | 0.020043 | 0.020762 | 0.082042 | 0.099312 | -0.003205 | 0.075374 | 0.17994 | 0.023245 | -0.069743 | -0.029598 | 0.018638 | -0.015177 | 0.015137 | 0.10497 | 0.090551 | 0.052843 | 0.038422
3320.2812 | 122.2412 | -0.11902 | 122.2916 | 0.14017 | -0.026784 | -0.016578 | -0.011281 | 0.036265 | 0.062691 | -0.039826 | 0.038752 | 0.1479 | -0.008798 | -0.10637 | -0.057062 | -0.013405 | -0.042641 | -0.016906 | 0.17221 | 0.005259 | 0.015465 | 0.020762 | 0.068308 | 0.094734 | -0.007783 | 0.070795 | 0.17994 | 0.023245 | -0.074322 | -0.025019 | 0.018638 | -0.010598 | 0.015137 | 0.095814 | 0.081393 | 0.048264 | 0.033843
3322.0625 | 122.1588 | -0.13275 | 121.9254 | 0.12643 | -0.026784 | -0.016578 | -0.002124 | 0.045421 | 0.062691 | -0.026092 | 0.038752 | 0.13874 | -0.004219 | -0.092628 | -0.061641 | -0.017983 | -0.04722 | -0.016906 | 0.15847 | 0.005259 | 0.015465 | 0.029919 | 0.077464 | 0.094734 | 0.005951 | 0.070795 | 0.17079 | 0.027824 | -0.060585 | -0.029598 | 0.01406 | -0.015177 | 0.015137 | 0.10039 | 0.085972 | 0.057422 | 0.043001
3323.7656 | 122.3511 | -0.09613 | 121.9757 | 0.14017 | -0.022205 | -0.016578 | -0.006703 | 0.049999 | 0.067269 | -0.039826 | 0.043331 | 0.14332 | -0.008798 | -0.10179 | -0.061641 | -0.013405 | -0.051798 | -0.012328 | 0.17221 | 0.009838 | 0.015465 | 0.02534 | 0.082042 | 0.099312 | -0.007783 | 0.075374 | 0.17536 | 0.023245 | -0.069743 | -0.029598 | 0.018638 | -0.019755 | 0.019715 | 0.10497 | 0.095129 | 0.052843 | 0.043
3325.4688 | 122.4289 | -0.064087 | 122.2961 | 0.14017 | -0.022205 | -0.021157 | -0.011281 | 0.049999 | 0.062691 | -0.035248 | 0.043331 | 0.13874 | -0.013376 | -0.10637 | -0.061641 | -0.022561 | -0.042641 | -0.016906 | 0.17221 | 0.009838 | 0.010886 | 0.020762 | 0.082042 | 0.094734 | -0.003205 | 0.075374 | 0.17079 | 0.018667 | -0.074322 | -0.029598 | 0.009482 | -0.010598 | 0.015137 | 0.10497 | 0.085972 | 0.048265 | 0.029265
3327.2344 | 122.0215 | -0.09613 | 122.3511 | 0.14474 | -0.022205 | -0.012 | -0.006703 | 0.045421 | 0.067269 | -0.039826 | 0.038752 | 0.1479 | -0.004219 | -0.10637 | -0.061641 | -0.013405 | -0.042641 | -0.021484 | 0.17679 | 0.009838 | 0.020043 | 0.02534 | 0.077464 | 0.099312 | -0.007783 | 0.070795 | 0.17994 | 0.027824 | -0.074322 | -0.029598 | 0.018638 | -0.010598 | 0.010559 | 0.10039 | 0.081393 | 0.057422 | 0.038422
3329 | 122.4243 | -0.07782 | 122.3145 | 0.14017 | -0.031363 | -0.016578 | -0.002124 | 0.040843 | 0.067269 | -0.039826 | 0.043331 | 0.14332 | -0.008798 | -0.097207 | -0.057062 | -0.013405 | -0.042641 | -0.012328 | 0.17221 | 0.00068 | 0.015465 | 0.029919 | 0.072886 | 0.099312 | -0.007783 | 0.075374 | 0.17536 | 0.023245 | -0.065164 | -0.025019 | 0.018638 | -0.010598 | 0.019715 | 0.10039 | 0.085972 | 0.048264 | 0.033843
3330.7031 | 122.1863 | -0.11902 | 122.3419 | 0.13101 | -0.026784 | -0.025735 | -0.011281 | 0.040843 | 0.076426 | -0.035248 | 0.047909 | 0.13874 | -0.004219 | -0.097207 | -0.066219 | -0.013405 | -0.051798 | -0.012328 | 0.16305 | 0.005259 | 0.006308 | 0.020762 | 0.072886 | 0.10847 | -0.003205 | 0.079952 | 0.17079 | 0.027824 | -0.065164 | -0.034176 | 0.018638 | -0.019755 | 0.019715 | 0.11413 | 0.099707 | 0.062 | 0.047579
3332.4219 | 122.4792 | -0.050354 | 122.3053 | 0.14017 | -0.022205 | -0.016578 | -0.006703 | 0.040843 | 0.062691 | -0.039826 | 0.043331 | 0.13874 | -0.008798 | -0.10179 | -0.057062 | -0.013405 | -0.056376 | -0.016906 | 0.17221 | 0.009838 | 0.015465 | 0.02534 | 0.072886 | 0.094734 | -0.007783 | 0.075374 | 0.17079 | 0.023245 | -0.069743 | -0.025019 | 0.018638 | -0.024333 | 0.015137 | 0.10039 | 0.099707 | 0.048264 | 0.047578
3334.1875 | 122.4838 | -0.059509 | 122.3282 | 0.14017 | -0.031363 | -0.025735 | -0.011281 | 0.036265 | 0.067269 | -0.035248 | 0.038752 | 0.13416 | -0.008798 | -0.074312 | -0.057062 | -0.008827 | -0.051798 | -0.016906 | 0.17221 | 0.00068 | 0.006308 | 0.020762 | 0.068308 | 0.099312 | -0.003205 | 0.070795 | 0.16621 | 0.023245 | -0.042269 | -0.025019 | 0.023216 | -0.019755 | 0.015137 | 0.095814 | 0.09055 | 0.048264 | 0.043
3335.8906 | 122.4426 | -0.073242 | 122.3419 | 0.13559 | -0.026784 | -0.021157 | -0.006703 | 0.040843 | 0.062691 | -0.03067 | 0.043331 | 0.14332 | -0.013376 | -0.10179 | -0.066219 | -0.004248 | -0.056376 | -0.021484 | 0.16763 | 0.005259 | 0.010886 | 0.02534 | 0.072886 | 0.094734 | 0.001373 | 0.075374 | 0.17536 | 0.018667 | -0.069743 | -0.034176 | 0.027795 | -0.024333 | 0.010559 | 0.10955 | 0.099707 | 0.052843 | 0.043
3337.6562 | 122.3557 | -0.1236 | 122.3831 | 0.14017 | -0.022205 | -0.021157 | -0.006703 | 0.049999 | 0.071848 | -0.039826 | 0.038752 | 0.13416 | 0.000359 | -0.097207 | -0.061641 | -0.004248 | -0.051798 | -0.016906 | 0.17221 | 0.009838 | 0.010886 | 0.02534 | 0.082042 | 0.10389 | -0.007783 | 0.070795 | 0.16621 | 0.032402 | -0.065164 | -0.029598 | 0.027795 | -0.019755 | 0.015137 | 0.10039 | 0.09055 | 0.062 | 0.052157
3339.3438 | 122.438 | -0.07782 | 122.3419 | 0.13559 | -0.035942 | -0.021157 | -0.011281 | 0.045421 | 0.062691 | -0.035248 | 0.038752 | 0.13874 | -0.013376 | -0.10637 | -0.057062 | -0.013405 | -0.04722 | -0.021484 | 0.16763 | -0.003899 | 0.010886 | 0.020762 | 0.077464 | 0.094734 | -0.003205 | 0.070795 | 0.17079 | 0.018667 | -0.074322 | -0.025019 | 0.018638 | -0.015177 | 0.010559 | 0.095814 | 0.085972 | 0.043686 | 0.033844
3341.125 | 122.374 | -0.13275 | 122.3602 | 0.14017 | -0.026784 | -0.012 | -0.006703 | 0.045421 | 0.076426 | -0.044405 | 0.047909 | 0.1479 | -0.004219 | -0.10637 | -0.066219 | -0.013405 | -0.04722 | -0.016906 | 0.17221 | 0.005259 | 0.020043 | 0.02534 | 0.077464 | 0.10847 | -0.012362 | 0.079952 | 0.17994 | 0.027824 | -0.074322 | -0.034176 | 0.018638 | -0.015177 | 0.015137 | 0.11413 | 0.095129 | 0.062 | 0.043001
3342.8906 | 122.2549 | -0.10071 | 122.2778 | 0.13559 | -0.022205 | -0.012 | -0.006703 | 0.045421 | 0.071848 | -0.035248 | 0.043331 | 0.13874 | -0.004219 | -0.097207 | -0.052484 | -0.017983 | -0.04722 | -0.021484 | 0.16763 | 0.009838 | 0.020043 | 0.02534 | 0.077464 | 0.10389 | -0.003205 | 0.075374 | 0.17079 | 0.027824 | -0.065164 | -0.020441 | 0.01406 | -0.015177 | 0.010559 | 0.095815 | 0.090551 | 0.048265 | 0.043001
3344.6406 | 122.4564 | -0.064087 | 122.3328 | 0.13559 | -0.026784 | -0.021157 | -0.006703 | 0.045421 | 0.071848 | -0.035248 | 0.043331 | 0.14332 | 0.004937 | -0.10179 | -0.057062 | -0.013405 | -0.051798 | -0.016906 | 0.16763 | 0.005259 | 0.010886 | 0.02534 | 0.077464 | 0.10389 | -0.003205 | 0.075374 | 0.17536 | 0.03698 | -0.069743 | -0.025019 | 0.018638 | -0.019755 | 0.015137 | 0.10039 | 0.095129 | 0.061999 | 0.056735
3346.3438 | 122.3648 | -0.091553 | 122.374 | 0.13559 | -0.031363 | -0.021157 | -0.011281 | 0.049999 | 0.067269 | -0.026092 | 0.043331 | 0.14332 | 0.000359 | -0.11094 | -0.057062 | -0.013405 | -0.04722 | -0.016906 | 0.16763 | 0.00068 | 0.010886 | 0.020762 | 0.082042 | 0.099312 | 0.005951 | 0.075374 | 0.17536 | 0.032402 | -0.078901 | -0.025019 | 0.018638 | -0.015177 | 0.015137 | 0.10039 | 0.090551 | 0.057421 | 0.047579
3348.1094 | 122.3648 | -0.10986 | 122.3969 | 0.14474 | -0.031363 | -0.021157 | -0.006703 | 0.049999 | 0.071848 | -0.039826 | 0.043331 | 0.13874 | -0.004219 | -0.10179 | -0.061641 | -0.013405 | -0.042641 | -0.016906 | 0.17679 | 0.00068 | 0.010886 | 0.02534 | 0.082042 | 0.10389 | -0.007783 | 0.075374 | 0.17079 | 0.027824 | -0.069743 | -0.029598 | 0.018638 | -0.010598 | 0.015137 | 0.10497 | 0.085972 | 0.057422 | 0.038422
3349.8594 | 122.3877 | -0.11444 | 122.3694 | 0.13559 | -0.022205 | -0.025735 | -0.011281 | 0.045421 | 0.076426 | -0.03067 | 0.038752 | 0.13874 | -0.004219 | -0.10637 | -0.066219 | -0.017983 | -0.04722 | -0.012328 | 0.16763 | 0.009838 | 0.006308 | 0.020762 | 0.077464 | 0.10847 | 0.001373 | 0.070795 | 0.17079 | 0.027824 | -0.074322 | -0.034176 | 0.01406 | -0.015177 | 0.019715 | 0.10497 | 0.085972 | 0.062 | 0.043001
3351.6094 | 122.5113 | -0.059509 | 122.3694 | 0.14017 | -0.031363 | -0.025735 | -0.011281 | 0.040843 | 0.071848 | -0.039826 | 0.038752 | 0.14332 | -0.004219 | -0.10179 | -0.061641 | -0.008827 | -0.04722 | -0.016906 | 0.17221 | 0.00068 | 0.006308 | 0.020762 | 0.072886 | 0.10389 | -0.007783 | 0.070795 | 0.17536 | 0.027824 | -0.069743 | -0.029598 | 0.023216 | -0.015177 | 0.015137 | 0.10039 | 0.085972 | 0.057422 | 0.043001
3353.3281 | 122.3923 | -0.10529 | 122.3877 | 0.13559 | -0.031363 | -0.016578 | -0.002124 | 0.040843 | 0.067269 | -0.035248 | 0.047909 | 0.13874 | 0.000359 | -0.08347 | -0.066219 | -0.008827 | -0.038063 | -0.016906 | 0.16763 | 0.00068 | 0.015465 | 0.029919 | 0.072886 | 0.099312 | -0.003205 | 0.079952 | 0.17079 | 0.032402 | -0.051427 | -0.034176 | 0.023216 | -0.00602 | 0.015137 | 0.11413 | 0.085972 | 0.066578 | 0.038422
3355.0625 | 122.3877 | -0.11902 | 122.3785 | 0.14017 | -0.026784 | -0.021157 | -0.011281 | 0.045421 | 0.067269 | -0.03067 | 0.043331 | 0.13874 | -0.008798 | -0.11094 | -0.061641 | -0.008827 | -0.04722 | -0.016906 | 0.17221 | 0.005259 | 0.010886 | 0.020762 | 0.077464 | 0.099312 | 0.001373 | 0.075374 | 0.17079 | 0.023245 | -0.078901 | -0.029598 | 0.023216 | -0.015177 | 0.015137 | 0.10497 | 0.090551 | 0.052843 | 0.038422
3356.8281 | 122.3602 | -0.10071 | 122.3694 | 0.13101 | -0.026784 | -0.016578 | -0.006703 | 0.049999 | 0.071848 | -0.035248 | 0.043331 | 0.1479 | 0.000359 | -0.10637 | -0.052484 | -0.008827 | -0.04722 | -0.021484 | 0.16305 | 0.005259 | 0.015465 | 0.02534 | 0.082042 | 0.10389 | -0.003205 | 0.075374 | 0.17994 | 0.032402 | -0.074322 | -0.020441 | 0.023216 | -0.015177 | 0.010559 | 0.095815 | 0.090551 | 0.052843 | 0.047579
3358.5938 | 122.4655 | -0.07782 | 122.3694 | 0.13559 | -0.026784 | -0.030314 | -0.002124 | 0.036265 | 0.067269 | -0.039826 | 0.043331 | 0.14332 | -0.008798 | -0.088049 | -0.061641 | -0.013405 | -0.051798 | -0.016906 | 0.16763 | 0.005259 | 0.001729 | 0.029919 | 0.068308 | 0.099312 | -0.007783 | 0.075374 | 0.17536 | 0.023245 | -0.056006 | -0.029598 | 0.018638 | -0.019755 | 0.015137 | 0.10497 | 0.095129 | 0.052843 | 0.043
3360.2812 | 122.438 | -0.1236 | 122.3923 | 0.13559 | -0.031363 | -0.016578 | -0.006703 | 0.040843 | 0.076426 | -0.03067 | 0.043331 | 0.13874 | -0.008798 | -0.10179 | -0.057062 | -0.008827 | -0.04722 | -0.016906 | 0.16763 | 0.00068 | 0.015465 | 0.02534 | 0.072886 | 0.10847 | 0.001373 | 0.075374 | 0.17079 | 0.023245 | -0.069743 | -0.025019 | 0.023216 | -0.015177 | 0.015137 | 0.10039 | 0.090551 | 0.048264 | 0.038422
3362.0469 | 122.3923 | -0.10071 | 122.2504 | 0.13559 | -0.026784 | -0.021157 | -0.002124 | 0.045421 | 0.071848 | -0.026092 | 0.047909 | 0.1479 | -0.004219 | -0.092628 | -0.061641 | -0.017983 | -0.042641 | -0.012328 | 0.16763 | 0.005259 | 0.010886 | 0.029919 | 0.077464 | 0.10389 | 0.005951 | 0.079952 | 0.17994 | 0.027824 | -0.060585 | -0.029598 | 0.01406 | -0.010598 | 0.019715 | 0.10955 | 0.09055 | 0.057422 | 0.038422
3363.8125 | 122.4014 | -0.10529 | 122.1909 | 0.14017 | -0.026784 | -0.016578 | -0.006703 | 0.045421 | 0.067269 | -0.026092 | 0.038752 | 0.14332 | 0.004937 | -0.078891 | -0.066219 | -0.017983 | -0.042641 | -0.016906 | 0.17221 | 0.005259 | 0.015465 | 0.02534 | 0.077464 | 0.099312 | 0.005951 | 0.070795 | 0.17536 | 0.03698 | -0.046848 | -0.034176 | 0.01406 | -0.010598 | 0.015137 | 0.10497 | 0.081393 | 0.071156 | 0.047578
3365.5781 | 122.319 | -0.10986 | 122.1771 | 0.13559 | -0.026784 | -0.025735 | -0.006703 | 0.049999 | 0.067269 | -0.039826 | 0.038752 | 0.13874 | -0.004219 | -0.10179 | -0.061641 | -0.008827 | -0.04722 | -0.016906 | 0.16763 | 0.005259 | 0.006308 | 0.02534 | 0.082042 | 0.099312 | -0.007783 | 0.070795 | 0.17079 | 0.027824 | -0.069743 | -0.029598 | 0.023216 | -0.015177 | 0.015137 | 0.10039 | 0.085972 | 0.057422 | 0.043001
3367.2969 | 122.2275 | -0.10529 | 122.3785 | 0.13559 | -0.026784 | -0.012 | -0.006703 | 0.045421 | 0.071848 | -0.035248 | 0.052488 | 0.13874 | 0.004937 | -0.097207 | -0.057062 | -0.008827 | -0.04722 | -0.016906 | 0.16763 | 0.005259 | 0.020043 | 0.02534 | 0.077464 | 0.10389 | -0.003205 | 0.084531 | 0.17079 | 0.03698 | -0.065164 | -0.025019 | 0.023216 | -0.015177 | 0.015137 | 0.10955 | 0.099708 | 0.061999 | 0.052157
3369 | 122.4701 | -0.082397 | 122.406 | 0.13559 | -0.031363 | -0.021157 | -0.002124 | 0.049999 | 0.076426 | -0.03067 | 0.038752 | 0.14332 | -0.004219 | -0.097207 | -0.057062 | -0.004248 | -0.04722 | -0.021484 | 0.16763 | 0.00068 | 0.010886 | 0.029919 | 0.082042 | 0.10847 | 0.001373 | 0.070795 | 0.17536 | 0.027824 | -0.065164 | -0.025019 | 0.027795 | -0.015177 | 0.010559 | 0.095814 | 0.085972 | 0.052843 | 0.043001
3370.7031 | 122.3465 | -0.086975 | 122.4014 | 0.14017 | -0.026784 | -0.016578 | -0.011281 | 0.045421 | 0.067269 | -0.039826 | 0.043331 | 0.14332 | -0.004219 | -0.088049 | -0.061641 | -0.008827 | -0.04722 | -0.021484 | 0.17221 | 0.005259 | 0.015465 | 0.020762 | 0.077464 | 0.099312 | -0.007783 | 0.075374 | 0.17536 | 0.027824 | -0.056006 | -0.029598 | 0.023216 | -0.015177 | 0.010559 | 0.10497 | 0.090551 | 0.057422 | 0.043001
3372.4531 | 122.4518 | -0.082397 | 122.406 | 0.13559 | -0.026784 | -0.025735 | -0.011281 | 0.036265 | 0.062691 | -0.039826 | 0.043331 | 0.14332 | -0.004219 | -0.097207 | -0.061641 | -0.017983 | -0.04722 | -0.012328 | 0.16763 | 0.005259 | 0.006308 | 0.020762 | 0.068308 | 0.094734 | -0.007783 | 0.075374 | 0.17536 | 0.027824 | -0.065164 | -0.029598 | 0.01406 | -0.015177 | 0.019715 | 0.10497 | 0.090551 | 0.057422 | 0.043001
3374.1562 | 122.5433 | -0.059509 | 122.3831 | 0.13101 | -0.026784 | -0.021157 | -0.006703 | 0.040843 | 0.071848 | -0.039826 | 0.043331 | 0.1479 | -0.004219 | -0.10637 | -0.057062 | -0.008827 | -0.04722 | -0.016906 | 0.16305 | 0.005259 | 0.010886 | 0.02534 | 0.072886 | 0.10389 | -0.007783 | 0.075374 | 0.17994 | 0.027824 | -0.074322 | -0.025019 | 0.023216 | -0.015177 | 0.015137 | 0.10039 | 0.090551 | 0.052843 | 0.043001
3375.9219 | 122.4472 | -0.11902 | 122.4426 | 0.14474 | -0.026784 | -0.016578 | -0.002124 | 0.040843 | 0.067269 | -0.03067 | 0.038752 | 0.14332 | -0.004219 | -0.10637 | -0.061641 | -0.008827 | -0.042641 | -0.016906 | 0.17679 | 0.005259 | 0.015465 | 0.029919 | 0.072886 | 0.099312 | 0.001373 | 0.070795 | 0.17536 | 0.027824 | -0.074322 | -0.029598 | 0.023216 | -0.010598 | 0.015137 | 0.10039 | 0.081393 | 0.057422 | 0.038422
3377.6875 | 122.4197 | -0.10986 | 122.438 | 0.13559 | -0.031363 | -0.025735 | -0.006703 | 0.049999 | 0.071848 | -0.03067 | 0.047909 | 0.14332 | -0.004219 | -0.10637 | -0.061641 | -0.013405 | -0.04722 | -0.016906 | 0.16763 | 0.00068 | 0.006308 | 0.02534 | 0.082042 | 0.10389 | 0.001373 | 0.079952 | 0.17536 | 0.027824 | -0.074322 | -0.029598 | 0.018638 | -0.015177 | 0.015137 | 0.10955 | 0.095129 | 0.057422 | 0.043001
3379.4375 | 122.4655 | -0.09613 | 122.438 | 0.14017 | -0.026784 | -0.016578 | -0.006703 | 0.049999 | 0.076426 | -0.03067 | 0.043331 | 0.14332 | -0.008798 | -0.097207 | -0.057062 | -0.017983 | -0.051798 | -0.012328 | 0.17221 | 0.005259 | 0.015465 | 0.02534 | 0.082042 | 0.10847 | 0.001373 | 0.075374 | 0.17536 | 0.023245 | -0.065164 | -0.025019 | 0.01406 | -0.019755 | 0.019715 | 0.10039 | 0.095129 | 0.048264 | 0.043
3381.1406 | 122.5525 | -0.086975 | 122.3831 | 0.14474 | -0.026784 | -0.012 | -0.011281 | 0.045421 | 0.067269 | -0.035248 | 0.043331 | 0.14332 | -0.004219 | -0.10637 | -0.057062 | -0.008827 | -0.042641 | -0.016906 | 0.17679 | 0.005259 | 0.020043 | 0.020762 | 0.077464 | 0.099312 | -0.003205 | 0.075374 | 0.17536 | 0.027824 | -0.074322 | -0.025019 | 0.023216 | -0.010598 | 0.015137 | 0.10039 | 0.085972 | 0.052843 | 0.038422
3382.9062 | 122.4884 | -0.09613 | 122.438 | 0.13559 | -0.022205 | -0.021157 | -0.006703 | 0.036265 | 0.067269 | -0.035248 | 0.043331 | 0.1479 | -0.008798 | -0.10179 | -0.061641 | -0.013405 | -0.04722 | -0.016906 | 0.16763 | 0.009838 | 0.010886 | 0.02534 | 0.068308 | 0.099312 | -0.003205 | 0.075374 | 0.17994 | 0.023245 | -0.069743 | -0.029598 | 0.018638 | -0.015177 | 0.015137 | 0.10497 | 0.090551 | 0.052843 | 0.038422
3384.6562 | 122.5296 | -0.086975 | 122.4243 | 0.14017 | -0.017627 | -0.016578 | -0.002124 | 0.049999 | 0.067269 | -0.035248 | 0.047909 | 0.14332 | -0.004219 | -0.097207 | -0.057062 | -0.013405 | -0.04722 | -0.021484 | 0.17221 | 0.014416 | 0.015465 | 0.029919 | 0.082042 | 0.099312 | -0.003205 | 0.079952 | 0.17536 | 0.027824 | -0.065164 | -0.025019 | 0.018638 | -0.015177 | 0.010559 | 0.10497 | 0.095129 | 0.052843 | 0.043001
3386.4062 | 122.58 | -0.064087 | 122.3831 | 0.14017 | -0.026784 | -0.012 | -0.002124 | 0.045421 | 0.071848 | -0.035248 | 0.043331 | 0.1479 | -0.004219 | -0.092628 | -0.057062 | -0.013405 | -0.056376 | -0.016906 | 0.17221 | 0.005259 | 0.020043 | 0.029919 | 0.077464 | 0.10389 | -0.003205 | 0.075374 | 0.17994 | 0.027824 | -0.060585 | -0.025019 | 0.018638 | -0.024333 | 0.015137 | 0.10039 | 0.099707 | 0.052843 | 0.052157
3388.1094 | 122.5296 | -0.086975 | 122.3877 | 0.14017 | -0.031363 | -0.016578 | -0.002124 | 0.045421 | 0.062691 | -0.035248 | 0.043331 | 0.14332 | -0.004219 | -0.10637 | -0.061641 | -0.017983 | -0.051798 | -0.012328 | 0.17221 | 0.00068 | 0.015465 | 0.029919 | 0.077464 | 0.094734 | -0.003205 | 0.075374 | 0.17536 | 0.027824 | -0.074322 | -0.029598 | 0.01406 | -0.019755 | 0.019715 | 0.10497 | 0.095129 | 0.057422 | 0.047579
3389.8594 | 122.3694 | -0.10071 | 122.4518 | 0.14017 | -0.022205 | -0.016578 | -0.006703 | 0.045421 | 0.067269 | -0.039826 | 0.043331 | 0.13874 | -0.017954 | -0.11094 | -0.061641 | -0.008827 | -0.04722 | -0.021484 | 0.17221 | 0.009838 | 0.015465 | 0.02534 | 0.077464 | 0.099312 | -0.007783 | 0.075374 | 0.17079 | 0.014089 | -0.078901 | -0.029598 | 0.023216 | -0.015177 | 0.010559 | 0.10497 | 0.090551 | 0.043687 | 0.029266
3391.625 | 122.5113 | -0.09613 | 122.4197 | 0.13101 | -0.022205 | -0.016578 | -0.011281 | 0.040843 | 0.062691 | -0.044405 | 0.047909 | 0.13874 | -0.008798 | -0.097207 | -0.057062 | -0.008827 | -0.04722 | -0.016906 | 0.16305 | 0.009838 | 0.015465 | 0.020762 | 0.072886 | 0.094734 | -0.012362 | 0.079952 | 0.17079 | 0.023245 | -0.065164 | -0.025019 | 0.023216 | -0.015177 | 0.015137 | 0.10497 | 0.095129 | 0.048264 | 0.038422
3393.3281 | 122.5845 | -0.068665 | 122.4106 | 0.14017 | -0.022205 | -0.016578 | 0.002454 | 0.049999 | 0.071848 | -0.035248 | 0.047909 | 0.14332 | -0.004219 | -0.092628 | -0.052484 | -0.008827 | -0.051798 | -0.016906 | 0.17221 | 0.009838 | 0.015465 | 0.034497 | 0.082042 | 0.10389 | -0.003205 | 0.079952 | 0.17536 | 0.027824 | -0.060585 | -0.020441 | 0.023216 | -0.019755 | 0.015137 | 0.10039 | 0.099707 | 0.048265 | 0.047579
3395.0781 | 122.5616 | -0.073242 | 122.4243 | 0.14017 | -0.031363 | -0.021157 | -0.002124 | 0.049999 | 0.062691 | -0.035248 | 0.043331 | 0.1479 | 0.000359 | -0.097207 | -0.066219 | -0.013405 | -0.04722 | -0.021484 | 0.17221 | 0.00068 | 0.010886 | 0.029919 | 0.082042 | 0.094734 | -0.003205 | 0.075374 | 0.17994 | 0.032402 | -0.065164 | -0.034176 | 0.018638 | -0.015177 | 0.010559 | 0.10955 | 0.090551 | 0.066578 | 0.047579
3396.8438 | 122.5342 | -0.091553 | 122.4197 | 0.14017 | -0.026784 | -0.030314 | -0.011281 | 0.045421 | 0.067269 | -0.035248 | 0.043331 | 0.13874 | -0.004219 | -0.097207 | -0.057062 | -0.008827 | -0.04722 | -0.00775 | 0.17221 | 0.005259 | 0.001729 | 0.020762 | 0.077464 | 0.099312 | -0.003205 | 0.075374 | 0.17079 | 0.027824 | -0.065164 | -0.025019 | 0.023216 | -0.015177 | 0.024293 | 0.10039 | 0.090551 | 0.052843 | 0.043001
3398.6094 | 122.5662 | -0.050354 | 122.406 | 0.13101 | -0.022205 | -0.021157 | -0.011281 | 0.045421 | 0.071848 | -0.03067 | 0.047909 | 0.15248 | -0.008798 | -0.11094 | -0.057062 | -0.013405 | -0.042641 | -0.016906 | 0.16305 | 0.009838 | 0.010886 | 0.020762 | 0.077464 | 0.10389 | 0.001373 | 0.079952 | 0.18452 | 0.023245 | -0.078901 | -0.025019 | 0.018638 | -0.010598 | 0.015137 | 0.10497 | 0.09055 | 0.048264 | 0.033843
3400.2969 | 122.4701 | -0.11902 | 122.4747 | 0.13559 | -0.017627 | -0.021157 | -0.002124 | 0.040843 | 0.062691 | -0.03067 | 0.043331 | 0.14332 | -0.004219 | -0.092628 | -0.066219 | -0.008827 | -0.04722 | -0.00775 | 0.16763 | 0.014416 | 0.010886 | 0.029919 | 0.072886 | 0.094734 | 0.001373 | 0.075374 | 0.17536 | 0.027824 | -0.060585 | -0.034176 | 0.023216 | -0.015177 | 0.024293 | 0.10955 | 0.090551 | 0.062 | 0.043001
3402.0625 | 122.4747 | -0.10986 | 122.4518 | 0.13101 | -0.022205 | -0.016578 | -0.002124 | 0.049999 | 0.071848 | -0.035248 | 0.043331 | 0.1479 | 0.000359 | -0.11094 | -0.061641 | -0.008827 | -0.04722 | -0.012328 | 0.16305 | 0.009838 | 0.015465 | 0.029919 | 0.082042 | 0.10389 | -0.003205 | 0.075374 | 0.17994 | 0.032402 | -0.078901 | -0.029598 | 0.023216 | -0.015177 | 0.019715 | 0.10497 | 0.090551 | 0.062 | 0.047579
3403.8125 | 122.5983 | -0.054932 | 122.4197 | 0.13559 | -0.026784 | -0.025735 | -0.011281 | 0.040843 | 0.067269 | -0.039826 | 0.038752 | 0.1479 | -0.004219 | -0.10637 | -0.061641 | -0.013405 | -0.04722 | -0.021484 | 0.16763 | 0.005259 | 0.006308 | 0.020762 | 0.072886 | 0.099312 | -0.007783 | 0.070795 | 0.17994 | 0.027824 | -0.074322 | -0.029598 | 0.018638 | -0.015177 | 0.010559 | 0.10039 | 0.085972 | 0.057422 | 0.043001
3405.5625 | 122.4655 | -0.11444 | 122.4426 | 0.14017 | -0.022205 | -0.016578 | -0.002124 | 0.045421 | 0.071848 | -0.03067 | 0.038752 | 0.15248 | -0.004219 | -0.10637 | -0.061641 | -0.013405 | -0.04722 | -0.016906 | 0.17221 | 0.009838 | 0.015465 | 0.029919 | 0.077464 | 0.10389 | 0.001373 | 0.070795 | 0.18452 | 0.027824 | -0.074322 | -0.029598 | 0.018638 | -0.015177 | 0.015137 | 0.10039 | 0.085972 | 0.057422 | 0.043001
3407.2656 | 122.3648 | -0.091553 | 122.0535 | 0.13101 | -0.022205 | -0.021157 | -0.002124 | 0.054577 | 0.067269 | -0.044405 | 0.043331 | 0.1479 | 0.009515 | -0.10637 | -0.052484 | -0.008827 | -0.04722 | -0.016906 | 0.16305 | 0.009838 | 0.010886 | 0.029919 | 0.08662 | 0.099312 | -0.012362 | 0.075374 | 0.17994 | 0.041558 | -0.074322 | -0.020441 | 0.023216 | -0.015177 | 0.015137 | 0.095815 | 0.090551 | 0.061999 | 0.056735
3409.0312 | 122.5342 | -0.086975 | 122.4518 | 0.13559 | -0.031363 | -0.016578 | -0.011281 | 0.049999 | 0.062691 | -0.039826 | 0.043331 | 0.13874 | 0.000359 | -0.097207 | -0.057062 | -0.013405 | -0.042641 | -0.012328 | 0.16763 | 0.00068 | 0.015465 | 0.020762 | 0.082042 | 0.094734 | -0.007783 | 0.075374 | 0.17079 | 0.032402 | -0.065164 | -0.025019 | 0.018638 | -0.010598 | 0.019715 | 0.10039 | 0.085972 | 0.057421 | 0.043
3410.7344 | 122.438 | -0.091553 | 122.4564 | 0.14017 | -0.026784 | -0.016578 | -0.002124 | 0.045421 | 0.076426 | -0.03067 | 0.047909 | 0.13874 | -0.008798 | -0.10179 | -0.057062 | -0.008827 | -0.051798 | -0.016906 | 0.17221 | 0.005259 | 0.015465 | 0.029919 | 0.077464 | 0.10847 | 0.001373 | 0.079952 | 0.17079 | 0.023245 | -0.069743 | -0.025019 | 0.023216 | -0.019755 | 0.015137 | 0.10497 | 0.099707 | 0.048264 | 0.043
3412.5 | 122.5754 | -0.050354 | 122.4426 | 0.13559 | -0.026784 | -0.021157 | -0.006703 | 0.040843 | 0.067269 | -0.044405 | 0.043331 | 0.1479 | 0.000359 | -0.10179 | -0.057062 | -0.008827 | -0.04722 | -0.016906 | 0.16763 | 0.005259 | 0.010886 | 0.02534 | 0.072886 | 0.099312 | -0.012362 | 0.075374 | 0.17994 | 0.032402 | -0.069743 | -0.025019 | 0.023216 | -0.015177 | 0.015137 | 0.10039 | 0.090551 | 0.057421 | 0.047579
3414.2656 | 122.5937 | -0.050354 | 122.4426 | 0.13559 | -0.026784 | -0.021157 | -0.006703 | 0.040843 | 0.071848 | -0.035248 | 0.047909 | 0.1479 | 0.000359 | -0.10179 | -0.061641 | -0.004248 | -0.04722 | -0.016906 | 0.16763 | 0.005259 | 0.010886 | 0.02534 | 0.072886 | 0.10389 | -0.003205 | 0.079952 | 0.17994 | 0.032402 | -0.069743 | -0.029598 | 0.027795 | -0.015177 | 0.015137 | 0.10955 | 0.095129 | 0.062 | 0.047579
3416.0312 | 122.5113 | -0.11902 | 122.4838 | 0.13101 | -0.022205 | -0.012 | -0.006703 | 0.045421 | 0.067269 | -0.035248 | 0.047909 | 0.13416 | 0.000359 | -0.092628 | -0.052484 | -0.013405 | -0.051798 | -0.016906 | 0.16305 | 0.009838 | 0.020043 | 0.02534 | 0.077464 | 0.099312 | -0.003205 | 0.079952 | 0.16621 | 0.032402 | -0.060585 | -0.020441 | 0.018638 | -0.019755 | 0.015137 | 0.10039 | 0.099707 | 0.052843 | 0.052157
3417.7344 | 122.6074 | -0.082397 | 122.4289 | 0.13559 | -0.035942 | -0.025735 | -0.011281 | 0.045421 | 0.071848 | -0.03067 | 0.052488 | 0.14332 | 0.009515 | -0.097207 | -0.057062 | -0.013405 | -0.04722 | -0.021484 | 0.16763 | -0.003899 | 0.006308 | 0.020762 | 0.077464 | 0.10389 | 0.001373 | 0.084531 | 0.17536 | 0.041558 | -0.065164 | -0.025019 | 0.018638 | -0.015177 | 0.010559 | 0.10955 | 0.099708 | 0.066577 | 0.056735
3419.5 | 122.4884 | -0.09613 | 122.4655 | 0.13101 | -0.022205 | -0.016578 | -0.006703 | 0.049999 | 0.076426 | -0.035248 | 0.043331 | 0.14332 | 0.004937 | -0.092628 | -0.057062 | -0.022561 | -0.038063 | -0.016906 | 0.16305 | 0.009838 | 0.015465 | 0.02534 | 0.082042 | 0.10847 | -0.003205 | 0.075374 | 0.17536 | 0.03698 | -0.060585 | -0.025019 | 0.009482 | -0.00602 | 0.015137 | 0.10039 | 0.081394 | 0.061999 | 0.043
3421.2031 | 122.5021 | -0.10529 | 122.4838 | 0.13101 | -0.031363 | -0.025735 | -0.01586 | 0.045421 | 0.067269 | -0.035248 | 0.052488 | 0.1479 | 0.009515 | -0.11094 | -0.066219 | -0.013405 | -0.051798 | -0.012328 | 0.16305 | 0.00068 | 0.006308 | 0.016183 | 0.077464 | 0.099312 | -0.003205 | 0.084531 | 0.17994 | 0.041558 | -0.078901 | -0.034176 | 0.018638 | -0.019755 | 0.019715 | 0.11871 | 0.10429 | 0.075734 | 0.061313
3422.9531 | 122.5983 | -0.068665 | 122.4335 | 0.14474 | -0.031363 | -0.021157 | -0.002124 | 0.040843 | 0.067269 | -0.039826 | 0.047909 | 0.1479 | 0.000359 | -0.092628 | -0.057062 | -0.008827 | -0.051798 | -0.016906 | 0.17679 | 0.00068 | 0.010886 | 0.029919 | 0.072886 | 0.099312 | -0.007783 | 0.079952 | 0.17994 | 0.032402 | -0.060585 | -0.025019 | 0.023216 | -0.019755 | 0.015137 | 0.10497 | 0.099707 | 0.057421 | 0.052157
3424.7031 | 122.4838 | -0.09613 | 122.4564 | 0.13559 | -0.026784 | -0.016578 | 0.002454 | 0.049999 | 0.067269 | -0.044405 | 0.052488 | 0.15248 | -0.004219 | -0.10179 | -0.057062 | -0.013405 | -0.042641 | -0.021484 | 0.16763 | 0.005259 | 0.015465 | 0.034497 | 0.082042 | 0.099312 | -0.012362 | 0.084531 | 0.18452 | 0.027824 | -0.069743 | -0.025019 | 0.018638 | -0.010598 | 0.010559 | 0.10955 | 0.095129 | 0.052843 | 0.038422
3426.4531 | 122.6028 | -0.068665 | 122.4518 | 0.13559 | -0.026784 | -0.025735 | -0.011281 | 0.045421 | 0.071848 | -0.03067 | 0.038752 | 0.14332 | 0.004937 | -0.10179 | -0.057062 | -0.013405 | -0.04722 | -0.016906 | 0.16763 | 0.005259 | 0.006308 | 0.020762 | 0.077464 | 0.10389 | 0.001373 | 0.070795 | 0.17536 | 0.03698 | -0.069743 | -0.025019 | 0.018638 | -0.015177 | 0.015137 | 0.095814 | 0.085972 | 0.061999 | 0.052157
3428.1719 | 122.5616 | -0.086975 | 122.4609 | 0.14017 | -0.017627 | -0.016578 | -0.006703 | 0.049999 | 0.076426 | -0.035248 | 0.043331 | 0.1479 | 0.000359 | -0.10637 | -0.061641 | -0.013405 | -0.042641 | -0.021484 | 0.17221 | 0.014416 | 0.015465 | 0.02534 | 0.082042 | 0.10847 | -0.003205 | 0.075374 | 0.17994 | 0.032402 | -0.074322 | -0.029598 | 0.018638 | -0.010598 | 0.010559 | 0.10497 | 0.085972 | 0.062 | 0.043
3429.9375 | 122.6395 | -0.050354 | 122.4564 | 0.13559 | -0.026784 | -0.025735 | -0.011281 | 0.040843 | 0.067269 | -0.03067 | 0.047909 | 0.14332 | 0.000359 | -0.097207 | -0.061641 | -0.008827 | -0.042641 | -0.016906 | 0.16763 | 0.005259 | 0.006308 | 0.020762 | 0.072886 | 0.099312 | 0.001373 | 0.079952 | 0.17536 | 0.032402 | -0.065164 | -0.029598 | 0.023216 | -0.010598 | 0.015137 | 0.10955 | 0.09055 | 0.062 | 0.043
3431.6875 | 122.5113 | -0.10071 | 122.4976 | 0.13101 | -0.031363 | -0.016578 | -0.006703 | 0.049999 | 0.067269 | -0.035248 | 0.047909 | 0.13874 | -0.004219 | -0.097207 | -0.052484 | -0.004248 | -0.051798 | -0.016906 | 0.16305 | 0.00068 | 0.015465 | 0.02534 | 0.082042 | 0.099312 | -0.003205 | 0.079952 | 0.17079 | 0.027824 | -0.065164 | -0.020441 | 0.027795 | -0.019755 | 0.015137 | 0.10039 | 0.099707 | 0.048265 | 0.047579
3433.4688 | 122.4884 | -0.11444 | 122.5342 | 0.14474 | -0.031363 | -0.021157 | -0.006703 | 0.045421 | 0.076426 | -0.03067 | 0.052488 | 0.1479 | -0.004219 | -0.10179 | -0.061641 | -0.008827 | -0.051798 | -0.026063 | 0.17679 | 0.00068 | 0.010886 | 0.02534 | 0.077464 | 0.10847 | 0.001373 | 0.084531 | 0.17994 | 0.027824 | -0.069743 | -0.029598 | 0.023216 | -0.019755 | 0.00598 | 0.11413 | 0.10429 | 0.057422 | 0.047579
3435.2188 | 122.612 | -0.07782 | 122.4792 | 0.14017 | -0.031363 | -0.025735 | -0.011281 | 0.045421 | 0.062691 | -0.035248 | 0.043331 | 0.14332 | -0.004219 | -0.092628 | -0.061641 | -0.008827 | -0.056376 | -0.016906 | 0.17221 | 0.00068 | 0.006308 | 0.020762 | 0.077464 | 0.094734 | -0.003205 | 0.075374 | 0.17536 | 0.027824 | -0.060585 | -0.029598 | 0.023216 | -0.024333 | 0.015137 | 0.10497 | 0.099707 | 0.057422 | 0.052157
3436.9219 | 122.5845 | -0.059509 | 122.4655 | 0.12643 | -0.031363 | -0.025735 | -0.011281 | 0.049999 | 0.071848 | -0.044405 | 0.057066 | 0.14332 | 0.000359 | -0.10637 | -0.043328 | -0.013405 | -0.042641 | -0.012328 | 0.15847 | 0.00068 | 0.006308 | 0.020762 | 0.082042 | 0.10389 | -0.012362 | 0.089109 | 0.17536 | 0.032402 | -0.074322 | -0.011285 | 0.018638 | -0.010598 | 0.019715 | 0.10039 | 0.099707 | 0.043687 | 0.043
3438.7031 | 122.4884 | -0.10529 | 122.525 | 0.13559 | -0.022205 | -0.021157 | -0.002124 | 0.049999 | 0.076426 | -0.035248 | 0.043331 | 0.14332 | 0.000359 | -0.11094 | -0.052484 | -0.004248 | -0.04722 | -0.012328 | 0.16763 | 0.009838 | 0.010886 | 0.029919 | 0.082042 | 0.10847 | -0.003205 | 0.075374 | 0.17536 | 0.032402 | -0.078901 | -0.020441 | 0.027795 | -0.015177 | 0.019715 | 0.095815 | 0.090551 | 0.052843 | 0.047579
3440.4062 | 122.5983 | -0.068665 | 122.4747 | 0.13559 | -0.031363 | -0.016578 | -0.006703 | 0.036265 | 0.071848 | -0.035248 | 0.047909 | 0.13874 | 0.000359 | -0.11094 | -0.057062 | -0.017983 | -0.042641 | -0.016906 | 0.16763 | 0.00068 | 0.015465 | 0.02534 | 0.068308 | 0.10389 | -0.003205 | 0.079952 | 0.17079 | 0.032402 | -0.078901 | -0.025019 | 0.01406 | -0.010598 | 0.015137 | 0.10497 | 0.09055 | 0.057421 | 0.043
3442.1719 | 122.58 | -0.10529 | 122.4701 | 0.12643 | -0.026784 | -0.021157 | -0.006703 | 0.045421 | 0.071848 | -0.039826 | 0.052488 | 0.1479 | -0.008798 | -0.10637 | -0.061641 | -0.004248 | -0.04722 | -0.012328 | 0.15847 | 0.005259 | 0.010886 | 0.02534 | 0.077464 | 0.10389 | -0.007783 | 0.084531 | 0.17994 | 0.023245 | -0.074322 | -0.029598 | 0.027795 | -0.015177 | 0.019715 | 0.11413 | 0.099708 | 0.052843 | 0.038422
3443.9375 | 122.6486 | -0.064087 | 122.4747 | 0.13101 | -0.026784 | -0.021157 | -0.006703 | 0.049999 | 0.067269 | -0.035248 | 0.047909 | 0.1479 | 0.000359 | -0.097207 | -0.057062 | -0.008827 | -0.051798 | -0.016906 | 0.16305 | 0.005259 | 0.010886 | 0.02534 | 0.082042 | 0.099312 | -0.003205 | 0.079952 | 0.17994 | 0.032402 | -0.065164 | -0.025019 | 0.023216 | -0.019755 | 0.015137 | 0.10497 | 0.099707 | 0.057421 | 0.052157
3445.6875 | 122.5525 | -0.10529 | 122.5159 | 0.12643 | -0.022205 | -0.016578 | 0.002454 | 0.049999 | 0.062691 | -0.039826 | 0.047909 | 0.1479 | 0.004937 | -0.097207 | -0.061641 | -0.004248 | -0.042641 | -0.021484 | 0.15847 | 0.009838 | 0.015465 | 0.034497 | 0.082042 | 0.094734 | -0.007783 | 0.079952 | 0.17994 | 0.03698 | -0.065164 | -0.029598 | 0.027795 | -0.010598 | 0.010559 | 0.10955 | 0.09055 | 0.066578 | 0.047578
3447.3906 | 122.5983 | -0.059509 | 122.4609 | 0.13101 | -0.022205 | -0.021157 | -0.006703 | 0.045421 | 0.071848 | -0.039826 | 0.047909 | 0.1479 | -0.008798 | -0.11094 | -0.052484 | -0.004248 | -0.056376 | -0.012328 | 0.16305 | 0.009838 | 0.010886 | 0.02534 | 0.077464 | 0.10389 | -0.007783 | 0.079952 | 0.17994 | 0.023245 | -0.078901 | -0.020441 | 0.027795 | -0.024333 | 0.019715 | 0.10039 | 0.10429 | 0.043686 | 0.047578
3449.1562 | 122.6395 | -0.091553 | 122.493 | 0.14017 | -0.026784 | -0.021157 | -0.002124 | 0.049999 | 0.071848 | -0.035248 | 0.038752 | 0.14332 | -0.004219 | -0.10179 | -0.057062 | -0.008827 | -0.042641 | -0.012328 | 0.17221 | 0.005259 | 0.010886 | 0.029919 | 0.082042 | 0.10389 | -0.003205 | 0.070795 | 0.17536 | 0.027824 | -0.069743 | -0.025019 | 0.023216 | -0.010598 | 0.019715 | 0.095814 | 0.081393 | 0.052843 | 0.038422
3450.8594 | 122.6212 | -0.064087 | 122.4655 | 0.13559 | -0.026784 | -0.016578 | -0.006703 | 0.049999 | 0.062691 | -0.039826 | 0.043331 | 0.13874 | -0.004219 | -0.10637 | -0.061641 | -0.017983 | -0.04722 | -0.012328 | 0.16763 | 0.005259 | 0.015465 | 0.02534 | 0.082042 | 0.094734 | -0.007783 | 0.075374 | 0.17079 | 0.027824 | -0.074322 | -0.029598 | 0.01406 | -0.015177 | 0.019715 | 0.10497 | 0.090551 | 0.057422 | 0.043001
3452.625 | 122.6074 | -0.086975 | 122.4747 | 0.13559 | -0.026784 | -0.016578 | 0.002454 | 0.049999 | 0.067269 | -0.03067 | 0.043331 | 0.15248 | 0.000359 | -0.097207 | -0.061641 | -0.008827 | -0.04722 | -0.016906 | 0.16763 | 0.005259 | 0.015465 | 0.034497 | 0.082042 | 0.099312 | 0.001373 | 0.075374 | 0.18452 | 0.032402 | -0.065164 | -0.029598 | 0.023216 | -0.015177 | 0.015137 | 0.10497 | 0.090551 | 0.062 | 0.047579
3454.4062 | 122.6578 | -0.041199 | 122.4701 | 0.13101 | -0.031363 | -0.021157 | -0.006703 | 0.045421 | 0.067269 | -0.039826 | 0.052488 | 0.14332 | -0.008798 | -0.10179 | -0.057062 | -0.013405 | -0.04722 | -0.016906 | 0.16305 | 0.00068 | 0.010886 | 0.02534 | 0.077464 | 0.099312 | -0.007783 | 0.084531 | 0.17536 | 0.023245 | -0.069743 | -0.025019 | 0.018638 | -0.015177 | 0.015137 | 0.10955 | 0.099708 | 0.048264 | 0.038422
3456.1875 | 122.5433 | -0.11902 | 122.5388 | 0.13559 | -0.031363 | -0.021157 | -0.002124 | 0.049999 | 0.071848 | -0.035248 | 0.043331 | 0.1479 | 0.000359 | -0.10179 | -0.061641 | -0.013405 | -0.051798 | -0.012328 | 0.16763 | 0.00068 | 0.010886 | 0.029919 | 0.082042 | 0.10389 | -0.003205 | 0.075374 | 0.17994 | 0.032402 | -0.069743 | -0.029598 | 0.018638 | -0.019755 | 0.019715 | 0.10497 | 0.095129 | 0.062 | 0.052157
3457.8906 | 122.6395 | -0.068665 | 122.4564 | 0.13559 | -0.031363 | -0.025735 | -0.006703 | 0.040843 | 0.071848 | -0.03067 | 0.047909 | 0.14332 | 0.009515 | -0.10179 | -0.052484 | -0.008827 | -0.04722 | -0.016906 | 0.16763 | 0.00068 | 0.006308 | 0.02534 | 0.072886 | 0.10389 | 0.001373 | 0.079952 | 0.17536 | 0.041558 | -0.069743 | -0.020441 | 0.023216 | -0.015177 | 0.015137 | 0.10039 | 0.095129 | 0.061999 | 0.056735
3459.6562 | 122.525 | -0.11444 | 122.4976 | 0.13559 | -0.031363 | -0.021157 | -0.011281 | 0.045421 | 0.071848 | -0.03067 | 0.047909 | 0.1479 | -0.008798 | -0.10637 | -0.052484 | -0.017983 | -0.04722 | -0.012328 | 0.16763 | 0.00068 | 0.010886 | 0.020762 | 0.077464 | 0.10389 | 0.001373 | 0.079952 | 0.17994 | 0.023245 | -0.074322 | -0.020441 | 0.01406 | -0.015177 | 0.019715 | 0.10039 | 0.095129 | 0.043686 | 0.038422
3461.4219 | 122.5571 | -0.082397 | 122.5433 | 0.13101 | -0.022205 | -0.002842 | -0.002124 | 0.049999 | 0.071848 | -0.039826 | 0.038752 | 0.14332 | -0.004219 | -0.10637 | -0.066219 | -0.013405 | -0.051798 | -0.016906 | 0.16305 | 0.009838 | 0.029201 | 0.029919 | 0.082042 | 0.10389 | -0.007783 | 0.070795 | 0.17536 | 0.027824 | -0.074322 | -0.034176 | 0.018638 | -0.019755 | 0.015137 | 0.10497 | 0.09055 | 0.062 | 0.047579
3463.1875 | 122.6212 | -0.082397 | 122.5067 | 0.13559 | -0.026784 | -0.021157 | -0.002124 | 0.045421 | 0.071848 | -0.026092 | 0.047909 | 0.14332 | 0.000359 | -0.10179 | -0.061641 | -0.008827 | -0.042641 | -0.012328 | 0.16763 | 0.005259 | 0.010886 | 0.029919 | 0.077464 | 0.10389 | 0.005951 | 0.079952 | 0.17536 | 0.032402 | -0.069743 | -0.029598 | 0.023216 | -0.010598 | 0.019715 | 0.10955 | 0.09055 | 0.062 | 0.043
3464.9375 | 122.5708 | -0.09613 | 122.4838 | 0.14017 | -0.022205 | -0.016578 | -0.006703 | 0.049999 | 0.067269 | -0.035248 | 0.047909 | 0.1479 | -0.004219 | -0.10637 | -0.057062 | -0.013405 | -0.051798 | -0.012328 | 0.17221 | 0.009838 | 0.015465 | 0.02534 | 0.082042 | 0.099312 | -0.003205 | 0.079952 | 0.17994 | 0.027824 | -0.074322 | -0.025019 | 0.018638 | -0.019755 | 0.019715 | 0.10497 | 0.099707 | 0.052843 | 0.047579
3466.6406 | 122.5388 | -0.1236 | 122.5113 | 0.13559 | -0.022205 | -0.025735 | -0.002124 | 0.049999 | 0.071848 | -0.03067 | 0.047909 | 0.1479 | 0.004937 | -0.10637 | -0.057062 | -0.013405 | -0.04722 | -0.016906 | 0.16763 | 0.009838 | 0.006308 | 0.029919 | 0.082042 | 0.10389 | 0.001373 | 0.079952 | 0.17994 | 0.03698 | -0.074322 | -0.025019 | 0.018638 | -0.015177 | 0.015137 | 0.10497 | 0.095129 | 0.061999 | 0.052157
3468.4062 | 122.6578 | -0.068665 | 122.5204 | 0.13559 | -0.035942 | -0.007421 | -0.006703 | 0.045421 | 0.076426 | -0.03067 | 0.043331 | 0.1479 | 0.000359 | -0.08347 | -0.061641 | -0.013405 | -0.051798 | -0.012328 | 0.16763 | -0.003899 | 0.024622 | 0.02534 | 0.077464 | 0.10847 | 0.001373 | 0.075374 | 0.17994 | 0.032402 | -0.051427 | -0.029598 | 0.018638 | -0.019755 | 0.019715 | 0.10497 | 0.095129 | 0.062 | 0.052157
3470.1094 | 122.4976 | -0.11902 | 122.5525 | 0.14017 | -0.022205 | -0.025735 | -0.011281 | 0.045421 | 0.067269 | -0.035248 | 0.047909 | 0.14332 | 0.004937 | -0.10637 | -0.057062 | -0.013405 | -0.042641 | -0.021484 | 0.17221 | 0.009838 | 0.006308 | 0.020762 | 0.077464 | 0.099312 | -0.003205 | 0.079952 | 0.17536 | 0.03698 | -0.074322 | -0.025019 | 0.018638 | -0.010598 | 0.010559 | 0.10497 | 0.09055 | 0.061999 | 0.047578
3471.8594 | 122.5296 | -0.11902 | 122.5433 | 0.13559 | -0.031363 | -0.016578 | -0.006703 | 0.045421 | 0.067269 | -0.035248 | 0.043331 | 0.14332 | -0.004219 | -0.10179 | -0.057062 | -0.008827 | -0.051798 | -0.012328 | 0.16763 | 0.00068 | 0.015465 | 0.02534 | 0.077464 | 0.099312 | -0.003205 | 0.075374 | 0.17536 | 0.027824 | -0.069743 | -0.025019 | 0.023216 | -0.019755 | 0.019715 | 0.10039 | 0.095129 | 0.052843 | 0.047579
3473.6406 | 122.6212 | -0.07782 | 122.5113 | 0.13559 | -0.031363 | -0.025735 | -0.002124 | 0.049999 | 0.071848 | -0.035248 | 0.052488 | 0.1479 | 0.004937 | -0.10637 | -0.057062 | -0.013405 | -0.051798 | -0.012328 | 0.16763 | 0.00068 | 0.006308 | 0.029919 | 0.082042 | 0.10389 | -0.003205 | 0.084531 | 0.17994 | 0.03698 | -0.074322 | -0.025019 | 0.018638 | -0.019755 | 0.019715 | 0.10955 | 0.10429 | 0.061999 | 0.056735
3475.3438 | 122.5754 | -0.10529 | 122.5708 | 0.14017 | -0.026784 | -0.021157 | -0.002124 | 0.045421 | 0.076426 | -0.026092 | 0.047909 | 0.1479 | -0.004219 | -0.097207 | -0.047906 | -0.004248 | -0.038063 | -0.016906 | 0.17221 | 0.005259 | 0.010886 | 0.029919 | 0.077464 | 0.10847 | 0.005951 | 0.079952 | 0.17994 | 0.027824 | -0.065164 | -0.015863 | 0.027795 | -0.00602 | 0.015137 | 0.095815 | 0.085972 | 0.043687 | 0.033844
3477.0469 | 122.5891 | -0.086975 | 122.5388 | 0.13559 | -0.031363 | -0.021157 | -0.002124 | 0.049999 | 0.076426 | -0.03067 | 0.043331 | 0.14332 | -0.008798 | -0.10179 | -0.057062 | -0.008827 | -0.042641 | -0.016906 | 0.16763 | 0.00068 | 0.010886 | 0.029919 | 0.082042 | 0.10847 | 0.001373 | 0.075374 | 0.17536 | 0.023245 | -0.069743 | -0.025019 | 0.023216 | -0.010598 | 0.015137 | 0.10039 | 0.085972 | 0.048264 | 0.033843
3478.8125 | 122.6578 | -0.073242 | 122.4838 | 0.13101 | -0.031363 | -0.025735 | -0.006703 | 0.049999 | 0.062691 | -0.03067 | 0.052488 | 0.1479 | 0.000359 | -0.10179 | -0.061641 | -0.008827 | -0.04722 | -0.021484 | 0.16305 | 0.00068 | 0.006308 | 0.02534 | 0.082042 | 0.094734 | 0.001373 | 0.084531 | 0.17994 | 0.032402 | -0.069743 | -0.029598 | 0.023216 | -0.015177 | 0.010559 | 0.11413 | 0.099708 | 0.062 | 0.047579
3480.5781 | 122.6303 | -0.073242 | 122.5159 | 0.13101 | -0.026784 | -0.025735 | -0.011281 | 0.045421 | 0.067269 | -0.035248 | 0.047909 | 0.14332 | -0.008798 | -0.10179 | -0.057062 | -0.013405 | -0.051798 | -0.00775 | 0.16305 | 0.005259 | 0.006308 | 0.020762 | 0.077464 | 0.099312 | -0.003205 | 0.079952 | 0.17536 | 0.023245 | -0.069743 | -0.025019 | 0.018638 | -0.019755 | 0.024293 | 0.10497 | 0.099707 | 0.048264 | 0.043
3482.2812 | 122.5754 | -0.10986 | 122.5571 | 0.13101 | -0.022205 | -0.025735 | -0.002124 | 0.049999 | 0.076426 | -0.035248 | 0.047909 | 0.13874 | 0.000359 | -0.097207 | -0.057062 | -0.008827 | -0.051798 | -0.021484 | 0.16305 | 0.009838 | 0.006308 | 0.029919 | 0.082042 | 0.10847 | -0.003205 | 0.079952 | 0.17079 | 0.032402 | -0.065164 | -0.025019 | 0.023216 | -0.019755 | 0.010559 | 0.10497 | 0.099707 | 0.057421 | 0.052157
3484.0625 | 122.6349 | -0.07782 | 122.5525 | 0.12643 | -0.031363 | -0.016578 | -0.011281 | 0.049999 | 0.067269 | -0.039826 | 0.047909 | 0.13874 | 0.004937 | -0.092628 | -0.052484 | -0.008827 | -0.042641 | -0.012328 | 0.15847 | 0.00068 | 0.015465 | 0.020762 | 0.082042 | 0.099312 | -0.007783 | 0.079952 | 0.17079 | 0.03698 | -0.060585 | -0.020441 | 0.023216 | -0.010598 | 0.019715 | 0.10039 | 0.09055 | 0.057421 | 0.047578
3485.8281 | 122.6028 | -0.086975 | 122.5571 | 0.13559 | -0.026784 | -0.016578 | -0.01586 | 0.036265 | 0.067269 | -0.026092 | 0.043331 | 0.14332 | 0.004937 | -0.10637 | -0.057062 | -0.004248 | -0.042641 | -0.012328 | 0.16763 | 0.005259 | 0.015465 | 0.016183 | 0.068308 | 0.099312 | 0.005951 | 0.075374 | 0.17536 | 0.03698 | -0.074322 | -0.025019 | 0.027795 | -0.010598 | 0.019715 | 0.10039 | 0.085972 | 0.061999 | 0.047578
3487.5938 | 122.5616 | -0.10529 | 122.5433 | 0.12643 | -0.022205 | -0.021157 | -0.01586 | 0.040843 | 0.071848 | -0.03067 | 0.047909 | 0.13874 | -0.008798 | -0.097207 | -0.052484 | -0.004248 | -0.051798 | -0.012328 | 0.15847 | 0.009838 | 0.010886 | 0.016183 | 0.072886 | 0.10389 | 0.001373 | 0.079952 | 0.17079 | 0.023245 | -0.065164 | -0.020441 | 0.027795 | -0.019755 | 0.019715 | 0.10039 | 0.099707 | 0.043686 | 0.043
3489.2969 | 122.6303 | -0.091553 | 122.5479 | 0.12643 | -0.031363 | -0.016578 | -0.011281 | 0.040843 | 0.067269 | -0.039826 | 0.043331 | 0.13874 | -0.004219 | -0.078891 | -0.057062 | -0.008827 | -0.04722 | -0.012328 | 0.15847 | 0.00068 | 0.015465 | 0.020762 | 0.072886 | 0.099312 | -0.007783 | 0.075374 | 0.17079 | 0.027824 | -0.046848 | -0.025019 | 0.023216 | -0.015177 | 0.019715 | 0.10039 | 0.090551 | 0.052843 | 0.043001
3491.0625 | 122.5845 | -0.10529 | 122.5708 | 0.13101 | -0.031363 | -0.012 | -0.006703 | 0.045421 | 0.071848 | -0.039826 | 0.052488 | 0.14332 | 0.000359 | -0.097207 | -0.061641 | -0.004248 | -0.04722 | -0.016906 | 0.16305 | 0.00068 | 0.020043 | 0.02534 | 0.077464 | 0.10389 | -0.007783 | 0.084531 | 0.17536 | 0.032402 | -0.065164 | -0.029598 | 0.027795 | -0.015177 | 0.015137 | 0.11413 | 0.099708 | 0.062 | 0.047579
3492.8125 | 122.5754 | -0.10071 | 122.5525 | 0.13101 | -0.026784 | -0.021157 | -0.002124 | 0.045421 | 0.067269 | -0.039826 | 0.043331 | 0.13874 | 0.000359 | -0.10179 | -0.057062 | -0.013405 | -0.042641 | -0.012328 | 0.16305 | 0.005259 | 0.010886 | 0.029919 | 0.077464 | 0.099312 | -0.007783 | 0.075374 | 0.17079 | 0.032402 | -0.069743 | -0.025019 | 0.018638 | -0.010598 | 0.019715 | 0.10039 | 0.085972 | 0.057421 | 0.043
3494.5781 | 122.5616 | -0.11902 | 122.5571 | 0.12643 | -0.022205 | -0.016578 | -0.006703 | 0.049999 | 0.071848 | -0.035248 | 0.043331 | 0.14332 | -0.004219 | -0.092628 | -0.057062 | -0.004248 | -0.04722 | -0.016906 | 0.15847 | 0.009838 | 0.015465 | 0.02534 | 0.082042 | 0.10389 | -0.003205 | 0.075374 | 0.17536 | 0.027824 | -0.060585 | -0.025019 | 0.027795 | -0.015177 | 0.015137 | 0.10039 | 0.090551 | 0.052843 | 0.043001
3496.2812 | 122.6532 | -0.073242 | 122.5388 | 0.13101 | -0.031363 | -0.016578 | -0.006703 | 0.045421 | 0.062691 | -0.03067 | 0.047909 | 0.13874 | -0.004219 | -0.10179 | -0.057062 | -0.008827 | -0.04722 | -0.016906 | 0.16305 | 0.00068 | 0.015465 | 0.02534 | 0.077464 | 0.094734 | 0.001373 | 0.079952 | 0.17079 | 0.027824 | -0.069743 | -0.025019 | 0.023216 | -0.015177 | 0.015137 | 0.10497 | 0.095129 | 0.052843 | 0.043001
3498.0469 | 122.6395 | -0.068665 | 122.5342 | 0.12185 | -0.035942 | -0.021157 | -0.011281 | 0.045421 | 0.067269 | -0.035248 | 0.052488 | 0.14332 | 0.000359 | -0.11094 | -0.057062 | -0.008827 | -0.04722 | -0.012328 | 0.15389 | -0.003899 | 0.010886 | 0.020762 | 0.077464 | 0.099312 | -0.003205 | 0.084531 | 0.17536 | 0.032402 | -0.078901 | -0.025019 | 0.023216 | -0.015177 | 0.019715 | 0.10955 | 0.099708 | 0.057421 | 0.047579
3499.8281 | 122.5662 | -0.10071 | 122.5754 | 0.13101 | -0.026784 | -0.021157 | -0.002124 | 0.054577 | 0.067269 | -0.039826 | 0.052488 | 0.1479 | -0.004219 | -0.078891 | -0.057062 | -0.008827 | -0.04722 | -0.012328 | 0.16305 | 0.005259 | 0.010886 | 0.029919 | 0.08662 | 0.099312 | -0.007783 | 0.084531 | 0.17994 | 0.027824 | -0.046848 | -0.025019 | 0.023216 | -0.015177 | 0.019715 | 0.10955 | 0.099708 | 0.052843 | 0.043001
3501.5312 | 122.699 | -0.086975 | 122.5388 | 0.13101 | -0.035942 | -0.030314 | -0.002124 | 0.040843 | 0.067269 | -0.035248 | 0.047909 | 0.15248 | -0.004219 | -0.10179 | -0.052484 | -0.004248 | -0.04722 | -0.012328 | 0.16305 | -0.003899 | 0.001729 | 0.029919 | 0.072886 | 0.099312 | -0.003205 | 0.079952 | 0.18452 | 0.027824 | -0.069743 | -0.020441 | 0.027795 | -0.015177 | 0.019715 | 0.10039 | 0.095129 | 0.048265 | 0.043001
3503.2344 | 122.6395 | -0.068665 | 122.5525 | 0.12643 | -0.031363 | -0.025735 | -0.006703 | 0.049999 | 0.071848 | -0.039826 | 0.052488 | 0.1479 | 0.000359 | -0.097207 | -0.057062 | -0.013405 | -0.051798 | -0.016906 | 0.15847 | 0.00068 | 0.006308 | 0.02534 | 0.082042 | 0.10389 | -0.007783 | 0.084531 | 0.17994 | 0.032402 | -0.065164 | -0.025019 | 0.018638 | -0.019755 | 0.015137 | 0.10955 | 0.10429 | 0.057421 | 0.052157
3505 | 122.6944 | -0.059509 | 122.5525 | 0.13101 | -0.026784 | -0.025735 | -0.011281 | 0.045421 | 0.067269 | -0.035248 | 0.047909 | 0.1479 | -0.004219 | -0.097207 | -0.057062 | -0.008827 | -0.051798 | -0.026063 | 0.16305 | 0.005259 | 0.006308 | 0.020762 | 0.077464 | 0.099312 | -0.003205 | 0.079952 | 0.17994 | 0.027824 | -0.065164 | -0.025019 | 0.023216 | -0.019755 | 0.00598 | 0.10497 | 0.099707 | 0.052843 | 0.047579
3506.7031 | 122.7036 | -0.073242 | 122.5479 | 0.12185 | -0.026784 | -0.012 | -0.011281 | 0.036265 | 0.062691 | -0.03067 | 0.052488 | 0.13874 | 0.000359 | -0.10637 | -0.052484 | -0.004248 | -0.042641 | -0.016906 | 0.15389 | 0.005259 | 0.020043 | 0.020762 | 0.068308 | 0.094734 | 0.001373 | 0.084531 | 0.17079 | 0.032402 | -0.074322 | -0.020441 | 0.027795 | -0.010598 | 0.015137 | 0.10497 | 0.095129 | 0.052843 | 0.043
3508.4688 | 122.5983 | -0.10071 | 122.5891 | 0.13101 | -0.031363 | -0.025735 | -0.002124 | 0.045421 | 0.067269 | -0.035248 | 0.043331 | 0.15248 | 0.009515 | -0.097207 | -0.061641 | -0.013405 | -0.04722 | -0.012328 | 0.16305 | 0.00068 | 0.006308 | 0.029919 | 0.077464 | 0.099312 | -0.003205 | 0.075374 | 0.18452 | 0.041558 | -0.065164 | -0.029598 | 0.018638 | -0.015177 | 0.019715 | 0.10497 | 0.090551 | 0.071156 | 0.056735
3510.1719 | 122.6807 | -0.059509 | 122.5571 | 0.12643 | -0.026784 | -0.021157 | -0.006703 | 0.040843 | 0.071848 | -0.035248 | 0.047909 | 0.1479 | 0.009515 | -0.10637 | -0.057062 | -0.008827 | -0.04722 | -0.016906 | 0.15847 | 0.005259 | 0.010886 | 0.02534 | 0.072886 | 0.10389 | -0.003205 | 0.079952 | 0.17994 | 0.041558 | -0.074322 | -0.025019 | 0.023216 | -0.015177 | 0.015137 | 0.10497 | 0.095129 | 0.066577 | 0.056735
3511.9375 | 122.6166 | -0.082397 | 122.5616 | 0.12643 | -0.022205 | -0.016578 | -0.011281 | 0.045421 | 0.067269 | -0.026092 | 0.043331 | 0.14332 | 0.004937 | -0.10637 | -0.057062 | -0.013405 | -0.042641 | -0.016906 | 0.15847 | 0.009838 | 0.015465 | 0.020762 | 0.077464 | 0.099312 | 0.005951 | 0.075374 | 0.17536 | 0.03698 | -0.074322 | -0.025019 | 0.018638 | -0.010598 | 0.015137 | 0.10039 | 0.085972 | 0.061999 | 0.047578
3513.6562 | 122.58 | -0.13275 | 122.5708 | 0.13101 | -0.026784 | -0.016578 | -0.006703 | 0.045421 | 0.071848 | -0.035248 | 0.043331 | 0.1479 | -0.004219 | -0.092628 | -0.057062 | -0.008827 | -0.04722 | -0.00775 | 0.16305 | 0.005259 | 0.015465 | 0.02534 | 0.077464 | 0.10389 | -0.003205 | 0.075374 | 0.17994 | 0.027824 | -0.060585 | -0.025019 | 0.023216 | -0.015177 | 0.024293 | 0.10039 | 0.090551 | 0.052843 | 0.043001
3515.4219 | 122.6532 | -0.086975 | 122.5342 | 0.12643 | -0.022205 | -0.012 | -0.01586 | 0.040843 | 0.067269 | -0.035248 | 0.057066 | 0.15248 | 0.000359 | -0.10637 | -0.057062 | -0.013405 | -0.04722 | -0.026063 | 0.15847 | 0.009838 | 0.020043 | 0.016183 | 0.072886 | 0.099312 | -0.003205 | 0.089109 | 0.18452 | 0.032402 | -0.074322 | -0.025019 | 0.018638 | -0.015177 | 0.00598 | 0.11413 | 0.10429 | 0.057421 | 0.047579
3517.1719 | 122.6898 | -0.068665 | 122.5479 | 0.12643 | -0.026784 | -0.021157 | -0.006703 | 0.049999 | 0.076426 | -0.039826 | 0.057066 | 0.1479 | 0.000359 | -0.10637 | -0.057062 | -0.008827 | -0.051798 | -0.016906 | 0.15847 | 0.005259 | 0.010886 | 0.02534 | 0.082042 | 0.10847 | -0.007783 | 0.089109 | 0.17994 | 0.032402 | -0.074322 | -0.025019 | 0.023216 | -0.019755 | 0.015137 | 0.11413 | 0.10886 | 0.057421 | 0.052157
3518.875 | 122.6761 | -0.091553 | 122.5433 | 0.13101 | -0.026784 | -0.021157 | -0.006703 | 0.045421 | 0.062691 | -0.03067 | 0.052488 | 0.14332 | 0.000359 | -0.08347 | -0.047906 | -0.013405 | -0.04722 | -0.016906 | 0.16305 | 0.005259 | 0.010886 | 0.02534 | 0.077464 | 0.094734 | 0.001373 | 0.084531 | 0.17536 | 0.032402 | -0.051427 | -0.015863 | 0.018638 | -0.015177 | 0.015137 | 0.10039 | 0.099708 | 0.048265 | 0.047579
3520.625 | 122.5708 | -0.10529 | 122.612 | 0.12643 | -0.031363 | -0.016578 | -0.011281 | 0.045421 | 0.071848 | -0.03067 | 0.047909 | 0.1479 | 0.000359 | -0.097207 | -0.052484 | -0.013405 | -0.04722 | -0.016906 | 0.15847 | 0.00068 | 0.015465 | 0.020762 | 0.077464 | 0.10389 | 0.001373 | 0.079952 | 0.17994 | 0.032402 | -0.065164 | -0.020441 | 0.018638 | -0.015177 | 0.015137 | 0.10039 | 0.095129 | 0.052843 | 0.047579
3522.3906 | 122.6303 | -0.10071 | 122.58 | 0.12643 | -0.026784 | -0.016578 | -0.002124 | 0.040843 | 0.071848 | -0.035248 | 0.052488 | 0.15248 | -0.004219 | -0.088049 | -0.057062 | -0.013405 | -0.04722 | -0.016906 | 0.15847 | 0.005259 | 0.015465 | 0.029919 | 0.072886 | 0.10389 | -0.003205 | 0.084531 | 0.18452 | 0.027824 | -0.056006 | -0.025019 | 0.018638 | -0.015177 | 0.015137 | 0.10955 | 0.099708 | 0.052843 | 0.043001
3524.0938 | 122.5937 | -0.10071 | 122.5937 | 0.12643 | -0.026784 | -0.021157 | -0.002124 | 0.045421 | 0.067269 | -0.035248 | 0.057066 | 0.13874 | 0.000359 | -0.11552 | -0.052484 | -0.013405 | -0.042641 | -0.012328 | 0.15847 | 0.005259 | 0.010886 | 0.029919 | 0.077464 | 0.099312 | -0.003205 | 0.089109 | 0.17079 | 0.032402 | -0.08348 | -0.020441 | 0.018638 | -0.010598 | 0.019715 | 0.10955 | 0.099707 | 0.052843 | 0.043
3525.8438 | 122.644 | -0.09613 | 122.5891 | 0.12185 | -0.035942 | -0.021157 | -0.011281 | 0.045421 | 0.071848 | -0.035248 | 0.052488 | 0.1479 | 0.000359 | -0.097207 | -0.057062 | -0.013405 | -0.051798 | -0.012328 | 0.15389 | -0.003899 | 0.010886 | 0.020762 | 0.077464 | 0.10389 | -0.003205 | 0.084531 | 0.17994 | 0.032402 | -0.065164 | -0.025019 | 0.018638 | -0.019755 | 0.019715 | 0.10955 | 0.10429 | 0.057421 | 0.052157
3527.6094 | 122.7127 | -0.07782 | 122.5754 | 0.12185 | -0.031363 | -0.016578 | -0.002124 | 0.045421 | 0.067269 | -0.044405 | 0.047909 | 0.15248 | 0.004937 | -0.10637 | -0.066219 | -0.017983 | -0.04722 | -0.012328 | 0.15389 | 0.00068 | 0.015465 | 0.029919 | 0.077464 | 0.099312 | -0.012362 | 0.079952 | 0.18452 | 0.03698 | -0.074322 | -0.034176 | 0.01406 | -0.015177 | 0.019715 | 0.11413 | 0.095129 | 0.071156 | 0.052157
3529.3281 | 122.6074 | -0.091553 | 122.6074 | 0.12643 | -0.026784 | -0.021157 | 0.002454 | 0.045421 | 0.076426 | -0.026092 | 0.052488 | 0.15248 | -0.008798 | -0.10637 | -0.052484 | -0.013405 | -0.04722 | -0.012328 | 0.15847 | 0.005259 | 0.010886 | 0.034497 | 0.077464 | 0.10847 | 0.005951 | 0.084531 | 0.18452 | 0.023245 | -0.074322 | -0.020441 | 0.018638 | -0.015177 | 0.019715 | 0.10497 | 0.099708 | 0.043686 | 0.038422
3531.0938 | 122.5937 | -0.1236 | 122.5983 | 0.13101 | -0.031363 | -0.016578 | -0.006703 | 0.045421 | 0.071848 | -0.03067 | 0.047909 | 0.1479 | 0.004937 | -0.097207 | -0.057062 | -0.008827 | -0.042641 | -0.016906 | 0.16305 | 0.00068 | 0.015465 | 0.02534 | 0.077464 | 0.10389 | 0.001373 | 0.079952 | 0.17994 | 0.03698 | -0.065164 | -0.025019 | 0.023216 | -0.010598 | 0.015137 | 0.10497 | 0.09055 | 0.061999 | 0.047578
3532.8438 | 122.6349 | -0.11444 | 122.6028 | 0.13101 | -0.031363 | -0.012 | -0.006703 | 0.049999 | 0.071848 | -0.03067 | 0.047909 | 0.14332 | 0.004937 | -0.097207 | -0.057062 | -0.013405 | -0.051798 | -0.012328 | 0.16305 | 0.00068 | 0.020043 | 0.02534 | 0.082042 | 0.10389 | 0.001373 | 0.079952 | 0.17536 | 0.03698 | -0.065164 | -0.025019 | 0.018638 | -0.019755 | 0.019715 | 0.10497 | 0.099707 | 0.061999 | 0.056735
3534.5469 | 122.6486 | -0.09613 | 122.6257 | 0.13101 | -0.031363 | -0.021157 | -0.006703 | 0.040843 | 0.062691 | -0.021514 | 0.047909 | 0.1479 | 0.000359 | -0.10179 | -0.057062 | -0.013405 | -0.04722 | -0.016906 | 0.16305 | 0.00068 | 0.010886 | 0.02534 | 0.072886 | 0.094734 | 0.010529 | 0.079952 | 0.17994 | 0.032402 | -0.069743 | -0.025019 | 0.018638 | -0.015177 | 0.015137 | 0.10497 | 0.095129 | 0.057421 | 0.047579
3536.25 | 122.6303 | -0.07782 | 122.5891 | 0.12643 | -0.035942 | -0.016578 | -0.002124 | 0.049999 | 0.076426 | -0.035248 | 0.047909 | 0.1479 | -0.004219 | -0.10637 | -0.061641 | -0.017983 | -0.042641 | -0.003172 | 0.15847 | -0.003899 | 0.015465 | 0.029919 | 0.082042 | 0.10847 | -0.003205 | 0.079952 | 0.17994 | 0.027824 | -0.074322 | -0.029598 | 0.01406 | -0.010598 | 0.028871 | 0.10955 | 0.09055 | 0.057422 | 0.038422
3538.0156 | 122.6486 | -0.082397 | 122.58 | 0.13101 | -0.031363 | -0.021157 | -0.006703 | 0.049999 | 0.076426 | -0.035248 | 0.057066 | 0.15706 | -0.008798 | -0.10637 | -0.029593 | -0.017983 | -0.006014 | 0.005985 | 0.16305 | 0.00068 | 0.010886 | 0.02534 | 0.082042 | 0.10847 | -0.003205 | 0.089109 | 0.1891 | 0.023245 | -0.074322 | 0.00245 | 0.01406 | 0.026029 | 0.038028 | 0.086659 | 0.06308 | 0.020795 | -0.002784
3539.7188 | 122.6486 | -0.091553 | 122.6028 | 0.12643 | -0.026784 | -0.012 | -0.006703 | 0.049999 | 0.071848 | -0.035248 | 0.057066 | 0.15248 | 0.000359 | -0.10179 | -0.070797 | -0.013405 | -0.04722 | -0.012328 | 0.15847 | 0.005259 | 0.020043 | 0.02534 | 0.082042 | 0.10389 | -0.003205 | 0.089109 | 0.18452 | 0.032402 | -0.069743 | -0.038754 | 0.018638 | -0.015177 | 0.019715 | 0.12786 | 0.10429 | 0.071156 | 0.047579
3541.4219 | 122.7493 | -0.086975 | 122.5571 | 0.12643 | -0.031363 | -0.021157 | -0.011281 | 0.040843 | 0.067269 | -0.035248 | 0.052488 | 0.14332 | 0.000359 | -0.10179 | -0.061641 | -0.008827 | -0.04722 | -0.016906 | 0.15847 | 0.00068 | 0.010886 | 0.020762 | 0.072886 | 0.099312 | -0.003205 | 0.084531 | 0.17536 | 0.032402 | -0.069743 | -0.029598 | 0.023216 | -0.015177 | 0.015137 | 0.11413 | 0.099708 | 0.062 | 0.047579
3543.1719 | 122.6898 | -0.068665 | 122.5662 | 0.13101 | -0.026784 | -0.021157 | -0.011281 | 0.045421 | 0.076426 | -0.035248 | 0.061645 | 0.1479 | -0.008798 | -0.092628 | -0.070797 | -0.004248 | -0.04722 | -0.016906 | 0.16305 | 0.005259 | 0.010886 | 0.020762 | 0.077464 | 0.10847 | -0.003205 | 0.093688 | 0.17994 | 0.023245 | -0.060585 | -0.038754 | 0.027795 | -0.015177 | 0.015137 | 0.13244 | 0.10886 | 0.061999 | 0.038422
3544.9375 | 122.6303 | -0.10986 | 122.5937 | 0.13101 | -0.026784 | -0.016578 | -0.002124 | 0.049999 | 0.071848 | -0.035248 | 0.047909 | 0.15248 | -0.004219 | -0.10637 | -0.066219 | -0.004248 | -0.056376 | -0.021484 | 0.16305 | 0.005259 | 0.015465 | 0.029919 | 0.082042 | 0.10389 | -0.003205 | 0.079952 | 0.18452 | 0.027824 | -0.074322 | -0.034176 | 0.027795 | -0.024333 | 0.010559 | 0.11413 | 0.10429 | 0.062 | 0.052157
3546.6875 | 122.7402 | -0.054932 | 122.5708 | 0.13101 | -0.035942 | -0.012 | -0.002124 | 0.045421 | 0.071848 | -0.035248 | 0.052488 | 0.1479 | -0.008798 | -0.097207 | -0.075375 | -0.008827 | -0.051798 | -0.012328 | 0.16305 | -0.003899 | 0.020043 | 0.029919 | 0.077464 | 0.10389 | -0.003205 | 0.084531 | 0.17994 | 0.023245 | -0.065164 | -0.043332 | 0.023216 | -0.019755 | 0.019715 | 0.12786 | 0.10429 | 0.066577 | 0.043
3548.3906 | 122.7264 | -0.068665 | 122.5571 | 0.13559 | -0.040521 | -0.025735 | -0.011281 | 0.045421 | 0.067269 | -0.035248 | 0.052488 | 0.14332 | 0.000359 | -0.11094 | -0.061641 | -0.013405 | -0.051798 | -0.016906 | 0.16763 | -0.008478 | 0.006308 | 0.020762 | 0.077464 | 0.099312 | -0.003205 | 0.084531 | 0.17536 | 0.032402 | -0.078901 | -0.029598 | 0.018638 | -0.019755 | 0.015137 | 0.11413 | 0.10429 | 0.062 | 0.052157
3550.1719 | 122.5937 | -0.12817 | 122.6212 | 0.13101 | -0.026784 | -0.012 | -0.002124 | 0.045421 | 0.076426 | -0.03067 | 0.047909 | 0.14332 | 0.004937 | -0.10179 | -0.075375 | -0.013405 | -0.051798 | -0.016906 | 0.16305 | 0.005259 | 0.020043 | 0.029919 | 0.077464 | 0.10847 | 0.001373 | 0.079952 | 0.17536 | 0.03698 | -0.069743 | -0.043332 | 0.018638 | -0.019755 | 0.015137 | 0.12328 | 0.099707 | 0.080312 | 0.056735
3551.875 | 122.6578 | -0.086975 | 122.5937 | 0.13101 | -0.022205 | -0.012 | -0.002124 | 0.045421 | 0.067269 | -0.03067 | 0.052488 | 0.13874 | -0.004219 | -0.11094 | -0.075375 | -0.013405 | -0.051798 | -0.016906 | 0.16305 | 0.009838 | 0.020043 | 0.029919 | 0.077464 | 0.099312 | 0.001373 | 0.084531 | 0.17079 | 0.027824 | -0.078901 | -0.043332 | 0.018638 | -0.019755 | 0.015137 | 0.12786 | 0.10429 | 0.071156 | 0.047579
3553.6406 | 122.7081 | -0.07782 | 122.5891 | 0.12643 | -0.035942 | -0.021157 | -0.006703 | 0.040843 | 0.067269 | -0.044405 | 0.047909 | 0.1479 | -0.004219 | -0.08347 | -0.070797 | -0.008827 | -0.051798 | -0.012328 | 0.15847 | -0.003899 | 0.010886 | 0.02534 | 0.072886 | 0.099312 | -0.012362 | 0.079952 | 0.17994 | 0.027824 | -0.051427 | -0.038754 | 0.023216 | -0.019755 | 0.019715 | 0.11871 | 0.099707 | 0.066578 | 0.047579
3555.3438 | 122.6257 | -0.10071 | 122.612 | 0.13101 | -0.022205 | -0.025735 | -0.006703 | 0.049999 | 0.071848 | -0.035248 | 0.052488 | 0.1479 | 0.000359 | -0.10637 | -0.070797 | -0.008827 | -0.04722 | -0.016906 | 0.16305 | 0.009838 | 0.006308 | 0.02534 | 0.082042 | 0.10389 | -0.003205 | 0.084531 | 0.17994 | 0.032402 | -0.074322 | -0.038754 | 0.023216 | -0.015177 | 0.015137 | 0.12329 | 0.099708 | 0.071156 | 0.047579
3557.0938 | 122.7493 | -0.064087 | 122.5891 | 0.13101 | -0.031363 | -0.021157 | -0.006703 | 0.045421 | 0.067269 | -0.039826 | 0.052488 | 0.1479 | 0.004937 | -0.10179 | -0.075375 | -0.008827 | -0.04722 | -0.00775 | 0.16305 | 0.00068 | 0.010886 | 0.02534 | 0.077464 | 0.099312 | -0.007783 | 0.084531 | 0.17994 | 0.03698 | -0.069743 | -0.043332 | 0.023216 | -0.015177 | 0.024293 | 0.12786 | 0.099708 | 0.080312 | 0.052157
3558.7812 | 122.612 | -0.10071 | 122.6303 | 0.12643 | -0.031363 | -0.021157 | -0.002124 | 0.045421 | 0.067269 | -0.035248 | 0.043331 | 0.1479 | 0.004937 | -0.097207 | -0.070797 | -0.013405 | -0.051798 | -0.016906 | 0.15847 | 0.00068 | 0.010886 | 0.029919 | 0.077464 | 0.099312 | -0.003205 | 0.075374 | 0.17994 | 0.03698 | -0.065164 | -0.038754 | 0.018638 | -0.019755 | 0.015137 | 0.11413 | 0.095129 | 0.075734 | 0.056735
3560.5312 | 122.7264 | -0.082397 | 122.5983 | 0.13559 | -0.031363 | -0.021157 | -0.002124 | 0.040843 | 0.067269 | -0.035248 | 0.052488 | 0.1479 | -0.004219 | -0.10179 | -0.066219 | -0.008827 | -0.04722 | -0.016906 | 0.16763 | 0.00068 | 0.010886 | 0.029919 | 0.072886 | 0.099312 | -0.003205 | 0.084531 | 0.17994 | 0.027824 | -0.069743 | -0.034176 | 0.023216 | -0.015177 | 0.015137 | 0.11871 | 0.099708 | 0.062 | 0.043001
3562.2969 | 122.7402 | -0.068665 | 122.58 | 0.12643 | -0.026784 | -0.016578 | -0.002124 | 0.040843 | 0.071848 | -0.03067 | 0.047909 | 0.14332 | 0.000359 | -0.10179 | -0.061641 | -0.013405 | -0.051798 | -0.016906 | 0.15847 | 0.005259 | 0.015465 | 0.029919 | 0.072886 | 0.10389 | 0.001373 | 0.079952 | 0.17536 | 0.032402 | -0.069743 | -0.029598 | 0.018638 | -0.019755 | 0.015137 | 0.10955 | 0.099707 | 0.062 | 0.052157
3564.0625 | 122.699 | -0.086975 | 122.5845 | 0.13101 | -0.026784 | -0.016578 | -0.006703 | 0.040843 | 0.081005 | -0.035248 | 0.057066 | 0.15248 | -0.004219 | -0.10179 | -0.061641 | -0.013405 | -0.056376 | -0.012328 | 0.16305 | 0.005259 | 0.015465 | 0.02534 | 0.072886 | 0.11305 | -0.003205 | 0.089109 | 0.18452 | 0.027824 | -0.069743 | -0.029598 | 0.018638 | -0.024333 | 0.019715 | 0.11871 | 0.11344 | 0.057422 | 0.052157
3565.8438 | 122.6166 | -0.11902 | 122.6349 | 0.13101 | -0.031363 | -0.016578 | -0.006703 | 0.045421 | 0.071848 | -0.039826 | 0.052488 | 0.1479 | -0.004219 | -0.10179 | -0.066219 | -0.004248 | -0.04722 | -0.016906 | 0.16305 | 0.00068 | 0.015465 | 0.02534 | 0.077464 | 0.10389 | -0.007783 | 0.084531 | 0.17994 | 0.027824 | -0.069743 | -0.034176 | 0.027795 | -0.015177 | 0.015137 | 0.11871 | 0.099708 | 0.062 | 0.043001
3567.5469 | 122.731 | -0.091553 | 122.5937 | 0.13101 | -0.031363 | -0.016578 | -0.006703 | 0.045421 | 0.071848 | -0.03067 | 0.047909 | 0.14332 | 0.000359 | -0.097207 | -0.075375 | -0.013405 | -0.051798 | -0.026063 | 0.16305 | 0.00068 | 0.015465 | 0.02534 | 0.077464 | 0.10389 | 0.001373 | 0.079952 | 0.17536 | 0.032402 | -0.065164 | -0.043332 | 0.018638 | -0.019755 | 0.00598 | 0.12328 | 0.099707 | 0.075734 | 0.052157
3569.3125 | 122.7173 | -0.086975 | 122.5937 | 0.13101 | -0.035942 | -0.021157 | -0.006703 | 0.045421 | 0.062691 | -0.03067 | 0.052488 | 0.14332 | -0.004219 | -0.11094 | -0.066219 | -0.008827 | -0.04722 | -0.00775 | 0.16305 | -0.003899 | 0.010886 | 0.02534 | 0.077464 | 0.094734 | 0.001373 | 0.084531 | 0.17536 | 0.027824 | -0.078901 | -0.034176 | 0.023216 | -0.015177 | 0.024293 | 0.11871 | 0.099708 | 0.062 | 0.043001
3571.0781 | 122.6303 | -0.10529 | 122.6212 | 0.13101 | -0.031363 | -0.021157 | -0.002124 | 0.040843 | 0.067269 | -0.03067 | 0.052488 | 0.15248 | 0.000359 | -0.11094 | -0.075375 | -0.008827 | -0.056376 | -0.016906 | 0.16305 | 0.00068 | 0.010886 | 0.029919 | 0.072886 | 0.099312 | 0.001373 | 0.084531 | 0.18452 | 0.032402 | -0.078901 | -0.043332 | 0.023216 | -0.024333 | 0.015137 | 0.12786 | 0.10886 | 0.075734 | 0.056735
3572.8438 | 122.6303 | -0.10071 | 122.6624 | 0.12185 | -0.035942 | -0.021157 | -0.011281 | 0.040843 | 0.062691 | -0.035248 | 0.052488 | 0.1479 | -0.004219 | -0.097207 | -0.066219 | -0.008827 | -0.042641 | -0.00775 | 0.15389 | -0.003899 | 0.010886 | 0.020762 | 0.072886 | 0.094734 | -0.003205 | 0.084531 | 0.17994 | 0.027824 | -0.065164 | -0.034176 | 0.023216 | -0.010598 | 0.024293 | 0.11871 | 0.095129 | 0.062 | 0.038422
3574.5312 | 122.7219 | -0.082397 | 122.5937 | 0.12643 | -0.022205 | -0.016578 | -0.006703 | 0.045421 | 0.062691 | -0.035248 | 0.047909 | 0.1479 | 0.004937 | -0.078891 | -0.075375 | -0.008827 | -0.04722 | -0.012328 | 0.15847 | 0.009838 | 0.015465 | 0.02534 | 0.077464 | 0.094734 | -0.003205 | 0.079952 | 0.17994 | 0.03698 | -0.046848 | -0.043332 | 0.023216 | -0.015177 | 0.019715 | 0.12328 | 0.095129 | 0.080312 | 0.052157
3576.3281 | 122.6303 | -0.10986 | 122.6486 | 0.13101 | -0.022205 | -0.016578 | -0.006703 | 0.054577 | 0.062691 | -0.035248 | 0.047909 | 0.1479 | 0.004937 | -0.10637 | -0.066219 | -0.013405 | -0.04722 | -0.021484 | 0.16305 | 0.009838 | 0.015465 | 0.02534 | 0.08662 | 0.094734 | -0.003205 | 0.079952 | 0.17994 | 0.03698 | -0.074322 | -0.034176 | 0.018638 | -0.015177 | 0.010559 | 0.11413 | 0.095129 | 0.071156 | 0.052157
3578.0938 | 122.7264 | -0.091553 | 122.612 | 0.12643 | -0.031363 | -0.025735 | -0.006703 | 0.045421 | 0.067269 | -0.035248 | 0.052488 | 0.1479 | 0.000359 | -0.10637 | -0.075375 | -0.017983 | -0.042641 | -0.021484 | 0.15847 | 0.00068 | 0.006308 | 0.02534 | 0.077464 | 0.099312 | -0.003205 | 0.084531 | 0.17994 | 0.032402 | -0.074322 | -0.043332 | 0.01406 | -0.010598 | 0.010559 | 0.12786 | 0.095129 | 0.075734 | 0.043
3579.8594 | 122.6074 | -0.10986 | 122.644 | 0.12643 | -0.031363 | -0.021157 | -0.006703 | 0.049999 | 0.067269 | -0.039826 | 0.047909 | 0.15248 | 0.004937 | -0.10637 | -0.070797 | -0.013405 | -0.051798 | -0.012328 | 0.15847 | 0.00068 | 0.010886 | 0.02534 | 0.082042 | 0.099312 | -0.007783 | 0.079952 | 0.18452 | 0.03698 | -0.074322 | -0.038754 | 0.018638 | -0.019755 | 0.019715 | 0.11871 | 0.099707 | 0.075734 | 0.056735
3581.5625 | 122.7081 | -0.07782 | 122.5937 | 0.13101 | -0.026784 | -0.016578 | -0.006703 | 0.036265 | 0.071848 | -0.026092 | 0.057066 | 0.1479 | 0.004937 | -0.10179 | -0.075375 | -0.017983 | -0.042641 | -0.016906 | 0.16305 | 0.005259 | 0.015465 | 0.02534 | 0.068308 | 0.10389 | 0.005951 | 0.089109 | 0.17994 | 0.03698 | -0.069743 | -0.043332 | 0.01406 | -0.010598 | 0.015137 | 0.13244 | 0.099707 | 0.080312 | 0.047578
3583.2656 | 122.6624 | -0.10986 | 122.6532 | 0.12643 | -0.026784 | -0.021157 | -0.006703 | 0.040843 | 0.067269 | -0.03067 | 0.052488 | 0.1479 | 0.004937 | -0.11094 | -0.057062 | -0.013405 | -0.051798 | -0.016906 | 0.15847 | 0.005259 | 0.010886 | 0.02534 | 0.072886 | 0.099312 | 0.001373 | 0.084531 | 0.17994 | 0.03698 | -0.078901 | -0.025019 | 0.018638 | -0.019755 | 0.015137 | 0.10955 | 0.10429 | 0.061999 | 0.056735
3585.0312 | 122.7768 | -0.068665 | 122.5983 | 0.12185 | -0.035942 | -0.025735 | -0.002124 | 0.040843 | 0.058113 | -0.035248 | 0.047909 | 0.1479 | -0.004219 | -0.097207 | -0.066219 | -0.013405 | -0.04722 | -0.00775 | 0.15389 | -0.003899 | 0.006308 | 0.029919 | 0.072886 | 0.090156 | -0.003205 | 0.079952 | 0.17994 | 0.027824 | -0.065164 | -0.034176 | 0.018638 | -0.015177 | 0.024293 | 0.11413 | 0.095129 | 0.062 | 0.043001
3586.7969 | 122.7448 | -0.086975 | 122.5983 | 0.13101 | -0.035942 | -0.016578 | -0.006703 | 0.049999 | 0.071848 | -0.035248 | 0.057066 | 0.15248 | 0.000359 | -0.10637 | -0.066219 | -0.008827 | -0.04722 | -0.00775 | 0.16305 | -0.003899 | 0.015465 | 0.02534 | 0.082042 | 0.10389 | -0.003205 | 0.089109 | 0.18452 | 0.032402 | -0.074322 | -0.034176 | 0.023216 | -0.015177 | 0.024293 | 0.12329 | 0.10429 | 0.066578 | 0.047579
3588.5625 | 122.6852 | -0.10071 | 122.644 | 0.12643 | -0.026784 | -0.021157 | -0.002124 | 0.049999 | 0.071848 | -0.03067 | 0.057066 | 0.1479 | 0.000359 | -0.11094 | -0.061641 | -0.008827 | -0.04722 | -0.00775 | 0.15847 | 0.005259 | 0.010886 | 0.029919 | 0.082042 | 0.10389 | 0.001373 | 0.089109 | 0.17994 | 0.032402 | -0.078901 | -0.029598 | 0.023216 | -0.015177 | 0.024293 | 0.11871 | 0.10429 | 0.062 | 0.047579
3590.3281 | 122.7356 | -0.086975 | 122.6028 | 0.13101 | -0.040521 | -0.021157 | -0.002124 | 0.045421 | 0.071848 | -0.035248 | 0.052488 | 0.1479 | 0.000359 | -0.088049 | -0.066219 | -0.004248 | -0.04722 | -0.012328 | 0.16305 | -0.008478 | 0.010886 | 0.029919 | 0.077464 | 0.10389 | -0.003205 | 0.084531 | 0.17994 | 0.032402 | -0.056006 | -0.034176 | 0.027795 | -0.015177 | 0.019715 | 0.11871 | 0.099708 | 0.066578 | 0.047579
3592.0312 | 122.6486 | -0.12817 | 122.6349 | 0.12643 | -0.035942 | -0.021157 | 0.002454 | 0.045421 | 0.071848 | -0.03067 | 0.052488 | 0.15248 | 0.000359 | -0.10637 | -0.070797 | -0.013405 | -0.051798 | -0.016906 | 0.15847 | -0.003899 | 0.010886 | 0.034497 | 0.077464 | 0.10389 | 0.001373 | 0.084531 | 0.18452 | 0.032402 | -0.074322 | -0.038754 | 0.018638 | -0.019755 | 0.015137 | 0.12329 | 0.10429 | 0.071156 | 0.052157
3593.7969 | 122.7448 | -0.082397 | 122.6028 | 0.12643 | -0.035942 | -0.021157 | -0.006703 | 0.045421 | 0.076426 | -0.035248 | 0.061645 | 0.1479 | 0.004937 | -0.10179 | -0.075375 | -0.004248 | -0.04722 | -0.00775 | 0.15847 | -0.003899 | 0.010886 | 0.02534 | 0.077464 | 0.10847 | -0.003205 | 0.093688 | 0.17994 | 0.03698 | -0.069743 | -0.043332 | 0.027795 | -0.015177 | 0.024293 | 0.13702 | 0.10886 | 0.080312 | 0.052157
3595.5625 | 122.7081 | -0.09613 | 122.6349 | 0.12643 | -0.035942 | -0.016578 | -0.002124 | 0.045421 | 0.067269 | -0.039826 | 0.047909 | 0.1479 | 0.004937 | -0.10179 | -0.070797 | -0.013405 | -0.042641 | -0.021484 | 0.15847 | -0.003899 | 0.015465 | 0.029919 | 0.077464 | 0.099312 | -0.007783 | 0.079952 | 0.17994 | 0.03698 | -0.069743 | -0.038754 | 0.018638 | -0.010598 | 0.010559 | 0.11871 | 0.09055 | 0.075734 | 0.047578
3597.3281 | 122.6715 | -0.12817 | 122.6807 | 0.13101 | -0.035942 | -0.021157 | -0.006703 | 0.045421 | 0.071848 | -0.03067 | 0.043331 | 0.15706 | 0.000359 | -0.08347 | -0.070797 | -0.013405 | -0.042641 | -0.016906 | 0.16305 | -0.003899 | 0.010886 | 0.02534 | 0.077464 | 0.10389 | 0.001373 | 0.075374 | 0.1891 | 0.032402 | -0.051427 | -0.038754 | 0.018638 | -0.010598 | 0.015137 | 0.11413 | 0.085972 | 0.071156 | 0.043
3599.0938 | 122.6578 | -0.10071 | 122.644 | 0.12643 | -0.031363 | -0.012 | -0.006703 | 0.040843 | 0.071848 | -0.03067 | 0.047909 | 0.13874 | 0.000359 | -0.10637 | -0.066219 | 0.00033 | -0.051798 | -0.00775 | 0.15847 | 0.00068 | 0.020043 | 0.02534 | 0.072886 | 0.10389 | 0.001373 | 0.079952 | 0.17079 | 0.032402 | -0.074322 | -0.034176 | 0.032373 | -0.019755 | 0.024293 | 0.11413 | 0.099707 | 0.066578 | 0.052157
3600.7969 | 122.644 | -0.10986 | 122.6761 | 0.12643 | -0.031363 | -0.021157 | -0.002124 | 0.049999 | 0.062691 | -0.039826 | 0.047909 | 0.14332 | 0.004937 | -0.10637 | -0.066219 | -0.008827 | -0.042641 | -0.00775 | 0.15847 | 0.00068 | 0.010886 | 0.029919 | 0.082042 | 0.094734 | -0.007783 | 0.079952 | 0.17536 | 0.03698 | -0.074322 | -0.034176 | 0.023216 | -0.010598 | 0.024293 | 0.11413 | 0.09055 | 0.071156 | 0.047578
3602.5625 | 122.644 | -0.11444 | 122.6852 | 0.13559 | -0.035942 | -0.012 | -0.011281 | 0.040843 | 0.062691 | -0.035248 | 0.057066 | 0.1479 | 0.004937 | -0.097207 | -0.075375 | -0.004248 | -0.042641 | -0.021484 | 0.16763 | -0.003899 | 0.020043 | 0.020762 | 0.072886 | 0.094734 | -0.003205 | 0.089109 | 0.17994 | 0.03698 | -0.065164 | -0.043332 | 0.027795 | -0.010598 | 0.010559 | 0.13244 | 0.099707 | 0.080312 | 0.047578
3604.2656 | 122.731 | -0.091553 | 122.6212 | 0.13101 | -0.026784 | -0.016578 | -0.002124 | 0.036265 | 0.071848 | -0.03067 | 0.052488 | 0.15248 | 0.000359 | -0.10179 | -0.066219 | -0.013405 | -0.051798 | -0.012328 | 0.16305 | 0.005259 | 0.015465 | 0.029919 | 0.068308 | 0.10389 | 0.001373 | 0.084531 | 0.18452 | 0.032402 | -0.069743 | -0.034176 | 0.018638 | -0.019755 | 0.019715 | 0.11871 | 0.10429 | 0.066578 | 0.052157
3606.0312 | 122.7402 | -0.082397 | 122.6212 | 0.12643 | -0.031363 | -0.016578 | -0.002124 | 0.045421 | 0.071848 | -0.035248 | 0.052488 | 0.15248 | 0.004937 | -0.11094 | -0.066219 | -0.013405 | -0.04722 | -0.016906 | 0.15847 | 0.00068 | 0.015465 | 0.029919 | 0.077464 | 0.10389 | -0.003205 | 0.084531 | 0.18452 | 0.03698 | -0.078901 | -0.034176 | 0.018638 | -0.015177 | 0.015137 | 0.11871 | 0.099708 | 0.071156 | 0.052157
3607.7812 | 122.731 | -0.086975 | 122.6074 | 0.13101 | -0.035942 | -0.030314 | -0.006703 | 0.049999 | 0.062691 | -0.035248 | 0.057066 | 0.15248 | -0.004219 | -0.10637 | -0.066219 | -0.008827 | -0.04722 | -0.016906 | 0.16305 | -0.003899 | 0.001729 | 0.02534 | 0.082042 | 0.094734 | -0.003205 | 0.089109 | 0.18452 | 0.027824 | -0.074322 | -0.034176 | 0.023216 | -0.015177 | 0.015137 | 0.12329 | 0.10429 | 0.062 | 0.043001
3609.5312 | 122.7905 | -0.073242 | 122.5891 | 0.12185 | -0.031363 | -0.012 | -0.011281 | 0.049999 | 0.076426 | -0.039826 | 0.057066 | 0.14332 | 0.004937 | -0.097207 | -0.070797 | -0.004248 | -0.04722 | -0.016906 | 0.15389 | 0.00068 | 0.020043 | 0.020762 | 0.082042 | 0.10847 | -0.007783 | 0.089109 | 0.17536 | 0.03698 | -0.065164 | -0.038754 | 0.027795 | -0.015177 | 0.015137 | 0.12786 | 0.10429 | 0.075734 | 0.052157
3611.2969 | 122.7402 | -0.086975 | 122.6166 | 0.13101 | -0.035942 | -0.016578 | -0.006703 | 0.054577 | 0.067269 | -0.039826 | 0.052488 | 0.1479 | 0.000359 | -0.11552 | -0.066219 | -0.008827 | -0.04722 | -0.012328 | 0.16305 | -0.003899 | 0.015465 | 0.02534 | 0.08662 | 0.099312 | -0.007783 | 0.084531 | 0.17994 | 0.032402 | -0.08348 | -0.034176 | 0.023216 | -0.015177 | 0.019715 | 0.11871 | 0.099708 | 0.066578 | 0.047579
3613.0469 | 122.7951 | -0.068665 | 122.6074 | 0.12185 | -0.035942 | -0.021157 | -0.006703 | 0.045421 | 0.071848 | -0.035248 | 0.047909 | 0.1479 | 0.004937 | -0.10637 | -0.075375 | -0.004248 | -0.04722 | -0.016906 | 0.15389 | -0.003899 | 0.010886 | 0.02534 | 0.077464 | 0.10389 | -0.003205 | 0.079952 | 0.17994 | 0.03698 | -0.074322 | -0.043332 | 0.027795 | -0.015177 | 0.015137 | 0.12328 | 0.095129 | 0.080312 | 0.052157
3614.8125 | 122.6852 | -0.10529 | 122.6624 | 0.13101 | -0.026784 | -0.021157 | -0.006703 | 0.049999 | 0.071848 | -0.03067 | 0.052488 | 0.1479 | 0.000359 | -0.10179 | -0.061641 | -0.008827 | -0.04722 | -0.012328 | 0.16305 | 0.005259 | 0.010886 | 0.02534 | 0.082042 | 0.10389 | 0.001373 | 0.084531 | 0.17994 | 0.032402 | -0.069743 | -0.029598 | 0.023216 | -0.015177 | 0.019715 | 0.11413 | 0.099708 | 0.062 | 0.047579
3616.5312 | 122.6852 | -0.10071 | 122.6532 | 0.13559 | -0.031363 | -0.012 | 0.002454 | 0.045421 | 0.076426 | -0.03067 | 0.047909 | 0.1479 | 0.004937 | -0.10637 | -0.075375 | -0.004248 | -0.04722 | -0.012328 | 0.16763 | 0.00068 | 0.020043 | 0.034497 | 0.077464 | 0.10847 | 0.001373 | 0.079952 | 0.17994 | 0.03698 | -0.074322 | -0.043332 | 0.027795 | -0.015177 | 0.019715 | 0.12328 | 0.095129 | 0.080312 | 0.052157
3618.2969 | 122.7722 | -0.086975 | 122.6166 | 0.13101 | -0.026784 | -0.021157 | 0.002454 | 0.045421 | 0.071848 | -0.03067 | 0.047909 | 0.15248 | 0.004937 | -0.10637 | -0.070797 | -0.013405 | -0.051798 | -0.021484 | 0.16305 | 0.005259 | 0.010886 | 0.034497 | 0.077464 | 0.10389 | 0.001373 | 0.079952 | 0.18452 | 0.03698 | -0.074322 | -0.038754 | 0.018638 | -0.019755 | 0.010559 | 0.11871 | 0.099707 | 0.075734 | 0.056735
3620.0625 | 122.7768 | -0.082397 | 122.6257 | 0.12185 | -0.035942 | -0.021157 | -0.006703 | 0.045421 | 0.076426 | -0.026092 | 0.052488 | 0.14332 | 0.004937 | -0.10637 | -0.070797 | -0.013405 | -0.042641 | -0.021484 | 0.15389 | -0.003899 | 0.010886 | 0.02534 | 0.077464 | 0.10847 | 0.005951 | 0.084531 | 0.17536 | 0.03698 | -0.074322 | -0.038754 | 0.018638 | -0.010598 | 0.010559 | 0.12329 | 0.095129 | 0.075734 | 0.047578
3621.7656 | 122.818 | -0.068665 | 122.6395 | 0.12643 | -0.031363 | -0.025735 | -0.002124 | 0.045421 | 0.067269 | -0.03067 | 0.047909 | 0.1479 | 0.000359 | -0.10179 | -0.070797 | -0.008827 | -0.051798 | -0.016906 | 0.15847 | 0.00068 | 0.006308 | 0.029919 | 0.077464 | 0.099312 | 0.001373 | 0.079952 | 0.17994 | 0.032402 | -0.069743 | -0.038754 | 0.023216 | -0.019755 | 0.015137 | 0.11871 | 0.099707 | 0.071156 | 0.052157
3623.5312 | 122.7951 | -0.064087 | 122.6303 | 0.12643 | -0.031363 | -0.016578 | -0.002124 | 0.040843 | 0.062691 | -0.035248 | 0.052488 | 0.15248 | 0.000359 | -0.10637 | -0.070797 | -0.008827 | -0.051798 | -0.016906 | 0.15847 | 0.00068 | 0.015465 | 0.029919 | 0.072886 | 0.094734 | -0.003205 | 0.084531 | 0.18452 | 0.032402 | -0.074322 | -0.038754 | 0.023216 | -0.019755 | 0.015137 | 0.12329 | 0.10429 | 0.071156 | 0.052157
3625.2188 | 122.6624 | -0.10986 | 122.6807 | 0.13101 | -0.031363 | -0.021157 | -0.002124 | 0.036265 | 0.071848 | -0.03067 | 0.047909 | 0.1479 | 0.000359 | -0.10179 | -0.066219 | -0.008827 | -0.04722 | -0.026063 | 0.16305 | 0.00068 | 0.010886 | 0.029919 | 0.068308 | 0.10389 | 0.001373 | 0.079952 | 0.17994 | 0.032402 | -0.069743 | -0.034176 | 0.023216 | -0.015177 | 0.00598 | 0.11413 | 0.095129 | 0.066578 | 0.047579
3626.9844 | 122.7036 | -0.086975 | 122.6624 | 0.13101 | -0.031363 | -0.016578 | -0.006703 | 0.045421 | 0.071848 | -0.039826 | 0.057066 | 0.1479 | 0.000359 | -0.097207 | -0.066219 | -0.008827 | -0.042641 | -0.012328 | 0.16305 | 0.00068 | 0.015465 | 0.02534 | 0.077464 | 0.10389 | -0.007783 | 0.089109 | 0.17994 | 0.032402 | -0.065164 | -0.034176 | 0.023216 | -0.010598 | 0.019715 | 0.12329 | 0.099707 | 0.066578 | 0.043
3628.75 | 122.7173 | -0.10529 | 122.6395 | 0.13101 | -0.031363 | -0.021157 | -0.006703 | 0.045421 | 0.081005 | -0.03067 | 0.047909 | 0.1479 | 0.000359 | -0.10637 | -0.070797 | -0.008827 | -0.042641 | -0.016906 | 0.16305 | 0.00068 | 0.010886 | 0.02534 | 0.077464 | 0.11305 | 0.001373 | 0.079952 | 0.17994 | 0.032402 | -0.074322 | -0.038754 | 0.023216 | -0.010598 | 0.015137 | 0.11871 | 0.09055 | 0.071156 | 0.043
3630.5156 | 122.6669 | -0.1236 | 122.6761 | 0.12643 | -0.026784 | -0.016578 | -0.002124 | 0.049999 | 0.071848 | -0.035248 | 0.052488 | 0.14332 | 0.000359 | -0.11094 | -0.070797 | -0.008827 | -0.042641 | -0.012328 | 0.15847 | 0.005259 | 0.015465 | 0.029919 | 0.082042 | 0.10389 | -0.003205 | 0.084531 | 0.17536 | 0.032402 | -0.078901 | -0.038754 | 0.023216 | -0.010598 | 0.019715 | 0.12329 | 0.095129 | 0.071156 | 0.043
3632.2812 | 122.7859 | -0.045776 | 122.6624 | 0.12185 | -0.035942 | -0.021157 | -0.011281 | 0.045421 | 0.071848 | -0.039826 | 0.047909 | 0.1479 | 0.000359 | -0.10637 | -0.070797 | -0.013405 | -0.042641 | -0.016906 | 0.15389 | -0.003899 | 0.010886 | 0.020762 | 0.077464 | 0.10389 | -0.007783 | 0.079952 | 0.17994 | 0.032402 | -0.074322 | -0.038754 | 0.018638 | -0.010598 | 0.015137 | 0.11871 | 0.09055 | 0.071156 | 0.043
3634.0469 | 122.7539 | -0.07782 | 122.6761 | 0.12185 | -0.040521 | -0.021157 | -0.011281 | 0.045421 | 0.067269 | -0.039826 | 0.047909 | 0.1479 | 0.000359 | -0.10637 | -0.070797 | -0.017983 | -0.042641 | -0.021484 | 0.15389 | -0.008478 | 0.010886 | 0.020762 | 0.077464 | 0.099312 | -0.007783 | 0.079952 | 0.17994 | 0.032402 | -0.074322 | -0.038754 | 0.01406 | -0.010598 | 0.010559 | 0.11871 | 0.09055 | 0.071156 | 0.043
3635.8125 | 122.8043 | -0.041199 | 122.6349 | 0.12643 | -0.035942 | -0.016578 | -0.011281 | 0.045421 | 0.062691 | -0.03067 | 0.052488 | 0.1479 | -0.004219 | -0.11094 | -0.061641 | -0.008827 | -0.042641 | -0.012328 | 0.15847 | -0.003899 | 0.015465 | 0.020762 | 0.077464 | 0.094734 | 0.001373 | 0.084531 | 0.17994 | 0.027824 | -0.078901 | -0.029598 | 0.023216 | -0.010598 | 0.019715 | 0.11413 | 0.095129 | 0.057422 | 0.038422
3637.5 | 122.699 | -0.11444 | 122.6807 | 0.13559 | -0.035942 | -0.021157 | 0.002454 | 0.045421 | 0.067269 | -0.03067 | 0.052488 | 0.1479 | 0.000359 | -0.10179 | -0.066219 | -0.008827 | -0.04722 | -0.016906 | 0.16763 | -0.003899 | 0.010886 | 0.034497 | 0.077464 | 0.099312 | 0.001373 | 0.084531 | 0.17994 | 0.032402 | -0.069743 | -0.034176 | 0.023216 | -0.015177 | 0.015137 | 0.11871 | 0.099708 | 0.066578 | 0.047579
3639.2031 | 122.6898 | -0.11902 | 122.6715 | 0.12185 | -0.035942 | -0.025735 | -0.006703 | 0.059155 | 0.067269 | -0.035248 | 0.052488 | 0.15248 | -0.004219 | -0.10637 | -0.066219 | -0.008827 | -0.04722 | -0.021484 | 0.15389 | -0.003899 | 0.006308 | 0.02534 | 0.091198 | 0.099312 | -0.003205 | 0.084531 | 0.18452 | 0.027824 | -0.074322 | -0.034176 | 0.023216 | -0.015177 | 0.010559 | 0.11871 | 0.099708 | 0.062 | 0.043001
3640.9688 | 122.818 | -0.068665 | 122.6486 | 0.12643 | -0.031363 | -0.016578 | -0.002124 | 0.045421 | 0.071848 | -0.03067 | 0.047909 | 0.1479 | 0.000359 | -0.10637 | -0.061641 | -0.008827 | -0.051798 | -0.012328 | 0.15847 | 0.00068 | 0.015465 | 0.029919 | 0.077464 | 0.10389 | 0.001373 | 0.079952 | 0.17994 | 0.032402 | -0.074322 | -0.029598 | 0.023216 | -0.019755 | 0.019715 | 0.10955 | 0.099707 | 0.062 | 0.052157
3642.7188 | 122.6898 | -0.11902 | 122.6715 | 0.13101 | -0.040521 | -0.016578 | -0.002124 | 0.049999 | 0.076426 | -0.035248 | 0.047909 | 0.1479 | 0.004937 | -0.11094 | -0.070797 | 0.00033 | -0.051798 | -0.016906 | 0.16305 | -0.008478 | 0.015465 | 0.029919 | 0.082042 | 0.10847 | -0.003205 | 0.079952 | 0.17994 | 0.03698 | -0.078901 | -0.038754 | 0.032373 | -0.019755 | 0.015137 | 0.11871 | 0.099707 | 0.075734 | 0.056735
3644.4688 | 122.6715 | -0.1236 | 122.699 | 0.12643 | -0.035942 | -0.025735 | -0.002124 | 0.049999 | 0.071848 | -0.026092 | 0.052488 | 0.15248 | -0.004219 | -0.088049 | -0.070797 | -0.004248 | -0.051798 | -0.016906 | 0.15847 | -0.003899 | 0.006308 | 0.029919 | 0.082042 | 0.10389 | 0.005951 | 0.084531 | 0.18452 | 0.027824 | -0.056006 | -0.038754 | 0.027795 | -0.019755 | 0.015137 | 0.12329 | 0.10429 | 0.066578 | 0.047579
3646.2344 | 122.7173 | -0.11444 | 122.699 | 0.12643 | -0.031363 | -0.016578 | -0.006703 | 0.054577 | 0.076426 | -0.03067 | 0.057066 | 0.15706 | 0.004937 | -0.10637 | -0.070797 | -0.013405 | -0.04722 | -0.012328 | 0.15847 | 0.00068 | 0.015465 | 0.02534 | 0.08662 | 0.10847 | 0.001373 | 0.089109 | 0.1891 | 0.03698 | -0.074322 | -0.038754 | 0.018638 | -0.015177 | 0.019715 | 0.12786 | 0.10429 | 0.075734 | 0.052157
3647.9375 | 122.8043 | -0.073242 | 122.6532 | 0.12643 | -0.031363 | -0.021157 | -0.011281 | 0.045421 | 0.062691 | -0.035248 | 0.047909 | 0.15248 | 0.000359 | -0.097207 | -0.066219 | -0.004248 | -0.051798 | -0.016906 | 0.15847 | 0.00068 | 0.010886 | 0.020762 | 0.077464 | 0.094734 | -0.003205 | 0.079952 | 0.18452 | 0.032402 | -0.065164 | -0.034176 | 0.027795 | -0.019755 | 0.015137 | 0.11413 | 0.099707 | 0.066578 | 0.052157
3649.7031 | 122.7585 | -0.091553 | 122.6532 | 0.12643 | -0.040521 | -0.016578 | -0.006703 | 0.049999 | 0.067269 | -0.039826 | 0.047909 | 0.1479 | 0.000359 | -0.10179 | -0.057062 | -0.008827 | -0.042641 | -0.012328 | 0.15847 | -0.008478 | 0.015465 | 0.02534 | 0.082042 | 0.099312 | -0.007783 | 0.079952 | 0.17994 | 0.032402 | -0.069743 | -0.025019 | 0.023216 | -0.010598 | 0.019715 | 0.10497 | 0.09055 | 0.057421 | 0.043
3651.4844 | 122.6807 | -0.10071 | 122.6624 | 0.12643 | -0.031363 | -0.021157 | -0.006703 | 0.045421 | 0.067269 | -0.039826 | 0.052488 | 0.1479 | -0.004219 | -0.10637 | -0.070797 | -0.004248 | -0.04722 | -0.016906 | 0.15847 | 0.00068 | 0.010886 | 0.02534 | 0.077464 | 0.099312 | -0.007783 | 0.084531 | 0.17994 | 0.027824 | -0.074322 | -0.038754 | 0.027795 | -0.015177 | 0.015137 | 0.12329 | 0.099708 | 0.066578 | 0.043001
3653.25 | 122.7951 | -0.059509 | 122.6624 | 0.13101 | -0.031363 | -0.025735 | -0.011281 | 0.049999 | 0.071848 | -0.035248 | 0.057066 | 0.1479 | 0.000359 | -0.097207 | -0.070797 | -0.008827 | -0.051798 | -0.012328 | 0.16305 | 0.00068 | 0.006308 | 0.020762 | 0.082042 | 0.10389 | -0.003205 | 0.089109 | 0.17994 | 0.032402 | -0.065164 | -0.038754 | 0.023216 | -0.019755 | 0.019715 | 0.12786 | 0.10886 | 0.071156 | 0.052157
3654.9531 | 122.7585 | -0.073242 | 122.6807 | 0.13101 | -0.026784 | -0.021157 | -0.006703 | 0.045421 | 0.067269 | -0.035248 | 0.047909 | 0.1479 | 0.004937 | -0.10637 | -0.061641 | -0.013405 | -0.04722 | -0.012328 | 0.16305 | 0.005259 | 0.010886 | 0.02534 | 0.077464 | 0.099312 | -0.003205 | 0.079952 | 0.17994 | 0.03698 | -0.074322 | -0.029598 | 0.018638 | -0.015177 | 0.019715 | 0.10955 | 0.095129 | 0.066578 | 0.052157
3656.7344 | 122.7905 | -0.07782 | 122.6761 | 0.13101 | -0.026784 | -0.021157 | -0.002124 | 0.049999 | 0.071848 | -0.03067 | 0.043331 | 0.15248 | -0.004219 | -0.10179 | -0.070797 | -0.004248 | -0.051798 | -0.026063 | 0.16305 | 0.005259 | 0.010886 | 0.029919 | 0.082042 | 0.10389 | 0.001373 | 0.075374 | 0.18452 | 0.027824 | -0.069743 | -0.038754 | 0.027795 | -0.019755 | 0.00598 | 0.11413 | 0.095129 | 0.066578 | 0.047579
3658.4375 | 122.699 | -0.11444 | 122.6761 | 0.11727 | -0.031363 | -0.021157 | -0.002124 | 0.040843 | 0.071848 | -0.035248 | 0.057066 | 0.14332 | 0.000359 | -0.11094 | -0.070797 | -0.008827 | -0.04722 | -0.016906 | 0.14932 | 0.00068 | 0.010886 | 0.029919 | 0.072886 | 0.10389 | -0.003205 | 0.089109 | 0.17536 | 0.032402 | -0.078901 | -0.038754 | 0.023216 | -0.015177 | 0.015137 | 0.12786 | 0.10429 | 0.071156 | 0.047579
3660.1875 | 122.6761 | -0.10529 | 122.6898 | 0.12185 | -0.031363 | -0.016578 | -0.01586 | 0.054577 | 0.071848 | -0.039826 | 0.052488 | 0.1479 | -0.004219 | -0.11552 | -0.070797 | -0.017983 | -0.04722 | -0.00775 | 0.15389 | 0.00068 | 0.015465 | 0.016183 | 0.08662 | 0.10389 | -0.007783 | 0.084531 | 0.17994 | 0.027824 | -0.08348 | -0.038754 | 0.01406 | -0.015177 | 0.024293 | 0.12329 | 0.099708 | 0.066578 | 0.043001
3661.8906 | 122.6852 | -0.12817 | 122.6807 | 0.13101 | -0.022205 | -0.012 | -0.011281 | 0.040843 | 0.071848 | -0.03067 | 0.043331 | 0.14332 | 0.004937 | -0.10179 | -0.070797 | -0.013405 | -0.04722 | -0.00775 | 0.16305 | 0.009838 | 0.020043 | 0.020762 | 0.072886 | 0.10389 | 0.001373 | 0.075374 | 0.17536 | 0.03698 | -0.069743 | -0.038754 | 0.018638 | -0.015177 | 0.024293 | 0.11413 | 0.090551 | 0.075734 | 0.052157
3663.6562 | 122.8134 | -0.073242 | 122.6532 | 0.13101 | -0.035942 | -0.016578 | -0.011281 | 0.049999 | 0.071848 | -0.039826 | 0.052488 | 0.15248 | 0.000359 | -0.088049 | -0.066219 | -0.004248 | -0.04722 | -0.012328 | 0.16305 | -0.003899 | 0.015465 | 0.020762 | 0.082042 | 0.10389 | -0.007783 | 0.084531 | 0.18452 | 0.032402 | -0.056006 | -0.034176 | 0.027795 | -0.015177 | 0.019715 | 0.11871 | 0.099708 | 0.066578 | 0.047579
3665.4062 | 122.7539 | -0.086975 | 122.644 | 0.12643 | -0.035942 | -0.016578 | -0.006703 | 0.049999 | 0.071848 | -0.03067 | 0.061645 | 0.14332 | 0.000359 | -0.10637 | -0.070797 | -0.004248 | -0.042641 | -0.021484 | 0.15847 | -0.003899 | 0.015465 | 0.02534 | 0.082042 | 0.10389 | 0.001373 | 0.093688 | 0.17536 | 0.032402 | -0.074322 | -0.038754 | 0.027795 | -0.010598 | 0.010559 | 0.13244 | 0.10429 | 0.071156 | 0.043
3667.1719 | 122.7722 | -0.082397 | 122.6578 | 0.12643 | -0.031363 | -0.021157 | -0.011281 | 0.045421 | 0.067269 | -0.035248 | 0.052488 | 0.1479 | 0.004937 | -0.11552 | -0.066219 | -0.008827 | -0.04722 | -0.016906 | 0.15847 | 0.00068 | 0.010886 | 0.020762 | 0.077464 | 0.099312 | -0.003205 | 0.084531 | 0.17994 | 0.03698 | -0.08348 | -0.034176 | 0.023216 | -0.015177 | 0.015137 | 0.11871 | 0.099708 | 0.071156 | 0.052157
3668.875 | 122.6898 | -0.10986 | 122.7081 | 0.13559 | -0.031363 | -0.016578 | -0.002124 | 0.040843 | 0.076426 | -0.03067 | 0.061645 | 0.15248 | 0.004937 | -0.10637 | -0.070797 | -0.013405 | -0.04722 | -0.00775 | 0.16763 | 0.00068 | 0.015465 | 0.029919 | 0.072886 | 0.10847 | 0.001373 | 0.093688 | 0.18452 | 0.03698 | -0.074322 | -0.038754 | 0.018638 | -0.015177 | 0.024293 | 0.13244 | 0.10886 | 0.075734 | 0.052157
3670.6406 | 122.8088 | -0.059509 | 122.6944 | 0.13101 | -0.031363 | -0.021157 | -0.002124 | 0.045421 | 0.071848 | -0.026092 | 0.052488 | 0.1479 | 0.000359 | -0.10637 | -0.066219 | -0.008827 | -0.04722 | -0.00775 | 0.16305 | 0.00068 | 0.010886 | 0.029919 | 0.077464 | 0.10389 | 0.005951 | 0.084531 | 0.17994 | 0.032402 | -0.074322 | -0.034176 | 0.023216 | -0.015177 | 0.024293 | 0.11871 | 0.099708 | 0.066578 | 0.047579
3672.4062 | 122.699 | -0.10986 | 122.6807 | 0.13101 | -0.031363 | -0.021157 | -0.011281 | 0.049999 | 0.067269 | -0.035248 | 0.052488 | 0.13874 | 0.000359 | -0.10637 | -0.066219 | -0.013405 | -0.051798 | -0.016906 | 0.16305 | 0.00068 | 0.010886 | 0.020762 | 0.082042 | 0.099312 | -0.003205 | 0.084531 | 0.17079 | 0.032402 | -0.074322 | -0.034176 | 0.018638 | -0.019755 | 0.015137 | 0.11871 | 0.10429 | 0.066578 | 0.052157
3674.1562 | 122.699 | -0.10529 | 122.7081 | 0.12643 | -0.031363 | -0.016578 | -0.011281 | 0.049999 | 0.071848 | -0.035248 | 0.052488 | 0.1479 | -0.004219 | -0.10179 | -0.070797 | -0.008827 | -0.04722 | -0.016906 | 0.15847 | 0.00068 | 0.015465 | 0.020762 | 0.082042 | 0.10389 | -0.003205 | 0.084531 | 0.17994 | 0.027824 | -0.069743 | -0.038754 | 0.023216 | -0.015177 | 0.015137 | 0.12329 | 0.099708 | 0.066578 | 0.043001
3675.8594 | 122.7859 | -0.07782 | 122.6669 | 0.13101 | -0.031363 | -0.016578 | -0.011281 | 0.040843 | 0.067269 | -0.03067 | 0.047909 | 0.15248 | 0.004937 | -0.10637 | -0.070797 | -0.004248 | -0.051798 | -0.012328 | 0.16305 | 0.00068 | 0.015465 | 0.020762 | 0.072886 | 0.099312 | 0.001373 | 0.079952 | 0.18452 | 0.03698 | -0.074322 | -0.038754 | 0.027795 | -0.019755 | 0.019715 | 0.11871 | 0.099707 | 0.075734 | 0.056735
3677.625 | 122.7127 | -0.1236 | 122.6944 | 0.13559 | -0.031363 | -0.016578 | -0.002124 | 0.045421 | 0.071848 | -0.035248 | 0.047909 | 0.15706 | 0.000359 | -0.10179 | -0.075375 | -0.008827 | -0.051798 | -0.016906 | 0.16763 | 0.00068 | 0.015465 | 0.029919 | 0.077464 | 0.10389 | -0.003205 | 0.079952 | 0.1891 | 0.032402 | -0.069743 | -0.043332 | 0.023216 | -0.019755 | 0.015137 | 0.12328 | 0.099707 | 0.075734 | 0.052157
3679.3125 | 122.7036 | -0.11444 | 122.7081 | 0.13101 | -0.031363 | -0.016578 | -0.011281 | 0.036265 | 0.076426 | -0.026092 | 0.052488 | 0.14332 | 0.009515 | -0.10179 | -0.075375 | -0.004248 | -0.051798 | -0.012328 | 0.16305 | 0.00068 | 0.015465 | 0.020762 | 0.068308 | 0.10847 | 0.005951 | 0.084531 | 0.17536 | 0.041558 | -0.069743 | -0.043332 | 0.027795 | -0.019755 | 0.019715 | 0.12786 | 0.10429 | 0.08489 | 0.061313
3681.0781 | 122.8363 | -0.054932 | 122.6715 | 0.12643 | -0.035942 | -0.016578 | 0.007033 | 0.045421 | 0.076426 | -0.035248 | 0.052488 | 0.1479 | 0.004937 | -0.10179 | -0.070797 | -0.008827 | -0.04722 | -0.016906 | 0.15847 | -0.003899 | 0.015465 | 0.039076 | 0.077464 | 0.10847 | -0.003205 | 0.084531 | 0.17994 | 0.03698 | -0.069743 | -0.038754 | 0.023216 | -0.015177 | 0.015137 | 0.12329 | 0.099708 | 0.075734 | 0.052157
3682.7812 | 122.7814 | -0.09613 | 122.6852 | 0.13101 | -0.031363 | -0.021157 | -0.011281 | 0.045421 | 0.071848 | -0.044405 | 0.052488 | 0.1479 | -0.004219 | -0.10637 | -0.066219 | -0.004248 | -0.038063 | -0.016906 | 0.16305 | 0.00068 | 0.010886 | 0.020762 | 0.077464 | 0.10389 | -0.012362 | 0.084531 | 0.17994 | 0.027824 | -0.074322 | -0.034176 | 0.027795 | -0.00602 | 0.015137 | 0.11871 | 0.090551 | 0.062 | 0.033844
3684.5312 | 122.8363 | -0.082397 | 122.6715 | 0.13101 | -0.040521 | -0.021157 | -0.006703 | 0.049999 | 0.071848 | -0.035248 | 0.052488 | 0.15248 | 0.000359 | -0.11094 | -0.075375 | -0.004248 | -0.042641 | -0.021484 | 0.16305 | -0.008478 | 0.010886 | 0.02534 | 0.082042 | 0.10389 | -0.003205 | 0.084531 | 0.18452 | 0.032402 | -0.078901 | -0.043332 | 0.027795 | -0.010598 | 0.010559 | 0.12786 | 0.095129 | 0.075734 | 0.043
3686.2344 | 122.8363 | -0.045776 | 122.6578 | 0.12643 | -0.026784 | -0.016578 | -0.006703 | 0.049999 | 0.067269 | -0.035248 | 0.052488 | 0.15248 | 0.000359 | -0.11094 | -0.061641 | -0.008827 | -0.042641 | -0.012328 | 0.15847 | 0.005259 | 0.015465 | 0.02534 | 0.082042 | 0.099312 | -0.003205 | 0.084531 | 0.18452 | 0.032402 | -0.078901 | -0.029598 | 0.023216 | -0.010598 | 0.019715 | 0.11413 | 0.095129 | 0.062 | 0.043
3688 | 122.8455 | -0.064087 | 122.6532 | 0.13101 | -0.031363 | -0.021157 | -0.01586 | 0.049999 | 0.062691 | -0.026092 | 0.052488 | 0.1479 | 0.000359 | -0.088049 | -0.070797 | -0.004248 | -0.04722 | -0.021484 | 0.16305 | 0.00068 | 0.010886 | 0.016183 | 0.082042 | 0.094734 | 0.005951 | 0.084531 | 0.17994 | 0.032402 | -0.056006 | -0.038754 | 0.027795 | -0.015177 | 0.010559 | 0.12329 | 0.099708 | 0.071156 | 0.047579
3689.7656 | 122.7539 | -0.10071 | 122.7127 | 0.12643 | -0.031363 | -0.025735 | -0.011281 | 0.049999 | 0.071848 | -0.03067 | 0.043331 | 0.15248 | 0.004937 | -0.10637 | -0.070797 | -0.017983 | -0.038063 | -0.021484 | 0.15847 | 0.00068 | 0.006308 | 0.020762 | 0.082042 | 0.10389 | 0.001373 | 0.075374 | 0.18452 | 0.03698 | -0.074322 | -0.038754 | 0.01406 | -0.00602 | 0.010559 | 0.11413 | 0.081394 | 0.075734 | 0.043
3691.4688 | 122.7036 | -0.10986 | 122.699 | 0.13101 | -0.026784 | -0.016578 | 0.002454 | 0.054577 | 0.071848 | -0.035248 | 0.052488 | 0.1479 | 0.000359 | -0.10179 | -0.070797 | -0.004248 | -0.04722 | -0.016906 | 0.16305 | 0.005259 | 0.015465 | 0.034497 | 0.08662 | 0.10389 | -0.003205 | 0.084531 | 0.17994 | 0.032402 | -0.069743 | -0.038754 | 0.027795 | -0.015177 | 0.015137 | 0.12329 | 0.099708 | 0.071156 | 0.047579
3693.2344 | 122.7081 | -0.12817 | 122.7173 | 0.13101 | -0.035942 | -0.021157 | -0.006703 | 0.045421 | 0.076426 | -0.039826 | 0.047909 | 0.1479 | 0.004937 | -0.10179 | -0.070797 | -0.013405 | -0.042641 | -0.016906 | 0.16305 | -0.003899 | 0.010886 | 0.02534 | 0.077464 | 0.10847 | -0.007783 | 0.079952 | 0.17994 | 0.03698 | -0.069743 | -0.038754 | 0.018638 | -0.010598 | 0.015137 | 0.11871 | 0.09055 | 0.075734 | 0.047578
3695 | 122.7219 | -0.10986 | 122.7264 | 0.12643 | -0.035942 | -0.021157 | -0.011281 | 0.049999 | 0.071848 | -0.026092 | 0.043331 | 0.15248 | -0.008798 | -0.10637 | -0.066219 | -0.004248 | -0.051798 | -0.016906 | 0.15847 | -0.003899 | 0.010886 | 0.020762 | 0.082042 | 0.10389 | 0.005951 | 0.075374 | 0.18452 | 0.023245 | -0.074322 | -0.034176 | 0.027795 | -0.019755 | 0.015137 | 0.10955 | 0.095129 | 0.057421 | 0.043
3696.7031 | 122.7768 | -0.10986 | 122.7127 | 0.12185 | -0.031363 | -0.025735 | -0.006703 | 0.045421 | 0.081005 | -0.026092 | 0.057066 | 0.1479 | 0.004937 | -0.10179 | -0.066219 | -0.013405 | -0.042641 | -0.012328 | 0.15389 | 0.00068 | 0.006308 | 0.02534 | 0.077464 | 0.11305 | 0.005951 | 0.089109 | 0.17994 | 0.03698 | -0.069743 | -0.034176 | 0.018638 | -0.010598 | 0.019715 | 0.12329 | 0.099707 | 0.071156 | 0.047578
3698.4688 | 122.7402 | -0.10986 | 122.7173 | 0.12643 | -0.031363 | -0.021157 | -0.006703 | 0.045421 | 0.067269 | -0.035248 | 0.052488 | 0.15706 | 0.000359 | -0.10637 | -0.070797 | -0.004248 | -0.042641 | -0.012328 | 0.15847 | 0.00068 | 0.010886 | 0.02534 | 0.077464 | 0.099312 | -0.003205 | 0.084531 | 0.1891 | 0.032402 | -0.074322 | -0.038754 | 0.027795 | -0.010598 | 0.019715 | 0.12329 | 0.095129 | 0.071156 | 0.043
3700.2188 | 122.7539 | -0.09613 | 122.699 | 0.12185 | -0.035942 | -0.012 | -0.006703 | 0.040843 | 0.071848 | -0.03067 | 0.057066 | 0.1479 | -0.004219 | -0.11094 | -0.066219 | -0.004248 | -0.04722 | -0.012328 | 0.15389 | -0.003899 | 0.020043 | 0.02534 | 0.072886 | 0.10389 | 0.001373 | 0.089109 | 0.17994 | 0.027824 | -0.078901 | -0.034176 | 0.027795 | -0.015177 | 0.019715 | 0.12329 | 0.10429 | 0.062 | 0.043001
3701.9219 | 122.7036 | -0.1236 | 122.7402 | 0.12643 | -0.026784 | -0.016578 | -0.002124 | 0.049999 | 0.071848 | -0.035248 | 0.061645 | 0.15706 | 0.009515 | -0.10637 | -0.070797 | -0.008827 | -0.04722 | -0.012328 | 0.15847 | 0.005259 | 0.015465 | 0.029919 | 0.082042 | 0.10389 | -0.003205 | 0.093688 | 0.1891 | 0.041558 | -0.074322 | -0.038754 | 0.023216 | -0.015177 | 0.019715 | 0.13244 | 0.10886 | 0.080312 | 0.056735
3703.6719 | 122.8592 | -0.068665 | 122.7036 | 0.12643 | -0.026784 | -0.016578 | -0.002124 | 0.049999 | 0.071848 | -0.026092 | 0.047909 | 0.14332 | 0.004937 | -0.10179 | -0.075375 | -0.008827 | -0.051798 | -0.016906 | 0.15847 | 0.005259 | 0.015465 | 0.029919 | 0.082042 | 0.10389 | 0.005951 | 0.079952 | 0.17536 | 0.03698 | -0.069743 | -0.043332 | 0.023216 | -0.019755 | 0.015137 | 0.12328 | 0.099707 | 0.080312 | 0.056735
3705.4375 | 122.7264 | -0.10529 | 122.7402 | 0.13101 | -0.031363 | -0.016578 | -0.002124 | 0.045421 | 0.076426 | -0.016936 | 0.061645 | 0.15248 | -0.004219 | -0.10637 | -0.070797 | -0.004248 | -0.042641 | -0.012328 | 0.16305 | 0.00068 | 0.015465 | 0.029919 | 0.077464 | 0.10847 | 0.015107 | 0.093688 | 0.18452 | 0.027824 | -0.074322 | -0.038754 | 0.027795 | -0.010598 | 0.019715 | 0.13244 | 0.10429 | 0.066578 | 0.038422
3707.1875 | 122.7997 | -0.07782 | 122.6944 | 0.12643 | -0.035942 | -0.025735 | 0.002454 | 0.049999 | 0.071848 | -0.03067 | 0.057066 | 0.1479 | 0.004937 | -0.10179 | -0.070797 | -0.008827 | -0.04722 | -0.012328 | 0.15847 | -0.003899 | 0.006308 | 0.034497 | 0.082042 | 0.10389 | 0.001373 | 0.089109 | 0.17994 | 0.03698 | -0.069743 | -0.038754 | 0.023216 | -0.015177 | 0.019715 | 0.12786 | 0.10429 | 0.075734 | 0.052157
3708.8906 | 122.7264 | -0.11444 | 122.7356 | 0.13559 | -0.031363 | -0.016578 | -0.002124 | 0.045421 | 0.067269 | -0.03067 | 0.066223 | 0.14332 | -0.008798 | -0.10637 | -0.066219 | -0.008827 | -0.056376 | -0.016906 | 0.16763 | 0.00068 | 0.015465 | 0.029919 | 0.077464 | 0.099312 | 0.001373 | 0.098266 | 0.17536 | 0.023245 | -0.074322 | -0.034176 | 0.023216 | -0.024333 | 0.015137 | 0.13244 | 0.1226 | 0.057421 | 0.047578
3710.6562 | 122.7722 | -0.07782 | 122.699 | 0.13101 | -0.031363 | -0.016578 | -0.002124 | 0.045421 | 0.062691 | -0.035248 | 0.061645 | 0.15248 | 0.004937 | -0.11094 | -0.066219 | -0.008827 | -0.051798 | -0.016906 | 0.16305 | 0.00068 | 0.015465 | 0.029919 | 0.077464 | 0.094734 | -0.003205 | 0.093688 | 0.18452 | 0.03698 | -0.078901 | -0.034176 | 0.023216 | -0.019755 | 0.015137 | 0.12786 | 0.11344 | 0.071156 | 0.056735
3712.3594 | 122.7539 | -0.1236 | 122.7356 | 0.13559 | -0.026784 | -0.016578 | -0.006703 | 0.045421 | 0.067269 | -0.026092 | 0.052488 | 0.1479 | -0.004219 | -0.10637 | -0.070797 | -0.004248 | -0.042641 | -0.016906 | 0.16763 | 0.005259 | 0.015465 | 0.02534 | 0.077464 | 0.099312 | 0.005951 | 0.084531 | 0.17994 | 0.027824 | -0.074322 | -0.038754 | 0.027795 | -0.010598 | 0.015137 | 0.12329 | 0.095129 | 0.066578 | 0.038422
3714.125 | 122.8409 | -0.064087 | 122.7081 | 0.12643 | -0.035942 | -0.021157 | -0.006703 | 0.054577 | 0.067269 | -0.035248 | 0.057066 | 0.14332 | -0.008798 | -0.08347 | -0.079953 | -0.004248 | -0.04722 | -0.012328 | 0.15847 | -0.003899 | 0.010886 | 0.02534 | 0.08662 | 0.099312 | -0.003205 | 0.089109 | 0.17536 | 0.023245 | -0.051427 | -0.04791 | 0.027795 | -0.015177 | 0.019715 | 0.13702 | 0.10429 | 0.071155 | 0.038422
3715.8125 | 122.7036 | -0.10071 | 122.7448 | 0.12643 | -0.035942 | -0.025735 | 0.002454 | 0.045421 | 0.071848 | -0.035248 | 0.057066 | 0.1479 | -0.004219 | -0.10637 | -0.070797 | -0.008827 | -0.042641 | -0.016906 | 0.15847 | -0.003899 | 0.006308 | 0.034497 | 0.077464 | 0.10389 | -0.003205 | 0.089109 | 0.17994 | 0.027824 | -0.074322 | -0.038754 | 0.023216 | -0.010598 | 0.015137 | 0.12786 | 0.099707 | 0.066578 | 0.038422
3717.5781 | 122.8409 | -0.064087 | 122.699 | 0.12643 | -0.040521 | -0.021157 | -0.006703 | 0.045421 | 0.071848 | -0.03067 | 0.057066 | 0.15248 | 0.004937 | -0.10179 | -0.070797 | -0.004248 | -0.04722 | -0.012328 | 0.15847 | -0.008478 | 0.010886 | 0.02534 | 0.077464 | 0.10389 | 0.001373 | 0.089109 | 0.18452 | 0.03698 | -0.069743 | -0.038754 | 0.027795 | -0.015177 | 0.019715 | 0.12786 | 0.10429 | 0.075734 | 0.052157
3719.2812 | 122.7081 | -0.10529 | 122.7173 | 0.12643 | -0.022205 | -0.012 | -0.002124 | 0.049999 | 0.062691 | -0.035248 | 0.052488 | 0.1479 | 0.000359 | -0.10637 | -0.066219 | -0.013405 | -0.04722 | -0.021484 | 0.15847 | 0.009838 | 0.020043 | 0.029919 | 0.082042 | 0.094734 | -0.003205 | 0.084531 | 0.17994 | 0.032402 | -0.074322 | -0.034176 | 0.018638 | -0.015177 | 0.010559 | 0.11871 | 0.099708 | 0.066578 | 0.047579
3721.0469 | 122.7264 | -0.11902 | 122.7264 | 0.12185 | -0.026784 | -0.007421 | -0.002124 | 0.045421 | 0.071848 | -0.026092 | 0.057066 | 0.1479 | 0.000359 | -0.10179 | -0.070797 | -0.008827 | -0.051798 | -0.016906 | 0.15389 | 0.005259 | 0.024622 | 0.029919 | 0.077464 | 0.10389 | 0.005951 | 0.089109 | 0.17994 | 0.032402 | -0.069743 | -0.038754 | 0.023216 | -0.019755 | 0.015137 | 0.12786 | 0.10886 | 0.071156 | 0.052157
3722.75 | 122.8455 | -0.07782 | 122.7219 | 0.12643 | -0.035942 | -0.021157 | -0.002124 | 0.045421 | 0.076426 | -0.035248 | 0.057066 | 0.15248 | -0.008798 | -0.11094 | -0.066219 | -0.008827 | -0.04722 | -0.016906 | 0.15847 | -0.003899 | 0.010886 | 0.029919 | 0.077464 | 0.10847 | -0.003205 | 0.089109 | 0.18452 | 0.023245 | -0.078901 | -0.034176 | 0.023216 | -0.015177 | 0.015137 | 0.12329 | 0.10429 | 0.057421 | 0.038422
3724.5156 | 122.8546 | -0.059509 | 122.731 | 0.13101 | -0.031363 | -0.021157 | -0.006703 | 0.040843 | 0.076426 | -0.039826 | 0.057066 | 0.1479 | 0.000359 | -0.11094 | -0.066219 | -0.017983 | -0.04722 | -0.021484 | 0.16305 | 0.00068 | 0.010886 | 0.02534 | 0.072886 | 0.10847 | -0.007783 | 0.089109 | 0.17994 | 0.032402 | -0.078901 | -0.034176 | 0.01406 | -0.015177 | 0.010559 | 0.12329 | 0.10429 | 0.066578 | 0.047579
3726.2188 | 122.7997 | -0.091553 | 122.6898 | 0.12643 | -0.035942 | -0.021157 | -0.002124 | 0.045421 | 0.062691 | -0.03067 | 0.052488 | 0.15248 | 0.004937 | -0.10637 | -0.070797 | -0.004248 | -0.04722 | -0.012328 | 0.15847 | -0.003899 | 0.010886 | 0.029919 | 0.077464 | 0.094734 | 0.001373 | 0.084531 | 0.18452 | 0.03698 | -0.074322 | -0.038754 | 0.027795 | -0.015177 | 0.019715 | 0.12329 | 0.099708 | 0.075734 | 0.052157
3727.9844 | 122.7081 | -0.11902 | 122.7356 | 0.12643 | -0.026784 | -0.012 | 0.002454 | 0.045421 | 0.058113 | -0.035248 | 0.057066 | 0.1479 | -0.004219 | -0.10637 | -0.066219 | -0.008827 | -0.04722 | -0.012328 | 0.15847 | 0.005259 | 0.020043 | 0.034497 | 0.077464 | 0.090156 | -0.003205 | 0.089109 | 0.17994 | 0.027824 | -0.074322 | -0.034176 | 0.023216 | -0.015177 | 0.019715 | 0.12329 | 0.10429 | 0.062 | 0.043001
3729.7344 | 122.7219 | -0.10071 | 122.7356 | 0.12643 | -0.031363 | -0.025735 | 0.002454 | 0.045421 | 0.071848 | -0.039826 | 0.052488 | 0.1479 | 0.000359 | -0.10179 | -0.070797 | -0.008827 | -0.04722 | -0.012328 | 0.15847 | 0.00068 | 0.006308 | 0.034497 | 0.077464 | 0.10389 | -0.007783 | 0.084531 | 0.17994 | 0.032402 | -0.069743 | -0.038754 | 0.023216 | -0.015177 | 0.019715 | 0.12329 | 0.099708 | 0.071156 | 0.047579
3731.5 | 122.7539 | -0.11444 | 122.7356 | 0.13101 | -0.035942 | -0.016578 | -0.006703 | 0.040843 | 0.071848 | -0.026092 | 0.052488 | 0.1479 | 0.000359 | -0.097207 | -0.066219 | -0.013405 | -0.042641 | -0.00775 | 0.16305 | -0.003899 | 0.015465 | 0.02534 | 0.072886 | 0.10389 | 0.005951 | 0.084531 | 0.17994 | 0.032402 | -0.065164 | -0.034176 | 0.018638 | -0.010598 | 0.024293 | 0.11871 | 0.095129 | 0.066578 | 0.043
3733.2812 | 122.7722 | -0.11902 | 122.7676 | 0.13101 | -0.026784 | -0.016578 | -0.006703 | 0.054577 | 0.071848 | -0.026092 | 0.057066 | 0.15248 | 0.004937 | -0.11094 | -0.070797 | -0.008827 | -0.042641 | -0.012328 | 0.16305 | 0.005259 | 0.015465 | 0.02534 | 0.08662 | 0.10389 | 0.005951 | 0.089109 | 0.18452 | 0.03698 | -0.078901 | -0.038754 | 0.023216 | -0.010598 | 0.019715 | 0.12786 | 0.099707 | 0.075734 | 0.047578
3735.0469 | 122.7127 | -0.11902 | 122.7219 | 0.12643 | -0.035942 | -0.016578 | 0.002454 | 0.049999 | 0.076426 | -0.03067 | 0.057066 | 0.15248 | -0.004219 | -0.10637 | -0.070797 | -0.004248 | -0.042641 | -0.021484 | 0.15847 | -0.003899 | 0.015465 | 0.034497 | 0.082042 | 0.10847 | 0.001373 | 0.089109 | 0.18452 | 0.027824 | -0.074322 | -0.038754 | 0.027795 | -0.010598 | 0.010559 | 0.12786 | 0.099707 | 0.066578 | 0.038422
3736.7656 | 122.7814 | -0.091553 | 122.7173 | 0.13101 | -0.026784 | -0.012 | -0.002124 | 0.049999 | 0.076426 | -0.03067 | 0.052488 | 0.15248 | 0.000359 | -0.11094 | -0.061641 | -0.004248 | -0.042641 | -0.016906 | 0.16305 | 0.005259 | 0.020043 | 0.029919 | 0.082042 | 0.10847 | 0.001373 | 0.084531 | 0.18452 | 0.032402 | -0.078901 | -0.029598 | 0.027795 | -0.010598 | 0.015137 | 0.11413 | 0.095129 | 0.062 | 0.043
3738.4844 | 122.8683 | -0.07782 | 122.6898 | 0.13101 | -0.035942 | -0.021157 | -0.002124 | 0.054577 | 0.067269 | -0.026092 | 0.052488 | 0.15248 | 0.004937 | -0.10637 | -0.066219 | -0.008827 | -0.04722 | -0.016906 | 0.16305 | -0.003899 | 0.010886 | 0.029919 | 0.08662 | 0.099312 | 0.005951 | 0.084531 | 0.18452 | 0.03698 | -0.074322 | -0.034176 | 0.023216 | -0.015177 | 0.015137 | 0.11871 | 0.099708 | 0.071156 | 0.052157
3740.25 | 122.8226 | -0.086975 | 122.6807 | 0.13101 | -0.031363 | -0.025735 | -0.011281 | 0.049999 | 0.067269 | -0.035248 | 0.061645 | 0.15706 | 0.004937 | -0.092628 | -0.070797 | -0.013405 | -0.04722 | -0.021484 | 0.16305 | 0.00068 | 0.006308 | 0.020762 | 0.082042 | 0.099312 | -0.003205 | 0.093688 | 0.1891 | 0.03698 | -0.060585 | -0.038754 | 0.018638 | -0.015177 | 0.010559 | 0.13244 | 0.10886 | 0.075734 | 0.052157
3742.0156 | 122.8638 | -0.068665 | 122.6944 | 0.13101 | -0.031363 | -0.016578 | -0.006703 | 0.045421 | 0.067269 | -0.03067 | 0.047909 | 0.15706 | 0.000359 | -0.10179 | -0.066219 | -0.004248 | -0.04722 | -0.021484 | 0.16305 | 0.00068 | 0.015465 | 0.02534 | 0.077464 | 0.099312 | 0.001373 | 0.079952 | 0.1891 | 0.032402 | -0.069743 | -0.034176 | 0.027795 | -0.015177 | 0.010559 | 0.11413 | 0.095129 | 0.066578 | 0.047579
3743.7188 | 122.818 | -0.082397 | 122.7081 | 0.13101 | -0.035942 | -0.021157 | 0.002454 | 0.045421 | 0.071848 | -0.035248 | 0.047909 | 0.15248 | 0.004937 | -0.10637 | -0.070797 | -0.004248 | -0.04722 | -0.021484 | 0.16305 | -0.003899 | 0.010886 | 0.034497 | 0.077464 | 0.10389 | -0.003205 | 0.079952 | 0.18452 | 0.03698 | -0.074322 | -0.038754 | 0.027795 | -0.015177 | 0.010559 | 0.11871 | 0.095129 | 0.075734 | 0.052157
3745.4844 | 122.8592 | -0.086975 | 122.7081 | 0.12643 | -0.026784 | -0.012 | -0.006703 | 0.049999 | 0.076426 | -0.035248 | 0.057066 | 0.15706 | 0.004937 | -0.10637 | -0.070797 | -0.008827 | -0.042641 | -0.021484 | 0.15847 | 0.005259 | 0.020043 | 0.02534 | 0.082042 | 0.10847 | -0.003205 | 0.089109 | 0.1891 | 0.03698 | -0.074322 | -0.038754 | 0.023216 | -0.010598 | 0.010559 | 0.12786 | 0.099707 | 0.075734 | 0.047578
3747.1719 | 122.8729 | -0.07782 | 122.699 | 0.12643 | -0.031363 | -0.016578 | -0.002124 | 0.049999 | 0.067269 | -0.035248 | 0.052488 | 0.15248 | 0.000359 | -0.10637 | -0.070797 | -0.013405 | -0.051798 | -0.00775 | 0.15847 | 0.00068 | 0.015465 | 0.029919 | 0.082042 | 0.099312 | -0.003205 | 0.084531 | 0.18452 | 0.032402 | -0.074322 | -0.038754 | 0.018638 | -0.019755 | 0.024293 | 0.12329 | 0.10429 | 0.071156 | 0.052157
3748.9375 | 122.7859 | -0.09613 | 122.7356 | 0.12643 | -0.031363 | -0.025735 | -0.002124 | 0.054577 | 0.071848 | -0.035248 | 0.052488 | 0.15706 | 0.000359 | -0.10179 | -0.070797 | -0.008827 | -0.04722 | -0.00775 | 0.15847 | 0.00068 | 0.006308 | 0.029919 | 0.08662 | 0.10389 | -0.003205 | 0.084531 | 0.1891 | 0.032402 | -0.069743 | -0.038754 | 0.023216 | -0.015177 | 0.024293 | 0.12329 | 0.099708 | 0.071156 | 0.047579
3750.6875 | 122.7356 | -0.1236 | 122.7448 | 0.12643 | -0.035942 | -0.021157 | -0.002124 | 0.049999 | 0.071848 | -0.03067 | 0.052488 | 0.1479 | 0.000359 | -0.11094 | -0.066219 | -0.008827 | -0.042641 | -0.016906 | 0.15847 | -0.003899 | 0.010886 | 0.029919 | 0.082042 | 0.10389 | 0.001373 | 0.084531 | 0.17994 | 0.032402 | -0.078901 | -0.034176 | 0.023216 | -0.010598 | 0.015137 | 0.11871 | 0.095129 | 0.066578 | 0.043
3752.4531 | 122.7493 | -0.14648 | 122.7539 | 0.11727 | -0.040521 | -0.016578 | -0.006703 | 0.040843 | 0.071848 | -0.03067 | 0.061645 | 0.1479 | 0.004937 | -0.078891 | -0.066219 | -0.008827 | -0.042641 | -0.012328 | 0.14932 | -0.008478 | 0.015465 | 0.02534 | 0.072886 | 0.10389 | 0.001373 | 0.093688 | 0.17994 | 0.03698 | -0.046848 | -0.034176 | 0.023216 | -0.010598 | 0.019715 | 0.12786 | 0.10429 | 0.071156 | 0.047578
3754.2031 | 122.7402 | -0.11444 | 122.7356 | 0.13101 | -0.035942 | -0.021157 | -0.002124 | 0.049999 | 0.071848 | -0.03067 | 0.057066 | 0.1479 | 0.004937 | -0.11094 | -0.070797 | -0.017983 | -0.051798 | -0.016906 | 0.16305 | -0.003899 | 0.010886 | 0.029919 | 0.082042 | 0.10389 | 0.001373 | 0.089109 | 0.17994 | 0.03698 | -0.078901 | -0.038754 | 0.01406 | -0.019755 | 0.015137 | 0.12786 | 0.10886 | 0.075734 | 0.056735
3755.9062 | 122.818 | -0.091553 | 122.7264 | 0.13101 | -0.031363 | -0.021157 | -0.006703 | 0.049999 | 0.067269 | -0.035248 | 0.052488 | 0.1479 | 0.000359 | -0.10179 | -0.066219 | -0.017983 | -0.04722 | -0.016906 | 0.16305 | 0.00068 | 0.010886 | 0.02534 | 0.082042 | 0.099312 | -0.003205 | 0.084531 | 0.17994 | 0.032402 | -0.069743 | -0.034176 | 0.01406 | -0.015177 | 0.015137 | 0.11871 | 0.099708 | 0.066578 | 0.047579
3757.6719 | 122.7219 | -0.10986 | 122.7219 | 0.13101 | -0.031363 | -0.021157 | -0.002124 | 0.045421 | 0.081005 | -0.03067 | 0.057066 | 0.1479 | 0.004937 | -0.11094 | -0.057062 | -0.017983 | -0.042641 | -0.012328 | 0.16305 | 0.00068 | 0.010886 | 0.029919 | 0.077464 | 0.11305 | 0.001373 | 0.089109 | 0.17994 | 0.03698 | -0.078901 | -0.025019 | 0.01406 | -0.010598 | 0.019715 | 0.11413 | 0.099707 | 0.061999 | 0.047578
3759.4375 | 122.8546 | -0.091553 | 122.7219 | 0.12185 | -0.022205 | -0.016578 | -0.006703 | 0.049999 | 0.071848 | -0.03067 | 0.052488 | 0.1479 | 0.004937 | -0.10637 | -0.070797 | -0.004248 | -0.04722 | -0.012328 | 0.15389 | 0.009838 | 0.015465 | 0.02534 | 0.082042 | 0.10389 | 0.001373 | 0.084531 | 0.17994 | 0.03698 | -0.074322 | -0.038754 | 0.027795 | -0.015177 | 0.019715 | 0.12329 | 0.099708 | 0.075734 | 0.052157
3761.1406 | 122.85 | -0.082397 | 122.7081 | 0.12643 | -0.035942 | -0.016578 | -0.006703 | 0.045421 | 0.067269 | -0.035248 | 0.057066 | 0.1479 | -0.004219 | -0.11094 | -0.070797 | -0.008827 | -0.04722 | -0.012328 | 0.15847 | -0.003899 | 0.015465 | 0.02534 | 0.077464 | 0.099312 | -0.003205 | 0.089109 | 0.17994 | 0.027824 | -0.078901 | -0.038754 | 0.023216 | -0.015177 | 0.019715 | 0.12786 | 0.10429 | 0.066578 | 0.043001
3762.9062 | 122.8455 | -0.09613 | 122.7127 | 0.13101 | -0.040521 | -0.016578 | -0.002124 | 0.049999 | 0.062691 | -0.03067 | 0.052488 | 0.15248 | 0.000359 | -0.10179 | -0.070797 | -0.013405 | -0.04722 | -0.016906 | 0.16305 | -0.008478 | 0.015465 | 0.029919 | 0.082042 | 0.094734 | 0.001373 | 0.084531 | 0.18452 | 0.032402 | -0.069743 | -0.038754 | 0.018638 | -0.015177 | 0.015137 | 0.12329 | 0.099708 | 0.071156 | 0.047579
3764.6719 | 122.8592 | -0.07782 | 122.7127 | 0.12185 | -0.022205 | -0.016578 | -0.011281 | 0.045421 | 0.071848 | -0.035248 | 0.052488 | 0.15248 | 0.009515 | -0.11094 | -0.066219 | -0.008827 | -0.042641 | -0.012328 | 0.15389 | 0.009838 | 0.015465 | 0.020762 | 0.077464 | 0.10389 | -0.003205 | 0.084531 | 0.18452 | 0.041558 | -0.078901 | -0.034176 | 0.023216 | -0.010598 | 0.019715 | 0.11871 | 0.095129 | 0.075734 | 0.052156
3766.375 | 122.8775 | -0.07782 | 122.7173 | 0.12185 | -0.031363 | -0.016578 | -0.006703 | 0.040843 | 0.067269 | -0.035248 | 0.057066 | 0.15706 | 0.004937 | -0.11094 | -0.070797 | -0.004248 | -0.042641 | -0.00775 | 0.15389 | 0.00068 | 0.015465 | 0.02534 | 0.072886 | 0.099312 | -0.003205 | 0.089109 | 0.1891 | 0.03698 | -0.078901 | -0.038754 | 0.027795 | -0.010598 | 0.024293 | 0.12786 | 0.099707 | 0.075734 | 0.047578
3768.1406 | 122.7814 | -0.091553 | 122.7448 | 0.12643 | -0.035942 | -0.021157 | -0.002124 | 0.054577 | 0.071848 | -0.03067 | 0.052488 | 0.1479 | 0.004937 | -0.10637 | -0.070797 | -0.004248 | -0.04722 | -0.012328 | 0.15847 | -0.003899 | 0.010886 | 0.029919 | 0.08662 | 0.10389 | 0.001373 | 0.084531 | 0.17994 | 0.03698 | -0.074322 | -0.038754 | 0.027795 | -0.015177 | 0.019715 | 0.12329 | 0.099708 | 0.075734 | 0.052157
3769.8438 | 122.8821 | -0.082397 | 122.7219 | 0.12185 | -0.031363 | -0.016578 | -0.002124 | 0.054577 | 0.081005 | -0.03067 | 0.057066 | 0.16164 | 0.004937 | -0.10637 | -0.066219 | -0.013405 | -0.04722 | -0.012328 | 0.15389 | 0.00068 | 0.015465 | 0.029919 | 0.08662 | 0.11305 | 0.001373 | 0.089109 | 0.19368 | 0.03698 | -0.074322 | -0.034176 | 0.018638 | -0.015177 | 0.019715 | 0.12329 | 0.10429 | 0.071156 | 0.052157
3771.6094 | 122.8455 | -0.082397 | 122.7264 | 0.12643 | -0.026784 | -0.016578 | -0.002124 | 0.049999 | 0.071848 | -0.044405 | 0.057066 | 0.1479 | -0.004219 | -0.10637 | -0.070797 | 0.00033 | -0.04722 | -0.012328 | 0.15847 | 0.005259 | 0.015465 | 0.029919 | 0.082042 | 0.10389 | -0.012362 | 0.089109 | 0.17994 | 0.027824 | -0.074322 | -0.038754 | 0.032373 | -0.015177 | 0.019715 | 0.12786 | 0.10429 | 0.066578 | 0.043001
3773.375 | 122.7676 | -0.10986 | 122.7448 | 0.12185 | -0.031363 | -0.012 | 0.007033 | 0.045421 | 0.071848 | -0.03067 | 0.061645 | 0.14332 | 0.004937 | -0.10179 | -0.061641 | -0.008827 | -0.042641 | -0.016906 | 0.15389 | 0.00068 | 0.020043 | 0.039076 | 0.077464 | 0.10389 | 0.001373 | 0.093688 | 0.17536 | 0.03698 | -0.069743 | -0.029598 | 0.023216 | -0.010598 | 0.015137 | 0.12329 | 0.10429 | 0.066578 | 0.047578
3775.1406 | 122.8455 | -0.09613 | 122.7036 | 0.12643 | -0.031363 | -0.021157 | -0.006703 | 0.054577 | 0.067269 | -0.035248 | 0.061645 | 0.16164 | -0.004219 | -0.097207 | -0.061641 | -0.008827 | -0.042641 | -0.021484 | 0.15847 | 0.00068 | 0.010886 | 0.02534 | 0.08662 | 0.099312 | -0.003205 | 0.093688 | 0.19368 | 0.027824 | -0.065164 | -0.029598 | 0.023216 | -0.010598 | 0.010559 | 0.12329 | 0.10429 | 0.057422 | 0.038422
3776.8438 | 122.85 | -0.064087 | 122.7173 | 0.12643 | -0.040521 | -0.021157 | -0.002124 | 0.049999 | 0.076426 | -0.035248 | 0.052488 | 0.15248 | 0.004937 | -0.10637 | -0.070797 | -0.017983 | -0.051798 | -0.00775 | 0.15847 | -0.008478 | 0.010886 | 0.029919 | 0.082042 | 0.10847 | -0.003205 | 0.084531 | 0.18452 | 0.03698 | -0.074322 | -0.038754 | 0.01406 | -0.019755 | 0.024293 | 0.12329 | 0.10429 | 0.075734 | 0.056735
3778.625 | 122.85 | -0.086975 | 122.7127 | 0.12643 | -0.031363 | -0.021157 | -0.006703 | 0.049999 | 0.067269 | -0.03067 | 0.061645 | 0.1479 | 0.004937 | -0.11094 | -0.061641 | -0.008827 | -0.04722 | -0.00775 | 0.15847 | 0.00068 | 0.010886 | 0.02534 | 0.082042 | 0.099312 | 0.001373 | 0.093688 | 0.17994 | 0.03698 | -0.078901 | -0.029598 | 0.023216 | -0.015177 | 0.024293 | 0.12329 | 0.10886 | 0.066578 | 0.052157
3780.3125 | 122.8043 | -0.10071 | 122.7402 | 0.12643 | -0.026784 | -0.021157 | -0.006703 | 0.049999 | 0.076426 | -0.026092 | 0.052488 | 0.15706 | 0.000359 | -0.10637 | -0.075375 | -0.017983 | -0.051798 | -0.016906 | 0.15847 | 0.005259 | 0.010886 | 0.02534 | 0.082042 | 0.10847 | 0.005951 | 0.084531 | 0.1891 | 0.032402 | -0.074322 | -0.043332 | 0.01406 | -0.019755 | 0.015137 | 0.12786 | 0.10429 | 0.075734 | 0.052157
3782.0781 | 122.8638 | -0.091553 | 122.6944 | 0.12185 | -0.035942 | -0.016578 | -0.006703 | 0.045421 | 0.067269 | -0.021514 | 0.057066 | 0.1479 | 0.004937 | -0.10179 | -0.066219 | -0.017983 | -0.051798 | -0.00775 | 0.15389 | -0.003899 | 0.015465 | 0.02534 | 0.077464 | 0.099312 | 0.010529 | 0.089109 | 0.17994 | 0.03698 | -0.069743 | -0.034176 | 0.01406 | -0.019755 | 0.024293 | 0.12329 | 0.10886 | 0.071156 | 0.056735
3783.8438 | 122.7631 | -0.1236 | 122.7585 | 0.13101 | -0.035942 | -0.021157 | -0.006703 | 0.049999 | 0.076426 | -0.035248 | 0.057066 | 0.14332 | 0.004937 | -0.11094 | -0.070797 | -0.004248 | -0.051798 | -0.016906 | 0.16305 | -0.003899 | 0.010886 | 0.02534 | 0.082042 | 0.10847 | -0.003205 | 0.089109 | 0.17536 | 0.03698 | -0.078901 | -0.038754 | 0.027795 | -0.019755 | 0.015137 | 0.12786 | 0.10886 | 0.075734 | 0.056735
3785.5469 | 122.8134 | -0.086975 | 122.7402 | 0.13101 | -0.026784 | -0.012 | -0.002124 | 0.045421 | 0.076426 | -0.035248 | 0.052488 | 0.15248 | 0.009515 | -0.11094 | -0.066219 | -0.004248 | -0.04722 | -0.021484 | 0.16305 | 0.005259 | 0.020043 | 0.029919 | 0.077464 | 0.10847 | -0.003205 | 0.084531 | 0.18452 | 0.041558 | -0.078901 | -0.034176 | 0.027795 | -0.015177 | 0.010559 | 0.11871 | 0.099708 | 0.075734 | 0.056735
3787.2969 | 122.7676 | -0.10529 | 122.7493 | 0.12643 | -0.022205 | -0.016578 | -0.002124 | 0.049999 | 0.071848 | -0.03067 | 0.047909 | 0.15248 | 0.000359 | -0.10637 | -0.066219 | -0.013405 | -0.051798 | -0.012328 | 0.15847 | 0.009838 | 0.015465 | 0.029919 | 0.082042 | 0.10389 | 0.001373 | 0.079952 | 0.18452 | 0.032402 | -0.074322 | -0.034176 | 0.018638 | -0.019755 | 0.019715 | 0.11413 | 0.099707 | 0.066578 | 0.052157
3789.0625 | 122.7722 | -0.10986 | 122.7722 | 0.12185 | -0.031363 | -0.021157 | 0.002454 | 0.054577 | 0.067269 | -0.03067 | 0.047909 | 0.15248 | 0.000359 | -0.10637 | -0.066219 | -0.008827 | -0.04722 | -0.016906 | 0.15389 | 0.00068 | 0.010886 | 0.034497 | 0.08662 | 0.099312 | 0.001373 | 0.079952 | 0.18452 | 0.032402 | -0.074322 | -0.034176 | 0.023216 | -0.015177 | 0.015137 | 0.11413 | 0.095129 | 0.066578 | 0.047579
3790.75 | 122.8683 | -0.073242 | 122.7219 | 0.12185 | -0.035942 | -0.016578 | -0.006703 | 0.045421 | 0.071848 | -0.035248 | 0.061645 | 0.15248 | 0.000359 | -0.11094 | -0.13031 | -0.091232 | -0.13879 | -0.10847 | 0.15389 | -0.003899 | 0.015465 | 0.02534 | 0.077464 | 0.10389 | -0.003205 | 0.093688 | 0.18452 | 0.032402 | -0.078901 | -0.09827 | -0.059189 | -0.10674 | -0.076427 | 0.19196 | 0.20043 | 0.13067 | 0.13915
3792.5156 | 122.8912 | -0.07782 | 122.7356 | 0.12643 | -0.031363 | -0.025735 | -0.002124 | 0.045421 | 0.067269 | -0.026092 | 0.057066 | 0.1479 | 0.000359 | -0.11094 | -0.057062 | -0.004248 | -0.042641 | -0.012328 | 0.15847 | 0.00068 | 0.006308 | 0.029919 | 0.077464 | 0.099312 | 0.005951 | 0.089109 | 0.17994 | 0.032402 | -0.078901 | -0.025019 | 0.027795 | -0.010598 | 0.019715 | 0.11413 | 0.099707 | 0.057421 | 0.043
3794.2812 | 122.7951 | -0.10529 | 122.7264 | 0.12643 | -0.031363 | -0.016578 | -0.011281 | 0.045421 | 0.062691 | -0.03067 | 0.052488 | 0.1479 | 0.004937 | -0.11094 | -0.061641 | -0.008827 | -0.04722 | -0.00775 | 0.15847 | 0.00068 | 0.015465 | 0.020762 | 0.077464 | 0.094734 | 0.001373 | 0.084531 | 0.17994 | 0.03698 | -0.078901 | -0.029598 | 0.023216 | -0.015177 | 0.024293 | 0.11413 | 0.099708 | 0.066578 | 0.052157
3796.0469 | 122.7676 | -0.10529 | 122.731 | 0.12643 | -0.022205 | -0.016578 | -0.002124 | 0.045421 | 0.067269 | -0.03067 | 0.061645 | 0.15248 | 0.000359 | -0.10637 | -0.066219 | -0.004248 | -0.051798 | -0.012328 | 0.15847 | 0.009838 | 0.015465 | 0.029919 | 0.077464 | 0.099312 | 0.001373 | 0.093688 | 0.18452 | 0.032402 | -0.074322 | -0.034176 | 0.027795 | -0.019755 | 0.019715 | 0.12786 | 0.11344 | 0.066578 | 0.052157
3797.8125 | 122.8592 | -0.07782 | 122.7127 | 0.12643 | -0.031363 | -0.021157 | -0.002124 | 0.045421 | 0.067269 | -0.03067 | 0.057066 | 0.1479 | 0.000359 | -0.11094 | -0.070797 | -0.008827 | -0.042641 | -0.012328 | 0.15847 | 0.00068 | 0.010886 | 0.029919 | 0.077464 | 0.099312 | 0.001373 | 0.089109 | 0.17994 | 0.032402 | -0.078901 | -0.038754 | 0.023216 | -0.010598 | 0.019715 | 0.12786 | 0.099707 | 0.071156 | 0.043
3799.5312 | 122.8867 | -0.07782 | 122.699 | 0.13101 | -0.031363 | -0.025735 | -0.002124 | 0.040843 | 0.071848 | -0.035248 | 0.057066 | 0.15706 | -0.004219 | -0.10179 | -0.061641 | -0.008827 | -0.042641 | -0.012328 | 0.16305 | 0.00068 | 0.006308 | 0.029919 | 0.072886 | 0.10389 | -0.003205 | 0.089109 | 0.1891 | 0.027824 | -0.069743 | -0.029598 | 0.023216 | -0.010598 | 0.019715 | 0.11871 | 0.099707 | 0.057422 | 0.038422
3801.2344 | 122.8317 | -0.091553 | 122.7219 | 0.12643 | -0.031363 | -0.016578 | -0.002124 | 0.045421 | 0.067269 | -0.035248 | 0.057066 | 0.1479 | -0.004219 | -0.10637 | -0.061641 | 0.00033 | -0.04722 | -0.016906 | 0.15847 | 0.00068 | 0.015465 | 0.029919 | 0.077464 | 0.099312 | -0.003205 | 0.089109 | 0.17994 | 0.027824 | -0.074322 | -0.029598 | 0.032373 | -0.015177 | 0.015137 | 0.11871 | 0.10429 | 0.057422 | 0.043001
3802.9844 | 122.8912 | -0.054932 | 122.7356 | 0.12643 | -0.035942 | -0.016578 | -0.011281 | 0.040843 | 0.067269 | -0.035248 | 0.047909 | 0.1479 | 0.004937 | -0.10637 | -0.070797 | -0.008827 | -0.042641 | -0.012328 | 0.15847 | -0.003899 | 0.015465 | 0.020762 | 0.072886 | 0.099312 | -0.003205 | 0.079952 | 0.17994 | 0.03698 | -0.074322 | -0.038754 | 0.023216 | -0.010598 | 0.019715 | 0.11871 | 0.09055 | 0.075734 | 0.047578
3804.6875 | 122.8088 | -0.09613 | 122.7585 | 0.12643 | -0.035942 | -0.021157 | -0.011281 | 0.045421 | 0.071848 | -0.035248 | 0.057066 | 0.15706 | 0.000359 | -0.10637 | -0.066219 | -0.008827 | -0.051798 | -0.016906 | 0.15847 | -0.003899 | 0.010886 | 0.020762 | 0.077464 | 0.10389 | -0.003205 | 0.089109 | 0.1891 | 0.032402 | -0.074322 | -0.034176 | 0.023216 | -0.019755 | 0.015137 | 0.12329 | 0.10886 | 0.066578 | 0.052157
3806.3906 | 122.7722 | -0.10071 | 122.7676 | 0.13101 | -0.022205 | -0.016578 | 0.002454 | 0.045421 | 0.071848 | -0.026092 | 0.061645 | 0.14332 | -0.004219 | -0.10637 | -0.066219 | -0.013405 | -0.051798 | -0.012328 | 0.16305 | 0.009838 | 0.015465 | 0.034497 | 0.077464 | 0.10389 | 0.005951 | 0.093688 | 0.17536 | 0.027824 | -0.074322 | -0.034176 | 0.018638 | -0.019755 | 0.019715 | 0.12786 | 0.11344 | 0.062 | 0.047579
3808.1562 | 122.8546 | -0.086975 | 122.7356 | 0.12185 | -0.026784 | -0.016578 | -0.002124 | 0.045421 | 0.071848 | -0.026092 | 0.052488 | 0.15706 | 0.000359 | -0.11094 | -0.066219 | 0.00033 | -0.042641 | -0.016906 | 0.15389 | 0.005259 | 0.015465 | 0.029919 | 0.077464 | 0.10389 | 0.005951 | 0.084531 | 0.1891 | 0.032402 | -0.078901 | -0.034176 | 0.032373 | -0.010598 | 0.015137 | 0.11871 | 0.095129 | 0.066578 | 0.043
3809.9219 | 122.7814 | -0.091553 | 122.7493 | 0.12643 | -0.026784 | -0.021157 | -0.002124 | 0.054577 | 0.076426 | -0.03067 | 0.057066 | 0.15248 | 0.004937 | -0.10179 | -0.070797 | -0.008827 | -0.038063 | -0.016906 | 0.15847 | 0.005259 | 0.010886 | 0.029919 | 0.08662 | 0.10847 | 0.001373 | 0.089109 | 0.18452 | 0.03698 | -0.069743 | -0.038754 | 0.023216 | -0.00602 | 0.015137 | 0.12786 | 0.095129 | 0.075734 | 0.043
3811.7031 | 122.8271 | -0.086975 | 122.7631 | 0.12643 | -0.031363 | -0.021157 | -0.002124 | 0.045421 | 0.071848 | -0.03067 | 0.061645 | 0.15706 | 0.000359 | -0.11094 | -0.070797 | -0.004248 | -0.04722 | -0.016906 | 0.15847 | 0.00068 | 0.010886 | 0.029919 | 0.077464 | 0.10389 | 0.001373 | 0.093688 | 0.1891 | 0.032402 | -0.078901 | -0.038754 | 0.027795 | -0.015177 | 0.015137 | 0.13244 | 0.10886 | 0.071156 | 0.047579
3813.4062 | 122.85 | -0.091553 | 122.7631 | 0.12643 | -0.040521 | -0.016578 | -0.011281 | 0.036265 | 0.062691 | -0.035248 | 0.057066 | 0.15248 | 0.000359 | -0.11094 | -0.061641 | -0.008827 | -0.038063 | -0.012328 | 0.15847 | -0.008478 | 0.015465 | 0.020762 | 0.068308 | 0.094734 | -0.003205 | 0.089109 | 0.18452 | 0.032402 | -0.078901 | -0.029598 | 0.023216 | -0.00602 | 0.019715 | 0.11871 | 0.095129 | 0.062 | 0.038422
3815.1719 | 122.8226 | -0.10529 | 122.7676 | 0.13101 | -0.035942 | -0.021157 | -0.002124 | 0.045421 | 0.071848 | -0.035248 | 0.052488 | 0.15248 | 0.004937 | -0.11094 | -0.070797 | -0.008827 | -0.038063 | -0.012328 | 0.16305 | -0.003899 | 0.010886 | 0.029919 | 0.077464 | 0.10389 | -0.003205 | 0.084531 | 0.18452 | 0.03698 | -0.078901 | -0.038754 | 0.023216 | -0.00602 | 0.019715 | 0.12329 | 0.090551 | 0.075734 | 0.043
3816.9375 | 122.8638 | -0.091553 | 122.7448 | 0.12185 | -0.031363 | -0.016578 | -0.006703 | 0.045421 | 0.067269 | -0.03067 | 0.061645 | 0.15706 | 0.000359 | -0.11094 | -0.066219 | -0.008827 | -0.042641 | -0.016906 | 0.15389 | 0.00068 | 0.015465 | 0.02534 | 0.077464 | 0.099312 | 0.001373 | 0.093688 | 0.1891 | 0.032402 | -0.078901 | -0.034176 | 0.023216 | -0.010598 | 0.015137 | 0.12786 | 0.10429 | 0.066578 | 0.043
3818.7188 | 122.7676 | -0.1236 | 122.7768 | 0.12643 | -0.026784 | -0.021157 | -0.002124 | 0.049999 | 0.067269 | -0.026092 | 0.057066 | 0.16164 | -0.004219 | -0.097207 | -0.066219 | -0.008827 | -0.042641 | -0.016906 | 0.15847 | 0.005259 | 0.010886 | 0.029919 | 0.082042 | 0.099312 | 0.005951 | 0.089109 | 0.19368 | 0.027824 | -0.065164 | -0.034176 | 0.023216 | -0.010598 | 0.015137 | 0.12329 | 0.099707 | 0.062 | 0.038422
3820.4375 | 122.8683 | -0.10071 | 122.7585 | 0.12643 | -0.026784 | -0.021157 | -0.006703 | 0.040843 | 0.071848 | -0.03067 | 0.057066 | 0.1479 | 0.000359 | -0.10637 | -0.066219 | -0.004248 | -0.04722 | -0.012328 | 0.15847 | 0.005259 | 0.010886 | 0.02534 | 0.072886 | 0.10389 | 0.001373 | 0.089109 | 0.17994 | 0.032402 | -0.074322 | -0.034176 | 0.027795 | -0.015177 | 0.019715 | 0.12329 | 0.10429 | 0.066578 | 0.047579
3822.2031 | 122.8592 | -0.10529 | 122.7356 | 0.13101 | -0.026784 | -0.021157 | -0.002124 | 0.045421 | 0.071848 | -0.039826 | 0.061645 | 0.14332 | 0.000359 | -0.10637 | -0.061641 | -0.017983 | -0.04722 | -0.00775 | 0.16305 | 0.005259 | 0.010886 | 0.029919 | 0.077464 | 0.10389 | -0.007783 | 0.093688 | 0.17536 | 0.032402 | -0.074322 | -0.029598 | 0.01406 | -0.015177 | 0.024293 | 0.12329 | 0.10886 | 0.062 | 0.047579
3823.9688 | 122.8043 | -0.11902 | 122.7768 | 0.12643 | -0.031363 | -0.021157 | 0.002454 | 0.045421 | 0.071848 | -0.026092 | 0.057066 | 0.15706 | 0.000359 | -0.11094 | -0.066219 | -0.008827 | -0.042641 | -0.016906 | 0.15847 | 0.00068 | 0.010886 | 0.034497 | 0.077464 | 0.10389 | 0.005951 | 0.089109 | 0.1891 | 0.032402 | -0.078901 | -0.034176 | 0.023216 | -0.010598 | 0.015137 | 0.12329 | 0.099707 | 0.066578 | 0.043
3825.6719 | 122.905 | -0.059509 | 122.7448 | 0.12185 | -0.031363 | -0.012 | -0.006703 | 0.049999 | 0.067269 | -0.035248 | 0.061645 | 0.15706 | 0.009515 | -0.097207 | -0.066219 | -0.004248 | -0.042641 | -0.016906 | 0.15389 | 0.00068 | 0.020043 | 0.02534 | 0.082042 | 0.099312 | -0.003205 | 0.093688 | 0.1891 | 0.041558 | -0.065164 | -0.034176 | 0.027795 | -0.010598 | 0.015137 | 0.12786 | 0.10429 | 0.075734 | 0.052156
3827.375 | 122.9187 | -0.068665 | 122.7081 | 0.12185 | -0.031363 | -0.016578 | -0.002124 | 0.049999 | 0.071848 | -0.03067 | 0.057066 | 0.1479 | -0.004219 | -0.11094 | -0.061641 | -0.008827 | -0.04722 | -0.016906 | 0.15389 | 0.00068 | 0.015465 | 0.029919 | 0.082042 | 0.10389 | 0.001373 | 0.089109 | 0.17994 | 0.027824 | -0.078901 | -0.029598 | 0.023216 | -0.015177 | 0.015137 | 0.11871 | 0.10429 | 0.057422 | 0.043001
3829.1406 | 122.8867 | -0.082397 | 122.7585 | 0.12643 | -0.026784 | -0.021157 | -0.006703 | 0.040843 | 0.071848 | -0.035248 | 0.057066 | 0.15248 | -0.004219 | -0.11094 | -0.066219 | -0.004248 | -0.042641 | -0.012328 | 0.15847 | 0.005259 | 0.010886 | 0.02534 | 0.072886 | 0.10389 | -0.003205 | 0.089109 | 0.18452 | 0.027824 | -0.078901 | -0.034176 | 0.027795 | -0.010598 | 0.019715 | 0.12329 | 0.099707 | 0.062 | 0.038422
3830.9062 | 122.7722 | -0.11444 | 122.7951 | 0.12643 | -0.026784 | -0.016578 | -0.011281 | 0.045421 | 0.071848 | -0.03067 | 0.061645 | 0.15706 | 0.004937 | -0.10179 | -0.066219 | -0.004248 | -0.042641 | -0.012328 | 0.15847 | 0.005259 | 0.015465 | 0.020762 | 0.077464 | 0.10389 | 0.001373 | 0.093688 | 0.1891 | 0.03698 | -0.069743 | -0.034176 | 0.027795 | -0.010598 | 0.019715 | 0.12786 | 0.10429 | 0.071156 | 0.047578
3832.625 | 122.8271 | -0.086975 | 122.7768 | 0.13101 | -0.035942 | -0.021157 | -0.006703 | 0.049999 | 0.076426 | -0.03067 | 0.061645 | 0.15248 | -0.004219 | -0.10637 | -0.057062 | -0.013405 | -0.042641 | -0.012328 | 0.16305 | -0.003899 | 0.010886 | 0.02534 | 0.082042 | 0.10847 | 0.001373 | 0.093688 | 0.18452 | 0.027824 | -0.074322 | -0.025019 | 0.018638 | -0.010598 | 0.019715 | 0.11871 | 0.10429 | 0.052843 | 0.038422
3834.4062 | 122.9233 | -0.07782 | 122.7173 | 0.12643 | -0.026784 | -0.016578 | -0.011281 | 0.049999 | 0.067269 | -0.039826 | 0.057066 | 0.1479 | -0.004219 | -0.11094 | -0.066219 | -0.013405 | -0.04722 | -0.00775 | 0.15847 | 0.005259 | 0.015465 | 0.020762 | 0.082042 | 0.099312 | -0.007783 | 0.089109 | 0.17994 | 0.027824 | -0.078901 | -0.034176 | 0.018638 | -0.015177 | 0.024293 | 0.12329 | 0.10429 | 0.062 | 0.043001
3836.1719 | 122.7859 | -0.11902 | 122.7997 | 0.13101 | -0.026784 | -0.021157 | -0.002124 | 0.045421 | 0.076426 | -0.035248 | 0.052488 | 0.15248 | 0.004937 | -0.11094 | -0.066219 | -0.008827 | -0.042641 | -0.00775 | 0.16305 | 0.005259 | 0.010886 | 0.029919 | 0.077464 | 0.10847 | -0.003205 | 0.084531 | 0.18452 | 0.03698 | -0.078901 | -0.034176 | 0.023216 | -0.010598 | 0.024293 | 0.11871 | 0.095129 | 0.071156 | 0.047578
3837.9375 | 122.7722 | -0.091553 | 122.7905 | 0.12643 | -0.022205 | -0.021157 | -0.006703 | 0.040843 | 0.071848 | -0.039826 | 0.057066 | 0.1479 | 0.000359 | -0.10637 | -0.057062 | 0.00033 | -0.038063 | -0.003172 | 0.15847 | 0.009838 | 0.010886 | 0.02534 | 0.072886 | 0.10389 | -0.007783 | 0.089109 | 0.17994 | 0.032402 | -0.074322 | -0.025019 | 0.032373 | -0.00602 | 0.028871 | 0.11413 | 0.095129 | 0.057421 | 0.038422
3839.6562 | 122.9141 | -0.054932 | 122.7631 | 0.13101 | -0.031363 | -0.012 | -0.002124 | 0.040843 | 0.071848 | -0.03067 | 0.061645 | 0.16164 | -0.004219 | -0.097207 | -0.066219 | -0.008827 | -0.04722 | -0.00775 | 0.16305 | 0.00068 | 0.020043 | 0.029919 | 0.072886 | 0.10389 | 0.001373 | 0.093688 | 0.19368 | 0.027824 | -0.065164 | -0.034176 | 0.023216 | -0.015177 | 0.024293 | 0.12786 | 0.10886 | 0.062 | 0.043001
3841.3594 | 122.8592 | -0.086975 | 122.7356 | 0.13101 | -0.031363 | -0.021157 | -0.002124 | 0.040843 | 0.071848 | -0.03067 | 0.052488 | 0.15706 | 0.004937 | -0.10637 | -0.061641 | -0.008827 | -0.042641 | -0.00775 | 0.16305 | 0.00068 | 0.010886 | 0.029919 | 0.072886 | 0.10389 | 0.001373 | 0.084531 | 0.1891 | 0.03698 | -0.074322 | -0.029598 | 0.023216 | -0.010598 | 0.024293 | 0.11413 | 0.095129 | 0.066578 | 0.047578
3843.1094 | 122.8867 | -0.082397 | 122.7264 | 0.12643 | -0.031363 | -0.016578 | -0.011281 | 0.040843 | 0.071848 | -0.03067 | 0.057066 | 0.15248 | 0.000359 | -0.10637 | -0.066219 | -0.008827 | -0.042641 | -0.00775 | 0.15847 | 0.00068 | 0.015465 | 0.020762 | 0.072886 | 0.10389 | 0.001373 | 0.089109 | 0.18452 | 0.032402 | -0.074322 | -0.034176 | 0.023216 | -0.010598 | 0.024293 | 0.12329 | 0.099707 | 0.066578 | 0.043
3844.875 | 122.7814 | -0.09613 | 122.7631 | 0.12643 | -0.026784 | -0.016578 | 0.002454 | 0.045421 | 0.067269 | -0.021514 | 0.057066 | 0.15706 | 0.000359 | -0.11094 | -0.061641 | -0.004248 | -0.04722 | -0.00775 | 0.15847 | 0.005259 | 0.015465 | 0.034497 | 0.077464 | 0.099312 | 0.010529 | 0.089109 | 0.1891 | 0.032402 | -0.078901 | -0.029598 | 0.027795 | -0.015177 | 0.024293 | 0.11871 | 0.10429 | 0.062 | 0.047579
3846.6406 | 122.8912 | -0.07782 | 122.7402 | 0.12185 | -0.026784 | -0.012 | -0.002124 | 0.049999 | 0.071848 | -0.035248 | 0.057066 | 0.15706 | 0.000359 | -0.10637 | -0.061641 | -0.008827 | -0.033484 | -0.012328 | 0.15389 | 0.005259 | 0.020043 | 0.029919 | 0.082042 | 0.10389 | -0.003205 | 0.089109 | 0.1891 | 0.032402 | -0.074322 | -0.029598 | 0.023216 | -0.001441 | 0.019715 | 0.11871 | 0.09055 | 0.062 | 0.033843
3848.3906 | 122.9095 | -0.068665 | 122.7493 | 0.12643 | -0.022205 | -0.021157 | -0.011281 | 0.036265 | 0.067269 | -0.035248 | 0.052488 | 0.15248 | 0.004937 | -0.11552 | -0.066219 | -0.008827 | -0.038063 | -0.00775 | 0.15847 | 0.009838 | 0.010886 | 0.020762 | 0.068308 | 0.099312 | -0.003205 | 0.084531 | 0.18452 | 0.03698 | -0.08348 | -0.034176 | 0.023216 | -0.00602 | 0.024293 | 0.11871 | 0.090551 | 0.071156 | 0.043
3850.0938 | 122.8455 | -0.013733 | 122.8867 | 0.12185 | -0.031363 | -0.012 | -0.002124 | 0.049999 | 0.067269 | -0.03067 | 0.052488 | 0.15706 | 0.000359 | -0.10179 | -0.052484 | -0.013405 | -0.033484 | -0.00775 | 0.15389 | 0.00068 | 0.020043 | 0.029919 | 0.082042 | 0.099312 | 0.001373 | 0.084531 | 0.1891 | 0.032402 | -0.069743 | -0.020441 | 0.018638 | -0.001441 | 0.024293 | 0.10497 | 0.085972 | 0.052843 | 0.033843
3851.8594 | 122.7676 | -0.10986 | 122.7951 | 0.11727 | -0.035942 | -0.025735 | -0.006703 | 0.036265 | 0.062691 | -0.039826 | 0.043331 | 0.13874 | -0.013376 | -0.10179 | -0.043328 | -0.004248 | -0.038063 | 0.005985 | 0.14932 | -0.003899 | 0.006308 | 0.02534 | 0.068308 | 0.094734 | -0.007783 | 0.075374 | 0.17079 | 0.018667 | -0.069743 | -0.011285 | 0.027795 | -0.00602 | 0.038028 | 0.086659 | 0.081394 | 0.029952 | 0.024687
3853.5625 | 122.9279 | -0.086975 | 122.7539 | 0.13101 | -0.035942 | -0.012 | -0.002124 | 0.040843 | 0.071848 | -0.03067 | 0.057066 | 0.1479 | -0.004219 | -0.10179 | -0.061641 | -0.008827 | -0.04722 | -0.016906 | 0.16305 | -0.003899 | 0.020043 | 0.029919 | 0.072886 | 0.10389 | 0.001373 | 0.089109 | 0.17994 | 0.027824 | -0.069743 | -0.029598 | 0.023216 | -0.015177 | 0.015137 | 0.11871 | 0.10429 | 0.057422 | 0.043001
3855.3438 | 122.9141 | -0.073242 | 122.7539 | 0.12643 | -0.022205 | -0.021157 | -0.006703 | 0.045421 | 0.071848 | -0.039826 | 0.061645 | 0.1479 | 0.004937 | -0.11094 | -0.057062 | -0.008827 | -0.04722 | -0.026063 | 0.15847 | 0.009838 | 0.010886 | 0.02534 | 0.077464 | 0.10389 | -0.007783 | 0.093688 | 0.17994 | 0.03698 | -0.078901 | -0.025019 | 0.023216 | -0.015177 | 0.00598 | 0.11871 | 0.10886 | 0.061999 | 0.052157
3857.1094 | 122.8729 | -0.064087 | 122.7539 | 0.12643 | -0.031363 | -0.016578 | -0.011281 | 0.040843 | 0.067269 | -0.035248 | 0.052488 | 0.13874 | -0.004219 | -0.11552 | -0.052484 | -0.013405 | -0.04722 | -0.016906 | 0.15847 | 0.00068 | 0.015465 | 0.020762 | 0.072886 | 0.099312 | -0.003205 | 0.084531 | 0.17079 | 0.027824 | -0.08348 | -0.020441 | 0.018638 | -0.015177 | 0.015137 | 0.10497 | 0.099708 | 0.048265 | 0.043001
3858.8125 | 122.8088 | -0.10529 | 122.7859 | 0.12643 | -0.022205 | -0.021157 | -0.006703 | 0.045421 | 0.071848 | -0.03067 | 0.057066 | 0.15248 | -0.004219 | -0.10637 | -0.052484 | -0.004248 | -0.042641 | -0.00775 | 0.15847 | 0.009838 | 0.010886 | 0.02534 | 0.077464 | 0.10389 | 0.001373 | 0.089109 | 0.18452 | 0.027824 | -0.074322 | -0.020441 | 0.027795 | -0.010598 | 0.024293 | 0.10955 | 0.099707 | 0.048265 | 0.038422
3860.5781 | 122.9233 | -0.086975 | 122.7493 | 0.11727 | -0.022205 | -0.021157 | -0.006703 | 0.040843 | 0.076426 | -0.026092 | 0.057066 | 0.15248 | 0.004937 | -0.10637 | -0.052484 | -0.013405 | -0.04722 | -0.016906 | 0.14932 | 0.009838 | 0.010886 | 0.02534 | 0.072886 | 0.10847 | 0.005951 | 0.089109 | 0.18452 | 0.03698 | -0.074322 | -0.020441 | 0.018638 | -0.015177 | 0.015137 | 0.10955 | 0.10429 | 0.057421 | 0.052157
3862.3438 | 122.7997 | -0.10986 | 122.7814 | 0.12643 | -0.031363 | -0.016578 | -0.002124 | 0.040843 | 0.081005 | -0.03067 | 0.057066 | 0.14332 | 0.004937 | -0.10637 | -0.057062 | 0.00033 | -0.051798 | -0.012328 | 0.15847 | 0.00068 | 0.015465 | 0.029919 | 0.072886 | 0.11305 | 0.001373 | 0.089109 | 0.17536 | 0.03698 | -0.074322 | -0.025019 | 0.032373 | -0.019755 | 0.019715 | 0.11413 | 0.10886 | 0.061999 | 0.056735
3864.1094 | 122.8638 | -0.07782 | 122.7539 | 0.12643 | -0.026784 | -0.030314 | 0.002454 | 0.045421 | 0.071848 | -0.026092 | 0.057066 | 0.15706 | 0.000359 | -0.10637 | -0.057062 | -0.004248 | -0.04722 | -0.016906 | 0.15847 | 0.005259 | 0.001729 | 0.034497 | 0.077464 | 0.10389 | 0.005951 | 0.089109 | 0.1891 | 0.032402 | -0.074322 | -0.025019 | 0.027795 | -0.015177 | 0.015137 | 0.11413 | 0.10429 | 0.057421 | 0.047579
3865.875 | 122.8317 | -0.14191 | 122.7997 | 0.12643 | -0.031363 | -0.021157 | -0.006703 | 0.045421 | 0.071848 | -0.03067 | 0.052488 | 0.15248 | 0.004937 | -0.10179 | -0.047906 | -0.008827 | -0.042641 | -0.021484 | 0.15847 | 0.00068 | 0.010886 | 0.02534 | 0.077464 | 0.10389 | 0.001373 | 0.084531 | 0.18452 | 0.03698 | -0.069743 | -0.015863 | 0.023216 | -0.010598 | 0.010559 | 0.10039 | 0.095129 | 0.052843 | 0.047578
3867.6406 | 122.8226 | -0.11902 | 122.7722 | 0.12643 | -0.031363 | -0.021157 | -0.002124 | 0.049999 | 0.071848 | -0.026092 | 0.061645 | 0.1479 | 0.004937 | -0.10637 | -0.052484 | -0.008827 | -0.042641 | -0.012328 | 0.15847 | 0.00068 | 0.010886 | 0.029919 | 0.082042 | 0.10389 | 0.005951 | 0.093688 | 0.17994 | 0.03698 | -0.074322 | -0.020441 | 0.023216 | -0.010598 | 0.019715 | 0.11413 | 0.10429 | 0.057421 | 0.047578
3869.3281 | 122.9187 | -0.068665 | 122.731 | 0.13101 | -0.026784 | -0.016578 | -0.011281 | 0.045421 | 0.071848 | -0.03067 | 0.061645 | 0.15248 | 0.004937 | -0.11094 | -0.052484 | -0.004248 | -0.04722 | -0.016906 | 0.16305 | 0.005259 | 0.015465 | 0.020762 | 0.077464 | 0.10389 | 0.001373 | 0.093688 | 0.18452 | 0.03698 | -0.078901 | -0.020441 | 0.027795 | -0.015177 | 0.015137 | 0.11413 | 0.10886 | 0.057421 | 0.052157
3871.1094 | 122.8546 | -0.091553 | 122.7493 | 0.12643 | -0.026784 | -0.021157 | -0.002124 | 0.054577 | 0.067269 | -0.026092 | 0.057066 | 0.15706 | 0.000359 | -0.11094 | -0.052484 | -0.013405 | -0.042641 | -0.012328 | 0.15847 | 0.005259 | 0.010886 | 0.029919 | 0.08662 | 0.099312 | 0.005951 | 0.089109 | 0.1891 | 0.032402 | -0.078901 | -0.020441 | 0.018638 | -0.010598 | 0.019715 | 0.10955 | 0.099707 | 0.052843 | 0.043
3872.8125 | 122.9416 | -0.086975 | 122.7493 | 0.12643 | -0.026784 | -0.021157 | -0.006703 | 0.045421 | 0.067269 | -0.035248 | 0.052488 | 0.15706 | -0.004219 | -0.10637 | -0.047906 | -0.013405 | -0.04722 | -0.021484 | 0.15847 | 0.005259 | 0.010886 | 0.02534 | 0.077464 | 0.099312 | -0.003205 | 0.084531 | 0.1891 | 0.027824 | -0.074322 | -0.015863 | 0.018638 | -0.015177 | 0.010559 | 0.10039 | 0.099708 | 0.043687 | 0.043001
3874.5781 | 122.8821 | -0.09613 | 122.7814 | 0.13101 | -0.031363 | -0.021157 | -0.006703 | 0.040843 | 0.071848 | -0.039826 | 0.066223 | 0.15248 | 0.000359 | -0.10637 | -0.043328 | -0.008827 | -0.04722 | -0.021484 | 0.16305 | 0.00068 | 0.010886 | 0.02534 | 0.072886 | 0.10389 | -0.007783 | 0.098266 | 0.18452 | 0.032402 | -0.074322 | -0.011285 | 0.023216 | -0.015177 | 0.010559 | 0.10955 | 0.11344 | 0.043687 | 0.047579
3876.2812 | 122.818 | -0.091553 | 122.7997 | 0.13101 | -0.031363 | -0.025735 | 0.007033 | 0.049999 | 0.076426 | -0.035248 | 0.061645 | 0.15706 | 0.004937 | -0.10637 | -0.057062 | 0.00033 | -0.051798 | -0.012328 | 0.16305 | 0.00068 | 0.006308 | 0.039076 | 0.082042 | 0.10847 | -0.003205 | 0.093688 | 0.1891 | 0.03698 | -0.074322 | -0.025019 | 0.032373 | -0.019755 | 0.019715 | 0.11871 | 0.11344 | 0.061999 | 0.056735
3878.0469 | 122.9324 | -0.082397 | 122.7722 | 0.12643 | -0.035942 | -0.016578 | -0.002124 | 0.054577 | 0.071848 | -0.03067 | 0.061645 | 0.15248 | 0.004937 | -0.11094 | -0.052484 | -0.008827 | -0.04722 | -0.021484 | 0.15847 | -0.003899 | 0.015465 | 0.029919 | 0.08662 | 0.10389 | 0.001373 | 0.093688 | 0.18452 | 0.03698 | -0.078901 | -0.020441 | 0.023216 | -0.015177 | 0.010559 | 0.11413 | 0.10886 | 0.057421 | 0.052157
3879.7969 | 122.9553 | -0.07782 | 122.7448 | 0.12185 | -0.031363 | -0.025735 | -0.002124 | 0.040843 | 0.076426 | -0.03067 | 0.057066 | 0.15706 | 0.000359 | -0.10179 | -0.061641 | -0.004248 | -0.038063 | -0.021484 | 0.15389 | 0.00068 | 0.006308 | 0.029919 | 0.072886 | 0.10847 | 0.001373 | 0.089109 | 0.1891 | 0.032402 | -0.069743 | -0.029598 | 0.027795 | -0.00602 | 0.010559 | 0.11871 | 0.095129 | 0.062 | 0.038422
3881.5625 | 122.8271 | -0.10071 | 122.7951 | 0.13101 | -0.031363 | -0.021157 | 0.002454 | 0.049999 | 0.071848 | -0.035248 | 0.057066 | 0.15248 | 0.000359 | -0.11094 | -0.052484 | -0.013405 | -0.042641 | -0.012328 | 0.16305 | 0.00068 | 0.010886 | 0.034497 | 0.082042 | 0.10389 | -0.003205 | 0.089109 | 0.18452 | 0.032402 | -0.078901 | -0.020441 | 0.018638 | -0.010598 | 0.019715 | 0.10955 | 0.099707 | 0.052843 | 0.043
3883.3281 | 122.8729 | -0.091553 | 122.7768 | 0.12185 | -0.031363 | -0.021157 | -0.002124 | 0.036265 | 0.071848 | -0.03067 | 0.057066 | 0.1479 | 0.000359 | -0.11094 | -0.057062 | -0.004248 | -0.04722 | -0.012328 | 0.15389 | 0.00068 | 0.010886 | 0.029919 | 0.068308 | 0.10389 | 0.001373 | 0.089109 | 0.17994 | 0.032402 | -0.078901 | -0.025019 | 0.027795 | -0.015177 | 0.019715 | 0.11413 | 0.10429 | 0.057421 | 0.047579
3885.0938 | 122.8775 | -0.082397 | 122.7859 | 0.12643 | -0.031363 | -0.016578 | -0.002124 | 0.040843 | 0.062691 | -0.035248 | 0.061645 | 0.16164 | 0.000359 | -0.11094 | -0.057062 | -0.008827 | -0.042641 | -0.012328 | 0.15847 | 0.00068 | 0.015465 | 0.029919 | 0.072886 | 0.094734 | -0.003205 | 0.093688 | 0.19368 | 0.032402 | -0.078901 | -0.025019 | 0.023216 | -0.010598 | 0.019715 | 0.11871 | 0.10429 | 0.057421 | 0.043
3886.7812 | 122.818 | -0.1236 | 122.7768 | 0.12643 | -0.026784 | -0.021157 | 0.002454 | 0.049999 | 0.067269 | -0.035248 | 0.061645 | 0.15248 | 0.000359 | -0.11552 | -0.047906 | -0.004248 | -0.04722 | -0.016906 | 0.15847 | 0.005259 | 0.010886 | 0.034497 | 0.082042 | 0.099312 | -0.003205 | 0.093688 | 0.18452 | 0.032402 | -0.08348 | -0.015863 | 0.027795 | -0.015177 | 0.015137 | 0.10955 | 0.10886 | 0.048265 | 0.047579
3888.5312 | 122.8546 | -0.11444 | 122.8043 | 0.12643 | -0.026784 | -0.021157 | -0.002124 | 0.040843 | 0.071848 | -0.03067 | 0.066223 | 0.16164 | -0.004219 | -0.11094 | -0.052484 | -0.008827 | -0.04722 | -0.021484 | 0.15847 | 0.005259 | 0.010886 | 0.029919 | 0.072886 | 0.10389 | 0.001373 | 0.098266 | 0.19368 | 0.027824 | -0.078901 | -0.020441 | 0.023216 | -0.015177 | 0.010559 | 0.11871 | 0.11344 | 0.048265 | 0.043001
3890.2344 | 122.8134 | -0.10529 | 122.8134 | 0.13101 | -0.022205 | -0.016578 | 0.002454 | 0.045421 | 0.071848 | -0.03067 | 0.057066 | 0.15248 | 0.000359 | -0.11094 | -0.052484 | -0.004248 | -0.04722 | -0.012328 | 0.16305 | 0.009838 | 0.015465 | 0.034497 | 0.077464 | 0.10389 | 0.001373 | 0.089109 | 0.18452 | 0.032402 | -0.078901 | -0.020441 | 0.027795 | -0.015177 | 0.019715 | 0.10955 | 0.10429 | 0.052843 | 0.047579
3891.9844 | 122.8134 | -0.091553 | 122.8043 | 0.12185 | -0.035942 | -0.021157 | -0.006703 | 0.040843 | 0.067269 | -0.035248 | 0.061645 | 0.15706 | 0.004937 | -0.11094 | -0.061641 | -0.004248 | -0.051798 | -0.00775 | 0.15389 | -0.003899 | 0.010886 | 0.02534 | 0.072886 | 0.099312 | -0.003205 | 0.093688 | 0.1891 | 0.03698 | -0.078901 | -0.029598 | 0.027795 | -0.019755 | 0.024293 | 0.12329 | 0.11344 | 0.066578 | 0.056735
3893.75 | 122.9233 | -0.07782 | 122.7356 | 0.13101 | -0.026784 | -0.025735 | -0.002124 | 0.036265 | 0.067269 | -0.03067 | 0.057066 | 0.15706 | 0.000359 | -0.11094 | -0.052484 | -0.013405 | -0.042641 | -0.012328 | 0.16305 | 0.005259 | 0.006308 | 0.029919 | 0.068308 | 0.099312 | 0.001373 | 0.089109 | 0.1891 | 0.032402 | -0.078901 | -0.020441 | 0.018638 | -0.010598 | 0.019715 | 0.10955 | 0.099707 | 0.052843 | 0.043
3895.5156 | 122.8592 | -0.11444 | 122.8317 | 0.13101 | -0.040521 | -0.030314 | -0.002124 | 0.040843 | 0.076426 | -0.03067 | 0.061645 | 0.15248 | 0.004937 | -0.11094 | -0.052484 | -0.008827 | -0.042641 | -0.012328 | 0.16305 | -0.008478 | 0.001729 | 0.029919 | 0.072886 | 0.10847 | 0.001373 | 0.093688 | 0.18452 | 0.03698 | -0.078901 | -0.020441 | 0.023216 | -0.010598 | 0.019715 | 0.11413 | 0.10429 | 0.057421 | 0.047578

## Thermal Data
Fire Time | A Position - Middle
-0.0583 | 11.6893
0.9417 | 11.6937
1.9417 | 11.6813
2.9417 | 11.9107
3.9417 | 12.1939
4.9417 | 12.4208
5.9417 | 12.715
6.9417 | 13.5542
7.9417 | 14.8398
8.9417 | 16.4983
9.9417 | 19.2395
10.9417 | 21.8187
11.9417 | 22.9714
12.9417 | 25.3637
13.9417 | 27.8617
14.9417 | 29.5195
15.9417 | 31.9766
16.9417 | 35.6237
17.9417 | 37.7455
18.9417 | 39.4374
19.9417 | 41.5533
20.9417 | 43.2566
21.9417 | 45.6329
22.9417 | 49.8808
23.9417 | 51.7237
24.9417 | 52.8708
25.9417 | 54.9827
26.9417 | 56.3522
27.9417 | 57.4051
28.9417 | 59.3849
29.9417 | 60.3408
30.9417 | 61.7717
31.9417 | 63.6561
32.9417 | 65.8968
33.9417 | 67.7791
34.9417 | 68.818
35.9417 | 70.1144
36.9417 | 72.0747
37.9417 | 74.0116
38.9417 | 75.8396
39.9417 | 77.6837
40.9417 | 78.0242
41.9417 | 79.3196
42.9417 | 81.4927
43.9417 | 83.5013
44.9417 | 86.3064
45.9417 | 89.5866
46.9417 | 90.8632
47.9417 | 92.2614
48.9417 | 93.4732
49.9417 | 94.8449
50.9417 | 95.2158
51.9417 | 97.1443
52.9417 | 97.7064
53.9417 | 98.7667
54.9417 | 100.6935
55.9417 | 101.7639
56.9417 | 102.1449
57.9417 | 102.2011
58.9417 | 104.337
59.9417 | 106.844
60.9417 | 108.9181
61.9417 | 109.0972
62.9417 | 110.6029
63.9417 | 111.508
64.9417 | 111.6329
65.9417 | 112.4446
66.9417 | 113.4273
67.9417 | 115.0578
68.9417 | 115.3668
69.9417 | 116.3443
70.9417 | 116.2626
71.9417 | 117.8658
72.9417 | 119.0517
73.9417 | 121.8207
74.9417 | 122.9252
75.9417 | 122.9644
76.9417 | 123.8699
77.9417 | 125.6346
78.9417 | 127.482
79.9417 | 129.4851
80.9417 | 132.1319
81.9417 | 134.522
82.9417 | 133.9409
83.9417 | 134.647
84.9417 | 135.199
85.9417 | 137.354
86.9417 | 138.4396
87.9417 | 137.7803
88.9417 | 138.9665
89.9417 | 139.5898
90.9417 | 141.2253
91.9417 | 141.1573
92.9417 | 141.0508
93.9417 | 140.3075
94.9417 | 140.0955
95.9417 | 139.1029
96.9417 | 141.3302
97.9417 | 143.6142
98.9417 | 146.717
99.9417 | 147.1182
100.9417 | 146.4282
101.9417 | 146.5044
102.9417 | 146.7819
103.9417 | 147.4239
104.9417 | 147.1898
105.9417 | 149.3365
106.9417 | 149.9891
107.9417 | 149.6916
108.9417 | 151.8983
109.9417 | 151.6478
110.9417 | 152.0181
111.9417 | 150.0972
112.9417 | 148.9977
113.9417 | 148.4484
114.9417 | 148.6529
115.9417 | 148.2122
116.9417 | 148.9127
117.9417 | 148.3482
118.9417 | 146.7657
119.9417 | 145.9507
120.9417 | 145.7949
121.9417 | 144.6831
122.9417 | 145.2109
123.9417 | 145.1392
124.9417 | 146.0479
125.9417 | 147.5336
126.9417 | 148.1184
127.9417 | 149.6564
128.9417 | 149.2411
129.9417 | 150.9544
130.9417 | 152.6081
131.9417 | 153.4668
132.9417 | 152.9967
133.9417 | 151.4101
134.9417 | 150.7752
135.9417 | 150.7273
136.9417 | 147.9368
137.9417 | 146.5763
138.9417 | 147.5091
139.9417 | 146.9604
140.9417 | 148.4239
141.9417 | 150.649
142.9417 | 150.3224
143.9417 | 150.3268
144.9417 | 151.7689
145.9417 | 153.3717
146.9417 | 153.1972
147.9417 | 153.454
148.9417 | 155.246
149.9417 | 155.3285
150.9417 | 155.4378
151.9417 | 154.6105
152.9417 | 153.3606
153.9417 | 153.1284
154.9573 | 155.8921
155.9573 | 156.3926
156.9417 | 154.8732
157.9417 | 155.6259
158.9573 | 157.7487
159.9573 | 159.9788
160.9573 | 161.7424
161.9417 | 162.18
162.9417 | 162.1602
163.9417 | 162.7231
164.9417 | 164.2731
165.9417 | 164.6684
166.9417 | 164.3484
167.9417 | 163.9475
168.9417 | 164.8985
169.9417 | 166.3433
170.9417 | 164.7313
171.9417 | 166.3498
172.9417 | 165.8031
173.9417 | 164.5465
174.9417 | 165.5925
175.9417 | 164.0957
176.9417 | 163.1529
177.9417 | 163.7205
178.9417 | 163.0501
179.9417 | 162.7203
180.9417 | 162.0883
181.9417 | 161.3419
182.9417 | 161.0186
183.9417 | 161.614
184.9417 | 161.9144
185.9417 | 160.9192
186.9417 | 161.1708
187.9417 | 160.8423
188.9417 | 161.5153
189.9417 | 163.4895
190.9417 | 163.7413
191.9417 | 165.0515
192.9417 | 164.4533
193.9417 | 163.1609
194.9417 | 161.518
195.9417 | 161.6016
196.9417 | 162.3767
197.9417 | 162.5532
198.9417 | 164.2141
199.9417 | 164.352
200.9417 | 163.8457
201.9417 | 162.276
202.9417 | 162.4921
203.9417 | 164.4745
204.9417 | 163.655
205.9417 | 163.8207
206.9417 | 165.2695
207.9417 | 165.5213
208.9417 | 165.2481
209.9417 | 164.8205
210.9417 | 165.158
211.9417 | 164.6123
212.9417 | 163.1949
213.9417 | 163.9848
214.9417 | 163.8451
215.9417 | 162.6142
216.9417 | 161.5812
217.9417 | 160.5756
218.9417 | 160.0416
219.9417 | 159.5215
220.9417 | 160.2791
221.9417 | 160.7477
222.9417 | 160.569
223.9417 | 160.1653
224.9417 | 160.5381
225.9417 | 160.0506
226.9417 | 160.2817
227.9417 | 159.938
228.9417 | 160.224
229.9417 | 160.8928
230.9417 | 160.1842
231.9417 | 161.7826
232.9417 | 161.2274
233.9417 | 160.5065
234.9417 | 160.0521
235.9417 | 159.7449
236.9417 | 160.1934
237.9417 | 160.1352
238.9417 | 160.3998
239.9417 | 159.7567
240.9417 | 159.9212
241.9417 | 159.9669
242.9417 | 159.6139
243.9417 | 159.3901
244.9417 | 159.395
245.9417 | 159.3178
246.9417 | 158.623
247.9417 | 159.0906
248.9417 | 158.6934
249.9417 | 158.982
250.9417 | 159.9769
251.9417 | 159.7445
252.9417 | 160.206
253.9417 | 161.9308
254.9417 | 163.3
255.9417 | 164.1547
256.9417 | 163.6026
257.9417 | 163.7251
258.9417 | 166.0433
259.9417 | 167.0019
260.9417 | 166.7981
261.9417 | 167.1427
262.9417 | 166.4874
263.9417 | 166.4313
264.9417 | 166.8268
265.9417 | 165.682
266.9417 | 165.2026
267.9417 | 165.1451
268.9417 | 166.0465
269.9417 | 165.6348
270.9417 | 165.6661
271.9417 | 166.2362
272.9417 | 165.969
273.9417 | 167.4348
274.9417 | 168.5479
275.9417 | 168.3229
276.9417 | 168.9226
277.9417 | 170.4252
278.9417 | 171.0388
279.9417 | 171.6828
280.9417 | 172.2423
281.9417 | 172.8617
282.9417 | 172.1857
283.9417 | 172.4697
284.9417 | 172.3714
285.9417 | 171.688
286.9417 | 171.9336
287.9417 | 171.5533
288.9417 | 171.528
289.9417 | 172.1983
290.9417 | 171.9178
291.9417 | 172.9294
292.9417 | 171.7454
293.9417 | 171.8276
294.9417 | 172.3191
295.9417 | 178.3764
296.9417 | 179.8631
297.9417 | 182.0608
298.9417 | 181.4944
299.9417 | 180.6297
300.9417 | 180.1621
301.9417 | 181.4229
302.9417 | 181.0502
303.9417 | 180.6422
304.9417 | 181.3135
305.9417 | 180.0347
306.9417 | 179.9603
307.9417 | 179.4608
308.9417 | 181.0881
309.9417 | 181.7475
310.9417 | 180.8719
311.9417 | 180.5161
312.9417 | 180.6562
313.9417 | 181.9929
314.9417 | 182.6245
315.9417 | 182.8255
316.9417 | 183.3613
317.9417 | 185.0022
318.9417 | 185.0294
319.9417 | 186.7416
320.9417 | 187.7076
321.9417 | 189.0385
322.9417 | 189.118
323.9417 | 192.4834
324.9417 | 191.4724
325.9417 | 191.3463
326.9417 | 190.9328
327.9417 | 192.0148
328.9417 | 191.0331
329.9417 | 191.6954
330.9417 | 191.0455
331.9417 | 190.5303
332.9417 | 190.3634
333.9417 | 189.4768
334.9417 | 188.052
335.9417 | 189.2648
336.9417 | 191.4379
337.9417 | 191.5643
338.9417 | 192.2142
339.9417 | 192.5353
340.9417 | 192.0757
341.9417 | 190.9321
342.9417 | 190.3995
343.9417 | 189.6954
344.9417 | 190.5809
345.9417 | 189.7674
346.9417 | 189.7677
347.9417 | 188.5237
348.9417 | 186.5431
349.9417 | 185.9632
350.9417 | 184.4737
351.9417 | 184.8626
352.9417 | 185.6277
353.9417 | 186.632
354.9417 | 188.3703
355.9417 | 189.516
356.9417 | 188.9615
357.9417 | 190.2249
358.9417 | 192.3868
359.9417 | 194.2599
360.9417 | 194.9013
361.9417 | 194.1341
362.9417 | 195.7831
363.9417 | 197.1277
364.9417 | 197.6096
365.9417 | 197.3796
366.9417 | 198.7741
367.9417 | 198.9007
368.9417 | 199.0047
369.9417 | 198.6685
370.9417 | 199.5582
371.9417 | 198.5611
372.9417 | 198.9454
373.9417 | 199.6967
374.9417 | 199.6076
375.9417 | 200.1977
376.9417 | 200.2712
377.9417 | 202.5411
378.9417 | 204.547
379.9417 | 205.3171
380.9417 | 205.9842
381.9417 | 204.703
382.9417 | 204.8975
383.9417 | 208.0106
384.9417 | 209.7912
385.9417 | 210.3944
386.9417 | 210.5262
387.9417 | 210.2692
388.9417 | 210.5431
389.9417 | 209.5298
390.9417 | 209.4366
391.9417 | 210.1657
392.9417 | 211.5091
393.9417 | 212.121
394.9417 | 212.3175
395.9417 | 213.9152
396.9417 | 214.387
397.9417 | 213.2689
398.9417 | 214.093
399.9417 | 214.2629
400.9417 | 214.7475
401.9417 | 214.5943
402.9417 | 212.8784
403.9417 | 211.653
404.9417 | 211.1637
405.9417 | 210.5616
406.9417 | 207.9632
407.9417 | 207.8786
408.9417 | 207.8509
409.9417 | 207.6759
410.9417 | 206.8161
411.9417 | 206.7035
412.9417 | 208.9134
413.9417 | 210.1171
414.9417 | 208.5147
415.9417 | 207.1451
416.9417 | 207.1114
417.9417 | 208.0274
418.9417 | 207.9878
419.9417 | 208.0312
420.9417 | 210.1072
421.9417 | 212.1128
422.9417 | 214.6264
423.9417 | 215.4316
424.9417 | 216.0521
425.9417 | 217.5253
426.9417 | 220.3589
427.9417 | 221.026
428.9417 | 222.0045
429.9417 | 222.8005
430.9417 | 222.3744
431.9417 | 221.964
432.9417 | 222.3245
433.9417 | 222.2378
434.9417 | 221.1174
435.9417 | 222.8892
436.9417 | 221.5387
437.9417 | 221.545
438.9417 | 227.9309
439.9417 | 226.9692
440.9417 | 227.5387
441.9417 | 228.0103
442.9417 | 228.3899
443.9417 | 227.8774
444.9417 | 227.6338
445.9417 | 228.3472
446.9417 | 227.4792
447.9417 | 228.6758
448.9417 | 230.6214
449.9417 | 231.0636
450.9417 | 231.8103
451.9417 | 232.2385
452.9417 | 232.5481
453.9417 | 229.9383
454.9417 | 229.1069
455.9417 | 227.8691
456.9417 | 227.4925
457.9417 | 226.8201
458.9417 | 224.2533
459.9417 | 226.7217
460.9417 | 228.1609
461.9417 | 229.5654
462.9417 | 228.4464
463.9417 | 228.9031
464.9417 | 229.3502
465.9417 | 229.7816
466.9417 | 231.8431
467.9417 | 232.1965
468.9417 | 234.1638
469.9417 | 236.2328
470.9417 | 238.2762
471.9417 | 238.3255
472.9417 | 239.3939
473.9417 | 237.1828
474.9417 | 237.4976
475.9417 | 241.6927
476.9417 | 240.6409
477.9417 | 241.1913
478.9417 | 241.6656
479.9417 | 241.598
480.9417 | 241.4489
481.9417 | 241.7792
482.9417 | 247.1184
483.9417 | 246.9357
484.9417 | 248.0555
485.9417 | 248.6262
486.9417 | 250.3861
487.9417 | 250.0552
488.9417 | 250.4598
489.9417 | 249.6676
490.9417 | 250.2101
491.9417 | 251.1123
492.9417 | 250.1007
493.9417 | 249.572
494.9417 | 250.1924
495.9417 | 250.0543
496.9417 | 248.7919
497.9417 | 248.8966
498.9417 | 247.6878
499.9417 | 249.0591
500.9573 | 249.2328
501.9417 | 248.3085
502.9417 | 248.7694
503.9417 | 248.4382
504.9417 | 250.674
505.9417 | 251.0395
506.9417 | 250.0628
507.9417 | 247.9637
508.9417 | 249.2574
509.9417 | 250.5595
510.9417 | 251.4975
511.9417 | 251.0795
512.9417 | 250.6958
513.9417 | 250.4313
514.9417 | 251.9406
515.9417 | 251.1452
516.9417 | 251.7376
517.9417 | 251.6276
518.9573 | 252.6213
519.9417 | 254.8587
520.9417 | 254.9855
521.9417 | 256.2176
522.9417 | 260.7293
523.9417 | 260.0141
524.9417 | 260.6712
525.9417 | 260.4927
526.9417 | 261.51
527.9417 | 263.0385
528.9417 | 263.0222
529.9417 | 263.0596
530.9417 | 261.7435
531.9417 | 260.7794
532.9417 | 261.9452
533.9417 | 261.0559
534.9417 | 262.1383
535.9417 | 266.1242
536.9417 | 266.2088
537.9417 | 265.8025
538.9417 | 266.8094
539.9417 | 265.2799
540.9417 | 264.9306
541.9417 | 264.8981
542.9417 | 264.7702
543.9417 | 264.2021
544.9417 | 263.9024
545.9417 | 264.0546
546.9417 | 263.9315
547.9417 | 266.6542
548.9573 | 266.391
549.9417 | 264.1526
550.9417 | 262.5683
551.9417 | 262.4475
552.9417 | 259.4432
553.9417 | 258.9833
554.9417 | 257.4334
555.9417 | 256.491
556.9417 | 255.3568
557.9417 | 255.5687
558.9417 | 254.3318
559.9417 | 255.1087
560.9417 | 253.9586
561.9417 | 254.5328
562.9417 | 254.4907
563.9417 | 254.963
564.9417 | 254.3051
565.9417 | 254.0958
566.9417 | 253.9764
567.9417 | 254.0443
568.9417 | 255.6891
569.9417 | 255.8334
570.9417 | 257.9849
571.9417 | 262.196
572.9417 | 261.1598
573.9417 | 263.0949
574.9417 | 263.431
575.9417 | 261.7208
576.9417 | 261.831
577.9417 | 261.4369
578.9417 | 263.1913
579.9417 | 263.7123
580.9417 | 263.0552
581.9417 | 262.8703
582.9417 | 261.7355
583.9417 | 262.2025
584.9417 | 262.6359
585.9417 | 262.7186
586.9417 | 262.7571
587.9417 | 262.9762
588.9417 | 261.9943
589.9417 | 260.6787
590.9417 | 261.1548
591.9417 | 263.4584
592.9417 | 264.163
593.9417 | 264.8879
594.9417 | 266.1198
595.9417 | 268.2805
596.9417 | 268.4144
597.9417 | 269.783
598.9417 | 271.469
599.9417 | 271.6774
600.9417 | 272.8642
601.9417 | 273.7878
602.9417 | 274.81
603.9417 | 280.1669
604.9417 | 280.9867
605.9417 | 284.4013
606.9417 | 286.7424
607.9417 | 291.9541
608.9573 | 292.2119
609.9417 | 294.137
610.9573 | 294.5843
611.9573 | 298.2242
612.9417 | 300.2345
613.9573 | 299.6802
614.9417 | 299.145
615.9417 | 300.3406
616.9417 | 296.9381
617.9417 | 297.1593
618.9417 | 296.4012
619.9417 | 294.4333
620.9417 | 296.746
621.9417 | 296.7018
622.9417 | 299.2516
623.9417 | 298.4812
624.9417 | 302.6272
625.9417 | 309.7997
626.9417 | 313.3926
627.9417 | 313.4897
628.9417 | 312.9418
629.9417 | 313.805
630.9417 | 312.4907
631.9417 | 312.4904
632.9417 | 313.4534
633.9417 | 311.3625
634.9417 | 312.405
635.9417 | 313.2594
636.9417 | 311.9915
637.9417 | 309.9788
638.9417 | 311.016
639.9417 | 312.3843
640.9417 | 312.7646
641.9417 | 318.8455
642.9417 | 319.9901
643.9417 | 321.1651
644.9417 | 319.6559
645.9417 | 317.8692
646.9417 | 315.8956
647.9417 | 317.2102
648.9417 | 316.9748
649.9417 | 322.0679
650.9417 | 333.9735
651.9417 | 334.1758
652.9417 | 335.6515
653.9417 | 335.7617
654.9417 | 336.5669
655.9417 | 336.9003
656.9417 | 337.6543
657.9417 | 343.4616
658.9417 | 344.3017
659.9417 | 348.0206
660.9417 | 348.2796
661.9417 | 350.138
662.9417 | 352.2574
663.9417 | 353.5964
664.9417 | 351.1373
665.9417 | 346.4976
666.9417 | 345.2304
667.9417 | 344.8415
668.9417 | 344.3658
669.9417 | 351.4153
670.9417 | 353.4928
671.9417 | 357.1505
672.9417 | 354.962
673.9417 | 357.804
674.9417 | 353.824
675.9417 | 351.7211
676.9417 | 349.9743
677.9417 | 350.5426
678.9417 | 347.8358
679.9417 | 350.6954
680.9417 | 348.145
681.9417 | 349.0721
682.9417 | 355.1393
683.9417 | 357.5006
684.9417 | 358.881
685.9417 | 358.8826
686.9417 | 361.5647
687.9417 | 385.4769
688.9417 | 387.7184
689.9417 | 387.8221
690.9417 | 390.725
691.9417 | 387.0563
692.9417 | 387.0821
693.9417 | 390.4165
694.9417 | 388.4776
695.9417 | 384.7316
696.9417 | 384.4357
697.9417 | 410.6983
698.9417 | 402.3649
699.9417 | 415.4409
700.9417 | 406.655
701.9417 | 417.6275
702.9417 | 410.2224
703.9417 | 406.1157
704.9417 | 399.0267
705.9417 | 392.1326
706.9417 | 396.6118
707.9417 | 391.759
708.9417 | 403.3539
709.9417 | 417.6861
710.9417 | 420.6568
711.9417 | 432.23
712.9417 | 432.5763
713.9417 | 421.2883
714.9417 | 411.5837
715.9417 | 403.9974
716.9417 | 400.3372
717.9417 | 410.4274
718.9417 | 404.4451
719.9417 | 425.6077
720.9417 | 429.0191
721.9417 | 447.5482
722.9417 | 442.9628
723.9417 | 435.8417
724.9417 | 457.9759
725.9417 | 473.1656
726.9417 | 466.9532
727.9417 | 492.1531
728.9417 | 479.7987
729.9417 | 495.6748
730.9417 | 495.1531
731.9417 | 494.5008
732.9417 | 509.5266
733.9417 | 504.733
734.9417 | 499.1112
735.9417 | 484.796
736.9417 | 472.7092
737.9417 | 463.3789
738.9417 | 455.1801
739.9417 | 444.7984
740.9417 | 447.0473
741.9417 | 455.1254
742.9417 | 449.469
743.9417 | 454.7809
744.9417 | 477.4632
745.9417 | 482.5759
746.9417 | 483.457
747.9417 | 504.9764
748.9417 | 491.6209
749.9417 | 488.5868
750.9417 | 480.3962
751.9417 | 468.0662
752.9417 | 478.9049
753.9417 | 482.1362
754.9417 | 483.0231
755.9417 | 479.3242
756.9417 | 478.0622
757.9417 | 471.9276
758.9573 | 466.6788
759.9417 | 467.6074
760.9417 | 474.0986
761.9417 | 477.8874
762.9417 | 477.8068
763.9417 | 471.8617
764.9417 | 481.5615
765.9417 | 484.1897
766.9417 | 471.9656
767.9417 | 464.7724
768.9417 | 456.6196
769.9417 | 450.0567
770.9417 | 440.5663
771.9417 | 435.5991
772.9417 | 430.8884
773.9417 | 423.1435
774.9417 | 421.5378
775.9417 | 417.7113
776.9417 | 416.0923
777.9417 | 414.9124
778.9417 | 429.8241
779.9417 | 422.1037
780.9417 | 422.9798
781.9417 | 419.571
782.9417 | 415.4898
783.9417 | 414.2504
784.9417 | 428.0662
785.9417 | 443.3781
786.9417 | 450.5647
787.9417 | 445.666
788.9417 | 438.4511
789.9417 | 447.1597
790.9417 | 440.3969
791.9417 | 434.562
792.9417 | 427.8442
793.9417 | 420.4096
794.9417 | 417.7126
795.9417 | 418.0668
796.9417 | 413.848
797.9417 | 416.1877
798.9417 | 422.7261
799.9417 | 415.2954
800.9417 | 416.4479
801.9417 | 417.2888
802.9417 | 420.529
803.9417 | 420.2501
804.9417 | 425.8731
805.9417 | 418.5793
806.9417 | 413.9659
807.9417 | 423.3896
808.9417 | 440.2225
809.9417 | 451.8181
810.9417 | 455.4226
811.9417 | 452.6851
812.9417 | 469.9824
813.9417 | 458.8938
814.9417 | 451.4837
815.9417 | 444.2069
816.9417 | 440.1909
817.9417 | 431.4748
818.9417 | 424.3043
819.9417 | 430.199
820.9417 | 445.2872
821.9417 | 435.4354
822.9417 | 431.1088
823.9417 | 424.9197
824.9417 | 421.284
825.9417 | 416.4034
826.9417 | 412.3756
827.9417 | 416.2496
828.9417 | 418.5801
829.9417 | 414.9071
830.9417 | 411.738
831.9417 | 408.3062
832.9417 | 409.8125
833.9417 | 402.8873
834.9417 | 400.6768
835.9417 | 395.7389
836.9417 | 396.2122
837.9417 | 391.1694
838.9417 | 388.1821
839.9417 | 385.0485
840.9417 | 381.9541
841.9417 | 378.6648
842.9417 | 376.9407
843.9417 | 373.8667
844.9417 | 372.2037
845.9417 | 369.1362
846.9417 | 369.4233
847.9417 | 365.4577
848.9417 | 363.6505
849.9417 | 363.1765
850.9417 | 366.3031
851.9417 | 365.9785
852.9417 | 366.9688
853.9417 | 366.4783
854.9417 | 365.4924
855.9417 | 368.1675
856.9417 | 367.0034
857.9417 | 367.3347
858.9417 | 364.9081
859.9417 | 363.9902
860.9417 | 364.8553
861.9417 | 366.5156
862.9417 | 381.7908
863.9417 | 379.6478
864.9417 | 381.5604
865.9417 | 377.1731
866.9417 | 380.1764
867.9417 | 377.3779
868.9417 | 375.3202
869.9417 | 378.5017
870.9417 | 409.8014
871.9417 | 420.1824
872.9417 | 419.7908
873.9417 | 417.1268
874.9417 | 413.4594
875.9417 | 417.8045
876.9417 | 422.627
877.9417 | 422.4149
878.9417 | 417.271
879.9417 | 414.9692
880.9417 | 407.0337
881.9417 | 402.9408
882.9417 | 396.3347
883.9417 | 394.5411
884.9417 | 397.1908
885.9417 | 404.3923
886.9417 | 408.3719
887.9417 | 413.115
888.9417 | 408.8185
889.9417 | 406.175
890.9417 | 402.6568
891.9417 | 399.1505
892.9417 | 396.2594
893.9417 | 393.9096
894.9417 | 391.2305
895.9417 | 390.4316
896.9417 | 388.6949
897.9417 | 388.3123
898.9417 | 391.7343
899.9417 | 387.0712
900.9417 | 386.4958
901.9417 | 397.0384
902.9417 | 395.7583
903.9417 | 391.4702
904.9417 | 391.9376
905.9417 | 392.9345
906.9417 | 394.7226
907.9417 | 392.9855
908.9417 | 391.7831
909.9417 | 388.742
910.9417 | 384.4445
911.9417 | 383.8035
912.9417 | 385.9702
913.9417 | 387.6735
914.9417 | 390.5908
915.9417 | 395.7517
916.9417 | 392.9521
917.9417 | 389.0612
918.9417 | 385.4055
919.9417 | 381.816
920.9417 | 381.1279
921.9417 | 385.9631
922.9417 | 394.7361
923.9417 | 394.9826
924.9417 | 393.8763
925.9417 | 392.8614
926.9417 | 391.6137
927.9417 | 393.4715
928.9417 | 390.5664
929.9417 | 389.4954
930.9417 | 387.1638
931.9417 | 389.7689
932.9417 | 392.7375
933.9417 | 395.3998
934.9417 | 396.2361
935.9417 | 392.9625
936.9417 | 390.0265
937.9417 | 388.0011
938.9417 | 386.6228
939.9417 | 385.0211
940.9417 | 386.9295
941.9417 | 386.7037
942.9417 | 384.7988
943.9417 | 386.0204
944.9417 | 384.9177
945.9417 | 386.1428
946.9417 | 382.9207
947.9417 | 381.3578
948.9417 | 384.5015
949.9417 | 387.1146
950.9417 | 388.4733
951.9417 | 386.718
952.9417 | 384.4051
953.9417 | 383.6244
954.9417 | 384.2786
955.9417 | 385.2647
956.9417 | 383.2035
957.9417 | 380.7972
958.9417 | 381.19
959.9417 | 380.4988
960.9417 | 381.6242
961.9417 | 382.6814
962.9417 | 382.2514
963.9417 | 380.0265
964.9417 | 382.7537
965.9417 | 385.7126
966.9417 | 387.4043
967.9417 | 388.4328
968.9417 | 390.3603
969.9417 | 393.8038
970.9417 | 399.2911
971.9417 | 402.5505
972.9417 | 404.4014
973.9417 | 403.3439
974.9417 | 403.7409
975.9417 | 404.891
976.9417 | 404.489
977.9417 | 403.6677
978.9417 | 400.2149
979.9417 | 397.6648
980.9417 | 395.5208
981.9417 | 394.8939
982.9417 | 395.5745
983.9417 | 395.8348
984.9417 | 396.6961
985.9417 | 395.6479
986.9417 | 391.846
987.9417 | 396.4968
988.9417 | 398.8106
989.9417 | 402.3776
990.9417 | 405.9344
991.9417 | 407.4062
992.9417 | 404.3461
993.9417 | 403.2227
994.9417 | 400.9504
995.9417 | 402.9558
996.9417 | 406.4977
997.9417 | 409.7549
998.9417 | 411.435
999.9417 | 415.6523
1000.9417 | 415.624
1001.9417 | 416.1734
1002.9417 | 413.6662
1003.9417 | 413.4482
1004.9417 | 414.7899
1005.9417 | 413.328
1006.9417 | 411.0191
1007.9417 | 407.3724
1008.9417 | 407.3991
1009.9417 | 405.392
1010.9417 | 403.1057
1011.9417 | 401.4876
1012.9417 | 402.3723
1013.9417 | 410.0255
1014.9417 | 406.3581
1015.9417 | 403.6095
1016.9417 | 404.3288
1017.9417 | 405.0505
1018.9417 | 400.9253
1019.9417 | 401.2663
1020.9417 | 400.636
1021.9417 | 401.3055
1022.9417 | 398.7029
1023.9417 | 399.1751
1024.9417 | 399.1257
1025.9417 | 397.6552
1026.9417 | 398.7748
1027.9417 | 399.5601
1028.9417 | 400.3595
1029.9417 | 399.1213
1030.9417 | 399.5207
1031.9417 | 398.9577
1032.9417 | 397.6355
1033.9417 | 396.9034
1034.9417 | 395.9079
1035.9417 | 395.0833
1036.9417 | 393.6486
1037.9417 | 394.0808
1038.9417 | 393.89
1039.9417 | 390.6408
1040.9417 | 387.8515
1041.9417 | 386.2625
1042.9417 | 384.5646
1043.9417 | 383.4427
1044.9417 | 385.5235
1045.9417 | 386.1923
1046.9417 | 387.3086
1047.9417 | 390.5262
1048.9417 | 393.0528
1049.9417 | 393.7566
1050.9417 | 394.8606
1051.9417 | 394.7902
1052.9417 | 397.7066
1053.9417 | 399.5554
1054.9417 | 396.128
1055.9417 | 397.2917
1056.9417 | 396.588
1057.9417 | 396.1868
1058.9417 | 395.0591
1059.9417 | 400.0437
1060.9417 | 402.9364
1061.9417 | 404.0986
1062.9417 | 409.2009
1063.9417 | 409.2096
1064.9417 | 410.0872
1065.9417 | 408.7316
1066.9417 | 406.5589
1067.9417 | 406.3343
1068.9417 | 407.4863
1069.9417 | 408.2868
1070.9417 | 409.7371
1071.9417 | 408.9236
1072.9417 | 407.1854
1073.9573 | 406.4293
1074.9417 | 408.3038
1075.9417 | 407.1712
1076.9417 | 405.5574
1077.9417 | 404.9782
1078.9417 | 404.3464
1079.9573 | 402.9807
1080.9417 | 401.3668
1081.9417 | 401.1027
1082.9417 | 400.0296
1083.9417 | 400.7207
1084.9417 | 397.659
1085.9417 | 396.508
1086.9417 | 397.2692
1087.9417 | 395.1928
1088.9417 | 394.262
1089.9417 | 391.8492
1090.9417 | 394.2316
1091.9417 | 393.9964
1092.9417 | 394.8802
1093.9417 | 395.0378
1094.9417 | 396.5706
1095.9417 | 395.0761
1096.9417 | 395.0284
1097.9417 | 394.6592
1098.9417 | 398.3228
1099.9417 | 405.1781
1100.9417 | 410.1625
1101.9417 | 417.2402
1102.9417 | 415.1154
1103.9417 | 414.876
1104.9417 | 412.5763
1105.9417 | 409.2323
1106.9417 | 406.7417
1107.9417 | 407.2372
1108.9417 | 405.1935
1109.9417 | 402.1675
1110.9417 | 401.9235
1111.9417 | 408.3786
1112.9417 | 409.8164
1113.9417 | 413.4571
1114.9417 | 417.5916
1115.9417 | 420.2572
1116.9417 | 420.6956
1117.9417 | 426.0377
1118.9417 | 425.017
1119.9417 | 422.0915
1120.9417 | 421.9207
1121.9417 | 419.5599
1122.9417 | 417.1396
1123.9417 | 414.5122
1124.9417 | 410.8257
1125.9417 | 410.7323
1126.9417 | 412.5884
1127.9417 | 412.758
1128.9417 | 414.2389
1129.9417 | 416.1193
1130.9417 | 423.6316
1131.9417 | 428.3549
1132.9417 | 429.1204
1133.9417 | 425.7188
1134.9417 | 422.9651
1135.9417 | 423.3003
1136.9417 | 421.7504
1137.9417 | 420.5413
1138.9417 | 421.7932
1139.9417 | 421.1881
1140.9417 | 424.9748
1141.9417 | 429.2718
1142.9417 | 433.8824
1143.9417 | 436.9076
1144.9417 | 436.0974
1145.9417 | 434.2625
1146.9417 | 435.3814
1147.9417 | 431.8359
1148.9417 | 428.7144
1149.9417 | 431.2434
1150.9417 | 432.0647
1151.9417 | 434.8091
1152.9417 | 438.1745
1153.9417 | 440.9194
1154.9417 | 443.9409
1155.9417 | 447.4401
1156.9417 | 452.3567
1157.9417 | 452.1104
1158.9417 | 450.5133
1159.9417 | 447.4927
1160.9417 | 446.8386
1161.9417 | 445.3473
1162.9417 | 441.1122
1163.9417 | 437.4206
1164.9417 | 441.7995
1165.9417 | 439.0638
1166.9417 | 439.3849
1167.9417 | 438.9032
1168.9417 | 439.1452
1169.9417 | 437.514
1170.9417 | 438.3006
1171.9417 | 439.0385
1172.9417 | 436.1955
1173.9417 | 433.4585
1174.9417 | 431.5431
1175.9417 | 428.0729
1176.9417 | 427.8912
1177.9417 | 429.9764
1178.9417 | 430.4194
1179.9417 | 431.8294
1180.9417 | 435.6506
1181.9417 | 434.3447
1182.9417 | 432.8122
1183.9417 | 433.4508
1184.9417 | 432.9175
1185.9417 | 435.7107
1186.9417 | 435.631
1187.9417 | 434.435
1188.9417 | 434.7605
1189.9417 | 435.7649
1190.9417 | 439.1661
1191.9417 | 441.1489
1192.9417 | 439.3081
1193.9417 | 438.5235
1194.9417 | 437.042
1195.9417 | 441.1807
1196.9417 | 462.4969
1197.9417 | 459.492
1198.9417 | 456.2368
1199.9417 | 453.6529
1200.9417 | 452.1684
1201.9417 | 450.5376
1202.9417 | 449.3056
1203.9417 | 445.3471
1204.9417 | 445.3016
1205.9417 | 445.3665
1206.9417 | 445.7535
1207.9417 | 446.8797
1208.9417 | 447.5124
1209.9417 | 448.4464
1210.9417 | 446.1246
1211.9417 | 444.7335
1212.9417 | 441.2053
1213.9417 | 445.7264
1214.9417 | 444.7965
1215.9417 | 444.7558
1216.9417 | 447.4197
1217.9417 | 451.251
1218.9417 | 450.0789
1219.9417 | 450.0427
1220.9417 | 449.4778
1221.9417 | 466.721
1222.9417 | 467.848
1223.9417 | 473.3961
1224.9417 | 488.1302
1225.9417 | 497.2483
1226.9417 | 492.8332
1227.9417 | 492.8029
1228.9417 | 490.1291
1229.9417 | 488.242
1230.9417 | 489.4797
1231.9417 | 488.4051
1232.9417 | 488.6626
1233.9417 | 483.508
1234.9417 | 478.6784
1235.9417 | 474.8403
1236.9417 | 470.7225
1237.9417 | 470.8174
1238.9417 | 470.2148
1239.9417 | 466.7373
1240.9417 | 462.1639
1241.9417 | 460.7447
1242.9417 | 461.6479
1243.9417 | 468.1807
1244.9417 | 467.6123
1245.9417 | 470.5067
1246.9417 | 472.5376
1247.9417 | 474.9686
1248.9417 | 475.6161
1249.9417 | 478.8816
1250.9417 | 480.5752
1251.9417 | 482.6062
1252.9417 | 492.0194
1253.9417 | 500.9895
1254.9417 | 504.7481
1255.9417 | 500.8203
1256.9417 | 501.6998
1257.9417 | 502.3536
1258.9417 | 503.1519
1259.9417 | 498.9856
1260.9417 | 495.9094
1261.9417 | 498.7643
1262.9417 | 498.587
1263.9417 | 493.9674
1264.9417 | 489.4295
1265.9417 | 485.8861
1266.9417 | 485.2783
1267.9417 | 489.5558
1268.9417 | 489.4397
1269.9417 | 494.4699
1270.9417 | 500.3727
1271.9417 | 511.9385
1272.9417 | 507.7092
1273.9417 | 503.6613
1274.9417 | 501.1539
1275.9417 | 500.1487
1276.9417 | 495.305
1277.9417 | 500.3298
1278.9417 | 497.8972
1279.9417 | 496.9055
1280.9417 | 492.6418
1281.9417 | 488.4942
1282.9417 | 483.0609
1283.9417 | 478.8294
1284.9417 | 477.7609
1285.9417 | 474.5225
1286.9417 | 477.5578
1287.9417 | 474.7603
1288.9417 | 468.3329
1289.9417 | 464.0797
1290.9417 | 458.3104
1291.9417 | 457.7464
1292.9417 | 459.4981
1293.9417 | 463.6029
1294.9417 | 465.9449
1295.9417 | 464.9908
1296.9417 | 460.9962
1297.9417 | 461.9249
1298.9417 | 461.9706
1299.9417 | 459.0222
1300.9417 | 457.494
1301.9417 | 457.5184
1302.9417 | 454.2866
1303.9417 | 452.5611
1304.9417 | 451.7901
1305.9417 | 453.7279
1306.9417 | 453.8398
1307.9417 | 451.7355
1308.9417 | 449.1515
1309.9417 | 448.535
1310.9417 | 446.5732
1311.9417 | 443.7638
1312.9417 | 441.3173
1313.9417 | 439.6783
1314.9417 | 437.7481
1315.9417 | 434.4423
1316.9417 | 432.3395
1317.9417 | 435.2812
1318.9417 | 434.2628
1319.9417 | 436.8348
1320.9417 | 437.7525
1321.9417 | 441.6938
1322.9417 | 443.8954
1323.9417 | 444.6978
1324.9417 | 446.1874
1325.9417 | 447.5077
1326.9417 | 447.5106
1327.9417 | 444.059
1328.9417 | 438.5003
1329.9417 | 440.4667
1330.9417 | 442.6726
1331.9417 | 443.8396
1332.9417 | 450.4146
1333.9417 | 461.165
1334.9417 | 463.5493
1335.9417 | 466.2549
1336.9417 | 466.8632
1337.9417 | 469.8153
1338.9417 | 473.2989
1339.9417 | 470.2363
1340.9417 | 464.9541
1341.9417 | 462.192
1342.9417 | 462.3882
1343.9417 | 459.3462
1344.9417 | 458.5917
1345.9417 | 456.0294
1346.9417 | 452.1759
1347.9417 | 452.4416
1348.9417 | 454.0615
1349.9417 | 452.8226
1350.9417 | 448.2688
1351.9417 | 442.7308
1352.9417 | 440.8947
1353.9417 | 442.066
1354.9417 | 441.4074
1355.9417 | 438.5585
1356.9417 | 441.1624
1357.9417 | 443.2832
1358.9417 | 438.9508
1359.9417 | 435.0288
1360.9417 | 432.8652
1361.9417 | 432.9148
1362.9417 | 436.32
1363.9417 | 434.4083
1364.9417 | 433.5859
1365.9417 | 433.195
1366.9417 | 429.0925
1367.9417 | 428.697
1368.9417 | 429.0204
1369.9417 | 429.9048
1370.9417 | 429.83
1371.9417 | 428.9457
1372.9417 | 434.0627
1373.9417 | 442.2314
1374.9417 | 445.6707
1375.9417 | 445.3537
1376.9417 | 442.9155
1377.9417 | 440.3947
1378.9417 | 437.0439
1379.9417 | 435.4621
1380.9417 | 432.5293
1381.9417 | 432.6865
1382.9417 | 430.5524
1383.9417 | 428.3292
1384.9417 | 427.237
1385.9417 | 427.3719
1386.9417 | 426.1885
1387.9417 | 426.7542
1388.9417 | 424.5739
1389.9417 | 424.2109
1390.9417 | 424.5611
1391.9417 | 425.4858
1392.9417 | 425.4064
1393.9417 | 425.6036
1394.9417 | 425.0652
1395.9417 | 429.8331
1396.9417 | 431.7695
1397.9417 | 433.2113
1398.9417 | 430.5774
1399.9417 | 431.6002
1400.9417 | 432.2728
1401.9417 | 431.3889
1402.9417 | 432.0508
1403.9417 | 429.7654
1404.9417 | 427.9956
1405.9417 | 427.8139
1406.9417 | 425.2406
1407.9417 | 425.486
1408.9417 | 425.0207
1409.9417 | 424.4757
1410.9417 | 427.444
1411.9417 | 438.7853
1412.9417 | 441.2762
1413.9417 | 440.5457
1414.9417 | 439.5207
1415.9417 | 438.8137
1416.9417 | 440.6762
1417.9417 | 441.0041
1418.9417 | 440.7766
1419.9417 | 439.1099
1420.9417 | 439.0852
1421.9417 | 440.153
1422.9417 | 438.9536
1423.9417 | 440.347
1424.9417 | 440.7452
1425.9417 | 439.5108
1426.9417 | 440.5764
1427.9417 | 436.4652
1428.9417 | 433.6702
1429.9417 | 431.3099
1430.9417 | 434.2759
1431.9417 | 437.2855
1432.9417 | 441.0842
1433.9417 | 443.4028
1434.9417 | 452.3506
1435.9417 | 459.3107
1436.9417 | 465.9613
1437.9417 | 494.2943
1438.9417 | 497.3636
1439.9417 | 500.278
1440.9417 | 499.2663
1441.9417 | 495.5773
1442.9417 | 493.8382
1443.9417 | 501.5685
1444.9417 | 504.4311
1445.9417 | 501.0617
1446.9417 | 506.2104
1447.9417 | 502.2557
1448.9417 | 499.8014
1449.9417 | 504.5074
1450.9417 | 516.8881
1451.9417 | 519.7145
1452.9417 | 515.9211
1453.9417 | 516.9858
1454.9417 | 530.8827
1455.9417 | 530.487
1456.9417 | 525.6686
1457.9417 | 550.4325
1458.9417 | 545.7374
1459.9417 | 537.2585
1460.9417 | 533.9769
1461.9417 | 527.4944
1462.9417 | 519.7462
1463.9417 | 517.8489
1464.9417 | 510.6071
1465.9417 | 508.6375
1466.9417 | 504.6142
1467.9417 | 508.5281
1468.9417 | 516.3316
1469.9417 | 513.388
1470.9417 | 509.7983
1471.9417 | 508.1236
1472.9417 | 501.4081
1473.9417 | 513.3683
1474.9417 | 506.7213
1475.9417 | 512.8519
1476.9417 | 512.5186
1477.9417 | 511.1898
1478.9417 | 505.1779
1479.9417 | 501.4858
1480.9417 | 506.6379
1481.9417 | 503.2178
1482.9417 | 498.0323
1483.9417 | 493.8174
1484.9417 | 498.2695
1485.9417 | 495.6484
1486.9417 | 493.4035
1487.9417 | 488.4772
1488.9417 | 489.8522
1489.9417 | 485.1833
1490.9417 | 482.4321
1491.9417 | 480.313
1492.9417 | 477.3424
1493.9417 | 488.5458
1494.9417 | 489.471
1495.9417 | 489.4983
1496.9417 | 498.8092
1497.9417 | 494.9567
1498.9417 | 489.8585
1499.9417 | 490.3434
1500.9417 | 484.7312
1501.9417 | 479.1093
1502.9417 | 476.1925
1503.9417 | 481.8195
1504.9417 | 486.2602
1505.9417 | 488.6794
1506.9417 | 493.9457
1507.9417 | 498.9491
1508.9417 | 499.3198
1509.9417 | 500.5628
1510.9417 | 508.5212
1511.9417 | 513.4041
1512.9417 | 517.8579
1513.9417 | 517.5347
1514.9417 | 518.6578
1515.9417 | 521.6222
1516.9417 | 525.5224
1517.9417 | 530.8485
1518.9417 | 535.6931
1519.9417 | 546.7503
1520.9417 | 550.9374
1521.9417 | 559.1288
1522.9417 | 563.3319
1523.9417 | 566.6991
1524.9417 | 567.0791
1525.9417 | 571.5618
1526.9417 | 571.3235
1527.9417 | 576.8125
1528.9417 | 586.3354
1529.9417 | 590.1762
1530.9417 | 589.2035
1531.9417 | 583.9725
1532.9417 | 580.5066
1533.9417 | 579.9741
1534.9417 | 575.3094
1535.9417 | 573.1622
1536.9417 | 588.6858
1537.9417 | 585.7619
1538.9417 | 590.0053
1539.9417 | 596.0974
1540.9417 | 597.6276
1541.9417 | 596.7376
1542.9417 | 596.8979
1543.9417 | 591.418
1544.9417 | 592.8191
1545.9417 | 589.098
1546.9417 | 586.8745
1547.9417 | 580.5312
1548.9417 | 593.5679
1549.9417 | 587.6371
1550.9417 | 586.0781
1551.9417 | 583.9457
1552.9417 | 587.5531
1553.9417 | 581.5052
1554.9417 | 575.4774
1555.9417 | 566.6152
1556.9417 | 560.0638
1557.9417 | 549.2104
1558.9417 | 542.0227
1559.9417 | 554.0101
1560.9417 | 554.659
1561.9417 | 551.0838
1562.9417 | 548.9378
1563.9417 | 548.8525
1564.9417 | 543.2131
1565.9417 | 544.8034
1566.9417 | 555.4691
1567.9417 | 555.0691
1568.9417 | 559.8377
1569.9417 | 561.3897
1570.9417 | 564.8727
1571.9417 | 560.0499
1572.9417 | 558.5631
1573.9417 | 552.3742
1574.9417 | 552.0732
1575.9417 | 552.5297
1576.9417 | 555.9196
1577.9417 | 558.8126
1578.9417 | 553.7657
1579.9417 | 554.3118
1580.9417 | 554.7725
1581.9417 | 552.7864
1582.9417 | 554.3223
1583.9417 | 558.2967
1584.9417 | 578.0515
1585.9417 | 575.5202
1586.9417 | 573.5195
1587.9417 | 573.3611
1588.9417 | 577.4047
1589.9417 | 571.3069
1590.9417 | 576.5131
1591.9417 | 573.5091
1592.9417 | 572.6054
1593.9417 | 565.0087
1594.9417 | 568.6002
1595.9417 | 564.1884
1596.9417 | 581.0195
1597.9417 | 578.5634
1598.9417 | 575.4441
1599.9573 | 577.1184
1600.9417 | 591.4109
1601.9417 | 603.9602
1602.9417 | 596.3295
1603.9417 | 586.2657
1604.9417 | 585.4455
1605.9417 | 588.8287
1606.9417 | 584.9811
1607.9417 | 585.1265
1608.9417 | 576.1968
1609.9417 | 567.855
1610.9417 | 571.724
1611.9417 | 586.451
1612.9417 | 588.2314
1613.9417 | 594.7996
1614.9417 | 599.7443
1615.9417 | 591.5135
1616.9417 | 585.1487
1617.9417 | 581.9759
1618.9573 | 580.5015
1619.9417 | 575.5982
1620.9417 | 572.0364
1621.9417 | 579.9977
1622.9417 | 573.1185
1623.9573 | 570.2379
1624.9417 | 569.3587
1625.9417 | 566.5772
1626.9573 | 560.9291
1627.9417 | 557.76
1628.9417 | 562.0379
1629.9573 | 577.2256
1630.9417 | 578.8856
1631.9417 | 576.4097
1632.9417 | 596.4946
1633.9573 | 583.397
1634.9417 | 587.2141
1635.9417 | 599.067
1636.9417 | 591.8245
1637.9417 | 597.9971
1638.9573 | 585.7085
1639.9417 | 578.4966
1640.9417 | 586.0403
1641.9417 | 577.8574
1642.9417 | 419.9548
1643.9417 | 20.4591
1644.9417 | 652.7681
1645.9417 | 645.5099
1646.9417 | 636.6601
1647.9417 | 626.9182
1648.9417 | 402.9681
1649.9417 | 613.8979
1650.9417 | 605.4458
1651.9417 | 42.018
1652.9417 | 555.563
1653.9417 | 459.6509
1654.9417 | 605.9909
1655.9417 | 618.988
1656.9417 | 613.0096
1657.9417 | 15.1951
1658.9417 | 500.7104
1659.9417 | 552.4485
1660.9417 | 330.8639
1661.9417 | 673.1928
1662.9417 | 164.6141
1663.9417 | 687.8519
1664.9417 | 645.0345
1665.9417 | 116.9174
1666.9417 | 317.8888
1667.9417 | 560.8692
1668.9417 | 720.35
1669.9417 | 734.062
1670.9417 | 720.8264
1671.9417 | 717.5474
1672.9417 | 730.844
1673.9417 | 640.9826
1674.9417 | 715.7287
1675.9417 | 696.9441
1676.9417 | 698.7311
1677.9417 | 691.6937
1678.9417 | 682.4009
1679.9417 | 668.7989
1680.9417 | 672.133
1681.9417 | 667.2367
1682.9417 | 666.8273
1683.9417 | 654.4085
1684.9417 | 668.5089
1685.9417 | 655.0367
1686.9417 | 658.791
1687.9417 | 656.4243
1688.9417 | 662.6241
1689.9417 | 655.6767
1690.9417 | 650.7236
1691.9417 | 645.4602
1692.9417 | 623.6309
1693.9417 | 348.4592
1694.9417 | 650.0011
1695.9417 | 646.1709
1696.9417 | 637.3294
1697.9417 | 640.1443
1698.9417 | 633.9011
1699.9417 | 630.7524
1700.9417 | 617.7913
1701.9417 | 625.5144
1702.9417 | 643.4938
1703.9417 | 656.7523
1704.9417 | 664.6196
1705.9417 | 661.8121
1706.9417 | 655.3922
1707.9417 | 648.1663
1708.9417 | 637.737
1709.9417 | 628.0129
1710.9417 | 617.9331
1711.9417 | 610.5098
1712.9417 | 600.6541
1713.9417 | 591.4108
1714.9417 | 597.5908
1715.9417 | 602.6284
1716.9417 | 598.2148
1717.9417 | 589.6458
1718.9417 | 585.7449
1719.9417 | 595.2491
1720.9417 | 593.9996
1721.9417 | 589.2455
1722.9417 | 597.0882
1723.9417 | 604.9895
1724.9417 | 618.2353
1725.9417 | 634.4226
1726.9417 | 646.7845
1727.9417 | 653.9798
1728.9417 | 649.9585
1729.9417 | 651.1257
1730.9417 | 645.5416
1731.9417 | 639.6949
1732.9417 | 631.185
1733.9417 | 632.5477
1734.9417 | 638.6202
1735.9417 | 634.119
1736.9417 | 634.1449
1737.9417 | 626.5398
1738.9417 | 629.3739
1739.9417 | 626.4571
1740.9417 | 638.8748
1741.9417 | 654.2354
1742.9417 | 668.9792
1743.9417 | 683.5323
1744.9417 | 694.4158
1745.9417 | 702.7492
1746.9417 | 717.128
1747.9417 | 718.9565
1748.9417 | 719.5759
1749.9417 | 725.7793
1750.9417 | 716.6899
1751.9417 | 712.0664
1752.9417 | 715.9466
1753.9417 | 719.4782
1754.9417 | 720.1978
1755.9417 | 727.813
1756.9417 | 725.5451
1757.9417 | 723.2722
1758.9417 | 722.91
1759.9417 | 724.6527
1760.9417 | 728.7372
1761.9417 | 725.911
1762.9417 | 727.3651
1763.9417 | 731.2266
1764.9417 | 723.2789
1765.9417 | 720.6113
1766.9417 | 727.8774
1767.9417 | 735.8916
1768.9417 | 736.9427
1769.9417 | 733.7048
1770.9417 | 738.7539
1771.9417 | 736.9116
1772.9573 | 737.7201
1773.9417 | 742.106
1774.9417 | 748.7475
1775.9417 | 745.7106
1776.9417 | 737.2071
1777.9417 | 719.451
1778.9417 | 721.7546
1779.9417 | 726.5727
1780.9417 | 733.761
1781.9417 | 736.8275
1782.9417 | 738.6025
1783.9417 | 745.8595
1784.9417 | 741.1883
1785.9417 | 748.8435
1786.9417 | 748.6657
1787.9417 | 739.0376
1788.9417 | 721.6617
1789.9417 | 710.0912
1790.9417 | 694.6706
1791.9417 | 676.9148
1792.9417 | 657.7228
1793.9417 | 672.4144
1794.9417 | 684.1678
1795.9417 | 695.4026
1796.9417 | 703.1924
1797.9417 | 720.1857
1798.9417 | 720.5738
1799.9417 | 720.9335
1800.9417 | 729.3724
1801.9417 | 732.113
1802.9417 | 741.3092
1803.9417 | 739.114
1804.9417 | 738.7842
1805.9417 | 736.3255
1806.9417 | 737.5082
1807.9417 | 738.4808
1808.9417 | 742.1967
1809.9417 | 729.3001
1810.9417 | 728.2587
1811.9417 | 730.4852
1812.9417 | 728.9949
1813.9417 | 732.407
1814.9417 | 728.5373
1815.9417 | 732.7072
1816.9417 | 734.5015
1817.9417 | 734.852
1818.9417 | 735.8052
1819.9417 | 724.1133
1820.9417 | 727.8958
1821.9417 | 735.4333
1822.9417 | 733.5773
1823.9417 | 730.4822
1824.9417 | 734.7128
1825.9417 | 739.882
1826.9417 | 744.827
1827.9417 | 741.9087
1828.9417 | 745.5086
1829.9417 | 743.7708
1830.9417 | 742.3019
1831.9417 | 741.9784
1832.9417 | 740.4334
1833.9417 | 741.4685
1834.9417 | 736.5949
1835.9417 | 737.9242
1836.9417 | 735.6016
1837.9417 | 729.9048
1838.9417 | 736.055
1839.9417 | 725.81
1840.9417 | 720.4991
1841.9417 | 716.1371
1842.9417 | 704.6335
1843.9417 | 706.4117
1844.9417 | 713.4946
1845.9417 | 730.922
1846.9417 | 737.3217
1847.9417 | 741.5421
1848.9417 | 742.9078
1849.9417 | 741.3562
1850.9417 | 741.2249
1851.9417 | 743.9216
1852.9417 | 741.0775
1853.9417 | 742.7814
1854.9417 | 747.988
1855.9417 | 760.0569
1856.9417 | 759.7145
1857.9417 | 760.0284
1858.9417 | 747.1786
1859.9417 | 735.5077
1860.9417 | 744.9337
1861.9417 | 746.9986
1862.9417 | 726.4687
1863.9417 | 720.4373
1864.9417 | 718.3826
1865.9417 | 728.5695
1866.9417 | 726.1901
1867.9417 | 725.2304
1868.9417 | 718.813
1869.9417 | 737.8456
1870.9417 | 724.9995
1871.9417 | 728.7276
1872.9417 | 731.3076
1873.9417 | 736.74
1874.9417 | 741.591
1875.9417 | 747.5604
1876.9417 | 742.6438
1877.9417 | 744.7244
1878.9417 | 747.1088
1879.9417 | 746.4473
1880.9417 | 737.2344
1881.9417 | 715.5322
1882.9417 | 701.5357
1883.9417 | 693.182
1884.9417 | 691.3663
1885.9417 | 702.6598
1886.9417 | 698.8745
1887.9417 | 698.2127
1888.9417 | 697.6811
1889.9417 | 687.3402
1890.9417 | 677.8293
1891.9417 | 677.811
1892.9417 | 676.046
1893.9417 | 690.791
1894.9417 | 676.0765
1895.9417 | 669.0577
1896.9417 | 653.1214
1897.9417 | 655.2696
1898.9417 | 658.0405
1899.9417 | 646.9874
1900.9417 | 634.3532
1901.9417 | 647.0716
1902.9417 | 651.8024
1903.9417 | 663.5614
1904.9417 | 684.6144
1905.9417 | 678.6016
1906.9417 | 667.1308
1907.9417 | 660.4983
1908.9573 | 659.2767
1909.9417 | 675.9485
1910.9417 | 688.0977
1911.9417 | 697.1485
1912.9417 | 707.3346
1913.9417 | 708.9517
1914.9417 | 719.4142
1915.9417 | 730.1755
1916.9417 | 737.0096
1917.9417 | 742.1754
1918.9417 | 741.8066
1919.9417 | 750.2112
1920.9417 | 754.3531
1921.9417 | 752.9358
1922.9417 | 762.7373
1923.9573 | 759.5691
1924.9417 | 759.5883
1925.9417 | 755.5741
1926.9417 | 754.1844
1927.9417 | 756.0097
1928.9417 | 748.5104
1929.9573 | 735.9218
1930.9417 | 738.5949
1931.9573 | 743.9472
1932.9417 | 745.0005
1933.9573 | 743.8203
1934.9417 | 744.5412
1935.9417 | 747.4957
1936.9417 | 753.5896
1937.9417 | 748.6789
1938.9417 | 743.113
1939.9417 | 748.8026
1940.9417 | 745.3464
1941.9417 | 745.1953
1942.9417 | 745.7099
1943.9417 | 750.9828
1944.9417 | 754.0743
1945.9417 | 745.273
1946.9417 | 741.4797
1947.9417 | 745.3717
1948.9417 | 750.6668
1949.9417 | 748.7411
1950.9417 | 747.8456
1951.9417 | 745.3929
1952.9417 | 749.2445
1953.9417 | 751.2966
1954.9417 | 744.2542
1955.9417 | 745.45
1956.9417 | 750.6883
1957.9417 | 757.8382
1958.9417 | 753.2918
1959.9417 | 746.4469
1960.9417 | 747.7715
1961.9417 | 750.2367
1962.9417 | 751.1202
1963.9417 | 749.2329
1964.9417 | 744.187
1965.9417 | 725.6949
1966.9417 | 729.4457
1967.9417 | 740.0541
1968.9573 | 752.5937
1969.9417 | 756.8998
1970.9417 | 750.9056
1971.9417 | 749.9675
1972.9417 | 745.6824
1973.9417 | 748.9164
1974.9417 | 755.0936
1975.9417 | 764.5087
1976.9417 | 757.1359
1977.9417 | 758.0896
1978.9417 | 765.5677
1979.9417 | 765.373
1980.9417 | 763.7129
1981.9417 | 764.6841
1982.9417 | 758.9512
1983.9417 | 760.6299
1984.9417 | 770.8132
1985.9417 | 765.1128
1986.9417 | 760.268
1987.9417 | 764.0707
1988.9417 | 764.6477
1989.9417 | 761.6929
1990.9417 | 757.5199
1991.9417 | 754.5782
1992.9417 | 750.819
1993.9573 | 753.4465
1994.9417 | 746.3348
1995.9417 | 740.8018
1996.9417 | 744.1784
1997.9417 | 745.648
1998.9417 | 722.8514
1999.9417 | 725.6908
2000.9417 | 732.6651
2001.9417 | 736.5586
2002.9417 | 735.4216
2003.9417 | 746.4037
2004.9417 | 739.8512
2005.9417 | 750.1322
2006.9417 | 757.2719
2007.9417 | 756.6216
2008.9417 | 749.8151
2009.9417 | 750.7362
2010.9417 | 751.2329
2011.9417 | 755.4684
2012.9417 | 744.9244
2013.9417 | 747.7796
2014.9417 | 750.8968
2015.9417 | 754.5555
2016.9417 | 755.2121
2017.9417 | 755.2295
2018.9417 | 758.9918
2019.9417 | 760.348
2020.9417 | 753.5106
2021.9417 | 750.6824
2022.9417 | 759.7107
2023.9417 | 757.5769
2024.9417 | 757.1527
2025.9417 | 758.9912
2026.9417 | 750.8196
2027.9417 | 745.1071
2028.9417 | 741.6054
2029.9417 | 736.301
2030.9417 | 735.3157
2031.9417 | 738.5968
2032.9417 | 737.3361
2033.9417 | 740.4768
2034.9417 | 748.9111
2035.9417 | 752.8361
2036.9417 | 747.2792
2037.9417 | 747.1191
2038.9417 | 741.9775
2039.9417 | 746.9675
2040.9417 | 750.7726
2041.9417 | 744.4086
2042.9417 | 736.4627
2043.9417 | 724.6388
2044.9417 | 724.9435
2045.9417 | 727.4717
2046.9417 | 727.933
2047.9417 | 730.4553
2048.9417 | 738.4561
2049.9417 | 732.5155
2050.9417 | 741.9163
2051.9417 | 735.4161
2052.9417 | 737.1798
2053.9417 | 740.5321
2054.9417 | 740.4151
2055.9417 | 745.8797
2056.9417 | 746.8889
2057.9417 | 750.3499
2058.9417 | 747.096
2059.9417 | 751.5632
2060.9417 | 743.5377
2061.9417 | 748.039
2062.9417 | 757.9057
2063.9417 | 750.024
2064.9417 | 742.7596
2065.9417 | 741.3759
2066.9417 | 730.892
2067.9417 | 725.475
2068.9417 | 728.6641
2069.9417 | 729.5472
2070.9417 | 739.4802
2071.9417 | 742.8651
2072.9417 | 736.542
2073.9417 | 737.1243
2074.9417 | 740.1147
2075.9417 | 738.4898
2076.9417 | 741.5408
2077.9417 | 740.3613
2078.9417 | 736.3785
2079.9417 | 742.7097
2080.9417 | 755.8861
2081.9417 | 755.6855
2082.9417 | 752.1765
2083.9417 | 751.4109
2084.9417 | 751.4296
2085.9417 | 750.624
2086.9417 | 755.0803
2087.9417 | 752.94
2088.9417 | 757.849
2089.9417 | 762.8098
2090.9417 | 761.9208
2091.9417 | 762.0114
2092.9417 | 748.7857
2093.9417 | 749.6387
2094.9417 | 746.3705
2095.9417 | 741.0112
2096.9417 | 752.267
2097.9417 | 758.3103
2098.9417 | 756.4485
2099.9417 | 751.6464
2100.9417 | 761.0466
2101.9417 | 754.9039
2102.9417 | 759.5646
2103.9417 | 767.7033
2104.9417 | 759.6651
2105.9417 | 757.8118
2106.9417 | 758.7667
2107.9417 | 753.4001
2108.9417 | 745.43
2109.9417 | 742.9979
2110.9417 | 739.0383
2111.9417 | 739.2921
2112.9417 | 747.7265
2113.9417 | 747.6219
2114.9417 | 750.9373
2115.9417 | 754.1943
2116.9417 | 748.045
2117.9417 | 747.6393
2118.9417 | 746.069
2119.9417 | 752.5404
2120.9417 | 755.0211
2121.9417 | 756.4024
2122.9417 | 753.0092
2123.9417 | 743.6845
2124.9417 | 747.6201
2125.9417 | 737.4145
2126.9417 | 736.3212
2127.9417 | 736.694
2128.9417 | 734.5386
2129.9417 | 737.1001
2130.9417 | 735.7744
2131.9417 | 741.3789
2132.9417 | 752.4055
2133.9417 | 758.0453
2134.9417 | 758.3333
2135.9417 | 755.7148
2136.9417 | 744.806
2137.9417 | 736.235
2138.9417 | 739.5899
2139.9417 | 742.4963
2140.9417 | 736.7069
2141.9417 | 740.0459
2142.9417 | 749.2087
2143.9417 | 749.0218
2144.9417 | 754.2871
2145.9417 | 769.5233
2146.9417 | 771.6126
2147.9417 | 778.4603
2148.9417 | 780.3537
2149.9417 | 781.1555
2150.9417 | 783.8724
2151.9417 | 783.1555
2152.9417 | 782.3947
2153.9417 | 778.0867
2154.9417 | 774.4731
2155.9417 | 780.1811
2156.9417 | 780.1338
2157.9417 | 774.1815
2158.9417 | 777.8727
2159.9417 | 765.2888
2160.9417 | 766.5938
2161.9417 | 761.6494
2162.9417 | 755.0082
2163.9417 | 758.2768
2164.9417 | 768.148
2165.9417 | 777.0876
2166.9417 | 773.9438
2167.9417 | 773.2501
2168.9417 | 774.5909
2169.9417 | 768.2669
2170.9417 | 758.3083
2171.9417 | 756.7243
2172.9417 | 746.7662
2173.9417 | 735.4324
2174.9417 | 739.2052
2175.9417 | 740.5566
2176.9417 | 741.2323
2177.9417 | 751.1459
2178.9417 | 752.1135
2179.9417 | 748.419
2180.9417 | 754.4292
2181.9417 | 748.1637
2182.9417 | 752.9067
2183.9417 | 754.3948
2184.9417 | 748.5856
2185.9417 | 736.7216
2186.9573 | 735.1816
2187.9417 | 732.4292
2188.9417 | 728.383
2189.9417 | 736.903
2190.9417 | 733.6984
2191.9417 | 729.9057
2192.9417 | 727.5858
2193.9417 | 723.4719
2194.9417 | 736.9772
2195.9417 | 728.7274
2196.9417 | 720.0514
2197.9417 | 724.9366
2198.9417 | 725.9203
2199.9417 | 732.8107
2200.9417 | 730.3848
2201.9417 | 733.6417
2202.9417 | 732.1742
2203.9417 | 735.5179
2204.9417 | 730.5717
2205.9417 | 723.9097
2206.9417 | 723.5696
2207.9417 | 724.2296
2208.9417 | 720.488
2209.9417 | 717.0374
2210.9417 | 711.8264
2211.9417 | 700.847
2212.9417 | 701.8822
2213.9417 | 704.4117
2214.9417 | 709.8537
2215.9417 | 701.5946
2216.9417 | 719.1843
2217.9417 | 717.6802
2218.9417 | 710.6849
2219.9417 | 713.5084
2220.9417 | 714.9361
2221.9417 | 715.5299
2222.9417 | 719.3184
2223.9417 | 721.1764
2224.9417 | 721.025
2225.9417 | 713.2098
2226.9417 | 709.4071
2227.9417 | 700.5646
2228.9417 | 701.1511
2229.9417 | 695.5187
2230.9417 | 695.3098
2231.9417 | 697.6352
2232.9417 | 698.635
2233.9417 | 691.9148
2234.9417 | 692.7391
2235.9417 | 685.9548
2236.9417 | 689.4927
2237.9417 | 704.6878
2238.9417 | 715.9823
2239.9417 | 719.4371
2240.9417 | 724.6969
2241.9417 | 729.0935
2242.9417 | 727.2273
2243.9417 | 730.7039
2244.9417 | 735.0766
2245.9417 | 747.6237
2246.9417 | 751.7923
2247.9417 | 755.7906
2248.9417 | 765.2914
2249.9417 | 766.7739
2250.9417 | 767.0162
2251.9417 | 763.0741
2252.9417 | 751.7538
2253.9417 | 748.7541
2254.9417 | 737.4917
2255.9417 | 730.0333
2256.9417 | 720.3719
2257.9417 | 716.5578
2258.9417 | 720.0811
2259.9417 | 711.6008
2260.9417 | 714.9069
2261.9417 | 714.0377
2262.9417 | 712.8876
2263.9573 | 716.7666
2264.9417 | 709.085
2265.9417 | 707.1704
2266.9417 | 706.324
2267.9417 | 706.0907
2268.9573 | 704.1263
2269.9417 | 709.8764
2270.9417 | 710.7971
2271.9417 | 702.65
2272.9417 | 703.9923
2273.9417 | 705.1085
2274.9417 | 710.3007
2275.9417 | 712.4147
2276.9417 | 712.4313
2277.9417 | 717.3795
2278.9417 | 720.3136
2279.9417 | 729.1834
2280.9417 | 734.8803
2281.9417 | 734.9781
2282.9417 | 721.6148
2283.9417 | 718.2819
2284.9417 | 716.0288
2285.9417 | 718.3591
2286.9417 | 715.8596
2287.9417 | 712.2698
2288.9417 | 705.7931
2289.9417 | 709.8504
2290.9417 | 706.808
2291.9417 | 707.6178
2292.9417 | 701.358
2293.9417 | 709.2697
2294.9417 | 717.215
2295.9417 | 719.463
2296.9417 | 724.7286
2297.9417 | 724.5028
2298.9417 | 733.2727
2299.9417 | 725.2946
2300.9417 | 721.4078
2301.9417 | 726.0475
2302.9417 | 731.7157
2303.9417 | 733.2385
2304.9417 | 731.6005
2305.9417 | 732.8737
2306.9417 | 726.7293
2307.9417 | 726.4385
2308.9417 | 730.3158
2309.9417 | 733.534
2310.9417 | 736.6013
2311.9417 | 737.2927
2312.9417 | 741.4882
2313.9417 | 736.3095
2314.9417 | 736.417
2315.9417 | 735.8924
2316.9417 | 731.8342
2317.9417 | 721.4598
2318.9417 | 716.0722
2319.9417 | 708.9431
2320.9417 | 710.5161
2321.9417 | 719.8795
2322.9417 | 717.4517
2323.9417 | 720.6923
2324.9417 | 724.0003
2325.9417 | 716.1302
2326.9417 | 714.5017
2327.9417 | 715.3964
2328.9417 | 718.9819
2329.9417 | 719.1032
2330.9417 | 723.4771
2331.9417 | 728.3203
2332.9417 | 730.282
2333.9417 | 733.9154
2334.9417 | 733.4104
2335.9417 | 728.9959
2336.9417 | 722.2044
2337.9417 | 720.5641
2338.9417 | 718.463
2339.9417 | 709.4226
2340.9417 | 707.5043
2341.9417 | 710.0413
2342.9417 | 702.4191
2343.9417 | 709.4399
2344.9417 | 705.2929
2345.9417 | 715.5342
2346.9417 | 716.8931
2347.9417 | 721.2166
2348.9417 | 720.8423
2349.9417 | 712.0343
2350.9417 | 710.191
2351.9417 | 711.7426
2352.9417 | 713.4096
2353.9417 | 713.5608
2354.9417 | 708.8445
2355.9417 | 709.4214
2356.9417 | 704.7548
2357.9417 | 705.9013
2358.9417 | 709.3602
2359.9417 | 702.7268
2360.9417 | 696.5402
2361.9417 | 694.3643
2362.9417 | 694.7571
2363.9417 | 690.8831
2364.9417 | 697.1283
2365.9417 | 694.7236
2366.9417 | 697.9157
2367.9417 | 693.8259
2368.9417 | 689.6697
2369.9417 | 693.0921
2370.9417 | 692.989
2371.9417 | 691.1327
2372.9417 | 684.6115
2373.9417 | 672.8952
2374.9417 | 670.0584
2375.9417 | 677.4998
2376.9417 | 677.8037
2377.9417 | 680.6747
2378.9417 | 678.9978
2379.9417 | 687.6043
2380.9417 | 696.2203
2381.9417 | 703.0337
2382.9417 | 709.616
2383.9417 | 701.122
2384.9417 | 705.5306
2385.9417 | 704.6871
2386.9417 | 707.0219
2387.9417 | 708.6593
2388.9573 | 704.7791
2389.9417 | 702.4526
2390.9417 | 699.677
2391.9417 | 698.4298
2392.9417 | 705.4712
2393.9417 | 709.7149
2394.9417 | 710.6113
2395.9417 | 716.8405
2396.9417 | 721.0256
2397.9417 | 726.4966
2398.9417 | 722.3718
2399.9417 | 715.7578
2400.9417 | 721.8855
2401.9417 | 712.2843
2402.9417 | 707.2205
2403.9417 | 698.1739
2404.9417 | 699.2908
2405.9417 | 701.7538
2406.9417 | 704.5614
2407.9417 | 704.1611
2408.9417 | 706.4166
2409.9417 | 696.6936
2410.9417 | 694.8777
2411.9417 | 692.374
2412.9417 | 696.2981
2413.9417 | 693.3416
2414.9417 | 690.064
2415.9417 | 688.4996
2416.9417 | 694.5539
2417.9417 | 699.9092
2418.9417 | 712.7735
2419.9417 | 715.143
2420.9417 | 722.616
2421.9573 | 734.705
2422.9417 | 734.5753
2423.9417 | 739.6994
2424.9417 | 745.112
2425.9573 | 733.3302
2426.9417 | 733.0538
2427.9573 | 732.9065
2428.9573 | 740.0165
2429.9573 | 746.1021
2430.9417 | 742.424
2431.9417 | 731.3616
2432.9573 | 732.8931
2433.9417 | 729.8948
2434.9573 | 718.4841
2435.9417 | 718.438
2436.9417 | 725.0505
2437.9417 | 721.8019
2438.9417 | 719.4588
2439.9417 | 712.9807
2440.9417 | 711.5322
2441.9417 | 710.1263
2442.9417 | 703.0772
2443.9417 | 702.7324
2444.9417 | 709.5376
2445.9417 | 715.7783
2446.9417 | 711.6971
2447.9417 | 710.4244
2448.9573 | 713.5648
2449.9417 | 715.1037
2450.9417 | 713.3854
2451.9417 | 714.7102
2452.9417 | 720.5916
2453.9417 | 716.56
2454.9417 | 715.5824
2455.9417 | 716.9819
2456.9417 | 720.2652
2457.9417 | 728.0109
2458.9417 | 735.3768
2459.9417 | 733.1196
2460.9417 | 731.3082
2461.9417 | 729.9796
2462.9417 | 720.4373
2463.9417 | 704.8459
2464.9417 | 700.6305
2465.9417 | 692.4089
2466.9417 | 695.3432
2467.9417 | 691.4492
2468.9417 | 699.5536
2469.9417 | 702.9378
2470.9417 | 705.0613
2471.9417 | 705.8353
2472.9417 | 706.1097
2473.9417 | 701.7213
2474.9417 | 698.55
2475.9417 | 696.6615
2476.9417 | 696.422
2477.9417 | 706.7825
2478.9417 | 709.226
2479.9417 | 709.4649
2480.9417 | 706.0959
2481.9417 | 705.5347
2482.9417 | 701.3482
2483.9417 | 702.8214
2484.9417 | 701.3013
2485.9417 | 698.1257
2486.9417 | 701.2574
2487.9417 | 700.0017
2488.9417 | 698.6022
2489.9417 | 696.6763
2490.9417 | 689.8557
2491.9417 | 686.9512
2492.9417 | 683.9061
2493.9417 | 686.0793
2494.9417 | 686.1925
2495.9417 | 680.1046
2496.9417 | 675.1945
2497.9417 | 675.7375
2498.9417 | 682.2325
2499.9417 | 676.1331
2500.9417 | 674.817
2501.9417 | 669.9314
2502.9417 | 680.6934
2503.9417 | 687.2908
2504.9417 | 692.497
2505.9417 | 694.2218
2506.9417 | 696.5936
2507.9417 | 694.3916
2508.9417 | 694.3003
2509.9417 | 700.6138
2510.9417 | 704.9371
2511.9417 | 704.929
2512.9417 | 705.4413
2513.9417 | 690.7518
2514.9417 | 684.571
2515.9417 | 677.0554
2516.9417 | 677.1002
2517.9417 | 676.1151
2518.9417 | 675.3574
2519.9417 | 680.6043
2520.9417 | 689.0116
2521.9417 | 690.9887
2522.9417 | 699.1161
2523.9417 | 699.6711
2524.9417 | 694.8538
2525.9417 | 699.3148
2526.9417 | 701.4786
2527.9417 | 702.6332
2528.9417 | 704.9105
2529.9417 | 703.8501
2530.9417 | 704.3695
2531.9417 | 703.4981
2532.9417 | 708.4043
2533.9417 | 701.6906
2534.9417 | 700.8961
2535.9417 | 696.9088
2536.9417 | 697.3879
2537.9417 | 697.481
2538.9417 | 706.3307
2539.9417 | 704.4623
2540.9417 | 710.4108
2541.9417 | 718.6833
2542.9417 | 722.1888
2543.9417 | 721.1812
2544.9417 | 715.1322
2545.9417 | 706.4081
2546.9417 | 709.3242
2547.9417 | 707.4621
2548.9417 | 714.2927
2549.9417 | 718.4609
2550.9417 | 714.0114
2551.9417 | 711.9272
2552.9417 | 712.0734
2553.9417 | 711.455
2554.9417 | 708.9258
2555.9417 | 703.2749
2556.9417 | 700.0451
2557.9417 | 706.547
2558.9417 | 704.1176
2559.9417 | 700.148
2560.9417 | 694.0491
2561.9417 | 685.673
2562.9417 | 684.3072
2563.9417 | 681.1348
2564.9417 | 678.8713
2565.9417 | 680.8982
2566.9417 | 682.7779
2567.9417 | 684.7837
2568.9417 | 689.4043
2569.9417 | 689.2163
2570.9417 | 692.153
2571.9417 | 689.0311
2572.9417 | 695.1889
2573.9417 | 701.191
2574.9417 | 708.2627
2575.9417 | 707.5014
2576.9417 | 711.7172
2577.9417 | 717.7626
2578.9417 | 720.9112
2579.9417 | 712.9753
2580.9417 | 703.7762
2581.9417 | 703.704
2582.9417 | 697.8817
2583.9417 | 692.1865
2584.9417 | 686.5364
2585.9417 | 686.1443
2586.9417 | 685.9012
2587.9417 | 687.3921
2588.9417 | 681.3633
2589.9417 | 688.5085
2590.9417 | 682.7445
2591.9417 | 682.8227
2592.9417 | 681.2225
2593.9417 | 681.8417
2594.9417 | 682.7372
2595.9417 | 681.3554
2596.9417 | 680.8943
2597.9417 | 681.0743
2598.9417 | 685.6229
2599.9417 | 688.4544
2600.9417 | 693.8697
2601.9417 | 698.0653
2602.9417 | 705.6386
2603.9417 | 704.017
2604.9417 | 699.9042
2605.9417 | 697.8083
2606.9417 | 693.8394
2607.9417 | 683.2062
2608.9417 | 674.8864
2609.9417 | 676.1556
2610.9417 | 678.4348
2611.9417 | 676.9133
2612.9417 | 673.9006
2613.9417 | 680.8219
2614.9417 | 681.2907
2615.9417 | 677.493
2616.9417 | 682.8855
2617.9417 | 683.1537
2618.9417 | 683.5156
2619.9417 | 682.6241
2620.9417 | 682.9513
2621.9417 | 683.3195
2622.9417 | 673.8256
2623.9417 | 677.6336
2624.9417 | 683.5024
2625.9417 | 680.4568
2626.9417 | 679.3332
2627.9417 | 672.8952
2628.9417 | 676.2368
2629.9417 | 680.9107
2630.9417 | 684.9845
2631.9417 | 684.1939
2632.9417 | 684.3217
2633.9417 | 691.6996
2634.9417 | 692.2698
2635.9417 | 698.3147
2636.9417 | 709.179
2637.9417 | 720.9178
2638.9417 | 722.0668
2639.9417 | 716.4341
2640.9417 | 713.6537
2641.9417 | 713.4158
2642.9417 | 717.3905
2643.9417 | 716.9696
2644.9417 | 719.7164
2645.9417 | 716.2709
2646.9417 | 711.5474
2647.9417 | 712.3788
2648.9417 | 713.1561
2649.9417 | 704.931
2650.9417 | 698.2986
2651.9417 | 690.5009
2652.9417 | 683.7313
2653.9417 | 680.6424
2654.9417 | 681.3538
2655.9417 | 672.9186
2656.9417 | 666.1211
2657.9417 | 662.8434
2658.9417 | 665.1031
2659.9417 | 670.5094
2660.9417 | 665.5085
2661.9417 | 666.6509
2662.9417 | 669.7021
2663.9417 | 673.7387
2664.9417 | 681.6255
2665.9417 | 677.1809
2666.9417 | 678.72
2667.9417 | 682.0289
2668.9417 | 685.1876
2669.9417 | 691.5775
2670.9417 | 696.6512
2671.9417 | 703.0248
2672.9417 | 704.3499
2673.9417 | 704.8097
2674.9417 | 699.6699
2675.9417 | 699.8646
2676.9417 | 693.3129
2677.9417 | 691.119
2678.9417 | 694.2988
2679.9417 | 689.565
2680.9417 | 691.0789
2681.9417 | 691.5269
2682.9417 | 690.5012
2683.9417 | 687.5455
2684.9417 | 688.5225
2685.9417 | 681.5823
2686.9417 | 681.3335
2687.9417 | 689.411
2688.9417 | 689.5902
2689.9417 | 677.7259
2690.9417 | 664.6964
2691.9417 | 665.0033
2692.9417 | 670.9871
2693.9417 | 669.3973
2694.9417 | 667.8757
2695.9417 | 671.4059
2696.9417 | 672.537
2697.9417 | 681.6831
2698.9417 | 685.7708
2699.9417 | 685.6042
2700.9417 | 687.8634
2701.9417 | 689.3911
2702.9417 | 694.2942
2703.9417 | 696.1434
2704.9417 | 698.5471
2705.9417 | 693.6911
2706.9417 | 694.1792
2707.9417 | 689.3745
2708.9417 | 686.616
2709.9417 | 687.9843
2710.9417 | 687.4863
2711.9417 | 694.6662
2712.9417 | 697.343
2713.9417 | 703.3065
2714.9417 | 703.3376
2715.9417 | 709.1446
2716.9417 | 717.5895
2717.9417 | 722.1868
2718.9417 | 720.7192
2719.9417 | 715.9619
2720.9417 | 708.7315
2721.9417 | 704.4957
2722.9417 | 699.4091
2723.9417 | 696.7217
2724.9417 | 695.3934
2725.9417 | 699.7933
2726.9417 | 699.3209
2727.9417 | 701.2307
2728.9417 | 699.2639
2729.9417 | 697.8679
2730.9417 | 692.2919
2731.9417 | 689.6948
2732.9417 | 684.2706
2733.9417 | 685.9878
2734.9417 | 691.111
2735.9417 | 695.0375
2736.9417 | 694.6713
2737.9417 | 692.4085
2738.9417 | 690.0578
2739.9417 | 691.7155
2740.9417 | 691.1711
2741.9417 | 685.5352
2742.9417 | 691.5216
2743.9417 | 695.0389
2744.9417 | 699.7704
2745.9417 | 700.8841
2746.9417 | 699.974
2747.9417 | 698.3088
2748.9417 | 693.2806
2749.9417 | 696.3916
2750.9417 | 704.0542
2751.9417 | 707.0289
2752.9417 | 709.5649
2753.9417 | 721.7779
2754.9417 | 718.2596
2755.9417 | 719.1993
2756.9417 | 724.9824
2757.9417 | 727.1048
2758.9417 | 730.7897
2759.9417 | 724.6208
2760.9417 | 721.4334
2761.9417 | 714.054
2762.9417 | 716.2322
2763.9417 | 715.0746
2764.9417 | 711.1636
2765.9417 | 705.2455
2766.9417 | 710.8879
2767.9417 | 719.0466
2768.9417 | 716.1167
2769.9417 | 705.2988
2770.9417 | 705.3819
2771.9417 | 707.0832
2772.9417 | 708.8384
2773.9417 | 709.1115
2774.9417 | 708.5001
2775.9417 | 705.1702
2776.9417 | 698.0697
2777.9417 | 694.2645
2778.9417 | 690.0208
2779.9417 | 678.5336
2780.9417 | 669.9876
2781.9417 | 663.7374
2782.9417 | 666.3167
2783.9417 | 672.5278
2784.9417 | 680.3036
2785.9417 | 687.9909
2786.9417 | 693.6742
2787.9417 | 692.2832
2788.9417 | 698.7557
2789.9417 | 707.9681
2790.9417 | 715.191
2791.9417 | 719.2514
2792.9417 | 719.761
2793.9417 | 718.7679
2794.9417 | 708.0999
2795.9417 | 701.4143
2796.9417 | 697.0131
2797.9417 | 693.7141
2798.9417 | 694.464
2799.9417 | 691.3391
2800.9417 | 688.4083
2801.9417 | 688.9492
2802.9417 | 695.6791
2803.9417 | 700.6152
2804.9417 | 700.0859
2805.9417 | 698.1971
2806.9417 | 697.8247
2807.9417 | 698.523
2808.9417 | 700.1558
2809.9417 | 700.9142
2810.9417 | 701.3524
2811.9417 | 694.8062
2812.9417 | 688.1031
2813.9417 | 685.0939
2814.9417 | 682.1759
2815.9417 | 685.0721
2816.9417 | 686.4097
2817.9417 | 678.1492
2818.9417 | 680.7644
2819.9417 | 679.1095
2820.9417 | 674.9058
2821.9417 | 674.9079
2822.9417 | 677.0909
2823.9417 | 686.4978
2824.9417 | 693.5397
2825.9417 | 702.9805
2826.9417 | 703.8695
2827.9417 | 707.4677
2828.9417 | 713.0842
2829.9417 | 716.8898
2830.9417 | 712.0698
2831.9417 | 709.6905
2832.9417 | 708.0847
2833.9417 | 710.6921
2834.9417 | 710.5727
2835.9417 | 709.7758
2836.9417 | 702.7404
2837.9417 | 694.2465
2838.9417 | 690.3054
2839.9417 | 686.7017
2840.9417 | 683.1586
2841.9417 | 681.0825
2842.9417 | 679.8773
2843.9417 | 680.5443
2844.9417 | 682.8295
2845.9417 | 684.0192
2846.9417 | 682.5357
2847.9417 | 675.5581
2848.9417 | 666.9069
2849.9417 | 661.5275
2850.9417 | 656.9753
2851.9417 | 649.7392
2852.9417 | 645.2593
2853.9417 | 647.5231
2854.9417 | 648.5719
2855.9417 | 654.3046
2856.9417 | 653.5528
2857.9417 | 649.4319
2858.9417 | 646.454
2859.9417 | 649.507
2860.9417 | 647.9813
2861.9417 | 642.9593
2862.9417 | 643.4804
2863.9417 | 644.4047
2864.9417 | 652.8756
2865.9417 | 662.8647
2866.9417 | 677.773
2867.9417 | 678.5836
2868.9417 | 670.9018
2869.9417 | 665.6742
2870.9417 | 656.8184
2871.9417 | 652.4879
2872.9417 | 647.3892
2873.9417 | 646.156
2874.9417 | 657.7446
2875.9417 | 669.012
2876.9417 | 675.1438
2877.9417 | 680.8782
2878.9417 | 682.7472
2879.9417 | 684.8255
2880.9417 | 686.4707
2881.9417 | 692.3435
2882.9417 | 693.1034
2883.9417 | 683.2714
2884.9417 | 678.6052
2885.9417 | 670.4496
2886.9417 | 665.7739
2887.9417 | 668.8094
2888.9417 | 670.5775
2889.9417 | 669.4279
2890.9417 | 673.7566
2891.9417 | 672.836
2892.9417 | 674.7598
2893.9417 | 675.5356
2894.9417 | 674.4983
2895.9417 | 680.8821
2896.9417 | 688.524
2897.9417 | 681.4637
2898.9417 | 684.9704
2899.9417 | 677.8758
2900.9417 | 673.9403
2901.9417 | 674.3714
2902.9417 | 672.0631
2903.9417 | 664.7797
2904.9417 | 662.665
2905.9417 | 666.1802
2906.9417 | 669.3698
2907.9417 | 665.01
2908.9417 | 668.17
2909.9417 | 674.4249
2910.9417 | 679.8011
2911.9417 | 683.9988
2912.9417 | 681.2224
2913.9729 | 678.9839
2914.9417 | 677.32
2915.9417 | 680.0022
2916.9417 | 681.411
2917.9417 | 675.9453
2918.9417 | 674.4843
2919.9417 | 673.0434
2920.9417 | 673.0452
2921.9417 | 672.4137
2922.9417 | 676.8814
2923.9417 | 675.2006
2924.9417 | 669.7215
2925.9417 | 666.5162
2926.9417 | 668.9107
2927.9417 | 673.7328
2928.9417 | 679.4613
2929.9417 | 684.5403
2930.9417 | 689.6313
2931.9417 | 690.1682
2932.9417 | 686.4616
2933.9417 | 681.9613
2934.9417 | 680.544
2935.9417 | 679.1797
2936.9417 | 676.1223
2937.9417 | 677.8703
2938.9417 | 675.3666
2939.9417 | 673.7408
2940.9417 | 663.8721
2941.9417 | 662.0816
2942.9417 | 659.3127
2943.9417 | 655.9064
2944.9417 | 656.9138
2945.9417 | 656.8893
2946.9417 | 655.3313
2947.9417 | 657.1921
2948.9417 | 657.0626
2949.9417 | 654.8662
2950.9573 | 651.0025
2951.9417 | 654.9083
2952.9417 | 658.4846
2953.9417 | 663.7294
2954.9417 | 661.7527
2955.9417 | 662.2025
2956.9417 | 657.8408
2957.9417 | 650.9512
2958.9417 | 652.1283
2959.9417 | 654.3015
2960.9417 | 657.6301
2961.9417 | 657.3183
2962.9417 | 659.2143
2963.9417 | 659.5033
2964.9417 | 656.6959
2965.9417 | 655.9835
2966.9417 | 655.5334
2967.9417 | 657.5762
2968.9417 | 659.0192
2969.9417 | 658.0179
2970.9417 | 656.1915
2971.9417 | 654.3431
2972.9417 | 652.8978
2973.9417 | 650.9652
2974.9417 | 648.1059
2975.9417 | 651.1641
2976.9417 | 650.1502
2977.9417 | 650.9613
2978.9417 | 647.3962
2979.9417 | 645.4395
2980.9573 | 643.8597
2981.9417 | 646.9305
2982.9417 | 645.8122
2983.9417 | 646.8782
2984.9417 | 643.7161
2985.9417 | 641.8944
2986.9417 | 648.493
2987.9417 | 651.7551
2988.9417 | 652.3087
2989.9417 | 654.3861
2990.9417 | 652.6891
2991.9417 | 650.395
2992.9417 | 647.8405
2993.9417 | 646.7722
2994.9417 | 647.4983
2995.9417 | 643.6284
2996.9417 | 639.7184
2997.9417 | 642.8532
2998.9417 | 642.679
2999.9417 | 641.5056
3000.9417 | 641.4485
3001.9417 | 641.6588
3002.9417 | 632.6479
3003.9417 | 630.8794
3004.9417 | 628.8374
3005.9417 | 628.0357
3006.9417 | 631.4668
3007.9417 | 635.5408
3008.9417 | 637.333
3009.9417 | 638.4213
3010.9417 | 641.7266
3011.9417 | 645.7715
3012.9417 | 650.6289
3013.9417 | 651.5482
3014.9417 | 650.648
3015.9417 | 650.0827
3016.9417 | 649.8416
3017.9417 | 652.1174
3018.9417 | 655.4287
3019.9417 | 660.7143
3020.9417 | 666.9046
3021.9417 | 668.1184
3022.9417 | 665.8201
3023.9417 | 666.7755
3024.9417 | 660.399
3025.9417 | 663.2698
3026.9417 | 665.1846
3027.9417 | 664.2093
3028.9417 | 666.9028
3029.9417 | 666.8989
3030.9417 | 665.9233
3031.9417 | 668.2415
3032.9417 | 667.8663
3033.9417 | 662.9906
3034.9417 | 657.8045
3035.9417 | 659.8761
3036.9417 | 662.2837
3037.9417 | 661.8222
3038.9417 | 667.5227
3039.9417 | 674.7666
3040.9417 | 676.2053
3041.9417 | 675.4091
3042.9417 | 672.7989
3043.9417 | 673.396
3044.9417 | 676.2701
3045.9417 | 675.8061
3046.9417 | 673.9034
3047.9417 | 673.7993
3048.9417 | 676.2665
3049.9417 | 679.4499
3050.9417 | 682.34
3051.9417 | 678.1071
3052.9417 | 677.5216
3053.9417 | 677.5235
3054.9417 | 678.1088
3055.9417 | 682.3259
3056.9417 | 681.9112
3057.9417 | 683.3847
3058.9417 | 683.8907
3059.9417 | 680.684
3060.9417 | 674.8758
3061.9417 | 672.0848
3062.9417 | 668.9701
3063.9417 | 673.2791
3064.9417 | 672.4716
3065.9417 | 670.3172
3066.9417 | 667.05
3067.9417 | 665.4337
3068.9417 | 665.1081
3069.9417 | 663.1495
3070.9417 | 664.6321
3071.9417 | 665.7095
3072.9417 | 670.4317
3073.9417 | 667.3888
3074.9417 | 663.9826
3075.9417 | 661.9961
3076.9417 | 661.1637
3077.9417 | 661.0356
3078.9417 | 664.0645
3079.9417 | 665.7602
3080.9417 | 664.5876
3081.9417 | 660.1367
3082.9417 | 665.4086
3083.9417 | 662.8385
3084.9417 | 659.6127
3085.9417 | 657.9106
3086.9417 | 654.5499
3087.9417 | 646.7082
3088.9417 | 648.5411
3089.9417 | 648.4421
3090.9417 | 650.1289
3091.9417 | 650.9279
3092.9417 | 659.7749
3093.9417 | 663.6345
3094.9417 | 665.6085
3095.9417 | 672.2646
3096.9417 | 672.8292
3097.9417 | 672.0877
3098.9417 | 673.8241
3099.9417 | 678.3912
3100.9417 | 678.0129
3101.9417 | 675.4048
3102.9417 | 671.7793
3103.9417 | 667.3841
3104.9417 | 664.433
3105.9417 | 662.1755
3106.9417 | 663.401
3107.9417 | 668.7464
3108.9417 | 670.5285
3109.9417 | 670.1109
3110.9417 | 671.0042
3111.9417 | 668.7353
3112.9417 | 665.4847
3113.9417 | 663.141
3114.9417 | 661.4609
3115.9417 | 660.8197
3116.9417 | 657.2527
3117.9417 | 652.3667
3118.9417 | 648.1265
3119.9417 | 645.8394
3120.9417 | 646.0237
3121.9417 | 648.5133
3122.9417 | 645.5146
3123.9417 | 642.6897
3124.9417 | 644.0258
3125.9417 | 643.7789
3126.9417 | 643.6637
3127.9417 | 642.3122
3128.9417 | 641.3623
3129.9417 | 642.1704
3130.9417 | 644.3863
3131.9417 | 641.8067
3132.9417 | 642.2117
3133.9417 | 642.13
3134.9417 | 645.8893
3135.9417 | 648.3665
3136.9417 | 645.7855
3137.9417 | 646.4328
3138.9417 | 646.1953
3139.9417 | 649.8711
3140.9417 | 650.0069
3141.9417 | 651.4788
3142.9417 | 657.7868
3143.9417 | 656.5545
3144.9417 | 656.6675
3145.9417 | 653.9874
3146.9417 | 650.2082
3147.9417 | 646.9152
3148.9417 | 647.3302
3149.9417 | 642.3924
3150.9417 | 635.0606
3151.9417 | 636.2438
3152.9417 | 635.8269
3153.9417 | 634.8624
3154.9417 | 632.8782
3155.9417 | 629.4786
3156.9417 | 631.0295
3157.9417 | 634.5848
3158.9417 | 634.9158
3159.9417 | 638.5455
3160.9417 | 641.8942
3161.9417 | 640.6823
3162.9417 | 640.2859
3163.9417 | 643.3486
3164.9417 | 644.1745
3165.9417 | 647.3779
3166.9417 | 650.4676
3167.9417 | 651.6532
3168.9417 | 652.2379
3169.9417 | 654.6061
3170.9417 | 657.6865
3171.9417 | 660.1782
3172.9417 | 658.7816
3173.9417 | 658.805
3174.9417 | 663.1909
3175.9417 | 664.0466
3176.9417 | 666.9111
3177.9417 | 667.8868
3178.9417 | 669.1473
3179.9417 | 672.9677
3180.9417 | 666.0059
3181.9417 | 663.2271
3182.9417 | 663.2304
3183.9417 | 659.724
3184.9417 | 658.851
3185.9417 | 656.3375
3186.9417 | 655.4421
3187.9417 | 656.9637
3188.9417 | 656.554
3189.9417 | 653.5468
3190.9417 | 650.0775
3191.9417 | 650.267
3192.9417 | 651.7409
3193.9417 | 650.4668
3194.9417 | 646.5664
3195.9417 | 651.8364
3196.9417 | 652.6888
3197.9417 | 652.7693
3198.9417 | 654.7334
3199.9417 | 656.6536
3200.9417 | 655.5594
3201.9417 | 654.8374
3202.9417 | 654.0023
3203.9417 | 653.0895
3204.9417 | 653.4027
3205.9417 | 652.6836
3206.9417 | 651.121
3207.9417 | 650.0709
3208.9417 | 648.4955
3209.9417 | 648.7428
3210.9417 | 650.051
3211.9417 | 646.8874
3212.9417 | 644.0895
3213.9417 | 647.9584
3214.9417 | 649.0563
3215.9417 | 652.8518
3216.9417 | 654.129
3217.9417 | 654.9065
3218.9417 | 654.8854
3219.9417 | 651.3031
3220.9417 | 646.9032
3221.9417 | 641.1454
3222.9417 | 635.0246
3223.9417 | 632.9116
3224.9417 | 627.1352
3225.9417 | 625.8048
3226.9417 | 625.0931
3227.9417 | 625.2671
3228.9417 | 628.6815
3229.9417 | 631.625
3230.9417 | 634.5263
3231.9417 | 631.9329
3232.9417 | 629.1707
3233.9417 | 625.757
3234.9417 | 624.9655
3235.9417 | 627.7924
3236.9417 | 629.9414
3237.9417 | 628.243
3238.9417 | 625.6989
3239.9417 | 626.6782
3240.9417 | 631.3955
3241.9417 | 632.3429
3242.9417 | 631.4247
3243.9417 | 634.922
3244.9417 | 640.9754
3245.9417 | 646.5658
3246.9417 | 649.756
3247.9417 | 646.2297
3248.9417 | 642.5876
3249.9417 | 638.9159
3250.9417 | 637.4235
3251.9417 | 636.004
3252.9417 | 639.0388
3253.9417 | 640.824
3254.9417 | 641.9402
3255.9417 | 644.1271
3256.9417 | 646.3362
3257.9417 | 647.7046
3258.9417 | 649.2876
3259.9417 | 654.1527
3260.9417 | 655.0154
3261.9417 | 651.9294
3262.9417 | 649.2584
3263.9417 | 648.5033
3264.9417 | 648.8349
3265.9417 | 646.9873
3266.9417 | 646.3478
3267.9417 | 645.0007
3268.9417 | 645.9311
3269.9417 | 645.3894
3270.9417 | 648.9745
3271.9417 | 650.7823
3272.9417 | 653.817
3273.9417 | 650.9519
3274.9417 | 647.387
3275.9417 | 640.5093
3276.9417 | 638.4408
3277.9417 | 640.3716
3278.9417 | 638.6875
3279.9417 | 637.1374
3280.9417 | 636.373
3281.9417 | 633.7954
3282.9417 | 630.8116
3283.9417 | 626.903
3284.9417 | 627.8935
3285.9417 | 629.0735
3286.9417 | 630.3226
3287.9417 | 629.7643
3288.9417 | 631.4445
3289.9417 | 632.1354
3290.9417 | 627.8969
3291.9417 | 628.3061
3292.9417 | 628.0874
3293.9417 | 626.5691
3294.9417 | 627.0585
3295.9417 | 622.8155
3296.9417 | 625.6693
3297.9417 | 631.6078
3298.9417 | 637.9919
3299.9417 | 638.1343
3300.9417 | 636.1816
3301.9417 | 638.1421
3302.9417 | 634.6756
3303.9417 | 632.0778
3304.9417 | 626.7763
3305.9417 | 623.6819
3306.9417 | 625.2451
3307.9417 | 622.48
3308.9417 | 619.9461
3309.9417 | 622.4635
3310.9417 | 624.0013
3311.9417 | 622.0428
3312.9417 | 627.646
3313.9417 | 626.927
3314.9417 | 626.7725
3315.9417 | 632.0605
3316.9417 | 634.7474
3317.9417 | 637.8891
3318.9417 | 640.3032
3319.9417 | 640.0662
3320.9417 | 636.4898
3321.9417 | 632.2875
3322.9417 | 635.3601
3323.9417 | 639.9074
3324.9417 | 643.1752
3325.9417 | 646.3614
3326.9417 | 642.6876
3327.9417 | 638.7135
3328.9417 | 636.9936
3329.9417 | 636.1368
3330.9417 | 636.4834
3331.9417 | 635.121
3332.9417 | 635.8121
3333.9417 | 636.6327
3334.9417 | 633.3245
3335.9417 | 628.2185
3336.9417 | 624.8231
3337.9417 | 621.2239
3338.9417 | 617.6328
3339.9417 | 615.4792
3340.9417 | 614.2445
3341.9417 | 609.3878
3342.9417 | 610.6402
3343.9417 | 610.1245
3344.9417 | 610.7838
3345.9417 | 611.8236
3346.9417 | 615.4079
3347.9417 | 616.1408
3348.9417 | 619.5609
3349.9417 | 620.2799
3350.9417 | 620.5547
3351.9417 | 623.8683
3352.9417 | 625.3631
3353.9417 | 623.7362
3354.9417 | 627.4195
3355.9417 | 634.8741
3356.9417 | 637.8234
3357.9417 | 637.6642
3358.9417 | 640.1497
3359.9417 | 641.4765
3360.9417 | 642.4447
3361.9417 | 638.5642
3362.9417 | 634.6566
3363.9417 | 637.5826
3364.9417 | 638.6809
3365.9417 | 639.6192
3366.9417 | 638.0384
3367.9417 | 636.7702
3368.9417 | 635.4469
3369.9417 | 637.7937
3370.9417 | 638.5532
3371.9417 | 634.4326
3372.9417 | 634.9446
3373.9417 | 636.2937
3374.9417 | 636.9986
3375.9417 | 633.2743
3376.9417 | 628.0158
3377.9417 | 624.622
3378.9417 | 623.5655
3379.9417 | 627.659
3380.9417 | 629.3916
3381.9417 | 626.6467
3382.9417 | 623.5724
3383.9417 | 622.7546
3384.9417 | 624.9104
3385.9417 | 623.2699
3386.9417 | 620.9805
3387.9417 | 616.7848
3388.9417 | 616.2774
3389.9417 | 613.4167
3390.9417 | 610.6402
3391.9417 | 608.6313
3392.9417 | 609.1488
3393.9417 | 613.8379
3394.9417 | 615.206
3395.9417 | 614.1826
3396.9417 | 611.6525
3397.9417 | 611.8028
3398.9417 | 616.1267
3399.9417 | 615.4851
3400.9417 | 613.8442
3401.9417 | 615.8543
3402.9417 | 620.4736
3403.9417 | 623.8636
3404.9417 | 620.2471
3405.9417 | 614.8591
3406.9417 | 615.9682
3407.9417 | 616.5017
3408.9417 | 617.2796
3409.9417 | 617.9842
3410.9417 | 617.0619
3411.9417 | 615.615
3412.9417 | 618.1416
3413.9417 | 613.6587
3414.9417 | 614.4596
3415.9417 | 616.4445
3416.9417 | 616.073
3417.9417 | 617.2392
3418.9417 | 621.4709
3419.9417 | 623.524
3420.9417 | 622.3322
3421.9417 | 623.6474
3422.9417 | 622.6232
3423.9417 | 624.2057
3424.9417 | 629.5664
3425.9417 | 630.8481
3426.9417 | 633.9739
3427.9417 | 633.3699
3428.9417 | 636.2638
3429.9417 | 640.9729
3430.9417 | 642.4854
3431.9417 | 639.0552
3432.9417 | 634.2627
3433.9417 | 628.7693
3434.9417 | 623.1745
3435.9417 | 623.5275
3436.9417 | 624.1182
3437.9417 | 621.9877
3438.9417 | 617.7534
3439.9417 | 613.0317
3440.9417 | 611.0641
3441.9417 | 613.7102
3442.9417 | 615.7643
3443.9417 | 612.6949
3444.9417 | 610.6006
3445.9417 | 603.7198
3446.9417 | 597.0658
3447.9417 | 595.4363
3448.9417 | 595.5564
3449.9417 | 596.2799
3450.9417 | 595.6854
3451.9417 | 596.5328
3452.9417 | 596.6173
3453.9417 | 597.33
3454.9417 | 600.6982
3455.9417 | 604.9156
3456.9417 | 605.2544
3457.9417 | 608.5998
3458.9417 | 611.9526
3459.9417 | 612.4922
3460.9417 | 613.6843
3461.9417 | 615.2425
3462.9417 | 616.2887
3463.9417 | 619.5401
3464.9417 | 621.1954
3465.9417 | 622.1945
3466.9417 | 617.6068
3467.9417 | 613.0891
3468.9417 | 610.9232
3469.9417 | 609.8953
3470.9417 | 607.2864
3471.9417 | 606.5639
3472.9417 | 607.9587
3473.9417 | 607.404
3474.9417 | 609.1055
3475.9417 | 610.9036
3476.9417 | 610.8437
3477.9417 | 610.3473
3478.9417 | 605.9544
3479.9417 | 606.4333
3480.9417 | 605.6957
3481.9417 | 605.7271
3482.9417 | 602.978
3483.9417 | 601.285
3484.9417 | 601.6924
3485.9417 | 601.55
3486.9417 | 603.7788
3487.9417 | 608.3083
3488.9417 | 612.3661
3489.9417 | 609.8092
3490.9417 | 606.4417
3491.9417 | 608.8287
3492.9417 | 616.9217
3493.9417 | 623.2532
3494.9417 | 625.96
3495.9417 | 628.5519
3496.9417 | 627.623
3497.9417 | 628.1798
3498.9417 | 626.1315
3499.9417 | 623.9804
3500.9417 | 625.6497
3501.9417 | 624.9631
3502.9417 | 622.1085
3503.9417 | 617.741
3504.9417 | 613.273
3505.9417 | 609.9276
3506.9417 | 606.8877
3507.9417 | 606.7051
3508.9417 | 606.5758
3509.9417 | 607.2511
3510.9417 | 608.9606
3511.9417 | 611.2541
3512.9417 | 607.259
3513.9573 | 604.4163
3514.9417 | 603.0982
3515.9417 | 601.434
3516.9417 | 600.412
3517.9417 | 599.3567
3518.9417 | 598.9251
3519.9417 | 599.6235
3520.9417 | 600.6725
3521.9417 | 600.9098
3522.9417 | 599.0787
3523.9417 | 601.7014
3524.9417 | 606.3402
3525.9417 | 613.1704
3526.9417 | 614.6892
3527.9417 | 615.3579
3528.9417 | 614.5659
3529.9417 | 613.8842
3530.9417 | 614.2465
3531.9417 | 613.5886
3532.9417 | 613.7893
3533.9417 | 612.8994
3534.9417 | 610.3664
3535.9417 | 607.9276
3536.9417 | 606.6965
3537.9417 | 605.0589
3538.9417 | 600.9669
3539.9417 | 598.8885
3540.9417 | 597.0466
3541.9417 | 597.8564
3542.9417 | 599.9539
3543.9417 | 603.7672
3544.9417 | 607.0337
3545.9417 | 609.0616
3546.9417 | 608.9923
3547.9417 | 607.7559
3548.9417 | 609.2931
3549.9417 | 608.9969
3550.9417 | 605.8563
3551.9417 | 601.3254
3552.9417 | 596.2191
3553.9417 | 592.4995
3554.9417 | 590.3169
3555.9417 | 587.9884
3556.9417 | 586.6359
3557.9417 | 584.5323
3558.9417 | 583.4788
3559.9417 | 585.1491
3560.9417 | 589.3999
3561.9417 | 589.7409
3562.9417 | 591.1494
3563.9417 | 591.7674
3564.9417 | 593.3869
3565.9417 | 596.0047
3566.9417 | 595.8561
3567.9417 | 594.192
3568.9417 | 591.3885
3569.9417 | 593.0973
3570.9417 | 595.2479
3571.9417 | 601.866
3572.9417 | 608.1064
3573.9417 | 608.6948
3574.9417 | 608.059
3575.9417 | 609.9883
3576.9417 | 610.6181
3577.9417 | 605.9408
3578.9417 | 601.1984
3579.9417 | 600.3734
3580.9417 | 600.5871
3581.9417 | 598.7489
3582.9417 | 599.6865
3583.9417 | 599.5019
3584.9417 | 598.529
3585.9417 | 597.3295
3586.9417 | 596.234
3587.9417 | 594.5948
3588.9417 | 596.521
3589.9417 | 598.9229
3590.9417 | 598.8713
3591.9417 | 598.3785
3592.9417 | 596.807
3593.9417 | 594.4293
3594.9417 | 594.3539
3595.9417 | 594.5055
3596.9417 | 596.5874
3597.9417 | 597.5515
3598.9417 | 596.7389
3599.9417 | 594.9843
3600.9417 | 593.8196
3601.9417 | 595.0065
3602.9417 | 598.1624
3603.9417 | 598.3514
3604.9417 | 595.8857
3605.9417 | 592.3516
3606.9417 | 592.9904
3607.9417 | 592.186
3608.9417 | 590.6049
3609.9417 | 589.7835
3610.9417 | 589.4599
3611.9417 | 593.3283
3612.9417 | 597.7888
3613.9417 | 597.9666
3614.9417 | 596.8887
3615.9417 | 593.3026
3616.9417 | 589.9286
3617.9417 | 590.2348
3618.9417 | 592.4343
3619.9417 | 594.455
3620.9417 | 592.7518
3621.9417 | 589.5582
3622.9417 | 589.9437
3623.9417 | 589.0903
3624.9417 | 591.3425
3625.9417 | 589.8192
3626.9417 | 589.3624
3627.9417 | 586.4041
3628.9417 | 587.9546
3629.9417 | 591.3153
3630.9417 | 590.5372
3631.9417 | 590.5718
3632.9417 | 594.7812
3633.9573 | 600.5799
3634.9417 | 603.459
3635.9417 | 608.4585
3636.9417 | 609.375
3637.9573 | 609.759
3638.9417 | 612.9063
3639.9417 | 610.9668
3640.9417 | 614.5788
3641.9417 | 616.8881
3642.9417 | 614.528
3643.9417 | 612.1302
3644.9417 | 607.9012
3645.9417 | 608.1935
3646.9417 | 609.2922
3647.9417 | 607.7151
3648.9417 | 606.7978
3649.9417 | 606.3592
3650.9417 | 606.8243
3651.9417 | 607.55
3652.9417 | 604.4092
3653.9417 | 599.9419
3654.9417 | 595.3196
3655.9417 | 593.9557
3656.9417 | 593.8275
3657.9417 | 592.7306
3658.9417 | 592.9787
3659.9417 | 593.3893
3660.9417 | 592.4946
3661.9417 | 592.0418
3662.9417 | 594.0983
3663.9417 | 595.6233
3664.9417 | 594.749
3665.9417 | 597.2615
3666.9417 | 598.0544
3667.9417 | 599.8978
3668.9417 | 602.2788
3669.9417 | 604.2131
3670.9417 | 608.1118
3671.9417 | 607.5492
3672.9417 | 606.6448
3673.9417 | 609.404
3674.9417 | 611.085
3675.9417 | 608.0768
3676.9417 | 611.5545
3677.9417 | 616.682
3678.9417 | 614.6948
3679.9417 | 610.7533
3680.9417 | 603.8979
3681.9417 | 601.5049
3682.9417 | 600.2525
3683.9417 | 598.429
3684.9417 | 596.9439
3685.9417 | 597.5326
3686.9417 | 595.692
3687.9417 | 593.1292
3688.9417 | 591.38
3689.9417 | 593.8787
3690.9417 | 598.3848
3691.9417 | 599.5263
3692.9417 | 599.1252
3693.9417 | 598.4692
3694.9417 | 599.9175
3695.9417 | 600.0874
3696.9417 | 599.7307
3697.9417 | 598.4869
3698.9417 | 596.4906
3699.9417 | 597.7266
3700.9417 | 598.7171
3701.9417 | 597.5942
3702.9417 | 596.8359
3703.9417 | 597.2152
3704.9417 | 602.7822
3705.9417 | 603.2899
3706.9417 | 600.5074
3707.9417 | 597.594
3708.9417 | 598.1999
3709.9417 | 599.5592
3710.9417 | 600.362
3711.9417 | 603.6557
3712.9417 | 605.9761
3713.9417 | 610.4702
3714.9417 | 613.1338
3715.9417 | 614.5727
3716.9417 | 616.959
3717.9417 | 617.0618
3718.9417 | 616.4055
3719.9417 | 613.994
3720.9417 | 609.0075
3721.9417 | 606.804
3722.9417 | 603.5064
3723.9417 | 602.8819
3724.9417 | 599.9468
3725.9417 | 597.156
3726.9417 | 596.0895
3727.9417 | 594.103
3728.9417 | 591.0485
3729.9417 | 587.4702
3730.9417 | 586.1474
3731.9417 | 584.8313
3732.9417 | 583.8672
3733.9417 | 583.1096
3734.9417 | 583.2939
3735.9417 | 585.1217
3736.9417 | 589.0349
3737.9417 | 592.84
3738.9417 | 595.7578
3739.9417 | 597.4736
3740.9417 | 597.1148
3741.9417 | 595.9988
3742.9417 | 593.6695
3743.9417 | 594.9394
3744.9417 | 597.9508
3745.9417 | 599.8548
3746.9417 | 601.6011
3747.9417 | 601.1702
3748.9417 | 601.1978
3749.9417 | 604.4415
3750.9417 | 604.9017
3751.9417 | 607.4042
3752.9417 | 611.3686
3753.9417 | 611.5652
3754.9417 | 611.3663
3755.9417 | 611.2188
3756.9417 | 611.9066
3757.9417 | 607.3837
3758.9417 | 605.8876
3759.9417 | 606.5337
3760.9417 | 606.929
3761.9417 | 608.1293
3762.9417 | 605.6577
3763.9417 | 602.4732
3764.9417 | 601.8407
3765.9417 | 600.6924
3766.9417 | 602.5132
3767.9417 | 606.2207
3768.9417 | 607.477
3769.9417 | 607.7263
3770.9417 | 608.2551
3771.9417 | 608.7294
3772.9417 | 613.8444
3773.9417 | 616.6953
3774.9417 | 615.1235
3775.9417 | 610.9818
3776.9417 | 606.8552
3777.9417 | 601.3421
3778.9417 | 598.1945
3779.9417 | 595.7493
3780.9417 | 592.857
3781.9417 | 590.1185
3782.9417 | 587.7242
3783.9417 | 585.6722
3784.9417 | 584.4743
3785.9417 | 585.0032
3786.9417 | 585.9827
3787.9417 | 587.4892
3788.9417 | 586.7437
3789.9417 | 590.3717
3790.9417 | 595.7477
3791.9417 | 599.5283
3792.9417 | 598.6542
3793.9417 | 595.0822
3794.9417 | 591.894
3795.9417 | 589.3975
3796.9417 | 588.9217
3797.9417 | 589.7964
3798.9417 | 587.4634
3799.9417 | 584.917
3800.9417 | 583.8359
3801.9417 | 580.4507
3802.9417 | 578.4699
3803.9417 | 578.5161
3804.9417 | 579.6235
3805.9417 | 580.3562
3806.9417 | 581.0756
3807.9417 | 583.1398
3808.9417 | 582.7645
3809.9417 | 582.199
3810.9417 | 581.9939
3811.9417 | 582.1269
3812.9417 | 583.6618
3813.9417 | 585.1775
3814.9417 | 586.4762
3815.9417 | 584.9708
3816.9417 | 582.7632
3817.9417 | 582.232
3818.9417 | 581.9676
3819.9417 | 580.8112
3820.9417 | 581.9075
3821.9417 | 581.6177
3822.9417 | 580.5653
3823.9417 | 582.1688
3824.9417 | 580.609
3825.9417 | 577.4446
3826.9417 | 577.0534
3827.9417 | 576.9766
3828.9417 | 577.6661
3829.9417 | 576.9802
3830.9417 | 578.8596
3831.9417 | 581.157
3832.9417 | 586.0113
3833.9417 | 587.7744
3834.9417 | 589.1793
3835.9417 | 588.2532
3836.9417 | 585.7914
3837.9417 | 584.8666
3838.9417 | 585.6578
3839.9417 | 583.6221
3840.9417 | 585.3029
3841.9417 | 586.0512
3842.9417 | 587.302
3843.9417 | 590.1969
3844.9417 | 589.1056
3845.9417 | 587.8302
3846.9417 | 588.0194
3847.9417 | 586.0118
3848.9417 | 585.2039
3849.9417 | 586.7386
3850.9417 | 587.5372
3851.9573 | 585.4946
3852.9417 | 583.6977
3853.9417 | 581.0341
3854.9417 | 580.1115
3855.9417 | 579.9184
3856.9417 | 580.6784
3857.9417 | 580.9398
3858.9417 | 579.5671
3859.9417 | 578.9868
3860.9417 | 578.2522
3861.9417 | 577.0478
3862.9417 | 577.2597
3863.9417 | 579.1377
3864.9417 | 582.2788
3865.9417 | 583.7943
3866.9417 | 581.8632
3867.9417 | 579.7766
3868.9417 | 578.1671
3869.9417 | 577.2621
3870.9417 | 576.2576
3871.9417 | 576.034
3872.9417 | 577.9065
3873.9417 | 580.2201
3874.9417 | 579.2581
3875.9417 | 578.0797
3876.9417 | 578.7904
3877.9417 | 577.5554
3878.9417 | 577.6839
3879.9417 | 579.5408
3880.9417 | 580.7664
3881.9573 | 582.2038
3882.9417 | 582.0287
3883.9417 | 582.5397
3884.9417 | 582.4137
3885.9417 | 581.9357
3886.9417 | 581.9028
3887.9417 | 580.9409
3888.9417 | 579.5548
3889.9417 | 579.828
3890.9417 | 582.0383
3891.9417 | 583.022
3892.9417 | 583.3815
3893.9417 | 582.95
3894.9417 | 582.6947