## Test Conditions
DESIREE-FIRE Intermediate Scale Test Number 12 - Circuit Simulator Data Only
Test Date: | 2009-11-23
DCSim DAQ Start Time | 15:07
DCSim Time for Synchronization | 15:08
Heat Source Synchronization | 0:01 | hour:minutes:seconds
Heat Source DAQ Start Time | 15:08
Fire Time | 15:57
Offset | 0:50 | hour:minutes:seconds | This is the time after the DCSim DAQ was started and the heat source was initiated.
| 3026 | seconds
Heat Source Offset | 0:50 | hour:minutes:seconds | This is the time after the Heat Source DAQ was started and the heat source was initiated.
| 2991 | seconds
Heat Source Stop Time | 17:02
Test Duration | 1:05 | hour:minutes:seconds
| 3894 | seconds
CT500 turns | 2 | 1 or 2 | This is the number of times the lead conductor within the DCSim Panels were wrapped around the Hall Effect Device of the current transducer.
CT35 turns | 5 | 1 or 5
Pre-Test Baseline: | Gathered | Gathered or Not Gathered
Cable Information: | Record info about cable type on each circuit and which of the cable thermocouples corresponds to cable and air temperature
Unit number | Cable Type |  | Cable TC channel | Air TC Channel
MOV 1 | EPR/CPE, 7c, 12AWG |  | Cable thermocouples were not used for this test. | Channel 5, 6, and 7 represents the air temperature 3', 5', and 7' down the cable tray located in D-Position. These are labeled as "D-Position - 3'", "D-Position - Middle", " D-Position - 7'", respectively.
MOV 2 | EPR/CPE, 7c, 12AWG |  | Cable thermocouples were not used for this test. | Channel 1 which is defined as "B Position - Middle" in the Temperature Data File respresents the temperature in the center of the cable tray.
A Note on Data Conversion and Accuracy:
Two different types of voltage transducers were used for each circuit. A bidirectional transducer (Ohio Semitronics, model number VT7-005X5-11) produces a 0 - 5V output signal which is directly proportional to the DC input ranging from 0 - 150VDC. The accuracy of this device is +/-0.25% full scale at DC and the response time is 50 mircoseconds. The unidirectional DC voltage isolator (Ohio Semitronics, model number VTU-005X5) used throughout tests also produces a 0 - 5V output over a 0 - 150VDC range. The accuracy of this device is +/-0.25% Rdg., +/-1% full scale at DC and the response time is 500 microseconds. Two different current transducers were for each circuit. One current transducer (Ohio Semitronics, model number CTL-51/35) was used to detect lower (0 - 35A) amperage transient behavior through a paired and calibrated signal conditioner (CTA201RX5). The other transducer (Ohio Semitronics, model number CTL-601/500) was set to detect transient current increases from 0 - 500A. These were also paired and calibrated with a signal conditioner (CTA2-1X5).
The readings were monitored using a National Instruments SCXI-1100 modules attached to SCXI-1300 multiplexers and housed within a SCXI-1001, 12-slot chassis. The "Raw Data" worksheet has been previously converted by LabView program created for this test series. The nominal zero point readings for each current transducer was taken before each test due to an electromagnetic effect created by direct current power. Zero Point values are provided, and the full run is documented in a separate data sheet (see "Current Offsets" worksheet). The converted data are presented as nominal indications of circuit path voltage and current. The data gathering equipment (transducers and DAQ card) have not been subject to specific calibration beyond that provided by the manufacturers. The accuracy of the converted data is estimated at +/-2%.

## Electrical Data
Fire Time (s) | Ground_VT7_1 | Ground_VTU_1 | Ground_VTU_2 | MOV-1_CT500 | MOV-1a_CT35_1_P | MOV-1a_CT35_2_N | MOV-1b_CT35_1_G | MOV-1b_CT35_2_R | MOV-1b_CT35_3_YO | MOV-1b_CT35_4_YC | MOV-2_CT500 | MOV-2a_CT35_1_P | MOV-2a_CT35_2_N | MOV-2b_CT35_1_G | MOV-2b_CT35_2_R | MOV-2b_CT35_3_YO | 2b_CT35_4_YC1 | MOV-1a_VT7_1_SP | MOV-1a_VTU_1_P | MOV-1a_VTU_2_N | MOV-1b_VT7_1_G | MOV-1b_VT7_2_R | MOV-1b_VT7_3_YO1 | MOV-1b_VT7_4_YC1 | MOV-2a_VT7_1_SP | MOV-2a_VTU_1_P | MOV-2a_VTU_2_N | MOV-2b_VT7_1_G | MOV-2b_VT7_2_R | 2b_VT7_3_YO1 | MOV-2b_VT7_4_YC1 | {MOV1} V(N) - V(Batt -) | {MOV1} V(P) - V(Batt +) | {MOV1} V(G) - V(Batt +) | {MOV1} V(R) - V(Batt -) | {MOV1} V(YC1) - V(Batt -) | {MOV1} V(YO1) - V(Batt -) | {MOV1} V(YC1) - V(N) | {MOV1} V(YO1) - V(N) | {MOV2} V(N) - V(Batt -) | {MOV2} V(P) - V(Batt +) | {MOV2} V(G) - V(Batt +) | {MOV2} V(R) - V(Batt -) | {MOV2} V(YC1) - V(Batt -) | {MOV2} V(YO1) - V(Batt -) | {MOV2} V(YC1) - V(N) | {MOV2} V(YO1) - V(N) | {MOV-1} V(R) - V(N) | {MOV-1} V(G) - V(N) | {MOV-2} V(R) - V(N) | {MOV-2} V(G) - V(N) | {MOV-1} V(P) - V(N) | {MOV-2} V(P) - V(N) | {MOV-1} V(P) - V(Batt -) | {MOV-2} V(P) - V(Batt -) | {MOV-1} V(N) - V(Batt +) | {MOV-2} V(N) - V(Batt +) | {MOV-1} V(G) - V(Batt -) | {MOV2} V(G) - V(Batt-) | {MOV1} V(SP) - V(Batt -) | {MOV2} V(SP) - V(Batt -)
-1.3438 | 122.3145 | -62.2742 | 59.7427 | -0.013657 | 0.0012027 | 0.062666 | 0.060103 | 0.0017132 | -0.0042745 | 0.0010831 | -0.0021057 | 0.001303 | 0.073006 | 0.063132 | -0.0058191 | 0.016022 | -0.003561 | -0.11902 | 59.5871 | -62.2513 | 59.8846 | -62.0682 | -62.5534 | -62.5305 | -0.013733 | 59.5505 | -62.3108 | 59.8206 | -62.1918 | -62.3795 | -62.4344 | 0.022888 | -0.15564 | 0.14191 | 0.20599 | -0.25635 | -0.27924 | -0.27924 | -0.30212 | -0.036621 | -0.19226 | 0.07782 | 0.082398 | -0.16022 | -0.10529 | -0.1236 | -0.068665 | 0.18311 | 122.1359 | 0.11902 | 122.1313 | 121.8384 | 121.8613 | 121.8613 | 121.8246 | -121.994 | -122.0535 | 122.1588 | 122.0947 | 62.1552 | 62.2604
0.40625 | 122.2366 | -62.265 | 59.8068 | -0.013657 | 0.0018435 | 0.063734 | 0.063521 | -0.001491 | -0.0057699 | -0.0010531 | -0.0021057 | 0.0021576 | 0.073006 | 0.069541 | -0.0088097 | 0.014954 | 7.04e-05 | 0.004578 | 59.5779 | -62.2513 | 59.9258 | -62.0178 | -62.5031 | -62.4893 | 0.07782 | 59.5917 | -62.2833 | 59.8297 | -62.1872 | -62.3978 | -62.4573 | 0.013733 | -0.22888 | 0.11902 | 0.24719 | -0.2243 | -0.23804 | -0.23804 | -0.25177 | -0.01831 | -0.21515 | 0.022888 | 0.07782 | -0.19226 | -0.13275 | -0.17395 | -0.11444 | 0.23346 | 122.1771 | 0.09613 | 122.113 | 121.8292 | 121.875 | 121.843 | 121.8567 | -122.0581 | -122.0901 | 122.1909 | 122.0947 | 62.2696 | 62.3428
2.1406 | 122.2366 | -62.2833 | 59.8114 | -0.0060272 | 0.0020571 | 0.060957 | 0.059462 | 0.0017132 | -0.0034201 | -0.00041227 | -0.0021057 | 0.0042938 | 0.073647 | 0.058005 | -0.0062463 | 0.016022 | -0.003561 | 0.004578 | 59.5917 | -62.2513 | 59.8755 | -62.0911 | -62.5168 | -62.5259 | 0.013733 | 59.6375 | -62.2925 | 59.7977 | -62.2009 | -62.4023 | -62.4664 | 0.032043 | -0.21973 | 0.064087 | 0.19226 | -0.24262 | -0.23346 | -0.27466 | -0.2655 | -0.009155 | -0.17395 | -0.013733 | 0.082397 | -0.18311 | -0.11902 | -0.17395 | -0.10986 | 0.16022 | 122.1268 | 0.091552 | 122.0901 | 121.843 | 121.9299 | 121.875 | 121.9208 | -122.0627 | -122.1039 | 122.1588 | 122.081 | 62.2879 | 62.2971
3.875 | 122.3419 | -62.265 | 59.7427 | -0.0060272 | -0.0002927 | 0.061598 | 0.057753 | -0.0040546 | -0.0072653 | 0.0021511 | 0.0009461 | -0.00061956 | 0.071724 | 0.071036 | -0.0075281 | 0.01474 | -0.0005704 | -0.013733 | 59.5459 | -62.2375 | 59.9442 | -61.9812 | -62.4207 | -62.4207 | 0.10986 | 59.5734 | -62.2833 | 59.8618 | -62.1094 | -62.3016 | -62.3932 | 0.027466 | -0.19684 | 0.20142 | 0.28381 | -0.15564 | -0.15564 | -0.1831 | -0.1831 | -0.01831 | -0.16937 | 0.11902 | 0.15564 | -0.12817 | -0.036621 | -0.10986 | -0.018311 | 0.25635 | 122.1817 | 0.17395 | 122.1451 | 121.7834 | 121.8567 | 121.8109 | 121.8384 | -121.9803 | -122.0261 | 122.2092 | 122.1268 | 62.2513 | 62.3749
5.5781 | 122.1817 | -62.2559 | 59.8022 | -0.0060272 | 0.0003483 | 0.063307 | 0.059676 | -0.001491 | -0.0044883 | -0.0021213 | -0.0021057 | 0.0042938 | 0.072578 | 0.063346 | -0.0081689 | 0.015595 | -0.0039884 | 0.009155 | 59.5917 | -62.2467 | 59.8572 | -62.0773 | -62.5168 | -62.5214 | 0 | 59.6237 | -62.2971 | 59.7565 | -62.2192 | -62.4115 | -62.5122 | 0.009155 | -0.21057 | 0.054932 | 0.17853 | -0.2655 | -0.26093 | -0.27466 | -0.27008 | -0.041199 | -0.17853 | -0.045776 | 0.036621 | -0.25635 | -0.15564 | -0.21515 | -0.11444 | 0.16937 | 122.1039 | 0.07782 | 122.0535 | 121.8384 | 121.9208 | 121.8475 | 121.8796 | -122.0489 | -122.0993 | 122.113 | 122.0123 | 62.265 | 62.2559
7.3281 | 122.2137 | -62.265 | 59.8068 | -0.013657 | -0.0011471 | 0.061385 | 0.059676 | -0.0034136 | -0.0044883 | -0.0019077 | 0.0039977 | 0.0021576 | 0.073647 | 0.068045 | -0.0058191 | 0.015595 | 0.0041294 | -0.013733 | 59.6008 | -62.2559 | 59.8709 | -62.0682 | -62.5351 | -62.5259 | 0 | 59.6237 | -62.2742 | 59.7565 | -62.2147 | -62.4115 | -62.4893 | 0.009156 | -0.20599 | 0.064087 | 0.19684 | -0.26093 | -0.27008 | -0.27008 | -0.27924 | -0.009155 | -0.18311 | -0.050354 | 0.050354 | -0.2243 | -0.14648 | -0.21515 | -0.13733 | 0.18768 | 122.1268 | 0.059509 | 122.0306 | 121.8567 | 121.8979 | 121.8658 | 121.8887 | -122.0627 | -122.081 | 122.1359 | 122.0215 | 62.2513 | 62.265
9.0156 | 122.1909 | -62.2833 | 59.8022 | -0.0060272 | 0.0003483 | 0.061385 | 0.059462 | -0.0061908 | -0.0044883 | -0.0042575 | -0.0051575 | 0.0017304 | 0.071938 | 0.059928 | -0.0064599 | 0.016876 | -0.0048428 | -0.022888 | 59.6008 | -62.2421 | 59.8663 | -62.0865 | -62.5076 | -62.5214 | -0.013733 | 59.6329 | -62.2833 | 59.761 | -62.2513 | -62.439 | -62.4985 | 0.041199 | -0.20142 | 0.064087 | 0.19684 | -0.23804 | -0.2243 | -0.27924 | -0.2655 | 0 | -0.16937 | -0.041199 | 0.032043 | -0.21515 | -0.15564 | -0.21515 | -0.15564 | 0.15564 | 122.1085 | 0.032043 | 122.0444 | 121.843 | 121.9162 | 121.8842 | 121.9162 | -122.0444 | -122.0856 | 122.1497 | 122.0444 | 62.2604 | 62.2696
10.75 | 122.2733 | -62.2696 | 59.7473 | -0.0060272 | 0.0009891 | 0.063734 | 0.061598 | -0.0023456 | -0.0070517 | -0.0010531 | -0.0021057 | 0.0021576 | 0.073219 | 0.074241 | -0.0083825 | 0.014099 | -0.0014248 | -0.13733 | 59.5505 | -62.2742 | 59.848 | -62.1094 | -62.5763 | -62.5717 | -0.059509 | 59.5596 | -62.3245 | 59.7885 | -62.2375 | -62.4207 | -62.4847 | -0.004578 | -0.19684 | 0.10071 | 0.16022 | -0.30212 | -0.3067 | -0.29755 | -0.30212 | -0.054932 | -0.18768 | 0.041199 | 0.032043 | -0.21515 | -0.15106 | -0.16022 | -0.09613 | 0.16479 | 122.1222 | 0.086975 | 122.113 | 121.8246 | 121.8842 | 121.8201 | 121.8292 | -122.0215 | -122.0718 | 122.1176 | 122.0581 | 62.1323 | 62.2101
12.4844 | 122.2137 | -62.2925 | 59.8022 | -0.013657 | -0.0007199 | 0.060744 | 0.058394 | -0.0019184 | -0.0044883 | -0.0029759 | 0.0009461 | 0.001944 | 0.072792 | 0.060569 | -0.0071009 | 0.014313 | -0.0039884 | 0.013733 | 59.5734 | -62.233 | 59.8846 | -62.0544 | -62.5168 | -62.5122 | 0.022888 | 59.61 | -62.2879 | 59.7565 | -62.233 | -62.4023 | -62.5168 | 0.059509 | -0.22888 | 0.082398 | 0.23804 | -0.21973 | -0.22431 | -0.27924 | -0.28381 | 0.004577 | -0.19226 | -0.045776 | 0.059509 | -0.22431 | -0.10986 | -0.22888 | -0.11444 | 0.17853 | 122.1176 | 0.054932 | 122.0444 | 121.8063 | 121.8979 | 121.8658 | 121.9025 | -122.0352 | -122.0901 | 122.1771 | 122.0489 | 62.3062 | 62.3154
14.2344 | 122.2092 | -62.3016 | 59.8206 | -0.0060272 | 0.0020571 | 0.062239 | 0.059676 | 4.192e-06 | -0.0040609 | -0.0044711 | -0.0021057 | 0.0032256 | 0.072151 | 0.064841 | -0.0068871 | 0.015381 | -0.0029202 | 0 | 59.61 | -62.2284 | 59.8618 | -62.0911 | -62.5305 | -62.5351 | 0.018311 | 59.6237 | -62.3062 | 59.761 | -62.233 | -62.4298 | -62.4985 | 0.073242 | -0.21057 | 0.041198 | 0.21057 | -0.23346 | -0.22888 | -0.3067 | -0.30212 | -0.004577 | -0.19684 | -0.05951 | 0.068665 | -0.19684 | -0.12817 | -0.19226 | -0.1236 | 0.13733 | 122.0901 | 0.073242 | 122.0673 | 121.8384 | 121.9299 | 121.9116 | 121.9254 | -122.049 | -122.1268 | 122.1634 | 122.0627 | 62.3016 | 62.3199
16 | 122.1909 | -62.3291 | 59.7885 | -0.0060272 | 0.0052615 | 0.064375 | 0.06288 | -0.0010638 | -0.0036337 | -0.0021213 | -0.0021057 | 0.0021576 | 0.071297 | 0.064627 | -0.0077417 | 0.01709 | 0.0002842 | -0.091553 | 59.5871 | -62.2513 | 59.8343 | -62.1277 | -62.5946 | -62.5809 | -0.091553 | 59.6054 | -62.3199 | 59.7382 | -62.2833 | -62.4985 | -62.5168 | 0.07782 | -0.20142 | 0.045777 | 0.20142 | -0.25177 | -0.2655 | -0.32959 | -0.34332 | 0.009156 | -0.18311 | -0.050354 | 0.045777 | -0.18768 | -0.16937 | -0.19684 | -0.17853 | 0.1236 | 122.0856 | 0.036621 | 122.0581 | 121.8384 | 121.9254 | 121.9162 | 121.9345 | -122.0398 | -122.1085 | 122.1634 | 122.0673 | 62.2375 | 62.2375
17.6875 | 122.2549 | -62.3245 | 59.7702 | -0.013657 | 0.0020571 | 0.063734 | 0.061385 | 0.004704 | -0.0038473 | -0.0019077 | -0.0051575 | 0.0040802 | 0.074501 | 0.062064 | -0.0077417 | 0.015595 | -0.005911 | -0.13733 | 59.5642 | -62.2787 | 59.8297 | -62.1231 | -62.59 | -62.5763 | -0.086975 | 59.5642 | -62.3199 | 59.7565 | -62.2604 | -62.4619 | -62.5076 | 0.045776 | -0.20599 | 0.059509 | 0.20142 | -0.25177 | -0.2655 | -0.29755 | -0.31128 | 0.004578 | -0.20599 | -0.013733 | 0.064087 | -0.18311 | -0.13733 | -0.18768 | -0.14191 | 0.15564 | 122.1085 | 0.059509 | 122.0764 | 121.843 | 121.8842 | 121.8887 | 121.8887 | -122.049 | -122.0901 | 122.1542 | 122.081 | 62.1872 | 62.2375
19.4219 | 122.2137 | -62.3154 | 59.7656 | -0.013657 | 0.0024845 | 0.06523 | 0.062239 | 0.0019268 | -0.0036337 | -0.0014805 | -0.0051575 | 0.0025848 | 0.074074 | 0.06655 | -0.0045373 | 0.018585 | -0.0027066 | -0.13733 | 59.6008 | -62.265 | 59.8206 | -62.146 | -62.6175 | -62.5763 | -0.091553 | 59.5734 | -62.3154 | 59.7427 | -62.2833 | -62.471 | -62.5168 | 0.050354 | -0.16479 | 0.054932 | 0.16937 | -0.26093 | -0.30212 | -0.31128 | -0.35248 | 0 | -0.19226 | -0.022888 | 0.032044 | -0.20142 | -0.15564 | -0.20142 | -0.15564 | 0.11902 | 122.0856 | 0.032044 | 122.0581 | 121.8658 | 121.8887 | 121.9162 | 121.8887 | -122.0306 | -122.081 | 122.1359 | 122.0581 | 62.178 | 62.2238
21.1562 | 122.2549 | -62.2787 | 59.7839 | 0.0016023 | 0.0007755 | 0.062453 | 0.060103 | -0.0012774 | -0.0049155 | -0.0029759 | -0.0021057 | 0.001944 | 0.073433 | 0.074668 | -0.0081689 | 0.01474 | -0.0016384 | 0.018311 | 59.5963 | -62.2696 | 59.8984 | -62.0728 | -62.5031 | -62.5214 | 0.018311 | 59.6191 | -62.2742 | 59.7977 | -62.2055 | -62.3932 | -62.4527 | 0.009156 | -0.18768 | 0.11444 | 0.20599 | -0.24261 | -0.2243 | -0.25177 | -0.23346 | 0.004578 | -0.16479 | 0.013732 | 0.073243 | -0.17395 | -0.11444 | -0.17853 | -0.11902 | 0.19684 | 122.168 | 0.068665 | 122.0718 | 121.8658 | 121.8933 | 121.875 | 121.8979 | -122.0535 | -122.0581 | 122.1771 | 122.0764 | 62.2971 | 62.2971
22.8906 | 122.2229 | -62.3108 | 59.7977 | -0.013657 | 0.0031253 | 0.062239 | 0.062666 | 0.0017132 | -0.0027793 | -0.0014805 | -0.0051575 | 0.0038666 | 0.072151 | 0.064414 | -0.0068871 | 0.015381 | -0.0001432 | -0.12817 | 59.6008 | -62.2742 | 59.7977 | -62.1323 | -62.5992 | -62.5809 | -0.07782 | 59.5917 | -62.3245 | 59.7656 | -62.2696 | -62.4802 | -62.5122 | 0.036621 | -0.19684 | 0 | 0.17853 | -0.27008 | -0.28839 | -0.3067 | -0.32501 | -0.013733 | -0.20599 | -0.032043 | 0.041199 | -0.20142 | -0.16937 | -0.18768 | -0.15564 | 0.14191 | 122.0718 | 0.054932 | 122.0901 | 121.875 | 121.9162 | 121.9116 | 121.9025 | -122.0718 | -122.1222 | 122.1085 | 122.0764 | 62.1826 | 62.233
24.5625 | 122.3282 | -62.2559 | 59.7931 | 0.0016023 | 0.0005619 | 0.061812 | 0.056898 | -0.0017048 | -0.0057699 | -0.0019077 | 0.0009461 | -0.00061956 | 0.071938 | 0.062705 | -0.0083825 | 0.014099 | -0.0001432 | -0.036621 | 59.5413 | -62.2375 | 59.9213 | -62.0087 | -62.471 | -62.4664 | 0.050354 | 59.5367 | -62.2833 | 59.8434 | -62.1323 | -62.2925 | -62.3932 | 0.01831 | -0.25177 | 0.12817 | 0.24719 | -0.21057 | -0.21515 | -0.22888 | -0.23346 | -0.027466 | -0.25635 | 0.050354 | 0.1236 | -0.13733 | -0.036621 | -0.10986 | -0.009155 | 0.22888 | 122.1588 | 0.15106 | 122.1268 | 121.7789 | 121.8201 | 121.7972 | 121.7926 | -122.0306 | -122.0764 | 122.1771 | 122.0993 | 62.2192 | 62.3062
26.25 | 122.3099 | -62.2742 | 59.7794 | 0.0016023 | 0.0018435 | 0.060957 | 0.059248 | -0.0017048 | -0.0051291 | -0.0038303 | -0.0021057 | 0.00066224 | 0.070869 | 0.069968 | -0.0077417 | 0.014313 | -0.0046292 | -0.054932 | 59.5413 | -62.233 | 59.9121 | -62.0453 | -62.5168 | -62.4985 | 0.032043 | 59.5505 | -62.2833 | 59.8068 | -62.1735 | -62.3383 | -62.4298 | 0.041199 | -0.23804 | 0.13275 | 0.22888 | -0.2243 | -0.24262 | -0.2655 | -0.28381 | -0.009155 | -0.22888 | 0.027466 | 0.10071 | -0.15564 | -0.064087 | -0.14649 | -0.054932 | 0.18768 | 122.1451 | 0.10986 | 122.0901 | 121.7743 | 121.8338 | 121.8155 | 121.8246 | -122.0123 | -122.0627 | 122.1863 | 122.081 | 62.2192 | 62.3062
27.9844 | 122.3282 | -62.2559 | 59.8022 | -0.0060272 | 0.0001345 | 0.059889 | 0.059462 | -0.0036274 | -0.0061971 | -0.0029759 | -0.0021057 | 0.00023504 | 0.071938 | 0.06655 | -0.0096643 | 0.014526 | -0.0046292 | 0.050354 | 59.5322 | -62.2467 | 60.0037 | -61.9354 | -62.4023 | -62.4207 | 0.16022 | 59.5596 | -62.2696 | 59.8709 | -62.1094 | -62.2971 | -62.3749 | 0.009155 | -0.27008 | 0.20142 | 0.32043 | -0.16479 | -0.14648 | -0.17395 | -0.15564 | -0.013733 | -0.24261 | 0.068665 | 0.14648 | -0.11902 | -0.041199 | -0.10529 | -0.027466 | 0.31128 | 122.2504 | 0.16022 | 122.1405 | 121.7789 | 121.8292 | 121.788 | 121.8155 | -122.0489 | -122.0718 | 122.2595 | 122.1268 | 62.3062 | 62.4161
29.7188 | 122.3053 | -62.2925 | 59.7198 | 0.0016023 | 0.0022709 | 0.063521 | 0.059889 | 0.0023542 | -0.0047019 | -0.0044711 | 0.0009461 | 0.00066224 | 0.072792 | 0.063773 | -0.0077417 | 0.016235 | -0.0027066 | -0.068665 | 59.5001 | -62.2421 | 59.9487 | -62.0041 | -62.4847 | -62.471 | 0.068665 | 59.5413 | -62.3016 | 59.8389 | -62.1826 | -62.3611 | -62.4207 | 0.050354 | -0.21973 | 0.22888 | 0.28839 | -0.17853 | -0.19226 | -0.22888 | -0.24262 | -0.009156 | -0.17853 | 0.11902 | 0.10986 | -0.12817 | -0.068665 | -0.11902 | -0.059509 | 0.23804 | 122.1909 | 0.11902 | 122.1405 | 121.7422 | 121.843 | 121.7926 | 121.8338 | -121.962 | -122.0215 | 122.2412 | 122.1313 | 62.2238 | 62.3611
31.4688 | 122.2183 | -62.2925 | 59.8206 | 0.0092313 | -0.0011471 | 0.062025 | 0.05818 | -0.0017048 | -0.0061971 | 0.00044213 | 0.0009461 | 0.0017304 | 0.072578 | 0.072532 | -0.0079553 | 0.015381 | -0.0016384 | 0.032043 | 59.5734 | -62.2604 | 59.9121 | -62.0453 | -62.5168 | -62.5076 | 0.027466 | 59.6146 | -62.2879 | 59.7656 | -62.2284 | -62.4161 | -62.4939 | 0.032043 | -0.24719 | 0.091552 | 0.24719 | -0.21515 | -0.22431 | -0.24719 | -0.25635 | 0.004577 | -0.20599 | -0.054932 | 0.064086 | -0.20142 | -0.1236 | -0.20599 | -0.12817 | 0.21515 | 122.1725 | 0.059509 | 122.0535 | 121.8338 | 121.9025 | 121.8658 | 121.907 | -122.081 | -122.1085 | 122.2046 | 122.0581 | 62.3245 | 62.3199
33.1406 | 122.2549 | -62.2925 | 59.7794 | 0.0092313 | 0.0031253 | 0.062666 | 0.061812 | -0.0078998 | -0.0049155 | 0.0010831 | -0.0051575 | 0.0038666 | 0.072578 | 0.061423 | -0.0081689 | 0.016022 | -0.0033474 | -0.12817 | 59.6008 | -62.2742 | 59.8434 | -62.114 | -62.5992 | -62.5717 | -0.073242 | 59.5734 | -62.3291 | 59.7748 | -62.2559 | -62.4527 | -62.5076 | 0.01831 | -0.17853 | 0.064087 | 0.17853 | -0.27924 | -0.3067 | -0.29755 | -0.32501 | -0.036622 | -0.20599 | -0.004578 | 0.036621 | -0.21515 | -0.16022 | -0.17853 | -0.1236 | 0.16022 | 122.1176 | 0.073243 | 122.1039 | 121.875 | 121.9025 | 121.8933 | 121.8658 | -122.0535 | -122.1085 | 122.1359 | 122.0673 | 62.1643 | 62.2192
34.875 | 122.3053 | -62.2879 | 59.729 | -0.013657 | 0.0003483 | 0.064375 | 0.059462 | -0.0032 | -0.0044883 | -0.0014805 | -0.0021057 | 0.00044864 | 0.072578 | 0.060782 | -0.0083825 | 0.01474 | -0.003561 | -0.082397 | 59.5322 | -62.2055 | 59.9442 | -61.9766 | -62.4939 | -62.4573 | 0.054932 | 59.5139 | -62.3108 | 59.8251 | -62.1826 | -62.3657 | -62.4252 | 0.082398 | -0.19684 | 0.21515 | 0.31128 | -0.16937 | -0.20599 | -0.25177 | -0.28839 | -0.022888 | -0.21515 | 0.09613 | 0.10529 | -0.13733 | -0.07782 | -0.11444 | -0.054932 | 0.22888 | 122.1497 | 0.12817 | 122.1359 | 121.7377 | 121.8246 | 121.8201 | 121.8018 | -121.9345 | -122.0398 | 122.2321 | 122.113 | 62.2055 | 62.3428
36.5625 | 122.2458 | -62.2833 | 59.7885 | -0.0060272 | 0.0035525 | 0.061598 | 0.061171 | -0.0010638 | -0.0023519 | -0.0014805 | -0.0051575 | 0.0027984 | 0.072578 | 0.065909 | -0.0060327 | 0.018799 | -0.0048428 | -0.009155 | 59.5825 | -62.2421 | 59.9075 | -62.027 | -62.5031 | -62.4985 | 0.07782 | 59.6237 | -62.2833 | 59.8114 | -62.1826 | -62.4023 | -62.4435 | 0.041199 | -0.20599 | 0.11902 | 0.25635 | -0.21515 | -0.21973 | -0.25635 | -0.26093 | 0 | -0.1648 | 0.022888 | 0.10071 | -0.16022 | -0.11902 | -0.16022 | -0.11902 | 0.21515 | 122.1497 | 0.10071 | 122.0947 | 121.8246 | 121.907 | 121.8658 | 121.907 | -122.0306 | -122.0718 | 122.1909 | 122.0947 | 62.2742 | 62.3611
38.3125 | 122.2549 | -62.2559 | 59.8297 | -0.0060272 | 0.0033389 | 0.063094 | 0.062239 | -0.0042682 | -0.0029929 | -0.0010531 | -0.0021057 | 0.0017304 | 0.073219 | 0.068045 | -0.0081689 | 0.018799 | -0.0005704 | 0.018311 | 59.6237 | -62.233 | 59.8892 | -62.0773 | -62.5076 | -62.5122 | 0.041199 | 59.642 | -62.2833 | 59.7977 | -62.1964 | -62.3932 | -62.439 | 0.022888 | -0.20599 | 0.059509 | 0.17853 | -0.25635 | -0.25177 | -0.27924 | -0.27466 | -0.027466 | -0.18768 | -0.032044 | 0.059509 | -0.18311 | -0.13733 | -0.15564 | -0.10986 | 0.15564 | 122.1222 | 0.086975 | 122.081 | 121.8567 | 121.9254 | 121.8796 | 121.8979 | -122.0627 | -122.113 | 122.1451 | 122.0535 | 62.2742 | 62.2971
40.0625 | 122.2504 | -62.2833 | 59.8114 | -0.021286 | 0.0026981 | 0.062453 | 0.062239 | 0.00021799 | -0.0055563 | -0.0016941 | -0.0051575 | 0.0027984 | 0.073647 | 0.071036 | -0.0090235 | 0.017517 | -0.002493 | 0.004578 | 59.6008 | -62.2375 | 59.9167 | -62.0178 | -62.5031 | -62.5031 | 0.059509 | 59.5917 | -62.2833 | 59.8114 | -62.1872 | -62.384 | -62.4252 | 0.045776 | -0.21057 | 0.10529 | 0.2655 | -0.21973 | -0.21973 | -0.2655 | -0.2655 | 0 | -0.21973 | 0 | 0.09613 | -0.14191 | -0.10071 | -0.14191 | -0.10071 | 0.21973 | 122.1542 | 0.09613 | 122.0947 | 121.8384 | 121.875 | 121.8842 | 121.875 | -122.0489 | -122.0947 | 122.2 | 122.0947 | 62.2879 | 62.3428
41.8125 | 122.2275 | -62.2559 | 59.8526 | -0.013657 | -0.0005063 | 0.061385 | 0.060103 | 0.0010724 | -0.0055563 | -0.0038303 | -0.0021057 | 0.00087584 | 0.073219 | 0.067191 | -0.0058191 | 0.015381 | -0.0001432 | 0 | 59.6146 | -62.2238 | 59.8618 | -62.0773 | -62.5397 | -62.5397 | -0.004578 | 59.6146 | -62.3016 | 59.7656 | -62.233 | -62.4252 | -62.471 | 0.032043 | -0.23804 | 0.009155 | 0.17853 | -0.28381 | -0.28381 | -0.31586 | -0.31586 | -0.045777 | -0.23804 | -0.086975 | 0.022888 | -0.21515 | -0.16937 | -0.16937 | -0.1236 | 0.14648 | 122.0856 | 0.068665 | 122.0673 | 121.8384 | 121.9162 | 121.8704 | 121.8704 | -122.0764 | -122.1542 | 122.1176 | 122.0215 | 62.2559 | 62.2513
43.4844 | 122.2 | -62.3062 | 59.8022 | -0.0060272 | 0.0031253 | 0.064375 | 0.061385 | 0.00021799 | -0.0044883 | -0.00062587 | 0.0009461 | 0.00087584 | 0.071938 | 0.074027 | -0.0064599 | 0.017517 | 0.0028476 | -0.11444 | 59.5963 | -62.2467 | 59.8206 | -62.146 | -62.5992 | -62.5763 | -0.10529 | 59.6237 | -62.3199 | 59.7198 | -62.3016 | -62.4847 | -62.5351 | 0.059509 | -0.20599 | 0.018311 | 0.16022 | -0.27008 | -0.29297 | -0.32959 | -0.35248 | -0.013733 | -0.17853 | -0.082397 | 0.004577 | -0.22888 | -0.17853 | -0.21515 | -0.16479 | 0.10071 | 122.0673 | 0.01831 | 122.0398 | 121.843 | 121.9437 | 121.9025 | 121.9299 | -122.0489 | -122.1222 | 122.1268 | 122.0261 | 62.1918 | 62.2009
45.2344 | 122.3099 | -62.265 | 59.761 | -0.0060272 | 0.0014163 | 0.062666 | 0.059248 | -0.0040546 | -0.0032065 | -0.0027621 | -0.0021057 | -0.0019012 | 0.07386 | 0.059714 | -0.0075281 | 0.01474 | -0.002493 | -0.054932 | 59.5688 | -62.2375 | 59.9167 | -62.027 | -62.4847 | -62.4847 | 0.032043 | 59.5596 | -62.3016 | 59.8343 | -62.1597 | -62.3337 | -62.4161 | 0.027466 | -0.19226 | 0.15564 | 0.23804 | -0.21973 | -0.21973 | -0.24719 | -0.24719 | -0.036621 | -0.20142 | 0.073243 | 0.10529 | -0.15106 | -0.068664 | -0.11444 | -0.032043 | 0.21057 | 122.1542 | 0.14191 | 122.1359 | 121.8063 | 121.8613 | 121.8338 | 121.8246 | -121.9986 | -122.0627 | 122.1817 | 122.0993 | 62.2101 | 62.2971
46.9844 | 122.319 | -62.2467 | 59.7656 | 0.0016023 | -0.0002927 | 0.060744 | 0.058394 | -0.0036274 | -0.0032065 | -0.0021213 | -0.0051575 | 0.00087584 | 0.071938 | 0.066123 | -0.0094507 | 0.014954 | 7.04e-05 | 0.054932 | 59.5505 | -62.2238 | 59.9808 | -61.9537 | -62.4161 | -62.4115 | 0.14191 | 59.5688 | -62.2787 | 59.8572 | -62.1048 | -62.3016 | -62.3886 | 0.022888 | -0.21515 | 0.21515 | 0.29297 | -0.16479 | -0.16937 | -0.18768 | -0.19226 | -0.032044 | -0.19684 | 0.091553 | 0.14191 | -0.14191 | -0.054932 | -0.10986 | -0.022888 | 0.27008 | 122.2046 | 0.17395 | 122.1359 | 121.7743 | 121.8475 | 121.7972 | 121.8155 | -121.9894 | -122.0444 | 122.2275 | 122.1039 | 62.3016 | 62.3886
48.6562 | 122.3465 | -62.2833 | 59.7382 | -0.0060272 | 0.0026981 | 0.066084 | 0.059035 | -0.001491 | -0.0040609 | -0.0019077 | -0.0021057 | -0.00083316 | 0.071083 | 0.06655 | -0.0092371 | 0.016022 | 0.0013522 | -0.07782 | 59.4864 | -62.2559 | 59.9442 | -61.9904 | -62.4802 | -62.4573 | 0.054932 | 59.5276 | -62.3062 | 59.8526 | -62.1689 | -62.3383 | -62.4161 | 0.027466 | -0.25177 | 0.20599 | 0.29297 | -0.17395 | -0.19684 | -0.20142 | -0.22431 | -0.022888 | -0.21057 | 0.11444 | 0.11444 | -0.13275 | -0.054932 | -0.10986 | -0.032044 | 0.2655 | 122.2 | 0.13733 | 122.1588 | 121.7422 | 121.8338 | 121.7697 | 121.8109 | -121.994 | -122.0444 | 122.2275 | 122.1359 | 62.2055 | 62.3383
50.3438 | 122.2504 | -62.265 | 59.816 | 0.0016023 | 0.0016299 | 0.06053 | 0.060957 | -0.00555 | -0.0036337 | -0.0019077 | -0.0021057 | 0.0049346 | 0.073433 | 0.065482 | -0.0075281 | 0.015808 | -0.0048428 | 0.013733 | 59.5917 | -62.2513 | 59.8892 | -62.0636 | -62.4939 | -62.5259 | 0.059509 | 59.6237 | -62.3016 | 59.8068 | -62.1872 | -62.3978 | -62.4298 | 0.013733 | -0.2243 | 0.073242 | 0.20142 | -0.26093 | -0.22888 | -0.27466 | -0.24261 | -0.036621 | -0.19226 | -0.009155 | 0.07782 | -0.1648 | -0.13275 | -0.12817 | -0.09613 | 0.18768 | 122.1405 | 0.11444 | 122.1085 | 121.843 | 121.9254 | 121.8567 | 121.8887 | -122.0673 | -122.1176 | 122.1542 | 122.0718 | 62.2787 | 62.3245
52.0938 | 122.2961 | -62.2833 | 59.7656 | -0.013657 | 0.0012027 | 0.062453 | 0.058821 | -0.00042301 | -0.0051291 | -0.0010531 | -0.0021057 | 0.001303 | 0.074074 | 0.060782 | -0.0075281 | 0.015167 | -0.0044156 | -0.086975 | 59.523 | -62.2421 | 59.8984 | -62.0224 | -62.4985 | -62.4939 | 0.013733 | 59.5322 | -62.3016 | 59.7977 | -62.2147 | -62.3703 | -62.439 | 0.041199 | -0.24262 | 0.13275 | 0.26093 | -0.21057 | -0.21515 | -0.25177 | -0.25635 | -0.018311 | -0.23346 | 0.032043 | 0.068664 | -0.15564 | -0.086975 | -0.13733 | -0.068664 | 0.21973 | 122.1405 | 0.086975 | 122.0993 | 121.7651 | 121.8338 | 121.8063 | 121.8155 | -122.0078 | -122.0673 | 122.1817 | 122.081 | 62.1963 | 62.2971
53.8281 | 122.3145 | -62.2879 | 59.7427 | 0.0016023 | 0.0001345 | 0.061385 | 0.058821 | 0.002995 | -0.0042745 | -0.00062587 | -0.0021057 | 0.001303 | 0.070656 | 0.055869 | -0.0079553 | 0.017303 | -0.0039884 | -0.064087 | 59.5551 | -62.2604 | 59.903 | -62.0361 | -62.4939 | -62.4893 | 0.036621 | 59.5459 | -62.2925 | 59.816 | -62.1735 | -62.352 | -62.4023 | 0.027466 | -0.18768 | 0.16022 | 0.25177 | -0.20142 | -0.20599 | -0.22888 | -0.23346 | -0.004577 | -0.19684 | 0.073242 | 0.11444 | -0.11444 | -0.064087 | -0.10986 | -0.05951 | 0.2243 | 122.1634 | 0.11902 | 122.1085 | 121.8155 | 121.8384 | 121.843 | 121.8338 | -122.0032 | -122.0352 | 122.1909 | 122.1039 | 62.2238 | 62.3245
55.5 | 122.2412 | -62.2787 | 59.7839 | -0.013657 | 0.0033389 | 0.063948 | 0.064375 | 4.192e-06 | -0.0029929 | 0.00065573 | 0.0009461 | 0.0045074 | 0.07151 | 0.071677 | -0.0075281 | 0.016876 | -0.0009976 | -0.009155 | 59.5825 | -62.2467 | 59.9121 | -62.0361 | -62.5122 | -62.5076 | 0.050354 | 59.5963 | -62.2879 | 59.8022 | -62.2238 | -62.4069 | -62.4573 | 0.032044 | -0.20142 | 0.12817 | 0.24262 | -0.22888 | -0.23346 | -0.26093 | -0.2655 | -0.009155 | -0.18768 | 0.01831 | 0.054932 | -0.17853 | -0.12817 | -0.16937 | -0.11902 | 0.21057 | 122.1588 | 0.064087 | 122.0901 | 121.8292 | 121.8842 | 121.8613 | 121.875 | -122.0306 | -122.0718 | 122.1909 | 122.081 | 62.2696 | 62.3291
57.2344 | 122.3282 | -62.2833 | 59.7427 | -0.013657 | 0.0020571 | 0.06523 | 0.061171 | 0.0019268 | -0.0044883 | -0.0025485 | 0.0009461 | 0.00087584 | 0.072792 | 0.065055 | -0.0085961 | 0.014099 | 0.0002842 | -0.07782 | 59.5047 | -62.2467 | 59.9258 | -61.9949 | -62.4756 | -62.4664 | 0.064087 | 59.5184 | -62.2925 | 59.8434 | -62.1552 | -62.3337 | -62.4023 | 0.036621 | -0.23804 | 0.18311 | 0.28839 | -0.18311 | -0.19226 | -0.21973 | -0.22888 | -0.009155 | -0.2243 | 0.10071 | 0.12817 | -0.11902 | -0.050354 | -0.10986 | -0.041199 | 0.25177 | 122.1725 | 0.13733 | 122.1359 | 121.7514 | 121.8109 | 121.788 | 121.8018 | -121.9894 | -122.0352 | 122.2092 | 122.1268 | 62.2055 | 62.3474
58.9844 | 122.3419 | -62.2742 | 59.7382 | 0.0016023 | 0.0026981 | 0.063307 | 0.061385 | -0.0025592 | -0.0068381 | -0.0036167 | -0.0051575 | -0.00019216 | 0.070656 | 0.065909 | -0.0081689 | 0.01474 | 0.0022068 | -0.082397 | 59.5184 | -62.2421 | 59.9396 | -61.9904 | -62.4847 | -62.471 | 0.041199 | 59.523 | -62.2925 | 59.8663 | -62.146 | -62.3611 | -62.4069 | 0.032044 | -0.21973 | 0.20142 | 0.28381 | -0.19684 | -0.21057 | -0.22888 | -0.24262 | -0.01831 | -0.21515 | 0.12817 | 0.12817 | -0.13275 | -0.086975 | -0.11444 | -0.068665 | 0.25177 | 122.1817 | 0.14648 | 122.1588 | 121.7606 | 121.8155 | 121.7926 | 121.7972 | -121.9803 | -122.0306 | 122.2137 | 122.1405 | 62.1918 | 62.3154
60.6719 | 122.2504 | -62.3016 | 59.8022 | 0.0016023 | -0.0002927 | 0.061598 | 0.060103 | 0.0010724 | -0.0029929 | -0.0027621 | 0.0009461 | 0.003653 | 0.070656 | 0.067618 | -0.0077417 | 0.016449 | -0.0048428 | 0.041199 | 59.5505 | -62.2467 | 59.9579 | -61.972 | -62.4435 | -62.4207 | 0.10529 | 59.5917 | -62.2604 | 59.8114 | -62.1643 | -62.3566 | -62.4252 | 0.054932 | -0.25177 | 0.15564 | 0.32959 | -0.11902 | -0.14191 | -0.17395 | -0.19684 | 0.041199 | -0.21057 | 0.009155 | 0.13733 | -0.1236 | -0.054931 | -0.16479 | -0.09613 | 0.27466 | 122.2046 | 0.09613 | 122.0718 | 121.7972 | 121.8521 | 121.8521 | 121.8933 | -122.0489 | -122.0627 | 122.2595 | 122.113 | 62.3428 | 62.4069
62.4219 | 122.2046 | -62.3016 | 59.7931 | -0.013657 | 0.0029117 | 0.064802 | 0.061812 | 4.192e-06 | -0.0032065 | 0.00044213 | -0.0021057 | 0.0025848 | 0.07151 | 0.067191 | -0.0088097 | 0.016449 | -0.0039884 | -0.09613 | 59.5779 | -62.265 | 59.816 | -62.1506 | -62.6266 | -62.6266 | -0.13275 | 59.5917 | -62.3199 | 59.7427 | -62.2971 | -62.5031 | -62.5031 | 0.036621 | -0.21515 | 0.022888 | 0.15106 | -0.32501 | -0.32501 | -0.36163 | -0.36163 | -0.01831 | -0.20142 | -0.050354 | 0.004578 | -0.20142 | -0.20142 | -0.18311 | -0.18311 | 0.11444 | 122.081 | 0.022888 | 122.0627 | 121.843 | 121.9116 | 121.8796 | 121.8933 | -122.0581 | -122.113 | 122.1176 | 122.0444 | 62.2055 | 62.1689
64.1562 | 122.3145 | -62.2696 | 59.7748 | 0.0016023 | 0.0001345 | 0.060957 | 0.057753 | -0.0059772 | -0.0057699 | -0.0016941 | -0.0051575 | 0.0010894 | 0.071297 | 0.064841 | -0.0068871 | 0.015808 | -0.0020658 | 0.054932 | 59.5367 | -62.2192 | 59.9808 | -61.972 | -62.4252 | -62.4207 | 0.13733 | 59.5871 | -62.2879 | 59.8618 | -62.1048 | -62.3108 | -62.3795 | 0.050354 | -0.23804 | 0.20599 | 0.29755 | -0.15106 | -0.15564 | -0.20142 | -0.20599 | -0.018311 | -0.18768 | 0.086975 | 0.1648 | -0.10986 | -0.041199 | -0.091553 | -0.022888 | 0.24719 | 122.2 | 0.18311 | 122.1497 | 121.756 | 121.875 | 121.8063 | 121.8567 | -121.994 | -122.0627 | 122.2504 | 122.1313 | 62.3245 | 62.4069
65.8438 | 122.3373 | -62.265 | 59.7107 | -0.013657 | 0.0039799 | 0.06288 | 0.058607 | -0.0027728 | -0.0014975 | -0.0019077 | -0.0082093 | 0.001303 | 0.072365 | 0.069541 | -0.0092371 | 0.017731 | -0.0003568 | -0.073242 | 59.5505 | -62.2147 | 59.9442 | -61.9995 | -62.4985 | -62.471 | 0.041199 | 59.5001 | -62.3062 | 59.8572 | -62.1414 | -62.3428 | -62.3978 | 0.050354 | -0.16022 | 0.23346 | 0.2655 | -0.20599 | -0.23346 | -0.25635 | -0.28381 | -0.041198 | -0.21057 | 0.14648 | 0.1236 | -0.13275 | -0.077819 | -0.091553 | -0.036621 | 0.21515 | 122.1588 | 0.16479 | 122.1634 | 121.7651 | 121.8063 | 121.8155 | 121.7651 | -121.9254 | -122.0169 | 122.2092 | 122.1222 | 62.1918 | 62.3062
67.5781 | 122.3145 | -62.2742 | 59.7519 | -0.013657 | -7.9104e-05 | 0.061385 | 0.056685 | -0.0036274 | -0.0057699 | -0.0044711 | -0.0021057 | -0.00040596 | 0.072578 | 0.061637 | -0.0073145 | 0.014313 | 0.0002842 | -0.064087 | 59.5551 | -62.2421 | 59.903 | -62.027 | -62.4985 | -62.4802 | 0.027466 | 59.5413 | -62.3108 | 59.8343 | -62.1689 | -62.3291 | -62.4069 | 0.032044 | -0.19684 | 0.15106 | 0.24719 | -0.20599 | -0.2243 | -0.23804 | -0.25635 | -0.036621 | -0.21057 | 0.082398 | 0.10529 | -0.13275 | -0.054932 | -0.09613 | -0.018311 | 0.21515 | 122.1451 | 0.14191 | 122.1451 | 121.7972 | 121.8521 | 121.8292 | 121.8155 | -121.994 | -122.0627 | 122.1771 | 122.1085 | 62.2101 | 62.3016
69.25 | 122.2549 | -62.2787 | 59.8297 | 0.0016023 | 0.0035525 | 0.062239 | 0.061171 | 0.00064519 | -0.0049155 | -0.0029759 | -0.0082093 | 0.0027984 | 0.072792 | 0.059501 | -0.0062463 | 0.015595 | -0.004202 | 0.009155 | 59.5825 | -62.2421 | 59.9075 | -62.027 | -62.5076 | -62.5076 | 0.07782 | 59.5779 | -62.2879 | 59.8251 | -62.1918 | -62.384 | -62.4481 | 0.036622 | -0.24719 | 0.07782 | 0.25177 | -0.22888 | -0.22888 | -0.2655 | -0.2655 | -0.009155 | -0.25177 | -0.004578 | 0.086976 | -0.16937 | -0.10529 | -0.16022 | -0.09613 | 0.21515 | 122.1497 | 0.096131 | 122.113 | 121.8246 | 121.8658 | 121.8613 | 121.8567 | -122.0718 | -122.1176 | 122.1863 | 122.1039 | 62.2879 | 62.3566
71 | 122.3053 | -62.2787 | 59.7519 | -0.0060272 | 0.0020571 | 0.061171 | 0.056471 | -0.0027728 | -0.0036337 | -0.00083947 | -0.0021057 | 0.00023504 | 0.071297 | 0.063559 | -0.0062463 | 0.013245 | -0.0014248 | -0.073242 | 59.5322 | -62.2513 | 59.8846 | -62.0544 | -62.5168 | -62.4939 | 0.009155 | 59.5413 | -62.3062 | 59.8114 | -62.1735 | -62.352 | -62.4252 | 0.027466 | -0.21973 | 0.13275 | 0.22431 | -0.21515 | -0.23804 | -0.24261 | -0.2655 | -0.027465 | -0.21057 | 0.059509 | 0.10529 | -0.14648 | -0.073242 | -0.11902 | -0.045777 | 0.19684 | 122.1359 | 0.13275 | 122.1176 | 121.7834 | 121.8475 | 121.8109 | 121.8201 | -122.0032 | -122.0581 | 122.1634 | 122.0901 | 62.2055 | 62.2879
72.6875 | 122.3785 | -62.2375 | 59.7656 | 0.0092313 | -0.0015743 | 0.061598 | 0.058394 | -0.0064044 | -0.0047019 | -0.0025485 | -0.0021057 | 0.0015166 | 0.072151 | 0.0689 | -0.0085961 | 0.017944 | -0.004202 | 0.018311 | 59.5596 | -62.2238 | 59.9762 | -61.9308 | -62.4298 | -62.4115 | 0.17853 | 59.5505 | -62.265 | 59.8938 | -62.0865 | -62.265 | -62.3886 | 0.013733 | -0.20599 | 0.21057 | 0.3067 | -0.17395 | -0.19226 | -0.18768 | -0.20599 | -0.027466 | -0.21515 | 0.12817 | 0.15106 | -0.15106 | -0.027466 | -0.1236 | 0 | 0.29297 | 122.2 | 0.17853 | 122.1588 | 121.7834 | 121.8155 | 121.7972 | 121.788 | -121.9894 | -122.0306 | 122.2137 | 122.1313 | 62.2559 | 62.4161
74.4375 | 122.3602 | -62.2559 | 59.7794 | 0.0016023 | -0.0017881 | 0.060103 | 0.059676 | -0.0027728 | -0.0072653 | -0.00041227 | -0.0021057 | 0.0015166 | 0.07151 | 0.066123 | -0.0083825 | 0.015808 | -0.0048428 | 0.009155 | 59.5276 | -62.233 | 59.9762 | -61.9492 | -62.4298 | -62.4069 | 0.16022 | 59.5642 | -62.2742 | 59.8892 | -62.0819 | -62.2559 | -62.3566 | 0.022888 | -0.25177 | 0.19684 | 0.3067 | -0.15106 | -0.17395 | -0.17395 | -0.19684 | -0.018311 | -0.21515 | 0.10986 | 0.17395 | -0.10071 | 0 | -0.082397 | 0.018311 | 0.28381 | 122.2092 | 0.19226 | 122.1634 | 121.7606 | 121.8384 | 121.7834 | 121.8201 | -122.0123 | -122.0535 | 122.2321 | 122.1451 | 62.265 | 62.4161
76.125 | 122.2961 | -62.2833 | 59.7519 | 0.0016023 | 0.0020571 | 0.061385 | 0.060316 | 0.00064519 | -0.0051291 | 0.00022853 | -0.0021057 | 0.00087584 | 0.069588 | 0.064841 | -0.0088097 | 0.016876 | -0.003561 | -0.082397 | 59.5001 | -62.2604 | 59.9167 | -62.0041 | -62.5076 | -62.4802 | 0.022888 | 59.5367 | -62.3016 | 59.8114 | -62.2009 | -62.3749 | -62.4207 | 0.022888 | -0.25177 | 0.1648 | 0.27924 | -0.19684 | -0.2243 | -0.21973 | -0.24719 | -0.018311 | -0.21515 | 0.059509 | 0.082397 | -0.13733 | -0.091553 | -0.11902 | -0.073242 | 0.25635 | 122.1771 | 0.10071 | 122.113 | 121.7606 | 121.8384 | 121.7834 | 121.8201 | -122.0123 | -122.0535 | 122.2 | 122.0947 | 62.2009 | 62.3062
77.8438 | 122.2229 | -62.265 | 59.8297 | -0.0060272 | -0.0015743 | 0.062025 | 0.060316 | -0.0042682 | -0.0064109 | -0.00019867 | -0.0082093 | 0.0038666 | 0.072151 | 0.059501 | -0.0083825 | 0.018372 | -0.0003568 | 0.009155 | 59.6054 | -62.2467 | 59.8709 | -62.0911 | -62.5351 | -62.5397 | 0.009155 | 59.6146 | -62.2879 | 59.7748 | -62.2101 | -62.4115 | -62.4573 | 0.018311 | -0.2243 | 0.041199 | 0.17395 | -0.27466 | -0.27008 | -0.29297 | -0.28839 | -0.022888 | -0.21515 | -0.054932 | 0.054932 | -0.19226 | -0.14648 | -0.16937 | -0.1236 | 0.15564 | 122.1176 | 0.07782 | 122.0627 | 121.8521 | 121.9025 | 121.8704 | 121.8796 | -122.0764 | -122.1176 | 122.1359 | 122.0398 | 62.2742 | 62.2742
79.5156 | 122.2961 | -62.2879 | 59.729 | -0.0060272 | 0.0035525 | 0.060316 | 0.062025 | -0.00555 | -0.0044883 | -0.0021213 | -0.0082093 | 0.0021576 | 0.071724 | 0.062064 | -0.0085961 | 0.015595 | 0.0013522 | -0.13275 | 59.5779 | -62.2696 | 59.8618 | -62.0956 | -62.5626 | -62.5534 | -0.032043 | 59.5551 | -62.3108 | 59.8114 | -62.2147 | -62.4023 | -62.4023 | 0.018311 | -0.15106 | 0.13275 | 0.19226 | -0.2655 | -0.27466 | -0.28381 | -0.29297 | -0.022888 | -0.17395 | 0.082397 | 0.073242 | -0.11444 | -0.11444 | -0.091553 | -0.091553 | 0.17395 | 122.1313 | 0.09613 | 122.1222 | 121.8475 | 121.8658 | 121.8658 | 121.843 | -121.9986 | -122.0398 | 122.1497 | 122.0993 | 62.1552 | 62.2559
81.2656 | 122.2 | -62.2696 | 59.8526 | -0.0060272 | 0.0014163 | 0.061812 | 0.060316 | -0.0025592 | -0.0051291 | 0.0012967 | 0.0009461 | 0.0021576 | 0.072578 | 0.065055 | -0.0085961 | 0.015167 | -0.0029202 | -0.013733 | 59.6283 | -62.2559 | 59.8663 | -62.0728 | -62.5214 | -62.5168 | 0.013733 | 59.6283 | -62.3062 | 59.7565 | -62.2421 | -62.4115 | -62.4527 | 0.013733 | -0.2243 | 0.013733 | 0.19684 | -0.24719 | -0.25177 | -0.26093 | -0.2655 | -0.036621 | -0.2243 | -0.09613 | 0.027466 | -0.18311 | -0.14191 | -0.14648 | -0.10529 | 0.1831 | 122.1222 | 0.064087 | 122.0627 | 121.8842 | 121.9345 | 121.8979 | 121.8979 | -122.1085 | -122.1588 | 122.1359 | 122.0261 | 62.2559 | 62.2833
83 | 122.2412 | -62.2559 | 59.7931 | -0.013657 | 0.0031253 | 0.062025 | 0.059035 | 0.00085879 | -0.0049155 | -0.0025485 | -0.0021057 | 0.001944 | 0.072365 | 0.071463 | -0.0058191 | 0.016663 | -0.0016384 | 0.013733 | 59.61 | -62.2513 | 59.9075 | -62.0453 | -62.4802 | -62.5214 | 0.059509 | 59.6146 | -62.3016 | 59.8206 | -62.178 | -62.4069 | -62.3795 | 0.004577 | -0.18311 | 0.11444 | 0.21057 | -0.2655 | -0.22431 | -0.27008 | -0.22888 | -0.045777 | -0.17853 | 0.027466 | 0.077819 | -0.1236 | -0.15106 | -0.07782 | -0.10528 | 0.20599 | 122.1588 | 0.1236 | 122.1222 | 121.8613 | 121.9162 | 121.8658 | 121.8704 | -122.0444 | -122.0947 | 122.1634 | 122.0764 | 62.2696 | 62.3154
84.6719 | 122.3236 | -62.2604 | 59.7427 | -0.013657 | 0.0037661 | 0.063094 | 0.05818 | -0.00063661 | -0.0029929 | -0.0019077 | -0.0051575 | 2.1442e-05 | 0.071724 | 0.067832 | -0.0062463 | 0.013458 | -0.0022794 | -0.07782 | 59.5184 | -62.2604 | 59.9396 | -61.9904 | -62.4847 | -62.4573 | 0.050354 | 59.5139 | -62.3245 | 59.8572 | -62.1506 | -62.3383 | -62.2375 | 0 | -0.2243 | 0.19684 | 0.27008 | -0.19684 | -0.2243 | -0.19684 | -0.2243 | -0.064087 | -0.22888 | 0.11444 | 0.10986 | 0.022888 | -0.07782 | 0.086975 | -0.013733 | 0.27008 | 122.2 | 0.17395 | 122.1817 | 121.7789 | 121.8384 | 121.7789 | 121.7743 | -122.0032 | -122.0673 | 122.2 | 122.1176 | 62.1826 | 62.3108
86.4062 | 122.3145 | -62.2604 | 59.7794 | -0.0060272 | 0.0001345 | 0.059676 | 0.058394 | -0.00020941 | -0.0042745 | -0.00041227 | -0.0021057 | 0.00087584 | 0.070656 | 0.0689 | -0.0068871 | 0.016876 | -0.005911 | 0.050354 | 59.5413 | -62.2467 | 59.9899 | -61.94 | -62.4161 | -62.4115 | 0.14191 | 59.5642 | -62.2742 | 59.8663 | -62.1185 | -62.2971 | -62.2467 | 0.013733 | -0.23804 | 0.21057 | 0.32044 | -0.15106 | -0.15564 | -0.16479 | -0.16937 | -0.013733 | -0.21515 | 0.086975 | 0.14191 | 0.013733 | -0.036621 | 0.027466 | -0.022888 | 0.3067 | 122.2366 | 0.15564 | 122.1405 | 121.788 | 121.8384 | 121.8018 | 121.8246 | -122.0261 | -122.0535 | 122.2504 | 122.1268 | 62.3108 | 62.4023
88.1562 | 122.2504 | -62.2742 | 59.8251 | 0.0016023 | 0.0046207 | 0.061385 | 0.060744 | -0.002132 | -0.0066245 | -0.0025485 | -0.0051575 | 0.0027984 | 0.07386 | 0.070823 | -0.0075281 | 0.016235 | -0.0022794 | 0.022888 | 59.5963 | -62.2513 | 59.903 | -62.0453 | -62.5031 | -62.5168 | 0.073242 | 59.61 | -62.3062 | 59.8251 | -62.1872 | -62.3978 | -62.3611 | 0.022888 | -0.22888 | 0.07782 | 0.22888 | -0.24262 | -0.22888 | -0.2655 | -0.25177 | -0.032043 | -0.21515 | 0 | 0.086975 | -0.086975 | -0.1236 | -0.054932 | -0.091553 | 0.20599 | 122.1542 | 0.11902 | 122.1313 | 121.8475 | 121.9162 | 121.8704 | 121.8842 | -122.0764 | -122.1313 | 122.1771 | 122.0993 | 62.2971 | 62.3474
89.9062 | 122.2412 | -62.2742 | 59.8022 | -0.0060272 | 0.0029117 | 0.062025 | 0.061812 | 0.002995 | -0.0055563 | -0.0029759 | -0.0021057 | 0.003653 | 0.072792 | 0.064414 | -0.0068871 | 0.016022 | -0.000784 | 0.004578 | 59.6191 | -62.233 | 59.903 | -62.0224 | -62.5122 | -62.5168 | 0.054932 | 59.5963 | -62.3062 | 59.7977 | -62.1918 | -62.4161 | -62.3978 | 0.041199 | -0.1831 | 0.10071 | 0.25177 | -0.24262 | -0.23804 | -0.28381 | -0.27924 | -0.032043 | -0.20599 | -0.004578 | 0.082398 | -0.1236 | -0.14191 | -0.091553 | -0.10986 | 0.21057 | 122.1359 | 0.11444 | 122.1039 | 121.8521 | 121.9025 | 121.8933 | 121.8704 | -122.0352 | -122.1085 | 122.1771 | 122.0718 | 62.2787 | 62.3291
91.5938 | 122.3419 | -62.2513 | 59.7565 | -0.0060272 | -0.0020017 | 0.06053 | 0.059248 | -0.00020941 | -0.0053427 | -0.00019867 | -0.0051575 | 0.00044864 | 0.07151 | 0.067191 | -0.0083825 | 0.015808 | -0.0018522 | 0.036621 | 59.5139 | -62.2467 | 59.9945 | -61.8942 | -62.3932 | -62.4069 | 0.15564 | 59.5688 | -62.2879 | 59.8709 | -62.0819 | -62.2787 | -62.3154 | 0.004578 | -0.24262 | 0.23804 | 0.35706 | -0.15564 | -0.14191 | -0.16022 | -0.14648 | -0.036621 | -0.18768 | 0.11444 | 0.16937 | -0.064087 | -0.027466 | -0.027466 | 0.009155 | 0.35248 | 122.2412 | 0.20599 | 122.1588 | 121.7606 | 121.8567 | 121.7651 | 121.8201 | -122.0032 | -122.0444 | 122.2458 | 122.1222 | 62.2879 | 62.4069
93.3438 | 122.3373 | -62.2284 | 59.7565 | -0.0060272 | -0.0020017 | 0.060957 | 0.057753 | -0.0061908 | -0.0074789 | -0.00062587 | -0.0021057 | 0.00044864 | 0.07151 | 0.055442 | -0.0068871 | 0.016022 | -0.0003568 | 0.022888 | 59.5367 | -62.2101 | 59.9854 | -61.9125 | -62.4115 | -62.4069 | 0.16022 | 59.5551 | -62.2833 | 59.8663 | -62.1002 | -62.2787 | -62.3199 | 0.018311 | -0.21973 | 0.22888 | 0.31586 | -0.17853 | -0.1831 | -0.19684 | -0.20142 | -0.054931 | -0.20142 | 0.10986 | 0.12817 | -0.091552 | -0.050354 | -0.036621 | 0.004577 | 0.29755 | 122.1954 | 0.1831 | 122.1497 | 121.7468 | 121.8384 | 121.7651 | 121.7834 | -121.9666 | -122.0398 | 122.2137 | 122.0947 | 62.2513 | 62.3886
95.0781 | 122.2092 | -62.3154 | 59.7794 | -0.013657 | 0.0018435 | 0.061171 | 0.06288 | -0.00020941 | -0.0036337 | -0.0029759 | -0.0051575 | 0.0027984 | 0.073219 | 0.062705 | -0.0094507 | 0.015808 | 0.002634 | -0.1236 | 59.5779 | -62.2925 | 59.816 | -62.1368 | -62.6083 | -62.5992 | -0.10071 | 59.5779 | -62.3337 | 59.7473 | -62.2833 | -62.4802 | -62.4573 | 0.022889 | -0.20142 | 0.036621 | 0.17853 | -0.28381 | -0.29297 | -0.3067 | -0.31586 | -0.01831 | -0.20142 | -0.032044 | 0.032044 | -0.14191 | -0.1648 | -0.1236 | -0.14649 | 0.15564 | 122.1085 | 0.050354 | 122.081 | 121.8704 | 121.9116 | 121.8933 | 121.8933 | -122.0718 | -122.113 | 122.1313 | 122.0627 | 62.1918 | 62.2147
96.7656 | 122.2 | -62.2879 | 59.7931 | -0.013657 | 0.0020571 | 0.062666 | 0.063094 | -0.0023456 | -0.0019247 | -0.0027621 | -0.0051575 | 0.003653 | 0.070869 | 0.077445 | -0.0071009 | 0.016663 | 0.0022068 | -0.068665 | 59.6008 | -62.2513 | 59.8663 | -62.1048 | -62.5763 | -62.5809 | -0.064087 | 59.6008 | -62.3199 | 59.7427 | -62.2696 | -62.4664 | -62.4664 | 0.036621 | -0.19226 | 0.073242 | 0.18311 | -0.29297 | -0.28839 | -0.32959 | -0.32501 | -0.032043 | -0.19226 | -0.050354 | 0.018311 | -0.17853 | -0.17853 | -0.14648 | -0.14648 | 0.14649 | 122.1176 | 0.050354 | 122.0627 | 121.8521 | 121.9208 | 121.8887 | 121.8887 | -122.0444 | -122.113 | 122.1542 | 122.0306 | 62.2192 | 62.2238
98.5156 | 122.2824 | -62.2742 | 59.7702 | -0.0060272 | 0.0003483 | 0.061812 | 0.059035 | -0.0032 | -0.0047019 | -0.0036167 | -0.0021057 | 2.1442e-05 | 0.073433 | 0.059714 | -0.0088097 | 0.016022 | 0.000925 | -0.086975 | 59.5367 | -62.265 | 59.8984 | -62.0453 | -62.5076 | -62.4985 | -0.013733 | 59.5551 | -62.3199 | 59.7931 | -62.1826 | -62.3749 | -62.4252 | 0.009155 | -0.23346 | 0.12817 | 0.22888 | -0.2243 | -0.23346 | -0.23346 | -0.24261 | -0.045776 | -0.21515 | 0.022888 | 0.091553 | -0.15106 | -0.10071 | -0.10529 | -0.054932 | 0.21973 | 122.1634 | 0.13733 | 122.113 | 121.8018 | 121.875 | 121.8109 | 121.8292 | -122.0352 | -122.0901 | 122.1725 | 122.0673 | 62.1872 | 62.2604
100.2031 | 122.2549 | -62.2604 | 59.8206 | -0.0060272 | 0.0024845 | 0.062025 | 0.059248 | -0.001491 | -0.0049155 | -0.0031895 | 0.0009461 | 0.0015166 | 0.07151 | 0.072318 | -0.0085961 | 0.015381 | 0.0024204 | 0.013733 | 59.5917 | -62.2467 | 59.8984 | -62.0499 | -62.5122 | -62.5259 | 0.073242 | 59.5963 | -62.2925 | 59.8114 | -62.2009 | -62.3886 | -62.4252 | 0.013733 | -0.22888 | 0.077819 | 0.21057 | -0.2655 | -0.25177 | -0.27924 | -0.2655 | -0.032043 | -0.22431 | -0.009156 | 0.059509 | -0.16479 | -0.12817 | -0.13275 | -0.096131 | 0.19684 | 122.1451 | 0.091552 | 122.1039 | 121.8384 | 121.8887 | 121.8521 | 121.8567 | -122.0673 | -122.113 | 122.1588 | 122.0718 | 62.2742 | 62.3337
101.9531 | 122.2916 | -62.2925 | 59.7702 | -0.0060272 | 0.0014163 | 0.062239 | 0.057967 | -0.0042682 | -0.0021383 | -0.0016941 | -0.0051575 | -0.00061956 | 0.070656 | 0.059928 | -0.0066735 | 0.017303 | -0.0009976 | -0.073242 | 59.5505 | -62.2513 | 59.8801 | -62.0453 | -62.5259 | -62.4893 | 0.009155 | 59.5413 | -62.3016 | 59.7977 | -62.1872 | -62.3749 | -62.4344 | 0.041198 | -0.21973 | 0.10986 | 0.24719 | -0.19684 | -0.23346 | -0.23804 | -0.27466 | -0.009156 | -0.22888 | 0.027465 | 0.10528 | -0.14191 | -0.082398 | -0.13275 | -0.073242 | 0.20599 | 122.1313 | 0.11444 | 122.0993 | 121.8018 | 121.843 | 121.843 | 121.8338 | -122.0215 | -122.0718 | 122.1725 | 122.0901 | 62.2192 | 62.3016
103.625 | 122.2275 | -62.2742 | 59.8343 | -0.013657 | -0.0007199 | 0.061385 | 0.060744 | 0.00043159 | -0.0072653 | -0.0036167 | -0.0021057 | 0.0042938 | 0.073219 | 0.067405 | -0.0088097 | 0.016449 | -0.000784 | -0.004578 | 59.61 | -62.2604 | 59.8572 | -62.0956 | -62.5397 | -62.5259 | 0.009155 | 59.6283 | -62.3108 | 59.7702 | -62.2238 | -62.4161 | -62.4573 | 0.013733 | -0.22431 | 0.022888 | 0.17853 | -0.25177 | -0.2655 | -0.2655 | -0.27924 | -0.036621 | -0.20599 | -0.064087 | 0.050354 | -0.18311 | -0.14191 | -0.14648 | -0.10529 | 0.1648 | 122.1176 | 0.086975 | 122.081 | 121.8704 | 121.9391 | 121.8842 | 121.9025 | -122.0947 | -122.1451 | 122.1313 | 122.0444 | 62.2696 | 62.2833
105.3125 | 122.3328 | -62.2833 | 59.7336 | -0.0060272 | 0.0048343 | 0.064589 | 0.059462 | 0.00021799 | -0.0049155 | -0.0012669 | -0.0082093 | 0.0021576 | 0.07151 | 0.063132 | -0.0098779 | 0.015595 | 0.0024204 | -0.10071 | 59.5276 | -62.265 | 59.935 | -62.0132 | -62.4893 | -62.4847 | 0.032043 | 59.5322 | -62.2971 | 59.8251 | -62.1689 | -62.3611 | -62.3749 | 0.01831 | -0.20599 | 0.20142 | 0.27008 | -0.20142 | -0.20599 | -0.21973 | -0.2243 | -0.013733 | -0.20142 | 0.091552 | 0.11444 | -0.091553 | -0.07782 | -0.07782 | -0.064087 | 0.25177 | 122.2 | 0.12817 | 122.1222 | 121.7926 | 121.8292 | 121.8109 | 121.8155 | -121.9986 | -122.0306 | 122.2183 | 122.1085 | 62.1826 | 62.3154
107.0625 | 122.2824 | -62.2604 | 59.7382 | -0.013657 | 0.0007755 | 0.062025 | 0.058607 | -0.001491 | -0.0034201 | -0.0012669 | -0.0051575 | 0.00044864 | 0.073006 | 0.064627 | -0.0071009 | 0.016022 | -0.000784 | -0.091553 | 59.523 | -62.2375 | 59.9258 | -62.0407 | -62.5168 | -62.4847 | 0.009155 | 59.5322 | -62.3016 | 59.8068 | -62.2009 | -62.3703 | -62.4344 | 0.022888 | -0.21515 | 0.18768 | 0.21973 | -0.2243 | -0.25635 | -0.24719 | -0.27924 | -0.041199 | -0.20599 | 0.068665 | 0.059509 | -0.17395 | -0.10986 | -0.13275 | -0.068664 | 0.19684 | 122.1634 | 0.10071 | 122.1085 | 121.7606 | 121.8338 | 121.7834 | 121.7926 | -121.9757 | -122.0398 | 122.1863 | 122.0673 | 62.1689 | 62.2696
108.8125 | 122.3694 | -62.2467 | 59.7427 | -0.0060272 | -0.0002927 | 0.060316 | 0.058607 | -0.0023456 | -0.0021383 | -0.0029759 | -0.0082093 | 0.001944 | 0.070015 | 0.0642 | -0.0083825 | 0.015167 | -0.0044156 | 0.009155 | 59.5367 | -62.2467 | 59.9625 | -61.9537 | -62.4207 | -62.4298 | 0.14191 | 59.5642 | -62.2833 | 59.8938 | -62.1094 | -62.2787 | -62.3657 | 0 | -0.20599 | 0.21973 | 0.29297 | -0.18311 | -0.17395 | -0.18311 | -0.17395 | -0.036621 | -0.17853 | 0.15106 | 0.13733 | -0.11902 | -0.032044 | -0.082398 | 0.004577 | 0.29297 | 122.2092 | 0.17395 | 122.1771 | 121.7834 | 121.8475 | 121.7834 | 121.8109 | -121.9894 | -122.0261 | 122.2092 | 122.1405 | 62.2559 | 62.3886
110.5156 | 122.3053 | -62.2742 | 59.7473 | -0.013657 | 0.0003483 | 0.060744 | 0.059676 | -0.0040546 | -0.0042745 | -0.0025485 | -0.0021057 | 0.00066224 | 0.070015 | 0.062705 | -0.0083825 | 0.015381 | -0.0039884 | -0.064087 | 59.5367 | -62.2559 | 59.8938 | -62.0544 | -62.5168 | -62.4939 | 0.013733 | 59.5551 | -62.3062 | 59.8251 | -62.1643 | -62.3566 | -62.4207 | 0.018311 | -0.21057 | 0.14648 | 0.21973 | -0.21973 | -0.24262 | -0.23804 | -0.26093 | -0.032043 | -0.19226 | 0.07782 | 0.10986 | -0.14648 | -0.082397 | -0.11444 | -0.050354 | 0.20142 | 122.1497 | 0.14191 | 122.1313 | 121.7926 | 121.8613 | 121.8109 | 121.8292 | -122.0032 | -122.0535 | 122.168 | 122.0993 | 62.2101 | 62.2879
112.2031 | 122.3373 | -62.2833 | 59.697 | -0.0060272 | 0.0018435 | 0.063094 | 0.060957 | 0.0025678 | -0.0055563 | -0.0057529 | -0.0051575 | 0.0038666 | 0.074287 | 0.068259 | -0.0096643 | 0.016235 | -0.0048428 | -0.068665 | 59.5139 | -62.2467 | 59.935 | -62.0087 | -62.4985 | -62.4664 | 0.045776 | 59.5413 | -62.3108 | 59.8526 | -62.1689 | -62.3566 | -62.3886 | 0.036621 | -0.1831 | 0.23804 | 0.27466 | -0.18311 | -0.21515 | -0.21973 | -0.25177 | -0.027466 | -0.15564 | 0.15564 | 0.11444 | -0.10529 | -0.073242 | -0.07782 | -0.045776 | 0.23804 | 122.1817 | 0.14191 | 122.1634 | 121.7606 | 121.8521 | 121.7972 | 121.8246 | -121.9437 | -122.0078 | 122.2183 | 122.1359 | 62.2147 | 62.3291
113.9375 | 122.3053 | -62.2971 | 59.7473 | -0.013657 | 0.0018435 | 0.062025 | 0.060103 | 0.0017132 | -0.0070517 | -0.0010531 | -0.0051575 | 0.0015166 | 0.070229 | 0.061209 | -0.0060327 | 0.016449 | -0.002493 | -0.082397 | 59.5413 | -62.2421 | 59.9075 | -62.0407 | -62.5397 | -62.4847 | 0.013733 | 59.5413 | -62.3016 | 59.8114 | -62.1964 | -62.3886 | -62.439 | 0.054932 | -0.20599 | 0.16022 | 0.25635 | -0.18768 | -0.24262 | -0.24262 | -0.29755 | -0.004578 | -0.20599 | 0.064087 | 0.10071 | -0.14191 | -0.091553 | -0.13733 | -0.086975 | 0.20142 | 122.1497 | 0.10529 | 122.113 | 121.7834 | 121.843 | 121.8384 | 121.8384 | -121.9894 | -122.049 | 122.2046 | 122.1085 | 62.2147 | 62.3108
115.6719 | 122.2824 | -62.2742 | 59.7702 | -0.0060272 | 0.0009891 | 0.062239 | 0.060103 | -0.00042301 | -0.0047019 | -0.0012669 | -0.0021057 | 0.0017304 | 0.072792 | 0.067405 | -0.0085961 | 0.016876 | -0.0027066 | -0.086975 | 59.5367 | -62.265 | 59.8846 | -62.0499 | -62.5168 | -62.4939 | 0.004578 | 59.5413 | -62.2879 | 59.8022 | -62.2009 | -62.3657 | -62.439 | 0.009155 | -0.23346 | 0.11444 | 0.2243 | -0.21973 | -0.24262 | -0.22888 | -0.25177 | -0.013733 | -0.22888 | 0.032043 | 0.073242 | -0.1648 | -0.091553 | -0.15106 | -0.07782 | 0.21515 | 122.1497 | 0.086975 | 122.0901 | 121.8018 | 121.8292 | 121.8109 | 121.8155 | -122.0352 | -122.0581 | 122.1588 | 122.0764 | 62.1872 | 62.2787
117.3594 | 122.2412 | -62.2971 | 59.7656 | -0.0060272 | 0.0022709 | 0.06288 | 0.062239 | -0.0019184 | -0.0044883 | 0.00086953 | 0.0009461 | 0.0027984 | 0.07386 | 0.067405 | -0.0085961 | 0.016876 | -0.0014248 | -0.14191 | 59.5917 | -62.2971 | 59.8343 | -62.1231 | -62.5809 | -62.5854 | -0.07782 | 59.5825 | -62.3428 | 59.7702 | -62.2696 | -62.4527 | -62.4756 | 0 | -0.17395 | 0.068665 | 0.17395 | -0.28839 | -0.28381 | -0.28839 | -0.28381 | -0.045776 | -0.1831 | 0.004578 | 0.027466 | -0.17853 | -0.15564 | -0.13275 | -0.10986 | 0.17395 | 122.1313 | 0.073242 | 122.113 | 121.8887 | 121.9254 | 121.8887 | 121.8796 | -122.0627 | -122.1085 | 122.1313 | 122.0673 | 62.1552 | 62.2192
119.1094 | 122.2458 | -62.2742 | 59.7977 | -0.0060272 | 0.0026981 | 0.061385 | 0.062025 | 0.0023542 | -0.0036337 | 0.00022853 | -0.0021057 | 0.003012 | 0.070656 | 0.072745 | -0.0075281 | 0.016876 | -0.0014248 | -0.004578 | 59.5825 | -62.2513 | 59.9258 | -62.0224 | -62.5031 | -62.4985 | 0.059509 | 59.5779 | -62.2971 | 59.8068 | -62.2192 | -62.3886 | -62.4298 | 0.022888 | -0.21515 | 0.12817 | 0.25177 | -0.2243 | -0.22888 | -0.24719 | -0.25177 | -0.022888 | -0.21973 | 0.009156 | 0.054932 | -0.15564 | -0.11444 | -0.13275 | -0.091553 | 0.22888 | 122.1771 | 0.07782 | 122.1039 | 121.8338 | 121.875 | 121.8567 | 121.8521 | -122.049 | -122.0947 | 122.2 | 122.081 | 62.2696 | 62.3337
120.7969 | 122.2641 | -62.2467 | 59.8297 | -0.013657 | 0.0018435 | 0.062025 | 0.061385 | -0.0036274 | -0.0034201 | -0.0021213 | -0.0051575 | 0.0034392 | 0.072792 | 0.064414 | -0.0075281 | 0.015167 | -0.0033474 | 0.009155 | 59.5963 | -62.233 | 59.8846 | -62.0728 | -62.5076 | -62.5076 | 0.013733 | 59.6329 | -62.3016 | 59.8068 | -62.1964 | -62.3932 | -62.439 | 0.013733 | -0.23346 | 0.054932 | 0.17395 | -0.26093 | -0.26093 | -0.27466 | -0.27466 | -0.054932 | -0.19684 | -0.022888 | 0.050354 | -0.19226 | -0.14648 | -0.13733 | -0.091552 | 0.16022 | 122.1176 | 0.10529 | 122.1085 | 121.8292 | 121.9345 | 121.843 | 121.8796 | -122.0627 | -122.1313 | 122.1313 | 122.0535 | 62.2559 | 62.2604
122.7031 | 122.2504 | -62.2467 | 59.8251 | 0.0092313 | 0.0022709 | 0.061385 | 0.061598 | -0.0010638 | -0.0049155 | -0.0036167 | -0.0021057 | 0.001944 | 0.074074 | 0.073386 | -0.0068871 | 0.015595 | -0.0018522 | 0.013733 | 59.6191 | -62.233 | 59.8801 | -62.0911 | -62.5214 | -62.5214 | 0.036621 | 59.6146 | -62.2879 | 59.7885 | -62.1918 | -62.4023 | -62.4298 | 0.013733 | -0.20599 | 0.054932 | 0.15564 | -0.27466 | -0.27466 | -0.28839 | -0.28839 | -0.041199 | -0.21057 | -0.036621 | 0.054932 | -0.18311 | -0.15564 | -0.14191 | -0.11444 | 0.14191 | 122.113 | 0.096131 | 122.0764 | 121.8521 | 121.9025 | 121.8658 | 121.8613 | -122.0581 | -122.113 | 122.1268 | 122.0352 | 62.2604 | 62.2833
124.4688 | 122.2504 | -62.2833 | 59.7931 | -0.0060272 | 0.0033389 | 0.062025 | 0.061812 | -0.00020941 | -0.0025655 | -0.0021213 | 0.0009461 | 0.003012 | 0.073647 | 0.067618 | -0.0083825 | 0.016876 | -0.0020658 | 0.018311 | 59.5825 | -62.2421 | 59.9075 | -62.0361 | -62.5031 | -62.5122 | 0.050354 | 59.5963 | -62.2879 | 59.816 | -62.178 | -62.3657 | -62.4115 | 0.041199 | -0.21057 | 0.11444 | 0.24719 | -0.22888 | -0.21973 | -0.27008 | -0.26093 | -0.004578 | -0.19684 | 0.022888 | 0.10528 | -0.12817 | -0.082398 | -0.1236 | -0.07782 | 0.20599 | 122.1497 | 0.10986 | 122.1039 | 121.8246 | 121.8842 | 121.8658 | 121.8796 | -122.0352 | -122.081 | 122.1909 | 122.0993 | 62.3016 | 62.3337
126.1562 | 122.2961 | -62.2971 | 59.7656 | -0.0060272 | 0.0031253 | 0.061385 | 0.059462 | -0.00020941 | -0.0053427 | -0.0029759 | -0.0051575 | 0.001303 | 0.07386 | 0.062491 | -0.0066735 | 0.013458 | -0.0003568 | -0.082397 | 59.5459 | -62.265 | 59.8984 | -62.0087 | -62.5214 | -62.4847 | 0.018311 | 59.5139 | -62.3199 | 59.8068 | -62.1964 | -62.3657 | -62.4069 | 0.032043 | -0.21973 | 0.13275 | 0.28839 | -0.18768 | -0.2243 | -0.21973 | -0.25635 | -0.022888 | -0.25177 | 0.041199 | 0.10071 | -0.10986 | -0.068665 | -0.086975 | -0.045777 | 0.25635 | 122.1634 | 0.1236 | 122.1268 | 121.8109 | 121.8338 | 121.843 | 121.8109 | -122.0306 | -122.0856 | 122.1954 | 122.1039 | 62.2147 | 62.3154
127.8906 | 122.3282 | -62.2467 | 59.7702 | -0.013657 | -0.0007199 | 0.062666 | 0.058607 | -0.001491 | -0.0070517 | -0.0016941 | -0.0021057 | -0.00019216 | 0.072151 | 0.061423 | -0.0079553 | 0.016663 | -0.0022794 | 0.050354 | 59.5642 | -62.2375 | 59.9854 | -61.94 | -62.4207 | -62.4069 | 0.16479 | 59.5688 | -62.2604 | 59.8618 | -62.1231 | -62.2925 | -62.3703 | 0.009155 | -0.20599 | 0.21515 | 0.3067 | -0.16022 | -0.17395 | -0.16937 | -0.1831 | -0.013733 | -0.20142 | 0.091552 | 0.1236 | -0.1236 | -0.045776 | -0.10986 | -0.032043 | 0.29755 | 122.2229 | 0.13733 | 122.1222 | 121.8018 | 121.8292 | 121.8109 | 121.8155 | -122.0078 | -122.0306 | 122.2321 | 122.1085 | 62.2971 | 62.4115
129.625 | 122.2183 | -62.2238 | 59.8068 | -0.0060272 | 0.0024845 | 0.061385 | 0.059889 | -0.0017048 | -0.0053427 | -0.0044711 | -0.0021057 | 0.0010894 | 0.074074 | 0.06655 | -0.0088097 | 0.015595 | -0.0027066 | 0.068665 | 59.5551 | -62.2421 | 59.9396 | -61.9904 | -62.4619 | -62.439 | 0.10529 | 59.6191 | -62.2696 | 59.7931 | -62.1826 | -62.3749 | -62.4527 | -0.01831 | -0.25177 | 0.13275 | 0.23346 | -0.21515 | -0.23804 | -0.19684 | -0.21973 | -0.045776 | -0.18768 | -0.013733 | 0.041199 | -0.22888 | -0.15106 | -0.18311 | -0.10529 | 0.25177 | 122.1817 | 0.086975 | 122.0627 | 121.7972 | 121.8887 | 121.7789 | 121.843 | -122.0489 | -122.0764 | 122.1634 | 122.0169 | 62.2925 | 62.3291
131.3125 | 122.3328 | -62.2971 | 59.7336 | 0.0016023 | 0.0012027 | 0.063948 | 0.058821 | -0.00063661 | -0.0038473 | 0.00065573 | -0.0082093 | 0.00044864 | 0.069588 | 0.06655 | -0.0083825 | 0.015595 | -0.0037748 | -0.07782 | 59.4955 | -62.2467 | 59.9533 | -62.0087 | -62.4847 | -62.4573 | 0.054932 | 59.5367 | -62.2925 | 59.848 | -62.1506 | -62.3383 | -62.4069 | 0.050354 | -0.23804 | 0.21973 | 0.28839 | -0.16022 | -0.18768 | -0.21057 | -0.23804 | 0.004578 | -0.19684 | 0.11444 | 0.14648 | -0.10986 | -0.041199 | -0.11444 | -0.045777 | 0.23804 | 122.2 | 0.14191 | 122.1405 | 121.7422 | 121.8292 | 121.7926 | 121.8338 | -121.9803 | -122.0261 | 122.2504 | 122.1451 | 62.2192 | 62.352
133.0625 | 122.3145 | -62.2971 | 59.7427 | -0.0060272 | 0.0014163 | 0.062666 | 0.060957 | -0.00085021 | -0.0053427 | -0.0019077 | 0.0009461 | 0.00066224 | 0.073647 | 0.064414 | -0.0075281 | 0.016876 | -0.0033474 | -0.068665 | 59.5276 | -62.2513 | 59.9258 | -62.0041 | -62.5031 | -62.4664 | 0.050354 | 59.5139 | -62.2971 | 59.8297 | -62.1689 | -62.3611 | -62.4252 | 0.045776 | -0.21515 | 0.18311 | 0.29297 | -0.16937 | -0.20599 | -0.21515 | -0.25177 | 0 | -0.22888 | 0.086975 | 0.12817 | -0.12817 | -0.064087 | -0.12817 | -0.064087 | 0.24719 | 122.1771 | 0.12817 | 122.1268 | 121.7789 | 121.8109 | 121.8246 | 121.8109 | -121.994 | -122.0398 | 122.2229 | 122.1268 | 62.2284 | 62.3474
134.75 | 122.3557 | -62.2467 | 59.7427 | 0.0016023 | -0.0017881 | 0.059462 | 0.06053 | 0.00021799 | -0.0061971 | -0.0021213 | -0.0021057 | 0.0021576 | 0.070656 | 0.063346 | -0.0077417 | 0.014099 | -0.0009976 | -0.009155 | 59.5276 | -62.2604 | 59.9579 | -61.9583 | -62.4207 | -62.4207 | 0.11902 | 59.5688 | -62.2742 | 59.8618 | -62.1231 | -62.2787 | -62.3657 | -0.013733 | -0.21515 | 0.21515 | 0.28839 | -0.17395 | -0.17395 | -0.16022 | -0.16022 | -0.027466 | -0.17395 | 0.11902 | 0.1236 | -0.11902 | -0.032044 | -0.091553 | -0.004578 | 0.30212 | 122.2183 | 0.15106 | 122.1359 | 121.788 | 121.843 | 121.7743 | 121.8155 | -122.0032 | -122.0169 | 122.2046 | 122.1085 | 62.2375 | 62.3657
136.5 | 122.2549 | -62.2925 | 59.8251 | -0.0060272 | 0.0024845 | 0.061812 | 0.059889 | -0.0032 | -0.0049155 | -0.00083947 | -0.0051575 | 0.0038666 | 0.070656 | 0.068473 | -0.010092 | 0.015808 | -0.0044156 | 0.013733 | 59.6008 | -62.2604 | 59.8846 | -62.0544 | -62.5031 | -62.5168 | 0.036621 | 59.6466 | -62.2833 | 59.7931 | -62.2101 | -62.3978 | -62.439 | 0.032043 | -0.2243 | 0.05951 | 0.23804 | -0.22431 | -0.21057 | -0.25635 | -0.24261 | 0.009155 | -0.17853 | -0.032043 | 0.082397 | -0.14649 | -0.10529 | -0.15564 | -0.11444 | 0.20599 | 122.1451 | 0.073242 | 122.0764 | 121.8613 | 121.9299 | 121.8933 | 121.9391 | -122.0856 | -122.1085 | 122.1771 | 122.0856 | 62.3062 | 62.3291
138.1875 | 122.3602 | -62.2559 | 59.7565 | 0.0016023 | 0.0003483 | 0.062453 | 0.057967 | -0.0025592 | -0.0064109 | -0.0025485 | 0.0009461 | -0.0010468 | 0.071083 | 0.067191 | -0.0077417 | 0.015167 | 0.002634 | 0.027466 | 59.5276 | -62.2284 | 60.0174 | -61.9034 | -62.384 | -62.384 | 0.15564 | 59.5642 | -62.2971 | 59.8755 | -62.0911 | -62.2787 | -62.3657 | 0.027465 | -0.22888 | 0.26093 | 0.35248 | -0.12817 | -0.12817 | -0.15564 | -0.15564 | -0.041199 | -0.19226 | 0.11902 | 0.16479 | -0.10986 | -0.022889 | -0.068665 | 0.01831 | 0.32501 | 122.2458 | 0.20599 | 122.1725 | 121.756 | 121.8613 | 121.7834 | 121.8201 | -121.9849 | -122.0535 | 122.2733 | 122.1313 | 62.2833 | 62.4115
139.9219 | 122.3557 | -62.2375 | 59.7885 | -0.0060272 | 0.0014163 | 0.061385 | 0.058394 | -0.004909 | -0.0053427 | -0.0025485 | -0.0051575 | 0.00066224 | 0.073433 | 0.06655 | -0.0088097 | 0.013245 | -0.0039884 | 0.018311 | 59.5505 | -62.2147 | 59.9579 | -61.9446 | -62.4207 | -62.4115 | 0.15106 | 59.5367 | -62.2833 | 59.8709 | -62.1002 | -62.2696 | -62.3611 | 0.022888 | -0.23804 | 0.16937 | 0.29297 | -0.17395 | -0.1831 | -0.19684 | -0.20599 | -0.045776 | -0.25177 | 0.082398 | 0.13733 | -0.1236 | -0.032043 | -0.07782 | 0.013733 | 0.27008 | 122.1725 | 0.1831 | 122.1542 | 121.7651 | 121.8201 | 121.788 | 121.7743 | -122.0032 | -122.0718 | 122.1954 | 122.1085 | 62.2559 | 62.3886
141.6562 | 122.2504 | -62.2559 | 59.8251 | -0.0060272 | 0.0029117 | 0.063307 | 0.059462 | 0.0014996 | -0.0083335 | 0.00022853 | 0.0009461 | 0.003012 | 0.070229 | 0.058432 | -0.0090235 | 0.016449 | -0.0012112 | 0.068665 | 59.5779 | -62.2147 | 59.9625 | -61.9995 | -62.4527 | -62.4619 | 0.10529 | 59.6008 | -62.3016 | 59.8022 | -62.1918 | -62.3795 | -62.4527 | 0.041198 | -0.24719 | 0.13733 | 0.25635 | -0.20599 | -0.19684 | -0.24719 | -0.23804 | -0.045777 | -0.2243 | -0.022888 | 0.064087 | -0.19684 | -0.1236 | -0.15106 | -0.07782 | 0.21515 | 122.1771 | 0.10986 | 122.1039 | 121.7926 | 121.9025 | 121.8338 | 121.8567 | -122.0398 | -122.1268 | 122.2183 | 122.0581 | 62.3245 | 62.3611
143.3438 | 122.2229 | -62.3154 | 59.7519 | -0.0060272 | 0.0037661 | 0.062453 | 0.062239 | 4.192e-06 | -0.0047019 | -0.0014805 | -0.0021057 | 0.0034392 | 0.072365 | 0.070395 | -0.0077417 | 0.016235 | -0.0003568 | -0.13275 | 59.6008 | -62.2833 | 59.8206 | -62.1323 | -62.5992 | -62.5763 | -0.073242 | 59.6146 | -62.3016 | 59.7519 | -62.2742 | -62.4664 | -62.5076 | 0.032044 | -0.15106 | 0.068665 | 0.18311 | -0.26093 | -0.28381 | -0.29297 | -0.31586 | 0.013733 | -0.13733 | 0 | 0.041199 | -0.19226 | -0.15106 | -0.20599 | -0.16479 | 0.15106 | 122.1039 | 0.027466 | 122.0535 | 121.8842 | 121.9162 | 121.9162 | 121.9299 | -122.0352 | -122.0535 | 122.1359 | 122.0673 | 62.1826 | 62.2421
145.1094 | 122.2504 | -62.2925 | 59.7931 | -0.0060272 | 0.0039799 | 0.061598 | 0.062025 | 0.0014996 | -0.0055563 | -0.0014805 | -0.0051575 | 0.0027984 | 0.072151 | 0.069754 | -0.0092371 | 0.016235 | -0.0016384 | -0.022888 | 59.6146 | -62.2467 | 59.9213 | -62.027 | -62.5168 | -62.5076 | 0.045776 | 59.5779 | -62.2971 | 59.7977 | -62.2055 | -62.4023 | -62.4527 | 0.045776 | -0.17853 | 0.12817 | 0.2655 | -0.21515 | -0.22431 | -0.26093 | -0.27008 | -0.004578 | -0.21515 | 0.004577 | 0.086975 | -0.16022 | -0.10986 | -0.15564 | -0.10529 | 0.21973 | 122.168 | 0.091553 | 122.0947 | 121.8613 | 121.875 | 121.907 | 121.8704 | -122.0398 | -122.0901 | 122.2137 | 122.0901 | 62.2696 | 62.3383
146.7969 | 122.2321 | -62.2604 | 59.8206 | -0.013657 | -0.0017881 | 0.061385 | 0.057967 | 0.0049176 | -0.0066245 | -0.0031895 | -0.0051575 | 0.00023504 | 0.07386 | 0.066977 | -0.0068871 | 0.01474 | -0.0001432 | 0.054932 | 59.5688 | -62.2467 | 59.9442 | -61.9949 | -62.4481 | -62.4344 | 0.11444 | 59.5917 | -62.2925 | 59.7839 | -62.1735 | -62.3703 | -62.4481 | 0.013733 | -0.25177 | 0.1236 | 0.2655 | -0.17395 | -0.18768 | -0.18768 | -0.20142 | -0.032043 | -0.22888 | -0.036621 | 0.086975 | -0.18768 | -0.10986 | -0.15564 | -0.07782 | 0.25177 | 122.1909 | 0.11902 | 122.0764 | 121.8155 | 121.8842 | 121.8292 | 121.8521 | -122.0673 | -122.113 | 122.2046 | 122.0444 | 62.3154 | 62.3749
148.5312 | 122.3602 | -62.2742 | 59.7931 | -0.0060272 | 0.0007755 | 0.061171 | 0.057112 | -0.00085021 | -0.0064109 | -0.0042575 | -0.0021057 | 0.0017304 | 0.074287 | 0.059073 | -0.0068871 | 0.016876 | -0.0016384 | 0.018311 | 59.5459 | -62.2513 | 59.9762 | -61.9354 | -62.4115 | -62.4069 | 0.17395 | 59.5551 | -62.2742 | 59.8846 | -62.0865 | -62.2604 | -62.3657 | 0.022888 | -0.24719 | 0.18311 | 0.33874 | -0.13275 | -0.13733 | -0.15564 | -0.16022 | 0 | -0.23804 | 0.091553 | 0.18768 | -0.091553 | 0.013733 | -0.091553 | 0.013733 | 0.31586 | 122.2275 | 0.18768 | 122.1588 | 121.7972 | 121.8292 | 121.8201 | 121.8292 | -122.0444 | -122.0673 | 122.2504 | 122.1588 | 62.2925 | 62.4481
150.2188 | 122.2458 | -62.2833 | 59.7839 | -0.013657 | 0.0018435 | 0.062666 | 0.061385 | -0.00042301 | -0.0055563 | -0.0019077 | 0.0009461 | 0.005362 | 0.073006 | 0.067618 | -0.0077417 | 0.017731 | -0.0014248 | -0.009155 | 59.5917 | -62.2559 | 59.9075 | -62.0453 | -62.5214 | -62.5168 | 0.054932 | 59.6191 | -62.2604 | 59.7702 | -62.2192 | -62.4298 | -62.471 | 0.027466 | -0.19226 | 0.1236 | 0.23804 | -0.23346 | -0.23804 | -0.26093 | -0.2655 | 0.022888 | -0.16479 | -0.013733 | 0.064087 | -0.18768 | -0.14649 | -0.21057 | -0.16937 | 0.21057 | 122.1634 | 0.041199 | 122.0306 | 121.8475 | 121.8796 | 121.875 | 121.9025 | -122.0398 | -122.0444 | 122.1909 | 122.0535 | 62.2742 | 62.3383
151.9531 | 122.3465 | -62.2833 | 59.7153 | 0.0016023 | 0.0022709 | 0.062453 | 0.059462 | -0.00063661 | -0.0042745 | 0.00022853 | 0.0009461 | 0.001303 | 0.072365 | 0.059714 | -0.0081689 | 0.016235 | -0.0003568 | -0.086975 | 59.5322 | -62.2513 | 59.9213 | -62.0087 | -62.4939 | -62.4619 | 0.050354 | 59.5322 | -62.3199 | 59.8389 | -62.1597 | -62.3657 | -62.3795 | 0.032043 | -0.18311 | 0.20599 | 0.27466 | -0.17853 | -0.21057 | -0.21057 | -0.24261 | -0.036621 | -0.18311 | 0.1236 | 0.1236 | -0.096131 | -0.082398 | -0.05951 | -0.045777 | 0.24262 | 122.1725 | 0.16022 | 122.1588 | 121.7834 | 121.8521 | 121.8155 | 121.8155 | -121.9666 | -122.0352 | 122.2046 | 122.1222 | 62.1963 | 62.3337
153.6875 | 122.3007 | -62.2833 | 59.761 | -0.0060272 | 0.0009891 | 0.063094 | 0.06053 | -0.002132 | -0.0059835 | -0.0019077 | -0.0021057 | -0.00019216 | 0.072578 | 0.060355 | -0.0071009 | 0.014954 | -0.0012112 | -0.10071 | 59.5505 | -62.2604 | 59.8846 | -62.0224 | -62.5031 | -62.4847 | 0.018311 | 59.5734 | -62.2971 | 59.8068 | -62.1918 | -62.384 | -62.4481 | 0.022888 | -0.21057 | 0.1236 | 0.26093 | -0.20142 | -0.21973 | -0.2243 | -0.24261 | -0.013733 | -0.18768 | 0.045777 | 0.091553 | -0.1648 | -0.10071 | -0.15106 | -0.086975 | 0.23804 | 122.1451 | 0.10529 | 122.1039 | 121.8109 | 121.8704 | 121.8338 | 121.8567 | -122.0215 | -122.0581 | 122.168 | 122.0901 | 62.1826 | 62.3016
155.375 | 122.2321 | -62.2742 | 59.8343 | -0.013657 | -0.0005063 | 0.060744 | 0.06053 | -0.00042301 | -0.0036337 | -0.0055393 | -0.0021057 | 0.001303 | 0.071297 | 0.068045 | -0.0081689 | 0.01474 | -0.004202 | -0.004578 | 59.6191 | -62.2787 | 59.8663 | -62.0911 | -62.5214 | -62.5259 | 0.027466 | 59.6283 | -62.2696 | 59.7885 | -62.2101 | -62.3886 | -62.4573 | -0.004578 | -0.21515 | 0.032043 | 0.18311 | -0.25177 | -0.24719 | -0.24719 | -0.24261 | 0.004578 | -0.20599 | -0.045777 | 0.064087 | -0.18311 | -0.11444 | -0.18768 | -0.11902 | 0.18768 | 122.1451 | 0.059509 | 122.0581 | 121.8979 | 121.8979 | 121.8933 | 121.9025 | -122.113 | -122.1039 | 122.1405 | 122.0627 | 62.2696 | 62.3016
157.125 | 122.3373 | -62.265 | 59.7382 | -0.0060272 | 0.0012027 | 0.060744 | 0.058394 | -0.0044818 | -0.0049155 | -0.00062587 | 0.0009461 | 0.001303 | 0.072151 | 0.064841 | -0.0094507 | 0.014954 | -0.0012112 | -0.045776 | 59.5276 | -62.2467 | 59.935 | -61.9766 | -62.4527 | -62.439 | 0.082397 | 59.5963 | -62.2925 | 59.8663 | -62.1323 | -62.3016 | -62.3749 | 0.018311 | -0.21057 | 0.19684 | 0.28839 | -0.17395 | -0.18768 | -0.19226 | -0.20599 | -0.027465 | -0.14191 | 0.12817 | 0.13275 | -0.10986 | -0.036621 | -0.082398 | -0.009156 | 0.27008 | 122.1817 | 0.16022 | 122.1588 | 121.7743 | 121.8887 | 121.7926 | 121.8613 | -121.9849 | -122.0306 | 122.2 | 122.1313 | 62.2192 | 62.3474
158.7969 | 122.2183 | -62.2833 | 59.8206 | 0.0016023 | 0.0003483 | 0.060957 | 0.062025 | -0.002132 | -0.0047019 | -0.0012669 | -0.0021057 | 0.0034392 | 0.074501 | 0.067191 | -0.0090235 | 0.015808 | 7.04e-05 | 0.054932 | 59.5734 | -62.2375 | 59.9304 | -62.0087 | -62.4619 | -62.4664 | 0.07782 | 59.6146 | -62.2696 | 59.7748 | -62.2147 | -62.3932 | -62.4756 | 0.045776 | -0.24719 | 0.10986 | 0.27466 | -0.18311 | -0.17853 | -0.22888 | -0.2243 | 0.013733 | -0.20599 | -0.045777 | 0.068664 | -0.19226 | -0.10986 | -0.20599 | -0.1236 | 0.22888 | 122.168 | 0.054931 | 122.0444 | 121.8109 | 121.8842 | 121.8567 | 121.8979 | -122.0581 | -122.0901 | 122.2137 | 122.0581 | 62.3383 | 62.3611
160.5469 | 122.2916 | -62.2833 | 59.7565 | -0.0060272 | -0.0002927 | 0.063094 | 0.057753 | 0.00021799 | -0.0032065 | -0.0038303 | -0.0021057 | 0.00044864 | 0.074074 | 0.063346 | -0.0071009 | 0.015595 | -0.0029202 | -0.10071 | 59.5367 | -62.2696 | 59.8801 | -62.059 | -62.5168 | -62.4939 | -0.013733 | 59.5505 | -62.2879 | 59.8022 | -62.1964 | -62.3795 | -62.4435 | 0.013733 | -0.21973 | 0.1236 | 0.2243 | -0.21057 | -0.23346 | -0.2243 | -0.24719 | -0.004578 | -0.20599 | 0.045776 | 0.086975 | -0.16022 | -0.096131 | -0.15564 | -0.091553 | 0.21057 | 122.1497 | 0.091553 | 122.0901 | 121.8063 | 121.8384 | 121.8201 | 121.8338 | -122.0261 | -122.0444 | 122.1634 | 122.0856 | 62.1826 | 62.2696
162.2969 | 122.2549 | -62.2467 | 59.8297 | -0.0060272 | -7.9104e-05 | 0.06053 | 0.059248 | -0.001491 | -0.0053427 | 0.00065573 | -0.0051575 | 0.0015166 | 0.07151 | 0.066336 | -0.0083825 | 0.016022 | -0.002493 | 0.041199 | 59.5276 | -62.2467 | 59.9533 | -61.9858 | -62.4435 | -62.4298 | 0.11444 | 59.5825 | -62.2604 | 59.816 | -62.1643 | -62.3566 | -62.4252 | 0 | -0.30212 | 0.1236 | 0.26093 | -0.18311 | -0.19684 | -0.18311 | -0.19684 | -0.013733 | -0.24719 | -0.013733 | 0.082397 | -0.17853 | -0.10986 | -0.16479 | -0.09613 | 0.26093 | 122.2 | 0.09613 | 122.0764 | 121.7743 | 121.843 | 121.7743 | 121.8292 | -122.0764 | -122.0901 | 122.2 | 122.0627 | 62.2879 | 62.3611
164.0312 | 122.2595 | -62.2879 | 59.8206 | -0.0060272 | 0.0020571 | 0.060957 | 0.063948 | -0.0034136 | -0.0040609 | -0.0019077 | 0.0009461 | 0.0023712 | 0.07151 | 0.065909 | -0.0077417 | 0.016449 | -0.0039884 | 0 | 59.5917 | -62.2604 | 59.903 | -62.0453 | -62.4985 | -62.5076 | 0.059509 | 59.6191 | -62.2925 | 59.8068 | -62.1826 | -62.3886 | -62.439 | 0.027466 | -0.22888 | 0.082397 | 0.24262 | -0.21973 | -0.21057 | -0.24719 | -0.23804 | -0.004577 | -0.20142 | -0.013733 | 0.10529 | -0.15106 | -0.10071 | -0.14649 | -0.096131 | 0.21515 | 122.1634 | 0.10986 | 122.0993 | 121.8521 | 121.9116 | 121.8796 | 121.907 | -122.081 | -122.113 | 122.1909 | 122.0947 | 62.2879 | 62.3474
165.7031 | 122.2961 | -62.3016 | 59.7565 | -0.0060272 | 0.0024845 | 0.061598 | 0.06053 | 0.0032086 | -0.0066245 | -0.0012669 | 0.0009461 | 0.0015166 | 0.07151 | 0.05886 | -0.0090235 | 0.014313 | -0.000784 | -0.091553 | 59.5093 | -62.2696 | 59.903 | -62.0087 | -62.5168 | -62.471 | 0.013733 | 59.5642 | -62.3016 | 59.8068 | -62.178 | -62.3703 | -62.4298 | 0.032044 | -0.24719 | 0.14648 | 0.29297 | -0.16937 | -0.21515 | -0.20142 | -0.24719 | 0 | -0.19226 | 0.050354 | 0.1236 | -0.12817 | -0.068664 | -0.12817 | -0.068664 | 0.26093 | 122.1725 | 0.1236 | 122.1085 | 121.7789 | 121.8658 | 121.8109 | 121.8658 | -122.0261 | -122.0581 | 122.2046 | 122.1085 | 62.2101 | 62.3154
167.4531 | 122.3145 | -62.2421 | 59.7931 | -0.0060272 | 0.0003483 | 0.060744 | 0.059462 | -0.0017048 | -0.0061971 | -0.0016941 | -0.0051575 | 0.00066224 | 0.069801 | 0.064414 | -0.0079553 | 0.01474 | -0.0033474 | 0.064087 | 59.5322 | -62.2284 | 59.9854 | -61.9537 | -62.4298 | -62.4161 | 0.13733 | 59.5779 | -62.2742 | 59.8526 | -62.1368 | -62.3199 | -62.3886 | 0.013732 | -0.26093 | 0.19226 | 0.28839 | -0.17395 | -0.18768 | -0.18768 | -0.20142 | -0.032044 | -0.21515 | 0.059509 | 0.10529 | -0.14648 | -0.07782 | -0.11444 | -0.045776 | 0.27466 | 122.2137 | 0.13733 | 122.1268 | 121.7606 | 121.8521 | 121.7743 | 121.8201 | -122.0215 | -122.0673 | 122.2275 | 122.0947 | 62.3062 | 62.3795
169.2031 | 122.2046 | -62.2696 | 59.8297 | 0.0016023 | 0.0009891 | 0.06053 | 0.060744 | -0.0040546 | -0.0051291 | 0.00086953 | -0.0082093 | 0.0027984 | 0.074074 | 0.065482 | -0.0094507 | 0.013031 | -0.0022794 | -0.009155 | 59.5917 | -62.2604 | 59.8572 | -62.0819 | -62.5259 | -62.5259 | 0.032043 | 59.6512 | -62.2833 | 59.7702 | -62.2284 | -62.4115 | -62.4847 | 0.009155 | -0.23804 | 0.027466 | 0.18768 | -0.25635 | -0.25635 | -0.2655 | -0.2655 | -0.013733 | -0.17853 | -0.059509 | 0.041198 | -0.21515 | -0.14191 | -0.20142 | -0.12817 | 0.17853 | 122.1176 | 0.054931 | 122.0535 | 121.8521 | 121.9345 | 121.8613 | 121.9208 | -122.0901 | -122.113 | 122.1268 | 122.0398 | 62.2604 | 62.3016
170.8906 | 122.3099 | -62.265 | 59.7931 | -0.0060272 | -0.0015743 | 0.063094 | 0.056898 | -0.0010638 | -0.0053427 | -0.00062587 | 0.0009461 | 0.0015166 | 0.07151 | 0.066123 | -0.0071009 | 0.01474 | -0.002493 | 0.064087 | 59.5276 | -62.2421 | 59.9716 | -61.9629 | -62.439 | -62.4252 | 0.13733 | 59.5779 | -62.2604 | 59.848 | -62.1368 | -62.3062 | -62.4023 | 0.022889 | -0.2655 | 0.17853 | 0.30212 | -0.16022 | -0.17395 | -0.18311 | -0.19684 | 0.004578 | -0.21515 | 0.054931 | 0.12817 | -0.13733 | -0.041198 | -0.14191 | -0.045776 | 0.27923 | 122.2137 | 0.1236 | 122.1085 | 121.7697 | 121.8384 | 121.7926 | 121.843 | -122.0352 | -122.0535 | 122.2366 | 122.113 | 62.3291 | 62.4023
172.6406 | 122.2824 | -62.2787 | 59.761 | -0.0060272 | 0.0044071 | 0.06288 | 0.060744 | 0.0014996 | -0.0053427 | -0.0031895 | -0.0051575 | 0.00087584 | 0.071938 | 0.072318 | -0.0077417 | 0.016876 | -0.0031338 | -0.073242 | 59.5322 | -62.2421 | 59.9167 | -61.9995 | -62.5076 | -62.4847 | 0.045776 | 59.5367 | -62.3108 | 59.8297 | -62.1735 | -62.3611 | -62.4298 | 0.036622 | -0.22888 | 0.15564 | 0.27924 | -0.20599 | -0.22888 | -0.24262 | -0.2655 | -0.032043 | -0.2243 | 0.068665 | 0.10529 | -0.15106 | -0.082397 | -0.11902 | -0.050354 | 0.24261 | 122.1588 | 0.13733 | 122.1405 | 121.7743 | 121.8475 | 121.8109 | 121.8155 | -122.0032 | -122.0718 | 122.1954 | 122.1085 | 62.2055 | 62.3245
174.375 | 122.3511 | -62.2513 | 59.7565 | -0.021286 | -0.0013607 | 0.059248 | 0.059035 | -0.0019184 | -0.0042745 | -0.0014805 | 0.0009461 | 0.0010894 | 0.071083 | 0.064841 | -0.0064599 | 0.016449 | -0.0016384 | 0.013733 | 59.5505 | -62.233 | 59.9579 | -61.9537 | -62.4207 | -62.4252 | 0.16022 | 59.5459 | -62.2787 | 59.8938 | -62.1094 | -62.2833 | -62.3749 | 0.018311 | -0.20599 | 0.20142 | 0.29755 | -0.17395 | -0.16937 | -0.19226 | -0.18768 | -0.027466 | -0.21057 | 0.13733 | 0.14191 | -0.1236 | -0.032043 | -0.09613 | -0.004577 | 0.27924 | 122.1909 | 0.16937 | 122.1725 | 121.7834 | 121.8246 | 121.8018 | 121.7972 | -121.9894 | -122.0352 | 122.2092 | 122.1451 | 62.265 | 62.4115
176.1094 | 122.3236 | -62.2421 | 59.7702 | -0.013657 | -0.0011471 | 0.059248 | 0.059462 | 0.0014996 | -0.0051291 | -0.0014805 | -0.0021057 | 0.0023712 | 0.070656 | 0.062918 | -0.0088097 | 0.014313 | -0.002493 | 0.054932 | 59.5505 | -62.2284 | 59.9899 | -61.9308 | -62.4207 | -62.4252 | 0.15564 | 59.5734 | -62.2925 | 59.8618 | -62.114 | -62.2925 | -62.3886 | 0.013732 | -0.21973 | 0.21973 | 0.31128 | -0.18311 | -0.17853 | -0.19684 | -0.19226 | -0.050354 | -0.19684 | 0.091552 | 0.12817 | -0.14648 | -0.050354 | -0.096131 | 0 | 0.29755 | 122.2183 | 0.17853 | 122.1542 | 121.7789 | 121.8658 | 121.7926 | 121.8155 | -121.9986 | -122.0627 | 122.2321 | 122.1039 | 62.2971 | 62.3978
177.8594 | 122.2092 | -62.3199 | 59.8022 | -0.021286 | 0.0031253 | 0.061812 | 0.063948 | -0.0017048 | -0.0044883 | -0.0025485 | 0.0009461 | 0.003653 | 0.072578 | 0.06655 | -0.0092371 | 0.017944 | -0.0012112 | -0.10986 | 59.5917 | -62.2742 | 59.8114 | -62.1689 | -62.6495 | -62.6175 | -0.091553 | 59.5871 | -62.3291 | 59.7382 | -62.3016 | -62.4985 | -62.5076 | 0.045776 | -0.21057 | 0.009155 | 0.15106 | -0.29755 | -0.32959 | -0.34332 | -0.37537 | -0.009156 | -0.21515 | -0.064087 | 0.01831 | -0.18768 | -0.17853 | -0.17853 | -0.16937 | 0.10529 | 122.0856 | 0.027466 | 122.0673 | 121.8658 | 121.9162 | 121.9116 | 121.907 | -122.0764 | -122.1313 | 122.1313 | 122.0581 | 62.2101 | 62.2284
179.5469 | 122.3007 | -62.2604 | 59.7748 | 0.0016023 | 0.0007755 | 0.061171 | 0.057967 | 0.001286 | -0.0044883 | -0.0012669 | -0.0021057 | 0.0027984 | 0.070015 | 0.065696 | -0.0068871 | 0.016449 | -0.0012112 | -0.068665 | 59.5367 | -62.2604 | 59.8846 | -62.0453 | -62.5076 | -62.4939 | 0.013733 | 59.5551 | -62.3108 | 59.8206 | -62.1552 | -62.3337 | -62.4069 | 0 | -0.23804 | 0.10986 | 0.21515 | -0.23346 | -0.24719 | -0.23346 | -0.24719 | -0.050354 | -0.21973 | 0.045777 | 0.10529 | -0.14648 | -0.073242 | -0.09613 | -0.022888 | 0.21515 | 122.1451 | 0.15564 | 122.1313 | 121.7972 | 121.8658 | 121.7972 | 121.8155 | -122.0352 | -122.0856 | 122.1451 | 122.081 | 62.1918 | 62.2742
181.2969 | 122.2961 | -62.2833 | 59.7153 | 0.0016023 | 0.0024845 | 0.064162 | 0.059676 | 0.0010724 | -0.0034201 | -0.0031895 | -0.0051575 | -0.00019216 | 0.07386 | 0.065909 | -0.0064599 | 0.014526 | -0.000784 | -0.064087 | 59.5276 | -62.2559 | 59.9258 | -61.9858 | -62.5076 | -62.4619 | 0.054932 | 59.523 | -62.3108 | 59.8251 | -62.178 | -62.3566 | -62.4207 | 0.027466 | -0.18768 | 0.21057 | 0.29755 | -0.17853 | -0.2243 | -0.20599 | -0.25177 | -0.027466 | -0.19226 | 0.10986 | 0.10528 | -0.13733 | -0.073242 | -0.10986 | -0.045776 | 0.27008 | 122.1817 | 0.13275 | 122.1359 | 121.7834 | 121.8338 | 121.8109 | 121.8063 | -121.9711 | -122.0261 | 122.2092 | 122.1085 | 62.2192 | 62.3383
183.0469 | 122.2916 | -62.2833 | 59.729 | 0.0016023 | 0.0020571 | 0.064162 | 0.058821 | -0.0012774 | -0.0047019 | -0.0023349 | 0.0039977 | 0.0027984 | 0.069588 | 0.062705 | -0.0071009 | 0.01709 | -0.0018522 | -0.07782 | 59.523 | -62.2559 | 59.9579 | -61.9858 | -62.4847 | -62.4664 | 0.054932 | 59.5276 | -62.3016 | 59.8297 | -62.1872 | -62.3611 | -62.4207 | 0.027466 | -0.20599 | 0.22888 | 0.29755 | -0.18311 | -0.20142 | -0.21057 | -0.22888 | -0.018311 | -0.20142 | 0.10071 | 0.09613 | -0.13733 | -0.07782 | -0.11902 | -0.059509 | 0.27008 | 122.2137 | 0.11444 | 122.1313 | 121.7789 | 121.8292 | 121.8063 | 121.8109 | -121.9849 | -122.0306 | 122.2412 | 122.113 | 62.2055 | 62.3383
184.7344 | 122.3373 | -62.2375 | 59.7885 | -0.0060272 | -0.0007199 | 0.061812 | 0.060103 | -0.00555 | -0.0064109 | 0.00022853 | -0.0051575 | 0.0015166 | 0.072151 | 0.067618 | -0.0094507 | 0.016022 | -0.0022794 | 0.050354 | 59.5505 | -62.2513 | 59.9854 | -61.9125 | -62.4115 | -62.4115 | 0.16022 | 59.5779 | -62.2787 | 59.8892 | -62.0911 | -62.2696 | -62.3749 | -0.013733 | -0.23804 | 0.19684 | 0.32501 | -0.17395 | -0.17395 | -0.16022 | -0.16022 | -0.041199 | -0.21057 | 0.10071 | 0.14648 | -0.13733 | -0.032043 | -0.09613 | 0.009156 | 0.33875 | 122.2366 | 0.18768 | 122.168 | 121.8018 | 121.8567 | 121.788 | 121.8155 | -122.0398 | -122.0673 | 122.2229 | 122.1268 | 62.2879 | 62.3978
186.4844 | 122.3648 | -62.2696 | 59.7427 | -0.0060272 | -0.0022153 | 0.060744 | 0.058821 | -0.0017048 | -0.0042745 | -0.0021213 | -0.0082093 | -0.00019216 | 0.073647 | 0.068259 | -0.0068871 | 0.014954 | -0.0012112 | -0.009155 | 59.5276 | -62.2467 | 59.9487 | -61.972 | -62.439 | -62.439 | 0.11902 | 59.5459 | -62.3108 | 59.8801 | -62.114 | -62.2879 | -62.3611 | 0.022888 | -0.21515 | 0.20599 | 0.29755 | -0.16937 | -0.16937 | -0.19226 | -0.19226 | -0.041199 | -0.19684 | 0.13733 | 0.15564 | -0.091553 | -0.018311 | -0.050354 | 0.022888 | 0.27466 | 122.1954 | 0.19684 | 122.1909 | 121.7743 | 121.8567 | 121.7972 | 121.8155 | -121.9894 | -122.0535 | 122.2183 | 122.1497 | 62.2604 | 62.3886
188.2344 | 122.3373 | -62.265 | 59.7702 | -0.021286 | -0.0002927 | 0.060957 | 0.058607 | 0.001286 | -0.0079061 | -0.0021213 | 0.0009461 | 0.0023712 | 0.071724 | 0.070823 | -0.0073145 | 0.015167 | -0.000784 | 0.032043 | 59.5322 | -62.2559 | 60.0082 | -61.9034 | -62.3978 | -62.3932 | 0.16479 | 59.5779 | -62.2696 | 59.8846 | -62.0819 | -62.2742 | -62.3611 | 0.009156 | -0.23804 | 0.23804 | 0.36163 | -0.12817 | -0.13275 | -0.13733 | -0.14191 | -0.004577 | -0.19226 | 0.11444 | 0.18311 | -0.09613 | -0.009155 | -0.091553 | -0.004578 | 0.35248 | 122.2641 | 0.18768 | 122.1542 | 121.788 | 121.8475 | 121.7972 | 121.843 | -122.0261 | -122.0398 | 122.2733 | 122.1497 | 62.2971 | 62.4298
189.9844 | 122.2183 | -62.265 | 59.7977 | -0.013657 | -0.0009335 | 0.058821 | 0.058607 | 0.0019268 | -0.0055563 | -0.00062587 | 0.0009461 | 0.0040802 | 0.072151 | 0.069968 | -0.0073145 | 0.015381 | -0.0039884 | 0.004578 | 59.5871 | -62.2559 | 59.8618 | -62.0773 | -62.5305 | -62.5214 | 0.009155 | 59.6466 | -62.2787 | 59.7748 | -62.2284 | -62.4161 | -62.4756 | 0.009156 | -0.21057 | 0.064087 | 0.18768 | -0.25635 | -0.2655 | -0.2655 | -0.27466 | -0.013733 | -0.15106 | -0.022888 | 0.036621 | -0.21057 | -0.15106 | -0.19684 | -0.13733 | 0.17853 | 122.1176 | 0.050354 | 122.0535 | 121.843 | 121.9254 | 121.8521 | 121.9116 | -122.0535 | -122.0764 | 122.1268 | 122.0398 | 62.2696 | 62.2742
191.6719 | 122.3602 | -62.2467 | 59.7473 | -0.0060272 | 0.0020571 | 0.060103 | 0.059035 | -0.0042682 | -0.0076925 | -0.0021213 | -0.0021057 | 0.00044864 | 0.071938 | 0.059714 | -0.0083825 | 0.015381 | -0.0065518 | 0.022888 | 59.5505 | -62.233 | 59.9762 | -61.9308 | -62.4207 | -62.4298 | 0.16022 | 59.5505 | -62.2925 | 59.903 | -62.0728 | -62.2559 | -62.352 | 0.013733 | -0.19684 | 0.22888 | 0.31586 | -0.18311 | -0.17395 | -0.19684 | -0.18768 | -0.045776 | -0.19684 | 0.15564 | 0.17395 | -0.10529 | -0.009155 | -0.05951 | 0.036621 | 0.30212 | 122.2092 | 0.21973 | 122.1954 | 121.7834 | 121.843 | 121.7972 | 121.7972 | -121.9803 | -122.0398 | 122.2229 | 122.1497 | 62.2696 | 62.4069
193.4062 | 122.2092 | -62.2787 | 59.8297 | -0.0060272 | 0.0031253 | 0.062025 | 0.062239 | -0.0019184 | -0.0027793 | -0.0029759 | -0.0051575 | 0.0040802 | 0.07386 | 0.064841 | -0.0075281 | 0.014313 | -0.0016384 | -0.004578 | 59.6191 | -62.2467 | 59.8709 | -62.0773 | -62.5259 | -62.5351 | 0.018311 | 59.642 | -62.3108 | 59.7748 | -62.2513 | -62.4252 | -62.4893 | 0.032044 | -0.21057 | 0.041199 | 0.20142 | -0.25635 | -0.24719 | -0.28839 | -0.27924 | -0.032043 | -0.18768 | -0.054932 | 0.027466 | -0.21057 | -0.14648 | -0.17853 | -0.11444 | 0.16937 | 122.1176 | 0.059509 | 122.0856 | 121.8658 | 121.9528 | 121.8979 | 121.9208 | -122.0764 | -122.1405 | 122.1497 | 122.0535 | 62.2742 | 62.2971
195.0781 | 122.2137 | -62.2879 | 59.7885 | 0.0016023 | 0.0026981 | 0.062239 | 0.062239 | 0.0051312 | -0.0053427 | -0.0010531 | -0.0021057 | 0.0066436 | 0.071083 | 0.063773 | -0.0075281 | 0.015595 | -0.0020658 | -0.036621 | 59.5917 | -62.2787 | 59.8663 | -62.0819 | -62.5717 | -62.5488 | -0.027466 | 59.6237 | -62.3245 | 59.7839 | -62.2604 | -62.4664 | -62.4847 | 0.009155 | -0.19684 | 0.07782 | 0.20599 | -0.26093 | -0.28381 | -0.27008 | -0.29297 | -0.036621 | -0.1648 | -0.004577 | 0.027466 | -0.19684 | -0.17853 | -0.16022 | -0.14191 | 0.19684 | 122.1451 | 0.064087 | 122.1085 | 121.8704 | 121.9482 | 121.8796 | 121.9116 | -122.0673 | -122.113 | 122.1542 | 122.0718 | 62.2513 | 62.2604
196.8125 | 122.2229 | -62.2742 | 59.7931 | -0.013657 | 0.0041935 | 0.063521 | 0.064803 | 0.00043159 | -0.0040609 | -0.0038303 | -0.0021057 | 0.0045074 | 0.073647 | 0.068259 | -0.0077417 | 0.017517 | -0.0046292 | -0.022888 | 59.5963 | -62.2513 | 59.8938 | -62.0453 | -62.5259 | -62.5076 | 0.018311 | 59.5917 | -62.3108 | 59.8068 | -62.2238 | -62.4344 | -62.471 | 0.022888 | -0.19684 | 0.10071 | 0.22888 | -0.23346 | -0.25177 | -0.25635 | -0.27466 | -0.036621 | -0.20142 | 0.013733 | 0.050354 | -0.19684 | -0.16022 | -0.16022 | -0.1236 | 0.20599 | 122.1451 | 0.086975 | 122.1176 | 121.8475 | 121.9025 | 121.8704 | 121.8658 | -122.0444 | -122.1039 | 122.168 | 122.081 | 62.2513 | 62.2925
198.5 | 122.2046 | -62.2787 | 59.8206 | 0.0016023 | -0.0007199 | 0.062239 | 0.059035 | -0.002132 | -0.0055563 | -0.0019077 | -0.0021057 | 0.001303 | 0.074074 | 0.063346 | -0.0064599 | 0.015808 | -0.000784 | 0.018311 | 59.5963 | -62.2604 | 59.8618 | -62.0636 | -62.5488 | -62.5214 | 0.018311 | 59.6329 | -62.2971 | 59.7748 | -62.2192 | -62.4069 | -62.4802 | 0.018311 | -0.22431 | 0.041198 | 0.21515 | -0.24261 | -0.27008 | -0.26093 | -0.28839 | -0.01831 | -0.18768 | -0.045777 | 0.05951 | -0.20142 | -0.12817 | -0.18311 | -0.10986 | 0.19684 | 122.1222 | 0.07782 | 122.0718 | 121.8567 | 121.9299 | 121.875 | 121.9116 | -122.081 | -122.1176 | 122.1405 | 122.0535 | 62.2971 | 62.2971
200.25 | 122.3282 | -62.2787 | 59.7244 | -0.0060272 | 0.0037661 | 0.063307 | 0.059462 | 0.001286 | -0.0066245 | -0.0012669 | -0.0021057 | 0.00087584 | 0.071297 | 0.059501 | -0.0075281 | 0.017303 | 0.0011386 | -0.07782 | 59.5276 | -62.2467 | 59.935 | -61.9766 | -62.4802 | -62.4619 | 0.064087 | 59.5276 | -62.3154 | 59.8572 | -62.1506 | -62.3428 | -62.4115 | 0.032044 | -0.19684 | 0.21057 | 0.30212 | -0.1831 | -0.20142 | -0.21515 | -0.23346 | -0.036621 | -0.19684 | 0.13275 | 0.12817 | -0.13275 | -0.064086 | -0.09613 | -0.027465 | 0.27008 | 122.1817 | 0.16479 | 122.1725 | 121.7743 | 121.843 | 121.8063 | 121.8063 | -121.9711 | -122.0398 | 122.2137 | 122.1359 | 62.2009 | 62.3428
202 | 122.3282 | -62.2742 | 59.7382 | -0.0060272 | 0.0033389 | 0.063734 | 0.059462 | 0.0032086 | -0.0040609 | -0.0031895 | -0.0021057 | 0.001944 | 0.07386 | 0.067405 | -0.0098779 | 0.017303 | 0.0002842 | -0.07782 | 59.5413 | -62.2467 | 59.9258 | -61.9995 | -62.4847 | -62.471 | 0.036621 | 59.5413 | -62.3062 | 59.8526 | -62.1552 | -62.3657 | -62.3795 | 0.027466 | -0.19684 | 0.18768 | 0.27466 | -0.19684 | -0.21057 | -0.2243 | -0.23804 | -0.032043 | -0.19684 | 0.11444 | 0.11902 | -0.10529 | -0.091553 | -0.073243 | -0.05951 | 0.24719 | 122.1725 | 0.15106 | 122.1588 | 121.788 | 121.8475 | 121.8155 | 121.8155 | -121.9849 | -122.0444 | 122.2 | 122.1268 | 62.1963 | 62.3108
203.6875 | 122.2595 | -62.265 | 59.8068 | -0.013657 | 0.0048343 | 0.060957 | 0.060957 | 0.001286 | -0.0068381 | -0.0023349 | -0.0051575 | 0.0034392 | 0.072151 | 0.064841 | -0.0066735 | 0.016449 | 0.0004978 | 0.013733 | 59.6054 | -62.2513 | 59.903 | -62.0361 | -62.5214 | -62.5122 | 0.041199 | 59.6329 | -62.2879 | 59.816 | -62.1689 | -62.3886 | -62.4344 | 0.013733 | -0.20142 | 0.09613 | 0.22888 | -0.24719 | -0.25635 | -0.26092 | -0.27008 | -0.022888 | -0.17395 | 0.009155 | 0.096131 | -0.16937 | -0.1236 | -0.14648 | -0.10071 | 0.21515 | 122.1542 | 0.11902 | 122.1039 | 121.8567 | 121.9208 | 121.8704 | 121.8979 | -122.0581 | -122.0947 | 122.168 | 122.081 | 62.2787 | 62.3062
205.4375 | 122.3373 | -62.2787 | 59.7244 | -0.0060272 | 0.0026981 | 0.062025 | 0.058607 | 0.00021799 | -0.0040609 | -0.0014805 | 0.0009461 | 0.0021576 | 0.070869 | 0.06655 | -0.0088097 | 0.016022 | -0.003561 | -0.082397 | 59.5322 | -62.2604 | 59.9396 | -61.9949 | -62.4985 | -62.4619 | 0.045776 | 59.5413 | -62.3062 | 59.8663 | -62.1414 | -62.3245 | -62.3886 | 0.018311 | -0.19226 | 0.21515 | 0.28381 | -0.1831 | -0.21973 | -0.20142 | -0.23804 | -0.027465 | -0.1831 | 0.14191 | 0.13733 | -0.10986 | -0.045776 | -0.082398 | -0.018311 | 0.2655 | 122.2 | 0.16479 | 122.1725 | 121.7926 | 121.8475 | 121.8109 | 121.8201 | -121.9849 | -122.0306 | 122.2183 | 122.1451 | 62.1964 | 62.3245
207.1094 | 122.3145 | -62.2559 | 59.7565 | 0.0016023 | 0.0016299 | 0.063521 | 0.061385 | -0.00063661 | -0.0044883 | -0.0036167 | 0.0009461 | 0.00066224 | 0.070229 | 0.062064 | -0.0071009 | 0.016449 | 0.0011386 | -0.13733 | 59.5551 | -62.2787 | 59.8801 | -62.0911 | -62.558 | -62.5397 | -0.018311 | 59.5459 | -62.3199 | 59.8251 | -62.1964 | -62.3703 | -62.4298 | -0.022889 | -0.20142 | 0.1236 | 0.16479 | -0.28381 | -0.30212 | -0.26093 | -0.27923 | -0.064087 | -0.21057 | 0.068664 | 0.059509 | -0.17395 | -0.11444 | -0.10986 | -0.050354 | 0.18768 | 122.1588 | 0.1236 | 122.1451 | 121.8338 | 121.8658 | 121.8109 | 121.8018 | -122.0352 | -122.0764 | 122.1359 | 122.081 | 62.1185 | 62.2375
208.8594 | 122.319 | -62.2787 | 59.7473 | -0.0060272 | -0.0005063 | 0.062453 | 0.059248 | -0.0010638 | -0.0055563 | -0.0023349 | -0.0051575 | 0.0015166 | 0.073006 | 0.061423 | -0.0077417 | 0.017303 | -0.0016384 | -0.09613 | 59.523 | -62.2696 | 59.8938 | -62.0087 | -62.5351 | -62.4893 | 0.018311 | 59.5642 | -62.3062 | 59.816 | -62.1918 | -62.3611 | -62.4252 | 0.009156 | -0.2243 | 0.14648 | 0.27008 | -0.21057 | -0.25635 | -0.21973 | -0.2655 | -0.027465 | -0.18311 | 0.068665 | 0.086976 | -0.14648 | -0.082397 | -0.11902 | -0.054932 | 0.26093 | 122.1634 | 0.11444 | 122.1222 | 121.7926 | 121.8704 | 121.8018 | 121.843 | -122.0169 | -122.0535 | 122.1725 | 122.0947 | 62.1826 | 62.2971
210.625 | 122.2275 | -62.3108 | 59.7931 | -0.021286 | 0.0022709 | 0.064162 | 0.059462 | 0.0034222 | -0.0034201 | -0.0021213 | -0.0021057 | 0.0040802 | 0.074074 | 0.066123 | -0.0088097 | 0.019012 | -0.0018522 | -0.14648 | 59.5871 | -62.2742 | 59.8206 | -62.1277 | -62.5946 | -62.5809 | -0.082397 | 59.5917 | -62.3108 | 59.7519 | -62.2787 | -62.4756 | -62.4939 | 0.036621 | -0.20599 | 0.027466 | 0.18311 | -0.27008 | -0.28381 | -0.3067 | -0.32043 | 0 | -0.20142 | -0.041199 | 0.032043 | -0.1831 | -0.16479 | -0.1831 | -0.16479 | 0.14648 | 122.0947 | 0.032043 | 122.0627 | 121.8613 | 121.9025 | 121.8979 | 121.9025 | -122.0673 | -122.1039 | 122.1313 | 122.0627 | 62.1643 | 62.2284
212.3125 | 122.2092 | -62.2742 | 59.8389 | -0.013657 | -0.0017881 | 0.06053 | 0.059462 | -0.00042301 | -0.0061971 | -0.0012669 | -0.0051575 | 0.00066224 | 0.07386 | 0.064627 | -0.0085961 | 0.015381 | -0.000784 | 0.009155 | 59.5963 | -62.2513 | 59.8618 | -62.059 | -62.5259 | -62.5214 | 0.032043 | 59.6191 | -62.2833 | 59.7702 | -62.2192 | -62.4069 | -62.4664 | 0.022888 | -0.24262 | 0.022888 | 0.21515 | -0.24719 | -0.25177 | -0.27008 | -0.27466 | -0.009155 | -0.21973 | -0.068664 | 0.054932 | -0.19226 | -0.13275 | -0.18311 | -0.1236 | 0.19226 | 122.113 | 0.064087 | 122.0535 | 121.8475 | 121.9025 | 121.8704 | 121.8933 | -122.0901 | -122.1222 | 122.1359 | 122.0444 | 62.2833 | 62.3062
214.0469 | 122.2412 | -62.2604 | 59.8389 | 0.0016023 | 0.0005619 | 0.06053 | 0.059676 | -0.0012774 | -0.0055563 | -0.0025485 | 0.0039977 | 0.0027984 | 0.073006 | 0.063773 | -0.0081689 | 0.016663 | -0.0027066 | -0.004578 | 59.61 | -62.2787 | 59.848 | -62.0773 | -62.5397 | -62.5214 | 0.009155 | 59.6237 | -62.2971 | 59.7839 | -62.2055 | -62.3886 | -62.439 | -0.018311 | -0.22888 | 0.009155 | 0.18311 | -0.26093 | -0.27924 | -0.24261 | -0.26093 | -0.036621 | -0.21515 | -0.054931 | 0.054932 | -0.17853 | -0.12817 | -0.14191 | -0.091553 | 0.20142 | 122.1268 | 0.091553 | 122.081 | 121.8887 | 121.9208 | 121.8704 | 121.8842 | -122.1176 | -122.1359 | 122.1085 | 122.0444 | 62.2559 | 62.2696
215.7812 | 122.3419 | -62.265 | 59.7748 | -0.013657 | 0.0003483 | 0.062666 | 0.058394 | -0.002132 | -0.0029929 | 0.0010831 | -0.0021057 | 0.00023504 | 0.070442 | 0.07659 | -0.0090235 | 0.01474 | -0.0029202 | -0.064087 | 59.5367 | -62.2696 | 59.9167 | -62.0087 | -62.4527 | -62.4619 | 0.064087 | 59.5505 | -62.2971 | 59.8526 | -62.1368 | -62.3108 | -62.3703 | -0.004577 | -0.23804 | 0.14191 | 0.25635 | -0.19684 | -0.18768 | -0.19226 | -0.18311 | -0.032043 | -0.2243 | 0.07782 | 0.12817 | -0.10529 | -0.045776 | -0.073242 | -0.013733 | 0.26093 | 122.1863 | 0.16022 | 122.1497 | 121.8063 | 121.8475 | 121.8018 | 121.8155 | -122.0444 | -122.0718 | 122.1817 | 122.1176 | 62.2009 | 62.3291
217.5469 | 122.3328 | -62.2971 | 59.7382 | -0.013657 | 0.0018435 | 0.062666 | 0.060103 | -0.00085021 | -0.0029929 | -0.0019077 | -0.0051575 | 0.0032256 | 0.07151 | 0.060569 | -0.010305 | 0.016022 | -0.0027066 | -0.14191 | 59.5688 | -62.2559 | 59.8846 | -62.0728 | -62.5442 | -62.5305 | 0 | 59.5596 | -62.3062 | 59.8389 | -62.1872 | -62.3657 | -62.3978 | 0.041199 | -0.16937 | 0.14648 | 0.2243 | -0.23346 | -0.24719 | -0.27466 | -0.28839 | -0.009155 | -0.17853 | 0.10071 | 0.10986 | -0.10071 | -0.068665 | -0.091553 | -0.05951 | 0.1831 | 122.1405 | 0.11902 | 122.1451 | 121.8246 | 121.8658 | 121.8658 | 121.8567 | -121.994 | -122.0444 | 122.1817 | 122.1359 | 62.1552 | 62.2971
219.2344 | 122.2321 | -62.2879 | 59.8022 | 0.0016023 | 0.0014163 | 0.061385 | 0.061385 | -0.001491 | -0.0055563 | -0.0025485 | -0.0021057 | 0.003012 | 0.072792 | 0.064841 | -0.0092371 | 0.018158 | 0.0019932 | 0 | 59.6146 | -62.2787 | 59.8618 | -62.0956 | -62.5305 | -62.5214 | 0.013733 | 59.6146 | -62.3108 | 59.7839 | -62.2238 | -62.4069 | -62.4298 | 0.009155 | -0.18768 | 0.059509 | 0.19226 | -0.23346 | -0.24262 | -0.24261 | -0.25177 | -0.022888 | -0.18768 | -0.01831 | 0.064087 | -0.14191 | -0.11902 | -0.11902 | -0.09613 | 0.18311 | 122.1405 | 0.086975 | 122.0947 | 121.8933 | 121.9254 | 121.9025 | 121.9025 | -122.081 | -122.113 | 122.1497 | 122.0718 | 62.2879 | 62.3016
220.9844 | 122.3419 | -62.2559 | 59.761 | -0.0060272 | -0.0005063 | 0.061171 | 0.058821 | -0.0034136 | -0.0051291 | -0.00083947 | 0.0009461 | 0.00023504 | 0.071938 | 0.055228 | -0.0058191 | 0.014954 | 0.0002842 | -0.036621 | 59.5413 | -62.2604 | 59.9121 | -62.0041 | -62.471 | -62.4573 | 0.068665 | 59.5596 | -62.3199 | 59.8618 | -62.1323 | -62.3016 | -62.3657 | -0.004578 | -0.21973 | 0.15106 | 0.25177 | -0.20142 | -0.21515 | -0.19684 | -0.21057 | -0.064087 | -0.20142 | 0.10071 | 0.1236 | -0.10986 | -0.045777 | -0.045777 | 0.01831 | 0.25635 | 122.1725 | 0.18768 | 122.1817 | 121.8018 | 121.8796 | 121.7972 | 121.8155 | -122.0215 | -122.081 | 122.168 | 122.1176 | 62.2192 | 62.3245
222.75 | 122.3053 | -62.2833 | 59.7565 | 0.0016023 | -0.0013607 | 0.06053 | 0.057539 | -0.003841 | -0.0044883 | -0.00062587 | -0.0051575 | 0.001303 | 0.072365 | 0.059073 | -0.0075281 | 0.015808 | 0.000925 | -0.064087 | 59.5184 | -62.2787 | 59.8709 | -62.0499 | -62.5214 | -62.4847 | 0.013733 | 59.5459 | -62.3016 | 59.8068 | -62.1918 | -62.3474 | -62.4069 | 0.004577 | -0.23804 | 0.11444 | 0.23346 | -0.20142 | -0.23804 | -0.20599 | -0.24261 | -0.018311 | -0.21057 | 0.050354 | 0.091553 | -0.1236 | -0.064087 | -0.10528 | -0.045776 | 0.22888 | 122.1497 | 0.10986 | 122.1085 | 121.7972 | 121.8475 | 121.8018 | 121.8292 | -122.0352 | -122.0581 | 122.1542 | 122.0901 | 62.2192 | 62.2971
224.4375 | 122.2458 | -62.2604 | 59.8022 | -0.0060272 | 0.0016299 | 0.059462 | 0.059462 | -0.0019184 | -0.0034201 | -0.00083947 | -0.0051575 | 0.0025848 | 0.071297 | 0.067832 | -0.010305 | 0.015595 | -0.0022794 | 0.004578 | 59.6146 | -62.2604 | 59.8846 | -62.059 | -62.4985 | -62.5076 | 0.027466 | 59.6375 | -62.2879 | 59.8114 | -62.1826 | -62.3932 | -62.4435 | 0 | -0.18768 | 0.082398 | 0.20142 | -0.24719 | -0.23804 | -0.24719 | -0.23804 | -0.027466 | -0.16479 | 0.009155 | 0.07782 | -0.1831 | -0.13275 | -0.15564 | -0.10529 | 0.20142 | 122.1451 | 0.10529 | 122.0993 | 121.875 | 121.9254 | 121.875 | 121.8979 | -122.0627 | -122.0901 | 122.1451 | 122.0718 | 62.265 | 62.2879
226.1875 | 122.319 | -62.2833 | 59.7519 | -0.0060272 | 0.0048343 | 0.061812 | 0.062239 | -0.0032 | -0.0040609 | -0.00083947 | -0.0051575 | 0.0034392 | 0.070869 | 0.066336 | -0.0064599 | 0.016449 | -0.0050564 | -0.13275 | 59.5734 | -62.3016 | 59.8343 | -62.0956 | -62.5717 | -62.558 | -0.054932 | 59.5459 | -62.3383 | 59.816 | -62.2147 | -62.3932 | -62.4161 | -0.018311 | -0.17853 | 0.082398 | 0.18768 | -0.27466 | -0.28839 | -0.25635 | -0.27008 | -0.054932 | -0.20599 | 0.064087 | 0.068664 | -0.13275 | -0.10986 | -0.07782 | -0.054931 | 0.20599 | 122.1359 | 0.1236 | 122.1542 | 121.875 | 121.8842 | 121.8567 | 121.8292 | -122.0535 | -122.0901 | 122.1176 | 122.0993 | 62.1506 | 62.2284
227.8594 | 122.2183 | -62.2833 | 59.8343 | -0.013657 | -0.0002927 | 0.058821 | 0.057967 | -0.0019184 | -0.0040609 | -0.0012669 | -0.0082093 | 0.0025848 | 0.07386 | 0.069541 | -0.0081689 | 0.016876 | -0.002493 | 0 | 59.6329 | -62.2559 | 59.848 | -62.1002 | -62.5442 | -62.5305 | 0.004578 | 59.6329 | -62.2971 | 59.7656 | -62.2147 | -62.4115 | -62.4756 | 0.027466 | -0.20142 | 0.013732 | 0.1831 | -0.24719 | -0.26093 | -0.27466 | -0.28839 | -0.013733 | -0.20142 | -0.068665 | 0.068664 | -0.19226 | -0.12817 | -0.17853 | -0.11444 | 0.15564 | 122.1039 | 0.082397 | 122.0627 | 121.8887 | 121.9299 | 121.9162 | 121.9162 | -122.0901 | -122.1313 | 122.1313 | 122.0489 | 62.2833 | 62.2879
229.5938 | 122.2458 | -62.2787 | 59.8206 | -0.0060272 | 0.0001345 | 0.061171 | 0.060316 | -0.001491 | -0.0064109 | -0.0019077 | 0.0009461 | 0.0025848 | 0.072151 | 0.068045 | -0.0058191 | 0.016235 | -0.0016384 | 0 | 59.6283 | -62.2559 | 59.8709 | -62.0773 | -62.5305 | -62.5442 | 0.027466 | 59.6146 | -62.3016 | 59.8022 | -62.1872 | -62.4023 | -62.4344 | 0.022889 | -0.19226 | 0.050354 | 0.20142 | -0.2655 | -0.25177 | -0.28839 | -0.27466 | -0.022888 | -0.20599 | -0.018311 | 0.091553 | -0.15564 | -0.1236 | -0.13275 | -0.10071 | 0.17853 | 122.1268 | 0.11444 | 122.1039 | 121.8842 | 121.9162 | 121.907 | 121.8933 | -122.0764 | -122.1222 | 122.1497 | 122.081 | 62.2787 | 62.3062
231.3281 | 122.2092 | -62.2925 | 59.8389 | -0.013657 | 0.0029117 | 0.059676 | 0.060957 | -0.00085021 | -0.0053427 | -0.0019077 | -0.0051575 | 0.0027984 | 0.073647 | 0.064414 | -0.0060327 | 0.017944 | 0.0041294 | 0.004578 | 59.6191 | -62.2513 | 59.8434 | -62.1048 | -62.5259 | -62.5397 | 0.022888 | 59.6375 | -62.3016 | 59.7748 | -62.2238 | -62.3978 | -62.4527 | 0.041198 | -0.21973 | 0.004578 | 0.18768 | -0.24719 | -0.23346 | -0.28839 | -0.27466 | -0.009156 | -0.20142 | -0.064087 | 0.068664 | -0.16022 | -0.10529 | -0.15106 | -0.09613 | 0.14649 | 122.0947 | 0.07782 | 122.0764 | 121.8704 | 121.9391 | 121.9116 | 121.9299 | -122.0901 | -122.1405 | 122.1359 | 122.0673 | 62.2971 | 62.3154
233.0625 | 122.2687 | -62.2742 | 59.7839 | -0.0060272 | 0.0001345 | 0.061812 | 0.059248 | -0.0017048 | -0.0038473 | -0.00019867 | -0.0021057 | 0.0017304 | 0.071724 | 0.06655 | -0.0060327 | 0.018372 | -0.000784 | 0.004578 | 59.5917 | -62.2421 | 59.903 | -62.0361 | -62.4985 | -62.5076 | 0.086975 | 59.6054 | -62.2925 | 59.8068 | -62.178 | -62.4023 | -62.4344 | 0.032044 | -0.19226 | 0.11902 | 0.23804 | -0.23346 | -0.2243 | -0.2655 | -0.25635 | -0.01831 | -0.17853 | 0.022888 | 0.09613 | -0.16022 | -0.12817 | -0.14191 | -0.10986 | 0.20599 | 122.1451 | 0.11444 | 122.0993 | 121.8338 | 121.8979 | 121.8658 | 121.8796 | -122.0261 | -122.0764 | 122.1771 | 122.081 | 62.2787 | 62.3611
234.7969 | 122.2733 | -62.2696 | 59.8206 | -0.0060272 | 0.0016299 | 0.060957 | 0.059889 | 0.00021799 | -0.0032065 | -0.0014805 | -0.0051575 | 0.004721 | 0.072365 | 0.070823 | -0.0079553 | 0.016235 | -0.0016384 | 0.022888 | 59.6191 | -62.2604 | 59.8846 | -62.059 | -62.5214 | -62.5122 | 0.050354 | 59.6008 | -62.3154 | 59.8068 | -62.2055 | -62.3932 | -62.4298 | 0.009155 | -0.20142 | 0.064087 | 0.21057 | -0.24261 | -0.25177 | -0.25177 | -0.26093 | -0.045777 | -0.21973 | -0.013733 | 0.064087 | -0.16022 | -0.1236 | -0.11444 | -0.077819 | 0.20142 | 122.1451 | 0.10986 | 122.1222 | 121.8796 | 121.9162 | 121.8887 | 121.8704 | -122.081 | -122.1359 | 122.1542 | 122.0764 | 62.2925 | 62.3199
236.5312 | 122.3282 | -62.2971 | 59.7382 | -0.013657 | 0.0035525 | 0.063734 | 0.060103 | 0.0034222 | -0.0055563 | -0.0046847 | -0.0021057 | 0.0010894 | 0.074074 | 0.060569 | -0.0068871 | 0.016235 | -0.0022794 | -0.13733 | 59.5779 | -62.2696 | 59.8709 | -62.059 | -62.5488 | -62.5122 | 0.013733 | 59.5459 | -62.3154 | 59.8206 | -62.1826 | -62.3886 | -62.384 | 0.027466 | -0.16022 | 0.13275 | 0.23804 | -0.21515 | -0.25177 | -0.24261 | -0.27924 | -0.018311 | -0.19226 | 0.082398 | 0.11444 | -0.086975 | -0.091553 | -0.068664 | -0.073242 | 0.21057 | 122.1405 | 0.13275 | 122.1359 | 121.8475 | 121.8613 | 121.875 | 121.843 | -122.0078 | -122.0535 | 122.168 | 122.1176 | 62.1597 | 62.3108
238.2188 | 122.2046 | -62.2925 | 59.7885 | -0.013657 | 0.0035525 | 0.064802 | 0.059889 | 0.0010724 | -0.0032065 | -0.0023349 | -0.0021057 | 0.0049346 | 0.072792 | 0.075095 | -0.0085961 | 0.017517 | -0.0044156 | -0.1236 | 59.6191 | -62.2742 | 59.8114 | -62.1506 | -62.6038 | -62.5992 | -0.082397 | 59.5871 | -62.3337 | 59.7519 | -62.2879 | -62.4664 | -62.5031 | 0.01831 | -0.16937 | 0.022888 | 0.14191 | -0.3067 | -0.31128 | -0.32501 | -0.32959 | -0.041199 | -0.20142 | -0.036621 | 0.004577 | -0.21057 | -0.17395 | -0.16937 | -0.13275 | 0.1236 | 122.0856 | 0.045776 | 122.0856 | 121.8933 | 121.9208 | 121.9116 | 121.8796 | -122.0627 | -122.1222 | 122.1039 | 122.0444 | 62.1689 | 62.2101
239.9531 | 122.2366 | -62.2742 | 59.8206 | -0.0060272 | 0.0018435 | 0.062666 | 0.060744 | 0.0017132 | -0.0040609 | 0.00065573 | -0.0021057 | 0.003012 | 0.072365 | 0.068473 | -0.010732 | 0.017731 | -0.00527 | -0.032043 | 59.5917 | -62.265 | 59.8801 | -62.0407 | -62.5351 | -62.5214 | 0.041199 | 59.5871 | -62.3337 | 59.7839 | -62.2375 | -62.4252 | -62.471 | 0.009155 | -0.22888 | 0.059509 | 0.23346 | -0.24719 | -0.26093 | -0.25635 | -0.27008 | -0.059509 | -0.23346 | -0.036621 | 0.036621 | -0.19684 | -0.15106 | -0.13733 | -0.091553 | 0.22431 | 122.1451 | 0.09613 | 122.1176 | 121.8567 | 121.9208 | 121.8658 | 121.8613 | -122.0856 | -122.1542 | 122.1542 | 122.0581 | 62.2421 | 62.3154
241.7031 | 122.3419 | -62.265 | 59.7382 | -0.013657 | 0.0035525 | 0.064375 | 0.059889 | 0.0014996 | -0.0042745 | -0.0040439 | 0.0009461 | 0.0021576 | 0.074928 | 0.05886 | -0.0081689 | 0.016876 | -0.002493 | -0.068665 | 59.5413 | -62.2559 | 59.9167 | -62.0132 | -62.4939 | -62.4802 | 0.059509 | 59.5276 | -62.3154 | 59.8526 | -62.1506 | -62.3474 | -62.3749 | 0.009156 | -0.19684 | 0.17853 | 0.25177 | -0.21515 | -0.22888 | -0.22431 | -0.23804 | -0.050354 | -0.21057 | 0.11444 | 0.11444 | -0.10986 | -0.082397 | -0.059509 | -0.032043 | 0.24261 | 122.1725 | 0.16479 | 122.168 | 121.7972 | 121.843 | 121.8063 | 121.7926 | -121.994 | -122.0535 | 122.1817 | 122.1176 | 62.1963 | 62.3245
243.3906 | 122.2046 | -62.3245 | 59.8022 | -0.0060272 | 0.0046207 | 0.062025 | 0.061171 | 0.0010724 | -0.0053427 | -0.0016941 | -0.0051575 | 0.0023712 | 0.073647 | 0.067832 | -0.0075281 | 0.016235 | -0.0003568 | -0.10986 | 59.6191 | -62.2787 | 59.816 | -62.1368 | -62.6175 | -62.6038 | -0.10986 | 59.5779 | -62.3428 | 59.7244 | -62.3016 | -62.4985 | -62.4985 | 0.045776 | -0.1831 | 0.013733 | 0.18768 | -0.27924 | -0.29297 | -0.32501 | -0.33875 | -0.01831 | -0.2243 | -0.07782 | 0.022888 | -0.17395 | -0.17395 | -0.15564 | -0.15564 | 0.14191 | 122.0947 | 0.041198 | 122.0673 | 121.8979 | 121.9208 | 121.9437 | 121.9025 | -122.081 | -122.1451 | 122.1405 | 122.0489 | 62.2147 | 62.2147
245.1406 | 122.2366 | -62.2833 | 59.816 | 0.0016023 | 0.0039799 | 0.06523 | 0.060103 | 0.0010724 | -0.0053427 | -0.0042575 | -0.0051575 | 0.003012 | 0.071724 | 0.070182 | -0.0073145 | 0.014099 | 7.04e-05 | -0.004578 | 59.6283 | -62.2559 | 59.9121 | -62.0361 | -62.5031 | -62.4893 | 0.091553 | 59.6054 | -62.2971 | 59.8206 | -62.1872 | -62.3978 | -62.4207 | 0.027466 | -0.18768 | 0.09613 | 0.24719 | -0.20599 | -0.21973 | -0.23346 | -0.24719 | -0.013733 | -0.21057 | 0.004578 | 0.09613 | -0.13733 | -0.11444 | -0.1236 | -0.10071 | 0.21973 | 122.168 | 0.10986 | 122.1176 | 121.8842 | 121.9025 | 121.9116 | 121.8887 | -122.0718 | -122.113 | 122.1954 | 122.1039 | 62.2787 | 62.3749
246.8906 | 122.2504 | -62.2787 | 59.7839 | -0.0060272 | 0.0037661 | 0.063521 | 0.06053 | 0.0023542 | -0.0059835 | 0.00086953 | -0.0021057 | 0.00066224 | 0.072792 | 0.067832 | -0.0073145 | 0.015808 | 7.04e-05 | 0.004578 | 59.61 | -62.2513 | 59.9121 | -62.0132 | -62.5076 | -62.5076 | 0.059509 | 59.6008 | -62.3062 | 59.8297 | -62.2055 | -62.3932 | -62.4298 | 0.027466 | -0.17395 | 0.12817 | 0.2655 | -0.22888 | -0.22888 | -0.25635 | -0.25635 | -0.027465 | -0.18311 | 0.045776 | 0.073243 | -0.15106 | -0.11444 | -0.1236 | -0.086975 | 0.23804 | 122.1634 | 0.10071 | 122.1359 | 121.8613 | 121.907 | 121.8887 | 121.8796 | -122.0352 | -122.0901 | 122.1909 | 122.1085 | 62.2833 | 62.3383
248.6406 | 122.319 | -62.2742 | 59.7931 | -0.0060272 | 0.0001345 | 0.059676 | 0.05583 | -0.0012774 | -0.0038473 | 0.00086953 | -0.0021057 | -0.00040596 | 0.072151 | 0.067618 | -0.0075281 | 0.015595 | -0.0014248 | 0.054932 | 59.5459 | -62.2284 | 59.967 | -61.9446 | -62.4207 | -62.4115 | 0.14648 | 59.5551 | -62.2833 | 59.8618 | -62.114 | -62.2971 | -62.3795 | 0.045776 | -0.24719 | 0.17395 | 0.32959 | -0.13733 | -0.14648 | -0.1831 | -0.19226 | -0.009155 | -0.23804 | 0.068664 | 0.16022 | -0.10529 | -0.022888 | -0.096131 | -0.013733 | 0.28381 | 122.1954 | 0.16937 | 122.1451 | 121.7743 | 121.8384 | 121.8201 | 121.8292 | -122.0215 | -122.0764 | 122.2412 | 122.1359 | 62.3291 | 62.4207
250.3281 | 122.3373 | -62.265 | 59.7427 | -0.013657 | 0.0029117 | 0.062453 | 0.058394 | -0.0023456 | -0.0061971 | -0.0034031 | -0.0021057 | 0.00087584 | 0.070442 | 0.063773 | -0.0085961 | 0.015595 | 0.0007114 | -0.073242 | 59.5551 | -62.2696 | 59.935 | -61.9995 | -62.5031 | -62.4664 | 0.059509 | 59.5322 | -62.3199 | 59.8572 | -62.1506 | -62.3337 | -62.3749 | -0.004577 | -0.18768 | 0.19226 | 0.2655 | -0.20142 | -0.23804 | -0.19684 | -0.23346 | -0.054931 | -0.21057 | 0.11444 | 0.11444 | -0.10986 | -0.068664 | -0.054932 | -0.013733 | 0.27008 | 122.2046 | 0.16937 | 122.1771 | 121.8246 | 121.8521 | 121.8201 | 121.7972 | -122.0123 | -122.0627 | 122.2 | 122.1222 | 62.1918 | 62.3245
252.0781 | 122.3648 | -62.2604 | 59.7656 | -0.0060272 | -0.0015743 | 0.061812 | 0.057753 | -0.00085021 | -0.0055563 | -0.00041227 | -0.0021057 | -0.00019216 | 0.072365 | 0.06185 | -0.0075281 | 0.014526 | -0.0018522 | -0.013733 | 59.5642 | -62.2696 | 59.9304 | -61.972 | -62.4481 | -62.4298 | 0.11902 | 59.5551 | -62.3016 | 59.8572 | -62.1185 | -62.2833 | -62.3749 | -0.009155 | -0.20142 | 0.16479 | 0.28839 | -0.16937 | -0.18768 | -0.16022 | -0.17853 | -0.041199 | -0.21057 | 0.091553 | 0.14191 | -0.11444 | -0.022888 | -0.073242 | 0.018311 | 0.29755 | 122.2 | 0.18311 | 122.1588 | 121.8338 | 121.8567 | 121.8246 | 121.8155 | -122.0352 | -122.0673 | 122.1909 | 122.1176 | 62.2467 | 62.3795
253.7656 | 122.2229 | -62.3154 | 59.7839 | -0.013657 | 0.0050479 | 0.063307 | 0.063094 | -0.00063661 | -0.0047019 | -0.0040439 | -0.0051575 | 0.0051482 | 0.072365 | 0.065909 | -0.0088097 | 0.018799 | 0.0015658 | -0.10986 | 59.61 | -62.2925 | 59.8022 | -62.1643 | -62.6312 | -62.6129 | -0.091553 | 59.61 | -62.3291 | 59.7519 | -62.2971 | -62.4893 | -62.5122 | 0.022889 | -0.17395 | 0.01831 | 0.15106 | -0.29755 | -0.31586 | -0.32044 | -0.33875 | -0.013733 | -0.17395 | -0.032044 | 0.018311 | -0.19684 | -0.17395 | -0.1831 | -0.16022 | 0.12817 | 122.0947 | 0.032044 | 122.081 | 121.9025 | 121.9391 | 121.9254 | 121.9254 | -122.0764 | -122.113 | 122.1176 | 122.0673 | 62.2055 | 62.2238
255.5 | 122.3145 | -62.2971 | 59.7473 | -0.0060272 | 0.0024845 | 0.063307 | 0.061598 | -0.002132 | -0.0049155 | -0.0031895 | -0.0051575 | 0.00044864 | 0.072151 | 0.066336 | -0.0079553 | 0.017517 | -0.0039884 | -0.14191 | 59.5917 | -62.2833 | 59.848 | -62.0865 | -62.5946 | -62.558 | -0.032043 | 59.5734 | -62.3474 | 59.8206 | -62.2147 | -62.3932 | -62.4344 | 0.013733 | -0.15564 | 0.10071 | 0.21057 | -0.26093 | -0.29755 | -0.27466 | -0.31128 | -0.050354 | -0.17395 | 0.073243 | 0.082397 | -0.13733 | -0.09613 | -0.086975 | -0.045776 | 0.19684 | 122.1313 | 0.13275 | 122.168 | 121.875 | 121.9208 | 121.8887 | 121.8704 | -122.0306 | -122.0947 | 122.1451 | 122.1176 | 62.1552 | 62.265
257.1719 | 122.3419 | -62.2559 | 59.7656 | 0.0016023 | 0.0005619 | 0.060744 | 0.057753 | -0.0027728 | -0.0059835 | -0.0025485 | -0.0021057 | 0.0021576 | 0.070869 | 0.066336 | -0.0083825 | 0.013886 | -0.0048428 | -0.045776 | 59.5596 | -62.2467 | 59.9121 | -62.0087 | -62.4802 | -62.4619 | 0.059509 | 59.5642 | -62.2879 | 59.848 | -62.1414 | -62.3108 | -62.3795 | 0.009155 | -0.20599 | 0.14648 | 0.24719 | -0.20599 | -0.22431 | -0.21515 | -0.23346 | -0.032044 | -0.20142 | 0.082397 | 0.11444 | -0.1236 | -0.054932 | -0.091553 | -0.022888 | 0.23804 | 122.1588 | 0.14648 | 122.1359 | 121.8063 | 121.8521 | 121.8155 | 121.8201 | -122.0123 | -122.0535 | 122.168 | 122.1039 | 62.2101 | 62.3154
258.9062 | 122.2366 | -62.2879 | 59.8206 | -0.013657 | 0.0005619 | 0.06053 | 0.059248 | -0.0025592 | -0.0059835 | -0.0029759 | -0.0021057 | 0.0015166 | 0.072792 | 0.067405 | -0.0081689 | 0.015808 | -0.0022794 | 0.054932 | 59.5642 | -62.233 | 59.9075 | -62.0224 | -62.4939 | -62.4802 | 0.073242 | 59.6375 | -62.3016 | 59.7656 | -62.2238 | -62.3932 | -62.4664 | 0.054932 | -0.25635 | 0.086975 | 0.2655 | -0.19226 | -0.20599 | -0.24719 | -0.26093 | -0.013733 | -0.18311 | -0.054932 | 0.064087 | -0.17853 | -0.10529 | -0.16479 | -0.091552 | 0.21057 | 122.1405 | 0.07782 | 122.0673 | 121.7972 | 121.9391 | 121.8521 | 121.9254 | -122.0535 | -122.1222 | 122.1954 | 122.0535 | 62.3428 | 62.3611
260.6562 | 122.3145 | -62.2787 | 59.7198 | -0.0060272 | 0.0016299 | 0.063734 | 0.058394 | -0.0019184 | -0.0047019 | -0.0031895 | -0.0021057 | 0.0010894 | 0.073433 | 0.071036 | -0.0081689 | 0.015595 | 0.0019932 | -0.086975 | 59.5184 | -62.265 | 59.8938 | -62.0041 | -62.5122 | -62.4847 | 0.041199 | 59.5413 | -62.2971 | 59.8251 | -62.1918 | -62.3703 | -62.4115 | 0.013733 | -0.20142 | 0.17395 | 0.27466 | -0.20599 | -0.23346 | -0.21973 | -0.24719 | -0.01831 | -0.17853 | 0.10528 | 0.086976 | -0.13275 | -0.091552 | -0.11444 | -0.073242 | 0.26093 | 122.1588 | 0.10529 | 122.1222 | 121.7834 | 121.8384 | 121.7972 | 121.8201 | -121.9849 | -122.0169 | 122.1725 | 122.1039 | 62.1918 | 62.3199
262.3438 | 122.2046 | -62.3154 | 59.7977 | -0.0060272 | 0.0018435 | 0.060316 | 0.062239 | 0.00043159 | -0.0055563 | -0.0021213 | -0.0082093 | 0.0038666 | 0.072578 | 0.070823 | -0.0083825 | 0.01709 | 0.0017794 | -0.054932 | 59.5963 | -62.2787 | 59.8709 | -62.0819 | -62.558 | -62.558 | -0.027466 | 59.5963 | -62.3199 | 59.7565 | -62.2696 | -62.4847 | -62.4939 | 0.036621 | -0.20142 | 0.073243 | 0.23346 | -0.24261 | -0.24261 | -0.27923 | -0.27923 | -0.004577 | -0.20142 | -0.041198 | 0.045777 | -0.17853 | -0.16937 | -0.17395 | -0.16479 | 0.19684 | 122.1497 | 0.050354 | 122.0764 | 121.875 | 121.9162 | 121.9116 | 121.9116 | -122.0764 | -122.1176 | 122.1863 | 122.0718 | 62.2604 | 62.2879
264.0312 | 122.3511 | -62.2787 | 59.7656 | -0.013657 | -0.0002927 | 0.060957 | 0.058821 | -0.0029864 | -0.0049155 | -0.0031895 | -0.0021057 | 0.00087584 | 0.07386 | 0.066764 | -0.0075281 | 0.012604 | -0.0027066 | -0.032043 | 59.5596 | -62.2375 | 59.9121 | -61.9904 | -62.4527 | -62.4435 | 0.086975 | 59.5871 | -62.3016 | 59.8846 | -62.1277 | -62.2787 | -62.3749 | 0.041199 | -0.20599 | 0.14648 | 0.28839 | -0.16479 | -0.17395 | -0.20599 | -0.21515 | -0.022888 | -0.17853 | 0.11902 | 0.15106 | -0.09613 | 0 | -0.073242 | 0.022888 | 0.24719 | 122.1497 | 0.17395 | 122.1863 | 121.7972 | 121.8887 | 121.8384 | 121.8658 | -122.0032 | -122.0673 | 122.1909 | 122.1634 | 62.2467 | 62.3657
265.7812 | 122.3373 | -62.2513 | 59.7656 | 0.0092313 | 0.0001345 | 0.060957 | 0.058394 | -0.0019184 | -0.0061971 | -0.0025485 | 0.0009461 | -0.00040596 | 0.071938 | 0.064414 | -0.0073145 | 0.015381 | -0.0020658 | -0.045776 | 59.5276 | -62.2787 | 59.903 | -62.0132 | -62.4802 | -62.471 | 0.059509 | 59.5551 | -62.3108 | 59.8434 | -62.1277 | -62.3108 | -62.3795 | -0.027466 | -0.23804 | 0.13733 | 0.23804 | -0.21973 | -0.22888 | -0.19226 | -0.20142 | -0.059509 | -0.21057 | 0.07782 | 0.1236 | -0.12817 | -0.059509 | -0.068665 | 0 | 0.2655 | 122.1817 | 0.18311 | 122.1542 | 121.8063 | 121.8658 | 121.7789 | 121.8063 | -122.0444 | -122.0764 | 122.1542 | 122.0947 | 62.2055 | 62.3108
267.5312 | 122.2183 | -62.3062 | 59.7931 | -0.013657 | 0.0009891 | 0.063521 | 0.061812 | 0.00064519 | -0.0076925 | -0.0042575 | 0.0039977 | 0.0034392 | 0.072365 | 0.0689 | -0.0088097 | 0.018372 | -0.0016384 | -0.12817 | 59.61 | -62.2833 | 59.816 | -62.1506 | -62.6129 | -62.5854 | -0.082397 | 59.6008 | -62.3291 | 59.7473 | -62.2925 | -62.4893 | -62.4939 | 0.022888 | -0.18311 | 0.022888 | 0.15564 | -0.27924 | -0.3067 | -0.30212 | -0.32959 | -0.022889 | -0.19226 | -0.045777 | 0.013733 | -0.18768 | -0.18311 | -0.16479 | -0.16022 | 0.13275 | 122.0993 | 0.036622 | 122.0764 | 121.8933 | 121.9299 | 121.9162 | 121.907 | -122.0764 | -122.1222 | 122.1222 | 122.0535 | 62.178 | 62.2238
269.2188 | 122.2321 | -62.2787 | 59.8389 | -0.013657 | -0.0005063 | 0.059035 | 0.059248 | -0.003841 | -0.0047019 | -0.0036167 | 0.0009461 | 0.00066224 | 0.072578 | 0.067618 | -0.0058191 | 0.014954 | 0.0004978 | 0.027466 | 59.5779 | -62.265 | 59.8755 | -62.0499 | -62.5351 | -62.5168 | 0.045776 | 59.6237 | -62.3062 | 59.761 | -62.2284 | -62.4023 | -62.4664 | 0.013733 | -0.26093 | 0.036621 | 0.22888 | -0.23804 | -0.25635 | -0.25177 | -0.27008 | -0.027465 | -0.21515 | -0.07782 | 0.050354 | -0.18768 | -0.1236 | -0.16022 | -0.096131 | 0.21515 | 122.1405 | 0.077819 | 122.0673 | 121.843 | 121.9299 | 121.8567 | 121.9025 | -122.1039 | -122.1451 | 122.1542 | 122.0398 | 62.3062 | 62.3245
270.9531 | 122.3007 | -62.2787 | 59.7794 | -0.013657 | -0.0005063 | 0.06053 | 0.058607 | -0.003841 | -0.0047019 | -0.0019077 | -0.0021057 | 0.00023504 | 0.070442 | 0.063987 | -0.0073145 | 0.016449 | 0.0011386 | -0.07782 | 59.5642 | -62.3016 | 59.8755 | -62.0453 | -62.5259 | -62.5031 | 0.009155 | 59.5459 | -62.3245 | 59.7931 | -62.2009 | -62.3611 | -62.4207 | -0.022888 | -0.21515 | 0.09613 | 0.23346 | -0.2243 | -0.24719 | -0.20142 | -0.2243 | -0.045776 | -0.23346 | 0.013733 | 0.07782 | -0.14191 | -0.082397 | -0.09613 | -0.036621 | 0.25635 | 122.1771 | 0.1236 | 122.1176 | 121.8658 | 121.8704 | 121.843 | 121.8246 | -122.081 | -122.1039 | 122.1542 | 122.0718 | 62.2009 | 62.2879
272.7031 | 122.2412 | -62.2787 | 59.8297 | 0.0092313 | 0.0024845 | 0.06053 | 0.061812 | 0.00085879 | -0.0055563 | -0.0021213 | -0.0021057 | 0.0023712 | 0.073433 | 0.069968 | -0.0085961 | 0.017731 | -0.0031338 | 0.009155 | 59.61 | -62.2742 | 59.8526 | -62.0911 | -62.5442 | -62.5305 | 0.009155 | 59.6283 | -62.3016 | 59.7885 | -62.2055 | -62.3978 | -62.4664 | 0.004578 | -0.21973 | 0.022888 | 0.18768 | -0.25177 | -0.2655 | -0.25635 | -0.27008 | -0.022888 | -0.20142 | -0.041199 | 0.073243 | -0.18768 | -0.11902 | -0.16479 | -0.09613 | 0.18311 | 122.1268 | 0.096131 | 122.0901 | 121.8842 | 121.9299 | 121.8887 | 121.907 | -122.1039 | -122.1313 | 122.1313 | 122.0673 | 62.2879 | 62.2879
274.4531 | 122.3099 | -62.2787 | 59.7382 | -0.013657 | 0.0016299 | 0.06288 | 0.060316 | -0.0012774 | -0.0064109 | -0.0016941 | -0.0021057 | 0.001944 | 0.070869 | 0.063346 | -0.0073145 | 0.016022 | 0.0013522 | -0.07782 | 59.5184 | -62.2604 | 59.9396 | -61.9766 | -62.4893 | -62.4619 | 0.068665 | 59.5413 | -62.3154 | 59.8526 | -62.1689 | -62.3657 | -62.4069 | 0.018311 | -0.21973 | 0.20142 | 0.30212 | -0.1831 | -0.21057 | -0.20142 | -0.22888 | -0.036621 | -0.19684 | 0.11444 | 0.10986 | -0.12817 | -0.086975 | -0.091552 | -0.050354 | 0.28381 | 122.2 | 0.14648 | 122.168 | 121.7789 | 121.8567 | 121.7972 | 121.8201 | -121.9986 | -122.0535 | 122.2183 | 122.1313 | 62.2009 | 62.3474
276.1875 | 122.2504 | -62.3108 | 59.7473 | 0.0016023 | 0.0050479 | 0.062666 | 0.061812 | 0.0027814 | -0.0057699 | -0.0031895 | -0.0021057 | 0.00044864 | 0.071083 | 0.060141 | -0.0085961 | 0.015808 | -0.0033474 | -0.13733 | 59.5734 | -62.2971 | 59.8297 | -62.1185 | -62.6083 | -62.5763 | -0.073242 | 59.6008 | -62.3566 | 59.7931 | -62.2513 | -62.4435 | -62.471 | 0.013733 | -0.17395 | 0.082398 | 0.19226 | -0.2655 | -0.29755 | -0.27924 | -0.31128 | -0.045776 | -0.14648 | 0.045777 | 0.059509 | -0.16022 | -0.13275 | -0.11444 | -0.086975 | 0.17853 | 122.1268 | 0.10528 | 122.1497 | 121.8704 | 121.9574 | 121.8842 | 121.9116 | -122.0444 | -122.1039 | 122.1405 | 122.1039 | 62.1735 | 62.2375
277.875 | 122.2641 | -62.2925 | 59.7702 | -0.0060272 | 0.0031253 | 0.063307 | 0.061171 | 0.0038494 | -0.0036337 | -0.00083947 | 0.0009461 | 0.0027984 | 0.071724 | 0.068259 | -0.0077417 | 0.016876 | -0.0009976 | -0.13275 | 59.5825 | -62.2742 | 59.8389 | -62.1002 | -62.5946 | -62.5763 | -0.041199 | 59.5642 | -62.3383 | 59.7839 | -62.2559 | -62.4298 | -62.4435 | 0.01831 | -0.18768 | 0.068664 | 0.19226 | -0.28381 | -0.30212 | -0.30212 | -0.32043 | -0.045777 | -0.20599 | 0.013733 | 0.036621 | -0.15106 | -0.13733 | -0.10529 | -0.091553 | 0.17395 | 122.113 | 0.082398 | 122.1222 | 121.8567 | 121.9025 | 121.875 | 121.8567 | -122.0444 | -122.1085 | 122.1313 | 122.0764 | 62.1597 | 62.2513
279.625 | 122.3602 | -62.2604 | 59.7382 | -0.013657 | 0.0020571 | 0.062025 | 0.058394 | -0.0036274 | -0.0068381 | -0.00041227 | 0.0009461 | 0.00066224 | 0.070015 | 0.063773 | -0.0090235 | 0.01474 | 0.0011386 | -0.054932 | 59.523 | -62.265 | 59.9258 | -61.9858 | -62.4893 | -62.4619 | 0.059509 | 59.5276 | -62.3062 | 59.8663 | -62.1689 | -62.3383 | -62.3749 | -0.004578 | -0.21515 | 0.18768 | 0.27466 | -0.20142 | -0.22888 | -0.19684 | -0.2243 | -0.045776 | -0.21057 | 0.12817 | 0.091553 | -0.11444 | -0.07782 | -0.068665 | -0.032044 | 0.27924 | 122.1909 | 0.13733 | 122.1725 | 121.788 | 121.8338 | 121.7834 | 121.788 | -122.0032 | -122.0444 | 122.1863 | 122.1268 | 62.2055 | 62.3199
281.375 | 122.3785 | -62.2238 | 59.7748 | -0.013657 | -0.0002927 | 0.059676 | 0.05818 | -0.0019184 | -0.0038473 | 1.4934e-05 | -0.0051575 | 0.0010894 | 0.069801 | 0.053305 | -0.0090235 | 0.012604 | -0.000784 | 0.022888 | 59.5505 | -62.2375 | 59.967 | -61.9171 | -62.4298 | -62.4023 | 0.16937 | 59.5551 | -62.3108 | 59.8984 | -62.0728 | -62.2604 | -62.3291 | -0.013733 | -0.2243 | 0.19226 | 0.3067 | -0.17853 | -0.20599 | -0.16479 | -0.19226 | -0.086975 | -0.21973 | 0.1236 | 0.15106 | -0.10529 | -0.036621 | -0.018311 | 0.050354 | 0.32044 | 122.2046 | 0.23804 | 122.2092 | 121.788 | 121.8658 | 121.7743 | 121.7789 | -122.0123 | -122.0856 | 122.1909 | 122.1222 | 62.2467 | 62.3932
283.1094 | 122.3282 | -62.3062 | 59.7244 | -0.0060272 | 0.0020571 | 0.062453 | 0.060744 | -0.00063661 | -0.0049155 | -0.0027621 | -0.0021057 | 0.0025848 | 0.07151 | 0.067618 | -0.0092371 | 0.014954 | -0.0054838 | -0.073242 | 59.523 | -62.2787 | 59.935 | -61.9949 | -62.4756 | -62.471 | 0.064087 | 59.5322 | -62.3245 | 59.8526 | -62.1689 | -62.3383 | -62.3932 | 0.027465 | -0.20142 | 0.21057 | 0.31128 | -0.16479 | -0.16937 | -0.19226 | -0.19684 | -0.018311 | -0.19226 | 0.12817 | 0.13733 | -0.086975 | -0.032044 | -0.068664 | -0.013733 | 0.28381 | 122.2137 | 0.15564 | 122.1771 | 121.8018 | 121.8567 | 121.8292 | 121.8384 | -122.0032 | -122.0489 | 122.2412 | 122.1588 | 62.233 | 62.3703
284.8594 | 122.2458 | -62.3062 | 59.7977 | -0.013657 | 0.0026981 | 0.061598 | 0.061171 | -0.00063661 | -0.0040609 | -0.0012669 | -0.0021057 | 0.0045074 | 0.070229 | 0.066764 | -0.0081689 | 0.017731 | -0.0037748 | -0.11902 | 59.6146 | -62.2833 | 59.8251 | -62.1185 | -62.5992 | -62.59 | -0.073242 | 59.5642 | -62.3337 | 59.7839 | -62.2559 | -62.471 | -62.4527 | 0.022888 | -0.18311 | 0.027466 | 0.18768 | -0.28381 | -0.29297 | -0.3067 | -0.31586 | -0.027466 | -0.23346 | -0.013732 | 0.050354 | -0.14648 | -0.16479 | -0.11902 | -0.13733 | 0.16479 | 122.1085 | 0.07782 | 122.1176 | 121.8979 | 121.8979 | 121.9208 | 121.8704 | -122.081 | -122.1313 | 122.1313 | 122.0901 | 62.1872 | 62.233
286.5469 | 122.3099 | -62.2925 | 59.7336 | -0.0060272 | -0.0011471 | 0.06053 | 0.057112 | -0.0027728 | -0.0057699 | 0.00044213 | -0.0051575 | 0.001944 | 0.072792 | 0.064841 | -0.0075281 | 0.015595 | -0.0039884 | -0.064087 | 59.5551 | -62.2742 | 59.903 | -62.0499 | -62.4939 | -62.4939 | 0.013733 | 59.5642 | -62.3016 | 59.8343 | -62.1735 | -62.3291 | -62.3932 | 0.01831 | -0.17853 | 0.16937 | 0.24261 | -0.20142 | -0.20142 | -0.21973 | -0.21973 | -0.009156 | -0.16937 | 0.10071 | 0.11902 | -0.10071 | -0.036622 | -0.091552 | -0.027466 | 0.2243 | 122.1771 | 0.12817 | 122.1359 | 121.8292 | 121.8658 | 121.8475 | 121.8567 | -122.0078 | -122.0352 | 122.1954 | 122.1268 | 62.2284 | 62.3062
288.2969 | 122.2778 | -62.265 | 59.7794 | -0.0060272 | -0.0005063 | 0.060316 | 0.060316 | 0.00043159 | -0.0040609 | -0.0034031 | -0.0021057 | 0.0010894 | 0.074501 | 0.062278 | -0.0083825 | 0.016663 | 0.0002842 | -0.086975 | 59.5367 | -62.2467 | 59.8938 | -62.059 | -62.5031 | -62.5031 | 0.009155 | 59.5596 | -62.3016 | 59.8068 | -62.2055 | -62.3749 | -62.4252 | 0.018311 | -0.24262 | 0.11444 | 0.20599 | -0.23804 | -0.23804 | -0.25635 | -0.25635 | -0.036621 | -0.21973 | 0.027466 | 0.05951 | -0.16022 | -0.10986 | -0.1236 | -0.073242 | 0.18768 | 122.1405 | 0.096131 | 122.1085 | 121.7834 | 121.8613 | 121.8018 | 121.8246 | -122.0261 | -122.081 | 122.1588 | 122.0718 | 62.178 | 62.2742
290.0625 | 122.3557 | -62.2787 | 59.7748 | 0.0016023 | 0.0001345 | 0.059035 | 0.059035 | 0.001286 | -0.0049155 | -0.0023349 | -0.0021057 | 0.00087584 | 0.072365 | 0.074241 | -0.0098779 | 0.01474 | -0.0037748 | -0.004578 | 59.5322 | -62.2559 | 59.9487 | -61.9766 | -62.4298 | -62.4161 | 0.14191 | 59.5505 | -62.2879 | 59.8892 | -62.1185 | -62.3016 | -62.3566 | 0.022889 | -0.24261 | 0.17395 | 0.30212 | -0.13733 | -0.15106 | -0.16022 | -0.17395 | -0.009155 | -0.2243 | 0.11444 | 0.16022 | -0.077819 | -0.022888 | -0.068664 | -0.013733 | 0.27923 | 122.2046 | 0.16937 | 122.1771 | 121.788 | 121.8384 | 121.8109 | 121.8292 | -122.0306 | -122.0627 | 122.2275 | 122.168 | 62.2742 | 62.4207
291.75 | 122.2137 | -62.2787 | 59.8434 | 0.0016023 | -0.0009335 | 0.060957 | 0.060316 | -0.0044818 | -0.0051291 | -0.0012669 | -0.0021057 | 0.0045074 | 0.073647 | 0.068473 | -0.0083825 | 0.015595 | -0.0056974 | 0 | 59.6283 | -62.2467 | 59.8526 | -62.0773 | -62.5259 | -62.5122 | 0.036621 | 59.642 | -62.2742 | 59.7748 | -62.233 | -62.4161 | -62.4802 | 0.032044 | -0.21515 | 0.009155 | 0.20142 | -0.23346 | -0.24719 | -0.2655 | -0.27924 | 0.004578 | -0.20142 | -0.068665 | 0.045777 | -0.20142 | -0.13733 | -0.20599 | -0.14191 | 0.16937 | 122.0993 | 0.041199 | 122.0489 | 121.875 | 121.9162 | 121.907 | 121.9208 | -122.0901 | -122.1176 | 122.1313 | 122.0535 | 62.2787 | 62.3154
293.5 | 122.2092 | -62.2879 | 59.8389 | -0.0060272 | 0.0009891 | 0.059676 | 0.060103 | 0.0027814 | -0.0036337 | -0.0019077 | -0.0021057 | 0.0015166 | 0.071938 | 0.073813 | -0.0085961 | 0.01474 | -0.005911 | -0.013733 | 59.6283 | -62.2925 | 59.8755 | -62.0728 | -62.5305 | -62.5214 | 0.032043 | 59.6283 | -62.2925 | 59.761 | -62.2284 | -62.4115 | -62.4573 | -0.004577 | -0.21057 | 0.036621 | 0.21515 | -0.23346 | -0.24262 | -0.22888 | -0.23804 | -0.004577 | -0.21057 | -0.07782 | 0.059509 | -0.16937 | -0.1236 | -0.1648 | -0.11902 | 0.21973 | 122.168 | 0.064086 | 122.0535 | 121.9208 | 121.9208 | 121.9162 | 121.9162 | -122.1313 | -122.1313 | 122.1634 | 122.0489 | 62.2742 | 62.3199
295.25 | 122.3465 | -62.2787 | 59.761 | -0.013657 | 0.0026981 | 0.06288 | 0.059462 | -0.0036274 | -0.0032065 | -0.00083947 | -0.0021057 | 0.0015166 | 0.069801 | 0.063346 | -0.0088097 | 0.015381 | -0.0016384 | -0.073242 | 59.523 | -62.2513 | 59.9442 | -61.9995 | -62.4985 | -62.471 | 0.064087 | 59.5276 | -62.3245 | 59.8755 | -62.1506 | -62.3383 | -62.3703 | 0.027466 | -0.23804 | 0.18311 | 0.27924 | -0.19226 | -0.21973 | -0.21973 | -0.24719 | -0.045776 | -0.23346 | 0.11444 | 0.12817 | -0.091552 | -0.059509 | -0.045776 | -0.013733 | 0.25177 | 122.1954 | 0.17395 | 122.2 | 121.7743 | 121.8521 | 121.8018 | 121.8063 | -122.0123 | -122.0856 | 122.2229 | 122.1542 | 62.2055 | 62.3428
296.9219 | 122.2916 | -62.2879 | 59.7656 | -0.0060272 | -0.0002927 | 0.060744 | 0.059248 | -0.0032 | -0.0038473 | -0.0036167 | -0.0051575 | 0.00066224 | 0.070442 | 0.066336 | -0.0085961 | 0.016876 | -0.0014248 | -0.07782 | 59.5459 | -62.2238 | 59.8801 | -62.0453 | -62.5259 | -62.5031 | 0.018311 | 59.5596 | -62.3337 | 59.8022 | -62.2009 | -62.3749 | -62.4207 | 0.064087 | -0.21973 | 0.11444 | 0.24262 | -0.21515 | -0.23804 | -0.27924 | -0.30212 | -0.045776 | -0.20599 | 0.036621 | 0.086975 | -0.13275 | -0.086975 | -0.086975 | -0.041199 | 0.17853 | 122.1039 | 0.13275 | 122.1359 | 121.7697 | 121.8933 | 121.8338 | 121.8475 | -121.9894 | -122.0993 | 122.168 | 122.0901 | 62.2101 | 62.3062
298.6719 | 122.2183 | -62.2833 | 59.816 | 0.0016023 | 0.0012027 | 0.061598 | 0.061171 | 0.00064519 | -0.0064109 | -0.00019867 | 0.0039977 | 0.0051482 | 0.070229 | 0.068259 | -0.0075281 | 0.017731 | -0.0054838 | 0.004578 | 59.6375 | -62.2513 | 59.8572 | -62.0865 | -62.5397 | -62.5351 | 0.027466 | 59.6283 | -62.3154 | 59.7702 | -62.233 | -62.4252 | -62.4527 | 0.032043 | -0.17853 | 0.041199 | 0.19684 | -0.25177 | -0.25635 | -0.28381 | -0.28839 | -0.032044 | -0.18768 | -0.045776 | 0.050354 | -0.16937 | -0.14191 | -0.13733 | -0.10986 | 0.1648 | 122.1085 | 0.082398 | 122.0856 | 121.8887 | 121.9437 | 121.9208 | 121.9116 | -122.0673 | -122.1313 | 122.1405 | 122.0535 | 62.2879 | 62.3108
300.4062 | 122.3648 | -62.2742 | 59.7748 | -0.0060272 | -0.0009335 | 0.061598 | 0.060103 | -0.0017048 | -0.0049155 | -0.00062587 | -0.0051575 | 0.00087584 | 0.072578 | 0.060141 | -0.0073145 | 0.016449 | -0.0005704 | 0.013733 | 59.5551 | -62.265 | 59.9579 | -61.9583 | -62.4207 | -62.4161 | 0.15106 | 59.5688 | -62.3016 | 59.8984 | -62.1002 | -62.2559 | -62.352 | 0.009155 | -0.21973 | 0.18311 | 0.31586 | -0.14191 | -0.14648 | -0.15106 | -0.15564 | -0.027466 | -0.20599 | 0.1236 | 0.17395 | -0.07782 | 0.018311 | -0.050354 | 0.045777 | 0.3067 | 122.2229 | 0.20142 | 122.2 | 121.8201 | 121.8704 | 121.8292 | 121.843 | -122.0398 | -122.0764 | 122.2321 | 122.1725 | 62.2879 | 62.4252
302.1406 | 122.3007 | -62.2833 | 59.7748 | -0.0060272 | 0.0016299 | 0.061385 | 0.059676 | -0.00042301 | -0.0068381 | -0.0023349 | -0.0021057 | 0.0032256 | 0.07151 | 0.062918 | -0.0064599 | 0.015595 | -0.0014248 | -0.09613 | 59.5413 | -62.2742 | 59.9075 | -62.0132 | -62.5122 | -62.4985 | 0.027466 | 59.5734 | -62.3199 | 59.8206 | -62.1872 | -62.3657 | -62.4115 | 0.009155 | -0.23346 | 0.13275 | 0.27008 | -0.21515 | -0.22888 | -0.2243 | -0.23804 | -0.036621 | -0.20142 | 0.045777 | 0.09613 | -0.12817 | -0.082398 | -0.091553 | -0.045777 | 0.26093 | 122.1817 | 0.13275 | 122.1405 | 121.8155 | 121.8933 | 121.8246 | 121.8567 | -122.0489 | -122.0947 | 122.1909 | 122.1039 | 62.1872 | 62.3108
303.8281 | 122.3373 | -62.2787 | 59.7382 | -0.0060272 | 0.0035525 | 0.063948 | 0.060316 | 0.00043159 | -0.0034201 | -0.0023349 | -0.0082093 | 0.0025848 | 0.07151 | 0.061637 | -0.0096643 | 0.018158 | -0.00527 | -0.068665 | 59.5413 | -62.265 | 59.9442 | -61.9904 | -62.4802 | -62.4619 | 0.07782 | 59.5367 | -62.3291 | 59.8663 | -62.146 | -62.3199 | -62.3932 | 0.013733 | -0.19684 | 0.20599 | 0.28839 | -0.1831 | -0.20142 | -0.19684 | -0.21515 | -0.050354 | -0.20142 | 0.12817 | 0.13275 | -0.11444 | -0.041198 | -0.064086 | 0.009156 | 0.27466 | 122.2092 | 0.18311 | 122.1954 | 121.8063 | 121.8658 | 121.8201 | 121.8155 | -122.0032 | -122.0673 | 122.2229 | 122.1451 | 62.2101 | 62.3566
305.5781 | 122.2778 | -62.2879 | 59.7473 | -0.013657 | 0.0003483 | 0.060744 | 0.059462 | -0.0044818 | -0.0059835 | 0.0023647 | -0.0021057 | 0.00044864 | 0.068947 | 0.061637 | -0.0096643 | 0.016235 | -0.004202 | -0.086975 | 59.5459 | -62.2833 | 59.8846 | -62.0499 | -62.5214 | -62.4893 | -0.004578 | 59.5734 | -62.3291 | 59.8114 | -62.2147 | -62.3932 | -62.4344 | 0.004578 | -0.20142 | 0.13733 | 0.23804 | -0.20142 | -0.23346 | -0.20599 | -0.23804 | -0.041199 | -0.17395 | 0.064087 | 0.073242 | -0.14648 | -0.10529 | -0.10529 | -0.064086 | 0.23346 | 122.168 | 0.11444 | 122.1405 | 121.8292 | 121.9025 | 121.8338 | 121.8613 | -122.0306 | -122.0764 | 122.1725 | 122.0993 | 62.2009 | 62.2833
307.2656 | 122.2641 | -62.2971 | 59.761 | 0.0016023 | 0.0022709 | 0.063307 | 0.062025 | -0.00020941 | -0.0034201 | -0.0014805 | -0.0051575 | 0.004721 | 0.072578 | 0.069541 | -0.0079553 | 0.016876 | 0.0011386 | -0.13733 | 59.5963 | -62.2787 | 59.8526 | -62.1094 | -62.59 | -62.5809 | -0.064087 | 59.5963 | -62.3199 | 59.7839 | -62.2421 | -62.4527 | -62.4527 | 0.01831 | -0.16479 | 0.091553 | 0.18768 | -0.28381 | -0.29297 | -0.30212 | -0.31128 | -0.022888 | -0.16479 | 0.022889 | 0.054932 | -0.15564 | -0.15564 | -0.13275 | -0.13275 | 0.16937 | 122.1313 | 0.07782 | 122.1039 | 121.875 | 121.9162 | 121.8933 | 121.8933 | -122.0398 | -122.081 | 122.1497 | 122.081 | 62.1597 | 62.233
309 | 122.2687 | -62.2879 | 59.7748 | 0.0016023 | 0.0031253 | 0.063521 | 0.060103 | -0.0010638 | -0.0051291 | -0.0027621 | -0.0051575 | 0.0057892 | 0.072151 | 0.064414 | -0.0053919 | 0.017944 | -0.0018522 | 0.009155 | 59.6237 | -62.2604 | 59.8892 | -62.059 | -62.5214 | -62.5168 | 0.054932 | 59.6008 | -62.2833 | 59.816 | -62.1964 | -62.384 | -62.439 | 0.027466 | -0.15106 | 0.11444 | 0.22888 | -0.22888 | -0.23346 | -0.25635 | -0.26093 | 0.004578 | -0.17395 | 0.041199 | 0.091553 | -0.15106 | -0.09613 | -0.15564 | -0.10071 | 0.20142 | 122.1497 | 0.086975 | 122.0993 | 121.8842 | 121.8842 | 121.9116 | 121.8887 | -122.0352 | -122.0581 | 122.1771 | 122.1039 | 62.2971 | 62.3428
310.75 | 122.2366 | -62.2879 | 59.7977 | 0.0016023 | 0.0022709 | 0.062239 | 0.060957 | 0.00021799 | -0.0029929 | -0.00062587 | 0.0009461 | 0.003012 | 0.072365 | 0.072104 | -0.0077417 | 0.019012 | -0.005911 | -0.009155 | 59.6237 | -62.2787 | 59.8938 | -62.0544 | -62.5076 | -62.5168 | 0.041199 | 59.6283 | -62.3016 | 59.8343 | -62.1964 | -62.384 | -62.4298 | 0.009155 | -0.17395 | 0.096131 | 0.23346 | -0.22888 | -0.21973 | -0.23804 | -0.22888 | -0.013733 | -0.16937 | 0.036622 | 0.091553 | -0.14191 | -0.09613 | -0.12817 | -0.082397 | 0.22431 | 122.1725 | 0.10529 | 122.1359 | 121.9025 | 121.9299 | 121.9116 | 121.9162 | -122.0764 | -122.0993 | 122.1817 | 122.1222 | 62.2787 | 62.3291
312.5 | 122.3053 | -62.2925 | 59.761 | -0.0060272 | 0.0029117 | 0.061812 | 0.058607 | -0.0019184 | -0.0040609 | -0.0021213 | -0.0021057 | -0.0016876 | 0.070656 | 0.069327 | -0.0060327 | 0.01709 | -0.0054838 | -0.091553 | 59.5596 | -62.2513 | 59.8755 | -62.0407 | -62.5076 | -62.4847 | 0.004578 | 59.5596 | -62.3062 | 59.8114 | -62.1964 | -62.3657 | -62.4115 | 0.041198 | -0.20142 | 0.11444 | 0.25177 | -0.19226 | -0.21515 | -0.23346 | -0.25635 | -0.013733 | -0.20142 | 0.050354 | 0.09613 | -0.11902 | -0.073243 | -0.10529 | -0.05951 | 0.21057 | 122.1268 | 0.10986 | 122.1176 | 121.8109 | 121.8658 | 121.8521 | 121.8521 | -122.0123 | -122.0673 | 122.168 | 122.1039 | 62.2009 | 62.2971
314.1875 | 122.3465 | -62.2925 | 59.7519 | 0.0016023 | 0.0029117 | 0.061385 | 0.058607 | -0.0017048 | -0.0025655 | -0.0038303 | -0.0021057 | 0.0010894 | 0.07151 | 0.0642 | -0.0092371 | 0.015808 | -0.0012112 | -0.10986 | 59.6054 | -62.2742 | 59.8984 | -62.0499 | -62.5168 | -62.4893 | 0.018311 | 59.5596 | -62.3199 | 59.8663 | -62.1689 | -62.3474 | -62.3703 | 0.01831 | -0.14648 | 0.14648 | 0.24261 | -0.19684 | -0.22431 | -0.21515 | -0.24262 | -0.027466 | -0.19226 | 0.11444 | 0.1236 | -0.07782 | -0.054932 | -0.050354 | -0.027466 | 0.2243 | 122.1725 | 0.15106 | 122.1863 | 121.8796 | 121.8796 | 121.8979 | 121.8521 | -122.0261 | -122.0718 | 122.1909 | 122.1588 | 62.1826 | 62.3108
315.9219 | 122.2046 | -62.2833 | 59.816 | -0.013657 | 0.0041935 | 0.064589 | 0.061598 | 0.0010724 | -0.0025655 | -0.00062587 | 0.0009461 | 0.003012 | 0.071938 | 0.067191 | -0.0073145 | 0.017944 | -0.0022794 | -0.045776 | 59.6237 | -62.265 | 59.8663 | -62.0819 | -62.5717 | -62.5626 | -0.018311 | 59.6191 | -62.3154 | 59.7748 | -62.2696 | -62.4756 | -62.4802 | 0.01831 | -0.19226 | 0.050354 | 0.20142 | -0.27924 | -0.28839 | -0.29755 | -0.3067 | -0.032044 | -0.19684 | -0.041199 | 0.013733 | -0.19684 | -0.19226 | -0.1648 | -0.16022 | 0.18311 | 122.1313 | 0.045777 | 122.0901 | 121.8887 | 121.9345 | 121.907 | 121.9025 | -122.081 | -122.1313 | 122.1497 | 122.0581 | 62.2375 | 62.265
317.5938 | 122.319 | -62.2971 | 59.729 | -0.0060272 | 0.0039799 | 0.060744 | 0.058607 | -0.00020941 | -0.0053427 | -0.0016941 | 0.0009461 | -0.00083316 | 0.072578 | 0.061209 | -0.0079553 | 0.015167 | 7.04e-05 | -0.073242 | 59.5413 | -62.2375 | 59.9304 | -61.9858 | -62.4985 | -62.4664 | 0.036621 | 59.5322 | -62.3428 | 59.8434 | -62.1872 | -62.3566 | -62.4069 | 0.059509 | -0.18768 | 0.20142 | 0.31128 | -0.16937 | -0.20142 | -0.22888 | -0.26093 | -0.045776 | -0.19684 | 0.11444 | 0.10986 | -0.10986 | -0.059509 | -0.064087 | -0.013733 | 0.25177 | 122.168 | 0.15564 | 122.1863 | 121.7789 | 121.875 | 121.8384 | 121.8292 | -121.9666 | -122.0718 | 122.2275 | 122.1405 | 62.2238 | 62.3337
319.2812 | 122.3053 | -62.2925 | 59.7519 | -0.0060272 | 0.0037661 | 0.062239 | 0.061598 | -0.00042301 | -0.0053427 | -0.0021213 | 0.0039977 | 0.0038666 | 0.073647 | 0.062705 | -0.0088097 | 0.016876 | 7.04e-05 | -0.13275 | 59.6008 | -62.2879 | 59.8434 | -62.1094 | -62.59 | -62.5534 | -0.018311 | 59.5596 | -62.3154 | 59.8434 | -62.2192 | -62.3978 | -62.4069 | 0.004577 | -0.15106 | 0.091553 | 0.1831 | -0.26093 | -0.29755 | -0.2655 | -0.30212 | -0.022889 | -0.19226 | 0.091553 | 0.073242 | -0.11444 | -0.10529 | -0.091552 | -0.082397 | 0.17853 | 122.1313 | 0.096131 | 122.1588 | 121.8887 | 121.875 | 121.8933 | 121.8521 | -122.0398 | -122.0673 | 122.1359 | 122.1359 | 62.1597 | 62.2742
321 | 122.2687 | -62.2696 | 59.8114 | 0.0016023 | -0.0015743 | 0.061812 | 0.057753 | -0.0017048 | -0.0068381 | 0.00044213 | -0.0021057 | -0.00061956 | 0.074501 | 0.067832 | -0.0098779 | 0.016022 | -0.00527 | 0.064087 | 59.5596 | -62.2513 | 59.9533 | -61.9675 | -62.4435 | -62.439 | 0.11444 | 59.5871 | -62.3016 | 59.8434 | -62.1414 | -62.3337 | -62.3978 | 0.01831 | -0.25177 | 0.14191 | 0.30212 | -0.16937 | -0.17395 | -0.18768 | -0.19226 | -0.032044 | -0.2243 | 0.032044 | 0.12817 | -0.12817 | -0.064087 | -0.09613 | -0.032043 | 0.28381 | 122.2046 | 0.16022 | 122.1451 | 121.8109 | 121.8887 | 121.8292 | 121.8567 | -122.0627 | -122.113 | 122.2229 | 122.113 | 62.3337 | 62.384
322.75 | 122.287 | -62.2787 | 59.7565 | -0.0060272 | 0.0022709 | 0.061812 | 0.058394 | -0.00042301 | -0.0057699 | 0.00065573 | -0.0021057 | 0.00023504 | 0.071724 | 0.057151 | -0.0077417 | 0.01709 | -0.0056974 | -0.091553 | 59.5459 | -62.2742 | 59.903 | -62.0132 | -62.5122 | -62.4802 | 0.050354 | 59.5459 | -62.3016 | 59.848 | -62.1872 | -62.3703 | -62.4161 | 0.004578 | -0.21057 | 0.14648 | 0.2655 | -0.20142 | -0.23346 | -0.20599 | -0.23804 | -0.022888 | -0.21057 | 0.091552 | 0.091553 | -0.13733 | -0.091552 | -0.11444 | -0.068664 | 0.26093 | 122.1771 | 0.11444 | 122.1497 | 121.8201 | 121.8475 | 121.8246 | 121.8246 | -122.0306 | -122.0581 | 122.1817 | 122.1268 | 62.1872 | 62.3291
324.4844 | 122.374 | -62.2559 | 59.7931 | 0.0016023 | -0.0011471 | 0.059462 | 0.057753 | -0.00042301 | -0.0055563 | -0.0034031 | -0.0021057 | 0.00066224 | 0.072151 | 0.062918 | -0.010946 | 0.016022 | -0.0020658 | 0.018311 | 59.5596 | -62.2513 | 59.9716 | -61.94 | -62.4252 | -62.4115 | 0.16022 | 59.5505 | -62.2742 | 59.9075 | -62.1002 | -62.2604 | -62.3428 | 0.004577 | -0.23346 | 0.17853 | 0.31586 | -0.15564 | -0.16937 | -0.16022 | -0.17395 | -0.018311 | -0.24261 | 0.11444 | 0.15564 | -0.086975 | -0.004578 | -0.068664 | 0.013733 | 0.31128 | 122.2229 | 0.17395 | 122.1817 | 121.8109 | 121.8246 | 121.8155 | 121.8063 | -122.0444 | -122.0673 | 122.2275 | 122.1634 | 62.2742 | 62.4161
326.2188 | 122.3602 | -62.2467 | 59.7839 | -0.0060272 | -0.0017881 | 0.06053 | 0.058607 | -0.001491 | -0.0055563 | 0.00044213 | -0.0051575 | 0.001944 | 0.070869 | 0.072959 | -0.0096643 | 0.017303 | -0.00527 | 0.032043 | 59.5459 | -62.233 | 59.9762 | -61.9125 | -62.4069 | -62.4023 | 0.19226 | 59.5688 | -62.2879 | 59.8846 | -62.0865 | -62.2559 | -62.3566 | 0.013733 | -0.23804 | 0.19226 | 0.33417 | -0.15564 | -0.16022 | -0.16937 | -0.17395 | -0.041199 | -0.21515 | 0.10071 | 0.16022 | -0.10986 | -0.009155 | -0.068664 | 0.032044 | 0.32043 | 122.2092 | 0.20142 | 122.1725 | 121.7789 | 121.8567 | 121.7926 | 121.8155 | -122.0169 | -122.0718 | 122.2229 | 122.1313 | 62.2787 | 62.439
327.9531 | 122.319 | -62.2879 | 59.7382 | -0.021286 | 0.0039799 | 0.063307 | 0.058821 | 0.001286 | -0.0027793 | -0.0025485 | -0.0021057 | 0.0017304 | 0.073433 | 0.069114 | -0.0085961 | 0.016876 | -0.0037748 | -0.073242 | 59.5139 | -62.2787 | 59.9304 | -61.9949 | -62.4893 | -62.4573 | 0.059509 | 59.5459 | -62.3108 | 59.8663 | -62.1597 | -62.3383 | -62.3611 | 0.009155 | -0.2243 | 0.19226 | 0.29297 | -0.16937 | -0.20142 | -0.17853 | -0.21057 | -0.022888 | -0.19226 | 0.12817 | 0.12817 | -0.073242 | -0.050354 | -0.050354 | -0.027466 | 0.28381 | 122.2092 | 0.15106 | 122.1771 | 121.7926 | 121.8567 | 121.8018 | 121.8338 | -122.0169 | -122.049 | 122.2183 | 122.1542 | 62.2147 | 62.3474
329.6406 | 122.2183 | -62.3016 | 59.7977 | -0.0060272 | 0.0033389 | 0.062239 | 0.06288 | -0.0010638 | -0.0055563 | -0.0040439 | -0.0051575 | 0.003653 | 0.073647 | 0.072104 | -0.0085961 | 0.015167 | -0.0012112 | -0.050354 | 59.5963 | -62.2742 | 59.8709 | -62.0911 | -62.5671 | -62.5442 | -0.004578 | 59.61 | -62.3383 | 59.7748 | -62.265 | -62.4573 | -62.4802 | 0.027466 | -0.20142 | 0.073243 | 0.21057 | -0.24261 | -0.2655 | -0.27008 | -0.29297 | -0.036621 | -0.18768 | -0.022888 | 0.036621 | -0.17853 | -0.15564 | -0.14191 | -0.11902 | 0.18311 | 122.1451 | 0.073242 | 122.113 | 121.8704 | 121.9482 | 121.8979 | 121.9116 | -122.0718 | -122.1359 | 122.1725 | 122.0764 | 62.2513 | 62.2971
331.375 | 122.1954 | -62.2833 | 59.8068 | -0.013657 | 0.0031253 | 0.061598 | 0.061812 | 0.0049176 | -0.0044883 | 0.0010831 | -0.0051575 | 0.0032256 | 0.070869 | 0.070182 | -0.0079553 | 0.018372 | -0.0022794 | -0.059509 | 59.61 | -62.2971 | 59.8434 | -62.1002 | -62.5946 | -62.5717 | -0.045776 | 59.6191 | -62.3245 | 59.761 | -62.2787 | -62.4664 | -62.4802 | -0.013733 | -0.19684 | 0.036621 | 0.1831 | -0.28839 | -0.31128 | -0.27466 | -0.29755 | -0.041199 | -0.18768 | -0.045777 | 0.004577 | -0.19684 | -0.18311 | -0.15564 | -0.14191 | 0.19684 | 122.1405 | 0.045776 | 122.0856 | 121.907 | 121.9437 | 121.8933 | 121.9025 | -122.1039 | -122.1313 | 122.1268 | 122.0444 | 62.2238 | 62.2375
333.0469 | 122.287 | -62.2604 | 59.7794 | -0.013657 | 0.0007755 | 0.061598 | 0.058607 | -0.001491 | -0.0038473 | -0.0025485 | -0.0021057 | 0.001303 | 0.071938 | 0.062918 | -0.0077417 | 0.014954 | 0.0002842 | -0.073242 | 59.5734 | -62.2604 | 59.8846 | -62.0682 | -62.5168 | -62.5031 | 0.004578 | 59.5642 | -62.3245 | 59.816 | -62.1964 | -62.3657 | -62.4161 | 0 | -0.20599 | 0.10529 | 0.19226 | -0.24261 | -0.25635 | -0.24261 | -0.25635 | -0.064087 | -0.21515 | 0.036621 | 0.064087 | -0.15564 | -0.10529 | -0.091553 | -0.041199 | 0.19226 | 122.1451 | 0.12817 | 122.1405 | 121.8338 | 121.8887 | 121.8338 | 121.8246 | -122.0398 | -122.1039 | 122.1451 | 122.0764 | 62.1872 | 62.265
334.8125 | 122.2961 | -62.2879 | 59.7702 | -0.0060272 | 0.0005619 | 0.059676 | 0.059889 | -0.0019184 | -0.0064109 | -0.0027621 | 0.0009461 | 0.00066224 | 0.070442 | 0.059073 | -0.0064599 | 0.014954 | -0.0018522 | -0.10071 | 59.5459 | -62.2833 | 59.8938 | -62.0361 | -62.5214 | -62.4939 | -0.004578 | 59.5688 | -62.3062 | 59.8297 | -62.2101 | -62.3795 | -62.4344 | 0.004578 | -0.22431 | 0.1236 | 0.25177 | -0.20599 | -0.23346 | -0.21057 | -0.23804 | -0.01831 | -0.20142 | 0.059509 | 0.07782 | -0.14648 | -0.091553 | -0.12817 | -0.073243 | 0.24719 | 122.1771 | 0.09613 | 122.1359 | 121.8292 | 121.875 | 121.8338 | 121.8567 | -122.0535 | -122.0764 | 122.1817 | 122.1176 | 62.1872 | 62.2833
336.4844 | 122.1954 | -62.2833 | 59.8251 | 0.0092313 | -0.0009335 | 0.059889 | 0.059462 | -0.0017048 | -0.0061971 | -0.0023349 | -0.0051575 | 0.0023712 | 0.072365 | 0.059073 | -0.0077417 | 0.015381 | -0.0001432 | -0.013733 | 59.6054 | -62.2742 | 59.8526 | -62.0865 | -62.5259 | -62.5031 | 0.027466 | 59.6512 | -62.2971 | 59.7839 | -62.2375 | -62.4161 | -62.4664 | 0.009155 | -0.21973 | 0.027466 | 0.19684 | -0.21973 | -0.24262 | -0.22888 | -0.25177 | -0.013733 | -0.17395 | -0.041198 | 0.045776 | -0.18311 | -0.13275 | -0.16937 | -0.11902 | 0.18768 | 122.1268 | 0.059509 | 122.081 | 121.8796 | 121.9482 | 121.8887 | 121.9345 | -122.0993 | -122.1222 | 122.1359 | 122.0673 | 62.2696 | 62.3108
338.1719 | 122.2092 | -62.3108 | 59.7839 | -0.0060272 | 0.0048343 | 0.061812 | 0.063521 | 0.0014996 | -0.0055563 | -0.0023349 | -0.0021057 | 0.003653 | 0.070869 | 0.0642 | -0.0079553 | 0.018158 | 0.0011386 | -0.11444 | 59.6191 | -62.2696 | 59.8068 | -62.1735 | -62.6358 | -62.5992 | -0.086975 | 59.6054 | -62.3428 | 59.7565 | -62.2971 | -62.4893 | -62.5031 | 0.041199 | -0.16479 | 0.022888 | 0.13733 | -0.28839 | -0.32501 | -0.32959 | -0.36621 | -0.032043 | -0.17853 | -0.027466 | 0.013733 | -0.19226 | -0.17853 | -0.16022 | -0.14648 | 0.09613 | 122.0764 | 0.045776 | 122.0993 | 121.8887 | 121.9482 | 121.9299 | 121.9162 | -122.0535 | -122.1268 | 122.1176 | 122.0673 | 62.1964 | 62.2238
339.9219 | 122.3236 | -62.2742 | 59.7153 | -0.0060272 | 0.0014163 | 0.063734 | 0.06053 | -0.0012774 | -0.0040609 | -0.0019077 | -0.0051575 | 0.0034392 | 0.072578 | 0.062278 | -0.0085961 | 0.015381 | 0.0011386 | -0.086975 | 59.5505 | -62.2559 | 59.9213 | -61.9858 | -62.4893 | -62.4619 | 0.064087 | 59.5642 | -62.3108 | 59.8618 | -62.1552 | -62.352 | -62.3795 | 0.018311 | -0.16479 | 0.20599 | 0.28839 | -0.18768 | -0.21515 | -0.20599 | -0.23346 | -0.036621 | -0.15106 | 0.14648 | 0.11902 | -0.10529 | -0.07782 | -0.068665 | -0.041199 | 0.27008 | 122.1771 | 0.15564 | 122.1725 | 121.8063 | 121.875 | 121.8246 | 121.8384 | -121.9711 | -122.0261 | 122.1954 | 122.1359 | 62.1872 | 62.3383
341.6719 | 122.2229 | -62.2742 | 59.7885 | 0.0016023 | 0.0016299 | 0.062239 | 0.062453 | 0.00043159 | -0.0034201 | -0.0012669 | -0.011261 | 0.0032256 | 0.072792 | 0.065055 | -0.0083825 | 0.017517 | -0.0029202 | -0.018311 | 59.61 | -62.265 | 59.8892 | -62.0636 | -62.5259 | -62.5214 | 0.032043 | 59.6008 | -62.3291 | 59.7977 | -62.233 | -62.4298 | -62.4435 | 0.009155 | -0.17853 | 0.10071 | 0.21057 | -0.24719 | -0.25177 | -0.25635 | -0.26093 | -0.054932 | -0.18768 | 0.009155 | 0.041199 | -0.16937 | -0.15564 | -0.11444 | -0.10071 | 0.20142 | 122.1542 | 0.096131 | 122.1268 | 121.875 | 121.9299 | 121.8842 | 121.875 | -122.0535 | -122.1176 | 122.1634 | 122.0718 | 62.2559 | 62.3062
343.4062 | 122.2183 | -62.3062 | 59.7931 | 0.0016023 | 0.0029117 | 0.062453 | 0.060316 | 0.00085879 | -0.0059835 | -0.00041227 | 0.0009461 | 0.0010894 | 0.072792 | 0.06655 | -0.0071009 | 0.017517 | -0.0003568 | -0.032043 | 59.6191 | -62.2833 | 59.8755 | -62.0728 | -62.5717 | -62.5351 | 0.004578 | 59.6054 | -62.3062 | 59.7748 | -62.2696 | -62.4802 | -62.4847 | 0.022888 | -0.17395 | 0.082397 | 0.23346 | -0.22888 | -0.2655 | -0.25177 | -0.28839 | 0 | -0.18768 | -0.018311 | 0.036621 | -0.17853 | -0.17395 | -0.17853 | -0.17395 | 0.21057 | 122.1588 | 0.036621 | 122.081 | 121.9025 | 121.9116 | 121.9254 | 121.9116 | -122.0764 | -122.0993 | 122.1817 | 122.081 | 62.2742 | 62.3108
345.1562 | 122.2 | -62.3108 | 59.816 | -0.0060272 | 0.0037661 | 0.062453 | 0.06288 | -0.00042301 | -0.0040609 | -0.0044711 | 0.0009461 | 0.003653 | 0.074287 | 0.058432 | -0.0062463 | 0.020081 | -0.0020658 | -0.091553 | 59.6329 | -62.2879 | 59.8251 | -62.1231 | -62.5946 | -62.5671 | -0.082397 | 59.6146 | -62.3154 | 59.7473 | -62.2925 | -62.4847 | -62.471 | 0.022888 | -0.1831 | 0.009155 | 0.18768 | -0.25635 | -0.28381 | -0.27924 | -0.3067 | -0.004578 | -0.20142 | -0.068665 | 0.018311 | -0.16022 | -0.17395 | -0.15564 | -0.16937 | 0.16479 | 122.113 | 0.022889 | 122.0627 | 121.9208 | 121.9299 | 121.9437 | 121.9254 | -122.1039 | -122.1313 | 122.1359 | 122.0581 | 62.2192 | 62.2284
346.8438 | 122.3328 | -62.2742 | 59.7244 | -0.021286 | 0.0026981 | 0.061385 | 0.059462 | 0.0044904 | -0.0032065 | -0.0016941 | 0.0039977 | 0.0010894 | 0.07151 | 0.060141 | -0.0064599 | 0.016876 | -0.0022794 | -0.07782 | 59.5276 | -62.2513 | 59.9304 | -61.9812 | -62.4802 | -62.4435 | 0.068665 | 59.5322 | -62.3337 | 59.848 | -62.1643 | -62.3474 | -62.3657 | 0.022888 | -0.19684 | 0.20599 | 0.29297 | -0.16937 | -0.20599 | -0.19226 | -0.22888 | -0.059509 | -0.19226 | 0.1236 | 0.10986 | -0.091553 | -0.073242 | -0.032044 | -0.013733 | 0.27008 | 122.1817 | 0.16937 | 122.1817 | 121.7789 | 121.8658 | 121.8018 | 121.8063 | -121.9757 | -122.0581 | 122.2046 | 122.1222 | 62.1963 | 62.3428
348.5781 | 122.3419 | -62.2833 | 59.7473 | -0.021286 | 0.0044071 | 0.062239 | 0.059248 | 4.192e-06 | -0.0057699 | -0.0025485 | -0.0051575 | 0.0017304 | 0.070869 | 0.063559 | -0.0066735 | 0.017303 | 0.0022068 | -0.064087 | 59.5413 | -62.2559 | 59.935 | -62.0087 | -62.4893 | -62.4573 | 0.050354 | 59.5047 | -62.3108 | 59.8572 | -62.1643 | -62.3474 | -62.3703 | 0.027466 | -0.20599 | 0.18768 | 0.27466 | -0.17395 | -0.20599 | -0.20142 | -0.23346 | -0.027466 | -0.24261 | 0.10986 | 0.11902 | -0.086975 | -0.064087 | -0.059509 | -0.036621 | 0.24719 | 122.1909 | 0.14648 | 122.168 | 121.7972 | 121.8155 | 121.8246 | 121.788 | -122.0032 | -122.0581 | 122.2183 | 122.1405 | 62.2192 | 62.3337
350.3281 | 122.3099 | -62.2559 | 59.7794 | -0.0060272 | 0.0014163 | 0.061385 | 0.056471 | -0.0027728 | -0.0038473 | 0.00086953 | -0.0021057 | 0.0015166 | 0.071297 | 0.056296 | -0.0068871 | 0.016663 | -0.0065518 | 0.050354 | 59.5642 | -62.2467 | 59.967 | -61.9583 | -62.4344 | -62.4207 | 0.14648 | 59.5779 | -62.2696 | 59.8526 | -62.1185 | -62.2971 | -62.3703 | 0.009155 | -0.21515 | 0.18768 | 0.29755 | -0.16479 | -0.17853 | -0.17395 | -0.18768 | -0.013733 | -0.20142 | 0.073242 | 0.13733 | -0.11444 | -0.041199 | -0.10071 | -0.027466 | 0.28839 | 122.2137 | 0.15106 | 122.1222 | 121.8109 | 121.8475 | 121.8201 | 121.8338 | -122.0261 | -122.049 | 122.2229 | 122.1085 | 62.3062 | 62.4023
352.0781 | 122.3145 | -62.2833 | 59.7244 | -0.0060272 | 0.0037661 | 0.061598 | 0.061171 | -0.0023456 | -0.0047019 | -0.0038303 | -0.0051575 | 0.0021576 | 0.071083 | 0.064627 | -0.0075281 | 0.016235 | 0.0017794 | -0.13733 | 59.5596 | -62.2879 | 59.848 | -62.0773 | -62.5626 | -62.5488 | -0.018311 | 59.5688 | -62.3245 | 59.8389 | -62.2009 | -62.384 | -62.3795 | -0.004578 | -0.16479 | 0.1236 | 0.20599 | -0.2655 | -0.27924 | -0.26093 | -0.27466 | -0.041199 | -0.15564 | 0.11444 | 0.082397 | -0.096131 | -0.10071 | -0.054932 | -0.059509 | 0.21057 | 122.1359 | 0.1236 | 122.1634 | 121.8475 | 121.8933 | 121.843 | 121.8521 | -122.0123 | -122.0489 | 122.1313 | 122.1222 | 62.146 | 62.265
353.7656 | 122.2183 | -62.265 | 59.8297 | -0.013657 | -7.9104e-05 | 0.059462 | 0.057112 | -0.0036274 | -0.0089743 | -0.0029759 | -0.0051575 | 0.003012 | 0.073647 | 0.065055 | -0.0060327 | 0.015595 | -0.00527 | -0.004578 | 59.61 | -62.2833 | 59.8618 | -62.0636 | -62.5305 | -62.5259 | 0.032043 | 59.6283 | -62.3245 | 59.7748 | -62.2284 | -62.4161 | -62.4619 | -0.01831 | -0.21973 | 0.032043 | 0.20142 | -0.26093 | -0.2655 | -0.24262 | -0.24719 | -0.059509 | -0.20142 | -0.054932 | 0.036621 | -0.19684 | -0.15106 | -0.13733 | -0.091553 | 0.21973 | 122.1451 | 0.09613 | 122.0993 | 121.8933 | 121.9528 | 121.875 | 121.8933 | -122.113 | -122.1542 | 122.1268 | 122.0398 | 62.2604 | 62.2971
355.5156 | 122.3465 | -62.2421 | 59.7748 | -0.013657 | 0.0001345 | 0.060957 | 0.058821 | -0.001491 | -0.0036337 | -0.0027621 | -0.0051575 | -0.00019216 | 0.074074 | 0.058432 | -0.0075281 | 0.018158 | -0.0033474 | 0.022888 | 59.5596 | -62.2421 | 59.9579 | -61.9583 | -62.4344 | -62.4344 | 0.15106 | 59.5825 | -62.2925 | 59.8892 | -62.1094 | -62.2787 | -62.352 | 0 | -0.21515 | 0.18311 | 0.28381 | -0.19226 | -0.19226 | -0.19226 | -0.19226 | -0.050354 | -0.19226 | 0.11444 | 0.13275 | -0.10986 | -0.036622 | -0.05951 | 0.013732 | 0.28381 | 122.2 | 0.1831 | 122.1817 | 121.8018 | 121.875 | 121.8018 | 121.8246 | -122.0169 | -122.0673 | 122.2 | 122.1313 | 62.265 | 62.3932
357.2031 | 122.2504 | -62.2787 | 59.8434 | -0.0060272 | 0.0033389 | 0.059889 | 0.060316 | 0.0017132 | -0.0070517 | -0.00083947 | -0.0021057 | 0.0023712 | 0.072365 | 0.062064 | -0.0088097 | 0.016663 | -0.0001432 | 0.018311 | 59.6237 | -62.2833 | 59.8709 | -62.0773 | -62.4985 | -62.5076 | 0.045776 | 59.6283 | -62.2971 | 59.8068 | -62.2055 | -62.4069 | -62.4252 | -0.004577 | -0.21973 | 0.027466 | 0.20142 | -0.22888 | -0.21973 | -0.2243 | -0.21515 | -0.01831 | -0.21515 | -0.036621 | 0.073243 | -0.14648 | -0.12817 | -0.12817 | -0.10986 | 0.20599 | 122.1542 | 0.091553 | 122.1039 | 121.907 | 121.9254 | 121.9025 | 121.907 | -122.1268 | -122.1405 | 122.1497 | 122.0856 | 62.2971 | 62.3245
358.9375 | 122.2046 | -62.265 | 59.8297 | 0.0016023 | 0.0003483 | 0.062239 | 0.059035 | -0.001491 | -0.0059835 | -0.0023349 | -0.0021057 | 0.0025848 | 0.070869 | 0.067405 | -0.0064599 | 0.017944 | 0.000925 | 0 | 59.6329 | -62.2513 | 59.8572 | -62.0682 | -62.5214 | -62.5168 | 0.018311 | 59.6375 | -62.3108 | 59.7748 | -62.2238 | -62.3978 | -62.4527 | 0.013733 | -0.19684 | 0.027466 | 0.19684 | -0.25177 | -0.25635 | -0.2655 | -0.27008 | -0.045776 | -0.19226 | -0.054932 | 0.041199 | -0.18768 | -0.13275 | -0.14191 | -0.086975 | 0.18311 | 122.1085 | 0.086975 | 122.0856 | 121.8842 | 121.9482 | 121.8979 | 121.9025 | -122.081 | -122.1405 | 122.1222 | 122.0398 | 62.265 | 62.2833
360.6875 | 122.3007 | -62.2696 | 59.7565 | -0.013657 | 0.0009891 | 0.061812 | 0.057753 | 4.192e-06 | -0.0040609 | -0.0027621 | 0.0009461 | 0.00087584 | 0.068733 | 0.065909 | -0.0088097 | 0.015381 | -0.0003568 | -0.086975 | 59.5505 | -62.265 | 59.8984 | -62.0132 | -62.5031 | -62.4756 | 0.050354 | 59.5551 | -62.3337 | 59.8251 | -62.2192 | -62.3611 | -62.4252 | 0.004577 | -0.20599 | 0.14191 | 0.25635 | -0.20599 | -0.23346 | -0.21057 | -0.23804 | -0.064087 | -0.20142 | 0.068664 | 0.050354 | -0.15564 | -0.091553 | -0.091553 | -0.027466 | 0.25177 | 122.1634 | 0.11444 | 122.1588 | 121.8155 | 121.8887 | 121.8201 | 121.8246 | -122.0215 | -122.0901 | 122.168 | 122.0947 | 62.1826 | 62.3199
362.3594 | 122.2137 | -62.3199 | 59.7885 | -0.013657 | 0.0046207 | 0.061598 | 0.061598 | -0.0023456 | -0.0036337 | 1.4934e-05 | -0.0021057 | 0.0045074 | 0.07151 | 0.056723 | -0.0066735 | 0.016876 | -0.0027066 | -0.12817 | 59.6054 | -62.2833 | 59.8022 | -62.1552 | -62.6083 | -62.5763 | -0.07782 | 59.5871 | -62.3291 | 59.7565 | -62.2787 | -62.471 | -62.4756 | 0.036621 | -0.18311 | 0.013733 | 0.1648 | -0.25635 | -0.28839 | -0.29297 | -0.32501 | -0.009156 | -0.20142 | -0.032043 | 0.041198 | -0.15564 | -0.15106 | -0.14648 | -0.14191 | 0.12817 | 122.0856 | 0.050354 | 122.0856 | 121.8887 | 121.9162 | 121.9254 | 121.907 | -122.0718 | -122.1176 | 122.1222 | 122.0764 | 62.1918 | 62.2421
364.1094 | 122.2 | -62.3016 | 59.816 | -0.0060272 | 0.0029117 | 0.061812 | 0.061812 | 0.00064519 | -0.0053427 | -0.00019867 | 0.0009461 | 0.0027984 | 0.070656 | 0.067618 | -0.0079553 | 0.016235 | -0.0001432 | -0.054932 | 59.6146 | -62.2833 | 59.8389 | -62.114 | -62.5946 | -62.5809 | -0.068665 | 59.6283 | -62.3154 | 59.7656 | -62.2833 | -62.4664 | -62.4847 | 0.018311 | -0.20142 | 0.022888 | 0.18768 | -0.27924 | -0.29297 | -0.29755 | -0.31128 | -0.013733 | -0.18768 | -0.050354 | 0.018311 | -0.1831 | -0.16479 | -0.16937 | -0.15106 | 0.16937 | 122.1222 | 0.032044 | 122.081 | 121.8979 | 121.9437 | 121.9162 | 121.9299 | -122.0993 | -122.1313 | 122.1405 | 122.0673 | 62.2467 | 62.233
365.7969 | 122.2595 | -62.2879 | 59.8022 | 0.0016023 | 0.0022709 | 0.061598 | 0.061385 | -0.0012774 | -0.0044883 | -0.0021213 | -0.0051575 | 0.0032256 | 0.072578 | 0.068259 | -0.010092 | 0.016449 | -0.0020658 | 0.004578 | 59.6283 | -62.2604 | 59.903 | -62.027 | -62.4985 | -62.4985 | 0.07782 | 59.6146 | -62.2971 | 59.816 | -62.2009 | -62.384 | -62.3978 | 0.027466 | -0.17395 | 0.10071 | 0.26093 | -0.21057 | -0.21057 | -0.23804 | -0.23804 | -0.009155 | -0.18768 | 0.013733 | 0.086975 | -0.10986 | -0.09613 | -0.10071 | -0.086975 | 0.23346 | 122.1634 | 0.09613 | 122.113 | 121.8887 | 121.9116 | 121.9162 | 121.9025 | -122.0627 | -122.0993 | 122.1909 | 122.1039 | 62.2925 | 62.3657
367.5312 | 122.2046 | -62.2971 | 59.8068 | -0.0060272 | 0.0029117 | 0.061812 | 0.058607 | 0.0010724 | -0.0027793 | -0.0012669 | -0.0021057 | 0.0027984 | 0.072792 | 0.065055 | -0.0068871 | 0.018799 | -0.000784 | -0.10529 | 59.6008 | -62.3062 | 59.8251 | -62.1506 | -62.6129 | -62.6038 | -0.11902 | 59.6146 | -62.3337 | 59.7427 | -62.2925 | -62.4802 | -62.5076 | -0.009155 | -0.20599 | 0.01831 | 0.14648 | -0.3067 | -0.31586 | -0.29755 | -0.3067 | -0.036621 | -0.19226 | -0.064087 | 0.004578 | -0.21057 | -0.18311 | -0.17395 | -0.14649 | 0.15564 | 122.1313 | 0.041199 | 122.0764 | 121.907 | 121.9482 | 121.8979 | 121.9116 | -122.113 | -122.1405 | 122.1222 | 122.0398 | 62.1918 | 62.178
369.2656 | 122.2137 | -62.2787 | 59.816 | -0.013657 | 0.0024845 | 0.063521 | 0.06053 | -0.0025592 | -0.0059835 | -0.00062587 | -0.0051575 | 0.001944 | 0.071083 | 0.064627 | -0.0064599 | 0.018158 | -0.0005704 | -0.064087 | 59.6191 | -62.2833 | 59.8389 | -62.1185 | -62.59 | -62.5626 | -0.045776 | 59.5963 | -62.3245 | 59.7565 | -62.265 | -62.4847 | -62.4664 | -0.004577 | -0.19684 | 0.022888 | 0.16022 | -0.28381 | -0.31128 | -0.27924 | -0.3067 | -0.045776 | -0.21973 | -0.059509 | 0.013733 | -0.18768 | -0.20599 | -0.14191 | -0.16022 | 0.16479 | 122.1222 | 0.059509 | 122.081 | 121.9025 | 121.9208 | 121.8979 | 121.875 | -122.0993 | -122.1405 | 122.1176 | 122.0352 | 62.2147 | 62.233
371 | 122.3328 | -62.2879 | 59.7473 | -0.0060272 | 0.0020571 | 0.062453 | 0.058821 | 0.0023542 | -0.0051291 | -0.0021213 | -0.0051575 | 0.00023504 | 0.070015 | 0.053946 | -0.0071009 | 0.016022 | 0.0017794 | -0.059509 | 59.5551 | -62.2559 | 59.9304 | -62.0087 | -62.5031 | -62.471 | 0.059509 | 59.5184 | -62.2879 | 59.8572 | -62.1368 | -62.3199 | -62.3749 | 0.032044 | -0.19226 | 0.18311 | 0.27924 | -0.1831 | -0.21515 | -0.21515 | -0.24719 | 0 | -0.22888 | 0.10986 | 0.15106 | -0.086975 | -0.032043 | -0.086975 | -0.032043 | 0.24719 | 122.1863 | 0.15106 | 122.1451 | 121.8109 | 121.8063 | 121.843 | 121.8063 | -122.0032 | -122.0352 | 122.2183 | 122.1451 | 62.2284 | 62.3474
372.6875 | 122.2275 | -62.2879 | 59.8297 | -0.0060272 | 0.0009891 | 0.061598 | 0.060744 | -0.0027728 | -0.0047019 | -0.0012669 | -0.0021057 | 0.0015166 | 0.072578 | 0.067191 | -0.0068871 | 0.017944 | 0.002634 | -0.004578 | 59.6512 | -62.2559 | 59.8389 | -62.0865 | -62.5305 | -62.5351 | 0.013733 | 59.6695 | -62.3016 | 59.7748 | -62.2513 | -62.4161 | -62.4527 | 0.032044 | -0.17853 | 0.009155 | 0.20142 | -0.24719 | -0.24262 | -0.27924 | -0.27466 | -0.013733 | -0.16022 | -0.054932 | 0.036621 | -0.16479 | -0.12817 | -0.15106 | -0.11444 | 0.16937 | 122.0947 | 0.050354 | 122.0764 | 121.907 | 121.9711 | 121.9391 | 121.9574 | -122.0856 | -122.1313 | 122.1268 | 122.0627 | 62.2833 | 62.3016
374.4375 | 122.2412 | -62.2925 | 59.7748 | 0.0016023 | 0.0007755 | 0.062453 | 0.059248 | -0.0025592 | -0.0053427 | -0.0038303 | -0.0021057 | 0.00044864 | 0.073647 | 0.068473 | -0.0090235 | 0.017944 | 0.0030612 | -0.13733 | 59.6054 | -62.2742 | 59.8068 | -62.114 | -62.5992 | -62.5854 | -0.091553 | 59.5871 | -62.3428 | 59.761 | -62.2879 | -62.4756 | -62.4847 | 0.01831 | -0.16937 | 0.032044 | 0.17853 | -0.29297 | -0.3067 | -0.31128 | -0.32501 | -0.050354 | -0.18768 | -0.013733 | 0.004577 | -0.19226 | -0.18311 | -0.14191 | -0.13275 | 0.16022 | 122.081 | 0.054931 | 122.1039 | 121.8796 | 121.9299 | 121.8979 | 121.8796 | -122.0489 | -122.1176 | 122.0993 | 122.0535 | 62.1552 | 62.2009
376.1875 | 122.287 | -62.2971 | 59.7519 | -0.013657 | 0.0022709 | 0.062025 | 0.058607 | 0.00085879 | -0.0053427 | -0.0046847 | -0.0021057 | 2.1442e-05 | 0.07386 | 0.06185 | -0.0077417 | 0.016235 | 0.0004978 | -0.10071 | 59.5642 | -62.265 | 59.8709 | -62.0453 | -62.5076 | -62.4847 | -0.009155 | 59.5459 | -62.3108 | 59.7931 | -62.2101 | -62.3795 | -62.4115 | 0.032043 | -0.18768 | 0.11902 | 0.25177 | -0.18768 | -0.21057 | -0.21973 | -0.24261 | -0.013733 | -0.20599 | 0.041199 | 0.086975 | -0.11444 | -0.082398 | -0.10071 | -0.068665 | 0.21973 | 122.1359 | 0.10071 | 122.1039 | 121.8292 | 121.8567 | 121.8613 | 121.843 | -122.0169 | -122.0627 | 122.168 | 122.0901 | 62.1964 | 62.2879
377.8594 | 122.3053 | -62.2833 | 59.761 | -0.0060272 | 0.0001345 | 0.059889 | 0.057326 | 4.192e-06 | -0.0049155 | 0.00044213 | -0.0021057 | 0.00066224 | 0.071938 | 0.065268 | -0.0085961 | 0.015808 | -0.003561 | -0.091553 | 59.5505 | -62.2696 | 59.8846 | -62.0544 | -62.5214 | -62.5031 | 0.009155 | 59.5596 | -62.3108 | 59.8068 | -62.2101 | -62.384 | -62.4207 | 0.013733 | -0.21057 | 0.1236 | 0.22888 | -0.21973 | -0.23804 | -0.23346 | -0.25177 | -0.027466 | -0.20142 | 0.045777 | 0.073242 | -0.13733 | -0.10071 | -0.10986 | -0.073242 | 0.21515 | 122.1542 | 0.10071 | 122.1176 | 121.8201 | 121.8704 | 121.8338 | 121.843 | -122.0306 | -122.0718 | 122.168 | 122.0901 | 62.1918 | 62.2925
379.6094 | 122.2229 | -62.2833 | 59.8297 | -0.0060272 | -0.0002927 | 0.06053 | 0.059676 | -0.0032 | -0.0064109 | -0.0029759 | -0.0021057 | 0.003012 | 0.073219 | 0.060996 | -0.0085961 | 0.016876 | 0.0019932 | -0.009155 | 59.6375 | -62.2971 | 59.8434 | -62.1002 | -62.5442 | -62.5397 | 0.009155 | 59.642 | -62.3199 | 59.7885 | -62.2238 | -62.4069 | -62.4481 | -0.013733 | -0.19226 | 0.013733 | 0.1831 | -0.25635 | -0.26093 | -0.24262 | -0.24719 | -0.036621 | -0.18768 | -0.041199 | 0.059509 | -0.1648 | -0.1236 | -0.12817 | -0.086975 | 0.19684 | 122.1405 | 0.09613 | 122.1085 | 121.9345 | 121.962 | 121.9208 | 121.9254 | -122.1268 | -122.1497 | 122.1268 | 122.0718 | 62.2742 | 62.2925
381.3594 | 122.2961 | -62.2833 | 59.7473 | 0.0016023 | 0.0020571 | 0.060103 | 0.05818 | 0.001286 | -0.0038473 | -0.0038303 | 0.0009461 | 0.001303 | 0.070656 | 0.057364 | -0.0083825 | 0.016876 | 0.0032748 | -0.082397 | 59.5596 | -62.2513 | 59.9075 | -61.9949 | -62.5122 | -62.4756 | 0.045776 | 59.5367 | -62.3154 | 59.8206 | -62.1826 | -62.352 | -62.4115 | 0.032043 | -0.18768 | 0.16022 | 0.28839 | -0.19226 | -0.22888 | -0.2243 | -0.26092 | -0.032044 | -0.21057 | 0.073243 | 0.10071 | -0.12817 | -0.068665 | -0.09613 | -0.036621 | 0.25635 | 122.1588 | 0.13275 | 122.1359 | 121.8109 | 121.8521 | 121.843 | 121.8201 | -121.9986 | -122.0627 | 122.1909 | 122.1039 | 62.2009 | 62.3291
383.1094 | 122.2046 | -62.3062 | 59.8022 | -0.0060272 | 0.0054751 | 0.061385 | 0.059889 | 0.00043159 | -0.0057699 | -0.0016941 | -0.0082093 | 0.003653 | 0.074501 | 0.068473 | -0.0075281 | 0.016022 | -0.0027066 | -0.11444 | 59.6329 | -62.3016 | 59.7931 | -62.1735 | -62.6358 | -62.6083 | -0.09613 | 59.6146 | -62.3291 | 59.7519 | -62.3062 | -62.4802 | -62.4985 | 0.004577 | -0.16937 | -0.009155 | 0.13275 | -0.30212 | -0.32959 | -0.3067 | -0.33417 | -0.022889 | -0.18768 | -0.050354 | 0 | -0.19226 | -0.17395 | -0.16937 | -0.15106 | 0.12817 | 122.0947 | 0.022889 | 122.081 | 121.9345 | 121.9437 | 121.9391 | 121.9208 | -122.1039 | -122.1313 | 122.0993 | 122.0581 | 62.1918 | 62.2101
384.8125 | 122.3282 | -62.2604 | 59.7748 | -0.0060272 | -0.0015743 | 0.060316 | 0.057753 | 0.00043159 | -0.0049155 | -0.0021213 | -0.0051575 | 0.0015166 | 0.068947 | 0.063132 | -0.0085961 | 0.016876 | -0.0016384 | -0.050354 | 59.5596 | -62.2833 | 59.8709 | -62.0316 | -62.4893 | -62.4802 | 0.045776 | 59.5734 | -62.2925 | 59.848 | -62.1506 | -62.3245 | -62.3703 | -0.022888 | -0.21515 | 0.096131 | 0.22888 | -0.21973 | -0.22888 | -0.19684 | -0.20599 | -0.032043 | -0.20142 | 0.073242 | 0.10986 | -0.10986 | -0.064087 | -0.07782 | -0.032044 | 0.25177 | 122.1542 | 0.14191 | 122.1405 | 121.843 | 121.8658 | 121.8201 | 121.8338 | -122.0581 | -122.0673 | 122.1313 | 122.1085 | 62.2101 | 62.3062
386.5625 | 122.2916 | -62.2742 | 59.7656 | -0.0060272 | -7.9104e-05 | 0.06053 | 0.058394 | 0.00085879 | -0.0042745 | -0.0029759 | -0.0021057 | -0.00061956 | 0.07151 | 0.065909 | -0.010092 | 0.016235 | -0.0027066 | -0.068665 | 59.5551 | -62.2421 | 59.8984 | -62.0316 | -62.5305 | -62.4664 | 0.050354 | 59.5688 | -62.3108 | 59.8343 | -62.1918 | -62.3795 | -62.4161 | 0.032044 | -0.21057 | 0.13275 | 0.24262 | -0.19226 | -0.25635 | -0.22431 | -0.28839 | -0.036621 | -0.19684 | 0.068665 | 0.082398 | -0.14191 | -0.10529 | -0.10529 | -0.068665 | 0.21057 | 122.1405 | 0.11902 | 122.1451 | 121.7972 | 121.8796 | 121.8292 | 121.843 | -122.0078 | -122.0764 | 122.1725 | 122.1085 | 62.2055 | 62.3245
388.3125 | 122.3969 | -62.2787 | 59.761 | -0.013657 | 0.0016299 | 0.062453 | 0.056685 | -0.0023456 | -0.0053427 | -0.00019867 | -0.0051575 | 0.0023712 | 0.072365 | 0.065268 | -0.010519 | 0.014954 | -0.0039884 | -0.068665 | 59.5367 | -62.2604 | 59.9304 | -61.9949 | -62.4985 | -62.471 | 0.059509 | 59.5367 | -62.3245 | 59.8297 | -62.1872 | -62.3703 | -62.3978 | 0.018311 | -0.2243 | 0.16937 | 0.28381 | -0.19226 | -0.21973 | -0.21057 | -0.23804 | -0.045776 | -0.2243 | 0.068665 | 0.091553 | -0.11902 | -0.091552 | -0.073242 | -0.045776 | 0.2655 | 122.1909 | 0.13733 | 122.1542 | 121.7972 | 121.8613 | 121.8155 | 121.8155 | -122.0215 | -122.0856 | 122.2092 | 122.1085 | 62.2101 | 62.3383
390.0625 | 122.2229 | -62.2787 | 59.816 | -0.013657 | 0.0052615 | 0.059676 | 0.062453 | -0.0023456 | -0.0042745 | -0.0031895 | -0.0021057 | 0.0040802 | 0.070656 | 0.069327 | -0.0081689 | 0.015595 | -0.002493 | -0.045776 | 59.6054 | -62.2696 | 59.8709 | -62.0682 | -62.5671 | -62.5534 | 0.013733 | 59.6329 | -62.3291 | 59.7748 | -62.265 | -62.4619 | -62.4802 | 0.009156 | -0.21057 | 0.054932 | 0.21057 | -0.27466 | -0.28839 | -0.28381 | -0.29755 | -0.050354 | -0.1831 | -0.041199 | 0.013733 | -0.20142 | -0.1831 | -0.15106 | -0.13275 | 0.20142 | 122.1405 | 0.064087 | 122.1039 | 121.875 | 121.962 | 121.8842 | 121.9116 | -122.0856 | -122.1451 | 122.1497 | 122.0535 | 62.233 | 62.2925
391.7344 | 122.3053 | -62.2787 | 59.7656 | 0.0016023 | 0.0012027 | 0.060316 | 0.060957 | -0.002132 | -0.0049155 | -0.0053257 | -0.0021057 | 0.0015166 | 0.07151 | 0.068045 | -0.0071009 | 0.016876 | 7.04e-05 | -0.082397 | 59.5596 | -62.2742 | 59.8892 | -62.0361 | -62.5214 | -62.4939 | -0.013733 | 59.5642 | -62.3154 | 59.8068 | -62.2055 | -62.3932 | -62.4252 | 0.004578 | -0.20599 | 0.1236 | 0.24262 | -0.21515 | -0.24261 | -0.21973 | -0.24719 | -0.036621 | -0.20142 | 0.041199 | 0.073243 | -0.14648 | -0.11444 | -0.10986 | -0.077819 | 0.23804 | 122.1634 | 0.10986 | 122.1222 | 121.8338 | 121.8796 | 121.8384 | 121.843 | -122.0398 | -122.081 | 122.168 | 122.0856 | 62.1964 | 62.265
393.4688 | 122.3282 | -62.2742 | 59.7656 | 0.0016023 | 0.0014163 | 0.060744 | 0.061171 | 0.002995 | -0.0038473 | -0.0010531 | -0.0021057 | 0.0032256 | 0.069801 | 0.063987 | -0.010092 | 0.016022 | -0.0018522 | -0.1236 | 59.5825 | -62.2787 | 59.8618 | -62.059 | -62.5351 | -62.5076 | 0.009155 | 59.5551 | -62.3245 | 59.8434 | -62.1735 | -62.3657 | -62.384 | -0.004578 | -0.1831 | 0.09613 | 0.21515 | -0.23346 | -0.26093 | -0.22888 | -0.25635 | -0.050354 | -0.21057 | 0.07782 | 0.10071 | -0.10986 | -0.091553 | -0.059509 | -0.041199 | 0.21973 | 122.1405 | 0.15106 | 122.168 | 121.8613 | 121.8796 | 121.8567 | 121.8292 | -122.0444 | -122.0901 | 122.1359 | 122.1176 | 62.1506 | 62.2833
395.1562 | 122.2687 | -62.2742 | 59.7977 | -0.0060272 | 0.0014163 | 0.060957 | 0.061385 | -0.0029864 | -0.0070517 | -0.0014805 | -0.0051575 | 0.0032256 | 0.070869 | 0.073172 | -0.010092 | 0.016876 | -0.000784 | 0.022888 | 59.6283 | -62.2787 | 59.8984 | -62.0544 | -62.5168 | -62.5214 | 0.073242 | 59.6146 | -62.3016 | 59.816 | -62.1872 | -62.4069 | -62.4161 | -0.004578 | -0.16937 | 0.10071 | 0.21973 | -0.24719 | -0.24262 | -0.24261 | -0.23804 | -0.027466 | -0.18311 | 0.018311 | 0.086975 | -0.14191 | -0.13275 | -0.11444 | -0.10528 | 0.22431 | 122.1771 | 0.11444 | 122.1176 | 121.907 | 121.9162 | 121.9025 | 121.8887 | -122.0764 | -122.0993 | 122.1725 | 122.0901 | 62.2971 | 62.3474
396.8906 | 122.2092 | -62.2833 | 59.8251 | -0.013657 | -7.9104e-05 | 0.059676 | 0.060316 | -0.0046954 | -0.0053427 | 1.4934e-05 | 0.0039977 | 0.0015166 | 0.072151 | 0.065268 | -0.0079553 | 0.01709 | 0.0007114 | -0.009155 | 59.6191 | -62.2604 | 59.848 | -62.0865 | -62.5305 | -62.5168 | 0.018311 | 59.6649 | -62.3154 | 59.7748 | -62.2284 | -62.4207 | -62.4481 | 0.022888 | -0.20599 | 0.022888 | 0.19684 | -0.23346 | -0.24719 | -0.25635 | -0.27008 | -0.032044 | -0.16022 | -0.050354 | 0.054931 | -0.1648 | -0.13733 | -0.13275 | -0.10529 | 0.17395 | 122.1085 | 0.086975 | 122.0901 | 121.8796 | 121.9803 | 121.9025 | 121.9482 | -122.0856 | -122.1405 | 122.1313 | 122.0581 | 62.2742 | 62.3016
398.625 | 122.2275 | -62.2833 | 59.8343 | 0.0016023 | 0.0001345 | 0.058394 | 0.059462 | -0.0012774 | -0.0059835 | -0.0023349 | -0.0051575 | 0.0017304 | 0.072578 | 0.063773 | -0.0073145 | 0.015595 | -0.0020658 | 0 | 59.6283 | -62.265 | 59.8434 | -62.0773 | -62.5259 | -62.5351 | 0.013733 | 59.6558 | -62.3245 | 59.7656 | -62.2467 | -62.4252 | -62.4802 | 0.01831 | -0.20599 | 0.009155 | 0.20599 | -0.25177 | -0.24262 | -0.27008 | -0.26093 | -0.041199 | -0.17853 | -0.068665 | 0.036621 | -0.19684 | -0.14191 | -0.15564 | -0.10071 | 0.18768 | 122.1085 | 0.07782 | 122.0901 | 121.8933 | 121.9803 | 121.9116 | 121.9391 | -122.0993 | -122.1588 | 122.1268 | 122.0489 | 62.2833 | 62.2971
400.3281 | 122.3419 | -62.265 | 59.7839 | -0.0060272 | -0.0024289 | 0.060103 | 0.05583 | -0.00063661 | -0.0047019 | -0.00041227 | -0.0021057 | -0.00040596 | 0.07386 | 0.060782 | -0.0058191 | 0.017731 | 0.0011386 | -0.036621 | 59.5779 | -62.2559 | 59.9167 | -62.0041 | -62.4619 | -62.4527 | 0.07782 | 59.5734 | -62.3154 | 59.8663 | -62.1323 | -62.2925 | -62.3657 | 0.009156 | -0.20599 | 0.13275 | 0.26093 | -0.18768 | -0.19684 | -0.19684 | -0.20599 | -0.050354 | -0.21057 | 0.082397 | 0.13275 | -0.10071 | -0.027465 | -0.050354 | 0.022889 | 0.25177 | 122.1725 | 0.18311 | 122.1817 | 121.8338 | 121.8887 | 121.843 | 121.8384 | -122.0398 | -122.0993 | 122.1817 | 122.1313 | 62.2284 | 62.3428
402.0625 | 122.2961 | -62.2787 | 59.7748 | -0.0060272 | 0.0009891 | 0.062666 | 0.05818 | 0.0019268 | -0.0049155 | -0.0034031 | -0.0051575 | -0.00061956 | 0.070656 | 0.065482 | -0.0081689 | 0.015381 | -0.0031338 | -0.07782 | 59.5459 | -62.2696 | 59.8618 | -62.0499 | -62.5076 | -62.5031 | 0 | 59.5779 | -62.3199 | 59.8114 | -62.2009 | -62.3795 | -62.4069 | 0.009156 | -0.22888 | 0.086975 | 0.22888 | -0.2243 | -0.22888 | -0.23346 | -0.23804 | -0.041198 | -0.19684 | 0.036621 | 0.07782 | -0.12817 | -0.10071 | -0.086975 | -0.05951 | 0.21973 | 122.1313 | 0.11902 | 122.1313 | 121.8155 | 121.8979 | 121.8246 | 121.8567 | -122.0444 | -122.0947 | 122.1405 | 122.0901 | 62.2009 | 62.2787
403.8125 | 122.2733 | -62.3016 | 59.7656 | -0.013657 | 0.0020571 | 0.061171 | 0.060103 | -0.00042301 | -0.0025655 | -0.0036167 | -0.0021057 | 0.0023712 | 0.074715 | 0.067191 | -0.0090235 | 0.016876 | -0.0020658 | -0.13275 | 59.6237 | -62.265 | 59.816 | -62.1094 | -62.6038 | -62.5809 | -0.064087 | 59.5825 | -62.3154 | 59.7794 | -62.2696 | -62.4481 | -62.4435 | 0.036621 | -0.14191 | 0.050354 | 0.19226 | -0.27924 | -0.30212 | -0.31586 | -0.33875 | -0.013733 | -0.1831 | 0.013733 | 0.032044 | -0.14191 | -0.14648 | -0.12817 | -0.13275 | 0.15564 | 122.081 | 0.045777 | 122.0947 | 121.8887 | 121.8979 | 121.9254 | 121.8842 | -122.0306 | -122.081 | 122.1176 | 122.081 | 62.1689 | 62.2375
405.5 | 122.2549 | -62.2879 | 59.7885 | -0.0060272 | 0.0031253 | 0.061812 | 0.063094 | 0.0010724 | -0.0061971 | -0.00083947 | -0.0051575 | 0.001303 | 0.073433 | 0.066977 | -0.0083825 | 0.017303 | -0.002493 | -0.013733 | 59.6008 | -62.2513 | 59.9121 | -62.0178 | -62.4985 | -62.5031 | 0.068665 | 59.61 | -62.2925 | 59.816 | -62.1826 | -62.3703 | -62.4207 | 0.036621 | -0.18768 | 0.1236 | 0.27008 | -0.21515 | -0.21057 | -0.25177 | -0.24719 | -0.004577 | -0.17853 | 0.027466 | 0.10529 | -0.13275 | -0.082397 | -0.12817 | -0.07782 | 0.23346 | 122.1634 | 0.10986 | 122.1085 | 121.8521 | 121.9025 | 121.8887 | 121.8979 | -122.0398 | -122.081 | 122.2 | 122.1039 | 62.2742 | 62.3566
407.2344 | 122.2916 | -62.2833 | 59.7565 | -0.013657 | 0.0033389 | 0.061171 | 0.060316 | -0.001491 | -0.0047019 | -0.0029759 | -0.0021057 | -0.00019216 | 0.069801 | 0.066336 | -0.0083825 | 0.016663 | -0.003561 | -0.082397 | 59.5367 | -62.2604 | 59.8618 | -62.059 | -62.5122 | -62.4893 | -0.009155 | 59.5734 | -62.3291 | 59.816 | -62.2101 | -62.384 | -62.4161 | 0.022888 | -0.21973 | 0.10529 | 0.2243 | -0.20599 | -0.22888 | -0.22888 | -0.25177 | -0.045777 | -0.18311 | 0.059509 | 0.073242 | -0.13275 | -0.10071 | -0.086975 | -0.054931 | 0.20142 | 122.1222 | 0.11902 | 122.1451 | 121.7972 | 121.9025 | 121.8201 | 121.8567 | -122.0169 | -122.0856 | 122.1451 | 122.0993 | 62.2009 | 62.2742
408.9062 | 122.2961 | -62.2971 | 59.7473 | -0.0060272 | 0.0026981 | 0.062453 | 0.059676 | -0.0010638 | -0.0047019 | 0.0015103 | -0.0021057 | -0.00019216 | 0.072151 | 0.066123 | -0.0090235 | 0.016663 | -0.0005704 | -0.068665 | 59.5367 | -62.2513 | 59.9121 | -62.0132 | -62.5076 | -62.4802 | 0.073242 | 59.5551 | -62.3154 | 59.8251 | -62.2009 | -62.352 | -62.4023 | 0.045776 | -0.21057 | 0.16479 | 0.28381 | -0.18311 | -0.21057 | -0.22888 | -0.25635 | -0.018311 | -0.19226 | 0.07782 | 0.09613 | -0.10529 | -0.054932 | -0.086975 | -0.036621 | 0.23804 | 122.1634 | 0.11444 | 122.1405 | 121.788 | 121.8704 | 121.8338 | 121.8521 | -121.9986 | -122.0627 | 122.2092 | 122.1222 | 62.2284 | 62.3703
410.6562 | 122.3373 | -62.2879 | 59.7153 | -0.0060272 | 0.0031253 | 0.06053 | 0.057326 | 0.0010724 | -0.0034201 | -0.0021213 | 0.0009461 | 0.00087584 | 0.06852 | 0.059501 | -0.012228 | 0.017944 | -0.0048428 | -0.059509 | 59.523 | -62.2742 | 59.9304 | -61.9949 | -62.5076 | -62.4481 | 0.059509 | 59.5322 | -62.3108 | 59.8618 | -62.1643 | -62.3383 | -62.3886 | 0.013733 | -0.19226 | 0.21515 | 0.29297 | -0.16022 | -0.21973 | -0.17395 | -0.23346 | -0.022888 | -0.18311 | 0.14648 | 0.1236 | -0.10071 | -0.050354 | -0.07782 | -0.027466 | 0.27924 | 122.2046 | 0.14648 | 122.1725 | 121.7972 | 121.843 | 121.8109 | 121.8201 | -121.9894 | -122.0261 | 122.2183 | 122.1497 | 62.2284 | 62.3474
412.3438 | 122.2137 | -62.3108 | 59.7885 | 0.0016023 | 0.0033389 | 0.062239 | 0.061598 | -0.0025592 | -0.0064109 | -0.00019867 | -0.0051575 | 0.003653 | 0.072151 | 0.065696 | -0.0079553 | 0.018585 | -0.0037748 | -0.11444 | 59.6283 | -62.2833 | 59.8068 | -62.1552 | -62.6312 | -62.6175 | -0.073242 | 59.6054 | -62.3154 | 59.7473 | -62.2971 | -62.4893 | -62.4847 | 0.027466 | -0.16022 | 0.018311 | 0.15564 | -0.3067 | -0.32043 | -0.33417 | -0.3479 | -0.004578 | -0.18311 | -0.041199 | 0.013733 | -0.17395 | -0.17853 | -0.16937 | -0.17395 | 0.12817 | 122.0901 | 0.018311 | 122.0627 | 121.9116 | 121.9208 | 121.9391 | 121.9162 | -122.0718 | -122.1039 | 122.1176 | 122.0581 | 62.1964 | 62.2375
414.0938 | 122.2595 | -62.2742 | 59.7977 | -0.013657 | 0.0020571 | 0.06288 | 0.060103 | -0.0027728 | -0.0038473 | -0.0034031 | 0.0039977 | 0.003653 | 0.071297 | 0.069541 | -0.0096643 | 0.017517 | -0.0003568 | 0.018311 | 59.6237 | -62.2925 | 59.8938 | -62.027 | -62.5122 | -62.4939 | 0.082397 | 59.6329 | -62.3016 | 59.8114 | -62.1918 | -62.3932 | -62.4115 | -0.01831 | -0.17395 | 0.096131 | 0.24719 | -0.21973 | -0.23804 | -0.20142 | -0.21973 | -0.027466 | -0.16479 | 0.013733 | 0.082398 | -0.13733 | -0.11902 | -0.10986 | -0.091552 | 0.2655 | 122.1863 | 0.10986 | 122.113 | 121.9162 | 121.9345 | 121.8979 | 121.907 | -122.0901 | -122.0993 | 122.168 | 122.0856 | 62.2925 | 62.3566
415.7969 | 122.319 | -62.2559 | 59.7931 | -0.013657 | 0.0018435 | 0.059248 | 0.057539 | -0.0010638 | -0.0040609 | -0.0012669 | -0.0051575 | -0.00061956 | 0.071938 | 0.063773 | -0.0068871 | 0.013886 | -0.0014248 | 0.068665 | 59.5642 | -62.265 | 59.967 | -61.9492 | -62.4161 | -62.4023 | 0.14191 | 59.5825 | -62.3108 | 59.8755 | -62.1094 | -62.2879 | -62.3474 | -0.009156 | -0.22888 | 0.17395 | 0.3067 | -0.14648 | -0.16022 | -0.13733 | -0.15106 | -0.054932 | -0.21057 | 0.082397 | 0.14648 | -0.091553 | -0.032044 | -0.036621 | 0.022888 | 0.31586 | 122.2321 | 0.20142 | 122.1863 | 121.8292 | 121.8933 | 121.8201 | 121.8384 | -122.0581 | -122.1039 | 122.2229 | 122.1313 | 62.3245 | 62.3978
417.4688 | 122.2229 | -62.3108 | 59.7931 | -0.0060272 | 0.0033389 | 0.061812 | 0.061598 | -0.00085021 | -0.0034201 | -0.0029759 | 0.0009461 | 0.0027984 | 0.071724 | 0.061637 | -0.0075281 | 0.017944 | -0.0009976 | -0.013733 | 59.5917 | -62.2879 | 59.8801 | -62.059 | -62.5397 | -62.5214 | 0.027466 | 59.6375 | -62.3245 | 59.8068 | -62.2421 | -62.4161 | -62.4481 | 0.022888 | -0.20142 | 0.086975 | 0.25177 | -0.21057 | -0.22888 | -0.23346 | -0.25177 | -0.013733 | -0.15564 | 0.013733 | 0.068665 | -0.13733 | -0.10529 | -0.1236 | -0.091553 | 0.22888 | 122.168 | 0.082398 | 122.1313 | 121.8796 | 121.962 | 121.9025 | 121.9482 | -122.081 | -122.1176 | 122.1909 | 122.1176 | 62.2971 | 62.3383
419.2031 | 122.2778 | -62.3062 | 59.7748 | -0.0060272 | -0.0007199 | 0.06053 | 0.061385 | -0.00020941 | -0.0051291 | -0.0021213 | -0.0082093 | 0.003653 | 0.071083 | 0.058432 | -0.0085961 | 0.016449 | -0.0014248 | -0.15106 | 59.5734 | -62.3016 | 59.816 | -62.1185 | -62.5946 | -62.558 | -0.068665 | 59.5779 | -62.3337 | 59.7702 | -62.233 | -62.439 | -62.4481 | 0.004577 | -0.20142 | 0.041199 | 0.18768 | -0.25177 | -0.28839 | -0.25635 | -0.29297 | -0.027466 | -0.19684 | -0.004577 | 0.073242 | -0.14191 | -0.13275 | -0.11444 | -0.10529 | 0.18311 | 122.1176 | 0.10071 | 122.1039 | 121.875 | 121.9116 | 121.8796 | 121.8842 | -122.0764 | -122.1085 | 122.1222 | 122.0764 | 62.1552 | 62.2375
420.8906 | 122.2504 | -62.2833 | 59.7931 | -0.013657 | 0.0035525 | 0.061385 | 0.058607 | -0.0017048 | -0.0032065 | -0.0019077 | -0.0051575 | 0.0027984 | 0.071724 | 0.066336 | -0.0083825 | 0.017731 | 0.002634 | 0.009155 | 59.6237 | -62.265 | 59.903 | -62.027 | -62.5031 | -62.4985 | 0.064087 | 59.6054 | -62.3016 | 59.8114 | -62.1918 | -62.4069 | -62.4252 | 0.01831 | -0.16937 | 0.10986 | 0.25635 | -0.21515 | -0.21973 | -0.23346 | -0.23804 | -0.018311 | -0.18768 | 0.01831 | 0.091553 | -0.14191 | -0.1236 | -0.1236 | -0.10528 | 0.23804 | 122.168 | 0.10986 | 122.113 | 121.8887 | 121.907 | 121.907 | 121.8887 | -122.0581 | -122.0947 | 122.1863 | 122.0947 | 62.2925 | 62.3474
422.6562 | 122.2321 | -62.3016 | 59.8572 | -0.0060272 | 0.0014163 | 0.059035 | 0.060316 | -0.0023456 | -0.0066245 | -0.0023349 | -0.0051575 | 0.0010894 | 0.073433 | 0.065055 | -0.0071009 | 0.017517 | 0.0024204 | 0.013733 | 59.6558 | -62.2696 | 59.8251 | -62.0911 | -62.5397 | -62.5214 | 0.013733 | 59.6558 | -62.3199 | 59.7794 | -62.2192 | -62.3978 | -62.4298 | 0.032044 | -0.20142 | -0.032044 | 0.21057 | -0.21973 | -0.23804 | -0.25177 | -0.27008 | -0.01831 | -0.20142 | -0.07782 | 0.082398 | -0.12817 | -0.09613 | -0.10986 | -0.07782 | 0.17853 | 122.0947 | 0.10071 | 122.0993 | 121.9254 | 121.9757 | 121.9574 | 121.9574 | -122.1268 | -122.1771 | 122.1268 | 122.081 | 62.3154 | 62.3154
424.3438 | 122.2961 | -62.2833 | 59.7382 | 0.0016023 | 0.0012027 | 0.061812 | 0.056258 | -0.0019184 | -0.0040609 | -0.00083947 | -0.0021057 | 0.001303 | 0.071083 | 0.058432 | -0.0073145 | 0.016663 | -0.0046292 | -0.082397 | 59.5367 | -62.2513 | 59.9121 | -61.9904 | -62.5122 | -62.4664 | 0.045776 | 59.5413 | -62.3245 | 59.816 | -62.1918 | -62.3611 | -62.3886 | 0.032043 | -0.20142 | 0.17395 | 0.29297 | -0.18311 | -0.22888 | -0.21515 | -0.26092 | -0.041199 | -0.19684 | 0.07782 | 0.091553 | -0.10529 | -0.07782 | -0.064087 | -0.036621 | 0.26093 | 122.1634 | 0.13275 | 122.1405 | 121.788 | 121.8658 | 121.8201 | 121.8246 | -121.9894 | -122.0627 | 122.1954 | 122.0993 | 62.2009 | 62.3291
426.0781 | 122.2366 | -62.2742 | 59.8343 | -0.0060272 | 0.0003483 | 0.060957 | 0.059035 | -0.002132 | -0.0040609 | -0.0012669 | -0.0021057 | 0.0034392 | 0.072578 | 0.066764 | -0.0094507 | 0.017731 | -0.0022794 | -0.009155 | 59.6466 | -62.3108 | 59.8526 | -62.1048 | -62.5259 | -62.5168 | 0.009155 | 59.6329 | -62.3245 | 59.7794 | -62.2375 | -62.4023 | -62.4298 | -0.036621 | -0.18768 | 0.01831 | 0.16937 | -0.24262 | -0.25177 | -0.20599 | -0.21515 | -0.050354 | -0.20142 | -0.054932 | 0.036621 | -0.15564 | -0.12817 | -0.10529 | -0.07782 | 0.20599 | 122.1634 | 0.086975 | 122.1039 | 121.9574 | 121.9574 | 121.9208 | 121.907 | -122.1451 | -122.1588 | 122.1268 | 122.0535 | 62.265 | 62.2833
427.8281 | 122.2458 | -62.2925 | 59.8343 | 0.0092313 | 0.0020571 | 0.060103 | 0.059248 | -0.0017048 | -0.0057699 | -0.0016941 | 0.0009461 | 0.001303 | 0.072578 | 0.062705 | -0.0098779 | 0.018158 | -0.0029202 | 0.004578 | 59.642 | -62.2833 | 59.8618 | -62.0819 | -62.5214 | -62.5214 | 0.027466 | 59.6603 | -62.2925 | 59.8114 | -62.1918 | -62.4023 | -62.4252 | 0.009155 | -0.19226 | 0.027465 | 0.21057 | -0.22888 | -0.22888 | -0.23804 | -0.23804 | 0 | -0.17395 | -0.022889 | 0.10071 | -0.13275 | -0.10986 | -0.13275 | -0.10986 | 0.20142 | 122.1451 | 0.10071 | 122.1039 | 121.9254 | 121.9528 | 121.9345 | 121.9528 | -122.1176 | -122.1268 | 122.1542 | 122.1039 | 62.2971 | 62.3199
429.5156 | 122.3373 | -62.2696 | 59.7153 | -0.0060272 | 0.0029117 | 0.061598 | 0.061385 | -0.0010638 | -0.0021383 | 0.0015103 | -0.0021057 | 0.0010894 | 0.07386 | 0.05416 | -0.0090235 | 0.016449 | -0.0018522 | -0.07782 | 59.5367 | -62.2787 | 59.9121 | -61.9995 | -62.4939 | -62.4756 | 0.045776 | 59.5322 | -62.3245 | 59.8755 | -62.1597 | -62.3245 | -62.3657 | -0.009156 | -0.17853 | 0.19684 | 0.27008 | -0.20599 | -0.2243 | -0.19684 | -0.21515 | -0.054932 | -0.18311 | 0.16022 | 0.10986 | -0.096131 | -0.054932 | -0.041199 | 0 | 0.27924 | 122.1909 | 0.16479 | 122.2 | 121.8155 | 121.8567 | 121.8063 | 121.8018 | -121.994 | -122.0398 | 122.1817 | 122.1451 | 62.1918 | 62.3154
431.2812 | 122.2961 | -62.3062 | 59.7336 | -0.013657 | 0.0016299 | 0.061812 | 0.059889 | -0.0010638 | -0.0019247 | -0.0046847 | 0.0009461 | 0.0021576 | 0.07151 | 0.068259 | -0.010519 | 0.017517 | -0.0005704 | -0.14191 | 59.5917 | -62.3062 | 59.8343 | -62.0956 | -62.5854 | -62.5488 | -0.022888 | 59.5551 | -62.3108 | 59.8068 | -62.2055 | -62.4115 | -62.3932 | 0 | -0.14191 | 0.10071 | 0.21057 | -0.24262 | -0.27924 | -0.24262 | -0.27924 | -0.004578 | -0.17853 | 0.073242 | 0.10071 | -0.086975 | -0.10529 | -0.082397 | -0.10071 | 0.21057 | 122.1405 | 0.10529 | 122.1176 | 121.8979 | 121.8658 | 121.8979 | 121.8613 | -122.0398 | -122.0444 | 122.1405 | 122.113 | 62.1643 | 62.2833
433.0312 | 122.2733 | -62.2787 | 59.816 | -0.0060272 | 0.0039799 | 0.060316 | 0.059889 | 0.0040632 | -0.0044883 | -0.00019867 | -0.0021057 | 0.001303 | 0.071724 | 0.073386 | -0.0094507 | 0.017517 | -0.0014248 | 0.004578 | 59.6054 | -62.2696 | 59.8938 | -62.0407 | -62.5076 | -62.5076 | 0.068665 | 59.642 | -62.3154 | 59.8251 | -62.1689 | -62.3886 | -62.4069 | 0.009156 | -0.21057 | 0.07782 | 0.23804 | -0.22888 | -0.22888 | -0.23804 | -0.23804 | -0.036621 | -0.17395 | 0.009155 | 0.10986 | -0.12817 | -0.10986 | -0.091552 | -0.073242 | 0.22888 | 122.1634 | 0.14648 | 122.1405 | 121.875 | 121.9574 | 121.8842 | 121.9208 | -122.0856 | -122.1313 | 122.1725 | 122.1039 | 62.2833 | 62.3474
434.7188 | 122.287 | -62.2742 | 59.8068 | -0.0060272 | -0.0009335 | 0.060316 | 0.056685 | -0.0036274 | -0.0061971 | -0.0021213 | -0.0021057 | 0.0010894 | 0.070656 | 0.058219 | -0.0090235 | 0.016449 | 0.0007114 | 0.064087 | 59.5596 | -62.2559 | 59.9533 | -61.972 | -62.4344 | -62.4207 | 0.14648 | 59.5871 | -62.2879 | 59.8297 | -62.1414 | -62.3199 | -62.3703 | 0.018311 | -0.24719 | 0.14648 | 0.30212 | -0.14648 | -0.16022 | -0.16479 | -0.17853 | -0.013733 | -0.21973 | 0.022888 | 0.13275 | -0.09613 | -0.045776 | -0.082397 | -0.032043 | 0.28381 | 122.2092 | 0.14648 | 122.1176 | 121.8155 | 121.875 | 121.8338 | 121.8613 | -122.0627 | -122.0947 | 122.2275 | 122.1039 | 62.3383 | 62.4207
436.4531 | 122.2641 | -62.2696 | 59.8297 | -0.021286 | -0.0009335 | 0.06053 | 0.062453 | -0.0042682 | -0.0076925 | -0.0014805 | -0.0021057 | 0.0034392 | 0.072151 | 0.060782 | -0.0068871 | 0.015381 | -0.0009976 | -0.009155 | 59.6329 | -62.2833 | 59.8709 | -62.0865 | -62.5122 | -62.5305 | 0.013733 | 59.642 | -62.2879 | 59.8068 | -62.2009 | -62.4069 | -62.4207 | -0.013733 | -0.19684 | 0.041199 | 0.18311 | -0.26093 | -0.24261 | -0.24719 | -0.22888 | -0.018311 | -0.18768 | -0.022888 | 0.068664 | -0.15106 | -0.13733 | -0.13275 | -0.11902 | 0.19684 | 122.1542 | 0.086975 | 122.0947 | 121.9162 | 121.9299 | 121.9025 | 121.9116 | -122.113 | -122.1176 | 122.1405 | 122.0764 | 62.2604 | 62.2833
438.125 | 122.287 | -62.2833 | 59.7748 | -0.0060272 | 0.0018435 | 0.062025 | 0.058607 | -0.002132 | -0.0057699 | -0.0014805 | -0.0051575 | -0.00040596 | 0.070869 | 0.060782 | -0.0090235 | 0.015808 | 7.04e-05 | -0.09613 | 59.5505 | -62.2604 | 59.8801 | -62.0178 | -62.5168 | -62.4802 | 0.027466 | 59.5642 | -62.2971 | 59.8251 | -62.2055 | -62.3657 | -62.4161 | 0.022888 | -0.2243 | 0.10529 | 0.2655 | -0.19684 | -0.23346 | -0.21973 | -0.25635 | -0.013733 | -0.21057 | 0.050354 | 0.07782 | -0.13275 | -0.082398 | -0.11902 | -0.068665 | 0.24262 | 122.1405 | 0.091553 | 122.1222 | 121.8109 | 121.8613 | 121.8338 | 121.8475 | -122.0352 | -122.0718 | 122.1634 | 122.1085 | 62.1872 | 62.3108
439.875 | 122.2321 | -62.2787 | 59.7931 | -0.0060272 | 0.0005619 | 0.060957 | 0.061812 | 0.0010724 | -0.0049155 | -0.0046847 | -0.0051575 | 0.0032256 | 0.071083 | 0.068686 | -0.0085961 | 0.016663 | -0.0037748 | -0.018311 | 59.6054 | -62.2559 | 59.8755 | -62.0453 | -62.5259 | -62.5168 | 0.041199 | 59.6146 | -62.3199 | 59.7931 | -62.2192 | -62.4344 | -62.439 | 0.022889 | -0.18768 | 0.082397 | 0.23346 | -0.23804 | -0.24719 | -0.26093 | -0.27008 | -0.041198 | -0.17853 | 0 | 0.05951 | -0.16022 | -0.15564 | -0.11902 | -0.11444 | 0.21057 | 122.1313 | 0.10071 | 122.113 | 121.8613 | 121.9345 | 121.8842 | 121.8933 | -122.0489 | -122.113 | 122.1542 | 122.0718 | 62.2604 | 62.3199
441.6094 | 122.3099 | -62.2879 | 59.7656 | -0.021286 | 0.0001345 | 0.059248 | 0.056898 | 0.00085879 | -0.0068381 | -0.0025485 | -0.0021057 | 2.1442e-05 | 0.072792 | 0.05651 | -0.0098779 | 0.016876 | -0.0005704 | -0.086975 | 59.5688 | -62.2742 | 59.8663 | -62.0316 | -62.5168 | -62.4847 | -0.004578 | 59.5642 | -62.3062 | 59.8068 | -62.2147 | -62.3886 | -62.4252 | 0.013733 | -0.19684 | 0.10071 | 0.25635 | -0.19684 | -0.22888 | -0.21057 | -0.24262 | -0.01831 | -0.20142 | 0.041199 | 0.073242 | -0.13733 | -0.10071 | -0.11902 | -0.082398 | 0.24262 | 122.1405 | 0.091552 | 122.113 | 121.843 | 121.8704 | 121.8567 | 121.8521 | -122.0398 | -122.0718 | 122.1542 | 122.0947 | 62.2009 | 62.2833
443.2812 | 122.2595 | -62.2787 | 59.816 | 0.016861 | 0.0014163 | 0.059889 | 0.059035 | -0.00063661 | -0.0027793 | -0.00019867 | -0.0021057 | 0.00023504 | 0.070015 | 0.065055 | -0.0077417 | 0.017517 | -0.0029202 | 0.068665 | 59.5779 | -62.2284 | 59.9213 | -61.9949 | -62.4619 | -62.4664 | 0.091553 | 59.6191 | -62.2879 | 59.7885 | -62.1964 | -62.3657 | -62.4298 | 0.050354 | -0.23804 | 0.10529 | 0.28381 | -0.18768 | -0.1831 | -0.23804 | -0.23346 | -0.009155 | -0.19684 | -0.027466 | 0.082398 | -0.15106 | -0.086975 | -0.14191 | -0.07782 | 0.23346 | 122.1497 | 0.091553 | 122.0764 | 121.8063 | 121.907 | 121.8567 | 121.8979 | -122.0444 | -122.1039 | 122.2 | 122.0673 | 62.3474 | 62.3703
445.0312 | 122.2046 | -62.2833 | 59.8434 | -0.013657 | -0.0013607 | 0.058821 | 0.05818 | -0.003841 | -0.0055563 | -0.0019077 | -0.0051575 | 0.00087584 | 0.072578 | 0.062064 | -0.0098779 | 0.016022 | -0.0014248 | -0.013733 | 59.6512 | -62.3016 | 59.848 | -62.0865 | -62.5259 | -62.5168 | 0.013733 | 59.6603 | -62.3062 | 59.761 | -62.2421 | -62.4115 | -62.4527 | -0.018311 | -0.19226 | 0.004577 | 0.19684 | -0.23346 | -0.24262 | -0.21515 | -0.2243 | -0.022888 | -0.18311 | -0.082398 | 0.041199 | -0.16937 | -0.12817 | -0.14648 | -0.10529 | 0.21515 | 122.1497 | 0.064087 | 122.0673 | 121.9528 | 121.9666 | 121.9345 | 121.9437 | -122.1451 | -122.1497 | 122.1313 | 122.0444 | 62.2696 | 62.2971
446.7188 | 122.2733 | -62.265 | 59.8068 | -0.0060272 | 0.0001345 | 0.059889 | 0.056685 | -0.00063661 | -0.0081197 | -0.0027621 | -0.0021057 | -0.0010468 | 0.074074 | 0.059287 | -0.0090235 | 0.015595 | -0.0029202 | 0.068665 | 59.5734 | -62.2513 | 59.9533 | -61.9858 | -62.439 | -62.4252 | 0.11902 | 59.5963 | -62.2742 | 59.8389 | -62.1735 | -62.3337 | -62.384 | 0.013733 | -0.23346 | 0.14648 | 0.27924 | -0.16022 | -0.17395 | -0.17395 | -0.18768 | -0.009155 | -0.21057 | 0.032043 | 0.091553 | -0.11902 | -0.068664 | -0.10986 | -0.059509 | 0.2655 | 122.2046 | 0.10071 | 122.113 | 121.8246 | 121.8704 | 121.8384 | 121.8613 | -122.0581 | -122.081 | 122.2183 | 122.1039 | 62.3337 | 62.384
448.4531 | 122.2961 | -62.2696 | 59.7473 | -0.013657 | 0.0031253 | 0.061598 | 0.059462 | 4.192e-06 | -0.0057699 | -0.0040439 | -0.0021057 | -0.0010468 | 0.068733 | 0.063773 | -0.0085961 | 0.016663 | -0.0037748 | -0.07782 | 59.5413 | -62.2559 | 59.903 | -62.0087 | -62.5168 | -62.4802 | 0.050354 | 59.5596 | -62.3062 | 59.8343 | -62.1872 | -62.3474 | -62.4023 | 0.013733 | -0.20599 | 0.15564 | 0.26093 | -0.21057 | -0.24719 | -0.22431 | -0.26093 | -0.036621 | -0.18768 | 0.086976 | 0.082397 | -0.13275 | -0.07782 | -0.096131 | -0.041199 | 0.24719 | 122.1588 | 0.11902 | 122.1405 | 121.7972 | 121.8658 | 121.8109 | 121.8292 | -122.0032 | -122.0535 | 122.1725 | 122.1039 | 62.1918 | 62.3199
450.2031 | 122.2321 | -62.2971 | 59.8022 | -0.013657 | 0.0046207 | 0.061598 | 0.061598 | 0.0036358 | -0.0051291 | -0.0031895 | 0.0009461 | 0.0023712 | 0.070656 | 0.0689 | -0.0096643 | 0.017303 | 0.0004978 | -0.13733 | 59.5963 | -62.3016 | 59.816 | -62.146 | -62.5946 | -62.5854 | -0.068665 | 59.6237 | -62.3566 | 59.7519 | -62.2833 | -62.4664 | -62.4802 | -0.004578 | -0.20599 | 0.013733 | 0.15106 | -0.28839 | -0.29755 | -0.28381 | -0.29297 | -0.059509 | -0.17853 | -0.050354 | 0.013733 | -0.18311 | -0.16937 | -0.1236 | -0.10986 | 0.15564 | 122.1176 | 0.073242 | 122.1085 | 121.8979 | 121.9803 | 121.8933 | 121.9208 | -122.1039 | -122.1588 | 122.113 | 122.0489 | 62.1597 | 62.2284
451.8906 | 122.3419 | -62.2559 | 59.7794 | -0.0060272 | -0.0022153 | 0.059035 | 0.058607 | 0.00064519 | -0.0042745 | -0.0019077 | -0.0021057 | 0.001944 | 0.07151 | 0.067405 | -0.0083825 | 0.015167 | -0.0048428 | 0.054932 | 59.5596 | -62.2559 | 59.9625 | -61.9446 | -62.4252 | -62.4069 | 0.14648 | 59.5779 | -62.2833 | 59.8709 | -62.1094 | -62.2925 | -62.3474 | 0 | -0.21973 | 0.1831 | 0.31128 | -0.15106 | -0.16937 | -0.15106 | -0.16937 | -0.027466 | -0.20142 | 0.091553 | 0.14648 | -0.091553 | -0.036621 | -0.064087 | -0.009155 | 0.31128 | 122.2183 | 0.17395 | 122.1542 | 121.8155 | 121.8613 | 121.8155 | 121.8338 | -122.0352 | -122.0627 | 122.2183 | 122.1268 | 62.3108 | 62.4023
453.6406 | 122.2778 | -62.2925 | 59.7931 | -0.013657 | 0.0018435 | 0.062453 | 0.06288 | 0.00064519 | -0.0034201 | -0.00083947 | 0.0009461 | 0.0040802 | 0.071938 | 0.065696 | -0.0090235 | 0.015381 | -0.004202 | 0.013733 | 59.6237 | -62.2742 | 59.8801 | -62.0682 | -62.4985 | -62.5076 | 0.07782 | 59.6329 | -62.3245 | 59.8206 | -62.1826 | -62.4023 | -62.4161 | 0.01831 | -0.16937 | 0.086975 | 0.2243 | -0.21515 | -0.20599 | -0.23346 | -0.2243 | -0.032044 | -0.16022 | 0.027466 | 0.10986 | -0.1236 | -0.10986 | -0.091553 | -0.07782 | 0.20599 | 122.1542 | 0.14191 | 122.1451 | 121.8979 | 121.9574 | 121.9162 | 121.9254 | -122.0673 | -122.1176 | 122.1725 | 122.113 | 62.3062 | 62.3703
455.375 | 122.2092 | -62.3062 | 59.8022 | -0.0060272 | 0.0022709 | 0.062453 | 0.062025 | 0.0014996 | -0.0032065 | -0.0036167 | -0.0021057 | 0.0021576 | 0.073006 | 0.063773 | -0.0066735 | 0.01709 | -0.0027066 | -0.073242 | 59.6146 | -62.2696 | 59.8434 | -62.0956 | -62.5763 | -62.5534 | -0.018311 | 59.6283 | -62.3383 | 59.7656 | -62.2787 | -62.4756 | -62.471 | 0.036621 | -0.18768 | 0.041199 | 0.21057 | -0.24719 | -0.27008 | -0.28381 | -0.3067 | -0.032044 | -0.17395 | -0.036621 | 0.027465 | -0.16479 | -0.16937 | -0.13275 | -0.13733 | 0.17395 | 122.113 | 0.059509 | 122.1039 | 121.8842 | 121.9666 | 121.9208 | 121.9345 | -122.0718 | -122.1405 | 122.1497 | 122.0718 | 62.233 | 62.2879
457.1094 | 122.3099 | -62.2833 | 59.7565 | 0.0092313 | 0.0026981 | 0.061171 | 0.057967 | -0.0032 | -0.0040609 | -0.00019867 | 0.0009461 | 0.00066224 | 0.070656 | 0.062491 | -0.0066735 | 0.015808 | -0.0001432 | -0.082397 | 59.5642 | -62.265 | 59.8984 | -61.9949 | -62.5122 | -62.4847 | 0.059509 | 59.5367 | -62.352 | 59.8251 | -62.178 | -62.3566 | -62.3886 | 0.01831 | -0.19226 | 0.14191 | 0.28839 | -0.20142 | -0.22888 | -0.21973 | -0.24719 | -0.068665 | -0.21973 | 0.068664 | 0.10528 | -0.10529 | -0.073242 | -0.036621 | -0.004577 | 0.27008 | 122.1634 | 0.17395 | 122.1771 | 121.8292 | 121.8887 | 121.8475 | 121.8201 | -122.0215 | -122.1085 | 122.1817 | 122.1085 | 62.2009 | 62.3428
458.8438 | 122.3053 | -62.2467 | 59.7473 | -0.021286 | 0.0020571 | 0.059462 | 0.059035 | -0.0059772 | -0.0053427 | -0.00019867 | -0.0051575 | 0.00023504 | 0.070869 | 0.067618 | -0.0068871 | 0.015381 | -0.0033474 | -0.082397 | 59.5413 | -62.2787 | 59.903 | -62.0178 | -62.5122 | -62.4802 | 0.036621 | 59.5642 | -62.3245 | 59.8297 | -62.1964 | -62.3749 | -62.3978 | -0.032044 | -0.20599 | 0.15564 | 0.22888 | -0.23346 | -0.2655 | -0.20142 | -0.23346 | -0.07782 | -0.18311 | 0.082398 | 0.050354 | -0.15106 | -0.12817 | -0.073242 | -0.050354 | 0.26093 | 122.1817 | 0.12817 | 122.1542 | 121.8201 | 121.8887 | 121.788 | 121.8109 | -122.0261 | -122.0718 | 122.1497 | 122.0764 | 62.1643 | 62.2833
460.5156 | 122.2366 | -62.265 | 59.816 | -0.0060272 | 0.0007755 | 0.061812 | 0.058821 | 4.192e-06 | -0.0057699 | -0.00062587 | 0.0039977 | 0.001303 | 0.072151 | 0.065055 | -0.0098779 | 0.016876 | -0.0005704 | 0.022888 | 59.6008 | -62.2742 | 59.8663 | -62.0453 | -62.5168 | -62.5031 | 0.041199 | 59.6283 | -62.3016 | 59.7794 | -62.2238 | -62.4115 | -62.4435 | -0.009155 | -0.21515 | 0.050354 | 0.21973 | -0.23804 | -0.25177 | -0.22888 | -0.24262 | -0.036621 | -0.18768 | -0.036621 | 0.041199 | -0.17853 | -0.14648 | -0.14191 | -0.10986 | 0.22888 | 122.1405 | 0.07782 | 122.081 | 121.875 | 121.9299 | 121.8658 | 121.8933 | -122.0901 | -122.1176 | 122.1313 | 122.0444 | 62.2879 | 62.3062
462.2656 | 122.3145 | -62.2787 | 59.7473 | -0.0060272 | -0.0011471 | 0.062453 | 0.058394 | -0.0019184 | -0.0066245 | -0.0034031 | 0.0039977 | 0.00023504 | 0.070015 | 0.055442 | -0.0081689 | 0.016663 | -0.0031338 | -0.064087 | 59.5688 | -62.2559 | 59.8709 | -62.0316 | -62.5214 | -62.4847 | 0.018311 | 59.5825 | -62.3108 | 59.8297 | -62.178 | -62.3566 | -62.3886 | 0.022889 | -0.17853 | 0.1236 | 0.24719 | -0.20599 | -0.24261 | -0.22888 | -0.2655 | -0.032043 | -0.16479 | 0.082398 | 0.10071 | -0.10986 | -0.077819 | -0.07782 | -0.045776 | 0.2243 | 122.1268 | 0.13275 | 122.1405 | 121.8246 | 121.8933 | 121.8475 | 121.8613 | -122.0032 | -122.0581 | 122.1497 | 122.1085 | 62.2147 | 62.2971
464.0156 | 122.2641 | -62.2742 | 59.8022 | -0.013657 | 0.0046207 | 0.060103 | 0.061171 | -0.00085021 | -0.0051291 | -0.00083947 | -0.0082093 | 0.0045074 | 0.073219 | 0.074454 | -0.0090235 | 0.017944 | -0.0009976 | 0.022888 | 59.6237 | -62.2696 | 59.8709 | -62.0544 | -62.5168 | -62.5076 | 0.068665 | 59.6146 | -62.3108 | 59.816 | -62.1826 | -62.3886 | -62.4161 | 0.004578 | -0.17853 | 0.068665 | 0.21973 | -0.23346 | -0.24262 | -0.23804 | -0.24719 | -0.036621 | -0.18768 | 0.013733 | 0.091553 | -0.14191 | -0.11444 | -0.10529 | -0.07782 | 0.21515 | 122.1405 | 0.12817 | 122.1268 | 121.8933 | 121.9254 | 121.8979 | 121.8887 | -122.0718 | -122.113 | 122.1451 | 122.0901 | 62.2971 | 62.3428
465.7656 | 122.3099 | -62.2696 | 59.7839 | -0.013657 | 0.0005619 | 0.061598 | 0.057753 | -0.0010638 | -0.0055563 | -0.0010531 | -0.0051575 | 2.1442e-05 | 0.071724 | 0.063773 | -0.0075281 | 0.016449 | -0.0048428 | -0.082397 | 59.5596 | -62.2833 | 59.8663 | -62.0361 | -62.5168 | -62.4802 | 0.022888 | 59.5642 | -62.3154 | 59.8297 | -62.1964 | -62.3337 | -62.4023 | -0.013733 | -0.2243 | 0.082397 | 0.23346 | -0.21057 | -0.24719 | -0.19684 | -0.23346 | -0.045777 | -0.21973 | 0.045776 | 0.073242 | -0.13275 | -0.064087 | -0.086975 | -0.01831 | 0.24719 | 122.1497 | 0.11902 | 122.1451 | 121.843 | 121.8796 | 121.8292 | 121.8338 | -122.0673 | -122.0993 | 122.1359 | 122.0993 | 62.1872 | 62.2925
467.4531 | 122.2321 | -62.2833 | 59.8022 | 0.0016023 | 0.0041935 | 0.060957 | 0.059462 | 0.00064519 | -0.0053427 | -0.0010531 | 0.0009461 | 0.004721 | 0.07151 | 0.068045 | -0.0077417 | 0.018372 | -0.0014248 | -0.018311 | 59.6146 | -62.233 | 59.8801 | -62.059 | -62.5397 | -62.5442 | 0.036621 | 59.6191 | -62.3199 | 59.7977 | -62.2284 | -62.4435 | -62.4435 | 0.050354 | -0.18768 | 0.07782 | 0.2243 | -0.26093 | -0.25635 | -0.31128 | -0.3067 | -0.036621 | -0.1831 | -0.004578 | 0.054931 | -0.16022 | -0.16022 | -0.1236 | -0.1236 | 0.17395 | 122.113 | 0.091552 | 122.1176 | 121.8475 | 121.9391 | 121.8979 | 121.9025 | -122.0352 | -122.1222 | 122.1634 | 122.081 | 62.265 | 62.3199
469.1875 | 122.287 | -62.2513 | 59.8068 | 0.0016023 | -0.0015743 | 0.06053 | 0.056471 | 0.0025678 | -0.0068381 | -0.00041227 | -0.0021057 | 0.001944 | 0.07151 | 0.067832 | -0.0085961 | 0.017303 | -0.0020658 | 0.068665 | 59.5734 | -62.2696 | 59.9579 | -61.9675 | -62.4435 | -62.4161 | 0.12817 | 59.5871 | -62.2742 | 59.8297 | -62.1552 | -62.3337 | -62.3795 | -0.01831 | -0.23346 | 0.15106 | 0.28381 | -0.16479 | -0.19226 | -0.14648 | -0.17395 | -0.022888 | -0.21973 | 0.022888 | 0.096131 | -0.12817 | -0.082397 | -0.10529 | -0.059509 | 0.30212 | 122.2275 | 0.11902 | 122.1039 | 121.843 | 121.8613 | 121.8246 | 121.8384 | -122.0764 | -122.081 | 122.2092 | 122.081 | 62.3199 | 62.3795
470.875 | 122.3602 | -62.2604 | 59.761 | -0.0060272 | -0.0013607 | 0.059676 | 0.057967 | -0.0023456 | -0.0047019 | -0.0016941 | -0.0051575 | -0.00019216 | 0.072578 | 0.063346 | -0.0071009 | 0.016876 | -0.0009976 | 0.004578 | 59.5779 | -62.2559 | 59.935 | -61.9492 | -62.4207 | -62.4023 | 0.14191 | 59.5871 | -62.3062 | 59.8801 | -62.1002 | -62.2833 | -62.3337 | 0.004578 | -0.1831 | 0.17395 | 0.31128 | -0.14191 | -0.16022 | -0.14648 | -0.16479 | -0.045776 | -0.17395 | 0.11902 | 0.16022 | -0.073242 | -0.022888 | -0.027466 | 0.022888 | 0.3067 | 122.1909 | 0.20599 | 122.1863 | 121.8338 | 121.8933 | 121.8384 | 121.8475 | -122.0169 | -122.0673 | 122.1954 | 122.1405 | 62.265 | 62.4023
472.625 | 122.3557 | -62.2696 | 59.7427 | -0.0060272 | 0.0039799 | 0.06288 | 0.062025 | -0.00042301 | -0.0042745 | -0.0023349 | -0.0051575 | 0.00087584 | 0.071083 | 0.062705 | -0.012869 | 0.019226 | -0.0044156 | -0.07782 | 59.5276 | -62.2696 | 59.9121 | -62.0224 | -62.4893 | -62.4756 | 0.036621 | 59.5642 | -62.3154 | 59.8572 | -62.1643 | -62.3428 | -62.3566 | 0 | -0.21515 | 0.16937 | 0.24719 | -0.20599 | -0.21973 | -0.20599 | -0.21973 | -0.045777 | -0.17853 | 0.11444 | 0.10529 | -0.086975 | -0.073242 | -0.041198 | -0.027465 | 0.24719 | 122.1817 | 0.15106 | 122.1725 | 121.7972 | 121.8796 | 121.7972 | 121.8338 | -122.0123 | -122.0581 | 122.1817 | 122.1268 | 62.1918 | 62.3062
474.3594 | 122.3099 | -62.2833 | 59.7702 | 0.0016023 | 0.0007755 | 0.060316 | 0.058607 | -0.0012774 | -0.0051291 | -0.0053257 | 0.0009461 | 0.00023504 | 0.07151 | 0.057364 | -0.0085961 | 0.015808 | -0.003561 | -0.10529 | 59.5688 | -62.2742 | 59.8846 | -62.0407 | -62.5214 | -62.4756 | 0.018311 | 59.5596 | -62.3199 | 59.816 | -62.1826 | -62.3795 | -62.3978 | 0.009155 | -0.20142 | 0.11444 | 0.24262 | -0.19226 | -0.23804 | -0.20142 | -0.24719 | -0.036621 | -0.21057 | 0.045776 | 0.10071 | -0.11444 | -0.096131 | -0.07782 | -0.05951 | 0.23346 | 122.1588 | 0.13733 | 122.1359 | 121.843 | 121.8796 | 121.8521 | 121.843 | -122.0444 | -122.0901 | 122.168 | 122.0993 | 62.178 | 62.3016
476.0938 | 122.3511 | -62.2879 | 59.7382 | -0.0060272 | 0.0033389 | 0.060957 | 0.059035 | 0.00085879 | -0.0059835 | -0.0046847 | -0.0051575 | 0.001303 | 0.070229 | 0.065055 | -0.0081689 | 0.016449 | -0.0054838 | -0.07782 | 59.5139 | -62.2787 | 59.9258 | -62.0041 | -62.4985 | -62.471 | 0.050354 | 59.5551 | -62.3199 | 59.8755 | -62.1506 | -62.3337 | -62.3703 | 0.009155 | -0.2243 | 0.18768 | 0.28381 | -0.1831 | -0.21057 | -0.19226 | -0.21973 | -0.032043 | -0.18311 | 0.13733 | 0.13733 | -0.082397 | -0.045776 | -0.050354 | -0.013733 | 0.27466 | 122.2046 | 0.16937 | 122.1954 | 121.7926 | 121.875 | 121.8018 | 121.843 | -122.0169 | -122.0581 | 122.2137 | 122.1634 | 62.2101 | 62.3383
477.7656 | 122.2321 | -62.2696 | 59.8251 | -0.0060272 | -0.0013607 | 0.060103 | 0.060103 | 0.0032086 | -0.0040609 | -0.0012669 | -0.0051575 | 0.00023504 | 0.074074 | 0.065268 | -0.0090235 | 0.017303 | -0.0029202 | 0.059509 | 59.5963 | -62.2559 | 59.8892 | -62.0407 | -62.4802 | -62.471 | 0.073242 | 59.6283 | -62.3016 | 59.7794 | -62.2147 | -62.4069 | -62.4435 | 0.013733 | -0.22888 | 0.064087 | 0.22888 | -0.20142 | -0.21057 | -0.21515 | -0.22431 | -0.032044 | -0.19684 | -0.045776 | 0.054931 | -0.17395 | -0.13733 | -0.14191 | -0.10528 | 0.21515 | 122.1451 | 0.086975 | 122.081 | 121.8521 | 121.9299 | 121.8658 | 121.8979 | -122.081 | -122.1268 | 122.1588 | 122.049 | 62.3291 | 62.3428
479.5156 | 122.2366 | -62.2787 | 59.816 | 0.0016023 | -0.0007199 | 0.059676 | 0.059889 | -0.0019184 | -0.0066245 | -0.0036167 | 0.0009461 | 0.0038666 | 0.071724 | 0.068259 | -0.0088097 | 0.016663 | -0.0050564 | -0.004578 | 59.6558 | -62.2925 | 59.8526 | -62.0911 | -62.5442 | -62.5305 | 0 | 59.6649 | -62.3108 | 59.7794 | -62.2375 | -62.4161 | -62.4344 | -0.013732 | -0.16022 | 0.036621 | 0.18768 | -0.25177 | -0.2655 | -0.23804 | -0.25177 | -0.032043 | -0.15106 | -0.036621 | 0.041199 | -0.15564 | -0.13733 | -0.1236 | -0.10529 | 0.20142 | 122.1451 | 0.073242 | 122.0901 | 121.9482 | 121.9757 | 121.9345 | 121.9437 | -122.1085 | -122.1268 | 122.1313 | 122.0581 | 62.2742 | 62.2787
481.2031 | 122.3419 | -62.2833 | 59.7427 | -0.0060272 | 0.0024845 | 0.062025 | 0.059889 | 0.0019268 | -0.0059835 | -0.0023349 | -0.0051575 | 0.001944 | 0.070015 | 0.073172 | -0.0081689 | 0.017731 | -0.0031338 | -0.082397 | 59.5459 | -62.2513 | 59.9258 | -61.9949 | -62.4939 | -62.4664 | 0.050354 | 59.5413 | -62.3383 | 59.8663 | -62.146 | -62.3383 | -62.3749 | 0.032043 | -0.19684 | 0.18311 | 0.28839 | -0.18311 | -0.21057 | -0.21515 | -0.24261 | -0.054932 | -0.20142 | 0.1236 | 0.13733 | -0.091553 | -0.054932 | -0.036621 | 0 | 0.25635 | 122.1771 | 0.19226 | 122.2046 | 121.7972 | 121.8796 | 121.8292 | 121.8246 | -121.994 | -122.081 | 122.2092 | 122.1497 | 62.2009 | 62.3337
482.9531 | 122.2275 | -62.3016 | 59.8434 | 0.0016023 | -0.0013607 | 0.061598 | 0.059462 | -0.0027728 | -0.0091879 | -0.0031895 | -0.0051575 | 0.0032256 | 0.073006 | 0.060569 | -0.0088097 | 0.01474 | -0.004202 | -0.004578 | 59.6146 | -62.2696 | 59.8572 | -62.0773 | -62.5305 | -62.5214 | 0.027466 | 59.6603 | -62.3016 | 59.7748 | -62.2284 | -62.4161 | -62.4435 | 0.032044 | -0.22888 | 0.013733 | 0.2243 | -0.21973 | -0.22888 | -0.25177 | -0.26093 | 0 | -0.18311 | -0.068665 | 0.073242 | -0.14191 | -0.11444 | -0.14191 | -0.11444 | 0.19226 | 122.1268 | 0.073242 | 122.0764 | 121.8842 | 121.962 | 121.9162 | 121.962 | -122.113 | -122.1451 | 122.1588 | 122.0764 | 62.2971 | 62.3291
484.6406 | 122.3511 | -62.2604 | 59.7473 | -0.0060272 | -0.0028561 | 0.060103 | 0.056898 | -0.0019184 | -0.0038473 | -0.0016941 | 0.0009461 | -0.00083316 | 0.071297 | 0.063987 | -0.0088097 | 0.016876 | -0.002493 | -0.009155 | 59.5642 | -62.2971 | 59.9442 | -61.9537 | -62.4161 | -62.4161 | 0.14191 | 59.5871 | -62.3062 | 59.9121 | -62.0911 | -62.2696 | -62.352 | -0.036621 | -0.18311 | 0.19684 | 0.3067 | -0.15564 | -0.15564 | -0.11902 | -0.11902 | -0.045776 | -0.16022 | 0.16479 | 0.16937 | -0.091553 | -0.009155 | -0.045777 | 0.036621 | 0.34332 | 122.2412 | 0.21515 | 122.2183 | 121.8613 | 121.8933 | 121.8246 | 121.8475 | -122.0444 | -122.0535 | 122.2046 | 122.1725 | 62.2513 | 62.4023
486.3906 | 122.2595 | -62.2696 | 59.8206 | 0.0016023 | 0.0012027 | 0.060103 | 0.060744 | -0.00020941 | -0.0070517 | -0.0016941 | -0.0021057 | 0.0034392 | 0.069801 | 0.065482 | -0.010732 | 0.017944 | -0.0018522 | 0.018311 | 59.6329 | -62.265 | 59.8755 | -62.0636 | -62.5031 | -62.5168 | 0.022888 | 59.6512 | -62.2971 | 59.8114 | -62.2147 | -62.3978 | -62.4252 | 0.004577 | -0.18768 | 0.054931 | 0.20599 | -0.24719 | -0.23346 | -0.25177 | -0.23804 | -0.027466 | -0.16937 | -0.009156 | 0.054931 | -0.15564 | -0.12817 | -0.12817 | -0.10071 | 0.20142 | 122.1405 | 0.082397 | 122.1085 | 121.8979 | 121.9482 | 121.9025 | 121.9208 | -122.0856 | -122.1176 | 122.1451 | 122.081 | 62.2879 | 62.2925
488.125 | 122.2687 | -62.2742 | 59.8114 | -0.0060272 | 0.0022709 | 0.059035 | 0.05818 | -0.00020941 | -0.0047019 | 1.4934e-05 | -0.0021057 | 0.003012 | 0.071938 | 0.066764 | -0.010519 | 0.019653 | -0.0027066 | -0.004578 | 59.6146 | -62.2742 | 59.8938 | -62.027 | -62.5122 | -62.4893 | 0.07782 | 59.6283 | -62.3337 | 59.8297 | -62.2009 | -62.3886 | -62.3978 | 0 | -0.19684 | 0.082398 | 0.24719 | -0.21515 | -0.23804 | -0.21515 | -0.23804 | -0.059509 | -0.1831 | 0.018311 | 0.073242 | -0.1236 | -0.11444 | -0.064087 | -0.054932 | 0.24719 | 122.168 | 0.13275 | 122.1634 | 121.8887 | 121.962 | 121.8887 | 121.9025 | -122.0856 | -122.1451 | 122.168 | 122.1039 | 62.2696 | 62.352
489.8125 | 122.2137 | -62.2787 | 59.8343 | -0.013657 | -0.0015743 | 0.059035 | 0.056471 | -0.00020941 | -0.0079061 | -0.0014805 | -0.0082093 | 0.0032256 | 0.073219 | 0.064414 | -0.0088097 | 0.017731 | -0.0037748 | -0.027466 | 59.6283 | -62.2604 | 59.848 | -62.0728 | -62.5259 | -62.5076 | 0.018311 | 59.6603 | -62.3016 | 59.761 | -62.2284 | -62.4069 | -62.4435 | 0.018311 | -0.20599 | 0.013732 | 0.20599 | -0.22888 | -0.24719 | -0.24719 | -0.2655 | -0.022888 | -0.17395 | -0.073243 | 0.050354 | -0.16479 | -0.12817 | -0.14191 | -0.10528 | 0.18768 | 122.1085 | 0.073242 | 122.0627 | 121.8887 | 121.962 | 121.907 | 121.9391 | -122.0947 | -122.1359 | 122.1268 | 122.0398 | 62.2513 | 62.2971
491.5625 | 122.2824 | -62.2833 | 59.7885 | -0.013657 | 0.0026981 | 0.060103 | 0.05818 | -0.00085021 | -0.0042745 | -0.0031895 | -0.0021057 | 0.0015166 | 0.074715 | 0.056723 | -0.0096643 | 0.017303 | -0.0033474 | -0.07782 | 59.5779 | -62.2696 | 59.8572 | -62.0499 | -62.5214 | -62.5168 | -0.004578 | 59.5688 | -62.3108 | 59.816 | -62.1964 | -62.3611 | -62.3886 | 0.013733 | -0.21057 | 0.068665 | 0.23346 | -0.23346 | -0.23804 | -0.24719 | -0.25177 | -0.027466 | -0.21973 | 0.027466 | 0.086975 | -0.10529 | -0.07782 | -0.07782 | -0.050354 | 0.21973 | 122.1268 | 0.11444 | 122.1268 | 121.8475 | 121.8796 | 121.8613 | 121.8521 | -122.0581 | -122.0993 | 122.1405 | 122.0993 | 62.2055 | 62.2787
493.2969 | 122.2961 | -62.2879 | 59.7839 | -0.013657 | 0.0012027 | 0.061385 | 0.056898 | -0.0019184 | -0.0049155 | -0.00041227 | -0.0051575 | 0.001303 | 0.070869 | 0.062918 | -0.0094507 | 0.017517 | -0.0020658 | -0.082397 | 59.5642 | -62.2971 | 59.8755 | -62.0316 | -62.5168 | -62.4893 | 0.009155 | 59.5642 | -62.3016 | 59.8068 | -62.1918 | -62.3703 | -62.4069 | -0.009155 | -0.21973 | 0.091552 | 0.25635 | -0.20142 | -0.22888 | -0.19226 | -0.21973 | -0.013733 | -0.21973 | 0.022888 | 0.096131 | -0.11902 | -0.082397 | -0.10528 | -0.068664 | 0.2655 | 122.1725 | 0.10986 | 122.1085 | 121.8613 | 121.8658 | 121.8521 | 121.8521 | -122.081 | -122.0856 | 122.1634 | 122.0947 | 62.2055 | 62.2971
495.0469 | 122.2458 | -62.265 | 59.8297 | -0.0060272 | 0.0005619 | 0.057753 | 0.059889 | -0.0046954 | -0.0053427 | -0.0021213 | -0.0021057 | 0.00087584 | 0.071938 | 0.06655 | -0.0098779 | 0.016235 | 0.0017794 | 0.045776 | 59.5734 | -62.2467 | 59.9258 | -61.9995 | -62.4435 | -62.4664 | 0.082397 | 59.6146 | -62.2971 | 59.7839 | -62.2009 | -62.3749 | -62.4207 | 0.018311 | -0.25635 | 0.09613 | 0.2655 | -0.20142 | -0.17853 | -0.21973 | -0.19684 | -0.032043 | -0.21515 | -0.045776 | 0.064087 | -0.15564 | -0.10986 | -0.1236 | -0.07782 | 0.24719 | 122.1725 | 0.09613 | 122.081 | 121.8201 | 121.9116 | 121.8384 | 121.8796 | -122.0764 | -122.1268 | 122.1909 | 122.049 | 62.3108 | 62.3474
496.7969 | 122.287 | -62.2787 | 59.7565 | -0.0060272 | 0.0020571 | 0.060744 | 0.059248 | -0.0012774 | -0.0057699 | -0.0023349 | -0.0021057 | 0.0010894 | 0.071083 | 0.068473 | -0.0085961 | 0.016235 | -0.0014248 | -0.09613 | 59.5642 | -62.2833 | 59.8709 | -62.0361 | -62.5076 | -62.4802 | 0.022888 | 59.5459 | -62.3383 | 59.816 | -62.1964 | -62.3703 | -62.3978 | -0.004577 | -0.19226 | 0.11444 | 0.24262 | -0.20142 | -0.22888 | -0.19684 | -0.2243 | -0.059509 | -0.21057 | 0.059509 | 0.082398 | -0.11902 | -0.091552 | -0.059509 | -0.032043 | 0.24719 | 122.1542 | 0.14191 | 122.1542 | 121.8475 | 121.8842 | 121.843 | 121.8246 | -122.0398 | -122.0947 | 122.1497 | 122.0947 | 62.1826 | 62.3016
498.4688 | 122.2366 | -62.2467 | 59.8389 | -0.013657 | -7.9104e-05 | 0.059248 | 0.06053 | 0.001286 | -0.0057699 | -0.0025485 | -0.0021057 | 0.0027984 | 0.071297 | 0.062491 | -0.0085961 | 0.016235 | -0.0050564 | -0.013733 | 59.6329 | -62.2742 | 59.8434 | -62.0956 | -62.5442 | -62.5442 | 0.004578 | 59.6603 | -62.3108 | 59.7748 | -62.2101 | -62.4023 | -62.4161 | -0.027466 | -0.20599 | 0.004578 | 0.15106 | -0.29755 | -0.29755 | -0.27008 | -0.27008 | -0.064087 | -0.17853 | -0.064087 | 0.036621 | -0.16937 | -0.15564 | -0.10529 | -0.091553 | 0.17853 | 122.1176 | 0.10071 | 122.0856 | 121.907 | 121.9711 | 121.8796 | 121.907 | -122.113 | -122.1497 | 122.0901 | 122.0215 | 62.233 | 62.2513
500.2031 | 122.2595 | -62.2604 | 59.7885 | -0.013657 | 0.0009891 | 0.06053 | 0.060316 | -0.002132 | -0.0042745 | -0.00083947 | -0.0021057 | 0.005362 | 0.074074 | 0.065055 | -0.0094507 | 0.016876 | -0.0012112 | -0.004578 | 59.6237 | -62.2925 | 59.8938 | -62.0453 | -62.5259 | -62.4985 | 0.068665 | 59.642 | -62.2879 | 59.8297 | -62.1872 | -62.3932 | -62.3978 | -0.032043 | -0.1648 | 0.10529 | 0.21515 | -0.23804 | -0.2655 | -0.20599 | -0.23346 | -0.027466 | -0.14648 | 0.041199 | 0.073242 | -0.13733 | -0.13275 | -0.10986 | -0.10529 | 0.24719 | 122.1863 | 0.10071 | 122.1176 | 121.9162 | 121.9299 | 121.8842 | 121.9025 | -122.081 | -122.0764 | 122.1542 | 122.0901 | 62.2559 | 62.3291
501.9375 | 122.3373 | -62.2971 | 59.7519 | -0.013657 | 0.0037661 | 0.061812 | 0.060103 | -0.00020941 | -0.0042745 | -0.0025485 | -0.0021057 | 0.0027984 | 0.070229 | 0.061209 | -0.0096643 | 0.018158 | -0.0031338 | -0.086975 | 59.5596 | -62.2604 | 59.9258 | -61.9904 | -62.4893 | -62.4802 | 0.073242 | 59.5642 | -62.3062 | 59.8755 | -62.1643 | -62.3337 | -62.352 | 0.036621 | -0.19226 | 0.17395 | 0.3067 | -0.18311 | -0.19226 | -0.21973 | -0.22888 | -0.009155 | -0.18768 | 0.1236 | 0.13275 | -0.054932 | -0.036621 | -0.045777 | -0.027466 | 0.27008 | 122.1863 | 0.14191 | 122.1817 | 121.8201 | 121.8704 | 121.8567 | 121.8613 | -122.0123 | -122.0581 | 122.2229 | 122.1725 | 62.2101 | 62.3703
503.625 | 122.3236 | -62.2696 | 59.7885 | -0.0060272 | -0.0020017 | 0.059889 | 0.057112 | -0.004909 | -0.0059835 | -0.0044711 | -0.0021057 | -0.00083316 | 0.071083 | 0.065268 | -0.0079553 | 0.016449 | -0.0033474 | -0.064087 | 59.5459 | -62.265 | 59.8938 | -62.0087 | -62.4893 | -62.4664 | 0.050354 | 59.5871 | -62.3062 | 59.8663 | -62.1597 | -62.3154 | -62.352 | 0.004577 | -0.24262 | 0.10529 | 0.26093 | -0.19684 | -0.21973 | -0.20142 | -0.2243 | -0.036621 | -0.20142 | 0.07782 | 0.10986 | -0.082398 | -0.045777 | -0.045777 | -0.009156 | 0.25635 | 122.1588 | 0.14648 | 122.1725 | 121.8109 | 121.8933 | 121.8155 | 121.8567 | -122.0535 | -122.0947 | 122.1634 | 122.1359 | 62.2055 | 62.3199
505.375 | 122.3602 | -62.2559 | 59.7702 | -0.013657 | -0.0020017 | 0.061171 | 0.057539 | 0.00043159 | -0.0044883 | -0.0014805 | -0.0051575 | 2.1442e-05 | 0.071297 | 0.067832 | -0.0088097 | 0.016022 | -0.0065518 | 0 | 59.5551 | -62.2559 | 59.935 | -61.9675 | -62.4435 | -62.4069 | 0.14648 | 59.5871 | -62.2833 | 59.903 | -62.0956 | -62.2696 | -62.3337 | 0 | -0.21515 | 0.16479 | 0.28839 | -0.15106 | -0.18768 | -0.15106 | -0.18768 | -0.027466 | -0.18311 | 0.13275 | 0.16022 | -0.07782 | -0.013733 | -0.050354 | 0.013733 | 0.28839 | 122.1909 | 0.18768 | 122.1863 | 121.8109 | 121.8704 | 121.8109 | 121.843 | -122.0261 | -122.0535 | 122.1909 | 122.1588 | 62.2559 | 62.4023
507.125 | 122.3511 | -62.2742 | 59.7244 | -0.0060272 | 0.0022709 | 0.06053 | 0.06053 | -0.0027728 | -0.0047019 | -0.0029759 | -0.0021057 | 0.0010894 | 0.071297 | 0.072959 | -0.0075281 | 0.018158 | -0.0005704 | -0.11902 | 59.5688 | -62.2833 | 59.8984 | -62.0224 | -62.5122 | -62.4939 | 0.041199 | 59.5459 | -62.3154 | 59.8663 | -62.1826 | -62.3611 | -62.352 | -0.009155 | -0.15564 | 0.17395 | 0.25177 | -0.21973 | -0.23804 | -0.21057 | -0.22888 | -0.041199 | -0.17853 | 0.14191 | 0.091553 | -0.07782 | -0.086975 | -0.036621 | -0.045776 | 0.26093 | 122.1817 | 0.13275 | 122.1817 | 121.8521 | 121.8613 | 121.843 | 121.8201 | -122.0078 | -122.0398 | 122.1725 | 122.1405 | 62.1552 | 62.3154
508.7969 | 122.2961 | -62.2742 | 59.7565 | -0.013657 | 0.0009891 | 0.058607 | 0.059462 | -0.0017048 | -0.0068381 | -0.0034031 | -0.0021057 | 0.0021576 | 0.071297 | 0.059073 | -0.0094507 | 0.016022 | -0.0016384 | -0.091553 | 59.5688 | -62.2559 | 59.8938 | -62.0453 | -62.5122 | -62.4893 | 0.009155 | 59.5917 | -62.3016 | 59.8206 | -62.2009 | -62.3703 | -62.4023 | 0.018311 | -0.18768 | 0.13733 | 0.22888 | -0.21515 | -0.23804 | -0.23346 | -0.25635 | -0.027466 | -0.16479 | 0.064087 | 0.073242 | -0.12817 | -0.09613 | -0.10071 | -0.068664 | 0.21057 | 122.1497 | 0.10071 | 122.1222 | 121.8246 | 121.8933 | 121.843 | 121.8658 | -122.0123 | -122.0581 | 122.168 | 122.0947 | 62.1826 | 62.2833
510.5312 | 122.3373 | -62.2559 | 59.7931 | -0.0060272 | 0.0012027 | 0.057326 | 0.05818 | 0.0023542 | -0.0076925 | -0.0012669 | -0.0051575 | -0.00019216 | 0.071938 | 0.065055 | -0.0092371 | 0.016663 | -0.0027066 | 0.032043 | 59.5413 | -62.265 | 59.9716 | -61.94 | -62.4115 | -62.4115 | 0.16479 | 59.5917 | -62.2971 | 59.8846 | -62.1002 | -62.2787 | -62.3383 | -0.009156 | -0.25177 | 0.17853 | 0.31586 | -0.15564 | -0.15564 | -0.14648 | -0.14648 | -0.041199 | -0.20142 | 0.091553 | 0.15564 | -0.082398 | -0.022889 | -0.041199 | 0.01831 | 0.32501 | 122.2366 | 0.19684 | 122.1817 | 121.8063 | 121.8887 | 121.7972 | 121.8475 | -122.0581 | -122.0901 | 122.2275 | 122.1405 | 62.2879 | 62.4207
512.2812 | 122.3007 | -62.2925 | 59.7656 | -0.0060272 | 0.0007755 | 0.060957 | 0.059248 | -0.0010638 | -0.0027793 | -0.00019867 | -0.0021057 | 2.1442e-05 | 0.071724 | 0.063559 | -0.010092 | 0.017944 | -0.0039884 | -0.09613 | 59.5688 | -62.2696 | 59.9075 | -61.9995 | -62.5122 | -62.471 | 0.054932 | 59.5596 | -62.3154 | 59.848 | -62.1872 | -62.3611 | -62.3749 | 0.022888 | -0.19684 | 0.14191 | 0.29297 | -0.17853 | -0.21973 | -0.20142 | -0.24261 | -0.022889 | -0.20599 | 0.082397 | 0.10528 | -0.082398 | -0.068665 | -0.059509 | -0.045776 | 0.27008 | 122.1771 | 0.12817 | 122.1634 | 121.8384 | 121.875 | 121.8613 | 121.8521 | -122.0352 | -122.081 | 122.2 | 122.1405 | 62.1963 | 62.3474
514.0156 | 122.3328 | -62.2513 | 59.7748 | -0.0060272 | -0.0015743 | 0.059676 | 0.058821 | -0.0010638 | -0.0068381 | -0.0021213 | -0.0021057 | 0.00044864 | 0.071724 | 0.074241 | -0.0068871 | 0.013886 | -0.0033474 | -0.059509 | 59.5825 | -62.2604 | 59.8938 | -62.0453 | -62.4893 | -62.4756 | 0.036621 | 59.5963 | -62.3062 | 59.848 | -62.1597 | -62.3428 | -62.3428 | -0.009155 | -0.19226 | 0.11902 | 0.20599 | -0.2243 | -0.23804 | -0.21515 | -0.22888 | -0.054931 | -0.17853 | 0.073242 | 0.091553 | -0.091552 | -0.091552 | -0.036621 | -0.036621 | 0.21515 | 122.1542 | 0.14648 | 122.1542 | 121.843 | 121.9025 | 121.8338 | 121.8475 | -122.0352 | -122.081 | 122.1451 | 122.0993 | 62.1918 | 62.2879
515.6875 | 122.2595 | -62.2833 | 59.816 | -0.0060272 | 0.0031253 | 0.060744 | 0.061171 | 0.001286 | -0.0027793 | -0.0034031 | -0.0051575 | 0.0023712 | 0.072578 | 0.065482 | -0.0098779 | 0.018158 | 0.0015658 | -0.004578 | 59.6329 | -62.2559 | 59.9075 | -62.0407 | -62.5031 | -62.4939 | 0.059509 | 59.6237 | -62.3154 | 59.8206 | -62.2101 | -62.4069 | -62.3245 | 0.027466 | -0.1831 | 0.091553 | 0.24262 | -0.21057 | -0.21973 | -0.23804 | -0.24719 | -0.032044 | -0.19226 | 0.004578 | 0.073242 | -0.041199 | -0.1236 | -0.009155 | -0.091552 | 0.21515 | 122.1634 | 0.10529 | 122.1359 | 121.8887 | 121.9391 | 121.9162 | 121.907 | -122.0718 | -122.1313 | 122.1909 | 122.1039 | 62.2787 | 62.3428
517.4375 | 122.2595 | -62.2696 | 59.8068 | -0.0060272 | -0.0002927 | 0.059676 | 0.060744 | -0.0017048 | -0.0049155 | -0.0016941 | -0.0051575 | 0.00023504 | 0.073219 | 0.070395 | -0.0096643 | 0.016663 | 0.0019932 | 0.004578 | 59.6466 | -62.2604 | 59.8892 | -62.059 | -62.5076 | -62.5214 | 0.045776 | 59.6237 | -62.3108 | 59.8297 | -62.1964 | -62.4069 | -62.2467 | 0.009155 | -0.16022 | 0.082397 | 0.21057 | -0.25177 | -0.23804 | -0.26093 | -0.24719 | -0.041199 | -0.18311 | 0.022888 | 0.073242 | 0.022888 | -0.13733 | 0.064087 | -0.09613 | 0.20142 | 122.1497 | 0.11444 | 122.1405 | 121.907 | 121.9345 | 121.9162 | 121.8933 | -122.0673 | -122.1176 | 122.1588 | 122.0993 | 62.2742 | 62.3154
519.1719 | 122.2733 | -62.2971 | 59.7748 | -0.021286 | -7.9104e-05 | 0.060744 | 0.056685 | -0.002132 | -0.0066245 | -0.0027621 | -0.0051575 | -0.00019216 | 0.073219 | 0.061423 | -0.0075281 | 0.016876 | -0.0016384 | -0.086975 | 59.5413 | -62.2833 | 59.8755 | -62.0407 | -62.5305 | -62.4985 | -0.009155 | 59.5688 | -62.3337 | 59.8297 | -62.2009 | -62.3795 | -62.2238 | 0.013733 | -0.23346 | 0.10071 | 0.25635 | -0.20142 | -0.23346 | -0.21515 | -0.24719 | -0.036621 | -0.20599 | 0.054932 | 0.09613 | 0.073242 | -0.082398 | 0.10986 | -0.045777 | 0.24262 | 122.1588 | 0.13275 | 122.1634 | 121.8246 | 121.9025 | 121.8384 | 121.8658 | -122.0581 | -122.1085 | 122.1725 | 122.1268 | 62.2101 | 62.2879
520.8594 | 122.2046 | -62.2833 | 59.8434 | -0.0060272 | -0.0009335 | 0.057967 | 0.05818 | -0.0023456 | -0.0072653 | -0.0014805 | -0.0021057 | 0.0015166 | 0.074715 | 0.065696 | -0.0077417 | 0.013245 | 0.000925 | 0 | 59.6283 | -62.2559 | 59.8618 | -62.0682 | -62.5305 | -62.5168 | 0.022888 | 59.6695 | -62.3016 | 59.7748 | -62.2284 | -62.4207 | -62.3154 | 0.027466 | -0.21515 | 0.01831 | 0.21515 | -0.23346 | -0.24719 | -0.26093 | -0.27466 | -0.018311 | -0.17395 | -0.068665 | 0.054931 | -0.032044 | -0.13733 | -0.013733 | -0.11902 | 0.18768 | 122.1176 | 0.073242 | 122.0764 | 121.8842 | 121.9711 | 121.9116 | 121.9528 | -122.0993 | -122.1451 | 122.1451 | 122.0581 | 62.2833 | 62.3062
522.625 | 122.2137 | -62.2971 | 59.8022 | -0.0060272 | 0.0018435 | 0.064162 | 0.059462 | 0.004704 | -0.0064109 | -0.0010531 | -0.0021057 | 0.0032256 | 0.072578 | 0.064627 | -0.0077417 | 0.020081 | -0.0018522 | -0.10986 | 59.642 | -62.2879 | 59.7977 | -62.1597 | -62.6358 | -62.5992 | -0.10071 | 59.6146 | -62.3566 | 59.761 | -62.2879 | -62.4985 | -62.3703 | 0.009155 | -0.16022 | -0.004578 | 0.13733 | -0.30212 | -0.33875 | -0.31128 | -0.3479 | -0.059509 | -0.18768 | -0.041199 | 0.009155 | -0.073242 | -0.20142 | -0.013733 | -0.14191 | 0.12817 | 122.0856 | 0.068664 | 122.1176 | 121.9299 | 121.9711 | 121.9391 | 121.9116 | -122.0901 | -122.1588 | 122.0947 | 122.0581 | 62.1872 | 62.1964
524.3594 | 122.2366 | -62.3062 | 59.8114 | -0.013657 | 0.0014163 | 0.061598 | 0.058821 | 0.00043159 | -0.0059835 | -0.0021213 | 0.0009461 | 0.004721 | 0.072365 | 0.071891 | -0.0096643 | 0.017303 | -0.0027066 | -0.032043 | 59.61 | -62.2833 | 59.8892 | -62.0407 | -62.5305 | -62.5122 | 0.032043 | 59.642 | -62.3154 | 59.8022 | -62.2238 | -62.4298 | -62.2696 | 0.022888 | -0.20142 | 0.07782 | 0.2655 | -0.20599 | -0.22431 | -0.22888 | -0.24719 | -0.009156 | -0.16937 | -0.009155 | 0.082397 | 0.036621 | -0.1236 | 0.045777 | -0.11444 | 0.24262 | 122.1725 | 0.091553 | 122.1176 | 121.8933 | 121.9574 | 121.9162 | 121.9482 | -122.0947 | -122.1268 | 122.1954 | 122.1085 | 62.2742 | 62.3383
526.1094 | 122.2916 | -62.2879 | 59.7656 | -0.013657 | 0.0018435 | 0.061812 | 0.057967 | -0.001491 | -0.0051291 | -0.0021213 | -0.0051575 | 0.0015166 | 0.073219 | 0.0642 | -0.0085961 | 0.016663 | -0.0048428 | -0.10986 | 59.5367 | -62.2467 | 59.8663 | -62.0132 | -62.5122 | -62.4847 | 0.032043 | 59.5688 | -62.3108 | 59.8251 | -62.1872 | -62.3566 | -62.265 | 0.041199 | -0.22888 | 0.10071 | 0.27466 | -0.19684 | -0.2243 | -0.23804 | -0.2655 | -0.022888 | -0.19684 | 0.059509 | 0.10071 | 0.022888 | -0.068664 | 0.045776 | -0.045776 | 0.23346 | 122.113 | 0.1236 | 122.1359 | 121.7834 | 121.8796 | 121.8246 | 121.8567 | -122.0123 | -122.0764 | 122.1542 | 122.113 | 62.178 | 62.3199
527.8594 | 122.2321 | -62.3108 | 59.8022 | -0.013657 | 0.0016299 | 0.062453 | 0.061812 | 0.00043159 | -0.0040609 | -0.0016941 | -0.0021057 | 0.0040802 | 0.075569 | 0.072532 | -0.0071009 | 0.017944 | 0.0002842 | -0.027466 | 59.6146 | -62.2696 | 59.8846 | -62.059 | -62.5397 | -62.5076 | 0.050354 | 59.6146 | -62.3062 | 59.8206 | -62.2101 | -62.4207 | -62.2925 | 0.041199 | -0.18768 | 0.082398 | 0.25177 | -0.19684 | -0.22888 | -0.23804 | -0.27008 | 0.004578 | -0.18768 | 0.018311 | 0.10071 | 0.018311 | -0.10986 | 0.013733 | -0.11444 | 0.21057 | 122.1542 | 0.09613 | 122.1268 | 121.8842 | 121.9208 | 121.9254 | 121.9254 | -122.0718 | -122.1085 | 122.1954 | 122.1313 | 62.2833 | 62.3611
529.5469 | 122.2321 | -62.2742 | 59.8389 | -0.021286 | 0.0001345 | 0.061171 | 0.058821 | 0.0025678 | -0.0051291 | -0.0031895 | -0.011261 | 0.0040802 | 0.073006 | 0.060569 | -0.0092371 | 0.017944 | -0.0003568 | -0.004578 | 59.6329 | -62.2833 | 59.8434 | -62.0911 | -62.5442 | -62.5168 | 0.018311 | 59.642 | -62.3062 | 59.7839 | -62.2101 | -62.4023 | -62.3108 | -0.009155 | -0.20599 | 0.004578 | 0.18311 | -0.24262 | -0.27008 | -0.23346 | -0.26093 | -0.032043 | -0.19684 | -0.054931 | 0.064087 | -0.036621 | -0.12817 | -0.004578 | -0.096131 | 0.19226 | 122.1268 | 0.09613 | 122.0901 | 121.9162 | 121.9482 | 121.907 | 121.9162 | -122.1222 | -122.1451 | 122.1176 | 122.0581 | 62.2696 | 62.2925
531.2812 | 122.3465 | -62.2604 | 59.7702 | -0.0060272 | 0.0001345 | 0.06053 | 0.054762 | -0.0017048 | -0.0051291 | -0.0031895 | -0.0021057 | 0.001303 | 0.071297 | 0.066977 | -0.0088097 | 0.016876 | 0.0011386 | -0.009155 | 59.5779 | -62.2559 | 59.9258 | -61.972 | -62.439 | -62.4252 | 0.13733 | 59.5642 | -62.3016 | 59.8984 | -62.1002 | -62.2879 | -62.3062 | 0.004578 | -0.19226 | 0.15564 | 0.28839 | -0.16479 | -0.17853 | -0.16937 | -0.18311 | -0.041199 | -0.20599 | 0.12817 | 0.16022 | -0.045776 | -0.027466 | -0.004577 | 0.013733 | 0.28381 | 122.1817 | 0.20142 | 122.2 | 121.8338 | 121.8658 | 121.8384 | 121.8246 | -122.0261 | -122.0718 | 122.1863 | 122.1588 | 62.2513 | 62.3978
533.0312 | 122.2549 | -62.2696 | 59.8022 | -0.013657 | 0.0035525 | 0.060103 | 0.060103 | -0.0017048 | -0.0049155 | -0.0010531 | -0.0021057 | 0.0032256 | 0.072792 | 0.070395 | -0.0094507 | 0.017303 | 0.0004978 | -0.018311 | 59.6191 | -62.2787 | 59.8846 | -62.0316 | -62.5214 | -62.5122 | 0.036621 | 59.6146 | -62.3154 | 59.8022 | -62.2375 | -62.4207 | -62.3932 | -0.009156 | -0.1831 | 0.082398 | 0.23804 | -0.24261 | -0.25177 | -0.23346 | -0.24261 | -0.045777 | -0.18768 | 0 | 0.032043 | -0.1236 | -0.15106 | -0.077819 | -0.10529 | 0.24719 | 122.1634 | 0.07782 | 122.1176 | 121.8979 | 121.9299 | 121.8887 | 121.8842 | -122.081 | -122.1176 | 122.1542 | 122.0718 | 62.2513 | 62.3062
534.7188 | 122.374 | -62.265 | 59.7794 | -0.0060272 | -0.0015743 | 0.058821 | 0.058607 | 4.192e-06 | -0.0059835 | -0.0021213 | -0.0051575 | 0.0010894 | 0.070015 | 0.062278 | -0.0090235 | 0.015167 | -0.0044156 | 0.009155 | 59.5779 | -62.2421 | 59.9442 | -61.9308 | -62.4298 | -62.4069 | 0.15106 | 59.5734 | -62.2787 | 59.903 | -62.0819 | -62.2559 | -62.2787 | 0.022889 | -0.20142 | 0.16479 | 0.33417 | -0.14191 | -0.1648 | -0.16479 | -0.18768 | -0.013733 | -0.20599 | 0.1236 | 0.18311 | -0.013733 | 0.009156 | 0 | 0.022889 | 0.31128 | 122.1863 | 0.19684 | 122.1817 | 121.8201 | 121.8521 | 121.843 | 121.8384 | -122.0215 | -122.0581 | 122.2092 | 122.168 | 62.2742 | 62.4161
536.4531 | 122.2549 | -62.2696 | 59.8343 | 0.0016023 | 0.0001345 | 0.060316 | 0.059248 | -0.0046954 | -0.0057699 | -0.0019077 | -0.0051575 | 0.0021576 | 0.074501 | 0.067832 | -0.0096643 | 0.017731 | -0.0037748 | 0.059509 | 59.5825 | -62.265 | 59.935 | -61.9858 | -62.4573 | -62.439 | 0.11444 | 59.642 | -62.3016 | 59.8114 | -62.178 | -62.384 | -62.3749 | 0.004577 | -0.25177 | 0.10071 | 0.28381 | -0.16937 | -0.18768 | -0.17395 | -0.19226 | -0.032044 | -0.19226 | -0.022889 | 0.091552 | -0.10529 | -0.11444 | -0.073242 | -0.082397 | 0.27924 | 122.2 | 0.1236 | 122.113 | 121.8475 | 121.9437 | 121.8521 | 121.9116 | -122.0993 | -122.1359 | 122.2046 | 122.081 | 62.3291 | 62.384
538.2031 | 122.2595 | -62.2604 | 59.8572 | -0.013657 | -0.0011471 | 0.060316 | 0.060316 | -0.0010638 | -0.0057699 | -0.00041227 | -0.0021057 | 0.0025848 | 0.072365 | 0.063559 | -0.0092371 | 0.017517 | -0.0003568 | -0.004578 | 59.642 | -62.2513 | 59.8434 | -62.1002 | -62.5442 | -62.5442 | 0.013733 | 59.6558 | -62.3245 | 59.8114 | -62.2055 | -62.3932 | -62.3978 | 0.009155 | -0.21515 | -0.013733 | 0.16022 | -0.28381 | -0.28381 | -0.29297 | -0.29297 | -0.064087 | -0.20142 | -0.045777 | 0.054932 | -0.13733 | -0.13275 | -0.073242 | -0.068664 | 0.15106 | 122.0947 | 0.11902 | 122.1359 | 121.8933 | 121.9803 | 121.9025 | 121.9162 | -122.1085 | -122.1817 | 122.1039 | 122.0718 | 62.2559 | 62.2742
539.8906 | 122.3602 | -62.2879 | 59.729 | -0.021286 | 0.0020571 | 0.060103 | 0.057753 | -0.00020941 | -0.0034201 | -0.0014805 | -0.0021057 | 0.0027984 | 0.073219 | 0.069754 | -0.0098779 | 0.016449 | -0.0001432 | -0.07782 | 59.5688 | -62.2879 | 59.903 | -61.9949 | -62.5031 | -62.4756 | 0.045776 | 59.5505 | -62.3337 | 59.8709 | -62.1689 | -62.3474 | -62.3428 | 0 | -0.16022 | 0.17395 | 0.29297 | -0.18768 | -0.21515 | -0.18768 | -0.21515 | -0.045776 | -0.17853 | 0.14191 | 0.11902 | -0.054931 | -0.059509 | -0.009155 | -0.013733 | 0.29297 | 122.1909 | 0.16479 | 122.2046 | 121.8567 | 121.8842 | 121.8567 | 121.8384 | -122.0169 | -122.0627 | 122.1909 | 122.1588 | 62.2101 | 62.3337
541.6406 | 122.2366 | -62.2971 | 59.8618 | 0.0016023 | -0.0002927 | 0.059676 | 0.059462 | 0.0017132 | -0.0079061 | -0.0038303 | -0.0021057 | 0.0021576 | 0.071938 | 0.071677 | -0.0092371 | 0.017517 | -0.0022794 | 0.004578 | 59.6329 | -62.2742 | 59.8434 | -62.1002 | -62.5305 | -62.5305 | 0.009155 | 59.6649 | -62.2925 | 59.7748 | -62.2238 | -62.4161 | -62.4207 | 0.022888 | -0.22888 | -0.01831 | 0.19684 | -0.23346 | -0.23346 | -0.25635 | -0.25635 | 0.004578 | -0.19684 | -0.086975 | 0.073242 | -0.1236 | -0.11902 | -0.12817 | -0.1236 | 0.17395 | 122.1176 | 0.068664 | 122.0673 | 121.907 | 121.9574 | 121.9299 | 121.962 | -122.1359 | -122.1542 | 122.1405 | 122.0718 | 62.3016 | 62.3062
543.375 | 122.2549 | -62.2971 | 59.8022 | -0.013657 | 0.0024845 | 0.061385 | 0.060744 | 0.0051312 | -0.0040609 | -0.00083947 | -0.0051575 | 0.0034392 | 0.074287 | 0.063773 | -0.0092371 | 0.016663 | 0.0019932 | 0 | 59.61 | -62.2787 | 59.8846 | -62.0361 | -62.5031 | -62.5031 | 0.07782 | 59.6329 | -62.2971 | 59.8343 | -62.1964 | -62.3611 | -62.3795 | 0.01831 | -0.19226 | 0.082398 | 0.26093 | -0.20599 | -0.20599 | -0.2243 | -0.2243 | 0 | -0.16937 | 0.032044 | 0.10071 | -0.082398 | -0.064087 | -0.082398 | -0.064087 | 0.24262 | 122.1634 | 0.10071 | 122.1313 | 121.8887 | 121.9299 | 121.907 | 121.9299 | -122.081 | -122.0993 | 122.1817 | 122.1313 | 62.2971 | 62.3749
545.125 | 122.2961 | -62.2879 | 59.7931 | -0.013657 | -0.0011471 | 0.059676 | 0.057539 | -0.0042682 | -0.0061971 | -0.0012669 | -0.0021057 | -0.0010468 | 0.07151 | 0.066977 | -0.0085961 | 0.017303 | -0.000784 | -0.09613 | 59.5596 | -62.2879 | 59.8938 | -62.027 | -62.5076 | -62.471 | -0.009155 | 59.5642 | -62.3199 | 59.8114 | -62.2147 | -62.352 | -62.3795 | 0 | -0.23346 | 0.10071 | 0.26093 | -0.1831 | -0.21973 | -0.1831 | -0.21973 | -0.032043 | -0.22888 | 0.01831 | 0.073242 | -0.091553 | -0.064087 | -0.05951 | -0.032044 | 0.26093 | 122.1817 | 0.10529 | 122.1313 | 121.8475 | 121.8842 | 121.8475 | 121.8521 | -122.081 | -122.113 | 122.1817 | 122.0993 | 62.1918 | 62.2787
546.8125 | 122.2137 | -62.3199 | 59.7931 | -0.0060272 | 0.0020571 | 0.06053 | 0.061171 | 0.0034222 | -0.0049155 | -0.0036167 | -0.0021057 | 0.0023712 | 0.073647 | 0.072745 | -0.0085961 | 0.017731 | -0.0016384 | -0.11902 | 59.6054 | -62.2925 | 59.7931 | -62.1552 | -62.6129 | -62.59 | -0.082397 | 59.6054 | -62.3337 | 59.7519 | -62.2833 | -62.4939 | -62.4619 | 0.027466 | -0.18768 | 0 | 0.1648 | -0.27008 | -0.29297 | -0.29755 | -0.32044 | -0.013733 | -0.18768 | -0.041199 | 0.036621 | -0.14191 | -0.17395 | -0.12817 | -0.16022 | 0.13733 | 122.0856 | 0.050354 | 122.0856 | 121.8979 | 121.9391 | 121.9254 | 121.9254 | -122.0856 | -122.1268 | 122.113 | 122.0718 | 62.2009 | 62.2375
548.5469 | 122.287 | -62.2879 | 59.7656 | 0.0016023 | 0.0024845 | 0.061385 | 0.060744 | -0.00085021 | -0.0036337 | -0.0027621 | -0.0051575 | 0.0025848 | 0.07151 | 0.070182 | -0.0081689 | 0.019012 | -0.0012112 | -0.14648 | 59.6283 | -62.2971 | 59.8206 | -62.1185 | -62.5809 | -62.5626 | -0.059509 | 59.5963 | -62.3245 | 59.8022 | -62.2284 | -62.4207 | -62.4115 | -0.009155 | -0.13733 | 0.054932 | 0.16937 | -0.27466 | -0.29297 | -0.2655 | -0.28381 | -0.036621 | -0.16937 | 0.036621 | 0.059509 | -0.1236 | -0.13275 | -0.086975 | -0.09613 | 0.17853 | 122.1176 | 0.09613 | 122.1268 | 121.9254 | 121.9208 | 121.9162 | 121.8842 | -122.0627 | -122.0901 | 122.1085 | 122.0901 | 62.1414 | 62.2284
550.2188 | 122.3236 | -62.2559 | 59.7885 | 0.0016023 | 0.0003483 | 0.060957 | 0.058821 | 0.0021406 | -0.0061971 | 0.00065573 | -0.0021057 | 0.00023504 | 0.070442 | 0.063559 | -0.0096643 | 0.01709 | -0.0014248 | 0.059509 | 59.5779 | -62.265 | 59.9579 | -61.9537 | -62.4298 | -62.4252 | 0.14191 | 59.5917 | -62.2742 | 59.8709 | -62.114 | -62.2879 | -62.3199 | -0.009156 | -0.21057 | 0.16937 | 0.30212 | -0.16937 | -0.17395 | -0.16022 | -0.1648 | -0.018311 | -0.19684 | 0.082398 | 0.14191 | -0.064087 | -0.032044 | -0.045776 | -0.013733 | 0.31128 | 122.2229 | 0.16022 | 122.1451 | 121.843 | 121.8658 | 121.8338 | 121.8475 | -122.0535 | -122.0627 | 122.2137 | 122.1268 | 62.3154 | 62.3978
551.9844 | 122.3373 | -62.2559 | 59.7839 | -0.0060272 | -0.0005063 | 0.060744 | 0.057112 | 0.0010724 | -0.0066245 | -0.0034031 | -0.0021057 | 0.0027984 | 0.072792 | 0.063987 | -0.0098779 | 0.018372 | -0.0009976 | 0.041199 | 59.5596 | -62.2467 | 59.9533 | -61.9583 | -62.439 | -62.4252 | 0.14191 | 59.6054 | -62.2787 | 59.8663 | -62.1277 | -62.3199 | -62.3199 | 0.009155 | -0.2243 | 0.16937 | 0.29755 | -0.16937 | -0.18311 | -0.17853 | -0.19226 | -0.022889 | -0.17853 | 0.082397 | 0.12817 | -0.064087 | -0.064087 | -0.041198 | -0.041198 | 0.28839 | 122.2 | 0.15106 | 122.1451 | 121.8063 | 121.8842 | 121.8155 | 121.8613 | -122.0306 | -122.0627 | 122.2092 | 122.1222 | 62.2971 | 62.3978
553.7188 | 122.3373 | -62.265 | 59.7931 | -0.0060272 | -0.0002927 | 0.059248 | 0.057539 | -0.0023456 | -0.0053427 | -0.0027621 | -0.0051575 | 0.00044864 | 0.073006 | 0.058432 | -0.0081689 | 0.016663 | -0.0005704 | 0.045776 | 59.5734 | -62.2742 | 59.9579 | -61.9263 | -62.4069 | -62.4115 | 0.16479 | 59.5917 | -62.2696 | 59.8755 | -62.1002 | -62.2696 | -62.2971 | -0.009155 | -0.21973 | 0.1648 | 0.33874 | -0.14648 | -0.14191 | -0.13733 | -0.13275 | -0.004577 | -0.20142 | 0.082397 | 0.16479 | -0.032043 | -0.004577 | -0.027466 | 0 | 0.3479 | 122.2321 | 0.16937 | 122.1451 | 121.8475 | 121.8613 | 121.8384 | 121.8567 | -122.0673 | -122.0627 | 122.2229 | 122.1405 | 62.3108 | 62.4298
555.4688 | 122.3557 | -62.2284 | 59.761 | 0.0016023 | -0.0005063 | 0.059462 | 0.057967 | -0.0010638 | -0.0083335 | 0.00022853 | 0.0009461 | 0.0025848 | 0.071083 | 0.060569 | -0.010946 | 0.015381 | -0.0020658 | 0.032043 | 59.5551 | -62.2742 | 59.9762 | -61.9217 | -62.4115 | -62.4023 | 0.16022 | 59.6008 | -62.2696 | 59.8755 | -62.1002 | -62.265 | -62.3062 | -0.045776 | -0.20599 | 0.21515 | 0.3067 | -0.17395 | -0.1831 | -0.12817 | -0.13733 | -0.041198 | -0.16022 | 0.11444 | 0.12817 | -0.077819 | -0.036621 | -0.036621 | 0.004577 | 0.35248 | 122.2504 | 0.16937 | 122.1451 | 121.8292 | 121.8704 | 121.7834 | 121.8292 | -122.0352 | -122.0306 | 122.2046 | 122.1039 | 62.2604 | 62.3886
557.2344 | 122.3694 | -62.2604 | 59.7748 | -0.0060272 | 0.0007755 | 0.060957 | 0.057539 | -0.0027728 | -0.0057699 | -0.0038303 | -0.0021057 | -0.00019216 | 0.071938 | 0.061209 | -0.0088097 | 0.016235 | 7.04e-05 | 0.022888 | 59.5642 | -62.2284 | 59.9533 | -61.9217 | -62.4161 | -62.4023 | 0.19684 | 59.5779 | -62.2604 | 59.8892 | -62.1048 | -62.2742 | -62.2971 | 0.032043 | -0.21057 | 0.17853 | 0.33875 | -0.14191 | -0.15564 | -0.17395 | -0.18768 | 0 | -0.19684 | 0.11444 | 0.15564 | -0.036621 | -0.013733 | -0.036621 | -0.013733 | 0.3067 | 122.1817 | 0.15564 | 122.1497 | 121.7926 | 121.8384 | 121.8246 | 121.8384 | -122.0032 | -122.0352 | 122.2137 | 122.1497 | 62.2833 | 62.4573
558.9062 | 122.2229 | -62.2787 | 59.8434 | -0.0060272 | -0.0009335 | 0.059248 | 0.06053 | -0.0053362 | -0.0053427 | -0.0014805 | -0.0051575 | 0.0038666 | 0.071724 | 0.068473 | -0.0098779 | 0.018158 | -0.0031338 | -0.018311 | 59.6237 | -62.2604 | 59.8343 | -62.0865 | -62.5305 | -62.5214 | 0.032043 | 59.6695 | -62.3016 | 59.7702 | -62.2375 | -62.4115 | -62.4069 | 0.018311 | -0.21973 | -0.009155 | 0.19226 | -0.24261 | -0.25177 | -0.26093 | -0.27008 | -0.022888 | -0.17395 | -0.073242 | 0.041199 | -0.12817 | -0.13275 | -0.10528 | -0.10986 | 0.17395 | 122.0947 | 0.064087 | 122.0718 | 121.8842 | 121.9711 | 121.9025 | 121.9482 | -122.1039 | -122.1451 | 122.113 | 122.049 | 62.2604 | 62.3108
560.6562 | 122.3053 | -62.2742 | 59.7702 | -0.013657 | -0.0002927 | 0.06053 | 0.057539 | 0.0021406 | -0.0040609 | -0.0019077 | -0.0021057 | -0.00019216 | 0.074287 | 0.069754 | -0.0068871 | 0.01709 | 0.0015658 | -0.086975 | 59.6054 | -62.2925 | 59.8709 | -62.059 | -62.5259 | -62.4985 | 0 | 59.5963 | -62.3291 | 59.8068 | -62.2101 | -62.384 | -62.3657 | -0.01831 | -0.1648 | 0.10071 | 0.21515 | -0.2243 | -0.25177 | -0.20599 | -0.23346 | -0.054932 | -0.17395 | 0.036621 | 0.064087 | -0.091553 | -0.10986 | -0.036621 | -0.054931 | 0.23346 | 122.1634 | 0.11902 | 122.1359 | 121.8979 | 121.9254 | 121.8796 | 121.8704 | -122.0627 | -122.0993 | 122.1451 | 122.081 | 62.1872 | 62.2742
562.4062 | 122.3145 | -62.2742 | 59.7519 | -0.013657 | 0.0018435 | 0.059462 | 0.057753 | -0.0023456 | -0.0049155 | -0.0029759 | -0.0021057 | 0.0021576 | 0.071297 | 0.063559 | -0.0077417 | 0.016022 | -0.0009976 | -0.07782 | 59.5688 | -62.2742 | 59.8572 | -62.0407 | -62.5122 | -62.4939 | 0.018311 | 59.5825 | -62.2879 | 59.848 | -62.1735 | -62.3428 | -62.3428 | 0 | -0.1831 | 0.10529 | 0.23346 | -0.21973 | -0.23804 | -0.21973 | -0.23804 | -0.013733 | -0.16937 | 0.09613 | 0.10071 | -0.068664 | -0.068664 | -0.054931 | -0.054931 | 0.23346 | 122.1313 | 0.11444 | 122.1359 | 121.843 | 121.8704 | 121.843 | 121.8567 | -122.0261 | -122.0398 | 122.1313 | 122.1222 | 62.1963 | 62.2925
564.1406 | 122.3236 | -62.2421 | 59.8068 | -0.0060272 | -0.0005063 | 0.059889 | 0.058607 | -0.0019184 | -0.0070517 | -0.0019077 | -0.0021057 | 0.0017304 | 0.068947 | 0.065268 | -0.0088097 | 0.018158 | -0.002493 | 0.045776 | 59.5596 | -62.2559 | 59.9625 | -61.9354 | -62.4161 | -62.4023 | 0.16937 | 59.5825 | -62.2925 | 59.8938 | -62.1048 | -62.2787 | -62.3016 | -0.013733 | -0.24719 | 0.15564 | 0.3067 | -0.16022 | -0.17395 | -0.14648 | -0.16022 | -0.050354 | -0.2243 | 0.086975 | 0.13733 | -0.05951 | -0.036622 | -0.009156 | 0.013732 | 0.32043 | 122.2183 | 0.18768 | 122.1863 | 121.8155 | 121.875 | 121.8018 | 121.8246 | -122.0627 | -122.0993 | 122.2046 | 122.1359 | 62.2879 | 62.4115
565.8125 | 122.2595 | -62.2559 | 59.7931 | -0.013657 | 0.0009891 | 0.06053 | 0.062666 | 0.0025678 | -0.0074789 | -0.0029759 | -0.0051575 | 0.0051482 | 0.073006 | 0.058646 | -0.0083825 | 0.016449 | -0.006979 | -0.004578 | 59.5917 | -62.2513 | 59.8938 | -62.0316 | -62.5214 | -62.4985 | 0.07782 | 59.6466 | -62.3245 | 59.8297 | -62.2009 | -62.3886 | -62.3657 | 0.004577 | -0.20142 | 0.10071 | 0.2243 | -0.24262 | -0.2655 | -0.24719 | -0.27008 | -0.068665 | -0.14648 | 0.036621 | 0.054931 | -0.10986 | -0.13275 | -0.041199 | -0.064087 | 0.21973 | 122.1451 | 0.1236 | 122.1542 | 121.843 | 121.9711 | 121.8475 | 121.9025 | -122.0444 | -122.1176 | 122.1497 | 122.0856 | 62.2513 | 62.3337
567.5781 | 122.3511 | -62.2879 | 59.7656 | -0.0060272 | -0.0024289 | 0.059676 | 0.057112 | -0.0025592 | -0.0081197 | -0.0021213 | -0.0021057 | 2.1442e-05 | 0.070442 | 0.062064 | -0.0088097 | 0.014954 | -0.0065518 | -0.054932 | 59.5917 | -62.265 | 59.9167 | -62.0224 | -62.4664 | -62.4527 | 0.073242 | 59.5917 | -62.3016 | 59.8663 | -62.1277 | -62.2925 | -62.2971 | 0.022888 | -0.17395 | 0.15106 | 0.2655 | -0.16479 | -0.17853 | -0.18768 | -0.20142 | -0.013733 | -0.17395 | 0.10071 | 0.16022 | -0.009155 | -0.004577 | 0.004578 | 0.009156 | 0.24262 | 122.1817 | 0.17395 | 122.168 | 121.8567 | 121.8933 | 121.8796 | 121.8796 | -122.0306 | -122.0673 | 122.2046 | 122.1542 | 62.233 | 62.3611
569.2656 | 122.2137 | -62.2833 | 59.7839 | -0.013657 | 0.0005619 | 0.062239 | 0.059889 | -0.0023456 | -0.0076925 | -0.00083947 | -0.0021057 | 0.0045074 | 0.072151 | 0.065909 | -0.0085961 | 0.016022 | -0.0027066 | -0.032043 | 59.6191 | -62.2742 | 59.8892 | -62.0499 | -62.5397 | -62.5168 | 0.036621 | 59.6375 | -62.3154 | 59.7977 | -62.233 | -62.439 | -62.4023 | 0.009155 | -0.16479 | 0.10529 | 0.23346 | -0.23346 | -0.25635 | -0.24262 | -0.2655 | -0.032044 | -0.14648 | 0.013732 | 0.050354 | -0.11902 | -0.15564 | -0.086975 | -0.1236 | 0.2243 | 122.1634 | 0.082398 | 122.113 | 121.8933 | 121.9528 | 121.9025 | 121.9208 | -122.0581 | -122.0993 | 122.1725 | 122.081 | 62.2513 | 62.3199
571.0156 | 122.3373 | -62.2696 | 59.7839 | -0.0060272 | -0.0030697 | 0.060744 | 0.056898 | -0.0027728 | -0.0044883 | -0.0023349 | -0.0021057 | 0.00023504 | 0.073006 | 0.062491 | -0.0096643 | 0.016022 | -0.0012112 | 0.045776 | 59.6054 | -62.2742 | 59.9762 | -61.9492 | -62.4069 | -62.4069 | 0.14648 | 59.5688 | -62.2696 | 59.8801 | -62.1185 | -62.2971 | -62.3154 | -0.004578 | -0.17853 | 0.19226 | 0.32043 | -0.13733 | -0.13733 | -0.13275 | -0.13275 | 0 | -0.21515 | 0.09613 | 0.15106 | -0.045777 | -0.027466 | -0.045777 | -0.027466 | 0.32501 | 122.2504 | 0.15106 | 122.1497 | 121.8796 | 121.8384 | 121.875 | 121.8384 | -122.0581 | -122.0535 | 122.2458 | 122.1497 | 62.3154 | 62.4161
572.7656 | 122.2137 | -62.2925 | 59.8251 | 0.0016023 | 0.0039799 | 0.060316 | 0.059462 | 0.0021406 | -0.0055563 | -0.0019077 | -0.0021057 | 0.0032256 | 0.071938 | 0.066123 | -0.0090235 | 0.016663 | -0.000784 | -0.045776 | 59.61 | -62.2833 | 59.8572 | -62.0728 | -62.5763 | -62.5397 | -0.009155 | 59.6283 | -62.3337 | 59.7794 | -62.2467 | -62.4573 | -62.4435 | 0.009155 | -0.21515 | 0.032044 | 0.21973 | -0.24719 | -0.28381 | -0.25635 | -0.29297 | -0.041199 | -0.19684 | -0.045776 | 0.045776 | -0.15106 | -0.1648 | -0.10986 | -0.1236 | 0.21057 | 122.1405 | 0.086975 | 122.113 | 121.8933 | 121.962 | 121.9025 | 121.9208 | -122.1085 | -122.1588 | 122.1497 | 122.0718 | 62.2467 | 62.2833
574.5156 | 122.2183 | -62.3062 | 59.7885 | -0.0060272 | 0.0039799 | 0.062239 | 0.060316 | 0.0023542 | -0.0051291 | -0.0031895 | -0.0021057 | 0.0040802 | 0.073219 | 0.059501 | -0.0077417 | 0.019012 | 0.0007114 | -0.11444 | 59.6283 | -62.3154 | 59.8114 | -62.146 | -62.6129 | -62.6038 | -0.07782 | 59.6191 | -62.3199 | 59.761 | -62.2925 | -62.4756 | -62.4527 | -0.009156 | -0.16022 | 0.022888 | 0.16022 | -0.29755 | -0.3067 | -0.28839 | -0.29755 | -0.013733 | -0.16937 | -0.027466 | 0.013733 | -0.14648 | -0.16937 | -0.13275 | -0.15564 | 0.16937 | 122.1268 | 0.027466 | 122.081 | 121.9437 | 121.9391 | 121.9345 | 121.9254 | -122.1039 | -122.1085 | 122.1176 | 122.0673 | 62.1918 | 62.2284
576.2031 | 122.2412 | -62.2971 | 59.8114 | 0.0016023 | 0.0037661 | 0.060744 | 0.059248 | 0.0025678 | -0.0051291 | -0.0036167 | -0.0021057 | 0.0025848 | 0.073647 | 0.066336 | -0.0085961 | 0.01709 | -0.0001432 | -0.027466 | 59.6237 | -62.2742 | 59.8892 | -62.0361 | -62.5122 | -62.5076 | 0.054932 | 59.6329 | -62.3199 | 59.8114 | -62.2147 | -62.4115 | -62.4069 | 0.022888 | -0.18768 | 0.07782 | 0.26093 | -0.21057 | -0.21515 | -0.23346 | -0.23804 | -0.022888 | -0.17853 | 0 | 0.082397 | -0.10986 | -0.11444 | -0.086975 | -0.091553 | 0.23804 | 122.1634 | 0.10529 | 122.1313 | 121.8979 | 121.9528 | 121.9208 | 121.9299 | -122.0856 | -122.1313 | 122.1863 | 122.1085 | 62.2696 | 62.352
577.9688 | 122.2275 | -62.2787 | 59.8251 | -0.0060272 | -0.0005063 | 0.059462 | 0.058394 | -0.0046954 | -0.0051291 | 0.00022853 | 0.0009461 | 0.0023712 | 0.071938 | 0.064841 | -0.0064599 | 0.015381 | -0.0031338 | 0.032043 | 59.61 | -62.2879 | 59.8572 | -62.0453 | -62.5076 | -62.5031 | 0.036621 | 59.6649 | -62.3108 | 59.7748 | -62.2147 | -62.3978 | -62.439 | -0.009155 | -0.21515 | 0.032044 | 0.23346 | -0.2243 | -0.22888 | -0.21515 | -0.21973 | -0.032043 | -0.16022 | -0.050354 | 0.064087 | -0.16022 | -0.11902 | -0.12817 | -0.086975 | 0.24262 | 122.1451 | 0.09613 | 122.0856 | 121.8979 | 121.9757 | 121.8887 | 121.9437 | -122.113 | -122.1359 | 122.1359 | 122.0535 | 62.3108 | 62.3154
579.6562 | 122.3694 | -62.2559 | 59.7565 | -0.013657 | -0.0002927 | 0.06053 | 0.056685 | -0.0027728 | -0.0072653 | -0.0012669 | -0.0051575 | 0.0015166 | 0.072792 | 0.060569 | -0.0085961 | 0.01709 | -0.0037748 | 0.018311 | 59.5505 | -62.2879 | 59.9579 | -61.9354 | -62.4252 | -62.4069 | 0.16022 | 59.5779 | -62.2833 | 59.9075 | -62.0819 | -62.2742 | -62.2925 | -0.032044 | -0.20599 | 0.20142 | 0.32043 | -0.15106 | -0.16937 | -0.11902 | -0.13733 | -0.027466 | -0.17853 | 0.15106 | 0.17395 | -0.036621 | -0.018311 | -0.009155 | 0.009155 | 0.35248 | 122.2458 | 0.20142 | 122.1909 | 121.8384 | 121.8613 | 121.8063 | 121.8338 | -122.0444 | -122.0398 | 122.2137 | 122.1634 | 62.2742 | 62.4161
581.3906 | 122.2366 | -62.2879 | 59.8343 | -0.0060272 | 0.0016299 | 0.059035 | 0.059248 | -0.00085021 | -0.0055563 | -0.00062587 | -0.0051575 | 0.001944 | 0.072365 | 0.063559 | -0.0079553 | 0.017944 | 0.0022068 | -0.013733 | 59.6649 | -62.2696 | 59.8251 | -62.0865 | -62.5351 | -62.5351 | 0.018311 | 59.6649 | -62.3016 | 59.7977 | -62.2101 | -62.4023 | -62.4023 | 0.018311 | -0.16937 | -0.009156 | 0.20142 | -0.24719 | -0.24719 | -0.2655 | -0.2655 | -0.013733 | -0.16937 | -0.036622 | 0.07782 | -0.11444 | -0.11444 | -0.10071 | -0.10071 | 0.18311 | 122.0947 | 0.091553 | 122.0993 | 121.9345 | 121.9666 | 121.9528 | 121.9528 | -122.1039 | -122.1359 | 122.113 | 122.0856 | 62.2742 | 62.3062
583.1406 | 122.2 | -62.3199 | 59.8114 | -0.013657 | 0.0046207 | 0.062239 | 0.060957 | 0.0017132 | -0.0076925 | -0.0031895 | -0.0021057 | 0.0040802 | 0.072151 | 0.066764 | -0.0098779 | 0.019226 | -0.003561 | -0.064087 | 59.6283 | -62.2879 | 59.8434 | -62.114 | -62.5992 | -62.5763 | -0.059509 | 59.642 | -62.3337 | 59.7519 | -62.2742 | -62.4893 | -62.4252 | 0.032043 | -0.1831 | 0.032044 | 0.20599 | -0.25635 | -0.27924 | -0.28839 | -0.31128 | -0.013733 | -0.16937 | -0.059509 | 0.045776 | -0.10529 | -0.16937 | -0.091553 | -0.15564 | 0.17395 | 122.1313 | 0.059509 | 122.0856 | 121.9162 | 121.9757 | 121.9482 | 121.962 | -122.0993 | -122.1451 | 122.1634 | 122.0718 | 62.2559 | 62.2604
584.8281 | 122.2229 | -62.2604 | 59.8526 | -0.0060272 | -7.9104e-05 | 0.057539 | 0.058394 | -0.0019184 | -0.0057699 | -0.0016941 | 0.0009461 | 0.001303 | 0.072578 | 0.065909 | -0.0079553 | 0.017517 | -0.0001432 | -0.013733 | 59.6375 | -62.2604 | 59.8251 | -62.1002 | -62.5259 | -62.5397 | 0.027466 | 59.6695 | -62.2925 | 59.7794 | -62.2238 | -62.4069 | -62.3932 | 0 | -0.21515 | -0.027466 | 0.16022 | -0.27924 | -0.2655 | -0.27924 | -0.2655 | -0.032043 | -0.18311 | -0.073242 | 0.036621 | -0.13275 | -0.14648 | -0.10071 | -0.11444 | 0.16022 | 122.0856 | 0.068664 | 122.0718 | 121.8979 | 121.962 | 121.8979 | 121.9299 | -122.113 | -122.1451 | 122.0856 | 122.0398 | 62.2467 | 62.2879
586.5625 | 122.2229 | -62.2696 | 59.8343 | -0.0060272 | 0.0037661 | 0.059676 | 0.06053 | 0.0038494 | -0.0068381 | -0.0031895 | -0.0051575 | 0.004721 | 0.072792 | 0.064627 | -0.0092371 | 0.018585 | -0.002493 | -0.036621 | 59.6146 | -62.2879 | 59.8755 | -62.0636 | -62.5305 | -62.5214 | 0.018311 | 59.6146 | -62.3291 | 59.7931 | -62.2513 | -62.4435 | -62.4115 | -0.018311 | -0.21973 | 0.041198 | 0.20599 | -0.25177 | -0.26093 | -0.23346 | -0.24262 | -0.05951 | -0.21973 | -0.041199 | 0.01831 | -0.14191 | -0.17395 | -0.082397 | -0.11444 | 0.2243 | 122.1634 | 0.07782 | 122.1222 | 121.9025 | 121.9437 | 121.8842 | 121.8842 | -122.1222 | -122.1634 | 122.1451 | 122.0627 | 62.233 | 62.2879
588.25 | 122.2092 | -62.3062 | 59.8022 | 0.0016023 | 0.0020571 | 0.061171 | 0.059035 | -0.00085021 | -0.0070517 | -0.0012669 | -0.0021057 | 0.0023712 | 0.072792 | 0.066977 | -0.0094507 | 0.018372 | -0.0005704 | -0.064087 | 59.6237 | -62.2787 | 59.8389 | -62.0682 | -62.5671 | -62.5442 | -0.018311 | 59.6375 | -62.3154 | 59.7656 | -62.2604 | -62.4664 | -62.4161 | 0.027465 | -0.17853 | 0.036621 | 0.23804 | -0.23804 | -0.26093 | -0.2655 | -0.28839 | -0.009156 | -0.16479 | -0.036621 | 0.045776 | -0.10986 | -0.16022 | -0.10071 | -0.15106 | 0.21057 | 122.1176 | 0.054932 | 122.081 | 121.9025 | 121.9528 | 121.9299 | 121.9437 | -122.081 | -122.1176 | 122.1451 | 122.0718 | 62.2421 | 62.2879
590 | 122.1954 | -62.3062 | 59.8068 | 0.0016023 | 0.0035525 | 0.062666 | 0.061598 | 0.001286 | -0.0044883 | -0.0019077 | -0.0021057 | 0.0034392 | 0.073006 | 0.067618 | -0.0068871 | 0.017517 | 0.0017794 | -0.10986 | 59.6375 | -62.2833 | 59.8068 | -62.1414 | -62.5992 | -62.59 | -0.082397 | 59.6283 | -62.3474 | 59.7382 | -62.3016 | -62.4939 | -62.4435 | 0.022888 | -0.16937 | 0 | 0.16479 | -0.28381 | -0.29297 | -0.3067 | -0.31586 | -0.041199 | -0.17853 | -0.068665 | 0.004577 | -0.13733 | -0.18768 | -0.09613 | -0.14648 | 0.14191 | 122.0901 | 0.045776 | 122.0856 | 121.9208 | 121.9757 | 121.9437 | 121.9345 | -122.0901 | -122.1542 | 122.113 | 122.0444 | 62.1964 | 62.2238
591.7344 | 122.3328 | -62.265 | 59.7382 | -0.013657 | 0.0012027 | 0.060316 | 0.059889 | -0.00020941 | -0.0038473 | -0.0025485 | -0.0021057 | 0.0032256 | 0.070229 | 0.058005 | -0.0073145 | 0.017731 | 0.0004978 | -0.15564 | 59.6054 | -62.2879 | 59.8297 | -62.0773 | -62.558 | -62.5442 | -0.009155 | 59.5779 | -62.3199 | 59.8389 | -62.1872 | -62.384 | -62.3199 | -0.022888 | -0.13275 | 0.091553 | 0.18768 | -0.27923 | -0.29297 | -0.25635 | -0.27008 | -0.054931 | -0.16022 | 0.10071 | 0.07782 | -0.054931 | -0.11902 | 0 | -0.064087 | 0.21057 | 122.1176 | 0.13275 | 122.1588 | 121.8933 | 121.8979 | 121.8704 | 121.843 | -122.0261 | -122.0581 | 122.0947 | 122.1039 | 62.1094 | 62.2559
593.4844 | 122.3557 | -62.2925 | 59.7382 | -0.013657 | 0.0037661 | 0.061812 | 0.05818 | 0.0040632 | -0.0047019 | -0.0031895 | -0.0021057 | 0.00066224 | 0.071297 | 0.069754 | -0.010732 | 0.018372 | -0.0027066 | -0.091553 | 59.5596 | -62.2742 | 59.8938 | -62.0132 | -62.4985 | -62.4756 | 0.045776 | 59.5459 | -62.3108 | 59.8572 | -62.1735 | -62.352 | -62.3108 | 0.01831 | -0.17853 | 0.15564 | 0.27923 | -0.18311 | -0.20599 | -0.20142 | -0.2243 | -0.018311 | -0.19226 | 0.11902 | 0.11902 | -0.018311 | -0.05951 | 0 | -0.041199 | 0.26093 | 122.168 | 0.13733 | 122.168 | 121.8338 | 121.8567 | 121.8521 | 121.8384 | -122.0123 | -122.049 | 122.1863 | 122.1497 | 62.2009 | 62.3383
595.1562 | 122.3099 | -62.2833 | 59.7519 | 0.0016023 | 0.0014163 | 0.060316 | 0.059248 | -0.0029864 | -0.0047019 | -0.0031895 | -0.0051575 | 0.00087584 | 0.072151 | 0.064627 | -0.0092371 | 0.01709 | -0.0012112 | -0.09613 | 59.5688 | -62.2787 | 59.8801 | -62.0132 | -62.5214 | -62.4802 | 0.032043 | 59.5459 | -62.3245 | 59.8343 | -62.1918 | -62.3657 | -62.3199 | 0.004577 | -0.1831 | 0.12817 | 0.27008 | -0.19684 | -0.23804 | -0.20142 | -0.24261 | -0.041199 | -0.20599 | 0.082398 | 0.091553 | -0.036621 | -0.082398 | 0.004578 | -0.041199 | 0.2655 | 122.1588 | 0.13275 | 122.1588 | 121.8475 | 121.8704 | 121.8521 | 121.8292 | -122.0306 | -122.0764 | 122.1634 | 122.1176 | 62.1872 | 62.3154
596.8906 | 122.2961 | -62.2742 | 59.7748 | -0.013657 | 0.0009891 | 0.061385 | 0.057112 | -0.002132 | -0.0053427 | 1.4934e-05 | 0.0009461 | 0.0015166 | 0.072151 | 0.056296 | -0.0090235 | 0.016663 | -0.0014248 | -0.082397 | 59.5688 | -62.2787 | 59.8572 | -62.0453 | -62.5076 | -62.4893 | 0.032043 | 59.6008 | -62.3062 | 59.816 | -62.1872 | -62.3611 | -62.3062 | -0.004578 | -0.20599 | 0.082398 | 0.22888 | -0.21515 | -0.23346 | -0.21057 | -0.22888 | -0.032043 | -0.17395 | 0.041199 | 0.086975 | -0.032043 | -0.086975 | 0 | -0.054932 | 0.23346 | 122.1359 | 0.11902 | 122.1222 | 121.8475 | 121.907 | 121.843 | 121.875 | -122.0535 | -122.081 | 122.1313 | 122.0901 | 62.1918 | 62.3062
598.6406 | 122.2183 | -62.3016 | 59.8114 | 0.016861 | 0.0031253 | 0.063094 | 0.062453 | -0.0029864 | -0.0047019 | -0.0019077 | 0.0009461 | 0.0034392 | 0.073219 | 0.06655 | -0.011373 | 0.018799 | -0.000784 | -0.059509 | 59.61 | -62.2787 | 59.8343 | -62.1048 | -62.5946 | -62.5626 | -0.050354 | 59.6375 | -62.3154 | 59.7748 | -62.265 | -62.4939 | -62.3657 | 0.022888 | -0.20142 | 0.022889 | 0.19684 | -0.26093 | -0.29297 | -0.28381 | -0.31586 | -0.013733 | -0.17395 | -0.036621 | 0.036621 | -0.064087 | -0.19226 | -0.050354 | -0.17853 | 0.17395 | 122.113 | 0.050354 | 122.0901 | 121.8887 | 121.9528 | 121.9116 | 121.9391 | -122.0901 | -122.1268 | 122.1359 | 122.0764 | 62.2421 | 62.2513
600.3906 | 122.2183 | -62.2833 | 59.8434 | -0.013657 | 0.0005619 | 0.058394 | 0.057326 | -0.0012774 | -0.0066245 | -0.0021213 | 0.0009461 | 0.0038666 | 0.07386 | 0.06655 | -0.0085961 | 0.015808 | -0.003561 | -0.032043 | 59.642 | -62.2696 | 59.8389 | -62.0865 | -62.5259 | -62.5397 | 0.018311 | 59.6832 | -62.3016 | 59.7656 | -62.2147 | -62.4115 | -62.3428 | 0.013733 | -0.20142 | -0.004578 | 0.19684 | -0.25635 | -0.24262 | -0.27008 | -0.25635 | -0.018311 | -0.16022 | -0.07782 | 0.068664 | -0.059509 | -0.12817 | -0.041198 | -0.10986 | 0.18311 | 122.1085 | 0.086975 | 122.0673 | 121.9116 | 121.9849 | 121.9254 | 121.9666 | -122.113 | -122.1451 | 122.1222 | 122.0489 | 62.2513 | 62.3016
602.1406 | 122.2321 | -62.3108 | 59.7702 | -0.0060272 | 0.0039799 | 0.060103 | 0.060316 | -0.0017048 | -0.0047019 | -0.0016941 | -0.0051575 | 0.001944 | 0.072578 | 0.065055 | -0.010305 | 0.017944 | -0.0001432 | -0.12817 | 59.6146 | -62.3108 | 59.7931 | -62.146 | -62.6221 | -62.59 | -0.09613 | 59.6283 | -62.352 | 59.7656 | -62.3016 | -62.4893 | -62.3703 | 0 | -0.15564 | 0.022888 | 0.1648 | -0.27924 | -0.31128 | -0.27924 | -0.31128 | -0.041199 | -0.14191 | -0.004578 | 0.009155 | -0.059509 | -0.17853 | -0.01831 | -0.13733 | 0.1648 | 122.1039 | 0.050354 | 122.1176 | 121.9254 | 121.9803 | 121.9254 | 121.9391 | -122.081 | -122.1222 | 122.1039 | 122.0764 | 62.1826 | 62.2147
603.9062 | 122.2275 | -62.3108 | 59.7931 | -0.0060272 | 0.0037661 | 0.062453 | 0.060316 | -0.00085021 | -0.0051291 | -0.0027621 | -0.0021057 | 0.0032256 | 0.072365 | 0.062491 | -0.0077417 | 0.018585 | -0.0009976 | -0.14648 | 59.642 | -62.2879 | 59.7931 | -62.146 | -62.6083 | -62.59 | -0.10529 | 59.6146 | -62.3337 | 59.761 | -62.2925 | -62.4802 | -62.3749 | 0.022888 | -0.15106 | 0 | 0.1648 | -0.27924 | -0.29755 | -0.30212 | -0.32043 | -0.022888 | -0.17853 | -0.032044 | 0.018311 | -0.064087 | -0.16937 | -0.041199 | -0.14649 | 0.14191 | 122.081 | 0.041199 | 122.0947 | 121.9299 | 121.9482 | 121.9528 | 121.9254 | -122.081 | -122.1268 | 122.1039 | 122.0718 | 62.1643 | 62.2055
605.6562 | 122.3145 | -62.2879 | 59.7519 | -0.0060272 | -0.0007199 | 0.060957 | 0.059676 | -0.003841 | -0.0061971 | -0.0036167 | -0.0082093 | 0.00044864 | 0.071297 | 0.057364 | -0.0085961 | 0.014526 | 0.0013522 | -0.10529 | 59.6008 | -62.2833 | 59.8526 | -62.0453 | -62.5031 | -62.4893 | 0.004578 | 59.6191 | -62.2925 | 59.7977 | -62.2055 | -62.3749 | -62.3383 | 0.004578 | -0.15106 | 0.10071 | 0.24262 | -0.20142 | -0.21515 | -0.20599 | -0.21973 | -0.004577 | -0.13275 | 0.045776 | 0.082398 | -0.050354 | -0.086975 | -0.045777 | -0.082398 | 0.23804 | 122.1359 | 0.086975 | 122.0901 | 121.8842 | 121.9116 | 121.8887 | 121.907 | -122.0352 | -122.0444 | 122.1405 | 122.0856 | 62.1826 | 62.2925
607.3281 | 122.2687 | -62.2879 | 59.8618 | -0.0060272 | 0.0020571 | 0.05818 | 0.060103 | 0.0010724 | -0.0061971 | -0.00083947 | -0.0051575 | 0.0025848 | 0.073647 | 0.067832 | -0.010305 | 0.017944 | -0.0044156 | -0.013733 | 59.642 | -62.2879 | 59.8434 | -62.1002 | -62.5259 | -62.5305 | 0.022888 | 59.6695 | -62.3154 | 59.7977 | -62.2147 | -62.3978 | -62.3566 | 0 | -0.21973 | -0.01831 | 0.18768 | -0.24262 | -0.23804 | -0.24262 | -0.23804 | -0.027466 | -0.19226 | -0.064087 | 0.073242 | -0.068664 | -0.10986 | -0.041198 | -0.082397 | 0.18768 | 122.1313 | 0.10071 | 122.113 | 121.9299 | 121.9849 | 121.9299 | 121.9574 | -122.1497 | -122.1771 | 122.1313 | 122.0856 | 62.2742 | 62.3108
609.0781 | 122.2733 | -62.2696 | 59.8297 | -0.0060272 | -0.0002927 | 0.059462 | 0.059248 | 0.00021799 | -0.0068381 | 0.00022853 | -0.0021057 | 0.0032256 | 0.072151 | 0.060569 | -0.0071009 | 0.016449 | -0.004202 | -0.004578 | 59.642 | -62.2559 | 59.8663 | -62.0544 | -62.4939 | -62.5076 | 0.027466 | 59.642 | -62.2787 | 59.8206 | -62.2009 | -62.3978 | -62.3611 | 0.013733 | -0.18768 | 0.036621 | 0.21515 | -0.23804 | -0.2243 | -0.25177 | -0.23804 | -0.009156 | -0.18768 | -0.009155 | 0.068664 | -0.091553 | -0.12817 | -0.082397 | -0.11902 | 0.20142 | 122.1222 | 0.07782 | 122.0993 | 121.8979 | 121.9208 | 121.9116 | 121.9116 | -122.0856 | -122.1085 | 122.1359 | 122.0901 | 62.265 | 62.2971
610.75 | 122.2137 | -62.3016 | 59.8206 | -0.0060272 | 0.0018435 | 0.061171 | 0.057967 | 0.0036358 | -0.0038473 | -0.0021213 | -0.0021057 | 0.0038666 | 0.072365 | 0.058646 | -0.0068871 | 0.018585 | 0.0032748 | -0.1236 | 59.642 | -62.3199 | 59.7794 | -62.1826 | -62.6221 | -62.6175 | -0.086975 | 59.6375 | -62.3291 | 59.7656 | -62.2925 | -62.4802 | -62.4344 | -0.01831 | -0.17853 | -0.041199 | 0.11902 | -0.31586 | -0.32043 | -0.29755 | -0.30212 | -0.027466 | -0.18311 | -0.054932 | 0.009156 | -0.13275 | -0.17853 | -0.10529 | -0.15106 | 0.13733 | 122.0993 | 0.036622 | 122.0947 | 121.962 | 121.9666 | 121.9437 | 121.9391 | -122.1405 | -122.1497 | 122.081 | 122.0673 | 62.178 | 62.2147
612.5 | 122.3602 | -62.2742 | 59.7748 | -0.0060272 | -0.0002927 | 0.058394 | 0.056258 | 0.001286 | -0.0074789 | 1.4934e-05 | -0.0051575 | 0.00066224 | 0.072365 | 0.065268 | -0.0090235 | 0.017303 | -0.0027066 | -0.018311 | 59.5734 | -62.2742 | 59.9121 | -61.9858 | -62.4252 | -62.439 | 0.1236 | 59.6054 | -62.3154 | 59.8801 | -62.1094 | -62.2787 | -62.3154 | 0 | -0.20142 | 0.13733 | 0.28839 | -0.1648 | -0.15106 | -0.1648 | -0.15106 | -0.041199 | -0.16937 | 0.10529 | 0.16479 | -0.041199 | -0.004578 | 0 | 0.036621 | 0.28839 | 122.1863 | 0.20599 | 122.1954 | 121.8475 | 121.9208 | 121.8475 | 121.8796 | -122.0489 | -122.0901 | 122.1863 | 122.1542 | 62.2559 | 62.3978
614.25 | 122.2366 | -62.3108 | 59.7885 | -0.0060272 | 0.0012027 | 0.061171 | 0.061385 | 0.0034222 | -0.0047019 | -0.0012669 | -0.0021057 | 0.0025848 | 0.071724 | 0.069327 | -0.010305 | 0.019012 | 0.0039158 | -0.15106 | 59.61 | -62.3108 | 59.8022 | -62.1368 | -62.6038 | -62.5809 | -0.07782 | 59.6191 | -62.3566 | 59.7656 | -62.265 | -62.471 | -62.439 | 0 | -0.17853 | 0.013733 | 0.17395 | -0.27008 | -0.29297 | -0.27008 | -0.29297 | -0.045776 | -0.16937 | -0.022888 | 0.045776 | -0.12817 | -0.16022 | -0.082398 | -0.11444 | 0.17395 | 122.113 | 0.091552 | 122.1222 | 121.9208 | 121.9757 | 121.9208 | 121.9299 | -122.0993 | -122.1451 | 122.113 | 122.0764 | 62.1597 | 62.233
616 | 122.3511 | -62.2696 | 59.7702 | -0.021286 | 0.0031253 | 0.058821 | 0.059676 | 0.0019268 | -0.0034201 | -0.0014805 | 0.0009461 | 0.001303 | 0.07151 | 0.062491 | -0.0083825 | 0.018585 | -0.0031338 | -0.11902 | 59.6008 | -62.2833 | 59.8984 | -62.0316 | -62.5076 | -62.4985 | 0.032043 | 59.5779 | -62.3245 | 59.8709 | -62.1643 | -62.3566 | -62.3291 | -0.013733 | -0.16937 | 0.12817 | 0.23804 | -0.22888 | -0.23804 | -0.21515 | -0.2243 | -0.054932 | -0.19226 | 0.10071 | 0.10529 | -0.05951 | -0.086975 | -0.004578 | -0.032043 | 0.25177 | 122.1817 | 0.16022 | 122.1954 | 121.8842 | 121.9025 | 121.8704 | 121.8475 | -122.0535 | -122.0947 | 122.168 | 122.1405 | 62.1506 | 62.3016
617.6875 | 122.2733 | -62.2925 | 59.8526 | -0.0060272 | 0.0024845 | 0.059889 | 0.059676 | -0.00020941 | -0.0061971 | 0.00022853 | -0.0021057 | 0.0027984 | 0.07151 | 0.067405 | -0.0098779 | 0.017731 | 7.04e-05 | -0.009155 | 59.6603 | -62.265 | 59.8434 | -62.0728 | -62.5122 | -62.5031 | 0.022888 | 59.6649 | -62.2971 | 59.8068 | -62.1964 | -62.3978 | -62.3932 | 0.027465 | -0.19226 | -0.009155 | 0.21973 | -0.21057 | -0.21973 | -0.23804 | -0.24719 | -0.004578 | -0.18768 | -0.045776 | 0.09613 | -0.10071 | -0.10529 | -0.09613 | -0.10071 | 0.19226 | 122.1085 | 0.10071 | 122.1039 | 121.9254 | 121.962 | 121.9528 | 121.9574 | -122.1176 | -122.1497 | 122.1359 | 122.0993 | 62.2833 | 62.3154
619.4531 | 122.3511 | -62.2467 | 59.761 | 0.0092313 | -0.0028561 | 0.059248 | 0.056685 | -0.0040546 | -0.0072653 | -0.0031895 | -0.0051575 | 0.00023504 | 0.07151 | 0.055655 | -0.010092 | 0.016663 | -0.0037748 | -0.018311 | 59.5596 | -62.2696 | 59.9213 | -61.9629 | -62.439 | -62.4207 | 0.14648 | 59.5871 | -62.2925 | 59.8984 | -62.0865 | -62.2787 | -62.3062 | -0.022888 | -0.20142 | 0.16022 | 0.28381 | -0.17395 | -0.19226 | -0.15106 | -0.16937 | -0.045776 | -0.17395 | 0.13733 | 0.16022 | -0.059509 | -0.032044 | -0.013733 | 0.013732 | 0.3067 | 122.1909 | 0.20599 | 122.1909 | 121.8292 | 121.8796 | 121.8063 | 121.8338 | -122.0306 | -122.0535 | 122.168 | 122.1451 | 62.2284 | 62.3932
621.1406 | 122.2824 | -62.2604 | 59.8114 | -0.0060272 | 0.0003483 | 0.061385 | 0.056685 | 0.0017132 | -0.0059835 | -0.00083947 | -0.0082093 | 0.0021576 | 0.070869 | 0.055228 | -0.0081689 | 0.017517 | -0.000784 | 0.045776 | 59.5734 | -62.2604 | 59.9167 | -61.9766 | -62.439 | -62.4252 | 0.1236 | 59.6329 | -62.265 | 59.8297 | -62.1689 | -62.352 | -62.3749 | 0 | -0.23804 | 0.10529 | 0.28381 | -0.16479 | -0.17853 | -0.16479 | -0.17853 | -0.004578 | -0.17853 | 0.018311 | 0.091553 | -0.11444 | -0.091553 | -0.10986 | -0.086975 | 0.28381 | 122.1771 | 0.096131 | 122.0947 | 121.8338 | 121.8979 | 121.8338 | 121.8933 | -122.0718 | -122.0764 | 122.1771 | 122.0901 | 62.3062 | 62.384
622.8906 | 122.2229 | -62.2925 | 59.7977 | 0.0016023 | 0.0029117 | 0.062453 | 0.062453 | -0.00085021 | -0.0051291 | -0.0010531 | -0.0051575 | 0.0027984 | 0.071297 | 0.063346 | -0.0075281 | 0.018158 | -0.0031338 | -0.064087 | 59.6237 | -62.3062 | 59.8343 | -62.114 | -62.5854 | -62.5717 | -0.041199 | 59.6375 | -62.3199 | 59.7702 | -62.2742 | -62.4847 | -62.4481 | -0.013733 | -0.17395 | 0.036622 | 0.17853 | -0.27924 | -0.29297 | -0.2655 | -0.27924 | -0.027466 | -0.16022 | -0.027465 | 0.01831 | -0.15564 | -0.19226 | -0.12817 | -0.16479 | 0.19226 | 122.1405 | 0.045776 | 122.0901 | 121.9299 | 121.9574 | 121.9162 | 121.9299 | -122.1039 | -122.1176 | 122.1268 | 122.0627 | 62.2284 | 62.2513
624.6406 | 122.3511 | -62.265 | 59.7839 | -0.0060272 | -7.9104e-05 | 0.059035 | 0.057112 | -0.001491 | -0.0053427 | -0.0027621 | -0.0021057 | 0.0021576 | 0.074074 | 0.063559 | -0.010732 | 0.016449 | -0.0018522 | 0.036621 | 59.5825 | -62.2742 | 59.9854 | -61.908 | -62.4115 | -62.4207 | 0.15564 | 59.5871 | -62.2787 | 59.8846 | -62.1002 | -62.2742 | -62.3108 | -0.009155 | -0.20142 | 0.20142 | 0.35706 | -0.15564 | -0.14648 | -0.14648 | -0.13733 | -0.013733 | -0.19684 | 0.10071 | 0.16479 | -0.045776 | -0.009155 | -0.032043 | 0.004578 | 0.36621 | 122.2595 | 0.17853 | 122.1634 | 121.8567 | 121.8658 | 121.8475 | 121.8521 | -122.0581 | -122.0627 | 122.2504 | 122.1497 | 62.3016 | 62.4207
626.3594 | 122.2137 | -62.2879 | 59.8297 | -0.021286 | 0.0024845 | 0.060744 | 0.056471 | 0.001286 | -0.0042745 | -0.0036167 | -0.0051575 | 0.0027984 | 0.073433 | 0.064414 | -0.01116 | 0.015167 | -0.0039884 | -0.013733 | 59.642 | -62.2742 | 59.8389 | -62.0682 | -62.5305 | -62.5031 | 0.045776 | 59.6558 | -62.3016 | 59.7656 | -62.2192 | -62.4069 | -62.439 | 0.013733 | -0.18768 | 0.009155 | 0.21973 | -0.21515 | -0.24262 | -0.22888 | -0.25635 | -0.013733 | -0.17395 | -0.064087 | 0.068665 | -0.15106 | -0.11902 | -0.13733 | -0.10528 | 0.20599 | 122.113 | 0.082398 | 122.0673 | 121.9162 | 121.9574 | 121.9299 | 121.9437 | -122.1039 | -122.1313 | 122.1268 | 122.0535 | 62.2742 | 62.3337
628.0625 | 122.3648 | -62.2559 | 59.761 | -0.021286 | 0.0012027 | 0.057539 | 0.054549 | -0.00020941 | -0.0072653 | -0.0029759 | 0.0009461 | 0.00023504 | 0.071938 | 0.061637 | -0.0092371 | 0.018158 | -0.0031338 | 0.027466 | 59.5642 | -62.2559 | 59.9716 | -61.9217 | -62.3932 | -62.3795 | 0.16479 | 59.6054 | -62.2833 | 59.8755 | -62.0865 | -62.2742 | -62.3199 | 0 | -0.19684 | 0.21057 | 0.33417 | -0.1236 | -0.13733 | -0.1236 | -0.13733 | -0.027466 | -0.15564 | 0.11444 | 0.16937 | -0.064087 | -0.018311 | -0.036621 | 0.009155 | 0.33417 | 122.2275 | 0.19684 | 122.1588 | 121.8201 | 121.8887 | 121.8201 | 121.8613 | -122.0169 | -122.0444 | 122.2275 | 122.1313 | 62.2833 | 62.4207
629.7969 | 122.2733 | -62.2787 | 59.816 | -0.013657 | -0.0002927 | 0.059676 | 0.058607 | -0.00085021 | -0.0061971 | 1.4934e-05 | -0.0051575 | 0.0023712 | 0.071083 | 0.068686 | -0.0081689 | 0.017517 | -0.00527 | 0.050354 | 59.5734 | -62.2559 | 59.935 | -61.9812 | -62.4298 | -62.4252 | 0.13733 | 59.6375 | -62.2879 | 59.8389 | -62.1597 | -62.3383 | -62.3749 | 0.022889 | -0.24262 | 0.11902 | 0.29755 | -0.14648 | -0.15106 | -0.16937 | -0.17395 | -0.009155 | -0.17853 | 0.022888 | 0.11902 | -0.09613 | -0.059509 | -0.086975 | -0.050354 | 0.27466 | 122.1909 | 0.12817 | 122.1268 | 121.8292 | 121.9254 | 121.8521 | 121.9162 | -122.0718 | -122.1039 | 122.2137 | 122.1176 | 62.3291 | 62.4161
631.5312 | 122.3328 | -62.265 | 59.7702 | -0.0060272 | -0.0007199 | 0.061171 | 0.058394 | -0.0040546 | -0.0083335 | -0.0029759 | 0.0009461 | -0.0019012 | 0.072365 | 0.060782 | -0.0079553 | 0.017731 | -0.000784 | -0.064087 | 59.5551 | -62.265 | 59.8846 | -62.0407 | -62.4985 | -62.4756 | 0.041199 | 59.5871 | -62.3154 | 59.8434 | -62.1552 | -62.3383 | -62.3611 | 0 | -0.21515 | 0.11444 | 0.22431 | -0.21057 | -0.23346 | -0.21057 | -0.23346 | -0.050354 | -0.18311 | 0.073242 | 0.10986 | -0.09613 | -0.073242 | -0.045776 | -0.022888 | 0.22431 | 122.1497 | 0.16022 | 122.1588 | 121.8201 | 121.9025 | 121.8201 | 121.8521 | -122.0352 | -122.0856 | 122.1497 | 122.1085 | 62.2009 | 62.3062
633.2812 | 122.2275 | -62.2925 | 59.8022 | 0.0016023 | 0.0026981 | 0.061812 | 0.061598 | -0.0010638 | -0.0068381 | -0.0019077 | -0.0021057 | 0.0049346 | 0.07386 | 0.070182 | -0.0096643 | 0.018799 | -0.0014248 | -0.082397 | 59.6054 | -62.2787 | 59.8251 | -62.1368 | -62.5946 | -62.5854 | -0.054932 | 59.6237 | -62.3291 | 59.7656 | -62.2971 | -62.4893 | -62.471 | 0.013732 | -0.19684 | 0.022888 | 0.15564 | -0.29297 | -0.30212 | -0.3067 | -0.31586 | -0.036622 | -0.17853 | -0.036621 | -0.004578 | -0.17853 | -0.19684 | -0.14191 | -0.16022 | 0.14191 | 122.1039 | 0.032044 | 122.0947 | 121.8842 | 121.9528 | 121.8979 | 121.9162 | -122.081 | -122.1313 | 122.1176 | 122.0581 | 62.2101 | 62.2375
635.0469 | 122.2366 | -62.3108 | 59.816 | -0.0060272 | 0.0022709 | 0.060744 | 0.063948 | -0.0032 | -0.0051291 | -0.0014805 | -0.0021057 | 0.005362 | 0.070656 | 0.066336 | -0.0068871 | 0.01944 | -0.0020658 | -0.12817 | 59.6191 | -62.3154 | 59.7977 | -62.1414 | -62.6221 | -62.5946 | -0.086975 | 59.642 | -62.352 | 59.761 | -62.2696 | -62.471 | -62.4481 | -0.004578 | -0.19684 | -0.018311 | 0.16937 | -0.28381 | -0.31128 | -0.27923 | -0.3067 | -0.041199 | -0.17395 | -0.054932 | 0.041199 | -0.13733 | -0.16022 | -0.09613 | -0.11902 | 0.17395 | 122.113 | 0.082398 | 122.113 | 121.9345 | 121.994 | 121.9299 | 121.9528 | -122.1313 | -122.168 | 122.1085 | 122.0718 | 62.1826 | 62.2238
636.7969 | 122.3465 | -62.2604 | 59.7336 | -0.0060272 | 0.0024845 | 0.061385 | 0.059676 | -0.001491 | -0.0053427 | -0.0038303 | -0.0021057 | 0.001303 | 0.071724 | 0.067191 | -0.0077417 | 0.017944 | -0.0037748 | -0.1236 | 59.5779 | -62.2833 | 59.8892 | -62.0361 | -62.5305 | -62.5122 | 0.041199 | 59.5367 | -62.3199 | 59.8618 | -62.1735 | -62.3566 | -62.3474 | -0.022888 | -0.15564 | 0.15564 | 0.2243 | -0.25177 | -0.27008 | -0.22888 | -0.24719 | -0.059509 | -0.19684 | 0.12817 | 0.086975 | -0.086975 | -0.09613 | -0.027466 | -0.036621 | 0.24719 | 122.1725 | 0.14648 | 122.1817 | 121.8613 | 121.8567 | 121.8384 | 121.7972 | -122.0169 | -122.0535 | 122.1497 | 122.1222 | 62.1368 | 62.3016
638.4844 | 122.2229 | -62.2879 | 59.8022 | 0.0016023 | 0.0005619 | 0.060103 | 0.060103 | 0.0042768 | -0.0053427 | -0.0036167 | -0.0021057 | 0.0038666 | 0.072365 | 0.070182 | -0.01116 | 0.018372 | -0.006979 | -0.054932 | 59.6329 | -62.3016 | 59.8618 | -62.0773 | -62.5763 | -62.5397 | 0 | 59.6329 | -62.3291 | 59.761 | -62.2467 | -62.4573 | -62.4481 | -0.013733 | -0.16937 | 0.059509 | 0.21057 | -0.25177 | -0.28839 | -0.23804 | -0.27466 | -0.041199 | -0.16937 | -0.041199 | 0.041199 | -0.16022 | -0.16937 | -0.11902 | -0.12817 | 0.2243 | 122.1634 | 0.082398 | 122.0901 | 121.9345 | 121.962 | 121.9208 | 121.9208 | -122.1039 | -122.1313 | 122.1497 | 122.0489 | 62.233 | 62.2879
640.2188 | 122.2778 | -62.2787 | 59.8343 | -0.013657 | 0.0012027 | 0.059889 | 0.060957 | 0.0017132 | -0.0023519 | -0.0023349 | -0.0051575 | 0.00023504 | 0.073219 | 0.065909 | -0.0092371 | 0.015808 | -0.004202 | -0.013733 | 59.6191 | -62.2971 | 59.8846 | -62.027 | -62.5305 | -62.5031 | 0.082397 | 59.6375 | -62.3062 | 59.8251 | -62.1872 | -62.3795 | -62.3932 | -0.01831 | -0.21515 | 0.050354 | 0.25177 | -0.2243 | -0.25177 | -0.20599 | -0.23346 | -0.027465 | -0.19684 | -0.009156 | 0.091553 | -0.11444 | -0.10071 | -0.086975 | -0.073243 | 0.27008 | 122.1817 | 0.11902 | 122.1313 | 121.9162 | 121.9437 | 121.8979 | 121.9162 | -122.1313 | -122.1405 | 122.1634 | 122.1039 | 62.265 | 62.3611
641.9531 | 122.2046 | -62.3108 | 59.8068 | -0.021286 | 0.0018435 | 0.058821 | 0.060957 | 0.002995 | -0.0055563 | -0.0025485 | -0.0021057 | 0.00066224 | 0.070869 | 0.062278 | -0.0073145 | 0.017731 | -0.0001432 | -0.10529 | 59.61 | -62.2879 | 59.8114 | -62.1368 | -62.5992 | -62.5946 | -0.09613 | 59.6695 | -62.3566 | 59.729 | -62.2925 | -62.4985 | -62.4847 | 0.022888 | -0.19684 | 0.004577 | 0.17395 | -0.28381 | -0.28839 | -0.3067 | -0.31128 | -0.045776 | -0.13733 | -0.07782 | 0.018311 | -0.17395 | -0.18768 | -0.12817 | -0.14191 | 0.15106 | 122.0993 | 0.064087 | 122.0856 | 121.8979 | 122.0261 | 121.9208 | 121.9803 | -122.0947 | -122.1634 | 122.1222 | 122.0398 | 62.2055 | 62.2147
643.7031 | 122.3648 | -62.2604 | 59.7519 | -0.0060272 | -0.0011471 | 0.058821 | 0.054549 | -0.0023456 | -0.0040609 | -0.0025485 | 0.0009461 | 0.00044864 | 0.073219 | 0.053946 | -0.0090235 | 0.018799 | -0.0033474 | 0.004578 | 59.5596 | -62.2559 | 59.9442 | -61.9263 | -62.4207 | -62.384 | 0.18768 | 59.5963 | -62.2742 | 59.8755 | -62.1002 | -62.2742 | -62.3199 | 0.004578 | -0.19226 | 0.19226 | 0.33417 | -0.1236 | -0.16022 | -0.12817 | -0.16479 | -0.013733 | -0.15564 | 0.1236 | 0.16022 | -0.059509 | -0.013733 | -0.045776 | 0 | 0.32959 | 122.2 | 0.17395 | 122.1497 | 121.8155 | 121.8704 | 121.8201 | 121.8567 | -122.0078 | -122.0261 | 122.2046 | 122.1359 | 62.265 | 62.4481
645.3906 | 122.2275 | -62.3016 | 59.8251 | -0.013657 | 0.0044071 | 0.059248 | 0.060957 | 0.0021406 | -0.0051291 | -0.0057529 | -0.0021057 | 0.0017304 | 0.073433 | 0.066977 | -0.0088097 | 0.018372 | -0.0039884 | -0.059509 | 59.6649 | -62.2742 | 59.8572 | -62.0773 | -62.5671 | -62.5488 | -0.022888 | 59.6375 | -62.3383 | 59.7656 | -62.2513 | -62.4756 | -62.4481 | 0.027466 | -0.16022 | 0.032044 | 0.2243 | -0.24719 | -0.2655 | -0.27466 | -0.29297 | -0.036621 | -0.18768 | -0.059509 | 0.050354 | -0.14648 | -0.17395 | -0.10986 | -0.13733 | 0.19684 | 122.1313 | 0.086975 | 122.1039 | 121.9391 | 121.9757 | 121.9666 | 121.9391 | -122.0993 | -122.1634 | 122.1588 | 122.0673 | 62.2421 | 62.2787
647.1406 | 122.1909 | -62.3154 | 59.816 | -0.013657 | 0.0046207 | 0.062025 | 0.062025 | 0.0023542 | -0.0068381 | -0.00083947 | 0.0009461 | 0.0032256 | 0.072151 | 0.062918 | -0.011587 | 0.01709 | -0.0027066 | -0.11444 | 59.6329 | -62.3016 | 59.8114 | -62.1368 | -62.6221 | -62.5626 | -0.091553 | 59.6329 | -62.3245 | 59.7382 | -62.3108 | -62.4985 | -62.4619 | 0.013733 | -0.1831 | -0.004578 | 0.17853 | -0.24719 | -0.3067 | -0.26093 | -0.32043 | -0.009155 | -0.1831 | -0.07782 | 0.004578 | -0.14648 | -0.18311 | -0.13733 | -0.17395 | 0.1648 | 122.113 | 0.013733 | 122.0627 | 121.9345 | 121.9574 | 121.9482 | 121.9482 | -122.1176 | -122.1405 | 122.1268 | 122.0535 | 62.2009 | 62.2238
648.8438 | 122.2183 | -62.2879 | 59.8389 | -0.013657 | -0.0009335 | 0.058821 | 0.059248 | -0.0053362 | -0.0061971 | -0.00041227 | 0.0009461 | 0.0038666 | 0.071297 | 0.060782 | -0.010732 | 0.017303 | 0.0015658 | -0.018311 | 59.6603 | -62.2742 | 59.8297 | -62.0865 | -62.5351 | -62.5259 | 0 | 59.6741 | -62.3383 | 59.7748 | -62.233 | -62.4252 | -62.4344 | 0.013733 | -0.17853 | -0.009155 | 0.20142 | -0.23804 | -0.24719 | -0.25177 | -0.26093 | -0.050354 | -0.16479 | -0.064087 | 0.054932 | -0.14648 | -0.13733 | -0.09613 | -0.086975 | 0.18768 | 122.1039 | 0.10529 | 122.113 | 121.9345 | 122.0123 | 121.9482 | 121.962 | -122.113 | -122.1771 | 122.1176 | 122.0627 | 62.2696 | 62.2879
650.5781 | 122.2595 | -62.2833 | 59.8572 | -0.0060272 | -0.0002927 | 0.05818 | 0.058821 | 0.0010724 | -0.0066245 | -0.0010531 | -0.0021057 | 0.0034392 | 0.073006 | 0.065055 | -0.0083825 | 0.018799 | -0.0014248 | -0.013733 | 59.6695 | -62.2833 | 59.8251 | -62.0865 | -62.5488 | -62.5305 | 0.013733 | 59.6649 | -62.3154 | 59.7794 | -62.2238 | -62.4161 | -62.4252 | 0 | -0.18768 | -0.032044 | 0.19684 | -0.24719 | -0.2655 | -0.24719 | -0.2655 | -0.032044 | -0.19226 | -0.07782 | 0.059509 | -0.14191 | -0.13275 | -0.10986 | -0.10071 | 0.19684 | 122.1085 | 0.091553 | 122.0947 | 121.9528 | 121.9803 | 121.9528 | 121.9482 | -122.1405 | -122.1725 | 122.1085 | 122.0627 | 62.2696 | 62.2971
652.25 | 122.3602 | -62.2696 | 59.7427 | -0.013657 | 0.0039799 | 0.060744 | 0.059676 | -0.00020941 | -0.0064109 | -0.0027621 | -0.0082093 | 0.00087584 | 0.072792 | 0.059287 | -0.0090235 | 0.016449 | -0.0020658 | -0.10986 | 59.5963 | -62.2742 | 59.8938 | -62.0087 | -62.4985 | -62.4893 | 0.054932 | 59.5779 | -62.3245 | 59.8618 | -62.1597 | -62.3566 | -62.3428 | -0.004578 | -0.14648 | 0.15106 | 0.26093 | -0.21973 | -0.22888 | -0.21515 | -0.2243 | -0.054932 | -0.16479 | 0.11902 | 0.10986 | -0.073242 | -0.086975 | -0.01831 | -0.032043 | 0.2655 | 122.168 | 0.16479 | 122.1863 | 121.8704 | 121.9025 | 121.8658 | 121.8475 | -122.0169 | -122.0673 | 122.1634 | 122.1313 | 62.1597 | 62.3245
654 | 122.2275 | -62.3016 | 59.7977 | -0.0060272 | 0.0026981 | 0.058394 | 0.060957 | -0.0010638 | -0.0049155 | -0.0012669 | -0.0051575 | 0.001944 | 0.072151 | 0.064627 | -0.010092 | 0.020508 | -0.0014248 | -0.027466 | 59.61 | -62.2742 | 59.8663 | -62.0544 | -62.5305 | -62.5076 | 0.045776 | 59.6375 | -62.3108 | 59.7931 | -62.2284 | -62.4115 | -62.4252 | 0.027466 | -0.18768 | 0.068665 | 0.24719 | -0.20599 | -0.22888 | -0.23346 | -0.25635 | -0.009155 | -0.16022 | -0.004577 | 0.073242 | -0.1236 | -0.10986 | -0.11444 | -0.10071 | 0.21973 | 122.1405 | 0.082397 | 122.1039 | 121.8842 | 121.9482 | 121.9116 | 121.9391 | -122.0718 | -122.1085 | 122.168 | 122.0947 | 62.2742 | 62.3474
655.7344 | 122.2 | -62.3154 | 59.7931 | -0.0060272 | 0.0041935 | 0.059462 | 0.058394 | 0.0017132 | -0.0047019 | -0.0027621 | -0.0021057 | 0.003012 | 0.071724 | 0.071891 | -0.0077417 | 0.018158 | 0.004343 | -0.11444 | 59.6329 | -62.2833 | 59.7931 | -62.1414 | -62.6175 | -62.5854 | -0.10529 | 59.6375 | -62.3657 | 59.729 | -62.3154 | -62.4847 | -62.471 | 0.032044 | -0.16022 | 0 | 0.17395 | -0.27008 | -0.30212 | -0.30212 | -0.33417 | -0.050354 | -0.15564 | -0.064087 | 0 | -0.15564 | -0.16937 | -0.10528 | -0.11902 | 0.14191 | 122.0764 | 0.050354 | 122.0947 | 121.9162 | 122.0032 | 121.9482 | 121.9528 | -122.0764 | -122.1588 | 122.1085 | 122.0444 | 62.2009 | 62.2101
657.4375 | 122.3328 | -62.2833 | 59.7565 | 0.0016023 | 0.0012027 | 0.058394 | 0.056471 | -0.0068316 | -0.0049155 | -0.00083947 | -0.0021057 | 2.1442e-05 | 0.071724 | 0.061423 | -0.0081689 | 0.016876 | 0.0013522 | -0.082397 | 59.5917 | -62.2787 | 59.8709 | -62.0499 | -62.5076 | -62.471 | 0.036621 | 59.61 | -62.3154 | 59.8297 | -62.1643 | -62.3428 | -62.3657 | 0.004577 | -0.16479 | 0.11444 | 0.23346 | -0.18768 | -0.2243 | -0.19226 | -0.22888 | -0.032044 | -0.14648 | 0.073242 | 0.11902 | -0.082398 | -0.059509 | -0.050354 | -0.027465 | 0.22888 | 122.1497 | 0.15106 | 122.1451 | 121.8704 | 121.9254 | 121.875 | 121.8933 | -122.0352 | -122.0718 | 122.1542 | 122.113 | 62.2009 | 62.3199
659.1875 | 122.3236 | -62.2559 | 59.7931 | 0.0016023 | 0.0014163 | 0.061598 | 0.055617 | -0.0036274 | -0.0055563 | -0.0021213 | -0.0021057 | 0.0010894 | 0.071083 | 0.060141 | -0.0094507 | 0.01474 | -0.0018522 | 0.041199 | 59.5825 | -62.2421 | 59.9442 | -61.9675 | -62.4252 | -62.3978 | 0.14191 | 59.5963 | -62.3108 | 59.8755 | -62.1277 | -62.2971 | -62.3337 | 0.013733 | -0.21057 | 0.15106 | 0.28839 | -0.14191 | -0.16937 | -0.15564 | -0.18311 | -0.054932 | -0.19684 | 0.082397 | 0.12817 | -0.07782 | -0.041199 | -0.022888 | 0.013733 | 0.27466 | 122.1863 | 0.18311 | 122.1863 | 121.8246 | 121.907 | 121.8384 | 121.8521 | -122.0352 | -122.1039 | 122.2 | 122.1313 | 62.2971 | 62.3978
660.875 | 122.3145 | -62.2971 | 59.729 | -0.0060272 | 0.0033389 | 0.05818 | 0.057967 | 0.0010724 | -0.0072653 | -0.00062587 | 0.0009461 | 0.0010894 | 0.072365 | 0.061209 | -0.010946 | 0.017303 | 0.000925 | -0.082397 | 59.5551 | -62.2559 | 59.9167 | -61.9949 | -62.4893 | -62.4619 | 0.068665 | 59.5734 | -62.3154 | 59.8434 | -62.1689 | -62.3703 | -62.3703 | 0.041199 | -0.17395 | 0.18768 | 0.30212 | -0.16479 | -0.19226 | -0.20599 | -0.23346 | -0.018311 | -0.15564 | 0.11444 | 0.12817 | -0.073242 | -0.073242 | -0.054931 | -0.054931 | 0.26093 | 122.1725 | 0.14648 | 122.1588 | 121.8109 | 121.8887 | 121.8521 | 121.8704 | -121.9849 | -122.0444 | 122.2137 | 122.1405 | 62.2147 | 62.3657
662.625 | 122.3282 | -62.2925 | 59.761 | -0.0060272 | -0.0013607 | 0.058394 | 0.057326 | -0.00020941 | -0.0074789 | -0.00019867 | -0.0082093 | 0.00023504 | 0.070229 | 0.062278 | -0.0075281 | 0.017731 | -0.004202 | -0.07782 | 59.5871 | -62.3062 | 59.8663 | -62.0361 | -62.4985 | -62.4756 | 0.027466 | 59.6237 | -62.3245 | 59.8389 | -62.1689 | -62.3199 | -62.3703 | -0.013733 | -0.17395 | 0.10529 | 0.25635 | -0.18311 | -0.20599 | -0.16937 | -0.19226 | -0.032044 | -0.13733 | 0.07782 | 0.1236 | -0.07782 | -0.027466 | -0.045776 | 0.004578 | 0.27008 | 122.1725 | 0.15564 | 122.1634 | 121.8933 | 121.9482 | 121.8796 | 121.9162 | -122.0673 | -122.0856 | 122.1588 | 122.1313 | 62.2147 | 62.3199
664.3281 | 122.3648 | -62.2879 | 59.7382 | 0.0016023 | 0.0035525 | 0.061812 | 0.059462 | 0.0010724 | -0.0049155 | -0.0046847 | -0.0051575 | 0.00066224 | 0.070869 | 0.065055 | -0.011587 | 0.018585 | -0.0031338 | -0.091553 | 59.5551 | -62.2742 | 59.9075 | -62.0224 | -62.4939 | -62.4664 | 0.054932 | 59.5688 | -62.3108 | 59.8663 | -62.1735 | -62.352 | -62.3291 | 0.013733 | -0.18311 | 0.16937 | 0.2655 | -0.17853 | -0.20599 | -0.19226 | -0.21973 | -0.022888 | -0.16937 | 0.12817 | 0.11444 | -0.041199 | -0.064087 | -0.018311 | -0.041199 | 0.25177 | 122.1817 | 0.13733 | 122.1771 | 121.8292 | 121.8796 | 121.843 | 121.8567 | -122.0123 | -122.049 | 122.1954 | 122.1542 | 62.1964 | 62.3428
666.0625 | 122.2229 | -62.2879 | 59.8114 | -0.0060272 | 0.0037661 | 0.059889 | 0.061812 | 0.00043159 | -0.0059835 | -0.0014805 | -0.0021057 | 0.0034392 | 0.074287 | 0.07125 | -0.0096643 | 0.01944 | -0.0033474 | -0.064087 | 59.6283 | -62.2925 | 59.848 | -62.1048 | -62.5946 | -62.5763 | -0.041199 | 59.642 | -62.3428 | 59.761 | -62.2696 | -62.4802 | -62.4481 | -0.004577 | -0.1831 | 0.036621 | 0.18311 | -0.28839 | -0.3067 | -0.28381 | -0.30212 | -0.054931 | -0.16937 | -0.050354 | 0.018311 | -0.16022 | -0.19226 | -0.10529 | -0.13733 | 0.18768 | 122.1405 | 0.073242 | 122.1039 | 121.9208 | 121.9849 | 121.9162 | 121.9299 | -122.1039 | -122.1542 | 122.1359 | 122.0489 | 62.2238 | 62.2467
667.8125 | 122.2046 | -62.3062 | 59.8068 | -0.013657 | 0.0022709 | 0.061598 | 0.061385 | 0.001286 | -0.0057699 | -0.0019077 | -0.0051575 | 0.0034392 | 0.073433 | 0.068686 | -0.0081689 | 0.018799 | -0.0016384 | -0.11902 | 59.6466 | -62.3062 | 59.7977 | -62.1506 | -62.6175 | -62.59 | -0.11444 | 59.6329 | -62.352 | 59.7382 | -62.2971 | -62.4985 | -62.4573 | 0 | -0.16022 | -0.009156 | 0.15564 | -0.28381 | -0.31128 | -0.28381 | -0.31128 | -0.045777 | -0.17395 | -0.068665 | 0.009155 | -0.15106 | -0.19226 | -0.10529 | -0.14648 | 0.15564 | 122.1039 | 0.054932 | 122.0901 | 121.9528 | 121.9849 | 121.9528 | 121.9391 | -122.113 | -122.1588 | 122.1039 | 122.0444 | 62.1872 | 62.1918
669.5 | 122.2412 | -62.2742 | 59.7931 | -0.0060272 | 0.0026981 | 0.061598 | 0.057967 | 0.0040632 | -0.0061971 | -0.00041227 | -0.0051575 | 0.0038666 | 0.072792 | 0.063132 | -0.0068871 | 0.018585 | 0.0002842 | -0.032043 | 59.6558 | -62.2833 | 59.8801 | -62.0453 | -62.5214 | -62.5214 | 0.050354 | 59.642 | -62.3062 | 59.7885 | -62.2238 | -62.4298 | -62.4115 | -0.009155 | -0.13733 | 0.086975 | 0.22888 | -0.24719 | -0.24719 | -0.23804 | -0.23804 | -0.032043 | -0.15106 | -0.004578 | 0.050354 | -0.13733 | -0.15564 | -0.10529 | -0.1236 | 0.23804 | 122.1634 | 0.082397 | 122.0947 | 121.9391 | 121.9482 | 121.9299 | 121.9162 | -122.0764 | -122.0993 | 122.1542 | 122.0627 | 62.2421 | 62.3245
671.1719 | 122.3328 | -62.3062 | 59.7336 | -0.013657 | 0.0026981 | 0.061171 | 0.058821 | 0.00085879 | -0.0047019 | -0.0031895 | -0.0051575 | 0.00087584 | 0.071938 | 0.062491 | -0.0092371 | 0.018158 | -0.004202 | -0.13275 | 59.6054 | -62.2925 | 59.8801 | -62.0361 | -62.5168 | -62.4847 | 0.032043 | 59.5779 | -62.3428 | 59.8526 | -62.1597 | -62.3428 | -62.3474 | 0.013733 | -0.12817 | 0.14648 | 0.27008 | -0.17853 | -0.21057 | -0.19226 | -0.22431 | -0.036621 | -0.15564 | 0.11902 | 0.14648 | -0.041199 | -0.036621 | -0.004578 | 0 | 0.25635 | 122.1725 | 0.18311 | 122.1954 | 121.8979 | 121.9208 | 121.9116 | 121.8842 | -122.0261 | -122.0764 | 122.1863 | 122.1588 | 62.1735 | 62.3383
672.9219 | 122.3511 | -62.2421 | 59.7748 | -0.0060272 | 0.0003483 | 0.058607 | 0.057753 | -0.0044818 | -0.0049155 | -0.00062587 | -0.0051575 | -0.0010468 | 0.067879 | 0.063132 | -0.0068871 | 0.017944 | -0.0003568 | 0.013733 | 59.5688 | -62.2604 | 59.9716 | -61.9217 | -62.4023 | -62.3978 | 0.13733 | 59.6008 | -62.2833 | 59.8846 | -62.0865 | -62.2742 | -62.3199 | -0.018311 | -0.20599 | 0.19684 | 0.32043 | -0.15564 | -0.16022 | -0.13733 | -0.14191 | -0.041199 | -0.17395 | 0.10986 | 0.15564 | -0.07782 | -0.032044 | -0.036621 | 0.009155 | 0.33875 | 122.2321 | 0.19684 | 122.168 | 121.8292 | 121.8842 | 121.8109 | 121.843 | -122.0352 | -122.0581 | 122.2137 | 122.1268 | 62.2559 | 62.3795
674.6094 | 122.2824 | -62.2787 | 59.8251 | -0.0060272 | -0.0005063 | 0.059462 | 0.058607 | -0.00555 | -0.0057699 | -0.0023349 | -0.0021057 | 0.00023504 | 0.071938 | 0.064414 | -0.0090235 | 0.016235 | -0.0063382 | 0.036621 | 59.5963 | -62.265 | 59.9213 | -61.9858 | -62.4527 | -62.439 | 0.13275 | 59.6375 | -62.2925 | 59.8343 | -62.1689 | -62.352 | -62.3703 | 0.013733 | -0.22888 | 0.096131 | 0.29297 | -0.16022 | -0.17395 | -0.17395 | -0.18768 | -0.013732 | -0.18768 | 0.009156 | 0.10986 | -0.091552 | -0.073242 | -0.07782 | -0.05951 | 0.27924 | 122.1863 | 0.1236 | 122.1268 | 121.8613 | 121.9299 | 121.875 | 121.9162 | -122.0901 | -122.1176 | 122.2 | 122.113 | 62.3154 | 62.4115
676.3438 | 122.319 | -62.2787 | 59.761 | -0.013657 | -0.0007199 | 0.060103 | 0.060316 | -0.0027728 | -0.0047019 | -0.0021213 | -0.0051575 | -0.00019216 | 0.071724 | 0.070182 | -0.0092371 | 0.016449 | 7.04e-05 | -0.07782 | 59.5734 | -62.2971 | 59.8846 | -62.0499 | -62.5031 | -62.4756 | 0.041199 | 59.5963 | -62.3108 | 59.8343 | -62.1643 | -62.3383 | -62.3657 | -0.01831 | -0.18768 | 0.1236 | 0.22888 | -0.19684 | -0.2243 | -0.17853 | -0.20599 | -0.032043 | -0.16479 | 0.073243 | 0.11444 | -0.086975 | -0.059509 | -0.054932 | -0.027466 | 0.24719 | 122.1817 | 0.14648 | 122.1451 | 121.8704 | 121.907 | 121.8521 | 121.875 | -122.0581 | -122.0718 | 122.1634 | 122.113 | 62.2009 | 62.3199
678.0781 | 122.2275 | -62.2925 | 59.8251 | -0.013657 | 0.0014163 | 0.060103 | 0.057112 | 0.0032086 | -0.0068381 | -0.0021213 | -0.0021057 | 0.0023712 | 0.071297 | 0.063773 | -0.0085961 | 0.016663 | 0.0002842 | 0.045776 | 59.5779 | -62.2559 | 59.8984 | -62.0132 | -62.4756 | -62.4664 | 0.086975 | 59.6466 | -62.2879 | 59.7977 | -62.2101 | -62.3886 | -62.4344 | 0.036621 | -0.24719 | 0.073242 | 0.27923 | -0.17395 | -0.18311 | -0.21057 | -0.21973 | 0.004577 | -0.17853 | -0.027466 | 0.082397 | -0.14191 | -0.096131 | -0.14648 | -0.10071 | 0.24261 | 122.1542 | 0.07782 | 122.0856 | 121.8338 | 121.9345 | 121.8704 | 121.9391 | -122.081 | -122.113 | 122.1909 | 122.0901 | 62.3383 | 62.3795
679.7656 | 122.2092 | -62.2971 | 59.8114 | -0.0060272 | 0.0044071 | 0.061171 | 0.060957 | 0.002995 | -0.0049155 | -0.0042575 | -0.0021057 | 0.0034392 | 0.073433 | 0.066977 | -0.010305 | 0.018158 | -0.0056974 | -0.12817 | 59.6283 | -62.2879 | 59.8022 | -62.146 | -62.6175 | -62.5946 | -0.073242 | 59.6329 | -62.3383 | 59.7656 | -62.2971 | -62.4939 | -62.4435 | 0.009155 | -0.1831 | -0.009155 | 0.15106 | -0.29755 | -0.32044 | -0.3067 | -0.32959 | -0.041199 | -0.17853 | -0.045776 | 0 | -0.14648 | -0.19684 | -0.10529 | -0.15564 | 0.14191 | 122.0901 | 0.041199 | 122.1039 | 121.9162 | 121.9711 | 121.9254 | 121.9299 | -122.0993 | -122.1497 | 122.0993 | 122.0627 | 62.1689 | 62.2238
681.5 | 122.2183 | -62.3016 | 59.8114 | 0.0016023 | 0.0037661 | 0.059676 | 0.061598 | -0.00085021 | -0.0059835 | -0.00041227 | -0.0021057 | 0.0051482 | 0.070442 | 0.062278 | -0.0085961 | 0.019012 | -0.002493 | -0.068665 | 59.6375 | -62.2696 | 59.8434 | -62.0956 | -62.5992 | -62.5534 | -0.027466 | 59.6466 | -62.3428 | 59.7656 | -62.265 | -62.4664 | -62.4527 | 0.032044 | -0.17395 | 0.032044 | 0.20599 | -0.25177 | -0.29755 | -0.28381 | -0.32959 | -0.041198 | -0.16479 | -0.045776 | 0.036621 | -0.15106 | -0.16479 | -0.10986 | -0.1236 | 0.17395 | 122.113 | 0.077819 | 122.1085 | 121.907 | 121.9894 | 121.9391 | 121.9482 | -122.081 | -122.1542 | 122.1451 | 122.0673 | 62.233 | 62.2742
683.2344 | 122.3053 | -62.2879 | 59.7473 | -0.0060272 | 0.0014163 | 0.061385 | 0.060103 | -0.00085021 | -0.0034201 | -0.0016941 | -0.0021057 | 0.0017304 | 0.072151 | 0.066977 | -0.0098779 | 0.020508 | -0.0020658 | -0.16937 | 59.6191 | -62.2971 | 59.8297 | -62.114 | -62.5854 | -62.558 | -0.050354 | 59.5963 | -62.3611 | 59.816 | -62.2009 | -62.3978 | -62.3978 | -0.009155 | -0.12817 | 0.082398 | 0.17395 | -0.27008 | -0.29755 | -0.26093 | -0.28839 | -0.073242 | -0.15106 | 0.068665 | 0.086975 | -0.10986 | -0.10986 | -0.036621 | -0.036621 | 0.1831 | 122.1268 | 0.16022 | 122.1771 | 121.9162 | 121.9574 | 121.907 | 121.8842 | -122.0444 | -122.1085 | 122.1176 | 122.1039 | 62.1185 | 62.2375
684.9844 | 122.2229 | -62.2833 | 59.8114 | -0.0060272 | 0.0037661 | 0.060957 | 0.060316 | 0.00064519 | -0.0074789 | -0.0010531 | -0.0051575 | 0.0021576 | 0.072365 | 0.065482 | -0.0066735 | 0.019012 | -0.004202 | -0.041199 | 59.6283 | -62.2925 | 59.8526 | -62.0773 | -62.5763 | -62.5442 | 0 | 59.6558 | -62.3337 | 59.7885 | -62.2513 | -62.471 | -62.4344 | -0.009155 | -0.1831 | 0.041199 | 0.20599 | -0.26093 | -0.29297 | -0.25177 | -0.28381 | -0.050354 | -0.15564 | -0.022888 | 0.032043 | -0.15106 | -0.18768 | -0.10071 | -0.13733 | 0.21515 | 122.1451 | 0.082397 | 122.1222 | 121.9208 | 121.9894 | 121.9116 | 121.9391 | -122.1039 | -122.1451 | 122.1359 | 122.0718 | 62.2421 | 62.2833
686.7188 | 122.2733 | -62.2696 | 59.8251 | -0.013657 | 0.0007755 | 0.06288 | 0.059248 | 0.0010724 | -0.0055563 | -0.0023349 | -0.0051575 | 0.003012 | 0.073433 | 0.068259 | -0.0085961 | 0.017731 | -0.0031338 | 0.009155 | 59.6603 | -62.2742 | 59.8663 | -62.0544 | -62.5031 | -62.5076 | 0.050354 | 59.6603 | -62.3016 | 59.8206 | -62.1872 | -62.384 | -62.3886 | -0.004578 | -0.16479 | 0.041199 | 0.21515 | -0.23804 | -0.23346 | -0.23346 | -0.22888 | -0.032044 | -0.16479 | -0.004577 | 0.082397 | -0.11902 | -0.11444 | -0.086975 | -0.082397 | 0.21973 | 122.1405 | 0.11444 | 122.1222 | 121.9345 | 121.962 | 121.9299 | 121.9299 | -122.0993 | -122.1268 | 122.1359 | 122.0901 | 62.2787 | 62.3199
688.4062 | 122.2961 | -62.3016 | 59.7931 | -0.0060272 | 0.0022709 | 0.060957 | 0.056258 | 0.001286 | -0.0061971 | -0.0029759 | -0.0021057 | -0.001474 | 0.070442 | 0.057364 | -0.0075281 | 0.017303 | -0.0001432 | -0.07782 | 59.5688 | -62.2971 | 59.8663 | -62.059 | -62.5305 | -62.5031 | 0.009155 | 59.5779 | -62.3291 | 59.7977 | -62.2055 | -62.3795 | -62.3795 | 0.004578 | -0.2243 | 0.073242 | 0.24262 | -0.20142 | -0.22888 | -0.20599 | -0.23346 | -0.027466 | -0.21515 | 0.004577 | 0.096131 | -0.07782 | -0.07782 | -0.050354 | -0.050354 | 0.23804 | 122.1634 | 0.1236 | 122.1268 | 121.8658 | 121.907 | 121.8704 | 121.8796 | -122.0901 | -122.1222 | 122.168 | 122.0993 | 62.2238 | 62.3108
690.1562 | 122.3145 | -62.2513 | 59.816 | -0.0060272 | -0.0022153 | 0.059248 | 0.058607 | -0.0017048 | -0.0064109 | -0.0029759 | -0.0021057 | -0.001474 | 0.071724 | 0.067405 | -0.010732 | 0.018158 | 0.0004978 | 0.036621 | 59.5642 | -62.265 | 59.9487 | -61.9766 | -62.439 | -62.4161 | 0.14648 | 59.61 | -62.3016 | 59.8618 | -62.1414 | -62.3108 | -62.3383 | -0.013733 | -0.25177 | 0.13275 | 0.27466 | -0.16479 | -0.18768 | -0.15106 | -0.17395 | -0.050354 | -0.20599 | 0.045776 | 0.10986 | -0.086975 | -0.059509 | -0.036621 | -0.009155 | 0.28839 | 122.2137 | 0.16022 | 122.1634 | 121.8292 | 121.9116 | 121.8155 | 121.8613 | -122.081 | -122.1176 | 122.2 | 122.113 | 62.2879 | 62.3978
691.8906 | 122.3373 | -62.2696 | 59.8114 | -0.0060272 | -0.0024289 | 0.060103 | 0.057112 | -0.0010638 | -0.0029929 | -0.0021213 | -0.0051575 | 0.00066224 | 0.068947 | 0.061637 | -0.011373 | 0.019653 | 0.0013522 | 0.041199 | 59.5779 | -62.2787 | 59.9487 | -61.9675 | -62.4344 | -62.4115 | 0.14648 | 59.5917 | -62.2742 | 59.8663 | -62.1094 | -62.2925 | -62.3199 | -0.009156 | -0.23346 | 0.13733 | 0.30212 | -0.14191 | -0.16479 | -0.13275 | -0.15564 | -0.004578 | -0.21973 | 0.054932 | 0.16022 | -0.050354 | -0.022888 | -0.045776 | -0.01831 | 0.31128 | 122.2275 | 0.16479 | 122.1405 | 121.8567 | 121.8658 | 121.8475 | 121.8613 | -122.0901 | -122.0856 | 122.2183 | 122.1359 | 62.3108 | 62.4161
693.5781 | 122.2183 | -62.2833 | 59.7839 | -0.0060272 | 0.0037661 | 0.062025 | 0.063948 | 0.00021799 | -0.0064109 | -0.0016941 | -0.0021057 | 0.0034392 | 0.070442 | 0.068045 | -0.0083825 | 0.018372 | -0.0003568 | -0.13733 | 59.6329 | -62.3199 | 59.7839 | -62.1689 | -62.6495 | -62.5854 | -0.086975 | 59.642 | -62.3428 | 59.7519 | -62.2879 | -62.4802 | -62.4481 | -0.036621 | -0.15106 | 0 | 0.11444 | -0.30212 | -0.36621 | -0.2655 | -0.32959 | -0.059509 | -0.14191 | -0.032044 | -0.004578 | -0.1648 | -0.19684 | -0.10529 | -0.13733 | 0.15106 | 122.1039 | 0.054931 | 122.0947 | 121.9528 | 121.9849 | 121.9162 | 121.9254 | -122.1039 | -122.1268 | 122.0673 | 122.0352 | 62.146 | 62.1963
695.3281 | 122.2137 | -62.2879 | 59.8297 | -0.0060272 | 0.0003483 | 0.056685 | 0.059248 | 0.00021799 | -0.0068381 | -0.0025485 | -0.0082093 | 0.00087584 | 0.071724 | 0.061423 | -0.010092 | 0.018158 | -0.0012112 | 0.022888 | 59.5917 | -62.265 | 59.8572 | -62.0544 | -62.5214 | -62.4985 | 0.054932 | 59.6695 | -62.2879 | 59.7794 | -62.2055 | -62.4023 | -62.4161 | 0.022888 | -0.23804 | 0.027466 | 0.23346 | -0.21057 | -0.23346 | -0.23346 | -0.25635 | 0 | -0.16022 | -0.050354 | 0.082398 | -0.12817 | -0.11444 | -0.12817 | -0.11444 | 0.21057 | 122.1222 | 0.082398 | 122.0673 | 121.8567 | 121.9574 | 121.8796 | 121.9574 | -122.0947 | -122.1176 | 122.1451 | 122.0673 | 62.3108 | 62.3428
697.0625 | 122.2504 | -62.2879 | 59.8389 | -0.021286 | 0.0001345 | 0.058394 | 0.057112 | -0.002132 | -0.0061971 | -0.0010531 | -0.0021057 | 0.0015166 | 0.071297 | 0.057792 | -0.0098779 | 0.017944 | -0.000784 | -0.004578 | 59.6466 | -62.2696 | 59.8297 | -62.0911 | -62.5442 | -62.5305 | 0.018311 | 59.6649 | -62.2925 | 59.7839 | -62.2192 | -62.4207 | -62.3795 | 0.018311 | -0.19226 | -0.009155 | 0.19684 | -0.24262 | -0.25635 | -0.26093 | -0.27466 | -0.004577 | -0.17395 | -0.054931 | 0.068665 | -0.091553 | -0.13275 | -0.086976 | -0.12817 | 0.17853 | 122.0993 | 0.073242 | 122.0764 | 121.9162 | 121.9574 | 121.9345 | 121.9528 | -122.1085 | -122.1313 | 122.1176 | 122.0718 | 62.2833 | 62.3062
698.7344 | 122.3145 | -62.3062 | 59.7336 | -0.0060272 | 0.0024845 | 0.061171 | 0.061171 | -0.0023456 | -0.0042745 | -0.00062587 | 0.0009461 | 0.0025848 | 0.071938 | 0.065055 | -0.0098779 | 0.020294 | -0.0020658 | -0.15106 | 59.6191 | -62.2879 | 59.8251 | -62.1048 | -62.5946 | -62.5442 | -0.018311 | 59.6008 | -62.352 | 59.8434 | -62.1964 | -62.3886 | -62.3428 | 0.01831 | -0.11444 | 0.091552 | 0.20142 | -0.23804 | -0.28839 | -0.25635 | -0.3067 | -0.045777 | -0.13275 | 0.10986 | 0.10986 | -0.036621 | -0.082398 | 0.009156 | -0.036621 | 0.18311 | 122.113 | 0.15564 | 122.1954 | 121.907 | 121.9528 | 121.9254 | 121.907 | -122.0215 | -122.0856 | 122.1313 | 122.1497 | 62.1552 | 62.2879
700.4844 | 122.3373 | -62.2375 | 59.8022 | -0.0060272 | 0.0001345 | 0.05818 | 0.056258 | -0.00085021 | -0.0049155 | -0.0016941 | -0.0021057 | 0.0010894 | 0.072578 | 0.060782 | -0.0079553 | 0.016663 | -0.002493 | 0.022888 | 59.5871 | -62.2742 | 59.9533 | -61.94 | -62.4207 | -62.3886 | 0.16479 | 59.61 | -62.3016 | 59.8709 | -62.0865 | -62.2787 | -62.2742 | -0.036621 | -0.21515 | 0.15106 | 0.29755 | -0.15106 | -0.1831 | -0.11444 | -0.14648 | -0.064087 | -0.19226 | 0.068665 | 0.15106 | -0.036621 | -0.041199 | 0.027466 | 0.022888 | 0.33417 | 122.2275 | 0.21515 | 122.1725 | 121.8613 | 121.9116 | 121.8246 | 121.8475 | -122.0764 | -122.1039 | 122.1909 | 122.1085 | 62.2604 | 62.4023
702.2344 | 122.2778 | -62.2833 | 59.8297 | -0.0060272 | 0.0014163 | 0.059462 | 0.060957 | -0.0040546 | -0.0068381 | -0.0023349 | -0.0051575 | 0.0021576 | 0.070869 | 0.05886 | -0.010305 | 0.017517 | 0.0013522 | -0.004578 | 59.6649 | -62.2787 | 59.8572 | -62.0911 | -62.5122 | -62.5259 | 0.027466 | 59.6786 | -62.3108 | 59.8114 | -62.2238 | -62.4115 | -62.3703 | 0.004577 | -0.16479 | 0.027466 | 0.19226 | -0.24262 | -0.22888 | -0.24719 | -0.23346 | -0.027466 | -0.15106 | -0.018311 | 0.059509 | -0.086975 | -0.12817 | -0.059509 | -0.10071 | 0.18768 | 122.1359 | 0.086975 | 122.1222 | 121.9437 | 121.9894 | 121.9482 | 121.962 | -122.1085 | -122.1405 | 122.1405 | 122.0947 | 62.2787 | 62.3108
703.9844 | 122.2641 | -62.2559 | 59.8251 | -0.0060272 | 0.0026981 | 0.060316 | 0.059676 | 0.00043159 | -0.0059835 | -0.0023349 | -0.0051575 | 0.0025848 | 0.070442 | 0.066123 | -0.010946 | 0.018585 | -0.0016384 | 0.013733 | 59.6283 | -62.2879 | 59.8801 | -62.0544 | -62.5076 | -62.5076 | 0.07782 | 59.6603 | -62.3108 | 59.8434 | -62.1964 | -62.3703 | -62.352 | -0.032044 | -0.19684 | 0.054932 | 0.20142 | -0.25177 | -0.25177 | -0.21973 | -0.21973 | -0.054932 | -0.16479 | 0.018311 | 0.059509 | -0.096131 | -0.11444 | -0.041199 | -0.059509 | 0.23346 | 122.168 | 0.11444 | 122.1542 | 121.9162 | 121.9711 | 121.8842 | 121.9162 | -122.113 | -122.1359 | 122.1359 | 122.0993 | 62.2696 | 62.3337
705.6719 | 122.3648 | -62.2467 | 59.7656 | -0.013657 | 0.0001345 | 0.059889 | 0.058607 | -0.0019184 | -0.0055563 | -0.0044711 | -0.0051575 | -0.00019216 | 0.073006 | 0.059287 | -0.0068871 | 0.015167 | -0.0046292 | 0.004578 | 59.5825 | -62.2559 | 59.9625 | -61.9537 | -62.4069 | -62.3932 | 0.17395 | 59.5825 | -62.3108 | 59.8846 | -62.1002 | -62.2604 | -62.2879 | -0.009155 | -0.1831 | 0.19684 | 0.29297 | -0.14648 | -0.16022 | -0.13733 | -0.15106 | -0.064087 | -0.1831 | 0.11902 | 0.14648 | -0.041199 | -0.013733 | 0.022888 | 0.050354 | 0.30212 | 122.2183 | 0.21057 | 122.1954 | 121.8384 | 121.8933 | 121.8292 | 121.8292 | -122.0215 | -122.0764 | 122.2092 | 122.1313 | 62.2513 | 62.4207
707.4062 | 122.2275 | -62.2971 | 59.8434 | -0.013657 | -0.0002927 | 0.059889 | 0.057967 | -0.00085021 | -0.0070517 | -0.0055393 | -0.0082093 | 0.0017304 | 0.071938 | 0.059501 | -0.0079553 | 0.017731 | -0.0031338 | 0.032043 | 59.6329 | -62.2467 | 59.8663 | -62.059 | -62.5168 | -62.4985 | 0.036621 | 59.6512 | -62.2971 | 59.7748 | -62.2238 | -62.3978 | -62.3978 | 0.050354 | -0.21057 | 0.022888 | 0.23804 | -0.20142 | -0.21973 | -0.25177 | -0.27008 | 0 | -0.19226 | -0.068665 | 0.073242 | -0.10071 | -0.10071 | -0.10071 | -0.10071 | 0.18768 | 122.113 | 0.073242 | 122.0718 | 121.8796 | 121.9482 | 121.9299 | 121.9482 | -122.0901 | -122.1405 | 122.1634 | 122.0718 | 62.3291 | 62.3337
709.1562 | 122.2412 | -62.3062 | 59.8068 | -0.013657 | 0.0012027 | 0.062453 | 0.062453 | -0.0012774 | -0.0042745 | -0.00041227 | -0.0051575 | 0.0027984 | 0.073433 | 0.070609 | -0.0077417 | 0.016663 | -0.0029202 | -0.12817 | 59.6558 | -62.2971 | 59.7839 | -62.1506 | -62.6175 | -62.59 | -0.064087 | 59.6237 | -62.3474 | 59.7656 | -62.2925 | -62.471 | -62.4252 | 0.009155 | -0.15106 | -0.022888 | 0.15564 | -0.28381 | -0.31128 | -0.29297 | -0.32044 | -0.041199 | -0.18311 | -0.041199 | 0.013733 | -0.11902 | -0.16479 | -0.07782 | -0.1236 | 0.14648 | 122.081 | 0.054932 | 122.113 | 121.9528 | 121.9711 | 121.962 | 121.9299 | -122.1039 | -122.1542 | 122.0901 | 122.0718 | 62.178 | 62.2421
710.9062 | 122.3373 | -62.2467 | 59.8068 | -0.013657 | -0.0011471 | 0.059035 | 0.059035 | 0.00043159 | -0.0055563 | -0.0027621 | 0.0009461 | 0.00023504 | 0.071083 | 0.060996 | -0.010305 | 0.016876 | -0.0027066 | 0.032043 | 59.5688 | -62.2559 | 59.9625 | -61.9354 | -62.4207 | -62.4115 | 0.16022 | 59.6283 | -62.2971 | 59.8755 | -62.114 | -62.2971 | -62.3062 | -0.009155 | -0.23804 | 0.15564 | 0.31128 | -0.16479 | -0.17395 | -0.15564 | -0.16479 | -0.050354 | -0.17853 | 0.068664 | 0.13275 | -0.059509 | -0.050354 | -0.009155 | 0 | 0.32043 | 122.2183 | 0.1831 | 122.1725 | 121.8246 | 121.9254 | 121.8155 | 121.875 | -122.0627 | -122.1039 | 122.2092 | 122.1222 | 62.2787 | 62.4069
712.5938 | 122.2229 | -62.2742 | 59.8389 | 0.0092313 | -0.0009335 | 0.059462 | 0.057539 | 0.001286 | -0.0057699 | -0.0014805 | -0.0021057 | 0.0049346 | 0.072365 | 0.056083 | -0.011373 | 0.018158 | -0.0020658 | -0.018311 | 59.6375 | -62.2833 | 59.8343 | -62.0728 | -62.5259 | -62.5168 | 0.032043 | 59.6832 | -62.3108 | 59.7748 | -62.2375 | -62.4069 | -62.4069 | -0.009155 | -0.20142 | -0.004577 | 0.20142 | -0.24262 | -0.25177 | -0.23346 | -0.24262 | -0.036621 | -0.15564 | -0.064087 | 0.036621 | -0.13275 | -0.13275 | -0.09613 | -0.09613 | 0.21057 | 122.1176 | 0.073242 | 122.0856 | 121.9208 | 121.994 | 121.9116 | 121.9574 | -122.1222 | -122.1497 | 122.1085 | 122.0489 | 62.2559 | 62.3062
714.3281 | 122.2321 | -62.2833 | 59.8618 | -0.013657 | -0.0007199 | 0.057967 | 0.059462 | -0.006618 | -0.0066245 | -0.0027621 | 0.0009461 | 0.0017304 | 0.07386 | 0.059501 | -0.0081689 | 0.017303 | -0.0027066 | -0.009155 | 59.6512 | -62.2742 | 59.816 | -62.0911 | -62.5259 | -62.5397 | 0.018311 | 59.6649 | -62.3383 | 59.7702 | -62.2192 | -62.4207 | -62.4298 | 0.009155 | -0.21057 | -0.045776 | 0.19226 | -0.25635 | -0.24262 | -0.2655 | -0.25177 | -0.054932 | -0.19684 | -0.091552 | 0.064087 | -0.14649 | -0.13733 | -0.091553 | -0.082397 | 0.18311 | 122.0901 | 0.11902 | 122.1085 | 121.9254 | 122.0032 | 121.9345 | 121.9482 | -122.1359 | -122.2 | 122.0993 | 122.0535 | 62.2742 | 62.3016
716.0781 | 122.319 | -62.2925 | 59.7885 | -0.0060272 | 0.0009891 | 0.060103 | 0.056685 | 0.001286 | -0.0057699 | 0.00086953 | -0.0051575 | 0.00066224 | 0.071297 | 0.060355 | -0.0098779 | 0.018158 | -0.005911 | -0.082397 | 59.5688 | -62.265 | 59.848 | -62.059 | -62.5259 | -62.4802 | 0 | 59.5871 | -62.3245 | 59.8022 | -62.2055 | -62.3703 | -62.3886 | 0.027465 | -0.21973 | 0.059509 | 0.23346 | -0.18768 | -0.23346 | -0.21515 | -0.26093 | -0.032044 | -0.20142 | 0.013733 | 0.086975 | -0.096131 | -0.07782 | -0.064087 | -0.045776 | 0.20599 | 122.113 | 0.11902 | 122.1268 | 121.8338 | 121.9116 | 121.8613 | 121.8796 | -122.0535 | -122.113 | 122.1405 | 122.0947 | 62.2101 | 62.2925
717.7656 | 122.2595 | -62.2879 | 59.8022 | -0.0060272 | 0.0033389 | 0.062666 | 0.06053 | -0.001491 | -0.0059835 | -0.0019077 | 0.0009461 | 0.00087584 | 0.070442 | 0.0642 | -0.010092 | 0.01709 | -0.0078336 | -0.032043 | 59.642 | -62.2742 | 59.8801 | -62.0499 | -62.5214 | -62.5214 | 0.045776 | 59.6603 | -62.3245 | 59.816 | -62.2284 | -62.439 | -62.4069 | 0.013733 | -0.16022 | 0.07782 | 0.23804 | -0.23346 | -0.23346 | -0.24719 | -0.24719 | -0.036621 | -0.14191 | 0.013733 | 0.059509 | -0.11902 | -0.15106 | -0.082397 | -0.11444 | 0.2243 | 122.1542 | 0.09613 | 122.1405 | 121.9162 | 121.9849 | 121.9299 | 121.9482 | -122.0764 | -122.1268 | 122.168 | 122.1039 | 62.2559 | 62.3337
719.5 | 122.374 | -62.2787 | 59.7794 | -0.0060272 | -0.0002927 | 0.059248 | 0.056685 | -0.00063661 | -0.0066245 | -0.0025485 | -0.0051575 | 0.0023712 | 0.070869 | 0.062918 | -0.0083825 | 0.016449 | -0.0022794 | 0.004578 | 59.5963 | -62.2467 | 59.9304 | -61.9308 | -62.4207 | -62.4023 | 0.15564 | 59.5779 | -62.3062 | 59.9121 | -62.0728 | -62.2604 | -62.2879 | 0.032044 | -0.18311 | 0.15106 | 0.3479 | -0.1236 | -0.14191 | -0.15564 | -0.17395 | -0.027465 | -0.20142 | 0.13275 | 0.20599 | -0.009155 | 0.018311 | 0.01831 | 0.045776 | 0.31586 | 122.1771 | 0.23346 | 122.2183 | 121.843 | 121.8842 | 121.875 | 121.8567 | -122.0261 | -122.0856 | 122.2092 | 122.1909 | 62.2833 | 62.4344
721.2344 | 122.3465 | -62.2696 | 59.7565 | -0.013657 | 0.0018435 | 0.059676 | 0.057539 | 0.0017132 | -0.0076925 | -0.00019867 | -0.0021057 | 0.0017304 | 0.070229 | 0.056937 | -0.010092 | 0.015167 | -0.0031338 | 0 | 59.5963 | -62.2604 | 59.9396 | -61.9675 | -62.4344 | -62.4115 | 0.15106 | 59.6008 | -62.3108 | 59.8984 | -62.0865 | -62.2787 | -62.3154 | 0.009155 | -0.16022 | 0.1831 | 0.30212 | -0.14191 | -0.16479 | -0.15106 | -0.17395 | -0.041199 | -0.15564 | 0.14191 | 0.18311 | -0.045777 | -0.009156 | -0.004578 | 0.032043 | 0.29297 | 122.2 | 0.2243 | 122.2092 | 121.8567 | 121.9116 | 121.8658 | 121.8704 | -122.0169 | -122.0673 | 122.2092 | 122.168 | 62.2696 | 62.4207
722.9844 | 122.3511 | -62.2696 | 59.7748 | 0.0016023 | -0.0007199 | 0.057112 | 0.057112 | -0.0032 | -0.0059835 | -0.0019077 | -0.0051575 | 0.0015166 | 0.070869 | 0.070395 | -0.0092371 | 0.016449 | -0.0046292 | 0.027466 | 59.5642 | -62.265 | 59.9579 | -61.9354 | -62.4252 | -62.4023 | 0.16022 | 59.6054 | -62.2787 | 59.8709 | -62.1048 | -62.2879 | -62.2971 | 0.004577 | -0.21057 | 0.18311 | 0.33417 | -0.13275 | -0.15564 | -0.13733 | -0.16022 | -0.009156 | -0.16937 | 0.096131 | 0.1648 | -0.027466 | -0.018311 | -0.01831 | -0.009155 | 0.32959 | 122.2229 | 0.17395 | 122.1497 | 121.8292 | 121.8842 | 121.8338 | 121.875 | -122.0398 | -122.0535 | 122.2275 | 122.1405 | 62.2971 | 62.4298
724.6719 | 122.3694 | -62.2559 | 59.7794 | 0.0016023 | -0.0009335 | 0.058394 | 0.056685 | -0.0012774 | -0.0064109 | -0.00083947 | -0.0021057 | 0.0010894 | 0.073433 | 0.060782 | -0.010519 | 0.018158 | -0.0056974 | 0.022888 | 59.5734 | -62.2742 | 59.967 | -61.9171 | -62.3978 | -62.384 | 0.16022 | 59.5917 | -62.3062 | 59.8938 | -62.1002 | -62.2604 | -62.3108 | -0.018311 | -0.20599 | 0.18768 | 0.33875 | -0.12817 | -0.14191 | -0.10986 | -0.1236 | -0.050354 | -0.18768 | 0.11444 | 0.15564 | -0.054932 | -0.004578 | -0.004578 | 0.045776 | 0.35706 | 122.2412 | 0.20599 | 122.2 | 121.8475 | 121.8979 | 121.8292 | 121.8475 | -122.0535 | -122.0856 | 122.2229 | 122.1497 | 62.2787 | 62.4161
726.4062 | 122.2961 | -62.2559 | 59.8251 | -0.0060272 | 0.0024845 | 0.059248 | 0.057753 | -0.0023456 | -0.0068381 | -0.0023349 | -0.0051575 | 0.001944 | 0.073647 | 0.060569 | -0.0098779 | 0.016449 | -0.0033474 | 0.050354 | 59.5779 | -62.2787 | 59.935 | -61.9858 | -62.4573 | -62.4298 | 0.11444 | 59.6603 | -62.3154 | 59.8343 | -62.1735 | -62.3566 | -62.3383 | -0.022889 | -0.24719 | 0.10986 | 0.27008 | -0.17395 | -0.20142 | -0.15106 | -0.17853 | -0.05951 | -0.16479 | 0.009156 | 0.082397 | -0.082398 | -0.10071 | -0.022888 | -0.041198 | 0.29297 | 122.2137 | 0.14191 | 122.1497 | 121.8567 | 121.9757 | 121.8338 | 121.9162 | -122.1039 | -122.1405 | 122.1909 | 122.0901 | 62.3062 | 62.3703
728.1406 | 122.2778 | -62.2833 | 59.816 | -0.013657 | 0.0009891 | 0.05818 | 0.060957 | 0.001286 | -0.0064109 | -0.00083947 | -0.0021057 | 0.0032256 | 0.072578 | 0.060355 | -0.0081689 | 0.018799 | -0.002493 | 0.013733 | 59.6237 | -62.3016 | 59.8892 | -62.0636 | -62.5214 | -62.4985 | 0.07782 | 59.6832 | -62.3383 | 59.8297 | -62.1918 | -62.3932 | -62.3749 | -0.018311 | -0.19226 | 0.073242 | 0.21973 | -0.21515 | -0.23804 | -0.19684 | -0.21973 | -0.054932 | -0.13275 | 0.013733 | 0.091553 | -0.091553 | -0.10986 | -0.036621 | -0.054931 | 0.23804 | 122.1909 | 0.14648 | 122.168 | 121.9254 | 122.0215 | 121.907 | 121.9666 | -122.1176 | -122.1542 | 122.1725 | 122.113 | 62.2971 | 62.3611
729.8281 | 122.2321 | -62.2879 | 59.8251 | -0.013657 | 0.0003483 | 0.059035 | 0.057753 | -0.0068316 | -0.0040609 | 0.0010831 | -0.0082093 | 0.003653 | 0.071938 | 0.071463 | -0.0088097 | 0.017944 | -0.003561 | -0.022888 | 59.6375 | -62.265 | 59.8389 | -62.114 | -62.5351 | -62.5351 | 0.009155 | 59.6832 | -62.3337 | 59.7931 | -62.2284 | -62.4207 | -62.4023 | 0.022888 | -0.18768 | 0.013733 | 0.17395 | -0.24719 | -0.24719 | -0.27008 | -0.27008 | -0.045776 | -0.14191 | -0.032043 | 0.059509 | -0.11444 | -0.13275 | -0.068665 | -0.086975 | 0.15106 | 122.1039 | 0.10528 | 122.1268 | 121.9025 | 122.0169 | 121.9254 | 121.9711 | -122.0901 | -122.1588 | 122.1268 | 122.081 | 62.265 | 62.2971
731.5625 | 122.3373 | -62.2971 | 59.7244 | -0.0060272 | 0.0024845 | 0.061598 | 0.058821 | -0.0012774 | -0.0044883 | -0.0044711 | -0.0051575 | -0.00083316 | 0.07151 | 0.071463 | -0.0092371 | 0.016663 | -0.0054838 | -0.073242 | 59.5688 | -62.265 | 59.9167 | -61.9858 | -62.4847 | -62.4527 | 0.07782 | 59.5688 | -62.3245 | 59.8526 | -62.1643 | -62.3611 | -62.3428 | 0.032043 | -0.15564 | 0.19226 | 0.31128 | -0.15564 | -0.18768 | -0.18768 | -0.21973 | -0.027466 | -0.15564 | 0.12817 | 0.13275 | -0.045776 | -0.064087 | -0.01831 | -0.036621 | 0.27924 | 122.1817 | 0.16022 | 122.1771 | 121.8338 | 121.8933 | 121.8658 | 121.8658 | -121.9894 | -122.0489 | 122.2137 | 122.1497 | 62.2238 | 62.3749
733.3125 | 122.3465 | -62.2742 | 59.761 | -0.0060272 | 0.0018435 | 0.062025 | 0.056258 | -0.003841 | -0.0064109 | -0.00083947 | 0.0009461 | 0.00087584 | 0.07151 | 0.06655 | -0.0092371 | 0.017731 | 0.0017794 | -0.09613 | 59.5505 | -62.2971 | 59.9121 | -61.9904 | -62.4847 | -62.4435 | 0.064087 | 59.5734 | -62.3199 | 59.8709 | -62.1643 | -62.3474 | -62.3245 | -0.022888 | -0.21057 | 0.15106 | 0.28381 | -0.16937 | -0.21057 | -0.14648 | -0.18768 | -0.045776 | -0.18768 | 0.10986 | 0.10986 | -0.050354 | -0.073242 | -0.004578 | -0.027466 | 0.3067 | 122.2092 | 0.15564 | 122.1909 | 121.8475 | 121.8933 | 121.8246 | 121.8475 | -122.0581 | -122.081 | 122.1863 | 122.1451 | 62.178 | 62.3383
735.0625 | 122.3328 | -62.2879 | 59.7473 | -0.013657 | 0.0041935 | 0.061598 | 0.057967 | -0.00020941 | -0.0029929 | -0.0040439 | -0.0021057 | 0.0034392 | 0.072578 | 0.063987 | -0.01116 | 0.016235 | -0.0014248 | -0.082397 | 59.5367 | -62.2787 | 59.9213 | -61.9949 | -62.5076 | -62.4664 | 0.050354 | 59.5825 | -62.3154 | 59.8526 | -62.146 | -62.3383 | -62.3199 | 0.009155 | -0.21057 | 0.17395 | 0.29297 | -0.17853 | -0.21973 | -0.18768 | -0.22888 | -0.027466 | -0.16479 | 0.10529 | 0.14191 | -0.032043 | -0.050354 | -0.004577 | -0.022888 | 0.28381 | 122.2 | 0.16937 | 122.168 | 121.8155 | 121.8979 | 121.8246 | 121.8704 | -122.0261 | -122.0627 | 122.2092 | 122.1405 | 62.2055 | 62.3383
736.75 | 122.3465 | -62.2742 | 59.7794 | -0.013657 | -0.0009335 | 0.059462 | 0.057539 | -0.00042301 | -0.0038473 | -0.0019077 | -0.0021057 | -0.0010468 | 0.069588 | 0.063346 | -0.0088097 | 0.018585 | -0.0046292 | -0.068665 | 59.5825 | -62.2879 | 59.8892 | -62.0224 | -62.4756 | -62.4664 | 0.068665 | 59.6191 | -62.3016 | 59.8846 | -62.1368 | -62.2879 | -62.3199 | -0.013733 | -0.19684 | 0.10986 | 0.25177 | -0.19226 | -0.20142 | -0.17853 | -0.18768 | -0.027466 | -0.16022 | 0.10529 | 0.13733 | -0.045776 | -0.013733 | -0.01831 | 0.013733 | 0.2655 | 122.1771 | 0.1648 | 122.1863 | 121.8704 | 121.9208 | 121.8567 | 121.8933 | -122.0673 | -122.081 | 122.1634 | 122.1588 | 62.2055 | 62.3428
738.4844 | 122.3099 | -62.2833 | 59.7794 | -0.013657 | 0.0005619 | 0.059889 | 0.056258 | 0.0032086 | -0.0055563 | -0.0023349 | -0.0021057 | 0.0017304 | 0.072151 | 0.0642 | -0.0090235 | 0.016876 | -0.0022794 | -0.073242 | 59.5734 | -62.2833 | 59.8663 | -62.0499 | -62.5168 | -62.4939 | 0.041199 | 59.61 | -62.3108 | 59.8251 | -62.1689 | -62.3566 | -62.352 | 0 | -0.20599 | 0.086975 | 0.23346 | -0.21057 | -0.23346 | -0.21057 | -0.23346 | -0.027466 | -0.16937 | 0.045776 | 0.11444 | -0.068665 | -0.073242 | -0.041199 | -0.045776 | 0.23346 | 122.1497 | 0.14191 | 122.1359 | 121.8567 | 121.9208 | 121.8567 | 121.8933 | -122.0627 | -122.0901 | 122.1497 | 122.1085 | 62.2101 | 62.3245
740.2344 | 122.3282 | -62.3199 | 59.7473 | -0.013657 | 0.0029117 | 0.062666 | 0.057326 | 0.002995 | -0.0032065 | -0.0016941 | -0.0051575 | 0.0025848 | 0.072151 | 0.071463 | -0.0085961 | 0.017731 | -0.0046292 | -0.086975 | 59.5688 | -62.2604 | 59.9258 | -61.9858 | -62.4893 | -62.4664 | 0.07782 | 59.5917 | -62.2925 | 59.848 | -62.178 | -62.3657 | -62.3428 | 0.059509 | -0.17853 | 0.17853 | 0.33417 | -0.14648 | -0.16937 | -0.20599 | -0.22888 | 0.027466 | -0.15564 | 0.10071 | 0.14191 | -0.022888 | -0.045777 | -0.050354 | -0.073243 | 0.27466 | 122.1863 | 0.11444 | 122.1405 | 121.8292 | 121.8842 | 121.8887 | 121.9116 | -122.0078 | -122.0398 | 122.2458 | 122.168 | 62.233 | 62.3978
741.9688 | 122.319 | -62.3199 | 59.761 | -0.013657 | 0.0041935 | 0.061385 | 0.061598 | -0.0027728 | -0.0068381 | -0.00041227 | -0.0051575 | -0.00019216 | 0.070869 | 0.065909 | -0.011373 | 0.017944 | -0.0018522 | -0.082397 | 59.5871 | -62.2833 | 59.9075 | -62.0132 | -62.5076 | -62.4756 | 0.064087 | 59.5871 | -62.3337 | 59.8434 | -62.1872 | -62.3566 | -62.3383 | 0.036621 | -0.17395 | 0.14649 | 0.3067 | -0.15564 | -0.18768 | -0.19226 | -0.2243 | -0.013733 | -0.17395 | 0.082398 | 0.13275 | -0.018311 | -0.036621 | -0.004578 | -0.022888 | 0.27008 | 122.1909 | 0.14648 | 122.1771 | 121.8704 | 121.9208 | 121.907 | 121.907 | -122.0444 | -122.0947 | 122.2275 | 122.1634 | 62.2375 | 62.384
743.6406 | 122.2458 | -62.265 | 59.8206 | 0.0016023 | -0.0005063 | 0.058394 | 0.060103 | -0.0017048 | -0.0089743 | -0.0021213 | -0.0051575 | 0.0021576 | 0.071724 | 0.055655 | -0.010092 | 0.017303 | -0.0016384 | -0.013733 | 59.6558 | -62.2742 | 59.8343 | -62.1048 | -62.5442 | -62.5259 | 0.032043 | 59.6832 | -62.3245 | 59.7839 | -62.2238 | -62.3978 | -62.3795 | -0.009155 | -0.16479 | 0.013733 | 0.16022 | -0.26093 | -0.27923 | -0.25177 | -0.27008 | -0.059509 | -0.13733 | -0.036621 | 0.041199 | -0.11444 | -0.13275 | -0.054932 | -0.073242 | 0.16937 | 122.1085 | 0.10071 | 122.1085 | 121.9299 | 122.0078 | 121.9208 | 121.9482 | -122.0947 | -122.1451 | 122.0993 | 122.049 | 62.2513 | 62.2971
745.3906 | 122.2183 | -62.2833 | 59.8251 | -0.021286 | 0.0012027 | 0.062025 | 0.056471 | -0.00042301 | -0.0076925 | -0.0027621 | -0.0021057 | 0.0025848 | 0.071938 | 0.065268 | -0.0075281 | 0.018372 | -0.0005704 | 0.036621 | 59.5963 | -62.265 | 59.8755 | -62.0544 | -62.5076 | -62.5168 | 0.054932 | 59.6695 | -62.3291 | 59.7794 | -62.2192 | -62.3978 | -62.4023 | 0.01831 | -0.22888 | 0.050354 | 0.22888 | -0.23346 | -0.2243 | -0.25177 | -0.24261 | -0.045777 | -0.15564 | -0.045776 | 0.064087 | -0.11902 | -0.11444 | -0.073242 | -0.068664 | 0.21057 | 122.1405 | 0.10986 | 122.1085 | 121.8613 | 121.9986 | 121.8796 | 121.9528 | -122.0901 | -122.1542 | 122.1588 | 122.0627 | 62.3199 | 62.3383
747.0625 | 122.2687 | -62.2787 | 59.816 | 0.0016023 | 0.0024845 | 0.060744 | 0.05818 | 0.0025678 | -0.0051291 | -0.00083947 | -0.0021057 | 0.001944 | 0.074501 | 0.063559 | -0.0085961 | 0.016663 | -0.0031338 | 0 | 59.6329 | -62.2787 | 59.8846 | -62.0407 | -62.5214 | -62.5076 | 0.068665 | 59.6603 | -62.3062 | 59.8114 | -62.1918 | -62.3886 | -62.3566 | 0 | -0.1831 | 0.068665 | 0.23804 | -0.22888 | -0.24261 | -0.22888 | -0.24261 | -0.027465 | -0.15564 | -0.004578 | 0.086976 | -0.077819 | -0.10986 | -0.050354 | -0.082398 | 0.23804 | 122.1634 | 0.11444 | 122.1176 | 121.9116 | 121.9666 | 121.9116 | 121.9391 | -122.0947 | -122.1222 | 122.1634 | 122.0901 | 62.2787 | 62.3474
748.7969 | 122.2733 | -62.2559 | 59.7977 | 0.0016023 | 0.0005619 | 0.061171 | 0.06053 | -0.00042301 | -0.0072653 | -0.0019077 | -0.0051575 | 0.0021576 | 0.073006 | 0.0689 | -0.0068871 | 0.017517 | -0.0022794 | 0 | 59.6191 | -62.3062 | 59.8846 | -62.0361 | -62.4985 | -62.5031 | 0.07782 | 59.6558 | -62.3062 | 59.8389 | -62.1826 | -62.3703 | -62.3383 | -0.050354 | -0.17853 | 0.086976 | 0.21973 | -0.24719 | -0.24262 | -0.19684 | -0.19226 | -0.050354 | -0.14191 | 0.041199 | 0.073242 | -0.082398 | -0.11444 | -0.032044 | -0.064087 | 0.27008 | 122.1909 | 0.1236 | 122.1451 | 121.9254 | 121.962 | 121.875 | 121.9116 | -122.1039 | -122.1039 | 122.1405 | 122.0947 | 62.2559 | 62.3337
750.5469 | 122.3465 | -62.2925 | 59.7473 | -0.013657 | 0.0020571 | 0.060744 | 0.058821 | 0.0017132 | -0.0044883 | -0.00019867 | -0.0051575 | 0.0032256 | 0.07151 | 0.063132 | -0.0090235 | 0.01944 | -0.0022794 | -0.091553 | 59.5779 | -62.3199 | 59.8984 | -62.0087 | -62.4939 | -62.4847 | 0.041199 | 59.5779 | -62.3474 | 59.8663 | -62.1506 | -62.352 | -62.2742 | -0.027466 | -0.16937 | 0.15106 | 0.28381 | -0.19226 | -0.20142 | -0.16479 | -0.17395 | -0.054932 | -0.16937 | 0.11902 | 0.14191 | 0.01831 | -0.05951 | 0.073242 | -0.004578 | 0.31128 | 122.2183 | 0.19684 | 122.2137 | 121.8979 | 121.9254 | 121.8704 | 121.8704 | -122.0673 | -122.0947 | 122.1909 | 122.1588 | 62.2009 | 62.3337
752.2969 | 122.2549 | -62.2696 | 59.8114 | 0.0016023 | 0.0029117 | 0.058821 | 0.059676 | -0.0010638 | -0.0066245 | -0.0016941 | -0.0051575 | 0.0045074 | 0.07151 | 0.065909 | -0.0085961 | 0.019012 | -0.0065518 | -0.018311 | 59.6375 | -62.3016 | 59.8846 | -62.0407 | -62.5259 | -62.5076 | 0.054932 | 59.6466 | -62.3383 | 59.816 | -62.2101 | -62.4069 | -62.3428 | -0.032044 | -0.17395 | 0.073243 | 0.22888 | -0.23804 | -0.25635 | -0.20599 | -0.2243 | -0.068665 | -0.16479 | 0.004578 | 0.059509 | -0.073242 | -0.13733 | -0.004577 | -0.068664 | 0.26093 | 122.1863 | 0.12817 | 122.1542 | 121.9391 | 121.9849 | 121.907 | 121.9162 | -122.113 | -122.1497 | 122.1542 | 122.0856 | 62.2513 | 62.3245
753.9688 | 122.3145 | -62.2925 | 59.7839 | -0.013657 | -0.0011471 | 0.060316 | 0.057326 | -0.0010638 | -0.0044883 | -0.0027621 | -0.0021057 | 0.0017304 | 0.073647 | 0.06185 | -0.0064599 | 0.018158 | -0.0009976 | -0.11902 | 59.5688 | -62.2787 | 59.8801 | -62.0178 | -62.5305 | -62.4756 | 0.018311 | 59.5734 | -62.3154 | 59.8343 | -62.1918 | -62.3703 | -62.3199 | 0.013732 | -0.21515 | 0.09613 | 0.27466 | -0.18311 | -0.23804 | -0.19684 | -0.25177 | -0.022889 | -0.21057 | 0.050354 | 0.10071 | -0.027466 | -0.07782 | -0.004577 | -0.054931 | 0.26093 | 122.1588 | 0.1236 | 122.1497 | 121.8475 | 121.8887 | 121.8613 | 121.8658 | -122.0627 | -122.0993 | 122.1725 | 122.1268 | 62.1735 | 62.3108
755.7188 | 122.3511 | -62.2513 | 59.761 | 0.0016023 | -0.0007199 | 0.059676 | 0.057326 | -0.0012774 | -0.0059835 | -0.00083947 | -0.0082093 | 0.0027984 | 0.07151 | 0.063987 | -0.0079553 | 0.018372 | -0.002493 | -0.022888 | 59.5734 | -62.265 | 59.9213 | -61.9629 | -62.439 | -62.4298 | 0.12817 | 59.6237 | -62.3062 | 59.8938 | -62.1002 | -62.2742 | -62.2696 | -0.013733 | -0.18768 | 0.16022 | 0.28839 | -0.17853 | -0.18768 | -0.1648 | -0.17395 | -0.054931 | -0.13733 | 0.13275 | 0.15106 | -0.01831 | -0.022888 | 0.036621 | 0.032043 | 0.30212 | 122.1863 | 0.20599 | 122.2 | 121.8384 | 121.9299 | 121.8246 | 121.875 | -122.0261 | -122.0673 | 122.1725 | 122.1451 | 62.2284 | 62.3795
757.4688 | 122.2092 | -62.2833 | 59.8389 | -0.0060272 | -0.0005063 | 0.058821 | 0.057967 | -0.0012774 | -0.0070517 | -0.0023349 | -0.0021057 | 0.0010894 | 0.073006 | 0.061637 | -0.0092371 | 0.01709 | -0.0012112 | -0.004578 | 59.642 | -62.2879 | 59.848 | -62.0819 | -62.5214 | -62.5122 | 0.041199 | 59.6786 | -62.3016 | 59.7839 | -62.2101 | -62.4023 | -62.3795 | -0.004578 | -0.19684 | 0.009155 | 0.20142 | -0.22888 | -0.23804 | -0.2243 | -0.23346 | -0.018311 | -0.16022 | -0.054931 | 0.073242 | -0.096131 | -0.11902 | -0.07782 | -0.10071 | 0.20599 | 122.1359 | 0.091553 | 122.0856 | 121.9299 | 121.9803 | 121.9254 | 121.962 | -122.1268 | -122.1405 | 122.1313 | 122.0673 | 62.2787 | 62.3245
759.2188 | 122.3465 | -62.2375 | 59.7565 | -0.0060272 | -0.0017881 | 0.060103 | 0.059889 | -0.0025592 | -0.0059835 | -0.0027621 | -0.0051575 | 0.00066224 | 0.072792 | 0.059287 | -0.0085961 | 0.015808 | -0.0005704 | -0.013733 | 59.5825 | -62.3016 | 59.9258 | -61.9675 | -62.439 | -62.4161 | 0.12817 | 59.6375 | -62.3154 | 59.8892 | -62.114 | -62.265 | -62.2742 | -0.064087 | -0.17395 | 0.16937 | 0.27008 | -0.17853 | -0.20142 | -0.11444 | -0.13733 | -0.07782 | -0.11902 | 0.13275 | 0.1236 | -0.036621 | -0.027466 | 0.041199 | 0.050354 | 0.33417 | 122.2275 | 0.20142 | 122.2046 | 121.8842 | 121.9528 | 121.8201 | 121.875 | -122.0581 | -122.0718 | 122.1634 | 122.1268 | 62.2238 | 62.3657
760.9688 | 122.3511 | -62.265 | 59.7794 | -0.013657 | -0.0026425 | 0.057967 | 0.057967 | -0.0034136 | -0.0070517 | -0.00041227 | -0.0021057 | 0.001303 | 0.072792 | 0.062278 | -0.010519 | 0.020081 | -0.003561 | 0.018311 | 59.5688 | -62.2696 | 59.9533 | -61.94 | -62.4161 | -62.3932 | 0.1831 | 59.5963 | -62.2879 | 59.8892 | -62.1048 | -62.2742 | -62.2925 | -0.004577 | -0.21057 | 0.17395 | 0.32501 | -0.12817 | -0.15106 | -0.1236 | -0.14648 | -0.022888 | -0.18311 | 0.10986 | 0.16022 | -0.027465 | -0.009155 | -0.004577 | 0.013733 | 0.32959 | 122.2229 | 0.18311 | 122.1771 | 121.8384 | 121.8842 | 121.8338 | 121.8613 | -122.049 | -122.0673 | 122.2183 | 122.1542 | 62.2833 | 62.4481
762.6562 | 122.2183 | -62.3154 | 59.816 | -0.0060272 | 0.0007755 | 0.059462 | 0.061812 | 0.001286 | -0.0070517 | -0.0021213 | -0.0021057 | 0.0032256 | 0.073006 | 0.067618 | -0.0098779 | 0.018158 | -0.0048428 | -0.032043 | 59.6283 | -62.2925 | 59.8618 | -62.0773 | -62.558 | -62.5442 | 0.004578 | 59.6512 | -62.3383 | 59.7748 | -62.2604 | -62.4573 | -62.4207 | 0.022889 | -0.18768 | 0.045776 | 0.23804 | -0.22888 | -0.24261 | -0.25177 | -0.2655 | -0.022888 | -0.16479 | -0.041199 | 0.054932 | -0.10529 | -0.14191 | -0.082397 | -0.11902 | 0.21515 | 122.1542 | 0.07782 | 122.113 | 121.9208 | 121.9894 | 121.9437 | 121.9666 | -122.1085 | -122.1542 | 122.1771 | 122.0901 | 62.2833 | 62.3199
764.3906 | 122.2229 | -62.3062 | 59.8297 | -0.013657 | -0.0024289 | 0.058821 | 0.058394 | -0.0027728 | -0.0053427 | -0.0010531 | -0.0051575 | 0.0025848 | 0.07151 | 0.055228 | -0.0077417 | 0.016663 | -0.002493 | -0.022888 | 59.6466 | -62.265 | 59.8251 | -62.0728 | -62.5259 | -62.5259 | 0.013733 | 59.6649 | -62.3428 | 59.7885 | -62.2238 | -62.4207 | -62.4161 | 0.041198 | -0.18311 | -0.004578 | 0.23346 | -0.21973 | -0.21973 | -0.26093 | -0.26093 | -0.036621 | -0.16479 | -0.041199 | 0.082397 | -0.10986 | -0.11444 | -0.073243 | -0.07782 | 0.19226 | 122.0901 | 0.11902 | 122.1313 | 121.9116 | 122.0078 | 121.9528 | 121.9711 | -122.0947 | -122.1725 | 122.1313 | 122.0947 | 62.2833 | 62.3199
766.1406 | 122.3053 | -62.3016 | 59.7748 | -0.0060272 | 0.0003483 | 0.061598 | 0.056258 | -0.0029864 | -0.0068381 | -0.0034031 | -0.0082093 | -0.00061956 | 0.070442 | 0.066123 | -0.0092371 | 0.01709 | -0.0039884 | -0.091553 | 59.5779 | -62.2879 | 59.8755 | -62.0316 | -62.5259 | -62.471 | 0.004578 | 59.5871 | -62.3291 | 59.8206 | -62.1826 | -62.3749 | -62.3749 | 0.013733 | -0.19684 | 0.10071 | 0.27008 | -0.16937 | -0.2243 | -0.1831 | -0.23804 | -0.027466 | -0.18768 | 0.045777 | 0.11902 | -0.073242 | -0.073242 | -0.045776 | -0.045776 | 0.25635 | 122.1634 | 0.14648 | 122.1497 | 121.8658 | 121.9162 | 121.8796 | 121.8887 | -122.0627 | -122.1039 | 122.1771 | 122.1222 | 62.2101 | 62.3062
767.8125 | 122.2321 | -62.2925 | 59.7839 | -0.0060272 | 0.0029117 | 0.062666 | 0.062666 | 0.001286 | -0.0029929 | -0.0040439 | -0.0021057 | 0.0032256 | 0.072578 | 0.0642 | -0.0094507 | 0.016449 | -0.0016384 | -0.086975 | 59.6283 | -62.3199 | 59.8251 | -62.146 | -62.6083 | -62.5671 | -0.073242 | 59.6512 | -62.3291 | 59.7519 | -62.2787 | -62.4802 | -62.4344 | -0.027466 | -0.15564 | 0.041198 | 0.14648 | -0.27466 | -0.31586 | -0.24719 | -0.28839 | -0.036622 | -0.13275 | -0.032044 | 0.013732 | -0.14191 | -0.18768 | -0.10529 | -0.15106 | 0.17395 | 122.1451 | 0.050354 | 122.081 | 121.9482 | 121.9803 | 121.9208 | 121.9437 | -122.1039 | -122.113 | 122.1176 | 122.0444 | 62.2055 | 62.2192
769.5625 | 122.3145 | -62.2879 | 59.7519 | -0.0060272 | 0.0033389 | 0.059462 | 0.057753 | 0.0010724 | -0.0040609 | -0.0066073 | -0.0051575 | -0.00019216 | 0.07386 | 0.060355 | -0.0090235 | 0.017731 | 0.0004978 | -0.09613 | 59.5551 | -62.2787 | 59.8709 | -62.0224 | -62.5168 | -62.4893 | 0.013733 | 59.6146 | -62.3199 | 59.8297 | -62.2055 | -62.3703 | -62.3703 | 0.009155 | -0.19684 | 0.11902 | 0.2655 | -0.20142 | -0.22888 | -0.21057 | -0.23804 | -0.032043 | -0.13733 | 0.07782 | 0.082398 | -0.082397 | -0.082397 | -0.050354 | -0.050354 | 0.25635 | 122.1497 | 0.11444 | 122.1497 | 121.8338 | 121.9345 | 121.843 | 121.9025 | -122.0306 | -122.0718 | 122.1588 | 122.1176 | 62.1918 | 62.3016
771.2656 | 122.3053 | -62.2787 | 59.7198 | -0.021286 | 0.0033389 | 0.059462 | 0.056471 | -0.0012774 | -0.0064109 | -0.0016941 | -0.0051575 | 0.00087584 | 0.072792 | 0.057151 | -0.0092371 | 0.01709 | 0.000925 | -0.091553 | 59.5734 | -62.2925 | 59.9075 | -62.0041 | -62.5214 | -62.4847 | 0.050354 | 59.5596 | -62.3428 | 59.8389 | -62.178 | -62.352 | -62.3611 | -0.013732 | -0.14649 | 0.18768 | 0.27466 | -0.20599 | -0.24261 | -0.19226 | -0.22888 | -0.064086 | -0.16022 | 0.11902 | 0.10071 | -0.082397 | -0.073242 | -0.018311 | -0.009156 | 0.28839 | 122.2 | 0.16479 | 122.1817 | 121.8658 | 121.9025 | 121.8521 | 121.8384 | -122.0123 | -122.0627 | 122.1863 | 122.1176 | 62.1872 | 62.3291
773 | 122.3511 | -62.2925 | 59.7427 | -0.013657 | 0.0046207 | 0.060103 | 0.057112 | -0.0023456 | -0.0068381 | -0.0016941 | -0.0051575 | 0.00087584 | 0.073006 | 0.069114 | -0.01116 | 0.019226 | -0.004202 | -0.082397 | 59.5642 | -62.2833 | 59.9167 | -61.9949 | -62.4985 | -62.4619 | 0.059509 | 59.61 | -62.3291 | 59.8709 | -62.1323 | -62.3245 | -62.3199 | 0.009155 | -0.17853 | 0.17395 | 0.29755 | -0.16937 | -0.20599 | -0.17853 | -0.21515 | -0.036622 | -0.13275 | 0.12817 | 0.16022 | -0.027466 | -0.032044 | 0.009156 | 0.004578 | 0.28839 | 122.2 | 0.19684 | 122.2 | 121.8475 | 121.9391 | 121.8567 | 121.9025 | -122.0261 | -122.0718 | 122.2092 | 122.1634 | 62.2101 | 62.352
774.75 | 122.3145 | -62.2971 | 59.7702 | 0.0016023 | -0.0002927 | 0.062025 | 0.057967 | -0.0034136 | -0.0059835 | -0.0036167 | -0.0051575 | 0.001303 | 0.070869 | 0.063559 | -0.0098779 | 0.015808 | 0.000925 | -0.10986 | 59.5825 | -62.3062 | 59.8663 | -62.0453 | -62.5214 | -62.4802 | 0.009155 | 59.6237 | -62.3428 | 59.8297 | -62.2009 | -62.384 | -62.352 | -0.009155 | -0.18768 | 0.09613 | 0.25177 | -0.18311 | -0.2243 | -0.17395 | -0.21515 | -0.045776 | -0.14649 | 0.059509 | 0.09613 | -0.054932 | -0.086975 | -0.009156 | -0.041199 | 0.26093 | 122.1725 | 0.14191 | 122.1725 | 121.8887 | 121.9666 | 121.8796 | 121.9208 | -122.0764 | -122.113 | 122.1634 | 122.1268 | 62.1872 | 62.3062
776.4375 | 122.2366 | -62.3062 | 59.7839 | -0.0060272 | 0.0050479 | 0.059889 | 0.062453 | 0.00043159 | -0.0049155 | -0.0016941 | -0.0051575 | 0.003653 | 0.072365 | 0.062918 | -0.010732 | 0.018158 | 0.0004978 | -0.12817 | 59.6191 | -62.3199 | 59.7839 | -62.1643 | -62.6266 | -62.5809 | -0.086975 | 59.6558 | -62.352 | 59.7702 | -62.2833 | -62.4985 | -62.4069 | -0.013733 | -0.16479 | 0 | 0.14191 | -0.27466 | -0.32044 | -0.26093 | -0.3067 | -0.045777 | -0.12817 | -0.013733 | 0.022888 | -0.10071 | -0.19226 | -0.054931 | -0.14648 | 0.15564 | 122.1039 | 0.068665 | 122.1222 | 121.9391 | 122.0078 | 121.9254 | 121.962 | -122.1039 | -122.1359 | 122.0901 | 122.0764 | 62.178 | 62.2192
778.1875 | 122.374 | -62.265 | 59.7748 | -0.013657 | -0.0013607 | 0.06053 | 0.057967 | 0.0032086 | -0.0072653 | 1.4934e-05 | 0.0009461 | 0.0017304 | 0.069588 | 0.057792 | -0.0096643 | 0.01709 | -0.0016384 | 0.018311 | 59.5779 | -62.2696 | 59.9487 | -61.9263 | -62.4207 | -62.4161 | 0.17853 | 59.5963 | -62.2696 | 59.9213 | -62.0728 | -62.2696 | -62.2238 | -0.004577 | -0.19684 | 0.17395 | 0.33874 | -0.15106 | -0.15564 | -0.14648 | -0.15106 | -0.004577 | -0.17853 | 0.14648 | 0.19226 | 0.041199 | -0.004577 | 0.045776 | 0 | 0.34332 | 122.2183 | 0.19684 | 122.1909 | 121.8475 | 121.8658 | 121.843 | 121.8613 | -122.0444 | -122.0444 | 122.2137 | 122.1863 | 62.2833 | 62.4435
779.875 | 122.2961 | -62.2604 | 59.7656 | -0.0060272 | 0.0007755 | 0.060744 | 0.057967 | 0.0023542 | -0.0072653 | -0.0025485 | 0.0009461 | 0.0032256 | 0.073006 | 0.069968 | -0.0094507 | 0.017517 | -0.0037748 | -0.10071 | 59.5688 | -62.2879 | 59.8892 | -62.0041 | -62.5351 | -62.471 | 0.036621 | 59.6054 | -62.3245 | 59.848 | -62.1826 | -62.3611 | -62.2238 | -0.027466 | -0.19684 | 0.1236 | 0.25635 | -0.21057 | -0.27466 | -0.1831 | -0.24719 | -0.064087 | -0.16022 | 0.082397 | 0.07782 | 0.036621 | -0.10071 | 0.10071 | -0.036621 | 0.28381 | 122.1771 | 0.14191 | 122.1725 | 121.8567 | 121.9299 | 121.8292 | 121.8658 | -122.0535 | -122.0901 | 122.1497 | 122.1085 | 62.1597 | 62.2971
781.6094 | 122.3511 | -62.2787 | 59.7382 | 0.0016023 | 0.0020571 | 0.060103 | 0.059248 | -0.0034136 | -0.0074789 | -0.0040439 | -0.0051575 | 0.00023504 | 0.070442 | 0.063773 | -0.011373 | 0.018799 | -0.0050564 | -0.13275 | 59.6008 | -62.3016 | 59.8846 | -62.0453 | -62.5351 | -62.5031 | 0.022888 | 59.6008 | -62.3199 | 59.8709 | -62.1643 | -62.3795 | -62.178 | -0.022888 | -0.13733 | 0.14648 | 0.23346 | -0.2243 | -0.25635 | -0.20142 | -0.23346 | -0.041198 | -0.13733 | 0.13275 | 0.11444 | 0.10071 | -0.10071 | 0.14191 | -0.05951 | 0.25635 | 122.1863 | 0.15564 | 122.1909 | 121.9025 | 121.9208 | 121.8796 | 121.8796 | -122.0398 | -122.0581 | 122.1634 | 122.1497 | 62.146 | 62.3016
783.3594 | 122.3373 | -62.2833 | 59.7519 | -0.0060272 | 0.0020571 | 0.060103 | 0.061171 | -0.0010638 | -0.0061971 | -0.0014805 | -0.0021057 | 2.1442e-05 | 0.073647 | 0.065482 | -0.010732 | 0.018585 | -0.0039884 | -0.14191 | 59.6237 | -62.3062 | 59.8572 | -62.0728 | -62.5671 | -62.5259 | -0.013733 | 59.5917 | -62.3383 | 59.8663 | -62.178 | -62.3703 | -62.2879 | -0.022888 | -0.12817 | 0.10529 | 0.21057 | -0.24262 | -0.28381 | -0.21973 | -0.26093 | -0.054932 | -0.16022 | 0.11444 | 0.10528 | -0.004578 | -0.086975 | 0.050354 | -0.032043 | 0.23346 | 122.1634 | 0.16022 | 122.2046 | 121.9299 | 121.9299 | 121.907 | 121.875 | -122.0581 | -122.0901 | 122.1405 | 122.1497 | 62.1414 | 62.2696
785.125 | 122.2687 | -62.3108 | 59.8022 | -0.013657 | 0.0035525 | 0.060103 | 0.060957 | 0.0021406 | -0.0064109 | -0.0042575 | -0.0021057 | 0.0045074 | 0.071938 | 0.071677 | -0.011373 | 0.018799 | 0.0011386 | -0.004578 | 59.6375 | -62.2925 | 59.8938 | -62.0407 | -62.5122 | -62.5031 | 0.068665 | 59.6649 | -62.3062 | 59.8206 | -62.2009 | -62.4115 | -62.3795 | 0.018311 | -0.16479 | 0.091553 | 0.27008 | -0.19226 | -0.20142 | -0.21057 | -0.21973 | 0.004578 | -0.13733 | 0.018311 | 0.10986 | -0.068665 | -0.10071 | -0.073243 | -0.10529 | 0.25177 | 122.1863 | 0.10529 | 122.1268 | 121.9299 | 121.9711 | 121.9482 | 121.9757 | -122.0947 | -122.1085 | 122.2046 | 122.1313 | 62.3062 | 62.3795
786.875 | 122.2321 | -62.2833 | 59.7931 | -0.0060272 | 0.0033389 | 0.06053 | 0.060103 | 0.001286 | -0.0064109 | -0.0027621 | -0.0021057 | 0.0040802 | 0.071938 | 0.0689 | -0.010305 | 0.017944 | -0.006979 | -0.032043 | 59.6466 | -62.265 | 59.8663 | -62.0682 | -62.558 | -62.5442 | 0.009155 | 59.6329 | -62.352 | 59.7931 | -62.2559 | -62.4573 | -62.4069 | 0.01831 | -0.14648 | 0.073242 | 0.21515 | -0.26093 | -0.27466 | -0.27923 | -0.29297 | -0.068665 | -0.16022 | 0 | 0.027466 | -0.1236 | -0.17395 | -0.054931 | -0.10529 | 0.19684 | 122.1313 | 0.096131 | 122.1451 | 121.9116 | 121.9849 | 121.9299 | 121.9162 | -122.0581 | -122.1451 | 122.1497 | 122.0764 | 62.2513 | 62.2925
788.5625 | 122.3099 | -62.2742 | 59.7656 | -0.0060272 | 0.0020571 | 0.061598 | 0.056898 | -0.003841 | -0.0053427 | -0.0042575 | -0.0021057 | -0.0019012 | 0.072578 | 0.0642 | -0.0077417 | 0.020508 | -0.0022794 | -0.09613 | 59.5688 | -62.2879 | 59.8755 | -62.0453 | -62.5214 | -62.4893 | 0.018311 | 59.6191 | -62.3245 | 59.8251 | -62.1872 | -62.3566 | -62.352 | -0.013733 | -0.19684 | 0.10986 | 0.22888 | -0.21515 | -0.24719 | -0.20142 | -0.23346 | -0.050354 | -0.14648 | 0.059509 | 0.086975 | -0.07782 | -0.082397 | -0.027466 | -0.032043 | 0.24262 | 122.1634 | 0.13733 | 122.1497 | 121.8567 | 121.9437 | 121.843 | 121.8933 | -122.0535 | -122.0901 | 122.1497 | 122.0993 | 62.178 | 62.2925
790.3281 | 122.3053 | -62.2787 | 59.7885 | -0.013657 | 0.0016299 | 0.059676 | 0.056471 | -0.0023456 | -0.0049155 | -0.0019077 | -0.0051575 | 0.001303 | 0.072365 | 0.052237 | -0.0092371 | 0.016022 | -0.002493 | 0.041199 | 59.5963 | -62.2467 | 59.9396 | -61.9583 | -62.439 | -62.4207 | 0.13733 | 59.6191 | -62.3016 | 59.8618 | -62.114 | -62.2971 | -62.3199 | 0.032044 | -0.19226 | 0.15106 | 0.32044 | -0.14191 | -0.16022 | -0.17395 | -0.19226 | -0.022888 | -0.16937 | 0.073242 | 0.16479 | -0.041198 | -0.01831 | -0.01831 | 0.004578 | 0.28839 | 122.1863 | 0.18768 | 122.1634 | 121.843 | 121.9208 | 121.875 | 121.8979 | -122.0352 | -122.0901 | 122.2183 | 122.1405 | 62.3199 | 62.4161
792.0156 | 122.3099 | -62.2787 | 59.7656 | -0.0060272 | 0.0020571 | 0.061385 | 0.058607 | 0.0017132 | -0.0055563 | 0.00044213 | -0.0021057 | -0.00019216 | 0.073647 | 0.061637 | -0.0075281 | 0.016663 | -0.0039884 | -0.10071 | 59.5963 | -62.2925 | 59.8755 | -62.0499 | -62.5305 | -62.4756 | 0.004578 | 59.61 | -62.3474 | 59.816 | -62.2009 | -62.3611 | -62.3657 | -0.013732 | -0.16937 | 0.10986 | 0.22888 | -0.19684 | -0.25177 | -0.18311 | -0.23804 | -0.068664 | -0.15564 | 0.050354 | 0.07782 | -0.086975 | -0.082397 | -0.018311 | -0.013733 | 0.24261 | 122.168 | 0.14648 | 122.1634 | 121.8887 | 121.9574 | 121.875 | 121.8887 | -122.0581 | -122.113 | 122.1542 | 122.0947 | 62.178 | 62.2833
793.7656 | 122.2504 | -62.2742 | 59.7931 | 0.0016023 | 0.0016299 | 0.059462 | 0.059462 | -0.0044818 | -0.0049155 | -0.0025485 | -0.0021057 | 0.0034392 | 0.071724 | 0.072104 | -0.012228 | 0.020508 | -0.0012112 | -0.13275 | 59.6283 | -62.2925 | 59.7885 | -62.146 | -62.6129 | -62.5763 | -0.068665 | 59.6603 | -62.3199 | 59.7702 | -62.2742 | -62.4664 | -62.4161 | -0.01831 | -0.16479 | -0.004578 | 0.12817 | -0.30212 | -0.33875 | -0.28381 | -0.32044 | -0.045776 | -0.13275 | -0.022888 | 0 | -0.14191 | -0.19226 | -0.096131 | -0.14648 | 0.14648 | 122.081 | 0.045776 | 122.0901 | 121.9208 | 121.9803 | 121.9025 | 121.9345 | -122.0856 | -122.113 | 122.0627 | 122.0444 | 62.1414 | 62.2055
795.5156 | 122.2366 | -62.3062 | 59.8434 | -0.0060272 | 0.0012027 | 0.059676 | 0.05818 | 4.192e-06 | -0.0059835 | -0.0025485 | 0.0009461 | 0.003012 | 0.071938 | 0.06185 | -0.010732 | 0.018585 | -0.003561 | -0.004578 | 59.6283 | -62.2742 | 59.848 | -62.0728 | -62.5442 | -62.5122 | 0.041199 | 59.6695 | -62.3291 | 59.7885 | -62.2238 | -62.4161 | -62.4161 | 0.032043 | -0.21515 | 0.004577 | 0.23346 | -0.20599 | -0.23804 | -0.23804 | -0.27008 | -0.022889 | -0.17395 | -0.054932 | 0.082397 | -0.10986 | -0.10986 | -0.086975 | -0.086975 | 0.20142 | 122.1222 | 0.10529 | 122.1176 | 121.9025 | 121.9986 | 121.9345 | 121.9757 | -122.1176 | -122.1725 | 122.1542 | 122.0947 | 62.3016 | 62.3474
797.2031 | 122.3099 | -62.2787 | 59.7702 | 0.0016023 | 0.0022709 | 0.059248 | 0.056685 | -0.00555 | -0.0074789 | -0.0021213 | -0.0051575 | 0.00066224 | 0.070442 | 0.068259 | -0.0090235 | 0.018158 | -0.0018522 | -0.086975 | 59.5825 | -62.3016 | 59.8618 | -62.059 | -62.5259 | -62.4939 | 0 | 59.6283 | -62.3428 | 59.8343 | -62.2101 | -62.3795 | -62.3886 | -0.022888 | -0.18768 | 0.091552 | 0.21973 | -0.21515 | -0.24719 | -0.19226 | -0.2243 | -0.064086 | -0.14191 | 0.064087 | 0.068665 | -0.10986 | -0.10071 | -0.045777 | -0.036622 | 0.24262 | 122.1634 | 0.13275 | 122.1771 | 121.8842 | 121.9711 | 121.8613 | 121.907 | -122.0718 | -122.113 | 122.1405 | 122.113 | 62.1918 | 62.2787
798.9531 | 122.3557 | -62.2513 | 59.7931 | -0.0060272 | 0.0003483 | 0.057112 | 0.057112 | -0.002132 | -0.0068381 | -0.0021213 | -0.0051575 | 0.00087584 | 0.069588 | 0.060355 | -0.010092 | 0.019012 | -0.0020658 | 0.036621 | 59.5825 | -62.2787 | 59.9625 | -61.9446 | -62.4207 | -62.4023 | 0.16022 | 59.5963 | -62.2971 | 59.8938 | -62.1002 | -62.3016 | -62.3154 | -0.027466 | -0.21057 | 0.16937 | 0.3067 | -0.15106 | -0.16937 | -0.1236 | -0.14191 | -0.045776 | -0.19684 | 0.10071 | 0.15106 | -0.064087 | -0.050354 | -0.018311 | -0.004578 | 0.33417 | 122.2412 | 0.19684 | 122.1909 | 121.8613 | 121.8933 | 121.8338 | 121.8475 | -122.0718 | -122.0901 | 122.2137 | 122.1451 | 62.2879 | 62.4115
800.6406 | 122.3099 | -62.3016 | 59.7382 | 0.0016023 | 0.0024845 | 0.062666 | 0.059462 | -0.00020941 | -0.0044883 | -0.0010531 | -0.0021057 | 0.0027984 | 0.071297 | 0.063346 | -0.010305 | 0.016235 | 7.04e-05 | -0.07782 | 59.5688 | -62.2513 | 59.9258 | -61.9858 | -62.5076 | -62.471 | 0.041199 | 59.6008 | -62.3199 | 59.848 | -62.1735 | -62.3566 | -62.352 | 0.050354 | -0.16937 | 0.18768 | 0.31586 | -0.16937 | -0.20599 | -0.21973 | -0.25635 | -0.01831 | -0.13733 | 0.10986 | 0.12817 | -0.050354 | -0.054931 | -0.032044 | -0.036621 | 0.2655 | 122.1771 | 0.14648 | 122.168 | 121.8201 | 121.9208 | 121.8704 | 121.9025 | -121.9894 | -122.0581 | 122.2275 | 122.1497 | 62.2238 | 62.3428
802.3281 | 122.2824 | -62.2742 | 59.8206 | -0.021286 | 0.0020571 | 0.059462 | 0.061171 | -0.002132 | -0.0057699 | -0.0014805 | -0.0051575 | 0.0032256 | 0.070229 | 0.058432 | -0.0090235 | 0.018158 | -0.0037748 | 0.013733 | 59.6466 | -62.2879 | 59.8755 | -62.0453 | -62.5214 | -62.4893 | 0.059509 | 59.6786 | -62.3154 | 59.8343 | -62.1826 | -62.4023 | -62.3611 | -0.013733 | -0.17395 | 0.054931 | 0.22888 | -0.21515 | -0.24719 | -0.20142 | -0.23346 | -0.041199 | -0.14191 | 0.013733 | 0.091553 | -0.086975 | -0.12817 | -0.045776 | -0.086975 | 0.24262 | 122.1634 | 0.13275 | 122.1497 | 121.9345 | 121.994 | 121.9208 | 121.9528 | -122.1085 | -122.1359 | 122.1497 | 122.1085 | 62.2879 | 62.3337
804.0781 | 122.2366 | -62.2833 | 59.8389 | -0.013657 | 0.0029117 | 0.060103 | 0.05818 | -0.0019184 | -0.0053427 | -0.0027621 | -0.0051575 | 0.0023712 | 0.072792 | 0.0642 | -0.0090235 | 0.016022 | -0.0050564 | -0.032043 | 59.6695 | -62.265 | 59.8297 | -62.0865 | -62.5351 | -62.5259 | 0.013733 | 59.6786 | -62.3245 | 59.7794 | -62.2147 | -62.4161 | -62.3978 | 0.01831 | -0.16937 | -0.009155 | 0.19684 | -0.24262 | -0.25177 | -0.26093 | -0.27008 | -0.041199 | -0.16022 | -0.059509 | 0.068664 | -0.11444 | -0.13275 | -0.073242 | -0.091553 | 0.17853 | 122.0947 | 0.10986 | 122.1039 | 121.9345 | 122.0032 | 121.9528 | 121.962 | -122.1039 | -122.1634 | 122.113 | 122.0627 | 62.2513 | 62.2971
805.8438 | 122.2275 | -62.2971 | 59.8389 | -0.013657 | 0.0022709 | 0.059889 | 0.058821 | -0.00020941 | -0.0083335 | -0.0025485 | -0.0021057 | 0.0021576 | 0.071938 | 0.062064 | -0.0090235 | 0.017303 | 0.0062656 | -0.013733 | 59.6695 | -62.2604 | 59.8434 | -62.0819 | -62.5397 | -62.5168 | 0.022888 | 59.6741 | -62.3291 | 59.7794 | -62.2284 | -62.4161 | -62.4069 | 0.036621 | -0.16937 | 0.004578 | 0.21515 | -0.21973 | -0.24262 | -0.25635 | -0.27924 | -0.032044 | -0.16479 | -0.059509 | 0.068664 | -0.10986 | -0.11902 | -0.077819 | -0.086975 | 0.17853 | 122.1039 | 0.10071 | 122.1085 | 121.9299 | 122.0032 | 121.9666 | 121.9711 | -122.0993 | -122.168 | 122.1405 | 122.0764 | 62.2833 | 62.3199
807.5938 | 122.287 | -62.2833 | 59.8206 | -0.013657 | 0.0026981 | 0.059035 | 0.061598 | -0.00042301 | -0.0074789 | -0.00062587 | 0.0009461 | 0.0015166 | 0.07151 | 0.060996 | -0.0090235 | 0.016876 | -0.0018522 | -0.004578 | 59.6375 | -62.2787 | 59.8984 | -62.027 | -62.5168 | -62.5031 | 0.082397 | 59.6695 | -62.3199 | 59.8526 | -62.1918 | -62.3886 | -62.352 | 0.004577 | -0.18311 | 0.077819 | 0.25635 | -0.21973 | -0.23346 | -0.2243 | -0.23804 | -0.036621 | -0.15106 | 0.032043 | 0.091553 | -0.068665 | -0.10529 | -0.032044 | -0.068665 | 0.25177 | 122.1771 | 0.12817 | 122.1725 | 121.9162 | 121.9894 | 121.9208 | 121.9528 | -122.0993 | -122.1405 | 122.1817 | 122.1359 | 62.2787 | 62.3657
809.2812 | 122.3557 | -62.2559 | 59.7656 | -0.013657 | 0.0005619 | 0.060744 | 0.056258 | -0.0023456 | -0.0066245 | -0.0012669 | -0.0082093 | -0.0019012 | 0.072151 | 0.062064 | -0.0096643 | 0.014526 | 0.0024204 | 0.032043 | 59.61 | -62.2696 | 59.9716 | -61.908 | -62.4023 | -62.3795 | 0.15564 | 59.6191 | -62.3154 | 59.8938 | -62.0819 | -62.2833 | -62.2833 | -0.013733 | -0.15564 | 0.20599 | 0.3479 | -0.1236 | -0.14648 | -0.10986 | -0.13275 | -0.05951 | -0.14648 | 0.12817 | 0.17395 | -0.027466 | -0.027466 | 0.032044 | 0.032044 | 0.36163 | 122.2412 | 0.23346 | 122.2092 | 121.8796 | 121.9345 | 121.8658 | 121.875 | -122.0352 | -122.081 | 122.2275 | 122.1497 | 62.2879 | 62.4115
811.0156 | 122.3419 | -62.2696 | 59.8022 | -0.013657 | -0.0024289 | 0.059889 | 0.057967 | -0.001491 | -0.0079061 | -0.0031895 | -0.0051575 | 0.0023712 | 0.07151 | 0.064414 | -0.0092371 | 0.018158 | -0.0012112 | 0.041199 | 59.5963 | -62.2742 | 59.9533 | -61.9263 | -62.4161 | -62.3978 | 0.17853 | 59.5917 | -62.3154 | 59.8938 | -62.0956 | -62.2742 | -62.3016 | -0.004578 | -0.20599 | 0.15106 | 0.34332 | -0.12817 | -0.14648 | -0.1236 | -0.14191 | -0.045777 | -0.21057 | 0.091553 | 0.17395 | -0.032044 | -0.004578 | 0.013733 | 0.041199 | 0.3479 | 122.2275 | 0.21973 | 122.2092 | 121.8704 | 121.907 | 121.8658 | 121.8613 | -122.0764 | -122.1176 | 122.2229 | 122.1634 | 62.3108 | 62.4481
812.75 | 122.3007 | -62.2696 | 59.7748 | -0.0060272 | -0.0002927 | 0.057539 | 0.058607 | -0.00020941 | -0.0053427 | -0.0019077 | -0.0051575 | 0.00023504 | 0.072578 | 0.060782 | -0.0094507 | 0.017944 | -0.0029202 | -0.09613 | 59.5642 | -62.2833 | 59.8755 | -62.0316 | -62.5168 | -62.4802 | 0.004578 | 59.6054 | -62.352 | 59.8297 | -62.2101 | -62.3611 | -62.3566 | -0.013733 | -0.21057 | 0.10071 | 0.23804 | -0.21057 | -0.24719 | -0.19684 | -0.23346 | -0.082398 | -0.16937 | 0.054932 | 0.059509 | -0.086975 | -0.091553 | -0.004577 | -0.009155 | 0.25177 | 122.1588 | 0.14191 | 122.1817 | 121.8475 | 121.9574 | 121.8338 | 121.875 | -122.0581 | -122.1268 | 122.1451 | 122.0993 | 62.1735 | 62.2742
814.4844 | 122.2046 | -62.2971 | 59.816 | -0.0060272 | 0.0024845 | 0.061598 | 0.060957 | 0.0025678 | -0.0061971 | -0.0023349 | -0.0021057 | 0.00066224 | 0.073433 | 0.072532 | -0.011587 | 0.017303 | -0.0048428 | -0.082397 | 59.6603 | -62.3016 | 59.8206 | -62.1277 | -62.6083 | -62.5809 | -0.059509 | 59.6695 | -62.3154 | 59.7748 | -62.3016 | -62.4802 | -62.4298 | -0.004578 | -0.15564 | 0.004578 | 0.16937 | -0.28381 | -0.31128 | -0.27924 | -0.3067 | -0.018311 | -0.14648 | -0.041199 | -0.004578 | -0.13275 | -0.18311 | -0.11444 | -0.1648 | 0.17395 | 122.1222 | 0.013733 | 122.0901 | 121.962 | 121.9849 | 121.9574 | 121.9666 | -122.1176 | -122.1313 | 122.1176 | 122.0718 | 62.2147 | 62.2375
816.1719 | 122.2366 | -62.2833 | 59.8434 | -0.0060272 | 0.0007755 | 0.057753 | 0.058821 | -0.0023456 | -0.0066245 | -0.0036167 | -0.0051575 | 0.0023712 | 0.073219 | 0.065055 | -0.0077417 | 0.017731 | -0.000784 | 0.009155 | 59.6375 | -62.2742 | 59.8618 | -62.0636 | -62.5351 | -62.5031 | 0.032043 | 59.6832 | -62.3016 | 59.7839 | -62.2009 | -62.3886 | -62.4069 | 0.009155 | -0.20599 | 0.01831 | 0.21973 | -0.21973 | -0.25177 | -0.22888 | -0.26093 | -0.018311 | -0.16022 | -0.059509 | 0.082397 | -0.1236 | -0.10529 | -0.10528 | -0.086975 | 0.21057 | 122.1359 | 0.10071 | 122.0856 | 121.9116 | 121.9849 | 121.9208 | 121.9666 | -122.1176 | -122.1451 | 122.1451 | 122.0673 | 62.2925 | 62.3154
817.9219 | 122.3648 | -62.2421 | 59.7839 | -0.0060272 | -0.0009335 | 0.061385 | 0.054762 | -0.0042682 | -0.0064109 | -0.00083947 | -0.0021057 | 0.0015166 | 0.072792 | 0.063132 | -0.0094507 | 0.017303 | -0.0020658 | -0.041199 | 59.5825 | -62.2787 | 59.9121 | -61.9949 | -62.4527 | -62.439 | 0.09613 | 59.61 | -62.3245 | 59.8938 | -62.1094 | -62.2833 | -62.2971 | -0.036622 | -0.20142 | 0.12817 | 0.24719 | -0.19684 | -0.21057 | -0.16022 | -0.17395 | -0.082398 | -0.17395 | 0.10986 | 0.13275 | -0.054932 | -0.041199 | 0.027466 | 0.041199 | 0.28381 | 122.1909 | 0.21515 | 122.2183 | 121.8613 | 121.9345 | 121.8246 | 121.8521 | -122.0627 | -122.1085 | 122.1542 | 122.1359 | 62.2009 | 62.3383
819.6719 | 122.2733 | -62.265 | 59.8206 | 0.0016023 | -0.0002927 | 0.057753 | 0.057539 | -0.00042301 | -0.0055563 | -0.0031895 | -0.0051575 | 0.00023504 | 0.070015 | 0.065268 | -0.0090235 | 0.018585 | -0.0009976 | 0.054932 | 59.61 | -62.2742 | 59.935 | -61.972 | -62.439 | -62.4207 | 0.12817 | 59.6466 | -62.3016 | 59.8526 | -62.1552 | -62.3474 | -62.3383 | -0.009155 | -0.21057 | 0.11444 | 0.29297 | -0.15564 | -0.17395 | -0.14648 | -0.1648 | -0.036621 | -0.17395 | 0.032043 | 0.10986 | -0.073242 | -0.082397 | -0.036621 | -0.045776 | 0.30212 | 122.2092 | 0.14649 | 122.1542 | 121.8842 | 121.9482 | 121.875 | 121.9116 | -122.0947 | -122.1222 | 122.2 | 122.1176 | 62.3199 | 62.3932
821.3594 | 122.3694 | -62.2467 | 59.7885 | -0.0060272 | 0.0007755 | 0.059676 | 0.057326 | -0.0012774 | -0.01047 | -0.0027621 | -0.0082093 | 0.003653 | 0.071083 | 0.060782 | -0.0090235 | 0.017303 | -0.0014248 | 0.027466 | 59.5734 | -62.265 | 59.9533 | -61.9308 | -62.4298 | -62.3978 | 0.20599 | 59.6191 | -62.2696 | 59.9075 | -62.1094 | -62.265 | -62.2925 | -0.018311 | -0.21515 | 0.16479 | 0.31586 | -0.15106 | -0.18311 | -0.13275 | -0.1648 | -0.022888 | -0.16937 | 0.11902 | 0.13733 | -0.045776 | -0.018311 | -0.022888 | 0.004577 | 0.33417 | 122.2183 | 0.16022 | 122.1771 | 121.8384 | 121.8887 | 121.8201 | 121.8658 | -122.0535 | -122.0581 | 122.2 | 122.1542 | 62.2742 | 62.4527
823.1094 | 122.3145 | -62.2696 | 59.8206 | -0.013657 | 0.0009891 | 0.057112 | 0.056898 | 0.0017132 | -0.0089743 | 0.0010831 | -0.0021057 | 0.0023712 | 0.071938 | 0.072104 | -0.010305 | 0.01709 | -0.004202 | 0.059509 | 59.5825 | -62.233 | 59.9533 | -61.9583 | -62.4298 | -62.4115 | 0.14648 | 59.6466 | -62.2833 | 59.8709 | -62.1277 | -62.3108 | -62.3291 | 0.036621 | -0.23804 | 0.13275 | 0.31128 | -0.14191 | -0.16022 | -0.17853 | -0.19684 | -0.013733 | -0.17395 | 0.050354 | 0.14191 | -0.05951 | -0.041199 | -0.045777 | -0.027466 | 0.27466 | 122.1863 | 0.15564 | 122.1542 | 121.8155 | 121.9299 | 121.8521 | 121.9162 | -122.0535 | -122.1039 | 122.2229 | 122.1405 | 62.3291 | 62.4161
824.8594 | 122.3648 | -62.2787 | 59.7702 | -0.0060272 | 0.0044071 | 0.061812 | 0.059248 | 0.00085879 | -0.0038473 | -0.0019077 | -0.0051575 | 0.0017304 | 0.072151 | 0.06185 | -0.01116 | 0.018585 | -0.0033474 | -0.064087 | 59.5917 | -62.2971 | 59.9258 | -61.9949 | -62.5214 | -62.471 | 0.064087 | 59.5963 | -62.3199 | 59.8846 | -62.1414 | -62.3428 | -62.3199 | -0.01831 | -0.17853 | 0.15564 | 0.28381 | -0.19226 | -0.24261 | -0.17395 | -0.2243 | -0.041198 | -0.17395 | 0.11444 | 0.13733 | -0.041198 | -0.064086 | 0 | -0.022888 | 0.30212 | 122.2229 | 0.17853 | 122.2046 | 121.8887 | 121.9162 | 121.8704 | 121.875 | -122.0673 | -122.0901 | 122.2046 | 122.1634 | 62.2147 | 62.3428
826.6094 | 122.3099 | -62.2513 | 59.816 | -0.0060272 | -0.0013607 | 0.059676 | 0.057326 | -0.0012774 | -0.0036337 | 1.4934e-05 | -0.0021057 | 0.00044864 | 0.07151 | 0.062705 | -0.0081689 | 0.017731 | 0.0007114 | 0.045776 | 59.6054 | -62.2604 | 59.9442 | -61.9629 | -62.4344 | -62.4115 | 0.13275 | 59.6558 | -62.3062 | 59.8572 | -62.1368 | -62.3062 | -62.3245 | -0.009155 | -0.21057 | 0.12817 | 0.28839 | -0.16022 | -0.1831 | -0.15106 | -0.17395 | -0.054931 | -0.16022 | 0.041199 | 0.11444 | -0.073242 | -0.054931 | -0.018311 | 0 | 0.29755 | 122.2046 | 0.16937 | 122.1634 | 121.8658 | 121.962 | 121.8567 | 121.907 | -122.0764 | -122.1222 | 122.1954 | 122.1085 | 62.2971 | 62.384
828.2969 | 122.3465 | -62.2742 | 59.7427 | -0.0060272 | 0.0052615 | 0.05818 | 0.061171 | -0.00042301 | -0.0059835 | -0.0029759 | -0.0051575 | 0.0040802 | 0.073219 | 0.067618 | -0.012441 | 0.019012 | -0.0044156 | -0.13733 | 59.6146 | -62.3154 | 59.8801 | -62.059 | -62.5214 | -62.4893 | 0.022888 | 59.6008 | -62.3291 | 59.8755 | -62.1643 | -62.3566 | -62.3154 | -0.041199 | -0.12817 | 0.13733 | 0.21515 | -0.21515 | -0.24719 | -0.17395 | -0.20599 | -0.054932 | -0.14191 | 0.13275 | 0.10986 | -0.041199 | -0.082397 | 0.013733 | -0.027465 | 0.25635 | 122.1954 | 0.16479 | 122.2046 | 121.9299 | 121.9299 | 121.8887 | 121.875 | -122.0581 | -122.0718 | 122.1542 | 122.1497 | 62.1368 | 62.2971
830.0625 | 122.2275 | -62.2787 | 59.848 | -0.013657 | 0.0012027 | 0.059462 | 0.057753 | 0.0034222 | -0.0061971 | -0.0031895 | -0.0021057 | 0.0023712 | 0.073219 | 0.061637 | -0.0096643 | 0.017303 | -0.003561 | -0.027466 | 59.6512 | -62.2604 | 59.8526 | -62.0956 | -62.5351 | -62.5168 | 0.045776 | 59.6878 | -62.3016 | 59.7885 | -62.2192 | -62.4115 | -62.4115 | 0.018311 | -0.19684 | 0.004578 | 0.18311 | -0.23804 | -0.25635 | -0.25635 | -0.27466 | -0.022888 | -0.16022 | -0.059509 | 0.05951 | -0.13275 | -0.13275 | -0.10986 | -0.10986 | 0.1648 | 122.113 | 0.082398 | 122.0901 | 121.9116 | 121.9894 | 121.9299 | 121.9666 | -122.1085 | -122.1497 | 122.1313 | 122.0673 | 62.2513 | 62.3245
831.8125 | 122.319 | -62.2696 | 59.7702 | -0.0060272 | 0.0022709 | 0.063307 | 0.056044 | -0.0023456 | -0.0083335 | -0.0027621 | -0.0082093 | 0.00066224 | 0.070656 | 0.062918 | -0.0081689 | 0.017303 | 0.0002842 | -0.07782 | 59.5825 | -62.2696 | 59.9121 | -61.9949 | -62.5076 | -62.4573 | 0.068665 | 59.5734 | -62.3154 | 59.8572 | -62.1689 | -62.3566 | -62.3337 | 0 | -0.18768 | 0.14191 | 0.27466 | -0.18768 | -0.23804 | -0.18768 | -0.23804 | -0.045777 | -0.19684 | 0.086975 | 0.10071 | -0.064087 | -0.086975 | -0.01831 | -0.041198 | 0.27466 | 122.1817 | 0.14648 | 122.1725 | 121.8521 | 121.8887 | 121.8521 | 121.843 | -122.0398 | -122.0856 | 122.1817 | 122.1268 | 62.1918 | 62.3383
833.4844 | 122.2504 | -62.2787 | 59.848 | -0.013657 | 0.0001345 | 0.060957 | 0.059248 | 0.0023542 | -0.0098287 | -0.0023349 | -0.0082093 | 0.0023712 | 0.071297 | 0.063559 | -0.010519 | 0.016876 | -0.0033474 | 0.009155 | 59.6512 | -62.2742 | 59.8709 | -62.0728 | -62.5168 | -62.5031 | 0.050354 | 59.6832 | -62.3016 | 59.8389 | -62.1872 | -62.3978 | -62.3703 | 0.004578 | -0.19684 | 0.022889 | 0.20599 | -0.2243 | -0.23804 | -0.22888 | -0.24262 | -0.022888 | -0.16479 | -0.009155 | 0.091553 | -0.091552 | -0.11902 | -0.068664 | -0.09613 | 0.20142 | 122.1451 | 0.11444 | 122.1405 | 121.9254 | 121.9849 | 121.9299 | 121.962 | -122.1222 | -122.1497 | 122.1497 | 122.1176 | 62.2879 | 62.3291
835.1562 | 122.3648 | -62.2559 | 59.7519 | -0.013657 | 0.0037661 | 0.061171 | 0.057967 | -0.0010638 | -0.0053427 | -0.0016941 | -0.0051575 | 0.0015166 | 0.073006 | 0.064414 | -0.0090235 | 0.018799 | -0.003561 | -0.082397 | 59.5963 | -62.2787 | 59.9213 | -61.9995 | -62.4985 | -62.4527 | 0.050354 | 59.5734 | -62.3108 | 59.8755 | -62.1368 | -62.3291 | -62.3291 | -0.022889 | -0.15564 | 0.16937 | 0.25635 | -0.19684 | -0.24262 | -0.17395 | -0.21973 | -0.054932 | -0.17853 | 0.1236 | 0.11902 | -0.073243 | -0.073243 | -0.018311 | -0.018311 | 0.27924 | 122.2 | 0.17395 | 122.1863 | 121.875 | 121.8842 | 121.8521 | 121.8292 | -122.0306 | -122.0627 | 122.1771 | 122.1313 | 62.1735 | 62.3062
836.8438 | 122.2961 | -62.2604 | 59.7702 | -0.013657 | 0.0016299 | 0.059462 | 0.057112 | 0.00021799 | -0.0042745 | -0.0019077 | -0.0021057 | 0.0017304 | 0.072151 | 0.061423 | -0.0088097 | 0.017731 | -0.0003568 | -0.086975 | 59.6054 | -62.2971 | 59.8709 | -62.0224 | -62.5168 | -62.4802 | 0.004578 | 59.6146 | -62.3245 | 59.8297 | -62.1918 | -62.3611 | -62.352 | -0.036621 | -0.1648 | 0.10071 | 0.23804 | -0.21973 | -0.25635 | -0.18311 | -0.21973 | -0.064087 | -0.15564 | 0.059509 | 0.068665 | -0.091553 | -0.10071 | -0.027466 | -0.036621 | 0.27466 | 122.168 | 0.13275 | 122.1542 | 121.9025 | 121.9391 | 121.8658 | 121.875 | -122.0673 | -122.0947 | 122.1313 | 122.0901 | 62.1735 | 62.265
838.5312 | 122.2641 | -62.2696 | 59.8389 | -0.0060272 | 0.0007755 | 0.05818 | 0.058607 | 0.001286 | -0.0081197 | -0.0010531 | -0.0051575 | 0.0017304 | 0.073219 | 0.065909 | -0.010092 | 0.020081 | -0.0003568 | -0.009155 | 59.6695 | -62.3016 | 59.848 | -62.1002 | -62.5259 | -62.5259 | 0.009155 | 59.6741 | -62.3245 | 59.7977 | -62.2101 | -62.4023 | -62.3886 | -0.032044 | -0.16937 | 0.009155 | 0.16937 | -0.25635 | -0.25635 | -0.2243 | -0.2243 | -0.054932 | -0.16479 | -0.041199 | 0.059509 | -0.11902 | -0.13275 | -0.064087 | -0.07782 | 0.20142 | 122.1497 | 0.11444 | 122.1222 | 121.9711 | 121.9986 | 121.9391 | 121.9437 | -122.1405 | -122.1634 | 122.1176 | 122.0673 | 62.2604 | 62.2787
840.2344 | 122.2229 | -62.2971 | 59.8389 | -0.0060272 | 0.0037661 | 0.06288 | 0.059889 | 0.002995 | -0.0034201 | -0.0023349 | 0.0009461 | 0.003653 | 0.072365 | 0.065055 | -0.010732 | 0.019867 | -0.0016384 | -0.041199 | 59.6603 | -62.2925 | 59.8663 | -62.0865 | -62.5717 | -62.5442 | -0.027466 | 59.6741 | -62.3428 | 59.7931 | -62.2513 | -62.4527 | -62.4161 | 0.004578 | -0.17853 | 0.027466 | 0.21057 | -0.24719 | -0.27466 | -0.25177 | -0.27924 | -0.045776 | -0.16479 | -0.045776 | 0.045776 | -0.11902 | -0.15564 | -0.073243 | -0.10986 | 0.20599 | 122.1588 | 0.091552 | 122.1359 | 121.9528 | 122.0169 | 121.9574 | 121.9711 | -122.1313 | -122.1817 | 122.1634 | 122.0901 | 62.2559 | 62.2696
841.9844 | 122.2321 | -62.265 | 59.8801 | -0.021286 | -7.9104e-05 | 0.059889 | 0.059676 | -0.0010638 | -0.0061971 | -0.0038303 | -0.0051575 | 0.0042938 | 0.071297 | 0.058432 | -0.010305 | 0.019012 | 0.0013522 | -0.009155 | 59.6832 | -62.2879 | 59.8526 | -62.0682 | -62.5214 | -62.5305 | 0.022888 | 59.6786 | -62.3383 | 59.8022 | -62.2101 | -62.4115 | -62.4115 | -0.022888 | -0.19684 | -0.027466 | 0.19684 | -0.2655 | -0.25635 | -0.24262 | -0.23346 | -0.073242 | -0.20142 | -0.07782 | 0.054932 | -0.14648 | -0.14648 | -0.073242 | -0.073242 | 0.21973 | 122.1405 | 0.12817 | 122.1405 | 121.9711 | 122.0169 | 121.9482 | 121.9437 | -122.168 | -122.2183 | 122.1176 | 122.0673 | 62.2559 | 62.2879
843.7344 | 122.2229 | -62.2833 | 59.8022 | 0.0016023 | 0.0026981 | 0.06053 | 0.056685 | 0.00043159 | -0.0057699 | -0.00083947 | -0.0021057 | 0.003012 | 0.073647 | 0.063987 | -0.0088097 | 0.018158 | -0.0003568 | -0.050354 | 59.642 | -62.2742 | 59.8663 | -62.0636 | -62.5488 | -62.5351 | 0.009155 | 59.6603 | -62.3108 | 59.7931 | -62.2284 | -62.4481 | -62.3978 | 0.009155 | -0.16022 | 0.064087 | 0.21973 | -0.25177 | -0.2655 | -0.26093 | -0.27466 | -0.027466 | -0.14191 | -0.009155 | 0.054931 | -0.11444 | -0.1648 | -0.086975 | -0.13733 | 0.21057 | 122.1405 | 0.082397 | 122.1039 | 121.9162 | 121.9711 | 121.9254 | 121.9437 | -122.0764 | -122.113 | 122.1497 | 122.0764 | 62.233 | 62.2925
845.4219 | 122.3236 | -62.2467 | 59.8068 | -0.0060272 | -0.0002927 | 0.059248 | 0.057326 | 0.0027814 | -0.0059835 | -0.00019867 | -0.0021057 | 0.0015166 | 0.07151 | 0.053519 | -0.0088097 | 0.018585 | -0.0031338 | 0.054932 | 59.61 | -62.2696 | 59.9579 | -61.9446 | -62.4207 | -62.3978 | 0.14648 | 59.6237 | -62.2833 | 59.8755 | -62.114 | -62.3016 | -62.3062 | -0.022888 | -0.19684 | 0.15106 | 0.30212 | -0.15106 | -0.17395 | -0.12817 | -0.15106 | -0.036621 | -0.18311 | 0.068664 | 0.13275 | -0.059509 | -0.054932 | -0.022888 | -0.018311 | 0.32501 | 122.2275 | 0.16937 | 122.1588 | 121.8796 | 121.907 | 121.8567 | 121.8704 | -122.0764 | -122.0901 | 122.2046 | 122.1222 | 62.3016 | 62.3932
847.1562 | 122.2183 | -62.2925 | 59.8022 | -0.0060272 | 0.0033389 | 0.063094 | 0.059248 | 0.00043159 | -0.0068381 | 0.00022853 | -0.0021057 | 0.0045074 | 0.073006 | 0.068686 | -0.0083825 | 0.017731 | -0.0061246 | -0.11902 | 59.697 | -62.3108 | 59.8114 | -62.1414 | -62.6129 | -62.5854 | -0.10986 | 59.6695 | -62.3474 | 59.7839 | -62.2696 | -62.471 | -62.4252 | -0.018311 | -0.10529 | 0.009155 | 0.15106 | -0.29297 | -0.32044 | -0.27466 | -0.30212 | -0.054932 | -0.13275 | -0.01831 | 0.022888 | -0.13275 | -0.17853 | -0.07782 | -0.1236 | 0.16937 | 122.1222 | 0.07782 | 122.1313 | 122.0078 | 122.0169 | 121.9894 | 121.962 | -122.113 | -122.1497 | 122.1039 | 122.0764 | 62.1735 | 62.1826
848.9062 | 122.374 | -62.2375 | 59.7794 | -0.0060272 | -0.0005063 | 0.060316 | 0.057967 | -0.001491 | -0.0061971 | -0.0023349 | -0.0051575 | -0.0010468 | 0.072151 | 0.061209 | -0.0098779 | 0.017303 | -0.0044156 | -0.036621 | 59.5963 | -62.2604 | 59.9213 | -61.9766 | -62.4435 | -62.4252 | 0.10529 | 59.6237 | -62.2787 | 59.9075 | -62.1048 | -62.2696 | -62.2833 | -0.022888 | -0.18311 | 0.14191 | 0.26093 | -0.18768 | -0.20599 | -0.16479 | -0.1831 | -0.041199 | -0.15564 | 0.12817 | 0.13275 | -0.045776 | -0.032043 | -0.004577 | 0.009156 | 0.28381 | 122.1817 | 0.17395 | 122.1863 | 121.8567 | 121.9025 | 121.8338 | 121.8613 | -122.0398 | -122.0581 | 122.1588 | 122.1451 | 62.2009 | 62.3428
850.6562 | 122.2412 | -62.2604 | 59.8343 | -0.0060272 | 0.0033389 | 0.060316 | 0.059248 | -0.00063661 | -0.0083335 | 0.00065573 | -0.0051575 | 0.0040802 | 0.071938 | 0.066123 | -0.010519 | 0.020294 | -0.0014248 | -0.045776 | 59.642 | -62.2971 | 59.8572 | -62.0728 | -62.5626 | -62.5259 | -0.004578 | 59.6786 | -62.3108 | 59.7931 | -62.233 | -62.4573 | -62.4161 | -0.036621 | -0.19226 | 0.022888 | 0.18768 | -0.2655 | -0.30212 | -0.22888 | -0.2655 | -0.050354 | -0.15564 | -0.041199 | 0.027466 | -0.15564 | -0.19684 | -0.10529 | -0.14648 | 0.2243 | 122.1542 | 0.07782 | 122.1039 | 121.9391 | 121.9894 | 121.9025 | 121.9391 | -122.1313 | -122.1451 | 122.1176 | 122.0535 | 62.2147 | 62.2559
852.3438 | 122.3557 | -62.2559 | 59.7565 | -0.0060272 | 0.0035525 | 0.06053 | 0.058394 | -0.00085021 | -0.0068381 | -0.0014805 | -0.0051575 | -0.002115 | 0.072365 | 0.06655 | -0.010946 | 0.019012 | -0.0018522 | -0.086975 | 59.6008 | -62.265 | 59.9304 | -61.9949 | -62.5076 | -62.439 | 0.036621 | 59.5963 | -62.3199 | 59.8846 | -62.1506 | -62.3154 | -62.3062 | -0.009156 | -0.15564 | 0.17395 | 0.26093 | -0.18311 | -0.25177 | -0.17395 | -0.24261 | -0.064087 | -0.16022 | 0.12817 | 0.10529 | -0.050354 | -0.05951 | 0.013733 | 0.004577 | 0.27008 | 122.1954 | 0.16937 | 122.2046 | 121.8658 | 121.9162 | 121.8567 | 121.8521 | -122.0215 | -122.0764 | 122.1863 | 122.1405 | 62.1689 | 62.2925
854.0938 | 122.3145 | -62.2559 | 59.7748 | -0.013657 | -7.9104e-05 | 0.059035 | 0.057753 | -0.0019184 | -0.0059835 | -0.0031895 | -0.0021057 | 0.0017304 | 0.072365 | 0.068686 | -0.0085961 | 0.016876 | -0.0012112 | -0.10986 | 59.5825 | -62.2742 | 59.8892 | -61.9949 | -62.5214 | -62.4664 | 0.036621 | 59.6283 | -62.3291 | 59.8434 | -62.1597 | -62.3474 | -62.352 | -0.018311 | -0.19226 | 0.11444 | 0.26093 | -0.21057 | -0.2655 | -0.19226 | -0.24719 | -0.073243 | -0.14648 | 0.068665 | 0.09613 | -0.096131 | -0.091553 | -0.022888 | -0.01831 | 0.27924 | 122.1634 | 0.16937 | 122.1725 | 121.8567 | 121.9574 | 121.8384 | 121.8842 | -122.0489 | -122.1039 | 122.1451 | 122.0993 | 62.146 | 62.2925
855.8438 | 122.3282 | -62.2192 | 59.816 | -0.0060272 | 0.0009891 | 0.061171 | 0.056898 | -0.0036274 | -0.0072653 | -0.0023349 | -0.0021057 | 0.0010894 | 0.071297 | 0.063987 | -0.0094507 | 0.020081 | -0.0020658 | 0.054932 | 59.6008 | -62.2467 | 59.9716 | -61.9446 | -62.4161 | -62.4069 | 0.16022 | 59.6466 | -62.2696 | 59.8938 | -62.1048 | -62.2787 | -62.3062 | -0.027466 | -0.21515 | 0.15564 | 0.27466 | -0.18768 | -0.19684 | -0.16022 | -0.16937 | -0.050354 | -0.16937 | 0.07782 | 0.11444 | -0.086975 | -0.05951 | -0.036621 | -0.009156 | 0.30212 | 122.2183 | 0.1648 | 122.1634 | 121.8475 | 121.9162 | 121.8201 | 121.8658 | -122.0627 | -122.0856 | 122.1909 | 122.113 | 62.2742 | 62.3795
857.5938 | 122.2824 | -62.265 | 59.8068 | -0.0060272 | 0.0031253 | 0.06053 | 0.059248 | 0.00021799 | -0.0072653 | -0.0012669 | -0.0021057 | 0.003012 | 0.070869 | 0.062918 | -0.010946 | 0.019012 | -0.0044156 | -0.004578 | 59.6603 | -62.2604 | 59.9121 | -62.027 | -62.5076 | -62.4756 | 0.073242 | 59.6878 | -62.3062 | 59.8526 | -62.1689 | -62.3795 | -62.3474 | 0.004578 | -0.14648 | 0.10529 | 0.23804 | -0.21057 | -0.24261 | -0.21515 | -0.24719 | -0.041198 | -0.11902 | 0.045776 | 0.096131 | -0.082397 | -0.11444 | -0.041199 | -0.073243 | 0.23346 | 122.1725 | 0.13733 | 122.1588 | 121.9208 | 121.994 | 121.9254 | 121.9528 | -122.0673 | -122.113 | 122.1771 | 122.1176 | 62.2604 | 62.3383
859.2656 | 122.3236 | -62.2696 | 59.7839 | -0.0060272 | 0.0003483 | 0.059676 | 0.05818 | -0.004909 | -0.0044883 | 0.00086953 | -0.0051575 | 0.0021576 | 0.072151 | 0.067832 | -0.0096643 | 0.019012 | -0.0009976 | -0.091553 | 59.6237 | -62.2604 | 59.8755 | -62.0407 | -62.5076 | -62.4756 | 0.018311 | 59.6466 | -62.3016 | 59.8572 | -62.1643 | -62.352 | -62.3474 | 0.009155 | -0.16022 | 0.091552 | 0.22888 | -0.20599 | -0.23804 | -0.21515 | -0.24719 | -0.032044 | -0.13733 | 0.073242 | 0.10529 | -0.07782 | -0.082398 | -0.045776 | -0.050354 | 0.21973 | 122.1359 | 0.13733 | 122.1588 | 121.8842 | 121.9482 | 121.8933 | 121.9162 | -122.0444 | -122.0856 | 122.1451 | 122.1268 | 62.178 | 62.2879
861.0156 | 122.2229 | -62.2559 | 59.8618 | -0.0060272 | 0.0007755 | 0.05818 | 0.056898 | -0.0070452 | -0.0068381 | -0.0036167 | -0.0051575 | 0.0032256 | 0.070656 | 0.059928 | -0.0073145 | 0.01709 | -0.0001432 | -0.004578 | 59.6649 | -62.265 | 59.8663 | -62.0544 | -62.5259 | -62.5122 | 0.036621 | 59.6878 | -62.2833 | 59.8114 | -62.1872 | -62.3795 | -62.3932 | -0.009156 | -0.19684 | 0.004578 | 0.20142 | -0.25635 | -0.27008 | -0.24719 | -0.26093 | -0.027466 | -0.17395 | -0.050354 | 0.068664 | -0.13733 | -0.1236 | -0.10986 | -0.096131 | 0.21057 | 122.1313 | 0.09613 | 122.0947 | 121.9299 | 121.9711 | 121.9208 | 121.9437 | -122.1268 | -122.1451 | 122.1222 | 122.0673 | 62.2513 | 62.2925
862.7656 | 122.2916 | -62.2467 | 59.848 | -0.013657 | 0.0033389 | 0.061171 | 0.059462 | -0.00042301 | -0.0055563 | -0.0038303 | -0.0021057 | 0.0023712 | 0.071724 | 0.065482 | -0.011373 | 0.018372 | -0.0016384 | -0.004578 | 59.6878 | -62.2467 | 59.9075 | -62.027 | -62.4893 | -62.4847 | 0.086975 | 59.6786 | -62.3016 | 59.8663 | -62.1414 | -62.3566 | -62.3428 | 0 | -0.16022 | 0.05951 | 0.21973 | -0.23804 | -0.24262 | -0.23804 | -0.24262 | -0.054932 | -0.16937 | 0.018311 | 0.10529 | -0.09613 | -0.10986 | -0.041198 | -0.054931 | 0.21973 | 122.1542 | 0.16022 | 122.168 | 121.9345 | 121.9803 | 121.9345 | 121.9254 | -122.0947 | -122.1497 | 122.1542 | 122.113 | 62.2421 | 62.3337
864.4531 | 122.2321 | -62.3016 | 59.8297 | -0.013657 | 0.0018435 | 0.060957 | 0.060316 | 0.0025678 | -0.0044883 | 1.4934e-05 | -0.0021057 | 0.0032256 | 0.074928 | 0.063987 | -0.0094507 | 0.018158 | 0.0015658 | -0.13275 | 59.6832 | -62.2879 | 59.816 | -62.1277 | -62.5946 | -62.5534 | -0.082397 | 59.6603 | -62.3154 | 59.7885 | -62.2604 | -62.4619 | -62.4161 | 0.013733 | -0.14648 | -0.013733 | 0.17395 | -0.25177 | -0.29297 | -0.2655 | -0.3067 | -0.013733 | -0.16937 | -0.041199 | 0.041199 | -0.11444 | -0.16022 | -0.10071 | -0.14648 | 0.16022 | 122.1039 | 0.054932 | 122.1039 | 121.9711 | 121.9757 | 121.9849 | 121.962 | -122.1176 | -122.1451 | 122.1176 | 122.0901 | 62.1689 | 62.2192
866.2031 | 122.2687 | -62.2513 | 59.8389 | -0.013657 | 0.0009891 | 0.060103 | 0.059889 | 4.192e-06 | -0.0091879 | -0.00062587 | 0.0009461 | 0.0017304 | 0.074501 | 0.057151 | -0.0088097 | 0.020294 | -0.0014248 | -0.004578 | 59.6924 | -62.2696 | 59.8709 | -62.0636 | -62.5031 | -62.4802 | 0.041199 | 59.7198 | -62.2925 | 59.8389 | -62.1689 | -62.384 | -62.3474 | -0.01831 | -0.14648 | 0.032044 | 0.18768 | -0.22888 | -0.25177 | -0.21057 | -0.23346 | -0.041198 | -0.11902 | 0 | 0.082398 | -0.09613 | -0.13275 | -0.054932 | -0.091553 | 0.20599 | 122.1405 | 0.1236 | 122.1313 | 121.962 | 122.0123 | 121.9437 | 121.9711 | -122.1085 | -122.1313 | 122.1222 | 122.0901 | 62.2467 | 62.2925
867.9531 | 122.3145 | -62.2787 | 59.7748 | -0.013657 | 0.0050479 | 0.06053 | 0.061171 | 4.192e-06 | -0.0044883 | -0.0019077 | -0.0021057 | 0.0045074 | 0.069588 | 0.067618 | -0.0075281 | 0.018799 | -0.0056974 | -0.13275 | 59.6832 | -62.3062 | 59.848 | -62.0819 | -62.5626 | -62.5214 | -0.032043 | 59.6329 | -62.3108 | 59.8434 | -62.1872 | -62.3795 | -62.3337 | -0.027465 | -0.091552 | 0.073242 | 0.19684 | -0.24261 | -0.28381 | -0.21515 | -0.25635 | -0.032043 | -0.14191 | 0.068665 | 0.091553 | -0.054931 | -0.10071 | -0.022888 | -0.068665 | 0.2243 | 122.1542 | 0.1236 | 122.1542 | 121.9894 | 121.9437 | 121.962 | 121.9116 | -122.081 | -122.0856 | 122.1268 | 122.1222 | 62.146 | 62.2467
869.6406 | 122.287 | -62.2421 | 59.8434 | 0.0016023 | 0.0009891 | 0.058607 | 0.059248 | -0.00042301 | -0.0042745 | -0.0029759 | -0.0021057 | 0.001944 | 0.072792 | 0.065268 | -0.0092371 | 0.016876 | -0.0012112 | -0.013733 | 59.6649 | -62.2787 | 59.9075 | -62.0178 | -62.4847 | -62.4756 | 0.086975 | 59.6832 | -62.2696 | 59.8801 | -62.1597 | -62.352 | -62.3337 | -0.036622 | -0.17853 | 0.064087 | 0.2243 | -0.23346 | -0.24262 | -0.19684 | -0.20599 | -0.027466 | -0.16022 | 0.036621 | 0.082397 | -0.091553 | -0.10986 | -0.064087 | -0.082398 | 0.26093 | 122.1863 | 0.10986 | 122.1497 | 121.9437 | 121.9528 | 121.907 | 121.9254 | -122.1222 | -122.113 | 122.1497 | 122.1222 | 62.2284 | 62.3291
871.3281 | 122.2687 | -62.2467 | 59.8663 | -0.0060272 | 0.0029117 | 0.060744 | 0.056471 | -0.00085021 | -0.0057699 | -0.0023349 | -0.0051575 | 0.0010894 | 0.071724 | 0.065055 | -0.0083825 | 0.018158 | -0.0033474 | -0.009155 | 59.6786 | -62.2559 | 59.9121 | -61.9949 | -62.4893 | -62.4619 | 0.073242 | 59.6832 | -62.265 | 59.8709 | -62.1414 | -62.3474 | -62.3245 | -0.009155 | -0.18768 | 0.045776 | 0.25177 | -0.21515 | -0.24262 | -0.20599 | -0.23346 | -0.018311 | -0.1831 | 0.004578 | 0.10529 | -0.07782 | -0.10071 | -0.059509 | -0.082397 | 0.26093 | 122.168 | 0.1236 | 122.1359 | 121.9345 | 121.9482 | 121.9254 | 121.9299 | -122.1222 | -122.1313 | 122.1588 | 122.1176 | 62.2375 | 62.3199
873.0625 | 122.319 | -62.2421 | 59.8022 | -0.0060272 | 0.0029117 | 0.059462 | 0.056685 | 0.0010724 | -0.0044883 | -0.0068211 | -0.0051575 | 0.0032256 | 0.073006 | 0.066764 | -0.0081689 | 0.016876 | -0.0037748 | -0.16479 | 59.6558 | -62.2833 | 59.8755 | -62.059 | -62.5534 | -62.5076 | -0.022888 | 59.6512 | -62.3199 | 59.8709 | -62.1597 | -62.3474 | -62.3016 | -0.041199 | -0.14648 | 0.073242 | 0.1831 | -0.2655 | -0.31128 | -0.2243 | -0.27008 | -0.07782 | -0.15106 | 0.068665 | 0.082397 | -0.05951 | -0.10529 | 0.01831 | -0.027466 | 0.2243 | 122.1588 | 0.16022 | 122.1909 | 121.9391 | 121.9711 | 121.8979 | 121.8933 | -122.0856 | -122.1222 | 122.1176 | 122.113 | 62.0773 | 62.2192
874.8125 | 122.2595 | -62.2696 | 59.8572 | -0.013657 | -0.0007199 | 0.057967 | 0.056258 | -0.0023456 | -0.0076925 | -0.0034031 | 0.0009461 | 0.00066224 | 0.071297 | 0.060569 | -0.0066735 | 0.018158 | -0.0039884 | 0.041199 | 59.6558 | -62.2513 | 59.8984 | -62.0132 | -62.4802 | -62.4481 | 0.059509 | 59.697 | -62.2879 | 59.8297 | -62.1826 | -62.3611 | -62.3474 | 0.01831 | -0.20142 | 0.041198 | 0.25635 | -0.17853 | -0.21057 | -0.19684 | -0.22888 | -0.018311 | -0.16022 | -0.027466 | 0.086975 | -0.07782 | -0.091553 | -0.059509 | -0.073242 | 0.23804 | 122.1497 | 0.10529 | 122.1176 | 121.907 | 121.9849 | 121.9254 | 121.9666 | -122.1085 | -122.1451 | 122.168 | 122.0993 | 62.3108 | 62.3291
876.5781 | 122.2321 | -62.2604 | 59.8389 | -0.0060272 | 0.0022709 | 0.059248 | 0.057967 | 0.0010724 | -0.0064109 | -0.0048985 | -0.0021057 | 0.0034392 | 0.071297 | 0.058646 | -0.010305 | 0.019226 | -0.0005704 | -0.1236 | 59.6924 | -62.2833 | 59.8251 | -62.1048 | -62.5809 | -62.5351 | -0.07782 | 59.6741 | -62.2925 | 59.816 | -62.2421 | -62.439 | -62.2604 | -0.022888 | -0.14648 | -0.013733 | 0.15564 | -0.27466 | -0.32043 | -0.25177 | -0.29755 | -0.032043 | -0.16479 | -0.022888 | 0.018311 | 0 | -0.17853 | 0.032043 | -0.14649 | 0.17853 | 122.1085 | 0.050354 | 122.1085 | 121.9757 | 121.9666 | 121.9528 | 121.9345 | -122.1222 | -122.1313 | 122.0856 | 122.0764 | 62.1368 | 62.1826
878.2656 | 122.2366 | -62.2421 | 59.8984 | 0.0092313 | -0.0007199 | 0.056471 | 0.057112 | 0.0027814 | -0.0066245 | -0.00041227 | -0.0082093 | 0.003653 | 0.072151 | 0.060782 | -0.010092 | 0.018585 | -0.0071926 | -0.009155 | 59.697 | -62.2467 | 59.8938 | -62.0316 | -62.5076 | -62.4756 | 0.018311 | 59.7198 | -62.2559 | 59.8206 | -62.178 | -62.3657 | -62.2192 | -0.004578 | -0.20142 | -0.004577 | 0.21057 | -0.23346 | -0.2655 | -0.22888 | -0.26093 | -0.013733 | -0.17853 | -0.077819 | 0.064086 | 0.022888 | -0.1236 | 0.036621 | -0.10986 | 0.21515 | 122.1405 | 0.077819 | 122.0764 | 121.9437 | 121.9757 | 121.9391 | 121.962 | -122.1451 | -122.1542 | 122.1359 | 122.0627 | 62.233 | 62.2604
880.0156 | 122.319 | -62.233 | 59.7748 | -0.013657 | 0.0031253 | 0.06053 | 0.059248 | -0.00020941 | -0.0055563 | -0.00083947 | -0.0082093 | 2.1442e-05 | 0.073219 | 0.059714 | -0.0083825 | 0.016022 | -0.0003568 | -0.086975 | 59.6237 | -62.2238 | 59.9396 | -61.9446 | -62.4573 | -62.4161 | 0.054932 | 59.6283 | -62.2833 | 59.8984 | -62.1277 | -62.3154 | -62.1735 | 0.009155 | -0.15106 | 0.16479 | 0.28839 | -0.18311 | -0.2243 | -0.19226 | -0.23346 | -0.050354 | -0.14648 | 0.1236 | 0.10529 | 0.059509 | -0.082398 | 0.10986 | -0.032044 | 0.27924 | 122.1634 | 0.15564 | 122.1817 | 121.8475 | 121.9116 | 121.8567 | 121.8613 | -121.9986 | -122.0581 | 122.1725 | 122.1313 | 62.146 | 62.2879
881.7031 | 122.2137 | -62.233 | 59.8618 | 0.0016023 | 0.0048343 | 0.059889 | 0.059676 | 0.0023542 | -0.0047019 | -0.0014805 | -0.0051575 | 0.0045074 | 0.072792 | 0.063132 | -0.0079553 | 0.019012 | -0.0012112 | -0.054932 | 59.697 | -62.2375 | 59.8938 | -62.0453 | -62.5442 | -62.5168 | -0.022888 | 59.6878 | -62.2879 | 59.8206 | -62.233 | -62.4207 | -62.2559 | -0.004578 | -0.1648 | 0.032044 | 0.18768 | -0.28381 | -0.31128 | -0.27924 | -0.3067 | -0.054932 | -0.17395 | -0.041198 | 0 | -0.022888 | -0.18768 | 0.032044 | -0.13275 | 0.19226 | 122.1313 | 0.054932 | 122.1085 | 121.9345 | 121.9757 | 121.9299 | 121.9208 | -122.0993 | -122.1497 | 122.1268 | 122.0535 | 62.178 | 62.2101
883.3906 | 122.2504 | -62.2192 | 59.8938 | -0.0060272 | -0.0007199 | 0.06053 | 0.057753 | -0.0032 | -0.0072653 | -0.0057529 | -0.0051575 | 0.0017304 | 0.07151 | 0.059928 | -0.0092371 | 0.017944 | -0.0050564 | -0.004578 | 59.7244 | -62.265 | 59.8846 | -62.059 | -62.4985 | -62.4847 | 0.018311 | 59.7427 | -62.2742 | 59.8343 | -62.1597 | -62.3566 | -62.3062 | -0.045777 | -0.16937 | -0.009155 | 0.16022 | -0.2655 | -0.27924 | -0.21973 | -0.23346 | -0.054932 | -0.15106 | -0.059509 | 0.059509 | -0.086975 | -0.13733 | -0.032043 | -0.082397 | 0.20599 | 122.1497 | 0.11444 | 122.1085 | 121.9894 | 122.0169 | 121.9437 | 121.962 | -122.1588 | -122.168 | 122.1039 | 122.0535 | 62.2147 | 62.2375
885.125 | 122.2229 | -62.2284 | 59.9121 | -0.013657 | -0.0022153 | 0.05818 | 0.057326 | -0.0017048 | -0.0055563 | 0.00022853 | -0.0082093 | 0.0015166 | 0.072151 | 0.060569 | -0.0096643 | 0.017944 | -0.0016384 | -0.004578 | 59.7198 | -62.2238 | 59.8846 | -62.027 | -62.4893 | -62.4847 | 0.018311 | 59.7153 | -62.265 | 59.8297 | -62.1872 | -62.3703 | -62.3199 | 0.004578 | -0.19226 | -0.027465 | 0.20142 | -0.25635 | -0.26093 | -0.26093 | -0.2655 | -0.036621 | -0.19684 | -0.082397 | 0.041199 | -0.091552 | -0.14191 | -0.054931 | -0.10529 | 0.19684 | 122.1085 | 0.07782 | 122.0947 | 121.9437 | 121.9803 | 121.9482 | 121.9437 | -122.1359 | -122.1771 | 122.113 | 122.0581 | 62.2238 | 62.2467
886.8125 | 122.3419 | -62.2147 | 59.8618 | -0.0060272 | -0.0013607 | 0.05818 | 0.054762 | 0.00043159 | -0.0096151 | -0.0023349 | -0.0051575 | 0.00087584 | 0.070442 | 0.053519 | -0.0094507 | 0.016235 | -0.002493 | 0.045776 | 59.6512 | -62.1918 | 59.9899 | -61.8988 | -62.3795 | -62.3566 | 0.15106 | 59.7061 | -62.2375 | 59.935 | -62.0773 | -62.2421 | -62.2147 | 0.022889 | -0.21057 | 0.12817 | 0.31586 | -0.14191 | -0.16479 | -0.16479 | -0.18768 | -0.022888 | -0.15564 | 0.073243 | 0.13733 | 0 | -0.027465 | 0.022888 | -0.004577 | 0.29297 | 122.1817 | 0.16022 | 122.1725 | 121.843 | 121.9437 | 121.8658 | 121.9208 | -122.0535 | -122.0993 | 122.2046 | 122.1497 | 62.2604 | 62.3657
888.5 | 122.2778 | -62.1964 | 59.8938 | -0.013657 | 0.0024845 | 0.058394 | 0.057539 | -0.0025592 | -0.0044883 | -0.0044711 | -0.0021057 | 0.0034392 | 0.070442 | 0.057364 | -0.010946 | 0.018585 | -0.004202 | 0 | 59.7061 | -62.2147 | 59.9487 | -61.9858 | -62.4573 | -62.4344 | 0.073242 | 59.7153 | -62.265 | 59.903 | -62.1368 | -62.3199 | -62.2742 | -0.018311 | -0.18768 | 0.054931 | 0.21057 | -0.23804 | -0.26093 | -0.21973 | -0.24261 | -0.068665 | -0.17853 | 0.009155 | 0.059509 | -0.07782 | -0.1236 | -0.009155 | -0.054931 | 0.22888 | 122.1634 | 0.12817 | 122.168 | 121.9208 | 121.9803 | 121.9025 | 121.9116 | -122.1085 | -122.1588 | 122.1451 | 122.0993 | 62.1964 | 62.2696
890.1875 | 122.2458 | -62.2375 | 59.903 | -0.013657 | 0.0009891 | 0.058607 | 0.059676 | -0.0010638 | -0.0059835 | 0.00065573 | -0.0051575 | 0.003653 | 0.071938 | 0.072532 | -0.010732 | 0.018158 | 0.000925 | -0.018311 | 59.697 | -62.2192 | 59.9213 | -61.9904 | -62.4802 | -62.4527 | 0.050354 | 59.7198 | -62.2421 | 59.8663 | -62.1689 | -62.384 | -62.3108 | 0.018311 | -0.20599 | 0.018311 | 0.24719 | -0.21515 | -0.24262 | -0.23346 | -0.26093 | -0.004577 | -0.1831 | -0.036621 | 0.068665 | -0.073242 | -0.14648 | -0.068665 | -0.14191 | 0.22888 | 122.1405 | 0.073242 | 122.1085 | 121.9162 | 121.962 | 121.9345 | 121.9574 | -122.1222 | -122.1451 | 122.1588 | 122.1039 | 62.2192 | 62.2879
891.9375 | 122.2366 | -62.2055 | 59.903 | -0.013657 | 0.0005619 | 0.056685 | 0.056044 | -0.0032 | -0.0038473 | 0.00044213 | -0.0051575 | 0.003012 | 0.072792 | 0.066336 | -0.0083825 | 0.01709 | -0.0031338 | 0.041199 | 59.7107 | -62.2147 | 59.9442 | -61.972 | -62.439 | -62.4115 | 0.059509 | 59.7473 | -62.2284 | 59.8526 | -62.146 | -62.3337 | -62.3108 | -0.009156 | -0.19226 | 0.041199 | 0.23346 | -0.20599 | -0.23346 | -0.19684 | -0.2243 | -0.022889 | -0.15564 | -0.050354 | 0.059509 | -0.10529 | -0.12817 | -0.082397 | -0.10528 | 0.24262 | 122.1588 | 0.082398 | 122.081 | 121.9254 | 121.9757 | 121.9162 | 121.9528 | -122.1176 | -122.1313 | 122.1497 | 122.0581 | 62.2467 | 62.265
893.6094 | 122.319 | -62.2055 | 59.8297 | -0.013657 | 0.0020571 | 0.060103 | 0.059462 | -0.0036274 | -0.0042745 | -0.0019077 | -0.0021057 | 0.001303 | 0.071297 | 0.066977 | -0.011587 | 0.018799 | -0.0027066 | -0.13733 | 59.7061 | -62.2375 | 59.8984 | -62.0316 | -62.5214 | -62.4893 | -0.041199 | 59.6741 | -62.2879 | 59.8984 | -62.114 | -62.3108 | -62.2559 | -0.032044 | -0.1236 | 0.068664 | 0.17395 | -0.28381 | -0.31586 | -0.25177 | -0.28381 | -0.082398 | -0.15564 | 0.068664 | 0.091552 | -0.050354 | -0.10529 | 0.032044 | -0.022888 | 0.20599 | 122.1359 | 0.17395 | 122.1863 | 121.9437 | 121.962 | 121.9116 | 121.8796 | -122.0673 | -122.1176 | 122.1039 | 122.1039 | 62.0682 | 62.1643
895.3125 | 122.3282 | -62.2147 | 59.8572 | -0.0060272 | 0.0005619 | 0.059462 | 0.057112 | -0.0029864 | -0.0053427 | -0.0046847 | 0.0009461 | -0.00083316 | 0.070656 | 0.059287 | -0.0098779 | 0.019867 | -0.0009976 | -0.073242 | 59.6649 | -62.2192 | 59.935 | -61.9766 | -62.4527 | -62.4069 | 0.013733 | 59.6832 | -62.233 | 59.903 | -62.0911 | -62.2879 | -62.2604 | -0.004577 | -0.19226 | 0.07782 | 0.23804 | -0.19226 | -0.23804 | -0.18768 | -0.23346 | -0.01831 | -0.17395 | 0.045776 | 0.1236 | -0.045776 | -0.073242 | -0.027466 | -0.054932 | 0.24261 | 122.1542 | 0.14191 | 122.1359 | 121.8842 | 121.9162 | 121.8796 | 121.8979 | -122.0764 | -122.0901 | 122.1497 | 122.1176 | 62.1414 | 62.2284
897.0625 | 122.2733 | -62.2147 | 59.9075 | -0.0060272 | 0.0039799 | 0.060744 | 0.061171 | 0.00064519 | -0.0049155 | -0.00019867 | -0.0051575 | 0.0034392 | 0.070229 | 0.067405 | -0.012441 | 0.018158 | -0.0061246 | 0.009155 | 59.729 | -62.2192 | 59.9854 | -61.9446 | -62.4344 | -62.4069 | 0.068665 | 59.7244 | -62.2421 | 59.9167 | -62.1368 | -62.3108 | -62.2787 | -0.004577 | -0.17853 | 0.07782 | 0.27008 | -0.19226 | -0.21973 | -0.18768 | -0.21515 | -0.027465 | -0.18311 | 0.009155 | 0.07782 | -0.064087 | -0.09613 | -0.036622 | -0.068665 | 0.27466 | 122.2046 | 0.10529 | 122.1588 | 121.9482 | 121.9666 | 121.9437 | 121.9391 | -122.1268 | -122.1497 | 122.2 | 122.1313 | 62.2238 | 62.2833
898.75 | 122.2687 | -62.178 | 59.935 | -0.021286 | -0.0005063 | 0.059889 | 0.055617 | -0.00063661 | -0.0066245 | -0.0051121 | -0.0051575 | 0.0021576 | 0.069801 | 0.058646 | -0.010092 | 0.016876 | -0.0022794 | 0.041199 | 59.6832 | -62.1918 | 60.0082 | -61.8988 | -62.3703 | -62.3337 | 0.10529 | 59.7336 | -62.2238 | 59.9121 | -62.0773 | -62.2742 | -62.2375 | -0.013732 | -0.25177 | 0.073242 | 0.27924 | -0.15564 | -0.19226 | -0.14191 | -0.17853 | -0.045776 | -0.20142 | -0.022889 | 0.10071 | -0.059509 | -0.09613 | -0.013733 | -0.050354 | 0.29297 | 122.2 | 0.14648 | 122.1359 | 121.875 | 121.9574 | 121.8613 | 121.9116 | -122.1268 | -122.1588 | 122.1863 | 122.0901 | 62.2192 | 62.2833
900.4375 | 122.3602 | -62.2055 | 59.8343 | -0.0060272 | 0.0024845 | 0.059676 | 0.059035 | -0.0012774 | -0.0036337 | -0.0036167 | -0.0021057 | 0.0015166 | 0.071938 | 0.057578 | -0.010946 | 0.019653 | -0.004202 | -0.086975 | 59.697 | -62.1964 | 59.9899 | -61.9354 | -62.4207 | -62.3749 | 0.045776 | 59.6832 | -62.233 | 59.9487 | -62.0773 | -62.2513 | -62.2284 | 0.009155 | -0.13733 | 0.15564 | 0.27008 | -0.16937 | -0.21515 | -0.17853 | -0.2243 | -0.027466 | -0.15106 | 0.11444 | 0.12817 | -0.022889 | -0.045777 | 0.004577 | -0.018311 | 0.26093 | 122.1863 | 0.15564 | 122.1817 | 121.8933 | 121.9162 | 121.9025 | 121.8887 | -122.0306 | -122.0673 | 122.1954 | 122.1542 | 62.1185 | 62.2513
902.2031 | 122.2778 | -62.1918 | 59.9213 | -0.021286 | 0.0018435 | 0.060957 | 0.05818 | 0.0027814 | -0.0070517 | -0.00041227 | -0.0021057 | 0.0027984 | 0.07386 | 0.069327 | -0.0096643 | 0.018158 | -0.0003568 | 0.009155 | 59.7702 | -62.1918 | 59.9808 | -61.9354 | -62.4252 | -62.3978 | 0.073242 | 59.7565 | -62.2101 | 59.9304 | -62.1002 | -62.2833 | -62.2421 | 0 | -0.15106 | 0.059509 | 0.25635 | -0.20599 | -0.23346 | -0.20599 | -0.23346 | -0.018311 | -0.16479 | 0.009155 | 0.091552 | -0.050354 | -0.091553 | -0.032043 | -0.073242 | 0.25635 | 122.1725 | 0.10986 | 122.1405 | 121.962 | 121.9666 | 121.962 | 121.9482 | -122.113 | -122.1313 | 122.1725 | 122.1222 | 62.2009 | 62.265
903.9375 | 122.287 | -62.178 | 59.9167 | -0.021286 | 0.0001345 | 0.059035 | 0.058394 | 0.0038494 | -0.0064109 | -0.0023349 | -0.0082093 | 0.001303 | 0.072792 | 0.070609 | -0.010732 | 0.021149 | 0.000925 | -0.004578 | 59.7565 | -62.1826 | 59.9579 | -61.9537 | -62.4161 | -62.4115 | 0.045776 | 59.7656 | -62.1964 | 59.9167 | -62.0819 | -62.2742 | -62.2513 | -0.004577 | -0.16022 | 0.041199 | 0.22431 | -0.23346 | -0.23804 | -0.22888 | -0.23346 | -0.01831 | -0.15106 | 0 | 0.096131 | -0.073242 | -0.09613 | -0.054932 | -0.07782 | 0.22888 | 122.1405 | 0.11444 | 122.113 | 121.9391 | 121.962 | 121.9345 | 121.9437 | -122.0993 | -122.113 | 122.1359 | 122.0947 | 62.1735 | 62.2238
905.6719 | 122.2549 | -62.1872 | 59.9487 | -0.0060272 | -0.0011471 | 0.059035 | 0.057326 | -0.0034136 | -0.0076925 | -0.0021213 | -0.0051575 | 0.0027984 | 0.073219 | 0.060569 | -0.0081689 | 0.018158 | 0.0002842 | 0.045776 | 59.7473 | -62.1689 | 59.9899 | -61.9125 | -62.3657 | -62.352 | 0.064087 | 59.7885 | -62.2009 | 59.9075 | -62.1048 | -62.2833 | -62.2513 | 0.018311 | -0.20142 | 0.041199 | 0.27466 | -0.16479 | -0.17853 | -0.18311 | -0.19684 | -0.013733 | -0.16022 | -0.041198 | 0.082398 | -0.064087 | -0.09613 | -0.050354 | -0.082397 | 0.25635 | 122.1588 | 0.096131 | 122.1085 | 121.9162 | 121.9894 | 121.9345 | 121.9757 | -122.1176 | -122.1497 | 122.1771 | 122.0947 | 62.233 | 62.2513
907.3594 | 122.2137 | -62.2101 | 59.9258 | -0.013657 | 0.0035525 | 0.061171 | 0.061171 | -0.00085021 | -0.0066245 | -0.0021213 | -0.0051575 | 0.003653 | 0.072792 | 0.063132 | -0.0085961 | 0.019012 | -0.0012112 | -0.10071 | 59.7565 | -62.178 | 59.9075 | -62.0544 | -62.5305 | -62.4802 | -0.11444 | 59.7656 | -62.2604 | 59.8663 | -62.1735 | -62.3749 | -62.2787 | 0.032043 | -0.16937 | -0.01831 | 0.15564 | -0.27008 | -0.32044 | -0.30212 | -0.35248 | -0.050354 | -0.16022 | -0.059509 | 0.036621 | -0.068665 | -0.1648 | -0.018311 | -0.11444 | 0.1236 | 122.0856 | 0.086975 | 122.1268 | 121.9345 | 122.0261 | 121.9666 | 121.9757 | -122.1039 | -122.1863 | 122.1176 | 122.0764 | 62.1094 | 62.0956
909.0938 | 122.287 | -62.1368 | 59.935 | 0.0016023 | 0.0029117 | 0.059248 | 0.057112 | 0.001286 | -0.0061971 | -0.0019077 | -0.0051575 | 0.0021576 | 0.070015 | 0.061423 | -0.0092371 | 0.018799 | -0.0018522 | 0.004578 | 59.7656 | -62.1872 | 59.9899 | -61.9171 | -62.4023 | -62.3886 | 0.07782 | 59.7748 | -62.1918 | 59.9442 | -62.0682 | -62.2787 | -62.2055 | -0.050354 | -0.16937 | 0.054931 | 0.21973 | -0.25177 | -0.2655 | -0.20142 | -0.21515 | -0.054931 | -0.16022 | 0.009155 | 0.068665 | -0.068664 | -0.14191 | -0.013733 | -0.086976 | 0.27008 | 122.1771 | 0.1236 | 122.1359 | 121.9528 | 121.9666 | 121.9025 | 121.9116 | -122.1222 | -122.1268 | 122.1268 | 122.081 | 62.1414 | 62.2147
910.8438 | 122.3373 | -62.1552 | 59.8892 | -0.021286 | 0.0007755 | 0.061812 | 0.056471 | -0.001491 | -0.0040609 | -0.0027621 | -0.0051575 | 0.0015166 | 0.071083 | 0.060355 | -0.0064599 | 0.017731 | -0.0003568 | -0.091553 | 59.7198 | -62.1506 | 59.9945 | -61.8851 | -62.3978 | -62.3474 | 0.041199 | 59.7061 | -62.2101 | 59.9625 | -62.0682 | -62.2375 | -62.2009 | 0.004577 | -0.16937 | 0.10529 | 0.27008 | -0.19226 | -0.24262 | -0.19684 | -0.24719 | -0.054932 | -0.1831 | 0.073242 | 0.086975 | -0.045777 | -0.082398 | 0.009155 | -0.027466 | 0.2655 | 122.1451 | 0.14191 | 122.1725 | 121.8704 | 121.9162 | 121.875 | 121.8613 | -122.0398 | -122.0993 | 122.1497 | 122.1176 | 62.0636 | 62.1963
912.6094 | 122.3282 | -62.1643 | 59.9213 | 0.0016023 | -7.9104e-05 | 0.061385 | 0.056044 | -0.00555 | -0.0064109 | -0.00062587 | -0.0051575 | 0.00087584 | 0.072151 | 0.069327 | -0.010305 | 0.016876 | -0.0046292 | -0.07782 | 59.729 | -62.1506 | 59.9899 | -61.9263 | -62.3978 | -62.3291 | 0.032043 | 59.7473 | -62.1872 | 59.9533 | -62.027 | -62.2192 | -62.1735 | 0.013733 | -0.19226 | 0.068664 | 0.23804 | -0.16479 | -0.23346 | -0.17853 | -0.24719 | -0.022888 | -0.17395 | 0.032043 | 0.13733 | -0.009155 | -0.054931 | 0.013733 | -0.032043 | 0.2243 | 122.1405 | 0.16022 | 122.1405 | 121.8796 | 121.9345 | 121.8933 | 121.9116 | -122.0718 | -122.1085 | 122.1542 | 122.1176 | 62.0865 | 62.1964
914.3125 | 122.2778 | -62.1323 | 59.9808 | -0.013657 | 0.0016299 | 0.060744 | 0.06053 | 4.192e-06 | -0.0051291 | -0.0016941 | -0.0051575 | 0.0023712 | 0.071938 | 0.062278 | -0.011373 | 0.018158 | -0.0048428 | -0.013733 | 59.7839 | -62.1414 | 59.9899 | -61.9492 | -62.3749 | -62.3703 | 0.022888 | 59.8297 | -62.1872 | 59.9533 | -62.0499 | -62.2559 | -62.2101 | -0.009155 | -0.19684 | 0.009155 | 0.18311 | -0.23804 | -0.24262 | -0.22888 | -0.23346 | -0.054932 | -0.15106 | -0.027466 | 0.082397 | -0.07782 | -0.1236 | -0.022888 | -0.068664 | 0.19226 | 122.1313 | 0.13733 | 122.1405 | 121.9254 | 122.0169 | 121.9162 | 121.962 | -122.1222 | -122.168 | 122.1222 | 122.0856 | 62.1185 | 62.1552
916.0625 | 122.3145 | -62.1094 | 59.9579 | -0.0060272 | -7.9104e-05 | 0.058607 | 0.055617 | -0.0019184 | -0.0070517 | -0.0016941 | 0.0009461 | 0.00044864 | 0.072365 | 0.064414 | -0.0083825 | 0.017303 | -0.003561 | 0.050354 | 59.7427 | -62.1094 | 60.0952 | -61.8164 | -62.2604 | -62.2696 | 0.14191 | 59.7931 | -62.1506 | 60.0082 | -61.9904 | -62.1552 | -62.1414 | 0 | -0.21515 | 0.13733 | 0.29297 | -0.16022 | -0.15106 | -0.16022 | -0.15106 | -0.041199 | -0.1648 | 0.050354 | 0.11902 | -0.032043 | -0.045776 | 0.009156 | -0.004577 | 0.29297 | 122.2046 | 0.16022 | 122.1588 | 121.8521 | 121.9437 | 121.8521 | 121.9025 | -122.0673 | -122.1085 | 122.2046 | 122.1176 | 62.1597 | 62.2513
917.8281 | 122.3785 | -62.1094 | 59.935 | -0.0060272 | -0.0020017 | 0.059889 | 0.054976 | 0.0017132 | -0.0083335 | -0.0031895 | -0.0051575 | -0.00040596 | 0.073433 | 0.059287 | -0.0088097 | 0.017517 | -0.004202 | 0.032043 | 59.7473 | -62.1185 | 60.1273 | -61.7706 | -62.2375 | -62.2192 | 0.1831 | 59.7656 | -62.146 | 60.0403 | -61.94 | -62.1323 | -62.1094 | -0.009155 | -0.18768 | 0.19226 | 0.33875 | -0.10986 | -0.12817 | -0.10071 | -0.11902 | -0.036621 | -0.16937 | 0.10529 | 0.16937 | 0 | -0.022888 | 0.036621 | 0.013733 | 0.3479 | 122.2458 | 0.20599 | 122.1863 | 121.8658 | 121.9116 | 121.8567 | 121.875 | -122.0535 | -122.081 | 122.2366 | 122.1497 | 62.1414 | 62.2925
919.5781 | 122.2275 | -62.1231 | 60.0357 | -0.0060272 | -0.0007199 | 0.059035 | 0.059889 | -0.0017048 | -0.0079061 | -0.0014805 | -0.0021057 | 0.001944 | 0.072365 | 0.067191 | -0.0098779 | 0.01709 | -0.0050564 | -0.009155 | 59.8389 | -62.1094 | 59.9991 | -61.9171 | -62.3795 | -62.3611 | 0.009155 | 59.8572 | -62.146 | 59.9396 | -62.0865 | -62.2467 | -62.2147 | 0.013733 | -0.19684 | -0.036622 | 0.20599 | -0.23804 | -0.25635 | -0.25177 | -0.27008 | -0.022888 | -0.17853 | -0.096131 | 0.036621 | -0.091553 | -0.1236 | -0.068665 | -0.10071 | 0.19226 | 122.1085 | 0.059509 | 122.0856 | 121.9482 | 122.0032 | 121.962 | 121.9803 | -122.1451 | -122.1817 | 122.1222 | 122.0627 | 62.114 | 62.1323
921.25 | 122.319 | -62.1185 | 59.9442 | -0.0060272 | 0.0018435 | 0.059889 | 0.058394 | -0.0051226 | -0.0066245 | -0.0014805 | -0.0021057 | -0.00019216 | 0.07151 | 0.060141 | -0.0083825 | 0.015381 | -0.0014248 | -0.086975 | 59.7427 | -62.1185 | 60.0266 | -61.8988 | -62.3703 | -62.3245 | -0.022888 | 59.7794 | -62.1735 | 59.9854 | -62.0224 | -62.2147 | -62.1643 | 0 | -0.20142 | 0.082397 | 0.21973 | -0.20599 | -0.25177 | -0.20599 | -0.25177 | -0.054932 | -0.16479 | 0.041199 | 0.09613 | -0.045777 | -0.096131 | 0.009155 | -0.041199 | 0.21973 | 122.1451 | 0.15106 | 122.1588 | 121.8613 | 121.9528 | 121.8613 | 121.8979 | -122.0627 | -122.1176 | 122.1451 | 122.1039 | 62.0316 | 62.0956
923 | 122.2549 | -62.1185 | 60.0082 | -0.013657 | -0.0007199 | 0.059889 | 0.06053 | -0.0032 | -0.0081197 | -0.0014805 | -0.0021057 | 0.0025848 | 0.068947 | 0.0689 | -0.010732 | 0.017731 | -0.0037748 | -0.004578 | 59.848 | -62.1002 | 60.0311 | -61.9263 | -62.352 | -62.3428 | 0.022888 | 59.8572 | -62.1277 | 59.9808 | -62.0316 | -62.2192 | -62.1735 | 0.01831 | -0.16022 | 0.022888 | 0.19226 | -0.2243 | -0.23346 | -0.24261 | -0.25177 | -0.009156 | -0.15106 | -0.027466 | 0.086975 | -0.054932 | -0.10071 | -0.045776 | -0.091552 | 0.17395 | 122.1313 | 0.096131 | 122.1085 | 121.9482 | 121.9849 | 121.9666 | 121.9757 | -122.1085 | -122.1359 | 122.1497 | 122.0993 | 62.114 | 62.1414
924.75 | 122.3099 | -62.114 | 59.9808 | -0.013657 | 0.0037661 | 0.059462 | 0.056898 | -0.001491 | -0.0042745 | -0.0053257 | -0.0021057 | 0.00066224 | 0.070015 | 0.063346 | -0.0098779 | 0.020081 | -0.0029202 | -0.086975 | 59.7885 | -62.0911 | 60.0769 | -61.8393 | -62.3428 | -62.2879 | 0.032043 | 59.8068 | -62.1552 | 60.0174 | -62.0178 | -62.1872 | -62.1552 | 0.022889 | -0.19226 | 0.09613 | 0.27466 | -0.17395 | -0.22888 | -0.19684 | -0.25177 | -0.041198 | -0.17395 | 0.036621 | 0.096131 | -0.041198 | -0.073242 | 0 | -0.032044 | 0.25177 | 122.168 | 0.13733 | 122.1725 | 121.8796 | 121.962 | 121.9025 | 121.9208 | -122.0718 | -122.1359 | 122.1909 | 122.1313 | 62.027 | 62.146
926.4375 | 122.2458 | -62.0911 | 60.022 | 0.0016023 | -0.0011471 | 0.057539 | 0.058607 | 4.192e-06 | -0.0066245 | 0.0017239 | 0.0009461 | 0.0027984 | 0.072792 | 0.062064 | -0.010305 | 0.017303 | -0.0001432 | 0 | 59.8526 | -62.0956 | 60.0449 | -61.8805 | -62.3383 | -62.3108 | 0.036621 | 59.8755 | -62.1277 | 59.9808 | -62.0316 | -62.2147 | -62.1826 | -0.004578 | -0.16937 | 0.022888 | 0.21057 | -0.21973 | -0.24719 | -0.21515 | -0.24262 | -0.036622 | -0.14649 | -0.041199 | 0.059509 | -0.091553 | -0.1236 | -0.054931 | -0.086975 | 0.21515 | 122.1405 | 0.096131 | 122.1085 | 121.9482 | 122.0032 | 121.9437 | 121.9666 | -122.1176 | -122.1497 | 122.1359 | 122.0718 | 62.0911 | 62.1277
928.1875 | 122.2916 | -62.0819 | 60.0082 | -0.0060272 | 0.0024845 | 0.061598 | 0.062025 | -0.00085021 | -0.0059835 | -0.0031895 | -0.0021057 | 0.0021576 | 0.07151 | 0.068686 | -0.0090235 | 0.019226 | -0.00527 | 0 | 59.8526 | -62.0956 | 60.0906 | -61.8301 | -62.3062 | -62.2925 | 0.07782 | 59.8526 | -62.0911 | 60.0403 | -61.9766 | -62.1872 | -62.1231 | -0.013733 | -0.15564 | 0.082397 | 0.25177 | -0.21057 | -0.2243 | -0.19684 | -0.21057 | -0.009155 | -0.15564 | 0.032043 | 0.10529 | -0.041199 | -0.10529 | -0.032044 | -0.096131 | 0.2655 | 122.1863 | 0.11444 | 122.1313 | 121.9482 | 121.9437 | 121.9345 | 121.9345 | -122.1039 | -122.0993 | 122.1725 | 122.1222 | 62.0819 | 62.1597
929.9375 | 122.3511 | -62.0407 | 59.9487 | -0.013657 | 0.0018435 | 0.061171 | 0.058821 | -0.00085021 | -0.0034201 | -0.0029759 | -0.0021057 | -0.00083316 | 0.070442 | 0.061209 | -0.010732 | 0.018585 | -0.0005704 | -0.082397 | 59.7794 | -62.0636 | 60.1227 | -61.7889 | -62.2971 | -62.2421 | 0.073242 | 59.8068 | -62.1231 | 60.0952 | -61.9446 | -62.1185 | -62.0773 | -0.022889 | -0.16937 | 0.17395 | 0.25177 | -0.20142 | -0.25635 | -0.17853 | -0.23346 | -0.082398 | -0.14191 | 0.14649 | 0.09613 | -0.036622 | -0.07782 | 0.045776 | 0.004578 | 0.27466 | 122.1863 | 0.17853 | 122.2183 | 121.843 | 121.9299 | 121.8201 | 121.8475 | -122.0123 | -122.0718 | 122.1634 | 122.1359 | 61.9583 | 62.114
931.6875 | 122.287 | -62.0453 | 60.0632 | -0.013657 | 0.0012027 | 0.057112 | 0.059676 | -0.00020941 | -0.0053427 | -0.0034031 | 0.0009461 | 0.0023712 | 0.071938 | 0.067405 | -0.010732 | 0.016449 | -0.0027066 | -0.004578 | 59.8938 | -62.0544 | 60.0906 | -61.853 | -62.2833 | -62.2742 | 0.018311 | 59.8892 | -62.0682 | 60.0677 | -61.972 | -62.1643 | -62.1002 | -0.009155 | -0.16937 | 0.027466 | 0.19226 | -0.22888 | -0.23804 | -0.21973 | -0.22888 | -0.022888 | -0.17395 | 0.004578 | 0.073242 | -0.054932 | -0.11902 | -0.032044 | -0.096131 | 0.20142 | 122.1451 | 0.09613 | 122.1359 | 121.9482 | 121.9574 | 121.9391 | 121.9345 | -122.1176 | -122.1313 | 122.1359 | 122.113 | 62.0407 | 62.0636
933.375 | 122.319 | -62.0132 | 60.0494 | -0.0060272 | 0.0014163 | 0.058394 | 0.055403 | -0.0025592 | -0.0064109 | -0.0034031 | 0.0009461 | 0.001303 | 0.073006 | 0.050528 | -0.010519 | 0.019012 | -0.0009976 | 0.050354 | 59.8801 | -62.0544 | 60.1913 | -61.7111 | -62.1872 | -62.1735 | 0.12817 | 59.8984 | -62.0636 | 60.0998 | -61.8759 | -62.059 | -62.0178 | -0.041198 | -0.16937 | 0.14191 | 0.30212 | -0.16022 | -0.17395 | -0.11902 | -0.13275 | -0.050354 | -0.15106 | 0.050354 | 0.13733 | -0.004577 | -0.045776 | 0.045777 | 0.004578 | 0.34332 | 122.2458 | 0.18768 | 122.1634 | 121.9345 | 121.962 | 121.8933 | 121.9116 | -122.1039 | -122.113 | 122.2046 | 122.113 | 62.0636 | 62.1414
935.1094 | 122.2458 | -62.0224 | 60.0952 | -0.013657 | -7.9104e-05 | 0.059462 | 0.055189 | -0.00042301 | -0.0064109 | -0.0012669 | -0.0021057 | 0.00066224 | 0.072151 | 0.053519 | -0.010732 | 0.01709 | -0.0048428 | 0.036621 | 59.8755 | -62.027 | 60.1364 | -61.7844 | -62.2467 | -62.2147 | 0.059509 | 59.9213 | -62.0361 | 60.054 | -61.9675 | -62.1368 | -62.1094 | -0.004578 | -0.21973 | 0.041199 | 0.23804 | -0.19226 | -0.2243 | -0.18768 | -0.21973 | -0.013733 | -0.17395 | -0.041199 | 0.054932 | -0.086975 | -0.11444 | -0.073242 | -0.10071 | 0.24262 | 122.1634 | 0.068665 | 122.0901 | 121.9025 | 121.9574 | 121.8979 | 121.9437 | -122.1222 | -122.1313 | 122.1588 | 122.0764 | 62.059 | 62.0819
936.7812 | 122.2092 | -62.0407 | 60.1044 | -0.0060272 | 0.0029117 | 0.059248 | 0.060316 | 0.00043159 | -0.0042745 | -0.0025485 | -0.0082093 | 0.0055756 | 0.071724 | 0.070395 | -0.010092 | 0.017944 | -0.002493 | -0.091553 | 59.935 | -62.0316 | 60.0952 | -61.8439 | -62.3199 | -62.2742 | -0.07782 | 59.9579 | -62.0499 | 60.054 | -62.0041 | -62.1964 | -62.0865 | 0.009155 | -0.16937 | -0.009155 | 0.19684 | -0.23346 | -0.27924 | -0.24262 | -0.28839 | -0.009156 | -0.14648 | -0.050354 | 0.036621 | -0.045777 | -0.15564 | -0.036621 | -0.14648 | 0.18768 | 122.1268 | 0.045777 | 122.1039 | 121.9666 | 122.0078 | 121.9757 | 121.9986 | -122.1359 | -122.1542 | 122.1359 | 122.0947 | 61.9492 | 61.9629
938.5312 | 122.2641 | -61.9858 | 60.141 | -0.0060272 | 0.0012027 | 0.060103 | 0.056898 | 0.0019268 | -0.0070517 | -0.0034031 | -0.0051575 | 0.0025848 | 0.071724 | 0.065055 | -0.0094507 | 0.018372 | -0.0039884 | -0.018311 | 59.9625 | -62.0087 | 60.1273 | -61.8027 | -62.2559 | -62.2421 | 0.013733 | 59.9716 | -62.0361 | 60.0906 | -61.9263 | -62.1185 | -62.027 | -0.022888 | -0.17853 | -0.013733 | 0.18311 | -0.25635 | -0.27008 | -0.23346 | -0.24719 | -0.050354 | -0.16937 | -0.050354 | 0.059509 | -0.041199 | -0.13275 | 0.009155 | -0.082397 | 0.20599 | 122.1359 | 0.10986 | 122.1268 | 121.9711 | 122.0078 | 121.9482 | 121.9574 | -122.1497 | -122.1771 | 122.113 | 122.0764 | 61.9675 | 61.9995
940.2188 | 122.3373 | -61.9583 | 60.0815 | -0.0060272 | 0.0001345 | 0.058394 | 0.054762 | -0.0046954 | -0.0085471 | -0.0025485 | -0.0021057 | -0.00083316 | 0.073433 | 0.055655 | -0.010519 | 0.016449 | 0.000925 | 0.041199 | 59.903 | -61.9629 | 60.2509 | -61.6608 | -62.1231 | -62.114 | 0.16022 | 59.9075 | -62.0041 | 60.1776 | -61.8073 | -61.9858 | -61.8942 | -0.004578 | -0.17853 | 0.16937 | 0.29755 | -0.15564 | -0.1648 | -0.15106 | -0.16022 | -0.045776 | -0.17395 | 0.09613 | 0.15106 | 0.064087 | -0.027466 | 0.10986 | 0.01831 | 0.30212 | 122.2137 | 0.19684 | 122.1817 | 121.8658 | 121.9116 | 121.8613 | 121.8658 | -122.0444 | -122.0856 | 122.2092 | 122.1359 | 61.9995 | 62.1185
941.9688 | 122.3511 | -61.94 | 60.1044 | -0.0060272 | -7.9104e-05 | 0.060957 | 0.056258 | 0.0038494 | -0.0036337 | -0.0038303 | -0.0082093 | 0.0027984 | 0.07151 | 0.063132 | -0.0088097 | 0.018372 | -0.003561 | 0.050354 | 59.9167 | -61.9537 | 60.2737 | -61.647 | -62.114 | -62.1048 | 0.15564 | 59.9442 | -61.9904 | 60.2097 | -61.7844 | -61.9858 | -61.8896 | -0.013733 | -0.18768 | 0.16937 | 0.29297 | -0.16479 | -0.17395 | -0.15106 | -0.16022 | -0.050354 | -0.16022 | 0.10529 | 0.15564 | 0.050354 | -0.045777 | 0.10071 | 0.004577 | 0.3067 | 122.2275 | 0.20599 | 122.2 | 121.8704 | 121.9345 | 121.8567 | 121.8842 | -122.0581 | -122.0947 | 122.2137 | 122.1497 | 61.9904 | 62.0956
943.7188 | 122.3419 | -61.9217 | 60.0952 | -0.0060272 | 0.0024845 | 0.059889 | 0.060316 | 0.00064519 | -0.0027793 | -0.0051121 | -0.0051575 | 0.0023712 | 0.06916 | 0.0642 | -0.011801 | 0.017303 | -0.0016384 | -0.11444 | 59.9487 | -61.9537 | 60.2188 | -61.702 | -62.1964 | -62.1506 | 0.018311 | 59.935 | -61.9904 | 60.2051 | -61.8301 | -62.0224 | -61.8622 | -0.032043 | -0.14649 | 0.1236 | 0.21973 | -0.22888 | -0.27466 | -0.19684 | -0.24262 | -0.068664 | -0.16022 | 0.10986 | 0.091553 | 0.059509 | -0.10071 | 0.12817 | -0.032044 | 0.25177 | 122.1725 | 0.16022 | 122.1954 | 121.9025 | 121.9254 | 121.8704 | 121.8567 | -122.049 | -122.0856 | 122.1405 | 122.1268 | 61.8073 | 61.94
945.4219 | 122.3557 | -61.8759 | 60.1456 | -0.013657 | -0.0002927 | 0.05818 | 0.055617 | -0.0023456 | -0.0081197 | -0.0027621 | -0.0051575 | 2.1442e-05 | 0.071297 | 0.063559 | -0.0092371 | 0.017944 | -0.0037748 | 0.041199 | 59.9442 | -61.9217 | 60.3287 | -61.5692 | -62.0636 | -62.0316 | 0.18768 | 59.9579 | -61.9766 | 60.2463 | -61.7294 | -61.9308 | -61.8439 | -0.045776 | -0.20142 | 0.1831 | 0.3067 | -0.15564 | -0.18768 | -0.10986 | -0.14191 | -0.10071 | -0.18768 | 0.10071 | 0.14648 | 0.032044 | -0.054931 | 0.13275 | 0.045777 | 0.35248 | 122.2504 | 0.24719 | 122.2229 | 121.8658 | 121.9345 | 121.8201 | 121.8338 | -122.0673 | -122.1222 | 122.2046 | 122.1222 | 61.9171 | 62.0636
947.1719 | 122.2733 | -61.9171 | 60.2005 | 0.0016023 | 0.0005619 | 0.059035 | 0.060103 | -0.00085021 | -0.0057699 | -0.0046847 | -0.0051575 | 0.0017304 | 0.071724 | 0.071677 | -0.010305 | 0.018372 | 0.0007114 | 0.004578 | 60.0357 | -61.9217 | 60.2463 | -61.6882 | -62.1414 | -62.1323 | 0.054932 | 60.054 | -61.9492 | 60.1959 | -61.821 | -62.0178 | -61.94 | -0.004578 | -0.16479 | 0.045777 | 0.22888 | -0.21515 | -0.2243 | -0.21057 | -0.21973 | -0.032044 | -0.14648 | -0.004577 | 0.09613 | -0.022888 | -0.10071 | 0.009156 | -0.068664 | 0.23346 | 122.168 | 0.12817 | 122.1451 | 121.9574 | 122.0032 | 121.9528 | 121.9711 | -122.1222 | -122.1497 | 122.1634 | 122.113 | 61.9217 | 61.972
948.9062 | 122.3373 | -61.8576 | 60.173 | -0.0060272 | -0.0011471 | 0.058394 | 0.054762 | -0.002132 | -0.0059835 | 0.00065573 | -0.0021057 | 0.003012 | 0.070229 | 0.061423 | -0.010092 | 0.01709 | 0.0007114 | 0.050354 | 59.9945 | -61.8896 | 60.3378 | -61.5646 | -62.0453 | -62.0087 | 0.13733 | 60.0266 | -61.9171 | 60.2783 | -61.734 | -61.8988 | -61.8759 | -0.032043 | -0.17853 | 0.16479 | 0.29297 | -0.15106 | -0.18768 | -0.11902 | -0.15564 | -0.059509 | -0.14648 | 0.10529 | 0.1236 | -0.018311 | -0.041199 | 0.041198 | 0.01831 | 0.32501 | 122.2275 | 0.1831 | 122.1954 | 121.8842 | 121.9437 | 121.8521 | 121.8842 | -122.0627 | -122.0901 | 122.1954 | 122.1359 | 61.908 | 61.9949
950.6562 | 122.2778 | -61.8759 | 60.2463 | -0.0060272 | 0.0022709 | 0.058607 | 0.05818 | 0.001286 | -0.0061971 | -0.0027621 | -0.0021057 | 0.001303 | 0.073006 | 0.061637 | -0.010732 | 0.017303 | -0.0020658 | -0.004578 | 60.0632 | -61.8851 | 60.26 | -61.6699 | -62.1231 | -62.1048 | 0.036621 | 60.0952 | -61.9217 | 60.228 | -61.7889 | -61.9858 | -61.9446 | -0.009155 | -0.18311 | 0.013733 | 0.20599 | -0.22888 | -0.24719 | -0.21973 | -0.23804 | -0.045776 | -0.15106 | -0.018311 | 0.086976 | -0.068664 | -0.10986 | -0.022888 | -0.064087 | 0.21515 | 122.1451 | 0.13275 | 122.1497 | 121.9482 | 122.0169 | 121.9391 | 121.9711 | -122.1313 | -122.168 | 122.1359 | 122.1039 | 61.8713 | 61.9125
952.3438 | 122.2275 | -61.8713 | 60.2737 | -0.013657 | 0.0001345 | 0.057967 | 0.057326 | -0.0027728 | -0.0059835 | -0.0031895 | -0.0082093 | 0.0023712 | 0.074074 | 0.062491 | -0.0077417 | 0.017731 | -0.003561 | -0.018311 | 60.0952 | -61.8668 | 60.2554 | -61.6562 | -62.1048 | -62.1002 | 0.027466 | 60.1044 | -61.8622 | 60.2188 | -61.8027 | -61.9904 | -61.9446 | 0.004578 | -0.17853 | -0.018311 | 0.21515 | -0.22888 | -0.23346 | -0.23346 | -0.23804 | 0.009155 | -0.16937 | -0.054932 | 0.068665 | -0.073242 | -0.11902 | -0.082397 | -0.12817 | 0.21057 | 122.1222 | 0.05951 | 122.081 | 121.962 | 121.9666 | 121.9666 | 121.9757 | -122.1405 | -122.1359 | 122.1268 | 122.0901 | 61.853 | 61.8988
954.0938 | 122.3465 | -61.821 | 60.2234 | -0.0060272 | -0.0011471 | 0.059462 | 0.055189 | -0.00085021 | -0.0087607 | -0.0044711 | -0.0021057 | -0.00061956 | 0.072578 | 0.062064 | -0.010732 | 0.018799 | -0.0046292 | 0.036621 | 60.054 | -61.8164 | 60.4248 | -61.4777 | -61.94 | -61.9446 | 0.13733 | 60.0769 | -61.8393 | 60.3378 | -61.6379 | -61.821 | -61.8118 | 0.004578 | -0.16937 | 0.20142 | 0.34332 | -0.1236 | -0.11902 | -0.12817 | -0.1236 | -0.01831 | -0.14648 | 0.11444 | 0.18311 | 0.009155 | 0 | 0.027465 | 0.01831 | 0.33875 | 122.2412 | 0.20142 | 122.1771 | 121.8704 | 121.9162 | 121.875 | 121.8979 | -122.0398 | -122.0627 | 122.2458 | 122.1588 | 61.8576 | 61.9583
955.8438 | 122.2641 | -61.821 | 60.2829 | -0.021286 | 0.0050479 | 0.059035 | 0.060103 | -0.0032 | -0.0074789 | -0.0031895 | -0.0021057 | 0.0040802 | 0.069588 | 0.070823 | -0.0085961 | 0.018799 | -0.0016384 | -0.12817 | 60.1273 | -61.8484 | 60.2737 | -61.6791 | -62.1368 | -62.0956 | -0.07782 | 60.141 | -61.8759 | 60.2646 | -61.7844 | -61.9858 | -61.9171 | -0.027466 | -0.15564 | -0.009155 | 0.14191 | -0.27466 | -0.31586 | -0.24719 | -0.28839 | -0.054932 | -0.14191 | -0.018311 | 0.036621 | -0.09613 | -0.16479 | -0.041198 | -0.10986 | 0.16937 | 122.1222 | 0.091553 | 122.1405 | 121.9757 | 122.0169 | 121.9482 | 121.962 | -122.1313 | -122.1588 | 122.0947 | 122.0856 | 61.6928 | 61.7432
957.5938 | 122.2733 | -61.8027 | 60.2966 | -0.0060272 | 0.0024845 | 0.060103 | 0.06053 | -0.004909 | -0.0040609 | -0.0036167 | -0.0051575 | 0.0032256 | 0.07151 | 0.062918 | -0.0081689 | 0.01944 | -0.0014248 | -0.12817 | 60.1547 | -61.8073 | 60.3195 | -61.6333 | -62.0956 | -62.0819 | -0.068665 | 60.1273 | -61.8347 | 60.3058 | -61.7569 | -61.94 | -61.8713 | -0.004578 | -0.14191 | 0.022888 | 0.16937 | -0.27924 | -0.29297 | -0.27466 | -0.28839 | -0.032044 | -0.16937 | 0.009155 | 0.045776 | -0.068665 | -0.13733 | -0.036621 | -0.10529 | 0.17395 | 122.1268 | 0.07782 | 122.1405 | 121.962 | 121.962 | 121.9574 | 121.9299 | -122.1039 | -122.1313 | 122.1222 | 122.1085 | 61.6745 | 61.734
959.2656 | 122.4014 | -61.7294 | 60.3653 | -0.0060272 | -0.0005063 | 0.057539 | 0.055617 | -0.0019184 | -0.0083335 | -0.0040439 | -0.0051575 | -0.00040596 | 0.071083 | 0.06185 | -0.0085961 | 0.017303 | -0.0061246 | 0.027466 | 60.1181 | -61.7249 | 60.4935 | -61.4136 | -61.8988 | -61.8668 | 0.1831 | 60.1639 | -61.7432 | 60.4477 | -61.5372 | -61.734 | -61.7065 | 0.004577 | -0.24719 | 0.12817 | 0.31586 | -0.13733 | -0.16937 | -0.14191 | -0.17395 | -0.013733 | -0.20142 | 0.082398 | 0.19226 | 0.022888 | -0.004578 | 0.036621 | 0.009155 | 0.31128 | 122.2183 | 0.20599 | 122.1909 | 121.843 | 121.907 | 121.8475 | 121.8933 | -122.0901 | -122.1085 | 122.2229 | 122.1771 | 61.7569 | 61.9125
961 | 122.3282 | -61.7111 | 60.3241 | -0.021286 | 0.0039799 | 0.059035 | 0.057967 | 0.0025678 | -0.0047019 | -0.0025485 | -0.0051575 | 0.0010894 | 0.071297 | 0.058005 | -0.0096643 | 0.016235 | -0.000784 | -0.07782 | 60.1639 | -61.7157 | 60.466 | -61.4594 | -61.9583 | -61.9125 | 0.054932 | 60.1318 | -61.7661 | 60.3973 | -61.6425 | -61.8027 | -61.7615 | -0.004577 | -0.16022 | 0.14191 | 0.25177 | -0.20142 | -0.24719 | -0.19684 | -0.24261 | -0.054931 | -0.19226 | 0.073242 | 0.068665 | -0.050354 | -0.091552 | 0.004577 | -0.036621 | 0.25635 | 122.1817 | 0.1236 | 122.1634 | 121.8796 | 121.8979 | 121.875 | 121.843 | -122.0398 | -122.0901 | 122.1771 | 122.1085 | 61.6333 | 61.7661
962.7344 | 122.2733 | -61.702 | 60.4294 | -0.0060272 | 0.0001345 | 0.058394 | 0.058821 | -0.00020941 | -0.0085471 | -0.0027621 | -0.0082093 | 0.0045074 | 0.073006 | 0.064414 | -0.010305 | 0.021362 | 0.0002842 | 0 | 60.2692 | -61.7157 | 60.4385 | -61.496 | -61.9629 | -61.9263 | 0.022888 | 60.2966 | -61.7157 | 60.3973 | -61.615 | -61.8118 | -61.7889 | -0.013733 | -0.16022 | 0.009156 | 0.20599 | -0.22431 | -0.26093 | -0.21057 | -0.24719 | -0.013733 | -0.13275 | -0.032043 | 0.086975 | -0.086975 | -0.10986 | -0.073242 | -0.096131 | 0.21973 | 122.1542 | 0.10071 | 122.113 | 121.9849 | 122.0123 | 121.9711 | 121.9986 | -122.1451 | -122.1451 | 122.1405 | 122.0993 | 61.702 | 61.7249
964.4219 | 122.3328 | -61.6882 | 60.3882 | 0.0016023 | -0.0011471 | 0.059035 | 0.05583 | -0.003841 | -0.0070517 | -0.0025485 | -0.0051575 | 0.00023504 | 0.070869 | 0.060355 | -0.0083825 | 0.01944 | -0.0020658 | -0.064087 | 60.2005 | -61.6745 | 60.4523 | -61.4456 | -61.9171 | -61.8942 | 0.004578 | 60.2005 | -61.7157 | 60.4477 | -61.5875 | -61.7477 | -61.7294 | 0.013732 | -0.18768 | 0.064087 | 0.24261 | -0.20599 | -0.22888 | -0.21973 | -0.24261 | -0.027466 | -0.18768 | 0.059509 | 0.10071 | -0.041199 | -0.05951 | -0.013733 | -0.032044 | 0.22888 | 122.1268 | 0.12817 | 122.1634 | 121.875 | 121.9162 | 121.8887 | 121.8887 | -122.0627 | -122.1039 | 122.1405 | 122.1359 | 61.6241 | 61.6928
966.1719 | 122.2412 | -61.6425 | 60.5026 | -0.0060272 | -0.0028561 | 0.057753 | 0.057967 | -0.006618 | -0.0083335 | -0.0019077 | -0.0021057 | 0.003653 | 0.074928 | 0.070609 | -0.012655 | 0.017944 | -0.0031338 | -0.004578 | 60.3104 | -61.6562 | 60.4706 | -61.4502 | -61.908 | -61.8942 | 0.013733 | 60.347 | -61.6837 | 60.4156 | -61.5967 | -61.7889 | -61.7615 | -0.013733 | -0.19226 | -0.032044 | 0.19226 | -0.25177 | -0.2655 | -0.23804 | -0.25177 | -0.041199 | -0.15564 | -0.086976 | 0.045776 | -0.11902 | -0.14648 | -0.07782 | -0.10528 | 0.20599 | 122.1268 | 0.086975 | 122.0993 | 121.9666 | 122.0306 | 121.9528 | 121.9894 | -122.1588 | -122.1863 | 122.113 | 122.0581 | 61.6379 | 61.6562
967.9219 | 122.3099 | -61.6425 | 60.4523 | -0.021286 | 0.0003483 | 0.060103 | 0.058607 | -0.0064044 | -0.0059835 | -0.0012669 | -0.0051575 | -0.001474 | 0.07151 | 0.052665 | -0.0092371 | 0.018158 | -0.0001432 | -0.064087 | 60.2417 | -61.6196 | 60.5255 | -61.3998 | -61.8759 | -61.8164 | -0.004578 | 60.2921 | -61.6562 | 60.466 | -61.5372 | -61.6974 | -61.6928 | 0.022888 | -0.21057 | 0.073242 | 0.24262 | -0.17395 | -0.23346 | -0.19684 | -0.25635 | -0.013733 | -0.16022 | 0.013732 | 0.10529 | -0.050354 | -0.054932 | -0.036621 | -0.041199 | 0.21973 | 122.1451 | 0.11902 | 122.1222 | 121.8613 | 121.9482 | 121.8842 | 121.9345 | -122.0718 | -122.1085 | 122.168 | 122.1085 | 61.5784 | 61.6379
969.6719 | 122.2412 | -61.5646 | 60.5759 | -0.013657 | -0.0005063 | 0.056685 | 0.057112 | 4.192e-06 | -0.0057699 | -0.0021213 | -0.0051575 | 0.0032256 | 0.073219 | 0.072318 | -0.010732 | 0.019226 | -0.003561 | 0.004578 | 60.3973 | -61.5829 | 60.5255 | -61.409 | -61.853 | -61.8301 | 0.009155 | 60.3836 | -61.6104 | 60.498 | -61.5097 | -61.7065 | -61.6928 | -0.018311 | -0.17853 | -0.050354 | 0.15564 | -0.2655 | -0.28839 | -0.24719 | -0.27008 | -0.045777 | -0.19226 | -0.07782 | 0.054931 | -0.12817 | -0.14191 | -0.082397 | -0.09613 | 0.17395 | 122.1085 | 0.10071 | 122.1085 | 121.9803 | 121.994 | 121.962 | 121.9482 | -122.1588 | -122.1863 | 122.0901 | 122.0627 | 61.5692 | 61.5738
971.3438 | 122.3145 | -61.5646 | 60.4889 | -0.0060272 | 0.0020571 | 0.06053 | 0.056898 | 0.001286 | -0.0040609 | -0.0023349 | -0.0082093 | 0.0010894 | 0.069801 | 0.060569 | -0.010092 | 0.018372 | -0.0018522 | -0.091553 | 60.2966 | -61.5463 | 60.6125 | -61.3083 | -61.821 | -61.7569 | 0.036621 | 60.3241 | -61.6241 | 60.553 | -61.4594 | -61.6241 | -61.6379 | 0.01831 | -0.19226 | 0.1236 | 0.25635 | -0.19226 | -0.25635 | -0.21057 | -0.27466 | -0.05951 | -0.16479 | 0.064087 | 0.10529 | -0.073242 | -0.05951 | -0.013732 | 0 | 0.23804 | 122.1588 | 0.1648 | 122.1771 | 121.843 | 121.9482 | 121.8613 | 121.8887 | -122.0352 | -122.113 | 122.1771 | 122.1176 | 61.4731 | 61.6013
973.0938 | 122.3282 | -61.5189 | 60.5347 | 0.0016023 | 0.0024845 | 0.06053 | 0.057112 | 0.0019268 | -0.0055563 | -0.0027621 | -0.0051575 | 0.0015166 | 0.071938 | 0.057151 | -0.010092 | 0.016663 | -0.0018522 | -0.07782 | 60.3653 | -61.528 | 60.672 | -61.235 | -61.7615 | -61.6928 | 0.050354 | 60.3607 | -61.5646 | 60.6262 | -61.4273 | -61.5921 | -61.5829 | -0.009155 | -0.16937 | 0.13733 | 0.28381 | -0.17395 | -0.24262 | -0.16479 | -0.23346 | -0.045776 | -0.17395 | 0.091553 | 0.091553 | -0.064087 | -0.073242 | -0.018311 | -0.027466 | 0.29297 | 122.2 | 0.13733 | 122.1909 | 121.8933 | 121.9254 | 121.8842 | 121.8796 | -122.0627 | -122.0993 | 122.1909 | 122.1451 | 61.441 | 61.5692
974.8438 | 122.3465 | -61.4182 | 60.6262 | -0.021286 | -0.0013607 | 0.056044 | 0.057967 | -0.0029864 | -0.0081197 | -0.0023349 | -0.0021057 | 0.00087584 | 0.069801 | 0.05886 | -0.010305 | 0.017303 | -0.0050564 | 0.036621 | 60.4202 | -61.4639 | 60.7819 | -61.1343 | -61.6013 | -61.5784 | 0.15106 | 60.434 | -61.4594 | 60.7086 | -61.2854 | -61.4822 | -61.4639 | -0.045776 | -0.20599 | 0.15564 | 0.28381 | -0.16022 | -0.1831 | -0.11444 | -0.13733 | -0.041199 | -0.19226 | 0.082397 | 0.13275 | -0.045776 | -0.064087 | -0.004577 | -0.022888 | 0.32959 | 122.2458 | 0.17395 | 122.168 | 121.8842 | 121.8933 | 121.8384 | 121.8521 | -122.0901 | -122.0856 | 122.2 | 122.1268 | 61.4548 | 61.5692
976.5938 | 122.3236 | -61.3861 | 60.64 | -0.013657 | 0.0007755 | 0.058821 | 0.056258 | 0.0010724 | -0.0059835 | -0.00083947 | -0.0021057 | -0.00040596 | 0.070656 | 0.063773 | -0.010732 | 0.018158 | -0.0005704 | -0.10529 | 60.466 | -61.3998 | 60.791 | -61.1526 | -61.6333 | -61.5875 | 0.013733 | 60.5255 | -61.4319 | 60.7315 | -61.3083 | -61.4731 | -61.4685 | -0.013733 | -0.17395 | 0.15106 | 0.23346 | -0.20142 | -0.24719 | -0.18768 | -0.23346 | -0.045777 | -0.11444 | 0.091552 | 0.077819 | -0.082398 | -0.086975 | -0.036621 | -0.041198 | 0.24719 | 122.1909 | 0.1236 | 122.1634 | 121.8658 | 121.9574 | 121.8521 | 121.9116 | -122.0398 | -122.0718 | 122.1771 | 122.1176 | 61.2808 | 61.3998
978.2812 | 122.3557 | -61.3174 | 60.6995 | -0.0060272 | 0.0037661 | 0.061171 | 0.058607 | 0.001286 | -0.0049155 | -0.0038303 | -0.0051575 | 0.0025848 | 0.070015 | 0.0689 | -0.012441 | 0.018158 | -0.0027066 | -0.068665 | 60.5392 | -61.3129 | 60.8688 | -61.0657 | -61.5555 | -61.5051 | 0.054932 | 60.5347 | -61.3907 | 60.8322 | -61.1984 | -61.3861 | -61.3586 | 0.004578 | -0.16022 | 0.16937 | 0.25177 | -0.18768 | -0.23804 | -0.19226 | -0.24262 | -0.073242 | -0.16479 | 0.13275 | 0.11902 | -0.041199 | -0.068664 | 0.032043 | 0.004578 | 0.24719 | 122.1817 | 0.19226 | 122.2229 | 121.8521 | 121.9254 | 121.8567 | 121.8521 | -122.0123 | -122.0901 | 122.1863 | 122.1497 | 61.2488 | 61.3724
980.0312 | 122.2687 | -61.2946 | 60.7819 | -0.013657 | 0.0039799 | 0.058821 | 0.059035 | -0.00020941 | -0.0083335 | 1.4934e-05 | -0.0021057 | 0.0027984 | 0.072365 | 0.070823 | -0.010732 | 0.020081 | -0.0044156 | -0.004578 | 60.6171 | -61.3129 | 60.8368 | -61.0886 | -61.5784 | -61.5509 | 0.041199 | 60.6262 | -61.3449 | 60.8047 | -61.2671 | -61.4639 | -61.4365 | -0.01831 | -0.1648 | 0.054932 | 0.20599 | -0.25635 | -0.28381 | -0.23804 | -0.2655 | -0.050354 | -0.15564 | 0.022889 | 0.027466 | -0.14191 | -0.16937 | -0.091552 | -0.11902 | 0.2243 | 122.1497 | 0.07782 | 122.1497 | 121.9299 | 121.9711 | 121.9116 | 121.9208 | -122.0947 | -122.1268 | 122.1313 | 122.0993 | 61.29 | 61.3358
981.7812 | 122.3373 | -61.3129 | 60.7727 | -0.013657 | 0.0003483 | 0.060103 | 0.057112 | 0.00064519 | -0.0057699 | -0.0010531 | -0.0051575 | 0.0010894 | 0.073006 | 0.062918 | -0.0088097 | 0.017731 | -0.0029202 | -0.050354 | 60.5896 | -61.2991 | 60.8505 | -61.0565 | -61.5189 | -61.5005 | 0.054932 | 60.5896 | -61.3403 | 60.8551 | -61.1847 | -61.3312 | -61.3358 | 0.013733 | -0.18311 | 0.07782 | 0.25635 | -0.18768 | -0.20599 | -0.20142 | -0.21973 | -0.027466 | -0.18311 | 0.082398 | 0.12817 | -0.022888 | -0.018311 | 0.004578 | 0.009155 | 0.24261 | 122.1497 | 0.15564 | 122.1954 | 121.8887 | 121.9299 | 121.9025 | 121.9025 | -122.0718 | -122.113 | 122.1634 | 122.168 | 61.2625 | 61.3678
983.5312 | 122.3145 | -61.2442 | 60.8047 | -0.0060272 | 0.0003483 | 0.059462 | 0.058821 | 4.192e-06 | -0.0053427 | -0.0010531 | -0.0051575 | 0.001303 | 0.071297 | 0.059501 | -0.012228 | 0.016876 | -0.0037748 | -0.086975 | 60.6583 | -61.2488 | 60.8917 | -61.0428 | -61.5143 | -61.4548 | 0.004578 | 60.64 | -61.2991 | 60.8597 | -61.1801 | -61.3541 | -61.3358 | -0.004577 | -0.14648 | 0.086975 | 0.20142 | -0.21057 | -0.27008 | -0.20599 | -0.2655 | -0.054931 | -0.16479 | 0.054931 | 0.064087 | -0.091552 | -0.10986 | -0.036621 | -0.054932 | 0.20599 | 122.1405 | 0.11902 | 122.1588 | 121.907 | 121.9391 | 121.9025 | 121.8842 | -122.0535 | -122.1039 | 122.1359 | 122.1039 | 61.1572 | 61.2488
985.2031 | 122.2733 | -61.171 | 60.9787 | -0.0060272 | 0.0012027 | 0.058821 | 0.060103 | -0.0010638 | -0.0070517 | -0.0016941 | -0.0082093 | 0.00066224 | 0.074287 | 0.068473 | -0.0094507 | 0.019226 | -0.0063382 | 0.027466 | 60.7864 | -61.1938 | 60.9879 | -60.9787 | -61.409 | -61.409 | 0.050354 | 60.8047 | -61.1938 | 60.9421 | -61.1206 | -61.3037 | -61.2396 | -0.022889 | -0.19226 | 0.009155 | 0.19226 | -0.23804 | -0.23804 | -0.21515 | -0.21515 | -0.022889 | -0.17395 | -0.036621 | 0.050354 | -0.068665 | -0.13275 | -0.045776 | -0.10986 | 0.21515 | 122.1817 | 0.073243 | 122.1359 | 121.9803 | 121.9986 | 121.9574 | 121.9757 | -122.1725 | -122.1725 | 122.1588 | 122.113 | 61.1984 | 61.2213
986.9531 | 122.2275 | -61.0931 | 60.9924 | -0.013657 | 0.0020571 | 0.057326 | 0.056685 | -0.0034136 | -0.0083335 | -0.0010531 | -0.0051575 | 0.0045074 | 0.071724 | 0.065696 | -0.0083825 | 0.017731 | -0.0020658 | 0.009155 | 60.8002 | -61.1481 | 60.9787 | -60.9421 | -61.3907 | -61.3724 | 0.041199 | 60.8231 | -61.1618 | 60.9283 | -61.0977 | -61.2671 | -61.2762 | -0.054931 | -0.19226 | -0.013733 | 0.15106 | -0.27923 | -0.29755 | -0.2243 | -0.24262 | -0.068664 | -0.16937 | -0.064087 | -0.004577 | -0.18311 | -0.17395 | -0.11444 | -0.10529 | 0.20599 | 122.1268 | 0.064087 | 122.0901 | 121.9482 | 121.9849 | 121.8933 | 121.9162 | -122.1405 | -122.1542 | 122.0718 | 122.0215 | 61.1023 | 61.1343
988.7031 | 122.2824 | -61.1069 | 60.965 | -0.013657 | 0.0018435 | 0.06053 | 0.059462 | 0.0017132 | -0.0059835 | -0.0055393 | -0.0021057 | 0.0027984 | 0.071938 | 0.064841 | -0.0088097 | 0.017517 | -0.0037748 | -0.11902 | 60.8231 | -61.1206 | 60.9833 | -60.9512 | -61.4319 | -61.4044 | -0.059509 | 60.8139 | -61.203 | 60.9924 | -61.084 | -61.2808 | -61.2167 | -0.013732 | -0.14191 | 0.01831 | 0.15564 | -0.29755 | -0.32501 | -0.28381 | -0.31128 | -0.09613 | -0.15106 | 0.027466 | 0.022889 | -0.10986 | -0.17395 | -0.013733 | -0.07782 | 0.16937 | 122.1039 | 0.11902 | 122.1954 | 121.9437 | 122.0169 | 121.9299 | 121.9208 | -122.0856 | -122.168 | 122.0901 | 122.0993 | 60.9879 | 61.0474
990.4688 | 122.287 | -61.0291 | 61.0794 | -0.0060272 | 0.0018435 | 0.059676 | 0.05818 | -0.001491 | -0.0051291 | -0.0027621 | -0.0021057 | 0.0025848 | 0.073433 | 0.063346 | -0.010519 | 0.019226 | 0.000925 | 0.004578 | 60.9055 | -61.0336 | 61.1435 | -60.7956 | -61.2762 | -61.2396 | 0.07782 | 60.9192 | -61.0657 | 61.0794 | -60.9558 | -61.1481 | -61.1023 | -0.004577 | -0.17395 | 0.064087 | 0.23346 | -0.21057 | -0.24719 | -0.20599 | -0.24262 | -0.036621 | -0.16022 | 0 | 0.073242 | -0.073242 | -0.11902 | -0.036621 | -0.082397 | 0.23804 | 122.1771 | 0.10986 | 122.1451 | 121.9391 | 121.9849 | 121.9345 | 121.9482 | -122.113 | -122.1451 | 122.1725 | 122.1085 | 61.0336 | 61.1069
992.1562 | 122.2366 | -61.0016 | 61.1435 | -0.013657 | -0.0005063 | 0.058607 | 0.057539 | 0.0032086 | -0.0053427 | -0.0019077 | 0.0009461 | 0.003012 | 0.072792 | 0.062705 | -0.0073145 | 0.018158 | -0.0022794 | -0.009155 | 60.9604 | -60.9924 | 61.1252 | -60.8093 | -61.2717 | -61.2396 | 0.013733 | 60.9695 | -61.0199 | 61.084 | -60.9512 | -61.1252 | -61.1069 | 0.009155 | -0.18311 | -0.018311 | 0.19226 | -0.23804 | -0.27008 | -0.24719 | -0.27923 | -0.01831 | -0.17395 | -0.05951 | 0.050354 | -0.10529 | -0.1236 | -0.086976 | -0.10529 | 0.18311 | 122.1176 | 0.068664 | 122.1039 | 121.9528 | 121.9894 | 121.962 | 121.9711 | -122.1359 | -122.1634 | 122.1268 | 122.0856 | 60.9924 | 61.0153
993.9062 | 122.3236 | -60.9558 | 61.1023 | -0.0060272 | -0.0005063 | 0.058394 | 0.055617 | -0.0027728 | -0.0057699 | -0.0016941 | -0.0082093 | 0.0017304 | 0.071938 | 0.065482 | -0.0083825 | 0.016663 | -0.0018522 | -0.082397 | 60.8917 | -60.9467 | 61.2305 | -60.6812 | -61.1984 | -61.1435 | 0.050354 | 60.9192 | -60.9924 | 61.171 | -60.8643 | -61.0245 | -61.0062 | 0.009156 | -0.21057 | 0.12817 | 0.27466 | -0.18768 | -0.24261 | -0.19684 | -0.25177 | -0.036621 | -0.18311 | 0.068664 | 0.091553 | -0.050354 | -0.068664 | -0.013733 | -0.032043 | 0.2655 | 122.1771 | 0.12817 | 122.1634 | 121.8384 | 121.9116 | 121.8475 | 121.875 | -122.0489 | -122.0947 | 122.1863 | 122.1268 | 60.8734 | 61.0062
995.5938 | 122.2321 | -60.9238 | 61.1847 | -0.0060272 | 0.0026981 | 0.058607 | 0.059035 | 0.00064519 | -0.0044883 | -0.0016941 | 0.0009461 | 0.00023504 | 0.072792 | 0.064414 | -0.010732 | 0.019012 | 0.0034884 | -0.10986 | 61.0474 | -60.9421 | 61.1481 | -60.8002 | -61.2762 | -61.2259 | -0.07782 | 61.0611 | -60.9741 | 61.1343 | -60.9329 | -61.116 | -61.0519 | -0.018311 | -0.13733 | -0.036621 | 0.1236 | -0.30212 | -0.35248 | -0.28381 | -0.33417 | -0.050354 | -0.1236 | -0.050354 | -0.009155 | -0.12817 | -0.19226 | -0.07782 | -0.14191 | 0.14191 | 122.0901 | 0.041199 | 122.1085 | 121.9894 | 122.0352 | 121.9711 | 121.9849 | -122.1268 | -122.1588 | 122.0718 | 122.0581 | 60.8139 | 60.8459
997.2656 | 122.2916 | -60.8276 | 61.2854 | -0.0060272 | 0.0001345 | 0.058607 | 0.05818 | -0.0017048 | -0.0081197 | -0.0040439 | -0.0021057 | 0.0025848 | 0.072151 | 0.063346 | -0.0077417 | 0.01944 | -0.0012112 | 0.022888 | 61.1252 | -60.8414 | 61.3037 | -60.6171 | -61.084 | -61.0519 | 0.064087 | 61.1069 | -60.8871 | 61.2854 | -60.7544 | -60.9512 | -60.9283 | -0.013733 | -0.16022 | 0.018311 | 0.21057 | -0.2243 | -0.25635 | -0.21057 | -0.24261 | -0.059509 | -0.17853 | 0 | 0.073242 | -0.10071 | -0.1236 | -0.041199 | -0.064087 | 0.22431 | 122.1451 | 0.13275 | 122.1725 | 121.9666 | 121.994 | 121.9528 | 121.9345 | -122.1268 | -122.1725 | 122.1313 | 122.113 | 60.8505 | 60.8917
999.0312 | 122.2778 | -60.7773 | 61.3678 | -0.0060272 | 0.0001345 | 0.059889 | 0.060316 | 0.0010724 | -0.0076925 | -0.0021213 | -0.0021057 | 0.001944 | 0.069588 | 0.066977 | -0.010305 | 0.015595 | 0.0011386 | -0.004578 | 61.203 | -60.8002 | 61.3541 | -60.5759 | -61.0199 | -61.0153 | 0.022888 | 61.1984 | -60.791 | 61.3312 | -60.6949 | -60.8871 | -60.8459 | -0.022888 | -0.16479 | -0.013733 | 0.20142 | -0.23804 | -0.24261 | -0.21515 | -0.21973 | -0.013733 | -0.16937 | -0.036621 | 0.082398 | -0.068664 | -0.10986 | -0.054931 | -0.09613 | 0.2243 | 122.1542 | 0.096131 | 122.1222 | 122.0032 | 121.9894 | 121.9803 | 121.9757 | -122.168 | -122.1588 | 122.1313 | 122.1085 | 60.7727 | 60.8002
1000.7188 | 122.3145 | -60.7178 | 61.377 | -0.013657 | 0.0001345 | 0.058821 | 0.056898 | -0.0017048 | -0.0055563 | -0.0031895 | -0.0021057 | 2.1442e-05 | 0.072578 | 0.062278 | -0.0090235 | 0.018585 | -0.0044156 | -0.086975 | 61.1938 | -60.7315 | 61.441 | -60.4889 | -60.9467 | -60.91 | -0.009155 | 61.1755 | -60.7636 | 61.3998 | -60.6308 | -60.8002 | -60.7864 | -0.013733 | -0.1831 | 0.064087 | 0.22888 | -0.19226 | -0.22888 | -0.17853 | -0.21515 | -0.045777 | -0.20142 | 0.022888 | 0.086975 | -0.068665 | -0.082398 | -0.022888 | -0.036621 | 0.24261 | 122.1725 | 0.13275 | 122.1634 | 121.9254 | 121.9391 | 121.9116 | 121.8933 | -122.1085 | -122.1405 | 122.1588 | 122.1176 | 60.6308 | 60.7086
1002.4062 | 122.3419 | -60.6262 | 61.409 | 0.0016023 | 0.0016299 | 0.059035 | 0.05818 | 0.0027814 | -0.0044883 | -0.0012669 | -0.0021057 | 0.0017304 | 0.071938 | 0.066977 | -0.010732 | 0.018799 | -0.0031338 | -0.11902 | 61.2671 | -60.6354 | 61.5189 | -60.4111 | -60.8826 | -60.8414 | 0.022888 | 61.2305 | -60.6812 | 61.528 | -60.5438 | -60.7178 | -60.6857 | -0.009155 | -0.14191 | 0.10986 | 0.21515 | -0.21515 | -0.25635 | -0.20599 | -0.24719 | -0.054931 | -0.17853 | 0.11902 | 0.082398 | -0.059509 | -0.091552 | -0.004578 | -0.036621 | 0.2243 | 122.1542 | 0.13733 | 122.2092 | 121.9025 | 121.9116 | 121.8933 | 121.8567 | -122.0444 | -122.0901 | 122.1451 | 122.1542 | 60.5072 | 60.6491
1004.1562 | 122.2137 | -60.5301 | 61.5967 | -0.013657 | -0.0002927 | 0.055617 | 0.05583 | -0.00085021 | -0.0059835 | -0.0019077 | -0.0051575 | 0.0023712 | 0.071938 | 0.063346 | -0.0090235 | 0.018372 | -0.0031338 | -0.009155 | 61.4182 | -60.5576 | 61.5646 | -60.3424 | -60.791 | -60.7773 | 0.027466 | 61.4548 | -60.5667 | 61.5234 | -60.498 | -60.6583 | -60.6766 | -0.027466 | -0.17853 | -0.032044 | 0.18768 | -0.24719 | -0.26093 | -0.21973 | -0.23346 | -0.036621 | -0.14191 | -0.073243 | 0.032043 | -0.14648 | -0.12817 | -0.10986 | -0.091553 | 0.21515 | 122.1222 | 0.068664 | 122.0901 | 121.9757 | 122.0215 | 121.9482 | 121.9849 | -122.1542 | -122.1634 | 122.0947 | 122.0535 | 60.5209 | 60.5576
1005.9062 | 122.3373 | -60.4385 | 61.5967 | 0.0092313 | 0.0009891 | 0.060103 | 0.057967 | -0.00085021 | -0.0055563 | -0.0023349 | 0.0039977 | 0.00023504 | 0.071297 | 0.065696 | -0.010732 | 0.019012 | 0.0004978 | -0.068665 | 61.4639 | -60.434 | 61.7615 | -60.1547 | -60.6445 | -60.6079 | 0.059509 | 61.4548 | -60.4568 | 61.702 | -60.3561 | -60.5209 | -60.498 | 0.004578 | -0.13275 | 0.16479 | 0.28381 | -0.16937 | -0.20599 | -0.17395 | -0.21057 | -0.01831 | -0.14191 | 0.10529 | 0.082398 | -0.059509 | -0.082397 | -0.041199 | -0.064087 | 0.27924 | 122.1954 | 0.10071 | 122.1588 | 121.8979 | 121.9116 | 121.9025 | 121.8933 | -122.0306 | -122.0535 | 122.2 | 122.1405 | 60.3699 | 60.498
1007.6562 | 122.2137 | -60.347 | 61.7569 | -0.013657 | 0.0050479 | 0.061385 | 0.060316 | 0.0036358 | -0.0029929 | -0.0053257 | -0.0051575 | 0.0040802 | 0.073006 | 0.063987 | -0.010732 | 0.018585 | 0.0013522 | -0.050354 | 61.5967 | -60.3561 | 61.7889 | -60.1593 | -60.6537 | -60.6033 | -0.036621 | 61.6013 | -60.3928 | 61.7111 | -60.3424 | -60.5255 | -60.4797 | -0.009155 | -0.16022 | 0.032043 | 0.18768 | -0.25635 | -0.3067 | -0.24719 | -0.29755 | -0.045776 | -0.15564 | -0.045776 | 0.004578 | -0.13275 | -0.17853 | -0.086975 | -0.13275 | 0.19684 | 122.1451 | 0.050354 | 122.1039 | 121.9528 | 121.994 | 121.9437 | 121.9482 | -122.113 | -122.1497 | 122.1359 | 122.0581 | 60.2966 | 60.3104
1009.3438 | 122.2458 | -60.26 | 61.8576 | -0.013657 | -0.0011471 | 0.059248 | 0.056258 | 0.0025678 | -0.0091879 | -0.0019077 | -0.0021057 | 0.0021576 | 0.07151 | 0.063346 | -0.0079553 | 0.018372 | -0.0033474 | 0.050354 | 61.6516 | -60.26 | 61.8759 | -60.0311 | -60.5072 | -60.4752 | 0.064087 | 61.6974 | -60.2737 | 61.8027 | -60.2097 | -60.3928 | -60.3882 | 0 | -0.20599 | 0.018311 | 0.22888 | -0.21515 | -0.24719 | -0.21515 | -0.24719 | -0.013733 | -0.16022 | -0.054932 | 0.050354 | -0.12817 | -0.13275 | -0.11444 | -0.11902 | 0.22888 | 122.1359 | 0.064087 | 122.0764 | 121.9116 | 121.9711 | 121.9116 | 121.9574 | -122.1176 | -122.1313 | 122.1359 | 122.0627 | 60.3104 | 60.3241
1011.0938 | 122.3785 | -60.1273 | 61.9263 | -0.0060272 | -0.0005063 | 0.057539 | 0.055617 | -0.0012774 | -0.0070517 | -0.0029759 | 0.0039977 | 0.00044864 | 0.069588 | 0.063987 | -0.012014 | 0.016449 | -0.004202 | 0.054932 | 61.7111 | -60.1868 | 62.0773 | -59.8251 | -60.3149 | -60.3058 | 0.17395 | 61.7386 | -60.1959 | 62.0041 | -59.9991 | -60.1822 | -60.1959 | -0.05951 | -0.21515 | 0.15106 | 0.30212 | -0.17853 | -0.18768 | -0.11902 | -0.12817 | -0.068665 | -0.18768 | 0.077819 | 0.12817 | -0.068665 | -0.054932 | 0 | 0.013733 | 0.36163 | 122.2641 | 0.19684 | 122.2 | 121.8979 | 121.9345 | 121.8384 | 121.8658 | -122.113 | -122.1222 | 122.2046 | 122.1313 | 60.1822 | 60.3012
1012.8438 | 122.374 | -60.054 | 61.9766 | -0.013657 | 0.0035525 | 0.060957 | 0.059676 | 0.0036358 | -0.0072653 | -0.0027621 | -0.0051575 | 0.0025848 | 0.072365 | 0.063132 | -0.0098779 | 0.019012 | -0.0027066 | -0.10071 | 61.8256 | -60.0861 | 62.114 | -59.816 | -60.2921 | -60.2463 | 0.045776 | 61.8301 | -60.1089 | 62.0865 | -59.9625 | -60.141 | -60.1044 | -0.032044 | -0.15106 | 0.13733 | 0.23804 | -0.19226 | -0.23804 | -0.16022 | -0.20599 | -0.054932 | -0.14648 | 0.10986 | 0.091553 | -0.050354 | -0.086975 | 0.004578 | -0.032043 | 0.27008 | 122.2 | 0.14648 | 122.1954 | 121.9116 | 121.9391 | 121.8796 | 121.8842 | -122.0627 | -122.0856 | 122.168 | 122.1405 | 59.9533 | 60.0998
1014.5781 | 122.3557 | -59.9716 | 62.0956 | -0.0060272 | -0.0002927 | 0.059248 | 0.056685 | -0.00555 | -0.0059835 | -0.0046847 | -0.0051575 | 0.001944 | 0.069588 | 0.065268 | -0.010305 | 0.016235 | -0.0048428 | 0.036621 | 61.8942 | -59.9625 | 62.2192 | -59.6832 | -60.1501 | -60.1227 | 0.16479 | 61.9125 | -60.0128 | 62.1689 | -59.8389 | -59.9991 | -60.0128 | 0.009156 | -0.20142 | 0.1236 | 0.28839 | -0.15106 | -0.17853 | -0.16022 | -0.18768 | -0.041198 | -0.1831 | 0.073242 | 0.13275 | -0.041198 | -0.027465 | 0 | 0.013733 | 0.27923 | 122.1817 | 0.17395 | 122.1817 | 121.8567 | 121.9254 | 121.8658 | 121.8842 | -122.0581 | -122.1085 | 122.1909 | 122.1405 | 60.0082 | 60.1364
1016.2656 | 122.3648 | -59.8434 | 62.1918 | -0.0060272 | 0.0018435 | 0.059676 | 0.056471 | 0.0023542 | -0.0047019 | -0.0040439 | -0.0021057 | -0.00061956 | 0.06916 | 0.060996 | -0.010092 | 0.017731 | -0.0050564 | -0.054932 | 62.0132 | -59.8526 | 62.3291 | -59.6146 | -60.1044 | -60.0586 | 0.050354 | 62.0041 | -59.9258 | 62.2925 | -59.7519 | -59.9258 | -59.9075 | -0.009155 | -0.17853 | 0.13733 | 0.22888 | -0.21515 | -0.26093 | -0.20599 | -0.25177 | -0.082397 | -0.18768 | 0.10071 | 0.091553 | -0.064087 | -0.082397 | 0.01831 | 0 | 0.23804 | 122.1817 | 0.17395 | 122.2183 | 121.8658 | 121.9299 | 121.8567 | 121.8475 | -122.0444 | -122.1176 | 122.1725 | 122.1359 | 59.7885 | 59.8938
1018.0312 | 122.3236 | -59.8022 | 62.2559 | -0.0060272 | 0.0024845 | 0.062239 | 0.059889 | 0.0023542 | -0.0036337 | -0.0044711 | -0.0021057 | 0.0017304 | 0.071938 | 0.064414 | -0.011373 | 0.020508 | -0.0016384 | -0.12817 | 62.1506 | -59.8343 | 62.3154 | -59.6375 | -60.1044 | -60.0632 | -0.032043 | 62.1231 | -59.848 | 62.3337 | -59.7427 | -59.9304 | -59.8801 | -0.032044 | -0.10529 | 0.05951 | 0.16479 | -0.26093 | -0.30212 | -0.22888 | -0.27008 | -0.045776 | -0.13275 | 0.07782 | 0.059509 | -0.07782 | -0.12817 | -0.032044 | -0.082398 | 0.19684 | 122.1497 | 0.10529 | 122.1817 | 121.9849 | 121.9711 | 121.9528 | 121.9254 | -122.0901 | -122.1039 | 122.1176 | 122.1359 | 59.6741 | 59.7702
1019.7812 | 122.2504 | -59.761 | 62.3749 | 0.0016023 | -0.0002927 | 0.059676 | 0.055189 | -0.0076862 | -0.0079061 | -0.0019077 | -0.0021057 | 0.001303 | 0.072151 | 0.05886 | -0.01116 | 0.017944 | -0.008688 | 0.045776 | 62.1506 | -59.7656 | 62.4115 | -59.5276 | -59.9854 | -59.9716 | 0.068665 | 62.2009 | -59.7839 | 62.3199 | -59.6924 | -59.8892 | -59.8846 | -0.004578 | -0.2243 | 0.036621 | 0.23346 | -0.21057 | -0.22431 | -0.20599 | -0.21973 | -0.022889 | -0.17395 | -0.054932 | 0.068664 | -0.1236 | -0.12817 | -0.10071 | -0.10529 | 0.23804 | 122.1771 | 0.091553 | 122.1039 | 121.9162 | 121.9849 | 121.9116 | 121.962 | -122.1405 | -122.1588 | 122.1725 | 122.081 | 59.8068 | 59.8297
1021.4688 | 122.3557 | -59.6237 | 62.4115 | 0.0016023 | 0.0035525 | 0.060744 | 0.057326 | 0.0019268 | -0.0066245 | -0.0016941 | -0.0051575 | 0.00044864 | 0.073219 | 0.065268 | -0.0094507 | 0.020294 | -0.0046292 | -0.082397 | 62.2375 | -59.6512 | 62.5717 | -59.3765 | -59.8434 | -59.816 | 0.073242 | 62.265 | -59.6786 | 62.5031 | -59.5459 | -59.7107 | -59.6741 | -0.027466 | -0.17395 | 0.16022 | 0.24719 | -0.19226 | -0.21973 | -0.16479 | -0.19226 | -0.054932 | -0.14648 | 0.091553 | 0.07782 | -0.050354 | -0.086975 | 0.004578 | -0.032043 | 0.27466 | 122.2229 | 0.13275 | 122.1817 | 121.8887 | 121.9437 | 121.8613 | 121.8887 | -122.0627 | -122.0901 | 122.1954 | 122.1268 | 59.5413 | 59.697
1023.2188 | 122.3694 | -59.5047 | 62.5031 | -0.0060272 | -0.0015743 | 0.05583 | 0.057753 | -0.0040546 | -0.0079061 | -0.0021213 | -0.0021057 | 0.001303 | 0.071724 | 0.063559 | -0.011801 | 0.017731 | 7.04e-05 | 0.004578 | 62.3337 | -59.5596 | 62.6724 | -59.2392 | -59.7107 | -59.6649 | 0.15564 | 62.3611 | -59.5459 | 62.6633 | -59.3628 | -59.5322 | -59.5596 | -0.054931 | -0.16937 | 0.16937 | 0.2655 | -0.16022 | -0.20599 | -0.10529 | -0.15106 | -0.041198 | -0.14191 | 0.16022 | 0.14191 | -0.054931 | -0.027466 | -0.013733 | 0.013732 | 0.32043 | 122.2321 | 0.1831 | 122.2092 | 121.8933 | 121.907 | 121.8384 | 121.8658 | -122.0627 | -122.0489 | 122.1771 | 122.168 | 59.5093 | 59.6603
1024.9688 | 122.2366 | -59.4086 | 62.7228 | -0.013657 | 0.0033389 | 0.061385 | 0.062025 | -0.0012774 | -0.0053427 | -0.0036167 | -0.0021057 | 0.0040802 | 0.071297 | 0.070395 | -0.010305 | 0.01709 | -0.0005704 | -0.059509 | 62.5397 | -59.3903 | 62.7411 | -59.2117 | -59.6832 | -59.6878 | -0.032043 | 62.5809 | -59.4223 | 62.6724 | -59.404 | -59.5871 | -59.5276 | 0.01831 | -0.1831 | 0.018311 | 0.19684 | -0.27924 | -0.27466 | -0.29755 | -0.29297 | -0.013733 | -0.14191 | -0.050354 | 0.004577 | -0.11902 | -0.17853 | -0.10529 | -0.16479 | 0.17853 | 122.1313 | 0.01831 | 122.0947 | 121.9299 | 122.0032 | 121.9482 | 121.9894 | -122.113 | -122.1451 | 122.1497 | 122.081 | 59.3491 | 59.3765
1026.7031 | 122.3465 | -59.3262 | 62.7228 | -0.013657 | 0.0029117 | 0.060103 | 0.059248 | 0.0014996 | -0.0059835 | -0.00083947 | -0.0021057 | -0.00019216 | 0.070442 | 0.065696 | -0.010519 | 0.018799 | 0.000925 | -0.068665 | 62.5534 | -59.3124 | 62.8922 | -59.0561 | -59.5413 | -59.4955 | 0.064087 | 62.5534 | -59.3628 | 62.8281 | -59.2209 | -59.3903 | -59.3857 | 0.013733 | -0.16937 | 0.16937 | 0.27008 | -0.16937 | -0.21515 | -0.18311 | -0.22888 | -0.036621 | -0.16937 | 0.10529 | 0.10529 | -0.059509 | -0.064087 | -0.022888 | -0.027466 | 0.25635 | 122.2046 | 0.14191 | 122.1909 | 121.8658 | 121.9162 | 121.8796 | 121.8796 | -122.0352 | -122.0856 | 122.2183 | 122.1542 | 59.2575 | 59.3903
1028.3906 | 122.3053 | -59.2941 | 62.796 | -0.021286 | 0.0026981 | 0.05818 | 0.05583 | -0.00063661 | -0.0070517 | -0.0014805 | -0.0082093 | 0.0017304 | 0.070656 | 0.056296 | -0.012014 | 0.019867 | -0.004202 | -0.09613 | 62.6221 | -59.2667 | 62.8601 | -59.079 | -59.5413 | -59.491 | -0.022888 | 62.6083 | -59.317 | 62.8235 | -59.2072 | -59.3765 | -59.3719 | 0.027465 | -0.17395 | 0.064086 | 0.21515 | -0.19684 | -0.24719 | -0.2243 | -0.27466 | -0.022889 | -0.18768 | 0.027465 | 0.086975 | -0.07782 | -0.082398 | -0.054931 | -0.059509 | 0.18768 | 122.1268 | 0.10986 | 122.1405 | 121.8887 | 121.9254 | 121.9162 | 121.9025 | -122.0627 | -122.113 | 122.1542 | 122.1176 | 59.198 | 59.2712
1030.125 | 122.2275 | -59.2072 | 62.9288 | -0.0060272 | -0.0020017 | 0.059889 | 0.057112 | -0.0040546 | -0.0070517 | -0.0048985 | -0.0021057 | 0.0023712 | 0.071724 | 0.057578 | -0.010305 | 0.01944 | -0.0050564 | 0.045776 | 62.7228 | -59.198 | 62.9562 | -58.9783 | -59.436 | -59.4131 | 0.054932 | 62.7502 | -59.2255 | 62.8738 | -59.1705 | -59.3353 | -59.3216 | 0.009155 | -0.20599 | 0.027466 | 0.22888 | -0.20599 | -0.22888 | -0.21515 | -0.23804 | -0.018311 | -0.17853 | -0.054932 | 0.036621 | -0.11444 | -0.12817 | -0.09613 | -0.10986 | 0.21973 | 122.1542 | 0.054932 | 122.0993 | 121.9208 | 121.9757 | 121.9299 | 121.9574 | -122.1268 | -122.1542 | 122.1634 | 122.081 | 59.2529 | 59.2621
1031.875 | 122.2321 | -59.0744 | 63.0295 | -0.013657 | 0.0014163 | 0.058607 | 0.056044 | -0.00042301 | -0.0068381 | 0.00044213 | -0.0051575 | 0.001944 | 0.073006 | 0.059714 | -0.0090235 | 0.019867 | -0.000784 | 0.050354 | 62.851 | -59.0836 | 63.0661 | -58.8776 | -59.3124 | -59.3079 | 0.050354 | 62.9059 | -59.1019 | 62.9883 | -59.0378 | -59.2072 | -59.2255 | -0.009155 | -0.17853 | 0.036621 | 0.19684 | -0.23346 | -0.23804 | -0.2243 | -0.22888 | -0.027466 | -0.1236 | -0.041199 | 0.036621 | -0.15106 | -0.13275 | -0.1236 | -0.10528 | 0.20599 | 122.1497 | 0.064087 | 122.0901 | 121.9345 | 122.0078 | 121.9254 | 121.9803 | -122.113 | -122.1313 | 122.1405 | 122.0627 | 59.1248 | 59.1248
1033.5625 | 122.2412 | -59.024 | 63.1302 | -0.013657 | 0.0014163 | 0.060103 | 0.059035 | -0.001491 | -0.0070517 | -0.0038303 | -0.0021057 | 0.0034392 | 0.072151 | 0.064841 | -0.010519 | 0.018585 | -0.0018522 | -0.013733 | 62.9425 | -59.024 | 63.089 | -58.8684 | -59.3033 | -59.2804 | 0.018311 | 62.9471 | -59.0744 | 63.0615 | -58.9783 | -59.1385 | -59.1248 | 0 | -0.18768 | -0.041199 | 0.15564 | -0.25635 | -0.27924 | -0.25635 | -0.27924 | -0.050354 | -0.1831 | -0.068665 | 0.045777 | -0.10071 | -0.11444 | -0.050354 | -0.064087 | 0.15564 | 122.113 | 0.096131 | 122.1359 | 121.9666 | 122.0215 | 121.9666 | 121.9711 | -122.1542 | -122.2046 | 122.113 | 122.0856 | 59.0103 | 59.0424
1035.25 | 122.3328 | -58.9645 | 63.0798 | -0.013657 | -7.9104e-05 | 0.059248 | 0.057539 | -0.00085021 | -0.0079061 | -0.0040439 | -0.0082093 | -0.00019216 | 0.07151 | 0.0642 | -0.0090235 | 0.019653 | -0.0050564 | -0.082397 | 62.9425 | -59.0012 | 63.1622 | -58.7723 | -59.2346 | -59.1751 | 0 | 62.9333 | -59.0195 | 63.1393 | -58.8821 | -59.0607 | -59.0515 | -0.036621 | -0.13733 | 0.082397 | 0.19226 | -0.21057 | -0.27008 | -0.17395 | -0.23346 | -0.054931 | -0.14648 | 0.059509 | 0.082398 | -0.086975 | -0.09613 | -0.032044 | -0.041199 | 0.22888 | 122.1634 | 0.13733 | 122.1588 | 121.9437 | 121.9528 | 121.907 | 121.8979 | -122.081 | -122.0993 | 122.1268 | 122.1039 | 58.8821 | 58.9645
1037 | 122.3511 | -58.8821 | 63.1622 | -0.013657 | 0.0033389 | 0.059889 | 0.060316 | 0.0027814 | -0.0051291 | -0.0031895 | -0.0051575 | 0.003012 | 0.073433 | 0.067405 | -0.010305 | 0.019653 | -0.0012112 | -0.10986 | 63.0203 | -58.905 | 63.2858 | -58.667 | -59.1293 | -59.1019 | 0.013733 | 63.0295 | -58.9325 | 63.2812 | -58.7814 | -58.9508 | -58.9142 | -0.022888 | -0.14191 | 0.1236 | 0.21515 | -0.21973 | -0.24719 | -0.19684 | -0.2243 | -0.050354 | -0.13275 | 0.11902 | 0.10071 | -0.032044 | -0.068665 | 0.01831 | -0.018311 | 0.23804 | 122.1909 | 0.15106 | 122.2137 | 121.9254 | 121.962 | 121.9025 | 121.9116 | -122.0673 | -122.0947 | 122.168 | 122.1634 | 58.7723 | 58.8959
1038.75 | 122.2275 | -58.7769 | 63.3179 | 0.0016023 | 0.0052615 | 0.062025 | 0.06053 | 0.0036358 | -0.0061971 | -0.0019077 | -0.0021057 | 0.0040802 | 0.070869 | 0.062705 | -0.010092 | 0.020721 | -0.0020658 | -0.12817 | 63.1714 | -58.8181 | 63.2858 | -58.6899 | -59.1339 | -59.1019 | -0.09613 | 63.1897 | -58.8501 | 63.2629 | -58.8226 | -58.992 | -58.9325 | -0.041199 | -0.14648 | -0.032043 | 0.086975 | -0.32501 | -0.35706 | -0.28381 | -0.31586 | -0.073243 | -0.12817 | -0.054932 | -0.045777 | -0.15564 | -0.21515 | -0.082397 | -0.14191 | 0.12817 | 122.1039 | 0.027466 | 122.113 | 121.9894 | 122.0398 | 121.9482 | 121.9666 | -122.1359 | -122.168 | 122.0627 | 122.0398 | 58.6487 | 58.6807
1040.4531 | 122.2321 | -58.6899 | 63.4369 | -0.0060272 | -0.0009335 | 0.059889 | 0.057539 | -0.0010638 | -0.0079061 | -0.0029759 | -0.0021057 | 0.00066224 | 0.071938 | 0.063346 | -0.0088097 | 0.019653 | 0.0004978 | 0 | 63.2538 | -58.7173 | 63.414 | -58.5205 | -58.9691 | -58.9371 | 0.018311 | 63.295 | -58.7311 | 63.3591 | -58.6578 | -58.8501 | -58.8501 | -0.027466 | -0.18311 | -0.022889 | 0.16937 | -0.24719 | -0.27924 | -0.21973 | -0.25177 | -0.041199 | -0.14191 | -0.07782 | 0.032043 | -0.16022 | -0.16022 | -0.11902 | -0.11902 | 0.19684 | 122.1313 | 0.073242 | 122.0901 | 121.9711 | 122.0261 | 121.9437 | 121.9849 | -122.1542 | -122.168 | 122.1039 | 122.049 | 58.6899 | 58.7082
1042.2031 | 122.3511 | -58.6487 | 63.4048 | -0.013657 | 0.0018435 | 0.059248 | 0.058821 | 0.00043159 | -0.0047019 | -0.0025485 | -0.0021057 | -0.00019216 | 0.071938 | 0.066336 | -0.0085961 | 0.021149 | -0.000784 | -0.11444 | 63.2767 | -58.6716 | 63.4872 | -58.4564 | -58.9188 | -58.8776 | -0.013733 | 63.2401 | -58.6853 | 63.5056 | -58.5663 | -58.7265 | -58.6899 | -0.022888 | -0.12817 | 0.082398 | 0.19226 | -0.22888 | -0.27008 | -0.20599 | -0.24719 | -0.036621 | -0.16479 | 0.10071 | 0.082398 | -0.041198 | -0.077819 | -0.004577 | -0.041198 | 0.21515 | 122.1588 | 0.11902 | 122.1909 | 121.9482 | 121.9254 | 121.9254 | 121.8887 | -122.0764 | -122.0901 | 122.1359 | 122.1542 | 58.5342 | 58.6349
1043.9531 | 122.2916 | -58.6029 | 63.5056 | 0.0016023 | 0.0009891 | 0.057326 | 0.056471 | 0.00043159 | -0.0068381 | -0.0014805 | -0.0051575 | 0.0027984 | 0.070229 | 0.065055 | -0.012014 | 0.017303 | -0.0065518 | 0.027466 | 63.3591 | -58.6075 | 63.5239 | -58.429 | -58.8547 | -58.8593 | 0.036621 | 63.3453 | -58.6349 | 63.501 | -58.548 | -58.7311 | -58.699 | -0.004578 | -0.14648 | 0.018311 | 0.17395 | -0.25635 | -0.25177 | -0.25177 | -0.24719 | -0.032044 | -0.16022 | -0.004577 | 0.054931 | -0.096131 | -0.12817 | -0.064087 | -0.09613 | 0.17853 | 122.1313 | 0.086975 | 122.1359 | 121.9666 | 121.9803 | 121.962 | 121.9482 | -122.113 | -122.1405 | 122.1268 | 122.1039 | 58.6304 | 58.6395
1045.6406 | 122.3648 | -58.5434 | 63.5193 | -0.021286 | -0.0020017 | 0.058394 | 0.054121 | -0.0010638 | -0.0057699 | -0.0027621 | -0.0051575 | 0.00066224 | 0.070869 | 0.062705 | -0.0092371 | 0.018372 | -0.0009976 | -0.013733 | 63.3636 | -58.548 | 63.6475 | -58.2825 | -58.7494 | -58.7082 | 0.1236 | 63.3453 | -58.5663 | 63.6246 | -58.3969 | -58.5388 | -58.5709 | -0.004578 | -0.15564 | 0.12817 | 0.26093 | -0.16479 | -0.20599 | -0.16022 | -0.20142 | -0.022888 | -0.17395 | 0.10529 | 0.14648 | -0.027466 | 0.004578 | -0.004578 | 0.027466 | 0.2655 | 122.1954 | 0.16937 | 122.1909 | 121.9116 | 121.9116 | 121.907 | 121.8887 | -122.0673 | -122.0856 | 122.1909 | 122.168 | 58.5297 | 58.667
1047.3281 | 122.3419 | -58.493 | 63.5193 | -0.013657 | 0.0020571 | 0.059889 | 0.05818 | 0.0010724 | -0.0068381 | -0.0063937 | -0.0082093 | 0.001303 | 0.074928 | 0.04946 | -0.0083825 | 0.019012 | -0.0063382 | -0.073242 | 63.3591 | -58.5342 | 63.6658 | -58.2596 | -58.7769 | -58.7219 | 0.050354 | 63.3362 | -58.5709 | 63.6108 | -58.4564 | -58.6075 | -58.5846 | -0.041199 | -0.16022 | 0.14648 | 0.23346 | -0.22888 | -0.28381 | -0.18768 | -0.24261 | -0.07782 | -0.1831 | 0.091553 | 0.036621 | -0.091553 | -0.11444 | -0.013733 | -0.036621 | 0.27466 | 122.2 | 0.11444 | 122.1817 | 121.8933 | 121.907 | 121.8521 | 121.8292 | -122.0535 | -122.0901 | 122.1588 | 122.1039 | 58.4198 | 58.5434
1049.0781 | 122.2321 | -58.429 | 63.6841 | -0.013657 | 0.0029117 | 0.061812 | 0.05818 | 0.0010724 | -0.0044883 | -0.0016941 | -0.0021057 | 0.0032256 | 0.072365 | 0.069114 | -0.0092371 | 0.019012 | -0.0031338 | -0.054932 | 63.5284 | -58.4518 | 63.6932 | -58.255 | -58.7265 | -58.7128 | -0.013733 | 63.5284 | -58.4839 | 63.6383 | -58.4335 | -58.6166 | -58.5617 | -0.022888 | -0.15564 | 0.009155 | 0.17395 | -0.28381 | -0.29755 | -0.26093 | -0.27466 | -0.054932 | -0.15564 | -0.045776 | -0.004578 | -0.13275 | -0.18768 | -0.07782 | -0.13275 | 0.19684 | 122.1451 | 0.050354 | 122.1222 | 121.9803 | 122.0123 | 121.9574 | 121.9574 | -122.1359 | -122.168 | 122.1222 | 122.0673 | 58.374 | 58.4152
1050.7656 | 122.3785 | -58.2962 | 63.7619 | -0.013657 | -0.0015743 | 0.059248 | 0.056258 | -0.0017048 | -0.0070517 | -0.0012669 | -0.0021057 | -0.00083316 | 0.072792 | 0.059714 | -0.010946 | 0.01709 | -0.0033474 | -0.027466 | 63.5788 | -58.3511 | 63.8626 | -58.0765 | -58.5114 | -58.4793 | 0.10529 | 63.5834 | -58.3511 | 63.8489 | -58.1772 | -58.3282 | -58.3374 | -0.054931 | -0.18311 | 0.10071 | 0.21973 | -0.1831 | -0.21515 | -0.12817 | -0.16022 | -0.054931 | -0.17853 | 0.086975 | 0.11902 | -0.041198 | -0.032043 | 0.013733 | 0.022888 | 0.27466 | 122.2137 | 0.17395 | 122.2 | 121.9299 | 121.9345 | 121.875 | 121.8796 | -122.113 | -122.113 | 122.1588 | 122.1451 | 58.2687 | 58.4015
1052.5156 | 122.2321 | -58.2367 | 63.9084 | -0.0060272 | 0.0031253 | 0.060744 | 0.058607 | 0.007481 | -0.0057699 | -0.0019077 | -0.0021057 | 0.004721 | 0.07151 | 0.068045 | -0.010732 | 0.020508 | -0.0033474 | -0.013733 | 63.7299 | -58.2367 | 63.9038 | -58.0582 | -58.5434 | -58.5159 | -0.009155 | 63.7115 | -58.2642 | 63.826 | -58.2413 | -58.4106 | -58.3832 | 0 | -0.17853 | -0.004577 | 0.17853 | -0.27924 | -0.3067 | -0.27924 | -0.3067 | -0.027466 | -0.19684 | -0.082397 | -0.004578 | -0.14648 | -0.17395 | -0.11902 | -0.14649 | 0.17853 | 122.1405 | 0.022888 | 122.0901 | 121.9666 | 121.9757 | 121.9666 | 121.9482 | -122.1451 | -122.1725 | 122.1405 | 122.0627 | 58.223 | 58.2275
1054.2031 | 122.2275 | -58.2092 | 63.9542 | -0.021286 | -0.0011471 | 0.059889 | 0.058394 | -0.0046954 | -0.0076925 | -0.0025485 | -0.0051575 | 0.0034392 | 0.070442 | 0.065482 | -0.0073145 | 0.015167 | -0.002493 | -0.004578 | 63.7665 | -58.2092 | 63.9221 | -58.017 | -58.461 | -58.429 | 0.027466 | 63.8168 | -58.2184 | 63.8809 | -58.168 | -58.342 | -58.3328 | 0 | -0.18768 | -0.032044 | 0.19226 | -0.21973 | -0.25177 | -0.21973 | -0.25177 | -0.009155 | -0.13733 | -0.073243 | 0.041199 | -0.1236 | -0.13275 | -0.11444 | -0.1236 | 0.19226 | 122.1313 | 0.050354 | 122.0993 | 121.9757 | 122.0352 | 121.9757 | 122.0261 | -122.1634 | -122.1725 | 122.1313 | 122.0901 | 58.2047 | 58.2367
1055.9531 | 122.2778 | -58.1635 | 63.9542 | -0.0060272 | 0.0029117 | 0.06053 | 0.059676 | 0.0025678 | -0.0059835 | -0.0034031 | -0.0021057 | 0.001944 | 0.071938 | 0.0642 | -0.010946 | 0.019226 | -0.0050564 | 0.018311 | 63.7802 | -58.1589 | 63.9954 | -57.9391 | -58.4061 | -58.3878 | 0.07782 | 63.7848 | -58.1635 | 63.9725 | -58.0994 | -58.2687 | -58.2275 | 0.004577 | -0.17395 | 0.041198 | 0.2243 | -0.2243 | -0.24262 | -0.22888 | -0.24719 | 0 | -0.16937 | 0.01831 | 0.064087 | -0.064087 | -0.10529 | -0.064087 | -0.10529 | 0.21973 | 122.1542 | 0.064087 | 122.1359 | 121.9391 | 121.9482 | 121.9437 | 121.9482 | -122.113 | -122.1176 | 122.1588 | 122.1359 | 58.1818 | 58.2413
1057.6562 | 122.2641 | -58.0582 | 64.064 | -0.0060272 | -0.0013607 | 0.058821 | 0.056044 | -0.00085021 | -0.0059835 | -0.0023349 | 0.0039977 | 0.0021576 | 0.072365 | 0.058005 | -0.010092 | 0.018372 | 7.04e-05 | 0.059509 | 63.8489 | -58.0444 | 64.1327 | -57.8156 | -58.2642 | -58.2275 | 0.10529 | 63.9038 | -58.0948 | 64.0182 | -57.9987 | -58.168 | -58.1726 | 0.013733 | -0.21515 | 0.068664 | 0.24262 | -0.16937 | -0.20599 | -0.1831 | -0.21973 | -0.036621 | -0.16022 | -0.045776 | 0.05951 | -0.11444 | -0.10986 | -0.077819 | -0.073242 | 0.22888 | 122.1771 | 0.096131 | 122.113 | 121.8933 | 121.9986 | 121.907 | 121.962 | -122.1085 | -122.1588 | 122.1909 | 122.0764 | 58.1177 | 58.1635
1059.4062 | 122.2824 | -58.0032 | 64.1052 | -0.021286 | 0.0005619 | 0.05818 | 0.054976 | -0.0034136 | -0.0091879 | -0.0040439 | -0.0051575 | 0.0017304 | 0.073006 | 0.068473 | -0.0098779 | 0.018372 | -0.0039884 | 0.004578 | 63.9587 | -58.0078 | 64.119 | -57.8384 | -58.2642 | -58.2504 | 0.027466 | 63.9816 | -58.0444 | 64.0732 | -57.9483 | -58.1543 | -58.0948 | -0.004577 | -0.14649 | 0.013733 | 0.16479 | -0.24719 | -0.26093 | -0.24262 | -0.25635 | -0.041199 | -0.1236 | -0.032044 | 0.054932 | -0.091553 | -0.15106 | -0.050354 | -0.10986 | 0.16937 | 122.1268 | 0.096131 | 122.1176 | 121.9666 | 122.0261 | 121.962 | 121.9849 | -122.113 | -122.1497 | 122.1222 | 122.0764 | 58.0078 | 58.0307
1061.0938 | 122.2641 | -57.8796 | 64.2334 | -0.013657 | 0.0029117 | 0.061171 | 0.057539 | 0.0038494 | -0.0049155 | -0.0027621 | -0.0021057 | 0.0015166 | 0.071083 | 0.059501 | -0.0083825 | 0.019226 | -0.0027066 | -0.1236 | 64.1052 | -57.8934 | 64.2334 | -57.7332 | -58.1863 | -58.1497 | -0.068665 | 64.0778 | -57.8979 | 64.2197 | -57.8567 | -58.0353 | -57.9849 | -0.013733 | -0.12817 | 0 | 0.14648 | -0.27008 | -0.3067 | -0.25635 | -0.29297 | -0.01831 | -0.15564 | -0.013732 | 0.022889 | -0.10529 | -0.15564 | -0.086975 | -0.13733 | 0.16022 | 122.1268 | 0.041199 | 122.1176 | 121.9986 | 121.9757 | 121.9849 | 121.9574 | -122.1268 | -122.1313 | 122.113 | 122.0993 | 57.756 | 57.811
1062.8438 | 122.374 | -57.7057 | 64.3341 | -0.0060272 | 0.0007755 | 0.061812 | 0.056471 | -0.0036274 | -0.0064109 | -0.0040439 | -0.0021057 | 0.00023504 | 0.072792 | 0.069327 | -0.010092 | 0.016663 | -0.0012112 | -0.068665 | 64.1739 | -57.724 | 64.476 | -57.4722 | -57.962 | -57.8979 | 0.064087 | 64.1647 | -57.7469 | 64.4394 | -57.6141 | -57.7789 | -57.7606 | -0.018311 | -0.16022 | 0.14191 | 0.23346 | -0.19226 | -0.25635 | -0.17395 | -0.23804 | -0.041199 | -0.16937 | 0.10529 | 0.091552 | -0.054932 | -0.073243 | -0.013733 | -0.032044 | 0.25177 | 122.2 | 0.13275 | 122.1863 | 121.8979 | 121.9116 | 121.8796 | 121.8704 | -122.0581 | -122.081 | 122.1817 | 122.1451 | 57.637 | 57.7698
1064.5312 | 122.2504 | -57.6187 | 64.5401 | -0.0060272 | 0.0020571 | 0.060957 | 0.059889 | 0.002995 | -0.0076925 | -0.0019077 | -0.0051575 | 0.003653 | 0.071724 | 0.064414 | -0.0092371 | 0.019012 | 0.0017794 | -0.027466 | 64.3478 | -57.6004 | 64.5493 | -57.4081 | -57.8796 | -57.8522 | 0.018311 | 64.3616 | -57.6508 | 64.4669 | -57.5867 | -57.7606 | -57.7194 | 0.01831 | -0.19226 | 0.009155 | 0.21057 | -0.23346 | -0.26093 | -0.25177 | -0.27924 | -0.032044 | -0.17853 | -0.073242 | 0.032043 | -0.10071 | -0.14191 | -0.068664 | -0.10986 | 0.19226 | 122.1497 | 0.064087 | 122.1176 | 121.9482 | 122.0123 | 121.9666 | 121.9803 | -122.1405 | -122.1909 | 122.168 | 122.0856 | 57.5912 | 57.637
1066.2188 | 122.3328 | -57.5317 | 64.5355 | -0.0060272 | -7.9104e-05 | 0.058394 | 0.055617 | -0.00020941 | -0.0053427 | 0.0012967 | -0.0021057 | 0.00044864 | 0.071938 | 0.060996 | -0.0085961 | 0.017944 | -0.0027066 | -0.064087 | 64.3524 | -57.5546 | 64.6088 | -57.3257 | -57.7835 | -57.7469 | 0.013733 | 64.3524 | -57.5821 | 64.5813 | -57.4585 | -57.6141 | -57.6096 | -0.022888 | -0.1831 | 0.073243 | 0.20599 | -0.21515 | -0.25177 | -0.19226 | -0.22888 | -0.050354 | -0.1831 | 0.045777 | 0.073242 | -0.07782 | -0.082398 | -0.027466 | -0.032044 | 0.22888 | 122.1634 | 0.1236 | 122.1634 | 121.907 | 121.9345 | 121.8842 | 121.8842 | -122.0901 | -122.1176 | 122.1405 | 122.113 | 57.4677 | 57.5455
1067.9688 | 122.3877 | -57.4493 | 64.595 | -0.013657 | -0.0026425 | 0.056898 | 0.055403 | 0.002995 | -0.0068381 | -0.0036167 | -0.0021057 | 0.00023504 | 0.070229 | 0.059714 | -0.011373 | 0.017517 | 0.0004978 | 0.013733 | 64.4257 | -57.4539 | 64.7186 | -57.1838 | -57.6508 | -57.6096 | 0.14191 | 64.4211 | -57.486 | 64.6912 | -57.3303 | -57.486 | -57.4905 | -0.004577 | -0.16937 | 0.1236 | 0.2655 | -0.16022 | -0.20142 | -0.15564 | -0.19684 | -0.036621 | -0.17395 | 0.09613 | 0.11902 | -0.041199 | -0.036621 | -0.004578 | 0 | 0.27008 | 122.1725 | 0.15564 | 122.1771 | 121.8796 | 121.907 | 121.875 | 121.8704 | -122.049 | -122.081 | 122.168 | 122.1405 | 57.4631 | 57.5912
1069.7344 | 122.3465 | -57.3441 | 64.7141 | 0.0016023 | 0.0026981 | 0.059676 | 0.060744 | 0.0010724 | -0.0036337 | -0.0023349 | -0.0021057 | 0.0023712 | 0.071083 | 0.060141 | -0.011373 | 0.018372 | -0.0074064 | -0.086975 | 64.563 | -57.3669 | 64.8239 | -57.1426 | -57.6096 | -57.5592 | 0.059509 | 64.5493 | -57.3715 | 64.801 | -57.2662 | -57.4448 | -57.3853 | -0.022888 | -0.15106 | 0.10986 | 0.20142 | -0.21515 | -0.2655 | -0.19226 | -0.24262 | -0.027466 | -0.16479 | 0.086975 | 0.07782 | -0.041199 | -0.10071 | -0.013733 | -0.073242 | 0.2243 | 122.1909 | 0.10529 | 122.1725 | 121.9299 | 121.9208 | 121.907 | 121.8933 | -122.081 | -122.0856 | 122.168 | 122.1451 | 57.2571 | 57.4036
1071.4062 | 122.3602 | -57.28 | 64.7873 | 0.0016023 | -0.0013607 | 0.060957 | 0.056685 | -0.0032 | -0.0047019 | -0.00083947 | -0.0051575 | 0.0010894 | 0.071724 | 0.061423 | -0.011373 | 0.015381 | -0.0033474 | -0.032043 | 64.6317 | -57.2891 | 64.8834 | -57.0511 | -57.4997 | -57.4585 | 0.082397 | 64.6362 | -57.3029 | 64.8788 | -57.1655 | -57.3257 | -57.312 | -0.009156 | -0.15564 | 0.096131 | 0.22888 | -0.17853 | -0.21973 | -0.16937 | -0.21057 | -0.022888 | -0.15106 | 0.091553 | 0.11444 | -0.032044 | -0.045777 | -0.009156 | -0.022889 | 0.23804 | 122.1725 | 0.13733 | 122.1817 | 121.9208 | 121.9391 | 121.9116 | 121.9162 | -122.0764 | -122.0901 | 122.1634 | 122.1588 | 57.2479 | 57.3624
1073.0938 | 122.2458 | -57.2021 | 64.9521 | 0.0016023 | 0.0018435 | 0.059035 | 0.059248 | 0.0021406 | -0.0076925 | -0.0014805 | -0.0021057 | 0.0023712 | 0.071083 | 0.060569 | -0.0098779 | 0.018585 | -0.0029202 | 0.013733 | 64.7736 | -57.2113 | 64.9063 | -57.0602 | -57.486 | -57.4631 | 0.009155 | 64.7598 | -57.2571 | 64.8651 | -57.193 | -57.3532 | -57.3441 | -0.009156 | -0.17853 | -0.045776 | 0.14191 | -0.26093 | -0.28381 | -0.25177 | -0.27466 | -0.054932 | -0.19226 | -0.086975 | 0.009155 | -0.14191 | -0.15106 | -0.086975 | -0.09613 | 0.15106 | 122.1176 | 0.064087 | 122.1222 | 121.9849 | 122.0169 | 121.9757 | 121.962 | -122.1634 | -122.2092 | 122.1085 | 122.0673 | 57.2159 | 57.2113
1074.8438 | 122.2549 | -57.0648 | 65.062 | -0.0060272 | 0.0001345 | 0.056898 | 0.056258 | 0.00064519 | -0.0081197 | -0.0053257 | -0.0021057 | 0.0010894 | 0.071938 | 0.063132 | -0.0094507 | 0.015808 | 0.0013522 | 0.054932 | 64.8743 | -57.074 | 65.0711 | -56.8771 | -57.3029 | -57.2845 | 0.045776 | 64.9017 | -57.106 | 65.0024 | -57.0465 | -57.2113 | -57.2021 | -0.009156 | -0.18768 | 0.009155 | 0.18768 | -0.21973 | -0.23804 | -0.21057 | -0.22888 | -0.041199 | -0.16022 | -0.05951 | 0.01831 | -0.13733 | -0.14648 | -0.09613 | -0.10529 | 0.19684 | 122.1451 | 0.059509 | 122.1085 | 121.9482 | 122.0078 | 121.9391 | 121.9666 | -122.1359 | -122.168 | 122.1359 | 122.0673 | 57.1198 | 57.1106
1076.5938 | 122.2549 | -56.987 | 65.1169 | 0.0016023 | 0.0031253 | 0.06288 | 0.060744 | -0.0012774 | -0.0057699 | -0.0038303 | -0.0021057 | 0.0023712 | 0.072151 | 0.069754 | -0.0098779 | 0.017303 | -0.0012112 | 0.009155 | 64.9704 | -56.9824 | 65.1718 | -56.7993 | -57.2479 | -57.2067 | 0.064087 | 64.9841 | -57.0099 | 65.0986 | -56.9458 | -57.1426 | -57.0831 | 0.004578 | -0.14648 | 0.054932 | 0.18768 | -0.21973 | -0.26093 | -0.2243 | -0.2655 | -0.022888 | -0.13275 | -0.01831 | 0.041199 | -0.09613 | -0.15564 | -0.073242 | -0.13275 | 0.18311 | 122.1542 | 0.064087 | 122.1085 | 121.9528 | 121.994 | 121.9574 | 121.9711 | -122.0993 | -122.1268 | 122.1588 | 122.0856 | 56.9962 | 57.0511
1078.2812 | 122.3007 | -56.9687 | 65.1581 | -0.0060272 | -0.0002927 | 0.059035 | 0.056898 | -0.0036274 | -0.0064109 | -0.0036167 | -0.0051575 | 0.0017304 | 0.072792 | 0.063346 | -0.010092 | 0.017944 | -0.00527 | 0.086975 | 64.9292 | -56.9641 | 65.2359 | -56.7215 | -57.1518 | -57.1381 | 0.1236 | 64.9704 | -56.9733 | 65.1443 | -56.8909 | -57.0602 | -57.0511 | 0.004578 | -0.22888 | 0.07782 | 0.24719 | -0.16937 | -0.18311 | -0.17395 | -0.18768 | -0.004578 | -0.18768 | -0.013733 | 0.07782 | -0.082397 | -0.091553 | -0.077819 | -0.086975 | 0.24261 | 122.2 | 0.082398 | 122.1176 | 121.8933 | 121.9437 | 121.8979 | 121.9391 | -122.1222 | -122.1313 | 122.2046 | 122.113 | 57.0557 | 57.0923
1080.0312 | 122.3145 | -56.9366 | 65.1443 | -0.0060272 | 0.0009891 | 0.057967 | 0.056685 | -0.0040546 | -0.0057699 | -0.0036167 | -0.0021057 | -0.0010468 | 0.071297 | 0.06185 | -0.0090235 | 0.018799 | -0.0029202 | -0.059509 | 64.9658 | -56.9504 | 65.1947 | -56.7581 | -57.1976 | -57.1701 | 0 | 64.9612 | -56.9962 | 65.1718 | -56.8863 | -57.0328 | -57.0145 | -0.013732 | -0.17853 | 0.050354 | 0.17853 | -0.23346 | -0.26093 | -0.21973 | -0.24719 | -0.059509 | -0.1831 | 0.027466 | 0.050354 | -0.077819 | -0.09613 | -0.01831 | -0.036621 | 0.19226 | 122.1451 | 0.10986 | 122.168 | 121.9162 | 121.9574 | 121.9025 | 121.8979 | -122.0947 | -122.1405 | 122.1313 | 122.1085 | 56.8771 | 56.9366
1081.7031 | 122.2733 | -56.9458 | 65.1672 | -0.013657 | 0.0039799 | 0.059035 | 0.05818 | 0.001286 | -0.0057699 | -0.0027621 | -0.0051575 | 0.003653 | 0.07386 | 0.059501 | -0.010305 | 0.019653 | -0.0018522 | -0.12817 | 65.0208 | -56.9641 | 65.1672 | -56.8085 | -57.2662 | -57.2067 | -0.054932 | 65.0208 | -56.9733 | 65.1443 | -56.9321 | -57.1106 | -57.0602 | -0.01831 | -0.14648 | 0 | 0.13733 | -0.26093 | -0.32043 | -0.24262 | -0.30212 | -0.027466 | -0.14648 | -0.022888 | 0.013733 | -0.11444 | -0.16479 | -0.086975 | -0.13733 | 0.15564 | 122.1313 | 0.041199 | 122.1176 | 121.9849 | 121.994 | 121.9666 | 121.9666 | -122.1313 | -122.1405 | 122.113 | 122.0901 | 56.8176 | 56.8909
1083.3906 | 122.3557 | -56.6711 | 65.3595 | -0.013657 | -0.0020017 | 0.056685 | 0.057326 | 4.192e-06 | -0.0072653 | -0.0027621 | 0.0009461 | -0.0016876 | 0.069588 | 0.061423 | -0.012655 | 0.017731 | -0.0050564 | 0.041199 | 65.1901 | -56.6986 | 65.538 | -56.3828 | -56.8497 | -56.8268 | 0.15564 | 65.1947 | -56.7169 | 65.4556 | -56.5521 | -56.7169 | -56.7261 | -0.027465 | -0.16937 | 0.17853 | 0.28839 | -0.15564 | -0.17853 | -0.12817 | -0.15106 | -0.045776 | -0.16479 | 0.09613 | 0.11902 | -0.054931 | -0.045776 | -0.009155 | 0 | 0.31586 | 122.2366 | 0.16479 | 122.1725 | 121.8887 | 121.9116 | 121.8613 | 121.8658 | -122.0581 | -122.0764 | 122.2092 | 122.1268 | 56.7123 | 56.8268
1085.0938 | 122.3602 | -56.6666 | 65.3549 | -0.0060272 | 0.0007755 | 0.059676 | 0.057326 | 0.00043159 | -0.0074789 | -0.0055393 | -0.0082093 | 0.003653 | 0.072365 | 0.060141 | -0.012228 | 0.019012 | -0.0009976 | 0.059509 | 65.2267 | -56.6849 | 65.5243 | -56.4011 | -56.8726 | -56.8359 | 0.16937 | 65.2084 | -56.7169 | 65.4648 | -56.5613 | -56.7078 | -56.7307 | -0.01831 | -0.12817 | 0.16937 | 0.2655 | -0.16937 | -0.20599 | -0.15106 | -0.18768 | -0.050354 | -0.14648 | 0.10986 | 0.10529 | -0.064087 | -0.041199 | -0.013733 | 0.009155 | 0.28381 | 122.2092 | 0.15564 | 122.1817 | 121.9116 | 121.9254 | 121.8933 | 121.875 | -122.0398 | -122.0718 | 122.1909 | 122.1313 | 56.7261 | 56.8359
1086.8438 | 122.2458 | -56.543 | 65.5701 | -0.013657 | -0.0007199 | 0.058821 | 0.05583 | -0.0025592 | -0.0049155 | -0.0034031 | -0.0051575 | 0.0023712 | 0.071724 | 0.062064 | -0.0098779 | 0.016022 | -0.0016384 | 0.059509 | 65.3687 | -56.5521 | 65.6296 | -56.3187 | -56.7673 | -56.7398 | 0.086975 | 65.419 | -56.5933 | 65.5243 | -56.4972 | -56.6803 | -56.6757 | -0.009155 | -0.20142 | 0.05951 | 0.2243 | -0.19684 | -0.2243 | -0.18768 | -0.21515 | -0.050354 | -0.15106 | -0.045776 | 0.045777 | -0.13275 | -0.13733 | -0.082397 | -0.086975 | 0.23346 | 122.1817 | 0.096131 | 122.1176 | 121.9208 | 122.0123 | 121.9116 | 121.962 | -122.1222 | -122.1634 | 122.1725 | 122.0673 | 56.6025 | 56.6299
1088.5312 | 122.3373 | -56.3553 | 65.7211 | -0.0060272 | -0.0005063 | 0.056685 | 0.057967 | -0.001491 | -0.0074789 | -0.0029759 | -0.0021057 | -0.0012604 | 0.073219 | 0.0642 | -0.0096643 | 0.016449 | -0.0061246 | -0.054932 | 65.5472 | -56.3828 | 65.7852 | -56.1905 | -56.6254 | -56.5796 | 0.022888 | 65.538 | -56.3965 | 65.7623 | -56.2775 | -56.4377 | -56.4239 | -0.027465 | -0.17395 | 0.064087 | 0.16479 | -0.2243 | -0.27008 | -0.19684 | -0.24262 | -0.041198 | -0.1831 | 0.041199 | 0.07782 | -0.068664 | -0.082397 | -0.027466 | -0.041199 | 0.19226 | 122.168 | 0.11902 | 122.1588 | 121.9299 | 121.9345 | 121.9025 | 121.8933 | -122.1039 | -122.1176 | 122.1405 | 122.1176 | 56.3004 | 56.3782
1090.2188 | 122.2687 | -56.3004 | 65.8493 | -0.0060272 | 0.0003483 | 0.056685 | 0.059889 | -0.0044818 | -0.0059835 | -0.0038303 | -0.0021057 | 0.0042938 | 0.071724 | 0.065482 | -0.010519 | 0.019867 | -0.0033474 | 0.018311 | 65.6662 | -56.3232 | 65.8264 | -56.1447 | -56.5659 | -56.5338 | 0.032043 | 65.6754 | -56.3278 | 65.8127 | -56.25 | -56.4331 | -56.4011 | -0.022888 | -0.1831 | -0.022888 | 0.15564 | -0.23346 | -0.2655 | -0.21057 | -0.24262 | -0.027466 | -0.17395 | -0.036621 | 0.050354 | -0.10071 | -0.13275 | -0.073242 | -0.10528 | 0.17853 | 122.1497 | 0.07782 | 122.1405 | 121.9894 | 122.0032 | 121.9666 | 121.9757 | -122.1725 | -122.1771 | 122.1268 | 122.113 | 56.3187 | 56.3324
1091.9688 | 122.3145 | -56.1813 | 65.918 | -0.013657 | 0.0020571 | 0.059035 | 0.056044 | -0.0027728 | -0.0066245 | -0.0040439 | -0.0051575 | 0.0015166 | 0.070656 | 0.056937 | -0.0096643 | 0.018372 | -0.004202 | -0.07782 | 65.7394 | -56.1539 | 66.0141 | -55.9296 | -56.4056 | -56.3644 | 0.022888 | 65.7394 | -56.1768 | 65.9546 | -56.1035 | -56.25 | -56.2454 | 0.027465 | -0.17853 | 0.09613 | 0.25177 | -0.18311 | -0.22431 | -0.21057 | -0.25177 | 0.004577 | -0.17853 | 0.036621 | 0.077819 | -0.064087 | -0.068665 | -0.068664 | -0.073242 | 0.22431 | 122.168 | 0.073242 | 122.1313 | 121.8933 | 121.9162 | 121.9208 | 121.9208 | -122.0718 | -122.0947 | 122.1954 | 122.1359 | 56.1035 | 56.2042
1093.6562 | 122.2366 | -56.0211 | 66.1285 | -0.0060272 | 0.0024845 | 0.061385 | 0.061171 | 0.0032086 | -0.0055563 | -0.0027621 | -0.0051575 | 0.0034392 | 0.070869 | 0.063773 | -0.012869 | 0.017731 | -0.0039884 | -0.045776 | 65.9454 | -56.0669 | 66.1011 | -55.8792 | -56.337 | -56.2912 | -0.036621 | 65.9729 | -56.0394 | 66.0461 | -56.044 | -56.2271 | -56.163 | -0.045777 | -0.1831 | -0.027466 | 0.14191 | -0.27008 | -0.31586 | -0.2243 | -0.27008 | -0.018311 | -0.15564 | -0.082397 | -0.022888 | -0.14191 | -0.20599 | -0.1236 | -0.18768 | 0.18768 | 122.168 | -0.004577 | 122.0856 | 122.0123 | 122.0123 | 121.9666 | 121.994 | -122.1954 | -122.168 | 122.1222 | 122.0673 | 55.9753 | 55.9845
1095.3438 | 122.3511 | -55.9113 | 66.1514 | -0.0060272 | 0.0016299 | 0.060744 | 0.056898 | -0.00063661 | -0.0057699 | -0.0021213 | -0.0021057 | 0.0021576 | 0.069801 | 0.061637 | -0.010946 | 0.019653 | -0.0056974 | -0.07782 | 66.0004 | -55.9067 | 66.2659 | -55.7098 | -56.163 | -56.131 | 0.032043 | 65.9775 | -55.9708 | 66.2476 | -55.8289 | -56.0028 | -55.9525 | 0.004578 | -0.15106 | 0.11444 | 0.20142 | -0.21973 | -0.25177 | -0.2243 | -0.25635 | -0.059509 | -0.17395 | 0.096131 | 0.082398 | -0.041199 | -0.091553 | 0.01831 | -0.032044 | 0.19684 | 122.1725 | 0.14191 | 122.2183 | 121.907 | 121.9482 | 121.9116 | 121.8887 | -122.0581 | -122.1222 | 122.1771 | 122.1588 | 55.8334 | 55.9433
1097.0938 | 122.3785 | -55.806 | 66.2476 | -0.0060272 | 0.0026981 | 0.060744 | 0.058821 | 0.00085879 | -0.0057699 | -0.0036167 | -0.0051575 | 0.0023712 | 0.071297 | 0.065268 | -0.0098779 | 0.017944 | -0.0005704 | -0.045776 | 66.0919 | -55.8289 | 66.3712 | -55.5954 | -56.0715 | -56.0211 | 0.041199 | 66.0645 | -55.8884 | 66.3345 | -55.7281 | -55.8838 | -55.8426 | -0.022888 | -0.15564 | 0.1236 | 0.21057 | -0.21515 | -0.2655 | -0.19226 | -0.24262 | -0.082398 | -0.18311 | 0.086975 | 0.07782 | -0.036621 | -0.07782 | 0.045777 | 0.004578 | 0.23346 | 122.2 | 0.16022 | 122.2229 | 121.9208 | 121.9528 | 121.8979 | 121.8704 | -122.0764 | -122.1359 | 122.1771 | 122.1405 | 55.7602 | 55.8472
1098.8281 | 122.319 | -55.5405 | 66.5451 | -0.013657 | 0.0018435 | 0.058394 | 0.057539 | -0.003841 | -0.0057699 | -0.0031895 | -0.0051575 | 0.00044864 | 0.070015 | 0.063346 | -0.0081689 | 0.017731 | -0.0009976 | -0.07782 | 66.362 | -55.5588 | 66.6275 | -55.3391 | -55.8014 | -55.7602 | 0.009155 | 66.3574 | -55.5725 | 66.568 | -55.4947 | -55.6458 | -55.6229 | -0.018311 | -0.18311 | 0.082397 | 0.20142 | -0.21973 | -0.26093 | -0.20142 | -0.24262 | -0.032044 | -0.18768 | 0.022888 | 0.045776 | -0.082398 | -0.10529 | -0.050354 | -0.073242 | 0.21973 | 122.1863 | 0.07782 | 122.1405 | 121.9208 | 121.9299 | 121.9025 | 121.8979 | -122.1039 | -122.1176 | 122.168 | 122.1085 | 55.4626 | 55.5496
1100.5938 | 122.3923 | -55.1743 | 66.8701 | 0.0016023 | 0.0001345 | 0.057539 | 0.055189 | 0.0014996 | -0.0074789 | -0.0016941 | -0.0021057 | 0.00087584 | 0.072578 | 0.062705 | -0.0098779 | 0.016876 | -0.0048428 | 0.018311 | 66.7053 | -55.2017 | 67.0166 | -54.9316 | -55.3802 | -55.3528 | 0.14648 | 66.7053 | -55.2246 | 66.9617 | -55.0507 | -55.22 | -55.2292 | -0.027466 | -0.16479 | 0.14649 | 0.24261 | -0.17853 | -0.20599 | -0.15106 | -0.17853 | -0.050354 | -0.16479 | 0.091553 | 0.1236 | -0.054932 | -0.045777 | -0.004578 | 0.004577 | 0.27008 | 122.2183 | 0.17395 | 122.1863 | 121.907 | 121.9299 | 121.8796 | 121.8796 | -122.0718 | -122.0947 | 122.1909 | 122.1359 | 55.1926 | 55.3207
1102.2812 | 122.2412 | -55.0369 | 67.1082 | -0.0060272 | 0.0029117 | 0.059889 | 0.060316 | 0.0019268 | -0.0038473 | -0.0036167 | -0.0051575 | 0.0045074 | 0.071083 | 0.068259 | -0.01351 | 0.020721 | 0.0011386 | -0.09613 | 66.9617 | -55.0323 | 67.0761 | -54.9454 | -55.3848 | -55.3528 | -0.082397 | 66.9571 | -55.069 | 67.0441 | -55.0598 | -55.2338 | -55.1559 | 0.004577 | -0.14648 | -0.032043 | 0.091552 | -0.31586 | -0.3479 | -0.32043 | -0.35248 | -0.032044 | -0.15106 | -0.064087 | -0.022888 | -0.11902 | -0.19684 | -0.086975 | -0.16479 | 0.086975 | 122.1085 | 0.009156 | 122.113 | 121.994 | 122.0261 | 121.9986 | 121.994 | -122.1405 | -122.1771 | 122.113 | 122.081 | 54.9408 | 54.9545
1104.0312 | 122.3328 | -54.9179 | 67.1356 | -0.021286 | -0.0002927 | 0.058821 | 0.056898 | -0.0017048 | -0.0047019 | -0.0038303 | -0.0021057 | 0.00044864 | 0.071724 | 0.055228 | -0.010732 | 0.018799 | -0.002493 | -0.064087 | 66.9708 | -54.9637 | 67.1951 | -54.776 | -55.1971 | -55.1651 | -0.009155 | 66.9662 | -54.9866 | 67.1722 | -54.8859 | -55.0598 | -55.0415 | -0.045776 | -0.16479 | 0.059509 | 0.14191 | -0.24719 | -0.27924 | -0.20142 | -0.23346 | -0.068664 | -0.16937 | 0.036621 | 0.032044 | -0.1236 | -0.14191 | -0.054932 | -0.073242 | 0.18768 | 122.1588 | 0.10071 | 122.1588 | 121.9345 | 121.9528 | 121.8887 | 121.8842 | -122.0993 | -122.1222 | 122.113 | 122.0901 | 54.8538 | 54.9088
1105.7812 | 122.2458 | -54.9316 | 67.1997 | 0.0016023 | 0.0005619 | 0.057539 | 0.060103 | 0.0014996 | -0.0085471 | -0.0036167 | -0.0021057 | 0.0034392 | 0.073219 | 0.0642 | -0.0094507 | 0.019867 | -0.000784 | 0.009155 | 67.0532 | -54.9088 | 67.1906 | -54.8035 | -55.2155 | -55.188 | 0.004578 | 67.0441 | -54.9728 | 67.131 | -54.8996 | -55.0873 | -55.0507 | 0.022889 | -0.14648 | -0.009155 | 0.12817 | -0.25635 | -0.28381 | -0.27924 | -0.3067 | -0.041198 | -0.15564 | -0.068665 | 0.032044 | -0.11902 | -0.15564 | -0.07782 | -0.11444 | 0.10529 | 122.0993 | 0.073242 | 122.1039 | 121.962 | 122.0169 | 121.9849 | 121.9757 | -122.1085 | -122.1725 | 122.1222 | 122.0627 | 54.9408 | 54.9362
1107.4844 | 122.2549 | -54.9545 | 67.1768 | -0.013657 | 0.0003483 | 0.057967 | 0.059035 | -0.0012774 | -0.0053427 | -0.0036167 | -0.0021057 | 0.0023712 | 0.072792 | 0.071036 | -0.0096643 | 0.017517 | 0.0013522 | 0.013733 | 67.0303 | -54.9774 | 67.1356 | -54.8264 | -55.2383 | -55.2338 | 0.013733 | 67.012 | -54.982 | 67.1082 | -54.9225 | -55.0964 | -55.0873 | -0.022888 | -0.14648 | -0.041199 | 0.12817 | -0.27924 | -0.28381 | -0.25635 | -0.26093 | -0.027466 | -0.16479 | -0.068665 | 0.032044 | -0.13275 | -0.14191 | -0.10529 | -0.11444 | 0.15106 | 122.113 | 0.05951 | 122.0901 | 122.0078 | 121.994 | 121.9849 | 121.9666 | -122.1542 | -122.1588 | 122.0901 | 122.0627 | 54.9683 | 54.9683
1109.2188 | 122.2641 | -54.8218 | 67.2958 | -0.0060272 | 0.0009891 | 0.05818 | 0.060316 | 0.0057722 | -0.0057699 | -0.00062587 | -0.0021057 | 0.0027984 | 0.068947 | 0.060355 | -0.0088097 | 0.017944 | -0.0061246 | -0.018311 | 67.0898 | -54.8676 | 67.3096 | -54.6616 | -55.1239 | -55.0781 | 0.036621 | 67.1448 | -54.8721 | 67.2638 | -54.8172 | -55.0049 | -54.9545 | -0.045777 | -0.20599 | 0.013733 | 0.16022 | -0.25635 | -0.30212 | -0.21057 | -0.25635 | -0.050354 | -0.15106 | -0.032043 | 0.004577 | -0.13275 | -0.18311 | -0.082398 | -0.13275 | 0.20599 | 122.1771 | 0.054931 | 122.1359 | 121.9574 | 122.0169 | 121.9116 | 121.9666 | -122.1634 | -122.168 | 122.1313 | 122.0856 | 54.8035 | 54.8584
1110.9688 | 122.2458 | -54.7943 | 67.3416 | 0.0016023 | 0.0024845 | 0.060103 | 0.060744 | 0.0025678 | -0.0032065 | -0.0038303 | -0.0021057 | 0.0045074 | 0.074074 | 0.06655 | -0.01116 | 0.01944 | 0.0022068 | -0.091553 | 67.1951 | -54.808 | 67.3004 | -54.6936 | -55.1285 | -55.0919 | -0.082397 | 67.1677 | -54.8172 | 67.2775 | -54.8035 | -54.982 | -54.9088 | -0.013732 | -0.14649 | -0.041199 | 0.10071 | -0.29755 | -0.33417 | -0.28381 | -0.32043 | -0.022888 | -0.17395 | -0.064087 | -0.009155 | -0.11444 | -0.18768 | -0.091552 | -0.16479 | 0.11444 | 122.1085 | 0.013733 | 122.0947 | 122.0032 | 121.9849 | 121.9894 | 121.962 | -122.1497 | -122.1588 | 122.0947 | 122.0718 | 54.7028 | 54.7119
1112.6719 | 122.287 | -54.6295 | 67.4515 | -0.0060272 | 0.0031253 | 0.057967 | 0.057967 | -0.00042301 | -0.0051291 | 1.4934e-05 | -0.0051575 | 0.0042938 | 0.074501 | 0.068473 | -0.0090235 | 0.019012 | -0.0022794 | 0.013733 | 67.337 | -54.657 | 67.5201 | -54.4327 | -54.8859 | -54.8492 | 0.068665 | 67.3233 | -54.689 | 67.4744 | -54.5975 | -54.7668 | -54.7302 | -0.027465 | -0.11444 | 0.068665 | 0.19684 | -0.21973 | -0.25635 | -0.19226 | -0.22888 | -0.059509 | -0.12817 | 0.022888 | 0.032044 | -0.10071 | -0.13733 | -0.041199 | -0.07782 | 0.2243 | 122.1771 | 0.091553 | 122.1634 | 121.994 | 122.0123 | 121.9666 | 121.9528 | -122.1085 | -122.1405 | 122.1497 | 122.1039 | 54.6433 | 54.6982
1114.4375 | 122.2778 | -54.4373 | 67.6941 | 0.0016023 | 0.0044071 | 0.058394 | 0.057539 | 0.0036358 | -0.0066245 | -0.0061801 | -0.0082093 | 0.003012 | 0.073433 | 0.064841 | -0.0090235 | 0.017303 | 0.0022068 | 0.027466 | 67.5156 | -54.4373 | 67.6941 | -54.2587 | -54.7119 | -54.689 | 0.07782 | 67.4927 | -54.483 | 67.6804 | -54.3869 | -54.57 | -54.5334 | 0 | -0.17853 | 0 | 0.17853 | -0.25177 | -0.27466 | -0.25177 | -0.27466 | -0.045776 | -0.20142 | -0.013733 | 0.050354 | -0.09613 | -0.13275 | -0.050354 | -0.086975 | 0.17853 | 122.1313 | 0.09613 | 122.1634 | 121.9528 | 121.9757 | 121.9528 | 121.9299 | -122.1313 | -122.1771 | 122.1313 | 122.1176 | 54.4647 | 54.5151
1116.125 | 122.3236 | -54.2084 | 67.8772 | -0.0060272 | 0.0024845 | 0.058821 | 0.056258 | -0.0053362 | -0.0055563 | -0.0027621 | -0.0051575 | 2.1442e-05 | 0.072151 | 0.068686 | -0.0083825 | 0.01709 | -0.000784 | -0.064087 | 67.6941 | -54.213 | 67.9413 | -54.0115 | -54.4647 | -54.4189 | 0.018311 | 67.7078 | -54.2404 | 67.8955 | -54.1534 | -54.2999 | -54.2816 | -0.004578 | -0.1831 | 0.064087 | 0.19684 | -0.21057 | -0.25635 | -0.20599 | -0.25177 | -0.032043 | -0.16937 | 0.018311 | 0.054932 | -0.073242 | -0.091553 | -0.041199 | -0.05951 | 0.20142 | 122.1542 | 0.086975 | 122.1359 | 121.907 | 121.9482 | 121.9025 | 121.9162 | -122.0901 | -122.1176 | 122.1497 | 122.1039 | 54.1443 | 54.2267
1117.875 | 122.2916 | -53.9474 | 68.1702 | 0.0016023 | 0.0014163 | 0.058607 | 0.05818 | -0.0029864 | -0.0055563 | -0.0016941 | -0.0021057 | 0.0051482 | 0.071724 | 0.073813 | -0.010732 | 0.016663 | -0.0039884 | 0.022888 | 68.0283 | -53.952 | 68.1885 | -53.8193 | -54.2175 | -54.1901 | 0.032043 | 68.0328 | -53.9658 | 68.1427 | -53.9108 | -54.0665 | -54.039 | -0.004577 | -0.14191 | 0.018311 | 0.12817 | -0.24261 | -0.27008 | -0.23804 | -0.2655 | -0.01831 | -0.13733 | -0.027466 | 0.036621 | -0.091552 | -0.11902 | -0.073242 | -0.10071 | 0.13275 | 122.1405 | 0.054931 | 122.1085 | 121.9803 | 121.9986 | 121.9757 | 121.9803 | -122.1222 | -122.1359 | 122.1359 | 122.0901 | 53.9703 | 53.9795
1119.625 | 122.2366 | -53.7643 | 68.3578 | 0.0016023 | 0.0016299 | 0.059248 | 0.056258 | -0.0019184 | -0.0053427 | -0.0038303 | -0.0021057 | 0.0025848 | 0.072792 | 0.063987 | -0.0088097 | 0.017944 | -0.0029202 | 0.004578 | 68.1885 | -53.7827 | 68.3395 | -53.6316 | -54.0665 | -54.0253 | 0.027466 | 68.2022 | -53.8193 | 68.2709 | -53.7735 | -53.9154 | -53.92 | -0.018311 | -0.16937 | -0.01831 | 0.13275 | -0.26093 | -0.30212 | -0.24262 | -0.28381 | -0.054932 | -0.15564 | -0.086975 | -0.009156 | -0.15564 | -0.15106 | -0.10071 | -0.09613 | 0.15106 | 122.1222 | 0.045776 | 122.0901 | 121.9711 | 122.0215 | 121.9528 | 121.9666 | -122.1405 | -122.1771 | 122.1039 | 122.0352 | 53.7689 | 53.7918
1121.3125 | 122.3602 | -53.5263 | 68.5043 | -0.013657 | 0.0022709 | 0.06053 | 0.05818 | -0.0023456 | -0.0044883 | -0.0038303 | -0.0021057 | 2.1442e-05 | 0.070229 | 0.075309 | -0.010519 | 0.018585 | -0.0014248 | -0.041199 | 68.3578 | -53.5721 | 68.6462 | -53.3249 | -53.801 | -53.7415 | 0.054932 | 68.3166 | -53.5721 | 68.605 | -53.4576 | -53.6316 | -53.5904 | -0.045777 | -0.14648 | 0.14191 | 0.20142 | -0.21515 | -0.27466 | -0.16937 | -0.22888 | -0.045777 | -0.18768 | 0.10071 | 0.068664 | -0.064087 | -0.10529 | -0.01831 | -0.059509 | 0.24719 | 122.2183 | 0.11444 | 122.1771 | 121.9299 | 121.8887 | 121.8842 | 121.843 | -122.0764 | -122.0764 | 122.1725 | 122.1313 | 53.4851 | 53.5812
1123.0625 | 122.3557 | -53.1876 | 68.8522 | -0.0060272 | -0.0007199 | 0.056471 | 0.057539 | -0.00042301 | -0.0089743 | -0.0048985 | -0.0051575 | -0.0010468 | 0.070656 | 0.062278 | -0.010305 | 0.019226 | -0.0022794 | -0.018311 | 68.6371 | -53.27 | 68.9117 | -53.0273 | -53.4714 | -53.421 | 0.07782 | 68.6829 | -53.2562 | 68.9072 | -53.1326 | -53.2928 | -53.2654 | -0.082397 | -0.21515 | 0.059509 | 0.16022 | -0.23346 | -0.28381 | -0.15106 | -0.20142 | -0.068665 | -0.16937 | 0.054932 | 0.054932 | -0.07782 | -0.10529 | -0.009155 | -0.036621 | 0.24261 | 122.1817 | 0.1236 | 122.1634 | 121.907 | 121.9391 | 121.8246 | 121.8704 | -122.1222 | -122.1085 | 122.0993 | 122.0947 | 53.1693 | 53.2654
1124.8125 | 122.2458 | -52.9678 | 69.1727 | -0.0060272 | 0.0029117 | 0.06053 | 0.059889 | 4.192e-06 | -0.0059835 | -0.0023349 | -0.0051575 | 0.0032256 | 0.070229 | 0.064414 | -0.0098779 | 0.018799 | 0.0017794 | -0.09613 | 69.0125 | -52.9907 | 69.1315 | -52.9037 | -53.3386 | -53.2608 | -0.073242 | 68.9941 | -52.9907 | 69.1132 | -53.0045 | -53.1647 | -53.0914 | -0.022889 | -0.16022 | -0.041198 | 0.064086 | -0.29297 | -0.37079 | -0.27008 | -0.3479 | -0.022889 | -0.17853 | -0.059509 | -0.036622 | -0.1236 | -0.19684 | -0.10071 | -0.17395 | 0.086975 | 122.1222 | -0.013733 | 122.1039 | 122.0032 | 121.9849 | 121.9803 | 121.962 | -122.1634 | -122.1634 | 122.0993 | 122.081 | 52.8717 | 52.8946
1126.5 | 122.3877 | -52.6794 | 69.3741 | 0.0092313 | -0.0022153 | 0.056898 | 0.055403 | -0.0040546 | -0.0081197 | -0.0034031 | -0.0021057 | 0.0021576 | 0.074501 | 0.069541 | -0.0098779 | 0.015595 | -0.0027066 | 0.041199 | 69.2047 | -52.7069 | 69.5114 | -52.4506 | -52.8717 | -52.8534 | 0.15106 | 69.191 | -52.7206 | 69.4839 | -52.5513 | -52.6932 | -52.7161 | -0.027466 | -0.16937 | 0.13733 | 0.22888 | -0.17395 | -0.19226 | -0.14648 | -0.16479 | -0.041199 | -0.1831 | 0.10986 | 0.12817 | -0.036621 | -0.013733 | 0.004578 | 0.027466 | 0.25635 | 122.2183 | 0.16937 | 122.2046 | 121.9116 | 121.9116 | 121.8842 | 121.8704 | -122.081 | -122.0947 | 122.1909 | 122.1634 | 52.7206 | 52.8305
1128.1875 | 122.2504 | -52.4048 | 69.7357 | -0.021286 | 0.0003483 | 0.059248 | 0.058394 | 0.001286 | -0.0053427 | -0.0012669 | -0.0021057 | 0.0025848 | 0.072151 | 0.063987 | -0.0098779 | 0.019653 | -0.0033474 | -0.004578 | 69.5984 | -52.3819 | 69.7449 | -52.2491 | -52.6749 | -52.6611 | 0.013733 | 69.5618 | -52.4048 | 69.6854 | -52.4139 | -52.5787 | -52.5146 | 0.022888 | -0.13733 | 0.009155 | 0.15564 | -0.25635 | -0.27008 | -0.27924 | -0.29297 | 0 | -0.17395 | -0.050354 | -0.009155 | -0.10986 | -0.17395 | -0.10986 | -0.17395 | 0.13275 | 122.1268 | -0.009155 | 122.0901 | 121.9803 | 121.9666 | 122.0032 | 121.9666 | -122.1176 | -122.1405 | 122.1497 | 122.0901 | 52.4002 | 52.4185
1129.9531 | 122.2412 | -52.0157 | 70.1202 | -0.013657 | 0.0001345 | 0.059035 | 0.056685 | -0.0032 | -0.0089743 | -0.0029759 | -0.0051575 | 0.0017304 | 0.07386 | 0.062064 | -0.0096643 | 0.018372 | -0.0039884 | 0.013733 | 69.9646 | -52.0294 | 70.0836 | -51.915 | -52.3132 | -52.2675 | 0.022888 | 69.9646 | -52.0432 | 70.0424 | -52.0203 | -52.1805 | -52.1347 | -0.013733 | -0.15564 | -0.036621 | 0.10071 | -0.25177 | -0.29755 | -0.23804 | -0.28381 | -0.027466 | -0.15564 | -0.07782 | -0.004578 | -0.11902 | -0.16479 | -0.091553 | -0.13733 | 0.11444 | 122.113 | 0.022888 | 122.0856 | 121.994 | 122.0078 | 121.9803 | 121.9803 | -122.1497 | -122.1634 | 122.0993 | 122.0581 | 52.0294 | 52.0386
1131.7031 | 122.2778 | -51.5533 | 70.546 | 0.0092313 | 0.0046207 | 0.06053 | 0.057326 | -0.0017048 | -0.0083335 | -0.0019077 | 0.0009461 | 0.0038666 | 0.07151 | 0.067832 | -0.0098779 | 0.019653 | -0.002493 | 0.041199 | 70.4086 | -51.5762 | 70.5734 | -51.4206 | -51.8417 | -51.8097 | 0.07782 | 70.3949 | -51.5854 | 70.5368 | -51.535 | -51.709 | -51.6586 | -0.022888 | -0.13733 | 0.027466 | 0.13275 | -0.25635 | -0.28839 | -0.23346 | -0.2655 | -0.032043 | -0.15106 | -0.009155 | 0.018311 | -0.10529 | -0.15564 | -0.073242 | -0.1236 | 0.15564 | 122.1497 | 0.050354 | 122.1222 | 121.9849 | 121.9803 | 121.962 | 121.9482 | -122.1222 | -122.1313 | 122.1268 | 122.0901 | 51.5945 | 51.6312
1133.3906 | 122.319 | -51.3657 | 70.7108 | -0.0060272 | 0.0005619 | 0.06053 | 0.057326 | -0.0027728 | -0.0051291 | -0.0036167 | -0.0021057 | -0.0010468 | 0.073006 | 0.056083 | -0.0094507 | 0.019012 | -0.0029202 | -0.045776 | 70.578 | -51.3702 | 70.7611 | -51.2238 | -51.6449 | -51.5717 | -0.004578 | 70.5276 | -51.3794 | 70.7153 | -51.329 | -51.4755 | -51.4343 | -0.004577 | -0.13275 | 0.050354 | 0.14191 | -0.20599 | -0.27923 | -0.20142 | -0.27466 | -0.013733 | -0.1831 | 0.004578 | 0.036621 | -0.068664 | -0.10986 | -0.054931 | -0.09613 | 0.14648 | 122.1313 | 0.050354 | 122.0947 | 121.9482 | 121.907 | 121.9437 | 121.8933 | -122.081 | -122.0901 | 122.1268 | 122.081 | 51.3199 | 51.3611
1135.1406 | 122.3419 | -51.0223 | 71.0083 | -0.0060272 | 0.0044071 | 0.058821 | 0.058394 | -0.0010638 | -0.0053427 | -0.0021213 | -0.0082093 | 0.003012 | 0.072151 | 0.068686 | -0.012228 | 0.020294 | -0.0022794 | -0.082397 | 70.9305 | -51.0818 | 71.0632 | -50.9125 | -51.3611 | -51.3062 | -0.009155 | 70.8847 | -51.0956 | 71.0999 | -51.004 | -51.1597 | -51.1185 | -0.059509 | -0.07782 | 0.054931 | 0.10986 | -0.28381 | -0.33874 | -0.2243 | -0.27924 | -0.073242 | -0.1236 | 0.091553 | 0.018311 | -0.09613 | -0.13733 | -0.022888 | -0.064087 | 0.16937 | 122.1451 | 0.091553 | 122.1954 | 122.0123 | 121.9803 | 121.9528 | 121.907 | -122.0901 | -122.1039 | 122.0856 | 122.1222 | 50.9399 | 51.0132
1136.8906 | 122.3511 | -50.6653 | 71.4203 | 0.0016023 | 0.0001345 | 0.057967 | 0.056685 | -0.0034136 | -0.0055563 | -0.00019867 | 0.0009461 | 0.0021576 | 0.072365 | 0.059501 | -0.0094507 | 0.017517 | -0.0018522 | 0.10071 | 71.228 | -50.6699 | 71.5393 | -50.4501 | -50.8759 | -50.8392 | 0.15564 | 71.2646 | -50.6927 | 71.4752 | -50.5783 | -50.7248 | -50.7156 | -0.004578 | -0.19226 | 0.11902 | 0.21515 | -0.17395 | -0.21057 | -0.16937 | -0.20599 | -0.027466 | -0.15564 | 0.054932 | 0.086975 | -0.050354 | -0.059509 | -0.022888 | -0.032043 | 0.21973 | 122.2092 | 0.11444 | 122.168 | 121.8979 | 121.9574 | 121.8933 | 121.9299 | -122.0901 | -122.113 | 122.2046 | 122.1405 | 50.766 | 50.8209
1138.6406 | 122.3099 | -50.267 | 71.8094 | -0.013657 | 0.0005619 | 0.057753 | 0.056685 | -0.0042682 | -0.0072653 | -0.0029759 | -0.0082093 | 0.0021576 | 0.070442 | 0.060569 | -0.010732 | 0.018585 | -0.003561 | 0.091553 | 71.6263 | -50.2991 | 71.9147 | -50.0931 | -50.4959 | -50.4501 | 0.13275 | 71.6675 | -50.3128 | 71.8231 | -50.235 | -50.3906 | -50.3815 | -0.032043 | -0.1831 | 0.10529 | 0.17395 | -0.1831 | -0.22888 | -0.15106 | -0.19684 | -0.045776 | -0.14191 | 0.013733 | 0.032044 | -0.11444 | -0.1236 | -0.068665 | -0.07782 | 0.20599 | 122.2137 | 0.07782 | 122.1359 | 121.9254 | 121.9803 | 121.8933 | 121.9345 | -122.1085 | -122.1222 | 122.1817 | 122.0901 | 50.3586 | 50.3998
1140.3281 | 122.2458 | -49.9466 | 72.1893 | -0.013657 | -0.0013607 | 0.059035 | 0.057753 | 0.00085879 | -0.0089743 | -0.0016941 | -0.0051575 | 0.003012 | 0.073219 | 0.068259 | -0.010305 | 0.019012 | -0.0009976 | 0.032043 | 72.02 | -49.9878 | 72.1436 | -49.8779 | -50.267 | -50.2396 | 0.013733 | 72.0108 | -49.9924 | 72.0932 | -49.9649 | -50.1251 | -50.0793 | -0.041199 | -0.16937 | -0.045776 | 0.068664 | -0.29297 | -0.32044 | -0.25177 | -0.27924 | -0.045777 | -0.17853 | -0.09613 | -0.018311 | -0.13275 | -0.17853 | -0.086975 | -0.13275 | 0.10986 | 122.1313 | 0.027466 | 122.0856 | 122.0078 | 122.0032 | 121.9666 | 121.9574 | -122.1771 | -122.1817 | 122.0901 | 122.0398 | 49.9786 | 49.9603
1142.0625 | 122.2275 | -49.5163 | 72.6196 | -0.0060272 | 0.0033389 | 0.060103 | 0.060103 | -0.0029864 | -0.0044883 | -0.0029759 | -0.0021057 | 0.001944 | 0.071297 | 0.067618 | -0.0092371 | 0.017517 | -0.0003568 | -0.050354 | 72.4686 | -49.5117 | 72.5739 | -49.4888 | -49.8962 | -49.8413 | -0.09613 | 72.4548 | -49.5483 | 72.5327 | -49.5758 | -49.736 | -49.6674 | 0.004577 | -0.15106 | -0.045776 | 0.027465 | -0.32501 | -0.37994 | -0.32959 | -0.38452 | -0.032044 | -0.16479 | -0.086975 | -0.05951 | -0.15106 | -0.21973 | -0.11902 | -0.18768 | 0.022888 | 122.0856 | -0.027466 | 122.081 | 121.9803 | 122.0032 | 121.9849 | 121.9711 | -122.1313 | -122.168 | 122.0901 | 122.0489 | 49.4659 | 49.4202
1143.8125 | 122.319 | -48.9441 | 73.114 | -0.0060272 | 0.0026981 | 0.058821 | 0.05583 | -0.0012774 | -0.0055563 | -0.0029759 | -0.0051575 | 0.0010894 | 0.073219 | 0.056083 | -0.0079553 | 0.018799 | 0.0002842 | -0.050354 | 72.963 | -48.967 | 73.2056 | -48.7976 | -49.2371 | -49.1913 | 0.054932 | 72.9355 | -48.999 | 73.1506 | -48.9349 | -49.0677 | -49.0402 | -0.022888 | -0.15106 | 0.091552 | 0.14648 | -0.24719 | -0.29297 | -0.2243 | -0.27008 | -0.054931 | -0.17853 | 0.036621 | 0.009155 | -0.09613 | -0.1236 | -0.041199 | -0.068665 | 0.16937 | 122.1725 | 0.064086 | 122.1497 | 121.9299 | 121.9345 | 121.907 | 121.8796 | -122.081 | -122.113 | 122.1497 | 122.0947 | 48.8937 | 48.999
1145.5625 | 122.2412 | -48.4955 | 73.6816 | -0.013657 | 0.0029117 | 0.060316 | 0.059035 | -0.0012774 | -0.0059835 | -0.0019077 | -0.0051575 | 0.0032256 | 0.073433 | 0.065696 | -0.0096643 | 0.019867 | -0.0020658 | -0.086975 | 73.5123 | -48.4909 | 73.6084 | -48.4314 | -48.8434 | -48.7839 | -0.068665 | 73.5077 | -48.4955 | 73.5764 | -48.5367 | -48.7015 | -48.6237 | 0.004577 | -0.16937 | -0.073243 | 0.064087 | -0.28839 | -0.3479 | -0.29297 | -0.35248 | 0 | -0.17395 | -0.10529 | -0.041199 | -0.12817 | -0.20599 | -0.12817 | -0.20599 | 0.05951 | 122.0993 | -0.041199 | 122.0718 | 122.0032 | 122.0032 | 122.0078 | 122.0032 | -122.1725 | -122.1771 | 122.1039 | 122.0718 | 48.4085 | 48.4268
1147.25 | 122.2321 | -47.9462 | 74.231 | -0.013657 | 0.0044071 | 0.059462 | 0.058821 | -0.00063661 | -0.0066245 | -0.0019077 | -0.0082093 | 0.0049346 | 0.073219 | 0.071463 | -0.010305 | 0.020508 | 0.000925 | -0.068665 | 74.0479 | -47.9324 | 74.1623 | -47.8683 | -48.3032 | -48.2391 | -0.041199 | 74.0204 | -47.9599 | 74.1257 | -47.9919 | -48.1293 | -48.0743 | 0.013733 | -0.1831 | -0.068665 | 0.07782 | -0.29297 | -0.35706 | -0.3067 | -0.37079 | -0.013733 | -0.21057 | -0.10529 | -0.045776 | -0.12817 | -0.1831 | -0.11444 | -0.16937 | 0.064087 | 122.0947 | -0.032043 | 122.0856 | 121.9803 | 121.9803 | 121.994 | 121.9666 | -122.1634 | -122.1909 | 122.1085 | 122.0718 | 47.8775 | 47.905
1148.9844 | 122.2275 | -47.4289 | 74.7162 | 0.0016023 | 0.0031253 | 0.059676 | 0.059889 | 0.0057722 | -0.0068381 | -0.0014805 | -0.0082093 | 0.005362 | 0.073433 | 0.066977 | -0.010519 | 0.01944 | -0.0003568 | -0.068665 | 74.5926 | -47.4335 | 74.6475 | -47.4106 | -47.7951 | -47.731 | -0.064087 | 74.5514 | -47.4609 | 74.6384 | -47.493 | -47.644 | -47.5708 | -0.004578 | -0.1236 | -0.068665 | 0.018311 | -0.30212 | -0.36621 | -0.29755 | -0.36163 | -0.032043 | -0.16479 | -0.07782 | -0.064087 | -0.14191 | -0.21515 | -0.10986 | -0.18311 | 0.022889 | 122.081 | -0.032044 | 122.0993 | 122.0261 | 122.0123 | 122.0215 | 121.9803 | -122.1497 | -122.1771 | 122.0764 | 122.0673 | 47.3602 | 47.3648
1150.7344 | 122.2733 | -46.7743 | 75.3616 | 0.0016023 | 0.0005619 | 0.059462 | 0.054976 | -0.002132 | -0.0072653 | -0.0044711 | -0.0051575 | 0.00023504 | 0.072365 | 0.061637 | -0.0098779 | 0.017303 | -0.0048428 | 0.086975 | 75.1694 | -46.756 | 75.4395 | -46.6049 | -46.9803 | -46.962 | 0.13275 | 75.1923 | -46.7606 | 75.3387 | -46.7331 | -46.8796 | -46.8521 | 0.018311 | -0.19226 | 0.07782 | 0.16937 | -0.18768 | -0.20599 | -0.20599 | -0.22431 | 0.013733 | -0.16937 | -0.022888 | 0.041199 | -0.07782 | -0.10529 | -0.091553 | -0.11902 | 0.15106 | 122.1954 | 0.027466 | 122.0993 | 121.9254 | 121.9528 | 121.9437 | 121.9666 | -122.1176 | -122.1222 | 122.2137 | 122.113 | 46.8613 | 46.907
1152.4219 | 122.3602 | -46.1288 | 75.9247 | -0.021286 | 0.0007755 | 0.060957 | 0.059248 | 0.001286 | -0.0051291 | -0.00083947 | -0.0021057 | 0.001303 | 0.070442 | 0.065055 | -0.0094507 | 0.018799 | -0.0044156 | -0.013733 | 75.7553 | -46.1426 | 76.0483 | -46.0007 | -46.4172 | -46.3623 | 0.09613 | 75.7324 | -46.1517 | 76.0025 | -46.0968 | -46.2479 | -46.2021 | -0.013733 | -0.16937 | 0.1236 | 0.12817 | -0.23346 | -0.28839 | -0.21973 | -0.27466 | -0.022888 | -0.19226 | 0.077819 | 0.032043 | -0.073242 | -0.11902 | -0.050354 | -0.096131 | 0.14191 | 122.1909 | 0.054931 | 122.1542 | 121.8979 | 121.8842 | 121.8842 | 121.8613 | -122.0673 | -122.0764 | 122.1771 | 122.1313 | 46.1151 | 46.225
1154.1094 | 122.2321 | -45.5978 | 76.5335 | -0.0060272 | 0.0059025 | 0.058821 | 0.06288 | -0.0017048 | -0.0053427 | -0.0031895 | -0.0051575 | 0.003012 | 0.072578 | 0.06655 | -0.011587 | 0.019226 | 0.0011386 | -0.009155 | 76.387 | -45.5978 | 76.506 | -45.5612 | -45.9595 | -45.9274 | -0.027466 | 76.3687 | -45.6482 | 76.4328 | -45.6848 | -45.8359 | -45.7626 | 0 | -0.14648 | -0.027466 | 0.036621 | -0.32959 | -0.36163 | -0.32959 | -0.36163 | -0.050354 | -0.16479 | -0.10071 | -0.086975 | -0.16479 | -0.23804 | -0.11444 | -0.18768 | 0.036621 | 122.1039 | -0.036621 | 122.081 | 121.9849 | 122.0169 | 121.9849 | 121.9666 | -122.1313 | -122.1817 | 122.1039 | 122.0306 | 45.5887 | 45.5704
1155.8594 | 122.3465 | -44.8883 | 77.1927 | -0.0060272 | 0.0029117 | 0.058607 | 0.058821 | 0.00043159 | -0.0055563 | -0.0036167 | -0.0021057 | 0.001944 | 0.073433 | 0.068686 | -0.0098779 | 0.016876 | 0.0015658 | -0.073242 | 77.0737 | -44.9066 | 77.2202 | -44.8334 | -45.2408 | -45.1813 | 0.045776 | 77.0325 | -44.9249 | 77.2339 | -44.8746 | -45.0394 | -44.957 | -0.01831 | -0.11902 | 0.027466 | 0.054932 | -0.29297 | -0.35248 | -0.27466 | -0.33417 | -0.036621 | -0.16022 | 0.041199 | 0.013733 | -0.068664 | -0.15106 | -0.032043 | -0.11444 | 0.073242 | 122.1268 | 0.050354 | 122.1588 | 121.9803 | 121.9574 | 121.962 | 121.9208 | -122.0993 | -122.1176 | 122.1085 | 122.1222 | 44.8151 | 44.9341
1157.6094 | 122.3373 | -44.101 | 78.0304 | -0.0060272 | -0.0017881 | 0.056471 | 0.056258 | -0.00085021 | -0.0064109 | -0.0031895 | 0.0009461 | -0.0010468 | 0.071724 | 0.058646 | -0.0094507 | 0.018158 | -0.0033474 | 0.091553 | 77.7969 | -44.1238 | 78.0991 | -43.9407 | -44.3344 | -44.3024 | 0.16937 | 77.8015 | -44.1422 | 78.0212 | -44.0735 | -44.2017 | -44.1879 | -0.022888 | -0.23346 | 0.068664 | 0.16022 | -0.20142 | -0.23346 | -0.17853 | -0.21057 | -0.041199 | -0.22888 | -0.009156 | 0.027466 | -0.086975 | -0.10071 | -0.045776 | -0.059509 | 0.18311 | 122.2229 | 0.068665 | 122.1634 | 121.9208 | 121.9437 | 121.8979 | 121.9025 | -122.1542 | -122.1725 | 122.2 | 122.1222 | 44.1925 | 44.2703
1159.2969 | 122.3236 | -43.309 | 78.7811 | 0.0016023 | -0.0007199 | 0.056044 | 0.057326 | -0.001491 | -0.0053427 | -0.0029759 | -0.0051575 | 0.0032256 | 0.071083 | 0.061209 | -0.0094507 | 0.017303 | -0.0020658 | -0.027466 | 78.6118 | -43.3228 | 78.8177 | -43.2358 | -43.6249 | -43.5608 | 0.041199 | 78.6118 | -43.3182 | 78.772 | -43.3136 | -43.4509 | -43.4097 | -0.013733 | -0.16937 | 0.036621 | 0.073242 | -0.25177 | -0.31586 | -0.23804 | -0.30212 | -0.009155 | -0.16937 | -0.009155 | -0.004578 | -0.10071 | -0.14191 | -0.091553 | -0.13275 | 0.086975 | 122.1405 | 0.004577 | 122.0901 | 121.9345 | 121.9299 | 121.9208 | 121.9208 | -122.1039 | -122.0993 | 122.1268 | 122.081 | 43.2816 | 43.3502
1161.0625 | 122.3557 | -42.2928 | 79.7745 | -0.0060272 | 0.0012027 | 0.059676 | 0.056898 | -0.00063661 | -0.0053427 | 0.0012967 | -0.0021057 | 0.0032256 | 0.06916 | 0.058646 | -0.010519 | 0.020294 | -0.0037748 | -0.064087 | 79.6646 | -42.3248 | 79.8294 | -42.2424 | -42.6086 | -42.5674 | 0.064087 | 79.6005 | -42.3523 | 79.8294 | -42.2974 | -42.4393 | -42.3614 | -0.032043 | -0.10986 | 0.054932 | 0.050354 | -0.27466 | -0.31586 | -0.24262 | -0.28381 | -0.059509 | -0.17395 | 0.054932 | -0.004577 | -0.068664 | -0.14648 | -0.009155 | -0.086975 | 0.082397 | 122.1542 | 0.054932 | 122.1817 | 121.9894 | 121.9528 | 121.9574 | 121.8933 | -122.0993 | -122.1268 | 122.1222 | 122.1222 | 42.2287 | 42.3569
1162.8125 | 122.319 | -41.2582 | 80.8411 | -0.013657 | -0.0005063 | 0.058394 | 0.057326 | 0.0019268 | -0.0061971 | -0.0019077 | -0.0051575 | 0.0015166 | 0.071083 | 0.060569 | -0.010732 | 0.017517 | -0.0046292 | -0.027466 | 80.6763 | -41.2766 | 80.8594 | -41.2125 | -41.5878 | -41.5512 | 0.064087 | 80.6488 | -41.2857 | 80.8136 | -41.2994 | -41.423 | -41.3681 | -0.01831 | -0.16479 | 0.018311 | 0.045777 | -0.29297 | -0.32959 | -0.27466 | -0.31128 | -0.027466 | -0.19226 | -0.027465 | -0.041198 | -0.10986 | -0.16479 | -0.082397 | -0.13733 | 0.064087 | 122.1359 | -0.013732 | 122.0993 | 121.9528 | 121.9345 | 121.9345 | 121.907 | -122.1176 | -122.1268 | 122.1176 | 122.0718 | 41.2308 | 41.3223
1164.5781 | 122.2092 | -40.2832 | 81.8802 | -0.0060272 | 0.0035525 | 0.059889 | 0.06053 | -0.0032 | -0.0042745 | -0.0034031 | -0.0021057 | 0.0025848 | 0.075569 | 0.063773 | -0.012014 | 0.017303 | 0.0004978 | -0.022888 | 81.7429 | -40.2786 | 81.8024 | -40.3198 | -40.6769 | -40.6265 | -0.018311 | 81.7245 | -40.2878 | 81.7749 | -40.3839 | -40.5167 | -40.4205 | 0.004578 | -0.13733 | -0.07782 | -0.036621 | -0.34332 | -0.39368 | -0.3479 | -0.39825 | -0.004578 | -0.15564 | -0.10529 | -0.10071 | -0.13733 | -0.23346 | -0.13275 | -0.22888 | -0.041199 | 122.081 | -0.09613 | 122.0627 | 122.0215 | 122.0123 | 122.0261 | 122.0078 | -122.1588 | -122.168 | 122.0856 | 122.0581 | 40.2603 | 40.2649
1166.2656 | 122.2504 | -39.3036 | 82.8598 | -0.0060272 | 0.0020571 | 0.059248 | 0.058607 | 0.0017132 | -0.0087607 | -0.00019867 | -0.0051575 | 0.003012 | 0.070015 | 0.064627 | -0.011801 | 0.01944 | -0.0022794 | 0.036621 | 82.6904 | -39.3173 | 82.8415 | -39.2441 | -39.6149 | -39.5828 | 0.09613 | 82.695 | -39.3036 | 82.7774 | -39.3448 | -39.5142 | -39.4363 | -0.013733 | -0.16937 | -0.01831 | 0.059509 | -0.27924 | -0.31128 | -0.2655 | -0.29755 | 0 | -0.16479 | -0.082397 | -0.041199 | -0.13275 | -0.21057 | -0.13275 | -0.21057 | 0.073242 | 122.1588 | -0.041199 | 122.081 | 122.0078 | 121.9986 | 121.994 | 121.9986 | -122.1771 | -122.1634 | 122.1451 | 122.081 | 39.3402 | 39.3997
1168.0156 | 122.2778 | -38.1775 | 83.9905 | -0.013657 | -0.0005063 | 0.059462 | 0.058394 | -0.00020941 | -0.0070517 | -0.0038303 | -0.0082093 | 0.0042938 | 0.070656 | 0.066336 | -0.010732 | 0.018372 | -0.0022794 | 0.068665 | 83.8348 | -38.1821 | 83.9218 | -38.1866 | -38.5162 | -38.4705 | 0.091553 | 83.8074 | -38.2004 | 83.8943 | -38.2233 | -38.3743 | -38.3194 | -0.004578 | -0.15564 | -0.068665 | -0.009156 | -0.29297 | -0.33875 | -0.28839 | -0.33417 | -0.022888 | -0.18311 | -0.096131 | -0.045777 | -0.14191 | -0.19684 | -0.11902 | -0.17395 | -0.004578 | 122.1039 | -0.022889 | 122.0947 | 122.0169 | 122.0078 | 122.0123 | 121.9849 | -122.1725 | -122.1909 | 122.0993 | 122.0718 | 38.2462 | 38.269
1169.75 | 122.2183 | -37.0743 | 85.1074 | -0.013657 | 0.0046207 | 0.058607 | 0.058607 | 0.0010724 | -0.0059835 | -0.0036167 | -0.0082093 | 0.0025848 | 0.073006 | 0.068686 | -0.0098779 | 0.017517 | -0.0016384 | -0.041199 | 84.9335 | -37.0789 | 84.9792 | -37.1246 | -37.4725 | -37.4039 | -0.013733 | 84.906 | -37.1063 | 84.9655 | -37.1979 | -37.3169 | -37.2391 | -0.004577 | -0.17395 | -0.12817 | -0.050354 | -0.32959 | -0.39825 | -0.32501 | -0.39368 | -0.032043 | -0.20142 | -0.14191 | -0.1236 | -0.16479 | -0.24262 | -0.13275 | -0.21057 | -0.045777 | 122.0581 | -0.091553 | 122.0718 | 122.0123 | 122.0123 | 122.0078 | 121.9803 | -122.1863 | -122.2137 | 122.0535 | 122.0398 | 37.0331 | 37.0605
1171.4531 | 122.2275 | -35.9573 | 86.2244 | -0.0060272 | 0.0003483 | 0.058394 | 0.057326 | -0.00063661 | -0.0072653 | -0.0021213 | 0.0009461 | 0.003653 | 0.072578 | 0.066336 | -0.0094507 | 0.017944 | -0.0005704 | 0.068665 | 86.0321 | -35.9573 | 86.1511 | -35.9344 | -36.2732 | -36.2457 | 0.10071 | 86.0275 | -35.9665 | 86.0779 | -36.0306 | -36.1588 | -36.1404 | 0 | -0.19226 | -0.073242 | 0.022888 | -0.28839 | -0.31586 | -0.28839 | -0.31586 | -0.009156 | -0.19684 | -0.14648 | -0.073243 | -0.18311 | -0.20142 | -0.17395 | -0.19226 | 0.022888 | 122.1085 | -0.064087 | 122.0444 | 121.9894 | 121.994 | 121.9894 | 121.9849 | -122.1817 | -122.1909 | 122.1085 | 122.0352 | 36.026 | 36.058
1173.1875 | 122.3236 | -34.8816 | 87.2406 | -0.0060272 | 0.0020571 | 0.057967 | 0.058821 | 0.0014996 | -0.0068381 | -0.0019077 | -0.0021057 | 0.00066224 | 0.072365 | 0.059928 | -0.0094507 | 0.018585 | -0.0033474 | -0.009155 | 87.0209 | -34.8907 | 87.2543 | -34.8221 | -35.1929 | -35.1517 | 0.10529 | 87.0255 | -34.8953 | 87.1902 | -34.9319 | -35.0418 | -35.0052 | -0.009155 | -0.21973 | 0.013732 | 0.059509 | -0.27008 | -0.31128 | -0.26093 | -0.30212 | -0.013733 | -0.21515 | -0.050354 | -0.050354 | -0.1236 | -0.16022 | -0.10986 | -0.14648 | 0.068664 | 122.1451 | -0.036621 | 122.0856 | 121.9116 | 121.9208 | 121.9025 | 121.907 | -122.1313 | -122.1359 | 122.1359 | 122.0718 | 34.8724 | 34.9869
1174.9219 | 122.3557 | -29.6402 | 92.5003 | -0.013657 | 0.0033389 | 0.055617 | 0.055617 | -0.00085021 | -0.0066245 | -0.0014805 | -0.0051575 | 2.1442e-05 | 0.072578 | 0.069541 | -0.010305 | 0.017517 | 0.0002842 | 0.29297 | 92.2668 | -29.6906 | 92.4912 | -29.6036 | -29.9103 | -29.8553 | 0.46692 | 92.2577 | -29.6768 | 92.4912 | -29.6173 | -29.7226 | -29.7134 | -0.050354 | -0.23346 | -0.009155 | 0.036621 | -0.21515 | -0.27008 | -0.16479 | -0.21973 | -0.036621 | -0.24262 | -0.009155 | 0.022888 | -0.073242 | -0.082397 | -0.036621 | -0.045776 | 0.086975 | 122.1817 | 0.059509 | 122.168 | 121.9574 | 121.9345 | 121.907 | 121.8979 | -122.1909 | -122.1771 | 122.1313 | 122.1313 | 29.9332 | 30.1071
1176.7031 | 122.1909 | -20.6772 | 101.5778 | 0.0016023 | -0.0002927 | 0.057967 | 0.055617 | -0.00020941 | -0.0066245 | -0.0025485 | 0.0009461 | 0.0038666 | 0.068947 | 0.071891 | -0.012014 | 0.01709 | -0.0029202 | 0.16479 | 101.3718 | -20.6223 | 101.4816 | -20.6589 | -20.9061 | -20.8694 | 0.20142 | 101.3718 | -20.6177 | 101.3855 | -20.6955 | -20.8008 | -20.8054 | 0.054932 | -0.20599 | -0.096131 | 0.01831 | -0.19226 | -0.22888 | -0.24719 | -0.28381 | 0.059509 | -0.20599 | -0.19226 | -0.018311 | -0.12817 | -0.1236 | -0.18768 | -0.18311 | -0.036622 | 122.1039 | -0.07782 | 122.0032 | 121.994 | 121.9894 | 122.0489 | 122.0489 | -122.2 | -122.1954 | 122.1588 | 122.0627 | 20.842 | 20.8786
1178.3906 | 122.3419 | -19.0521 | 103.1021 | -0.013657 | 0.0005619 | 0.05818 | 0.05284 | 4.192e-06 | -0.0055563 | -0.0021213 | -0.0051575 | 0.0023712 | 0.070869 | 0.057792 | -0.01116 | 0.016876 | -0.00527 | 0.18768 | 102.9099 | -19.075 | 103.1525 | -18.9789 | -19.2078 | -19.2032 | 0.32959 | 102.8732 | -19.0521 | 103.038 | -18.988 | -19.1025 | -19.1025 | -0.022888 | -0.19226 | 0.050354 | 0.073242 | -0.15106 | -0.15564 | -0.12817 | -0.13275 | 0 | -0.22888 | -0.064087 | 0.064087 | -0.050354 | -0.050354 | -0.050354 | -0.050354 | 0.09613 | 122.2275 | 0.064087 | 122.0901 | 121.9849 | 121.9254 | 121.962 | 121.9254 | -122.1771 | -122.1542 | 122.2046 | 122.0901 | 19.2398 | 19.3817
1180.1406 | 122.3099 | -17.8711 | 104.2648 | -0.013657 | 0.0035525 | 0.057539 | 0.054976 | 0.0023542 | -0.0072653 | -0.0042575 | -0.0051575 | 0.0025848 | 0.070869 | 0.058432 | -0.012869 | 0.019226 | -0.0018522 | 0.054932 | 104.0955 | -17.8894 | 104.2694 | -17.8482 | -18.1 | -18.0588 | 0.21973 | 104.0817 | -17.8757 | 104.1916 | -17.8894 | -17.9855 | -17.9626 | -0.01831 | -0.16937 | 0.004577 | 0.022888 | -0.18768 | -0.22888 | -0.16937 | -0.21057 | -0.004577 | -0.18311 | -0.073243 | -0.01831 | -0.091552 | -0.11444 | -0.086975 | -0.10986 | 0.041198 | 122.1588 | -0.013733 | 122.0673 | 121.9849 | 121.9574 | 121.9666 | 121.9528 | -122.1542 | -122.1405 | 122.1405 | 122.0627 | 17.926 | 18.0908
1181.875 | 122.3099 | -17.0151 | 105.162 | 0.0016023 | -7.9104e-05 | 0.058394 | 0.054976 | -0.0059772 | -0.0079061 | -0.0044711 | -0.0021057 | 0.0032256 | 0.073006 | 0.058646 | -0.0098779 | 0.017731 | -0.005911 | 0.17395 | 104.924 | -17.0105 | 105.1529 | -16.9693 | -17.1844 | -17.1616 | 0.3067 | 104.9377 | -17.0334 | 105.0659 | -16.983 | -17.0975 | -17.0883 | 0.004578 | -0.23804 | -0.009155 | 0.045777 | -0.14648 | -0.16937 | -0.15106 | -0.17395 | -0.01831 | -0.2243 | -0.09613 | 0.032044 | -0.073242 | -0.082397 | -0.054932 | -0.064087 | 0.041199 | 122.1634 | 0.050354 | 122.0993 | 121.9345 | 121.9711 | 121.9391 | 121.9528 | -122.1725 | -122.1954 | 122.168 | 122.081 | 17.189 | 17.3218
1183.625 | 122.319 | -16.3925 | 105.7571 | -0.0060272 | 0.0031253 | 0.058394 | 0.060103 | -0.0012774 | -0.0044883 | -0.0046847 | -0.0021057 | 0.0027984 | 0.073647 | 0.066123 | -0.010732 | 0.016663 | -0.0012112 | -0.004578 | 105.629 | -16.3971 | 105.6976 | -16.4337 | -16.6626 | -16.6214 | 0.15564 | 105.574 | -16.4154 | 105.6885 | -16.3834 | -16.4932 | -16.4612 | -0.004578 | -0.12817 | -0.059509 | -0.041199 | -0.22888 | -0.27008 | -0.2243 | -0.2655 | -0.022888 | -0.1831 | -0.068664 | 0.009155 | -0.068665 | -0.10071 | -0.045777 | -0.07782 | -0.036621 | 122.0947 | 0.032043 | 122.1039 | 122.0261 | 121.9894 | 122.0215 | 121.9666 | -122.1542 | -122.1725 | 122.0901 | 122.081 | 16.3879 | 16.5482
1185.3594 | 122.3236 | -15.9485 | 106.2286 | 0.0016023 | 0.0029117 | 0.056898 | 0.06053 | -0.0012774 | -0.0059835 | -0.0048985 | -0.0051575 | 0.0023712 | 0.070656 | 0.062278 | -0.010732 | 0.019653 | -0.00527 | -0.013733 | 106.1005 | -15.9393 | 106.1691 | -15.9943 | -16.1819 | -16.1362 | 0.16479 | 106.0547 | -15.9439 | 106.1646 | -15.9119 | -16.0355 | -15.9851 | 0.009155 | -0.12817 | -0.05951 | -0.045777 | -0.18768 | -0.23346 | -0.19684 | -0.24262 | 0.004577 | -0.17395 | -0.064087 | 0.036621 | -0.036621 | -0.086975 | -0.041198 | -0.091552 | -0.054932 | 122.1085 | 0.032044 | 122.1085 | 122.0398 | 121.9986 | 122.049 | 122.0032 | -122.168 | -122.1725 | 122.1176 | 122.113 | 15.9348 | 16.1133
1187.0469 | 122.374 | -15.3534 | 106.8054 | -0.0060272 | -0.0005063 | 0.057753 | 0.053908 | 4.192e-06 | -0.0070517 | -0.0019077 | -0.0021057 | 0.0010894 | 0.070869 | 0.065482 | -0.011373 | 0.018372 | -0.000784 | 0.11902 | 106.6315 | -15.3534 | 106.8512 | -15.2573 | -15.477 | -15.4633 | 0.32959 | 106.6177 | -15.3488 | 106.7642 | -15.2435 | -15.358 | -15.3534 | 0 | -0.17395 | 0.045776 | 0.096131 | -0.10986 | -0.1236 | -0.10986 | -0.1236 | 0.004578 | -0.18768 | -0.041199 | 0.10986 | 0 | -0.004577 | -0.004578 | -0.009155 | 0.096131 | 122.2046 | 0.10529 | 122.113 | 121.9849 | 121.9666 | 121.9849 | 121.9711 | -122.1588 | -122.1542 | 122.2046 | 122.1176 | 15.4724 | 15.683
1188.7812 | 122.2504 | -14.9414 | 107.2952 | 0.0016023 | 0.0001345 | 0.057539 | 0.057539 | 0.004704 | -0.0044883 | -0.0010531 | -0.0021057 | 0.0034392 | 0.070656 | 0.062918 | -0.012441 | 0.017944 | -0.0012112 | 0.11902 | 107.1121 | -14.9323 | 107.2083 | -14.946 | -15.1245 | -15.097 | 0.21515 | 107.1167 | -14.9231 | 107.1304 | -14.9185 | -15.033 | -14.9918 | 0.009155 | -0.1831 | -0.086975 | -0.004578 | -0.15564 | -0.18311 | -0.16479 | -0.19226 | 0.01831 | -0.17853 | -0.16479 | 0.022888 | -0.050354 | -0.091553 | -0.068664 | -0.10986 | -0.013733 | 122.1405 | 0.004578 | 122.0535 | 122.0444 | 122.0398 | 122.0535 | 122.0581 | -122.2275 | -122.2183 | 122.1497 | 122.0718 | 15.0604 | 15.1566
1190.5312 | 122.2412 | -14.534 | 107.6935 | 0.0092313 | 0.0001345 | 0.056258 | 0.054335 | -0.00063661 | -0.0072653 | -0.0034031 | 0.0009461 | 0.0032256 | 0.071724 | 0.061423 | -0.010305 | 0.018799 | -0.0020658 | 0.15106 | 107.5058 | -14.4974 | 107.6248 | -14.4928 | -14.6942 | -14.6713 | 0.23804 | 107.515 | -14.5065 | 107.5058 | -14.5203 | -14.6347 | -14.6301 | 0.036622 | -0.18768 | -0.068664 | 0.041199 | -0.13733 | -0.16022 | -0.17395 | -0.19684 | 0.027466 | -0.17853 | -0.18768 | 0.013733 | -0.09613 | -0.10071 | -0.1236 | -0.12817 | 0.004577 | 122.1222 | -0.013733 | 122.0123 | 122.0032 | 122.0215 | 122.0398 | 122.049 | -122.1909 | -122.2 | 122.1588 | 122.0398 | 14.6851 | 14.772
1192.2188 | 122.3557 | -14.1449 | 108.0231 | -0.0060272 | -0.0009335 | 0.057326 | 0.056685 | -0.0017048 | -0.0066245 | -0.0048985 | -0.0051575 | 0.00023504 | 0.070229 | 0.055442 | -0.0092371 | 0.018799 | -0.004202 | 0.064087 | 107.8125 | -14.1678 | 108.0002 | -14.1037 | -14.3234 | -14.2548 | 0.23804 | 107.8125 | -14.1586 | 107.9498 | -14.0625 | -14.1586 | -14.1769 | -0.022889 | -0.21057 | -0.022888 | 0.041198 | -0.10986 | -0.17853 | -0.086975 | -0.15564 | -0.013733 | -0.21057 | -0.073242 | 0.082397 | -0.032044 | -0.013733 | -0.018311 | 0 | 0.064087 | 122.168 | 0.09613 | 122.1085 | 121.9803 | 121.9711 | 121.9574 | 121.9574 | -122.1909 | -122.1817 | 122.1451 | 122.0947 | 14.209 | 14.3829
1193.9688 | 122.3648 | -13.8977 | 108.2428 | 0.0016023 | -0.0009335 | 0.057753 | 0.056258 | -0.0017048 | -0.0081197 | -0.0014805 | -0.0051575 | -0.0010468 | 0.069374 | 0.059714 | -0.0083825 | 0.020935 | -0.0037748 | 0.086975 | 108.0917 | -13.8886 | 108.2886 | -13.8153 | -13.9984 | -13.9801 | 0.28839 | 108.0597 | -13.8886 | 108.2382 | -13.7741 | -13.8886 | -13.8977 | 0.009155 | -0.15106 | 0.045776 | 0.082397 | -0.082398 | -0.10071 | -0.091553 | -0.10986 | 0.009155 | -0.18311 | -0.004578 | 0.1236 | 0 | 0.009155 | -0.009155 | 0 | 0.073242 | 122.1771 | 0.11444 | 122.1268 | 121.9803 | 121.9482 | 121.9894 | 121.9574 | -122.1313 | -122.1313 | 122.1863 | 122.1359 | 13.9847 | 14.1861
1195.7344 | 122.3419 | -13.4583 | 108.6868 | -0.0060272 | -0.0005063 | 0.057326 | 0.058394 | -0.0025592 | -0.0061971 | -0.0010531 | -0.0021057 | 2.1442e-05 | 0.070656 | 0.065268 | -0.012014 | 0.016449 | -0.0037748 | 0.14648 | 108.5312 | -13.4491 | 108.7372 | -13.353 | -13.559 | -13.5315 | 0.33417 | 108.5175 | -13.472 | 108.6548 | -13.353 | -13.4674 | -13.4674 | 0.009155 | -0.15564 | 0.050354 | 0.10529 | -0.073242 | -0.10071 | -0.082397 | -0.10986 | -0.013733 | -0.16937 | -0.032044 | 0.10529 | -0.009155 | -0.009155 | 0.004578 | 0.004578 | 0.096131 | 122.1863 | 0.11902 | 122.1268 | 121.9803 | 121.9894 | 121.9894 | 121.9757 | -122.1359 | -122.1588 | 122.1954 | 122.113 | 13.6047 | 13.7924
1197.4062 | 122.3053 | -13.3667 | 108.7784 | 0.0092313 | 0.0026981 | 0.059248 | 0.056898 | -0.0010638 | -0.0059835 | -0.0021213 | -0.0021057 | 0.0038666 | 0.069588 | 0.064627 | -0.0090235 | 0.018372 | -0.004202 | 0.041199 | 108.6182 | -13.353 | 108.815 | -13.2797 | -13.504 | -13.4628 | 0.22888 | 108.5907 | -13.3896 | 108.7326 | -13.2935 | -13.4079 | -13.3804 | 0.013733 | -0.16022 | 0.036621 | 0.086975 | -0.096131 | -0.13733 | -0.10986 | -0.15106 | -0.022888 | -0.18768 | -0.045776 | 0.073242 | -0.013733 | -0.041199 | 0.009155 | -0.018311 | 0.073242 | 122.168 | 0.09613 | 122.1222 | 121.9711 | 121.9803 | 121.9849 | 121.9574 | -122.1313 | -122.168 | 122.1817 | 122.0993 | 13.4079 | 13.5956
1199.1562 | 122.3694 | -13.0142 | 109.1629 | -0.013657 | -0.0022153 | 0.056044 | 0.05583 | 0.0019268 | -0.0061971 | -0.0040439 | -0.0021057 | 0.0027984 | 0.072365 | 0.066123 | -0.010732 | 0.017517 | -0.0056974 | 0.10071 | 108.9523 | -13.0051 | 109.1675 | -12.9089 | -13.1012 | -13.0692 | 0.3067 | 108.9844 | -13.0005 | 109.108 | -12.8952 | -12.9639 | -12.9868 | 0.009155 | -0.21057 | 0.004577 | 0.10528 | -0.054932 | -0.086975 | -0.064087 | -0.09613 | 0.013733 | -0.17853 | -0.054932 | 0.11902 | 0.027466 | 0.050354 | 0.013733 | 0.036621 | 0.09613 | 122.1725 | 0.10529 | 122.1085 | 121.9574 | 121.9849 | 121.9666 | 121.9986 | -122.168 | -122.1634 | 122.1817 | 122.1222 | 13.1149 | 13.3209
1200.8438 | 122.3053 | -12.6663 | 109.4925 | 0.0016023 | 0.0035525 | 0.057112 | 0.057112 | -0.00085021 | -0.0066245 | -0.0040439 | -0.0051575 | 0.0021576 | 0.072578 | 0.063987 | -0.0096643 | 0.019226 | -0.0018522 | 0.036621 | 109.3506 | -12.648 | 109.4742 | -12.6251 | -12.822 | -12.7716 | 0.1831 | 109.3414 | -12.6526 | 109.4009 | -12.6114 | -12.7075 | -12.6846 | 0.018311 | -0.14191 | -0.018311 | 0.041199 | -0.10529 | -0.15564 | -0.1236 | -0.17395 | 0.013733 | -0.15106 | -0.091553 | 0.054932 | -0.01831 | -0.041199 | -0.032043 | -0.054932 | 0.022888 | 122.1222 | 0.041199 | 122.0535 | 121.9986 | 121.994 | 122.0169 | 122.0078 | -122.1405 | -122.1451 | 122.1405 | 122.0673 | 12.7029 | 12.8494
1202.5781 | 122.3373 | -12.2681 | 109.8679 | 0.0016023 | 0.0018435 | 0.059248 | 0.060316 | 0.00043159 | -0.0051291 | -0.0036167 | -0.0051575 | 0.0023712 | 0.070442 | 0.063987 | -0.011373 | 0.018799 | -0.0022794 | 0.064087 | 109.7031 | -12.2864 | 109.9091 | -12.1994 | -12.3962 | -12.3596 | 0.27466 | 109.6893 | -12.2818 | 109.8358 | -12.1994 | -12.3093 | -12.2772 | -0.018311 | -0.16479 | 0.041199 | 0.068664 | -0.091553 | -0.12817 | -0.073242 | -0.10986 | -0.013733 | -0.17853 | -0.032044 | 0.068664 | -0.009156 | -0.041199 | 0.004577 | -0.027466 | 0.086975 | 122.1954 | 0.082397 | 122.1176 | 121.9894 | 121.9711 | 121.9711 | 121.9574 | -122.1542 | -122.1497 | 122.1771 | 122.1039 | 12.3322 | 12.5427
1204.25 | 122.2733 | -11.9247 | 110.2844 | 0.0092313 | 0.0029117 | 0.056471 | 0.059248 | 0.00021799 | -0.0072653 | -0.0014805 | 0.0009461 | 0.0051482 | 0.073006 | 0.067618 | -0.011801 | 0.018585 | -0.0061246 | 0.13733 | 110.1608 | -11.911 | 110.2295 | -11.8835 | -12.0621 | -12.0392 | 0.27924 | 110.1059 | -11.9339 | 110.1562 | -11.8561 | -11.9797 | -11.9431 | 0.013733 | -0.1236 | -0.054932 | 0.041199 | -0.11444 | -0.13733 | -0.12817 | -0.15106 | -0.009155 | -0.17853 | -0.12817 | 0.068665 | -0.01831 | -0.054931 | -0.009155 | -0.045776 | 0.027466 | 122.1405 | 0.07782 | 122.0901 | 122.0718 | 122.0398 | 122.0856 | 122.0306 | -122.1954 | -122.2183 | 122.1542 | 122.081 | 12.0621 | 12.204
1206.0156 | 122.3145 | -11.5356 | 110.6873 | -0.0060272 | 0.0018435 | 0.057112 | 0.057539 | -0.0027728 | -0.0094015 | -0.00062587 | -0.0051575 | 0.001944 | 0.073433 | 0.060996 | -0.0090235 | 0.018372 | -0.004202 | 0.045776 | 110.4904 | -11.5219 | 110.6003 | -11.4624 | -11.6547 | -11.618 | 0.18768 | 110.4767 | -11.5173 | 110.5637 | -11.4441 | -11.5173 | -11.5219 | 0.013733 | -0.19684 | -0.086975 | 0.073243 | -0.082397 | -0.11902 | -0.09613 | -0.13275 | 0.018311 | -0.21057 | -0.1236 | 0.091553 | 0.013733 | 0.018311 | -0.004578 | 0 | 0.05951 | 122.1222 | 0.073242 | 122.081 | 122.0123 | 121.994 | 122.0261 | 122.0123 | -122.2092 | -122.2046 | 122.1359 | 122.0993 | 11.5814 | 11.7233
1207.7031 | 122.2504 | -11.2244 | 111.0352 | -0.013657 | 0.0052615 | 0.059462 | 0.058821 | -0.0010638 | -0.0070517 | 1.4934e-05 | -0.0051575 | 0.0042938 | 0.070656 | 0.069968 | -0.0088097 | 0.020081 | -0.0005704 | 0.009155 | 110.8932 | -11.1832 | 110.8978 | -11.2244 | -11.3983 | -11.3663 | 0.11902 | 110.8658 | -11.1877 | 110.8612 | -11.1877 | -11.3022 | -11.2518 | 0.041198 | -0.14191 | -0.13733 | 0 | -0.14191 | -0.17395 | -0.18311 | -0.21515 | 0.036621 | -0.16937 | -0.17395 | 0.036621 | -0.027466 | -0.07782 | -0.064087 | -0.11444 | -0.041198 | 122.081 | 0 | 122.0489 | 122.0764 | 122.0535 | 122.1176 | 122.0901 | -122.2183 | -122.2229 | 122.1222 | 122.0856 | 11.2335 | 11.3434
1209.3906 | 122.2366 | -10.7941 | 111.438 | -0.0060272 | 0.0037661 | 0.057967 | 0.059248 | 0.0038494 | -0.0042745 | -0.0036167 | -0.0051575 | 0.0042938 | 0.070656 | 0.061637 | -0.010305 | 0.017944 | -0.0016384 | 0.086975 | 111.2823 | -10.7666 | 111.3647 | -10.7254 | -10.9406 | -10.9039 | 0.2243 | 111.2457 | -10.7941 | 111.264 | -10.7529 | -10.8856 | -10.8261 | 0.027465 | -0.15564 | -0.073242 | 0.068664 | -0.10986 | -0.14649 | -0.13733 | -0.17395 | 0 | -0.19226 | -0.17395 | 0.041198 | -0.032044 | -0.091553 | -0.032044 | -0.091553 | 0.041199 | 122.1313 | 0.041198 | 122.0581 | 122.049 | 122.0398 | 122.0764 | 122.0398 | -122.2046 | -122.2321 | 122.1588 | 122.0581 | 10.881 | 11.0184
1211.1406 | 122.3145 | -10.5469 | 111.6531 | 0.0016023 | 0.0009891 | 0.061598 | 0.057112 | 0.00043159 | -0.0061971 | -0.0014805 | -0.0051575 | 0.0015166 | 0.074074 | 0.059714 | -0.010092 | 0.018158 | -0.0020658 | 0.041199 | 111.4792 | -10.5148 | 111.6669 | -10.3867 | -10.6018 | -10.5652 | 0.26093 | 111.4426 | -10.5331 | 111.5891 | -10.405 | -10.5103 | -10.4874 | 0.032043 | -0.17395 | 0.013733 | 0.16022 | -0.018311 | -0.054932 | -0.050354 | -0.086975 | 0.013733 | -0.21057 | -0.064087 | 0.14191 | 0.059509 | 0.036621 | 0.045776 | 0.022888 | 0.12817 | 122.1817 | 0.12817 | 122.1222 | 121.994 | 121.9757 | 122.0261 | 121.9894 | -122.168 | -122.1863 | 122.2137 | 122.1359 | 10.5881 | 10.8078
1212.8906 | 122.3465 | -10.2722 | 111.9003 | -0.0060272 | -0.0002927 | 0.056685 | 0.057112 | 0.0017132 | -0.0085471 | -0.0019077 | -0.0051575 | 0.00044864 | 0.070015 | 0.067832 | -0.011587 | 0.018158 | -0.004202 | 0.045776 | 111.7493 | -10.2676 | 111.882 | -10.1715 | -10.3592 | -10.318 | 0.20599 | 111.7447 | -10.2768 | 111.85 | -10.1578 | -10.2402 | -10.2219 | 0.004578 | -0.15106 | -0.018311 | 0.10071 | -0.045776 | -0.086975 | -0.050354 | -0.091553 | -0.004577 | -0.15564 | -0.050354 | 0.11444 | 0.050354 | 0.032044 | 0.054931 | 0.036621 | 0.09613 | 122.1497 | 0.11902 | 122.1268 | 122.0169 | 122.0215 | 122.0215 | 122.0169 | -122.168 | -122.1771 | 122.1542 | 122.1222 | 10.318 | 10.4782
1214.6406 | 122.3465 | -9.9609 | 112.2345 | 0.0016023 | 0.0056887 | 0.059676 | 0.058821 | 0.004704 | -0.0047019 | -0.0036167 | 0.0009461 | 0.00066224 | 0.07151 | 0.060569 | -0.0090235 | 0.019867 | -0.0016384 | 0.013733 | 112.1017 | -9.9747 | 112.1841 | -9.8877 | -10.0708 | -10.0296 | 0.24261 | 112.0331 | -9.9747 | 112.175 | -9.8373 | -9.938 | -9.8785 | -0.013733 | -0.13275 | -0.050354 | 0.073242 | -0.068665 | -0.10986 | -0.054932 | -0.096131 | -0.013733 | -0.20142 | -0.059509 | 0.1236 | 0.082397 | 0.022888 | 0.09613 | 0.036621 | 0.086975 | 122.1588 | 0.13733 | 122.1497 | 122.0764 | 122.0078 | 122.0627 | 121.994 | -122.2092 | -122.2092 | 122.1451 | 122.1359 | 9.9747 | 10.2036
1216.3438 | 122.3099 | -9.6817 | 112.5 | -0.0060272 | -7.9104e-05 | 0.058607 | 0.054335 | -0.0044818 | -0.0053427 | -0.0021213 | -0.0021057 | 0.0017304 | 0.069374 | 0.058219 | -0.010519 | 0.018158 | -0.006979 | 0.032043 | 112.3123 | -9.6863 | 112.4725 | -9.5535 | -9.7595 | -9.7275 | 0.21057 | 112.3032 | -9.668 | 112.4084 | -9.581 | -9.6771 | -9.6405 | -0.004577 | -0.18768 | -0.027466 | 0.12817 | -0.045776 | -0.077819 | -0.041199 | -0.073242 | 0.013733 | -0.19684 | -0.091553 | 0.10071 | 0.041199 | 0.004578 | 0.027466 | -0.009155 | 0.13275 | 122.1588 | 0.086975 | 122.0764 | 121.9986 | 121.9711 | 121.994 | 121.9849 | -122.1863 | -122.168 | 122.1542 | 122.0901 | 9.7137 | 9.8923
1218.0938 | 122.3145 | -9.4254 | 112.7655 | -0.021286 | -0.0011471 | 0.057753 | 0.054549 | -0.00042301 | -0.0066245 | -0.0034031 | -0.0021057 | 0.0015166 | 0.073006 | 0.068259 | -0.0090235 | 0.017517 | -0.003561 | 0.054932 | 112.5824 | -9.4299 | 112.7151 | -9.3475 | -9.5261 | -9.4711 | 0.2243 | 112.5641 | -9.4299 | 112.6694 | -9.3063 | -9.3979 | -9.375 | -0.004578 | -0.18311 | -0.050354 | 0.07782 | -0.045776 | -0.10071 | -0.041198 | -0.09613 | -0.004578 | -0.20142 | -0.09613 | 0.11902 | 0.050354 | 0.027466 | 0.054932 | 0.032044 | 0.082398 | 122.1451 | 0.1236 | 122.0993 | 122.0123 | 121.994 | 122.0078 | 121.9894 | -122.1954 | -122.1954 | 122.1405 | 122.0947 | 9.4803 | 9.6497
1219.8438 | 122.3053 | -41.3452 | 80.9463 | 0.0016023 | 0.0029117 | 0.059248 | 0.059676 | 0.00043159 | -0.0091879 | -0.0027621 | -0.0051575 | 0.0045074 | 0.071297 | 0.063773 | -0.012869 | 0.018372 | -0.0020658 | -1.3962 | 79.4128 | -42.5217 | 80.8823 | -41.1484 | -41.4734 | -41.3315 | -0.041199 | 80.7953 | -41.2949 | 80.2551 | -41.6977 | -42.0959 | -41.6428 | -1.1765 | -1.5335 | -0.064087 | 0.19684 | 0.013733 | -0.12817 | 1.1902 | 1.0483 | 0.050354 | -0.15106 | -0.69122 | -0.35248 | -0.29755 | -0.75073 | -0.3479 | -0.80109 | 1.3733 | 123.4039 | -0.40283 | 121.55 | 121.9345 | 122.0901 | 120.7581 | 122.1405 | -123.468 | -122.2412 | 122.2275 | 121.6003 | 39.949 | 41.304
1221.5312 | 121.9894 | -29.4846 | 92.2943 | -0.013657 | 0.0024845 | 0.057539 | 0.056044 | 4.192e-06 | -0.0074789 | -0.0010531 | -0.0021057 | 0.001944 | 0.070015 | 0.058432 | -0.01116 | 0.017944 | -0.0061246 | -0.4303 | 92.0929 | -29.4937 | 92.308 | -29.425 | -29.7867 | -29.9194 | 0.050354 | 92.1387 | -29.4388 | 92.2668 | -29.5395 | -29.6082 | -29.5853 | -0.009155 | -0.20142 | 0.013732 | 0.059509 | -0.43488 | -0.30212 | -0.42572 | -0.29297 | 0.045776 | -0.15564 | -0.027466 | -0.054932 | -0.10071 | -0.1236 | -0.14648 | -0.16937 | 0.068664 | 121.8018 | -0.10071 | 121.7056 | 121.5866 | 121.5775 | 121.5775 | 121.6232 | -121.788 | -121.7331 | 121.7926 | 121.7514 | 29.0543 | 29.5349
1223.2812 | 122.1588 | -0.49896 | 121.8384 | 0.0016023 | 0.0007755 | 0.056471 | 0.057326 | 0.0027814 | -0.0089743 | -0.0023349 | -0.0021057 | 0.0038666 | 0.070442 | 0.069327 | -0.011587 | 0.020721 | -0.0050564 | 0.091553 | 121.5271 | -0.51727 | 121.5179 | -0.4715 | -0.60425 | -0.57678 | 0.28839 | 121.4355 | -0.58594 | 121.6324 | -0.21057 | -0.33875 | -0.27466 | -0.018311 | -0.31128 | -0.32044 | 0.027465 | -0.07782 | -0.10529 | -0.059509 | -0.086975 | -0.086975 | -0.40283 | -0.20599 | 0.28839 | 0.2243 | 0.16022 | 0.31128 | 0.24719 | 0.045776 | 122.0352 | 0.37537 | 122.2183 | 122.0444 | 122.0215 | 122.0261 | 121.9345 | -122.3557 | -122.4243 | 122.0169 | 122.1313 | 0.59052 | 0.78735
1225.0312 | 122.1542 | -5.2917 | 116.748 | 0.0016023 | 0.0056887 | 0.059889 | 0.056258 | 0.0044904 | -0.0070517 | -0.0034031 | -0.0021057 | 0.001944 | 0.07151 | 0.062918 | -0.010305 | 0.019012 | -0.0001432 | 0.16022 | 116.5283 | -5.2963 | 116.7023 | -5.1178 | -5.3101 | -5.2505 | 0.42572 | 116.5146 | -5.2872 | 116.6885 | -5.0537 | -5.1178 | -5.1086 | -0.004578 | -0.21973 | -0.045776 | 0.17395 | 0.041199 | -0.018311 | 0.045777 | -0.013733 | 0.004578 | -0.23346 | -0.059509 | 0.23804 | 0.18311 | 0.17395 | 0.17853 | 0.16937 | 0.17853 | 121.9986 | 0.23346 | 121.9757 | 121.8246 | 121.8018 | 121.8201 | 121.8063 | -122.0444 | -122.0352 | 121.994 | 121.9803 | 5.452 | 5.7175
1226.7969 | 122.1634 | -121.2158 | 0.73242 | -0.0060272 | 0.0024845 | 0.061385 | 0.060744 | -0.0029864 | -0.0089743 | -0.0034031 | -0.0051575 | 0.001303 | 0.072792 | 0.079367 | -0.010946 | 0.018799 | -0.005911 | -0.39825 | 0.62714 | -121.2936 | 0.60425 | -120.6116 | -121.3348 | -121.3577 | -0.71411 | 0.69122 | -121.4035 | 0.64545 | -120.8359 | -121.2204 | -121.1609 | -0.07782 | -0.10529 | -0.12817 | 0.60425 | -0.14191 | -0.11902 | -0.064087 | -0.041199 | -0.18768 | -0.041199 | -0.086975 | 0.37994 | 0.054931 | -0.004578 | 0.24261 | 0.1831 | 0.68207 | 121.8979 | 0.56763 | 122.049 | 121.9208 | 122.0947 | 121.843 | 121.907 | -122.0261 | -122.1359 | 121.8201 | 121.8613 | 120.8176 | 120.5017
1228.5625 | 122.2824 | -120.9778 | 0.97046 | -0.0060272 | 0.0007755 | 0.062453 | 0.060103 | 0.0027814 | -0.0064109 | -0.0040439 | -0.0082093 | 0.0025848 | 0.074928 | 0.062918 | -0.010305 | 0.021362 | -0.0005704 | -0.39825 | 0.88348 | -121.019 | 0.90637 | -120.3598 | -121.106 | -121.1243 | -0.6134 | 0.93384 | -121.1655 | 0.99792 | -120.5658 | -120.9595 | -120.8633 | -0.041199 | -0.086975 | -0.064087 | 0.61798 | -0.14648 | -0.12817 | -0.10529 | -0.086975 | -0.18768 | -0.036621 | 0.027466 | 0.41199 | 0.11444 | 0.01831 | 0.30212 | 0.20599 | 0.65918 | 121.9254 | 0.59967 | 122.1634 | 121.9025 | 122.0993 | 121.8613 | 121.9116 | -121.9894 | -122.1359 | 121.8842 | 121.9757 | 120.5795 | 120.3644
1230.25 | 122.2 | -120.932 | 1.1719 | 0.0092313 | -0.0013607 | 0.058394 | 0.05818 | -0.0019184 | -0.0076925 | -0.00083947 | -0.0051575 | 0.0017304 | 0.073219 | 0.059073 | -0.0094507 | 0.018585 | -0.0014248 | -0.19684 | 1.0117 | -120.9366 | 1.0529 | -120.2408 | -120.9641 | -120.9732 | -0.52185 | 1.0941 | -121.0648 | 1.0391 | -120.5063 | -120.9 | -120.845 | -0.004577 | -0.16022 | -0.11902 | 0.69122 | -0.041199 | -0.032043 | -0.036622 | -0.027466 | -0.13275 | -0.07782 | -0.13275 | 0.42572 | 0.086975 | 0.032044 | 0.21973 | 0.16479 | 0.6958 | 121.9894 | 0.55847 | 122.1039 | 121.9482 | 122.1588 | 121.9437 | 122.0261 | -122.1085 | -122.2366 | 121.9849 | 121.9711 | 120.7352 | 120.4102
1232 | 122.3053 | -121.0373 | 1.0208 | -0.0060272 | -0.0007199 | 0.06053 | 0.056044 | -0.0051226 | -0.0051291 | -0.0016941 | -0.0082093 | -0.0010468 | 0.074074 | 0.060569 | -0.0090235 | 0.020081 | -0.0009976 | -0.27008 | 0.90179 | -121.0419 | 0.92468 | -120.3735 | -121.0876 | -121.0968 | -0.52185 | 0.97504 | -121.1746 | 0.98877 | -120.5841 | -120.9457 | -120.8954 | -0.004578 | -0.11902 | -0.09613 | 0.66376 | -0.05951 | -0.050354 | -0.054932 | -0.045776 | -0.13733 | -0.045776 | -0.032043 | 0.45319 | 0.14191 | 0.091552 | 0.27924 | 0.22888 | 0.66833 | 121.9666 | 0.59052 | 122.1634 | 121.9437 | 122.1497 | 121.9391 | 122.0123 | -122.0627 | -122.1954 | 121.962 | 122.0261 | 120.7672 | 120.5154
1233.75 | 122.2229 | -121.0693 | 1.0712 | -0.0060272 | -0.0005063 | 0.058821 | 0.056685 | -0.001491 | -0.0061971 | -0.0029759 | -0.0051575 | 2.1442e-05 | 0.068733 | 0.063773 | -0.0083825 | 0.016876 | -0.0046292 | -0.14648 | 0.94299 | -121.0464 | 0.94299 | -120.3598 | -121.0831 | -121.1105 | -0.47607 | 1.0162 | -121.1334 | 0.93842 | -120.6299 | -121.019 | -120.9641 | 0.022888 | -0.12817 | -0.12817 | 0.70953 | -0.041199 | -0.013733 | -0.064087 | -0.036621 | -0.064087 | -0.054932 | -0.13275 | 0.43945 | 0.10529 | 0.050354 | 0.16937 | 0.11444 | 0.68665 | 121.9894 | 0.50354 | 122.0718 | 121.9894 | 122.1497 | 122.0123 | 122.0856 | -122.1176 | -122.2046 | 122.0123 | 122.0078 | 120.9229 | 120.5933
1235.4375 | 122.2366 | -120.8633 | 1.2817 | -0.0060272 | 0.0022709 | 0.05818 | 0.060744 | 0.0032086 | -0.0059835 | 0.0019375 | -0.0051575 | 0.0027984 | 0.071724 | 0.068045 | -0.0092371 | 0.019867 | -0.0020658 | -0.16479 | 1.1627 | -120.8176 | 1.1673 | -120.1767 | -120.8954 | -120.9412 | -0.45776 | 1.2039 | -120.9595 | 1.1902 | -120.4193 | -120.8176 | -120.7443 | 0.045776 | -0.11902 | -0.11444 | 0.68664 | -0.07782 | -0.032044 | -0.1236 | -0.07782 | -0.096131 | -0.07782 | -0.091552 | 0.44403 | 0.11902 | 0.045776 | 0.21515 | 0.14191 | 0.64087 | 121.9849 | 0.54016 | 122.1497 | 121.9803 | 122.1634 | 122.0261 | 122.0673 | -122.0993 | -122.2412 | 122.0306 | 122.0535 | 120.6985 | 120.4056
1237.1875 | 122.3328 | -121.0236 | 1.0757 | -0.013657 | -7.9104e-05 | 0.059676 | 0.055189 | -0.0032 | -0.0072653 | -0.0012669 | -0.0051575 | 2.1442e-05 | 0.072792 | 0.060569 | -0.0096643 | 0.019226 | -0.00527 | -0.20599 | 0.94757 | -120.9595 | 0.99792 | -120.3186 | -121.0419 | -121.0648 | -0.48065 | 1.03 | -121.1105 | 1.0666 | -120.5246 | -120.8954 | -120.845 | 0.064087 | -0.12817 | -0.07782 | 0.70496 | -0.041198 | -0.01831 | -0.10528 | -0.082397 | -0.086975 | -0.045777 | -0.009156 | 0.49896 | 0.17853 | 0.12817 | 0.2655 | 0.21515 | 0.64087 | 121.9574 | 0.58594 | 122.1771 | 121.907 | 122.1405 | 121.9711 | 122.0535 | -122.0352 | -122.1863 | 122.0215 | 122.0901 | 120.8176 | 120.5429
1238.9219 | 122.2412 | -120.5246 | 1.6022 | 0.0016023 | 0.0022709 | 0.05818 | 0.057753 | 0.0040632 | -0.0057699 | -0.00062587 | -0.0021057 | 0.0032256 | 0.07386 | 0.062918 | -0.010305 | 0.02179 | -0.0063382 | -0.15564 | 1.4557 | -120.5109 | 1.506 | -119.8471 | -120.5933 | -120.6162 | -0.4303 | 1.5381 | -120.6207 | 1.5289 | -120.0897 | -120.4834 | -120.4147 | 0.013733 | -0.14648 | -0.096131 | 0.67749 | -0.091553 | -0.068665 | -0.10529 | -0.082398 | -0.096131 | -0.064087 | -0.073242 | 0.43488 | 0.10986 | 0.041199 | 0.20599 | 0.13733 | 0.66376 | 122.0169 | 0.53101 | 122.1497 | 121.9666 | 122.1588 | 121.9803 | 122.0627 | -122.113 | -122.2229 | 122.0306 | 122.0535 | 120.369 | 120.0943
1240.6719 | 122.1909 | -120.6116 | 1.5335 | -0.013657 | 0.0037661 | 0.058607 | 0.059889 | -0.0012774 | -0.0066245 | -0.0038303 | -0.0051575 | 0.0042938 | 0.07151 | 0.065055 | -0.010519 | 0.020081 | 0.000925 | -0.17395 | 1.387 | -120.5612 | 1.3824 | -119.9753 | -120.7123 | -120.726 | -0.53558 | 1.4832 | -120.7123 | 1.4099 | -120.2271 | -120.6345 | -120.5475 | 0.050354 | -0.14648 | -0.15106 | 0.63629 | -0.11444 | -0.10071 | -0.16479 | -0.15106 | -0.10071 | -0.050354 | -0.1236 | 0.38452 | 0.064087 | -0.022888 | 0.1648 | 0.07782 | 0.58594 | 121.9437 | 0.48523 | 122.1222 | 121.9482 | 122.1954 | 121.9986 | 122.0947 | -122.0947 | -122.2458 | 121.994 | 122.0215 | 120.4376 | 120.076
1242.3594 | 122.2504 | -120.7901 | 1.3367 | 0.0016023 | 0.0009891 | 0.06053 | 0.056471 | -0.0023456 | -0.0061971 | -0.0036167 | -0.0051575 | 0.0034392 | 0.072151 | 0.063773 | -0.012655 | 0.018799 | -0.0020658 | -0.27924 | 1.2039 | -120.7901 | 1.1536 | -120.1996 | -120.9412 | -120.932 | -0.58136 | 1.2726 | -120.9045 | 1.2222 | -120.3873 | -120.7993 | -120.7169 | 0 | -0.13275 | -0.18311 | 0.59051 | -0.14191 | -0.15106 | -0.14191 | -0.15106 | -0.11444 | -0.064087 | -0.11444 | 0.40283 | 0.073242 | -0.009155 | 0.18768 | 0.10529 | 0.59051 | 121.9437 | 0.51727 | 122.1268 | 121.994 | 122.1771 | 121.994 | 122.0627 | -122.1268 | -122.2412 | 121.9437 | 122.0123 | 120.5109 | 120.2087
1244.1094 | 122.2504 | -120.9915 | 1.1444 | -0.0060272 | 0.0005619 | 0.060103 | 0.057539 | 0.0053448 | -0.0064109 | -0.00041227 | -0.0051575 | 0.001944 | 0.074287 | 0.062064 | -0.010732 | 0.02179 | -0.003561 | -0.13733 | 1.0162 | -120.9732 | 1.0345 | -120.3232 | -121.0602 | -121.0739 | -0.4303 | 1.0895 | -121.0785 | 1.0712 | -120.5383 | -120.9595 | -120.8771 | 0.01831 | -0.12817 | -0.10986 | 0.66833 | -0.082398 | -0.068665 | -0.10071 | -0.086975 | -0.086975 | -0.054931 | -0.073242 | 0.45319 | 0.11444 | 0.032043 | 0.20142 | 0.11902 | 0.65002 | 122.0078 | 0.54016 | 122.1497 | 121.9894 | 122.168 | 122.0078 | 122.081 | -122.1176 | -122.2229 | 122.0261 | 122.0627 | 120.8542 | 120.5612
1245.8438 | 122.3328 | -121.0602 | 0.99335 | -0.013657 | 0.0009891 | 0.062239 | 0.056471 | 0.0025678 | -0.0066245 | -0.0016941 | -0.0021057 | 0.001303 | 0.07386 | 0.058646 | -0.01116 | 0.018585 | 0.0007114 | -0.25177 | 0.88806 | -121.051 | 0.91095 | -120.4468 | -121.1884 | -121.1975 | -0.52185 | 0.93842 | -121.1746 | 1.0025 | -120.6207 | -121.019 | -120.9137 | 0.009156 | -0.10528 | -0.082397 | 0.6134 | -0.13733 | -0.12817 | -0.14648 | -0.13733 | -0.11444 | -0.054931 | 0.009155 | 0.43945 | 0.14648 | 0.041199 | 0.26093 | 0.15564 | 0.60425 | 121.962 | 0.55389 | 122.1771 | 121.9391 | 122.113 | 121.9482 | 121.9986 | -122.0444 | -122.168 | 121.9711 | 122.0627 | 120.8084 | 120.5383
1247.5938 | 122.3145 | -121.138 | 0.93842 | -0.013657 | -0.0013607 | 0.060316 | 0.054976 | -0.00042301 | -0.0083335 | -0.0038303 | -0.0051575 | -0.00061956 | 0.072792 | 0.063132 | -0.0094507 | 0.018372 | -0.0046292 | -0.20599 | 0.81024 | -121.1334 | 0.84686 | -120.4742 | -121.2021 | -121.2204 | -0.50812 | 0.88348 | -121.2708 | 0.90179 | -120.694 | -121.051 | -121.0098 | 0.004577 | -0.12817 | -0.091553 | 0.66376 | -0.082398 | -0.064087 | -0.086975 | -0.068664 | -0.13275 | -0.054932 | -0.036622 | 0.44403 | 0.12817 | 0.086975 | 0.26093 | 0.21973 | 0.65918 | 121.9803 | 0.57678 | 122.1725 | 121.9437 | 122.1542 | 121.9482 | 122.0215 | -122.0718 | -122.2092 | 121.9849 | 122.0398 | 120.932 | 120.6299
1249.2812 | 122.2 | -121.2296 | 0.91095 | -0.0060272 | 0.0007755 | 0.059462 | 0.05818 | 0.00085879 | -0.0038473 | -0.0031895 | 0.0009461 | 0.0027984 | 0.070229 | 0.070609 | -0.010092 | 0.020294 | -0.0039884 | -0.16022 | 0.78735 | -121.2387 | 0.77362 | -120.5887 | -121.3348 | -121.3486 | -0.50354 | 0.85602 | -121.3165 | 0.78735 | -120.8313 | -121.2479 | -121.1517 | -0.009155 | -0.1236 | -0.13733 | 0.64087 | -0.11902 | -0.10529 | -0.10986 | -0.096131 | -0.086975 | -0.054932 | -0.1236 | 0.39825 | 0.07782 | -0.018311 | 0.1648 | 0.068664 | 0.65002 | 122.0123 | 0.48523 | 122.1039 | 122.0261 | 122.1725 | 122.0169 | 122.0856 | -122.1497 | -122.2275 | 122.0032 | 122.0169 | 121.0693 | 120.726
1251.0312 | 122.1863 | -121.2387 | 0.90637 | 0.0016023 | 0.0001345 | 0.058394 | 0.057326 | 0.00085879 | -0.0089743 | -0.0042575 | -0.0021057 | 0.00087584 | 0.071724 | 0.053733 | -0.010092 | 0.019226 | 0.000925 | -0.14648 | 0.77362 | -121.2524 | 0.71869 | -120.6253 | -121.3486 | -121.3623 | -0.49896 | 0.82398 | -121.3669 | 0.73242 | -120.8496 | -121.2433 | -121.1792 | -0.013733 | -0.13275 | -0.18768 | 0.6134 | -0.1236 | -0.10986 | -0.10986 | -0.096131 | -0.12817 | -0.082397 | -0.17395 | 0.3891 | 0.059509 | -0.004578 | 0.18768 | 0.1236 | 0.62714 | 121.9711 | 0.51727 | 122.0993 | 122.0261 | 122.1909 | 122.0123 | 122.0627 | -122.1588 | -122.2733 | 121.9574 | 121.9711 | 121.0922 | 120.7397
1252.7969 | 122.2733 | -121.2067 | 0.90179 | -0.0060272 | 0.0007755 | 0.058821 | 0.056898 | 0.00064519 | -0.0061971 | -0.0038303 | -0.0021057 | -0.0010468 | 0.071083 | 0.056937 | -0.0094507 | 0.016449 | -0.0027066 | -0.2243 | 0.74616 | -121.2158 | 0.80566 | -120.5429 | -121.2799 | -121.2753 | -0.52185 | 0.82398 | -121.3211 | 0.82398 | -120.7764 | -121.1563 | -121.0831 | -0.009155 | -0.15564 | -0.09613 | 0.66376 | -0.068665 | -0.073242 | -0.05951 | -0.064087 | -0.11444 | -0.077819 | -0.077819 | 0.4303 | 0.1236 | 0.050354 | 0.23804 | 0.16479 | 0.67291 | 122.0215 | 0.54474 | 122.1451 | 121.962 | 122.1451 | 121.9528 | 122.0306 | -122.1176 | -122.2229 | 122.0123 | 122.0306 | 120.9824 | 120.6848
1254.5625 | 122.3236 | -121.2204 | 0.82398 | -0.013657 | 0.0016299 | 0.060316 | 0.056685 | 0.0049176 | -0.0085471 | -0.0019077 | -0.0021057 | 0.00087584 | 0.071083 | 0.064627 | -0.01351 | 0.020508 | -0.002493 | -0.15564 | 0.69122 | -121.225 | 0.83313 | -120.5246 | -121.2799 | -121.2845 | -0.45319 | 0.7782 | -121.3531 | 0.86517 | -120.7535 | -121.1426 | -121.0693 | -0.004578 | -0.13275 | 0.009155 | 0.6958 | -0.064087 | -0.059509 | -0.059509 | -0.054931 | -0.13275 | -0.045777 | 0.041198 | 0.46692 | 0.15106 | 0.07782 | 0.28381 | 0.21057 | 0.70038 | 122.0581 | 0.59967 | 122.2183 | 121.9162 | 122.1313 | 121.9116 | 121.9986 | -122.049 | -122.1771 | 122.0535 | 122.0856 | 121.0648 | 120.7672
1256.2656 | 122.3236 | -121.2524 | 0.82855 | -0.0060272 | 0.0003483 | 0.057326 | 0.057539 | 0.002995 | -0.0072653 | -0.0029759 | -0.0051575 | 0.00044864 | 0.069801 | 0.0642 | -0.011587 | 0.019653 | -0.0003568 | -0.17395 | 0.68665 | -121.2708 | 0.75531 | -120.5978 | -121.2982 | -121.3211 | -0.48981 | 0.76904 | -121.3898 | 0.79651 | -120.7901 | -121.1563 | -121.1151 | -0.018311 | -0.14191 | -0.073242 | 0.6546 | -0.068665 | -0.045777 | -0.050354 | -0.027466 | -0.13733 | -0.059509 | -0.032043 | 0.46234 | 0.13733 | 0.09613 | 0.27466 | 0.23346 | 0.67291 | 122.0261 | 0.59967 | 122.1863 | 121.9574 | 122.1588 | 121.9391 | 122.0215 | -122.0993 | -122.2183 | 122.0078 | 122.049 | 121.0785 | 120.7626
1258.0156 | 122.2046 | -121.2524 | 0.90637 | -0.0060272 | 0.0012027 | 0.061385 | 0.058607 | 0.0027814 | -0.0055563 | -0.0012669 | -0.0051575 | 0.001303 | 0.070015 | 0.0689 | -0.010092 | 0.02179 | -0.0022794 | -0.13275 | 0.75073 | -121.257 | 0.76904 | -120.6024 | -121.344 | -121.3623 | -0.5127 | 0.81024 | -121.3348 | 0.76904 | -120.8496 | -121.2708 | -121.1746 | -0.004578 | -0.15564 | -0.13733 | 0.65002 | -0.10986 | -0.091553 | -0.10529 | -0.086975 | -0.082398 | -0.09613 | -0.13733 | 0.40283 | 0.077819 | -0.018311 | 0.16022 | 0.064087 | 0.6546 | 122.0261 | 0.48523 | 122.1039 | 122.0078 | 122.1451 | 122.0032 | 122.0627 | -122.1634 | -122.2412 | 122.0215 | 122.0215 | 121.1197 | 120.7397
1259.7656 | 122.3373 | -121.2616 | 0.7782 | -0.013657 | -0.0020017 | 0.05818 | 0.05348 | -0.0025592 | -0.0079061 | -0.0034031 | 0.0009461 | -0.001474 | 0.072151 | 0.065268 | -0.011587 | 0.018372 | 0.0017794 | -0.10986 | 0.67291 | -121.2936 | 0.78735 | -120.5338 | -121.2845 | -121.2891 | -0.36621 | 0.73242 | -121.3943 | 0.79651 | -120.7626 | -121.1197 | -121.1151 | -0.032043 | -0.10528 | 0.009156 | 0.72784 | -0.027465 | -0.022888 | 0.004578 | 0.009155 | -0.13275 | -0.045776 | 0.018311 | 0.49896 | 0.14648 | 0.14191 | 0.27924 | 0.27466 | 0.75989 | 122.081 | 0.63171 | 122.1909 | 121.9666 | 122.1268 | 121.9345 | 121.994 | -122.0718 | -122.1725 | 122.049 | 122.0581 | 121.1517 | 120.8954
1261.4688 | 122.1909 | -121.3211 | 0.8606 | -0.013657 | 0.0012027 | 0.057539 | 0.056685 | 0.0038494 | -0.0068381 | -0.0012669 | -0.0021057 | 0.0027984 | 0.070442 | 0.059287 | -0.010732 | 0.020508 | -0.0054838 | -0.15106 | 0.6958 | -121.3257 | 0.6546 | -120.7031 | -121.4081 | -121.4172 | -0.54932 | 0.78735 | -121.4447 | 0.67749 | -120.9274 | -121.312 | -121.225 | -0.004578 | -0.1648 | -0.20599 | 0.61798 | -0.09613 | -0.086975 | -0.091552 | -0.082397 | -0.1236 | -0.073242 | -0.18311 | 0.39368 | 0.09613 | 0.009155 | 0.21973 | 0.13275 | 0.62256 | 121.9803 | 0.51727 | 122.1222 | 122.0215 | 122.2321 | 122.0169 | 122.1085 | -122.1863 | -122.3053 | 121.9757 | 121.9986 | 121.17 | 120.7718
1263.2031 | 122.2641 | -121.3257 | 0.76446 | -0.013657 | 0.0022709 | 0.059676 | 0.056898 | -0.00020941 | -0.0085471 | -0.0021213 | -0.0082093 | -0.001474 | 0.070869 | 0.060782 | -0.010092 | 0.018158 | -0.0018522 | -0.19684 | 0.63171 | -121.312 | 0.68207 | -120.6711 | -121.3989 | -121.4127 | -0.56305 | 0.72327 | -121.4539 | 0.70496 | -120.8817 | -121.2524 | -121.1975 | 0.013733 | -0.13275 | -0.082397 | 0.6546 | -0.086975 | -0.073242 | -0.10071 | -0.086975 | -0.12817 | -0.041198 | -0.059509 | 0.44403 | 0.12817 | 0.073243 | 0.25635 | 0.20142 | 0.64087 | 121.994 | 0.5722 | 122.1588 | 121.9437 | 122.1771 | 121.9574 | 122.049 | -122.0764 | -122.2183 | 122.0078 | 122.0306 | 121.1288 | 120.7626
1264.9531 | 122.3328 | -121.2936 | 0.75531 | -0.013657 | 0.0016299 | 0.059676 | 0.056258 | -0.0051226 | -0.0053427 | -0.0014805 | -0.0021057 | 0.00066224 | 0.071938 | 0.059714 | -0.012228 | 0.018799 | -0.0029202 | -0.16937 | 0.61798 | -121.2891 | 0.75073 | -120.6024 | -121.3531 | -121.3577 | -0.48065 | 0.70496 | -121.4218 | 0.7782 | -120.845 | -121.2296 | -121.1517 | 0.004578 | -0.13733 | -0.004578 | 0.69122 | -0.064087 | -0.059509 | -0.068665 | -0.064087 | -0.12817 | -0.050354 | 0.022888 | 0.44861 | 0.14191 | 0.064087 | 0.27008 | 0.19226 | 0.68664 | 122.0398 | 0.57678 | 122.2 | 121.907 | 122.1268 | 121.9116 | 121.9986 | -122.0444 | -122.1771 | 122.0444 | 122.0718 | 121.1243 | 120.813
1266.6406 | 122.3465 | -121.3165 | 0.76904 | -0.013657 | -0.0022153 | 0.056898 | 0.057112 | -0.0029864 | -0.0074789 | -0.0031895 | -0.0021057 | -0.00083316 | 0.070656 | 0.066123 | -0.012655 | 0.020081 | -0.0012112 | -0.10529 | 0.62256 | -121.3257 | 0.75073 | -120.575 | -121.3348 | -121.3257 | -0.41657 | 0.6958 | -121.4264 | 0.79651 | -120.7855 | -121.1655 | -121.1197 | -0.009156 | -0.14648 | -0.018311 | 0.74158 | -0.009156 | -0.018311 | 0 | -0.009155 | -0.10986 | -0.073242 | 0.027466 | 0.53101 | 0.19684 | 0.15106 | 0.3067 | 0.26093 | 0.75073 | 122.0764 | 0.64087 | 122.2229 | 121.9482 | 122.1222 | 121.9391 | 122.0123 | -122.0947 | -122.1954 | 122.0673 | 122.113 | 121.2112 | 120.9
1268.3281 | 122.2733 | -121.2753 | 0.82398 | 0.0016023 | 0.0003483 | 0.058821 | 0.056685 | -0.0023456 | -0.0070517 | -0.00083947 | -0.0082093 | -0.00019216 | 0.073433 | 0.062278 | -0.0098779 | 0.019012 | -0.00527 | -0.18768 | 0.64545 | -121.2753 | 0.75531 | -120.5887 | -121.3531 | -121.3394 | -0.51727 | 0.74158 | -121.3806 | 0.7782 | -120.8359 | -121.2158 | -121.1426 | 0 | -0.17853 | -0.068665 | 0.68665 | -0.064087 | -0.077819 | -0.064087 | -0.077819 | -0.10529 | -0.082398 | -0.045777 | 0.43945 | 0.13275 | 0.05951 | 0.23804 | 0.1648 | 0.68665 | 122.0306 | 0.54474 | 122.1588 | 121.9208 | 122.1222 | 121.9208 | 122.0169 | -122.0993 | -122.2046 | 122.0306 | 122.0535 | 121.0876 | 120.7581
1270.0781 | 122.2412 | -121.225 | 0.86975 | -0.013657 | 0.0041935 | 0.059248 | 0.058821 | -0.0012774 | -0.0064109 | -0.0029759 | -0.0021057 | 0.0034392 | 0.073006 | 0.065696 | -0.013082 | 0.020294 | -0.006979 | -0.10071 | 0.74158 | -121.257 | 0.7782 | -120.5887 | -121.312 | -121.3257 | -0.48523 | 0.83771 | -121.3303 | 0.81482 | -120.8038 | -121.2021 | -121.1014 | -0.032043 | -0.12817 | -0.091553 | 0.63629 | -0.10071 | -0.086975 | -0.068665 | -0.054932 | -0.10528 | -0.032043 | -0.054932 | 0.42114 | 0.1236 | 0.022889 | 0.22888 | 0.12817 | 0.66833 | 122.0352 | 0.52643 | 122.1451 | 121.9986 | 122.168 | 121.9666 | 122.0627 | -122.1268 | -122.2 | 122.0032 | 122.0398 | 121.1243 | 120.7397
1271.8438 | 122.2687 | -121.1197 | 0.99335 | -0.0060272 | -0.0037107 | 0.057539 | 0.055189 | -0.0027728 | -0.0091879 | -0.0029759 | -0.0021057 | -0.00040596 | 0.072151 | 0.065696 | -0.011373 | 0.01944 | -0.0033474 | -0.073242 | 0.83313 | -121.106 | 0.96588 | -120.3964 | -121.1243 | -121.1243 | -0.44861 | 0.92468 | -121.225 | 0.93842 | -120.6162 | -121.0236 | -120.9686 | 0.013733 | -0.16022 | -0.027466 | 0.72327 | -0.004578 | -0.004578 | -0.018311 | -0.018311 | -0.10529 | -0.068664 | -0.054931 | 0.50354 | 0.15106 | 0.09613 | 0.25635 | 0.20142 | 0.70953 | 122.0718 | 0.60883 | 122.1634 | 121.9391 | 122.1497 | 121.9528 | 122.0444 | -122.0993 | -122.2183 | 122.0856 | 122.0581 | 121.0464 | 120.6711
1273.5938 | 122.3236 | -120.9091 | 1.149 | -0.013657 | 0.0016299 | 0.060316 | 0.057539 | -0.0019184 | -0.0072653 | -0.0029759 | -0.0051575 | 0.0015166 | 0.072792 | 0.059287 | -0.010519 | 0.01944 | -0.0009976 | -0.16479 | 1.0071 | -120.9091 | 1.1536 | -120.1996 | -120.9457 | -120.9457 | -0.48065 | 1.0895 | -121.0373 | 1.1627 | -120.4285 | -120.8221 | -120.7489 | 0 | -0.14191 | 0.004577 | 0.70953 | -0.036621 | -0.036621 | -0.036621 | -0.036621 | -0.12817 | -0.059509 | 0.013733 | 0.48065 | 0.16022 | 0.086975 | 0.28839 | 0.21515 | 0.70953 | 122.0627 | 0.60882 | 122.2 | 121.9162 | 122.1268 | 121.9162 | 121.9986 | -122.0581 | -122.1863 | 122.0627 | 122.0718 | 120.7443 | 120.4285
1275.2812 | 122.2458 | -121.0144 | 1.1078 | -0.013657 | 0.0018435 | 0.059676 | 0.057112 | 0.0010724 | -0.0070517 | -0.0034031 | -0.0082093 | 0.0023712 | 0.073433 | 0.0689 | -0.01116 | 0.019653 | -0.004202 | -0.082397 | 0.96588 | -121.0556 | 0.98419 | -120.3781 | -121.1105 | -121.1243 | -0.50354 | 1.0254 | -121.1426 | 1.0071 | -120.5978 | -120.9961 | -120.9091 | -0.041199 | -0.14191 | -0.1236 | 0.63629 | -0.10986 | -0.096131 | -0.068665 | -0.054932 | -0.12817 | -0.082397 | -0.10071 | 0.41657 | 0.10528 | 0.01831 | 0.23346 | 0.14648 | 0.67749 | 122.0398 | 0.54474 | 122.1497 | 122.0215 | 122.168 | 121.9803 | 122.0398 | -122.1634 | -122.2504 | 121.9986 | 122.0215 | 120.932 | 120.5109
1277.0156 | 122.2778 | -120.9915 | 1.0574 | -0.013657 | 0.0024845 | 0.059676 | 0.059462 | 4.192e-06 | -0.0061971 | -0.0029759 | -0.0051575 | 0.0027984 | 0.071938 | 0.065055 | -0.010946 | 0.019653 | -0.003561 | -0.2243 | 0.95215 | -121.0327 | 0.97504 | -120.3964 | -121.138 | -121.1243 | -0.59967 | 1.0162 | -121.138 | 1.0483 | -120.575 | -120.9549 | -120.8633 | -0.041199 | -0.10529 | -0.082397 | 0.59509 | -0.13275 | -0.14648 | -0.091553 | -0.10529 | -0.14648 | -0.041199 | -0.009155 | 0.41657 | 0.12817 | 0.036621 | 0.27466 | 0.18311 | 0.63629 | 122.0078 | 0.56305 | 122.1863 | 121.9849 | 122.1542 | 121.9437 | 122.0078 | -122.0901 | -122.1954 | 121.9666 | 122.0398 | 120.7672 | 120.3918
1278.7656 | 122.3236 | -119.5908 | 2.4948 | -0.0060272 | -0.0024289 | 0.057112 | 0.054762 | -0.0027728 | -0.0079061 | -0.00041227 | -0.0082093 | -0.0012604 | 0.074074 | 0.059928 | -0.010732 | 0.016663 | -0.002493 | -0.12817 | 2.3346 | -119.5999 | 2.4536 | -118.895 | -119.6136 | -119.6365 | -0.48981 | 2.417 | -119.7281 | 2.4857 | -119.0964 | -119.4626 | -119.4168 | -0.009156 | -0.16022 | -0.041199 | 0.6958 | -0.045777 | -0.022888 | -0.036621 | -0.013732 | -0.13733 | -0.07782 | -0.009155 | 0.49438 | 0.17395 | 0.12817 | 0.31128 | 0.2655 | 0.70496 | 122.0535 | 0.63171 | 122.2137 | 121.9345 | 122.1451 | 121.9254 | 122.0078 | -122.0947 | -122.2229 | 122.0444 | 122.0764 | 119.4626 | 119.101
1280.4531 | 122.2137 | -119.4717 | 2.6047 | -0.0060272 | 0.0020571 | 0.058821 | 0.058394 | 0.0027814 | -0.0079061 | -0.0025485 | 0.0009461 | 0.0015166 | 0.071938 | 0.059501 | -0.010092 | 0.021149 | -0.003561 | -0.07782 | 2.4902 | -119.4809 | 2.5589 | -118.8354 | -119.5587 | -119.5816 | -0.49439 | 2.5681 | -119.6136 | 2.5269 | -119.0643 | -119.458 | -119.3619 | -0.009155 | -0.11444 | -0.045776 | 0.63629 | -0.10986 | -0.086975 | -0.10071 | -0.07782 | -0.14191 | -0.036621 | -0.07782 | 0.40741 | 0.10986 | 0.013733 | 0.25177 | 0.15564 | 0.64545 | 122.0398 | 0.54932 | 122.1405 | 121.9711 | 122.1817 | 121.962 | 122.0398 | -122.0856 | -122.2183 | 122.0306 | 121.9986 | 119.3939 | 118.9774
1282.2188 | 122.2275 | -119.6823 | 2.4307 | -0.0060272 | 0.0009891 | 0.059462 | 0.05818 | 0.0032086 | -0.0070517 | -0.00019867 | -0.0082093 | 0.0045074 | 0.071938 | 0.06655 | -0.0090235 | 0.01944 | 0.0013522 | -0.10071 | 2.2705 | -119.751 | 2.2614 | -119.101 | -119.8059 | -119.8334 | -0.5722 | 2.3529 | -119.8288 | 2.2797 | -119.2841 | -119.6732 | -119.5953 | -0.068665 | -0.16022 | -0.16937 | 0.58136 | -0.15106 | -0.1236 | -0.082397 | -0.054931 | -0.14648 | -0.07782 | -0.15106 | 0.39825 | 0.086975 | 0.009155 | 0.23346 | 0.15564 | 0.65002 | 122.0123 | 0.54474 | 122.1085 | 122.0215 | 122.1817 | 121.9528 | 122.0352 | -122.1817 | -122.2595 | 121.9437 | 121.962 | 119.5816 | 119.1101
1283.9688 | 122.3145 | -120.5658 | 1.474 | -0.013657 | 0.0035525 | 0.059462 | 0.057753 | -0.0012774 | -0.0066245 | -0.0038303 | -0.0051575 | 0.00066224 | 0.072365 | 0.067832 | -0.010092 | 0.019012 | -0.0018522 | -0.16937 | 1.355 | -120.5841 | 1.4648 | -119.8975 | -120.6528 | -120.6528 | -0.55389 | 1.4099 | -120.7031 | 1.506 | -120.1035 | -120.4971 | -120.3918 | -0.01831 | -0.11902 | -0.009155 | 0.66833 | -0.086975 | -0.086975 | -0.068665 | -0.068665 | -0.13733 | -0.064087 | 0.032043 | 0.46234 | 0.17395 | 0.068665 | 0.31128 | 0.20599 | 0.68664 | 122.049 | 0.59967 | 122.2092 | 121.9391 | 122.113 | 121.9208 | 121.9757 | -122.0581 | -122.1771 | 122.0306 | 122.0718 | 120.3964 | 120.0119
1285.7188 | 122.2092 | -120.7214 | 1.4236 | 0.0016023 | -0.0007199 | 0.05818 | 0.054121 | -0.001491 | -0.0053427 | -0.0042575 | -0.0051575 | 0.00066224 | 0.070442 | 0.062491 | -0.010305 | 0.018585 | -0.002493 | -0.091553 | 1.2543 | -120.6894 | 1.3184 | -120.0394 | -120.7581 | -120.7809 | -0.54932 | 1.3458 | -120.8084 | 1.2634 | -120.3049 | -120.6757 | -120.6299 | 0.032044 | -0.16937 | -0.10529 | 0.68207 | -0.059509 | -0.036621 | -0.091553 | -0.068665 | -0.086975 | -0.07782 | -0.16022 | 0.41656 | 0.091553 | 0.045777 | 0.17853 | 0.13275 | 0.65002 | 122.0078 | 0.50354 | 122.0718 | 121.9437 | 122.1542 | 121.9757 | 122.0673 | -122.113 | -122.2321 | 122.0398 | 121.9849 | 120.6299 | 120.1721
1287.4062 | 122.2137 | -120.7123 | 1.4328 | -0.0060272 | 0.0001345 | 0.059035 | 0.057112 | 0.00085879 | -0.0089743 | -0.0025485 | -0.0051575 | 0.001944 | 0.074501 | 0.057364 | -0.0098779 | 0.017944 | -0.0037748 | -0.13275 | 1.2909 | -120.726 | 1.236 | -120.1309 | -120.8176 | -120.8496 | -0.63171 | 1.3824 | -120.8359 | 1.2634 | -120.3232 | -120.7031 | -120.639 | -0.013733 | -0.14191 | -0.19684 | 0.58136 | -0.13733 | -0.10529 | -0.1236 | -0.091553 | -0.1236 | -0.050354 | -0.16937 | 0.3891 | 0.073242 | 0.009155 | 0.19684 | 0.13275 | 0.59509 | 121.962 | 0.51269 | 122.0993 | 122.0169 | 122.2183 | 122.0032 | 122.0947 | -122.1588 | -122.2687 | 121.9482 | 121.9757 | 120.5795 | 120.0806
1289.1562 | 122.2366 | -120.7031 | 1.442 | -0.013657 | 0.0012027 | 0.059248 | 0.059248 | -0.002132 | -0.0059835 | -0.0025485 | -0.0051575 | 0.0032256 | 0.072151 | 0.0689 | -0.011587 | 0.020721 | -0.002493 | -0.09613 | 1.2726 | -120.7123 | 1.3 | -120.0623 | -120.7855 | -120.8221 | -0.53101 | 1.3504 | -120.8267 | 1.3275 | -120.2728 | -120.6665 | -120.5658 | -0.009155 | -0.16937 | -0.14191 | 0.64087 | -0.11902 | -0.082397 | -0.10986 | -0.073242 | -0.1236 | -0.091553 | -0.11444 | 0.4303 | 0.13733 | 0.036621 | 0.26093 | 0.16022 | 0.65002 | 122.0123 | 0.55389 | 122.1542 | 121.9849 | 122.1771 | 121.9757 | 122.0535 | -122.1542 | -122.2687 | 122.0032 | 122.0306 | 120.607 | 120.1721
1290.9062 | 122.2549 | -120.7306 | 1.3687 | -0.0060272 | 0.0018435 | 0.059248 | 0.058607 | -0.00042301 | -0.0061971 | -0.0036167 | -0.0051575 | 0.0034392 | 0.072151 | 0.063559 | -0.01116 | 0.022644 | -0.0009976 | -0.07782 | 1.2405 | -120.7535 | 1.2543 | -120.0897 | -120.8313 | -120.845 | -0.54932 | 1.3092 | -120.8771 | 1.2817 | -120.3186 | -120.726 | -120.6253 | -0.022888 | -0.12817 | -0.11444 | 0.64087 | -0.11444 | -0.10071 | -0.091553 | -0.07782 | -0.14648 | -0.059509 | -0.086975 | 0.41199 | 0.10529 | 0.004578 | 0.25177 | 0.15106 | 0.66376 | 122.0078 | 0.55847 | 122.1588 | 121.994 | 122.1863 | 121.9711 | 122.0398 | -122.1222 | -122.2458 | 121.9849 | 122.0123 | 120.6528 | 120.1813
1292.5938 | 122.2504 | -120.6802 | 1.4191 | -0.0060272 | 0.0009891 | 0.059035 | 0.057539 | -0.00042301 | -0.0044883 | -0.0019077 | -0.0051575 | 2.1442e-05 | 0.07151 | 0.065268 | -0.010519 | 0.019226 | -0.0016384 | -0.091553 | 1.2909 | -120.7077 | 1.3184 | -120.0302 | -120.7809 | -120.7855 | -0.55389 | 1.3779 | -120.7901 | 1.3367 | -120.2591 | -120.6436 | -120.5521 | -0.027466 | -0.12817 | -0.10071 | 0.65002 | -0.10528 | -0.10071 | -0.077819 | -0.073242 | -0.10986 | -0.041198 | -0.082397 | 0.42114 | 0.12817 | 0.036621 | 0.23804 | 0.14648 | 0.67749 | 122.0261 | 0.53101 | 122.1268 | 121.9986 | 122.168 | 121.9711 | 122.0581 | -122.1268 | -122.2092 | 121.9986 | 122.0169 | 120.5887 | 120.1263
1294.2812 | 122.2504 | -120.5704 | 1.5564 | -0.013657 | 0.0003483 | 0.059035 | 0.056898 | -0.0034136 | -0.0055563 | -0.0010531 | -0.0021057 | 0.0023712 | 0.071297 | 0.065268 | -0.010305 | 0.019012 | -0.0014248 | -0.10071 | 1.3779 | -120.6207 | 1.3962 | -119.9661 | -120.6894 | -120.694 | -0.56763 | 1.4557 | -120.6848 | 1.4557 | -120.1355 | -120.52 | -120.4422 | -0.050354 | -0.17853 | -0.16022 | 0.60425 | -0.1236 | -0.11902 | -0.073242 | -0.068664 | -0.11444 | -0.10071 | -0.10071 | 0.43488 | 0.12817 | 0.050354 | 0.24261 | 0.16479 | 0.6546 | 122.0169 | 0.54932 | 122.1405 | 121.9986 | 122.1405 | 121.9482 | 122.0261 | -122.1771 | -122.2412 | 121.9666 | 122.0261 | 120.4697 | 120.0027
1296.0312 | 122.2641 | -119.5038 | 2.5772 | -0.013657 | 0.0007755 | 0.057753 | 0.054549 | -0.0023456 | -0.0070517 | -0.0044711 | -0.0051575 | -0.0023286 | 0.072792 | 0.066977 | -0.0096643 | 0.018799 | -0.0031338 | -0.16479 | 2.4033 | -119.5084 | 2.5314 | -118.8126 | -119.5816 | -119.5679 | -0.59509 | 2.4857 | -119.6045 | 2.536 | -119.0781 | -119.4305 | -119.3527 | -0.004578 | -0.17395 | -0.045776 | 0.69122 | -0.064087 | -0.07782 | -0.059509 | -0.073242 | -0.10071 | -0.091552 | -0.041198 | 0.42572 | 0.15106 | 0.073242 | 0.25177 | 0.17395 | 0.6958 | 122.0398 | 0.52643 | 122.1405 | 121.9116 | 122.0901 | 121.907 | 121.9894 | -122.0856 | -122.1817 | 122.0352 | 122.0398 | 119.339 | 118.9087
1297.7969 | 122.3328 | -119.7418 | 2.3117 | -0.013657 | 0.0007755 | 0.060103 | 0.057967 | -0.0017048 | -0.0066245 | -0.0031895 | -0.0051575 | 0.001944 | 0.072151 | 0.063987 | -0.012655 | 0.018372 | -0.0027066 | -0.14648 | 2.1515 | -119.7693 | 2.2842 | -119.0872 | -119.8151 | -119.8288 | -0.56763 | 2.2156 | -119.8517 | 2.3163 | -119.2932 | -119.6777 | -119.5724 | -0.027466 | -0.16022 | -0.027466 | 0.6546 | -0.086975 | -0.073242 | -0.059509 | -0.045776 | -0.10986 | -0.096131 | 0.004577 | 0.44861 | 0.16937 | 0.064087 | 0.27924 | 0.17395 | 0.68207 | 122.0535 | 0.55847 | 122.168 | 121.9208 | 122.0673 | 121.8933 | 121.9574 | -122.081 | -122.1634 | 122.0261 | 122.0581 | 119.5953 | 119.1742
1299.5469 | 122.1909 | -117.2516 | 4.866 | -0.013657 | 0.0044071 | 0.058821 | 0.059035 | 0.0036358 | -0.0064109 | -0.0014805 | -0.0082093 | 0.003012 | 0.074501 | 0.063346 | -0.010732 | 0.019226 | -0.0012112 | -0.09613 | 4.7333 | -117.2287 | 4.7607 | -116.629 | -117.3615 | -117.3706 | -0.60425 | 4.7745 | -117.3569 | 4.7424 | -116.8945 | -117.247 | -117.1555 | 0.022888 | -0.13275 | -0.10529 | 0.62256 | -0.11902 | -0.10986 | -0.14191 | -0.13275 | -0.10529 | -0.091553 | -0.1236 | 0.35706 | 0.09613 | 0.004578 | 0.20142 | 0.10986 | 0.59967 | 121.9894 | 0.46234 | 122.0993 | 121.962 | 122.1313 | 121.9849 | 122.0261 | -122.0947 | -122.2229 | 122.0123 | 121.994 | 117.1555 | 116.6473
1301.2188 | 122.2687 | -117.1555 | 4.9484 | -0.013657 | 0.0007755 | 0.05818 | 0.054121 | -0.0017048 | -0.0053427 | -0.0034031 | -0.0051575 | -0.00061956 | 0.071083 | 0.05886 | -0.010519 | 0.017944 | -0.0033474 | -0.045776 | 4.7745 | -117.1555 | 4.9164 | -116.4642 | -117.1783 | -117.1829 | -0.50812 | 4.8614 | -117.2562 | 4.8752 | -116.7252 | -117.0822 | -117.0227 | 0 | -0.17395 | -0.032043 | 0.69122 | -0.027465 | -0.022888 | -0.027465 | -0.022888 | -0.10071 | -0.086975 | -0.073242 | 0.4303 | 0.13275 | 0.073243 | 0.23346 | 0.17395 | 0.69122 | 122.0718 | 0.53101 | 122.1313 | 121.9299 | 122.1176 | 121.9299 | 122.0169 | -122.1039 | -122.2046 | 122.0718 | 122.0306 | 117.1097 | 116.6473
1302.9688 | 122.3099 | -116.716 | 5.3192 | -0.0060272 | 0.0039799 | 0.059676 | 0.055403 | 0.0040632 | -0.0034201 | -0.0029759 | -0.0051575 | 0.00066224 | 0.071083 | 0.069327 | -0.012441 | 0.018158 | -0.0012112 | -0.15564 | 5.2048 | -116.7068 | 5.3467 | -116.066 | -116.7938 | -116.7892 | -0.56763 | 5.2597 | -116.835 | 5.3741 | -116.2674 | -116.6473 | -116.5283 | 0.009155 | -0.11444 | 0.027466 | 0.65002 | -0.073243 | -0.07782 | -0.082398 | -0.086975 | -0.11902 | -0.059509 | 0.054932 | 0.44861 | 0.18768 | 0.068664 | 0.3067 | 0.18768 | 0.64087 | 122.0535 | 0.56763 | 122.2092 | 121.9116 | 122.0947 | 121.9208 | 121.9757 | -122.0261 | -122.1542 | 122.0627 | 122.0901 | 116.5604 | 116.1484
1304.7188 | 122.319 | -115.6082 | 6.4362 | 0.0016023 | -0.0011471 | 0.057753 | 0.055617 | 4.192e-06 | -0.0087607 | 1.4934e-05 | 0.0009461 | 0.00066224 | 0.072151 | 0.060569 | -0.011801 | 0.018585 | -0.002493 | -0.032043 | 6.2805 | -115.6403 | 6.4819 | -114.8895 | -115.6128 | -115.6448 | -0.46234 | 6.3446 | -115.7272 | 6.4636 | -115.1367 | -115.5029 | -115.4663 | -0.032044 | -0.15564 | 0.045777 | 0.71869 | -0.036621 | -0.004578 | -0.004577 | 0.027466 | -0.11902 | -0.091553 | 0.027466 | 0.4715 | 0.14191 | 0.10528 | 0.26093 | 0.2243 | 0.75073 | 122.1222 | 0.59051 | 122.1909 | 121.9208 | 122.0718 | 121.8887 | 121.9528 | -122.0764 | -122.1634 | 122.0901 | 122.0718 | 115.5762 | 115.1459
1306.4219 | 122.2 | -116.2766 | 5.8411 | -0.021286 | -7.9104e-05 | 0.057539 | 0.056044 | -0.0023456 | -0.0068381 | -0.0012669 | -0.0051575 | 0.0017304 | 0.071083 | 0.062918 | -0.010732 | 0.018372 | -0.0029202 | -0.11444 | 5.6992 | -116.2903 | 5.7083 | -115.7135 | -116.3956 | -116.4139 | -0.63171 | 5.777 | -116.4001 | 5.69 | -115.9378 | -116.2949 | -116.2216 | -0.013733 | -0.14191 | -0.13275 | 0.56305 | -0.13733 | -0.11902 | -0.1236 | -0.10529 | -0.1236 | -0.064086 | -0.15106 | 0.33875 | 0.054931 | -0.018311 | 0.17853 | 0.10529 | 0.57678 | 121.9986 | 0.46234 | 122.0901 | 121.9894 | 122.1771 | 121.9757 | 122.0535 | -122.1313 | -122.2412 | 121.9849 | 121.9666 | 116.1621 | 115.6448
1308.1719 | 122.287 | -116.5237 | 5.5206 | -0.013657 | 0.0024845 | 0.059676 | 0.057112 | -0.0029864 | -0.0074789 | -0.0010531 | -0.0051575 | 0.003653 | 0.073433 | 0.060782 | -0.0098779 | 0.019226 | 0.0007114 | -0.22888 | 5.4062 | -116.5649 | 5.4428 | -115.9561 | -116.6885 | -116.684 | -0.66834 | 5.4565 | -116.6748 | 5.5023 | -116.1438 | -116.5192 | -116.4001 | -0.041198 | -0.11444 | -0.07782 | 0.56763 | -0.16022 | -0.16479 | -0.11902 | -0.1236 | -0.15106 | -0.064087 | -0.018311 | 0.37994 | 0.1236 | 0.004578 | 0.27466 | 0.15564 | 0.60883 | 122.0078 | 0.53101 | 122.1771 | 121.9711 | 122.1313 | 121.9299 | 121.9803 | -122.0856 | -122.1954 | 121.9666 | 122.0261 | 116.2949 | 115.8554
1309.9219 | 122.2733 | -116.7297 | 5.3467 | -0.013657 | -0.0005063 | 0.060744 | 0.057753 | -0.0017048 | -0.0055563 | -0.0021213 | -0.0021057 | 0.00066224 | 0.070869 | 0.063773 | -0.010732 | 0.017944 | -0.0048428 | -0.17395 | 5.1773 | -116.7343 | 5.2826 | -116.1209 | -116.8259 | -116.8167 | -0.64087 | 5.2505 | -116.8579 | 5.2963 | -116.3269 | -116.6702 | -116.5924 | -0.004578 | -0.16937 | -0.064087 | 0.60882 | -0.086975 | -0.096131 | -0.082397 | -0.091553 | -0.12817 | -0.096131 | -0.050354 | 0.40283 | 0.13733 | 0.059509 | 0.2655 | 0.18768 | 0.6134 | 122.0169 | 0.53101 | 122.1542 | 121.9116 | 122.1085 | 121.907 | 121.9803 | -122.081 | -122.2046 | 122.0123 | 122.0261 | 116.5558 | 116.0889
1311.6875 | 122.2321 | -117.2653 | 4.8706 | -0.0060272 | -0.0015743 | 0.057967 | 0.061385 | 0.0027814 | -0.0087607 | -0.0010531 | -0.0051575 | 0.0023712 | 0.071297 | 0.059928 | -0.010946 | 0.020294 | 0.0002842 | -0.09613 | 4.7241 | -117.2882 | 4.7195 | -116.6977 | -117.3706 | -117.3798 | -0.65918 | 4.7836 | -117.3843 | 4.7333 | -116.8671 | -117.247 | -117.1463 | -0.022888 | -0.14648 | -0.15106 | 0.56763 | -0.11444 | -0.10528 | -0.091553 | -0.082397 | -0.11902 | -0.086975 | -0.13733 | 0.39826 | 0.11902 | 0.018311 | 0.23804 | 0.13733 | 0.59051 | 122.0078 | 0.51727 | 122.1176 | 122.0123 | 122.168 | 121.9894 | 122.049 | -122.1588 | -122.2549 | 121.9849 | 121.9986 | 117.1692 | 116.6061
1313.4375 | 122.2458 | -116.9586 | 5.1407 | -0.013657 | 0.0018435 | 0.059248 | 0.058394 | -0.0019184 | -0.0047019 | -0.0036167 | -0.0021057 | 0.0010894 | 0.071938 | 0.062918 | -0.012228 | 0.01944 | 0.0017794 | -0.086975 | 5.0079 | -116.9998 | 5.0537 | -116.3544 | -117.0502 | -117.0776 | -0.60425 | 5.0858 | -117.0914 | 5.0583 | -116.5604 | -116.9357 | -116.8304 | -0.041199 | -0.13275 | -0.086975 | 0.60425 | -0.11902 | -0.091553 | -0.07782 | -0.050354 | -0.13275 | -0.054932 | -0.082397 | 0.39825 | 0.12817 | 0.022888 | 0.26093 | 0.15564 | 0.64545 | 122.0535 | 0.53101 | 122.1497 | 122.0078 | 122.1771 | 121.9666 | 122.0444 | -122.1405 | -122.2321 | 122.0123 | 122.0169 | 116.8716 | 116.3544
1315.125 | 122.3236 | -116.3177 | 5.6946 | -0.0060272 | 0.0026981 | 0.061171 | 0.057112 | -0.0029864 | -0.0044883 | -0.0029759 | -0.0082093 | 0.0015166 | 0.072578 | 0.062705 | -0.010946 | 0.019226 | 0.0002842 | -0.14191 | 5.5481 | -116.3315 | 5.7266 | -115.6677 | -116.3864 | -116.3956 | -0.6134 | 5.6305 | -116.4459 | 5.7449 | -115.8875 | -116.2491 | -116.1713 | -0.013733 | -0.14648 | 0.032044 | 0.65002 | -0.07782 | -0.068665 | -0.064087 | -0.054932 | -0.12817 | -0.064087 | 0.050354 | 0.4303 | 0.14648 | 0.068665 | 0.27466 | 0.19684 | 0.66376 | 122.0581 | 0.55847 | 122.1909 | 121.8796 | 122.0764 | 121.8658 | 121.9482 | -122.0261 | -122.1405 | 122.0444 | 122.0627 | 116.1758 | 115.7043
1316.875 | 122.2092 | -116.3406 | 5.8182 | -0.028916 | -0.0028561 | 0.058394 | 0.056471 | -0.0053362 | -0.0074789 | -0.00062587 | -0.0021057 | 0.001303 | 0.075783 | 0.05886 | -0.010946 | 0.019012 | -0.0020658 | -0.11444 | 5.6671 | -116.3315 | 5.6717 | -115.7364 | -116.4139 | -116.4276 | -0.66834 | 5.7266 | -116.4368 | 5.6717 | -115.947 | -116.3132 | -116.2125 | 0.009155 | -0.15106 | -0.14648 | 0.60425 | -0.086975 | -0.073242 | -0.09613 | -0.082397 | -0.096131 | -0.091552 | -0.14648 | 0.39368 | 0.12817 | 0.027466 | 0.22431 | 0.1236 | 0.59509 | 122.0032 | 0.48981 | 122.1085 | 121.9986 | 122.1634 | 122.0078 | 122.0673 | -122.1497 | -122.2549 | 122.0123 | 122.0123 | 116.2262 | 115.6723
1318.5469 | 122.3007 | -116.4047 | 5.6396 | -0.0060272 | 0.0022709 | 0.060316 | 0.056258 | -0.00555 | -0.0036337 | -0.0031895 | -0.0051575 | -0.00040596 | 0.07151 | 0.060782 | -0.01116 | 0.016876 | 0.0013522 | -0.1831 | 5.484 | -116.4093 | 5.6625 | -115.741 | -116.4825 | -116.4642 | -0.62256 | 5.5527 | -116.5283 | 5.6351 | -116.0065 | -116.3727 | -116.2811 | -0.004578 | -0.15564 | 0.022889 | 0.66376 | -0.059509 | -0.07782 | -0.054931 | -0.073242 | -0.1236 | -0.086975 | -0.004577 | 0.39825 | 0.1236 | 0.032043 | 0.24719 | 0.15564 | 0.66833 | 122.0718 | 0.52185 | 122.1634 | 121.8933 | 122.081 | 121.8887 | 121.9574 | -122.0489 | -122.168 | 122.0673 | 122.0398 | 116.2216 | 115.7822
1320.2344 | 122.2733 | -118.8858 | 3.241 | -0.013657 | -0.0024289 | 0.06053 | 0.059462 | -0.0019184 | -0.0055563 | -0.00041227 | -0.0021057 | 0.0017304 | 0.06916 | 0.064627 | -0.012228 | 0.017944 | -0.0018522 | -0.10529 | 3.1265 | -118.8583 | 3.1586 | -118.2358 | -118.9316 | -118.9682 | -0.6546 | 3.186 | -118.9636 | 3.1815 | -118.4509 | -118.8126 | -118.7256 | 0.027466 | -0.11444 | -0.082398 | 0.65002 | -0.082398 | -0.045777 | -0.10986 | -0.073243 | -0.07782 | -0.054932 | -0.059509 | 0.43487 | 0.16022 | 0.073242 | 0.23804 | 0.15106 | 0.62256 | 122.0169 | 0.51269 | 122.1451 | 121.9849 | 122.1497 | 122.0123 | 122.0718 | -122.0993 | -122.2046 | 122.0444 | 122.0673 | 118.7805 | 118.2312
1321.9844 | 122.3648 | -119.6411 | 2.4216 | -0.0060272 | -0.0007199 | 0.057753 | 0.054976 | -0.001491 | -0.0076925 | -0.00083947 | -0.0051575 | -0.00040596 | 0.074074 | 0.067832 | -0.010519 | 0.017944 | -0.0037748 | -0.13275 | 2.2751 | -119.6732 | 2.417 | -118.9407 | -119.6732 | -119.6686 | -0.63629 | 2.3575 | -119.7693 | 2.4399 | -119.1467 | -119.5038 | -119.4489 | -0.032044 | -0.14649 | -0.004578 | 0.70038 | -0.027466 | -0.032044 | 0.004578 | 0 | -0.12817 | -0.064087 | 0.01831 | 0.49438 | 0.19226 | 0.13733 | 0.32043 | 0.2655 | 0.73242 | 122.0901 | 0.62256 | 122.2092 | 121.9482 | 122.1268 | 121.9162 | 121.9986 | -122.0947 | -122.1909 | 122.0581 | 122.081 | 119.5084 | 119.0048
1323.7344 | 122.2412 | -119.9341 | 2.179 | -0.021286 | 0.0020571 | 0.059889 | 0.058821 | 0.00021799 | -0.0047019 | -0.0023349 | -0.0051575 | 0.00023504 | 0.07151 | 0.066123 | -0.01116 | 0.020081 | -0.0022794 | -0.22888 | 2.0462 | -119.957 | 2.0142 | -119.3619 | -120.108 | -120.0943 | -0.81024 | 2.1103 | -120.0531 | 2.092 | -119.5633 | -119.9387 | -119.8196 | -0.022888 | -0.13275 | -0.1648 | 0.5722 | -0.16022 | -0.17395 | -0.13733 | -0.15106 | -0.11902 | -0.068664 | -0.086975 | 0.37079 | 0.11444 | -0.004578 | 0.23346 | 0.11444 | 0.59509 | 121.9711 | 0.48981 | 122.1451 | 122.0032 | 122.1634 | 121.9803 | 122.0444 | -122.1359 | -122.2321 | 121.9482 | 122.0261 | 119.7052 | 119.1238
1325.4062 | 122.2046 | -119.9936 | 2.1881 | -0.0060272 | -0.0017881 | 0.056898 | 0.057112 | -0.0012774 | -0.0040609 | -0.00062587 | -0.0051575 | 0.0025848 | 0.072151 | 0.064414 | -0.010732 | 0.01944 | -0.0009976 | -0.13275 | 2.0279 | -119.9936 | 1.9913 | -119.3665 | -120.0943 | -120.1126 | -0.737 | 2.1011 | -120.0897 | 2.005 | -119.5816 | -119.9615 | -119.8791 | 0 | -0.16022 | -0.19684 | 0.62714 | -0.11902 | -0.10071 | -0.11902 | -0.10071 | -0.096131 | -0.086975 | -0.1831 | 0.41199 | 0.11444 | 0.032043 | 0.21057 | 0.12817 | 0.62714 | 121.9849 | 0.50812 | 122.0947 | 122.0215 | 122.1909 | 122.0215 | 122.0947 | -122.1817 | -122.2778 | 121.9849 | 121.9986 | 119.8608 | 119.2566
1327.1562 | 122.3419 | -119.7418 | 2.3254 | -0.013657 | 0.0044071 | 0.061385 | 0.057539 | -0.00042301 | -0.0057699 | -0.0027621 | -0.0051575 | 0.001944 | 0.07151 | 0.058646 | -0.012655 | 0.020294 | 0.0011386 | -0.16479 | 2.1835 | -119.7418 | 2.3071 | -119.0552 | -119.7876 | -119.7922 | -0.67749 | 2.2522 | -119.8608 | 2.3621 | -119.2795 | -119.6503 | -119.5221 | 0 | -0.14191 | -0.01831 | 0.68664 | -0.050354 | -0.045777 | -0.050354 | -0.045777 | -0.11902 | -0.073242 | 0.036622 | 0.46234 | 0.21973 | 0.091552 | 0.33875 | 0.21057 | 0.68664 | 122.049 | 0.58136 | 122.2229 | 121.9254 | 122.113 | 121.9254 | 121.994 | -122.0673 | -122.1863 | 122.049 | 122.1039 | 119.577 | 119.0643
1328.9062 | 122.1863 | -120.1172 | 2.0325 | -0.013657 | 0.0001345 | 0.057539 | 0.05583 | -0.001491 | -0.0053427 | -0.0038303 | -0.0082093 | 0.00066224 | 0.070656 | 0.064841 | -0.012014 | 0.017731 | -0.0046292 | -0.14191 | 1.8906 | -120.1263 | 1.8723 | -119.4992 | -120.1996 | -120.2316 | -0.76904 | 1.9684 | -120.2271 | 1.8723 | -119.7189 | -120.1035 | -120.0027 | -0.009156 | -0.14191 | -0.16022 | 0.61798 | -0.11444 | -0.082398 | -0.10528 | -0.073242 | -0.10986 | -0.064087 | -0.16022 | 0.39825 | 0.11444 | 0.013732 | 0.2243 | 0.1236 | 0.62714 | 121.9986 | 0.50812 | 122.0993 | 122.0169 | 122.1954 | 122.0078 | 122.0856 | -122.1588 | -122.2595 | 121.9894 | 121.9894 | 119.9753 | 119.3481
1330.5938 | 122.2137 | -120.2591 | 1.9089 | 0.0016023 | -0.0022153 | 0.057539 | 0.054335 | -0.0023456 | -0.0064109 | -0.0025485 | -0.0021057 | 0.00087584 | 0.073006 | 0.06655 | -0.010519 | 0.020508 | -0.0018522 | -0.086975 | 1.7532 | -120.2499 | 1.7578 | -119.6274 | -120.3323 | -120.3415 | -0.72784 | 1.8402 | -120.3278 | 1.7487 | -119.8425 | -120.2179 | -120.1355 | 0.009155 | -0.15564 | -0.15106 | 0.63171 | -0.082398 | -0.073242 | -0.091553 | -0.082397 | -0.068665 | -0.068665 | -0.16022 | 0.41657 | 0.1236 | 0.041198 | 0.19226 | 0.10986 | 0.62256 | 122.0078 | 0.48523 | 122.0764 | 122.0032 | 122.168 | 122.0123 | 122.0993 | -122.1588 | -122.2366 | 122.0169 | 122.0078 | 120.1721 | 119.5312
1332.2812 | 122.2504 | -120.2087 | 1.8997 | -0.013657 | 0.0020571 | 0.058607 | 0.057967 | -0.0019184 | -0.0059835 | -0.0036167 | -0.0021057 | 0.001944 | 0.073647 | 0.061423 | -0.010519 | 0.020721 | 7.04e-05 | -0.23346 | 1.7853 | -120.2316 | 1.7715 | -119.6045 | -120.3506 | -120.3506 | -0.80109 | 1.8448 | -120.3186 | 1.8311 | -119.8059 | -120.1813 | -120.0348 | -0.022888 | -0.11444 | -0.12817 | 0.60425 | -0.14191 | -0.14191 | -0.11902 | -0.11902 | -0.10986 | -0.054931 | -0.068664 | 0.40283 | 0.17395 | 0.027466 | 0.28381 | 0.13733 | 0.62714 | 122.0032 | 0.5127 | 122.1497 | 122.0169 | 122.1634 | 121.994 | 122.0535 | -122.1313 | -122.2183 | 121.9803 | 122.0398 | 119.9753 | 119.4077
1334.0312 | 122.3328 | -120.0577 | 2.0279 | -0.0060272 | -0.0030697 | 0.060744 | 0.053267 | -0.0034136 | -0.0072653 | -0.0016941 | -0.0051575 | -0.0012604 | 0.070869 | 0.067832 | -0.010732 | 0.019012 | -0.0031338 | -0.15106 | 1.8814 | -120.1126 | 2.005 | -119.371 | -120.0897 | -120.0897 | -0.6958 | 1.9547 | -120.1538 | 2.0325 | -119.5633 | -119.9478 | -119.8517 | -0.054932 | -0.14648 | -0.022888 | 0.68664 | -0.032044 | -0.032044 | 0.022888 | 0.022888 | -0.096131 | -0.073242 | 0.004578 | 0.49438 | 0.20599 | 0.10986 | 0.30212 | 0.20599 | 0.74158 | 122.1176 | 0.59052 | 122.1863 | 121.994 | 122.1085 | 121.9391 | 122.0123 | -122.1405 | -122.1817 | 122.0627 | 122.0901 | 119.9066 | 119.3619
1335.7188 | 122.2778 | -120.1401 | 1.9455 | -0.021286 | 0.0026981 | 0.059889 | 0.055617 | -0.00555 | -0.0096151 | -0.0019077 | -0.0051575 | 0.0015166 | 0.071297 | 0.060996 | -0.0096643 | 0.01944 | -0.0022794 | -0.19226 | 1.7944 | -120.1721 | 1.8768 | -119.4901 | -120.2316 | -120.2316 | -0.75531 | 1.8631 | -120.2728 | 1.8906 | -119.7281 | -120.0989 | -119.9982 | -0.032043 | -0.15106 | -0.068665 | 0.65002 | -0.091552 | -0.091552 | -0.059509 | -0.059509 | -0.13275 | -0.082398 | -0.054932 | 0.41199 | 0.14191 | 0.041199 | 0.27466 | 0.17395 | 0.68207 | 122.0489 | 0.54474 | 122.1634 | 121.9666 | 122.1359 | 121.9345 | 122.0032 | -122.1176 | -122.2183 | 122.0169 | 122.0306 | 119.9478 | 119.3848
1337.4062 | 122.3282 | -120.163 | 1.8906 | -0.013657 | 0.0029117 | 0.059676 | 0.05583 | 0.0017132 | -0.0087607 | -0.00062587 | -0.0082093 | 0.0015166 | 0.071297 | 0.067405 | -0.011373 | 0.019226 | -0.0020658 | -0.16022 | 1.7349 | -120.1859 | 1.886 | -119.5038 | -120.2271 | -120.2454 | -0.72784 | 1.8173 | -120.2866 | 1.918 | -119.7189 | -120.0943 | -119.9707 | -0.022888 | -0.15564 | -0.004578 | 0.65918 | -0.082397 | -0.064087 | -0.059509 | -0.041199 | -0.1236 | -0.073242 | 0.027466 | 0.44403 | 0.19226 | 0.068665 | 0.31586 | 0.19226 | 0.68207 | 122.0718 | 0.56763 | 122.2046 | 121.9208 | 122.1039 | 121.8979 | 121.9803 | -122.0764 | -122.1771 | 122.049 | 122.081 | 120.0027 | 119.4351
1339.1562 | 122.2275 | -120.1584 | 1.9867 | -0.0060272 | -0.0017881 | 0.058821 | 0.057753 | 4.192e-06 | -0.0074789 | 1.4934e-05 | -0.0082093 | 0.0010894 | 0.07151 | 0.069327 | -0.013296 | 0.020081 | -0.0044156 | -0.10986 | 1.8539 | -120.1813 | 1.8219 | -119.5633 | -120.2591 | -120.2774 | -0.79193 | 1.9135 | -120.2682 | 1.8631 | -119.7556 | -120.1401 | -120.0302 | -0.022888 | -0.13275 | -0.1648 | 0.59509 | -0.11902 | -0.10071 | -0.096131 | -0.07782 | -0.10986 | -0.073242 | -0.1236 | 0.40283 | 0.12817 | 0.01831 | 0.23804 | 0.12817 | 0.61798 | 122.0032 | 0.5127 | 122.1313 | 122.0352 | 122.1817 | 122.0123 | 122.0718 | -122.168 | -122.2549 | 121.9803 | 122.0215 | 120.0485 | 119.3665
1340.9062 | 122.168 | -120.1447 | 2.0142 | -0.013657 | 0.0029117 | 0.06053 | 0.058607 | -0.001491 | -0.0053427 | -0.0021213 | -0.0082093 | 0.003012 | 0.073219 | 0.069754 | -0.012441 | 0.020081 | -0.0029202 | -0.16937 | 1.8768 | -120.1309 | 1.8448 | -119.577 | -120.2911 | -120.2774 | -0.86975 | 1.9455 | -120.2545 | 1.8631 | -119.7922 | -120.1721 | -120.0165 | 0.013733 | -0.13733 | -0.16937 | 0.56763 | -0.13275 | -0.14648 | -0.14648 | -0.16022 | -0.10986 | -0.068664 | -0.15106 | 0.35248 | 0.12817 | -0.027466 | 0.23804 | 0.082398 | 0.55389 | 121.9757 | 0.46234 | 122.1176 | 122.0078 | 122.2 | 122.0215 | 122.0901 | -122.1451 | -122.2687 | 121.9894 | 122.0078 | 119.9753 | 119.2749
1342.6719 | 122.2916 | -120.1309 | 1.9547 | -0.021286 | 0.0020571 | 0.060103 | 0.058394 | 0.0017132 | -0.0053427 | -0.0038303 | -0.0082093 | 0.0021576 | 0.071938 | 0.06655 | -0.012441 | 0.020081 | -0.0029202 | -0.23346 | 1.8448 | -120.1584 | 1.8494 | -119.5404 | -120.2911 | -120.2637 | -0.83771 | 1.9043 | -120.2362 | 1.9272 | -119.7098 | -120.0851 | -119.9615 | -0.027466 | -0.10986 | -0.10529 | 0.59051 | -0.13275 | -0.16022 | -0.10529 | -0.13275 | -0.10529 | -0.050354 | -0.027466 | 0.42114 | 0.16937 | 0.045776 | 0.27466 | 0.15106 | 0.61798 | 122.0078 | 0.52643 | 122.1634 | 122.0032 | 122.1405 | 121.9757 | 122.0352 | -122.113 | -122.1909 | 121.9803 | 122.0581 | 119.8975 | 119.2932
1344.4219 | 122.3328 | -120.2042 | 1.8723 | -0.013657 | -0.0011471 | 0.056685 | 0.054335 | -0.00020941 | -0.0064109 | -0.0025485 | -0.0082093 | -0.00061956 | 0.072792 | 0.060141 | -0.01116 | 0.018158 | -0.0033474 | -0.15106 | 1.7166 | -120.2133 | 1.8402 | -119.5267 | -120.2454 | -120.2454 | -0.76446 | 1.8173 | -120.3186 | 1.8814 | -119.7098 | -120.076 | -119.9844 | -0.009155 | -0.15564 | -0.032043 | 0.67749 | -0.041198 | -0.041198 | -0.032043 | -0.032043 | -0.11444 | -0.054931 | 0.009156 | 0.49438 | 0.21973 | 0.12817 | 0.33417 | 0.24261 | 0.68665 | 122.0535 | 0.60883 | 122.2 | 121.9299 | 122.1359 | 121.9208 | 122.0215 | -122.0856 | -122.1909 | 122.0444 | 122.0856 | 120.0531 | 119.4397
1346.1094 | 122.3145 | -119.9158 | 2.1561 | -0.013657 | 0.0029117 | 0.060316 | 0.057753 | -0.001491 | -0.0042745 | -0.0042575 | -0.0082093 | 0.00087584 | 0.070442 | 0.060996 | -0.012228 | 0.021149 | -0.0020658 | -0.21973 | 2.0233 | -119.9615 | 2.0737 | -119.3115 | -120.0256 | -120.0485 | -0.81024 | 2.0599 | -120.0531 | 2.1561 | -119.4946 | -119.8746 | -119.6732 | -0.045777 | -0.13275 | -0.082398 | 0.60425 | -0.13275 | -0.10986 | -0.086975 | -0.064087 | -0.13733 | -0.09613 | 0 | 0.42114 | 0.24261 | 0.041198 | 0.37994 | 0.17853 | 0.65002 | 122.0352 | 0.55847 | 122.2092 | 121.9849 | 122.113 | 121.9391 | 121.9757 | -122.1176 | -122.2092 | 121.9894 | 122.0718 | 119.696 | 119.1055
1347.8125 | 122.2733 | -118.7988 | 3.3279 | -0.013657 | -0.0011471 | 0.060316 | 0.056898 | -0.003841 | -0.0061971 | -0.0010531 | -0.0082093 | 0.0015166 | 0.070442 | 0.061423 | -0.012014 | 0.019653 | -0.0031338 | -0.054932 | 3.154 | -118.7759 | 3.3051 | -118.0801 | -118.7805 | -118.7988 | -0.70496 | 3.2547 | -118.895 | 3.2867 | -118.3136 | -118.6798 | -118.5562 | 0.022888 | -0.17395 | -0.022888 | 0.71869 | 0 | 0.01831 | -0.022888 | -0.004578 | -0.09613 | -0.073242 | -0.041199 | 0.48523 | 0.24262 | 0.11902 | 0.33875 | 0.21515 | 0.6958 | 122.081 | 0.58136 | 122.1817 | 121.9299 | 122.1497 | 121.9528 | 122.0535 | -122.1039 | -122.2229 | 122.1039 | 122.0856 | 118.7439 | 118.0939
1349.5625 | 122.3282 | -119.0414 | 3.0121 | -0.0060272 | 0.0014163 | 0.057539 | 0.059035 | 0.00064519 | -0.0072653 | -0.0063937 | -0.0082093 | 0.001303 | 0.070442 | 0.062064 | -0.011373 | 0.020721 | 0.0024204 | -0.19226 | 2.8748 | -119.0872 | 2.9938 | -118.4052 | -119.133 | -119.133 | -0.77362 | 2.9388 | -119.1513 | 3.0396 | -118.5974 | -118.9819 | -118.8034 | -0.045776 | -0.13733 | -0.018311 | 0.63629 | -0.091553 | -0.091553 | -0.045777 | -0.045777 | -0.10986 | -0.073242 | 0.027466 | 0.44403 | 0.23804 | 0.059509 | 0.3479 | 0.16937 | 0.68207 | 122.081 | 0.55389 | 122.1909 | 121.962 | 122.0901 | 121.9162 | 121.9803 | -122.0993 | -122.1634 | 122.0352 | 122.081 | 118.8492 | 118.2678
1351.25 | 122.2183 | -118.6615 | 3.4836 | -0.013657 | -0.0005063 | 0.058394 | 0.054335 | -0.00085021 | -0.0047019 | -0.0025485 | -0.0082093 | 0.00044864 | 0.072365 | 0.064627 | -0.010305 | 0.020508 | -0.003561 | -0.073242 | 3.2913 | -118.6661 | 3.3554 | -118.0298 | -118.721 | -118.7576 | -0.80566 | 3.4103 | -118.7714 | 3.3417 | -118.2724 | -118.6386 | -118.5059 | -0.004578 | -0.19226 | -0.12817 | 0.63171 | -0.09613 | -0.059509 | -0.091552 | -0.054931 | -0.10986 | -0.073243 | -0.14191 | 0.3891 | 0.15564 | 0.022888 | 0.2655 | 0.13275 | 0.63629 | 122.0215 | 0.49896 | 122.113 | 121.9574 | 122.1817 | 121.9528 | 122.0718 | -122.1497 | -122.2549 | 122.0169 | 122.0032 | 118.5883 | 117.8558
1353 | 122.319 | -118.8171 | 3.2867 | -0.021286 | -7.9104e-05 | 0.059248 | 0.054335 | -0.0036274 | -0.0053427 | -0.0031895 | -0.0051575 | 0.00044864 | 0.07386 | 0.064841 | -0.010732 | 0.018372 | 0.0002842 | -0.14648 | 3.1357 | -118.8309 | 3.2501 | -118.1396 | -118.8492 | -118.8538 | -0.77362 | 3.2043 | -118.8995 | 3.2867 | -118.3182 | -118.6844 | -118.5562 | -0.013733 | -0.15106 | -0.036621 | 0.67749 | -0.036621 | -0.032043 | -0.022888 | -0.01831 | -0.082397 | -0.082397 | 0 | 0.49896 | 0.26093 | 0.13275 | 0.34332 | 0.21515 | 0.69122 | 122.081 | 0.58136 | 122.1863 | 121.9666 | 122.1039 | 121.9528 | 122.0215 | -122.1176 | -122.1863 | 122.0673 | 122.1039 | 118.6707 | 118.0435
1354.75 | 122.3236 | -118.5013 | 3.5706 | -0.0060272 | 0.0046207 | 0.060744 | 0.057326 | -0.002132 | -0.0049155 | -0.0016941 | -0.0051575 | 0.0027984 | 0.071297 | 0.063773 | -0.01116 | 0.019653 | -0.0037748 | -0.13275 | 3.4195 | -118.483 | 3.5889 | -117.7917 | -118.5196 | -118.5333 | -0.76446 | 3.5065 | -118.5974 | 3.6118 | -118.0206 | -118.3914 | -118.277 | 0.018311 | -0.15106 | 0.01831 | 0.70953 | -0.032043 | -0.01831 | -0.050354 | -0.036621 | -0.09613 | -0.064087 | 0.041198 | 0.48065 | 0.2243 | 0.10986 | 0.32043 | 0.20599 | 0.69122 | 122.0718 | 0.57678 | 122.2092 | 121.9025 | 122.1039 | 121.9208 | 122.0078 | -122.0535 | -122.168 | 122.0901 | 122.113 | 118.3685 | 117.7368
1356.4375 | 122.2 | -118.4738 | 3.653 | -0.0060272 | 0.0026981 | 0.058821 | 0.06053 | 0.00085879 | -0.0047019 | -0.0023349 | -0.0021057 | 0.0032256 | 0.07151 | 0.065268 | -0.011373 | 0.018585 | -0.002493 | -0.21057 | 3.5248 | -118.515 | 3.4973 | -117.9382 | -118.6707 | -118.6569 | -0.92926 | 3.6072 | -118.5837 | 3.5339 | -118.1305 | -118.5059 | -118.364 | -0.041199 | -0.12817 | -0.15564 | 0.53558 | -0.1831 | -0.19684 | -0.14191 | -0.15564 | -0.10986 | -0.045776 | -0.11902 | 0.34332 | 0.10986 | -0.032043 | 0.21973 | 0.07782 | 0.57678 | 122.0123 | 0.45319 | 122.1176 | 122.0398 | 122.1909 | 121.9986 | 122.081 | -122.168 | -122.2366 | 121.9711 | 122.0078 | 118.2632 | 117.5446
1358.1875 | 122.1863 | -118.0618 | 4.0833 | -0.013657 | 0.0037661 | 0.060103 | 0.059035 | -0.00020941 | -0.0044883 | -0.0042575 | -0.0021057 | 0.0023712 | 0.074928 | 0.059714 | -0.010732 | 0.019653 | -0.0027066 | -0.19226 | 3.9276 | -118.0664 | 3.9185 | -117.4988 | -118.2083 | -118.2266 | -0.95215 | 4.01 | -118.1717 | 3.9276 | -117.7231 | -118.0939 | -117.9611 | -0.004577 | -0.15564 | -0.16479 | 0.56305 | -0.16479 | -0.14648 | -0.16022 | -0.14191 | -0.10986 | -0.073242 | -0.15564 | 0.33875 | 0.10071 | -0.032043 | 0.21057 | 0.07782 | 0.56763 | 121.9849 | 0.44861 | 122.0993 | 121.994 | 122.1817 | 121.9894 | 122.0718 | -122.1497 | -122.2549 | 121.9803 | 121.9894 | 117.8696 | 117.1097
1359.9375 | 122.2092 | -118.0344 | 4.0833 | -0.013657 | 0.0035525 | 0.060316 | 0.059462 | 0.0032086 | -0.0061971 | -0.00019867 | -0.0051575 | 0.003653 | 0.071297 | 0.067618 | -0.0092371 | 0.019226 | -0.0031338 | -0.13733 | 3.9368 | -118.0481 | 3.978 | -117.4255 | -118.1625 | -118.1671 | -0.88348 | 4.0146 | -118.1442 | 3.9688 | -117.6819 | -118.0527 | -117.9245 | -0.013733 | -0.14648 | -0.10529 | 0.60883 | -0.13275 | -0.12817 | -0.11902 | -0.11444 | -0.10986 | -0.068665 | -0.11444 | 0.35248 | 0.10986 | -0.01831 | 0.21973 | 0.091553 | 0.62256 | 122.0261 | 0.46234 | 122.113 | 121.9849 | 122.1588 | 121.9711 | 122.049 | -122.1313 | -122.2275 | 122.0123 | 122.0032 | 117.897 | 117.1509
1361.7031 | 122.2137 | -117.4255 | 4.7287 | -0.0060272 | -0.0034971 | 0.057967 | 0.057326 | -0.00555 | -0.0076925 | -0.0025485 | -0.0051575 | 0.001944 | 0.073006 | 0.06185 | -0.011373 | 0.018372 | -0.0056974 | -0.1236 | 4.5822 | -117.453 | 4.5822 | -116.8213 | -117.5034 | -117.5308 | -0.87891 | 4.6692 | -117.54 | 4.5822 | -117.0319 | -117.3981 | -117.3111 | -0.027466 | -0.14649 | -0.14649 | 0.60425 | -0.10529 | -0.07782 | -0.07782 | -0.050354 | -0.11444 | -0.05951 | -0.14649 | 0.39368 | 0.11444 | 0.027466 | 0.22888 | 0.14191 | 0.63171 | 122.0352 | 0.50812 | 122.1222 | 122.0352 | 122.2092 | 122.0078 | 122.0947 | -122.1817 | -122.2687 | 122.0078 | 122.0078 | 117.3019 | 116.5466
1363.4062 | 122.2321 | -116.5283 | 5.6122 | 0.0016023 | 0.0033389 | 0.060103 | 0.057967 | -0.00063661 | -0.0074789 | -0.0019077 | -0.0021057 | 0.0023712 | 0.075355 | 0.066336 | -0.012014 | 0.021149 | -0.0037748 | -0.086975 | 5.4565 | -116.5375 | 5.5344 | -115.9012 | -116.6107 | -116.6153 | -0.78278 | 5.5023 | -116.6245 | 5.5115 | -116.1301 | -116.4963 | -116.3681 | -0.009156 | -0.15564 | -0.07782 | 0.62714 | -0.086975 | -0.082398 | -0.077819 | -0.073242 | -0.096131 | -0.10986 | -0.10071 | 0.39825 | 0.16022 | 0.032043 | 0.25635 | 0.12817 | 0.63629 | 122.0718 | 0.49438 | 122.1359 | 121.994 | 122.1268 | 121.9849 | 122.0306 | -122.1497 | -122.2366 | 122.0627 | 122.0398 | 116.4413 | 115.7455
1365.1562 | 122.2137 | -113.681 | 8.4824 | -0.0060272 | -0.0020017 | 0.056044 | 0.055189 | -0.0010638 | -0.0055563 | -0.0023349 | -0.0051575 | 0.0023712 | 0.071083 | 0.061209 | -0.010946 | 0.020081 | -0.0029202 | -0.1236 | 8.3221 | -113.6948 | 8.3542 | -113.0997 | -113.7726 | -113.7863 | -0.84686 | 8.3817 | -113.7543 | 8.3633 | -113.3102 | -113.6627 | -113.5574 | -0.013733 | -0.16022 | -0.12817 | 0.58136 | -0.10529 | -0.091553 | -0.091553 | -0.07782 | -0.073242 | -0.10071 | -0.11902 | 0.37079 | 0.1236 | 0.01831 | 0.19684 | 0.091552 | 0.59509 | 122.0489 | 0.44403 | 122.1176 | 122.0169 | 122.1359 | 122.0032 | 122.0627 | -122.1771 | -122.2366 | 122.0352 | 122.0444 | 113.5574 | 112.8342
1366.9062 | 122.319 | -114.4226 | 7.6263 | -0.0060272 | -0.0028561 | 0.059248 | 0.054762 | -0.001491 | -0.0064109 | -0.0016941 | -0.0082093 | 2.1442e-05 | 0.071938 | 0.052237 | -0.0088097 | 0.016663 | -0.0031338 | -0.064087 | 7.457 | -114.473 | 7.6721 | -113.7405 | -114.4409 | -114.4547 | -0.71869 | 7.5348 | -114.5142 | 7.663 | -113.9694 | -114.3173 | -114.2349 | -0.050354 | -0.16937 | 0.045776 | 0.68207 | -0.032044 | -0.018311 | 0.01831 | 0.032043 | -0.091553 | -0.091553 | 0.036621 | 0.45319 | 0.18768 | 0.10528 | 0.27924 | 0.19684 | 0.73242 | 122.1451 | 0.54474 | 122.1771 | 121.9299 | 122.049 | 121.8796 | 121.9574 | -122.0993 | -122.1405 | 122.0947 | 122.0856 | 114.3585 | 113.7039
1368.5938 | 122.2504 | -114.9261 | 7.196 | -0.0060272 | 0.0012027 | 0.057967 | 0.057539 | -0.0012774 | -0.0061971 | -0.0029759 | -0.0021057 | 0.0027984 | 0.072365 | 0.05886 | -0.013296 | 0.020721 | -0.0044156 | -0.22888 | 7.0404 | -114.9216 | 7.0587 | -114.3814 | -115.0909 | -115.0772 | -0.93842 | 7.0953 | -115.0635 | 7.0999 | -114.5782 | -114.949 | -114.798 | 0.004577 | -0.15564 | -0.13733 | 0.54474 | -0.15106 | -0.16479 | -0.15564 | -0.16937 | -0.13733 | -0.10071 | -0.09613 | 0.3479 | 0.12817 | -0.022889 | 0.2655 | 0.11444 | 0.54016 | 121.9803 | 0.48523 | 122.1634 | 121.962 | 122.1588 | 121.9666 | 122.0215 | -122.1176 | -122.2595 | 121.9849 | 122.0261 | 114.6973 | 113.9877
1370.2812 | 122.2 | -113.6078 | 8.5098 | -0.0060272 | -0.0002927 | 0.057753 | 0.055403 | -0.0017048 | -0.0070517 | -0.0023349 | -0.0051575 | 0.0034392 | 0.070869 | 0.061423 | -0.010092 | 0.01944 | -0.0056974 | -0.050354 | 8.3633 | -113.6353 | 8.4274 | -113.0127 | -113.7131 | -113.7131 | -0.82855 | 8.4137 | -113.7405 | 8.4091 | -113.2599 | -113.5849 | -113.4979 | -0.027466 | -0.14649 | -0.082398 | 0.59509 | -0.10529 | -0.10529 | -0.07782 | -0.07782 | -0.13275 | -0.096131 | -0.10071 | 0.3479 | 0.10986 | 0.022888 | 0.24262 | 0.15564 | 0.62256 | 122.0627 | 0.48065 | 122.1497 | 121.9986 | 122.1542 | 121.9711 | 122.0215 | -122.1451 | -122.2504 | 122.0352 | 122.0169 | 113.5574 | 112.7792
1372.0156 | 122.2366 | -113.7817 | 8.3313 | -0.021286 | -0.0002927 | 0.058607 | 0.056471 | -0.0012774 | -0.0072653 | -0.00083947 | -0.0082093 | -0.00061956 | 0.069374 | 0.063987 | -0.01116 | 0.019867 | -0.0009976 | -0.09613 | 8.1848 | -113.8184 | 8.2443 | -113.2187 | -113.8824 | -113.9053 | -0.86517 | 8.2443 | -113.8916 | 8.2489 | -113.4064 | -113.768 | -113.6444 | -0.036621 | -0.14649 | -0.086975 | 0.56305 | -0.1236 | -0.10071 | -0.086975 | -0.064087 | -0.10986 | -0.086975 | -0.082398 | 0.37537 | 0.13733 | 0.013733 | 0.24719 | 0.1236 | 0.59967 | 122.0627 | 0.48523 | 122.1405 | 122.0032 | 122.1359 | 121.9666 | 122.0261 | -122.1497 | -122.2229 | 122.0261 | 122.0306 | 113.6856 | 112.9166
1373.7656 | 122.2504 | -113.1821 | 8.9172 | -0.013657 | -0.0005063 | 0.056898 | 0.05818 | -0.0032 | -0.0081197 | -0.00041227 | -0.0082093 | 0.0015166 | 0.072151 | 0.066764 | -0.012228 | 0.020721 | -0.0003568 | -0.068665 | 8.7662 | -113.2141 | 8.8806 | -112.5824 | -113.2919 | -113.2874 | -0.80566 | 8.8211 | -113.2828 | 8.9035 | -112.7792 | -113.15 | -113.0127 | -0.032043 | -0.15106 | -0.036621 | 0.59967 | -0.10529 | -0.10986 | -0.073243 | -0.07782 | -0.10071 | -0.09613 | -0.013733 | 0.40283 | 0.16937 | 0.032044 | 0.27008 | 0.13275 | 0.63171 | 122.0947 | 0.50354 | 122.1863 | 121.9803 | 122.1039 | 121.9482 | 122.0032 | -122.1313 | -122.2 | 122.0627 | 122.0856 | 113.1134 | 112.3764
1375.4375 | 122.3053 | -112.9211 | 9.1644 | -0.0060272 | 0.0012027 | 0.057753 | 0.055403 | 0.0014996 | -0.0049155 | -0.0038303 | -0.011261 | 0.00023504 | 0.070869 | 0.055442 | -0.0094507 | 0.020294 | -0.0012112 | -0.16937 | 9.0042 | -112.9166 | 9.1324 | -112.3352 | -112.9944 | -113.0127 | -0.89722 | 9.0546 | -113.0356 | 9.1553 | -112.5183 | -112.8662 | -112.7518 | 0.004578 | -0.16022 | -0.032044 | 0.58594 | -0.091552 | -0.073242 | -0.09613 | -0.07782 | -0.11444 | -0.10986 | -0.009156 | 0.40283 | 0.16937 | 0.054932 | 0.28381 | 0.16937 | 0.58136 | 122.049 | 0.51727 | 122.1909 | 121.9208 | 122.0901 | 121.9254 | 121.9757 | -122.081 | -122.2 | 122.0535 | 122.0764 | 112.7518 | 112.0239
1377.1875 | 122.2229 | -112.1567 | 9.9609 | 0.0016023 | -0.0007199 | 0.057967 | 0.054121 | -0.0040546 | -0.0076925 | -0.0021213 | -0.0021057 | -0.00040596 | 0.071938 | 0.062705 | -0.010092 | 0.019226 | -0.0003568 | -0.059509 | 9.7733 | -112.207 | 9.906 | -111.5616 | -112.2391 | -112.2437 | -0.82398 | 9.8511 | -112.2345 | 9.874 | -111.7996 | -112.1475 | -112.0605 | -0.050354 | -0.18768 | -0.054931 | 0.59509 | -0.086975 | -0.082398 | -0.036621 | -0.032044 | -0.07782 | -0.10986 | -0.086975 | 0.35706 | 0.09613 | 0.009155 | 0.17395 | 0.086975 | 0.64545 | 122.113 | 0.43488 | 122.1085 | 121.9803 | 122.0856 | 121.9299 | 122.0078 | -122.168 | -122.1954 | 122.0627 | 122.0306 | 112.0972 | 111.3327
1378.875 | 122.2092 | -111.2412 | 10.881 | -0.0060272 | -0.0022153 | 0.055403 | 0.056471 | -0.00555 | -0.0076925 | -0.0031895 | -0.0021057 | 0.0010894 | 0.073647 | 0.058005 | -0.01116 | 0.018158 | -0.0031338 | -0.050354 | 10.6934 | -111.2366 | 10.8398 | -110.6506 | -111.3281 | -111.3419 | -0.83771 | 10.7758 | -111.319 | 10.7986 | -110.8932 | -111.2366 | -111.1267 | 0.004578 | -0.18768 | -0.041198 | 0.59052 | -0.10071 | -0.086975 | -0.10529 | -0.091553 | -0.07782 | -0.10529 | -0.082397 | 0.3479 | 0.11444 | 0.004578 | 0.19226 | 0.082398 | 0.58594 | 122.0764 | 0.42572 | 122.1176 | 121.9299 | 122.0947 | 121.9345 | 122.0169 | -122.1176 | -122.2 | 122.081 | 122.0398 | 111.1908 | 110.4034
1380.625 | 122.319 | -111.026 | 10.9817 | -0.013657 | 0.0035525 | 0.059248 | 0.057326 | 0.0055584 | -0.0072653 | -0.0012669 | -0.0021057 | 0.00066224 | 0.071724 | 0.060569 | -0.011801 | 0.01944 | -0.0020658 | -0.1236 | 10.8444 | -111.0718 | 11.0733 | -110.4172 | -111.1313 | -111.1176 | -0.8194 | 10.8856 | -111.1404 | 11.087 | -110.6369 | -110.9802 | -110.8612 | -0.045776 | -0.13733 | 0.091553 | 0.60883 | -0.091553 | -0.10529 | -0.045777 | -0.05951 | -0.11444 | -0.09613 | 0.10529 | 0.3891 | 0.16479 | 0.045776 | 0.27924 | 0.16022 | 0.6546 | 122.1451 | 0.50354 | 122.2275 | 121.9162 | 122.0261 | 121.8704 | 121.9116 | -122.0535 | -122.1222 | 122.0993 | 122.113 | 110.9024 | 110.2066
1382.3125 | 122.2046 | -111.676 | 10.4553 | 0.0016023 | -0.0028561 | 0.057753 | 0.056898 | -0.0032 | -0.0068381 | -0.0034031 | -0.0021057 | 0.0034392 | 0.072792 | 0.062491 | -0.010519 | 0.018799 | -0.0033474 | -0.10529 | 10.318 | -111.6898 | 10.3775 | -111.1176 | -111.7859 | -111.7905 | -0.88806 | 10.3775 | -111.7584 | 10.35 | -111.3281 | -111.6714 | -111.5662 | -0.013733 | -0.13733 | -0.07782 | 0.55847 | -0.11444 | -0.10986 | -0.10071 | -0.096131 | -0.082398 | -0.07782 | -0.10529 | 0.3479 | 0.10986 | 0.004577 | 0.19226 | 0.086975 | 0.5722 | 122.0673 | 0.4303 | 122.1085 | 122.0078 | 122.1359 | 121.994 | 122.0535 | -122.1451 | -122.2137 | 122.0535 | 122.0261 | 111.5707 | 110.788
1384.0625 | 122.2 | -111.5753 | 10.5606 | -0.013657 | -0.0002927 | 0.058394 | 0.057539 | -0.002132 | -0.0091879 | -0.0016941 | -0.0082093 | 0.003012 | 0.072578 | 0.061423 | -0.011801 | 0.019867 | -0.0027066 | -0.10071 | 10.4279 | -111.5845 | 10.4965 | -111.0168 | -111.6714 | -111.6898 | -0.92468 | 10.4919 | -111.6669 | 10.4828 | -111.2183 | -111.557 | -111.4426 | -0.009156 | -0.13275 | -0.064087 | 0.55847 | -0.11444 | -0.096131 | -0.10528 | -0.086975 | -0.091553 | -0.068665 | -0.07782 | 0.35706 | 0.13275 | 0.01831 | 0.2243 | 0.10986 | 0.56763 | 122.081 | 0.44861 | 122.1497 | 122.0123 | 122.1588 | 122.0032 | 122.0673 | -122.1451 | -122.2275 | 122.0718 | 122.0581 | 111.4746 | 110.6506
1385.75 | 122.3099 | -111.5524 | 10.4919 | 0.0016023 | -0.0009335 | 0.059462 | 0.056258 | -0.0034136 | -0.0066245 | -0.0051121 | -0.0021057 | -0.00061956 | 0.071724 | 0.061209 | -0.011373 | 0.017303 | -0.004202 | -0.16479 | 10.3546 | -111.5524 | 10.5789 | -110.8887 | -111.6074 | -111.6028 | -0.86517 | 10.405 | -111.6119 | 10.5789 | -111.1496 | -111.4746 | -111.3647 | 0 | -0.13733 | 0.086975 | 0.66376 | -0.050354 | -0.054932 | -0.050354 | -0.054932 | -0.059509 | -0.086975 | 0.086975 | 0.40283 | 0.18768 | 0.07782 | 0.24719 | 0.13733 | 0.66376 | 122.1313 | 0.46234 | 122.1909 | 121.907 | 122.0169 | 121.907 | 121.9574 | -122.0444 | -122.1039 | 122.1313 | 122.1313 | 111.3876 | 110.6873
1387.5 | 122.2137 | -111.9507 | 10.144 | -0.013657 | 0.0035525 | 0.057539 | 0.059248 | -0.0010638 | -0.0066245 | -0.0029759 | -0.0082093 | 0.0017304 | 0.072365 | 0.069327 | -0.012441 | 0.019226 | -0.0020658 | -0.21973 | 9.9838 | -112.0193 | 10.0388 | -111.4792 | -112.1475 | -112.1429 | -1.0071 | 10.0662 | -112.0743 | 10.0754 | -111.6577 | -112.0056 | -111.8271 | -0.068664 | -0.16022 | -0.10529 | 0.4715 | -0.19226 | -0.19684 | -0.1236 | -0.12817 | -0.1236 | -0.07782 | -0.068665 | 0.29297 | 0.1236 | -0.054931 | 0.24719 | 0.068665 | 0.54016 | 122.0581 | 0.41657 | 122.1497 | 122.0032 | 122.1405 | 121.9345 | 122.0169 | -122.1634 | -122.2183 | 121.9894 | 122.0261 | 111.731 | 110.9436
1389.1875 | 122.3053 | -111.5982 | 10.4645 | -0.0060272 | -0.0013607 | 0.059248 | 0.055403 | -0.003841 | -0.0055563 | -0.0042575 | -0.0021057 | -0.0016876 | 0.072365 | 0.05416 | -0.010519 | 0.019867 | -0.0020658 | -0.17395 | 10.3134 | -111.6165 | 10.4599 | -111.0077 | -111.6989 | -111.6898 | -0.90637 | 10.35 | -111.7172 | 10.4874 | -111.2 | -111.5295 | -111.4243 | -0.01831 | -0.15106 | -0.004578 | 0.59052 | -0.091552 | -0.10071 | -0.073242 | -0.082398 | -0.11902 | -0.11444 | 0.022888 | 0.39826 | 0.17395 | 0.068665 | 0.29297 | 0.18768 | 0.60883 | 122.0764 | 0.51727 | 122.2046 | 121.9299 | 122.0673 | 121.9116 | 121.9482 | -122.081 | -122.1817 | 122.0581 | 122.0856 | 111.4243 | 110.6918
1390.9375 | 122.2412 | -111.1221 | 10.9863 | -0.0060272 | 0.0037661 | 0.058607 | 0.055189 | -0.0019184 | -0.0068381 | -0.0040439 | -0.0051575 | 0.0045074 | 0.071083 | 0.065909 | -0.013082 | 0.020081 | -0.0029202 | -0.12817 | 10.8124 | -111.1725 | 10.9589 | -110.5499 | -111.2457 | -111.2457 | -0.90179 | 10.8444 | -111.2366 | 10.968 | -110.7605 | -111.1267 | -110.9756 | -0.050354 | -0.17395 | -0.027466 | 0.5722 | -0.1236 | -0.1236 | -0.073243 | -0.073243 | -0.11444 | -0.14191 | -0.01831 | 0.36163 | 0.14648 | -0.004578 | 0.26093 | 0.10986 | 0.62256 | 122.1313 | 0.47607 | 122.2046 | 121.9849 | 122.081 | 121.9345 | 121.9666 | -122.1588 | -122.2229 | 122.081 | 122.0901 | 110.994 | 110.2203
1392.625 | 122.3373 | -111.5387 | 10.524 | -0.0060272 | -0.0009335 | 0.058394 | 0.055189 | 0.00043159 | -0.0068381 | -0.0061801 | -0.0051575 | -0.001474 | 0.071938 | 0.059714 | -0.010519 | 0.018585 | -0.000784 | -0.13275 | 10.3546 | -111.5707 | 10.5515 | -110.9253 | -111.5982 | -111.6074 | -0.88348 | 10.4233 | -111.6531 | 10.5927 | -111.1038 | -111.4197 | -111.3052 | -0.032044 | -0.16937 | 0.027466 | 0.6134 | -0.068665 | -0.05951 | -0.036621 | -0.027466 | -0.11444 | -0.10071 | 0.068664 | 0.43488 | 0.23346 | 0.11902 | 0.3479 | 0.23346 | 0.64545 | 122.1222 | 0.54932 | 122.2458 | 121.9254 | 122.0764 | 121.8933 | 121.962 | -122.0947 | -122.1771 | 122.0901 | 122.1313 | 111.4059 | 110.6552
1394.3125 | 122.2916 | -111.8317 | 10.2127 | -0.028916 | 0.0012027 | 0.057539 | 0.05583 | -0.00042301 | -0.0057699 | -0.0021213 | -0.0051575 | 0.001303 | 0.07151 | 0.052878 | -0.011373 | 0.021362 | -0.0031338 | -0.16022 | 10.0433 | -111.85 | 10.2676 | -111.2366 | -111.9553 | -111.9415 | -0.9201 | 10.0983 | -111.9644 | 10.231 | -111.47 | -111.795 | -111.6714 | -0.018311 | -0.16937 | 0.054931 | 0.59509 | -0.10986 | -0.1236 | -0.091552 | -0.10528 | -0.13275 | -0.11444 | 0.01831 | 0.36163 | 0.16022 | 0.036621 | 0.29297 | 0.16937 | 0.6134 | 122.1176 | 0.49438 | 122.1954 | 121.8933 | 122.0627 | 121.875 | 121.9299 | -122.0627 | -122.1771 | 122.0993 | 122.0627 | 111.6714 | 110.9116
1396.0469 | 122.3465 | -112.2849 | 9.7641 | -0.0060272 | -0.0015743 | 0.057112 | 0.05583 | -0.0023456 | -0.0087607 | -0.0036167 | -0.0051575 | 0.0010894 | 0.07151 | 0.058219 | -0.011801 | 0.018585 | -0.0050564 | -0.073242 | 9.6222 | -112.326 | 9.8785 | -111.5845 | -112.2757 | -112.2803 | -0.83313 | 9.6817 | -112.3627 | 9.8373 | -111.8088 | -112.1658 | -112.0834 | -0.041199 | -0.14191 | 0.11444 | 0.70038 | 0.004578 | 0.009155 | 0.045777 | 0.050354 | -0.07782 | -0.082397 | 0.073242 | 0.47607 | 0.20142 | 0.11902 | 0.27924 | 0.19684 | 0.74158 | 122.2046 | 0.55389 | 122.2 | 121.9482 | 122.0444 | 121.907 | 121.9666 | -122.0901 | -122.1268 | 122.1634 | 122.1222 | 112.2116 | 111.4517
1397.7969 | 122.3602 | -112.4817 | 9.5673 | -0.0060272 | -0.0005063 | 0.055403 | 0.055617 | 0.001286 | -0.0076925 | -0.0019077 | -0.0021057 | 2.1442e-05 | 0.07151 | 0.058432 | -0.013082 | 0.017303 | -0.0018522 | -0.09613 | 9.4162 | -112.4908 | 9.6405 | -111.8225 | -112.5229 | -112.5092 | -0.83313 | 9.4711 | -112.6099 | 9.6634 | -112.0239 | -112.3581 | -112.2849 | -0.009156 | -0.15106 | 0.073242 | 0.65918 | -0.027466 | -0.041199 | -0.01831 | -0.032043 | -0.12817 | -0.096131 | 0.09613 | 0.45776 | 0.19684 | 0.1236 | 0.32501 | 0.25177 | 0.66833 | 122.1313 | 0.58594 | 122.2733 | 121.907 | 122.081 | 121.8979 | 121.9528 | -122.0581 | -122.1771 | 122.1222 | 122.1451 | 112.3856 | 111.6486
1399.5469 | 122.2916 | -113.0768 | 9.0088 | 0.0016023 | -7.9104e-05 | 0.059035 | 0.056258 | -0.00042301 | -0.0059835 | -0.0012669 | -0.0021057 | 0.00044864 | 0.071083 | 0.06185 | -0.012655 | 0.019012 | -0.0009976 | -0.16937 | 8.8669 | -113.0905 | 8.9951 | -112.468 | -113.1775 | -113.1454 | -1.0025 | 8.9355 | -113.1683 | 9.0088 | -112.6877 | -113.0035 | -112.9074 | -0.013733 | -0.14191 | -0.013733 | 0.60882 | -0.068665 | -0.10071 | -0.054932 | -0.086975 | -0.091553 | -0.073242 | 0 | 0.3891 | 0.16937 | 0.073242 | 0.26093 | 0.16479 | 0.62256 | 122.0856 | 0.48065 | 122.1771 | 121.9574 | 122.1039 | 121.9437 | 122.0123 | -122.0993 | -122.1771 | 122.0718 | 122.0856 | 112.9074 | 112.0743
1401.2188 | 122.3419 | -113.8641 | 8.1482 | -0.021286 | -7.9104e-05 | 0.058607 | 0.05583 | -0.00042301 | -0.0057699 | -0.0042575 | -0.0051575 | 0.0025848 | 0.072365 | 0.057151 | -0.012014 | 0.01944 | -0.002493 | -0.14191 | 8.0109 | -113.887 | 8.2214 | -113.237 | -113.974 | -113.9694 | -0.96588 | 8.0704 | -113.9923 | 8.2443 | -113.4567 | -113.8 | -113.681 | -0.022888 | -0.13733 | 0.073243 | 0.62714 | -0.10528 | -0.10986 | -0.082397 | -0.086975 | -0.12817 | -0.077819 | 0.096131 | 0.40741 | 0.18311 | 0.064087 | 0.31128 | 0.19226 | 0.65002 | 122.1085 | 0.53558 | 122.2366 | 121.8979 | 122.0627 | 121.875 | 121.9345 | -122.0352 | -122.1405 | 122.0856 | 122.1085 | 113.7222 | 112.8983
1402.9688 | 122.3328 | -114.0015 | 8.0383 | -0.0060272 | 0.0020571 | 0.060103 | 0.05583 | 0.0025678 | -0.0070517 | -0.0014805 | -0.0051575 | 0.0027984 | 0.070015 | 0.056723 | -0.012228 | 0.020508 | -0.0054838 | -0.17853 | 7.8644 | -114.0472 | 8.0887 | -113.3789 | -114.0884 | -114.0747 | -0.98419 | 7.9514 | -114.1296 | 8.1024 | -113.5849 | -113.942 | -113.8138 | -0.045776 | -0.17395 | 0.050354 | 0.62256 | -0.073242 | -0.086975 | -0.027466 | -0.041199 | -0.12817 | -0.086975 | 0.064087 | 0.41656 | 0.18768 | 0.059509 | 0.31586 | 0.18768 | 0.66833 | 122.1359 | 0.54474 | 122.2321 | 121.9116 | 122.081 | 121.8658 | 121.9528 | -122.0856 | -122.168 | 122.0901 | 122.1039 | 113.8229 | 113.0173
1404.6562 | 122.2183 | -113.974 | 8.1802 | -0.013657 | 0.0024845 | 0.061598 | 0.059035 | 0.0025678 | -0.0070517 | -0.0034031 | -0.0021057 | 0.0023712 | 0.074287 | 0.066336 | -0.0088097 | 0.021576 | -0.0005704 | -0.20599 | 8.0338 | -113.9832 | 8.0475 | -113.4521 | -114.1479 | -114.1296 | -1.1215 | 8.1024 | -114.0518 | 8.0795 | -113.6124 | -113.974 | -113.8412 | -0.009155 | -0.14649 | -0.13275 | 0.52185 | -0.15564 | -0.17395 | -0.14648 | -0.16479 | -0.07782 | -0.07782 | -0.10071 | 0.36163 | 0.13275 | 0 | 0.21057 | 0.07782 | 0.53101 | 122.0306 | 0.43945 | 122.1313 | 122.0169 | 122.1542 | 122.0078 | 122.0764 | -122.1634 | -122.2321 | 122.0215 | 122.0535 | 113.768 | 112.8525
1406.3906 | 122.2916 | -114.4455 | 7.6401 | -0.013657 | -0.0009335 | 0.05818 | 0.055189 | -0.0010638 | -0.0061971 | -0.0034031 | -0.0051575 | 0.00066224 | 0.067879 | 0.060141 | -0.010732 | 0.018585 | -0.003561 | -0.19684 | 7.4936 | -114.473 | 7.5943 | -113.8596 | -114.5416 | -114.5508 | -1.0849 | 7.5073 | -114.5599 | 7.6218 | -114.0427 | -114.3723 | -114.2807 | -0.027465 | -0.14648 | -0.045777 | 0.58594 | -0.10528 | -0.09613 | -0.07782 | -0.068665 | -0.11444 | -0.13275 | -0.018311 | 0.40283 | 0.1648 | 0.073243 | 0.27924 | 0.18768 | 0.6134 | 122.0673 | 0.51727 | 122.1817 | 121.9666 | 122.0673 | 121.9391 | 121.9528 | -122.113 | -122.2 | 122.0398 | 122.0673 | 114.2487 | 113.3606
1408.0938 | 122.3648 | -114.9857 | 7.077 | -0.013657 | -0.0007199 | 0.056685 | 0.053053 | -0.00063661 | -0.0081197 | -0.0036167 | 0.0009461 | 0.0010894 | 0.073219 | 0.062705 | -0.012228 | 0.018585 | 0.0002842 | -0.14191 | 6.926 | -114.9902 | 7.132 | -114.2899 | -115.0085 | -115.0131 | -0.99792 | 7.0129 | -115.0909 | 7.1457 | -114.5279 | -114.8621 | -114.798 | -0.004577 | -0.15106 | 0.054932 | 0.6958 | -0.027466 | -0.022888 | -0.022889 | -0.018311 | -0.10528 | -0.064087 | 0.068665 | 0.45776 | 0.18768 | 0.1236 | 0.29297 | 0.22888 | 0.70038 | 122.1222 | 0.56305 | 122.2366 | 121.9162 | 122.1039 | 121.9116 | 121.9986 | -122.0673 | -122.168 | 122.1176 | 122.1313 | 114.8438 | 113.9877
1409.8438 | 122.2321 | -114.8529 | 7.3013 | -0.0060272 | 0.0007755 | 0.057753 | 0.058821 | -0.0023456 | -0.0066245 | -0.0019077 | -0.0021057 | 0.003012 | 0.072792 | 0.060569 | -0.0096643 | 0.020294 | -0.0014248 | -0.10529 | 7.1457 | -114.8941 | 7.1915 | -114.2715 | -114.9353 | -114.949 | -1.0712 | 7.2556 | -114.9399 | 7.1869 | -114.473 | -114.8483 | -114.7156 | -0.041199 | -0.15564 | -0.10986 | 0.58136 | -0.096131 | -0.082398 | -0.054932 | -0.041199 | -0.086975 | -0.045777 | -0.11444 | 0.37994 | 0.13733 | 0.004577 | 0.2243 | 0.091552 | 0.62256 | 122.0856 | 0.46692 | 122.1268 | 122.0398 | 122.1954 | 121.9986 | 122.1085 | -122.1954 | -122.2412 | 122.0444 | 122.0398 | 114.7476 | 113.7817
1411.5469 | 122.2458 | -115.2603 | 6.8756 | -0.013657 | -0.0007199 | 0.056258 | 0.055617 | -0.0019184 | -0.0034201 | -0.0053257 | -0.0021057 | 0.00066224 | 0.071724 | 0.059073 | -0.010946 | 0.017517 | -0.0033474 | -0.091553 | 6.665 | -115.2969 | 6.8161 | -114.6332 | -115.3015 | -115.2878 | -1.0437 | 6.7841 | -115.3702 | 6.7841 | -114.8438 | -115.1916 | -115.1001 | -0.036621 | -0.21057 | -0.059509 | 0.62714 | -0.027466 | -0.041199 | 0.009155 | -0.004578 | -0.10986 | -0.091552 | -0.091552 | 0.41657 | 0.16022 | 0.068665 | 0.27008 | 0.17853 | 0.66376 | 122.113 | 0.52643 | 122.1542 | 121.962 | 122.1542 | 121.9254 | 122.0444 | -122.1725 | -122.2458 | 122.0764 | 122.0444 | 115.1688 | 114.2166
1413.2344 | 122.2183 | -115.2649 | 6.8756 | -0.021286 | -0.0002927 | 0.060103 | 0.057539 | -0.0044818 | -0.0074789 | -0.00019867 | -0.0051575 | 0.003012 | 0.071724 | 0.063559 | -0.010305 | 0.020508 | 0.0007114 | -0.10529 | 6.8024 | -115.2191 | 6.7932 | -114.6698 | -115.3656 | -115.3702 | -1.1307 | 6.8344 | -115.361 | 6.7749 | -114.8895 | -115.2466 | -115.1321 | 0.045777 | -0.073242 | -0.082397 | 0.59509 | -0.10528 | -0.10071 | -0.15106 | -0.14648 | -0.09613 | -0.041198 | -0.10071 | 0.37537 | 0.13275 | 0.018311 | 0.22888 | 0.11444 | 0.54932 | 122.0123 | 0.4715 | 122.1359 | 122.0215 | 122.1954 | 122.0673 | 122.0993 | -122.0947 | -122.2366 | 122.0581 | 122.0398 | 115.1596 | 114.1342
1414.9688 | 122.2275 | -115.3198 | 6.8207 | -0.013657 | -0.0002927 | 0.057753 | 0.056044 | 0.0036358 | -0.0061971 | -0.0012669 | -0.0051575 | 0.001944 | 0.07386 | 0.066336 | -0.010305 | 0.020508 | -0.0003568 | -0.11902 | 6.6742 | -115.3381 | 6.6879 | -114.7888 | -115.4617 | -115.4709 | -1.1353 | 6.72 | -115.4572 | 6.6971 | -114.9536 | -115.3198 | -115.21 | -0.018311 | -0.14649 | -0.13275 | 0.53101 | -0.15106 | -0.14191 | -0.13275 | -0.1236 | -0.13733 | -0.10071 | -0.1236 | 0.36621 | 0.10986 | 0 | 0.24719 | 0.13733 | 0.54932 | 122.0261 | 0.50354 | 122.1542 | 122.0123 | 122.1771 | 121.994 | 122.0398 | -122.1588 | -122.2778 | 122.0078 | 122.0169 | 115.2008 | 114.1846
1416.7188 | 122.2961 | -115.567 | 6.514 | -0.0060272 | -0.0002927 | 0.058821 | 0.056258 | -0.0044818 | -0.0053427 | -0.0046847 | -0.0051575 | -0.0010468 | 0.073433 | 0.060782 | -0.0098779 | 0.01944 | -0.0029202 | -0.18768 | 6.34 | -115.6036 | 6.459 | -114.9857 | -115.6906 | -115.6723 | -1.1261 | 6.4087 | -115.7043 | 6.4911 | -115.1505 | -115.5167 | -115.4022 | -0.036621 | -0.17395 | -0.054932 | 0.58136 | -0.10528 | -0.1236 | -0.068664 | -0.086975 | -0.13733 | -0.10529 | -0.022888 | 0.41657 | 0.1648 | 0.050354 | 0.30212 | 0.18768 | 0.61798 | 122.0627 | 0.55389 | 122.1954 | 121.9437 | 122.113 | 121.907 | 121.9757 | -122.1176 | -122.2183 | 122.0261 | 122.0581 | 115.3793 | 114.4409
1418.4062 | 122.319 | -115.6769 | 6.3629 | -0.013657 | 0.0003483 | 0.057753 | 0.055617 | -0.0025592 | -0.0057699 | -0.0034031 | -0.0051575 | 0.00044864 | 0.071297 | 0.067405 | -0.012228 | 0.021149 | -0.0018522 | -0.16937 | 6.2027 | -115.6998 | 6.4224 | -115.0314 | -115.7501 | -115.7364 | -1.0941 | 6.2851 | -115.8142 | 6.4133 | -115.242 | -115.6082 | -115.4938 | -0.022888 | -0.16022 | 0.059509 | 0.64545 | -0.059509 | -0.073242 | -0.036621 | -0.050354 | -0.13733 | -0.07782 | 0.050354 | 0.43488 | 0.18311 | 0.068665 | 0.32044 | 0.20599 | 0.66833 | 122.1222 | 0.57221 | 122.2275 | 121.9025 | 122.0993 | 121.8796 | 121.962 | -122.0627 | -122.1771 | 122.0993 | 122.0901 | 115.5075 | 114.5828
1420.1562 | 122.3145 | -115.5716 | 6.4957 | -0.013657 | 0.0031253 | 0.059035 | 0.058394 | 0.0014996 | -0.0059835 | -0.0021213 | -0.0082093 | 0.001944 | 0.072792 | 0.065909 | -0.012228 | 0.019012 | -0.0065518 | -0.23346 | 6.4041 | -115.5853 | 6.4728 | -114.9857 | -115.7043 | -115.6677 | -1.1719 | 6.459 | -115.6631 | 6.5414 | -115.155 | -115.5258 | -115.361 | -0.013733 | -0.091553 | -0.022889 | 0.58594 | -0.096131 | -0.13275 | -0.082398 | -0.11902 | -0.091553 | -0.036622 | 0.045776 | 0.41657 | 0.21057 | 0.045776 | 0.30212 | 0.13733 | 0.59967 | 122.0581 | 0.50812 | 122.2046 | 121.9894 | 122.1222 | 121.9757 | 122.0306 | -122.081 | -122.1588 | 122.0444 | 122.113 | 115.3381 | 114.3997
1421.8594 | 122.3282 | -115.4022 | 6.6833 | -0.021286 | 0.0022709 | 0.060103 | 0.057326 | 4.192e-06 | -0.0059835 | -0.0021213 | -0.0051575 | 0.003012 | 0.073219 | 0.062278 | -0.01116 | 0.018585 | -0.0063382 | -0.21515 | 6.5414 | -115.4388 | 6.665 | -114.7751 | -115.5029 | -115.4755 | -1.1444 | 6.6055 | -115.5075 | 6.7108 | -114.9536 | -115.3152 | -115.1688 | -0.036621 | -0.14191 | -0.018311 | 0.62714 | -0.073242 | -0.10071 | -0.036621 | -0.064087 | -0.10529 | -0.07782 | 0.027465 | 0.44861 | 0.23346 | 0.086975 | 0.33875 | 0.19226 | 0.66376 | 122.1039 | 0.55389 | 122.2183 | 121.9803 | 122.113 | 121.9437 | 122.0078 | -122.1222 | -122.1909 | 122.0673 | 122.113 | 115.1871 | 114.2578
1423.6094 | 122.2137 | -115.3564 | 6.8069 | -0.013657 | -0.0002927 | 0.056898 | 0.056685 | 0.0017132 | -0.0068381 | -0.0027621 | -0.0021057 | 0.003653 | 0.070656 | 0.060355 | -0.0094507 | 0.019653 | -0.0009976 | -0.1236 | 6.6422 | -115.3839 | 6.6742 | -114.7659 | -115.4388 | -115.4755 | -1.1627 | 6.7108 | -115.4526 | 6.6879 | -114.9811 | -115.3336 | -115.1825 | -0.027466 | -0.16479 | -0.13275 | 0.59051 | -0.11902 | -0.082398 | -0.091553 | -0.054932 | -0.096131 | -0.096131 | -0.11902 | 0.37537 | 0.17395 | 0.022888 | 0.27008 | 0.11902 | 0.61798 | 122.0581 | 0.4715 | 122.1405 | 122.0261 | 122.1634 | 121.9986 | 122.0673 | -122.1909 | -122.2595 | 122.0306 | 122.0444 | 115.2328 | 114.1937
1425.2969 | 122.374 | -115.2878 | 6.7657 | -0.013657 | -0.0034971 | 0.057326 | 0.054549 | 0.002995 | -0.0081197 | -0.00019867 | -0.0082093 | -0.00040596 | 0.072365 | 0.052451 | -0.012228 | 0.019012 | -0.0046292 | -0.10071 | 6.601 | -115.3244 | 6.8253 | -114.592 | -115.2969 | -115.3152 | -1.0162 | 6.6925 | -115.3931 | 6.8253 | -114.7888 | -115.1413 | -115.0177 | -0.036621 | -0.16479 | 0.059509 | 0.6958 | -0.027466 | -0.009155 | 0.009155 | 0.027466 | -0.10529 | -0.073242 | 0.059509 | 0.49896 | 0.27008 | 0.14648 | 0.37537 | 0.25177 | 0.73242 | 122.1497 | 0.60425 | 122.2183 | 121.9254 | 122.0856 | 121.8887 | 121.9803 | -122.0901 | -122.1588 | 122.113 | 122.113 | 115.1871 | 114.2715
1427.0625 | 122.2641 | -115.4526 | 6.665 | -0.0060272 | 0.0009891 | 0.056471 | 0.056471 | -0.0025592 | -0.0076925 | -0.0010531 | -0.0021057 | 0.0032256 | 0.071083 | 0.064627 | -0.01116 | 0.018372 | -0.0005704 | -0.10071 | 6.5048 | -115.5075 | 6.5735 | -114.8712 | -115.5807 | -115.5807 | -1.1353 | 6.5826 | -115.567 | 6.601 | -115.0681 | -115.4297 | -115.274 | -0.054931 | -0.16022 | -0.091553 | 0.58136 | -0.12817 | -0.12817 | -0.073243 | -0.073243 | -0.11444 | -0.082397 | -0.064087 | 0.38452 | 0.17853 | 0.022889 | 0.29297 | 0.13733 | 0.63629 | 122.081 | 0.49896 | 122.168 | 122.0123 | 122.1497 | 121.9574 | 122.0352 | -122.1725 | -122.2321 | 122.0261 | 122.0535 | 115.3519 | 114.3173
1428.75 | 122.3602 | -115.9195 | 6.134 | -0.028916 | -0.0026425 | 0.057753 | 0.051558 | -0.00555 | -0.0049155 | -0.0014805 | -0.0051575 | -0.00040596 | 0.070229 | 0.058219 | -0.0098779 | 0.019226 | -0.0009976 | -0.1236 | 5.9784 | -115.9744 | 6.1615 | -115.2512 | -115.9515 | -115.9561 | -1.0941 | 6.0654 | -116.0431 | 6.1981 | -115.4755 | -115.8051 | -115.6815 | -0.054931 | -0.15564 | 0.027466 | 0.66833 | -0.036621 | -0.032043 | 0.01831 | 0.022888 | -0.1236 | -0.068664 | 0.064087 | 0.44403 | 0.23804 | 0.11444 | 0.36163 | 0.23804 | 0.72327 | 122.1359 | 0.56763 | 122.2412 | 121.9528 | 122.1085 | 121.8979 | 121.9849 | -122.1085 | -122.1771 | 122.081 | 122.1176 | 115.7959 | 114.8254
1430.4375 | 122.3511 | -116.1667 | 5.8594 | -0.0060272 | 0.0037661 | 0.059248 | 0.057326 | -0.0040546 | -0.0059835 | -0.0025485 | -0.0082093 | 0.00087584 | 0.070656 | 0.065268 | -0.010732 | 0.018372 | -0.0039884 | -0.15106 | 5.7358 | -116.2216 | 5.9235 | -115.5167 | -116.2491 | -116.217 | -1.1353 | 5.8228 | -116.2994 | 5.9189 | -115.7455 | -116.1118 | -115.9515 | -0.054932 | -0.1236 | 0.064087 | 0.65002 | -0.050354 | -0.082397 | 0.004578 | -0.027465 | -0.13275 | -0.036621 | 0.059509 | 0.42114 | 0.21515 | 0.054932 | 0.3479 | 0.18768 | 0.70496 | 122.1451 | 0.55389 | 122.2183 | 121.9574 | 122.1222 | 121.9025 | 121.9894 | -122.081 | -122.1588 | 122.0901 | 122.0856 | 116.0156 | 115.0314
1432.1875 | 122.3419 | -116.2125 | 5.8411 | -0.013657 | -0.0005063 | 0.058607 | 0.053694 | 0.00085879 | -0.0089743 | -0.0042575 | -0.0082093 | 0.001303 | 0.070442 | 0.065696 | -0.012014 | 0.01944 | -0.0044156 | -0.11444 | 5.6763 | -116.2582 | 5.9052 | -115.4846 | -116.2262 | -116.2308 | -1.1215 | 5.7678 | -116.304 | 5.8777 | -115.7181 | -116.0934 | -115.9653 | -0.045777 | -0.16479 | 0.064087 | 0.72784 | -0.018311 | -0.013733 | 0.027466 | 0.032044 | -0.091553 | -0.073242 | 0.036622 | 0.49438 | 0.24719 | 0.11902 | 0.33875 | 0.21057 | 0.77362 | 122.1634 | 0.58594 | 122.1817 | 121.9345 | 122.0718 | 121.8887 | 121.9803 | -122.0993 | -122.1451 | 122.1176 | 122.0901 | 116.098 | 115.0909
1433.9375 | 122.1954 | -116.153 | 5.9967 | -0.013657 | 0.0016299 | 0.060316 | 0.058607 | -0.003841 | -0.0055563 | -0.0016941 | -0.0021057 | 0.0027984 | 0.07151 | 0.066336 | -0.010946 | 0.020294 | -0.0014248 | -0.16937 | 5.8548 | -116.1621 | 5.8411 | -115.6265 | -116.3223 | -116.2994 | -1.3046 | 5.9052 | -116.272 | 5.8914 | -115.8234 | -116.1713 | -115.9515 | -0.009155 | -0.14191 | -0.15564 | 0.52643 | -0.14648 | -0.16937 | -0.13733 | -0.16022 | -0.11902 | -0.091553 | -0.10529 | 0.32959 | 0.20142 | -0.018311 | 0.32044 | 0.10071 | 0.53558 | 122.0032 | 0.44861 | 122.1634 | 122.0169 | 122.1771 | 122.0078 | 122.0581 | -122.1588 | -122.2687 | 121.994 | 122.0444 | 115.9836 | 114.8483
1435.6875 | 122.3465 | -116.4871 | 5.5847 | 0.0016023 | -0.0017881 | 0.059035 | 0.055617 | -0.0036274 | -0.0066245 | -0.0051121 | -0.0082093 | 0.00087584 | 0.073006 | 0.063773 | -0.0096643 | 0.018799 | -0.0037748 | -0.17395 | 5.4382 | -116.5192 | 5.571 | -115.8142 | -116.5466 | -116.5329 | -1.2085 | 5.5161 | -116.6107 | 5.6076 | -116.0522 | -116.391 | -116.2537 | -0.032043 | -0.14649 | -0.013733 | 0.67291 | -0.045776 | -0.059509 | -0.013733 | -0.027466 | -0.1236 | -0.068665 | 0.022888 | 0.43488 | 0.23346 | 0.096131 | 0.35706 | 0.21973 | 0.70496 | 122.0901 | 0.55847 | 122.2183 | 121.9574 | 122.1268 | 121.9254 | 122.0032 | -122.1039 | -122.1954 | 122.0581 | 122.0947 | 116.3132 | 115.2786
1437.375 | 122.2687 | -116.5558 | 5.5618 | -0.0060272 | 0.0012027 | 0.05818 | 0.05818 | -0.0023456 | -0.0089743 | -0.0051121 | -0.0021057 | 0.0025848 | 0.073006 | 0.064414 | -0.011587 | 0.022858 | -0.0031338 | -0.19226 | 5.4611 | -116.5375 | 5.4749 | -115.9744 | -116.6748 | -116.6382 | -1.2863 | 5.5298 | -116.6199 | 5.5252 | -116.1575 | -116.5237 | -116.3315 | 0.01831 | -0.10071 | -0.086975 | 0.58136 | -0.082398 | -0.11902 | -0.10071 | -0.13733 | -0.064087 | -0.032044 | -0.036621 | 0.39825 | 0.2243 | 0.032043 | 0.28839 | 0.09613 | 0.56305 | 122.0123 | 0.46234 | 122.1451 | 121.9986 | 122.1497 | 122.0169 | 122.0856 | -122.0993 | -122.1817 | 122.0306 | 122.081 | 116.3635 | 115.2695
1439.125 | 122.2275 | -116.5375 | 5.6259 | 0.0016023 | -0.0011471 | 0.057967 | 0.055189 | -0.0010638 | -0.0068381 | -0.0044711 | -0.0021057 | 0.0017304 | 0.073433 | 0.063559 | -0.0098779 | 0.019653 | 0.000925 | -0.1236 | 5.4794 | -116.5466 | 5.4657 | -115.9424 | -116.6107 | -116.6428 | -1.2589 | 5.5527 | -116.6382 | 5.4886 | -116.1758 | -116.5283 | -116.3544 | -0.009155 | -0.14649 | -0.16022 | 0.59509 | -0.10528 | -0.073242 | -0.09613 | -0.064087 | -0.10071 | -0.073243 | -0.13733 | 0.36163 | 0.18311 | 0.009156 | 0.28381 | 0.10986 | 0.60425 | 122.0123 | 0.46234 | 122.1268 | 122.0261 | 122.1909 | 122.0169 | 122.0901 | -122.1725 | -122.2641 | 122.0032 | 122.0261 | 116.4139 | 115.2786
1440.875 | 122.2595 | -116.5192 | 5.5893 | -0.0060272 | 0.0031253 | 0.058394 | 0.058607 | 4.192e-06 | -0.0055563 | -0.0016941 | -0.0051575 | 0.0010894 | 0.070229 | 0.0689 | -0.011373 | 0.019226 | -0.0001432 | -0.25177 | 5.452 | -116.5741 | 5.5161 | -115.9744 | -116.6885 | -116.6611 | -1.3412 | 5.5023 | -116.6382 | 5.5069 | -116.153 | -116.5283 | -116.3315 | -0.054932 | -0.13733 | -0.073242 | 0.54474 | -0.14191 | -0.16937 | -0.086975 | -0.11444 | -0.11902 | -0.086975 | -0.082397 | 0.36621 | 0.18768 | -0.009155 | 0.3067 | 0.10986 | 0.59967 | 122.0901 | 0.48523 | 122.1451 | 122.0261 | 122.1405 | 121.9711 | 122.0215 | -122.1634 | -122.2275 | 122.0352 | 122.0261 | 116.2674 | 115.1779
1442.625 | 122.2321 | -116.6931 | 5.4428 | -0.021286 | 0.0016299 | 0.057967 | 0.055403 | -0.00085021 | -0.0083335 | -0.00062587 | -0.0051575 | 0.0021576 | 0.071083 | 0.062491 | -0.010519 | 0.019012 | -0.0031338 | -0.091553 | 5.2643 | -116.7206 | 5.3696 | -116.0568 | -116.7709 | -116.7664 | -1.2589 | 5.3558 | -116.7984 | 5.3329 | -116.3086 | -116.6473 | -116.5192 | -0.027466 | -0.17853 | -0.073242 | 0.63629 | -0.073242 | -0.07782 | -0.045776 | -0.050354 | -0.10529 | -0.086975 | -0.10986 | 0.38452 | 0.17395 | 0.045776 | 0.27924 | 0.15106 | 0.66376 | 122.0901 | 0.48981 | 122.1313 | 121.9849 | 122.1542 | 121.9574 | 122.049 | -122.1634 | -122.2412 | 122.0627 | 122.0261 | 116.6016 | 115.4343
1444.3125 | 122.2366 | -116.9083 | 5.2597 | -0.0060272 | -0.0015743 | 0.057967 | 0.057326 | -0.0040546 | -0.0083335 | -0.0012669 | -0.0051575 | 0.0023712 | 0.073647 | 0.067618 | -0.01351 | 0.020294 | -0.0031338 | -0.13733 | 5.1086 | -116.9403 | 5.1178 | -116.2994 | -116.9861 | -116.9861 | -1.3 | 5.2094 | -116.9815 | 5.1132 | -116.5329 | -116.89 | -116.7297 | -0.032044 | -0.15106 | -0.14191 | 0.60883 | -0.07782 | -0.07782 | -0.045776 | -0.045776 | -0.073242 | -0.050354 | -0.14649 | 0.37537 | 0.17853 | 0.01831 | 0.25177 | 0.091552 | 0.64087 | 122.0581 | 0.44861 | 122.0947 | 122.049 | 122.1909 | 122.0169 | 122.1176 | -122.2 | -122.2412 | 122.0261 | 122.0215 | 116.7709 | 115.6082
1446 | 122.3511 | -116.9952 | 5.0583 | -0.0060272 | 0.0016299 | 0.06053 | 0.057326 | -0.0051226 | -0.0042745 | -0.00062587 | -0.0051575 | -0.0010468 | 0.071083 | 0.069541 | -0.010946 | 0.021149 | -0.0009976 | -0.14191 | 4.9393 | -116.9907 | 5.1086 | -116.2994 | -117.0502 | -117.0456 | -1.2589 | 4.9896 | -117.0959 | 5.1132 | -116.5283 | -116.8945 | -116.7114 | 0.004577 | -0.11902 | 0.050354 | 0.6958 | -0.050354 | -0.054932 | -0.054931 | -0.059509 | -0.10071 | -0.068665 | 0.054931 | 0.46692 | 0.28381 | 0.10071 | 0.38452 | 0.20142 | 0.69122 | 122.0993 | 0.56763 | 122.2092 | 121.9299 | 122.0856 | 121.9345 | 121.9849 | -122.049 | -122.1542 | 122.1039 | 122.1085 | 116.8533 | 115.7364
1447.75 | 122.3373 | -117.16 | 4.8706 | -0.0060272 | -0.0015743 | 0.056471 | 0.056044 | -0.0064044 | -0.0079061 | -0.0023349 | -0.0082093 | -0.0016876 | 0.070656 | 0.058646 | -0.0098779 | 0.020721 | -0.0078336 | -0.091553 | 4.7104 | -117.2379 | 4.9255 | -116.4597 | -117.1829 | -117.1783 | -1.181 | 4.8203 | -117.2836 | 4.9118 | -116.7023 | -117.0593 | -116.9174 | -0.07782 | -0.16022 | 0.054932 | 0.70038 | -0.018311 | -0.022888 | 0.059509 | 0.054932 | -0.1236 | -0.050354 | 0.041199 | 0.45776 | 0.24262 | 0.10071 | 0.36621 | 0.2243 | 0.7782 | 122.1634 | 0.58136 | 122.1954 | 121.9482 | 122.1039 | 121.8704 | 121.9803 | -122.1085 | -122.1542 | 122.0856 | 122.0718 | 117.0685 | 115.979
1449.4531 | 122.3419 | -117.2882 | 4.7974 | -0.013657 | -0.0028561 | 0.060103 | 0.053908 | -0.006618 | -0.0068381 | -0.0046847 | -0.0051575 | 0.0015166 | 0.072151 | 0.063346 | -0.013082 | 0.019012 | -0.0022794 | -0.068665 | 4.6234 | -117.3477 | 4.834 | -116.5878 | -117.2974 | -117.3248 | -1.1948 | 4.6967 | -117.3843 | 4.8157 | -116.7847 | -117.16 | -116.9998 | -0.059509 | -0.17395 | 0.036621 | 0.70038 | -0.036621 | -0.009155 | 0.022888 | 0.050354 | -0.09613 | -0.10071 | 0.018311 | 0.50354 | 0.28839 | 0.12817 | 0.38452 | 0.2243 | 0.75989 | 122.1817 | 0.59967 | 122.2 | 121.9711 | 122.081 | 121.9116 | 121.9849 | -122.1451 | -122.1817 | 122.1222 | 122.1039 | 117.2195 | 116.0934
1451.1875 | 122.3145 | -117.3523 | 4.7287 | -0.013657 | -7.9104e-05 | 0.058394 | 0.055617 | -0.00085021 | -0.0072653 | -0.0025485 | -0.0021057 | 0.0010894 | 0.072365 | 0.065268 | -0.010732 | 0.019012 | 0.000925 | -0.17853 | 4.5731 | -117.3706 | 4.747 | -116.6748 | -117.421 | -117.3981 | -1.2863 | 4.6417 | -117.4484 | 4.7379 | -116.9449 | -117.2791 | -117.1051 | -0.01831 | -0.15564 | 0.01831 | 0.67749 | -0.045776 | -0.068664 | -0.027466 | -0.050354 | -0.09613 | -0.086975 | 0.009155 | 0.40741 | 0.24719 | 0.073242 | 0.34332 | 0.16937 | 0.6958 | 122.1176 | 0.50354 | 122.1863 | 121.9437 | 122.0901 | 121.9254 | 121.994 | -122.0993 | -122.1771 | 122.0993 | 122.0901 | 117.1738 | 116.066
1452.9375 | 122.2046 | -117.572 | 4.5639 | -0.013657 | 0.0024845 | 0.058607 | 0.057967 | 0.0034222 | -0.010897 | -0.0046847 | -0.0051575 | 0.0021576 | 0.07151 | 0.068686 | -0.012228 | 0.020935 | -0.005911 | -0.16937 | 4.3991 | -117.6361 | 4.4632 | -116.9678 | -117.6956 | -117.691 | -1.3962 | 4.4952 | -117.6682 | 4.4678 | -117.215 | -117.5949 | -117.3935 | -0.064087 | -0.16479 | -0.10071 | 0.60425 | -0.11902 | -0.1236 | -0.054932 | -0.05951 | -0.096131 | -0.068665 | -0.096131 | 0.35706 | 0.17853 | -0.022889 | 0.27466 | 0.073242 | 0.66833 | 122.0993 | 0.45319 | 122.1359 | 122.0352 | 122.1634 | 121.9711 | 122.0673 | -122.2 | -122.2321 | 122.0352 | 122.0398 | 117.4026 | 116.1758
1454.6875 | 122.3511 | -117.6315 | 4.4174 | -0.013657 | 0.0016299 | 0.062239 | 0.056044 | -0.0012774 | -0.0066245 | -0.0031895 | -0.0082093 | 0.00087584 | 0.073006 | 0.063773 | -0.01116 | 0.020081 | -0.0029202 | -0.16937 | 4.2938 | -117.6773 | 4.4678 | -116.9495 | -117.691 | -117.6682 | -1.3229 | 4.3625 | -117.746 | 4.4769 | -117.1875 | -117.5446 | -117.3706 | -0.045776 | -0.1236 | 0.050354 | 0.68207 | -0.036621 | -0.059509 | 0.009155 | -0.013733 | -0.11444 | -0.054931 | 0.05951 | 0.44403 | 0.26093 | 0.086975 | 0.37537 | 0.20142 | 0.72784 | 122.1451 | 0.55847 | 122.2229 | 121.9711 | 122.1085 | 121.9254 | 121.994 | -122.0947 | -122.1634 | 122.0993 | 122.1085 | 117.4622 | 116.3086
1456.375 | 122.2687 | -117.746 | 4.3991 | -0.013657 | 0.0005619 | 0.057112 | 0.057967 | -0.0025592 | -0.0068381 | -0.0021213 | -0.0082093 | 0.0015166 | 0.072792 | 0.067405 | -0.010305 | 0.020294 | -0.003561 | -0.10529 | 4.2618 | -117.7597 | 4.3396 | -117.0868 | -117.8146 | -117.8192 | -1.3458 | 4.3167 | -117.8192 | 4.3304 | -117.3203 | -117.7002 | -117.485 | -0.013733 | -0.13733 | -0.059509 | 0.65918 | -0.073242 | -0.068664 | -0.059509 | -0.054931 | -0.073242 | -0.082398 | -0.068665 | 0.42572 | 0.26093 | 0.045777 | 0.33417 | 0.11902 | 0.67291 | 122.0993 | 0.49896 | 122.1497 | 122.0215 | 122.1359 | 122.0078 | 122.0627 | -122.1588 | -122.2183 | 122.0856 | 122.0764 | 117.6407 | 116.4001
1458.125 | 122.3511 | -117.8192 | 4.2526 | -0.0060272 | 0.0003483 | 0.060744 | 0.059889 | 0.004704 | -0.0089743 | -0.0027621 | -0.0051575 | 0.0017304 | 0.072578 | 0.067405 | -0.010305 | 0.021576 | -0.0031338 | -0.21515 | 4.1199 | -117.8513 | 4.2435 | -117.1783 | -117.9245 | -117.9199 | -1.3779 | 4.1519 | -117.9611 | 4.303 | -117.3569 | -117.746 | -117.5171 | -0.032043 | -0.13275 | -0.009156 | 0.64087 | -0.10071 | -0.10529 | -0.068665 | -0.073243 | -0.14191 | -0.10071 | 0.050354 | 0.46234 | 0.30212 | 0.073242 | 0.44403 | 0.21515 | 0.67291 | 122.0947 | 0.60425 | 122.2641 | 121.9711 | 122.113 | 121.9391 | 121.9711 | -122.1039 | -122.2137 | 122.0627 | 122.1222 | 117.6041 | 116.4413
1459.875 | 122.3465 | -117.9611 | 4.1107 | -0.013657 | 0.0033389 | 0.059676 | 0.057326 | -0.00085021 | -0.0055563 | -0.0031895 | -0.0051575 | 0.0017304 | 0.073219 | 0.060569 | -0.012441 | 0.020294 | -0.0031338 | -0.20599 | 3.9459 | -117.9932 | 4.1382 | -117.2882 | -118.0069 | -118.0069 | -1.387 | 4.0329 | -118.0756 | 4.1611 | -117.4942 | -117.8604 | -117.6773 | -0.032043 | -0.1648 | 0.027466 | 0.67291 | -0.045776 | -0.045776 | -0.013733 | -0.013733 | -0.11444 | -0.07782 | 0.050354 | 0.46692 | 0.28381 | 0.10071 | 0.39826 | 0.21515 | 0.70496 | 122.1313 | 0.58136 | 122.2366 | 121.9391 | 122.1085 | 121.907 | 121.994 | -122.1039 | -122.1863 | 122.0993 | 122.1222 | 117.7551 | 116.5741
1461.625 | 122.3419 | -118.6295 | 3.4332 | -0.021286 | 0.0016299 | 0.060316 | 0.054762 | -0.00020941 | -0.0061971 | -0.00062587 | -0.0021057 | 2.1442e-05 | 0.071297 | 0.058432 | -0.011801 | 0.019226 | -0.002493 | -0.19684 | 3.3096 | -118.6523 | 3.4561 | -117.9657 | -118.6981 | -118.6798 | -1.387 | 3.36 | -118.7531 | 3.4607 | -118.1808 | -118.5379 | -118.3823 | -0.022888 | -0.1236 | 0.022888 | 0.66376 | -0.050354 | -0.068664 | -0.027466 | -0.045776 | -0.1236 | -0.073243 | 0.027465 | 0.44861 | 0.24719 | 0.091553 | 0.37079 | 0.21515 | 0.68665 | 122.1085 | 0.5722 | 122.2137 | 121.962 | 122.113 | 121.9391 | 121.9894 | -122.0856 | -122.1863 | 122.0856 | 122.0901 | 118.4326 | 117.2424
1463.2969 | 122.2687 | -118.7485 | 3.3783 | -0.0060272 | 0.0003483 | 0.058394 | 0.056898 | -0.00020941 | -0.0081197 | -0.0025485 | -0.0051575 | 0.0038666 | 0.074501 | 0.060141 | -0.011587 | 0.020081 | -0.0003568 | -0.11444 | 3.2364 | -118.8217 | 3.2959 | -118.1122 | -118.84 | -118.8354 | -1.4053 | 3.3051 | -118.8675 | 3.3051 | -118.3319 | -118.7256 | -118.5608 | -0.073242 | -0.14191 | -0.082398 | 0.63629 | -0.086975 | -0.091553 | -0.013733 | -0.018311 | -0.11902 | -0.073242 | -0.073242 | 0.41657 | 0.18768 | 0.022888 | 0.3067 | 0.14191 | 0.70953 | 122.1176 | 0.53558 | 122.1725 | 122.0581 | 122.1725 | 121.9849 | 122.0535 | -122.2 | -122.2458 | 122.0444 | 122.0535 | 118.634 | 117.3431
1465.0469 | 122.2321 | -118.8812 | 3.3234 | -0.0060272 | -0.0020017 | 0.056898 | 0.053053 | 0.001286 | -0.0064109 | -0.00062587 | -0.0021057 | -0.00083316 | 0.073433 | 0.055442 | -0.0098779 | 0.018158 | -0.0016384 | -0.13733 | 3.1357 | -118.8858 | 3.1586 | -118.2404 | -118.9499 | -118.9545 | -1.4877 | 3.2318 | -118.9728 | 3.1586 | -118.4601 | -118.8263 | -118.689 | -0.004577 | -0.18768 | -0.1648 | 0.64087 | -0.073242 | -0.068664 | -0.068665 | -0.064087 | -0.091552 | -0.091552 | -0.1648 | 0.42114 | 0.19226 | 0.054932 | 0.28381 | 0.14648 | 0.64545 | 122.0444 | 0.5127 | 122.1313 | 122.0215 | 122.2046 | 122.0169 | 122.113 | -122.2092 | -122.2961 | 122.0398 | 122.0398 | 118.7439 | 117.3935
1466.7969 | 122.3373 | -118.8126 | 3.2501 | -0.013657 | 0.0005619 | 0.059889 | 0.056685 | 4.192e-06 | -0.0064109 | -0.0057529 | -0.0021057 | 0.00023504 | 0.072151 | 0.061423 | -0.010092 | 0.018158 | -0.0027066 | -0.14648 | 3.1174 | -118.8263 | 3.2639 | -118.1396 | -118.8812 | -118.8721 | -1.4465 | 3.154 | -118.9545 | 3.2639 | -118.364 | -118.7302 | -118.5837 | -0.013733 | -0.13275 | 0.013733 | 0.67291 | -0.059509 | -0.068665 | -0.045776 | -0.054932 | -0.14191 | -0.09613 | 0.013733 | 0.44861 | 0.22888 | 0.082397 | 0.37079 | 0.2243 | 0.68665 | 122.0901 | 0.59052 | 122.2183 | 121.9437 | 122.1085 | 121.9299 | 121.9666 | -122.0764 | -122.2046 | 122.0764 | 122.0764 | 118.6661 | 117.366
1468.5625 | 122.2641 | -118.8904 | 3.2501 | 0.0016023 | 0.0020571 | 0.056258 | 0.055617 | -0.0012774 | -0.0091879 | -0.0021213 | -0.0021057 | 0.0017304 | 0.072578 | 0.062918 | -0.010732 | 0.018158 | -0.0056974 | -0.11444 | 3.1311 | -118.9133 | 3.1494 | -118.2678 | -118.9682 | -118.9819 | -1.4648 | 3.1815 | -118.9957 | 3.154 | -118.4601 | -118.8538 | -118.6707 | -0.022888 | -0.11902 | -0.10071 | 0.62256 | -0.091553 | -0.07782 | -0.068665 | -0.054932 | -0.10529 | -0.068664 | -0.09613 | 0.4303 | 0.21973 | 0.036621 | 0.32501 | 0.14191 | 0.64545 | 122.0627 | 0.53558 | 122.1497 | 122.0444 | 122.1771 | 122.0215 | 122.0718 | -122.1634 | -122.2458 | 122.0398 | 122.0444 | 118.7759 | 117.4255
1470.25 | 122.3145 | -118.8858 | 3.2318 | -0.013657 | -0.0030697 | 0.056898 | 0.054335 | 0.00021799 | -0.0066245 | -0.0048985 | 0.0009461 | 0.0015166 | 0.072365 | 0.057578 | -0.010732 | 0.018799 | 0.000925 | -0.2243 | 3.0853 | -118.895 | 3.1769 | -118.2266 | -118.9453 | -118.9362 | -1.5472 | 3.1586 | -118.9957 | 3.1906 | -118.4509 | -118.8034 | -118.6157 | -0.009155 | -0.14649 | -0.054932 | 0.65918 | -0.050354 | -0.059509 | -0.041199 | -0.050354 | -0.10986 | -0.073243 | -0.041199 | 0.43487 | 0.27008 | 0.082397 | 0.37994 | 0.19226 | 0.66833 | 122.0718 | 0.54474 | 122.1863 | 121.9803 | 122.1542 | 121.9711 | 122.0444 | -122.1268 | -122.2275 | 122.0627 | 122.0764 | 118.6615 | 117.3386
1472.0312 | 122.2412 | -118.9133 | 3.2547 | 0.0016023 | 0.0001345 | 0.059462 | 0.060316 | -0.0044818 | -0.0083335 | -0.0040439 | -0.0021057 | 0.0040802 | 0.071297 | 0.061637 | -0.012655 | 0.022217 | -0.0046292 | -0.1236 | 3.1219 | -118.9087 | 3.154 | -118.2678 | -118.9865 | -118.9819 | -1.5015 | 3.1631 | -118.9819 | 3.1677 | -118.4921 | -118.8858 | -118.6523 | 0.004578 | -0.13275 | -0.10071 | 0.64545 | -0.068665 | -0.073242 | -0.073243 | -0.07782 | -0.068665 | -0.091553 | -0.086975 | 0.42114 | 0.26093 | 0.027466 | 0.32959 | 0.096131 | 0.64087 | 122.0627 | 0.48981 | 122.1497 | 122.0306 | 122.1451 | 122.0352 | 122.0764 | -122.1634 | -122.2366 | 122.0673 | 122.081 | 118.7897 | 117.4118
1473.7812 | 122.2595 | -118.8995 | 3.2593 | -0.0060272 | -0.0005063 | 0.05818 | 0.060744 | -0.0019184 | -0.0070517 | -0.0059665 | -0.0021057 | 0.0038666 | 0.071938 | 0.066764 | -0.01116 | 0.020294 | -0.000784 | -0.11902 | 3.0762 | -118.9087 | 3.154 | -118.2495 | -118.9682 | -118.9636 | -1.474 | 3.1631 | -118.9682 | 3.1631 | -118.4738 | -118.8538 | -118.6478 | -0.009155 | -0.1831 | -0.10528 | 0.65002 | -0.064087 | -0.068665 | -0.054932 | -0.05951 | -0.068665 | -0.09613 | -0.09613 | 0.42572 | 0.25177 | 0.045776 | 0.32043 | 0.11444 | 0.65918 | 122.0627 | 0.49438 | 122.1313 | 121.9849 | 122.1313 | 121.9757 | 122.0627 | -122.168 | -122.2275 | 122.0535 | 122.0627 | 118.7805 | 117.4255
1475.4688 | 122.2549 | -118.9682 | 3.1677 | -0.021286 | 0.0003483 | 0.058821 | 0.054549 | -0.00020941 | -0.0070517 | -0.0038303 | -0.0051575 | 0.003012 | 0.072365 | 0.061423 | -0.012441 | 0.021149 | 0.0015658 | -0.12817 | 3.0487 | -119.0186 | 3.0441 | -118.3685 | -119.0735 | -119.0781 | -1.5381 | 3.1082 | -119.0735 | 3.0899 | -118.5333 | -118.9178 | -118.7302 | -0.050354 | -0.11902 | -0.1236 | 0.59967 | -0.10986 | -0.10529 | -0.059509 | -0.054931 | -0.10529 | -0.05951 | -0.07782 | 0.43488 | 0.23804 | 0.050354 | 0.34332 | 0.15564 | 0.65002 | 122.0627 | 0.54016 | 122.1634 | 122.0673 | 122.1817 | 122.0169 | 122.0764 | -122.1863 | -122.2412 | 122.0123 | 122.0581 | 118.84 | 117.4301
1477.2188 | 122.3236 | -118.9682 | 3.1265 | -0.0060272 | 0.0001345 | 0.057753 | 0.05284 | 0.0017132 | -0.0072653 | -0.0029759 | -0.0082093 | 2.1442e-05 | 0.072365 | 0.063346 | -0.010305 | 0.018799 | -0.0022794 | -0.17853 | 2.9755 | -119.0186 | 3.0533 | -118.3273 | -119.0369 | -119.0414 | -1.5518 | 3.0396 | -119.0918 | 3.1082 | -118.5196 | -118.8675 | -118.7027 | -0.050354 | -0.15106 | -0.073242 | 0.64087 | -0.073242 | -0.068664 | -0.022888 | -0.01831 | -0.1236 | -0.086975 | -0.018311 | 0.44861 | 0.2655 | 0.10071 | 0.3891 | 0.2243 | 0.69122 | 122.0718 | 0.5722 | 122.2 | 121.994 | 122.1313 | 121.9437 | 122.0078 | -122.1451 | -122.2183 | 122.0215 | 122.0764 | 118.7897 | 117.4164
1478.9844 | 122.2961 | -119.0781 | 3.0304 | -0.0060272 | 0.0009891 | 0.059035 | 0.056258 | -0.00085021 | -0.0059835 | -0.0021213 | -0.0051575 | -0.00019216 | 0.071724 | 0.060141 | -0.01116 | 0.020935 | 0.0019932 | -0.1831 | 2.8839 | -119.0735 | 3.0075 | -118.396 | -119.133 | -119.1147 | -1.5884 | 2.948 | -119.165 | 3.0029 | -118.6478 | -118.9957 | -118.8126 | 0.004578 | -0.14649 | -0.022889 | 0.68207 | -0.036621 | -0.054932 | -0.041199 | -0.05951 | -0.086975 | -0.082398 | -0.027466 | 0.4303 | 0.2655 | 0.082397 | 0.35248 | 0.16937 | 0.67749 | 122.081 | 0.51727 | 122.168 | 121.9574 | 122.113 | 121.962 | 122.0261 | -122.1039 | -122.1954 | 122.0856 | 122.081 | 118.895 | 117.4896
1480.6719 | 122.2458 | -119.3024 | 2.8519 | -0.021286 | 0.0009891 | 0.06053 | 0.057112 | 0.0038494 | -0.0057699 | -0.0031895 | 0.0009461 | 0.0021576 | 0.071083 | 0.059928 | -0.011587 | 0.021149 | -0.000784 | -0.13733 | 2.7008 | -119.3298 | 2.7466 | -118.6615 | -119.3939 | -119.3939 | -1.5884 | 2.7649 | -119.3985 | 2.7512 | -118.895 | -119.2703 | -119.0643 | -0.027466 | -0.15106 | -0.10529 | 0.64087 | -0.091553 | -0.091553 | -0.064087 | -0.064087 | -0.096131 | -0.086975 | -0.10071 | 0.40741 | 0.23804 | 0.032043 | 0.33417 | 0.12817 | 0.66833 | 122.0764 | 0.50354 | 122.1497 | 122.0306 | 122.1634 | 122.0032 | 122.0673 | -122.1817 | -122.2504 | 122.049 | 122.0535 | 119.165 | 117.7139
1482.3438 | 122.3557 | -119.3756 | 2.7145 | -0.0060272 | -7.9104e-05 | 0.059035 | 0.05284 | -0.0012774 | -0.0079061 | -0.0023349 | -0.0051575 | -0.001474 | 0.072151 | 0.061209 | -0.011801 | 0.019012 | -0.0033474 | -0.09613 | 2.5543 | -119.4122 | 2.7145 | -118.6432 | -119.371 | -119.3619 | -1.4969 | 2.6459 | -119.4901 | 2.7145 | -118.8721 | -119.2474 | -119.0781 | -0.036621 | -0.16022 | 0 | 0.73242 | 0.013733 | 0.004577 | 0.050354 | 0.041198 | -0.11444 | -0.068665 | 0 | 0.50354 | 0.29755 | 0.12817 | 0.41199 | 0.24261 | 0.76904 | 122.1268 | 0.61798 | 122.2046 | 121.9666 | 122.1359 | 121.9299 | 122.0215 | -122.1268 | -122.2046 | 122.0901 | 122.0901 | 119.2795 | 117.8787
1484.0938 | 122.3053 | -119.4855 | 2.623 | -0.013657 | 0.0026981 | 0.058394 | 0.056044 | 4.192e-06 | -0.0091879 | -0.0042575 | -0.0051575 | -0.00019216 | 0.071938 | 0.053305 | -0.012441 | 0.018799 | -0.0001432 | -0.2243 | 2.4673 | -119.4855 | 2.5681 | -118.8263 | -119.5679 | -119.5267 | -1.6617 | 2.5406 | -119.5862 | 2.5955 | -119.0506 | -119.4214 | -119.22 | 0 | -0.15564 | -0.054932 | 0.65918 | -0.041198 | -0.082397 | -0.041198 | -0.082397 | -0.10071 | -0.082398 | -0.027466 | 0.43488 | 0.2655 | 0.064087 | 0.36621 | 0.16479 | 0.65918 | 122.0535 | 0.53558 | 122.1817 | 121.9528 | 122.1268 | 121.9528 | 122.0261 | -122.1085 | -122.2092 | 122.0535 | 122.081 | 119.2612 | 117.8238
1485.7656 | 122.2778 | -119.5404 | 2.6093 | -0.0060272 | 0.0016299 | 0.057753 | 0.059248 | 0.00043159 | -0.0070517 | -0.0038303 | -0.011261 | 0.0032256 | 0.071938 | 0.064841 | -0.012441 | 0.018158 | -0.0009976 | -0.1236 | 2.4307 | -119.5908 | 2.5085 | -118.8858 | -119.6457 | -119.6365 | -1.5839 | 2.5269 | -119.6503 | 2.5131 | -119.1376 | -119.5129 | -119.2978 | -0.050354 | -0.17853 | -0.10071 | 0.6546 | -0.096131 | -0.10529 | -0.045777 | -0.054932 | -0.10986 | -0.082398 | -0.09613 | 0.40283 | 0.24261 | 0.027466 | 0.35248 | 0.13733 | 0.70496 | 122.0993 | 0.5127 | 122.1634 | 122.0215 | 122.1771 | 121.9711 | 122.0673 | -122.2 | -122.2595 | 122.049 | 122.0535 | 119.4168 | 117.9565
1487.4531 | 122.2687 | -119.7235 | 2.417 | -0.013657 | 0.0018435 | 0.059248 | 0.057539 | 0.00043159 | -0.0085471 | -0.0031895 | -0.0051575 | 0.00044864 | 0.072578 | 0.068473 | -0.013082 | 0.020508 | 0.0002842 | -0.14191 | 2.2659 | -119.7556 | 2.3071 | -119.1101 | -119.783 | -119.8196 | -1.6388 | 2.3666 | -119.8013 | 2.3438 | -119.3024 | -119.6732 | -119.4763 | -0.032043 | -0.15106 | -0.10986 | 0.6134 | -0.09613 | -0.059509 | -0.064087 | -0.027466 | -0.07782 | -0.050354 | -0.073242 | 0.42114 | 0.24719 | 0.050354 | 0.32501 | 0.12817 | 0.64545 | 122.0627 | 0.49896 | 122.1451 | 122.0215 | 122.168 | 121.9894 | 122.0901 | -122.1725 | -122.2183 | 122.0306 | 122.0673 | 119.5816 | 118.0847
1489.1406 | 122.3648 | -119.751 | 2.3346 | -0.0060272 | -0.0034971 | 0.057967 | 0.054335 | -0.0040546 | -0.0076925 | 1.4934e-05 | -0.0021057 | 2.1442e-05 | 0.072365 | 0.063987 | -0.010732 | 0.017517 | -0.0003568 | -0.12817 | 2.1835 | -119.7922 | 2.3209 | -119.046 | -119.7739 | -119.7784 | -1.5793 | 2.2614 | -119.8563 | 2.3575 | -119.252 | -119.6091 | -119.4489 | -0.041198 | -0.15106 | -0.013733 | 0.70496 | -0.027465 | -0.022888 | 0.013733 | 0.01831 | -0.10528 | -0.073242 | 0.022888 | 0.49896 | 0.30212 | 0.14191 | 0.40741 | 0.24719 | 0.74615 | 122.113 | 0.60425 | 122.2137 | 121.9757 | 122.1176 | 121.9345 | 122.0123 | -122.1268 | -122.1909 | 122.0718 | 122.1085 | 119.6228 | 118.1717
1490.8906 | 122.2275 | -119.8746 | 2.3163 | -0.0060272 | -0.0002927 | 0.058394 | 0.054976 | -0.003841 | -0.0070517 | -0.0029759 | -0.0051575 | 0.0017304 | 0.070229 | 0.063987 | -0.010519 | 0.018372 | -0.0012112 | -0.14191 | 2.179 | -119.8791 | 2.1561 | -119.2474 | -119.9615 | -119.9707 | -1.712 | 2.2614 | -119.9524 | 2.1606 | -119.4763 | -119.838 | -119.6411 | -0.004577 | -0.13733 | -0.16022 | 0.62714 | -0.09613 | -0.086975 | -0.091553 | -0.082398 | -0.07782 | -0.054931 | -0.15564 | 0.39825 | 0.23346 | 0.036621 | 0.31128 | 0.11444 | 0.63171 | 122.0352 | 0.47607 | 122.113 | 122.0581 | 122.2137 | 122.0535 | 122.1359 | -122.1954 | -122.2687 | 122.0306 | 122.0352 | 119.7327 | 118.1625
1492.6406 | 122.3511 | -119.8837 | 2.211 | -0.0060272 | 0.0016299 | 0.058394 | 0.057112 | -0.00063661 | -0.0055563 | -0.0036167 | -0.0021057 | 2.1442e-05 | 0.070229 | 0.056937 | -0.012014 | 0.019653 | -0.002493 | -0.18768 | 2.0508 | -119.9158 | 2.1927 | -119.2154 | -119.9432 | -119.9432 | -1.68 | 2.1286 | -119.9844 | 2.243 | -119.4214 | -119.7876 | -119.5541 | -0.032043 | -0.16022 | -0.018311 | 0.66833 | -0.059509 | -0.059509 | -0.027466 | -0.027466 | -0.10071 | -0.082398 | 0.032043 | 0.46234 | 0.32959 | 0.09613 | 0.4303 | 0.19684 | 0.70038 | 122.1085 | 0.56305 | 122.2275 | 121.9666 | 122.113 | 121.9345 | 122.0123 | -122.1268 | -122.1954 | 122.0764 | 122.1268 | 119.696 | 118.2037
1494.3281 | 122.3236 | -119.9707 | 2.1423 | -0.013657 | -0.0022153 | 0.06053 | 0.054762 | -0.00020941 | -0.0079061 | -0.0051121 | -0.0021057 | 2.1442e-05 | 0.072578 | 0.055442 | -0.011801 | 0.019226 | 0.0002842 | -0.10529 | 1.9775 | -120.0256 | 2.1332 | -119.2657 | -119.989 | -119.9799 | -1.6342 | 2.0462 | -120.0714 | 2.1332 | -119.4809 | -119.8425 | -119.6274 | -0.054932 | -0.1648 | -0.009155 | 0.70496 | -0.009155 | -0.018311 | 0.045777 | 0.036621 | -0.10071 | -0.09613 | -0.009155 | 0.48981 | 0.34332 | 0.12817 | 0.44403 | 0.22888 | 0.75989 | 122.1588 | 0.59051 | 122.2046 | 122.0032 | 122.1176 | 121.9482 | 122.0169 | -122.168 | -122.2137 | 122.1039 | 122.1039 | 119.8654 | 118.3365
1496.0781 | 122.2961 | -120.0256 | 2.0737 | -0.013657 | 0.0018435 | 0.057967 | 0.056258 | -0.0023456 | -0.0079061 | -0.0040439 | -0.0082093 | 0.00087584 | 0.073433 | 0.061637 | -0.012655 | 0.020081 | -0.0027066 | -0.2243 | 1.9318 | -120.0577 | 2.0187 | -119.3802 | -120.1126 | -120.0806 | -1.767 | 2.0096 | -120.1263 | 2.0462 | -119.5908 | -119.9524 | -119.7189 | -0.032043 | -0.14191 | -0.054931 | 0.64545 | -0.054931 | -0.086975 | -0.022888 | -0.054932 | -0.10071 | -0.064086 | -0.027465 | 0.43488 | 0.3067 | 0.073242 | 0.40741 | 0.17395 | 0.67749 | 122.0764 | 0.53558 | 122.1725 | 121.9894 | 122.1359 | 121.9574 | 122.0352 | -122.1313 | -122.2 | 122.0444 | 122.0718 | 119.8013 | 118.2587
1497.8125 | 122.2549 | -120.108 | 2.0737 | -0.0060272 | 0.0003483 | 0.05818 | 0.060103 | -0.0036274 | -0.0066245 | -0.0044711 | -0.0051575 | 0.003012 | 0.071297 | 0.063346 | -0.013082 | 0.01944 | -0.0054838 | -0.14648 | 1.9272 | -120.1401 | 1.9135 | -119.5038 | -120.1996 | -120.1996 | -1.7715 | 2.0004 | -120.1767 | 1.9409 | -119.6777 | -120.0531 | -119.8425 | -0.032044 | -0.14648 | -0.16022 | 0.60425 | -0.091553 | -0.091553 | -0.059509 | -0.059509 | -0.068665 | -0.073242 | -0.13275 | 0.4303 | 0.2655 | 0.054931 | 0.33417 | 0.1236 | 0.63629 | 122.0535 | 0.49896 | 122.1176 | 122.0673 | 122.1771 | 122.0352 | 122.1085 | -122.2137 | -122.2504 | 122.0215 | 122.0489 | 119.9615 | 118.3365
1499.5781 | 122.3236 | -120.1218 | 1.9867 | -0.0060272 | 0.0033389 | 0.060316 | 0.058821 | 0.0036358 | -0.0070517 | -0.0036167 | -0.0082093 | 0.003012 | 0.075142 | 0.057364 | -0.012869 | 0.01944 | 7.04e-05 | -0.25635 | 1.8677 | -120.163 | 1.8997 | -119.5038 | -120.2408 | -120.2362 | -1.8082 | 1.9318 | -120.2087 | 1.9913 | -119.6732 | -120.0485 | -119.8425 | -0.041199 | -0.11902 | -0.086975 | 0.61798 | -0.11444 | -0.11902 | -0.073242 | -0.07782 | -0.086975 | -0.054931 | 0.004578 | 0.44861 | 0.27924 | 0.073242 | 0.36621 | 0.16022 | 0.65918 | 122.0627 | 0.53558 | 122.2 | 122.0306 | 122.1405 | 121.9894 | 122.0535 | -122.1497 | -122.1954 | 122.0215 | 122.113 | 119.8654 | 118.3136
1501.2656 | 122.2641 | -120.1584 | 1.9958 | -0.013657 | -7.9104e-05 | 0.057326 | 0.058821 | -0.003841 | -0.0068381 | -0.0042575 | -0.0021057 | 0.0015166 | 0.07151 | 0.066764 | -0.010519 | 0.019653 | -0.0044156 | -0.13275 | 1.8539 | -120.2225 | 1.8539 | -119.5496 | -120.2454 | -120.2545 | -1.7899 | 1.9272 | -120.2454 | 1.9043 | -119.7327 | -120.1126 | -119.9066 | -0.064087 | -0.14191 | -0.14191 | 0.60882 | -0.096131 | -0.086975 | -0.032044 | -0.022888 | -0.086975 | -0.068665 | -0.091553 | 0.42572 | 0.25177 | 0.045776 | 0.33875 | 0.13275 | 0.67291 | 122.0764 | 0.5127 | 122.1497 | 122.0764 | 122.1725 | 122.0123 | 122.0856 | -122.2183 | -122.2412 | 122.0123 | 122.0627 | 120.0256 | 118.3685
1503.0312 | 122.2504 | -120.2087 | 1.9501 | -0.0060272 | 0.0029117 | 0.05818 | 0.057753 | -0.0023456 | -0.0070517 | -0.0036167 | -0.0051575 | 0.003653 | 0.072151 | 0.067618 | -0.010732 | 0.019226 | 7.04e-05 | -0.14191 | 1.7807 | -120.2499 | 1.8311 | -119.5633 | -120.3186 | -120.3232 | -1.7944 | 1.8448 | -120.3232 | 1.8356 | -119.8288 | -120.2042 | -119.9799 | -0.041199 | -0.16937 | -0.11902 | 0.64545 | -0.11444 | -0.10986 | -0.073242 | -0.068665 | -0.11444 | -0.10528 | -0.11444 | 0.37994 | 0.22888 | 0.004577 | 0.34332 | 0.11902 | 0.68665 | 122.081 | 0.49439 | 122.1588 | 122.0306 | 122.168 | 121.9894 | 122.0535 | -122.2 | -122.2733 | 122.0398 | 122.0444 | 120.0668 | 118.4143
1504.7812 | 122.2641 | -120.2545 | 1.886 | -0.0060272 | 0.0005619 | 0.057539 | 0.055403 | -0.0032 | -0.0074789 | -0.0036167 | -0.0082093 | 0.001944 | 0.072792 | 0.063559 | -0.010946 | 0.01944 | -0.0005704 | -0.13275 | 1.7395 | -120.3186 | 1.7715 | -119.6228 | -120.3735 | -120.3644 | -1.8127 | 1.8127 | -120.3781 | 1.799 | -119.8288 | -120.2179 | -120.0119 | -0.064087 | -0.14648 | -0.11444 | 0.63171 | -0.10986 | -0.11902 | -0.045776 | -0.054931 | -0.1236 | -0.073242 | -0.086975 | 0.42572 | 0.24262 | 0.036621 | 0.36621 | 0.16022 | 0.6958 | 122.0901 | 0.54932 | 122.1771 | 122.0581 | 122.1909 | 121.994 | 122.0673 | -122.2046 | -122.2641 | 122.0261 | 122.0535 | 120.1218 | 118.4418
1506.4688 | 122.2092 | -120.3186 | 1.8539 | -0.013657 | 0.0022709 | 0.059676 | 0.058394 | 0.0027814 | -0.0059835 | -0.0040439 | -0.011261 | 0.0042938 | 0.073433 | 0.065055 | -0.012441 | 0.018585 | -0.003561 | -0.1831 | 1.7075 | -120.3598 | 1.6937 | -119.7235 | -120.4468 | -120.4514 | -1.9318 | 1.7853 | -120.4285 | 1.712 | -119.9387 | -120.3323 | -120.0943 | -0.041198 | -0.14648 | -0.16022 | 0.59509 | -0.13275 | -0.12817 | -0.091553 | -0.086975 | -0.10986 | -0.068665 | -0.14191 | 0.37994 | 0.2243 | -0.013732 | 0.33417 | 0.096131 | 0.63629 | 122.0535 | 0.48981 | 122.1405 | 122.0673 | 122.2137 | 122.0261 | 122.1039 | -122.2137 | -122.2824 | 122.0123 | 122.0306 | 120.1355 | 118.3868
1508.2188 | 122.3602 | -120.3369 | 1.7624 | -0.013657 | 0.0018435 | 0.059889 | 0.056685 | -0.0032 | -0.0044883 | -0.0021213 | -0.0021057 | -0.00040596 | 0.073433 | 0.054374 | -0.012228 | 0.020294 | -0.0001432 | -0.20599 | 1.6022 | -120.3644 | 1.7532 | -119.6411 | -120.3781 | -120.3735 | -1.8448 | 1.6846 | -120.4285 | 1.799 | -119.8517 | -120.2316 | -120.0302 | -0.027466 | -0.16022 | -0.009155 | 0.6958 | -0.036621 | -0.041199 | -0.009155 | -0.013733 | -0.091553 | -0.07782 | 0.036621 | 0.48523 | 0.3067 | 0.10529 | 0.39825 | 0.19684 | 0.72327 | 122.1176 | 0.57678 | 122.2275 | 121.9666 | 122.113 | 121.9391 | 122.0215 | -122.1268 | -122.1909 | 122.0901 | 122.1359 | 120.1309 | 118.4921
1509.9688 | 122.3465 | -120.3369 | 1.7303 | -0.013657 | 0.0014163 | 0.059676 | 0.056044 | -0.00042301 | -0.0066245 | -0.0034031 | -0.0082093 | 0.001303 | 0.07386 | 0.065055 | -0.013296 | 0.018585 | -0.0016384 | -0.23804 | 1.6067 | -120.3873 | 1.6983 | -119.7006 | -120.4285 | -120.4239 | -1.8677 | 1.6617 | -120.4605 | 1.767 | -119.8975 | -120.2408 | -120.0623 | -0.050354 | -0.1236 | -0.032044 | 0.63629 | -0.086975 | -0.091553 | -0.036621 | -0.041199 | -0.1236 | -0.068665 | 0.036621 | 0.43945 | 0.27466 | 0.09613 | 0.39825 | 0.21973 | 0.68665 | 122.0856 | 0.56305 | 122.2275 | 121.994 | 122.1222 | 121.9437 | 121.9986 | -122.1176 | -122.1909 | 122.0352 | 122.1039 | 120.0989 | 118.4692
1511.7188 | 122.2275 | -120.4147 | 1.7532 | -0.0060272 | 0.0018435 | 0.060316 | 0.057539 | -0.002132 | -0.0070517 | -0.0012669 | -0.0051575 | 0.0015166 | 0.070442 | 0.067618 | -0.012228 | 0.020508 | -0.0020658 | -0.23804 | 1.6251 | -120.4559 | 1.5747 | -119.8608 | -120.5887 | -120.5795 | -2.0279 | 1.6983 | -120.5292 | 1.6067 | -120.0623 | -120.4468 | -120.2271 | -0.041199 | -0.12817 | -0.17853 | 0.55389 | -0.16479 | -0.17395 | -0.1236 | -0.13275 | -0.11444 | -0.054932 | -0.14649 | 0.35248 | 0.18768 | -0.032043 | 0.30212 | 0.082398 | 0.59509 | 122.0306 | 0.46692 | 122.1359 | 122.081 | 122.2275 | 122.0398 | 122.113 | -122.2092 | -122.2824 | 121.9894 | 122.0215 | 120.1767 | 118.3868
1513.4062 | 122.2183 | -120.4834 | 1.7166 | 0.0016023 | -0.0013607 | 0.057967 | 0.056258 | -0.0029864 | -0.0087607 | 0.00022853 | -0.0051575 | 0.0021576 | 0.072151 | 0.070609 | -0.0090235 | 0.018585 | -0.0001432 | -0.15564 | 1.561 | -120.488 | 1.5427 | -119.8425 | -120.5521 | -120.5658 | -1.9455 | 1.6342 | -120.5658 | 1.5518 | -120.0577 | -120.4422 | -120.2591 | -0.004578 | -0.15564 | -0.17395 | 0.64087 | -0.082398 | -0.068665 | -0.07782 | -0.064087 | -0.082398 | -0.082398 | -0.1648 | 0.42572 | 0.2243 | 0.041198 | 0.3067 | 0.1236 | 0.64545 | 122.0306 | 0.50812 | 122.1176 | 122.049 | 122.2 | 122.0444 | 122.1176 | -122.2046 | -122.2824 | 122.0261 | 122.0352 | 120.3278 | 118.5379
1515.1562 | 122.3145 | -120.4422 | 1.6571 | -0.021286 | 0.0018435 | 0.059676 | 0.057967 | 0.0019268 | -0.0061971 | -0.0023349 | -0.0021057 | 0.004721 | 0.071938 | 0.065268 | -0.011801 | 0.017944 | -0.0029202 | -0.27924 | 1.5152 | -120.5338 | 1.5335 | -119.8746 | -120.6024 | -120.5887 | -1.9958 | 1.5884 | -120.5841 | 1.6067 | -120.0439 | -120.3964 | -120.1813 | -0.091552 | -0.14191 | -0.1236 | 0.56763 | -0.14648 | -0.16022 | -0.054932 | -0.068665 | -0.14191 | -0.068664 | -0.050354 | 0.39826 | 0.26093 | 0.045777 | 0.40283 | 0.18768 | 0.65918 | 122.0673 | 0.54016 | 122.1909 | 122.049 | 122.1725 | 121.9574 | 122.0306 | -122.1909 | -122.2412 | 121.9757 | 122.049 | 120.163 | 118.4463
1516.9219 | 122.3053 | -120.5063 | 1.6434 | -0.013657 | -0.0013607 | 0.056898 | 0.053053 | -0.0027728 | -0.0081197 | -0.0016941 | -0.0021057 | 0.00023504 | 0.070656 | 0.059928 | -0.013082 | 0.017731 | -0.0016384 | -0.22888 | 1.4648 | -120.52 | 1.5747 | -119.8196 | -120.5521 | -120.5475 | -1.9592 | 1.5472 | -120.5887 | 1.5976 | -120.0714 | -120.4102 | -120.2042 | -0.013733 | -0.17853 | -0.068665 | 0.68665 | -0.041198 | -0.045776 | -0.027465 | -0.032043 | -0.082397 | -0.096131 | -0.045777 | 0.43488 | 0.30212 | 0.096131 | 0.38452 | 0.17853 | 0.70038 | 122.0947 | 0.51727 | 122.1863 | 121.9849 | 122.1359 | 121.9711 | 122.0535 | -122.1634 | -122.2321 | 122.081 | 122.1039 | 120.2774 | 118.5471
1518.6719 | 122.287 | -120.5063 | 1.6067 | -0.013657 | 0.0003483 | 0.059035 | 0.057112 | -0.0023456 | -0.0057699 | -0.0029759 | -0.0051575 | 2.1442e-05 | 0.071938 | 0.060782 | -0.010946 | 0.019653 | -0.0031338 | -0.12817 | 1.4648 | -120.5841 | 1.5106 | -119.8746 | -120.607 | -120.6024 | -1.9547 | 1.5427 | -120.6162 | 1.561 | -120.0897 | -120.4605 | -120.2591 | -0.077819 | -0.14191 | -0.09613 | 0.63171 | -0.09613 | -0.10071 | -0.018311 | -0.022889 | -0.10986 | -0.064086 | -0.045776 | 0.41657 | 0.24719 | 0.045777 | 0.35706 | 0.15564 | 0.70953 | 122.0947 | 0.52643 | 122.1771 | 122.049 | 122.1588 | 121.9711 | 122.049 | -122.1909 | -122.2229 | 122.0169 | 122.0673 | 120.3781 | 118.5516
1520.3594 | 122.2412 | -120.5795 | 1.6159 | -0.0060272 | -0.0011471 | 0.056685 | 0.057326 | -0.0042682 | -0.0064109 | -0.0016941 | -0.0051575 | 0.0023712 | 0.071083 | 0.061423 | -0.0092371 | 0.019012 | 0.0032748 | -0.14191 | 1.4603 | -120.6253 | 1.4328 | -119.9615 | -120.6711 | -120.6757 | -2.037 | 1.5472 | -120.6757 | 1.4603 | -120.163 | -120.5383 | -120.3232 | -0.045776 | -0.15564 | -0.18311 | 0.61798 | -0.09613 | -0.091553 | -0.050354 | -0.045777 | -0.09613 | -0.068665 | -0.15564 | 0.41656 | 0.25635 | 0.041199 | 0.35248 | 0.13733 | 0.66376 | 122.0581 | 0.51269 | 122.1359 | 122.0856 | 122.2229 | 122.0398 | 122.1268 | -122.2412 | -122.2916 | 122.0123 | 122.0398 | 120.4376 | 118.5425
1522.125 | 122.2092 | -120.5841 | 1.5656 | 0.0016023 | 0.0035525 | 0.059889 | 0.057753 | -0.00085021 | -0.0070517 | -0.0012669 | -0.0051575 | 0.0025848 | 0.073433 | 0.065909 | -0.0096643 | 0.020081 | -0.0005704 | -0.1831 | 1.4236 | -120.6253 | 1.4465 | -119.9707 | -120.6894 | -120.6894 | -2.0645 | 1.5106 | -120.6985 | 1.4603 | -120.2042 | -120.5933 | -120.3552 | -0.041199 | -0.14191 | -0.11902 | 0.6134 | -0.10529 | -0.10529 | -0.064087 | -0.064087 | -0.11444 | -0.054932 | -0.10529 | 0.37994 | 0.22888 | -0.009156 | 0.34332 | 0.10529 | 0.6546 | 122.0718 | 0.49438 | 122.1588 | 122.0489 | 122.2092 | 122.0078 | 122.0947 | -122.1909 | -122.2641 | 122.0306 | 122.0444 | 120.401 | 118.5196
1523.875 | 122.3099 | -120.6024 | 1.5518 | -0.0060272 | -0.0009335 | 0.059676 | 0.054335 | -0.0023456 | -0.0072653 | -0.0036167 | -0.0082093 | -0.00019216 | 0.07151 | 0.059928 | -0.012228 | 0.017303 | -0.0033474 | -0.23346 | 1.3962 | -120.6162 | 1.4603 | -119.9387 | -120.6436 | -120.6573 | -2.092 | 1.474 | -120.6757 | 1.4969 | -120.1355 | -120.5017 | -120.2911 | -0.013733 | -0.15564 | -0.091553 | 0.66376 | -0.054932 | -0.041199 | -0.041199 | -0.027466 | -0.073242 | -0.07782 | -0.054932 | 0.46692 | 0.31128 | 0.10071 | 0.38452 | 0.17395 | 0.67749 | 122.0764 | 0.54016 | 122.1725 | 122.0123 | 122.1497 | 121.9986 | 122.0764 | -122.168 | -122.2275 | 122.0627 | 122.0993 | 120.369 | 118.5104
1525.5625 | 122.3419 | -120.5978 | 1.5152 | -0.0060272 | -0.0032833 | 0.059248 | 0.054549 | 0.00064519 | -0.0059835 | -0.0059665 | -0.0082093 | 0.001944 | 0.070869 | 0.062064 | -0.01116 | 0.019012 | -0.0046292 | -0.20142 | 1.3641 | -120.6207 | 1.4374 | -119.9478 | -120.6528 | -120.6436 | -2.0645 | 1.4374 | -120.7031 | 1.4923 | -120.1263 | -120.488 | -120.2866 | -0.022889 | -0.15106 | -0.07782 | 0.65002 | -0.045777 | -0.054932 | -0.022888 | -0.032043 | -0.10529 | -0.07782 | -0.022888 | 0.4715 | 0.31128 | 0.10986 | 0.41657 | 0.21515 | 0.67291 | 122.0581 | 0.57678 | 122.1954 | 121.9849 | 122.1405 | 121.962 | 122.0352 | -122.1359 | -122.2183 | 122.0352 | 122.0901 | 120.3964 | 118.5333
1527.25 | 122.3373 | -120.5933 | 1.5106 | -0.021286 | 0.0048343 | 0.058607 | 0.057967 | -0.0029864 | -0.0083335 | -0.0042575 | -0.0082093 | 0.003012 | 0.07151 | 0.057151 | -0.013296 | 0.019226 | 0.0002842 | -0.26093 | 1.3779 | -120.6528 | 1.4511 | -119.9478 | -120.6802 | -120.6802 | -2.1057 | 1.442 | -120.6985 | 1.5015 | -120.1355 | -120.5154 | -120.2545 | -0.059509 | -0.13275 | -0.059509 | 0.64545 | -0.086975 | -0.086975 | -0.027466 | -0.027466 | -0.10529 | -0.068664 | -0.009155 | 0.45776 | 0.33874 | 0.07782 | 0.44403 | 0.18311 | 0.70496 | 122.1039 | 0.56305 | 122.2 | 122.0306 | 122.1405 | 121.9711 | 122.0352 | -122.1634 | -122.2092 | 122.0444 | 122.0947 | 120.3323 | 118.4875
1529 | 122.3419 | -120.607 | 1.4969 | -0.0060272 | -0.0020017 | 0.059676 | 0.054762 | -0.00085021 | -0.0076925 | -0.0016941 | -0.0021057 | -0.0012604 | 0.071724 | 0.061423 | -0.011373 | 0.018585 | -0.003561 | -0.091553 | 1.3412 | -120.6482 | 1.5015 | -119.8883 | -120.6116 | -120.6253 | -2.0187 | 1.4191 | -120.694 | 1.4832 | -120.1263 | -120.4834 | -120.3003 | -0.041198 | -0.15564 | 0.004578 | 0.71869 | -0.01831 | -0.004577 | 0.022888 | 0.036621 | -0.086975 | -0.07782 | -0.013733 | 0.48065 | 0.3067 | 0.1236 | 0.39368 | 0.21057 | 0.75989 | 122.1497 | 0.56763 | 122.1771 | 121.9894 | 122.113 | 121.9482 | 122.0261 | -122.1451 | -122.1909 | 122.1085 | 122.0901 | 120.5154 | 118.5883
1530.75 | 122.2549 | -120.6573 | 1.5106 | -0.013657 | -0.0026425 | 0.057967 | 0.053908 | -0.0034136 | -0.0085471 | -0.0016941 | -0.0051575 | 0.0023712 | 0.070656 | 0.059928 | -0.011587 | 0.018585 | -0.000784 | -0.09613 | 1.3229 | -120.6619 | 1.4328 | -119.9615 | -120.6802 | -120.6848 | -2.1194 | 1.4282 | -120.7214 | 1.4008 | -120.2179 | -120.607 | -120.4102 | -0.004577 | -0.18768 | -0.07782 | 0.6958 | -0.027465 | -0.022888 | -0.022888 | -0.018311 | -0.064087 | -0.082397 | -0.10986 | 0.43945 | 0.24719 | 0.050354 | 0.31128 | 0.11444 | 0.70038 | 122.0947 | 0.50354 | 122.1222 | 121.9849 | 122.1497 | 121.9803 | 122.0856 | -122.1725 | -122.2321 | 122.0901 | 122.0581 | 120.5612 | 118.5379
1532.4375 | 122.3465 | -120.6024 | 1.4694 | -0.028916 | 0.0020571 | 0.062025 | 0.056258 | 0.0032086 | -0.0053427 | -0.0046847 | -0.0051575 | 0.003653 | 0.070656 | 0.067405 | -0.013082 | 0.019226 | -0.003561 | -0.22888 | 1.3229 | -120.6665 | 1.4328 | -119.9615 | -120.6757 | -120.694 | -2.1515 | 1.4099 | -120.7397 | 1.5152 | -120.1675 | -120.5566 | -120.3049 | -0.064087 | -0.14648 | -0.036621 | 0.64087 | -0.091553 | -0.073242 | -0.027466 | -0.009155 | -0.13733 | -0.059509 | 0.045777 | 0.43488 | 0.29755 | 0.045776 | 0.43487 | 0.1831 | 0.70496 | 122.0993 | 0.5722 | 122.2549 | 121.9894 | 122.1497 | 121.9254 | 122.0123 | -122.1359 | -122.2092 | 122.0352 | 122.1176 | 120.3735 | 118.4509
1534.2031 | 122.2687 | -120.607 | 1.5152 | -0.021286 | 0.0014163 | 0.059248 | 0.056258 | 0.0014996 | -0.0083335 | -0.0044711 | -0.0021057 | 0.0025848 | 0.072365 | 0.067191 | -0.012228 | 0.01944 | -0.004202 | -0.13733 | 1.3596 | -120.6573 | 1.4191 | -119.9936 | -120.7031 | -120.7123 | -2.1561 | 1.4603 | -120.7397 | 1.4328 | -120.195 | -120.5841 | -120.369 | -0.050354 | -0.15564 | -0.096131 | 0.6134 | -0.10529 | -0.09613 | -0.054931 | -0.045776 | -0.13275 | -0.054932 | -0.082398 | 0.41199 | 0.23804 | 0.022889 | 0.37079 | 0.15564 | 0.66376 | 122.0764 | 0.54474 | 122.1725 | 122.0169 | 122.2 | 121.9666 | 122.0673 | -122.1725 | -122.2549 | 122.0261 | 122.0398 | 120.4697 | 118.4509
1535.8906 | 122.2595 | -120.6757 | 1.4923 | -0.013657 | -0.0009335 | 0.057753 | 0.057967 | -0.002132 | -0.0079061 | -0.0014805 | -0.0051575 | 0.0010894 | 0.069588 | 0.066764 | -0.01116 | 0.01944 | -0.0029202 | -0.16022 | 1.3641 | -120.6985 | 1.3412 | -120.0714 | -120.7672 | -120.7672 | -2.2522 | 1.4374 | -120.7489 | 1.3641 | -120.2637 | -120.6299 | -120.4102 | -0.022888 | -0.12817 | -0.15106 | 0.60425 | -0.091553 | -0.091553 | -0.068665 | -0.068665 | -0.073242 | -0.054932 | -0.12817 | 0.41199 | 0.2655 | 0.045776 | 0.33875 | 0.11902 | 0.62714 | 122.0398 | 0.48523 | 122.113 | 122.0627 | 122.1863 | 122.0398 | 122.113 | -122.1909 | -122.2412 | 122.0169 | 122.0398 | 120.5154 | 118.4235
1537.6406 | 122.2961 | -120.6665 | 1.4465 | -0.0060272 | -0.0015743 | 0.057326 | 0.056258 | -0.0010638 | -0.0061971 | -0.0025485 | -0.0051575 | -0.0012604 | 0.071724 | 0.052665 | -0.010305 | 0.01944 | -0.003561 | -0.23346 | 1.3092 | -120.7031 | 1.3779 | -120.0165 | -120.7489 | -120.7352 | -2.2842 | 1.3733 | -120.7672 | 1.4008 | -120.2179 | -120.6024 | -120.3873 | -0.036621 | -0.13733 | -0.068664 | 0.65002 | -0.068664 | -0.082397 | -0.032043 | -0.045776 | -0.10071 | -0.073242 | -0.045776 | 0.44861 | 0.27924 | 0.064087 | 0.37994 | 0.16479 | 0.68665 | 122.081 | 0.54932 | 122.168 | 122.0123 | 122.1405 | 121.9757 | 122.0398 | -122.1497 | -122.2137 | 122.0444 | 122.0673 | 120.433 | 118.3823
1539.3281 | 122.2229 | -120.7214 | 1.4648 | -0.0060272 | 0.0033389 | 0.059035 | 0.05818 | -0.001491 | -0.0055563 | -0.0016941 | -0.0051575 | 0.0034392 | 0.073006 | 0.061637 | -0.013723 | 0.019653 | -0.0037748 | -0.2655 | 1.3184 | -120.7306 | 1.2772 | -120.1263 | -120.8313 | -120.8405 | -2.3804 | 1.4008 | -120.7947 | 1.3504 | -120.3278 | -120.7031 | -120.4742 | -0.009155 | -0.14648 | -0.18768 | 0.59509 | -0.11902 | -0.10986 | -0.10986 | -0.10071 | -0.073242 | -0.064087 | -0.11444 | 0.39368 | 0.24719 | 0.018311 | 0.32044 | 0.091553 | 0.60425 | 122.0078 | 0.46692 | 122.1451 | 122.049 | 122.1954 | 122.0398 | 122.1222 | -122.1954 | -122.2595 | 121.9986 | 122.0718 | 120.4559 | 118.3411
1541.0938 | 122.3465 | -120.6436 | 1.4465 | -0.0060272 | 0.0033389 | 0.059462 | 0.056471 | 0.0025678 | -0.0053427 | -0.0055393 | -0.0082093 | -0.00083316 | 0.072365 | 0.0642 | -0.01415 | 0.019226 | -0.0020658 | -0.25177 | 1.3412 | -120.6985 | 1.387 | -120.0165 | -120.7535 | -120.7306 | -2.2751 | 1.3687 | -120.7626 | 1.442 | -120.2042 | -120.5841 | -120.3598 | -0.054931 | -0.10529 | -0.059509 | 0.62714 | -0.086975 | -0.10986 | -0.032044 | -0.054932 | -0.11902 | -0.07782 | -0.004577 | 0.43945 | 0.28381 | 0.05951 | 0.40283 | 0.17853 | 0.68207 | 122.0856 | 0.55847 | 122.2046 | 122.0398 | 122.1313 | 121.9849 | 122.0123 | -122.1451 | -122.2092 | 122.0306 | 122.0856 | 120.3918 | 118.3685
1542.8438 | 122.2733 | -120.7169 | 1.4557 | 0.0016023 | -7.9104e-05 | 0.05583 | 0.056258 | 0.00021799 | -0.0081197 | -0.0027621 | -0.0051575 | 0.0021576 | 0.070869 | 0.0689 | -0.011801 | 0.020935 | -0.0016384 | -0.14648 | 1.3138 | -120.7306 | 1.3321 | -120.0668 | -120.7626 | -120.7901 | -2.3117 | 1.3962 | -120.7809 | 1.3779 | -120.2591 | -120.6436 | -120.4285 | -0.013733 | -0.14191 | -0.1236 | 0.65002 | -0.073242 | -0.045776 | -0.059509 | -0.032043 | -0.064087 | -0.059509 | -0.077819 | 0.45776 | 0.28839 | 0.073242 | 0.35248 | 0.13733 | 0.66376 | 122.0627 | 0.52185 | 122.1588 | 122.0444 | 122.1771 | 122.0306 | 122.113 | -122.1863 | -122.2366 | 122.049 | 122.0947 | 120.5704 | 118.4052
1544.5312 | 122.2549 | -120.7123 | 1.4465 | -0.013657 | 0.0018435 | 0.059676 | 0.056044 | -0.00020941 | -0.0079061 | -0.0021213 | -0.0021057 | 0.001944 | 0.073433 | 0.062918 | -0.011373 | 0.020508 | -0.003561 | -0.15564 | 1.2955 | -120.7581 | 1.3412 | -120.0623 | -120.813 | -120.813 | -2.3346 | 1.3596 | -120.813 | 1.3504 | -120.3094 | -120.6848 | -120.4651 | -0.045777 | -0.15106 | -0.10529 | 0.65002 | -0.10071 | -0.10071 | -0.054931 | -0.054931 | -0.10071 | -0.086975 | -0.09613 | 0.40283 | 0.24719 | 0.027466 | 0.3479 | 0.12817 | 0.6958 | 122.0993 | 0.50354 | 122.1634 | 122.0535 | 122.1725 | 122.0078 | 122.0718 | -122.2046 | -122.2595 | 122.0535 | 122.0627 | 120.5566 | 118.3777
1546.2188 | 122.3557 | -120.6528 | 1.4282 | -0.013657 | -0.0015743 | 0.058821 | 0.054976 | -0.002132 | -0.0072653 | -0.0040439 | -0.0082093 | -0.00061956 | 0.070869 | 0.057151 | -0.0098779 | 0.018585 | -0.0003568 | -0.11444 | 1.2543 | -120.726 | 1.4374 | -119.9249 | -120.6711 | -120.6757 | -2.2522 | 1.3367 | -120.7901 | 1.4236 | -120.1675 | -120.5292 | -120.3461 | -0.073242 | -0.17395 | 0.009155 | 0.72784 | -0.022888 | -0.018311 | 0.050354 | 0.054931 | -0.13733 | -0.091553 | -0.004578 | 0.48523 | 0.3067 | 0.1236 | 0.44403 | 0.26093 | 0.80109 | 122.1634 | 0.62256 | 122.2137 | 121.9803 | 122.1268 | 121.907 | 121.9894 | -122.1542 | -122.2183 | 122.0901 | 122.0764 | 120.5383 | 118.4006
1547.9688 | 122.2366 | -120.7489 | 1.4374 | -0.013657 | -0.0013607 | 0.055189 | 0.054762 | 0.001286 | -0.0094015 | -0.0029759 | -0.0051575 | 0.0038666 | 0.072792 | 0.0642 | -0.01351 | 0.019012 | -0.0031338 | -0.16479 | 1.2909 | -120.7809 | 1.2589 | -120.1355 | -120.8313 | -120.8542 | -2.4307 | 1.3641 | -120.8359 | 1.2772 | -120.3506 | -120.7031 | -120.5063 | -0.032044 | -0.14648 | -0.17853 | 0.6134 | -0.10529 | -0.082398 | -0.073242 | -0.050354 | -0.086975 | -0.073242 | -0.16022 | 0.39825 | 0.24261 | 0.045776 | 0.32959 | 0.13275 | 0.64545 | 122.0398 | 0.48523 | 122.113 | 122.0718 | 122.2 | 122.0398 | 122.113 | -122.2183 | -122.2733 | 122.0078 | 122.0261 | 120.5841 | 118.3182
1549.6562 | 122.2778 | -120.7123 | 1.4236 | -0.0060272 | 0.0005619 | 0.057753 | 0.056044 | 0.00021799 | -0.0081197 | -0.0038303 | -0.0051575 | 0.0021576 | 0.071083 | 0.063773 | -0.012869 | 0.020721 | -0.0014248 | -0.14648 | 1.2909 | -120.7993 | 1.2589 | -120.1447 | -120.8313 | -120.8542 | -2.449 | 1.355 | -120.8313 | 1.3092 | -120.3186 | -120.6985 | -120.4651 | -0.086975 | -0.13275 | -0.1648 | 0.56763 | -0.14191 | -0.11902 | -0.054932 | -0.032044 | -0.11902 | -0.068665 | -0.11444 | 0.39368 | 0.24719 | 0.013733 | 0.36621 | 0.13275 | 0.6546 | 122.0581 | 0.5127 | 122.1405 | 122.0901 | 122.1863 | 122.0032 | 122.0673 | -122.2229 | -122.2549 | 121.9711 | 122.0215 | 120.5658 | 118.2632
1551.3438 | 122.2961 | -120.7306 | 1.3687 | -0.013657 | -0.0007199 | 0.057753 | 0.054121 | -0.0019184 | -0.0061971 | -0.0025485 | -0.0082093 | 0.0017304 | 0.070015 | 0.056296 | -0.0085961 | 0.018799 | -0.0014248 | -0.22888 | 1.2405 | -120.7626 | 1.2863 | -120.1035 | -120.8313 | -120.8084 | -2.4948 | 1.2817 | -120.8359 | 1.3092 | -120.3094 | -120.6665 | -120.4514 | -0.032043 | -0.12817 | -0.082397 | 0.62714 | -0.07782 | -0.10071 | -0.045777 | -0.068665 | -0.10528 | -0.086975 | -0.059509 | 0.42114 | 0.27924 | 0.064087 | 0.38452 | 0.16937 | 0.65918 | 122.049 | 0.52643 | 122.1451 | 122.0032 | 122.1176 | 121.9711 | 122.0123 | -122.1313 | -122.2046 | 122.0169 | 122.0398 | 120.5017 | 118.2358
1553.0938 | 122.2824 | -120.7626 | 1.3687 | -0.0060272 | -0.0005063 | 0.057326 | 0.054121 | -0.00063661 | -0.0076925 | -0.0038303 | -0.0021057 | -0.00040596 | 0.071297 | 0.061209 | -0.011373 | 0.020508 | -0.004202 | -0.23346 | 1.1948 | -120.7993 | 1.2909 | -120.1035 | -120.8313 | -120.8038 | -2.5269 | 1.2955 | -120.8496 | 1.3275 | -120.3232 | -120.6894 | -120.4742 | -0.036621 | -0.17395 | -0.077819 | 0.65918 | -0.041199 | -0.068665 | -0.004578 | -0.032044 | -0.086975 | -0.073242 | -0.041198 | 0.43945 | 0.28839 | 0.073242 | 0.37537 | 0.16022 | 0.6958 | 122.0901 | 0.52643 | 122.1771 | 121.994 | 122.1451 | 121.9574 | 122.0581 | -122.168 | -122.2183 | 122.0535 | 122.0901 | 120.5292 | 118.2358
1554.8594 | 122.3602 | -120.7718 | 1.3504 | -0.0060272 | -0.0020017 | 0.057753 | 0.05583 | -0.0051226 | -0.0081197 | -0.0014805 | -0.0082093 | -0.00083316 | 0.073647 | 0.057364 | -0.012655 | 0.018372 | -0.0054838 | -0.17395 | 1.1948 | -120.8038 | 1.3184 | -120.076 | -120.7764 | -120.7809 | -2.4307 | 1.2863 | -120.8542 | 1.355 | -120.2682 | -120.6253 | -120.4742 | -0.032043 | -0.15564 | -0.032044 | 0.6958 | -0.009155 | -0.004577 | 0.022888 | 0.027466 | -0.082397 | -0.064087 | 0.004577 | 0.50354 | 0.29755 | 0.14648 | 0.37994 | 0.22888 | 0.72784 | 122.1222 | 0.58594 | 122.2092 | 121.9986 | 122.1405 | 121.9666 | 122.0581 | -122.1542 | -122.2046 | 122.0901 | 122.1268 | 120.5978 | 118.3411
1556.6094 | 122.3511 | -120.7626 | 1.3184 | -0.021286 | -7.9104e-05 | 0.059889 | 0.056898 | -0.0036274 | -0.0061971 | -0.0012669 | -0.0051575 | 0.001944 | 0.072578 | 0.065909 | -0.012869 | 0.020508 | -0.0046292 | -0.21057 | 1.1719 | -120.7855 | 1.3229 | -120.0989 | -120.8221 | -120.8221 | -2.4948 | 1.2451 | -120.8725 | 1.3504 | -120.282 | -120.6757 | -120.488 | -0.022888 | -0.14648 | 0.004578 | 0.66376 | -0.05951 | -0.05951 | -0.036622 | -0.036622 | -0.10986 | -0.073242 | 0.032044 | 0.48065 | 0.27466 | 0.086975 | 0.38452 | 0.19684 | 0.68664 | 122.1085 | 0.59052 | 122.2229 | 121.9574 | 122.1176 | 121.9345 | 122.0078 | -122.1039 | -122.1909 | 122.0856 | 122.113 | 120.5521 | 118.2678
1558.2969 | 122.2229 | -120.8496 | 1.355 | -0.013657 | -0.0013607 | 0.058607 | 0.054762 | -0.0057636 | -0.0061971 | -0.00041227 | -0.0082093 | 0.0025848 | 0.073433 | 0.069114 | -0.012869 | 0.018158 | 0.0002842 | -0.17853 | 1.1902 | -120.8817 | 1.1673 | -120.2271 | -120.9274 | -120.9366 | -2.6001 | 1.2726 | -120.9137 | 1.1948 | -120.433 | -120.7993 | -120.6436 | -0.032044 | -0.16479 | -0.18768 | 0.62256 | -0.086975 | -0.07782 | -0.054931 | -0.045776 | -0.064087 | -0.082397 | -0.16022 | 0.41657 | 0.20599 | 0.050354 | 0.27008 | 0.11444 | 0.6546 | 122.049 | 0.48065 | 122.1085 | 122.0718 | 122.1863 | 122.0398 | 122.1222 | -122.2366 | -122.2687 | 122.0169 | 122.0444 | 120.6711 | 118.2495
1560.0469 | 122.2733 | -120.726 | 1.442 | -0.021286 | 0.0007755 | 0.05583 | 0.059248 | 0.004704 | -0.0068381 | -0.0038303 | -0.0082093 | 0.0023712 | 0.07386 | 0.062918 | -0.011801 | 0.020508 | -0.0039884 | -0.14191 | 1.3046 | -120.7535 | 1.3641 | -120.0439 | -120.7718 | -120.7855 | -2.5543 | 1.3733 | -120.7901 | 1.3824 | -120.2682 | -120.6528 | -120.4697 | -0.027466 | -0.13733 | -0.07782 | 0.68207 | -0.059509 | -0.045777 | -0.032043 | -0.018311 | -0.064087 | -0.068665 | -0.05951 | 0.45776 | 0.25635 | 0.073242 | 0.32043 | 0.13733 | 0.70953 | 122.1176 | 0.52185 | 122.1725 | 122.0581 | 122.1634 | 122.0306 | 122.0993 | -122.1954 | -122.2321 | 122.0901 | 122.1085 | 120.5841 | 118.1717
1561.8125 | 122.2229 | -120.6848 | 1.506 | -0.013657 | 0.0035525 | 0.06053 | 0.057967 | -0.0029864 | -0.0053427 | -0.0016941 | -0.0051575 | 0.0032256 | 0.071724 | 0.073172 | -0.011373 | 0.01944 | -0.0014248 | -0.25177 | 1.3779 | -120.7031 | 1.3138 | -120.1218 | -120.8221 | -120.8084 | -2.7328 | 1.442 | -120.7809 | 1.3733 | -120.3094 | -120.6894 | -120.4605 | -0.018311 | -0.12817 | -0.19226 | 0.56305 | -0.1236 | -0.13733 | -0.10529 | -0.11902 | -0.096131 | -0.064086 | -0.13275 | 0.37537 | 0.2243 | -0.004578 | 0.32044 | 0.091553 | 0.58136 | 122.0169 | 0.4715 | 122.1542 | 122.081 | 122.2229 | 122.0627 | 122.1268 | -122.2092 | -122.287 | 121.9986 | 122.0581 | 120.433 | 117.952
1563.5 | 122.2275 | -120.6573 | 1.5015 | -0.013657 | -0.0011471 | 0.057753 | 0.056471 | -0.0032 | -0.0091879 | -0.0019077 | -0.0051575 | -0.00040596 | 0.073647 | 0.063346 | -0.012441 | 0.018799 | -0.0033474 | -0.1236 | 1.3641 | -120.6985 | 1.3962 | -120.0165 | -120.7077 | -120.726 | -2.6459 | 1.442 | -120.7443 | 1.3916 | -120.2316 | -120.6116 | -120.4514 | -0.041198 | -0.13733 | -0.10529 | 0.64087 | -0.068664 | -0.050354 | -0.027466 | -0.009156 | -0.086975 | -0.059509 | -0.10986 | 0.42572 | 0.20599 | 0.045777 | 0.29297 | 0.13275 | 0.68207 | 122.0947 | 0.5127 | 122.1359 | 122.0627 | 122.1863 | 122.0215 | 122.0993 | -122.2 | -122.2458 | 122.0535 | 122.049 | 120.5338 | 118.0115
1565.1719 | 122.3053 | -120.8267 | 1.3046 | -0.0060272 | 0.0033389 | 0.057753 | 0.05348 | -0.0029864 | -0.0066245 | -0.0021213 | -0.0021057 | -0.00061956 | 0.071297 | 0.060141 | -0.012655 | 0.019653 | -0.0016384 | -0.24719 | 1.1536 | -120.8359 | 1.2268 | -120.163 | -120.8908 | -120.8771 | -2.742 | 1.2405 | -120.9183 | 1.2589 | -120.3873 | -120.7489 | -120.5612 | -0.009155 | -0.15106 | -0.077819 | 0.66376 | -0.050354 | -0.064087 | -0.041199 | -0.054932 | -0.091553 | -0.064086 | -0.045776 | 0.43945 | 0.2655 | 0.07782 | 0.35706 | 0.16937 | 0.67291 | 122.0627 | 0.53101 | 122.1771 | 121.9894 | 122.1588 | 121.9803 | 122.0673 | -122.1405 | -122.2229 | 122.0535 | 122.0856 | 120.5795 | 118.0847
1566.9219 | 122.2229 | -120.6528 | 1.5152 | -0.013657 | -0.0013607 | 0.055617 | 0.057112 | -0.00042301 | -0.0081197 | -0.0042575 | -0.0082093 | 0.0015166 | 0.071938 | 0.060782 | -0.010092 | 0.018585 | -0.003561 | -0.1831 | 1.387 | -120.7031 | 1.3458 | -120.0668 | -120.7535 | -120.7626 | -2.7557 | 1.4603 | -120.7489 | 1.387 | -120.2454 | -120.639 | -120.4468 | -0.050354 | -0.12817 | -0.16937 | 0.58594 | -0.10986 | -0.10071 | -0.059509 | -0.050354 | -0.09613 | -0.054932 | -0.12817 | 0.40741 | 0.20599 | 0.013733 | 0.30212 | 0.10986 | 0.63629 | 122.049 | 0.50354 | 122.1359 | 122.0901 | 122.2092 | 122.0398 | 122.113 | -122.2183 | -122.2641 | 121.9986 | 122.0398 | 120.4697 | 117.897
1568.6875 | 122.3053 | -120.5887 | 1.4694 | -0.0060272 | 0.0014163 | 0.059248 | 0.055403 | -0.0027728 | -0.0068381 | -0.0036167 | -0.0021057 | 0.00044864 | 0.072792 | 0.058219 | -0.010305 | 0.019867 | -0.002493 | -0.2243 | 1.3367 | -120.6299 | 1.4877 | -119.9066 | -120.6528 | -120.6436 | -2.71 | 1.3916 | -120.6848 | 1.4969 | -120.1813 | -120.5246 | -120.3278 | -0.041199 | -0.13275 | 0.018311 | 0.68207 | -0.054932 | -0.064087 | -0.013733 | -0.022888 | -0.09613 | -0.077819 | 0.027466 | 0.40741 | 0.26093 | 0.064087 | 0.35706 | 0.16022 | 0.72327 | 122.1176 | 0.50354 | 122.1817 | 121.9666 | 122.0764 | 121.9254 | 121.9803 | -122.0993 | -122.1542 | 122.0764 | 122.0856 | 120.3644 | 117.8787
1570.4531 | 122.3053 | -120.6207 | 1.4786 | -0.0060272 | -0.0013607 | 0.057112 | 0.054121 | -0.0010638 | -0.0091879 | -0.0042575 | -0.011261 | 0.00066224 | 0.071938 | 0.058005 | -0.012014 | 0.020294 | -0.0009976 | -0.25177 | 1.355 | -120.6665 | 1.4099 | -119.9844 | -120.6985 | -120.6848 | -2.8244 | 1.4053 | -120.7031 | 1.4374 | -120.1813 | -120.5566 | -120.2957 | -0.045776 | -0.1236 | -0.068665 | 0.63629 | -0.064086 | -0.077819 | -0.01831 | -0.032043 | -0.082397 | -0.073243 | -0.041199 | 0.43945 | 0.32501 | 0.064087 | 0.40741 | 0.14648 | 0.68207 | 122.0764 | 0.52185 | 122.1405 | 122.0215 | 122.1085 | 121.9757 | 122.0261 | -122.1451 | -122.1817 | 122.0306 | 122.0581 | 120.369 | 117.7963
1572.1406 | 122.2046 | -120.694 | 1.4877 | -0.013657 | 0.0016299 | 0.06053 | 0.057539 | 0.0010724 | -0.0079061 | -0.0016941 | -0.0021057 | 0.0038666 | 0.06852 | 0.069541 | -0.013082 | 0.020935 | -0.0005704 | -0.25635 | 1.3458 | -120.7443 | 1.2909 | -120.108 | -120.8267 | -120.8359 | -2.948 | 1.4191 | -120.7718 | 1.3733 | -120.3049 | -120.6848 | -120.3827 | -0.050354 | -0.14191 | -0.19684 | 0.58594 | -0.14191 | -0.13275 | -0.091552 | -0.082397 | -0.07782 | -0.068665 | -0.11444 | 0.3891 | 0.31128 | 0.009156 | 0.3891 | 0.086976 | 0.63629 | 122.0352 | 0.46692 | 122.1451 | 122.0901 | 122.1909 | 122.0398 | 122.113 | -122.2321 | -122.2595 | 121.9849 | 122.0673 | 120.4376 | 117.746
1573.8281 | 122.2641 | -120.726 | 1.4374 | -0.0060272 | 0.0007755 | 0.058607 | 0.057539 | -0.001491 | -0.0074789 | -0.0034031 | -0.0021057 | 0.003653 | 0.072578 | 0.058219 | -0.012228 | 0.022644 | -0.0033474 | -0.15106 | 1.3 | -120.7718 | 1.2955 | -120.0989 | -120.8084 | -120.8038 | -2.8748 | 1.3596 | -120.813 | 1.3458 | -120.282 | -120.6848 | -120.4239 | -0.045777 | -0.13733 | -0.14191 | 0.62714 | -0.07782 | -0.082398 | -0.032043 | -0.036621 | -0.086975 | -0.07782 | -0.091553 | 0.44403 | 0.30212 | 0.041199 | 0.3891 | 0.12817 | 0.67291 | 122.0673 | 0.53101 | 122.1588 | 122.0718 | 122.1725 | 122.0261 | 122.0856 | -122.2092 | -122.2504 | 122.0215 | 122.0718 | 120.575 | 117.8513
1575.5938 | 122.2321 | -120.7123 | 1.474 | -0.0060272 | -0.0002927 | 0.058394 | 0.055403 | -0.00085021 | -0.010683 | -0.0040439 | -0.0021057 | 0.003653 | 0.071083 | 0.058432 | -0.010732 | 0.018799 | -0.0020658 | -0.13733 | 1.2817 | -120.7397 | 1.3367 | -120.0577 | -120.7626 | -120.7626 | -2.8931 | 1.3779 | -120.8176 | 1.3275 | -120.2957 | -120.6711 | -120.4971 | -0.027466 | -0.19226 | -0.13733 | 0.6546 | -0.050354 | -0.050354 | -0.022888 | -0.022888 | -0.10529 | -0.09613 | -0.14648 | 0.41657 | 0.21515 | 0.041198 | 0.32044 | 0.14648 | 0.68207 | 122.0764 | 0.52185 | 122.1451 | 122.0215 | 122.1954 | 121.994 | 122.0901 | -122.2137 | -122.2916 | 122.049 | 122.0398 | 120.575 | 117.8192
1577.2812 | 122.3465 | -120.8038 | 1.268 | -0.013657 | -0.0030697 | 0.057539 | 0.054121 | -0.0087542 | -0.0074789 | -0.0023349 | -0.0051575 | -0.00019216 | 0.072578 | 0.0642 | -0.011587 | 0.018158 | -0.0014248 | -0.14648 | 1.1169 | -120.8267 | 1.2909 | -120.0577 | -120.7947 | -120.8038 | -2.8336 | 1.1993 | -120.8908 | 1.3 | -120.2911 | -120.6573 | -120.5154 | -0.022888 | -0.15106 | 0.022889 | 0.74616 | 0 | 0.009155 | 0.022888 | 0.032043 | -0.086975 | -0.068664 | 0.032044 | 0.51269 | 0.28839 | 0.14648 | 0.37537 | 0.23346 | 0.76904 | 122.1176 | 0.59967 | 122.1909 | 121.9437 | 122.0901 | 121.9208 | 122.0032 | -122.0947 | -122.1588 | 122.0947 | 122.1039 | 120.6573 | 117.9703
1579.0312 | 122.1954 | -120.7214 | 1.2405 | -0.0060272 | 0.0020571 | 0.061171 | 0.057326 | 0.00043159 | -0.0068381 | -0.0012669 | -0.0082093 | 0.00044864 | 0.071297 | 0.064414 | -0.011801 | 0.020508 | -0.0063382 | -0.2655 | 1.1307 | -120.7626 | 1.1627 | -120.1126 | -120.8405 | -120.8405 | -3.0029 | 1.1765 | -120.8221 | 1.2405 | -120.2637 | -120.6436 | -120.4514 | -0.041198 | -0.10986 | -0.07782 | 0.60883 | -0.11902 | -0.11902 | -0.07782 | -0.07782 | -0.10071 | -0.064087 | 0 | 0.45776 | 0.27008 | 0.07782 | 0.37079 | 0.17853 | 0.65002 | 121.9254 | 0.55847 | 122.0627 | 121.8933 | 121.9986 | 121.8521 | 121.8979 | -122.0032 | -122.0627 | 121.8842 | 121.962 | 120.4559 | 117.7185
1580.7344 | 122.1588 | -120.9549 | 1.1627 | -0.021286 | 0.0033389 | 0.059248 | 0.057967 | 0.00064519 | -0.0055563 | -0.0016941 | -0.0051575 | 0.0015166 | 0.073433 | 0.063987 | -0.012441 | 0.021149 | -0.0022794 | -0.27466 | 1.0391 | -120.9961 | 0.99335 | -120.4102 | -121.1243 | -121.106 | -3.1586 | 1.1353 | -121.0419 | 1.0437 | -120.5841 | -120.9549 | -120.7397 | -0.041199 | -0.1236 | -0.16937 | 0.54474 | -0.15106 | -0.16937 | -0.10986 | -0.12817 | -0.086975 | -0.027466 | -0.11902 | 0.37079 | 0.21515 | 0 | 0.30212 | 0.086975 | 0.58594 | 121.9894 | 0.45776 | 122.0856 | 122.0352 | 122.1771 | 121.994 | 122.0901 | -122.1588 | -122.2046 | 121.9482 | 121.9986 | 120.6802 | 117.7963
1582.4219 | 122.2733 | -120.5658 | 1.5244 | -0.0060272 | -0.0020017 | 0.057967 | 0.053267 | -0.001491 | -0.0096151 | -0.0034031 | -0.0082093 | -0.00040596 | 0.072792 | 0.064414 | -0.012228 | 0.019012 | 0.0028476 | -0.24719 | 1.3779 | -120.6162 | 1.4374 | -119.9295 | -120.639 | -120.639 | -3.1082 | 1.4557 | -120.6757 | 1.4832 | -120.1355 | -120.4971 | -120.314 | -0.050354 | -0.14648 | -0.086975 | 0.63629 | -0.073242 | -0.073242 | -0.022888 | -0.022888 | -0.10986 | -0.068665 | -0.041199 | 0.4303 | 0.25177 | 0.068665 | 0.36163 | 0.17853 | 0.68665 | 122.0535 | 0.54016 | 122.1588 | 121.994 | 122.1313 | 121.9437 | 122.0215 | -122.1405 | -122.2 | 122.0032 | 122.049 | 120.3186 | 117.4576
1584.1719 | 122.1909 | -120.6894 | 1.4832 | -0.013657 | -0.0017881 | 0.057967 | 0.05583 | -0.0023456 | -0.0081197 | -0.0014805 | -0.0021057 | 0.001303 | 0.071938 | 0.06185 | -0.012655 | 0.018799 | -0.0031338 | -0.17395 | 1.3184 | -120.7169 | 1.3275 | -120.0485 | -120.7672 | -120.7718 | -3.1219 | 1.4145 | -120.7397 | 1.3184 | -120.2637 | -120.6345 | -120.4468 | -0.027466 | -0.1648 | -0.15564 | 0.64087 | -0.082398 | -0.07782 | -0.054932 | -0.050354 | -0.050354 | -0.068664 | -0.1648 | 0.42572 | 0.24262 | 0.054932 | 0.29297 | 0.10529 | 0.66833 | 122.0444 | 0.47607 | 122.0581 | 122.0352 | 122.1542 | 122.0078 | 122.1039 | -122.2 | -122.2229 | 122.0169 | 122.0078 | 120.5154 | 117.5674
1585.9219 | 122.2321 | -120.282 | 1.8677 | -0.013657 | 0.0001345 | 0.057539 | 0.055403 | 0.0032086 | -0.0064109 | -0.0051121 | -0.0051575 | 0.0025848 | 0.073006 | 0.061209 | -0.012441 | 0.018799 | -0.0022794 | -0.16479 | 1.7212 | -120.314 | 1.7166 | -119.6594 | -120.3506 | -120.3781 | -3.1128 | 1.7853 | -120.3552 | 1.7532 | -119.8425 | -120.2316 | -120.0531 | -0.032044 | -0.14648 | -0.15106 | 0.62256 | -0.096131 | -0.068665 | -0.064087 | -0.036621 | -0.073243 | -0.082398 | -0.11444 | 0.43945 | 0.22888 | 0.050354 | 0.30212 | 0.1236 | 0.6546 | 122.0306 | 0.5127 | 122.1085 | 122.0352 | 122.1405 | 122.0032 | 122.0673 | -122.1817 | -122.2229 | 121.9986 | 122.0352 | 120.1172 | 117.1692
1587.6719 | 122.2092 | -120.2637 | 1.8768 | -0.013657 | -0.0009335 | 0.059035 | 0.054121 | -0.0010638 | -0.0091879 | -0.0025485 | -0.0082093 | 0.00066224 | 0.071938 | 0.059928 | -0.010092 | 0.017731 | -0.0012112 | -0.11902 | 1.7029 | -120.2774 | 1.7899 | -119.5816 | -120.3003 | -120.3049 | -3.1403 | 1.8127 | -120.3461 | 1.7624 | -119.8288 | -120.2179 | -120.0806 | -0.013733 | -0.17395 | -0.086975 | 0.68207 | -0.041199 | -0.036621 | -0.027466 | -0.022888 | -0.082397 | -0.064087 | -0.11444 | 0.43488 | 0.18311 | 0.045776 | 0.2655 | 0.12817 | 0.6958 | 122.0673 | 0.51727 | 122.1085 | 121.9803 | 122.1588 | 121.9666 | 122.0764 | -122.1542 | -122.2229 | 122.0535 | 122.0261 | 120.1447 | 117.1234
1589.4219 | 122.3236 | -120.4697 | 1.593 | -0.028916 | 0.0026981 | 0.058607 | 0.056898 | -0.00085021 | -0.0036337 | -0.0019077 | -0.0051575 | 0.001944 | 0.071297 | 0.051596 | -0.012441 | 0.022858 | -0.0033474 | -0.21057 | 1.4648 | -120.4742 | 1.6067 | -119.7693 | -120.5017 | -120.4926 | -3.1815 | 1.5244 | -120.5521 | 1.6479 | -119.9661 | -120.3461 | -120.1675 | -0.004577 | -0.12817 | 0.013732 | 0.70038 | -0.022888 | -0.032043 | -0.018311 | -0.027466 | -0.082397 | -0.068665 | 0.054931 | 0.50354 | 0.30212 | 0.1236 | 0.38452 | 0.20599 | 0.70496 | 122.081 | 0.58594 | 122.2 | 121.9391 | 122.0764 | 121.9345 | 121.994 | -122.0673 | -122.1451 | 122.0764 | 122.1176 | 120.2591 | 117.2882
1591.1094 | 122.2778 | -120.4926 | 1.5701 | -0.0060272 | 0.0033389 | 0.059889 | 0.05818 | -0.0042682 | -0.0053427 | -0.0042575 | -0.0051575 | 0.001944 | 0.072365 | 0.060996 | -0.01415 | 0.020935 | -0.0014248 | -0.30212 | 1.4648 | -120.5521 | 1.4648 | -119.8975 | -120.6436 | -120.6253 | -3.3142 | 1.5152 | -120.6207 | 1.5472 | -120.076 | -120.4514 | -120.2316 | -0.059509 | -0.10529 | -0.10529 | 0.59509 | -0.13275 | -0.15106 | -0.073242 | -0.091553 | -0.12817 | -0.054931 | -0.022888 | 0.41656 | 0.26093 | 0.041199 | 0.3891 | 0.16937 | 0.6546 | 122.0169 | 0.54474 | 122.168 | 122.0169 | 122.1359 | 121.9574 | 122.0078 | -122.1222 | -122.1909 | 121.9574 | 122.0398 | 120.1904 | 117.1783
1592.8594 | 122.3557 | -120.6436 | 1.4053 | -0.013657 | -0.0026425 | 0.057539 | 0.054121 | 0.00043159 | -0.0070517 | -0.0021213 | -0.0021057 | 0.00044864 | 0.071297 | 0.056723 | -0.012441 | 0.018372 | 0.0007114 | -0.15106 | 1.2589 | -120.7214 | 1.4053 | -119.9341 | -120.6619 | -120.6802 | -3.2043 | 1.3275 | -120.7489 | 1.4465 | -120.1355 | -120.5109 | -120.3781 | -0.07782 | -0.14648 | 0 | 0.70953 | -0.036621 | -0.01831 | 0.041199 | 0.05951 | -0.10529 | -0.077819 | 0.041199 | 0.50812 | 0.2655 | 0.13275 | 0.37079 | 0.23804 | 0.78735 | 122.1268 | 0.6134 | 122.1954 | 121.9803 | 122.0764 | 121.9025 | 121.9711 | -122.1268 | -122.1542 | 122.0489 | 122.0901 | 120.4926 | 117.4393
1594.5625 | 122.2641 | -120.6665 | 1.4465 | -0.0060272 | -7.9104e-05 | 0.05583 | 0.056258 | -0.0023456 | -0.0083335 | -0.0029759 | -0.0051575 | 0.00044864 | 0.072792 | 0.063773 | -0.012228 | 0.020508 | -0.002493 | -0.14191 | 1.3046 | -120.7306 | 1.3504 | -120.0119 | -120.7397 | -120.7489 | -3.3279 | 1.3962 | -120.7581 | 1.3962 | -120.2271 | -120.5933 | -120.4422 | -0.064087 | -0.14191 | -0.09613 | 0.6546 | -0.082397 | -0.073242 | -0.01831 | -0.009155 | -0.091553 | -0.050354 | -0.050354 | 0.43945 | 0.2243 | 0.073242 | 0.31586 | 0.16479 | 0.71869 | 122.081 | 0.53101 | 122.1542 | 122.0352 | 122.1542 | 121.9711 | 122.0627 | -122.1771 | -122.2046 | 122.0169 | 122.0627 | 120.5246 | 117.3386
1596.25 | 122.2366 | -120.6573 | 1.4694 | -0.0060272 | 0.0014163 | 0.057753 | 0.057967 | -0.00063661 | -0.0087607 | -0.0016941 | -0.0051575 | 0.0032256 | 0.07151 | 0.060782 | -0.010305 | 0.021149 | 0.0002842 | -0.16937 | 1.3367 | -120.6848 | 1.3779 | -119.9753 | -120.726 | -120.7169 | -3.392 | 1.4145 | -120.7397 | 1.4008 | -120.2179 | -120.6116 | -120.4376 | -0.027465 | -0.13275 | -0.091552 | 0.68207 | -0.059509 | -0.068664 | -0.032044 | -0.041199 | -0.082397 | -0.054931 | -0.068664 | 0.43945 | 0.21973 | 0.045777 | 0.30212 | 0.12817 | 0.70953 | 122.0627 | 0.52185 | 122.1405 | 122.0215 | 122.1542 | 121.994 | 122.0718 | -122.1542 | -122.2092 | 122.0352 | 122.0581 | 120.488 | 117.2653
1598.0156 | 122.3145 | -120.7169 | 1.3504 | -0.0060272 | -0.0028561 | 0.057326 | 0.05348 | -0.002132 | -0.0066245 | -0.0034031 | -0.0082093 | -0.0010468 | 0.071297 | 0.060355 | -0.011373 | 0.019653 | -0.002493 | -0.21057 | 1.2268 | -120.7535 | 1.3138 | -120.0302 | -120.7397 | -120.7535 | -3.4058 | 1.2955 | -120.7993 | 1.3733 | -120.2133 | -120.5658 | -120.4514 | -0.036621 | -0.1236 | -0.036621 | 0.68665 | -0.036621 | -0.022888 | 0 | 0.013733 | -0.082397 | -0.054932 | 0.022888 | 0.50354 | 0.2655 | 0.15106 | 0.3479 | 0.23346 | 0.72327 | 122.0673 | 0.58594 | 122.1725 | 121.9803 | 122.0947 | 121.9437 | 122.0123 | -122.1039 | -122.1497 | 122.0306 | 122.0901 | 120.5063 | 117.3111
1599.7656 | 122.1863 | -120.5612 | 1.5839 | 0.0016023 | 0.0026981 | 0.058607 | 0.055403 | 0.0051312 | -0.0074789 | -0.0029759 | -0.0082093 | 0.0027984 | 0.070656 | 0.061423 | -0.010519 | 0.020508 | -0.000784 | -0.25177 | 1.4282 | -120.5795 | 1.3962 | -120.0119 | -120.7306 | -120.7214 | -3.598 | 1.5244 | -120.6665 | 1.4374 | -120.195 | -120.5795 | -120.3827 | -0.018311 | -0.15564 | -0.18768 | 0.54932 | -0.16022 | -0.16937 | -0.14191 | -0.15106 | -0.10529 | -0.059509 | -0.14648 | 0.36621 | 0.17853 | -0.018311 | 0.28381 | 0.086975 | 0.56763 | 121.9757 | 0.4715 | 122.1039 | 122.0078 | 122.1909 | 121.9894 | 122.0856 | -122.1634 | -122.2504 | 121.9574 | 121.9986 | 120.3094 | 116.9632
1601.4531 | 122.2275 | -120.401 | 1.6937 | -0.013657 | 0.0001345 | 0.05818 | 0.057326 | -0.0040546 | -0.0079061 | -0.0034031 | -0.0051575 | -0.00083316 | 0.070656 | 0.059287 | -0.010732 | 0.01944 | -0.000784 | -0.25635 | 1.5381 | -120.4102 | 1.6113 | -119.7281 | -120.4788 | -120.4605 | -3.5797 | 1.5976 | -120.5017 | 1.6342 | -119.9524 | -120.3278 | -120.1813 | -0.009155 | -0.15564 | -0.082398 | 0.67291 | -0.059509 | -0.07782 | -0.050354 | -0.068665 | -0.10071 | -0.096131 | -0.05951 | 0.44861 | 0.21973 | 0.073242 | 0.32044 | 0.17395 | 0.68207 | 122.0215 | 0.54932 | 122.1359 | 121.9482 | 122.0993 | 121.9391 | 121.9986 | -122.1039 | -122.1954 | 122.0123 | 122.0352 | 120.1447 | 116.8213
1603.1875 | 122.287 | -120.8084 | 1.2909 | -0.013657 | -0.0009335 | 0.057753 | 0.05348 | -0.0023456 | -0.0083335 | -0.0012669 | -0.0051575 | -0.00040596 | 0.069801 | 0.057151 | -0.01116 | 0.018799 | -0.0020658 | -0.24261 | 1.1353 | -120.8359 | 1.2222 | -120.1538 | -120.8633 | -120.8542 | -3.6255 | 1.2314 | -120.8862 | 1.2497 | -120.3506 | -120.7123 | -120.5429 | -0.027465 | -0.15564 | -0.068665 | 0.6546 | -0.045776 | -0.054931 | -0.018311 | -0.027466 | -0.077819 | -0.05951 | -0.041199 | 0.45776 | 0.2655 | 0.096131 | 0.34332 | 0.17395 | 0.68207 | 122.0581 | 0.53558 | 122.1359 | 121.9711 | 122.1176 | 121.9437 | 122.0398 | -122.1268 | -122.1771 | 122.0306 | 122.0581 | 120.5658 | 117.1829
1604.9375 | 122.2366 | -120.8176 | 1.2955 | -0.013657 | 0.0024845 | 0.057753 | 0.059462 | -0.00063661 | -0.0059835 | -0.0038303 | -0.0051575 | 0.0032256 | 0.070229 | 0.062491 | -0.012655 | 0.020081 | -0.0033474 | -0.16479 | 1.1673 | -120.845 | 1.2177 | -120.163 | -120.8908 | -120.9091 | -3.6118 | 1.2405 | -120.9045 | 1.236 | -120.3781 | -120.7809 | -120.5978 | -0.027466 | -0.12817 | -0.07782 | 0.6546 | -0.091553 | -0.073242 | -0.064087 | -0.045776 | -0.086975 | -0.054931 | -0.059509 | 0.43945 | 0.21973 | 0.036621 | 0.3067 | 0.1236 | 0.68207 | 122.0627 | 0.52643 | 122.1405 | 122.0123 | 122.1451 | 121.9849 | 122.0581 | -122.1405 | -122.2 | 122.0352 | 122.0535 | 120.6528 | 117.2058
1606.7031 | 122.1954 | -120.7718 | 1.3504 | -0.0060272 | 0.0009891 | 0.058821 | 0.059462 | 0.00043159 | -0.0074789 | -0.0027621 | -0.0051575 | 0.0025848 | 0.074074 | 0.064627 | -0.011373 | 0.019867 | -0.0003568 | -0.29755 | 1.2314 | -120.7947 | 1.1993 | -120.1813 | -120.9137 | -120.8862 | -3.804 | 1.3 | -120.845 | 1.2497 | -120.3781 | -120.7718 | -120.5658 | -0.022888 | -0.11902 | -0.15106 | 0.59052 | -0.11444 | -0.14191 | -0.091552 | -0.11902 | -0.073242 | -0.050354 | -0.10071 | 0.39368 | 0.20599 | 0 | 0.27924 | 0.073242 | 0.6134 | 121.994 | 0.46692 | 122.0947 | 122.0261 | 122.1451 | 122.0032 | 122.0718 | -122.1451 | -122.1954 | 121.9711 | 122.0215 | 120.4742 | 116.9678
1608.375 | 122.2092 | -120.7809 | 1.3229 | -0.013657 | -0.0032833 | 0.057967 | 0.05284 | 0.00043159 | -0.0083335 | -0.0014805 | -0.0021057 | 0.0015166 | 0.073006 | 0.057792 | -0.01116 | 0.018585 | 7.04e-05 | -0.1236 | 1.1536 | -120.7764 | 1.2497 | -120.0394 | -120.7489 | -120.7672 | -3.7033 | 1.2543 | -120.8313 | 1.2268 | -120.3003 | -120.6802 | -120.5292 | 0.004578 | -0.16937 | -0.073242 | 0.74158 | 0.013733 | 0.032044 | 0.009155 | 0.027466 | -0.050354 | -0.068665 | -0.09613 | 0.48065 | 0.25177 | 0.10071 | 0.30212 | 0.15106 | 0.737 | 122.0261 | 0.53101 | 122.0581 | 121.9299 | 122.0856 | 121.9345 | 122.0352 | -122.0993 | -122.1542 | 122.0306 | 122.0078 | 120.6573 | 117.0776
1610.125 | 122.1542 | -120.7169 | 1.3824 | -0.0060272 | 0.0029117 | 0.057112 | 0.057753 | 0.0040632 | -0.0061971 | -0.0016941 | 0.0009461 | 0.0023712 | 0.074074 | 0.062491 | -0.010946 | 0.022003 | 0.000925 | -0.19684 | 1.2222 | -120.7626 | 1.2543 | -120.0989 | -120.8221 | -120.8267 | -3.8177 | 1.2955 | -120.8176 | 1.2772 | -120.3232 | -120.7169 | -120.5383 | -0.045776 | -0.16022 | -0.12817 | 0.61798 | -0.10986 | -0.10529 | -0.064087 | -0.05951 | -0.10071 | -0.086975 | -0.10529 | 0.39368 | 0.17853 | 0 | 0.27924 | 0.10071 | 0.66376 | 122.0169 | 0.49438 | 122.0947 | 121.9849 | 122.113 | 121.9391 | 122.0123 | -122.1451 | -122.2 | 121.9711 | 121.994 | 120.52 | 116.8991
1611.8906 | 122.1909 | -120.6848 | 1.3962 | -0.013657 | 0.0035525 | 0.057753 | 0.058821 | 0.0019268 | -0.0072653 | -0.00041227 | -0.0051575 | 0.0042938 | 0.071724 | 0.064841 | -0.01351 | 0.019226 | -0.0033474 | -0.16022 | 1.2726 | -120.7443 | 1.3046 | -120.0302 | -120.7626 | -120.7672 | -3.8086 | 1.3321 | -120.7947 | 1.3321 | -120.2362 | -120.6207 | -120.4514 | -0.05951 | -0.1236 | -0.091553 | 0.6546 | -0.082398 | -0.07782 | -0.022888 | -0.01831 | -0.10986 | -0.064087 | -0.064087 | 0.44861 | 0.23346 | 0.064086 | 0.34332 | 0.17395 | 0.71411 | 122.049 | 0.55847 | 122.1268 | 122.0169 | 122.1268 | 121.9574 | 122.0169 | -122.1405 | -122.1909 | 121.9894 | 122.0169 | 120.5246 | 116.8762
1613.6406 | 122.1771 | -120.5475 | 1.5106 | -0.021286 | 0.0024845 | 0.059035 | 0.051558 | -0.00555 | -0.0081197 | -0.0038303 | -0.0021057 | 0.0017304 | 0.071938 | 0.060355 | -0.010732 | 0.017944 | -0.0033474 | -0.23346 | 1.3412 | -120.5612 | 1.4236 | -119.8471 | -120.5887 | -120.5704 | -3.9047 | 1.4145 | -120.6436 | 1.4557 | -120.0897 | -120.4514 | -120.2911 | -0.013733 | -0.16937 | -0.086975 | 0.70038 | -0.022889 | -0.041199 | -0.009156 | -0.027466 | -0.096131 | -0.09613 | -0.054932 | 0.45776 | 0.25635 | 0.09613 | 0.35248 | 0.19226 | 0.71411 | 121.9849 | 0.55389 | 122.0993 | 121.9025 | 122.0581 | 121.8887 | 121.962 | -122.0718 | -122.1542 | 121.9711 | 122.0032 | 120.314 | 116.6428
1615.3281 | 122.1954 | -120.6345 | 1.4465 | -0.0060272 | 0.0026981 | 0.057326 | 0.05818 | -0.00042301 | -0.0049155 | -0.0036167 | -0.0082093 | 0.0027984 | 0.070656 | 0.059073 | -0.012441 | 0.022217 | 7.04e-05 | -0.16022 | 1.3138 | -120.6619 | 1.3275 | -119.9707 | -120.7077 | -120.7214 | -3.9185 | 1.3687 | -120.7306 | 1.3733 | -120.1904 | -120.575 | -120.4102 | -0.027466 | -0.13275 | -0.11902 | 0.66376 | -0.086976 | -0.073243 | -0.05951 | -0.045777 | -0.096131 | -0.07782 | -0.073242 | 0.44403 | 0.2243 | 0.059509 | 0.32044 | 0.15564 | 0.69122 | 121.9894 | 0.54016 | 122.1039 | 121.9757 | 122.0993 | 121.9482 | 122.0032 | -122.1085 | -122.1771 | 121.962 | 122.0078 | 120.4742 | 116.716
1617.0938 | 122.168 | -120.5978 | 1.4786 | -0.013657 | -0.0026425 | 0.058394 | 0.054121 | 0.0017132 | -0.0083335 | -0.0012669 | -0.0051575 | 0.00023504 | 0.071083 | 0.064627 | -0.010732 | 0.019867 | 0.0002842 | -0.13733 | 1.3229 | -120.6253 | 1.4008 | -119.9066 | -120.6162 | -120.6482 | -3.9597 | 1.3779 | -120.6848 | 1.3779 | -120.1447 | -120.5246 | -120.3827 | -0.027466 | -0.15564 | -0.07782 | 0.69122 | -0.050354 | -0.018311 | -0.022888 | 0.009155 | -0.086975 | -0.10071 | -0.10071 | 0.45319 | 0.21515 | 0.073242 | 0.30212 | 0.16022 | 0.71869 | 122.0261 | 0.54016 | 122.0627 | 121.9482 | 122.0627 | 121.9208 | 121.9757 | -122.1039 | -122.1634 | 121.9986 | 121.9757 | 120.4605 | 116.6382
1618.8438 | 122.1725 | -120.5795 | 1.4923 | -0.0060272 | 0.0005619 | 0.05818 | 0.056258 | 4.192e-06 | -0.0079061 | -0.0012669 | 0.0009461 | 0.0015166 | 0.071938 | 0.061209 | -0.013937 | 0.019226 | 0.0002842 | -0.20142 | 1.3275 | -120.639 | 1.3229 | -119.9936 | -120.6802 | -120.694 | -4.0924 | 1.4145 | -120.6985 | 1.3687 | -120.1584 | -120.5338 | -120.3735 | -0.059509 | -0.1648 | -0.16937 | 0.58594 | -0.11444 | -0.10071 | -0.054932 | -0.041199 | -0.11902 | -0.07782 | -0.1236 | 0.42114 | 0.20599 | 0.045777 | 0.32501 | 0.16479 | 0.64545 | 121.962 | 0.54016 | 122.0673 | 121.9666 | 122.113 | 121.907 | 121.994 | -122.1313 | -122.1909 | 121.9025 | 121.9482 | 120.3781 | 116.4871
1620.5312 | 122.1634 | -120.5704 | 1.5472 | -0.013657 | -0.0015743 | 0.057112 | 0.055403 | -0.00020941 | -0.0074789 | -0.0034031 | -0.0051575 | 0.0017304 | 0.07151 | 0.066764 | -0.011587 | 0.020508 | 0.003702 | -0.19226 | 1.4145 | -120.6116 | 1.3687 | -119.9432 | -120.6528 | -120.6665 | -4.1611 | 1.4877 | -120.6299 | 1.4099 | -120.1447 | -120.5246 | -120.3552 | -0.041198 | -0.13275 | -0.17853 | 0.62714 | -0.09613 | -0.082397 | -0.054932 | -0.041199 | -0.059509 | -0.059509 | -0.13733 | 0.42572 | 0.21515 | 0.045777 | 0.27466 | 0.10529 | 0.66833 | 121.9803 | 0.48523 | 122.0398 | 122.0261 | 122.1176 | 121.9849 | 122.0581 | -122.1588 | -122.1771 | 121.9391 | 121.9803 | 120.3781 | 116.4093
1622.2188 | 122.1909 | -120.5521 | 1.4969 | -0.013657 | -0.0009335 | 0.057326 | 0.054121 | 0.001286 | -0.0066245 | -0.0019077 | -0.0051575 | 0.0015166 | 0.070656 | 0.058219 | -0.012869 | 0.020935 | -0.0039884 | -0.24261 | 1.355 | -120.6024 | 1.4465 | -119.8837 | -120.6162 | -120.607 | -4.1931 | 1.4053 | -120.6436 | 1.474 | -120.0943 | -120.4559 | -120.3094 | -0.050354 | -0.14191 | -0.050354 | 0.66833 | -0.054932 | -0.064087 | -0.004578 | -0.013733 | -0.091553 | -0.091553 | -0.022888 | 0.45776 | 0.24262 | 0.09613 | 0.33417 | 0.18768 | 0.71869 | 122.049 | 0.54932 | 122.1176 | 121.9574 | 122.0489 | 121.907 | 121.9574 | -122.0993 | -122.1405 | 121.9986 | 122.0261 | 120.3094 | 116.3589
1623.9688 | 122.1268 | -120.5063 | 1.5793 | -0.013657 | 0.0026981 | 0.059889 | 0.056258 | 0.0019268 | -0.0068381 | -0.00083947 | -0.0051575 | 0.00044864 | 0.071083 | 0.061209 | -0.012014 | 0.019226 | 7.04e-05 | -0.28381 | 1.4465 | -120.5154 | 1.4099 | -119.9341 | -120.6573 | -120.6299 | -4.3213 | 1.5518 | -120.5933 | 1.4603 | -120.1172 | -120.5154 | -120.3232 | -0.009155 | -0.13275 | -0.16937 | 0.5722 | -0.1236 | -0.15106 | -0.11444 | -0.14191 | -0.086975 | -0.027466 | -0.11902 | 0.3891 | 0.18311 | -0.009155 | 0.27008 | 0.07782 | 0.58136 | 121.9254 | 0.47607 | 122.0535 | 121.962 | 122.1451 | 121.9528 | 122.0581 | -122.0947 | -122.1725 | 121.9162 | 121.9666 | 120.2225 | 116.185
1625.7188 | 122.2046 | -120.3461 | 1.712 | 0.0016023 | -0.0026425 | 0.059462 | 0.054121 | -0.0051226 | -0.0079061 | -0.0036167 | -0.0051575 | 0.00087584 | 0.074074 | 0.059073 | -0.010732 | 0.017517 | -0.0037748 | -0.13275 | 1.5518 | -120.3827 | 1.68 | -119.6274 | -120.3598 | -120.3644 | -4.1931 | 1.6251 | -120.433 | 1.6846 | -119.8791 | -120.2362 | -120.0943 | -0.036621 | -0.16022 | -0.032043 | 0.71869 | -0.018311 | -0.013733 | 0.01831 | 0.022888 | -0.086975 | -0.086975 | -0.027466 | 0.46692 | 0.25177 | 0.10986 | 0.33874 | 0.19684 | 0.75531 | 122.0627 | 0.55389 | 122.1176 | 121.9345 | 122.0581 | 121.8979 | 121.9711 | -122.0947 | -122.1451 | 122.0261 | 122.0306 | 120.2133 | 116.153
1627.4062 | 122.3007 | -120.3278 | 1.7075 | -0.013657 | -7.9104e-05 | 0.058607 | 0.053694 | -0.0012774 | -0.0083335 | -0.0048985 | -0.0082093 | 0.00023504 | 0.068733 | 0.05416 | -0.013937 | 0.020081 | -0.000784 | -0.15106 | 1.5656 | -120.3369 | 1.7258 | -119.5724 | -120.2957 | -120.3186 | -4.2114 | 1.6434 | -120.4147 | 1.7395 | -119.8059 | -120.1584 | -120.0531 | -0.009155 | -0.14191 | 0.018311 | 0.75531 | 0.009155 | 0.032044 | 0.01831 | 0.041199 | -0.086975 | -0.064086 | 0.032044 | 0.52185 | 0.27466 | 0.16937 | 0.36163 | 0.25635 | 0.76446 | 122.0627 | 0.60883 | 122.1542 | 121.9025 | 122.0581 | 121.8933 | 121.9711 | -122.0444 | -122.1222 | 122.0535 | 122.0673 | 120.1767 | 116.1163
1629.1562 | 122.0947 | -120.4788 | 1.6067 | -0.013657 | 0.0009891 | 0.056898 | 0.054549 | 0.0040632 | -0.0081197 | -0.0048985 | -0.0021057 | 0.001303 | 0.072151 | 0.058005 | -0.011587 | 0.020508 | -0.0014248 | -0.15106 | 1.4511 | -120.5246 | 1.474 | -119.8242 | -120.5429 | -120.5521 | -4.3625 | 1.5381 | -120.5429 | 1.4603 | -120.0623 | -120.433 | -120.2911 | -0.045776 | -0.15564 | -0.13275 | 0.6546 | -0.073242 | -0.064087 | -0.027466 | -0.018311 | -0.064087 | -0.068664 | -0.14648 | 0.41656 | 0.18768 | 0.045777 | 0.25177 | 0.10986 | 0.70038 | 121.9986 | 0.48065 | 122.0032 | 121.9757 | 122.081 | 121.9299 | 122.0169 | -122.1313 | -122.1497 | 121.9528 | 121.9391 | 120.3278 | 116.1163
1630.8594 | 122.1039 | -120.4651 | 1.5701 | -0.0060272 | -0.0007199 | 0.056258 | 0.055403 | -0.0017048 | -0.0072653 | -0.0025485 | -0.0021057 | 0.0051482 | 0.071938 | 0.055014 | -0.011801 | 0.016235 | -0.0016384 | -0.16022 | 1.4008 | -120.4651 | 1.4099 | -119.8013 | -120.5063 | -120.5109 | -4.4403 | 1.4877 | -120.5292 | 1.4236 | -120.0302 | -120.3964 | -120.2499 | 0 | -0.16937 | -0.16022 | 0.66376 | -0.045776 | -0.041199 | -0.045776 | -0.041199 | -0.064087 | -0.082397 | -0.14648 | 0.43488 | 0.21515 | 0.068665 | 0.27924 | 0.13275 | 0.66376 | 121.875 | 0.49896 | 121.9528 | 121.8658 | 122.0169 | 121.8658 | 121.9528 | -122.0352 | -122.0993 | 121.875 | 121.8887 | 120.3049 | 116.0248
1632.5469 | 122.168 | -120.4742 | 1.6479 | -0.013657 | -7.9104e-05 | 0.057753 | 0.05583 | -0.0029864 | -0.0081197 | -0.0027621 | -0.0051575 | 0.0021576 | 0.072792 | 0.061637 | -0.012869 | 0.019867 | -0.0014248 | -0.17853 | 1.5152 | -120.4926 | 1.4832 | -119.8471 | -120.5429 | -120.5566 | -4.4952 | 1.5656 | -120.5383 | 1.5244 | -120.0073 | -120.3918 | -120.2225 | -0.018311 | -0.13275 | -0.1648 | 0.62714 | -0.082398 | -0.068665 | -0.064087 | -0.050354 | -0.064087 | -0.082397 | -0.1236 | 0.46692 | 0.25177 | 0.082397 | 0.31586 | 0.14648 | 0.64545 | 121.9757 | 0.53101 | 122.0627 | 122.0078 | 122.1039 | 121.9894 | 122.0398 | -122.1405 | -122.1863 | 121.9574 | 121.9986 | 120.2957 | 115.979
1634.2344 | 122.1039 | -120.4971 | 1.5518 | -0.013657 | 0.0018435 | 0.059889 | 0.058607 | 0.0044904 | -0.0066245 | -0.0034031 | -0.0051575 | 0.0017304 | 0.071938 | 0.062064 | -0.011801 | 0.019867 | 0.0034884 | -0.28839 | 1.4236 | -120.5383 | 1.3916 | -119.9341 | -120.6528 | -120.6528 | -4.6509 | 1.5244 | -120.6024 | 1.442 | -120.1172 | -120.52 | -120.3094 | -0.041199 | -0.12817 | -0.16022 | 0.56305 | -0.15564 | -0.15564 | -0.11444 | -0.11444 | -0.10529 | -0.027466 | -0.10986 | 0.37994 | 0.18768 | -0.022889 | 0.29297 | 0.082397 | 0.60425 | 121.9299 | 0.48523 | 122.0444 | 121.962 | 122.1268 | 121.9208 | 122.0215 | -122.0901 | -122.1542 | 121.8887 | 121.9391 | 120.2087 | 115.8463
1635.9844 | 122.1863 | -120.4559 | 1.4923 | -0.021286 | 0.0039799 | 0.059462 | 0.05583 | 0.0038494 | -0.0076925 | -0.0055393 | -0.0082093 | 0.0025848 | 0.070229 | 0.054587 | -0.011373 | 0.019653 | -0.0016384 | -0.30212 | 1.3824 | -120.488 | 1.3824 | -119.8654 | -120.5841 | -120.5704 | -4.6555 | 1.4557 | -120.5475 | 1.4832 | -119.989 | -120.3918 | -120.1904 | -0.032043 | -0.10986 | -0.10986 | 0.59052 | -0.11444 | -0.12817 | -0.082398 | -0.09613 | -0.091552 | -0.036622 | -0.009156 | 0.46692 | 0.2655 | 0.064087 | 0.35705 | 0.15564 | 0.62256 | 121.8704 | 0.55847 | 122.0306 | 121.8704 | 122.0032 | 121.8384 | 121.9116 | -121.9803 | -122.0398 | 121.8384 | 121.9391 | 120.1538 | 115.8005
1637.7344 | 120.6665 | -119.0506 | 1.5839 | -0.021286 | -0.0024289 | 0.058394 | 0.053694 | -0.0017048 | -0.0085471 | -0.0036167 | -0.0082093 | 0.0027984 | 0.070869 | 0.060355 | -0.012441 | 0.017731 | -0.0014248 | -0.15564 | 1.4053 | -119.1788 | 1.4374 | -118.4006 | -119.2154 | -119.1513 | -4.6326 | 1.5152 | -119.2657 | 1.4465 | -118.5745 | -119.0918 | -118.8721 | -0.12817 | -0.17853 | -0.14648 | 0.65002 | -0.10071 | -0.1648 | 0.027466 | -0.036621 | -0.21515 | -0.068664 | -0.13733 | 0.47607 | 0.17853 | -0.041199 | 0.39368 | 0.17395 | 0.7782 | 120.6161 | 0.69122 | 120.7123 | 120.5841 | 120.7809 | 120.4559 | 120.5658 | -120.7626 | -120.8496 | 120.488 | 120.4971 | 118.895 | 114.418
1639.4219 | 121.9391 | -111.8866 | 10.0204 | -0.0060272 | -0.0020017 | 0.055189 | 0.053267 | 0.0010724 | -0.0064109 | -0.0025485 | -0.0021057 | 0.001303 | 0.071938 | 0.063346 | -0.011373 | 0.019653 | -0.0022794 | -0.091553 | 9.8602 | -111.9095 | 9.9884 | -111.2274 | -111.9186 | -111.9095 | -4.1931 | 9.9289 | -111.9278 | 9.938 | -111.4563 | -111.8088 | -111.676 | -0.022888 | -0.16022 | -0.032044 | 0.65918 | -0.022888 | -0.032043 | 0 | -0.009155 | -0.041198 | -0.091553 | -0.082398 | 0.4303 | 0.21057 | 0.07782 | 0.25177 | 0.11902 | 0.68207 | 121.8979 | 0.4715 | 121.8658 | 121.7697 | 121.8567 | 121.7468 | 121.8155 | -121.9299 | -121.9482 | 121.875 | 121.8246 | 111.795 | 107.6935
1641.1719 | 121.9437 | -111.2686 | 10.6247 | -0.0060272 | 0.0016299 | 0.058394 | 0.057753 | 0.00043159 | -0.0061971 | -0.0038303 | 0.0009461 | 0.0023712 | 0.072151 | 0.059714 | -0.01351 | 0.019226 | 0.0011386 | -0.17853 | 10.4599 | -111.2915 | 10.5652 | -110.6873 | -111.3831 | -111.3602 | -4.2572 | 10.5423 | -111.3098 | 10.5606 | -110.8978 | -111.2778 | -111.0901 | -0.022888 | -0.16479 | -0.059509 | 0.58136 | -0.091552 | -0.11444 | -0.068664 | -0.091553 | -0.041198 | -0.082398 | -0.064087 | 0.37079 | 0.17853 | -0.009155 | 0.21973 | 0.032043 | 0.60425 | 121.8567 | 0.41199 | 121.8704 | 121.7514 | 121.8521 | 121.7285 | 121.8109 | -121.9162 | -121.9345 | 121.8338 | 121.8292 | 111.0901 | 107.0114
1642.8594 | 122.0581 | -108.934 | 12.8586 | -0.013657 | -0.0011471 | 0.056471 | 0.055403 | -0.002132 | -0.0091879 | -0.0012669 | -0.0051575 | -0.00019216 | 0.071083 | 0.059714 | -0.012228 | 0.017517 | 0.0002842 | -0.10986 | 12.6892 | -108.9981 | 12.9776 | -108.2703 | -108.9661 | -108.9523 | -4.0421 | 12.7625 | -109.0164 | 12.9593 | -108.4671 | -108.783 | -108.6868 | -0.064087 | -0.16937 | 0.11902 | 0.66376 | -0.018311 | -0.032043 | 0.045776 | 0.032044 | -0.082397 | -0.096131 | 0.10071 | 0.46692 | 0.24719 | 0.15106 | 0.32959 | 0.23346 | 0.72784 | 121.9757 | 0.54932 | 121.9757 | 121.6873 | 121.7789 | 121.6232 | 121.6965 | -121.8567 | -121.875 | 121.9116 | 121.8933 | 108.8242 | 104.892
1644.625 | 121.8658 | -115.535 | 6.2714 | -0.013657 | 0.0029117 | 0.05818 | 0.057753 | -0.0032 | -0.0047019 | -0.0066073 | -0.0021057 | 0.0023712 | 0.071297 | 0.063987 | -0.010732 | 0.018372 | -0.0037748 | -0.28839 | 6.134 | -115.5762 | 6.1295 | -115.0177 | -115.7227 | -115.6998 | -4.7653 | 6.1844 | -115.6219 | 6.1386 | -115.2145 | -115.5716 | -115.3885 | -0.041199 | -0.13733 | -0.14191 | 0.51727 | -0.1648 | -0.18768 | -0.1236 | -0.14648 | -0.086975 | -0.086975 | -0.13275 | 0.32043 | 0.14648 | -0.036621 | 0.23346 | 0.050354 | 0.55847 | 121.7056 | 0.40741 | 121.7606 | 121.7102 | 121.8063 | 121.669 | 121.7194 | -121.8475 | -121.8933 | 121.6644 | 121.6736 | 115.2466 | 110.7697
1646.3281 | 121.8384 | -117.2058 | 4.4678 | -0.0060272 | 0.0041935 | 0.05818 | 0.057967 | 0.0010724 | -0.0059835 | -0.0046847 | -0.0051575 | 0.0017304 | 0.072151 | 0.065909 | -0.011587 | 0.021362 | 0.0019932 | -0.21973 | 4.335 | -117.2791 | 4.4266 | -116.5375 | -117.2699 | -117.3431 | -4.7562 | 4.4128 | -117.3248 | 4.3808 | -116.803 | -117.2195 | -117.041 | -0.073242 | -0.13275 | -0.041198 | 0.66833 | -0.13733 | -0.064086 | -0.064087 | 0.009156 | -0.11902 | -0.054931 | -0.086975 | 0.40283 | 0.16479 | -0.013732 | 0.28381 | 0.10529 | 0.74158 | 121.7056 | 0.52185 | 121.7056 | 121.6141 | 121.7377 | 121.5408 | 121.6187 | -121.7468 | -121.7926 | 121.6324 | 121.5866 | 116.9861 | 112.4496
1648.0781 | 121.701 | -116.1804 | 5.452 | -0.013657 | -0.0007199 | 0.054762 | 0.054762 | -0.0017048 | -0.0074789 | -0.0048985 | -0.0082093 | 0.0023712 | 0.072792 | 0.067618 | -0.015432 | 0.021149 | -0.0018522 | -0.23346 | 5.3192 | -116.2354 | 5.3009 | -115.6403 | -116.3086 | -116.2903 | -4.8431 | 5.3833 | -116.2903 | 5.3375 | -115.8051 | -116.1667 | -115.9882 | -0.054932 | -0.13275 | -0.15106 | 0.54016 | -0.10986 | -0.12817 | -0.054931 | -0.073242 | -0.10986 | -0.068664 | -0.11444 | 0.37537 | 0.19226 | 0.013733 | 0.30212 | 0.1236 | 0.59509 | 121.5363 | 0.48523 | 121.6278 | 121.5546 | 121.6736 | 121.4996 | 121.5637 | -121.6873 | -121.7422 | 121.4813 | 121.5179 | 115.947 | 111.3373
1649.7656 | 121.701 | -115.773 | 5.69 | -0.0060272 | -0.0017881 | 0.056685 | 0.05284 | -0.0042682 | -0.0083335 | -0.0034031 | -0.0082093 | -0.00061956 | 0.069374 | 0.055869 | -0.010305 | 0.01709 | -0.0022794 | -0.17395 | 5.4749 | -115.8188 | 5.6808 | -115.0909 | -115.7547 | -115.8325 | -4.7195 | 5.5801 | -115.8554 | 5.658 | -115.2969 | -115.6265 | -115.4892 | -0.045777 | -0.21515 | -0.009155 | 0.68207 | -0.05951 | 0.01831 | -0.013733 | 0.064087 | -0.082398 | -0.10986 | -0.032043 | 0.47607 | 0.28381 | 0.14648 | 0.36621 | 0.22888 | 0.72785 | 121.4996 | 0.55847 | 121.5134 | 121.2936 | 121.4355 | 121.2479 | 121.3531 | -121.5088 | -121.5454 | 121.4539 | 121.431 | 115.5991 | 111.0535
1651.4688 | 121.6232 | -117.2974 | 4.248 | -0.0060272 | -0.0005063 | 0.056898 | 0.054976 | -0.0032 | -0.0083335 | -0.0019077 | -0.0051575 | 0.001944 | 0.071297 | 0.059928 | -0.011373 | 0.020508 | -0.0001432 | -0.20142 | 4.1245 | -117.3386 | 4.1016 | -116.6977 | -117.3843 | -117.4026 | -4.985 | 4.1794 | -117.3706 | 4.1153 | -116.9037 | -117.247 | -117.0685 | -0.041199 | -0.1236 | -0.14648 | 0.59967 | -0.10529 | -0.086975 | -0.064087 | -0.045776 | -0.073242 | -0.068665 | -0.13275 | 0.39368 | 0.22888 | 0.050354 | 0.30212 | 0.1236 | 0.64087 | 121.4401 | 0.46692 | 121.4859 | 121.463 | 121.55 | 121.4218 | 121.4767 | -121.5866 | -121.6187 | 121.3989 | 121.4127 | 117.0959 | 112.3123
1653.2188 | 121.4584 | -114.4775 | 6.7154 | -0.0060272 | -0.0041379 | 0.057326 | 0.053053 | 0.00085879 | -0.0057699 | -0.0048985 | -0.0051575 | 2.1442e-05 | 0.072792 | 0.061209 | -0.012869 | 0.017944 | -0.002493 | -0.1236 | 6.5643 | -114.5187 | 6.7612 | -113.768 | -114.4775 | -114.4867 | -4.7516 | 6.6284 | -114.5782 | 6.752 | -113.9877 | -114.3402 | -114.1891 | -0.041199 | -0.15106 | 0.045776 | 0.70953 | -0.009155 | 0 | 0.032044 | 0.041199 | -0.10071 | -0.086975 | 0.036621 | 0.48981 | 0.28839 | 0.13733 | 0.3891 | 0.23804 | 0.75073 | 121.2799 | 0.59052 | 121.3303 | 121.0831 | 121.2067 | 121.0419 | 121.106 | -121.2341 | -121.2936 | 121.2387 | 121.2296 | 114.3539 | 109.726
1654.9688 | 121.5683 | -117.6956 | 3.6163 | -0.021286 | -0.0011471 | 0.056044 | 0.052412 | -0.01025 | -0.0089743 | -0.0031895 | -0.011261 | -0.00083316 | 0.070656 | 0.069541 | -0.013937 | 0.020081 | -0.0039884 | -0.10986 | 3.6072 | -117.5949 | 3.7765 | -116.8488 | -117.5491 | -117.5583 | -4.9805 | 3.6942 | -117.6361 | 3.6118 | -117.2104 | -117.6315 | -117.4347 | 0.10071 | -0.009155 | 0.16022 | 0.84686 | 0.13733 | 0.14648 | 0.036621 | 0.045777 | 0.05951 | 0.07782 | -0.004578 | 0.48523 | 0.26093 | 0.064087 | 0.20142 | 0.004577 | 0.74616 | 121.3715 | 0.42572 | 121.2479 | 121.2021 | 121.3303 | 121.3028 | 121.3898 | -121.2112 | -121.2524 | 121.4722 | 121.3074 | 117.5858 | 112.7151
1656.7344 | 121.3303 | -116.3361 | 4.9759 | -0.013657 | 0.0031253 | 0.058821 | 0.056685 | 0.00043159 | -0.0074789 | -0.0036167 | -0.0021057 | 0.003012 | 0.072792 | 0.063132 | -0.011801 | 0.020294 | 0.0024204 | -0.27008 | 4.8065 | -116.3818 | 4.8065 | -115.8188 | -116.4688 | -116.4413 | -5.1819 | 4.8981 | -116.4597 | 4.8157 | -115.9195 | -116.3361 | -116.185 | -0.045776 | -0.16937 | -0.16937 | 0.51727 | -0.10528 | -0.13275 | -0.059509 | -0.086975 | -0.1236 | -0.07782 | -0.16022 | 0.41657 | 0.15106 | 0 | 0.27466 | 0.1236 | 0.56305 | 121.1884 | 0.54016 | 121.2753 | 121.1884 | 121.3577 | 121.1426 | 121.2341 | -121.3577 | -121.4355 | 121.1426 | 121.1517 | 116.066 | 111.1542
1658.4844 | 121.2387 | -114.4867 | 6.5643 | -0.0060272 | -0.0011471 | 0.056258 | 0.05348 | 0.0023542 | -0.0070517 | -0.0057529 | -0.0051575 | 0.0015166 | 0.072151 | 0.062064 | -0.012869 | 0.017517 | -0.0018522 | -0.26093 | 6.3904 | -114.4867 | 6.4865 | -113.8184 | -114.5096 | -114.505 | -5.1086 | 6.4728 | -114.5599 | 6.5643 | -114.061 | -114.3448 | -114.1754 | 0 | -0.17395 | -0.07782 | 0.66833 | -0.018311 | -0.022889 | -0.018311 | -0.022889 | -0.073243 | -0.091553 | 0 | 0.42572 | 0.31128 | 0.14191 | 0.38452 | 0.21515 | 0.66833 | 120.9732 | 0.49896 | 121.1243 | 120.8771 | 121.0327 | 120.8771 | 120.9595 | -121.051 | -121.1243 | 120.9732 | 121.051 | 114.2258 | 109.3781
1660.1719 | 121.0327 | -113.6856 | 7.251 | -0.0060272 | 0.0009891 | 0.057112 | 0.057539 | -0.0046954 | -0.0076925 | -0.0016941 | -0.0051575 | 0.0023712 | 0.070015 | 0.061209 | -0.012441 | 0.021362 | -0.010183 | -0.15106 | 7.1228 | -113.6856 | 7.196 | -113.0447 | -113.7543 | -113.7268 | -5.0308 | 7.1869 | -113.6856 | 7.2556 | -113.2004 | -113.6124 | -113.5025 | 0 | -0.12817 | -0.054932 | 0.64087 | -0.041199 | -0.068664 | -0.041199 | -0.068664 | 0 | -0.064087 | 0.004577 | 0.48523 | 0.18311 | 0.073242 | 0.18311 | 0.073242 | 0.64087 | 120.8817 | 0.48523 | 120.9412 | 120.8084 | 120.8725 | 120.8084 | 120.8725 | -120.9366 | -120.9366 | 120.8817 | 120.9412 | 113.5345 | 108.6548
1661.9219 | 121.1334 | -115.5075 | 5.4245 | -0.013657 | -0.0017881 | 0.056898 | 0.054121 | 0.0014996 | -0.0091879 | -0.0042575 | -0.0051575 | 0.001303 | 0.070442 | 0.059501 | -0.01351 | 0.017303 | -0.0065518 | -0.12817 | 5.2826 | -115.535 | 5.4382 | -114.8254 | -115.5258 | -115.535 | -5.1544 | 5.3375 | -115.5853 | 5.4428 | -115.0406 | -115.3427 | -115.21 | -0.027466 | -0.14191 | 0.013732 | 0.68207 | -0.027466 | -0.018311 | 0 | 0.009155 | -0.07782 | -0.086976 | 0.01831 | 0.46692 | 0.29755 | 0.16479 | 0.37537 | 0.24262 | 0.70953 | 120.9732 | 0.54474 | 121.0281 | 120.8176 | 120.9229 | 120.7901 | 120.845 | -120.9595 | -121.0098 | 120.9457 | 120.9503 | 115.3793 | 110.3531
1663.6094 | 121.2891 | -118.8995 | 2.3483 | -0.013657 | 0.0031253 | 0.059035 | 0.056258 | 0.00064519 | -0.0057699 | -0.0034031 | -0.0082093 | 0.003012 | 0.071938 | 0.063773 | -0.010305 | 0.01944 | -0.0020658 | -0.33417 | 2.1973 | -118.9224 | 2.1606 | -118.396 | -119.0369 | -119.0872 | -5.7312 | 2.2842 | -119.0002 | 2.211 | -118.5242 | -118.8904 | -118.6844 | -0.022888 | -0.15106 | -0.18768 | 0.50354 | -0.18768 | -0.13733 | -0.16479 | -0.11444 | -0.10071 | -0.064087 | -0.13733 | 0.37537 | 0.21515 | 0.009155 | 0.31586 | 0.10986 | 0.52643 | 121.0831 | 0.47607 | 121.2112 | 121.1197 | 121.2845 | 121.0968 | 121.1838 | -121.2708 | -121.3486 | 121.0602 | 121.1105 | 118.5654 | 113.1683
1665.2969 | 121.2067 | -117.4393 | 3.7125 | -0.021286 | -7.9104e-05 | 0.059676 | 0.057539 | 0.00064519 | -0.0091879 | 0.00086953 | -0.0082093 | 0.00044864 | 0.072792 | 0.065055 | -0.012228 | 0.020721 | -0.0029202 | -0.27466 | 3.5385 | -117.5308 | 3.6072 | -116.8213 | -117.5446 | -117.5583 | -5.5527 | 3.6163 | -117.5308 | 3.5706 | -117.0731 | -117.4164 | -117.2195 | -0.091553 | -0.17395 | -0.10528 | 0.61798 | -0.11902 | -0.10529 | -0.027466 | -0.013733 | -0.091553 | -0.09613 | -0.14191 | 0.36621 | 0.21973 | 0.022888 | 0.31128 | 0.11444 | 0.70953 | 121.138 | 0.45776 | 121.1014 | 121.0693 | 121.1472 | 120.9778 | 121.0556 | -121.2433 | -121.2433 | 121.0464 | 121.0098 | 117.1646 | 111.8866
1667.0469 | 121.1929 | -116.7709 | 4.1748 | -0.0060272 | -0.0013607 | 0.055403 | 0.054549 | -0.0019184 | -0.0085471 | -0.0051121 | -0.011261 | -0.00019216 | 0.071083 | 0.05651 | -0.011373 | 0.018585 | -0.0029202 | -0.21973 | 4.1016 | -116.7435 | 4.2343 | -116.0797 | -116.7252 | -116.803 | -5.4703 | 4.1245 | -116.8167 | 4.2252 | -116.2537 | -116.629 | -116.5421 | 0.027466 | -0.073243 | 0.059509 | 0.69122 | -0.032044 | 0.045776 | -0.05951 | 0.01831 | -0.045776 | -0.050354 | 0.050354 | 0.51727 | 0.22888 | 0.14191 | 0.27466 | 0.18768 | 0.66376 | 120.9778 | 0.56305 | 121.0419 | 120.845 | 120.9412 | 120.8725 | 120.8954 | -120.9183 | -120.9915 | 121.0052 | 120.9961 | 116.5512 | 111.3007
1668.7969 | 121.4447 | -119.7784 | 1.5106 | -0.013657 | 0.0033389 | 0.058821 | 0.056471 | 0.0049176 | -0.0072653 | -0.0034031 | -0.0051575 | 0.001944 | 0.071724 | 0.064627 | -0.013937 | 0.021362 | -0.0005704 | -0.32501 | 1.4191 | -119.8425 | 1.3962 | -119.1971 | -119.9066 | -119.9066 | -5.8594 | 1.4694 | -119.838 | 1.4786 | -119.3756 | -119.751 | -119.5404 | -0.064087 | -0.091553 | -0.11444 | 0.58136 | -0.12817 | -0.12817 | -0.064087 | -0.064087 | -0.05951 | -0.041199 | -0.032043 | 0.40283 | 0.23804 | 0.027465 | 0.29755 | 0.086975 | 0.64545 | 121.2387 | 0.46234 | 121.3165 | 121.2616 | 121.3074 | 121.1975 | 121.2479 | -121.3531 | -121.3486 | 121.1746 | 121.257 | 119.4534 | 113.9191
1670.5469 | 121.4127 | -119.1147 | 2.1561 | 0.0016023 | 0.0001345 | 0.056685 | 0.056471 | 4.192e-06 | -0.011111 | -0.0029759 | -0.0021057 | 0.0032256 | 0.072792 | 0.068686 | -0.012655 | 0.020294 | -0.0014248 | -0.20142 | 2.0096 | -119.1834 | 2.0462 | -118.4738 | -119.1879 | -119.2154 | -5.7953 | 2.0828 | -119.2062 | 2.0966 | -118.6752 | -119.0414 | -118.8812 | -0.068665 | -0.14648 | -0.10986 | 0.64087 | -0.10071 | -0.073242 | -0.032043 | -0.004577 | -0.091553 | -0.073242 | -0.059509 | 0.43945 | 0.23346 | 0.073242 | 0.32501 | 0.16479 | 0.70953 | 121.2296 | 0.53101 | 121.3028 | 121.1929 | 121.2891 | 121.1243 | 121.1975 | -121.3394 | -121.3623 | 121.1609 | 121.2112 | 118.9133 | 113.3194
1672.2344 | 121.2616 | -119.4214 | 1.8402 | -0.013657 | -0.0020017 | 0.054549 | 0.05348 | 4.192e-06 | -0.0083335 | -0.0023349 | -0.0051575 | 0.0017304 | 0.073006 | 0.058646 | -0.010092 | 0.019867 | -0.0016384 | -0.27466 | 1.7029 | -119.4626 | 1.6663 | -118.8309 | -119.5175 | -119.5221 | -5.9509 | 1.7761 | -119.5129 | 1.7212 | -119.046 | -119.4305 | -119.2337 | -0.041198 | -0.13733 | -0.17395 | 0.59051 | -0.10071 | -0.09613 | -0.05951 | -0.054932 | -0.091552 | -0.064087 | -0.11902 | 0.37537 | 0.18768 | -0.009155 | 0.27923 | 0.082397 | 0.63171 | 121.1288 | 0.46692 | 121.2341 | 121.1655 | 121.2891 | 121.1243 | 121.1975 | -121.3028 | -121.3531 | 121.0876 | 121.1426 | 119.1467 | 113.4705
1673.9219 | 121.2936 | -118.0756 | 3.0441 | -0.013657 | 0.0001345 | 0.055403 | 0.052199 | 0.00085879 | -0.0068381 | -0.0034031 | -0.0051575 | -0.00083316 | 0.068306 | 0.05886 | -0.010946 | 0.019867 | -0.0033474 | -0.13275 | 2.8748 | -118.1351 | 3.035 | -117.3752 | -118.0847 | -118.0939 | -5.7404 | 2.948 | -118.1305 | 3.067 | -117.5354 | -117.9337 | -117.7872 | -0.059509 | -0.16937 | -0.009155 | 0.70038 | -0.01831 | -0.009155 | 0.041199 | 0.050354 | -0.054931 | -0.09613 | 0.022889 | 0.54016 | 0.28839 | 0.14191 | 0.34332 | 0.19684 | 0.75989 | 121.17 | 0.59509 | 121.1975 | 121.0098 | 121.0785 | 120.9503 | 121.0236 | -121.1792 | -121.1746 | 121.1105 | 121.1426 | 117.9428 | 112.3352
1675.6719 | 121.1609 | -118.2861 | 2.8519 | -0.013657 | 0.0033389 | 0.059248 | 0.057112 | -0.0040546 | -0.0068381 | -0.0023349 | -0.0021057 | 0.0034392 | 0.071083 | 0.065055 | -0.013296 | 0.020294 | -0.004202 | -0.23346 | 2.7008 | -118.3228 | 2.7145 | -117.6727 | -118.396 | -118.4143 | -6.0699 | 2.7924 | -118.3914 | 2.7145 | -117.9337 | -118.2953 | -118.0939 | -0.036621 | -0.15106 | -0.13733 | 0.6134 | -0.12817 | -0.10986 | -0.091553 | -0.073242 | -0.10528 | -0.05951 | -0.13733 | 0.35248 | 0.19226 | -0.009155 | 0.29755 | 0.09613 | 0.65002 | 121.0373 | 0.45776 | 121.106 | 121.0236 | 121.1838 | 120.9869 | 121.0785 | -121.1746 | -121.2433 | 121.0007 | 121.0007 | 118.0527 | 112.2162
1677.4375 | 121.2479 | -118.6844 | 2.536 | -0.021286 | -0.0020017 | 0.054335 | 0.053267 | -0.0051226 | -0.0074789 | -0.0042575 | -0.0051575 | 0.0023712 | 0.070229 | 0.055014 | -0.012655 | 0.01944 | -0.0005704 | -0.16022 | 2.4994 | -118.6157 | 2.4811 | -117.9565 | -118.6478 | -118.6935 | -6.0745 | 2.5223 | -118.6707 | 2.3941 | -118.2449 | -118.6295 | -118.4647 | 0.068664 | -0.036621 | -0.054932 | 0.72784 | -0.009155 | 0.036621 | -0.077819 | -0.032043 | 0.013733 | -0.013733 | -0.14191 | 0.43945 | 0.21973 | 0.054931 | 0.20599 | 0.041198 | 0.65918 | 121.0968 | 0.42572 | 121.0648 | 121.1151 | 121.1929 | 121.1838 | 121.2067 | -121.1517 | -121.2067 | 121.1655 | 121.0785 | 118.5242 | 112.6099
1679.125 | 121.1609 | -117.6956 | 3.3188 | -0.028916 | 0.0003483 | 0.055617 | 0.05348 | -0.0012774 | -0.0070517 | -0.0010531 | -0.0021057 | -0.00019216 | 0.071938 | 0.059714 | -0.011373 | 0.018585 | -0.0065518 | -0.19684 | 3.2639 | -117.6224 | 3.3783 | -116.9403 | -117.6407 | -117.627 | -6.0745 | 3.3417 | -117.7094 | 3.273 | -117.2607 | -117.6086 | -117.4667 | 0.073243 | -0.054932 | 0.059509 | 0.75531 | 0.068665 | 0.054932 | -0.004578 | -0.018311 | -0.013733 | 0.022888 | -0.045777 | 0.43488 | 0.22888 | 0.086975 | 0.24262 | 0.10071 | 0.68207 | 121.0007 | 0.44861 | 120.9824 | 120.8862 | 121.051 | 120.9595 | 121.0373 | -120.9412 | -121.0281 | 121.0739 | 120.9686 | 117.4988 | 111.6211
1680.875 | 121.2204 | -118.103 | 3.0121 | -0.0060272 | 0.0001345 | 0.056685 | 0.055403 | -0.00085021 | -0.010897 | -0.0031895 | -0.0051575 | 0.00023504 | 0.071297 | 0.070182 | -0.012441 | 0.020721 | -0.0022794 | -0.26093 | 2.8702 | -118.1534 | 2.8198 | -117.5308 | -118.2037 | -118.2266 | -6.2668 | 2.9114 | -118.1808 | 2.916 | -117.5079 | -118.0298 | -117.9108 | -0.050354 | -0.14191 | -0.19226 | 0.5722 | -0.1236 | -0.10071 | -0.073243 | -0.050354 | -0.07782 | -0.10071 | -0.09613 | 0.59509 | 0.19226 | 0.073242 | 0.27008 | 0.15106 | 0.62256 | 120.9732 | 0.67291 | 121.0968 | 121.0236 | 121.0922 | 120.9732 | 121.0144 | -121.1655 | -121.1929 | 120.9229 | 121.019 | 117.8421 | 111.8362
1682.5781 | 121.106 | -116.1484 | 4.6692 | -0.0060272 | -0.0032833 | 0.057112 | 0.052412 | -0.0012774 | -0.0076925 | -0.0027621 | -0.014313 | 0.00066224 | 0.070442 | 0.061423 | -0.013296 | 0.017303 | -0.0027066 | -0.20599 | 4.5181 | -116.217 | 4.6783 | -115.4388 | -116.1896 | -116.0248 | -6.0425 | 4.6143 | -116.1896 | 4.6692 | -115.6906 | -115.9973 | -115.8554 | -0.068665 | -0.15106 | 0.009156 | 0.70953 | 0.1236 | -0.041199 | 0.19226 | 0.027466 | -0.041199 | -0.054931 | 0 | 0.45776 | 0.29297 | 0.15106 | 0.33417 | 0.19226 | 0.7782 | 120.8954 | 0.49896 | 120.8588 | 120.7352 | 120.8038 | 120.6665 | 120.7626 | -120.8862 | -120.8588 | 120.8267 | 120.8176 | 115.9424 | 110.1059
1684.2656 | 120.9183 | -115.6448 | 5.1041 | -0.0060272 | -0.0026425 | 0.057112 | 0.054549 | 0.00021799 | -0.0061971 | -0.0046847 | -0.0021057 | 0.00087584 | 0.069801 | 0.059501 | -0.0098779 | 0.018799 | 0.0007114 | -0.33417 | 4.9576 | -115.7089 | 5.0583 | -115.0589 | -115.741 | -115.7501 | -6.2164 | 4.985 | -115.7593 | 5.0491 | -115.1596 | -115.6265 | -115.3702 | -0.064087 | -0.14648 | -0.045776 | 0.58594 | -0.10529 | -0.096131 | -0.041199 | -0.032044 | -0.11444 | -0.11902 | -0.054932 | 0.48523 | 0.27466 | 0.01831 | 0.3891 | 0.13275 | 0.65002 | 120.7672 | 0.59967 | 120.8084 | 120.6665 | 120.7443 | 120.6024 | 120.6299 | -120.813 | -120.8633 | 120.7031 | 120.694 | 115.3107 | 109.4284
1685.9531 | 120.8221 | -114.4592 | 6.0745 | -0.021286 | 0.0016299 | 0.05818 | 0.05583 | -0.0040546 | -0.0068381 | -0.0019077 | -0.0082093 | 0.001944 | 0.069801 | 0.059501 | -0.012869 | 0.020508 | -0.002493 | -0.21057 | 5.9418 | -114.505 | 6.1249 | -113.8184 | -114.5142 | -114.4959 | -6.1066 | 6.0287 | -114.5462 | 6.1615 | -114.0289 | -114.3539 | -114.1754 | -0.045776 | -0.13275 | 0.050354 | 0.64087 | -0.036621 | -0.054931 | 0.009155 | -0.009155 | -0.086975 | -0.045776 | 0.086975 | 0.4303 | 0.28381 | 0.10529 | 0.37079 | 0.19226 | 0.68665 | 120.6299 | 0.51727 | 120.7077 | 120.4468 | 120.575 | 120.401 | 120.488 | -120.5795 | -120.6207 | 120.5841 | 120.6207 | 114.2487 | 108.3527
1687.6406 | 120.5704 | -113.4247 | 7.0816 | 0.0016023 | 0.0033389 | 0.057967 | 0.057539 | 0.0017132 | -0.0070517 | -0.0040439 | -0.0051575 | 0.0042938 | 0.070442 | 0.056296 | -0.013723 | 0.020294 | -0.000784 | -0.32044 | 6.8848 | -113.5391 | 7.0358 | -112.8937 | -113.5757 | -113.4705 | -6.2531 | 7.0129 | -113.5208 | 6.9901 | -113.0035 | -113.4155 | -113.2507 | -0.11444 | -0.19684 | -0.045776 | 0.53101 | -0.045776 | -0.15106 | 0.068665 | -0.036621 | -0.09613 | -0.068665 | -0.091553 | 0.42114 | 0.17395 | 0.009156 | 0.27008 | 0.10529 | 0.64545 | 120.575 | 0.51727 | 120.5109 | 120.4239 | 120.5338 | 120.3094 | 120.4376 | -120.6207 | -120.6024 | 120.4605 | 120.4147 | 113.1042 | 107.1716
1689.3438 | 120.4559 | -113.681 | 6.6971 | -0.021286 | 0.0001345 | 0.056898 | 0.055617 | 0.0021406 | -0.0064109 | -0.0044711 | -0.0051575 | 0.003012 | 0.074287 | 0.064627 | -0.013723 | 0.022644 | -0.0029202 | -0.4303 | 6.5369 | -113.7451 | 6.4819 | -113.2736 | -113.8596 | -113.974 | -6.6101 | 6.5598 | -113.9191 | 6.3721 | -113.1866 | -113.5803 | -113.4476 | -0.064087 | -0.16022 | -0.21515 | 0.40741 | -0.29297 | -0.17853 | -0.22888 | -0.11444 | -0.23804 | -0.13733 | -0.32501 | 0.49438 | 0.23346 | 0.10071 | 0.4715 | 0.33875 | 0.4715 | 120.2271 | 0.73242 | 120.2911 | 120.282 | 120.4788 | 120.2179 | 120.2408 | -120.4422 | -120.6162 | 120.163 | 120.0531 | 113.2507 | 107.0709
1691.0938 | 120.7947 | -115.9653 | 4.5822 | -0.0060272 | 0.0003483 | 0.055403 | 0.053908 | -0.004909 | -0.0096151 | -0.0044711 | -0.0051575 | 0.00023504 | 0.070229 | 0.052237 | -0.012228 | 0.019653 | -0.00527 | -0.19226 | 4.3213 | -116.2262 | 4.5273 | -115.4984 | -116.153 | -116.1667 | -6.427 | 4.3991 | -116.2537 | 4.4632 | -115.7181 | -116.0339 | -115.5991 | -0.26093 | -0.26092 | -0.054931 | 0.46692 | -0.20142 | -0.18768 | 0.059509 | 0.073242 | -0.28839 | -0.1831 | -0.11902 | 0.24719 | 0.36621 | -0.068665 | 0.6546 | 0.21973 | 0.72784 | 120.7535 | 0.53558 | 120.7169 | 120.5475 | 120.6528 | 120.2866 | 120.3644 | -120.8084 | -120.8359 | 120.4926 | 120.4285 | 115.773 | 109.5383
1692.8594 | 120.5933 | -115.0314 | 5.4932 | -0.0060272 | -0.0017881 | 0.054335 | 0.053694 | -0.00085021 | -0.0083335 | -0.0023349 | -0.0051575 | 0.0017304 | 0.069801 | 0.057364 | -0.013082 | 0.019226 | -0.005911 | -0.18768 | 5.3696 | -115.0497 | 5.4016 | -114.3906 | -115.1001 | -115.1093 | -6.4865 | 5.4428 | -115.0726 | 5.3879 | -114.5966 | -114.9765 | -114.8346 | -0.018311 | -0.1236 | -0.091553 | 0.64087 | -0.07782 | -0.068665 | -0.059509 | -0.050354 | -0.041199 | -0.050354 | -0.10529 | 0.43488 | 0.19684 | 0.054932 | 0.23804 | 0.096131 | 0.65918 | 120.4514 | 0.47607 | 120.4605 | 120.4193 | 120.5154 | 120.401 | 120.4742 | -120.5429 | -120.5658 | 120.433 | 120.4193 | 114.8438 | 108.5449
1694.5625 | 120.6573 | -114.798 | 5.6259 | -0.013657 | 0.0016299 | 0.059035 | 0.056685 | 0.0025678 | -0.0085471 | -0.0016941 | -0.0051575 | 0.0021576 | 0.072365 | 0.059073 | -0.013296 | 0.020294 | -0.0014248 | -0.46692 | 5.3513 | -115.123 | 5.3467 | -114.418 | -115.2512 | -115.2328 | -6.3538 | 5.4062 | -114.9948 | 5.484 | -114.4821 | -114.679 | -114.2578 | -0.32501 | -0.27466 | -0.27924 | 0.37994 | -0.43488 | -0.45319 | -0.10986 | -0.12817 | -0.19684 | -0.21973 | -0.14191 | 0.31586 | 0.54016 | 0.11902 | 0.737 | 0.31586 | 0.70496 | 120.4697 | 0.51269 | 120.4788 | 120.4742 | 120.401 | 120.1492 | 120.2042 | -120.7489 | -120.6207 | 120.1447 | 120.282 | 114.3311 | 108.4442
1696.25 | 120.4102 | -113.7772 | 6.5781 | -0.013657 | 0.0007755 | 0.057326 | 0.055189 | 0.00085879 | -0.0072653 | -0.0016941 | -0.0021057 | 0.0023712 | 0.070015 | 0.060141 | -0.014364 | 0.020935 | -0.0033474 | -0.2243 | 6.4499 | -113.7863 | 6.5414 | -113.0676 | -113.7909 | -113.8733 | -6.427 | 6.5598 | -113.6993 | 6.5231 | -113.4705 | -113.8 | -113.5391 | -0.009155 | -0.12817 | -0.036621 | 0.70953 | -0.09613 | -0.013733 | -0.086975 | -0.004578 | 0.07782 | -0.018311 | -0.054932 | 0.3067 | 0.23804 | -0.022888 | 0.16022 | -0.10071 | 0.71869 | 120.3278 | 0.22888 | 120.2225 | 120.2362 | 120.2591 | 120.2271 | 120.3369 | -120.3644 | -120.2774 | 120.3186 | 120.3003 | 113.5529 | 107.3502
1698 | 120.5933 | -116.4413 | 4.0878 | -0.021286 | 0.0016299 | 0.056258 | 0.058607 | 0.00064519 | -0.0053427 | -0.0023349 | -0.0082093 | 0.0023712 | 0.074715 | 0.061423 | -0.010946 | 0.022003 | -0.0016384 | -0.2655 | 3.772 | -116.6748 | 3.8727 | -115.9653 | -116.8991 | -116.6428 | -7.0267 | 3.8773 | -116.6748 | 3.9551 | -115.9973 | -116.3086 | -116.1804 | -0.23346 | -0.31586 | -0.21515 | 0.47607 | -0.20142 | -0.45776 | 0.032044 | -0.2243 | -0.23346 | -0.21057 | -0.13275 | 0.44403 | 0.26093 | 0.13275 | 0.49439 | 0.36621 | 0.70953 | 120.5475 | 0.67749 | 120.6299 | 120.4468 | 120.5521 | 120.2133 | 120.3186 | -120.7626 | -120.7626 | 120.314 | 120.3964 | 116.1758 | 109.4147
1699.6875 | 120.3094 | -113.1363 | 7.1365 | -0.0060272 | -0.0015743 | 0.057112 | 0.054121 | -0.0012774 | -0.01047 | -0.0053257 | -0.0082093 | 2.1442e-05 | 0.071083 | 0.060569 | -0.010519 | 0.019653 | -0.0001432 | -0.11444 | 7.0084 | -113.1271 | 7.0358 | -112.5137 | -113.1912 | -113.205 | -6.6742 | 7.0633 | -113.2141 | 7.0404 | -112.7197 | -113.0722 | -112.9669 | 0.009156 | -0.12817 | -0.10071 | 0.62256 | -0.068664 | -0.054931 | -0.07782 | -0.064087 | -0.077819 | -0.073243 | -0.096131 | 0.41656 | 0.16937 | 0.064087 | 0.24719 | 0.14191 | 0.6134 | 120.163 | 0.49438 | 120.2545 | 120.1355 | 120.2774 | 120.1447 | 120.1996 | -120.2637 | -120.3506 | 120.1721 | 120.1767 | 113.0219 | 106.4621
1701.3906 | 120.8038 | -120.6253 | 0.10986 | -0.013657 | 0.0003483 | 0.055189 | 0.053908 | -0.002132 | -0.0074789 | -0.0010531 | -0.0021057 | 2.1442e-05 | 0.072151 | 0.059073 | -0.010092 | 0.019653 | -0.0050564 | -0.26093 | -0.045776 | -120.6802 | -0.041199 | -120.0027 | -120.6848 | -120.7077 | -7.4799 | 0.050354 | -120.7352 | -0.041199 | -120.2087 | -120.5978 | -120.433 | -0.054932 | -0.15564 | -0.15106 | 0.62256 | -0.082398 | -0.059509 | -0.027466 | -0.004577 | -0.10986 | -0.059509 | -0.15106 | 0.41656 | 0.19226 | 0.027466 | 0.30212 | 0.13733 | 0.67749 | 120.639 | 0.52643 | 120.694 | 120.6345 | 120.7855 | 120.5795 | 120.6757 | -120.7901 | -120.845 | 120.5841 | 120.5841 | 120.3644 | 113.1454
1703.0781 | 121.1563 | -120.8313 | 0.082397 | -0.013657 | 0.0016299 | 0.058821 | 0.057326 | 0.00064519 | -0.0059835 | -0.00083947 | -0.0051575 | 0.00066224 | 0.072365 | 0.065482 | -0.011373 | 0.020081 | -0.0039884 | -0.35706 | -0.032043 | -120.9229 | 0.004578 | -120.1859 | -120.9091 | -120.9229 | -7.5027 | 0.018311 | -120.9503 | 0.091553 | -120.3415 | -120.7352 | -120.5338 | -0.091553 | -0.11444 | -0.077819 | 0.64545 | -0.091553 | -0.07782 | 0 | 0.013733 | -0.11902 | -0.064086 | 0.009156 | 0.48981 | 0.29755 | 0.096131 | 0.41656 | 0.21515 | 0.737 | 120.9274 | 0.60882 | 121.0419 | 120.8908 | 120.9686 | 120.7993 | 120.8496 | -121.0052 | -121.0327 | 120.8359 | 120.9229 | 120.4742 | 113.3286
1704.7656 | 121.1151 | -120.9457 | 0.10986 | -0.013657 | 0.0016299 | 0.058607 | 0.054762 | -0.00063661 | -0.0064109 | -0.0019077 | -0.0082093 | 0.0027984 | 0.069588 | 0.06185 | -0.01116 | 0.021362 | -0.0012112 | -0.27008 | -0.032043 | -120.9869 | -0.018311 | -120.2911 | -121.0236 | -121.0464 | -7.6172 | 0.041199 | -121.051 | 0.009155 | -120.5017 | -120.9137 | -120.694 | -0.041198 | -0.14191 | -0.12817 | 0.6546 | -0.10071 | -0.07782 | -0.05951 | -0.036622 | -0.10528 | -0.068664 | -0.10071 | 0.44403 | 0.25177 | 0.032044 | 0.35706 | 0.13733 | 0.6958 | 120.9686 | 0.54932 | 121.0602 | 120.9549 | 121.0922 | 120.9137 | 120.9869 | -121.0968 | -121.1609 | 120.9274 | 120.9549 | 120.6757 | 113.3286
1706.4531 | 121.2616 | -120.9595 | 0.059509 | -0.021286 | 0.0012027 | 0.059248 | 0.054121 | 0.0051312 | -0.0047019 | -0.0034031 | -0.0051575 | -0.00040596 | 0.072151 | 0.064414 | -0.012869 | 0.018158 | -0.0016384 | -0.3067 | -0.068665 | -121.0007 | 0.059509 | -120.2454 | -120.9869 | -120.9961 | -7.6721 | -0.013733 | -121.019 | 0.09613 | -120.4376 | -120.8405 | -120.6528 | -0.041198 | -0.12817 | 0 | 0.71411 | -0.036621 | -0.027465 | 0.004577 | 0.013733 | -0.059509 | -0.073242 | 0.036621 | 0.52185 | 0.3067 | 0.11902 | 0.36621 | 0.17853 | 0.75531 | 121.0602 | 0.58136 | 121.1151 | 120.932 | 121.0052 | 120.8908 | 120.9457 | -121.0602 | -121.0785 | 121.019 | 121.0556 | 120.6528 | 113.2874
1708.2031 | 121.1792 | -121.019 | 0.11444 | -0.013657 | 0.0018435 | 0.055189 | 0.055189 | -0.00042301 | -0.0061971 | 1.4934e-05 | -0.0082093 | 0.0034392 | 0.072792 | 0.059287 | -0.016073 | 0.018799 | -0.000784 | -0.28381 | -0.013733 | -121.0876 | -0.045776 | -120.4193 | -121.1517 | -121.1472 | -7.869 | 0.045776 | -121.1243 | -0.027466 | -120.6116 | -121.019 | -120.8221 | -0.068664 | -0.12817 | -0.16022 | 0.59967 | -0.12817 | -0.13275 | -0.05951 | -0.064087 | -0.10529 | -0.068665 | -0.14191 | 0.40741 | 0.19684 | 0 | 0.30212 | 0.10529 | 0.66833 | 121.0419 | 0.5127 | 121.0968 | 121.0739 | 121.17 | 121.0052 | 121.0648 | -121.2021 | -121.2387 | 120.9732 | 120.9915 | 120.7352 | 113.15
1709.9531 | 121.3531 | -121.0144 | 0.082397 | -0.013657 | 0.0022709 | 0.059248 | 0.054976 | -0.0029864 | -0.0068381 | -0.0053257 | -0.0051575 | 0.001944 | 0.071297 | 0.063987 | -0.012228 | 0.021362 | -0.0012112 | -0.29755 | -0.059509 | -121.0831 | 0.045776 | -120.3232 | -121.0602 | -121.0464 | -7.8735 | -0.004578 | -121.1334 | 0.10071 | -120.5109 | -120.9091 | -120.7306 | -0.068665 | -0.14191 | -0.036621 | 0.69122 | -0.032044 | -0.045777 | 0.036621 | 0.022888 | -0.11902 | -0.086975 | 0.018311 | 0.50354 | 0.28381 | 0.10528 | 0.40283 | 0.2243 | 0.75989 | 121.1288 | 0.62256 | 121.2341 | 121.0236 | 121.1288 | 120.9549 | 121.0098 | -121.1655 | -121.2158 | 121.0602 | 121.1151 | 120.7169 | 113.1409
1711.6406 | 121.3531 | -121.0327 | 0.068665 | -0.013657 | 0.0012027 | 0.059462 | 0.056044 | 0.0027814 | -0.0055563 | -0.0034031 | -0.0051575 | 0.001944 | 0.068947 | 0.059073 | -0.011373 | 0.019653 | -0.0020658 | -0.35248 | -0.064087 | -121.1288 | 0.018311 | -120.3918 | -121.1243 | -121.1288 | -7.9926 | 0.027466 | -121.1563 | 0.10071 | -120.5566 | -120.9549 | -120.726 | -0.09613 | -0.13275 | -0.050354 | 0.64087 | -0.09613 | -0.091553 | 0 | 0.004577 | -0.1236 | -0.041199 | 0.032043 | 0.47607 | 0.3067 | 0.07782 | 0.4303 | 0.20142 | 0.737 | 121.1472 | 0.59967 | 121.257 | 121.0648 | 121.1838 | 120.9686 | 121.0602 | -121.1975 | -121.225 | 121.051 | 121.1334 | 120.6802 | 113.0402
1713.3281 | 121.2662 | -121.1426 | 0.10986 | -0.0060272 | -0.0017881 | 0.055403 | 0.054762 | -0.0023456 | -0.0074789 | 0.0012967 | -0.0082093 | 0.0025848 | 0.071297 | 0.057364 | -0.012228 | 0.020081 | -0.0033474 | -0.27008 | -0.022888 | -121.1884 | -0.064087 | -120.488 | -121.2021 | -121.2204 | -8.1345 | 0.064087 | -121.2021 | -0.041199 | -120.6894 | -121.0876 | -120.9137 | -0.045776 | -0.13275 | -0.17395 | 0.6546 | -0.07782 | -0.059509 | -0.032044 | -0.013733 | -0.059509 | -0.045776 | -0.15106 | 0.45319 | 0.22888 | 0.054932 | 0.28839 | 0.11444 | 0.70038 | 121.1243 | 0.5127 | 121.1609 | 121.1655 | 121.2662 | 121.1197 | 121.2067 | -121.2982 | -121.312 | 121.0785 | 121.1014 | 120.8725 | 113.0081
1715.0156 | 121.4264 | -121.0876 | 0.054932 | -0.013657 | 0.0029117 | 0.059676 | 0.056258 | 0.0042768 | -0.0076925 | -0.0051121 | -0.011261 | 0.0021576 | 0.070229 | 0.065909 | -0.01415 | 0.020081 | -0.0056974 | -0.29755 | -0.082397 | -121.1517 | 0.064087 | -120.3964 | -121.138 | -121.1426 | -8.1573 | -0.013733 | -121.1792 | 0.10986 | -120.5887 | -120.9778 | -120.7855 | -0.064087 | -0.13733 | 0.009155 | 0.69122 | -0.054932 | -0.050354 | 0.009155 | 0.013733 | -0.091553 | -0.068665 | 0.054931 | 0.49896 | 0.30212 | 0.10986 | 0.39368 | 0.20142 | 0.75531 | 121.2158 | 0.59051 | 121.2891 | 121.0693 | 121.1655 | 121.0052 | 121.0739 | -121.2067 | -121.2341 | 121.1517 | 121.1975 | 120.7901 | 112.9303
1716.7812 | 121.4401 | -121.1472 | 0.068665 | -0.021286 | -0.0015743 | 0.054762 | 0.054121 | 0.001286 | -0.010256 | -0.00083947 | -0.0021057 | 0.00066224 | 0.070869 | 0.056083 | -0.012014 | 0.019867 | -0.00527 | -0.29755 | -0.07782 | -121.1884 | 0.027466 | -120.4376 | -121.1563 | -121.1517 | -8.2352 | 0.013733 | -121.2296 | 0.10071 | -120.5933 | -120.9778 | -120.8221 | -0.041198 | -0.14649 | -0.041199 | 0.70953 | -0.004577 | -0.009155 | 0.036621 | 0.032043 | -0.082397 | -0.054932 | 0.032043 | 0.55389 | 0.32501 | 0.16937 | 0.40741 | 0.25177 | 0.75073 | 121.2158 | 0.63629 | 121.3303 | 121.1105 | 121.2433 | 121.0693 | 121.1609 | -121.257 | -121.2982 | 121.1746 | 121.2479 | 120.8496 | 112.912
1718.4688 | 121.3257 | -121.1884 | 0.1236 | -0.013657 | 0.0020571 | 0.058394 | 0.056685 | 0.0025678 | -0.0076925 | -0.0023349 | -0.0051575 | 0.0010894 | 0.069374 | 0.066977 | -0.013082 | 0.021362 | 0.0002842 | -0.32501 | -0.032043 | -121.2296 | -0.059509 | -120.6207 | -121.3394 | -121.3165 | -8.4961 | 0.045776 | -121.2845 | -0.032043 | -120.7809 | -121.1884 | -120.9595 | -0.041199 | -0.15564 | -0.1831 | 0.56763 | -0.12817 | -0.15106 | -0.086975 | -0.10986 | -0.096131 | -0.07782 | -0.15564 | 0.40741 | 0.22888 | 0 | 0.32501 | 0.096131 | 0.60882 | 121.17 | 0.50354 | 121.2524 | 121.1975 | 121.3303 | 121.1563 | 121.2341 | -121.3531 | -121.4081 | 121.1288 | 121.1563 | 120.8633 | 112.6923
1720.2188 | 121.3623 | -121.1929 | 0.11902 | -0.021286 | 0.0003483 | 0.057112 | 0.05583 | -0.00020941 | -0.0061971 | -0.0016941 | -0.0051575 | 0.0034392 | 0.069801 | 0.057792 | -0.012228 | 0.02179 | -0.0012112 | -0.37537 | -0.032043 | -121.2341 | -0.091553 | -120.6299 | -121.3348 | -121.3303 | -8.6105 | 0.059509 | -121.2982 | -0.018311 | -120.7901 | -121.1929 | -120.9732 | -0.041199 | -0.15106 | -0.21057 | 0.56305 | -0.13733 | -0.14191 | -0.09613 | -0.10071 | -0.10529 | -0.05951 | -0.13733 | 0.40283 | 0.21973 | 0 | 0.32501 | 0.10529 | 0.60425 | 121.1426 | 0.50812 | 121.2799 | 121.2021 | 121.3577 | 121.1609 | 121.2524 | -121.3531 | -121.4172 | 121.1014 | 121.1746 | 120.8176 | 112.5824
1721.9688 | 121.4401 | -121.2341 | 0.09613 | -0.0060272 | 0.0009891 | 0.056258 | 0.054762 | 0.0017132 | -0.0083335 | -0.00019867 | -0.0051575 | 0.001944 | 0.070656 | 0.066123 | -0.011587 | 0.022644 | -0.0065518 | -0.25635 | -0.013733 | -121.2799 | -0.018311 | -120.5658 | -121.2708 | -121.2982 | -8.5876 | 0.050354 | -121.3211 | 0.022888 | -120.7306 | -121.138 | -120.9549 | -0.045776 | -0.10986 | -0.11444 | 0.66833 | -0.064087 | -0.036621 | -0.018311 | 0.009155 | -0.086975 | -0.045776 | -0.073242 | 0.50354 | 0.27924 | 0.096131 | 0.36621 | 0.18311 | 0.71411 | 121.2616 | 0.59051 | 121.344 | 121.2662 | 121.3715 | 121.2204 | 121.2845 | -121.376 | -121.4172 | 121.2158 | 121.257 | 120.9778 | 112.6465
1723.6562 | 121.5042 | -121.225 | 0.064087 | -0.0060272 | -0.0024289 | 0.057326 | 0.053694 | -0.0032 | -0.0066245 | -0.0012669 | -0.0021057 | -0.00061956 | 0.071083 | 0.053946 | -0.010092 | 0.019226 | -0.00527 | -0.32959 | -0.064087 | -121.2891 | 0 | -120.5521 | -121.2524 | -121.2662 | -8.7021 | 0.018311 | -121.3165 | 0.073242 | -120.6802 | -121.0785 | -120.9229 | -0.064086 | -0.12817 | -0.064087 | 0.67291 | -0.041198 | -0.027465 | 0.022888 | 0.036621 | -0.091552 | -0.045776 | 0.009155 | 0.54474 | 0.30212 | 0.14648 | 0.39368 | 0.23804 | 0.737 | 121.2891 | 0.63629 | 121.3898 | 121.225 | 121.3348 | 121.1609 | 121.2433 | -121.3531 | -121.3806 | 121.225 | 121.2982 | 120.8954 | 112.5229
1725.3438 | 121.4905 | -121.225 | 0.07782 | -0.013657 | -0.0015743 | 0.057539 | 0.051985 | -0.00020941 | -0.0083335 | -0.0038303 | -0.0051575 | 0.00087584 | 0.070869 | 0.05416 | -0.012655 | 0.019226 | -0.0018522 | -0.34332 | -0.064087 | -121.2799 | 0.022888 | -120.5658 | -121.2982 | -121.2936 | -8.844 | 0.013733 | -121.3211 | 0.050354 | -120.7397 | -121.138 | -120.9503 | -0.054931 | -0.14191 | -0.054932 | 0.65918 | -0.068664 | -0.073242 | -0.013733 | -0.018311 | -0.09613 | -0.064087 | -0.027466 | 0.48523 | 0.27466 | 0.086976 | 0.37079 | 0.18311 | 0.71411 | 121.3028 | 0.58136 | 121.3715 | 121.2158 | 121.3348 | 121.1609 | 121.2387 | -121.3577 | -121.3989 | 121.2479 | 121.2753 | 120.8817 | 112.381
1727.0938 | 121.5546 | -121.2433 | 0.082397 | -0.021286 | 0.0005619 | 0.058607 | 0.056471 | 0.0021406 | -0.0049155 | -0.0027621 | -0.0051575 | 0.001944 | 0.070656 | 0.062491 | -0.014578 | 0.021149 | -0.0061246 | -0.31586 | -0.07782 | -121.2341 | 0.073242 | -120.5429 | -121.2799 | -121.2753 | -8.8806 | 0.041199 | -121.3303 | 0.11444 | -120.7031 | -121.106 | -120.9137 | 0.009155 | -0.16022 | -0.009155 | 0.70038 | -0.032044 | -0.036621 | -0.041199 | -0.045776 | -0.086975 | -0.041198 | 0.032044 | 0.54016 | 0.32959 | 0.13733 | 0.41656 | 0.2243 | 0.69122 | 121.3074 | 0.62714 | 121.4447 | 121.1563 | 121.3715 | 121.1655 | 121.2845 | -121.3165 | -121.4127 | 121.3165 | 121.3577 | 120.9274 | 112.3627
1728.7812 | 121.4584 | -121.2845 | 0.10529 | -0.021286 | -0.0007199 | 0.056685 | 0.056258 | 0.00043159 | -0.0068381 | 1.4934e-05 | -0.0082093 | 0.0025848 | 0.073433 | 0.063773 | -0.014791 | 0.01944 | 0.0007114 | -0.2655 | -0.018311 | -121.344 | -0.073242 | -120.694 | -121.3715 | -121.3943 | -9.0591 | 0.045776 | -121.3852 | -0.018311 | -120.813 | -121.2296 | -121.0373 | -0.059509 | -0.1236 | -0.17853 | 0.59052 | -0.10986 | -0.086975 | -0.050354 | -0.027466 | -0.10071 | -0.05951 | -0.1236 | 0.4715 | 0.24719 | 0.054932 | 0.3479 | 0.15564 | 0.65002 | 121.2708 | 0.5722 | 121.3669 | 121.3257 | 121.431 | 121.2662 | 121.3303 | -121.4493 | -121.4905 | 121.2112 | 121.2662 | 121.019 | 112.2253
1730.4688 | 121.4905 | -121.2891 | 0.10986 | -0.013657 | -0.0005063 | 0.055189 | 0.055403 | 0.0034222 | -0.0076925 | -0.0023349 | -0.0051575 | 0.004721 | 0.070015 | 0.059287 | -0.014791 | 0.020081 | -0.0009976 | -0.24719 | -0.018311 | -121.344 | -0.027466 | -120.639 | -121.344 | -121.376 | -9.1324 | 0.045776 | -121.3577 | 0.022888 | -120.7901 | -121.2204 | -121.0281 | -0.054932 | -0.12817 | -0.13733 | 0.65002 | -0.086976 | -0.054932 | -0.032044 | 0 | -0.068665 | -0.064087 | -0.086975 | 0.49896 | 0.26093 | 0.068664 | 0.32959 | 0.13733 | 0.70496 | 121.3165 | 0.56763 | 121.3806 | 121.3257 | 121.4035 | 121.2708 | 121.3348 | -121.4539 | -121.4676 | 121.2616 | 121.3119 | 121.0419 | 112.1567
1732.2344 | 121.582 | -121.2708 | 0.073242 | 0.0016023 | -0.0026425 | 0.056471 | 0.052626 | -0.0017048 | -0.0068381 | -0.0029759 | -0.0082093 | -0.0019012 | 0.070015 | 0.05651 | -0.01351 | 0.01944 | 0.0015658 | -0.3067 | -0.068665 | -121.3348 | 0.027466 | -120.575 | -121.2845 | -121.3074 | -9.2102 | 0.018311 | -121.3943 | 0.082397 | -120.7352 | -121.1288 | -120.9457 | -0.064087 | -0.14191 | -0.045776 | 0.6958 | -0.036621 | -0.013733 | 0.027466 | 0.050354 | -0.1236 | -0.054931 | 0.009155 | 0.53558 | 0.32501 | 0.14191 | 0.44861 | 0.2655 | 0.75989 | 121.3623 | 0.65918 | 121.4767 | 121.2662 | 121.4127 | 121.2021 | 121.2891 | -121.4081 | -121.4676 | 121.2982 | 121.3531 | 120.9641 | 112.0605
1733.9844 | 121.5591 | -121.2936 | 0.09613 | -0.021286 | -0.0011471 | 0.056898 | 0.054549 | -0.00042301 | -0.0085471 | -0.0063937 | -0.0051575 | -0.00061956 | 0.06916 | 0.056937 | -0.014364 | 0.019867 | -0.000784 | -0.37537 | -0.064087 | -121.3486 | 0.009155 | -120.6482 | -121.3623 | -121.3486 | -9.4162 | 0 | -121.4035 | 0.032043 | -120.8176 | -121.2158 | -121.019 | -0.054932 | -0.16022 | -0.086975 | 0.64545 | -0.054932 | -0.068665 | 0 | -0.013733 | -0.10986 | -0.09613 | -0.064087 | 0.47607 | 0.27466 | 0.07782 | 0.38452 | 0.18768 | 0.70038 | 121.3577 | 0.58594 | 121.4355 | 121.2845 | 121.4035 | 121.2296 | 121.2936 | -121.4447 | -121.4996 | 121.3028 | 121.3257 | 120.9183 | 111.8774
1735.7344 | 121.5271 | -121.3623 | 0.10529 | -0.013657 | 0.0012027 | 0.056898 | 0.056898 | 0.0025678 | -0.0064109 | -0.0048985 | -0.0051575 | 0.0032256 | 0.070869 | 0.065909 | -0.014364 | 0.020081 | -0.0054838 | -0.27008 | -0.041199 | -121.3806 | -0.009155 | -120.6802 | -121.3989 | -121.431 | -9.4757 | 0.050354 | -121.4264 | 0.032043 | -120.8359 | -121.2479 | -121.0419 | -0.01831 | -0.14649 | -0.11444 | 0.68207 | -0.068664 | -0.036621 | -0.050354 | -0.018311 | -0.064087 | -0.054932 | -0.073243 | 0.52643 | 0.32044 | 0.11444 | 0.38452 | 0.17853 | 0.70038 | 121.3715 | 0.59052 | 121.4584 | 121.3394 | 121.4767 | 121.3211 | 121.4127 | -121.4859 | -121.5317 | 121.3531 | 121.3943 | 121.0922 | 111.8866
1737.4375 | 121.5088 | -121.344 | 0.11444 | -0.021286 | 0.0024845 | 0.05818 | 0.056044 | 0.001286 | -0.0081197 | -0.0027621 | -0.0082093 | 0.0040802 | 0.073647 | 0.064841 | -0.011373 | 0.019867 | -0.0009976 | -0.30212 | -0.032043 | -121.4081 | -0.027466 | -120.7123 | -121.4539 | -121.4493 | -9.6863 | 0.036621 | -121.431 | -0.009155 | -120.8954 | -121.3348 | -121.0968 | -0.064087 | -0.14648 | -0.14191 | 0.63171 | -0.10529 | -0.10986 | -0.041199 | -0.045776 | -0.086975 | -0.07782 | -0.1236 | 0.44861 | 0.24719 | 0.009155 | 0.33417 | 0.09613 | 0.6958 | 121.3806 | 0.53558 | 121.4218 | 121.376 | 121.4676 | 121.312 | 121.3806 | -121.5225 | -121.5454 | 121.3165 | 121.3348 | 121.0419 | 111.6577
1739.1875 | 121.6324 | -121.3257 | 0.09613 | -0.0060272 | -0.0026425 | 0.057112 | 0.053908 | -0.0057636 | -0.0076925 | -0.0016941 | -0.011261 | 0.00087584 | 0.072365 | 0.055655 | -0.012228 | 0.020081 | -0.0022794 | -0.25177 | -0.068665 | -121.3806 | 0.054932 | -120.607 | -121.3211 | -121.3394 | -9.6451 | 0.027466 | -121.4127 | 0.082397 | -120.7626 | -121.1884 | -120.9915 | -0.054931 | -0.16479 | -0.041198 | 0.71869 | -0.013733 | 0.004578 | 0.041198 | 0.059509 | -0.086975 | -0.068664 | -0.013733 | 0.56305 | 0.33417 | 0.13733 | 0.42114 | 0.22431 | 0.77362 | 121.4355 | 0.65002 | 121.4951 | 121.312 | 121.4401 | 121.257 | 121.3531 | -121.4767 | -121.5088 | 121.3806 | 121.4081 | 121.0739 | 111.6806
1740.875 | 121.6415 | -121.3394 | 0.073242 | -0.0060272 | 0.0020571 | 0.057326 | 0.054549 | 0.0021406 | -0.0068381 | -0.0036167 | -0.0021057 | -0.0016876 | 0.073006 | 0.056723 | -0.012014 | 0.01944 | -0.0033474 | -0.34332 | -0.073242 | -121.3623 | 0.082397 | -120.639 | -121.3806 | -121.3669 | -9.8557 | 0.004578 | -121.4035 | 0.09613 | -120.8084 | -121.2296 | -121.0144 | -0.022888 | -0.14648 | 0.009155 | 0.70038 | -0.027465 | -0.041198 | -0.004577 | -0.01831 | -0.064086 | -0.068664 | 0.022888 | 0.53101 | 0.32501 | 0.10986 | 0.3891 | 0.17395 | 0.72327 | 121.4447 | 0.59509 | 121.4996 | 121.2891 | 121.4081 | 121.2662 | 121.344 | -121.4355 | -121.4767 | 121.4218 | 121.4355 | 120.9961 | 111.4838
1742.625 | 121.5408 | -121.376 | 0.10529 | 0.0016023 | 0.0035525 | 0.056685 | 0.056258 | -0.002132 | -0.0087607 | 0.00022853 | -0.0051575 | 0.0034392 | 0.07151 | 0.057578 | -0.012014 | 0.02179 | 0.0015658 | -0.3891 | -0.036621 | -121.463 | -0.07782 | -120.8313 | -121.5454 | -121.5317 | -10.1349 | 0.064087 | -121.4951 | -0.027466 | -120.9641 | -121.3898 | -121.138 | -0.086975 | -0.14191 | -0.18311 | 0.54474 | -0.15564 | -0.16937 | -0.068664 | -0.082397 | -0.11902 | -0.041199 | -0.13275 | 0.41199 | 0.23804 | -0.013733 | 0.35706 | 0.10529 | 0.63171 | 121.3852 | 0.53101 | 121.4676 | 121.4264 | 121.5591 | 121.3394 | 121.4401 | -121.5683 | -121.6003 | 121.2982 | 121.3486 | 120.9869 | 111.2411
1744.3594 | 121.7056 | -121.3715 | 0.09613 | -0.0060272 | -0.0002927 | 0.055617 | 0.051772 | -0.0046954 | -0.0087607 | -0.0066073 | -0.014313 | 0.00023504 | 0.07151 | 0.056083 | -0.012655 | 0.01944 | -0.0003568 | -0.27008 | -0.073242 | -121.4127 | 0.073242 | -120.6345 | -121.3531 | -121.3669 | -10.0433 | 0.004578 | -121.463 | 0.082397 | -120.7672 | -121.1884 | -121.0052 | -0.041199 | -0.16937 | -0.022888 | 0.737 | 0.004578 | 0.018311 | 0.045777 | 0.05951 | -0.091553 | -0.091552 | -0.013733 | 0.60425 | 0.36621 | 0.18311 | 0.45776 | 0.27466 | 0.7782 | 121.4859 | 0.6958 | 121.5454 | 121.3394 | 121.4676 | 121.2982 | 121.376 | -121.5088 | -121.5591 | 121.4447 | 121.4539 | 121.1014 | 111.3281
1746.0625 | 121.6507 | -121.3852 | 0.086975 | -0.013657 | -0.0002927 | 0.05818 | 0.054549 | -0.003841 | -0.0072653 | -0.0051121 | -0.0021057 | -0.00019216 | 0.069801 | 0.06655 | -0.014364 | 0.020508 | -0.005911 | -0.36163 | -0.064087 | -121.431 | 0.004578 | -120.7397 | -121.4493 | -121.4447 | -10.3271 | 0.009155 | -121.4813 | 0.041199 | -120.8588 | -121.2753 | -121.0739 | -0.045776 | -0.15106 | -0.082397 | 0.64545 | -0.059509 | -0.064087 | -0.013733 | -0.018311 | -0.09613 | -0.07782 | -0.045776 | 0.52643 | 0.31128 | 0.10986 | 0.40741 | 0.20599 | 0.69122 | 121.4355 | 0.62256 | 121.5225 | 121.3669 | 121.4905 | 121.3211 | 121.3943 | -121.5179 | -121.5683 | 121.3898 | 121.4264 | 121.0236 | 111.058
1747.8125 | 121.6553 | -121.3943 | 0.07782 | -0.0060272 | 0.0020571 | 0.056685 | 0.054335 | -0.0040546 | -0.0081197 | -0.0046847 | -0.0051575 | 0.00044864 | 0.070229 | 0.057364 | -0.012228 | 0.020081 | -0.0037748 | -0.38452 | -0.064087 | -121.4401 | 0.004578 | -120.7306 | -121.4493 | -121.4584 | -10.4691 | 0.027466 | -121.4951 | 0.050354 | -120.8908 | -121.2936 | -121.0831 | -0.045777 | -0.14191 | -0.073242 | 0.66376 | -0.064087 | -0.054932 | -0.01831 | -0.009155 | -0.10071 | -0.050354 | -0.027466 | 0.50354 | 0.31128 | 0.10071 | 0.41199 | 0.20142 | 0.70953 | 121.4447 | 0.60425 | 121.5454 | 121.376 | 121.5225 | 121.3303 | 121.4218 | -121.5179 | -121.5729 | 121.3989 | 121.4447 | 121.0098 | 110.9253
1749.5 | 121.7148 | -121.3852 | 0.082397 | -0.021286 | -0.0015743 | 0.057112 | 0.053053 | -0.0010638 | -0.0079061 | -0.0046847 | -0.0051575 | 0.0023712 | 0.073219 | 0.056723 | -0.012869 | 0.019867 | -0.00762 | -0.27466 | -0.068665 | -121.4584 | 0.073242 | -120.6299 | -121.3577 | -121.3715 | -10.4736 | 0.018311 | -121.4813 | 0.091553 | -120.8221 | -121.2433 | -121.0373 | -0.073242 | -0.15106 | -0.009155 | 0.75531 | 0.013733 | 0.027466 | 0.086975 | 0.10071 | -0.09613 | -0.064086 | 0.009156 | 0.56305 | 0.3479 | 0.14191 | 0.44403 | 0.23804 | 0.82855 | 121.5317 | 0.65918 | 121.5729 | 121.3898 | 121.4996 | 121.3165 | 121.4035 | -121.5408 | -121.5637 | 121.4584 | 121.4767 | 121.1105 | 110.9116
1751.1875 | 121.5866 | -121.4447 | 0.10529 | -0.013657 | 0.0037661 | 0.056471 | 0.057539 | 0.0038494 | -0.0096151 | -0.0042575 | -0.0021057 | 0.0042938 | 0.069801 | 0.064627 | -0.011801 | 0.019653 | -0.003561 | -0.40741 | -0.009155 | -121.4996 | -0.073242 | -120.8908 | -121.5912 | -121.5729 | -10.8398 | 0.045776 | -121.5408 | -0.022888 | -121.0098 | -121.4447 | -121.1655 | -0.054932 | -0.11444 | -0.17853 | 0.55389 | -0.12817 | -0.14648 | -0.073242 | -0.091553 | -0.096131 | -0.05951 | -0.12817 | 0.43488 | 0.27924 | 0 | 0.37537 | 0.096131 | 0.60883 | 121.4264 | 0.53101 | 121.5179 | 121.4905 | 121.5866 | 121.4355 | 121.4905 | -121.6049 | -121.6461 | 121.3715 | 121.4218 | 121.0373 | 110.6049
1752.9531 | 121.7102 | -121.4218 | 0.082397 | -0.013657 | 0.0029117 | 0.057753 | 0.05348 | 0.0017132 | -0.0049155 | -0.0040439 | -0.0051575 | 0.0010894 | 0.071938 | 0.07125 | -0.012228 | 0.01944 | -0.0037748 | -0.3891 | -0.059509 | -121.4767 | 0.045776 | -120.7443 | -121.4905 | -121.4813 | -10.8536 | 0.022888 | -121.5088 | 0.11444 | -120.8771 | -121.3028 | -121.0281 | -0.054932 | -0.14191 | -0.036621 | 0.67749 | -0.059509 | -0.068665 | -0.004577 | -0.013733 | -0.086975 | -0.059509 | 0.032044 | 0.54474 | 0.39368 | 0.11902 | 0.48065 | 0.20599 | 0.73242 | 121.5225 | 0.63171 | 121.6232 | 121.4172 | 121.5317 | 121.3623 | 121.4447 | -121.5591 | -121.5912 | 121.4676 | 121.5363 | 121.0327 | 110.5682
1754.7031 | 121.6553 | -121.463 | 0.10986 | -0.021286 | -0.0007199 | 0.057967 | 0.054976 | 0.00064519 | -0.0070517 | -0.00062587 | -0.0021057 | 0.0032256 | 0.072151 | 0.069114 | -0.01415 | 0.019653 | -0.003561 | -0.29297 | -0.018311 | -121.5454 | -0.013733 | -120.7947 | -121.5134 | -121.5317 | -11.0001 | 0.041199 | -121.5363 | 0.018311 | -120.9457 | -121.3715 | -121.106 | -0.082397 | -0.12817 | -0.1236 | 0.66833 | -0.068664 | -0.050354 | 0.013733 | 0.032043 | -0.073242 | -0.068664 | -0.091552 | 0.51727 | 0.35706 | 0.091553 | 0.4303 | 0.16479 | 0.75073 | 121.5317 | 0.59051 | 121.5546 | 121.5271 | 121.5775 | 121.4447 | 121.5042 | -121.6553 | -121.6461 | 121.4493 | 121.4813 | 121.17 | 110.463
1756.3906 | 121.6599 | -121.463 | 0.11444 | -0.013657 | -0.0007199 | 0.057539 | 0.057326 | 0.0049176 | -0.0068381 | -0.0044711 | -0.0051575 | 0.003012 | 0.073433 | 0.058005 | -0.011373 | 0.020935 | -0.0039884 | -0.3067 | -0.027466 | -121.5408 | -0.041199 | -120.8405 | -121.5271 | -121.5637 | -11.1786 | 0.064087 | -121.5546 | 0.018311 | -120.9503 | -121.3898 | -121.1243 | -0.07782 | -0.14191 | -0.15564 | 0.62256 | -0.10071 | -0.064087 | -0.022888 | 0.013733 | -0.091552 | -0.050354 | -0.09613 | 0.5127 | 0.33875 | 0.073242 | 0.4303 | 0.16479 | 0.70038 | 121.4996 | 0.60425 | 121.5729 | 121.5134 | 121.6187 | 121.4355 | 121.5271 | -121.6553 | -121.669 | 121.4218 | 121.4813 | 121.1563 | 110.2844
1758.1406 | 121.7056 | -121.4493 | 0.09613 | -0.021286 | 0.0016299 | 0.059035 | 0.056258 | -0.00063661 | -0.0079061 | -0.0029759 | -0.0021057 | 0.001303 | 0.071724 | 0.056083 | -0.013082 | 0.020294 | 7.04e-05 | -0.41657 | -0.022888 | -121.5088 | -0.009155 | -120.8176 | -121.5454 | -121.5363 | -11.3571 | 0.032043 | -121.5454 | 0.086975 | -120.9137 | -121.344 | -121.0419 | -0.059509 | -0.11902 | -0.10528 | 0.63171 | -0.086975 | -0.09613 | -0.027466 | -0.036621 | -0.09613 | -0.064087 | -0.009155 | 0.53558 | 0.40741 | 0.10529 | 0.50354 | 0.20142 | 0.69122 | 121.4996 | 0.63171 | 121.6324 | 121.4859 | 121.5775 | 121.4264 | 121.4813 | -121.6049 | -121.6415 | 121.4401 | 121.5363 | 121.0327 | 110.0922
1759.8281 | 121.669 | -121.463 | 0.09613 | -0.013657 | -0.0009335 | 0.057753 | 0.056044 | -0.00085021 | -0.0047019 | -0.0014805 | -0.0051575 | 0.0023712 | 0.070656 | 0.055228 | -0.012014 | 0.021362 | 0.0002842 | -0.43945 | -0.027466 | -121.5363 | -0.059509 | -120.8771 | -121.6141 | -121.6003 | -11.5631 | 0.032043 | -121.5866 | 0.009155 | -121.0098 | -121.431 | -121.1243 | -0.073242 | -0.1236 | -0.15564 | 0.58594 | -0.13733 | -0.15106 | -0.064087 | -0.07782 | -0.1236 | -0.064087 | -0.086975 | 0.45319 | 0.33875 | 0.032044 | 0.46234 | 0.15564 | 0.65918 | 121.4767 | 0.57678 | 121.5958 | 121.5088 | 121.6187 | 121.4355 | 121.4951 | -121.6324 | -121.6827 | 121.4035 | 121.4722 | 121.0236 | 109.8999
1761.5156 | 121.6599 | -121.4905 | 0.1236 | -0.021286 | -0.0005063 | 0.056898 | 0.055189 | 0.0051312 | -0.0089743 | -0.0014805 | -0.0021057 | 0.0023712 | 0.07151 | 0.060996 | -0.014578 | 0.019867 | 0.0017794 | -0.32044 | -0.018311 | -121.5637 | -0.064087 | -120.8725 | -121.5729 | -121.6141 | -11.6547 | 0.045776 | -121.6049 | -0.027466 | -120.9869 | -121.4218 | -121.1517 | -0.073242 | -0.14191 | -0.18768 | 0.61798 | -0.1236 | -0.082397 | -0.050354 | -0.009155 | -0.11444 | -0.07782 | -0.15106 | 0.50354 | 0.33875 | 0.068665 | 0.45319 | 0.1831 | 0.69122 | 121.4996 | 0.61798 | 121.5775 | 121.5454 | 121.6507 | 121.4722 | 121.5363 | -121.6873 | -121.7285 | 121.4264 | 121.463 | 121.17 | 109.8358
1763.2188 | 121.6507 | -121.4996 | 0.10986 | -0.013657 | 0.0024845 | 0.058607 | 0.05818 | 0.0023542 | -0.0085471 | -0.0014805 | -0.0051575 | 0.0017304 | 0.069588 | 0.070609 | -0.012655 | 0.02243 | 0.0007114 | -0.37537 | -0.032043 | -121.5454 | -0.054932 | -120.8954 | -121.6141 | -121.6415 | -11.8561 | 0.059509 | -121.5912 | -0.032043 | -121.051 | -121.5088 | -121.1746 | -0.045776 | -0.14191 | -0.16479 | 0.60425 | -0.14191 | -0.11444 | -0.096131 | -0.068665 | -0.091553 | -0.050354 | -0.14191 | 0.44861 | 0.32501 | -0.009155 | 0.41657 | 0.082398 | 0.65002 | 121.4905 | 0.54016 | 121.5591 | 121.5134 | 121.6507 | 121.4676 | 121.5591 | -121.6553 | -121.7011 | 121.4447 | 121.4676 | 121.1243 | 109.6436
1764.9688 | 121.7606 | -121.4859 | 0.09613 | -0.021286 | -0.0007199 | 0.057112 | 0.05348 | -0.00020941 | -0.0068381 | -0.0012669 | -0.0082093 | -0.00061956 | 0.072578 | 0.059928 | -0.010732 | 0.019012 | -0.0039884 | -0.3891 | -0.064087 | -121.5408 | -0.009155 | -120.8496 | -121.5637 | -121.5408 | -11.9476 | 0.018311 | -121.5958 | 0.027466 | -120.9641 | -121.3715 | -121.0785 | -0.054932 | -0.16022 | -0.10528 | 0.63629 | -0.054932 | -0.07782 | 0 | -0.022888 | -0.10986 | -0.077819 | -0.068664 | 0.52185 | 0.40741 | 0.11444 | 0.51727 | 0.2243 | 0.69122 | 121.5317 | 0.63171 | 121.6232 | 121.4767 | 121.6141 | 121.4218 | 121.5042 | -121.637 | -121.6919 | 121.4767 | 121.5134 | 121.0968 | 109.5383
1766.7188 | 121.669 | -121.5271 | 0.12817 | -0.0060272 | -0.0002927 | 0.054976 | 0.054762 | 0.001286 | -0.0081197 | -0.0048985 | -0.0021057 | 0.0023712 | 0.070229 | 0.063132 | -0.012655 | 0.017303 | -0.0033474 | -0.34332 | -0.027466 | -121.6095 | -0.068665 | -120.9137 | -121.6095 | -121.6553 | -12.1216 | 0.036621 | -121.6003 | -0.045776 | -121.0556 | -121.4767 | -121.1609 | -0.082397 | -0.15564 | -0.19684 | 0.6134 | -0.12817 | -0.082397 | -0.045776 | 0 | -0.073242 | -0.091553 | -0.17395 | 0.4715 | 0.36621 | 0.050354 | 0.43945 | 0.1236 | 0.6958 | 121.5408 | 0.54474 | 121.5546 | 121.582 | 121.637 | 121.4996 | 121.5637 | -121.7377 | -121.7285 | 121.4584 | 121.4813 | 121.1838 | 109.4055
1768.4062 | 121.7239 | -121.5134 | 0.11902 | -0.013657 | -0.0002927 | 0.054976 | 0.056044 | 0.0021406 | -0.0079061 | -0.0025485 | -0.0051575 | 0.0049346 | 0.070656 | 0.067405 | -0.012655 | 0.021576 | -0.002493 | -0.31128 | -0.041199 | -121.5775 | 0.009155 | -120.8542 | -121.5912 | -121.582 | -12.2177 | 0.041199 | -121.5866 | 0.013733 | -121.0007 | -121.4493 | -121.1563 | -0.064087 | -0.16022 | -0.10986 | 0.65918 | -0.068664 | -0.07782 | -0.004577 | -0.013733 | -0.073242 | -0.07782 | -0.10529 | 0.5127 | 0.35706 | 0.064087 | 0.4303 | 0.13733 | 0.72327 | 121.5866 | 0.58594 | 121.6003 | 121.5363 | 121.6278 | 121.4722 | 121.5546 | -121.6965 | -121.7056 | 121.5225 | 121.5271 | 121.2021 | 109.2957
1770.1562 | 121.6782 | -121.5546 | 0.12817 | -0.013657 | 0.0039799 | 0.057967 | 0.05583 | 0.0014996 | -0.0068381 | -0.0066073 | 0.0009461 | 0.0023712 | 0.072578 | 0.064841 | -0.013082 | 0.020081 | -0.0029202 | -0.41199 | -0.036621 | -121.5866 | -0.091553 | -120.9686 | -121.6827 | -121.701 | -12.5565 | 0.059509 | -121.637 | -0.027466 | -121.0876 | -121.5179 | -121.2158 | -0.032044 | -0.1648 | -0.21973 | 0.58594 | -0.14648 | -0.12817 | -0.11444 | -0.09613 | -0.082398 | -0.068665 | -0.15564 | 0.46692 | 0.33875 | 0.036621 | 0.42114 | 0.11902 | 0.61798 | 121.4951 | 0.54932 | 121.6095 | 121.55 | 121.6965 | 121.5179 | 121.6141 | -121.7148 | -121.7651 | 121.463 | 121.5271 | 121.1426 | 108.9981
1771.9219 | 121.7331 | -121.5408 | 0.11444 | -0.013657 | -0.0002927 | 0.058607 | 0.055189 | -0.0040546 | -0.0076925 | -0.0036167 | -0.0082093 | 0.0015166 | 0.070015 | 0.062064 | -0.010732 | 0.020508 | -0.0029202 | -0.31128 | -0.027466 | -121.6095 | -0.032043 | -120.8954 | -121.5958 | -121.6278 | -12.5656 | 0.041199 | -121.6187 | 0.022888 | -121.0098 | -121.4539 | -121.1792 | -0.068664 | -0.14191 | -0.14648 | 0.64545 | -0.086975 | -0.054931 | -0.018311 | 0.013733 | -0.077819 | -0.073242 | -0.091553 | 0.53101 | 0.36163 | 0.086976 | 0.43945 | 0.16479 | 0.71411 | 121.5775 | 0.60882 | 121.6415 | 121.582 | 121.6599 | 121.5134 | 121.582 | -121.7239 | -121.7331 | 121.5088 | 121.5637 | 121.2296 | 108.9752
1773.6875 | 121.7102 | -121.5912 | 0.11902 | -0.0060272 | -0.0009335 | 0.055403 | 0.051985 | -0.0061908 | -0.0079061 | -0.0053257 | -0.0051575 | 0.0023712 | 0.070015 | 0.055228 | -0.013296 | 0.018372 | -0.0022794 | -0.31586 | -0.050354 | -121.6049 | -0.059509 | -120.9091 | -121.6232 | -121.6324 | -12.767 | 0.054932 | -121.6187 | -0.032043 | -121.0556 | -121.4859 | -121.2479 | -0.013732 | -0.16937 | -0.17853 | 0.68207 | -0.041198 | -0.032043 | -0.027466 | -0.018311 | -0.027465 | -0.064087 | -0.15106 | 0.53558 | 0.34332 | 0.10529 | 0.37079 | 0.13275 | 0.6958 | 121.5454 | 0.56305 | 121.5866 | 121.5546 | 121.6736 | 121.5408 | 121.6461 | -121.7239 | -121.7377 | 121.5317 | 121.5591 | 121.2753 | 108.8242
1775.375 | 121.843 | -121.5179 | 0.082397 | -0.0060272 | -0.0047787 | 0.055403 | 0.05284 | -0.0025592 | -0.0089743 | -0.0021213 | -0.0021057 | 2.1442e-05 | 0.069374 | 0.058005 | -0.011373 | 0.019653 | -0.0027066 | -0.28839 | -0.064087 | -121.5454 | 0.068665 | -120.7489 | -121.5042 | -121.5225 | -12.7533 | -0.004578 | -121.6049 | 0.091553 | -120.9045 | -121.3531 | -121.1151 | -0.027466 | -0.14648 | -0.013732 | 0.76904 | -0.004578 | 0.013733 | 0.022888 | 0.041199 | -0.086975 | -0.086975 | 0.009156 | 0.6134 | 0.40283 | 0.16479 | 0.48981 | 0.25177 | 0.79651 | 121.6141 | 0.70038 | 121.6965 | 121.4813 | 121.6003 | 121.4539 | 121.5134 | -121.6278 | -121.6873 | 121.5866 | 121.6095 | 121.2296 | 108.7646
1777.125 | 121.843 | -121.5225 | 0.082397 | -0.013657 | -0.0009335 | 0.057112 | 0.052626 | 0.0019268 | -0.0072653 | -0.0031895 | -0.0082093 | 2.1442e-05 | 0.071297 | 0.059287 | -0.015005 | 0.019012 | -0.0037748 | -0.34332 | -0.07782 | -121.582 | 0.050354 | -120.813 | -121.5179 | -121.5408 | -12.9547 | 0.018311 | -121.6187 | 0.10071 | -120.932 | -121.3577 | -121.1105 | -0.059509 | -0.16022 | -0.032043 | 0.70953 | -0.018311 | 0.004578 | 0.041198 | 0.064087 | -0.09613 | -0.064086 | 0.018311 | 0.59051 | 0.41199 | 0.16479 | 0.50812 | 0.26093 | 0.76904 | 121.6324 | 0.68664 | 121.7194 | 121.5042 | 121.637 | 121.4447 | 121.5408 | -121.6644 | -121.701 | 121.5729 | 121.6232 | 121.1792 | 108.5678
1778.875 | 121.8521 | -121.5271 | 0.059509 | -0.013657 | -0.0039243 | 0.056044 | 0.053694 | -0.0012774 | -0.0064109 | -0.0023349 | -0.0051575 | 0.0015166 | 0.06916 | 0.057578 | -0.01351 | 0.019653 | -0.0031338 | -0.33875 | -0.068665 | -121.582 | 0.059509 | -120.8313 | -121.5363 | -121.5363 | -13.1104 | 0.009155 | -121.6415 | 0.086975 | -120.9366 | -121.3623 | -121.1014 | -0.054931 | -0.12817 | 0 | 0.6958 | -0.009155 | -0.009155 | 0.045776 | 0.045776 | -0.11444 | -0.050354 | 0.027466 | 0.59052 | 0.42572 | 0.16479 | 0.54016 | 0.27924 | 0.75073 | 121.6415 | 0.70496 | 121.7285 | 121.5134 | 121.6507 | 121.4584 | 121.5363 | -121.6415 | -121.7011 | 121.5866 | 121.6141 | 121.1884 | 108.4167
1780.625 | 121.7651 | -121.5683 | 0.09613 | -0.0060272 | 0.0029117 | 0.056258 | 0.057112 | -0.003841 | -0.0083335 | -0.0063937 | -0.0021057 | 0.0025848 | 0.070869 | 0.063346 | -0.01415 | 0.020508 | 0.0004978 | -0.31128 | -0.032043 | -121.6278 | -0.004578 | -120.9183 | -121.6461 | -121.6461 | -13.3713 | 0.036621 | -121.6553 | 0.018311 | -121.0373 | -121.4951 | -121.1746 | -0.05951 | -0.12817 | -0.10071 | 0.65002 | -0.07782 | -0.07782 | -0.01831 | -0.01831 | -0.086975 | -0.059509 | -0.077819 | 0.53101 | 0.39368 | 0.073242 | 0.48065 | 0.16022 | 0.70953 | 121.6232 | 0.61798 | 121.6736 | 121.5958 | 121.6919 | 121.5363 | 121.6049 | -121.7239 | -121.7514 | 121.5637 | 121.5866 | 121.257 | 108.197
1782.3281 | 121.7606 | -121.5866 | 0.10071 | -0.021286 | 0.0016299 | 0.059889 | 0.057753 | -0.001491 | -0.0068381 | -0.0040439 | -0.0051575 | 0.0021576 | 0.071724 | 0.063559 | -0.013082 | 0.020294 | -0.0065518 | -0.45319 | -0.041199 | -121.6461 | -0.059509 | -120.9869 | -121.7056 | -121.7148 | -13.6459 | 0.050354 | -121.6644 | -0.009155 | -121.1197 | -121.5637 | -121.1746 | -0.059509 | -0.14191 | -0.16022 | 0.59967 | -0.12817 | -0.11902 | -0.068665 | -0.059509 | -0.07782 | -0.050354 | -0.10986 | 0.46692 | 0.41199 | 0.022888 | 0.48981 | 0.10071 | 0.65918 | 121.5866 | 0.54474 | 121.6553 | 121.6049 | 121.7148 | 121.5454 | 121.637 | -121.7468 | -121.7651 | 121.5271 | 121.5775 | 121.1334 | 107.9407
1784.0938 | 121.8155 | -121.5958 | 0.086975 | -0.013657 | -0.0015743 | 0.055403 | 0.05284 | -0.001491 | -0.0051291 | -0.0025485 | -0.0082093 | -0.0012604 | 0.070656 | 0.056937 | -0.011587 | 0.022217 | -0.0027066 | -0.42572 | -0.064087 | -121.6141 | -0.004578 | -120.9229 | -121.637 | -121.637 | -13.7878 | 0.018311 | -121.6644 | 0.032043 | -121.0464 | -121.4584 | -121.1105 | -0.018311 | -0.15106 | -0.091553 | 0.67291 | -0.041199 | -0.041199 | -0.022888 | -0.022888 | -0.068665 | -0.068664 | -0.054932 | 0.54932 | 0.48523 | 0.13733 | 0.55389 | 0.20599 | 0.69122 | 121.6095 | 0.61798 | 121.6965 | 121.55 | 121.6827 | 121.5317 | 121.6141 | -121.701 | -121.7514 | 121.5912 | 121.6278 | 121.17 | 107.8079
1785.8438 | 121.7377 | -121.6003 | 0.10986 | -0.028916 | 0.0026981 | 0.056258 | 0.056685 | -0.00063661 | -0.0061971 | -0.0051121 | -0.0021057 | 0.0045074 | 0.072792 | 0.062705 | -0.012869 | 0.021362 | -0.003561 | -0.40741 | -0.022888 | -121.6507 | -0.059509 | -121.0007 | -121.7422 | -121.7285 | -14.0259 | 0.032043 | -121.6873 | -0.022888 | -121.1517 | -121.5866 | -121.1884 | -0.050354 | -0.13275 | -0.16937 | 0.59967 | -0.12817 | -0.14191 | -0.07782 | -0.091553 | -0.086975 | -0.07782 | -0.13275 | 0.44861 | 0.41199 | 0.013733 | 0.49896 | 0.10071 | 0.65002 | 121.5912 | 0.53558 | 121.6644 | 121.6278 | 121.7194 | 121.5775 | 121.6324 | -121.7606 | -121.7972 | 121.5408 | 121.5775 | 121.1929 | 107.5745
1787.6094 | 121.7514 | -121.5958 | 0.10529 | -0.013657 | 0.0033389 | 0.057967 | 0.057326 | -0.00063661 | -0.0064109 | -0.0034031 | -0.011261 | 0.001944 | 0.070229 | 0.066764 | -0.013723 | 0.020081 | -0.0044156 | -0.35706 | -0.032043 | -121.6278 | -0.022888 | -120.9549 | -121.6873 | -121.6965 | -14.1403 | 0.036621 | -121.701 | 0 | -121.1105 | -121.5729 | -121.17 | -0.032044 | -0.13733 | -0.12817 | 0.64087 | -0.10071 | -0.091553 | -0.068664 | -0.059509 | -0.10529 | -0.068665 | -0.10529 | 0.48523 | 0.42572 | 0.022888 | 0.53101 | 0.12817 | 0.67291 | 121.6049 | 0.59051 | 121.701 | 121.5958 | 121.7377 | 121.5637 | 121.6324 | -121.7331 | -121.8063 | 121.5729 | 121.5958 | 121.2387 | 107.4554
1789.3125 | 121.7926 | -121.6049 | 0.11902 | -0.0060272 | -0.0005063 | 0.057967 | 0.056044 | -0.0034136 | -0.0072653 | -0.0029759 | -0.0051575 | -0.00040596 | 0.070656 | 0.061423 | -0.012869 | 0.01944 | -0.00527 | -0.3479 | -0.032043 | -121.7056 | -0.064087 | -121.0052 | -121.6873 | -121.7148 | -14.3372 | 0.032043 | -121.701 | -0.032043 | -121.0831 | -121.5454 | -121.1655 | -0.10071 | -0.15106 | -0.18311 | 0.59967 | -0.10986 | -0.082398 | -0.009156 | 0.01831 | -0.096131 | -0.086976 | -0.15106 | 0.52185 | 0.43945 | 0.059509 | 0.53558 | 0.15564 | 0.70038 | 121.6415 | 0.61798 | 121.669 | 121.6736 | 121.7331 | 121.5729 | 121.637 | -121.8246 | -121.8201 | 121.5408 | 121.5729 | 121.257 | 107.2678
1791.0625 | 121.907 | -121.5775 | 0.086975 | -0.021286 | -7.9104e-05 | 0.057326 | 0.052626 | -0.001491 | -0.0064109 | 0.00044213 | -0.0051575 | -0.0019012 | 0.070869 | 0.05181 | -0.011373 | 0.020935 | 0.0013522 | -0.37994 | -0.059509 | -121.6232 | 0.054932 | -120.8679 | -121.5729 | -121.5958 | -14.3829 | 0.013733 | -121.6782 | 0.09613 | -120.9641 | -121.4127 | -121.0876 | -0.045776 | -0.14648 | -0.032043 | 0.70953 | -0.01831 | 0.004578 | 0.027466 | 0.050354 | -0.10071 | -0.073242 | 0.009155 | 0.6134 | 0.48981 | 0.16479 | 0.59052 | 0.2655 | 0.75531 | 121.6782 | 0.71411 | 121.7743 | 121.5637 | 121.6919 | 121.5179 | 121.5912 | -121.7102 | -121.7651 | 121.6324 | 121.6736 | 121.1975 | 107.1945
1792.75 | 121.8063 | -121.6141 | 0.086975 | -0.0060272 | 0.0014163 | 0.057112 | 0.055617 | -0.00085021 | -0.0061971 | -0.0042575 | -0.0021057 | 0.0010894 | 0.072365 | 0.064627 | -0.012014 | 0.020294 | -0.0005704 | -0.35706 | -0.027466 | -121.6644 | 0 | -120.9457 | -121.669 | -121.6965 | -14.6805 | 0.045776 | -121.6827 | 0.018311 | -121.0922 | -121.5546 | -121.17 | -0.050354 | -0.11444 | -0.086975 | 0.66833 | -0.082397 | -0.054931 | -0.032043 | -0.004577 | -0.068664 | -0.041199 | -0.068664 | 0.52185 | 0.44403 | 0.05951 | 0.51269 | 0.12817 | 0.71869 | 121.6644 | 0.59051 | 121.701 | 121.637 | 121.7285 | 121.5866 | 121.6599 | -121.7514 | -121.7697 | 121.6141 | 121.6324 | 121.257 | 106.9336
1794.4531 | 121.9116 | -121.5866 | 0.068665 | -0.013657 | 0.0009891 | 0.056685 | 0.054549 | -0.0025592 | -0.0079061 | -0.0016941 | -0.0082093 | 0.0027984 | 0.071297 | 0.057151 | -0.014791 | 0.019653 | -0.0012112 | -0.46692 | -0.032043 | -121.6599 | 0.032043 | -120.9091 | -121.6507 | -121.6507 | -14.9094 | 0.013733 | -121.669 | 0.10986 | -121.0052 | -121.4722 | -121.1655 | -0.073242 | -0.10071 | -0.036622 | 0.67749 | -0.064087 | -0.064087 | 0.009155 | 0.009155 | -0.082397 | -0.054932 | 0.041198 | 0.58136 | 0.42114 | 0.11444 | 0.50354 | 0.19684 | 0.75073 | 121.6919 | 0.66376 | 121.7789 | 121.6278 | 121.6827 | 121.5546 | 121.6003 | -121.7285 | -121.7377 | 121.6187 | 121.6965 | 121.1197 | 106.6772
1796.2031 | 121.843 | -121.6095 | 0.07782 | -0.021286 | -0.0017881 | 0.056044 | 0.052626 | 0.0025678 | -0.0074789 | -0.0048985 | -0.0051575 | 0.00066224 | 0.072365 | 0.053519 | -0.0092371 | 0.018585 | 0.0004978 | -0.43945 | -0.068665 | -121.6461 | 0.022888 | -120.9183 | -121.6644 | -121.6507 | -15.1199 | 0.022888 | -121.7056 | 0.050354 | -121.0373 | -121.4996 | -121.1563 | -0.036621 | -0.14649 | -0.054932 | 0.69122 | -0.041199 | -0.054932 | -0.004578 | -0.018311 | -0.09613 | -0.054932 | -0.027466 | 0.57221 | 0.45319 | 0.10986 | 0.54932 | 0.20599 | 0.72784 | 121.669 | 0.66834 | 121.756 | 121.5775 | 121.7285 | 121.5408 | 121.6324 | -121.7239 | -121.7834 | 121.6324 | 121.6599 | 121.17 | 106.4896
1797.9688 | 121.907 | -121.5958 | 0.068665 | -0.0060272 | 0.0022709 | 0.058394 | 0.053694 | -0.00063661 | -0.0085471 | -0.00062587 | -0.0051575 | 0.0010894 | 0.069801 | 0.062064 | -0.012014 | 0.022003 | -0.0044156 | -0.41657 | -0.064087 | -121.6553 | 0.054932 | -120.8817 | -121.6415 | -121.6324 | -15.3259 | -0.004578 | -121.6827 | 0.10071 | -121.019 | -121.4539 | -121.0922 | -0.059509 | -0.13275 | -0.013733 | 0.71411 | -0.036621 | -0.045777 | 0.022888 | 0.013732 | -0.086975 | -0.073243 | 0.032043 | 0.57678 | 0.50354 | 0.14191 | 0.59051 | 0.22888 | 0.77362 | 121.7102 | 0.66376 | 121.7834 | 121.5912 | 121.6782 | 121.5317 | 121.5912 | -121.7239 | -121.7514 | 121.6507 | 121.6965 | 121.1792 | 106.2698
1799.7188 | 121.9116 | -121.582 | 0.082397 | -0.013657 | -0.0024289 | 0.053267 | 0.053694 | -0.0019184 | -0.0064109 | -0.0038303 | -0.0082093 | -0.0010468 | 0.071724 | 0.059073 | -0.012014 | 0.017731 | -0.0044156 | -0.32501 | -0.050354 | -121.6736 | 0.073242 | -120.845 | -121.5729 | -121.5866 | -15.4587 | 0.013733 | -121.6827 | 0.07782 | -120.9869 | -121.431 | -121.138 | -0.091553 | -0.13275 | -0.009155 | 0.737 | -0.004578 | 0.009155 | 0.086975 | 0.10071 | -0.10071 | -0.068664 | -0.004577 | 0.59509 | 0.44403 | 0.15106 | 0.54474 | 0.25177 | 0.82855 | 121.7468 | 0.6958 | 121.7606 | 121.6232 | 121.6965 | 121.5317 | 121.5958 | -121.756 | -121.7651 | 121.6553 | 121.6599 | 121.257 | 106.1234
1801.4531 | 121.7651 | -121.6644 | 0.10529 | -0.021286 | 0.0020571 | 0.057112 | 0.057326 | -0.0044818 | -0.0055563 | -0.0046847 | -0.011261 | 0.0027984 | 0.072151 | 0.065055 | -0.01351 | 0.019653 | -0.0050564 | -0.46692 | -0.032043 | -121.7056 | -0.09613 | -121.1105 | -121.8155 | -121.8063 | -15.9348 | 0.059509 | -121.7285 | -0.018311 | -121.1792 | -121.637 | -121.2845 | -0.041198 | -0.13733 | -0.20142 | 0.55389 | -0.14191 | -0.15106 | -0.10071 | -0.10986 | -0.064087 | -0.045777 | -0.1236 | 0.48523 | 0.37994 | 0.027466 | 0.44403 | 0.091553 | 0.59509 | 121.6095 | 0.54932 | 121.7102 | 121.6736 | 121.788 | 121.6324 | 121.7239 | -121.8109 | -121.8338 | 121.5683 | 121.6461 | 121.1975 | 105.7297
1803.1406 | 121.9254 | -121.6049 | 0.068665 | -0.021286 | 0.0018435 | 0.057753 | 0.055403 | 0.0042768 | -0.0068381 | -0.0025485 | -0.011261 | -0.00040596 | 0.070442 | 0.056296 | -0.013723 | 0.021149 | 0.0007114 | -0.41199 | -0.059509 | -121.6782 | 0.064087 | -120.9137 | -121.6507 | -121.637 | -15.9851 | 0 | -121.7194 | 0.11444 | -121.0052 | -121.4676 | -121.1426 | -0.073243 | -0.12817 | -0.004578 | 0.69122 | -0.032044 | -0.045777 | 0.041199 | 0.027466 | -0.11444 | -0.068665 | 0.045776 | 0.59967 | 0.46234 | 0.13733 | 0.57678 | 0.25177 | 0.76447 | 121.7422 | 0.71411 | 121.8338 | 121.6187 | 121.7194 | 121.5454 | 121.6049 | -121.7468 | -121.788 | 121.669 | 121.7194 | 121.1929 | 105.6198
1804.8906 | 121.8887 | -121.6461 | 0.082397 | -0.013657 | 0.0018435 | 0.057326 | 0.056258 | 0.00085879 | -0.0066245 | -0.0036167 | -0.0051575 | 0.0010894 | 0.072578 | 0.065268 | -0.012014 | 0.019226 | -0.0037748 | -0.45319 | -0.068665 | -121.669 | 0.027466 | -120.932 | -121.6873 | -121.6919 | -16.2827 | 0.009155 | -121.701 | 0.054932 | -121.0648 | -121.5317 | -121.2112 | -0.022888 | -0.15106 | -0.054931 | 0.71411 | -0.045777 | -0.041199 | -0.022889 | -0.018311 | -0.054932 | -0.073242 | -0.027465 | 0.58136 | 0.43488 | 0.11444 | 0.48981 | 0.16937 | 0.737 | 121.6965 | 0.63629 | 121.756 | 121.6003 | 121.7102 | 121.5775 | 121.6553 | -121.7514 | -121.7834 | 121.6736 | 121.701 | 121.1929 | 105.3635
1806.6406 | 121.7972 | -121.6782 | 0.11444 | -0.021286 | 0.0022709 | 0.056044 | 0.058607 | 0.00085879 | -0.0083335 | -0.0019077 | -0.0021057 | 0.003653 | 0.070442 | 0.062278 | -0.012441 | 0.020294 | -0.002493 | -0.50812 | -0.032043 | -121.7377 | -0.082397 | -121.1197 | -121.8384 | -121.8018 | -16.6534 | 0.036621 | -121.7514 | -0.032043 | -121.1792 | -121.6461 | -121.2662 | -0.059509 | -0.14648 | -0.19684 | 0.55847 | -0.1236 | -0.16022 | -0.064087 | -0.10071 | -0.073242 | -0.07782 | -0.14648 | 0.49896 | 0.41199 | 0.032044 | 0.48523 | 0.10529 | 0.61798 | 121.6553 | 0.5722 | 121.7194 | 121.7056 | 121.788 | 121.6461 | 121.7148 | -121.8521 | -121.8658 | 121.5958 | 121.6461 | 121.17 | 105.0247
1808.3906 | 121.8063 | -121.6827 | 0.11902 | -0.028916 | 0.0033389 | 0.060316 | 0.059035 | 0.00021799 | -0.0085471 | -0.0038303 | -0.0051575 | 0.003012 | 0.074074 | 0.059287 | -0.012228 | 0.019653 | -0.0014248 | -0.4715 | -0.050354 | -121.7285 | -0.082397 | -121.106 | -121.8109 | -121.8246 | -16.9144 | 0.045776 | -121.7514 | -0.022888 | -121.1792 | -121.6461 | -121.2845 | -0.045777 | -0.16937 | -0.20142 | 0.57678 | -0.14191 | -0.12817 | -0.09613 | -0.082397 | -0.068665 | -0.073243 | -0.14191 | 0.50354 | 0.39825 | 0.036621 | 0.46692 | 0.10529 | 0.62256 | 121.6461 | 0.5722 | 121.7285 | 121.6782 | 121.7972 | 121.6324 | 121.7285 | -121.8475 | -121.8704 | 121.6003 | 121.6599 | 121.2112 | 104.7684
1810.0781 | 121.9391 | -121.6141 | 0.073242 | -0.021286 | 0.0009891 | 0.059248 | 0.055189 | -0.0010638 | -0.0061971 | -0.0031895 | -0.0051575 | 0.00044864 | 0.071297 | 0.063987 | -0.012228 | 0.019226 | -0.005911 | -0.44403 | -0.054932 | -121.6873 | 0.054932 | -120.9366 | -121.6873 | -121.6644 | -16.9876 | 0.018311 | -121.7285 | 0.11902 | -121.0419 | -121.4951 | -121.1838 | -0.073242 | -0.12817 | -0.01831 | 0.67749 | -0.050354 | -0.073242 | 0.022888 | 0 | -0.11444 | -0.054931 | 0.045777 | 0.5722 | 0.4303 | 0.11902 | 0.54474 | 0.23346 | 0.75073 | 121.7422 | 0.68665 | 121.8475 | 121.6324 | 121.7468 | 121.5591 | 121.6324 | -121.7606 | -121.8018 | 121.669 | 121.7331 | 121.17 | 104.6265
1811.8281 | 121.8796 | -121.637 | 0.10529 | 0.0016023 | -0.0013607 | 0.05583 | 0.052412 | -0.002132 | -0.0089743 | -0.0038303 | -0.0051575 | 0.00023504 | 0.071297 | 0.057578 | -0.010519 | 0.018799 | -0.0012112 | -0.33875 | -0.068665 | -121.7194 | 0.036621 | -120.9503 | -121.6507 | -121.6873 | -17.2302 | 0.027466 | -121.7606 | 0.032043 | -121.0739 | -121.5454 | -121.2936 | -0.082397 | -0.17395 | -0.068665 | 0.68665 | -0.050354 | -0.013733 | 0.032043 | 0.068664 | -0.1236 | -0.07782 | -0.073243 | 0.56305 | 0.34332 | 0.091553 | 0.46692 | 0.21515 | 0.76904 | 121.756 | 0.68664 | 121.7926 | 121.6507 | 121.788 | 121.5683 | 121.6644 | -121.8246 | -121.8658 | 121.6736 | 121.669 | 121.2982 | 104.4067
1813.5938 | 121.8246 | -121.6827 | 0.11902 | -0.013657 | 0.0005619 | 0.058821 | 0.057539 | -0.0010638 | -0.0068381 | -0.0012669 | -0.0051575 | 0.0038666 | 0.072365 | 0.060141 | -0.012655 | 0.022217 | 0.0002842 | -0.43945 | -0.041199 | -121.7377 | -0.041199 | -121.0602 | -121.7651 | -121.7789 | -17.6376 | 0.064087 | -121.7377 | 0 | -121.1655 | -121.6599 | -121.3623 | -0.054932 | -0.16022 | -0.16022 | 0.62256 | -0.096131 | -0.082398 | -0.041199 | -0.027466 | -0.054932 | -0.054932 | -0.11902 | 0.51727 | 0.32043 | 0.022888 | 0.37537 | 0.07782 | 0.67749 | 121.6965 | 0.57221 | 121.7377 | 121.6965 | 121.8018 | 121.6415 | 121.7468 | -121.8567 | -121.8567 | 121.6415 | 121.6827 | 121.2433 | 104.0451
1815.2812 | 121.8475 | -121.6827 | 0.086975 | -0.0060272 | -0.0009335 | 0.058607 | 0.055403 | 0.001286 | -0.0089743 | -0.0029759 | -0.0051575 | 0.001303 | 0.069588 | 0.069968 | -0.013082 | 0.020294 | -0.0029202 | -0.41199 | -0.027466 | -121.756 | -0.027466 | -121.0373 | -121.7651 | -121.7789 | -17.8528 | 0.054932 | -121.7468 | 0.013733 | -121.1426 | -121.6415 | -121.3394 | -0.073242 | -0.11444 | -0.11444 | 0.64545 | -0.096131 | -0.082398 | -0.022889 | -0.009156 | -0.064087 | -0.032043 | -0.073242 | 0.54016 | 0.34332 | 0.041198 | 0.40741 | 0.10528 | 0.71869 | 121.7285 | 0.60425 | 121.7606 | 121.7285 | 121.8018 | 121.6553 | 121.7377 | -121.843 | -121.8338 | 121.6553 | 121.6965 | 121.2708 | 103.83
1817.0312 | 121.9254 | -121.6827 | 0.091553 | -0.0060272 | -0.0020017 | 0.057967 | 0.053908 | -0.0061908 | -0.0053427 | -0.0040439 | -0.0082093 | 0.00023504 | 0.070442 | 0.060996 | -0.012441 | 0.019653 | -0.0029202 | -0.47607 | -0.059509 | -121.6965 | 0.013733 | -120.9641 | -121.7194 | -121.7239 | -18.1412 | 0.004578 | -121.7514 | 0.054932 | -121.0739 | -121.5454 | -121.2936 | -0.013733 | -0.15106 | -0.07782 | 0.71869 | -0.041199 | -0.036621 | -0.027466 | -0.022888 | -0.068665 | -0.086975 | -0.036621 | 0.60882 | 0.3891 | 0.13733 | 0.45776 | 0.20599 | 0.73242 | 121.7102 | 0.67749 | 121.8063 | 121.637 | 121.756 | 121.6232 | 121.6873 | -121.788 | -121.843 | 121.6965 | 121.7377 | 121.2067 | 103.5416
1818.7812 | 121.8842 | -121.6599 | 0.09613 | -0.013657 | 0.0031253 | 0.057112 | 0.057112 | 0.0068402 | -0.0085471 | -0.0016941 | -0.0021057 | 0.0038666 | 0.070656 | 0.062491 | -0.012014 | 0.021149 | -0.0005704 | -0.39368 | -0.022888 | -121.7331 | 0.004578 | -121.0236 | -121.7422 | -121.756 | -18.4204 | 0.045776 | -121.7468 | 0.022888 | -121.1151 | -121.6049 | -121.3348 | -0.073242 | -0.11902 | -0.091552 | 0.63629 | -0.09613 | -0.082398 | -0.022888 | -0.009156 | -0.086975 | -0.050354 | -0.073242 | 0.54474 | 0.32501 | 0.054932 | 0.41199 | 0.14191 | 0.70953 | 121.7377 | 0.63171 | 121.7697 | 121.7102 | 121.7926 | 121.637 | 121.7056 | -121.8292 | -121.843 | 121.6644 | 121.6827 | 121.2662 | 103.2394
1820.5312 | 121.9757 | -121.6507 | 0.07782 | 0.0016023 | 0.0001345 | 0.056685 | 0.054121 | -0.0068316 | -0.0091879 | -0.0063937 | -0.0082093 | 0.0017304 | 0.070442 | 0.048819 | -0.012869 | 0.020294 | -0.0048428 | -0.37537 | -0.073242 | -121.7148 | 0.054932 | -120.9229 | -121.6461 | -121.6736 | -18.6447 | 0.009155 | -121.756 | 0.091553 | -121.019 | -121.5042 | -121.2662 | -0.064087 | -0.15106 | -0.022888 | 0.72784 | -0.022888 | 0.004578 | 0.041199 | 0.068665 | -0.10529 | -0.068665 | 0.013733 | 0.63171 | 0.38452 | 0.14648 | 0.48981 | 0.25177 | 0.79193 | 121.7697 | 0.737 | 121.8475 | 121.6415 | 121.7651 | 121.5775 | 121.6599 | -121.7926 | -121.8338 | 121.7056 | 121.7422 | 121.2753 | 103.006
1822.2188 | 121.9345 | -121.6644 | 0.082397 | -0.0060272 | -0.0011471 | 0.057539 | 0.05049 | -0.0042682 | -0.0057699 | -0.0051121 | -0.0021057 | -0.00019216 | 0.071297 | 0.061423 | -0.013723 | 0.020721 | -0.003561 | -0.36163 | -0.073242 | -121.7377 | 0.068665 | -120.9412 | -121.669 | -121.6782 | -18.9514 | 0.013733 | -121.7514 | 0.064087 | -121.0281 | -121.5179 | -121.2799 | -0.073242 | -0.15564 | -0.013732 | 0.72327 | -0.013733 | -0.004577 | 0.059509 | 0.068665 | -0.086975 | -0.068664 | -0.01831 | 0.63629 | 0.38452 | 0.14648 | 0.4715 | 0.23346 | 0.79651 | 121.8063 | 0.72327 | 121.8155 | 121.6644 | 121.7651 | 121.5912 | 121.6782 | -121.8201 | -121.8338 | 121.7331 | 121.7285 | 121.3028 | 102.713
1823.9688 | 122.0078 | -121.669 | 0.082397 | -0.021286 | -0.0028561 | 0.05818 | 0.053053 | -0.002132 | -0.0053427 | -0.0038303 | -0.0021057 | 2.1442e-05 | 0.072151 | 0.057578 | -0.013723 | 0.018799 | -0.0016384 | -0.40741 | -0.068665 | -121.7422 | 0.059509 | -120.9457 | -121.6782 | -121.6919 | -19.2764 | 0.009155 | -121.7422 | 0.10529 | -121.0098 | -121.4905 | -121.2616 | -0.073243 | -0.15106 | -0.022888 | 0.72327 | -0.022889 | -0.009156 | 0.050354 | 0.064087 | -0.073243 | -0.073242 | 0.022889 | 0.65918 | 0.40741 | 0.17853 | 0.48065 | 0.25177 | 0.79651 | 121.8018 | 0.73242 | 121.8475 | 121.6736 | 121.7514 | 121.6003 | 121.6782 | -121.8246 | -121.8246 | 121.7285 | 121.7743 | 121.2616 | 102.3926
1825.7188 | 121.9025 | -121.6873 | 0.09613 | -0.013657 | 0.0003483 | 0.059035 | 0.055617 | 0.00085879 | -0.0059835 | -0.0021213 | -0.0082093 | 0.0025848 | 0.070015 | 0.063559 | -0.013723 | 0.021149 | -0.0037748 | -0.39825 | -0.045776 | -121.7789 | 0 | -121.0464 | -121.7606 | -121.7926 | -19.6884 | 0.050354 | -121.7697 | 0.036621 | -121.1288 | -121.6187 | -121.344 | -0.091553 | -0.14191 | -0.09613 | 0.64087 | -0.10529 | -0.073242 | -0.013733 | 0.018311 | -0.082397 | -0.045776 | -0.059509 | 0.55847 | 0.34332 | 0.068665 | 0.42572 | 0.15106 | 0.73242 | 121.7789 | 0.64087 | 121.8063 | 121.7331 | 121.8201 | 121.6415 | 121.7377 | -121.875 | -121.8658 | 121.6873 | 121.7239 | 121.2891 | 101.9989
1827.4062 | 121.8613 | -121.7102 | 0.1236 | -0.013657 | -0.0015743 | 0.054121 | 0.054976 | 0.00085879 | -0.0070517 | -0.0027621 | -0.0082093 | 0.0027984 | 0.072792 | 0.060782 | -0.012228 | 0.021576 | -0.004202 | -0.45319 | -0.013733 | -121.7972 | -0.082397 | -121.1151 | -121.8063 | -121.8292 | -20.0912 | 0.054932 | -121.8201 | -0.059509 | -121.1746 | -121.669 | -121.4035 | -0.086975 | -0.13733 | -0.20599 | 0.59509 | -0.11902 | -0.09613 | -0.032044 | -0.009155 | -0.10986 | -0.068664 | -0.1831 | 0.53558 | 0.3067 | 0.041199 | 0.41657 | 0.15106 | 0.68207 | 121.7148 | 0.64545 | 121.7606 | 121.7834 | 121.875 | 121.6965 | 121.7651 | -121.9208 | -121.9437 | 121.6278 | 121.6507 | 121.257 | 101.619
1829.1562 | 121.9757 | -121.6736 | 0.068665 | -0.0060272 | 0.0022709 | 0.058821 | 0.054121 | -0.0025592 | -0.0081197 | -0.0023349 | -0.011261 | 0.0017304 | 0.072151 | 0.060141 | -0.010732 | 0.019867 | -0.0037748 | -0.49439 | -0.07782 | -121.7468 | 0.059509 | -120.9732 | -121.7148 | -121.7148 | -20.3476 | 0.018311 | -121.788 | 0.10529 | -121.0602 | -121.5454 | -121.2524 | -0.073242 | -0.14649 | -0.009156 | 0.70038 | -0.041199 | -0.041199 | 0.032043 | 0.032043 | -0.11444 | -0.050354 | 0.036621 | 0.6134 | 0.42114 | 0.12817 | 0.53558 | 0.24262 | 0.77362 | 121.8063 | 0.72784 | 121.8933 | 121.669 | 121.8063 | 121.5958 | 121.6919 | -121.8155 | -121.8567 | 121.7331 | 121.7789 | 121.1792 | 101.326
1830.8438 | 122.0078 | -121.6919 | 0.082397 | -0.021286 | 0.0035525 | 0.056471 | 0.05583 | 0.0021406 | -0.0076925 | -0.0021213 | -0.0082093 | -0.0016876 | 0.070015 | 0.060141 | -0.015432 | 0.02179 | -0.0003568 | -0.48981 | -0.068665 | -121.7194 | 0.064087 | -120.9961 | -121.7239 | -121.7148 | -20.668 | 0.004578 | -121.7789 | 0.10071 | -121.0602 | -121.5546 | -121.2112 | -0.027465 | -0.15106 | -0.01831 | 0.6958 | -0.022888 | -0.032043 | 0.004577 | -0.004578 | -0.086975 | -0.077819 | 0.018311 | 0.63171 | 0.48065 | 0.13733 | 0.56763 | 0.22431 | 0.72327 | 121.7834 | 0.71869 | 121.8796 | 121.6507 | 121.7834 | 121.6232 | 121.6965 | -121.8018 | -121.8613 | 121.756 | 121.7926 | 121.2021 | 101.0239
1832.5938 | 121.994 | -121.6965 | 0.073242 | -0.021286 | -0.0034971 | 0.054762 | 0.053908 | -0.0046954 | -0.0087607 | -0.0014805 | -0.0051575 | -0.00019216 | 0.070015 | 0.062491 | -0.013937 | 0.020294 | -0.0022794 | -0.39825 | -0.064087 | -121.7743 | 0.064087 | -120.9457 | -121.6553 | -121.6827 | -20.9427 | 0.013733 | -121.7789 | 0.082397 | -121.0327 | -121.5317 | -121.225 | -0.07782 | -0.13733 | -0.009155 | 0.75073 | 0.013733 | 0.041199 | 0.091553 | 0.11902 | -0.082398 | -0.059509 | 0.009155 | 0.66376 | 0.4715 | 0.16479 | 0.55389 | 0.24719 | 0.82855 | 121.8384 | 0.74616 | 121.8613 | 121.7102 | 121.7926 | 121.6324 | 121.7102 | -121.8475 | -121.8521 | 121.7606 | 121.7789 | 121.2982 | 100.7538
1834.3594 | 121.8521 | -121.7194 | 0.10986 | -0.013657 | 0.0007755 | 0.059035 | 0.055617 | 0.0023542 | -0.0076925 | -0.0010531 | -0.0051575 | 0.0027984 | 0.070869 | 0.063987 | -0.012869 | 0.021149 | -0.0029202 | -0.50812 | -0.022888 | -121.7926 | -0.073242 | -121.1563 | -121.8613 | -121.8613 | -21.5469 | 0.059509 | -121.8018 | -0.041199 | -121.2112 | -121.7377 | -121.3623 | -0.073243 | -0.13275 | -0.18311 | 0.56305 | -0.14191 | -0.14191 | -0.068664 | -0.068664 | -0.082398 | -0.050354 | -0.15106 | 0.50812 | 0.35705 | -0.018311 | 0.43945 | 0.064087 | 0.63629 | 121.7194 | 0.59052 | 121.7606 | 121.7697 | 121.8613 | 121.6965 | 121.7789 | -121.9025 | -121.9116 | 121.6461 | 121.6782 | 121.2112 | 100.1724
1836.0469 | 121.8887 | -121.7422 | 0.1236 | -0.0060272 | -0.0002927 | 0.056258 | 0.055189 | -0.0017048 | -0.0079061 | -0.0048985 | -0.011261 | 0.0027984 | 0.073006 | 0.063987 | -0.012228 | 0.01944 | -0.0001432 | -0.46234 | -0.032043 | -121.8018 | -0.082397 | -121.1334 | -121.8338 | -121.8613 | -21.8307 | 0.054932 | -121.8521 | -0.036621 | -121.1746 | -121.6873 | -121.3165 | -0.059509 | -0.15564 | -0.20599 | 0.60883 | -0.11902 | -0.091552 | -0.059509 | -0.032043 | -0.10986 | -0.068664 | -0.16022 | 0.56763 | 0.42572 | 0.054932 | 0.53558 | 0.1648 | 0.66834 | 121.7194 | 0.67749 | 121.8155 | 121.7697 | 121.907 | 121.7102 | 121.7972 | -121.9254 | -121.9757 | 121.6599 | 121.7056 | 121.2799 | 99.9115
1837.7969 | 121.9574 | -121.7468 | 0.068665 | 0.0016023 | -0.0009335 | 0.056258 | 0.051985 | -0.0027728 | -0.0094015 | -0.0036167 | -0.0051575 | -0.002115 | 0.072151 | 0.054801 | -0.012014 | 0.020721 | -0.0022794 | -0.52643 | -0.045776 | -121.7743 | 0.004578 | -121.0556 | -121.7789 | -121.7743 | -22.1695 | 0.018311 | -121.8155 | 0.050354 | -121.1334 | -121.6095 | -121.3074 | -0.027466 | -0.11444 | -0.064087 | 0.69122 | -0.027466 | -0.032044 | 0 | -0.004578 | -0.068665 | -0.050354 | -0.018311 | 0.6134 | 0.43945 | 0.13733 | 0.50812 | 0.20599 | 0.71869 | 121.7789 | 0.68207 | 121.8658 | 121.7285 | 121.8338 | 121.701 | 121.7651 | -121.843 | -121.8842 | 121.7514 | 121.7972 | 121.2204 | 99.5773
1839.5625 | 121.8887 | -121.756 | 0.15106 | -0.013657 | -0.0034971 | 0.056258 | 0.053908 | -0.0057636 | -0.0079061 | -0.0059665 | -0.0082093 | 0.001303 | 0.072792 | 0.058005 | -0.012655 | 0.020935 | -0.0027066 | -0.4715 | -0.022888 | -121.8109 | -0.059509 | -121.1288 | -121.8338 | -121.8384 | -22.5769 | 0.050354 | -121.8201 | -0.041199 | -121.1838 | -121.6919 | -121.4035 | -0.054932 | -0.17395 | -0.21057 | 0.62714 | -0.082398 | -0.07782 | -0.027466 | -0.022888 | -0.064087 | -0.10071 | -0.19226 | 0.5722 | 0.35248 | 0.064086 | 0.41657 | 0.12817 | 0.68207 | 121.7514 | 0.63629 | 121.7789 | 121.788 | 121.8704 | 121.7331 | 121.8063 | -121.962 | -121.9711 | 121.6965 | 121.7148 | 121.2845 | 99.1791
1841.25 | 122.0078 | -121.7239 | 0.082397 | -0.021286 | -0.0026425 | 0.057753 | 0.054335 | -0.0012774 | -0.0070517 | -0.00062587 | -0.0082093 | 0.0023712 | 0.071297 | 0.066123 | -0.01351 | 0.018585 | -0.0029202 | -0.41199 | -0.073242 | -121.7926 | 0.068665 | -120.9778 | -121.7194 | -121.7422 | -22.76 | -0.004578 | -121.8155 | 0.07782 | -121.0464 | -121.5591 | -121.2982 | -0.068665 | -0.15564 | -0.013732 | 0.74616 | -0.018311 | 0.004578 | 0.050354 | 0.073243 | -0.091553 | -0.086975 | -0.004577 | 0.67749 | 0.42572 | 0.16479 | 0.51727 | 0.25635 | 0.81482 | 121.8613 | 0.76904 | 121.8933 | 121.7194 | 121.8109 | 121.6507 | 121.7194 | -121.875 | -121.8979 | 121.7926 | 121.8018 | 121.312 | 98.9639
1843 | 121.9666 | -121.7468 | 0.091553 | -0.013657 | -0.0007199 | 0.055189 | 0.054121 | -0.004909 | -0.0083335 | -0.0023349 | -0.0082093 | 0.00066224 | 0.07151 | 0.057151 | -0.012014 | 0.020081 | -0.0016384 | -0.54016 | -0.073242 | -121.7834 | -0.004578 | -121.0785 | -121.788 | -121.788 | -23.2452 | 0.013733 | -121.8475 | 0.027466 | -121.1014 | -121.6095 | -121.3348 | -0.036621 | -0.16479 | -0.096131 | 0.66833 | -0.041199 | -0.041199 | -0.004578 | -0.004578 | -0.10071 | -0.07782 | -0.064087 | 0.64545 | 0.41199 | 0.13733 | 0.51269 | 0.23804 | 0.70496 | 121.7789 | 0.74616 | 121.875 | 121.7102 | 121.8613 | 121.6736 | 121.7606 | -121.875 | -121.9391 | 121.7422 | 121.7743 | 121.2067 | 98.5016
1844.75 | 121.9116 | -121.7697 | 0.10529 | -0.0060272 | 0.0031253 | 0.056044 | 0.057539 | 0.00064519 | -0.0081197 | -0.0042575 | -0.0051575 | 0.0040802 | 0.070442 | 0.062278 | -0.014364 | 0.021576 | -0.0003568 | -0.48065 | -0.032043 | -121.7972 | -0.018311 | -121.1014 | -121.8338 | -121.8475 | -23.5931 | 0.050354 | -121.8475 | 0 | -121.1655 | -121.7148 | -121.4218 | -0.027466 | -0.13733 | -0.1236 | 0.66833 | -0.07782 | -0.064087 | -0.050354 | -0.036621 | -0.07782 | -0.054932 | -0.10529 | 0.60425 | 0.3479 | 0.054931 | 0.42572 | 0.13275 | 0.6958 | 121.7789 | 0.68207 | 121.8475 | 121.7651 | 121.8979 | 121.7377 | 121.8201 | -121.9025 | -121.9528 | 121.7514 | 121.7697 | 121.2891 | 98.1766
1846.4531 | 121.9162 | -121.7972 | 0.10529 | -0.0060272 | -0.0007199 | 0.05284 | 0.055403 | -0.0019184 | -0.0068381 | -0.0042575 | -0.0051575 | 0.003012 | 0.071724 | 0.058646 | -0.010946 | 0.019867 | -0.0009976 | -0.48981 | -0.027466 | -121.843 | -0.07782 | -121.1655 | -121.8384 | -121.8842 | -24.0051 | 0.054932 | -121.8567 | -0.041199 | -121.1884 | -121.7102 | -121.4584 | -0.045777 | -0.13275 | -0.18311 | 0.63171 | -0.086975 | -0.041199 | -0.041198 | 0.004578 | -0.059509 | -0.050354 | -0.14649 | 0.60883 | 0.33875 | 0.086975 | 0.39825 | 0.14648 | 0.67749 | 121.7651 | 0.66833 | 121.8155 | 121.8155 | 121.9116 | 121.7697 | 121.8521 | -121.9482 | -121.962 | 121.7194 | 121.756 | 121.3074 | 97.7921
1848.2031 | 121.8933 | -121.7514 | 0.10986 | -0.013657 | -0.0026425 | 0.056898 | 0.056044 | -0.0034136 | -0.0085471 | -0.0014805 | -0.0082093 | 0.0021576 | 0.069588 | 0.057578 | -0.01116 | 0.019653 | 0.0004978 | -0.48065 | -0.022888 | -121.843 | -0.068665 | -121.1472 | -121.8658 | -121.8613 | -24.3805 | 0.050354 | -121.8567 | -0.054932 | -121.1884 | -121.7148 | -121.4539 | -0.091553 | -0.13275 | -0.17853 | 0.60425 | -0.10986 | -0.11444 | -0.01831 | -0.022888 | -0.10529 | -0.059509 | -0.16479 | 0.56305 | 0.29755 | 0.036621 | 0.40283 | 0.14191 | 0.6958 | 121.7743 | 0.66833 | 121.8018 | 121.8201 | 121.907 | 121.7285 | 121.8018 | -121.9528 | -121.9666 | 121.6827 | 121.6965 | 121.2708 | 97.3709
1849.9531 | 121.9528 | -121.7789 | 0.10529 | -0.013657 | -7.9104e-05 | 0.056898 | 0.055617 | -0.002132 | -0.0068381 | -0.0036167 | -0.0051575 | 0.0027984 | 0.074074 | 0.052878 | -0.014364 | 0.020721 | -0.003561 | -0.46234 | -0.032043 | -121.8475 | -0.050354 | -121.1472 | -121.8292 | -121.8658 | -24.7009 | 0.059509 | -121.875 | 0.009155 | -121.138 | -121.6919 | -121.4035 | -0.068664 | -0.13733 | -0.15564 | 0.63171 | -0.086975 | -0.050354 | -0.018311 | 0.01831 | -0.09613 | -0.045777 | -0.096131 | 0.64087 | 0.37537 | 0.086975 | 0.4715 | 0.1831 | 0.70038 | 121.7972 | 0.737 | 121.8842 | 121.8155 | 121.9345 | 121.7468 | 121.8384 | -121.9528 | -121.9803 | 121.7285 | 121.788 | 121.3165 | 97.0779
1851.7031 | 121.9849 | -121.7239 | 0.10071 | -0.013657 | -0.0034971 | 0.056471 | 0.054335 | -0.0025592 | -0.0083335 | -0.0034031 | -0.0082093 | -0.0016876 | 0.07151 | 0.056937 | -0.013937 | 0.019653 | -0.0001432 | -0.54932 | -0.050354 | -121.7926 | -0.018311 | -121.0831 | -121.8201 | -121.8063 | -25.0809 | 0.018311 | -121.8338 | 0.045776 | -121.1014 | -121.6141 | -121.3531 | -0.068665 | -0.15106 | -0.11902 | 0.64087 | -0.082397 | -0.09613 | -0.013732 | -0.027465 | -0.10986 | -0.082397 | -0.054932 | 0.62256 | 0.37079 | 0.10986 | 0.48065 | 0.21973 | 0.70953 | 121.7743 | 0.73242 | 121.8796 | 121.7422 | 121.8521 | 121.6736 | 121.7422 | -121.8933 | -121.9345 | 121.7056 | 121.7697 | 121.1746 | 96.6431
1853.3906 | 121.994 | -121.756 | 0.086975 | -0.021286 | -0.0015743 | 0.05583 | 0.054976 | 0.0036358 | -0.0081197 | -0.0034031 | -0.0082093 | 0.001944 | 0.071297 | 0.064841 | -0.012441 | 0.019012 | 0.0024204 | -0.56763 | -0.064087 | -121.8292 | 0 | -121.1151 | -121.8109 | -121.8246 | -25.4425 | 0.022888 | -121.843 | 0.032043 | -121.1243 | -121.6461 | -121.3623 | -0.073243 | -0.15106 | -0.086975 | 0.64087 | -0.068665 | -0.054932 | 0.004578 | 0.018311 | -0.086976 | -0.064087 | -0.054932 | 0.63171 | 0.39368 | 0.10986 | 0.48065 | 0.19684 | 0.71411 | 121.8292 | 0.71869 | 121.875 | 121.7651 | 121.8658 | 121.6919 | 121.7789 | -121.9162 | -121.9299 | 121.756 | 121.788 | 121.1884 | 96.3135
1855.1406 | 121.994 | -121.7651 | 0.09613 | -0.013657 | -0.0009335 | 0.056044 | 0.054976 | -0.002132 | -0.0089743 | -0.0063937 | -0.0051575 | 0.00087584 | 0.070015 | 0.060355 | -0.01415 | 0.020935 | -0.004202 | -0.55847 | -0.050354 | -121.8063 | 0 | -121.0968 | -121.8063 | -121.8246 | -25.8591 | 0.013733 | -121.8658 | 0.041199 | -121.1151 | -121.6324 | -121.3577 | -0.041198 | -0.14648 | -0.09613 | 0.66833 | -0.059509 | -0.041198 | -0.018311 | 0 | -0.10071 | -0.082397 | -0.054931 | 0.65002 | 0.40741 | 0.13275 | 0.50812 | 0.23346 | 0.70953 | 121.8063 | 0.75073 | 121.907 | 121.756 | 121.8796 | 121.7148 | 121.7789 | -121.9025 | -121.962 | 121.7651 | 121.8063 | 121.2067 | 95.9061
1856.9062 | 121.9803 | -121.7377 | 0.086975 | -0.013657 | 0.0022709 | 0.057967 | 0.053694 | -0.0036274 | -0.0074789 | -0.0021213 | -0.0051575 | 0.0021576 | 0.073219 | 0.05886 | -0.013723 | 0.01944 | -0.002493 | -0.54932 | -0.073242 | -121.7926 | 0.041199 | -121.0419 | -121.8063 | -121.8063 | -26.1795 | 0.009155 | -121.843 | 0.064087 | -121.1014 | -121.6324 | -121.3486 | -0.054932 | -0.16022 | -0.045776 | 0.6958 | -0.068664 | -0.068664 | -0.013732 | -0.013732 | -0.10529 | -0.07782 | -0.022888 | 0.63629 | 0.3891 | 0.10529 | 0.49438 | 0.21057 | 0.75073 | 121.8338 | 0.74158 | 121.907 | 121.7194 | 121.8521 | 121.6644 | 121.7468 | -121.8796 | -121.9299 | 121.7789 | 121.8018 | 121.1884 | 95.5582
1858.6094 | 122.0032 | -121.7422 | 0.091553 | -0.0060272 | -0.0022153 | 0.056898 | 0.053908 | -0.00063661 | -0.0096151 | -0.0031895 | -0.0051575 | -0.00083316 | 0.070229 | 0.069968 | -0.015859 | 0.01944 | -0.0048428 | -0.58136 | -0.050354 | -121.8109 | 0.004578 | -121.0876 | -121.8109 | -121.8018 | -26.6602 | 0.018311 | -121.8567 | 0.045776 | -121.1197 | -121.6553 | -121.3486 | -0.068664 | -0.14191 | -0.086975 | 0.6546 | -0.059509 | -0.068664 | 0.009155 | 0 | -0.11444 | -0.073242 | -0.045777 | 0.62256 | 0.39368 | 0.086976 | 0.50812 | 0.20142 | 0.72327 | 121.8155 | 0.737 | 121.9025 | 121.7606 | 121.875 | 121.6919 | 121.7606 | -121.9025 | -121.9482 | 121.7468 | 121.788 | 121.1609 | 95.0821
1860.2969 | 122.0261 | -121.7331 | 0.059509 | -0.013657 | 0.0007755 | 0.059676 | 0.055403 | -0.0029864 | -0.0072653 | -0.00083947 | -0.0021057 | 0.0021576 | 0.072365 | 0.062705 | -0.013296 | 0.020935 | 0.0007114 | -0.56305 | -0.07782 | -121.8201 | 0.064087 | -121.0373 | -121.7972 | -121.7972 | -26.9669 | 0 | -121.8109 | 0.086975 | -121.1014 | -121.6232 | -121.344 | -0.086975 | -0.13733 | 0.004578 | 0.6958 | -0.064087 | -0.064087 | 0.022888 | 0.022888 | -0.07782 | -0.059509 | 0.027466 | 0.63171 | 0.3891 | 0.10986 | 0.46692 | 0.18768 | 0.78278 | 121.8842 | 0.70953 | 121.8979 | 121.7422 | 121.8109 | 121.6553 | 121.7331 | -121.8796 | -121.8704 | 121.7972 | 121.8201 | 121.17 | 94.7662
1862.0469 | 122.0032 | -121.7651 | 0.082397 | -0.013657 | -7.9104e-05 | 0.057539 | 0.056685 | -0.001491 | -0.0087607 | -0.0031895 | -0.0082093 | 0.0015166 | 0.071938 | 0.05416 | -0.012869 | 0.020935 | -0.0031338 | -0.58594 | -0.073242 | -121.8155 | 0.009155 | -121.0876 | -121.8201 | -121.8201 | -27.4063 | 0 | -121.8613 | 0.050354 | -121.1151 | -121.6507 | -121.3715 | -0.050354 | -0.15564 | -0.073242 | 0.67749 | -0.054931 | -0.054931 | -0.004577 | -0.004577 | -0.09613 | -0.082397 | -0.032043 | 0.65002 | 0.39368 | 0.11444 | 0.48981 | 0.21057 | 0.72784 | 121.8246 | 0.74616 | 121.9116 | 121.7422 | 121.8613 | 121.6919 | 121.7651 | -121.8979 | -121.9437 | 121.7743 | 121.8155 | 121.1792 | 94.3588
1863.7969 | 122.0627 | -121.7422 | 0.059509 | -0.0060272 | 0.0003483 | 0.058607 | 0.056044 | 0.0014996 | -0.0068381 | -0.0025485 | -0.0051575 | 0.003012 | 0.072578 | 0.059287 | -0.015005 | 0.019226 | -0.002493 | -0.54474 | -0.054932 | -121.8155 | 0.068665 | -121.0602 | -121.8018 | -121.7972 | -27.8091 | 0.009155 | -121.8292 | 0.11902 | -121.051 | -121.6187 | -121.312 | -0.073242 | -0.11444 | 0.009156 | 0.68207 | -0.054931 | -0.059509 | 0.018311 | 0.013733 | -0.086975 | -0.050354 | 0.05951 | 0.69122 | 0.4303 | 0.1236 | 0.51727 | 0.21057 | 0.75531 | 121.8842 | 0.7782 | 121.9482 | 121.7606 | 121.8384 | 121.6873 | 121.7514 | -121.875 | -121.8887 | 121.8109 | 121.8613 | 121.1975 | 93.9331
1865.4844 | 121.9528 | -121.756 | 0.10986 | -0.0060272 | 0.0020571 | 0.059248 | 0.054549 | -0.0012774 | -0.0047019 | -0.00083947 | -0.0051575 | 0.003653 | 0.071297 | 0.06655 | -0.013723 | 0.020081 | -0.002493 | -0.52185 | -0.013733 | -121.843 | -0.009155 | -121.1517 | -121.8658 | -121.8842 | -28.2623 | 0.036621 | -121.8475 | -0.009155 | -121.1746 | -121.7422 | -121.431 | -0.086976 | -0.1236 | -0.11902 | 0.60425 | -0.12817 | -0.10986 | -0.041198 | -0.022888 | -0.091553 | -0.073242 | -0.11902 | 0.58136 | 0.32501 | 0.013732 | 0.41656 | 0.10528 | 0.69122 | 121.8338 | 0.67291 | 121.8384 | 121.8292 | 121.8842 | 121.7422 | 121.7926 | -121.9528 | -121.9574 | 121.7468 | 121.7468 | 121.2341 | 93.4937
1867.1875 | 121.9574 | -121.788 | 0.10071 | -0.021286 | 0.0024845 | 0.057539 | 0.058607 | -0.002132 | -0.0057699 | -0.0048985 | -0.0051575 | 0.001944 | 0.074501 | 0.059714 | -0.01351 | 0.023926 | -0.0031338 | -0.51727 | -0.041199 | -121.8613 | -0.018311 | -121.1334 | -121.8567 | -121.8842 | -28.6652 | 0.041199 | -121.875 | 0 | -121.1517 | -121.7239 | -121.4127 | -0.073242 | -0.14191 | -0.11902 | 0.6546 | -0.09613 | -0.068664 | -0.022888 | 0.004578 | -0.086975 | -0.059509 | -0.10071 | 0.63629 | 0.37537 | 0.064087 | 0.46234 | 0.15106 | 0.72784 | 121.843 | 0.72327 | 121.875 | 121.8201 | 121.9162 | 121.7468 | 121.8292 | -121.962 | -121.9757 | 121.7697 | 121.788 | 121.2708 | 93.1229
1868.9531 | 122.0261 | -121.756 | 0.064087 | -0.021286 | 0.0007755 | 0.056471 | 0.054549 | 0.0027814 | -0.0070517 | -0.0046847 | -0.0082093 | 0.001303 | 0.07151 | 0.059073 | -0.013723 | 0.020508 | -0.0031338 | -0.58594 | -0.064087 | -121.7972 | 0.064087 | -121.0464 | -121.8109 | -121.7972 | -29.0451 | 0.004578 | -121.8475 | 0.082397 | -121.0785 | -121.6553 | -121.3486 | -0.041199 | -0.12817 | 0 | 0.70953 | -0.041199 | -0.054932 | 0 | -0.013733 | -0.091553 | -0.059509 | 0.01831 | 0.67749 | 0.40741 | 0.10071 | 0.49896 | 0.19226 | 0.75073 | 121.8613 | 0.76904 | 121.9299 | 121.7331 | 121.8521 | 121.6919 | 121.7606 | -121.8613 | -121.9116 | 121.8201 | 121.8384 | 121.17 | 92.7109
1870.625 | 121.9528 | -121.8109 | 0.11444 | -0.0060272 | 0.0003483 | 0.056258 | 0.057539 | -0.0040546 | -0.0085471 | -0.0044711 | -0.0082093 | 0.0023712 | 0.071297 | 0.068045 | -0.011801 | 0.021576 | -0.0039884 | -0.53558 | -0.022888 | -121.8842 | -0.022888 | -121.138 | -121.8887 | -121.8979 | -29.512 | 0.059509 | -121.8933 | 0.009155 | -121.17 | -121.7514 | -121.4401 | -0.073242 | -0.13733 | -0.13733 | 0.67291 | -0.086975 | -0.07782 | -0.013733 | -0.004578 | -0.082398 | -0.054932 | -0.10529 | 0.64087 | 0.37079 | 0.059509 | 0.45319 | 0.14191 | 0.74616 | 121.8613 | 0.72327 | 121.9025 | 121.8613 | 121.9528 | 121.788 | 121.8704 | -121.9986 | -122.0078 | 121.788 | 121.8201 | 121.2753 | 92.2989
1872.375 | 121.9299 | -121.8292 | 0.13733 | -0.0060272 | 0.0026981 | 0.059035 | 0.056471 | -0.0029864 | -0.0098287 | -0.0059665 | -0.0082093 | 0.00087584 | 0.071938 | 0.061209 | -0.012014 | 0.023071 | -0.0027066 | -0.58136 | -0.041199 | -121.8704 | -0.064087 | -121.1929 | -121.9345 | -121.9391 | -30.0247 | 0.059509 | -121.9025 | -0.036621 | -121.2158 | -121.7972 | -121.463 | -0.041198 | -0.17853 | -0.20142 | 0.63629 | -0.10986 | -0.10529 | -0.068665 | -0.064087 | -0.073242 | -0.07782 | -0.17395 | 0.6134 | 0.36621 | 0.032044 | 0.43945 | 0.10529 | 0.67749 | 121.8063 | 0.68665 | 121.8658 | 121.8292 | 121.962 | 121.788 | 121.8887 | -122.0078 | -122.0398 | 121.7651 | 121.7926 | 121.2479 | 91.8045
1874.0781 | 121.9574 | -121.8109 | 0.091553 | -0.013657 | 0.0026981 | 0.057112 | 0.057539 | 0.00085879 | -0.0079061 | -0.0034031 | -0.0021057 | 0.0027984 | 0.07151 | 0.062491 | -0.010305 | 0.019867 | 0.0004978 | -0.62714 | -0.013733 | -121.8704 | -0.10529 | -121.2524 | -121.9574 | -121.962 | -30.4367 | 0.036621 | -121.9116 | -0.032043 | -121.2067 | -121.7789 | -121.4493 | -0.059509 | -0.10529 | -0.19684 | 0.55847 | -0.15106 | -0.14648 | -0.091553 | -0.086975 | -0.10071 | -0.054932 | -0.1236 | 0.60425 | 0.36163 | 0.032043 | 0.46234 | 0.13275 | 0.61798 | 121.7651 | 0.70496 | 121.8796 | 121.8567 | 121.9482 | 121.7972 | 121.8475 | -121.962 | -122.0032 | 121.7056 | 121.7789 | 121.1838 | 91.3742
1875.8281 | 121.994 | -121.7926 | 0.10986 | -0.021286 | -0.0002927 | 0.055617 | 0.052199 | 0.0017132 | -0.0076925 | -0.0031895 | -0.0051575 | 0.0034392 | 0.071724 | 0.063987 | -0.011801 | 0.019867 | -0.0016384 | -0.53558 | -0.013733 | -121.8796 | -0.059509 | -121.1975 | -121.8842 | -121.9116 | -30.7983 | 0.045776 | -121.9116 | -0.013733 | -121.138 | -121.7377 | -121.431 | -0.086975 | -0.1236 | -0.16937 | 0.59509 | -0.11902 | -0.091552 | -0.032043 | -0.004577 | -0.11902 | -0.064087 | -0.1236 | 0.6546 | 0.36163 | 0.054932 | 0.48065 | 0.17395 | 0.68207 | 121.8201 | 0.77362 | 121.8979 | 121.8658 | 121.9574 | 121.7789 | 121.8384 | -121.9894 | -122.0215 | 121.7331 | 121.7789 | 121.257 | 90.9943
1877.5156 | 121.962 | -121.843 | 0.12817 | -0.013657 | -0.0030697 | 0.055617 | 0.05348 | -0.0010638 | -0.0094015 | -0.0016941 | -0.0051575 | 0.001303 | 0.074074 | 0.061637 | -0.0096643 | 0.018158 | -0.0001432 | -0.56305 | -0.009155 | -121.8979 | -0.091553 | -121.1975 | -121.8979 | -121.9208 | -31.2286 | 0.054932 | -121.9162 | -0.032043 | -121.1838 | -121.7606 | -121.4676 | -0.054931 | -0.13733 | -0.21973 | 0.64545 | -0.077819 | -0.054931 | -0.022888 | 0 | -0.073242 | -0.073242 | -0.16022 | 0.65918 | 0.37537 | 0.082398 | 0.44861 | 0.15564 | 0.70038 | 121.8063 | 0.73242 | 121.8842 | 121.8887 | 121.9711 | 121.8338 | 121.8979 | -122.0261 | -122.0444 | 121.7514 | 121.8109 | 121.2799 | 90.6143
1879.2812 | 122.1085 | -121.7606 | 0.068665 | -0.013657 | -0.0045651 | 0.056685 | 0.050917 | -0.0051226 | -0.0079061 | -0.0038303 | -0.0051575 | -0.0010468 | 0.070656 | 0.0642 | -0.010946 | 0.019653 | -0.0027066 | -0.56305 | -0.045776 | -121.875 | 0.027466 | -121.051 | -121.7789 | -121.7926 | -31.5308 | -0.013733 | -121.8658 | 0.10529 | -121.0281 | -121.5958 | -121.2662 | -0.11444 | -0.11444 | -0.041199 | 0.70953 | -0.032044 | -0.018311 | 0.082397 | 0.09613 | -0.10529 | -0.082398 | 0.036621 | 0.73242 | 0.49438 | 0.16479 | 0.59967 | 0.27008 | 0.82398 | 121.9025 | 0.83771 | 121.9711 | 121.8292 | 121.8521 | 121.7148 | 121.7468 | -121.9437 | -121.9345 | 121.788 | 121.8658 | 121.1975 | 90.2298
1881.0312 | 122.0444 | -121.7972 | 0.086975 | -0.013657 | 0.0029117 | 0.056258 | 0.057112 | 0.0036358 | -0.0074789 | -0.0038303 | -0.0051575 | 0.0021576 | 0.073433 | 0.064841 | -0.014364 | 0.021576 | 0.0004978 | -0.66834 | -0.027466 | -121.875 | -0.054932 | -121.2021 | -121.9162 | -121.9254 | -32.1304 | 0.027466 | -121.8933 | 0.036621 | -121.1334 | -121.7102 | -121.3028 | -0.07782 | -0.11444 | -0.14191 | 0.59509 | -0.12817 | -0.11902 | -0.050354 | -0.041199 | -0.096131 | -0.059509 | -0.050354 | 0.66376 | 0.49438 | 0.086975 | 0.59052 | 0.18311 | 0.67291 | 121.8201 | 0.75989 | 121.9299 | 121.8475 | 121.9208 | 121.7697 | 121.8246 | -121.962 | -121.9803 | 121.7422 | 121.8338 | 121.1288 | 89.6667
1882.7656 | 122.0581 | -121.8246 | 0.10986 | -0.013657 | -0.0007199 | 0.057753 | 0.05348 | -0.0036274 | -0.0079061 | -0.0016941 | -0.0082093 | 0.00066224 | 0.069588 | 0.059073 | -0.011801 | 0.019226 | 0.000925 | -0.62714 | -0.050354 | -121.8658 | -0.018311 | -121.1563 | -121.875 | -121.8658 | -32.5882 | 0.018311 | -121.9025 | 0.027466 | -121.0968 | -121.6599 | -121.3028 | -0.041199 | -0.16022 | -0.12817 | 0.66833 | -0.041199 | -0.050354 | 0 | -0.009155 | -0.07782 | -0.091552 | -0.082397 | 0.72784 | 0.52185 | 0.16479 | 0.59967 | 0.24262 | 0.70953 | 121.8475 | 0.80566 | 121.9299 | 121.8155 | 121.9208 | 121.7743 | 121.843 | -121.9757 | -122.0123 | 121.8063 | 121.8521 | 121.1975 | 89.2364
1884.4688 | 121.9437 | -121.8475 | 0.11444 | -0.013657 | -0.0015743 | 0.053694 | 0.054762 | 0.0019268 | -0.0079061 | -0.0019077 | -0.0051575 | 0.0032256 | 0.073006 | 0.059714 | -0.013082 | 0.020081 | -0.0031338 | -0.58136 | -0.032043 | -121.9025 | -0.082397 | -121.2067 | -121.9025 | -121.9254 | -33.0048 | 0.054932 | -121.907 | -0.041199 | -121.1838 | -121.7651 | -121.3852 | -0.054932 | -0.14648 | -0.19684 | 0.64087 | -0.07782 | -0.054932 | -0.022888 | 0 | -0.059509 | -0.059509 | -0.15564 | 0.66376 | 0.46234 | 0.082397 | 0.52185 | 0.14191 | 0.6958 | 121.8201 | 0.72327 | 121.8658 | 121.8704 | 121.962 | 121.8155 | 121.9025 | -122.0169 | -122.0215 | 121.7651 | 121.8063 | 121.2662 | 88.8428
1886.2188 | 122.0627 | -121.7789 | 0.082397 | -0.013657 | 0.0022709 | 0.056044 | 0.05348 | -0.00063661 | -0.0083335 | -0.0036167 | -0.0051575 | 0.00044864 | 0.07151 | 0.049247 | -0.01415 | 0.020294 | -0.0029202 | -0.62256 | -0.045776 | -121.8521 | 0.054932 | -121.0693 | -121.8201 | -121.8201 | -33.3664 | -0.004578 | -121.8933 | 0.07782 | -121.0876 | -121.6644 | -121.2753 | -0.073242 | -0.12817 | -0.027465 | 0.70953 | -0.041198 | -0.041198 | 0.032044 | 0.032044 | -0.11444 | -0.086975 | -0.004577 | 0.69122 | 0.50354 | 0.11444 | 0.61798 | 0.22888 | 0.78278 | 121.907 | 0.80566 | 121.9711 | 121.8063 | 121.8887 | 121.7331 | 121.7743 | -121.9345 | -121.9757 | 121.8338 | 121.8567 | 121.1563 | 88.4125
1887.9688 | 121.9711 | -121.843 | 0.10071 | -0.013657 | -0.0022153 | 0.057112 | 0.053908 | 0.0014996 | -0.0091879 | -0.0010531 | -0.0051575 | 0.0017304 | 0.073006 | 0.065909 | -0.012014 | 0.019653 | -0.0003568 | -0.58136 | -0.009155 | -121.9162 | -0.068665 | -121.2433 | -121.9345 | -121.9345 | -33.8791 | 0.054932 | -121.9025 | -0.036621 | -121.1746 | -121.7514 | -121.3577 | -0.073242 | -0.10986 | -0.16937 | 0.59967 | -0.091552 | -0.091552 | -0.01831 | -0.01831 | -0.059509 | -0.045776 | -0.13733 | 0.66833 | 0.48523 | 0.091553 | 0.54474 | 0.15106 | 0.67291 | 121.8475 | 0.72784 | 121.8658 | 121.907 | 121.9574 | 121.8338 | 121.8979 | -122.0169 | -122.0032 | 121.7743 | 121.8063 | 121.2616 | 87.9639
1889.7344 | 122.0169 | -121.8155 | 0.09613 | -0.0060272 | 0.0031253 | 0.055189 | 0.054335 | -0.0032 | -0.010256 | -0.0046847 | -0.0082093 | 0.0032256 | 0.072792 | 0.068686 | -0.012869 | 0.021149 | 0.000925 | -0.5722 | -0.032043 | -121.8842 | 0 | -121.1517 | -121.8933 | -121.907 | -34.2865 | 0.032043 | -121.9162 | 0 | -121.1472 | -121.7514 | -121.3348 | -0.068664 | -0.12817 | -0.09613 | 0.66376 | -0.091552 | -0.07782 | -0.022888 | -0.009156 | -0.10071 | -0.064087 | -0.09613 | 0.66833 | 0.48065 | 0.064087 | 0.58136 | 0.1648 | 0.73242 | 121.8842 | 0.76904 | 121.9162 | 121.8521 | 121.9482 | 121.7834 | 121.8475 | -121.9803 | -122.0123 | 121.8155 | 121.8155 | 121.2433 | 87.529
1891.5 | 121.9757 | -121.8704 | 0.11902 | -0.013657 | -0.0009335 | 0.056685 | 0.054976 | -0.00063661 | -0.0096151 | -0.0040439 | -0.0082093 | 0.0023712 | 0.072151 | 0.065055 | -0.013937 | 0.020721 | -0.003561 | -0.59509 | -0.009155 | -121.9208 | -0.082397 | -121.225 | -121.9254 | -121.962 | -34.7214 | 0.050354 | -121.9299 | -0.045776 | -121.1655 | -121.7743 | -121.376 | -0.050354 | -0.12817 | -0.20142 | 0.64545 | -0.091553 | -0.054932 | -0.041199 | -0.004578 | -0.05951 | -0.068665 | -0.16479 | 0.70496 | 0.49438 | 0.09613 | 0.55389 | 0.15564 | 0.6958 | 121.8384 | 0.76447 | 121.8842 | 121.9116 | 121.9803 | 121.8613 | 121.9208 | -122.0398 | -122.049 | 121.788 | 121.8246 | 121.2753 | 87.149
1893.1875 | 122.0673 | -121.8201 | 0.082397 | -0.028916 | -0.0005063 | 0.05818 | 0.053267 | -0.001491 | -0.010043 | -0.0059665 | -0.0082093 | -0.00040596 | 0.073647 | 0.055014 | -0.013937 | 0.017731 | -0.0005704 | -0.54016 | -0.054932 | -121.875 | 0.064087 | -121.0831 | -121.8063 | -121.8155 | -35.0464 | 0.013733 | -121.875 | 0.064087 | -121.051 | -121.637 | -121.312 | -0.054932 | -0.13733 | -0.01831 | 0.737 | 0.004577 | 0.013733 | 0.059509 | 0.068665 | -0.054932 | -0.068664 | -0.01831 | 0.76904 | 0.50812 | 0.18311 | 0.56305 | 0.23804 | 0.79193 | 121.9391 | 0.82398 | 121.9391 | 121.8201 | 121.8887 | 121.7651 | 121.8338 | -121.9574 | -121.9574 | 121.8842 | 121.8842 | 121.2799 | 86.7737
1894.9375 | 122.1039 | -121.788 | 0.068665 | -0.0060272 | 0.0035525 | 0.05818 | 0.055189 | 0.00085879 | -0.0053427 | -0.0046847 | -0.0082093 | 0.0021576 | 0.074074 | 0.061637 | -0.013296 | 0.020935 | 0.0002842 | -0.64087 | -0.036621 | -121.8979 | 0.041199 | -121.106 | -121.8475 | -121.8567 | -35.5316 | 0.004578 | -121.8842 | 0.09613 | -121.0648 | -121.6553 | -121.2936 | -0.10986 | -0.10529 | -0.027466 | 0.68207 | -0.068664 | -0.059509 | 0.041199 | 0.050354 | -0.09613 | -0.064087 | 0.027465 | 0.72327 | 0.49439 | 0.13275 | 0.59052 | 0.22888 | 0.79193 | 121.9391 | 0.8194 | 121.9803 | 121.8613 | 121.8887 | 121.7514 | 121.7926 | -121.9666 | -121.9528 | 121.8292 | 121.8842 | 121.1472 | 86.2564
1896.6875 | 122.0306 | -121.843 | 0.09613 | 0.0016023 | -0.0022153 | 0.056685 | 0.051558 | -0.0019184 | -0.0083335 | 1.4934e-05 | -0.0051575 | 0.0010894 | 0.073006 | 0.052451 | -0.01351 | 0.018585 | -0.0018522 | -0.55847 | -0.054932 | -121.8979 | 0.036621 | -121.1197 | -121.8201 | -121.8567 | -35.9528 | 0.027466 | -121.907 | 0.009155 | -121.1105 | -121.6965 | -121.3852 | -0.054931 | -0.15106 | -0.059509 | 0.72327 | -0.013732 | 0.022889 | 0.041199 | 0.07782 | -0.064086 | -0.068664 | -0.086975 | 0.73242 | 0.45776 | 0.14648 | 0.52185 | 0.21057 | 0.7782 | 121.9345 | 0.79651 | 121.9162 | 121.843 | 121.9345 | 121.788 | 121.8704 | -121.994 | -122.0032 | 121.8796 | 121.8521 | 121.2845 | 85.8902
1898.3906 | 122.1176 | -121.8109 | 0.07782 | -0.013657 | 0.0018435 | 0.059248 | 0.054976 | 0.0014996 | -0.010043 | -0.0016941 | 0.0009461 | 2.1442e-05 | 0.070229 | 0.051169 | -0.01351 | 0.020935 | -0.0009976 | -0.65002 | -0.054932 | -121.8842 | 0.045776 | -121.0922 | -121.8384 | -121.843 | -36.4563 | -0.013733 | -121.8933 | 0.10986 | -121.0556 | -121.6553 | -121.3211 | -0.073242 | -0.13275 | -0.032044 | 0.71869 | -0.032044 | -0.027466 | 0.041198 | 0.045776 | -0.082398 | -0.091553 | 0.032043 | 0.75531 | 0.48981 | 0.15564 | 0.5722 | 0.23804 | 0.79193 | 121.9299 | 0.83771 | 122.0032 | 121.8292 | 121.8796 | 121.756 | 121.7972 | -121.962 | -121.9711 | 121.8567 | 121.9208 | 121.1609 | 85.3546
1900.1562 | 122.1176 | -121.788 | 0.068665 | 0.0016023 | 0.0018435 | 0.058394 | 0.054549 | 4.192e-06 | -0.0081197 | -0.0014805 | -0.0051575 | 0.00044864 | 0.071938 | 0.058219 | -0.011801 | 0.021149 | -0.0018522 | -0.65002 | -0.064087 | -121.8613 | 0.050354 | -121.0968 | -121.8338 | -121.8338 | -37.0148 | -0.004578 | -121.8933 | 0.10529 | -121.051 | -121.6553 | -121.3165 | -0.073242 | -0.13275 | -0.018311 | 0.69122 | -0.045776 | -0.045776 | 0.027466 | 0.027466 | -0.10529 | -0.073243 | 0.036621 | 0.737 | 0.4715 | 0.13275 | 0.57678 | 0.23804 | 0.76447 | 121.9116 | 0.84229 | 121.9986 | 121.7972 | 121.8887 | 121.7239 | 121.7834 | -121.9299 | -121.962 | 121.8384 | 121.8933 | 121.138 | 84.7733
1901.9219 | 122.1222 | -121.8201 | 0.064087 | -0.028916 | 0.0020571 | 0.057112 | 0.053908 | 0.0019268 | -0.0070517 | -0.0023349 | -0.011261 | 2.1442e-05 | 0.071083 | 0.065696 | -0.012869 | 0.020935 | -0.0029202 | -0.65002 | -0.064087 | -121.8658 | 0.064087 | -121.106 | -121.8613 | -121.8475 | -37.4405 | -0.013733 | -121.8796 | 0.10529 | -121.051 | -121.6599 | -121.3165 | -0.045777 | -0.12817 | 0 | 0.71411 | -0.027466 | -0.041199 | 0.018311 | 0.004578 | -0.05951 | -0.07782 | 0.041199 | 0.76904 | 0.50354 | 0.16022 | 0.56305 | 0.21973 | 0.75989 | 121.9299 | 0.82855 | 121.9849 | 121.8018 | 121.8658 | 121.756 | 121.8063 | -121.9299 | -121.9437 | 121.8842 | 121.9254 | 121.17 | 84.3796
1903.6094 | 122.0123 | -121.8384 | 0.1236 | -0.013657 | 0.0014163 | 0.056898 | 0.057539 | 0.001286 | -0.0074789 | -0.0034031 | -0.0082093 | 0.0040802 | 0.072792 | 0.065055 | -0.013296 | 0.021149 | -0.0063382 | -0.63171 | -0.013733 | -121.9254 | -0.013733 | -121.2021 | -121.9437 | -121.9345 | -38.0722 | 0.045776 | -121.9345 | 0 | -121.1472 | -121.7697 | -121.4355 | -0.086975 | -0.13733 | -0.13733 | 0.63629 | -0.09613 | -0.10529 | -0.009155 | -0.018311 | -0.09613 | -0.07782 | -0.1236 | 0.69122 | 0.40283 | 0.068665 | 0.49896 | 0.1648 | 0.72327 | 121.9116 | 0.78735 | 121.9345 | 121.9116 | 121.9803 | 121.8246 | 121.8842 | -122.049 | -122.0581 | 121.8246 | 121.8384 | 121.2067 | 83.7662
1905.2969 | 122.1497 | -121.8201 | 0.073242 | -0.013657 | 0.0018435 | 0.057753 | 0.055403 | -0.0032 | -0.0079061 | -0.0014805 | -0.0051575 | 0.00066224 | 0.071938 | 0.066764 | -0.012655 | 0.020721 | -0.0029202 | -0.65918 | -0.050354 | -121.8887 | 0.045776 | -121.1197 | -121.875 | -121.8567 | -38.3743 | 0 | -121.907 | 0.11444 | -121.0281 | -121.6827 | -121.3074 | -0.068665 | -0.1236 | -0.027466 | 0.70038 | -0.036621 | -0.054932 | 0.032044 | 0.013733 | -0.086975 | -0.073242 | 0.041199 | 0.79193 | 0.5127 | 0.13733 | 0.59967 | 0.2243 | 0.76904 | 121.9345 | 0.87891 | 122.0215 | 121.8384 | 121.907 | 121.7697 | 121.8201 | -121.962 | -121.9803 | 121.8658 | 121.9345 | 121.1609 | 83.4457
1907.0469 | 121.9986 | -121.8521 | 0.11902 | -0.021286 | -0.0009335 | 0.056258 | 0.052412 | -0.0010638 | -0.0094015 | -0.0055393 | -0.0021057 | 0.0025848 | 0.073219 | 0.058219 | -0.012441 | 0.01944 | -0.0014248 | -0.6546 | -0.036621 | -121.9299 | -0.073242 | -121.2524 | -121.9482 | -121.9437 | -38.9786 | 0.041199 | -121.962 | -0.050354 | -121.1792 | -121.7926 | -121.431 | -0.07782 | -0.15564 | -0.19226 | 0.59967 | -0.091553 | -0.09613 | -0.013733 | -0.01831 | -0.10986 | -0.07782 | -0.16937 | 0.67291 | 0.42114 | 0.059509 | 0.53101 | 0.16937 | 0.67749 | 121.8567 | 0.78278 | 121.9116 | 121.8933 | 122.0032 | 121.8155 | 121.8933 | -122.049 | -122.081 | 121.7789 | 121.8018 | 121.1975 | 82.8735
1908.8125 | 122.0718 | -121.8201 | 0.082397 | -0.0060272 | -0.0011471 | 0.057539 | 0.052626 | -0.0012774 | -0.0066245 | -0.0044711 | -0.0051575 | -0.00040596 | 0.072151 | 0.056083 | -0.012655 | 0.020294 | -0.0029202 | -0.71411 | -0.068665 | -121.9116 | -0.004578 | -121.17 | -121.8933 | -121.9116 | -39.3494 | 0.009155 | -121.9116 | 0.041199 | -121.106 | -121.6965 | -121.3348 | -0.091553 | -0.15106 | -0.086975 | 0.65002 | -0.091553 | -0.073243 | 0 | 0.01831 | -0.091553 | -0.073242 | -0.041198 | 0.71411 | 0.48523 | 0.1236 | 0.57678 | 0.21515 | 0.74158 | 121.907 | 0.80566 | 121.9528 | 121.843 | 121.9208 | 121.7514 | 121.8292 | -121.994 | -121.994 | 121.8155 | 121.8613 | 121.106 | 82.4707
1910.5625 | 122.0901 | -121.843 | 0.086975 | -0.021286 | 0.0022709 | 0.055403 | 0.056258 | 0.0017132 | -0.0061971 | -0.0042575 | -0.0051575 | 0.0034392 | 0.072365 | 0.067405 | -0.012655 | 0.020081 | -0.0027066 | -0.74616 | -0.018311 | -121.9345 | -0.022888 | -121.225 | -121.9574 | -121.9391 | -39.8163 | 0.022888 | -121.9299 | 0.07782 | -121.0922 | -121.701 | -121.2662 | -0.091552 | -0.10529 | -0.10986 | 0.61798 | -0.09613 | -0.11444 | -0.004578 | -0.022888 | -0.086975 | -0.064087 | -0.009155 | 0.75073 | 0.57678 | 0.14191 | 0.66376 | 0.22888 | 0.70953 | 121.9116 | 0.83771 | 122.0078 | 121.9162 | 121.9528 | 121.8246 | 121.8658 | -122.0215 | -122.0169 | 121.8201 | 121.9208 | 121.0968 | 82.0267
1912.25 | 122.081 | -121.8246 | 0.073242 | -0.0060272 | 0.0020571 | 0.05583 | 0.05348 | -0.00063661 | -0.0091879 | -0.0023349 | -0.0021057 | -0.00019216 | 0.072151 | 0.060355 | -0.011587 | 0.018585 | -0.0016384 | -0.72784 | -0.059509 | -121.9116 | 0 | -121.1792 | -121.907 | -121.907 | -40.2374 | 0.009155 | -121.9345 | 0.036621 | -121.0831 | -121.701 | -121.3486 | -0.086975 | -0.13275 | -0.073242 | 0.64545 | -0.082397 | -0.082397 | 0.004578 | 0.004578 | -0.10986 | -0.064087 | -0.036621 | 0.74158 | 0.47607 | 0.1236 | 0.58594 | 0.23346 | 0.73242 | 121.9116 | 0.85144 | 121.9711 | 121.8521 | 121.9437 | 121.7651 | 121.8338 | -121.9849 | -122.0078 | 121.8246 | 121.8613 | 121.0968 | 81.5872
1914 | 122.1359 | -121.8246 | 0.068665 | -0.0060272 | -0.0032833 | 0.057112 | 0.054121 | -0.0017048 | -0.0074789 | -0.0016941 | -0.0021057 | 0.0015166 | 0.072578 | 0.061637 | -0.01351 | 0.019653 | -0.0020658 | -0.6134 | -0.059509 | -121.9025 | 0.068665 | -121.1014 | -121.8246 | -121.8384 | -40.5991 | -0.009155 | -121.9162 | 0.086975 | -121.0052 | -121.6324 | -121.3394 | -0.07782 | -0.12817 | 0 | 0.72327 | -0.013733 | 0 | 0.064087 | 0.07782 | -0.091553 | -0.07782 | 0.01831 | 0.8194 | 0.48523 | 0.19226 | 0.57678 | 0.28381 | 0.80109 | 121.9711 | 0.91095 | 122.0032 | 121.843 | 121.907 | 121.7651 | 121.8155 | -121.9711 | -121.9849 | 121.8933 | 121.9116 | 121.2112 | 81.2256
1915.75 | 122.0673 | -121.8658 | 0.10986 | -0.013657 | -0.0002927 | 0.056258 | 0.055403 | 0.00064519 | -0.0076925 | -0.0014805 | -0.0082093 | 0.0049346 | 0.071724 | 0.064841 | -0.015219 | 0.020935 | -0.0009976 | -0.63629 | -0.032043 | -121.9437 | -0.022888 | -121.2158 | -121.9345 | -121.9528 | -41.1621 | 0.041199 | -121.9437 | 0.022888 | -121.1014 | -121.7514 | -121.3989 | -0.07782 | -0.14191 | -0.13275 | 0.65002 | -0.086975 | -0.068664 | -0.009155 | 0.009156 | -0.07782 | -0.068664 | -0.086975 | 0.76447 | 0.46692 | 0.11444 | 0.54474 | 0.19226 | 0.72785 | 121.9208 | 0.84229 | 121.9666 | 121.9116 | 121.9849 | 121.8338 | 121.907 | -122.0535 | -122.0535 | 121.843 | 121.8887 | 121.2296 | 80.7037
1917.4375 | 122.0398 | -121.875 | 0.10071 | -0.021286 | -7.9104e-05 | 0.056471 | 0.055189 | 0.001286 | -0.0094015 | -0.0019077 | -0.011261 | 0.0023712 | 0.073219 | 0.058646 | -0.015005 | 0.022217 | -0.0020658 | -0.65918 | -0.013733 | -121.9437 | -0.073242 | -121.2799 | -121.9574 | -121.9849 | -41.5512 | 0.054932 | -121.9711 | -0.009155 | -121.1151 | -121.7651 | -121.431 | -0.068665 | -0.11444 | -0.17395 | 0.59509 | -0.10986 | -0.082397 | -0.041198 | -0.013732 | -0.09613 | -0.045776 | -0.10986 | 0.75989 | 0.44403 | 0.10986 | 0.54016 | 0.20599 | 0.66376 | 121.8704 | 0.85602 | 121.962 | 121.9299 | 122.0261 | 121.8613 | 121.9299 | -122.0444 | -122.0718 | 121.8018 | 121.8658 | 121.2158 | 80.3238
1919.1875 | 122.0947 | -121.8704 | 0.082397 | -0.0060272 | 0.0001345 | 0.054549 | 0.052626 | -0.0029864 | -0.0076925 | -0.0031895 | -0.0082093 | 0.00066224 | 0.070229 | 0.062278 | -0.012869 | 0.019653 | -0.003561 | -0.75073 | -0.050354 | -121.907 | -0.009155 | -121.1975 | -121.9162 | -121.8933 | -42.0273 | 0.009155 | -121.9528 | 0.041199 | -121.0693 | -121.7285 | -121.3898 | -0.036621 | -0.13275 | -0.091552 | 0.67291 | -0.022889 | -0.045777 | 0.013732 | -0.009156 | -0.082398 | -0.073242 | -0.041198 | 0.80109 | 0.48065 | 0.14191 | 0.56305 | 0.2243 | 0.70953 | 121.8979 | 0.88348 | 121.994 | 121.8567 | 121.962 | 121.8201 | 121.8796 | -121.9894 | -122.0352 | 121.8613 | 121.9116 | 121.1197 | 79.8431
1920.9375 | 122.0535 | -121.8567 | 0.10529 | -0.013657 | 0.0003483 | 0.056685 | 0.056044 | -0.0025592 | -0.0098287 | -0.0038303 | -0.0082093 | 0.0032256 | 0.071724 | 0.062918 | -0.013296 | 0.020294 | -0.0037748 | -0.65002 | -0.013733 | -121.9391 | -0.027466 | -121.2479 | -121.9299 | -121.9574 | -42.485 | 0.054932 | -121.9482 | 0.013733 | -121.0831 | -121.756 | -121.4081 | -0.082398 | -0.11902 | -0.13275 | 0.60882 | -0.10071 | -0.073243 | -0.01831 | 0.009155 | -0.091553 | -0.050354 | -0.091553 | 0.77362 | 0.44861 | 0.10071 | 0.54016 | 0.19226 | 0.69122 | 121.9116 | 0.86517 | 121.962 | 121.9254 | 122.0032 | 121.843 | 121.9116 | -122.0444 | -122.0535 | 121.8292 | 121.8704 | 121.2067 | 79.3716
1922.625 | 122.1268 | -121.8796 | 0.086975 | -0.013657 | -0.0020017 | 0.054335 | 0.056044 | 0.0010724 | -0.0081197 | -0.0014805 | -0.0051575 | 0.001944 | 0.072151 | 0.057364 | -0.013082 | 0.02179 | -0.0039884 | -0.63629 | -0.068665 | -121.9162 | 0.059509 | -121.1105 | -121.8521 | -121.8567 | -42.7048 | 0.013733 | -121.9208 | 0.091553 | -120.9961 | -121.6553 | -121.3577 | -0.036621 | -0.15564 | -0.027466 | 0.76904 | 0.022889 | 0.027466 | 0.05951 | 0.064087 | -0.041198 | -0.073242 | 0.004578 | 0.88348 | 0.52185 | 0.22431 | 0.56305 | 0.2655 | 0.80566 | 121.9757 | 0.92468 | 122.0123 | 121.8475 | 121.9345 | 121.8109 | 121.8933 | -122.0032 | -122.0078 | 121.9391 | 121.9711 | 121.2433 | 79.1748
1924.3125 | 122.0352 | -121.8521 | 0.11902 | -0.0060272 | 0.0016299 | 0.057539 | 0.056898 | 0.0027814 | -0.0072653 | -0.0027621 | -0.0051575 | 0.0023712 | 0.071938 | 0.059073 | -0.01351 | 0.02243 | -0.0033474 | -0.68665 | -0.036621 | -121.9482 | -0.018311 | -121.2296 | -121.9666 | -121.962 | -43.1351 | 0.032043 | -121.9711 | -0.009155 | -121.1105 | -121.7972 | -121.431 | -0.09613 | -0.15564 | -0.13733 | 0.62256 | -0.10986 | -0.11444 | -0.013733 | -0.018311 | -0.11902 | -0.086976 | -0.12817 | 0.74158 | 0.42114 | 0.054932 | 0.54016 | 0.17395 | 0.71869 | 121.9299 | 0.8606 | 121.962 | 121.9116 | 122.0032 | 121.8155 | 121.8842 | -122.0673 | -122.0901 | 121.8338 | 121.843 | 121.1655 | 78.717
1926.0625 | 122.1542 | -121.8384 | 0.082397 | -0.013657 | 0.0003483 | 0.057967 | 0.054549 | -0.0025592 | -0.0059835 | -0.00083947 | -0.0021057 | 0.00023504 | 0.072792 | 0.054374 | -0.012869 | 0.021362 | -0.0009976 | -0.72784 | -0.054932 | -121.9208 | 0.041199 | -121.1472 | -121.8842 | -121.8933 | -43.6157 | 0.013733 | -121.9208 | 0.10986 | -121.0052 | -121.6873 | -121.3623 | -0.082397 | -0.13733 | -0.041198 | 0.69122 | -0.054932 | -0.045776 | 0.027465 | 0.036621 | -0.082397 | -0.068664 | 0.027466 | 0.83313 | 0.47607 | 0.15106 | 0.55847 | 0.23346 | 0.77362 | 121.962 | 0.91553 | 122.0306 | 121.8658 | 121.9345 | 121.7834 | 121.8521 | -122.0032 | -122.0032 | 121.8796 | 121.9482 | 121.1105 | 78.2227
1927.8125 | 122.0718 | -121.8842 | 0.091553 | -0.013657 | 0.0012027 | 0.056258 | 0.056471 | 0.0010724 | -0.0066245 | -0.00083947 | -0.0021057 | 0.0017304 | 0.071724 | 0.058646 | -0.012228 | 0.023712 | -0.0048428 | -0.68665 | -0.032043 | -121.9391 | -0.022888 | -121.225 | -121.9299 | -121.9666 | -44.0002 | 0.032043 | -121.9528 | 0.004578 | -121.0648 | -121.7468 | -121.4584 | -0.054932 | -0.1236 | -0.11444 | 0.65918 | -0.082398 | -0.045777 | -0.027466 | 0.009155 | -0.068665 | -0.05951 | -0.086975 | 0.8194 | 0.42572 | 0.13733 | 0.49439 | 0.20599 | 0.71411 | 121.9162 | 0.88806 | 121.9574 | 121.907 | 121.9849 | 121.8521 | 121.9162 | -122.0306 | -122.0444 | 121.8613 | 121.8887 | 121.1975 | 77.8839
1929.5781 | 122.1588 | -121.843 | 0.082397 | -0.013657 | 0.0018435 | 0.057326 | 0.054121 | 0.007481 | -0.0068381 | -0.0036167 | -0.0051575 | 0.001944 | 0.071938 | 0.058219 | -0.01351 | 0.021576 | -0.0009976 | -0.75531 | -0.050354 | -121.907 | 0.041199 | -121.1563 | -121.8979 | -121.9025 | -44.4946 | -0.004578 | -121.9299 | 0.10529 | -121.0098 | -121.701 | -121.376 | -0.064086 | -0.13275 | -0.041198 | 0.68665 | -0.059509 | -0.054931 | 0.004577 | 0.009155 | -0.086975 | -0.086975 | 0.022889 | 0.83313 | 0.46692 | 0.14191 | 0.55389 | 0.22888 | 0.75073 | 121.9482 | 0.9201 | 122.0352 | 121.8567 | 121.9254 | 121.7926 | 121.8384 | -121.9894 | -122.0123 | 121.8842 | 121.9482 | 121.0876 | 77.3483
1931.2656 | 122.1359 | -121.8567 | 0.073242 | -0.021286 | 0.0018435 | 0.057112 | 0.054121 | -0.0059772 | -0.0087607 | -0.0051121 | -0.0051575 | 2.1442e-05 | 0.069374 | 0.064414 | -0.01351 | 0.019867 | 0.0002842 | -0.75531 | -0.073242 | -121.8979 | 0.054932 | -121.1288 | -121.8796 | -121.8842 | -44.8425 | 0.004578 | -121.9391 | 0.07782 | -121.0007 | -121.6827 | -121.3852 | -0.041199 | -0.14648 | -0.01831 | 0.72784 | -0.027466 | -0.022889 | 0.013733 | 0.01831 | -0.082398 | -0.068664 | 0.004578 | 0.85602 | 0.4715 | 0.17395 | 0.55389 | 0.25635 | 0.76904 | 121.9528 | 0.93842 | 122.0169 | 121.8246 | 121.9437 | 121.7834 | 121.8613 | -121.9711 | -122.0123 | 121.9116 | 121.9345 | 121.1014 | 77.0142
1933.0312 | 122.1634 | -121.8475 | 0.082397 | -0.021286 | 0.0001345 | 0.058607 | 0.052626 | -0.00085021 | -0.0061971 | -0.0036167 | -0.0082093 | 0.001944 | 0.070869 | 0.063346 | -0.01116 | 0.01944 | 0.0032748 | -0.75073 | -0.064087 | -121.9162 | 0.054932 | -121.1426 | -121.8887 | -121.8933 | -45.2866 | 0.009155 | -121.9299 | 0.10529 | -120.9869 | -121.6965 | -121.3806 | -0.068665 | -0.14648 | -0.027465 | 0.70496 | -0.045777 | -0.041199 | 0.022888 | 0.027466 | -0.082398 | -0.073242 | 0.022889 | 0.8606 | 0.46692 | 0.15106 | 0.54932 | 0.23346 | 0.77362 | 121.9711 | 0.94299 | 122.0352 | 121.8521 | 121.9391 | 121.7834 | 121.8567 | -121.9986 | -122.0123 | 121.9025 | 121.9528 | 121.0968 | 76.561
1934.7969 | 122.0535 | -121.875 | 0.086975 | -0.028916 | 0.0033389 | 0.057539 | 0.056685 | -0.0029864 | -0.0064109 | -0.0012669 | -0.0051575 | 0.0027984 | 0.068947 | 0.064841 | -0.013723 | 0.02179 | 7.04e-05 | -0.83313 | -0.022888 | -121.9528 | -0.086975 | -121.2936 | -122.0078 | -122.0123 | -45.8359 | 0.036621 | -121.9757 | 0.004578 | -121.1014 | -121.8018 | -121.4676 | -0.07782 | -0.10986 | -0.17395 | 0.58136 | -0.13733 | -0.13275 | -0.059509 | -0.054931 | -0.10071 | -0.050354 | -0.082397 | 0.77362 | 0.40741 | 0.073242 | 0.50812 | 0.17395 | 0.65918 | 121.8658 | 0.87433 | 121.9803 | 121.9299 | 122.0123 | 121.8521 | 121.9116 | -122.0398 | -122.0627 | 121.788 | 121.8796 | 121.0419 | 76.0391
1936.4844 | 122.0352 | -121.907 | 0.10529 | -0.013657 | -0.0011471 | 0.054335 | 0.054335 | 0.0027814 | -0.0072653 | -0.0016941 | -0.0051575 | 0.0015166 | 0.068733 | 0.060569 | -0.010305 | 0.019226 | -0.0031338 | -0.74616 | -0.027466 | -121.9894 | -0.073242 | -121.2799 | -121.9803 | -122.0078 | -46.3669 | 0.045776 | -122.0032 | -0.064087 | -121.0968 | -121.7972 | -121.4951 | -0.082398 | -0.13275 | -0.17853 | 0.62714 | -0.10071 | -0.073243 | -0.01831 | 0.009155 | -0.096131 | -0.05951 | -0.16937 | 0.81024 | 0.41199 | 0.10986 | 0.50812 | 0.20599 | 0.70953 | 121.9162 | 0.90637 | 121.9391 | 121.962 | 122.049 | 121.8796 | 121.9528 | -122.0947 | -122.1085 | 121.8338 | 121.843 | 121.1609 | 75.5402
1938.25 | 122.168 | -121.8567 | 0.082397 | -0.013657 | 0.0031253 | 0.057112 | 0.053694 | -0.00020941 | -0.0074789 | -0.0019077 | -0.0051575 | -0.00061956 | 0.072578 | 0.064414 | -0.012228 | 0.02243 | -0.0003568 | -0.76446 | -0.054932 | -121.9116 | 0.041199 | -121.1609 | -121.9116 | -121.8887 | -46.6232 | 0.004578 | -121.9254 | 0.10529 | -120.9869 | -121.6827 | -121.312 | -0.054932 | -0.13733 | -0.041198 | 0.6958 | -0.032044 | -0.054932 | 0.022888 | 0 | -0.068665 | -0.077819 | 0.022889 | 0.86975 | 0.54474 | 0.17395 | 0.6134 | 0.24262 | 0.75073 | 121.9528 | 0.93842 | 122.0306 | 121.8567 | 121.9299 | 121.8018 | 121.8613 | -121.994 | -122.0078 | 121.8979 | 121.962 | 121.0922 | 75.2335
1940.0156 | 122.0352 | -121.8704 | 0.10071 | -0.0060272 | 0.0007755 | 0.057753 | 0.056471 | 0.00021799 | -0.0083335 | -0.0038303 | -0.0021057 | 0.003012 | 0.072792 | 0.065909 | -0.013082 | 0.023926 | -0.0020658 | -0.737 | -0.013733 | -121.994 | -0.032043 | -121.2433 | -121.9894 | -121.9849 | -47.1588 | 0.027466 | -121.9482 | 0 | -121.0922 | -121.8109 | -121.4493 | -0.1236 | -0.11444 | -0.13275 | 0.62714 | -0.11444 | -0.11902 | 0.009156 | 0.004578 | -0.07782 | -0.073242 | -0.10071 | 0.7782 | 0.42114 | 0.059509 | 0.49896 | 0.13733 | 0.75073 | 121.962 | 0.85602 | 121.9482 | 121.9803 | 121.9757 | 121.8567 | 121.8979 | -122.0947 | -122.0489 | 121.8384 | 121.8704 | 121.1334 | 74.7116
1941.7031 | 122.1909 | -121.8521 | 0.073242 | -0.013657 | -0.0013607 | 0.055189 | 0.053694 | -0.0040546 | -0.0085471 | -0.0044711 | -0.0082093 | -0.00019216 | 0.073219 | 0.067618 | -0.013723 | 0.019653 | -0.0020658 | -0.76446 | -0.064087 | -121.9528 | 0.045776 | -121.1472 | -121.8567 | -121.875 | -47.4976 | 0 | -121.9666 | 0.091553 | -120.932 | -121.6461 | -121.3394 | -0.10071 | -0.13733 | -0.027466 | 0.70496 | -0.022888 | -0.004577 | 0.07782 | 0.096131 | -0.11444 | -0.073242 | 0.018311 | 0.92011 | 0.5127 | 0.20599 | 0.62714 | 0.32044 | 0.80566 | 121.9986 | 1.0345 | 122.0581 | 121.8887 | 121.9666 | 121.788 | 121.8521 | -122.0261 | -122.0398 | 121.8979 | 121.9437 | 121.0876 | 74.3546
1943.4062 | 122.1771 | -121.8658 | 0.086975 | -0.013657 | -0.0020017 | 0.055403 | 0.05348 | -0.0019184 | -0.0081197 | 0.00044213 | -0.0021057 | 0.00023504 | 0.071724 | 0.061423 | -0.013296 | 0.020508 | -0.0009976 | -0.70038 | -0.073242 | -121.9482 | 0.064087 | -121.1334 | -121.8613 | -121.8796 | -47.9187 | -0.004578 | -121.9528 | 0.086975 | -120.9412 | -121.6644 | -121.4035 | -0.082397 | -0.16022 | -0.022888 | 0.73242 | -0.013733 | 0.004578 | 0.068664 | 0.086975 | -0.086975 | -0.091553 | 0 | 0.92468 | 0.46234 | 0.20142 | 0.54932 | 0.28839 | 0.81482 | 122.0123 | 1.0117 | 122.0398 | 121.875 | 121.9482 | 121.7926 | 121.8613 | -122.0352 | -122.0398 | 121.9299 | 121.9528 | 121.1655 | 73.9471
1945.1562 | 122.1405 | -121.8704 | 0.086975 | -0.0060272 | 0.0007755 | 0.056471 | 0.054121 | 0.00021799 | -0.0079061 | -0.0021213 | -0.011261 | 0.0015166 | 0.072151 | 0.059073 | -0.01415 | 0.018799 | -0.0029202 | -0.81024 | -0.068665 | -121.9254 | 0.054932 | -121.17 | -121.9116 | -121.8979 | -48.3215 | 0.009155 | -121.9574 | 0.086975 | -120.9961 | -121.7102 | -121.4172 | -0.054932 | -0.15564 | -0.032043 | 0.70038 | -0.027466 | -0.041199 | 0.027466 | 0.013733 | -0.086975 | -0.07782 | 0 | 0.87433 | 0.45319 | 0.16022 | 0.54016 | 0.24719 | 0.75531 | 121.9803 | 0.9613 | 122.0444 | 121.8567 | 121.9666 | 121.8018 | 121.8796 | -122.0123 | -122.0444 | 121.9254 | 121.9574 | 121.0602 | 73.5489
1946.8438 | 122.0215 | -121.907 | 0.11902 | -0.0060272 | 0.0012027 | 0.057112 | 0.05583 | 0.0021406 | -0.0059835 | -0.0027621 | -0.0051575 | 0.004721 | 0.071724 | 0.059287 | -0.014791 | 0.021149 | -0.0018522 | -0.82855 | -0.018311 | -122.0032 | -0.073242 | -121.3303 | -122.0398 | -122.0398 | -49.0952 | 0.045776 | -121.9757 | -0.036621 | -121.106 | -121.8658 | -121.4905 | -0.096131 | -0.13733 | -0.19226 | 0.57678 | -0.13275 | -0.13275 | -0.036621 | -0.036621 | -0.068665 | -0.073243 | -0.15564 | 0.80109 | 0.41656 | 0.041198 | 0.48523 | 0.10986 | 0.67291 | 121.9299 | 0.86975 | 121.9391 | 121.9849 | 122.0215 | 121.8887 | 121.9528 | -122.1222 | -122.0947 | 121.8338 | 121.8704 | 121.0785 | 72.8119
1948.6094 | 122.1909 | -121.8613 | 0.082397 | -0.013657 | -0.0013607 | 0.055403 | 0.052412 | -0.0044818 | -0.0074789 | -0.0053257 | -0.0082093 | 0.00044864 | 0.070442 | 0.061637 | -0.012228 | 0.021576 | -0.000784 | -0.72327 | -0.07782 | -121.9666 | 0.068665 | -121.1426 | -121.875 | -121.8704 | -49.3881 | 0.009155 | -121.9666 | 0.086975 | -120.9366 | -121.6736 | -121.376 | -0.10529 | -0.16022 | -0.013732 | 0.71869 | -0.009155 | -0.013733 | 0.096131 | 0.091553 | -0.10529 | -0.073242 | 0.004578 | 0.92468 | 0.48523 | 0.18768 | 0.59052 | 0.29297 | 0.82398 | 122.0352 | 1.03 | 122.0535 | 121.8887 | 121.9757 | 121.7834 | 121.8704 | -122.049 | -122.049 | 121.9299 | 121.9482 | 121.138 | 72.4731
1950.2969 | 122.0901 | -121.8979 | 0.1236 | -0.013657 | -0.0013607 | 0.056471 | 0.054335 | -0.0029864 | -0.0053427 | -0.0016941 | -0.0051575 | 0.0017304 | 0.071938 | 0.057151 | -0.014791 | 0.021362 | -0.0018522 | -0.76446 | -0.009155 | -121.994 | -0.045776 | -121.2753 | -121.9666 | -121.9894 | -50.0061 | 0.032043 | -121.9849 | 0.004578 | -121.019 | -121.788 | -121.431 | -0.096131 | -0.13275 | -0.16937 | 0.62256 | -0.091553 | -0.068665 | 0.004578 | 0.027466 | -0.086975 | -0.091553 | -0.11902 | 0.87891 | 0.46692 | 0.10986 | 0.55389 | 0.19684 | 0.71869 | 121.9482 | 0.96588 | 121.9894 | 121.9849 | 122.0169 | 121.8887 | 121.9299 | -122.1176 | -122.1085 | 121.8521 | 121.9025 | 121.1334 | 71.8918
1952.0625 | 122.0581 | -121.9025 | 0.1236 | -0.013657 | 0.0026981 | 0.056685 | 0.055617 | 0.0010724 | -0.0079061 | -0.0040439 | -0.0051575 | 0.001944 | 0.072792 | 0.063987 | -0.013937 | 0.022858 | 0.0028476 | -0.81024 | -0.032043 | -121.9803 | -0.050354 | -121.2891 | -122.0352 | -122.0215 | -50.4959 | 0.050354 | -121.9849 | -0.032043 | -121.0648 | -121.843 | -121.4767 | -0.07782 | -0.15564 | -0.17395 | 0.6134 | -0.11902 | -0.13275 | -0.041198 | -0.054931 | -0.082397 | -0.073242 | -0.15564 | 0.83771 | 0.42572 | 0.059509 | 0.50812 | 0.14191 | 0.69122 | 121.9299 | 0.92011 | 121.9528 | 121.9482 | 122.0352 | 121.8704 | 121.9528 | -122.1039 | -122.1085 | 121.8521 | 121.8704 | 121.0922 | 71.4066
1953.75 | 122.0901 | -121.9025 | 0.11444 | -0.0060272 | 0.0020571 | 0.056044 | 0.054549 | 0.0023542 | -0.010897 | -0.0038303 | -0.0082093 | 0.003653 | 0.073433 | 0.063987 | -0.01351 | 0.021149 | 0.0017794 | -0.77362 | -0.009155 | -121.9849 | -0.032043 | -121.2753 | -121.9666 | -121.994 | -50.9033 | 0.050354 | -121.994 | 0.013733 | -120.9915 | -121.788 | -121.3898 | -0.082397 | -0.1236 | -0.14648 | 0.62714 | -0.091553 | -0.064087 | -0.009156 | 0.01831 | -0.091553 | -0.064087 | -0.10071 | 0.91095 | 0.5127 | 0.11444 | 0.60425 | 0.20599 | 0.70953 | 121.9528 | 1.0025 | 122.0078 | 121.9757 | 122.0444 | 121.8933 | 121.9528 | -122.0993 | -122.1085 | 121.8704 | 121.9162 | 121.1288 | 70.9991
1955.5 | 122.0947 | -121.8979 | 0.10529 | -0.013657 | -0.0041379 | 0.055403 | 0.054976 | -0.0046954 | -0.011324 | -0.0016941 | -0.0051575 | 0.0034392 | 0.072151 | 0.062918 | -0.011587 | 0.020935 | -0.003561 | -0.79193 | -0.009155 | -122.0215 | -0.068665 | -121.2982 | -121.9849 | -122.0078 | -51.3611 | 0.041199 | -122.0078 | -0.013733 | -121.0052 | -121.7926 | -121.4722 | -0.1236 | -0.11444 | -0.17395 | 0.59967 | -0.10986 | -0.086975 | 0.013733 | 0.036621 | -0.10986 | -0.064087 | -0.11902 | 0.89264 | 0.42572 | 0.10528 | 0.53558 | 0.21515 | 0.72327 | 121.9528 | 1.0025 | 121.994 | 122.0123 | 122.049 | 121.8887 | 121.9391 | -122.1268 | -122.113 | 121.8292 | 121.8842 | 121.106 | 70.5368
1957.1875 | 122.1909 | -121.8796 | 0.10071 | -0.013657 | -0.0054197 | 0.053267 | 0.051558 | -0.001491 | -0.0089743 | -0.0046847 | -0.0051575 | 0.00023504 | 0.071938 | 0.057578 | -0.012655 | 0.019012 | -0.0048428 | -0.77362 | -0.059509 | -121.9711 | 0.068665 | -121.106 | -121.8613 | -121.8796 | -51.7593 | -0.004578 | -121.9437 | 0.07782 | -120.8954 | -121.6599 | -121.4035 | -0.091552 | -0.16022 | -0.032043 | 0.77362 | 0 | 0.018311 | 0.091552 | 0.10986 | -0.064087 | -0.10529 | -0.022888 | 0.98419 | 0.47607 | 0.21973 | 0.54016 | 0.28381 | 0.86517 | 122.0398 | 1.0483 | 122.0215 | 121.9116 | 121.9391 | 121.8201 | 121.875 | -122.0718 | -122.0444 | 121.9482 | 121.9574 | 121.106 | 70.1202
1958.9375 | 122.2092 | -121.8842 | 0.086975 | -0.021286 | -0.0007199 | 0.056044 | 0.053694 | -0.0034136 | -0.0089743 | -0.0031895 | -0.0082093 | -0.00019216 | 0.070869 | 0.054801 | -0.013723 | 0.019653 | -0.0003568 | -0.83313 | -0.059509 | -121.9208 | 0.004578 | -121.1884 | -121.9025 | -121.9162 | -52.1988 | 0.004578 | -121.9757 | 0.086975 | -120.8862 | -121.6644 | -121.376 | -0.036621 | -0.14648 | -0.082397 | 0.6958 | -0.032044 | -0.018311 | 0.004577 | 0.01831 | -0.091553 | -0.082397 | 0 | 0.99793 | 0.50812 | 0.21973 | 0.59967 | 0.31128 | 0.73242 | 121.9254 | 1.0895 | 122.0627 | 121.8613 | 121.9803 | 121.8246 | 121.8887 | -122.0078 | -122.0627 | 121.8887 | 121.9711 | 121.051 | 69.6854
1960.6406 | 122.0718 | -121.9299 | 0.11902 | -0.0060272 | -0.0017881 | 0.055403 | 0.054335 | -0.002132 | -0.0089743 | -0.0034031 | -0.011261 | 0.003012 | 0.071297 | 0.062491 | -0.01351 | 0.022003 | -0.0005704 | -0.8194 | -0.032043 | -121.9894 | -0.059509 | -121.2982 | -122.0169 | -122.0078 | -52.8442 | 0.045776 | -122.0169 | -0.050354 | -121.019 | -121.8109 | -121.4493 | -0.059509 | -0.15106 | -0.17853 | 0.63171 | -0.077819 | -0.086975 | -0.01831 | -0.027466 | -0.086975 | -0.073243 | -0.16937 | 0.91095 | 0.48065 | 0.11902 | 0.56763 | 0.20599 | 0.69122 | 121.9299 | 0.99793 | 121.9666 | 121.9574 | 122.0627 | 121.8979 | 121.9757 | -122.1085 | -122.1359 | 121.8704 | 121.8796 | 121.1105 | 69.0857
1962.4062 | 122.0993 | -121.8979 | 0.11444 | -0.0060272 | -0.0009335 | 0.057112 | 0.054762 | 0.0010724 | -0.0098287 | -0.0029759 | -0.0021057 | 0.0038666 | 0.071083 | 0.072532 | -0.015005 | 0.02179 | -0.0012112 | -0.82398 | -0.050354 | -121.9894 | -0.004578 | -121.2479 | -121.9986 | -121.994 | -53.2883 | 0.032043 | -121.9757 | 0.013733 | -121.0144 | -121.8246 | -121.4539 | -0.091553 | -0.16479 | -0.11902 | 0.65002 | -0.096131 | -0.10071 | -0.004578 | -0.009155 | -0.07782 | -0.082398 | -0.10071 | 0.88348 | 0.44403 | 0.073242 | 0.52185 | 0.15106 | 0.74158 | 121.9849 | 0.9613 | 121.9894 | 121.9391 | 122.0078 | 121.8475 | 121.9299 | -122.1039 | -122.0901 | 121.8933 | 121.9116 | 121.0739 | 68.6096
1964.1406 | 122.1405 | -121.8979 | 0.09613 | -0.021286 | -0.0002927 | 0.056898 | 0.051772 | -0.003841 | -0.0061971 | -0.0016941 | -0.0082093 | 0.00023504 | 0.071297 | 0.062064 | -0.012869 | 0.021149 | -0.0016384 | -0.89264 | -0.054932 | -121.962 | -0.009155 | -121.2433 | -121.9711 | -121.9666 | -53.7827 | 0.018311 | -121.9894 | 0.041199 | -120.9412 | -121.7514 | -121.4676 | -0.064087 | -0.15106 | -0.10528 | 0.6546 | -0.068665 | -0.073242 | -0.004578 | -0.009155 | -0.091553 | -0.077819 | -0.054931 | 0.95673 | 0.4303 | 0.14648 | 0.52185 | 0.23804 | 0.71869 | 121.9528 | 1.0483 | 122.0306 | 121.907 | 122.0078 | 121.843 | 121.9162 | -122.0581 | -122.0856 | 121.8887 | 121.9391 | 121.0052 | 68.1152
1965.8281 | 122.2046 | -121.9025 | 0.09613 | -0.0060272 | -0.0024289 | 0.056044 | 0.051772 | -0.001491 | -0.0068381 | -0.0038303 | -0.011261 | -0.00061956 | 0.070442 | 0.054801 | -0.013937 | 0.020294 | -0.0031338 | -0.80109 | -0.059509 | -121.9528 | 0.059509 | -121.1334 | -121.8613 | -121.8842 | -54.1443 | -0.004578 | -121.9574 | 0.091553 | -120.845 | -121.6599 | -121.431 | -0.050354 | -0.15564 | -0.036621 | 0.76904 | 0.018311 | 0.041199 | 0.068665 | 0.091553 | -0.054931 | -0.10071 | -0.004577 | 1.0574 | 0.4715 | 0.24262 | 0.52643 | 0.29755 | 0.8194 | 122.0123 | 1.1124 | 122.049 | 121.8933 | 121.9528 | 121.843 | 121.8979 | -122.049 | -122.0535 | 121.962 | 121.994 | 121.1014 | 67.7582
1967.5781 | 122.1222 | -121.9208 | 0.091553 | -0.013657 | 0.0005619 | 0.057112 | 0.058821 | 0.00043159 | -0.0091879 | -0.00083947 | -0.0051575 | 0.0027984 | 0.073647 | 0.056723 | -0.015219 | 0.020935 | -0.0003568 | -0.93842 | -0.022888 | -121.9757 | -0.059509 | -121.3165 | -122.0398 | -122.0352 | -54.8676 | 0.032043 | -122.0078 | 0.018311 | -120.9595 | -121.7972 | -121.4767 | -0.054932 | -0.11444 | -0.15106 | 0.60425 | -0.11444 | -0.11902 | -0.059509 | -0.064087 | -0.086975 | -0.05951 | -0.073242 | 0.9613 | 0.44403 | 0.1236 | 0.531 | 0.21057 | 0.65918 | 121.9162 | 1.0483 | 122.0261 | 121.9528 | 122.0398 | 121.8979 | 121.9528 | -122.0673 | -122.0993 | 121.8613 | 121.9391 | 120.9824 | 67.0532
1969.2812 | 122.081 | -121.9345 | 0.10986 | 0.0016023 | 0.0007755 | 0.057967 | 0.05583 | 0.0017132 | -0.0087607 | -0.0059665 | -0.0051575 | 0.0040802 | 0.074928 | 0.065055 | -0.013082 | 0.021576 | -0.0039884 | -0.93842 | -0.018311 | -121.994 | -0.082397 | -121.3715 | -122.0764 | -122.0627 | -55.3986 | 0.036621 | -122.0032 | -0.032043 | -121.0144 | -121.8613 | -121.4767 | -0.05951 | -0.12817 | -0.19226 | 0.56305 | -0.12817 | -0.14191 | -0.068664 | -0.082397 | -0.068665 | -0.073242 | -0.14191 | 0.92011 | 0.45776 | 0.073242 | 0.52643 | 0.14191 | 0.62256 | 121.9116 | 0.98877 | 121.9711 | 121.9757 | 122.0398 | 121.9162 | 121.9711 | -122.1039 | -122.113 | 121.8521 | 121.9025 | 120.9961 | 66.5359
1971.0312 | 122.1954 | -121.8979 | 0.082397 | -0.013657 | -0.0030697 | 0.055403 | 0.051558 | -0.001491 | -0.0089743 | -0.0029759 | -0.011261 | 0.001303 | 0.072365 | 0.061423 | -0.012014 | 0.02179 | -0.0014248 | -0.81024 | -0.059509 | -121.9574 | 0.068665 | -121.1472 | -121.8842 | -121.8979 | -55.5725 | 0 | -121.9803 | 0.07782 | -120.8267 | -121.6827 | -121.3211 | -0.059509 | -0.14191 | -0.013732 | 0.75073 | 0 | 0.013733 | 0.059509 | 0.073242 | -0.082398 | -0.082397 | -0.004577 | 1.0712 | 0.57678 | 0.21515 | 0.65918 | 0.29755 | 0.81024 | 122.0261 | 1.1536 | 122.0581 | 121.8979 | 121.9803 | 121.8384 | 121.8979 | -122.0398 | -122.0627 | 121.9666 | 121.9757 | 121.0876 | 66.3254
1972.7656 | 122.113 | -121.9345 | 0.11902 | -0.021286 | -0.0017881 | 0.053694 | 0.05348 | -0.00042301 | -0.0083335 | -0.0029759 | -0.0021057 | 0.0021576 | 0.072792 | 0.062705 | -0.013082 | 0.020935 | -0.0014248 | -0.85144 | -0.004578 | -122.0398 | -0.073242 | -121.3165 | -122.0261 | -122.0444 | -56.3049 | 0.032043 | -122.0215 | -0.027466 | -120.9412 | -121.8063 | -121.4951 | -0.10529 | -0.1236 | -0.19226 | 0.61798 | -0.10986 | -0.091553 | -0.004578 | 0.013733 | -0.086975 | -0.086976 | -0.14649 | 0.99335 | 0.43945 | 0.12817 | 0.52643 | 0.21515 | 0.72327 | 121.9666 | 1.0803 | 121.994 | 122.0352 | 122.0535 | 121.9299 | 121.9666 | -122.1588 | -122.1405 | 121.8613 | 121.907 | 121.0831 | 65.6296
1974.5312 | 122.1954 | -121.875 | 0.086975 | -0.0060272 | 0.0014163 | 0.056471 | 0.053053 | 0.004704 | -0.0085471 | -0.0027621 | -0.0082093 | 0.0015166 | 0.073006 | 0.063987 | -0.013937 | 0.022217 | -0.0020658 | -0.90179 | -0.064087 | -121.9528 | 0.041199 | -121.2067 | -121.9482 | -121.9254 | -56.7352 | 0.013733 | -121.9849 | 0.10986 | -120.8359 | -121.7148 | -121.3669 | -0.07782 | -0.15106 | -0.045776 | 0.66833 | -0.050354 | -0.073242 | 0.027466 | 0.004578 | -0.10986 | -0.073242 | 0.022888 | 1.0391 | 0.50812 | 0.16022 | 0.61798 | 0.27008 | 0.74616 | 121.994 | 1.149 | 122.0947 | 121.8887 | 121.9986 | 121.8109 | 121.8887 | -122.0398 | -122.0718 | 121.9162 | 121.9849 | 120.9732 | 65.1398
1976.2344 | 122.1817 | -121.8887 | 0.091553 | -0.0060272 | -0.0041379 | 0.056471 | 0.052626 | -0.001491 | -0.0098287 | -0.0016941 | -0.0051575 | 0.001303 | 0.07151 | 0.057578 | -0.01351 | 0.019653 | -0.0022794 | -0.92468 | -0.064087 | -121.9849 | 0.004578 | -121.2433 | -121.962 | -121.9711 | -57.1747 | 0.004578 | -122.0169 | 0.041199 | -120.8588 | -121.7239 | -121.4172 | -0.09613 | -0.15564 | -0.086975 | 0.64545 | -0.082397 | -0.073242 | 0.013733 | 0.022888 | -0.12817 | -0.086975 | -0.050354 | 1.03 | 0.4715 | 0.16479 | 0.59967 | 0.29297 | 0.74158 | 121.9894 | 1.1581 | 122.0581 | 121.9208 | 122.0215 | 121.8246 | 121.8933 | -122.0764 | -122.1085 | 121.8933 | 121.9299 | 120.9641 | 64.7141
1977.9844 | 122.1268 | -121.9254 | 0.11902 | 0.0016023 | 0.0007755 | 0.054976 | 0.054549 | -0.002132 | -0.0074789 | -0.0016941 | 0.0009461 | 0.0032256 | 0.072365 | 0.068259 | -0.015005 | 0.020721 | -0.0003568 | -0.84686 | -0.018311 | -122.0169 | -0.036621 | -121.3074 | -121.994 | -122.0169 | -57.6462 | 0.036621 | -122.0078 | 0.009155 | -120.9045 | -121.7789 | -121.4584 | -0.091553 | -0.13733 | -0.15564 | 0.61798 | -0.091553 | -0.068665 | 0 | 0.022888 | -0.082397 | -0.082398 | -0.10986 | 1.0208 | 0.46692 | 0.14648 | 0.54932 | 0.22888 | 0.70953 | 121.9803 | 1.1032 | 122.0169 | 121.9986 | 122.0444 | 121.907 | 121.962 | -122.1359 | -122.1268 | 121.8887 | 121.9345 | 121.0785 | 64.2792
1979.7344 | 122.0718 | -121.9345 | 0.10986 | -0.0060272 | 0.0018435 | 0.055189 | 0.056258 | 0.00043159 | -0.0072653 | -0.0021213 | -0.0051575 | 0.0034392 | 0.072151 | 0.054801 | -0.015432 | 0.023071 | -0.0016384 | -0.92926 | -0.013733 | -121.9849 | -0.059509 | -121.3303 | -122.0673 | -122.0627 | -58.1955 | 0.045776 | -122.0032 | -0.041199 | -120.9641 | -121.8704 | -121.5179 | -0.050354 | -0.1236 | -0.16937 | 0.60425 | -0.12817 | -0.13275 | -0.07782 | -0.082398 | -0.068665 | -0.064087 | -0.15106 | 0.97046 | 0.41657 | 0.064087 | 0.48523 | 0.13275 | 0.6546 | 121.9254 | 1.0391 | 121.962 | 121.9711 | 122.049 | 121.9208 | 121.9803 | -122.0947 | -122.113 | 121.875 | 121.8933 | 121.0052 | 63.739
1981.4844 | 122.2092 | -121.9208 | 0.073242 | -0.013657 | -0.0034971 | 0.05284 | 0.053694 | -0.0040546 | -0.0061971 | -0.0034031 | -0.0082093 | -0.00061956 | 0.072578 | 0.059928 | -0.012655 | 0.019653 | -0.0046292 | -0.93384 | -0.059509 | -122.0032 | 0.004578 | -121.2296 | -121.9528 | -121.9391 | -58.3923 | 0 | -122.0215 | 0.068665 | -120.7993 | -121.6965 | -121.3989 | -0.082398 | -0.13275 | -0.068664 | 0.69122 | -0.018311 | -0.032044 | 0.064087 | 0.050354 | -0.10071 | -0.073242 | -0.004577 | 1.1215 | 0.52185 | 0.2243 | 0.62256 | 0.32501 | 0.77362 | 122.0078 | 1.2222 | 122.0901 | 121.9437 | 122.0215 | 121.8613 | 121.9208 | -122.0764 | -122.0947 | 121.9254 | 121.9894 | 120.9869 | 63.5284
1983.2344 | 122.113 | -121.9299 | 0.10071 | -0.013657 | -0.0007199 | 0.054335 | 0.05284 | 0.00085879 | -0.0076925 | -0.0014805 | -0.0051575 | 0.003012 | 0.072792 | 0.059501 | -0.014578 | 0.02179 | -0.0027066 | -0.88806 | -0.022888 | -122.0261 | -0.064087 | -121.3348 | -122.0123 | -122.049 | -58.992 | 0.022888 | -122.0352 | -0.018311 | -120.8679 | -121.8018 | -121.4859 | -0.09613 | -0.1236 | -0.1648 | 0.59509 | -0.11902 | -0.082397 | -0.022888 | 0.013733 | -0.10529 | -0.07782 | -0.11902 | 1.062 | 0.44403 | 0.12817 | 0.54932 | 0.23346 | 0.69122 | 121.962 | 1.1673 | 122.0169 | 122.0032 | 122.0581 | 121.907 | 121.9528 | -122.1268 | -122.1359 | 121.8658 | 121.9116 | 121.0419 | 62.9379
1984.9844 | 122.113 | -121.9391 | 0.10529 | -0.013657 | -0.0009335 | 0.055189 | 0.053908 | 0.0010724 | -0.0094015 | -0.0057529 | -0.0082093 | 0.0015166 | 0.069801 | 0.064627 | -0.013082 | 0.021149 | -0.0020658 | -0.90637 | -0.027466 | -122.0398 | -0.073242 | -121.3257 | -122.0123 | -122.0352 | -59.3491 | 0.027466 | -122.0352 | -0.036621 | -120.8633 | -121.8063 | -121.4813 | -0.10071 | -0.13275 | -0.17853 | 0.6134 | -0.09613 | -0.073242 | 0.004578 | 0.027466 | -0.09613 | -0.07782 | -0.14191 | 1.0757 | 0.45776 | 0.13275 | 0.55389 | 0.22888 | 0.71411 | 121.9666 | 1.1719 | 121.9986 | 122.0123 | 122.0627 | 121.9116 | 121.9666 | -122.1451 | -122.1405 | 121.8658 | 121.9025 | 121.0327 | 62.59
1986.6719 | 122.1313 | -121.9345 | 0.10071 | -0.021286 | 0.0031253 | 0.056685 | 0.056471 | 0.0036358 | -0.0087607 | -0.0040439 | -0.0051575 | 0.0023712 | 0.073006 | 0.065696 | -0.013082 | 0.020081 | -0.0022794 | -1.0208 | -0.018311 | -122.0032 | -0.073242 | -121.3348 | -122.0718 | -122.0627 | -59.7198 | 0.022888 | -122.0398 | 0 | -120.8817 | -121.8246 | -121.4905 | -0.068665 | -0.11902 | -0.17395 | 0.59967 | -0.12817 | -0.13733 | -0.059509 | -0.068664 | -0.10529 | -0.07782 | -0.10071 | 1.0529 | 0.44403 | 0.10986 | 0.54932 | 0.21515 | 0.66833 | 121.9299 | 1.1581 | 122.0398 | 121.9849 | 122.0627 | 121.9162 | 121.9574 | -122.1039 | -122.1405 | 121.8613 | 121.9345 | 120.9137 | 62.2147
1988.4219 | 122.1359 | -121.9208 | 0.10986 | -0.021286 | -0.0022153 | 0.053908 | 0.051772 | 0.00043159 | -0.0087607 | -0.0036167 | -0.0082093 | 0.0023712 | 0.070442 | 0.059714 | -0.013723 | 0.019226 | -0.0022794 | -0.86517 | -0.054932 | -122.0169 | 0.022888 | -121.225 | -121.9437 | -121.962 | -60.1089 | 0.032043 | -122.0032 | 0 | -120.8176 | -121.756 | -121.4813 | -0.096131 | -0.16479 | -0.086975 | 0.6958 | -0.041199 | -0.022889 | 0.054932 | 0.073242 | -0.082398 | -0.07782 | -0.10986 | 1.1032 | 0.43945 | 0.16479 | 0.52185 | 0.24719 | 0.79193 | 122.0398 | 1.1856 | 122.0032 | 121.962 | 122.0352 | 121.8658 | 121.9528 | -122.1268 | -122.113 | 121.9437 | 121.9208 | 121.0556 | 61.8118
1990.125 | 122.1085 | -121.9666 | 0.11902 | -0.021286 | -0.0015743 | 0.054121 | 0.054121 | -0.0044818 | -0.0079061 | -0.00083947 | -0.011261 | 0.0032256 | 0.072578 | 0.057151 | -0.011801 | 0.020294 | -0.003561 | -0.93384 | -0.004578 | -122.0123 | -0.07782 | -121.3577 | -122.0215 | -122.0581 | -60.4248 | 0.032043 | -122.049 | -0.059509 | -120.8588 | -121.8292 | -121.5179 | -0.045776 | -0.1236 | -0.19684 | 0.60883 | -0.091552 | -0.054931 | -0.045776 | -0.009155 | -0.082397 | -0.086976 | -0.17853 | 1.1078 | 0.44861 | 0.13733 | 0.53101 | 0.21973 | 0.6546 | 121.9345 | 1.1902 | 121.9894 | 122.0078 | 122.081 | 121.962 | 121.9986 | -122.1313 | -122.168 | 121.8887 | 121.907 | 121.0327 | 61.5417
1991.875 | 122.1863 | -121.907 | 0.09613 | -0.021286 | 0.0039799 | 0.055189 | 0.054976 | 0.0025678 | -0.0047019 | -0.0034031 | -0.0051575 | 0.0021576 | 0.070869 | 0.063987 | -0.013723 | 0.023712 | 7.04e-05 | -1.0391 | -0.013733 | -122.0352 | -0.022888 | -121.3028 | -122.0352 | -122.0169 | -60.8551 | 0.027466 | -121.9986 | 0.064087 | -120.7581 | -121.7606 | -121.4218 | -0.12817 | -0.10986 | -0.11902 | 0.60425 | -0.10986 | -0.12817 | 0.01831 | 0 | -0.091553 | -0.068664 | -0.032043 | 1.149 | 0.48523 | 0.14648 | 0.57678 | 0.23804 | 0.73242 | 122.0123 | 1.2405 | 122.0627 | 122.0215 | 122.0261 | 121.8933 | 121.9345 | -122.1313 | -122.0947 | 121.8842 | 121.9711 | 120.8679 | 61.0519
1993.625 | 122.1542 | -121.9345 | 0.086975 | -0.013657 | -0.0005063 | 0.056471 | 0.055403 | 0.001286 | -0.0094015 | -0.0046847 | -0.0021057 | 0.0015166 | 0.075142 | 0.065268 | -0.012441 | 0.019653 | -0.0009976 | -0.92468 | -0.032043 | -122.0306 | -0.036621 | -121.2799 | -121.9894 | -122.0352 | -61.2762 | 0.054932 | -122.0306 | 0.018311 | -120.7809 | -121.7926 | -121.463 | -0.096131 | -0.11902 | -0.1236 | 0.6546 | -0.10071 | -0.054932 | -0.004577 | 0.041199 | -0.096131 | -0.032043 | -0.068664 | 1.1536 | 0.4715 | 0.14191 | 0.56763 | 0.23804 | 0.75073 | 121.994 | 1.2497 | 122.049 | 121.9986 | 122.0856 | 121.9025 | 121.9894 | -122.1176 | -122.1176 | 121.8979 | 121.9528 | 121.0098 | 60.6583
1995.375 | 122.2137 | -121.907 | 0.086975 | -0.013657 | -0.0024289 | 0.056044 | 0.051772 | -0.0032 | -0.010256 | -0.0046847 | -0.0082093 | -0.001474 | 0.07621 | 0.062491 | -0.011587 | 0.018372 | -0.0016384 | -0.90179 | -0.064087 | -121.9894 | 0.054932 | -121.1563 | -121.8842 | -121.9162 | -61.5509 | 0 | -122.0078 | 0.07782 | -120.6711 | -121.6736 | -121.4035 | -0.082398 | -0.15106 | -0.032043 | 0.75073 | -0.009156 | 0.022888 | 0.073242 | 0.10529 | -0.10071 | -0.086975 | -0.009155 | 1.236 | 0.50354 | 0.23346 | 0.60425 | 0.33417 | 0.83313 | 122.0444 | 1.3367 | 122.0856 | 121.9254 | 122.0078 | 121.843 | 121.907 | -122.0764 | -122.0947 | 121.962 | 121.9849 | 121.0052 | 60.3561
1997.125 | 122.1085 | -121.9528 | 0.10529 | -0.013657 | 0.0018435 | 0.056898 | 0.057539 | 0.0040632 | -0.0068381 | -0.0044711 | -0.0051575 | 0.0027984 | 0.07151 | 0.064627 | -0.015005 | 0.022003 | -0.0018522 | -0.97504 | -0.036621 | -122.0032 | -0.032043 | -121.2891 | -122.0215 | -122.049 | -62.0728 | 0.036621 | -122.0581 | -0.013733 | -120.8038 | -121.8475 | -121.5546 | -0.050354 | -0.14191 | -0.13733 | 0.66376 | -0.09613 | -0.068664 | -0.045776 | -0.01831 | -0.10528 | -0.068665 | -0.11902 | 1.149 | 0.39826 | 0.10529 | 0.50354 | 0.21057 | 0.71411 | 121.9711 | 1.2543 | 122.0444 | 121.9666 | 122.0947 | 121.9162 | 121.9894 | -122.1085 | -122.1634 | 121.9208 | 121.9391 | 120.9778 | 59.8801
1998.8125 | 122.1497 | -121.9299 | 0.09613 | -0.0060272 | 0.0003483 | 0.056258 | 0.053694 | 0.0027814 | -0.010043 | -0.0034031 | -0.0051575 | 0.0034392 | 0.074287 | 0.068259 | -0.013723 | 0.021576 | -0.0005704 | -0.94299 | -0.022888 | -122.0215 | -0.022888 | -121.2708 | -122.0123 | -122.0215 | -62.4802 | 0.018311 | -122.0627 | 0.022888 | -120.726 | -121.7789 | -121.5042 | -0.091552 | -0.11902 | -0.11902 | 0.65918 | -0.091552 | -0.082397 | 0 | 0.009155 | -0.13275 | -0.077819 | -0.073242 | 1.2039 | 0.42572 | 0.15106 | 0.55847 | 0.28381 | 0.75073 | 121.9986 | 1.3367 | 122.0856 | 121.9986 | 122.081 | 121.907 | 121.9482 | -122.1176 | -122.1588 | 121.907 | 121.9528 | 120.9869 | 59.4498
2000.5781 | 122.2229 | -121.9025 | 0.086975 | -0.021286 | -0.0002927 | 0.056258 | 0.054762 | -0.0010638 | -0.0070517 | -0.0029759 | -0.0082093 | 0.0023712 | 0.069801 | 0.059928 | -0.012014 | 0.020935 | -0.0009976 | -1.0666 | -0.027466 | -122.0123 | -0.004578 | -121.2982 | -122.0123 | -122.0123 | -62.7777 | 0.022888 | -122.0169 | 0.086975 | -120.6757 | -121.7377 | -121.463 | -0.10986 | -0.11444 | -0.091553 | 0.60425 | -0.10986 | -0.10986 | 0 | 0 | -0.11444 | -0.064087 | 0 | 1.2268 | 0.43945 | 0.16479 | 0.55389 | 0.27924 | 0.71411 | 122.0078 | 1.3412 | 122.1039 | 121.9849 | 122.0398 | 121.875 | 121.9254 | -122.0993 | -122.1039 | 121.8979 | 121.9894 | 120.8359 | 59.1248
2002.2812 | 122.1863 | -121.9482 | 0.10071 | -0.0060272 | -0.0043515 | 0.056898 | 0.053053 | 0.00043159 | -0.0081197 | -0.0025485 | -0.0051575 | 0.00066224 | 0.071297 | 0.057364 | -0.011801 | 0.019226 | 0.0017794 | -1.0757 | -0.054932 | -122.0169 | -0.013733 | -121.2799 | -121.9986 | -121.994 | -63.176 | 0.004578 | -122.0261 | 0.022888 | -120.6802 | -121.756 | -121.5134 | -0.068665 | -0.15564 | -0.11444 | 0.66833 | -0.045777 | -0.050354 | 0.022888 | 0.018311 | -0.07782 | -0.09613 | -0.07782 | 1.268 | 0.43487 | 0.19226 | 0.51269 | 0.27008 | 0.737 | 122.0032 | 1.3458 | 122.0489 | 121.962 | 122.0306 | 121.8933 | 121.9528 | -122.1176 | -122.1268 | 121.9345 | 121.9711 | 120.8725 | 58.7723
2004.0312 | 122.1405 | -121.9574 | 0.11444 | -0.0060272 | -0.0022153 | 0.056044 | 0.054549 | 4.192e-06 | -0.0089743 | -0.0027621 | -0.0051575 | 0.003653 | 0.07386 | 0.057792 | -0.014791 | 0.02179 | -0.0033474 | -0.97504 | -0.009155 | -122.049 | -0.054932 | -121.3257 | -122.0123 | -122.0398 | -63.588 | 0.032043 | -122.0215 | -0.009155 | -120.694 | -121.7926 | -121.5363 | -0.091553 | -0.1236 | -0.16937 | 0.63171 | -0.082398 | -0.054932 | 0.009155 | 0.036621 | -0.064087 | -0.082398 | -0.1236 | 1.2634 | 0.42114 | 0.16479 | 0.48523 | 0.22888 | 0.72327 | 121.994 | 1.3275 | 122.0123 | 122.0398 | 122.0535 | 121.9482 | 121.9894 | -122.1634 | -122.1359 | 121.9025 | 121.9482 | 120.9824 | 58.3694
2005.7812 | 122.2321 | -121.9345 | 0.073242 | -0.0060272 | -0.0024289 | 0.054762 | 0.051344 | 0.001286 | -0.0089743 | -0.0034031 | -0.0021057 | 0.00066224 | 0.071938 | 0.056937 | -0.015219 | 0.01944 | -0.0005704 | -0.96588 | -0.073242 | -122.0169 | 0.064087 | -121.1792 | -121.8979 | -121.9162 | -63.6108 | 0 | -121.9849 | 0.091553 | -120.5704 | -121.669 | -121.4401 | -0.082398 | -0.14648 | -0.009155 | 0.75531 | 0.01831 | 0.036621 | 0.10071 | 0.11902 | -0.050354 | -0.073242 | 0.018311 | 1.3641 | 0.49438 | 0.2655 | 0.54474 | 0.31586 | 0.83771 | 122.081 | 1.4145 | 122.0764 | 121.9437 | 121.9849 | 121.8613 | 121.9345 | -122.0901 | -122.0581 | 121.9986 | 122.0261 | 120.9686 | 58.3237
2007.5312 | 122.1268 | -121.9299 | 0.10986 | -0.021286 | -0.0005063 | 0.057112 | 0.055617 | 0.00085879 | -0.0089743 | -0.0048985 | -0.0051575 | 0.004721 | 0.071938 | 0.056296 | -0.01415 | 0.02243 | -0.0018522 | -1.0025 | -0.013733 | -122.0444 | -0.018311 | -121.2799 | -122.0123 | -122.0261 | -64.0778 | 0.022888 | -122.0444 | 0.022888 | -120.6711 | -121.788 | -121.5179 | -0.11444 | -0.1236 | -0.12817 | 0.65002 | -0.09613 | -0.082397 | 0.018311 | 0.032044 | -0.11444 | -0.086975 | -0.086975 | 1.2588 | 0.41199 | 0.14191 | 0.52643 | 0.25635 | 0.76447 | 122.0261 | 1.3733 | 122.0673 | 122.0306 | 122.0673 | 121.9162 | 121.9528 | -122.1542 | -122.1542 | 121.9116 | 121.9528 | 120.9274 | 57.8522
2009.2812 | 122.1497 | -121.962 | 0.10529 | -0.0060272 | -0.0002927 | 0.057753 | 0.053267 | -0.0010638 | -0.0079061 | -0.0021213 | -0.0051575 | 2.1442e-05 | 0.071083 | 0.060569 | -0.014791 | 0.019867 | -0.004202 | -0.96588 | -0.054932 | -122.0123 | 0.041199 | -121.2296 | -121.9391 | -121.9711 | -64.4165 | 0.004578 | -122.0306 | 0.018311 | -120.6116 | -121.7606 | -121.5042 | -0.050354 | -0.16022 | -0.064087 | 0.73242 | -0.009155 | 0.022888 | 0.041199 | 0.073242 | -0.068665 | -0.10071 | -0.086975 | 1.3504 | 0.45776 | 0.20142 | 0.52643 | 0.27008 | 0.78278 | 122.0535 | 1.4191 | 122.049 | 121.9574 | 122.0352 | 121.907 | 121.9666 | -122.1176 | -122.1359 | 122.0032 | 121.9803 | 120.9961 | 57.5455
2011.0312 | 122.2321 | -121.9116 | 0.086975 | 0.0016023 | 0.0001345 | 0.056258 | 0.053694 | -0.0023456 | -0.0072653 | -0.0027621 | -0.0021057 | -0.00019216 | 0.07151 | 0.058646 | -0.01415 | 0.020508 | 0.0002842 | -1.0803 | -0.054932 | -121.994 | 0.045776 | -121.2433 | -121.9528 | -121.9803 | -64.7232 | -0.018311 | -122.0261 | 0.10071 | -120.5704 | -121.7194 | -121.4035 | -0.082398 | -0.14191 | -0.041199 | 0.66833 | -0.068665 | -0.041199 | 0.013733 | 0.041199 | -0.11444 | -0.10529 | 0.013733 | 1.3412 | 0.50812 | 0.19226 | 0.62256 | 0.3067 | 0.75073 | 122.0398 | 1.4557 | 122.1268 | 121.9391 | 122.0078 | 121.8567 | 121.8933 | -122.081 | -122.113 | 121.9574 | 122.0123 | 120.8313 | 57.1884
2012.7812 | 122.1588 | -121.9482 | 0.10986 | -0.0060272 | -0.0007199 | 0.057112 | 0.054549 | 0.0023542 | -0.0085471 | -0.0036167 | -0.0051575 | 0.0038666 | 0.074287 | 0.060782 | -0.012228 | 0.019012 | 0.000925 | -1.0162 | -0.032043 | -122.0169 | -0.013733 | -121.2936 | -122.0261 | -122.0306 | -65.1764 | 0.018311 | -122.049 | 0.032043 | -120.5978 | -121.7926 | -121.4767 | -0.068665 | -0.14191 | -0.1236 | 0.6546 | -0.082398 | -0.07782 | -0.013733 | -0.009155 | -0.10071 | -0.091552 | -0.07782 | 1.3504 | 0.4715 | 0.15564 | 0.5722 | 0.25635 | 0.72327 | 122.0032 | 1.4511 | 122.081 | 121.9849 | 122.0673 | 121.9162 | 121.9666 | -122.1268 | -122.1588 | 121.9345 | 121.9803 | 120.932 | 56.7718
2014.4688 | 122.1405 | -121.9666 | 0.11902 | -0.013657 | 0.0005619 | 0.056685 | 0.054549 | -0.00085021 | -0.0068381 | -0.0016941 | -0.0082093 | 0.0032256 | 0.073219 | 0.060355 | -0.015005 | 0.021576 | -0.0005704 | -1.0345 | -0.027466 | -122.0169 | -0.004578 | -121.2982 | -122.0123 | -122.0444 | -65.4282 | 0.022888 | -122.0444 | 0.009155 | -120.6024 | -121.788 | -121.4813 | -0.050354 | -0.14649 | -0.1236 | 0.66833 | -0.07782 | -0.045776 | -0.027466 | 0.004578 | -0.07782 | -0.096131 | -0.10986 | 1.3641 | 0.48523 | 0.17853 | 0.56305 | 0.25635 | 0.71869 | 122.0123 | 1.442 | 122.0535 | 121.9894 | 122.0673 | 121.9391 | 121.9894 | -122.1359 | -122.1634 | 121.962 | 121.9757 | 120.932 | 56.5384
2016.2188 | 122.1954 | -121.9391 | 0.09613 | -0.013657 | -0.0015743 | 0.055617 | 0.053053 | -0.0017048 | -0.0081197 | -0.0029759 | -0.0082093 | 0.00087584 | 0.072365 | 0.05416 | -0.013082 | 0.020081 | -0.0014248 | -1.1124 | -0.054932 | -122.0352 | -0.027466 | -121.2845 | -121.9986 | -121.994 | -65.6525 | 0.018311 | -122.0169 | 0.041199 | -120.5292 | -121.7331 | -121.4355 | -0.09613 | -0.15106 | -0.1236 | 0.6546 | -0.054932 | -0.059509 | 0.041198 | 0.036621 | -0.07782 | -0.077819 | -0.054931 | 1.4099 | 0.50354 | 0.20599 | 0.58136 | 0.28381 | 0.75073 | 122.0078 | 1.4877 | 122.0581 | 121.9803 | 122.0352 | 121.8842 | 121.9574 | -122.1313 | -122.113 | 121.9116 | 121.9803 | 120.8267 | 56.2866
2017.9844 | 122.1359 | -121.9711 | 0.10986 | -0.021286 | 0.0020571 | 0.056044 | 0.055403 | 0.00064519 | -0.0057699 | -0.0016941 | -0.0082093 | 0.003653 | 0.072151 | 0.060996 | -0.012441 | 0.021149 | 0.002634 | -1.1536 | -0.022888 | -122.0352 | -0.082397 | -121.3715 | -122.0901 | -122.0901 | -66.1011 | 0.032043 | -122.0398 | -0.018311 | -120.6162 | -121.8521 | -121.4905 | -0.064087 | -0.13275 | -0.19226 | 0.59967 | -0.11902 | -0.11902 | -0.054932 | -0.054932 | -0.068665 | -0.07782 | -0.12817 | 1.355 | 0.48065 | 0.11902 | 0.54932 | 0.18768 | 0.66376 | 121.9528 | 1.4236 | 122.0215 | 122.0123 | 122.0718 | 121.9482 | 122.0032 | -122.1451 | -122.1497 | 121.8887 | 121.9528 | 120.8176 | 55.8701
2019.6719 | 122.0993 | -121.9574 | 0.11902 | -0.013657 | -0.0002927 | 0.057112 | 0.056258 | 0.0021406 | -0.010043 | -0.0027621 | -0.0021057 | 0.0025848 | 0.074715 | 0.062491 | -0.012228 | 0.020935 | -0.0031338 | -1.1673 | -0.009155 | -122.0581 | -0.07782 | -121.4035 | -122.113 | -122.113 | -66.4169 | 0.041199 | -122.0673 | -0.027466 | -120.6207 | -121.8613 | -121.4951 | -0.10071 | -0.12817 | -0.19684 | 0.55389 | -0.15564 | -0.15564 | -0.054932 | -0.054932 | -0.10986 | -0.07782 | -0.14649 | 1.3367 | 0.46234 | 0.09613 | 0.5722 | 0.20599 | 0.6546 | 121.9803 | 1.4465 | 122.0398 | 122.0489 | 122.1085 | 121.9482 | 121.9986 | -122.1771 | -122.1863 | 121.8796 | 121.9299 | 120.7901 | 55.5405
2021.4219 | 122.0901 | -121.9803 | 0.1236 | -0.013657 | -7.9104e-05 | 0.055403 | 0.057326 | 0.00021799 | -0.0059835 | -0.0044711 | -0.0082093 | 0.0040802 | 0.074715 | 0.062705 | -0.01351 | 0.020935 | -0.0033474 | -1.1261 | -0.013733 | -122.0535 | -0.059509 | -121.3486 | -122.0856 | -122.0901 | -66.5634 | 0.022888 | -122.0764 | -0.032043 | -120.607 | -121.875 | -121.4859 | -0.073242 | -0.13733 | -0.1831 | 0.63171 | -0.10986 | -0.10528 | -0.036621 | -0.032043 | -0.09613 | -0.10071 | -0.15564 | 1.3733 | 0.49439 | 0.10529 | 0.59051 | 0.20142 | 0.70496 | 121.994 | 1.4694 | 122.0444 | 122.0398 | 122.0993 | 121.9666 | 122.0032 | -122.1771 | -122.2 | 121.9208 | 121.9482 | 120.8542 | 55.4169
2023.1719 | 122.2 | -121.9528 | 0.091553 | -0.021286 | -7.9104e-05 | 0.056258 | 0.051772 | -0.00020941 | -0.0076925 | -0.0040439 | -0.0051575 | 0.0015166 | 0.07151 | 0.057792 | -0.01351 | 0.020508 | -0.0001432 | -1.149 | -0.059509 | -122.0169 | 0.013733 | -121.257 | -121.9803 | -121.9803 | -66.6275 | 0.009155 | -122.0306 | 0.054932 | -120.4788 | -121.7377 | -121.3943 | -0.064087 | -0.15106 | -0.07782 | 0.6958 | -0.027466 | -0.027466 | 0.036621 | 0.036621 | -0.07782 | -0.082398 | -0.036621 | 1.474 | 0.55847 | 0.21515 | 0.63629 | 0.29297 | 0.75989 | 122.0306 | 1.5518 | 122.0856 | 121.9574 | 122.0398 | 121.8933 | 121.962 | -122.1085 | -122.1222 | 121.9666 | 122.0078 | 120.8038 | 55.3253
2024.8594 | 122.1085 | -121.9757 | 0.10071 | -0.0060272 | 0.0026981 | 0.05583 | 0.055617 | 0.0034222 | -0.0066245 | -0.0044711 | -0.0051575 | 0.0017304 | 0.073433 | 0.063773 | -0.015432 | 0.021576 | -0.000784 | -1.1902 | -0.022888 | -122.0444 | -0.09613 | -121.4172 | -122.1497 | -122.1313 | -67.012 | 0.032043 | -122.0718 | -0.041199 | -120.5978 | -121.8613 | -121.5042 | -0.068665 | -0.1236 | -0.19684 | 0.55847 | -0.15564 | -0.17395 | -0.086975 | -0.10529 | -0.09613 | -0.068665 | -0.14191 | 1.3779 | 0.4715 | 0.11444 | 0.56763 | 0.21057 | 0.62714 | 121.9482 | 1.474 | 122.0306 | 122.0215 | 122.1039 | 121.9528 | 122.0078 | -122.1451 | -122.1725 | 121.8796 | 121.9345 | 120.7855 | 54.9637
2026.6094 | 122.1817 | -121.9574 | 0.082397 | -0.021286 | 0.0012027 | 0.056685 | 0.055189 | 0.0057722 | -0.0083335 | -0.0029759 | -0.0051575 | 0.0021576 | 0.072365 | 0.060782 | -0.012869 | 0.023071 | -0.0009976 | -1.2222 | -0.018311 | -122.0627 | -0.068665 | -121.3715 | -122.0901 | -122.081 | -67.0853 | 0.032043 | -122.0398 | 0.013733 | -120.5521 | -121.7926 | -121.4584 | -0.10529 | -0.10071 | -0.15106 | 0.58594 | -0.1236 | -0.13275 | -0.018311 | -0.027466 | -0.082398 | -0.050354 | -0.068664 | 1.4053 | 0.49896 | 0.16479 | 0.58136 | 0.24719 | 0.69122 | 121.994 | 1.4877 | 122.0535 | 122.0444 | 122.0718 | 121.9391 | 121.9894 | -122.1451 | -122.1222 | 121.8887 | 121.9711 | 120.7352 | 54.8721
2028.2969 | 122.1588 | -121.962 | 0.10529 | -0.013657 | -7.9104e-05 | 0.056898 | 0.056685 | 0.0025678 | -0.0079061 | -0.0038303 | -0.0051575 | 0.0015166 | 0.072792 | 0.063132 | -0.013937 | 0.02243 | -0.0014248 | -1.2177 | -0.013733 | -122.0581 | -0.068665 | -121.3715 | -122.0947 | -122.0947 | -67.2592 | 0.032043 | -122.049 | 0.018311 | -120.5612 | -121.8201 | -121.4447 | -0.09613 | -0.11902 | -0.17395 | 0.59051 | -0.13275 | -0.13275 | -0.036622 | -0.036622 | -0.086975 | -0.073243 | -0.086975 | 1.4008 | 0.51727 | 0.14191 | 0.60425 | 0.22888 | 0.68664 | 121.9894 | 1.4877 | 122.0673 | 122.0444 | 122.081 | 121.9482 | 121.994 | -122.1634 | -122.1542 | 121.8933 | 121.9803 | 120.7443 | 54.7028
2030.0469 | 122.2366 | -121.9162 | 0.091553 | -0.013657 | -0.0039243 | 0.054762 | 0.051772 | -0.0023456 | -0.0083335 | -0.0044711 | -0.0051575 | -0.00061956 | 0.071297 | 0.057792 | -0.013937 | 0.018585 | -0.0014248 | -1.0849 | -0.064087 | -122.0261 | 0.054932 | -121.1792 | -121.907 | -121.9528 | -67.3004 | -0.022888 | -122.0261 | 0.073242 | -120.4422 | -121.669 | -121.3852 | -0.10986 | -0.15564 | -0.036621 | 0.737 | -0.036621 | 0.009156 | 0.073242 | 0.11902 | -0.10986 | -0.11444 | -0.018311 | 1.474 | 0.53101 | 0.24719 | 0.64087 | 0.35706 | 0.84686 | 122.081 | 1.5839 | 122.0993 | 121.962 | 122.0032 | 121.8521 | 121.8933 | -122.1176 | -122.1176 | 121.9711 | 121.9894 | 120.8313 | 54.6158
2031.7969 | 122.1405 | -121.9574 | 0.091553 | -0.021286 | 0.0022709 | 0.054121 | 0.054762 | 0.0021406 | -0.0076925 | -0.0042575 | -0.0051575 | 0.0034392 | 0.074074 | 0.062705 | -0.015219 | 0.020081 | -0.0027066 | -1.2405 | -0.013733 | -122.0398 | -0.086975 | -121.3943 | -122.0764 | -122.0901 | -67.4515 | 0.050354 | -122.0764 | 0 | -120.575 | -121.8521 | -121.4813 | -0.082398 | -0.10529 | -0.17853 | 0.56305 | -0.13275 | -0.11902 | -0.050354 | -0.036621 | -0.11902 | -0.041199 | -0.091553 | 1.3824 | 0.47607 | 0.10528 | 0.59509 | 0.2243 | 0.64545 | 121.9528 | 1.5015 | 122.0764 | 122.0261 | 122.1268 | 121.9437 | 122.0078 | -122.1313 | -122.168 | 121.8704 | 121.9574 | 120.7169 | 54.5059
2033.5312 | 122.2046 | -121.9666 | 0.07782 | -0.0060272 | -0.0013607 | 0.054335 | 0.056044 | -0.00042301 | -0.0066245 | -0.0042575 | -0.0082093 | -0.00061956 | 0.071297 | 0.059073 | -0.010305 | 0.01944 | -0.0020658 | -1.2039 | -0.059509 | -122.0261 | 0.009155 | -121.2753 | -122.0169 | -121.994 | -67.5659 | -0.013733 | -122.0398 | 0.036621 | -120.5292 | -121.7422 | -121.4218 | -0.059509 | -0.13733 | -0.068665 | 0.69122 | -0.027466 | -0.050354 | 0.032043 | 0.009155 | -0.073242 | -0.091553 | -0.041199 | 1.4374 | 0.54474 | 0.2243 | 0.61798 | 0.29755 | 0.75073 | 122.0352 | 1.5106 | 122.0764 | 121.9666 | 122.0261 | 121.907 | 121.9528 | -122.1039 | -122.1176 | 121.9757 | 122.0032 | 120.7626 | 54.4006
2035.2656 | 122.1909 | -121.9574 | 0.073242 | -0.021286 | -0.0005063 | 0.056258 | 0.054335 | -0.0012774 | -0.0072653 | -0.0034031 | -0.0051575 | 0.0023712 | 0.07386 | 0.059073 | -0.013296 | 0.021149 | 0.0017794 | -1.2222 | -0.045776 | -122.0215 | -0.027466 | -121.3028 | -122.0123 | -122.0123 | -67.7353 | 0.013733 | -122.0535 | 0.013733 | -120.5338 | -121.7468 | -121.431 | -0.064087 | -0.11902 | -0.10071 | 0.6546 | -0.054932 | -0.054932 | 0.009155 | 0.009155 | -0.096131 | -0.059509 | -0.059509 | 1.4236 | 0.52643 | 0.21057 | 0.62256 | 0.3067 | 0.71869 | 121.994 | 1.5198 | 122.0673 | 121.9757 | 122.0673 | 121.9116 | 121.9711 | -122.0947 | -122.1268 | 121.9299 | 121.9711 | 120.7352 | 54.2221
2037.0469 | 122.2778 | -121.9299 | 0.086975 | -0.013657 | -0.0039243 | 0.056471 | 0.052199 | -0.001491 | -0.0085471 | -0.0025485 | -0.0082093 | 0.001303 | 0.072365 | 0.057578 | -0.016714 | 0.020935 | -0.004202 | -1.1307 | -0.059509 | -122.0352 | 0.041199 | -121.225 | -121.9391 | -121.9482 | -67.717 | -0.013733 | -122.0123 | 0.10986 | -120.4422 | -121.6553 | -121.3715 | -0.10529 | -0.14648 | -0.045776 | 0.70496 | -0.01831 | -0.009155 | 0.086975 | 0.09613 | -0.082397 | -0.10071 | 0.022888 | 1.4877 | 0.55847 | 0.27466 | 0.64087 | 0.35706 | 0.81024 | 122.0764 | 1.5701 | 122.1222 | 121.9757 | 121.9986 | 121.8704 | 121.9162 | -122.1222 | -122.0993 | 121.9711 | 122.0398 | 120.7993 | 54.213
2038.7344 | 122.1405 | -121.9803 | 0.09613 | 0.0016023 | 0.0016299 | 0.055617 | 0.054121 | 0.0025678 | -0.0079061 | -0.0027621 | -0.0082093 | 0.003653 | 0.068092 | 0.059714 | -0.01415 | 0.020935 | -0.002493 | -1.1673 | -0.013733 | -122.0581 | -0.018311 | -121.3028 | -122.049 | -122.0581 | -68.0649 | 0.018311 | -122.049 | 0 | -120.5795 | -121.8155 | -121.4767 | -0.077819 | -0.10986 | -0.11444 | 0.67749 | -0.077819 | -0.068664 | 0 | 0.009155 | -0.068664 | -0.077819 | -0.09613 | 1.4008 | 0.50354 | 0.1648 | 0.5722 | 0.23346 | 0.75531 | 122.0398 | 1.4694 | 122.049 | 122.0444 | 122.0673 | 121.9666 | 121.9986 | -122.1542 | -122.1451 | 121.962 | 121.9803 | 120.813 | 53.9154
2040.4844 | 122.2458 | -121.9437 | 0.082397 | -0.013657 | -0.0015743 | 0.057112 | 0.053053 | -0.0051226 | -0.0091879 | -0.0029759 | -0.011261 | 0.00023504 | 0.071938 | 0.055442 | -0.014578 | 0.020721 | -0.0018522 | -1.1993 | -0.045776 | -122.0352 | 0.013733 | -121.257 | -121.9528 | -121.9757 | -68.0603 | 0.013733 | -122.049 | 0.082397 | -120.4697 | -121.6827 | -121.3577 | -0.091552 | -0.12817 | -0.068664 | 0.68665 | -0.032043 | -0.009155 | 0.059509 | 0.082397 | -0.10529 | -0.068664 | 0 | 1.474 | 0.58594 | 0.26093 | 0.69122 | 0.36621 | 0.7782 | 122.049 | 1.5793 | 122.1313 | 121.9894 | 122.0627 | 121.8979 | 121.9574 | -122.1176 | -122.1313 | 121.9574 | 122.0261 | 120.7443 | 53.8834
2042.2344 | 122.1085 | -121.9849 | 0.10986 | -0.021286 | 0.0031253 | 0.056471 | 0.056258 | 0.0014996 | -0.0076925 | -0.00041227 | 0.0009461 | 0.003012 | 0.074287 | 0.062064 | -0.013937 | 0.022217 | -0.0014248 | -1.2268 | -0.018311 | -122.0673 | -0.054932 | -121.376 | -122.0856 | -122.0993 | -68.3258 | 0.041199 | -122.0673 | -0.022888 | -120.6162 | -121.8521 | -121.4767 | -0.082398 | -0.12817 | -0.16479 | 0.60883 | -0.11444 | -0.10071 | -0.032043 | -0.01831 | -0.082398 | -0.068664 | -0.13275 | 1.3687 | 0.50812 | 0.13275 | 0.59051 | 0.21515 | 0.69122 | 122.0123 | 1.4511 | 122.0444 | 122.049 | 122.1085 | 121.9666 | 122.0261 | -122.1771 | -122.1771 | 121.9299 | 121.962 | 120.7581 | 53.6591
2044 | 122.1176 | -121.994 | 0.10529 | -0.0060272 | 0.0026981 | 0.05818 | 0.055403 | -0.00085021 | -0.0083335 | -0.0040439 | -0.0082093 | 0.0021576 | 0.073433 | 0.064627 | -0.014364 | 0.020508 | -0.0003568 | -1.2817 | -0.004578 | -122.0398 | -0.091553 | -121.4172 | -122.1222 | -122.1176 | -68.3716 | 0.032043 | -122.0444 | -0.022888 | -120.6116 | -121.843 | -121.4859 | -0.045776 | -0.10986 | -0.19684 | 0.57678 | -0.1236 | -0.12817 | -0.07782 | -0.082397 | -0.050354 | -0.073243 | -0.12817 | 1.3824 | 0.50812 | 0.15106 | 0.55847 | 0.20142 | 0.62256 | 121.9482 | 1.4328 | 122.0215 | 122.0352 | 122.0764 | 121.9894 | 122.0261 | -122.1451 | -122.1497 | 121.9025 | 121.9711 | 120.7123 | 53.6224
2045.75 | 122.1176 | -121.9986 | 0.11902 | -0.013657 | -7.9104e-05 | 0.054549 | 0.053908 | -0.0017048 | -0.010683 | -0.0048985 | -0.0082093 | 0.0023712 | 0.072792 | 0.059714 | -0.012441 | 0.023071 | 0.0002842 | -1.2222 | -0.022888 | -122.0856 | -0.086975 | -121.3577 | -122.0718 | -122.0856 | -68.2938 | 0.032043 | -122.0581 | -0.068665 | -120.607 | -121.8246 | -121.5042 | -0.086975 | -0.14191 | -0.20599 | 0.64087 | -0.086975 | -0.073242 | 0 | 0.013733 | -0.059509 | -0.086976 | -0.18768 | 1.3916 | 0.49439 | 0.17395 | 0.55389 | 0.23346 | 0.72784 | 121.9986 | 1.4511 | 121.9894 | 122.0627 | 122.0901 | 121.9757 | 122.0306 | -122.2046 | -122.1771 | 121.9116 | 121.9299 | 120.7764 | 53.7048
2047.4531 | 122.1817 | -121.9757 | 0.10986 | -0.013657 | 0.0003483 | 0.056258 | 0.05348 | 0.0010724 | -0.0076925 | -0.0027621 | -0.0021057 | 0.0049346 | 0.075142 | 0.062064 | -0.013082 | 0.01944 | 0.0011386 | -1.1902 | -0.004578 | -122.0581 | -0.009155 | -121.312 | -122.0398 | -122.0535 | -68.3258 | 0.027466 | -122.0581 | 0.032043 | -120.3873 | -121.7834 | -121.4447 | -0.082397 | -0.11444 | -0.11902 | 0.66376 | -0.07782 | -0.064087 | 0.004577 | 0.01831 | -0.082397 | -0.082397 | -0.07782 | 1.5884 | 0.53101 | 0.19226 | 0.6134 | 0.27466 | 0.74615 | 122.0489 | 1.6708 | 122.0901 | 122.0535 | 122.0856 | 121.9711 | 122.0032 | -122.168 | -122.168 | 121.9666 | 122.0078 | 120.7855 | 53.6499
2049.2031 | 122.1268 | -121.9986 | 0.10986 | -0.013657 | 0.0044071 | 0.057326 | 0.057112 | 0.00064519 | -0.0087607 | -0.0051121 | -0.0051575 | 0.003012 | 0.072365 | 0.069541 | -0.011373 | 0.022003 | -0.0009976 | -1.3046 | -0.013733 | -122.0444 | -0.10071 | -121.431 | -122.1451 | -122.1313 | -68.3716 | 0.041199 | -122.0764 | -0.032043 | -120.4239 | -121.8567 | -121.5042 | -0.045777 | -0.1236 | -0.21057 | 0.56763 | -0.13275 | -0.14648 | -0.086975 | -0.10071 | -0.07782 | -0.068664 | -0.14191 | 1.5747 | 0.49439 | 0.14191 | 0.5722 | 0.21973 | 0.6134 | 121.9437 | 1.6525 | 122.0444 | 122.0306 | 122.1176 | 121.9849 | 122.0398 | -122.1542 | -122.1863 | 121.8979 | 121.9666 | 120.694 | 53.627
2050.9062 | 122.2275 | -121.9666 | 0.09613 | -0.013657 | 0.0012027 | 0.056685 | 0.056044 | 0.0025678 | -0.0079061 | -0.0031895 | -0.0021057 | 0.0027984 | 0.073433 | 0.057151 | -0.010946 | 0.021576 | -0.0005704 | -1.3504 | -0.009155 | -122.0352 | -0.045776 | -121.3348 | -122.081 | -122.0764 | -68.28 | 0.018311 | -122.049 | 0.050354 | -120.2911 | -121.7514 | -121.4355 | -0.068664 | -0.10528 | -0.14191 | 0.63171 | -0.10986 | -0.11444 | -0.041199 | -0.045777 | -0.082397 | -0.077819 | -0.045776 | 1.6754 | 0.53101 | 0.21515 | 0.6134 | 0.29755 | 0.70038 | 121.9894 | 1.7578 | 122.0993 | 122.0261 | 122.0673 | 121.9574 | 121.9849 | -122.1313 | -122.1451 | 121.9208 | 122.0169 | 120.6162 | 53.6865
2052.6562 | 122.2961 | -121.9528 | 0.091553 | -0.021286 | -0.0026425 | 0.054976 | 0.05049 | -0.00042301 | -0.0081197 | -0.0031895 | -0.0051575 | -0.00040596 | 0.073647 | 0.055869 | -0.013082 | 0.021149 | -0.002493 | -1.2222 | -0.041199 | -122.0352 | 0.059509 | -121.2158 | -121.9482 | -121.9482 | -68.1564 | -0.013733 | -122.0169 | 0.086975 | -120.1584 | -121.6415 | -121.376 | -0.082397 | -0.13275 | -0.032044 | 0.737 | 0.004578 | 0.004578 | 0.086975 | 0.086975 | -0.064087 | -0.10529 | -0.004578 | 1.7944 | 0.57678 | 0.31128 | 0.64087 | 0.37537 | 0.8194 | 122.0947 | 1.8585 | 122.1039 | 121.994 | 122.0032 | 121.9116 | 121.9391 | -122.1268 | -122.1085 | 122.0123 | 122.0398 | 120.7306 | 53.7964
2054.4062 | 122.1268 | -122.0032 | 0.10529 | -0.013657 | 0.0048343 | 0.055617 | 0.054976 | -0.0023456 | -0.0070517 | -0.0048985 | -0.0082093 | 0.0038666 | 0.072792 | 0.058432 | -0.012228 | 0.022003 | -0.0029202 | -1.3596 | -0.013733 | -122.0764 | -0.091553 | -121.4447 | -122.1451 | -122.1451 | -69.1269 | 0.027466 | -122.0581 | -0.022888 | -120.3598 | -121.8521 | -121.4951 | -0.073242 | -0.11902 | -0.19684 | 0.55847 | -0.14191 | -0.14191 | -0.068665 | -0.068665 | -0.054931 | -0.07782 | -0.12817 | 1.6434 | 0.50812 | 0.15106 | 0.56305 | 0.20599 | 0.63171 | 121.9849 | 1.6983 | 122.0352 | 122.0627 | 122.0856 | 121.9894 | 122.0306 | -122.1817 | -122.1634 | 121.9116 | 121.9803 | 120.6436 | 52.8763
2056.1719 | 122.1817 | -121.9894 | 0.11444 | 0.0016023 | -0.0002927 | 0.054549 | 0.055403 | 0.0019268 | -0.0057699 | -0.0016941 | -0.0021057 | 0.0023712 | 0.073647 | 0.065696 | -0.013723 | 0.02179 | -0.0009976 | -1.2543 | -0.018311 | -122.081 | -0.050354 | -121.3715 | -122.049 | -122.0947 | -69.6304 | 0.050354 | -122.0764 | -0.004578 | -120.2591 | -121.788 | -121.4355 | -0.091553 | -0.13275 | -0.16479 | 0.61798 | -0.10529 | -0.059509 | -0.013733 | 0.032044 | -0.086975 | -0.064087 | -0.11902 | 1.7303 | 0.55389 | 0.20142 | 0.64087 | 0.28839 | 0.70953 | 122.0306 | 1.8173 | 122.0718 | 122.0627 | 122.1268 | 121.9711 | 122.0398 | -122.1954 | -122.1909 | 121.9391 | 121.9849 | 120.7352 | 52.359
2057.8594 | 122.2549 | -121.9574 | 0.07782 | -0.0060272 | -0.0007199 | 0.057539 | 0.054121 | 4.192e-06 | -0.0076925 | -0.0044711 | -0.0082093 | 0.0015166 | 0.074074 | 0.060569 | -0.015005 | 0.023926 | -0.0033474 | -1.3275 | -0.045776 | -122.0306 | 0.022888 | -121.2662 | -122.0032 | -122.0169 | -69.7403 | 0.004578 | -122.0444 | 0.10071 | -120.163 | -121.6965 | -121.2936 | -0.073243 | -0.1236 | -0.054932 | 0.69122 | -0.05951 | -0.045777 | 0.013733 | 0.027466 | -0.086976 | -0.073242 | 0.022888 | 1.7944 | 0.66376 | 0.26093 | 0.75073 | 0.3479 | 0.76447 | 122.0535 | 1.8814 | 122.1451 | 121.9849 | 122.049 | 121.9116 | 121.962 | -122.1085 | -122.1222 | 121.9803 | 122.0581 | 120.6299 | 52.2171
2059.625 | 122.1817 | -121.9757 | 0.10529 | -0.021286 | -7.9104e-05 | 0.056471 | 0.049849 | -0.003841 | -0.0079061 | -0.0027621 | -0.0021057 | 0.0010894 | 0.07386 | 0.063346 | -0.012869 | 0.02179 | -0.0009976 | -1.2405 | -0.036621 | -122.0581 | 0.004578 | -121.2799 | -121.994 | -122.0169 | -69.7769 | 0 | -122.0352 | -0.013733 | -120.2225 | -121.7697 | -121.3623 | -0.082397 | -0.14191 | -0.10071 | 0.6958 | -0.041199 | -0.018311 | 0.041198 | 0.064086 | -0.059509 | -0.10529 | -0.11902 | 1.7532 | 0.6134 | 0.20599 | 0.67291 | 0.2655 | 0.7782 | 122.0627 | 1.8127 | 122.0215 | 122.0215 | 122.0352 | 121.9391 | 121.9757 | -122.1634 | -122.1405 | 121.9803 | 121.962 | 120.7352 | 52.1988
2061.3125 | 122.2549 | -121.9482 | 0.068665 | -0.013657 | 0.0022709 | 0.056898 | 0.053053 | -0.0036274 | -0.0053427 | -0.0016941 | -0.0082093 | 0.0017304 | 0.072151 | 0.061637 | -0.01351 | 0.020294 | -0.0014248 | -1.3458 | -0.050354 | -122.0306 | 0.036621 | -121.2616 | -122.0032 | -121.994 | -69.6899 | -0.009155 | -122.0169 | 0.091553 | -120.108 | -121.6782 | -121.2616 | -0.082398 | -0.11902 | -0.032044 | 0.68664 | -0.045777 | -0.054932 | 0.036621 | 0.027466 | -0.068665 | -0.07782 | 0.022888 | 1.8402 | 0.68664 | 0.27008 | 0.75531 | 0.33875 | 0.76904 | 122.0673 | 1.9089 | 122.1085 | 121.9803 | 122.0078 | 121.8979 | 121.9391 | -122.0993 | -122.0856 | 121.9849 | 122.0398 | 120.6024 | 52.2583
2063.0625 | 122.1497 | -121.9986 | 0.11444 | -0.0060272 | -0.0007199 | 0.057112 | 0.054976 | -0.00063661 | -0.0064109 | -0.0029759 | -0.0051575 | 0.0032256 | 0.072578 | 0.061637 | -0.014364 | 0.020508 | -0.0012112 | -1.3046 | -0.018311 | -122.0718 | -0.027466 | -121.3486 | -122.0627 | -122.0901 | -69.7998 | 0.022888 | -122.0718 | -0.013733 | -120.1813 | -121.8018 | -121.3898 | -0.073242 | -0.13275 | -0.14191 | 0.65002 | -0.091553 | -0.064087 | -0.018311 | 0.009155 | -0.073242 | -0.091553 | -0.12817 | 1.8173 | 0.60883 | 0.19684 | 0.68207 | 0.27008 | 0.72327 | 122.0444 | 1.8906 | 122.0581 | 122.0535 | 122.0947 | 121.9803 | 122.0215 | -122.1863 | -122.1863 | 121.9711 | 121.9849 | 120.694 | 52.1988
2064.75 | 122.1863 | -121.962 | 0.11444 | -0.0060272 | -0.0009335 | 0.056044 | 0.055617 | -0.00020941 | -0.011111 | -0.00083947 | -0.0051575 | 0.001944 | 0.074287 | 0.063132 | -0.013723 | 0.021576 | -0.000784 | -1.3138 | -0.041199 | -122.0856 | -0.068665 | -121.3806 | -122.0444 | -122.0856 | -69.8593 | 0.032043 | -122.0764 | -0.018311 | -120.1355 | -121.7834 | -121.3898 | -0.1236 | -0.15564 | -0.18311 | 0.58136 | -0.1236 | -0.082398 | 0 | 0.041198 | -0.11444 | -0.082398 | -0.13275 | 1.8265 | 0.5722 | 0.17853 | 0.68664 | 0.29297 | 0.70496 | 122.0169 | 1.9409 | 122.0581 | 122.0444 | 122.1085 | 121.9208 | 121.994 | -122.2 | -122.1909 | 121.8933 | 121.9437 | 120.6482 | 52.1027
2066.5156 | 122.2504 | -121.962 | 0.091553 | -0.021286 | -0.0028561 | 0.053267 | 0.052199 | -0.002132 | -0.0064109 | -0.00041227 | -0.0051575 | 0.0015166 | 0.074501 | 0.064627 | -0.013082 | 0.020935 | -0.0001432 | -1.3733 | -0.041199 | -122.0581 | -0.013733 | -121.2936 | -122.0215 | -122.0261 | -69.7678 | 0.009155 | -122.0444 | 0.045776 | -120.0256 | -121.6873 | -121.3074 | -0.09613 | -0.13275 | -0.10529 | 0.66833 | -0.064087 | -0.059509 | 0.032043 | 0.036621 | -0.082398 | -0.082398 | -0.045777 | 1.9363 | 0.6546 | 0.27466 | 0.737 | 0.35706 | 0.76447 | 122.0444 | 2.0187 | 122.0901 | 122.0169 | 122.0535 | 121.9208 | 121.9711 | -122.1497 | -122.1359 | 121.9482 | 122.0078 | 120.5887 | 52.1942
2068.2656 | 122.1725 | -121.9711 | 0.10071 | -0.013657 | 0.0003483 | 0.056685 | 0.054121 | -0.0025592 | -0.0083335 | -0.0034031 | -0.0082093 | 0.0025848 | 0.072365 | 0.061209 | -0.015646 | 0.021362 | 0.0015658 | -1.4557 | -0.018311 | -122.0901 | -0.082397 | -121.4035 | -122.113 | -122.1222 | -69.8227 | 0.018311 | -122.0856 | 0.004578 | -120.0943 | -121.8109 | -121.3806 | -0.11902 | -0.11902 | -0.18311 | 0.56763 | -0.15106 | -0.14191 | -0.032043 | -0.022888 | -0.11444 | -0.082397 | -0.09613 | 1.8768 | 0.59051 | 0.16022 | 0.70496 | 0.27466 | 0.68665 | 122.0078 | 1.9913 | 122.0901 | 122.0718 | 122.1039 | 121.9528 | 121.9894 | -122.1909 | -122.1863 | 121.8887 | 121.9757 | 120.5154 | 52.1484
2070.0156 | 122.1222 | -122.0123 | 0.10986 | -0.021286 | 0.0014163 | 0.055617 | 0.05583 | 0.0066266 | -0.0085471 | -0.0014805 | -0.0021057 | 0.0027984 | 0.074928 | 0.06655 | -0.012228 | 0.020508 | 7.04e-05 | -1.4053 | 0 | -122.0947 | -0.086975 | -121.431 | -122.1268 | -122.1313 | -69.841 | 0.036621 | -122.1039 | -0.054932 | -120.1035 | -121.8567 | -121.4447 | -0.082398 | -0.10986 | -0.19684 | 0.58136 | -0.11902 | -0.11444 | -0.036621 | -0.032043 | -0.091553 | -0.073242 | -0.16479 | 1.9089 | 0.56763 | 0.15564 | 0.65918 | 0.24719 | 0.66376 | 122.0078 | 2.0004 | 122.049 | 122.0947 | 122.1405 | 122.0123 | 122.0489 | -122.2046 | -122.2137 | 121.9254 | 121.9574 | 120.607 | 52.1713
2071.7031 | 122.2504 | -121.9803 | 0.073242 | -0.0060272 | 0.0001345 | 0.054976 | 0.053053 | -0.00020941 | -0.0064109 | -0.0016941 | -0.0082093 | 0.0015166 | 0.071938 | 0.058646 | -0.012655 | 0.020721 | -0.0020658 | -1.4191 | -0.041199 | -122.081 | 0.004578 | -121.2936 | -122.0306 | -122.0261 | -69.6671 | 0.018311 | -122.0535 | 0.050354 | -119.9295 | -121.701 | -121.3577 | -0.10071 | -0.11444 | -0.068664 | 0.68665 | -0.045776 | -0.050354 | 0.054932 | 0.050354 | -0.073242 | -0.054931 | -0.022888 | 2.0508 | 0.62256 | 0.27924 | 0.6958 | 0.35248 | 0.78735 | 122.0856 | 2.124 | 122.1039 | 122.0398 | 122.0718 | 121.9391 | 121.9986 | -122.1542 | -122.1268 | 121.9849 | 122.0306 | 120.5612 | 52.3132
2073.4688 | 122.2275 | -121.9666 | 0.091553 | -0.028916 | -0.0002927 | 0.056258 | 0.051985 | -0.0027728 | -0.0072653 | -0.0051121 | -0.0082093 | 0.001944 | 0.071724 | 0.061209 | -0.013723 | 0.022003 | 0.0004978 | -1.4236 | -0.045776 | -122.0535 | -0.004578 | -121.3028 | -122.0398 | -122.0215 | -69.5251 | -0.018311 | -122.049 | 0.027466 | -119.9387 | -121.7194 | -121.376 | -0.086975 | -0.13733 | -0.096131 | 0.66376 | -0.054931 | -0.073242 | 0.032044 | 0.013733 | -0.082397 | -0.10986 | -0.064087 | 2.0279 | 0.59052 | 0.24719 | 0.67291 | 0.32959 | 0.75073 | 122.049 | 2.1103 | 122.0764 | 122.0078 | 122.0306 | 121.9208 | 121.9482 | -122.1451 | -122.1405 | 121.962 | 121.994 | 120.5429 | 52.4414
2075.2031 | 122.2366 | -121.9711 | 0.091553 | -0.013657 | -0.0011471 | 0.053694 | 0.053267 | -0.0017048 | -0.0083335 | -0.0021213 | -0.0082093 | 0.0010894 | 0.07386 | 0.062278 | -0.013296 | 0.020081 | -0.005911 | -1.442 | -0.036621 | -122.049 | -0.027466 | -121.3211 | -122.0444 | -122.0398 | -69.7266 | 0 | -122.0627 | 0.032043 | -119.8746 | -121.6919 | -121.344 | -0.07782 | -0.12817 | -0.11902 | 0.65002 | -0.068665 | -0.073243 | 0.009155 | 0.004577 | -0.091553 | -0.091553 | -0.05951 | 2.0966 | 0.62714 | 0.27923 | 0.71869 | 0.37079 | 0.72784 | 122.0215 | 2.1881 | 122.0947 | 122.0123 | 122.0627 | 121.9345 | 121.9711 | -122.1405 | -122.1542 | 121.9437 | 122.0032 | 120.5292 | 52.2446
2076.9062 | 122.2321 | -121.9666 | 0.082397 | -0.021286 | 0.0014163 | 0.056685 | 0.054121 | -0.0023456 | -0.0087607 | -0.0014805 | -0.0082093 | 0.0015166 | 0.072151 | 0.059714 | -0.014791 | 0.020721 | -0.0027066 | -1.4511 | -0.050354 | -122.0306 | 0.022888 | -121.2845 | -122.0352 | -122.0261 | -69.8227 | 0.009155 | -122.0398 | 0.050354 | -119.8196 | -121.7194 | -121.3165 | -0.064087 | -0.13275 | -0.059509 | 0.68207 | -0.059509 | -0.068664 | 0.004578 | -0.004577 | -0.073242 | -0.073242 | -0.032043 | 2.1469 | 0.65002 | 0.24719 | 0.72327 | 0.32044 | 0.74616 | 122.0535 | 2.2202 | 122.0901 | 121.9803 | 122.049 | 121.9162 | 121.9757 | -122.113 | -122.1222 | 121.9894 | 122.0169 | 120.5154 | 52.1439
2078.6406 | 122.3007 | -121.962 | 0.07782 | -0.013657 | -0.0017881 | 0.055617 | 0.05348 | -0.00020941 | -0.0074789 | -0.0019077 | -0.0051575 | 0.00023504 | 0.072151 | 0.058432 | -0.011801 | 0.019653 | -0.0005704 | -1.387 | -0.045776 | -122.081 | 0.054932 | -121.2433 | -121.9666 | -121.9757 | -69.8227 | 0 | -122.0444 | 0.10529 | -119.7189 | -121.6232 | -121.2845 | -0.11902 | -0.1236 | -0.022888 | 0.71869 | -0.013733 | -0.004578 | 0.10529 | 0.11444 | -0.082398 | -0.07782 | 0.027466 | 2.243 | 0.67749 | 0.33874 | 0.75989 | 0.42114 | 0.83771 | 122.1359 | 2.3254 | 122.1497 | 122.0352 | 122.0444 | 121.9162 | 121.962 | -122.1588 | -122.1222 | 122.0169 | 122.0673 | 120.575 | 52.1393
2080.3906 | 122.1954 | -122.0032 | 0.091553 | -0.021286 | 0.0012027 | 0.056258 | 0.057112 | -0.0019184 | -0.0059835 | -0.0031895 | -0.0051575 | 0.0051482 | 0.073647 | 0.063559 | -0.014578 | 0.022217 | 7.04e-05 | -1.3962 | -0.022888 | -122.081 | -0.013733 | -121.3303 | -122.0627 | -122.081 | -69.9921 | 0.022888 | -122.081 | 0.027466 | -119.7556 | -121.7651 | -121.3715 | -0.07782 | -0.11444 | -0.10529 | 0.67291 | -0.07782 | -0.059509 | 0 | 0.018311 | -0.07782 | -0.068665 | -0.064087 | 2.2476 | 0.63171 | 0.23804 | 0.70953 | 0.31586 | 0.75073 | 122.0673 | 2.3254 | 122.1085 | 122.0581 | 122.1039 | 121.9803 | 122.0261 | -122.1725 | -122.1725 | 121.9894 | 122.0306 | 120.607 | 52.0111
2082.1406 | 122.1451 | -122.0169 | 0.1236 | -0.021286 | -0.0030697 | 0.056044 | 0.054335 | 0.00043159 | -0.0094015 | -0.0044711 | -0.0082093 | 0.003653 | 0.072578 | 0.059714 | -0.012655 | 0.022217 | -0.0018522 | -1.4374 | -0.004578 | -122.1085 | -0.068665 | -121.4127 | -122.0993 | -122.1268 | -70.2713 | 0.036621 | -122.0856 | -0.036621 | -119.7464 | -121.8063 | -121.4127 | -0.091552 | -0.12817 | -0.19226 | 0.60425 | -0.10986 | -0.082397 | -0.018311 | 0.009155 | -0.068664 | -0.086975 | -0.16022 | 2.2705 | 0.60425 | 0.21057 | 0.67291 | 0.27924 | 0.6958 | 122.0398 | 2.3392 | 122.049 | 122.1039 | 122.1222 | 122.0123 | 122.0535 | -122.2321 | -122.2092 | 121.9482 | 121.9803 | 120.5795 | 51.7456
2083.8906 | 122.2366 | -121.9711 | 0.073242 | -0.013657 | 0.0020571 | 0.058394 | 0.054121 | -0.0023456 | -0.0083335 | -0.00083947 | -0.0021057 | 0.001944 | 0.07386 | 0.055655 | -0.012869 | 0.022858 | -0.0022794 | -1.4923 | -0.050354 | -122.0352 | 0.045776 | -121.2662 | -122.0261 | -122.0123 | -70.2805 | 0.013733 | -122.0581 | 0.054932 | -119.6045 | -121.6873 | -121.344 | -0.064087 | -0.1236 | -0.027466 | 0.70496 | -0.041199 | -0.054932 | 0.022888 | 0.009155 | -0.086975 | -0.059509 | -0.01831 | 2.3666 | 0.62714 | 0.28381 | 0.71411 | 0.37079 | 0.76904 | 122.081 | 2.4536 | 122.113 | 121.9849 | 122.0718 | 121.9208 | 121.9849 | -122.1085 | -122.1313 | 122.0169 | 122.0261 | 120.4788 | 51.6907
2085.5781 | 122.1268 | -122.0078 | 0.10986 | -0.0060272 | -0.0022153 | 0.054335 | 0.051772 | -0.0040546 | -0.0085471 | -0.0019077 | -0.0051575 | 0.0025848 | 0.074928 | 0.059714 | -0.013082 | 0.020508 | -0.0005704 | -1.4603 | -0.018311 | -122.1313 | -0.07782 | -121.3989 | -122.0993 | -122.1039 | -70.5322 | 0.032043 | -122.081 | -0.054932 | -119.6228 | -121.8018 | -121.4584 | -0.1236 | -0.12817 | -0.18768 | 0.60882 | -0.096131 | -0.091553 | 0.027466 | 0.032044 | -0.073243 | -0.07782 | -0.16479 | 2.3849 | 0.54932 | 0.20599 | 0.62256 | 0.27924 | 0.73242 | 122.0535 | 2.4582 | 122.0261 | 122.113 | 122.113 | 121.9894 | 122.0398 | -122.2412 | -122.1909 | 121.9299 | 121.9528 | 120.5475 | 51.4755
2087.3281 | 122.2092 | -122.0078 | 0.09613 | -0.013657 | 0.0018435 | 0.055189 | 0.054549 | -0.00063661 | -0.0081197 | -0.0029759 | -0.0082093 | 0.0049346 | 0.073219 | 0.061423 | -0.014578 | 0.021576 | -0.000784 | -1.561 | -0.004578 | -122.081 | -0.073242 | -121.4035 | -122.1359 | -122.1359 | -70.6055 | 0.022888 | -122.0764 | 0.009155 | -119.6274 | -121.7834 | -121.3303 | -0.073243 | -0.10071 | -0.16937 | 0.60425 | -0.12817 | -0.12817 | -0.054931 | -0.054931 | -0.068665 | -0.073242 | -0.086975 | 2.3804 | 0.67749 | 0.2243 | 0.74616 | 0.29297 | 0.67749 | 122.0078 | 2.449 | 122.0856 | 122.0764 | 122.0993 | 122.0032 | 122.0306 | -122.1771 | -122.1725 | 121.9345 | 122.0169 | 120.4468 | 51.4023
2089.0938 | 122.2137 | -122.0032 | 0.10986 | -0.0060272 | 0.0016299 | 0.056685 | 0.053694 | 0.0017132 | -0.0066245 | -0.0014805 | -0.0051575 | 0.003012 | 0.073219 | 0.066336 | -0.013723 | 0.021149 | -0.0009976 | -1.4603 | -0.018311 | -122.1222 | -0.064087 | -121.3989 | -122.0718 | -122.1039 | -70.7245 | 0.027466 | -122.0947 | -0.009155 | -119.5541 | -121.7651 | -121.3028 | -0.11902 | -0.12817 | -0.17395 | 0.60425 | -0.10071 | -0.068664 | 0.01831 | 0.050354 | -0.091553 | -0.082397 | -0.11902 | 2.449 | 0.70038 | 0.23804 | 0.79193 | 0.32959 | 0.72327 | 122.0581 | 2.5406 | 122.0856 | 122.1039 | 122.1222 | 121.9849 | 122.0306 | -122.2321 | -122.2046 | 121.9391 | 121.994 | 120.5429 | 51.2787
2090.7812 | 122.1497 | -122.0215 | 0.11902 | -0.021286 | -0.0011471 | 0.05583 | 0.05348 | -0.00042301 | -0.010683 | -0.0031895 | -0.0051575 | 0.0027984 | 0.075996 | 0.05651 | -0.01351 | 0.02243 | -0.0031338 | -1.4786 | -0.009155 | -122.0993 | -0.064087 | -121.3806 | -122.0901 | -122.1176 | -70.9351 | 0.041199 | -122.1268 | -0.041199 | -119.5496 | -121.7789 | -121.3989 | -0.07782 | -0.12817 | -0.18311 | 0.64087 | -0.096131 | -0.068665 | -0.018311 | 0.009155 | -0.10529 | -0.07782 | -0.16022 | 2.4719 | 0.62256 | 0.24261 | 0.72784 | 0.3479 | 0.71869 | 122.0352 | 2.5772 | 122.0856 | 122.0901 | 122.168 | 122.0123 | 122.0627 | -122.2183 | -122.2458 | 121.9574 | 121.9803 | 120.5429 | 51.0864
2092.5312 | 122.1588 | -122.0306 | 0.09613 | -0.013657 | 0.0024845 | 0.056898 | 0.055617 | 0.00021799 | -0.0079061 | -0.0034031 | -0.0021057 | 0.0045074 | 0.074501 | 0.063987 | -0.01415 | 0.021576 | 0.0045566 | -1.5884 | -0.022888 | -122.0764 | -0.086975 | -121.4264 | -122.1451 | -122.1313 | -71.0861 | 0.041199 | -122.1085 | -0.022888 | -119.5129 | -121.8155 | -121.3577 | -0.045776 | -0.11902 | -0.1831 | 0.60425 | -0.10071 | -0.11444 | -0.054932 | -0.068665 | -0.077819 | -0.054931 | -0.11902 | 2.5177 | 0.67291 | 0.21515 | 0.75073 | 0.29297 | 0.65002 | 121.9894 | 2.5955 | 122.0856 | 122.0535 | 122.1497 | 122.0078 | 122.0718 | -122.1725 | -122.2046 | 121.9437 | 122.0078 | 120.4422 | 50.9445
2094.2812 | 122.2641 | -121.994 | 0.082397 | -0.013657 | -0.0020017 | 0.05583 | 0.051344 | 0.00021799 | -0.0079061 | -0.0029759 | -0.0051575 | 2.1442e-05 | 0.074287 | 0.061637 | -0.013937 | 0.02243 | -0.0014248 | -1.5747 | -0.054932 | -122.0993 | -0.041199 | -121.3303 | -122.0444 | -122.0627 | -71.022 | 0.004578 | -122.0856 | 0.036621 | -119.3848 | -121.6782 | -121.3531 | -0.10529 | -0.13733 | -0.1236 | 0.66376 | -0.068664 | -0.050354 | 0.036621 | 0.054931 | -0.091552 | -0.077819 | -0.045776 | 2.6093 | 0.64087 | 0.31586 | 0.73242 | 0.40741 | 0.76904 | 122.0581 | 2.7008 | 122.1222 | 122.0444 | 122.0901 | 121.9391 | 121.9986 | -122.1817 | -122.168 | 121.9528 | 122.0306 | 120.4193 | 50.972
2096.0469 | 122.1359 | -122.0078 | 0.11902 | -0.013657 | 0.0026981 | 0.055189 | 0.057326 | 0.00043159 | -0.0072653 | -0.0023349 | -0.0021057 | 0.0051482 | 0.072578 | 0.067832 | -0.012441 | 0.022644 | -0.0022794 | -1.5793 | -0.018311 | -122.0856 | -0.068665 | -121.4081 | -122.1451 | -122.1359 | -70.99 | 0.022888 | -122.0856 | -0.032043 | -119.458 | -121.8338 | -121.4447 | -0.07782 | -0.13733 | -0.18768 | 0.59967 | -0.12817 | -0.13733 | -0.050354 | -0.05951 | -0.07782 | -0.096131 | -0.15106 | 2.5497 | 0.56305 | 0.17395 | 0.64087 | 0.25177 | 0.67749 | 122.0169 | 2.6276 | 122.0535 | 122.0673 | 122.1085 | 121.9894 | 122.0306 | -122.2046 | -122.2046 | 121.9391 | 121.9757 | 120.4285 | 51.0178
2097.7969 | 122.1954 | -122.0032 | 0.09613 | -0.013657 | 0.0016299 | 0.057112 | 0.054762 | -0.0029864 | -0.0087607 | -0.0023349 | -0.0082093 | 0.0045074 | 0.075569 | 0.072318 | -0.01415 | 0.021149 | 0.0028476 | -1.5335 | -0.032043 | -122.0901 | -0.018311 | -121.3303 | -122.0581 | -122.0901 | -70.99 | 0.022888 | -122.0627 | 0.009155 | -119.3436 | -121.7422 | -121.3852 | -0.086975 | -0.12817 | -0.11444 | 0.67291 | -0.086975 | -0.054931 | 0 | 0.032044 | -0.059509 | -0.073242 | -0.086975 | 2.6596 | 0.61798 | 0.26093 | 0.67749 | 0.32043 | 0.75989 | 122.0718 | 2.7191 | 122.0718 | 122.0581 | 122.0856 | 121.9711 | 122.0261 | -122.1863 | -122.1588 | 121.9849 | 122.0123 | 120.4697 | 51.0132
2099.4844 | 122.2733 | -121.9849 | 0.068665 | -0.013657 | -0.0015743 | 0.054549 | 0.05284 | -0.001491 | -0.0070517 | -0.0023349 | -0.0051575 | 0.001944 | 0.073433 | 0.053946 | -0.012655 | 0.021576 | -0.0031338 | -1.4877 | -0.064087 | -122.0993 | 0.054932 | -121.2341 | -121.9849 | -121.9803 | -70.9259 | -0.013733 | -122.0581 | 0.073242 | -119.1696 | -121.6553 | -121.3348 | -0.11444 | -0.13275 | -0.013733 | 0.75073 | 0.004577 | 0 | 0.11902 | 0.11444 | -0.073242 | -0.082398 | 0.004577 | 2.8152 | 0.65002 | 0.32959 | 0.72327 | 0.40283 | 0.86517 | 122.1542 | 2.8885 | 122.1313 | 122.0352 | 122.0444 | 121.9208 | 121.9711 | -122.168 | -122.1268 | 122.0398 | 122.0581 | 120.4971 | 51.059
2101.2344 | 122.2824 | -121.9894 | 0.07782 | -0.021286 | 0.0029117 | 0.056258 | 0.054335 | -0.0019184 | -0.0072653 | -0.0023349 | -0.0051575 | -0.00040596 | 0.076637 | 0.05416 | -0.012441 | 0.020294 | 0.0002842 | -1.6022 | -0.045776 | -122.0535 | 0.009155 | -121.3257 | -122.0352 | -122.0261 | -71.0358 | -0.009155 | -122.0535 | 0.045776 | -119.1788 | -121.6644 | -121.3028 | -0.064087 | -0.1236 | -0.068665 | 0.66376 | -0.036621 | -0.045776 | 0.027466 | 0.018311 | -0.064087 | -0.086975 | -0.032044 | 2.8107 | 0.68665 | 0.32501 | 0.75073 | 0.3891 | 0.72784 | 122.0627 | 2.8748 | 122.0993 | 122.0078 | 122.0444 | 121.9437 | 121.9803 | -122.1313 | -122.1313 | 121.9986 | 122.0352 | 120.3873 | 50.9537
2102.9219 | 122.168 | -122.0306 | 0.10986 | -0.013657 | 0.0026981 | 0.055617 | 0.054335 | -0.0012774 | -0.0074789 | -0.0023349 | -0.011261 | 0.003012 | 0.073006 | 0.061637 | -0.014578 | 0.022644 | -0.0018522 | -1.6525 | -0.009155 | -122.1268 | -0.09613 | -121.4447 | -122.1817 | -122.168 | -71.1594 | 0.027466 | -122.081 | -0.032043 | -119.2612 | -121.8155 | -121.4127 | -0.09613 | -0.11902 | -0.20599 | 0.58594 | -0.13733 | -0.15106 | -0.041199 | -0.054932 | -0.050354 | -0.082397 | -0.14191 | 2.7695 | 0.61798 | 0.21515 | 0.66833 | 0.2655 | 0.68207 | 122.0306 | 2.8198 | 122.049 | 122.1176 | 122.1085 | 122.0215 | 122.0581 | -122.2366 | -122.1909 | 121.9345 | 121.9986 | 120.3781 | 50.8713
2104.6719 | 122.2824 | -121.9803 | 0.09613 | -0.0060272 | -0.0034971 | 0.055403 | 0.05049 | -0.0053362 | -0.0081197 | -0.0040439 | -0.0051575 | 0.003012 | 0.075355 | 0.059073 | -0.012228 | 0.022644 | -0.0014248 | -1.5381 | -0.050354 | -122.0673 | 0.054932 | -121.2341 | -121.9711 | -121.9894 | -70.9991 | -0.009155 | -122.0901 | 0.091553 | -119.046 | -121.6232 | -121.2799 | -0.086975 | -0.14648 | -0.041198 | 0.74616 | -0.009155 | 0.009156 | 0.07782 | 0.096131 | -0.10986 | -0.10528 | -0.004577 | 2.9343 | 0.70038 | 0.35706 | 0.81024 | 0.46692 | 0.83313 | 122.1222 | 3.0441 | 122.1817 | 122.0169 | 122.081 | 121.9299 | 121.9711 | -122.1634 | -122.1863 | 122.0352 | 122.0718 | 120.4422 | 50.9811
2106.4375 | 122.319 | -121.9986 | 0.07782 | -0.013657 | -0.0034971 | 0.055403 | 0.052626 | -0.0034136 | -0.0083335 | -0.0031895 | -0.0051575 | 0.001303 | 0.073219 | 0.062064 | -0.011801 | 0.020721 | 0.0002842 | -1.5793 | -0.045776 | -122.0581 | 0.050354 | -121.2616 | -121.9849 | -121.9986 | -72.1344 | -0.022888 | -122.0581 | 0.091553 | -118.9819 | -121.6232 | -121.2524 | -0.059509 | -0.1236 | -0.027466 | 0.737 | 0 | 0.013733 | 0.059509 | 0.073242 | -0.059509 | -0.10071 | 0.013733 | 3.0167 | 0.74616 | 0.37537 | 0.80566 | 0.43487 | 0.79651 | 122.1085 | 3.0762 | 122.1497 | 122.0123 | 122.0352 | 121.9528 | 121.9757 | -122.1359 | -122.1359 | 122.049 | 122.0901 | 120.4193 | 49.8642
2108.1406 | 122.2778 | -121.9803 | 0.068665 | -0.021286 | 0.0005619 | 0.057112 | 0.052626 | -0.00042301 | -0.0064109 | -0.0038303 | -0.0082093 | 0.004721 | 0.074715 | 0.0689 | -0.0165 | 0.02179 | -0.0005704 | -1.6388 | -0.059509 | -122.0398 | 0.059509 | -121.2662 | -122.0215 | -122.0032 | -72.5372 | 0.004578 | -122.0627 | 0.10071 | -118.9453 | -121.6599 | -121.2067 | -0.059509 | -0.12817 | -0.009156 | 0.71411 | -0.022888 | -0.041198 | 0.036621 | 0.018311 | -0.082397 | -0.064087 | 0.032043 | 3.035 | 0.77362 | 0.32044 | 0.85602 | 0.40283 | 0.77362 | 122.0993 | 3.1174 | 122.1634 | 121.9803 | 122.0673 | 121.9208 | 121.9849 | -122.1085 | -122.1313 | 122.0398 | 122.081 | 120.3415 | 49.4431
2109.875 | 122.3053 | -121.9849 | 0.09613 | -0.013657 | -0.0022153 | 0.057753 | 0.053908 | 0.0010724 | -0.0079061 | -0.0025485 | -0.0051575 | 0.0045074 | 0.072365 | 0.062491 | -0.01415 | 0.02179 | 0.002634 | -1.6067 | -0.041199 | -122.0581 | 0.045776 | -121.2524 | -121.9803 | -121.9803 | -72.8027 | 0.004578 | -122.0718 | 0.091553 | -118.8583 | -121.6049 | -121.1884 | -0.073242 | -0.13733 | -0.050354 | 0.73242 | 0.004577 | 0.004577 | 0.077819 | 0.077819 | -0.086975 | -0.091552 | -0.004577 | 3.1265 | 0.79651 | 0.37994 | 0.88348 | 0.46692 | 0.80566 | 122.1039 | 3.2135 | 122.1634 | 122.0169 | 122.0764 | 121.9437 | 121.9894 | -122.1542 | -122.168 | 122.0306 | 122.0764 | 120.3781 | 49.1821
2111.6406 | 122.2458 | -122.0078 | 0.086975 | -0.021286 | -0.0024289 | 0.054335 | 0.050917 | -0.0029864 | -0.01047 | -0.0019077 | -0.0051575 | 0.0010894 | 0.073647 | 0.05886 | -0.014364 | 0.020081 | -0.0014248 | -1.5701 | -0.054932 | -122.1085 | 0.059509 | -121.2799 | -121.994 | -122.0123 | -72.8622 | 0.009155 | -122.0718 | 0.032043 | -118.8492 | -121.6553 | -121.2341 | -0.10071 | -0.14191 | -0.027466 | 0.72784 | -0.004578 | 0.013732 | 0.09613 | 0.11444 | -0.064087 | -0.07782 | -0.054932 | 3.1586 | 0.77362 | 0.35248 | 0.83771 | 0.41657 | 0.82855 | 122.168 | 3.2227 | 122.1039 | 122.0535 | 122.081 | 121.9528 | 122.0169 | -122.1954 | -122.1588 | 122.0673 | 122.0398 | 120.4376 | 49.1455
2113.4062 | 122.2137 | -121.994 | 0.10986 | 0.0016023 | 0.0022709 | 0.056685 | 0.055617 | 0.00085879 | -0.0066245 | -0.0044711 | -0.0082093 | 0.0027984 | 0.078773 | 0.064414 | -0.015646 | 0.023926 | -0.0033474 | -1.5976 | -0.009155 | -122.1085 | -0.022888 | -121.344 | -122.0673 | -122.0901 | -73.5489 | 0.041199 | -122.0901 | 0.027466 | -118.8446 | -121.7102 | -121.2296 | -0.11444 | -0.11902 | -0.13275 | 0.65002 | -0.09613 | -0.073242 | 0.01831 | 0.041198 | -0.09613 | -0.068664 | -0.082397 | 3.1494 | 0.76447 | 0.28381 | 0.8606 | 0.37994 | 0.76447 | 122.0856 | 3.2455 | 122.1176 | 122.0993 | 122.1313 | 121.9849 | 122.0352 | -122.2183 | -122.2 | 121.9711 | 122.0215 | 120.3964 | 48.4451
2115.0938 | 122.1588 | -122.0306 | 0.1236 | -0.021286 | -0.0030697 | 0.054121 | 0.054335 | -0.0034136 | -0.010043 | -0.0053257 | -0.0082093 | 0.0038666 | 0.074928 | 0.061423 | -0.012228 | 0.02179 | -0.0001432 | -1.6571 | -0.009155 | -122.1039 | -0.082397 | -121.4081 | -122.1039 | -122.1313 | -73.8464 | 0.041199 | -122.1313 | -0.036621 | -118.8354 | -121.7514 | -121.2799 | -0.073242 | -0.13275 | -0.20599 | 0.62256 | -0.10071 | -0.073242 | -0.027466 | 0 | -0.10071 | -0.082397 | -0.16022 | 3.1952 | 0.75073 | 0.27924 | 0.85144 | 0.37994 | 0.6958 | 122.0215 | 3.2959 | 122.0947 | 122.0947 | 122.1725 | 122.0215 | 122.0718 | -122.2275 | -122.2549 | 121.9482 | 121.994 | 120.3735 | 48.1842
2116.8438 | 122.2641 | -121.9711 | 0.091553 | -0.013657 | -0.0026425 | 0.057112 | 0.051344 | -0.001491 | -0.0079061 | -0.0044711 | -0.0051575 | 0.0023712 | 0.074501 | 0.06185 | -0.014578 | 0.022217 | -0.0003568 | -1.6067 | -0.059509 | -122.0718 | 0.054932 | -121.2524 | -121.9894 | -122.0032 | -73.8831 | 0.013733 | -122.0856 | 0.050354 | -118.6707 | -121.6141 | -121.1472 | -0.10071 | -0.15106 | -0.036621 | 0.71869 | -0.032044 | -0.018311 | 0.068664 | 0.082397 | -0.11444 | -0.07782 | -0.041199 | 3.3005 | 0.82397 | 0.35706 | 0.93842 | 0.4715 | 0.8194 | 122.1268 | 3.4149 | 122.1359 | 122.0123 | 122.0993 | 121.9116 | 121.9849 | -122.1634 | -122.1771 | 122.0261 | 122.0215 | 120.3644 | 48.0881
2118.5938 | 122.3236 | -122.0078 | 0.068665 | -0.0060272 | -0.0011471 | 0.053908 | 0.052199 | -0.0040546 | -0.0091879 | -0.0031895 | -0.0082093 | 0.00066224 | 0.074501 | 0.052665 | -0.015432 | 0.019653 | 0.0004978 | -1.6571 | -0.059509 | -122.0718 | 0.064087 | -121.2296 | -121.9757 | -121.9803 | -73.9609 | -0.009155 | -122.0718 | 0.07782 | -118.5608 | -121.5591 | -121.0785 | -0.064087 | -0.12817 | -0.004578 | 0.7782 | 0.027465 | 0.032043 | 0.091552 | 0.09613 | -0.064087 | -0.07782 | 0.009155 | 3.447 | 0.92926 | 0.44861 | 0.99335 | 0.51269 | 0.84229 | 122.1359 | 3.511 | 122.1497 | 122.0123 | 122.0627 | 121.9482 | 121.9986 | -122.1405 | -122.1405 | 122.0718 | 122.0856 | 120.3506 | 48.0469
2120.2812 | 122.1817 | -122.0306 | 0.1236 | -0.0060272 | 0.0018435 | 0.054121 | 0.054549 | 4.192e-06 | -0.0068381 | -0.0070347 | -0.0051575 | 0.0057892 | 0.07386 | 0.063132 | -0.013723 | 0.022644 | -0.0027066 | -1.6891 | -0.013733 | -122.1359 | -0.068665 | -121.4081 | -122.1085 | -122.113 | -74.2813 | 0.018311 | -122.081 | -0.022888 | -118.6569 | -121.7056 | -121.2479 | -0.10528 | -0.13733 | -0.19226 | 0.62256 | -0.082397 | -0.077819 | 0.022888 | 0.027466 | -0.050354 | -0.10528 | -0.14648 | 3.3737 | 0.78278 | 0.32501 | 0.83313 | 0.37537 | 0.72784 | 122.0673 | 3.4241 | 122.0581 | 122.1222 | 122.0993 | 122.0169 | 122.049 | -122.2595 | -122.2046 | 121.962 | 122.0078 | 120.3415 | 47.7493
2122.0469 | 122.2229 | -122.0123 | 0.10071 | -0.021286 | 0.0016299 | 0.056898 | 0.054549 | 4.192e-06 | -0.0083335 | -0.0027621 | -0.0082093 | 0.0038666 | 0.075783 | 0.06655 | -0.014791 | 0.022217 | -0.0014248 | -1.6846 | -0.013733 | -122.081 | 0 | -121.3486 | -122.0718 | -122.0947 | -74.4553 | 0.050354 | -122.081 | 0.032043 | -118.5745 | -121.6919 | -121.2479 | -0.068665 | -0.11444 | -0.10071 | 0.66376 | -0.082398 | -0.059509 | -0.013733 | 0.009156 | -0.068665 | -0.050354 | -0.068665 | 3.4378 | 0.76446 | 0.32043 | 0.83313 | 0.3891 | 0.73242 | 122.081 | 3.5065 | 122.113 | 122.0673 | 122.1313 | 121.9986 | 122.0627 | -122.1817 | -122.1817 | 122.0123 | 122.0444 | 120.3278 | 47.5571
2123.7969 | 122.2916 | -121.9849 | 0.07782 | -0.013657 | -0.0028561 | 0.057326 | 0.051131 | -0.0019184 | -0.0079061 | -0.0029759 | -0.0082093 | 0.001303 | 0.074074 | 0.06185 | -0.013937 | 0.021149 | -0.0033474 | -1.6891 | -0.059509 | -122.0718 | 0.059509 | -121.2662 | -121.9894 | -121.9894 | -74.6292 | -0.013733 | -122.0856 | 0.082397 | -118.4555 | -121.5775 | -121.1838 | -0.086975 | -0.13733 | -0.018311 | 0.71869 | -0.004578 | -0.004578 | 0.082397 | 0.082397 | -0.10071 | -0.091553 | 0.004577 | 3.5294 | 0.80109 | 0.40741 | 0.90179 | 0.50812 | 0.80566 | 122.1313 | 3.6301 | 122.168 | 122.0123 | 122.0718 | 121.9254 | 121.9711 | -122.1497 | -122.1634 | 122.0444 | 122.0673 | 120.2957 | 47.3557
2125.4844 | 122.1817 | -122.0078 | 0.11902 | -0.0060272 | -0.0009335 | 0.05583 | 0.054335 | -0.0046954 | -0.0096151 | -0.0025485 | -0.0021057 | 0.0023712 | 0.077278 | 0.060996 | -0.012228 | 0.023926 | -0.000784 | -1.7303 | -0.004578 | -122.113 | -0.073242 | -121.4264 | -122.1268 | -122.1451 | -75.1419 | 0.036621 | -122.1451 | -0.036621 | -118.5425 | -121.7239 | -121.3074 | -0.10529 | -0.1236 | -0.19226 | 0.58136 | -0.13733 | -0.11902 | -0.032044 | -0.013733 | -0.13733 | -0.082398 | -0.15564 | 3.4653 | 0.70038 | 0.28381 | 0.83771 | 0.42114 | 0.68664 | 122.0398 | 3.6026 | 122.1085 | 122.1085 | 122.1817 | 122.0032 | 122.0444 | -122.2321 | -122.2641 | 121.9345 | 121.9711 | 120.2774 | 46.8658
2127.2344 | 122.287 | -122.0169 | 0.07782 | -0.013657 | 0.0020571 | 0.056471 | 0.051558 | -0.003841 | -0.0083335 | -0.0048985 | -0.0082093 | 0.003012 | 0.072578 | 0.055228 | -0.013296 | 0.022217 | -0.0009976 | -1.7853 | -0.041199 | -122.0856 | 0.004578 | -121.3211 | -122.0352 | -122.049 | -75.293 | 0.004578 | -122.081 | 0.068665 | -118.4143 | -121.582 | -121.1929 | -0.068664 | -0.11902 | -0.073242 | 0.6958 | -0.032043 | -0.01831 | 0.036621 | 0.050354 | -0.064087 | -0.073242 | -0.009155 | 3.6026 | 0.82398 | 0.43488 | 0.88806 | 0.49896 | 0.76447 | 122.0901 | 3.6667 | 122.1497 | 122.0444 | 122.0856 | 121.9757 | 122.0215 | -122.1634 | -122.1588 | 122.0215 | 122.0856 | 120.2316 | 46.7239
2129 | 122.1771 | -122.0352 | 0.10071 | -0.013657 | 0.0022709 | 0.058394 | 0.055617 | 0.0040632 | -0.0081197 | -0.0042575 | -0.011261 | 0.0040802 | 0.07621 | 0.062064 | -0.012655 | 0.023712 | 0.000925 | -1.8539 | -0.004578 | -122.0901 | -0.086975 | -121.4447 | -122.1588 | -122.1588 | -75.5493 | 0.027466 | -122.1085 | -0.004578 | -118.5379 | -121.7331 | -121.2708 | -0.054932 | -0.10529 | -0.18768 | 0.59051 | -0.1236 | -0.1236 | -0.068664 | -0.068664 | -0.073242 | -0.073242 | -0.10529 | 3.4973 | 0.76447 | 0.30212 | 0.83771 | 0.37537 | 0.64545 | 122.0032 | 3.5706 | 122.1039 | 122.0856 | 122.1359 | 122.0306 | 122.0627 | -122.1909 | -122.2092 | 121.9482 | 122.0306 | 120.1813 | 46.4859
2130.6875 | 122.1771 | -122.0215 | 0.10529 | -0.013657 | 0.0031253 | 0.054335 | 0.055403 | -0.0017048 | -0.0087607 | -0.0038303 | -0.0051575 | 0.0038666 | 0.074715 | 0.065055 | -0.013937 | 0.02243 | 0.0041294 | -1.799 | -0.018311 | -122.1222 | -0.036621 | -121.3806 | -122.1176 | -122.1451 | -75.8652 | 0.032043 | -122.113 | -0.009155 | -118.5196 | -121.7422 | -121.3028 | -0.10071 | -0.1236 | -0.14191 | 0.64087 | -0.1236 | -0.096131 | -0.022889 | 0.004577 | -0.091553 | -0.073243 | -0.11444 | 3.5019 | 0.71869 | 0.27923 | 0.81024 | 0.37079 | 0.74158 | 122.0856 | 3.5934 | 122.1039 | 122.1039 | 122.1451 | 122.0032 | 122.0535 | -122.2275 | -122.2183 | 121.9849 | 122.0123 | 120.2225 | 46.1563
2132.4531 | 122.287 | -121.9849 | 0.09613 | -0.021286 | 0.0012027 | 0.058607 | 0.053053 | -0.0025592 | -0.0064109 | -0.0014805 | -0.0051575 | 0.0023712 | 0.075142 | 0.063773 | -0.013082 | 0.021149 | -0.0009976 | -1.8265 | -0.073242 | -122.0718 | 0.050354 | -121.257 | -122.0215 | -122.0306 | -75.975 | -0.013733 | -122.0947 | 0.073242 | -118.3502 | -121.5866 | -121.1563 | -0.086975 | -0.16937 | -0.045776 | 0.72784 | -0.045777 | -0.036621 | 0.041198 | 0.050354 | -0.10986 | -0.10986 | -0.022888 | 3.6346 | 0.82855 | 0.39825 | 0.93842 | 0.50812 | 0.81482 | 122.1222 | 3.7445 | 122.168 | 121.9986 | 122.081 | 121.9116 | 121.9711 | -122.168 | -122.1909 | 122.0352 | 122.0581 | 120.1584 | 46.0098
2134.2031 | 122.1725 | -122.0352 | 0.11902 | -0.013657 | -0.0041379 | 0.054121 | 0.053267 | -0.0029864 | -0.0087607 | -0.0042575 | -0.0082093 | 0.0045074 | 0.074501 | 0.064414 | -0.012869 | 0.021362 | -0.0001432 | -1.7807 | -0.036621 | -122.1313 | -0.064087 | -121.3852 | -122.113 | -122.1222 | -76.1536 | 0.027466 | -122.1176 | -0.050354 | -118.4189 | -121.6873 | -121.2845 | -0.096131 | -0.15564 | -0.18311 | 0.65002 | -0.086975 | -0.07782 | 0.009156 | 0.018311 | -0.082398 | -0.091553 | -0.16937 | 3.6163 | 0.75073 | 0.3479 | 0.83313 | 0.4303 | 0.74616 | 122.0673 | 3.6987 | 122.0673 | 122.0947 | 122.1451 | 121.9986 | 122.0627 | -122.2504 | -122.2366 | 121.9711 | 121.9849 | 120.2545 | 45.8817
2135.875 | 122.2595 | -122.0078 | 0.086975 | -0.013657 | -0.0015743 | 0.057326 | 0.051985 | 0.0010724 | -0.0083335 | -0.0046847 | -0.0051575 | 0.0023712 | 0.075783 | 0.055442 | -0.01415 | 0.019653 | 0.0032748 | -1.8723 | -0.041199 | -122.0764 | -0.018311 | -121.344 | -122.0718 | -122.0627 | -76.2268 | -0.009155 | -122.0947 | 0.027466 | -118.3228 | -121.6324 | -121.1838 | -0.068665 | -0.12817 | -0.10529 | 0.66376 | -0.054932 | -0.064087 | 0.013733 | 0.004578 | -0.086976 | -0.09613 | -0.059509 | 3.685 | 0.82397 | 0.37537 | 0.91095 | 0.46234 | 0.73242 | 122.0581 | 3.772 | 122.1222 | 122.0352 | 122.0856 | 121.9666 | 121.9986 | -122.1634 | -122.1817 | 121.9894 | 122.0352 | 120.1355 | 45.7809
2137.6406 | 122.168 | -122.0581 | 0.1236 | -0.013657 | -0.0015743 | 0.053694 | 0.054121 | -0.00020941 | -0.0094015 | -0.0036167 | -0.0082093 | 0.0049346 | 0.078346 | 0.063773 | -0.015005 | 0.02179 | 0.0004978 | -1.8448 | -0.013733 | -122.1451 | -0.082397 | -121.4218 | -122.1222 | -122.1451 | -76.4786 | 0.032043 | -122.1268 | -0.050354 | -118.3365 | -121.6827 | -121.2341 | -0.086976 | -0.13733 | -0.20599 | 0.63629 | -0.086976 | -0.064087 | 0 | 0.022889 | -0.068665 | -0.091553 | -0.17395 | 3.7216 | 0.82397 | 0.37537 | 0.89264 | 0.44403 | 0.72327 | 122.0627 | 3.7903 | 122.0764 | 122.1313 | 122.1588 | 122.0444 | 122.0901 | -122.2687 | -122.2504 | 121.9757 | 122.0078 | 120.2133 | 45.5795
2139.3438 | 122.2961 | -121.9803 | 0.064087 | -0.013657 | -0.0017881 | 0.054549 | 0.052199 | -0.0034136 | -0.0068381 | -0.0021213 | -0.011261 | 0.0010894 | 0.07386 | 0.055655 | -0.015219 | 0.022003 | 0.0015658 | -1.8082 | -0.050354 | -122.0901 | 0.059509 | -121.2158 | -121.9574 | -121.9894 | -76.4236 | -0.009155 | -122.0901 | 0.073242 | -118.1442 | -121.5317 | -121.0831 | -0.10986 | -0.11444 | -0.004578 | 0.76447 | -0.009155 | 0.022889 | 0.10071 | 0.13275 | -0.10986 | -0.073242 | 0.009155 | 3.8361 | 0.89722 | 0.44861 | 1.0071 | 0.55847 | 0.87433 | 122.1497 | 3.9459 | 122.1634 | 122.0398 | 122.081 | 121.9299 | 121.9711 | -122.1542 | -122.1542 | 122.0398 | 122.0535 | 120.1721 | 45.5566
2141.0938 | 122.287 | -122.0078 | 0.09613 | -0.013657 | -0.0009335 | 0.054335 | 0.05284 | -0.0019184 | -0.0076925 | -0.0029759 | -0.011261 | 0.0021576 | 0.074715 | 0.062705 | -0.014364 | 0.023499 | -0.0001432 | -1.8082 | -0.041199 | -122.0993 | 0.064087 | -121.2616 | -122.0078 | -122.0123 | -76.561 | 0.009155 | -122.081 | 0.064087 | -118.1168 | -121.5363 | -121.0922 | -0.091553 | -0.13733 | -0.032043 | 0.74615 | -0.004578 | 0 | 0.086975 | 0.091553 | -0.073243 | -0.086975 | -0.032043 | 3.891 | 0.91553 | 0.4715 | 0.98877 | 0.54474 | 0.83771 | 122.1634 | 3.9642 | 122.1451 | 122.0581 | 122.0901 | 121.9666 | 122.0169 | -122.1954 | -122.1771 | 122.0718 | 122.0718 | 120.1996 | 45.4468
2142.8594 | 122.2824 | -121.9986 | 0.091553 | -0.013657 | -0.0022153 | 0.054549 | 0.050276 | -0.0029864 | -0.0087607 | -0.0023349 | -0.0082093 | 0.0017304 | 0.073433 | 0.065482 | -0.013723 | 0.021149 | -0.000784 | -1.8173 | -0.036621 | -122.0993 | 0.054932 | -121.2662 | -122.0078 | -122.0169 | -76.6663 | -0.018311 | -122.1085 | 0.064087 | -118.0481 | -121.5454 | -121.0739 | -0.10071 | -0.12817 | -0.036621 | 0.73242 | -0.018311 | -0.009155 | 0.082397 | 0.091553 | -0.10986 | -0.10986 | -0.027466 | 3.9505 | 0.92468 | 0.45319 | 1.0345 | 0.56305 | 0.83313 | 122.1542 | 4.0604 | 122.1725 | 122.0627 | 122.0901 | 121.962 | 121.9803 | -122.1909 | -122.2 | 122.0535 | 122.0627 | 120.1813 | 45.3323
2144.6094 | 122.2641 | -122.0078 | 0.07782 | -0.021286 | 0.0018435 | 0.057326 | 0.054976 | -0.0029864 | -0.0079061 | -0.0066073 | -0.0082093 | 0.0038666 | 0.074287 | 0.064414 | -0.01351 | 0.021576 | -0.0016384 | -1.9272 | -0.054932 | -122.0398 | 0.050354 | -121.2753 | -122.0398 | -122.0398 | -76.6846 | 0.004578 | -122.1039 | 0.073242 | -117.9703 | -121.5729 | -121.0648 | -0.032044 | -0.13275 | -0.027466 | 0.73242 | -0.032044 | -0.032044 | 0 | 0 | -0.096131 | -0.073242 | -0.004578 | 4.0375 | 0.94299 | 0.43488 | 1.0391 | 0.53101 | 0.76447 | 122.0901 | 4.1336 | 122.1771 | 121.9849 | 122.1085 | 121.9528 | 122.0123 | -122.1176 | -122.1817 | 122.0581 | 122.081 | 120.0806 | 45.3232
2146.2969 | 122.1909 | -122.0444 | 0.11444 | -0.021286 | -0.0002927 | 0.055189 | 0.054976 | -0.00020941 | -0.0083335 | -0.0076755 | -0.0082093 | 0.005362 | 0.078133 | 0.064627 | -0.016287 | 0.024353 | 0.002634 | -2.0004 | -0.009155 | -122.1039 | -0.07782 | -121.4493 | -122.1634 | -122.1588 | -77.1378 | 0.041199 | -122.113 | -0.013733 | -117.9016 | -121.6873 | -121.1472 | -0.059509 | -0.1236 | -0.19226 | 0.59509 | -0.11444 | -0.11902 | -0.054931 | -0.059509 | -0.068664 | -0.073242 | -0.12817 | 4.1428 | 0.89722 | 0.35706 | 0.96588 | 0.42572 | 0.6546 | 122.0261 | 4.2114 | 122.0993 | 122.0947 | 122.1542 | 122.0352 | 122.0856 | -122.2183 | -122.2275 | 121.9666 | 122.0306 | 120.0439 | 44.9066
2148.0625 | 122.2458 | -122.0032 | 0.07782 | -0.013657 | 0.0031253 | 0.055403 | 0.053694 | -0.00085021 | -0.0070517 | -0.0036167 | -0.0051575 | 0.0038666 | 0.074287 | 0.057792 | -0.015646 | 0.022003 | -0.0009976 | -2.0142 | -0.036621 | -122.0993 | -0.004578 | -121.3577 | -122.049 | -122.0673 | -77.2522 | -0.004578 | -122.0947 | 0.022888 | -117.5583 | -121.5775 | -121.0831 | -0.09613 | -0.11444 | -0.082398 | 0.64545 | -0.064087 | -0.045776 | 0.032043 | 0.050354 | -0.091553 | -0.082398 | -0.054932 | 4.4449 | 0.92011 | 0.42572 | 1.0117 | 0.51727 | 0.74158 | 122.0947 | 4.5364 | 122.1176 | 122.0627 | 122.0901 | 121.9666 | 121.9986 | -122.1771 | -122.1725 | 121.9986 | 122.0261 | 119.989 | 44.751
2149.75 | 122.3099 | -121.9803 | 0.054932 | -0.021286 | 0.0026981 | 0.054976 | 0.056258 | -0.0025592 | -0.0064109 | -0.0019077 | -0.0051575 | 0.0025848 | 0.073433 | 0.061637 | -0.015432 | 0.022644 | 0.000925 | -1.973 | -0.059509 | -122.0718 | 0.064087 | -121.2845 | -122.0444 | -122.0123 | -77.1973 | -0.009155 | -122.0901 | 0.10529 | -117.1921 | -121.5271 | -120.9961 | -0.091552 | -0.11444 | 0.009155 | 0.6958 | -0.032043 | -0.064087 | 0.059509 | 0.027465 | -0.10986 | -0.064087 | 0.050354 | 4.7882 | 0.98419 | 0.45319 | 1.0941 | 0.56305 | 0.78735 | 122.1359 | 4.8981 | 122.1954 | 122.0123 | 122.081 | 121.9208 | 121.9711 | -122.1268 | -122.1451 | 122.0444 | 122.0856 | 120.0073 | 44.783
2151.5 | 122.3007 | -122.0078 | 0.082397 | 0.0016023 | -0.0026425 | 0.055403 | 0.052626 | -0.00020941 | -0.011751 | -0.0021213 | -0.0082093 | 0.0040802 | 0.076424 | 0.062278 | -0.013082 | 0.022217 | -0.000784 | -1.918 | -0.045776 | -122.1039 | 0.059509 | -121.2433 | -121.962 | -121.9849 | -77.2614 | -0.013733 | -122.081 | 0.082397 | -116.7755 | -121.4813 | -120.9869 | -0.096131 | -0.12817 | -0.022888 | 0.76447 | 0.022888 | 0.045776 | 0.11902 | 0.14191 | -0.073243 | -0.09613 | 0 | 5.2322 | 1.0208 | 0.52643 | 1.0941 | 0.59967 | 0.8606 | 122.1634 | 5.3055 | 122.1634 | 122.0581 | 122.0673 | 121.962 | 121.994 | -122.1863 | -122.1634 | 122.0673 | 122.0901 | 120.0897 | 44.7464
2153.1875 | 122.1863 | -122.049 | 0.11444 | -0.021286 | -0.0002927 | 0.055617 | 0.054335 | -0.0012774 | -0.0089743 | -0.0055393 | -0.0051575 | 0.0032256 | 0.076424 | 0.067405 | -0.013082 | 0.020294 | -0.0003568 | -1.9226 | -0.018311 | -122.113 | -0.032043 | -121.3623 | -122.0947 | -122.0947 | -77.4994 | 0.045776 | -122.1268 | -0.027466 | -116.478 | -121.6095 | -121.106 | -0.064087 | -0.13275 | -0.14648 | 0.68664 | -0.045777 | -0.045777 | 0.01831 | 0.01831 | -0.07782 | -0.068665 | -0.14191 | 5.571 | 0.94299 | 0.43945 | 1.0208 | 0.51727 | 0.75073 | 122.081 | 5.6488 | 122.0993 | 122.0947 | 122.1725 | 122.0306 | 122.0947 | -122.2275 | -122.2412 | 122.0169 | 122.0215 | 120.1263 | 44.5496
2154.9219 | 122.1771 | -122.0261 | 0.11444 | -0.021286 | 0.0035525 | 0.056471 | 0.057967 | 0.0040632 | -0.0091879 | -0.0029759 | -0.011261 | 0.0051482 | 0.076851 | 0.068045 | -0.013082 | 0.023712 | 0.0011386 | -2.0737 | -0.009155 | -122.1222 | -0.11444 | -121.4767 | -122.1954 | -122.1954 | -77.7512 | 0.036621 | -122.1313 | -0.041199 | -116.0156 | -121.6782 | -121.106 | -0.09613 | -0.1236 | -0.22888 | 0.54932 | -0.16937 | -0.16937 | -0.073243 | -0.073243 | -0.10529 | -0.07782 | -0.15564 | 6.0104 | 0.9201 | 0.3479 | 1.0254 | 0.45319 | 0.64545 | 122.0078 | 6.1157 | 122.0901 | 122.113 | 122.168 | 122.0169 | 122.0627 | -122.2366 | -122.2458 | 121.9116 | 121.9849 | 119.9524 | 44.2749
2156.6719 | 122.2321 | -121.9849 | 0.13275 | -0.013657 | 0.0001345 | 0.054762 | 0.054976 | 0.00064519 | -0.0081197 | -0.0023349 | -0.0082093 | 0.0049346 | 0.12342 | 0.060355 | -0.01351 | 0.024139 | 0.002634 | -1.9867 | 0.013733 | -122.1085 | 0.027466 | -121.3165 | -122.0581 | -122.0673 | -73.4116 | 0.064087 | -122.0718 | 0.059509 | -30.0156 | -121.5225 | -120.9183 | -0.1236 | -0.11902 | -0.10529 | 0.66833 | -0.082398 | -0.073242 | 0.041198 | 0.050354 | -0.086975 | -0.068664 | -0.073242 | 91.9693 | 1.0666 | 0.46234 | 1.1536 | 0.54932 | 0.79193 | 122.1359 | 92.0563 | 122.1313 | 122.1222 | 122.1359 | 121.9986 | 122.049 | -122.2412 | -122.2046 | 122.0123 | 122.0444 | 119.9982 | 48.5733
2158.4219 | 122.1863 | -121.994 | 0.16022 | -0.013657 | 0.0031253 | 0.055617 | 0.055189 | -0.0017048 | -0.0079061 | -0.00083947 | -0.011261 | 0.0051482 | 0.13111 | 0.065909 | -0.012228 | 0.025208 | -0.000784 | -2.1011 | 0.018311 | -122.0947 | -0.064087 | -121.4447 | -122.1542 | -122.1497 | -73.1735 | 0.073242 | -122.0947 | 0.013733 | -21.3684 | -121.582 | -120.932 | -0.10071 | -0.14191 | -0.2243 | 0.54932 | -0.15564 | -0.16022 | -0.054931 | -0.059509 | -0.10071 | -0.086975 | -0.14648 | 100.6256 | 1.062 | 0.41199 | 1.1627 | 0.5127 | 0.65002 | 122.0306 | 100.7263 | 122.1085 | 122.113 | 122.168 | 122.0123 | 122.0673 | -122.2549 | -122.2549 | 121.9299 | 122.0078 | 119.8929 | 48.8205
2160.1094 | 122.1634 | -121.9803 | 0.14191 | 0.0016023 | 0.0016299 | 0.054335 | 0.055403 | 0.0042768 | -0.0083335 | -0.0027621 | -0.0051575 | 0.0060028 | 0.12769 | 0.0642 | -0.01116 | 0.023499 | 0.0013522 | -2.0828 | 0.032043 | -122.081 | -0.027466 | -121.3852 | -122.1176 | -122.1085 | -73.2239 | 0.082397 | -122.1085 | -0.004578 | -21.5652 | -121.5729 | -120.9183 | -0.10071 | -0.10986 | -0.16937 | 0.59509 | -0.12817 | -0.13733 | -0.027465 | -0.036621 | -0.12817 | -0.05951 | -0.14649 | 100.415 | 1.062 | 0.40741 | 1.1902 | 0.53558 | 0.6958 | 122.0535 | 100.5432 | 122.1039 | 122.113 | 122.1909 | 122.0123 | 122.0627 | -122.2229 | -122.2504 | 121.9528 | 121.9757 | 119.8975 | 48.7564
2161.8594 | 122.2641 | -121.962 | 0.1236 | -0.021286 | -0.0007199 | 0.057326 | 0.053267 | -0.003841 | -0.0089743 | -0.0012669 | -0.0051575 | 0.0025848 | 0.12769 | 0.063346 | -0.013937 | 0.022858 | -0.0009976 | -2.1103 | -0.022888 | -122.0261 | 0.054932 | -121.2616 | -122.0169 | -122.0078 | -73.1827 | 0.041199 | -122.0261 | 0.091553 | -20.6955 | -121.4355 | -120.8176 | -0.064087 | -0.14648 | -0.068664 | 0.70038 | -0.045776 | -0.054932 | 0.018311 | 0.009155 | -0.064087 | -0.082397 | -0.032043 | 101.2665 | 1.1444 | 0.52643 | 1.2085 | 0.59051 | 0.76447 | 122.081 | 101.3306 | 122.1176 | 122.0032 | 122.0673 | 121.9391 | 122.0032 | -122.1497 | -122.1497 | 122.0169 | 122.0535 | 119.8517 | 48.7793
2163.5469 | 122.3236 | -121.9666 | 0.10986 | -0.0060272 | -0.0028561 | 0.053267 | 0.051558 | -0.0027728 | -0.0076925 | -0.0040439 | -0.0082093 | 0.001944 | 0.12962 | 0.060355 | -0.01351 | 0.022644 | 0.0017794 | -2.0508 | -0.022888 | -122.0627 | 0.091553 | -121.2387 | -121.9391 | -121.962 | -72.9858 | 0.036621 | -122.0215 | 0.16022 | -20.0272 | -121.3394 | -120.7626 | -0.09613 | -0.13275 | -0.01831 | 0.72785 | 0.004578 | 0.027466 | 0.10071 | 0.1236 | -0.054931 | -0.073242 | 0.050354 | 101.9394 | 1.2039 | 0.62714 | 1.2588 | 0.68207 | 0.82398 | 122.1542 | 101.9943 | 122.1817 | 122.0398 | 122.0581 | 121.9437 | 122.0032 | -122.1725 | -122.1313 | 122.0581 | 122.1268 | 119.9158 | 48.9807
2165.2969 | 122.2137 | -121.9528 | 0.14648 | -0.013657 | 0.0016299 | 0.055189 | 0.053908 | 0.0042768 | -0.010043 | -0.0029759 | -0.0051575 | 0.0049346 | 0.13004 | 0.062064 | -0.015646 | 0.024139 | 0.000925 | -2.0508 | 0.032043 | -122.081 | 0 | -121.3165 | -122.049 | -122.081 | -72.9538 | 0.064087 | -122.0581 | 0.041199 | -20.4941 | -121.463 | -120.8405 | -0.12817 | -0.11444 | -0.14648 | 0.63629 | -0.12817 | -0.09613 | 0 | 0.032044 | -0.10528 | -0.082397 | -0.10529 | 101.4587 | 1.1124 | 0.48981 | 1.2177 | 0.59509 | 0.76447 | 122.081 | 101.564 | 122.0993 | 122.113 | 122.1222 | 121.9849 | 122.0169 | -122.2275 | -122.2046 | 121.9528 | 121.994 | 119.902 | 48.999
2167.0469 | 122.2641 | -121.962 | 0.11444 | -0.013657 | -0.0017881 | 0.055617 | 0.051985 | -0.00063661 | -0.0072653 | -0.0023349 | -0.0051575 | 0.003012 | 0.12897 | 0.056296 | -0.014364 | 0.022217 | 0.0019932 | -2.1515 | -0.004578 | -122.0444 | 0.022888 | -121.3028 | -122.0169 | -122.0078 | -72.789 | 0.045776 | -122.049 | 0.073242 | -21.167 | -121.3806 | -120.7535 | -0.082398 | -0.11902 | -0.091553 | 0.65918 | -0.045776 | -0.054932 | 0.036622 | 0.027466 | -0.086975 | -0.068665 | -0.041199 | 100.795 | 1.2085 | 0.58136 | 1.2955 | 0.66833 | 0.74158 | 122.0673 | 100.882 | 122.1222 | 122.0398 | 122.0947 | 121.9574 | 122.0078 | -122.1588 | -122.1634 | 121.9849 | 122.0352 | 119.8105 | 49.173
2168.7344 | 122.2458 | -121.9666 | 0.12817 | -0.028916 | 0.0029117 | 0.05583 | 0.05348 | -0.0010638 | -0.0064109 | -0.0048985 | -0.0051575 | 0.001944 | 0.13026 | 0.059501 | -0.014791 | 0.025848 | 0.000925 | -2.1927 | -0.004578 | -122.0581 | 0.027466 | -121.3074 | -122.0444 | -122.0261 | -72.8165 | 0.036621 | -122.0444 | 0.050354 | -20.256 | -121.4035 | -120.7672 | -0.091552 | -0.13275 | -0.10071 | 0.65918 | -0.059509 | -0.07782 | 0.032043 | 0.013732 | -0.07782 | -0.091553 | -0.07782 | 101.7105 | 1.1993 | 0.56305 | 1.2772 | 0.64087 | 0.75073 | 122.0856 | 101.7883 | 122.0947 | 122.0535 | 122.081 | 121.962 | 122.0032 | -122.1863 | -122.1725 | 121.994 | 122.0169 | 119.7739 | 49.1501
2170.4844 | 122.2137 | -121.962 | 0.12817 | -0.021286 | 0.0022709 | 0.056044 | 0.05348 | 0.0034222 | -0.0098287 | -0.0034031 | -0.0082093 | 0.0049346 | 0.13132 | 0.064627 | -0.014791 | 0.026276 | 0.0062656 | -2.1286 | 0.022888 | -122.0581 | 0.032043 | -121.312 | -122.0581 | -122.0627 | -72.8165 | 0.064087 | -122.0535 | 0.045776 | -19.9493 | -121.4539 | -120.7809 | -0.09613 | -0.10529 | -0.096131 | 0.65002 | -0.10071 | -0.09613 | -0.004578 | 0 | -0.091553 | -0.064087 | -0.082398 | 102.0126 | 1.181 | 0.50812 | 1.2726 | 0.59967 | 0.74615 | 122.0901 | 102.1042 | 122.0993 | 122.081 | 122.1176 | 121.9849 | 122.0261 | -122.1863 | -122.1817 | 121.994 | 122.0078 | 119.8334 | 49.1455
2172.1875 | 122.1542 | -121.9986 | 0.14191 | -0.013657 | 0.0048343 | 0.056258 | 0.055403 | 0.002995 | -0.0085471 | -0.0031895 | -0.0051575 | 0.0038666 | 0.13197 | 0.068473 | -0.013937 | 0.024353 | 0.0013522 | -2.2064 | 0.009155 | -122.0764 | -0.032043 | -121.3806 | -122.113 | -122.1222 | -73.1232 | 0.068665 | -122.0718 | 0.004578 | -18.4982 | -121.5271 | -120.7901 | -0.07782 | -0.13275 | -0.17395 | 0.61798 | -0.1236 | -0.11444 | -0.045776 | -0.036621 | -0.073242 | -0.073242 | -0.13733 | 103.5004 | 1.2085 | 0.4715 | 1.2817 | 0.54474 | 0.6958 | 122.0444 | 103.5736 | 122.0764 | 122.0856 | 122.1405 | 122.0078 | 122.0673 | -122.2183 | -122.2137 | 121.9666 | 122.0032 | 119.7922 | 48.8754
2173.9375 | 122.1771 | -121.9986 | 0.16937 | -0.013657 | -0.0013607 | 0.053908 | 0.054335 | -0.0053362 | -0.0079061 | -0.0027621 | -0.0082093 | 0.0045074 | 0.13026 | 0.066123 | -0.013082 | 0.023926 | 0.004343 | -2.1835 | 0.050354 | -122.0856 | -0.045776 | -121.3669 | -122.0856 | -122.1085 | -72.8073 | 0.086975 | -122.0764 | -0.009155 | -19.2947 | -121.4676 | -120.7901 | -0.086975 | -0.11902 | -0.21515 | 0.63171 | -0.10986 | -0.086975 | -0.022888 | 0 | -0.07782 | -0.082398 | -0.17853 | 102.7039 | 1.2085 | 0.53101 | 1.2863 | 0.60883 | 0.71869 | 122.0398 | 102.7817 | 122.0673 | 122.1359 | 122.1634 | 122.049 | 122.0856 | -122.2549 | -122.2458 | 121.9528 | 121.9894 | 119.8151 | 49.1913
2175.6875 | 122.2275 | -121.9986 | 0.16022 | -0.0060272 | -0.0002927 | 0.054976 | 0.055189 | 0.00021799 | -0.0083335 | -0.0012669 | -0.0051575 | 0.0042938 | 0.13047 | 0.063773 | -0.014578 | 0.025635 | 0.000925 | -2.1881 | 0.022888 | -122.0901 | -0.018311 | -121.3577 | -122.0535 | -122.081 | -72.8806 | 0.064087 | -122.0764 | 0.045776 | -19.2719 | -121.4264 | -120.7031 | -0.091553 | -0.13733 | -0.17853 | 0.64087 | -0.082398 | -0.054932 | 0.009155 | 0.036621 | -0.07782 | -0.09613 | -0.11444 | 102.7267 | 1.2955 | 0.5722 | 1.3733 | 0.65002 | 0.73242 | 122.0718 | 102.8046 | 122.1222 | 122.113 | 122.1405 | 122.0215 | 122.0627 | -122.2504 | -122.2366 | 121.9803 | 122.0444 | 119.8105 | 49.118
2177.4531 | 122.1771 | -121.9894 | 0.14648 | -0.021286 | -0.0013607 | 0.053908 | 0.051558 | 0.001286 | -0.010043 | -0.0046847 | -0.0051575 | 0.0049346 | 0.13239 | 0.069327 | -0.013082 | 0.023285 | 0.0022068 | -2.2293 | 0.027466 | -122.1085 | -0.036621 | -121.3806 | -122.0856 | -122.0947 | -73.1186 | 0.082397 | -122.0856 | 0 | -18.8553 | -121.4401 | -120.7443 | -0.11902 | -0.11902 | -0.18311 | 0.60883 | -0.10529 | -0.09613 | 0.013732 | 0.022888 | -0.09613 | -0.064087 | -0.14648 | 103.1342 | 1.2451 | 0.54932 | 1.3412 | 0.64545 | 0.72784 | 122.0718 | 103.2303 | 122.0856 | 122.1359 | 122.168 | 122.0169 | 122.0718 | -122.2549 | -122.2321 | 121.9528 | 121.9894 | 119.7601 | 48.8709
2179.1875 | 122.2275 | -121.9482 | 0.15564 | -0.013657 | 0.0031253 | 0.056044 | 0.054976 | 0.00043159 | -0.0089743 | -0.0036167 | -0.0082093 | 0.0057892 | 0.13175 | 0.065482 | -0.01351 | 0.02478 | 0.0030612 | -2.211 | 0.027466 | -122.0993 | 0.013733 | -121.3211 | -122.0535 | -122.0718 | -73.1186 | 0.086975 | -122.0673 | 0.064087 | -17.9626 | -121.3852 | -120.6619 | -0.15106 | -0.12817 | -0.14191 | 0.62714 | -0.1236 | -0.10529 | 0.027466 | 0.045776 | -0.11902 | -0.068665 | -0.091553 | 103.9856 | 1.2863 | 0.56305 | 1.4053 | 0.68207 | 0.7782 | 122.113 | 104.1046 | 122.1313 | 122.1268 | 122.1542 | 121.9757 | 122.0352 | -122.2549 | -122.2229 | 121.962 | 122.0123 | 119.7372 | 48.8297
2180.875 | 122.1542 | -121.9894 | 0.14191 | -0.013657 | 0.0018435 | 0.055189 | 0.053908 | -0.0010638 | -0.0091879 | -0.0029759 | -0.0082093 | 0.0042938 | 0.13346 | 0.060355 | -0.012869 | 0.024994 | 0.0017794 | -2.2842 | 0.018311 | -122.0444 | -0.022888 | -121.3898 | -122.1176 | -122.1268 | -72.9767 | 0.068665 | -122.081 | -0.013733 | -17.7429 | -121.4584 | -120.7352 | -0.054932 | -0.1236 | -0.16479 | 0.59967 | -0.13733 | -0.12817 | -0.082397 | -0.073242 | -0.091553 | -0.073242 | -0.15564 | 104.2465 | 1.2543 | 0.53101 | 1.3458 | 0.62256 | 0.6546 | 122.0215 | 104.3381 | 122.0673 | 122.0627 | 122.1497 | 122.0078 | 122.0581 | -122.1863 | -122.2229 | 121.9666 | 121.9757 | 119.7052 | 49.0128
2182.6406 | 122.2961 | -121.9299 | 0.12817 | -0.021286 | 0.0020571 | 0.056258 | 0.054121 | 0.0017132 | -0.0072653 | -0.0048985 | -0.0082093 | 0.0025848 | 0.13197 | 0.062491 | -0.012228 | 0.023926 | 0.0032748 | -2.3529 | -0.013733 | -122.049 | 0.036621 | -121.2845 | -122.0169 | -122.0261 | -72.67 | 0.036621 | -122.0627 | 0.1236 | -14.447 | -121.3165 | -120.5429 | -0.11902 | -0.14191 | -0.091553 | 0.64545 | -0.09613 | -0.086975 | 0.022888 | 0.032043 | -0.13275 | -0.091553 | -0.004578 | 107.4829 | 1.387 | 0.6134 | 1.5198 | 0.74616 | 0.76447 | 122.0856 | 107.6157 | 122.1863 | 122.0352 | 122.0993 | 121.9162 | 121.9666 | -122.1771 | -122.1909 | 121.9666 | 122.0535 | 119.577 | 49.2599
2184.3906 | 122.1771 | -122.0078 | 0.15564 | -0.013657 | -0.0028561 | 0.053694 | 0.050917 | -0.0023456 | -0.0094015 | -0.0038303 | -0.0051575 | 0.0017304 | 0.13624 | 0.064627 | -0.01351 | 0.023285 | 0.0039158 | -2.2659 | -0.004578 | -122.0901 | -0.009155 | -121.3165 | -122.0215 | -122.0444 | -72.5372 | 0.07782 | -122.0581 | -0.004578 | -12.4283 | -121.3852 | -120.6345 | -0.082398 | -0.16022 | -0.16479 | 0.69122 | -0.036622 | -0.013733 | 0.045776 | 0.068665 | -0.050354 | -0.07782 | -0.16022 | 109.5795 | 1.3733 | 0.62256 | 1.4236 | 0.67291 | 0.77362 | 122.081 | 109.6298 | 122.0535 | 122.0856 | 122.1359 | 122.0032 | 122.0856 | -122.2458 | -122.2137 | 121.9986 | 122.0032 | 119.7418 | 49.4705
2186.1406 | 122.1771 | -121.9849 | 0.16022 | -0.021286 | -0.0011471 | 0.056685 | 0.054549 | 0.001286 | -0.0064109 | -0.0048985 | -0.0051575 | 0.005362 | 0.13645 | 0.064627 | -0.01415 | 0.023712 | 0.004343 | -2.3163 | 0.018311 | -122.081 | 0.009155 | -121.3303 | -122.0673 | -122.0901 | -72.4686 | 0.068665 | -122.0581 | 0.013733 | -11.1374 | -121.3989 | -120.5887 | -0.096131 | -0.14191 | -0.15106 | 0.6546 | -0.10529 | -0.082398 | -0.009155 | 0.013733 | -0.073242 | -0.091552 | -0.14648 | 110.8475 | 1.3962 | 0.58594 | 1.4694 | 0.65918 | 0.75073 | 122.0901 | 110.9207 | 122.0718 | 122.0993 | 122.1268 | 122.0032 | 122.0535 | -122.2412 | -122.2183 | 121.994 | 121.9986 | 119.6686 | 49.5163
2187.8281 | 122.1588 | -121.9986 | 0.14648 | -0.013657 | 0.0018435 | 0.054549 | 0.054121 | -0.0012774 | -0.0079061 | -0.0027621 | -0.0051575 | 0.0060028 | 0.13453 | 0.054587 | -0.01415 | 0.023712 | 0.0056246 | -2.3621 | 0.013733 | -122.0764 | -0.032043 | -121.3531 | -122.1039 | -122.1085 | -72.6608 | 0.073242 | -122.081 | 0 | -11.5265 | -121.4127 | -120.607 | -0.07782 | -0.13275 | -0.17853 | 0.64545 | -0.10986 | -0.10529 | -0.032043 | -0.027466 | -0.082398 | -0.073242 | -0.14648 | 110.4721 | 1.3916 | 0.58594 | 1.474 | 0.66833 | 0.72327 | 122.0444 | 110.5545 | 122.081 | 122.0901 | 122.1542 | 122.0123 | 122.0718 | -122.2229 | -122.2275 | 121.9666 | 121.9986 | 119.6365 | 49.3378
2189.5781 | 122.2504 | -121.962 | 0.12817 | -0.0060272 | -0.0041379 | 0.056044 | 0.05049 | -0.0025592 | -0.010683 | -0.0034031 | -0.0082093 | 0.0017304 | 0.13731 | 0.058432 | -0.013296 | 0.024139 | 0.006052 | -2.4261 | 0.004578 | -122.0718 | 0.004578 | -121.2982 | -122.0306 | -122.0306 | -72.6151 | 0.032043 | -122.0306 | 0.068665 | -10.5606 | -121.3028 | -120.52 | -0.10986 | -0.1236 | -0.1236 | 0.66376 | -0.068665 | -0.068665 | 0.041198 | 0.041198 | -0.068665 | -0.096131 | -0.059509 | 111.4014 | 1.442 | 0.65918 | 1.5106 | 0.72785 | 0.77362 | 122.0764 | 111.47 | 122.0993 | 122.0764 | 122.0627 | 121.9666 | 121.994 | -122.2 | -122.1588 | 121.9666 | 122.0306 | 119.5358 | 49.3469
2191.3281 | 122.2046 | -121.9711 | 0.17395 | -0.013657 | 0.0005619 | 0.055617 | 0.054335 | 0.0010724 | -0.0061971 | -0.0061801 | -0.0051575 | 0.0049346 | 0.13517 | 0.059073 | -0.013082 | 0.026276 | 0.0069064 | -2.3575 | 0.027466 | -122.0947 | 0.022888 | -121.3074 | -122.0398 | -122.0444 | -72.6379 | 0.07782 | -122.049 | 0.045776 | -10.35 | -121.3303 | -120.5017 | -0.1236 | -0.14648 | -0.15106 | 0.66376 | -0.073243 | -0.068665 | 0.050354 | 0.054932 | -0.07782 | -0.09613 | -0.12817 | 111.6211 | 1.4694 | 0.64087 | 1.5472 | 0.71869 | 0.78735 | 122.1176 | 111.6989 | 122.0947 | 122.1222 | 122.1268 | 121.9986 | 122.049 | -122.2687 | -122.2229 | 121.994 | 122.0169 | 119.6136 | 49.3332
2193.0938 | 122.287 | -121.9391 | 0.11902 | -0.0060272 | 0.0001345 | 0.054762 | 0.053908 | 0.00043159 | -0.0081197 | -0.0025485 | -0.0051575 | 0.003012 | 0.13496 | 0.064414 | -0.014791 | 0.023926 | 0.0041294 | -2.4307 | -0.027466 | -122.0535 | 0.073242 | -121.2387 | -121.9803 | -121.9711 | -72.1893 | 0.041199 | -122.0352 | 0.12817 | -12.9822 | -121.2387 | -120.4376 | -0.11444 | -0.14649 | -0.045777 | 0.70038 | -0.032043 | -0.041199 | 0.082398 | 0.073242 | -0.09613 | -0.07782 | 0.009155 | 108.9569 | 1.5015 | 0.70038 | 1.5976 | 0.79651 | 0.81482 | 122.1268 | 109.053 | 122.1634 | 122.0261 | 122.0764 | 121.9116 | 121.9803 | -122.1725 | -122.1542 | 122.0123 | 122.0673 | 119.5084 | 49.7498
2194.7812 | 122.2137 | -121.9666 | 0.14191 | -0.013657 | 0.0009891 | 0.056044 | 0.056258 | 0.00085879 | -0.0070517 | -0.0021213 | -0.0051575 | 0.0034392 | 0.13773 | 0.062705 | -0.013296 | 0.024994 | 0.0069064 | -2.5131 | 0.018311 | -122.0764 | -0.027466 | -121.3898 | -122.1176 | -122.1085 | -71.9009 | 0.07782 | -122.0764 | 0.045776 | -11.412 | -121.3394 | -120.4651 | -0.10986 | -0.1236 | -0.16937 | 0.57678 | -0.14191 | -0.15106 | -0.032043 | -0.041199 | -0.10986 | -0.064087 | -0.096131 | 110.5545 | 1.5015 | 0.62714 | 1.6113 | 0.737 | 0.68664 | 122.0489 | 110.6644 | 122.1222 | 122.0947 | 122.1542 | 121.9849 | 122.0444 | -122.2183 | -122.2183 | 121.9391 | 122.0123 | 119.4534 | 50.0656
2196.5469 | 122.2504 | -121.9711 | 0.12817 | -0.021286 | -0.0015743 | 0.054762 | 0.051344 | -0.00020941 | -0.0064109 | -0.0023349 | -0.0082093 | 0.003012 | 0.13731 | 0.062918 | -0.01351 | 0.025421 | 0.0047702 | -2.504 | 0.013733 | -122.0306 | 0.022888 | -121.3028 | -122.0169 | -122.0215 | -71.8597 | 0.054932 | -122.0444 | 0.059509 | -11.4853 | -121.2296 | -120.3964 | -0.05951 | -0.11444 | -0.10529 | 0.66833 | -0.050354 | -0.045777 | 0.009156 | 0.013733 | -0.073243 | -0.073242 | -0.068665 | 110.4858 | 1.5747 | 0.74158 | 1.6479 | 0.81482 | 0.72785 | 122.0535 | 110.5591 | 122.1039 | 122.0444 | 122.0993 | 121.9849 | 122.0261 | -122.1588 | -122.1725 | 121.994 | 122.0306 | 119.4672 | 50.1114
2198.2969 | 122.3099 | -121.9482 | 0.12817 | -0.021286 | 0.0005619 | 0.056685 | 0.054335 | 4.192e-06 | -0.0083335 | -0.0055393 | -0.0021057 | 0.003012 | 0.13517 | 0.06655 | -0.016073 | 0.025208 | 0.0049838 | -2.4948 | -0.004578 | -121.9894 | 0.10071 | -121.2387 | -121.9849 | -121.9849 | -71.814 | 0.032043 | -122.0352 | 0.1236 | -12.9776 | -121.2021 | -120.314 | -0.041199 | -0.13275 | -0.027466 | 0.70953 | -0.036621 | -0.036621 | 0.004578 | 0.004578 | -0.086975 | -0.096131 | -0.004578 | 108.9706 | 1.6342 | 0.74615 | 1.7212 | 0.83313 | 0.75073 | 122.0901 | 109.0576 | 122.1588 | 121.9849 | 122.0673 | 121.9437 | 121.9803 | -122.1176 | -122.1634 | 122.0489 | 122.0718 | 119.4534 | 50.1343
2199.9844 | 122.1634 | -121.9894 | 0.15106 | -0.013657 | -7.9104e-05 | 0.056044 | 0.055617 | 0.0021406 | -0.0096151 | -0.0038303 | -0.0082093 | 0.0034392 | 0.13624 | 0.066336 | -0.015005 | 0.02478 | 0.005411 | -2.5589 | 0.027466 | -122.0901 | -0.068665 | -121.4355 | -122.1542 | -122.1497 | -71.9971 | 0.07782 | -122.0718 | 0 | -12.9135 | -121.3715 | -120.4102 | -0.10071 | -0.1236 | -0.21973 | 0.55389 | -0.16022 | -0.16479 | -0.059509 | -0.064087 | -0.082397 | -0.073242 | -0.15106 | 109.0759 | 1.5793 | 0.61798 | 1.6617 | 0.70038 | 0.6546 | 122.0215 | 109.1583 | 122.0718 | 122.1176 | 122.1497 | 122.0169 | 122.0673 | -122.2412 | -122.2229 | 121.9208 | 121.9894 | 119.4305 | 49.9924
2201.75 | 122.1954 | -121.9528 | 0.13733 | -0.013657 | -7.9104e-05 | 0.054335 | 0.054976 | -0.0036274 | -0.0096151 | -0.0027621 | -0.0051575 | 0.0038666 | 0.13474 | 0.062278 | -0.013937 | 0.024139 | 0.0062656 | -2.4857 | 0.041199 | -122.081 | -0.022888 | -121.3669 | -122.0673 | -122.0673 | -72.1985 | 0.073242 | -122.0627 | 0.041199 | -13.06 | -121.2799 | -120.3461 | -0.12817 | -0.09613 | -0.16022 | 0.58594 | -0.11444 | -0.11444 | 0.013733 | 0.013733 | -0.10986 | -0.064087 | -0.09613 | 108.8928 | 1.6068 | 0.67291 | 1.7166 | 0.78278 | 0.71411 | 122.0581 | 109.0027 | 122.1039 | 122.1222 | 122.1359 | 121.994 | 122.0261 | -122.2183 | -122.2 | 121.9299 | 121.994 | 119.4672 | 49.7543
2203.4531 | 122.2549 | -121.9757 | 0.12817 | -0.013657 | -0.0005063 | 0.054976 | 0.053053 | -0.0051226 | -0.010256 | -0.0046847 | -0.011261 | 0.0040802 | 0.13239 | 0.063773 | -0.013296 | 0.024353 | 0.0079746 | -2.5955 | -0.013733 | -122.049 | 0.018311 | -121.312 | -122.0261 | -122.0261 | -72.3587 | 0.032043 | -122.0581 | 0.054932 | -18.3838 | -121.2204 | -120.2957 | -0.073242 | -0.14191 | -0.10986 | 0.66376 | -0.050354 | -0.050354 | 0.022888 | 0.022888 | -0.082397 | -0.096131 | -0.073242 | 103.5919 | 1.68 | 0.75531 | 1.7624 | 0.83771 | 0.737 | 122.0673 | 103.6743 | 122.113 | 122.0352 | 122.0901 | 121.962 | 122.0078 | -122.1771 | -122.1863 | 121.994 | 122.0306 | 119.3802 | 49.617
2205.125 | 122.2275 | -121.9666 | 0.15564 | -0.013657 | -0.0013607 | 0.054549 | 0.056044 | 0.004704 | -0.011111 | -0.0042575 | -0.0082093 | 0.0049346 | 0.13581 | 0.068473 | -0.014791 | 0.024139 | 0.0062656 | -2.5131 | 0.004578 | -122.081 | 0.018311 | -121.312 | -122.0535 | -122.0581 | -72.496 | 0.068665 | -122.081 | 0.073242 | -14.7079 | -121.2387 | -120.2866 | -0.11444 | -0.15106 | -0.13733 | 0.6546 | -0.091552 | -0.086975 | 0.022889 | 0.027466 | -0.11444 | -0.086975 | -0.082398 | 107.2586 | 1.68 | 0.72785 | 1.7944 | 0.84229 | 0.76904 | 122.0993 | 107.373 | 122.1542 | 122.0856 | 122.1497 | 121.9711 | 122.0352 | -122.2366 | -122.2366 | 121.9849 | 122.0398 | 119.4534 | 49.4705
2206.875 | 122.1863 | -122.0169 | 0.13275 | -0.013657 | -0.0011471 | 0.054549 | 0.052199 | 0.00021799 | -0.0089743 | -0.0040439 | -0.0082093 | 0.0057892 | 0.13068 | 0.067618 | -0.015432 | 0.024994 | 0.005411 | -2.5726 | 0.018311 | -122.1085 | -0.054932 | -121.3806 | -122.1039 | -122.113 | -73.1781 | 0.068665 | -122.081 | -0.018311 | -25.0946 | -121.2753 | -120.314 | -0.091552 | -0.11444 | -0.18768 | 0.63629 | -0.09613 | -0.086975 | -0.004578 | 0.004577 | -0.064087 | -0.064086 | -0.15106 | 96.9223 | 1.7029 | 0.74158 | 1.767 | 0.80566 | 0.72784 | 122.0535 | 96.9864 | 122.0627 | 122.1268 | 122.1497 | 122.0352 | 122.0856 | -122.2412 | -122.2137 | 121.962 | 121.9986 | 119.4443 | 48.8388
2208.625 | 122.3328 | -121.9437 | 0.1236 | -0.021286 | -0.0022153 | 0.053694 | 0.050276 | -0.002132 | -0.0083335 | -0.0046847 | -0.0082093 | 0.0034392 | 0.13111 | 0.056723 | -0.015219 | 0.023285 | 0.0028476 | -2.5543 | -0.022888 | -122.0627 | 0.086975 | -121.2112 | -121.9574 | -121.962 | -72.9996 | 0.004578 | -122.0306 | 0.1236 | -23.1537 | -121.106 | -120.1355 | -0.11902 | -0.14648 | -0.036621 | 0.73242 | -0.01831 | -0.013732 | 0.10071 | 0.10529 | -0.086975 | -0.11902 | 0 | 98.79 | 1.8082 | 0.83771 | 1.8951 | 0.92468 | 0.85144 | 122.1497 | 98.877 | 122.1542 | 122.0398 | 122.0352 | 121.9208 | 121.9482 | -122.1863 | -122.1542 | 122.0306 | 122.0673 | 119.3893 | 48.9441
2210.3281 | 122.2549 | -121.9803 | 0.13733 | -0.013657 | -0.0013607 | 0.055403 | 0.050063 | 0.0014996 | -0.0074789 | -0.0021213 | -0.0082093 | 0.0032256 | 0.13474 | 0.0642 | -0.013937 | 0.026062 | 0.0051974 | -2.536 | -0.013733 | -122.0673 | 0.07782 | -121.2341 | -121.9711 | -121.9986 | -72.7478 | 0.054932 | -122.0535 | 0.07782 | -21.1853 | -121.1563 | -120.1447 | -0.086975 | -0.15106 | -0.059509 | 0.74616 | -0.01831 | 0.009156 | 0.068665 | 0.096131 | -0.073242 | -0.082397 | -0.059509 | 100.795 | 1.8356 | 0.82398 | 1.9089 | 0.89722 | 0.83313 | 122.1451 | 100.8682 | 122.1313 | 122.0535 | 122.1085 | 121.9666 | 122.0352 | -122.2046 | -122.1909 | 122.0581 | 122.0581 | 119.4443 | 49.2325
2212.0781 | 122.3053 | -121.9391 | 0.12817 | -0.0060272 | 0.0016299 | 0.055403 | 0.053694 | -0.0036274 | -0.0070517 | -0.0031895 | -0.0051575 | 0.0045074 | 0.1294 | 0.068045 | -0.014791 | 0.024567 | 0.0047702 | -2.6184 | 0 | -122.0535 | 0.059509 | -121.2662 | -122.0032 | -121.9711 | -72.2946 | 0.032043 | -122.049 | 0.11444 | -20.668 | -121.1151 | -120.0623 | -0.11444 | -0.12817 | -0.068665 | 0.67291 | -0.032043 | -0.064087 | 0.082398 | 0.050354 | -0.10986 | -0.096131 | -0.013733 | 101.2711 | 1.8768 | 0.82398 | 1.9867 | 0.93384 | 0.78735 | 122.113 | 101.3809 | 122.1634 | 122.0535 | 122.081 | 121.9391 | 121.9711 | -122.1817 | -122.1771 | 121.9986 | 122.0535 | 119.3207 | 49.6445
2213.8438 | 122.3007 | -121.9666 | 0.11902 | -0.0060272 | -0.0043515 | 0.056471 | 0.054121 | -0.004909 | -0.0091879 | -0.0036167 | -0.0021057 | 0.0042938 | 0.12962 | 0.063773 | -0.013723 | 0.022217 | 0.0045566 | -2.6688 | -0.013733 | -122.0764 | 0.073242 | -121.2662 | -121.9711 | -121.9757 | -71.8643 | 0.032043 | -122.0535 | 0.11902 | -22.5266 | -121.1151 | -120.0394 | -0.10986 | -0.13275 | -0.045777 | 0.70038 | -0.009155 | -0.004577 | 0.10071 | 0.10529 | -0.086975 | -0.086976 | 0 | 99.44 | 1.9272 | 0.85144 | 2.0142 | 0.93842 | 0.81024 | 122.1497 | 99.527 | 122.1725 | 122.0627 | 122.0856 | 121.9528 | 121.9986 | -122.1954 | -122.1725 | 122.0398 | 122.0856 | 119.2978 | 50.1022
2215.5938 | 122.2916 | -121.9528 | 0.1236 | -0.0060272 | 0.0003483 | 0.056258 | 0.055403 | 0.0019268 | -0.0091879 | -0.0031895 | -0.0082093 | 0.00643 | 0.13432 | 0.067405 | -0.015432 | 0.025421 | 0.006052 | -2.7603 | 0.018311 | -122.081 | 0.013733 | -121.312 | -122.0581 | -122.049 | -71.4661 | 0.068665 | -122.0169 | 0.1236 | -18.3243 | -121.17 | -120.0027 | -0.12817 | -0.10528 | -0.10986 | 0.64087 | -0.09613 | -0.10528 | 0.032044 | 0.022889 | -0.064087 | -0.054931 | 0 | 103.6285 | 1.9501 | 0.78278 | 2.0142 | 0.84686 | 0.76904 | 122.0947 | 103.6926 | 122.1405 | 122.0993 | 122.0856 | 121.9711 | 122.0215 | -122.2046 | -122.1405 | 121.9666 | 122.0764 | 119.1925 | 50.4868
2217.2812 | 122.2824 | -121.9666 | 0.09613 | -0.0060272 | 0.0018435 | 0.058821 | 0.055403 | -0.0025592 | -0.0085471 | -0.0063937 | -0.0082093 | 0.0040802 | 0.12833 | 0.067405 | -0.014364 | 0.02478 | 0.005411 | -2.7054 | -0.022888 | -122.0306 | 0.10071 | -121.2341 | -122.0032 | -121.9849 | -72.0108 | 0.013733 | -122.0306 | 0.13275 | -27.6398 | -121.1243 | -119.9524 | -0.064087 | -0.11902 | 0.004578 | 0.73242 | -0.01831 | -0.036621 | 0.045777 | 0.027466 | -0.064087 | -0.082397 | 0.036621 | 94.3268 | 2.0142 | 0.84229 | 2.0782 | 0.90637 | 0.79651 | 122.1313 | 94.3909 | 122.1634 | 122.0078 | 122.0444 | 121.9437 | 121.9803 | -122.1268 | -122.1268 | 122.0673 | 122.0993 | 119.2612 | 49.9558
2219.0312 | 122.2046 | -121.9666 | 0.13733 | -0.013657 | 0.0031253 | 0.053908 | 0.05583 | -0.002132 | -0.0096151 | -0.0021213 | -0.011261 | 0.0051482 | 0.12727 | 0.068686 | -0.013937 | 0.026062 | 0.003702 | -2.7054 | 0.009155 | -122.0993 | 0 | -121.3531 | -122.0444 | -122.0764 | -72.2992 | 0.064087 | -122.0718 | 0.041199 | -28.2303 | -121.1975 | -119.9936 | -0.13275 | -0.12817 | -0.13733 | 0.6134 | -0.10986 | -0.07782 | 0.022888 | 0.054931 | -0.10528 | -0.073242 | -0.09613 | 93.7363 | 1.973 | 0.76904 | 2.0782 | 0.87433 | 0.74616 | 122.0993 | 93.8416 | 122.113 | 122.1085 | 122.1359 | 121.9757 | 122.0306 | -122.2366 | -122.2092 | 121.9666 | 122.0078 | 119.2612 | 49.6674
2220.7969 | 122.3053 | -121.9482 | 0.10529 | -0.013657 | -0.0037107 | 0.053694 | 0.051558 | -0.0036274 | -0.010256 | -0.0021213 | -0.0021057 | 0.0032256 | 0.12833 | 0.065055 | -0.013296 | 0.023926 | 0.011393 | -2.7878 | 0.004578 | -122.0947 | 0.036621 | -121.2936 | -122.0123 | -122.0078 | -72.4045 | 0.064087 | -122.0581 | 0.10529 | -24.7192 | -121.0876 | -119.838 | -0.14649 | -0.10071 | -0.068665 | 0.6546 | -0.059509 | -0.064087 | 0.086976 | 0.082398 | -0.10986 | -0.041199 | 0 | 97.229 | 2.1103 | 0.8606 | 2.2202 | 0.97046 | 0.80109 | 122.1313 | 97.3389 | 122.1634 | 122.0993 | 122.1222 | 121.9528 | 122.0123 | -122.2 | -122.1634 | 121.9849 | 122.0535 | 119.1605 | 49.5438
2222.5 | 122.1909 | -122.0535 | 0.14648 | -0.021286 | -0.0026425 | 0.054335 | 0.053053 | -0.00020941 | -0.0083335 | -0.0048985 | -0.0082093 | 0.0038666 | 0.13026 | 0.061423 | -0.015859 | 0.025208 | 0.0086154 | -2.7054 | -0.009155 | -122.0718 | 0.041199 | -121.2891 | -122.0123 | -122.0352 | -72.3541 | 0.068665 | -122.0718 | 0.009155 | -21.8353 | -121.17 | -119.8471 | -0.01831 | -0.15564 | -0.10529 | 0.76447 | 0.018311 | 0.041199 | 0.036621 | 0.059509 | -0.01831 | -0.077819 | -0.13733 | 100.2182 | 2.2064 | 0.88348 | 2.2247 | 0.90179 | 0.78278 | 122.113 | 100.2365 | 122.081 | 122.0627 | 122.1405 | 122.0444 | 122.1222 | -122.2183 | -122.2183 | 122.0947 | 122.0627 | 119.3481 | 49.6994
2224.25 | 122.2961 | -121.9574 | 0.11444 | -0.021286 | 0.0009891 | 0.05583 | 0.053908 | 0.0021406 | -0.0072653 | -0.0016941 | -0.0021057 | 0.004721 | 0.13175 | 0.065268 | -0.013937 | 0.025848 | 0.0096836 | -2.8381 | -0.004578 | -122.0444 | 0.064087 | -121.2433 | -122.0078 | -122.0032 | -72.1527 | 0.032043 | -122.0352 | 0.14648 | -20.6451 | -121.0785 | -119.6274 | -0.086976 | -0.11902 | -0.050354 | 0.71411 | -0.045777 | -0.050354 | 0.041199 | 0.036622 | -0.07782 | -0.082398 | 0.032043 | 101.3123 | 2.33 | 0.87891 | 2.4078 | 0.95673 | 0.80109 | 122.1085 | 101.3901 | 122.1817 | 122.0398 | 122.0673 | 121.9528 | 121.9894 | -122.1588 | -122.1497 | 122.0215 | 122.1039 | 119.1193 | 49.8047
2226 | 122.2046 | -121.9849 | 0.14648 | -0.013657 | 0.0005619 | 0.054335 | 0.055403 | -0.0010638 | -0.0076925 | -0.0031895 | -0.0051575 | 0.00643 | 0.13346 | 0.068259 | -0.015646 | 0.026489 | 0.00712 | -2.9022 | 0.041199 | -122.0993 | -0.041199 | -121.3898 | -122.1359 | -122.1222 | -72.1893 | 0.068665 | -122.0673 | 0.018311 | -20.6451 | -121.1792 | -119.6457 | -0.11444 | -0.10529 | -0.18768 | 0.59509 | -0.13733 | -0.15106 | -0.022888 | -0.036621 | -0.082398 | -0.077819 | -0.12817 | 101.3397 | 2.3392 | 0.80566 | 2.4216 | 0.88806 | 0.70953 | 122.0581 | 101.4221 | 122.0856 | 122.1405 | 122.1359 | 122.0261 | 122.0535 | -122.2458 | -122.2137 | 121.9437 | 122.0032 | 119.0826 | 49.7955
2227.6875 | 122.2 | -121.9986 | 0.14648 | -0.021286 | -0.0005063 | 0.057967 | 0.055189 | 0.0010724 | -0.0079061 | -0.0048985 | -0.0082093 | 0.0051482 | 0.12983 | 0.067405 | -0.01415 | 0.025208 | 0.00947 | -2.9297 | 0.022888 | -122.0764 | -0.041199 | -121.3806 | -122.1268 | -122.113 | -72.6471 | 0.086975 | -122.081 | 0.022888 | -23.4283 | -121.1472 | -119.5679 | -0.07782 | -0.1236 | -0.18768 | 0.61798 | -0.11444 | -0.12817 | -0.036621 | -0.050354 | -0.082398 | -0.059509 | -0.1236 | 98.5703 | 2.4307 | 0.85144 | 2.5131 | 0.93384 | 0.6958 | 122.0352 | 98.6526 | 122.1039 | 122.0993 | 122.168 | 122.0215 | 122.0856 | -122.2229 | -122.2275 | 121.9574 | 122.0215 | 119.0689 | 49.3515
2229.4688 | 122.2687 | -121.9711 | 0.12817 | -0.0060272 | -0.0002927 | 0.057112 | 0.052412 | 4.192e-06 | -0.0096151 | -0.0010531 | -0.0051575 | 0.0017304 | 0.13004 | 0.068686 | -0.013723 | 0.026703 | 0.010965 | -2.7878 | -0.009155 | -122.0718 | 0.073242 | -121.2204 | -121.962 | -121.994 | -72.4457 | 0.059509 | -122.0352 | 0.07782 | -25.676 | -121.019 | -119.4031 | -0.10071 | -0.13733 | -0.054932 | 0.75073 | -0.022889 | 0.009155 | 0.077819 | 0.10986 | -0.064087 | -0.068665 | -0.050354 | 96.2952 | 2.5681 | 0.95215 | 2.6321 | 1.0162 | 0.85144 | 122.1451 | 96.3593 | 122.113 | 122.0627 | 122.0947 | 121.962 | 122.0306 | -122.2 | -122.1634 | 122.0444 | 122.049 | 119.1833 | 49.5255
2231.2188 | 122.2 | -121.994 | 0.18768 | -0.0060272 | -0.0002927 | 0.053267 | 0.053053 | -0.001491 | -0.011538 | -0.0066073 | -0.0051575 | 0.00643 | 0.1309 | 0.066336 | -0.015646 | 0.027557 | 0.035532 | -2.8839 | 0.045776 | -122.1039 | -0.032043 | -121.3669 | -122.0718 | -122.0901 | -72.1664 | 0.10071 | -122.0627 | 0.004578 | -24.0326 | -121.0968 | -105.4733 | -0.10986 | -0.14191 | -0.21973 | 0.62714 | -0.09613 | -0.077819 | 0.013733 | 0.032044 | -0.068664 | -0.086975 | -0.1831 | 97.9614 | 16.5207 | 0.89722 | 16.5894 | 0.96588 | 0.737 | 122.0718 | 98.0301 | 122.0673 | 122.1497 | 122.1634 | 122.0398 | 122.0947 | -122.2916 | -122.2504 | 121.962 | 121.9986 | 119.1101 | 49.8276
2232.9062 | 122.2183 | -121.4584 | 0.55389 | -0.021286 | -0.0015743 | 0.056898 | 0.050063 | -0.0029864 | -0.0094015 | -0.0040439 | -0.0051575 | 0.0034392 | 0.12321 | 0.05651 | -0.0165 | 0.023926 | 0.73878 | -2.9297 | 0.42114 | -121.5958 | 0.44861 | -120.8038 | -121.5317 | -121.5317 | -68.9301 | 0.4715 | -121.4996 | 0.49439 | -34.0256 | -120.3735 | -9.6771 | -0.13733 | -0.13275 | -0.10529 | 0.6546 | -0.073242 | -0.073242 | 0.064087 | 0.064087 | -0.041199 | -0.082397 | -0.059509 | 87.4329 | 111.7813 | 1.0849 | 111.8225 | 1.1261 | 0.79193 | 122.0444 | 87.4741 | 121.994 | 122.0169 | 121.9711 | 121.8796 | 121.9299 | -122.1497 | -122.0535 | 121.907 | 121.9528 | 118.5287 | 52.5284
2234.6562 | 122.2321 | -121.4127 | 0.53558 | -0.0060272 | -0.0015743 | 0.055617 | 0.051985 | -0.00020941 | -0.0085471 | -0.0034031 | -0.0051575 | 0.00643 | 0.12577 | 0.057151 | -0.017996 | 0.022644 | 0.73664 | -2.8748 | 0.41199 | -121.5591 | 0.50812 | -120.7031 | -121.4584 | -121.4493 | -68.2892 | 0.45776 | -121.4584 | 0.54474 | -30.8533 | -120.2866 | -8.7616 | -0.14648 | -0.1236 | -0.027465 | 0.70953 | -0.036621 | -0.045776 | 0.10986 | 0.10071 | -0.045776 | -0.077819 | 0.009156 | 90.5594 | 112.6511 | 1.1261 | 112.6968 | 1.1719 | 0.85602 | 122.0673 | 90.6052 | 122.0032 | 121.9711 | 121.9162 | 121.8246 | 121.8704 | -122.0947 | -121.994 | 121.9208 | 121.9574 | 118.5379 | 53.1235
2236.4062 | 122.081 | -121.4584 | 0.55847 | -0.021286 | 0.0031253 | 0.056258 | 0.056258 | 0.0025678 | -0.0074789 | -0.0025485 | -0.0082093 | 0.0092072 | 0.12556 | 0.05886 | -0.018423 | 0.025208 | 0.73985 | -2.9205 | 0.41657 | -121.5591 | 0.44403 | -120.8084 | -121.5363 | -121.5683 | -68.1793 | 0.48065 | -121.4996 | 0.45319 | -29.7363 | -120.4193 | -8.4732 | -0.10071 | -0.14191 | -0.11444 | 0.65002 | -0.10986 | -0.07782 | -0.009155 | 0.022888 | -0.041199 | -0.07782 | -0.10529 | 91.7221 | 112.9852 | 1.0391 | 113.0264 | 1.0803 | 0.75073 | 122.0032 | 91.7633 | 121.9528 | 121.9757 | 121.9803 | 121.875 | 121.9391 | -122.1176 | -122.0581 | 121.9025 | 121.9116 | 118.5379 | 53.2791
2238.1719 | 122.0856 | -121.4676 | 0.5722 | -0.021286 | -0.0002927 | 0.056258 | 0.054976 | -0.0027728 | -0.0094015 | -0.0053257 | -0.0051575 | 0.0083526 | 0.13047 | 0.05886 | -0.017996 | 0.026489 | 0.73622 | -2.9343 | 0.43488 | -121.5637 | 0.39368 | -120.813 | -121.5408 | -121.5454 | -67.9871 | 0.48065 | -121.4767 | 0.44403 | -28.8025 | -120.3644 | -8.1161 | -0.096131 | -0.13733 | -0.17853 | 0.6546 | -0.07782 | -0.073243 | 0.018311 | 0.022888 | -0.009156 | -0.091553 | -0.12817 | 92.6651 | 113.3514 | 1.1032 | 113.3606 | 1.1124 | 0.75073 | 121.9574 | 92.6743 | 121.9208 | 121.9986 | 121.9574 | 121.9025 | 121.9482 | -122.1359 | -122.049 | 121.8613 | 121.9116 | 118.5333 | 53.4805
2239.8594 | 122.1817 | -121.4401 | 0.5127 | 0.0016023 | 0.0012027 | 0.057539 | 0.054121 | 0.0044904 | -0.0070517 | -0.0044711 | -0.0051575 | 0.0038666 | 0.12876 | 0.059501 | -0.017568 | 0.025208 | 0.72853 | -3.0121 | 0.42114 | -121.5088 | 0.50354 | -120.7077 | -121.4584 | -121.463 | -67.9871 | 0.44861 | -121.4493 | 0.54474 | -29.0314 | -120.2728 | -7.9605 | -0.068664 | -0.091552 | -0.009155 | 0.73242 | -0.022888 | -0.01831 | 0.045776 | 0.050354 | -0.009155 | -0.064087 | 0.032044 | 92.4088 | 113.4796 | 1.1673 | 113.4888 | 1.1765 | 0.80109 | 122.0123 | 92.4179 | 121.994 | 121.9299 | 121.8979 | 121.8613 | 121.8887 | -122.0215 | -121.962 | 121.9437 | 121.9849 | 118.428 | 53.4531
2241.6094 | 122.0718 | -121.4676 | 0.56305 | -0.013657 | -7.9104e-05 | 0.055189 | 0.051985 | -0.0010638 | -0.0083335 | -0.0036167 | -0.0082093 | 0.0079254 | 0.12791 | 0.060355 | -0.017782 | 0.026062 | 0.73152 | -2.9526 | 0.41199 | -121.5454 | 0.43488 | -120.7535 | -121.4767 | -121.4951 | -67.9001 | 0.45319 | -121.4859 | 0.43488 | -29.3884 | -120.3323 | -7.6767 | -0.07782 | -0.15106 | -0.12817 | 0.71411 | -0.027466 | -0.009156 | 0.050354 | 0.068664 | -0.018311 | -0.10986 | -0.12817 | 92.0792 | 113.7909 | 1.1353 | 113.8092 | 1.1536 | 0.79193 | 121.9803 | 92.0975 | 121.9208 | 121.9574 | 121.9391 | 121.8796 | 121.9208 | -122.1085 | -122.049 | 121.9025 | 121.9025 | 118.515 | 53.5675
2243.3594 | 122.0901 | -121.1105 | 0.54474 | -0.1281 | -0.0011471 | 0.053908 | 0.051772 | -0.0019184 | -0.0083335 | -0.0027621 | -0.0082093 | 0.0051482 | 0.13047 | 0.048819 | -0.014578 | 0.024139 | 0.71464 | -2.9892 | 0.11902 | -96.9635 | 0.2655 | -120.4422 | -121.138 | -121.1197 | -67.6117 | 0.13275 | -100.0076 | 0.36621 | -28.6697 | -119.9753 | -9.8557 | 24.147 | -0.42572 | -0.27924 | 0.66833 | -0.009155 | -0.027465 | -24.1562 | -24.1745 | 21.1029 | -0.41199 | -0.17853 | 92.4408 | 111.2549 | 1.1353 | 90.152 | -19.9677 | -23.4787 | 97.229 | 71.3379 | 100.3738 | 97.0825 | 100.1404 | 121.2296 | 121.2433 | -97.5082 | -100.5524 | 121.376 | 121.4767 | 118.1213 | 53.4988
2245.1094 | 122.1863 | -121.4172 | 0.50354 | -0.39513 | -0.0020017 | 0.055403 | 0.050276 | -0.0032 | -0.0087607 | -0.0042575 | -0.0021057 | 0.0049346 | 0.12876 | 0.055228 | -0.016073 | 0.025421 | 0.70716 | -3.0029 | 0.38452 | -121.637 | 0.4715 | -120.488 | -121.2799 | -121.2341 | -68.074 | 0.40741 | -121.2296 | 0.48523 | -28.2761 | -119.9615 | -10.6247 | -0.21973 | -0.11902 | -0.032043 | 0.92926 | 0.1831 | 0.13733 | 0.40283 | 0.35706 | 0.18768 | -0.09613 | -0.018311 | 93.1412 | 110.7925 | 1.4557 | 110.6049 | 1.268 | 1.149 | 122.1085 | 92.9535 | 121.7148 | 122.0215 | 121.637 | 121.8018 | 121.8246 | -122.1405 | -121.7331 | 121.8887 | 121.9025 | 118.4143 | 53.3432
2246.7969 | 121.8475 | -121.1563 | 0.54474 | -0.1281 | -0.0028561 | 0.053267 | 0.05284 | -0.0053362 | -0.010256 | -0.0029759 | -0.0021057 | 0.005362 | 0.12983 | 0.060569 | -0.018209 | 0.024353 | 0.70802 | -3.0853 | 0.40283 | -108.8196 | 0.33417 | -120.4651 | -121.2204 | -121.1838 | -67.7353 | 0.48065 | -118.3594 | 0.37994 | -28.0014 | -120.0851 | -9.5993 | 12.3367 | -0.14191 | -0.21057 | 0.69122 | -0.027466 | -0.064087 | -12.3642 | -12.4008 | 2.7969 | -0.064087 | -0.16479 | 93.1549 | 111.557 | 1.0712 | 108.7601 | -1.7258 | -11.6455 | 109.1537 | 90.358 | 118.7393 | 109.2224 | 118.84 | 121.5591 | 121.637 | -109.3643 | -118.9041 | 121.4905 | 121.5363 | 118.071 | 53.421
2248.5469 | 121.4447 | -120.8267 | 0.54932 | -0.0060272 | 0.027905 | 0.1103 | 0.059035 | 0.046788 | 0.057676 | -0.010239 | -0.0021057 | -0.0087372 | 0.12257 | 0.055228 | -0.021841 | 0.016022 | 0.69605 | -3.2547 | 0.4303 | -121.4218 | 0.37079 | -121.1334 | -121.4081 | -121.7377 | -67.1677 | 0.45776 | -117.8192 | 0.39368 | -27.5528 | -115.0772 | -9.4254 | -0.59509 | -0.11902 | -0.17853 | -0.3067 | -0.91095 | -0.58136 | -0.31586 | 0.013733 | 3.0075 | -0.091552 | -0.15564 | 93.2739 | 111.4014 | 5.7495 | 108.3939 | 2.742 | 0.28839 | 121.7926 | 90.2664 | 118.2129 | 121.8521 | 118.277 | 121.257 | 121.2845 | -121.9711 | -118.3685 | 121.1975 | 121.2204 | 117.572 | 53.6591
2250.2344 | 121.8292 | -121.2616 | 0.52643 | -0.55534 | -0.010974 | 0.046645 | 0.053267 | 0.00021799 | -0.012392 | -0.0048985 | -0.0021057 | 0.0074982 | 0.13367 | 0.055442 | -0.015646 | 0.024994 | 0.69947 | -3.2364 | 0.42572 | -121.0648 | 0.33875 | -120.4697 | -121.2753 | -121.2204 | -67.0258 | 0.46234 | -120.6802 | 0.42572 | -27.6718 | -119.87 | -9.1461 | 0.19684 | -0.10071 | -0.18768 | 0.79193 | 0.041199 | -0.013733 | -0.15564 | -0.21057 | 0.58136 | -0.064087 | -0.10071 | 93.5898 | 112.1155 | 1.3916 | 111.5341 | 0.81024 | 0.59509 | 121.4035 | 93.0084 | 121.106 | 121.4905 | 121.1426 | 121.6873 | 121.7239 | -121.5912 | -121.2067 | 121.6003 | 121.6873 | 118.0252 | 54.2358
2252 | 122.168 | -121.4264 | 0.49439 | -0.28831 | 0.0003483 | 0.05583 | 0.051985 | 0.0023542 | -0.0083335 | -0.0040439 | -0.0051575 | 0.004721 | 0.13132 | 0.058646 | -0.017141 | 0.026703 | 0.69947 | -3.1769 | 0.37994 | -121.2479 | 0.48065 | -120.607 | -121.4035 | -121.312 | -66.7145 | 0.42114 | -120.9549 | 0.5127 | -28.006 | -120.0027 | -9.1003 | 0.17853 | -0.11444 | -0.013733 | 0.8194 | 0.11444 | 0.022889 | -0.064087 | -0.15564 | 0.4715 | -0.073242 | 0.01831 | 93.4204 | 112.3261 | 1.4236 | 111.8546 | 0.95215 | 0.64087 | 121.7285 | 92.9489 | 121.4676 | 121.6278 | 121.376 | 121.8063 | 121.8475 | -121.7422 | -121.4493 | 121.907 | 121.9391 | 118.2495 | 54.7119
2253.7031 | 122.1268 | -121.4493 | 0.52643 | -0.5172 | -0.0013607 | 0.055189 | 0.051985 | 0.0014996 | -0.0096151 | -0.0048985 | 0.0009461 | 0.0055756 | 0.13068 | 0.059501 | -0.019491 | 0.025208 | 0.68324 | -3.1174 | 0.3479 | -121.0327 | 0.45319 | -120.726 | -121.4539 | -121.4035 | -66.3528 | 0.42572 | -120.9274 | 0.45776 | -28.7979 | -119.9615 | -11.9614 | 0.41657 | -0.17853 | -0.073242 | 0.72327 | 0.045777 | -0.004577 | -0.37079 | -0.42114 | 0.52185 | -0.10071 | -0.068664 | 92.6514 | 109.4879 | 1.4877 | 108.9661 | 0.96588 | 0.3067 | 121.4859 | 92.1295 | 121.3852 | 121.3806 | 121.3531 | 121.7972 | 121.875 | -121.5591 | -121.4539 | 121.9025 | 121.907 | 118.3319 | 55.0964
2255.4688 | 122.168 | -121.431 | 0.46692 | -0.56297 | 0.0016299 | 0.055617 | 0.054335 | -0.00085021 | -0.0083335 | -0.0034031 | -0.0021057 | 0.0079254 | 0.13175 | 0.058646 | -0.016714 | 0.026489 | 0.65568 | -3.2822 | 0.36163 | -121.3074 | 0.41199 | -120.6985 | -121.4355 | -121.3531 | -66.3071 | 0.39825 | -121.1838 | 0.48523 | -29.8782 | -119.989 | -15.77 | 0.1236 | -0.10529 | -0.054932 | 0.73242 | 0.07782 | -0.004578 | -0.045776 | -0.12817 | 0.24719 | -0.068665 | 0.01831 | 91.5527 | 105.661 | 1.442 | 105.4138 | 1.1948 | 0.60883 | 121.7194 | 91.3055 | 121.669 | 121.669 | 121.582 | 121.7926 | 121.8292 | -121.7743 | -121.6507 | 121.843 | 121.9162 | 118.1488 | 55.1239
2257.2188 | 122.1039 | -121.4401 | 0.50812 | -0.24254 | -0.0022153 | 0.055403 | 0.052199 | -0.00042301 | -0.0066245 | -0.0025485 | 0.0009461 | 0.004721 | 0.13261 | 0.052665 | -0.017355 | 0.027344 | 0.69563 | -3.3096 | 0.37079 | -121.5134 | 0.43488 | -120.7443 | -121.4996 | -121.4767 | -65.863 | 0.42114 | -121.3669 | 0.45776 | -31.0867 | -120.0714 | -8.9813 | -0.073242 | -0.13733 | -0.073243 | 0.6958 | -0.036621 | -0.059509 | 0.036621 | 0.013733 | 0.073243 | -0.086975 | -0.050354 | 90.3534 | 112.4588 | 1.3687 | 112.3856 | 1.2955 | 0.76904 | 121.9482 | 90.2802 | 121.8246 | 121.8842 | 121.788 | 121.8109 | 121.8613 | -122.0215 | -121.875 | 121.875 | 121.8979 | 118.1305 | 55.5771
2258.9844 | 122.113 | -121.4172 | 0.50354 | -0.62401 | -0.0054197 | 0.054762 | 0.054549 | 0.00085879 | -0.0076925 | -0.0025485 | -0.0021057 | 0.0083526 | 0.13132 | 0.06185 | -0.017141 | 0.026062 | 0.69349 | -3.3646 | 0.41657 | -121.5317 | 0.37994 | -120.7901 | -121.4859 | -121.4035 | -65.9775 | 0.4303 | -121.3074 | 0.45776 | -32.6706 | -119.957 | -8.1573 | -0.11444 | -0.086975 | -0.1236 | 0.62714 | 0.013733 | -0.068665 | 0.12817 | 0.045776 | 0.10986 | -0.073242 | -0.045776 | 88.7466 | 113.2599 | 1.4603 | 113.15 | 1.3504 | 0.74158 | 121.9116 | 88.6368 | 121.7651 | 121.9482 | 121.7377 | 121.8338 | 121.8475 | -122.0352 | -121.8109 | 121.7972 | 121.875 | 118.0527 | 55.4398
2260.6719 | 122.0993 | -121.3852 | 0.49439 | -0.0060272 | -0.0002927 | 0.054762 | 0.05284 | 0.001286 | -0.0061971 | -0.0042575 | -0.0051575 | 0.0034392 | 0.13111 | 0.058646 | -0.015432 | 0.027557 | 0.68965 | -3.36 | 0.36621 | -121.5088 | 0.41657 | -120.7443 | -121.4767 | -121.4813 | -65.7211 | 0.43488 | -121.4676 | 0.44861 | -33.5175 | -120.0211 | -8.6563 | -0.1236 | -0.12817 | -0.07782 | 0.64087 | -0.09613 | -0.091553 | 0.027466 | 0.032043 | -0.082397 | -0.05951 | -0.045777 | 87.8677 | 112.7289 | 1.3641 | 112.8113 | 1.4465 | 0.76446 | 121.9254 | 87.9501 | 121.9162 | 121.875 | 121.9025 | 121.7514 | 121.8201 | -122.0032 | -121.962 | 121.8018 | 121.8338 | 118.0252 | 55.6641
2262.3594 | 122.1542 | -121.4172 | 0.49896 | -0.013657 | -0.0009335 | 0.051771 | 0.05348 | -0.0027728 | -0.0083335 | -0.0034031 | -0.0051575 | 0.004721 | 0.12897 | 0.060996 | -0.018209 | 0.025635 | 0.6873 | -3.3005 | 0.37079 | -121.5042 | 0.47607 | -120.6711 | -121.4081 | -121.431 | -65.8218 | 0.41199 | -121.4493 | 0.48981 | -38.4018 | -119.9432 | -8.2718 | -0.086975 | -0.12817 | -0.022888 | 0.74615 | -0.013733 | 0.009155 | 0.073242 | 0.09613 | -0.032044 | -0.086975 | -0.009155 | 83.0154 | 113.1454 | 1.474 | 113.1775 | 1.506 | 0.83313 | 121.9803 | 83.0475 | 121.9391 | 121.875 | 121.8613 | 121.788 | 121.8292 | -122.0032 | -121.9482 | 121.8933 | 121.907 | 118.1168 | 55.5954
2264.1094 | 122.113 | -121.3943 | 0.5127 | -0.059433 | -0.0037107 | 0.053267 | 0.051985 | -0.0040546 | -0.0074789 | -0.0031895 | -0.0021057 | 0.0045074 | 0.13538 | 0.062705 | -0.016714 | 0.025208 | 0.68495 | -3.392 | 0.37537 | -121.5179 | 0.41199 | -120.7581 | -121.4767 | -121.4722 | -65.4739 | 0.42572 | -121.4355 | 0.45319 | -30.368 | -119.9432 | -8.1985 | -0.1236 | -0.13733 | -0.10071 | 0.63629 | -0.07782 | -0.082398 | 0.045776 | 0.041198 | -0.041199 | -0.086975 | -0.059509 | 91.0263 | 113.1958 | 1.4511 | 113.237 | 1.4923 | 0.75989 | 121.9299 | 91.0675 | 121.8887 | 121.8933 | 121.8613 | 121.7697 | 121.8201 | -122.0306 | -121.9482 | 121.8063 | 121.8475 | 118.0023 | 55.9204
2265.7969 | 121.8887 | -121.4035 | 0.52185 | -0.25017 | -0.0028561 | 0.052626 | 0.053267 | -0.0019184 | -0.0091879 | -0.0014805 | -0.0021057 | 0.0057892 | 0.13538 | 0.062705 | -0.016287 | 0.026276 | 0.68516 | -3.3691 | 0.40283 | -121.1792 | 0.35706 | -120.8038 | -121.5179 | -121.5363 | -65.7257 | 0.45319 | -121.4539 | 0.35706 | -30.098 | -120.0165 | -7.9697 | 0.2243 | -0.11902 | -0.16479 | 0.59967 | -0.13275 | -0.11444 | -0.35706 | -0.33875 | -0.050354 | -0.068665 | -0.16479 | 91.3055 | 113.4338 | 1.387 | 113.4842 | 1.4374 | 0.37537 | 121.5363 | 91.3559 | 121.8109 | 121.582 | 121.907 | 121.8063 | 121.8567 | -121.701 | -121.9757 | 121.7606 | 121.7606 | 118.0344 | 55.6778
2267.5469 | 122.1313 | -121.3898 | 0.48065 | -0.11284 | -0.0015743 | 0.053694 | 0.05049 | -0.004909 | -0.0085471 | -0.0063937 | -0.0051575 | 0.0038666 | 0.13346 | 0.059501 | -0.015432 | 0.026489 | 0.68516 | -3.3371 | 0.37994 | -121.4539 | 0.48981 | -120.6345 | -121.3898 | -121.3989 | -65.712 | 0.40741 | -121.431 | 0.48981 | -29.6082 | -119.838 | -7.5668 | -0.064086 | -0.10071 | 0.009155 | 0.75531 | -0.009155 | 0 | 0.054931 | 0.064086 | -0.041198 | -0.073242 | 0.009155 | 91.7816 | 113.8229 | 1.5518 | 113.8641 | 1.593 | 0.8194 | 121.9437 | 91.8228 | 121.9208 | 121.8338 | 121.8384 | 121.7697 | 121.7972 | -121.9345 | -121.9116 | 121.8796 | 121.8796 | 118.0527 | 55.6778
2269.2969 | 122.1085 | -121.4127 | 0.48065 | -0.60875 | -0.0011471 | 0.054762 | 0.054335 | -0.0027728 | -0.0089743 | -0.0034031 | 0.0009461 | 0.0070708 | 0.1341 | 0.056937 | -0.017568 | 0.027344 | 0.68345 | -3.4515 | 0.37537 | -121.5363 | 0.43488 | -120.7306 | -121.4401 | -121.4355 | -65.9958 | 0.41199 | -121.4355 | 0.4715 | -29.2419 | -119.8563 | -7.4203 | -0.1236 | -0.10529 | -0.045777 | 0.68207 | -0.022888 | -0.027466 | 0.10071 | 0.09613 | -0.022888 | -0.068665 | -0.009155 | 92.1707 | 113.9923 | 1.5564 | 114.0152 | 1.5793 | 0.80566 | 121.9711 | 92.1936 | 121.907 | 121.9116 | 121.8475 | 121.788 | 121.8246 | -122.0169 | -121.9162 | 121.8475 | 121.8842 | 117.9611 | 55.4169
2270.9688 | 121.701 | -121.0007 | 0.52643 | 0.0016023 | 0.028119 | 0.11116 | 0.040449 | 0.046788 | 0.057462 | 0.051285 | -0.0082093 | -0.0036102 | 0.11744 | 0.052024 | -0.015646 | 0.011963 | 0.68217 | -3.4836 | 0.40283 | -121.2662 | 0.37079 | -120.8359 | -121.5775 | -121.4539 | -66.0461 | 0.46692 | -121.4539 | 0.36621 | -29.0726 | -119.957 | -7.2372 | -0.2655 | -0.1236 | -0.15564 | 0.16479 | -0.45319 | -0.57678 | -0.18768 | -0.31128 | -0.45319 | -0.059509 | -0.16022 | 91.9281 | 113.7634 | 1.0437 | 114.2166 | 1.4969 | 0.4303 | 121.637 | 92.3813 | 121.8201 | 121.669 | 121.9208 | 121.4035 | 121.4676 | -121.7926 | -121.9803 | 121.3715 | 121.3669 | 117.5171 | 54.9545
2272.7188 | 122.0673 | -121.1975 | 0.50812 | -0.0060272 | -0.0017881 | 0.049208 | 0.041304 | -0.014522 | -0.013674 | -0.021561 | -0.0021057 | -0.00019216 | 0.12214 | 0.048178 | -0.027609 | 0.023071 | 0.64478 | -3.447 | 0.39368 | -120.9 | 0.37994 | -120.7901 | -121.4355 | -121.3303 | -66.037 | 0.43488 | -120.8313 | 0.41199 | -28.7888 | -119.7235 | -10.0571 | 0.29755 | -0.11444 | -0.12817 | 0.40741 | -0.13275 | -0.23804 | -0.4303 | -0.53558 | 0.36621 | -0.073243 | -0.096131 | 92.4088 | 111.1404 | 1.474 | 110.7742 | 1.1078 | 0.10986 | 121.2799 | 92.0425 | 121.2433 | 121.2936 | 121.2662 | 121.5912 | 121.6324 | -121.4081 | -121.3394 | 121.5775 | 121.6095 | 117.7505 | 55.1605
2274.4688 | 121.9894 | -121.4081 | 0.50812 | -0.0060272 | -0.0096921 | 0.10924 | 0.044295 | -0.0034136 | 0.020719 | 0.050644 | -0.0051575 | 0.001944 | 0.12406 | 0.05416 | -0.021627 | 0.013031 | 0.64372 | -3.5614 | 0.38452 | -121.0098 | 0.33417 | -120.8176 | -121.5317 | -121.3989 | -66.3849 | 0.42572 | -120.8221 | 0.35248 | -30.4047 | -119.8471 | -9.5673 | 0.39825 | -0.1236 | -0.17395 | 0.59051 | 0.009155 | -0.1236 | -0.3891 | -0.52185 | 0.58594 | -0.082398 | -0.15564 | 91.0034 | 111.8408 | 1.561 | 111.2549 | 0.97504 | 0.19226 | 121.344 | 90.4175 | 121.1746 | 121.3943 | 121.2479 | 121.7926 | 121.8338 | -121.5179 | -121.3303 | 121.7422 | 121.7606 | 117.8467 | 55.0232
2276.1562 | 122.1176 | -121.4676 | 0.38452 | -0.013657 | 0.0007755 | 0.055617 | 0.056685 | 0.0027814 | -0.010043 | -0.0038303 | -0.0051575 | 0.0077118 | 0.13325 | 0.075736 | -0.016073 | 0.027344 | 0.51426 | -3.6209 | 0.27008 | -121.463 | 0.3479 | -120.8038 | -121.5546 | -121.5591 | -67.3965 | 0.32044 | -121.2708 | 0.41199 | -30.8029 | -120.0165 | -35.4126 | 0.004577 | -0.11444 | -0.036621 | 0.66376 | -0.091553 | -0.086975 | -0.09613 | -0.091552 | 0.19684 | -0.064086 | 0.027466 | 90.6647 | 86.055 | 1.4511 | 85.8582 | 1.2543 | 0.65918 | 121.8109 | 90.4678 | 121.6827 | 121.7331 | 121.5912 | 121.7377 | 121.788 | -121.8475 | -121.6553 | 121.8155 | 121.8796 | 117.8467 | 54.071
2277.9062 | 122.0352 | -121.5591 | 0.39368 | -0.013657 | -0.0026425 | 0.11116 | 0.049849 | -0.0044818 | 0.057676 | 0.052353 | -0.0051575 | 0.0025848 | 0.12022 | 0.048819 | -0.020132 | 0.011536 | 0.42817 | -3.6118 | 0.25177 | -121.2845 | 0.25177 | -120.9091 | -121.6736 | -121.5637 | -68.1839 | 0.30212 | -120.9412 | 0.24261 | -32.4463 | -120.0897 | -41.3727 | 0.27466 | -0.14191 | -0.14191 | 0.65002 | -0.004578 | -0.11444 | -0.27924 | -0.3891 | 0.61798 | -0.091553 | -0.15106 | 89.1129 | 80.1865 | 1.4694 | 79.5685 | 0.85144 | 0.37537 | 121.5363 | 88.4949 | 121.1838 | 121.5363 | 121.2433 | 121.8109 | 121.8613 | -121.6782 | -121.3348 | 121.8109 | 121.8018 | 117.9474 | 53.3752
2279.6562 | 121.994 | -121.4493 | 0.49896 | 0.0016023 | -0.013324 | 0.10881 | 0.053053 | -0.002132 | 0.056608 | 0.050644 | -0.0021057 | 0.0068572 | 0.12492 | 0.061637 | -0.0165 | 0.01944 | 0.63624 | -3.6209 | 0.38452 | -121.2112 | 0.31586 | -120.7993 | -121.5866 | -121.5042 | -67.4835 | 0.42572 | -120.8588 | 0.34332 | -33.5312 | -119.957 | -11.4487 | 0.23804 | -0.11444 | -0.18311 | 0.65002 | -0.054931 | -0.13733 | -0.29297 | -0.37537 | 0.59051 | -0.073242 | -0.15564 | 87.9181 | 110.0006 | 1.4923 | 109.4101 | 0.9018 | 0.41199 | 121.5271 | 87.3276 | 121.2021 | 121.5958 | 121.2845 | 121.8338 | 121.875 | -121.7102 | -121.3577 | 121.7651 | 121.7926 | 117.8284 | 53.9658
2281.3438 | 121.9894 | -121.4676 | 0.48523 | -0.0060272 | -0.0009335 | 0.054762 | 0.051772 | -0.0042682 | -0.0096151 | -0.0059665 | -0.0021057 | 0.0083526 | 0.13303 | 0.055655 | -0.016714 | 0.028412 | 0.64585 | -3.6575 | 0.37537 | -121.0968 | 0.29755 | -120.8313 | -121.5225 | -121.5591 | -68.1702 | 0.42572 | -120.9732 | 0.33875 | -34.3185 | -119.9387 | -11.412 | 0.37079 | -0.10986 | -0.18768 | 0.63629 | -0.091553 | -0.054932 | -0.46234 | -0.42572 | 0.49438 | -0.059509 | -0.14648 | 87.149 | 110.0555 | 1.5289 | 109.5612 | 1.0345 | 0.2655 | 121.3943 | 86.6547 | 121.312 | 121.4722 | 121.3989 | 121.843 | 121.8933 | -121.582 | -121.4584 | 121.7651 | 121.8063 | 117.8101 | 53.2974
2283.0938 | 122.0444 | -121.4493 | 0.48981 | -0.0060272 | -0.0069149 | 0.038527 | 0.054762 | -0.019008 | -0.023287 | -0.023484 | -0.0021057 | 0.0089934 | 0.12193 | 0.061637 | -0.017782 | 0.018158 | 0.63175 | -3.6255 | 0.37079 | -121.3669 | 0.37079 | -120.6757 | -121.5042 | -121.4859 | -68.4998 | 0.40741 | -120.813 | 0.3891 | -39.4821 | -119.8608 | -10.8353 | 0.082398 | -0.11902 | -0.11902 | 0.77362 | -0.036621 | -0.054931 | -0.11902 | -0.13733 | 0.63629 | -0.082397 | -0.10071 | 81.9672 | 110.614 | 1.5884 | 109.9777 | 0.95215 | 0.69122 | 121.7377 | 81.3309 | 121.2021 | 121.7377 | 121.2204 | 121.8201 | 121.8567 | -121.8567 | -121.3028 | 121.8201 | 121.8384 | 117.8238 | 52.9495
2284.8594 | 121.9986 | -121.7377 | 0.25177 | -0.013657 | -0.0020017 | 0.05348 | 0.052412 | 0.0019268 | -0.0085471 | -0.0046847 | -0.0051575 | 0.51806 | 0.1309 | 0.066764 | -0.015859 | 0.027985 | 0.67875 | -3.7308 | 0.10529 | -121.4859 | 0.032043 | -121.0739 | -121.7926 | -121.8155 | -69.0903 | 0.11902 | -121.2845 | 0.032043 | -37.4496 | -120.2042 | -5.3329 | 0.25177 | -0.14648 | -0.21973 | 0.66376 | -0.07782 | -0.054932 | -0.32959 | -0.3067 | 0.45319 | -0.13275 | -0.21973 | 84.288 | 116.4047 | 1.5335 | 115.9515 | 1.0803 | 0.41199 | 121.5179 | 83.8348 | 121.3165 | 121.5912 | 121.4035 | 121.843 | 121.8567 | -121.7377 | -121.5363 | 121.7697 | 121.7697 | 118.0069 | 52.6474
2286.625 | 122.0627 | -121.7743 | 0.10986 | 0.0016023 | -0.0032833 | 0.051985 | 0.051558 | -0.0019184 | -0.0091879 | -0.0025485 | -0.0021057 | 0.6834 | 0.13004 | 0.054801 | -0.016714 | 0.026489 | 0.68601 | -3.8132 | 0.009155 | -121.8521 | 0 | -121.0831 | -121.8384 | -121.8155 | -68.7973 | 0 | -121.788 | 0.027466 | -35.2112 | -120.1767 | -3.5248 | -0.07782 | -0.10071 | -0.10986 | 0.69122 | -0.041199 | -0.064087 | 0.036621 | 0.013733 | -0.013733 | -0.10986 | -0.082397 | 86.5631 | 118.2495 | 1.5976 | 118.2632 | 1.6113 | 0.76904 | 121.8521 | 86.5768 | 121.8155 | 121.8613 | 121.788 | 121.7834 | 121.7743 | -121.962 | -121.8979 | 121.7743 | 121.8018 | 117.9611 | 52.977
2288.375 | 121.9757 | -121.7651 | 0.15106 | -0.013657 | -0.0041379 | 0.10881 | 0.051772 | -0.012386 | -0.02756 | -0.010666 | -0.0051575 | 0.699 | 0.12193 | 0.048178 | -0.021627 | 0.014954 | 0.69285 | -3.7811 | 0.022888 | -121.8155 | -0.013733 | -121.0098 | -121.8613 | -121.8658 | -67.9779 | 0 | -121.3623 | -0.022888 | -36.232 | -120.2362 | -0.40741 | -0.050354 | -0.12817 | -0.16479 | 0.75531 | -0.10071 | -0.09613 | -0.050354 | -0.045776 | 0.40283 | -0.15106 | -0.17395 | 85.5331 | 121.3577 | 1.5289 | 120.9549 | 1.1261 | 0.80566 | 121.8018 | 85.1303 | 121.3394 | 121.8384 | 121.3623 | 121.788 | 121.7651 | -121.9666 | -121.5134 | 121.7514 | 121.7422 | 117.984 | 53.7872
2290.0625 | 122.0444 | -121.7606 | 0.10986 | -0.013657 | 0.0003483 | 0.054335 | 0.053267 | -0.002132 | -0.0076925 | -0.0016941 | -0.0051575 | 0.70669 | 0.12876 | 0.056083 | -0.015859 | 0.028626 | 0.69926 | -3.8681 | 0.004578 | -121.8613 | 0.018311 | -121.0785 | -121.8063 | -121.8063 | -67.6849 | -0.022888 | -121.7972 | 0.013733 | -35.9482 | -120.1813 | -0.29297 | -0.10071 | -0.10529 | -0.091552 | 0.68207 | -0.045776 | -0.045776 | 0.054932 | 0.054932 | -0.036621 | -0.13275 | -0.09613 | 85.8124 | 121.4676 | 1.5793 | 121.5042 | 1.6159 | 0.78278 | 121.8796 | 85.849 | 121.8109 | 121.8658 | 121.7743 | 121.7651 | 121.7377 | -121.9711 | -121.907 | 121.7789 | 121.7743 | 117.8925 | 54.0756
2291.8125 | 122.0673 | -121.7285 | 0.10071 | -0.013657 | 0.0026981 | 0.055617 | 0.054762 | 0.0021406 | -0.0070517 | -0.0040439 | -0.0021057 | 0.70327 | 0.12727 | 0.066977 | -0.015432 | 0.028412 | 0.6984 | -3.8956 | -0.032043 | -121.843 | 0.073242 | -121.0327 | -121.7743 | -121.8018 | -67.8955 | -0.027466 | -121.7834 | 0.07782 | -39.6332 | -120.1035 | -0.2243 | -0.11444 | -0.13275 | -0.027466 | 0.6958 | -0.073242 | -0.045776 | 0.041199 | 0.068665 | -0.054931 | -0.12817 | -0.022888 | 82.0953 | 121.5042 | 1.6251 | 121.5591 | 1.68 | 0.81024 | 121.9162 | 82.1503 | 121.8613 | 121.8109 | 121.756 | 121.6965 | 121.701 | -121.9437 | -121.8842 | 121.8018 | 121.8063 | 117.8329 | 53.833
2293.5625 | 122.0673 | -121.7422 | 0.10986 | -0.013657 | 0.0020571 | 0.054976 | 0.054976 | 0.0038494 | -0.0089743 | -0.0038303 | 0.0009461 | 0.70113 | 0.13261 | 0.060996 | -0.015859 | 0.026489 | 0.69755 | -3.9322 | -0.022888 | -121.8384 | 0.07782 | -121.0236 | -121.7697 | -121.7834 | -67.5293 | -0.004578 | -121.7514 | 0.050354 | -36.9736 | -120.108 | -0.24719 | -0.09613 | -0.13275 | -0.032043 | 0.71869 | -0.041198 | -0.027465 | 0.054932 | 0.068665 | -0.009155 | -0.11444 | -0.059509 | 84.7687 | 121.4951 | 1.6342 | 121.5042 | 1.6434 | 0.81482 | 121.9162 | 84.7778 | 121.8018 | 121.8155 | 121.7468 | 121.7194 | 121.7377 | -121.9482 | -121.8613 | 121.8201 | 121.7926 | 117.8101 | 54.213
2295.2656 | 121.994 | -121.7789 | 0.14648 | -0.0060272 | 0.0018435 | 0.047713 | 0.053053 | -0.0034136 | -0.013247 | -0.014298 | -0.0021057 | 0.6928 | 0.12385 | 0.049674 | -0.016287 | 0.02179 | 0.692 | -3.891 | 0.022888 | -121.875 | 0.018311 | -121.0968 | -121.8155 | -121.8521 | -67.5293 | 0 | -121.7972 | -0.013733 | -36.7447 | -120.1492 | -0.27466 | -0.09613 | -0.1236 | -0.12817 | 0.68207 | -0.073242 | -0.036621 | 0.022888 | 0.059509 | -0.01831 | -0.14648 | -0.16022 | 85.0342 | 121.5042 | 1.6296 | 121.5225 | 1.6479 | 0.7782 | 121.8933 | 85.0525 | 121.7834 | 121.8979 | 121.7972 | 121.8018 | 121.7789 | -122.0215 | -121.9437 | 121.7972 | 121.7651 | 117.8879 | 54.2496
2297.0156 | 121.9299 | -121.7651 | 0.15106 | -0.013657 | -0.0064877 | 0.044295 | 0.054976 | -0.0096088 | -0.024996 | -0.025406 | -0.0051575 | 0.70006 | 0.12705 | 0.066977 | -0.014791 | 0.022644 | 0.68388 | -3.9963 | 0.018311 | -121.8842 | -0.027466 | -121.1563 | -121.8933 | -121.8933 | -67.804 | 0.018311 | -121.7789 | -0.073242 | -38.2416 | -120.2042 | -0.32959 | -0.11902 | -0.13275 | -0.17853 | 0.60883 | -0.12817 | -0.12817 | -0.009156 | -0.009156 | -0.013733 | -0.13275 | -0.2243 | 83.5236 | 121.4355 | 1.561 | 121.4493 | 1.5747 | 0.72784 | 121.8567 | 83.5373 | 121.7056 | 121.9025 | 121.7972 | 121.7834 | 121.7834 | -122.0352 | -121.9299 | 121.7377 | 121.6919 | 117.7689 | 53.9612
2298.7812 | 122.0123 | -121.7285 | 0.1236 | -0.013657 | -0.0037107 | 0.053908 | 0.051131 | 0.0019268 | -0.0096151 | -0.0034031 | -0.0021057 | 0.69622 | 0.12897 | 0.050742 | -0.015432 | 0.027557 | 0.6905 | -3.9368 | -0.009155 | -121.8475 | 0.082397 | -121.0236 | -121.756 | -121.7697 | -68.0328 | -0.013733 | -121.7789 | -0.004578 | -41.4642 | -120.0989 | -0.25177 | -0.11902 | -0.13275 | -0.041199 | 0.70496 | -0.041198 | -0.027465 | 0.07782 | 0.091553 | -0.050354 | -0.13733 | -0.12817 | 80.2643 | 121.4767 | 1.6296 | 121.5271 | 1.68 | 0.82397 | 121.9299 | 80.3146 | 121.7743 | 121.8384 | 121.7651 | 121.7194 | 121.7148 | -121.9711 | -121.9025 | 121.8109 | 121.7239 | 117.7917 | 53.6957
2300.5469 | 122.0215 | -121.7697 | 0.10529 | -0.0060272 | -0.0002927 | 0.053053 | 0.054549 | -0.0010638 | -0.011324 | -0.0010531 | -0.0051575 | 0.69259 | 0.11253 | 0.062064 | -0.014364 | 0.027557 | 0.68281 | -4.0924 | -0.013733 | -121.8704 | 0.013733 | -121.0785 | -121.8063 | -121.8155 | -70.1477 | -0.027466 | -121.788 | -0.013733 | -68.486 | -120.1263 | -0.25635 | -0.10071 | -0.11902 | -0.091553 | 0.69122 | -0.045777 | -0.036621 | 0.054931 | 0.064087 | -0.018311 | -0.13275 | -0.11902 | 53.2837 | 121.5134 | 1.6434 | 121.5317 | 1.6617 | 0.79193 | 121.8842 | 53.302 | 121.7743 | 121.8567 | 121.7606 | 121.756 | 121.7422 | -121.9757 | -121.8933 | 121.7834 | 121.756 | 117.6773 | 51.622
2302.2344 | 122.0718 | -121.7468 | 0.1236 | -0.0060272 | -0.0026425 | 0.054335 | 0.052412 | -0.0044818 | -0.0081197 | -0.0051121 | -0.0021057 | 0.69344 | 0.11701 | 0.058219 | -0.016714 | 0.029053 | 0.68601 | -4.0878 | -0.004578 | -121.8658 | 0.036621 | -121.0419 | -121.7651 | -121.7789 | -69.9142 | -0.059509 | -121.7743 | 0.018311 | -64.2517 | -120.0302 | -0.21515 | -0.11902 | -0.12817 | -0.086975 | 0.70496 | -0.032044 | -0.018311 | 0.086975 | 0.10071 | -0.027466 | -0.1831 | -0.10528 | 57.4951 | 121.5317 | 1.7166 | 121.5591 | 1.7441 | 0.82397 | 121.9025 | 57.5226 | 121.7926 | 121.8613 | 121.7148 | 121.7422 | 121.6873 | -121.9894 | -121.8979 | 121.7834 | 121.7651 | 117.659 | 51.8326
2303.9844 | 122.0306 | -121.7514 | 0.10986 | -0.0060272 | -0.0009335 | 0.055403 | 0.05284 | -0.0044818 | -0.0094015 | -0.0042575 | -0.0051575 | 0.69045 | 0.12556 | 0.061637 | -0.017568 | 0.028198 | 0.68345 | -4.1611 | -0.018311 | -121.843 | 0.018311 | -121.0785 | -121.7926 | -121.8018 | -68.9163 | -0.013733 | -121.7468 | -0.009155 | -52.1301 | -120.0531 | -0.25635 | -0.091553 | -0.12817 | -0.091552 | 0.67291 | -0.050354 | -0.041199 | 0.041199 | 0.050354 | 0.004578 | -0.1236 | -0.11902 | 69.6213 | 121.4951 | 1.6983 | 121.4905 | 1.6937 | 0.76447 | 121.8613 | 69.6167 | 121.7377 | 121.8246 | 121.7331 | 121.7331 | 121.7377 | -121.9528 | -121.8567 | 121.7697 | 121.7422 | 117.5903 | 52.8351
2305.6719 | 122.0215 | -121.7377 | 0.10071 | -0.0060272 | -0.0005063 | 0.052626 | 0.05348 | 0.0010724 | -0.0076925 | -0.0044711 | -0.0021057 | 0.68725 | 0.12492 | 0.053305 | -0.016928 | 0.027771 | 0.67661 | -4.1977 | -0.013733 | -121.8063 | 0.073242 | -121.0098 | -121.7926 | -121.7789 | -69.0857 | -0.027466 | -121.7697 | 0.013733 | -53.8925 | -120.0348 | -0.26093 | -0.068664 | -0.11444 | -0.027466 | 0.72784 | -0.041199 | -0.054932 | 0.027465 | 0.013732 | -0.032043 | -0.12817 | -0.086975 | 67.8452 | 121.4767 | 1.7029 | 121.5088 | 1.7349 | 0.79651 | 121.8796 | 67.8772 | 121.7834 | 121.7926 | 121.7422 | 121.7239 | 121.7102 | -121.907 | -121.8704 | 121.8109 | 121.7514 | 117.54 | 52.652
2307.4375 | 122.0764 | -121.7194 | 0.086975 | -0.0060272 | 0.0022709 | 0.055189 | 0.054549 | -0.001491 | -0.0072653 | -0.0048985 | -0.0051575 | 0.68532 | 0.12214 | 0.065482 | -0.016287 | 0.030548 | 0.67854 | -4.2068 | -0.013733 | -121.8109 | 0.10071 | -120.9961 | -121.7514 | -121.7422 | -69.1544 | -0.022888 | -121.7422 | 0.064087 | -53.421 | -119.9387 | -0.19226 | -0.091553 | -0.10071 | 0.013733 | 0.72327 | -0.022889 | -0.032044 | 0.068664 | 0.059509 | -0.022889 | -0.10986 | -0.022888 | 68.2983 | 121.5271 | 1.7807 | 121.55 | 1.8036 | 0.81482 | 121.9116 | 68.3212 | 121.8063 | 121.7972 | 121.7194 | 121.7056 | 121.6965 | -121.8979 | -121.8292 | 121.8201 | 121.7834 | 117.5125 | 52.565
2309.1406 | 122.0306 | -121.7331 | 0.11444 | -0.0060272 | 0.0001345 | 0.055617 | 0.053908 | 0.0017132 | -0.0074789 | -0.0055393 | -0.0051575 | 0.68511 | 0.12321 | 0.062705 | -0.017355 | 0.027771 | 0.67426 | -4.2618 | -0.027466 | -121.8201 | 0.068665 | -121.0144 | -121.7743 | -121.7743 | -69.0491 | -0.018311 | -121.7651 | 0.036621 | -53.096 | -119.9432 | -0.21515 | -0.086975 | -0.14191 | -0.045776 | 0.71869 | -0.041199 | -0.041199 | 0.045776 | 0.045776 | -0.032044 | -0.13275 | -0.07782 | 68.6371 | 121.5179 | 1.7899 | 121.55 | 1.8219 | 0.80566 | 121.8887 | 68.6691 | 121.8018 | 121.7926 | 121.7468 | 121.7056 | 121.7148 | -121.9345 | -121.8796 | 121.8018 | 121.7697 | 117.4713 | 52.684
2310.8906 | 121.9162 | -121.7606 | 0.14191 | 0.0016023 | -0.0052059 | 0.045149 | 0.056471 | 0.029057 | -0.026491 | -0.011734 | -0.0051575 | 0.67507 | 0.11829 | 0.052665 | -0.015859 | 0.015381 | 0.67256 | -4.2664 | 0.027466 | -121.8887 | -0.018311 | -121.1197 | -121.8658 | -121.875 | -69.2505 | 0.013733 | -121.7514 | -0.064087 | -52.6382 | -119.9982 | -0.28381 | -0.12817 | -0.11444 | -0.16022 | 0.64087 | -0.11444 | -0.10529 | 0.013733 | 0.022888 | 0.009155 | -0.12817 | -0.20599 | 69.1223 | 121.4767 | 1.7624 | 121.4676 | 1.7532 | 0.76904 | 121.8704 | 69.1132 | 121.6873 | 121.9162 | 121.7651 | 121.788 | 121.7743 | -122.0306 | -121.8933 | 121.7422 | 121.6965 | 117.4942 | 52.5101
2312.6562 | 122.0306 | -121.6965 | 0.13733 | -0.0060272 | 0.0031253 | 0.056685 | 0.057112 | 0.0023542 | -0.0079061 | -0.0040439 | -0.0082093 | 0.65136 | 0.12492 | 0.09603 | -0.016073 | 0.030762 | 0.67234 | -4.3854 | 0.022888 | -121.7926 | 0.018311 | -121.0739 | -121.8246 | -121.8109 | -69.3649 | -0.004578 | -121.7377 | 0.041199 | -52.034 | -119.838 | -0.16937 | -0.096131 | -0.11444 | -0.11902 | 0.62256 | -0.11444 | -0.12817 | -0.01831 | -0.032043 | -0.041199 | -0.14191 | -0.09613 | 69.6625 | 121.5271 | 1.8585 | 121.5683 | 1.8997 | 0.71869 | 121.8109 | 69.7037 | 121.7789 | 121.8155 | 121.7331 | 121.7194 | 121.6919 | -121.9299 | -121.875 | 121.7148 | 121.7377 | 117.3111 | 52.3315
2314.3594 | 122.0306 | -121.4951 | 0.16479 | -0.0060272 | -0.0017881 | 0.054335 | 0.053267 | -0.0017048 | -0.0085471 | -0.00083947 | 0.0009461 | 0.60778 | 0.1247 | 0.13384 | -0.015219 | 0.029907 | 0.66743 | -4.4037 | 0.018311 | -121.7972 | 0.086975 | -120.8359 | -121.8109 | -121.756 | -69.4199 | 0.036621 | -121.6599 | 0.050354 | -52.0065 | -119.7464 | -0.17853 | -0.30212 | -0.14648 | -0.07782 | 0.65918 | -0.26093 | -0.31586 | 0.041199 | -0.013733 | -0.16479 | -0.12817 | -0.11444 | 69.4885 | 121.3165 | 1.7487 | 121.4813 | 1.9135 | 0.9613 | 121.8842 | 69.6533 | 121.7102 | 121.8155 | 121.6965 | 121.5134 | 121.5317 | -121.962 | -121.8246 | 121.582 | 121.5454 | 117.0914 | 52.0752
2316.1094 | 121.9254 | -121.7148 | 0.14191 | -0.0060272 | -0.010974 | 0.042372 | 0.056685 | -0.0087542 | -0.025637 | -0.012375 | -0.0021057 | 0.60287 | 0.13004 | 0.13918 | -0.016073 | 0.032257 | 0.66828 | -4.4586 | 0.022888 | -121.8475 | -0.054932 | -121.1426 | -121.8887 | -121.8704 | -69.7174 | -0.009155 | -121.7743 | -0.064087 | -51.7685 | -119.8471 | -0.25635 | -0.13275 | -0.11902 | -0.19684 | 0.5722 | -0.15564 | -0.17395 | -0.022888 | -0.041199 | -0.059509 | -0.15106 | -0.20599 | 69.9463 | 121.4584 | 1.8677 | 121.5179 | 1.9272 | 0.70496 | 121.7926 | 70.0058 | 121.7102 | 121.8704 | 121.7651 | 121.7377 | 121.7056 | -121.9894 | -121.9162 | 121.6599 | 121.6507 | 117.2562 | 51.9974
2317.8594 | 121.9437 | -121.7377 | 0.14191 | -0.0060272 | -0.0043515 | 0.045149 | 0.054549 | -0.016017 | -0.02051 | 0.051071 | -0.0051575 | 0.60009 | 0.11936 | 0.13405 | -0.017141 | 0.021149 | 0.66017 | -4.4357 | 0.013733 | -121.8796 | -0.022888 | -121.0968 | -121.8567 | -121.8658 | -69.7449 | 0.013733 | -121.7606 | -0.059509 | -51.9058 | -119.7922 | -0.27466 | -0.14191 | -0.12817 | -0.16479 | 0.64087 | -0.12817 | -0.11902 | 0.013733 | 0.022889 | -0.022888 | -0.12817 | -0.20142 | 69.8318 | 121.463 | 1.9455 | 121.4859 | 1.9684 | 0.78278 | 121.8567 | 69.8547 | 121.701 | 121.8933 | 121.7743 | 121.7514 | 121.7514 | -122.0215 | -121.9025 | 121.7148 | 121.6782 | 117.3019 | 51.9928
2319.5469 | 122.0123 | -121.7194 | 0.11444 | -0.013657 | -0.0015743 | 0.056685 | 0.051558 | 4.192e-06 | -0.0072653 | -0.0031895 | -0.0021057 | 0.64858 | 0.12769 | 0.087699 | -0.016287 | 0.02948 | 0.66123 | -4.5136 | -0.013733 | -121.788 | 0.004578 | -121.0373 | -121.7789 | -121.7743 | -69.7815 | -0.022888 | -121.7697 | 0.009155 | -51.0956 | -119.6594 | -0.23804 | -0.068665 | -0.12817 | -0.10986 | 0.68207 | -0.054932 | -0.05951 | 0.013733 | 0.009155 | -0.050354 | -0.13733 | -0.10529 | 70.6238 | 121.4813 | 2.0599 | 121.5317 | 2.1103 | 0.75073 | 121.7926 | 70.6741 | 121.7789 | 121.7743 | 121.7468 | 121.7056 | 121.6965 | -121.9025 | -121.8842 | 121.7239 | 121.7285 | 117.2058 | 51.9379
2321.2344 | 121.875 | -121.7239 | 0.14191 | -0.013657 | 0.0014163 | 0.048994 | 0.056471 | -0.0051226 | -0.013033 | -0.014298 | -0.0051575 | 0.63662 | 0.13047 | 0.10201 | -0.015859 | 0.03418 | 0.66123 | -4.5822 | 0.027466 | -121.8475 | -0.064087 | -121.17 | -121.8842 | -121.907 | -69.8227 | 0.009155 | -121.7834 | -0.059509 | -50.2945 | -119.632 | -0.27466 | -0.1236 | -0.11444 | -0.20599 | 0.55389 | -0.1831 | -0.16022 | -0.059509 | -0.036621 | -0.059509 | -0.13275 | -0.20142 | 71.4294 | 121.4493 | 2.092 | 121.5088 | 2.1515 | 0.67749 | 121.7834 | 71.489 | 121.7239 | 121.875 | 121.7926 | 121.7514 | 121.7331 | -121.9894 | -121.9254 | 121.6599 | 121.6644 | 117.1417 | 51.9012
2323 | 121.9849 | -121.7468 | 0.14648 | -0.0060272 | -0.0007199 | 0.049635 | 0.056258 | -0.0096088 | -0.014956 | -0.017288 | -0.0021057 | 0.64944 | 0.12812 | 0.084922 | -0.016928 | 0.024139 | 0.64799 | -4.5136 | 0 | -121.8704 | 0 | -121.051 | -121.7834 | -121.8109 | -69.5343 | 0.004578 | -121.7102 | 0 | -49.6078 | -119.5541 | -0.23804 | -0.1236 | -0.14648 | -0.14648 | 0.6958 | -0.064087 | -0.036621 | 0.059509 | 0.086975 | 0.036621 | -0.14191 | -0.14648 | 72.139 | 121.5088 | 2.1927 | 121.4722 | 2.1561 | 0.8194 | 121.8704 | 72.1024 | 121.7102 | 121.8704 | 121.7148 | 121.7468 | 121.7514 | -122.0169 | -121.8567 | 121.7468 | 121.7468 | 117.2333 | 52.2125
2324.7031 | 121.9299 | -121.701 | 0.10529 | 0.0016023 | -0.0007199 | 0.056258 | 0.052412 | -0.0012774 | -0.010683 | -0.0048985 | -0.0021057 | 0.61761 | 0.14414 | 0.11419 | -0.017141 | 0.033966 | 0.66102 | -4.6188 | -0.009155 | -121.7972 | 0.086975 | -120.9641 | -121.7285 | -121.7422 | -69.3512 | -0.041199 | -121.756 | 0.082397 | -48.9761 | -119.4489 | -0.15106 | -0.09613 | -0.11444 | -0.018311 | 0.737 | -0.041199 | -0.027466 | 0.054931 | 0.068664 | -0.054931 | -0.14649 | -0.022889 | 72.7249 | 121.55 | 2.2522 | 121.6049 | 2.3071 | 0.83313 | 121.8842 | 72.7798 | 121.8384 | 121.788 | 121.7148 | 121.6919 | 121.6599 | -121.9025 | -121.8613 | 121.788 | 121.7834 | 117.0822 | 52.3499
2326.4531 | 121.9254 | -121.7422 | 0.13275 | -0.013657 | -0.0020017 | 0.053267 | 0.052626 | 0.00085879 | -0.0094015 | -0.0074619 | -0.0051575 | 0.57595 | 0.1309 | 0.15755 | -0.017141 | 0.032898 | 0.66038 | -4.6555 | 0.018311 | -121.8658 | -0.064087 | -121.106 | -121.8109 | -121.8292 | -69.5297 | 0.009155 | -121.7789 | -0.09613 | -49.1684 | -119.5267 | -0.25177 | -0.1236 | -0.11444 | -0.19684 | 0.63629 | -0.086975 | -0.068664 | 0.036621 | 0.054932 | -0.036621 | -0.1236 | -0.22888 | 72.5739 | 121.4905 | 2.2156 | 121.5271 | 2.2522 | 0.75989 | 121.8018 | 72.6105 | 121.6827 | 121.8842 | 121.788 | 121.7606 | 121.7514 | -121.9986 | -121.9116 | 121.6782 | 121.6461 | 117.0868 | 52.2125
2328.2031 | 122.0169 | -121.669 | 0.10071 | -0.013657 | -0.0005063 | 0.054549 | 0.051985 | 0.0017132 | -0.0068381 | -0.0027621 | -0.0051575 | 0.55843 | 0.13175 | 0.17486 | -0.016714 | 0.032684 | 0.65568 | -4.7562 | 0.013733 | -121.8155 | 0.054932 | -120.9915 | -121.7331 | -121.7377 | -69.397 | -0.018311 | -121.7285 | 0.050354 | -50.1022 | -119.4168 | -0.13275 | -0.14648 | -0.086975 | -0.045776 | 0.67749 | -0.068665 | -0.064087 | 0.07782 | 0.082398 | -0.05951 | -0.11902 | -0.050354 | 71.5668 | 121.5363 | 2.2522 | 121.5958 | 2.3117 | 0.82397 | 121.8704 | 71.6263 | 121.7789 | 121.8292 | 121.7102 | 121.6827 | 121.6507 | -121.9162 | -121.8292 | 121.7239 | 121.7194 | 116.9128 | 52.272
2329.9688 | 121.962 | -121.7148 | 0.10529 | -0.013657 | 0.0003483 | 0.056471 | 0.054762 | 0.0014996 | -0.0089743 | -0.0093845 | -0.0021057 | 0.60543 | 0.16444 | 0.19216 | -0.016928 | 0.026703 | 0.64607 | -4.7012 | 0.009155 | -121.8658 | -0.013733 | -121.0373 | -121.8018 | -121.8201 | -65.181 | -0.027466 | -121.7697 | -0.041199 | -0.10071 | -119.3207 | -0.23804 | -0.15106 | -0.096131 | -0.11902 | 0.67749 | -0.10529 | -0.086975 | 0.045777 | 0.064087 | -0.054931 | -0.13275 | -0.14649 | 121.6141 | 121.4767 | 2.3941 | 121.5317 | 2.449 | 0.82855 | 121.8521 | 121.669 | 121.7285 | 121.875 | 121.7422 | 121.7239 | 121.6873 | -121.9711 | -121.875 | 121.701 | 121.6736 | 117.0135 | 56.5338
2331.6562 | 121.9757 | -121.7331 | 0.086975 | -0.0060272 | 0.0009891 | 0.05348 | 0.05284 | -0.00020941 | -0.0087607 | -0.011093 | -0.0051575 | 0.59966 | 0.16465 | 0.19707 | -0.015646 | 0.026703 | 0.63859 | -4.747 | 0 | -121.8384 | 0 | -121.0602 | -121.7972 | -121.8063 | -64.8834 | -0.022888 | -121.7606 | -0.045776 | -0.091553 | -119.3161 | -0.24719 | -0.10529 | -0.086975 | -0.086975 | 0.67291 | -0.073242 | -0.064087 | 0.032044 | 0.041199 | -0.027466 | -0.10986 | -0.13275 | 121.6415 | 121.4859 | 2.417 | 121.5134 | 2.4445 | 0.7782 | 121.8384 | 121.669 | 121.7148 | 121.8384 | 121.7377 | 121.7331 | 121.7102 | -121.9254 | -121.8475 | 121.7331 | 121.6873 | 116.9861 | 56.8497
2333.4062 | 122.0444 | -121.7148 | 0.07782 | 0.0092313 | -0.0011471 | 0.054121 | 0.051985 | 0.0014996 | -0.010256 | -0.0053257 | -0.0051575 | 0.53173 | 0.16358 | 0.26159 | -0.014578 | 0.033539 | 0.6497 | -4.7928 | -0.045776 | -121.8338 | 0.068665 | -120.9412 | -121.6782 | -121.701 | -64.3662 | -0.041199 | -121.7194 | 0.004578 | 0.036621 | -119.1834 | -0.17853 | -0.11902 | -0.1236 | -0.009155 | 0.77362 | 0.013733 | 0.036621 | 0.13275 | 0.15564 | -0.004577 | -0.11902 | -0.073242 | 121.7514 | 121.5363 | 2.5314 | 121.5408 | 2.536 | 0.89264 | 121.9025 | 121.756 | 121.7239 | 121.788 | 121.6782 | 121.669 | 121.6736 | -121.9116 | -121.7972 | 121.7834 | 121.7194 | 116.922 | 57.3486
2335.1562 | 121.9986 | -121.7331 | 0.064087 | -0.013657 | 0.0005619 | 0.057326 | 0.053267 | 0.001286 | -0.0072653 | -0.0061801 | -0.0021057 | 0.52318 | 0.1655 | 0.28103 | -0.017355 | 0.032684 | 0.65098 | -4.8981 | -0.041199 | -121.8063 | 0.036621 | -120.9824 | -121.7743 | -121.7514 | -64.3387 | -0.059509 | -121.756 | -0.013733 | -0.032043 | -119.2062 | -0.18768 | -0.073242 | -0.10529 | -0.027466 | 0.75073 | -0.018311 | -0.041199 | 0.054931 | 0.032043 | -0.022888 | -0.1236 | -0.07782 | 121.701 | 121.5454 | 2.5269 | 121.5683 | 2.5497 | 0.82397 | 121.843 | 121.7239 | 121.7422 | 121.7651 | 121.6965 | 121.6919 | 121.6736 | -121.8704 | -121.8201 | 121.7697 | 121.7194 | 116.835 | 57.3944
2336.9219 | 121.8658 | -121.7651 | 0.10986 | -0.0060272 | 0.0048343 | 0.04814 | 0.056258 | 4.192e-06 | -0.013674 | -0.0087437 | -0.0021057 | 0.53152 | 0.16721 | 0.26095 | -0.016073 | 0.032043 | 0.64671 | -4.9255 | -0.009155 | -121.8567 | -0.068665 | -121.138 | -121.8613 | -121.8704 | -64.064 | -0.018311 | -121.7697 | -0.10986 | -0.13275 | -119.2566 | -0.27924 | -0.091552 | -0.11902 | -0.17853 | 0.62714 | -0.10529 | -0.09613 | -0.013733 | -0.004578 | -0.004577 | -0.12817 | -0.21973 | 121.6324 | 121.4859 | 2.5085 | 121.4905 | 2.5131 | 0.71869 | 121.788 | 121.637 | 121.6599 | 121.8475 | 121.7514 | 121.756 | 121.7468 | -121.9666 | -121.8796 | 121.6965 | 121.6553 | 116.8396 | 57.7011
2338.6094 | 121.9345 | -121.7468 | 0.11444 | -0.013657 | 0.0016299 | 0.055403 | 0.054121 | 0.0014996 | -0.0094015 | -0.0046847 | -0.0021057 | 0.50503 | 0.1655 | 0.29021 | -0.01351 | 0.029694 | 0.63816 | -4.9072 | 0.004578 | -121.843 | -0.009155 | -121.0373 | -121.7743 | -121.8246 | -63.9679 | -0.036621 | -121.788 | -0.054932 | -0.041199 | -119.1696 | -0.23346 | -0.096131 | -0.10986 | -0.1236 | 0.70953 | -0.07782 | -0.027466 | 0.018311 | 0.068665 | -0.041199 | -0.15106 | -0.16937 | 121.7056 | 121.5134 | 2.5772 | 121.5546 | 2.6184 | 0.80567 | 121.8338 | 121.7468 | 121.7331 | 121.8475 | 121.7514 | 121.7514 | 121.7102 | -121.9574 | -121.9025 | 121.7377 | 121.6919 | 116.8396 | 57.7789
2340.3594 | 121.962 | -121.7514 | 0.09613 | -0.013657 | -0.0007199 | 0.056044 | 0.049208 | -0.002132 | -0.0083335 | -0.00083947 | -0.0051575 | 0.4826 | 0.16892 | 0.31115 | -0.01351 | 0.03418 | 0.64927 | -5.0491 | -0.032043 | -121.8063 | -0.013733 | -121.0281 | -121.7651 | -121.7834 | -63.739 | -0.032043 | -121.7468 | -0.059509 | -0.032043 | -119.1055 | -0.18768 | -0.054931 | -0.12817 | -0.10986 | 0.72327 | -0.032043 | -0.013733 | 0.022888 | 0.041198 | 0.004578 | -0.12817 | -0.15564 | 121.7194 | 121.5637 | 2.6459 | 121.5591 | 2.6413 | 0.7782 | 121.7926 | 121.7148 | 121.6873 | 121.7743 | 121.7148 | 121.7194 | 121.7194 | -121.9025 | -121.843 | 121.7377 | 121.6919 | 116.7023 | 58.0124
2342.1094 | 121.9254 | -121.6919 | 0.10529 | -0.021286 | -0.0011471 | 0.054121 | 0.054762 | -0.008327 | -0.01047 | -0.0098117 | 0.0009461 | 0.010062 | 0.0050736 | 0.0063083 | -0.0088097 | 0.013886 | -0.0018522 | -4.9896 | -0.022888 | -121.8201 | -0.009155 | -121.0419 | -121.7651 | -121.7789 | 0.022888 | 0.022888 | -0.16479 | 0.004578 | 0.09613 | -0.027466 | 0.082397 | -0.12817 | -0.12817 | -0.11444 | 0.65002 | -0.086975 | -0.073242 | 0.041198 | 0.054931 | 121.5271 | -0.082398 | -0.10071 | 121.788 | 121.7743 | 121.6644 | 0.24719 | 0.13733 | 0.7782 | 121.8109 | 0.26092 | 0.16937 | 121.7972 | 0.18768 | 121.669 | 121.7148 | -121.9254 | -0.27008 | 121.6827 | 121.6965 | 116.7023 | 121.7148
2343.7969 | 121.9711 | -121.8109 | 0.10529 | -0.0060272 | 0.0022709 | 0.053694 | 0.056471 | -0.00063661 | -0.0083335 | -0.0044711 | -0.0082093 | 0.011771 | 0.0052872 | -0.0035183 | -0.010732 | 0.024567 | 0.0032748 | -5.1865 | -0.009155 | -121.9025 | -0.091553 | -121.2158 | -121.9437 | -121.9345 | -0.059509 | 0.032043 | -0.16479 | -0.045776 | 0.036621 | -0.086975 | 0.050354 | -0.091553 | -0.11444 | -0.19684 | 0.59509 | -0.1236 | -0.13275 | -0.032043 | -0.041199 | 121.6461 | -0.073243 | -0.15106 | 121.8475 | 121.8613 | 121.7239 | 0.21515 | 0.07782 | 0.68665 | 121.8109 | 0.20142 | 0.11902 | 121.8933 | 0.19684 | 121.8018 | 121.843 | -122.0078 | -0.27008 | 121.7194 | 121.7651 | 116.6245 | 121.7514
2345.5625 | 122.1039 | -121.7926 | 0.086975 | -0.013657 | 0.0003483 | 0.055617 | 0.053694 | 0.00021799 | -0.0076925 | -0.0066073 | -0.0021057 | 0.012198 | 0.0022964 | 0.0013949 | -0.01351 | 0.022644 | 0.0013522 | -5.191 | -0.050354 | -121.8796 | 0.064087 | -121.0648 | -121.8201 | -121.8338 | 0.10529 | 0 | -0.12817 | 0.073242 | 0.16937 | 0.073242 | 0.11902 | -0.086975 | -0.13733 | -0.022888 | 0.72785 | -0.041198 | -0.027465 | 0.045777 | 0.05951 | 121.6644 | -0.086975 | -0.013733 | 121.962 | 121.9116 | 121.8658 | 0.24719 | 0.20142 | 0.81482 | 121.9437 | 0.29755 | 0.20142 | 121.8292 | 0.12817 | 121.7422 | 121.7926 | -121.9666 | -0.21515 | 121.8567 | 121.8658 | 116.6016 | 121.8979
2347.25 | 122.1405 | -121.7972 | 0.07782 | -0.0060272 | -0.0026425 | 0.053908 | 0.051772 | -0.004909 | -0.0079061 | -0.0063937 | -0.0021057 | 0.013052 | 0.0033646 | 0.00011332 | -0.013296 | 0.020508 | -0.002493 | -5.1498 | -0.054932 | -121.9208 | 0.064087 | -121.051 | -121.8018 | -121.8018 | 0.14191 | 0.009155 | -0.10986 | 0.059509 | 0.19684 | 0.10529 | 0.13275 | -0.1236 | -0.13275 | -0.013733 | 0.74616 | -0.004578 | -0.004578 | 0.11902 | 0.11902 | 121.6873 | -0.068665 | -0.018311 | 121.994 | 121.9299 | 121.9025 | 0.24261 | 0.21515 | 0.86975 | 121.9849 | 0.3067 | 0.16937 | 121.8658 | 0.11902 | 121.7422 | 121.8063 | -121.9986 | -0.18768 | 121.8613 | 121.8567 | 116.6473 | 121.9391
2349 | 122.1451 | -121.8155 | 0.086975 | -0.0060272 | -0.0041379 | 0.054335 | 0.052199 | -0.0010638 | -0.0087607 | -0.0036167 | -0.0051575 | 0.012198 | 0.0018692 | 0.0050265 | -0.015219 | 0.022003 | -0.0001432 | -5.2139 | -0.054932 | -121.9528 | 0.059509 | -121.0739 | -121.8109 | -121.8292 | 0.086975 | -0.004578 | -0.10529 | 0.059509 | 0.1831 | 0.11444 | 0.14191 | -0.13733 | -0.14191 | -0.027466 | 0.74158 | -0.013733 | 0.004578 | 0.1236 | 0.14191 | 121.7102 | -0.091553 | -0.027466 | 121.9986 | 121.9574 | 121.9299 | 0.24719 | 0.21973 | 0.87891 | 122.0123 | 0.28839 | 0.16479 | 121.8979 | 0.10071 | 121.7606 | 121.8109 | -122.0398 | -0.19226 | 121.875 | 121.875 | 116.6016 | 121.9025
2350.7656 | 122.0581 | -121.8613 | 0.07782 | 0.0016023 | 0.0014163 | 0.055403 | 0.056044 | -0.00042301 | -0.01282 | -0.010666 | 0.0009461 | 0.015189 | 0.0022964 | 0.0063083 | -0.017355 | 0.02243 | -0.000784 | -5.3009 | -0.022888 | -121.9711 | -0.022888 | -121.1792 | -121.9162 | -121.9437 | 0 | 0.045776 | -0.13275 | -0.013733 | 0.068665 | -0.022888 | 0.054932 | -0.10986 | -0.10071 | -0.10071 | 0.68207 | -0.082398 | -0.054932 | 0.027465 | 0.054931 | 121.7285 | -0.032044 | -0.091553 | 121.9299 | 121.9162 | 121.8384 | 0.18768 | 0.10986 | 0.79193 | 121.9482 | 0.20142 | 0.11902 | 121.9482 | 0.17853 | 121.8384 | 121.907 | -122.049 | -0.21057 | 121.8384 | 121.8475 | 116.5604 | 121.8613
2352.5156 | 122.1268 | -121.843 | 0.091553 | -0.021286 | -0.0015743 | 0.053694 | 0.052626 | -0.00085021 | -0.0089743 | -0.0016941 | -0.0021057 | 0.010489 | 0.003151 | -0.00031408 | -0.01415 | 0.020935 | -0.0027066 | -5.4382 | -0.027466 | -121.9574 | -0.027466 | -121.1655 | -121.9116 | -121.9025 | 0 | 0.009155 | -0.10986 | 0.013733 | 0.14648 | 0.054932 | 0.10071 | -0.11444 | -0.11902 | -0.11902 | 0.67749 | -0.059509 | -0.068664 | 0.054931 | 0.045776 | 121.7331 | -0.082398 | -0.07782 | 121.9894 | 121.9437 | 121.8979 | 0.21057 | 0.16479 | 0.79193 | 121.9299 | 0.25635 | 0.1236 | 121.9299 | 0.11902 | 121.8155 | 121.8521 | -122.049 | -0.20142 | 121.8155 | 121.8567 | 116.4047 | 121.843
2354.2656 | 122.1588 | -121.8292 | 0.082397 | -0.0060272 | 0.0020571 | 0.054762 | 0.053694 | 0.004704 | -0.0068381 | -0.0042575 | -0.0082093 | 0.011771 | -0.00026697 | -0.0011685 | -0.014791 | 0.022217 | 0.0011386 | -5.4749 | -0.054932 | -121.9482 | 0.050354 | -121.1243 | -121.8842 | -121.8842 | 0.082397 | 0.009155 | -0.10071 | 0.07782 | 0.17395 | 0.07782 | 0.14191 | -0.11902 | -0.13733 | -0.032043 | 0.70496 | -0.054931 | -0.054931 | 0.064087 | 0.064087 | 121.7285 | -0.073242 | -0.004577 | 122.0032 | 121.9711 | 121.907 | 0.24262 | 0.17853 | 0.82397 | 121.9986 | 0.27466 | 0.17853 | 121.8933 | 0.10986 | 121.7743 | 121.8384 | -122.0306 | -0.18311 | 121.8796 | 121.907 | 116.3544 | 121.9116
2356.0312 | 122.1451 | -121.8704 | 0.07782 | 0.0016023 | -0.0009335 | 0.05348 | 0.051344 | -0.0017048 | -0.0098287 | -0.0044711 | 0.0009461 | 0.011771 | 0.0040054 | 0.0097263 | -0.015646 | 0.02179 | -0.003561 | -5.4749 | -0.064087 | -121.9711 | 0.045776 | -121.0968 | -121.8384 | -121.8567 | 0.091553 | 0.018311 | -0.10986 | 0.050354 | 0.1831 | 0.09613 | 0.1236 | -0.10071 | -0.14191 | -0.032044 | 0.77362 | 0.013733 | 0.032043 | 0.11444 | 0.13275 | 121.7606 | -0.059509 | -0.027466 | 122.0535 | 121.994 | 121.9666 | 0.23346 | 0.20599 | 0.87433 | 122.0169 | 0.29297 | 0.16022 | 121.907 | 0.12817 | 121.8063 | 121.8887 | -122.049 | -0.18768 | 121.9162 | 121.9208 | 116.3956 | 121.962
2357.7344 | 122.0398 | -121.9116 | 0.1236 | -0.0060272 | -0.0030697 | 0.054549 | 0.054549 | 0.00043159 | -0.0087607 | -0.0027621 | -0.0082093 | 0.011984 | 0.0016556 | 0.0058811 | -0.014578 | 0.021149 | -0.0001432 | -5.5939 | 0 | -122.0352 | -0.09613 | -121.2753 | -121.9803 | -122.0032 | -0.086975 | 0.054932 | -0.14191 | -0.07782 | 0.045776 | -0.045776 | 0.022888 | -0.1236 | -0.1236 | -0.21973 | 0.63629 | -0.091553 | -0.068665 | 0.032043 | 0.054931 | 121.7697 | -0.068664 | -0.20142 | 121.9574 | 121.9345 | 121.8658 | 0.16479 | 0.096131 | 0.75989 | 121.9391 | 0.18768 | 0.064087 | 122.0352 | 0.19684 | 121.9116 | 121.9666 | -122.1588 | -0.2655 | 121.8155 | 121.8338 | 116.3177 | 121.8246
2359.4844 | 122.2092 | -121.8613 | 0.059509 | -0.0060272 | -0.0041379 | 0.055189 | 0.052412 | 4.192e-06 | -0.0098287 | -0.0042575 | -0.0051575 | 0.010489 | 0.0033646 | 0.0075901 | -0.016073 | 0.020081 | -0.0003568 | -5.6305 | -0.045776 | -121.9711 | 0.050354 | -121.106 | -121.8567 | -121.8613 | 0.1236 | 0.004578 | -0.091553 | 0.073242 | 0.20599 | 0.10529 | 0.12817 | -0.10986 | -0.10528 | -0.009155 | 0.75531 | 0 | 0.004578 | 0.10986 | 0.11444 | 121.7697 | -0.054931 | 0.013733 | 122.0673 | 121.9894 | 121.9666 | 0.21973 | 0.19684 | 0.86517 | 122.0215 | 0.29755 | 0.16479 | 121.9254 | 0.096131 | 121.8155 | 121.8658 | -122.0306 | -0.15106 | 121.9116 | 121.9345 | 116.2308 | 121.9849
2361.1719 | 122.0673 | -121.9116 | 0.091553 | -0.013657 | -0.0034971 | 0.055189 | 0.052626 | -0.00063661 | -0.0094015 | -0.0016941 | -0.0082093 | 0.013052 | 0.0027236 | 0.0011813 | -0.015005 | 0.021149 | 0.0011386 | -5.6671 | -0.027466 | -121.994 | 0.004578 | -121.1792 | -121.907 | -121.9254 | 0.018311 | 0.027466 | -0.10986 | -0.032043 | 0.09613 | 0.013733 | 0.041199 | -0.082398 | -0.11902 | -0.086975 | 0.73242 | -0.013733 | 0.004578 | 0.068665 | 0.086976 | 121.8018 | -0.064087 | -0.1236 | 122.0078 | 121.9528 | 121.9254 | 0.15106 | 0.1236 | 0.81482 | 121.9986 | 0.20599 | 0.07782 | 121.9666 | 0.13733 | 121.8842 | 121.9391 | -122.0856 | -0.20142 | 121.9162 | 121.8796 | 116.2445 | 121.9299
2362.9375 | 122.0901 | -121.8933 | 0.11444 | -0.013657 | 0.0014163 | 0.05284 | 0.057112 | 0.0021406 | -0.0085471 | -0.0042575 | -0.0082093 | 0.013052 | 0.0029372 | 0.0054537 | -0.013937 | 0.02243 | -0.0005704 | -5.7632 | -0.018311 | -122.0169 | -0.059509 | -121.2479 | -121.9574 | -121.9986 | -0.041199 | 0.045776 | -0.12817 | -0.009155 | 0.082397 | 0 | 0.068665 | -0.1236 | -0.13275 | -0.17395 | 0.64545 | -0.10529 | -0.064086 | 0.018311 | 0.05951 | 121.7651 | -0.068665 | -0.1236 | 121.9757 | 121.962 | 121.8933 | 0.19684 | 0.12817 | 0.76904 | 121.9574 | 0.21057 | 0.11902 | 121.9986 | 0.17395 | 121.875 | 121.9391 | -122.1313 | -0.24262 | 121.8338 | 121.8842 | 116.1301 | 121.8521
2364.6875 | 122.1451 | -121.9116 | 0.07782 | -0.0060272 | 0.0024845 | 0.054549 | 0.052412 | -0.003841 | -0.0094015 | -0.0042575 | -0.0051575 | 0.010062 | 0.004219 | 0.0067355 | -0.013082 | 0.021576 | -0.0005704 | -5.9235 | -0.032043 | -121.9849 | 0 | -121.2021 | -121.9391 | -121.9391 | 0.018311 | 0.009155 | -0.11902 | 0 | 0.10529 | 0.032043 | 0.086975 | -0.073242 | -0.10986 | -0.07782 | 0.70953 | -0.027466 | -0.027466 | 0.045776 | 0.045776 | 121.7926 | -0.068665 | -0.07782 | 122.0169 | 121.9986 | 121.9437 | 0.20599 | 0.15106 | 0.78278 | 121.9849 | 0.22431 | 0.11902 | 121.9528 | 0.12817 | 121.8796 | 121.9208 | -122.0627 | -0.19684 | 121.9116 | 121.9116 | 115.9882 | 121.9299
2366.375 | 122.1405 | -121.9025 | 0.07782 | 0.0016023 | -0.0020017 | 0.054335 | 0.052626 | -0.0053362 | -0.0070517 | -0.0040439 | -0.0021057 | 0.012625 | 0.001442 | 0.0054537 | -0.014578 | 0.020508 | -0.0003568 | -5.8594 | -0.050354 | -121.9803 | 0.054932 | -121.138 | -121.9116 | -121.8933 | 0.082397 | 0.013733 | -0.11902 | 0.032043 | 0.16022 | 0.059509 | 0.10071 | -0.07782 | -0.12817 | -0.022888 | 0.76447 | 0.009155 | -0.009155 | 0.086975 | 0.068665 | 121.7834 | -0.064087 | -0.045777 | 122.0627 | 122.0032 | 121.962 | 0.21973 | 0.17853 | 0.84229 | 122.0352 | 0.27924 | 0.15106 | 121.9299 | 0.13275 | 121.8521 | 121.9162 | -122.0581 | -0.19684 | 121.9574 | 121.9345 | 116.0431 | 121.9849
2368.125 | 122.1771 | -121.8704 | 0.073242 | -0.013657 | 0.0016299 | 0.055403 | 0.054976 | -0.0023456 | -0.0096151 | -0.0034031 | -0.0021057 | 0.013266 | 0.0012282 | 0.0011813 | -0.013937 | 0.020721 | -0.005911 | -6.0562 | -0.036621 | -121.9803 | 0.027466 | -121.1929 | -121.9437 | -121.9345 | 0.10071 | 0.004578 | -0.091553 | 0.073242 | 0.17853 | 0.059509 | 0.14191 | -0.10986 | -0.10986 | -0.045776 | 0.67749 | -0.064087 | -0.073243 | 0.045777 | 0.036621 | 121.7789 | -0.068664 | 0 | 122.049 | 122.0123 | 121.9299 | 0.23346 | 0.15106 | 0.78735 | 122.0078 | 0.27008 | 0.16479 | 121.9437 | 0.096131 | 121.8338 | 121.875 | -122.0535 | -0.16479 | 121.8979 | 121.9437 | 115.8142 | 121.9711
2369.875 | 122.0764 | -121.962 | 0.10529 | 0.0016023 | -0.0032833 | 0.055617 | 0.053694 | -0.0017048 | -0.0094015 | -0.0040439 | -0.0051575 | 0.014334 | 0.003151 | 0.011222 | -0.013723 | 0.020935 | 0.0019932 | -6.0791 | -0.013733 | -122.0535 | -0.07782 | -121.2753 | -122.0078 | -122.0261 | -0.064087 | 0.045776 | -0.13275 | -0.073242 | 0.041199 | -0.036621 | 0.027466 | -0.091553 | -0.11902 | -0.18311 | 0.68664 | -0.064087 | -0.045776 | 0.027466 | 0.045777 | 121.8292 | -0.05951 | -0.17853 | 122.0032 | 121.9894 | 121.9254 | 0.16022 | 0.09613 | 0.7782 | 121.9757 | 0.17395 | 0.059509 | 122.0398 | 0.17853 | 121.9482 | 122.0078 | -122.1588 | -0.23804 | 121.8842 | 121.8887 | 115.8829 | 121.8979
2371.5625 | 122.113 | -121.9162 | 0.09613 | -0.013657 | 0.0018435 | 0.054976 | 0.057326 | 0.0021406 | -0.0072653 | -0.0029759 | -0.0051575 | 0.013266 | 0.0044326 | 0.0097263 | -0.015432 | 0.020508 | -0.0012112 | -6.221 | -0.018311 | -122.0261 | -0.068665 | -121.2936 | -122.0306 | -122.0398 | -0.013733 | 0.036621 | -0.11902 | 0 | 0.082397 | -0.009155 | 0.068665 | -0.10986 | -0.11444 | -0.16479 | 0.62256 | -0.1236 | -0.11444 | -0.013733 | -0.004578 | 121.7972 | -0.059509 | -0.09613 | 121.9986 | 121.9849 | 121.907 | 0.18768 | 0.10986 | 0.73242 | 121.9574 | 0.20142 | 0.11902 | 122.0078 | 0.15564 | 121.8979 | 121.9528 | -122.1222 | -0.21515 | 121.8475 | 121.9162 | 115.6952 | 121.9025
2373.3125 | 122.2 | -121.9162 | 0.068665 | 0.0016023 | -0.0020017 | 0.054762 | 0.051985 | 0.0025678 | -0.0089743 | -0.0036167 | -0.0051575 | 0.011343 | 0.0020828 | 0.0045993 | -0.015646 | 0.019653 | 0.0002842 | -6.1707 | -0.041199 | -122.0123 | 0.059509 | -121.1197 | -121.8842 | -121.8887 | 0.14648 | -0.009155 | -0.086975 | 0.059509 | 0.21057 | 0.10071 | 0.1236 | -0.09613 | -0.10986 | -0.009156 | 0.79651 | 0.027466 | 0.032044 | 0.1236 | 0.12817 | 121.8292 | -0.07782 | -0.009156 | 122.1268 | 122.0398 | 122.0169 | 0.21057 | 0.18768 | 0.89264 | 122.0718 | 0.29755 | 0.14648 | 121.9711 | 0.07782 | 121.875 | 121.907 | -122.081 | -0.15564 | 121.9757 | 121.9757 | 115.7455 | 122.0627
2375.0781 | 122.0764 | -121.9482 | 0.11444 | 0.0016023 | -0.0030697 | 0.053267 | 0.051772 | -0.003841 | -0.01047 | -0.0038303 | -0.0051575 | 0.012839 | 0.0037918 | 0.010581 | -0.015646 | 0.022858 | 0.0028476 | -6.2805 | 0.009155 | -122.0123 | -0.082397 | -121.2982 | -122.0215 | -122.0352 | -0.059509 | 0.054932 | -0.12817 | -0.064087 | 0.050354 | -0.041199 | 0.036621 | -0.064087 | -0.10529 | -0.19684 | 0.65002 | -0.086975 | -0.073242 | -0.022888 | -0.009155 | 121.8201 | -0.059509 | -0.17853 | 121.9986 | 121.9849 | 121.907 | 0.1648 | 0.086975 | 0.71411 | 121.9299 | 0.17853 | 0.064087 | 122.0215 | 0.18311 | 121.9574 | 122.0032 | -122.1268 | -0.24262 | 121.8658 | 121.8842 | 115.6677 | 121.8887
2376.7656 | 122.0718 | -121.9345 | 0.09613 | -0.021286 | 0.0003483 | 0.053694 | 0.055189 | -0.0027728 | -0.0079061 | -0.0012669 | 0.0009461 | 0.013693 | 0.0040054 | 0.0080173 | -0.0098779 | 0.016022 | 0.0007114 | -6.34 | -0.018311 | -122.0535 | -0.022888 | -121.2433 | -122.0078 | -122.0261 | -0.013733 | 0.041199 | -0.11444 | -0.018311 | 0.059509 | -0.045776 | 0.045776 | -0.11902 | -0.11444 | -0.11902 | 0.69122 | -0.091553 | -0.073242 | 0.027466 | 0.045777 | 121.8201 | -0.054931 | -0.11444 | 121.994 | 121.9803 | 121.8887 | 0.16022 | 0.068665 | 0.81024 | 122.0306 | 0.17395 | 0.09613 | 122.0352 | 0.15564 | 121.9162 | 121.9757 | -122.1497 | -0.21057 | 121.9116 | 121.9162 | 115.5945 | 121.9208
2378.5156 | 122.0764 | -121.9345 | 0.10986 | -0.0060272 | 0.0022709 | 0.054762 | 0.054976 | -0.00020941 | -0.0070517 | -0.0025485 | 0.0009461 | 0.013266 | 0.0037918 | 0.0090853 | -0.014578 | 0.022003 | -0.0005704 | -6.5002 | -0.018311 | -122.0627 | -0.086975 | -121.3577 | -122.0947 | -122.0581 | -0.073242 | 0.050354 | -0.11444 | -0.045776 | 0.022888 | -0.068665 | 0.022888 | -0.12817 | -0.12817 | -0.19684 | 0.57678 | -0.1236 | -0.16022 | 0.004578 | -0.032044 | 121.8201 | -0.059509 | -0.15564 | 121.9574 | 121.9574 | 121.8658 | 0.13733 | 0.045776 | 0.70496 | 121.9757 | 0.13733 | 0.068665 | 122.0444 | 0.16479 | 121.9162 | 121.9849 | -122.1725 | -0.2243 | 121.8475 | 121.8887 | 115.4343 | 121.8613
2380.2031 | 122.1817 | -121.9208 | 0.086975 | -0.013657 | 0.0001345 | 0.053908 | 0.051344 | -0.00042301 | -0.0096151 | -0.0038303 | -0.0082093 | 0.010489 | 0.0016556 | 0.0037447 | -0.012014 | 0.018799 | 0.002634 | -6.5231 | -0.022888 | -122.0352 | -0.004578 | -121.2341 | -121.9528 | -121.9528 | 0.032043 | 0.009155 | -0.091553 | 0.041199 | 0.16937 | 0.07782 | 0.10986 | -0.11444 | -0.10986 | -0.091553 | 0.68664 | -0.032044 | -0.032044 | 0.082397 | 0.082397 | 121.8292 | -0.07782 | -0.045776 | 122.0901 | 122.0306 | 121.9986 | 0.20142 | 0.16937 | 0.80109 | 122.0306 | 0.26093 | 0.13275 | 122.0123 | 0.10071 | 121.8979 | 121.9299 | -122.1222 | -0.17853 | 121.9162 | 121.962 | 115.3976 | 121.9528
2381.9531 | 122.0535 | -121.9345 | 0.11902 | -0.0060272 | 0.0035525 | 0.054121 | 0.054762 | 0.0042768 | -0.0087607 | -0.0066073 | -0.0021057 | 0.014975 | 0.0022964 | 0.0063083 | -0.014364 | 0.022003 | -0.0031338 | -6.633 | -0.004578 | -122.049 | -0.091553 | -121.3531 | -122.0581 | -122.0901 | -0.086975 | 0.045776 | -0.11444 | -0.054932 | 0.022888 | -0.073242 | 0.032043 | -0.11444 | -0.1236 | -0.21057 | 0.58136 | -0.15564 | -0.1236 | -0.041199 | -0.009155 | 121.8201 | -0.073243 | -0.17395 | 121.9574 | 121.9666 | 121.8613 | 0.14648 | 0.041199 | 0.6958 | 121.9574 | 0.13733 | 0.059509 | 122.0444 | 0.16022 | 121.9299 | 121.9803 | -122.168 | -0.23346 | 121.843 | 121.8796 | 115.3015 | 121.8475
2383.7188 | 122.0901 | -121.962 | 0.10071 | -0.0060272 | -0.0009335 | 0.055617 | 0.051985 | -0.00063661 | -0.011324 | -0.0036167 | -0.011261 | 0.011984 | 0.00251 | 0.0067355 | -0.013082 | 0.020294 | -0.0009976 | -6.6101 | -0.009155 | -122.0352 | -0.050354 | -121.2799 | -121.9986 | -122.0261 | -0.036621 | 0.054932 | -0.11444 | -0.073242 | 0.059509 | -0.022888 | 0.036621 | -0.073242 | -0.10986 | -0.15106 | 0.68207 | -0.064087 | -0.036621 | 0.009155 | 0.036621 | 121.8475 | -0.045776 | -0.17395 | 122.0215 | 121.9986 | 121.9391 | 0.15106 | 0.091553 | 0.75531 | 121.9849 | 0.17395 | 0.041199 | 122.0261 | 0.16937 | 121.9528 | 122.0169 | -122.1359 | -0.21515 | 121.9116 | 121.8887 | 115.3519 | 121.9254
2385.4844 | 122.1451 | -121.9116 | 0.10071 | 0.0016023 | -0.0007199 | 0.05284 | 0.051985 | 0.001286 | -0.0085471 | -0.0014805 | -0.0051575 | 0.011984 | 0.003151 | 0.00011332 | -0.013937 | 0.020721 | 0.0019932 | -6.6559 | -0.041199 | -122.049 | 0.018311 | -121.1929 | -121.9345 | -121.9528 | 0.027466 | 0.032043 | -0.10071 | -0.018311 | 0.10529 | 0.027466 | 0.068665 | -0.13733 | -0.14191 | -0.082397 | 0.71869 | -0.041199 | -0.022888 | 0.09613 | 0.11444 | 121.8109 | -0.068665 | -0.11902 | 122.0169 | 121.9803 | 121.9391 | 0.16937 | 0.12817 | 0.85602 | 122.0673 | 0.20599 | 0.082397 | 122.0078 | 0.13275 | 121.8704 | 121.9437 | -122.1497 | -0.20142 | 121.9299 | 121.8933 | 115.2557 | 121.9391
2387.2344 | 122.1039 | -121.9711 | 0.09613 | -0.013657 | -0.0002927 | 0.056471 | 0.05284 | -0.0010638 | -0.0083335 | -0.0021213 | -0.0051575 | 0.011557 | 0.0016556 | 0.010154 | -0.01415 | 0.020721 | 0.0002842 | -6.7749 | -0.004578 | -122.0581 | -0.068665 | -121.2799 | -122.0215 | -122.0444 | -0.050354 | 0.059509 | -0.11444 | -0.064087 | 0.050354 | -0.036621 | 0.022888 | -0.086975 | -0.10071 | -0.16479 | 0.69122 | -0.073243 | -0.050354 | 0.013732 | 0.036621 | 121.8567 | -0.036621 | -0.16022 | 122.0215 | 121.994 | 121.9345 | 0.13733 | 0.07782 | 0.7782 | 121.9894 | 0.16479 | 0.050354 | 122.0535 | 0.17395 | 121.9666 | 122.0306 | -122.1542 | -0.21057 | 121.9025 | 121.907 | 115.1962 | 121.9208
2388.9219 | 122.2275 | -121.9162 | 0.064087 | -0.0060272 | 0.0001345 | 0.055617 | 0.05284 | -0.0017048 | -0.0079061 | -0.0036167 | -0.0021057 | 0.010702 | 0.0027236 | 0.0022495 | -0.01351 | 0.022644 | -0.0018522 | -6.7978 | -0.041199 | -122.0261 | 0.050354 | -121.138 | -121.8933 | -121.9162 | 0.11902 | 0.018311 | -0.086975 | 0.068665 | 0.19684 | 0.10986 | 0.13275 | -0.10986 | -0.10529 | -0.013733 | 0.7782 | 0 | 0.022888 | 0.10986 | 0.13275 | 121.8292 | -0.045776 | 0.004578 | 122.113 | 122.049 | 122.0261 | 0.21973 | 0.19684 | 0.88806 | 122.0764 | 0.28381 | 0.15564 | 121.9849 | 0.10529 | 121.875 | 121.9345 | -122.0901 | -0.15106 | 121.9666 | 121.9849 | 115.1184 | 122.0352
2390.6719 | 122.1771 | -121.9345 | 0.09613 | -0.0060272 | -0.0020017 | 0.056044 | 0.05284 | -0.00042301 | -0.0098287 | -0.0019077 | -0.0021057 | 0.011557 | -5.3368e-05 | 0.01229 | -0.015005 | 0.018799 | 0.0004978 | -6.8802 | -0.054932 | -122.0261 | 0.050354 | -121.1838 | -121.9254 | -121.9437 | 0.059509 | 0.013733 | -0.09613 | 0.018311 | 0.14648 | 0.064087 | 0.09613 | -0.091553 | -0.15106 | -0.045776 | 0.75073 | -0.009156 | 0.009155 | 0.082397 | 0.10071 | 121.8384 | -0.082397 | -0.077819 | 122.081 | 122.0306 | 121.9986 | 0.19226 | 0.16022 | 0.84228 | 122.0764 | 0.24261 | 0.11444 | 121.9711 | 0.10986 | 121.8796 | 121.9482 | -122.1222 | -0.19226 | 121.9849 | 121.9528 | 115.0543 | 121.994
2392.4219 | 122.0901 | -121.9437 | 0.10986 | -0.013657 | 0.0022709 | 0.053694 | 0.057326 | 0.0017132 | -0.010043 | -0.0034031 | -0.0021057 | 0.015829 | 0.0035782 | 0.0090853 | -0.014364 | 0.020935 | 0.000925 | -7.045 | -0.018311 | -122.0535 | -0.036621 | -121.2936 | -122.0581 | -122.0581 | -0.027466 | 0.036621 | -0.11902 | -0.050354 | 0.045776 | -0.050354 | 0.022888 | -0.10986 | -0.12817 | -0.14648 | 0.65002 | -0.11444 | -0.11444 | -0.004577 | -0.004577 | 121.8246 | -0.073242 | -0.16022 | 121.9894 | 121.9666 | 121.8933 | 0.14191 | 0.068665 | 0.75989 | 122.0169 | 0.16479 | 0.068665 | 122.0352 | 0.15564 | 121.9254 | 121.9803 | -122.1634 | -0.22888 | 121.907 | 121.8933 | 114.8987 | 121.9162
2394.1719 | 122.2 | -121.962 | 0.07782 | -0.013657 | -0.0009335 | 0.053694 | 0.051558 | -0.0025592 | -0.010256 | -0.0051121 | -0.0021057 | 0.011343 | 0.0022964 | 0.0050265 | -0.014578 | 0.020081 | -0.0027066 | -7.1365 | -0.022888 | -122.0398 | -0.013733 | -121.2433 | -121.994 | -121.9986 | 0.027466 | 0.022888 | -0.09613 | 0.027466 | 0.15106 | 0.068665 | 0.10986 | -0.07782 | -0.10071 | -0.091553 | 0.71869 | -0.036621 | -0.032044 | 0.041199 | 0.045776 | 121.8658 | -0.054932 | -0.050354 | 122.113 | 122.0718 | 122.0306 | 0.20599 | 0.16479 | 0.79651 | 122.0261 | 0.24719 | 0.1236 | 122.0169 | 0.11902 | 121.9391 | 121.9849 | -122.1176 | -0.17395 | 121.9482 | 121.9894 | 114.8254 | 121.9894
2395.8594 | 122.1497 | -121.9528 | 0.10986 | -0.013657 | -0.0020017 | 0.057112 | 0.05583 | 0.0034222 | -0.0072653 | -0.0021213 | -0.0021057 | 0.013266 | 0.0020828 | 0.0092989 | -0.015005 | 0.016876 | -0.0014248 | -7.1548 | -0.022888 | -122.0856 | -0.018311 | -121.2479 | -121.9894 | -122.0215 | 0.036621 | 0.045776 | -0.11444 | 0.009155 | 0.10529 | 0.009155 | 0.082397 | -0.13275 | -0.13275 | -0.12817 | 0.70496 | -0.068664 | -0.036621 | 0.064087 | 0.09613 | 121.8384 | -0.064087 | -0.10071 | 122.0581 | 122.0352 | 121.962 | 0.19684 | 0.1236 | 0.83771 | 122.0673 | 0.21973 | 0.1236 | 122.0627 | 0.16022 | 121.9299 | 121.9986 | -122.1954 | -0.2243 | 121.9345 | 121.962 | 114.798 | 121.9894
2397.6094 | 122.0901 | -121.9711 | 0.1236 | -0.013657 | 0.0026981 | 0.056471 | 0.053267 | 0.0027814 | -0.0089743 | -0.0040439 | -0.0021057 | 0.012839 | 0.00251 | 0.0069491 | -0.012869 | 0.023071 | -0.0012112 | -7.2922 | -0.022888 | -122.0627 | -0.059509 | -121.3348 | -122.081 | -122.0993 | -0.073242 | 0.041199 | -0.10986 | -0.050354 | 0.022888 | -0.059509 | 0.032043 | -0.091553 | -0.14648 | -0.1831 | 0.63629 | -0.12817 | -0.10986 | -0.036621 | -0.018311 | 121.8613 | -0.082397 | -0.17395 | 121.994 | 122.0032 | 121.9116 | 0.14191 | 0.050354 | 0.72784 | 122.0032 | 0.13275 | 0.059509 | 122.0398 | 0.15106 | 121.9482 | 122.0123 | -122.1863 | -0.23346 | 121.9116 | 121.9208 | 114.679 | 121.8979
2399.2969 | 122.1085 | -121.9849 | 0.10071 | 0.0016023 | -0.0017881 | 0.054762 | 0.054762 | 0.0017132 | -0.0089743 | -0.0038303 | -0.0051575 | 0.01412 | 0.0044326 | 0.00032692 | -0.013082 | 0.020721 | -0.0005704 | -7.3792 | 0.009155 | -122.0993 | -0.086975 | -121.3257 | -122.0398 | -122.0718 | -0.059509 | 0.059509 | -0.12817 | -0.064087 | 0.041199 | -0.027466 | 0.022888 | -0.11444 | -0.091553 | -0.18768 | 0.65918 | -0.086975 | -0.054932 | 0.027466 | 0.059509 | 121.8567 | -0.041199 | -0.1648 | 122.0261 | 122.0078 | 121.9574 | 0.15106 | 0.10071 | 0.77362 | 122.0123 | 0.16937 | 0.064087 | 122.1085 | 0.18768 | 121.994 | 122.0444 | -122.2 | -0.22888 | 121.8979 | 121.9208 | 114.6057 | 121.9254
2401.0625 | 122.2366 | -121.9116 | 0.054932 | -0.0060272 | 0.0026981 | 0.056685 | 0.054762 | -0.00042301 | -0.0085471 | -0.0038303 | -0.0082093 | 0.011984 | 0.0012282 | -0.0026639 | -0.01415 | 0.022003 | 0.0013522 | -7.4661 | -0.041199 | -122.0306 | 0.050354 | -121.1929 | -121.9666 | -121.9711 | 0.11444 | 0.004578 | -0.07782 | 0.09613 | 0.17853 | 0.091553 | 0.15564 | -0.11902 | -0.096131 | -0.004578 | 0.71869 | -0.059509 | -0.054932 | 0.05951 | 0.064087 | 121.8338 | -0.050354 | 0.041198 | 122.0901 | 122.0673 | 122.0032 | 0.23346 | 0.16937 | 0.83771 | 122.081 | 0.25635 | 0.17395 | 121.9894 | 0.082398 | 121.8704 | 121.9162 | -122.0856 | -0.13275 | 121.962 | 122.0078 | 114.4455 | 122.0261
2402.75 | 122.2275 | -121.9254 | 0.059509 | -0.013657 | 0.0016299 | 0.056258 | 0.053694 | -0.0025592 | -0.0053427 | -0.0021213 | -0.0082093 | 0.011557 | 0.0035782 | 0.0054537 | -0.013937 | 0.022217 | 0.0019932 | -7.5577 | -0.045776 | -122.0306 | 0.045776 | -121.1884 | -121.9528 | -121.9437 | 0.10071 | 0.013733 | -0.082397 | 0.073242 | 0.18768 | 0.086975 | 0.12817 | -0.10529 | -0.10528 | -0.013733 | 0.737 | -0.018311 | -0.027466 | 0.086975 | 0.07782 | 121.843 | -0.045776 | 0.013733 | 122.113 | 122.0535 | 122.0123 | 0.21057 | 0.16937 | 0.84229 | 122.0764 | 0.27008 | 0.15564 | 121.9849 | 0.09613 | 121.8796 | 121.9391 | -122.0901 | -0.14191 | 121.9711 | 121.9986 | 114.3677 | 122.0261
2404.5 | 122.2412 | -121.8979 | 0.073242 | 0.0016023 | -0.0041379 | 0.054121 | 0.051558 | 0.00043159 | -0.0087607 | -0.0059665 | -0.0051575 | 0.012198 | 0.0018692 | 0.00032692 | -0.015005 | 0.022003 | -0.0022794 | -7.5668 | -0.032043 | -122.0535 | 0.068665 | -121.1334 | -121.9162 | -121.9391 | 0.10529 | 0.018311 | -0.073242 | 0.064087 | 0.19684 | 0.11444 | 0.13275 | -0.15564 | -0.10529 | -0.004577 | 0.76447 | -0.041199 | -0.018311 | 0.11444 | 0.13733 | 121.8246 | -0.054931 | -0.009155 | 122.0947 | 122.0306 | 122.0123 | 0.20599 | 0.18768 | 0.92011 | 122.1222 | 0.27008 | 0.13733 | 122.0215 | 0.091553 | 121.8658 | 121.9162 | -122.1268 | -0.14648 | 121.9666 | 121.962 | 114.3311 | 122.0032
2406.2031 | 122.1588 | -121.9437 | 0.091553 | 0.0016023 | -0.0011471 | 0.054762 | 0.054976 | -0.00020941 | -0.0087607 | -0.00083947 | -0.0021057 | 0.014548 | 0.0046462 | 0.013572 | -0.016714 | 0.021576 | 0.0004978 | -7.6813 | -0.018311 | -122.0764 | -0.018311 | -121.2662 | -122.0215 | -122.049 | 0.027466 | 0.032043 | -0.10986 | 0.018311 | 0.10986 | 0.009155 | 0.086975 | -0.13275 | -0.10986 | -0.10986 | 0.67749 | -0.10529 | -0.077819 | 0.027466 | 0.054932 | 121.8338 | -0.05951 | -0.073242 | 122.0535 | 122.0306 | 121.9528 | 0.19684 | 0.11902 | 0.81024 | 122.0581 | 0.21973 | 0.12817 | 122.0581 | 0.14191 | 121.9254 | 121.9757 | -122.168 | -0.20142 | 121.9254 | 121.962 | 114.2624 | 121.9711
2407.9531 | 122.1542 | -121.9849 | 0.10071 | 0.0016023 | -0.0024289 | 0.055189 | 0.05348 | 0.00021799 | -0.0096151 | -0.0023349 | -0.0051575 | 0.015829 | 0.0063552 | 0.0095127 | -0.014578 | 0.02179 | 0.0022068 | -7.8278 | -0.009155 | -122.0947 | -0.091553 | -121.3394 | -122.0535 | -122.081 | -0.054932 | 0.059509 | -0.10529 | -0.054932 | 0.086975 | -0.018311 | 0.041199 | -0.10986 | -0.10986 | -0.19226 | 0.64545 | -0.096131 | -0.068665 | 0.013733 | 0.041199 | 121.8796 | -0.041199 | -0.15564 | 122.0718 | 122.0261 | 121.9666 | 0.14649 | 0.086975 | 0.75531 | 122.0032 | 0.19226 | 0.050354 | 122.0856 | 0.16479 | 121.9757 | 122.0444 | -122.1954 | -0.20599 | 121.8933 | 121.9299 | 114.1571 | 121.9299
2409.7031 | 122.2504 | -121.9345 | 0.068665 | -0.013657 | 0.0005619 | 0.054121 | 0.052412 | 4.192e-06 | -0.0083335 | -0.0044711 | -0.0082093 | 0.010916 | 0.003151 | 0.0052401 | -0.012441 | 0.02179 | 0.0013522 | -7.9422 | -0.045776 | -122.0306 | 0.036621 | -121.2067 | -121.9849 | -121.9803 | 0.091553 | -0.004578 | -0.073242 | 0.086975 | 0.16479 | 0.073242 | 0.14191 | -0.096131 | -0.11444 | -0.032044 | 0.72784 | -0.045777 | -0.050354 | 0.050354 | 0.045777 | 121.8613 | -0.073243 | 0.01831 | 122.0993 | 122.0764 | 122.0078 | 0.21515 | 0.14648 | 0.82398 | 122.0673 | 0.23804 | 0.16022 | 121.9849 | 0.068664 | 121.8887 | 121.9299 | -122.0993 | -0.14191 | 121.9711 | 122.0215 | 113.9923 | 122.0261
2411.4688 | 122.2504 | -121.9666 | 0.07782 | -0.013657 | -0.0026425 | 0.053267 | 0.050063 | 0.0025678 | -0.0091879 | -0.0034031 | -0.0082093 | 0.011984 | 0.00251 | 0.0035311 | -0.016287 | 0.018585 | 0.0013522 | -8.02 | -0.041199 | -122.0535 | 0.022888 | -121.2021 | -121.9711 | -121.9574 | 0.086975 | 0.022888 | -0.09613 | 0.068665 | 0.20599 | 0.10986 | 0.12817 | -0.086975 | -0.11902 | -0.054932 | 0.76447 | 0.009156 | -0.004577 | 0.096131 | 0.082398 | 121.8704 | -0.054932 | -0.009155 | 122.1725 | 122.0947 | 122.0764 | 0.2243 | 0.20599 | 0.85144 | 122.0764 | 0.30212 | 0.16479 | 122.0123 | 0.11902 | 121.9254 | 121.9894 | -122.1313 | -0.17395 | 121.9894 | 122.0352 | 113.9465 | 122.0535
2413.2188 | 122.1039 | -121.9849 | 0.11444 | -0.021286 | 0.0033389 | 0.055189 | 0.054121 | 0.0010724 | -0.0064109 | -0.0025485 | -0.0021057 | 0.01412 | 0.0048598 | 0.0060947 | -0.013723 | 0.022003 | 0.0007114 | -8.1802 | 0 | -122.0764 | -0.086975 | -121.3577 | -122.1039 | -122.0993 | -0.068665 | 0.045776 | -0.11444 | -0.059509 | 0.004578 | -0.082397 | 0.022888 | -0.091553 | -0.11444 | -0.20142 | 0.62714 | -0.11444 | -0.11902 | -0.022888 | -0.027466 | 121.8704 | -0.068665 | -0.17395 | 121.9894 | 122.0078 | 121.9025 | 0.13733 | 0.032044 | 0.71869 | 121.9894 | 0.11902 | 0.054932 | 122.0764 | 0.16022 | 121.9849 | 122.0306 | -122.1909 | -0.22888 | 121.8979 | 121.9254 | 113.8046 | 121.9162
2414.9688 | 122.2778 | -121.9437 | 0.07782 | -0.0060272 | -0.0041379 | 0.053694 | 0.050703 | -0.0029864 | -0.0081197 | -0.0014805 | -0.0051575 | 0.01113 | 0.0035782 | 0.0037447 | -0.014364 | 0.020935 | -0.0037748 | -8.1894 | -0.041199 | -122.0627 | 0.045776 | -121.1746 | -121.9299 | -121.9528 | 0.12817 | 0.013733 | -0.068665 | 0.082397 | 0.21973 | 0.1236 | 0.16022 | -0.11902 | -0.11902 | -0.032044 | 0.76904 | -0.009155 | 0.013733 | 0.10986 | 0.13275 | 121.875 | -0.064087 | 0.004577 | 122.1634 | 122.1039 | 122.0673 | 0.22888 | 0.19226 | 0.88806 | 122.1085 | 0.28839 | 0.15106 | 122.0215 | 0.082398 | 121.9025 | 121.9574 | -122.1405 | -0.14649 | 121.9894 | 122.0261 | 113.7543 | 122.0718
2416.6562 | 122.1634 | -121.994 | 0.10986 | 0.0016023 | -0.0039243 | 0.056044 | 0.054549 | -0.0029864 | -0.0094015 | -0.0016941 | 0.0009461 | 0.01412 | 0.003151 | 0.0097263 | -0.015219 | 0.02243 | 0.0002842 | -8.3267 | -0.013733 | -122.0993 | -0.082397 | -121.3394 | -122.0673 | -122.081 | -0.059509 | 0.036621 | -0.10986 | -0.045776 | 0.064087 | -0.018311 | 0.059509 | -0.10529 | -0.1236 | -0.19226 | 0.6546 | -0.086975 | -0.073242 | 0.01831 | 0.032043 | 121.8842 | -0.073242 | -0.15564 | 122.0581 | 122.0535 | 121.9757 | 0.16937 | 0.091552 | 0.75989 | 122.0169 | 0.17395 | 0.064087 | 122.0856 | 0.14648 | 121.9803 | 122.0306 | -122.2092 | -0.21973 | 121.9116 | 121.9482 | 113.6673 | 121.9345
2418.3438 | 122.2275 | -121.9894 | 0.068665 | 0.0016023 | -0.0026425 | 0.055189 | 0.05049 | -0.0012774 | -0.0091879 | -0.0034031 | -0.0051575 | 0.012411 | 0.0040054 | 0.0013949 | -0.015646 | 0.020721 | 0.0002842 | -8.3817 | -0.045776 | -122.0627 | 0.045776 | -121.1929 | -121.9391 | -121.962 | 0.082397 | 0.022888 | -0.10071 | 0.041199 | 0.1831 | 0.086975 | 0.1236 | -0.073242 | -0.11444 | -0.022889 | 0.79651 | 0.027466 | 0.050354 | 0.10071 | 0.1236 | 121.8887 | -0.045777 | -0.027466 | 122.1725 | 122.113 | 122.0764 | 0.2243 | 0.18768 | 0.86975 | 122.1085 | 0.28381 | 0.14191 | 122.0169 | 0.1236 | 121.9437 | 122.0123 | -122.1313 | -0.16937 | 122.0352 | 122.0306 | 113.6078 | 122.0718
2420.0938 | 122.2687 | -121.9254 | 0.059509 | -0.021286 | 0.0014163 | 0.055403 | 0.053053 | 0.0034222 | -0.0061971 | -0.0051121 | -0.0051575 | 0.013693 | 0.0027236 | 0.012076 | -0.016287 | 0.022003 | -0.0046292 | -8.5785 | -0.045776 | -122.0535 | 0.050354 | -121.1838 | -121.9849 | -121.9757 | 0.10071 | 0.022888 | -0.086975 | 0.09613 | 0.17395 | 0.10071 | 0.13733 | -0.12817 | -0.10528 | -0.009155 | 0.74158 | -0.050354 | -0.059509 | 0.07782 | 0.068665 | 121.8384 | -0.036621 | 0.036621 | 122.0993 | 122.0627 | 122.0261 | 0.2243 | 0.18768 | 0.86975 | 122.1039 | 0.26092 | 0.1831 | 122.0078 | 0.10986 | 121.8796 | 121.9482 | -122.113 | -0.14648 | 121.9757 | 122.0215 | 113.3469 | 122.0261
2421.7969 | 122.3053 | -121.9574 | 0.054932 | -0.021286 | -0.0020017 | 0.056685 | 0.054121 | -0.00085021 | -0.0083335 | -0.0010531 | -0.0051575 | 0.01348 | 0.0016556 | 0.0016085 | -0.015432 | 0.021149 | -0.005911 | -8.638 | -0.041199 | -122.0901 | 0.050354 | -121.1884 | -121.9437 | -121.9711 | 0.13275 | 0.004578 | -0.10529 | 0.086975 | 0.20599 | 0.1236 | 0.12817 | -0.13275 | -0.096131 | -0.004578 | 0.76904 | -0.013733 | 0.013732 | 0.11902 | 0.14648 | 121.8521 | -0.050354 | 0.032043 | 122.1634 | 122.0856 | 122.081 | 0.23346 | 0.22888 | 0.90179 | 122.1405 | 0.31128 | 0.19226 | 122.0489 | 0.10986 | 121.9162 | 121.962 | -122.1451 | -0.16022 | 122.0078 | 122.0444 | 113.3194 | 122.0901
2423.5625 | 122.2733 | -121.9757 | 0.091553 | -0.0060272 | -0.0007199 | 0.054121 | 0.050703 | -0.0036274 | -0.010043 | -0.0019077 | 0.0009461 | 0.009848 | -5.3368e-05 | 0.00075412 | -0.016073 | 0.020935 | -0.002493 | -8.8211 | -0.041199 | -122.0627 | 0.013733 | -121.2479 | -121.9986 | -121.9894 | 0.050354 | 0.004578 | -0.10986 | 0.036621 | 0.16022 | 0.091553 | 0.11902 | -0.086975 | -0.13275 | -0.07782 | 0.72784 | -0.013733 | -0.022888 | 0.073242 | 0.064087 | 121.8658 | -0.086975 | -0.054932 | 122.1359 | 122.0947 | 122.0673 | 0.22888 | 0.20142 | 0.81482 | 122.0764 | 0.27008 | 0.14648 | 122.0215 | 0.11444 | 121.9345 | 121.9803 | -122.1542 | -0.20142 | 121.9894 | 122.0123 | 113.1546 | 122.0261
2425.25 | 122.1405 | -121.9894 | 0.11444 | -0.013657 | 0.0001345 | 0.051771 | 0.053267 | -0.0029864 | -0.0094015 | -0.0040439 | -0.0051575 | 0.01348 | 0.0033646 | 0.0050265 | -0.013296 | 0.02179 | -0.0012112 | -8.8715 | -0.018311 | -122.081 | -0.004578 | -121.2524 | -121.9757 | -122.0215 | 0 | 0.045776 | -0.10529 | -0.032043 | 0.07782 | -0.013733 | 0.041199 | -0.091553 | -0.13275 | -0.11902 | 0.737 | -0.032043 | 0.013733 | 0.05951 | 0.10529 | 121.8842 | -0.068665 | -0.14648 | 122.0673 | 122.0306 | 121.9757 | 0.14649 | 0.091553 | 0.82855 | 122.0764 | 0.18311 | 0.073243 | 122.0627 | 0.15106 | 121.9711 | 122.0352 | -122.1954 | -0.21973 | 121.9849 | 121.9574 | 113.118 | 121.9894
2427 | 122.2595 | -121.9666 | 0.07782 | -0.021286 | -0.0002927 | 0.055189 | 0.053694 | -0.001491 | -0.0085471 | -0.0012669 | -0.0051575 | 0.012198 | 0.0018692 | 0.0048129 | -0.015005 | 0.020935 | 0.0022068 | -9.082 | -0.027466 | -122.0856 | 0 | -121.2616 | -122.0032 | -122.0078 | 0.045776 | 0.009155 | -0.10071 | 0.045776 | 0.15564 | 0.086975 | 0.1236 | -0.11902 | -0.10529 | -0.07782 | 0.70496 | -0.041198 | -0.036621 | 0.07782 | 0.082397 | 121.8658 | -0.068665 | -0.032044 | 122.1222 | 122.0901 | 122.0535 | 0.2243 | 0.18768 | 0.82397 | 122.0856 | 0.25635 | 0.14648 | 122.0581 | 0.10986 | 121.9391 | 121.9757 | -122.1634 | -0.17853 | 121.9666 | 122.0123 | 112.8845 | 122.0123
2428.6875 | 122.2137 | -121.9666 | 0.068665 | -0.013657 | -0.0007199 | 0.053694 | 0.053694 | -0.001491 | -0.010683 | -0.0019077 | -0.0021057 | 0.012625 | 0.0035782 | 0.0084445 | -0.013723 | 0.020294 | -0.0020658 | -9.2194 | -0.032043 | -122.0856 | -0.022888 | -121.2845 | -122.0352 | -122.0352 | 0.009155 | 0.009155 | -0.10529 | 0.027466 | 0.12817 | 0.032043 | 0.10071 | -0.11902 | -0.10071 | -0.091553 | 0.68207 | -0.068664 | -0.068664 | 0.050354 | 0.050354 | 121.8613 | -0.05951 | -0.041199 | 122.0947 | 122.0673 | 121.9986 | 0.20599 | 0.13733 | 0.80109 | 122.0627 | 0.23346 | 0.13275 | 122.0535 | 0.11444 | 121.9345 | 121.9757 | -122.1542 | -0.17395 | 121.9437 | 121.994 | 112.7472 | 121.9757
2430.4375 | 122.1771 | -121.994 | 0.10071 | -0.0060272 | 0.0026981 | 0.055617 | 0.056258 | 0.00043159 | -0.0094015 | -0.0038303 | 0.0009461 | 0.015616 | 0.0035782 | 0.0078037 | -0.014791 | 0.023926 | -0.0027066 | -9.4254 | -0.004578 | -122.1085 | -0.07782 | -121.3669 | -122.1176 | -122.1085 | -0.032043 | 0.032043 | -0.10071 | -0.018311 | 0.050354 | -0.032043 | 0.050354 | -0.11444 | -0.10529 | -0.17853 | 0.62714 | -0.11444 | -0.1236 | 0 | -0.009156 | 121.8933 | -0.068665 | -0.11902 | 122.0444 | 122.0444 | 121.962 | 0.15106 | 0.068665 | 0.74158 | 122.0306 | 0.15106 | 0.082397 | 122.1039 | 0.13275 | 121.9894 | 122.0261 | -122.2092 | -0.20142 | 121.9162 | 121.9757 | 112.5687 | 121.962
2432.2031 | 122.1817 | -121.9894 | 0.1236 | -0.0060272 | -0.0011471 | 0.052626 | 0.056044 | -0.00042301 | -0.010043 | -0.0027621 | -0.0051575 | 0.013907 | 0.0020828 | -0.00052768 | -0.014578 | 0.022858 | -0.0009976 | -9.462 | 0.004578 | -122.1268 | -0.082397 | -121.344 | -122.0627 | -122.0901 | -0.054932 | 0.054932 | -0.11902 | -0.027466 | 0.082397 | -0.013733 | 0.059509 | -0.13733 | -0.11902 | -0.20599 | 0.64545 | -0.10071 | -0.073242 | 0.036621 | 0.064087 | 121.8704 | -0.068664 | -0.15106 | 122.0718 | 122.049 | 121.9757 | 0.17853 | 0.10529 | 0.78278 | 122.0444 | 0.20142 | 0.091553 | 122.1313 | 0.17395 | 121.994 | 122.0444 | -122.2504 | -0.24261 | 121.907 | 121.962 | 112.5275 | 121.9345
2433.8906 | 122.2183 | -121.9757 | 0.073242 | -0.0060272 | -0.0002927 | 0.054335 | 0.051985 | -0.0010638 | -0.0079061 | -0.0038303 | -0.0021057 | 0.010275 | 0.0046462 | 0.0080173 | -0.01116 | 0.020508 | -0.0012112 | -9.6863 | -0.045776 | -122.081 | -0.018311 | -121.2845 | -122.0352 | -122.0398 | 0.004578 | 0.018311 | -0.09613 | 0.009155 | 0.1236 | 0.036621 | 0.086975 | -0.10529 | -0.11902 | -0.091553 | 0.69122 | -0.064087 | -0.059509 | 0.041199 | 0.045777 | 121.8796 | -0.054931 | -0.064087 | 122.0993 | 122.0627 | 122.0123 | 0.1831 | 0.13275 | 0.79651 | 122.0627 | 0.21973 | 0.10528 | 122.0352 | 0.11444 | 121.9299 | 121.994 | -122.1542 | -0.16937 | 121.9574 | 121.9849 | 112.2894 | 121.9803
2435.6562 | 122.2229 | -121.9711 | 0.086975 | -0.0060272 | -0.0030697 | 0.055617 | 0.050917 | 0.001286 | -0.0098287 | -0.0036167 | -0.0021057 | 0.011984 | 0.0044326 | 0.0060947 | -0.015646 | 0.022644 | -0.0037748 | -9.7137 | -0.050354 | -122.081 | 0.041199 | -121.2112 | -121.9666 | -121.9803 | 0.082397 | 0.013733 | -0.086975 | 0.027466 | 0.16022 | 0.073242 | 0.091553 | -0.10986 | -0.13733 | -0.045776 | 0.75989 | -0.009156 | 0.004577 | 0.10071 | 0.11444 | 121.8842 | -0.073242 | -0.059509 | 122.1313 | 122.0627 | 122.0444 | 0.17853 | 0.16022 | 0.86975 | 122.1222 | 0.24719 | 0.11444 | 122.0306 | 0.10071 | 121.9208 | 121.9849 | -122.168 | -0.17395 | 122.0123 | 121.9986 | 112.2574 | 122.0535
2437.4062 | 122.1497 | -122.0078 | 0.11902 | -0.0060272 | -0.0032833 | 0.05583 | 0.053267 | -0.0019184 | -0.0091879 | -0.0023349 | -0.011261 | 0.014548 | 0.00251 | 0.0037447 | -0.012869 | 0.020508 | -0.0009976 | -9.9335 | 0.009155 | -122.113 | -0.073242 | -121.3303 | -122.0901 | -122.0901 | -0.059509 | 0.068665 | -0.11902 | -0.059509 | 0.054932 | -0.036621 | 0.004578 | -0.10529 | -0.10986 | -0.19226 | 0.67749 | -0.082398 | -0.082398 | 0.022888 | 0.022888 | 121.8887 | -0.050354 | -0.17853 | 122.0627 | 122.0123 | 121.9711 | 0.1236 | 0.082398 | 0.78278 | 122.0398 | 0.17395 | 0.05951 | 122.1222 | 0.18768 | 122.0169 | 122.0764 | -122.2321 | -0.23804 | 121.9345 | 121.9482 | 112.0743 | 121.9482
2439.0938 | 122.2641 | -121.9894 | 0.073242 | -0.021286 | -0.0032833 | 0.055189 | 0.05348 | -0.00042301 | -0.010256 | -0.0057529 | -0.0082093 | 0.012198 | 0.001442 | 0.011649 | -0.015219 | 0.021362 | -0.0031338 | -10.1303 | -0.022888 | -122.113 | -0.013733 | -121.2616 | -122.0215 | -122.0215 | 0.022888 | 0.018311 | -0.091553 | 0.036621 | 0.15106 | 0.064087 | 0.09613 | -0.1236 | -0.09613 | -0.086975 | 0.72784 | -0.032043 | -0.032043 | 0.091553 | 0.091553 | 121.8979 | -0.054931 | -0.036621 | 122.1405 | 122.0856 | 122.0535 | 0.18768 | 0.15564 | 0.85144 | 122.0993 | 0.24261 | 0.12817 | 122.0901 | 0.10986 | 121.9666 | 122.0078 | -122.1863 | -0.16479 | 121.9757 | 122.0261 | 111.8591 | 122.0123
2440.8594 | 122.1634 | -122.0078 | 0.10529 | -0.0060272 | -0.0011471 | 0.05583 | 0.054549 | 0.0014996 | -0.0085471 | 0.0021511 | -0.0021057 | 0.011984 | 0.0044326 | 0.0082309 | -0.015219 | 0.023071 | -0.0039884 | -10.2631 | 0.004578 | -122.1405 | -0.082397 | -121.3669 | -122.0947 | -122.113 | -0.068665 | 0.050354 | -0.1236 | -0.050354 | 0.059509 | -0.036621 | 0.036621 | -0.13275 | -0.10071 | -0.18768 | 0.64087 | -0.10529 | -0.086976 | 0.027466 | 0.045776 | 121.8842 | -0.054932 | -0.15564 | 122.0673 | 122.0444 | 121.9711 | 0.16022 | 0.086975 | 0.77362 | 122.0581 | 0.1831 | 0.073242 | 122.1451 | 0.17395 | 122.0123 | 122.0581 | -122.2458 | -0.22888 | 121.9254 | 121.9574 | 111.7447 | 121.9391
2442.625 | 122.2595 | -121.9757 | 0.073242 | -0.021286 | 0.0016299 | 0.056898 | 0.05348 | -0.0036274 | -0.0074789 | -0.0027621 | -0.0082093 | 0.010916 | 0.001442 | 0.0041721 | -0.015219 | 0.021149 | -0.0029202 | -10.4645 | -0.059509 | -122.0627 | 0.050354 | -121.2021 | -122.0123 | -121.9986 | 0.11902 | 0.018311 | -0.073242 | 0.082397 | 0.17853 | 0.086975 | 0.1236 | -0.086975 | -0.13275 | -0.022888 | 0.77362 | -0.022888 | -0.036621 | 0.064087 | 0.050354 | 121.9025 | -0.054931 | 0.009155 | 122.1542 | 122.0993 | 122.0627 | 0.19684 | 0.16022 | 0.8606 | 122.113 | 0.25177 | 0.15564 | 122.0032 | 0.091553 | 121.9162 | 121.994 | -122.1359 | -0.14648 | 122.0261 | 122.0581 | 111.5112 | 122.0947
2444.3125 | 122.2183 | -121.9666 | 0.091553 | -0.013657 | -0.0015743 | 0.05583 | 0.054549 | -0.0012774 | -0.0087607 | -0.0027621 | -0.0051575 | 0.013907 | 0.003151 | 0.0065219 | -0.014578 | 0.021362 | -0.0027066 | -10.7071 | -0.009155 | -122.1085 | -0.059509 | -121.3394 | -122.1085 | -122.1176 | -0.004578 | 0.036621 | -0.10529 | 0.036621 | 0.10986 | 0.022888 | 0.091553 | -0.14191 | -0.10071 | -0.15106 | 0.62714 | -0.15106 | -0.14191 | -0.009156 | 0 | 121.8613 | -0.054932 | -0.054932 | 122.0764 | 122.0581 | 121.9894 | 0.19684 | 0.12817 | 0.76904 | 122.0489 | 0.21515 | 0.14191 | 122.0993 | 0.14191 | 121.9574 | 122.0032 | -122.2 | -0.19684 | 121.907 | 122.0032 | 111.2595 | 121.962
2446.0781 | 122.2092 | -122.0078 | 0.10529 | -0.0060272 | 0.0003483 | 0.056258 | 0.055403 | -0.0081134 | -0.0087607 | -0.0034031 | -0.0082093 | 0.014334 | 0.0033646 | 0.0071627 | -0.014364 | 0.022003 | -0.0012112 | -10.7574 | -0.022888 | -122.113 | -0.022888 | -121.2799 | -122.049 | -122.0764 | 0.027466 | 0.045776 | -0.086975 | 0.004578 | 0.11444 | 0.018311 | 0.073242 | -0.10529 | -0.12817 | -0.12817 | 0.72784 | -0.068665 | -0.041199 | 0.036621 | 0.064087 | 121.9208 | -0.05951 | -0.10071 | 122.1222 | 122.081 | 122.0261 | 0.16022 | 0.10529 | 0.83313 | 122.0901 | 0.20142 | 0.091553 | 122.0901 | 0.13275 | 121.9849 | 122.0535 | -122.2183 | -0.19226 | 121.9849 | 122.0123 | 111.2503 | 122.0352
2447.7656 | 122.2 | -122.0398 | 0.10071 | -0.013657 | -0.0009335 | 0.055403 | 0.05348 | -0.0044818 | -0.01047 | -0.0029759 | -0.0051575 | 0.013266 | 0.0029372 | 0.0039585 | -0.015859 | 0.021362 | 0.0013522 | -10.9817 | 0.004578 | -122.1268 | -0.068665 | -121.3531 | -122.0673 | -122.1085 | -0.045776 | 0.041199 | -0.09613 | -0.036621 | 0.064087 | 0 | 0.064087 | -0.086975 | -0.09613 | -0.16937 | 0.68665 | -0.068664 | -0.027466 | 0.018311 | 0.059509 | 121.9437 | -0.059509 | -0.13733 | 122.1039 | 122.1039 | 122.0398 | 0.16022 | 0.09613 | 0.77362 | 122.0581 | 0.16022 | 0.059509 | 122.1313 | 0.13733 | 122.0444 | 122.081 | -122.2275 | -0.19684 | 121.9711 | 122.0032 | 111.058 | 121.994
2449.5312 | 122.2412 | -121.9849 | 0.086975 | -0.013657 | -0.0015743 | 0.054976 | 0.051558 | 0.00021799 | -0.0085471 | -0.0040439 | -0.0021057 | 0.013907 | 0.001442 | 0.0067355 | -0.015005 | 0.022217 | 0.0032748 | -11.2473 | -0.027466 | -122.1222 | -0.032043 | -121.2708 | -122.0306 | -122.0444 | 0.013733 | 0.022888 | -0.073242 | 0.018311 | 0.1236 | 0.041199 | 0.091553 | -0.13733 | -0.11444 | -0.11902 | 0.71411 | -0.05951 | -0.045777 | 0.077819 | 0.091552 | 121.9116 | -0.064087 | -0.068664 | 122.1085 | 122.0764 | 122.0261 | 0.16479 | 0.11444 | 0.85144 | 122.0901 | 0.19684 | 0.091553 | 122.0947 | 0.09613 | 121.9574 | 122.0078 | -122.2092 | -0.16022 | 121.9528 | 122.0032 | 110.7376 | 121.9986
2451.2969 | 122.2504 | -121.9803 | 0.07782 | -0.0060272 | 0.0007755 | 0.055403 | 0.051558 | -0.00020941 | -0.0081197 | -0.0059665 | -0.0082093 | 0.013266 | 0.0040054 | 0.0067355 | -0.0165 | 0.02179 | -0.0027066 | -11.3846 | -0.050354 | -122.0901 | 0.013733 | -121.2433 | -122.0306 | -122.0169 | 0.082397 | 0.036621 | -0.068665 | 0.045776 | 0.14191 | 0.059509 | 0.091553 | -0.10986 | -0.12817 | -0.064087 | 0.737 | -0.036621 | -0.050354 | 0.073242 | 0.059509 | 121.9116 | -0.041199 | -0.032044 | 122.1222 | 122.0718 | 122.0398 | 0.16022 | 0.12817 | 0.84686 | 122.1039 | 0.21057 | 0.11444 | 122.0398 | 0.10529 | 121.9299 | 122.0169 | -122.168 | -0.14649 | 121.994 | 122.0261 | 110.5957 | 122.0627
2453.0781 | 122.1542 | -122.0261 | 0.091553 | 0.0092313 | -0.0002927 | 0.056258 | 0.056044 | 0.0053448 | -0.0094015 | -0.0021213 | -0.0051575 | 0.013052 | 0.0048598 | 0.0037447 | -0.014364 | 0.021362 | -0.0031338 | -11.554 | -0.013733 | -122.1268 | -0.041199 | -121.3303 | -122.0901 | -122.1085 | -0.013733 | 0.064087 | -0.10986 | -0.022888 | 0.041199 | -0.059509 | 0.022888 | -0.10071 | -0.10529 | -0.13275 | 0.6958 | -0.082397 | -0.064087 | 0.018311 | 0.036621 | 121.9162 | -0.027466 | -0.11444 | 122.0673 | 122.0489 | 121.9666 | 0.13275 | 0.050354 | 0.79651 | 122.0856 | 0.15106 | 0.086975 | 122.113 | 0.17395 | 122.0123 | 122.0901 | -122.2183 | -0.20142 | 121.9849 | 122.0032 | 110.4721 | 122.0123
2454.7656 | 122.2183 | -122.0032 | 0.086975 | -0.0060272 | 0.0018435 | 0.056471 | 0.054335 | -0.001491 | -0.0070517 | -0.0059665 | -0.0051575 | 0.013266 | 0.0029372 | 0.0080173 | -0.013296 | 0.022217 | -0.0003568 | -11.8195 | -0.009155 | -122.1176 | -0.07782 | -121.3531 | -122.113 | -122.1268 | -0.018311 | 0.050354 | -0.07782 | -0.009155 | 0.082397 | -0.009155 | 0.07782 | -0.11444 | -0.09613 | -0.16479 | 0.65002 | -0.1236 | -0.10986 | -0.009155 | 0.004578 | 121.9254 | -0.036621 | -0.09613 | 122.0856 | 122.081 | 121.994 | 0.15564 | 0.068665 | 0.76447 | 122.0398 | 0.16022 | 0.068665 | 122.1085 | 0.12817 | 121.994 | 122.0535 | -122.2046 | -0.16479 | 121.9254 | 121.994 | 110.1837 | 121.9849
2456.5156 | 122.2641 | -122.0078 | 0.086975 | -0.021286 | -0.0030697 | 0.055403 | 0.051772 | -0.0010638 | -0.0085471 | -0.0023349 | -0.0021057 | 0.010702 | 0.0027236 | -0.0015957 | -0.014364 | 0.021576 | 0.0013522 | -11.9797 | -0.050354 | -122.1176 | -0.027466 | -121.2845 | -122.0306 | -122.0444 | 0.013733 | 0.027466 | -0.07782 | 0.027466 | 0.14648 | 0.054932 | 0.10071 | -0.10986 | -0.13733 | -0.11444 | 0.72327 | -0.036622 | -0.022889 | 0.073242 | 0.086975 | 121.9299 | -0.059509 | -0.059509 | 122.1542 | 122.1085 | 122.0627 | 0.17853 | 0.13275 | 0.83313 | 122.0901 | 0.2243 | 0.10529 | 122.0673 | 0.10529 | 121.9574 | 122.0352 | -122.2046 | -0.16479 | 121.9803 | 122.0352 | 110.0281 | 122.0215
2458.2031 | 122.3099 | -121.962 | 0.073242 | -0.013657 | -0.0022153 | 0.055403 | 0.050063 | -0.0051226 | -0.0096151 | -0.0029759 | -0.0051575 | 0.013052 | 0.0010146 | 0.0045993 | -0.013296 | 0.020935 | 0.0034884 | -12.0987 | -0.041199 | -122.1039 | 0.041199 | -121.1929 | -121.9757 | -121.9894 | 0.13275 | 0.013733 | -0.068665 | 0.086975 | 0.21973 | 0.13275 | 0.14191 | -0.14191 | -0.11444 | -0.032043 | 0.76904 | -0.027466 | -0.013733 | 0.11444 | 0.12817 | 121.8933 | -0.059509 | 0.013733 | 122.1817 | 122.1039 | 122.0947 | 0.21057 | 0.20142 | 0.91095 | 122.1451 | 0.28839 | 0.15564 | 122.0627 | 0.082398 | 121.9208 | 121.9757 | -122.1771 | -0.14191 | 122.0032 | 122.0489 | 109.8633 | 122.0947
2459.9531 | 122.3145 | -121.9894 | 0.082397 | -0.0060272 | -0.0024289 | 0.054121 | 0.051344 | -0.002132 | -0.0072653 | -0.0029759 | -0.0051575 | 0.011771 | 0.0037918 | 0.0054537 | -0.014364 | 0.022003 | -0.0016384 | -12.2772 | -0.050354 | -122.0901 | 0.036621 | -121.1929 | -121.962 | -121.9849 | 0.15106 | 0 | -0.064087 | 0.086975 | 0.21057 | 0.13733 | 0.15106 | -0.10071 | -0.13275 | -0.045776 | 0.79651 | 0.004578 | 0.027466 | 0.10529 | 0.12817 | 121.9254 | -0.082397 | 0.004578 | 122.2 | 122.1405 | 122.1268 | 0.21515 | 0.20142 | 0.89722 | 122.1268 | 0.27466 | 0.15106 | 122.0398 | 0.064087 | 121.9391 | 121.9894 | -122.1725 | -0.14648 | 122.0261 | 122.0764 | 109.7122 | 122.1405
2461.7188 | 122.168 | -122.0444 | 0.10071 | -0.0060272 | -0.0022153 | 0.05348 | 0.05348 | -0.0051226 | -0.0064109 | -0.0042575 | -0.0021057 | 0.015189 | 0.0035782 | 0.0073763 | -0.015646 | 0.023499 | -0.003561 | -12.5198 | -0.004578 | -122.1863 | -0.07782 | -121.3486 | -122.0901 | -122.113 | -0.041199 | 0.064087 | -0.10529 | -0.059509 | 0.041199 | -0.032043 | 0.032043 | -0.14191 | -0.10529 | -0.17853 | 0.6958 | -0.068664 | -0.045776 | 0.073242 | 0.09613 | 121.9391 | -0.036621 | -0.16022 | 122.0856 | 122.0764 | 122.0123 | 0.13733 | 0.073243 | 0.83771 | 122.1085 | 0.14649 | 0.045777 | 122.1817 | 0.16937 | 122.0398 | 122.1085 | -122.287 | -0.20599 | 121.9666 | 121.9849 | 109.5245 | 122.0032
2463.4062 | 122.2046 | -122.0078 | 0.10071 | -0.0060272 | -0.0020017 | 0.054121 | 0.05049 | -0.0027728 | -0.0085471 | -0.0034031 | -0.0051575 | 0.012198 | 0.0044326 | -0.0013821 | -0.01415 | 0.021362 | -0.0054838 | -12.6434 | -0.045776 | -122.1176 | 0.027466 | -121.2479 | -122.0078 | -122.0306 | 0.041199 | 0.013733 | -0.10529 | -0.009155 | 0.11902 | 0.036621 | 0.059509 | -0.10986 | -0.14648 | -0.073242 | 0.75989 | -0.022889 | 0 | 0.086975 | 0.10986 | 121.9025 | -0.086975 | -0.10986 | 122.1268 | 122.0673 | 122.0444 | 0.16479 | 0.14191 | 0.86975 | 122.1451 | 0.22431 | 0.096131 | 122.0718 | 0.11902 | 121.962 | 122.0215 | -122.2183 | -0.20599 | 122.0352 | 121.9986 | 109.3643 | 122.049
2465.1562 | 122.1817 | -122.049 | 0.10529 | -0.013657 | -0.0026425 | 0.05348 | 0.051558 | -0.0040546 | -0.0081197 | -0.0051121 | -0.0082093 | 0.013907 | 0.0048598 | 0.0065219 | -0.0165 | 0.021149 | -0.0016384 | -12.8998 | -0.022888 | -122.1405 | 0.009155 | -121.2662 | -122.0215 | -122.0444 | 0.022888 | 0.045776 | -0.09613 | -0.018311 | 0.10071 | 0.004578 | 0.050354 | -0.091553 | -0.12817 | -0.096131 | 0.78278 | 0.004577 | 0.027466 | 0.09613 | 0.11902 | 121.9528 | -0.05951 | -0.1236 | 122.1497 | 122.0993 | 122.0535 | 0.14648 | 0.10071 | 0.87433 | 122.1497 | 0.19684 | 0.077819 | 122.1176 | 0.14191 | 122.0261 | 122.0947 | -122.2458 | -0.20142 | 122.0581 | 122.0306 | 109.1492 | 122.0718
2466.9219 | 122.2824 | -122.0078 | 0.09613 | -0.021286 | 0.0022709 | 0.056898 | 0.054549 | 0.001286 | -0.0072653 | -0.0027621 | -0.0051575 | 0.012625 | 0.0046462 | 0.0075901 | -0.013937 | 0.023071 | -0.0001432 | -13.2339 | -0.013733 | -122.1085 | -0.009155 | -121.2982 | -122.0627 | -122.0673 | 0.064087 | 0.032043 | -0.07782 | 0.059509 | 0.15106 | 0.073242 | 0.13275 | -0.10071 | -0.10986 | -0.10528 | 0.70953 | -0.05951 | -0.054932 | 0.041198 | 0.045776 | 121.9299 | -0.064087 | -0.036621 | 122.1588 | 122.1405 | 122.081 | 0.21057 | 0.15106 | 0.81024 | 122.0993 | 0.22888 | 0.13733 | 122.0947 | 0.10986 | 121.994 | 122.0398 | -122.2046 | -0.17395 | 121.9986 | 122.0673 | 108.7738 | 122.0718
2468.6875 | 122.2916 | -122.0032 | 0.086975 | -0.0060272 | -0.0020017 | 0.054549 | 0.053267 | -0.0057636 | -0.010043 | -0.0019077 | -0.0021057 | 0.009848 | 0.00080103 | 0.0037447 | -0.013296 | 0.019867 | 0.0024204 | -13.4354 | -0.036621 | -122.1268 | -0.004578 | -121.2662 | -122.0169 | -122.0215 | 0.07782 | 0.009155 | -0.068665 | 0.054932 | 0.19226 | 0.10529 | 0.13733 | -0.1236 | -0.1236 | -0.091553 | 0.737 | -0.01831 | -0.013733 | 0.10529 | 0.10986 | 121.9345 | -0.07782 | -0.032043 | 122.1954 | 122.1405 | 122.1085 | 0.20599 | 0.17395 | 0.8606 | 122.1222 | 0.26093 | 0.1236 | 122.0901 | 0.07782 | 121.9666 | 122.0123 | -122.2137 | -0.15564 | 121.9986 | 122.0581 | 108.5678 | 122.081
2470.375 | 122.1817 | -122.0261 | 0.1236 | -0.013657 | -0.0017881 | 0.055403 | 0.05284 | 0.0017132 | -0.0085471 | -0.0042575 | -0.0051575 | 0.012198 | 0.0022964 | 0.0071627 | -0.01351 | 0.019867 | -0.0003568 | -13.6505 | 0.013733 | -122.168 | -0.086975 | -121.3715 | -122.0901 | -122.1313 | -0.073242 | 0.073242 | -0.10986 | -0.032043 | 0.059509 | -0.032043 | 0.032043 | -0.14191 | -0.10986 | -0.21057 | 0.6546 | -0.10529 | -0.064087 | 0.036621 | 0.07782 | 121.9162 | -0.050354 | -0.15564 | 122.0856 | 122.0581 | 121.994 | 0.14191 | 0.07782 | 0.79651 | 122.081 | 0.16937 | 0.07782 | 122.1817 | 0.18311 | 122.0398 | 122.0993 | -122.2916 | -0.23346 | 121.9391 | 121.994 | 108.3755 | 121.9528
2472.1406 | 122.168 | -122.0444 | 0.11444 | -0.021286 | -0.0022153 | 0.055189 | 0.055189 | -0.00020941 | -0.0083335 | -0.0063937 | -0.0021057 | 0.012625 | 0.0018692 | 0.0022495 | -0.012869 | 0.022217 | -0.0001432 | -13.8657 | -0.004578 | -122.1817 | -0.086975 | -121.3303 | -122.0993 | -122.1176 | -0.050354 | 0.054932 | -0.10071 | -0.054932 | 0.073242 | -0.032043 | 0.013733 | -0.13733 | -0.11902 | -0.20142 | 0.71411 | -0.073242 | -0.054931 | 0.064087 | 0.082398 | 121.9437 | -0.059509 | -0.16937 | 122.1176 | 122.0581 | 122.0123 | 0.11444 | 0.068665 | 0.85144 | 122.0947 | 0.17395 | 0.045776 | 122.1771 | 0.15564 | 122.0398 | 122.0993 | -122.2961 | -0.21515 | 121.9574 | 121.9894 | 108.1787 | 121.994
2473.9062 | 122.1634 | -122.0352 | 0.11902 | -0.021286 | 0.0018435 | 0.056258 | 0.054762 | 0.001286 | -0.0070517 | -0.0023349 | -0.0051575 | 0.01348 | 0.0040054 | 0.011008 | -0.015432 | 0.022217 | 0.0011386 | -14.1815 | 0 | -122.1313 | -0.091553 | -121.3852 | -122.1588 | -122.168 | -0.050354 | 0.064087 | -0.1236 | -0.045776 | 0.041199 | -0.054932 | 0.036621 | -0.096131 | -0.11902 | -0.21057 | 0.65002 | -0.13275 | -0.1236 | -0.036621 | -0.027465 | 121.9116 | -0.054932 | -0.16479 | 122.0764 | 122.0718 | 121.9803 | 0.16022 | 0.068664 | 0.74616 | 122.0398 | 0.16479 | 0.07782 | 122.1313 | 0.18768 | 122.0352 | 122.0993 | -122.2504 | -0.24261 | 121.9437 | 121.9894 | 107.8537 | 121.9849
2475.6094 | 122.2183 | -121.9849 | 0.12817 | -0.013657 | 0.0005619 | 0.055617 | 0.054549 | 0.0017132 | -0.0096151 | -0.0031895 | -0.0051575 | 0.012625 | 0.0029372 | 0.0092989 | -0.015646 | 0.024567 | 0.0002842 | -14.3188 | 0.009155 | -122.1542 | -0.045776 | -121.3211 | -122.0673 | -122.0993 | 0 | 0.073242 | -0.09613 | 0 | 0.10986 | 0.013733 | 0.082397 | -0.16937 | -0.11902 | -0.17395 | 0.66376 | -0.11444 | -0.082398 | 0.054932 | 0.086975 | 121.8887 | -0.054932 | -0.12817 | 122.0947 | 122.0673 | 121.9986 | 0.17853 | 0.10986 | 0.83313 | 122.1085 | 0.20599 | 0.09613 | 122.1634 | 0.16937 | 121.994 | 122.0581 | -122.2824 | -0.2243 | 121.9391 | 121.9849 | 107.666 | 121.9849
2477.2969 | 122.2549 | -122.0261 | 0.064087 | -0.021286 | 0.0009891 | 0.053908 | 0.051985 | 0.00043159 | -0.0036337 | -0.0042575 | -0.0082093 | 0.011771 | 0.003151 | 0.0075901 | -0.013723 | 0.021576 | -0.0022794 | -14.6301 | -0.050354 | -122.0901 | -0.004578 | -121.2616 | -122.0673 | -122.0535 | 0.036621 | 0.013733 | -0.07782 | 0.027466 | 0.12817 | 0.036621 | 0.10071 | -0.064087 | -0.11444 | -0.068665 | 0.76447 | -0.027466 | -0.041199 | 0.036621 | 0.022888 | 121.9482 | -0.050354 | -0.036621 | 122.1542 | 122.1268 | 122.0627 | 0.17853 | 0.11444 | 0.82855 | 122.0856 | 0.20599 | 0.10529 | 122.0398 | 0.091553 | 121.9757 | 122.0398 | -122.1542 | -0.14191 | 122.0215 | 122.0535 | 107.3959 | 122.0627
2479.0469 | 122.2549 | -122.0078 | 0.091553 | -0.0060272 | -0.0002927 | 0.05284 | 0.052626 | 0.00021799 | -0.0094015 | -0.0055393 | -0.0021057 | 0.012198 | 0.0033646 | 0.0069491 | -0.015859 | 0.019012 | 0.003702 | -14.8315 | -0.036621 | -122.1497 | -0.013733 | -121.2891 | -122.0581 | -122.0627 | 0.009155 | 0.004578 | -0.082397 | 0.009155 | 0.13733 | 0.041199 | 0.10071 | -0.14191 | -0.12817 | -0.10529 | 0.71869 | -0.054932 | -0.050354 | 0.086975 | 0.091553 | 121.9254 | -0.086975 | -0.082398 | 122.1451 | 122.1085 | 122.049 | 0.18311 | 0.1236 | 0.8606 | 122.1359 | 0.21973 | 0.091552 | 122.113 | 0.086975 | 121.9711 | 122.0123 | -122.2412 | -0.17395 | 121.994 | 122.0169 | 107.1762 | 122.0169
2480.7969 | 122.2961 | -122.0032 | 0.068665 | -0.0060272 | 0.0048343 | 0.057539 | 0.052626 | -0.0012774 | -0.0091879 | -0.0078891 | -0.0051575 | 0.011343 | 0.00080103 | 0.0048129 | -0.014364 | 0.02179 | -0.004202 | -15.0696 | -0.050354 | -122.0993 | 0.050354 | -121.2021 | -122.0123 | -122.0306 | 0.11444 | 0.027466 | -0.054932 | 0.082397 | 0.1831 | 0.086975 | 0.13275 | -0.09613 | -0.11902 | -0.018311 | 0.80109 | -0.027466 | -0.009155 | 0.068664 | 0.086975 | 121.9482 | -0.041199 | 0.013732 | 122.1863 | 122.1359 | 122.0901 | 0.18768 | 0.14191 | 0.89722 | 122.1497 | 0.23804 | 0.13733 | 122.049 | 0.082398 | 121.9528 | 122.0306 | -122.168 | -0.1236 | 122.0535 | 122.0856 | 106.9336 | 122.1176
2482.5 | 122.1771 | -122.0581 | 0.11444 | -0.0060272 | -0.0013607 | 0.053267 | 0.053267 | -0.00555 | -0.0096151 | -0.0038303 | -0.0051575 | 0.013693 | 0.00251 | 0.0099399 | -0.015219 | 0.023071 | -0.0009976 | -15.2893 | 0.004578 | -122.1817 | -0.086975 | -121.3486 | -122.1085 | -122.1359 | -0.064087 | 0.059509 | -0.10986 | -0.054932 | 0.050354 | -0.027466 | 0.036621 | -0.1236 | -0.10986 | -0.20142 | 0.70953 | -0.07782 | -0.050354 | 0.045777 | 0.073243 | 121.9482 | -0.054932 | -0.16937 | 122.1085 | 122.0947 | 122.0306 | 0.14648 | 0.082397 | 0.83313 | 122.0947 | 0.16022 | 0.054931 | 122.1863 | 0.16937 | 122.0627 | 122.1176 | -122.2961 | -0.2243 | 121.9711 | 122.0032 | 106.7688 | 121.994
2484.25 | 122.3145 | -122.0078 | 0.054932 | -0.013657 | 0.0016299 | 0.055403 | 0.052199 | -0.003841 | -0.0055563 | -0.0042575 | -0.0021057 | 0.011984 | 0.0016556 | 0.00096772 | -0.015005 | 0.022644 | -0.0005704 | -15.5273 | -0.050354 | -122.0947 | 0.050354 | -121.225 | -122.0261 | -122.0261 | 0.11902 | 0.022888 | -0.068665 | 0.10071 | 0.17853 | 0.10529 | 0.14648 | -0.086976 | -0.10529 | -0.004578 | 0.78278 | -0.018311 | -0.018311 | 0.068665 | 0.068665 | 121.9391 | -0.032044 | 0.045776 | 122.1863 | 122.1542 | 122.113 | 0.21515 | 0.17395 | 0.86975 | 122.1451 | 0.24719 | 0.16937 | 122.0444 | 0.091553 | 121.9574 | 122.0306 | -122.1497 | -0.1236 | 122.0581 | 122.1085 | 106.4804 | 122.1268
2486 | 122.2733 | -122.0078 | 0.082397 | -0.021286 | 0.0007755 | 0.054335 | 0.052626 | -0.003841 | -0.0076925 | -0.0059665 | -0.0021057 | 0.010702 | 0.00058743 | 0.0073763 | -0.013937 | 0.021576 | -0.0012112 | -15.8157 | -0.054932 | -122.1359 | -0.004578 | -121.257 | -122.0718 | -122.0581 | 0.036621 | 0.018311 | -0.082397 | 0.036621 | 0.13733 | 0.050354 | 0.086975 | -0.12817 | -0.13733 | -0.086975 | 0.75073 | -0.050354 | -0.064087 | 0.07782 | 0.064087 | 121.9254 | -0.064086 | -0.045776 | 122.1451 | 122.0947 | 122.0581 | 0.16937 | 0.13275 | 0.87891 | 122.1313 | 0.21973 | 0.11902 | 122.081 | 0.10071 | 121.9528 | 122.0261 | -122.2183 | -0.16479 | 122.0032 | 122.0444 | 106.192 | 122.0444
2487.7031 | 122.1909 | -122.0398 | 0.11444 | -0.013657 | 0.0026981 | 0.056258 | 0.056685 | 4.192e-06 | -0.0066245 | -0.0057529 | -0.0051575 | 0.012411 | 0.0022964 | 0.0088717 | -0.01351 | 0.022003 | -0.0012112 | -16.0675 | 0.004578 | -122.1588 | -0.09613 | -121.4035 | -122.1817 | -122.1771 | -0.050354 | 0.064087 | -0.10529 | -0.050354 | 0.022888 | -0.050354 | 0.032043 | -0.11902 | -0.10986 | -0.21057 | 0.63629 | -0.13733 | -0.14191 | -0.018311 | -0.022889 | 121.9345 | -0.050354 | -0.16479 | 122.0627 | 122.0718 | 121.9894 | 0.13733 | 0.054932 | 0.75531 | 122.0627 | 0.12817 | 0.054932 | 122.1634 | 0.16937 | 122.0444 | 122.1039 | -122.2733 | -0.21973 | 121.9437 | 121.9894 | 105.9723 | 121.9894
2489.4531 | 122.1771 | -122.0535 | 0.12817 | -0.013657 | -0.0032833 | 0.05284 | 0.054121 | -0.0040546 | -0.010256 | -0.0029759 | -0.0082093 | 0.011984 | 0.0027236 | 0.0082309 | -0.015005 | 0.020721 | -0.0014248 | -16.3055 | 0.004578 | -122.1634 | -0.07782 | -121.3394 | -122.1085 | -122.1313 | -0.050354 | 0.054932 | -0.10071 | -0.050354 | 0.064087 | -0.032043 | 0.013733 | -0.10986 | -0.1236 | -0.20599 | 0.71411 | -0.07782 | -0.054931 | 0.032043 | 0.054932 | 121.9528 | -0.073242 | -0.17853 | 122.1176 | 122.0673 | 122.0215 | 0.11444 | 0.068665 | 0.82397 | 122.0856 | 0.1648 | 0.050354 | 122.168 | 0.15564 | 122.0581 | 122.1085 | -122.2916 | -0.22888 | 121.9757 | 122.0032 | 105.748 | 122.0032
2491.2031 | 122.3236 | -122.0078 | 0.07782 | -0.021286 | -0.0039243 | 0.056044 | 0.049635 | -0.0059772 | -0.0072653 | -0.0031895 | -0.014313 | 0.01113 | 0.003151 | 0.0090853 | -0.013723 | 0.018799 | 0.0004978 | -16.5436 | -0.018311 | -122.1542 | 0.009155 | -121.2524 | -122.0352 | -122.0352 | 0.068665 | 0.036621 | -0.086975 | 0.064087 | 0.1831 | 0.091553 | 0.13275 | -0.14648 | -0.096131 | -0.068665 | 0.75531 | -0.027466 | -0.027466 | 0.11902 | 0.11902 | 121.9208 | -0.041199 | -0.013733 | 122.1909 | 122.1405 | 122.0993 | 0.21973 | 0.17853 | 0.90179 | 122.1634 | 0.27008 | 0.15106 | 122.1359 | 0.1236 | 121.9894 | 122.0444 | -122.2321 | -0.16479 | 122.0169 | 122.0718 | 105.4642 | 122.0764
2492.8906 | 122.1863 | -122.0169 | 0.12817 | 0.0016023 | 0.0022709 | 0.055617 | 0.052626 | -0.0012774 | -0.0076925 | -0.0031895 | -0.0051575 | 0.012839 | 0.0029372 | 0.0080173 | -0.014364 | 0.019867 | -0.0022794 | -16.7679 | -0.018311 | -122.1405 | -0.032043 | -121.3257 | -122.113 | -122.1359 | 0.009155 | 0.068665 | -0.091553 | -0.018311 | 0.064087 | -0.041199 | 0.045776 | -0.1236 | -0.14649 | -0.16022 | 0.69122 | -0.11902 | -0.09613 | 0.004578 | 0.027466 | 121.9254 | -0.059509 | -0.14649 | 122.081 | 122.0627 | 121.9757 | 0.13733 | 0.050354 | 0.81482 | 122.1085 | 0.15564 | 0.073242 | 122.1222 | 0.16022 | 121.9986 | 122.0856 | -122.2687 | -0.21973 | 121.9849 | 121.9986 | 105.249 | 122.0261
2494.6406 | 122.2092 | -122.049 | 0.10986 | -0.013657 | 0.0029117 | 0.054121 | 0.056471 | 4.192e-06 | -0.0096151 | -0.0051121 | -0.0021057 | 0.013052 | 0.0022964 | 0.0028903 | -0.01351 | 0.020508 | -0.0005704 | -17.1066 | -0.013733 | -122.1634 | -0.027466 | -121.312 | -122.1039 | -122.1313 | 0.009155 | 0.059509 | -0.082397 | -0.004578 | 0.086975 | -0.018311 | 0.059509 | -0.11444 | -0.1236 | -0.13733 | 0.737 | -0.082398 | -0.054932 | 0.032043 | 0.059509 | 121.9666 | -0.050354 | -0.11444 | 122.1359 | 122.1085 | 122.0306 | 0.14191 | 0.064086 | 0.85144 | 122.1359 | 0.16937 | 0.077819 | 122.1497 | 0.14191 | 122.0352 | 122.1085 | -122.2733 | -0.19226 | 122.0215 | 122.0444 | 104.9423 | 122.0581
2496.3281 | 122.1954 | -122.0581 | 0.11902 | -0.013657 | -0.0015743 | 0.054121 | 0.052626 | -0.0059772 | -0.011751 | -0.0029759 | -0.0021057 | 0.012411 | 0.0029372 | 0.0026767 | -0.013082 | 0.021576 | -0.0005704 | -17.3355 | -0.004578 | -122.1863 | -0.10986 | -121.3577 | -122.1085 | -122.1451 | -0.07782 | 0.068665 | -0.10071 | -0.045776 | 0.068665 | -0.027466 | 0.041199 | -0.12817 | -0.1236 | -0.22888 | 0.70038 | -0.086976 | -0.050354 | 0.041198 | 0.07782 | 121.9574 | -0.050354 | -0.16479 | 122.1268 | 122.0993 | 122.0306 | 0.14191 | 0.073242 | 0.82855 | 122.0764 | 0.16937 | 0.054932 | 122.1817 | 0.16937 | 122.0535 | 122.1268 | -122.3053 | -0.21973 | 121.9482 | 122.0123 | 104.7226 | 121.9803
2498.1094 | 122.2229 | -122.049 | 0.10071 | -0.013657 | -0.0009335 | 0.055617 | 0.050703 | -0.0010638 | -0.012179 | -0.0042575 | -0.0051575 | 0.012198 | 0.0044326 | 0.0075901 | -0.013937 | 0.020294 | 0.0004978 | -17.5735 | 0.009155 | -122.1817 | -0.064087 | -121.3211 | -122.0947 | -122.1176 | -0.009155 | 0.059509 | -0.086975 | 0.004578 | 0.11902 | 0.009155 | 0.073242 | -0.13275 | -0.091553 | -0.1648 | 0.72784 | -0.068665 | -0.045777 | 0.064087 | 0.086975 | 121.962 | -0.041199 | -0.09613 | 122.168 | 122.1222 | 122.0581 | 0.16022 | 0.09613 | 0.8606 | 122.1176 | 0.20599 | 0.091553 | 122.1909 | 0.14648 | 122.0581 | 122.1085 | -122.2824 | -0.18768 | 121.9849 | 122.0535 | 104.4754 | 122.0398
2499.7969 | 122.2046 | -122.081 | 0.10529 | -0.0060272 | -0.0030697 | 0.05284 | 0.050276 | -0.0010638 | -0.011111 | -0.0036167 | -0.0051575 | 0.012839 | 0.00080103 | -0.0028775 | -0.015432 | 0.019226 | -0.0020658 | -17.7795 | -0.032043 | -122.168 | -0.059509 | -121.3211 | -122.0901 | -122.113 | -0.032043 | 0.064087 | -0.10529 | -0.041199 | 0.07782 | -0.009155 | 0.027466 | -0.086975 | -0.13733 | -0.16479 | 0.75989 | -0.032043 | -0.009155 | 0.054932 | 0.07782 | 121.9757 | -0.041199 | -0.14649 | 122.1588 | 122.1085 | 122.0718 | 0.13275 | 0.096131 | 0.84686 | 122.1085 | 0.18311 | 0.064087 | 122.1359 | 0.16937 | 122.049 | 122.1451 | -122.2733 | -0.21057 | 122.0215 | 122.0398 | 104.3015 | 122.049
2501.5469 | 122.3282 | -122.0123 | 0.086975 | 0.0016023 | 0.0014163 | 0.054762 | 0.05348 | -0.00063661 | -0.0083335 | -0.0046847 | -0.0082093 | 0.011984 | 0.001442 | -0.00010048 | -0.015432 | 0.024353 | -0.002493 | -18.0542 | -0.045776 | -122.1176 | 0.050354 | -121.1975 | -122.0261 | -122.0261 | 0.11902 | 0 | -0.059509 | 0.091553 | 0.17395 | 0.10986 | 0.13733 | -0.10529 | -0.13275 | -0.036621 | 0.81482 | -0.013733 | -0.013733 | 0.091553 | 0.091553 | 121.9528 | -0.086975 | 0.004578 | 122.1863 | 122.1497 | 122.1222 | 0.19684 | 0.16937 | 0.92011 | 122.168 | 0.23346 | 0.15106 | 122.0718 | 0.059509 | 121.9666 | 122.0123 | -122.2046 | -0.14648 | 122.0627 | 122.1039 | 103.9581 | 122.1313
2503.2969 | 122.2733 | -122.0215 | 0.091553 | -0.021286 | -0.0007199 | 0.054762 | 0.053267 | 0.0034222 | -0.0085471 | -0.0051121 | -0.0051575 | 0.011984 | 0.0020828 | 0.0031039 | -0.015219 | 0.019867 | 0.0002842 | -18.338 | -0.041199 | -122.1313 | -0.004578 | -121.2753 | -122.0718 | -122.0627 | 0.032043 | 0.013733 | -0.073242 | 0.027466 | 0.14191 | 0.059509 | 0.09613 | -0.10986 | -0.13275 | -0.096131 | 0.74615 | -0.041199 | -0.050354 | 0.068665 | 0.05951 | 121.9482 | -0.07782 | -0.064087 | 122.1634 | 122.1176 | 122.081 | 0.16937 | 0.13275 | 0.85602 | 122.1268 | 0.21515 | 0.10071 | 122.0901 | 0.086975 | 121.9803 | 122.0352 | -122.2229 | -0.16479 | 122.0169 | 122.049 | 103.6835 | 122.0535
2505.0469 | 122.319 | -122.0169 | 0.082397 | -0.013657 | 0.0005619 | 0.055403 | 0.054762 | 0.0034222 | -0.0079061 | -0.0025485 | -0.0051575 | 0.012625 | 0.0016556 | 0.0041721 | -0.017355 | 0.020081 | 0.0011386 | -18.6218 | -0.018311 | -122.1542 | -0.032043 | -121.3074 | -122.0947 | -122.1176 | 0.059509 | 0.032043 | -0.064087 | 0.064087 | 0.17395 | 0.07782 | 0.1236 | -0.13733 | -0.10071 | -0.11444 | 0.70953 | -0.10071 | -0.07782 | 0.036621 | 0.059509 | 121.9528 | -0.050354 | -0.01831 | 122.1909 | 122.1405 | 122.0947 | 0.18768 | 0.14191 | 0.84686 | 122.1222 | 0.23804 | 0.12817 | 122.1359 | 0.09613 | 121.9986 | 122.049 | -122.2366 | -0.14648 | 121.9849 | 122.081 | 103.3951 | 122.0764
2506.7344 | 122.319 | -122.0261 | 0.086975 | -0.021286 | -0.0020017 | 0.054121 | 0.052199 | -0.0034136 | -0.0087607 | -0.0051121 | -0.0021057 | 0.010702 | -0.00026697 | 0.011222 | -0.016287 | 0.023071 | 0.0032748 | -18.7454 | -0.050354 | -122.1451 | 0.050354 | -121.2067 | -121.994 | -122.0078 | 0.10529 | 0.041199 | -0.059509 | 0.073242 | 0.21057 | 0.11902 | 0.13275 | -0.11902 | -0.13733 | -0.036621 | 0.8194 | 0.018311 | 0.032043 | 0.13733 | 0.15106 | 121.9666 | -0.045776 | -0.013733 | 122.2366 | 122.1588 | 122.1451 | 0.19226 | 0.17853 | 0.93842 | 122.1954 | 0.27008 | 0.13275 | 122.0947 | 0.10071 | 121.9757 | 122.0673 | -122.2321 | -0.14648 | 122.0764 | 122.0993 | 103.2806 | 122.1313
2508.5 | 122.1817 | -122.0535 | 0.1236 | -0.013657 | 0.0029117 | 0.056258 | 0.055403 | 0.0027814 | -0.0094015 | -0.0055393 | -0.0051575 | 0.015829 | 0.0040054 | 0.010154 | -0.015859 | 0.022003 | -0.0048428 | -19.0384 | -0.013733 | -122.1542 | -0.054932 | -121.3577 | -122.1634 | -122.1588 | -0.045776 | 0.068665 | -0.09613 | -0.036621 | 0.041199 | -0.054932 | 0.032043 | -0.10071 | -0.13733 | -0.17853 | 0.6958 | -0.10528 | -0.10986 | -0.004577 | -0.009155 | 121.9574 | -0.054931 | -0.16022 | 122.0947 | 122.0856 | 121.9986 | 0.12817 | 0.041198 | 0.79651 | 122.0993 | 0.13733 | 0.059509 | 122.1405 | 0.16479 | 122.0398 | 122.1222 | -122.2778 | -0.21973 | 121.9986 | 122.0169 | 103.0151 | 122.0078
2510.2031 | 122.3373 | -122.0306 | 0.086975 | -0.021286 | -0.0030697 | 0.053267 | 0.051558 | -0.0023456 | -0.0083335 | -0.0025485 | -0.0051575 | 0.010062 | 0.00080103 | 0.0037447 | -0.012869 | 0.020508 | -0.002493 | -19.2535 | -0.032043 | -122.1451 | 0.022888 | -121.2341 | -122.0123 | -122.0261 | 0.10986 | 0.027466 | -0.064087 | 0.091553 | 0.21515 | 0.12817 | 0.15564 | -0.11444 | -0.11902 | -0.064087 | 0.79651 | 0.004578 | 0.018311 | 0.11902 | 0.13275 | 121.9666 | -0.059509 | 0.004578 | 122.2458 | 122.1863 | 122.1588 | 0.21973 | 0.19226 | 0.91095 | 122.168 | 0.27924 | 0.15564 | 122.113 | 0.091553 | 121.9986 | 122.0581 | -122.2321 | -0.15106 | 122.0535 | 122.1222 | 102.7771 | 122.1405
2511.9531 | 122.2687 | -122.0169 | 0.091553 | -0.0060272 | -0.0028561 | 0.056044 | 0.050917 | -0.0051226 | -0.010043 | -0.0051121 | -0.0051575 | 0.011343 | 0.00058743 | 0.0082309 | -0.017141 | 0.021362 | -0.0020658 | -19.4687 | -0.045776 | -122.1588 | 0.032043 | -121.2158 | -122.0215 | -122.0398 | 0.07782 | 0.032043 | -0.068665 | 0.032043 | 0.15106 | 0.064087 | 0.10529 | -0.14191 | -0.13733 | -0.05951 | 0.80109 | -0.022888 | -0.004577 | 0.11902 | 0.13733 | 121.9482 | -0.05951 | -0.05951 | 122.168 | 122.1222 | 122.081 | 0.17395 | 0.13275 | 0.94299 | 122.1909 | 0.21973 | 0.10071 | 122.113 | 0.10071 | 121.9711 | 122.049 | -122.2504 | -0.16022 | 122.049 | 122.049 | 102.5482 | 122.0947
2513.7031 | 122.3602 | -122.0261 | 0.082397 | -0.013657 | -0.0022153 | 0.056044 | 0.052199 | -0.00042301 | -0.010897 | -0.0040439 | -0.0082093 | 0.010489 | 0.00016023 | 0.00054052 | -0.015219 | 0.020508 | -0.0044156 | -19.7525 | -0.041199 | -122.1405 | 0.064087 | -121.1792 | -121.9849 | -122.0078 | 0.15564 | 0.027466 | -0.036621 | 0.07782 | 0.2243 | 0.12817 | 0.15106 | -0.11444 | -0.1236 | -0.01831 | 0.84686 | 0.018311 | 0.041199 | 0.13275 | 0.15564 | 121.9894 | -0.054931 | -0.004577 | 122.2504 | 122.1771 | 122.1542 | 0.18768 | 0.1648 | 0.9613 | 122.2046 | 0.26093 | 0.11444 | 122.0993 | 0.064087 | 121.9849 | 122.0535 | -122.2229 | -0.11902 | 122.0901 | 122.1039 | 102.2736 | 122.1817
2515.3906 | 122.1954 | -122.0673 | 0.11902 | -0.0060272 | -0.0015743 | 0.054549 | 0.054549 | 4.192e-06 | -0.010043 | -0.0046847 | -0.0051575 | 0.013052 | 0.0033646 | 0.0050265 | -0.015859 | 0.021149 | -0.0018522 | -20.0912 | -0.009155 | -122.168 | -0.07782 | -121.3394 | -122.1268 | -122.1405 | -0.032043 | 0.068665 | -0.10071 | -0.041199 | 0.064087 | -0.022888 | 0.032043 | -0.10071 | -0.12817 | -0.19684 | 0.72784 | -0.073242 | -0.059509 | 0.027466 | 0.041199 | 121.9666 | -0.050354 | -0.16022 | 122.1313 | 122.0993 | 122.0444 | 0.13275 | 0.07782 | 0.82855 | 122.0901 | 0.1648 | 0.059509 | 122.1588 | 0.16937 | 122.0581 | 122.1359 | -122.287 | -0.21973 | 121.9894 | 122.0261 | 101.976 | 122.0352
2517.1406 | 122.2595 | -122.0535 | 0.10986 | -0.021286 | -0.0015743 | 0.053908 | 0.054976 | -0.0012774 | -0.0068381 | -0.0034031 | -0.0051575 | 0.014334 | 0.0048598 | 0.012503 | -0.015859 | 0.02179 | -0.0029202 | -20.3018 | -0.004578 | -122.1954 | -0.032043 | -121.312 | -122.0947 | -122.1176 | 0.022888 | 0.064087 | -0.07782 | 0.022888 | 0.10529 | 0.041199 | 0.10071 | -0.14191 | -0.11444 | -0.14191 | 0.74158 | -0.064087 | -0.041199 | 0.07782 | 0.10071 | 121.9757 | -0.045776 | -0.086975 | 122.1588 | 122.1542 | 122.0947 | 0.17853 | 0.11902 | 0.88348 | 122.1634 | 0.18311 | 0.10071 | 122.1909 | 0.14191 | 122.049 | 122.1176 | -122.3053 | -0.18768 | 122.0215 | 122.0764 | 101.7517 | 122.0764
2518.8281 | 122.2595 | -122.0398 | 0.10986 | -0.0060272 | 0.0014163 | 0.053694 | 0.056044 | 0.001286 | -0.0094015 | -0.0031895 | -0.0021057 | 0.012625 | 0.0037918 | 0.0065219 | -0.013723 | 0.020081 | -0.0014248 | -20.4941 | -0.013733 | -122.2046 | -0.009155 | -121.2753 | -122.081 | -122.1085 | 0.041199 | 0.050354 | -0.073242 | 0.027466 | 0.11902 | 0.027466 | 0.091553 | -0.16479 | -0.1236 | -0.11902 | 0.76447 | -0.068664 | -0.041199 | 0.096131 | 0.1236 | 121.9666 | -0.059509 | -0.082397 | 122.1588 | 122.1313 | 122.0673 | 0.16479 | 0.10071 | 0.92926 | 122.1954 | 0.19226 | 0.10071 | 122.1909 | 0.1236 | 122.0261 | 122.0901 | -122.3145 | -0.18311 | 122.0306 | 122.0673 | 101.5457 | 122.081
2520.5781 | 122.319 | -122.0123 | 0.091553 | -0.013657 | 0.0003483 | 0.053694 | 0.051772 | 0.0036358 | -0.0061971 | -0.0034031 | -0.0021057 | 0.011771 | 0.0018692 | -0.00052768 | -0.014791 | 0.021149 | 0.0013522 | -20.8603 | -0.009155 | -122.1817 | -0.018311 | -121.2753 | -122.113 | -122.1085 | 0.054932 | 0.027466 | -0.073242 | 0.082397 | 0.16937 | 0.086975 | 0.14191 | -0.16937 | -0.10071 | -0.10986 | 0.737 | -0.09613 | -0.10071 | 0.073243 | 0.068665 | 121.9391 | -0.064087 | -0.009156 | 122.1817 | 122.1542 | 122.0993 | 0.21515 | 0.16022 | 0.90637 | 122.1634 | 0.24261 | 0.15564 | 122.1725 | 0.10071 | 122.0032 | 122.0398 | -122.2733 | -0.16479 | 121.994 | 122.0947 | 101.152 | 122.0673
2522.2812 | 122.3053 | -122.0215 | 0.086975 | -0.0060272 | -0.0017881 | 0.055189 | 0.052199 | 0.0040632 | -0.0083335 | -0.0048985 | -0.011261 | 0.01113 | 0.00080103 | 0.0045993 | -0.012655 | 0.020935 | -0.0022794 | -21.1075 | -0.041199 | -122.1542 | -0.022888 | -121.2616 | -122.0581 | -122.0673 | 0.032043 | 0.054932 | -0.073242 | 0.036621 | 0.16022 | 0.091553 | 0.12817 | -0.13275 | -0.12817 | -0.10986 | 0.75989 | -0.045777 | -0.036621 | 0.086975 | 0.096131 | 121.9482 | -0.032043 | -0.050354 | 122.1817 | 122.1497 | 122.113 | 0.20142 | 0.16479 | 0.89264 | 122.1313 | 0.23346 | 0.10986 | 122.113 | 0.12817 | 121.9803 | 122.0764 | -122.2412 | -0.16022 | 121.9986 | 122.0581 | 100.914 | 122.0535
2524.0469 | 122.3511 | -122.0261 | 0.07782 | -0.0060272 | -0.0022153 | 0.053267 | 0.051344 | 0.004704 | -0.0087607 | 1.4934e-05 | -0.0051575 | 0.013052 | 0.0035782 | 0.0071627 | -0.013937 | 0.020721 | 0.000925 | -21.3043 | -0.036621 | -122.1497 | 0.018311 | -121.2296 | -122.0261 | -122.0398 | 0.091553 | 0.032043 | -0.068665 | 0.082397 | 0.20599 | 0.1236 | 0.14648 | -0.1236 | -0.11444 | -0.059509 | 0.79651 | -0.013733 | 0 | 0.10986 | 0.1236 | 121.9574 | -0.045777 | 0.004577 | 122.2321 | 122.1725 | 122.1497 | 0.21515 | 0.19226 | 0.92011 | 122.168 | 0.27466 | 0.15106 | 122.113 | 0.10071 | 121.9894 | 122.0581 | -122.2275 | -0.14649 | 122.0444 | 122.1085 | 100.7217 | 122.1176
2525.7344 | 122.3557 | -122.0352 | 0.07782 | -0.013657 | -0.0009335 | 0.053053 | 0.051558 | -0.0017048 | -0.0094015 | -0.0027621 | -0.0051575 | 0.011557 | 0.0035782 | 0.0065219 | -0.016287 | 0.021576 | -0.0009976 | -21.5378 | -0.041199 | -122.1634 | 0.036621 | -121.2204 | -122.0261 | -122.0352 | 0.12817 | 0.018311 | -0.045776 | 0.091553 | 0.2243 | 0.14191 | 0.16022 | -0.12817 | -0.11902 | -0.041199 | 0.81482 | 0 | 0.009155 | 0.12817 | 0.13733 | 121.9894 | -0.059509 | 0.013733 | 122.2595 | 122.1954 | 122.1771 | 0.20599 | 0.18768 | 0.94299 | 122.2 | 0.27008 | 0.13733 | 122.1222 | 0.064087 | 121.994 | 122.0535 | -122.2412 | -0.1236 | 122.0718 | 122.1268 | 100.4974 | 122.1634
2527.4844 | 122.3419 | -122.0261 | 0.086975 | 0.0016023 | -0.0028561 | 0.053694 | 0.051344 | -0.00042301 | -0.0083335 | -0.0027621 | -0.0021057 | 0.010702 | 0.0027236 | 0.0041721 | -0.017782 | 0.022003 | -0.0044156 | -21.8765 | -0.041199 | -122.1588 | -0.009155 | -121.257 | -122.0398 | -122.049 | 0.082397 | 0.045776 | -0.07782 | 0.059509 | 0.18768 | 0.11444 | 0.14648 | -0.13275 | -0.12817 | -0.09613 | 0.76904 | -0.022888 | -0.013733 | 0.10986 | 0.11902 | 121.9482 | -0.041199 | -0.027466 | 122.2137 | 122.1725 | 122.1405 | 0.2243 | 0.19226 | 0.90179 | 122.1497 | 0.2655 | 0.13733 | 122.1176 | 0.1236 | 121.9849 | 122.0718 | -122.2458 | -0.16479 | 122.0169 | 122.0856 | 100.1495 | 122.1085
2529.2344 | 122.2549 | -122.0627 | 0.09613 | -0.0060272 | -0.0017881 | 0.05348 | 0.054976 | 0.0014996 | -0.0081197 | -0.0055393 | -0.0051575 | 0.016043 | 0.0033646 | 0.0067355 | -0.015859 | 0.022644 | -0.0027066 | -22.11 | -0.009155 | -122.1954 | -0.027466 | -121.2891 | -122.1085 | -122.1176 | 0.032043 | 0.068665 | -0.07782 | 0.022888 | 0.12817 | 0.013733 | 0.086975 | -0.13275 | -0.10528 | -0.1236 | 0.77362 | -0.054932 | -0.045776 | 0.07782 | 0.086976 | 121.9849 | -0.027465 | -0.073242 | 122.1909 | 122.1497 | 122.0764 | 0.16479 | 0.091553 | 0.90637 | 122.168 | 0.20599 | 0.10071 | 122.1863 | 0.14649 | 122.0535 | 122.1313 | -122.2916 | -0.17395 | 122.0352 | 122.0856 | 99.9527 | 122.0947
2531 | 122.2504 | -122.0764 | 0.10986 | 0.0016023 | -0.0015743 | 0.054335 | 0.054121 | -0.0029864 | -0.01282 | -0.0019077 | -0.0082093 | 0.01348 | 0.0050736 | 0.0084445 | -0.014364 | 0.020721 | -0.0016384 | -22.3389 | 0.009155 | -122.2092 | -0.064087 | -121.3394 | -122.1313 | -122.1497 | -0.036621 | 0.064087 | -0.086975 | -0.018311 | 0.10529 | -0.009155 | 0.068665 | -0.13275 | -0.10071 | -0.17395 | 0.737 | -0.073242 | -0.054932 | 0.059509 | 0.077819 | 121.9894 | -0.045776 | -0.12817 | 122.1817 | 122.1451 | 122.0673 | 0.15564 | 0.07782 | 0.86975 | 122.1451 | 0.19226 | 0.068664 | 122.2183 | 0.15106 | 122.0856 | 122.1405 | -122.319 | -0.19684 | 122.0123 | 122.0581 | 99.7375 | 122.0398
2532.7031 | 122.374 | -122.0261 | 0.082397 | -0.013657 | -0.0026425 | 0.054762 | 0.05284 | -0.002132 | -0.0061971 | -0.0042575 | -0.0051575 | 0.0094208 | 0.00058743 | 0.0018221 | -0.015859 | 0.020294 | -0.0003568 | -22.6089 | -0.036621 | -122.1542 | 0.045776 | -121.1609 | -122.0032 | -122.0261 | 0.13733 | 0.032043 | -0.054932 | 0.082397 | 0.21515 | 0.14191 | 0.14191 | -0.12817 | -0.11902 | -0.036621 | 0.86517 | 0 | 0.022888 | 0.12817 | 0.15106 | 121.9711 | -0.050354 | 0 | 122.2412 | 122.168 | 122.168 | 0.19684 | 0.19684 | 0.99335 | 122.2 | 0.27008 | 0.13733 | 122.1176 | 0.086975 | 121.9894 | 122.0581 | -122.2366 | -0.13733 | 122.0718 | 122.1085 | 99.4171 | 122.1634
2534.4688 | 122.3282 | -122.0169 | 0.082397 | -0.0060272 | -0.0037107 | 0.053267 | 0.05049 | 0.0019268 | -0.0089743 | -0.0021213 | -0.0051575 | 0.012411 | 0.00058743 | 0.0073763 | -0.014364 | 0.02179 | 0.0013522 | -22.9294 | -0.050354 | -122.1588 | 0.068665 | -121.1746 | -122.0078 | -122.0261 | 0.11444 | 0.041199 | -0.054932 | 0.086975 | 0.21973 | 0.14191 | 0.14191 | -0.14191 | -0.13275 | -0.013732 | 0.84229 | -0.009155 | 0.009156 | 0.13275 | 0.15106 | 121.962 | -0.041198 | 0.004578 | 122.2366 | 122.1588 | 122.1588 | 0.19684 | 0.19684 | 0.98419 | 122.2275 | 0.27466 | 0.14191 | 122.1085 | 0.096131 | 121.9666 | 122.0581 | -122.2412 | -0.13733 | 122.0856 | 122.1039 | 99.0875 | 122.1313
2536.1562 | 122.3648 | -122.0215 | 0.073242 | -0.013657 | -0.0045651 | 0.054762 | 0.051558 | -0.0010638 | -0.0096151 | -0.0036167 | -0.0051575 | 0.0094208 | 0.0035782 | 0.0011813 | -0.017141 | 0.020294 | 0.0013522 | -23.1949 | -0.013733 | -122.1542 | 0.054932 | -121.1746 | -122.0032 | -122.0261 | 0.13733 | 0.018311 | -0.041199 | 0.10071 | 0.25177 | 0.15564 | 0.15106 | -0.13275 | -0.086975 | -0.01831 | 0.84686 | -0.004578 | 0.01831 | 0.12817 | 0.15106 | 121.9803 | -0.054931 | 0.027466 | 122.2733 | 122.1725 | 122.1771 | 0.19226 | 0.19684 | 0.97961 | 122.2092 | 0.29297 | 0.14191 | 122.1405 | 0.05951 | 122.0078 | 122.0398 | -122.2275 | -0.11444 | 122.0764 | 122.1222 | 98.8266 | 122.1588
2537.9219 | 121.2524 | -50.7202 | 56.3553 | -0.074692 | -0.018664 | 0.10924 | -0.012956 | 0.046574 | 0.057035 | 0.050857 | 0.043671 | 0.029715 | 0.010841 | 0.0056675 | 0.26762 | 0.037811 | 0.031473 | 0.10071 | 36.7538 | -29.2328 | 38.1042 | -27.3743 | -24.4217 | -21.3821 | 0.10071 | 0.09613 | -0.10986 | 0.09613 | 0.10529 | 0.10071 | 0.10071 | 21.4874 | -19.6014 | -18.251 | 23.3459 | 29.3381 | 26.2985 | 7.8506 | 4.8111 | 50.6104 | -56.2592 | -56.2592 | 50.8255 | 50.8209 | 50.8209 | 0.21057 | 0.21057 | 1.8585 | 67.337 | 0.21515 | 0.20599 | 65.9866 | 0.20599 | 87.4741 | 50.8163 | -85.5881 | -56.4651 | 88.8245 | 50.8163 | 50.8209 | 50.8209
2539.6719 | 121.6736 | -0.082397 | 121.2067 | 0.16182 | -0.0022153 | 0.051985 | 0.050917 | -0.0029864 | -0.0079061 | -0.00041227 | -0.11807 | 0.010062 | 0.00251 | 0.0097263 | -0.013082 | 0.020294 | -0.0029202 | 6.0837 | 121.019 | 0.004578 | 121.2982 | 0.059509 | -0.16479 | -0.13275 | 0.022888 | -0.13733 | 0.2655 | 0.041199 | 0.13275 | 0.041199 | 0.086975 | 0.086975 | -0.18768 | 0.091553 | 0.14191 | -0.050354 | -0.082398 | -0.13733 | -0.16937 | 0.3479 | -121.344 | -121.1655 | 0.21515 | 0.16937 | 0.1236 | -0.17853 | -0.2243 | 0.054931 | 121.2936 | -0.13275 | -0.2243 | 121.0144 | -0.40283 | 121.1014 | -0.054932 | -121.2021 | -120.9412 | 121.3806 | 0.1236 | 6.1661 | 0.10528
2541.4219 | 121.7697 | -0.09613 | 121.1334 | 0.16182 | -0.0030697 | 0.051131 | 0.050063 | -0.0046954 | -0.0091879 | -0.0027621 | -0.11502 | 0.009848 | 0.0018692 | -0.0022367 | -0.013937 | 0.021576 | -0.0001432 | 5.9372 | 121.4035 | -0.1236 | 121.431 | 0.11444 | -0.11902 | -0.086975 | 0.054932 | 0.009155 | 0.19684 | 0.036621 | 0.15106 | 0.073242 | 0.10529 | -0.027466 | 0.27008 | 0.29755 | 0.21057 | 0.009155 | -0.022889 | 0.036621 | 0.004577 | 0.29297 | -121.1243 | -121.0968 | 0.24719 | 0.20142 | 0.16937 | -0.091552 | -0.1236 | 0.23804 | 121.5546 | -0.045776 | -0.16022 | 121.5271 | -0.18768 | 121.4996 | 0.10528 | -121.257 | -120.9366 | 121.5271 | 0.13275 | 6.0333 | 0.15106
2543.125 | 121.3348 | -0.054932 | 117.8741 | 0.14656 | -0.014178 | 0.047926 | 0.043013 | -0.0012774 | -0.010897 | -0.0031895 | -0.014313 | 0.0094208 | 0.0035782 | 0.0078037 | -0.014364 | 0.022003 | -0.0016384 | 5.6671 | 121.4859 | -0.09613 | 120.8542 | -0.23346 | -0.3067 | 0.050354 | 0.022888 | 0.013733 | 0.25635 | 0.032043 | -0.082397 | -0.35706 | -0.23804 | -0.041198 | 3.6118 | 2.98 | -0.17853 | 0.10529 | -0.25177 | 0.14648 | -0.21057 | 0.31128 | -117.8604 | -117.8421 | -0.027465 | -0.1831 | -0.30212 | -0.49439 | -0.6134 | -0.13733 | 120.9503 | -0.33875 | -0.22431 | 121.582 | -0.24262 | 121.5408 | 0.068665 | -117.9703 | -117.6178 | 120.9091 | 0.086975 | 5.722 | 0.07782
2544.875 | 117.1509 | -40.6631 | 76.6342 | 0.0016023 | -0.0041379 | 0.051131 | 0.049635 | 0.0023542 | -0.010897 | 0.00022853 | -0.0051575 | 0.012411 | 0.00058743 | 0.00054052 | -0.014791 | 0.020294 | 0.0002842 | -5.5344 | 72.583 | -42.7872 | 73.4024 | -42.2562 | -42.9062 | -42.8421 | 0.082397 | -0.28381 | -0.027466 | 0.027466 | -0.027466 | -0.23804 | -0.23804 | -2.124 | -4.0512 | -3.2318 | -1.593 | -2.179 | -2.243 | -0.054932 | -0.11902 | 40.6357 | -76.918 | -76.6067 | 40.6357 | 40.4251 | 40.4251 | -0.21057 | -0.21057 | 0.53101 | 116.1896 | 0 | 0.054932 | 115.3702 | -0.25635 | 113.2462 | 40.3793 | -119.4214 | -76.6617 | 114.0656 | 40.6906 | 35.1288 | 40.7455
2546.5625 | 121.3989 | -0.42572 | 120.0256 | -0.1815 | -0.0026425 | 0.051985 | 0.050276 | 0.00021799 | -0.010683 | -0.0051121 | -0.18826 | 0.0094208 | 0.0010146 | 0.0043857 | -0.013937 | 0.020935 | 0.0002842 | 5.9235 | 120.3049 | -0.22888 | 120.5933 | -0.24719 | -0.52185 | -0.54016 | 0.10529 | -0.14191 | 0.22888 | 0.07782 | 0.13275 | -0.041199 | -0.050354 | 0.19684 | 0.27924 | 0.56763 | 0.17853 | -0.11444 | -0.096131 | -0.31128 | -0.29297 | 0.6546 | -120.1675 | -119.9478 | 0.55847 | 0.37537 | 0.38452 | -0.27924 | -0.27008 | -0.01831 | 120.8221 | -0.096131 | -0.15106 | 120.5338 | -0.37079 | 120.7306 | 0.28381 | -120.2545 | -119.7968 | 121.019 | 0.50354 | 6.3492 | 0.53101
2548.3125 | 121.2845 | -0.27466 | 115.8234 | -0.45616 | -0.0067013 | 0.047926 | -0.01317 | 0.048497 | -0.021792 | 0.05278 | 0.061981 | 0.030356 | -0.0015488 | 0.0067355 | 0.26826 | 0.038879 | 0.032541 | 5.69 | 104.9149 | -0.17395 | 110.5499 | 0.21515 | 0.16479 | 0.13275 | -0.073242 | -0.3067 | -0.09613 | 0.041199 | 0.009155 | 0.10071 | 0.11902 | 0.10071 | -10.9085 | -5.2734 | 0.48981 | 0.40741 | 0.43945 | 0.3067 | 0.33874 | 0.17853 | -116.1301 | -115.7822 | 0.28381 | 0.39368 | 0.37537 | 0.21515 | 0.19684 | 0.3891 | 110.7239 | 0.10528 | 0.13733 | 105.0888 | -0.21057 | 105.1895 | -0.032044 | -115.9973 | -115.9195 | 110.8246 | 0.31586 | 5.9647 | 0.20142
2550.0781 | 109.1034 | 0.091553 | 102.7176 | 0.13893 | -0.019519 | 0.04109 | 0.038741 | -0.0087542 | -0.016665 | -0.0063937 | 0.055878 | 0.00023504 | -0.0034714 | -0.0015957 | -0.011801 | 0.022217 | 0.0022068 | 6.2576 | 120.2682 | 0.013733 | 110.9344 | -0.20142 | 0.10986 | 0.11902 | -0.1831 | -0.013733 | -0.091553 | -0.25177 | 0.009155 | -0.082397 | 0 | -0.07782 | 17.5507 | 8.2169 | -0.29297 | 0.027466 | 0.01831 | 0.10529 | 0.09613 | -0.18311 | -102.7313 | -102.9694 | -0.082398 | -0.091553 | -0.17395 | 0.091553 | 0.009156 | -0.21515 | 110.9207 | 0.10071 | -0.16022 | 120.2545 | 0.07782 | 120.1767 | -0.10529 | -102.7039 | -102.8091 | 110.8429 | -0.34332 | 6.1661 | -0.27466
2551.7969 | 121.2708 | -0.15564 | 121.0693 | 0.12367 | -0.0017881 | 0.051771 | 0.047499 | -0.0017048 | -0.0074789 | -0.0036167 | -0.047882 | 0.0094208 | 0.0018692 | -0.0022367 | -0.014791 | 0.022644 | -0.0005704 | 5.6168 | 120.5429 | 0.013733 | 120.2957 | -0.3067 | -0.46234 | -0.16022 | 0.086975 | -0.33417 | 0.068665 | 0.073242 | -0.10071 | -0.24719 | -0.16937 | 0.16937 | -0.52643 | -0.77362 | -0.15106 | -0.004577 | -0.3067 | -0.17395 | -0.47607 | 0.22431 | -121.4035 | -120.9961 | 0.054932 | -0.013733 | -0.091552 | -0.23804 | -0.31586 | -0.32043 | 120.282 | -0.16937 | 0.004577 | 120.5292 | -0.40283 | 120.6985 | -0.17853 | -121.0556 | -121.0007 | 120.4514 | 0.22888 | 5.7724 | 0.24261
2553.5625 | 121.2662 | -0.1831 | 120.3964 | 0.11604 | 0.028546 | -0.014665 | 0.054976 | -0.013881 | -0.019656 | -0.023056 | 0.043671 | 0.0070708 | -0.013298 | -0.0065091 | -0.023123 | 0.015167 | -0.013601 | 0.15106 | 120.5612 | 0.054932 | 100.6119 | 0.14191 | 0.10071 | 0.10071 | -0.17395 | -0.009155 | -0.091553 | -0.1236 | -0.086975 | 0.091553 | 0.10986 | 0.23804 | 0.16479 | -19.7845 | 0.32501 | 0.28381 | 0.28381 | 0.045776 | 0.045776 | 0.091552 | -120.4056 | -120.52 | 0.09613 | 0.29297 | 0.27466 | 0.20142 | 0.18311 | 0.086975 | 100.5569 | 0.004578 | -0.032043 | 120.5063 | 0.082398 | 120.7443 | 0.17395 | -120.3415 | -120.488 | 100.795 | 0.059509 | 0.33417 | 0.009155
2555.3281 | 121.3211 | -0.19226 | 106.7551 | 0.10841 | 0.027692 | 0.10945 | -0.012956 | 0.04636 | 0.056608 | 0.051071 | 0.046722 | 0.029074 | 0.010628 | 0.0056675 | 0.2674 | 0.037598 | 0.031259 | 0.09613 | 120.7397 | -0.068665 | 91.0126 | 0.11444 | 0.086975 | 0.091553 | -0.013733 | -0.17395 | -0.10071 | -0.14648 | 0.09613 | 0.10071 | 0.10071 | 0.1236 | 13.9847 | -15.7425 | 0.3067 | 0.28381 | 0.27924 | 0.16022 | 0.15564 | 0.091553 | -106.929 | -106.9016 | 0.28839 | 0.29297 | 0.29297 | 0.20142 | 0.20142 | 0.18311 | 91.0812 | 0.19684 | -0.045776 | 120.8084 | -0.073242 | 120.932 | 0.018311 | -106.8237 | -106.8558 | 91.2048 | 0.045777 | 0.28839 | 0.17853
2557.0938 | 120.7809 | -61.2076 | 59.0286 | 0.12367 | -0.012469 | 0.047926 | 0.045576 | -0.001491 | -0.0094015 | -0.0044711 | -0.27066 | 0.0094208 | 0.003151 | 0.0024631 | -0.0165 | 0.022217 | 0.0013522 | -10.9772 | 59.1568 | -60.7819 | 58.5297 | -61.2167 | -61.8668 | -59.0332 | 0.022888 | -0.3067 | 0 | 0 | -0.25177 | -0.28381 | -0.1831 | 0.42572 | 0.12817 | -0.49896 | -0.009155 | 2.1744 | -0.65918 | 1.7487 | -1.0849 | 61.2076 | -59.3353 | -59.0286 | 60.9558 | 61.0245 | 60.9238 | -0.1831 | -0.28381 | -0.43488 | 119.3115 | -0.25177 | 0 | 119.9387 | -0.3067 | 120.3644 | 60.9009 | -119.8105 | -59.0286 | 119.7372 | 61.2076 | 50.2304 | 61.2305
2558.7969 | 120.9503 | -116.3452 | 4.1107 | -0.0060272 | -0.0052059 | 0.054549 | 0.051985 | -0.0046954 | -0.0083335 | -0.0010531 | -0.0051575 | 0.012198 | 0.001442 | 0.00075412 | -0.012441 | 0.020081 | 0.0030612 | -27.0355 | 4.0558 | -116.5329 | 4.0375 | -115.4938 | -116.3086 | -116.272 | 0.027466 | -0.059509 | 0.23346 | 0.041199 | 0.14648 | 0.054932 | 0.086975 | -0.18768 | -0.054932 | -0.073242 | 0.85144 | 0.073242 | 0.036621 | 0.26093 | 0.2243 | 116.5787 | -4.1702 | -4.0695 | 116.4917 | 116.4322 | 116.4001 | -0.14648 | -0.17853 | 1.0391 | 120.5704 | -0.086975 | -0.19226 | 120.5887 | -0.29297 | 120.401 | 116.2857 | -120.6436 | -3.8773 | 120.3827 | 116.3864 | 89.3097 | 116.3727
2560.5625 | 120.9412 | -61.0428 | 59.4955 | -0.0060272 | -0.0022153 | 0.052412 | 0.051985 | -0.001491 | -0.0083335 | -0.0046847 | -0.063141 | 0.0085662 | 0.0029372 | -0.00010048 | -0.015646 | 0.020081 | 0.0002842 | -10.5927 | 59.4315 | -60.4523 | 59.4681 | -60.4294 | -60.9604 | -60.8734 | 0.10986 | -0.14191 | 0.21515 | 0.068665 | 0.068665 | -0.059509 | -0.059509 | 0.59051 | -0.064086 | -0.027465 | 0.6134 | 0.16937 | 0.082398 | -0.42114 | -0.50812 | 61.2579 | -59.6375 | -59.4269 | 61.1115 | 60.9833 | 60.9833 | -0.27466 | -0.27466 | 0.022889 | 119.9204 | -0.14648 | -0.14648 | 119.8837 | -0.35706 | 120.4742 | 60.9009 | -119.9478 | -59.2804 | 120.5109 | 61.1115 | 50.4501 | 61.1526
2562.2969 | 120.9091 | -114.4318 | 6.0104 | -0.013657 | 0.0024845 | 0.056685 | 0.050276 | -0.0051226 | -0.017947 | -0.011307 | -0.0082093 | 0.0083526 | -0.0024032 | -0.0043729 | -0.015432 | 0.020508 | -0.0050564 | -26.5228 | 6.0471 | -114.6286 | 6.0196 | -102.7817 | -105.5923 | -103.7613 | -0.018311 | -0.32044 | 0.022888 | -0.15564 | -0.041199 | -0.086975 | -0.041199 | -0.19684 | 0.036621 | 0.009155 | 11.6501 | 10.6705 | 8.8394 | 10.8673 | 9.0363 | 114.4547 | -6.3309 | -6.1661 | 114.3906 | 114.3906 | 114.3448 | -0.064087 | -0.10986 | 11.8469 | 120.6482 | -0.064087 | -0.17853 | 120.6757 | -0.34332 | 120.4788 | 114.1113 | -120.639 | -5.9875 | 120.4514 | 114.2761 | 87.9089 | 114.4135
2564.0625 | 121.106 | -116.2079 | 4.4449 | -0.013657 | -0.0005063 | 0.053694 | 0.051344 | -0.0044818 | -0.011111 | -0.00019867 | -0.0021057 | 0.010702 | 0.0016556 | -0.0037321 | -0.01351 | 0.020294 | -0.002493 | -26.9073 | 4.3442 | -116.4139 | 4.4266 | -115.1962 | -116.0156 | -115.9836 | 0.10986 | 0.022888 | 0.21515 | 0.091553 | 0.18768 | 0.004578 | -0.013733 | -0.20599 | -0.10071 | -0.01831 | 1.0117 | 0.2243 | 0.19226 | 0.4303 | 0.39825 | 116.423 | -4.422 | -4.3533 | 116.3956 | 116.1942 | 116.2125 | -0.22888 | -0.21057 | 1.2177 | 120.8405 | -0.027466 | -0.1236 | 120.7581 | -0.19226 | 120.5521 | 116.2308 | -120.8588 | -4.2297 | 120.6345 | 116.2994 | 89.3005 | 116.3177
2565.75 | 120.1721 | -0.10529 | 120.3918 | 0.15419 | -0.0043515 | 0.050063 | 0.049635 | -0.0032 | -0.0096151 | -0.0031895 | -0.16385 | 0.0096344 | 0.00058743 | -0.0018093 | -0.016073 | 0.020721 | -0.0005704 | 7.8644 | 119.4809 | 0.14191 | 120.0577 | 0.12817 | -0.11902 | -0.10986 | 0.12817 | -0.33417 | 0.068665 | 0.082397 | 0.14191 | 0.050354 | 0.068665 | 0.24719 | -0.91095 | -0.33417 | 0.23346 | -0.004577 | -0.013733 | -0.25177 | -0.26093 | 0.17395 | -120.726 | -120.3094 | 0.24719 | 0.17395 | 0.15564 | 0 | -0.018311 | -0.013733 | 119.9158 | 0.073242 | 0.013732 | 119.339 | -0.40283 | 119.5862 | -0.22888 | -120.2499 | -120.3232 | 120.163 | 0.18768 | 7.9697 | 0.23346
2567.5156 | 120.9045 | -0.10071 | 119.9387 | 0.11604 | -0.0030697 | 0.051558 | 0.049422 | -0.0023456 | -0.0094015 | -0.0027621 | -0.12112 | 0.01113 | 0.00251 | 0.00032692 | -0.01351 | 0.017944 | -0.0037748 | 7.0633 | 119.8929 | 0.045776 | 120.5658 | 0.068665 | -0.16022 | -0.1236 | 0.027466 | -0.14648 | 0.27008 | 0.009155 | 0.1236 | 0.045776 | 0.091553 | 0.14648 | -0.045777 | 0.62714 | 0.16937 | -0.022888 | -0.059509 | -0.16937 | -0.20599 | 0.37079 | -120.0851 | -119.9295 | 0.2243 | 0.19226 | 0.14648 | -0.17853 | -0.22431 | 0.022889 | 120.52 | -0.14649 | -0.26093 | 119.8471 | -0.41657 | 119.9936 | -0.045776 | -119.8929 | -119.6686 | 120.6665 | 0.10986 | 7.164 | 0.12817
2569.2188 | 121.5637 | 0.022888 | 91.3605 | 0.11604 | -0.0045651 | 0.034041 | 0.080183 | -0.010463 | -0.021365 | -0.013443 | 0.040619 | 0.029074 | -0.0021896 | -0.0024503 | 0.10697 | 0.014313 | 0.031259 | 7.338 | 108.078 | 0.009155 | 109.7031 | 0.16022 | 0.10071 | 0.10071 | -0.23804 | 0.004578 | -0.09613 | -0.12817 | 0.086975 | 0.09613 | 0.10071 | -0.013733 | 16.7175 | 18.3426 | 0.13733 | 0.07782 | 0.07782 | 0.091553 | 0.091553 | -0.11902 | -91.3559 | -91.4886 | 0.064087 | 0.07782 | 0.073242 | 0.19684 | 0.19226 | 0.15106 | 109.6939 | 0.1831 | -0.032044 | 108.0688 | 0.10071 | 108.0551 | -0.01831 | -91.3513 | -91.4566 | 109.6802 | -0.15106 | 7.3151 | -0.26093
2570.9688 | 120.4147 | -0.059509 | 120.2271 | 0.11604 | 0.0014163 | 0.053694 | 0.051344 | -0.0019184 | -0.0085471 | -0.0040439 | -0.2493 | 0.010062 | 0.0016556 | 0.0045993 | -0.016073 | 0.020081 | -0.0020658 | 6.9351 | 120.7443 | 0.032043 | 120.3873 | 0.050354 | -0.29755 | -0.31586 | 0.13275 | -0.12817 | 0.32501 | 0.091553 | 0.068665 | -0.068665 | -0.027466 | 0.091552 | 0.51727 | 0.16022 | 0.10986 | -0.25635 | -0.23804 | -0.3479 | -0.32959 | 0.38452 | -120.3552 | -120.1355 | 0.12817 | 0.032043 | -0.009156 | -0.35248 | -0.39368 | 0.018311 | 120.3552 | -0.25635 | -0.23346 | 120.7123 | -0.45319 | 120.8038 | -0.068665 | -120.195 | -119.902 | 120.4468 | 0.15106 | 6.9946 | 0.19226
2572.7188 | 120.5612 | -0.07782 | 120.639 | 0.10841 | -0.0015743 | 0.052412 | 0.051558 | -0.0023456 | -0.0074789 | -0.0051121 | -0.19437 | 0.0087798 | 0.0022964 | -0.0011685 | -0.01351 | 0.019226 | 0.0011386 | 7.0404 | 120.7626 | -0.068665 | 120.726 | 0.16479 | -0.19684 | -0.21973 | 0.12817 | -0.036621 | 0.3067 | 0.086975 | 0.14191 | -0.004578 | 0.027466 | 0.009155 | 0.1236 | 0.086975 | 0.24261 | -0.14191 | -0.11902 | -0.15106 | -0.12817 | 0.38452 | -120.6757 | -120.5521 | 0.21973 | 0.10529 | 0.073242 | -0.27924 | -0.31128 | 0.23346 | 120.7947 | -0.16479 | -0.21973 | 120.8313 | -0.34332 | 120.8405 | 0.041199 | -120.7077 | -120.3323 | 120.8038 | 0.16479 | 7.1182 | 0.20599
2574.4688 | 120.5383 | -0.032043 | 120.4926 | 0.10078 | 0.0001345 | 0.050276 | 0.051344 | -0.00020941 | -0.0094015 | -0.0034031 | -0.21878 | 0.010489 | 0.0020828 | 0.0067355 | -0.015859 | 0.01944 | 0.000925 | 7.0953 | 120.8588 | -0.11444 | 120.8542 | 0.16937 | -0.19684 | -0.23804 | 0.1236 | 0.018311 | 0.24261 | 0.073242 | 0.14648 | -0.036621 | 0.018311 | -0.082398 | 0.36621 | 0.36163 | 0.20142 | -0.20599 | -0.1648 | -0.1236 | -0.082397 | 0.27466 | -120.4742 | -120.4193 | 0.17853 | 0.050354 | -0.004578 | -0.2243 | -0.27924 | 0.28381 | 120.9686 | -0.096131 | -0.16937 | 120.9732 | -0.2243 | 120.8908 | 0.050354 | -120.607 | -120.2499 | 120.8862 | 0.10529 | 7.1274 | 0.15564
2576.2188 | 104.0359 | 0.09613 | 121.1472 | 0.10841 | 0.027692 | 0.049635 | 0.038527 | -0.014308 | -0.025851 | -0.01622 | 0.043671 | -0.0019012 | -0.0096664 | 0.0022495 | -0.020346 | 0.01709 | -0.00527 | 6.9077 | 120.6482 | -0.12817 | 120.3918 | -0.29297 | 0.09613 | 0.10071 | -0.041199 | -0.009155 | 0.19684 | -0.1236 | -0.32501 | 0.059509 | 0.13733 | -0.2243 | -0.49896 | -0.75531 | -0.3891 | 0.004578 | 0 | 0.22888 | 0.2243 | 0.10071 | -121.1563 | -121.2708 | -0.42114 | 0.041199 | -0.036621 | -0.059509 | -0.13733 | -0.16479 | 120.52 | -0.52185 | -0.32043 | 120.7764 | -0.20599 | 120.5521 | -0.10528 | -121.2753 | -120.9503 | 120.2957 | -0.21973 | 6.8115 | -0.13733
2577.9844 | 120.4742 | -0.073242 | 120.2957 | 0.10078 | -0.0013607 | 0.049422 | 0.049849 | 0.00043159 | -0.0081197 | -0.0036167 | -0.15775 | 0.011343 | 0.0016556 | 0.00096772 | -0.01351 | 0.019226 | -0.0039884 | 7.3105 | 120.3323 | -0.14191 | 120.9824 | 0.20142 | -0.050354 | -0.11902 | 0.13275 | 0.018311 | 0.12817 | 0.07782 | 0.21057 | 0.032043 | 0.004578 | -0.068665 | 0.036621 | 0.68665 | 0.27466 | -0.045777 | 0.022888 | 0.022888 | 0.091553 | 0.20142 | -120.2774 | -120.2179 | 0.28381 | 0.07782 | 0.10529 | -0.1236 | -0.096131 | 0.34332 | 121.1243 | 0.082397 | -0.050354 | 120.4742 | -0.10986 | 120.4056 | 0.091553 | -120.4376 | -120.1675 | 121.0556 | 0.15106 | 7.3837 | 0.20599
2579.7344 | 112.7747 | 0.17853 | 105.4596 | 0.10078 | -0.016314 | 0.044508 | 0.044081 | -0.00020941 | -0.013247 | -0.0059665 | 0.058929 | 0.0051482 | 0.00058743 | 0.0090853 | -0.013723 | 0.020721 | -0.0005704 | 7.1594 | 120.9869 | -0.18768 | 120.3369 | -0.050354 | -0.53558 | 0.086975 | -0.009155 | 0.064087 | 0.10986 | 0.009155 | -0.10529 | -0.36163 | -0.036621 | -0.36621 | 15.5273 | 14.8773 | -0.22888 | -0.091553 | -0.71411 | 0.27466 | -0.3479 | -0.068665 | -105.3955 | -105.4504 | -0.28381 | -0.21515 | -0.54016 | -0.14648 | -0.4715 | 0.13733 | 120.5246 | -0.21515 | -0.10071 | 121.1746 | -0.045776 | 120.8084 | -0.11444 | -105.6473 | -105.3497 | 120.1584 | -0.16937 | 6.9809 | -0.18768
2581.4219 | 120.8771 | 0.050354 | 120.3232 | 0.10841 | 0.0014163 | 0.053694 | 0.05284 | -0.002132 | -0.0074789 | -0.0059665 | -0.25235 | 0.011343 | -0.0011216 | 0.0028903 | -0.013937 | 0.024567 | 0.0013522 | 7.4249 | 120.9778 | -0.14648 | 120.813 | 0.17395 | -0.1831 | -0.33417 | 0.10529 | 0.022888 | 0.032043 | 0.10986 | 0.15106 | -0.064087 | -0.086975 | -0.19684 | 0.6546 | 0.48981 | 0.1236 | -0.38452 | -0.23346 | -0.18768 | -0.036621 | -0.018311 | -120.3003 | -120.2133 | 0.10071 | -0.13733 | -0.11444 | -0.11902 | -0.09613 | 0.32043 | 120.9595 | 0.11902 | 0.07782 | 121.1243 | -0.009155 | 120.9274 | -0.027466 | -120.4697 | -120.2911 | 120.7626 | 0.059509 | 7.3746 | 0.054932
2583.1875 | 121.3669 | 0.036621 | 106.7139 | 0.10078 | -0.0039243 | 0.051131 | 0.048994 | -0.0010638 | -0.013033 | -0.0057529 | -0.20047 | 0.0074982 | 0.0022964 | -0.0039457 | -0.01351 | 0.019226 | 0.0013522 | 7.5531 | 121.0236 | -0.14648 | 121.0327 | 0.16937 | -0.064087 | -0.21057 | 0.073242 | 0.036621 | 0.054932 | 0.027466 | 0.14191 | -0.10529 | -0.17853 | -0.18311 | 14.3097 | 14.3188 | 0.13275 | -0.24719 | -0.10071 | -0.064087 | 0.082397 | 0.018311 | -106.6772 | -106.6864 | 0.10529 | -0.21515 | -0.14191 | -0.23346 | -0.16022 | 0.31586 | 121.1792 | 0.086975 | -0.027466 | 121.17 | -0.018311 | 120.9869 | 0 | -106.8604 | -106.6589 | 120.9961 | -0.009155 | 7.5165 | 0.036621
2584.875 | 121.2799 | -0.086975 | 113.1866 | 0.10078 | -0.0009335 | 0.050276 | 0.052199 | -0.0032 | -0.010043 | -0.0057529 | -0.24319 | 0.010489 | 0.0037918 | 0.0018221 | -0.014364 | 0.019653 | -0.0009976 | 7.6263 | 120.813 | -0.027466 | 121.0327 | 0.14648 | -0.13275 | -0.29755 | 0.059509 | 0.054932 | 0.16022 | -0.004578 | 0.073242 | -0.23804 | -0.28381 | 0.059509 | 7.6263 | 7.8461 | 0.23346 | -0.21057 | -0.045776 | -0.27008 | -0.10529 | 0.24719 | -113.1317 | -113.1912 | 0.16022 | -0.19684 | -0.15106 | -0.44403 | -0.39825 | 0.17395 | 121.0602 | -0.086975 | -0.16479 | 120.8405 | -0.10528 | 120.9 | 0.14191 | -113.2141 | -113.0264 | 121.1197 | 0.082397 | 7.7133 | 0.14648
2586.625 | 121.051 | -0.018311 | 121.3623 | 0.093155 | -0.0017881 | 0.05049 | 0.047285 | 0.001286 | -0.0089743 | -0.00019867 | -0.084503 | 0.003653 | 0.0037918 | 0.0035311 | -0.010732 | 0.020081 | -0.0020658 | 7.6584 | 116.7801 | 0.036621 | 120.6665 | 0.022888 | -0.37537 | -0.19684 | -0.041199 | 0.068665 | 0.16022 | -0.032043 | -0.13733 | -0.10529 | 0.086975 | 0.054932 | -4.5822 | -0.6958 | 0.041199 | -0.17853 | -0.35705 | -0.23346 | -0.41199 | 0.17853 | -121.2936 | -121.3943 | -0.11902 | 0.10529 | -0.086975 | -0.073242 | -0.2655 | -0.013733 | 120.6299 | -0.29755 | -0.19226 | 116.7435 | -0.091552 | 116.7984 | 0.086976 | -121.3257 | -121.2021 | 120.6848 | -0.013732 | 7.6767 | -0.022888
2588.3906 | 121.4172 | -0.07782 | 121.2479 | 0.10078 | -0.0062741 | 0.049849 | 0.050276 | -0.001491 | -0.0087607 | -0.0040439 | -0.1669 | 0.012198 | 0.0012282 | 0.0048129 | -0.014364 | 0.021576 | -0.0020658 | 7.5806 | 121.1105 | -0.16022 | 120.8038 | 0.09613 | -0.22888 | -0.3479 | 0.064087 | 0.027466 | 0.032043 | 0.073242 | 0.14648 | -0.14648 | -0.21057 | -0.082397 | -0.13733 | -0.44403 | 0.17395 | -0.27008 | -0.15106 | -0.18768 | -0.068665 | 0.10986 | -121.2204 | -121.1746 | 0.2243 | -0.13275 | -0.068664 | -0.24261 | -0.17853 | 0.25635 | 120.9641 | 0.11444 | 0.041199 | 121.2708 | -0.004577 | 121.1884 | 0.10529 | -121.4081 | -121.2158 | 120.8817 | 0.15106 | 7.6584 | 0.14191
2590.1562 | 121.3303 | -0.12817 | 120.7443 | 0.10841 | -0.0020017 | 0.050917 | 0.050917 | -0.002132 | -0.010897 | -0.0044711 | -0.24625 | 0.012411 | 0.0052872 | -0.00052768 | -0.011587 | 0.020508 | -0.0033474 | 7.869 | 115.2878 | -0.027466 | 120.9549 | 0.082397 | -0.15564 | -0.35706 | -0.022888 | 0.059509 | 0.082397 | -0.032043 | 0.059509 | -0.26093 | -0.3067 | 0.10071 | -5.4565 | 0.21057 | 0.21057 | -0.22888 | -0.027466 | -0.32959 | -0.12817 | 0.21057 | -120.6848 | -120.7764 | 0.18768 | -0.17853 | -0.13275 | -0.3891 | -0.34332 | 0.10986 | 120.9824 | -0.022888 | -0.11444 | 115.3152 | -0.022888 | 115.416 | 0.18768 | -120.7718 | -120.6619 | 121.0831 | 0.096131 | 7.9971 | 0.10529
2591.9062 | 121.4859 | -0.19226 | 120.4971 | 0.11604 | -0.0024289 | 0.051344 | 0.050917 | -0.0010638 | -0.0089743 | -0.0036167 | -0.050934 | 0.010062 | 0.0012282 | -0.0018093 | -0.013082 | 0.022003 | -0.0009976 | 7.901 | 120.9595 | -0.2655 | 121.1334 | 0.14191 | -0.14191 | -0.091553 | 0.086975 | 0.041199 | -0.073242 | 0.07782 | 0.17853 | 0.10529 | 0.1236 | -0.073242 | 0.46234 | 0.63629 | 0.33417 | 0.10071 | 0.050354 | 0.17395 | 0.1236 | 0.11902 | -120.4559 | -120.4193 | 0.37079 | 0.31586 | 0.29755 | 0.19684 | 0.17853 | 0.40741 | 121.3989 | 0.25177 | 0.15106 | 121.225 | 0.11444 | 121.1517 | 0.23346 | -120.7626 | -120.5704 | 121.3257 | 0.27008 | 8.0933 | 0.27924
2593.6094 | 120.6894 | -0.10071 | 116.7114 | 0.062637 | 0.025556 | 0.079542 | -0.012956 | 0.047642 | -0.014742 | 0.05043 | 0.046722 | 0.02886 | 0.0099868 | 0.0056675 | 0.26719 | 0.037384 | 0.031473 | 7.7637 | 101.3672 | 0.064087 | 119.7098 | -0.018311 | -0.43488 | 0.10071 | -0.13733 | -0.20142 | -0.09613 | -0.050354 | -0.20142 | 0.10071 | 0.09613 | 0.1648 | -15.3442 | 2.9984 | 0.082397 | 0.20142 | -0.33417 | 0.036621 | -0.49896 | 0.004578 | -116.9128 | -116.7618 | -0.10071 | 0.19684 | 0.20142 | 0.19226 | 0.19684 | -0.082398 | 119.6457 | -0.10529 | 0.045776 | 101.3031 | -0.10529 | 101.4679 | -0.10071 | -116.6473 | -116.8076 | 119.8105 | 0.050354 | 7.8644 | -0.036621
2595.3594 | 120.8725 | -0.13275 | 120.2911 | 0.10078 | -0.0075559 | 0.050917 | 0.040877 | -0.0027728 | -0.010256 | -0.0051121 | -0.014313 | -0.0029694 | -0.0021896 | 0.00054052 | -0.020132 | 0.01239 | -0.014883 | 7.9239 | 104.9652 | 0.086975 | 119.8883 | 0.032043 | -0.32501 | -0.21515 | -0.13733 | -0.11444 | 0.25177 | -0.027466 | -0.068665 | -0.09613 | 0.09613 | 0.21973 | -15.3259 | -0.40283 | 0.16479 | -0.082398 | -0.19226 | -0.30212 | -0.41199 | 0.38452 | -120.4056 | -120.3186 | 0.064086 | 0.22888 | 0.036621 | -0.15564 | -0.3479 | -0.054932 | 119.8013 | -0.32044 | -0.27924 | 104.8782 | -0.36621 | 105.098 | 0.01831 | -120.2042 | -120.0394 | 120.0211 | 0.10529 | 8.0566 | -0.004578
2597.0469 | 120.8908 | -0.11444 | 120.2133 | -0.56297 | 0.028119 | 0.10902 | -0.01317 | 0.04636 | 0.056181 | 0.05043 | 0.046722 | 0.02886 | 0.0102 | 0.0056675 | 0.26719 | 0.037384 | 0.031259 | 7.814 | 120.8359 | 0.013733 | 121.1105 | 0.018311 | -0.40741 | 0.10071 | -0.22888 | -0.13275 | 0.27924 | -0.018311 | -0.086975 | -0.14191 | 0.091553 | 0.12817 | 0.62256 | 0.89722 | 0.13275 | 0.21515 | -0.29297 | 0.086975 | -0.42114 | 0.39368 | -120.3461 | -120.2316 | 0.027466 | 0.20599 | -0.027466 | -0.18768 | -0.42114 | 0.004578 | 121.0968 | -0.36621 | -0.29755 | 120.8221 | -0.41199 | 120.9503 | -0.01831 | -120.1996 | -119.9341 | 121.225 | 0.09613 | 7.9285 | -0.11444
2598.7969 | 120.7535 | -0.14191 | 120.1904 | -0.18913 | 0.028119 | 0.10988 | 0.039168 | -0.004909 | 0.056394 | 0.050644 | -0.053986 | -0.097818 | -0.001976 | -0.0077909 | -0.04064 | 0.015167 | -0.010397 | 8.2581 | 120.0851 | -0.064087 | 117.5674 | 0 | -0.34332 | -0.16022 | -0.25635 | -0.10071 | 0.1831 | -0.032043 | -0.045776 | -0.43488 | 0.059509 | 0.07782 | -0.10529 | -2.623 | 0.14191 | -0.01831 | -0.20142 | -0.09613 | -0.27924 | 0.32501 | -120.2911 | -120.2225 | 0.096131 | 0.20142 | -0.29297 | -0.1236 | -0.61798 | 0.064087 | 117.6315 | -0.22888 | -0.21515 | 120.1492 | -0.28381 | 120.2271 | 0.041199 | -120.2545 | -120.0073 | 117.7094 | 0.10986 | 8.4 | -0.11444
2600.5469 | 120.3415 | -0.11444 | 120.1767 | 0.0016023 | -0.013324 | 0.10945 | 0.036391 | 0.046574 | 0.059599 | 0.051498 | -0.057037 | 0.02886 | 0.011269 | -0.012704 | 0.26698 | 0.038025 | 0.031687 | 8.4641 | 111.0077 | -0.064087 | 109.1675 | 0.068665 | -0.25635 | -0.13733 | -0.22888 | -0.17853 | 0.24719 | -0.041199 | -0.018311 | -0.37079 | 0.10071 | 0.050354 | -9.169 | -11.0092 | 0.18311 | -0.022888 | -0.14191 | -0.073242 | -0.19226 | 0.36163 | -120.3552 | -120.2179 | 0.09613 | 0.21515 | -0.25635 | -0.14648 | -0.61798 | 0.13275 | 109.2316 | -0.2655 | -0.28839 | 111.0718 | -0.42572 | 111.1221 | -0.064087 | -120.2408 | -119.9295 | 109.2819 | 0.073242 | 8.5785 | -0.11444
2602.2969 | 121.1792 | -0.13275 | 120.6253 | -0.013657 | 0.02876 | 0.11009 | 0.037886 | 0.046574 | 0.057249 | 0.051285 | -0.173 | 0.029501 | 0.011269 | -0.0035183 | 0.17662 | 0.03717 | 0.032114 | 8.1024 | 121.3623 | -0.07782 | 103.9444 | 0.054932 | -0.24719 | -0.35248 | -0.20142 | -0.15106 | 0.21057 | -0.13275 | -0.027466 | -0.33875 | -0.009155 | 0.054931 | 0.737 | -16.6809 | 0.18768 | -0.21973 | -0.11444 | -0.27466 | -0.16937 | 0.34332 | -120.7764 | -120.7581 | 0.10529 | 0.1236 | -0.20599 | -0.21973 | -0.54932 | 0.13275 | 104.0222 | -0.23804 | -0.34332 | 121.4401 | -0.36163 | 121.4951 | -0.018311 | -120.7031 | -120.4147 | 104.0771 | 0 | 8.2352 | -0.068665
2604 | 121.0831 | -0.082397 | 121.0144 | 0.10841 | 0.0018435 | 0.051131 | 0.050276 | 4.192e-06 | -0.0079061 | -0.0048985 | -0.0082093 | 0.013052 | 0.00058743 | 0.0090853 | -0.013296 | 0.020935 | 0.0022068 | 8.4549 | 120.8542 | -0.14191 | 120.845 | 0.2243 | -0.032043 | 0.054932 | 0.11444 | 0.036621 | -0.041199 | 0.059509 | 0.17395 | 0.09613 | 0.13275 | -0.05951 | -0.16022 | -0.16937 | 0.3067 | 0.13733 | 0.050354 | 0.19684 | 0.10986 | 0.041198 | -120.9778 | -120.9549 | 0.25635 | 0.21515 | 0.17853 | 0.17395 | 0.13733 | 0.36621 | 120.9869 | 0.21515 | 0.10071 | 120.9961 | 0.07782 | 120.9366 | 0.11902 | -121.1563 | -121.0556 | 120.9274 | 0.14191 | 8.5373 | 0.19684
2605.75 | 120.8908 | -0.073242 | 120.6482 | 0.12367 | -0.0032833 | 0.048994 | 0.051131 | -0.003841 | -0.0096151 | -0.0038303 | -0.0021057 | 0.009848 | 0.00016023 | -0.0018093 | -0.0165 | 0.020935 | -0.000784 | 8.5876 | 120.3003 | -0.13733 | 120.9915 | 0.23804 | 0.013733 | 0.073242 | 0.12817 | 0.032043 | -0.054932 | 0.07782 | 0.21057 | 0.13733 | 0.13733 | -0.064087 | -0.3479 | 0.34332 | 0.31128 | 0.14648 | 0.086975 | 0.21057 | 0.15106 | 0.01831 | -120.6162 | -120.5704 | 0.28381 | 0.21057 | 0.21057 | 0.19226 | 0.19226 | 0.37537 | 121.1288 | 0.2655 | 0.13275 | 120.4376 | 0.086975 | 120.3735 | 0.10529 | -120.7855 | -120.7031 | 121.0648 | 0.15106 | 8.6609 | 0.20142
2607.5156 | 120.9641 | -0.10529 | 120.6116 | -0.044174 | -0.0026425 | 0.051558 | 0.050063 | 4.192e-06 | -0.0079061 | -0.0036167 | -0.0021057 | 0.009848 | 0.0010146 | -0.00074128 | -0.014791 | 0.022003 | 0.000925 | 8.5648 | 120.9595 | -0.12817 | 120.9778 | 0.20142 | -0.050354 | 0.045776 | 0.082397 | 0.032043 | -0.050354 | 0.036621 | 0.12817 | 0.059509 | 0.1236 | -0.022888 | 0.3479 | 0.36621 | 0.3067 | 0.15106 | 0.054932 | 0.17395 | 0.07782 | 0.054932 | -120.5795 | -120.575 | 0.23346 | 0.22888 | 0.16479 | 0.17395 | 0.10986 | 0.32959 | 121.106 | 0.17853 | 0.086975 | 121.0876 | 0.082397 | 121.0648 | 0.13733 | -120.7397 | -120.6619 | 121.0831 | 0.14191 | 8.67 | 0.18768
2609.2188 | 120.8679 | -0.091553 | 120.3369 | -0.15099 | -0.0009335 | 0.052412 | 0.051131 | 0.0014996 | -0.0076925 | -0.0031895 | -0.0051575 | 0.0094208 | 0.0016556 | 0.0016085 | -0.014364 | 0.021149 | -0.0001432 | 8.6929 | 120.4468 | -0.13275 | 121.0464 | 0.25177 | 0.009155 | 0.082397 | 0.14648 | 0.032043 | -0.045776 | 0.07782 | 0.20599 | 0.13275 | 0.14191 | -0.041198 | 0.10986 | 0.70953 | 0.34332 | 0.17395 | 0.10071 | 0.21515 | 0.14191 | 0.045777 | -120.3049 | -120.2591 | 0.29755 | 0.23346 | 0.2243 | 0.18768 | 0.17853 | 0.38452 | 121.1792 | 0.25177 | 0.1236 | 120.5795 | 0.077819 | 120.5383 | 0.1236 | -120.4697 | -120.3827 | 121.138 | 0.16937 | 8.7845 | 0.23804
2610.9688 | 121.3852 | -0.07782 | 121.2799 | 0.11604 | -0.0092649 | 0.049635 | 0.050703 | 0.0019268 | -0.0085471 | -0.0063937 | -0.084503 | 0.011557 | 0.00251 | 0.0054537 | -0.014578 | 0.022858 | 0.0015658 | 8.6243 | 121.0739 | -0.14648 | 120.9686 | 0.082397 | -0.13733 | -0.09613 | 0.022888 | 0.054932 | -0.07782 | 0.036621 | 0.12817 | 0.045776 | 0.045776 | -0.068664 | -0.20599 | -0.31128 | 0.16022 | -0.01831 | -0.059509 | 0.050354 | 0.009155 | 0 | -121.225 | -121.2433 | 0.20599 | 0.1236 | 0.1236 | 0.1236 | 0.1236 | 0.22888 | 121.1151 | 0.20599 | 0.11444 | 121.2204 | 0.13275 | 121.1517 | 0.13275 | -121.4264 | -121.3577 | 121.0464 | 0.11444 | 8.7021 | 0.10071
2612.6562 | 121.0098 | -0.10071 | 120.4285 | 0.10841 | -0.0037107 | 0.050703 | 0.051131 | -0.0023456 | -0.0081197 | -0.0038303 | 0.0009461 | 0.01113 | 0.0048598 | -0.00074128 | -0.013082 | 0.020081 | 0.0015658 | 8.7296 | 121.0648 | -0.1236 | 121.0281 | 0.13275 | -0.059509 | 0.009155 | 0.036621 | 0.041199 | -0.064087 | 0.004578 | 0.14191 | 0.059509 | 0.10529 | -0.022888 | 0.63629 | 0.59967 | 0.23346 | 0.10986 | 0.041199 | 0.13275 | 0.064087 | 0.036621 | -120.3873 | -120.4239 | 0.24262 | 0.20599 | 0.16022 | 0.16937 | 0.1236 | 0.25635 | 121.1517 | 0.20599 | 0.068665 | 121.1884 | 0.10529 | 121.1655 | 0.14191 | -120.5521 | -120.4926 | 121.1288 | 0.10529 | 8.8303 | 0.13733
2614.4062 | 121.0144 | -0.1236 | 120.7443 | 0.12367 | -0.0030697 | 0.051131 | 0.05049 | -0.003841 | -0.0089743 | -0.0051121 | -0.0051575 | 0.011984 | 0.0016556 | -0.00095488 | -0.012869 | 0.020294 | 0.002634 | 8.7708 | 121.0739 | -0.14191 | 121.051 | 0.14191 | -0.07782 | 0 | 0.027466 | 0.041199 | -0.059509 | 0.032043 | 0.13733 | 0.045776 | 0.10529 | -0.018311 | 0.32959 | 0.3067 | 0.2655 | 0.1236 | 0.045776 | 0.14191 | 0.064087 | 0.064087 | -120.7031 | -120.7123 | 0.26093 | 0.22888 | 0.16937 | 0.16479 | 0.10528 | 0.28381 | 121.1929 | 0.19684 | 0.091552 | 121.2158 | 0.10071 | 121.1975 | 0.16479 | -120.8862 | -120.8038 | 121.1746 | 0.15564 | 8.8943 | 0.15106
2616.1562 | 120.7809 | -0.073242 | 120.7672 | 0.10841 | 0.0020571 | 0.051131 | 0.05284 | 0.0025678 | -0.0094015 | -0.0046847 | -0.011261 | 0.011984 | 0.001442 | 0.00032692 | -0.015646 | 0.022217 | -0.000784 | 8.8852 | 121.106 | -0.12817 | 121.1609 | 0.21973 | -0.027466 | 0.059509 | 0.1236 | 0.027466 | -0.036621 | 0.09613 | 0.19684 | 0.07782 | 0.14648 | -0.054932 | 0.33875 | 0.39368 | 0.29297 | 0.13275 | 0.045776 | 0.18768 | 0.10071 | 0.036621 | -120.7397 | -120.6711 | 0.27008 | 0.21973 | 0.15106 | 0.18311 | 0.11444 | 0.3479 | 121.2891 | 0.23346 | 0.13275 | 121.2341 | 0.064087 | 121.1792 | 0.10071 | -120.8954 | -120.8038 | 121.2341 | 0.16937 | 8.9584 | 0.19684
2617.8438 | 121.106 | -0.091553 | 121.1975 | 0.10841 | -0.0020017 | 0.054121 | 0.050917 | 4.192e-06 | -0.0096151 | -0.0027621 | -0.0051575 | 0.01113 | 0.0012282 | -0.0062955 | -0.01415 | 0.018585 | 7.04e-05 | 8.9081 | 121.1243 | -0.16022 | 121.1105 | 0.13733 | -0.068665 | 0.013733 | 0.041199 | 0.036621 | -0.07782 | 0.045776 | 0.15106 | 0.059509 | 0.11902 | -0.068664 | -0.073242 | -0.086975 | 0.22888 | 0.10529 | 0.022888 | 0.17395 | 0.091552 | 0.013733 | -121.1609 | -121.1517 | 0.24261 | 0.21057 | 0.15106 | 0.19684 | 0.13733 | 0.29755 | 121.2708 | 0.22888 | 0.1236 | 121.2845 | 0.11444 | 121.2158 | 0.12817 | -121.3577 | -121.2753 | 121.2021 | 0.13733 | 8.9996 | 0.13275
2619.5938 | 121.0419 | -0.10071 | 120.9412 | 0.11604 | -7.9104e-05 | 0.050703 | 0.05049 | 0.0021406 | -0.010897 | -0.0046847 | -0.011261 | 0.010275 | 0.003151 | 0.0075901 | -0.012014 | 0.019867 | -0.0044156 | 9.0637 | 120.0256 | -0.14648 | 120.7718 | 0.1831 | 0 | 0.041199 | 0.054932 | 0.064087 | -0.068665 | 0.032043 | 0.13275 | 0.050354 | 0.045776 | -0.045776 | -0.91553 | -0.16937 | 0.28381 | 0.14191 | 0.10071 | 0.18768 | 0.14648 | 0.032043 | -120.8771 | -120.9091 | 0.23346 | 0.14648 | 0.15106 | 0.11444 | 0.11902 | 0.32959 | 120.9183 | 0.20142 | 0.10071 | 120.1721 | 0.13275 | 120.1263 | 0.1648 | -121.0876 | -121.0098 | 120.8725 | 0.13275 | 9.1644 | 0.15564
2621.2812 | 121.2387 | -0.11902 | 112.7792 | -0.12047 | -0.011615 | 0.039168 | 0.034041 | -0.014736 | -0.014315 | -0.019211 | -0.12112 | -0.0053192 | -0.014153 | -0.01249 | -0.037008 | 0.017303 | -0.014456 | 8.876 | 120.5383 | -0.15106 | 120.7489 | 0.10071 | -0.10529 | -0.16022 | 0.013733 | 0.064087 | -0.086975 | 0.022888 | 0.11444 | -0.11902 | -0.28381 | -0.032043 | 7.7591 | 7.9697 | 0.21973 | -0.041198 | 0.013733 | -0.009155 | 0.045776 | 0.032044 | -112.7151 | -112.7563 | 0.23346 | -0.16479 | 0 | -0.19684 | -0.032044 | 0.25177 | 120.9 | 0.20142 | 0.10986 | 120.6894 | 0.15106 | 120.6573 | 0.18311 | -112.9303 | -112.8662 | 120.8679 | 0.14191 | 8.9951 | 0.13275
2623.0312 | 121.2387 | -57.6324 | 63.0753 | -0.013657 | -0.0009335 | 0.052626 | 0.053053 | 0.00085879 | -0.011111 | -0.0038303 | -0.0051575 | 0.0094208 | 0.0016556 | 0.00096772 | -0.013937 | 0.022644 | 0.0022068 | -14.4928 | 62.9791 | -57.8796 | 63.1302 | -57.3944 | -58.0124 | -57.9391 | 0.050354 | 0.041199 | -0.059509 | 0.059509 | 0.1236 | 0.050354 | 0.10071 | -0.24719 | -0.09613 | 0.054932 | 0.23804 | -0.3067 | -0.37994 | -0.059509 | -0.13275 | 57.5729 | -63.0341 | -63.0157 | 57.756 | 57.7332 | 57.6828 | 0.16022 | 0.10986 | 0.48523 | 121.0098 | 0.1831 | 0.11902 | 120.8588 | 0.10071 | 120.6116 | 57.6736 | -120.9549 | -63.1348 | 120.7626 | 57.692 | 43.1396 | 57.6828
2624.7969 | 120.4422 | -11.6135 | 109.1354 | -0.24254 | -0.01076 | 0.037031 | 0.036818 | -0.019008 | -0.019656 | -0.014084 | -0.13943 | 0.0042938 | -0.0096664 | -0.015268 | -0.038076 | 0.038452 | -0.0095426 | 4.3808 | 109.9228 | -11.6638 | 109.1629 | -11.467 | -11.6959 | -11.6867 | 0.022888 | 0.068665 | -0.064087 | 0.036621 | 0.11902 | -0.086975 | -0.28839 | -0.050354 | 0.78735 | 0.027466 | 0.14648 | -0.073243 | -0.082398 | -0.022889 | -0.032044 | 11.5494 | -109.0668 | -109.0988 | 11.7325 | 11.3251 | 11.5265 | -0.2243 | -0.022888 | 0.19684 | 120.8267 | 0.18311 | 0.10071 | 121.5866 | 0.13275 | 121.5363 | 11.6821 | -120.7993 | -109.1995 | 120.7764 | 11.6501 | 15.9943 | 11.6364
2626.5625 | 120.4926 | -12.6022 | 108.3481 | -0.0060272 | -0.010333 | 0.10924 | 0.036604 | 0.04636 | 0.060453 | 0.051285 | -0.084503 | 0.00643 | -0.0030442 | -0.0065091 | 0.08433 | 0.03653 | 0.032968 | 3.8818 | 107.7393 | -12.6114 | 108.0597 | -12.4558 | -12.7167 | -12.6526 | -0.036621 | 0.059509 | -0.064087 | 0.032043 | 0.10529 | -0.064087 | -0.25177 | -0.009155 | -0.60882 | -0.28839 | 0.14648 | -0.050354 | -0.11444 | -0.041199 | -0.10529 | 12.5381 | -108.2886 | -108.316 | 12.7075 | 12.3505 | 12.5381 | -0.18768 | 0 | 0.15564 | 120.6711 | 0.16937 | 0.09613 | 120.3506 | 0.1236 | 120.3415 | 12.6617 | -120.9595 | -108.4122 | 120.6619 | 12.6343 | 16.4841 | 12.5656
2628.2656 | 121.0876 | -15.8386 | 105.3406 | -0.0060272 | 0.027905 | 0.11052 | 0.041731 | 0.047215 | 0.057462 | 0.051285 | -0.04483 | -0.004892 | -0.00069437 | -0.0039457 | -0.039144 | 0.043152 | 0.035105 | 2.5635 | 105.1941 | -15.9164 | 104.6356 | -15.7333 | -16.0675 | -15.8981 | -0.018311 | 0.068665 | -0.059509 | 0.004578 | 0.082397 | -0.050354 | -0.18768 | -0.07782 | -0.14648 | -0.70496 | 0.10529 | -0.059509 | -0.22888 | 0.018311 | -0.15106 | 15.7791 | -105.2719 | -105.336 | 15.921 | 15.6509 | 15.7883 | -0.12817 | 0.009155 | 0.18311 | 120.5521 | 0.14191 | 0.064087 | 121.1105 | 0.12817 | 121.0327 | 15.9073 | -121.257 | -105.4001 | 120.4742 | 15.8432 | 18.4021 | 15.8203
2630.0312 | 121.1426 | -16.8594 | 104.3884 | -0.036545 | 0.028333 | 0.11073 | 0.048994 | 0.044651 | 0.059171 | 0.052139 | -0.017365 | 0.0021576 | -0.012657 | 0.0022495 | -0.019277 | 0.0049134 | -0.018515 | 2.1698 | 104.3701 | -16.8732 | 103.6102 | -16.7221 | -17.038 | -16.864 | -0.045776 | 0.086975 | -0.091553 | -0.036621 | 0.050354 | -0.054932 | -0.10071 | -0.013733 | -0.018311 | -0.7782 | 0.13733 | -0.004578 | -0.17853 | 0.009155 | -0.16479 | 16.7679 | -104.3015 | -104.425 | 16.9098 | 16.7587 | 16.8045 | -0.009155 | 0.036621 | 0.15106 | 120.4834 | 0.14191 | 0.054932 | 121.2433 | 0.17853 | 121.2296 | 16.9464 | -121.2616 | -104.48 | 120.4697 | 16.8228 | 19.0292 | 16.8137
2631.7812 | 121.3943 | -18.3151 | 102.9282 | -0.40276 | -0.0011471 | 0.050063 | 0.049849 | -0.001491 | -0.01047 | -0.0029759 | -0.0021057 | 0.009848 | 0.004219 | 0.0090853 | -0.013082 | 0.018585 | 0.0007114 | 1.7258 | 102.4429 | -18.3517 | 102.8778 | -18.1229 | -18.457 | -18.4296 | 0.07782 | 0.022888 | -0.068665 | 0.045776 | 0.16479 | 0.07782 | 0.10529 | -0.036621 | -0.48523 | -0.050354 | 0.19226 | -0.11444 | -0.14191 | -0.077819 | -0.10529 | 18.2465 | -102.9053 | -102.8824 | 18.4799 | 18.4204 | 18.3929 | 0.17395 | 0.14649 | 0.22888 | 121.2296 | 0.23346 | 0.11444 | 120.7947 | 0.091553 | 120.7581 | 18.338 | -121.2799 | -102.9968 | 121.1929 | 18.3609 | 20.0409 | 18.3929
2633.5312 | 121.5271 | -58.1268 | 62.8738 | -0.0060272 | 0.0009891 | 0.054549 | 0.053267 | 0.0019268 | -0.0072653 | -0.0012669 | -0.0051575 | 0.012839 | 0.0035782 | -0.00010048 | -0.014364 | 0.023712 | 0.0011386 | -15.4678 | 62.7319 | -58.4152 | 62.9471 | -57.8293 | -58.4702 | -58.4152 | 0.11444 | 0.022888 | -0.041199 | 0.10986 | 0.16937 | 0.086975 | 0.13733 | -0.28839 | -0.14191 | 0.073243 | 0.29755 | -0.28839 | -0.34332 | 0 | -0.054932 | 58.0856 | -62.851 | -62.764 | 58.2962 | 58.2642 | 58.2138 | 0.17853 | 0.12817 | 0.58594 | 121.3623 | 0.21057 | 0.15106 | 121.1472 | 0.064087 | 120.8588 | 58.1497 | -121.2891 | -62.915 | 121.0739 | 58.2367 | 42.659 | 58.2413
2635.25 | 121.5317 | -58.3054 | 62.7502 | -0.0060272 | 0.0018435 | 0.054335 | 0.051558 | 0.0027814 | -0.0087607 | -0.0081027 | -0.0051575 | 0.013052 | 0.001442 | -0.0020231 | -0.015646 | 0.020508 | -0.000784 | -15.5228 | 62.6724 | -58.4976 | 62.8693 | -57.9346 | -58.5892 | -58.5251 | 0.11902 | 0.027466 | -0.050354 | 0.10071 | 0.15564 | 0.10071 | 0.14191 | -0.19226 | -0.07782 | 0.11902 | 0.37079 | -0.21973 | -0.28381 | -0.027465 | -0.091552 | 58.255 | -62.7228 | -62.6495 | 58.461 | 58.4473 | 58.4061 | 0.19226 | 0.15106 | 0.56305 | 121.3669 | 0.20599 | 0.15106 | 121.17 | 0.07782 | 120.9778 | 58.3328 | -121.2479 | -62.8006 | 121.1746 | 58.4061 | 42.7826 | 58.4244
2637 | 121.4081 | -58.5938 | 62.6404 | -0.013657 | -0.0084103 | 0.044295 | 0.056258 | 4.192e-06 | -0.023074 | 0.050003 | 0.0009461 | 0.00023504 | -0.007103 | -0.012704 | -0.019491 | 0.005127 | -0.0037748 | -15.6876 | 62.5626 | -58.6945 | 62.5671 | -58.2779 | -58.9005 | -58.7814 | -0.050354 | 0.07782 | -0.073242 | -0.022888 | 0.027466 | -0.07782 | 0.041199 | -0.10071 | -0.07782 | -0.073242 | 0.31586 | -0.18768 | -0.3067 | -0.086975 | -0.20599 | 58.5205 | -62.5626 | -62.6633 | 58.6212 | 58.6349 | 58.5159 | 0.11444 | -0.004578 | 0.41656 | 121.2616 | 0.10071 | 0.050354 | 121.257 | 0.15106 | 121.1563 | 58.6716 | -121.3348 | -62.7136 | 121.1609 | 58.5709 | 42.9062 | 58.5434
2638.6875 | 121.5088 | -58.1863 | 63.0386 | -0.0060272 | 0.0016299 | 0.053267 | 0.055189 | 0.002995 | -0.0081197 | -0.0040439 | -0.0051575 | 0.011557 | 0.00080103 | 0.0052401 | -0.015219 | 0.022217 | 0.0058384 | -15.6235 | 62.9929 | -58.287 | 63.0295 | -57.8247 | -58.4427 | -58.3969 | 0.032043 | 0.054932 | -0.064087 | 0.073242 | 0.1236 | 0.036621 | 0.11902 | -0.10071 | -0.045776 | -0.009155 | 0.36163 | -0.21057 | -0.25635 | -0.10986 | -0.15564 | 58.1223 | -62.9837 | -62.9654 | 58.3099 | 58.3054 | 58.223 | 0.18311 | 0.10071 | 0.46234 | 121.3165 | 0.18768 | 0.13733 | 121.2799 | 0.11902 | 121.1792 | 58.2413 | -121.3257 | -63.1027 | 121.2158 | 58.2596 | 42.5629 | 58.2184
2640.4531 | 121.4401 | -56.0394 | 65.2496 | -0.021286 | -0.0005063 | 0.049635 | 0.054549 | -0.00063661 | -0.013674 | -0.0063937 | 0.0009461 | 0.012625 | 0.0029372 | 0.0082309 | -0.015432 | 0.023285 | -0.0003568 | -14.7308 | 64.9841 | -56.2958 | 65.1581 | -55.751 | -56.2775 | -56.2546 | -0.032043 | 0.07782 | -0.07782 | 0 | 0.045776 | -0.036621 | 0.032043 | -0.25635 | -0.2655 | -0.091553 | 0.28839 | -0.21515 | -0.23804 | 0.041198 | 0.01831 | 55.9616 | -65.1718 | -65.2496 | 56.0852 | 56.0715 | 56.0028 | 0.10986 | 0.041199 | 0.54474 | 121.4539 | 0.1236 | 0.07782 | 121.2799 | 0.15564 | 121.0236 | 56.1172 | -121.5454 | -65.3275 | 121.1975 | 56.0394 | 41.3086 | 56.0074
2642.2031 | 120.7031 | -33.0505 | 88.2385 | -0.15862 | -0.0028561 | 0.049849 | 0.053908 | -0.001491 | -0.0072653 | -0.0044711 | -0.0021057 | 0.012839 | 0.00251 | 0.0045993 | -0.016073 | 0.021576 | 7.04e-05 | -4.715 | 88.147 | -33.197 | 87.8174 | -33.2245 | -33.6502 | -33.5632 | 0.013733 | 0.07782 | -0.064087 | 0.064087 | 0.13275 | 0.018311 | 0.11444 | -0.14648 | -0.091552 | -0.42114 | -0.17395 | -0.5127 | -0.59967 | -0.36621 | -0.45319 | 32.9864 | -88.1607 | -88.1744 | 33.1833 | 33.165 | 33.0688 | 0.17853 | 0.082398 | -0.027466 | 121.0144 | 0.19684 | 0.12817 | 121.344 | 0.14191 | 121.1975 | 33.1284 | -121.4355 | -88.3026 | 120.8679 | 33.1146 | 28.3356 | 33.0643
2643.8906 | 121.3623 | -23.8174 | 97.5403 | 0.0016023 | -0.0022153 | 0.050917 | 0.049422 | -0.0042682 | -0.0096151 | -0.0025485 | -0.0021057 | 0.011343 | 0.0010146 | -0.0020231 | -0.015219 | 0.02243 | 0.0032748 | -0.49896 | 97.6181 | -23.6938 | 97.4625 | -23.6481 | -24.1104 | -24.0601 | 0.036621 | 0.050354 | -0.068665 | 0.036621 | 0.14648 | 0.054932 | 0.11444 | 0.1236 | 0.07782 | -0.07782 | 0.16937 | -0.24262 | -0.29297 | -0.36621 | -0.41657 | 23.7488 | -97.4899 | -97.5037 | 23.9639 | 23.9319 | 23.8724 | 0.18311 | 0.1236 | 0.045777 | 121.1563 | 0.21515 | 0.10529 | 121.312 | 0.11902 | 121.4355 | 23.8678 | -121.2341 | -97.6089 | 121.2799 | 23.8541 | 23.3185 | 23.8541
2645.6406 | 121.2341 | -15.1062 | 106.3477 | 0.12367 | -0.0002927 | 0.053267 | 0.050917 | -0.00042301 | -0.0072653 | -0.0040439 | -0.0021057 | 0.009848 | 0.00251 | -0.0013821 | -0.015646 | 0.020721 | 0.0007114 | 3.2776 | 106.4301 | -14.9048 | 106.2103 | -14.9368 | -15.3992 | -15.2939 | 0.13275 | 0.036621 | -0.068665 | 0.091553 | 0.18768 | 0.086975 | 0.1236 | 0.20142 | 0.082398 | -0.13733 | 0.16937 | -0.18768 | -0.29297 | -0.3891 | -0.49438 | 15.0375 | -106.311 | -106.2561 | 15.2939 | 15.2298 | 15.1932 | 0.19226 | 0.15564 | -0.032044 | 121.1151 | 0.25635 | 0.16022 | 121.3348 | 0.10529 | 121.5363 | 15.1428 | -121.2524 | -106.4163 | 121.3165 | 15.1978 | 18.3838 | 15.239
2647.3906 | 121.1243 | -13.5361 | 107.84 | 0.10841 | 0.0005619 | 0.051558 | 0.054121 | -0.0025592 | -0.0094015 | -0.0023349 | -0.0021057 | 0.012839 | 0.003151 | 0.0052401 | -0.01415 | 0.021576 | 0.0039158 | 3.9413 | 107.7438 | -13.6047 | 107.7713 | -13.3759 | -13.678 | -13.6368 | 0.11902 | 0.036621 | -0.036621 | 0.11444 | 0.1831 | 0.086975 | 0.16022 | -0.068664 | -0.096131 | -0.068665 | 0.16022 | -0.10071 | -0.14191 | -0.032044 | -0.073243 | 13.4995 | -107.8033 | -107.7255 | 13.7192 | 13.6963 | 13.623 | 0.19684 | 0.1236 | 0.22888 | 121.376 | 0.21973 | 0.15106 | 121.3486 | 0.073242 | 121.2799 | 13.5727 | -121.4447 | -107.8766 | 121.3074 | 13.6505 | 17.4774 | 13.6551
2649.1406 | 121.3028 | -14.3509 | 107.016 | 0.11604 | -0.0020017 | 0.052199 | 0.050703 | -0.0012774 | -0.0081197 | -0.0029759 | -0.0021057 | 0.010916 | 0.0010146 | 0.0075901 | -0.015646 | 0.021362 | 7.04e-05 | 3.5385 | 106.8924 | -14.4882 | 106.9336 | -14.2456 | -14.5569 | -14.4974 | 0.11444 | 0.054932 | -0.059509 | 0.091553 | 0.1831 | 0.091553 | 0.15564 | -0.13733 | -0.1236 | -0.082397 | 0.10529 | -0.14648 | -0.20599 | -0.009155 | -0.068665 | 14.2914 | -106.9611 | -106.9244 | 14.534 | 14.5065 | 14.4424 | 0.21515 | 0.15106 | 0.24262 | 121.4218 | 0.24261 | 0.15106 | 121.3806 | 0.11444 | 121.2433 | 14.4058 | -121.5042 | -107.0755 | 121.2845 | 14.4424 | 17.8894 | 14.4653
2650.8906 | 120.1721 | -23.259 | 97.5128 | -0.013657 | -0.0011471 | 0.044722 | 0.054549 | 0.001286 | -0.016024 | -0.012802 | -0.0051575 | 0.013907 | 0.0016556 | 0.0024631 | -0.015432 | 0.020935 | 0.0004978 | -0.45776 | 97.5082 | -23.3414 | 97.4121 | -23.1812 | -23.5794 | -23.5199 | -0.027466 | 0.082397 | -0.073242 | -0.018311 | 0.059509 | -0.027466 | 0.059509 | -0.082398 | -0.004577 | -0.10071 | 0.07782 | -0.26093 | -0.32043 | -0.17853 | -0.23804 | 23.1857 | -97.4304 | -97.5311 | 23.3185 | 23.3185 | 23.2315 | 0.13275 | 0.045776 | 0.16022 | 120.7535 | 0.13275 | 0.054931 | 120.8496 | 0.15564 | 120.7672 | 23.3414 | -120.8542 | -97.5861 | 120.6711 | 23.2407 | 22.8012 | 23.2315
2652.5781 | 121.2662 | -15.1794 | 105.9814 | 0.13893 | -0.0015743 | 0.050917 | 0.05049 | -0.0032 | -0.0096151 | -0.0044711 | -0.0021057 | 0.013266 | 0.00251 | 0.0082309 | -0.013723 | 0.021149 | -0.0003568 | 3.2639 | 105.2032 | -15.2664 | 105.7983 | -15.0879 | -15.3946 | -15.358 | -0.041199 | 0.064087 | -0.086975 | -0.073242 | 0.07782 | -0.022888 | 0.027466 | -0.086975 | -0.7782 | -0.1831 | 0.091552 | -0.17853 | -0.21515 | -0.091553 | -0.12817 | 15.0925 | -105.9174 | -106.0547 | 15.2573 | 15.2069 | 15.1566 | 0.11444 | 0.064087 | 0.17853 | 121.0648 | 0.16479 | 0.013733 | 120.4697 | 0.15106 | 120.3827 | 15.2435 | -121.2479 | -106.0684 | 120.9778 | 15.1062 | 18.4433 | 15.1382
2654.2812 | 120.5154 | -15.271 | 105.542 | -0.4409 | -0.0022153 | 0.050703 | 0.050917 | 0.00021799 | -0.010683 | -0.0053257 | -0.0051575 | 0.010916 | 0.0035782 | 0.0022495 | -0.016287 | 0.021362 | -0.0016384 | 3.2089 | 105.3177 | -15.3351 | 105.8212 | -15.1474 | -15.4449 | -15.4175 | -0.036621 | 0.073242 | -0.082397 | -0.050354 | 0.073242 | -0.013733 | 0.022888 | -0.064087 | -0.2243 | 0.27924 | 0.1236 | -0.14648 | -0.17395 | -0.082397 | -0.10986 | 15.1886 | -105.4688 | -105.5923 | 15.3442 | 15.2939 | 15.2573 | 0.10528 | 0.068664 | 0.18768 | 121.1563 | 0.15564 | 0.032043 | 120.6528 | 0.15564 | 120.5887 | 15.3442 | -120.8771 | -105.6244 | 121.0922 | 15.2206 | 18.4799 | 15.2344
2656.0312 | 121.5179 | -59.3216 | 61.702 | 0.0016023 | -0.0020017 | 0.052626 | 0.05049 | 0.0027814 | -0.010897 | -0.0036167 | -0.0051575 | 0.012198 | 0.0020828 | 0.0043857 | -0.016073 | 0.020935 | 0.0030612 | -17.3676 | 61.5417 | -59.61 | 61.6928 | -59.0561 | -59.6832 | -59.6466 | 0.09613 | 0.041199 | -0.045776 | 0.064087 | 0.1831 | 0.10529 | 0.11444 | -0.28839 | -0.16022 | -0.009155 | 0.2655 | -0.32501 | -0.36163 | -0.036621 | -0.073243 | 59.2758 | -61.6608 | -61.6379 | 59.5047 | 59.436 | 59.4269 | 0.16022 | 0.15106 | 0.55389 | 121.3028 | 0.22888 | 0.10986 | 121.1517 | 0.086975 | 120.8633 | 59.3628 | -121.3119 | -61.7477 | 121.0144 | 59.3857 | 41.954 | 59.4177
2657.7812 | 120.7672 | -18.6768 | 102.5757 | 0.16945 | -0.0062741 | 0.054976 | 0.052626 | -0.0034136 | -0.0089743 | -0.0038303 | -0.0021057 | 0.012625 | 0.0027236 | 0.00054052 | -0.014791 | 0.02243 | 7.04e-05 | 2.33 | 102.4658 | -18.7912 | 102.5208 | -18.5577 | -18.9011 | -18.8461 | 0.10986 | 0.036621 | -0.045776 | 0.09613 | 0.16937 | 0.073242 | 0.16479 | -0.11444 | -0.10986 | -0.054932 | 0.11902 | -0.16937 | -0.2243 | -0.054931 | -0.10986 | 18.631 | -102.5391 | -102.4796 | 18.8461 | 18.8416 | 18.75 | 0.21057 | 0.11902 | 0.23346 | 121.312 | 0.21515 | 0.14191 | 121.257 | 0.082397 | 121.1426 | 18.7134 | -121.3669 | -102.6215 | 121.1975 | 18.7729 | 21.0068 | 18.7866
2659.5469 | 121.5363 | -58.905 | 62.1735 | 0.0016023 | -0.0049923 | 0.043867 | 0.05348 | -0.0023456 | -0.013674 | -0.0059665 | -0.0021057 | 0.01412 | 0.0044326 | 0.0084445 | -0.015432 | 0.022003 | -0.0005704 | -17.5827 | 62.1918 | -59.0836 | 62.2284 | -58.6441 | -59.3033 | -59.2621 | -0.013733 | 0.068665 | -0.086975 | 0.004578 | 0.064087 | -0.013733 | 0.068665 | -0.17853 | 0.01831 | 0.054932 | 0.26093 | -0.35706 | -0.39825 | -0.17853 | -0.21973 | 58.8181 | -62.1048 | -62.1689 | 58.9691 | 58.9737 | 58.8913 | 0.15564 | 0.073242 | 0.43945 | 121.312 | 0.15106 | 0.091553 | 121.2753 | 0.15564 | 121.0968 | 58.9737 | -121.257 | -62.2604 | 121.1334 | 58.9096 | 41.3223 | 58.8913
2661.3125 | 121.5042 | -57.7286 | 63.414 | -0.0060272 | -0.0069149 | 0.10283 | 0.05583 | -0.003841 | -0.022219 | -0.011093 | -0.0021057 | 0.011984 | -0.0015488 | 0.00054052 | -0.014791 | 0.010468 | -0.0044156 | -16.7908 | 63.2446 | -58.1039 | 63.3728 | -57.3395 | -58.136 | -58.1863 | -0.07782 | 0.073242 | -0.09613 | -0.013733 | 0.018311 | -0.059509 | 0.050354 | -0.37537 | -0.16937 | -0.041198 | 0.3891 | -0.45776 | -0.40741 | -0.082397 | -0.032043 | 57.6324 | -63.3408 | -63.4277 | 57.7469 | 57.7789 | 57.6691 | 0.14648 | 0.036621 | 0.76447 | 121.4767 | 0.11444 | 0.082397 | 121.3486 | 0.16937 | 120.9732 | 57.8018 | -121.5179 | -63.5101 | 121.1014 | 57.7148 | 40.9378 | 57.6508
2663.0781 | 121.5775 | -57.1289 | 64.0594 | -0.0060272 | 0.0009891 | 0.053053 | 0.049849 | 0.001286 | -0.0094015 | -0.0034031 | -0.0021057 | 0.010702 | 0.0027236 | 0.0063083 | -0.014364 | 0.020508 | 0.0004978 | -16.3971 | 64.1144 | -57.2113 | 63.9038 | -56.9824 | -57.7515 | -57.637 | 0.11444 | 0.045776 | -0.045776 | 0.10986 | 0.13733 | 0.07782 | 0.11902 | -0.082398 | 0.054932 | -0.15564 | 0.14648 | -0.50812 | -0.62256 | -0.42572 | -0.54016 | 57.0831 | -64.0137 | -63.9496 | 57.2662 | 57.2479 | 57.2067 | 0.16479 | 0.1236 | 0.22888 | 121.1151 | 0.18311 | 0.15564 | 121.3257 | 0.091552 | 121.2433 | 57.1747 | -121.2708 | -64.1052 | 121.0327 | 57.2388 | 40.7318 | 57.2433
2664.7812 | 121.7194 | -43.4601 | 73.5443 | -0.021286 | 0.0024845 | 0.044295 | 0.055189 | -0.01324 | -0.032046 | 0.046371 | -0.0021057 | 0.0010894 | -0.013084 | -0.0054409 | -0.039572 | 0.033539 | -0.020651 | -2.9526 | 81.1844 | -40.8463 | 94.0659 | -39.8483 | -48.5184 | -51.0544 | 0.054932 | 0.054932 | -0.059509 | 0.054932 | 0.1236 | 0.022888 | 0.09613 | 2.6138 | 7.6401 | 20.5215 | 3.6118 | -7.5943 | -5.0583 | -10.2081 | -7.6721 | 43.4006 | -73.4894 | -73.4894 | 43.5837 | 43.5562 | 43.483 | 0.15564 | 0.082397 | 0.99792 | 134.9121 | 0.1831 | 0.11444 | 122.0306 | 0.11444 | 124.6445 | 43.515 | -114.3906 | -73.6038 | 137.5259 | 43.515 | 40.5075 | 43.515
2666.5312 | 121.637 | -59.6741 | 61.5555 | -0.0060272 | 0.0007755 | 0.051344 | 0.050276 | -0.00555 | -0.0089743 | -0.0021213 | -0.0051575 | 0.010916 | 0.0012282 | 0.0011813 | -0.015005 | 0.01944 | 7.04e-05 | -17.9214 | 61.4731 | -59.8343 | 61.6425 | -59.2667 | -59.935 | -59.8892 | 0.009155 | 0.036621 | -0.073242 | 0.045776 | 0.11902 | 0.054932 | 0.09613 | -0.16022 | -0.082398 | 0.086975 | 0.40741 | -0.21515 | -0.26093 | -0.054931 | -0.10071 | 59.6008 | -61.5189 | -61.5097 | 59.7931 | 59.7702 | 59.729 | 0.16937 | 0.12817 | 0.56763 | 121.4767 | 0.19226 | 0.11902 | 121.3074 | 0.10986 | 121.1472 | 59.7107 | -121.3898 | -61.6287 | 121.3165 | 59.7198 | 41.7526 | 59.6832
2668.2188 | 121.6324 | -58.5022 | 62.796 | 0.0016023 | 0.0001345 | 0.051344 | 0.051558 | -0.01089 | -0.0076925 | -0.017502 | -0.0021057 | 0.00066224 | -0.0011216 | -0.00010048 | -0.041281 | 0.037384 | -0.013174 | -17.2943 | 62.8601 | -58.493 | 62.7914 | -58.1039 | -58.7494 | -58.7448 | 0.041199 | 0.045776 | -0.059509 | 0.050354 | 0.11444 | 0.018311 | 0.082397 | 0.009155 | 0.064086 | -0.004578 | 0.39825 | -0.24262 | -0.24719 | -0.25177 | -0.25635 | 58.4427 | -62.7502 | -62.7457 | 58.6166 | 58.5846 | 58.5205 | 0.14191 | 0.07782 | 0.3891 | 121.2845 | 0.17395 | 0.10986 | 121.3531 | 0.10528 | 121.3623 | 58.548 | -121.2891 | -62.8555 | 121.2936 | 58.5526 | 41.2079 | 58.5434
2669.9844 | 121.7422 | -53.1189 | 67.1265 | -0.0060272 | 0.0001345 | 0.055403 | 0.051558 | 0.00021799 | -0.0098287 | -0.00062587 | -0.0082093 | 0.010702 | 0.001442 | 0.0016085 | -0.013296 | 0.018585 | -0.0029202 | -16.5619 | 65.7715 | -55.7236 | 65.4831 | -55.4535 | -56.3461 | -56.2592 | 0.11902 | 0.013733 | -0.045776 | 0.10986 | 0.18768 | 0.07782 | 0.13275 | -2.6047 | -1.355 | -1.6434 | -2.3346 | -3.1403 | -3.2272 | -0.53558 | -0.62256 | 53.0731 | -67.1127 | -67.0166 | 53.3066 | 53.2516 | 53.1967 | 0.17853 | 0.1236 | 0.27008 | 121.2067 | 0.23346 | 0.15564 | 121.4951 | 0.059509 | 118.8904 | 53.1326 | -122.85 | -67.1722 | 118.602 | 53.2288 | 36.557 | 53.2379
2671.75 | 121.3989 | -13.9801 | 107.5058 | -0.0060272 | -0.016314 | 0.047499 | 0.051558 | -0.0074726 | -0.018374 | -0.022843 | -0.0082093 | 0.0057892 | 0.0018692 | 0.0056675 | -0.018209 | 0.016235 | -0.0054838 | 4.3671 | 107.3364 | -14.1266 | 106.8649 | -13.829 | -14.1632 | -14.0945 | -0.064087 | 0.064087 | -0.10529 | 0 | 0.032043 | -0.045776 | 0.027466 | -0.14648 | -0.16937 | -0.64087 | 0.15106 | -0.11444 | -0.1831 | 0.032044 | -0.036621 | 13.8748 | -107.4417 | -107.5058 | 14.0121 | 14.0076 | 13.9343 | 0.13275 | 0.05951 | 0.29755 | 120.9915 | 0.13733 | 0.10529 | 121.463 | 0.16937 | 121.3165 | 14.0442 | -121.6324 | -107.6111 | 120.845 | 13.9801 | 18.3472 | 13.916
2673.5 | 121.7468 | -57.724 | 63.5605 | -0.0060272 | -0.0002927 | 0.054335 | 0.053053 | -0.00063661 | -0.0091879 | -0.0019077 | -0.0021057 | 0.013693 | 0.0027236 | 0.0082309 | -0.013723 | 0.01944 | 0.0034884 | -17.3904 | 63.4644 | -57.8293 | 63.5925 | -57.3212 | -57.9575 | -57.93 | 0.10529 | 0.022888 | -0.064087 | 0.086975 | 0.20599 | 0.09613 | 0.11902 | -0.10529 | -0.096131 | 0.032043 | 0.40283 | -0.20599 | -0.23346 | -0.10071 | -0.12817 | 57.6599 | -63.5376 | -63.4735 | 57.93 | 57.843 | 57.8201 | 0.18311 | 0.16022 | 0.50812 | 121.4218 | 0.27008 | 0.15106 | 121.2936 | 0.086975 | 121.1884 | 57.7469 | -121.3898 | -63.6246 | 121.3165 | 57.811 | 40.3336 | 57.8293
2675.2812 | 121.6599 | -57.4356 | 63.9084 | -0.013657 | -0.0007199 | 0.052412 | 0.049635 | 0.0010724 | -0.0079061 | -0.00041227 | -0.0021057 | 0.012411 | 0.0010146 | 0.0065219 | -0.013937 | 0.020935 | -0.0016384 | -17.1844 | 63.7848 | -57.605 | 63.9359 | -57.0053 | -57.6691 | -57.6324 | 0.036621 | 0.050354 | -0.059509 | 0.036621 | 0.10529 | 0.018311 | 0.068665 | -0.16937 | -0.1236 | 0.027466 | 0.4303 | -0.19684 | -0.23346 | -0.027466 | -0.064087 | 57.3761 | -63.858 | -63.8718 | 57.5409 | 57.5043 | 57.4539 | 0.12817 | 0.07782 | 0.59967 | 121.5408 | 0.16479 | 0.09613 | 121.3898 | 0.10986 | 121.2204 | 57.486 | -121.5134 | -63.9679 | 121.3715 | 57.4722 | 40.2512 | 57.4722
2677.0469 | 121.6919 | -55.188 | 66.1697 | 0.0016023 | 0.0029117 | 0.053694 | 0.053908 | -0.00042301 | -0.0087607 | -0.0014805 | -0.0021057 | 0.012411 | 0.0035782 | 0.0069491 | -0.013937 | 0.021362 | 7.04e-05 | -16.1957 | 66.1285 | -55.3116 | 66.1377 | -54.8859 | -55.5679 | -55.4993 | 0.022888 | 0.064087 | -0.059509 | 0.073242 | 0.10986 | 0.032043 | 0.10986 | -0.1236 | -0.041199 | -0.032044 | 0.30212 | -0.31128 | -0.37994 | -0.18768 | -0.25635 | 55.1285 | -66.1057 | -66.0965 | 55.2979 | 55.2979 | 55.22 | 0.16937 | 0.091552 | 0.42572 | 121.4493 | 0.16937 | 0.13275 | 121.4401 | 0.1236 | 121.3165 | 55.2521 | -121.4813 | -66.2292 | 121.3257 | 55.2612 | 38.9923 | 55.2109
2678.7344 | 121.6827 | -53.2791 | 68.161 | -0.021286 | -0.0005063 | 0.051344 | 0.051772 | -0.0019184 | -0.012179 | -0.0031895 | -0.0051575 | 0.010489 | 0.0044326 | -0.0011685 | -0.015432 | 0.021576 | -0.0009976 | -15.4083 | 67.8131 | -53.6453 | 68.0099 | -52.9633 | -53.7781 | -53.7094 | 0.032043 | 0.041199 | -0.082397 | 0.045776 | 0.11444 | 0.032043 | 0.086975 | -0.36621 | -0.3479 | -0.15106 | 0.31586 | -0.4303 | -0.49896 | -0.064087 | -0.13275 | 53.1967 | -68.1198 | -68.1152 | 53.3936 | 53.3661 | 53.3112 | 0.16937 | 0.11444 | 0.68207 | 121.6553 | 0.19684 | 0.12817 | 121.4584 | 0.1236 | 121.0922 | 53.3203 | -121.8063 | -68.2434 | 121.2891 | 53.3249 | 37.8708 | 53.3112
2680.4844 | 121.6507 | -52.4094 | 69.0537 | -0.013657 | -0.0009335 | 0.054549 | 0.051985 | -0.0010638 | -0.0081197 | -0.0040439 | -0.0051575 | 0.012625 | 0.00251 | 0.0052401 | -0.016073 | 0.022644 | -0.0005704 | -14.5706 | 68.9026 | -52.4872 | 68.9713 | -52.0752 | -52.6566 | -52.6291 | 0.050354 | 0.059509 | -0.064087 | 0.041199 | 0.13733 | 0.036621 | 0.073242 | -0.07782 | -0.15106 | -0.082398 | 0.33417 | -0.21973 | -0.24719 | -0.14191 | -0.16937 | 52.3453 | -68.9941 | -69.0125 | 52.5467 | 52.4826 | 52.446 | 0.13733 | 0.10071 | 0.41199 | 121.4584 | 0.20142 | 0.10529 | 121.3898 | 0.1236 | 121.312 | 52.4689 | -121.5408 | -69.1177 | 121.3806 | 52.4506 | 37.8387 | 52.4597
2682.1875 | 121.7285 | -51.059 | 70.3537 | -0.013657 | 0.0026981 | 0.05348 | 0.053053 | 0.0023542 | -0.0091879 | -0.0042575 | -0.0051575 | 0.013693 | 0.0027236 | 0.0097263 | -0.015646 | 0.02243 | 0.0013522 | -14.2502 | 70.3354 | -51.1597 | 70.2942 | -50.7843 | -51.4206 | -51.3611 | 0.009155 | 0.073242 | -0.082397 | 0.068665 | 0.1236 | 0.045776 | 0.10986 | -0.10071 | -0.018311 | -0.05951 | 0.27466 | -0.30212 | -0.36163 | -0.20142 | -0.26092 | 50.9766 | -70.2805 | -70.285 | 51.1826 | 51.1688 | 51.1047 | 0.19226 | 0.12817 | 0.37537 | 121.4539 | 0.20599 | 0.15106 | 121.4951 | 0.15564 | 121.3943 | 51.1322 | -121.5134 | -70.4361 | 121.3531 | 51.1276 | 36.8088 | 51.0681
2683.9531 | 121.6324 | -47.5845 | 73.9471 | -0.0060272 | 0.0033389 | 0.045576 | 0.056685 | 0.0021406 | -0.014529 | -0.0083163 | -0.0051575 | 0.013907 | 0.00251 | 0.0082309 | -0.015646 | 0.020935 | 0.0011386 | -12.442 | 73.8785 | -47.6212 | 73.8693 | -47.2504 | -47.8592 | -47.7997 | -0.045776 | 0.073242 | -0.064087 | 0.009155 | 0.041199 | -0.068665 | 0.041199 | -0.036621 | -0.068665 | -0.07782 | 0.33417 | -0.21515 | -0.27466 | -0.17853 | -0.23804 | 47.5204 | -73.8739 | -73.938 | 47.6257 | 47.6257 | 47.5159 | 0.10529 | -0.004578 | 0.37079 | 121.4905 | 0.10529 | 0.073242 | 121.4996 | 0.13733 | 121.463 | 47.6578 | -121.5683 | -74.0112 | 121.4539 | 47.5937 | 35.1425 | 47.5388
2685.7188 | 121.756 | -44.2566 | 77.2202 | 0.0016023 | -0.0026425 | 0.05284 | 0.051558 | 0.00064519 | -0.01047 | -0.0010531 | -0.011261 | 0.009848 | 0.0029372 | 0.00054052 | -0.013723 | 0.02179 | 0.0019932 | -10.437 | 77.3712 | -44.0552 | 77.4307 | -43.7027 | -44.3207 | -44.3069 | 0.14191 | -0.004578 | -0.07782 | 0.10986 | 0.22888 | 0.13733 | 0.14648 | 0.20142 | 0.15106 | 0.21057 | 0.55389 | -0.050354 | -0.064087 | -0.25177 | -0.2655 | 44.1788 | -77.2247 | -77.1103 | 44.4855 | 44.4031 | 44.3939 | 0.2243 | 0.21515 | 0.35248 | 121.4859 | 0.3067 | 0.18768 | 121.4264 | 0.073242 | 121.6278 | 44.252 | -121.2753 | -77.298 | 121.6873 | 44.3665 | 33.8196 | 44.3985
2687.4062 | 121.6415 | -41.4871 | 80.04 | -0.21202 | 0.0003483 | 0.050276 | 0.053908 | -0.00020941 | -0.0096151 | -0.0031895 | -0.0021057 | 0.011343 | 0.00037383 | 0.0058811 | -0.014364 | 0.02179 | 0.0015658 | -9.1965 | 80.2094 | -41.2674 | 79.9667 | -41.2308 | -41.6748 | -41.7023 | -0.027466 | 0.073242 | -0.091553 | -0.045776 | 0.073242 | -0.022888 | 0.027466 | 0.21973 | 0.16937 | -0.073242 | 0.25635 | -0.21515 | -0.18768 | -0.43488 | -0.40741 | 41.3956 | -79.9667 | -80.0858 | 41.5604 | 41.5146 | 41.4642 | 0.11902 | 0.068665 | 0.036621 | 121.2341 | 0.16479 | 0.045777 | 121.4767 | 0.16479 | 121.6965 | 41.5604 | -121.3074 | -80.1315 | 121.4539 | 41.4413 | 32.2906 | 41.4597
2689.1562 | 121.669 | -38.6215 | 82.901 | -0.013657 | -7.9104e-05 | 0.048994 | 0.054121 | -0.00042301 | -0.010897 | -0.0014805 | -0.0051575 | 0.01412 | 0.0018692 | 0.0065219 | -0.014791 | 0.022644 | -0.002493 | -7.9147 | 83.0109 | -38.5483 | 82.8598 | -38.324 | -38.8687 | -38.7589 | -0.036621 | 0.068665 | -0.091553 | -0.004578 | 0.041199 | -0.036621 | 0.050354 | 0.073242 | 0.10986 | -0.041199 | 0.29755 | -0.13733 | -0.24719 | -0.21057 | -0.32043 | 38.53 | -82.8323 | -82.9056 | 38.6627 | 38.6719 | 38.5849 | 0.14191 | 0.054932 | 0.2243 | 121.4081 | 0.13275 | 0.086975 | 121.5591 | 0.16022 | 121.6324 | 38.6902 | -121.4493 | -82.9926 | 121.4813 | 38.6169 | 30.7068 | 38.5849
2690.9219 | 121.7514 | -45.5246 | 75.9796 | -0.013657 | 0.0029117 | 0.05348 | 0.051772 | 0.00043159 | -0.0087607 | -0.0025485 | -0.0051575 | 0.011557 | 0.0012282 | -0.0048001 | -0.015432 | 0.022003 | 0.0002842 | -11.5128 | 75.8652 | -45.6253 | 76.0025 | -45.1492 | -45.7718 | -45.7169 | 0.13733 | -0.004578 | -0.045776 | 0.10529 | 0.20599 | 0.09613 | 0.14191 | -0.10071 | -0.11444 | 0.022888 | 0.37537 | -0.19226 | -0.24719 | -0.091553 | -0.14649 | 45.4788 | -75.9842 | -75.8743 | 45.7306 | 45.6665 | 45.6207 | 0.18768 | 0.14191 | 0.47607 | 121.6278 | 0.25177 | 0.15106 | 121.4905 | 0.041198 | 121.3898 | 45.52 | -121.6049 | -76.0254 | 121.5271 | 45.6299 | 34.0118 | 45.6619
2692.625 | 120.9274 | -41.9952 | 79.6143 | -0.013657 | 0.0005619 | 0.051344 | 0.054335 | -0.0087542 | -0.0098287 | -0.0087437 | -0.0021057 | 0.0087798 | 0.0037918 | 0.00011332 | -0.018637 | 0.014099 | -0.012747 | -9.9747 | 79.1428 | -42.4484 | 79.1061 | -42.0593 | -42.7002 | -42.6773 | 0.041199 | 0.059509 | -0.064087 | 0.027466 | 0.12817 | 0.027466 | 0.082397 | -0.45319 | -0.4715 | -0.50812 | -0.064087 | -0.68207 | -0.70496 | -0.22888 | -0.25177 | 41.9312 | -79.5547 | -79.5868 | 42.1234 | 42.0776 | 42.0227 | 0.14648 | 0.091553 | 0.3891 | 121.5546 | 0.19226 | 0.091553 | 121.5912 | 0.1236 | 121.138 | 42.0547 | -122.0627 | -79.6783 | 121.1014 | 42.0227 | 32.0206 | 42.0364
2694.3594 | 121.4767 | -40.48 | 81.0745 | -0.0060272 | 0.0007755 | 0.053694 | 0.05284 | -0.003841 | -0.010043 | -0.0034031 | -0.0021057 | 0.010489 | 0.0020828 | -0.0024503 | -0.015432 | 0.021362 | -0.0009976 | -8.8531 | 81.2073 | -40.3244 | 81.1386 | -40.0818 | -40.6586 | -40.686 | -0.004578 | 0.050354 | -0.068665 | -0.027466 | 0.10071 | 0.004578 | 0.050354 | 0.15564 | 0.13275 | 0.064087 | 0.39825 | -0.20599 | -0.17853 | -0.36163 | -0.33417 | 40.4114 | -81.0242 | -81.102 | 40.5807 | 40.5304 | 40.4846 | 0.11902 | 0.073243 | 0.24262 | 121.463 | 0.16937 | 0.041199 | 121.5317 | 0.11902 | 121.6873 | 40.5304 | -121.3989 | -81.1432 | 121.6187 | 40.4526 | 31.6269 | 40.4755
2696.0781 | 121.756 | -43.2587 | 78.2867 | -0.0060272 | 0.0009891 | 0.053694 | 0.052199 | -0.0017048 | -0.0081197 | -0.0027621 | -0.0021057 | 0.011984 | 0.0022964 | 0.00075412 | -0.015432 | 0.020508 | -0.0009976 | -10.5515 | 78.1815 | -43.3731 | 78.2364 | -42.9611 | -43.5425 | -43.4555 | 0.041199 | 0.041199 | -0.054932 | 0.027466 | 0.13733 | 0.059509 | 0.10071 | -0.11444 | -0.10528 | -0.050354 | 0.29755 | -0.19684 | -0.28381 | -0.082397 | -0.16937 | 43.2037 | -78.2455 | -78.2593 | 43.396 | 43.3594 | 43.3182 | 0.15564 | 0.11444 | 0.41199 | 121.6095 | 0.19226 | 0.082398 | 121.5546 | 0.096131 | 121.4401 | 43.2999 | -121.6599 | -78.3417 | 121.4951 | 43.2861 | 32.7072 | 43.2999
2697.8281 | 121.7926 | -40.8188 | 80.69 | -0.013657 | 0.0031253 | 0.052199 | 0.05348 | 0.001286 | -0.0079061 | -0.0059665 | -0.0021057 | 0.013052 | 0.00016023 | 0.0031039 | -0.015646 | 0.021576 | -0.0005704 | -9.4025 | 80.4016 | -41.1667 | 80.5115 | -40.7639 | -41.2537 | -41.1804 | 0.082397 | 0.032043 | -0.064087 | 0.07782 | 0.16479 | 0.068665 | 0.13733 | -0.3479 | -0.28839 | -0.17853 | 0.054932 | -0.36163 | -0.43487 | -0.013733 | -0.086975 | 40.7547 | -80.658 | -80.6122 | 40.9836 | 40.9561 | 40.8875 | 0.20142 | 0.13275 | 0.40283 | 121.6782 | 0.22888 | 0.14191 | 121.5683 | 0.09613 | 121.2204 | 40.8508 | -121.8567 | -80.7541 | 121.3303 | 40.8966 | 31.4163 | 40.9012
2699.5938 | 121.8018 | -39.949 | 81.4819 | -0.0060272 | 0.0033389 | 0.05284 | 0.055189 | 0.00064519 | -0.0074789 | -0.0055393 | -0.0021057 | 0.012839 | 0.0027236 | 0.0060947 | -0.015005 | 0.02243 | 0.0011386 | -8.6975 | 81.5735 | -40.036 | 81.7612 | -39.679 | -40.3015 | -40.2145 | 0.086975 | 0.041199 | -0.059509 | 0.086975 | 0.1831 | 0.073242 | 0.13275 | -0.086975 | 0.091552 | 0.27923 | 0.27008 | -0.2655 | -0.35248 | -0.17853 | -0.2655 | 39.8895 | -81.4407 | -81.395 | 40.1321 | 40.0818 | 40.0223 | 0.19226 | 0.13275 | 0.35706 | 121.7972 | 0.24261 | 0.14648 | 121.6095 | 0.10071 | 121.5225 | 39.9902 | -121.5179 | -81.5414 | 121.7102 | 40.036 | 31.2515 | 40.036
2701.2969 | 121.8201 | -44.1971 | 77.2888 | -0.013657 | 0.0022709 | 0.05284 | 0.054549 | -0.00063661 | -0.0087607 | -0.0038303 | -0.0051575 | 0.010702 | 0.0012282 | 0.011008 | -0.016928 | 0.022217 | -0.0044156 | -11.4807 | 76.5976 | -45.0256 | 77.1652 | -43.8904 | -44.6686 | -44.6091 | 0.054932 | 0.041199 | -0.064087 | 0.07782 | 0.16937 | 0.064087 | 0.14648 | -0.82855 | -0.69122 | -0.1236 | 0.3067 | -0.41199 | -0.4715 | 0.41656 | 0.35706 | 44.133 | -77.2476 | -77.211 | 44.3665 | 44.3436 | 44.2612 | 0.21057 | 0.12817 | 1.1353 | 122.1909 | 0.23346 | 0.14191 | 121.6232 | 0.10529 | 120.7947 | 44.2383 | -122.3145 | -77.3529 | 121.3623 | 44.2749 | 32.7164 | 44.252
2703.0469 | 121.6873 | -42.7277 | 79.0787 | 0.0016023 | -0.0009335 | 0.053908 | 0.050276 | -0.00020941 | -0.010683 | -0.0042575 | -0.0021057 | 0.013693 | 0.001442 | 0.0020359 | -0.011587 | 0.020081 | 0.0039158 | -10.1852 | 78.9185 | -42.6819 | 79.4998 | -41.5054 | -42.4164 | -42.5354 | -0.036621 | 0.07782 | -0.082397 | -0.059509 | 0.059509 | -0.009155 | 0.027466 | 0.045776 | -0.16022 | 0.42114 | 1.2222 | 0.19226 | 0.31128 | 0.14648 | 0.2655 | 42.6453 | -79.0009 | -79.1382 | 42.7872 | 42.7551 | 42.7185 | 0.10986 | 0.073242 | 1.1765 | 122.1817 | 0.14191 | 0.022888 | 121.6003 | 0.16022 | 121.6461 | 42.8055 | -121.7606 | -79.1611 | 122.2275 | 42.6682 | 32.5424 | 42.691
2704.8438 | 121.8567 | -38.4659 | 82.8415 | -0.013657 | 0.0016299 | 0.054121 | 0.051772 | 0.00085879 | -0.0074789 | -0.0027621 | -0.0021057 | 0.012839 | 0.0012282 | 0.0026767 | -0.014364 | 0.024139 | -0.0031338 | -7.1777 | 83.7112 | -37.7838 | 83.2809 | -37.9532 | -38.4567 | -38.4293 | 0.10071 | 0.045776 | -0.045776 | 0.086975 | 0.1831 | 0.082397 | 0.15106 | 0.68207 | 0.86975 | 0.43945 | 0.5127 | 0.036621 | 0.009155 | -0.64545 | -0.67291 | 38.4201 | -82.7957 | -82.7545 | 38.649 | 38.6169 | 38.5483 | 0.19684 | 0.12817 | -0.16937 | 121.0648 | 0.22888 | 0.13275 | 121.4951 | 0.091552 | 122.1771 | 38.5117 | -120.6253 | -82.8873 | 121.7468 | 38.5529 | 31.2881 | 38.5666
2706.5312 | 121.7926 | -37.294 | 84.4116 | -0.013657 | 0.0018435 | 0.053908 | 0.055189 | 0.0038494 | -0.0083335 | -0.0027621 | -0.0021057 | 0.012625 | -0.0015488 | 0.0033175 | -0.016714 | 0.022003 | 0.0011386 | -7.1091 | 84.2239 | -37.3947 | 84.1873 | -37.0697 | -37.738 | -37.6144 | 0.068665 | 0.041199 | -0.064087 | 0.07782 | 0.17853 | 0.086975 | 0.14191 | -0.10071 | -0.18768 | -0.2243 | 0.2243 | -0.32043 | -0.44403 | -0.21973 | -0.34332 | 37.2299 | -84.3704 | -84.3338 | 37.4725 | 37.4359 | 37.381 | 0.20599 | 0.15106 | 0.32501 | 121.582 | 0.24261 | 0.14191 | 121.6187 | 0.10529 | 121.5179 | 37.3352 | -121.8063 | -84.4757 | 121.4813 | 37.3718 | 30.1849 | 37.3627
2708.2969 | 120.9412 | -31.7368 | 89.9139 | -0.013657 | 0.0020571 | 0.036604 | 0.055403 | 0.00085879 | -0.012606 | -0.0070347 | -0.0082093 | 0.015189 | 0.0012282 | 0.010154 | -0.018209 | 0.020935 | -0.003561 | -4.3991 | 89.8132 | -31.8604 | 89.8178 | -31.5033 | -32.0938 | -31.9931 | -0.045776 | 0.068665 | -0.082397 | -0.022888 | 0.041199 | -0.050354 | 0.050354 | -0.1236 | -0.10071 | -0.09613 | 0.23346 | -0.25635 | -0.35706 | -0.13275 | -0.23346 | 31.6544 | -89.8453 | -89.9368 | 31.778 | 31.7871 | 31.6864 | 0.13275 | 0.032043 | 0.35706 | 121.6782 | 0.1236 | 0.059509 | 121.6736 | 0.15106 | 121.55 | 31.8054 | -121.7743 | -89.9963 | 121.5546 | 31.7139 | 27.3376 | 31.691
2710.0625 | 121.4996 | -30.5649 | 91.0721 | 0.0016023 | -0.0032833 | 0.051558 | 0.052199 | -0.0012774 | -0.0089743 | -0.0036167 | -0.0021057 | 0.011343 | 0.00251 | -0.00074128 | -0.01415 | 0.020294 | -0.0012112 | -3.4836 | 90.3625 | -31.1554 | 89.772 | -31.2561 | -31.192 | -30.9219 | -0.027466 | 0.082397 | -0.073242 | -0.059509 | 0.086975 | 0.009155 | 0.041199 | -0.59052 | -0.70953 | -1.3 | -0.69122 | -0.35706 | -0.62714 | 0.23346 | -0.036621 | 30.4916 | -90.9897 | -91.1316 | 30.6519 | 30.6061 | 30.574 | 0.11444 | 0.082397 | -0.10071 | 120.9274 | 0.16022 | 0.013733 | 121.5179 | 0.15564 | 120.9274 | 30.6473 | -122.2275 | -91.1453 | 120.3369 | 30.5054 | 27.0813 | 30.5374
2711.7656 | 120.9595 | -29.0543 | 92.6834 | -0.013657 | -0.0011471 | 0.051131 | 0.050703 | -0.001491 | -0.0094015 | -0.0066073 | 0.0009461 | 0.012198 | 0.0044326 | 0.0026767 | -0.017141 | 0.020935 | 7.04e-05 | -3.035 | 92.3584 | -29.3381 | 92.3126 | -28.981 | -29.5807 | -29.5578 | -0.036621 | 0.073242 | -0.091553 | -0.050354 | 0.082397 | -0.018311 | 0.045776 | -0.28381 | -0.32501 | -0.37079 | 0.073242 | -0.50354 | -0.52643 | -0.21973 | -0.24261 | 28.9627 | -92.6102 | -92.7338 | 29.1367 | 29.1 | 29.0359 | 0.13733 | 0.073242 | 0.35706 | 121.6507 | 0.17395 | 0.041199 | 121.6965 | 0.16479 | 121.4127 | 29.1275 | -122.0215 | -92.775 | 121.3669 | 29.0039 | 26.0193 | 29.0176
2713.4688 | 121.756 | -41.1942 | 80.4474 | -0.22728 | -0.0015743 | 0.052199 | 0.049635 | -0.002132 | -0.010683 | -0.0027621 | -0.0021057 | 0.012625 | 0.0033646 | 0.0058811 | -0.015005 | 0.021362 | -0.000784 | -9.4666 | 80.7129 | -40.9378 | 80.3696 | -40.654 | -41.2216 | -41.2445 | -0.045776 | 0.059509 | -0.082397 | -0.059509 | 0.064087 | -0.004578 | 0.032043 | 0.25635 | 0.2655 | -0.07782 | 0.54016 | -0.050354 | -0.027466 | -0.3067 | -0.28381 | 41.1118 | -80.3879 | -80.5069 | 41.2582 | 41.2262 | 41.1896 | 0.11444 | 0.077819 | 0.28381 | 121.3074 | 0.14648 | 0.022888 | 121.6507 | 0.14191 | 121.907 | 41.2537 | -121.3852 | -80.5298 | 121.5637 | 41.1346 | 31.7276 | 41.1484
2715.25 | 121.9116 | -120.0027 | 1.6067 | -0.013657 | -0.0037107 | 0.055189 | 0.053908 | -0.0025592 | -0.011111 | -0.0025485 | -0.0021057 | 0.013266 | -0.00048057 | 0.00054052 | -0.018423 | 0.013458 | -0.0099698 | -51.6586 | 1.5381 | -120.2225 | 1.4099 | -118.9774 | -120.1218 | -120.1767 | -0.054932 | 0.064087 | 0.013733 | -0.009155 | 0.086975 | -0.018311 | 0.050354 | -0.21973 | -0.068664 | -0.19684 | 1.0254 | -0.17395 | -0.11902 | 0.045776 | 0.10071 | 120.0165 | -1.5427 | -1.6159 | 120.0897 | 120.0531 | 119.9844 | 0.036621 | -0.032044 | 1.2451 | 121.6324 | 0.073242 | -0.022888 | 121.7606 | 0.050354 | 121.5408 | 120.0668 | -121.8292 | -1.593 | 121.4127 | 119.9936 | 68.3441 | 119.9478
2717.0156 | 121.9757 | -121.1655 | 0.46692 | -0.0060272 | -0.0034971 | 0.054762 | 0.051558 | -0.0012774 | -0.011751 | -0.00083947 | -0.0051575 | 0.0089934 | -0.001976 | -0.0022367 | -0.013723 | 0.019653 | 0.0002842 | -52.1439 | 0.37537 | -121.3028 | 0.31128 | -120.0302 | -121.2067 | -121.2296 | 0.022888 | 0.041199 | -0.068665 | 0.059509 | 0.14648 | 0.068665 | 0.11902 | -0.13733 | -0.091553 | -0.15564 | 1.1353 | -0.064087 | -0.041199 | 0.073242 | 0.09613 | 121.0968 | -0.42572 | -0.40741 | 121.3119 | 121.2845 | 121.2341 | 0.18768 | 0.13733 | 1.2726 | 121.6141 | 0.21515 | 0.12817 | 121.6782 | 0.10986 | 121.5408 | 121.2067 | -121.7697 | -0.53558 | 121.4767 | 121.225 | 69.0216 | 121.1884
2718.7031 | 121.843 | -121.2891 | 0.45319 | -0.013657 | -0.0032833 | 0.054335 | 0.054335 | -0.0025592 | -0.011751 | -0.0019077 | -0.0051575 | 0.01348 | 0.00058743 | 0.0031039 | -0.013937 | 0.02179 | -0.000784 | -52.1896 | 0.37537 | -121.3577 | 0.21973 | -120.1126 | -121.2799 | -121.3348 | -0.045776 | 0.068665 | -0.082397 | -0.009155 | 0.036621 | -0.004578 | 0.050354 | -0.068665 | -0.07782 | -0.23346 | 1.1765 | -0.045777 | 0.009155 | 0.022888 | 0.07782 | 121.2067 | -0.38452 | -0.46234 | 121.3257 | 121.3394 | 121.2845 | 0.13275 | 0.077819 | 1.2451 | 121.5775 | 0.11902 | 0.073242 | 121.7331 | 0.15106 | 121.6644 | 121.3577 | -121.8109 | -0.53558 | 121.5088 | 121.2799 | 69.0994 | 121.2433
2720.4062 | 121.9803 | -121.2112 | 0.48065 | -0.013657 | -0.0026425 | 0.05049 | 0.052199 | -0.0061908 | -0.0087607 | -0.0038303 | -0.0051575 | 0.010062 | 0.001442 | -0.0015957 | -0.013082 | 0.02243 | 0.0007114 | -52.1255 | 0.40741 | -121.3074 | 0.38452 | -119.957 | -121.1472 | -121.1609 | 0.10529 | 0.022888 | -0.059509 | 0.1236 | 0.1831 | 0.10529 | 0.15564 | -0.09613 | -0.073242 | -0.096131 | 1.2543 | 0.050354 | 0.064087 | 0.14648 | 0.16022 | 121.1517 | -0.45776 | -0.35706 | 121.3943 | 121.3669 | 121.3165 | 0.21515 | 0.16479 | 1.3504 | 121.6919 | 0.24261 | 0.1831 | 121.7148 | 0.082397 | 121.6187 | 121.2341 | -121.788 | -0.54016 | 121.5958 | 121.3348 | 69.0857 | 121.3165
2722.1562 | 122.0306 | -120.9366 | 0.68665 | -0.013657 | -0.0024289 | 0.051131 | 0.051344 | 0.0027814 | -0.010256 | -0.0031895 | -0.0082093 | 0.011984 | -0.00048057 | -0.0028775 | -0.015219 | 0.02243 | -0.0033474 | -52.1759 | 0.58136 | -121.1105 | 0.62714 | -119.7144 | -120.9274 | -120.9686 | 0.12817 | 0.027466 | -0.041199 | 0.10986 | 0.18768 | 0.11444 | 0.14648 | -0.17395 | -0.10529 | -0.05951 | 1.2222 | -0.032044 | 0.009155 | 0.14191 | 0.18311 | 120.8954 | -0.65918 | -0.57678 | 121.1243 | 121.0831 | 121.051 | 0.18768 | 0.15564 | 1.3962 | 121.7377 | 0.22888 | 0.15106 | 121.6919 | 0.068665 | 121.5179 | 120.9641 | -121.7972 | -0.72784 | 121.5637 | 121.0464 | 68.7607 | 121.0648
2723.8438 | 102.681 | -61.9354 | 59.7519 | -0.0060272 | -0.0028561 | 0.051985 | 0.05284 | -0.0012774 | -0.010897 | -0.0046847 | -0.011261 | -0.0040376 | 0.00080103 | -0.0065091 | 0.26591 | 0.038239 | 0.032755 | -20.137 | 59.6237 | -62.0132 | 59.7748 | -61.2762 | -62.0636 | -61.94 | 0.041199 | 0.064087 | -0.07782 | 0.068665 | 0.09613 | 0.032043 | 0.07782 | -0.07782 | -0.12817 | 0.022888 | 0.65918 | -0.004577 | -0.12817 | 0.073243 | -0.050354 | 61.8576 | -59.6878 | -59.6832 | 62.0316 | 62.0132 | 61.9675 | 0.15564 | 0.10986 | 0.737 | 121.788 | 0.17395 | 0.14649 | 121.637 | 0.14191 | 121.5591 | 61.9995 | -121.7651 | -59.8297 | 121.7102 | 62.0041 | 41.7984 | 61.9766
2725.6094 | 121.4172 | -61.5005 | 60.1913 | -0.0060272 | -0.0009335 | 0.05348 | 0.051344 | 0.00064519 | -0.0091879 | -0.0019077 | -0.0051575 | 0.012411 | 0.00251 | 0.0054537 | -0.013296 | 0.020508 | 0.0017794 | -20.1279 | 60.0082 | -61.5738 | 60.228 | -60.7819 | -61.5829 | -61.5738 | 0.07782 | 0.054932 | -0.073242 | 0.064087 | 0.14648 | 0.068665 | 0.10071 | -0.073243 | -0.1831 | 0.036621 | 0.71869 | -0.073243 | -0.082398 | 0 | -0.009155 | 61.4273 | -60.1364 | -60.1273 | 61.647 | 61.6013 | 61.5692 | 0.17395 | 0.14191 | 0.79193 | 121.8018 | 0.21973 | 0.13733 | 121.582 | 0.12817 | 121.5088 | 61.5555 | -121.7651 | -60.2646 | 121.7285 | 61.5646 | 41.3727 | 61.5784
2727.2969 | 121.6324 | -61.3815 | 60.3149 | -0.013657 | 0.0014163 | 0.053267 | 0.053694 | 0.0023542 | -0.0096151 | -0.0031895 | -0.0051575 | 0.0094208 | 0.0033646 | -0.0024503 | -0.030813 | 0.038239 | -0.0095426 | -20.0134 | 60.2325 | -61.4365 | 60.3241 | -60.7178 | -61.5143 | -61.4777 | 0.036621 | 0.045776 | -0.07782 | 0.054932 | 0.13275 | 0.022888 | 0.07782 | -0.054931 | -0.082397 | 0.009156 | 0.66376 | -0.09613 | -0.13275 | -0.041199 | -0.07782 | 61.3037 | -60.2692 | -60.26 | 61.5143 | 61.4594 | 61.4044 | 0.15564 | 0.10071 | 0.71869 | 121.7606 | 0.21057 | 0.13275 | 121.669 | 0.1236 | 121.6141 | 61.4273 | -121.7514 | -60.3928 | 121.7056 | 61.4365 | 41.3681 | 61.4182
2729.0469 | 121.907 | -61.8988 | 59.7382 | -0.0060272 | -0.0017881 | 0.053267 | 0.051985 | -0.0019184 | -0.0089743 | -0.0014805 | -0.0021057 | 0.010702 | 0.0018692 | 0.00075412 | -0.017355 | 0.020081 | -0.0033474 | -20.2881 | 59.6695 | -61.9858 | 59.8434 | -61.1755 | -62.0041 | -61.9904 | 0.086975 | 0.032043 | -0.050354 | 0.054932 | 0.19684 | 0.091553 | 0.10529 | -0.086975 | -0.068664 | 0.10529 | 0.72327 | -0.091552 | -0.10529 | -0.004577 | -0.01831 | 61.8484 | -59.7061 | -59.6832 | 62.0956 | 62.0041 | 61.9904 | 0.15564 | 0.14191 | 0.81024 | 121.8292 | 0.24719 | 0.10529 | 121.6553 | 0.082397 | 121.5683 | 61.9308 | -121.7239 | -59.7885 | 121.7422 | 61.9537 | 41.6107 | 61.9858
2730.75 | 121.669 | -61.8393 | 59.8572 | -0.013657 | 0.0012027 | 0.054335 | 0.052199 | 0.0044904 | -0.0072653 | -0.0044711 | -0.0051575 | 0.012839 | 0.00251 | 0.0065219 | -0.016073 | 0.02179 | -0.000784 | -20.4666 | 59.7382 | -61.972 | 59.7656 | -61.2625 | -62.1002 | -62.0544 | -0.036621 | 0.082397 | -0.073242 | -0.013733 | 0.073242 | -0.041199 | 0.059509 | -0.13275 | -0.11902 | -0.091553 | 0.57678 | -0.21515 | -0.26093 | -0.082397 | -0.12817 | 61.7661 | -59.7748 | -59.8709 | 61.9125 | 61.8988 | 61.7981 | 0.13275 | 0.032043 | 0.70953 | 121.7377 | 0.14648 | 0.059509 | 121.7102 | 0.15564 | 121.5775 | 61.9217 | -121.8292 | -59.9304 | 121.6049 | 61.8256 | 41.3727 | 61.8027
2732.4375 | 121.875 | -62.1048 | 59.6237 | -0.013657 | -0.0017881 | 0.05348 | 0.050703 | -0.00042301 | -0.0091879 | -0.0051121 | -0.0051575 | 0.008139 | 0.0020828 | 0.0041721 | -0.01415 | 0.019653 | 7.04e-05 | -20.5032 | 59.4864 | -62.1597 | 59.6649 | -61.3449 | -62.1643 | -62.1552 | 0.073242 | 0.041199 | -0.068665 | 0.009155 | 0.14191 | 0.059509 | 0.082397 | -0.054932 | -0.13733 | 0.041199 | 0.75989 | -0.050354 | -0.05951 | 0.004578 | -0.004578 | 62.0361 | -59.5825 | -59.6146 | 62.2467 | 62.1872 | 62.1643 | 0.15106 | 0.12817 | 0.81482 | 121.8246 | 0.21057 | 0.07782 | 121.6461 | 0.10986 | 121.5912 | 62.146 | -121.7834 | -59.6924 | 121.7697 | 62.114 | 41.6016 | 62.178
2734.1875 | 121.9162 | -62.059 | 59.6191 | -0.013657 | 0.0001345 | 0.05284 | 0.052626 | -0.0023456 | -0.0083335 | -0.0046847 | -0.0082093 | 0.011771 | -0.00048057 | 0.0031039 | -0.01351 | 0.023499 | 0.0002842 | -20.6223 | 59.5047 | -62.1323 | 59.6329 | -61.3861 | -62.2284 | -62.1872 | 0.041199 | 0.054932 | -0.068665 | 0.013733 | 0.15106 | 0.064087 | 0.091553 | -0.073242 | -0.11444 | 0.013733 | 0.67291 | -0.12817 | -0.16937 | -0.054932 | -0.096131 | 61.9904 | -59.5642 | -59.6054 | 62.2101 | 62.1506 | 62.1231 | 0.16022 | 0.13275 | 0.74616 | 121.7651 | 0.21973 | 0.082398 | 121.637 | 0.1236 | 121.5637 | 62.114 | -121.7514 | -59.6878 | 121.6919 | 62.0728 | 41.4368 | 62.1002
2735.875 | 121.8613 | -62.2559 | 59.5047 | -0.013657 | -0.0024289 | 0.052199 | 0.052626 | -0.001491 | -0.0091879 | -0.0010531 | -0.0021057 | 0.011771 | 0.0018692 | 0.010581 | -0.01351 | 0.022644 | -0.0016384 | -20.6543 | 59.3353 | -62.3566 | 59.4635 | -61.5601 | -62.4161 | -62.3886 | 0.004578 | 0.064087 | -0.068665 | -0.041199 | 0.09613 | -0.013733 | 0.036621 | -0.10071 | -0.16937 | -0.041199 | 0.6958 | -0.13275 | -0.16022 | -0.032044 | -0.05951 | 62.1872 | -59.4406 | -59.5459 | 62.352 | 62.2925 | 62.2421 | 0.10529 | 0.054932 | 0.79651 | 121.8201 | 0.16479 | 0.027466 | 121.6919 | 0.13275 | 121.5912 | 62.3199 | -121.8613 | -59.5734 | 121.7194 | 62.2147 | 41.6016 | 62.2604
2737.6406 | 121.9391 | -62.7457 | 58.9417 | -0.0060272 | 0.0018435 | 0.054335 | 0.052412 | -0.00063661 | -0.0081197 | -0.0034031 | -0.0021057 | 0.010916 | 0.001442 | 0.011863 | -0.015219 | 0.021149 | 0.0011386 | -20.9702 | 58.8409 | -62.8418 | 58.9783 | -62.0453 | -62.9105 | -62.8555 | 0.045776 | 0.032043 | -0.050354 | 0.027466 | 0.12817 | 0.054932 | 0.09613 | -0.09613 | -0.10071 | 0.036621 | 0.70038 | -0.10986 | -0.16479 | -0.013733 | -0.068664 | 62.6953 | -58.9096 | -58.9142 | 62.8738 | 62.8418 | 62.8006 | 0.14648 | 0.10529 | 0.79651 | 121.8201 | 0.17853 | 0.07782 | 121.6827 | 0.082397 | 121.5866 | 62.7777 | -121.7834 | -58.992 | 121.7239 | 62.7731 | 41.7755 | 62.7914
2739.3281 | 121.8796 | -63.1851 | 58.6075 | -0.013657 | -0.0017881 | 0.052199 | 0.053267 | -0.00042301 | -0.0087607 | -0.0063937 | -0.0051575 | 0.013907 | 0.0027236 | 0.0078037 | -0.015005 | 0.02243 | 0.0007114 | -21.1761 | 58.4793 | -63.2538 | 58.5114 | -62.5168 | -63.3545 | -63.3408 | -0.041199 | 0.07782 | -0.091553 | -0.032043 | 0.086975 | 0.004578 | 0.050354 | -0.068664 | -0.12817 | -0.09613 | 0.66833 | -0.15564 | -0.16937 | -0.086975 | -0.10071 | 63.0936 | -58.5297 | -58.6395 | 63.2721 | 63.2355 | 63.1897 | 0.14191 | 0.096131 | 0.737 | 121.7651 | 0.17853 | 0.05951 | 121.7331 | 0.16937 | 121.6644 | 63.2629 | -121.8613 | -58.699 | 121.6965 | 63.1531 | 42.009 | 63.1439
2741.0781 | 121.9025 | -63.9267 | 57.8293 | -0.0060272 | -0.0009335 | 0.051131 | 0.052199 | -0.0032 | -0.0098287 | -0.0040439 | -0.0051575 | 0.011984 | 0.0027236 | 0.0033175 | -0.015859 | 0.020935 | 7.04e-05 | -21.6568 | 57.7011 | -64.0274 | 57.7698 | -63.2584 | -64.0915 | -64.0915 | -0.036621 | 0.07782 | -0.07782 | -0.013733 | 0.091553 | 0 | 0.059509 | -0.10071 | -0.12817 | -0.05951 | 0.66833 | -0.1648 | -0.1648 | -0.064087 | -0.064087 | 63.8489 | -57.7515 | -57.843 | 64.0182 | 63.9862 | 63.9267 | 0.13733 | 0.07782 | 0.76904 | 121.7972 | 0.16937 | 0.064087 | 121.7285 | 0.15564 | 121.6278 | 64.0045 | -121.8567 | -57.9071 | 121.6965 | 63.913 | 42.2699 | 63.8901
2742.7656 | 121.8933 | -2.4399 | 119.014 | 0.15419 | 0.029187 | 0.11095 | 0.037032 | 0.042729 | 0.057035 | 0.051925 | -0.032623 | -0.0040376 | -5.3368e-05 | -0.0062955 | -0.04064 | 0.0032044 | -0.010824 | 12.4924 | 119.0872 | -2.1423 | 118.9224 | -2.0874 | -2.4536 | -2.3895 | -0.10986 | -0.004578 | 0.009155 | -0.050354 | 0.041199 | -0.059509 | 0.054932 | 0.29755 | 0.073242 | -0.091553 | 0.35248 | 0.050354 | -0.013733 | -0.24719 | -0.31128 | 2.449 | -119.0186 | -119.0643 | 2.4811 | 2.4948 | 2.3804 | 0.045777 | -0.068664 | 0.054932 | 121.0648 | 0.032044 | -0.059509 | 121.2296 | -0.013733 | 121.5271 | 2.4353 | -121.1563 | -119.0048 | 121.3623 | 2.3895 | 14.9323 | 2.33
2744.5156 | 121.9666 | -4.0054 | 117.453 | 0.17708 | -0.0024289 | 0.049208 | 0.050703 | -0.0051226 | -0.0096151 | -0.0038303 | -0.0021057 | 0.013052 | 0.0016556 | -0.0026639 | -0.016073 | 0.020721 | -0.0044156 | 11.4944 | 112.3718 | -4.0146 | 117.5125 | -3.6301 | -3.9917 | -3.9597 | -0.045776 | -0.27924 | -0.09613 | -0.041199 | 0.054932 | -0.013733 | 0.032043 | -0.009155 | -5.0812 | 0.059509 | 0.37537 | 0.045776 | 0.013733 | 0.054931 | 0.022888 | 3.9093 | -117.7322 | -117.4942 | 4.0604 | 4.0375 | 3.9917 | 0.12817 | 0.082397 | 0.38452 | 121.5271 | 0.15106 | 0.054931 | 116.3864 | -0.18311 | 116.3773 | 3.7262 | -121.4676 | -117.5491 | 121.5179 | 3.9642 | 15.4999 | 3.9597
2746.2812 | 121.788 | -116.5512 | 4.8019 | 0.15419 | -0.0064877 | 0.037886 | 0.038954 | -0.011531 | -0.02051 | -0.015152 | -0.21268 | 0.0010894 | -0.0075302 | 0.00075412 | -0.017782 | 0.016663 | -0.005911 | -39.8071 | 4.9393 | -113.4705 | 0.10986 | -95.0363 | -103.5324 | -102.9922 | -0.35706 | 0.091553 | -0.11902 | -0.14648 | 0.09613 | 0.10071 | 0.10071 | 3.0807 | 0.13733 | -4.6921 | 21.5149 | 13.559 | 13.0188 | 10.4782 | 9.938 | 116.4322 | -4.7104 | -4.9484 | 116.6473 | 116.6519 | 116.6519 | 0.21973 | 0.21973 | 18.4341 | 113.5803 | 0.21515 | -0.027465 | 118.4097 | 0.21057 | 121.4905 | 116.6428 | -118.2724 | -4.921 | 116.6611 | 116.4047 | 76.7441 | 116.1942
2748.0469 | 121.756 | -117.2745 | 4.1199 | 0.15419 | -0.0026425 | 0.056258 | 0.05348 | -0.0046954 | -0.0083335 | 0.0015103 | -0.0082093 | 0.011343 | 0.00080103 | 0.00032692 | -0.0165 | 0.019867 | 0.0030612 | -50.8942 | 4.0466 | -116.8396 | 3.9734 | -115.5487 | -116.9495 | -116.922 | 0.11444 | -0.16479 | 0.29755 | 0.082397 | 0.10529 | -0.032043 | -0.013733 | 0.43487 | -0.073242 | -0.14648 | 1.7258 | 0.35248 | 0.32501 | -0.082397 | -0.10986 | 117.572 | -4.2847 | -4.0375 | 117.3798 | 117.2607 | 117.2424 | -0.31128 | -0.32959 | 1.2909 | 120.813 | -0.19226 | -0.21515 | 120.8862 | -0.46234 | 121.3211 | 117.1097 | -120.9595 | -3.8223 | 121.2479 | 117.3569 | 66.3803 | 117.3889
2749.75 | 121.7377 | -117.5583 | 3.8452 | 0.13893 | -0.0028561 | 0.051985 | 0.050703 | -0.0032 | -0.0094015 | -0.0031895 | -0.0021057 | 0.011771 | 0.0010146 | 0.0011813 | -0.013723 | 0.019012 | -0.0009976 | -51.1002 | 3.7354 | -117.1234 | 3.7765 | -115.9332 | -117.2882 | -117.2791 | 0.14648 | -0.013733 | 0.23346 | 0.09613 | 0.21973 | 0.082397 | 0.068665 | 0.43488 | -0.10986 | -0.068665 | 1.6251 | 0.27924 | 0.27008 | -0.15564 | -0.16479 | 117.7917 | -3.8589 | -3.7491 | 117.778 | 117.627 | 117.6407 | -0.16479 | -0.15106 | 1.1902 | 120.9 | -0.013732 | -0.13733 | 120.8588 | -0.24719 | 121.2936 | 117.5446 | -120.9686 | -3.6118 | 121.3348 | 117.6544 | 66.4581 | 117.7048
2751.5312 | 121.6599 | -117.7139 | 3.6484 | 0.1313 | -0.0054197 | 0.052199 | 0.051985 | -0.00063661 | -0.0085471 | 0.00044213 | -0.047882 | 0.011557 | 0.00251 | 0.0028903 | -0.014364 | 0.020294 | -0.0027066 | -51.0727 | 3.5797 | -117.3523 | 3.5385 | -116.2537 | -117.572 | -117.897 | 0.068665 | 0.041199 | 0.14191 | 0.082397 | 0.10071 | -0.21057 | -0.1831 | 0.36163 | -0.068664 | -0.10986 | 1.4603 | -0.18311 | 0.14191 | -0.54474 | -0.21973 | 117.8558 | -3.6072 | -3.566 | 117.8146 | 117.5308 | 117.5034 | -0.32501 | -0.35248 | 1.0986 | 120.8908 | -0.041199 | -0.05951 | 120.932 | -0.10071 | 121.2936 | 117.7551 | -121.0007 | -3.5065 | 121.2524 | 117.7963 | 66.6412 | 117.7826
2753.2188 | 121.5912 | -117.7826 | 3.6026 | 0.11604 | -0.0041379 | 0.05348 | 0.049849 | -0.0044818 | -0.0098287 | -0.00083947 | -0.0021057 | 0.0096344 | 0.0033646 | 0.0028903 | -0.01415 | 0.019226 | -0.002493 | -51.0956 | 3.5019 | -117.865 | 3.4653 | -116.2994 | -117.5995 | -117.5674 | 0.036621 | 0.050354 | -0.022888 | 0.032043 | 0.13275 | 0.059509 | 0.10529 | -0.082397 | -0.10071 | -0.13733 | 1.4832 | 0.21515 | 0.18311 | 0.29755 | 0.2655 | 117.7597 | -3.5522 | -3.5706 | 117.9153 | 117.8879 | 117.8421 | 0.12817 | 0.082397 | 1.5656 | 121.3303 | 0.15564 | 0.054931 | 121.3669 | 0.073242 | 121.2845 | 117.8329 | -121.4676 | -3.6255 | 121.2479 | 117.8146 | 66.687 | 117.8192
2754.9844 | 121.582 | -117.7277 | 3.5751 | 0.11604 | -0.0022153 | 0.05348 | 0.052626 | -0.00020941 | -0.0079061 | -0.0038303 | -0.0051575 | 0.010489 | 0.0022964 | -0.00052768 | -0.016073 | 0.020508 | 7.04e-05 | -51.0773 | 3.4882 | -117.6727 | 3.5522 | -116.098 | -117.4347 | -117.3843 | 0.11902 | 0.027466 | -0.027466 | 0.082397 | 0.16937 | 0.073242 | 0.064087 | 0.054932 | -0.086975 | -0.022888 | 1.6296 | 0.34332 | 0.29297 | 0.28839 | 0.23804 | 117.7002 | -3.5477 | -3.4927 | 117.897 | 117.7917 | 117.8009 | 0.091553 | 0.10071 | 1.5747 | 121.225 | 0.19684 | 0.10986 | 121.1609 | 0.054932 | 121.2158 | 117.7551 | -121.2479 | -3.6026 | 121.2799 | 117.8101 | 66.6504 | 117.8467
2756.75 | 121.5729 | -117.897 | 3.4287 | -0.3875 | -0.0034971 | 0.051771 | 0.051772 | -0.0036274 | -0.010897 | -0.0038303 | 0.0009461 | 0.0094208 | 0.001442 | -0.00095488 | -0.014364 | 0.021149 | 7.04e-05 | -51.1505 | 3.3325 | -117.8741 | 3.3142 | -116.4642 | -117.7414 | -117.6773 | 0.050354 | 0.036621 | -0.064087 | 0.054932 | 0.16937 | 0.09613 | 0.1236 | 0.022888 | -0.09613 | -0.11444 | 1.4328 | 0.21973 | 0.15564 | 0.19684 | 0.13275 | 117.8329 | -3.392 | -3.3737 | 118.0664 | 118.0206 | 117.9932 | 0.18768 | 0.16022 | 1.4099 | 121.1884 | 0.23346 | 0.11902 | 121.2067 | 0.10071 | 121.2296 | 117.9337 | -121.3028 | -3.4927 | 121.2112 | 117.952 | 66.7465 | 117.9474
2758.5156 | 121.5225 | -117.9749 | 3.2318 | -0.013657 | 0.0018435 | 0.047713 | 0.04344 | -0.012599 | -0.024142 | -0.018357 | -0.04483 | 0.0025848 | -0.0085984 | -0.0080045 | -0.017782 | 0.018585 | -0.0089016 | -43.6478 | 3.186 | -117.952 | 2.7283 | -100.3876 | -106.7688 | -105.7526 | -0.23346 | 0.018311 | -0.10986 | -0.35248 | -0.091553 | 0.073242 | 0.10071 | 0.022889 | -0.045777 | -0.50354 | 17.5873 | 12.2223 | 11.2061 | 12.1994 | 11.1832 | 117.865 | -3.2135 | -3.5843 | 117.8833 | 118.0756 | 118.0481 | 0.21057 | 0.18311 | 17.5644 | 120.6802 | 0.01831 | -0.24262 | 121.138 | 0.12817 | 121.1609 | 117.9932 | -121.1838 | -3.3417 | 120.7031 | 117.6224 | 74.3271 | 117.7414
2760.2031 | 121.5683 | -118.0481 | 3.154 | -0.028916 | -7.9104e-05 | 0.054549 | 0.052199 | -0.0034136 | -0.0068381 | -0.0029759 | -0.0051575 | 0.01348 | 0.0010146 | 0.0045993 | -0.014364 | 0.023285 | 0.0034884 | -51.21 | 3.1036 | -118.1946 | 2.916 | -116.9083 | -118.103 | -118.2953 | 0.032043 | -0.07782 | 0.2655 | 0.073242 | -0.041199 | -0.24261 | -0.21515 | -0.14648 | -0.050354 | -0.23804 | 1.1398 | -0.24719 | -0.054931 | -0.10071 | 0.091553 | 118.3136 | -3.2318 | -3.0808 | 118.0069 | 117.8329 | 117.8055 | -0.48065 | -0.50812 | 1.2863 | 121.1105 | -0.3067 | -0.19226 | 121.2982 | -0.34332 | 121.1517 | 117.9703 | -121.3486 | -2.8885 | 120.9641 | 118.1213 | 66.8381 | 118.0801
2761.9531 | 121.5729 | -118.1305 | 3.1128 | 0.15419 | -0.0020017 | 0.054335 | 0.052626 | -0.00085021 | -0.010043 | -0.0051121 | -0.0021057 | 0.010062 | 0.00037383 | 0.0033175 | -0.015859 | 0.020081 | -0.0014248 | -51.4938 | 3.0029 | -118.222 | 3.0853 | -116.2811 | -117.7597 | -117.7048 | 0.12817 | 0.032043 | 0.09613 | 0.10986 | 0.1831 | 0.045776 | 0.032043 | -0.091553 | -0.10986 | -0.027466 | 1.8494 | 0.42572 | 0.37079 | 0.51727 | 0.46234 | 118.2266 | -3.0808 | -3.0029 | 118.3136 | 118.1625 | 118.1763 | -0.064087 | -0.050354 | 1.9409 | 121.3074 | 0.086975 | 0.013733 | 121.225 | -0.064087 | 121.1334 | 118.1625 | -121.3348 | -3.0167 | 121.2158 | 118.2404 | 66.6367 | 118.2587
2763.7031 | 121.4539 | -118.1946 | 3.1219 | -0.15862 | 0.027905 | 0.11095 | 0.043013 | 0.0017132 | -0.01581 | 0.051498 | -0.15775 | 0.029501 | -0.0041122 | 0.0054537 | 0.26869 | 0.038452 | 0.032968 | -51.6083 | 3.0029 | -118.0573 | 2.7603 | -94.8807 | -97.9843 | -96.5469 | 0.041199 | 0 | 0.20142 | 0.027466 | -0.15564 | 0.10529 | 0.13275 | 0.13733 | -0.11902 | -0.36163 | 23.3139 | 21.6476 | 20.2103 | 21.5103 | 20.0729 | 118.396 | -3.1219 | -3.0945 | 118.0389 | 118.3273 | 118.2999 | -0.068665 | -0.09613 | 23.1766 | 120.8176 | -0.35706 | -0.17395 | 121.0602 | -0.20142 | 121.1975 | 118.1946 | -121.1792 | -2.9205 | 120.9549 | 118.222 | 66.5863 | 118.2358
2765.4531 | 121.3989 | -118.2312 | 3.067 | -0.013657 | -0.011188 | 0.052199 | 0.053267 | -0.0070452 | -0.026278 | -0.021347 | -0.09671 | 0.0023712 | -0.0049668 | -0.0013821 | -0.018637 | 0.015381 | -0.000784 | -51.8417 | 2.9938 | -118.1946 | 2.742 | -106.4987 | -110.6003 | -107.2952 | -0.050354 | 0.10071 | 0.004578 | -0.027466 | 0.004578 | -0.37079 | -0.032043 | 0.036621 | -0.073243 | -0.32501 | 11.7325 | 10.936 | 7.6309 | 10.8994 | 7.5943 | 118.2358 | -2.9663 | -3.0945 | 118.2358 | 118.1992 | 117.8604 | -0.036621 | -0.37537 | 11.6959 | 120.9366 | 0 | -0.032044 | 121.1884 | 0.09613 | 121.225 | 118.3319 | -121.2616 | -3.0624 | 120.9732 | 118.2037 | 66.3895 | 118.1808
2767.2188 | 121.4905 | -118.2312 | 2.9984 | -0.0060272 | 0.0022709 | 0.054549 | 0.051772 | 0.00043159 | -0.0087607 | -0.0021213 | -0.0082093 | 0.010916 | 0.0016556 | 0.0069491 | -0.016073 | 0.019867 | 0.0024204 | -54.0939 | 2.8839 | -118.3228 | 2.9434 | -116.391 | -117.8329 | -117.778 | 0.1236 | 0.045776 | -0.050354 | 0.10529 | 0.1831 | 0.086975 | 0.09613 | -0.091553 | -0.11444 | -0.054932 | 1.8402 | 0.45319 | 0.39825 | 0.54474 | 0.48981 | 118.1808 | -2.9526 | -2.8931 | 118.4143 | 118.3273 | 118.3182 | 0.14648 | 0.13733 | 1.9318 | 121.2662 | 0.23346 | 0.15564 | 121.2067 | 0.09613 | 121.1151 | 118.277 | -121.3211 | -3.0487 | 121.1746 | 118.3365 | 64.1373 | 118.3548
2768.9062 | 121.4401 | -118.2541 | 2.9526 | -0.15862 | -0.0020017 | 0.052412 | 0.051985 | 0.0025678 | -0.010683 | -0.0042575 | -0.0051575 | 0.010062 | 0.001442 | 0.0026767 | -0.015646 | 0.020721 | -0.0022794 | -54.808 | 2.861 | -118.3228 | 2.9022 | -116.5466 | -117.9794 | -117.9474 | 0.10529 | 0.022888 | -0.054932 | 0.082397 | 0.15564 | 0.068665 | 0.14648 | -0.068665 | -0.091553 | -0.050354 | 1.7075 | 0.3067 | 0.27466 | 0.37537 | 0.34332 | 118.1992 | -2.9297 | -2.8702 | 118.4097 | 118.4006 | 118.3228 | 0.20142 | 0.1236 | 1.7761 | 121.225 | 0.21057 | 0.13733 | 121.1838 | 0.07782 | 121.1151 | 118.277 | -121.2753 | -3.0075 | 121.1563 | 118.3365 | 63.446 | 118.3594
2770.6719 | 121.4539 | -118.2587 | 2.916 | -0.39513 | -0.0011471 | 0.054762 | 0.052412 | 0.0053448 | -0.0083335 | -0.0031895 | -0.0051575 | 0.010489 | 0.004219 | 0.0041721 | -0.015859 | 0.023071 | -0.0022794 | -55.1468 | 2.8152 | -118.3502 | 2.8702 | -116.5192 | -117.9245 | -117.8741 | 0.13275 | 0.032043 | -0.050354 | 0.09613 | 0.1831 | 0.09613 | 0.13275 | -0.091553 | -0.10071 | -0.045777 | 1.7395 | 0.38452 | 0.33417 | 0.47607 | 0.42572 | 118.2083 | -2.8839 | -2.8198 | 118.4418 | 118.3914 | 118.3548 | 0.18311 | 0.14648 | 1.8311 | 121.2204 | 0.23346 | 0.14648 | 121.1655 | 0.082397 | 121.0739 | 118.2907 | -121.2662 | -2.9663 | 121.1288 | 118.3548 | 63.1119 | 118.3914
2772.3906 | 121.3943 | -118.309 | 2.8931 | -0.0060272 | -0.0011471 | 0.054549 | 0.051131 | 4.192e-06 | -0.010043 | -0.0057529 | -0.0021057 | 0.012198 | 0.0018692 | 0.0041721 | -0.015646 | 0.021149 | 7.04e-05 | -55.4718 | 2.7832 | -118.4006 | 2.8198 | -116.7892 | -118.1717 | -118.0939 | 0.073242 | 0.036621 | -0.045776 | 0.050354 | 0.14191 | 0.059509 | 0.11902 | -0.091553 | -0.10986 | -0.073242 | 1.5198 | 0.21515 | 0.13733 | 0.3067 | 0.22888 | 118.2632 | -2.8564 | -2.8427 | 118.4509 | 118.428 | 118.3685 | 0.16479 | 0.10528 | 1.6113 | 121.2204 | 0.18768 | 0.09613 | 121.1838 | 0.082397 | 121.0922 | 118.3456 | -121.2936 | -2.9388 | 121.1288 | 118.3594 | 62.8372 | 118.3823
2774.1562 | 121.376 | -118.3456 | 2.8427 | -0.013657 | -0.0015743 | 0.053694 | 0.05049 | -0.003841 | -0.0087607 | -0.0040439 | -0.0021057 | 0.01113 | 0.0020828 | 0.0060947 | -0.015219 | 0.022217 | -0.0029202 | -55.7098 | 2.7374 | -118.4143 | 2.7969 | -116.7847 | -118.2404 | -118.1396 | 0.082397 | 0.032043 | -0.054932 | 0.054932 | 0.1236 | 0.059509 | 0.10986 | -0.068665 | -0.10529 | -0.045776 | 1.561 | 0.20599 | 0.10529 | 0.27466 | 0.17395 | 118.2907 | -2.8107 | -2.7878 | 118.4692 | 118.4555 | 118.4052 | 0.16479 | 0.11444 | 1.6296 | 121.2112 | 0.17853 | 0.10986 | 121.1517 | 0.086975 | 121.0831 | 118.3777 | -121.257 | -2.8976 | 121.1426 | 118.4006 | 62.6358 | 118.428
2775.9219 | 121.0693 | -118.396 | 2.861 | -0.1281 | -0.0084103 | 0.051558 | 0.052412 | -0.00063661 | -0.0087607 | -0.0029759 | -0.0051575 | 0.0083526 | -0.0011216 | 0.0035311 | -0.012869 | 0.020294 | 0.0002842 | -55.9204 | 2.7008 | -118.1625 | 2.6688 | -116.6565 | -117.9245 | -118.1671 | -0.041199 | 0.082397 | -0.086975 | -0.027466 | 0.068665 | -0.022888 | -0.13275 | 0.23346 | -0.16022 | -0.19226 | 1.7395 | 0.22888 | 0.4715 | -0.004577 | 0.23804 | 118.309 | -2.7786 | -2.8885 | 118.4647 | 118.2632 | 118.3731 | -0.045776 | 0.064087 | 1.506 | 120.8313 | 0.15564 | 0.059509 | 120.8633 | 0.16937 | 121.0968 | 118.4784 | -121.0236 | -2.948 | 121.0648 | 118.3685 | 62.4756 | 118.3548
2777.6875 | 121.4035 | -118.3411 | 2.7878 | -0.50194 | -0.0022153 | 0.053908 | 0.052199 | 0.00043159 | -0.0089743 | -0.0040439 | -0.0051575 | 0.011343 | 0.00058743 | -0.0015957 | -0.016928 | 0.022217 | 0.0015658 | -56.0715 | 2.6779 | -118.428 | 2.7649 | -116.7801 | -118.2175 | -118.0893 | 0.13275 | 0.045776 | -0.059509 | 0.10071 | 0.18768 | 0.10071 | 0.13733 | -0.086976 | -0.10986 | -0.022888 | 1.561 | 0.25177 | 0.1236 | 0.33875 | 0.21057 | 118.2816 | -2.742 | -2.6871 | 118.5287 | 118.4784 | 118.4418 | 0.19684 | 0.16022 | 1.6479 | 121.1929 | 0.24719 | 0.16022 | 121.106 | 0.10528 | 121.019 | 118.3868 | -121.2158 | -2.8473 | 121.106 | 118.4418 | 62.2696 | 118.4738
2779.3906 | 121.344 | -118.3731 | 2.7969 | -0.41801 | -0.0022153 | 0.051985 | 0.049635 | -0.0019184 | -0.0094015 | -0.0031895 | -0.0051575 | 0.011557 | 0.0016556 | 0.0024631 | -0.015432 | 0.021362 | 0.0015658 | -56.2546 | 2.6688 | -118.4601 | 2.6962 | -116.8396 | -118.3136 | -118.2953 | 0.050354 | 0.041199 | -0.068665 | 0.032043 | 0.13733 | 0.041199 | 0.10071 | -0.086975 | -0.12817 | -0.10071 | 1.5335 | 0.07782 | 0.059509 | 0.16479 | 0.14648 | 118.3044 | -2.7557 | -2.7649 | 118.5104 | 118.4738 | 118.4143 | 0.16937 | 0.10986 | 1.6205 | 121.1563 | 0.20599 | 0.10071 | 121.1288 | 0.10986 | 121.0419 | 118.4143 | -121.257 | -2.8656 | 121.0693 | 118.4052 | 62.1185 | 118.4235
2781.1562 | 121.344 | -118.3823 | 2.7649 | -0.19676 | -0.0032833 | 0.05284 | 0.053694 | -0.0017048 | -0.010256 | -0.0042575 | -0.0051575 | 0.011557 | 0.0018692 | -0.0058683 | -0.015646 | 0.020935 | -0.0018522 | -56.3736 | 2.655 | -118.4738 | 2.6459 | -116.8671 | -118.3182 | -118.3594 | 0.018311 | 0.045776 | -0.059509 | 0.027466 | 0.12817 | 0.045776 | 0.091553 | -0.091553 | -0.10986 | -0.11902 | 1.5152 | 0.022888 | 0.064087 | 0.11444 | 0.15564 | 118.3228 | -2.7191 | -2.7374 | 118.5104 | 118.4738 | 118.428 | 0.15106 | 0.10528 | 1.6068 | 121.1197 | 0.18768 | 0.086975 | 121.1288 | 0.10528 | 121.0373 | 118.428 | -121.2387 | -2.8244 | 121.0281 | 118.4097 | 62.0087 | 118.4006
2782.8594 | 121.3303 | -118.3685 | 2.7695 | -0.11284 | -0.0028561 | 0.054762 | 0.05049 | -0.0027728 | -0.0091879 | -0.0012669 | 0.0009461 | 0.012839 | 0.0050736 | 0.0016085 | -0.015432 | 0.020721 | -0.0014248 | -56.4651 | 2.6413 | -118.1442 | 2.6917 | -116.7892 | -118.2587 | -118.1808 | 0.091553 | 0.050354 | -0.059509 | 0.022888 | 0.17395 | 0.068665 | 0.10529 | 0.2243 | -0.12817 | -0.07782 | 1.5793 | 0.18768 | 0.10986 | -0.036621 | -0.11444 | 118.309 | -2.7191 | -2.7466 | 118.5425 | 118.4738 | 118.4372 | 0.16479 | 0.12817 | 1.355 | 120.8359 | 0.23346 | 0.082397 | 120.7855 | 0.10986 | 121.0098 | 118.4189 | -120.9137 | -2.829 | 121.0602 | 118.3914 | 61.9034 | 118.4601
2784.625 | 121.3303 | -118.3731 | 2.7512 | -0.22728 | -0.0032833 | 0.05284 | 0.051131 | -0.0036274 | -0.0089743 | -0.0036167 | 0.0009461 | 0.010489 | 0.0010146 | 0.0078037 | -0.015859 | 0.020508 | -0.0003568 | -56.6299 | 2.6505 | -118.4601 | 2.6367 | -116.8167 | -118.2999 | -118.3228 | 0.045776 | 0.045776 | -0.073242 | 0.022888 | 0.17395 | 0.073242 | 0.11444 | -0.086975 | -0.10071 | -0.11444 | 1.5564 | 0.050354 | 0.073242 | 0.13733 | 0.16022 | 118.2999 | -2.7054 | -2.7283 | 118.5471 | 118.4875 | 118.4463 | 0.18768 | 0.14648 | 1.6434 | 121.0968 | 0.24719 | 0.09613 | 121.1105 | 0.11902 | 121.0236 | 118.4189 | -121.2112 | -2.8244 | 121.0098 | 118.396 | 61.7432 | 118.4189
2786.3906 | 121.0922 | -118.3273 | 2.8152 | -0.12047 | -0.0015743 | 0.053053 | 0.051985 | 0.0014996 | -0.0076925 | -0.0040439 | -0.0051575 | 0.011984 | 0.0016556 | 0.0054537 | -0.015005 | 0.022217 | -0.0005704 | -56.749 | 2.6871 | -117.8696 | 2.6276 | -116.7938 | -118.2953 | -118.1717 | -0.009155 | 0.086975 | -0.091553 | -0.050354 | 0.07782 | -0.018311 | 0.027466 | 0.45776 | -0.12817 | -0.18768 | 1.5335 | 0.15564 | 0.032044 | -0.30212 | -0.42572 | 118.2358 | -2.7283 | -2.8656 | 118.4052 | 118.3548 | 118.309 | 0.11902 | 0.073242 | 1.0757 | 120.4971 | 0.16937 | 0.041199 | 120.5566 | 0.17853 | 121.0144 | 118.4143 | -120.6848 | -2.9068 | 120.9549 | 118.277 | 61.5784 | 118.3182
2788.1562 | 121.4493 | -118.3548 | 2.623 | -0.0060272 | -0.0047787 | 0.053694 | 0.050276 | -0.00555 | -0.0066245 | -0.0027621 | -0.0051575 | 0.010275 | 0.0018692 | 0.010154 | -0.015005 | 0.019653 | -0.0003568 | -56.9778 | 2.3987 | -118.1259 | 2.5543 | -116.6748 | -118.1442 | -118.1305 | 0.11902 | -0.29297 | 0.21515 | 0.07782 | 0.21057 | 0.10071 | 0.10071 | 0.22888 | -0.2243 | -0.068665 | 1.68 | 0.2243 | 0.21057 | -0.004577 | -0.01831 | 118.5699 | -2.916 | -2.5452 | 118.5654 | 118.4555 | 118.4555 | -0.11444 | -0.11444 | 1.4511 | 120.6802 | -0.004578 | -0.13733 | 120.5246 | -0.50812 | 120.7535 | 118.0618 | -120.7489 | -2.4078 | 120.9091 | 118.4326 | 61.377 | 118.4738
2789.8594 | 121.2891 | -118.4738 | 2.6321 | 0.12367 | -0.0009335 | 0.050917 | 0.050703 | -0.00555 | -0.0096151 | -0.0036167 | -0.04483 | 0.01348 | 0.003151 | -0.0013821 | -0.015005 | 0.020508 | -0.004202 | -56.9366 | 2.5223 | -114.9033 | 2.4353 | -116.7938 | -118.6295 | -117.9062 | -0.059509 | -0.2243 | -0.041199 | -0.045776 | -0.21973 | -0.11902 | 0.013733 | 3.5706 | -0.10986 | -0.19684 | 1.68 | 0.56763 | -0.15564 | -3.0029 | -3.7262 | 118.4326 | -2.8564 | -2.6779 | 118.2541 | 118.4875 | 118.3548 | 0.054932 | -0.07782 | -1.8906 | 117.3386 | -0.17853 | -0.004577 | 117.4255 | -0.18311 | 120.9961 | 118.2495 | -117.5354 | -2.6733 | 120.9091 | 118.428 | 61.5372 | 118.4143
2791.625 | 121.376 | -118.4692 | 2.5543 | 0.10841 | 0.0014163 | 0.054549 | 0.051772 | 0.00085879 | -0.0089743 | 0.00065573 | -0.0021057 | 0.011343 | 0.0027236 | 0.0018221 | -0.016928 | 0.020935 | -0.0012112 | -57.1152 | 2.4673 | -118.1442 | 2.5452 | -116.6153 | -118.1076 | -118.0344 | 0.11902 | 0.009155 | 0.16022 | 0.10071 | 0.17395 | 0.064087 | 0.032043 | 0.32501 | -0.086975 | -0.009155 | 1.8539 | 0.43488 | 0.36163 | 0.10986 | 0.036621 | 118.6295 | -2.5452 | -2.4536 | 118.6432 | 118.5013 | 118.5333 | -0.12817 | -0.09613 | 1.5289 | 120.6894 | 0.013733 | -0.059509 | 120.6116 | -0.15106 | 120.9366 | 118.4784 | -120.6985 | -2.3941 | 121.0144 | 118.5699 | 61.3541 | 118.5883
2793.3125 | 121.3623 | -118.5013 | 2.5452 | -0.18913 | -0.0041379 | 0.053267 | 0.051985 | -0.0019184 | -0.0076925 | -0.0061801 | -0.0021057 | 0.012198 | 0.0020828 | -0.0030911 | -0.014578 | 0.020721 | -0.000784 | -57.2571 | 2.4719 | -118.3044 | 2.5177 | -116.835 | -118.2266 | -118.1717 | 0.14648 | 0.022888 | 0.054932 | 0.10529 | 0.21515 | 0.13733 | 0.11444 | 0.19684 | -0.073242 | -0.027466 | 1.6663 | 0.32959 | 0.27466 | 0.13275 | 0.077819 | 118.5562 | -2.5223 | -2.4399 | 118.7164 | 118.6157 | 118.6386 | 0.059509 | 0.082397 | 1.4694 | 120.8221 | 0.16022 | 0.050354 | 120.7764 | -0.032044 | 120.9732 | 118.5242 | -120.8496 | -2.4902 | 121.019 | 118.6066 | 61.2442 | 118.6478
2795.0781 | 121.3028 | -118.5379 | 2.5543 | 0.10841 | -0.0013607 | 0.055403 | 0.049849 | 0.00064519 | -0.0051291 | -0.0046847 | -0.0051575 | 0.0087798 | 0.0027236 | 0.0048129 | -0.014791 | 0.019653 | -0.0003568 | -57.431 | 2.4353 | -118.3182 | 2.4994 | -116.7618 | -118.1854 | -118.1168 | 0.1236 | 0.027466 | -0.018311 | 0.09613 | 0.16937 | 0.07782 | 0.082397 | 0.21973 | -0.11902 | -0.054931 | 1.7761 | 0.42114 | 0.35248 | 0.20142 | 0.13275 | 118.5196 | -2.5269 | -2.4582 | 118.7073 | 118.6203 | 118.6157 | 0.10071 | 0.096131 | 1.5564 | 120.8176 | 0.18768 | 0.11444 | 120.7535 | 0.045777 | 120.9732 | 118.5654 | -120.8725 | -2.5726 | 121.0373 | 118.634 | 61.1069 | 118.6615
2796.7812 | 121.2158 | -118.5745 | 2.5635 | -0.074692 | 0.027265 | 0.10966 | 0.053694 | 0.046147 | 0.056608 | 0.050216 | -0.1669 | 0.029288 | -0.0079574 | 0.0054537 | 0.2674 | 0.037598 | -0.011038 | -57.7103 | 2.449 | -118.1442 | 2.4445 | -117.0456 | -107.2083 | -97.2336 | -0.013733 | 0.068665 | 0.091553 | 0.022888 | 0.082397 | -0.3479 | 0.10529 | 0.4303 | -0.11444 | -0.11902 | 1.5289 | 21.3409 | 11.3663 | 20.9106 | 10.936 | 118.6661 | -2.4948 | -2.5406 | 118.6569 | 118.6798 | 118.2266 | 0.013733 | -0.43945 | 1.0986 | 120.5887 | -0.009156 | -0.068665 | 120.5933 | -0.022888 | 121.0236 | 118.6432 | -120.7077 | -2.4719 | 121.019 | 118.5974 | 60.8643 | 118.5608
2798.5469 | 120.6757 | -1.0025 | 119.6411 | -0.013657 | 0.0033389 | 0.057753 | 0.054549 | 0.04636 | -0.016665 | 0.050644 | -0.0051575 | 0.0083526 | -0.011375 | 0.0056675 | 0.26762 | 0.038239 | 0.0319 | 14.2593 | 119.545 | -1.0986 | 118.9041 | -0.45319 | -0.93384 | -0.86975 | -0.27008 | -0.37994 | -0.050354 | 0.10986 | 0.10071 | 0.10071 | 0.10071 | -0.096131 | -0.09613 | -0.737 | 0.54932 | 0.13275 | 0.068664 | 0.22888 | 0.1648 | 0.95215 | -120.0211 | -119.5312 | 1.1032 | 1.1032 | 1.1032 | 0.15106 | 0.15106 | 0.64545 | 120.0027 | 0.15106 | 0.16022 | 120.6436 | -0.32959 | 120.5475 | 0.62256 | -120.7397 | -119.6915 | 119.9066 | 1.1124 | 15.2618 | 0.73242
2800.25 | 121.0327 | -1.0117 | 119.7418 | -0.0060272 | -0.0007199 | 0.053267 | 0.051558 | -0.0044818 | -0.010043 | -0.0031895 | -0.0082093 | 0.009848 | -0.00069437 | -0.0050137 | -0.015646 | 0.020935 | 0.0017794 | 14.2319 | 119.7189 | -1.0529 | 119.7235 | -0.37079 | -0.84228 | -0.78735 | 0.1236 | 0.022888 | 0.13275 | 0.10071 | 0.21515 | 0.082397 | 0.091553 | -0.041198 | -0.022888 | -0.01831 | 0.64087 | 0.2243 | 0.16937 | 0.2655 | 0.21057 | 1.1444 | -119.7189 | -119.6411 | 1.2268 | 1.1032 | 1.0941 | -0.041198 | -0.050354 | 0.68207 | 120.7764 | 0.082398 | -0.032043 | 120.7718 | -0.10986 | 120.7306 | 1.0345 | -120.7947 | -119.6091 | 120.7352 | 1.1124 | 15.2435 | 1.1353
2802 | 121.0693 | -0.93384 | 119.9707 | -0.0060272 | -0.0032833 | 0.05049 | 0.052412 | 0.0032086 | -0.0094015 | -0.0019077 | -0.0051575 | 0.011557 | -5.3368e-05 | 0.010154 | -0.016287 | 0.022217 | 0.0011386 | 14.2731 | 119.8425 | -0.98419 | 119.9432 | -0.28839 | -0.77362 | -0.71869 | 0.091553 | 0.045776 | -0.009155 | 0.041199 | 0.13275 | -0.09613 | -0.13275 | -0.050354 | -0.12817 | -0.027466 | 0.64545 | 0.21515 | 0.16022 | 0.2655 | 0.21057 | 0.92468 | -119.9249 | -119.9295 | 1.0666 | 0.80109 | 0.83771 | -0.1236 | -0.086975 | 0.6958 | 120.9274 | 0.14191 | 0.050354 | 120.8267 | 0.054931 | 120.7764 | 0.97961 | -120.9549 | -119.9799 | 120.8771 | 0.97504 | 15.2069 | 1.0254
2803.75 | 121.051 | -0.95673 | 120.0668 | -0.013657 | -0.0011471 | 0.05049 | 0.05284 | 0.00043159 | -0.0089743 | -0.0038303 | -0.0021057 | 0.011557 | 0.00037383 | 0.0011813 | -0.012869 | 0.021149 | -0.0020658 | 14.1815 | 119.9341 | -1.0345 | 119.9249 | -0.35706 | -0.8194 | -0.79193 | -0.009155 | 0.059509 | -0.073242 | -0.027466 | 0.054932 | -0.21973 | -0.30212 | -0.07782 | -0.13275 | -0.14191 | 0.59967 | 0.16479 | 0.13733 | 0.24261 | 0.21515 | 0.88348 | -120.0073 | -120.0943 | 1.0117 | 0.6546 | 0.737 | -0.22888 | -0.14649 | 0.67749 | 120.9595 | 0.12817 | 0.045776 | 120.9686 | 0.13275 | 120.8908 | 1.0162 | -121.1014 | -120.1401 | 120.8817 | 0.92926 | 15.1382 | 0.94757
2805.4531 | 121.1288 | -1.1581 | 119.9432 | -0.0060272 | 0.0016299 | 0.047926 | 0.051772 | -0.00063661 | -0.0089743 | -0.0040439 | -0.0051575 | 0.01348 | 0.0046462 | 0.011222 | -0.014791 | 0.016022 | -0.002493 | 14.0762 | 119.9753 | -1.0986 | 119.8929 | -0.52643 | -0.9613 | -0.87891 | -0.050354 | 0.068665 | -0.091553 | -0.027466 | 0.009155 | -0.37994 | 0.10529 | 0.059509 | 0.032044 | -0.050354 | 0.63171 | 0.27924 | 0.19684 | 0.21973 | 0.13733 | 1.0666 | -119.8746 | -119.9707 | 1.1673 | 1.2634 | 0.7782 | 0.19684 | -0.28839 | 0.5722 | 120.9915 | 0.10071 | 0.064087 | 121.0739 | 0.16022 | 121.1334 | 1.2268 | -121.0419 | -120.0348 | 121.051 | 1.1307 | 15.2344 | 1.1078
2807.2031 | 121.1197 | -0.96588 | 120.1904 | -0.021286 | 0.0026981 | 0.04814 | 0.05348 | 0.0019268 | -0.0083335 | -0.0021213 | -0.0051575 | 0.013693 | 0.0027236 | 0.0056675 | -0.01116 | 0.020935 | -0.0027066 | 14.09 | 120.1172 | -1.0208 | 119.9478 | -0.45776 | -0.92926 | -0.87433 | -0.054932 | 0.073242 | -0.059509 | -0.027466 | 0.027466 | -0.2655 | -0.27008 | -0.054932 | -0.073243 | -0.24262 | 0.50812 | 0.091552 | 0.036621 | 0.14648 | 0.091553 | 0.90637 | -120.1172 | -120.2179 | 0.99335 | 0.6958 | 0.70038 | -0.21057 | -0.20599 | 0.56305 | 120.9686 | 0.086975 | 0.032043 | 121.138 | 0.13275 | 121.0831 | 1.0391 | -121.2112 | -120.2499 | 120.9137 | 0.93841 | 15.0558 | 0.91095
2808.9062 | 121.2479 | -0.93842 | 120.2133 | -0.0060272 | 0.0007755 | 0.05284 | 0.051558 | 0.004704 | -0.0081197 | -0.0044711 | -0.0082093 | 0.012411 | 0.00058743 | 0.0045993 | -0.014364 | 0.020935 | -0.000784 | 14.1174 | 120.0668 | -0.99335 | 120.0897 | -0.32959 | -0.83313 | -0.75989 | 0.041199 | 0.027466 | -0.059509 | 0.032043 | 0.12817 | 0.050354 | 0.073242 | -0.054931 | -0.14648 | -0.1236 | 0.60883 | 0.17853 | 0.10529 | 0.23346 | 0.16022 | 0.87891 | -120.1859 | -120.1813 | 1.0666 | 1.0117 | 0.98877 | 0.13275 | 0.10986 | 0.66376 | 121.0831 | 0.18768 | 0.091552 | 121.0602 | 0.086975 | 121.0052 | 0.96588 | -121.2067 | -120.2728 | 121.0281 | 0.97046 | 15.0558 | 0.97962
2810.6562 | 121.2479 | -0.95673 | 120.282 | -0.013657 | 0.0035525 | 0.051131 | 0.053694 | 4.192e-06 | -0.0091879 | -0.00083947 | -0.0051575 | 0.011771 | 0.0027236 | 0.0013949 | -0.017355 | 0.022858 | -0.003561 | 14.0717 | 120.1813 | -1.0071 | 120.0989 | -0.37079 | -0.89264 | -0.81482 | 0.045776 | 0.045776 | -0.073242 | 0.068665 | 0.16479 | 0.050354 | 0.004578 | -0.050354 | -0.10071 | -0.1831 | 0.58594 | 0.14191 | 0.064087 | 0.19226 | 0.11444 | 0.88348 | -120.2362 | -120.2133 | 1.1215 | 0.9613 | 1.0071 | 0.07782 | 0.1236 | 0.63629 | 121.106 | 0.23804 | 0.14191 | 121.1884 | 0.11902 | 121.138 | 1.0025 | -121.2891 | -120.3552 | 121.0556 | 1.0254 | 15.0284 | 1.0025
2812.4219 | 121.3806 | -0.91095 | 120.3232 | -0.0060272 | -0.0013607 | 0.050276 | 0.050276 | -0.00020941 | -0.01047 | -0.0012669 | -0.0082093 | 0.01113 | 0.0010146 | 0.0067355 | -0.01415 | 0.021576 | -0.0005704 | 14.1449 | 120.1538 | -0.99335 | 120.2316 | -0.21973 | -0.75073 | -0.68665 | 0.15564 | 0.027466 | -0.050354 | 0.10071 | 0.22888 | 0.13733 | 0.16022 | -0.082397 | -0.16937 | -0.091553 | 0.69122 | 0.2243 | 0.16022 | 0.3067 | 0.24262 | 0.8606 | -120.2957 | -120.2225 | 1.1398 | 1.0712 | 1.0483 | 0.21057 | 0.18768 | 0.77362 | 121.225 | 0.27924 | 0.15106 | 121.1472 | 0.07782 | 121.0648 | 0.93842 | -121.3165 | -120.3735 | 121.1426 | 1.0117 | 15.0558 | 1.0666
2814.1875 | 121.1884 | -0.93384 | 120.369 | -0.021286 | 0.0026981 | 0.051985 | 0.053694 | 0.00043159 | -0.010043 | -0.0051121 | -0.0051575 | 0.011343 | 0.0029372 | 0.0054537 | -0.014791 | 0.021576 | -0.0016384 | 14.0808 | 120.2133 | -1.0254 | 120.1721 | -0.35706 | -0.87891 | -0.80566 | 0.064087 | 0.059509 | -0.059509 | 0.064087 | 0.15564 | 0.041199 | 0.09613 | -0.091553 | -0.15564 | -0.19684 | 0.57678 | 0.12817 | 0.054932 | 0.21973 | 0.14648 | 0.87433 | -120.3094 | -120.3049 | 1.0895 | 1.03 | 0.97504 | 0.15564 | 0.10071 | 0.66833 | 121.1975 | 0.21515 | 0.1236 | 121.2387 | 0.11902 | 121.1472 | 0.99335 | -121.3943 | -120.4285 | 121.106 | 0.99792 | 15.0146 | 0.99792
2815.9375 | 120.5566 | -0.95673 | 120.401 | -0.0060272 | -0.0024289 | 0.044081 | 0.053694 | -0.019222 | -0.022433 | -0.020706 | -0.0021057 | 0.0057892 | -0.007103 | -0.0030911 | -0.020986 | 0.037384 | -0.017233 | 14.1678 | 120.2682 | -1.0071 | 120.1813 | -0.36163 | -0.87433 | -0.83313 | 0.022888 | 0.073242 | -0.073242 | -0.004578 | 0.07782 | -0.09613 | -0.26093 | -0.050354 | -0.13275 | -0.21973 | 0.59509 | 0.1236 | 0.082397 | 0.17395 | 0.13275 | 0.88348 | -120.3278 | -120.4056 | 1.0345 | 0.6958 | 0.8606 | -0.18768 | -0.022888 | 0.64545 | 121.1884 | 0.15106 | 0.068664 | 121.2753 | 0.14648 | 121.225 | 1.03 | -121.4081 | -120.4742 | 121.138 | 0.95215 | 15.1245 | 0.97961
2817.6562 | 121.3989 | -0.92926 | 120.3827 | -0.0060272 | 0.0012027 | 0.052412 | 0.051131 | -0.001491 | -0.0089743 | -0.0034031 | -0.0021057 | 0.010702 | 0.00058743 | 0.0050265 | -0.014364 | 0.020508 | -0.0005704 | 14.1541 | 120.2545 | -0.97504 | 120.2774 | -0.25177 | -0.81482 | -0.71869 | 0.091553 | 0.059509 | -0.064087 | 0.041199 | 0.15106 | 0.045776 | 0.10986 | -0.045777 | -0.12817 | -0.10528 | 0.67749 | 0.21057 | 0.11444 | 0.25635 | 0.16022 | 0.86517 | -120.3232 | -120.3415 | 1.0803 | 1.0391 | 0.97504 | 0.17395 | 0.10986 | 0.72327 | 121.2524 | 0.21515 | 0.10529 | 121.2296 | 0.1236 | 121.1838 | 0.98877 | -121.3577 | -120.4468 | 121.2067 | 0.97046 | 15.0833 | 1.0208
2819.3594 | 121.463 | -0.90637 | 120.4422 | -0.0060272 | -0.0015743 | 0.051985 | 0.052199 | 0.0014996 | -0.011538 | -0.0059665 | -0.0051575 | 0.011557 | 0.0012282 | 0.0056675 | -0.017355 | 0.020294 | -0.0016384 | 14.2044 | 120.2591 | -0.97961 | 120.3323 | -0.19684 | -0.70953 | -0.66834 | 0.14191 | 0.045776 | -0.059509 | 0.068665 | 0.21057 | 0.13275 | 0.14191 | -0.073242 | -0.18311 | -0.10986 | 0.70953 | 0.23804 | 0.19684 | 0.31128 | 0.27008 | 0.84686 | -120.3964 | -120.3735 | 1.1169 | 1.0483 | 1.0391 | 0.20142 | 0.19226 | 0.78278 | 121.3119 | 0.27008 | 0.12817 | 121.2387 | 0.10528 | 121.1655 | 0.95215 | -121.4218 | -120.5017 | 121.2387 | 0.97504 | 15.1108 | 1.0483
2821.1094 | 121.431 | -0.93842 | 120.4468 | -0.013657 | 0.0018435 | 0.054121 | 0.049635 | 0.00085879 | -0.0089743 | -0.0038303 | 0.0009461 | 0.009848 | 0.0018692 | -0.0015957 | -0.017782 | 0.020294 | -0.0016384 | 14.1586 | 120.3094 | -0.97961 | 120.2911 | -0.31586 | -0.83771 | -0.73242 | 0.027466 | 0.041199 | -0.073242 | 0.022888 | 0.14191 | 0.036621 | 0.091553 | -0.041198 | -0.13733 | -0.15564 | 0.62256 | 0.20599 | 0.10071 | 0.24719 | 0.14191 | 0.86517 | -120.4056 | -120.4239 | 1.0803 | 1.03 | 0.97504 | 0.16479 | 0.10986 | 0.66376 | 121.2708 | 0.21515 | 0.09613 | 121.2891 | 0.11444 | 121.2479 | 0.97962 | -121.4264 | -120.52 | 121.2296 | 0.9613 | 15.097 | 0.96588
2822.875 | 120.8221 | -0.97961 | 120.5292 | -0.013657 | 0.0012027 | 0.051771 | 0.053694 | 4.192e-06 | -0.0089743 | -0.0036167 | -0.0051575 | 0.012625 | 0.0016556 | 0.0011813 | -0.017141 | 0.022644 | -0.0003568 | 14.1403 | 120.369 | -1.0208 | 120.2591 | -0.37079 | -0.89264 | -0.81482 | -0.032043 | 0.07782 | -0.10529 | -0.032043 | 0.082397 | -0.018311 | 0.018311 | -0.041199 | -0.16022 | -0.27008 | 0.60882 | 0.1648 | 0.086975 | 0.20599 | 0.12817 | 0.87433 | -120.4514 | -120.5612 | 1.062 | 0.99792 | 0.9613 | 0.1236 | 0.086975 | 0.65002 | 121.2799 | 0.18768 | 0.073243 | 121.3898 | 0.18311 | 121.3486 | 1.0574 | -121.55 | -120.6345 | 121.2387 | 0.94757 | 15.1199 | 0.94757
2824.6406 | 121.3669 | -0.9201 | 120.5063 | -0.0060272 | 0.0044071 | 0.053053 | 0.052199 | -0.00020941 | -0.0057699 | -0.0023349 | -0.0021057 | 0.012625 | 0.003151 | 0.0018221 | -0.015646 | 0.022858 | -0.0029202 | 14.1724 | 120.4102 | -1.0025 | 120.3415 | -0.29755 | -0.83771 | -0.76904 | 0.086975 | 0.050354 | -0.07782 | 0.082397 | 0.17395 | 0.068665 | 0.14191 | -0.082397 | -0.096131 | -0.16479 | 0.62256 | 0.15106 | 0.082397 | 0.23346 | 0.16479 | 0.84228 | -120.4559 | -120.4239 | 1.0941 | 1.062 | 0.98877 | 0.21973 | 0.14649 | 0.70496 | 121.344 | 0.25177 | 0.16022 | 121.4127 | 0.12817 | 121.3303 | 0.97046 | -121.5088 | -120.5841 | 121.2616 | 1.0025 | 15.0925 | 1.0071
2826.3438 | 121.5637 | -0.9201 | 120.4834 | -0.0060272 | -0.0022153 | 0.049849 | 0.051131 | -0.0023456 | -0.010043 | -0.0027621 | -0.0051575 | 0.010275 | 0.0018692 | 0.0013949 | -0.015646 | 0.021576 | -0.0018522 | 14.2227 | 120.3735 | -0.97504 | 120.4102 | -0.20142 | -0.75989 | -0.67291 | 0.13275 | 0.036621 | -0.036621 | 0.064087 | 0.23804 | 0.14648 | 0.14191 | -0.054932 | -0.10986 | -0.073242 | 0.71869 | 0.24719 | 0.16022 | 0.30212 | 0.21515 | 0.88348 | -120.4468 | -120.4193 | 1.1581 | 1.062 | 1.0666 | 0.17853 | 0.18311 | 0.77362 | 121.3852 | 0.27466 | 0.10071 | 121.3486 | 0.073242 | 121.2936 | 0.95673 | -121.4584 | -120.52 | 121.3303 | 0.98419 | 15.1428 | 1.0529
2828.1094 | 121.2799 | -0.93384 | 120.2225 | -0.0060272 | 0.0007755 | 0.050703 | 0.049849 | -0.002132 | -0.0098287 | -0.0036167 | -0.0021057 | 0.012198 | 0.00058743 | 0.0048129 | -0.016073 | 0.022217 | 0.0011386 | 14.3372 | 120.1355 | -0.98419 | 120.4193 | -0.18768 | -0.75073 | -0.70496 | 0.064087 | 0.041199 | -0.068665 | 0.013733 | 0.15564 | 0.054932 | 0.086975 | -0.050354 | -0.086975 | 0.19684 | 0.74615 | 0.22888 | 0.18311 | 0.27924 | 0.23346 | 0.86517 | -120.1813 | -120.2087 | 1.0895 | 1.0208 | 0.98877 | 0.15564 | 0.1236 | 0.79651 | 121.4035 | 0.22431 | 0.082398 | 121.1197 | 0.10986 | 121.0693 | 0.97504 | -121.2067 | -120.2911 | 121.3531 | 0.94757 | 15.271 | 0.99792
2829.8125 | 120.6757 | -0.9613 | 119.7968 | -0.013657 | 0.0003483 | 0.052199 | 0.054549 | 0.0010724 | -0.0083335 | -0.0046847 | -0.0021057 | 0.012411 | 0.003151 | -0.0026639 | -0.013723 | 0.021362 | 0.0019932 | 14.3005 | 120.0897 | -1.0254 | 120.3323 | -0.30212 | -0.8606 | -0.83313 | -0.041199 | 0.086975 | -0.068665 | -0.027466 | 0.082397 | -0.004578 | 0.064087 | -0.064087 | 0.29297 | 0.53558 | 0.65918 | 0.12817 | 0.10071 | 0.19226 | 0.16479 | 0.89264 | -119.7098 | -119.8242 | 1.0437 | 1.0254 | 0.95673 | 0.13275 | 0.064087 | 0.72327 | 121.3577 | 0.15106 | 0.041199 | 121.1151 | 0.15564 | 121.051 | 1.0483 | -120.8221 | -119.8654 | 121.2936 | 0.93384 | 15.2618 | 0.92011
2831.5781 | 121.5408 | -0.9201 | 120.5154 | -0.013657 | -0.0069149 | 0.04579 | 0.052626 | -0.0032 | -0.027346 | -0.020493 | -0.0021057 | 0.011984 | -0.0045396 | 0.00054052 | -0.017996 | 0.0053406 | -0.008688 | 14.3417 | 120.4788 | -1.0025 | 120.4102 | -0.2243 | -0.82855 | -0.7782 | 0.036621 | 0.07782 | -0.064087 | 0 | 0.1236 | 0.009155 | 0.07782 | -0.082397 | -0.036621 | -0.10529 | 0.6958 | 0.14191 | 0.091553 | 0.2243 | 0.17395 | 0.85602 | -120.4376 | -120.5154 | 1.0437 | 0.99792 | 0.92926 | 0.14191 | 0.073242 | 0.7782 | 121.4127 | 0.18768 | 0.064087 | 121.4813 | 0.14191 | 121.3989 | 0.99792 | -121.5179 | -120.5795 | 121.3303 | 0.9201 | 15.2618 | 0.95673
2833.2812 | 121.1975 | -0.94299 | 120.575 | -0.0060272 | 0.0016299 | 0.051985 | 0.052412 | 0.002995 | -0.010043 | -0.0016941 | 0.0009461 | 0.009848 | 0.0010146 | -0.0015957 | -0.014578 | 0.020294 | 0.002634 | 14.3967 | 120.2408 | -0.98877 | 120.433 | -0.1831 | -0.7782 | -0.71411 | 0.032043 | 0.054932 | -0.07782 | -0.022888 | 0.11444 | 0.018311 | 0.045776 | -0.045777 | -0.33417 | -0.14191 | 0.75989 | 0.22888 | 0.1648 | 0.27466 | 0.21057 | 0.86517 | -120.52 | -120.5978 | 1.0574 | 0.98877 | 0.9613 | 0.1236 | 0.096131 | 0.80567 | 121.4218 | 0.19226 | 0.054932 | 121.2296 | 0.13275 | 121.1838 | 0.99792 | -121.5637 | -120.6528 | 121.376 | 0.9201 | 15.3397 | 0.97504
2835.0469 | 120.8588 | -0.96588 | 120.5933 | -0.013657 | 0.0024845 | 0.051985 | 0.053053 | -0.0032 | -0.0079061 | -0.0027621 | -0.0021057 | 0.013052 | 0.0044326 | 0.0041721 | -0.014364 | 0.021362 | 0.0022068 | 14.3692 | 120.433 | -1.0208 | 120.3644 | -0.27924 | -0.87891 | -0.82855 | -0.045776 | 0.073242 | -0.086975 | -0.032043 | 0.07782 | -0.018311 | 0.041199 | -0.054932 | -0.16022 | -0.22888 | 0.68664 | 0.13733 | 0.086975 | 0.19226 | 0.14191 | 0.87891 | -120.52 | -120.6253 | 1.0437 | 1.0071 | 0.94757 | 0.12817 | 0.068664 | 0.74158 | 121.3852 | 0.16479 | 0.054932 | 121.4539 | 0.16022 | 121.3989 | 1.0391 | -121.6141 | -120.6802 | 121.3303 | 0.93384 | 15.3351 | 0.9201
2836.8125 | 120.8176 | -0.92468 | 119.9707 | -0.013657 | -0.0020017 | 0.038313 | 0.053267 | -0.007259 | -0.020937 | -0.013016 | -0.0051575 | 0.013907 | -0.0032578 | 0.0063083 | -0.013937 | 0.013672 | -0.0012112 | 14.4608 | 120.5063 | -1.0071 | 120.4239 | -0.19226 | -0.82855 | -0.77362 | 0.041199 | 0.07782 | -0.064087 | 0.004578 | 0.1236 | 0.022888 | 0.082397 | -0.082397 | 0.53558 | 0.45319 | 0.73242 | 0.15106 | 0.096131 | 0.23346 | 0.17853 | 0.8606 | -119.8929 | -119.9661 | 1.0483 | 1.0071 | 0.94757 | 0.14648 | 0.086975 | 0.81482 | 121.431 | 0.18768 | 0.068665 | 121.5134 | 0.14191 | 121.431 | 1.0025 | -120.9778 | -120.0348 | 121.3486 | 0.92926 | 15.3854 | 0.96588
2838.5156 | 121.1975 | -0.95215 | 120.6253 | 0.0016023 | 0.0033389 | 0.047713 | 0.055403 | 0.0025678 | -0.01346 | -0.0034031 | -0.0021057 | 0.013907 | 0.0052872 | 0.0048129 | -0.015219 | 0.020935 | -0.0046292 | 14.4241 | 120.5795 | -1.0254 | 120.3827 | -0.27466 | -0.90179 | -0.83771 | -0.004578 | 0.068665 | -0.082397 | -0.018311 | 0.059509 | -0.022888 | 0.054932 | -0.073243 | -0.045776 | -0.24262 | 0.67749 | 0.11444 | 0.050354 | 0.18768 | 0.1236 | 0.86975 | -120.5566 | -120.6436 | 1.0117 | 1.0071 | 0.92926 | 0.13733 | 0.059509 | 0.75073 | 121.4081 | 0.14191 | 0.064086 | 121.6049 | 0.15106 | 121.5317 | 1.0208 | -121.6507 | -120.7077 | 121.3348 | 0.93384 | 15.3763 | 0.94757
2840.2188 | 120.9091 | -0.97046 | 120.6711 | -0.0060272 | -0.0015743 | 0.049208 | 0.053908 | -0.0089678 | -0.013033 | -0.010666 | -0.0021057 | 0.010916 | -0.0015488 | 0.0092989 | -0.016287 | 0.018585 | -0.0031338 | 14.4608 | 120.2545 | -1.0162 | 120.2545 | -0.20142 | -0.84686 | -0.78735 | 0.022888 | 0.054932 | -0.086975 | 0.013733 | 0.12817 | 0.013733 | 0.091553 | -0.045776 | -0.41656 | -0.41656 | 0.76904 | 0.1831 | 0.1236 | 0.22888 | 0.16937 | 0.88348 | -120.6162 | -120.6573 | 1.0986 | 1.062 | 0.98419 | 0.17853 | 0.10071 | 0.81482 | 121.2708 | 0.21515 | 0.10071 | 121.2708 | 0.14191 | 121.225 | 1.0254 | -121.6873 | -120.7581 | 121.225 | 0.98419 | 15.4312 | 0.99335
2841.9844 | 121.3165 | -0.9613 | 120.5978 | -0.0060272 | 0.0005619 | 0.045149 | 0.053694 | -0.00063661 | -0.012606 | -0.0051121 | -0.0021057 | 0.015402 | 0.0052872 | 0.0050265 | -0.015859 | 0.020081 | 0.0011386 | 14.4196 | 120.575 | -1.03 | 120.3323 | -0.27008 | -0.90179 | -0.85144 | -0.036621 | 0.091553 | -0.073242 | -0.027466 | 0.059509 | -0.041199 | 0.059509 | -0.068664 | -0.022888 | -0.2655 | 0.69122 | 0.10986 | 0.05951 | 0.17853 | 0.12817 | 0.88806 | -120.5063 | -120.6253 | 1.0208 | 1.0208 | 0.92011 | 0.13275 | 0.032043 | 0.75989 | 121.3623 | 0.13275 | 0.045776 | 121.6049 | 0.16479 | 121.5363 | 1.0529 | -121.6278 | -120.6711 | 121.2936 | 0.93384 | 15.3809 | 0.92468
2843.7344 | 121.0236 | -0.95673 | 120.3323 | -0.013657 | 0.0012027 | 0.051131 | 0.054121 | -0.00085021 | -0.0072653 | -0.0081027 | -0.0051575 | 0.013052 | 0.00037383 | 0.0013949 | -0.015646 | 0.022644 | -0.0014248 | 14.4882 | 120.2316 | -1.0162 | 120.1355 | -0.18768 | -0.82855 | -0.78278 | 0.013733 | 0.064087 | -0.073242 | -0.009155 | 0.1236 | 0.013733 | 0.082397 | -0.059509 | -0.10071 | -0.19684 | 0.76904 | 0.17395 | 0.12817 | 0.23346 | 0.18768 | 0.88348 | -120.2682 | -120.3415 | 1.0803 | 1.0391 | 0.97046 | 0.15564 | 0.086975 | 0.82855 | 121.1517 | 0.19684 | 0.064087 | 121.2479 | 0.13733 | 121.1884 | 1.0208 | -121.3486 | -120.4056 | 121.0922 | 0.94757 | 15.4449 | 0.97046
2845.4375 | 121.2662 | -0.97961 | 120.4926 | -0.0060272 | 0.0014163 | 0.041304 | 0.054976 | 0.00021799 | -0.013033 | -0.0046847 | -0.0021057 | 0.013907 | 0.0029372 | 0.0045993 | -0.015859 | 0.022644 | 0.0019932 | 14.415 | 120.6024 | -1.0345 | 120.1172 | -0.24719 | -0.9201 | -0.83771 | -0.050354 | 0.073242 | -0.09613 | -0.036621 | 0.036621 | -0.059509 | 0.050354 | -0.054932 | 0.10986 | -0.37537 | 0.73242 | 0.14191 | 0.059509 | 0.19684 | 0.11444 | 0.88348 | -120.4193 | -120.5292 | 1.0162 | 1.03 | 0.9201 | 0.14648 | 0.036621 | 0.78735 | 121.1517 | 0.13275 | 0.059509 | 121.637 | 0.16937 | 121.582 | 1.0529 | -121.5271 | -120.5887 | 121.0968 | 0.94299 | 15.3946 | 0.92926
2847.2031 | 121.7102 | -0.93842 | 120.6528 | -0.013657 | 0.0001345 | 0.051985 | 0.05049 | -0.0010638 | -0.01047 | -0.0019077 | -0.0051575 | 0.011343 | 0.00037383 | -0.0018093 | -0.015005 | 0.021576 | 0.0039158 | 14.4287 | 120.5566 | -0.99335 | 120.5017 | -0.12817 | -0.80109 | -0.72784 | 0.018311 | 0.050354 | -0.054932 | 0.032043 | 0.16022 | 0.07782 | 0.11902 | -0.054931 | -0.09613 | -0.15106 | 0.81024 | 0.21057 | 0.13733 | 0.2655 | 0.19226 | 0.88348 | -120.6024 | -120.6207 | 1.0986 | 1.0574 | 1.0162 | 0.17395 | 0.13275 | 0.86517 | 121.4951 | 0.21515 | 0.086975 | 121.55 | 0.10529 | 121.4951 | 0.98877 | -121.6461 | -120.7077 | 121.4401 | 0.97046 | 15.3671 | 0.95673
2848.9062 | 121.019 | -0.9613 | 120.0577 | 0.0016023 | 0.0020571 | 0.052626 | 0.054549 | 0.001286 | -0.010043 | -0.0089573 | -0.0021057 | 0.013693 | 0.0027236 | -0.0028775 | -0.015005 | 0.017944 | -0.0003568 | 14.447 | 120.2682 | -1.0208 | 120.2866 | -0.14648 | -0.83313 | -0.7782 | 0.036621 | 0.068665 | -0.068665 | 0.013733 | 0.1236 | 0.018311 | 0.086975 | -0.059509 | 0.21057 | 0.22888 | 0.81482 | 0.18311 | 0.12817 | 0.24262 | 0.18768 | 0.89264 | -119.989 | -120.0439 | 1.0849 | 1.0483 | 0.97962 | 0.15564 | 0.086976 | 0.87433 | 121.3074 | 0.19226 | 0.082398 | 121.2891 | 0.13733 | 121.2296 | 1.03 | -121.0785 | -120.1263 | 121.2479 | 0.97504 | 15.4083 | 0.99793
2850.6562 | 121.17 | -0.98877 | 120.2225 | -0.0060272 | 0.0009891 | 0.040877 | 0.053267 | 0.0021406 | -0.017092 | -0.010666 | 0.0009461 | 0.012411 | 0.0050736 | 0.0016085 | -0.017141 | 0.023499 | 0.0007114 | 14.3829 | 120.6207 | -1.03 | 120.1675 | -0.24719 | -0.94757 | -0.8606 | -0.082397 | 0.068665 | -0.10071 | -0.050354 | 0.022888 | -0.064087 | 0.041199 | -0.041198 | 0.39826 | -0.054931 | 0.74158 | 0.12817 | 0.041199 | 0.16937 | 0.082397 | 0.88806 | -120.1538 | -120.2728 | 1.0117 | 1.03 | 0.92468 | 0.14191 | 0.036621 | 0.78278 | 121.1975 | 0.1236 | 0.050354 | 121.6507 | 0.16937 | 121.6095 | 1.0574 | -121.2524 | -120.3232 | 121.1563 | 0.93842 | 15.3717 | 0.90637
2852.4219 | 121.6919 | -0.93842 | 120.7031 | 0.0016023 | -0.0005063 | 0.052412 | 0.050063 | -0.002132 | -0.0079061 | 1.4934e-05 | -0.0051575 | 0.009848 | 0.0020828 | -0.0035183 | -0.015859 | 0.019012 | -0.0044156 | 14.4104 | 120.5795 | -0.98877 | 120.5109 | -0.12817 | -0.81482 | -0.74158 | 0.009155 | 0.041199 | -0.068665 | 0 | 0.13275 | 0.045776 | 0.10071 | -0.050354 | -0.1236 | -0.19226 | 0.81024 | 0.19684 | 0.1236 | 0.24719 | 0.17395 | 0.86975 | -120.6619 | -120.7031 | 1.0712 | 1.0391 | 0.98419 | 0.16937 | 0.11444 | 0.8606 | 121.4996 | 0.20142 | 0.068665 | 121.5683 | 0.10986 | 121.5179 | 0.97962 | -121.6919 | -120.7718 | 121.4493 | 0.93842 | 15.3488 | 0.94757
2854.1875 | 121.7194 | -0.94299 | 120.7031 | 0.0016023 | -0.0002927 | 0.052412 | 0.05049 | -0.00085021 | -0.0096151 | -0.0023349 | -0.0051575 | 0.013266 | 0.0033646 | 0.0016085 | -0.017568 | 0.02243 | -0.0014248 | 14.4379 | 120.575 | -0.99335 | 120.6116 | -0.054932 | -0.75531 | -0.68207 | 0.091553 | 0.041199 | -0.045776 | 0.027466 | 0.16937 | 0.07782 | 0.1236 | -0.050354 | -0.12817 | -0.091553 | 0.88806 | 0.26092 | 0.18768 | 0.31128 | 0.23804 | 0.89722 | -120.6619 | -120.6757 | 1.1124 | 1.0666 | 1.0208 | 0.16937 | 0.1236 | 0.93841 | 121.6049 | 0.21515 | 0.073242 | 121.5683 | 0.086975 | 121.5179 | 0.98419 | -121.6965 | -120.7489 | 121.5546 | 0.97046 | 15.3809 | 1.0345
2855.875 | 121.7422 | -0.9201 | 120.5521 | -0.013657 | 0.0003483 | 0.050917 | 0.051344 | -0.0046954 | -0.0098287 | -0.0036167 | -0.0082093 | 0.011771 | 0.0016556 | 0.0022495 | -0.017568 | 0.022644 | -0.0022794 | 14.3646 | 120.4514 | -0.99792 | 120.6162 | -0.022888 | -0.74616 | -0.68207 | 0.10071 | 0.036621 | -0.050354 | 0.045776 | 0.19226 | 0.1236 | 0.12817 | -0.07782 | -0.10071 | 0.064087 | 0.89722 | 0.23804 | 0.17395 | 0.31586 | 0.25177 | 0.86975 | -120.5154 | -120.5063 | 1.1124 | 1.0483 | 1.0437 | 0.17853 | 0.17395 | 0.97504 | 121.6141 | 0.24261 | 0.09613 | 121.4493 | 0.086975 | 121.3715 | 0.95673 | -121.55 | -120.6024 | 121.5363 | 0.96588 | 15.2847 | 1.0208
2857.6562 | 121.7468 | -0.95673 | 120.6345 | -0.0060272 | -7.9104e-05 | 0.051771 | 0.051558 | -0.00085021 | -0.0079061 | -0.0012669 | -0.0051575 | 0.012625 | 0.0016556 | 0.00054052 | -0.015219 | 0.020294 | -0.000784 | 14.2593 | 120.6299 | -1.0071 | 120.5521 | -0.07782 | -0.81024 | -0.72327 | 0.032043 | 0.045776 | -0.059509 | 0.036621 | 0.16479 | 0.082397 | 0.11902 | -0.050354 | -0.004577 | -0.082397 | 0.87891 | 0.23346 | 0.14648 | 0.28381 | 0.19684 | 0.89722 | -120.5887 | -120.5978 | 1.1215 | 1.0757 | 1.0391 | 0.17853 | 0.14191 | 0.92926 | 121.5591 | 0.2243 | 0.09613 | 121.637 | 0.10528 | 121.5866 | 1.0025 | -121.6415 | -120.694 | 121.5088 | 0.99335 | 15.2161 | 0.98877
2859.3594 | 121.3806 | -0.98877 | 120.6665 | -0.013657 | -0.0009335 | 0.048994 | 0.056258 | -0.0051226 | -0.0091879 | -0.0040439 | -0.0021057 | 0.013907 | 0.0048598 | 0.0050265 | -0.016073 | 0.020935 | 0.0007114 | 14.2364 | 120.5292 | -1.0529 | 120.5017 | -0.14191 | -0.8606 | -0.80109 | -0.036621 | 0.073242 | -0.086975 | -0.054932 | 0.059509 | -0.027466 | 0.032043 | -0.064086 | -0.13733 | -0.16479 | 0.84686 | 0.18768 | 0.12817 | 0.25177 | 0.19226 | 0.9018 | -120.5933 | -120.7214 | 1.0483 | 1.0208 | 0.9613 | 0.11902 | 0.059509 | 0.91095 | 121.5546 | 0.14648 | 0.032043 | 121.582 | 0.16022 | 121.5179 | 1.062 | -121.7194 | -120.7535 | 121.4905 | 0.93384 | 15.2252 | 0.95215
2861.125 | 121.8109 | -0.9613 | 120.7397 | 0.0016023 | -0.0009335 | 0.04814 | 0.050917 | -0.00063661 | -0.0096151 | -0.0055393 | 0.0009461 | 0.010916 | 0.0010146 | 0.0045993 | -0.015219 | 0.022003 | -0.0003568 | 14.2364 | 120.5978 | -1.0071 | 120.6207 | -0.027466 | -0.75989 | -0.70038 | 0.10071 | 0.050354 | -0.054932 | 0.059509 | 0.21057 | 0.11902 | 0.15106 | -0.045776 | -0.14191 | -0.11902 | 0.93384 | 0.26093 | 0.20142 | 0.3067 | 0.24719 | 0.90637 | -120.6894 | -120.6802 | 1.1719 | 1.1124 | 1.0803 | 0.20599 | 0.17395 | 0.97961 | 121.6278 | 0.2655 | 0.11444 | 121.6049 | 0.10529 | 121.5591 | 1.0117 | -121.7468 | -120.7947 | 121.582 | 1.0208 | 15.1978 | 1.062
2862.8906 | 121.1929 | -0.97961 | 120.6207 | -0.013657 | -0.0024289 | 0.047285 | 0.047499 | -0.006618 | -0.019015 | -0.013016 | -0.0051575 | 0.012198 | -0.0038986 | -0.0045865 | -0.015646 | 0.008545 | 0.0011386 | 14.122 | 120.1721 | -1.0345 | 120.5887 | -0.073242 | -0.84228 | -0.7782 | 0.054932 | 0.068665 | -0.068665 | 0.018311 | 0.13275 | 0.027466 | 0.073242 | -0.054932 | -0.44861 | -0.032044 | 0.90637 | 0.20142 | 0.13733 | 0.25635 | 0.19226 | 0.91095 | -120.5521 | -120.6024 | 1.1124 | 1.0529 | 1.0071 | 0.14191 | 0.096131 | 0.9613 | 121.6232 | 0.20142 | 0.086976 | 121.2067 | 0.13733 | 121.1517 | 1.0483 | -121.6553 | -120.6894 | 121.5683 | 0.99792 | 15.1016 | 1.0345
2864.5781 | 121.3211 | -0.98877 | 120.7672 | -0.0060272 | -0.0081967 | 0.040236 | 0.051558 | -0.01089 | -0.022219 | -0.015793 | 0.0009461 | 0.014975 | -0.0013352 | 0.0078037 | -0.013937 | 0.01944 | -0.000784 | 13.7283 | 120.6985 | -1.0529 | 120.5063 | -0.15106 | -0.92926 | -0.84686 | -0.07782 | 0.082397 | -0.086975 | -0.045776 | 0.022888 | -0.059509 | 0.027466 | -0.064086 | -0.068665 | -0.26093 | 0.83771 | 0.14191 | 0.05951 | 0.20599 | 0.1236 | 0.9018 | -120.6848 | -120.813 | 1.0117 | 1.0162 | 0.92926 | 0.11444 | 0.027466 | 0.90179 | 121.5591 | 0.10986 | 0.041199 | 121.7514 | 0.16937 | 121.6873 | 1.0712 | -121.8201 | -120.8542 | 121.4951 | 0.94299 | 14.7171 | 0.91095
2866.3281 | 121.6782 | -0.98419 | 120.7306 | -0.0060272 | 0.0016299 | 0.048354 | 0.054762 | 0.0040632 | -0.0091879 | -0.0025485 | 0.0009461 | 0.015189 | 0.0022964 | 0.0054537 | -0.015005 | 0.022217 | -0.0012112 | 13.3163 | 120.7031 | -1.0345 | 120.5246 | -0.14648 | -0.89722 | -0.83313 | -0.032043 | 0.086975 | -0.082397 | -0.009155 | 0.073242 | -0.009155 | 0.064087 | -0.050354 | -0.027466 | -0.20599 | 0.83771 | 0.15106 | 0.086975 | 0.20142 | 0.13733 | 0.90179 | -120.6436 | -120.7397 | 1.0574 | 1.0483 | 0.97504 | 0.14648 | 0.073242 | 0.88806 | 121.5591 | 0.15564 | 0.073242 | 121.7377 | 0.16937 | 121.6873 | 1.0712 | -121.7651 | -120.813 | 121.5088 | 0.97504 | 14.3005 | 0.95215
2868.0938 | 121.2296 | -0.98877 | 120.2637 | -0.0060272 | 0.0029117 | 0.045363 | 0.054549 | -0.0051226 | -0.017306 | -0.017929 | -0.0051575 | 0.013052 | -0.00048057 | -0.0011685 | -0.017782 | 0.011963 | -0.00527 | 13.1699 | 120.3827 | -1.0391 | 120.4422 | -0.068665 | -0.82398 | -0.77362 | 0.022888 | 0.068665 | -0.07782 | -0.004578 | 0.10986 | 0.004578 | 0.068665 | -0.050354 | 0.11902 | 0.17853 | 0.92011 | 0.21515 | 0.1648 | 0.2655 | 0.21515 | 0.91095 | -120.195 | -120.2682 | 1.0986 | 1.0574 | 0.99335 | 0.14649 | 0.082398 | 0.97046 | 121.4813 | 0.18768 | 0.073242 | 121.4218 | 0.14649 | 121.3715 | 1.0574 | -121.3028 | -120.3415 | 121.431 | 0.98419 | 14.1586 | 1.0117
2869.7812 | 121.8338 | -0.95673 | 120.6985 | -0.013657 | 0.0037661 | 0.051344 | 0.051131 | 0.001286 | -0.0066245 | -0.0016941 | -0.0082093 | 0.012198 | 0.0018692 | -0.0022367 | -0.018209 | 0.02179 | 7.04e-05 | 13.0371 | 120.6894 | -1.0345 | 120.6299 | -0.018311 | -0.80566 | -0.71411 | 0.073242 | 0.036621 | -0.054932 | 0.073242 | 0.17853 | 0.086975 | 0.15564 | -0.07782 | -0.009155 | -0.068664 | 0.93841 | 0.24261 | 0.15106 | 0.32043 | 0.22888 | 0.90179 | -120.6619 | -120.6253 | 1.1353 | 1.1124 | 1.0437 | 0.21057 | 0.14191 | 1.0162 | 121.6644 | 0.23346 | 0.12817 | 121.7239 | 0.091553 | 121.6461 | 0.99335 | -121.7331 | -120.7535 | 121.5866 | 1.03 | 13.9938 | 1.03
2871.5312 | 121.843 | -0.97504 | 120.7855 | -0.0060272 | 0.0001345 | 0.050276 | 0.051344 | 0.00064519 | -0.0085471 | -0.0025485 | -0.0082093 | 0.010489 | 0.004219 | 0.0013949 | -0.015219 | 0.021362 | 0.0002842 | 12.9181 | 120.6711 | -1.0117 | 120.6345 | -0.018311 | -0.76446 | -0.68665 | 0.064087 | 0.045776 | -0.064087 | 0.041199 | 0.18768 | 0.11902 | 0.13733 | -0.036621 | -0.11444 | -0.15106 | 0.95673 | 0.28839 | 0.21057 | 0.32501 | 0.24719 | 0.91095 | -120.7397 | -120.7443 | 1.1627 | 1.1124 | 1.0941 | 0.20142 | 0.18311 | 0.99335 | 121.6461 | 0.25177 | 0.10529 | 121.6827 | 0.10986 | 121.6461 | 1.0208 | -121.7972 | -120.8496 | 121.6095 | 1.0162 | 13.8931 | 1.0391
2873.2344 | 121.8704 | -0.96588 | 120.7809 | -0.013657 | 0.0020571 | 0.050063 | 0.051985 | -0.00063661 | -0.0094015 | -0.0046847 | -0.0051575 | 0.010489 | 0.0012282 | -0.0048001 | -0.0165 | 0.02179 | -0.0029202 | 12.8128 | 120.6894 | -1.0071 | 120.6619 | 0.041199 | -0.737 | -0.66834 | 0.11444 | 0.050354 | -0.064087 | 0.07782 | 0.21973 | 0.12817 | 0.14648 | -0.041199 | -0.091553 | -0.11902 | 1.0071 | 0.29755 | 0.22888 | 0.33874 | 0.27008 | 0.90179 | -120.7306 | -120.7031 | 1.1856 | 1.1124 | 1.0941 | 0.21057 | 0.19226 | 1.0483 | 121.669 | 0.28381 | 0.14191 | 121.6965 | 0.11444 | 121.6553 | 1.0162 | -121.788 | -120.845 | 121.6278 | 1.0437 | 13.7787 | 1.0803
2874.9844 | 121.6095 | -0.99792 | 120.845 | -0.059433 | 0.0009891 | 0.051344 | 0.054762 | 0.0057722 | -0.0083335 | -0.0021213 | 0.0009461 | 0.013266 | 0.00251 | 0.0050265 | -0.016928 | 0.023712 | -0.0016384 | 12.7716 | 120.3827 | -1.0437 | 120.5521 | -0.10071 | -0.84686 | -0.80109 | -0.036621 | 0.064087 | -0.091553 | -0.036621 | 0.064087 | -0.018311 | 0.050354 | -0.045776 | -0.46234 | -0.29297 | 0.89722 | 0.19684 | 0.15106 | 0.24262 | 0.19684 | 0.90637 | -120.7809 | -120.8817 | 1.062 | 1.0483 | 0.97961 | 0.14191 | 0.073242 | 0.94299 | 121.5958 | 0.15564 | 0.054932 | 121.4264 | 0.15564 | 121.3806 | 1.062 | -121.8887 | -120.9366 | 121.55 | 0.9613 | 13.7695 | 0.9613
2876.7344 | 121.8842 | -0.96588 | 120.7764 | -0.0060272 | 0.0003483 | 0.049422 | 0.051131 | -0.0057636 | -0.0096151 | -0.0031895 | -0.0051575 | 0.01113 | 0.003151 | 0.0022495 | -0.018423 | 0.023712 | 0.000925 | 12.7533 | 120.6482 | -1.0391 | 120.7306 | 0.09613 | -0.70038 | -0.6546 | 0.13733 | 0.045776 | -0.041199 | 0.068665 | 0.21515 | 0.1236 | 0.14191 | -0.073243 | -0.12817 | -0.045776 | 1.062 | 0.31128 | 0.2655 | 0.38452 | 0.33875 | 0.92468 | -120.7306 | -120.7077 | 1.181 | 1.1078 | 1.0895 | 0.18311 | 0.16479 | 1.1353 | 121.7697 | 0.25635 | 0.10986 | 121.6873 | 0.086975 | 121.6141 | 1.0117 | -121.8155 | -120.8176 | 121.6965 | 1.0345 | 13.7192 | 1.1032
2878.5 | 121.7697 | -0.99792 | 120.7855 | -0.021286 | 0.0024845 | 0.041731 | 0.057326 | 0.0027814 | -0.013247 | -0.0046847 | -0.0021057 | 0.012839 | 0.0022964 | 0.0088717 | -0.015859 | 0.021149 | -0.0003568 | 12.5381 | 120.7443 | -1.0529 | 120.5566 | -0.086975 | -0.91095 | -0.81024 | -0.032043 | 0.07782 | -0.082397 | -0.041199 | 0.050354 | -0.045776 | 0.041199 | -0.054931 | -0.041198 | -0.22888 | 0.91095 | 0.18768 | 0.086975 | 0.24261 | 0.14191 | 0.91553 | -120.7077 | -120.8267 | 1.0483 | 1.0391 | 0.95215 | 0.1236 | 0.036621 | 0.96588 | 121.6095 | 0.13275 | 0.041198 | 121.7972 | 0.16022 | 121.7422 | 1.0757 | -121.8384 | -120.8679 | 121.5546 | 0.95673 | 13.5361 | 0.96588
2880.2656 | 121.8475 | -0.97504 | 120.7809 | -0.0060272 | 0.0031253 | 0.054549 | 0.052626 | -0.0027728 | -0.0079061 | -0.0048985 | -0.0082093 | 0.011984 | 0.001442 | -0.0050137 | -0.016287 | 0.019653 | 0.0007114 | 12.4374 | 120.6985 | -1.0071 | 120.694 | 0.091553 | -0.77362 | -0.68207 | 0.10529 | 0.027466 | -0.059509 | 0.036621 | 0.16022 | 0.082397 | 0.11444 | -0.032043 | -0.082398 | -0.086975 | 1.0666 | 0.29297 | 0.20142 | 0.32501 | 0.23346 | 0.91553 | -120.7535 | -120.7443 | 1.1353 | 1.0895 | 1.0574 | 0.17395 | 0.14191 | 1.0986 | 121.701 | 0.21973 | 0.09613 | 121.7056 | 0.086975 | 121.6736 | 1.0025 | -121.788 | -120.8405 | 121.669 | 1.0117 | 13.4125 | 1.0803
2882.0156 | 121.9254 | -0.97504 | 120.7809 | -0.0060272 | 0.0022709 | 0.05284 | 0.053267 | 0.0023542 | -0.0066245 | -0.0014805 | -0.0082093 | 0.010489 | 0.0027236 | 0.0039585 | -0.017568 | 0.019867 | -0.0001432 | 12.2406 | 120.7077 | -0.99792 | 120.6802 | 0.10529 | -0.75989 | -0.67749 | 0.12817 | 0.022888 | -0.045776 | 0.073242 | 0.17853 | 0.068665 | 0.12817 | -0.022888 | -0.073242 | -0.10071 | 1.0803 | 0.29755 | 0.21515 | 0.32043 | 0.23804 | 0.92926 | -120.7581 | -120.7077 | 1.1536 | 1.1032 | 1.0437 | 0.17395 | 0.11444 | 1.1032 | 121.6782 | 0.2243 | 0.11902 | 121.7056 | 0.068664 | 121.6827 | 0.99793 | -121.7789 | -120.8267 | 121.6553 | 1.0483 | 13.2156 | 1.1032
2883.7812 | 121.9116 | -0.97046 | 120.8084 | -0.0060272 | -0.0009335 | 0.052199 | 0.05348 | -0.0010638 | -0.0057699 | -0.0014805 | -0.0021057 | 0.010489 | 0.0016556 | -0.0056547 | -0.016073 | 0.021149 | -0.008688 | 11.998 | 120.5566 | -1.0208 | 120.726 | 0.15564 | -0.71411 | -0.6546 | 0.11444 | 0.041199 | -0.054932 | 0.064087 | 0.20599 | 0.10529 | 0.1236 | -0.050354 | -0.25177 | -0.082398 | 1.1261 | 0.31586 | 0.25635 | 0.36621 | 0.3067 | 0.91553 | -120.7672 | -120.7443 | 1.1765 | 1.0941 | 1.0757 | 0.17853 | 0.16022 | 1.1765 | 121.7468 | 0.26093 | 0.11902 | 121.5775 | 0.096131 | 121.5271 | 1.0117 | -121.8292 | -120.8633 | 121.6965 | 1.0345 | 12.9684 | 1.0849
2885.5 | 121.788 | -1.0071 | 120.7443 | -0.0060272 | 0.0014163 | 0.04814 | 0.054121 | -0.00555 | -0.010043 | -0.0046847 | 0.0009461 | 0.013052 | 0.004219 | 0.0018221 | -0.015859 | 0.023712 | -0.0018522 | 11.6821 | 120.4651 | -1.0666 | 120.6024 | 0.036621 | -0.83771 | -0.77362 | -0.032043 | 0.068665 | -0.09613 | -0.059509 | 0.064087 | -0.022888 | 0.022888 | -0.059509 | -0.27924 | -0.14191 | 1.0437 | 0.23346 | 0.16937 | 0.29297 | 0.22888 | 0.91095 | -120.6757 | -120.8038 | 1.0712 | 1.03 | 0.98419 | 0.11902 | 0.073242 | 1.1032 | 121.669 | 0.16022 | 0.036621 | 121.5317 | 0.16479 | 121.4722 | 1.0757 | -121.8109 | -120.8405 | 121.6095 | 0.94757 | 12.6892 | 0.97504
2887.25 | 121.875 | -0.99792 | 120.845 | -0.0060272 | -0.0009335 | 0.053053 | 0.054549 | -0.004909 | -0.0087607 | -0.0019077 | -0.0051575 | 0.012625 | 0.0020828 | -0.00010048 | -0.018209 | 0.021576 | -0.006979 | 11.4349 | 120.4651 | -1.0254 | 120.726 | 0.15106 | -0.74158 | -0.68665 | 0.07782 | 0.059509 | -0.068665 | 0.018311 | 0.15106 | 0.068665 | 0.10986 | -0.027466 | -0.37994 | -0.11902 | 1.149 | 0.31128 | 0.25635 | 0.33874 | 0.28381 | 0.92926 | -120.7855 | -120.8267 | 1.149 | 1.1078 | 1.0666 | 0.17853 | 0.13733 | 1.1765 | 121.7514 | 0.21973 | 0.086976 | 121.4905 | 0.12817 | 121.463 | 1.0574 | -121.8704 | -120.9137 | 121.7239 | 1.0162 | 12.4329 | 1.0757
2888.9375 | 90.3076 | -0.11902 | 89.5386 | 0.15419 | 0.029187 | 0.1103 | -0.012743 | 0.047642 | 0.058103 | 0.051925 | 0.058929 | 0.030356 | 0.011909 | 0.0067355 | 0.26847 | 0.038879 | 0.032755 | 0.11902 | 91.2231 | -0.10071 | 90.2802 | 0.11902 | 0.1236 | 0.1236 | 0.11902 | 0.1236 | -0.1236 | 0.11902 | 0.1236 | 0.11902 | 0.11902 | 0.018311 | 1.6846 | 0.74158 | 0.23804 | 0.24261 | 0.24261 | 0.2243 | 0.2243 | -0.004577 | -89.415 | -89.4196 | 0.24261 | 0.23804 | 0.23804 | 0.24261 | 0.24261 | 0.21973 | 90.3809 | 0.24719 | 0.24261 | 91.3239 | 0.24719 | 91.3422 | 0.24261 | -89.6393 | -89.6622 | 90.3992 | 0.23804 | 0.23804 | 0.23804
2890.6875 | 118.2678 | -0.68207 | 95.6726 | 0.16182 | -0.0058469 | 0.051344 | 0.039381 | -0.0040546 | -0.0064109 | -0.0044711 | 0.068085 | -0.002115 | -0.0068894 | -0.0071499 | -0.020132 | 0.018372 | -0.011892 | 10.9634 | 92.4133 | -0.15106 | 110.5637 | 0.20142 | 0.12817 | 0.13275 | -0.28381 | 0.082397 | -0.11902 | 0.09613 | 0.12817 | 0.12817 | 0.12817 | 0.53101 | -3.2593 | 14.8911 | 0.88348 | 0.81482 | 0.81024 | 0.28381 | 0.27924 | 0.56305 | -95.5902 | -95.5765 | 0.81024 | 0.81024 | 0.81024 | 0.24719 | 0.24719 | 0.35248 | 110.7147 | 0.24719 | 0.21515 | 92.5644 | 0.20142 | 93.0954 | 0.76446 | -95.8237 | -95.7916 | 111.2457 | 0.7782 | 11.6455 | 0.39826
2892.4375 | 94.8257 | -0.98877 | 92.2897 | 0.15419 | -0.0058469 | 0.050917 | 0.038527 | -0.0025592 | -0.0066245 | -0.0036167 | 0.068085 | 0.00044864 | -0.0075302 | -0.0035183 | -0.020346 | 0.016449 | -0.0091152 | 10.7529 | 92.0517 | -0.17853 | 110.788 | 0.2243 | 0.14648 | 0.12817 | 0.091553 | 0.12817 | -0.1236 | 0.10071 | 0.13275 | 0.12817 | 0.12817 | 0.81024 | -0.23804 | 18.4982 | 1.2131 | 1.1169 | 1.1353 | 0.3067 | 0.32501 | 0.86517 | -92.1616 | -92.189 | 1.1215 | 1.1169 | 1.1169 | 0.25177 | 0.25177 | 0.40283 | 110.9665 | 0.25635 | 0.2243 | 92.2302 | 0.25177 | 93.0405 | 1.1169 | -92.4683 | -92.4133 | 111.7767 | 1.0895 | 11.7416 | 1.0803
2894.2031 | 121.4127 | -22.7417 | 88.3667 | -0.021286 | -0.0041379 | 0.10924 | -0.011034 | 0.048069 | 0.05789 | 0.051925 | 0.061981 | 0.030783 | 0.012123 | 0.0067355 | 0.26826 | 0.038879 | 0.033182 | 0.13275 | 90.3168 | -0.21515 | 86.8561 | 0.16937 | 0.13275 | 0.12817 | 0.11902 | 0.1236 | -0.1236 | 0.12817 | 0.11902 | 0.1236 | 0.1236 | 22.5266 | 1.9501 | -1.5106 | 22.9111 | 22.8699 | 22.8744 | 0.34332 | 0.3479 | 22.6181 | -88.2431 | -88.2385 | 22.8607 | 22.8653 | 22.8653 | 0.24719 | 0.24719 | 0.38452 | 87.0712 | 0.24261 | 0.25177 | 90.5319 | 0.24719 | 113.0585 | 22.8653 | -88.5818 | -88.4903 | 109.5978 | 22.8699 | 22.8744 | 22.8607
2895.9062 | 121.9986 | -20.4483 | 88.0554 | 0.15419 | -0.014178 | 0.04814 | 0.039595 | 0.0089764 | -0.0096151 | -0.0027621 | -0.090607 | 0.0032256 | 0.00080103 | -0.0018093 | -0.014364 | 0.02243 | 0.0004978 | 5.0079 | 89.5157 | -10.0662 | 79.01 | -38.4247 | -27.8778 | -23.4924 | -0.086975 | 0.1236 | -0.1236 | -0.36163 | 0.041199 | -0.064087 | -0.045776 | 10.3821 | 1.4603 | -9.0454 | -17.9764 | -3.0441 | -7.4295 | -13.4262 | -17.8116 | 20.3247 | -87.9318 | -88.4171 | 20.4895 | 20.4025 | 20.3842 | 0.07782 | 0.059509 | -28.3585 | 89.0762 | 0.16479 | -0.23804 | 99.5819 | 0.24719 | 109.964 | 20.5719 | -98.1216 | -88.179 | 99.4583 | 20.0867 | 25.4562 | 20.3613
2897.6719 | 121.9345 | -0.86975 | 115.4388 | 0.15419 | -0.0096921 | 0.047926 | 0.042372 | -0.0059772 | -0.011965 | -0.0074619 | 0.065033 | -0.0044648 | -0.011162 | -0.015054 | -0.023336 | 0.011536 | -0.017447 | 8.7158 | 91.4337 | -0.21973 | 109.9869 | 0.21515 | 0.13275 | 0.12817 | 0.10071 | 0.1236 | -0.1236 | 0.09613 | 0.1236 | 0.12817 | 0.11902 | 0.65002 | -24.0051 | -5.452 | 1.0849 | 0.99793 | 1.0025 | 0.3479 | 0.35248 | 0.74616 | -115.3152 | -115.3427 | 0.99335 | 0.98877 | 0.99793 | 0.24261 | 0.25177 | 0.43488 | 110.2066 | 0.24719 | 0.21973 | 91.6534 | 0.24719 | 92.3035 | 0.99335 | -115.6586 | -115.5624 | 110.8566 | 0.96588 | 9.5856 | 0.97046
2899.4219 | 121.9208 | -4.8843 | 116.5604 | 0.0016023 | 0.0009891 | 0.052199 | 0.050276 | 4.192e-06 | -0.0098287 | -0.0036167 | -0.23099 | 0.0077118 | 0.00016023 | -0.00031408 | -0.017996 | 0.021576 | 0.0007114 | 8.876 | 116.5878 | -1.0941 | 119.5129 | -1.7761 | -2.5452 | -2.1652 | -0.018311 | -0.036621 | -0.13275 | 0.004578 | -0.032043 | -0.13275 | -0.13733 | 3.7903 | 0.027466 | 2.9526 | 3.1082 | 2.7191 | 2.3392 | -1.0712 | -1.4511 | 4.7516 | -116.597 | -116.5558 | 4.8523 | 4.747 | 4.7516 | -0.004578 | 0 | -0.68207 | 120.607 | 0.10071 | 0.13733 | 117.6819 | 0.09613 | 121.4722 | 4.8477 | -117.6544 | -116.6931 | 124.3973 | 4.8889 | 13.7604 | 4.866
2901.1719 | 121.6873 | -120.195 | 1.2405 | 0.1313 | 0.028546 | 0.11159 | 0.04579 | -0.014522 | -0.0098287 | -0.0076755 | -0.23404 | -0.00831 | -0.011162 | -0.012277 | -0.026327 | 0.01239 | -0.015738 | -32.0847 | 1.2039 | -120.3918 | 0.10986 | -89.5981 | -100.5524 | -100.9689 | -0.27466 | -0.064087 | -0.11444 | -0.059509 | -0.09613 | 0.11444 | 0.11902 | -0.19684 | -0.036622 | -1.1307 | 30.5969 | 19.2261 | 19.6426 | 19.4229 | 19.8395 | 120.0806 | -1.3046 | -1.3 | 120.0989 | 120.314 | 120.3094 | 0.23346 | 0.22888 | 30.7938 | 120.5017 | 0.018311 | 0.054932 | 121.5958 | 0.050354 | 121.3989 | 120.1309 | -121.6324 | -1.355 | 120.3049 | 120.1355 | 88.1104 | 119.9203
2902.9375 | 121.7285 | -120.1721 | 1.2314 | 0.15419 | -0.0022153 | 0.055617 | 0.053053 | -0.0017048 | -0.0070517 | 0.00022853 | -0.0021057 | 0.009848 | -0.00069437 | -0.0045865 | -0.014791 | 0.021149 | -0.0014248 | -49.3698 | 1.1536 | -120.3003 | 1.1307 | -115.9836 | -119.4626 | -119.5312 | 0.11444 | -0.11902 | 0.23804 | 0.082397 | 0.16479 | -0.036621 | -0.045776 | -0.12817 | -0.07782 | -0.10071 | 4.1885 | 0.64087 | 0.70953 | 0.76904 | 0.83771 | 120.4102 | -1.3504 | -1.149 | 120.3369 | 120.1263 | 120.1355 | -0.28381 | -0.27466 | 4.3167 | 121.431 | -0.073242 | -0.15564 | 121.4539 | -0.35706 | 121.3257 | 120.0531 | -121.5317 | -0.99335 | 121.3028 | 120.2545 | 70.8023 | 120.2866
2904.625 | 121.5683 | -120.1859 | 1.2405 | -0.57823 | -0.0041379 | 0.056685 | 0.050276 | -0.0070452 | -0.0064109 | -0.0083163 | -0.13638 | 0.0010894 | -0.0045396 | -0.0069363 | -0.022055 | 0.01004 | -0.0095426 | -48.468 | 1.0162 | -120.0485 | 0.78735 | -102.7542 | -107.5424 | -106.9794 | -0.045776 | -0.10529 | 0.18768 | -0.013733 | -0.15564 | 0.10071 | 0.11444 | 0.13733 | -0.2243 | -0.45319 | 17.4316 | 13.2065 | 12.6434 | 13.0692 | 12.5061 | 120.3735 | -1.3458 | -1.2543 | 120.0302 | 120.3003 | 120.2866 | -0.073242 | -0.086975 | 17.2943 | 120.8359 | -0.34332 | -0.20142 | 121.0648 | -0.29297 | 121.2021 | 120.0806 | -121.2891 | -1.0529 | 120.9732 | 120.1721 | 71.7178 | 120.1401
2906.3125 | 121.6003 | -120.163 | 1.1993 | -0.41801 | 0.0005619 | 0.05818 | 0.050917 | -0.0042682 | -0.0044883 | -0.00083947 | -0.0021057 | 0.011771 | 0.003151 | -0.0065091 | -0.015219 | 0.020081 | 0.0045566 | -47.8317 | 1.1307 | -120.195 | 1.0941 | -115.892 | -119.4992 | -119.5312 | 0.11902 | 0.027466 | 0.050354 | 0.086975 | 0.14191 | 0.059509 | 0.10071 | -0.032043 | -0.068665 | -0.10529 | 4.2709 | 0.63171 | 0.66376 | 0.66376 | 0.6958 | 120.2133 | -1.1719 | -1.1124 | 120.3049 | 120.2637 | 120.2225 | 0.050354 | 0.009155 | 4.303 | 121.2891 | 0.091553 | 0.036621 | 121.3257 | -0.022888 | 121.2936 | 120.1904 | -121.3943 | -1.149 | 121.257 | 120.2499 | 72.3312 | 120.282
2908.0781 | 121.55 | -120.1309 | 1.2039 | -0.16624 | -0.0013607 | 0.057967 | 0.052626 | -0.004909 | -0.0059835 | 1.4934e-05 | -0.0051575 | 0.009848 | 0.0018692 | -0.0028775 | -0.015219 | 0.022217 | 0.0024204 | -46.8109 | 1.1353 | -120.2225 | 1.0529 | -115.9973 | -119.6136 | -119.6274 | 0.032043 | 0.041199 | -0.050354 | 0.045776 | 0.13275 | 0.054932 | 0.10986 | -0.091553 | -0.068664 | -0.15106 | 4.1336 | 0.50354 | 0.51727 | 0.59509 | 0.60883 | 120.0806 | -1.1627 | -1.1581 | 120.2637 | 120.2408 | 120.1859 | 0.16022 | 0.10529 | 4.2252 | 121.2753 | 0.18311 | 0.09613 | 121.3577 | 0.091553 | 121.2662 | 120.1721 | -121.4264 | -1.2543 | 121.1838 | 120.1767 | 73.32 | 120.163
2909.8281 | 121.5134 | -120.1401 | 1.2039 | 0.12367 | -0.0005063 | 0.059889 | 0.05049 | -0.0046954 | -0.0047019 | 0.00044213 | -0.0051575 | 0.010275 | 0.0022964 | -0.0062955 | -0.014791 | 0.02243 | 0.000925 | -45.813 | 1.1307 | -120.1904 | 1.0666 | -115.9149 | -119.5587 | -119.5724 | 0.041199 | 0.054932 | -0.059509 | 0.050354 | 0.1236 | 0.045776 | 0.09613 | -0.050354 | -0.073242 | -0.13733 | 4.2252 | 0.56763 | 0.58136 | 0.61798 | 0.63171 | 120.0806 | -1.149 | -1.1536 | 120.2637 | 120.2362 | 120.1859 | 0.15564 | 0.10528 | 4.2755 | 121.257 | 0.1831 | 0.10986 | 121.3211 | 0.11444 | 121.2708 | 120.195 | -121.3943 | -1.2634 | 121.2067 | 120.1904 | 74.3271 | 120.1813
2911.5781 | 121.5271 | -120.1035 | 1.2085 | 0.1313 | -0.0026425 | 0.057112 | 0.05284 | -0.00042301 | -0.0057699 | -0.0021213 | -0.0051575 | 0.012198 | 0.0027236 | -0.0024503 | -0.015859 | 0.021149 | -0.0020658 | -44.9615 | 1.149 | -120.195 | 1.0986 | -115.8737 | -119.5404 | -119.5724 | 0.091553 | 0.050354 | -0.073242 | 0.073242 | 0.17853 | 0.10071 | 0.12817 | -0.091552 | -0.059509 | -0.10986 | 4.2297 | 0.53101 | 0.56305 | 0.62256 | 0.6546 | 120.0302 | -1.1581 | -1.1353 | 120.282 | 120.2316 | 120.2042 | 0.20142 | 0.17395 | 4.3213 | 121.2936 | 0.25177 | 0.14648 | 121.344 | 0.1236 | 121.2524 | 120.1538 | -121.4035 | -1.2817 | 121.2021 | 120.1767 | 75.1419 | 120.195
2913.2812 | 121.5134 | -120.0714 | 1.2039 | 0.10841 | 0.0003483 | 0.059676 | 0.054976 | 0.0036358 | -0.0036337 | -0.00041227 | -0.0051575 | 0.01113 | -0.00069437 | 0.0031039 | -0.014578 | 0.023071 | -0.0003568 | -43.7714 | 1.1261 | -120.1355 | 1.1078 | -115.6174 | -119.3344 | -119.3207 | 0.12817 | 0.036621 | -0.032043 | 0.10529 | 0.1831 | 0.07782 | 0.10529 | -0.064087 | -0.077819 | -0.09613 | 4.454 | 0.75073 | 0.737 | 0.81482 | 0.80109 | 120.0394 | -1.1673 | -1.0986 | 120.2545 | 120.1767 | 120.1492 | 0.13733 | 0.10986 | 4.5181 | 121.2433 | 0.21515 | 0.13733 | 121.2616 | 0.068664 | 121.1975 | 120.108 | -121.3394 | -1.236 | 121.1792 | 120.1767 | 76.3 | 120.1996
2915.0312 | 121.344 | -120.0989 | 1.2268 | -0.5706 | 0.028119 | 0.10945 | 0.040877 | 0.04636 | 0.057035 | 0.050857 | -0.10281 | 0.010275 | -0.0079574 | -0.0052273 | -0.039999 | 0.034607 | -0.013815 | -30.455 | 1.1765 | -120.1721 | 1.0208 | -115.4984 | -114.7476 | -105.368 | -0.036621 | 0.07782 | -0.086975 | -0.022888 | 0.036621 | -0.1236 | -0.30212 | -0.073242 | -0.050354 | -0.20599 | 4.6005 | 14.7308 | 5.3513 | 14.8041 | 5.4245 | 120.0119 | -1.149 | -1.2497 | 120.1355 | 119.7968 | 119.9753 | -0.21515 | -0.036621 | 4.6738 | 121.1929 | 0.1236 | 0.064087 | 121.3486 | 0.16479 | 121.2753 | 120.1767 | -121.3989 | -1.3138 | 121.1197 | 120.076 | 89.6439 | 120.0623
2916.7344 | 121.431 | -120.0348 | 1.2131 | -0.3875 | -0.0032833 | 0.057967 | 0.051131 | -0.00020941 | -0.0066245 | 1.4934e-05 | -0.0021057 | 0.011343 | 0.00058743 | -0.0011685 | -0.015646 | 0.02179 | -0.0014248 | -22.1741 | 1.1261 | -120.0897 | 1.0529 | -115.5533 | -119.5679 | -119.5633 | 0.032043 | 0.045776 | -0.045776 | 0.022888 | 0.12817 | 0.041199 | 0.09613 | -0.054932 | -0.086975 | -0.16022 | 4.4815 | 0.4715 | 0.46692 | 0.52643 | 0.52185 | 119.989 | -1.1673 | -1.1902 | 120.163 | 120.1309 | 120.076 | 0.14191 | 0.086975 | 4.5364 | 121.1426 | 0.17395 | 0.068664 | 121.2158 | 0.091552 | 121.1609 | 120.0806 | -121.3028 | -1.2589 | 121.0876 | 120.0577 | 97.8607 | 120.0668
2918.5 | 121.3715 | -120.0302 | 1.2314 | -0.013657 | -0.010974 | 0.04344 | 0.05049 | -0.0089678 | -0.017092 | -0.014298 | -0.035675 | -0.0033966 | -0.012016 | -0.0048001 | -0.022055 | 0.015381 | -0.011252 | -19.5923 | 1.1627 | -120.1401 | 1.0574 | -115.1093 | -119.4489 | -114.1891 | 0.036621 | 0.07782 | -0.091553 | 0.018311 | 0.11902 | 0.009155 | -0.17853 | -0.10986 | -0.068664 | -0.17395 | 4.921 | 5.8411 | 0.58136 | 5.9509 | 0.69122 | 119.9387 | -1.1536 | -1.2131 | 120.1492 | 119.8517 | 120.0394 | -0.086975 | 0.10071 | 5.0308 | 121.1975 | 0.21057 | 0.10986 | 121.3028 | 0.16937 | 121.1929 | 120.108 | -121.3715 | -1.3229 | 121.0876 | 120.0485 | 100.4379 | 120.0668
2920.2031 | 121.4127 | -119.9936 | 1.1993 | -0.013657 | -0.0011471 | 0.06053 | 0.052626 | 0.00043159 | -0.0023519 | -0.0012669 | -0.0021057 | 0.0096344 | 0.0020828 | -0.0045865 | -0.015005 | 0.021362 | -0.0016384 | -17.2348 | 1.1261 | -120.0851 | 1.0895 | -115.3198 | -119.5084 | -119.545 | 0.059509 | 0.036621 | -0.059509 | 0.050354 | 0.14191 | 0.050354 | 0.11902 | -0.091553 | -0.073242 | -0.10986 | 4.6738 | 0.44861 | 0.48523 | 0.54016 | 0.57678 | 119.9341 | -1.1627 | -1.149 | 120.1355 | 120.1126 | 120.0439 | 0.17853 | 0.10986 | 4.7653 | 121.1746 | 0.20142 | 0.10986 | 121.2112 | 0.09613 | 121.1197 | 120.0302 | -121.2845 | -1.2589 | 121.0831 | 120.0439 | 102.7588 | 120.0531
2921.9688 | 121.3806 | -120.0073 | 1.181 | 0.1313 | -0.0005063 | 0.059035 | 0.051985 | 0.00043159 | -0.0032065 | 0.00022853 | -0.0021057 | 0.012411 | 0.0029372 | 0.0020359 | -0.016287 | 0.021362 | -0.0016384 | -15.0879 | 1.1307 | -120.0577 | 1.1261 | -115.2008 | -119.458 | -119.458 | 0.1236 | 0.036621 | -0.045776 | 0.073242 | 0.16479 | 0.059509 | 0.10529 | -0.050354 | -0.050354 | -0.054931 | 4.8065 | 0.54932 | 0.54932 | 0.59967 | 0.59967 | 119.9615 | -1.1444 | -1.1078 | 120.1721 | 120.1126 | 120.0668 | 0.15106 | 0.10528 | 4.8569 | 121.1838 | 0.21057 | 0.11902 | 121.1884 | 0.082397 | 121.138 | 120.0439 | -121.2387 | -1.2268 | 121.1334 | 120.0806 | 104.9194 | 120.1309
2923.6719 | 121.3303 | -120.0027 | 1.2314 | -0.36461 | -0.015246 | 0.051344 | 0.054762 | -0.0064044 | -0.0059835 | -0.014298 | -0.0051575 | -0.00083316 | -0.0066758 | 0.0022495 | -0.019491 | 0.0036316 | -0.010397 | -13.7054 | 1.1581 | -120.0943 | 1.03 | -115.0085 | -119.133 | -119.6091 | 0.009155 | 0.064087 | -0.064087 | 0.013733 | 0.11444 | 0.009155 | -0.004578 | -0.091552 | -0.073242 | -0.20142 | 4.9942 | 0.39368 | 0.86975 | 0.48523 | 0.9613 | 119.9387 | -1.1673 | -1.2177 | 120.1172 | 119.9982 | 120.0119 | 0.059509 | 0.073242 | 5.0858 | 121.1243 | 0.17853 | 0.07782 | 121.2524 | 0.12817 | 121.1609 | 120.0668 | -121.3257 | -1.2955 | 121.0327 | 120.0165 | 106.2973 | 120.0119
2925.4219 | 121.2158 | -120.0119 | 1.2222 | -0.09758 | 0.028119 | 0.11052 | 0.052199 | 0.045933 | 0.058317 | 0.051925 | -0.0051575 | -0.0036102 | -0.0013352 | -0.00031408 | -0.025045 | 0.034607 | -0.019369 | -12.442 | 1.149 | -120.0211 | 1.0483 | -114.8895 | -119.1284 | -119.7968 | 0.004578 | 0.09613 | -0.073242 | -0.004578 | 0.091553 | -0.045776 | -0.004578 | -0.009155 | -0.073242 | -0.17395 | 5.1224 | 0.21515 | 0.88348 | 0.2243 | 0.89264 | 119.9387 | -1.1261 | -1.2268 | 120.1035 | 120.0073 | 119.9661 | 0.068664 | 0.027466 | 5.1315 | 121.0693 | 0.16479 | 0.068664 | 121.17 | 0.16937 | 121.1609 | 120.108 | -121.2433 | -1.2955 | 121.0602 | 120.0073 | 107.5699 | 120.0165
2927.1719 | 121.1609 | -119.9799 | 1.2222 | -0.0060272 | 0.0005619 | 0.11052 | 0.056471 | -0.018154 | 0.056394 | 0.051712 | -0.0051575 | 0.003012 | -0.0098802 | -0.0035183 | -0.021414 | 0.0070496 | -0.01766 | -12.8952 | 1.1673 | -120.0073 | 1.0208 | -114.8117 | -119.1559 | -119.4946 | -0.027466 | 0.086975 | -0.073242 | -0.032043 | 0.050354 | -0.050354 | 0.032043 | -0.027466 | -0.054932 | -0.20142 | 5.1682 | 0.48523 | 0.82397 | 0.51269 | 0.85144 | 119.9066 | -1.1353 | -1.2543 | 120.0302 | 120.0119 | 119.9295 | 0.10529 | 0.022888 | 5.1956 | 121.0281 | 0.1236 | 0.041199 | 121.1746 | 0.16022 | 121.1472 | 120.0668 | -121.2296 | -1.2955 | 121.0007 | 119.9478 | 107.0847 | 119.9524
2928.875 | 121.3531 | -119.9524 | 1.1856 | -0.013657 | 0.0014163 | 0.059248 | 0.053053 | -0.0010638 | -0.0059835 | -0.0019077 | 0.0009461 | 0.010916 | 0.0018692 | -0.0030911 | -0.015432 | 0.021576 | -0.0001432 | -11.2747 | 1.1353 | -120.0668 | 1.0437 | -114.8987 | -119.3985 | -119.5404 | 0.036621 | 0.050354 | -0.082397 | 0.027466 | 0.16022 | 0.068665 | 0.10529 | -0.11444 | -0.050354 | -0.14191 | 5.0537 | 0.41199 | 0.55389 | 0.52643 | 0.66833 | 119.87 | -1.1353 | -1.1581 | 120.1126 | 120.0577 | 120.0211 | 0.18768 | 0.15106 | 5.1682 | 121.1105 | 0.24261 | 0.10986 | 121.2021 | 0.13275 | 121.0876 | 120.0027 | -121.2524 | -1.268 | 120.9961 | 119.9799 | 108.6777 | 119.989
2930.6406 | 121.344 | -119.9524 | 1.1948 | -0.21965 | -0.0011471 | 0.060316 | 0.05348 | 0.00064519 | -0.0036337 | -0.0014805 | -0.0051575 | 0.010702 | 0.0040054 | 0.00054052 | -0.016287 | 0.020508 | -0.0014248 | -10.2448 | 1.1398 | -120.0394 | 1.0574 | -114.7842 | -119.3802 | -119.4992 | 0.059509 | 0.036621 | -0.059509 | 0.054932 | 0.17395 | 0.07782 | 0.11444 | -0.086975 | -0.054931 | -0.13733 | 5.1682 | 0.45319 | 0.5722 | 0.54016 | 0.65918 | 119.8929 | -1.1581 | -1.1398 | 120.1263 | 120.0668 | 120.0302 | 0.17395 | 0.13733 | 5.2551 | 121.0968 | 0.23346 | 0.11444 | 121.1792 | 0.09613 | 121.0922 | 119.989 | -121.2341 | -1.2543 | 121.0098 | 120.0073 | 109.7076 | 120.0119
2932.4062 | 121.344 | -119.9249 | 1.1948 | -0.12047 | -7.9104e-05 | 0.06053 | 0.053053 | -0.0019184 | -0.0064109 | 0.00022853 | -0.0051575 | 0.010702 | 0.001442 | -0.0033047 | -0.016073 | 0.022003 | 7.04e-05 | -9.2331 | 1.1124 | -119.9844 | 1.149 | -114.5828 | -119.2703 | -119.426 | 0.13275 | 0.045776 | -0.050354 | 0.07782 | 0.20599 | 0.12817 | 0.14191 | -0.059509 | -0.082397 | -0.045776 | 5.3421 | 0.49896 | 0.6546 | 0.55847 | 0.71411 | 119.8746 | -1.149 | -1.1169 | 120.1309 | 120.0668 | 120.0531 | 0.19226 | 0.17853 | 5.4016 | 121.1334 | 0.25635 | 0.12817 | 121.0968 | 0.09613 | 121.0373 | 119.9707 | -121.1792 | -1.2451 | 121.0739 | 120.0027 | 110.6918 | 120.0577
2934.1719 | 121.344 | -119.9249 | 1.2085 | -0.52483 | -0.0011471 | 0.062666 | 0.051558 | -0.00042301 | -0.0068381 | -0.0027621 | -0.0051575 | 0.01113 | 0.0010146 | 0.0024631 | -0.016287 | 0.020508 | -0.0029202 | -8.6426 | 1.1124 | -119.8425 | 1.1353 | -114.5142 | -119.252 | -119.426 | 0.11444 | 0.027466 | -0.045776 | 0.068665 | 0.21973 | 0.10986 | 0.13733 | 0.082398 | -0.09613 | -0.073242 | 5.4108 | 0.49896 | 0.67291 | 0.41657 | 0.59051 | 119.8792 | -1.181 | -1.1398 | 120.1447 | 120.0623 | 120.0348 | 0.18311 | 0.15564 | 5.3284 | 120.9778 | 0.2655 | 0.11444 | 120.9549 | 0.073242 | 121.0373 | 119.9524 | -121.051 | -1.2543 | 121.0602 | 119.9936 | 111.2823 | 120.0394
2935.9375 | 121.3028 | -119.9158 | 1.2039 | 0.0016023 | 0.0016299 | 0.061385 | 0.05284 | -0.0053362 | -0.0053427 | -0.0010531 | -0.0082093 | 0.009848 | 0.0018692 | 0.0071627 | -0.015859 | 0.023285 | -0.0005704 | -7.9468 | 1.1398 | -120.0256 | 1.062 | -114.5279 | -119.3253 | -119.4626 | 0.036621 | 0.059509 | -0.064087 | 0.036621 | 0.14648 | 0.073242 | 0.10986 | -0.10986 | -0.064086 | -0.14191 | 5.3879 | 0.45319 | 0.59052 | 0.56305 | 0.70038 | 119.8517 | -1.1444 | -1.1673 | 120.0623 | 120.0256 | 119.989 | 0.17395 | 0.13733 | 5.4977 | 121.0876 | 0.21057 | 0.10071 | 121.1655 | 0.1236 | 121.0556 | 119.9753 | -121.2296 | -1.268 | 120.9778 | 119.9524 | 111.969 | 119.9524
2937.6406 | 121.3028 | -119.8883 | 1.2085 | -0.013657 | -7.9104e-05 | 0.12248 | 0.050703 | -0.0027728 | -0.0051291 | -0.0023349 | -0.0051575 | 0.010916 | 0.00058743 | -0.0011685 | -0.016287 | 0.020081 | -0.0001432 | -7.6355 | 1.1444 | -119.6548 | 1.0712 | -114.4318 | -119.339 | -119.4489 | 0.041199 | 0.059509 | -0.054932 | 0.036621 | 0.16937 | 0.07782 | 0.11902 | 0.23346 | -0.064087 | -0.13733 | 5.4565 | 0.43945 | 0.54932 | 0.20599 | 0.31586 | 119.8334 | -1.149 | -1.1719 | 120.0577 | 120.0073 | 119.9661 | 0.17395 | 0.13275 | 5.2231 | 120.726 | 0.22431 | 0.091553 | 120.7993 | 0.11444 | 121.0327 | 119.9478 | -120.8633 | -1.2634 | 120.9595 | 119.9249 | 112.2528 | 119.9295
2939.4062 | 121.2158 | -119.6594 | 1.4282 | 0.17708 | -7.9104e-05 | 0.75032 | 0.050276 | -0.0023456 | -0.0051291 | 0.0010831 | -0.0021057 | 0.014975 | 0.0027236 | 0.0048129 | -0.014578 | 0.021149 | -0.0037748 | -9.0363 | 1.3275 | -119.3436 | 1.3367 | -114.0244 | -118.9362 | -119.101 | 0.068665 | 0.073242 | -0.064087 | 0.018311 | 0.13733 | 0.045776 | 0.086975 | 0.31586 | -0.10071 | -0.091553 | 5.6351 | 0.55847 | 0.72327 | 0.24261 | 0.40741 | 119.5953 | -1.355 | -1.4099 | 119.7968 | 119.7464 | 119.7052 | 0.15106 | 0.10986 | 5.3192 | 120.6802 | 0.20142 | 0.082398 | 120.6711 | 0.13733 | 120.9869 | 119.7327 | -120.7718 | -1.4923 | 120.9961 | 119.6777 | 110.6232 | 119.7281
2941.1562 | 121.5271 | -0.68207 | 120.5338 | -0.013657 | 0.0012027 | 0.044081 | 0.054121 | 0.0027814 | -0.0057699 | -0.0025485 | -0.0021057 | 0.010275 | 0.0018692 | -0.0050137 | -0.015432 | 0.020294 | -0.0031338 | 0.79651 | 120.4742 | -0.79193 | 120.4239 | 0.85602 | -0.37079 | -0.24719 | 0.050354 | -0.17853 | 0.3067 | 0.032043 | 0.14648 | 0.07782 | 0.10529 | -0.10986 | -0.059509 | -0.10986 | 1.5381 | 0.43488 | 0.31128 | 0.54474 | 0.42114 | 0.98877 | -120.7123 | -120.5017 | 0.82855 | 0.78735 | 0.75989 | -0.20142 | -0.22888 | 1.6479 | 121.2158 | -0.16022 | -0.27466 | 121.2662 | -0.48523 | 121.1563 | 0.50354 | -121.3257 | -120.2271 | 121.106 | 0.71411 | 1.4786 | 0.73242
2942.9062 | 121.6278 | -0.45776 | 120.8954 | -0.013657 | 0.0039799 | 0.049635 | 0.054549 | 0.0038494 | -0.0079061 | -0.0025485 | -0.0051575 | 0.012198 | 0.0012282 | 0.0071627 | -0.017141 | 0.023926 | -0.0014248 | 0.80566 | 120.8679 | -0.58594 | 120.7809 | 1.0574 | -0.22888 | -0.10529 | 0.054932 | 0.041199 | 0.16022 | 0.082397 | 0.045776 | -0.18768 | -0.14648 | -0.12817 | -0.027466 | -0.11444 | 1.5152 | 0.35248 | 0.22888 | 0.48065 | 0.35706 | 0.61798 | -120.8542 | -120.813 | 0.50354 | 0.31128 | 0.27008 | -0.3067 | -0.3479 | 1.6434 | 121.3669 | -0.11444 | -0.07782 | 121.4539 | -0.11902 | 121.3257 | 0.49896 | -121.4813 | -120.7352 | 121.2387 | 0.54016 | 1.2634 | 0.5127
2944.6094 | 115.9332 | -0.22888 | 115.8691 | -0.0060272 | 0.0037661 | 0.05348 | 0.039168 | -0.019222 | -0.016665 | -0.0048985 | -0.11197 | 0.010916 | -0.0077438 | 0.0052401 | 0.26676 | 0.03952 | -0.0016384 | 0.79193 | 116.9952 | -0.32501 | 111.5845 | 1.1856 | -1.1398 | -0.43945 | 0.041199 | -0.013733 | 0.26093 | 0.032043 | -0.2243 | 0.09613 | 0.11902 | -0.09613 | 1.1261 | -4.2847 | 1.4145 | -0.21057 | -0.91095 | -0.11444 | -0.81482 | 0.48981 | -115.8829 | -115.8371 | 0.004578 | 0.3479 | 0.32501 | -0.14191 | -0.1648 | 1.5106 | 111.9095 | -0.48523 | -0.22888 | 117.3203 | -0.27466 | 117.2241 | 0.21515 | -116.1942 | -115.6082 | 111.8134 | 0.26093 | 1.0208 | 0.27008
2946.375 | 120.9961 | -0.59967 | 120.4514 | -0.013657 | 0.0014163 | 0.048354 | 0.051131 | -0.0096088 | -0.022433 | -0.017288 | -0.10281 | -0.00019216 | -0.00090797 | -0.010995 | -0.028463 | 0.0057678 | -0.013601 | 0.99335 | 120.4056 | -0.66376 | 119.5587 | 1.0162 | -0.42114 | -0.35248 | -0.068665 | 0.086975 | 0.009155 | -0.027466 | -0.07782 | -0.41199 | 0.059509 | -0.064087 | -0.045776 | -0.89264 | 1.6159 | 0.24719 | 0.17853 | 0.31128 | 0.24261 | 0.60883 | -120.3644 | -120.4788 | 0.52185 | 0.65918 | 0.18768 | 0.050354 | -0.42114 | 1.68 | 120.2225 | -0.086975 | -0.036621 | 121.0693 | 0.07782 | 121.0052 | 0.68665 | -121.1151 | -120.4422 | 120.1584 | 0.5722 | 1.593 | 0.53101
2948.1406 | 121.1472 | -0.52643 | 120.5292 | -0.013657 | 0.0046207 | 0.049422 | 0.051131 | -0.016445 | -0.019228 | -0.0061801 | -0.12418 | -0.0042512 | -0.0045396 | -0.010568 | 0.14521 | 0.038452 | 0.031687 | 0.9201 | 120.5795 | -0.58136 | 119.8334 | 1.2314 | -0.27008 | -0.26093 | 0.036621 | 0.091553 | 0 | 0.018311 | -0.009155 | -0.26093 | 0.10071 | -0.054932 | 0.050354 | -0.6958 | 1.7578 | 0.2655 | 0.25635 | 0.32043 | 0.31128 | 0.52643 | -120.4376 | -120.5109 | 0.51727 | 0.62714 | 0.2655 | 0.10071 | -0.26093 | 1.8127 | 120.4147 | -0.009155 | 0.018311 | 121.1609 | 0.091553 | 121.106 | 0.61798 | -121.1105 | -120.5292 | 120.3598 | 0.54474 | 1.4465 | 0.56305
2949.8438 | 121.2158 | -0.52643 | 120.7764 | 0.0016023 | 0.0031253 | 0.061385 | 0.053694 | 0.002995 | -0.010683 | -0.0019077 | -0.0051575 | 0.010916 | 0.0029372 | 0.0039585 | -0.016073 | 0.021362 | 0.0004978 | 0.89722 | 120.3369 | -0.54474 | 120.5063 | 1.3229 | -0.16022 | -0.050354 | -0.022888 | 0.07782 | -0.073242 | -0.041199 | 0.054932 | -0.054932 | -0.16022 | -0.018311 | -0.43945 | -0.27008 | 1.8494 | 0.47607 | 0.36621 | 0.49438 | 0.38452 | 0.45319 | -120.6985 | -120.8176 | 0.58136 | 0.36621 | 0.4715 | -0.086975 | 0.01831 | 1.8677 | 121.051 | 0.12817 | 0.032043 | 120.8817 | 0.15106 | 120.8633 | 0.60425 | -121.3211 | -120.8496 | 121.0327 | 0.48523 | 1.4236 | 0.50354
2951.6094 | 120.8267 | -0.52643 | 120.8405 | -0.013657 | -0.0024289 | 0.047285 | 0.058821 | -0.016017 | -0.026064 | -0.010239 | -0.038727 | 0.0051482 | 0.004219 | -0.00010048 | -0.015646 | 0.014526 | -0.0044156 | 0.86517 | 120.7947 | -0.57678 | 119.9936 | 1.3184 | -0.22888 | -0.14648 | -0.045776 | 0.07782 | -0.07782 | -0.041199 | 0.022888 | -0.19226 | -0.28381 | -0.050354 | -0.045776 | -0.84686 | 1.8448 | 0.37994 | 0.29755 | 0.4303 | 0.3479 | 0.44861 | -120.7626 | -120.8817 | 0.54932 | 0.24262 | 0.33417 | -0.20599 | -0.11444 | 1.8951 | 120.5704 | 0.10071 | 0.036621 | 121.3715 | 0.15564 | 121.3211 | 0.60425 | -121.4172 | -120.9183 | 120.52 | 0.48523 | 1.3916 | 0.48065
2953.375 | 120.8771 | -0.48065 | 120.7993 | -0.021286 | 0.0016299 | 0.046431 | 0.057112 | -0.0091816 | -0.019869 | -0.016007 | -0.060089 | -0.0012604 | -0.0079574 | -0.0062955 | -0.030599 | 0.018585 | -0.014669 | 0.93842 | 120.7626 | -0.55389 | 119.8791 | 1.4603 | -0.11902 | -0.10071 | 0.045776 | 0.068665 | -0.064087 | 0.013733 | 0.11444 | -0.16937 | -0.16479 | -0.073242 | -0.036621 | -0.92011 | 1.9409 | 0.37994 | 0.36163 | 0.45319 | 0.43488 | 0.41657 | -120.7306 | -120.7855 | 0.59509 | 0.31586 | 0.31128 | -0.10071 | -0.10529 | 2.0142 | 120.433 | 0.17853 | 0.07782 | 121.3165 | 0.13275 | 121.2433 | 0.54932 | -121.3531 | -120.8633 | 120.3598 | 0.49439 | 1.4191 | 0.52643
2955.1406 | 121.4218 | -0.46692 | 120.8771 | -0.0060272 | 0.0031253 | 0.06523 | 0.057112 | 0.0019268 | -0.0061971 | -0.00083947 | -0.0021057 | 0.010275 | 0.00016023 | -0.0018093 | -0.0165 | 0.021362 | -0.000784 | 0.9613 | 120.7947 | -0.5127 | 120.7581 | 1.6067 | -0.054932 | 0.064087 | 0.11444 | 0.041199 | -0.036621 | 0.073242 | 0.17853 | 0.07782 | 0.12817 | -0.045776 | -0.082397 | -0.11902 | 2.0737 | 0.53101 | 0.41199 | 0.57678 | 0.45776 | 0.4303 | -120.8359 | -120.8038 | 0.64545 | 0.59509 | 0.54474 | 0.1648 | 0.11444 | 2.1194 | 121.2708 | 0.21515 | 0.10986 | 121.3074 | 0.07782 | 121.2616 | 0.50812 | -121.3898 | -120.9137 | 121.225 | 0.54016 | 1.4282 | 0.58136
2956.8906 | 121.0373 | -0.48065 | 120.7672 | 0.0016023 | 0.0048343 | 0.064162 | 0.053908 | -0.0034136 | -0.0089743 | -0.0034031 | -0.0051575 | 0.011343 | 0.0012282 | -0.0052273 | -0.014791 | 0.02179 | -0.0031338 | 1.0666 | 120.4926 | -0.49896 | 120.8176 | 1.6525 | -0.027466 | 0.10529 | 0.059509 | 0.059509 | -0.054932 | 0.018311 | 0.14648 | 0.050354 | 0.091553 | -0.01831 | -0.27466 | 0.050354 | 2.1332 | 0.58594 | 0.45319 | 0.60425 | 0.4715 | 0.42572 | -120.7077 | -120.7489 | 0.62714 | 0.57221 | 0.53101 | 0.14649 | 0.10529 | 2.1515 | 121.3165 | 0.20142 | 0.073243 | 120.9915 | 0.11444 | 120.9732 | 0.54016 | -121.2662 | -120.8221 | 121.2982 | 0.49896 | 1.5472 | 0.54016
2958.5938 | 120.9091 | -0.48981 | 120.4834 | -0.0060272 | 0.0063297 | 0.06288 | 0.057753 | 0.0017132 | -0.0070517 | -0.00083947 | -0.0021057 | 0.011557 | 0.0022964 | 0.00075412 | -0.01351 | 0.022217 | -0.0048428 | 1.0254 | 120.8862 | -0.54932 | 120.7535 | 1.5976 | -0.15564 | -0.009155 | 0.009155 | 0.073242 | -0.059509 | 0.054932 | 0.13733 | 0.050354 | 0.12817 | -0.059509 | 0.40283 | 0.27008 | 2.0874 | 0.48065 | 0.33417 | 0.54016 | 0.39368 | 0.4303 | -120.4102 | -120.4285 | 0.62714 | 0.61798 | 0.54016 | 0.18768 | 0.10986 | 2.1469 | 121.3028 | 0.19684 | 0.11444 | 121.4355 | 0.13275 | 121.376 | 0.56305 | -121.0327 | -120.5429 | 121.2433 | 0.54474 | 1.5152 | 0.49896
2960.2969 | 120.8176 | -0.4715 | 120.7626 | -0.028916 | 0.0003483 | 0.063734 | 0.056044 | -0.0034136 | -0.0081197 | -0.0014805 | 0.0009461 | 0.012625 | 0.00016023 | 0.0013949 | -0.015219 | 0.021362 | -0.0031338 | 1.062 | 120.607 | -0.50812 | 120.8496 | 1.7349 | -0.013733 | 0.10529 | 0.054932 | 0.073242 | -0.073242 | -0.009155 | 0.11444 | 0.018311 | 0.064087 | -0.036621 | -0.15564 | 0.086975 | 2.2064 | 0.57678 | 0.45776 | 0.6134 | 0.49438 | 0.39826 | -120.6894 | -120.7718 | 0.58594 | 0.53558 | 0.48981 | 0.13733 | 0.091553 | 2.243 | 121.3577 | 0.18768 | 0.064087 | 121.1151 | 0.14648 | 121.0785 | 0.54474 | -121.2708 | -120.8359 | 121.3211 | 0.46234 | 1.5335 | 0.52643
2962.0469 | 121.4035 | -0.42114 | 121.0098 | -0.013657 | 0.0024845 | 0.064589 | 0.058394 | -0.0040546 | -0.0068381 | -0.0023349 | -0.0051575 | 0.012625 | 0.0029372 | 0.0022495 | -0.016928 | 0.020508 | 0.0013522 | 1.0529 | 120.9274 | -0.49439 | 120.8633 | 1.7807 | -0.018311 | 0.13275 | 0.059509 | 0.032043 | -0.059509 | 0.027466 | 0.14648 | 0.036621 | 0.10071 | -0.073242 | -0.082398 | -0.14648 | 2.2018 | 0.55389 | 0.40283 | 0.62714 | 0.47607 | 0.36163 | -120.9778 | -120.9824 | 0.56763 | 0.52185 | 0.45776 | 0.16022 | 0.09613 | 2.2751 | 121.3577 | 0.20599 | 0.086975 | 121.4218 | 0.091552 | 121.3486 | 0.45319 | -121.5042 | -121.0693 | 121.2845 | 0.44861 | 1.474 | 0.48065
2963.8125 | 120.7581 | -0.46692 | 120.4834 | -0.32646 | 0.0033389 | 0.065657 | 0.055617 | 0.0017132 | -0.0091879 | 0.0012967 | -0.0021057 | 0.013266 | 0.0037918 | 0.0020359 | -0.015219 | 0.020935 | -0.0031338 | 1.0345 | 120.1904 | -0.48523 | 120.8817 | 1.8265 | -0.013733 | 0.10986 | -0.018311 | 0.073242 | -0.082397 | -0.036621 | 0.07782 | -0.018311 | 0.032043 | -0.01831 | -0.29297 | 0.39826 | 2.2934 | 0.57678 | 0.45319 | 0.59509 | 0.4715 | 0.38452 | -120.4102 | -120.52 | 0.54474 | 0.49896 | 0.44861 | 0.11444 | 0.064086 | 2.3117 | 121.3669 | 0.16022 | 0.045776 | 120.6757 | 0.15564 | 120.6573 | 0.54016 | -120.9686 | -120.5658 | 121.3486 | 0.4303 | 1.5015 | 0.44861
2965.5625 | 109.5978 | -0.38452 | 120.3873 | -0.021286 | -0.01311 | 0.047072 | 0.051772 | -0.010036 | -0.023074 | -0.017929 | -0.0051575 | -0.0033966 | -0.013512 | -0.01249 | -0.022055 | 0.016876 | -0.0084744 | 1.0574 | 120.4559 | -0.54016 | 120.813 | 1.8768 | -0.045776 | 0.07782 | 0.050354 | 0.068665 | -0.082397 | 0.004578 | 0.1236 | 0.022888 | -0.022888 | -0.15564 | 0.068665 | 0.42572 | 2.2614 | 0.46234 | 0.33875 | 0.61798 | 0.49439 | 0.30212 | -120.3186 | -120.3827 | 0.50812 | 0.36163 | 0.40741 | 0.059509 | 0.10528 | 2.417 | 121.3531 | 0.20599 | 0.086975 | 120.9961 | 0.15106 | 120.8405 | 0.45319 | -120.9274 | -120.4697 | 121.1975 | 0.3891 | 1.442 | 0.43488
2967.3125 | 120.8633 | -0.50354 | 121.0419 | -0.33409 | 0.0009891 | 0.065657 | 0.057326 | 0.00021799 | -0.0081197 | -0.00062587 | -0.0051575 | 0.011984 | 0.001442 | -0.00095488 | -0.015432 | 0.020721 | -0.0029202 | 1.0529 | 120.4834 | -0.50812 | 120.9 | 1.9409 | -0.004578 | 0.10986 | -0.004578 | 0.082397 | -0.09613 | -0.054932 | 0.091553 | -0.009155 | 0.036621 | -0.004578 | -0.55847 | -0.14191 | 2.4445 | 0.6134 | 0.49896 | 0.61798 | 0.50354 | 0.40741 | -120.9595 | -121.0968 | 0.59509 | 0.54016 | 0.49438 | 0.13275 | 0.086975 | 2.449 | 121.4081 | 0.18768 | 0.041198 | 120.9915 | 0.17853 | 120.9869 | 0.58594 | -121.55 | -121.138 | 121.4035 | 0.44861 | 1.5564 | 0.49896
2969.0781 | 120.9778 | -0.48065 | 120.3735 | -0.013657 | -0.0079831 | 0.047713 | 0.059676 | -0.0029864 | -0.018374 | -0.0070347 | -0.0051575 | 0.013693 | 0.0010146 | 0.010367 | -0.017141 | 0.023499 | 0.0011386 | 0.96588 | 121.0556 | -0.52643 | 120.8359 | 1.8906 | -0.10529 | 0.036621 | -0.041199 | 0.082397 | -0.091553 | -0.041199 | 0.041199 | -0.054932 | 0.036621 | -0.045776 | 0.68207 | 0.46234 | 2.3712 | 0.51727 | 0.37537 | 0.56305 | 0.42114 | 0.3891 | -120.2911 | -120.4147 | 0.52185 | 0.51727 | 0.42572 | 0.12817 | 0.036621 | 2.417 | 121.3623 | 0.13275 | 0.050354 | 121.582 | 0.17395 | 121.5363 | 0.56305 | -120.9 | -120.4651 | 121.3165 | 0.43945 | 1.4465 | 0.43945
2970.8438 | 121.4996 | -0.45776 | 121.1105 | -0.13573 | 0.0026981 | 0.065871 | 0.057112 | 0.00064519 | -0.0070517 | -0.00062587 | 0.0009461 | 0.012411 | 0.003151 | 0.0060947 | -0.015646 | 0.020081 | -0.0046292 | 1.0803 | 121.0236 | -0.50354 | 120.9824 | 2.124 | 0.022888 | 0.17395 | 0.10986 | 0.036621 | -0.054932 | 0.07782 | 0.17853 | 0.07782 | 0.13275 | -0.045776 | -0.086975 | -0.12817 | 2.5818 | 0.63171 | 0.48065 | 0.67749 | 0.52643 | 0.40283 | -121.0739 | -121.0327 | 0.63629 | 0.59052 | 0.53558 | 0.18768 | 0.13275 | 2.6276 | 121.4859 | 0.23346 | 0.13275 | 121.5271 | 0.091553 | 121.4813 | 0.49439 | -121.6141 | -121.1655 | 121.4401 | 0.53558 | 1.5381 | 0.56763
2972.6094 | 121.8109 | -0.43945 | 120.6848 | 0.15419 | 0.029401 | 0.11073 | 0.056471 | 0.046147 | 0.058744 | 0.052353 | -0.0021057 | -0.00040596 | -0.0021896 | -0.0071499 | -0.021414 | 0.0064088 | -0.008688 | 1.1169 | 121.051 | -0.54016 | 120.6436 | 2.0554 | -0.064087 | 0.064087 | -0.036621 | 0.064087 | -0.086975 | -0.054932 | 0.054932 | -0.045776 | 0.032043 | -0.10071 | 0.36621 | -0.041198 | 2.4948 | 0.50354 | 0.37537 | 0.60425 | 0.47607 | 0.35248 | -120.6207 | -120.7397 | 0.49438 | 0.4715 | 0.39368 | 0.11902 | 0.041199 | 2.5955 | 121.1838 | 0.14191 | 0.032043 | 121.5912 | 0.15106 | 121.4905 | 0.50354 | -121.225 | -120.7718 | 121.0831 | 0.38452 | 1.5564 | 0.40283
2974.3594 | 121.6873 | -0.45319 | 121.138 | -0.27306 | 0.0029117 | 0.066725 | 0.054976 | -0.0051226 | -0.0061971 | 0.00044213 | -0.0051575 | 0.0092072 | 0.0061416 | 0.00032692 | -0.015432 | 0.019226 | -0.0014248 | 1.1856 | 121.0373 | -0.48981 | 121.0236 | 2.2476 | 0.10986 | 0.21973 | 0.11444 | 0.041199 | -0.054932 | 0.064087 | 0.20599 | 0.11902 | 0.15106 | -0.036621 | -0.10071 | -0.11444 | 2.7008 | 0.67291 | 0.56305 | 0.70953 | 0.59967 | 0.39825 | -121.0968 | -121.0739 | 0.65918 | 0.60425 | 0.5722 | 0.20599 | 0.17395 | 2.7374 | 121.5134 | 0.26093 | 0.11902 | 121.5271 | 0.096131 | 121.4905 | 0.49438 | -121.6278 | -121.1929 | 121.4767 | 0.51727 | 1.6388 | 0.56763
2976.0781 | 121.7285 | -0.45319 | 120.9457 | -0.21965 | 0.0001345 | 0.065871 | 0.056258 | -0.0032 | -0.0061971 | 0.0017239 | -0.0021057 | 0.011343 | 0.003151 | 0.0078037 | -0.016287 | 0.02243 | 0.0002842 | 1.149 | 121.0739 | -0.49896 | 120.9961 | 2.2614 | 0.091553 | 0.21973 | 0.068665 | 0.041199 | -0.059509 | 0.041199 | 0.18768 | 0.10071 | 0.13733 | -0.045776 | 0.12817 | 0.050354 | 2.7145 | 0.67291 | 0.54474 | 0.71869 | 0.59052 | 0.39368 | -120.9045 | -120.9045 | 0.64087 | 0.59052 | 0.55389 | 0.19684 | 0.16022 | 2.7603 | 121.4951 | 0.24719 | 0.10071 | 121.5729 | 0.10071 | 121.5271 | 0.49438 | -121.4447 | -121.0052 | 121.4493 | 0.49438 | 1.6022 | 0.52185
2977.8281 | 121.1609 | -0.46234 | 121.0144 | -0.13573 | 0.025769 | 0.11116 | 0.057539 | -0.015377 | 0.055967 | 0.044235 | 0.0039977 | 0.0027984 | -0.0090256 | 0.0048129 | -0.013937 | 0.01239 | 7.04e-05 | 1.2863 | 121.1288 | -0.54474 | 120.8862 | 2.1744 | -0.032043 | 0.082397 | -0.09613 | 0.07782 | -0.09613 | -0.054932 | 0.032043 | -0.064087 | 0.032043 | -0.082398 | 0.11444 | -0.12817 | 2.6367 | 0.54474 | 0.4303 | 0.62714 | 0.5127 | 0.36621 | -120.9366 | -121.0693 | 0.49438 | 0.49438 | 0.39825 | 0.12817 | 0.032043 | 2.7191 | 121.431 | 0.12817 | 0.041198 | 121.6736 | 0.17395 | 121.5912 | 0.54016 | -121.5591 | -121.1105 | 121.3486 | 0.40741 | 1.7487 | 0.36621
2979.5938 | 121.7194 | -0.4715 | 120.9229 | -0.0060272 | 0.0046207 | 0.068434 | 0.056258 | -0.00020941 | -0.0061971 | -0.0016941 | -0.0082093 | 0.010702 | 0.0027236 | 0.00075412 | -0.015432 | 0.022003 | 0.0013522 | 1.3504 | 121.0876 | -0.52185 | 120.9915 | 2.3392 | 0.082397 | 0.1831 | 0.018311 | 0.054932 | -0.059509 | 0.013733 | 0.13733 | 0.064087 | 0.11444 | -0.050354 | 0.16479 | 0.068664 | 2.8107 | 0.6546 | 0.55389 | 0.70496 | 0.60425 | 0.41199 | -120.8679 | -120.9091 | 0.60883 | 0.58594 | 0.53558 | 0.17395 | 0.1236 | 2.861 | 121.5134 | 0.19684 | 0.073242 | 121.6095 | 0.11444 | 121.5591 | 0.52643 | -121.4447 | -120.9824 | 121.463 | 0.48523 | 1.8219 | 0.48981
2981.3438 | 121.7102 | -0.50354 | 121.138 | -0.15862 | 0.0029117 | 0.064375 | 0.057326 | -0.00042301 | -0.0055563 | -0.0012669 | -0.0051575 | 0.01113 | 0.0037918 | -0.0020231 | -0.016287 | 0.020508 | -0.0050564 | 1.5427 | 121.0785 | -0.53558 | 121.0098 | 2.4078 | 0.068665 | 0.20142 | 0.059509 | 0.045776 | -0.054932 | 0.045776 | 0.13275 | 0.045776 | 0.09613 | -0.032043 | -0.059509 | -0.12817 | 2.9114 | 0.70496 | 0.5722 | 0.737 | 0.60425 | 0.44861 | -121.0922 | -121.0922 | 0.63629 | 0.59967 | 0.54932 | 0.15106 | 0.10071 | 2.9434 | 121.5454 | 0.18768 | 0.10071 | 121.6141 | 0.10071 | 121.582 | 0.54932 | -121.6736 | -121.1929 | 121.5134 | 0.54932 | 2.0462 | 0.56305
2983.0938 | 121.7285 | -0.52185 | 120.8267 | 0.0016023 | 0.0052615 | 0.064589 | 0.057539 | -0.0012774 | -0.0053427 | 1.4934e-05 | -0.0021057 | 0.010916 | 0.0029372 | 0.0031039 | -0.016073 | 0.021362 | -0.0014248 | 1.6159 | 121.0419 | -0.57678 | 120.9778 | 2.4307 | 0.050354 | 0.17853 | 0.032043 | 0.050354 | -0.064087 | 0.027466 | 0.15106 | 0.068665 | 0.10529 | -0.054931 | 0.21515 | 0.15106 | 2.9526 | 0.70038 | 0.5722 | 0.75531 | 0.62714 | 0.45776 | -120.7764 | -120.7993 | 0.67291 | 0.62714 | 0.59052 | 0.16937 | 0.13275 | 3.0075 | 121.5546 | 0.21515 | 0.091553 | 121.6187 | 0.11444 | 121.5637 | 0.5722 | -121.4035 | -120.8908 | 121.4996 | 0.54932 | 2.1378 | 0.55389
2984.8594 | 120.9549 | -0.59052 | 120.8221 | -0.46379 | 0.0054751 | 0.064375 | 0.059676 | 0.0021406 | -0.0072653 | 0.00086953 | -0.0021057 | 0.011771 | 0.0027236 | 0.0024631 | -0.015005 | 0.020935 | -0.0033474 | 1.5106 | 121.2021 | -0.61798 | 120.9183 | 2.4216 | 0.004578 | 0.091553 | -0.054932 | 0.07782 | -0.07782 | -0.064087 | 0.059509 | -0.022888 | 0.036621 | -0.027466 | 0.37994 | 0.09613 | 3.0121 | 0.68207 | 0.59509 | 0.70953 | 0.62256 | 0.5127 | -120.7443 | -120.8862 | 0.65002 | 0.62714 | 0.56763 | 0.11444 | 0.054932 | 3.0396 | 121.5363 | 0.13733 | 0.013733 | 121.8201 | 0.15564 | 121.7926 | 0.66834 | -121.4401 | -120.9 | 121.5088 | 0.52643 | 2.1011 | 0.53558
2986.5625 | 120.9137 | -0.56763 | 120.6848 | -0.5706 | 0.0001345 | 0.10475 | 0.056258 | -0.015163 | -0.016878 | -0.016861 | -0.0021057 | 0.010702 | -0.0068894 | 0.00096772 | -0.015859 | 0.021149 | -0.002493 | 1.6159 | 121.1288 | -0.62256 | 120.9 | 2.4536 | -0.045776 | 0.091553 | -0.068665 | 0.07782 | -0.086975 | -0.041199 | 0.032043 | -0.050354 | 0.050354 | -0.054932 | 0.44403 | 0.21515 | 3.0212 | 0.65918 | 0.52185 | 0.71411 | 0.57678 | 0.48065 | -120.607 | -120.726 | 0.59967 | 0.61798 | 0.51727 | 0.13733 | 0.036621 | 3.0762 | 121.5225 | 0.11902 | 0.045776 | 121.7514 | 0.16479 | 121.6965 | 0.64545 | -121.3074 | -120.7718 | 121.4676 | 0.52643 | 2.1835 | 0.49896
2988.2656 | 121.5637 | -0.54932 | 121.1838 | -0.1281 | 0.0041935 | 0.065016 | 0.057967 | 0.0010724 | -0.0068381 | 0.0032193 | -0.0051575 | 0.012625 | 0.0033646 | -0.0013821 | -0.0165 | 0.021576 | -0.0020658 | 1.6571 | 120.5521 | -0.5722 | 121.0281 | 2.6871 | 0.12817 | 0.23804 | 0.07782 | 0.045776 | -0.050354 | 0.036621 | 0.18768 | 0.091553 | 0.11902 | -0.022889 | -0.63171 | -0.15564 | 3.2364 | 0.78735 | 0.67749 | 0.81024 | 0.70038 | 0.49896 | -121.138 | -121.1472 | 0.737 | 0.66834 | 0.64087 | 0.16937 | 0.14191 | 3.2593 | 121.6003 | 0.23804 | 0.086975 | 121.1243 | 0.09613 | 121.1014 | 0.59509 | -121.756 | -121.2341 | 121.5775 | 0.58594 | 2.2064 | 0.62714
2990.0156 | 121.2387 | -0.54474 | 120.3781 | -0.044174 | 0.0022709 | 0.11116 | 0.051985 | -0.013454 | -0.01047 | 0.051925 | -0.0082093 | 0.0060028 | -0.014793 | -0.0071499 | -0.022055 | 0.017517 | -0.0080472 | 1.6937 | 120.3415 | -0.63629 | 120.8038 | 2.6688 | 0.036621 | 0.16022 | 0.032043 | 0.091553 | -0.073242 | 0.022888 | 0.12817 | 0.032043 | 0.10529 | -0.091553 | -0.036621 | 0.42572 | 3.2135 | 0.70496 | 0.58136 | 0.79651 | 0.67291 | 0.4715 | -120.2866 | -120.3552 | 0.67291 | 0.65002 | 0.57678 | 0.17853 | 0.10529 | 3.3051 | 121.4401 | 0.20142 | 0.09613 | 120.9778 | 0.16479 | 120.8862 | 0.63629 | -121.0144 | -120.4514 | 121.3486 | 0.56763 | 2.2385 | 0.57678
2991.7656 | 120.9595 | -0.59967 | 120.6757 | -0.40276 | -0.0052059 | 0.061812 | 0.060103 | -0.00063661 | -0.0068381 | -0.0074619 | -0.0021057 | 0.01348 | -0.0030442 | 0.0084445 | -0.014791 | 0.015808 | -0.0046292 | 1.6342 | 120.3506 | -0.65002 | 120.7489 | 2.7283 | 0.064087 | 0.15564 | -0.013733 | 0.068665 | -0.07782 | -0.009155 | 0.11444 | 0 | 0.073242 | -0.050354 | -0.32501 | 0.073242 | 3.3279 | 0.75531 | 0.66376 | 0.80566 | 0.71411 | 0.52185 | -120.607 | -120.6848 | 0.71411 | 0.67291 | 0.59967 | 0.15106 | 0.07782 | 3.3783 | 121.3989 | 0.19226 | 0.068665 | 121.0007 | 0.14649 | 120.9503 | 0.66834 | -121.3257 | -120.7535 | 121.3486 | 0.59052 | 2.2339 | 0.58594
2993.5156 | 120.9824 | -0.58136 | 121.0236 | -0.21965 | -0.0047787 | 0.058394 | 0.058394 | -0.017299 | -0.016024 | -0.015793 | -0.0051575 | 0.012198 | -0.0094528 | -0.0018093 | -0.016073 | 0.010681 | -0.006979 | 1.6708 | 120.401 | -0.63629 | 120.5704 | 2.8244 | 0.07782 | 0.16479 | 0.036621 | 0.091553 | -0.07782 | 0 | 0.11902 | 0.018311 | 0.086975 | -0.054932 | -0.62256 | -0.45319 | 3.4058 | 0.74616 | 0.65918 | 0.80109 | 0.71411 | 0.50354 | -120.932 | -121.0236 | 0.70038 | 0.66834 | 0.59967 | 0.16479 | 0.096131 | 3.4607 | 121.2067 | 0.19684 | 0.07782 | 121.0373 | 0.16937 | 120.9824 | 0.67291 | -121.6599 | -121.1014 | 121.1517 | 0.58136 | 2.2522 | 0.61798
2995.2188 | 121.637 | -0.58136 | 121.1975 | -0.28831 | -0.0015743 | 0.065871 | 0.061812 | 0.0027814 | -0.0049155 | 0.00022853 | 0.0009461 | 0.012625 | 0.004219 | -0.0013821 | -0.016073 | 0.022003 | 0.0015658 | 1.6663 | 121.1334 | -0.61798 | 120.8679 | 2.8748 | 0.041199 | 0.15106 | 0.018311 | 0.059509 | -0.059509 | 0.027466 | 0.1236 | 0.032043 | 0.10071 | -0.036621 | -0.064087 | -0.32959 | 3.4561 | 0.73242 | 0.62256 | 0.76904 | 0.65918 | 0.52185 | -121.138 | -121.17 | 0.70496 | 0.68207 | 0.6134 | 0.16022 | 0.091552 | 3.4927 | 121.4859 | 0.1831 | 0.086975 | 121.7514 | 0.11902 | 121.7148 | 0.64087 | -121.8155 | -121.257 | 121.4493 | 0.60883 | 2.2476 | 0.59967
2996.9688 | 121.2982 | -0.60425 | 121.0144 | -0.28831 | 0.0073977 | 0.067366 | 0.06288 | -0.0019184 | -0.0074789 | -0.00019867 | -0.0082093 | 0.015189 | 0.0046462 | 0.0060947 | -0.017141 | 0.022644 | -0.0029202 | 1.6067 | 118.5699 | -0.65002 | 120.7352 | 2.9068 | 0.068665 | 0.16479 | -0.068665 | 0.082397 | -0.10986 | -0.054932 | 0.064087 | -0.018311 | 0.041199 | -0.045776 | -2.4445 | -0.27924 | 3.511 | 0.76904 | 0.67291 | 0.81482 | 0.71869 | 0.49439 | -120.932 | -121.0693 | 0.66834 | 0.64545 | 0.58594 | 0.15106 | 0.091552 | 3.5568 | 121.3852 | 0.17395 | 0.054931 | 119.22 | 0.19226 | 119.1742 | 0.68664 | -121.6644 | -121.1243 | 121.3394 | 0.54932 | 2.211 | 0.53558
2998.7344 | 121.3806 | -0.61798 | 121.1151 | -0.33409 | 0.0003483 | 0.060744 | 0.064589 | -0.010036 | -0.021365 | -0.01323 | -0.0021057 | 0.013266 | -0.0038986 | 0.0056675 | -0.016287 | 0.021149 | 0.0007114 | 1.68 | 121.1746 | -0.64087 | 120.4651 | 2.9343 | 0.022888 | 0.13275 | -0.059509 | 0.07782 | -0.10529 | -0.032043 | 0.036621 | -0.050354 | 0.027466 | -0.022888 | 0.05951 | -0.65002 | 3.5522 | 0.75073 | 0.64087 | 0.77362 | 0.66376 | 0.5127 | -121.0373 | -121.1472 | 0.6546 | 0.64545 | 0.56763 | 0.13275 | 0.054932 | 3.5751 | 121.106 | 0.14191 | 0.073243 | 121.8155 | 0.18311 | 121.7926 | 0.6958 | -121.756 | -121.2204 | 121.0831 | 0.58594 | 2.298 | 0.55847
3000.5 | 121.8292 | -0.53101 | 121.225 | 0.0016023 | 0.0099613 | 0.071425 | 0.058821 | 0.00064519 | -0.0042745 | 0.0015103 | -0.0021057 | 0.011984 | 0.00251 | 0.0037447 | -0.015432 | 0.022217 | 0.0007114 | 1.9638 | 121.1792 | -0.56305 | 121.0968 | 3.2318 | 0.2243 | 0.3479 | 0.082397 | 0.045776 | -0.041199 | 0.036621 | 0.14648 | 0.073242 | 0.10986 | -0.032043 | -0.045777 | -0.12817 | 3.7628 | 0.87891 | 0.75531 | 0.91095 | 0.78735 | 0.48981 | -121.1792 | -121.1884 | 0.67749 | 0.64087 | 0.60425 | 0.15106 | 0.11444 | 3.7949 | 121.6599 | 0.18768 | 0.07782 | 121.7422 | 0.086975 | 121.7102 | 0.57678 | -121.788 | -121.2662 | 121.6278 | 0.56763 | 2.4948 | 0.6134
3002.2031 | 121.9162 | -0.5127 | 121.2616 | -0.23491 | 0.0041935 | 0.068434 | 0.058821 | 0.00043159 | -0.0049155 | 1.4934e-05 | -0.0021057 | 0.010489 | 0.0033646 | 0.0039585 | -0.016287 | 0.021576 | -0.0020658 | 2.0325 | 120.8725 | -0.55389 | 121.1517 | 3.3417 | 0.30212 | 0.41199 | 0.14648 | 0.036621 | -0.054932 | 0.068665 | 0.21057 | 0.13275 | 0.14191 | -0.041199 | -0.3891 | -0.10986 | 3.8544 | 0.92468 | 0.81482 | 0.96588 | 0.85602 | 0.45776 | -121.225 | -121.1929 | 0.72327 | 0.6546 | 0.64545 | 0.19684 | 0.18768 | 3.8956 | 121.7056 | 0.2655 | 0.1236 | 121.4264 | 0.091553 | 121.3852 | 0.54932 | -121.8155 | -121.3165 | 121.6644 | 0.58136 | 2.5452 | 0.65918
3003.9688 | 121.8475 | -0.48065 | 121.2936 | -0.021286 | 0.0056887 | 0.069929 | 0.061812 | -0.0044818 | -0.0059835 | 0.0015103 | -0.0021057 | 0.012411 | 0.0046462 | -0.0035183 | -0.016714 | 0.020508 | -0.0014248 | 2.3941 | 121.2112 | -0.54016 | 121.1014 | 3.2822 | 0.24261 | 0.38452 | 0.018311 | 0.045776 | -0.073242 | 0.018311 | 0.13733 | 0.054932 | 0.10071 | -0.059509 | -0.082397 | -0.19226 | 3.7628 | 0.86517 | 0.72327 | 0.92468 | 0.78278 | 0.40741 | -121.2479 | -121.2753 | 0.61798 | 0.58136 | 0.53558 | 0.17395 | 0.12817 | 3.8223 | 121.6415 | 0.21057 | 0.091553 | 121.7514 | 0.11902 | 121.6919 | 0.52643 | -121.8338 | -121.3669 | 121.582 | 0.49896 | 2.8748 | 0.49896
3005.6875 | 121.0922 | -0.54932 | 121.2662 | -0.0060272 | -0.0054197 | 0.062453 | 0.051558 | -0.015163 | -0.023928 | -0.0031895 | -0.0051575 | 0.005362 | -0.012444 | -0.018472 | -0.019918 | 0.0053406 | -0.004202 | 2.1973 | 120.4651 | -0.59509 | 120.9732 | 3.3188 | 0.21973 | 0.31586 | 0.027466 | 0.059509 | -0.073242 | 0.013733 | 0.11902 | 0.022888 | 0.086975 | -0.045777 | -0.80109 | -0.29297 | 3.8681 | 0.86517 | 0.76904 | 0.91095 | 0.81482 | 0.47607 | -121.2067 | -121.2524 | 0.66834 | 0.63629 | 0.5722 | 0.16022 | 0.09613 | 3.9139 | 121.5683 | 0.19226 | 0.086975 | 121.0602 | 0.13275 | 121.0144 | 0.60883 | -121.8613 | -121.3394 | 121.5225 | 0.56305 | 2.7466 | 0.57678
3007.4375 | 121.312 | -0.54474 | 121.1929 | -0.26543 | 0.0041935 | 0.072279 | 0.063094 | -0.0032 | -0.0066245 | 0.0038601 | -0.0051575 | 0.013266 | 0.00058743 | 0.0060947 | -0.014791 | 0.021576 | -0.0050564 | 2.2339 | 120.4926 | -0.58594 | 121.051 | 3.3371 | 0.19684 | 0.32044 | -0.064087 | 0.086975 | -0.086975 | -0.050354 | 0.068665 | -0.022888 | 0.036621 | -0.041198 | -0.70038 | -0.14191 | 3.8818 | 0.86517 | 0.74158 | 0.90637 | 0.78277 | 0.45776 | -121.106 | -121.2433 | 0.6134 | 0.58136 | 0.52185 | 0.1236 | 0.064087 | 3.923 | 121.637 | 0.15564 | 0.036621 | 121.0785 | 0.17395 | 121.0373 | 0.63171 | -121.7789 | -121.2799 | 121.5958 | 0.49438 | 2.7786 | 0.48065
3009.1875 | 121.9208 | -0.6958 | 121.106 | 0.16945 | 0.0082523 | 0.06822 | 0.063521 | 0.001286 | -0.0044883 | -0.0012669 | 0.0009461 | 0.011343 | 0.00058743 | 0.0052401 | -0.015432 | 0.022858 | -0.0014248 | 2.124 | 121.0373 | -0.74158 | 120.9595 | 3.3463 | 0.091553 | 0.22888 | 0.11902 | 0.054932 | -0.050354 | 0.082397 | 0.1831 | 0.09613 | 0.14648 | -0.045776 | -0.068665 | -0.14648 | 4.0421 | 0.92468 | 0.78735 | 0.97046 | 0.83313 | 0.64545 | -121.051 | -121.0236 | 0.87891 | 0.84228 | 0.79193 | 0.19684 | 0.14648 | 4.0878 | 121.7011 | 0.23346 | 0.13275 | 121.7789 | 0.10529 | 121.7331 | 0.75073 | -121.8475 | -121.1563 | 121.6553 | 0.7782 | 2.8198 | 0.81482
3010.8906 | 121.2982 | -0.7782 | 120.6573 | -0.013657 | 0.0009891 | 0.11137 | 0.056044 | -0.0096088 | 0.057462 | 0.05278 | 0.0009461 | 0.0089934 | -0.0096664 | -0.010781 | -0.019491 | 0.0089722 | -0.0037748 | 1.8585 | 120.4971 | -0.81024 | 120.52 | 3.2364 | -0.013733 | 0.1236 | -0.036621 | 0.07782 | -0.10529 | -0.032043 | 0.050354 | -0.041199 | 0.041199 | -0.032044 | -0.16022 | -0.13733 | 4.0146 | 0.90179 | 0.76446 | 0.93384 | 0.79651 | 0.67291 | -120.5795 | -120.6894 | 0.82855 | 0.8194 | 0.737 | 0.14649 | 0.064087 | 4.0466 | 121.3303 | 0.15564 | 0.073243 | 121.3074 | 0.18311 | 121.2753 | 0.85602 | -121.4676 | -120.7626 | 121.2982 | 0.74615 | 2.6367 | 0.74158
3012.6406 | 121.4081 | -1.1032 | 120.0577 | 0.0016023 | 0.0078251 | 0.055617 | 0.062025 | 0.0025678 | -0.0066245 | -0.0036167 | -0.0021057 | 0.013266 | 0.00251 | 0.0022495 | -0.015859 | 0.020508 | -0.0012112 | 1.8585 | 120.0394 | -1.1398 | 120.2454 | 2.9251 | -0.32959 | -0.21057 | -0.045776 | 0.07782 | -0.086975 | -0.009155 | 0.10529 | 0.004578 | 0.068665 | -0.036622 | -0.01831 | 0.18768 | 4.0283 | 0.89264 | 0.77362 | 0.92926 | 0.81024 | 1.0162 | -119.9799 | -120.0668 | 1.2085 | 1.1719 | 1.1078 | 0.15564 | 0.091553 | 4.0649 | 121.3852 | 0.19226 | 0.07782 | 121.1792 | 0.16479 | 121.1426 | 1.181 | -121.1975 | -120.1447 | 121.3486 | 1.0941 | 2.9617 | 1.0574
3014.4062 | 121.312 | -1.2039 | 119.9341 | -0.013657 | -0.0034971 | 0.10924 | 0.062025 | -0.012599 | -0.011111 | 0.050216 | -0.0082093 | 0.01412 | -0.0068894 | 0.0039585 | -0.019491 | 0.013886 | -0.0056974 | 2.0187 | 120.3278 | -1.2451 | 119.838 | 2.8656 | -0.43488 | -0.29755 | -0.013733 | 0.086975 | -0.082397 | -0.050354 | 0.054932 | -0.050354 | 0.041199 | -0.041199 | 0.39368 | -0.09613 | 4.0695 | 0.90637 | 0.76904 | 0.94757 | 0.81024 | 1.1215 | -119.8471 | -119.9844 | 1.2589 | 1.2451 | 1.1536 | 0.1236 | 0.032043 | 4.1107 | 121.0831 | 0.13733 | 0.032043 | 121.5729 | 0.16937 | 121.5317 | 1.2909 | -121.1792 | -120.0165 | 121.0419 | 1.1536 | 3.2227 | 1.1902
3016.1719 | 121.907 | -1.1719 | 120.6436 | -0.0060272 | 0.0076113 | 0.052199 | 0.06288 | -0.00085021 | -0.0021383 | 0.0027921 | -0.0082093 | 0.011557 | 0.00080103 | -0.0067227 | -0.0165 | 0.022858 | -0.0003568 | 2.7145 | 120.5658 | -1.2543 | 120.4697 | 2.9251 | -0.37994 | -0.22888 | 0.041199 | 0.054932 | -0.068665 | 0.022888 | 0.12817 | 0.059509 | 0.10986 | -0.082397 | -0.07782 | -0.17395 | 4.097 | 0.94299 | 0.79193 | 1.0254 | 0.87433 | 1.1032 | -120.5887 | -120.6207 | 1.3 | 1.2817 | 1.2314 | 0.17853 | 0.12817 | 4.1794 | 121.7239 | 0.19684 | 0.091553 | 121.8201 | 0.1236 | 121.7377 | 1.2268 | -121.8979 | -120.7123 | 121.6415 | 1.1948 | 3.8864 | 1.2131
3017.8594 | 121.9391 | -1.2085 | 120.639 | -0.028916 | 0.0050479 | 0.051771 | 0.06288 | -0.00042301 | -0.0044883 | 0.0030057 | -0.0021057 | 0.009848 | 0.0020828 | -0.0045865 | -0.018209 | 0.02179 | -0.0020658 | 3.0396 | 120.5612 | -1.2726 | 120.4468 | 2.8839 | -0.38452 | -0.25177 | 0.027466 | 0.045776 | -0.068665 | 0.009155 | 0.13275 | 0.073242 | 0.10986 | -0.064087 | -0.07782 | -0.19226 | 4.0924 | 0.95673 | 0.82398 | 1.0208 | 0.88806 | 1.1398 | -120.5933 | -120.6299 | 1.3412 | 1.3184 | 1.2817 | 0.17853 | 0.14191 | 4.1565 | 121.7194 | 0.20142 | 0.07782 | 121.8338 | 0.11444 | 121.7697 | 1.2543 | -121.9116 | -120.7077 | 121.6553 | 1.2177 | 4.248 | 1.236
3019.625 | 121.4676 | -1.2405 | 120.6482 | -0.14336 | -0.0094785 | 0.047285 | 0.063094 | -0.014949 | -0.0087607 | -0.011734 | -0.0051575 | 0.011343 | -0.0058212 | -0.0039457 | -0.016073 | 0.012817 | -0.0029202 | 3.2364 | 119.9524 | -1.3092 | 120.2682 | 2.8427 | -0.42114 | -0.29755 | 0.018311 | 0.064087 | -0.07782 | -0.004578 | 0.10071 | 0.022888 | 0.091553 | -0.068664 | -0.6958 | -0.37994 | 4.0833 | 0.94299 | 0.8194 | 1.0117 | 0.88806 | 1.1627 | -120.5841 | -120.6528 | 1.3412 | 1.3321 | 1.2634 | 0.16937 | 0.10071 | 4.1519 | 121.5775 | 0.17853 | 0.073242 | 121.2616 | 0.14191 | 121.1929 | 1.3046 | -121.9574 | -120.726 | 121.5088 | 1.236 | 4.4769 | 1.2589
3021.3281 | 121.9482 | -1.2177 | 120.607 | -0.0060272 | 0.0099613 | 0.054121 | 0.06523 | 0.002995 | -0.0017111 | 0.0010831 | -0.0021057 | 0.01113 | 0.00058743 | 0.0031039 | -0.016928 | 0.021362 | -0.0029202 | 3.3783 | 120.5429 | -1.2726 | 120.4926 | 2.8885 | -0.36621 | -0.20142 | 0.11902 | 0.041199 | -0.050354 | 0.068665 | 0.17395 | 0.086975 | 0.13733 | -0.054932 | -0.064087 | -0.11444 | 4.1061 | 1.0162 | 0.85144 | 1.0712 | 0.90637 | 1.1673 | -120.5658 | -120.5383 | 1.3916 | 1.355 | 1.3046 | 0.18768 | 0.13733 | 4.1611 | 121.7651 | 0.2243 | 0.11902 | 121.8155 | 0.091553 | 121.7606 | 1.2589 | -121.8796 | -120.6573 | 121.7102 | 1.2863 | 4.5959 | 1.3367
3023.0781 | 121.9757 | -1.236 | 120.6024 | -0.10521 | 0.0039799 | 0.052199 | 0.06288 | -0.0017048 | -0.0047019 | 0.0025783 | 0.0039977 | 0.011984 | -5.3368e-05 | 0.0045993 | -0.017996 | 0.02179 | 0.0002842 | 3.3554 | 120.5338 | -1.3184 | 120.5063 | 2.9251 | -0.31128 | -0.20142 | 0.13275 | 0.032043 | -0.027466 | 0.082397 | 0.2243 | 0.13733 | 0.13275 | -0.082397 | -0.068665 | -0.09613 | 4.1611 | 1.0345 | 0.92468 | 1.1169 | 1.0071 | 1.2085 | -120.5704 | -120.52 | 1.4603 | 1.3687 | 1.3733 | 0.16022 | 0.16479 | 4.2435 | 121.8246 | 0.25177 | 0.10986 | 121.8521 | 0.059509 | 121.7697 | 1.268 | -121.9208 | -120.6299 | 121.7422 | 1.3184 | 4.5914 | 1.3687
3024.7812 | 121.4905 | -1.3 | 120.2133 | -0.0060272 | 0.028119 | 0.1103 | 0.060744 | -0.0087542 | 0.056822 | 0.051925 | -0.0051575 | 0.0072846 | -0.012016 | -0.0080045 | -0.0165 | 0.01004 | -0.0005704 | 3.0808 | 120.5795 | -1.3458 | 120.2271 | 2.742 | -0.49896 | -0.35248 | -0.045776 | 0.07782 | -0.07782 | -0.059509 | 0.027466 | -0.050354 | 0.027466 | -0.045776 | 0.36621 | 0.013733 | 4.0421 | 0.94757 | 0.80109 | 0.99335 | 0.84686 | 1.2222 | -120.1355 | -120.2728 | 1.3275 | 1.3275 | 1.2497 | 0.10529 | 0.027466 | 4.0878 | 121.5729 | 0.10529 | 0.018311 | 121.9254 | 0.15564 | 121.8796 | 1.3779 | -121.5591 | -120.2911 | 121.5271 | 1.2405 | 4.3808 | 1.2543
3026.5312 | 121.5317 | -1.3229 | 119.9524 | -0.051804 | 0.0071841 | 0.053267 | 0.065871 | -0.00042301 | -0.0034201 | 0.0055691 | -0.0021057 | 0.013907 | 0.0033646 | -0.0028775 | -0.015432 | 0.020721 | -0.0056974 | 2.9114 | 119.7647 | -1.3596 | 120.3369 | 2.7786 | -0.48065 | -0.32959 | -0.045776 | 0.091553 | -0.086975 | -0.045776 | 0.068665 | -0.013733 | 0.041199 | -0.036621 | -0.18768 | 0.38452 | 4.1016 | 0.99335 | 0.84228 | 1.03 | 0.87891 | 1.236 | -119.8608 | -119.9982 | 1.3916 | 1.3641 | 1.3092 | 0.12817 | 0.073242 | 4.1382 | 121.6965 | 0.15564 | 0.041199 | 121.1243 | 0.17853 | 121.0876 | 1.4145 | -121.312 | -120.0394 | 121.6599 | 1.2772 | 4.2343 | 1.2772
3028.2969 | 121.3577 | -1.3367 | 120.0577 | -0.0060272 | -0.0034971 | 0.033827 | 0.065657 | -0.0098224 | -0.019228 | -0.010666 | -0.0082093 | 0.012625 | -0.0075302 | 0.0026767 | -0.018209 | 0.010254 | -0.00762 | 2.7695 | 120.4697 | -1.3733 | 120.0073 | 2.8931 | -0.46234 | -0.31128 | 0.059509 | 0.086975 | -0.086975 | 0.018311 | 0.1236 | 0.032043 | 0.086975 | -0.036621 | 0.41199 | -0.050354 | 4.2297 | 1.0254 | 0.87433 | 1.062 | 0.91095 | 1.2497 | -119.9707 | -120.0394 | 1.4603 | 1.4236 | 1.3687 | 0.17395 | 0.11902 | 4.2664 | 121.3806 | 0.21057 | 0.10529 | 121.843 | 0.17395 | 121.8063 | 1.4236 | -121.431 | -120.1447 | 121.344 | 1.355 | 4.1061 | 1.3962
3030.0781 | 122.0169 | -51.8005 | 69.7861 | -0.028916 | 1.1155 | 0.092146 | 0.066512 | -0.014095 | -0.020083 | -0.0098117 | -0.0082093 | 0.014334 | -0.0090256 | 0.0069491 | -0.016073 | 0.013886 | -0.0074064 | -3.3646 | 69.5892 | -52.066 | 68.6966 | -43.158 | -51.8188 | -52.1072 | 0.036621 | 0.054932 | -0.054932 | 0.013733 | 0.12817 | 0.027466 | 0.082397 | -0.2655 | -0.19684 | -1.0895 | 8.6426 | -0.3067 | -0.018311 | -0.041199 | 0.24719 | 51.7456 | -69.7311 | -69.7723 | 51.9287 | 51.8829 | 51.828 | 0.13733 | 0.082398 | 8.9081 | 120.7626 | 0.18311 | 0.068665 | 121.6553 | 0.10986 | 121.3898 | 51.8555 | -121.8521 | -69.841 | 120.4971 | 51.8143 | 48.436 | 51.8372
3031.7812 | 122.0306 | -0.1831 | 121.6003 | -0.013657 | 0.0084659 | -0.0050521 | -0.011888 | -0.0023456 | -0.0079061 | -0.0053257 | -0.0051575 | 0.010702 | 0.003151 | -0.00052768 | -0.015859 | 0.021576 | -0.0005704 | -0.050354 | 0.082397 | -0.16937 | -0.009155 | 0.027466 | -0.16937 | -0.073242 | 0.068665 | -0.18768 | 0.30212 | 0.032043 | 0.13275 | 0.064087 | 0.091553 | 0.013732 | -121.5179 | -121.6095 | 0.21057 | 0.10986 | 0.013732 | 0.096131 | 0 | 0.48523 | -121.788 | -121.5683 | 0.31586 | 0.27466 | 0.24719 | -0.21057 | -0.23804 | 0.19684 | 0.16022 | -0.16937 | -0.27008 | 0.25177 | -0.48981 | 0.2655 | -0.004578 | -121.7697 | -121.2982 | 0.17395 | 0.21515 | 0.13275 | 0.25177
3033.5469 | 121.9437 | -0.13733 | 121.756 | -0.013657 | 0.0050479 | -0.012102 | -0.011888 | 0.0040632 | -0.010043 | -0.0042575 | -0.0021057 | 0.013693 | 0.0016556 | 0.0069491 | -0.016073 | 0.019653 | 7.04e-05 | -0.086975 | 0.10071 | -0.17853 | -0.1236 | -0.045776 | -0.1831 | -0.10529 | -0.045776 | 0.022888 | 0.24719 | -0.059509 | -0.091553 | -0.39368 | -0.19684 | -0.041199 | -121.6553 | -121.8796 | 0.091553 | 0.032043 | -0.045776 | 0.073242 | -0.004577 | 0.38452 | -121.7331 | -121.8155 | 0.045776 | -0.059509 | -0.25635 | -0.44403 | -0.64087 | 0.13275 | 0.054932 | -0.33874 | -0.3067 | 0.27924 | -0.2243 | 0.23804 | 0.16022 | -121.9345 | -121.5088 | 0.013733 | 0.07782 | 0.050354 | 0.091553
3035.25 | 121.9528 | -0.15106 | 121.7834 | -0.0060272 | 0.0059025 | -0.011461 | -0.011461 | 0.00021799 | -0.010043 | -0.0034031 | -0.0082093 | 0.013266 | 0.00251 | -0.0015957 | -0.013723 | 0.021149 | 0.0004978 | -0.086975 | 0.11444 | -0.15106 | -0.1236 | -0.054932 | -0.16937 | -0.11444 | -0.064087 | 0.068665 | 0.073242 | -0.032043 | 0.004578 | -0.35706 | -0.17395 | 0 | -121.669 | -121.907 | 0.09613 | 0.036621 | -0.018311 | 0.036621 | -0.018311 | 0.2243 | -121.7148 | -121.8155 | 0.15564 | -0.022888 | -0.20599 | -0.24719 | -0.4303 | 0.09613 | 0.027466 | -0.068664 | -0.10529 | 0.2655 | -0.004577 | 0.2655 | 0.21973 | -121.9345 | -121.7102 | 0.027466 | 0.11902 | 0.064087 | 0.086975
3037 | 121.9254 | -0.12817 | 121.8109 | 0.0016023 | -0.0015743 | 0.11137 | -0.022142 | 0.045292 | 0.05319 | -0.01387 | -0.057037 | -0.0046784 | -0.0066758 | -0.015481 | -0.039358 | 0.01709 | -0.011465 | -0.050354 | 0.10986 | -0.15106 | -0.11902 | -0.10986 | -0.27924 | -0.23804 | -0.068665 | 0.091553 | -0.004578 | -0.027466 | 0.009155 | -0.40283 | -0.045776 | -0.022888 | -121.701 | -121.9299 | 0.018311 | -0.10986 | -0.15106 | -0.086975 | -0.12817 | 0.1236 | -121.7194 | -121.8384 | 0.13733 | 0.082398 | -0.27466 | -0.041198 | -0.39825 | 0.041199 | 0.032043 | 0.013733 | -0.022888 | 0.26093 | 0.096131 | 0.23804 | 0.21973 | -121.962 | -121.8155 | 0.009155 | 0.10071 | 0.07782 | 0.059509
3038.75 | 121.9757 | -0.13733 | 121.8201 | -0.0060272 | 0.0071841 | -0.011034 | -0.011888 | 0.0021406 | -0.010683 | -0.0036167 | -0.032623 | 0.0092072 | 0.0018692 | 0.0039585 | -0.016714 | 0.017944 | -0.005911 | -0.07782 | 0.10529 | -0.16022 | -0.10986 | -0.027466 | -0.16937 | -0.13733 | -0.054932 | 0.064087 | -0.073242 | -0.027466 | 0.07782 | -0.22888 | -0.29755 | -0.022888 | -121.7148 | -121.9299 | 0.10986 | 0 | -0.032044 | 0.022888 | -0.009156 | 0.064087 | -121.756 | -121.8475 | 0.21515 | -0.16022 | -0.091553 | -0.2243 | -0.15564 | 0.13275 | 0.050354 | 0.15106 | 0.045776 | 0.2655 | 0.13733 | 0.24262 | 0.20142 | -121.9803 | -121.8933 | 0.027466 | 0.10986 | 0.059509 | 0.082397
3040.5156 | 122.0261 | -0.09613 | 121.8384 | -0.013657 | 0.0086795 | -0.0091109 | -0.012743 | -0.0032 | -0.0081197 | -0.0044711 | 0.0009461 | 0.010275 | 0.00058743 | -0.0041593 | -0.015005 | 0.01944 | 0.0011386 | -0.022888 | 0.054932 | -0.10071 | -0.041199 | 0.068665 | -0.10529 | -0.009155 | 0.041199 | 0.050354 | -0.068665 | 0.036621 | 0.11444 | 0.032043 | 0.10071 | -0.004578 | -121.7834 | -121.8796 | 0.16479 | 0.086975 | -0.009156 | 0.091553 | -0.004578 | 0.027465 | -121.788 | -121.8018 | 0.21057 | 0.19684 | 0.12817 | 0.16937 | 0.10071 | 0.16937 | 0.059509 | 0.18311 | 0.10529 | 0.15564 | 0.11902 | 0.15106 | 0.14648 | -121.9391 | -121.907 | 0.054931 | 0.13275 | 0.073242 | 0.13733
3042.2656 | 122.0673 | -0.09613 | 121.8246 | -0.0060272 | 0.010175 | -0.0080429 | -0.012102 | -0.00020941 | -0.010256 | -0.0059665 | -0.0021057 | 0.0096344 | 0.00058743 | -0.0026639 | -0.0165 | 0.022858 | 0.0030612 | 0.032043 | 0.054932 | -0.11444 | 0.018311 | 0.1236 | -0.07782 | 0.004578 | 0.12817 | 0.045776 | -0.064087 | 0.10071 | 0.17853 | 0.073242 | 0.14648 | -0.018311 | -121.7697 | -121.8063 | 0.21973 | 0.10071 | 0.01831 | 0.11902 | 0.036621 | 0.032043 | -121.7789 | -121.7239 | 0.27466 | 0.24261 | 0.16937 | 0.21057 | 0.13733 | 0.23804 | 0.13275 | 0.24261 | 0.1648 | 0.16937 | 0.10986 | 0.15106 | 0.14191 | -121.9391 | -121.8887 | 0.11444 | 0.19684 | 0.12817 | 0.2243
3044.0156 | 122.0306 | -0.11444 | 121.843 | -0.013657 | 0.0071841 | -0.010179 | -0.012315 | -0.0023456 | -0.010043 | -0.0061801 | -0.0051575 | 0.009848 | 0.0033646 | -0.0022367 | -0.0165 | 0.022217 | -0.0018522 | -0.032043 | 0.050354 | -0.1236 | -0.050354 | 0.050354 | -0.1236 | -0.036621 | 0.045776 | 0.036621 | -0.054932 | 0.032043 | 0.11902 | 0.041199 | 0.091553 | -0.009155 | -121.7926 | -121.8933 | 0.16479 | 0.07782 | -0.009155 | 0.086975 | 0 | 0.059509 | -121.8063 | -121.8109 | 0.23346 | 0.20599 | 0.15564 | 0.14649 | 0.096131 | 0.17395 | 0.073242 | 0.17395 | 0.086975 | 0.17395 | 0.091553 | 0.16479 | 0.15106 | -121.9666 | -121.8979 | 0.064087 | 0.14648 | 0.082398 | 0.16022
3045.7188 | 121.9208 | -0.16479 | 121.8567 | -0.044174 | 0.0067569 | -0.01082 | -0.011888 | -0.0023456 | -0.01047 | -0.0055393 | -0.0082093 | 0.012411 | 0.0040054 | 0.0086581 | -0.016073 | 0.022644 | -0.0014248 | -0.059509 | 0.10986 | -0.17395 | -0.12817 | -0.013733 | -0.18768 | -0.10071 | -0.059509 | 0.07782 | -0.073242 | -0.045776 | 0.050354 | -0.041199 | -0.064087 | -0.009155 | -121.7468 | -121.9849 | 0.15106 | 0.064087 | -0.022888 | 0.073242 | -0.013733 | 0.091553 | -121.7789 | -121.9025 | 0.21515 | 0.10071 | 0.1236 | 0.009155 | 0.032043 | 0.16022 | 0.045776 | 0.1236 | 0.027466 | 0.28381 | 0.15106 | 0.27466 | 0.24261 | -122.0306 | -121.9299 | 0.036621 | 0.11902 | 0.10529 | 0.10529
3047.4688 | 121.9574 | -0.14191 | 121.8338 | -0.013657 | 0.0052615 | -0.010393 | -0.011675 | -0.003841 | -0.011965 | -0.0027621 | -0.0021057 | 0.011557 | 0.0037918 | 0.0016085 | -0.015432 | 0.020721 | -0.0031338 | 0.018311 | 0.050354 | -0.12817 | -0.045776 | 0.064087 | -0.09613 | -0.022888 | 0 | 0.054932 | -0.064087 | -0.022888 | 0.091553 | 0 | 0.041199 | 0.013733 | -121.7834 | -121.8796 | 0.20599 | 0.11902 | 0.045777 | 0.10529 | 0.032044 | 0.07782 | -121.7789 | -121.8567 | 0.23346 | 0.18311 | 0.14191 | 0.10529 | 0.064087 | 0.19226 | 0.082398 | 0.15564 | 0.041199 | 0.17853 | 0.11902 | 0.19226 | 0.19684 | -121.962 | -121.8979 | 0.096131 | 0.11902 | 0.16022 | 0.14191
3049.1562 | 121.2982 | -0.12817 | 121.2662 | -0.013657 | 0.0088931 | -0.015947 | -0.013597 | -0.006618 | -0.018801 | -0.02092 | -0.0051575 | -0.0046784 | -0.0038986 | -0.0067227 | -0.026541 | 0.037598 | -0.018515 | 0 | 0.07782 | -0.14191 | -0.032043 | 0.050354 | -0.12817 | -0.068665 | 0.045776 | 0.073242 | -0.07782 | 0.041199 | 0.10986 | 0.013733 | -0.064087 | -0.013733 | -121.1884 | -121.2982 | 0.17853 | 0.059509 | 0 | 0.073242 | 0.013733 | 0.050354 | -121.1929 | -121.225 | 0.23804 | 0.064087 | 0.14191 | 0.013733 | 0.091553 | 0.19226 | 0.10986 | 0.18768 | 0.11902 | 0.21973 | 0.15106 | 0.20599 | 0.20142 | -121.4081 | -121.344 | 0.096131 | 0.16937 | 0.12817 | 0.17395
3050.9219 | 122.0718 | -0.082397 | 121.7331 | -0.013657 | 0.0056887 | -0.010179 | -0.014024 | -0.0027728 | -0.012392 | -0.0057529 | -0.0051575 | 0.010489 | 0.00037383 | -0.0011685 | -0.016287 | 0.020935 | -0.0012112 | 0.009155 | 0.054932 | -0.09613 | 0.054932 | 0.1831 | -0.022888 | 0.022888 | 0.10529 | 0.054932 | -0.041199 | 0.082397 | 0.2243 | 0.12817 | 0.12817 | -0.013733 | -121.6782 | -121.6782 | 0.2655 | 0.10528 | 0.059509 | 0.11902 | 0.073242 | 0.041198 | -121.6782 | -121.6507 | 0.3067 | 0.21057 | 0.21057 | 0.16937 | 0.16937 | 0.27924 | 0.15106 | 0.2655 | 0.1236 | 0.15106 | 0.096131 | 0.13733 | 0.13733 | -121.8292 | -121.7743 | 0.13733 | 0.16479 | 0.091552 | 0.18768
3052.6719 | 121.4996 | -0.15106 | 121.344 | 0.0016023 | 0.0056887 | -0.01082 | -0.014024 | -0.0029864 | -0.01047 | -0.0055393 | -0.0021057 | 0.012625 | 0.0033646 | -0.0022367 | -0.017355 | 0.021149 | 7.04e-05 | -0.068665 | 0.082397 | -0.14191 | -0.11444 | 0.004578 | -0.14191 | -0.091553 | -0.054932 | 0.09613 | -0.091553 | -0.054932 | 0.073242 | -0.027466 | 0.032043 | 0.009155 | -121.2616 | -121.4584 | 0.15564 | 0.059509 | 0.009155 | 0.050354 | 0 | 0.059509 | -121.2479 | -121.3989 | 0.2243 | 0.18311 | 0.1236 | 0.1236 | 0.064087 | 0.14649 | 0.027466 | 0.16479 | 0.036621 | 0.2243 | 0.18768 | 0.23346 | 0.24719 | -121.4859 | -121.4355 | 0.036621 | 0.09613 | 0.082397 | 0.09613
3054.3594 | 121.431 | -0.15564 | 121.3257 | -0.013657 | 0.0024845 | -0.028978 | -0.01552 | -0.011531 | -0.024142 | -0.022629 | -0.0051575 | 0.00023504 | -0.0045396 | -0.0086453 | -0.022055 | 0.014954 | -0.0048428 | -0.018311 | 0.082397 | -0.13733 | -0.091553 | 0.027466 | -0.16937 | -0.10529 | -0.022888 | 0.082397 | -0.086975 | -0.018311 | 0.07782 | -0.027466 | 0.032043 | 0.018311 | -121.2433 | -121.4172 | 0.18311 | 0.050354 | -0.013733 | 0.032043 | -0.032044 | 0.068665 | -121.2433 | -121.344 | 0.23346 | 0.18768 | 0.12817 | 0.11902 | 0.059509 | 0.16479 | 0.045776 | 0.16479 | 0.068664 | 0.21973 | 0.16937 | 0.23804 | 0.23804 | -121.463 | -121.4127 | 0.064087 | 0.13733 | 0.13733 | 0.13275
3056.125 | 122.0764 | -0.091553 | 121.9162 | -0.013657 | 0.0073977 | -0.011888 | -0.012743 | 0.001286 | -0.011965 | -0.0040439 | -0.0021057 | 0.0096344 | 0.0016556 | -0.00031408 | -0.016287 | 0.021576 | 0.0007114 | -0.027466 | 0.054932 | -0.10529 | -0.045776 | 0.086975 | -0.07782 | 0 | 0.059509 | 0.054932 | -0.059509 | 0.050354 | 0.18768 | 0.10071 | 0.1236 | -0.013733 | -121.8613 | -121.962 | 0.17853 | 0.091553 | 0.013733 | 0.10529 | 0.027466 | 0.032044 | -121.8613 | -121.8658 | 0.27924 | 0.21515 | 0.19226 | 0.1831 | 0.16022 | 0.19226 | 0.05951 | 0.24719 | 0.10986 | 0.16022 | 0.11444 | 0.14649 | 0.14649 | -122.0215 | -121.9757 | 0.045777 | 0.14191 | 0.064087 | 0.15106
3057.8281 | 121.6644 | -0.13733 | 121.9437 | -0.22728 | 0.0041935 | -0.011034 | -0.010606 | -0.00020941 | -0.01047 | -0.0066073 | 0.0009461 | 0.013907 | -0.0013352 | 0.00075412 | -0.016287 | 0.023285 | 0.0017794 | -0.018311 | 0.07782 | -0.12817 | -0.073242 | 0.036621 | -0.13733 | -0.064087 | -0.027466 | 0.064087 | -0.082397 | -0.036621 | 0.068665 | -0.009155 | 0.032043 | 0.009155 | -121.8658 | -122.0169 | 0.17395 | 0.073242 | 0 | 0.064087 | -0.009155 | 0.054932 | -121.8796 | -121.9803 | 0.20599 | 0.16937 | 0.12817 | 0.11444 | 0.073242 | 0.1648 | 0.054932 | 0.15106 | 0.045776 | 0.20599 | 0.14648 | 0.21515 | 0.20142 | -122.0718 | -122.0261 | 0.064087 | 0.10071 | 0.11902 | 0.10986
3059.5781 | 122.0718 | -0.10071 | 121.8979 | -0.0060272 | 0.0073977 | -0.0086837 | -0.011034 | -0.0010638 | -0.0096151 | -0.0085299 | -0.0021057 | 0.010489 | -0.00026697 | 0.00075412 | -0.015219 | 0.02179 | -0.0003568 | -0.009155 | 0.045776 | -0.10986 | 0.013733 | 0.12817 | -0.09613 | 0 | 0.10986 | 0.045776 | -0.045776 | 0.059509 | 0.17395 | 0.059509 | 0.10529 | -0.009155 | -121.8521 | -121.8842 | 0.22888 | 0.10071 | 0.004578 | 0.10986 | 0.013733 | 0.054932 | -121.8521 | -121.8384 | 0.27466 | 0.20599 | 0.16022 | 0.15106 | 0.10528 | 0.23804 | 0.1236 | 0.21973 | 0.10528 | 0.15564 | 0.091552 | 0.14648 | 0.14648 | -122.0078 | -121.9437 | 0.11444 | 0.16022 | 0.091553 | 0.21057
3061.3438 | 122.0718 | -0.086975 | 121.9208 | -0.021286 | 0.0067569 | -0.0071883 | -0.014238 | -0.0029864 | -0.011111 | -0.0040439 | -0.0021057 | 0.011343 | 0.001442 | -0.0015957 | -0.016287 | 0.020294 | -0.0031338 | -0.013733 | 0.041199 | -0.091553 | 0.009155 | 0.11902 | -0.09613 | -0.004578 | 0.11444 | 0.036621 | -0.050354 | 0.041199 | 0.15564 | 0.073242 | 0.10986 | -0.004578 | -121.8796 | -121.9116 | 0.20599 | 0.082397 | -0.009155 | 0.086975 | -0.004577 | 0.036621 | -121.8842 | -121.8796 | 0.24261 | 0.19684 | 0.16022 | 0.16022 | 0.1236 | 0.21057 | 0.10071 | 0.20599 | 0.091553 | 0.13275 | 0.086975 | 0.12817 | 0.1236 | -122.0123 | -121.9711 | 0.09613 | 0.12817 | 0.073242 | 0.20142
3063.1094 | 122.1085 | -0.10071 | 121.8475 | -0.0060272 | 0.0099613 | -0.0095383 | -0.010606 | -0.0010638 | -0.0081197 | -0.0036167 | -0.0082093 | 0.012625 | 0.0027236 | 0.00054052 | -0.016073 | 0.023071 | 0.000925 | -0.036621 | 0.059509 | -0.1236 | -0.018311 | 0.073242 | -0.11444 | -0.036621 | 0.07782 | 0.041199 | -0.054932 | 0.07782 | 0.1831 | 0.073242 | 0.14648 | -0.022888 | -121.788 | -121.8658 | 0.17395 | 0.064087 | -0.013733 | 0.086975 | 0.009155 | 0.045776 | -121.8063 | -121.7697 | 0.28381 | 0.24719 | 0.17395 | 0.20142 | 0.12817 | 0.19684 | 0.10528 | 0.23804 | 0.13275 | 0.1831 | 0.096131 | 0.16022 | 0.14191 | -121.9711 | -121.9025 | 0.082397 | 0.17853 | 0.064087 | 0.17853
3064.8125 | 122.1359 | -0.082397 | 121.9391 | -0.33409 | 0.0035525 | -0.011034 | -0.013597 | 0.0019268 | -0.014101 | -0.0031895 | -0.0021057 | 0.011557 | 0.001442 | 0.00011332 | -0.015646 | 0.021576 | 0.0004978 | -0.032043 | 0.036621 | -0.10986 | 0.009155 | 0.16022 | -0.036621 | 0.032043 | 0.13275 | 0.041199 | -0.059509 | 0.082397 | 0.2243 | 0.1236 | 0.14191 | -0.027466 | -121.9025 | -121.9299 | 0.24261 | 0.11444 | 0.045776 | 0.14191 | 0.073242 | 0.022888 | -121.8979 | -121.8567 | 0.3067 | 0.2243 | 0.20599 | 0.20142 | 0.1831 | 0.27008 | 0.11902 | 0.28381 | 0.14191 | 0.14648 | 0.10071 | 0.11902 | 0.1236 | -122.049 | -121.9986 | 0.091552 | 0.16479 | 0.050354 | 0.21515
3066.5781 | 121.4996 | -0.15564 | 121.3348 | -0.013657 | -0.0060605 | 0.10945 | -0.014665 | -0.013668 | -0.054049 | -0.017288 | 0.0009461 | 0.0049346 | -0.0077438 | -0.0022367 | -0.013937 | 0.007904 | -0.0020658 | -0.07782 | 0.068665 | -0.13733 | -0.13733 | -0.050354 | -0.21973 | -0.12817 | -0.073242 | 0.086975 | -0.09613 | -0.064087 | 0.018311 | -0.073242 | 0.013733 | 0.018311 | -121.2662 | -121.4722 | 0.10529 | 0.027466 | -0.064087 | 0.009155 | -0.082398 | 0.05951 | -121.2479 | -121.3989 | 0.17395 | 0.16937 | 0.082398 | 0.10986 | 0.022888 | 0.086975 | 0 | 0.11444 | 0.032043 | 0.20599 | 0.1831 | 0.22431 | 0.24261 | -121.4722 | -121.431 | 0.018311 | 0.091553 | 0.07782 | 0.082398
3068.2812 | 122.1222 | -0.10986 | 121.9391 | -0.15862 | 0.0033389 | 0.0011429 | -0.013597 | -0.0010638 | -0.011538 | -0.0036167 | -0.0021057 | 0.009848 | 0.0010146 | 0.00032692 | -0.015859 | 0.02179 | -0.0027066 | -0.022888 | 0.036621 | -0.10529 | 0.004578 | 0.15106 | -0.036621 | 0.059509 | 0.14648 | 0.022888 | -0.045776 | 0.073242 | 0.21973 | 0.1236 | 0.14191 | 0.004577 | -121.9025 | -121.9345 | 0.26093 | 0.16937 | 0.073242 | 0.16479 | 0.068665 | 0.064087 | -121.9162 | -121.8658 | 0.32959 | 0.25177 | 0.23346 | 0.18768 | 0.16937 | 0.25635 | 0.10986 | 0.2655 | 0.11902 | 0.14191 | 0.068664 | 0.14648 | 0.13275 | -122.0444 | -121.9849 | 0.11444 | 0.18311 | 0.086975 | 0.25635
3070.0312 | 122.113 | -0.086975 | 121.9803 | -0.57823 | 0.0073977 | 0.0015701 | -0.012956 | 0.00043159 | -0.0074789 | -0.0046847 | -0.0082093 | 0.013266 | 0.0022964 | 0.0016085 | -0.016714 | 0.022858 | 0.0004978 | -0.009155 | 0.004578 | -0.091553 | 0.009155 | 0.14191 | -0.073242 | 0.027466 | 0.11444 | 0.045776 | -0.054932 | 0.07782 | 0.19226 | 0.09613 | 0.13275 | -0.004578 | -121.9757 | -121.9711 | 0.22888 | 0.11444 | 0.013733 | 0.11902 | 0.018311 | 0.032043 | -121.9345 | -121.9025 | 0.27924 | 0.21973 | 0.1831 | 0.18768 | 0.15106 | 0.23346 | 0.10071 | 0.24719 | 0.13275 | 0.096131 | 0.10071 | 0.091553 | 0.13275 | -122.0718 | -122.0352 | 0.09613 | 0.16479 | 0.07782 | 0.20142
3071.7969 | 121.5958 | -0.12817 | 121.6003 | -0.013657 | 0.0037661 | 0.10945 | -0.013811 | -0.01089 | 0.051267 | -0.010453 | -0.0051575 | 0.0072846 | -0.0096664 | 0.0035311 | -0.014578 | 0.010681 | 0.0015658 | -0.07782 | 0.064087 | -0.13275 | -0.11902 | -0.059509 | -0.21057 | -0.13275 | -0.073242 | 0.082397 | -0.086975 | -0.059509 | 0.018311 | -0.068665 | 0.013733 | -0.004577 | -121.5363 | -121.7194 | 0.068665 | -0.004577 | -0.082397 | 0 | -0.07782 | 0.041199 | -121.5179 | -121.6599 | 0.14649 | 0.14191 | 0.059509 | 0.10071 | 0.01831 | 0.073242 | 0.013732 | 0.10529 | 0.027466 | 0.19684 | 0.16937 | 0.19226 | 0.21057 | -121.7331 | -121.6873 | 0.009155 | 0.068665 | 0.050354 | 0.054932
3073.5625 | 122.1176 | -0.10529 | 121.9574 | -0.0060272 | 0.0067569 | 0.0024247 | -0.013597 | -0.001491 | -0.0079061 | -0.0066073 | -0.0051575 | 0.010275 | 0.0033646 | 0.0031039 | -0.0165 | 0.020294 | -0.00527 | -0.082397 | 0.041199 | -0.11444 | -0.059509 | 0.082397 | -0.082397 | 0 | 0.036621 | 0.041199 | -0.068665 | 0.041199 | 0.16022 | 0.07782 | 0.10529 | -0.009155 | -121.9162 | -122.0169 | 0.18768 | 0.10529 | 0.022889 | 0.11444 | 0.032044 | 0.036621 | -121.9162 | -121.9162 | 0.2655 | 0.21057 | 0.18311 | 0.17395 | 0.14649 | 0.19684 | 0.054932 | 0.22888 | 0.10986 | 0.15564 | 0.10986 | 0.14649 | 0.14649 | -122.0718 | -122.0261 | 0.045777 | 0.14649 | 0.022889 | 0.14191
3075.2656 | 122.1222 | -0.068665 | 121.8292 | -0.41039 | 0.0061161 | 0.014174 | -0.012743 | -0.004909 | -0.0096151 | -0.0027621 | 0.0009461 | 0.010916 | 0.0022964 | -0.0018093 | -0.016714 | 0.021149 | -0.0005704 | -0.10986 | 0.027466 | -0.082397 | -0.059509 | 0.064087 | -0.10071 | -0.013733 | 0.027466 | 0.045776 | -0.064087 | 0.045776 | 0.15106 | 0.068665 | 0.10071 | -0.013732 | -121.8018 | -121.8887 | 0.13275 | 0.054932 | -0.032043 | 0.068664 | -0.018311 | 0.004578 | -121.7834 | -121.7834 | 0.21973 | 0.16937 | 0.13733 | 0.1648 | 0.13275 | 0.14648 | 0.022888 | 0.21515 | 0.10986 | 0.10986 | 0.10986 | 0.096131 | 0.11444 | -121.9116 | -121.8933 | 0.009156 | 0.11444 | -0.041198 | 0.096131
3077.0312 | 122.0901 | -0.12817 | 121.7514 | -0.0060272 | 0.0065433 | 0.013106 | -0.015093 | -0.0019184 | -0.011965 | -0.0076755 | -0.0021057 | 0.013052 | 0.0044326 | -0.0039457 | -0.012655 | 0.01474 | -0.0012112 | -0.10529 | 0.068665 | -0.13733 | -0.09613 | -0.018311 | -0.14648 | -0.09613 | -0.045776 | 0.091553 | -0.07782 | -0.022888 | 0.091553 | -0.009155 | 0.064087 | -0.009155 | -121.6827 | -121.8475 | 0.10986 | 0.032044 | -0.01831 | 0.041199 | -0.009155 | 0.050354 | -121.6599 | -121.7743 | 0.21973 | 0.19226 | 0.11902 | 0.14191 | 0.068665 | 0.11902 | 0.041199 | 0.16937 | 0.054932 | 0.20599 | 0.16937 | 0.19684 | 0.21973 | -121.8887 | -121.8292 | 0.032044 | 0.10529 | 0.022888 | 0.082398
3078.7969 | 122.0398 | -0.12817 | 121.9711 | -0.0060272 | -0.0039243 | 0.1086 | -0.013597 | -0.012813 | -0.019015 | -0.014298 | -0.0082093 | 0.012411 | -0.0062486 | -0.00052768 | -0.017141 | 0.013886 | -0.004202 | -0.12817 | 0.07782 | -0.11444 | -0.11444 | -0.059509 | -0.20142 | -0.12817 | -0.068665 | 0.07782 | -0.07782 | -0.027466 | 0.045776 | -0.064087 | 0.032043 | 0.013733 | -121.8933 | -122.0856 | 0.068665 | 0 | -0.073242 | -0.013733 | -0.086975 | 0.050354 | -121.8933 | -121.9986 | 0.17395 | 0.16022 | 0.064087 | 0.10986 | 0.013733 | 0.054932 | 0 | 0.1236 | 0.050354 | 0.19226 | 0.15564 | 0.20599 | 0.20599 | -122.0856 | -122.049 | 0.013733 | 0.10071 | 0 | 0.059509
3080.5 | 122.1634 | -0.086975 | 121.9711 | -0.42564 | 0.0071841 | 0.013747 | -0.012529 | -0.0025592 | -0.010897 | -0.0040439 | -0.0051575 | 0.012411 | 0.00251 | 0.0035311 | -0.016287 | 0.020508 | -0.0020658 | -0.073242 | 0.045776 | -0.09613 | 0.004578 | 0.16022 | -0.018311 | 0.045776 | 0.11902 | 0.041199 | -0.045776 | 0.07782 | 0.20599 | 0.11444 | 0.13275 | -0.009155 | -121.9254 | -121.9666 | 0.24719 | 0.13275 | 0.068664 | 0.14191 | 0.077819 | 0.041199 | -121.9299 | -121.8933 | 0.29297 | 0.21973 | 0.20142 | 0.17853 | 0.16022 | 0.25635 | 0.10071 | 0.25177 | 0.1236 | 0.14191 | 0.086975 | 0.13275 | 0.12817 | -122.0673 | -122.0169 | 0.091553 | 0.16479 | 0.013733 | 0.20599
3082.2031 | 122.1771 | -0.07782 | 121.9711 | -0.21965 | 0.0069705 | 0.017592 | -0.0099656 | 4.192e-06 | -0.0089743 | -0.0027621 | -0.0051575 | 0.011343 | 0.0027236 | -0.0026639 | -0.016928 | 0.021149 | -0.0020658 | -0.086975 | 0.041199 | -0.09613 | -0.009155 | 0.086975 | -0.091553 | 0.009155 | 0.10071 | 0.045776 | -0.045776 | 0.09613 | 0.18768 | 0.07782 | 0.14191 | -0.01831 | -121.9299 | -121.9803 | 0.16479 | 0.086975 | -0.013733 | 0.10528 | 0.004577 | 0.032044 | -121.9254 | -121.875 | 0.2655 | 0.21973 | 0.15564 | 0.18768 | 0.1236 | 0.1831 | 0.086975 | 0.23346 | 0.14191 | 0.13733 | 0.091552 | 0.11902 | 0.1236 | -122.0673 | -122.0169 | 0.068665 | 0.17395 | -0.009155 | 0.17853
3083.9688 | 122.0581 | -0.1236 | 122.0352 | -0.25017 | 0.027692 | 0.10966 | -0.010393 | -0.012813 | 0.055753 | -0.010025 | -0.0082093 | 0.013052 | -0.0073166 | 0.0075901 | -0.01351 | 0.014526 | -0.000784 | -0.11902 | 0.041199 | -0.13733 | -0.11444 | -0.041199 | -0.21515 | -0.11902 | -0.073242 | 0.086975 | -0.10529 | -0.022888 | 0.036621 | -0.054932 | 0.054932 | -0.013733 | -121.994 | -122.1497 | 0.082397 | 0.004577 | -0.091553 | 0.01831 | -0.07782 | 0.01831 | -121.9482 | -122.0581 | 0.16022 | 0.17853 | 0.068664 | 0.16022 | 0.050354 | 0.09613 | 0.022888 | 0.14191 | 0.082398 | 0.17853 | 0.19226 | 0.16479 | 0.21057 | -122.1725 | -122.1405 | 0.009155 | 0.10071 | 0.004577 | 0.050354
3085.6719 | 122.0627 | -0.13275 | 122.0444 | -0.013657 | -0.0026425 | 0.10795 | -0.009752 | -0.0034136 | 0.016874 | 0.050857 | -0.0051575 | 0.013052 | -0.007103 | -0.0048001 | -0.019491 | 0.0064088 | -0.0078336 | -0.10986 | 0.059509 | -0.11444 | -0.07782 | 0.009155 | -0.16937 | -0.09613 | -0.045776 | 0.07782 | -0.07782 | -0.041199 | 0.050354 | -0.036621 | 0.036621 | 0.01831 | -121.9849 | -122.1222 | 0.14191 | 0.036621 | -0.036622 | 0.018311 | -0.054932 | 0.054931 | -121.9666 | -122.0856 | 0.18311 | 0.16937 | 0.09613 | 0.11444 | 0.041199 | 0.1236 | 0.036621 | 0.12817 | 0.036621 | 0.17395 | 0.15564 | 0.19226 | 0.21057 | -122.1588 | -122.1222 | 0.054931 | 0.091552 | 0.022888 | 0.086975
3087.4375 | 122.1405 | -0.10071 | 122.0444 | -0.013657 | 0.0091067 | 0.01396 | -0.01082 | 0.0010724 | -0.0096151 | -0.0072483 | -0.0051575 | 0.012198 | 0.0018692 | 0.0056675 | -0.017355 | 0.022644 | 0.0034884 | -0.14191 | 0.068665 | -0.10986 | -0.09613 | 0.009155 | -0.16937 | -0.082397 | 0 | 0.054932 | -0.068665 | 0.041199 | 0.12817 | 0.022888 | 0.10529 | -0.009155 | -121.9757 | -122.1405 | 0.10986 | 0.018311 | -0.068665 | 0.027466 | -0.05951 | 0.032043 | -121.9894 | -122.0032 | 0.22888 | 0.20599 | 0.1236 | 0.17395 | 0.091553 | 0.11902 | 0.013733 | 0.19684 | 0.10986 | 0.17853 | 0.1236 | 0.16937 | 0.15564 | -122.1542 | -122.113 | 0.004578 | 0.14191 | -0.041199 | 0.10071
3089.1875 | 122.0993 | -0.11902 | 121.9162 | -0.0060272 | 0.0091067 | 0.0092605 | -0.010393 | 0.0017132 | -0.015169 | -0.0091709 | -0.0051575 | 0.014548 | -5.3368e-05 | -0.0045865 | -0.023977 | 0.006195 | -0.014242 | -0.1236 | 0.054932 | -0.1236 | -0.045776 | 0.064087 | -0.10071 | -0.059509 | 0.036621 | 0.091553 | -0.086975 | 0.013733 | 0.10986 | 0.018311 | 0.073242 | -0.004577 | -121.8613 | -121.962 | 0.18311 | 0.05951 | 0.018311 | 0.064087 | 0.022888 | 0.032044 | -121.8246 | -121.9025 | 0.22888 | 0.19226 | 0.13733 | 0.16022 | 0.10529 | 0.18768 | 0.07782 | 0.19684 | 0.10071 | 0.17853 | 0.17853 | 0.17395 | 0.21057 | -122.0398 | -122.0032 | 0.073243 | 0.13275 | -0.004577 | 0.15564
3090.8906 | 122.0764 | -0.1236 | 122.0398 | -0.0060272 | 0.0031253 | 0.012892 | -0.012102 | -0.0010638 | -0.012179 | -0.0059665 | -0.0021057 | 0.012839 | 0.0012282 | 0.0024631 | -0.017355 | 0.021362 | -0.0027066 | -0.16937 | 0.064087 | -0.11444 | -0.12817 | 0 | -0.16022 | -0.059509 | -0.041199 | 0.086975 | -0.091553 | -0.059509 | 0.050354 | -0.022888 | 0.041199 | 0.009155 | -121.9757 | -122.168 | 0.1236 | 0.064087 | -0.036621 | 0.054932 | -0.045776 | 0.032043 | -121.9528 | -122.0993 | 0.17395 | 0.16479 | 0.10071 | 0.13275 | 0.068665 | 0.11444 | -0.013733 | 0.14191 | 0.032044 | 0.17853 | 0.17853 | 0.18768 | 0.21057 | -122.1542 | -122.1313 | -0.004578 | 0.064087 | -0.045777 | 0.082397
3092.6406 | 122.1909 | -0.07782 | 122.0215 | 0.0016023 | 0.0088931 | 0.015456 | -0.010393 | 0.0042768 | -0.0091879 | -0.0025485 | -0.0021057 | 0.010916 | 0.0012282 | 0.0086581 | -0.017782 | 0.024353 | -0.0029202 | -0.11444 | 0.041199 | -0.10529 | -0.050354 | 0.073242 | -0.10071 | -0.027466 | 0.07782 | 0.059509 | -0.068665 | 0.073242 | 0.17395 | 0.07782 | 0.13275 | -0.027466 | -121.9803 | -122.0718 | 0.15106 | 0.050354 | -0.022888 | 0.07782 | 0.004578 | 0.009155 | -121.962 | -121.9482 | 0.25177 | 0.21057 | 0.15564 | 0.20142 | 0.14649 | 0.17853 | 0.054932 | 0.24261 | 0.14191 | 0.14649 | 0.12817 | 0.11902 | 0.13733 | -122.1268 | -122.0901 | 0.027466 | 0.15106 | -0.036621 | 0.15564
3094.3438 | 122.2229 | -0.086975 | 122.0032 | 0.0016023 | 0.0048343 | 0.016951 | -0.012315 | -0.00063661 | -0.0096151 | -0.0055393 | -0.0051575 | 0.009848 | 0.00251 | 0.00032692 | -0.016073 | 0.021362 | -0.0009976 | -0.10986 | 0.022888 | -0.10071 | -0.018311 | 0.10071 | -0.059509 | 0.036621 | 0.082397 | 0.045776 | -0.054932 | 0.045776 | 0.19226 | 0.11902 | 0.13733 | -0.013733 | -121.9803 | -122.0215 | 0.18768 | 0.1236 | 0.027466 | 0.13733 | 0.041199 | 0.032043 | -121.9574 | -121.9574 | 0.27924 | 0.2243 | 0.20599 | 0.19226 | 0.17395 | 0.20142 | 0.082397 | 0.24719 | 0.10071 | 0.1236 | 0.10071 | 0.10986 | 0.13275 | -122.1039 | -122.0581 | 0.068664 | 0.13275 | -0.022888 | 0.16937
3096.1094 | 122.0947 | -0.1236 | 122.0764 | -0.089951 | 0.0048343 | 0.014174 | -0.010393 | 0.00021799 | -0.012179 | -0.0021213 | -0.0021057 | 0.012198 | 0.0020828 | -0.00052768 | -0.018423 | 0.019653 | 0.0002842 | -0.09613 | 0.027466 | -0.10986 | -0.073242 | 0.054932 | -0.091553 | -0.027466 | -0.004578 | 0.082397 | -0.059509 | -0.045776 | 0.09613 | 0.004578 | 0.032043 | 0.013733 | -122.0489 | -122.1497 | 0.17853 | 0.09613 | 0.032043 | 0.082397 | 0.01831 | 0.064087 | -121.994 | -122.1222 | 0.21973 | 0.15564 | 0.12817 | 0.091552 | 0.064087 | 0.16479 | 0.036621 | 0.15564 | 0.013733 | 0.13733 | 0.14191 | 0.15106 | 0.20599 | -122.1863 | -122.1359 | 0.050354 | 0.07782 | 0.027466 | 0.11902
3097.875 | 122.2229 | -0.082397 | 121.9849 | -0.013657 | 0.0039799 | 0.014815 | -0.012102 | -0.0051226 | -0.0098287 | -0.0059665 | -0.0051575 | 0.011984 | 0.0018692 | -0.0018093 | -0.018423 | 0.022003 | -0.0039884 | -0.086975 | 0.036621 | -0.10986 | -0.009155 | 0.13733 | -0.041199 | 0.073242 | 0.10986 | 0.032043 | -0.050354 | 0.082397 | 0.21973 | 0.11444 | 0.15564 | -0.027466 | -121.9482 | -121.994 | 0.21973 | 0.15564 | 0.041198 | 0.18311 | 0.068664 | 0.032043 | -121.9528 | -121.9025 | 0.30212 | 0.23804 | 0.19684 | 0.20599 | 0.16479 | 0.24719 | 0.10071 | 0.27008 | 0.13275 | 0.14648 | 0.082397 | 0.11902 | 0.11444 | -122.0947 | -122.0352 | 0.073242 | 0.16479 | -0.004578 | 0.19226
3099.5781 | 122.0535 | -0.1236 | 121.9299 | -0.021286 | -0.0017881 | 0.054335 | -0.01317 | -0.010677 | -0.026064 | -0.019638 | -0.0021057 | 0.011771 | -0.0011216 | 0.0022495 | -0.012655 | 0.014526 | -0.0029202 | -0.13733 | 0.059509 | -0.13275 | -0.13275 | -0.045776 | -0.20142 | -0.10986 | -0.068665 | 0.10071 | -0.09613 | -0.050354 | 0.009155 | -0.07782 | 0.018311 | -0.009155 | -121.8704 | -122.0627 | 0.07782 | 0.013733 | -0.07782 | 0.022888 | -0.068665 | 0.027466 | -121.8292 | -121.9803 | 0.13275 | 0.14191 | 0.045776 | 0.11444 | 0.01831 | 0.086975 | 0 | 0.10528 | 0.045776 | 0.19226 | 0.19684 | 0.1831 | 0.2243 | -122.0627 | -122.0261 | -0.009155 | 0.073242 | -0.013733 | 0.054931
3101.3281 | 122.168 | -0.091553 | 122.0398 | -0.021286 | 0.0078251 | 0.016524 | -0.011888 | -0.0034136 | -0.0089743 | -0.0036167 | -0.0051575 | 0.011771 | 0.0016556 | -0.0020231 | -0.015219 | 0.022217 | -0.0009976 | -0.13733 | 0.022888 | -0.09613 | -0.054932 | 0.064087 | -0.086975 | -0.004578 | 0.018311 | 0.045776 | -0.059509 | 0.018311 | 0.1236 | 0.050354 | 0.09613 | -0.004577 | -122.0169 | -122.0947 | 0.15564 | 0.086975 | 0.004578 | 0.091552 | 0.009155 | 0.032044 | -121.994 | -122.0215 | 0.21515 | 0.18768 | 0.14191 | 0.15564 | 0.10986 | 0.16022 | 0.041198 | 0.1831 | 0.07782 | 0.11902 | 0.10528 | 0.11444 | 0.13733 | -122.1359 | -122.0993 | 0.036621 | 0.10986 | -0.045776 | 0.10986
3103.0938 | 122.2092 | -0.086975 | 122.0581 | -0.0060272 | 0.0050479 | 0.013747 | -0.012315 | -0.0010638 | -0.0096151 | -0.0040439 | -0.0051575 | 0.010275 | 0.00080103 | -0.00052768 | -0.017568 | 0.021576 | -0.0018522 | -0.086975 | 0.032043 | -0.07782 | 0.004578 | 0.12817 | -0.036621 | 0.036621 | 0.10071 | 0.041199 | -0.073242 | 0.045776 | 0.17395 | 0.10071 | 0.12817 | 0.009155 | -122.0261 | -122.0535 | 0.21515 | 0.1236 | 0.050354 | 0.11444 | 0.041199 | 0.013733 | -122.0169 | -122.0123 | 0.26092 | 0.21515 | 0.18768 | 0.20142 | 0.17395 | 0.20599 | 0.082398 | 0.24719 | 0.11902 | 0.10986 | 0.11444 | 0.11902 | 0.12817 | -122.1359 | -122.1313 | 0.091553 | 0.13275 | 0 | 0.18768
3104.7969 | 121.9757 | -0.13275 | 121.756 | -0.021286 | 0.0095341 | 0.020583 | -0.0099656 | 0.00021799 | -0.0091879 | -0.0063937 | -0.0051575 | 0.012839 | 0.0027236 | -0.0015957 | -0.014578 | 0.016449 | -0.0012112 | -0.13733 | 0.059509 | -0.1236 | -0.091553 | 0.004578 | -0.1236 | -0.050354 | -0.009155 | 0.082397 | -0.082397 | 0 | 0.091553 | 0.004578 | 0.068665 | 0.009155 | -121.6965 | -121.8475 | 0.13733 | 0.082397 | 0.009155 | 0.073242 | 0 | 0.050354 | -121.6736 | -121.756 | 0.2243 | 0.20142 | 0.13733 | 0.15106 | 0.086975 | 0.12817 | 0.032043 | 0.17395 | 0.082397 | 0.1831 | 0.16479 | 0.19226 | 0.21515 | -121.8796 | -121.8384 | 0.041198 | 0.13275 | -0.004578 | 0.1236
3106.5625 | 122.2 | -0.082397 | 122.0398 | -0.013657 | 0.0080387 | 0.020369 | -0.009752 | 0.0027814 | -0.010897 | -0.0027621 | -0.0051575 | 0.01113 | 0.0010146 | 0.0022495 | -0.016287 | 0.02179 | 0.0002842 | -0.12817 | 0.009155 | -0.086975 | -0.022888 | 0.086975 | -0.09613 | 0 | 0.054932 | 0.027466 | -0.073242 | 0.032043 | 0.14191 | 0.041199 | 0.086975 | -0.004578 | -122.0306 | -122.0627 | 0.16937 | 0.082397 | -0.013733 | 0.086975 | -0.009155 | 0.009155 | -122.0123 | -122.0078 | 0.2243 | 0.16937 | 0.1236 | 0.16022 | 0.11444 | 0.17395 | 0.064087 | 0.21515 | 0.10529 | 0.09613 | 0.10071 | 0.091552 | 0.10986 | -122.1268 | -122.113 | 0.059509 | 0.11444 | -0.045777 | 0.13733
3108.3281 | 122.2275 | -0.082397 | 122.0627 | -0.0060272 | 0.0041935 | 0.017805 | -0.01317 | 0.00064519 | -0.0094015 | -0.0063937 | -0.0021057 | 0.010275 | 0.0022964 | -0.0026639 | -0.017141 | 0.022858 | -0.0012112 | -0.13733 | 0.036621 | -0.091553 | -0.045776 | 0.064087 | -0.086975 | 0.004578 | 0.059509 | 0.050354 | -0.059509 | 0.036621 | 0.16937 | 0.073242 | 0.11902 | -0.009156 | -122.0261 | -122.1085 | 0.14648 | 0.086975 | -0.004578 | 0.096131 | 0.004578 | 0.022888 | -122.0123 | -122.0261 | 0.25177 | 0.20142 | 0.15564 | 0.17853 | 0.13275 | 0.15564 | 0.045777 | 0.22888 | 0.09613 | 0.12817 | 0.10986 | 0.11902 | 0.13275 | -122.1542 | -122.1222 | 0.036621 | 0.11902 | -0.054932 | 0.14191
3110.0938 | 121.9299 | -0.13733 | 121.7148 | -0.013657 | -0.0020017 | 0.0032791 | -0.013597 | -0.004909 | -0.02521 | -0.020066 | -0.0051575 | 0.013052 | -0.001976 | -0.0071499 | -0.017141 | 0.011108 | -0.0014248 | -0.14648 | 0.032043 | -0.11902 | -0.11444 | -0.027466 | -0.20142 | -0.10071 | -0.054932 | 0.086975 | -0.068665 | -0.054932 | 0.045776 | -0.068665 | 0.022888 | 0.01831 | -121.6827 | -121.8292 | 0.10986 | 0.036621 | -0.064087 | 0.018311 | -0.082397 | 0.068664 | -121.6278 | -121.7697 | 0.18311 | 0.16022 | 0.068664 | 0.091553 | 0 | 0.091553 | 0.004578 | 0.11444 | 0.013733 | 0.15106 | 0.15564 | 0.16937 | 0.2243 | -121.8338 | -121.7834 | 0.022888 | 0.082397 | -0.009155 | 0.082397
3111.8594 | 122.1954 | -0.09613 | 122.0901 | -0.013657 | 0.0069705 | 0.017165 | -0.011888 | -0.0010638 | -0.0094015 | -0.0053257 | -0.0051575 | 0.010916 | 0.00037383 | -0.0058683 | -0.015859 | 0.019867 | 0.0017794 | -0.14191 | 0.032043 | -0.10529 | -0.054932 | 0.054932 | -0.10986 | -0.018311 | 0.022888 | 0.045776 | -0.07782 | 0.027466 | 0.15564 | 0.045776 | 0.10529 | -0.009156 | -122.0581 | -122.1451 | 0.15106 | 0.077819 | -0.013733 | 0.086975 | -0.004577 | 0.01831 | -122.0444 | -122.0627 | 0.25177 | 0.20142 | 0.14191 | 0.18311 | 0.1236 | 0.16022 | 0.050354 | 0.23346 | 0.10529 | 0.13733 | 0.1236 | 0.12817 | 0.14191 | -122.1954 | -122.168 | 0.041198 | 0.1236 | -0.045777 | 0.11902
3113.5625 | 122.1313 | -0.13275 | 122.1176 | -0.0060272 | 0.0056887 | 0.017592 | -0.010606 | -0.001491 | -0.0089743 | -0.0031895 | -0.0082093 | 0.012625 | 0.0037918 | 0.0082309 | -0.018423 | 0.023071 | -0.0009976 | -0.18768 | 0.068665 | -0.12817 | -0.1236 | -0.027466 | -0.15106 | -0.045776 | -0.054932 | 0.086975 | -0.10986 | -0.054932 | 0.041199 | -0.036621 | 0.032043 | 0.004577 | -122.049 | -122.2412 | 0.10529 | 0.086975 | -0.018311 | 0.082398 | -0.022888 | 0.022888 | -122.0306 | -122.1725 | 0.17395 | 0.16479 | 0.09613 | 0.14191 | 0.073242 | 0.10071 | 0.004578 | 0.15106 | 0.054931 | 0.19684 | 0.19684 | 0.20142 | 0.21973 | -122.2458 | -122.2275 | 0.009155 | 0.077819 | -0.054932 | 0.077819
3115.3281 | 121.9849 | -0.1236 | 122.1359 | 0.0016023 | -0.0058469 | 0.10902 | -0.011675 | 0.048069 | 0.052335 | -0.01857 | -0.0082093 | 0.013693 | -0.0090256 | -0.0037321 | -0.017996 | 0.009613 | -0.0009976 | -0.14648 | 0.068665 | -0.13275 | -0.10071 | -0.004578 | -0.16479 | -0.082397 | -0.032043 | 0.082397 | -0.073242 | -0.032043 | 0.045776 | -0.064087 | 0.027466 | -0.009155 | -122.0673 | -122.2366 | 0.11902 | 0.041199 | -0.041199 | 0.050354 | -0.032044 | 0.050354 | -122.0535 | -122.168 | 0.16937 | 0.15106 | 0.059509 | 0.10071 | 0.009155 | 0.12817 | 0.032043 | 0.11902 | 0.041199 | 0.20142 | 0.15564 | 0.19226 | 0.20599 | -122.2687 | -122.2092 | 0.022888 | 0.091553 | -0.022888 | 0.091553
3117.0938 | 122.0627 | -0.10529 | 122.1222 | -0.0060272 | 0.0067569 | 0.022719 | -0.011461 | -0.0085406 | -0.0091879 | -0.01088 | 0.0009461 | 0.013266 | 0.001442 | 0.0090853 | -0.013296 | 0.01709 | -0.0018522 | -0.13733 | 0.073242 | -0.10986 | -0.073242 | 0.032043 | -0.13275 | -0.054932 | 0.018311 | 0.07782 | -0.068665 | 0.013733 | 0.12817 | 0.013733 | 0.086975 | -0.004577 | -122.049 | -122.1954 | 0.13733 | 0.050354 | -0.027465 | 0.054931 | -0.022888 | 0.036621 | -122.0444 | -122.1085 | 0.23346 | 0.19226 | 0.11902 | 0.15564 | 0.082398 | 0.14191 | 0.036621 | 0.19684 | 0.082398 | 0.18311 | 0.14649 | 0.17853 | 0.18311 | -122.2321 | -122.1909 | 0.032044 | 0.11902 | -0.032043 | 0.1236
3118.7812 | 122.287 | -0.091553 | 122.081 | -0.013657 | 0.0065433 | 0.028487 | -0.01317 | -0.0032 | -0.011324 | -0.0031895 | -0.0051575 | 0.01113 | 0.0029372 | -0.0026639 | -0.015432 | 0.020508 | 0.000925 | -0.11444 | 0.018311 | -0.082397 | -0.004578 | 0.13733 | -0.027466 | 0.050354 | 0.11444 | 0.032043 | -0.064087 | 0.086975 | 0.2243 | 0.14191 | 0.13733 | 0.009156 | -122.0627 | -122.0856 | 0.22888 | 0.14191 | 0.064087 | 0.13275 | 0.054931 | 0.027466 | -122.049 | -121.994 | 0.31586 | 0.22888 | 0.23346 | 0.20142 | 0.20599 | 0.21973 | 0.077819 | 0.28839 | 0.15106 | 0.10071 | 0.09613 | 0.10986 | 0.1236 | -122.1634 | -122.1451 | 0.086975 | 0.17853 | -0.022888 | 0.20599
3120.5469 | 122.2412 | -0.082397 | 122.0856 | -0.0060272 | 0.0024845 | 0.027418 | -0.014665 | -0.001491 | -0.011324 | -0.0051121 | -0.0051575 | 0.010275 | 0.0010146 | 0.00011332 | -0.016287 | 0.021576 | -0.0003568 | -0.15564 | 0.022888 | -0.09613 | -0.073242 | 0.050354 | -0.10529 | -0.004578 | 0.009155 | 0.059509 | -0.068665 | 0.018311 | 0.15564 | 0.064087 | 0.11444 | -0.013733 | -122.0627 | -122.1588 | 0.13275 | 0.077819 | -0.022889 | 0.091552 | -0.009156 | 0.013732 | -122.0261 | -122.0673 | 0.23804 | 0.19684 | 0.14648 | 0.18311 | 0.13275 | 0.14648 | 0.022888 | 0.22431 | 0.086976 | 0.11902 | 0.12817 | 0.10528 | 0.14191 | -122.1817 | -122.1542 | 0.009155 | 0.10071 | -0.073243 | 0.091552
3122.25 | 122.0306 | -0.32501 | 121.8475 | -0.013657 | -0.0026425 | 0.45253 | -0.013384 | -0.014095 | 0.056608 | -0.014298 | -0.0051575 | 0.0094208 | -0.0062486 | -0.011636 | -0.018637 | 0.005127 | 0.0004978 | -0.15106 | 0.009155 | -0.25635 | -0.091553 | 0.036621 | -0.27466 | -0.082397 | 0.041199 | 0.068665 | -0.07782 | -0.004578 | 0.10529 | -0.018311 | 0.073242 | 0.068664 | -121.8384 | -121.9391 | 0.36163 | 0.24262 | 0.050354 | 0.17395 | -0.01831 | 0.24719 | -121.7789 | -121.8521 | 0.4303 | 0.39825 | 0.3067 | 0.15106 | 0.059509 | 0.29297 | 0.1648 | 0.18311 | 0.073242 | 0.2655 | 0.14649 | 0.33417 | 0.39368 | -122.1039 | -121.9254 | 0.23346 | 0.32043 | 0.17395 | 0.36621
3124.0156 | 122.1359 | -1.03 | 120.9915 | -0.0060272 | 0.0003483 | 2.4834 | -0.01082 | -0.0036274 | -0.0091879 | -0.0012669 | -0.0051575 | 0.010489 | 0.0027236 | 0.00011332 | -0.017141 | 0.021576 | -0.000784 | -0.25177 | -0.17853 | -0.81024 | -0.18768 | 0.004578 | -0.64087 | -0.15106 | 0.09613 | 0.036621 | -0.041199 | 0.059509 | 0.19684 | 0.10529 | 0.1236 | 0.21973 | -121.17 | -121.1792 | 1.0345 | 0.87891 | 0.3891 | 0.65918 | 0.16937 | 0.98877 | -120.9549 | -120.932 | 1.2268 | 1.1536 | 1.1353 | 0.16479 | 0.14649 | 0.81482 | 0.62256 | 0.23804 | 0.10071 | 0.63171 | 0.07782 | 0.85144 | 1.0666 | -121.8018 | -121.0327 | 0.84228 | 1.0895 | 0.7782 | 1.1261
3125.7812 | 121.7789 | -1.7761 | 119.9112 | -0.20439 | -0.013537 | 5.2819 | 0.019301 | -0.0025592 | -0.01047 | 0.0025783 | -0.0051575 | 0.011557 | 0.0018692 | -0.0018093 | -0.016928 | 0.021362 | -0.0029202 | -0.49896 | -0.27008 | -1.4648 | -0.33417 | -0.027466 | -1.0757 | -0.17395 | 0.091553 | 0.041199 | -0.064087 | 0.09613 | 0.22888 | 0.14648 | 0.16937 | 0.31128 | -120.1813 | -120.2454 | 1.7487 | 1.6022 | 0.70038 | 1.2909 | 0.3891 | 1.712 | -119.87 | -119.8151 | 2.005 | 1.9455 | 1.9226 | 0.23346 | 0.21057 | 1.4374 | 1.1307 | 0.29297 | 0.16022 | 1.1948 | 0.10529 | 1.506 | 1.8173 | -121.376 | -119.9753 | 1.442 | 1.8723 | 1.2772 | 1.8677
3127.5 | 121.3165 | -2.8976 | 118.2358 | -0.34935 | -0.0002927 | 7.1045 | -0.0035568 | 0.00085879 | -0.0083335 | 0.0066373 | -0.0021057 | 0.012411 | -0.0015488 | 0.00032692 | -0.016928 | 0.022217 | -0.0074064 | -0.40283 | -0.3891 | -2.2797 | -0.50812 | -0.13733 | -1.8402 | -0.36621 | 0.15564 | 0.054932 | -0.054932 | 0.073242 | 0.21973 | 0.1236 | 0.14191 | 0.61798 | -118.6249 | -118.7439 | 2.7603 | 2.5314 | 1.0574 | 1.9135 | 0.43945 | 2.8427 | -118.1808 | -118.1625 | 3.1174 | 3.0396 | 3.0212 | 0.19684 | 0.17853 | 2.1423 | 1.7715 | 0.27466 | 0.12817 | 1.8906 | 0.10986 | 2.5085 | 2.9526 | -120.5154 | -118.2907 | 2.3895 | 2.9709 | 2.4948 | 3.0533
3129.1875 | 121.7056 | -67.6666 | 54.9088 | -0.0060272 | -0.0081967 | 0.0041337 | -0.013811 | 0.0021406 | -0.010897 | -0.0055393 | -0.0051575 | 0.01113 | 0.0029372 | -0.0062955 | -0.016073 | 0.021149 | -0.0022794 | -0.28839 | 0.045776 | 0.10986 | -0.15564 | -0.18768 | -0.42114 | -0.33875 | -0.009155 | -0.17853 | 0.28381 | -0.032043 | -0.16479 | -0.3067 | -0.26093 | 67.7765 | -54.863 | -55.0644 | 67.4789 | 67.3279 | 67.2455 | -0.44861 | -0.53101 | 67.9504 | -55.0873 | -54.9408 | 67.5018 | 67.4057 | 67.3599 | -0.54474 | -0.59051 | -0.29755 | -0.2655 | -0.44861 | -0.31586 | -0.064087 | -0.46234 | 67.7124 | 67.4881 | -54.7989 | -54.6249 | 67.511 | 67.6346 | 67.3782 | 67.6575
3130.9375 | 121.701 | -89.5203 | 32.0023 | -0.021286 | -0.0077695 | 0.0030655 | -0.014452 | -0.00042301 | -0.014315 | -0.00062587 | -0.020416 | 0.010489 | 0.00058743 | 0.00075412 | -0.015432 | 0.020081 | 0.0013522 | -0.56305 | 0.027466 | -0.054932 | -0.018311 | 0.041199 | -0.41199 | -0.14648 | 0.073242 | 0.036621 | 0.045776 | 0.032043 | 0.1236 | -0.068665 | -0.073242 | 89.4653 | -31.9748 | -32.0206 | 89.5615 | 89.3738 | 89.1083 | -0.091552 | -0.35706 | 89.566 | -31.9656 | -31.9702 | 89.6439 | 89.447 | 89.4516 | -0.11902 | -0.11444 | 0.096131 | 0.036621 | 0.07782 | -0.013733 | 0.082398 | -0.009155 | 89.5477 | 89.5569 | -32.0572 | -31.9565 | 89.502 | 89.5523 | 88.9572 | 89.5935
3132.7031 | 121.8155 | -80.4565 | 40.8829 | -0.013657 | -0.0064877 | 0.0041337 | -0.01552 | -0.0036274 | -0.01346 | -0.0019077 | -0.035675 | 0.011984 | 0.00251 | -0.0013821 | -0.0165 | 0.020081 | -0.000784 | -1.1261 | 0.032043 | -0.086975 | -0.068665 | 0.064087 | -0.56305 | -0.07782 | 0.041199 | 0.059509 | -0.059509 | 0.045776 | 0.10986 | 0.036621 | 0.091553 | 80.3696 | -40.8508 | -40.9515 | 80.5206 | 80.3787 | 79.8935 | 0.009155 | -0.47607 | 80.397 | -40.8234 | -40.8371 | 80.5664 | 80.5481 | 80.4932 | 0.15106 | 0.09613 | 0.15106 | 0.01831 | 0.16937 | 0.10528 | 0.11902 | 0.11902 | 80.4886 | 80.5161 | -40.9698 | -40.9424 | 80.3879 | 80.5023 | 79.3304 | 80.4977
3134.4688 | 121.6141 | -85.1349 | 36.0718 | 0.0016023 | -0.0079831 | 0.0043473 | -0.015306 | -0.0010638 | -0.013247 | -0.0027621 | -0.19742 | 0.0023712 | 0.0016556 | 0.00075412 | -0.015219 | 0.017944 | -0.0029202 | -1.1627 | 0.064087 | -0.10529 | -0.10529 | -0.23804 | -0.89264 | -0.19226 | -0.032043 | 0.086975 | -0.091553 | -0.009155 | 0.050354 | -0.37537 | 0.10071 | 85.0296 | -36.0077 | -36.1771 | 84.8969 | 84.9426 | 84.2422 | -0.086975 | -0.78735 | 85.0433 | -35.9848 | -36.0809 | 85.1852 | 85.2356 | 84.7595 | 0.19226 | -0.28381 | -0.13275 | 0 | 0.14191 | 0.082398 | 0.16937 | 0.17853 | 85.199 | 85.2219 | -36.1771 | -36.1633 | 85.0296 | 85.1257 | 83.9722 | 85.1028
3136.2344 | 121.5775 | -90.2847 | 31.0089 | -0.021286 | -0.0062741 | 0.00050205 | -0.015733 | 0.0055584 | -0.011324 | -0.0036167 | -0.047882 | -0.0051056 | -0.0015488 | -0.0043729 | -0.025472 | 0.0072632 | -0.016592 | -0.36621 | 0.064087 | -0.10071 | -0.07782 | -0.1831 | -0.49896 | 0.10529 | 0.013733 | 0.07782 | -0.064087 | 0.018311 | 0.091553 | -0.31586 | 0.10529 | 90.184 | -30.9448 | -31.0867 | 90.1016 | 90.39 | 89.7858 | 0.20599 | -0.39825 | 90.2206 | -30.9311 | -30.9906 | 90.3763 | 90.39 | 89.9689 | 0.16937 | -0.25177 | -0.082397 | 0.022888 | 0.15564 | 0.082398 | 0.1648 | 0.14191 | 90.3488 | 90.3625 | -31.1096 | -31.073 | 90.2069 | 90.303 | 89.9185 | 90.2985
3137.9531 | 121.3074 | -63.533 | 57.5912 | -0.013657 | -0.0077695 | 0.0011429 | -0.014452 | -0.0042682 | -0.013247 | -0.0031895 | -0.15164 | 0.0094208 | 0.0012282 | 0.0056675 | -0.017141 | 0.020935 | 0.0019932 | -0.43488 | 0.036621 | -0.086975 | -0.022888 | 0.10529 | -0.12817 | -0.16022 | 0.059509 | 0.07782 | -0.054932 | 0.041199 | 0.13275 | 0.027466 | -0.050354 | 63.446 | -57.5546 | -57.6141 | 63.6383 | 63.3728 | 63.4048 | -0.073242 | -0.041199 | 63.4781 | -57.5134 | -57.55 | 63.6658 | 63.4827 | 63.5605 | 0.004578 | 0.082398 | 0.19226 | 0.064087 | 0.18768 | 0.096131 | 0.1236 | 0.13275 | 63.5696 | 63.6108 | -57.6782 | -57.6462 | 63.5101 | 63.5742 | 63.0981 | 63.5925
3139.7031 | 120.6573 | -46.2891 | 74.7162 | -0.021286 | -0.0084103 | 0.0064835 | -0.018083 | 0.00064519 | -0.012606 | -0.0023349 | -0.090607 | 0.008139 | 0.0016556 | -0.0099271 | -0.015219 | 0.0074768 | -0.0022794 | -0.16479 | 0.022888 | -0.082397 | -0.004578 | 0.11902 | 0.10529 | -0.018311 | 0.1236 | 0.5722 | -0.004578 | 0.10071 | 0.19226 | 1.0162 | 0.07782 | 46.2067 | -74.6933 | -74.7208 | 46.4081 | 46.2708 | 46.3943 | 0.064086 | 0.18768 | 46.2845 | -74.144 | -74.6155 | 46.4813 | 46.3669 | 47.3053 | 0.082398 | 1.0208 | 0.20142 | 0.077819 | 0.19684 | 0.10529 | 0.10528 | 0.57678 | 46.312 | 46.8613 | -74.7986 | -74.7208 | 46.2845 | 46.3898 | 46.1243 | 46.4127
3141.4531 | 121.7651 | -72.757 | 48.5138 | -0.021286 | -0.0054197 | 0.0049881 | -0.015093 | -0.0046954 | -0.0087607 | -0.0053257 | -0.084503 | 0.010489 | 0.0016556 | 0.00032692 | -0.01415 | 0.02243 | 0.0049838 | -0.20142 | 0.027466 | 0.018311 | -0.045776 | -0.004578 | -0.20599 | -0.14648 | 0.032043 | -0.16479 | 0.31586 | 0.004578 | 0.11902 | 0.032043 | 0.054932 | 72.7753 | -48.4863 | -48.5596 | 72.7524 | 72.6105 | 72.551 | -0.16479 | -0.22431 | 73.0728 | -48.6786 | -48.5092 | 72.876 | 72.8119 | 72.789 | -0.26093 | -0.28381 | -0.022889 | -0.064087 | -0.19684 | -0.31128 | 0.009155 | -0.48065 | 72.7844 | 72.5922 | -48.4955 | -48.1979 | 72.7112 | 72.7615 | 72.5555 | 72.789
3143.2031 | 121.637 | -80.1453 | 41.2033 | -0.013657 | -0.0079831 | 0.0056291 | -0.01552 | -0.0010638 | -0.01047 | -0.0059665 | -0.10587 | 0.0089934 | 0.0016556 | -0.0075773 | -0.017782 | 0.021149 | 0.003702 | -0.19684 | 0.027466 | -0.068665 | -0.050354 | -0.013733 | -0.2243 | -0.16937 | 0.045776 | -0.11444 | 0.32959 | 0.041199 | 0.14191 | 0.018311 | 0.050354 | 80.0766 | -41.1758 | -41.2537 | 80.1315 | 79.9759 | 79.921 | -0.10071 | -0.15564 | 80.4749 | -41.3177 | -41.1621 | 80.2872 | 80.1956 | 80.1636 | -0.27924 | -0.31128 | 0.054932 | 0.018311 | -0.18768 | -0.28839 | 0.096131 | -0.44403 | 80.1727 | 80.0308 | -41.272 | -40.8737 | 80.0949 | 80.1865 | 79.9484 | 80.191
3144.8906 | 121.1517 | -1.3 | 120.52 | -0.013657 | -0.0081967 | 0.0028519 | -0.016588 | -0.0040546 | -0.010256 | -0.0048985 | -0.23709 | 0.010489 | 0.0040054 | -0.0052273 | -0.019277 | 0.020508 | -0.0014248 | -0.17395 | 0.018311 | 0.027466 | -0.21515 | -0.2655 | -0.43945 | -0.35706 | -0.13275 | 0.004578 | -0.09613 | -0.19684 | -0.27008 | -0.36621 | -0.32044 | 1.3275 | -120.5017 | -120.7352 | 1.0345 | 0.94299 | 0.8606 | -0.38452 | -0.46692 | 1.2039 | -120.5154 | -120.7169 | 1.03 | 0.97961 | 0.93384 | -0.22431 | -0.27008 | -0.29297 | -0.24261 | -0.17395 | -0.10071 | -0.009155 | 0.10071 | 1.3184 | 1.3046 | -120.4926 | -120.6162 | 1.0849 | 1.1032 | 1.1261 | 1.1673
3146.6562 | 121.7422 | -83.8715 | 37.3489 | -0.013657 | -0.0084103 | 0.0073379 | -0.013384 | 0.0017132 | -0.011324 | -0.0044711 | -0.10587 | 0.011771 | 0.00037383 | -0.0022367 | -0.015005 | 0.022644 | -0.0003568 | -0.16937 | 0.027466 | 0 | -0.022888 | -0.018311 | -0.21973 | -0.19226 | 0.09613 | -0.25635 | 0.21515 | 0.041199 | 0.10529 | 0 | 0.050354 | 83.8715 | -37.3215 | -37.3718 | 83.8531 | 83.6792 | 83.6517 | -0.19226 | -0.21973 | 84.0866 | -37.6053 | -37.3077 | 83.9767 | 83.9218 | 83.8715 | -0.16479 | -0.21515 | -0.018311 | -0.022888 | -0.10986 | -0.17395 | 0.027466 | -0.4715 | 83.8989 | 83.6151 | -37.3489 | -37.1338 | 83.8486 | 83.9127 | 83.7021 | 83.9676
3148.3438 | 121.637 | -97.5632 | 23.7213 | -0.028916 | -0.0090513 | 0.0049881 | -0.027269 | -0.012599 | -0.01047 | -0.0061801 | 0.034515 | 0.0027984 | -0.0092392 | -0.012277 | -0.042776 | 0.0040588 | -0.012106 | -0.21515 | 0.068665 | 0.15106 | 0.09613 | 0.10071 | 0.091553 | 0.091553 | -0.20142 | 0.013733 | -0.10071 | -0.16022 | 0.086975 | 0.091553 | 0.09613 | 97.7142 | -23.6526 | -23.6252 | 97.6639 | 97.6547 | 97.6547 | -0.059509 | -0.059509 | 97.4625 | -23.7076 | -23.8815 | 97.6501 | 97.6593 | 97.6547 | 0.19684 | 0.19226 | -0.050354 | -0.054932 | 0.18768 | -0.059509 | -0.082397 | 0.11444 | 97.6318 | 97.5769 | -23.5703 | -23.822 | 97.6593 | 97.403 | 97.348 | 97.3618
3150.1094 | 121.5912 | -120.108 | 1.1627 | -0.013657 | -0.0032833 | -0.0031295 | -0.022142 | -0.00555 | -0.011965 | -0.0078891 | -0.060089 | 0.003653 | 0.00058743 | -0.0082181 | -0.014791 | 0.023071 | -0.0027066 | -0.24719 | 0.073242 | -0.041199 | -0.32959 | 0.10529 | 0.10986 | 0.07782 | -0.041199 | -0.29755 | -0.013733 | 0.004578 | -0.25177 | -0.21515 | -0.004578 | 120.0668 | -1.0895 | -1.4923 | 120.2133 | 120.1859 | 120.2179 | 0.11902 | 0.15106 | 120.0943 | -1.4603 | -1.1581 | 119.8563 | 120.1035 | 119.8929 | 0.009155 | -0.20142 | 0.14649 | -0.28839 | -0.23804 | 0.018311 | 0.11444 | -0.28381 | 120.1813 | 119.8105 | -1.2039 | -1.1765 | 119.7784 | 120.1126 | 119.8608 | 120.0668
3151.8125 | 121.5317 | -120.1401 | 1.1948 | -0.013657 | -0.011401 | -0.0082565 | -0.02086 | -0.0074726 | -0.017092 | -0.011734 | 0.058929 | -0.0012604 | -0.001976 | -0.00031408 | -0.018423 | 0.022217 | -0.0018522 | -0.19226 | 0.059509 | -0.10529 | -0.49896 | -0.87433 | 0.10986 | 0.091553 | -0.018311 | -0.018311 | 0.24719 | -0.018311 | -0.11444 | -0.36163 | -0.018311 | 120.0348 | -1.1353 | -1.6937 | 119.2657 | 120.2316 | 120.2499 | 0.19684 | 0.21515 | 120.3873 | -1.2131 | -1.2131 | 120.0256 | 120.1218 | 119.7784 | -0.2655 | -0.60882 | -0.76904 | -0.39368 | -0.36163 | -0.2655 | 0.16479 | -0.2655 | 120.1996 | 120.1218 | -1.3 | -0.94757 | 119.6411 | 120.1218 | 119.9478 | 120.1218
3153.5781 | 121.5683 | -120.108 | 1.1719 | -0.013657 | -0.0039243 | 0.0026383 | -0.01082 | 0.0025678 | -0.010043 | -0.0021213 | -0.1669 | 0.010916 | 0.0010146 | 0.0063083 | -0.016928 | 0.024567 | 7.04e-05 | -0.17853 | 0.041199 | -0.10529 | -0.16937 | -0.29755 | -0.51727 | -0.23346 | 0.032043 | 0.064087 | 0.036621 | 0.07782 | 0.12817 | -0.10986 | -0.16022 | 120.0027 | -1.1307 | -1.3412 | 119.8105 | 119.8746 | 119.5908 | -0.12817 | -0.41199 | 120.1447 | -1.1078 | -1.0941 | 120.2362 | 119.9478 | 119.9982 | -0.19684 | -0.14648 | -0.19226 | -0.064087 | 0.091553 | 0.041199 | 0.14649 | 0.027466 | 120.1492 | 120.1721 | -1.2772 | -1.1353 | 119.9387 | 120.1859 | 119.9295 | 120.1401
3155.3438 | 121.0968 | -0.054932 | 121.6278 | 0.12367 | -0.01076 | -0.00077975 | -0.017015 | -0.0040546 | -0.011751 | -0.0053257 | -0.13333 | 0.0092072 | 0.0044326 | -0.00031408 | -0.015859 | 0.018799 | 0.000925 | -0.13275 | 0.022888 | 0.11444 | -0.032043 | 0.054932 | -0.12817 | -0.10071 | 0.091553 | -0.16937 | 0.31128 | 0.068665 | 0.16479 | 0.068665 | 0.091553 | 0.16937 | -121.6049 | -121.6599 | 0.10986 | -0.045776 | -0.073242 | -0.21515 | -0.24262 | 0.36621 | -121.7972 | -121.5591 | 0.21973 | 0.14649 | 0.1236 | -0.21973 | -0.24261 | -0.059509 | -0.14648 | -0.14648 | -0.24261 | -0.091553 | -0.48065 | 0.07782 | -0.11444 | -121.5134 | -121.3165 | 0.022889 | 0.1236 | -0.077819 | 0.14649
3157.0312 | 120.7535 | 0.11902 | 107.2815 | 0.16945 | -0.01311 | 0.0024247 | -0.01851 | 0.00064519 | -0.0091879 | -0.0031895 | -0.072296 | 0.011984 | 0.004219 | 0.0045993 | -0.015005 | 0.020508 | 7.04e-05 | -0.35248 | 0.064087 | 0.09613 | -0.23346 | -0.19226 | -0.24261 | -0.13275 | 0.045776 | -0.25177 | 0.12817 | -0.027466 | -0.17853 | -0.28381 | -0.23346 | -0.022889 | -107.2174 | -107.515 | -0.31128 | -0.25177 | -0.36163 | -0.22888 | -0.33874 | 0.009155 | -107.5333 | -107.309 | -0.29755 | -0.35248 | -0.40283 | -0.36163 | -0.41199 | -0.28839 | -0.32959 | -0.3067 | -0.15564 | -0.032043 | -0.37994 | -0.054932 | -0.37079 | -107.1854 | -107.1533 | -0.35248 | -0.14649 | -0.4715 | -0.073243
3158.7969 | 119.4443 | 0.11902 | 116.6245 | 0.15419 | -0.015887 | 0.0032791 | -0.018297 | 0.00064519 | -0.01047 | -0.0031895 | 0.8829 | 0.010489 | 0.0033646 | -0.0018093 | -0.015432 | 0.02179 | 0.0022068 | -0.32501 | 0.064087 | 0.018311 | -0.23804 | -0.16022 | -0.21973 | -0.40283 | 0.045776 | -0.19684 | 0.16022 | -0.027466 | -0.19684 | -0.29755 | -0.23804 | -0.10071 | -116.5604 | -116.8625 | -0.27924 | -0.52185 | -0.33875 | -0.42114 | -0.23804 | 0.041198 | -116.8213 | -116.6519 | -0.31586 | -0.35706 | -0.41656 | -0.39825 | -0.45776 | -0.17853 | -0.25635 | -0.35706 | -0.18768 | 0.045776 | -0.35706 | -0.054932 | -0.31586 | -116.6061 | -116.4642 | -0.35706 | -0.14649 | -0.44403 | -0.073243
3160.5625 | 104.2145 | 0.17853 | 118.1534 | 0.13893 | -0.0084103 | -0.0014205 | -0.018938 | -0.0042682 | -0.011324 | -0.0051121 | -0.060089 | 0.0089934 | 0.003151 | 0.0028903 | -0.015646 | 0.020508 | -0.0012112 | -0.15106 | -0.073242 | 0.13733 | -0.20142 | -0.25635 | -0.22888 | -0.25635 | -0.045776 | -0.2243 | -0.09613 | -0.27008 | -0.013733 | 0.09613 | 0.09613 | -0.041199 | -118.2266 | -118.3548 | -0.43488 | -0.43488 | -0.40741 | -0.39368 | -0.36621 | -0.27466 | -118.3777 | -118.4235 | -0.19226 | -0.082398 | -0.082398 | 0.19226 | 0.19226 | -0.39368 | -0.33875 | 0.082397 | -0.17395 | -0.21057 | -0.12817 | -0.25177 | -0.40283 | -118.0161 | -118.2495 | -0.37994 | -0.44861 | -0.32959 | -0.2243
3162.2656 | 98.6298 | 0.004578 | 106.6315 | 0.17708 | -0.0064877 | 0.0011429 | -0.02086 | -0.00085021 | -0.012179 | -0.0068211 | 0.061981 | 0.0034392 | -0.0013352 | -0.0039457 | -0.0165 | 0.01944 | -0.0067654 | -0.16937 | -0.21973 | 0.26093 | -0.19684 | -0.21057 | 0.10071 | 0.13733 | -0.064087 | -0.15106 | -0.032043 | -0.28839 | -0.10986 | 0.1236 | 0.10986 | 0.25635 | -106.8512 | -106.8283 | -0.21515 | 0.13275 | 0.09613 | -0.1236 | -0.16022 | -0.036621 | -106.7825 | -106.9199 | -0.11444 | 0.10529 | 0.11902 | 0.14191 | 0.15564 | -0.4715 | -0.45776 | -0.07782 | -0.25635 | -0.48065 | -0.11902 | -0.22431 | -0.15564 | -106.3705 | -106.6635 | -0.20142 | -0.29297 | -0.17395 | -0.068665
3164.0156 | 91.0446 | -0.20142 | 91.571 | -0.17387 | 0.028119 | 0.10966 | -0.013384 | 0.047429 | 0.057462 | 0.051071 | 0.052826 | 0.030142 | 0.011055 | 0.0058811 | 0.26783 | 0.038025 | 0.031687 | -0.41657 | -0.082397 | 0.16937 | -0.32501 | 0.10529 | 0.1236 | 0.10986 | -0.2243 | -0.27466 | 0.045776 | -0.064087 | 0.10529 | 0.10986 | 0.10986 | 0.37079 | -91.6534 | -91.8961 | 0.3067 | 0.31128 | 0.32501 | -0.05951 | -0.045777 | 0.24719 | -91.8457 | -91.6351 | 0.3067 | 0.31128 | 0.31128 | 0.064087 | 0.064087 | -0.064087 | -0.49439 | 0.05951 | -0.10986 | -0.25177 | -0.32043 | 0.11902 | -0.073242 | -91.4017 | -91.5253 | -0.1236 | 0.13733 | -0.21515 | -0.022888
3165.7656 | 121.788 | 0.022888 | 115.8829 | 0.11604 | -0.0086239 | 0.0024247 | -0.013597 | -0.0012774 | -0.0076925 | -0.0048985 | -0.18521 | 0.010702 | 0.0012282 | -0.0048001 | -0.017996 | 0.022217 | -0.0039884 | -0.054932 | 0.045776 | -0.073242 | -0.022888 | -0.036621 | -0.3479 | -0.32044 | 0.091553 | -0.004578 | 0.14648 | 0.086975 | 0.041199 | -0.13733 | -0.09613 | -0.09613 | -115.8371 | -115.9058 | -0.059509 | -0.34332 | -0.37079 | -0.24719 | -0.27466 | 0.1236 | -115.8875 | -115.7959 | 0.018311 | -0.11902 | -0.16022 | -0.24261 | -0.28381 | 0.036621 | 0.050354 | -0.10529 | -0.059509 | 0.11902 | -0.15106 | 0.022888 | -0.027466 | -115.9561 | -115.7364 | -0.045776 | 0.064087 | -0.07782 | 0.068665
3167.4688 | 121.1426 | -0.013733 | 121.0327 | 0.10078 | -0.0060605 | 0.0015701 | -0.012529 | -0.0029864 | -0.010897 | -0.0027621 | -0.2493 | 0.0087798 | 0.0027236 | 0.0033175 | -0.0165 | 0.020294 | -0.0016384 | -0.022888 | 0.018311 | -0.086975 | 0.013733 | 0.059509 | -0.25177 | -0.32501 | 0.12817 | 0.041199 | 0.16479 | 0.086975 | 0.13733 | -0.068665 | -0.032043 | -0.073242 | -121.0144 | -121.019 | 0.073242 | -0.31128 | -0.23804 | -0.23804 | -0.16479 | 0.17853 | -120.9915 | -120.9457 | 0.15106 | -0.01831 | -0.054932 | -0.19684 | -0.23346 | 0.14648 | 0.10071 | -0.027466 | -0.07782 | 0.10529 | -0.1236 | 0.032044 | 0.054932 | -121.1197 | -120.8679 | 0.027466 | 0.10071 | -0.009155 | 0.14191
3169.2188 | 121.431 | -0.07782 | 121.2433 | 0.10841 | -0.0071285 | 0.0030655 | -0.014238 | -0.003841 | -0.0091879 | -0.0074619 | -0.13333 | 0.01113 | 0.0029372 | -0.0018093 | -0.014791 | 0.021362 | -0.0071926 | -0.054932 | 0.032043 | -0.064087 | -0.032043 | 0.091553 | -0.13275 | -0.16022 | 0.064087 | 0.041199 | 0.073242 | 0.032043 | 0.14191 | 0.013733 | 0.054932 | 0.013733 | -121.2112 | -121.2753 | 0.16937 | -0.082397 | -0.054931 | -0.09613 | -0.068664 | 0.15106 | -121.2021 | -121.2112 | 0.21973 | 0.13275 | 0.091553 | -0.01831 | -0.059509 | 0.15564 | 0.032044 | 0.068665 | -0.041199 | 0.09613 | -0.032043 | 0.10986 | 0.11902 | -121.3074 | -121.17 | 0.045777 | 0.10986 | 0.022888 | 0.14191
3170.9219 | 121.1929 | -0.018311 | 121.1105 | 0.11604 | -0.0084103 | 0.0013565 | -0.015093 | 0.0027814 | -0.010256 | -0.0053257 | -0.16995 | 0.0087798 | 0.0016556 | -0.0054409 | -0.017996 | 0.020935 | -0.0031338 | -0.009155 | 0.027466 | -0.082397 | 0.013733 | 0.15564 | -0.07782 | -0.15564 | 0.1236 | 0.041199 | 0.11902 | 0.064087 | 0.21973 | 0.013733 | 0 | -0.064086 | -121.0831 | -121.0968 | 0.17395 | -0.13733 | -0.059509 | -0.073243 | 0.004577 | 0.13733 | -121.0693 | -121.0464 | 0.23804 | 0.018311 | 0.032044 | -0.11902 | -0.10529 | 0.23804 | 0.09613 | 0.10071 | -0.054932 | 0.10986 | -0.07782 | 0.045777 | 0.05951 | -121.1929 | -120.9915 | 0.032044 | 0.082398 | 0.009156 | 0.14191
3172.6875 | 121.2891 | -0.036621 | 121.0922 | 0.11604 | -0.0071285 | 0.0028519 | -0.014024 | 0.00064519 | -0.0072653 | -0.0044711 | -0.20352 | 0.008139 | 0.001442 | -0.0071499 | -0.015432 | 0.020721 | 0.0017794 | -0.022888 | 0.009155 | -0.068665 | 0.018311 | 0.13275 | -0.15106 | -0.2243 | 0.13275 | 0.045776 | 0.022888 | 0.068665 | 0.17853 | 0.004578 | 0.013733 | -0.032044 | -121.0831 | -121.0739 | 0.16937 | -0.18768 | -0.11444 | -0.15564 | -0.082397 | 0.059509 | -121.0464 | -121.0236 | 0.21515 | 0.050354 | 0.041199 | -0.009155 | -0.01831 | 0.20142 | 0.086976 | 0.15564 | 0.045777 | 0.07782 | 0.022888 | 0.045776 | 0.082397 | -121.1609 | -121.0693 | 0.054932 | 0.10529 | 0.013733 | 0.16937
3174.4375 | 121.4401 | -0.10071 | 121.1655 | 0.12367 | -0.0088375 | 0.0019975 | -0.012529 | -0.0040546 | -0.010256 | -0.0057529 | -0.13943 | 0.010489 | 0.00080103 | -0.00095488 | -0.014364 | 0.021362 | -0.0009976 | -0.041199 | 0.009155 | -0.073242 | -0.013733 | 0.11902 | -0.10071 | -0.14648 | 0.07782 | 0.045776 | -0.036621 | 0.027466 | 0.14648 | 0.032043 | 0.045776 | 0.027466 | -121.1563 | -121.1792 | 0.21973 | -0.045776 | 0 | -0.073242 | -0.027466 | 0.064087 | -121.1197 | -121.138 | 0.24719 | 0.14648 | 0.13275 | 0.082397 | 0.068664 | 0.19226 | 0.059509 | 0.18311 | 0.064087 | 0.082397 | 0.082397 | 0.10986 | 0.14648 | -121.2387 | -121.2021 | 0.086975 | 0.12817 | 0.059509 | 0.17853
3176.1875 | 121.4951 | -0.073242 | 121.17 | 0.0092313 | -0.010974 | 7.4854e-05 | -0.013811 | -0.001491 | -0.0096151 | -0.0061801 | -0.11502 | 0.0096344 | 0.0027236 | -0.0011685 | -0.017996 | 0.020508 | -0.0029202 | -0.054932 | 0.027466 | -0.086975 | -0.013733 | 0.11444 | -0.045776 | -0.068665 | 0.10529 | 0.036621 | -0.036621 | 0.082397 | 0.20142 | 0.10071 | 0.09613 | -0.013733 | -121.1426 | -121.1838 | 0.18768 | 0.004577 | 0.027466 | 0.01831 | 0.041199 | 0.036621 | -121.1334 | -121.0876 | 0.27466 | 0.16937 | 0.17395 | 0.13275 | 0.13733 | 0.20142 | 0.073242 | 0.23804 | 0.11902 | 0.11444 | 0.073242 | 0.10071 | 0.10986 | -121.257 | -121.2067 | 0.059509 | 0.15564 | 0.01831 | 0.17853
3177.9062 | 91.0492 | -0.10986 | 114.9902 | -0.3112 | 0.027692 | 0.10924 | -0.018297 | 0.045933 | 0.056822 | 0.050644 | 0.040619 | 0.029288 | 0.0099868 | 0.0054537 | 0.26676 | 0.037384 | 0.031046 | -0.054932 | 0.050354 | -0.10986 | -0.041199 | -0.11444 | 0.064087 | 0.045776 | 0.045776 | 0.068665 | 0.10529 | -0.17853 | -0.23804 | 0.09613 | 0.09613 | 0 | -114.9399 | -115.0314 | -0.004578 | 0.15564 | 0.17395 | 0.15564 | 0.17395 | 0.21515 | -114.9216 | -115.1688 | -0.12817 | 0.20599 | 0.20599 | -0.009156 | -0.009156 | -0.004578 | 0.068664 | -0.34332 | -0.28381 | 0.16022 | -0.036621 | 0.16022 | 0.17853 | -115.1001 | -114.8849 | 0.068664 | -0.068665 | 0.054931 | 0.15564
3179.6719 | 117.0639 | 0 | 118.1351 | 0.13893 | -0.0090513 | -0.0016341 | -0.012529 | -0.0019184 | -0.011111 | -0.0040439 | -0.24319 | 0.010062 | 0.0012282 | -0.0030911 | -0.016928 | 0.020508 | -0.0054838 | -0.068665 | 0.036621 | -0.091553 | -0.068665 | 0.022888 | -0.21973 | -0.3891 | -0.022888 | 0.082397 | -0.054932 | -0.050354 | 0.032043 | -0.3067 | -0.32501 | -0.091553 | -118.0984 | -118.2037 | 0.022888 | -0.3891 | -0.21973 | -0.29755 | -0.12817 | -0.054932 | -118.0527 | -118.1854 | 0.032043 | -0.32501 | -0.3067 | -0.27008 | -0.25177 | 0.11444 | 0.022888 | 0.086975 | 0.004578 | 0.12817 | 0.13733 | 0.036621 | 0.082397 | -118.2266 | -118.19 | -0.068665 | -0.050354 | -0.068665 | -0.022888
3181.4375 | 91.127 | -0.036621 | 109.433 | 0.12367 | 0.027692 | 0.11394 | -0.028124 | -0.0027728 | 0.056181 | 0.054275 | 0.046722 | 0.02886 | 0.0099868 | -0.012704 | -0.025045 | 0.034821 | -0.066794 | -0.068665 | 0.050354 | -0.10529 | -0.054932 | 0 | -0.48523 | 0.10071 | 0.054932 | 0.091553 | -0.041199 | -0.21057 | -0.21515 | 0.10071 | 0.10529 | -0.068665 | -109.3826 | -109.4879 | 0.036621 | 0.13733 | -0.44861 | 0.20599 | -0.37994 | -0.004578 | -109.3414 | -109.6436 | -0.17853 | 0.14191 | 0.13733 | 0.14649 | 0.14191 | 0.10529 | 0.050354 | -0.17395 | -0.16937 | 0.15564 | 0.13275 | 0.086975 | 0.12817 | -109.5383 | -109.4742 | -0.018311 | -0.17395 | -0.032044 | 0.091553
3183.2031 | 116.0706 | -0.041199 | 116.7572 | 0.10841 | -0.0071285 | 0.00050205 | -0.015093 | -0.0044818 | -0.010683 | -0.0044711 | -0.20963 | 0.010702 | 0.0044326 | 0.0013949 | -0.015646 | 0.022217 | -0.003561 | -0.086975 | -0.027466 | -0.10529 | -0.091553 | 0.009155 | -0.16022 | -0.31586 | -0.018311 | 0.091553 | -0.10071 | -0.054932 | 0.059509 | -0.2243 | -0.35248 | -0.064087 | -116.7847 | -116.8488 | 0.050354 | -0.27466 | -0.11902 | -0.21057 | -0.054931 | -0.059509 | -116.6656 | -116.8121 | 0.10071 | -0.31128 | -0.18311 | -0.25177 | -0.1236 | 0.11444 | 0.013733 | 0.16022 | 0.045776 | 0.07782 | 0.19226 | 0.013733 | 0.13275 | -116.8625 | -116.8579 | -0.050354 | -0.013733 | -0.045776 | 0.022888
3184.9062 | 121.3715 | -0.064087 | 122.081 | 0.10078 | -0.0086239 | 0.0022111 | -0.013597 | -0.00020941 | -0.0094015 | -0.0038303 | -0.093659 | 0.0079254 | 0.0022964 | -0.00052768 | -0.017568 | 0.02243 | -0.0029202 | -0.013733 | 0 | -0.064087 | 0.027466 | 0.12817 | -0.082397 | -0.059509 | 0.11444 | 0.050354 | -0.041199 | 0.082397 | 0.19684 | 0.086975 | 0.086975 | 0 | -122.081 | -122.0535 | 0.19226 | 0.004578 | -0.01831 | 0.004578 | -0.01831 | 0.022888 | -122.0306 | -121.9986 | 0.26093 | 0.15106 | 0.15106 | 0.12817 | 0.12817 | 0.19226 | 0.091553 | 0.23804 | 0.1236 | 0.064087 | 0.091553 | 0.064087 | 0.11444 | -122.1451 | -122.1222 | 0.091553 | 0.14648 | 0.050354 | 0.17853
3186.6562 | 121.4996 | -0.068665 | 121.2891 | 0.085525 | -0.0079831 | 0.0015701 | -0.01317 | -0.0010638 | -0.010256 | -0.0048985 | -0.066193 | 0.010275 | 0.0040054 | -0.0030911 | -0.017141 | 0.019012 | -0.003561 | -0.041199 | 0.027466 | -0.086975 | 0.013733 | 0.13275 | -0.073242 | -0.004578 | 0.10986 | 0.027466 | -0.045776 | 0.068665 | 0.17395 | 0.064087 | 0.10986 | -0.01831 | -121.2616 | -121.2753 | 0.20142 | 0.064087 | -0.004577 | 0.082397 | 0.013733 | 0.022889 | -121.2616 | -121.2204 | 0.24261 | 0.17853 | 0.13275 | 0.15564 | 0.10986 | 0.21973 | 0.10071 | 0.21973 | 0.11444 | 0.11444 | 0.073242 | 0.096131 | 0.096131 | -121.376 | -121.3348 | 0.082398 | 0.13733 | 0.027466 | 0.17853
3188.4219 | 121.4905 | -0.073242 | 121.9711 | -0.33409 | -0.0088375 | 0.0013565 | -0.01552 | 0.0010724 | -0.010256 | -0.0057529 | -0.032623 | 0.0096344 | 0.00080103 | 0.0016085 | -0.0165 | 0.02179 | 0.0013522 | -0.036621 | 0.027466 | -0.059509 | 0.027466 | 0.15106 | -0.013733 | 0.064087 | 0.15106 | 0.041199 | -0.064087 | 0.064087 | 0.21057 | 0.1236 | 0.10071 | 0.013733 | -121.9437 | -121.9437 | 0.2243 | 0.13733 | 0.059509 | 0.1236 | 0.045776 | 0.009155 | -121.9299 | -121.907 | 0.28381 | 0.17395 | 0.19684 | 0.1648 | 0.18768 | 0.21057 | 0.086975 | 0.27466 | 0.12817 | 0.086975 | 0.10529 | 0.10071 | 0.11444 | -122.0306 | -122.0352 | 0.10071 | 0.13733 | 0.036621 | 0.2243
3190.125 | 93.5349 | -0.036621 | 92.8757 | -0.5172 | -0.016314 | -0.0046249 | -0.023424 | -0.0053362 | -0.019442 | -0.016434 | -0.24319 | -0.0042512 | -0.011375 | -0.0041593 | -0.023336 | 0.0076904 | -0.0091152 | -0.10071 | 0.050354 | -0.09613 | -0.09613 | -0.018311 | -0.19226 | -0.40741 | -0.022888 | 0.10071 | -0.086975 | -0.045776 | -0.013733 | -0.37079 | 0.09613 | -0.059509 | -92.8253 | -92.9718 | 0.01831 | -0.37079 | -0.15564 | -0.31128 | -0.096131 | -0.050354 | -92.775 | -92.9214 | 0.022888 | 0.13275 | -0.33417 | 0.1831 | -0.28381 | 0.077819 | 0 | 0.073242 | 0.041199 | 0.14648 | 0.18768 | 0.086975 | 0.13733 | -92.9718 | -92.9626 | -0.059509 | -0.009155 | -0.064087 | 0.013733
3191.875 | 121.463 | -0.068665 | 121.4081 | -0.1815 | -0.0084103 | -0.0018479 | -0.014879 | 0.0019268 | -0.0091879 | -0.0034031 | -0.014313 | 0.0094208 | 0.0012282 | -0.0011685 | -0.017141 | 0.022217 | -0.0029202 | -0.027466 | 0.045776 | -0.073242 | 0.041199 | 0.17853 | -0.013733 | 0.050354 | 0.12817 | 0.054932 | -0.054932 | 0.059509 | 0.21515 | 0.1236 | 0.1236 | -0.004577 | -121.3623 | -121.3669 | 0.24719 | 0.11902 | 0.054932 | 0.1236 | 0.059509 | 0.013733 | -121.3531 | -121.3486 | 0.28381 | 0.19226 | 0.19226 | 0.17853 | 0.17853 | 0.25177 | 0.11444 | 0.27008 | 0.11444 | 0.11902 | 0.10986 | 0.11444 | 0.1236 | -121.4813 | -121.463 | 0.10986 | 0.12817 | 0.041199 | 0.19684
3193.6406 | 100.177 | 0.20142 | 111.7767 | -0.27306 | -0.0096921 | 0.0013565 | -0.018938 | -0.007259 | -0.011965 | -0.0070347 | -0.19437 | 0.0032256 | -0.004326 | -0.0022367 | -0.015859 | 0.015381 | -0.0020658 | -0.10986 | 0.059509 | -0.10529 | -0.091553 | -0.022888 | -0.13733 | -0.2655 | -0.054932 | 0.086975 | -0.086975 | -0.036621 | 0.022888 | -0.27008 | -0.018311 | -0.3067 | -111.7172 | -111.8683 | -0.2243 | -0.46692 | -0.33875 | -0.16022 | -0.032043 | -0.28839 | -111.6898 | -111.8134 | -0.17853 | -0.21973 | -0.4715 | 0.068664 | -0.18311 | 0.082398 | 0.013733 | 0.10986 | 0.050354 | 0.16479 | 0.17395 | -0.14191 | -0.11444 | -111.882 | -111.8637 | -0.29297 | -0.23804 | -0.31128 | -0.25635
3195.3594 | 113.0859 | 0.013733 | 121.257 | -0.13573 | -0.0092649 | 7.4854e-05 | -0.014879 | -0.0019184 | -0.011751 | -0.0040439 | -0.084503 | 0.009848 | 0.0022964 | 0.0033175 | -0.017141 | 0.02243 | 0.0015658 | -0.10529 | 0.064087 | -0.11902 | -0.10529 | -0.004578 | -0.14648 | -0.12817 | -0.041199 | 0.091553 | -0.091553 | -0.059509 | 0.064087 | -0.13275 | -0.26093 | -0.13275 | -121.1929 | -121.3623 | -0.018311 | -0.14191 | -0.16022 | -0.009155 | -0.027465 | -0.10529 | -121.1655 | -121.3165 | 0.050354 | -0.27466 | -0.14648 | -0.16937 | -0.041198 | 0.11444 | 0.013733 | 0.15564 | 0.032044 | 0.18311 | 0.18311 | 0.050354 | 0.07782 | -121.376 | -121.3486 | -0.11902 | -0.073242 | -0.11902 | -0.054932
3197.1094 | 121.5088 | -0.091553 | 121.5363 | -0.09758 | -0.0073423 | -0.0014205 | -0.014452 | 0.00021799 | -0.012392 | -0.0025485 | -0.0051575 | 0.008139 | 0.0010146 | -0.0043729 | -0.017568 | 0.019226 | -0.000784 | -0.022888 | 0.018311 | -0.059509 | 0.018311 | 0.16022 | -0.013733 | 0.054932 | 0.13275 | 0.059509 | -0.045776 | 0.050354 | 0.21973 | 0.13275 | 0.13733 | 0.032044 | -121.5179 | -121.5179 | 0.25177 | 0.14649 | 0.07782 | 0.11444 | 0.045776 | 0.045777 | -121.4767 | -121.4859 | 0.31128 | 0.22888 | 0.2243 | 0.18311 | 0.17853 | 0.21973 | 0.07782 | 0.2655 | 0.09613 | 0.07782 | 0.10528 | 0.10986 | 0.15106 | -121.5958 | -121.582 | 0.10986 | 0.14191 | 0.068665 | 0.2243
3198.8125 | 121.7606 | -0.07782 | 121.8063 | 0.17708 | -0.01076 | 0.0015701 | -0.013811 | -0.0074726 | -0.0098287 | -0.0042575 | -0.0082093 | 0.0092072 | 0.00016023 | -0.0028775 | -0.016073 | 0.020081 | 0.0019932 | -0.064087 | 0.013733 | -0.073242 | -0.027466 | 0.09613 | -0.059509 | 0.013733 | 0.086975 | 0.054932 | -0.068665 | 0.054932 | 0.20599 | 0.11902 | 0.13733 | 0.004578 | -121.7926 | -121.8338 | 0.17395 | 0.091553 | 0.018311 | 0.086975 | 0.013733 | 0.009155 | -121.7514 | -121.7514 | 0.28381 | 0.21515 | 0.19684 | 0.20599 | 0.18768 | 0.16937 | 0.045776 | 0.27466 | 0.1236 | 0.086975 | 0.1236 | 0.091553 | 0.13275 | -121.8796 | -121.875 | 0.050354 | 0.13275 | 0.013733 | 0.16479
3200.5781 | 93.6172 | 0.63171 | 121.4813 | -0.27306 | -0.0043515 | 0.10795 | -0.019792 | 0.044438 | 0.056608 | 0.050644 | -0.20657 | 0.028647 | 0.00016023 | -0.0020231 | -0.088491 | 0.038879 | -0.013601 | -0.032043 | 0.054932 | -0.1236 | -0.041199 | 0.045776 | -0.10986 | -0.24261 | 0.054932 | 0.086975 | -0.050354 | -0.082397 | 0 | -0.33417 | 0.032043 | -0.75531 | -121.4264 | -121.5225 | -0.58594 | -0.87433 | -0.74158 | -0.11902 | 0.013733 | -0.68207 | -121.3943 | -121.5637 | -0.63171 | -0.59967 | -0.96588 | 0.082397 | -0.28381 | 0.16937 | 0.082397 | 0.050354 | -0.032043 | 0.17853 | 0.13733 | -0.57678 | -0.54474 | -121.6049 | -121.5317 | -0.67291 | -0.71411 | -0.66376 | -0.57678
3202.2969 | 120.5933 | 0.004578 | 121.5683 | 0.11604 | -0.022082 | -0.0067611 | -0.012956 | -0.0012774 | -0.017733 | -0.0087437 | -0.047882 | 0.011984 | 0.0029372 | 0.0033175 | -0.017568 | 0.023285 | -0.002493 | -0.10071 | 0.036621 | -0.10986 | -0.10071 | -0.013733 | -0.1831 | -0.11902 | -0.013733 | 0.07782 | -0.091553 | -0.013733 | 0.07782 | -0.07782 | -0.14191 | -0.11444 | -121.5317 | -121.669 | -0.018311 | -0.1236 | -0.18768 | -0.009156 | -0.073242 | -0.096131 | -121.4905 | -121.582 | 0.073242 | -0.14649 | -0.082398 | -0.050354 | 0.013733 | 0.09613 | 0.009155 | 0.16937 | 0.07782 | 0.14648 | 0.16937 | 0.032043 | 0.073242 | -121.6782 | -121.6599 | -0.10529 | -0.018311 | -0.10529 | -0.018311
3204.0625 | 121.5317 | -0.064087 | 121.7651 | 0.10078 | -0.0054197 | 0.0019975 | -0.012102 | 0.0014996 | -0.0091879 | -0.0034031 | -0.0021057 | 0.010275 | 0.0012282 | 0.0065219 | -0.016287 | 0.022644 | 0.0017794 | 0 | 0.009155 | -0.07782 | 0.009155 | 0.1236 | -0.054932 | 0.018311 | 0.11444 | 0.041199 | -0.027466 | 0.091553 | 0.18768 | 0.091553 | 0.14648 | -0.013733 | -121.756 | -121.756 | 0.18768 | 0.082398 | 0.009155 | 0.096131 | 0.022888 | 0.036621 | -121.7239 | -121.6736 | 0.25177 | 0.21057 | 0.15564 | 0.17395 | 0.11902 | 0.20142 | 0.086975 | 0.21515 | 0.11902 | 0.086975 | 0.068665 | 0.073242 | 0.10529 | -121.843 | -121.7926 | 0.073242 | 0.15564 | 0.064087 | 0.17853
3205.7656 | 121.4584 | -0.068665 | 121.8155 | -2.6077 | -0.0077695 | 0.00050205 | -0.014024 | -0.00020941 | -0.0094015 | -0.0014805 | -0.0051575 | 0.011343 | 0.001442 | -0.00031408 | -0.019064 | 0.020935 | -0.0012112 | -0.022888 | 0.036621 | -0.068665 | 0.018311 | 0.14191 | -0.018311 | 0.041199 | 0.10529 | 0.064087 | -0.064087 | 0.054932 | 0.19226 | 0.086975 | 0.12817 | 0 | -121.7789 | -121.7972 | 0.21057 | 0.10986 | 0.050354 | 0.10986 | 0.050354 | 0.004578 | -121.7514 | -121.7606 | 0.26093 | 0.19684 | 0.15564 | 0.19226 | 0.15106 | 0.21057 | 0.086976 | 0.25635 | 0.11902 | 0.10529 | 0.12817 | 0.10529 | 0.13275 | -121.8842 | -121.8796 | 0.086976 | 0.1236 | 0.045777 | 0.17395
3207.5156 | 96.8719 | 0.1831 | 121.3623 | -0.21202 | 0.027905 | -0.062303 | -0.025987 | -0.063015 | -0.028628 | 0.048294 | -0.093659 | 0.011771 | -0.0051804 | -0.0080045 | -0.045339 | 0.042084 | -0.014242 | -0.018311 | 0.050354 | -0.10529 | -0.041199 | 0.045776 | -0.12817 | -0.10986 | 0.050354 | 0.082397 | -0.082397 | -0.10071 | 0.027466 | -0.2243 | -0.10071 | -0.28839 | -121.312 | -121.4035 | -0.13733 | -0.29297 | -0.31128 | -0.004577 | -0.022888 | -0.2655 | -121.2799 | -121.463 | -0.15564 | -0.28381 | -0.40741 | -0.018311 | -0.14191 | 0.15106 | 0.064087 | 0.10986 | -0.018311 | 0.15564 | 0.16479 | -0.13275 | -0.10071 | -121.4676 | -121.4447 | -0.2243 | -0.28381 | -0.20142 | -0.13275
3209.2188 | 121.7468 | -0.07782 | 121.8842 | 0.10078 | -0.0088375 | 0.0024247 | -0.012743 | -0.00042301 | -0.0089743 | -0.0031895 | -0.0082093 | 0.010489 | 0.00251 | 0.00054052 | -0.016714 | 0.020935 | 0.0022068 | -0.032043 | 0.004578 | -0.086975 | 0.004578 | 0.13733 | -0.064087 | 0.027466 | 0.14191 | 0.054932 | -0.054932 | 0.064087 | 0.16937 | 0.09613 | 0.11902 | -0.009155 | -121.8796 | -121.8796 | 0.21515 | 0.10529 | 0.013733 | 0.11444 | 0.022888 | 0.022888 | -121.8292 | -121.8201 | 0.24719 | 0.19684 | 0.17395 | 0.17395 | 0.15106 | 0.2243 | 0.091553 | 0.22431 | 0.11902 | 0.091553 | 0.10986 | 0.082398 | 0.13275 | -121.9711 | -121.9391 | 0.082398 | 0.14191 | 0.045777 | 0.21973
3210.9844 | 121.8704 | -0.082397 | 122.0078 | -0.48668 | -0.0069149 | 0.0026383 | -0.014452 | -0.00042301 | -0.0087607 | -0.0048985 | -0.0051575 | 0.011557 | 0.0010146 | -0.00031408 | -0.0165 | 0.022003 | -0.0067654 | -0.041199 | 0.013733 | -0.07782 | -0.032043 | 0.10071 | -0.091553 | 0.009155 | 0.064087 | 0.050354 | -0.059509 | 0.022888 | 0.13733 | 0.045776 | 0.10529 | 0.004577 | -121.994 | -122.0398 | 0.18311 | 0.091552 | -0.009156 | 0.086975 | -0.013733 | 0.022888 | -121.9574 | -121.9849 | 0.21973 | 0.18768 | 0.12817 | 0.16479 | 0.10528 | 0.17853 | 0.045777 | 0.19684 | 0.082397 | 0.091553 | 0.10986 | 0.09613 | 0.13275 | -122.0856 | -122.0673 | 0.050354 | 0.10528 | 0.041198 | 0.14648
3212.75 | 111.2595 | 0.073242 | 121.4035 | 0.12367 | 0.027692 | 0.10924 | -0.024278 | -0.0051226 | 0.056181 | 0.05043 | -0.0051575 | -0.0029694 | -0.011375 | -0.0058683 | -0.0212 | 0.005127 | -0.009329 | -0.086975 | 0.054932 | -0.11902 | -0.11902 | -0.050354 | -0.1831 | -0.10986 | -0.073242 | 0.091553 | -0.086975 | -0.045776 | 0.027466 | -0.15564 | -0.21057 | -0.19226 | -121.3486 | -121.5225 | -0.1236 | -0.18311 | -0.25635 | 0.009156 | -0.064086 | -0.16022 | -121.3119 | -121.4493 | -0.045776 | -0.28381 | -0.22888 | -0.1236 | -0.068665 | 0.068665 | 0 | 0.11444 | 0.041199 | 0.17395 | 0.17853 | -0.01831 | 0.018311 | -121.5225 | -121.4905 | -0.19226 | -0.11902 | -0.16022 | -0.14648
3214.4531 | 121.9116 | -0.082397 | 121.9803 | -0.1281 | -0.010119 | 0.0019975 | -0.015306 | -0.0027728 | -0.0098287 | -0.0057529 | -0.0051575 | 0.0079254 | 0.0020828 | -0.0075773 | -0.017568 | 0.020935 | 0.0002842 | -0.054932 | 0.018311 | -0.073242 | 0 | 0.11444 | -0.045776 | 0.054932 | 0.11902 | 0.045776 | -0.068665 | 0.068665 | 0.2243 | 0.11902 | 0.14648 | 0.009155 | -121.962 | -121.9803 | 0.19684 | 0.13733 | 0.036621 | 0.12817 | 0.027466 | 0.013732 | -121.9345 | -121.9116 | 0.3067 | 0.22888 | 0.20142 | 0.21515 | 0.18768 | 0.18768 | 0.073242 | 0.29297 | 0.13733 | 0.091553 | 0.11444 | 0.10071 | 0.12817 | -122.0535 | -122.049 | 0.082397 | 0.15106 | 0.027465 | 0.20142
3216.2031 | 121.7285 | -0.059509 | 122.0261 | 0.10078 | -0.0073423 | 0.0030655 | -0.012956 | 0.0040632 | -0.0085471 | -0.0059665 | -0.0021057 | 0.010062 | 0.0018692 | -0.0035183 | -0.017568 | 0.023712 | -0.0018522 | -0.004578 | 0.022888 | -0.073242 | 0.018311 | 0.11902 | -0.073242 | 0.018311 | 0.1236 | 0.041199 | -0.045776 | 0.07782 | 0.19684 | 0.09613 | 0.13275 | -0.013733 | -122.0032 | -122.0078 | 0.17853 | 0.07782 | -0.013733 | 0.091553 | 0 | 0.013733 | -121.9849 | -121.9482 | 0.25635 | 0.19226 | 0.15564 | 0.17853 | 0.14191 | 0.19226 | 0.091553 | 0.24261 | 0.1236 | 0.09613 | 0.086975 | 0.082397 | 0.10071 | -122.0993 | -122.0718 | 0.07782 | 0.13733 | 0.054931 | 0.1831
3217.9844 | 121.8246 | -0.054932 | 121.9894 | 0.10841 | -0.0090513 | 0.0034927 | -0.012529 | 0.0027814 | -0.0089743 | -0.00062587 | -0.0051575 | 0.012411 | 0.0027236 | -0.0065091 | -0.016073 | 0.02243 | -0.0020658 | -0.004578 | 0.013733 | -0.059509 | 0.018311 | 0.13275 | -0.068665 | 0.032043 | 0.11902 | 0.045776 | -0.045776 | 0.082397 | 0.18768 | 0.09613 | 0.13733 | -0.004577 | -121.9757 | -121.9711 | 0.18768 | 0.086975 | -0.013733 | 0.091552 | -0.009156 | 0.009156 | -121.9437 | -121.907 | 0.24261 | 0.19226 | 0.15106 | 0.18311 | 0.14191 | 0.19226 | 0.07782 | 0.23346 | 0.12817 | 0.073242 | 0.091552 | 0.068665 | 0.10071 | -122.049 | -122.0352 | 0.073243 | 0.13733 | 0.050354 | 0.17395
3219.75 | 121.9757 | -0.07782 | 122.0535 | 0.12367 | -0.0084103 | 0.00050205 | -0.012102 | -0.0032 | -0.01047 | -0.0053257 | -0.0051575 | 0.011771 | 0.003151 | -0.00095488 | -0.016928 | 0.021362 | 0.002634 | -0.050354 | 0.018311 | -0.068665 | -0.027466 | 0.09613 | -0.10529 | 0 | 0.064087 | 0.054932 | -0.064087 | 0.032043 | 0.14191 | 0.054932 | 0.11444 | 0.009155 | -122.0352 | -122.081 | 0.17395 | 0.07782 | -0.027466 | 0.068665 | -0.036621 | 0.013733 | -121.9986 | -122.0215 | 0.21973 | 0.19226 | 0.13275 | 0.17853 | 0.11902 | 0.16479 | 0.041199 | 0.20599 | 0.09613 | 0.086976 | 0.11902 | 0.096131 | 0.13275 | -122.1222 | -122.1176 | 0.050354 | 0.10986 | 0.027466 | 0.14191
3221.5312 | 121.4172 | -0.059509 | 121.7926 | 0.11604 | -0.018451 | -0.0014205 | -0.01082 | 0.00021799 | -0.010256 | -0.0044711 | -0.0021057 | 0.012625 | 0.001442 | 0.0065219 | -0.015005 | 0.022858 | 0.0028476 | -0.073242 | 0.050354 | -0.09613 | -0.068665 | 0.004578 | -0.1831 | -0.064087 | 0.022888 | 0.073242 | -0.07782 | 0.013733 | 0.11444 | 0.018311 | 0.10071 | -0.036621 | -121.7422 | -121.8613 | 0.064087 | -0.004578 | -0.1236 | 0.032043 | -0.086975 | -0.018311 | -121.7194 | -121.7789 | 0.17395 | 0.16022 | 0.07782 | 0.17853 | 0.096131 | 0.10071 | 0.027465 | 0.19226 | 0.091553 | 0.14648 | 0.15106 | 0.10986 | 0.13275 | -121.8887 | -121.8704 | -0.009156 | 0.073242 | -0.013733 | 0.082397
3223.2344 | 121.4493 | -0.07782 | 121.8887 | -0.40276 | -0.010119 | 0.00071565 | -0.012529 | 0.0014996 | -0.010256 | -0.0046847 | -0.0021057 | 0.013693 | 0.00251 | 0.0039585 | -0.019064 | 0.023285 | -0.0033474 | -0.082397 | 0.045776 | -0.12817 | -0.086975 | 0.027466 | -0.14191 | -0.064087 | 0.036621 | 0.07782 | -0.082397 | 0.041199 | 0.14191 | 0.050354 | 0.1236 | -0.050354 | -121.843 | -121.9757 | 0.10529 | 0.013733 | -0.064087 | 0.064087 | -0.013733 | -0.004577 | -121.8109 | -121.8475 | 0.21973 | 0.20142 | 0.12817 | 0.20599 | 0.13275 | 0.15564 | 0.041199 | 0.2243 | 0.1236 | 0.17395 | 0.16022 | 0.1236 | 0.15564 | -122.0169 | -121.9711 | -0.009155 | 0.11902 | -0.004577 | 0.11444
3225.0156 | 122.0718 | -0.07782 | 122.0673 | -0.50194 | -0.0092649 | 0.00028845 | -0.015093 | -0.0061908 | -0.0094015 | -0.0023349 | -0.0021057 | 0.010702 | 0.0020828 | 0.0039585 | -0.017782 | 0.019012 | 0.0002842 | -0.027466 | 0.027466 | -0.07782 | 0.004578 | 0.14191 | -0.032043 | 0.068665 | 0.13275 | 0.050354 | -0.045776 | 0.068665 | 0.19684 | 0.11902 | 0.14191 | 0 | -122.0398 | -122.0627 | 0.21973 | 0.14649 | 0.045777 | 0.14649 | 0.045777 | 0.032044 | -122.0169 | -121.9986 | 0.27466 | 0.21973 | 0.19684 | 0.18768 | 0.16479 | 0.21973 | 0.082398 | 0.24261 | 0.11444 | 0.10529 | 0.09613 | 0.10529 | 0.12817 | -122.1451 | -122.113 | 0.082398 | 0.14649 | 0.050354 | 0.21057
3226.7188 | 122.0078 | -0.022888 | 121.962 | -0.10521 | -0.010547 | 0.10902 | -0.020433 | -0.01324 | 0.042295 | 0.02565 | -0.0051575 | 0.0034392 | -0.008812 | 0.00011332 | -0.017141 | 0.01004 | -0.0044156 | -0.086975 | 0.054932 | -0.10986 | -0.11444 | -0.064087 | -0.21515 | -0.1236 | -0.068665 | 0.082397 | -0.091553 | -0.036621 | 0.032043 | -0.054932 | -0.059509 | -0.086975 | -121.907 | -122.0764 | -0.041199 | -0.10071 | -0.19226 | -0.013733 | -0.10529 | -0.068665 | -121.8796 | -121.9986 | 0.054931 | -0.036621 | -0.032044 | 0.032044 | 0.036621 | 0.045776 | -0.004578 | 0.1236 | 0.054932 | 0.16479 | 0.17395 | 0.07782 | 0.10528 | -122.0718 | -122.0535 | -0.091553 | -0.013733 | -0.064087 | -0.045777
3228.4844 | 112.1429 | 0.013733 | 121.3898 | -0.4409 | -0.02315 | -0.0082565 | -0.014665 | -0.012813 | -0.015169 | -0.021134 | -0.0082093 | 0.0096344 | -0.010735 | 0.0018221 | -0.0212 | 0.0055542 | -0.0091152 | -0.064087 | 0.054932 | -0.13275 | -0.059509 | 0.027466 | -0.1236 | -0.054932 | 0.013733 | 0.07782 | -0.07782 | -0.009155 | 0.11902 | -0.009155 | -0.059509 | -0.14648 | -121.3348 | -121.4493 | 0.013733 | -0.068665 | -0.13733 | 0.077819 | 0.009155 | -0.091553 | -121.312 | -121.3989 | 0.10529 | -0.073242 | -0.022888 | 0.018311 | 0.068665 | 0.16022 | 0.073242 | 0.19684 | 0.068665 | 0.18768 | 0.15564 | 0.041199 | 0.064087 | -121.5225 | -121.4676 | -0.073242 | -0.022888 | -0.07782 | 0
3230.1719 | 114.4043 | -0.032043 | 121.431 | -0.0060272 | 0.027692 | 0.11052 | -0.017656 | 0.045933 | 0.058103 | 0.051071 | -0.0051575 | 0.003653 | -0.013084 | 0.0016085 | -0.021841 | 0.014099 | -0.014669 | -0.13733 | 0.059509 | -0.10986 | -0.073242 | 0.022888 | -0.15106 | -0.07782 | -0.054932 | 0.086975 | -0.082397 | -0.09613 | 0.068665 | -0.064087 | -0.09613 | -0.07782 | -121.3715 | -121.5042 | 0.054931 | -0.045777 | -0.11902 | 0.032043 | -0.041199 | -0.050354 | -121.344 | -121.5271 | 0.10071 | -0.064087 | -0.032044 | -0.013733 | 0.01831 | 0.13275 | 0.036621 | 0.15106 | -0.013733 | 0.16937 | 0.16937 | 0.091552 | 0.11902 | -121.5408 | -121.5134 | -0.041199 | -0.064087 | -0.10529 | -0.022889
3231.9375 | 122.1725 | -0.073242 | 121.8475 | -0.013657 | -0.0086239 | 0.0022111 | -0.015306 | 0.0021406 | -0.0096151 | -0.0027621 | -0.0051575 | 0.010275 | 0.0018692 | -0.0024503 | -0.015005 | 0.021149 | 0.0011386 | -0.07782 | 0.013733 | -0.07782 | -0.054932 | 0.059509 | -0.086975 | -0.004578 | 0.018311 | 0.054932 | -0.07782 | 0.027466 | 0.15106 | 0.054932 | 0.11444 | -0.004578 | -121.8338 | -121.9025 | 0.13275 | 0.068664 | -0.013733 | 0.073242 | -0.009155 | -0.004578 | -121.7926 | -121.8201 | 0.2243 | 0.18768 | 0.12817 | 0.19226 | 0.13275 | 0.13733 | 0.022888 | 0.22888 | 0.10529 | 0.091553 | 0.13275 | 0.086975 | 0.12817 | -121.9254 | -121.9254 | 0.01831 | 0.10071 | -0.004578 | 0.091553
3233.7031 | 122.2229 | -0.091553 | 121.9025 | -0.021286 | -0.0067013 | -0.00013895 | -0.016161 | -0.00085021 | -0.0098287 | -0.0055393 | -0.0051575 | 0.0089934 | 0.0016556 | -0.0045865 | -0.017141 | 0.020935 | -0.0016384 | -0.073242 | 0.045776 | -0.091553 | -0.027466 | 0.073242 | -0.07782 | 0.013733 | 0.054932 | 0.045776 | -0.086975 | 0.036621 | 0.1831 | 0.091553 | 0.12817 | 0 | -121.8567 | -121.9299 | 0.16479 | 0.10529 | 0.013733 | 0.10529 | 0.013733 | 0.004578 | -121.8567 | -121.8658 | 0.27466 | 0.21973 | 0.18311 | 0.21515 | 0.17853 | 0.16479 | 0.064087 | 0.27008 | 0.1236 | 0.13733 | 0.13275 | 0.13733 | 0.13733 | -121.994 | -121.9894 | 0.064087 | 0.12817 | 0.018311 | 0.14649
3235.3906 | 119.5496 | -0.032043 | 121.4813 | -0.34172 | -0.017596 | -0.00013895 | -0.013597 | -0.006618 | -0.011324 | -0.010025 | -0.0051575 | 0.0079254 | -0.0034714 | 0.0058811 | -0.01415 | 0.016022 | -0.0014248 | -0.091553 | 0.064087 | -0.11902 | -0.10071 | -0.009155 | -0.13275 | -0.068665 | -0.027466 | 0.09613 | -0.07782 | -0.032043 | 0.10986 | 0.004578 | 0.022888 | -0.086976 | -121.4172 | -121.582 | 0.022888 | -0.036622 | -0.10071 | 0.050354 | -0.013732 | -0.045777 | -121.3852 | -121.5134 | 0.14191 | 0.054931 | 0.036621 | 0.10071 | 0.082398 | 0.10986 | 0.018311 | 0.18768 | 0.045777 | 0.18311 | 0.17395 | 0.09613 | 0.12817 | -121.6003 | -121.5591 | -0.068665 | 0 | -0.05951 | 0.004577
3237.1562 | 117.2012 | -0.045776 | 121.4767 | -0.20439 | 0.028119 | 0.11009 | -0.019151 | 0.046788 | 0.05789 | 0.051285 | -0.0051575 | 0.001944 | 0.0091324 | -0.013345 | -0.024191 | 0.017944 | -0.011465 | -0.11902 | 0.050354 | -0.086975 | -0.059509 | 0.032043 | -0.12817 | -0.068665 | 0.013733 | 0.091553 | -0.068665 | -0.027466 | 0.068665 | -0.050354 | -0.013733 | -0.041199 | -121.4264 | -121.5363 | 0.077819 | -0.022889 | -0.082398 | 0.01831 | -0.041199 | -0.022889 | -121.3852 | -121.5042 | 0.11444 | 0.032043 | -0.004578 | 0.054932 | 0.018311 | 0.11902 | 0.027466 | 0.13733 | 0.041199 | 0.13733 | 0.16022 | 0.09613 | 0.13733 | -121.5637 | -121.5454 | -0.013733 | 0.01831 | -0.073243 | 0.059509
3238.9219 | 122.0215 | -0.086975 | 122.0306 | -0.3875 | -0.0084103 | -0.00099335 | -0.01552 | -0.0012774 | -0.011324 | -0.0040439 | -0.0051575 | 0.010489 | 0.0016556 | -0.00095488 | -0.015219 | 0.020294 | -0.0031338 | -0.036621 | 0.032043 | -0.07782 | 0.018311 | 0.16022 | -0.013733 | 0.036621 | 0.11444 | 0.050354 | -0.054932 | 0.059509 | 0.21515 | 0.10529 | 0.13275 | 0.009155 | -121.9986 | -122.0123 | 0.24719 | 0.1236 | 0.073242 | 0.11444 | 0.064087 | 0.032043 | -121.9803 | -121.9711 | 0.30212 | 0.21973 | 0.19226 | 0.18768 | 0.16022 | 0.23804 | 0.096131 | 0.27008 | 0.11444 | 0.10986 | 0.10529 | 0.11902 | 0.13733 | -122.1085 | -122.0856 | 0.10529 | 0.14648 | 0.050354 | 0.20142
3240.6875 | 122.2961 | -0.050354 | 121.4035 | -0.013657 | -0.017383 | -0.01317 | -0.013384 | -0.0081134 | -0.024142 | -0.019211 | -0.0051575 | 0.0094208 | -0.0079574 | -0.0050137 | -0.018209 | 0.010895 | -0.0050564 | -0.041199 | 0.059509 | -0.13275 | -0.050354 | 0.036621 | -0.11902 | -0.022888 | 0.018311 | 0.082397 | -0.082397 | 0 | 0.1236 | 0.013733 | 0.050354 | -0.082397 | -121.344 | -121.4539 | 0.086975 | 0.027466 | -0.068665 | 0.10986 | 0.013732 | -0.032043 | -121.3211 | -121.4035 | 0.17395 | 0.10071 | 0.064087 | 0.13275 | 0.09613 | 0.16937 | 0.082397 | 0.20599 | 0.082397 | 0.19226 | 0.16479 | 0.10986 | 0.13275 | -121.5363 | -121.4859 | 0 | 0.050354 | 0.009155 | 0.068665
3242.4531 | 122.2092 | -0.073242 | 121.6599 | -0.23491 | 0.029187 | 0.11052 | -0.016374 | 0.04636 | 0.058103 | 0.051925 | -0.0021057 | 0.00643 | 0.00016023 | -0.00052768 | -0.020132 | 0.006195 | -0.01232 | -0.15106 | 0.050354 | -0.086975 | -0.07782 | 0.018311 | -0.16479 | -0.073242 | -0.018311 | 0.07782 | -0.09613 | -0.050354 | 0.050354 | -0.036621 | 0.004578 | -0.013733 | -121.6095 | -121.7377 | 0.091553 | 0 | -0.091553 | 0.013733 | -0.07782 | -0.022888 | -121.582 | -121.7102 | 0.1236 | 0.07782 | 0.036621 | 0.10071 | 0.059509 | 0.10529 | 0.009155 | 0.14648 | 0.045776 | 0.13733 | 0.17395 | 0.1236 | 0.15106 | -121.7468 | -121.756 | -0.004578 | 0.022888 | -0.07782 | 0.054931
3244.1562 | 121.669 | -0.11444 | 121.9116 | -0.60112 | -0.0058469 | 0.00092925 | -0.016374 | 0.0010724 | -0.012179 | -0.0025485 | -0.0051575 | 0.010916 | 0.0020828 | 0.0039585 | -0.015859 | 0.022003 | 0.0004978 | -0.064087 | 0.050354 | -0.091553 | -0.082397 | 0.036621 | -0.11444 | -0.036621 | -0.013733 | 0.068665 | -0.086975 | -0.064087 | 0.082397 | -0.018311 | 0.027466 | 0.022888 | -121.8613 | -121.994 | 0.15106 | 0.07782 | 0 | 0.054932 | -0.022888 | 0.027466 | -121.843 | -121.9757 | 0.19684 | 0.14191 | 0.09613 | 0.11444 | 0.068664 | 0.12817 | 0.009156 | 0.16937 | 0.022888 | 0.14191 | 0.15564 | 0.16479 | 0.18311 | -122.0032 | -121.9986 | 0.032044 | 0.050354 | 0.050354 | 0.10071
3245.9219 | 121.6461 | -0.10071 | 121.5088 | -0.15099 | -0.012256 | -0.0035567 | -0.011675 | 0.0023542 | -0.012179 | -0.0040439 | -0.0051575 | 0.013693 | 0.0020828 | 0.0016085 | -0.0165 | 0.022217 | 0.0022068 | -0.09613 | 0.054932 | -0.09613 | -0.09613 | -0.018311 | -0.18768 | -0.073242 | -0.022888 | 0.082397 | -0.09613 | -0.018311 | 0.082397 | -0.013733 | 0.068665 | 0.004578 | -121.4539 | -121.6049 | 0.082397 | 0.027466 | -0.086975 | 0.022888 | -0.091553 | 0.004578 | -121.4264 | -121.5271 | 0.18311 | 0.16937 | 0.086975 | 0.16479 | 0.082397 | 0.077819 | 0 | 0.17853 | 0.077819 | 0.15106 | 0.17853 | 0.15564 | 0.18311 | -121.6049 | -121.6049 | 0.004578 | 0.082397 | 0.004578 | 0.07782
3247.7031 | 121.4584 | -0.12817 | 121.8933 | -0.11284 | -0.0062741 | -0.00077975 | -0.013811 | -0.003841 | -0.010897 | -0.0036167 | -0.0051575 | 0.01113 | 0.00037383 | -0.0011685 | -0.017782 | 0.023926 | -0.0027066 | -0.1236 | 0.059509 | -0.11902 | -0.10986 | 0.004578 | -0.14648 | -0.073242 | -0.045776 | 0.086975 | -0.082397 | -0.073242 | 0.054932 | -0.027466 | 0.027466 | 0.009155 | -121.8338 | -122.0032 | 0.13275 | 0.054932 | -0.01831 | 0.045777 | -0.027465 | 0.045777 | -121.8063 | -121.9666 | 0.18311 | 0.15564 | 0.10071 | 0.10986 | 0.054931 | 0.1236 | 0.009156 | 0.13733 | 0.009155 | 0.17853 | 0.16937 | 0.18768 | 0.21515 | -122.0123 | -121.9757 | 0.018311 | 0.054932 | 0.004578 | 0.082398
3249.4844 | 122.1954 | -0.073242 | 122.1497 | -0.29594 | -0.0081967 | 0.0015701 | -0.014879 | -0.0034136 | -0.013033 | -0.0046847 | -0.0021057 | 0.0096344 | 0.003151 | 0.0054537 | -0.019277 | 0.020935 | 0.0011386 | -0.032043 | 0.018311 | -0.07782 | 0.013733 | 0.15564 | -0.004578 | 0.054932 | 0.11444 | 0.059509 | -0.059509 | 0.054932 | 0.21515 | 0.10529 | 0.12817 | -0.004578 | -122.1313 | -122.1359 | 0.22888 | 0.12817 | 0.068664 | 0.13275 | 0.073242 | 0.013733 | -122.0901 | -122.0947 | 0.28839 | 0.20142 | 0.17853 | 0.18768 | 0.16479 | 0.23346 | 0.091553 | 0.27466 | 0.11444 | 0.096131 | 0.11902 | 0.091553 | 0.13275 | -122.2275 | -122.2092 | 0.086975 | 0.12817 | 0.041199 | 0.18768
3251.1719 | 121.6095 | -0.11444 | 121.8613 | -0.60112 | -0.0090513 | 0.00071565 | -0.013384 | -0.0017048 | -0.012179 | -0.0025485 | -0.0051575 | 0.012198 | 0.0018692 | 0.0018221 | -0.0165 | 0.02179 | 0.000925 | -0.10986 | 0.045776 | -0.13733 | -0.11444 | -0.018311 | -0.12817 | -0.054932 | -0.073242 | 0.073242 | -0.10529 | -0.07782 | 0.054932 | -0.009155 | 0.027466 | -0.022888 | -121.8155 | -121.9757 | 0.09613 | 0.059509 | -0.013733 | 0.082397 | 0.009155 | 0.009155 | -121.788 | -121.9391 | 0.16937 | 0.14191 | 0.10529 | 0.13275 | 0.096131 | 0.11902 | 0.022888 | 0.16022 | 0.027466 | 0.18311 | 0.17853 | 0.16022 | 0.18768 | -121.9986 | -121.9666 | 0 | 0.036621 | 0.004578 | 0.041199
3252.9844 | 122.2916 | -0.073242 | 121.962 | 0.0016023 | -0.0052059 | 0.0013565 | -0.013811 | 0.0025678 | -0.010897 | -0.0046847 | -0.0082093 | 0.011343 | 0.0022964 | 0.0013949 | -0.019064 | 0.020294 | 0.0028476 | -0.013733 | 0.009155 | -0.09613 | 0.022888 | 0.13733 | -0.050354 | 0.018311 | 0.11444 | 0.036621 | -0.036621 | 0.07782 | 0.1831 | 0.086975 | 0.13733 | -0.022888 | -121.9528 | -121.9391 | 0.21057 | 0.091553 | 0.022888 | 0.11444 | 0.045776 | 0.036621 | -121.9254 | -121.8842 | 0.25635 | 0.21057 | 0.16022 | 0.17395 | 0.1236 | 0.23346 | 0.11902 | 0.21973 | 0.11444 | 0.10528 | 0.073242 | 0.082397 | 0.10986 | -122.0581 | -121.9986 | 0.09613 | 0.15106 | 0.059509 | 0.18768
3256.1875 | 121.9482 | -0.10529 | 122.1497 | -0.1281 | -0.0073423 | 0.0013565 | -0.014452 | -0.0034136 | -0.010897 | -0.0046847 | -0.0051575 | 0.0094208 | 0.0018692 | -0.0013821 | -0.015646 | 0.023926 | -0.0001432 | -0.036621 | 0.022888 | -0.086975 | -0.022888 | 0.091553 | -0.050354 | 0 | 0.018311 | 0.073242 | -0.064087 | -0.032043 | 0.10986 | 0.013733 | 0.059509 | 0.018311 | -122.1268 | -122.1725 | 0.19684 | 0.10529 | 0.054932 | 0.086975 | 0.036621 | 0.041199 | -122.0764 | -122.1817 | 0.21515 | 0.16479 | 0.11902 | 0.1236 | 0.07782 | 0.17853 | 0.064087 | 0.17395 | 0.032044 | 0.10986 | 0.13733 | 0.12817 | 0.17853 | -122.2366 | -122.2137 | 0.082398 | 0.073243 | 0.068665 | 0.1236
3260.4844 | 121.9528 | -0.086975 | 122.2 | -0.43327 | -0.011828 | 0.00028845 | -0.011247 | -0.00042301 | -0.011751 | -0.0048985 | -0.0021057 | 0.01348 | 0.0029372 | 0.0080173 | -0.018637 | 0.024139 | -0.0039884 | -0.09613 | 0.009155 | -0.12817 | -0.091553 | 0 | -0.17395 | -0.068665 | 0.004578 | 0.086975 | -0.086975 | 0.004578 | 0.11444 | -0.004578 | 0.082397 | -0.041199 | -122.1909 | -122.2916 | 0.086975 | 0.01831 | -0.086975 | 0.059509 | -0.045776 | 0 | -122.113 | -122.1954 | 0.20142 | 0.16937 | 0.082397 | 0.16937 | 0.082397 | 0.12817 | 0.036621 | 0.20142 | 0.091553 | 0.13733 | 0.17395 | 0.09613 | 0.17395 | -122.3282 | -122.287 | -0.004578 | 0.091553 | -0.009155 | 0.091553
3266.3125 | 121.4767 | -0.091553 | 122.0581 | -0.2578 | -0.019305 | -0.0067611 | -0.017015 | -0.015163 | -0.019656 | -0.014939 | 0.0039977 | 0.012839 | -0.0066758 | -0.0067227 | -0.01885 | 0.012177 | -0.00527 | -0.064087 | 0.045776 | -0.10529 | -0.068665 | 0.027466 | -0.11902 | -0.045776 | 0.009155 | 0.068665 | -0.082397 | 0 | 0.10986 | 0.004578 | 0.082397 | -0.013733 | -122.0123 | -122.1268 | 0.11902 | 0.045777 | -0.027466 | 0.05951 | -0.013733 | 0.009156 | -121.9894 | -122.0581 | 0.20142 | 0.17395 | 0.096131 | 0.16479 | 0.086975 | 0.13275 | 0.036621 | 0.19226 | 0.082397 | 0.15106 | 0.15106 | 0.13733 | 0.16022 | -122.1634 | -122.1405 | 0.022888 | 0.091553 | 0.027466 | 0.10071
3268 | 122.2321 | -0.07782 | 122.1863 | -0.2578 | -0.0056333 | 0.0045609 | -0.012743 | 0.00043159 | -0.010256 | -0.0048985 | -0.0051575 | 0.010702 | 0.0012282 | -0.0026639 | -0.017782 | 0.024353 | 0.0011386 | -0.050354 | 0.050354 | -0.09613 | -0.032043 | 0.082397 | -0.10071 | 0 | 0.082397 | 0.050354 | -0.059509 | 0.086975 | 0.1831 | 0.073242 | 0.14191 | -0.01831 | -122.1359 | -122.2183 | 0.16022 | 0.07782 | -0.022888 | 0.09613 | -0.004578 | 0.018311 | -122.1359 | -122.0993 | 0.26092 | 0.21973 | 0.15106 | 0.20142 | 0.13275 | 0.17853 | 0.064087 | 0.24261 | 0.14648 | 0.14648 | 0.10986 | 0.12817 | 0.12817 | -122.2824 | -122.2458 | 0.045777 | 0.16479 | 0.027466 | 0.16022
3269.6875 | 121.5912 | -0.11902 | 122.2595 | -0.1281 | -0.019946 | -0.0020615 | -0.013597 | -0.007259 | -0.012179 | -0.011521 | -0.0051575 | 0.012198 | -0.0038986 | -0.0065091 | -0.017141 | 0.017303 | 0.0007114 | -0.07782 | 0.050354 | -0.10071 | -0.086975 | 0.004578 | -0.10071 | -0.050354 | -0.013733 | 0.082397 | -0.082397 | -0.004578 | 0.10529 | 0.018311 | 0.07782 | 0.018311 | -122.2092 | -122.3465 | 0.1236 | 0.068665 | 0.018311 | 0.050354 | 0 | 0.036622 | -122.1771 | -122.2641 | 0.22431 | 0.19684 | 0.13733 | 0.16022 | 0.10071 | 0.10529 | 0.013733 | 0.18768 | 0.077819 | 0.15106 | 0.16479 | 0.16937 | 0.20142 | -122.3602 | -122.3419 | 0.032044 | 0.11444 | 0.041199 | 0.10529
3271.4531 | 121.7422 | -0.1236 | 122.2549 | -0.1281 | -0.013324 | 0.0011429 | -0.011247 | 0.0010724 | -0.011111 | -0.0053257 | -0.0051575 | 0.013266 | 0.0020828 | -0.00074128 | -0.017568 | 0.023712 | -0.000784 | -0.09613 | 0.073242 | -0.1236 | -0.10986 | -0.013733 | -0.14648 | -0.059509 | -0.050354 | 0.086975 | -0.082397 | -0.045776 | 0.086975 | 0.004578 | 0.050354 | 0 | -122.1817 | -122.3648 | 0.10986 | 0.064087 | -0.022888 | 0.064087 | -0.022888 | 0.041199 | -122.168 | -122.3007 | 0.21057 | 0.17395 | 0.12817 | 0.13275 | 0.086975 | 0.10986 | 0.013733 | 0.16937 | 0.036621 | 0.19684 | 0.16937 | 0.19684 | 0.21057 | -122.3785 | -122.3373 | 0.013733 | 0.07782 | 0.027466 | 0.073242
3273.2188 | 121.7514 | -0.10529 | 122.2275 | -0.54771 | -0.018023 | -0.0052657 | -0.014024 | -0.002132 | -0.011751 | -0.0048985 | -0.0051575 | 0.013907 | -0.0011216 | 0.0020359 | -0.013723 | 0.017944 | -0.0009976 | -0.086975 | 0.036621 | -0.11444 | -0.091553 | 0 | -0.13733 | -0.054932 | -0.022888 | 0.10071 | -0.086975 | -0.027466 | 0.10071 | 0 | 0.068665 | -0.009155 | -122.1909 | -122.319 | 0.10529 | 0.050354 | -0.032043 | 0.059509 | -0.022888 | 0.018311 | -122.1268 | -122.2549 | 0.20599 | 0.17395 | 0.10529 | 0.15564 | 0.086975 | 0.11444 | 0.022888 | 0.18768 | 0.059509 | 0.15106 | 0.18768 | 0.14191 | 0.20599 | -122.3419 | -122.3145 | 0.013733 | 0.07782 | 0.018311 | 0.082398
3274.9844 | 121.6187 | -0.09613 | 121.7377 | -0.013657 | -0.021441 | 0.1086 | -0.014879 | -0.013454 | -0.015169 | -0.013657 | -0.0021057 | 0.012411 | -0.007103 | -0.0054409 | -0.022055 | 0.006195 | -0.005911 | -0.10071 | 0.054932 | -0.11444 | -0.045776 | 0.059509 | -0.10986 | -0.036621 | 0.045776 | 0.086975 | -0.059509 | 0.009155 | 0.11902 | 0.022888 | 0.091553 | -0.018311 | -121.6827 | -121.7834 | 0.15564 | 0.059509 | -0.013733 | 0.07782 | 0.004578 | 0.036621 | -121.6507 | -121.7285 | 0.21515 | 0.18768 | 0.11902 | 0.15106 | 0.082397 | 0.17395 | 0.068665 | 0.17853 | 0.068664 | 0.16937 | 0.14648 | 0.15106 | 0.1831 | -121.8521 | -121.7972 | 0.050354 | 0.10528 | -0.004578 | 0.14191
3276.75 | 121.7834 | -0.10529 | 122.2458 | 0.0016023 | -0.0090513 | 0.0013565 | -0.01317 | -0.00042301 | -0.011538 | -0.0048985 | -0.0021057 | 0.013052 | 0.0044326 | -0.0024503 | -0.016928 | 0.021149 | -0.004202 | -0.10529 | 0.064087 | -0.10986 | -0.086975 | 0 | -0.13733 | -0.064087 | -0.050354 | 0.082397 | -0.10071 | -0.041199 | 0.086975 | 0.004578 | 0.068665 | -0.004577 | -122.1817 | -122.3328 | 0.10529 | 0.041199 | -0.032043 | 0.045776 | -0.027466 | 0.004578 | -122.1634 | -122.287 | 0.19226 | 0.17395 | 0.10986 | 0.16937 | 0.10529 | 0.10986 | 0.022888 | 0.18768 | 0.059509 | 0.17395 | 0.18311 | 0.16937 | 0.18768 | -122.3557 | -122.3465 | 0.018311 | 0.064087 | 0 | 0.054932
3278.4531 | 122.374 | -0.07782 | 122.2229 | -0.013657 | -0.010333 | -0.00035255 | -0.016374 | 0.00021799 | -0.0098287 | -0.0044711 | -0.0082093 | 0.011557 | 0.0040054 | -0.0026639 | -0.018423 | 0.019653 | 7.04e-05 | -0.032043 | 0.018311 | -0.086975 | 0.018311 | 0.16937 | -0.004578 | 0.050354 | 0.11444 | 0.045776 | -0.036621 | 0.073242 | 0.21973 | 0.12817 | 0.13733 | -0.009155 | -122.2046 | -122.2046 | 0.24719 | 0.12817 | 0.073242 | 0.13733 | 0.082397 | 0.041199 | -122.1771 | -122.1497 | 0.29755 | 0.21515 | 0.20599 | 0.17395 | 0.1648 | 0.25635 | 0.10529 | 0.25635 | 0.10986 | 0.10529 | 0.082397 | 0.096131 | 0.1236 | -122.3099 | -122.2595 | 0.096131 | 0.15106 | 0.045777 | 0.19226
3280.2188 | 121.9437 | -0.10529 | 122.2412 | 0.0016023 | -0.021655 | -0.0048385 | -0.011247 | -0.01794 | -0.023714 | -0.019425 | -0.0021057 | 0.012839 | -0.0011216 | 0.0045993 | -0.019491 | 0.022644 | -0.0033474 | -0.10986 | 0.045776 | -0.10986 | -0.11902 | -0.032043 | -0.19684 | -0.086975 | -0.054932 | 0.091553 | -0.10529 | -0.050354 | 0.018311 | -0.054932 | 0.036621 | -0.004577 | -122.1954 | -122.3602 | 0.073243 | 0.018311 | -0.091552 | 0.022888 | -0.086975 | 0 | -122.1497 | -122.2916 | 0.1236 | 0.14191 | 0.050354 | 0.14191 | 0.050354 | 0.07782 | -0.009156 | 0.1236 | 0.054932 | 0.15564 | 0.19684 | 0.15106 | 0.19684 | -122.3511 | -122.3465 | -0.013733 | 0.054932 | -0.004577 | 0.050354
3281.9219 | 122.3602 | -0.059509 | 122.2183 | 0.0016023 | -0.0030697 | 0.00092925 | -0.011461 | -0.00063661 | -0.0096151 | -0.0036167 | -0.0082093 | 0.012198 | 0.00251 | 0.0020359 | -0.016714 | 0.022858 | -0.0020658 | -0.064087 | 0.041199 | -0.09613 | -0.041199 | 0.091553 | -0.091553 | 0 | 0.091553 | 0.054932 | -0.073242 | 0.07782 | 0.17395 | 0.07782 | 0.15106 | -0.036621 | -122.1771 | -122.2595 | 0.15106 | 0.059509 | -0.032044 | 0.09613 | 0.004577 | -0.013733 | -122.1634 | -122.1405 | 0.23346 | 0.21057 | 0.13733 | 0.2243 | 0.15106 | 0.18768 | 0.054931 | 0.24719 | 0.15106 | 0.13733 | 0.12817 | 0.10071 | 0.11444 | -122.3145 | -122.2916 | 0.01831 | 0.13733 | -0.004578 | 0.15106
3283.7031 | 122.3969 | -0.07782 | 122.2183 | -0.0060272 | -0.0037107 | 0.0041337 | -0.013811 | 0.0025678 | -0.0091879 | -0.0051121 | 0.0009461 | 0.011771 | 0.00016023 | 0.0058811 | -0.017996 | 0.020935 | -0.004202 | -0.013733 | 0.032043 | -0.059509 | 0.004578 | 0.11902 | -0.059509 | 0.018311 | 0.10529 | 0.050354 | -0.064087 | 0.086975 | 0.18768 | 0.091553 | 0.14191 | 0.018311 | -122.1863 | -122.2137 | 0.19684 | 0.096131 | 0.018311 | 0.07782 | 0 | 0.013733 | -122.168 | -122.1313 | 0.2655 | 0.21973 | 0.16937 | 0.20599 | 0.15564 | 0.17853 | 0.064087 | 0.25177 | 0.15106 | 0.091552 | 0.11444 | 0.10986 | 0.12817 | -122.2778 | -122.2824 | 0.082398 | 0.16479 | 0.064087 | 0.18311
3285.4219 | 122.0306 | -0.11444 | 122.2824 | 0.16945 | 0.029828 | 0.11116 | -0.010606 | -0.010036 | -0.015383 | -0.013016 | -0.011261 | 0.01348 | -0.0034714 | 0.0045993 | -0.017355 | 0.024139 | 0.0007114 | -0.09613 | 0.050354 | -0.10529 | -0.13275 | -0.050354 | -0.18768 | -0.10071 | -0.059509 | 0.086975 | -0.086975 | -0.045776 | 0.036621 | -0.045776 | 0.027466 | 0.009155 | -122.2321 | -122.4152 | 0.064087 | 0.013733 | -0.073242 | 0.004578 | -0.082397 | 0.027466 | -122.1954 | -122.3282 | 0.15106 | 0.14191 | 0.068665 | 0.11444 | 0.041199 | 0.054932 | -0.027465 | 0.1236 | 0.041199 | 0.15564 | 0.17395 | 0.16479 | 0.20142 | -122.3877 | -122.3694 | -0.01831 | 0.068665 | 0.018311 | 0.054932
3287.1875 | 122.0673 | -0.11902 | 122.2458 | 0.0016023 | -0.02016 | -0.014024 | -0.012102 | -0.004909 | -0.02756 | -0.022415 | -0.0021057 | 0.013907 | 0.00037383 | 0.0018221 | -0.016073 | 0.024353 | -0.0009976 | -0.10071 | 0.054932 | -0.10986 | -0.12817 | -0.045776 | -0.19684 | -0.09613 | -0.050354 | 0.082397 | -0.10071 | -0.050354 | 0.036621 | -0.050354 | 0.059509 | 0.009156 | -122.1909 | -122.374 | 0.073243 | 0.022889 | -0.077819 | 0.013733 | -0.086975 | 0.018311 | -122.1634 | -122.2961 | 0.15564 | 0.17853 | 0.068665 | 0.16022 | 0.050354 | 0.064087 | -0.018311 | 0.13733 | 0.050354 | 0.16479 | 0.18311 | 0.17395 | 0.20142 | -122.3557 | -122.3465 | -0.009155 | 0.068665 | 0.018311 | 0.068665
3288.8906 | 122.3785 | -0.09613 | 122.2321 | -0.013657 | -0.0077695 | 0.0013565 | -0.014879 | -0.001491 | -0.0089743 | -0.0051121 | -0.0051575 | 0.012625 | 0.004219 | 0.00075412 | -0.016714 | 0.02243 | -0.0009976 | -0.086975 | 0.027466 | -0.10529 | -0.064087 | 0.068665 | -0.086975 | 0 | 0.027466 | 0.064087 | -0.059509 | 0.018311 | 0.14648 | 0.068665 | 0.10529 | -0.009156 | -122.2046 | -122.2961 | 0.16479 | 0.09613 | 0.009155 | 0.10529 | 0.018311 | 0.036621 | -122.168 | -122.2137 | 0.24261 | 0.20142 | 0.16479 | 0.16479 | 0.12817 | 0.17395 | 0.041199 | 0.20599 | 0.07782 | 0.13275 | 0.1236 | 0.1236 | 0.16022 | -122.3373 | -122.2916 | 0.032043 | 0.11444 | 0.009155 | 0.1236
3290.6719 | 122.374 | -0.09613 | 122.2137 | -0.10521 | -0.0060605 | -0.0027023 | -0.015306 | -0.00042301 | -0.010043 | -0.0076755 | -0.0082093 | 0.010489 | 0.0016556 | 0.0026767 | -0.017355 | 0.020721 | -0.0001432 | -0.032043 | 0.018311 | -0.091553 | 0.018311 | 0.14648 | -0.018311 | 0.027466 | 0.059509 | 0.054932 | -0.073242 | 0.041199 | 0.17395 | 0.086975 | 0.11902 | 0.004577 | -122.1954 | -122.1954 | 0.24261 | 0.1236 | 0.077819 | 0.11902 | 0.073242 | 0.022888 | -122.1588 | -122.1725 | 0.27008 | 0.21515 | 0.1831 | 0.19226 | 0.16022 | 0.23804 | 0.10986 | 0.24719 | 0.11444 | 0.10986 | 0.12817 | 0.11444 | 0.15106 | -122.3053 | -122.287 | 0.11444 | 0.13733 | 0.064087 | 0.15564
3292.3594 | 121.8613 | -0.11444 | 121.6599 | -0.021286 | -0.021228 | 0.10817 | -0.012529 | -0.01025 | -0.022005 | -0.011307 | -0.0082093 | 0.010489 | -0.0030442 | -0.0080045 | -0.017782 | 0.014099 | 0.0004978 | -0.07782 | 0.064087 | -0.091553 | -0.10986 | -0.018311 | -0.17853 | -0.09613 | -0.073242 | 0.10529 | -0.082397 | -0.064087 | 0.027466 | -0.07782 | 0.032043 | 0.022888 | -121.5958 | -121.7697 | 0.09613 | 0.018311 | -0.064087 | -0.004577 | -0.086975 | 0.032044 | -121.5546 | -121.7239 | 0.14191 | 0.14648 | 0.036621 | 0.11444 | 0.004577 | 0.073242 | -0.01831 | 0.10986 | 0.01831 | 0.15564 | 0.18768 | 0.17853 | 0.21973 | -121.7514 | -121.7422 | 0.004578 | 0.050354 | 0.036621 | 0.041199
3294.1094 | 122.374 | -0.082397 | 122.2458 | -0.0060272 | -0.0062741 | 0.0015701 | -0.015733 | 0.0032086 | -0.0087607 | -0.0061801 | -0.0051575 | 0.010702 | 0.0044326 | -0.00031408 | -0.020132 | 0.020721 | 0.0022068 | -0.036621 | 0.009155 | -0.073242 | -0.004578 | 0.11902 | -0.064087 | 0.027466 | 0.086975 | 0.054932 | -0.045776 | 0.032043 | 0.16022 | 0.054932 | 0.10986 | 0.009155 | -122.2366 | -122.2504 | 0.20142 | 0.10986 | 0.01831 | 0.10071 | 0.009155 | 0.036621 | -122.1909 | -122.2137 | 0.24261 | 0.19226 | 0.13733 | 0.15564 | 0.10071 | 0.19226 | 0.068664 | 0.20599 | 0.077819 | 0.082397 | 0.10071 | 0.091552 | 0.13733 | -122.319 | -122.2916 | 0.077819 | 0.11444 | 0.045776 | 0.16937
3295.8125 | 122.4197 | -0.059509 | 122.2595 | -0.09758 | -0.0052059 | 0.0013565 | -0.012956 | -0.0034136 | -0.010043 | -0.0029759 | -0.0051575 | 0.011771 | 0.0037918 | -0.0065091 | -0.016714 | 0.022003 | -0.0014248 | -0.045776 | 0.018311 | -0.082397 | 0 | 0.12817 | -0.027466 | 0.054932 | 0.11902 | 0.059509 | -0.082397 | 0.068665 | 0.21057 | 0.11902 | 0.16022 | -0.022888 | -122.2412 | -122.2595 | 0.18768 | 0.11444 | 0.032043 | 0.13733 | 0.054931 | -0.022888 | -122.2 | -122.1909 | 0.27008 | 0.21973 | 0.17853 | 0.24261 | 0.20142 | 0.21057 | 0.082397 | 0.29297 | 0.15106 | 0.10071 | 0.14191 | 0.07782 | 0.11902 | -122.3419 | -122.3419 | 0.059509 | 0.12817 | 0.013733 | 0.17853
3297.5625 | 122.4106 | -0.068665 | 122.2549 | -0.41801 | -0.0092649 | 7.4854e-05 | -0.015306 | 0.0010724 | -0.011111 | -0.0061801 | -0.0021057 | 0.010916 | 0.0016556 | -0.0037321 | -0.018209 | 0.022858 | -0.0001432 | -0.009155 | 0 | -0.07782 | 0.013733 | 0.16022 | -0.009155 | 0.045776 | 0.13275 | 0.045776 | -0.059509 | 0.064087 | 0.21515 | 0.1236 | 0.1236 | -0.009155 | -122.2549 | -122.2412 | 0.22888 | 0.11444 | 0.05951 | 0.1236 | 0.068665 | 0.009156 | -122.2092 | -122.1909 | 0.28381 | 0.19226 | 0.19226 | 0.1831 | 0.1831 | 0.23804 | 0.091553 | 0.27466 | 0.1236 | 0.07782 | 0.10528 | 0.068665 | 0.11444 | -122.3328 | -122.3145 | 0.082398 | 0.13275 | 0.05951 | 0.20142
3299.3281 | 122.4564 | -0.073242 | 122.2504 | 0.10841 | -0.0086239 | -0.0014205 | -0.01317 | -0.0019184 | -0.011111 | -0.0038303 | -0.0051575 | 0.010275 | 0.0029372 | 0.0016085 | -0.016287 | 0.023071 | -0.0031338 | -0.036621 | 0.022888 | -0.07782 | 0.018311 | 0.17395 | -0.009155 | 0.064087 | 0.14191 | 0.036621 | -0.045776 | 0.064087 | 0.21057 | 0.10986 | 0.13733 | -0.004578 | -122.2275 | -122.2321 | 0.24719 | 0.13733 | 0.064087 | 0.14191 | 0.068665 | 0.027466 | -122.2137 | -122.1863 | 0.28381 | 0.21057 | 0.18311 | 0.18311 | 0.15564 | 0.25177 | 0.096131 | 0.25635 | 0.10986 | 0.10071 | 0.082397 | 0.09613 | 0.10986 | -122.3282 | -122.2961 | 0.091553 | 0.13733 | 0.036621 | 0.21515
3301.1094 | 122.3785 | -0.091553 | 122.2595 | -0.3875 | -0.0086239 | 0.0019975 | -0.015306 | -0.0032 | -0.012392 | -0.0051121 | -0.0082093 | 0.010702 | 0.001442 | -0.0013821 | -0.0165 | 0.023499 | -0.0001432 | -0.07782 | 0.022888 | -0.07782 | -0.059509 | 0.054932 | -0.09613 | -0.004578 | 0.027466 | 0.064087 | -0.054932 | 0.013733 | 0.12817 | 0.032043 | 0.091553 | 0.013733 | -122.2366 | -122.319 | 0.14649 | 0.086975 | -0.004577 | 0.073242 | -0.01831 | 0.036621 | -122.1954 | -122.2458 | 0.21973 | 0.18311 | 0.1236 | 0.14649 | 0.086975 | 0.13275 | 0.018311 | 0.18311 | 0.068665 | 0.10071 | 0.11902 | 0.11444 | 0.15564 | -122.3373 | -122.3145 | 0.032044 | 0.10529 | 0.013733 | 0.11902
3302.8125 | 122.0535 | -0.11902 | 121.8796 | -0.013657 | -0.0056333 | 0.0013565 | -0.012956 | -0.0023456 | -0.010897 | -0.0055393 | -0.011261 | 0.012198 | 0.0027236 | -0.00031408 | -0.017782 | 0.023285 | -0.0020658 | -0.10986 | 0.068665 | -0.11902 | -0.11444 | -0.009155 | -0.15106 | -0.059509 | -0.041199 | 0.10071 | -0.10071 | -0.050354 | 0.082397 | -0.013733 | 0.032043 | 0 | -121.8109 | -121.994 | 0.10986 | 0.05951 | -0.032043 | 0.05951 | -0.032043 | 0.018311 | -121.7789 | -121.9299 | 0.20142 | 0.15106 | 0.10529 | 0.13275 | 0.086975 | 0.10986 | 0.004578 | 0.18311 | 0.050354 | 0.18768 | 0.20142 | 0.18768 | 0.21973 | -121.9986 | -121.9803 | 0.004578 | 0.068665 | 0.009156 | 0.07782
3304.5781 | 121.8475 | -0.11444 | 121.5637 | -0.021286 | -0.0054197 | -0.0012069 | -0.017015 | -0.0091816 | -0.013888 | -0.017288 | -0.0021057 | 0.012198 | -0.0038986 | 0.00075412 | -0.0165 | 0.010681 | -0.0033474 | -0.064087 | 0.050354 | -0.10071 | -0.054932 | 0.041199 | -0.11444 | -0.041199 | 0.009155 | 0.086975 | -0.086975 | 0.018311 | 0.11902 | 0.009155 | 0.086975 | 0.013733 | -121.5134 | -121.6187 | 0.15564 | 0.073242 | 0 | 0.059509 | -0.013733 | 0.027466 | -121.4767 | -121.5454 | 0.23346 | 0.20142 | 0.1236 | 0.17395 | 0.09613 | 0.14191 | 0.045776 | 0.20599 | 0.10529 | 0.15106 | 0.17395 | 0.16479 | 0.20142 | -121.6644 | -121.6507 | 0.059509 | 0.13275 | 0.050354 | 0.1236
3306.3594 | 122.4152 | -0.07782 | 122.2229 | -0.059433 | -0.010333 | 0.00028845 | -0.015306 | 0.0042768 | -0.011751 | -0.0042575 | -0.0021057 | 0.0074982 | 0.00251 | -0.0015957 | -0.016714 | 0.021362 | -0.0033474 | -0.045776 | 0.018311 | -0.07782 | 0.032043 | 0.16022 | -0.013733 | 0.045776 | 0.09613 | 0.050354 | -0.041199 | 0.073242 | 0.21515 | 0.11444 | 0.13733 | 0 | -122.2046 | -122.1909 | 0.23804 | 0.1236 | 0.064087 | 0.1236 | 0.064087 | 0.036621 | -122.1725 | -122.1497 | 0.29297 | 0.21515 | 0.19226 | 0.17853 | 0.15564 | 0.23804 | 0.10986 | 0.25635 | 0.11444 | 0.096131 | 0.091553 | 0.096131 | 0.12817 | -122.3007 | -122.2641 | 0.10986 | 0.15106 | 0.032044 | 0.17395
3308.125 | 121.8338 | -0.10529 | 121.6965 | -0.0060272 | -0.02016 | 0.1086 | -0.022569 | -0.011104 | -0.015597 | -0.027329 | -0.0051575 | 0.010275 | -0.0058212 | -0.0011685 | -0.016928 | 0.0072632 | -0.004202 | -0.068665 | 0.064087 | -0.10529 | -0.09613 | -0.004578 | -0.17395 | -0.09613 | -0.050354 | 0.10529 | -0.091553 | -0.045776 | 0.041199 | -0.045776 | 0.022888 | 0 | -121.6324 | -121.7926 | 0.10071 | 0.009156 | -0.068664 | 0.009156 | -0.068664 | 0.013733 | -121.5912 | -121.7422 | 0.14649 | 0.12817 | 0.05951 | 0.11444 | 0.045777 | 0.10071 | 0.009156 | 0.13275 | 0.045777 | 0.16937 | 0.19684 | 0.16937 | 0.21057 | -121.8018 | -121.788 | 0.009156 | 0.05951 | 0.036621 | 0.054932
3309.8906 | 122.4152 | -0.09613 | 122.2824 | -0.013657 | -0.010333 | 0.0013565 | -0.015733 | 0.00085879 | -0.011538 | -0.0034031 | -0.0082093 | 0.010275 | 0.0020828 | -0.0039457 | -0.017996 | 0.01944 | -0.0005704 | -0.082397 | 0.032043 | -0.09613 | -0.050354 | 0.073242 | -0.086975 | 0.013733 | 0.018311 | 0.059509 | -0.068665 | 0.018311 | 0.15106 | 0.064087 | 0.11444 | 0 | -122.2504 | -122.3328 | 0.16937 | 0.10986 | 0.009155 | 0.10986 | 0.009155 | 0.027465 | -122.2229 | -122.2641 | 0.24719 | 0.21057 | 0.16022 | 0.18311 | 0.13275 | 0.16937 | 0.045776 | 0.21973 | 0.086976 | 0.12817 | 0.12817 | 0.12817 | 0.15564 | -122.3785 | -122.3511 | 0.045776 | 0.11444 | 0.013733 | 0.11444
3311.5938 | 122.4426 | -0.068665 | 122.049 | -0.0060272 | -0.0052059 | 0.0041337 | -0.01317 | -0.0010638 | -0.010043 | -0.0055393 | -0.0051575 | 0.010916 | 0.0012282 | 0.0060947 | -0.016928 | 0.021576 | 7.04e-05 | 0.004578 | 0.009155 | -0.073242 | 0.041199 | 0.13275 | -0.054932 | 0.036621 | 0.10529 | 0.054932 | -0.050354 | 0.091553 | 0.1831 | 0.086975 | 0.14191 | -0.004577 | -122.0398 | -122.0078 | 0.20142 | 0.10529 | 0.013733 | 0.10986 | 0.01831 | 0.018311 | -121.994 | -121.9574 | 0.25177 | 0.21057 | 0.15564 | 0.19226 | 0.13733 | 0.20599 | 0.11444 | 0.23346 | 0.14191 | 0.082397 | 0.10529 | 0.07782 | 0.1236 | -122.1222 | -122.0993 | 0.10986 | 0.16022 | 0.073243 | 0.17395
3313.2812 | 122.4152 | -0.086975 | 122.3099 | -0.12047 | -0.0096921 | 0.0022111 | -0.014879 | -0.001491 | -0.0098287 | -0.0031895 | -0.0051575 | 0.011343 | 0.0033646 | -0.0056547 | -0.018637 | 0.022644 | -0.0009976 | -0.009155 | 0.018311 | -0.068665 | 0.036621 | 0.15106 | -0.022888 | 0.050354 | 0.082397 | 0.045776 | -0.050354 | 0.041199 | 0.19684 | 0.086975 | 0.12817 | 0.01831 | -122.2916 | -122.2733 | 0.23804 | 0.13733 | 0.064087 | 0.11902 | 0.045777 | 0.036621 | -122.2641 | -122.2687 | 0.28381 | 0.21515 | 0.17395 | 0.17853 | 0.13733 | 0.21973 | 0.10529 | 0.24719 | 0.091553 | 0.086976 | 0.09613 | 0.10529 | 0.13275 | -122.3785 | -122.3602 | 0.1236 | 0.12817 | 0.07782 | 0.16937
3315.0469 | 122.0078 | -0.10071 | 122.3328 | -0.40276 | 0.027692 | 0.10988 | -0.018083 | -0.0059772 | 0.057035 | -0.011307 | -0.0082093 | 0.01348 | -0.011589 | -0.0011685 | -0.0165 | 0.013031 | 0.0041294 | -0.068665 | 0.082397 | -0.091553 | -0.11902 | -0.036621 | -0.1831 | -0.09613 | -0.068665 | 0.091553 | -0.09613 | -0.064087 | 0.013733 | -0.07782 | 0.018311 | 0.009155 | -122.2504 | -122.4518 | 0.064087 | 0.004578 | -0.082397 | -0.004577 | -0.091552 | 0.004578 | -122.2412 | -122.3969 | 0.11444 | 0.11902 | 0.022888 | 0.11444 | 0.01831 | 0.054932 | -0.027466 | 0.10986 | 0.032043 | 0.17395 | 0.18768 | 0.18311 | 0.19226 | -122.4243 | -122.4289 | -0.018311 | 0.036621 | 0.032043 | 0.032043
3316.8125 | 122.4106 | -0.082397 | 122.2916 | -0.013657 | -0.0079831 | -0.00013895 | -0.016801 | -0.00085021 | -0.010256 | -0.0063937 | -0.0082093 | 0.011984 | 0.0052872 | 0.0011813 | -0.016928 | 0.021576 | 0.0011386 | -0.068665 | 0.032043 | -0.091553 | -0.050354 | 0.07782 | -0.091553 | 0.004578 | 0.027466 | 0.059509 | -0.064087 | 0.013733 | 0.14191 | 0.07782 | 0.11444 | -0.009156 | -122.2595 | -122.3419 | 0.16022 | 0.086975 | -0.009156 | 0.096131 | 0 | 0.01831 | -122.2321 | -122.2778 | 0.2243 | 0.19684 | 0.16022 | 0.17853 | 0.14191 | 0.16937 | 0.041199 | 0.20599 | 0.07782 | 0.1236 | 0.1236 | 0.11444 | 0.14191 | -122.3831 | -122.3557 | 0.032043 | 0.09613 | 0.013732 | 0.10986
3318.5781 | 122.3099 | -0.11902 | 122.319 | -0.19676 | -0.0084103 | 0.00028845 | -0.012743 | 4.192e-06 | -0.010897 | -0.0057529 | -0.0021057 | 0.011984 | 0.0044326 | 0.0026767 | -0.017782 | 0.021149 | -0.0001432 | -0.11444 | 0.059509 | -0.11902 | -0.11444 | 0.022888 | -0.11902 | -0.064087 | -0.050354 | 0.09613 | -0.091553 | -0.059509 | 0.064087 | -0.032043 | 0.018311 | 0 | -122.2595 | -122.4335 | 0.14191 | 0.054932 | 0 | 0.054932 | 0 | 0.027466 | -122.2229 | -122.3785 | 0.18311 | 0.13733 | 0.086976 | 0.10986 | 0.05951 | 0.14191 | 0.004578 | 0.15564 | 0.032044 | 0.17853 | 0.18768 | 0.17853 | 0.21515 | -122.438 | -122.4106 | 0.004578 | 0.05951 | 0.004578 | 0.068665
3320.2812 | 122.2412 | -0.11902 | 122.2916 | -0.0060272 | -0.019519 | -0.0024887 | -0.011675 | -0.0070452 | -0.023714 | -0.019638 | -0.0021057 | 0.012839 | -0.00048057 | 0.0018221 | -0.016714 | 0.021576 | -0.0039884 | -0.10071 | 0.041199 | -0.11444 | -0.09613 | -0.027466 | -0.18768 | -0.091553 | -0.059509 | 0.07782 | -0.09613 | -0.054932 | 0.032043 | -0.064087 | 0.045776 | 0.004578 | -122.2504 | -122.3877 | 0.091553 | 0.027466 | -0.068664 | 0.022888 | -0.073242 | 0.022889 | -122.2137 | -122.3465 | 0.15106 | 0.16479 | 0.054932 | 0.14191 | 0.032043 | 0.086975 | 0.018311 | 0.12817 | 0.041198 | 0.15564 | 0.17395 | 0.16022 | 0.19684 | -122.406 | -122.3877 | 0.022889 | 0.064087 | 0.018311 | 0.05951
3322.0625 | 122.1588 | -0.13275 | 121.9254 | -0.021286 | -0.0058469 | -0.00035255 | -0.013811 | -0.0010638 | -0.010043 | -0.0014805 | -0.0051575 | 0.010489 | 0.0010146 | 0.0035311 | -0.017782 | 0.02179 | 0.0004978 | -0.10071 | 0.054932 | -0.1236 | -0.10529 | -0.009155 | -0.14648 | -0.059509 | -0.041199 | 0.07782 | -0.091553 | -0.045776 | 0.091553 | -0.022888 | 0.045776 | 0.009155 | -121.8704 | -122.0306 | 0.1236 | 0.073242 | -0.013733 | 0.064087 | -0.022888 | 0.041198 | -121.8475 | -121.9711 | 0.2243 | 0.17853 | 0.10986 | 0.13733 | 0.068665 | 0.11444 | 0.01831 | 0.18311 | 0.045777 | 0.17853 | 0.16937 | 0.18768 | 0.21057 | -122.049 | -122.0169 | 0.027465 | 0.086975 | 0.032043 | 0.091552
3323.7656 | 122.3511 | -0.09613 | 121.9757 | 0.0016023 | -0.0043515 | -0.00077975 | -0.011461 | 4.192e-06 | -0.010256 | -0.0059665 | -0.0051575 | 0.012198 | 0.0033646 | -0.0020231 | -0.017996 | 0.023285 | 0.0034884 | -0.10071 | 0.064087 | -0.11902 | -0.10071 | 0 | -0.19226 | -0.07782 | -0.041199 | 0.10071 | -0.082397 | 0 | 0.07782 | -0.018311 | 0.064087 | -0.022889 | -121.9116 | -122.0764 | 0.09613 | 0.01831 | -0.096131 | 0.041199 | -0.073242 | 0.013733 | -121.875 | -121.9757 | 0.17395 | 0.16022 | 0.077819 | 0.14648 | 0.064086 | 0.11902 | 0.018311 | 0.16022 | 0.082397 | 0.18311 | 0.18311 | 0.16022 | 0.19684 | -122.0947 | -122.0581 | -0.004578 | 0.09613 | -0.004578 | 0.054931
3325.4688 | 122.4289 | -0.064087 | 122.2961 | -0.0060272 | -0.0064877 | 0.0030655 | -0.01552 | -0.001491 | -0.011111 | -0.0034031 | -0.0051575 | 0.010275 | 0.0027236 | -0.0041593 | -0.016714 | 0.019653 | 0.0004978 | -0.041199 | 0.018311 | -0.064087 | -0.022888 | 0.10529 | -0.09613 | 0.013733 | 0.068665 | 0.050354 | -0.064087 | 0.018311 | 0.13733 | 0.050354 | 0.09613 | 0 | -122.2778 | -122.319 | 0.16937 | 0.07782 | -0.032043 | 0.07782 | -0.032043 | 0 | -122.2458 | -122.2778 | 0.20142 | 0.16022 | 0.11444 | 0.16022 | 0.11444 | 0.16937 | 0.041199 | 0.20142 | 0.082398 | 0.082398 | 0.11444 | 0.082398 | 0.11444 | -122.3602 | -122.3602 | 0.041199 | 0.082398 | 0.022888 | 0.13275
3327.2344 | 122.0215 | -0.09613 | 122.3511 | -0.10521 | -0.0081967 | -0.0014205 | -0.014024 | -0.0076862 | -0.019015 | -0.014939 | -0.0021057 | 0.01113 | -0.0056076 | -0.012918 | -0.020986 | 0.006195 | -0.0074064 | -0.054932 | 0.032043 | -0.10986 | -0.022888 | 0.054932 | -0.10071 | -0.032043 | 0.059509 | 0.09613 | -0.09613 | 0.009155 | 0.11902 | 0.013733 | 0.091553 | -0.013733 | -122.319 | -122.374 | 0.15106 | 0.064087 | -0.004578 | 0.07782 | 0.009155 | 0 | -122.2549 | -122.3419 | 0.21515 | 0.18768 | 0.10986 | 0.18768 | 0.10986 | 0.16479 | 0.086975 | 0.21515 | 0.10528 | 0.14191 | 0.19226 | 0.12817 | 0.19226 | -122.4609 | -122.4472 | 0.073242 | 0.10528 | 0.041198 | 0.15564
3329 | 122.4243 | -0.07782 | 122.3145 | -0.0060272 | -0.0032833 | 0.0052017 | -0.013597 | 0.0021406 | -0.0096151 | -0.0048985 | -0.0082093 | 0.014548 | 0.0029372 | -0.0048001 | -0.017355 | 0.023712 | -0.0016384 | -0.10986 | 0.045776 | -0.11444 | -0.07782 | 0.022888 | -0.16022 | -0.050354 | 0.013733 | 0.086975 | -0.07782 | 0.022888 | 0.1236 | 0.032043 | 0.09613 | -0.036621 | -122.2687 | -122.3923 | 0.10071 | 0.027466 | -0.082397 | 0.064087 | -0.045776 | 0 | -122.2275 | -122.2916 | 0.20142 | 0.17395 | 0.10986 | 0.17395 | 0.10986 | 0.13733 | 0.036621 | 0.20142 | 0.10071 | 0.16022 | 0.16479 | 0.1236 | 0.16479 | -122.4289 | -122.3923 | 0 | 0.10071 | -0.032043 | 0.091553
3330.7031 | 122.1863 | -0.11902 | 122.3419 | -0.013657 | -0.0032833 | 0.00092925 | -0.013811 | 0.00064519 | -0.010256 | -0.0059665 | -0.0021057 | 0.011557 | 0.0029372 | -0.0011685 | -0.017568 | 0.020508 | -0.0018522 | -0.086975 | 0.054932 | -0.11902 | -0.10071 | 0.004578 | -0.11444 | -0.050354 | -0.018311 | 0.091553 | -0.07782 | 0 | 0.11902 | -0.004578 | 0.09613 | 0 | -122.287 | -122.4426 | 0.1236 | 0.068665 | 0.004578 | 0.068665 | 0.004578 | 0.041199 | -122.2504 | -122.3419 | 0.23804 | 0.21515 | 0.11444 | 0.17395 | 0.073242 | 0.1236 | 0.018311 | 0.19684 | 0.07782 | 0.17395 | 0.16937 | 0.17395 | 0.21057 | -122.4609 | -122.4197 | 0.018311 | 0.11902 | 0.032044 | 0.10071
3332.4219 | 122.4792 | -0.050354 | 122.3053 | -0.013657 | -0.0047787 | 0.0054153 | -0.014665 | 0.0025678 | -0.0081197 | -0.0027621 | -0.0051575 | 0.011343 | 0.00037383 | -0.0039457 | -0.018423 | 0.021576 | -0.0009976 | -0.022888 | 0.009155 | -0.059509 | 0.009155 | 0.13275 | -0.064087 | 0.018311 | 0.11902 | 0.050354 | -0.041199 | 0.082397 | 0.19684 | 0.091553 | 0.14648 | -0.009155 | -122.2961 | -122.2961 | 0.18311 | 0.068665 | -0.013733 | 0.07782 | -0.004578 | 0.009155 | -122.2549 | -122.2229 | 0.24719 | 0.19684 | 0.14191 | 0.18768 | 0.13275 | 0.19226 | 0.068664 | 0.23804 | 0.1236 | 0.068664 | 0.091553 | 0.059509 | 0.10071 | -122.3648 | -122.3465 | 0.059509 | 0.13275 | 0.027466 | 0.16937
3334.1875 | 122.4838 | -0.059509 | 122.3282 | -0.0060272 | -0.0060605 | 0.0026383 | -0.014238 | 0.00043159 | -0.0096151 | -0.0068211 | -0.0051575 | 0.008139 | 0.0012282 | -0.0024503 | -0.017141 | 0.021362 | -0.0014248 | -0.004578 | 0.009155 | -0.064087 | 0.013733 | 0.13275 | -0.059509 | 0.027466 | 0.14191 | 0.041199 | -0.045776 | 0.073242 | 0.1831 | 0.086975 | 0.15106 | -0.004578 | -122.319 | -122.3145 | 0.19226 | 0.086975 | 0 | 0.091553 | 0.004578 | 0.013733 | -122.287 | -122.2549 | 0.24261 | 0.21057 | 0.14648 | 0.19684 | 0.13275 | 0.19684 | 0.07782 | 0.22888 | 0.11902 | 0.073242 | 0.086975 | 0.068664 | 0.10071 | -122.3923 | -122.374 | 0.073242 | 0.13275 | 0.054931 | 0.20142
3335.8906 | 122.4426 | -0.073242 | 122.3419 | -0.0060272 | -0.0077695 | 0.0026383 | -0.014024 | 0.00043159 | -0.0091879 | -0.0038303 | -0.0021057 | 0.0096344 | 0.001442 | -0.0082181 | -0.016714 | 0.020935 | -0.0033474 | -0.068665 | 0.032043 | -0.082397 | -0.068665 | 0.064087 | -0.10986 | 0 | 0.032043 | 0.050354 | -0.073242 | 0.013733 | 0.14191 | 0.064087 | 0.10529 | -0.009155 | -122.3099 | -122.4106 | 0.13733 | 0.073242 | -0.036621 | 0.082397 | -0.027466 | 0 | -122.2916 | -122.3282 | 0.21515 | 0.17853 | 0.13733 | 0.17853 | 0.13733 | 0.14648 | 0.013732 | 0.21515 | 0.086975 | 0.11444 | 0.1236 | 0.10529 | 0.1236 | -122.4243 | -122.4152 | 0.004577 | 0.086975 | 0.004577 | 0.10529
3337.6562 | 122.3557 | -0.1236 | 122.3831 | -0.013657 | -0.018664 | 0.10924 | -0.011247 | -0.0017048 | 0.055326 | 0.049576 | -0.0021057 | 0.013693 | -0.0090256 | -0.0022367 | -0.016928 | 0.013458 | 0.000925 | -0.073242 | 0.059509 | -0.11444 | -0.091553 | -0.018311 | -0.18768 | -0.10986 | -0.050354 | 0.091553 | -0.07782 | -0.059509 | 0.036621 | -0.059509 | 0.041199 | 0.009155 | -122.3236 | -122.4747 | 0.10528 | 0.013733 | -0.064087 | 0.004578 | -0.073242 | 0.045776 | -122.2916 | -122.4426 | 0.16022 | 0.16479 | 0.064087 | 0.11902 | 0.018311 | 0.09613 | 0.022888 | 0.11444 | 0.018311 | 0.17395 | 0.16937 | 0.1831 | 0.21515 | -122.4976 | -122.4609 | 0.032043 | 0.064087 | 0.050354 | 0.073242
3339.3438 | 122.438 | -0.07782 | 122.3419 | -0.0060272 | -0.0041379 | 0.00028845 | -0.014452 | -0.0051226 | -0.010043 | -0.0051121 | -0.0082093 | 0.009848 | 0.0027236 | -0.0018093 | -0.018209 | 0.021362 | -0.0037748 | -0.073242 | 0.036621 | -0.07782 | -0.045776 | 0.068665 | -0.10071 | -0.009155 | 0.004578 | 0.054932 | -0.064087 | 0.004578 | 0.13733 | 0.036621 | 0.10071 | 0 | -122.3053 | -122.3877 | 0.14649 | 0.068665 | -0.022888 | 0.068665 | -0.022888 | 0.013733 | -122.287 | -122.3373 | 0.21515 | 0.17853 | 0.11444 | 0.1648 | 0.10071 | 0.14649 | 0.032044 | 0.20142 | 0.068665 | 0.11444 | 0.11902 | 0.11444 | 0.13275 | -122.4197 | -122.406 | 0.032044 | 0.082398 | 0.004578 | 0.082398
3341.125 | 122.374 | -0.13275 | 122.3602 | -0.013657 | -0.0062741 | 0.00028845 | -0.014238 | 4.192e-06 | -0.0091879 | -0.0074619 | -0.0082093 | 0.013693 | 0.003151 | 0.00054052 | -0.018209 | 0.021149 | -0.004202 | -0.11444 | 0.068665 | -0.12817 | -0.10071 | 0.004578 | -0.13275 | -0.073242 | -0.054932 | 0.09613 | -0.086975 | -0.073242 | 0.064087 | -0.018311 | 0.032043 | 0.004577 | -122.2916 | -122.4609 | 0.13733 | 0.059509 | 0 | 0.054932 | -0.004577 | 0.045776 | -122.2641 | -122.4335 | 0.19684 | 0.16479 | 0.11444 | 0.11902 | 0.068664 | 0.13275 | 0.027466 | 0.15106 | 0.013733 | 0.19684 | 0.1831 | 0.20142 | 0.22888 | -122.4884 | -122.4472 | 0.032043 | 0.059509 | 0.01831 | 0.077819
3342.8906 | 122.2549 | -0.10071 | 122.2778 | -0.013657 | -0.01076 | -0.011461 | -0.013384 | -0.017513 | -0.026064 | 0.051285 | -0.0082093 | 0.014761 | -0.0066758 | -0.0099271 | -0.017996 | 0.007904 | -0.003561 | -0.054932 | 0.041199 | -0.10986 | -0.082397 | 0.022888 | -0.16479 | -0.059509 | -0.022888 | 0.082397 | -0.07782 | -0.036621 | 0.054932 | -0.059509 | 0.041199 | -0.009155 | -122.2366 | -122.3602 | 0.1236 | 0.041199 | -0.064087 | 0.050354 | -0.054932 | 0.022888 | -122.1954 | -122.3145 | 0.15564 | 0.14191 | 0.041199 | 0.11902 | 0.018311 | 0.13275 | 0.027466 | 0.13275 | 0.041199 | 0.15106 | 0.16022 | 0.14191 | 0.18311 | -122.3877 | -122.3557 | 0.018311 | 0.064087 | 0.045776 | 0.07782
3344.6406 | 122.4564 | -0.064087 | 122.3328 | -0.013657 | -0.0047787 | 0.0026383 | -0.01552 | 0.00085879 | -0.0089743 | -0.0055393 | -0.011261 | 0.012625 | 0.004219 | -0.00031408 | -0.017996 | 0.020935 | 0.0002842 | -0.054932 | 0.022888 | -0.07782 | -0.018311 | 0.10071 | -0.10071 | 0 | 0.064087 | 0.050354 | -0.059509 | 0.018311 | 0.15106 | 0.050354 | 0.10986 | -0.013733 | -122.3099 | -122.3511 | 0.1648 | 0.064087 | -0.036621 | 0.07782 | -0.022888 | 0.004578 | -122.2824 | -122.3145 | 0.21515 | 0.17395 | 0.11444 | 0.16937 | 0.10986 | 0.17853 | 0.059509 | 0.21057 | 0.07782 | 0.10071 | 0.10986 | 0.086975 | 0.11444 | -122.4106 | -122.3923 | 0.045776 | 0.082398 | 0.009155 | 0.12817
3346.3438 | 122.3648 | -0.091553 | 122.374 | -0.013657 | -0.0058469 | 0.0028519 | -0.012529 | 4.192e-06 | -0.012179 | -0.0095981 | -0.0051575 | 0.012198 | 0.00080103 | -0.0035183 | -0.016714 | 0.020081 | -0.0005704 | -0.086975 | 0.064087 | -0.10529 | -0.082397 | 0.013733 | -0.10529 | -0.050354 | -0.018311 | 0.091553 | -0.082397 | -0.004578 | 0.10986 | 0.018311 | 0.073242 | -0.013733 | -122.3099 | -122.4564 | 0.10529 | 0.041199 | -0.013733 | 0.054932 | 0 | 0.009156 | -122.2824 | -122.3785 | 0.20142 | 0.16479 | 0.10986 | 0.15564 | 0.10071 | 0.11902 | 0.022889 | 0.19226 | 0.077819 | 0.16937 | 0.17395 | 0.15564 | 0.18311 | -122.4792 | -122.4564 | 0.009156 | 0.086975 | 0.004578 | 0.073242
3348.1094 | 122.3648 | -0.10986 | 122.3969 | -0.021286 | -0.0096921 | -0.012956 | -0.010393 | -0.0017048 | -0.020937 | -0.014084 | -0.0082093 | 0.013693 | 0.00058743 | 0.0026767 | -0.016928 | 0.023712 | 7.04e-05 | -0.10071 | 0.054932 | -0.10529 | -0.11902 | -0.032043 | -0.18768 | -0.091553 | -0.064087 | 0.091553 | -0.082397 | -0.045776 | 0.036621 | -0.050354 | 0.045776 | 0.004577 | -122.3419 | -122.5159 | 0.07782 | 0.01831 | -0.07782 | 0.013733 | -0.082397 | 0.027466 | -122.3053 | -122.4426 | 0.14648 | 0.15564 | 0.059509 | 0.12817 | 0.032043 | 0.073243 | -0.013733 | 0.11902 | 0.036621 | 0.16022 | 0.17395 | 0.16479 | 0.20142 | -122.5021 | -122.4792 | -0.009156 | 0.064087 | 0.009155 | 0.045776
3349.8594 | 122.3877 | -0.11444 | 122.3694 | -0.021286 | -0.0054197 | -0.012743 | -0.011888 | 0.00064519 | -0.020083 | -0.011521 | -0.0051575 | 0.011984 | 0.0035782 | 0.0031039 | -0.0165 | 0.021576 | -0.0005704 | -0.091553 | 0.054932 | -0.11444 | -0.12817 | -0.036621 | -0.19226 | -0.10071 | -0.064087 | 0.07782 | -0.086975 | -0.045776 | 0.050354 | -0.041199 | 0.050354 | 0 | -122.3145 | -122.4976 | 0.07782 | 0.013733 | -0.07782 | 0.013733 | -0.07782 | 0.027466 | -122.2916 | -122.4152 | 0.16479 | 0.16479 | 0.073242 | 0.13733 | 0.045776 | 0.07782 | -0.013733 | 0.13733 | 0.041199 | 0.16937 | 0.16479 | 0.16937 | 0.19226 | -122.4838 | -122.4564 | -0.013733 | 0.068665 | 0.022888 | 0.050354
3351.6094 | 122.5113 | -0.059509 | 122.3694 | -0.0060272 | -0.0045651 | 0.0045609 | -0.01317 | 0.0010724 | -0.0087607 | -0.0068211 | -0.0021057 | 0.0085662 | 0.001442 | 0.00011332 | -0.018209 | 0.02243 | -0.0018522 | -0.022888 | 0.018311 | -0.082397 | 0.018311 | 0.14191 | -0.054932 | 0.027466 | 0.11902 | 0.064087 | -0.059509 | 0.082397 | 0.19226 | 0.082397 | 0.13733 | -0.022888 | -122.3511 | -122.3511 | 0.20142 | 0.086975 | 0.004577 | 0.10986 | 0.027465 | 0 | -122.3053 | -122.287 | 0.25177 | 0.19684 | 0.14191 | 0.19684 | 0.14191 | 0.2243 | 0.10071 | 0.25177 | 0.14191 | 0.10071 | 0.1236 | 0.07782 | 0.1236 | -122.4518 | -122.4289 | 0.07782 | 0.14191 | 0.036621 | 0.17853
3353.3281 | 122.3923 | -0.10529 | 122.3877 | -0.013657 | -0.0026425 | 0.0015701 | -0.01082 | -0.0010638 | -0.0079061 | -0.0074619 | -0.0021057 | 0.014548 | 0.003151 | 0.00075412 | -0.017782 | 0.022858 | -0.000784 | -0.09613 | 0.045776 | -0.1236 | -0.10986 | -0.032043 | -0.18768 | -0.086975 | -0.045776 | 0.09613 | -0.09613 | -0.045776 | 0.045776 | -0.068665 | 0.036621 | -0.01831 | -122.3419 | -122.4976 | 0.073243 | 0.018311 | -0.082397 | 0.036621 | -0.064087 | 0.009156 | -122.2916 | -122.4335 | 0.15106 | 0.14191 | 0.036621 | 0.13275 | 0.027465 | 0.091553 | 0.013733 | 0.14191 | 0.050354 | 0.16937 | 0.19226 | 0.15106 | 0.20142 | -122.5113 | -122.4838 | -0.004577 | 0.05951 | 0.009156 | 0.05951
3355.0625 | 122.3877 | -0.11902 | 122.3785 | -0.013657 | -0.0094785 | 0.00050205 | -0.012956 | 0.0017132 | -0.011965 | -0.0063937 | -0.0051575 | 0.011343 | 0.001442 | 0.00011332 | -0.017996 | 0.021362 | -0.0050564 | -0.12817 | 0.059509 | -0.11902 | -0.11444 | -0.004578 | -0.13275 | -0.064087 | -0.050354 | 0.07782 | -0.091553 | -0.064087 | 0.064087 | -0.032043 | 0.050354 | 0 | -122.319 | -122.493 | 0.11444 | 0.054932 | -0.013732 | 0.054932 | -0.013732 | 0.027466 | -122.3007 | -122.4426 | 0.18311 | 0.16937 | 0.086976 | 0.14191 | 0.05951 | 0.11444 | 0.004578 | 0.15564 | 0.027466 | 0.17853 | 0.16937 | 0.17853 | 0.19684 | -122.4976 | -122.4701 | 0.004578 | 0.054932 | -0.009155 | 0.068665
3356.8281 | 122.3602 | -0.10071 | 122.3694 | -0.021286 | -0.013537 | 0.056258 | -0.011888 | -0.010677 | -0.021578 | -0.015152 | -0.0082093 | 0.011984 | -0.001976 | -0.0060819 | -0.018637 | 0.011536 | -0.0046292 | -0.050354 | 0.032043 | -0.10986 | -0.068665 | 0.064087 | -0.11902 | -0.036621 | 0.018311 | 0.086975 | -0.091553 | -0.009155 | 0.10071 | 0.013733 | 0.068665 | -0.009155 | -122.3373 | -122.438 | 0.1648 | 0.064087 | -0.018311 | 0.073242 | -0.009156 | 0.009155 | -122.2824 | -122.3785 | 0.20142 | 0.16937 | 0.11444 | 0.16022 | 0.10529 | 0.17395 | 0.041198 | 0.19226 | 0.082398 | 0.14191 | 0.17853 | 0.13275 | 0.18768 | -122.4792 | -122.4609 | 0.032043 | 0.091553 | 0.050354 | 0.11902
3358.5938 | 122.4655 | -0.07782 | 122.3694 | -0.013657 | -0.0049923 | 0.0015701 | -0.014665 | -0.0046954 | -0.010683 | -0.0040439 | -0.0082093 | 0.009848 | 0.00037383 | -0.0045865 | -0.018209 | 0.022217 | -0.000784 | -0.068665 | 0.022888 | -0.064087 | -0.041199 | 0.091553 | -0.082397 | -0.013733 | 0.041199 | 0.054932 | -0.068665 | 0.013733 | 0.15106 | 0.036621 | 0.10071 | 0.013733 | -122.3465 | -122.4106 | 0.16937 | 0.064087 | -0.004577 | 0.050354 | -0.01831 | 0.009155 | -122.3145 | -122.3557 | 0.22888 | 0.17853 | 0.11444 | 0.16937 | 0.10529 | 0.15564 | 0.022888 | 0.21973 | 0.082398 | 0.086975 | 0.1236 | 0.10071 | 0.13275 | -122.4335 | -122.438 | 0.036621 | 0.091553 | 0.009155 | 0.11902
3360.2812 | 122.438 | -0.1236 | 122.3923 | -0.013657 | -0.0067013 | 0.0011429 | -0.012743 | -0.0012774 | -0.010043 | -0.0063937 | -0.0082093 | 0.011771 | 0.0012282 | 0.0043857 | -0.017996 | 0.022644 | -0.0027066 | -0.09613 | 0.064087 | -0.09613 | -0.10986 | -0.009155 | -0.12817 | -0.064087 | -0.041199 | 0.082397 | -0.082397 | -0.036621 | 0.10529 | -0.009155 | 0.054932 | 0.027466 | -122.3282 | -122.5021 | 0.11444 | 0.059509 | -0.004578 | 0.032043 | -0.032044 | 0.041199 | -122.3099 | -122.4289 | 0.22888 | 0.17853 | 0.11444 | 0.13733 | 0.073242 | 0.086975 | -0.013733 | 0.18768 | 0.045776 | 0.16022 | 0.16479 | 0.18768 | 0.20599 | -122.4884 | -122.4747 | 0.013733 | 0.086975 | 0.027466 | 0.082397
3362.0469 | 122.3923 | -0.10071 | 122.2504 | -0.013657 | -0.0049923 | 0.0015701 | -0.012315 | 0.0025678 | -0.0096151 | -0.014298 | -0.0051575 | 0.013052 | 0.0020828 | -0.0030911 | -0.014364 | 0.018372 | -0.003561 | -0.064087 | 0.041199 | -0.091553 | -0.064087 | 0.045776 | -0.09613 | -0.041199 | 0.027466 | 0.082397 | -0.086975 | 0.009155 | 0.13275 | 0.036621 | 0.073242 | 0.009155 | -122.2092 | -122.3145 | 0.14648 | 0.059509 | 0.004578 | 0.050354 | -0.004577 | 0.013733 | -122.168 | -122.2412 | 0.23346 | 0.17395 | 0.13733 | 0.16022 | 0.1236 | 0.13733 | 0.027466 | 0.21973 | 0.09613 | 0.13275 | 0.16937 | 0.14191 | 0.18311 | -122.3419 | -122.3373 | 0.036621 | 0.10986 | 0.036621 | 0.12817
3363.8125 | 122.4014 | -0.10529 | 122.1909 | -0.013657 | -0.0069149 | 0.00028845 | -0.011888 | 0.00021799 | -0.010043 | -0.0034031 | -0.0082093 | 0.011771 | 0.0018692 | -0.0043729 | -0.016714 | 0.021362 | 0.0007114 | -0.091553 | 0.064087 | -0.11444 | -0.10529 | 0.004578 | -0.11444 | -0.045776 | -0.027466 | 0.091553 | -0.082397 | -0.009155 | 0.10986 | 0.013733 | 0.086975 | -0.009155 | -122.1268 | -122.2961 | 0.10986 | 0.05951 | -0.009155 | 0.068665 | 0 | 0.022889 | -122.0993 | -122.2 | 0.21515 | 0.19226 | 0.11902 | 0.16937 | 0.09613 | 0.11902 | 0.009155 | 0.19226 | 0.073242 | 0.17853 | 0.17395 | 0.16937 | 0.19684 | -122.3053 | -122.2733 | 0 | 0.096131 | 0.013733 | 0.07782
3365.5781 | 122.319 | -0.10986 | 122.1771 | -0.021286 | -0.0062741 | -0.01317 | -0.012315 | 0.0017132 | -0.02051 | -0.014725 | -0.0051575 | 0.013693 | 0.0035782 | 0.00075412 | -0.019064 | 0.020935 | 0.0011386 | -0.086975 | 0.041199 | -0.09613 | -0.1236 | -0.036621 | -0.1831 | -0.091553 | -0.068665 | 0.09613 | -0.091553 | -0.068665 | 0.027466 | -0.07782 | 0.027466 | 0.013733 | -122.1359 | -122.3007 | 0.073242 | 0.01831 | -0.073242 | 0.004577 | -0.086975 | 0.01831 | -122.081 | -122.2458 | 0.13733 | 0.13733 | 0.032043 | 0.11902 | 0.013733 | 0.059509 | -0.027466 | 0.11902 | 0.022888 | 0.13733 | 0.18768 | 0.15106 | 0.20599 | -122.2733 | -122.2687 | -0.013733 | 0.041198 | 0.022888 | 0.041198
3367.2969 | 122.2275 | -0.10529 | 122.3785 | -0.013657 | -0.0017881 | -0.0065475 | -0.014879 | 0.0049176 | -0.016238 | -0.011307 | 0.0009461 | 0.012198 | 0.003151 | -0.0013821 | -0.013723 | 0.018372 | -0.005911 | -0.050354 | 0.054932 | -0.10529 | -0.054932 | 0.068665 | -0.10529 | -0.022888 | 0.036621 | 0.073242 | -0.073242 | 0.004578 | 0.11902 | 0.018311 | 0.086975 | 0 | -122.3236 | -122.4335 | 0.17395 | 0.082398 | 0 | 0.082398 | 0 | 0.032044 | -122.3053 | -122.374 | 0.22431 | 0.19226 | 0.1236 | 0.16022 | 0.091553 | 0.17395 | 0.050354 | 0.19226 | 0.07782 | 0.16022 | 0.14648 | 0.16022 | 0.17853 | -122.4838 | -122.4518 | 0.050354 | 0.10986 | 0.054932 | 0.14191
3369 | 122.4701 | -0.082397 | 122.406 | -0.013657 | -0.0045651 | 0.0052017 | -0.01317 | 0.0014996 | -0.010043 | -0.0063937 | 0.0009461 | 0.010702 | 0.0027236 | -0.00010048 | -0.017782 | 0.021576 | 0.0024204 | -0.10071 | 0.064087 | -0.10986 | -0.10071 | 0 | -0.15106 | -0.068665 | -0.022888 | 0.07782 | -0.082397 | 0.004578 | 0.09613 | 0.004578 | 0.086975 | -0.027466 | -122.3419 | -122.5067 | 0.082397 | 0.013732 | -0.068665 | 0.041198 | -0.041199 | 0 | -122.3282 | -122.4014 | 0.17853 | 0.16937 | 0.086975 | 0.16937 | 0.086975 | 0.10986 | 0.009155 | 0.17853 | 0.086975 | 0.17395 | 0.16022 | 0.14648 | 0.16022 | -122.5159 | -122.4884 | -0.018311 | 0.086975 | -0.018311 | 0.059509
3370.7031 | 122.3465 | -0.086975 | 122.4014 | -0.0060272 | -0.0047787 | -0.00013895 | -0.015733 | -0.0010638 | -0.01282 | -0.010453 | -0.0051575 | 0.013052 | 0.00080103 | 0.0048129 | -0.015219 | 0.020935 | -0.0018522 | -0.054932 | 0.054932 | -0.10529 | -0.059509 | 0.059509 | -0.091553 | -0.027466 | 0.036621 | 0.082397 | -0.073242 | 0.004578 | 0.13275 | 0.045776 | 0.09613 | -0.018311 | -122.3465 | -122.4609 | 0.14648 | 0.059509 | -0.004578 | 0.07782 | 0.013733 | 0.013733 | -122.319 | -122.3969 | 0.21973 | 0.1831 | 0.13275 | 0.16937 | 0.11902 | 0.16479 | 0.045777 | 0.20599 | 0.07782 | 0.16022 | 0.15564 | 0.14191 | 0.16937 | -122.5067 | -122.4747 | 0.027466 | 0.091553 | 0.032043 | 0.1236
3372.4531 | 122.4518 | -0.082397 | 122.406 | -0.013657 | -0.0032833 | -0.00099335 | -0.011034 | 0.00043159 | -0.010043 | -0.0029759 | -0.0051575 | 0.013052 | 0.0029372 | 0.0037447 | -0.017355 | 0.023712 | 0.0019932 | -0.10071 | 0.054932 | -0.11902 | -0.12817 | 0 | -0.1831 | -0.07782 | -0.018311 | 0.086975 | -0.07782 | -0.018311 | 0.068665 | -0.027466 | 0.064087 | -0.036622 | -122.3511 | -122.5342 | 0.082397 | 0.004577 | -0.10071 | 0.041199 | -0.064086 | 0.004577 | -122.319 | -122.4243 | 0.15106 | 0.14648 | 0.054931 | 0.14191 | 0.050354 | 0.11902 | -0.009155 | 0.14649 | 0.059509 | 0.17395 | 0.16479 | 0.13733 | 0.16937 | -122.525 | -122.4838 | -0.045777 | 0.064086 | -0.018311 | 0.064086
3374.1562 | 122.5433 | -0.059509 | 122.3831 | -0.013657 | -0.0064877 | 0.0013565 | -0.014452 | -0.0053362 | -0.0098287 | -0.0023349 | -0.0021057 | 0.01113 | 0.0020828 | -0.0026639 | -0.016714 | 0.020935 | -0.0016384 | -0.050354 | 0 | -0.07782 | 0.009155 | 0.15106 | -0.009155 | 0.045776 | 0.11902 | 0.059509 | -0.054932 | 0.045776 | 0.20142 | 0.10071 | 0.12817 | -0.018311 | -122.3831 | -122.374 | 0.21057 | 0.10528 | 0.050354 | 0.1236 | 0.068665 | 0.004577 | -122.3236 | -122.3373 | 0.26093 | 0.18768 | 0.16022 | 0.18311 | 0.15564 | 0.22888 | 0.086975 | 0.25635 | 0.10071 | 0.07782 | 0.11444 | 0.059509 | 0.11902 | -122.4609 | -122.438 | 0.068664 | 0.10528 | 0.009155 | 0.17853
3375.9219 | 122.4472 | -0.11902 | 122.4426 | -0.013657 | -0.0052059 | -0.00013895 | -0.014879 | 0.0032086 | -0.012179 | -0.0046847 | -0.0082093 | 0.012411 | 0.0033646 | -0.00031408 | -0.017782 | 0.024139 | -0.004202 | -0.086975 | 0.045776 | -0.11902 | -0.11902 | -0.009155 | -0.15106 | -0.054932 | -0.050354 | 0.082397 | -0.10529 | -0.050354 | 0.073242 | -0.018311 | 0.054932 | 0 | -122.3969 | -122.5616 | 0.10986 | 0.064087 | -0.032043 | 0.064087 | -0.032043 | 0.013733 | -122.3602 | -122.493 | 0.19226 | 0.17395 | 0.10071 | 0.16022 | 0.086975 | 0.10986 | 0 | 0.17853 | 0.054932 | 0.16479 | 0.18768 | 0.16479 | 0.20142 | -122.5616 | -122.5479 | 0 | 0.068665 | 0.032044 | 0.068665
3377.6875 | 122.4197 | -0.10986 | 122.438 | -0.021286 | -0.0064877 | -0.0067611 | -0.012315 | 0.0014996 | -0.015383 | -0.0051121 | -0.011261 | 0.01348 | 0.0027236 | 0.0041721 | -0.019277 | 0.023285 | 7.04e-05 | -0.091553 | 0.068665 | -0.13275 | -0.12817 | -0.027466 | -0.18768 | -0.10071 | -0.054932 | 0.073242 | -0.086975 | -0.036621 | 0.036621 | -0.045776 | 0.045776 | -0.022888 | -122.3694 | -122.5662 | 0.082397 | 0.009155 | -0.07782 | 0.032043 | -0.054932 | 0.022888 | -122.3648 | -122.4747 | 0.14648 | 0.15564 | 0.064087 | 0.13275 | 0.041199 | 0.10529 | 0.004577 | 0.1236 | 0.050354 | 0.20142 | 0.16022 | 0.17853 | 0.18311 | -122.5708 | -122.525 | -0.018311 | 0.073242 | 0.01831 | 0.054931
3379.4375 | 122.4655 | -0.09613 | 122.438 | -0.013657 | -0.0060605 | 0.0011429 | -0.012102 | 0.00043159 | -0.011111 | -0.0091709 | -0.0051575 | 0.011771 | 0.0035782 | 0.0056675 | -0.017996 | 0.021576 | -0.0012112 | -0.059509 | 0.045776 | -0.086975 | -0.054932 | 0.059509 | -0.10071 | -0.022888 | 0.013733 | 0.073242 | -0.07782 | 0.009155 | 0.1236 | 0.022888 | 0.086975 | 0.009155 | -122.3923 | -122.493 | 0.15564 | 0.073242 | -0.004578 | 0.064087 | -0.013733 | 0.01831 | -122.3648 | -122.4289 | 0.21973 | 0.1831 | 0.11902 | 0.16479 | 0.10071 | 0.14648 | 0.032043 | 0.20142 | 0.086975 | 0.13275 | 0.15106 | 0.14191 | 0.16937 | -122.525 | -122.5159 | 0.041198 | 0.10528 | 0.036621 | 0.10986
3381.1406 | 122.5525 | -0.086975 | 122.3831 | -0.021286 | -0.0088375 | -0.00056615 | -0.01552 | -0.0027728 | -0.012392 | -0.0029759 | -0.0051575 | 0.0092072 | 0.0012282 | -0.0039457 | -0.017996 | 0.021576 | -0.0003568 | -0.041199 | 0.013733 | -0.091553 | 0.004578 | 0.1831 | 0 | 0.082397 | 0.14191 | 0.050354 | -0.064087 | 0.054932 | 0.22888 | 0.13275 | 0.14191 | -0.004578 | -122.3694 | -122.3785 | 0.27008 | 0.16937 | 0.086975 | 0.17395 | 0.091553 | 0.022888 | -122.3328 | -122.3282 | 0.31586 | 0.22888 | 0.21973 | 0.20599 | 0.19684 | 0.27466 | 0.096131 | 0.29297 | 0.11902 | 0.10529 | 0.11444 | 0.10071 | 0.13733 | -122.4747 | -122.4472 | 0.091553 | 0.14191 | 0.045776 | 0.22888
3382.9062 | 122.4884 | -0.09613 | 122.438 | -0.0060272 | -0.0037107 | 0.0015701 | -0.011888 | 0.0017132 | -0.0087607 | -0.0055393 | -0.0051575 | 0.011343 | 0.0037918 | 0.0071627 | -0.01885 | 0.023926 | -0.0061246 | -0.086975 | 0.054932 | -0.10529 | -0.10986 | 0.004578 | -0.16022 | -0.07782 | 0 | 0.082397 | -0.082397 | 0.009155 | 0.09613 | 0.004578 | 0.07782 | -0.009156 | -122.3831 | -122.5479 | 0.10071 | 0.01831 | -0.064087 | 0.027466 | -0.054931 | 0.013733 | -122.3557 | -122.4289 | 0.19226 | 0.17395 | 0.10071 | 0.16022 | 0.086975 | 0.10986 | -0.004577 | 0.17853 | 0.091552 | 0.16022 | 0.16479 | 0.15106 | 0.17853 | -122.5433 | -122.5204 | -0.013733 | 0.10528 | 0.009155 | 0.09613
3384.6562 | 122.5296 | -0.086975 | 122.4243 | -0.013657 | -0.0056333 | 0.0034927 | -0.014452 | 0.0025678 | -0.011324 | -0.0059665 | -0.0021057 | 0.010702 | -5.3368e-05 | -0.0052273 | -0.014791 | 0.020721 | -0.0046292 | -0.07782 | 0.027466 | -0.082397 | -0.041199 | 0.073242 | -0.086975 | 0.009155 | 0.018311 | 0.059509 | -0.068665 | 0.004578 | 0.12817 | 0.045776 | 0.10071 | 0.004578 | -122.3969 | -122.4655 | 0.16022 | 0.09613 | 0 | 0.091552 | -0.004578 | 0.01831 | -122.3648 | -122.4197 | 0.21515 | 0.18768 | 0.13275 | 0.16937 | 0.11444 | 0.15564 | 0.041198 | 0.19684 | 0.073243 | 0.10986 | 0.12817 | 0.11444 | 0.14648 | -122.5067 | -122.493 | 0.045776 | 0.091553 | 0.009155 | 0.10529
3386.4062 | 122.58 | -0.064087 | 122.3831 | -0.021286 | -0.0043515 | 0.0028519 | -0.015093 | 0.0027814 | -0.0096151 | -0.0046847 | -0.0021057 | 0.010702 | 0.0020828 | 0.00096772 | -0.018637 | 0.022858 | -0.0037748 | -0.013733 | 0.009155 | -0.064087 | 0.022888 | 0.11902 | -0.064087 | 0.041199 | 0.11444 | 0.059509 | -0.059509 | 0.086975 | 0.18768 | 0.082397 | 0.14191 | 0 | -122.374 | -122.3602 | 0.18311 | 0.10529 | 0 | 0.10529 | 0 | 0.004578 | -122.3236 | -122.2961 | 0.25177 | 0.20599 | 0.14648 | 0.20142 | 0.14191 | 0.18311 | 0.086975 | 0.24719 | 0.14648 | 0.073242 | 0.11902 | 0.073242 | 0.1236 | -122.4472 | -122.4426 | 0.086975 | 0.15106 | 0.050354 | 0.17853
3388.1094 | 122.5296 | -0.086975 | 122.3877 | -0.021286 | -0.0058469 | 0.0024247 | -0.015947 | -0.0012774 | -0.010683 | -0.0044711 | -0.0051575 | 0.010275 | 0.00037383 | -0.0058683 | -0.018209 | 0.021576 | -0.0027066 | -0.07782 | 0.022888 | -0.064087 | -0.036621 | 0.091553 | -0.086975 | 0.009155 | 0.041199 | 0.050354 | -0.059509 | 0.036621 | 0.14191 | 0.041199 | 0.09613 | 0.022888 | -122.3648 | -122.4243 | 0.17853 | 0.09613 | 0 | 0.073242 | -0.022888 | 0.027466 | -122.3373 | -122.3511 | 0.22888 | 0.1831 | 0.12817 | 0.15564 | 0.10071 | 0.15564 | 0.027466 | 0.20142 | 0.09613 | 0.086975 | 0.10986 | 0.10986 | 0.13733 | -122.4518 | -122.4472 | 0.050354 | 0.1236 | 0.009155 | 0.12817
3389.8594 | 122.3694 | -0.10071 | 122.4518 | -0.013657 | -0.013324 | 0.10881 | -0.012743 | -0.006618 | -0.012606 | -0.021347 | -0.0051575 | 0.010916 | -0.0045396 | -0.00031408 | -0.016073 | 0.015808 | -0.002493 | -0.059509 | 0.073242 | -0.11902 | -0.09613 | 0 | -0.17395 | -0.07782 | -0.013733 | 0.091553 | -0.07782 | -0.050354 | 0.059509 | -0.032043 | 0.032043 | -0.018311 | -122.3785 | -122.5479 | 0.10071 | 0.022888 | -0.073242 | 0.041199 | -0.054931 | 0.022888 | -122.3602 | -122.5021 | 0.16022 | 0.13275 | 0.068665 | 0.10986 | 0.045777 | 0.11902 | 0.022889 | 0.13733 | 0.027466 | 0.19226 | 0.16937 | 0.17395 | 0.19226 | -122.5708 | -122.5296 | 0.004578 | 0.050354 | 0.041199 | 0.086975
3391.625 | 122.5113 | -0.09613 | 122.4197 | -0.013657 | -0.0047787 | 0.0011429 | -0.015093 | 0.00021799 | -0.010256 | -0.0044711 | -0.0082093 | 0.010062 | 0.00037383 | -0.0056547 | -0.0165 | 0.021362 | -0.0046292 | -0.073242 | 0.013733 | -0.073242 | -0.059509 | 0.059509 | -0.10529 | -0.018311 | 0.032043 | 0.054932 | -0.082397 | 0.009155 | 0.13275 | 0.036621 | 0.082397 | 0.022888 | -122.406 | -122.4792 | 0.15564 | 0.077819 | -0.009156 | 0.054931 | -0.032044 | 0.013733 | -122.3648 | -122.4106 | 0.22888 | 0.17853 | 0.13275 | 0.16479 | 0.11902 | 0.13275 | 0.013733 | 0.21515 | 0.091552 | 0.086975 | 0.13733 | 0.10986 | 0.15106 | -122.493 | -122.5021 | 0.036621 | 0.10528 | 0.022888 | 0.12817
3393.3281 | 122.5845 | -0.068665 | 122.4106 | -0.021286 | -0.0081967 | 0.0022111 | -0.013597 | -0.0029864 | -0.011965 | -0.0059665 | -0.0051575 | 0.011343 | 0.00058743 | 0.0011813 | -0.017782 | 0.019867 | -0.0022794 | -0.064087 | 0.032043 | -0.086975 | -0.009155 | 0.13275 | -0.009155 | 0.050354 | 0.11902 | 0.068665 | -0.064087 | 0.07782 | 0.22888 | 0.11902 | 0.15106 | -0.01831 | -122.3785 | -122.4197 | 0.20142 | 0.11902 | 0.05951 | 0.13733 | 0.07782 | 0.004578 | -122.3419 | -122.3328 | 0.29755 | 0.21973 | 0.18768 | 0.21515 | 0.18311 | 0.21973 | 0.07782 | 0.29297 | 0.14191 | 0.11902 | 0.13275 | 0.10071 | 0.13733 | -122.4976 | -122.4747 | 0.05951 | 0.14649 | 0.004578 | 0.18768
3395.0781 | 122.5616 | -0.073242 | 122.4243 | -0.0060272 | -0.0079831 | 0.0015701 | -0.015093 | 0.0014996 | -0.012392 | -0.0074619 | -0.011261 | 0.010062 | 0.0022964 | 0.00054052 | -0.018637 | 0.020935 | -0.0039884 | -0.032043 | 0.009155 | -0.082397 | 0.027466 | 0.13275 | -0.009155 | 0.032043 | 0.10986 | 0.068665 | -0.041199 | 0.059509 | 0.18768 | 0.11444 | 0.1236 | -0.009155 | -122.4152 | -122.3969 | 0.20599 | 0.10529 | 0.064087 | 0.11444 | 0.073242 | 0.032043 | -122.3557 | -122.3648 | 0.26092 | 0.19684 | 0.18768 | 0.16479 | 0.15564 | 0.21515 | 0.10986 | 0.22888 | 0.10071 | 0.091552 | 0.10986 | 0.082397 | 0.14191 | -122.5067 | -122.4655 | 0.10071 | 0.13275 | 0.041199 | 0.18311
3396.8438 | 122.5342 | -0.091553 | 122.4197 | -0.013657 | -0.0069149 | -0.00035255 | -0.015733 | -0.001491 | -0.0098287 | -0.0027621 | -0.0051575 | 0.010916 | 0.0022964 | 0.0016085 | -0.0165 | 0.020294 | -0.0012112 | -0.068665 | 0.027466 | -0.082397 | -0.050354 | 0.059509 | -0.11444 | 0 | 0.022888 | 0.082397 | -0.068665 | 0.018311 | 0.15564 | 0.045776 | 0.09613 | 0.009156 | -122.3923 | -122.4701 | 0.15106 | 0.091553 | -0.022888 | 0.082397 | -0.032044 | 0.022888 | -122.3373 | -122.4014 | 0.24719 | 0.18768 | 0.13733 | 0.16479 | 0.11444 | 0.14191 | 0.032043 | 0.22431 | 0.086976 | 0.10986 | 0.15106 | 0.11902 | 0.17395 | -122.5021 | -122.4884 | 0.041199 | 0.10986 | 0.022888 | 0.11444
3398.6094 | 122.5662 | -0.050354 | 122.406 | -0.013657 | -0.0030697 | 0.0019975 | -0.014238 | 4.192e-06 | -0.0087607 | -0.0046847 | -0.0021057 | 0.012411 | 0.00251 | 0.0020359 | -0.020132 | 0.024353 | -0.0027066 | 0 | 0.009155 | -0.059509 | 0.032043 | 0.12817 | -0.064087 | 0.018311 | 0.10986 | 0.050354 | -0.050354 | 0.091553 | 0.1831 | 0.086975 | 0.14191 | -0.009155 | -122.3969 | -122.374 | 0.17853 | 0.068665 | -0.013733 | 0.07782 | -0.004578 | 0 | -122.3557 | -122.3145 | 0.23346 | 0.19226 | 0.13733 | 0.19226 | 0.13733 | 0.18768 | 0.091552 | 0.23346 | 0.14191 | 0.068664 | 0.10071 | 0.059509 | 0.10071 | -122.4655 | -122.4564 | 0.082397 | 0.14191 | 0.050354 | 0.16022
3400.2969 | 122.4701 | -0.11902 | 122.4747 | 0.0016023 | -0.0069149 | 0.00028845 | -0.016161 | -0.0023456 | -0.0098287 | -0.0068211 | -0.0051575 | 0.011343 | 0.0027236 | -0.0024503 | -0.016714 | 0.023499 | -0.0037748 | -0.059509 | 0.032043 | -0.10529 | -0.041199 | 0.073242 | -0.07782 | -0.022888 | 0.009155 | 0.07782 | -0.07782 | -0.041199 | 0.10071 | -0.009155 | 0.041199 | 0.013733 | -122.4426 | -122.5159 | 0.19226 | 0.096131 | 0.041199 | 0.082398 | 0.027466 | 0.041199 | -122.3969 | -122.5159 | 0.21973 | 0.16022 | 0.10986 | 0.11902 | 0.068665 | 0.17853 | 0.064087 | 0.17853 | 0.036621 | 0.13733 | 0.15564 | 0.15106 | 0.19684 | -122.58 | -122.5525 | 0.07782 | 0.07782 | 0.05951 | 0.12817
3402.0625 | 122.4747 | -0.10986 | 122.4518 | -0.0060272 | -0.0075559 | -0.00035255 | -0.014024 | 4.192e-06 | -0.011111 | -0.0048985 | -0.0021057 | 0.010702 | 0.0016556 | 0.0037447 | -0.017568 | 0.021576 | 0.0004978 | -0.054932 | 0.032043 | -0.07782 | -0.045776 | 0.091553 | -0.068665 | 0 | 0.009155 | 0.082397 | -0.091553 | -0.036621 | 0.10986 | -0.004578 | 0.054932 | 0.032043 | -122.4197 | -122.4976 | 0.20142 | 0.10986 | 0.041198 | 0.07782 | 0.009155 | 0.01831 | -122.3694 | -122.4884 | 0.21973 | 0.16479 | 0.10529 | 0.14649 | 0.086975 | 0.16937 | 0.032044 | 0.20142 | 0.054932 | 0.10986 | 0.17395 | 0.14191 | 0.19226 | -122.5296 | -122.5433 | 0.064087 | 0.073242 | 0.054931 | 0.11902
3403.8125 | 122.5983 | -0.054932 | 122.4197 | -0.013657 | -0.010547 | -0.0016341 | -0.015947 | -0.0032 | -0.011538 | -0.0059665 | -0.0021057 | 0.012198 | 0.00251 | -0.0035183 | -0.017141 | 0.021576 | 0.000925 | -0.032043 | 0.022888 | -0.086975 | 0.009155 | 0.16022 | -0.018311 | 0.054932 | 0.1236 | 0.045776 | -0.064087 | 0.068665 | 0.23804 | 0.14648 | 0.15564 | -0.032043 | -122.3969 | -122.4106 | 0.21515 | 0.10986 | 0.036621 | 0.14191 | 0.068664 | -0.009155 | -122.374 | -122.3511 | 0.29297 | 0.21057 | 0.20142 | 0.21973 | 0.21057 | 0.24719 | 0.09613 | 0.30212 | 0.13275 | 0.10986 | 0.10986 | 0.07782 | 0.10071 | -122.5067 | -122.4838 | 0.064087 | 0.1236 | 0.022889 | 0.17853
3405.5625 | 122.4655 | -0.11444 | 122.4426 | -0.013657 | -0.0099057 | 7.4854e-05 | -0.014024 | -0.0010638 | -0.010043 | -0.0016941 | -0.0082093 | 0.011984 | 0.0018692 | -0.0045865 | -0.017568 | 0.022217 | -0.0009976 | -0.073242 | 0.054932 | -0.082397 | -0.082397 | 0.050354 | -0.11444 | -0.036621 | -0.027466 | 0.073242 | -0.09613 | -0.045776 | 0.082397 | -0.009155 | 0.027466 | 0.032044 | -122.3877 | -122.525 | 0.16479 | 0.07782 | 0 | 0.045776 | -0.032044 | 0.018311 | -122.3694 | -122.4884 | 0.19684 | 0.14191 | 0.10529 | 0.1236 | 0.086975 | 0.13275 | 0 | 0.17853 | 0.050354 | 0.13733 | 0.16937 | 0.16937 | 0.18768 | -122.525 | -122.5388 | 0.032044 | 0.068665 | 0.041199 | 0.086975
3407.2656 | 122.3648 | -0.091553 | 122.0535 | -0.021286 | -0.012469 | 0.10902 | -0.012529 | -0.0078998 | -0.024569 | -0.021561 | -0.0021057 | 0.010702 | -0.005394 | -0.010995 | -0.019918 | 0.0032044 | -0.0037748 | -0.054932 | 0.041199 | -0.10529 | -0.059509 | 0.059509 | -0.12817 | -0.045776 | 0.032043 | 0.073242 | -0.086975 | -0.013733 | 0.073242 | -0.036621 | 0.041199 | -0.013733 | -122.0123 | -122.113 | 0.15106 | 0.045777 | -0.036621 | 0.05951 | -0.022888 | 0.004578 | -121.9803 | -122.0673 | 0.16479 | 0.13275 | 0.054932 | 0.12817 | 0.050354 | 0.16479 | 0.045777 | 0.16022 | 0.073242 | 0.14649 | 0.16022 | 0.13275 | 0.16479 | -122.1588 | -122.1405 | 0.032044 | 0.07782 | 0.036621 | 0.1236
3409.0312 | 122.5342 | -0.086975 | 122.4518 | -0.013657 | -0.0034971 | 0.0028519 | -0.012956 | 0.0010724 | -0.011538 | -0.0057529 | -0.0051575 | 0.011557 | 0.0016556 | -0.00095488 | -0.017996 | 0.022003 | -0.0012112 | -0.10986 | 0.064087 | -0.10529 | -0.086975 | 0.022888 | -0.16479 | -0.050354 | 0.004578 | 0.068665 | -0.082397 | 0.009155 | 0.11902 | 0.009155 | 0.091553 | -0.018311 | -122.3877 | -122.5388 | 0.10986 | 0.036621 | -0.07782 | 0.054932 | -0.059509 | 0.004578 | -122.3831 | -122.4426 | 0.20599 | 0.17853 | 0.09613 | 0.17395 | 0.091552 | 0.12817 | 0.018311 | 0.20142 | 0.091552 | 0.16937 | 0.15106 | 0.15106 | 0.15564 | -122.5571 | -122.5342 | 0 | 0.09613 | -0.022888 | 0.091553
3410.7344 | 122.438 | -0.091553 | 122.4564 | -0.013657 | -0.0058469 | -0.0018479 | -0.014238 | -0.0040546 | -0.01346 | -0.01387 | -0.0021057 | 0.012625 | 0.001442 | -0.0041593 | -0.013296 | 0.013031 | -0.0001432 | -0.036621 | 0.045776 | -0.10529 | -0.059509 | 0.064087 | -0.10071 | -0.036621 | 0.041199 | 0.07782 | -0.086975 | 0.018311 | 0.13275 | 0.018311 | 0.082397 | -0.013733 | -122.4106 | -122.5159 | 0.15564 | 0.054932 | -0.009155 | 0.068665 | 0.004578 | 0.004578 | -122.3785 | -122.438 | 0.2243 | 0.17395 | 0.10986 | 0.16937 | 0.10529 | 0.16937 | 0.045777 | 0.21973 | 0.10529 | 0.15106 | 0.16479 | 0.13733 | 0.16937 | -122.5616 | -122.5433 | 0.032044 | 0.10986 | 0.054932 | 0.13275
3412.5 | 122.5754 | -0.050354 | 122.4426 | -0.021286 | -0.0047787 | 0.0011429 | -0.013384 | 0.0032086 | -0.010897 | -0.0053257 | -0.0051575 | 0.010702 | 0.00080103 | 0.00075412 | -0.016928 | 0.022644 | -0.0005704 | -0.050354 | 0.027466 | -0.07782 | -0.013733 | 0.091553 | -0.091553 | 0.009155 | 0.082397 | 0.064087 | -0.064087 | 0.082397 | 0.17853 | 0.073242 | 0.15106 | -0.027466 | -122.4152 | -122.4564 | 0.14191 | 0.059509 | -0.041199 | 0.086975 | -0.013733 | -0.013733 | -122.3785 | -122.3602 | 0.22888 | 0.20142 | 0.1236 | 0.21515 | 0.13733 | 0.16937 | 0.064087 | 0.24261 | 0.14648 | 0.10529 | 0.12817 | 0.07782 | 0.11444 | -122.5204 | -122.5067 | 0.036621 | 0.13275 | 0 | 0.13275
3414.2656 | 122.5937 | -0.050354 | 122.4426 | -0.0060272 | -0.0058469 | 0.0039201 | -0.013384 | 0.0049176 | -0.0098287 | -0.0038303 | -0.0021057 | 0.011771 | 0.003151 | -0.0013821 | -0.018209 | 0.022217 | -0.0022794 | -0.036621 | 0.027466 | -0.086975 | -0.013733 | 0.10986 | -0.082397 | 0.018311 | 0.091553 | 0.059509 | -0.050354 | 0.07782 | 0.19684 | 0.086975 | 0.14648 | -0.036621 | -122.4152 | -122.4564 | 0.16022 | 0.068665 | -0.032043 | 0.10529 | 0.004578 | 0 | -122.3831 | -122.3648 | 0.24719 | 0.19684 | 0.13733 | 0.19684 | 0.13733 | 0.19684 | 0.073242 | 0.24719 | 0.12817 | 0.11444 | 0.10986 | 0.07782 | 0.10986 | -122.5296 | -122.493 | 0.036621 | 0.12817 | 0.013733 | 0.14191
3416.0312 | 122.5113 | -0.11902 | 122.4838 | -0.0060272 | -0.0071285 | -0.00013895 | -0.014665 | 0.00021799 | -0.010683 | -0.0063937 | -0.0082093 | 0.0087798 | -5.3368e-05 | -0.0043729 | -0.018637 | 0.020508 | -0.0005704 | -0.054932 | 0.045776 | -0.082397 | -0.013733 | 0.10071 | -0.050354 | 0.009155 | 0.050354 | 0.064087 | -0.082397 | -0.018311 | 0.1236 | 0.032043 | 0.073242 | 0.036622 | -122.438 | -122.4976 | 0.21973 | 0.12817 | 0.068665 | 0.091552 | 0.032043 | 0.036622 | -122.4197 | -122.5021 | 0.24261 | 0.19226 | 0.15106 | 0.15564 | 0.11444 | 0.18311 | 0.068664 | 0.20599 | 0.064086 | 0.12817 | 0.14648 | 0.16479 | 0.18311 | -122.5662 | -122.5662 | 0.10529 | 0.10071 | 0.064087 | 0.16937
3417.7344 | 122.6074 | -0.082397 | 122.4289 | -0.0060272 | -0.0056333 | 0.0026383 | -0.014024 | 0.0034222 | -0.012606 | -0.0042575 | -0.0051575 | 0.009848 | 0.0033646 | -0.0045865 | -0.019064 | 0.021149 | -0.0033474 | -0.073242 | 0.032043 | -0.073242 | -0.032043 | 0.10071 | -0.059509 | 0.027466 | 0.059509 | 0.045776 | -0.068665 | 0.032043 | 0.19226 | 0.10529 | 0.15106 | 0.009155 | -122.3969 | -122.4609 | 0.18311 | 0.10986 | 0.022888 | 0.10071 | 0.013733 | 0.013732 | -122.3831 | -122.3969 | 0.27466 | 0.23346 | 0.18768 | 0.21973 | 0.17395 | 0.17395 | 0.041199 | 0.26093 | 0.10071 | 0.10529 | 0.11444 | 0.11444 | 0.12817 | -122.5021 | -122.4976 | 0.050354 | 0.11444 | 0.009155 | 0.14191
3419.5 | 122.4884 | -0.09613 | 122.4655 | -0.0060272 | -0.0077695 | 0.00028845 | -0.011247 | -0.002132 | -0.013033 | -0.0068211 | -0.0051575 | 0.013052 | 0.0020828 | 0.0028903 | -0.016714 | 0.02243 | -0.0009976 | -0.13275 | 0.045776 | -0.13275 | -0.11902 | -0.009155 | -0.13275 | -0.059509 | -0.059509 | 0.10071 | -0.10529 | -0.073242 | 0.068665 | -0.013733 | 0.041199 | -0.036621 | -122.4197 | -122.5845 | 0.086975 | 0.036621 | -0.036621 | 0.073242 | 0 | -0.009156 | -122.3648 | -122.5388 | 0.16479 | 0.13733 | 0.082397 | 0.14649 | 0.091553 | 0.1236 | 0.013732 | 0.17395 | 0.032044 | 0.17853 | 0.20599 | 0.14191 | 0.19684 | -122.5983 | -122.5708 | -0.022889 | 0.022888 | -0.036621 | 0.036621
3421.2031 | 122.5021 | -0.10529 | 122.4838 | 0.0016023 | -0.0075559 | 0.00028845 | -0.013384 | -0.0032 | -0.011965 | -0.0040439 | -0.0051575 | 0.012839 | 0.0048598 | -0.0011685 | -0.017568 | 0.023071 | -0.0027066 | -0.10071 | 0.045776 | -0.1236 | -0.10529 | -0.018311 | -0.12817 | -0.07782 | -0.064087 | 0.10071 | -0.086975 | -0.041199 | 0.086975 | -0.013733 | 0.045776 | -0.01831 | -122.438 | -122.5891 | 0.086975 | 0.027466 | -0.022888 | 0.045776 | -0.004578 | 0.018311 | -122.3831 | -122.525 | 0.19226 | 0.15106 | 0.091553 | 0.13275 | 0.073242 | 0.10528 | 0.01831 | 0.17395 | 0.045776 | 0.16937 | 0.18768 | 0.15106 | 0.20599 | -122.6074 | -122.5708 | 0 | 0.064087 | 0.004578 | 0.041199
3422.9531 | 122.5983 | -0.068665 | 122.4335 | -0.013657 | -0.0032833 | 0.0024247 | -0.014238 | 0.0023542 | -0.010897 | -0.0042575 | -0.0051575 | 0.0089934 | 0.0022964 | -0.00010048 | -0.018209 | 0.02179 | -0.0020658 | -0.004578 | 0.013733 | -0.059509 | 0.018311 | 0.13733 | -0.059509 | 0.036621 | 0.11444 | 0.059509 | -0.036621 | 0.09613 | 0.19684 | 0.10071 | 0.15106 | 0.009156 | -122.4197 | -122.4152 | 0.20599 | 0.10529 | 0.009156 | 0.09613 | 0 | 0.032044 | -122.374 | -122.3373 | 0.2655 | 0.21973 | 0.16937 | 0.18768 | 0.13733 | 0.19684 | 0.07782 | 0.23346 | 0.13275 | 0.073242 | 0.09613 | 0.082398 | 0.12817 | -122.493 | -122.4701 | 0.086976 | 0.16479 | 0.064087 | 0.18311
3424.7031 | 122.4838 | -0.09613 | 122.4564 | -0.013657 | -0.0028561 | -0.0039841 | -0.010393 | -0.0057636 | -0.016878 | -0.014511 | -0.0051575 | 0.01348 | 0.0033646 | -0.0022367 | -0.016928 | 0.016876 | -0.002493 | -0.054932 | 0.064087 | -0.10529 | -0.068665 | 0.032043 | -0.14648 | -0.064087 | -0.004578 | 0.07782 | -0.09613 | -0.041199 | 0.068665 | -0.041199 | 0.032043 | -0.009156 | -122.3923 | -122.525 | 0.12817 | 0.032043 | -0.050354 | 0.041199 | -0.041198 | 0 | -122.3785 | -122.4976 | 0.16479 | 0.12817 | 0.054931 | 0.12817 | 0.054931 | 0.13733 | 0.036621 | 0.16479 | 0.054931 | 0.16937 | 0.17395 | 0.16022 | 0.17395 | -122.5616 | -122.5525 | 0.027465 | 0.054931 | 0.041198 | 0.091552
3426.4531 | 122.6028 | -0.068665 | 122.4518 | -0.0060272 | -0.0079831 | -0.00035255 | -0.014879 | -0.0023456 | -0.012179 | -0.0048985 | -0.0051575 | 0.010916 | 0.0018692 | -0.0084317 | -0.01885 | 0.020508 | -0.0074064 | -0.036621 | 0.009155 | -0.082397 | 0.013733 | 0.15564 | -0.013733 | 0.041199 | 0.086975 | 0.050354 | -0.041199 | 0.054932 | 0.20142 | 0.10986 | 0.13275 | -0.013732 | -122.4426 | -122.438 | 0.22431 | 0.10986 | 0.054932 | 0.1236 | 0.068664 | 0.027466 | -122.4014 | -122.3969 | 0.27008 | 0.20142 | 0.17853 | 0.17395 | 0.15106 | 0.23804 | 0.09613 | 0.24262 | 0.096131 | 0.091552 | 0.091553 | 0.07782 | 0.11902 | -122.5342 | -122.493 | 0.082398 | 0.1236 | 0.032044 | 0.15564
3428.1719 | 122.5616 | -0.086975 | 122.4609 | -0.013657 | -0.0084103 | 0.0015701 | -0.015306 | 0.00043159 | -0.011751 | -0.0059665 | -0.0021057 | 0.010916 | 0.00080103 | 0.0011813 | -0.016928 | 0.021149 | -0.0029202 | -0.032043 | 0.027466 | -0.073242 | -0.018311 | 0.11444 | -0.032043 | 0.045776 | 0.064087 | 0.054932 | -0.059509 | 0 | 0.14648 | 0.064087 | 0.068665 | 0.013733 | -122.4335 | -122.4792 | 0.20142 | 0.13275 | 0.054932 | 0.11902 | 0.041199 | 0.027466 | -122.406 | -122.4609 | 0.23346 | 0.15564 | 0.15106 | 0.12817 | 0.1236 | 0.18768 | 0.054931 | 0.20599 | 0.059509 | 0.10071 | 0.11444 | 0.11444 | 0.14191 | -122.5342 | -122.5204 | 0.068664 | 0.086975 | 0.054932 | 0.15106
3429.9375 | 122.6395 | -0.050354 | 122.4564 | 0.0016023 | -0.0090513 | 0.0019975 | -0.015947 | -0.00085021 | -0.010043 | -0.0040439 | -0.0082093 | 0.010062 | 0.00080103 | -0.0011685 | -0.017782 | 0.022217 | 7.04e-05 | -0.059509 | 0.013733 | -0.10071 | -0.009155 | 0.12817 | -0.022888 | 0.050354 | 0.12817 | 0.050354 | -0.059509 | 0.073242 | 0.20599 | 0.13275 | 0.15564 | -0.050354 | -122.4426 | -122.4655 | 0.17853 | 0.10071 | 0.027466 | 0.15106 | 0.07782 | -0.009155 | -122.406 | -122.3831 | 0.25635 | 0.20599 | 0.18311 | 0.21515 | 0.19226 | 0.22888 | 0.091553 | 0.2655 | 0.13275 | 0.11444 | 0.10986 | 0.064087 | 0.10071 | -122.5571 | -122.5159 | 0.041199 | 0.1236 | -0.009155 | 0.17853
3431.6875 | 122.5113 | -0.10071 | 122.4976 | -0.013657 | -0.0013607 | -0.00099335 | -0.011461 | 0.0023542 | -0.011751 | -0.0066073 | -0.0082093 | 0.013693 | 0.0027236 | 0.0048129 | -0.018423 | 0.024139 | -0.0012112 | -0.09613 | 0.059509 | -0.10986 | -0.11444 | -0.018311 | -0.18768 | -0.086975 | -0.036621 | 0.091553 | -0.10071 | -0.032043 | 0.054932 | -0.050354 | 0.068665 | -0.009155 | -122.438 | -122.612 | 0.082397 | 0.013733 | -0.086975 | 0.022888 | -0.07782 | 0 | -122.406 | -122.5296 | 0.15564 | 0.16937 | 0.050354 | 0.16937 | 0.050354 | 0.091552 | -0.004578 | 0.15564 | 0.068665 | 0.16937 | 0.19226 | 0.16022 | 0.19226 | -122.6074 | -122.5983 | -0.013733 | 0.068665 | 0.004578 | 0.064087
3433.4688 | 122.4884 | -0.11444 | 122.5342 | -0.021286 | -0.011828 | 0.1086 | -0.013811 | -0.014095 | 0.056822 | -0.021561 | -0.0051575 | 0.011771 | -0.0021896 | -0.0054409 | -0.017996 | 0.013458 | -0.0027066 | -0.054932 | 0.054932 | -0.11902 | -0.07782 | 0.032043 | -0.15564 | -0.073242 | -0.004578 | 0.09613 | -0.073242 | -0.032043 | 0.064087 | -0.041199 | 0.041199 | -0.004578 | -122.4792 | -122.612 | 0.14648 | 0.041199 | -0.041199 | 0.045777 | -0.036621 | 0.041199 | -122.4381 | -122.5662 | 0.17853 | 0.15564 | 0.073242 | 0.11444 | 0.032043 | 0.15106 | 0.041199 | 0.13733 | 0.041199 | 0.17395 | 0.16937 | 0.16937 | 0.21057 | -122.6532 | -122.6074 | 0.036621 | 0.082398 | 0.059509 | 0.10986
3435.2188 | 122.612 | -0.07782 | 122.4792 | -0.013657 | -0.0049923 | 0.0026383 | -0.012315 | 0.0068402 | -0.0087607 | -0.0044711 | -0.0051575 | 0.011557 | 0.0016556 | 0.00054052 | -0.017568 | 0.022858 | -0.0031338 | -0.091553 | 0.050354 | -0.082397 | -0.064087 | 0.054932 | -0.10529 | -0.027466 | 0.064087 | 0.045776 | -0.050354 | 0.059509 | 0.16479 | 0.073242 | 0.13275 | -0.004577 | -122.4289 | -122.5433 | 0.13275 | 0.050354 | -0.027466 | 0.054931 | -0.022889 | 0.027466 | -122.4335 | -122.4197 | 0.24261 | 0.21057 | 0.15106 | 0.18311 | 0.1236 | 0.13733 | 0.01831 | 0.21515 | 0.10986 | 0.13275 | 0.09613 | 0.12817 | 0.1236 | -122.5616 | -122.5296 | 0.013733 | 0.13733 | -0.013733 | 0.14191
3436.9219 | 122.5845 | -0.059509 | 122.4655 | -0.013657 | -0.0045651 | 0.0030655 | -0.015947 | -0.00020941 | -0.011965 | -0.0053257 | -0.0021057 | 0.012625 | 0.0044326 | -0.0067227 | -0.015432 | 0.020721 | -0.002493 | -0.036621 | 0.009155 | -0.054932 | 0 | 0.13733 | -0.054932 | 0.022888 | 0.10529 | 0.041199 | -0.054932 | 0.059509 | 0.16022 | 0.07782 | 0.11902 | 0.004577 | -122.4564 | -122.4655 | 0.19684 | 0.082397 | 0.004577 | 0.07782 | 0 | 0.004577 | -122.4243 | -122.406 | 0.21973 | 0.17853 | 0.13733 | 0.17395 | 0.13275 | 0.19226 | 0.054932 | 0.21515 | 0.11444 | 0.064087 | 0.096131 | 0.068664 | 0.10071 | -122.5204 | -122.5204 | 0.059509 | 0.11902 | 0.022888 | 0.16479
3438.7031 | 122.4884 | -0.10529 | 122.525 | -0.021286 | -0.0090513 | 0.10881 | -0.01317 | -0.0044818 | -0.025423 | -0.025833 | -0.0021057 | 0.014975 | -0.0015488 | -0.0045865 | -0.015859 | 0.015167 | -0.0031338 | -0.064087 | 0.054932 | -0.10071 | -0.068665 | 0.018311 | -0.15106 | -0.068665 | -0.013733 | 0.091553 | -0.07782 | -0.041199 | 0.050354 | -0.059509 | 0.032043 | 0.004578 | -122.4701 | -122.5937 | 0.1236 | 0.036621 | -0.045776 | 0.032043 | -0.050354 | 0.027466 | -122.4335 | -122.5662 | 0.15564 | 0.13733 | 0.045777 | 0.10986 | 0.018311 | 0.11902 | 0.032043 | 0.12817 | 0.036621 | 0.15564 | 0.16937 | 0.16022 | 0.19684 | -122.6257 | -122.6028 | 0.036621 | 0.064087 | 0.041199 | 0.091553
3440.4062 | 122.5983 | -0.068665 | 122.4747 | -0.021286 | -0.0043515 | 0.0019975 | -0.015093 | -0.0017048 | -0.010043 | -0.0014805 | -0.0021057 | 0.011343 | 0.0012282 | -0.00074128 | -0.018637 | 0.02243 | -0.0003568 | -0.036621 | 0.022888 | -0.07782 | 0.004578 | 0.13275 | -0.054932 | 0.027466 | 0.11444 | 0.054932 | -0.036621 | 0.054932 | 0.18768 | 0.082397 | 0.13275 | -0.009155 | -122.4518 | -122.4701 | 0.20142 | 0.096131 | 0.013733 | 0.10529 | 0.022888 | 0.032044 | -122.4197 | -122.4197 | 0.25635 | 0.20142 | 0.15106 | 0.16937 | 0.11902 | 0.21057 | 0.082398 | 0.2243 | 0.091553 | 0.10071 | 0.091553 | 0.091553 | 0.1236 | -122.5525 | -122.5113 | 0.073243 | 0.1236 | 0.032044 | 0.18311
3442.1719 | 122.58 | -0.10529 | 122.4701 | -0.0060272 | -0.0011471 | 0.0045609 | -0.012529 | 0.0032086 | -0.0087607 | -0.0038303 | -0.0021057 | 0.012839 | 0.0035782 | -0.00010048 | -0.01885 | 0.023071 | 0.0007114 | -0.10986 | 0.064087 | -0.10986 | -0.10529 | 0.013733 | -0.16937 | -0.073242 | -0.013733 | 0.073242 | -0.09613 | -0.009155 | 0.091553 | 0.009155 | 0.064087 | -0.004577 | -122.406 | -122.5754 | 0.11902 | 0.032044 | -0.064087 | 0.036621 | -0.05951 | 0.009156 | -122.3969 | -122.4792 | 0.19684 | 0.16937 | 0.11444 | 0.16022 | 0.10528 | 0.1236 | 0.004577 | 0.18768 | 0.086975 | 0.17395 | 0.16937 | 0.16937 | 0.17853 | -122.58 | -122.5662 | 0 | 0.096131 | -0.004577 | 0.091553
3443.9375 | 122.6486 | -0.064087 | 122.4747 | -0.0060272 | -0.0064877 | 0.00028845 | -0.014024 | 0.00064519 | -0.0091879 | -0.0027621 | -0.0082093 | 0.010062 | 0.001442 | -0.0092863 | -0.017355 | 0.02179 | -0.0027066 | -0.059509 | 0.013733 | -0.091553 | -0.013733 | 0.13733 | -0.036621 | 0.059509 | 0.09613 | 0.064087 | -0.064087 | 0.064087 | 0.2243 | 0.13733 | 0.15564 | -0.027466 | -122.4609 | -122.4884 | 0.20142 | 0.1236 | 0.027466 | 0.15106 | 0.054932 | 0 | -122.4106 | -122.4106 | 0.28839 | 0.21973 | 0.20142 | 0.21973 | 0.20142 | 0.22888 | 0.07782 | 0.28839 | 0.12817 | 0.10529 | 0.12817 | 0.07782 | 0.12817 | -122.5662 | -122.5388 | 0.050354 | 0.12817 | 0.004578 | 0.16022
3445.6875 | 122.5525 | -0.10529 | 122.5159 | -0.013657 | -0.0056333 | 7.4854e-05 | -0.012956 | 0.00085879 | -0.011538 | -0.0074619 | -0.0082093 | 0.011984 | 0.0044326 | -0.0024503 | -0.017355 | 0.015595 | -0.0054838 | -0.059509 | 0.054932 | -0.1236 | -0.064087 | 0.045776 | -0.10986 | -0.027466 | 0.036621 | 0.09613 | -0.068665 | -0.004578 | 0.11902 | 0.027466 | 0.091553 | -0.01831 | -122.4609 | -122.58 | 0.15106 | 0.07782 | -0.004577 | 0.09613 | 0.013733 | 0.036621 | -122.4197 | -122.5204 | 0.22431 | 0.19684 | 0.13275 | 0.16022 | 0.096131 | 0.16937 | 0.059509 | 0.18768 | 0.064087 | 0.17853 | 0.16479 | 0.16022 | 0.20142 | -122.6395 | -122.5845 | 0.041199 | 0.10071 | 0.045777 | 0.14191
3447.3906 | 122.5983 | -0.059509 | 122.4609 | -0.021286 | -0.0058469 | 0.00092925 | -0.014024 | -0.0012774 | -0.011965 | -0.0040439 | -0.0051575 | 0.010916 | 0.0012282 | -0.00095488 | -0.016714 | 0.020508 | -0.0020658 | -0.041199 | 0.018311 | -0.054932 | -0.018311 | 0.13275 | -0.068665 | 0.027466 | 0.10071 | 0.064087 | -0.050354 | 0.045776 | 0.16022 | 0.068665 | 0.10986 | 0.004577 | -122.4426 | -122.4792 | 0.19226 | 0.086975 | -0.009156 | 0.082398 | -0.013733 | 0.009155 | -122.3969 | -122.4152 | 0.21973 | 0.16937 | 0.12817 | 0.16022 | 0.11902 | 0.18768 | 0.036621 | 0.21057 | 0.09613 | 0.073243 | 0.11444 | 0.07782 | 0.1236 | -122.5159 | -122.5113 | 0.041198 | 0.10528 | 0.01831 | 0.16022
3449.1562 | 122.6395 | -0.091553 | 122.493 | -0.013657 | -0.0096921 | 0.0013565 | -0.014024 | -0.00085021 | -0.011751 | -0.0040439 | -0.0051575 | 0.0094208 | 0.0033646 | -0.00010048 | -0.020132 | 0.020508 | -0.0033474 | -0.036621 | 0.018311 | -0.082397 | 0.018311 | 0.15564 | 0 | 0.050354 | 0.11902 | 0.050354 | -0.054932 | 0.068665 | 0.21515 | 0.11902 | 0.12817 | 0.009156 | -122.4747 | -122.4747 | 0.24719 | 0.14191 | 0.091553 | 0.13275 | 0.082397 | 0.036621 | -122.4426 | -122.4243 | 0.3067 | 0.21973 | 0.21057 | 0.18311 | 0.17395 | 0.23804 | 0.10071 | 0.27008 | 0.1236 | 0.10071 | 0.10529 | 0.10986 | 0.14191 | -122.5754 | -122.5479 | 0.10986 | 0.16022 | 0.054932 | 0.21057
3450.8594 | 122.6212 | -0.064087 | 122.4655 | -0.0060272 | -0.0071285 | 0.0026383 | -0.01317 | 0.00064519 | -0.010043 | -0.0040439 | -0.0021057 | 0.010489 | 0.0020828 | 0.0018221 | -0.020559 | 0.022644 | -0.0020658 | -0.036621 | 0.032043 | -0.050354 | 0.009155 | 0.13275 | -0.059509 | 0.022888 | 0.10986 | 0.045776 | -0.036621 | 0.059509 | 0.18768 | 0.073242 | 0.12817 | 0.013733 | -122.4335 | -122.4564 | 0.19684 | 0.086975 | 0.004578 | 0.073242 | -0.009155 | 0.027466 | -122.4197 | -122.406 | 0.25177 | 0.19226 | 0.13733 | 0.1648 | 0.10986 | 0.18311 | 0.059509 | 0.2243 | 0.09613 | 0.082397 | 0.082397 | 0.09613 | 0.10986 | -122.5159 | -122.5021 | 0.073242 | 0.1236 | 0.027466 | 0.17395
3452.625 | 122.6074 | -0.086975 | 122.4747 | -0.013657 | -0.0037107 | 0.0026383 | -0.014024 | 0.0027814 | -0.010043 | -0.0040439 | -0.0051575 | 0.013052 | 0.0016556 | -0.0013821 | -0.019064 | 0.02179 | -0.0018522 | -0.07782 | 0.059509 | -0.09613 | -0.073242 | 0.041199 | -0.16022 | -0.054932 | 0.022888 | 0.073242 | -0.059509 | 0.027466 | 0.14191 | 0.054932 | 0.11444 | -0.009155 | -122.4152 | -122.5479 | 0.12817 | 0.032043 | -0.073242 | 0.041198 | -0.064087 | 0.027466 | -122.4014 | -122.4472 | 0.22888 | 0.20142 | 0.14191 | 0.17395 | 0.11444 | 0.13733 | 0.022888 | 0.20142 | 0.086975 | 0.15564 | 0.13275 | 0.14648 | 0.16022 | -122.5708 | -122.5342 | 0.013733 | 0.11444 | 0.009155 | 0.10986
3454.4062 | 122.6578 | -0.041199 | 122.4701 | -0.021286 | -0.0020017 | 0.00092925 | -0.012956 | 0.0053448 | -0.0085471 | -0.0046847 | -0.0021057 | 0.009848 | 0.0010146 | 0.00075412 | -0.016928 | 0.023926 | -0.00527 | -0.009155 | 0.018311 | -0.050354 | 0.013733 | 0.13733 | -0.054932 | 0.022888 | 0.1236 | 0.064087 | -0.059509 | 0.07782 | 0.19226 | 0.082397 | 0.15564 | -0.009155 | -122.4518 | -122.4564 | 0.17853 | 0.064087 | -0.013733 | 0.073242 | -0.004578 | -0.01831 | -122.406 | -122.3923 | 0.23346 | 0.19684 | 0.1236 | 0.21515 | 0.14191 | 0.18768 | 0.064087 | 0.25177 | 0.13733 | 0.068665 | 0.1236 | 0.05951 | 0.10529 | -122.5204 | -122.5296 | 0.054932 | 0.11902 | 0.032044 | 0.16479
3456.1875 | 122.5433 | -0.11902 | 122.5388 | -0.021286 | -0.0043515 | 0.00092925 | -0.014024 | -0.0012774 | -0.011111 | -0.0051121 | -0.0051575 | 0.013693 | 0.0018692 | -0.00052768 | -0.018209 | 0.020081 | 0.0007114 | -0.10071 | 0.059509 | -0.11902 | -0.13275 | -0.004578 | -0.15106 | -0.064087 | -0.054932 | 0.09613 | -0.086975 | -0.054932 | 0.059509 | -0.022888 | 0.050354 | 0 | -122.4792 | -122.6715 | 0.11444 | 0.054932 | -0.032043 | 0.054932 | -0.032043 | 0.032044 | -122.4426 | -122.5937 | 0.17853 | 0.16937 | 0.096131 | 0.13733 | 0.064087 | 0.11444 | -0.013732 | 0.14648 | 0.032043 | 0.17853 | 0.1831 | 0.17853 | 0.21515 | -122.6578 | -122.6257 | -0.013732 | 0.064087 | 0.018311 | 0.064087
3457.8906 | 122.6395 | -0.068665 | 122.4564 | -0.021286 | -0.0045651 | 0.0026383 | -0.014452 | 0.0014996 | -0.010256 | -0.0074619 | -0.0082093 | 0.011984 | 0.0022964 | -0.00074128 | -0.017141 | 0.02243 | 0.0002842 | -0.086975 | 0.018311 | -0.086975 | -0.036621 | 0.082397 | -0.10529 | -0.013733 | 0.07782 | 0.073242 | -0.064087 | 0.07782 | 0.17853 | 0.07782 | 0.14191 | -0.01831 | -122.438 | -122.493 | 0.15106 | 0.054932 | -0.036621 | 0.073242 | -0.018311 | 0.004578 | -122.3831 | -122.3785 | 0.24719 | 0.21057 | 0.14649 | 0.20599 | 0.14191 | 0.16937 | 0.050354 | 0.24261 | 0.14191 | 0.10529 | 0.13733 | 0.086976 | 0.14191 | -122.5433 | -122.5204 | 0.032044 | 0.14649 | -0.01831 | 0.14649
3459.6562 | 122.525 | -0.11444 | 122.4976 | -0.013657 | -0.0015743 | -0.0099655 | -0.011888 | 4.192e-06 | -0.013033 | -0.015793 | -0.0082093 | 0.012839 | 0.0029372 | 0.0048129 | -0.014791 | 0.019012 | 0.000925 | -0.07782 | 0.036621 | -0.10529 | -0.10986 | 0.004578 | -0.15564 | -0.086975 | -0.050354 | 0.09613 | -0.07782 | -0.054932 | 0.059509 | -0.050354 | 0.032043 | 0.009155 | -122.4609 | -122.6074 | 0.11902 | 0.027466 | -0.041199 | 0.018311 | -0.050354 | 0.036621 | -122.4014 | -122.5525 | 0.17395 | 0.14648 | 0.064087 | 0.10986 | 0.027466 | 0.10986 | -0.004577 | 0.13733 | 0.022888 | 0.14191 | 0.17395 | 0.15106 | 0.21057 | -122.6028 | -122.5754 | 0.004578 | 0.059509 | 0.036621 | 0.064087
3461.4219 | 122.5571 | -0.082397 | 122.5433 | -0.021286 | -0.0037107 | 0.0041337 | -0.011034 | 0.00085879 | -0.0081197 | -0.0083163 | -0.011261 | 0.012625 | 0.0040054 | -0.0035183 | -0.017141 | 0.018158 | -0.0063382 | -0.050354 | 0.054932 | -0.11444 | -0.068665 | 0.064087 | -0.10071 | -0.050354 | 0.045776 | 0.091553 | -0.086975 | 0.004578 | 0.13733 | 0.022888 | 0.082397 | -0.032044 | -122.4884 | -122.612 | 0.14648 | 0.032043 | -0.018311 | 0.064087 | 0.013733 | -0.004578 | -122.4518 | -122.5388 | 0.21973 | 0.16479 | 0.10528 | 0.16937 | 0.10986 | 0.17853 | 0.045776 | 0.2243 | 0.091553 | 0.16937 | 0.17853 | 0.13733 | 0.17395 | -122.6578 | -122.6303 | 0.013732 | 0.086975 | 0.032043 | 0.12817
3463.1875 | 122.6212 | -0.082397 | 122.5067 | -0.021286 | -0.0067013 | 0.00028845 | -0.01787 | -0.0034136 | -0.011538 | -0.0093845 | -0.0021057 | 0.0092072 | 0.0027236 | 0.0071627 | -0.017355 | 0.019653 | -0.0020658 | -0.050354 | 0.009155 | -0.082397 | 0.004578 | 0.14648 | -0.022888 | 0.036621 | 0.082397 | 0.068665 | -0.054932 | 0.013733 | 0.17853 | 0.086975 | 0.10986 | 0 | -122.4976 | -122.5021 | 0.22888 | 0.11902 | 0.059509 | 0.11902 | 0.059509 | 0.027465 | -122.438 | -122.493 | 0.26092 | 0.19226 | 0.16937 | 0.16479 | 0.14191 | 0.22888 | 0.086975 | 0.23346 | 0.068665 | 0.091552 | 0.1236 | 0.091552 | 0.15106 | -122.5891 | -122.5616 | 0.086975 | 0.09613 | 0.032043 | 0.16479
3464.9375 | 122.5708 | -0.09613 | 122.4838 | -0.0060272 | -0.010119 | 0.00050205 | -0.017015 | -0.0025592 | -0.011111 | -0.0036167 | -0.0082093 | 0.010916 | 0.0012282 | -0.00052768 | -0.016073 | 0.023285 | -0.0033474 | -0.050354 | 0.018311 | -0.086975 | -0.036621 | 0.10071 | -0.054932 | 0.018311 | 0.027466 | 0.082397 | -0.073242 | -0.027466 | 0.10986 | 0.018311 | 0.068665 | 0.009155 | -122.4655 | -122.5204 | 0.19684 | 0.11444 | 0.041198 | 0.10529 | 0.032043 | 0.022888 | -122.4014 | -122.5113 | 0.20599 | 0.16479 | 0.11444 | 0.14191 | 0.091553 | 0.18768 | 0.050354 | 0.18311 | 0.045776 | 0.10529 | 0.15564 | 0.11444 | 0.17853 | -122.5708 | -122.5571 | 0.059509 | 0.068664 | 0.045776 | 0.1236
3466.6406 | 122.5388 | -0.1236 | 122.5113 | -0.021286 | -0.0007199 | -0.0039841 | -0.010393 | -0.0032 | -0.01047 | -0.0072483 | -0.0051575 | 0.012625 | 0.0020828 | 0.0063083 | -0.01885 | 0.023712 | -0.002493 | -0.10071 | 0.064087 | -0.11444 | -0.13733 | -0.045776 | -0.21515 | -0.11444 | -0.082397 | 0.086975 | -0.10986 | -0.054932 | 0.041199 | -0.050354 | 0.041199 | 0.009155 | -122.4472 | -122.6486 | 0.07782 | 0.009155 | -0.091553 | 0 | -0.10071 | 0.013733 | -122.4243 | -122.5662 | 0.16479 | 0.16479 | 0.073242 | 0.15106 | 0.059509 | 0.068665 | -0.022888 | 0.15106 | 0.054931 | 0.17853 | 0.19684 | 0.18768 | 0.21057 | -122.6257 | -122.6212 | -0.013733 | 0.068664 | 0.022888 | 0.041199
3468.4062 | 122.6578 | -0.068665 | 122.5204 | -0.028916 | -0.0088375 | 0.0017837 | -0.016588 | -0.0032 | -0.012606 | -0.0076755 | -0.0051575 | 0.010489 | 0.0022964 | -0.0026639 | -0.018209 | 0.021362 | -0.0039884 | -0.022888 | 0.036621 | -0.07782 | 0.013733 | 0.16479 | -0.004578 | 0.050354 | 0.12817 | 0.050354 | -0.054932 | 0.054932 | 0.23346 | 0.13733 | 0.15106 | -0.009155 | -122.4838 | -122.5067 | 0.23346 | 0.11902 | 0.064087 | 0.12817 | 0.073242 | 0.013733 | -122.4701 | -122.4655 | 0.30212 | 0.21973 | 0.20599 | 0.20599 | 0.19226 | 0.24261 | 0.091553 | 0.28839 | 0.10986 | 0.11444 | 0.10529 | 0.10529 | 0.11902 | -122.5983 | -122.5754 | 0.082398 | 0.1236 | 0.045777 | 0.19684
3470.1094 | 122.4976 | -0.11902 | 122.5525 | -0.0060272 | -0.0024289 | -0.0080429 | -0.01317 | 0.0068402 | -0.014529 | -0.0074619 | -0.0051575 | 0.015189 | 0.0027236 | 0.0020359 | -0.019705 | 0.020721 | 0.003702 | -0.091553 | 0.064087 | -0.10529 | -0.10986 | -0.032043 | -0.17395 | -0.09613 | -0.086975 | 0.082397 | -0.07782 | -0.068665 | 0.022888 | -0.068665 | 0.018311 | 0.013733 | -122.4884 | -122.6624 | 0.086976 | 0.022889 | -0.054931 | 0.009156 | -0.068664 | 0.041199 | -122.4701 | -122.6212 | 0.14191 | 0.13733 | 0.050354 | 0.096131 | 0.009155 | 0.073243 | -0.004577 | 0.10071 | 0.009155 | 0.16937 | 0.16022 | 0.18311 | 0.20142 | -122.6578 | -122.6303 | 0.009156 | 0.050354 | 0.027466 | 0.032044
3471.8594 | 122.5296 | -0.11902 | 122.5433 | -0.0060272 | -0.0043515 | 0.0041337 | -0.012956 | 0.0014996 | -0.0096151 | -0.0055393 | -0.0021057 | 0.013266 | 0.0020828 | 0.0078037 | -0.017568 | 0.023071 | -0.0001432 | -0.10529 | 0.059509 | -0.11444 | -0.14191 | -0.036621 | -0.1831 | -0.10986 | -0.073242 | 0.091553 | -0.10071 | -0.041199 | 0.027466 | -0.064087 | 0.050354 | 0.004578 | -122.4838 | -122.6852 | 0.082398 | 0.009156 | -0.064086 | 0.004578 | -0.068664 | 0.018311 | -122.4518 | -122.5845 | 0.14649 | 0.16937 | 0.054932 | 0.15106 | 0.036621 | 0.07782 | -0.027466 | 0.12817 | 0.059509 | 0.17395 | 0.19226 | 0.17853 | 0.21057 | -122.6578 | -122.644 | -0.022888 | 0.07782 | 0.013733 | 0.045777
3473.6406 | 122.6212 | -0.07782 | 122.5113 | -0.013657 | -0.0056333 | 0.0017837 | -0.014452 | -0.0010638 | -0.0091879 | -0.0014805 | -0.0051575 | 0.0096344 | 0.0018692 | 0.0031039 | -0.0165 | 0.022003 | 0.0007114 | -0.050354 | -0.004578 | -0.068665 | -0.013733 | 0.13275 | -0.068665 | 0.018311 | 0.082397 | 0.027466 | -0.050354 | 0.032043 | 0.16022 | 0.050354 | 0.10529 | 0.009155 | -122.5159 | -122.525 | 0.21057 | 0.096131 | 0.009155 | 0.086976 | 0 | 0.027466 | -122.4838 | -122.4792 | 0.23804 | 0.18311 | 0.12817 | 0.15564 | 0.10071 | 0.20142 | 0.054932 | 0.21057 | 0.082397 | 0.064087 | 0.07782 | 0.073242 | 0.10529 | -122.58 | -122.5616 | 0.064087 | 0.10986 | 0.027466 | 0.16022
3475.3438 | 122.5754 | -0.10529 | 122.5708 | -0.0060272 | -0.0043515 | 0.0013565 | -0.013597 | 0.0017132 | -0.010683 | -0.0040439 | -0.0082093 | 0.012839 | 0.0012282 | -0.0013821 | -0.017782 | 0.02243 | -0.002493 | -0.091553 | 0.041199 | -0.11444 | -0.07782 | -0.004578 | -0.12817 | -0.059509 | -0.032043 | 0.10071 | -0.091553 | -0.013733 | 0.10071 | 0.004578 | 0.082397 | -0.009155 | -122.5296 | -122.6486 | 0.10071 | 0.045777 | -0.022888 | 0.054932 | -0.013733 | 0.013733 | -122.4701 | -122.5845 | 0.20599 | 0.18768 | 0.10986 | 0.17395 | 0.096131 | 0.10986 | 0.036621 | 0.19226 | 0.07782 | 0.15564 | 0.19226 | 0.14649 | 0.20599 | -122.6852 | -122.6624 | 0.027466 | 0.091553 | 0.013733 | 0.073243
3477.0469 | 122.5891 | -0.086975 | 122.5388 | -0.013657 | -0.0071285 | 0.0011429 | -0.011888 | 0.0038494 | -0.011538 | -0.0046847 | -0.0051575 | 0.013907 | 0.0022964 | 0.0020359 | -0.015432 | 0.018372 | -0.0005704 | -0.045776 | 0.041199 | -0.10986 | -0.050354 | 0.064087 | -0.09613 | -0.032043 | 0.045776 | 0.086975 | -0.07782 | 0 | 0.1236 | 0.013733 | 0.082397 | -0.022888 | -122.4976 | -122.5891 | 0.15106 | 0.054932 | -0.009155 | 0.07782 | 0.013733 | 0.009155 | -122.4518 | -122.5388 | 0.21057 | 0.16937 | 0.10071 | 0.16022 | 0.091553 | 0.17395 | 0.059509 | 0.20142 | 0.07782 | 0.15106 | 0.16479 | 0.12817 | 0.17395 | -122.6486 | -122.6166 | 0.036621 | 0.086975 | 0.041199 | 0.13275
3478.8125 | 122.6578 | -0.073242 | 122.4838 | -0.0060272 | -0.0039243 | 0.0024247 | -0.015306 | 0.00085879 | -0.0087607 | -0.0055393 | -0.0021057 | 0.012198 | 0.0020828 | 0.00011332 | -0.016287 | 0.020508 | -0.003561 | -0.018311 | -0.004578 | -0.064087 | -0.004578 | 0.13733 | -0.054932 | 0.022888 | 0.1236 | 0.032043 | -0.045776 | 0.064087 | 0.19226 | 0.07782 | 0.13733 | 0.009155 | -122.4884 | -122.4884 | 0.21057 | 0.09613 | 0.01831 | 0.086975 | 0.009155 | 0.027466 | -122.4518 | -122.4197 | 0.2655 | 0.21057 | 0.15106 | 0.18311 | 0.1236 | 0.20142 | 0.059509 | 0.23804 | 0.10986 | 0.059509 | 0.077819 | 0.068664 | 0.10529 | -122.5479 | -122.5296 | 0.068664 | 0.13733 | 0.054931 | 0.19684
3480.5781 | 122.6303 | -0.073242 | 122.5159 | -0.0060272 | -0.0043515 | 0.0030655 | -0.016801 | 0.00043159 | -0.0091879 | -0.0051121 | -0.0082093 | 0.012198 | -0.00069437 | 0.0020359 | -0.018637 | 0.020508 | -0.0033474 | -0.041199 | 0.013733 | -0.073242 | -0.022888 | 0.11902 | -0.068665 | 0.022888 | 0.082397 | 0.059509 | -0.045776 | 0.032043 | 0.15106 | 0.054932 | 0.10529 | 0 | -122.5021 | -122.5388 | 0.19226 | 0.09613 | 0.004577 | 0.09613 | 0.004577 | 0.027466 | -122.4564 | -122.4838 | 0.2243 | 0.17853 | 0.12817 | 0.15106 | 0.10071 | 0.19226 | 0.050354 | 0.19684 | 0.077819 | 0.086975 | 0.10528 | 0.086975 | 0.13275 | -122.5891 | -122.5616 | 0.050354 | 0.10529 | 0.032043 | 0.15564
3482.2812 | 122.5754 | -0.10986 | 122.5571 | 0.0016023 | -0.0094785 | 0.0019975 | -0.016588 | 0.0010724 | -0.011538 | -0.0025485 | -0.0082093 | 0.010275 | 0.0010146 | -0.0028775 | -0.017141 | 0.023071 | -0.0061246 | -0.050354 | 0.036621 | -0.07782 | -0.013733 | 0.10529 | -0.050354 | 0.018311 | 0.045776 | 0.064087 | -0.050354 | -0.018311 | 0.10986 | 0.013733 | 0.059509 | 0.032043 | -122.5204 | -122.5708 | 0.21515 | 0.12817 | 0.059509 | 0.096131 | 0.027466 | 0.059509 | -122.493 | -122.5754 | 0.21973 | 0.16937 | 0.1236 | 0.10986 | 0.064087 | 0.18311 | 0.064087 | 0.16022 | 0.032043 | 0.11444 | 0.11444 | 0.14648 | 0.17395 | -122.6349 | -122.6074 | 0.09613 | 0.091552 | 0.059509 | 0.15564
3484.0625 | 122.6349 | -0.07782 | 122.5525 | -0.0060272 | -0.0047787 | 0.0028519 | -0.014665 | 0.0014996 | -0.011324 | -0.0031895 | -0.0082093 | 0.011343 | 0.001442 | -0.0024503 | -0.017568 | 0.019867 | -0.0005704 | -0.086975 | 0.022888 | -0.07782 | -0.045776 | 0.073242 | -0.09613 | 0 | 0.022888 | 0.059509 | -0.068665 | 0.004578 | 0.13275 | 0.032043 | 0.091553 | 0 | -122.5296 | -122.5983 | 0.15106 | 0.07782 | -0.01831 | 0.07782 | -0.01831 | 0.009155 | -122.493 | -122.5479 | 0.21057 | 0.16937 | 0.10986 | 0.16022 | 0.10071 | 0.15106 | 0.032044 | 0.20142 | 0.073243 | 0.10071 | 0.12817 | 0.10071 | 0.13733 | -122.6303 | -122.6212 | 0.032044 | 0.082398 | -0.009155 | 0.10071
3485.8281 | 122.6028 | -0.086975 | 122.5571 | -0.013657 | -0.0060605 | 0.0026383 | -0.012743 | -0.0070452 | -0.011324 | -0.0029759 | -0.011261 | 0.012411 | 0.0027236 | 0.0020359 | -0.016714 | 0.015167 | -0.0046292 | -0.064087 | 0.045776 | -0.10071 | -0.054932 | 0.054932 | -0.10529 | -0.036621 | 0.045776 | 0.091553 | -0.068665 | 0.018311 | 0.1236 | 0.018311 | 0.086975 | -0.013733 | -122.5113 | -122.612 | 0.14191 | 0.050354 | -0.018311 | 0.064087 | -0.004578 | 0.01831 | -122.4655 | -122.5388 | 0.21057 | 0.17395 | 0.10529 | 0.15564 | 0.086976 | 0.15564 | 0.045776 | 0.19226 | 0.086976 | 0.14648 | 0.16022 | 0.13275 | 0.17853 | -122.6578 | -122.6257 | 0.032043 | 0.10529 | 0.022888 | 0.13275
3487.5938 | 122.5616 | -0.10529 | 122.5433 | -0.013657 | -0.0028561 | -0.0091109 | -0.012102 | 0.0019268 | -0.011324 | -0.0036167 | -0.0082093 | 0.01412 | 0.0044326 | -0.00010048 | -0.017568 | 0.023071 | 0.0028476 | -0.10529 | 0.054932 | -0.10529 | -0.1236 | -0.045776 | -0.20599 | -0.10071 | -0.050354 | 0.09613 | -0.091553 | -0.054932 | 0.036621 | -0.064087 | 0.054932 | 0 | -122.4884 | -122.6669 | 0.05951 | 0.004578 | -0.10071 | 0.004578 | -0.10071 | 0.013733 | -122.4472 | -122.5983 | 0.14191 | 0.16022 | 0.041199 | 0.14649 | 0.027466 | 0.05951 | -0.01831 | 0.12817 | 0.036621 | 0.16022 | 0.18768 | 0.16022 | 0.20142 | -122.6486 | -122.6349 | -0.01831 | 0.050354 | 0 | 0.054932
3489.2969 | 122.6303 | -0.091553 | 122.5479 | -0.0060272 | -0.0064877 | 0.0011429 | -0.017229 | 0.00021799 | -0.012179 | -0.0055393 | -0.0082093 | 0.009848 | 0.0027236 | 0.0018221 | -0.01885 | 0.021149 | 0.000925 | -0.09613 | 0.009155 | -0.073242 | -0.059509 | 0.064087 | -0.086975 | -0.009155 | 0.022888 | 0.050354 | -0.068665 | 0.004578 | 0.1236 | 0.027466 | 0.10071 | 0.018311 | -122.5388 | -122.6074 | 0.15564 | 0.082398 | 0.004578 | 0.064087 | -0.013733 | 0.022888 | -122.4976 | -122.5433 | 0.21515 | 0.19226 | 0.11902 | 0.16937 | 0.096131 | 0.13733 | 0.013733 | 0.19226 | 0.073243 | 0.082397 | 0.11902 | 0.10071 | 0.14191 | -122.6212 | -122.6166 | 0.032044 | 0.096131 | -0.004577 | 0.11444
3491.0625 | 122.5845 | -0.10529 | 122.5708 | -0.013657 | -0.0075559 | 0.0015701 | -0.014665 | 0.0038494 | -0.012179 | -0.0040439 | -0.0082093 | 0.012411 | 0.0037918 | 0.0052401 | -0.017782 | 0.023712 | -0.0012112 | -0.10529 | 0.054932 | -0.10986 | -0.10986 | 0.004578 | -0.12817 | -0.050354 | -0.032043 | 0.082397 | -0.086975 | -0.050354 | 0.091553 | -0.009155 | 0.054932 | -0.004577 | -122.5159 | -122.6807 | 0.10986 | 0.054932 | -0.022888 | 0.059509 | -0.018311 | 0.018311 | -122.4884 | -122.6212 | 0.19684 | 0.16022 | 0.096131 | 0.14191 | 0.07782 | 0.11444 | 0 | 0.17853 | 0.036621 | 0.16479 | 0.16937 | 0.16022 | 0.18768 | -122.6807 | -122.6578 | -0.004577 | 0.054932 | 0 | 0.073243
3492.8125 | 122.5754 | -0.10071 | 122.5525 | -0.0060272 | -0.0030697 | -0.0041977 | -0.012529 | 0.0066266 | -0.010043 | -0.0036167 | -0.0082093 | 0.015402 | 0.0050736 | 0.0084445 | -0.017355 | 0.021576 | -0.0003568 | -0.086975 | 0.073242 | -0.12817 | -0.13733 | -0.027466 | -0.17853 | -0.086975 | -0.059509 | 0.09613 | -0.09613 | -0.045776 | 0.036621 | -0.059509 | 0.041199 | -0.027466 | -122.4792 | -122.6898 | 0.073242 | 0.013733 | -0.07782 | 0.041199 | -0.050354 | 0.004578 | -122.4564 | -122.5983 | 0.13733 | 0.14191 | 0.041199 | 0.13733 | 0.036621 | 0.10071 | -0.009155 | 0.13275 | 0.050354 | 0.20142 | 0.19226 | 0.17395 | 0.19684 | -122.6807 | -122.6486 | -0.036621 | 0.054932 | 0.013733 | 0.041199
3494.5781 | 122.5616 | -0.11902 | 122.5571 | -0.0060272 | -0.0088375 | 0.00050205 | -0.011461 | 0.00021799 | -0.011538 | -0.0023349 | 0.0009461 | 0.012198 | 0.0020828 | -0.0035183 | -0.016073 | 0.02179 | -0.0039884 | -0.11902 | 0.054932 | -0.12817 | -0.13275 | -0.009155 | -0.14191 | -0.059509 | -0.068665 | 0.10071 | -0.091553 | -0.054932 | 0.082397 | -0.018311 | 0.050354 | -0.009155 | -122.5021 | -122.6898 | 0.10986 | 0.05951 | -0.022888 | 0.068665 | -0.013733 | 0.027466 | -122.4564 | -122.612 | 0.20142 | 0.16937 | 0.10071 | 0.14191 | 0.073242 | 0.11902 | -0.004577 | 0.17395 | 0.036621 | 0.18311 | 0.19226 | 0.17395 | 0.21973 | -122.6852 | -122.6486 | -0.013732 | 0.064087 | 0 | 0.050354
3496.2812 | 122.6532 | -0.073242 | 122.5388 | -0.013657 | -0.0024289 | 0.0019975 | -0.01552 | 0.0021406 | -0.0098287 | -0.0063937 | -0.0051575 | 0.01113 | 0.00251 | 0.0056675 | -0.020132 | 0.023071 | -0.0003568 | -0.082397 | 0.032043 | -0.09613 | -0.082397 | 0.041199 | -0.13733 | -0.036621 | 0.032043 | 0.07782 | -0.064087 | 0.045776 | 0.14648 | 0.041199 | 0.1236 | -0.022888 | -122.5067 | -122.6212 | 0.11444 | 0.036621 | -0.064087 | 0.059509 | -0.041199 | 0.009155 | -122.4609 | -122.493 | 0.21973 | 0.19684 | 0.11444 | 0.18768 | 0.10529 | 0.13733 | 0.013733 | 0.21057 | 0.10986 | 0.12817 | 0.14191 | 0.10529 | 0.15106 | -122.6349 | -122.6028 | -0.009155 | 0.11902 | -0.009155 | 0.10529
3498.0469 | 122.6395 | -0.068665 | 122.5342 | -0.013657 | -0.0056333 | 0.0013565 | -0.014665 | -0.00063661 | -0.0096151 | -0.0046847 | -0.0021057 | 0.010489 | 0.0020828 | -0.00074128 | -0.019918 | 0.022003 | -0.0048428 | -0.050354 | 0.022888 | -0.082397 | -0.032043 | 0.10529 | -0.086975 | 0.013733 | 0.07782 | 0.050354 | -0.059509 | 0.013733 | 0.14191 | 0.054932 | 0.09613 | -0.013732 | -122.5113 | -122.5662 | 0.17395 | 0.082398 | -0.01831 | 0.09613 | -0.004578 | 0.009156 | -122.4838 | -122.5204 | 0.21057 | 0.16479 | 0.1236 | 0.15564 | 0.11444 | 0.18768 | 0.050354 | 0.20142 | 0.073242 | 0.10528 | 0.10986 | 0.091553 | 0.11902 | -122.6166 | -122.5937 | 0.036622 | 0.082398 | 0.018311 | 0.14649
3499.8281 | 122.5662 | -0.10071 | 122.5754 | -0.0060272 | -0.0015743 | -0.015093 | -0.012956 | 0.0025678 | -0.020937 | -0.011734 | -0.0051575 | 0.014761 | 0.0027236 | 0.00032692 | -0.017141 | 0.022003 | -0.0012112 | -0.054932 | 0.045776 | -0.11444 | -0.082397 | 0.032043 | -0.15564 | -0.073242 | 0 | 0.073242 | -0.082397 | -0.036621 | 0.050354 | -0.045776 | 0.045776 | -0.013733 | -122.5296 | -122.6578 | 0.13275 | 0.027466 | -0.054932 | 0.041199 | -0.041199 | 0.018311 | -122.5021 | -122.612 | 0.15106 | 0.14648 | 0.054932 | 0.12817 | 0.036621 | 0.14648 | 0.032044 | 0.13275 | 0.045776 | 0.16022 | 0.15564 | 0.14648 | 0.17395 | -122.6898 | -122.6578 | 0.018311 | 0.064087 | 0.045776 | 0.10071
3501.5312 | 122.699 | -0.086975 | 122.5388 | -0.0060272 | -0.0090513 | 0.0024247 | -0.016161 | -0.0010638 | -0.011111 | -0.0059665 | -0.0082093 | 0.011557 | 0.00080103 | -0.0041593 | -0.016073 | 0.022003 | 0.0011386 | -0.054932 | 0.004578 | -0.082397 | -0.004578 | 0.12817 | -0.032043 | 0.022888 | 0.091553 | 0.050354 | -0.064087 | 0.059509 | 0.18768 | 0.1236 | 0.13733 | 0.004578 | -122.5342 | -122.5433 | 0.21515 | 0.10986 | 0.054932 | 0.10528 | 0.050354 | 0.022888 | -122.4884 | -122.4792 | 0.27466 | 0.2243 | 0.21057 | 0.20142 | 0.18768 | 0.21057 | 0.077819 | 0.25177 | 0.1236 | 0.086975 | 0.11444 | 0.091553 | 0.13733 | -122.6212 | -122.6028 | 0.082397 | 0.14648 | 0.032043 | 0.17853
3503.2344 | 122.6395 | -0.068665 | 122.5525 | -0.028916 | -0.0073423 | 0.0028519 | -0.016801 | 0.0027814 | -0.011324 | -0.0034031 | -0.0082093 | 0.010702 | 0.0027236 | 0.0041721 | -0.018209 | 0.019012 | 7.04e-05 | -0.059509 | 0.022888 | -0.073242 | -0.050354 | 0.10529 | -0.082397 | 0.013733 | 0.041199 | 0.068665 | -0.07782 | 0.009155 | 0.13733 | 0.036621 | 0.10529 | -0.004577 | -122.5296 | -122.6028 | 0.17395 | 0.082398 | -0.013732 | 0.086975 | -0.009155 | -0.009155 | -122.4838 | -122.5433 | 0.20599 | 0.17395 | 0.10529 | 0.18311 | 0.11444 | 0.17853 | 0.022888 | 0.21515 | 0.086975 | 0.09613 | 0.14649 | 0.091553 | 0.13733 | -122.6257 | -122.6303 | 0.018311 | 0.07782 | 0.009156 | 0.10986
3505 | 122.6944 | -0.059509 | 122.5525 | -0.0060272 | -0.0028561 | 0.0019975 | -0.0099656 | 0.00021799 | -0.011111 | -0.0031895 | -0.011261 | 0.010702 | 0.00058743 | 0.0067355 | -0.019277 | 0.022003 | 7.04e-05 | -0.009155 | 0.027466 | -0.064087 | 0 | 0.10986 | -0.050354 | 0.022888 | 0.10529 | 0.050354 | -0.041199 | 0.091553 | 0.19226 | 0.086975 | 0.14191 | -0.004578 | -122.525 | -122.5525 | 0.16937 | 0.082397 | 0.009155 | 0.086975 | 0.013733 | 0.01831 | -122.5021 | -122.4609 | 0.25177 | 0.20142 | 0.14648 | 0.18311 | 0.12817 | 0.17395 | 0.064087 | 0.23346 | 0.13275 | 0.091553 | 0.091553 | 0.086975 | 0.10986 | -122.6166 | -122.5937 | 0.059509 | 0.15106 | 0.050354 | 0.16479
3506.7031 | 122.7036 | -0.073242 | 122.5479 | 0.0016023 | -0.0077695 | 0.0019975 | -0.016588 | 0.00064519 | -0.011324 | -0.0019077 | -0.0082093 | 0.011771 | 0.0018692 | 0.0048129 | -0.01885 | 0.020721 | -0.0050564 | -0.027466 | 0.022888 | -0.068665 | 0.036621 | 0.1831 | 0 | 0.045776 | 0.13275 | 0.041199 | -0.045776 | 0.073242 | 0.22888 | 0.11902 | 0.13733 | 0.004577 | -122.525 | -122.5113 | 0.25635 | 0.11902 | 0.073242 | 0.11444 | 0.068665 | 0.027466 | -122.5067 | -122.4747 | 0.30212 | 0.21057 | 0.19226 | 0.18311 | 0.16479 | 0.25177 | 0.10529 | 0.27466 | 0.11902 | 0.091553 | 0.086975 | 0.09613 | 0.11444 | -122.6166 | -122.5937 | 0.10986 | 0.14648 | 0.045776 | 0.20599
3508.4688 | 122.5983 | -0.10071 | 122.5891 | -0.013657 | -0.0056333 | -0.0012069 | -0.014452 | 0.0025678 | -0.011538 | -0.0048985 | -0.0051575 | 0.012625 | 0.0022964 | 0.0056675 | -0.01885 | 0.024353 | -0.0005704 | -0.09613 | 0.050354 | -0.10529 | -0.11444 | -0.009155 | -0.13275 | -0.054932 | -0.064087 | 0.091553 | -0.10071 | -0.045776 | 0.082397 | -0.022888 | 0.054932 | -0.004578 | -122.5388 | -122.7036 | 0.091553 | 0.045776 | -0.032043 | 0.050354 | -0.027465 | 0 | -122.4976 | -122.6349 | 0.18311 | 0.15564 | 0.07782 | 0.15564 | 0.07782 | 0.096131 | -0.009155 | 0.18311 | 0.054932 | 0.15564 | 0.19226 | 0.15106 | 0.19226 | -122.6944 | -122.6898 | -0.013733 | 0.054932 | 0.004578 | 0.036621
3510.1719 | 122.6807 | -0.059509 | 122.5571 | -0.013657 | -0.0062741 | 0.0022111 | -0.014452 | -0.001491 | -0.011538 | -0.0057529 | -0.0051575 | 0.0094208 | 0.0020828 | 0.0011813 | -0.017141 | 0.023285 | -0.0003568 | -0.041199 | 0.004578 | -0.086975 | 0.018311 | 0.16479 | -0.004578 | 0.050354 | 0.11444 | 0.059509 | -0.045776 | 0.059509 | 0.19684 | 0.10071 | 0.13733 | -0.027466 | -122.5525 | -122.5388 | 0.2243 | 0.10986 | 0.054931 | 0.13733 | 0.082397 | 0.013733 | -122.4976 | -122.4976 | 0.25635 | 0.19684 | 0.16022 | 0.18311 | 0.14648 | 0.25177 | 0.10529 | 0.24261 | 0.10528 | 0.091553 | 0.10528 | 0.064087 | 0.11902 | -122.644 | -122.6028 | 0.07782 | 0.11902 | 0.01831 | 0.17395
3511.9375 | 122.6166 | -0.082397 | 122.5616 | -0.0060272 | -0.0090513 | 0.0015701 | -0.014879 | -0.0019184 | -0.013033 | -0.0029759 | -0.0051575 | 0.012198 | 0.0029372 | -0.00010048 | -0.017355 | 0.02243 | -0.0044156 | -0.032043 | 0.022888 | -0.064087 | -0.009155 | 0.11444 | -0.045776 | 0.013733 | 0.050354 | 0.059509 | -0.068665 | -0.018311 | 0.14648 | 0.036621 | 0.064087 | 0.01831 | -122.5388 | -122.5708 | 0.19684 | 0.09613 | 0.036621 | 0.07782 | 0.018311 | 0.013732 | -122.5021 | -122.58 | 0.22888 | 0.14648 | 0.11902 | 0.13275 | 0.10529 | 0.17853 | 0.054932 | 0.21515 | 0.050354 | 0.086975 | 0.12817 | 0.10528 | 0.14191 | -122.6257 | -122.6303 | 0.073242 | 0.064086 | 0.050354 | 0.13275
3513.6562 | 122.58 | -0.13275 | 122.5708 | -0.013657 | -0.0067013 | 0.00050205 | -0.014024 | 0.001286 | -0.011324 | -0.0046847 | -0.0082093 | 0.01113 | 0.0037918 | -0.013986 | -0.017355 | 0.02179 | -0.002493 | -0.10529 | 0.054932 | -0.11444 | -0.10986 | 0.022888 | -0.12817 | -0.059509 | -0.045776 | 0.10071 | -0.10986 | -0.059509 | 0.059509 | -0.032043 | 0.022888 | 0.01831 | -122.5159 | -122.6807 | 0.15564 | 0.073242 | 0.004577 | 0.054932 | -0.013733 | 0.022888 | -122.4701 | -122.6303 | 0.19226 | 0.15564 | 0.10071 | 0.13275 | 0.07782 | 0.13733 | 0.004578 | 0.16937 | 0.050354 | 0.16937 | 0.21057 | 0.18768 | 0.23346 | -122.6852 | -122.6807 | 0.022888 | 0.073242 | 0.027465 | 0.086975
3515.4219 | 122.6532 | -0.086975 | 122.5342 | -0.021286 | -0.0045651 | 0.00092925 | -0.016374 | -0.0032 | -0.011324 | -0.0085299 | -0.0021057 | 0.0092072 | 0.0037918 | 0.0037447 | -0.018209 | 0.02179 | -0.0014248 | -0.07782 | 0.027466 | -0.073242 | -0.036621 | 0.091553 | -0.091553 | 0 | 0.041199 | 0.064087 | -0.073242 | 0.022888 | 0.14191 | 0.045776 | 0.091553 | 0.013733 | -122.5067 | -122.5708 | 0.17853 | 0.086975 | -0.004578 | 0.073242 | -0.018311 | 0.013733 | -122.4701 | -122.5113 | 0.22888 | 0.17853 | 0.13275 | 0.16479 | 0.11902 | 0.16479 | 0.036621 | 0.21515 | 0.09613 | 0.10071 | 0.13733 | 0.11444 | 0.15106 | -122.6074 | -122.6074 | 0.050354 | 0.10986 | 0.009155 | 0.12817
3517.1719 | 122.6898 | -0.068665 | 122.5479 | -0.028916 | -0.0062741 | 0.00092925 | -0.016588 | -0.0023456 | -0.01047 | -0.0059665 | -0.0082093 | 0.010916 | 0.001442 | -0.0035183 | -0.018637 | 0.020721 | 7.04e-05 | -0.068665 | 0.027466 | -0.082397 | -0.041199 | 0.082397 | -0.059509 | 0.018311 | 0.050354 | 0.050354 | -0.068665 | 0.041199 | 0.17395 | 0.10071 | 0.12817 | -0.013732 | -122.5204 | -122.5891 | 0.15106 | 0.086976 | 0.009156 | 0.10071 | 0.022888 | 0 | -122.4976 | -122.5067 | 0.24261 | 0.19684 | 0.16937 | 0.19684 | 0.16937 | 0.16479 | 0.041198 | 0.24261 | 0.10986 | 0.10986 | 0.11902 | 0.096131 | 0.11902 | -122.6303 | -122.6166 | 0.027466 | 0.10986 | 0 | 0.11902
3518.875 | 122.6761 | -0.091553 | 122.5433 | -0.0060272 | -0.0030697 | 0.00050205 | -0.013811 | 0.0040632 | -0.011324 | -0.0098117 | -0.0082093 | 0.01348 | 0.0022964 | 0.00096772 | -0.017996 | 0.021362 | -0.0029202 | -0.073242 | 0.027466 | -0.073242 | -0.045776 | 0.064087 | -0.091553 | -0.013733 | 0.018311 | 0.07782 | -0.086975 | 0 | 0.14191 | 0.045776 | 0.10071 | 0.018311 | -122.5159 | -122.5891 | 0.15564 | 0.07782 | 0 | 0.059509 | -0.018311 | 0.004578 | -122.4655 | -122.5433 | 0.23346 | 0.19226 | 0.13733 | 0.18768 | 0.13275 | 0.13733 | 0.027466 | 0.22888 | 0.086975 | 0.10071 | 0.16479 | 0.11902 | 0.16937 | -122.6166 | -122.6303 | 0.045777 | 0.091553 | 0.018311 | 0.10986
3520.625 | 122.5708 | -0.10529 | 122.612 | 0.0016023 | -0.0060605 | -0.00099335 | -0.015093 | -0.00042301 | -0.010897 | -0.0044711 | -0.0082093 | 0.013052 | 0.0029372 | -0.0030911 | -0.019491 | 0.023712 | -0.0054838 | -0.1236 | 0.050354 | -0.11444 | -0.10986 | 0.009155 | -0.14648 | -0.059509 | -0.041199 | 0.09613 | -0.09613 | -0.050354 | 0.059509 | -0.022888 | 0.032043 | -0.009155 | -122.5616 | -122.7219 | 0.11444 | 0.045777 | -0.041198 | 0.054932 | -0.032043 | 0.009156 | -122.5159 | -122.6624 | 0.16479 | 0.13733 | 0.082398 | 0.12817 | 0.073242 | 0.1236 | 0.004578 | 0.15564 | 0.045776 | 0.16479 | 0.19226 | 0.15564 | 0.20142 | -122.7264 | -122.7081 | -0.004577 | 0.054932 | -0.01831 | 0.064087
3522.3906 | 122.6303 | -0.10071 | 122.58 | 0.0016023 | -0.0049923 | 0.0013565 | -0.014665 | -0.00063661 | -0.012392 | -0.0074619 | -0.0051575 | 0.012411 | 0.0029372 | 0.0035311 | -0.017996 | 0.018372 | -0.0046292 | -0.054932 | 0.064087 | -0.11902 | -0.068665 | 0.036621 | -0.1236 | -0.050354 | 0.013733 | 0.09613 | -0.068665 | -0.004578 | 0.11444 | 0.009155 | 0.091553 | -0.018311 | -122.5159 | -122.6486 | 0.13733 | 0.050354 | -0.022888 | 0.068665 | -0.004577 | 0.032043 | -122.4838 | -122.5845 | 0.21515 | 0.19226 | 0.10986 | 0.16022 | 0.07782 | 0.15564 | 0.050354 | 0.18311 | 0.064087 | 0.18311 | 0.16479 | 0.1648 | 0.19684 | -122.699 | -122.6486 | 0.032043 | 0.09613 | 0.045776 | 0.11444
3524.0938 | 122.5937 | -0.10071 | 122.5937 | -0.0060272 | -0.0058469 | -0.00099335 | -0.013597 | 0.00043159 | -0.011324 | -0.0044711 | -0.0051575 | 0.012198 | 0.0027236 | -0.0020231 | -0.0165 | 0.021576 | -0.0054838 | -0.10071 | 0.045776 | -0.11902 | -0.10986 | -0.009155 | -0.14648 | -0.059509 | -0.050354 | 0.09613 | -0.082397 | -0.07782 | 0.073242 | -0.009155 | 0.050354 | -0.018311 | -122.5479 | -122.7036 | 0.091553 | 0.041199 | -0.045776 | 0.05951 | -0.027465 | 0.018311 | -122.4976 | -122.6715 | 0.17395 | 0.15106 | 0.091553 | 0.13275 | 0.073242 | 0.10986 | 0.009156 | 0.15564 | 0.004577 | 0.16479 | 0.17853 | 0.14648 | 0.19684 | -122.7127 | -122.6761 | -0.009155 | 0.022888 | 0 | 0.050354
3525.8438 | 122.644 | -0.09613 | 122.5891 | -0.013657 | -0.0062741 | 0.0017837 | -0.013384 | -0.0010638 | -0.010683 | -0.0040439 | -0.0051575 | 0.012625 | 0.0046462 | -0.00052768 | -0.017141 | 0.018799 | 0.0007114 | -0.050354 | 0.054932 | -0.10071 | -0.064087 | 0.068665 | -0.11444 | -0.027466 | 0.041199 | 0.091553 | -0.073242 | 0.013733 | 0.13275 | 0.022888 | 0.086975 | -0.004578 | -122.5342 | -122.6532 | 0.16479 | 0.068664 | -0.018311 | 0.073242 | -0.013733 | 0.022888 | -122.4976 | -122.5754 | 0.22888 | 0.1831 | 0.11902 | 0.16022 | 0.09613 | 0.16937 | 0.036621 | 0.20599 | 0.086975 | 0.15564 | 0.16479 | 0.15106 | 0.18768 | -122.6898 | -122.6624 | 0.032043 | 0.10986 | 0.045776 | 0.13733
3527.6094 | 122.7127 | -0.07782 | 122.5754 | -0.0060272 | -0.0041379 | 0.0019975 | -0.014238 | -0.0032 | -0.0094015 | -0.0053257 | -0.0082093 | 0.01113 | 0.004219 | -0.0067227 | -0.016928 | 0.022858 | 0.000925 | -0.050354 | 0.036621 | -0.091553 | -0.032043 | 0.09613 | -0.07782 | 0.018311 | 0.09613 | 0.036621 | -0.064087 | 0.068665 | 0.20142 | 0.07782 | 0.14191 | -0.013733 | -122.5388 | -122.6074 | 0.17395 | 0.096131 | 0 | 0.10986 | 0.013733 | 0.013733 | -122.5388 | -122.5067 | 0.27924 | 0.21973 | 0.15564 | 0.20599 | 0.14191 | 0.18768 | 0.05951 | 0.2655 | 0.13275 | 0.12817 | 0.10071 | 0.11444 | 0.11444 | -122.6669 | -122.6395 | 0.045777 | 0.14649 | 0.027466 | 0.17395
3529.3281 | 122.6074 | -0.091553 | 122.6074 | -0.013657 | -0.0049923 | -0.014879 | -0.011888 | -0.008327 | -0.02521 | -0.014511 | -0.0082093 | 0.012625 | 0.0022964 | 0.0026767 | -0.017568 | 0.016449 | 0.0011386 | -0.050354 | 0.045776 | -0.10986 | -0.064087 | 0.036621 | -0.1236 | -0.045776 | 0.022888 | 0.068665 | -0.082397 | -0.027466 | 0.086975 | -0.009155 | 0.064087 | -0.01831 | -122.5616 | -122.6715 | 0.12817 | 0.045777 | -0.032043 | 0.064087 | -0.013733 | 0.009156 | -122.5388 | -122.6349 | 0.17853 | 0.15564 | 0.082398 | 0.14648 | 0.073242 | 0.14648 | 0.045776 | 0.16937 | 0.054931 | 0.15564 | 0.15106 | 0.13733 | 0.16022 | -122.7173 | -122.6898 | 0.027466 | 0.064087 | 0.041199 | 0.11444
3531.0938 | 122.5937 | -0.1236 | 122.5983 | -0.0060272 | -0.0077695 | -0.00035255 | -0.015733 | -0.00020941 | -0.011965 | -0.0074619 | -0.0021057 | 0.011557 | 0.0044326 | 0.0026767 | -0.017141 | 0.020935 | -0.0005704 | -0.11444 | 0.045776 | -0.1236 | -0.11902 | 0.018311 | -0.13275 | -0.050354 | -0.050354 | 0.091553 | -0.082397 | -0.073242 | 0.068665 | -0.018311 | 0.032043 | 0 | -122.5525 | -122.7173 | 0.14191 | 0.073242 | -0.009155 | 0.073242 | -0.009155 | 0.041199 | -122.5067 | -122.6715 | 0.19226 | 0.15564 | 0.10528 | 0.11444 | 0.064086 | 0.14191 | 0.004577 | 0.15106 | 0.009155 | 0.16937 | 0.17395 | 0.16937 | 0.21515 | -122.7219 | -122.6807 | 0.004577 | 0.050354 | 0.009155 | 0.073242
3532.8438 | 122.6349 | -0.11444 | 122.6028 | 0.0016023 | -0.0075559 | 0.00092925 | -0.012315 | 0.0010724 | -0.010043 | -0.0040439 | -0.0082093 | 0.011343 | 0.0020828 | 0.0080173 | -0.017141 | 0.023499 | -0.0039884 | -0.09613 | 0.054932 | -0.11444 | -0.10529 | 0.022888 | -0.10529 | -0.041199 | -0.013733 | 0.10986 | -0.086975 | -0.018311 | 0.11902 | 0.009155 | 0.07782 | 0 | -122.5479 | -122.7081 | 0.13733 | 0.073242 | 0.009155 | 0.073242 | 0.009155 | 0.027466 | -122.493 | -122.6212 | 0.23346 | 0.19226 | 0.1236 | 0.16479 | 0.09613 | 0.13733 | 0.009155 | 0.20599 | 0.068664 | 0.16937 | 0.19684 | 0.16937 | 0.2243 | -122.7173 | -122.6898 | 0.009155 | 0.09613 | 0.018311 | 0.10071
3534.5469 | 122.6486 | -0.09613 | 122.6257 | -0.021286 | -0.0067013 | 0.0022111 | -0.015093 | -0.0025592 | -0.010683 | -0.0059665 | -0.0082093 | 0.011557 | 0.0022964 | 0.00054052 | -0.018423 | 0.02179 | 0.0024204 | -0.068665 | 0.086975 | -0.10071 | -0.091553 | 0.027466 | -0.09613 | -0.036621 | -0.022888 | 0.11444 | -0.07782 | -0.004578 | 0.12817 | 0.013733 | 0.10529 | -0.004578 | -122.5388 | -122.7173 | 0.1236 | 0.059509 | 0 | 0.064087 | 0.004578 | 0.01831 | -122.5113 | -122.6303 | 0.2243 | 0.20142 | 0.10986 | 0.18311 | 0.091553 | 0.12817 | 0.009155 | 0.20599 | 0.073242 | 0.18768 | 0.19226 | 0.1831 | 0.21057 | -122.7264 | -122.7036 | 0.004577 | 0.091552 | 0.027465 | 0.073242
3536.25 | 122.6303 | -0.07782 | 122.5891 | -0.021286 | -0.0064877 | 0.00028845 | -0.011675 | 0.0019268 | -0.01282 | -0.0046847 | -0.0051575 | 0.011771 | 0.0044326 | 0.0035311 | -0.018637 | 0.023285 | 0.0004978 | -0.013733 | 0.10529 | -0.032043 | -0.013733 | 0.09613 | -0.073242 | -0.004578 | 0.068665 | 0.12817 | -0.022888 | 0.009155 | 0.14191 | 0.018311 | 0.082397 | 0.045777 | -122.4838 | -122.6028 | 0.17395 | 0.073242 | 0.004578 | 0.027465 | -0.041199 | 0.054932 | -122.4609 | -122.58 | 0.21973 | 0.16022 | 0.096131 | 0.10528 | 0.041199 | 0.12817 | 0.01831 | 0.16479 | 0.032043 | 0.13733 | 0.15106 | 0.18311 | 0.20599 | -122.6212 | -122.612 | 0.064087 | 0.086975 | 0.064087 | 0.14649
3538.0156 | 122.6486 | -0.082397 | 122.58 | -0.0060272 | -0.0064877 | 0.0032791 | -0.017015 | 0.0014996 | -0.011538 | -0.0034031 | -0.0082093 | 0.0096344 | 0.001442 | 0.00011332 | -0.016073 | 0.020508 | -0.0003568 | -0.068665 | 0.022888 | -0.07782 | -0.054932 | 0.091553 | -0.09613 | -0.004578 | 0.041199 | 0.064087 | -0.054932 | 0.004578 | 0.13733 | 0.027466 | 0.10529 | 0.004577 | -122.5571 | -122.6349 | 0.17395 | 0.077819 | -0.013733 | 0.073242 | -0.01831 | 0.027465 | -122.5159 | -122.5754 | 0.21973 | 0.18768 | 0.10986 | 0.16022 | 0.082398 | 0.16937 | 0.022888 | 0.19226 | 0.05951 | 0.10071 | 0.11902 | 0.10528 | 0.14648 | -122.6578 | -122.6349 | 0.027465 | 0.086975 | 0.013732 | 0.1236
3539.7188 | 122.6486 | -0.091553 | 122.6028 | -0.021286 | -0.0047787 | 0.0015701 | -0.012315 | -0.0017048 | -0.0091879 | -0.0053257 | -0.0082093 | 0.013693 | 0.0029372 | 0.00075412 | -0.017996 | 0.024353 | -0.0014248 | -0.064087 | 0.050354 | -0.091553 | -0.068665 | 0.022888 | -0.11444 | -0.041199 | 0.013733 | 0.073242 | -0.091553 | -0.009155 | 0.10529 | 0.013733 | 0.07782 | 0 | -122.5525 | -122.6715 | 0.11444 | 0.050354 | -0.022888 | 0.050354 | -0.022888 | 0 | -122.5296 | -122.612 | 0.19684 | 0.16937 | 0.10529 | 0.16937 | 0.10529 | 0.11444 | 0.022888 | 0.19684 | 0.082398 | 0.14191 | 0.16479 | 0.14191 | 0.16479 | -122.6944 | -122.6944 | 0.022888 | 0.082398 | 0.027466 | 0.10529
3541.4219 | 122.7493 | -0.086975 | 122.5571 | -0.0060272 | -0.0071285 | -0.00077975 | -0.015733 | -0.0019184 | -0.010683 | -0.0048985 | -0.0051575 | 0.0092072 | 0.001442 | -0.0037321 | -0.019064 | 0.021362 | 7.04e-05 | -0.036621 | 0.013733 | -0.073242 | 0.009155 | 0.1831 | -0.009155 | 0.073242 | 0.13275 | 0.059509 | -0.050354 | 0.068665 | 0.21973 | 0.11902 | 0.14191 | 0.013733 | -122.5433 | -122.5479 | 0.27008 | 0.16022 | 0.07782 | 0.14648 | 0.064087 | 0.036621 | -122.4976 | -122.4884 | 0.3067 | 0.22888 | 0.20599 | 0.19226 | 0.16937 | 0.25635 | 0.082397 | 0.27008 | 0.11902 | 0.086975 | 0.10986 | 0.10071 | 0.14648 | -122.6303 | -122.6074 | 0.09613 | 0.15564 | 0.050354 | 0.21973
3543.1719 | 122.6898 | -0.068665 | 122.5662 | -0.013657 | -0.0041379 | 0.0019975 | -0.014238 | 0.0036358 | -0.011751 | -0.0083163 | -0.0082093 | 0.0096344 | 0.0020828 | -0.0011685 | -0.018637 | 0.02179 | -0.0039884 | -0.059509 | 0.018311 | -0.073242 | -0.022888 | 0.10529 | -0.091553 | 0.004578 | 0.050354 | 0.054932 | -0.054932 | 0.022888 | 0.13275 | 0.054932 | 0.11444 | -0.004577 | -122.5479 | -122.5891 | 0.17395 | 0.073243 | -0.022888 | 0.07782 | -0.018311 | 0.013733 | -122.5113 | -122.5433 | 0.20142 | 0.18311 | 0.1236 | 0.16937 | 0.10986 | 0.17853 | 0.050354 | 0.18768 | 0.07782 | 0.091553 | 0.10986 | 0.086976 | 0.1236 | -122.6395 | -122.6212 | 0.045777 | 0.091553 | 0.009156 | 0.11902
3544.9375 | 122.6303 | -0.10986 | 122.5937 | -0.0060272 | -0.0052059 | 0.0030655 | -0.011034 | 0.0014996 | -0.0083335 | -0.0053257 | -0.0051575 | 0.011984 | 0.0022964 | 0.0050265 | -0.018637 | 0.023712 | -0.004202 | -0.091553 | 0.036621 | -0.1236 | -0.1236 | -0.013733 | -0.16479 | -0.091553 | -0.032043 | 0.09613 | -0.091553 | -0.032043 | 0.064087 | -0.050354 | 0.050354 | -0.013733 | -122.5571 | -122.7173 | 0.09613 | 0.01831 | -0.054932 | 0.032043 | -0.041199 | 0.01831 | -122.4976 | -122.6257 | 0.17395 | 0.16022 | 0.059509 | 0.14191 | 0.041199 | 0.10986 | 0 | 0.15564 | 0.05951 | 0.16022 | 0.18768 | 0.14648 | 0.20599 | -122.7173 | -122.6852 | -0.013733 | 0.07782 | 0.01831 | 0.07782
3546.6875 | 122.7402 | -0.054932 | 122.5708 | 0.0016023 | -0.0073423 | -0.00013895 | -0.015733 | -0.0046954 | -0.013888 | -0.0036167 | 0.0070495 | 0.012411 | 0.0018692 | -0.0015957 | -0.017568 | 0.019867 | 0.0022068 | -0.045776 | 0.018311 | -0.073242 | 0.018311 | 0.16479 | -0.004578 | 0.036621 | 0.11902 | 0.059509 | -0.045776 | 0.045776 | 0.21973 | 0.11444 | 0.13733 | -0.01831 | -122.5525 | -122.5525 | 0.21973 | 0.091553 | 0.050354 | 0.10986 | 0.068664 | 0.009156 | -122.5113 | -122.525 | 0.27466 | 0.19226 | 0.16937 | 0.18311 | 0.16022 | 0.23804 | 0.091553 | 0.2655 | 0.091552 | 0.091553 | 0.10528 | 0.073243 | 0.11444 | -122.644 | -122.6166 | 0.073243 | 0.10071 | 0.009156 | 0.17395
3548.3906 | 122.7264 | -0.068665 | 122.5571 | -0.028916 | -0.0043515 | 0.0034927 | -0.013597 | 0.00043159 | -0.0094015 | -0.0046847 | -0.011261 | 0.011984 | 0.00037383 | -0.0048001 | -0.018637 | 0.022003 | 0.0007114 | -0.068665 | 0.045776 | -0.10529 | -0.050354 | 0.050354 | -0.13275 | -0.032043 | 0.045776 | 0.059509 | -0.068665 | 0.059509 | 0.16479 | 0.073242 | 0.14648 | -0.036621 | -122.5113 | -122.6074 | 0.11902 | 0.036622 | -0.064086 | 0.073243 | -0.027465 | 0 | -122.4976 | -122.4976 | 0.23346 | 0.21515 | 0.14191 | 0.21515 | 0.14191 | 0.15564 | 0.054932 | 0.23346 | 0.12817 | 0.15106 | 0.12817 | 0.11444 | 0.12817 | -122.6624 | -122.6257 | 0.018311 | 0.12817 | 0 | 0.11444
3550.1719 | 122.5937 | -0.12817 | 122.6212 | -0.021286 | -0.0064877 | 7.4854e-05 | -0.014238 | -0.00020941 | -0.011965 | -0.0055393 | -0.0082093 | 0.012411 | 0.001442 | -0.0015957 | -0.017568 | 0.020081 | -0.0029202 | -0.13275 | 0.073242 | -0.10529 | -0.10986 | -0.004578 | -0.14191 | -0.054932 | -0.064087 | 0.068665 | -0.091553 | -0.07782 | 0.059509 | -0.027466 | 0.013733 | 0.022888 | -122.5479 | -122.731 | 0.1236 | 0.073242 | -0.013733 | 0.050354 | -0.036621 | 0.036621 | -122.5525 | -122.699 | 0.18768 | 0.14191 | 0.10071 | 0.10529 | 0.064087 | 0.10071 | -0.004577 | 0.15106 | 0.013733 | 0.17853 | 0.16022 | 0.20142 | 0.19684 | -122.7264 | -122.7127 | 0.018311 | 0.050354 | -0.004577 | 0.064087
3551.875 | 122.6578 | -0.086975 | 122.5937 | -0.021286 | -0.0041379 | 0.0011429 | -0.012956 | -0.0019184 | -0.01047 | -0.0066073 | -0.0051575 | 0.010275 | 0.0040054 | 0.0022495 | -0.016714 | 0.020935 | -0.0001432 | -0.050354 | 0.054932 | -0.09613 | -0.068665 | 0.064087 | -0.10071 | -0.032043 | 0.027466 | 0.07782 | -0.07782 | 0.018311 | 0.11444 | 0.022888 | 0.082397 | -0.009155 | -122.5388 | -122.6624 | 0.15106 | 0.054932 | -0.013733 | 0.064087 | -0.004578 | 0.009155 | -122.5159 | -122.5754 | 0.20142 | 0.16937 | 0.10986 | 0.16022 | 0.10071 | 0.16022 | 0.027465 | 0.19226 | 0.096131 | 0.15106 | 0.15564 | 0.14191 | 0.16479 | -122.6898 | -122.6715 | 0.01831 | 0.10529 | 0.036621 | 0.11444
3553.6406 | 122.7081 | -0.07782 | 122.5891 | -0.013657 | -0.0067013 | -0.00035255 | -0.015733 | -0.0025592 | -0.013247 | -0.0055393 | -0.0082093 | 0.0089934 | 0.0027236 | 0.00011332 | -0.016073 | 0.020935 | 0.002634 | -0.07782 | 0.036621 | -0.091553 | -0.064087 | 0.064087 | -0.086975 | 0.004578 | 0.036621 | 0.064087 | -0.073242 | 0.018311 | 0.16479 | 0.064087 | 0.11444 | -0.013733 | -122.5525 | -122.6532 | 0.14191 | 0.082398 | -0.009155 | 0.096131 | 0.004578 | 0.004578 | -122.525 | -122.5708 | 0.24261 | 0.19226 | 0.14191 | 0.18768 | 0.13733 | 0.15564 | 0.027466 | 0.23804 | 0.091553 | 0.12817 | 0.13733 | 0.11444 | 0.14191 | -122.6807 | -122.6624 | 0.013733 | 0.096131 | 0 | 0.11444
3555.3438 | 122.6257 | -0.10071 | 122.612 | -0.013657 | -0.0077695 | 0.0013565 | -0.014238 | -0.00020941 | -0.010256 | -0.0066073 | -0.0082093 | 0.010275 | 0.001442 | 0.0013949 | -0.015859 | 0.023071 | -0.0012112 | -0.054932 | 0.036621 | -0.09613 | -0.050354 | 0.086975 | -0.073242 | -0.004578 | 0.009155 | 0.091553 | -0.091553 | -0.059509 | 0.10071 | 0 | 0.050354 | 0.004578 | -122.5754 | -122.6624 | 0.18768 | 0.09613 | 0.027466 | 0.091552 | 0.022888 | 0.009155 | -122.5204 | -122.6715 | 0.20142 | 0.15106 | 0.10071 | 0.14191 | 0.091553 | 0.1831 | 0.045776 | 0.19226 | 0.032044 | 0.13275 | 0.18311 | 0.13733 | 0.19226 | -122.7081 | -122.7036 | 0.050354 | 0.041199 | 0.045776 | 0.10986
3557.0938 | 122.7493 | -0.064087 | 122.5891 | -0.013657 | -0.0081967 | 0.00092925 | -0.015947 | 0.0010724 | -0.0096151 | -0.0025485 | -0.0051575 | 0.010702 | 0.0027236 | -0.00031408 | -0.01885 | 0.020935 | -0.0037748 | -0.036621 | 0.004578 | -0.082397 | 0.018311 | 0.17395 | 0 | 0.073242 | 0.15564 | 0.059509 | -0.050354 | 0.068665 | 0.20599 | 0.10986 | 0.14191 | -0.01831 | -122.5845 | -122.5708 | 0.23804 | 0.13733 | 0.064087 | 0.15564 | 0.082397 | 0.013733 | -122.5296 | -122.5204 | 0.27008 | 0.20599 | 0.17395 | 0.19226 | 0.16022 | 0.25635 | 0.10071 | 0.25635 | 0.11902 | 0.086975 | 0.10986 | 0.068665 | 0.1236 | -122.6715 | -122.6395 | 0.082398 | 0.13275 | 0.027466 | 0.21973
3558.7812 | 122.612 | -0.10071 | 122.6303 | 0.0016023 | -0.0015743 | 0.0026383 | -0.012529 | -0.00020941 | -0.010043 | -0.0040439 | -0.0082093 | 0.012839 | 0.0033646 | -0.0033047 | -0.017141 | 0.020935 | -0.0029202 | -0.07782 | 0.059509 | -0.10071 | -0.10071 | 0.009155 | -0.17853 | -0.091553 | -0.054932 | 0.091553 | -0.082397 | -0.064087 | 0.041199 | -0.054932 | 0.027466 | 0 | -122.5708 | -122.731 | 0.10986 | 0.009155 | -0.07782 | 0.009155 | -0.07782 | 0.018311 | -122.5388 | -122.6944 | 0.14191 | 0.12817 | 0.045776 | 0.10986 | 0.027465 | 0.10986 | 0 | 0.1236 | 0.01831 | 0.16022 | 0.17395 | 0.16022 | 0.19226 | -122.731 | -122.7127 | 0 | 0.036621 | 0.022888 | 0.045776
3560.5312 | 122.7264 | -0.082397 | 122.5983 | -0.013657 | -0.0032833 | 0.0017837 | -0.014238 | 0.00064519 | -0.011111 | -0.0055393 | 0.0009461 | 0.010916 | 0.00251 | -0.00074128 | -0.015859 | 0.023499 | -0.0039884 | -0.032043 | 0.009155 | -0.050354 | 0.004578 | 0.15106 | -0.068665 | 0.036621 | 0.11444 | 0.045776 | -0.073242 | 0.059509 | 0.17853 | 0.064087 | 0.11902 | 0.032043 | -122.5891 | -122.5937 | 0.23346 | 0.11902 | 0.013732 | 0.086975 | -0.018311 | 0.009155 | -122.5525 | -122.5388 | 0.26092 | 0.20142 | 0.14648 | 0.19226 | 0.13733 | 0.20142 | 0.054932 | 0.25177 | 0.13275 | 0.059509 | 0.11902 | 0.091552 | 0.12817 | -122.6486 | -122.6715 | 0.086975 | 0.14191 | 0.050354 | 0.19684
3562.2969 | 122.7402 | -0.068665 | 122.58 | -0.013657 | -0.0043515 | 0.0028519 | -0.012315 | -0.00085021 | -0.0096151 | -0.0066073 | -0.0082093 | 0.0092072 | -0.00048057 | -0.0026639 | -0.016714 | 0.022858 | -0.0012112 | -0.004578 | 0.004578 | -0.064087 | 0.013733 | 0.15564 | -0.07782 | 0.032043 | 0.13733 | 0.045776 | -0.045776 | 0.073242 | 0.18768 | 0.082397 | 0.13733 | 0.004578 | -122.5754 | -122.5662 | 0.22431 | 0.10071 | -0.009155 | 0.09613 | -0.013733 | 0.022889 | -122.5342 | -122.5067 | 0.25635 | 0.20599 | 0.15106 | 0.18311 | 0.12817 | 0.21973 | 0.07782 | 0.23346 | 0.11902 | 0.068665 | 0.091552 | 0.073243 | 0.11444 | -122.644 | -122.6257 | 0.082398 | 0.14191 | 0.064087 | 0.20599
3564.0625 | 122.699 | -0.086975 | 122.5845 | -0.021286 | -0.0047787 | 0.0011429 | -0.014665 | 0.001286 | -0.011538 | -0.0044711 | -0.0082093 | 0.011557 | 0.001442 | -0.0071499 | -0.018637 | 0.021362 | 0.0015658 | -0.086975 | 0.032043 | -0.086975 | -0.050354 | 0.07782 | -0.10986 | -0.009155 | 0.036621 | 0.054932 | -0.073242 | 0.013733 | 0.13733 | 0.036621 | 0.086975 | 0 | -122.5525 | -122.6349 | 0.16479 | 0.07782 | -0.022888 | 0.07782 | -0.022888 | 0.013733 | -122.5296 | -122.5708 | 0.2243 | 0.17395 | 0.1236 | 0.16022 | 0.10986 | 0.16479 | 0.036621 | 0.21057 | 0.086975 | 0.11902 | 0.12817 | 0.11902 | 0.14191 | -122.6715 | -122.6578 | 0.036621 | 0.10071 | 0 | 0.1236
3565.8438 | 122.6166 | -0.11902 | 122.6349 | -0.021286 | -0.0034971 | -0.0078293 | -0.012315 | 0.0014996 | -0.014529 | -0.0083163 | -0.0082093 | 0.014548 | 0.00080103 | -0.00052768 | -0.017355 | 0.016449 | -0.0029202 | -0.091553 | 0.036621 | -0.10529 | -0.10071 | -0.022888 | -0.17853 | -0.091553 | -0.054932 | 0.11444 | -0.07782 | -0.050354 | 0.022888 | -0.068665 | 0.045776 | 0.013733 | -122.5983 | -122.7356 | 0.096131 | 0.027466 | -0.059509 | 0.013733 | -0.073242 | 0.041199 | -122.5204 | -122.6852 | 0.14191 | 0.16479 | 0.050354 | 0.1236 | 0.009155 | 0.082398 | 0.004578 | 0.10071 | 0.027466 | 0.14191 | 0.19226 | 0.15564 | 0.23346 | -122.7402 | -122.7127 | 0.018311 | 0.068665 | 0.027466 | 0.064087
3567.5469 | 122.731 | -0.091553 | 122.5937 | -0.0060272 | -0.0073423 | -0.00099335 | -0.01552 | -0.0017048 | -0.01047 | -0.0053257 | -0.0021057 | 0.0087798 | 0.0022964 | -0.00095488 | -0.017568 | 0.022217 | -0.0016384 | -0.091553 | 0 | -0.082397 | -0.064087 | 0.07782 | -0.09613 | 0 | 0.027466 | 0.064087 | -0.086975 | 0.004578 | 0.15564 | 0.064087 | 0.10986 | 0.009156 | -122.5937 | -122.6578 | 0.16937 | 0.091553 | -0.004577 | 0.082397 | -0.013733 | 0.004578 | -122.5296 | -122.5891 | 0.24719 | 0.20142 | 0.15564 | 0.19684 | 0.15106 | 0.16022 | 0.01831 | 0.24261 | 0.091553 | 0.082397 | 0.15106 | 0.091553 | 0.15564 | -122.6761 | -122.6807 | 0.027466 | 0.096131 | 0 | 0.11902
3569.3125 | 122.7173 | -0.086975 | 122.5937 | -0.013657 | -0.0067013 | -0.00013895 | -0.016161 | -0.00020941 | -0.01282 | -0.0034031 | -0.0051575 | 0.010275 | 0.0016556 | -0.0088589 | -0.018209 | 0.020935 | 0.0011386 | -0.086975 | 0.036621 | -0.086975 | -0.050354 | 0.073242 | -0.086975 | 0 | 0.022888 | 0.073242 | -0.07782 | 0.027466 | 0.15106 | 0.068665 | 0.10986 | 0 | -122.5571 | -122.644 | 0.16022 | 0.086975 | 0 | 0.086975 | 0 | 0.009155 | -122.5204 | -122.5662 | 0.23804 | 0.19684 | 0.15564 | 0.18768 | 0.14649 | 0.16022 | 0.036621 | 0.22888 | 0.10529 | 0.1236 | 0.15106 | 0.1236 | 0.16022 | -122.6807 | -122.6715 | 0.036621 | 0.11444 | 0 | 0.10986
3571.0781 | 122.6303 | -0.10529 | 122.6212 | -0.0060272 | -0.0028561 | 0.00028845 | -0.012743 | 0.00085879 | -0.0098287 | -0.0085299 | -0.0082093 | 0.013266 | 0.00080103 | -0.0086453 | -0.016714 | 0.011536 | 0.0028476 | -0.054932 | 0.045776 | -0.10529 | -0.068665 | 0.036621 | -0.14191 | -0.050354 | 0.004578 | 0.10986 | -0.068665 | -0.013733 | 0.07782 | -0.045776 | 0.045776 | 0 | -122.5754 | -122.6898 | 0.14191 | 0.054932 | -0.036621 | 0.054932 | -0.036621 | 0.036621 | -122.5113 | -122.6349 | 0.18311 | 0.15106 | 0.05951 | 0.11444 | 0.022889 | 0.14191 | 0.036621 | 0.14649 | 0.054932 | 0.15106 | 0.17853 | 0.15106 | 0.21515 | -122.7264 | -122.6898 | 0.036621 | 0.091553 | 0.050354 | 0.10986
3572.8438 | 122.6303 | -0.10071 | 122.6624 | -0.021286 | -0.0045651 | -0.0029159 | -0.01317 | -0.00085021 | -0.0096151 | -0.0038303 | -0.0051575 | 0.012625 | 0.0029372 | 0.0028903 | -0.0165 | 0.023499 | -0.0027066 | -0.091553 | 0.068665 | -0.10986 | -0.11902 | -0.027466 | -0.18768 | -0.09613 | -0.036621 | 0.10986 | -0.10986 | -0.027466 | 0.059509 | -0.050354 | 0.041199 | -0.009155 | -122.5937 | -122.7814 | 0.073242 | 0.004578 | -0.086975 | 0.013733 | -0.07782 | -0.009155 | -122.5525 | -122.6898 | 0.16022 | 0.14191 | 0.050354 | 0.15106 | 0.059509 | 0.082397 | -0.009156 | 0.16937 | 0.082397 | 0.17853 | 0.21973 | 0.16937 | 0.21057 | -122.7722 | -122.7722 | -0.018311 | 0.073242 | 0.009155 | 0.064087
3574.5312 | 122.7219 | -0.082397 | 122.5937 | -0.028916 | -0.0047787 | 0.0013565 | -0.01552 | 0.0014996 | -0.0094015 | -0.0055393 | -0.011261 | 0.0092072 | 0.0016556 | 0.0031039 | -0.017996 | 0.019226 | -0.0014248 | -0.032043 | 0.027466 | -0.068665 | -0.013733 | 0.15564 | -0.073242 | 0.022888 | 0.11444 | 0.073242 | -0.054932 | 0.059509 | 0.16022 | 0.059509 | 0.10529 | 0.013732 | -122.5662 | -122.6074 | 0.23804 | 0.10528 | 0.009155 | 0.091553 | -0.004577 | 0.027465 | -122.5204 | -122.5342 | 0.24261 | 0.18768 | 0.14191 | 0.16022 | 0.11444 | 0.22431 | 0.054932 | 0.21515 | 0.11444 | 0.096131 | 0.12817 | 0.10986 | 0.15564 | -122.6624 | -122.6486 | 0.068664 | 0.14191 | 0.050354 | 0.19684
3576.3281 | 122.6303 | -0.10986 | 122.6486 | -0.013657 | -0.0045651 | -0.0012069 | -0.013811 | 0.0019268 | -0.01346 | -0.0036167 | -0.0051575 | 0.013266 | 0.0027236 | -0.0062955 | -0.019491 | 0.022003 | 0.0019932 | -0.11444 | 0.059509 | -0.1236 | -0.11444 | -0.009155 | -0.14648 | -0.064087 | -0.036621 | 0.10071 | -0.086975 | -0.050354 | 0.059509 | -0.032043 | 0.045776 | -0.013733 | -122.5891 | -122.7631 | 0.10071 | 0.045776 | -0.036621 | 0.059509 | -0.022888 | 0.022888 | -122.5479 | -122.699 | 0.16937 | 0.15564 | 0.07782 | 0.13275 | 0.054932 | 0.11444 | 0.009155 | 0.14648 | 0.036621 | 0.1831 | 0.18768 | 0.16937 | 0.21057 | -122.7722 | -122.7356 | -0.004578 | 0.059509 | -0.004578 | 0.073242
3578.0938 | 122.7264 | -0.091553 | 122.612 | -0.013657 | -0.0067013 | 0.0015701 | -0.016588 | -0.0017048 | -0.01047 | -0.0057529 | -0.0082093 | 0.010275 | 0.00080103 | -0.0041593 | -0.018209 | 0.021362 | -0.0039884 | -0.07782 | 0.041199 | -0.07782 | -0.054932 | 0.07782 | -0.086975 | 0.004578 | 0.041199 | 0.064087 | -0.082397 | 0.009155 | 0.15106 | 0.068665 | 0.11444 | 0.013733 | -122.5708 | -122.6669 | 0.16937 | 0.096131 | 0.004578 | 0.082398 | -0.009155 | 0.009156 | -122.5479 | -122.6028 | 0.24261 | 0.20599 | 0.16022 | 0.19684 | 0.15106 | 0.15564 | 0.022888 | 0.23346 | 0.091552 | 0.11902 | 0.14648 | 0.13275 | 0.15564 | -122.6898 | -122.6944 | 0.036621 | 0.10071 | 0.013733 | 0.13275
3579.8594 | 122.6074 | -0.10986 | 122.644 | -0.021286 | -0.0026425 | -0.0024887 | -0.012956 | 0.0057722 | -0.01047 | -0.0068211 | -0.0051575 | 0.013907 | 0.00080103 | 0.0035311 | -0.019918 | 0.019653 | -0.002493 | -0.07782 | 0.064087 | -0.10986 | -0.1236 | -0.022888 | -0.19684 | -0.091553 | -0.064087 | 0.091553 | -0.082397 | -0.068665 | 0.041199 | -0.073242 | 0.022888 | 0 | -122.58 | -122.7676 | 0.086975 | 0.01831 | -0.086975 | 0.01831 | -0.086975 | 0.027466 | -122.5525 | -122.7127 | 0.15106 | 0.13275 | 0.036621 | 0.10528 | 0.009155 | 0.086975 | -0.013733 | 0.1236 | 0.013732 | 0.17395 | 0.17395 | 0.17395 | 0.20142 | -122.7539 | -122.7264 | -0.013733 | 0.041198 | 0.032043 | 0.045776
3581.5625 | 122.7081 | -0.07782 | 122.5937 | -0.013657 | -0.0058469 | 0.00092925 | -0.014024 | -0.00085021 | -0.013033 | -0.0053257 | -0.0051575 | 0.0096344 | 0.0016556 | -0.0062955 | -0.017996 | 0.02179 | 0.0004978 | -0.041199 | 0.022888 | -0.059509 | 0 | 0.15106 | -0.064087 | 0.009155 | 0.10071 | 0.064087 | -0.068665 | 0.036621 | 0.15564 | 0.059509 | 0.09613 | 0.018311 | -122.5708 | -122.5937 | 0.22888 | 0.086975 | 0.013733 | 0.068664 | -0.004578 | 0.009155 | -122.5296 | -122.5571 | 0.23346 | 0.17395 | 0.13733 | 0.16479 | 0.12817 | 0.21057 | 0.059509 | 0.22431 | 0.10529 | 0.082397 | 0.13275 | 0.10071 | 0.14191 | -122.6532 | -122.6624 | 0.07782 | 0.11444 | 0.036621 | 0.17853
3583.2656 | 122.6624 | -0.10986 | 122.6532 | -0.021286 | -0.0054197 | -0.00035255 | -0.014665 | 0.0017132 | -0.010683 | -0.0042575 | -0.0051575 | 0.012411 | 0.00037383 | 0.0084445 | -0.019277 | 0.023071 | -0.0020658 | -0.10071 | 0.073242 | -0.11902 | -0.10986 | 0 | -0.14191 | -0.059509 | -0.041199 | 0.086975 | -0.086975 | -0.059509 | 0.07782 | -0.022888 | 0.045776 | -0.009156 | -122.58 | -122.7631 | 0.10986 | 0.050354 | -0.032044 | 0.05951 | -0.022888 | 0.022888 | -122.5662 | -122.7127 | 0.18768 | 0.15564 | 0.086975 | 0.13275 | 0.064087 | 0.11902 | 0.009156 | 0.16479 | 0.027466 | 0.19226 | 0.17395 | 0.18311 | 0.19684 | -122.7722 | -122.7402 | 0 | 0.050354 | 0.009155 | 0.068664
3585.0312 | 122.7768 | -0.068665 | 122.5983 | -0.021286 | -0.0071285 | -0.00099335 | -0.018083 | -0.00020941 | -0.010683 | -0.0057529 | -0.0082093 | 0.010489 | 0.00251 | -0.0060819 | -0.017782 | 0.021576 | 0.0002842 | -0.050354 | 0.027466 | -0.086975 | -0.018311 | 0.12817 | -0.032043 | 0.045776 | 0.11444 | 0.054932 | -0.068665 | 0.054932 | 0.20599 | 0.11902 | 0.13733 | -0.01831 | -122.5708 | -122.6166 | 0.19684 | 0.11444 | 0.036622 | 0.13275 | 0.054932 | 0 | -122.5433 | -122.5433 | 0.27466 | 0.20599 | 0.18768 | 0.20599 | 0.18768 | 0.21515 | 0.068664 | 0.27466 | 0.1236 | 0.11444 | 0.1236 | 0.096131 | 0.1236 | -122.6852 | -122.6669 | 0.050354 | 0.1236 | 0.018311 | 0.18311
3586.7969 | 122.7448 | -0.086975 | 122.5983 | -0.0060272 | -0.0071285 | 0.0017837 | -0.016588 | 0.0021406 | -0.012606 | -0.0055393 | -0.011261 | 0.010062 | 0.0020828 | -0.0050137 | -0.018637 | 0.021576 | -0.003561 | -0.073242 | 0.018311 | -0.09613 | -0.050354 | 0.07782 | -0.068665 | 0.018311 | 0.045776 | 0.059509 | -0.086975 | 0.022888 | 0.17395 | 0.082397 | 0.12817 | -0.009155 | -122.58 | -122.6486 | 0.16479 | 0.10529 | 0.01831 | 0.11444 | 0.027465 | 0 | -122.5388 | -122.5754 | 0.26092 | 0.21515 | 0.16937 | 0.21515 | 0.16937 | 0.17395 | 0.045776 | 0.26092 | 0.10986 | 0.11444 | 0.14648 | 0.10529 | 0.14648 | -122.6944 | -122.6852 | 0.036621 | 0.10986 | 0.013733 | 0.13275
3588.5625 | 122.6852 | -0.10071 | 122.644 | -0.0060272 | -0.0073423 | 7.4854e-05 | -0.011888 | -0.007259 | -0.011111 | -0.0059665 | -0.0082093 | 0.013907 | -5.3368e-05 | -0.0062955 | -0.015219 | 0.014099 | -0.0018522 | -0.041199 | 0.050354 | -0.10986 | -0.045776 | 0.064087 | -0.11444 | -0.045776 | 0.036621 | 0.082397 | -0.086975 | -0.009155 | 0.10986 | -0.004578 | 0.068665 | -0.009155 | -122.5937 | -122.6898 | 0.1648 | 0.054932 | -0.013733 | 0.064087 | -0.004578 | 0.013733 | -122.5616 | -122.6532 | 0.21057 | 0.16937 | 0.09613 | 0.15564 | 0.082397 | 0.17395 | 0.064087 | 0.19684 | 0.07782 | 0.16022 | 0.16937 | 0.15106 | 0.18311 | -122.7539 | -122.731 | 0.054932 | 0.091553 | 0.059509 | 0.13733
3590.3281 | 122.7356 | -0.086975 | 122.6028 | -0.013657 | -0.0047787 | 0.0037063 | -0.016374 | -0.001491 | -0.010256 | -0.0061801 | -0.0051575 | 0.0096344 | 0.0010146 | 0.0011813 | -0.017355 | 0.023712 | -0.0018522 | -0.032043 | 0.013733 | -0.068665 | 0.004578 | 0.13733 | -0.059509 | 0.022888 | 0.10529 | 0.064087 | -0.068665 | 0.054932 | 0.17395 | 0.064087 | 0.11902 | 0.01831 | -122.5891 | -122.5983 | 0.2243 | 0.10986 | 0.027466 | 0.091553 | 0.009156 | 0.01831 | -122.5388 | -122.5479 | 0.26092 | 0.20599 | 0.15106 | 0.18768 | 0.13275 | 0.20599 | 0.073243 | 0.24261 | 0.1236 | 0.082398 | 0.13275 | 0.10071 | 0.15106 | -122.6715 | -122.6715 | 0.091553 | 0.14191 | 0.054932 | 0.19226
3592.0312 | 122.6486 | -0.12817 | 122.6349 | -0.013657 | -0.0069149 | -0.0016341 | -0.013597 | -0.0010638 | -0.011965 | -0.0076755 | -0.0082093 | 0.012411 | 0.00080103 | -0.00095488 | -0.017782 | 0.02243 | -0.0027066 | -0.09613 | 0.064087 | -0.1236 | -0.11902 | -0.009155 | -0.14191 | -0.064087 | -0.054932 | 0.09613 | -0.10986 | -0.050354 | 0.068665 | -0.018311 | 0.050354 | 0.004578 | -122.5708 | -122.7539 | 0.11902 | 0.064087 | -0.013733 | 0.059509 | -0.018311 | 0.018311 | -122.5388 | -122.6852 | 0.19684 | 0.17853 | 0.10986 | 0.16022 | 0.091552 | 0.11444 | 0.004577 | 0.17853 | 0.059509 | 0.18768 | 0.20599 | 0.19226 | 0.2243 | -122.7585 | -122.7448 | 0.009155 | 0.07782 | 0.032044 | 0.073242
3593.7969 | 122.7448 | -0.082397 | 122.6028 | -0.013657 | -0.0079831 | 0.00028845 | -0.01787 | -0.0042682 | -0.0094015 | -0.0023349 | -0.0082093 | 0.009848 | 0.0035782 | -0.0030911 | -0.017141 | 0.022644 | -0.0044156 | -0.07782 | 0.027466 | -0.082397 | -0.050354 | 0.082397 | -0.091553 | 0.018311 | 0.032043 | 0.050354 | -0.07782 | 0.018311 | 0.17395 | 0.068665 | 0.11444 | 0 | -122.5754 | -122.6532 | 0.16479 | 0.10071 | -0.009156 | 0.10071 | -0.009156 | 0.004577 | -122.5525 | -122.5845 | 0.25635 | 0.19684 | 0.15106 | 0.19226 | 0.14649 | 0.16479 | 0.032043 | 0.25177 | 0.096131 | 0.10986 | 0.12817 | 0.10986 | 0.13275 | -122.6852 | -122.6807 | 0.032043 | 0.10071 | 0.004577 | 0.11444
3595.5625 | 122.7081 | -0.09613 | 122.6349 | -0.013657 | -0.0075559 | 0.0019975 | -0.014879 | -0.0010638 | -0.011111 | -0.0031895 | -0.0021057 | 0.011557 | 0.0016556 | -0.0052273 | -0.019705 | 0.022003 | -0.0031338 | -0.054932 | 0.032043 | -0.10071 | 0.004578 | 0.11902 | -0.022888 | 0.022888 | 0.050354 | 0.064087 | -0.059509 | -0.009155 | 0.14191 | 0.041199 | 0.086975 | -0.004578 | -122.6028 | -122.6303 | 0.21515 | 0.11902 | 0.073242 | 0.1236 | 0.07782 | 0.036621 | -122.5708 | -122.644 | 0.23804 | 0.1831 | 0.13733 | 0.14648 | 0.10071 | 0.21973 | 0.10529 | 0.20142 | 0.050354 | 0.13275 | 0.1236 | 0.12817 | 0.16022 | -122.7356 | -122.6944 | 0.10071 | 0.086975 | 0.041198 | 0.14648
3597.3281 | 122.6715 | -0.12817 | 122.6807 | -0.021286 | -0.0069149 | 0.00092925 | -0.015947 | 0.00085879 | -0.010683 | -0.0042575 | -0.011261 | 0.010916 | 0.0016556 | 0.0018221 | -0.019491 | 0.020721 | -0.0050564 | -0.032043 | 0.027466 | -0.082397 | -0.027466 | 0.091553 | -0.054932 | 0.004578 | 0.027466 | 0.07782 | -0.073242 | -0.045776 | 0.09613 | 0.004578 | 0.045776 | 0.045777 | -122.6532 | -122.7081 | 0.21973 | 0.13275 | 0.073242 | 0.086975 | 0.027465 | 0.054932 | -122.6028 | -122.7264 | 0.2243 | 0.17395 | 0.13275 | 0.11902 | 0.07782 | 0.17395 | 0.054931 | 0.16937 | 0.027466 | 0.10986 | 0.15106 | 0.15564 | 0.20599 | -122.7631 | -122.7539 | 0.10071 | 0.082398 | 0.096131 | 0.15564
3599.0938 | 122.6578 | -0.10071 | 122.644 | 0.0016023 | -0.0058469 | 0.0015701 | -0.012743 | -0.011104 | -0.014315 | -0.0074619 | -0.0082093 | 0.013907 | 0.0020828 | -0.0022367 | -0.014791 | 0.014954 | -0.0044156 | -0.045776 | 0.045776 | -0.10071 | -0.07782 | 0.050354 | -0.13275 | -0.050354 | 0.013733 | 0.07782 | -0.091553 | -0.022888 | 0.082397 | -0.036621 | 0.050354 | 0 | -122.5983 | -122.7219 | 0.15106 | 0.050354 | -0.032043 | 0.050354 | -0.032043 | 0.009155 | -122.5662 | -122.6669 | 0.18311 | 0.15106 | 0.064087 | 0.14191 | 0.054932 | 0.15106 | 0.022888 | 0.17395 | 0.068665 | 0.14648 | 0.16937 | 0.14648 | 0.17853 | -122.7448 | -122.7356 | 0.022888 | 0.07782 | 0.054932 | 0.11444
3600.7969 | 122.644 | -0.10986 | 122.6761 | -0.028916 | -0.0056333 | -0.00013895 | -0.015947 | -0.0017048 | -0.012179 | -0.0070347 | -0.0082093 | 0.011557 | 0.0018692 | -0.0041593 | -0.017141 | 0.022858 | -0.0029202 | -0.10986 | 0.073242 | -0.10986 | -0.12817 | 0 | -0.13733 | -0.059509 | -0.045776 | 0.086975 | -0.09613 | -0.059509 | 0.068665 | -0.032043 | 0.041199 | 0 | -122.6028 | -122.8043 | 0.10986 | 0.050354 | -0.027466 | 0.050354 | -0.027466 | 0.013733 | -122.5891 | -122.7356 | 0.17853 | 0.15106 | 0.07782 | 0.13733 | 0.064087 | 0.10986 | -0.018311 | 0.16479 | 0.036621 | 0.18311 | 0.1831 | 0.18311 | 0.19684 | -122.7859 | -122.7722 | -0.018311 | 0.050354 | 0 | 0.064087
3602.5625 | 122.644 | -0.11444 | 122.6852 | -0.021286 | -0.0058469 | -0.00077975 | -0.01317 | -0.0023456 | -0.013033 | -0.0016941 | -0.0082093 | 0.011557 | 0.00080103 | 0.0013949 | -0.016287 | 0.021576 | -0.0018522 | -0.09613 | 0.068665 | -0.1236 | -0.11444 | -0.009155 | -0.13275 | -0.054932 | -0.054932 | 0.11902 | -0.10529 | -0.050354 | 0.068665 | -0.032043 | 0.041199 | -0.009155 | -122.6166 | -122.7997 | 0.10529 | 0.059509 | -0.01831 | 0.068664 | -0.009155 | 0.009155 | -122.5662 | -122.7356 | 0.18311 | 0.15564 | 0.082398 | 0.14649 | 0.073243 | 0.11444 | 0.009155 | 0.17395 | 0.054932 | 0.19226 | 0.22431 | 0.18311 | 0.23346 | -122.8088 | -122.7905 | 0 | 0.064087 | 0.018311 | 0.059509
3604.2656 | 122.731 | -0.091553 | 122.6212 | -0.013657 | -0.0049923 | 0.00092925 | -0.017229 | -0.002132 | -0.010043 | -0.0085299 | -0.0051575 | 0.011771 | 0.0037918 | 0.0013949 | -0.016287 | 0.021576 | 7.04e-05 | -0.045776 | 0.036621 | -0.068665 | -0.045776 | 0.11444 | -0.082397 | 0.009155 | 0.054932 | 0.064087 | -0.07782 | 0.018311 | 0.13733 | 0.045776 | 0.09613 | 0.022888 | -122.5845 | -122.6669 | 0.20599 | 0.10071 | 0.009156 | 0.07782 | -0.013732 | 0.013733 | -122.5571 | -122.6028 | 0.22888 | 0.18768 | 0.13733 | 0.17395 | 0.1236 | 0.18311 | 0.022889 | 0.21515 | 0.096131 | 0.10529 | 0.14191 | 0.12817 | 0.15564 | -122.6898 | -122.699 | 0.045777 | 0.10986 | 0.045777 | 0.14649
3606.0312 | 122.7402 | -0.082397 | 122.6212 | -0.021286 | -0.0060605 | 0.00092925 | -0.014879 | 0.00021799 | -0.0098287 | -0.0051121 | -0.0051575 | 0.011771 | 0.0037918 | -0.0026639 | -0.018209 | 0.022003 | 0.0004978 | -0.068665 | 0.032043 | -0.07782 | -0.045776 | 0.091553 | -0.07782 | 0.009155 | 0.032043 | 0.050354 | -0.064087 | 0.022888 | 0.13275 | 0.032043 | 0.082397 | 0.004577 | -122.5891 | -122.6669 | 0.17395 | 0.091552 | 0.004577 | 0.086975 | 0 | 0.01831 | -122.5708 | -122.5983 | 0.21515 | 0.16479 | 0.11444 | 0.14648 | 0.09613 | 0.16937 | 0.032044 | 0.19684 | 0.086975 | 0.10986 | 0.11444 | 0.11444 | 0.13275 | -122.699 | -122.6852 | 0.036621 | 0.10528 | 0.013732 | 0.11444
3607.7812 | 122.731 | -0.086975 | 122.6074 | -0.021286 | -0.0047787 | 0.0017837 | -0.013597 | -0.00063661 | -0.011324 | -0.0031895 | -0.0082093 | 0.011343 | 0.0020828 | -0.0048001 | -0.018637 | 0.02179 | -0.00527 | -0.07782 | 0.022888 | -0.07782 | -0.041199 | 0.09613 | -0.091553 | 0 | 0.022888 | 0.064087 | -0.073242 | 0.022888 | 0.13275 | 0.036621 | 0.091553 | 0.009155 | -122.5845 | -122.6486 | 0.1831 | 0.086975 | -0.004578 | 0.07782 | -0.013733 | 0.013733 | -122.5433 | -122.5845 | 0.21973 | 0.17853 | 0.1236 | 0.16479 | 0.10986 | 0.17395 | 0.036621 | 0.20599 | 0.09613 | 0.10071 | 0.13733 | 0.10986 | 0.15106 | -122.6852 | -122.6807 | 0.045776 | 0.10986 | 0.009155 | 0.10986
3609.5312 | 122.7905 | -0.073242 | 122.5891 | -0.0060272 | -0.0069149 | -0.0014205 | -0.014452 | 0.0021406 | -0.011538 | -0.0040439 | -0.0051575 | 0.010062 | 0.0050736 | -0.00031408 | -0.019277 | 0.019867 | -0.0016384 | -0.032043 | 0.032043 | -0.068665 | 0.027466 | 0.1831 | -0.004578 | 0.064087 | 0.15564 | 0.059509 | -0.068665 | 0.064087 | 0.21973 | 0.1236 | 0.14191 | 0.004577 | -122.5571 | -122.5616 | 0.25635 | 0.13733 | 0.068664 | 0.13275 | 0.064087 | 0.004577 | -122.5296 | -122.525 | 0.29297 | 0.21515 | 0.19684 | 0.21057 | 0.19226 | 0.25177 | 0.096131 | 0.28839 | 0.13275 | 0.10071 | 0.12817 | 0.10529 | 0.13275 | -122.6578 | -122.6578 | 0.10071 | 0.13733 | 0.041199 | 0.22888
3611.2969 | 122.7402 | -0.086975 | 122.6166 | -0.021286 | -0.0045651 | 0.0028519 | -0.014452 | -0.00085021 | -0.011965 | -0.0051121 | -0.0082093 | 0.0094208 | 0.0020828 | -0.0018093 | -0.017568 | 0.022858 | -0.0037748 | -0.054932 | 0.036621 | -0.086975 | -0.050354 | 0.07782 | -0.091553 | 0.009155 | 0.059509 | 0.073242 | -0.07782 | 0.022888 | 0.13733 | 0.041199 | 0.091553 | 0 | -122.58 | -122.6669 | 0.16479 | 0.09613 | -0.004578 | 0.09613 | -0.004578 | 0.009155 | -122.5433 | -122.5937 | 0.2243 | 0.17853 | 0.12817 | 0.16937 | 0.11902 | 0.16479 | 0.036621 | 0.21515 | 0.10071 | 0.1236 | 0.15106 | 0.1236 | 0.16022 | -122.7036 | -122.6944 | 0.036621 | 0.10986 | 0.032043 | 0.14648
3613.0469 | 122.7951 | -0.068665 | 122.6074 | -0.021286 | -0.0084103 | -0.00056615 | -0.015093 | -0.0042682 | -0.010897 | -0.0061801 | -0.0051575 | 0.010275 | 0.001442 | -0.0033047 | -0.01885 | 0.022003 | 0.0024204 | -0.045776 | 0.022888 | -0.082397 | -0.009155 | 0.11902 | -0.041199 | 0.050354 | 0.10986 | 0.064087 | -0.064087 | 0.064087 | 0.19684 | 0.10071 | 0.14191 | -0.013732 | -122.5845 | -122.6166 | 0.18768 | 0.11902 | 0.027466 | 0.13275 | 0.041198 | 0.004578 | -122.5433 | -122.5433 | 0.2655 | 0.21057 | 0.16937 | 0.20599 | 0.1648 | 0.20142 | 0.073242 | 0.26093 | 0.12817 | 0.10528 | 0.12817 | 0.091553 | 0.13275 | -122.6898 | -122.6715 | 0.05951 | 0.13275 | 0.022889 | 0.17853
3614.8125 | 122.6852 | -0.10529 | 122.6624 | -0.0060272 | -0.0043515 | 7.4854e-05 | -0.013811 | 0.001286 | -0.011538 | -0.0029759 | -0.0051575 | 0.012411 | 0.0035782 | 0.0013949 | -0.017996 | 0.023712 | -0.0031338 | -0.09613 | 0.059509 | -0.13733 | -0.10529 | -0.004578 | -0.12817 | -0.041199 | -0.045776 | 0.10071 | -0.10529 | -0.050354 | 0.082397 | -0.018311 | 0.064087 | -0.032043 | -122.6028 | -122.7676 | 0.10071 | 0.064087 | -0.022888 | 0.09613 | 0.009155 | 0 | -122.5616 | -122.7127 | 0.18768 | 0.16937 | 0.086975 | 0.16937 | 0.086975 | 0.13275 | 0.032043 | 0.18768 | 0.054932 | 0.19684 | 0.20599 | 0.16479 | 0.20599 | -122.7997 | -122.7676 | 0 | 0.054932 | 0.009156 | 0.05951
3616.5312 | 122.6852 | -0.10071 | 122.6532 | -0.028916 | -0.0071285 | 0.0017837 | -0.012529 | 0.0019268 | -0.010683 | -0.0042575 | -0.0051575 | 0.011984 | 0.0018692 | 0.0069491 | -0.018209 | 0.02243 | -0.0022794 | -0.086975 | 0.068665 | -0.11902 | -0.10071 | 0.004578 | -0.1236 | -0.050354 | -0.036621 | 0.1236 | -0.09613 | -0.027466 | 0.09613 | -0.004578 | 0.059509 | -0.018311 | -122.5845 | -122.7539 | 0.10529 | 0.050354 | -0.022888 | 0.068665 | -0.004577 | 0.004578 | -122.5296 | -122.6807 | 0.19684 | 0.16022 | 0.09613 | 0.15564 | 0.091552 | 0.1236 | 0.018311 | 0.19226 | 0.068664 | 0.18768 | 0.21973 | 0.16937 | 0.2243 | -122.7722 | -122.7493 | 0 | 0.073242 | 0.013733 | 0.064087
3618.2969 | 122.7722 | -0.086975 | 122.6166 | -0.013657 | -0.0028561 | 0.00071565 | -0.012315 | -0.0029864 | -0.0091879 | -0.0063937 | -0.0082093 | 0.012198 | 0.00251 | 0.0013949 | -0.017141 | 0.02243 | -0.0018522 | -0.064087 | 0.073242 | -0.09613 | -0.073242 | 0.045776 | -0.13275 | -0.041199 | 0.036621 | 0.091553 | -0.073242 | 0.054932 | 0.15564 | 0.054932 | 0.14191 | -0.009155 | -122.5433 | -122.6898 | 0.13275 | 0.045776 | -0.045776 | 0.054931 | -0.036621 | 0.013733 | -122.525 | -122.5616 | 0.24261 | 0.22888 | 0.14191 | 0.21515 | 0.12817 | 0.14191 | 0.022888 | 0.22888 | 0.12817 | 0.16937 | 0.16479 | 0.16022 | 0.17853 | -122.7127 | -122.6898 | 0.013733 | 0.14191 | 0.022888 | 0.1236
3620.0625 | 122.7768 | -0.082397 | 122.6257 | -0.021286 | -0.0086239 | -0.00077975 | -0.016374 | 0.001286 | -0.010683 | -0.0059665 | -0.0051575 | 0.0092072 | 0.0050736 | -0.010781 | -0.018637 | 0.022217 | -0.0014248 | -0.036621 | 0.018311 | -0.086975 | 0.018311 | 0.16479 | -0.013733 | 0.045776 | 0.11902 | 0.045776 | -0.068665 | 0.054932 | 0.21515 | 0.11902 | 0.13275 | -0.004578 | -122.6074 | -122.6074 | 0.24719 | 0.12817 | 0.068664 | 0.13275 | 0.073242 | 0.013732 | -122.58 | -122.5708 | 0.29755 | 0.21515 | 0.20142 | 0.20142 | 0.18768 | 0.25177 | 0.10529 | 0.28381 | 0.1236 | 0.10529 | 0.11444 | 0.10071 | 0.12817 | -122.7127 | -122.6944 | 0.10071 | 0.13733 | 0.045776 | 0.20142
3621.7656 | 122.818 | -0.068665 | 122.6395 | -0.013657 | -0.0062741 | 0.00028845 | -0.017229 | -0.00085021 | -0.010043 | -0.0063937 | -0.0082093 | 0.010702 | 0.00251 | 0.0052401 | -0.018423 | 0.022644 | 7.04e-05 | -0.041199 | 0.032043 | -0.086975 | 0.004578 | 0.16479 | -0.013733 | 0.054932 | 0.15564 | 0.068665 | -0.054932 | 0.07782 | 0.23346 | 0.13733 | 0.14648 | -0.01831 | -122.6074 | -122.6349 | 0.23346 | 0.1236 | 0.054932 | 0.14191 | 0.073242 | 0.013733 | -122.5708 | -122.5616 | 0.30212 | 0.21515 | 0.20599 | 0.20142 | 0.19226 | 0.25177 | 0.091553 | 0.28839 | 0.13275 | 0.11902 | 0.1236 | 0.10071 | 0.13733 | -122.7264 | -122.6944 | 0.073243 | 0.14649 | 0.027466 | 0.22431
3623.5312 | 122.7951 | -0.064087 | 122.6303 | -0.013657 | -0.0037107 | 0.0017837 | -0.013597 | 0.0019268 | -0.0096151 | -0.0057529 | -0.0082093 | 0.01113 | 0.004219 | 0.00096772 | -0.019064 | 0.023071 | -0.004202 | -0.009155 | 0.027466 | -0.064087 | 0.013733 | 0.12817 | -0.068665 | 0.022888 | 0.1236 | 0.041199 | -0.054932 | 0.086975 | 0.19226 | 0.091553 | 0.13733 | 0 | -122.6028 | -122.6166 | 0.19226 | 0.086975 | -0.004578 | 0.086975 | -0.004578 | 0.009155 | -122.5891 | -122.5433 | 0.25635 | 0.20142 | 0.15564 | 0.19226 | 0.14649 | 0.19226 | 0.07782 | 0.24719 | 0.14191 | 0.091553 | 0.096131 | 0.091553 | 0.10529 | -122.6944 | -122.6852 | 0.07782 | 0.15106 | 0.054932 | 0.18768
3625.2188 | 122.6624 | -0.10986 | 122.6807 | -0.0060272 | -0.0058469 | -0.0014205 | -0.013811 | -0.0019184 | -0.011111 | -0.0081027 | -0.0021057 | 0.013693 | 0.0016556 | 0.00011332 | -0.018209 | 0.020721 | -0.0005704 | -0.10529 | 0.068665 | -0.12817 | -0.11444 | 0.013733 | -0.11902 | -0.054932 | -0.041199 | 0.10071 | -0.10071 | -0.064087 | 0.068665 | -0.041199 | 0.041199 | -0.018311 | -122.612 | -122.7951 | 0.1236 | 0.054931 | -0.009156 | 0.073242 | 0.009155 | 0.009155 | -122.58 | -122.7448 | 0.17853 | 0.15106 | 0.068664 | 0.14191 | 0.059509 | 0.14191 | 0.013733 | 0.16937 | 0.036621 | 0.19684 | 0.20142 | 0.17853 | 0.21057 | -122.8088 | -122.7814 | -0.004578 | 0.045776 | 0.004577 | 0.068664
3626.9844 | 122.7036 | -0.086975 | 122.6624 | -0.013657 | -0.0047787 | 0.0017837 | -0.013811 | -0.00020941 | -0.0094015 | -0.0051121 | -0.0051575 | 0.012625 | 0.003151 | -0.00010048 | -0.015646 | 0.015595 | 0.0024204 | -0.032043 | 0.050354 | -0.11444 | -0.050354 | 0.068665 | -0.086975 | -0.027466 | 0.059509 | 0.091553 | -0.086975 | 0.013733 | 0.1236 | 0.018311 | 0.082397 | -0.027466 | -122.612 | -122.7127 | 0.15564 | 0.059509 | 0 | 0.086975 | 0.027466 | 0 | -122.5708 | -122.6486 | 0.21057 | 0.16937 | 0.10529 | 0.16937 | 0.10529 | 0.18311 | 0.064087 | 0.21057 | 0.10071 | 0.16479 | 0.17853 | 0.13733 | 0.17853 | -122.7768 | -122.7493 | 0.036621 | 0.10071 | 0.054932 | 0.14648
3628.75 | 122.7173 | -0.10529 | 122.6395 | -0.013657 | -0.0075559 | 0.00050205 | -0.012743 | -0.0042682 | -0.0091879 | -0.0019077 | -0.0021057 | 0.011557 | 0.003151 | 0.0026767 | -0.016073 | 0.02179 | -0.0014248 | -0.059509 | 0.064087 | -0.10529 | -0.073242 | 0.045776 | -0.10986 | -0.045776 | 0.018311 | 0.10071 | -0.086975 | 0.009155 | 0.11444 | 0.018311 | 0.09613 | 0 | -122.5754 | -122.7127 | 0.15106 | 0.05951 | -0.004577 | 0.05951 | -0.004577 | 0.018311 | -122.5388 | -122.6303 | 0.21973 | 0.20142 | 0.1236 | 0.1831 | 0.10529 | 0.15106 | 0.032044 | 0.20142 | 0.09613 | 0.16937 | 0.18768 | 0.16937 | 0.20599 | -122.7448 | -122.7264 | 0.032044 | 0.11444 | 0.045777 | 0.1236
3630.5156 | 122.6669 | -0.1236 | 122.6761 | -0.021286 | -0.0090513 | -0.00035255 | -0.016588 | 0.001286 | -0.01282 | -0.0031895 | -0.0051575 | 0.010489 | 0.0012282 | 0.0033175 | -0.017996 | 0.023926 | -0.0022794 | -0.11902 | 0.050354 | -0.13733 | -0.1236 | 0.022888 | -0.13733 | -0.045776 | -0.073242 | 0.10071 | -0.09613 | -0.07782 | 0.064087 | -0.032043 | 0.032043 | -0.013733 | -122.6257 | -122.7997 | 0.14648 | 0.07782 | -0.013733 | 0.091553 | 0 | 0.027466 | -122.5754 | -122.7539 | 0.18768 | 0.15564 | 0.091553 | 0.12817 | 0.064087 | 0.16022 | 0.013733 | 0.16022 | 0.01831 | 0.18768 | 0.19684 | 0.17395 | 0.2243 | -122.8134 | -122.7722 | 0 | 0.045776 | 0.004577 | 0.050354
3632.2812 | 122.7859 | -0.045776 | 122.6624 | -0.021286 | -0.0020017 | 0.0013565 | -0.016801 | -0.0025592 | -0.01047 | -0.0059665 | -0.0051575 | 0.010062 | 0.0022964 | -0.0039457 | -0.01885 | 0.022644 | -0.0033474 | -0.018311 | 0.018311 | -0.082397 | 0.018311 | 0.14191 | -0.054932 | 0.036621 | 0.1236 | 0.064087 | -0.050354 | 0.064087 | 0.20599 | 0.091553 | 0.13733 | -0.036621 | -122.644 | -122.644 | 0.18768 | 0.082397 | -0.009156 | 0.11902 | 0.027465 | -0.004578 | -122.5983 | -122.5983 | 0.25177 | 0.18311 | 0.13733 | 0.18768 | 0.14191 | 0.2243 | 0.10071 | 0.25635 | 0.11444 | 0.10071 | 0.11444 | 0.064087 | 0.10986 | -122.7448 | -122.7127 | 0.064087 | 0.10986 | 0.027465 | 0.16937
3634.0469 | 122.7539 | -0.07782 | 122.6761 | -0.021286 | -0.0075559 | -0.00077975 | -0.016161 | -0.0034136 | -0.011538 | -0.0046847 | -0.0051575 | 0.012411 | 0.0027236 | -0.0069363 | -0.019705 | 0.021576 | -0.0029202 | -0.050354 | 0.018311 | -0.068665 | 0.018311 | 0.15106 | -0.009155 | 0.059509 | 0.09613 | 0.068665 | -0.050354 | 0.027466 | 0.17853 | 0.07782 | 0.11902 | 0.009155 | -122.6578 | -122.6578 | 0.22888 | 0.13733 | 0.068665 | 0.12817 | 0.05951 | 0.027466 | -122.6074 | -122.6486 | 0.25635 | 0.19684 | 0.15564 | 0.16937 | 0.12817 | 0.21973 | 0.086976 | 0.22888 | 0.07782 | 0.086976 | 0.11902 | 0.096131 | 0.14649 | -122.7448 | -122.7264 | 0.096131 | 0.10529 | 0.027466 | 0.17395
3635.8125 | 122.8043 | -0.041199 | 122.6349 | -0.013657 | -0.0017881 | -0.00099335 | -0.012956 | 0.0014996 | -0.0098287 | -0.0051121 | -0.0051575 | 0.010062 | 0.0029372 | -0.0073635 | -0.021841 | 0.023285 | -0.0022794 | -0.018311 | 0.022888 | -0.073242 | 0.009155 | 0.13275 | -0.050354 | 0.041199 | 0.09613 | 0.059509 | -0.045776 | 0.086975 | 0.20142 | 0.091553 | 0.16937 | -0.032043 | -122.612 | -122.6257 | 0.17395 | 0.082398 | -0.009155 | 0.11444 | 0.022888 | -0.004577 | -122.5754 | -122.5479 | 0.24262 | 0.21057 | 0.13275 | 0.21515 | 0.13733 | 0.20599 | 0.082397 | 0.24719 | 0.13275 | 0.09613 | 0.10528 | 0.064087 | 0.10071 | -122.7081 | -122.6807 | 0.050354 | 0.12817 | 0.022888 | 0.13733
3637.5 | 122.699 | -0.11444 | 122.6807 | -0.028916 | -0.0092649 | 0.00028845 | -0.01552 | -0.007259 | -0.011751 | -0.0040439 | -0.0082093 | 0.011343 | 0.0022964 | 0.00011332 | -0.017782 | 0.023926 | 0.0007114 | -0.064087 | 0.045776 | -0.082397 | -0.041199 | 0.068665 | -0.054932 | -0.004578 | 0.018311 | 0.073242 | -0.091553 | -0.041199 | 0.10529 | 0.022888 | 0.059509 | 0.032044 | -122.6349 | -122.7219 | 0.18311 | 0.10986 | 0.059509 | 0.077819 | 0.027465 | 0.022888 | -122.6074 | -122.7219 | 0.21973 | 0.17395 | 0.13733 | 0.15106 | 0.11444 | 0.15106 | 0.041198 | 0.19684 | 0.050354 | 0.12817 | 0.16479 | 0.16022 | 0.18768 | -122.7631 | -122.7722 | 0.073242 | 0.073242 | 0.050354 | 0.13275
3639.2031 | 122.6898 | -0.11902 | 122.6715 | -0.021286 | -0.0020017 | -0.0027023 | -0.012102 | 0.0021406 | -0.012606 | -0.0089573 | -0.0082093 | 0.013052 | 0.0037918 | -0.0028775 | -0.017141 | 0.018372 | -0.000784 | -0.054932 | 0.059509 | -0.10529 | -0.059509 | 0.045776 | -0.12817 | -0.059509 | 0 | 0.10986 | -0.086975 | -0.018311 | 0.073242 | -0.022888 | 0.059509 | 0.013733 | -122.612 | -122.731 | 0.16479 | 0.05951 | -0.009155 | 0.045777 | -0.022888 | 0.032044 | -122.5616 | -122.6898 | 0.19226 | 0.17853 | 0.096131 | 0.14648 | 0.064087 | 0.15106 | 0.045777 | 0.16022 | 0.068664 | 0.16479 | 0.19684 | 0.17853 | 0.22888 | -122.7768 | -122.7585 | 0.05951 | 0.10071 | 0.064087 | 0.11902
3640.9688 | 122.818 | -0.068665 | 122.6486 | -0.0060272 | -0.0071285 | 0.0019975 | -0.015947 | 0.0036358 | -0.011751 | -0.0031895 | -0.0021057 | 0.0092072 | 0.0022964 | -0.0054409 | -0.017568 | 0.021362 | -0.0014248 | -0.059509 | 0.045776 | -0.09613 | -0.009155 | 0.13275 | -0.036621 | 0.059509 | 0.091553 | 0.050354 | -0.073242 | 0.068665 | 0.21973 | 0.10529 | 0.14648 | -0.027465 | -122.6028 | -122.6578 | 0.20142 | 0.12817 | 0.032044 | 0.15564 | 0.059509 | -0.004577 | -122.5983 | -122.58 | 0.28839 | 0.21515 | 0.17395 | 0.21973 | 0.17853 | 0.22888 | 0.086975 | 0.29297 | 0.14191 | 0.14191 | 0.1236 | 0.11444 | 0.11902 | -122.7448 | -122.7219 | 0.05951 | 0.13733 | 0.009156 | 0.16022
3642.7188 | 122.6898 | -0.11902 | 122.6715 | -0.0060272 | -0.0084103 | -0.00056615 | -0.016801 | 0.0036358 | -0.012392 | -0.0055393 | -0.0021057 | 0.011557 | 0.0016556 | -0.0013821 | -0.017782 | 0.022644 | 0.0032748 | -0.059509 | 0.027466 | -0.07782 | -0.050354 | 0.086975 | -0.064087 | 0.009155 | 0.022888 | 0.091553 | -0.091553 | -0.032043 | 0.086975 | 0.009155 | 0.050354 | 0.041199 | -122.644 | -122.7219 | 0.20599 | 0.12817 | 0.054932 | 0.086975 | 0.013733 | 0.027466 | -122.58 | -122.7036 | 0.20599 | 0.16937 | 0.12817 | 0.14191 | 0.10071 | 0.16479 | 0.027466 | 0.17853 | 0.05951 | 0.10529 | 0.18311 | 0.14649 | 0.21057 | -122.7493 | -122.7631 | 0.068665 | 0.086976 | 0.05951 | 0.14191
3644.4688 | 122.6715 | -0.1236 | 122.699 | -0.013657 | -0.0090513 | -0.0014205 | -0.01082 | -0.002132 | -0.012606 | -0.0070347 | -0.0082093 | 0.013266 | -5.3368e-05 | 0.00032692 | -0.019491 | 0.020935 | -0.002493 | -0.10071 | 0.059509 | -0.10986 | -0.11902 | 0.009155 | -0.12817 | -0.059509 | -0.036621 | 0.10529 | -0.10986 | -0.068665 | 0.064087 | -0.013733 | 0.041199 | 0.013733 | -122.6395 | -122.818 | 0.13275 | 0.064087 | -0.004578 | 0.050354 | -0.018311 | 0.013733 | -122.5937 | -122.7676 | 0.18768 | 0.16479 | 0.10986 | 0.15106 | 0.09613 | 0.11902 | -0.009156 | 0.17395 | 0.041198 | 0.16937 | 0.21515 | 0.1831 | 0.22888 | -122.8088 | -122.8088 | 0.004577 | 0.054931 | 0.022888 | 0.086975
3646.2344 | 122.7173 | -0.11444 | 122.699 | -0.013657 | -0.0067013 | -0.0024887 | -0.01552 | 0.0021406 | -0.011538 | -0.0072483 | -0.0051575 | 0.01113 | 0.001442 | 0.0045993 | -0.017996 | 0.023071 | -0.0018522 | -0.10071 | 0.059509 | -0.11444 | -0.11444 | 0.004578 | -0.14191 | -0.045776 | -0.041199 | 0.10529 | -0.091553 | -0.054932 | 0.064087 | -0.004578 | 0.045776 | 0 | -122.6395 | -122.8134 | 0.11902 | 0.068665 | -0.027466 | 0.068665 | -0.027466 | 0.022888 | -122.5937 | -122.7539 | 0.17853 | 0.16022 | 0.10986 | 0.13733 | 0.086975 | 0.11902 | 0 | 0.15564 | 0.036621 | 0.17395 | 0.19684 | 0.17395 | 0.21973 | -122.8134 | -122.7905 | 0 | 0.059509 | 0.013733 | 0.073242
3647.9375 | 122.8043 | -0.073242 | 122.6532 | -0.013657 | -0.0020017 | 0.0013565 | -0.014452 | 0.0040632 | -0.010043 | -0.0061801 | -0.0021057 | 0.0094208 | 0.0016556 | -0.0090725 | -0.017355 | 0.023285 | -0.0033474 | -0.009155 | 0.013733 | -0.064087 | 0.013733 | 0.14648 | -0.059509 | 0.036621 | 0.1236 | 0.068665 | -0.068665 | 0.07782 | 0.19226 | 0.082397 | 0.13275 | 0.009155 | -122.6395 | -122.6395 | 0.21973 | 0.10986 | 0.013733 | 0.10071 | 0.004578 | 0.004577 | -122.5845 | -122.5754 | 0.2655 | 0.20599 | 0.15564 | 0.20142 | 0.15106 | 0.21057 | 0.07782 | 0.26093 | 0.14649 | 0.07782 | 0.13733 | 0.086975 | 0.14191 | -122.7173 | -122.7219 | 0.086975 | 0.15106 | 0.064087 | 0.19684
3649.7031 | 122.7585 | -0.091553 | 122.6532 | -0.021286 | -0.0062741 | -0.0022751 | -0.015306 | -0.0010638 | -0.012179 | -0.0057529 | -0.0051575 | 0.009848 | 0.004219 | 0.0041721 | -0.017996 | 0.021149 | -0.0067654 | -0.082397 | 0.027466 | -0.086975 | -0.050354 | 0.059509 | -0.073242 | 0 | 0.027466 | 0.068665 | -0.07782 | 0.004578 | 0.13275 | 0.045776 | 0.09613 | 0.004578 | -122.6257 | -122.7036 | 0.15106 | 0.091553 | 0.018311 | 0.086975 | 0.013733 | 0.013733 | -122.5845 | -122.6486 | 0.2243 | 0.18768 | 0.13733 | 0.17395 | 0.1236 | 0.14648 | 0.036621 | 0.21057 | 0.082398 | 0.11444 | 0.14649 | 0.11902 | 0.16022 | -122.7402 | -122.731 | 0.041199 | 0.096131 | 0.009156 | 0.11902
3651.4844 | 122.6807 | -0.10071 | 122.6624 | -0.0060272 | -0.0041379 | 0.00092925 | -0.011675 | 0.0053448 | -0.0096151 | -0.0023349 | -0.0082093 | 0.013693 | 0.0022964 | -0.0015957 | -0.017996 | 0.021362 | 7.04e-05 | -0.07782 | 0.054932 | -0.10071 | -0.1236 | -0.004578 | -0.17853 | -0.086975 | -0.027466 | 0.086975 | -0.09613 | -0.045776 | 0.054932 | -0.041199 | 0.036621 | 0 | -122.6074 | -122.7859 | 0.09613 | 0.013733 | -0.07782 | 0.013733 | -0.07782 | 0.004578 | -122.5754 | -122.7081 | 0.15564 | 0.13733 | 0.059509 | 0.13275 | 0.054931 | 0.09613 | -0.022888 | 0.15106 | 0.050354 | 0.15564 | 0.1831 | 0.15564 | 0.18768 | -122.7631 | -122.7585 | -0.022888 | 0.054932 | 0.022888 | 0.073242
3653.25 | 122.7951 | -0.059509 | 122.6624 | -0.0060272 | -0.0020017 | 0.0022111 | -0.012102 | -0.00020941 | -0.0089743 | -0.0048985 | -0.011261 | 0.010062 | -0.00048057 | 0.0028903 | -0.017355 | 0.02179 | 0.0019932 | -0.082397 | 0.050354 | -0.10529 | -0.073242 | 0.045776 | -0.15106 | -0.027466 | 0.054932 | 0.07782 | -0.073242 | 0.050354 | 0.15564 | 0.054932 | 0.13275 | -0.045777 | -122.612 | -122.7356 | 0.10528 | 0.032043 | -0.091553 | 0.07782 | -0.045776 | -0.013733 | -122.5845 | -122.612 | 0.21515 | 0.19226 | 0.11444 | 0.20599 | 0.12817 | 0.15106 | 0.032044 | 0.22888 | 0.1236 | 0.15564 | 0.15106 | 0.10986 | 0.13733 | -122.7676 | -122.7356 | -0.013733 | 0.10986 | -0.022888 | 0.11444
3654.9531 | 122.7585 | -0.073242 | 122.6807 | -0.013657 | -0.0069149 | -0.00035255 | -0.015093 | -0.00020941 | -0.0085471 | -0.0053257 | -0.0051575 | 0.010489 | 0.0016556 | -0.0039457 | -0.017141 | 0.020935 | -0.0016384 | -0.064087 | 0.022888 | -0.073242 | -0.032043 | 0.09613 | -0.086975 | 0.018311 | 0.054932 | 0.054932 | -0.073242 | 0 | 0.13733 | 0.045776 | 0.10071 | 0 | -122.6578 | -122.7127 | 0.16937 | 0.091553 | -0.013733 | 0.091553 | -0.013733 | 0 | -122.6257 | -122.6807 | 0.21057 | 0.17395 | 0.11902 | 0.17395 | 0.11902 | 0.16937 | 0.041199 | 0.21057 | 0.073242 | 0.09613 | 0.12817 | 0.09613 | 0.12817 | -122.7539 | -122.7539 | 0.041199 | 0.073242 | 0.009155 | 0.12817
3656.7344 | 122.7905 | -0.07782 | 122.6761 | -0.028916 | -0.0039243 | 0.0019975 | -0.015947 | 0.00064519 | -0.0098287 | -0.0078891 | -0.0051575 | 0.010275 | 0.00058743 | -0.0011685 | -0.017996 | 0.021149 | -0.003561 | -0.032043 | 0.022888 | -0.059509 | 0.018311 | 0.16479 | -0.054932 | 0.013733 | 0.14191 | 0.064087 | -0.041199 | 0.059509 | 0.17853 | 0.07782 | 0.13275 | 0.018311 | -122.6532 | -122.6578 | 0.24261 | 0.091553 | 0.022888 | 0.073242 | 0.004577 | 0.036621 | -122.612 | -122.6166 | 0.25635 | 0.21057 | 0.15564 | 0.17395 | 0.11902 | 0.2243 | 0.07782 | 0.21973 | 0.10071 | 0.082397 | 0.10529 | 0.10071 | 0.14191 | -122.7356 | -122.7173 | 0.096131 | 0.13733 | 0.045777 | 0.21973
3658.4375 | 122.699 | -0.11444 | 122.6761 | -0.021286 | -0.0049923 | -0.00013895 | -0.01082 | 0.00085879 | -0.010683 | -0.0044711 | -0.0051575 | 0.012625 | 0.0022964 | 0.0011813 | -0.015005 | 0.023926 | -0.0012112 | -0.10071 | 0.059509 | -0.11902 | -0.13275 | -0.041199 | -0.19684 | -0.10529 | -0.054932 | 0.10529 | -0.086975 | -0.041199 | 0.045776 | -0.054932 | 0.041199 | -0.004578 | -122.6166 | -122.8088 | 0.073242 | 0.009155 | -0.082397 | 0.013733 | -0.077819 | 0.027466 | -122.5708 | -122.7173 | 0.16022 | 0.15564 | 0.059509 | 0.12817 | 0.032043 | 0.07782 | -0.013732 | 0.13275 | 0.045776 | 0.17853 | 0.19226 | 0.17395 | 0.21973 | -122.7951 | -122.7631 | -0.01831 | 0.073242 | 0.013733 | 0.059509
3660.1875 | 122.6761 | -0.10529 | 122.6898 | -0.028916 | -0.0024289 | 0.00071565 | -0.014238 | 0.00085879 | -0.0098287 | -0.0042575 | -0.0051575 | 0.011557 | 0.0029372 | 0.0031039 | -0.017782 | 0.022644 | -0.000784 | -0.064087 | 0.064087 | -0.10529 | -0.10071 | 0.018311 | -0.17395 | -0.086975 | -0.045776 | 0.10529 | -0.09613 | -0.045776 | 0.059509 | -0.045776 | 0.027466 | 0 | -122.6257 | -122.7905 | 0.1236 | 0.018311 | -0.068664 | 0.018311 | -0.068664 | 0.009156 | -122.5845 | -122.7356 | 0.16479 | 0.13275 | 0.05951 | 0.1236 | 0.050354 | 0.1236 | 0.004578 | 0.15564 | 0.050354 | 0.16937 | 0.20142 | 0.16937 | 0.21057 | -122.7951 | -122.7859 | 0.004578 | 0.05951 | 0.041199 | 0.05951
3661.8906 | 122.6852 | -0.12817 | 122.6807 | -0.013657 | -0.0067013 | 0.00028845 | -0.013597 | -0.0010638 | -0.011538 | -0.0051121 | -0.0082093 | 0.012411 | 0.0044326 | -0.00074128 | -0.016928 | 0.022217 | 0.0004978 | -0.12817 | 0.064087 | -0.11902 | -0.11902 | 0 | -0.11444 | -0.059509 | -0.045776 | 0.10071 | -0.091553 | -0.054932 | 0.073242 | -0.018311 | 0.041199 | 0.009155 | -122.6166 | -122.7997 | 0.12817 | 0.068665 | 0.013733 | 0.05951 | 0.004578 | 0.036621 | -122.58 | -122.7356 | 0.20142 | 0.16937 | 0.10986 | 0.13275 | 0.073242 | 0.11902 | 0 | 0.16479 | 0.036621 | 0.18311 | 0.19226 | 0.19226 | 0.22888 | -122.7997 | -122.7722 | 0.009155 | 0.073242 | 0 | 0.082398
3663.6562 | 122.8134 | -0.073242 | 122.6532 | -0.028916 | -0.0039243 | 0.0032791 | -0.013811 | -0.0010638 | -0.01047 | -0.0023349 | -0.0051575 | 0.010916 | 0.00016023 | -0.00052768 | -0.018209 | 0.023071 | -0.0027066 | -0.013733 | 0.013733 | -0.054932 | 0 | 0.15106 | -0.045776 | 0.032043 | 0.11902 | 0.045776 | -0.054932 | 0.050354 | 0.19684 | 0.07782 | 0.14648 | 0.01831 | -122.6395 | -122.6532 | 0.2243 | 0.10529 | 0.027466 | 0.086975 | 0.009156 | 0.01831 | -122.6074 | -122.6028 | 0.27008 | 0.21973 | 0.15106 | 0.20142 | 0.13275 | 0.20599 | 0.054932 | 0.25177 | 0.10529 | 0.068665 | 0.10071 | 0.086975 | 0.11902 | -122.7081 | -122.7081 | 0.073242 | 0.1236 | 0.059509 | 0.19226
3665.4062 | 122.7539 | -0.086975 | 122.644 | -0.021286 | -0.0056333 | -0.00099335 | -0.015947 | 4.192e-06 | -0.010256 | -0.0029759 | -0.0021057 | 0.0094208 | -0.00069437 | -0.0052273 | -0.020132 | 0.022644 | -0.0001432 | -0.07782 | 0.032043 | -0.086975 | -0.059509 | 0.082397 | -0.086975 | 0 | 0.022888 | 0.064087 | -0.086975 | 0.009155 | 0.14648 | 0.059509 | 0.091553 | 0 | -122.612 | -122.7036 | 0.16937 | 0.086975 | 0 | 0.086975 | 0 | 0 | -122.58 | -122.6349 | 0.23346 | 0.17853 | 0.14648 | 0.17853 | 0.14648 | 0.16937 | 0.027466 | 0.23346 | 0.09613 | 0.11902 | 0.15106 | 0.11902 | 0.15106 | -122.731 | -122.731 | 0.027466 | 0.09613 | 0.009155 | 0.10986
3667.1719 | 122.7722 | -0.082397 | 122.6578 | -0.013657 | -0.0060605 | -0.00077975 | -0.014879 | -0.0012774 | -0.012606 | -0.0042575 | -0.0021057 | 0.0094208 | 0.0020828 | -0.0024503 | -0.020132 | 0.022003 | -0.000784 | -0.054932 | 0.018311 | -0.10071 | -0.036621 | 0.10986 | -0.073242 | 0.013733 | 0.054932 | 0.064087 | -0.082397 | 0.013733 | 0.14648 | 0.045776 | 0.10529 | -0.018311 | -122.6395 | -122.6944 | 0.19226 | 0.09613 | 0.009155 | 0.11444 | 0.027466 | 0 | -122.5937 | -122.644 | 0.22888 | 0.18768 | 0.12817 | 0.18768 | 0.12817 | 0.21057 | 0.064087 | 0.22888 | 0.09613 | 0.11902 | 0.14648 | 0.10071 | 0.14648 | -122.7585 | -122.7402 | 0.045776 | 0.09613 | 0.027465 | 0.13733
3668.875 | 122.6898 | -0.10986 | 122.7081 | -0.013657 | -0.0077695 | -0.0022751 | -0.015093 | 0.00085879 | -0.010256 | -0.0023349 | -0.0051575 | 0.013693 | 0.0018692 | -0.0013821 | -0.016714 | 0.024353 | -0.0031338 | -0.11444 | 0.064087 | -0.1236 | -0.10529 | 0.004578 | -0.12817 | -0.059509 | -0.054932 | 0.10986 | -0.10071 | -0.064087 | 0.054932 | -0.027466 | 0.041199 | -0.013733 | -122.644 | -122.8134 | 0.11444 | 0.050354 | -0.018311 | 0.064087 | -0.004578 | 0.009155 | -122.5983 | -122.7722 | 0.16479 | 0.15106 | 0.082397 | 0.14191 | 0.073242 | 0.12817 | 0.01831 | 0.15564 | 0.036621 | 0.18768 | 0.21057 | 0.17395 | 0.21973 | -122.8317 | -122.8088 | 0.004577 | 0.045776 | -0.004578 | 0.054931
3670.6406 | 122.8088 | -0.059509 | 122.6944 | -0.0060272 | -0.0081967 | -0.00035255 | -0.016161 | -0.001491 | -0.012606 | -0.0038303 | -0.0021057 | 0.010916 | -0.0011216 | -0.0030911 | -0.019491 | 0.020508 | -0.0063382 | -0.032043 | 0.027466 | -0.073242 | 0.018311 | 0.16937 | -0.013733 | 0.068665 | 0.10986 | 0.050354 | -0.064087 | 0.068665 | 0.21057 | 0.11902 | 0.13275 | -0.013733 | -122.6669 | -122.6761 | 0.22888 | 0.12817 | 0.045776 | 0.14191 | 0.059509 | -0.004578 | -122.644 | -122.6257 | 0.27008 | 0.19226 | 0.17853 | 0.19684 | 0.18311 | 0.24261 | 0.091553 | 0.27466 | 0.13275 | 0.10071 | 0.11444 | 0.086975 | 0.10986 | -122.7676 | -122.7585 | 0.07782 | 0.12817 | 0.027466 | 0.16937
3672.4062 | 122.699 | -0.10986 | 122.6807 | -0.013657 | -0.0017881 | 0.0017837 | -0.011888 | 0.0014996 | -0.011324 | -0.0046847 | -0.0051575 | 0.012839 | 0.0020828 | -0.00052768 | -0.019491 | 0.024353 | -0.0005704 | -0.082397 | 0.091553 | -0.11444 | -0.13733 | -0.050354 | -0.19684 | -0.10986 | -0.050354 | 0.082397 | -0.091553 | -0.036621 | 0.041199 | -0.068665 | 0.045776 | -0.004578 | -122.5891 | -122.818 | 0.059509 | 0 | -0.086975 | 0.004578 | -0.082397 | 0.01831 | -122.5983 | -122.7173 | 0.15106 | 0.15564 | 0.041198 | 0.13733 | 0.022888 | 0.064087 | -0.022888 | 0.13275 | 0.054932 | 0.20599 | 0.17395 | 0.20142 | 0.19226 | -122.7951 | -122.7722 | -0.027466 | 0.073242 | 0.027466 | 0.059509
3674.1562 | 122.699 | -0.10529 | 122.7081 | -0.021286 | -0.0062741 | -0.0018479 | -0.015093 | 0.00021799 | -0.01346 | -0.0031895 | -0.011261 | 0.010275 | 0.0018692 | -0.0018093 | -0.018423 | 0.024139 | 7.04e-05 | -0.09613 | 0.07782 | -0.10986 | -0.11444 | -0.009155 | -0.14648 | -0.073242 | -0.045776 | 0.091553 | -0.10529 | -0.059509 | 0.064087 | -0.027466 | 0.041199 | -0.004577 | -122.6303 | -122.8226 | 0.096131 | 0.032044 | -0.041198 | 0.036621 | -0.036621 | 0 | -122.6166 | -122.7676 | 0.16937 | 0.14649 | 0.07782 | 0.14649 | 0.07782 | 0.10071 | -0.004578 | 0.16937 | 0.045777 | 0.18768 | 0.19684 | 0.18311 | 0.19684 | -122.818 | -122.8134 | -0.009155 | 0.045777 | 0.009156 | 0.05951
3675.8594 | 122.7859 | -0.07782 | 122.6669 | -0.013657 | -0.0037107 | 0.00050205 | -0.016801 | 0.0044904 | -0.013247 | -0.0059665 | -0.0082093 | 0.01113 | 0.001442 | -0.0056547 | -0.01885 | 0.021576 | -0.0044156 | -0.068665 | 0.032043 | -0.10071 | -0.054932 | 0.068665 | -0.07782 | 0.004578 | 0.022888 | 0.054932 | -0.064087 | 0.018311 | 0.15564 | 0.032043 | 0.086975 | -0.022888 | -122.6349 | -122.7219 | 0.14649 | 0.082398 | 0 | 0.10529 | 0.022888 | 0.013733 | -122.612 | -122.6486 | 0.23346 | 0.16479 | 0.10986 | 0.15106 | 0.09613 | 0.16937 | 0.045776 | 0.21973 | 0.082398 | 0.13275 | 0.11902 | 0.10986 | 0.13275 | -122.7676 | -122.731 | 0.022888 | 0.096131 | 0.009155 | 0.10071
3677.625 | 122.7127 | -0.1236 | 122.6944 | -0.0060272 | -0.0041379 | 0.00050205 | -0.011034 | 0.0017132 | -0.0087607 | -0.0055393 | -0.0021057 | 0.011557 | 0.0029372 | 0.0069491 | -0.018423 | 0.022217 | -0.004202 | -0.091553 | 0.068665 | -0.11902 | -0.12817 | -0.036621 | -0.17853 | -0.082397 | -0.050354 | 0.10986 | -0.10529 | -0.041199 | 0.050354 | -0.059509 | 0.041199 | 0.004577 | -122.6257 | -122.8226 | 0.086975 | 0.041199 | -0.054932 | 0.036622 | -0.059509 | 0.01831 | -122.5845 | -122.7356 | 0.17395 | 0.16479 | 0.064087 | 0.14649 | 0.045777 | 0.082398 | -0.009155 | 0.15564 | 0.064087 | 0.18768 | 0.21515 | 0.19226 | 0.23346 | -122.8134 | -122.7997 | -0.004578 | 0.082397 | 0.032043 | 0.073242
3679.3125 | 122.7036 | -0.11444 | 122.7081 | 0.0016023 | -0.0090513 | -0.00013895 | -0.014665 | 0.00043159 | -0.013033 | -0.0070347 | -0.0051575 | 0.011771 | 0.0029372 | -0.0024503 | -0.017996 | 0.020721 | -0.0012112 | -0.10529 | 0.068665 | -0.10986 | -0.1236 | 0.013733 | -0.11902 | -0.050354 | -0.059509 | 0.11444 | -0.10071 | -0.064087 | 0.068665 | -0.027466 | 0.032043 | 0.004578 | -122.6395 | -122.8317 | 0.12817 | 0.064087 | -0.004578 | 0.059509 | -0.009156 | 0.013733 | -122.5937 | -122.7722 | 0.18311 | 0.14648 | 0.086975 | 0.13275 | 0.073242 | 0.1236 | -0.013733 | 0.16937 | 0.036621 | 0.17853 | 0.21515 | 0.18311 | 0.22888 | -122.818 | -122.8088 | -0.009155 | 0.050354 | 0.009155 | 0.054932
3681.0781 | 122.8363 | -0.054932 | 122.6715 | -0.013657 | -0.0092649 | -0.0014205 | -0.015947 | 0.001286 | -0.012179 | -0.0057529 | -0.0082093 | 0.0085662 | 0.0033646 | -0.0041593 | -0.017141 | 0.02243 | -0.0009976 | -0.036621 | 0.027466 | -0.09613 | 0.036621 | 0.17853 | 0.013733 | 0.064087 | 0.10986 | 0.064087 | -0.054932 | 0.068665 | 0.21515 | 0.12817 | 0.13275 | -0.041198 | -122.644 | -122.6349 | 0.23346 | 0.11902 | 0.068665 | 0.16022 | 0.10986 | 0 | -122.6074 | -122.6028 | 0.27008 | 0.18768 | 0.18311 | 0.18768 | 0.18311 | 0.27466 | 0.13275 | 0.27008 | 0.1236 | 0.1236 | 0.11902 | 0.082398 | 0.11902 | -122.7676 | -122.7264 | 0.091553 | 0.1236 | 0.018311 | 0.16479
3682.7812 | 122.7814 | -0.09613 | 122.6852 | -0.021286 | -0.0054197 | 0.0011429 | -0.013811 | -0.0023456 | -0.0096151 | -0.0046847 | -0.0051575 | 0.011343 | 0.00080103 | 0.00096772 | -0.017355 | 0.020294 | -0.0022794 | -0.073242 | 0.036621 | -0.091553 | -0.041199 | 0.059509 | -0.082397 | 0 | 0.045776 | 0.064087 | -0.073242 | 0.009155 | 0.12817 | 0.050354 | 0.09613 | 0.004577 | -122.6486 | -122.7264 | 0.15564 | 0.09613 | 0.013733 | 0.091553 | 0.009156 | 0.022888 | -122.6212 | -122.6761 | 0.2243 | 0.19226 | 0.14648 | 0.16937 | 0.1236 | 0.15106 | 0.050354 | 0.20142 | 0.082397 | 0.12817 | 0.13733 | 0.13275 | 0.16022 | -122.7768 | -122.7585 | 0.054931 | 0.10528 | 0.022888 | 0.14191
3684.5312 | 122.8363 | -0.082397 | 122.6715 | -0.0060272 | -0.0056333 | 0.00028845 | -0.014665 | 4.192e-06 | -0.01047 | -0.0040439 | -0.0051575 | 0.011557 | 0.0033646 | -0.0026639 | -0.019705 | 0.020721 | -0.0018522 | -0.059509 | 0.036621 | -0.082397 | -0.013733 | 0.09613 | -0.045776 | 0.036621 | 0.09613 | 0.045776 | -0.068665 | 0.050354 | 0.18768 | 0.11444 | 0.13733 | 0 | -122.6349 | -122.6852 | 0.17853 | 0.11902 | 0.036621 | 0.11902 | 0.036621 | 0.013732 | -122.6257 | -122.6212 | 0.27008 | 0.21973 | 0.19684 | 0.20599 | 0.18311 | 0.17853 | 0.068664 | 0.25635 | 0.11902 | 0.11902 | 0.11444 | 0.11902 | 0.12817 | -122.7539 | -122.7402 | 0.068664 | 0.13275 | 0.022888 | 0.17853
3686.2344 | 122.8363 | -0.045776 | 122.6578 | -0.028916 | -0.0032833 | 0.0019975 | -0.014879 | 0.0034222 | -0.0083335 | -0.0083163 | -0.0021057 | 0.010916 | 0.0020828 | -0.00074128 | -0.019918 | 0.023499 | -0.0020658 | 0.004578 | 0.027466 | -0.086975 | 0 | 0.13733 | -0.064087 | 0.027466 | 0.11902 | 0.045776 | -0.054932 | 0.086975 | 0.18768 | 0.086975 | 0.14648 | -0.041199 | -122.6303 | -122.6578 | 0.18311 | 0.073242 | -0.018311 | 0.11444 | 0.022888 | -0.009156 | -122.612 | -122.5708 | 0.23346 | 0.19226 | 0.13275 | 0.20142 | 0.14191 | 0.2243 | 0.086975 | 0.24261 | 0.14191 | 0.11444 | 0.10071 | 0.073242 | 0.091552 | -122.7448 | -122.7127 | 0.045776 | 0.13275 | 0.050354 | 0.16479
3688 | 122.8455 | -0.064087 | 122.6532 | -0.0060272 | -0.0092649 | -0.00035255 | -0.016161 | -0.0017048 | -0.010683 | -0.0036167 | -0.011261 | 0.009848 | 0.0012282 | 0.0013949 | -0.019705 | 0.021576 | -0.0003568 | -0.013733 | 0.036621 | -0.086975 | 0.027466 | 0.18768 | 0.004578 | 0.082397 | 0.13275 | 0.054932 | -0.068665 | 0.059509 | 0.22888 | 0.11444 | 0.15106 | -0.022888 | -122.6166 | -122.6257 | 0.25177 | 0.14648 | 0.068665 | 0.16937 | 0.091553 | -0.004578 | -122.5983 | -122.5937 | 0.29297 | 0.21515 | 0.17853 | 0.21973 | 0.18311 | 0.27466 | 0.11444 | 0.29755 | 0.12817 | 0.1236 | 0.1236 | 0.10071 | 0.11902 | -122.7402 | -122.7219 | 0.091553 | 0.1236 | 0.050354 | 0.19684
3689.7656 | 122.7539 | -0.10071 | 122.7127 | -0.021286 | -0.0030697 | -0.0014205 | -0.011461 | 0.00085879 | -0.011111 | -0.0076755 | -0.0051575 | 0.011557 | 0.0018692 | 0.0031039 | -0.018209 | 0.016022 | -0.004202 | -0.036621 | 0.054932 | -0.10529 | -0.036621 | 0.073242 | -0.10071 | -0.036621 | 0.059509 | 0.091553 | -0.073242 | 0.018311 | 0.12817 | 0.018311 | 0.07782 | -0.004578 | -122.6578 | -122.7493 | 0.17395 | 0.064087 | 0 | 0.068665 | 0.004578 | 0.027466 | -122.6212 | -122.6944 | 0.22888 | 0.17853 | 0.11902 | 0.15106 | 0.091553 | 0.17853 | 0.068665 | 0.20142 | 0.091553 | 0.16022 | 0.16479 | 0.15564 | 0.19226 | -122.818 | -122.7859 | 0.064087 | 0.11902 | 0.064087 | 0.16022
3691.4688 | 122.7036 | -0.10986 | 122.699 | -0.021286 | -0.0034971 | 0.0022111 | -0.012315 | -0.0029864 | -0.0094015 | -0.0012669 | -0.0082093 | 0.011771 | 0.00080103 | 0.0041721 | -0.01885 | 0.021576 | -0.0031338 | -0.064087 | 0.059509 | -0.11444 | -0.086975 | 0.013733 | -0.16479 | -0.082397 | -0.036621 | 0.10529 | -0.073242 | -0.045776 | 0.041199 | -0.064087 | 0.018311 | -0.004578 | -122.6395 | -122.7859 | 0.1236 | 0.027466 | -0.054932 | 0.032044 | -0.050354 | 0.036621 | -122.5937 | -122.7448 | 0.15106 | 0.12817 | 0.045776 | 0.091553 | 0.009155 | 0.12817 | 0.027466 | 0.11444 | 0.027466 | 0.17395 | 0.17853 | 0.16937 | 0.21515 | -122.8134 | -122.7722 | 0.022888 | 0.064087 | 0.045776 | 0.073242
3693.2344 | 122.7081 | -0.12817 | 122.7173 | -0.013657 | -0.0069149 | -0.0012069 | -0.016801 | -0.0042682 | -0.011324 | -0.0048985 | -0.0082093 | 0.010916 | 0.0016556 | -0.0035183 | -0.017141 | 0.02179 | -0.0009976 | -0.073242 | 0.041199 | -0.091553 | -0.07782 | 0.036621 | -0.10529 | -0.045776 | -0.027466 | 0.091553 | -0.082397 | -0.059509 | 0.073242 | 0 | 0.022888 | 0.036621 | -122.6761 | -122.7951 | 0.1648 | 0.082398 | 0.022888 | 0.045777 | -0.013733 | 0.045777 | -122.6257 | -122.7768 | 0.20142 | 0.15106 | 0.12817 | 0.10528 | 0.082397 | 0.12817 | 0.013733 | 0.15564 | 0.022888 | 0.13275 | 0.17395 | 0.16937 | 0.21973 | -122.8088 | -122.7997 | 0.050354 | 0.068665 | 0.054932 | 0.10071
3695 | 122.7219 | -0.10986 | 122.7264 | -0.0060272 | -0.0011471 | -0.0018479 | -0.013597 | 0.002995 | -0.0091879 | -0.0068211 | -0.0051575 | 0.01348 | 0.0033646 | 0.00054052 | -0.019491 | 0.024567 | 7.04e-05 | -0.073242 | 0.059509 | -0.10071 | -0.091553 | 0.013733 | -0.15564 | -0.068665 | -0.022888 | 0.09613 | -0.082397 | -0.036621 | 0.068665 | -0.054932 | 0.036621 | 0.009155 | -122.6669 | -122.818 | 0.1236 | 0.041198 | -0.045777 | 0.032043 | -0.054932 | 0.027466 | -122.6303 | -122.7631 | 0.17853 | 0.14648 | 0.054931 | 0.11902 | 0.027465 | 0.11444 | 0.009155 | 0.15106 | 0.045776 | 0.16022 | 0.17853 | 0.16937 | 0.20599 | -122.8271 | -122.8088 | 0.01831 | 0.073242 | 0.036621 | 0.086975
3696.7031 | 122.7768 | -0.10986 | 122.7127 | -0.0060272 | -0.0054197 | 0.0015701 | -0.01317 | 0.0034222 | -0.010683 | -0.0031895 | -0.0021057 | 0.011557 | 0.00251 | -0.00052768 | -0.017996 | 0.02243 | -0.0005704 | -0.054932 | 0.073242 | -0.10986 | -0.064087 | 0.050354 | -0.10986 | -0.018311 | 0.036621 | 0.07782 | -0.091553 | 0.013733 | 0.11902 | 0.018311 | 0.082397 | 0 | -122.6395 | -122.7768 | 0.16022 | 0.091552 | 0 | 0.091552 | 0 | 0.01831 | -122.6349 | -122.699 | 0.22888 | 0.19226 | 0.12817 | 0.17395 | 0.10986 | 0.16022 | 0.045776 | 0.21057 | 0.10529 | 0.18311 | 0.16937 | 0.18311 | 0.18768 | -122.8226 | -122.8043 | 0.045776 | 0.1236 | 0.054931 | 0.14648
3698.4688 | 122.7402 | -0.10986 | 122.7173 | -0.021286 | -0.0043515 | 0.0017837 | -0.010393 | -0.00042301 | -0.011538 | -0.0038303 | -0.0021057 | 0.012411 | 0.0046462 | 0.0011813 | -0.017355 | 0.02478 | -0.0031338 | -0.059509 | 0.045776 | -0.09613 | -0.059509 | 0.073242 | -0.10529 | -0.032043 | 0.041199 | 0.09613 | -0.10071 | -0.004578 | 0.10986 | 0.004578 | 0.064087 | 0.013733 | -122.6715 | -122.7768 | 0.18311 | 0.07782 | 0.004577 | 0.064087 | -0.009156 | 0.009155 | -122.6212 | -122.7219 | 0.21973 | 0.17395 | 0.11444 | 0.1648 | 0.10529 | 0.16937 | 0.036621 | 0.21057 | 0.09613 | 0.14191 | 0.19684 | 0.15564 | 0.20599 | -122.8134 | -122.818 | 0.050354 | 0.10529 | 0.050354 | 0.15106
3700.2188 | 122.7539 | -0.09613 | 122.699 | -0.013657 | -0.0047787 | -0.00056615 | -0.011888 | 0.00043159 | -0.010256 | -0.0048985 | -0.0051575 | 0.011771 | 0.0022964 | -0.00095488 | -0.019064 | 0.021362 | 7.04e-05 | -0.064087 | 0.059509 | -0.086975 | -0.082397 | 0.064087 | -0.11444 | -0.036621 | 0.032043 | 0.091553 | -0.091553 | -0.009155 | 0.13733 | 0.018311 | 0.10071 | 0.009155 | -122.6395 | -122.7814 | 0.16022 | 0.059509 | -0.018311 | 0.050354 | -0.027466 | 0.004577 | -122.6074 | -122.7081 | 0.23346 | 0.19684 | 0.11444 | 0.19226 | 0.10986 | 0.15106 | 0.004578 | 0.22888 | 0.082398 | 0.14648 | 0.18311 | 0.15564 | 0.18768 | -122.7859 | -122.7905 | 0.013733 | 0.086975 | 0.032043 | 0.12817
3701.9219 | 122.7036 | -0.1236 | 122.7402 | -0.013657 | -0.0077695 | 0.0017837 | -0.014879 | -0.0029864 | -0.011751 | -0.0042575 | -0.0082093 | 0.010275 | 0.001442 | -0.0058683 | -0.017141 | 0.022003 | -0.000784 | -0.10529 | 0.082397 | -0.12817 | -0.14191 | 0.009155 | -0.13733 | -0.059509 | -0.045776 | 0.07782 | -0.086975 | -0.073242 | 0.082397 | -0.018311 | 0.036621 | -0.004578 | -122.6578 | -122.8821 | 0.13275 | 0.064087 | -0.013733 | 0.068665 | -0.009155 | 0.036621 | -122.6624 | -122.8134 | 0.20599 | 0.16022 | 0.10528 | 0.1236 | 0.068664 | 0.13733 | -0.013733 | 0.16937 | 0.013733 | 0.21057 | 0.16479 | 0.20599 | 0.20142 | -122.8683 | -122.8271 | -0.018311 | 0.050354 | 0.01831 | 0.07782
3703.6719 | 122.8592 | -0.068665 | 122.7036 | -0.0060272 | -0.0084103 | -0.0020615 | -0.016801 | 0.00085879 | -0.012179 | -0.0078891 | -0.0082093 | 0.0096344 | 0.0020828 | -0.0062955 | -0.017568 | 0.021149 | 0.0007114 | -0.036621 | 0.027466 | -0.082397 | 0.009155 | 0.16479 | -0.013733 | 0.064087 | 0.16022 | 0.068665 | -0.045776 | 0.050354 | 0.21973 | 0.11902 | 0.14191 | -0.013732 | -122.6761 | -122.6944 | 0.23346 | 0.13275 | 0.054932 | 0.14648 | 0.068664 | 0.022889 | -122.6349 | -122.6532 | 0.28839 | 0.21057 | 0.18768 | 0.18768 | 0.16479 | 0.24719 | 0.091552 | 0.2655 | 0.09613 | 0.10986 | 0.11444 | 0.096131 | 0.13733 | -122.7859 | -122.7493 | 0.07782 | 0.11902 | 0.032044 | 0.22888
3705.4375 | 122.7264 | -0.10529 | 122.7402 | -0.013657 | -0.0077695 | -0.0012069 | -0.016161 | 0.00043159 | -0.01282 | -0.0042575 | -0.011261 | 0.010702 | 0.00251 | -0.0086453 | -0.017568 | 0.02179 | -0.003561 | -0.09613 | 0.068665 | -0.11902 | -0.1236 | -0.009155 | -0.13275 | -0.068665 | -0.036621 | 0.10986 | -0.10071 | -0.064087 | 0.07782 | -0.022888 | 0.045776 | -0.013733 | -122.6715 | -122.8638 | 0.096131 | 0.036621 | -0.027465 | 0.050354 | -0.013732 | 0.004578 | -122.6303 | -122.8043 | 0.18311 | 0.15106 | 0.082398 | 0.14648 | 0.07782 | 0.10986 | -0.004577 | 0.17853 | 0.036621 | 0.18768 | 0.21057 | 0.17395 | 0.21515 | -122.8592 | -122.8409 | -0.01831 | 0.041199 | 0.009156 | 0.068665
3707.1875 | 122.7997 | -0.07782 | 122.6944 | -0.021286 | -0.0039243 | 7.4854e-05 | -0.014665 | 0.0017132 | -0.0085471 | -0.0029759 | -0.0051575 | 0.012839 | 0.0027236 | -0.00095488 | -0.019277 | 0.022644 | 0.0019932 | -0.091553 | 0.054932 | -0.10529 | -0.09613 | 0.022888 | -0.16479 | -0.050354 | 0.022888 | 0.068665 | -0.07782 | 0.013733 | 0.13733 | 0.041199 | 0.10986 | -0.027466 | -122.6395 | -122.7905 | 0.10071 | 0.027466 | -0.086975 | 0.054932 | -0.059509 | 0 | -122.6257 | -122.6807 | 0.21515 | 0.18768 | 0.11902 | 0.18768 | 0.11902 | 0.12817 | 0.009156 | 0.21515 | 0.091553 | 0.16022 | 0.14649 | 0.13275 | 0.14649 | -122.7997 | -122.7722 | -0.01831 | 0.091553 | -0.013733 | 0.10071
3708.8906 | 122.7264 | -0.11444 | 122.7356 | -0.0060272 | -0.0064877 | -0.00035255 | -0.016374 | -0.0032 | -0.01047 | -0.0068211 | -0.0051575 | 0.013052 | 0.0018692 | -0.0041593 | -0.016928 | 0.022858 | -0.00527 | -0.10986 | 0.073242 | -0.11902 | -0.13275 | -0.009155 | -0.13275 | -0.054932 | -0.050354 | 0.082397 | -0.082397 | -0.054932 | 0.064087 | -0.032043 | 0.036621 | -0.004578 | -122.6624 | -122.8683 | 0.10529 | 0.059509 | -0.01831 | 0.064087 | -0.013732 | 0.032044 | -122.6532 | -122.7905 | 0.17853 | 0.15106 | 0.082398 | 0.11902 | 0.050354 | 0.10986 | -0.013732 | 0.14648 | 0.027465 | 0.19226 | 0.16479 | 0.18768 | 0.19684 | -122.8546 | -122.818 | -0.01831 | 0.059509 | 0.004578 | 0.064087
3710.6562 | 122.7722 | -0.07782 | 122.699 | -0.013657 | -0.0037107 | 0.0011429 | -0.013597 | 0.0014996 | -0.010043 | -0.0068211 | -0.0051575 | 0.012411 | 0.001442 | 0.0022495 | -0.017996 | 0.02243 | -0.0003568 | -0.10986 | 0.054932 | -0.10529 | -0.10986 | 0.004578 | -0.17395 | -0.064087 | -0.004578 | 0.091553 | -0.10071 | -0.004578 | 0.09613 | 0.004578 | 0.082397 | -0.027466 | -122.644 | -122.8088 | 0.082398 | 0.013733 | -0.09613 | 0.041199 | -0.068664 | -0.022888 | -122.6074 | -122.7036 | 0.17395 | 0.16022 | 0.082398 | 0.18311 | 0.10529 | 0.10986 | -0.004577 | 0.19684 | 0.09613 | 0.16022 | 0.19226 | 0.13275 | 0.16937 | -122.8043 | -122.7997 | -0.032043 | 0.073242 | -0.032043 | 0.073242
3712.3594 | 122.7539 | -0.1236 | 122.7356 | -0.013657 | -0.0060605 | 0.00050205 | -0.013384 | 0.0044904 | -0.010043 | -0.0051121 | -0.0021057 | 0.010275 | 0.0018692 | 0.0035311 | -0.020773 | 0.022858 | -0.0020658 | -0.086975 | 0.064087 | -0.11444 | -0.10986 | -0.004578 | -0.11902 | -0.050354 | -0.041199 | 0.10529 | -0.10071 | -0.050354 | 0.10529 | 0 | 0.073242 | 0.009155 | -122.6715 | -122.8455 | 0.11902 | 0.073242 | 0.004577 | 0.064087 | -0.004578 | 0.022888 | -122.6303 | -122.7859 | 0.22888 | 0.19684 | 0.1236 | 0.17395 | 0.10071 | 0.10986 | 0.004578 | 0.20599 | 0.050354 | 0.17853 | 0.20599 | 0.18768 | 0.22888 | -122.85 | -122.8363 | 0.013733 | 0.073242 | 0.036621 | 0.082397
3714.125 | 122.8409 | -0.064087 | 122.7081 | -0.013657 | -0.0026425 | 0.0013565 | -0.013811 | 0.0027814 | -0.0096151 | -0.0046847 | -0.0051575 | 0.011343 | 0.0035782 | 0.0020359 | -0.019491 | 0.02243 | -0.0029202 | -0.07782 | 0.064087 | -0.10071 | -0.068665 | 0.054932 | -0.13275 | -0.032043 | 0.054932 | 0.068665 | -0.068665 | 0.059509 | 0.15106 | 0.068665 | 0.14191 | -0.036621 | -122.644 | -122.7768 | 0.11902 | 0.032044 | -0.068664 | 0.068665 | -0.032043 | -0.004578 | -122.6395 | -122.6486 | 0.21515 | 0.20599 | 0.13275 | 0.21057 | 0.13733 | 0.15564 | 0.032043 | 0.21973 | 0.12817 | 0.1648 | 0.13733 | 0.12817 | 0.13275 | -122.8088 | -122.7768 | -0.004578 | 0.1236 | -0.013733 | 0.11902
3715.8125 | 122.7036 | -0.10071 | 122.7448 | -0.013657 | -0.0039243 | -0.00077975 | -0.012743 | -0.0010638 | -0.010043 | -0.0048985 | -0.0051575 | 0.013907 | 0.0050736 | 0.00054052 | -0.017996 | 0.022217 | -0.0031338 | -0.082397 | 0.059509 | -0.11902 | -0.10071 | 0.018311 | -0.16022 | -0.073242 | -0.022888 | 0.082397 | -0.10071 | -0.041199 | 0.045776 | -0.054932 | 0.036621 | -0.018311 | -122.6852 | -122.8455 | 0.11902 | 0.027466 | -0.059509 | 0.045777 | -0.041198 | 0 | -122.6624 | -122.7859 | 0.14648 | 0.13733 | 0.045776 | 0.13733 | 0.045776 | 0.13733 | 0.018311 | 0.14648 | 0.059509 | 0.17853 | 0.18311 | 0.16022 | 0.18311 | -122.8638 | -122.8455 | 0 | 0.059509 | 0.018311 | 0.07782
3717.5781 | 122.8409 | -0.064087 | 122.699 | -0.0060272 | -0.0084103 | -0.0020615 | -0.01851 | -0.0010638 | -0.013247 | -0.0066073 | -0.0082093 | 0.01113 | -0.0013352 | -0.0041593 | -0.017568 | 0.022217 | -0.0056974 | -0.045776 | 0.027466 | -0.073242 | 0.004578 | 0.16022 | 0 | 0.045776 | 0.10529 | 0.064087 | -0.054932 | 0.059509 | 0.19684 | 0.10986 | 0.12817 | -0.009155 | -122.6715 | -122.6944 | 0.2243 | 0.10986 | 0.064087 | 0.11902 | 0.073242 | 0.009155 | -122.6349 | -122.6395 | 0.26093 | 0.19226 | 0.17395 | 0.18311 | 0.16479 | 0.23346 | 0.07782 | 0.25177 | 0.11444 | 0.10071 | 0.11902 | 0.091553 | 0.12817 | -122.7722 | -122.7539 | 0.068665 | 0.1236 | 0.018311 | 0.16937
3719.2812 | 122.7081 | -0.10529 | 122.7173 | -0.013657 | -0.0028561 | 0.00028845 | -0.012956 | 0.0025678 | -0.011324 | -0.0057529 | -0.0082093 | 0.011984 | 0.0018692 | 0.0054537 | -0.018209 | 0.024353 | 0.0013522 | -0.07782 | 0.041199 | -0.086975 | -0.086975 | -0.004578 | -0.16479 | -0.07782 | -0.036621 | 0.086975 | -0.091553 | -0.045776 | 0.032043 | -0.054932 | 0.032043 | 0.018311 | -122.6761 | -122.8043 | 0.10071 | 0.027466 | -0.059509 | 0.009155 | -0.07782 | 0.013733 | -122.6303 | -122.7631 | 0.13733 | 0.13733 | 0.050354 | 0.1236 | 0.036621 | 0.082397 | 0 | 0.1236 | 0.045777 | 0.12817 | 0.17853 | 0.14649 | 0.19226 | -122.8043 | -122.8088 | 0.018311 | 0.05951 | 0.027466 | 0.068665
3721.0469 | 122.7264 | -0.11902 | 122.7264 | -0.028916 | -0.0067013 | 0.00050205 | -0.01552 | -0.0017048 | -0.013888 | -0.0068211 | -0.0051575 | 0.0096344 | 0.00251 | -0.00074128 | -0.016714 | 0.02243 | -0.0009976 | -0.09613 | 0.041199 | -0.10529 | -0.10986 | 0.036621 | -0.12817 | -0.050354 | -0.027466 | 0.068665 | -0.10986 | -0.064087 | 0.064087 | -0.022888 | 0.032043 | 0.013733 | -122.6852 | -122.8363 | 0.15564 | 0.068665 | -0.009155 | 0.054932 | -0.022888 | 0.009156 | -122.6578 | -122.7905 | 0.18311 | 0.15106 | 0.096131 | 0.14191 | 0.086975 | 0.14191 | -0.004577 | 0.17395 | 0.045776 | 0.14649 | 0.17853 | 0.16022 | 0.18768 | -122.8317 | -122.8363 | 0.009156 | 0.054932 | 0.022889 | 0.091553
3722.75 | 122.8455 | -0.07782 | 122.7219 | -0.0060272 | -0.0086239 | -0.0020615 | -0.016588 | 0.004704 | -0.013033 | -0.0051121 | -0.0021057 | 0.0096344 | 0.0010146 | -0.0097135 | -0.020132 | 0.020081 | -0.0016384 | -0.07782 | 0.045776 | -0.10529 | -0.054932 | 0.082397 | -0.059509 | 0.013733 | 0.045776 | 0.086975 | -0.068665 | 0.022888 | 0.16937 | 0.07782 | 0.1236 | -0.027466 | -122.6761 | -122.7768 | 0.16022 | 0.091553 | 0.018311 | 0.11902 | 0.045777 | 0.009155 | -122.6349 | -122.699 | 0.24719 | 0.20142 | 0.15564 | 0.19226 | 0.14649 | 0.18768 | 0.050354 | 0.23804 | 0.091553 | 0.15106 | 0.15564 | 0.1236 | 0.16479 | -122.8271 | -122.7905 | 0.022888 | 0.10071 | 0 | 0.1236
3724.5156 | 122.8546 | -0.059509 | 122.731 | -0.0060272 | -0.0058469 | -0.00013895 | -0.017442 | -0.0019184 | -0.01047 | -0.0023349 | -0.0051575 | 0.009848 | 0.00080103 | -0.00074128 | -0.016928 | 0.02243 | 0.0004978 | -0.022888 | 0.018311 | -0.07782 | 0 | 0.14648 | -0.013733 | 0.064087 | 0.11444 | 0.068665 | -0.064087 | 0.045776 | 0.19684 | 0.10071 | 0.13275 | -0.018311 | -122.7127 | -122.731 | 0.20599 | 0.1236 | 0.045776 | 0.14191 | 0.064087 | -0.004578 | -122.6624 | -122.6852 | 0.25635 | 0.19226 | 0.16022 | 0.19684 | 0.1648 | 0.2243 | 0.07782 | 0.26093 | 0.10986 | 0.096131 | 0.13275 | 0.07782 | 0.12817 | -122.8088 | -122.7951 | 0.059509 | 0.10528 | 0.036621 | 0.17395
3726.2188 | 122.7997 | -0.091553 | 122.6898 | -0.021286 | -0.0054197 | 0.00071565 | -0.018083 | -0.0010638 | -0.011324 | -0.0053257 | -0.0051575 | 0.011984 | 0.001442 | 0.0028903 | -0.020346 | 0.020935 | -0.0029202 | -0.07782 | 0.041199 | -0.091553 | -0.068665 | 0.064087 | -0.086975 | -0.009155 | 0.018311 | 0.073242 | -0.073242 | 0.009155 | 0.14191 | 0.050354 | 0.10529 | 0 | -122.6486 | -122.7585 | 0.15564 | 0.082398 | 0.004578 | 0.082398 | 0.004578 | 0.018311 | -122.6166 | -122.6807 | 0.23346 | 0.19684 | 0.14191 | 0.17853 | 0.1236 | 0.15564 | 0.022888 | 0.21515 | 0.082397 | 0.13275 | 0.14648 | 0.13275 | 0.16479 | -122.7814 | -122.7631 | 0.022888 | 0.10071 | 0.013733 | 0.10986
3727.9844 | 122.7081 | -0.11902 | 122.7356 | -0.013657 | -0.0039243 | 0.0030655 | -0.010179 | 0.0014996 | -0.01047 | -0.0053257 | -0.0021057 | 0.013266 | -5.3368e-05 | -0.0033047 | -0.017568 | 0.02243 | -0.0044156 | -0.09613 | 0.07782 | -0.10071 | -0.14648 | -0.054932 | -0.19684 | -0.082397 | -0.082397 | 0.10986 | -0.10071 | -0.054932 | 0.050354 | -0.068665 | 0.032043 | 0.018311 | -122.6578 | -122.8821 | 0.064087 | 0.036622 | -0.077819 | 0.018311 | -0.09613 | 0.018311 | -122.6257 | -122.7905 | 0.16937 | 0.15106 | 0.050354 | 0.13275 | 0.032043 | 0.045776 | -0.045776 | 0.15106 | 0.045776 | 0.17853 | 0.21057 | 0.19684 | 0.22888 | -122.8363 | -122.8363 | -0.027465 | 0.064087 | 0.022889 | 0.036622
3729.7344 | 122.7219 | -0.10071 | 122.7356 | -0.013657 | -0.0039243 | 0.0019975 | -0.011461 | -0.0027728 | -0.011111 | -0.0044711 | -0.0082093 | 0.01113 | 0.0016556 | -0.00031408 | -0.017141 | 0.023926 | -0.0022794 | -0.07782 | 0.054932 | -0.10529 | -0.10986 | 0 | -0.16479 | -0.091553 | -0.041199 | 0.086975 | -0.082397 | -0.050354 | 0.050354 | -0.064087 | 0.018311 | -0.004578 | -122.6807 | -122.8455 | 0.10071 | 0.009155 | -0.064087 | 0.013733 | -0.059509 | 0.018311 | -122.6486 | -122.7859 | 0.15106 | 0.11902 | 0.036621 | 0.10071 | 0.01831 | 0.10529 | -0.004577 | 0.13275 | 0.032043 | 0.16022 | 0.16937 | 0.15564 | 0.18768 | -122.8409 | -122.818 | -0.009155 | 0.050354 | 0.022888 | 0.059509
3731.5 | 122.7539 | -0.11444 | 122.7356 | 0.0016023 | -0.0067013 | 0.0019975 | -0.014024 | -0.0010638 | -0.010683 | -0.0040439 | -0.0082093 | 0.012625 | 0.0022964 | 0.00032692 | -0.018637 | 0.023712 | -0.0012112 | -0.10529 | 0.054932 | -0.10986 | -0.10986 | 0.004578 | -0.13275 | -0.068665 | -0.041199 | 0.09613 | -0.10071 | -0.041199 | 0.091553 | -0.004578 | 0.059509 | 0.004578 | -122.6807 | -122.8455 | 0.11902 | 0.045776 | -0.01831 | 0.041198 | -0.022888 | 0.013733 | -122.6395 | -122.7768 | 0.20599 | 0.17395 | 0.10986 | 0.16022 | 0.09613 | 0.11444 | 0 | 0.19226 | 0.059509 | 0.16479 | 0.19684 | 0.16937 | 0.21057 | -122.8455 | -122.8363 | 0.004578 | 0.073242 | 0.009155 | 0.073242
3733.2812 | 122.7722 | -0.11902 | 122.7676 | -0.013657 | -0.0062741 | -0.0012069 | -0.013384 | -0.0017048 | -0.012606 | -0.0046847 | -0.0051575 | 0.012625 | -0.0015488 | 0.00054052 | -0.018423 | 0.022003 | -0.0027066 | -0.086975 | 0.059509 | -0.12817 | -0.091553 | 0.004578 | -0.13275 | -0.045776 | -0.036621 | 0.09613 | -0.09613 | -0.050354 | 0.09613 | -0.013733 | 0.054932 | -0.009155 | -122.7081 | -122.8592 | 0.1236 | 0.073243 | -0.013732 | 0.082398 | -0.004577 | 0.022889 | -122.6715 | -122.818 | 0.21515 | 0.17395 | 0.10529 | 0.15106 | 0.082397 | 0.13275 | 0.036621 | 0.19226 | 0.045776 | 0.18768 | 0.19226 | 0.17853 | 0.21515 | -122.8958 | -122.8638 | 0.027466 | 0.068665 | 0.032044 | 0.082398
3735.0469 | 122.7127 | -0.11902 | 122.7219 | -0.021286 | -0.0028561 | 0.0024247 | -0.014665 | 4.192e-06 | -0.0091879 | -0.0046847 | -0.0082093 | 0.012411 | 0.0040054 | -0.0024503 | -0.017782 | 0.024139 | -0.000784 | -0.086975 | 0.059509 | -0.10071 | -0.12817 | -0.027466 | -0.20142 | -0.10986 | -0.073242 | 0.10071 | -0.10071 | -0.064087 | 0.027466 | -0.082397 | 0.027466 | 0.018311 | -122.6624 | -122.85 | 0.091553 | 0.009156 | -0.082397 | -0.009155 | -0.10071 | 0.018311 | -122.6212 | -122.7859 | 0.14649 | 0.14649 | 0.036622 | 0.12817 | 0.018311 | 0.073242 | -0.027466 | 0.12817 | 0.036621 | 0.16022 | 0.20142 | 0.17853 | 0.21973 | -122.8226 | -122.8226 | -0.009155 | 0.054932 | 0.032044 | 0.045777
3736.7656 | 122.7814 | -0.091553 | 122.7173 | -0.0060272 | -0.0026425 | -0.00077975 | -0.01317 | 0.0055584 | -0.010897 | -0.0042575 | -0.0082093 | 0.011343 | 0.0027236 | -0.0041593 | -0.018637 | 0.02243 | -0.004202 | -0.064087 | 0.059509 | -0.11902 | -0.07782 | 0.059509 | -0.10071 | -0.032043 | 0.045776 | 0.082397 | -0.073242 | 0.018311 | 0.12817 | 0.018311 | 0.086975 | -0.027466 | -122.6578 | -122.7951 | 0.15106 | 0.05951 | -0.009155 | 0.086976 | 0.018311 | 0.018311 | -122.6349 | -122.699 | 0.21973 | 0.17853 | 0.10986 | 0.16022 | 0.091553 | 0.17853 | 0.041199 | 0.20142 | 0.091553 | 0.17853 | 0.15564 | 0.15106 | 0.17395 | -122.8363 | -122.7905 | 0.013733 | 0.10986 | 0.027466 | 0.13733
3738.4844 | 122.8683 | -0.07782 | 122.6898 | -0.0060272 | -0.0034971 | 0.00092925 | -0.014665 | 0.0036358 | -0.0076925 | -0.0072483 | -0.0051575 | 0.012198 | 0.0016556 | -0.0062955 | -0.020346 | 0.023071 | 7.04e-05 | -0.022888 | 0.027466 | -0.064087 | -0.009155 | 0.13733 | -0.045776 | 0.022888 | 0.10529 | 0.059509 | -0.068665 | 0.068665 | 0.20142 | 0.082397 | 0.14648 | 0.013733 | -122.6624 | -122.699 | 0.21515 | 0.10071 | 0.032044 | 0.086975 | 0.018311 | 0.009155 | -122.6303 | -122.6212 | 0.27924 | 0.2243 | 0.16022 | 0.21515 | 0.15106 | 0.20142 | 0.054932 | 0.27008 | 0.13733 | 0.091553 | 0.12817 | 0.10529 | 0.13733 | -122.7539 | -122.7585 | 0.068665 | 0.14649 | 0.054932 | 0.18311
3740.25 | 122.8226 | -0.086975 | 122.6807 | -0.021286 | -0.0032833 | 0.0024247 | -0.014024 | 0.0036358 | -0.011538 | -0.0085299 | -0.0082093 | 0.011557 | 0.00251 | -0.00031408 | -0.017782 | 0.024353 | -0.0012112 | -0.09613 | 0.054932 | -0.09613 | -0.091553 | 0.018311 | -0.15106 | -0.050354 | 0.032043 | 0.07782 | -0.073242 | 0.036621 | 0.14191 | 0.041199 | 0.11902 | -0.009155 | -122.6257 | -122.7722 | 0.10529 | 0.036621 | -0.064087 | 0.045776 | -0.054932 | 0.013733 | -122.6028 | -122.644 | 0.22888 | 0.20599 | 0.12817 | 0.19226 | 0.11444 | 0.11444 | 0.004577 | 0.21515 | 0.10986 | 0.15106 | 0.15106 | 0.14191 | 0.16479 | -122.7768 | -122.7539 | -0.004578 | 0.1236 | -0.009155 | 0.11902
3742.0156 | 122.8638 | -0.068665 | 122.6944 | -0.013657 | -0.0079831 | -0.00035255 | -0.01552 | -0.0017048 | -0.011538 | -0.0057529 | -0.0051575 | 0.0083526 | 0.0022964 | -0.0028775 | -0.018423 | 0.022644 | -0.0031338 | -0.032043 | 0.013733 | -0.07782 | -0.004578 | 0.17395 | 0 | 0.086975 | 0.15564 | 0.054932 | -0.068665 | 0.064087 | 0.21973 | 0.12817 | 0.10529 | -0.009155 | -122.6807 | -122.699 | 0.24261 | 0.15564 | 0.068665 | 0.16479 | 0.07782 | 0 | -122.6395 | -122.6303 | 0.28839 | 0.17395 | 0.19684 | 0.17395 | 0.19684 | 0.25177 | 0.073242 | 0.28839 | 0.13275 | 0.091553 | 0.1236 | 0.082398 | 0.1236 | -122.7722 | -122.7631 | 0.064087 | 0.13275 | 0.036622 | 0.22431
3743.7188 | 122.818 | -0.082397 | 122.7081 | -0.013657 | -0.0069149 | 0.0015701 | -0.016374 | 0.00085879 | -0.011538 | -0.0040439 | -0.0021057 | 0.010702 | 0.0012282 | -0.00052768 | -0.018637 | 0.021149 | 0.0004978 | -0.068665 | 0.050354 | -0.082397 | -0.054932 | 0.091553 | -0.10071 | 0 | 0.036621 | 0.064087 | -0.064087 | 0.022888 | 0.14191 | 0.045776 | 0.10529 | 0 | -122.6578 | -122.7631 | 0.17395 | 0.082397 | -0.018311 | 0.082397 | -0.018311 | 0.01831 | -122.644 | -122.6852 | 0.2243 | 0.18768 | 0.12817 | 0.16937 | 0.10986 | 0.17395 | 0.027465 | 0.20599 | 0.086975 | 0.13275 | 0.12817 | 0.13275 | 0.14648 | -122.7905 | -122.7722 | 0.027465 | 0.10528 | 0.013732 | 0.11902
3745.4844 | 122.8592 | -0.086975 | 122.7081 | -0.028916 | -0.0056333 | -0.00013895 | -0.015947 | 0.001286 | -0.012606 | -0.0051121 | -0.011261 | 0.01113 | 0.001442 | 0.00096772 | -0.018209 | 0.021576 | 0.003702 | -0.07782 | 0.027466 | -0.082397 | -0.054932 | 0.086975 | -0.073242 | 0.032043 | 0.07782 | 0.073242 | -0.068665 | 0.022888 | 0.16479 | 0.082397 | 0.11902 | 0.004578 | -122.6807 | -122.7631 | 0.17395 | 0.11902 | 0.013733 | 0.11444 | 0.009155 | 0.01831 | -122.6349 | -122.6852 | 0.25177 | 0.20599 | 0.16937 | 0.18768 | 0.15106 | 0.16937 | 0.027465 | 0.23346 | 0.091553 | 0.10986 | 0.14191 | 0.11444 | 0.16022 | -122.7905 | -122.7768 | 0.032043 | 0.10986 | 0.009155 | 0.16479
3747.1719 | 122.8729 | -0.07782 | 122.699 | -0.021286 | -0.0067013 | -0.00013895 | -0.015733 | 0.00043159 | -0.013033 | -0.0057529 | -0.0082093 | 0.0092072 | 0.0016556 | -0.0067227 | -0.018209 | 0.022217 | -0.0014248 | -0.045776 | 0.036621 | -0.082397 | -0.009155 | 0.11902 | -0.032043 | 0.064087 | 0.14191 | 0.073242 | -0.050354 | 0.068665 | 0.21057 | 0.11902 | 0.14191 | -0.004577 | -122.6624 | -122.7081 | 0.19684 | 0.14191 | 0.045777 | 0.14648 | 0.050354 | 0.027466 | -122.6257 | -122.6303 | 0.28839 | 0.21973 | 0.19684 | 0.19226 | 0.16937 | 0.20142 | 0.073242 | 0.26093 | 0.11902 | 0.11902 | 0.1236 | 0.11444 | 0.15106 | -122.7814 | -122.7493 | 0.068665 | 0.14649 | 0.032044 | 0.21973
3748.9375 | 122.7859 | -0.09613 | 122.7356 | -0.013657 | -0.0060605 | -0.0024887 | -0.014024 | 0.0032086 | -0.010683 | -0.0063937 | -0.0051575 | 0.013693 | 0.0029372 | -0.0062955 | -0.020773 | 0.021149 | 0.0019932 | -0.045776 | 0.073242 | -0.10071 | -0.073242 | 0.027466 | -0.11444 | -0.036621 | 0.027466 | 0.082397 | -0.073242 | -0.013733 | 0.10986 | 0.018311 | 0.082397 | -0.004578 | -122.6624 | -122.8088 | 0.1236 | 0.059509 | -0.018311 | 0.064087 | -0.013733 | 0.022888 | -122.6532 | -122.7493 | 0.20599 | 0.17853 | 0.11444 | 0.15564 | 0.091553 | 0.12817 | 0.027466 | 0.18311 | 0.059509 | 0.17395 | 0.15564 | 0.16937 | 0.17853 | -122.8363 | -122.8088 | 0.022888 | 0.082397 | 0.050354 | 0.1236
3750.6875 | 122.7356 | -0.1236 | 122.7448 | -0.028916 | -0.0024289 | -0.00056615 | -0.01082 | -0.0044818 | -0.0098287 | -0.0059665 | -0.0051575 | 0.012839 | 0.0012282 | 0.0075901 | -0.017996 | 0.024353 | -0.0009976 | -0.10986 | 0.073242 | -0.1236 | -0.13275 | -0.045776 | -0.19684 | -0.11902 | -0.082397 | 0.09613 | -0.09613 | -0.050354 | 0.027466 | -0.054932 | 0.027466 | 0 | -122.6715 | -122.8775 | 0.07782 | 0.004577 | -0.073242 | 0.004577 | -0.073242 | 0.027466 | -122.6486 | -122.7951 | 0.15106 | 0.15106 | 0.068664 | 0.1236 | 0.041198 | 0.07782 | -0.009155 | 0.1236 | 0.045776 | 0.19684 | 0.19226 | 0.19684 | 0.21973 | -122.8683 | -122.8409 | -0.009155 | 0.073242 | 0.013733 | 0.041199
3752.4531 | 122.7493 | -0.14648 | 122.7539 | -0.013657 | -0.0081967 | -0.0022751 | -0.012743 | -0.0036274 | -0.011751 | -0.0059665 | -0.0051575 | 0.0085662 | 0.0027236 | -0.00031408 | -0.0165 | 0.02243 | -0.0012112 | -0.11902 | 0.07782 | -0.11902 | -0.13733 | -0.009155 | -0.13733 | -0.059509 | -0.054932 | 0.09613 | -0.10071 | -0.068665 | 0.059509 | -0.036621 | 0.041199 | 0.027465 | -122.6761 | -122.8912 | 0.13733 | 0.086975 | 0.009155 | 0.05951 | -0.01831 | 0.045776 | -122.6578 | -122.8226 | 0.20599 | 0.18768 | 0.10986 | 0.14191 | 0.064087 | 0.10986 | -0.01831 | 0.16022 | 0.032043 | 0.19684 | 0.19684 | 0.2243 | 0.24261 | -122.8729 | -122.8546 | 0.009155 | 0.077819 | 0.027465 | 0.091552
3754.2031 | 122.7402 | -0.11444 | 122.7356 | -0.021286 | -0.0034971 | 7.4854e-05 | -0.012315 | 0.0040632 | -0.010683 | -0.0042575 | -0.0051575 | 0.010702 | 0.00251 | -0.00010048 | -0.0165 | 0.022858 | 7.04e-05 | -0.082397 | 0.054932 | -0.11902 | -0.10986 | 0.013733 | -0.1831 | -0.091553 | -0.054932 | 0.09613 | -0.10071 | -0.054932 | 0.041199 | -0.07782 | 0.045776 | -0.004578 | -122.6807 | -122.8455 | 0.12817 | 0.022888 | -0.068664 | 0.027466 | -0.064086 | 0.013733 | -122.6395 | -122.7905 | 0.15564 | 0.16022 | 0.036621 | 0.14648 | 0.022888 | 0.13275 | 0.009156 | 0.14191 | 0.045776 | 0.17395 | 0.19684 | 0.16937 | 0.21057 | -122.8546 | -122.8363 | 0.004578 | 0.059509 | 0.032044 | 0.059509
3755.9062 | 122.818 | -0.091553 | 122.7264 | -0.013657 | -0.0077695 | 0.00028845 | -0.017229 | -0.0019184 | -0.011111 | -0.0055393 | -0.0051575 | 0.010916 | 0.001442 | -0.0060819 | -0.018209 | 0.021149 | 0.000925 | -0.07782 | 0.013733 | -0.064087 | -0.050354 | 0.073242 | -0.11444 | 0 | 0.036621 | 0.073242 | -0.091553 | 0.013733 | 0.13733 | 0.027466 | 0.091553 | 0.027466 | -122.7127 | -122.7768 | 0.16479 | 0.091553 | -0.022888 | 0.064087 | -0.050354 | 0 | -122.6532 | -122.7127 | 0.22888 | 0.18311 | 0.11902 | 0.18311 | 0.11902 | 0.13733 | 0.013733 | 0.22888 | 0.10529 | 0.07782 | 0.16479 | 0.10529 | 0.16479 | -122.7905 | -122.818 | 0.041199 | 0.10529 | 0.013733 | 0.12817
3757.6719 | 122.7219 | -0.10986 | 122.7219 | -0.013657 | -0.0015743 | 0.0019975 | -0.012102 | 0.0036358 | -0.0098287 | -0.0055393 | -0.0051575 | 0.012625 | 0.0027236 | -0.00031408 | -0.018637 | 0.023712 | -0.0009976 | -0.10529 | 0.082397 | -0.11902 | -0.13733 | -0.054932 | -0.19226 | -0.10986 | -0.068665 | 0.10986 | -0.082397 | -0.041199 | 0.036621 | -0.054932 | 0.041199 | -0.009156 | -122.6395 | -122.8592 | 0.054931 | 0 | -0.082398 | 0.009156 | -0.073242 | 0.027466 | -122.612 | -122.7631 | 0.14648 | 0.15106 | 0.054931 | 0.1236 | 0.027465 | 0.064087 | -0.01831 | 0.11902 | 0.041198 | 0.20142 | 0.19226 | 0.19226 | 0.21973 | -122.8409 | -122.8043 | -0.027466 | 0.068664 | 0.004577 | 0.041198
3759.4375 | 122.8546 | -0.091553 | 122.7219 | -0.013657 | -0.0043515 | -0.00035255 | -0.015733 | -0.0034136 | -0.011538 | -0.0031895 | -0.0021057 | 0.011343 | -5.3368e-05 | -0.0062955 | -0.019277 | 0.023499 | -0.0027066 | -0.036621 | 0.032043 | -0.091553 | 0.004578 | 0.15564 | -0.018311 | 0.059509 | 0.11902 | 0.068665 | -0.059509 | 0.059509 | 0.20142 | 0.10071 | 0.1236 | 0 | -122.6898 | -122.7173 | 0.24719 | 0.15106 | 0.073242 | 0.15106 | 0.073242 | 0.032044 | -122.6532 | -122.6624 | 0.29297 | 0.21515 | 0.19226 | 0.1831 | 0.16022 | 0.24719 | 0.096131 | 0.26093 | 0.11902 | 0.1236 | 0.12817 | 0.1236 | 0.16022 | -122.8134 | -122.7814 | 0.096131 | 0.15106 | 0.054932 | 0.21057
3761.1406 | 122.85 | -0.082397 | 122.7081 | -0.0060272 | -0.0049923 | 0.00028845 | -0.014452 | 0.00085879 | -0.0085471 | -0.0061801 | -0.0051575 | 0.012625 | -0.0013352 | -0.0077909 | -0.019705 | 0.024353 | 0.002634 | -0.07782 | 0.059509 | -0.091553 | -0.036621 | 0.082397 | -0.086975 | 0.004578 | 0.091553 | 0.073242 | -0.068665 | 0.073242 | 0.16479 | 0.068665 | 0.13275 | -0.009156 | -122.6486 | -122.7448 | 0.16479 | 0.086975 | -0.004578 | 0.096131 | 0.004578 | 0.013732 | -122.6349 | -122.6349 | 0.24719 | 0.21515 | 0.15106 | 0.20142 | 0.13733 | 0.17395 | 0.054932 | 0.23346 | 0.14191 | 0.15106 | 0.14191 | 0.14191 | 0.15564 | -122.7997 | -122.7768 | 0.045776 | 0.15564 | 0.004577 | 0.17395
3762.9062 | 122.8455 | -0.09613 | 122.7127 | -0.013657 | -0.0069149 | 0.00028845 | -0.016801 | 0.00043159 | -0.011965 | -0.0076755 | -0.0082093 | 0.0094208 | 0.0018692 | -0.0015957 | -0.017996 | 0.020508 | 0.0004978 | -0.091553 | 0.036621 | -0.091553 | -0.068665 | 0.068665 | -0.09613 | -0.004578 | 0.036621 | 0.07782 | -0.082397 | 0.013733 | 0.12817 | 0.045776 | 0.086975 | 0.004577 | -122.6761 | -122.7814 | 0.16479 | 0.091552 | 0 | 0.086975 | -0.004577 | 0.013733 | -122.6349 | -122.699 | 0.2243 | 0.1831 | 0.14191 | 0.16937 | 0.12817 | 0.16022 | 0.022888 | 0.21057 | 0.09613 | 0.12817 | 0.16022 | 0.13275 | 0.17395 | -122.8043 | -122.7951 | 0.027465 | 0.10986 | 0.004577 | 0.13275
3764.6719 | 122.8592 | -0.07782 | 122.7127 | -0.013657 | -0.0075559 | 7.4854e-05 | -0.015947 | 0.00085879 | -0.011751 | -0.0066073 | -0.0021057 | 0.0089934 | -5.3368e-05 | -0.00052768 | -0.018209 | 0.023926 | -0.002493 | -0.050354 | 0.022888 | -0.082397 | 0.018311 | 0.16022 | -0.004578 | 0.054932 | 0.11902 | 0.068665 | -0.054932 | 0.064087 | 0.20599 | 0.10529 | 0.12817 | -0.004577 | -122.6898 | -122.6944 | 0.23804 | 0.13275 | 0.073242 | 0.13733 | 0.077819 | 0.022888 | -122.644 | -122.6486 | 0.28381 | 0.20599 | 0.18311 | 0.18311 | 0.16022 | 0.24261 | 0.10071 | 0.26093 | 0.11902 | 0.10528 | 0.1236 | 0.10071 | 0.14649 | -122.7951 | -122.7676 | 0.096131 | 0.14191 | 0.027466 | 0.19684
3766.375 | 122.8775 | -0.07782 | 122.7173 | -0.013657 | -0.0069149 | 0.00028845 | -0.018724 | 0.0034222 | -0.011965 | -0.0057529 | -0.0051575 | 0.0089934 | 0.00016023 | -0.0020231 | -0.019918 | 0.022003 | -0.0001432 | -0.073242 | 0.036621 | -0.091553 | -0.045776 | 0.091553 | -0.073242 | 0.027466 | 0.059509 | 0.073242 | -0.07782 | 0.050354 | 0.18768 | 0.091553 | 0.14191 | -0.013733 | -122.6807 | -122.7631 | 0.16937 | 0.10529 | 0.004578 | 0.11902 | 0.018311 | 0 | -122.644 | -122.6669 | 0.2655 | 0.21973 | 0.16937 | 0.21973 | 0.16937 | 0.18311 | 0.045777 | 0.2655 | 0.12817 | 0.12817 | 0.15106 | 0.11444 | 0.15106 | -122.8088 | -122.7951 | 0.032044 | 0.12817 | 0.004578 | 0.13733
3768.1406 | 122.7814 | -0.091553 | 122.7448 | -0.013657 | -0.0032833 | 0.0030655 | -0.01082 | 0.001286 | -0.011965 | -0.0059665 | -0.0021057 | 0.012839 | 0.0020828 | -0.0024503 | -0.019491 | 0.020081 | -0.0022794 | -0.036621 | 0.059509 | -0.10071 | -0.036621 | 0.064087 | -0.11444 | -0.027466 | 0.054932 | 0.086975 | -0.073242 | 0.013733 | 0.12817 | 0 | 0.082397 | -0.009155 | -122.6852 | -122.7814 | 0.15564 | 0.064087 | -0.022888 | 0.073242 | -0.013733 | 0.018311 | -122.6578 | -122.731 | 0.21973 | 0.17395 | 0.091553 | 0.15564 | 0.073242 | 0.1648 | 0.064087 | 0.20142 | 0.086975 | 0.16022 | 0.16022 | 0.15106 | 0.17853 | -122.8455 | -122.818 | 0.054932 | 0.10529 | 0.054932 | 0.14649
3769.8438 | 122.8821 | -0.082397 | 122.7219 | -0.021286 | -0.0067013 | -0.00035255 | -0.014879 | -0.003841 | -0.011538 | -0.0063937 | -0.0082093 | 0.010702 | 0.0018692 | -0.0073635 | -0.019705 | 0.02243 | -0.0018522 | -0.027466 | 0.027466 | -0.059509 | 0.022888 | 0.17853 | 0.018311 | 0.082397 | 0.1236 | 0.064087 | -0.064087 | 0.064087 | 0.22888 | 0.1236 | 0.15106 | 0.022888 | -122.6944 | -122.699 | 0.26092 | 0.16479 | 0.10071 | 0.14191 | 0.07782 | 0.01831 | -122.6578 | -122.6578 | 0.31128 | 0.23346 | 0.20599 | 0.21515 | 0.18768 | 0.23804 | 0.082397 | 0.29297 | 0.12817 | 0.086975 | 0.12817 | 0.10986 | 0.14648 | -122.7814 | -122.7859 | 0.10528 | 0.14648 | 0.054931 | 0.20599
3771.6094 | 122.8455 | -0.082397 | 122.7264 | -0.013657 | -0.0052059 | -0.0012069 | -0.01552 | -0.00020941 | -0.01047 | -0.0042575 | -0.0051575 | 0.0085662 | 0.00058743 | -0.0024503 | -0.019918 | 0.019653 | -0.0037748 | -0.054932 | 0.022888 | -0.068665 | -0.032043 | 0.12817 | -0.10071 | 0.004578 | 0.082397 | 0.068665 | -0.073242 | 0.018311 | 0.16022 | 0.032043 | 0.091553 | 0.013732 | -122.7036 | -122.7585 | 0.21057 | 0.086975 | -0.018311 | 0.073243 | -0.032043 | 0.009155 | -122.6578 | -122.7081 | 0.24261 | 0.17395 | 0.11444 | 0.16479 | 0.10529 | 0.19684 | 0.036622 | 0.23346 | 0.091553 | 0.091553 | 0.14191 | 0.10528 | 0.15106 | -122.7951 | -122.7997 | 0.050354 | 0.10071 | 0.027465 | 0.16479
3773.375 | 122.7676 | -0.10986 | 122.7448 | -0.0060272 | -0.0064877 | -0.0018479 | -0.01317 | 0.00021799 | -0.012392 | -0.0066073 | -0.0082093 | 0.011984 | -5.3368e-05 | -0.0018093 | -0.021841 | 0.02243 | -0.0022794 | -0.10986 | 0.07782 | -0.11902 | -0.1236 | -0.009155 | -0.15564 | -0.064087 | -0.054932 | 0.10986 | -0.10986 | -0.050354 | 0.07782 | -0.027466 | 0.050354 | -0.009156 | -122.6669 | -122.8683 | 0.10071 | 0.045776 | -0.045777 | 0.054932 | -0.036621 | 0 | -122.6349 | -122.7951 | 0.18768 | 0.16022 | 0.082397 | 0.16022 | 0.082397 | 0.10986 | -0.004577 | 0.18768 | 0.059509 | 0.19684 | 0.21973 | 0.18768 | 0.21973 | -122.8638 | -122.8546 | -0.013733 | 0.059509 | 0 | 0.054931
3775.1406 | 122.8455 | -0.09613 | 122.7036 | -0.0060272 | -0.0096921 | -0.00013895 | -0.014238 | -0.0040546 | -0.011751 | -0.0070347 | -0.0082093 | 0.010489 | -0.0011216 | -0.0097135 | -0.019277 | 0.019653 | -0.002493 | -0.036621 | 0.018311 | -0.086975 | -0.004578 | 0.15564 | -0.027466 | 0.068665 | 0.10529 | 0.064087 | -0.054932 | 0.054932 | 0.20142 | 0.10071 | 0.1236 | 0.009155 | -122.6852 | -122.7081 | 0.25177 | 0.16479 | 0.068664 | 0.15564 | 0.059509 | 0.041198 | -122.6395 | -122.6486 | 0.29755 | 0.21973 | 0.19684 | 0.17853 | 0.15564 | 0.24261 | 0.082397 | 0.25635 | 0.10986 | 0.10529 | 0.11902 | 0.11444 | 0.16022 | -122.7905 | -122.7585 | 0.091552 | 0.15106 | 0.059509 | 0.20142
3776.8438 | 122.85 | -0.064087 | 122.7173 | -0.021286 | -0.0041379 | 0.0030655 | -0.014024 | 0.0019268 | -0.0096151 | -0.0083163 | -0.0082093 | 0.0094208 | 0.0020828 | -0.00095488 | -0.019064 | 0.021576 | -0.00527 | -0.041199 | 0.009155 | -0.059509 | -0.004578 | 0.12817 | -0.073242 | 0.018311 | 0.10986 | 0.059509 | -0.068665 | 0.041199 | 0.15564 | 0.059509 | 0.10071 | 0.004578 | -122.7081 | -122.7219 | 0.19226 | 0.082398 | -0.009155 | 0.07782 | -0.013733 | -0.004578 | -122.6578 | -122.6761 | 0.21973 | 0.1648 | 0.1236 | 0.16937 | 0.12817 | 0.18768 | 0.054931 | 0.22431 | 0.10986 | 0.068664 | 0.12817 | 0.073242 | 0.1236 | -122.7768 | -122.7859 | 0.059509 | 0.10529 | 0.022888 | 0.17395
3778.625 | 122.85 | -0.086975 | 122.7127 | -0.013657 | -0.0037107 | 0.0015701 | -0.014879 | 0.0014996 | -0.010256 | -0.0034031 | -0.0082093 | 0.0096344 | 0.00251 | -0.0015957 | -0.01885 | 0.021362 | -0.0009976 | -0.027466 | 0.036621 | -0.064087 | -0.004578 | 0.15564 | -0.064087 | 0.004578 | 0.11902 | 0.054932 | -0.064087 | 0.064087 | 0.1831 | 0.073242 | 0.12817 | 0.022888 | -122.6761 | -122.7173 | 0.24261 | 0.091553 | 0.022888 | 0.068665 | 0 | 0.022888 | -122.6578 | -122.6486 | 0.27008 | 0.21515 | 0.16022 | 0.19226 | 0.13733 | 0.21973 | 0.059509 | 0.24719 | 0.12817 | 0.10071 | 0.11902 | 0.1236 | 0.14191 | -122.7768 | -122.7768 | 0.082397 | 0.15106 | 0.059509 | 0.20599
3780.3125 | 122.8043 | -0.10071 | 122.7402 | -0.0060272 | -0.0052059 | 0.00028845 | -0.014024 | 0.0044904 | -0.011965 | -0.0040439 | -0.011261 | 0.011771 | 0.0022964 | -0.0024503 | -0.020986 | 0.022217 | -0.0014248 | -0.064087 | 0.068665 | -0.091553 | -0.045776 | 0.064087 | -0.11444 | -0.032043 | 0.036621 | 0.09613 | -0.07782 | 0.018311 | 0.13733 | 0.004578 | 0.082397 | 0.009155 | -122.6715 | -122.7859 | 0.1648 | 0.068665 | -0.013733 | 0.05951 | -0.022888 | 0.022888 | -122.644 | -122.7219 | 0.23804 | 0.18311 | 0.10529 | 0.16022 | 0.082398 | 0.15564 | 0.045777 | 0.21515 | 0.096131 | 0.16022 | 0.17395 | 0.16937 | 0.19684 | -122.8317 | -122.818 | 0.054932 | 0.11902 | 0.036621 | 0.13733
3782.0781 | 122.8638 | -0.091553 | 122.6944 | -0.028916 | -0.0054197 | 0.00092925 | -0.015947 | -0.002132 | -0.011324 | -0.0061801 | -0.0021057 | 0.011557 | 0.0027236 | -0.0090725 | -0.016073 | 0.021362 | -0.0046292 | -0.07782 | 0.041199 | -0.10529 | -0.073242 | 0.064087 | -0.09613 | -0.009155 | 0.032043 | 0.068665 | -0.073242 | 0.032043 | 0.15564 | 0.073242 | 0.10529 | -0.013733 | -122.6532 | -122.7676 | 0.15564 | 0.082398 | -0.004577 | 0.096131 | 0.009156 | 0.018311 | -122.6257 | -122.6624 | 0.24719 | 0.19684 | 0.16479 | 0.17853 | 0.14648 | 0.16937 | 0.032044 | 0.22888 | 0.10529 | 0.14649 | 0.14191 | 0.13275 | 0.16022 | -122.7997 | -122.7676 | 0.018311 | 0.1236 | 0.013733 | 0.1236
3783.8438 | 122.7631 | -0.1236 | 122.7585 | -0.013657 | -0.0037107 | 0.0011429 | -0.011888 | 0.0036358 | -0.0091879 | -0.0029759 | -0.0051575 | 0.013266 | 0.0029372 | -0.0011685 | -0.019918 | 0.02478 | -0.0033474 | -0.11444 | 0.064087 | -0.11444 | -0.12817 | -0.032043 | -0.20142 | -0.086975 | -0.059509 | 0.10529 | -0.10529 | -0.036621 | 0.045776 | -0.073242 | 0.032043 | 0.009155 | -122.6944 | -122.8867 | 0.091553 | 0.036621 | -0.07782 | 0.027466 | -0.086975 | 0.01831 | -122.6532 | -122.7951 | 0.16937 | 0.15564 | 0.050354 | 0.13733 | 0.032044 | 0.082398 | -0.013733 | 0.15106 | 0.068665 | 0.17853 | 0.21057 | 0.18768 | 0.22888 | -122.8729 | -122.8638 | -0.004578 | 0.086975 | 0.009155 | 0.064087
3785.5469 | 122.8134 | -0.086975 | 122.7402 | -0.013657 | -0.0056333 | 0.00071565 | -0.012743 | -0.0012774 | -0.011965 | -0.0021213 | -0.0051575 | 0.013052 | -0.00048057 | -0.00010048 | -0.01885 | 0.020294 | -0.0014248 | -0.054932 | 0.068665 | -0.10986 | -0.045776 | 0.068665 | -0.10986 | -0.036621 | 0.050354 | 0.073242 | -0.064087 | 0.009155 | 0.13275 | 0.018311 | 0.07782 | -0.022888 | -122.6715 | -122.7859 | 0.15564 | 0.050354 | -0.022888 | 0.073242 | 0 | 0.022888 | -122.6669 | -122.731 | 0.21973 | 0.16479 | 0.10529 | 0.14191 | 0.082398 | 0.17853 | 0.064087 | 0.19684 | 0.073242 | 0.17853 | 0.13733 | 0.15564 | 0.16022 | -122.85 | -122.8043 | 0.041199 | 0.09613 | 0.032043 | 0.13733
3787.2969 | 122.7676 | -0.10529 | 122.7493 | -0.013657 | -0.0024289 | -0.00077975 | -0.012956 | -0.0017048 | -0.0098287 | -0.0048985 | -0.0051575 | 0.011984 | 0.003151 | 0.0031039 | -0.017782 | 0.020721 | -0.0050564 | -0.09613 | 0.068665 | -0.11444 | -0.13733 | -0.022888 | -0.19226 | -0.10071 | -0.041199 | 0.086975 | -0.10529 | -0.045776 | 0.045776 | -0.054932 | 0.050354 | -0.009155 | -122.6807 | -122.8867 | 0.082398 | 0.004578 | -0.086975 | 0.013733 | -0.07782 | 0 | -122.6624 | -122.7951 | 0.15106 | 0.15564 | 0.050354 | 0.15564 | 0.050354 | 0.091553 | -0.022888 | 0.15106 | 0.05951 | 0.18311 | 0.19226 | 0.17395 | 0.19226 | -122.8638 | -122.8546 | -0.032043 | 0.05951 | 0.009156 | 0.064087
3789.0625 | 122.7722 | -0.10986 | 122.7722 | -0.0060272 | -0.0075559 | -0.0027023 | -0.01552 | -0.0025592 | -0.01282 | -0.0044711 | -0.0082093 | 0.010489 | 0.0018692 | 0.00011332 | -0.01885 | 0.023499 | -0.0029202 | -0.09613 | 0.036621 | -0.10071 | -0.10986 | 0.036621 | -0.11902 | -0.045776 | -0.027466 | 0.10071 | -0.086975 | -0.059509 | 0.07782 | -0.009155 | 0.022888 | 0.009155 | -122.7356 | -122.8821 | 0.14648 | 0.064087 | -0.009156 | 0.054932 | -0.018311 | 0.022888 | -122.6715 | -122.8317 | 0.18768 | 0.13275 | 0.10071 | 0.10986 | 0.07782 | 0.13733 | -0.009155 | 0.16479 | 0.027466 | 0.13733 | 0.18768 | 0.14648 | 0.21057 | -122.8729 | -122.8592 | 0 | 0.050354 | 0.013733 | 0.082397
3790.75 | 122.8683 | -0.073242 | 122.7219 | -0.036545 | -0.0032833 | -0.00077975 | -0.015093 | 0.0040632 | -0.010897 | -0.0051121 | -0.011261 | 0.010916 | 0.0016556 | 0.0018221 | -0.018209 | 0.023285 | -0.0009976 | -0.09613 | 0.054932 | -0.10529 | -0.07782 | 0.054932 | -0.16022 | -0.036621 | 0.054932 | 0.07782 | -0.059509 | 0.054932 | 0.16022 | 0.054932 | 0.1236 | -0.032044 | -122.6669 | -122.7997 | 0.12817 | 0.036621 | -0.086975 | 0.068665 | -0.054931 | 0.013733 | -122.644 | -122.6669 | 0.23346 | 0.19684 | 0.12817 | 0.1831 | 0.11444 | 0.16022 | 0.027466 | 0.21973 | 0.11444 | 0.16022 | 0.13733 | 0.12817 | 0.15106 | -122.8271 | -122.7814 | -0.004578 | 0.12817 | -0.022888 | 0.12817
3792.5156 | 122.8912 | -0.07782 | 122.7356 | -0.013657 | -0.0067013 | -0.0018479 | -0.017656 | -0.0010638 | -0.012179 | -0.0031895 | -0.0082093 | 0.010702 | 0.0016556 | -0.0082181 | -0.016287 | 0.020721 | -0.0012112 | -0.068665 | 0.027466 | -0.09613 | -0.004578 | 0.13275 | -0.032043 | 0.050354 | 0.10986 | 0.064087 | -0.064087 | 0.064087 | 0.2243 | 0.11902 | 0.15564 | -0.01831 | -122.7081 | -122.7402 | 0.21057 | 0.12817 | 0.045777 | 0.14648 | 0.064087 | 0.013733 | -122.6715 | -122.6715 | 0.30212 | 0.23346 | 0.19684 | 0.21973 | 0.18311 | 0.22888 | 0.091552 | 0.28839 | 0.12817 | 0.1236 | 0.12817 | 0.10529 | 0.14191 | -122.8317 | -122.7997 | 0.073242 | 0.14191 | 0.009155 | 0.18768
3794.2812 | 122.7951 | -0.10529 | 122.7264 | -0.021286 | -0.0022153 | 0.0015701 | -0.012315 | 0.002995 | -0.010043 | -0.0048985 | -0.011261 | 0.013266 | 0.0018692 | 0.0037447 | -0.019277 | 0.024353 | -0.0031338 | -0.09613 | 0.068665 | -0.11902 | -0.13733 | -0.013733 | -0.17395 | -0.07782 | -0.027466 | 0.10071 | -0.091553 | -0.032043 | 0.068665 | -0.036621 | 0.050354 | -0.013733 | -122.6578 | -122.8638 | 0.091553 | 0.027466 | -0.068664 | 0.041199 | -0.054931 | 0.013733 | -122.6257 | -122.7585 | 0.17395 | 0.15564 | 0.068665 | 0.14191 | 0.054932 | 0.10529 | -0.01831 | 0.16022 | 0.05951 | 0.18768 | 0.19226 | 0.17395 | 0.20599 | -122.8455 | -122.818 | -0.032043 | 0.073243 | 0.009156 | 0.07782
3796.0469 | 122.7676 | -0.10529 | 122.731 | -0.021286 | -0.0015743 | -0.00035255 | -0.013597 | 0.00021799 | -0.010897 | -0.0031895 | -0.0051575 | 0.011984 | 0.0012282 | -0.00052768 | -0.018637 | 0.023285 | -0.002493 | -0.11444 | 0.045776 | -0.10529 | -0.1236 | -0.027466 | -0.18768 | -0.086975 | -0.041199 | 0.10071 | -0.09613 | -0.045776 | 0.050354 | -0.054932 | 0.032043 | 0 | -122.6852 | -122.8546 | 0.07782 | 0.018311 | -0.082397 | 0.018311 | -0.082397 | 0.009156 | -122.6303 | -122.7768 | 0.15564 | 0.13733 | 0.050354 | 0.12817 | 0.041198 | 0.07782 | -0.01831 | 0.14648 | 0.050354 | 0.15106 | 0.19684 | 0.15106 | 0.20599 | -122.8363 | -122.8271 | -0.01831 | 0.05951 | -0.009155 | 0.064087
3797.8125 | 122.8592 | -0.07782 | 122.7127 | -0.0060272 | -0.0056333 | -0.00056615 | -0.015306 | -0.0034136 | -0.011965 | -0.0068211 | -0.0082093 | 0.009848 | -5.3368e-05 | 0.00054052 | -0.017141 | 0.019653 | 0.0013522 | -0.09613 | 0.032043 | -0.091553 | -0.073242 | 0.073242 | -0.082397 | 0.009155 | 0.041199 | 0.050354 | -0.086975 | 0.032043 | 0.16022 | 0.054932 | 0.11902 | -0.013733 | -122.6807 | -122.7859 | 0.15106 | 0.086975 | -0.004577 | 0.10071 | 0.009156 | -0.009155 | -122.6624 | -122.6807 | 0.23804 | 0.19684 | 0.13275 | 0.20599 | 0.14191 | 0.16479 | 0.018311 | 0.24719 | 0.11902 | 0.1236 | 0.13733 | 0.10986 | 0.12817 | -122.8043 | -122.7997 | 0.004578 | 0.10986 | -0.01831 | 0.11902
3799.5312 | 122.8867 | -0.07782 | 122.699 | -0.021286 | -0.0088375 | -0.00077975 | -0.016161 | -0.0010638 | -0.01047 | -0.0051121 | -0.0051575 | 0.0096344 | 0.00016023 | -0.0035183 | -0.020773 | 0.022217 | 0.0004978 | -0.07782 | 0.027466 | -0.082397 | -0.050354 | 0.091553 | -0.073242 | 0.018311 | 0.054932 | 0.059509 | -0.064087 | 0.050354 | 0.18768 | 0.091553 | 0.13275 | -0.004577 | -122.6715 | -122.7493 | 0.16937 | 0.096131 | 0.004578 | 0.10071 | 0.009155 | 0.013733 | -122.6395 | -122.6486 | 0.2655 | 0.21057 | 0.16937 | 0.19684 | 0.15564 | 0.17395 | 0.032043 | 0.25177 | 0.11444 | 0.10986 | 0.1236 | 0.10529 | 0.13733 | -122.7814 | -122.7631 | 0.027466 | 0.12817 | 0 | 0.13275
3801.2344 | 122.8317 | -0.091553 | 122.7219 | -0.021286 | -0.0071285 | -0.00056615 | -0.017015 | -0.00020941 | -0.010043 | -0.0063937 | -0.0051575 | 0.01113 | 0.0012282 | -0.00074128 | -0.019491 | 0.019867 | 0.0032748 | -0.086975 | 0.009155 | -0.068665 | -0.036621 | 0.082397 | -0.09613 | 0 | 0.032043 | 0.064087 | -0.07782 | 0.004578 | 0.12817 | 0.036621 | 0.091553 | 0.022888 | -122.7127 | -122.7585 | 0.17395 | 0.091553 | -0.004577 | 0.068665 | -0.027465 | 0.013733 | -122.6578 | -122.7173 | 0.21973 | 0.18311 | 0.12817 | 0.16937 | 0.11444 | 0.15106 | 0.032044 | 0.20599 | 0.082398 | 0.07782 | 0.14191 | 0.10071 | 0.15564 | -122.7905 | -122.7997 | 0.054932 | 0.096131 | 0.004578 | 0.1236
3802.9844 | 122.8912 | -0.054932 | 122.7356 | 0.0016023 | -0.0052059 | 0.0013565 | -0.014879 | -0.00042301 | -0.0096151 | -0.0023349 | -0.0051575 | 0.012625 | -0.00069437 | 0.00054052 | -0.019918 | 0.022858 | -0.0029202 | -0.027466 | 0.009155 | -0.068665 | 0 | 0.13275 | -0.073242 | 0.022888 | 0.12817 | 0.064087 | -0.068665 | 0.073242 | 0.1831 | 0.07782 | 0.13733 | -0.013733 | -122.7264 | -122.7356 | 0.18768 | 0.07782 | -0.01831 | 0.091553 | -0.004577 | -0.013733 | -122.6715 | -122.6624 | 0.23804 | 0.19226 | 0.13275 | 0.20599 | 0.14649 | 0.20142 | 0.068665 | 0.25177 | 0.14191 | 0.07782 | 0.13275 | 0.064087 | 0.11902 | -122.8043 | -122.8043 | 0.054932 | 0.12817 | 0.027466 | 0.18311
3804.6875 | 122.8088 | -0.09613 | 122.7585 | -0.021286 | -0.0028561 | 0.00071565 | -0.01317 | 0.0010724 | -0.0089743 | -0.0016941 | -0.0082093 | 0.013052 | 0.0020828 | -0.0024503 | -0.020559 | 0.02179 | -0.000784 | -0.10529 | 0.059509 | -0.10529 | -0.11902 | -0.009155 | -0.1831 | -0.068665 | -0.027466 | 0.10071 | -0.086975 | -0.018311 | 0.068665 | -0.027466 | 0.050354 | -0.009156 | -122.699 | -122.8775 | 0.086975 | 0.027465 | -0.086975 | 0.036621 | -0.077819 | 0.009155 | -122.6578 | -122.7768 | 0.16479 | 0.14648 | 0.068664 | 0.13733 | 0.059509 | 0.096131 | -0.013733 | 0.15564 | 0.068664 | 0.16479 | 0.18768 | 0.15564 | 0.19684 | -122.8638 | -122.8455 | -0.022889 | 0.077819 | -0.009156 | 0.068664
3806.3906 | 122.7722 | -0.10071 | 122.7676 | -0.0060272 | -0.0039243 | 0.0015701 | -0.012956 | 0.0019268 | -0.011111 | -0.0063937 | -0.0082093 | 0.011984 | 0.0012282 | -0.0020231 | -0.019918 | 0.021362 | 0.0004978 | -0.10529 | 0.082397 | -0.13275 | -0.11902 | -0.027466 | -0.19684 | -0.10071 | -0.054932 | 0.10529 | -0.10529 | -0.050354 | 0.059509 | -0.082397 | 0.027466 | -0.032043 | -122.6852 | -122.8867 | 0.073242 | 0 | -0.09613 | 0.032043 | -0.064087 | -0.004578 | -122.6624 | -122.818 | 0.16022 | 0.12817 | 0.018311 | 0.13275 | 0.022889 | 0.10529 | 0.013732 | 0.16479 | 0.054932 | 0.21515 | 0.21057 | 0.18311 | 0.20599 | -122.9004 | -122.8729 | -0.018311 | 0.050354 | -0.004578 | 0.045776
3808.1562 | 122.8546 | -0.086975 | 122.7356 | -0.013657 | -0.0049923 | -0.00035255 | -0.016161 | 0.00064519 | -0.0083335 | -0.0057529 | -0.0051575 | 0.0089934 | 0.0033646 | -0.0056547 | -0.018209 | 0.021149 | -0.0005704 | -0.086975 | 0.032043 | -0.086975 | -0.064087 | 0.086975 | -0.09613 | 0.004578 | 0.045776 | 0.054932 | -0.068665 | 0.022888 | 0.13275 | 0.041199 | 0.091553 | 0 | -122.7036 | -122.7997 | 0.17395 | 0.091553 | -0.009155 | 0.091553 | -0.009155 | 0.01831 | -122.6807 | -122.7127 | 0.21973 | 0.17853 | 0.12817 | 0.16022 | 0.10986 | 0.17395 | 0.022888 | 0.20142 | 0.091553 | 0.11902 | 0.1236 | 0.11902 | 0.14191 | -122.8226 | -122.8043 | 0.022888 | 0.10986 | 0 | 0.13275
3809.9219 | 122.7814 | -0.091553 | 122.7493 | -0.021286 | -0.0015743 | -0.00013895 | -0.014452 | -0.00085021 | -0.012179 | -0.0048985 | -0.0082093 | 0.01412 | 0.0018692 | 0.00096772 | -0.017782 | 0.022858 | -0.0022794 | -0.054932 | 0.050354 | -0.10071 | -0.059509 | 0.054932 | -0.1236 | -0.032043 | 0.022888 | 0.11444 | -0.09613 | -0.013733 | 0.10071 | -0.018311 | 0.064087 | -0.009155 | -122.699 | -122.8088 | 0.14649 | 0.05951 | -0.032043 | 0.068665 | -0.022888 | -0.004577 | -122.6349 | -122.7631 | 0.19226 | 0.15564 | 0.073242 | 0.16022 | 0.077819 | 0.15564 | 0.041199 | 0.19684 | 0.082397 | 0.15106 | 0.21057 | 0.14191 | 0.20599 | -122.85 | -122.8455 | 0.032044 | 0.07782 | 0.036621 | 0.11444
3811.7031 | 122.8271 | -0.086975 | 122.7631 | -0.021286 | -0.0030697 | 0.0011429 | -0.014452 | -0.0012774 | -0.01047 | -0.0036167 | -0.0021057 | 0.010916 | 0.0020828 | -0.00031408 | -0.019277 | 0.023071 | -0.002493 | -0.054932 | 0.082397 | -0.10529 | -0.059509 | 0.082397 | -0.10071 | -0.032043 | 0.041199 | 0.091553 | -0.086975 | 0.004578 | 0.13733 | 0.013733 | 0.082397 | -0.018311 | -122.6807 | -122.8226 | 0.16937 | 0.054932 | -0.013733 | 0.073243 | 0.004578 | 0 | -122.6715 | -122.7585 | 0.2243 | 0.16937 | 0.10071 | 0.16937 | 0.10071 | 0.18768 | 0.045777 | 0.2243 | 0.091553 | 0.18768 | 0.17853 | 0.16937 | 0.17853 | -122.8683 | -122.85 | 0.027466 | 0.091553 | 0.032043 | 0.12817
3813.4062 | 122.85 | -0.091553 | 122.7631 | -0.021286 | -0.0092649 | -0.00013895 | -0.018083 | -0.004909 | -0.011111 | -0.0057529 | -0.0051575 | 0.009848 | 0.0020828 | -0.010781 | -0.01885 | 0.021362 | -0.0005704 | -0.09613 | 0.027466 | -0.09613 | -0.073242 | 0.068665 | -0.086975 | 0.009155 | 0.032043 | 0.064087 | -0.068665 | 0.018311 | 0.16479 | 0.073242 | 0.10071 | -0.004577 | -122.7356 | -122.8363 | 0.16022 | 0.10071 | 0.004578 | 0.10528 | 0.009155 | 0.022888 | -122.699 | -122.7448 | 0.25635 | 0.19226 | 0.16479 | 0.16937 | 0.14191 | 0.16479 | 0.022888 | 0.23346 | 0.086976 | 0.1236 | 0.13275 | 0.11902 | 0.15564 | -122.8592 | -122.8317 | 0.018311 | 0.10986 | -0.004577 | 0.1236
3815.1719 | 122.8226 | -0.10529 | 122.7676 | -0.021286 | -0.0052059 | -0.00013895 | -0.012956 | 0.0019268 | -0.010256 | -0.0061801 | -0.0051575 | 0.012198 | 0.0020828 | 0.0018221 | -0.019918 | 0.023285 | 0.0004978 | -0.064087 | 0.068665 | -0.09613 | -0.068665 | 0.050354 | -0.09613 | -0.022888 | 0.027466 | 0.10071 | -0.082397 | 0.022888 | 0.13733 | 0.022888 | 0.086975 | 0.009156 | -122.699 | -122.8363 | 0.15564 | 0.082398 | 0.009156 | 0.073242 | 0 | 0.022889 | -122.6669 | -122.7448 | 0.24262 | 0.19226 | 0.12817 | 0.16937 | 0.10528 | 0.14648 | 0.027465 | 0.21973 | 0.10528 | 0.16479 | 0.18311 | 0.17395 | 0.20599 | -122.8638 | -122.85 | 0.036621 | 0.12817 | 0.041199 | 0.13275
3816.9375 | 122.8638 | -0.091553 | 122.7448 | -0.013657 | -0.0032833 | 0.0013565 | -0.015306 | -0.00085021 | -0.010683 | -0.0070347 | -0.0021057 | 0.0089934 | 0.0016556 | -0.0045865 | -0.017355 | 0.021362 | -0.000784 | -0.036621 | 0.022888 | -0.091553 | -0.027466 | 0.13275 | -0.068665 | 0.009155 | 0.10986 | 0.050354 | -0.059509 | 0.036621 | 0.16479 | 0.064087 | 0.09613 | 0 | -122.7219 | -122.7722 | 0.2243 | 0.10071 | 0.022888 | 0.10071 | 0.022888 | 0.032044 | -122.6944 | -122.7081 | 0.25635 | 0.18768 | 0.15564 | 0.15564 | 0.1236 | 0.2243 | 0.064087 | 0.2243 | 0.09613 | 0.11444 | 0.10986 | 0.11444 | 0.14191 | -122.8363 | -122.8043 | 0.064087 | 0.12817 | 0.054932 | 0.20142
3818.7188 | 122.7676 | -0.1236 | 122.7768 | -0.013657 | -0.0032833 | 0.0015701 | -0.012956 | 0.0019268 | -0.011324 | -0.0057529 | -0.0051575 | 0.012411 | 0.001442 | -0.0028775 | -0.018209 | 0.022644 | -0.0009976 | -0.082397 | 0.064087 | -0.10071 | -0.10986 | -0.018311 | -0.1831 | -0.10071 | -0.068665 | 0.09613 | -0.10071 | -0.054932 | 0.041199 | -0.059509 | 0.027466 | 0.022888 | -122.7127 | -122.8867 | 0.10528 | 0.022888 | -0.059509 | 0 | -0.082397 | 0.022888 | -122.6807 | -122.8317 | 0.16479 | 0.15106 | 0.064087 | 0.12817 | 0.041199 | 0.082397 | -0.009155 | 0.14191 | 0.045776 | 0.1648 | 0.19684 | 0.18768 | 0.21973 | -122.8775 | -122.8775 | 0.013733 | 0.068664 | 0.041199 | 0.054931
3820.4375 | 122.8683 | -0.10071 | 122.7585 | -0.0060272 | -0.0084103 | 7.4854e-05 | -0.015733 | 0.0021406 | -0.012606 | -0.0040439 | -0.0021057 | 0.0094208 | 0.0029372 | 0.00032692 | -0.020132 | 0.02243 | 0.0004978 | -0.10071 | 0.036621 | -0.11902 | -0.082397 | 0.073242 | -0.10071 | 0 | 0.013733 | 0.068665 | -0.086975 | 0.004578 | 0.15106 | 0.036621 | 0.091553 | -0.018311 | -122.7219 | -122.8409 | 0.17395 | 0.10071 | 0 | 0.11902 | 0.018311 | 0.013733 | -122.6898 | -122.7539 | 0.25177 | 0.19226 | 0.13733 | 0.17853 | 0.1236 | 0.19226 | 0.036622 | 0.23804 | 0.091553 | 0.15564 | 0.15564 | 0.13733 | 0.16937 | -122.8775 | -122.8455 | 0.018311 | 0.10529 | 0 | 0.11444
3822.2031 | 122.8592 | -0.10529 | 122.7356 | -0.013657 | -0.0069149 | 0.0022111 | -0.015733 | -0.002132 | -0.010043 | -0.0076755 | 0.0039977 | 0.010275 | 0.00251 | -0.0090725 | -0.017141 | 0.02179 | -0.0022794 | -0.086975 | 0.027466 | -0.086975 | -0.068665 | 0.073242 | -0.09613 | -0.013733 | 0.018311 | 0.050354 | -0.086975 | -0.004578 | 0.13275 | 0.036621 | 0.091553 | 0.018311 | -122.7081 | -122.8043 | 0.17853 | 0.091553 | 0.009156 | 0.073242 | -0.009155 | 0.018311 | -122.6852 | -122.7402 | 0.23804 | 0.19684 | 0.14191 | 0.17853 | 0.1236 | 0.16022 | 0.01831 | 0.21973 | 0.082397 | 0.11444 | 0.13733 | 0.13275 | 0.15564 | -122.8226 | -122.8226 | 0.036621 | 0.10071 | 0.018311 | 0.1236
3823.9688 | 122.8043 | -0.11902 | 122.7768 | -0.013657 | -0.0052059 | -0.00099335 | -0.014879 | 0.0017132 | -0.010897 | -0.0078891 | -0.0082093 | 0.01348 | 0.0012282 | 0.0013949 | -0.020986 | 0.022003 | -0.003561 | -0.068665 | 0.059509 | -0.082397 | -0.054932 | 0.064087 | -0.11902 | -0.045776 | 0.045776 | 0.09613 | -0.10071 | -0.013733 | 0.09613 | -0.009155 | 0.059509 | 0.036622 | -122.7173 | -122.8317 | 0.18311 | 0.073243 | 0 | 0.036621 | -0.036622 | 0.018311 | -122.6807 | -122.7905 | 0.21515 | 0.17853 | 0.10986 | 0.16022 | 0.091553 | 0.14648 | 0.027465 | 0.19684 | 0.086975 | 0.14191 | 0.19684 | 0.17853 | 0.21515 | -122.8592 | -122.8775 | 0.064087 | 0.10529 | 0.050354 | 0.16479
3825.6719 | 122.905 | -0.059509 | 122.7448 | -0.013657 | -0.0081967 | -0.00099335 | -0.017015 | -0.0061908 | -0.011965 | -0.0042575 | -0.011261 | 0.0092072 | 0.00037383 | -0.0039457 | -0.018423 | 0.020508 | -0.004202 | -0.022888 | 0.022888 | -0.086975 | 0.009155 | 0.17853 | -0.004578 | 0.059509 | 0.11902 | 0.068665 | -0.068665 | 0.068665 | 0.23804 | 0.12817 | 0.11902 | -0.027466 | -122.7219 | -122.7356 | 0.23804 | 0.11902 | 0.054931 | 0.14648 | 0.082397 | -0.009156 | -122.6761 | -122.6761 | 0.29755 | 0.17853 | 0.18768 | 0.18768 | 0.19684 | 0.2655 | 0.09613 | 0.3067 | 0.13733 | 0.10986 | 0.13733 | 0.082397 | 0.12817 | -122.8317 | -122.8134 | 0.068664 | 0.12817 | 0.036621 | 0.17853
3827.375 | 122.9187 | -0.068665 | 122.7081 | -0.021286 | -0.0028561 | 0.0015701 | -0.014024 | 0.0038494 | -0.010043 | -0.0048985 | -0.011261 | 0.01113 | 0.0016556 | -0.0026639 | -0.018209 | 0.023071 | -0.003561 | -0.036621 | 0.009155 | -0.086975 | -0.004578 | 0.11902 | -0.073242 | 0.018311 | 0.10986 | 0.050354 | -0.073242 | 0.073242 | 0.1831 | 0.07782 | 0.13275 | -0.01831 | -122.699 | -122.7127 | 0.18768 | 0.086976 | -0.004577 | 0.10529 | 0.013733 | -0.004577 | -122.6578 | -122.6349 | 0.25177 | 0.20142 | 0.14649 | 0.20599 | 0.15106 | 0.20599 | 0.082397 | 0.25635 | 0.14648 | 0.09613 | 0.1236 | 0.07782 | 0.11902 | -122.7951 | -122.7814 | 0.064087 | 0.14191 | 0.032044 | 0.17853
3829.1406 | 122.8867 | -0.082397 | 122.7585 | -0.0060272 | -0.0090513 | 7.4854e-05 | -0.016588 | -0.00063661 | -0.013033 | -0.0059665 | -0.0082093 | 0.010489 | 0.00080103 | -0.00010048 | -0.018209 | 0.022003 | -0.0074064 | -0.045776 | 0.045776 | -0.07782 | 0.013733 | 0.15106 | -0.027466 | 0.045776 | 0.091553 | 0.082397 | -0.050354 | 0.041199 | 0.19226 | 0.09613 | 0.12817 | 0.004577 | -122.7127 | -122.7448 | 0.23346 | 0.12817 | 0.054931 | 0.1236 | 0.050354 | 0.032043 | -122.6761 | -122.7173 | 0.27466 | 0.21057 | 0.17853 | 0.17853 | 0.14648 | 0.22888 | 0.091553 | 0.24261 | 0.091553 | 0.1236 | 0.13275 | 0.12817 | 0.16479 | -122.8363 | -122.8088 | 0.09613 | 0.1236 | 0.036621 | 0.17395
3830.9062 | 122.7722 | -0.11444 | 122.7951 | -0.0060272 | -0.0071285 | -0.0041977 | -0.014665 | -0.00063661 | -0.011751 | -0.0053257 | -0.0021057 | 0.013693 | 0.0029372 | -0.0028775 | -0.020346 | 0.020935 | 0.0017794 | -0.09613 | 0.064087 | -0.10071 | -0.10071 | 0.022888 | -0.12817 | -0.041199 | -0.032043 | 0.11902 | -0.082397 | -0.059509 | 0.07782 | -0.022888 | 0.036621 | 0.013733 | -122.731 | -122.8958 | 0.13733 | 0.073242 | -0.013733 | 0.059509 | -0.027466 | 0.032044 | -122.6761 | -122.8546 | 0.19226 | 0.15106 | 0.091553 | 0.11902 | 0.059509 | 0.1236 | 0 | 0.16022 | 0.022888 | 0.1648 | 0.20142 | 0.17853 | 0.23346 | -122.8958 | -122.8775 | 0.013733 | 0.054932 | 0.018311 | 0.082398
3832.625 | 122.8271 | -0.086975 | 122.7768 | -0.028916 | -0.0054197 | 0.00028845 | -0.016161 | 0.001286 | -0.013247 | -0.0029759 | -0.0021057 | 0.012625 | 0.0010146 | 0.0033175 | -0.019705 | 0.022644 | -0.0033474 | -0.054932 | 0.068665 | -0.10071 | -0.073242 | 0.050354 | -0.10529 | -0.018311 | 0.032043 | 0.10986 | -0.086975 | 0.009155 | 0.11902 | 0.009155 | 0.086975 | -0.013733 | -122.7081 | -122.85 | 0.13733 | 0.068664 | -0.018311 | 0.082397 | -0.004578 | 0 | -122.6669 | -122.7676 | 0.20599 | 0.17395 | 0.09613 | 0.17395 | 0.09613 | 0.15106 | 0.027466 | 0.20599 | 0.09613 | 0.16937 | 0.19684 | 0.15564 | 0.19684 | -122.8775 | -122.8638 | 0.013733 | 0.09613 | 0.032043 | 0.11902
3834.4062 | 122.9233 | -0.07782 | 122.7173 | -0.013657 | -0.0092649 | -0.00035255 | -0.015306 | -0.00042301 | -0.010897 | -0.0040439 | -0.0082093 | 0.008139 | -5.3368e-05 | -0.0015957 | -0.017141 | 0.02243 | 7.04e-05 | -0.073242 | 0.036621 | -0.091553 | -0.027466 | 0.11902 | -0.050354 | 0.068665 | 0.068665 | 0.054932 | -0.082397 | 0.054932 | 0.21515 | 0.11444 | 0.13733 | -0.013733 | -122.6807 | -122.7448 | 0.19684 | 0.14649 | 0.027466 | 0.16022 | 0.041199 | -0.004577 | -122.6624 | -122.6624 | 0.29297 | 0.21515 | 0.19226 | 0.21973 | 0.19684 | 0.21057 | 0.064087 | 0.29755 | 0.13733 | 0.12817 | 0.13733 | 0.11444 | 0.13275 | -122.8088 | -122.7997 | 0.050354 | 0.13275 | 0.004578 | 0.14649
3836.1719 | 122.7859 | -0.11902 | 122.7997 | -0.0060272 | -0.0052059 | -0.0018479 | -0.012529 | -0.001491 | -0.012392 | -0.0059665 | -0.0051575 | 0.013693 | 0.00251 | -0.0041593 | -0.019491 | 0.023712 | 0.0017794 | -0.10986 | 0.082397 | -0.09613 | -0.10071 | 0.004578 | -0.12817 | -0.045776 | -0.045776 | 0.11444 | -0.10071 | -0.041199 | 0.082397 | -0.013733 | 0.050354 | 0.022889 | -122.7173 | -122.9004 | 0.1236 | 0.073243 | -0.009155 | 0.050354 | -0.032044 | 0.018311 | -122.6852 | -122.8409 | 0.20142 | 0.16937 | 0.10529 | 0.15106 | 0.086975 | 0.10071 | -0.004578 | 0.18311 | 0.059509 | 0.17853 | 0.21515 | 0.20142 | 0.23346 | -122.8958 | -122.9004 | 0.018311 | 0.07782 | 0.009156 | 0.073243
3837.9375 | 122.7722 | -0.091553 | 122.7905 | -0.013657 | -0.0079831 | -0.0027023 | -0.018938 | -0.0017048 | -0.010683 | -0.0040439 | -0.0082093 | 0.012411 | 0.0018692 | 0.0026767 | -0.017996 | 0.021149 | -0.0009976 | -0.054932 | 0.022888 | -0.068665 | -0.027466 | 0.086975 | -0.050354 | 0.032043 | 0.013733 | 0.09613 | -0.068665 | -0.027466 | 0.1236 | 0.036621 | 0.07782 | 0.022888 | -122.7676 | -122.818 | 0.17853 | 0.1236 | 0.041199 | 0.10071 | 0.018311 | 0.022888 | -122.6944 | -122.818 | 0.21515 | 0.16937 | 0.12817 | 0.14649 | 0.10529 | 0.15564 | 0.041199 | 0.19226 | 0.041199 | 0.091553 | 0.16479 | 0.11444 | 0.18768 | -122.8592 | -122.8592 | 0.064087 | 0.064087 | 0.036621 | 0.10529
3839.6562 | 122.9141 | -0.054932 | 122.7631 | -0.013657 | -0.0084103 | -0.00056615 | -0.013597 | -0.006618 | -0.011751 | -0.0059665 | -0.0082093 | 0.011771 | 0.0016556 | -0.0048001 | -0.017782 | 0.021149 | -0.0020658 | -0.022888 | 0.018311 | -0.07782 | 0 | 0.18768 | -0.004578 | 0.054932 | 0.13733 | 0.064087 | -0.064087 | 0.059509 | 0.2243 | 0.11444 | 0.14191 | -0.022888 | -122.7448 | -122.7631 | 0.24261 | 0.10986 | 0.050354 | 0.13275 | 0.073242 | -0.009155 | -122.699 | -122.7036 | 0.27924 | 0.19684 | 0.16937 | 0.20599 | 0.17853 | 0.2655 | 0.07782 | 0.28839 | 0.1236 | 0.096131 | 0.12817 | 0.073243 | 0.11902 | -122.8409 | -122.8271 | 0.054932 | 0.11444 | 0.032044 | 0.19226
3841.3594 | 122.8592 | -0.086975 | 122.7356 | -0.021286 | -0.0075559 | 7.4854e-05 | -0.015306 | -0.0027728 | -0.011324 | -0.0040439 | -0.0082093 | 0.0092072 | 0.0018692 | 0.0045993 | -0.017996 | 0.022003 | -0.0005704 | -0.086975 | 0.018311 | -0.09613 | -0.064087 | 0.050354 | -0.10071 | -0.018311 | 0.013733 | 0.073242 | -0.073242 | 0.009155 | 0.14648 | 0.045776 | 0.091553 | -0.009155 | -122.7173 | -122.7997 | 0.13733 | 0.068664 | -0.013733 | 0.077819 | -0.004578 | 0.013733 | -122.6624 | -122.7264 | 0.23346 | 0.17853 | 0.13275 | 0.16479 | 0.11902 | 0.14648 | 0.032043 | 0.21973 | 0.082397 | 0.11444 | 0.14648 | 0.10529 | 0.16022 | -122.8317 | -122.8088 | 0.022888 | 0.09613 | 0 | 0.10071
3843.1094 | 122.8867 | -0.082397 | 122.7264 | -0.013657 | -0.0026425 | 0.0028519 | -0.015947 | -0.0029864 | -0.011324 | -0.0053257 | -0.0082093 | 0.012411 | 0.00251 | -0.00031408 | -0.020132 | 0.022003 | -0.0022794 | -0.022888 | 0.004578 | -0.068665 | -0.004578 | 0.12817 | -0.073242 | 0.022888 | 0.11902 | 0.054932 | -0.073242 | 0.054932 | 0.16022 | 0.073242 | 0.10986 | 0.013732 | -122.7219 | -122.731 | 0.21057 | 0.10528 | 0.009155 | 0.091553 | -0.004577 | 0.009155 | -122.6715 | -122.6715 | 0.24261 | 0.19226 | 0.15564 | 0.18311 | 0.14648 | 0.19684 | 0.064087 | 0.23346 | 0.12817 | 0.073243 | 0.12817 | 0.086975 | 0.13733 | -122.7951 | -122.7997 | 0.077819 | 0.13733 | 0.059509 | 0.20142
3844.875 | 122.7814 | -0.09613 | 122.7631 | -0.036545 | -0.0022153 | 0.0013565 | -0.011461 | 0.00043159 | -0.012606 | -0.0059665 | -0.0021057 | 0.01412 | 0.00251 | -0.0033047 | -0.020346 | 0.019653 | -0.0018522 | -0.059509 | 0.059509 | -0.10986 | -0.073242 | 0.027466 | -0.12817 | -0.050354 | 0.009155 | 0.10986 | -0.07782 | -0.027466 | 0.068665 | -0.050354 | 0.032043 | -0.013733 | -122.7036 | -122.8363 | 0.1236 | 0.045776 | -0.032044 | 0.059509 | -0.018311 | 0.01831 | -122.6532 | -122.7905 | 0.16479 | 0.12817 | 0.045776 | 0.10986 | 0.027466 | 0.13733 | 0.036621 | 0.14649 | 0.050354 | 0.16937 | 0.18768 | 0.15564 | 0.20599 | -122.8729 | -122.8409 | 0.022888 | 0.068664 | 0.036621 | 0.10528
3846.6406 | 122.8912 | -0.07782 | 122.7402 | -0.013657 | -0.0064877 | 0.0019975 | -0.016161 | -0.0032 | -0.01047 | -0.0068211 | -0.0082093 | 0.010702 | 0.0018692 | -0.0056547 | -0.018637 | 0.023285 | -0.000784 | -0.082397 | 0.036621 | -0.086975 | -0.045776 | 0.091553 | -0.082397 | 0.009155 | 0.050354 | 0.059509 | -0.068665 | 0.041199 | 0.17395 | 0.082397 | 0.13275 | -0.009155 | -122.7036 | -122.7859 | 0.16937 | 0.086975 | -0.004577 | 0.09613 | 0.004578 | 0.009155 | -122.6807 | -122.699 | 0.25177 | 0.21057 | 0.16022 | 0.20142 | 0.15106 | 0.17853 | 0.041199 | 0.24261 | 0.10986 | 0.1236 | 0.12817 | 0.11444 | 0.13733 | -122.8271 | -122.8088 | 0.032044 | 0.11902 | -0.004577 | 0.12817
3848.3906 | 122.9095 | -0.068665 | 122.7493 | -0.021286 | -0.0041379 | -0.0018479 | -0.016161 | -0.0064044 | -0.010256 | -0.0046847 | -0.011261 | 0.0085662 | -0.0015488 | -0.0092863 | -0.020559 | 0.023712 | -0.0020658 | -0.027466 | 0.041199 | -0.073242 | 0.013733 | 0.15564 | -0.009155 | 0.059509 | 0.1236 | 0.07782 | -0.064087 | 0.068665 | 0.21515 | 0.11444 | 0.13733 | -0.004577 | -122.7081 | -122.7356 | 0.22431 | 0.12817 | 0.05951 | 0.13275 | 0.064087 | 0.004578 | -122.6715 | -122.6807 | 0.28381 | 0.20599 | 0.18311 | 0.20142 | 0.17853 | 0.22888 | 0.086975 | 0.27924 | 0.13275 | 0.11444 | 0.14191 | 0.10986 | 0.14649 | -122.8226 | -122.8134 | 0.082398 | 0.13733 | 0.041199 | 0.19226
3850.0938 | 122.8455 | -0.013733 | 122.8867 | -0.0060272 | -0.0069149 | 7.4854e-05 | -0.014024 | -0.00085021 | -0.011538 | -0.0038303 | -0.0021057 | 0.012198 | 0.0020828 | 0.0016085 | -0.019064 | 0.021149 | -0.005911 | 0.027466 | 0.1831 | 0.022888 | 0.022888 | 0.14191 | -0.009155 | 0.041199 | 0.09613 | 0.20142 | 0.032043 | 0.086975 | 0.20142 | 0.10071 | 0.15564 | 0.036621 | -122.7036 | -122.8638 | 0.15564 | 0.054932 | 0.004578 | 0.018311 | -0.032043 | 0.045776 | -122.6852 | -122.7997 | 0.21515 | 0.16937 | 0.11444 | 0.1236 | 0.068665 | 0.11902 | 0 | 0.16937 | 0.054932 | 0.16022 | 0.16937 | 0.19684 | 0.21515 | -122.8638 | -122.8546 | 0.036621 | 0.10071 | 0.041199 | 0.10986
3851.8594 | 122.7676 | -0.10986 | 122.7951 | -0.021286 | -0.0022153 | 0.0024247 | -0.012315 | -0.0012774 | -0.011751 | -0.0014805 | -0.0051575 | 0.011984 | 0.0018692 | 0.0031039 | -0.016287 | 0.022858 | -0.0031338 | -0.073242 | 0.082397 | -0.09613 | -0.10071 | 0.027466 | -0.16022 | -0.073242 | -0.018311 | 0.10529 | -0.10071 | -0.045776 | 0.059509 | -0.059509 | 0.027466 | 0.013733 | -122.7127 | -122.8958 | 0.13733 | 0.036621 | -0.050354 | 0.022888 | -0.064087 | 0.009155 | -122.6898 | -122.8409 | 0.16937 | 0.13733 | 0.050354 | 0.12817 | 0.041199 | 0.1236 | -0.004578 | 0.16022 | 0.054932 | 0.17853 | 0.20599 | 0.19226 | 0.21515 | -122.8912 | -122.8958 | 0.009155 | 0.064087 | 0.036621 | 0.091552
3853.5625 | 122.9279 | -0.086975 | 122.7539 | -0.013657 | -0.0084103 | 0.00028845 | -0.016374 | -0.00020941 | -0.01047 | -0.0051121 | -0.0082093 | 0.010275 | 0.0050736 | 0.00011332 | -0.017568 | 0.023499 | -0.0054838 | -0.064087 | 0.032043 | -0.091553 | -0.045776 | 0.10529 | -0.059509 | 0.032043 | 0.07782 | 0.068665 | -0.068665 | 0.059509 | 0.20599 | 0.11444 | 0.14191 | -0.004578 | -122.7219 | -122.7997 | 0.19226 | 0.11902 | 0.027466 | 0.1236 | 0.032044 | 0.01831 | -122.6852 | -122.6944 | 0.29297 | 0.22888 | 0.20142 | 0.21057 | 0.18311 | 0.19684 | 0.045777 | 0.27466 | 0.12817 | 0.1236 | 0.13733 | 0.11902 | 0.15564 | -122.8455 | -122.8226 | 0.041199 | 0.14648 | 0.022888 | 0.16479
3855.3438 | 122.9141 | -0.073242 | 122.7539 | -0.021286 | -0.0037107 | -0.0020615 | -0.013384 | 0.0032086 | -0.011111 | -0.0046847 | -0.0082093 | 0.011343 | 0.00016023 | 0.0024631 | -0.020132 | 0.024567 | -0.0016384 | -0.07782 | 0.059509 | -0.091553 | -0.050354 | 0.07782 | -0.10071 | -0.018311 | 0.064087 | 0.091553 | -0.086975 | 0.07782 | 0.16937 | 0.054932 | 0.13275 | -0.018311 | -122.6944 | -122.8043 | 0.15106 | 0.054931 | -0.027466 | 0.073242 | -0.009155 | -0.013733 | -122.6624 | -122.6761 | 0.24261 | 0.20599 | 0.12817 | 0.21973 | 0.14191 | 0.16937 | 0.041199 | 0.25635 | 0.16479 | 0.15106 | 0.17853 | 0.13275 | 0.16479 | -122.8455 | -122.8409 | 0.022888 | 0.15106 | -0.004578 | 0.13733
3857.1094 | 122.8729 | -0.064087 | 122.7539 | -0.013657 | -0.0039243 | 0.00050205 | -0.014024 | 0.0010724 | -0.0096151 | -0.0059665 | -0.0082093 | 0.010702 | 0.00016023 | -0.0094999 | -0.019064 | 0.021149 | -0.0056974 | -0.064087 | 0.022888 | -0.064087 | -0.027466 | 0.11444 | -0.10529 | 0.009155 | 0.068665 | 0.059509 | -0.064087 | 0.032043 | 0.15106 | 0.068665 | 0.10529 | 0 | -122.731 | -122.7814 | 0.17853 | 0.073242 | -0.041199 | 0.073242 | -0.041199 | 0 | -122.6944 | -122.7219 | 0.21515 | 0.16937 | 0.13275 | 0.16937 | 0.13275 | 0.17853 | 0.036621 | 0.21515 | 0.09613 | 0.086975 | 0.1236 | 0.086975 | 0.1236 | -122.818 | -122.818 | 0.036621 | 0.09613 | 0 | 0.13275
3858.8125 | 122.8088 | -0.10529 | 122.7859 | -0.013657 | -0.0041379 | 7.4854e-05 | -0.011888 | 4.192e-06 | -0.010043 | -0.0019077 | -0.011261 | 0.01348 | 0.0033646 | 0.0013949 | -0.021841 | 0.023926 | -0.0009976 | -0.10071 | 0.07782 | -0.13733 | -0.13275 | -0.013733 | -0.1831 | -0.082397 | -0.045776 | 0.09613 | -0.086975 | -0.027466 | 0.054932 | -0.036621 | 0.041199 | -0.032043 | -122.7081 | -122.9187 | 0.091553 | 0.022889 | -0.077819 | 0.054932 | -0.045776 | 0.018311 | -122.6898 | -122.8134 | 0.16022 | 0.14649 | 0.068665 | 0.12817 | 0.050354 | 0.1236 | 0.004578 | 0.14191 | 0.059509 | 0.21515 | 0.1831 | 0.18311 | 0.20142 | -122.9233 | -122.8729 | -0.027465 | 0.07782 | 0.004578 | 0.05951
3860.5781 | 122.9233 | -0.086975 | 122.7493 | -0.021286 | -0.0067013 | -0.0016341 | -0.016801 | 0.00021799 | -0.011538 | -0.0038303 | -0.0051575 | 0.010702 | 0.0022964 | -0.0065091 | -0.020986 | 0.022217 | 0.0013522 | -0.041199 | 0.032043 | -0.091553 | 0.013733 | 0.1831 | -0.009155 | 0.07782 | 0.10986 | 0.068665 | -0.054932 | 0.064087 | 0.21973 | 0.11902 | 0.13733 | -0.004578 | -122.7173 | -122.7356 | 0.27008 | 0.16479 | 0.07782 | 0.16937 | 0.082398 | 0.032043 | -122.6807 | -122.6852 | 0.3067 | 0.2243 | 0.20599 | 0.19226 | 0.17395 | 0.27466 | 0.10529 | 0.27466 | 0.11902 | 0.1236 | 0.1236 | 0.11902 | 0.15564 | -122.8409 | -122.8043 | 0.10071 | 0.15106 | 0.045776 | 0.19684
3862.3438 | 122.7997 | -0.10986 | 122.7814 | -0.021286 | -0.0045651 | 0.00092925 | -0.014238 | -0.0010638 | -0.011324 | -0.0016941 | -0.0082093 | 0.013266 | 0.0035782 | 0.0056675 | -0.020559 | 0.022217 | -0.0027066 | -0.09613 | 0.073242 | -0.11902 | -0.12817 | -0.009155 | -0.17395 | -0.068665 | -0.032043 | 0.10529 | -0.09613 | -0.022888 | 0.064087 | -0.054932 | 0.054932 | -0.009156 | -122.7081 | -122.9095 | 0.10071 | 0.041198 | -0.064087 | 0.050354 | -0.054931 | 0.013733 | -122.6761 | -122.8043 | 0.17395 | 0.16479 | 0.054931 | 0.15106 | 0.041198 | 0.10986 | -0.009155 | 0.16022 | 0.073242 | 0.19226 | 0.20142 | 0.18311 | 0.21515 | -122.9004 | -122.8775 | -0.018311 | 0.086975 | 0.013733 | 0.07782
3864.1094 | 122.8638 | -0.07782 | 122.7539 | -0.021286 | -0.0071285 | 0.00092925 | -0.014665 | -0.00020941 | -0.011751 | -0.0036167 | -0.0051575 | 0.010916 | 0.0016556 | -0.0020231 | -0.01885 | 0.021576 | -0.0022794 | -0.091553 | 0.036621 | -0.07782 | -0.064087 | 0.082397 | -0.09613 | 0 | 0.013733 | 0.064087 | -0.082397 | 0.009155 | 0.12817 | 0.041199 | 0.09613 | 0 | -122.7173 | -122.818 | 0.16022 | 0.07782 | -0.01831 | 0.07782 | -0.01831 | -0.004577 | -122.6898 | -122.7448 | 0.20599 | 0.17395 | 0.11902 | 0.17853 | 0.1236 | 0.16022 | 0.013733 | 0.21057 | 0.091552 | 0.11444 | 0.14648 | 0.11444 | 0.14191 | -122.8317 | -122.8363 | 0.013733 | 0.086975 | -0.013733 | 0.091553
3865.875 | 122.8317 | -0.14191 | 122.7997 | -0.021286 | -0.0069149 | -0.0014205 | -0.015947 | 0.0032086 | -0.013033 | -0.0057529 | -0.0082093 | 0.011984 | 0.0012282 | 0.00032692 | -0.019705 | 0.022858 | -0.004202 | -0.09613 | 0.064087 | -0.13275 | -0.10986 | 0 | -0.12817 | -0.054932 | -0.041199 | 0.10071 | -0.09613 | -0.027466 | 0.09613 | 0 | 0.054932 | 0.009156 | -122.7356 | -122.9095 | 0.14191 | 0.086975 | 0.013733 | 0.077819 | 0.004577 | 0.045777 | -122.699 | -122.8271 | 0.23804 | 0.19684 | 0.14191 | 0.15106 | 0.09613 | 0.13275 | 0.022888 | 0.19226 | 0.068664 | 0.19684 | 0.19684 | 0.20599 | 0.24262 | -122.9324 | -122.8958 | 0.032044 | 0.11444 | 0.045777 | 0.10071
3867.6406 | 122.8226 | -0.11902 | 122.7722 | -0.0060272 | -0.0060605 | -0.0014205 | -0.015093 | -0.0027728 | -0.012606 | -0.0046847 | -0.011261 | 0.011984 | 0.003151 | 0.00054052 | -0.019064 | 0.022003 | -0.003561 | -0.054932 | 0.036621 | -0.086975 | -0.041199 | 0.091553 | -0.068665 | 0.013733 | 0.027466 | 0.10529 | -0.09613 | -0.013733 | 0.10986 | 0.009155 | 0.059509 | 0.032044 | -122.7356 | -122.8134 | 0.21057 | 0.13275 | 0.050354 | 0.10071 | 0.01831 | 0.022889 | -122.6669 | -122.7859 | 0.22888 | 0.17853 | 0.12817 | 0.15564 | 0.10528 | 0.17853 | 0.045776 | 0.20599 | 0.082397 | 0.1236 | 0.20142 | 0.15564 | 0.22431 | -122.8592 | -122.8683 | 0.07782 | 0.10529 | 0.064087 | 0.14649
3869.3281 | 122.9187 | -0.068665 | 122.731 | -0.013657 | -0.0041379 | -0.00077975 | -0.014024 | -0.0040546 | -0.010897 | -0.0091709 | -0.0051575 | 0.011984 | -5.3368e-05 | -0.0045865 | -0.019491 | 0.024567 | 0.0015658 | -0.022888 | 0.009155 | -0.073242 | 0.004578 | 0.13733 | -0.059509 | 0.036621 | 0.11444 | 0.068665 | -0.045776 | 0.059509 | 0.18768 | 0.068665 | 0.14191 | -0.004577 | -122.7219 | -122.7264 | 0.20599 | 0.10529 | 0.009156 | 0.10986 | 0.013733 | 0.022889 | -122.6624 | -122.6715 | 0.25635 | 0.21057 | 0.13733 | 0.18768 | 0.11444 | 0.21057 | 0.07782 | 0.23346 | 0.10528 | 0.082397 | 0.11444 | 0.07782 | 0.13733 | -122.8043 | -122.7768 | 0.073243 | 0.12817 | 0.045777 | 0.18311
3871.1094 | 122.8546 | -0.091553 | 122.7493 | -0.013657 | -0.0047787 | -0.00056615 | -0.014238 | 0.001286 | -0.01047 | -0.0068211 | 0.0009461 | 0.010275 | 0.0010146 | 0.0016085 | -0.019064 | 0.02179 | -0.005911 | -0.10529 | 0.07782 | -0.11902 | -0.10986 | 0.013733 | -0.16022 | -0.068665 | -0.004578 | 0.082397 | -0.091553 | 0.009155 | 0.11444 | 0 | 0.082397 | -0.027466 | -122.6715 | -122.8592 | 0.10529 | 0.022888 | -0.068664 | 0.050354 | -0.041198 | 0 | -122.6669 | -122.7402 | 0.20599 | 0.17395 | 0.091553 | 0.17395 | 0.091553 | 0.13275 | 0.009156 | 0.20599 | 0.10071 | 0.19684 | 0.17395 | 0.16937 | 0.17395 | -122.8683 | -122.8409 | -0.01831 | 0.10071 | -0.013733 | 0.086975
3872.8125 | 122.9416 | -0.086975 | 122.7493 | -0.013657 | -0.0079831 | 7.4854e-05 | -0.016588 | 0.00043159 | -0.014101 | -0.0034031 | -0.0082093 | 0.0089934 | 0.001442 | -0.0084317 | -0.019491 | 0.02179 | -0.0046292 | -0.059509 | 0.013733 | -0.064087 | 0.013733 | 0.16022 | -0.009155 | 0.059509 | 0.14191 | 0.054932 | -0.068665 | 0.091553 | 0.22888 | 0.13275 | 0.16022 | 0.022888 | -122.7356 | -122.7356 | 0.24719 | 0.14648 | 0.07782 | 0.1236 | 0.054932 | 0.01831 | -122.6944 | -122.6578 | 0.31586 | 0.24719 | 0.21973 | 0.22888 | 0.20142 | 0.2243 | 0.07782 | 0.29755 | 0.16022 | 0.07782 | 0.1236 | 0.10071 | 0.14191 | -122.8134 | -122.818 | 0.10071 | 0.17853 | 0.027466 | 0.22888
3874.5781 | 122.8821 | -0.09613 | 122.7814 | -0.021286 | -0.0075559 | -0.00099335 | -0.013384 | 0.00043159 | -0.010256 | -0.0053257 | -0.0082093 | 0.01113 | -0.00026697 | -0.0033047 | -0.021841 | 0.022003 | -0.0031338 | -0.07782 | 0.045776 | -0.07782 | -0.059509 | 0.068665 | -0.091553 | -0.004578 | 0.022888 | 0.073242 | -0.07782 | 0.013733 | 0.14191 | 0.032043 | 0.086975 | 0.01831 | -122.7356 | -122.8409 | 0.16479 | 0.091552 | 0.004577 | 0.073242 | -0.013733 | 0.01831 | -122.7081 | -122.7676 | 0.23804 | 0.1831 | 0.12817 | 0.16479 | 0.10986 | 0.14649 | 0.018311 | 0.21973 | 0.091553 | 0.1236 | 0.15106 | 0.14191 | 0.16937 | -122.8592 | -122.8592 | 0.036621 | 0.10986 | 0.01831 | 0.11902
3876.2812 | 122.818 | -0.091553 | 122.7997 | -0.021286 | -0.0022153 | 0.00028845 | -0.012956 | 0.002995 | -0.010683 | -0.0048985 | -0.0082093 | 0.01348 | 0.003151 | 0.0028903 | -0.019918 | 0.016663 | -0.003561 | -0.064087 | 0.045776 | -0.09613 | -0.068665 | 0.041199 | -0.1236 | -0.045776 | 0.018311 | 0.10986 | -0.082397 | -0.004578 | 0.091553 | -0.027466 | 0.059509 | -0.004577 | -122.7539 | -122.8683 | 0.13275 | 0.045777 | -0.032043 | 0.050354 | -0.027466 | 0.009156 | -122.6898 | -122.8043 | 0.18311 | 0.15106 | 0.064087 | 0.14191 | 0.054931 | 0.13733 | 0.027465 | 0.17395 | 0.077819 | 0.14191 | 0.19226 | 0.13733 | 0.20142 | -122.8958 | -122.8821 | 0.022888 | 0.086975 | 0.027466 | 0.10986
3878.0469 | 122.9324 | -0.082397 | 122.7722 | -0.013657 | -0.0028561 | 7.4854e-05 | -0.015306 | 0.00043159 | -0.0096151 | -0.0070347 | -0.0051575 | 0.0092072 | 0.003151 | -0.0028775 | -0.019277 | 0.022217 | -0.0022794 | -0.018311 | 0.027466 | -0.091553 | 0.004578 | 0.13275 | -0.068665 | 0.027466 | 0.11444 | 0.059509 | -0.068665 | 0.091553 | 0.18768 | 0.07782 | 0.15106 | -0.009156 | -122.7448 | -122.7676 | 0.21515 | 0.10986 | 0.013732 | 0.11902 | 0.022888 | 0.013732 | -122.7127 | -122.6807 | 0.27008 | 0.23346 | 0.16022 | 0.21973 | 0.14649 | 0.2243 | 0.096131 | 0.25635 | 0.16022 | 0.11902 | 0.12817 | 0.10986 | 0.14191 | -122.8638 | -122.8409 | 0.086975 | 0.17395 | 0.064086 | 0.19684
3879.7969 | 122.9553 | -0.07782 | 122.7448 | -0.013657 | -0.0088375 | -0.0018479 | -0.016801 | -0.0010638 | -0.010043 | -0.0042575 | -0.0051575 | 0.0089934 | 0.00251 | -0.0030911 | -0.016714 | 0.022217 | 0.0011386 | -0.045776 | 0.022888 | -0.082397 | 0.022888 | 0.1831 | 0.013733 | 0.07782 | 0.11444 | 0.082397 | -0.082397 | 0.059509 | 0.21515 | 0.11444 | 0.13733 | -0.004577 | -122.7219 | -122.7219 | 0.26092 | 0.15564 | 0.091553 | 0.16022 | 0.09613 | -0.004577 | -122.6624 | -122.6852 | 0.29297 | 0.21515 | 0.19226 | 0.21973 | 0.19684 | 0.2655 | 0.10528 | 0.29755 | 0.14191 | 0.10528 | 0.16479 | 0.10071 | 0.16022 | -122.8271 | -122.8271 | 0.10071 | 0.13733 | 0.032044 | 0.19226
3881.5625 | 122.8271 | -0.10071 | 122.7951 | -0.013657 | -0.0069149 | -0.00035255 | -0.015947 | -0.0027728 | -0.011965 | -0.0068211 | -0.0082093 | 0.011771 | 0.00058743 | -0.0033047 | -0.018209 | 0.023712 | -0.0005704 | -0.041199 | 0.032043 | -0.07782 | -0.036621 | 0.10529 | -0.054932 | 0.009155 | 0.045776 | 0.07782 | -0.082397 | -0.018311 | 0.11444 | 0.004578 | 0.054932 | 0.022888 | -122.7631 | -122.8317 | 0.20599 | 0.10986 | 0.045776 | 0.086975 | 0.022888 | 0.018311 | -122.7173 | -122.8134 | 0.21515 | 0.15564 | 0.10529 | 0.13733 | 0.086975 | 0.18311 | 0.041199 | 0.19684 | 0.064086 | 0.10986 | 0.16022 | 0.13275 | 0.17853 | -122.8729 | -122.8775 | 0.064087 | 0.082397 | 0.059509 | 0.14648
3883.3281 | 122.8729 | -0.091553 | 122.7768 | -0.021286 | -0.0064877 | -0.00035255 | -0.015733 | 0.0010724 | -0.012606 | -0.0057529 | -0.0051575 | 0.0092072 | 0.00058743 | -0.012063 | -0.019491 | 0.019012 | 0.0028476 | -0.041199 | 0.018311 | -0.086975 | -0.013733 | 0.1236 | -0.032043 | 0.050354 | 0.068665 | 0.068665 | -0.082397 | 0.013733 | 0.15106 | 0.059509 | 0.091553 | 0.004578 | -122.7585 | -122.7905 | 0.21515 | 0.14191 | 0.05951 | 0.13733 | 0.054932 | 0.009156 | -122.7081 | -122.7631 | 0.24261 | 0.18311 | 0.15106 | 0.17395 | 0.14191 | 0.21057 | 0.073242 | 0.23346 | 0.09613 | 0.10529 | 0.15106 | 0.10986 | 0.16022 | -122.8638 | -122.8592 | 0.07782 | 0.10529 | 0.050354 | 0.16022
3885.0938 | 122.8775 | -0.082397 | 122.7859 | -0.028916 | -0.0039243 | -0.0014205 | -0.016161 | -0.0012774 | -0.011751 | -0.0042575 | -0.0082093 | 0.010916 | 0.0010146 | -0.0088589 | -0.020132 | 0.022217 | -0.003561 | -0.082397 | 0.036621 | -0.082397 | -0.050354 | 0.064087 | -0.10986 | -0.004578 | 0.022888 | 0.068665 | -0.07782 | 0.022888 | 0.14648 | 0.041199 | 0.10071 | 0 | -122.7493 | -122.8363 | 0.14648 | 0.077819 | -0.027466 | 0.077819 | -0.027466 | 0.004577 | -122.7173 | -122.7631 | 0.22888 | 0.18311 | 0.1236 | 0.17853 | 0.11902 | 0.14648 | 0.032043 | 0.2243 | 0.10071 | 0.11902 | 0.14649 | 0.11902 | 0.15106 | -122.8683 | -122.8638 | 0.032043 | 0.10528 | 0 | 0.10528
3886.7812 | 122.818 | -0.1236 | 122.7768 | -0.021286 | -0.0071285 | -0.00013895 | -0.015947 | 0.0038494 | -0.01282 | -0.0053257 | -0.0051575 | 0.011771 | 0.0022964 | 0.00032692 | -0.020559 | 0.022003 | -0.003561 | -0.1236 | 0.086975 | -0.12817 | -0.13733 | -0.004578 | -0.14648 | -0.045776 | -0.054932 | 0.10071 | -0.10986 | -0.059509 | 0.073242 | -0.027466 | 0.032043 | -0.004578 | -122.6898 | -122.9141 | 0.11902 | 0.07782 | -0.022888 | 0.082398 | -0.01831 | 0.013733 | -122.6761 | -122.8363 | 0.19684 | 0.15564 | 0.09613 | 0.14191 | 0.082397 | 0.1236 | -0.009155 | 0.18311 | 0.050354 | 0.21515 | 0.21057 | 0.21057 | 0.2243 | -122.905 | -122.8867 | -0.013733 | 0.064087 | 0 | 0.068664
3888.5312 | 122.8546 | -0.11444 | 122.8043 | -0.013657 | -0.0064877 | -0.0018479 | -0.01317 | -0.00063661 | -0.012606 | -0.0038303 | -0.0082093 | 0.012411 | 0.0016556 | 0.0058811 | -0.01885 | 0.023285 | -0.0014248 | -0.091553 | 0.054932 | -0.11902 | -0.09613 | 0.009155 | -0.11444 | -0.050354 | -0.004578 | 0.10071 | -0.10529 | 0 | 0.11902 | 0.004578 | 0.073242 | -0.004578 | -122.7493 | -122.9004 | 0.1236 | 0.064087 | 0 | 0.068665 | 0.004578 | 0.009155 | -122.7036 | -122.8043 | 0.23346 | 0.18768 | 0.11902 | 0.17853 | 0.10986 | 0.12817 | 0.022889 | 0.22431 | 0.10529 | 0.17395 | 0.20599 | 0.16937 | 0.21515 | -122.9233 | -122.9095 | 0.018311 | 0.11444 | 0.022888 | 0.10986
3890.2344 | 122.8134 | -0.10529 | 122.8134 | -0.028916 | -0.0041379 | 0.0022111 | -0.011034 | 0.0027814 | -0.010043 | -0.0048985 | -0.0082093 | 0.010916 | 0.0029372 | -0.00052768 | -0.018637 | 0.021362 | -0.0046292 | -0.054932 | 0.073242 | -0.1236 | -0.09613 | 0.032043 | -0.13733 | -0.064087 | 0 | 0.10529 | -0.09613 | -0.027466 | 0.073242 | -0.036621 | 0.041199 | -0.01831 | -122.7402 | -122.9095 | 0.13733 | 0.041199 | -0.032043 | 0.059509 | -0.013733 | 0.009156 | -122.7081 | -122.8409 | 0.17853 | 0.14649 | 0.068665 | 0.13733 | 0.059509 | 0.15564 | 0.027466 | 0.16937 | 0.068664 | 0.19684 | 0.20142 | 0.17853 | 0.21057 | -122.937 | -122.9095 | 0.009156 | 0.07782 | 0.050354 | 0.10529
3891.9844 | 122.8134 | -0.091553 | 122.8043 | -0.013657 | -0.0041379 | 7.4854e-05 | -0.01317 | -0.0019184 | -0.0085471 | -0.0044711 | -0.0082093 | 0.01348 | 0.001442 | -0.0013821 | -0.016928 | 0.023926 | 0.0002842 | -0.082397 | 0.045776 | -0.10529 | -0.09613 | 0.013733 | -0.17853 | -0.073242 | -0.036621 | 0.10071 | -0.10071 | -0.045776 | 0.064087 | -0.059509 | 0.045776 | -0.013733 | -122.7585 | -122.9004 | 0.10529 | 0.018311 | -0.086975 | 0.032044 | -0.073242 | -0.009155 | -122.7036 | -122.85 | 0.15564 | 0.13733 | 0.032044 | 0.14648 | 0.041199 | 0.11902 | 0.009156 | 0.1648 | 0.054932 | 0.15106 | 0.20142 | 0.13733 | 0.19226 | -122.9095 | -122.905 | -0.004577 | 0.045777 | 0.009156 | 0.054932
3893.75 | 122.9233 | -0.07782 | 122.7356 | -0.0060272 | -0.0049923 | -0.0016341 | -0.016588 | 0.0010724 | -0.0094015 | -0.0087437 | -0.0082093 | 0.0083526 | 0.0027236 | -0.0043729 | -0.019064 | 0.020081 | 0.0002842 | -0.045776 | 0.027466 | -0.082397 | 0.004578 | 0.15564 | -0.059509 | 0.032043 | 0.10071 | 0.064087 | -0.07782 | 0.068665 | 0.18768 | 0.086975 | 0.11444 | -0.004577 | -122.7081 | -122.731 | 0.23346 | 0.10986 | 0.018311 | 0.11444 | 0.022888 | 0 | -122.6715 | -122.6669 | 0.2655 | 0.19226 | 0.16479 | 0.19226 | 0.16479 | 0.23804 | 0.086975 | 0.2655 | 0.14649 | 0.10986 | 0.14191 | 0.10529 | 0.14191 | -122.818 | -122.8134 | 0.082398 | 0.14649 | 0.032044 | 0.17853
3895.5156 | 122.8592 | -0.11444 | 122.8317 | -0.021286 | -0.0062741 | -0.00077975 | -0.014024 | 0.0023542 | -0.011538 | -0.0061801 | -0.0021057 | 0.012625 | 0.0027236 | -0.00052768 | -0.0212 | 0.024353 | -0.002493 | -0.07782 | 0.073242 | -0.11902 | -0.073242 | 0.045776 | -0.11444 | -0.045776 | 0.018311 | 0.10986 | -0.10529 | 0.009155 | 0.13275 | 0.022888 | 0.082397 | -0.004578 | -122.7585 | -122.905 | 0.16022 | 0.068665 | 0 | 0.073243 | 0.004578 | 0.009155 | -122.7219 | -122.8226 | 0.24719 | 0.19684 | 0.13733 | 0.18768 | 0.12817 | 0.16479 | 0.045777 | 0.23804 | 0.11444 | 0.19226 | 0.21515 | 0.18768 | 0.2243 | -122.9507 | -122.937 | 0.041199 | 0.1236 | 0.036621 | 0.13275

## Thermal Data
Fire Time | B Position - Middle | D Position - 3' | D Position - Middle | D Position - 7'
-0.0583 | 11.5619 | 11.8028 | 11.4754 | 11.3328
0.9417 | 11.5572 | 11.7919 | 11.4776 | 11.3396
1.9417 | 11.5493 | 11.791 | 11.4738 | 11.3432
2.9417 | 11.5643 | 11.7938 | 11.473 | 11.3362
3.9417 | 11.5625 | 11.8975 | 11.6364 | 11.3356
4.9417 | 11.5861 | 11.8908 | 11.7283 | 11.3602
5.9417 | 11.5821 | 11.9285 | 12.1803 | 11.4919
6.9417 | 11.5964 | 12.4525 | 13.1849 | 11.9841
7.9417 | 11.6636 | 13.4049 | 14.9767 | 12.8124
8.9417 | 12.0506 | 15.2439 | 17.3875 | 13.8912
9.9417 | 12.7602 | 16.837 | 20.8801 | 15.0979
10.9417 | 14.019 | 18.7787 | 22.8732 | 15.9998
11.9417 | 14.8174 | 20.9919 | 25.639 | 17.595
12.9417 | 16.2291 | 23.1498 | 27.4367 | 18.9792
13.9417 | 17.593 | 24.7058 | 29.2454 | 20.1379
14.9417 | 18.8965 | 27.4029 | 32.1325 | 21.894
15.9417 | 20.493 | 29.2854 | 33.9997 | 24.117
16.9417 | 21.8667 | 30.9587 | 35.3315 | 26.057
17.9417 | 24.054 | 35.309 | 40.8634 | 28.8808
18.9417 | 25.0599 | 35.879 | 40.6854 | 30.2624
19.9417 | 27.9298 | 38.8776 | 43.447 | 31.9071
20.9417 | 31.637 | 46.9869 | 53.1825 | 33.6822
21.9417 | 32.8858 | 47.237 | 52.9027 | 36.7446
22.9417 | 33.4431 | 50.4234 | 55.4296 | 39.4767
23.9417 | 32.7347 | 47.8403 | 53.6915 | 41.4244
24.9417 | 36.7014 | 56.5425 | 65.6909 | 43.5684
25.9417 | 37.5564 | 58.5784 | 70.097 | 45.9187
26.9417 | 38.6308 | 60.9643 | 74.5392 | 47.9044
27.9417 | 39.688 | 63.3436 | 78.1845 | 52.1024
28.9417 | 41.6967 | 65.6166 | 80.6038 | 54.3732
29.9417 | 42.675 | 69.1985 | 85.0907 | 57.3204
30.9417 | 44.2965 | 71.9391 | 88.1583 | 59.3292
31.9417 | 45.5452 | 74.0425 | 90.6853 | 62.6812
32.9417 | 47.6999 | 75.4303 | 88.752 | 64.694
33.9417 | 49.4848 | 78.337 | 92.022 | 67.8388
34.9417 | 51.239 | 74.3246 | 85.2271 | 71.522
35.9417 | 53.424 | 75.8322 | 87.4335 | 73.5374
36.9417 | 55.306 | 76.5804 | 88.4006 | 76.2117
37.9417 | 56.3246 | 77.5829 | 89.5664 | 78.4931
38.9417 | 57.4937 | 79.9358 | 91.5744 | 80.0712
39.9417 | 56.7033 | 77.8879 | 88.9974 | 82.6658
40.9417 | 58.7386 | 80.6469 | 92.4333 | 84.1058
41.9417 | 62.9134 | 85.6652 | 96.9393 | 86.4991
42.9417 | 64.7413 | 87.7813 | 97.8098 | 88.6567
43.9417 | 66.4752 | 90.1641 | 101.4653 | 90.344
44.9417 | 66.253 | 90.1499 | 101.1627 | 93.4065
45.9417 | 67.742 | 93.1827 | 105.2474 | 95.5381
46.9417 | 68.5944 | 94.7943 | 107.0171 | 98.8728
47.9417 | 68.7961 | 94.4418 | 106.5222 | 100.2907
48.9417 | 70.7653 | 97.7341 | 109.8277 | 101.7942
49.9417 | 73.3124 | 99.3601 | 111.2313 | 103.5861
50.9417 | 74.5635 | 104.6541 | 118.1557 | 106.7343
51.9417 | 75.0255 | 105.1404 | 117.6325 | 109.1248
52.9417 | 75.5395 | 103.0872 | 114.8231 | 111.98
53.9417 | 76.2905 | 106.8334 | 119.0376 | 116.0427
54.9417 | 78.5767 | 112.1765 | 124.6833 | 118.6933
55.9417 | 79.4191 | 113.4263 | 126.4759 | 120.9568
56.9417 | 80.7875 | 114.6013 | 128.013 | 121.5866
57.9417 | 81.378 | 115.6314 | 129.2743 | 121.9387
58.9417 | 81.9163 | 116.1524 | 130.1634 | 123.5765
59.9417 | 82.9586 | 116.0033 | 129.3784 | 125.7787
60.9417 | 85.1504 | 118.2123 | 132.2417 | 127.6253
61.9417 | 85.5758 | 117.4836 | 132.0158 | 128.7739
62.9417 | 86.6657 | 118.3356 | 133.4686 | 130.5474
63.9417 | 87.6761 | 120.5679 | 136.011 | 131.3926
64.9417 | 88.5306 | 121.5353 | 136.8832 | 131.8166
65.9417 | 89.2559 | 123.2034 | 140.2308 | 132.5447
66.9417 | 89.9864 | 119.4941 | 135.6998 | 133.2027
67.9417 | 91.0911 | 123.1792 | 141.5717 | 133.9393
68.9417 | 91.3392 | 122.2046 | 140.4703 | 135.0433
69.9417 | 91.5518 | 124.0322 | 147.9267 | 135.4114
70.9417 | 92.2852 | 124.5521 | 148.2678 | 136.33
71.9417 | 92.9748 | 124.6656 | 148.9727 | 137.7874
72.9417 | 94.0329 | 124.995 | 147.1024 | 137.6061
73.9417 | 95.5673 | 125.3464 | 150.5391 | 138.934
74.9417 | 96.316 | 125.2868 | 151.8977 | 140.6171
75.9417 | 96.894 | 125.61 | 151.4981 | 140.8418
76.9417 | 98.4116 | 126.3635 | 151.8586 | 142.1607
77.9417 | 98.927 | 127.038 | 152.12 | 143.1109
78.9417 | 99.4571 | 127.4111 | 152.7169 | 145.0466
79.9417 | 99.8077 | 129.2468 | 155.1826 | 148.3839
80.9417 | 100.6363 | 130.2911 | 156.731 | 150.9433
81.9417 | 101.6434 | 130.5121 | 157.6015 | 151.4888
82.9417 | 101.7404 | 130.434 | 158.49 | 151.0678
83.9417 | 102.6884 | 130.5157 | 159.6408 | 153.1839
84.9417 | 103.416 | 130.5046 | 159.5689 | 152.8999
85.9417 | 103.8884 | 130.4638 | 160.698 | 154.0223
86.9417 | 104.4877 | 130.6696 | 161.1953 | 154.7669
87.9417 | 104.8456 | 131.3146 | 161.7792 | 154.5656
88.9417 | 105.6287 | 131.7138 | 162.4359 | 154.9308
89.9417 | 106.3145 | 132.289 | 162.6538 | 155.8489
90.9417 | 106.8242 | 132.9168 | 162.006 | 156.4614
91.9417 | 107.9164 | 132.8007 | 163.1921 | 156.5277
92.9417 | 108.6395 | 132.7804 | 163.058 | 157.8595
93.9417 | 109.1897 | 134.429 | 165.038 | 157.9274
94.9417 | 109.2328 | 135.1866 | 167.08 | 158.8781
95.9417 | 109.2004 | 137.081 | 167.9648 | 159.0682
96.9417 | 109.415 | 137.6181 | 167.7209 | 160.125
97.9417 | 110.4075 | 138.567 | 168.452 | 161.486
98.9417 | 111.5042 | 139.5016 | 169.1538 | 161.6847
99.9417 | 112.5081 | 141.4981 | 170.0998 | 160.9945
100.9417 | 113.3744 | 142.1185 | 170.7357 | 161.8765
101.9417 | 114.1465 | 142.544 | 170.9054 | 161.9735
102.9417 | 113.8326 | 143.6879 | 171.2288 | 162.0901
103.9417 | 114.2404 | 143.6283 | 172.044 | 163.8446
104.9417 | 115.0151 | 143.9977 | 172.3453 | 165.4336
105.9417 | 116.5826 | 145.4973 | 172.4705 | 165.2332
106.9417 | 117.0569 | 146.4515 | 171.5814 | 164.4338
107.9417 | 117.4643 | 146.1667 | 171.3597 | 163.7681
108.9417 | 118.6623 | 145.8388 | 172.3141 | 165.8408
109.9417 | 119.8892 | 147.6189 | 173.7399 | 167.1337
110.9417 | 120.3914 | 147.901 | 174.2996 | 168.0638
111.9417 | 120.1374 | 149.5473 | 175.2624 | 168.51
112.9417 | 120.1718 | 149.1172 | 174.9432 | 167.5151
113.9417 | 120.0497 | 148.6593 | 174.7945 | 166.3006
114.9417 | 120.3234 | 148.8674 | 174.693 | 166.8373
115.9417 | 120.2123 | 149.5739 | 175.9843 | 169.0706
116.9417 | 120.4041 | 150.3259 | 176.9747 | 169.7537
117.9417 | 120.4356 | 149.6397 | 177.9215 | 169.4385
118.9417 | 121.1965 | 149.4065 | 177.3803 | 168.701
119.9417 | 121.2942 | 149.41 | 177.9273 | 168.1279
120.9417 | 121.5927 | 149.464 | 177.8954 | 167.8545
121.9417 | 121.6696 | 152.1613 | 179.1139 | 168.2777
122.9417 | 121.6093 | 152.307 | 179.0396 | 168.4592
123.9417 | 121.4106 | 153.5862 | 179.3011 | 169.313
124.9417 | 121.4894 | 154.2603 | 179.8754 | 170.6303
125.9417 | 122.0875 | 153.623 | 180.3675 | 170.174
126.9417 | 122.9196 | 154.0755 | 180.8799 | 171.4577
127.9417 | 123.2534 | 154.1109 | 180.1535 | 172.4216
128.9417 | 123.8664 | 154.3126 | 180.6644 | 172.7012
129.9417 | 124.411 | 154.9909 | 180.6393 | 174.2893
130.9417 | 125.304 | 155.5198 | 181.5581 | 177.2545
131.9417 | 124.9177 | 155.3517 | 181.4636 | 177.2008
132.9417 | 125.0539 | 155.5517 | 182.1144 | 177.9912
133.9417 | 125.448 | 154.3882 | 181.4286 | 177.989
134.9417 | 126.2357 | 154.0314 | 181.2224 | 178.2199
135.9417 | 126.3227 | 153.1652 | 180.7834 | 177.6379
136.9417 | 126.8333 | 153.4053 | 180.7517 | 177.5842
137.9417 | 127.1914 | 154.1048 | 180.1149 | 176.4909
138.9417 | 127.1226 | 153.8305 | 179.2384 | 175.5952
139.9417 | 127.5269 | 153.5911 | 179.2645 | 174.9716
140.9417 | 127.7171 | 153.5124 | 178.8909 | 174.9335
141.9417 | 128.0022 | 153.9911 | 178.3715 | 174.9524
142.9417 | 128.1853 | 153.7967 | 178.3254 | 175.5028
143.9417 | 128.7728 | 153.3986 | 178.5366 | 175.8855
144.9417 | 129.2593 | 152.9891 | 178.8597 | 176.2321
145.9417 | 129.2439 | 152.3531 | 178.817 | 176.7225
146.9417 | 129.3077 | 151.5737 | 178.8797 | 177.2539
147.9417 | 129.4396 | 151.0783 | 179.4902 | 176.5207
148.9417 | 129.0823 | 150.6233 | 179.5741 | 176.5991
149.9417 | 129.1515 | 150.0427 | 179.762 | 176.9945
150.9417 | 129.3264 | 151.6362 | 179.4542 | 177.1964
151.9417 | 130.0483 | 151.9101 | 178.8653 | 176.5909
152.9417 | 129.9712 | 151.566 | 178.4114 | 175.6158
153.9417 | 130.1776 | 150.9315 | 178.8568 | 175.7421
154.9573 | 130.0944 | 150.4126 | 179.2123 | 175.8096
155.9573 | 130.0598 | 150.3509 | 179.9837 | 176.2744
156.9417 | 130.9671 | 152.1468 | 181.329 | 177.4139
157.9417 | 131.4445 | 152.3926 | 181.7539 | 179.0903
158.9573 | 132.0262 | 151.846 | 182.5342 | 179.1285
159.9573 | 131.1074 | 152.4408 | 182.3576 | 178.6614
160.9573 | 131.8454 | 153.1072 | 182.6421 | 180.4834
161.9417 | 132.0178 | 152.8166 | 182.8688 | 181.5091
162.9417 | 132.2798 | 153.3604 | 182.9629 | 181.7594
163.9417 | 133.4801 | 153.7739 | 182.9384 | 181.6397
164.9417 | 134.1109 | 154.8788 | 182.8704 | 182.0409
165.9417 | 134.4529 | 155.1417 | 182.612 | 181.7078
166.9417 | 134.3815 | 155.7164 | 183.815 | 181.7737
167.9417 | 134.8464 | 157.2267 | 184.3522 | 183.1406
168.9417 | 135.6925 | 157.8743 | 184.4263 | 182.8331
169.9417 | 136.1764 | 157.4116 | 185.8178 | 184.3202
170.9417 | 136.3322 | 156.5813 | 185.8257 | 186.1713
171.9417 | 136.5974 | 156.129 | 185.7477 | 185.6222
172.9417 | 136.5616 | 155.3415 | 185.1235 | 185.3756
173.9417 | 136.6308 | 155.6815 | 184.7131 | 184.7774
174.9417 | 136.4321 | 155.1167 | 183.7559 | 184.2936
175.9417 | 136.2473 | 154.9607 | 183.1019 | 184.21
176.9417 | 136.1553 | 153.6618 | 182.4911 | 183.0752
177.9417 | 135.7311 | 154.0104 | 182.7579 | 183.0031
178.9417 | 135.6088 | 154.3202 | 183.4107 | 182.3711
179.9417 | 135.4108 | 154.2647 | 183.2482 | 182.0688
180.9417 | 135.7616 | 153.8632 | 182.675 | 181.6577
181.9417 | 135.5509 | 153.0097 | 182.17 | 181.0452
182.9417 | 135.294 | 152.4067 | 182.1001 | 181.1879
183.9417 | 135.4864 | 151.9193 | 181.7301 | 181.089
184.9417 | 135.5416 | 152.1595 | 182.6132 | 180.8635
185.9417 | 135.6551 | 152.0075 | 182.6915 | 179.8251
186.9417 | 135.5918 | 151.7481 | 182.0705 | 179.769
187.9417 | 135.8234 | 151.849 | 182.1361 | 179.899
188.9417 | 135.812 | 152.0735 | 182.1173 | 179.821
189.9417 | 135.8232 | 152.8326 | 182.1702 | 180.6917
190.9417 | 135.9248 | 152.8279 | 182.1847 | 180.1166
191.9417 | 135.771 | 152.8493 | 183.4655 | 180.5893
192.9417 | 136.1532 | 152.7956 | 183.7709 | 180.5756
193.9417 | 136.3865 | 152.4876 | 183.1899 | 180.2214
194.9417 | 136.2942 | 151.9351 | 182.4465 | 179.8324
195.9417 | 136.1827 | 151.432 | 183.6519 | 180.0713
196.9417 | 135.9978 | 151.5884 | 184.3508 | 180.7898
197.9417 | 135.5813 | 151.5089 | 184.8734 | 181.5161
198.9417 | 135.9425 | 152.3125 | 185.5504 | 182.8755
199.9417 | 136.1714 | 153.9351 | 186.6073 | 184.0719
200.9417 | 135.9948 | 154.9559 | 186.6291 | 183.2145
201.9417 | 136.2344 | 154.2374 | 185.8939 | 182.5464
202.9417 | 136.2529 | 153.586 | 185.4287 | 182.1386
203.9417 | 136.228 | 153.3457 | 186.2511 | 181.7373
204.9417 | 135.9096 | 153.8222 | 186.4666 | 181.6914
205.9417 | 135.3441 | 153.0749 | 184.8797 | 181.7351
206.9417 | 135.595 | 154.2851 | 185.0178 | 181.3462
207.9417 | 135.0602 | 155.5515 | 185.3876 | 182.0176
208.9417 | 134.9647 | 155.866 | 187.6117 | 182.3882
209.9417 | 135.1865 | 156.4572 | 187.5284 | 183.1426
210.9417 | 135.3902 | 156.5278 | 186.6088 | 182.6467
211.9417 | 135.6645 | 156.261 | 186.5635 | 182.2744
212.9417 | 135.5073 | 155.9351 | 186.2679 | 181.3329
213.9417 | 135.854 | 156.002 | 185.8115 | 180.8305
214.9417 | 135.9664 | 155.7574 | 186.1428 | 180.5396
215.9417 | 136.0828 | 155.2491 | 185.4092 | 179.8499
216.9417 | 135.9551 | 155.0172 | 184.786 | 179.0659
217.9417 | 135.5387 | 154.5279 | 183.7735 | 178.4883
218.9417 | 135.8865 | 154.2752 | 183.3913 | 177.9809
219.9417 | 135.9853 | 154.712 | 183.0127 | 177.4787
220.9417 | 135.9159 | 154.9064 | 183.1664 | 177.6903
221.9417 | 135.8063 | 154.5053 | 183.1467 | 176.8876
222.9417 | 135.7651 | 155.2409 | 183.575 | 177.3904
223.9417 | 135.825 | 155.3344 | 183.7657 | 177.5008
224.9417 | 136.2422 | 155.4889 | 184.0111 | 178.0317
225.9417 | 135.572 | 155.0686 | 183.1901 | 178.0887
226.9417 | 135.7534 | 154.2088 | 183.187 | 178.1374
227.9417 | 136.6335 | 153.8999 | 182.4377 | 177.1365
228.9417 | 136.8419 | 153.7671 | 182.3046 | 176.5526
229.9417 | 137.8803 | 154.2169 | 182.2756 | 175.9669
230.9417 | 138.8563 | 154.264 | 182.7728 | 175.8618
231.9417 | 139.5635 | 154.3433 | 183.7782 | 175.9701
232.9417 | 140.1407 | 154.0286 | 183.3027 | 176.2585
233.9417 | 139.335 | 153.7213 | 184.4897 | 176.2476
234.9417 | 139.3661 | 153.8041 | 185.0619 | 176.4327
235.9417 | 139.4163 | 153.9808 | 183.7453 | 175.6694
236.9417 | 138.9872 | 153.5114 | 183.5515 | 174.8313
237.9417 | 138.7993 | 153.1278 | 182.9494 | 174.8016
238.9417 | 139.0887 | 153.2913 | 183.3517 | 174.5451
239.9417 | 139.4376 | 152.8559 | 184.0359 | 173.832
240.9417 | 139.1869 | 153.0514 | 183.9104 | 173.3012
241.9417 | 139.0628 | 153.1392 | 182.8015 | 173.3804
242.9417 | 138.9426 | 153.0168 | 181.8099 | 172.6081
243.9417 | 138.8806 | 152.8286 | 182.2155 | 172.2989
244.9417 | 138.9538 | 153.1399 | 182.3167 | 172.1234
245.9417 | 139.3271 | 152.9657 | 182.2229 | 171.977
246.9417 | 139.7254 | 153.248 | 182.2157 | 172.0285
247.9417 | 140.2683 | 153.084 | 182.2182 | 172.1437
248.9417 | 140.1657 | 153.0942 | 183.1126 | 172.3397
249.9417 | 140.2921 | 153.6087 | 182.7579 | 172.0498
250.9417 | 140.5186 | 153.8048 | 183.4941 | 171.3451
251.9417 | 140.6622 | 154.161 | 183.4146 | 171.0273
252.9417 | 140.5263 | 155.0276 | 184.65 | 173.0216
253.9417 | 140.8936 | 155.7337 | 185.0334 | 174.753
254.9417 | 141.5772 | 156.6367 | 186.0198 | 176.314
255.9417 | 142.5863 | 156.1369 | 186.6617 | 175.8369
256.9417 | 143.1105 | 156.442 | 186.958 | 176.4592
257.9417 | 143.5914 | 157.6885 | 188.5098 | 177.4774
258.9417 | 143.7067 | 157.6525 | 188.9605 | 178.318
259.9417 | 144.1709 | 158.2362 | 191.0553 | 179.4258
260.9417 | 145.1153 | 160.0707 | 191.7934 | 180.8709
261.9417 | 145.6975 | 160.8528 | 193.6154 | 182.0111
262.9417 | 145.7617 | 161.5652 | 193.8004 | 183.6436
263.9417 | 145.4209 | 162.6861 | 195.129 | 183.681
264.9417 | 145.5644 | 162.7364 | 195.5509 | 184.2695
265.9417 | 145.2236 | 163.147 | 195.6002 | 184.5263
266.9417 | 145.4077 | 163.2367 | 195.5597 | 183.9444
267.9417 | 145.3011 | 162.7778 | 195.3288 | 183.5388
268.9417 | 144.9479 | 162.519 | 195.118 | 182.6742
269.9417 | 145.3267 | 162.2405 | 194.5315 | 181.639
270.9417 | 145.2668 | 161.9144 | 194.1262 | 181.1859
271.9417 | 145.7573 | 163.326 | 194.0764 | 180.9527
272.9417 | 146.9945 | 164.1968 | 195.0036 | 181.5749
273.9417 | 147.2238 | 163.5508 | 194.6135 | 181.2518
274.9417 | 147.452 | 163.8263 | 194.7728 | 181.2615
275.9417 | 146.7307 | 163.5918 | 194.6081 | 181.8327
276.9417 | 145.6136 | 162.9556 | 194.179 | 181.7489
277.9417 | 147.4516 | 162.1538 | 194.8268 | 181.7851
278.9417 | 147.1033 | 161.9662 | 195.5343 | 181.7285
279.9417 | 147.9014 | 162.6255 | 195.9159 | 180.9506
280.9417 | 148.6062 | 163.2911 | 197.3364 | 181.1268
281.9417 | 148.141 | 163.5768 | 197.0193 | 181.839
282.9417 | 148.8377 | 163.0584 | 196.997 | 182.0558
283.9417 | 148.1874 | 162.752 | 196.9718 | 182.4748
284.9417 | 148.3663 | 162.7832 | 197.1596 | 182.7981
285.9417 | 147.9522 | 162.6958 | 197.177 | 183.1785
286.9417 | 147.9604 | 163.6439 | 197.5006 | 184.5947
287.9417 | 148.7098 | 165.6738 | 198.5935 | 185.6913
288.9417 | 149.0651 | 166.4612 | 198.989 | 185.3556
289.9417 | 149.5162 | 165.766 | 198.6305 | 185.1645
290.9417 | 149.8117 | 165.8888 | 197.6862 | 184.7484
291.9417 | 150.1582 | 166.0675 | 198.5431 | 186.4019
292.9417 | 150.6516 | 168.1778 | 199.4255 | 187.5125
293.9417 | 151.2061 | 169.313 | 199.8679 | 187.7744
294.9417 | 151.5087 | 169.2145 | 199.7596 | 187.8813
295.9417 | 151.361 | 169.345 | 201.4859 | 189.4623
296.9417 | 151.8808 | 169.3594 | 201.5257 | 190.9412
297.9417 | 153.1018 | 169.76 | 201.1277 | 191.4656
298.9417 | 151.6508 | 169.3953 | 201.091 | 190.8521
299.9417 | 152.0834 | 168.3394 | 201.7326 | 190.7713
300.9417 | 152.0972 | 167.3822 | 201.2759 | 189.559
301.9417 | 152.3885 | 167.3734 | 200.8361 | 188.9001
302.9417 | 151.9926 | 167.2297 | 201.9283 | 188.681
303.9417 | 151.8769 | 167.7724 | 202.0572 | 191.866
304.9417 | 151.7821 | 168.7455 | 202.6538 | 191.4626
305.9417 | 152.4071 | 170.2825 | 202.8834 | 190.3149
306.9417 | 153.4903 | 170.2356 | 202.6599 | 190.2247
307.9417 | 152.9688 | 170.0688 | 202.8096 | 190.2906
308.9417 | 152.5576 | 170.1259 | 202.5012 | 190.7783
309.9417 | 152.8344 | 170.1437 | 201.7262 | 191.9079
310.9417 | 153.0848 | 172.084 | 202.8268 | 193.0914
311.9417 | 153.5343 | 174.2571 | 203.3767 | 194.9111
312.9417 | 154.0986 | 173.8448 | 202.8359 | 194.8887
313.9417 | 154.5038 | 174.9302 | 203.0793 | 194.7274
314.9417 | 154.9373 | 175.0798 | 203.5225 | 195.6986
315.9417 | 154.2596 | 174.2757 | 203.572 | 196.5969
316.9417 | 153.9943 | 176.1109 | 204.5026 | 198.1327
317.9417 | 154.0467 | 176.6762 | 205.3392 | 199.8685
318.9417 | 154.9797 | 176.9112 | 205.2108 | 200.2654
319.9417 | 155.1032 | 177.5094 | 204.8769 | 199.7839
320.9417 | 155.0388 | 176.4935 | 205.8005 | 199.4182
321.9417 | 155.9701 | 176.0599 | 206.5248 | 200.1466
322.9417 | 156.1752 | 176.0909 | 207.1906 | 201.2034
323.9417 | 155.8861 | 174.9712 | 206.5732 | 200.6592
324.9417 | 155.904 | 173.9909 | 205.6193 | 200.8347
325.9417 | 155.7043 | 173.6745 | 205.7966 | 201.0552
326.9417 | 155.929 | 174.5362 | 205.8448 | 201.595
327.9417 | 156.0287 | 174.7497 | 206.0527 | 201.0425
328.9417 | 156.8697 | 174.2184 | 206.3381 | 201.1469
329.9417 | 157.2342 | 173.7284 | 205.6204 | 199.8493
330.9417 | 156.0911 | 173.4981 | 205.3031 | 199.5896
331.9417 | 155.8958 | 172.7501 | 204.8074 | 198.157
332.9417 | 155.5038 | 172.2169 | 204.2497 | 197.4736
333.9417 | 155.555 | 171.6114 | 203.5771 | 197.3942
334.9417 | 155.6116 | 170.6693 | 202.831 | 197.4642
335.9417 | 155.4911 | 170.2903 | 202.394 | 197.0719
336.9417 | 155.9922 | 170.9421 | 202.7941 | 197.7182
337.9417 | 155.9337 | 170.8014 | 202.26 | 197.3054
338.9417 | 156.4569 | 170.5618 | 202.2783 | 197.9991
339.9417 | 155.6902 | 170.2795 | 201.4472 | 198.2605
340.9417 | 155.9974 | 169.86 | 201.1567 | 197.9746
341.9417 | 155.3636 | 169.9376 | 201.5933 | 197.7261
342.9417 | 155.144 | 169.878 | 201.4648 | 196.4836
343.9417 | 155.4282 | 169.6089 | 202.3401 | 196.3356
344.9417 | 156.1445 | 169.7991 | 202.7341 | 196.28
345.9417 | 156.5652 | 171.078 | 203.6341 | 195.9355
346.9417 | 157.1276 | 171.0168 | 203.3358 | 195.2662
347.9417 | 157.911 | 170.8124 | 202.9717 | 194.9616
348.9417 | 158.0097 | 170.9059 | 202.3213 | 194.4869
349.9417 | 158.2258 | 171.4543 | 201.8074 | 193.8124
350.9417 | 157.5633 | 172.4846 | 202.0972 | 193.4544
351.9417 | 157.6055 | 173.6622 | 202.4316 | 193.3585
352.9417 | 157.36 | 173.8106 | 203.295 | 193.5375
353.9417 | 156.7477 | 173.3646 | 203.9228 | 193.1227
354.9417 | 156.547 | 173.508 | 204.6495 | 193.3925
355.9417 | 156.4609 | 172.8866 | 205.9416 | 193.5362
356.9417 | 156.8791 | 172.2038 | 206.1694 | 194.3854
357.9417 | 157.9218 | 172.8649 | 206.6075 | 195.3498
358.9417 | 158.6168 | 172.3257 | 207.5799 | 196.5712
359.9417 | 158.9931 | 172.2586 | 208.1195 | 198.6684
360.9417 | 158.8737 | 172.634 | 209.0126 | 199.5289
361.9417 | 159.6247 | 172.5183 | 209.5661 | 199.8753
362.9417 | 159.8349 | 171.8313 | 208.9605 | 199.3003
363.9417 | 160.0906 | 171.3593 | 208.8063 | 198.9791
364.9417 | 160.3443 | 172.2481 | 208.3454 | 198.9913
365.9417 | 160.1025 | 172.1427 | 208.1024 | 199.0929
366.9417 | 160.6742 | 172.7819 | 208.8412 | 199.3453
367.9417 | 161.0969 | 172.5167 | 209.0526 | 198.9977
368.9417 | 161.1076 | 171.9552 | 208.1828 | 198.4461
369.9417 | 160.5999 | 172.8374 | 208.5229 | 198.8052
370.9417 | 160.6287 | 172.9793 | 208.6481 | 200.0736
371.9417 | 160.825 | 172.6901 | 207.9636 | 199.4672
372.9417 | 161.3514 | 173.9477 | 207.8603 | 199.3487
373.9417 | 160.898 | 174.4578 | 208.5833 | 200.4509
374.9417 | 160.5351 | 174.6321 | 208.8669 | 200.2706
375.9417 | 160.797 | 174.0699 | 209.6703 | 201.1268
376.9417 | 161.0115 | 175.2438 | 210.3226 | 201.952
377.9417 | 160.8669 | 176.2428 | 210.7799 | 202.9567
378.9417 | 160.8584 | 176.8512 | 210.9001 | 202.9282
379.9417 | 161.6098 | 176.589 | 211.3122 | 204.1214
380.9417 | 161.1811 | 176.6005 | 211.3053 | 204.7561
381.9417 | 161.2856 | 178.2455 | 211.8071 | 204.3042
382.9417 | 161.8801 | 178.6582 | 212.5332 | 205.1691
383.9417 | 162.3672 | 178.7125 | 212.1964 | 205.3453
384.9417 | 162.8295 | 178.0517 | 213.3216 | 205.6784
385.9417 | 163.3183 | 178.5703 | 214.0423 | 206.161
386.9417 | 163.3059 | 177.9301 | 214.4005 | 206.5292
387.9417 | 163.1268 | 176.9846 | 214.8162 | 206.9333
388.9417 | 163.4189 | 179.2871 | 216.4576 | 208.2032
389.9417 | 163.6405 | 180.4235 | 216.6359 | 208.6084
390.9417 | 163.6778 | 180.3808 | 217.3065 | 209.3975
391.9417 | 163.9652 | 179.934 | 217.6292 | 210.1625
392.9417 | 164.6463 | 179.9671 | 217.3835 | 209.3468
393.9417 | 164.7435 | 179.396 | 216.5486 | 208.346
394.9417 | 164.8553 | 179.294 | 217.302 | 208.3727
395.9417 | 164.7266 | 178.7324 | 217.7362 | 210.1419
396.9417 | 164.6082 | 179.1257 | 218.4788 | 210.8546
397.9417 | 164.616 | 180.4471 | 219.2421 | 211.4235
398.9417 | 164.4667 | 180.8371 | 218.3046 | 212.1529
399.9417 | 165.083 | 180.5551 | 217.9258 | 211.9894
400.9417 | 165.7397 | 180.2553 | 219.0374 | 212.2192
401.9417 | 164.9353 | 179.5468 | 218.5142 | 212.3511
402.9417 | 165.3512 | 180.1136 | 217.9454 | 212.9885
403.9417 | 165.9546 | 179.6659 | 217.5323 | 212.7684
404.9417 | 165.7706 | 178.9444 | 216.6522 | 211.7024
405.9417 | 165.5151 | 178.2974 | 215.3832 | 210.828
406.9417 | 165.627 | 178.0325 | 214.4561 | 210.8308
407.9417 | 165.4144 | 177.7389 | 214.3064 | 210.6253
408.9417 | 165.247 | 177.4732 | 215.5022 | 210.9504
409.9417 | 165.3024 | 177.3469 | 215.0181 | 211.6204
410.9417 | 165.5028 | 177.2102 | 214.625 | 211.3162
411.9417 | 165.7917 | 177.4026 | 213.7816 | 211.4033
412.9417 | 165.5861 | 178.6373 | 213.9893 | 211.7773
413.9417 | 165.772 | 178.9481 | 214.1319 | 213.1743
414.9417 | 165.9683 | 178.6821 | 214.5908 | 212.5125
415.9417 | 165.6338 | 178.7738 | 213.9725 | 211.6388
416.9417 | 165.567 | 178.6287 | 212.9393 | 211.2999
417.9417 | 165.5713 | 177.7353 | 212.4173 | 210.3455
418.9417 | 165.0767 | 177.738 | 211.9543 | 210.07
419.9417 | 164.725 | 179.3364 | 213.2681 | 211.018
420.9417 | 164.5762 | 180.3547 | 214.5197 | 211.2503
421.9417 | 164.1058 | 180.3676 | 215.0616 | 211.9066
422.9417 | 163.8593 | 180.3287 | 215.6255 | 211.9332
423.9417 | 163.6346 | 180.5784 | 216.4651 | 211.3648
424.9417 | 163.2782 | 180.618 | 216.7357 | 211.2102
425.9417 | 163.4881 | 180.1948 | 216.6618 | 210.2201
426.9417 | 163.6653 | 180.6137 | 217.2327 | 209.3007
427.9417 | 163.7914 | 180.5249 | 217.4242 | 208.2321
428.9417 | 163.9282 | 180.152 | 216.2317 | 207.2624
429.9417 | 164.1999 | 179.7619 | 215.6581 | 207.4076
430.9417 | 164.2742 | 180.5323 | 215.8583 | 207.736
431.9417 | 164.1725 | 180.6243 | 215.6705 | 207.7401
432.9417 | 164.3838 | 180.0259 | 215.9556 | 207.3118
433.9417 | 164.6074 | 178.9764 | 215.686 | 206.1142
434.9417 | 164.6499 | 179.0204 | 215.52 | 205.3817
435.9417 | 165.8791 | 179.2997 | 215.8646 | 204.321
436.9417 | 166.8051 | 180.3228 | 216.8989 | 204.8434
437.9417 | 165.6035 | 180.9064 | 217.6317 | 204.9138
438.9417 | 165.0145 | 180.5761 | 217.9873 | 204.7719
439.9417 | 166.3084 | 180.8758 | 218.0175 | 204.6122
440.9417 | 167.1487 | 180.4832 | 218.5694 | 205.5029
441.9417 | 165.628 | 179.892 | 218.6192 | 205.66
442.9417 | 166.6051 | 180.2618 | 219.0182 | 206.6633
443.9417 | 166.563 | 180.7608 | 220.2642 | 207.5098
444.9417 | 166.3374 | 180.4321 | 220.7611 | 207.518
445.9417 | 166.5057 | 180.3853 | 220.4161 | 207.5448
446.9417 | 167.4201 | 179.803 | 221.0158 | 208.0531
447.9417 | 167.4341 | 179.638 | 221.038 | 207.7269
448.9417 | 167.3481 | 179.1423 | 223.0611 | 209.1741
449.9417 | 167.5886 | 178.2449 | 223.1191 | 209.7785
450.9417 | 168.2873 | 178.3382 | 223.0183 | 209.6033
451.9417 | 168.6155 | 178.4135 | 223.4494 | 209.4245
452.9417 | 168.9791 | 178.0388 | 223.3022 | 209.4017
453.9417 | 168.8908 | 178.8984 | 222.5309 | 209.2525
454.9417 | 168.787 | 178.7057 | 221.2587 | 208.3687
455.9417 | 168.477 | 178.3599 | 220.3046 | 208.2714
456.9417 | 168.6401 | 178.3463 | 220.7017 | 207.9981
457.9417 | 169.1139 | 178.4403 | 221.0671 | 208.1978
458.9417 | 169.1139 | 178.941 | 221.1989 | 208.7119
459.9417 | 170.1699 | 179.8366 | 222.7923 | 209.2707
460.9417 | 170.6141 | 179.9214 | 224.5486 | 210.1036
461.9417 | 170.9447 | 179.6565 | 225.0205 | 210.4213
462.9417 | 170.9703 | 179.9077 | 225.3532 | 211.1903
463.9417 | 171.3935 | 180.0726 | 224.6308 | 211.708
464.9417 | 171.1358 | 180.1609 | 225.7447 | 212.1958
465.9417 | 170.7166 | 180.0603 | 226.1429 | 212.3232
466.9417 | 170.9542 | 180.6192 | 226.1747 | 213.0332
467.9417 | 172.386 | 180.9828 | 226.2315 | 213.1386
468.9417 | 173.0628 | 181.8235 | 225.9849 | 213.1013
469.9417 | 172.7769 | 181.4048 | 226.1844 | 213.2971
470.9417 | 172.6616 | 181.7188 | 226.7267 | 213.6174
471.9417 | 171.9074 | 180.9948 | 226.8886 | 212.7199
472.9417 | 172.3435 | 181.042 | 227.2702 | 213.4626
473.9417 | 171.6332 | 181.3638 | 227.1582 | 213.5796
474.9417 | 170.9822 | 182.8676 | 228.0526 | 214.3335
475.9417 | 170.8964 | 184.6554 | 228.9717 | 214.9794
476.9417 | 171.3745 | 184.6043 | 229.6923 | 215.5556
477.9417 | 172.5616 | 184.9599 | 230.383 | 215.1705
478.9417 | 172.439 | 184.498 | 230.2122 | 213.9581
479.9417 | 172.5748 | 183.7807 | 229.1808 | 213.1947
480.9417 | 173.0865 | 184.0179 | 230.0893 | 213.5279
481.9417 | 172.3788 | 186.0868 | 230.2076 | 214.8378
482.9417 | 172.9574 | 186.0369 | 230.0894 | 214.2948
483.9417 | 173.1453 | 185.5024 | 229.637 | 213.7748
484.9417 | 173.445 | 185.4174 | 229.7525 | 214.2131
485.9417 | 174.1146 | 184.8268 | 228.9588 | 214.4751
486.9417 | 175.0079 | 184.2892 | 229.5142 | 214.4977
487.9417 | 175.1204 | 184.4178 | 229.7383 | 215.2001
488.9417 | 174.7383 | 184.4363 | 230.2022 | 215.0667
489.9417 | 174.6164 | 185.6069 | 229.694 | 214.739
490.9417 | 174.3099 | 186.488 | 229.7221 | 215.6512
491.9417 | 174.2083 | 187.3543 | 231.1293 | 215.6259
492.9417 | 175.1888 | 187.6167 | 231.731 | 216.1013
493.9417 | 175.2743 | 187.7211 | 231.7535 | 214.9241
494.9417 | 175.5143 | 187.0546 | 230.7994 | 215.5802
495.9417 | 176.4335 | 186.5998 | 231.0598 | 215.6613
496.9417 | 176.8497 | 186.0877 | 231.7241 | 216.6782
497.9417 | 177.1501 | 185.7274 | 231.2416 | 216.1985
498.9417 | 177.0284 | 185.2917 | 231.1856 | 215.6939
499.9417 | 176.95 | 185.4243 | 230.9798 | 215.5084
500.9573 | 176.873 | 185.6208 | 231.3188 | 215.4414
501.9417 | 176.9182 | 185.4193 | 230.5564 | 215.226
502.9417 | 177.3073 | 185.0718 | 230.1198 | 214.641
503.9417 | 177.1074 | 185.3146 | 229.7589 | 214.2809
504.9417 | 177.1624 | 186.1932 | 230.4101 | 213.9985
505.9417 | 176.7227 | 186.1993 | 230.3448 | 214.1232
506.9417 | 177.1768 | 186.0758 | 231.0104 | 214.2115
507.9417 | 177.2252 | 187.4308 | 232.1221 | 214.6258
508.9417 | 177.1501 | 187.6729 | 231.2523 | 214.6836
509.9417 | 177.1965 | 187.483 | 231.4791 | 214.2725
510.9417 | 176.4136 | 188.4045 | 231.9986 | 214.0366
511.9417 | 176.9925 | 188.0585 | 231.0093 | 213.2042
512.9417 | 176.8972 | 188.2364 | 231.2423 | 212.3372
513.9417 | 176.5665 | 188.4269 | 231.6257 | 211.5222
514.9417 | 176.4651 | 189.1566 | 233.7351 | 212.9317
515.9417 | 176.6714 | 191.0352 | 234.7783 | 215.7094
516.9417 | 177.859 | 192.3345 | 235.3718 | 217.0262
517.9417 | 177.7235 | 193.7113 | 237.3819 | 218.3286
518.9573 | 176.0793 | 195.0068 | 239.1755 | 219.0544
519.9417 | 175.4535 | 195.6573 | 239.3251 | 219.5321
520.9417 | 175.549 | 196.7871 | 239.8064 | 220.8472
521.9417 | 175.7548 | 197.4862 | 241.2497 | 222.5475
522.9417 | 176.5145 | 198.3017 | 243.8224 | 223.5298
523.9417 | 177.1133 | 197.5011 | 244.6951 | 224.6422
524.9417 | 177.628 | 198.473 | 245.5642 | 224.9641
525.9417 | 178.1462 | 198.0735 | 245.4736 | 225.1956
526.9417 | 178.156 | 198.5017 | 245.592 | 224.3207
527.9417 | 178.8494 | 199.28 | 246.153 | 224.577
528.9417 | 178.4571 | 200.1603 | 246.2928 | 225.8906
529.9417 | 178.7802 | 199.2891 | 246.2019 | 226.2101
530.9417 | 179.1056 | 199.6824 | 247.6888 | 226.9009
531.9417 | 178.8959 | 199.2775 | 246.8428 | 225.5904
532.9417 | 179.3435 | 201.5689 | 246.7434 | 226.623
533.9417 | 179.2481 | 202.2868 | 247.1392 | 228.6439
534.9417 | 179.7291 | 202.8011 | 246.1909 | 229.4105
535.9417 | 180.44 | 202.0429 | 245.7454 | 230.2397
536.9417 | 181.1394 | 201.9344 | 246.0598 | 231.0402
537.9417 | 181.6601 | 203.4211 | 245.7871 | 231.9099
538.9417 | 181.4345 | 205.0136 | 245.8147 | 232.1321
539.9417 | 181.8776 | 204.471 | 245.4251 | 232.687
540.9417 | 182.2668 | 205.1073 | 244.6678 | 232.1338
541.9417 | 183.2713 | 206.1284 | 244.2223 | 230.7219
542.9417 | 184.1278 | 204.6969 | 243.9995 | 229.3351
543.9417 | 184.1357 | 205.3808 | 243.5198 | 228.4711
544.9417 | 183.9207 | 204.8842 | 242.8314 | 227.0547
545.9417 | 184.8178 | 204.1257 | 242.6205 | 226.4299
546.9417 | 184.4418 | 203.1058 | 242.1038 | 226.409
547.9417 | 184.4766 | 202.4609 | 241.8727 | 225.0494
548.9573 | 184.0776 | 201.3593 | 242.0668 | 224.8945
549.9417 | 184.0968 | 201.199 | 241.6725 | 225.1685
550.9417 | 184.6257 | 200.0474 | 241.1491 | 225.3531
551.9417 | 184.3201 | 199.4157 | 241.2878 | 224.9171
552.9417 | 184.8254 | 198.3872 | 240.9124 | 224.5159
553.9417 | 184.7817 | 197.789 | 240.0721 | 223.0383
554.9417 | 184.5702 | 197.432 | 239.2072 | 222.8742
555.9417 | 184.4484 | 197.3208 | 238.2096 | 221.8736
556.9417 | 184.5918 | 197.5185 | 238.5011 | 221.6772
557.9417 | 183.8643 | 197.6038 | 237.7817 | 221.2022
558.9417 | 183.9278 | 196.3406 | 237.2272 | 220.036
559.9417 | 184.4856 | 195.6418 | 237.6685 | 220.3866
560.9417 | 185.8028 | 195.2912 | 238.4454 | 220.3275
561.9417 | 185.6057 | 195.4621 | 238.1494 | 220.5609
562.9417 | 185.5512 | 195.0968 | 237.4031 | 219.3851
563.9417 | 185.4875 | 194.6346 | 237.6559 | 219.3752
564.9417 | 185.1966 | 195.5989 | 237.9571 | 220.1644
565.9417 | 185.4124 | 196.0629 | 238.6935 | 219.9751
566.9417 | 185.5334 | 197.3074 | 238.2418 | 221.0577
567.9417 | 185.5298 | 197.8277 | 238.8899 | 221.2085
568.9417 | 185.7835 | 198.2206 | 240.1475 | 222.2977
569.9417 | 185.7813 | 200.042 | 241.2096 | 223.1714
570.9417 | 185.9889 | 200.2381 | 242.5728 | 223.4537
571.9417 | 185.614 | 200.5636 | 243.4487 | 223.8289
572.9417 | 185.9869 | 201.004 | 245.0686 | 223.255
573.9417 | 186.8005 | 201.1934 | 244.8522 | 222.8004
574.9417 | 188.1089 | 201.9168 | 246.0794 | 223.4553
575.9417 | 187.7939 | 201.646 | 247.135 | 227.1266
576.9417 | 187.5164 | 203.0761 | 247.0019 | 227.094
577.9417 | 187.8215 | 201.6791 | 246.5879 | 225.421
578.9417 | 188.267 | 201.3859 | 246.7182 | 225.9159
579.9417 | 188.0087 | 200.5183 | 246.2765 | 226.5241
580.9417 | 187.9158 | 199.4421 | 246.0277 | 226.4933
581.9417 | 188.2853 | 199.4369 | 245.6541 | 225.6312
582.9417 | 188.3647 | 198.6972 | 245.534 | 225.9128
583.9417 | 188.2676 | 198.3472 | 244.9933 | 224.9538
584.9417 | 187.4141 | 197.9479 | 244.613 | 225.2495
585.9417 | 187.2837 | 198.2713 | 244.9366 | 224.1111
586.9417 | 187.3016 | 198.0382 | 246.529 | 224.6477
587.9417 | 188.0118 | 199.6885 | 248.2331 | 225.5054
588.9417 | 188.8958 | 200.3591 | 250.5154 | 225.6477
589.9417 | 189.3909 | 201.7236 | 251.274 | 225.7609
590.9417 | 188.7235 | 202.8831 | 251.2225 | 225.5967
591.9417 | 188.3245 | 203.0709 | 250.9568 | 225.07
592.9417 | 187.3586 | 203.8407 | 251.4816 | 224.5899
593.9417 | 187.8219 | 204.4731 | 251.4941 | 224.4502
594.9417 | 189.2716 | 205.0337 | 252.6066 | 223.2272
595.9417 | 190.6349 | 205.6754 | 253.1667 | 222.8004
596.9417 | 191.8109 | 206.6908 | 255.1089 | 222.7261
597.9417 | 191.6544 | 206.6565 | 255.2825 | 222.8933
598.9417 | 191.1642 | 207.0706 | 256.0955 | 221.8108
599.9417 | 190.7633 | 207.7862 | 256.1517 | 222.8713
600.9417 | 191.2031 | 207.7842 | 255.3482 | 225.4172
601.9417 | 191.407 | 208.8775 | 255.7996 | 228.1635
602.9417 | 192.3398 | 208.4103 | 257.8699 | 230.3439
603.9417 | 192.1017 | 209.0106 | 257.887 | 231.9594
604.9417 | 192.4832 | 209.0756 | 257.6776 | 232.9166
605.9417 | 193.2201 | 208.5956 | 258.9959 | 235.3064
606.9417 | 193.3408 | 208.2133 | 259.1194 | 235.8875
607.9417 | 194.1298 | 207.3472 | 259.6128 | 236.2476
608.9573 | 194.394 | 207.8961 | 260.0014 | 235.9436
609.9417 | 194.9881 | 209.3751 | 261.5361 | 237.4168
610.9573 | 196.8058 | 210.0429 | 261.9415 | 236.9037
611.9573 | 195.8075 | 210.0256 | 261.0964 | 237.5623
612.9417 | 196.1591 | 209.7585 | 261.3285 | 236.5239
613.9573 | 197.0328 | 209.9524 | 261.1732 | 235.4658
614.9417 | 195.9128 | 210.6155 | 261.3125 | 236.0416
615.9417 | 195.0361 | 211.2794 | 261.813 | 236.0852
616.9417 | 194.6528 | 210.9536 | 262.6674 | 235.8868
617.9417 | 194.8762 | 211.7844 | 264.5229 | 236.2799
618.9417 | 195.8196 | 212.9583 | 264.2817 | 236.2264
619.9417 | 194.7833 | 213.7813 | 265.7519 | 236.2916
620.9417 | 194.2892 | 213.4856 | 265.5076 | 236.317
621.9417 | 193.4025 | 214.0889 | 265.7324 | 237.3926
622.9417 | 194.5748 | 214.4016 | 267.25 | 237.7618
623.9417 | 195.5297 | 214.036 | 267.4108 | 237.4849
624.9417 | 195.6226 | 214.878 | 267.574 | 237.9505
625.9417 | 195.9673 | 215.4612 | 267.3967 | 238.8884
626.9417 | 196.1427 | 214.4209 | 266.3652 | 238.8858
627.9417 | 196.9338 | 214.2817 | 266.6452 | 239.2933
628.9417 | 196.4566 | 213.7961 | 265.6471 | 238.967
629.9417 | 196.9676 | 215.9903 | 266.7276 | 238.5571
630.9417 | 197.3796 | 215.8462 | 266.3672 | 239.4095
631.9417 | 197.5457 | 216.1886 | 266.7114 | 239.4957
632.9417 | 198.9365 | 216.7453 | 268.3471 | 238.5713
633.9417 | 199.0844 | 217.6778 | 269.2023 | 237.7777
634.9417 | 198.504 | 218.2103 | 268.742 | 237.0982
635.9417 | 199.1155 | 219.0656 | 268.4222 | 237.9358
636.9417 | 200.0957 | 219.166 | 268.1548 | 237.5616
637.9417 | 199.9969 | 218.9721 | 267.2771 | 236.1798
638.9417 | 199.5632 | 218.3819 | 266.4981 | 234.8718
639.9417 | 199.48 | 218.072 | 265.7886 | 234.5476
640.9417 | 200.1197 | 218.1774 | 265.176 | 232.9766
641.9417 | 199.5936 | 218.2961 | 265.2095 | 232.6287
642.9417 | 199.1293 | 218.1927 | 265.9929 | 232.0219
643.9417 | 198.6646 | 217.7511 | 266.4352 | 232.1121
644.9417 | 198.0402 | 217.943 | 267.0738 | 231.5094
645.9417 | 197.8333 | 218.3514 | 266.736 | 232.5148
646.9417 | 197.6498 | 217.7459 | 265.5946 | 234.6814
647.9417 | 197.5073 | 217.4671 | 265.2067 | 234.864
648.9417 | 197.2226 | 217.6617 | 265.1431 | 235.3364
649.9417 | 196.5633 | 217.7591 | 264.9586 | 236.163
650.9417 | 196.5261 | 218.8671 | 267.1222 | 238.254
651.9417 | 197.3099 | 219.2683 | 266.7409 | 239.4846
652.9417 | 197.9927 | 219.288 | 267.3245 | 238.7646
653.9417 | 198.7901 | 220.0929 | 267.2058 | 237.4851
654.9417 | 199.9565 | 220.7394 | 268.1912 | 237.5636
655.9417 | 200.3045 | 221.5949 | 268.5506 | 237.0393
656.9417 | 200.8385 | 220.6841 | 268.2782 | 235.6275
657.9417 | 200.3056 | 221.2719 | 269.1017 | 234.7454
658.9417 | 200.0621 | 220.7004 | 268.3812 | 234.0645
659.9417 | 200.1447 | 220.9461 | 268.6341 | 234.9949
660.9417 | 199.3331 | 220.1448 | 271.1792 | 236.8184
661.9417 | 199.3097 | 219.8905 | 272.346 | 237.5871
662.9417 | 200.0596 | 220.1318 | 273.3749 | 237.9238
663.9417 | 201.1928 | 220.6317 | 273.4088 | 237.4644
664.9417 | 202.0372 | 221.6409 | 272.7573 | 236.6091
665.9417 | 202.9307 | 221.5337 | 272.0029 | 235.2022
666.9417 | 203.4076 | 221.3143 | 270.9444 | 234.4515
667.9417 | 202.9516 | 220.8599 | 271.7417 | 234.1621
668.9417 | 203.3655 | 223.45 | 272.5763 | 233.6205
669.9417 | 203.5152 | 223.8548 | 273.7161 | 234.438
670.9417 | 205.0167 | 223.3847 | 272.9323 | 234.8976
671.9417 | 205.5469 | 224.8076 | 272.1351 | 235.2406
672.9417 | 203.9501 | 225.519 | 271.6599 | 235.3234
673.9417 | 202.955 | 225.777 | 271.7359 | 236.5938
674.9417 | 202.4179 | 225.0749 | 272.9912 | 238.2557
675.9417 | 202.5341 | 225.5788 | 273.3978 | 238.002
676.9417 | 203.2874 | 225.0543 | 274.0625 | 238.6979
677.9417 | 203.7735 | 224.3263 | 273.694 | 239.1805
678.9417 | 204.1852 | 223.7053 | 275.2364 | 241.5929
679.9417 | 204.2453 | 223.978 | 275.6297 | 242.0146
680.9417 | 204.4454 | 224.3694 | 275.207 | 242.2227
681.9417 | 204.9427 | 223.5645 | 275.6107 | 241.2506
682.9417 | 204.4204 | 225.6209 | 276.1986 | 240.628
683.9417 | 204.1167 | 225.5991 | 275.7732 | 239.885
684.9417 | 204.9421 | 225.3039 | 276.2662 | 239.6108
685.9417 | 205.1134 | 224.6264 | 276.9627 | 240.2268
686.9417 | 205.0428 | 224.9347 | 276.9696 | 239.763
687.9417 | 204.0736 | 224.2881 | 277.5255 | 239.4245
688.9417 | 204.0975 | 223.6785 | 277.2336 | 239.6505
689.9417 | 204.6184 | 223.4516 | 276.7035 | 240.09
690.9417 | 203.804 | 223.6163 | 277.1733 | 240.4602
691.9417 | 203.1481 | 224.3683 | 276.5399 | 242.4249
692.9417 | 204.2003 | 223.9276 | 275.9168 | 242.6385
693.9417 | 205.3029 | 224.1004 | 275.3213 | 242.1082
694.9417 | 205.1901 | 224.7511 | 274.5905 | 242.1402
695.9417 | 205.2853 | 225.1236 | 275.331 | 242.1818
696.9417 | 205.7219 | 225.0979 | 275.2459 | 244.3235
697.9417 | 206.2279 | 225.9692 | 275.6972 | 245.5552
698.9417 | 205.7582 | 225.4197 | 275.8036 | 246.1878
699.9417 | 206.1573 | 225.1946 | 275.8087 | 246.5009
700.9417 | 205.9595 | 225.4094 | 275.8552 | 247.7864
701.9417 | 205.7111 | 226.7427 | 275.6481 | 248.75
702.9417 | 204.5742 | 226.7886 | 275.0726 | 249.7356
703.9417 | 203.6642 | 227.4951 | 274.3862 | 249.6505
704.9417 | 204.0865 | 226.2819 | 274.4795 | 248.9735
705.9417 | 203.5717 | 226.7214 | 274.4246 | 247.1632
706.9417 | 203.4591 | 226.3723 | 273.6923 | 246.1591
707.9417 | 202.8171 | 225.5164 | 273.4478 | 244.7998
708.9417 | 203.3006 | 225.8762 | 273.8425 | 243.9992
709.9417 | 204.0872 | 225.8308 | 273.1051 | 245.0069
710.9417 | 203.8694 | 225.4647 | 273.2381 | 244.7086
711.9417 | 204.22 | 225.2732 | 273.2807 | 244.6479
712.9417 | 204.496 | 224.1218 | 272.7491 | 243.5209
713.9417 | 205.1549 | 223.7075 | 272.3323 | 242.8597
714.9417 | 205.6095 | 223.5078 | 271.9556 | 241.179
715.9417 | 205.9091 | 223.1344 | 270.8245 | 239.7657
716.9417 | 206.5066 | 224.4841 | 270.5862 | 238.3403
717.9417 | 207.469 | 224.1936 | 270.6522 | 238.4882
718.9417 | 207.4208 | 224.4312 | 270.017 | 238.5211
719.9417 | 207.6669 | 224.6443 | 269.85 | 237.2903
720.9417 | 206.9833 | 223.6004 | 269.7061 | 238.1393
721.9417 | 206.3079 | 222.886 | 269.117 | 237.9103
722.9417 | 207.3585 | 223.0985 | 269.6227 | 237.3872
723.9417 | 208.5264 | 222.9582 | 270.3835 | 237.1468
724.9417 | 208.6199 | 222.2261 | 270.748 | 237.1982
725.9417 | 207.593 | 221.5885 | 271.1245 | 236.4559
726.9417 | 207.3892 | 220.663 | 271.9276 | 235.3305
727.9417 | 206.7397 | 220.59 | 272.1284 | 234.3901
728.9417 | 207.5857 | 220.6359 | 272.3802 | 233.4954
729.9417 | 206.6947 | 220.0766 | 272.5111 | 233.2914
730.9417 | 206.6455 | 219.7562 | 271.0022 | 233.7071
731.9417 | 206.7521 | 219.0462 | 270.1717 | 232.9367
732.9417 | 207.1266 | 218.7031 | 269.4379 | 233.0743
733.9417 | 207.4147 | 219.2757 | 269.4803 | 233.2152
734.9417 | 207.4328 | 218.6153 | 268.4003 | 232.4229
735.9417 | 207.0318 | 217.9788 | 267.2366 | 232.4026
736.9417 | 207.1586 | 218.029 | 267.3036 | 232.4384
737.9417 | 207.5967 | 218.2887 | 267.3468 | 232.2349
738.9417 | 207.1999 | 218.3279 | 266.9118 | 232.8179
739.9417 | 208.1462 | 219.0656 | 267.7913 | 232.9014
740.9417 | 208.8945 | 220.5265 | 269.5925 | 233.6044
741.9417 | 208.9742 | 220.5153 | 269.3383 | 234.8889
742.9417 | 209.2186 | 221.325 | 271.4469 | 236.4507
743.9417 | 208.0137 | 222.7554 | 272.6683 | 238.7112
744.9417 | 207.7973 | 222.7236 | 272.629 | 240.6762
745.9417 | 209.3002 | 222.927 | 272.7397 | 241.6879
746.9417 | 209.1202 | 222.6253 | 272.1147 | 240.5616
747.9417 | 208.564 | 222.37 | 271.3041 | 239.6718
748.9417 | 209.9797 | 222.9569 | 272.4258 | 240.4575
749.9417 | 210.8097 | 223.3887 | 272.5873 | 239.8184
750.9417 | 211.5361 | 223.2121 | 271.5799 | 238.3595
751.9417 | 212.4576 | 223.2892 | 271.251 | 238.3103
752.9417 | 213.3055 | 222.7823 | 271.6556 | 237.583
753.9417 | 214.2358 | 222.8763 | 272.2542 | 237.4065
754.9417 | 214.282 | 222.1476 | 272.9017 | 236.6022
755.9417 | 214.3133 | 221.6258 | 272.315 | 235.4474
756.9417 | 213.2521 | 221.5603 | 271.7416 | 234.9511
757.9417 | 213.1983 | 221.8829 | 270.8263 | 235.6494
758.9573 | 213.2743 | 221.8985 | 272.0252 | 235.1188
759.9417 | 212.6932 | 222.1019 | 271.5999 | 235.4722
760.9417 | 212.8995 | 221.7944 | 271.5164 | 235.2376
761.9417 | 213.0813 | 222.1651 | 270.5886 | 234.4787
762.9417 | 213.8044 | 221.9746 | 269.9617 | 233.5212
763.9417 | 214.004 | 222.6329 | 270.6644 | 234.8316
764.9417 | 214.5551 | 222.3513 | 271.5135 | 234.4946
765.9417 | 213.0918 | 222.5146 | 271.9846 | 234.2631
766.9417 | 212.98 | 222.5403 | 271.0112 | 235.7167
767.9417 | 213.4053 | 222.3644 | 271.1449 | 236.4363
768.9417 | 212.9498 | 222.5242 | 269.7744 | 237.7567
769.9417 | 213.3082 | 223.3664 | 269.821 | 238.0908
770.9417 | 213.0255 | 223.8644 | 270.8988 | 238.7036
771.9417 | 213.7711 | 224.2914 | 270.9936 | 240.1431
772.9417 | 214.539 | 226.1776 | 271.4726 | 240.9785
773.9417 | 215.2669 | 227.1331 | 272.7658 | 242.8913
774.9417 | 215.3959 | 227.1939 | 273.551 | 242.7806
775.9417 | 214.9489 | 230.2787 | 275.3699 | 242.0269
776.9417 | 214.5026 | 230.3179 | 275.8369 | 242.3471
777.9417 | 214.8554 | 230.3508 | 276.7761 | 241.9501
778.9417 | 214.8156 | 231.7176 | 276.4798 | 241.4903
779.9417 | 214.929 | 232.9832 | 276.6188 | 240.317
780.9417 | 214.6943 | 232.5971 | 276.8125 | 239.9595
781.9417 | 214.8202 | 232.9943 | 276.6761 | 238.7401
782.9417 | 215.2064 | 233.8456 | 277.3907 | 238.6924
783.9417 | 215.596 | 233.8239 | 277.8017 | 237.0064
784.9417 | 215.0141 | 234.2973 | 278.2437 | 236.7002
785.9417 | 215.2325 | 233.9426 | 277.5255 | 235.3748
786.9417 | 215.8056 | 232.9274 | 279.4688 | 235.26
787.9417 | 214.791 | 233.1158 | 279.7468 | 235.5885
788.9417 | 215.3591 | 234.2875 | 280.0353 | 236.8508
789.9417 | 215.4443 | 236.9803 | 280.2311 | 237.7596
790.9417 | 214.5044 | 236.1576 | 279.827 | 237.6807
791.9417 | 214.623 | 236.4141 | 279.8962 | 236.909
792.9417 | 215.8062 | 237.5345 | 280.2386 | 236.5381
793.9417 | 215.7544 | 238.5784 | 280.0869 | 235.5916
794.9417 | 215.663 | 240.6767 | 280.427 | 234.6777
795.9417 | 215.756 | 242.3364 | 280.5906 | 233.8509
796.9417 | 215.6885 | 243.4956 | 280.6979 | 233.3027
797.9417 | 215.7685 | 243.8539 | 280.9223 | 234.2543
798.9417 | 215.3156 | 243.799 | 281.376 | 236.3569
799.9417 | 215.6287 | 244.7059 | 281.7408 | 237.605
800.9417 | 216.093 | 245.1361 | 281.0242 | 236.6092
801.9417 | 216.6586 | 245.0917 | 281.9518 | 235.9162
802.9417 | 217.6434 | 244.6151 | 282.406 | 236.2274
803.9417 | 217.4092 | 244.2278 | 282.968 | 236.7213
804.9417 | 217.107 | 244.8635 | 282.4458 | 237.076
805.9417 | 217.8029 | 245.3506 | 282.6659 | 236.2918
806.9417 | 218.7561 | 244.3881 | 281.9034 | 235.1184
807.9417 | 219.8337 | 244.6009 | 281.9482 | 233.9458
808.9417 | 220.3883 | 244.3161 | 282.3231 | 234.0331
809.9417 | 219.8097 | 243.9741 | 282.5542 | 234.5342
810.9417 | 219.8396 | 242.5395 | 282.1981 | 235.0142
811.9417 | 219.8148 | 243.3207 | 283.4417 | 238.2314
812.9417 | 219.0257 | 242.9857 | 284.0734 | 241.0596
813.9417 | 218.8267 | 243.2351 | 284.0911 | 242.6488
814.9417 | 219.9067 | 243.7955 | 283.0255 | 243.2813
815.9417 | 219.7875 | 242.9847 | 282.7552 | 243.0861
816.9417 | 219.9024 | 243.1233 | 283.1462 | 243.4372
817.9417 | 219.8372 | 242.8683 | 283.1213 | 244.5297
818.9417 | 219.704 | 244.3518 | 282.9165 | 244.1751
819.9417 | 219.5004 | 244.5873 | 282.5735 | 243.6171
820.9417 | 219.1371 | 244.4662 | 282.5309 | 243.1102
821.9417 | 219.1668 | 243.6882 | 282.1635 | 242.9424
822.9417 | 219.1044 | 244.3445 | 282.394 | 242.5154
823.9417 | 219.2952 | 244.7986 | 282.7881 | 241.775
824.9417 | 220.4565 | 244.3978 | 283.0645 | 242.54
825.9417 | 221.3609 | 244.2283 | 283.0195 | 243.5965
826.9417 | 221.0582 | 244.6414 | 282.2657 | 243.1556
827.9417 | 221.3314 | 243.9716 | 282.0613 | 242.8371
828.9417 | 221.3265 | 242.4935 | 280.8182 | 243.6961
829.9417 | 221.5893 | 241.874 | 280.7811 | 244.6875
830.9417 | 221.4705 | 241.5361 | 280.0903 | 243.3569
831.9417 | 221.6797 | 241.1278 | 279.2763 | 242.1016
832.9417 | 222.3865 | 241.3103 | 279.2557 | 240.8868
833.9417 | 222.7042 | 240.5395 | 278.4558 | 239.5255
834.9417 | 222.3828 | 239.7678 | 277.5059 | 238.4009
835.9417 | 222.5582 | 238.7524 | 276.8684 | 237.2012
836.9417 | 221.9669 | 238.1705 | 276.9753 | 236.8519
837.9417 | 221.1173 | 237.7802 | 276.7267 | 236.2173
838.9417 | 220.9279 | 236.7927 | 276.2501 | 236.3893
839.9417 | 220.8223 | 237.3753 | 276.8425 | 236.3723
840.9417 | 221.2617 | 238.4944 | 277.995 | 235.6897
841.9417 | 221.6451 | 238.1657 | 277.5795 | 235.8027
842.9417 | 221.2708 | 237.6074 | 276.6959 | 235.4562
843.9417 | 221.4315 | 237.1714 | 276.6325 | 235.2249
844.9417 | 222.2824 | 236.9088 | 276.8523 | 234.5938
845.9417 | 222.3626 | 236.4802 | 276.3867 | 233.4389
846.9417 | 222.4601 | 236.8448 | 276.6004 | 233.6636
847.9417 | 222.5225 | 236.6126 | 276.1474 | 232.7949
848.9417 | 222.1178 | 235.7558 | 275.6927 | 231.9731
849.9417 | 222.0402 | 235.002 | 275.4158 | 231.2247
850.9417 | 222.0447 | 235.0414 | 275.3745 | 230.5294
851.9417 | 221.4938 | 235.9313 | 276.7111 | 231.7915
852.9417 | 220.9259 | 237.1334 | 277.1019 | 233.4273
853.9417 | 221.1041 | 237.2571 | 277.7867 | 235.3097
854.9417 | 220.6861 | 238.365 | 278.0912 | 236.7197
855.9417 | 220.6681 | 240.1355 | 279.0817 | 238.7969
856.9417 | 221.034 | 239.9201 | 278.6778 | 239.3403
857.9417 | 221.3212 | 239.7638 | 278.6696 | 239.7409
858.9417 | 221.045 | 240.3725 | 279.1037 | 239.17
859.9417 | 220.7587 | 242.4074 | 279.9964 | 241.4562
860.9417 | 221.3629 | 243.042 | 280.4345 | 242.7641
861.9417 | 220.0516 | 242.6056 | 281.4092 | 242.9527
862.9417 | 221.5503 | 242.0733 | 281.3843 | 242.7306
863.9417 | 222.4737 | 243.7584 | 282.9644 | 244.0231
864.9417 | 222.8345 | 245.0188 | 283.7422 | 245.725
865.9417 | 222.2173 | 245.1684 | 283.5862 | 245.9067
866.9417 | 222.3398 | 244.4086 | 283.8998 | 245.6922
867.9417 | 222.3773 | 245.5349 | 283.5133 | 246.2995
868.9417 | 222.9643 | 246.3226 | 284.6075 | 246.8588
869.9417 | 223.8461 | 246.2711 | 285.3614 | 246.8314
870.9417 | 223.2596 | 245.598 | 284.8152 | 246.8248
871.9417 | 223.8902 | 244.7147 | 285.4272 | 247.6324
872.9417 | 223.7319 | 244.1484 | 285.193 | 247.7889
873.9417 | 224.7431 | 244.2119 | 286.631 | 248.3918
874.9417 | 225.1386 | 244.4096 | 287.3023 | 247.3351
875.9417 | 225.7867 | 243.8545 | 286.4728 | 246.5262
876.9417 | 225.9934 | 242.9581 | 285.9053 | 246.6137
877.9417 | 225.2442 | 242.4688 | 285.8991 | 246.0313
878.9417 | 223.9803 | 241.1841 | 285.5016 | 245.7453
879.9417 | 224.4564 | 241.3345 | 285.1841 | 244.5578
880.9417 | 224.4495 | 241.2459 | 285.7296 | 243.8708
881.9417 | 224.7603 | 242.9315 | 285.5958 | 242.897
882.9417 | 225.9422 | 243.5096 | 285.1142 | 242.2746
883.9417 | 226.452 | 243.4558 | 286.1436 | 240.8212
884.9417 | 226.6946 | 243.0715 | 285.8098 | 240.3684
885.9417 | 227.9984 | 242.3864 | 286.9285 | 240.2102
886.9417 | 228.444 | 241.1177 | 287.2333 | 241.4958
887.9417 | 228.6427 | 240.7331 | 287.0391 | 240.8094
888.9417 | 228.597 | 239.6201 | 287.2386 | 240.1352
889.9417 | 229.144 | 239.0535 | 287.5058 | 239.4495
890.9417 | 230.2102 | 239.9467 | 287.6096 | 239.1487
891.9417 | 230.2024 | 239.2314 | 288.1151 | 238.1664
892.9417 | 231.3131 | 239.2825 | 289.5397 | 238.2238
893.9417 | 231.0191 | 238.4385 | 288.5807 | 237.3996
894.9417 | 231.3633 | 238.0733 | 287.636 | 236.8154
895.9417 | 230.8166 | 237.7682 | 286.7362 | 236.289
896.9417 | 230.5705 | 237.6082 | 286.17 | 236.0917
897.9417 | 230.8026 | 237.9011 | 285.8104 | 235.6576
898.9417 | 230.7935 | 237.5397 | 284.7798 | 235.7814
899.9417 | 230.8125 | 237.4756 | 284.8421 | 235.1215
900.9417 | 231.5887 | 237.4179 | 285.8225 | 235.2167
901.9417 | 231.7081 | 236.4804 | 284.3544 | 234.7245
902.9417 | 232.5364 | 236.4776 | 283.4723 | 235.0864
903.9417 | 232.3091 | 236.355 | 282.9816 | 234.4117
904.9417 | 232.2624 | 235.5645 | 282.2907 | 233.8537
905.9417 | 231.6365 | 235.106 | 280.9582 | 233.5661
906.9417 | 230.6014 | 234.5757 | 279.744 | 233.4657
907.9417 | 229.8351 | 235.2737 | 279.5756 | 232.9998
908.9417 | 229.1377 | 235.9143 | 280.3564 | 234.8209
909.9417 | 229.4761 | 236.2777 | 281.3465 | 234.9178
910.9417 | 229.915 | 235.9351 | 281.7425 | 235.477
911.9417 | 229.8677 | 235.8319 | 281.6163 | 235.6782
912.9417 | 229.0054 | 235.4659 | 282.3873 | 235.8047
913.9417 | 228.5269 | 235.7206 | 284.4015 | 237.8274
914.9417 | 229.6501 | 235.3956 | 285.842 | 238.4733
915.9417 | 229.7956 | 236.0818 | 288.0828 | 240.3533
916.9417 | 230.6746 | 237.218 | 288.0425 | 240.6955
917.9417 | 232.1546 | 237.0973 | 288.6624 | 241.5344
918.9417 | 232.4796 | 237.1203 | 287.2958 | 240.6807
919.9417 | 232.4456 | 237.1059 | 286.9869 | 240.6468
920.9417 | 233.4481 | 237.5661 | 286.6794 | 240.9618
921.9417 | 234.7746 | 237.3328 | 286.3032 | 241.9351
922.9417 | 235.2641 | 237.6447 | 287.0666 | 243.6536
923.9417 | 235.2377 | 238.1871 | 289.5363 | 244.4277
924.9417 | 234.6366 | 240.2447 | 290.6424 | 245.9541
925.9417 | 233.5163 | 241.7795 | 292.2097 | 246.0581
926.9417 | 234.5057 | 243.6955 | 293.6728 | 245.9296
927.9417 | 235.9989 | 243.8265 | 293.6225 | 246.5676
928.9417 | 235.7453 | 243.7507 | 293.8034 | 247.0659
929.9417 | 235.6029 | 247.5647 | 294.5163 | 249.0238
930.9417 | 236.3613 | 248.6207 | 294.6392 | 251.3697
931.9417 | 237.1899 | 250.7029 | 295.2106 | 253.6577
932.9417 | 238.7016 | 251.8394 | 296.9146 | 256.2954
933.9417 | 240.1394 | 252.7951 | 299.0617 | 256.6577
934.9417 | 241.2667 | 252.692 | 298.3663 | 257.3928
935.9417 | 242.8469 | 252.6269 | 299.0896 | 256.2669
936.9417 | 243.8804 | 252.1053 | 299.3958 | 255.5262
937.9417 | 244.974 | 251.844 | 298.22 | 255.0323
938.9417 | 245.9116 | 252.2176 | 299.168 | 254.055
939.9417 | 246.5877 | 251.6724 | 300.1647 | 252.8097
940.9417 | 247.1324 | 251.0086 | 299.1794 | 251.8627
941.9417 | 246.9833 | 251.1103 | 298.3707 | 250.7641
942.9417 | 248.8364 | 251.0789 | 300.2387 | 250.8672
943.9417 | 249.6011 | 251.054 | 299.1481 | 250.0109
944.9417 | 249.5755 | 251.7164 | 299.5488 | 250.277
945.9417 | 250.7562 | 252.1141 | 301.387 | 249.8254
946.9417 | 250.0124 | 251.3989 | 300.8865 | 249.3988
947.9417 | 249.9779 | 250.895 | 300.6796 | 249.3329
948.9417 | 249.761 | 250.8211 | 299.6891 | 249.374
949.9417 | 248.7892 | 250.6291 | 299.7143 | 249.3117
950.9417 | 248.8379 | 251.396 | 301.3321 | 250.774
951.9417 | 248.563 | 250.6656 | 302.2452 | 251.7518
952.9417 | 249.3178 | 250.1703 | 302.6528 | 252.2913
953.9417 | 250.2255 | 249.6813 | 301.1673 | 251.8274
954.9417 | 250.3233 | 249.6309 | 301.2496 | 251.8059
955.9417 | 249.8208 | 249.1954 | 300.3829 | 251.9845
956.9417 | 249.7692 | 248.8728 | 298.6783 | 252.3437
957.9417 | 249.0715 | 248.0548 | 297.6916 | 252.1758
958.9417 | 249.4154 | 247.4338 | 295.97 | 251.3928
959.9417 | 249.5619 | 247.5977 | 295.2259 | 250.7924
960.9417 | 250.8769 | 246.7396 | 294.013 | 250.0604
961.9417 | 249.8299 | 246.6148 | 292.7301 | 249.8455
962.9417 | 250.5012 | 247.2239 | 293.7469 | 248.8996
963.9417 | 250.7331 | 247.4135 | 294.418 | 248.6224
964.9417 | 250.9237 | 247.0083 | 293.955 | 248.1658
965.9417 | 251.0222 | 247.6322 | 294.6167 | 247.7752
966.9417 | 251.5188 | 247.5575 | 295.9341 | 248.4791
967.9417 | 252.7982 | 247.2721 | 297.0595 | 247.8926
968.9417 | 252.8969 | 246.4086 | 296.4518 | 247.5703
969.9417 | 252.5748 | 247.0055 | 296.9028 | 248.2172
970.9417 | 252.3135 | 248.7578 | 298.6714 | 250.3595
971.9417 | 252.2542 | 251.7339 | 300.4444 | 250.5069
972.9417 | 252.6443 | 252.1241 | 300.6803 | 251.7689
973.9417 | 252.9073 | 254.0158 | 301.5795 | 252.5484
974.9417 | 254.4364 | 255.5848 | 302.4335 | 256.0282
975.9417 | 254.8813 | 257.2632 | 304.2337 | 256.2313
976.9417 | 254.8355 | 258.0735 | 305.0179 | 256.0959
977.9417 | 253.9855 | 259.0902 | 307.0989 | 259.6651
978.9417 | 253.8298 | 260.1711 | 306.1459 | 261.2815
979.9417 | 254.2922 | 260.3167 | 305.8249 | 261.5091
980.9417 | 254.3854 | 260.049 | 305.7165 | 260.9944
981.9417 | 253.313 | 259.7122 | 304.4712 | 260.8194
982.9417 | 252.7091 | 261.5372 | 306.1002 | 262.6375
983.9417 | 252.2827 | 264.6113 | 307.4051 | 264.6452
984.9417 | 253.5627 | 266.3495 | 308.3332 | 265.0286
985.9417 | 253.5916 | 267.8309 | 308.535 | 265.028
986.9417 | 253.1188 | 268.5599 | 308.2241 | 264.1223
987.9417 | 253.2415 | 267.4933 | 306.9748 | 263.0232
988.9417 | 253.2467 | 267.2328 | 307.4815 | 263.3166
989.9417 | 253.9856 | 266.4622 | 307.3007 | 263.7551
990.9417 | 254.1449 | 265.7301 | 309.0674 | 265.9117
991.9417 | 254.6697 | 265.764 | 309.372 | 265.6724
992.9417 | 254.8824 | 265.5176 | 309.3572 | 265.0094
993.9417 | 254.9058 | 266.1736 | 309.9069 | 264.8654
994.9417 | 255.0314 | 267.2643 | 310.1335 | 265.3482
995.9417 | 256.3195 | 268.2777 | 311.0989 | 265.1619
996.9417 | 257.0045 | 268.2617 | 312.656 | 266.0212
997.9417 | 257.3312 | 268.7821 | 314.4918 | 267.8404
998.9417 | 258.2308 | 268.858 | 315.0602 | 268.3973
999.9417 | 259.799 | 269.7207 | 316.2672 | 270.1248
1000.9417 | 259.8523 | 269.3655 | 315.6184 | 269.8977
1001.9417 | 259.9276 | 268.2568 | 314.9883 | 268.4409
1002.9417 | 259.6241 | 268.5583 | 315.8193 | 267.4791
1003.9417 | 259.3549 | 270.4455 | 317.0373 | 267.8372
1004.9417 | 258.7914 | 270.8606 | 317.387 | 267.2888
1005.9417 | 258.6116 | 272.9407 | 317.4425 | 267.0415
1006.9417 | 258.1778 | 274.3702 | 317.577 | 266.3691
1007.9417 | 257.6627 | 275.0551 | 318.9512 | 265.343
1008.9417 | 257.9537 | 276.1946 | 318.6182 | 265.8723
1009.9417 | 257.5617 | 278.0397 | 319.5108 | 264.7826
1010.9417 | 256.8196 | 278.4702 | 319.6381 | 264.4147
1011.9417 | 256.6128 | 278.9502 | 319.14 | 264.0132
1012.9417 | 256.1155 | 280.1018 | 318.7748 | 265.1108
1013.9417 | 257.6029 | 281.3442 | 321.1267 | 266.1858
1014.9417 | 257.8129 | 282.0985 | 320.8365 | 265.9058
1015.9417 | 256.9904 | 282.3597 | 320.7624 | 265.6137
1016.9417 | 256.9328 | 283.5242 | 320.323 | 265.7089
1017.9417 | 256.4777 | 283.2212 | 319.526 | 265.1993
1018.9417 | 255.9421 | 282.744 | 318.278 | 264.2711
1019.9417 | 256.3793 | 282.3493 | 318.2563 | 263.6664
1020.9417 | 256.3675 | 284.114 | 319.5247 | 264.3917
1021.9417 | 255.4941 | 284.4913 | 321.8212 | 264.9175
1022.9417 | 254.9241 | 284.498 | 321.6411 | 264.2311
1023.9417 | 254.9763 | 284.6935 | 323.7052 | 264.0181
1024.9417 | 254.4229 | 284.441 | 323.0906 | 263.0305
1025.9417 | 254.2228 | 284.1491 | 322.3325 | 262.3828
1026.9417 | 254.3157 | 283.1774 | 321.436 | 262.0315
1027.9417 | 254.4898 | 282.4532 | 321.2045 | 261.4972
1028.9417 | 254.4241 | 282.1405 | 321.1574 | 260.8853
1029.9417 | 253.9549 | 281.6436 | 322.3807 | 260.5117
1030.9417 | 252.9193 | 281.4518 | 321.1047 | 259.8737
1031.9417 | 253.3605 | 280.5843 | 318.8617 | 259.1117
1032.9417 | 253.8295 | 280.3992 | 320.6837 | 259.4057
1033.9417 | 252.9336 | 281.1508 | 320.0248 | 258.6077
1034.9417 | 252.4508 | 281.6072 | 318.9516 | 257.5185
1035.9417 | 252.1884 | 281.5331 | 317.8768 | 256.5037
1036.9417 | 252.627 | 280.9653 | 318.5486 | 256.1913
1037.9417 | 251.9876 | 280.173 | 318.6197 | 255.8647
1038.9417 | 251.4152 | 280.6619 | 319.3677 | 255.5653
1039.9417 | 251.1872 | 281.4942 | 319.0402 | 254.9246
1040.9417 | 250.4389 | 282.5712 | 317.5682 | 254.1837
1041.9417 | 250.5332 | 282.8708 | 318.2588 | 253.8436
1042.9417 | 249.6471 | 282.4869 | 317.9823 | 253.5574
1043.9417 | 249.274 | 282.5733 | 318.3441 | 253.2502
1044.9417 | 249.7539 | 282.8195 | 319.2317 | 253.1206
1045.9417 | 251.1254 | 283.137 | 320.6193 | 253.8949
1046.9417 | 251.0571 | 283.5438 | 321.4939 | 254.5171
1047.9417 | 251.0518 | 282.7753 | 322.5626 | 254.851
1048.9417 | 251.1734 | 283.6753 | 322.9818 | 254.6326
1049.9417 | 251.5236 | 283.872 | 324.6217 | 255.4599
1050.9417 | 252.7928 | 284.0997 | 325.5916 | 257.1026
1051.9417 | 252.5082 | 284.2334 | 326.1395 | 256.8765
1052.9417 | 252.881 | 284.8437 | 325.1493 | 257.3017
1053.9417 | 253.4552 | 285.2271 | 324.5451 | 257.4773
1054.9417 | 253.6595 | 285.2414 | 324.3642 | 258.1181
1055.9417 | 253.9935 | 285.1989 | 324.2677 | 257.6449
1056.9417 | 254.0241 | 286.0287 | 324.9462 | 259.8979
1057.9417 | 254.8909 | 287.0262 | 327.5725 | 261.8524
1058.9417 | 255.0816 | 287.3242 | 326.429 | 261.4372
1059.9417 | 255.2131 | 286.9078 | 325.5635 | 261.3842
1060.9417 | 255.9518 | 286.7745 | 325.5171 | 262.1871
1061.9417 | 255.4236 | 286.4055 | 326.2328 | 263.0279
1062.9417 | 255.2121 | 288.0328 | 325.6181 | 262.5074
1063.9417 | 256.5797 | 287.3634 | 325.349 | 263.3365
1064.9417 | 256.7843 | 287.4663 | 325.3669 | 265.6327
1065.9417 | 256.5331 | 287.1665 | 325.3247 | 265.1415
1066.9417 | 256.752 | 287.2342 | 325.2674 | 265.1252
1067.9417 | 256.3952 | 287.2229 | 325.4964 | 264.3056
1068.9417 | 256.8077 | 287.2896 | 326.577 | 263.8849
1069.9417 | 256.2279 | 287.0415 | 326.8669 | 264.2878
1070.9417 | 256.7295 | 286.7443 | 327.1237 | 264.9208
1071.9417 | 257.017 | 287.8515 | 328.1068 | 265.3595
1072.9417 | 257.6687 | 287.4841 | 328.4368 | 266.1156
1073.9573 | 257.6863 | 287.4147 | 328.198 | 265.8742
1074.9417 | 257.5723 | 287.4889 | 329.1908 | 265.4554
1075.9417 | 257.7054 | 286.7305 | 330.7458 | 265.9996
1076.9417 | 256.7889 | 285.8574 | 330.7423 | 265.7207
1077.9417 | 256.2925 | 286.343 | 329.9511 | 265.1585
1078.9417 | 256.1775 | 287.2519 | 329.4328 | 264.1232
1079.9573 | 255.5214 | 288.1363 | 328.5806 | 263.2922
1080.9417 | 254.718 | 287.5171 | 326.1667 | 262.1438
1081.9417 | 254.562 | 288.5435 | 326.2817 | 262.1131
1082.9417 | 254.4099 | 289.2419 | 325.3259 | 261.6107
1083.9417 | 254.3271 | 290.2278 | 325.4383 | 260.8889
1084.9417 | 253.8251 | 290.6417 | 324.8634 | 260.2236
1085.9417 | 254.5643 | 290.4532 | 324.9513 | 260.1548
1086.9417 | 254.6412 | 291.6482 | 325.0229 | 259.9916
1087.9417 | 253.8729 | 292.2115 | 322.9183 | 259.3139
1088.9417 | 253.395 | 292.0943 | 321.5548 | 258.5323
1089.9417 | 252.6561 | 292.9495 | 321.6771 | 258.0322
1090.9417 | 252.8343 | 294.3377 | 322.552 | 258.6358
1091.9417 | 254.8805 | 295.4138 | 324.1948 | 259.4112
1092.9417 | 255.6389 | 297.1944 | 325.5955 | 259.0132
1093.9417 | 255.9824 | 297.5953 | 326.1956 | 258.1965
1094.9417 | 255.8116 | 298.4913 | 325.876 | 258.3107
1095.9417 | 255.796 | 299.5739 | 325.5141 | 258.4452
1096.9417 | 255.6041 | 298.6273 | 325.2394 | 258.7689
1097.9417 | 255.1752 | 298.3938 | 324.5076 | 257.8649
1098.9417 | 255.8518 | 298.4146 | 323.9211 | 257.9249
1099.9417 | 256.8694 | 298.1741 | 323.4874 | 259.1972
1100.9417 | 257.2799 | 298.0903 | 324.2014 | 258.3993
1101.9417 | 257.8651 | 297.2889 | 324.2254 | 258.6255
1102.9417 | 259.0798 | 296.2355 | 325.3358 | 259.0667
1103.9417 | 259.5108 | 296.7308 | 325.6586 | 260.5257
1104.9417 | 260.5233 | 296.3527 | 326.5203 | 261.7451
1105.9417 | 260.115 | 296.2888 | 327.046 | 262.0695
1106.9417 | 260.1186 | 296.1895 | 325.6547 | 261.798
1107.9417 | 259.972 | 297.2145 | 325.4269 | 261.7625
1108.9417 | 259.6403 | 297.9624 | 325.5146 | 261.6498
1109.9417 | 258.8388 | 298.55 | 324.3692 | 260.9035
1110.9417 | 258.4805 | 298.4863 | 324.1392 | 260.2167
1111.9417 | 258.7719 | 297.8458 | 325.3203 | 261.1536
1112.9417 | 259.4118 | 296.5632 | 325.285 | 261.2522
1113.9417 | 259.7463 | 295.3813 | 324.6927 | 261.6943
1114.9417 | 260.7163 | 295.9475 | 325.4094 | 263.7898
1115.9417 | 261.2488 | 295.5927 | 324.9493 | 264.7164
1116.9417 | 261.215 | 294.538 | 325.4288 | 264.1508
1117.9417 | 262.7978 | 295.1109 | 326.7615 | 265.1932
1118.9417 | 262.9409 | 296.3389 | 327.398 | 266.593
1119.9417 | 263.1593 | 296.7289 | 328.0595 | 266.1802
1120.9417 | 263.154 | 296.7003 | 327.9991 | 266.1176
1121.9417 | 262.496 | 296.7412 | 328.4582 | 266.3852
1122.9417 | 261.9759 | 297.6615 | 329.2672 | 266.8332
1123.9417 | 261.9543 | 297.8126 | 329.3583 | 267.2384
1124.9417 | 261.9823 | 298.3618 | 329.1646 | 268.8285
1125.9417 | 262.2877 | 298.1194 | 329.1578 | 268.8071
1126.9417 | 262.1822 | 297.8128 | 328.9583 | 268.6232
1127.9417 | 262.5253 | 298.5788 | 329.4546 | 270.3692
1128.9417 | 262.8532 | 300.3239 | 330.4339 | 272.5328
1129.9417 | 263.2635 | 300.4608 | 330.7457 | 271.595
1130.9417 | 263.309 | 300.731 | 329.9715 | 271.0576
1131.9417 | 264.2771 | 301.3314 | 329.9341 | 271.7943
1132.9417 | 264.3795 | 301.9904 | 330.1801 | 271.2415
1133.9417 | 263.9167 | 301.0759 | 330.808 | 270.2612
1134.9417 | 263.6552 | 301.7854 | 329.5746 | 269.7745
1135.9417 | 263.9285 | 301.8463 | 328.7306 | 269.5632
1136.9417 | 263.4082 | 301.9196 | 328.903 | 269.2808
1137.9417 | 262.91 | 301.5458 | 328.0219 | 268.231
1138.9417 | 263.0691 | 303.0768 | 329.4198 | 267.9103
1139.9417 | 263.0807 | 301.9972 | 328.9145 | 267.306
1140.9417 | 262.9818 | 302.4766 | 328.3126 | 266.4284
1141.9417 | 263.2346 | 302.1083 | 328.5255 | 266.2312
1142.9417 | 263.9936 | 301.4855 | 328.4458 | 267.9419
1143.9417 | 263.9267 | 303.0712 | 329.6417 | 272.8065
1144.9417 | 265.5065 | 303.7149 | 330.1043 | 275.2894
1145.9417 | 266.2708 | 303.4007 | 329.3545 | 275.6553
1146.9417 | 266.4579 | 302.8789 | 327.8056 | 274.2741
1147.9417 | 265.4014 | 302.3524 | 327.3061 | 273.6819
1148.9417 | 264.9391 | 302.3361 | 326.7304 | 273.3039
1149.9417 | 265.5405 | 302.6197 | 327.7482 | 273.7162
1150.9417 | 265.9437 | 301.2931 | 327.5609 | 275.0349
1151.9417 | 265.6157 | 300.7481 | 326.78 | 274.1396
1152.9417 | 264.8961 | 301.1486 | 328.2727 | 274.6083
1153.9417 | 264.6649 | 300.9602 | 328.465 | 276.0891
1154.9417 | 265.0334 | 299.7881 | 330.1023 | 277.2534
1155.9417 | 265.3318 | 300.2694 | 329.9116 | 276.4048
1156.9417 | 265.9788 | 300.539 | 331.746 | 278.432
1157.9417 | 266.6777 | 301.3434 | 332.6021 | 278.6426
1158.9417 | 266.5558 | 303.419 | 332.8962 | 278.3012
1159.9417 | 266.9955 | 303.3205 | 333.2135 | 277.7932
1160.9417 | 267.165 | 304.415 | 333.8163 | 277.8957
1161.9417 | 267.193 | 303.7642 | 333.9047 | 277.6028
1162.9417 | 267.2406 | 302.8025 | 332.7566 | 278.1819
1163.9417 | 266.7151 | 302.8517 | 331.5775 | 278.0882
1164.9417 | 267.7039 | 302.4079 | 330.6059 | 277.5916
1165.9417 | 266.4454 | 302.6134 | 330.4371 | 278.8054
1166.9417 | 266.4474 | 301.6112 | 329.6649 | 277.8644
1167.9417 | 266.6246 | 300.7164 | 329.9262 | 277.5813
1168.9417 | 266.5914 | 301.1397 | 330.2704 | 276.9967
1169.9417 | 267.4606 | 300.9976 | 330.0888 | 277.0231
1170.9417 | 268.0167 | 302.0184 | 331.4275 | 278.9485
1171.9417 | 267.1546 | 302.0621 | 331.8423 | 278.9023
1172.9417 | 267.0162 | 301.346 | 331.7161 | 278.3637
1173.9417 | 267.2279 | 302.1685 | 332.7957 | 279.0227
1174.9417 | 266.3962 | 301.6165 | 333.6481 | 278.86
1175.9417 | 266.4066 | 301.7263 | 333.4908 | 278.615
1176.9417 | 266.6241 | 302.2732 | 334.3124 | 278.4236
1177.9417 | 266.6255 | 302.7549 | 334.6615 | 277.9373
1178.9417 | 268.7443 | 302.2272 | 336.6888 | 277.955
1179.9417 | 268.6684 | 301.5437 | 337.1383 | 278.288
1180.9417 | 268.9194 | 302.327 | 337.8394 | 278.6198
1181.9417 | 268.8037 | 301.3994 | 337.9855 | 278.4988
1182.9417 | 268.8784 | 301.1115 | 338.4535 | 277.737
1183.9417 | 269.2212 | 302.7275 | 338.9508 | 276.9659
1184.9417 | 269.577 | 303.6722 | 338.5847 | 277.0231
1185.9417 | 269.6783 | 304.1082 | 338.6435 | 277.914
1186.9417 | 269.2907 | 304.872 | 338.1893 | 279.0009
1187.9417 | 269.1854 | 304.9426 | 337.7177 | 280.1612
1188.9417 | 269.338 | 306.3633 | 337.6676 | 279.8845
1189.9417 | 269.7383 | 306.1798 | 337.0813 | 280.495
1190.9417 | 270.8534 | 306.1384 | 337.445 | 282.5222
1191.9417 | 271.4008 | 306.0196 | 338.9058 | 285.08
1192.9417 | 272.0024 | 304.8723 | 338.047 | 284.1009
1193.9417 | 270.7698 | 305.0169 | 337.3743 | 283.7039
1194.9417 | 271.2629 | 304.3787 | 337.2468 | 283.6652
1195.9417 | 272.206 | 304.303 | 336.7823 | 284.7285
1196.9417 | 272.2482 | 305.3569 | 337.7378 | 285.8878
1197.9417 | 272.0941 | 305.2717 | 337.7459 | 288.1005
1198.9417 | 273.1731 | 304.9241 | 336.4401 | 287.1713
1199.9417 | 273.3675 | 304.2219 | 337.0393 | 286.3577
1200.9417 | 275.2387 | 304.2771 | 338.0605 | 285.1651
1201.9417 | 274.5186 | 303.599 | 336.097 | 284.2307
1202.9417 | 274.2896 | 302.4688 | 334.613 | 282.8863
1203.9417 | 274.3145 | 302.2057 | 333.3627 | 281.9027
1204.9417 | 273.4664 | 301.1953 | 333.9523 | 280.9164
1205.9417 | 273.6937 | 302.4378 | 334.8454 | 280.3568
1206.9417 | 274.3623 | 301.7405 | 334.2849 | 280.3333
1207.9417 | 275.0203 | 301.2344 | 333.7282 | 279.0928
1208.9417 | 276.6415 | 300.9683 | 334.6367 | 278.6378
1209.9417 | 277.7709 | 299.71 | 332.3297 | 277.2843
1210.9417 | 277.0765 | 298.755 | 331.8596 | 276.3298
1211.9417 | 278.0371 | 297.5223 | 332.2677 | 275.5716
1212.9417 | 277.4588 | 296.5571 | 331.1071 | 274.8053
1213.9417 | 276.9239 | 295.7446 | 330.7505 | 274.8868
1214.9417 | 277.4201 | 294.9677 | 330.5628 | 274.7428
1215.9417 | 277.5715 | 294.0658 | 330.0741 | 274.8322
1216.9417 | 278.5587 | 293.8313 | 330.7492 | 276.111
1217.9417 | 279.105 | 293.4195 | 332.4857 | 275.8247
1218.9417 | 279.5702 | 293.5464 | 332.6207 | 275.2109
1219.9417 | 279.9699 | 293.2477 | 333.3154 | 276.3968
1220.9417 | 279.1939 | 293.9684 | 333.9056 | 277.0857
1221.9417 | 279.3632 | 294.9435 | 334.5461 | 277.8616
1222.9417 | 280.1318 | 294.6826 | 335.8408 | 280.4584
1223.9417 | 280.1048 | 294.4705 | 336.0759 | 281.7626
1224.9417 | 281.1538 | 296.2172 | 337.3592 | 285.7664
1225.9417 | 280.4185 | 295.2257 | 337.4574 | 286.5538
1226.9417 | 279.6027 | 296.0462 | 337.4873 | 287.874
1227.9417 | 279.3826 | 296.5816 | 338.2317 | 287.1596
1228.9417 | 279.2106 | 297.3649 | 339.2857 | 285.845
1229.9417 | 278.7801 | 298.1399 | 339.3838 | 285.9947
1230.9417 | 278.6013 | 298.6805 | 339.3862 | 287.1488
1231.9417 | 277.8338 | 298.3978 | 340.3262 | 287.1067
1232.9417 | 278.0583 | 298.5518 | 340.1057 | 285.6807
1233.9417 | 278.7783 | 300.5227 | 339.9518 | 285.8071
1234.9417 | 277.988 | 301.0547 | 340.205 | 285.997
1235.9417 | 277.4482 | 301.1271 | 339.1102 | 284.9396
1236.9417 | 276.3098 | 302.3084 | 338.9299 | 286.1994
1237.9417 | 275.8361 | 303.2578 | 338.8589 | 286.2102
1238.9417 | 275.8336 | 303.5479 | 339.4312 | 287.2865
1239.9417 | 274.8138 | 302.963 | 340.8244 | 286.4767
1240.9417 | 274.2794 | 302.3979 | 339.943 | 285.1824
1241.9417 | 274.2972 | 302.3251 | 338.3828 | 283.6639
1242.9417 | 274.1451 | 301.0323 | 337.0837 | 282.4569
1243.9417 | 274.2813 | 299.8785 | 336.3973 | 281.1254
1244.9417 | 275.2182 | 300.4028 | 337.4809 | 281.2089
1245.9417 | 275.4965 | 299.6464 | 337.8313 | 282.8804
1246.9417 | 276.156 | 299.5129 | 337.7283 | 281.9411
1247.9417 | 276.3043 | 300.2725 | 338.1475 | 281.4068
1248.9417 | 276.4105 | 299.0163 | 338.5226 | 282.109
1249.9417 | 277.079 | 299.4603 | 338.4586 | 281.3029
1250.9417 | 277.4739 | 299.3879 | 338.5923 | 280.9571
1251.9417 | 277.8018 | 299.2299 | 338.8613 | 282.1505
1252.9417 | 278.3158 | 298.8451 | 338.662 | 283.1426
1253.9417 | 277.4273 | 298.1511 | 339.3949 | 283.7395
1254.9417 | 278.4054 | 297.865 | 339.9714 | 283.5474
1255.9417 | 277.3866 | 297.9624 | 340.0658 | 283.2603
1256.9417 | 277.6725 | 298.9475 | 341.1183 | 283.2315
1257.9417 | 277.5126 | 299.4737 | 341.0985 | 282.5446
1258.9417 | 277.3962 | 299.517 | 341.3624 | 281.6245
1259.9417 | 278.5431 | 299.6159 | 341.9484 | 281.18
1260.9417 | 278.7866 | 300.7248 | 342.4852 | 281.5984
1261.9417 | 278.4793 | 300.9396 | 342.9503 | 280.8474
1262.9417 | 278.8405 | 300.5331 | 343.1984 | 281.8189
1263.9417 | 278.5219 | 299.7165 | 343.3656 | 282.1061
1264.9417 | 278.8298 | 300.3757 | 343.8085 | 282.0179
1265.9417 | 277.8303 | 298.9948 | 342.8137 | 281.134
1266.9417 | 277.9666 | 298.8739 | 342.2955 | 280.7776
1267.9417 | 278.2699 | 299.5782 | 342.7246 | 282.9693
1268.9417 | 278.4909 | 299.0439 | 342.9795 | 284.3343
1269.9417 | 278.7132 | 298.3099 | 341.5587 | 284.1924
1270.9417 | 279.1194 | 297.1603 | 341.3158 | 284.1037
1271.9417 | 278.6534 | 296.0587 | 341.8114 | 284.034
1272.9417 | 277.8386 | 295.3203 | 342.1069 | 284.1245
1273.9417 | 277.0403 | 295.4257 | 341.756 | 282.852
1274.9417 | 276.2543 | 296.009 | 340.505 | 281.6986
1275.9417 | 276.7205 | 296.5958 | 340.5769 | 281.0376
1276.9417 | 276.3482 | 296.7093 | 340.6313 | 280.9182
1277.9417 | 276.4272 | 297.6366 | 339.9764 | 280.634
1278.9417 | 276.0868 | 297.8041 | 340.8165 | 280.3847
1279.9417 | 276.5286 | 298.4497 | 341.0037 | 279.436
1280.9417 | 276.2738 | 297.8378 | 340.081 | 278.4484
1281.9417 | 276.1684 | 298.6593 | 340.6184 | 277.8009
1282.9417 | 275.0041 | 300.7681 | 340.3309 | 276.8542
1283.9417 | 273.8282 | 301.5977 | 340.4124 | 275.9651
1284.9417 | 273.4376 | 301.3381 | 339.5432 | 276.5493
1285.9417 | 273.0345 | 300.8829 | 337.9028 | 275.7312
1286.9417 | 272.7927 | 301.1066 | 336.9984 | 274.3777
1287.9417 | 272.6491 | 301.5063 | 336.7207 | 274.1638
1288.9417 | 271.4787 | 301.2477 | 335.1612 | 274.005
1289.9417 | 271.0431 | 300.6284 | 332.8385 | 273.0502
1290.9417 | 271.4783 | 300.8872 | 330.7552 | 272.1347
1291.9417 | 270.9071 | 299.8617 | 328.5922 | 271.448
1292.9417 | 270.6046 | 299.5449 | 327.4484 | 273.3472
1293.9417 | 270.7211 | 299.0169 | 327.6864 | 272.7117
1294.9417 | 270.8121 | 300.1879 | 328.2295 | 273.5894
1295.9417 | 271.0784 | 300.3907 | 328.6643 | 273.0928
1296.9417 | 270.8735 | 300.6517 | 327.7459 | 272.404
1297.9417 | 271.5827 | 300.9687 | 327.9826 | 272.1138
1298.9417 | 272.7165 | 302.0907 | 330.5563 | 273.6104
1299.9417 | 273.2719 | 302.6294 | 332.981 | 275.629
1300.9417 | 273.0554 | 301.9912 | 334.2363 | 276.1287
1301.9417 | 272.8486 | 301.8246 | 333.791 | 275.8642
1302.9417 | 273.2929 | 302.6261 | 334.0207 | 275.4059
1303.9417 | 273.1688 | 302.5121 | 335.2262 | 275.5108
1304.9417 | 273.0512 | 302.3582 | 334.8324 | 274.7034
1305.9417 | 272.9916 | 302.5259 | 334.9997 | 274.78
1306.9417 | 272.5443 | 303.2145 | 335.1097 | 274.8228
1307.9417 | 272.2558 | 303.4553 | 334.2818 | 275.0397
1308.9417 | 271.6769 | 303.1594 | 334.2497 | 274.3396
1309.9417 | 270.9934 | 301.9733 | 332.6728 | 273.9272
1310.9417 | 270.3941 | 302.1154 | 331.5203 | 273.5078
1311.9417 | 269.6595 | 301.7079 | 331.0633 | 272.8823
1312.9417 | 269.2921 | 301.5863 | 329.9262 | 272.5671
1313.9417 | 268.2506 | 301.8516 | 328.5157 | 271.4084
1314.9417 | 267.582 | 301.4237 | 327.4123 | 270.5902
1315.9417 | 267.1213 | 301.8681 | 327.6836 | 270.5425
1316.9417 | 266.6829 | 301.7848 | 328.1238 | 270.5412
1317.9417 | 266.9898 | 303.0277 | 329.8281 | 270.3481
1318.9417 | 267.0603 | 304.2071 | 330.5077 | 270.5227
1319.9417 | 267.5136 | 303.6032 | 329.6206 | 271.0712
1320.9417 | 267.7679 | 302.5338 | 328.7587 | 270.5234
1321.9417 | 268.2986 | 301.6388 | 329.5839 | 272.1623
1322.9417 | 268.9083 | 301.3822 | 330.2653 | 273.1206
1323.9417 | 270.2134 | 302.4901 | 332.5884 | 275.6424
1324.9417 | 269.9686 | 302.0932 | 333.2123 | 274.9591
1325.9417 | 270.0334 | 304.4045 | 334.965 | 275.5641
1326.9417 | 270.0617 | 304.8469 | 335.8874 | 276.5226
1327.9417 | 270.924 | 305.0112 | 335.7517 | 275.6453
1328.9417 | 270.6072 | 305.3195 | 334.3784 | 275.6069
1329.9417 | 271.935 | 306.0289 | 334.0773 | 275.2237
1330.9417 | 273.2645 | 306.7803 | 334.0681 | 275.741
1331.9417 | 274.9332 | 306.815 | 334.3965 | 276.016
1332.9417 | 276.2654 | 307.3993 | 335.033 | 277.711
1333.9417 | 277.3181 | 307.6923 | 335.9466 | 279.4338
1334.9417 | 278.0195 | 307.7208 | 337.4147 | 280.5485
1335.9417 | 278.5391 | 307.1165 | 338.0092 | 281.7937
1336.9417 | 278.5717 | 307.2474 | 337.6017 | 282.5671
1337.9417 | 278.6625 | 307.5063 | 337.9107 | 282.2121
1338.9417 | 279.5078 | 306.927 | 338.7268 | 281.9647
1339.9417 | 278.8958 | 307.5779 | 338.6274 | 280.6813
1340.9417 | 278.2314 | 307.5519 | 338.7222 | 280.1322
1341.9417 | 277.6112 | 307.8655 | 339.3824 | 279.7016
1342.9417 | 276.9458 | 308.4744 | 339.6815 | 279.7955
1343.9417 | 277.3645 | 309.1068 | 339.27 | 279.6983
1344.9417 | 276.824 | 309.3103 | 338.1243 | 279.4258
1345.9417 | 276.582 | 310.0368 | 337.9597 | 278.7479
1346.9417 | 276.5981 | 311.7084 | 337.6958 | 278.498
1347.9417 | 276.2508 | 311.1128 | 336.9968 | 277.4309
1348.9417 | 275.6821 | 311.1472 | 335.8818 | 277.3619
1349.9417 | 275.8712 | 310.8135 | 335.2597 | 276.961
1350.9417 | 275.5578 | 310.2181 | 334.8072 | 276.4471
1351.9417 | 275.2509 | 309.9935 | 334.6231 | 275.6872
1352.9417 | 274.6624 | 311.6128 | 335.467 | 277.2652
1353.9417 | 274.8621 | 312.0519 | 335.4297 | 277.5438
1354.9417 | 275.4553 | 312.5222 | 334.99 | 277.7305
1355.9417 | 276.5031 | 311.6557 | 333.2898 | 276.7622
1356.9417 | 277.4134 | 310.6687 | 332.5627 | 276.0343
1357.9417 | 277.5165 | 309.6916 | 333.0983 | 276.6135
1358.9417 | 276.6143 | 310.8874 | 334.692 | 276.5979
1359.9417 | 277.4244 | 310.7347 | 335.3565 | 277.0314
1360.9417 | 276.9034 | 310.7316 | 335.4855 | 276.8722
1361.9417 | 276.7473 | 310.6742 | 335.5085 | 276.8249
1362.9417 | 277.0547 | 311.7584 | 335.8001 | 277.4882
1363.9417 | 277.3302 | 311.4161 | 336.1079 | 278.1818
1364.9417 | 276.8106 | 310.7347 | 337.8215 | 278.1711
1365.9417 | 275.6259 | 311.318 | 338.5276 | 278.0934
1366.9417 | 275.573 | 310.7172 | 338.5352 | 278.3585
1367.9417 | 275.577 | 310.0788 | 338.3426 | 278.597
1368.9417 | 275.8554 | 309.8997 | 339.8701 | 278.2008
1369.9417 | 276.9169 | 309.8712 | 341.1727 | 278.8794
1370.9417 | 277.0927 | 309.6148 | 343.5164 | 279.5912
1371.9417 | 277.5335 | 309.432 | 343.4427 | 278.8277
1372.9417 | 277.9752 | 310.0589 | 343.8833 | 278.1204
1373.9417 | 278.5725 | 310.7688 | 345.4259 | 278.1112
1374.9417 | 279.2977 | 310.2967 | 345.7164 | 278.8883
1375.9417 | 279.3102 | 311.0884 | 347.7152 | 279.7255
1376.9417 | 278.8833 | 311.5387 | 346.1224 | 278.7727
1377.9417 | 278.1231 | 312.8388 | 345.1848 | 278.0981
1378.9417 | 277.1623 | 314.1968 | 345.3545 | 277.7654
1379.9417 | 277.0867 | 314.4934 | 344.8948 | 277.6748
1380.9417 | 276.808 | 314.7107 | 345.0203 | 277.0941
1381.9417 | 276.3785 | 314.7562 | 343.0668 | 276.383
1382.9417 | 276.0855 | 314.8214 | 341.7768 | 275.5554
1383.9417 | 276.4082 | 314.9762 | 341.389 | 275.2372
1384.9417 | 276.1397 | 314.591 | 341.3579 | 275.4194
1385.9417 | 275.6825 | 314.9535 | 340.8572 | 275.8553
1386.9417 | 275.1983 | 314.227 | 339.4705 | 275.3012
1387.9417 | 275.1181 | 313.8289 | 339.841 | 276.082
1388.9417 | 274.4746 | 314.5587 | 339.8401 | 276.1323
1389.9417 | 274.7279 | 315.3238 | 339.9358 | 275.8773
1390.9417 | 274.9469 | 315.6202 | 338.3663 | 275.1182
1391.9417 | 274.8737 | 314.8989 | 337.2359 | 274.8615
1392.9417 | 274.8794 | 313.6905 | 336.8095 | 274.4429
1393.9417 | 275.0148 | 313.2941 | 336.8366 | 274.214
1394.9417 | 275.6093 | 313.4787 | 336.9332 | 275.038
1395.9417 | 275.8089 | 312.8208 | 337.4955 | 275.3233
1396.9417 | 275.6108 | 312.5817 | 337.4034 | 275.3544
1397.9417 | 275.0504 | 311.6762 | 336.6686 | 275.3438
1398.9417 | 274.6837 | 311.8164 | 336.7598 | 275.9277
1399.9417 | 275.3095 | 312.9316 | 336.2874 | 276.1013
1400.9417 | 275.1386 | 313.7878 | 336.6235 | 276.1714
1401.9417 | 275.102 | 313.8213 | 337.5899 | 276.271
1402.9417 | 275.3082 | 314.4453 | 338.0439 | 276.4228
1403.9417 | 275.4809 | 314.7608 | 337.3457 | 276.54
1404.9417 | 275.3119 | 313.8216 | 335.9698 | 276.5923
1405.9417 | 275.1102 | 313.2505 | 335.0195 | 276.7977
1406.9417 | 274.9479 | 313.4691 | 335.4876 | 278.2627
1407.9417 | 275.0679 | 313.8554 | 335.0042 | 279.8954
1408.9417 | 275.3417 | 314.091 | 334.9111 | 279.491
1409.9417 | 275.5257 | 313.2793 | 335.1096 | 279.3553
1410.9417 | 276.2331 | 313.1345 | 336.4237 | 279.6361
1411.9417 | 277.3905 | 314.5441 | 338.4892 | 281.3129
1412.9417 | 277.8788 | 313.3968 | 338.3213 | 282.3417
1413.9417 | 278.1224 | 313.3906 | 338.3481 | 282.4822
1414.9417 | 278.1801 | 313.8021 | 339.1705 | 282.8375
1415.9417 | 278.8415 | 313.4294 | 338.9243 | 282.6844
1416.9417 | 278.2593 | 312.5883 | 339.6116 | 282.0778
1417.9417 | 278.0169 | 312.2648 | 339.3169 | 281.3087
1418.9417 | 277.8163 | 312.0993 | 339.5393 | 280.9014
1419.9417 | 277.3446 | 311.8771 | 339.1248 | 280.2537
1420.9417 | 277.3386 | 312.4421 | 339.0406 | 279.9853
1421.9417 | 277.566 | 312.992 | 339.5516 | 279.7871
1422.9417 | 277.7252 | 313.2496 | 338.551 | 279.3498
1423.9417 | 278.1882 | 313.5036 | 339.9911 | 279.2358
1424.9417 | 277.8952 | 313.9987 | 339.8763 | 278.5747
1425.9417 | 278.0121 | 313.8507 | 340.4594 | 278.0047
1426.9417 | 278.364 | 315.6859 | 340.8121 | 278.22
1427.9417 | 278.317 | 315.8912 | 341.9855 | 278.6983
1428.9417 | 278.0421 | 315.644 | 340.8573 | 278.143
1429.9417 | 278.0974 | 316.251 | 340.8359 | 278.8184
1430.9417 | 278.4326 | 317.9195 | 342.1539 | 279.6147
1431.9417 | 278.7454 | 320.7091 | 343.4337 | 280.3726
1432.9417 | 278.9108 | 321.3331 | 344.9571 | 281.3535
1433.9417 | 279.247 | 322.481 | 344.6495 | 280.9157
1434.9417 | 280.2269 | 324.1999 | 344.4209 | 280.8114
1435.9417 | 280.7396 | 323.5536 | 344.4242 | 281.2469
1436.9417 | 280.8941 | 324.1123 | 345.1578 | 283.4328
1437.9417 | 282.2009 | 323.3379 | 346.0622 | 286.5184
1438.9417 | 282.3057 | 323.0737 | 346.4592 | 289.5261
1439.9417 | 282.679 | 322.1558 | 345.9524 | 289.3675
1440.9417 | 282.4296 | 320.8659 | 346.44 | 288.9067
1441.9417 | 282.6527 | 320.5398 | 345.6483 | 288.2492
1442.9417 | 282.4125 | 320.9414 | 346.5053 | 288.0058
1443.9417 | 282.5792 | 320.4485 | 347.3747 | 287.7025
1444.9417 | 283.3114 | 320.9864 | 348.0816 | 287.4709
1445.9417 | 282.9706 | 321.3649 | 349.0935 | 286.8042
1446.9417 | 282.3523 | 321.6379 | 349.5699 | 286.3519
1447.9417 | 282.2976 | 321.0838 | 349.8017 | 285.986
1448.9417 | 281.1541 | 321.5552 | 349.0142 | 285.3541
1449.9417 | 280.8579 | 321.6464 | 348.1906 | 284.5419
1450.9417 | 280.7108 | 321.1309 | 348.3581 | 284.0407
1451.9417 | 280.8326 | 321.3107 | 348.5301 | 283.628
1452.9417 | 280.9151 | 322.4973 | 349.0556 | 283.291
1453.9417 | 280.6608 | 322.5796 | 348.6288 | 282.8512
1454.9417 | 281.0096 | 322.8668 | 348.3621 | 282.5162
1455.9417 | 281.1981 | 322.8323 | 349.9633 | 282.9444
1456.9417 | 281.7312 | 322.2866 | 349.6679 | 282.4199
1457.9417 | 281.6968 | 321.8354 | 349.5077 | 282.3383
1458.9417 | 282.2061 | 321.2279 | 349.7461 | 282.2226
1459.9417 | 282.2753 | 320.6309 | 349.7659 | 282.181
1460.9417 | 282.0776 | 321.104 | 349.9665 | 282.7406
1461.9417 | 282.387 | 320.8274 | 352.3457 | 284.5539
1462.9417 | 282.4627 | 321.3604 | 353.5264 | 284.9375
1463.9417 | 282.6217 | 321.5646 | 353.3775 | 284.5855
1464.9417 | 282.3927 | 322.2081 | 353.0622 | 284.0889
1465.9417 | 282.6865 | 323.0153 | 351.8654 | 283.355
1466.9417 | 282.4127 | 323.3295 | 350.3898 | 282.814
1467.9417 | 282.6067 | 323.3793 | 349.2627 | 282.5962
1468.9417 | 283.2335 | 323.016 | 348.6365 | 282.7466
1469.9417 | 283.9541 | 322.6962 | 348.0539 | 284.1207
1470.9417 | 284.6009 | 323.2304 | 348.4579 | 286.3685
1471.9417 | 286.5438 | 324.1553 | 350.7709 | 286.8238
1472.9417 | 286.6252 | 323.0496 | 351.1886 | 286.0877
1473.9417 | 286.0892 | 323.5367 | 351.5008 | 286.2977
1474.9417 | 286.9755 | 323.3581 | 351.4984 | 286.817
1475.9417 | 286.7273 | 323.9479 | 351.5213 | 286.5433
1476.9417 | 287.1452 | 325.3312 | 351.7392 | 287.3288
1477.9417 | 287.6212 | 326.0242 | 351.7692 | 288.5915
1478.9417 | 287.7985 | 325.8393 | 352.055 | 289.0807
1479.9417 | 288.5839 | 326.1801 | 352.8671 | 289.5431
1480.9417 | 289.3371 | 325.5268 | 353.0854 | 290.0974
1481.9417 | 289.6274 | 325.2 | 353.2863 | 290.2553
1482.9417 | 289.1781 | 325.9589 | 354.2182 | 289.9102
1483.9417 | 288.5249 | 326.7929 | 354.1052 | 291.3095
1484.9417 | 288.5038 | 327.4343 | 352.9204 | 291.6962
1485.9417 | 289.7716 | 327.9749 | 353.0554 | 292.9844
1486.9417 | 289.9268 | 328.4204 | 353.5767 | 292.623
1487.9417 | 289.1499 | 328.7863 | 353.6963 | 292.7518
1488.9417 | 289.3131 | 328.7872 | 352.2264 | 292.3732
1489.9417 | 288.142 | 327.4624 | 351.189 | 291.6097
1490.9417 | 288.1922 | 327.3898 | 350.7198 | 291.8371
1491.9417 | 288.6673 | 327.6458 | 351.1406 | 291.7135
1492.9417 | 289.1321 | 328.0468 | 352.3094 | 291.8804
1493.9417 | 289.1891 | 328.072 | 352.0191 | 291.7937
1494.9417 | 288.4856 | 327.2744 | 350.9203 | 291.7137
1495.9417 | 288.5116 | 326.2818 | 351.0179 | 291.9064
1496.9417 | 289.3723 | 327.682 | 352.0891 | 292.899
1497.9417 | 289.8384 | 328.8472 | 352.3139 | 293.5557
1498.9417 | 290.2834 | 329.7277 | 353.1598 | 293.2539
1499.9417 | 289.9433 | 330.0132 | 352.6048 | 293.0983
1500.9417 | 291.0028 | 331.1127 | 353.5515 | 294.5199
1501.9417 | 290.2863 | 332.6393 | 355.0835 | 294.6653
1502.9417 | 289.8202 | 332.6179 | 354.9677 | 293.6871
1503.9417 | 290.8602 | 333.103 | 354.9617 | 293.0299
1504.9417 | 292.1348 | 334.0207 | 357.1651 | 294.3323
1505.9417 | 293.247 | 334.8797 | 359.1519 | 295.1002
1506.9417 | 294.1952 | 336.6412 | 360.8491 | 297.1845
1507.9417 | 295.5462 | 336.2893 | 361.04 | 296.6238
1508.9417 | 296.6749 | 337.0033 | 361.5707 | 296.7947
1509.9417 | 297.4932 | 337.16 | 362.9105 | 296.7065
1510.9417 | 298.8246 | 337.9121 | 363.2792 | 297.3699
1511.9417 | 301.1826 | 338.9375 | 364.8371 | 298.7628
1512.9417 | 302.4776 | 338.8346 | 366.4195 | 300.0994
1513.9417 | 304.3784 | 338.7949 | 367.9635 | 301.2811
1514.9417 | 305.6142 | 339.5175 | 369.429 | 302.0288
1515.9417 | 307.1186 | 340.3154 | 370.3279 | 303.309
1516.9417 | 308.325 | 341.523 | 372.4479 | 304.1663
1517.9417 | 311.0302 | 342.4343 | 375.108 | 307.303
1518.9417 | 311.9936 | 344.4732 | 377.6679 | 310.8738
1519.9417 | 313.9506 | 345.2031 | 379.8592 | 313.1544
1520.9417 | 315.695 | 345.6884 | 382.1192 | 315.7636
1521.9417 | 318.1036 | 345.3053 | 382.863 | 317.6082
1522.9417 | 321.5595 | 344.0759 | 383.2939 | 317.1629
1523.9417 | 322.0683 | 343.1488 | 383.0945 | 317.4852
1524.9417 | 321.6751 | 342.2291 | 383.475 | 318.5868
1525.9417 | 322.45 | 341.1797 | 382.6031 | 318.2134
1526.9417 | 322.8061 | 341.6266 | 381.7686 | 318.5686
1527.9417 | 324.5552 | 342.3049 | 383.8894 | 318.6002
1528.9417 | 326.0464 | 342.3467 | 385.4189 | 319.4944
1529.9417 | 328.0685 | 342.2807 | 387.3424 | 322.8144
1530.9417 | 329.6174 | 341.8722 | 386.834 | 322.4838
1531.9417 | 328.5399 | 340.7525 | 386.1465 | 321.4102
1532.9417 | 329.1567 | 341.338 | 386.458 | 321.5385
1533.9417 | 328.5187 | 341.3524 | 387.2529 | 321.6843
1534.9417 | 328.6531 | 341.5381 | 389.0643 | 321.922
1535.9417 | 328.867 | 341.9176 | 388.5354 | 322.2659
1536.9417 | 330.4422 | 342.7323 | 390.4808 | 322.2043
1537.9417 | 330.8522 | 342.3891 | 391.1125 | 321.6953
1538.9417 | 331.0317 | 342.689 | 391.8747 | 321.636
1539.9417 | 332.1987 | 342.2296 | 391.7879 | 321.6441
1540.9417 | 332.185 | 342.3187 | 392.0703 | 321.8852
1541.9417 | 334.0174 | 343.8453 | 394.7341 | 324.7077
1542.9417 | 335.6103 | 344.5166 | 396.2056 | 325.5508
1543.9417 | 335.6397 | 345.7532 | 397.5862 | 326.0636
1544.9417 | 336.3093 | 347.385 | 400.2699 | 325.3829
1545.9417 | 337.2892 | 349.0003 | 403.6852 | 325.8211
1546.9417 | 337.0843 | 350.2294 | 403.6157 | 324.9225
1547.9417 | 336.4679 | 351.0233 | 404.1923 | 324.7415
1548.9417 | 335.5587 | 351.6926 | 405.1407 | 326.2007
1549.9417 | 334.6491 | 353.4369 | 404.1279 | 324.7683
1550.9417 | 333.5848 | 353.621 | 402.8917 | 323.844
1551.9417 | 332.9453 | 353.1307 | 401.7094 | 323.7491
1552.9417 | 333.3635 | 354.0651 | 401.7344 | 324.182
1553.9417 | 332.6101 | 353.3549 | 402.1645 | 323.1541
1554.9417 | 331.9433 | 353.8871 | 402.2304 | 323.0172
1555.9417 | 330.5781 | 354.411 | 401.8451 | 321.6463
1556.9417 | 330.3131 | 356.0391 | 404.6743 | 321.7493
1557.9417 | 329.0408 | 356.9165 | 405.725 | 322.4301
1558.9417 | 328.7742 | 357.7191 | 404.2264 | 321.312
1559.9417 | 328.8297 | 358.2969 | 402.2178 | 320.0723
1560.9417 | 328.0882 | 359.9901 | 401.2102 | 319.3916
1561.9417 | 327.2759 | 361.4355 | 401.412 | 319.1504
1562.9417 | 326.5799 | 362.9026 | 399.6793 | 318.8316
1563.9417 | 325.8989 | 364.5127 | 399.7497 | 318.3337
1564.9417 | 325.383 | 364.9557 | 399.5855 | 318.9142
1565.9417 | 324.9986 | 365.2665 | 397.7959 | 319.0348
1566.9417 | 325.0239 | 365.9467 | 397.4403 | 318.7265
1567.9417 | 327.5188 | 367.3332 | 398.67 | 320.8452
1568.9417 | 329.0242 | 368.2774 | 399.8063 | 322.6128
1569.9417 | 329.6709 | 368.0749 | 400.8848 | 323.1674
1570.9417 | 332.23 | 367.8604 | 403.1497 | 323.4675
1571.9417 | 333.038 | 370.2239 | 404.7833 | 326.5062
1572.9417 | 334.5535 | 371.9716 | 405.4935 | 328.087
1573.9417 | 334.7684 | 372.956 | 405.2758 | 328.267
1574.9417 | 335.7757 | 374.0583 | 404.6768 | 328.5553
1575.9417 | 337.5585 | 375.9334 | 406.1011 | 329.6423
1576.9417 | 339.4806 | 377.23 | 409.2408 | 332.7507
1577.9417 | 339.6878 | 379.4086 | 411.4642 | 333.6707
1578.9417 | 339.1952 | 380.412 | 411.5152 | 334.2772
1579.9417 | 339.2438 | 380.8539 | 411.1837 | 334.3761
1580.9417 | 339.6757 | 381.176 | 411.2096 | 333.8097
1581.9417 | 339.2838 | 380.8771 | 409.6591 | 333.1286
1582.9417 | 339.5399 | 380.9835 | 409.7611 | 334.0999
1583.9417 | 340.2436 | 382.2607 | 411.1884 | 333.8524
1584.9417 | 340.7769 | 383.2677 | 411.2545 | 333.5512
1585.9417 | 341.0375 | 383.1992 | 411.8725 | 333.2084
1586.9417 | 341.9336 | 384.5698 | 413.0621 | 334.0425
1587.9417 | 342.4347 | 385.4177 | 414.1994 | 336.2257
1588.9417 | 343.3814 | 384.9085 | 413.79 | 335.6605
1589.9417 | 343.1496 | 384.7487 | 412.3489 | 334.7472
1590.9417 | 342.9622 | 384.5605 | 411.7216 | 335.6124
1591.9417 | 343.4499 | 383.9261 | 411.4312 | 336.7528
1592.9417 | 342.3592 | 383.4565 | 410.9726 | 335.9327
1593.9417 | 342.0854 | 383.1228 | 411.1078 | 335.5215
1594.9417 | 341.5536 | 382.8483 | 410.7248 | 335.2231
1595.9417 | 341.7156 | 382.6243 | 410.8389 | 335.2308
1596.9417 | 342.8358 | 382.7704 | 410.6238 | 335.3404
1597.9417 | 342.6606 | 381.5081 | 408.5805 | 334.5826
1598.9417 | 343.5142 | 380.4793 | 406.9974 | 333.8966
1599.9573 | 344.7905 | 380.5435 | 409.37 | 333.4748
1600.9417 | 344.6722 | 380.3844 | 408.919 | 333.421
1601.9417 | 344.6188 | 380.2932 | 410.802 | 333.1708
1602.9417 | 345.3946 | 380.6382 | 410.8178 | 332.8432
1603.9417 | 345.5655 | 381.1225 | 410.541 | 333.6525
1604.9417 | 344.9113 | 380.7138 | 409.7971 | 332.5124
1605.9417 | 344.3119 | 381.2802 | 410.2727 | 331.992
1606.9417 | 346.1897 | 381.777 | 411.2288 | 331.807
1607.9417 | 346.0033 | 381.1183 | 412.0151 | 332.1294
1608.9417 | 345.6863 | 380.3999 | 411.5643 | 331.025
1609.9417 | 345.1481 | 381.3191 | 413.0109 | 332.8579
1610.9417 | 344.7829 | 382.3518 | 413.0442 | 332.9742
1611.9417 | 345.5289 | 383.3149 | 412.4986 | 333.0207
1612.9417 | 344.9276 | 383.6155 | 411.492 | 331.7234
1613.9417 | 344.0802 | 383.7498 | 409.8439 | 330.7142
1614.9417 | 343.823 | 384.9806 | 408.9741 | 329.8555
1615.9417 | 343.0865 | 385.7699 | 408.3734 | 329.6967
1616.9417 | 343.5371 | 386.141 | 408.3845 | 330.7606
1617.9417 | 344.6657 | 387.6186 | 409.4649 | 332.6896
1618.9573 | 344.5322 | 388.1413 | 410.7136 | 334.0553
1619.9417 | 343.7747 | 388.4912 | 409.8355 | 333.9811
1620.9417 | 345.5026 | 389.3982 | 409.7884 | 332.9908
1621.9417 | 347.3426 | 389.3266 | 410.2761 | 331.7875
1622.9417 | 349.5245 | 389.6126 | 411.6545 | 331.6992
1623.9573 | 348.7167 | 389.4454 | 411.6901 | 331.3532
1624.9417 | 348.8056 | 388.4962 | 410.6917 | 331.5146
1625.9417 | 348.8637 | 389.8457 | 412.7315 | 333.0583
1626.9573 | 349.2818 | 391.1129 | 416.1872 | 334.9832
1627.9417 | 348.952 | 392.0681 | 416.5406 | 335.3184
1628.9417 | 349.5555 | 391.4209 | 416.0931 | 334.6674
1629.9573 | 350.2472 | 390.4135 | 414.404 | 334.8249
1630.9417 | 353.0252 | 390.6259 | 415.7334 | 336.7752
1631.9417 | 354.2342 | 390.9616 | 416.0516 | 337.3487
1632.9417 | 354.4547 | 391.1955 | 416.8189 | 337.9678
1633.9573 | 354.6888 | 391.7286 | 416.4971 | 337.6495
1634.9417 | 354.2006 | 391.9094 | 415.8362 | 337.6088
1635.9417 | 354.3373 | 392.1732 | 415.4717 | 336.7674
1636.9417 | 356.6734 | 391.8457 | 415.8842 | 336.5484
1637.9417 | 356.4532 | 390.5894 | 415.7887 | 336.0543
1638.9573 | 355.5461 | 389.5473 | 414.0819 | 336.1656
1639.9417 | 355.315 | 388.0774 | 411.7813 | 335.5348
1640.9417 | 354.9892 | 387.2901 | 410.8375 | 334.9602
1641.9417 | 355.1448 | 386.9064 | 410.1412 | 334.279
1642.9417 | 355.5961 | 386.9179 | 410.3554 | 333.6793
1643.9417 | 356.7465 | 387.0128 | 412.725 | 333.5982
1644.9417 | 359.08 | 387.0785 | 416.7648 | 333.4764
1645.9417 | 360.931 | 386.6073 | 417.3468 | 333.7606
1646.9417 | 361.0028 | 386.8866 | 418.9422 | 333.6087
1647.9417 | 361.4868 | 387.0613 | 420.2001 | 334.2976
1648.9417 | 361.3687 | 387.1283 | 418.7997 | 333.9236
1649.9417 | 360.1492 | 386.7241 | 417.4416 | 333.382
1650.9417 | 359.9765 | 386.4407 | 417.068 | 334.2703
1651.9417 | 360.2682 | 386.811 | 418.1364 | 333.9832
1652.9417 | 360.5404 | 387.6775 | 416.0441 | 332.6956
1653.9417 | 359.4032 | 388.2385 | 415.965 | 333.7308
1654.9417 | 359.8342 | 389.7833 | 417.6664 | 334.1754
1655.9417 | 361.2773 | 391.3256 | 419.6757 | 337.2863
1656.9417 | 362.7802 | 392.2027 | 421.4354 | 338.4911
1657.9417 | 364.0527 | 393.3008 | 420.9879 | 338.527
1658.9417 | 364.2379 | 393.6872 | 418.8736 | 337.5411
1659.9417 | 364.0685 | 394.8392 | 419.7524 | 337.7676
1660.9417 | 364.1769 | 396.5421 | 421.0836 | 337.7492
1661.9417 | 363.5788 | 397.9922 | 422.1971 | 338.1297
1662.9417 | 364.4179 | 398.1947 | 424.0328 | 339.8968
1663.9417 | 366.6079 | 398.8293 | 424.5694 | 341.3888
1664.9417 | 368.7017 | 398.3443 | 426.9744 | 341.7074
1665.9417 | 368.6569 | 397.6716 | 425.4545 | 340.8547
1666.9417 | 368.1114 | 397.654 | 425.1315 | 340.2063
1667.9417 | 368.575 | 398.2572 | 425.216 | 339.7588
1668.9417 | 368.4179 | 397.5956 | 426.6496 | 339.5155
1669.9417 | 367.3564 | 398.6137 | 426.8899 | 340.2488
1670.9417 | 367.8286 | 399.8383 | 427.736 | 340.1456
1671.9417 | 367.0922 | 399.5798 | 426.4273 | 339.7242
1672.9417 | 367.8075 | 399.4678 | 426.2303 | 339.5992
1673.9417 | 369.4788 | 400.6698 | 427.1088 | 339.1824
1674.9417 | 369.5234 | 401.0378 | 428.0848 | 339.1168
1675.9417 | 369.2531 | 400.7676 | 428.4149 | 338.8518
1676.9417 | 370.4121 | 400.5418 | 428.6113 | 339.7582
1677.9417 | 369.3168 | 399.8849 | 427.4183 | 339.1783
1678.9417 | 368.4521 | 400.7038 | 427.3059 | 339.8605
1679.9417 | 367.7077 | 402.1463 | 427.4206 | 342.2901
1680.9417 | 367.2685 | 402.2993 | 427.375 | 343.0018
1681.9417 | 367.3529 | 403.5911 | 428.4477 | 343.1906
1682.9417 | 367.6897 | 403.0242 | 428.0609 | 343.0413
1683.9417 | 369.4262 | 403.6881 | 429.4789 | 343.7153
1684.9417 | 370.2649 | 403.0602 | 429.5384 | 342.5942
1685.9417 | 370.4477 | 402.3825 | 428.9781 | 342.0184
1686.9417 | 370.3474 | 402.0093 | 429.0969 | 342.5261
1687.9417 | 369.4619 | 402.3697 | 429.7079 | 344.55
1688.9417 | 370.7072 | 402.9002 | 429.9703 | 343.7356
1689.9417 | 370.7101 | 404.3406 | 432.6577 | 343.9578
1690.9417 | 371.3792 | 405.7602 | 434.171 | 345.6522
1691.9417 | 371.1367 | 406.737 | 434.1221 | 345.8483
1692.9417 | 371.9913 | 406.7674 | 433.9302 | 347.7012
1693.9417 | 371.2918 | 406.4852 | 433.427 | 348.9763
1694.9417 | 372.6077 | 407.0356 | 434.0745 | 349.2627
1695.9417 | 373.6104 | 407.2025 | 434.3825 | 350.7467
1696.9417 | 373.6695 | 408.5101 | 436.0134 | 351.1112
1697.9417 | 374.6337 | 408.8115 | 436.5698 | 352.6415
1698.9417 | 377.3428 | 409.2352 | 437.5696 | 352.8438
1699.9417 | 378.8198 | 409.9669 | 440.7262 | 352.9653
1700.9417 | 379.461 | 408.5345 | 439.2925 | 351.9477
1701.9417 | 381.1002 | 408.8791 | 442.1184 | 351.2122
1702.9417 | 382.6585 | 408.5847 | 442.3447 | 350.3787
1703.9417 | 383.633 | 409.0212 | 443.0199 | 350.2264
1704.9417 | 385.3819 | 408.1591 | 442.8775 | 350.0335
1705.9417 | 384.5472 | 409.2008 | 446.8461 | 351.9905
1706.9417 | 384.5243 | 410.3122 | 447.1028 | 352.7861
1707.9417 | 383.518 | 410.6089 | 446.7437 | 352.1845
1708.9417 | 382.9541 | 410.8975 | 444.3539 | 351.0654
1709.9417 | 382.3439 | 411.0229 | 442.8543 | 350.6939
1710.9417 | 382.2979 | 412.1791 | 444.053 | 352.0932
1711.9417 | 382.452 | 413.5684 | 445.852 | 351.9362
1712.9417 | 382.1512 | 413.5145 | 446.3322 | 353.8474
1713.9417 | 381.0109 | 413.1726 | 446.7311 | 355.2957
1714.9417 | 378.9294 | 414.0301 | 446.5635 | 356.4687
1715.9417 | 379.6528 | 414.6342 | 445.0847 | 356.5897
1716.9417 | 379.8186 | 414.3635 | 444.5197 | 358.035
1717.9417 | 378.8104 | 412.853 | 444.3367 | 357.9026
1718.9417 | 378.3075 | 412.7747 | 443.2931 | 357.4167
1719.9417 | 377.7975 | 412.4103 | 443.2708 | 357.0428
1720.9417 | 378.7728 | 412.8093 | 443.0146 | 356.6659
1721.9417 | 380.1967 | 412.8584 | 443.1028 | 356.2197
1722.9417 | 379.7998 | 412.7561 | 442.5813 | 355.3738
1723.9417 | 379.4481 | 411.6043 | 441.3355 | 354.8157
1724.9417 | 379.7147 | 411.7357 | 442.1831 | 355.2158
1725.9417 | 379.4986 | 412.3898 | 441.9201 | 354.6599
1726.9417 | 378.3687 | 411.5803 | 440.5704 | 353.3798
1727.9417 | 380.1008 | 410.836 | 440.548 | 353.5857
1728.9417 | 379.5005 | 410.392 | 440.724 | 353.4074
1729.9417 | 379.4219 | 410.3264 | 439.4961 | 352.9946
1730.9417 | 379.7587 | 409.3905 | 438.8886 | 355.3985
1731.9417 | 380.6897 | 408.8045 | 439.1478 | 355.4711
1732.9417 | 381.3858 | 408.8433 | 440.7985 | 355.1366
1733.9417 | 381.9818 | 409.434 | 440.7846 | 355.0263
1734.9417 | 384.1845 | 408.9587 | 440.3777 | 354.3781
1735.9417 | 384.7248 | 407.8519 | 439.4478 | 353.7902
1736.9417 | 384.4522 | 407.5596 | 440.4512 | 354.6567
1737.9417 | 385.4456 | 407.9055 | 441.799 | 357.3216
1738.9417 | 387.2918 | 407.4448 | 440.7539 | 358.0117
1739.9417 | 387.7454 | 406.4265 | 439.8025 | 357.1658
1740.9417 | 387.5577 | 406.3327 | 439.9236 | 356.6057
1741.9417 | 387.935 | 407.1079 | 440.4966 | 357.5808
1742.9417 | 386.9712 | 408.1552 | 442.2284 | 358.6332
1743.9417 | 386.8725 | 408.7547 | 444.7471 | 358.9421
1744.9417 | 386.3335 | 409.1282 | 444.6815 | 360.8767
1745.9417 | 387.0301 | 409.7069 | 445.7213 | 360.043
1746.9417 | 388.4016 | 410.0883 | 445.28 | 359.4839
1747.9417 | 387.4979 | 409.6998 | 444.0915 | 358.7843
1748.9417 | 386.3302 | 409.9965 | 444.3705 | 359.261
1749.9417 | 386.1321 | 410.1363 | 444.0356 | 358.9801
1750.9417 | 386.0572 | 410.2598 | 446.2935 | 360.398
1751.9417 | 389.6104 | 412.3658 | 449.1376 | 360.4204
1752.9417 | 390.7688 | 414.804 | 452.0674 | 360.2353
1753.9417 | 390.5055 | 416.6242 | 453.9329 | 360.8636
1754.9417 | 391.8981 | 417.1219 | 453.5869 | 360.1794
1755.9417 | 394.3438 | 419.6514 | 457.1871 | 360.5948
1756.9417 | 394.6856 | 421.7747 | 459.8401 | 360.9791
1757.9417 | 394.2139 | 423.2224 | 463.1896 | 360.6883
1758.9417 | 393.8513 | 424.5607 | 463.2059 | 360.0112
1759.9417 | 392.7616 | 426.2799 | 461.2028 | 359.4246
1760.9417 | 391.2329 | 426.8251 | 459.184 | 359.8958
1761.9417 | 391.6321 | 428.6843 | 460.0653 | 362.9942
1762.9417 | 390.657 | 429.0408 | 460.4113 | 364.4917
1763.9417 | 390.881 | 429.9774 | 459.0439 | 363.2498
1764.9417 | 391.4028 | 429.7876 | 460.5511 | 364.2277
1765.9417 | 391.0574 | 429.2941 | 461.172 | 363.5953
1766.9417 | 390.9518 | 429.4979 | 461.6034 | 363.5501
1767.9417 | 392.7306 | 429.8843 | 462.2052 | 362.749
1768.9417 | 393.3308 | 431.2846 | 462.8759 | 362.4628
1769.9417 | 393.371 | 431.094 | 462.1588 | 362.2217
1770.9417 | 393.291 | 431.7544 | 462.5369 | 364.1638
1771.9417 | 393.6669 | 432.5659 | 463.0585 | 363.4808
1772.9573 | 394.3591 | 433.614 | 463.924 | 363.1723
1773.9417 | 394.3762 | 433.3644 | 463.2099 | 362.9108
1774.9417 | 394.8732 | 432.9609 | 463.8042 | 362.438
1775.9417 | 396.1452 | 432.0571 | 461.8865 | 362.7799
1776.9417 | 397.2645 | 431.6152 | 459.7698 | 362.6467
1777.9417 | 396.9186 | 431.2628 | 458.5135 | 362.6462
1778.9417 | 396.5593 | 429.9924 | 458.0104 | 362.8601
1779.9417 | 396.8833 | 429.4335 | 458.6869 | 362.7615
1780.9417 | 398.8592 | 428.8021 | 458.3131 | 362.1547
1781.9417 | 398.1085 | 428.1375 | 457.8175 | 362.7639
1782.9417 | 397.2686 | 427.7909 | 456.0965 | 362.8074
1783.9417 | 397.3572 | 426.8117 | 455.1063 | 362.7472
1784.9417 | 396.4693 | 426.6072 | 454.0813 | 361.6505
1785.9417 | 396.3187 | 428.1326 | 454.1202 | 362.0961
1786.9417 | 397.0823 | 429.3924 | 454.666 | 361.7714
1787.9417 | 398.4679 | 429.5842 | 454.7255 | 363.5476
1788.9417 | 399.2608 | 429.1938 | 453.4332 | 363.2043
1789.9417 | 399.7505 | 429.339 | 453.3727 | 361.9693
1790.9417 | 399.9374 | 428.5467 | 454.0645 | 361.8346
1791.9417 | 399.5546 | 428.0526 | 452.9045 | 361.4941
1792.9417 | 398.9087 | 427.8454 | 453.5833 | 360.969
1793.9417 | 397.6668 | 427.4685 | 451.499 | 360.067
1794.9417 | 396.2782 | 427.3832 | 450.2591 | 359.1647
1795.9417 | 396.1341 | 427.8558 | 450.9163 | 359.2923
1796.9417 | 395.111 | 428.2669 | 451.463 | 358.7237
1797.9417 | 395.4619 | 428.8687 | 454.2027 | 359.4496
1798.9417 | 395.852 | 430.3325 | 456.7237 | 359.4419
1799.9417 | 396.849 | 432.0706 | 458.1349 | 359.4641
1800.9417 | 398.089 | 433.2121 | 460.8356 | 360.7219
1801.9417 | 398.0176 | 434.8404 | 462.7526 | 361.0057
1802.9417 | 397.4537 | 435.4703 | 462.2629 | 361.8838
1803.9417 | 397.2019 | 435.4287 | 461.8157 | 361.8942
1804.9417 | 397.0357 | 436.1364 | 461.6455 | 363.6311
1805.9417 | 397.5577 | 436.6053 | 461.562 | 364.7624
1806.9417 | 398.5261 | 435.7915 | 460.0892 | 365.7671
1807.9417 | 398.2564 | 434.5017 | 458.7178 | 365.2389
1808.9417 | 398.0011 | 434.4619 | 457.8984 | 364.7152
1809.9417 | 398.3449 | 435.279 | 457.9533 | 364.7019
1810.9417 | 398.2064 | 435.8161 | 456.9042 | 363.5369
1811.9417 | 399.6342 | 434.6521 | 454.4361 | 363.1938
1812.9417 | 398.9796 | 434.6302 | 454.2308 | 362.8893
1813.9417 | 397.6952 | 434.1292 | 452.103 | 362.1764
1814.9417 | 397.8209 | 433.9392 | 450.5 | 361.8706
1815.9417 | 398.8229 | 434.7763 | 449.463 | 361.2968
1816.9417 | 397.7227 | 434.0965 | 448.0186 | 360.2269
1817.9417 | 398.0913 | 433.6048 | 446.1725 | 359.1461
1818.9417 | 398.9109 | 434.0812 | 446.0137 | 359.6568
1819.9417 | 399.2262 | 433.1401 | 444.3957 | 358.6795
1820.9417 | 400.3028 | 433.8435 | 444.755 | 358.5144
1821.9417 | 401.3071 | 433.4517 | 444.7072 | 358.2682
1822.9417 | 403.3628 | 434.0228 | 445.7153 | 358.2552
1823.9417 | 404.8222 | 433.7911 | 446.4392 | 358.0217
1824.9417 | 405.5025 | 432.8833 | 447.0936 | 358.1986
1825.9417 | 407.3684 | 432.9394 | 448.5377 | 358.2807
1826.9417 | 409.3323 | 433.3717 | 450.4993 | 358.5019
1827.9417 | 408.8196 | 433.2125 | 451.1523 | 358.6506
1828.9417 | 410.2038 | 432.566 | 452.1892 | 359.2212
1829.9417 | 410.8069 | 432.3795 | 453.539 | 358.7776
1830.9417 | 410.4777 | 431.8276 | 452.1776 | 358.4288
1831.9417 | 410.181 | 431.2641 | 451.1376 | 358.3518
1832.9417 | 410.7986 | 430.3204 | 451.3061 | 358.419
1833.9417 | 410.423 | 429.3433 | 451.0626 | 358.5953
1834.9417 | 410.3391 | 429.9339 | 451.6585 | 359.3925
1835.9417 | 410.4696 | 432.5136 | 453.6516 | 360.0598
1836.9417 | 412.5247 | 433.9389 | 456.5903 | 363.3467
1837.9417 | 414.1937 | 433.2984 | 458.0485 | 365.2825
1838.9417 | 415.6267 | 433.5983 | 459.8869 | 365.9708
1839.9417 | 416.8971 | 434.9591 | 461.0507 | 367.242
1840.9417 | 418.0489 | 434.3344 | 463.0025 | 367.4733
1841.9417 | 419.9834 | 434.1331 | 464.3851 | 368.5311
1842.9417 | 419.9001 | 433.6853 | 464.3782 | 369.2673
1843.9417 | 419.7071 | 434.6186 | 464.5964 | 370.7303
1844.9417 | 419.1852 | 435.3946 | 464.3049 | 371.4377
1845.9417 | 417.5698 | 435.4584 | 461.7934 | 370.0725
1846.9417 | 415.7026 | 435.6135 | 459.1278 | 368.85
1847.9417 | 417.1169 | 436.1261 | 457.9942 | 368.1238
1848.9417 | 418.0697 | 437.0841 | 459.179 | 368.0408
1849.9417 | 420.7595 | 436.0896 | 459.156 | 367.8867
1850.9417 | 421.1944 | 435.3538 | 458.7578 | 367.8527
1851.9417 | 421.2724 | 435.4384 | 459.9027 | 368.5046
1852.9417 | 421.9984 | 436.6827 | 460.418 | 369.2365
1853.9417 | 419.8783 | 436.5507 | 458.8862 | 369.1567
1854.9417 | 420.5919 | 435.0515 | 457.9866 | 368.9708
1855.9417 | 421.1992 | 434.6762 | 457.6281 | 368.9529
1856.9417 | 420.2335 | 435.1042 | 457.5792 | 368.7789
1857.9417 | 420.5332 | 435.3753 | 458.5256 | 368.4817
1858.9417 | 419.2357 | 436.0536 | 457.9689 | 367.5403
1859.9417 | 419.3294 | 436.0881 | 457.1242 | 367.2791
1860.9417 | 419.0305 | 435.4524 | 458.0995 | 366.7737
1861.9417 | 419.4583 | 435.3215 | 457.9589 | 366.703
1862.9417 | 417.1059 | 434.6355 | 457.0336 | 367.0335
1863.9417 | 415.3425 | 434.1629 | 457.113 | 368.3265
1864.9417 | 414.585 | 433.8694 | 456.9248 | 369.2524
1865.9417 | 413.1363 | 433.4977 | 456.4273 | 369.2109
1866.9417 | 411.9503 | 433.6817 | 453.6389 | 368.7447
1867.9417 | 412.7212 | 432.9384 | 452.863 | 368.1026
1868.9417 | 411.229 | 432.924 | 451.8734 | 368.3895
1869.9417 | 411.6693 | 433.6101 | 453.0483 | 367.8127
1870.9417 | 412.3046 | 434.841 | 453.3714 | 367.1415
1871.9417 | 413.3705 | 435.1304 | 452.9001 | 366.2327
1872.9417 | 412.6381 | 436.0314 | 453.4572 | 366.6417
1873.9417 | 413.5758 | 435.6578 | 453.3639 | 366.4963
1874.9417 | 413.0614 | 437.2662 | 451.825 | 366.6004
1875.9417 | 413.0173 | 436.3294 | 450.1486 | 365.6843
1876.9417 | 411.1958 | 436.6755 | 449.4662 | 365.3949
1877.9417 | 412.0838 | 436.0779 | 448.6883 | 366.2835
1878.9417 | 412.7208 | 437.0661 | 449.0564 | 365.6252
1879.9417 | 413.4362 | 437.1384 | 449.1994 | 365.1045
1880.9417 | 413.5653 | 437.1923 | 448.8567 | 364.9889
1881.9417 | 414.2829 | 436.6962 | 449.5341 | 364.9979
1882.9417 | 414.0323 | 434.9837 | 448.6538 | 365.0438
1883.9417 | 414.0031 | 434.8059 | 450.0996 | 367.0312
1884.9417 | 414.607 | 435.173 | 451.0579 | 367.752
1885.9417 | 414.3947 | 435.5721 | 450.2908 | 367.6879
1886.9417 | 415.3593 | 435.95 | 452.1189 | 368.4002
1887.9417 | 416.5793 | 436.2635 | 452.1663 | 370.2312
1888.9417 | 418.2602 | 436.5066 | 453.4581 | 369.7421
1889.9417 | 419.2224 | 436.2715 | 453.582 | 370.7443
1890.9417 | 419.6535 | 435.1396 | 453.5643 | 370.6173
1891.9417 | 418.7865 | 435.4289 | 453.0531 | 370.8641
1892.9417 | 418.6867 | 434.9257 | 453.3644 | 370.8069
1893.9417 | 416.6617 | 434.3303 | 452.9999 | 371.1743
1894.9417 | 416.1178 | 435.0938 | 452.2872 | 371.8474
1895.9417 | 414.2961 | 434.8428 | 452.2997 | 371.0667
1896.9417 | 414.1187 | 435.192 | 453.8279 | 371.5037
1897.9417 | 414.1576 | 434.7862 | 454.332 | 371.2408
1898.9417 | 414.4125 | 435.5029 | 453.6688 | 371.3504
1899.9417 | 415.8839 | 436.9547 | 455.2182 | 374.1341
1900.9417 | 416.5632 | 437.5719 | 456.7529 | 373.9045
1901.9417 | 415.271 | 436.8911 | 455.8529 | 372.7232
1902.9417 | 414.6398 | 437.0758 | 456.4392 | 372.604
1903.9417 | 415.7411 | 438.779 | 458.2721 | 373.8274
1904.9417 | 415.652 | 438.867 | 458.246 | 373.3882
1905.9417 | 416.9542 | 438.4899 | 458.7561 | 372.9919
1906.9417 | 417.2078 | 437.4781 | 459.097 | 373.5408
1907.9417 | 416.9998 | 437.504 | 461.2635 | 374.1789
1908.9573 | 416.8566 | 438.0952 | 461.3295 | 373.9666
1909.9417 | 415.3822 | 438.3103 | 461.0492 | 373.9931
1910.9417 | 415.0136 | 438.2101 | 461.5805 | 373.8246
1911.9417 | 414.9425 | 438.5718 | 460.8703 | 374.1147
1912.9417 | 413.6379 | 439.3821 | 460.0259 | 373.2617
1913.9417 | 415.0306 | 440.1224 | 459.804 | 372.9044
1914.9417 | 415.4692 | 439.7765 | 460.4537 | 372.393
1915.9417 | 415.6621 | 440.6236 | 460.5801 | 373.0866
1916.9417 | 416.072 | 441.5991 | 461.915 | 373.0919
1917.9417 | 414.7033 | 442.17 | 461.8592 | 372.8236
1918.9417 | 413.4225 | 441.8177 | 460.8686 | 372.462
1919.9417 | 413.141 | 442.0935 | 460.2519 | 372.5753
1920.9417 | 413.3837 | 441.7127 | 458.8188 | 371.7143
1921.9417 | 413.7852 | 441.2388 | 457.9357 | 371.2029
1922.9417 | 413.8782 | 441.2812 | 458.2524 | 371.0161
1923.9573 | 413.6876 | 442.4904 | 459.7843 | 371.4047
1924.9417 | 413.1345 | 442.4131 | 459.1577 | 371.2417
1925.9417 | 413.1073 | 441.0632 | 457.314 | 370.4691
1926.9417 | 412.8221 | 441.0859 | 456.5652 | 370.1422
1927.9417 | 411.5278 | 441.5835 | 455.5862 | 370.7719
1928.9417 | 410.5819 | 441.4419 | 455.6804 | 371.1604
1929.9573 | 410.1892 | 441.7475 | 456.282 | 372.5701
1930.9417 | 409.8774 | 443.4164 | 457.4465 | 372.2617
1931.9573 | 410.534 | 443.516 | 457.4935 | 372.0945
1932.9417 | 409.3652 | 443.2605 | 457.1024 | 371.987
1933.9573 | 411.1412 | 443.906 | 457.3126 | 371.7829
1934.9417 | 411.9206 | 443.7104 | 455.7499 | 372.0128
1935.9417 | 412.3575 | 443.3595 | 454.902 | 370.884
1936.9417 | 412.4551 | 444.0166 | 454.4728 | 370.9952
1937.9417 | 413.5749 | 445.0266 | 452.9862 | 370.4236
1938.9417 | 413.4345 | 444.9049 | 452.4485 | 369.1346
1939.9417 | 414.5754 | 445.9532 | 451.5675 | 368.8927
1940.9417 | 413.5496 | 445.3821 | 450.2178 | 368.1209
1941.9417 | 414.1578 | 444.641 | 449.3929 | 368.2425
1942.9417 | 414.713 | 443.7991 | 449.6416 | 367.8315
1943.9417 | 414.8473 | 444.7398 | 450.5325 | 367.5836
1944.9417 | 415.8356 | 444.1307 | 449.072 | 366.8513
1945.9417 | 417.8126 | 443.5959 | 449.1315 | 366.5396
1946.9417 | 419.8626 | 443.005 | 449.9176 | 367.5141
1947.9417 | 420.28 | 442.5577 | 450.5622 | 367.7817
1948.9417 | 420.5957 | 442.4422 | 450.9554 | 368.3438
1949.9417 | 420.0435 | 442.154 | 452.0603 | 368.6289
1950.9417 | 421.3985 | 441.8894 | 453.7363 | 368.5804
1951.9417 | 421.8907 | 441.2606 | 454.0209 | 368.4726
1952.9417 | 421.4755 | 440.8446 | 454.2842 | 368.6883
1953.9417 | 422.7458 | 440.7013 | 455.8176 | 369.9255
1954.9417 | 425.2389 | 440.0738 | 457.2882 | 370.192
1955.9417 | 427.2472 | 440.8564 | 457.1113 | 370.6546
1956.9417 | 426.8146 | 441.2662 | 457.2844 | 370.9687
1957.9417 | 425.5023 | 440.6023 | 458.2458 | 370.7498
1958.9417 | 423.4144 | 440.6625 | 456.3681 | 370.7183
1959.9417 | 424.5711 | 443.7127 | 456.2616 | 371.2175
1960.9417 | 424.7993 | 446.8852 | 457.4345 | 371.7594
1961.9417 | 424.4937 | 447.6417 | 457.1489 | 372.3538
1962.9417 | 425.7318 | 446.7311 | 457.311 | 372.5418
1963.9417 | 429.6832 | 446.7941 | 459.0382 | 373.5102
1964.9417 | 431.8663 | 445.1107 | 459.2534 | 373.8789
1965.9417 | 430.7521 | 443.7294 | 460.3801 | 374.2182
1966.9417 | 429.446 | 443.4014 | 459.8878 | 374.8656
1967.9417 | 428.7459 | 443.2046 | 461.4771 | 375.7352
1968.9573 | 428.5678 | 444.4178 | 463.0715 | 375.7282
1969.9417 | 427.0183 | 444.4854 | 463.1891 | 376.2704
1970.9417 | 426.1394 | 444.6253 | 464.3665 | 376.9497
1971.9417 | 425.1668 | 445.4826 | 465.7857 | 378.3571
1972.9417 | 424.1912 | 446.4746 | 466.0331 | 379.4203
1973.9417 | 422.9713 | 447.2209 | 465.7017 | 379.2797
1974.9417 | 422.0246 | 447.6658 | 465.1312 | 379.7717
1975.9417 | 420.9678 | 446.9703 | 465.9492 | 380.3603
1976.9417 | 420.5722 | 446.1591 | 465.2316 | 381.772
1977.9417 | 420.3329 | 444.8205 | 465.4864 | 381.9992
1978.9417 | 418.842 | 444.7158 | 464.5631 | 381.4079
1979.9417 | 417.5566 | 443.7297 | 463.0656 | 380.725
1980.9417 | 418.0645 | 443.6604 | 463.3729 | 381.8453
1981.9417 | 418.0068 | 443.3281 | 462.4262 | 381.9613
1982.9417 | 417.8516 | 443.1321 | 463.1097 | 381.6361
1983.9417 | 417.7606 | 443.1298 | 464.6901 | 381.4649
1984.9417 | 416.8388 | 442.3249 | 463.0132 | 381.5679
1985.9417 | 416.2008 | 442.7495 | 462.4027 | 381.6036
1986.9417 | 415.0682 | 442.9805 | 462.1202 | 382.0898
1987.9417 | 413.6695 | 443.4934 | 461.5847 | 381.3118
1988.9417 | 414.4758 | 443.2162 | 461.3921 | 380.9853
1989.9417 | 412.925 | 442.6715 | 460.2991 | 380.7078
1990.9417 | 412.7679 | 442.1717 | 458.2727 | 379.8955
1991.9417 | 413.7279 | 443.3449 | 458.7738 | 380.8711
1992.9417 | 414.1341 | 444.055 | 457.1925 | 380.4656
1993.9573 | 413.7083 | 444.3915 | 458.3354 | 379.7807
1994.9417 | 413.4973 | 445.5069 | 458.0824 | 378.8341
1995.9417 | 414.1831 | 445.5402 | 456.5541 | 378.8542
1996.9417 | 411.9867 | 445.4349 | 455.3233 | 377.8909
1997.9417 | 410.9694 | 445.3207 | 454.9061 | 377.7102
1998.9417 | 411.6783 | 445.0298 | 455.798 | 378.7767
1999.9417 | 411.3145 | 444.4317 | 455.7119 | 378.5627
2000.9417 | 411.9008 | 444.2296 | 455.9191 | 379.6276
2001.9417 | 412.4926 | 444.2629 | 456.0713 | 379.7463
2002.9417 | 411.3687 | 443.7913 | 454.5587 | 378.7534
2003.9417 | 410.9166 | 444.4479 | 453.3083 | 379.5509
2004.9417 | 409.696 | 444.9021 | 452.6329 | 378.8555
2005.9417 | 410.4778 | 445.1023 | 452.875 | 378.6773
2006.9417 | 411.4713 | 445.3476 | 452.6875 | 378.3148
2007.9417 | 410.1978 | 445.135 | 452.9788 | 378.4752
2008.9417 | 410.186 | 445.1334 | 454.2357 | 380.0714
2009.9417 | 409.4911 | 445.8683 | 453.8518 | 379.7922
2010.9417 | 409.0394 | 445.6602 | 452.0395 | 378.8466
2011.9417 | 408.9759 | 445.9777 | 451.6168 | 379.1126
2012.9417 | 409.6277 | 446.7617 | 452.1715 | 378.6582
2013.9417 | 409.8975 | 446.5843 | 452.8245 | 377.5841
2014.9417 | 410.9424 | 446.2423 | 454.3079 | 377.2238
2015.9417 | 410.3739 | 445.5001 | 453.1628 | 376.5262
2016.9417 | 410.4723 | 444.7573 | 452.9233 | 376.7703
2017.9417 | 409.6818 | 445.5094 | 451.6569 | 376.2002
2018.9417 | 407.5269 | 445.3092 | 449.9036 | 374.944
2019.9417 | 405.9589 | 445.8377 | 450.4359 | 374.8003
2020.9417 | 404.3545 | 446.1748 | 451.4232 | 375.8339
2021.9417 | 403.3474 | 446.5581 | 451.4781 | 376.4311
2022.9417 | 404.3885 | 446.2915 | 450.1203 | 375.2745
2023.9417 | 404.9045 | 446.6328 | 448.5899 | 374.8923
2024.9417 | 404.4415 | 446.6401 | 447.3679 | 374.425
2025.9417 | 402.5145 | 445.7251 | 446.0294 | 373.8718
2026.9417 | 401.2388 | 445.5461 | 444.5556 | 373.5203
2027.9417 | 400.8272 | 446.4707 | 444.1194 | 373.3921
2028.9417 | 400.7753 | 447.3213 | 444.3398 | 373.092
2029.9417 | 401.4662 | 447.966 | 444.9017 | 372.88
2030.9417 | 404.0344 | 448.6638 | 445.3887 | 372.9484
2031.9417 | 405.8634 | 448.8886 | 446.5438 | 373.3916
2032.9417 | 407.35 | 448.7308 | 446.8064 | 373.2445
2033.9417 | 407.4962 | 448.315 | 451.2433 | 372.7914
2034.9417 | 405.9095 | 447.549 | 461.8138 | 372.3228
2035.9417 | 405.6802 | 447.9837 | 459.9727 | 372.5683
2036.9417 | 405.6842 | 449.0651 | 459.6348 | 372.4344
2037.9417 | 407.2082 | 449.7903 | 458.8266 | 372.1424
2038.9417 | 408.6233 | 449.609 | 458.8742 | 372.3355
2039.9417 | 409.602 | 451.6784 | 458.5107 | 372.1827
2040.9417 | 409.7422 | 451.93 | 458.5392 | 371.952
2041.9417 | 409.1266 | 452.1751 | 457.6087 | 372.5393
2042.9417 | 409.3187 | 452.6201 | 457.1775 | 372.4459
2043.9417 | 410.3612 | 452.1994 | 455.649 | 371.8444
2044.9417 | 411.4906 | 451.3493 | 455.9807 | 371.9493
2045.9417 | 411.1983 | 450.6931 | 457.2944 | 371.98
2046.9417 | 412.482 | 450.6883 | 458.0506 | 372.8321
2047.9417 | 412.5852 | 450.5249 | 458.6734 | 373.2198
2048.9417 | 413.1174 | 449.624 | 457.0272 | 372.7194
2049.9417 | 412.7059 | 448.8622 | 455.1838 | 373.096
2050.9417 | 413.0275 | 448.8256 | 453.9664 | 374.4521
2051.9417 | 414.4324 | 448.9796 | 456.0766 | 375.53
2052.9417 | 412.8898 | 447.8188 | 454.6766 | 375.1927
2053.9417 | 412.2788 | 447.8888 | 455.5949 | 374.8233
2054.9417 | 411.9725 | 448.9669 | 453.7047 | 374.8735
2055.9417 | 410.7328 | 449.4732 | 453.7338 | 375.8913
2056.9417 | 409.942 | 449.0227 | 453.2934 | 375.9688
2057.9417 | 409.3357 | 448.8663 | 453.852 | 376.5497
2058.9417 | 408.6004 | 447.8706 | 452.2434 | 376.0438
2059.9417 | 408.2197 | 447.1147 | 453.3594 | 378.2602
2060.9417 | 409.7755 | 446.9301 | 453.9872 | 377.7703
2061.9417 | 410.4624 | 446.9955 | 454.5391 | 377.6582
2062.9417 | 410.5189 | 446.5263 | 455.9093 | 377.1792
2063.9417 | 410.6077 | 446.1028 | 455.427 | 376.5284
2064.9417 | 410.3834 | 446.1731 | 454.4582 | 375.9758
2065.9417 | 409.4869 | 445.9086 | 452.7546 | 375.4189
2066.9417 | 409.3739 | 445.8526 | 451.1322 | 376.0353
2067.9417 | 409.2162 | 445.8998 | 450.6944 | 375.0073
2068.9417 | 408.2264 | 446.0555 | 450.9938 | 374.6249
2069.9417 | 408.6829 | 446.17 | 449.9847 | 374.0953
2070.9417 | 409.4786 | 446.8309 | 450.3087 | 373.6765
2071.9417 | 409.1352 | 447.7633 | 449.5819 | 373.5012
2072.9417 | 409.9533 | 448.4898 | 449.2704 | 372.9642
2073.9417 | 410.1091 | 448.1335 | 447.072 | 372.4398
2074.9417 | 409.4561 | 447.158 | 444.9542 | 371.8358
2075.9417 | 409.6318 | 447.7399 | 445.3026 | 371.6202
2076.9417 | 410.6029 | 449.5838 | 447.2996 | 371.803
2077.9417 | 411.045 | 451.3225 | 448.7358 | 372.1051
2078.9417 | 410.9235 | 452.8124 | 448.8159 | 372.1263
2079.9417 | 410.2675 | 453.92 | 448.6293 | 371.8009
2080.9417 | 410.2067 | 454.2013 | 449.9153 | 371.7409
2081.9417 | 411.4466 | 454.8286 | 452.0656 | 371.7981
2082.9417 | 412.5653 | 454.4085 | 451.2574 | 372.2641
2083.9417 | 413.6575 | 453.3646 | 451.6034 | 372.635
2084.9417 | 414.4061 | 454.8656 | 452.8161 | 373.0626
2085.9417 | 412.9858 | 455.6339 | 451.5363 | 373.4711
2086.9417 | 413.1914 | 454.3667 | 450.2938 | 372.6929
2087.9417 | 413.8183 | 453.4906 | 449.2624 | 372.3342
2088.9417 | 416.6487 | 455.6161 | 453.4643 | 373.5464
2089.9417 | 418.6976 | 455.5503 | 456.4567 | 374.3056
2090.9417 | 421.8532 | 453.9657 | 455.9215 | 375.2536
2091.9417 | 423.2624 | 454.2497 | 457.48 | 375.7988
2092.9417 | 423.8889 | 454.0069 | 460.1498 | 376.0781
2093.9417 | 421.8617 | 453.6756 | 459.6842 | 375.8321
2094.9417 | 421.761 | 453.329 | 459.699 | 375.9855
2095.9417 | 419.4339 | 453.3331 | 459.0963 | 376.1918
2096.9417 | 418.6927 | 453.0371 | 458.9225 | 376.5256
2097.9417 | 417.3183 | 452.8073 | 459.8519 | 377.7835
2098.9417 | 415.4746 | 451.928 | 459.5814 | 378.1624
2099.9417 | 413.9368 | 451.7611 | 456.4371 | 379.8325
2100.9417 | 413.5891 | 451.9308 | 456.1791 | 379.5484
2101.9417 | 411.9165 | 451.394 | 454.1362 | 378.5395
2102.9417 | 410.9101 | 453.0113 | 453.2636 | 378.1951
2103.9417 | 409.0926 | 452.571 | 452.36 | 377.6901
2104.9417 | 408.7712 | 452.5751 | 452.4526 | 377.2403
2105.9417 | 408.443 | 452.2441 | 452.6381 | 377.644
2106.9417 | 407.5765 | 451.8285 | 453.1531 | 378.5725
2107.9417 | 407.1516 | 452.2606 | 452.2294 | 378.9232
2108.9417 | 405.0005 | 451.8246 | 451.9246 | 378.4595
2109.9417 | 404.7413 | 451.9878 | 451.7817 | 378.1742
2110.9417 | 405.6179 | 452.0529 | 451.0606 | 377.287
2111.9417 | 405.6564 | 452.1956 | 450.0644 | 376.5066
2112.9417 | 404.9299 | 452.8052 | 449.8646 | 375.6209
2113.9417 | 408.0754 | 454.5688 | 451.4329 | 375.4103
2114.9417 | 409.1053 | 453.1771 | 452.5151 | 375.2909
2115.9417 | 409.5711 | 452.4675 | 451.4449 | 375.1942
2116.9417 | 409.9401 | 454.4748 | 453.0442 | 376.2208
2117.9417 | 411.2606 | 456.1586 | 453.1622 | 376.089
2118.9417 | 413.3612 | 457.5076 | 453.4074 | 375.6862
2119.9417 | 413.671 | 457.4329 | 452.9968 | 375.764
2120.9417 | 414.3228 | 457.4404 | 454.1923 | 376.8664
2121.9417 | 416.1661 | 459.6685 | 457.4079 | 378.9591
2122.9417 | 417.7071 | 458.7606 | 458.1147 | 379.8815
2123.9417 | 417.2581 | 459.6371 | 458.3147 | 380.5317
2124.9417 | 416.9433 | 460.3668 | 459.1315 | 381.4432
2125.9417 | 416.8594 | 463.4115 | 459.9072 | 381.113
2126.9417 | 416.3575 | 463.9819 | 458.7047 | 380.6648
2127.9417 | 415.6329 | 463.8078 | 459.4444 | 380.5632
2128.9417 | 415.145 | 464.7635 | 460.6501 | 381.8357
2129.9417 | 416.9787 | 465.9423 | 461.0174 | 382.0845
2130.9417 | 417.7843 | 465.7591 | 462.3269 | 383.6167
2131.9417 | 418.01 | 465.5557 | 465.3836 | 385.9159
2132.9417 | 419.9493 | 467.0176 | 467.4455 | 387.9474
2133.9417 | 420.1382 | 467.7808 | 469.6103 | 388.0861
2134.9417 | 420.9426 | 467.676 | 469.0255 | 387.9777
2135.9417 | 422.1103 | 467.7102 | 470.9884 | 388.0344
2136.9417 | 422.6931 | 468.5629 | 473.56 | 388.1309
2137.9417 | 423.9237 | 469.4551 | 476.9836 | 388.534
2138.9417 | 426.4285 | 469.6332 | 478.523 | 390.0402
2139.9417 | 427.9796 | 470.0551 | 481.5723 | 390.6369
2140.9417 | 427.7537 | 471.1698 | 482.0031 | 392.6242
2141.9417 | 427.9529 | 470.6281 | 482.3677 | 392.1139
2142.9417 | 428.7101 | 468.6131 | 481.6339 | 392.5515
2143.9417 | 430.4009 | 468.666 | 480.7177 | 395.2685
2144.9417 | 432.0087 | 468.4811 | 480.9885 | 395.1075
2145.9417 | 430.6371 | 468.307 | 481.3299 | 395.4077
2146.9417 | 428.4005 | 468.5239 | 479.4063 | 395.4436
2147.9417 | 426.5502 | 467.5304 | 476.7304 | 394.5076
2148.9417 | 426.4676 | 467.1483 | 475.4232 | 395.5651
2149.9417 | 426.5312 | 466.6554 | 473.0836 | 394.107
2150.9417 | 425.0936 | 467.0737 | 472.6186 | 393.5872
2151.9417 | 424.3196 | 466.7933 | 472.6939 | 393.4028
2152.9417 | 424.0935 | 466.0502 | 471.8592 | 394.1977
2153.9417 | 425.4499 | 466.9914 | 475.5833 | 394.7134
2154.9417 | 425.8107 | 467.086 | 477.4742 | 395.4104
2155.9417 | 427.3223 | 467.7217 | 477.9253 | 396.7263
2156.9417 | 427.5609 | 466.4494 | 482.7553 | 398.2562
2157.9417 | 428.0107 | 466.2276 | 483.0662 | 398.1094
2158.9417 | 427.7078 | 466.4045 | 482.618 | 398.186
2159.9417 | 427.4058 | 466.772 | 482.023 | 397.8326
2160.9417 | 427.7657 | 466.1688 | 480.3999 | 397.0207
2161.9417 | 428.9251 | 465.2164 | 480.9228 | 397.7128
2162.9417 | 429.1412 | 465.8522 | 482.1056 | 398.1909
2163.9417 | 431.4087 | 465.5939 | 481.9344 | 399.4394
2164.9417 | 431.1392 | 465.2828 | 483.8295 | 399.6302
2165.9417 | 433.4701 | 466.9306 | 485.7582 | 401.5208
2166.9417 | 434.466 | 468.5839 | 492.0424 | 404.0979
2167.9417 | 435.0107 | 469.5833 | 497.4594 | 405.1957
2168.9417 | 435.361 | 469.9897 | 498.0806 | 405.1741
2169.9417 | 434.9276 | 471.6916 | 500.3206 | 404.3541
2170.9417 | 434.3978 | 471.4845 | 497.2548 | 403.3904
2171.9417 | 432.7382 | 470.7132 | 494.6288 | 401.5419
2172.9417 | 432.2113 | 471.8085 | 496.4845 | 401.3696
2173.9417 | 434.2213 | 474.3854 | 498.7385 | 402.1582
2174.9417 | 433.2315 | 474.7159 | 497.2764 | 401.3242
2175.9417 | 431.4975 | 475.5697 | 493.6323 | 400.2184
2176.9417 | 429.8361 | 476.6823 | 489.9547 | 399.0387
2177.9417 | 428.128 | 477.3887 | 487.1442 | 397.8675
2178.9417 | 428.0163 | 477.4597 | 486.4743 | 397.5712
2179.9417 | 428.141 | 478.2747 | 486.1305 | 397.9232
2180.9417 | 428.9585 | 479.78 | 485.534 | 397.6596
2181.9417 | 430.6404 | 480.0709 | 484.8997 | 397.3872
2182.9417 | 429.7535 | 477.966 | 483.8324 | 396.9166
2183.9417 | 429.2227 | 478.8347 | 483.7123 | 397.3288
2184.9417 | 427.6756 | 479.6335 | 482.9144 | 397.9061
2185.9417 | 427.6449 | 480.3566 | 481.6663 | 396.5194
2186.9573 | 426.6654 | 481.2254 | 479.5084 | 395.8733
2187.9417 | 426.6602 | 480.9984 | 481.0121 | 395.7107
2188.9417 | 424.248 | 479.1164 | 477.3385 | 394.383
2189.9417 | 424.2451 | 479.7271 | 478.4508 | 394.9127
2190.9417 | 426.366 | 480.8284 | 479.4892 | 397.6096
2191.9417 | 428.7965 | 480.7453 | 479.1592 | 397.9762
2192.9417 | 428.8665 | 480.9739 | 480.282 | 397.5802
2193.9417 | 427.9012 | 480.4626 | 481.4159 | 396.9456
2194.9417 | 428.1409 | 480.8509 | 480.8392 | 396.7181
2195.9417 | 428.0819 | 481.384 | 483.2627 | 396.7857
2196.9417 | 429.0173 | 481.6291 | 483.7726 | 396.3344
2197.9417 | 430.1788 | 482.7413 | 484.1063 | 396.8153
2198.9417 | 432.8322 | 483.3662 | 482.9678 | 396.8406
2199.9417 | 432.7258 | 483.1699 | 481.2588 | 395.9939
2200.9417 | 435.3407 | 484.3281 | 483.9223 | 397.0123
2201.9417 | 437.3979 | 484.0852 | 483.7728 | 396.6542
2202.9417 | 438.4274 | 482.1712 | 484.502 | 396.4528
2203.9417 | 437.8142 | 481.6477 | 484.6859 | 397.0303
2204.9417 | 437.2126 | 482.6333 | 489.5563 | 398.7466
2205.9417 | 435.9973 | 483.3929 | 491.3752 | 398.6461
2206.9417 | 436.0631 | 485.2719 | 492.661 | 398.4664
2207.9417 | 437.2614 | 485.9512 | 495.4052 | 398.7286
2208.9417 | 439.4239 | 487.2517 | 500.8231 | 401.1849
2209.9417 | 441.6501 | 486.7499 | 504.8221 | 403.6425
2210.9417 | 443.1516 | 487.1264 | 507.7366 | 404.5242
2211.9417 | 443.6555 | 486.8443 | 508.7052 | 404.8316
2212.9417 | 445.251 | 488.0858 | 513.0732 | 405.6335
2213.9417 | 446.3243 | 490.4273 | 516.499 | 405.9761
2214.9417 | 446.0177 | 492.047 | 518.2055 | 406.6998
2215.9417 | 444.937 | 495.0604 | 518.3788 | 406.2307
2216.9417 | 444.1047 | 496.5984 | 517.016 | 406.6765
2217.9417 | 445.2899 | 496.0887 | 522.2749 | 407.8575
2218.9417 | 446.1338 | 498.704 | 527.3515 | 410.6866
2219.9417 | 445.5977 | 499.9985 | 528.2778 | 410.3835
2220.9417 | 444.7278 | 501.7962 | 531.8118 | 410.2355
2221.9417 | 445.3915 | 504.6946 | 534.1455 | 410.0206
2222.9417 | 445.2623 | 506.0667 | 535.221 | 409.1535
2223.9417 | 446.5959 | 509.7679 | 541.9746 | 409.343
2224.9417 | 446.5429 | 512.103 | 542.6807 | 410.2509
2225.9417 | 444.9597 | 512.2724 | 541.8253 | 409.7747
2226.9417 | 445.4812 | 514.9535 | 547.3606 | 410.0365
2227.9417 | 446.4329 | 514.5334 | 546.6538 | 410.3673
2228.9417 | 446.3447 | 516.3923 | 544.8666 | 409.7668
2229.9417 | 445.4772 | 516.3843 | 542.3722 | 408.7591
2230.9417 | 443.6343 | 515.8019 | 539.5498 | 408.6371
2231.9417 | 443.8828 | 515.7226 | 535.8294 | 409.0722
2232.9417 | 444.6229 | 517.4452 | 536.6406 | 410.2665
2233.9417 | 445.9999 | 518.989 | 536.9727 | 410.7431
2234.9417 | 445.3805 | 519.9262 | 535.3861 | 411.6283
2235.9417 | 447.0663 | 523.4052 | 540.7631 | 411.9772
2236.9417 | 448.506 | 527.5005 | 546.8046 | 412.6277
2237.9417 | 450.212 | 529.8556 | 546.1285 | 413.4483
2238.9417 | 452.4253 | 531.747 | 546.8405 | 414.1168
2239.9417 | 453.6468 | 532.8239 | 547.1615 | 415.3291
2240.9417 | 454.0836 | 533.8341 | 549.9325 | 416.1323
2241.9417 | 454.5831 | 537.3935 | 550.2865 | 416.3074
2242.9417 | 453.1395 | 541.5471 | 547.9784 | 417.2148
2243.9417 | 452.7033 | 544.4352 | 548.1054 | 417.5151
2244.9417 | 451.3989 | 545.8107 | 545.86 | 417.192
2245.9417 | 452.2807 | 545.4846 | 549.6859 | 417.1942
2246.9417 | 449.6343 | 546.0119 | 550.9733 | 416.3246
2247.9417 | 449.8212 | 547.0391 | 563.664 | 417.9833
2248.9417 | 450.5189 | 549.2423 | 565.287 | 419.7265
2249.9417 | 449.3928 | 549.728 | 559.2762 | 420.0367
2250.9417 | 449.3031 | 549.7679 | 558.5431 | 419.6431
2251.9417 | 450.853 | 551.941 | 557.0463 | 419.7013
2252.9417 | 451.338 | 551.88 | 558.0432 | 420.0863
2253.9417 | 451.2139 | 552.9035 | 555.6649 | 418.9465
2254.9417 | 449.3704 | 552.2023 | 574.5684 | 417.7382
2255.9417 | 448.3461 | 555.8069 | 588.498 | 417.3729
2256.9417 | 448.7169 | 556.0787 | 596.708 | 416.7266
2257.9417 | 448.1801 | 556.6399 | 626.2458 | 416.136
2258.9417 | 446.916 | 557.5061 | 649.2319 | 415.381
2259.9417 | 446.4249 | 560.6434 | 650.3263 | 414.9005
2260.9417 | 445.9127 | 565.8271 | 645.4826 | 415.0705
2261.9417 | 448.3939 | 571.0893 | 637.581 | 415.6711
2262.9417 | 450.3527 | 569.9283 | 622.7631 | 415.2779
2263.9573 | 453.9484 | 584.5247 | 628.4558 | 415.7058
2264.9417 | 452.1516 | 587.5276 | 622.1218 | 415.4748
2265.9417 | 452.4827 | 592.1173 | 628.0247 | 415.5788
2266.9417 | 452.4194 | 595.3801 | 619.6773 | 416.0895
2267.9417 | 452.3169 | 599.804 | 609.3712 | 415.7926
2268.9573 | 453.6531 | 603.3321 | 600.9428 | 417.5111
2269.9417 | 454.3208 | 602.6868 | 596.3751 | 420.8164
2270.9417 | 456.3328 | 603.9978 | 594.6972 | 421.4863
2271.9417 | 455.7896 | 600.766 | 588.3732 | 421.5703
2272.9417 | 456.3756 | 606.8919 | 581.0312 | 420.0736
2273.9417 | 457.4392 | 607.387 | 597.9232 | 419.4505
2274.9417 | 459.1725 | 612.1851 | 598.5445 | 419.6706
2275.9417 | 460.1563 | 611.0408 | 594.8632 | 420.6773
2276.9417 | 461.144 | 612.4583 | 595.5533 | 421.2782
2277.9417 | 462.4929 | 611.6227 | 593.8093 | 421.8875
2278.9417 | 463.9219 | 609.0357 | 592.4938 | 422.5381
2279.9417 | 465.8872 | 606.3078 | 586.8414 | 423.23
2280.9417 | 469.0638 | 614.5418 | 595.8545 | 424.1873
2281.9417 | 471.4892 | 614.606 | 593.9411 | 429.0547
2282.9417 | 472.0668 | 613.4337 | 593.8226 | 431.072
2283.9417 | 470.0379 | 610.8147 | 598.5258 | 430.5704
2284.9417 | 469.0906 | 610.8859 | 595.0298 | 430.7796
2285.9417 | 468.903 | 609.8707 | 594.9801 | 429.6792
2286.9417 | 468.1951 | 609.3367 | 602.4289 | 429.824
2287.9417 | 468.4075 | 606.9183 | 599.3326 | 429.5531
2288.9417 | 468.9025 | 605.6665 | 602.4962 | 428.7322
2289.9417 | 470.3143 | 606.596 | 600.8621 | 427.745
2290.9417 | 470.3244 | 603.375 | 599.8659 | 427.7459
2291.9417 | 469.522 | 599.7107 | 597.7229 | 428.9924
2292.9417 | 468.6189 | 599.6812 | 600.0629 | 428.5676
2293.9417 | 469.1097 | 605.6995 | 609.021 | 428.1772
2294.9417 | 468.4825 | 606.8377 | 621.9909 | 426.8467
2295.9417 | 468.5643 | 607.0872 | 628.308 | 426.35
2296.9417 | 467.1148 | 608.835 | 631.5206 | 426.158
2297.9417 | 465.7493 | 612.274 | 644.6347 | 426.5814
2298.9417 | 465.4918 | 611.8712 | 646.936 | 427.0509
2299.9417 | 465.6966 | 609.7234 | 637.6864 | 428.1264
2300.9417 | 465.3697 | 611.8514 | 630.1801 | 428.7078
2301.9417 | 465.9073 | 618.532 | 633.3695 | 428.8343
2302.9417 | 466.425 | 619.1132 | 646.8757 | 429.5243
2303.9417 | 467.5383 | 621.7017 | 661.4916 | 430.3894
2304.9417 | 470.3857 | 626.2258 | 671.9092 | 431.511
2305.9417 | 470.455 | 630.6326 | 680.1454 | 432.5126
2306.9417 | 470.8933 | 634.2161 | 687.3507 | 433.8981
2307.9417 | 469.7886 | 639.6434 | 698.599 | 434.6946
2308.9417 | 470.475 | 638.5953 | 695.3887 | 435.83
2309.9417 | 470.3155 | 639.2885 | 695.3551 | 437.7969
2310.9417 | 471.8026 | 645.3381 | 698.6233 | 439.0066
2311.9417 | 474.8033 | 644.9123 | 701.0939 | 440.7592
2312.9417 | 477.7307 | 645.0404 | 694.4226 | 443.9601
2313.9417 | 478.7538 | 648.6915 | 695.6329 | 445.4175
2314.9417 | 480.1627 | 648.964 | 700.217 | 445.9332
2315.9417 | 483.4094 | 649.4921 | 696.4313 | 446.9954
2316.9417 | 486.4742 | 651.2148 | 694.4726 | 446.6524
2317.9417 | 490.7034 | 649.1613 | 692.9941 | 447.0707
2318.9417 | 490.7568 | 648.2709 | 694.7531 | 448.7757
2319.9417 | 491.3899 | 650.1795 | 699.4142 | 450.9958
2320.9417 | 494.3359 | 654.093 | 706.4943 | 451.6879
2321.9417 | 498.8695 | 655.2291 | 709.0984 | 453.3562
2322.9417 | 502.8368 | 654.5223 | 713.9386 | 455.9444
2323.9417 | 506.9492 | 653.7735 | 710.5952 | 457.2351
2324.9417 | 509.4523 | 650.7178 | 710.1325 | 457.6529
2325.9417 | 510.475 | 647.4728 | 718.912 | 457.9348
2326.9417 | 511.2955 | 650.2907 | 731.6948 | 458.0105
2327.9417 | 511.1359 | 647.1073 | 728.0389 | 459.0968
2328.9417 | 513.1823 | 648.0687 | 716.3784 | 459.6728
2329.9417 | 516.8843 | 652.7343 | 710.7848 | 462.1384
2330.9417 | 515.5999 | 654.6247 | 710.0989 | 462.6684
2331.9417 | 517.44 | 655.2578 | 698.0357 | 465.1392
2332.9417 | 518.053 | 659.577 | 692.7817 | 464.7632
2333.9417 | 517.4904 | 663.1196 | 695.3395 | 467.7319
2334.9417 | 517.0795 | 665.2881 | 700.221 | 467.9057
2335.9417 | 518.1944 | 660.7971 | 700.0303 | 470.237
2336.9417 | 518.848 | 659.5164 | 702.2715 | 469.635
2337.9417 | 519.518 | 662.8933 | 700.4327 | 470.0929
2338.9417 | 519.7905 | 664.9005 | 695.7762 | 471.0293
2339.9417 | 520.8137 | 668.5065 | 704.9708 | 471.8512
2340.9417 | 521.3101 | 668.9745 | 710.7506 | 473.0512
2341.9417 | 519.9754 | 672.5754 | 718.5821 | 472.403
2342.9417 | 517.6682 | 671.1115 | 711.6142 | 471.2827
2343.9417 | 519.1034 | 672.1344 | 715.0535 | 471.3257
2344.9417 | 519.3299 | 668.8918 | 704.4928 | 470.2175
2345.9417 | 518.2486 | 666.7744 | 694.2996 | 469.3072
2346.9417 | 517.3604 | 674.1958 | 696.4107 | 470.2485
2347.9417 | 517.898 | 674.7364 | 695.2095 | 472.7356
2348.9417 | 517.2592 | 679.8166 | 694.6907 | 473.4601
2349.9417 | 516.7899 | 679.3759 | 706.7451 | 474.1718
2350.9417 | 515.4847 | 681.6931 | 707.879 | 474.5645
2351.9417 | 517.8989 | 681.5998 | 703.7243 | 478.321
2352.9417 | 519.4518 | 681.8054 | 700.0645 | 481.1548
2353.9417 | 522.142 | 684.06 | 708.8561 | 481.3875
2354.9417 | 522.7623 | 683.1583 | 705.374 | 485.9507
2355.9417 | 522.3155 | 681.03 | 699.8952 | 489.0475
2356.9417 | 525.4901 | 680.7568 | 698.0845 | 488.9012
2357.9417 | 524.9966 | 680.5805 | 691.4801 | 489.7622
2358.9417 | 524.5201 | 677.7208 | 696.7864 | 489.6421
2359.9417 | 525.8965 | 674.0742 | 699.3877 | 489.5787
2360.9417 | 525.6928 | 674.0144 | 692.7471 | 488.7708
2361.9417 | 527.4803 | 673.2545 | 695.4137 | 490.0445
2362.9417 | 530.0882 | 673.7999 | 694.2407 | 490.4184
2363.9417 | 529.6756 | 673.5891 | 691.7476 | 489.8639
2364.9417 | 531.4308 | 675.4347 | 691.5459 | 490.9928
2365.9417 | 532.0499 | 674.0287 | 690.4821 | 491.4723
2366.9417 | 534.4053 | 676.6327 | 693.8296 | 494.9433
2367.9417 | 534.3543 | 676.5159 | 692.3154 | 496.522
2368.9417 | 532.4265 | 677.4521 | 691.1258 | 497.438
2369.9417 | 533.3546 | 679.0046 | 700.0343 | 497.5856
2370.9417 | 534.0295 | 678.8544 | 711.3452 | 501.258
2371.9417 | 534.3841 | 680.2167 | 720.5158 | 502.3526
2372.9417 | 534.2636 | 681.0036 | 720.0167 | 503.1611
2373.9417 | 533.7781 | 683.5254 | 730.6815 | 502.4287
2374.9417 | 531.0007 | 687.2889 | 746.7761 | 502.3784
2375.9417 | 529.6397 | 690.983 | 748.0097 | 503.0233
2376.9417 | 529.7765 | 692.0413 | 757.1918 | 503.6772
2377.9417 | 530.4618 | 694.2727 | 759.0132 | 504.4517
2378.9417 | 529.2506 | 696.8127 | 763.715 | 504.3843
2379.9417 | 528.2987 | 697.8652 | 746.922 | 504.6259
2380.9417 | 529.9162 | 694.9659 | 738.9149 | 505.9312
2381.9417 | 529.9126 | 691.9693 | 729.054 | 506.2064
2382.9417 | 529.0533 | 688.8021 | 719.1475 | 505.6485
2383.9417 | 527.1742 | 685.5388 | 715.2902 | 505.1017
2384.9417 | 524.8355 | 687.124 | 706.015 | 504.6049
2385.9417 | 523.8671 | 685.088 | 699.1183 | 508.1613
2386.9417 | 525.7121 | 683.3308 | 695.7064 | 510.8135
2387.9417 | 526.3411 | 680.8166 | 689.7938 | 513.327
2388.9573 | 529.8573 | 680.8642 | 698.0328 | 511.9051
2389.9417 | 529.4632 | 679.2208 | 705.9732 | 511.4153
2390.9417 | 530.0273 | 679.5 | 714.2983 | 512.935
2391.9417 | 528.8202 | 681.8878 | 721.2635 | 514.2889
2392.9417 | 526.9176 | 683.205 | 733.2921 | 513.9609
2393.9417 | 525.9321 | 682.1667 | 725.6049 | 515.8823
2394.9417 | 524.6976 | 682.503 | 727.7548 | 518.1557
2395.9417 | 525.8354 | 681.8165 | 718.1194 | 520.8093
2396.9417 | 528.7729 | 681.6248 | 712.6935 | 520.2493
2397.9417 | 532.0945 | 679.9246 | 704.5944 | 522.3222
2398.9417 | 534.2354 | 680.5034 | 697.0466 | 522.024
2399.9417 | 532.1346 | 682.1989 | 693.9094 | 520.6283
2400.9417 | 532.4085 | 684.4256 | 699.0904 | 521.0034
2401.9417 | 533.0076 | 686.3119 | 697.0087 | 520.7039
2402.9417 | 532.5224 | 689.3653 | 699.898 | 520.6394
2403.9417 | 533.5835 | 688.3962 | 694.4724 | 521.2537
2404.9417 | 532.1802 | 688.5422 | 693.632 | 523.9586
2405.9417 | 530.6351 | 692.0364 | 692.5997 | 524.3228
2406.9417 | 529.9378 | 694.2624 | 713.6946 | 523.983
2407.9417 | 528.4845 | 697.3767 | 710.0229 | 523.1173
2408.9417 | 527.5047 | 695.8529 | 703.339 | 522.9726
2409.9417 | 524.63 | 693.5928 | 696.4552 | 524.6565
2410.9417 | 522.9142 | 689.2228 | 689.8701 | 524.7332
2411.9417 | 521.2609 | 687.8075 | 681.937 | 523.0069
2412.9417 | 519.9896 | 689.4785 | 676.5043 | 524.3836
2413.9417 | 519.932 | 690.692 | 681.221 | 522.6942
2414.9417 | 520.8992 | 690.8181 | 698.0094 | 523.636
2415.9417 | 521.645 | 690.6819 | 695.7118 | 523.748
2416.9417 | 520.7081 | 693.4088 | 690.1812 | 522.9506
2417.9417 | 521.8344 | 694.3678 | 690.5713 | 524.577
2418.9417 | 520.5681 | 690.096 | 687.6206 | 525.6126
2419.9417 | 520.7173 | 688.1877 | 681.4698 | 527.126
2420.9417 | 521.6106 | 688.1051 | 677.63 | 527.8286
2421.9573 | 519.6726 | 687.9251 | 673.346 | 528.0592
2422.9417 | 521.8125 | 688.1155 | 673.3532 | 528.3656
2423.9417 | 526.1176 | 687.5159 | 676.3899 | 530.5214
2424.9417 | 528.3882 | 689.9074 | 676.8725 | 530.9887
2425.9573 | 527.4891 | 691.9033 | 674.5744 | 530.2098
2426.9417 | 527.7139 | 690.2175 | 672.505 | 532.41
2427.9573 | 527.4007 | 688.3078 | 667.672 | 533.2677
2428.9573 | 526.5995 | 687.5501 | 664.7949 | 534.2666
2429.9573 | 525.697 | 684.5331 | 660.452 | 532.8405
2430.9417 | 524.6207 | 681.4343 | 657.5514 | 532.4774
2431.9417 | 526.4455 | 679.2248 | 656.1883 | 533.0417
2432.9573 | 526.7847 | 679.0268 | 652.4491 | 531.316
2433.9417 | 526.3669 | 677.8186 | 651.2217 | 530.8769
2434.9573 | 526.0902 | 677.7971 | 651.7094 | 529.5045
2435.9417 | 526.5933 | 677.2131 | 649.1806 | 528.7801
2436.9417 | 528.011 | 678.9938 | 647.9017 | 527.2481
2437.9417 | 529.4644 | 680.0602 | 654.3764 | 528.436
2438.9417 | 531.5491 | 680.307 | 661.5533 | 527.2945
2439.9417 | 530.6522 | 682.762 | 671.6603 | 528.0706
2440.9417 | 529.7423 | 681.7994 | 668.8107 | 526.352
2441.9417 | 530.3086 | 685.9228 | 676.0137 | 525.4384
2442.9417 | 528.6233 | 687.7577 | 673.4469 | 524.1038
2443.9417 | 527.1678 | 691.9981 | 677.19 | 523.0967
2444.9417 | 526.6446 | 694.019 | 677.0043 | 523.82
2445.9417 | 525.3143 | 700.1578 | 678.1238 | 524.0875
2446.9417 | 527.4376 | 703.6801 | 682.1717 | 524.7846
2447.9417 | 526.2245 | 704.9231 | 674.9241 | 525.3373
2448.9573 | 526.5144 | 706.7598 | 669.0774 | 523.3123
2449.9417 | 524.6008 | 707.0451 | 679.3935 | 522.778
2450.9417 | 524.7707 | 706.7923 | 687.4073 | 523.0528
2451.9417 | 527.0804 | 702.9613 | 680.298 | 524.2363
2452.9417 | 530.473 | 699.8926 | 681.2691 | 523.6171
2453.9417 | 530.799 | 703.2196 | 682.6653 | 525.3336
2454.9417 | 529.8453 | 704.2815 | 680.6707 | 524.7056
2455.9417 | 529.3824 | 704.748 | 678.4139 | 524.6843
2456.9417 | 528.3346 | 703.2021 | 677.823 | 524.8581
2457.9417 | 530.998 | 701.6385 | 674.4511 | 528.1255
2458.9417 | 532.3586 | 698.9859 | 668.7155 | 529.4207
2459.9417 | 534.3301 | 699.5024 | 669.0958 | 529.6265
2460.9417 | 534.3265 | 698.0303 | 665.6275 | 527.1894
2461.9417 | 534.4919 | 696.9313 | 665.0516 | 528.8463
2462.9417 | 535.0231 | 693.9271 | 661.311 | 530.5915
2463.9417 | 533.7529 | 692.9134 | 660.2449 | 530.4894
2464.9417 | 532.4478 | 691.4103 | 653.5945 | 530.6645
2465.9417 | 538.1186 | 698.3673 | 652.7972 | 531.5827
2466.9417 | 541.7055 | 698.6265 | 663.7299 | 531.78
2467.9417 | 539.0077 | 697.2798 | 659.12 | 532.0693
2468.9417 | 534.8968 | 695.2603 | 656.7954 | 530.2729
2469.9417 | 534.2092 | 695.261 | 653.1401 | 529.7897
2470.9417 | 533.5163 | 693.4017 | 648.6183 | 529.2546
2471.9417 | 532.385 | 693.0052 | 648.5095 | 529.6086
2472.9417 | 529.1856 | 694.1967 | 648.7873 | 528.413
2473.9417 | 527.7974 | 695.7647 | 650.7295 | 527.3464
2474.9417 | 527.0107 | 699.5066 | 664.3295 | 524.792
2475.9417 | 529.0243 | 698.7681 | 662.8387 | 525.9439
2476.9417 | 531.0467 | 700.818 | 661.207 | 526.907
2477.9417 | 535.3936 | 699.7426 | 658.0527 | 533.2354
2478.9417 | 538.8041 | 699.2902 | 658.6948 | 531.3675
2479.9417 | 537.5511 | 699.7972 | 662.222 | 530.6984
2480.9417 | 533.4283 | 701.0847 | 660.7027 | 532.9239
2481.9417 | 532.4523 | 703.0394 | 657.0309 | 531.8797
2482.9417 | 531.0833 | 702.4334 | 664.9852 | 532.3053
2483.9417 | 529.0303 | 703.9596 | 671.6133 | 534.5241
2484.9417 | 529.1208 | 707.6495 | 668.703 | 535.3529
2485.9417 | 529.2905 | 702.8051 | 665.3461 | 535.5499
2486.9417 | 527.824 | 700.8203 | 661.699 | 535.5383
2487.9417 | 530.5956 | 700.9336 | 659.724 | 536.2718
2488.9417 | 531.9795 | 697.6521 | 657.3821 | 536.1673
2489.9417 | 534.4116 | 696.2976 | 655.3475 | 537.346
2490.9417 | 536.3853 | 694.29 | 654.8212 | 536.1812
2491.9417 | 539.9497 | 692.0221 | 658.6042 | 538.1531
2492.9417 | 541.6552 | 692.674 | 667.9431 | 538.6
2493.9417 | 542.1059 | 694.118 | 669.2435 | 536.3588
2494.9417 | 545.5769 | 695.4184 | 673.6984 | 537.2352
2495.9417 | 551.0935 | 692.3608 | 684.7274 | 542.5908
2496.9417 | 554.1958 | 691.248 | 685.1817 | 550.8808
2497.9417 | 557.0317 | 693.703 | 682.4881 | 548.6011
2498.9417 | 556.037 | 694.0553 | 686.7898 | 549.0858
2499.9417 | 554.0567 | 692.7924 | 683.8438 | 546.0688
2500.9417 | 553.715 | 692.3052 | 682.881 | 548.1305
2501.9417 | 556.2735 | 694.9662 | 700.0151 | 551.9526
2502.9417 | 553.9301 | 698.1319 | 705.341 | 557.004
2503.9417 | 562.3468 | 698.2354 | 718.0749 | 568.3937
2504.9417 | 571.946 | 701.0666 | 720.1619 | 574.5419
2505.9417 | 570.5721 | 703.375 | 717.8247 | 579.3353
2506.9417 | 567.6926 | 708.1456 | 716.059 | 578.6075
2507.9417 | 567.7041 | 709.0798 | 723.6951 | 582.9558
2508.9417 | 566.873 | 708.1132 | 728.7535 | 585.8399
2509.9417 | 567.5582 | 706.2907 | 722.8726 | 586.954
2510.9417 | 569.0917 | 703.594 | 721.3095 | 589.0612
2511.9417 | 569.9186 | 701.4943 | 716.2981 | 589.6708
2512.9417 | 569.9097 | 705.2713 | 717.7586 | 592.5523
2513.9417 | 576.2123 | 709.8811 | 718.039 | 595.5321
2514.9417 | 576.8046 | 711.4861 | 715.566 | 597.6794
2515.9417 | 576.6543 | 711.3326 | 711.3397 | 605.9748
2516.9417 | 575.5711 | 712.3321 | 710.0535 | 608.1076
2517.9417 | 572.3842 | 712.8942 | 715.5046 | 609.888
2518.9417 | 572.5686 | 710.6884 | 710.065 | 606.6011
2519.9417 | 572.5619 | 710.249 | 703.6898 | 608.8769
2520.9417 | 584.3642 | 706.9792 | 697.0278 | 619.6467
2521.9417 | 580.1623 | 708.5505 | 692.2982 | 625.5622
2522.9417 | 582.2382 | 706.0403 | 689.5376 | 621.2494
2523.9417 | 582.313 | 704.3442 | 685.7267 | 615.6536
2524.9417 | 581.8809 | 701.8613 | 680.037 | 614.4114
2525.9417 | 578.5575 | 704.3095 | 681.4313 | 609.3435
2526.9417 | 580.1872 | 705.3955 | 675.2899 | 605.2548
2527.9417 | 581.511 | 704.8087 | 674.8505 | 603.7108
2528.9417 | 578.9384 | 703.3309 | 669.9525 | 602.8607
2529.9417 | 578.3439 | 701.5937 | 668.696 | 597.9589
2530.9417 | 574.41 | 700.8128 | 666.2559 | 593.3084
2531.9417 | 573.2464 | 696.8971 | 664.8122 | 590.7195
2532.9417 | 571.0626 | 696.0094 | 661.5422 | 587.2387
2533.9417 | 566.3411 | 697.1524 | 670.5569 | 589.8169
2534.9417 | 568.0459 | 701.3177 | 678.6135 | 588.2062
2535.9417 | 565.4435 | 700.6779 | 682.6608 | 586.7669
2536.9417 | 560.646 | 706.7592 | 678.6343 | 583.0791
2537.9417 | 561.1491 | 705.5614 | 676.6726 | 581.1525
2538.9417 | 557.0033 | 707.3384 | 676.5249 | 579.337
2539.9417 | 554.6221 | 706.1494 | 678.3656 | 576.3724
2540.9417 | 552.1512 | 704.6907 | 679.2783 | 576.089
2541.9417 | 551.2364 | 701.7455 | 675.0822 | 574.7841
2542.9417 | 551.2554 | 700.6231 | 674.768 | 574.4285
2543.9417 | 550.2514 | 702.574 | 677.5931 | 574.4147
2544.9417 | 550.2673 | 701.6586 | 675.9924 | 572.9128
2545.9417 | 549.192 | 699.878 | 676.778 | 571.9588
2546.9417 | 546.0566 | 704.7869 | 683.6141 | 579.9119
2547.9417 | 545.9626 | 709.7221 | 686.4013 | 581.6976
2548.9417 | 546.0963 | 709.5465 | 687.0933 | 578.8703
2549.9417 | 545.321 | 711.1716 | 686.8735 | 578.5938
2550.9417 | 545.1369 | 715.3872 | 683.2947 | 574.5383
2551.9417 | 545.5193 | 715.0439 | 680.3565 | 571.1591
2552.9417 | 545.1212 | 714.9606 | 682.5997 | 573.3455
2553.9417 | 544.451 | 709.9563 | 681.647 | 575.3648
2554.9417 | 545.0413 | 707.9179 | 680.0684 | 573.9027
2555.9417 | 544.1275 | 708.515 | 681.1858 | 573.2861
2556.9417 | 544.2434 | 708.8544 | 677.8507 | 574.5685
2557.9417 | 542.8825 | 711.1589 | 680.632 | 570.2863
2558.9417 | 540.7029 | 716.0885 | 690.5333 | 569.1786
2559.9417 | 539.7375 | 716.5805 | 691.03 | 571.2953
2560.9417 | 541.2744 | 717.065 | 692.4952 | 581.7652
2561.9417 | 544.1037 | 719.4936 | 704.227 | 579.1993
2562.9417 | 543.9952 | 718.777 | 700.7064 | 581.59
2563.9417 | 545.3665 | 717.8933 | 695.8799 | 587.263
2564.9417 | 544.3101 | 717.3117 | 694.009 | 583.9632
2565.9417 | 542.0243 | 715.5369 | 691.5968 | 581.2201
2566.9417 | 545.3012 | 715.4968 | 688.3646 | 579.0659
2567.9417 | 548.2865 | 710.8069 | 685.1692 | 577.4474
2568.9417 | 553.5696 | 710.7529 | 683.4536 | 578.5694
2569.9417 | 553.4991 | 708.4813 | 678.4485 | 577.8277
2570.9417 | 555.2732 | 706.4579 | 674.815 | 575.1331
2571.9417 | 554.5214 | 706.283 | 671.9347 | 573.9367
2572.9417 | 555.6664 | 704.8964 | 673.801 | 574.2956
2573.9417 | 557.2251 | 703.6341 | 673.0973 | 572.4401
2574.9417 | 560.99 | 702.4687 | 677.7897 | 572.6032
2575.9417 | 561.2891 | 700.5353 | 679.0204 | 572.216
2576.9417 | 565.4279 | 701.2243 | 683.87 | 573.4157
2577.9417 | 573.7981 | 703.6511 | 681.2724 | 575.6269
2578.9417 | 575.573 | 702.0352 | 677.7994 | 572.1072
2579.9417 | 577.5751 | 704.3994 | 679.7843 | 574.2518
2580.9417 | 588.8568 | 703.8177 | 679.1308 | 575.7269
2581.9417 | 614.5187 | 704.0493 | 680.6918 | 578.8979
2582.9417 | 623.9118 | 702.4333 | 678.4071 | 582.1421
2583.9417 | 613.4836 | 701.956 | 678.6172 | 584.055
2584.9417 | 616.9092 | 701.5802 | 686.2936 | 606.2839
2585.9417 | 613.7591 | 703.0186 | 687.4258 | 614.2862
2586.9417 | 610.445 | 701.8159 | 691.7866 | 617.0037
2587.9417 | 606.548 | 702.4134 | 695.917 | 619.6862
2588.9417 | 608.0114 | 704.3828 | 696.4597 | 619.2114
2589.9417 | 602.8588 | 704.8622 | 690.9019 | 616.4606
2590.9417 | 601.4631 | 705.2924 | 696.223 | 613.6692
2591.9417 | 596.8634 | 707.2514 | 714.693 | 623.2532
2592.9417 | 593.8786 | 705.2728 | 720.4857 | 623.6526
2593.9417 | 587.557 | 703.7005 | 710.9868 | 625.9232
2594.9417 | 584.7207 | 702.823 | 704.2112 | 631.935
2595.9417 | 579.6517 | 706.1653 | 698.5432 | 627.6018
2596.9417 | 575.5077 | 703.7335 | 688.9565 | 624.5947
2597.9417 | 572.4538 | 702.5409 | 684.7589 | 624.3892
2598.9417 | 569.8805 | 703.3741 | 701.1142 | 626.6784
2599.9417 | 568.0162 | 702.2048 | 711.0298 | 638.8568
2600.9417 | 566.6171 | 703.6454 | 710.9809 | 654.6669
2601.9417 | 567.0212 | 706.4037 | 705.226 | 649.1937
2602.9417 | 567.553 | 706.7811 | 700.7266 | 646.4731
2603.9417 | 583.2904 | 703.9849 | 698.4983 | 648.6761
2604.9417 | 580.2242 | 700.4722 | 697.4256 | 642.0925
2605.9417 | 578.7881 | 699.8073 | 695.2657 | 635.7388
2606.9417 | 577.1153 | 699.4225 | 693.2926 | 646.077
2607.9417 | 574.2635 | 698.8614 | 688.7087 | 640.587
2608.9417 | 578.1962 | 697.5876 | 688.325 | 643.2037
2609.9417 | 578.6967 | 699.4633 | 695.9023 | 643.7499
2610.9417 | 577.6217 | 699.125 | 687.7853 | 641.2157
2611.9417 | 572.9366 | 699.5618 | 693.9684 | 639.6982
2612.9417 | 570.7624 | 698.6526 | 700.4953 | 638.8638
2613.9417 | 566.1381 | 699.9038 | 702.8408 | 645.1125
2614.9417 | 568.6179 | 700.9283 | 693.8403 | 641.0995
2615.9417 | 565.3834 | 701.8638 | 692.8749 | 632.0426
2616.9417 | 566.8626 | 702.9561 | 708.1198 | 626.5696
2617.9417 | 566.9226 | 705.2633 | 702.3198 | 624.8169
2618.9417 | 575.9845 | 707.8224 | 703.1328 | 622.0555
2619.9417 | 574.1398 | 707.0201 | 699.4431 | 619.3113
2620.9417 | 575.8002 | 705.4648 | 693.0411 | 615.6149
2621.9417 | 573.66 | 702.8182 | 687.3999 | 615.3397
2622.9417 | 572.8529 | 700.4399 | 699.9859 | 613.8003
2623.9417 | 578.7466 | 701.1884 | 700.5788 | 610.578
2624.9417 | 578.7651 | 702.0749 | 700.906 | 613.9899
2625.9417 | 586.1025 | 705.1387 | 696.2233 | 614.3854
2626.9417 | 582.3751 | 708.3933 | 710.2847 | 610.8629
2627.9417 | 578.8243 | 713.9228 | 707.3308 | 615.6245
2628.9417 | 575.2241 | 715.1996 | 713.388 | 620.3602
2629.9417 | 574.7613 | 719.9924 | 708.407 | 619.3319
2630.9417 | 575.506 | 720.0191 | 705.6787 | 617.4422
2631.9417 | 571.9295 | 717.1594 | 700.2357 | 613.2005
2632.9417 | 568.1207 | 713.202 | 697.3334 | 609.2995
2633.9417 | 569.2843 | 714.3725 | 692.2399 | 605.4019
2634.9417 | 571.4937 | 710.7312 | 686.6266 | 602.5023
2635.9417 | 572.2273 | 706.6773 | 681.9752 | 600.2531
2636.9417 | 577.1118 | 705.5616 | 675.9309 | 597.5673
2637.9417 | 578.5172 | 705.6869 | 679.8613 | 596.8881
2638.9417 | 587.36 | 705.6335 | 680.3638 | 595.7157
2639.9417 | 585.7028 | 708.9793 | 684.7057 | 594.0418
2640.9417 | 593.0267 | 710.281 | 682.1762 | 596.8849
2641.9417 | 591.7778 | 713.8541 | 683.1695 | 596.3167
2642.9417 | 590.8446 | 715.9527 | 679.058 | 597.34
2643.9417 | 592.5867 | 714.2618 | 678.169 | 595.4176
2644.9417 | 594.5366 | 714.08 | 676.3492 | 594.207
2645.9417 | 591.9451 | 712.9925 | 674.499 | 595.3302
2646.9417 | 589.5347 | 707.7693 | 674.4694 | 594.3369
2647.9417 | 599.2669 | 705.445 | 672.2162 | 597.9382
2648.9417 | 600.6609 | 705.5978 | 675.105 | 597.5074
2649.9417 | 604.0755 | 703.3518 | 673.4765 | 598.2573
2650.9417 | 598.6414 | 704.1902 | 674.7441 | 597.8185
2651.9417 | 592.8424 | 703.5462 | 673.8855 | 593.8226
2652.9417 | 590.531 | 706.6963 | 684.6319 | 595.5536
2653.9417 | 589.6712 | 704.6642 | 689.2225 | 595.7345
2654.9417 | 588.691 | 705.9188 | 694.252 | 600.3144
2655.9417 | 589.2476 | 710.6196 | 699.2757 | 602.388
2656.9417 | 594.3653 | 711.9399 | 692.7958 | 601.4875
2657.9417 | 595.1424 | 713.3795 | 697.4778 | 599.2329
2658.9417 | 591.5163 | 712.0629 | 694.5615 | 600.8976
2659.9417 | 590.0303 | 711.7804 | 691.4533 | 601.5993
2660.9417 | 589.8529 | 711.8009 | 695.3217 | 602.0188
2661.9417 | 587.7183 | 712.2817 | 703.4394 | 598.5442
2662.9417 | 583.7756 | 712.4256 | 704.6747 | 596.9747
2663.9417 | 583.5831 | 710.5981 | 707.7174 | 599.9821
2664.9417 | 588.4622 | 710.2001 | 713.4411 | 600.7274
2665.9417 | 586.2492 | 710.548 | 702.0169 | 602.9154
2666.9417 | 583.247 | 710.995 | 700.7947 | 599.8904
2667.9417 | 580.8335 | 711.2975 | 706.7121 | 603.0489
2668.9417 | 579.0782 | 708.7712 | 707.7767 | 602.56
2669.9417 | 581.7783 | 706.6603 | 706.3144 | 602.8
2670.9417 | 585.1351 | 703.104 | 699.3246 | 602.7998
2671.9417 | 585.6341 | 703.6901 | 694.8023 | 601.5307
2672.9417 | 590.1663 | 702.1138 | 692.3285 | 600.831
2673.9417 | 591.8287 | 704.197 | 691.0964 | 600.5531
2674.9417 | 595.9914 | 704.5867 | 696.227 | 602.9142
2675.9417 | 592.9168 | 707.9115 | 696.1544 | 613.9231
2676.9417 | 600.6691 | 706.5727 | 698.9635 | 614.727
2677.9417 | 599.4525 | 705.8344 | 692.5226 | 610.4494
2678.9417 | 596.4717 | 704.9878 | 695.1426 | 607.7729
2679.9417 | 596.4344 | 705.4175 | 691.8869 | 605.8913
2680.9417 | 593.1137 | 705.3116 | 689.1283 | 607.7212
2681.9417 | 591.3445 | 706.5033 | 686.3448 | 606.4168
2682.9417 | 592.9229 | 707.1411 | 688.2157 | 607.2858
2683.9417 | 617.8888 | 709.0195 | 691.5291 | 614.5633
2684.9417 | 615.2471 | 709.1447 | 695.6933 | 614.1653
2685.9417 | 614.7682 | 709.2332 | 697.9976 | 613.817
2686.9417 | 607.4986 | 709.3226 | 700.1378 | 620.7485
2687.9417 | 609.9792 | 710.4551 | 711.3492 | 623.9119
2688.9417 | 615.9329 | 710.9922 | 710.2625 | 626.0702
2689.9417 | 633.4359 | 715.1386 | 709.8628 | 622.6407
2690.9417 | 635.5143 | 717.9739 | 722.014 | 619.6988
2691.9417 | 642.5679 | 718.3464 | 718.8931 | 615.9886
2692.9417 | 634.7707 | 717.8208 | 717.642 | 612.8101
2693.9417 | 635.6723 | 716.8169 | 712.7258 | 614.6431
2694.9417 | 630.2942 | 716.2566 | 708.8997 | 614.4525
2695.9417 | 625.0971 | 716.8463 | 716.7521 | 614.8442
2696.9417 | 623.8853 | 716.9019 | 712.1664 | 617.6685
2697.9417 | 619.9058 | 719.7677 | 720.1994 | 615.855
2698.9417 | 618.2444 | 717.2296 | 713.6124 | 619.1579
2699.9417 | 618.6403 | 715.1327 | 706.1126 | 614.8738
2700.9417 | 613.5166 | 715.14 | 700.2432 | 612.5282
2701.9417 | 622.178 | 711.4971 | 703.4722 | 610.2076
2702.9417 | 626.2963 | 708.7778 | 698.479 | 611.103
2703.9417 | 635.1261 | 709.8311 | 698.9484 | 612.5892
2704.9417 | 628.3584 | 713.1613 | 696.7098 | 611.1451
2705.9417 | 625.7445 | 715.0013 | 698.0481 | 619.0094
2706.9417 | 629.0049 | 713.3417 | 693.9842 | 618.0976
2707.9417 | 623.8342 | 713.9337 | 690.937 | 615.8718
2708.9417 | 617.7751 | 717.3766 | 683.5633 | 616.5167
2709.9417 | 609.6365 | 721.3804 | 696.7702 | 615.1462
2710.9417 | 606.1945 | 721.8136 | 699.6317 | 616.9541
2711.9417 | 603.4858 | 720.8164 | 700.6478 | 615.6787
2712.9417 | 605.3608 | 717.8292 | 693.9037 | 612.6754
2713.9417 | 606.4303 | 712.8165 | 688.7385 | 609.5137
2714.9417 | 605.8056 | 709.334 | 687.4954 | 607.7486
2715.9417 | 612.3211 | 708.661 | 686.2656 | 607.6092
2716.9417 | 610.8827 | 705.6033 | 686.3245 | 607.9755
2717.9417 | 615.6125 | 704.303 | 684.0329 | 608.61
2718.9417 | 616.2831 | 704.5743 | 681.8739 | 605.9568
2719.9417 | 614.4496 | 706.0605 | 679.6225 | 605.6417
2720.9417 | 615.6846 | 706.3954 | 677.9345 | 609.0748
2721.9417 | 623.0423 | 707.9549 | 678.0104 | 610.9428
2722.9417 | 618.6875 | 710.0312 | 684.5963 | 609.9525
2723.9417 | 627.2267 | 709.511 | 689.5036 | 609.5177
2724.9417 | 635.5558 | 707.9619 | 684.715 | 609.522
2725.9417 | 632.0373 | 709.3589 | 690.6437 | 610.5595
2726.9417 | 628.0208 | 711.6044 | 685.7756 | 610.7565
2727.9417 | 622.0967 | 711.0681 | 680.3528 | 609.9868
2728.9417 | 621.6154 | 708.9191 | 681.7767 | 612.6515
2729.9417 | 619.8664 | 707.119 | 684.9519 | 614.2516
2730.9417 | 615.9832 | 714.0587 | 694.0987 | 614.0517
2731.9417 | 618.0519 | 714.8916 | 701.2484 | 625.8492
2732.9417 | 611.5919 | 717.7049 | 711.3215 | 624.4193
2733.9417 | 607.9952 | 717.2514 | 711.5783 | 622.3317
2734.9417 | 603.2161 | 718.9508 | 713.4715 | 622.6961
2735.9417 | 600.4689 | 721.8026 | 708.0057 | 619.1081
2736.9417 | 601.6236 | 720.548 | 703.4427 | 616.8053
2737.9417 | 599.052 | 715.7322 | 697.8568 | 616.853
2738.9417 | 601.6847 | 712.8139 | 692.3767 | 618.0756
2739.9417 | 605.0228 | 711.3866 | 687.8015 | 617.1972
2740.9417 | 605.3364 | 708.2523 | 682.4496 | 614.7233
2741.9417 | 602.4653 | 706.4213 | 683.0951 | 614.5902
2742.9417 | 603.1162 | 704.694 | 678.6318 | 612.4994
2743.9417 | 604.0038 | 706.9061 | 685.8822 | 616.9339
2744.9417 | 606.7282 | 705.1121 | 683.1771 | 617.8531
2745.9417 | 604.2303 | 705.4372 | 682.8751 | 616.5424
2746.9417 | 617.9305 | 705.6352 | 685.8546 | 617.8353
2747.9417 | 617.3296 | 703.2991 | 684.4332 | 616.6216
2748.9417 | 622.7899 | 703.1614 | 680.6473 | 613.5373
2749.9417 | 629.7683 | 703.9111 | 684.4577 | 609.8112
2750.9417 | 629.8689 | 704.6064 | 680.1552 | 609.8173
2751.9417 | 643.4244 | 701.6759 | 678.6815 | 610.1122
2752.9417 | 642.3588 | 701.2776 | 681.1198 | 611.4122
2753.9417 | 648.3522 | 703.6637 | 680.5533 | 612.4971
2754.9417 | 653.5 | 706.5196 | 682.3448 | 614.9032
2755.9417 | 653.4186 | 706.6255 | 682.9011 | 616.2507
2756.9417 | 657.3439 | 705.0766 | 681.0695 | 616.7229
2757.9417 | 654.0747 | 707.0678 | 682.821 | 613.7744
2758.9417 | 651.1751 | 707.8282 | 681.6056 | 613.4408
2759.9417 | 658.7654 | 707.0398 | 680.2311 | 612.2444
2760.9417 | 655.5302 | 706.2782 | 680.3103 | 616.4126
2761.9417 | 648.7944 | 706.4582 | 678.4082 | 616.6534
2762.9417 | 652.9283 | 708.6708 | 685.6522 | 620.8131
2763.9417 | 654.7324 | 710.5286 | 685.808 | 628.3558
2764.9417 | 659.5945 | 712.7914 | 684.0926 | 625.2703
2765.9417 | 652.3076 | 711.9333 | 683.7827 | 622.6678
2766.9417 | 657.3049 | 714.1837 | 686.8166 | 625.0571
2767.9417 | 654.4622 | 715.1765 | 688.4722 | 630.3435
2768.9417 | 655.1346 | 718.0642 | 692.5094 | 628.0857
2769.9417 | 654.6226 | 720.1433 | 696.4218 | 632.1057
2770.9417 | 659.1102 | 720.0449 | 691.4302 | 629.2633
2771.9417 | 656.611 | 716.625 | 690.2387 | 630.6726
2772.9417 | 671.6778 | 720.6391 | 687.2136 | 647.1027
2773.9417 | 667.786 | 716.3895 | 693.6509 | 657.7903
2774.9417 | 662.6003 | 714.4686 | 695.5246 | 655.4268
2775.9417 | 663.8163 | 715.1802 | 702.3148 | 659.457
2776.9417 | 657.0877 | 715.9581 | 706.5156 | 662.3599
2777.9417 | 652.3408 | 713.3782 | 711.1281 | 669.305
2778.9417 | 662.4726 | 714.3847 | 710.9516 | 676.8073
2779.9417 | 680.3356 | 716.5631 | 715.0841 | 677.3609
2780.9417 | 677.9566 | 718.7435 | 719.7192 | 671.5335
2781.9417 | 667.7423 | 720.3633 | 731.0504 | 673.5003
2782.9417 | 669.8712 | 719.7106 | 731.4842 | 668.8785
2783.9417 | 664.4932 | 714.8743 | 731.8677 | 664.3268
2784.9417 | 661.8892 | 713.4997 | 737.0598 | 660.9183
2785.9417 | 659.0798 | 710.797 | 724.4249 | 656.4054
2786.9417 | 661.6568 | 712.0759 | 720.482 | 651.0225
2787.9417 | 662.4596 | 713.7795 | 724.2727 | 653.6082
2788.9417 | 658.0558 | 713.4472 | 720.2878 | 652.4909
2789.9417 | 655.9214 | 714.6865 | 713.5212 | 648.9628
2790.9417 | 659.547 | 713.2307 | 712.7511 | 646.6418
2791.9417 | 656.7502 | 711.8852 | 707.0353 | 640.9643
2792.9417 | 656.48 | 708.9252 | 702.5568 | 637.2212
2793.9417 | 667.6263 | 707.0782 | 704.6012 | 638.7247
2794.9417 | 671.3824 | 707.4312 | 705.5321 | 646.3213
2795.9417 | 686.6863 | 710.5553 | 705.9337 | 666.2753
2796.9417 | 688.058 | 712.0094 | 714.5068 | 662.7691
2797.9417 | 694.8509 | 712.71 | 727.8788 | 667.699
2798.9417 | 694.2886 | 713.6632 | 726.7036 | 663.3006
2799.9417 | 700.239 | 712.9774 | 719.6273 | 664.6142
2800.9417 | 696.8299 | 709.7425 | 713.0126 | 659.1709
2801.9417 | 693.0747 | 709.1288 | 705.7867 | 654.5452
2802.9417 | 686.2651 | 705.513 | 702.2557 | 650.326
2803.9417 | 686.1805 | 708.197 | 706.4137 | 648.7908
2804.9417 | 684.4138 | 711.3537 | 707.2575 | 650.3612
2805.9417 | 686.4265 | 710.9627 | 705.2042 | 648.8345
2806.9417 | 682.6857 | 711.0288 | 710.1884 | 654.3733
2807.9417 | 689.4711 | 712.7896 | 707.8462 | 657.8031
2808.9417 | 695.1912 | 712.253 | 709.6976 | 657.0388
2809.9417 | 693.2383 | 711.799 | 705.558 | 654.5208
2810.9417 | 697.3016 | 713.5352 | 709.1723 | 654.3685
2811.9417 | 683.7386 | 714.6141 | 707.6375 | 650.8396
2812.9417 | 682.0273 | 713.3097 | 700.5404 | 655.8097
2813.9417 | 679.8517 | 710.4532 | 700.7773 | 656.4364
2814.9417 | 673.3612 | 707.721 | 700.6958 | 653.33
2815.9417 | 671.0699 | 705.6685 | 698.9072 | 650.4471
2816.9417 | 670.9594 | 705.0538 | 696.5036 | 646.3556
2817.9417 | 663.1265 | 702.1363 | 695.1909 | 643.0227
2818.9417 | 661.825 | 702.6176 | 690.0225 | 639.6828
2819.9417 | 661.1527 | 704.5905 | 690.6345 | 636.8774
2820.9417 | 657.7331 | 704.9905 | 690.0232 | 635.4393
2821.9417 | 661.4609 | 704.2089 | 690.8999 | 646.2826
2822.9417 | 666.1719 | 703.1099 | 688.8367 | 641.2505
2823.9417 | 666.2946 | 705.9991 | 690.0565 | 637.9945
2824.9417 | 667.3308 | 705.9252 | 692.5881 | 639.433
2825.9417 | 666.6836 | 709.6078 | 693.0249 | 639.3724
2826.9417 | 667.8175 | 715.2328 | 706.4515 | 639.1342
2827.9417 | 679.7996 | 715.8052 | 704.7114 | 648.4642
2828.9417 | 684.2778 | 713.1996 | 710.7274 | 657.9129
2829.9417 | 695.1779 | 711.2496 | 705.9941 | 655.376
2830.9417 | 689.7966 | 709.6055 | 701.3895 | 648.6445
2831.9417 | 680.5801 | 712.0139 | 707.3182 | 643.8213
2832.9417 | 678.1515 | 713.2286 | 709.7099 | 643.6815
2833.9417 | 684.199 | 712.01 | 706.8711 | 642.924
2834.9417 | 679.2358 | 708.3486 | 699.6428 | 641.7458
2835.9417 | 674.3705 | 708.7523 | 698.0692 | 638.3148
2836.9417 | 680.1127 | 706.6372 | 695.9555 | 636.2502
2837.9417 | 675.804 | 706.138 | 696.54 | 636.1701
2838.9417 | 691.7853 | 706.8326 | 696.762 | 633.3406
2839.9417 | 688.0619 | 705.8271 | 701.6191 | 635.5071
2840.9417 | 698.2174 | 703.7539 | 710.9781 | 639.3866
2841.9417 | 704.0264 | 705.2776 | 714.7515 | 640.3262
2842.9417 | 703.883 | 705.7632 | 715.1435 | 646.6597
2843.9417 | 700.2272 | 704.7453 | 718.0362 | 645.6903
2844.9417 | 696.2732 | 703.6313 | 711.9486 | 647.5172
2845.9417 | 697.1083 | 701.0293 | 705.3983 | 651.2308
2846.9417 | 694.4687 | 700.7043 | 705.2302 | 652.5827
2847.9417 | 695.9393 | 702.6873 | 699.5108 | 645.7942
2848.9417 | 691.3876 | 701.2135 | 696.8457 | 642.1226
2849.9417 | 691.3172 | 702.1323 | 705.7299 | 643.1438
2850.9417 | 683.936 | 708.9429 | 705.1437 | 638.6335
2851.9417 | 700.4128 | 708.132 | 720.906 | 651.6403
2852.9417 | 706.0443 | 705.8735 | 722.4566 | 649.2169
2853.9417 | 708.4142 | 706.4215 | 723.0703 | 651.2973
2854.9417 | 710.8346 | 710.514 | 726.7987 | 650.0971
2855.9417 | 703.9417 | 708.0356 | 725.347 | 651.8021
2856.9417 | 723.057 | 708.3189 | 727.3762 | 657.9376
2857.9417 | 723.2682 | 708.0849 | 736.8234 | 665.4899
2858.9417 | 724.2155 | 716.3303 | 739.358 | 666.2763
2859.9417 | 715.8371 | 714.2632 | 730.7145 | 661.8778
2860.9417 | 717.9793 | 716.4027 | 726.0828 | 659.1652
2861.9417 | 720.7331 | 716.6151 | 722.5087 | 655.4538
2862.9417 | 725.791 | 716.0959 | 725.4654 | 661.5418
2863.9417 | 732.9204 | 721.3691 | 733.7229 | 662.9762
2864.9417 | 736.6316 | 716.7398 | 736.3565 | 661.5044
2865.9417 | 731.7836 | 717.5319 | 743.344 | 662.2215
2866.9417 | 724.7599 | 715.3798 | 736.4403 | 663.6712
2867.9417 | 718.8151 | 712.9122 | 732.4745 | 663.1616
2868.9417 | 724.3425 | 712.0563 | 730.1045 | 668.0959
2869.9417 | 731.2397 | 712.902 | 729.5933 | 670.2343
2870.9417 | 728.4312 | 710.0881 | 732.5997 | 670.3174
2871.9417 | 736.9113 | 710.5863 | 729.1163 | 666.9741
2872.9417 | 727.7567 | 708.646 | 727.4039 | 665.123
2873.9417 | 727.4436 | 714.3988 | 744.4472 | 663.3467
2874.9417 | 720.6998 | 713.798 | 741.1754 | 662.386
2875.9417 | 713.9607 | 710.0948 | 726.7395 | 665.2072
2876.9417 | 706.9354 | 709.8955 | 719.9045 | 662.0468
2877.9417 | 703.6983 | 710.2961 | 718.5903 | 660.4111
2878.9417 | 713.3727 | 710.4881 | 715.2132 | 657.77
2879.9417 | 711.5342 | 711.2758 | 719.37 | 656.3084
2880.9417 | 708.3388 | 711.9238 | 717.8135 | 655.4894
2881.9417 | 707.5275 | 710.9469 | 716.2069 | 655.5564
2882.9417 | 712.6635 | 710.8311 | 711.9496 | 656.563
2883.9417 | 714.2391 | 711.825 | 715.7085 | 657.9065
2884.9417 | 714.8143 | 713.1141 | 721.3004 | 660.1642
2885.9417 | 721.6523 | 713.5086 | 725.8587 | 663.6571
2886.9417 | 725.69 | 711.1558 | 727.2473 | 662.0613
2887.9417 | 725.3857 | 707.4292 | 730.4379 | 667.7519
2888.9417 | 723.7248 | 704.9884 | 729.8809 | 668.0839
2889.9417 | 721.3801 | 700.3809 | 717.4561 | 666.3685
2890.9417 | 715.8363 | 698.6864 | 710.6364 | 664.7506
2891.9417 | 708.2881 | 697.6339 | 707.0606 | 664.4446
2892.9417 | 709.1252 | 697.1008 | 706.993 | 661.6179
2893.9417 | 711.266 | 695.3313 | 701.9761 | 658.9687
2894.9417 | 713.7355 | 694.0595 | 704.881 | 657.367
2895.9417 | 715.2096 | 691.319 | 705.3485 | 657.6036
2896.9417 | 713.938 | 692.9971 | 707.3779 | 656.3083
2897.9417 | 713.6898 | 696.3735 | 715.0451 | 655.777
2898.9417 | 716.9743 | 695.5881 | 705.7975 | 656.8434
2899.9417 | 722.9426 | 694.7855 | 711.3929 | 655.8168
2900.9417 | 722.726 | 692.5804 | 705.9233 | 654.1834
2901.9417 | 732.3996 | 690.3918 | 705.3777 | 656.3825
2902.9417 | 739.2708 | 689.8206 | 704.7504 | 658.0403
2903.9417 | 738.6342 | 694.3602 | 704.6493 | 653.9707
2904.9417 | 724.3495 | 693.555 | 703.1327 | 649.5179
2905.9417 | 724.4238 | 690.6058 | 699.1804 | 649.9421
2906.9417 | 728.5545 | 692.7477 | 707.4716 | 653.0554
2907.9417 | 737.2383 | 694.9595 | 710.1471 | 652.239
2908.9417 | 736.6057 | 695.5041 | 716.0809 | 652.8421
2909.9417 | 729.7916 | 693.9 | 710.3364 | 652.2114
2910.9417 | 736.7108 | 690.9706 | 705.4055 | 652.8487
2911.9417 | 738.7834 | 690.9171 | 702.2819 | 656.7792
2912.9417 | 730.6457 | 690.2098 | 700.2817 | 651.5797
2913.9729 | 727.0041 | 692.049 | 701.6736 | 647.5684
2914.9417 | 724.2738 | 691.9616 | 707.6315 | 651.218
2915.9417 | 727.9565 | 690.2904 | 703.7388 | 648.9456
2916.9417 | 744.7047 | 687.2545 | 702.8591 | 646.5499
2917.9417 | 741.2905 | 684.8917 | 699.7038 | 644.2021
2918.9417 | 739.3172 | 683.7356 | 695.5714 | 643.5429
2919.9417 | 738.9673 | 685.1594 | 694.9408 | 644.8654
2920.9417 | 735.6804 | 685.3038 | 694.1908 | 641.6846
2921.9417 | 727.213 | 685.6373 | 698.258 | 643.4507
2922.9417 | 729.4394 | 684.8142 | 694.5309 | 644.0947
2923.9417 | 726.8421 | 682.8723 | 691.9922 | 643.5321
2924.9417 | 719.6264 | 679.3934 | 688.8204 | 641.7018
2925.9417 | 719.74 | 677.8298 | 686.9438 | 640.0641
2926.9417 | 722.2985 | 675.8382 | 682.6596 | 637.3785
2927.9417 | 725.6992 | 675.3527 | 682.6933 | 640.938
2928.9417 | 732.8814 | 674.4107 | 688.9454 | 645.4699
2929.9417 | 722.9113 | 674.3532 | 687.495 | 644.1506
2930.9417 | 723.3841 | 673.566 | 689.8806 | 645.0426
2931.9417 | 720.0528 | 672.4626 | 691.7393 | 650.7108
2932.9417 | 723.7255 | 670.8076 | 693.3883 | 649.0432
2933.9417 | 727.7729 | 670.344 | 695.8512 | 649.5217
2934.9417 | 721.4185 | 671.0598 | 697.0747 | 655.829
2935.9417 | 730.9901 | 672.5294 | 696.3083 | 659.0084
2936.9417 | 731.8145 | 673.4169 | 696.6812 | 659.0705
2937.9417 | 734.75 | 673.9223 | 702.0865 | 659.383
2938.9417 | 736.0164 | 673.8035 | 706.0501 | 658.1256
2939.9417 | 737.5089 | 672.8424 | 704.6351 | 656.97
2940.9417 | 745.5162 | 671.8107 | 700.8104 | 653.8582
2941.9417 | 740.0017 | 670.3929 | 699.1367 | 654.673
2942.9417 | 735.9862 | 669.7013 | 708.9203 | 652.9781
2943.9417 | 733.8492 | 669.6599 | 700.4531 | 660.7736
2944.9417 | 724.9528 | 668.2224 | 698.3486 | 654.9859
2945.9417 | 726.2018 | 670.6491 | 702.4461 | 654.8295
2946.9417 | 723.9741 | 671.478 | 701.4981 | 654.5894
2947.9417 | 728.0328 | 671.0496 | 694.7746 | 655.6738
2948.9417 | 721.9582 | 669.7864 | 695.7984 | 651.7549
2949.9417 | 718.2793 | 668.046 | 693.827 | 648.6378
2950.9573 | 728.1909 | 666.9192 | 692.6566 | 651.2643
2951.9417 | 730.5281 | 665.96 | 693.853 | 648.9578
2952.9417 | 721.5822 | 664.0078 | 691.952 | 657.7013
2953.9417 | 728.6917 | 665.0316 | 691.8008 | 658.4135
2954.9417 | 723.2008 | 664.7999 | 695.0353 | 656.8564
2955.9417 | 723.1826 | 664.6211 | 699.0339 | 656.0878
2956.9417 | 729.279 | 664.7757 | 695.1379 | 652.2312
2957.9417 | 727.2519 | 666.5454 | 693.362 | 650.5127
2958.9417 | 720.0708 | 668.6186 | 705.5345 | 648.5344
2959.9417 | 721.9642 | 668.5762 | 711.8752 | 651.495
2960.9417 | 714.9033 | 667.8707 | 703.9777 | 648.7124
2961.9417 | 724.6179 | 667.9365 | 703.2619 | 647.0472
2962.9417 | 719.748 | 666.3483 | 699.3342 | 648.8043
2963.9417 | 724.1217 | 666.174 | 698.7502 | 649.5022
2964.9417 | 725.9968 | 667.2608 | 699.3696 | 648.493
2965.9417 | 713.9933 | 667.5524 | 693.7861 | 648.067
2966.9417 | 715.9042 | 666.7539 | 686.3112 | 646.9698
2967.9417 | 722.4594 | 664.7234 | 686.7548 | 649.8522
2968.9417 | 734.6233 | 664.6338 | 688.129 | 656.944
2969.9417 | 728.1813 | 665.9465 | 695.278 | 659.964
2970.9417 | 736.634 | 669.3962 | 695.4688 | 657.2398
2971.9417 | 728.1478 | 670.8938 | 699.7406 | 654.9213
2972.9417 | 734.5498 | 669.2243 | 700.8343 | 652.8255
2973.9417 | 726.6343 | 666.7127 | 698.711 | 648.5663
2974.9417 | 724.5889 | 666.8869 | 699.6054 | 647.2889
2975.9417 | 732.3704 | 667.4687 | 703.2608 | 646.3205
2976.9417 | 734.0743 | 665.9112 | 703.4418 | 650.8369
2977.9417 | 729.8036 | 667.9315 | 701.4491 | 647.7438
2978.9417 | 727.208 | 671.1565 | 705.0827 | 646.1649
2979.9417 | 720.2783 | 670.327 | 699.8221 | 643.6758
2980.9573 | 719.4539 | 667.8338 | 702.9594 | 642.5104
2981.9417 | 722.7046 | 665.0674 | 703.5814 | 640.3134
2982.9417 | 723.3196 | 668.0932 | 705.8602 | 642.3802
2983.9417 | 727.1045 | 671.1605 | 707.8986 | 648.5608
2984.9417 | 735.1142 | 671.4138 | 709.937 | 648.2426
2985.9417 | 732.2151 | 671.3523 | 700.3219 | 648.9936
2986.9417 | 732.549 | 669.6668 | 694.1998 | 649.7403
2987.9417 | 734.2722 | 667.6332 | 692.89 | 649.7502
2988.9417 | 730.4306 | 665.8833 | 691.3316 | 648.0717
2989.9417 | 729.5384 | 663.9895 | 687.3856 | 645.4696
2990.9417 | 727.8225 | 663.9783 | 689.2686 | 649.9532
2991.9417 | 731.4506 | 665.2036 | 696.2404 | 657.8403
2992.9417 | 729.3155 | 666.4153 | 707.8256 | 657.8839
2993.9417 | 735.404 | 665.3142 | 705.5854 | 660.501
2994.9417 | 733.451 | 665.8148 | 705.9182 | 659.9842
2995.9417 | 736.6465 | 673.0549 | 709.7661 | 674.9297
2996.9417 | 733.1037 | 676.8012 | 710.6741 | 680.1956
2997.9417 | 732.1206 | 676.456 | 708.1818 | 675.7148
2998.9417 | 733.7197 | 677.8088 | 710.0547 | 673.4243
2999.9417 | 728.833 | 679.3967 | 713.5429 | 675.0351
3000.9417 | 736.6657 | 678.2187 | 718.0424 | 667.8808
3001.9417 | 735.0202 | 679.4736 | 719.5944 | 671.0536
3002.9417 | 736.7931 | 682.2446 | 714.4008 | 668.3177
3003.9417 | 734.1217 | 679.5345 | 707.4603 | 665.3546
3004.9417 | 736.1517 | 675.792 | 696.8689 | 659.0712
3005.9417 | 735.076 | 674.1499 | 692.1173 | 655.0745
3006.9417 | 735.4988 | 671.6261 | 686.6993 | 651.9216
3007.9417 | 728.3594 | 670.8546 | 691.4152 | 649.0267
3008.9417 | 722.2259 | 668.7164 | 689.298 | 647.3608
3009.9417 | 723.724 | 668.5308 | 689.3236 | 646.2597
3010.9417 | 731.3445 | 668.0296 | 690.046 | 646.1056
3011.9417 | 734.0583 | 667.1759 | 687.5039 | 644.7095
3012.9417 | 726.5016 | 667.0077 | 685.0096 | 649.8673
3013.9417 | 726.6811 | 665.7231 | 682.8529 | 647.6875
3014.9417 | 724.1017 | 664.1401 | 686.4674 | 645.758
3015.9417 | 725.5382 | 662.7936 | 683.9268 | 646.8169
3016.9417 | 725.1743 | 661.353 | 685.4077 | 649.0365
3017.9417 | 731.8287 | 660.069 | 678.2607 | 646.618
3018.9417 | 734.7802 | 658.3258 | 674.4373 | 643.707
3019.9417 | 730.9998 | 656.6051 | 671.4568 | 642.6888
3020.9417 | 725.0937 | 655.3379 | 667.831 | 641.9739
3021.9417 | 717.4465 | 655.5588 | 670.0311 | 643.1455
3022.9417 | 720.163 | 656.3646 | 671.6698 | 644.3947
3023.9417 | 727.413 | 656.1888 | 672.7967 | 643.6324
3024.9417 | 722.6209 | 653.9608 | 669.8556 | 643.8334
3025.9417 | 733.5943 | 652.5243 | 669.09 | 641.6336
3026.9417 | 746.1019 | 651.2912 | 664.7893 | 655.1789
3027.9417 | 741.9895 | 650.9942 | 662.6315 | 648.1648
3028.9417 | 740.939 | 650.8845 | 664.1474 | 646.5226
3029.9417 | 737.8796 | 651.2283 | 661.4989 | 643.8543
3030.9417 | 730.471 | 651.3824 | 665.9654 | 645.0206
3031.9417 | 729.0325 | 651.6087 | 666.5832 | 652.1104
3032.9417 | 735.8179 | 652.2211 | 666.1838 | 659.2776
3033.9417 | 740.5257 | 653.544 | 665.1806 | 656.7786
3034.9417 | 741.5732 | 653.5838 | 666.4085 | 656.1255
3035.9417 | 735.672 | 652.0034 | 665.7633 | 662.6534
3036.9417 | 728.9271 | 650.4184 | 662.0473 | 659.3245
3037.9417 | 725.87 | 650.1203 | 660.5414 | 656.6068
3038.9417 | 722.7941 | 649.1173 | 661.8184 | 654.8307
3039.9417 | 717.03 | 648.2473 | 663.5295 | 652.79
3040.9417 | 710.9746 | 648.173 | 674.2826 | 651.3546
3041.9417 | 704.1611 | 649.4308 | 674.7558 | 648.1859
3042.9417 | 704.3925 | 648.9982 | 677.9821 | 650.969
3043.9417 | 716.0755 | 648.3849 | 679.8676 | 653.936
3044.9417 | 709.9687 | 646.8735 | 678.2119 | 651.4955
3045.9417 | 706.1596 | 646.7769 | 673.1678 | 647.5743
3046.9417 | 711.3926 | 645.7171 | 672.5913 | 644.9678
3047.9417 | 715.6748 | 645.3734 | 672.6043 | 644.3855
3048.9417 | 715.8304 | 644.8769 | 671.8835 | 645.0678
3049.9417 | 711.4785 | 644.1372 | 671.7521 | 642.9143
3050.9417 | 716.5767 | 642.951 | 671.1382 | 644.9963
3051.9417 | 705.4744 | 642.7357 | 671.418 | 642.7656
3052.9417 | 700.3974 | 642.9719 | 667.8495 | 641.007
3053.9417 | 702.6965 | 645.2615 | 667.7718 | 642.3141
3054.9417 | 708.4149 | 644.6944 | 668.2109 | 641.4966
3055.9417 | 705.4436 | 644.2833 | 668.6985 | 642.1619
3056.9417 | 711.6827 | 643.5372 | 667.0879 | 645.5467
3057.9417 | 705.6194 | 641.5906 | 662.0911 | 641.4177
3058.9417 | 699.2074 | 640.5985 | 661.7278 | 637.9934
3059.9417 | 693.0511 | 639.797 | 660.3921 | 637.7263
3060.9417 | 692.7936 | 639.4434 | 659.9939 | 637.1707
3061.9417 | 706.1654 | 638.4306 | 656.8789 | 635.583
3062.9417 | 710.0637 | 638.5507 | 652.6282 | 633.9736
3063.9417 | 705.0821 | 638.0088 | 650.5297 | 631.8035
3064.9417 | 702.9826 | 637.78 | 653.2333 | 633.3799
3065.9417 | 702.9806 | 639.3664 | 654.4612 | 633.1895
3066.9417 | 714.8057 | 639.4719 | 655.8395 | 638.3771
3067.9417 | 717.9687 | 639.9892 | 657.939 | 644.1002
3068.9417 | 710.7401 | 640.7868 | 663.7545 | 648.1003
3069.9417 | 702.7726 | 643.1356 | 665.3125 | 648.4703
3070.9417 | 694.6379 | 643.2359 | 662.0608 | 645.4634
3071.9417 | 692.2121 | 642.3544 | 662.8716 | 644.5729
3072.9417 | 706.363 | 642.1729 | 665.5195 | 641.7238
3073.9417 | 714.8825 | 643.1636 | 664.5603 | 640.9159
3074.9417 | 721.5884 | 643.1672 | 662.2755 | 640.3158
3075.9417 | 714.1262 | 642.749 | 666.9275 | 637.7691
3076.9417 | 714.2621 | 644.4594 | 669.3097 | 640.3476
3077.9417 | 720.6463 | 645.1647 | 666.9332 | 640.8759
3078.9417 | 722.3776 | 644.7085 | 663.1198 | 639.3762
3079.9417 | 725.4323 | 646.8322 | 665.933 | 642.7671
3080.9417 | 719.4907 | 647.1386 | 665.9346 | 639.5172
3081.9417 | 711.1909 | 648.7921 | 685.8666 | 636.8863
3082.9417 | 716.0667 | 648.5567 | 685.339 | 637.9767
3083.9417 | 716.7688 | 651.3412 | 681.5068 | 636.8096
3084.9417 | 718.6203 | 650.3305 | 679.5828 | 642.2711
3085.9417 | 721.7138 | 652.1327 | 679.114 | 645.6524
3086.9417 | 716.3954 | 651.4021 | 675.7021 | 644.2511
3087.9417 | 713.8585 | 651.3722 | 675.3076 | 640.755
3088.9417 | 718.6576 | 650.1359 | 671.0253 | 637.5752
3089.9417 | 725.3847 | 648.4573 | 667.6587 | 643.9078
3090.9417 | 724.5469 | 646.9821 | 667.8236 | 649.7568
3091.9417 | 725.6715 | 646.651 | 668.2948 | 645.629
3092.9417 | 724.0761 | 645.2588 | 668.9741 | 646.0414
3093.9417 | 716.8777 | 643.2923 | 663.3959 | 643.8825
3094.9417 | 711.4032 | 641.8853 | 661.7738 | 643.6674
3095.9417 | 706.5561 | 641.2802 | 660.0497 | 643.6857
3096.9417 | 710.3722 | 643.1895 | 662.7879 | 642.8279
3097.9417 | 714.4983 | 644.6704 | 665.5316 | 643.3332
3098.9417 | 715.8085 | 643.9354 | 662.7513 | 642.4623
3099.9417 | 713.0971 | 641.3809 | 661.8769 | 649.0225
3100.9417 | 711.2638 | 639.7095 | 659.3107 | 645.5646
3101.9417 | 704.8735 | 639 | 657.2383 | 641.7723
3102.9417 | 705.5227 | 637.212 | 657.5405 | 637.6963
3103.9417 | 707.3336 | 636.2529 | 658.2759 | 639.0234
3104.9417 | 710.1161 | 637.116 | 657.0956 | 640.8469
3105.9417 | 706.5982 | 638.2436 | 656.6398 | 657.9986
3106.9417 | 710.2462 | 637.073 | 653.7021 | 659.7728
3107.9417 | 708.1168 | 635.5008 | 652.4633 | 660.2274
3108.9417 | 706.3862 | 635.6656 | 651.2251 | 654.7049
3109.9417 | 711.4363 | 635.3083 | 654.9538 | 651.752
3110.9417 | 709.1543 | 636.0632 | 656.0688 | 647.9398
3111.9417 | 711.7897 | 636.5165 | 653.0012 | 643.5386
3112.9417 | 711.6488 | 636.7685 | 652.0999 | 643.386
3113.9417 | 712.5611 | 638.2191 | 649.8928 | 642.6003
3114.9417 | 708.788 | 638.5252 | 653.4013 | 648.1376
3115.9417 | 709.7116 | 638.5614 | 657.1486 | 653.551
3116.9417 | 708.0592 | 638.4052 | 656.0187 | 648.3098
3117.9417 | 707.8352 | 638.9165 | 653.2288 | 644.0997
3118.9417 | 710.5969 | 638.299 | 652.8547 | 643.3299
3119.9417 | 711.1961 | 637.5935 | 652.5199 | 641.3461
3120.9417 | 711.6249 | 636.2111 | 649.0514 | 641.2235
3121.9417 | 716.9736 | 637.1497 | 649.8083 | 645.2489
3122.9417 | 714.5825 | 636.6707 | 651.5929 | 645.2273
3123.9417 | 711.9967 | 637.2612 | 653.2674 | 641.2362
3124.9417 | 712.0828 | 637.2677 | 653.9332 | 638.7927
3125.9417 | 709.5621 | 637.2815 | 654.4946 | 639.9276
3126.9417 | 711.0388 | 637.3381 | 653.0593 | 644.3873
3127.9417 | 705.9718 | 636.1203 | 650.1196 | 646.3033
3128.9417 | 710.4935 | 635.878 | 646.6007 | 644.2416
3129.9417 | 713.638 | 634.5321 | 649.6158 | 645.8342
3130.9417 | 705.2297 | 635.1576 | 649.2845 | 642.0553
3131.9417 | 704.4271 | 634.3999 | 649.0117 | 640.9711
3132.9417 | 708.6789 | 633.511 | 645.0946 | 636.9172
3133.9417 | 705.8185 | 632.8702 | 644.1932 | 633.1157
3134.9417 | 710.3741 | 632.8632 | 646.3948 | 632.0249
3135.9417 | 714.0955 | 632.9484 | 644.3213 | 635.7937
3136.9417 | 710.9691 | 630.8838 | 641.3976 | 636.6179
3137.9417 | 709.4785 | 631.0714 | 638.9469 | 634.7647
3138.9417 | 710.645 | 631.3599 | 641.0544 | 634.2674
3139.9417 | 715.0354 | 631.2552 | 640.5595 | 634.2705
3140.9417 | 715.1211 | 631.2949 | 643.5011 | 639.0271
3141.9417 | 716.695 | 631.7479 | 644.2917 | 636.6731
3142.9417 | 719.6424 | 634.192 | 649.9903 | 645.9966
3143.9417 | 717.5988 | 635.7046 | 651.2622 | 644.4433
3144.9417 | 722.4366 | 634.6331 | 652.5559 | 642.5963
3145.9417 | 712.8364 | 635.3193 | 651.7788 | 639.6349
3146.9417 | 716.8254 | 634.1177 | 651.3486 | 637.0511
3147.9417 | 720.1452 | 634.9224 | 650.47 | 638.1942
3148.9417 | 711.8437 | 633.5861 | 645.8482 | 636.7033
3149.9417 | 710.4644 | 633.0256 | 645.382 | 633.7573
3150.9417 | 712.0367 | 615.8281 | 646.5564 | 623.9133
3151.9417 | 706.6888 | 635.9367 | 640.0458 | 627.0848
3152.9417 | 712.6823 | 636.9995 | 653.0896 | 625.4842
3153.9417 | 708.7727 | 637.4946 | 651.5306 | 624.4453
3154.9417 | 706.7417 | 638.8037 | 650.1578 | 629.1905
3155.9417 | 712.1516 | 641.354 | 653.8215 | 631.3322
3156.9417 | 721.2908 | 639.8755 | 649.198 | 639.6872
3157.9417 | 727.925 | 639.76 | 652.1699 | 635.0501
3158.9417 | 728.5061 | 640.5104 | 650.97 | 630.3126
3159.9417 | 731.7323 | 641.7199 | 653.7515 | 627.2139
3160.9417 | 723.2936 | 641.0452 | 648.1321 | 629.1361
3161.9417 | 722.1674 | 641.8209 | 646.2277 | 625.6458
3162.9417 | 719.6156 | 640.6064 | 643.7486 | 629.2812
3163.9417 | 713.0074 | 639.4227 | 644.4785 | 626.6236
3164.9417 | 716.7077 | 638.8201 | 648.7321 | 631.1109
3165.9417 | 714.1019 | 638.24 | 649.0501 | 630.3812
3166.9417 | 708.1838 | 638.0106 | 644.3172 | 630.036
3167.9417 | 714.4474 | 637.6994 | 644.6805 | 628.3969
3168.9417 | 718.0886 | 637.38 | 645.027 | 631.3945
3169.9417 | 714.3689 | 637.1994 | 645.3648 | 630.4409
3170.9417 | 716.688 | 637.2798 | 645.2962 | 627.6937
3171.9417 | 710.7199 | 635.5942 | 642.8604 | 627.0623
3172.9417 | 707.8984 | 634.5948 | 639.4196 | 623.7085
3173.9417 | 713.2487 | 633.3158 | 644.5773 | 622.3129
3174.9417 | 722.4729 | 632.7983 | 645.4571 | 625.4749
3175.9417 | 722.6916 | 632.001 | 643.6599 | 625.1713
3176.9417 | 715.764 | 630.7075 | 642.6261 | 623.9896
3177.9417 | 707.4065 | 629.6375 | 641.3832 | 626.6554
3178.9417 | 702.828 | 629.0786 | 644.5787 | 629.1928
3179.9417 | 694.7499 | 628.9655 | 643.324 | 628.9063
3180.9417 | 694.4841 | 632.0047 | 643.0603 | 628.8553
3181.9417 | 691.5565 | 632.7786 | 656.2295 | 627.947
3182.9417 | 694.3479 | 632.5319 | 651.7935 | 626.4135
3183.9417 | 691.2577 | 632.6495 | 651.9598 | 629.1065
3184.9417 | 691.4747 | 630.7879 | 649.3647 | 628.445
3185.9417 | 688.849 | 632.0091 | 649.0009 | 630.7274
3186.9417 | 689.5442 | 633.2796 | 648.8761 | 630.4675
3187.9417 | 702.3415 | 633.2981 | 649.5423 | 628.6475
3188.9417 | 706.3147 | 632.5552 | 652.3795 | 631.844
3189.9417 | 701.7839 | 633.1724 | 655.6277 | 637.9072
3190.9417 | 695.6644 | 634.2474 | 656.147 | 643.5493
3191.9417 | 697.7752 | 635.5227 | 656.0789 | 644.4544
3192.9417 | 692.6717 | 635.9384 | 660.9962 | 641.3573
3193.9417 | 704.3915 | 637.4971 | 662.2604 | 639.3174
3194.9417 | 700.2465 | 639.3825 | 661.8335 | 643.8718
3195.9417 | 700.5178 | 640.9212 | 664.5871 | 642.2326
3196.9417 | 697.2585 | 640.3582 | 658.8715 | 640.5126
3197.9417 | 695.1903 | 639.9422 | 660.3294 | 640.2778
3198.9417 | 691.287 | 640.2548 | 657.4607 | 640.1846
3199.9417 | 693.171 | 640.0501 | 659.8103 | 637.8899
3200.9417 | 691.2557 | 638.8891 | 656.6092 | 641.9103
3201.9417 | 690.4777 | 637.4096 | 653.28 | 637.4856
3202.9417 | 685.8024 | 636.8801 | 650.3776 | 637.432
3203.9417 | 696.8356 | 637.3805 | 647.89 | 635.1632
3204.9417 | 699.0323 | 638.0452 | 648.8762 | 635.0703
3205.9417 | 704.0171 | 636.9822 | 651.7838 | 632.7174
3206.9417 | 702.125 | 635.873 | 649.3067 | 632.1805
3207.9417 | 698.1206 | 635.3545 | 649.8099 | 631.2815
3208.9417 | 699.515 | 636.2539 | 647.9643 | 629.2678
3209.9417 | 694.2556 | 636.7614 | 650.5258 | 627.5503
3210.9417 | 694.2463 | 636.9699 | 650.824 | 627.3973
3211.9417 | 685.9423 | 635.9981 | 648.3649 | 627.0097
3212.9417 | 692.1055 | 636.244 | 645.8169 | 628.2635
3213.9417 | 696.7482 | 636.2933 | 649.3644 | 626.8753
3214.9417 | 710.7972 | 637.4095 | 646.0884 | 629.2468
3215.9417 | 702.8471 | 636.498 | 644.6231 | 627.0264
3216.9417 | 696.3342 | 635.5569 | 644.0775 | 624.862
3217.9417 | 705.884 | 634.7888 | 644.0562 | 627.3845
3218.9417 | 699.0927 | 635.445 | 647.0566 | 628.3219
3219.9417 | 698.4866 | 634.6995 | 648.9573 | 634.8443
3220.9417 | 699.0707 | 633.7369 | 652.8833 | 638.7161
3221.9417 | 706.1713 | 633.2656 | 660.3833 | 634.018
3222.9417 | 700.4296 | 634.1209 | 659.913 | 632.0687
3223.9417 | 707.079 | 636.6427 | 670.1812 | 632.2619
3224.9417 | 707.868 | 637.4531 | 677.1602 | 631.153
3225.9417 | 702.5368 | 638.3723 | 675.902 | 639.2491
3226.9417 | 705.3026 | 639.1265 | 683.1643 | 637.8236
3227.9417 | 699.3872 | 639.0024 | 678.0748 | 636.6242
3228.9417 | 698.9906 | 638.254 | 671.333 | 638.7967
3229.9417 | 699.881 | 637.3367 | 671.4593 | 638.3736
3230.9417 | 695.7134 | 637.2678 | 672.5729 | 637.284
3231.9417 | 697.5921 | 638.8795 | 667.8125 | 644.3007
3232.9417 | 696.0441 | 638.5481 | 661.4447 | 639.7416
3233.9417 | 695.1065 | 636.4598 | 659.7438 | 637.0723
3234.9417 | 688.7798 | 635.7393 | 654.2118 | 638.5744
3235.9417 | 690.4309 | 634.6745 | 654.6919 | 635.8622
3236.9417 | 692.2813 | 635.2187 | 652.7266 | 635.0664
3237.9417 | 691.3026 | 635.4423 | 657.5711 | 638.1318
3238.9417 | 691.703 | 635.1956 | 656.8526 | 636.2251
3239.9417 | 691.7943 | 634.6834 | 654.2769 | 633.9655
3240.9417 | 696.8712 | 634.0801 | 658.9478 | 632.6632
3241.9417 | 708.0175 | 636.7517 | 666.0884 | 633.8548
3242.9417 | 709.5794 | 639.2835 | 677.0035 | 637.7535
3243.9417 | 711.4528 | 642.7695 | 676.9833 | 637.8438
3244.9417 | 710.7365 | 645.0746 | 675.6003 | 636.7338
3245.9417 | 710.3006 | 644.1778 | 672.6347 | 637.4324
3246.9417 | 708.8715 | 643.1107 | 669.4403 | 636.8722
3247.9417 | 714.4499 | 641.1562 | 666.2824 | 641.4115
3248.9417 | 707.3693 | 640.3402 | 659.562 | 637.2335
3249.9417 | 698.5426 | 639.4449 | 655.8482 | 634.5951
3250.9417 | 698.5254 | 641.9166 | 665.3989 | 637.3925
3251.9417 | 698.1613 | 644.2278 | 668.927 | 636.3594
3252.9417 | 701.7815 | 643.2689 | 665.9292 | 636.6032
3253.9417 | 701.6102 | 643.0823 | 662.5964 | 643.1636
3254.9417 | 700.695 | 642.432 | 664.4399 | 644.0557
3255.9417 | 705.6491 | 645.2305 | 669.5725 | 647.3036
3256.9417 | 706.8106 | 644.962 | 671.9307 | 645.8708
3257.9417 | 705.0657 | 644.5647 | 666.6067 | 650.4008
3258.9417 | 698.1187 | 642.5944 | 663.094 | 651.6813
3259.9417 | 693.1837 | 646.1138 | 668.6514 | 653.2023
3260.9417 | 689.1106 | 645.7417 | 664.1258 | 650.7717
3261.9417 | 686.5732 | 644.0179 | 656.1468 | 645.4091
3262.9417 | 687.7528 | 645.2378 | 662.9725 | 639.576
3263.9417 | 694.3627 | 645.7952 | 660.8494 | 639.4995
3264.9417 | 696.2807 | 645.7887 | 657.7615 | 636.8407
3265.9417 | 696.0678 | 647.4265 | 652.7082 | 645.7918
3266.9417 | 696.3646 | 652.2331 | 656.9267 | 645.686
3267.9417 | 690.7349 | 651.6941 | 654.5315 | 641.8471
3268.9417 | 688.3476 | 651.0515 | 662.9708 | 647.0915
3269.9417 | 686.3123 | 648.494 | 658.2853 | 642.2198
3270.9417 | 685.7941 | 646.2331 | 657.2129 | 637.0911
3271.9417 | 684.1091 | 644.0303 | 655.0131 | 634.9155
3272.9417 | 687.4397 | 641.5578 | 650.3611 | 631.3082
3273.9417 | 697.7507 | 640.0657 | 665.3037 | 633.1566
3274.9417 | 695.3566 | 638.6696 | 659.8796 | 630.8268
3275.9417 | 701.563 | 640.0633 | 659.7413 | 627.5177
3276.9417 | 691.8936 | 638.8906 | 662.8327 | 624.3771
3277.9417 | 692.4807 | 637.6382 | 663.9238 | 625.626
3278.9417 | 693.3492 | 636.2021 | 654.862 | 627.9086
3279.9417 | 694.2152 | 636.4124 | 653.818 | 624.834
3280.9417 | 688.6103 | 636.9773 | 652.8902 | 635.8743
3281.9417 | 688.2435 | 640.6393 | 675.7977 | 641.0924
3282.9417 | 678.879 | 642.5121 | 680.5293 | 642.6121
3283.9417 | 679.9255 | 641.8157 | 668.4116 | 643.8722
3284.9417 | 679.232 | 640.1072 | 659.8416 | 644.7683
3285.9417 | 681.5703 | 638.8778 | 654.432 | 642.6373
3286.9417 | 684.2757 | 638.0313 | 651.8365 | 641.7379
3287.9417 | 681.0558 | 637.4993 | 655.4688 | 637.1719
3288.9417 | 683.5919 | 637.3147 | 651.953 | 632.4842
3289.9417 | 686.1722 | 637.6132 | 655.6128 | 632.9557
3290.9417 | 685.0979 | 638.5456 | 660.6541 | 630.3011
3291.9417 | 681.5566 | 642.9023 | 669.6059 | 626.4512
3292.9417 | 683.3381 | 641.1672 | 663.1636 | 622.3571
3293.9417 | 679.925 | 640.0548 | 656.7005 | 628.2074
3294.9417 | 678.9544 | 637.4683 | 650.0345 | 629.9658
3295.9417 | 681.203 | 636.291 | 647.6191 | 627.9436
3296.9417 | 681.9312 | 635.7591 | 643.2632 | 627.2127
3297.9417 | 675.5186 | 634.1905 | 639.6083 | 625.7429
3298.9417 | 672.2442 | 633.3896 | 637.4874 | 624.1051
3299.9417 | 671.3628 | 633.3626 | 635.436 | 621.777
3300.9417 | 676.5901 | 633.3423 | 636.0087 | 619.5886
3301.9417 | 682.1429 | 632.3124 | 634.1442 | 618.1507
3302.9417 | 679.9226 | 632.9833 | 632.4497 | 616.0775
3303.9417 | 684.5869 | 634.1168 | 634.7452 | 614.3247
3304.9417 | 686.6154 | 635.1432 | 639.4139 | 613.271
3305.9417 | 688.1939 | 642.4263 | 641.6647 | 613.5836
3306.9417 | 686.7971 | 643.2305 | 656.9145 | 626.9478
3307.9417 | 679.9406 | 645.467 | 655.2586 | 631.2473
3308.9417 | 676.027 | 645.8183 | 667.7796 | 631.0084
3309.9417 | 675.8759 | 650.0321 | 673.5384 | 627.7174
3310.9417 | 676.6281 | 655.3073 | 675.0016 | 632.861
3311.9417 | 674.1993 | 656.3626 | 677.591 | 632.9539
3312.9417 | 671.0856 | 656.6757 | 684.1711 | 631.8792
3313.9417 | 666.908 | 659.3473 | 690.7293 | 628.8167
3314.9417 | 678.0234 | 657.5979 | 687.7183 | 629.5288
3315.9417 | 684.5566 | 664.3338 | 682.6471 | 629.2078
3316.9417 | 685.103 | 660.5023 | 674.4173 | 626.3567
3317.9417 | 683.4219 | 656.3827 | 668.3994 | 625.9364
3318.9417 | 685.7506 | 654.2323 | 661.6014 | 623.5983
3319.9417 | 685.8859 | 656.5139 | 661.9896 | 624.908
3320.9417 | 695.0233 | 657.2881 | 661.274 | 627.8624
3321.9417 | 699.3324 | 656.3317 | 656.8015 | 634.7171
3322.9417 | 686.6423 | 651.833 | 649.6825 | 630.3164
3323.9417 | 681.0016 | 652.6707 | 647.5688 | 625.6189
3324.9417 | 676.1645 | 648.7113 | 647.2612 | 624.171
3325.9417 | 673.1435 | 647.8995 | 650.4015 | 625.3748
3326.9417 | 668.3043 | 650.9335 | 652.2135 | 627.2377
3327.9417 | 669.2443 | 652.7272 | 651.5305 | 628.9782
3328.9417 | 677.8299 | 651.0909 | 649.4944 | 626.9866
3329.9417 | 684.7087 | 649.446 | 647.6973 | 624.7521
3330.9417 | 684.7494 | 648.7942 | 664.3908 | 623.9854
3331.9417 | 686.7762 | 648.8059 | 667.9352 | 624.0773
3332.9417 | 689.3606 | 651.0055 | 669.8273 | 622.7767
3333.9417 | 689.5676 | 647.9484 | 661.9403 | 622.5005
3334.9417 | 689.4275 | 647.2993 | 665.1917 | 623.6183
3335.9417 | 690.3647 | 647.9363 | 678.2794 | 635.5665
3336.9417 | 682.3215 | 647.9024 | 677.5191 | 641.0211
3337.9417 | 680.6291 | 646.974 | 687.7077 | 638.7104
3338.9417 | 677.9999 | 649.036 | 687.3433 | 635.9464
3339.9417 | 678.2924 | 651.4171 | 696.5293 | 634.9911
3340.9417 | 680.4502 | 653.0143 | 695.6432 | 631.1833
3341.9417 | 678.8879 | 654.0405 | 685.3162 | 627.4039
3342.9417 | 677.7717 | 650.8969 | 683.4275 | 624.6837
3343.9417 | 680.3562 | 648.429 | 686.9267 | 623.2855
3344.9417 | 682.1289 | 650.5199 | 688.8435 | 623.4139
3345.9417 | 677.4777 | 647.7076 | 678.1472 | 621.6578
3346.9417 | 672.2258 | 645.6654 | 669.5052 | 620.5613
3347.9417 | 669.9643 | 643.8422 | 661.6478 | 618.73
3348.9417 | 671.1098 | 646.8932 | 660.9208 | 616.0647
3349.9417 | 673.8197 | 646.7905 | 653.0252 | 614.3408
3350.9417 | 676.0067 | 643.8472 | 647.0967 | 611.3878
3351.9417 | 676.2647 | 640.9833 | 642.6996 | 607.4098
3352.9417 | 671.9449 | 638.7828 | 637.6626 | 604.3198
3353.9417 | 666.135 | 637.8497 | 637.7823 | 612.454
3354.9417 | 670.955 | 634.7117 | 647.7009 | 613.9913
3355.9417 | 666.1223 | 633.4445 | 644.9306 | 613.9605
3356.9417 | 663.3273 | 632.0429 | 642.8357 | 612.9175
3357.9417 | 663.1988 | 631.4187 | 639.8374 | 610.5571
3358.9417 | 667.0342 | 631.0184 | 643.3247 | 612.5088
3359.9417 | 670.3529 | 630.7873 | 642.6698 | 610.9514
3360.9417 | 670.3363 | 628.7347 | 638.5066 | 611.2842
3361.9417 | 670.0466 | 628.4096 | 634.8059 | 614.7995
3362.9417 | 663.1074 | 627.6015 | 631.1848 | 615.811
3363.9417 | 662.4234 | 626.2337 | 628.4657 | 619.1994
3364.9417 | 658.0073 | 625.4936 | 634.7933 | 618.0025
3365.9417 | 666.6946 | 626.9093 | 646.3399 | 624.9752
3366.9417 | 665.7213 | 625.9852 | 641.4001 | 625.9489
3367.9417 | 661.9531 | 624.6858 | 639.4008 | 627.224
3368.9417 | 661.4984 | 624.6799 | 640.0606 | 625.5719
3369.9417 | 663.0291 | 624.4139 | 638.2876 | 630.2934
3370.9417 | 667.0406 | 624.4217 | 640.0606 | 628.4767
3371.9417 | 667.0461 | 624.4505 | 637.748 | 624.7173
3372.9417 | 666.6755 | 622.5288 | 632.9949 | 621.7044
3373.9417 | 667.2563 | 620.8044 | 633.1479 | 618.2556
3374.9417 | 669.0449 | 620.5314 | 634.3695 | 617.6872
3375.9417 | 670.5474 | 620.8045 | 643.3748 | 618.0897
3376.9417 | 666.8976 | 630.4906 | 651.9267 | 616.2506
3377.9417 | 663.8446 | 633.2189 | 665.3876 | 613.8878
3378.9417 | 656.3766 | 632.6168 | 658.2528 | 614.2115
3379.9417 | 661.9367 | 633.1091 | 657.2768 | 623.5351
3380.9417 | 664.9316 | 633.5126 | 657.2473 | 625.0696
3381.9417 | 663.5886 | 634.9915 | 655.5262 | 624.8329
3382.9417 | 662.6495 | 634.7117 | 649.9065 | 620.6917
3383.9417 | 660.1468 | 632.8213 | 642.1359 | 618.572
3384.9417 | 665.0662 | 632.2133 | 636.8053 | 617.7452
3385.9417 | 659.5062 | 634.5194 | 633.8557 | 620.9846
3386.9417 | 658.595 | 640.6773 | 646.8217 | 619.5534
3387.9417 | 650.1334 | 645.8262 | 663.0524 | 617.2119
3388.9417 | 648.5518 | 647.7689 | 664.7099 | 614.7678
3389.9417 | 645.2399 | 645.621 | 664.6437 | 612.4559
3390.9417 | 646.3554 | 642.7234 | 658.5902 | 613.7068
3391.9417 | 643.7487 | 641.0862 | 658.4941 | 612.2626
3392.9417 | 643.3953 | 639.2179 | 662.1145 | 613.9808
3393.9417 | 647.0629 | 641.6387 | 664.9325 | 613.8235
3394.9417 | 653.6609 | 639.586 | 658.8685 | 614.3351
3395.9417 | 650.8798 | 637.6258 | 650.3576 | 615.0312
3396.9417 | 650.0243 | 637.2519 | 658.4583 | 613.7652
3397.9417 | 644.2342 | 633.8559 | 653.0966 | 616.4416
3398.9417 | 640.7649 | 630.4363 | 645.598 | 617.2356
3399.9417 | 646.0769 | 630.3832 | 639.9051 | 615.4788
3400.9417 | 644.1249 | 628.5914 | 634.8113 | 613.5835
3401.9417 | 644.9572 | 626.911 | 636.2015 | 611.269
3402.9417 | 644.4561 | 625.6194 | 636.7723 | 610.3817
3403.9417 | 651.7632 | 624.1223 | 634.2059 | 609.9202
3404.9417 | 658.027 | 624.5311 | 633.3983 | 610.1705
3405.9417 | 652.3646 | 624.0972 | 629.547 | 613.2969
3406.9417 | 647.1972 | 622.4307 | 625.3566 | 613.4276
3407.9417 | 642.3442 | 621.8546 | 623.6477 | 610.0571
3408.9417 | 645.2401 | 620.1127 | 621.1776 | 608.7786
3409.9417 | 646.3433 | 620.8557 | 618.5554 | 606.2859
3410.9417 | 641.6385 | 621.4096 | 624.5905 | 604.8718
3411.9417 | 641.7767 | 620.9006 | 621.8176 | 606.0489
3412.9417 | 638.8156 | 619.4891 | 622.4313 | 609.739
3413.9417 | 639.7829 | 623.8197 | 627.0996 | 608.8351
3414.9417 | 643.9226 | 626.2103 | 641.6914 | 608.4351
3415.9417 | 648.5917 | 627.0941 | 642.8537 | 613.3483
3416.9417 | 652.2405 | 630.2706 | 648.2189 | 614.3275
3417.9417 | 651.9858 | 633.736 | 654.2374 | 625.4178
3418.9417 | 655.3365 | 640.7633 | 669.2431 | 630.0465
3419.9417 | 654.4404 | 643.3046 | 668.7749 | 624.9498
3420.9417 | 655.1907 | 645.2275 | 663.7991 | 621.9211
3421.9417 | 658.0726 | 646.9838 | 660.9042 | 619.7738
3422.9417 | 656.8134 | 644.1276 | 654.1665 | 616.1553
3423.9417 | 657.955 | 642.472 | 659.8017 | 613.855
3424.9417 | 664.3324 | 645.2076 | 662.9036 | 616.0463
3425.9417 | 662.0693 | 644.5578 | 654.7244 | 615.6673
3426.9417 | 658.3943 | 644.7794 | 649.8391 | 614.8413
3427.9417 | 654.821 | 642.7911 | 645.4064 | 612.2217
3428.9417 | 656.4932 | 640.7676 | 641.6685 | 610.0803
3429.9417 | 665.5764 | 638.7586 | 638.3803 | 608.934
3430.9417 | 660.863 | 635.3722 | 637.4578 | 611.6485
3431.9417 | 664.1441 | 634.4503 | 638.5505 | 611.0377
3432.9417 | 663.24 | 635.6864 | 639.8154 | 614.1121
3433.9417 | 661.3064 | 639.9158 | 641.7101 | 613.378
3434.9417 | 664.3453 | 642.5294 | 642.04 | 611.3335
3435.9417 | 657.6587 | 645.1499 | 655.16 | 609.6736
3436.9417 | 656.0032 | 646.1686 | 663.3287 | 609.6908
3437.9417 | 658.2374 | 649.5991 | 661.5701 | 610.4753
3438.9417 | 653.7804 | 653.3394 | 664.4686 | 609.4475
3439.9417 | 657.4759 | 656.6586 | 676.5718 | 606.6214
3440.9417 | 654.5702 | 659.2434 | 680.0751 | 606.6451
3441.9417 | 653.3103 | 657.8648 | 679.9437 | 605.9297
3442.9417 | 652.5649 | 651.8976 | 674.5858 | 607.2552
3443.9417 | 651.6141 | 647.1683 | 668.595 | 611.5811
3444.9417 | 650.5719 | 644.5904 | 668.2296 | 612.0496
3445.9417 | 647.5079 | 643.6009 | 669.851 | 610.6537
3446.9417 | 639.1166 | 644.9864 | 663.4006 | 608.9984
3447.9417 | 634.797 | 647.1617 | 675.3375 | 606.2049
3448.9417 | 630.9284 | 647.4457 | 673.5225 | 608.6514
3449.9417 | 629.8509 | 643.1283 | 662.6453 | 608.8173
3450.9417 | 625.8575 | 638.9975 | 662.3993 | 615.8244
3451.9417 | 634.6799 | 635.7489 | 659.5598 | 621.9134
3452.9417 | 633.2966 | 635.748 | 654.2232 | 626.9298
3453.9417 | 632.1121 | 634.701 | 664.282 | 629.9971
3454.9417 | 634.9388 | 633.9257 | 666.7995 | 629.0219
3455.9417 | 638.5446 | 636.9372 | 672.1301 | 630.6848
3456.9417 | 636.8926 | 637.0165 | 661.4148 | 638.5536
3457.9417 | 643.9376 | 634.814 | 660.7955 | 636.5538
3458.9417 | 643.6611 | 632.7582 | 653.0388 | 633.603
3459.9417 | 644.2318 | 631.8081 | 647.8598 | 628.2634
3460.9417 | 646.4891 | 630.6853 | 644.783 | 624.4119
3461.9417 | 646.7775 | 630.1071 | 641.974 | 626.7501
3462.9417 | 647.498 | 628.0416 | 638.5872 | 633.3681
3463.9417 | 647.6882 | 627.3585 | 641.0397 | 640.6998
3464.9417 | 650.8493 | 628.8887 | 647.0563 | 638.0149
3465.9417 | 650.3916 | 629.2141 | 642.419 | 635.2934
3466.9417 | 645.3447 | 627.5339 | 636.354 | 631.0474
3467.9417 | 646.6509 | 627.403 | 631.0175 | 627.9537
3468.9417 | 639.7139 | 626.582 | 624.4678 | 623.7163
3469.9417 | 636.6304 | 628.0002 | 624.2833 | 621.6453
3470.9417 | 633.6126 | 629.0747 | 632.9147 | 624.9455
3471.9417 | 629.0124 | 630.8085 | 636.3451 | 620.1225
3472.9417 | 634.1799 | 633.1329 | 648.2045 | 617.5843
3473.9417 | 636.2922 | 635.4785 | 660.0829 | 616.2139
3474.9417 | 633.9891 | 635.5517 | 661.1553 | 612.6774
3475.9417 | 637.0363 | 636.7674 | 653.3271 | 610.823
3476.9417 | 637.3023 | 635.1461 | 648.0723 | 608.6435
3477.9417 | 638.9816 | 632.7116 | 643.4582 | 607.2668
3478.9417 | 640.3358 | 631.0288 | 641.0716 | 609.1904
3479.9417 | 637.4009 | 629.6374 | 640.8647 | 614.4185
3480.9417 | 639.0402 | 629.6166 | 642.8208 | 618.7119
3481.9417 | 640.5143 | 628.4645 | 646.6255 | 622.9838
3482.9417 | 640.3439 | 631.0316 | 643.6017 | 620.321
3483.9417 | 638.1198 | 634.1756 | 638.671 | 619.8899
3484.9417 | 632.7609 | 635.4526 | 649.7912 | 615.906
3485.9417 | 635.3023 | 637.4428 | 657.557 | 615.9782
3486.9417 | 633.9287 | 638.2629 | 657.2526 | 612.7185
3487.9417 | 640.0839 | 637.6425 | 657.9158 | 608.0681
3488.9417 | 644.6069 | 636.2563 | 658.9704 | 607.782
3489.9417 | 646.5839 | 640.0867 | 664.3378 | 606.359
3490.9417 | 642.5069 | 642.469 | 671.0189 | 612.2082
3491.9417 | 637.7277 | 642.3916 | 669.6859 | 610.9
3492.9417 | 639.4764 | 643.3285 | 662.0656 | 608.244
3493.9417 | 639.2294 | 640.4557 | 660.1884 | 608.1529
3494.9417 | 636.9538 | 637.6863 | 653.9288 | 606.7931
3495.9417 | 637.8961 | 635.3471 | 654.3017 | 606.5763
3496.9417 | 639.8075 | 635.1729 | 652.7891 | 606.9405
3497.9417 | 639.6373 | 634.6892 | 646.4965 | 604.7174
3498.9417 | 647.1478 | 634.9847 | 645.3491 | 603.1666
3499.9417 | 645.4901 | 633.5379 | 646.6766 | 601.1934
3500.9417 | 642.3348 | 632.8403 | 646.4378 | 603.7807
3501.9417 | 642.1774 | 631.2017 | 650.4091 | 606.2631
3502.9417 | 638.6115 | 635.1886 | 659.9339 | 606.7079
3503.9417 | 634.3343 | 638.055 | 657.0363 | 604.7251
3504.9417 | 631.3769 | 635.929 | 661.3477 | 603.991
3505.9417 | 631.0646 | 635.2882 | 655.1818 | 603.2465
3506.9417 | 626.676 | 634.0578 | 651.7851 | 613.4084
3507.9417 | 626.046 | 633.4491 | 649.4197 | 613.3361
3508.9417 | 625.2199 | 632.0018 | 655.6318 | 612.883
3509.9417 | 625.8708 | 630.3091 | 649.9836 | 619.029
3510.9417 | 623.9199 | 629.9748 | 647.909 | 615.4925
3511.9417 | 625.9446 | 632.503 | 654.7332 | 618.845
3512.9417 | 634.8582 | 634.3511 | 652.3081 | 617.4484
3513.9573 | 636.8146 | 635.7242 | 660.3518 | 613.76
3514.9417 | 634.822 | 635.2505 | 655.9161 | 610.931
3515.9417 | 631.6627 | 631.8447 | 650.6315 | 613.3546
3516.9417 | 629.9692 | 630.7966 | 645.1344 | 620.3401
3517.9417 | 627.4748 | 634.1039 | 655.3332 | 622.2497
3518.9417 | 627.0586 | 634.5168 | 652.1019 | 618.6618
3519.9417 | 625.1409 | 635.0597 | 657.0302 | 614.5281
3520.9417 | 627.2477 | 636.6491 | 665.1497 | 611.9228
3521.9417 | 627.222 | 641.2285 | 669.6716 | 608.9829
3522.9417 | 621.8661 | 640.4652 | 676.0091 | 604.6707
3523.9417 | 624.9696 | 637.4047 | 675.6392 | 613.6725
3524.9417 | 625.7494 | 635.4238 | 668.7127 | 611.4557
3525.9417 | 630.1723 | 635.5544 | 666.6833 | 614.8371
3526.9417 | 628.495 | 634.1844 | 660.9375 | 612.8338
3527.9417 | 632.2607 | 634.4745 | 672.9013 | 610.0488
3528.9417 | 630.2735 | 635.3475 | 674.1599 | 606.1138
3529.9417 | 631.534 | 636.5925 | 678.0781 | 603.9404
3530.9417 | 637.1623 | 637.0864 | 668.7607 | 603.8448
3531.9417 | 642.945 | 638.4597 | 675.7619 | 607.2567
3532.9417 | 645.5414 | 638.8308 | 674.3459 | 611.4362
3533.9417 | 643.2432 | 640.1479 | 673.1599 | 609.5766
3534.9417 | 638.2288 | 640.8457 | 683.9205 | 612.5674
3535.9417 | 634.0776 | 641.0058 | 686.4968 | 610.5246
3536.9417 | 631.7261 | 639.9472 | 684.4809 | 606.9981
3537.9417 | 629.7688 | 643.4659 | 674.6948 | 606.1957
3538.9417 | 627.0917 | 645.2243 | 669.9914 | 604.2529
3539.9417 | 622.8745 | 646.0931 | 677.7355 | 603.6391
3540.9417 | 620.2255 | 646.2382 | 675.0631 | 601.2828
3541.9417 | 615.2354 | 646.3174 | 675.4702 | 599.177
3542.9417 | 612.8717 | 643.1588 | 671.1833 | 595.5523
3543.9417 | 614.634 | 640.2553 | 659.4678 | 595.3041
3544.9417 | 619.4426 | 638.221 | 657.4867 | 598.2195
3545.9417 | 624.9923 | 636.2503 | 649.679 | 606.3525
3546.9417 | 623.63 | 634.168 | 646.0874 | 602.2232
3547.9417 | 619.8878 | 631.9465 | 638.7757 | 600.3996
3548.9417 | 619.5473 | 630.3387 | 633.2186 | 600.1153
3549.9417 | 622.236 | 629.0078 | 630.0538 | 598.4243
3550.9417 | 621.8643 | 627.3209 | 625.592 | 607.2957
3551.9417 | 619.3286 | 627.3636 | 630.8623 | 609.4093
3552.9417 | 620.6602 | 627.3515 | 628.1017 | 605.9603
3553.9417 | 623.2134 | 627.2281 | 632.2323 | 602.0677
3554.9417 | 620.0894 | 630.9602 | 640.3157 | 598.2728
3555.9417 | 621.6927 | 633.0039 | 643.0129 | 597.062
3556.9417 | 622.4712 | 634.2325 | 643.8969 | 595.4638
3557.9417 | 618.7091 | 636.9224 | 651.6262 | 592.322
3558.9417 | 618.6114 | 638.0909 | 654.3106 | 590.9757
3559.9417 | 620.1906 | 639.2701 | 661.2882 | 590.2157
3560.9417 | 615.4875 | 638.9021 | 660.0143 | 588.2292
3561.9417 | 621.1642 | 637.5178 | 651.4014 | 590.0906
3562.9417 | 616.6651 | 635.4887 | 642.3214 | 592.3712
3563.9417 | 617.3241 | 635.621 | 655.9262 | 589.698
3564.9417 | 613.4693 | 635.3791 | 654.3381 | 594.8506
3565.9417 | 615.6495 | 635.4138 | 656.9407 | 592.3961
3566.9417 | 615.9005 | 635.4547 | 650.6139 | 589.3428
3567.9417 | 612.7819 | 638.5461 | 650.19 | 587.8633
3568.9417 | 607.8804 | 637.1017 | 649.4127 | 592.0632
3569.9417 | 607.5042 | 637.0371 | 656.9947 | 589.9037
3570.9417 | 612.0154 | 637.3963 | 659.3007 | 589.9382
3571.9417 | 629.6717 | 636.8945 | 653.3523 | 588.7764
3572.9417 | 632.3957 | 635.2605 | 649.3897 | 588.4749
3573.9417 | 632.4817 | 635.0463 | 643.1896 | 587.5125
3574.9417 | 637.5866 | 635.0573 | 637.2447 | 585.873
3575.9417 | 631.3846 | 634.8873 | 631.0609 | 583.9218
3576.9417 | 637.1574 | 635.8668 | 627.4876 | 582.3667
3577.9417 | 635.5769 | 636.1178 | 633.0457 | 580.1457
3578.9417 | 626.9676 | 635.007 | 632.2154 | 578.2574
3579.9417 | 619.8234 | 633.4329 | 629.9554 | 577.0146
3580.9417 | 615.9788 | 630.9253 | 626.5641 | 581.5157
3581.9417 | 618.1732 | 629.0934 | 626.254 | 580.6646
3582.9417 | 610.3984 | 628.0301 | 623.3828 | 580.5329
3583.9417 | 609.5109 | 627.9041 | 622.7398 | 581.665
3584.9417 | 618.2814 | 626.6077 | 623.5377 | 585.5327
3585.9417 | 614.3469 | 626.6091 | 628.7227 | 586.8924
3586.9417 | 611.9451 | 629.7154 | 632.8677 | 588.7207
3587.9417 | 607.9986 | 631.346 | 644.0118 | 587.934
3588.9417 | 608.4335 | 633.5226 | 643.9288 | 586.2629
3589.9417 | 610.6287 | 634.9773 | 645.0727 | 587.3118
3590.9417 | 612.0847 | 634.3144 | 641.1021 | 586.8176
3591.9417 | 609.0518 | 632.7829 | 634.5087 | 586.9932
3592.9417 | 606.2589 | 632.1362 | 628.8134 | 586.3844
3593.9417 | 603.5495 | 631.4301 | 631.0286 | 588.1445
3594.9417 | 599.0631 | 630.5919 | 633.7432 | 588.0533
3595.9417 | 599.1761 | 628.0557 | 630.5344 | 586.6595
3596.9417 | 599.6349 | 626.1627 | 628.002 | 591.3438
3597.9417 | 593.6332 | 625.7294 | 629.08 | 593.9457
3598.9417 | 593.1924 | 626.5662 | 626.1379 | 593.2498
3599.9417 | 593.5785 | 626.6793 | 621.3575 | 592.8583
3600.9417 | 591.9908 | 625.6049 | 618.8579 | 597.9599
3601.9417 | 590.6049 | 623.8512 | 616.2146 | 595.7092
3602.9417 | 594.9084 | 622.7852 | 613.6406 | 596.5004
3603.9417 | 597.6993 | 621.3124 | 611.7859 | 594.4453
3604.9417 | 599.6776 | 622.22 | 611.4725 | 593.9045
3605.9417 | 602.1789 | 621.3269 | 608.7817 | 595.113
3606.9417 | 602.7701 | 621.2447 | 605.7544 | 596.1665
3607.9417 | 597.5918 | 620.7859 | 603.3155 | 594.4162
3608.9417 | 600.7516 | 618.774 | 603.348 | 593.8771
3609.9417 | 599.8345 | 618.638 | 605.78 | 593.7724
3610.9417 | 595.3301 | 619.1123 | 608.5494 | 588.3328
3611.9417 | 593.8547 | 620.6191 | 613.311 | 583.8257
3612.9417 | 598.9115 | 618.7763 | 617.6078 | 582.7248
3613.9417 | 603.2729 | 619.8881 | 618.2693 | 583.1692
3614.9417 | 601.7551 | 620.3365 | 615.194 | 582.139
3615.9417 | 601.1856 | 621.0078 | 611.0446 | 582.0445
3616.9417 | 595.7202 | 620.071 | 609.8669 | 580.8501
3617.9417 | 593.7426 | 620.0906 | 618.5429 | 580.8653
3618.9417 | 599.6184 | 621.7979 | 619.1266 | 579.6763
3619.9417 | 598.9599 | 620.4318 | 620.979 | 582.8455
3620.9417 | 601.8753 | 620.8516 | 621.0271 | 582.3759
3621.9417 | 599.2031 | 625.7916 | 619.275 | 582.3527
3622.9417 | 594.4687 | 625.64 | 622.7008 | 585.0502
3623.9417 | 594.2119 | 626.9783 | 622.1797 | 585.3878
3624.9417 | 597.8579 | 626.619 | 631.5233 | 588.0313
3625.9417 | 593.931 | 628.6952 | 636.7976 | 585.6056
3626.9417 | 589.2469 | 628.0047 | 630.9068 | 583.9463
3627.9417 | 589.9079 | 630.6591 | 631.8097 | 580.9506
3628.9417 | 585.8654 | 630.9605 | 630.0497 | 579.8826
3629.9417 | 584.1947 | 631.4784 | 631.2518 | 578.5272
3630.9417 | 582.9054 | 630.674 | 626.5441 | 580.5775
3631.9417 | 583.7098 | 629.9538 | 632.5195 | 578.3953
3632.9417 | 583.0604 | 627.288 | 627.3683 | 576.8057
3633.9573 | 587.2533 | 624.806 | 628.5732 | 579.4192
3634.9417 | 600.4243 | 624.0488 | 635.17 | 582.3824
3635.9417 | 609.9207 | 622.0994 | 631.5979 | 580.2601
3636.9417 | 610.8033 | 621.11 | 630.4182 | 582.4398
3637.9573 | 609.7591 | 620.1268 | 628.9775 | 582.5923
3638.9417 | 608.4077 | 618.6606 | 620.8609 | 587.7821
3639.9417 | 605.6463 | 618.0771 | 616.1388 | 585.874
3640.9417 | 613.4227 | 617.3568 | 620.2505 | 592.7644
3641.9417 | 621.7608 | 616.8733 | 619.1136 | 590.7329
3642.9417 | 623.0367 | 616.1923 | 613.4548 | 589.4673
3643.9417 | 625.2688 | 614.9347 | 608.0683 | 586.8246
3644.9417 | 615.9537 | 616.8936 | 607.8834 | 585.7229
3645.9417 | 610.327 | 617.3081 | 609.527 | 583.8203
3646.9417 | 613.4259 | 619.1672 | 622.2122 | 583.0132
3647.9417 | 620.0103 | 620.7719 | 619.7947 | 581.8746
3648.9417 | 616.1616 | 621.617 | 622.2136 | 581.5678
3649.9417 | 607.8872 | 622.039 | 617.1899 | 586.8654
3650.9417 | 609.1551 | 621.5814 | 615.0044 | 591.1205
3651.9417 | 607.1755 | 620.2003 | 611.4014 | 589.4323
3652.9417 | 602.518 | 619.6752 | 607.9272 | 591.1897
3653.9417 | 595.4548 | 618.0128 | 603.1188 | 595.4695
3654.9417 | 591.7007 | 616.7372 | 604.2129 | 594.2287
3655.9417 | 589.1235 | 616.7555 | 601.4906 | 591.9173
3656.9417 | 589.871 | 616.0442 | 605.3402 | 587.6623
3657.9417 | 587.411 | 614.9827 | 601.7658 | 587.4439
3658.9417 | 587.7283 | 613.9437 | 600.9618 | 587.5209
3659.9417 | 590.7643 | 612.898 | 598.4496 | 584.1498
3660.9417 | 588.7319 | 613.9942 | 598.3933 | 587.9778
3661.9417 | 592.7353 | 615.5919 | 610.898 | 584.5999
3662.9417 | 593.5619 | 616.1097 | 619.1521 | 582.675
3663.9417 | 592.9026 | 616.9516 | 620.5094 | 580.6742
3664.9417 | 589.928 | 617.7089 | 625.3843 | 580.4708
3665.9417 | 596.1273 | 616.8381 | 622.8666 | 578.0962
3666.9417 | 593.1135 | 615.6493 | 622.3969 | 577.6138
3667.9417 | 591.5602 | 615.0979 | 619.0903 | 578.3031
3668.9417 | 594.4646 | 613.6147 | 614.0522 | 577.0024
3669.9417 | 596.2686 | 612.0506 | 615.9289 | 576.0956
3670.9417 | 598.2375 | 613.2983 | 616.6582 | 579.7816
3671.9417 | 600.7446 | 612.4432 | 614.2467 | 578.7339
3672.9417 | 601.3056 | 611.2786 | 611.0039 | 578.5852
3673.9417 | 600.7394 | 609.8446 | 608.5028 | 576.4516
3674.9417 | 601.0108 | 609.0009 | 605.4856 | 574.9877
3675.9417 | 597.4692 | 608.1677 | 602.1301 | 574.3431
3676.9417 | 597.8797 | 607.8146 | 600.2704 | 572.7115
3677.9417 | 597.7019 | 607.1034 | 600.1327 | 573.7789
3678.9417 | 597.1536 | 605.4102 | 596.6095 | 573.3211
3679.9417 | 597.4572 | 606.4884 | 593.7962 | 571.9091
3680.9417 | 591.4719 | 610.7566 | 597.6391 | 572.1689
3681.9417 | 589.4383 | 612.5801 | 597.8113 | 571.3583
3682.9417 | 588.3301 | 613.4211 | 601.7389 | 571.6767
3683.9417 | 587.9562 | 614.3916 | 612.3235 | 569.7235
3684.9417 | 588.1187 | 613.2527 | 619.575 | 568.1401
3685.9417 | 591.431 | 614.731 | 614.6384 | 568.2068
3686.9417 | 590.0604 | 616.6645 | 620.4126 | 567.3456
3687.9417 | 592.271 | 619.7067 | 619.4974 | 567.6065
3688.9417 | 587.4778 | 619.8167 | 629.9871 | 567.2767
3689.9417 | 587.9451 | 619.0007 | 637.2356 | 566.7502
3690.9417 | 588.5937 | 618.2532 | 636.9796 | 568.0836
3691.9417 | 593.8262 | 618.7042 | 630.3558 | 569.4886
3692.9417 | 595.4819 | 620.7832 | 631.472 | 573.8937
3693.9417 | 593.3162 | 620.5359 | 625.2003 | 574.8425
3694.9417 | 595.0853 | 619.0599 | 629.2496 | 573.2395
3695.9417 | 594.5552 | 620.0057 | 641.5737 | 572.6102
3696.9417 | 595.5063 | 618.671 | 631.9453 | 571.3639
3697.9417 | 595.563 | 619.1755 | 625.7799 | 569.9594
3698.9417 | 596.4524 | 619.2922 | 636.7497 | 571.7613
3699.9417 | 596.2946 | 618.8163 | 643.8224 | 572.3044
3700.9417 | 597.4719 | 618.16 | 647.5122 | 570.4601
3701.9417 | 597.5824 | 618.8568 | 639.3714 | 570.6002
3702.9417 | 594.2274 | 620 | 638.4765 | 570.0072
3703.9417 | 590.5795 | 618.3211 | 639.8895 | 568.1421
3704.9417 | 590.3381 | 615.705 | 636.4252 | 567.1394
3705.9417 | 602.8761 | 616.0135 | 635.0336 | 567.0859
3706.9417 | 597.94 | 617.5833 | 633.8845 | 566.8435
3707.9417 | 594.4831 | 619.1245 | 637.4277 | 566.2899
3708.9417 | 590.8732 | 617.608 | 630.6191 | 567.5311
3709.9417 | 588.5075 | 615.5485 | 627.4878 | 566.8193
3710.9417 | 588.4538 | 615.3093 | 627.2157 | 567.8852
3711.9417 | 585.9749 | 614.0103 | 619.4473 | 567.4089
3712.9417 | 586.9367 | 612.9855 | 619.1992 | 567.0909
3713.9417 | 596.105 | 611.3692 | 615.6596 | 566.9674
3714.9417 | 599.0439 | 609.884 | 613.5428 | 567.2009
3715.9417 | 601.8952 | 608.9227 | 609.4461 | 566.9548
3716.9417 | 596.6832 | 607.1044 | 608.0619 | 566.5639
3717.9417 | 595.2135 | 606.9795 | 609.4297 | 567.4771
3718.9417 | 599.9587 | 607.2341 | 610.8602 | 569.0601
3719.9417 | 607.3922 | 609.4516 | 607.9803 | 569.4293
3720.9417 | 598.5954 | 610.6103 | 613.4827 | 568.1228
3721.9417 | 593.4342 | 610.6019 | 610.545 | 566.5775
3722.9417 | 590.1144 | 611.345 | 608.0458 | 565.4188
3723.9417 | 588.0282 | 610.0337 | 610.863 | 567.161
3724.9417 | 586.0117 | 611.511 | 607.9906 | 566.0281
3725.9417 | 583.8142 | 611.2316 | 608.2627 | 565.5987
3726.9417 | 585.7633 | 612.3651 | 611.3843 | 566.7604
3727.9417 | 585.9706 | 612.3147 | 626.3056 | 566.1383
3728.9417 | 583.8759 | 614.0461 | 628.4691 | 566.0663
3729.9417 | 579.238 | 614.1774 | 624.3404 | 565.1734
3730.9417 | 577.2952 | 614.2356 | 623.5211 | 565.7798
3731.9417 | 573.9945 | 617.0317 | 624.4539 | 564.8565
3732.9417 | 571.9203 | 617.4069 | 620.8402 | 563.6454
3733.9417 | 572.6286 | 616.1595 | 618.6769 | 563.856
3734.9417 | 573.0609 | 617.2545 | 624.0119 | 563.4681
3735.9417 | 578.3215 | 616.3884 | 622.3533 | 568.7037
3736.9417 | 578.7849 | 613.9002 | 617.0809 | 567.2638
3737.9417 | 577.2135 | 612.9518 | 613.0154 | 566.26
3738.9417 | 573.9754 | 612.5205 | 610.5511 | 571.665
3739.9417 | 574.5052 | 612.281 | 610.8014 | 575.9467
3740.9417 | 575.7267 | 613.2069 | 610.9861 | 575.26
3741.9417 | 576.7416 | 612.8844 | 608.8176 | 573.661
3742.9417 | 580.0982 | 612.2912 | 607.1916 | 573.1633
3743.9417 | 578.7616 | 610.9298 | 606.3376 | 572.2157
3744.9417 | 578.9828 | 609.3336 | 603.0921 | 576.1042
3745.9417 | 575.4249 | 609.5165 | 603.3689 | 573.2685
3746.9417 | 574.7893 | 608.6365 | 604.5503 | 573.6602
3747.9417 | 574.3794 | 609.5562 | 602.6422 | 577.1175
3748.9417 | 578.0302 | 609.1317 | 606.057 | 575.2517
3749.9417 | 579.6133 | 608.1495 | 602.2407 | 572.2843
3750.9417 | 582.4364 | 607.5556 | 598.8712 | 572.1747
3751.9417 | 583.6582 | 606.052 | 598.4901 | 571.7353
3752.9417 | 587.8735 | 605.3171 | 598.082 | 570.9375
3753.9417 | 590.1653 | 603.9911 | 595.0577 | 569.7133
3754.9417 | 587.0017 | 604.0246 | 593.1122 | 566.503
3755.9417 | 582.5894 | 603.5846 | 592.2825 | 568.8169
3756.9417 | 583.5327 | 603.9875 | 591.3979 | 571.4774
3757.9417 | 584.7501 | 605.9335 | 592.5124 | 572.6462
3758.9417 | 579.4157 | 605.8576 | 594.0417 | 572.314
3759.9417 | 579.6836 | 605.7608 | 597.7227 | 571.638
3760.9417 | 581.2128 | 605.1452 | 600.6709 | 570.9915
3761.9417 | 586.2547 | 605.0594 | 603.6616 | 574.1558
3762.9417 | 591.3082 | 605.8616 | 604.4243 | 573.5246
3763.9417 | 589.1368 | 607.95 | 608.023 | 573.5443
3764.9417 | 590.8528 | 606.8999 | 609.9066 | 571.973
3765.9417 | 592.3325 | 607.0223 | 608.5189 | 574.4047
3766.9417 | 594.4522 | 605.7649 | 604.862 | 573.7713
3767.9417 | 595.4164 | 605.2658 | 604.9074 | 574.5201
3768.9417 | 599.0672 | 604.8555 | 604.9535 | 577.3215
3769.9417 | 604.1166 | 604.5904 | 603.7334 | 578.4818
3770.9417 | 604.5753 | 604.5337 | 605.2499 | 580.1869
3771.9417 | 602.2651 | 603.7536 | 603.9595 | 578.9173
3772.9417 | 602.045 | 601.4082 | 601.0558 | 578.79
3773.9417 | 601.2298 | 600.2016 | 599.5507 | 577.3469
3774.9417 | 601.5012 | 601.1454 | 598.8737 | 576.2466
3775.9417 | 602.6551 | 602.4765 | 601.4132 | 574.1922
3776.9417 | 601.2573 | 603.2273 | 610.0442 | 572.9276
3777.9417 | 597.0923 | 604.2147 | 617.415 | 571.5286
3778.9417 | 592.5393 | 604.3952 | 624.7006 | 572.5934
3779.9417 | 587.094 | 605.676 | 626.3542 | 570.8664
3780.9417 | 587.3588 | 609.2768 | 624.2703 | 570.3492
3781.9417 | 584.5087 | 611.4731 | 625.529 | 570.3526
3782.9417 | 583.3985 | 612.1077 | 626.1879 | 569.0258
3783.9417 | 582.7509 | 612.5955 | 626.9676 | 567.8043
3784.9417 | 581.3152 | 613.2984 | 625.4312 | 566.9168
3785.9417 | 583.5462 | 612.04 | 627.4798 | 567.2887
3786.9417 | 588.5344 | 610.745 | 624.589 | 571.503
3787.9417 | 590.7279 | 609.5123 | 625.6216 | 574.3289
3788.9417 | 594.8265 | 609.1847 | 624.9154 | 573.795
3789.9417 | 592.8034 | 606.9694 | 620.2857 | 572.3057
3790.9417 | 592.5121 | 604.6342 | 618.2578 | 571.0826
3791.9417 | 605.5588 | 603.6459 | 616.5825 | 570.3728
3792.9417 | 607.6422 | 604.8665 | 617.7858 | 572.0974
3793.9417 | 603.503 | 607.6469 | 618.1402 | 571.2377
3794.9417 | 597.7825 | 608.2004 | 626.5281 | 570.2512
3795.9417 | 592.6409 | 609.95 | 623.4765 | 568.9469
3796.9417 | 588.0134 | 609.5333 | 619.5954 | 568.0854
3797.9417 | 584.7305 | 608.9686 | 626.3611 | 567.4775
3798.9417 | 583.8406 | 610.4655 | 623.5504 | 567.4558
3799.9417 | 583.5926 | 612.452 | 631.1551 | 566.0902
3800.9417 | 580.7865 | 612.1684 | 628.3749 | 565.8477
3801.9417 | 577.3962 | 611.4217 | 630.725 | 564.755
3802.9417 | 576.7478 | 612.7225 | 634.2335 | 563.7833
3803.9417 | 574.4658 | 612.1986 | 626.4217 | 562.779
3804.9417 | 576.8514 | 612.5462 | 632.4643 | 561.8457
3805.9417 | 578.7868 | 612.8779 | 633.7068 | 563.4076
3806.9417 | 580.6214 | 611.7098 | 628.7087 | 563.9546
3807.9417 | 581.7701 | 609.873 | 623.1975 | 562.7947
3808.9417 | 582.9041 | 608.9543 | 619.0974 | 562.97
3809.9417 | 582.0206 | 608.8369 | 616.5596 | 562.632
3810.9417 | 579.9822 | 610.2401 | 623.3097 | 561.957
3811.9417 | 580.8541 | 610.9643 | 621.9387 | 562.732
3812.9417 | 580.2189 | 609.542 | 619.2293 | 563.4011
3813.9417 | 581.4869 | 609.0033 | 625.3266 | 562.6779
3814.9417 | 583.6151 | 608.0971 | 622.5574 | 562.0934
3815.9417 | 580.9027 | 609.693 | 621.6008 | 561.4877
3816.9417 | 576.6258 | 611.4108 | 620.3785 | 560.757
3817.9417 | 574.4166 | 611.0819 | 623.571 | 560.6757
3818.9417 | 574.9367 | 610.6978 | 636.2939 | 560.297
3819.9417 | 574.8478 | 610.1855 | 640.4088 | 560.244
3820.9417 | 574.0877 | 607.8844 | 629.8296 | 559.3011
3821.9417 | 579.1739 | 609.3292 | 627.3475 | 559.2369
3822.9417 | 577.0436 | 610.3475 | 620.5228 | 559.4976
3823.9417 | 577.3242 | 611.0457 | 619.5562 | 558.892
3824.9417 | 578.4619 | 611.6315 | 620.3224 | 559.4324
3825.9417 | 578.669 | 610.6927 | 621.4152 | 560.3074
3826.9417 | 575.4721 | 610.5862 | 620.9374 | 560.7544
3827.9417 | 572.2671 | 611.286 | 619.9998 | 559.7191
3828.9417 | 570.7245 | 611.872 | 620.0318 | 558.4766
3829.9417 | 567.4175 | 611.0738 | 617.6622 | 558.1379
3830.9417 | 566.916 | 609.6488 | 613.9349 | 558.4656
3831.9417 | 566.3286 | 608.0923 | 612.7332 | 563.5471
3832.9417 | 568.5066 | 606.1824 | 612.2756 | 565.0613
3833.9417 | 569.8791 | 605.6928 | 610.5301 | 567.6531
3834.9417 | 572.9395 | 606.7181 | 609.8186 | 569.4776
3835.9417 | 573.3374 | 609.1125 | 607.0378 | 569.2672
3836.9417 | 573.5619 | 610.9355 | 607.1308 | 573.0681
3837.9417 | 574.7899 | 610.35 | 609.7364 | 571.7897
3838.9417 | 575.6408 | 609.2344 | 611.5949 | 569.8041
3839.9417 | 573.9485 | 607.6896 | 609.8214 | 569.1114
3840.9417 | 572.3891 | 606.0001 | 605.1833 | 570.4459
3841.9417 | 577.2821 | 609.55 | 606.8019 | 571.3858
3842.9417 | 579.5251 | 611.344 | 605.0538 | 572.1595
3843.9417 | 577.5499 | 611.1593 | 605.889 | 572.2305
3844.9417 | 579.3346 | 611.6746 | 604.2483 | 574.2086
3845.9417 | 579.2812 | 611.761 | 611.099 | 572.7688
3846.9417 | 577.0285 | 611.0048 | 609.8349 | 571.887
3847.9417 | 577.521 | 611.8881 | 613.6499 | 572.8286
3848.9417 | 576.0515 | 611.6662 | 616.8151 | 570.9203
3849.9417 | 572.8591 | 610.0703 | 620.855 | 568.9684
3850.9417 | 571.1211 | 611.3991 | 619.9034 | 568.2395
3851.9573 | 570.146 | 613.5228 | 620.8869 | 567.144
3852.9417 | 570.9235 | 614.8877 | 621.2645 | 567.33
3853.9417 | 571.2009 | 614.1374 | 616.1086 | 566.2748
3854.9417 | 569.2967 | 612.3843 | 611.8182 | 565.2557
3855.9417 | 569.4508 | 612.1553 | 617.0554 | 565.6926
3856.9417 | 566.6291 | 612.2115 | 613.6656 | 564.4153
3857.9417 | 565.1939 | 611.8342 | 610.023 | 564.8794
3858.9417 | 564.4394 | 612.7232 | 609.3177 | 566.5466
3859.9417 | 563.9851 | 612.823 | 615.5335 | 565.5175
3860.9417 | 561.8665 | 611.9614 | 616.4789 | 564.8752
3861.9417 | 560.7917 | 611.8686 | 613.5307 | 564.6509
3862.9417 | 560.958 | 611.388 | 611.9034 | 564.1365
3863.9417 | 560.88 | 610.9499 | 609.1856 | 563.6999
3864.9417 | 563.9449 | 609.0738 | 607.1631 | 562.741
3865.9417 | 567.3601 | 609.1281 | 606.7727 | 564.3609
3866.9417 | 568.8454 | 609.6025 | 604.0527 | 563.1687
3867.9417 | 565.9227 | 609.4522 | 602.4926 | 562.0681
3868.9417 | 563.8566 | 609.0438 | 603.1295 | 561.6137
3869.9417 | 564.1611 | 610.0845 | 601.3313 | 562.3217
3870.9417 | 563.72 | 609.6823 | 599.3254 | 561.6471
3871.9417 | 563.6129 | 611.5581 | 600.3015 | 562.1421
3872.9417 | 563.2261 | 610.2241 | 598.231 | 561.4591
3873.9417 | 565.7606 | 610.0963 | 599.3765 | 562.5754
3874.9417 | 568.38 | 611.9077 | 602.9741 | 563.6805
3875.9417 | 570.1762 | 611.9587 | 600.8466 | 563.3595
3876.9417 | 568.0702 | 613.2573 | 603.9802 | 562.4413
3877.9417 | 567.5823 | 614.1513 | 604.0469 | 561.4721
3878.9417 | 566.6233 | 613.3185 | 602.6993 | 561.9712
3879.9417 | 566.8477 | 611.648 | 611.6579 | 561.1754
3880.9417 | 569.5387 | 612.0063 | 613.294 | 562.4644
3881.9573 | 571.4518 | 611.8132 | 614.6486 | 563.1557
3882.9417 | 572.7789 | 612.3564 | 614.7663 | 563.6733
3883.9417 | 573.8266 | 611.509 | 617.3024 | 564.1544
3884.9417 | 573.0304 | 611.9797 | 614.73 | 564.7486
3885.9417 | 572.1411 | 612.9828 | 613.5441 | 564.8902
3886.9417 | 569.1577 | 613.7435 | 612.5809 | 566.9424
3887.9417 | 569.2867 | 614.1093 | 614.6831 | 566.7621
3888.9417 | 569.1969 | 613.5946 | 615.2123 | 567.1953
3889.9417 | 571.1263 | 613.2786 | 617.907 | 568.7786
3890.9417 | 569.2367 | 610.1991 | 615.4265 | 568.0414
3891.9417 | 570.182 | 608.8792 | 613.6143 | 569.0571
3892.9417 | 569.5116 | 608.1813 | 610.5143 | 569.7922
3893.9417 | 569.3008 | 611.3183 | 611.7791 | 570.808
3894.9417 | 568.5471 | 610.7829 | 612.3791 | 569.4947